## Test Conditions
DESIREE-FIRE Intermediate Scale Test 5 - Circuit Data Only
Test Date: | 2010-03-01
DCSim DAQ Start Time | 13:30
DCSim Time for Synchronization | 13:42
Heat Source Synchronization | 0:01 | hours:minutes:seconds
Heat Source DAQ Start Time | 13:41
Fire Time | 14:02
Offset | 0:32 | hours:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 1920 | seconds
Heat Source Offset | 0:21 | hours:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 1288 | seconds
Heat Source Stop Time | 14:46
Test Duration | 0:44 | hours:minutes:seconds
| 2640 | seconds
CT500 turns | 2 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 turns | 5 | 1 or 5
Pre-Test Baseline: | Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
1" Solenoid Valve | XLPE/CSPE, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 1 represents the air temperature in the middle of the tray located in B Position. It is labeled as "B Position - Tray - Middle" in the temperature data file.
Large Coil | XLPE/CSPE, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 1 represents the air temperature in the middle of the tray located in B Position. It is labeled as "B Position - Tray - Middle" in the temperature data file.
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | 1"Coil_CT500 | 1"Coil_CT35_1_P | 1"Coil_CT35_2_G | 1"Coil_CT35_3_R | 1"Coil_CT35_4_N2 | 1"Coil_CT35_5_S | 1"Coil_CT35_6_N1 | LgCoil_CT500 | LgCoil_CT35_1_P | LgCoil_CT35_2_G | LgCoil_CT35_3_N2 | LgCoil_CT35_4_S | LgCoil_CT35_5_N1 | 1"Coil_VT7_1_G | 1"Coil_VT7_2_R | 1"Coil_VT7_3_SP | 1"Coil_VT7_4_S | 1"Coil_VTU_1_P | 1"Coil_VTU_2_N2 | 1"Coil_VTU_3_N1 | LgCoil_VT7_1_R | LgCoil_VT7_2_SP | LgCoil_VT7_3_S | LgCoil_VTU_1_P | LgCoil_VTU_2_G | LgCoil_VTU_3_N2 | LgCoil_VTU_4_N1 | {1"Valve} V(N2) - V(Batt -) | {1"Valve} V(N1) - V(Batt -) | {1"Valve} V(P) - V(Batt +) | {1"Valve} V(R) - V(Batt -) | {1"Valve} V(S) - V(Batt -) | {1"Valve} V(S) - V(N1) | {1"Valve} V(G) - V(Batt +) | {LgCoil} V(N2) - V(Batt -) | {LgCoil} V(N1) - V(Batt -) | {LgCoil} V(P) - V(Batt +) | {LgCoil} V(R) - V(Batt -) | {LgCoil} V(S) - V(Batt -) | {LgCoil} V(S) - V(N1) | {LgCoil} V(G) - V(Batt +) | {1"Valve} V(P) - V(Batt -) | {1"Valve} V(G) - V(Batt -) | {1"Valve} V(SP) - V(Batt -) | {1"Valve} V(N1) - V(Batt +) | {LgCoil} V(P) - V(Batt -) | {LgCoil} V(G) - V(Batt -) | {LgCoil} V(SP) - V(Batt -) | {LgCoil} V(N1) - V(Batt +)
-1.6094 | 124.0173 | -62.0407 | 61.8759 | 0.0067138 | 0.0079254 | 0.065322 | 0.0052531 | 0.067037 | -0.0026403 | -0.0037597 | -0.00083936 | -0.0041358 | 0.068131 | 0.071478 | -0.0025829 | -0.003339 | 61.9446 | -61.8027 | 0.068665 | -62.0224 | 61.7294 | -62.0453 | -61.9446 | -62.3383 | 0.082397 | -62.265 | 61.6745 | 61.7706 | -61.9125 | -62.1185 | -0.004578 | 0.09613 | -0.14648 | 0.23804 | 0.01831 | -0.07782 | 0.068664 | 0.12817 | -0.07782 | -0.20142 | -0.29755 | -0.22431 | -0.14648 | -0.10529 | 123.7701 | 123.9853 | 62.1094 | -123.8205 | 123.7152 | 123.8113 | 62.1231 | -123.9944
0.0625 | 123.9944 | -62.0316 | 61.908 | -0.0085447 | 0.0042938 | 0.066817 | 0.00098046 | 0.068105 | -0.0032813 | -0.0037597 | -0.00083936 | -0.0054174 | 0.065567 | 0.069342 | -0.0034373 | -0.0065432 | 61.94 | -61.8027 | 0.064087 | -62.0407 | 61.7523 | -62.0361 | -61.94 | -62.3795 | 0.059509 | -62.2742 | 61.6882 | 61.7569 | -61.9263 | -62.0865 | -0.004578 | 0.091553 | -0.15564 | 0.22888 | -0.009155 | -0.10071 | 0.032043 | 0.10528 | -0.054932 | -0.21973 | -0.3479 | -0.24262 | -0.18768 | -0.15106 | 123.7839 | 123.9716 | 62.0956 | -123.848 | 123.7198 | 123.7885 | 62.0911 | -123.9944
1.8125 | 124.1272 | -62.0544 | 61.8256 | -0.0085447 | 0.0038666 | 0.064467 | 0.0018351 | 0.067251 | 0.0024865 | -0.0020507 | -0.00083936 | -0.002854 | 0.063431 | 0.068915 | -0.00066033 | -0.0052616 | 61.8942 | -61.8805 | -0.004578 | -62.0682 | 61.7615 | -62.0819 | -61.9904 | -62.3886 | 0.068665 | -62.3154 | 61.6882 | 61.6974 | -61.9537 | -62.146 | -0.027466 | 0.064087 | -0.064087 | 0.17395 | -0.013733 | -0.07782 | 0.068664 | 0.10071 | -0.091553 | -0.13733 | -0.33417 | -0.26093 | -0.16937 | -0.12817 | 123.8159 | 123.9487 | 62.0499 | -123.8159 | 123.7427 | 123.7518 | 62.1231 | -123.9716
3.4844 | 123.9853 | -62.0773 | 61.8988 | -0.00091566 | 0.0034394 | 0.067031 | 0.0052531 | 0.068319 | -0.0032813 | -0.0024779 | -0.016098 | -0.004563 | 0.064286 | 0.069556 | -0.0032237 | -0.0063296 | 61.9354 | -61.8027 | 0.064087 | -62.0132 | 61.7569 | -62.0316 | -61.94 | -62.3749 | 0.059509 | -62.265 | 61.6974 | 61.7386 | -61.8851 | -62.1048 | 0.045777 | 0.13733 | -0.14191 | 0.27466 | 0.064087 | -0.073243 | 0.036621 | 0.19226 | -0.027465 | -0.20142 | -0.29755 | -0.18768 | -0.16022 | -0.16022 | 123.8342 | 124.0128 | 62.1414 | -123.8388 | 123.7747 | 123.8159 | 62.1368 | -124.0036
5.2344 | 124.0723 | -62.0499 | 61.8073 | -0.00091566 | 0.008139 | 0.067031 | 0.0048257 | 0.067678 | 0.0031275 | -0.0011963 | 0.0067901 | -0.0007178 | 0.065567 | 0.071905 | -0.0023693 | -0.0076114 | 61.9034 | -61.8896 | 0.082397 | -62.0544 | 61.7569 | -62.1048 | -62.0132 | -62.4298 | 0.050354 | -62.3932 | 61.6699 | 61.7203 | -61.9858 | -62.178 | -0.054931 | 0.036621 | -0.050354 | 0.16022 | -0.004577 | -0.041198 | 0.09613 | 0.064087 | -0.12817 | -0.13733 | -0.37994 | -0.34332 | -0.21515 | -0.086975 | 123.8068 | 123.9532 | 62.1323 | -123.8205 | 123.7198 | 123.7701 | 62.1002 | -123.9853
6.9688 | 124.0082 | -62.027 | 61.9034 | 0.0067138 | 0.0042938 | 0.067885 | 0.0054667 | 0.067251 | -0.0017859 | -0.0026917 | -0.0084684 | -0.0056312 | 0.062577 | 0.070624 | -0.0045055 | -0.003339 | 61.9034 | -61.8073 | 0.041199 | -62.0087 | 61.7798 | -62.0361 | -61.9263 | -62.384 | 0.032043 | -62.2833 | 61.702 | 61.7706 | -61.9034 | -62.0819 | -0.009155 | 0.10071 | -0.1236 | 0.21973 | 0.018311 | -0.082397 | 0 | 0.1236 | -0.054931 | -0.20142 | -0.35706 | -0.25635 | -0.20142 | -0.13275 | 123.8068 | 123.9304 | 62.0682 | -123.8297 | 123.7289 | 123.7976 | 62.059 | -123.9853
8.6406 | 124.1135 | -62.059 | 61.7706 | -0.00091566 | 0.0066438 | 0.06404 | 0.0039713 | 0.068319 | 0.0031275 | -0.0018371 | -0.00083936 | -0.0017858 | 0.065995 | 0.072333 | -0.0023693 | -0.0052616 | 61.8484 | -61.9583 | -0.045776 | -62.1094 | 61.7889 | -62.1414 | -62.0178 | -62.4481 | -0.013733 | -62.4069 | 61.6974 | 61.734 | -61.9812 | -62.1689 | -0.082397 | 0.041199 | 0.01831 | 0.10071 | -0.050354 | -0.091553 | 0.07782 | 0.07782 | -0.10986 | -0.073242 | -0.3891 | -0.3479 | -0.23804 | -0.036621 | 123.848 | 123.9075 | 62.0132 | -123.7885 | 123.7564 | 123.793 | 62.0453 | -123.9395
10.3906 | 123.9807 | -62.059 | 61.8668 | 0.0067138 | 0.0079254 | 0.068099 | 0.0071757 | 0.067678 | -0.0026403 | -0.0029053 | -0.00083936 | -0.004563 | 0.066849 | 0.071478 | -0.0021557 | -0.005048 | 61.9308 | -61.7752 | 0.14191 | -61.9904 | 61.7752 | -62.0499 | -61.94 | -62.3795 | 0.09613 | -62.3062 | 61.7065 | 61.7477 | -61.9125 | -62.1368 | 0.009155 | 0.11902 | -0.091552 | 0.28381 | 0.068665 | -0.050354 | 0.064087 | 0.14648 | -0.07782 | -0.16022 | -0.32043 | -0.24719 | -0.16937 | -0.11902 | 123.8342 | 123.9899 | 62.2009 | -123.8068 | 123.7656 | 123.8068 | 62.1552 | -124.0036
12.1406 | 123.9578 | -62.0224 | 61.8805 | -0.00091566 | 0.0057892 | 0.065962 | 0.0065347 | 0.065328 | -0.0015723 | -0.0022643 | -0.016098 | -0.004563 | 0.066422 | 0.069769 | -0.0057873 | -0.0056888 | 61.9492 | -61.7523 | 0.17395 | -61.9858 | 61.7798 | -62.0178 | -61.9354 | -62.3337 | 0.13275 | -62.233 | 61.7157 | 61.7477 | -61.9171 | -62.0911 | 0.004578 | 0.086975 | -0.10071 | 0.27008 | 0.036621 | -0.050354 | 0.068665 | 0.10529 | -0.068664 | -0.16479 | -0.31128 | -0.21057 | -0.14191 | -0.13275 | 123.8022 | 123.9716 | 62.1963 | -123.8159 | 123.7381 | 123.7701 | 62.1552 | -123.9716
13.875 | 123.967 | -62.0361 | 61.8851 | -0.00091566 | 0.008139 | 0.065322 | 0.0069621 | 0.068319 | -0.0015723 | -0.0029053 | -0.016098 | -0.0039222 | 0.065995 | 0.071051 | -0.0068553 | -0.007825 | 61.9354 | -61.7615 | 0.16022 | -61.9812 | 61.7615 | -62.027 | -61.9354 | -62.3291 | 0.13733 | -62.2284 | 61.7111 | 61.7432 | -61.8896 | -62.0956 | 0.009155 | 0.10071 | -0.1236 | 0.27466 | 0.054932 | -0.045776 | 0.050354 | 0.14648 | -0.059509 | -0.17395 | -0.29297 | -0.19226 | -0.13275 | -0.14191 | 123.7976 | 123.9716 | 62.1964 | -123.8205 | 123.7473 | 123.7793 | 62.1735 | -123.9807
15.5469 | 123.9899 | -62.0132 | 61.8988 | -0.0085447 | 0.0032258 | 0.069594 | 0.0041849 | 0.068746 | -0.0015723 | -0.0048279 | -0.00083936 | -0.004563 | 0.065354 | 0.068915 | -0.0042919 | -0.0065432 | 61.908 | -61.7981 | 0.045776 | -62.0178 | 61.7981 | -62.0132 | -61.9492 | -62.3703 | 0.032043 | -62.2742 | 61.7065 | 61.7661 | -61.9171 | -62.0911 | 0 | 0.064087 | -0.10071 | 0.21515 | -0.004577 | -0.068664 | 0.009155 | 0.096131 | -0.077819 | -0.19226 | -0.35706 | -0.26093 | -0.18311 | -0.13275 | 123.8113 | 123.9212 | 62.059 | -123.848 | 123.7198 | 123.7793 | 62.0453 | -123.9899
17.2969 | 123.9853 | -62.0316 | 61.9034 | -0.00091566 | 0.0062164 | 0.067244 | 0.0029031 | 0.066823 | -0.0019995 | -0.0029053 | -0.0084684 | -0.0056312 | 0.068558 | 0.06806 | -0.0045055 | -0.0071842 | 61.9171 | -61.8073 | 0.027466 | -62.0041 | 61.7706 | -62.0224 | -61.9308 | -62.3566 | 0.054932 | -62.2604 | 61.7065 | 61.7203 | -61.8988 | -62.1002 | 0.009155 | 0.10071 | -0.13275 | 0.2243 | 0.027466 | -0.073242 | 0.013733 | 0.13275 | -0.068665 | -0.19684 | -0.32501 | -0.22888 | -0.16022 | -0.18311 | 123.8022 | 123.9487 | 62.059 | -123.8342 | 123.7381 | 123.7518 | 62.0865 | -124.0036
18.9688 | 124.0997 | -62.0132 | 61.7981 | -0.016174 | 0.0051484 | 0.065962 | 0.0050393 | 0.065969 | 0.0048365 | -0.0016235 | 0.0067901 | 0.0007776 | 0.06514 | 0.071478 | -0.00044673 | -0.0082522 | 61.8622 | -61.8851 | 0.082397 | -62.0499 | 61.7798 | -62.0682 | -61.9995 | -62.3886 | 0.068665 | -62.352 | 61.702 | 61.7203 | -61.972 | -62.1368 | -0.054931 | 0.013733 | -0.018311 | 0.12817 | -0.036621 | -0.050354 | 0.064087 | 0.041199 | -0.1236 | -0.096131 | -0.37537 | -0.33875 | -0.21515 | -0.07782 | 123.793 | 123.8754 | 62.0956 | -123.7976 | 123.7152 | 123.7335 | 62.0819 | -123.9349
20.7188 | 123.9853 | -62.0132 | 61.8805 | -0.00091566 | 0.003653 | 0.06938 | 0.0058939 | 0.067464 | -0.0024267 | -0.0039733 | -0.0084684 | -0.0043494 | 0.063858 | 0.070196 | -0.0019419 | -0.0056888 | 61.9812 | -61.6882 | 0.16479 | -61.9583 | 61.7661 | -62.0041 | -61.9263 | -62.2879 | 0.15564 | -62.1918 | 61.6974 | 61.7157 | -61.853 | -62.0819 | 0.009156 | 0.086975 | -0.11444 | 0.32501 | 0.054932 | -0.032043 | 0.10071 | 0.16022 | -0.068664 | -0.18311 | -0.27466 | -0.17853 | -0.10986 | -0.16479 | 123.7793 | 123.9944 | 62.178 | -123.8068 | 123.7106 | 123.7289 | 62.1689 | -123.9624
22.4531 | 123.9761 | -62.0178 | 61.853 | -0.0085447 | 0.0077118 | 0.06938 | 0.0058939 | 0.069387 | -0.0030677 | -0.0018371 | -0.0084684 | -0.0064856 | 0.067276 | 0.069769 | -0.0040783 | -0.0069706 | 61.9629 | -61.6974 | 0.16937 | -61.9629 | 61.7844 | -62.0178 | -61.8942 | -62.2971 | 0.17853 | -62.1735 | 61.6882 | 61.7294 | -61.8988 | -62.0819 | 0 | 0.1236 | -0.068664 | 0.32043 | 0.054931 | -0.068665 | 0.10986 | 0.11902 | -0.064087 | -0.16479 | -0.27924 | -0.15564 | -0.091553 | -0.1236 | 123.8022 | 123.9807 | 62.1872 | -123.7473 | 123.7061 | 123.7473 | 62.1964 | -123.9349
24.1875 | 123.9578 | -62.0361 | 61.8668 | 0.0067138 | 0.0015168 | 0.068526 | 0.0029031 | 0.068746 | -0.00029051 | -0.0018371 | 0.0067901 | -0.0052038 | 0.064713 | 0.072333 | -0.0045055 | -0.0054752 | 61.9492 | -61.7294 | 0.16022 | -61.9629 | 61.7432 | -62.0407 | -61.9263 | -62.3199 | 0.14191 | -62.2375 | 61.6928 | 61.7249 | -61.908 | -62.1094 | -0.004577 | 0.10986 | -0.1236 | 0.3067 | 0.073242 | -0.036621 | 0.082398 | 0.12817 | -0.073242 | -0.17395 | -0.28381 | -0.20142 | -0.12817 | -0.14191 | 123.7793 | 123.9853 | 62.1964 | -123.793 | 123.7289 | 123.761 | 62.178 | -123.9761
25.9219 | 124.0265 | -62.0407 | 61.8164 | -0.00091566 | 0.0074982 | 0.065535 | 0.0056803 | 0.068319 | 0.00099129 | -0.0020507 | -0.0084684 | -0.0019996 | 0.066636 | 0.071905 | -0.0047191 | -0.0059024 | 61.853 | -61.8805 | 0.07782 | -62.0682 | 61.7889 | -62.0865 | -61.9766 | -62.4207 | 0.036621 | -62.3657 | 61.7294 | 61.7523 | -61.9537 | -62.0865 | -0.045777 | 0.064086 | -0.027466 | 0.16022 | -0.027466 | -0.091552 | 0.036621 | 0.086975 | -0.045777 | -0.086975 | -0.37994 | -0.32501 | -0.27924 | -0.064087 | 123.8296 | 123.8937 | 62.1185 | -123.793 | 123.7701 | 123.793 | 62.0773 | -123.9029
27.5938 | 123.9899 | -62.0087 | 61.8988 | -0.00091566 | 0.0047212 | 0.068312 | 0.0058939 | 0.065755 | -0.0019995 | -0.0037597 | -0.00083936 | -0.0052038 | 0.065354 | 0.069556 | -0.0051463 | -0.006116 | 61.8896 | -61.7935 | 0.018311 | -62.0041 | 61.7889 | -62.0132 | -61.9263 | -62.3703 | 0.050354 | -62.2513 | 61.702 | 61.7386 | -61.8759 | -62.0956 | -0.004578 | 0.082397 | -0.10986 | 0.21515 | 0.004578 | -0.077819 | -0.009156 | 0.13275 | -0.086975 | -0.19684 | -0.36163 | -0.24262 | -0.15564 | -0.16022 | 123.7976 | 123.8983 | 62.027 | -123.8251 | 123.7106 | 123.7473 | 62.059 | -123.9944
29.3438 | 124.0402 | -62.0361 | 61.7889 | -0.00091566 | 0.011771 | 0.063826 | 0.0058939 | 0.06661 | 0.0050501 | -0.0026917 | -0.00083936 | -0.0005042 | 0.066208 | 0.072333 | -0.0015147 | -0.007825 | 61.8118 | -61.9354 | -0.009155 | -62.0911 | 61.7798 | -62.0911 | -62.0178 | -62.4481 | -0.027466 | -62.4298 | 61.702 | 61.7111 | -61.9812 | -62.1735 | -0.054931 | 0.018311 | -0.009155 | 0.10071 | -0.054931 | -0.073242 | 0.022889 | 0.054932 | -0.13733 | -0.086975 | -0.41199 | -0.39368 | -0.25635 | -0.077819 | 123.8159 | 123.848 | 62.027 | -123.8068 | 123.7381 | 123.7473 | 62.0087 | -123.9624
31.0781 | 124.0219 | -62.0544 | 61.7844 | 0.0067138 | 0.010062 | 0.062758 | 0.0035441 | 0.06661 | 0.0016321 | 0.0011535 | -0.0084684 | -0.0009314 | 0.065567 | 0.072974 | -0.0010875 | -0.006116 | 61.8073 | -61.9125 | 0.004578 | -62.114 | 61.7523 | -62.114 | -62.0178 | -62.4344 | 0.004578 | -62.4069 | 61.6653 | 61.6882 | -61.972 | -62.178 | -0.05951 | 0.036621 | -0.032044 | 0.14191 | -0.05951 | -0.096131 | 0.022888 | 0.082397 | -0.1236 | -0.11902 | -0.37994 | -0.35248 | -0.22888 | -0.096131 | 123.8068 | 123.8617 | 62.059 | -123.8022 | 123.7198 | 123.7427 | 62.059 | -123.9624
32.8281 | 124.0723 | -62.0041 | 61.7615 | -0.0085447 | 0.0096344 | 0.06404 | 0.0061075 | 0.067892 | 0.00099129 | -0.0016235 | -0.00083936 | -0.0019996 | 0.068344 | 0.071051 | -0.0030101 | -0.0046206 | 61.8484 | -61.8851 | 0.07782 | -62.0407 | 61.7569 | -62.0636 | -61.9904 | -62.384 | 0.07782 | -62.3291 | 61.6837 | 61.7386 | -61.9675 | -62.1277 | -0.05951 | 0.013733 | -0.004578 | 0.11902 | -0.036621 | -0.050354 | 0.086975 | 0.036621 | -0.1236 | -0.07782 | -0.37994 | -0.32501 | -0.20142 | -0.022889 | 123.761 | 123.8525 | 62.0819 | -123.7518 | 123.6877 | 123.7427 | 62.0819 | -123.8892
34.5156 | 123.9258 | -62.0087 | 61.8439 | -0.0085447 | 0.0085664 | 0.067458 | 0.0052531 | 0.068746 | -0.0024267 | -0.0016235 | -0.00083936 | -0.002854 | 0.066849 | 0.07041 | -0.0040783 | -0.0052616 | 61.9217 | -61.7386 | 0.15564 | -61.9583 | 61.7432 | -62.0453 | -61.9171 | -62.3703 | 0.10986 | -62.2787 | 61.6837 | 61.7752 | -61.9125 | -62.0728 | -0.036621 | 0.091553 | -0.10071 | 0.27008 | 0.050354 | -0.041199 | 0.07782 | 0.09613 | -0.064087 | -0.16022 | -0.36163 | -0.27008 | -0.20599 | -0.068664 | 123.7518 | 123.9304 | 62.1643 | -123.761 | 123.6923 | 123.7839 | 62.1185 | -123.9166
36.2656 | 124.0036 | -62.0041 | 61.7844 | 0.0067138 | 0.0079254 | 0.067031 | 0.0052531 | 0.068105 | -0.0011451 | -0.0024779 | -0.00083936 | -0.0022132 | 0.065781 | 0.071692 | -0.0032237 | -0.0054752 | 61.8393 | -61.8576 | 0.054932 | -62.0407 | 61.7798 | -62.0682 | -61.9583 | -62.439 | 0.045776 | -62.3383 | 61.7249 | 61.7523 | -61.9308 | -62.1185 | -0.064087 | 0.045776 | -0.004578 | 0.14648 | -0.036621 | -0.082397 | 0.054931 | 0.073242 | -0.11444 | -0.059509 | -0.43488 | -0.33417 | -0.21973 | -0.032044 | 123.7839 | 123.8434 | 62.059 | -123.7427 | 123.7289 | 123.7564 | 62.0499 | -123.9029
38 | 123.9807 | -61.9858 | 61.8851 | -0.00091566 | 0.0060028 | 0.06874 | 0.0039713 | 0.067892 | -0.0066993 | -0.0039733 | -0.00083936 | -0.0066992 | 0.066208 | 0.067633 | -0.0036509 | -0.0029116 | 61.8851 | -61.7889 | 0.027466 | -61.9995 | 61.7569 | -61.9949 | -61.9217 | -62.3749 | 0.041199 | -62.2467 | 61.6882 | 61.7294 | -61.8851 | -62.0819 | -0.009155 | 0.064087 | -0.12817 | 0.19684 | -0.013733 | -0.07782 | 0 | 0.10071 | -0.09613 | -0.19684 | -0.3891 | -0.26093 | -0.16479 | -0.15564 | 123.7427 | 123.8709 | 62.0132 | -123.8068 | 123.674 | 123.7152 | 62.027 | -123.967
39.6719 | 123.9532 | -62.0087 | 61.8851 | -0.0085447 | 0.0049348 | 0.065322 | 0.0048257 | 0.067678 | -0.0024267 | -0.0041869 | -0.00083936 | -0.0047766 | 0.067063 | 0.069769 | -0.0034373 | -0.004407 | 61.8988 | -61.7798 | 0.027466 | -62.0041 | 61.7386 | -62.0132 | -61.9125 | -62.3566 | 0.050354 | -62.2238 | 61.6882 | 61.7432 | -61.8668 | -62.0682 | -0.004578 | 0.09613 | -0.14649 | 0.22888 | 0.004578 | -0.091552 | 0.013733 | 0.14191 | -0.059509 | -0.19684 | -0.3479 | -0.21515 | -0.15564 | -0.14191 | 123.7473 | 123.9075 | 62.0361 | -123.7976 | 123.6969 | 123.7518 | 62.059 | -123.9532
41.4062 | 123.967 | -62.0453 | 61.8393 | -0.00091566 | 0.0096344 | 0.06639 | 0.0093119 | 0.06661 | 0.00013669 | -0.0037597 | -0.00083936 | -0.0034948 | 0.068131 | 0.069983 | -0.0034373 | -0.0067568 | 61.8256 | -61.8622 | 0.07782 | -62.0499 | 61.7935 | -62.0544 | -61.9537 | -62.4161 | 0.036621 | -62.3245 | 61.702 | 61.7523 | -61.94 | -62.1231 | -0.009155 | 0.091553 | -0.045776 | 0.1831 | -0.004578 | -0.096131 | -0.013732 | 0.10529 | -0.07782 | -0.13733 | -0.37079 | -0.27924 | -0.20142 | -0.086975 | 123.8388 | 123.8708 | 62.1231 | -123.793 | 123.7473 | 123.7976 | 62.0819 | -123.9624
43.1406 | 123.912 | -62.0087 | 61.853 | -0.00091566 | 0.0079254 | 0.065535 | 0.0033305 | 0.067678 | 0.0016321 | -0.0022643 | -0.0084684 | -0.0043494 | 0.065567 | 0.069556 | -0.0032237 | -0.0067568 | 61.9263 | -61.7432 | 0.16937 | -61.9537 | 61.7432 | -62.0132 | -61.9217 | -62.3245 | 0.14191 | -62.2147 | 61.7111 | 61.7065 | -61.8851 | -62.0865 | -0.004578 | 0.086975 | -0.10986 | 0.2655 | 0.054932 | -0.032043 | 0.073243 | 0.1236 | -0.07782 | -0.14191 | -0.31586 | -0.20599 | -0.12817 | -0.14648 | 123.7518 | 123.9349 | 62.178 | -123.7747 | 123.7198 | 123.7152 | 62.1506 | -123.9395
44.9062 | 123.9487 | -62.0224 | 61.8713 | 0.0067138 | 0.003653 | 0.066603 | 0.0061075 | 0.06896 | -0.0017859 | -0.0037597 | 0.0067901 | -0.004563 | 0.065567 | 0.071051 | -0.0023693 | -0.0069706 | 61.9034 | -61.7569 | 0.054932 | -61.9904 | 61.734 | -62.0224 | -61.8988 | -62.3474 | 0.068665 | -62.2467 | 61.6562 | 61.7157 | -61.8805 | -62.0636 | 0 | 0.1236 | -0.13733 | 0.2655 | 0.032044 | -0.091552 | 0.032043 | 0.14191 | -0.041199 | -0.21515 | -0.32501 | -0.2243 | -0.1831 | -0.15564 | 123.7564 | 123.9258 | 62.0773 | -123.7701 | 123.6786 | 123.7381 | 62.0911 | -123.9349
46.5625 | 123.9944 | -62.0361 | 61.7615 | -0.00091566 | 0.0094208 | 0.066603 | 0.0014079 | 0.068105 | 0.0035547 | -0.0024779 | -0.016098 | 0.0001368 | 0.067063 | 0.072119 | -1.9327e-05 | -0.0069706 | 61.821 | -61.908 | 0.032043 | -62.0911 | 61.7569 | -62.0956 | -61.9995 | -62.4298 | 0.004578 | -62.384 | 61.6653 | 61.7065 | -61.9583 | -62.1552 | -0.059509 | 0.036621 | -0.004578 | 0.12817 | -0.054931 | -0.091552 | 0.059509 | 0.07782 | -0.11902 | -0.096131 | -0.39368 | -0.3479 | -0.22888 | -0.054932 | 123.793 | 123.8571 | 62.0682 | -123.761 | 123.7015 | 123.7427 | 62.0407 | -123.9166
48.2969 | 124.0494 | -62.0178 | 61.7661 | -0.016174 | 0.0057892 | 0.067458 | 0.0039713 | 0.065542 | -0.00093131 | -0.00076912 | -0.0084684 | 0.0009912 | 0.065995 | 0.071692 | -0.00023313 | -0.0069706 | 61.8027 | -61.94 | -0.041199 | -62.0911 | 61.7386 | -62.0865 | -62.0041 | -62.4573 | -0.036621 | -62.3886 | 61.647 | 61.7294 | -61.9492 | -62.1414 | -0.068665 | 0.013733 | -0.027466 | 0.07782 | -0.073242 | -0.086975 | 0.036621 | 0.068664 | -0.1236 | -0.11902 | -0.43945 | -0.37079 | -0.24719 | -0.036621 | 123.7564 | 123.8205 | 61.9766 | -123.7701 | 123.6649 | 123.7473 | 61.9812 | -123.9075
49.9688 | 124.0128 | -62.0132 | 61.7386 | -0.00091566 | 0.007071 | 0.067031 | 0.0046121 | 0.070028 | 0.00099129 | 0.00029908 | -0.0084684 | -0.0015722 | 0.06749 | 0.070624 | -0.0017283 | -0.0037662 | 61.8622 | -61.8439 | 0.082397 | -62.0316 | 61.7157 | -62.0819 | -61.9812 | -62.3611 | 0.10071 | -62.3337 | 61.6379 | 61.7111 | -61.9537 | -62.1277 | -0.068664 | 0.032044 | -0.022888 | 0.16937 | -0.01831 | -0.050354 | 0.1236 | 0.05951 | -0.11444 | -0.10071 | -0.3479 | -0.32043 | -0.20599 | -0.027465 | 123.7289 | 123.8754 | 62.0956 | -123.7198 | 123.6511 | 123.7244 | 62.114 | -123.8663
51.7344 | 123.9899 | -61.9949 | 61.8027 | -0.00091566 | 0.0038666 | 0.067885 | 0.00012606 | 0.06426 | -0.00029051 | 0.0013673 | -0.0084684 | -0.0047766 | 0.064713 | 0.069983 | -0.0032237 | -0.005048 | 61.9034 | -61.7615 | 0.064087 | -61.972 | 61.7065 | -62.0316 | -61.9354 | -62.3108 | 0.10529 | -62.2147 | 61.6241 | 61.6837 | -61.908 | -62.0728 | -0.036621 | 0.059509 | -0.09613 | 0.23346 | 0.022888 | -0.036621 | 0.10071 | 0.086975 | -0.07782 | -0.17853 | -0.31586 | -0.21973 | -0.14191 | -0.11902 | 123.7015 | 123.8983 | 62.059 | -123.7381 | 123.6191 | 123.6786 | 62.1002 | -123.8754
53.6719 | 123.9212 | -61.9949 | 61.8576 | -0.0085447 | 0.0047212 | 0.070449 | 0.0043985 | 0.067464 | -0.0054175 | -0.0024779 | 0.0067901 | -0.0039222 | 0.064072 | 0.068487 | -0.0045055 | -0.0037662 | 61.8668 | -61.7935 | 0.032043 | -61.9766 | 61.7615 | -61.9812 | -61.8759 | -62.352 | 0.032043 | -62.233 | 61.6745 | 61.7615 | -61.8759 | -62.0453 | 0.013733 | 0.11902 | -0.09613 | 0.20142 | 0.01831 | -0.10071 | 0.009155 | 0.11902 | -0.050354 | -0.1831 | -0.35706 | -0.23804 | -0.18768 | -0.09613 | 123.7564 | 123.8617 | 62.027 | -123.7335 | 123.6694 | 123.7564 | 62.027 | -123.9029
55.3594 | 124.0082 | -62.0132 | 61.7752 | -0.00091566 | 0.010916 | 0.064894 | 0.0050393 | 0.06661 | 0.0037683 | -0.00055532 | -0.00083936 | -7.6996e-05 | 0.066422 | 0.067633 | -0.00087393 | -0.0065432 | 61.8622 | -61.853 | 0.086975 | -62.027 | 61.7294 | -62.0544 | -61.9583 | -62.3978 | 0.054932 | -62.3428 | 61.6516 | 61.6928 | -61.9675 | -62.1552 | -0.041198 | 0.054932 | -0.045777 | 0.16022 | -0.013733 | -0.068665 | 0.086975 | 0.045777 | -0.14191 | -0.1236 | -0.38452 | -0.32959 | -0.18768 | -0.082398 | 123.7427 | 123.8754 | 62.1002 | -123.7335 | 123.6649 | 123.7061 | 62.0682 | -123.9304
57.0312 | 123.9578 | -61.9812 | 61.853 | -0.0085447 | 0.0066438 | 0.066603 | 0.0071757 | 0.067464 | -0.0054175 | -0.0037597 | -0.00083936 | -0.0064856 | 0.066849 | 0.068701 | -0.0053599 | -0.0031254 | 61.94 | -61.7065 | 0.11902 | -61.9308 | 61.7294 | -61.9766 | -61.8805 | -62.2787 | 0.15106 | -62.1552 | 61.647 | 61.702 | -61.8896 | -62.059 | 0.004577 | 0.10071 | -0.1236 | 0.27466 | 0.050354 | -0.050354 | 0.086975 | 0.091553 | -0.07782 | -0.20599 | -0.29755 | -0.17395 | -0.09613 | -0.15106 | 123.7106 | 123.9212 | 62.1002 | -123.7335 | 123.6282 | 123.6832 | 62.1323 | -123.912
58.6875 | 123.9578 | -61.9904 | 61.853 | -0.00091566 | 0.0038666 | 0.067458 | 0.0056803 | 0.067037 | -0.0034949 | -0.0050415 | 0.0067901 | -0.0049902 | 0.065781 | 0.07041 | -0.0040783 | -0.006116 | 61.9446 | -61.7111 | 0.1236 | -61.9308 | 61.7706 | -61.9354 | -61.8851 | -62.2879 | 0.12817 | -62.1643 | 61.6745 | 61.7065 | -61.8576 | -62.0544 | 0.054931 | 0.10528 | -0.082397 | 0.27923 | 0.059509 | -0.045776 | 0.091553 | 0.13275 | -0.064087 | -0.17853 | -0.29755 | -0.17395 | -0.10986 | -0.14648 | 123.761 | 123.9349 | 62.114 | -123.7381 | 123.6649 | 123.6969 | 62.1185 | -123.9075
60.3438 | 123.9716 | -62.0178 | 61.7798 | -0.0085447 | 0.012625 | 0.06639 | 0.0084573 | 0.064687 | 0.0018457 | -0.0037597 | -0.00083936 | -0.0005042 | 0.065781 | 0.07041 | -0.0027965 | -0.0073978 | 61.8301 | -61.8805 | 0.073242 | -62.027 | 61.7615 | -62.0453 | -61.9629 | -62.4023 | 0.036621 | -62.3154 | 61.7249 | 61.7477 | -61.9125 | -62.1094 | -0.027466 | 0.054931 | -0.01831 | 0.13733 | -0.009156 | -0.064087 | 0.050354 | 0.10529 | -0.091553 | -0.054931 | -0.38452 | -0.29755 | -0.20599 | -0.032043 | 123.7793 | 123.848 | 62.0911 | -123.7427 | 123.7427 | 123.7656 | 62.0544 | -123.8892
62.0156 | 123.9487 | -61.9858 | 61.8439 | -0.016174 | 0.0051484 | 0.066603 | 0.0050393 | 0.068746 | -0.0034949 | -0.0048279 | -0.00083936 | -0.004563 | 0.06749 | 0.071051 | -0.0042919 | -0.004407 | 61.8988 | -61.7477 | 0.07782 | -61.9446 | 61.7432 | -61.9812 | -61.8896 | -62.2742 | 0.10986 | -62.1643 | 61.6791 | 61.7523 | -61.8393 | -62.0316 | 0.004578 | 0.096131 | -0.10071 | 0.23804 | 0.041199 | -0.054932 | 0.054932 | 0.14648 | -0.045776 | -0.16479 | -0.28839 | -0.17853 | -0.13275 | -0.091553 | 123.7289 | 123.8846 | 62.0636 | -123.7335 | 123.6649 | 123.7381 | 62.0956 | -123.8754
64.0469 | 124.0448 | -62.0087 | 61.7569 | 0.014343 | 0.010275 | 0.065322 | 0.0031167 | 0.066823 | 0.0031275 | -0.0033325 | 0.0067901 | -7.6996e-05 | 0.067704 | 0.071051 | -0.0015147 | -0.0073978 | 61.7981 | -61.94 | -0.032043 | -62.059 | 61.7294 | -62.0865 | -61.9904 | -62.4161 | -0.022888 | -62.3566 | 61.6425 | 61.7386 | -61.9446 | -62.1185 | -0.07782 | 0.018311 | -0.027466 | 0.068665 | -0.050354 | -0.068665 | 0.041199 | 0.064087 | -0.10986 | -0.11444 | -0.40741 | -0.3479 | -0.23804 | -0.018311 | 123.7381 | 123.8068 | 61.9766 | -123.7473 | 123.6511 | 123.7473 | 61.9858 | -123.8754
65.8438 | 124.0356 | -61.9904 | 61.7523 | -0.00091566 | 0.0051484 | 0.065322 | 0.00098046 | 0.065328 | 0.0012049 | -0.0020507 | -0.00083936 | -0.0002906 | 0.064499 | 0.070837 | 0.00019427 | -0.0065432 | 61.8347 | -61.8622 | 0.073242 | -62.0316 | 61.7569 | -62.0407 | -61.9629 | -62.3795 | 0.059509 | -62.3108 | 61.6791 | 61.7386 | -61.9263 | -62.1323 | -0.050354 | 0.027465 | 0.004578 | 0.12817 | -0.041199 | -0.068664 | 0.082398 | 0.064086 | -0.14191 | -0.073242 | -0.3891 | -0.32044 | -0.17853 | -0.013733 | 123.7473 | 123.8251 | 62.0636 | -123.7152 | 123.6694 | 123.7289 | 62.0499 | -123.8846
67.5156 | 124.0356 | -61.9995 | 61.7615 | -0.00091566 | 0.00643 | 0.066817 | 0.0033305 | 0.066183 | 0.0029139 | -0.0016235 | -0.00083936 | -0.0017858 | 0.064713 | 0.070624 | 0.00040787 | -0.0041934 | 61.7844 | -61.9125 | -0.041199 | -62.059 | 61.7386 | -62.059 | -61.972 | -62.4161 | -0.018311 | -62.3474 | 61.6516 | 61.7157 | -61.9308 | -62.1368 | -0.059509 | 0.027466 | -0.022889 | 0.086975 | -0.059509 | -0.086975 | 0.022888 | 0.068665 | -0.13733 | -0.10986 | -0.41656 | -0.3479 | -0.21057 | -0.045777 | 123.7381 | 123.7839 | 61.9583 | -123.7335 | 123.6511 | 123.7152 | 61.9812 | -123.8983
69.2031 | 124.0494 | -61.9904 | 61.7386 | -0.00091566 | 0.0077118 | 0.066176 | 0.0039713 | 0.06661 | 0.0024865 | -0.0016235 | 0.0067901 | -0.0015722 | 0.066636 | 0.07041 | -0.00066033 | -0.0052616 | 61.7661 | -61.908 | -0.064087 | -62.059 | 61.7386 | -62.0728 | -61.9949 | -62.4298 | 0 | -62.3657 | 61.6562 | 61.7111 | -61.9675 | -62.1414 | -0.082398 | -0.004578 | 0 | 0.082397 | -0.068665 | -0.064087 | 0.027466 | 0.022888 | -0.15106 | -0.082397 | -0.43945 | -0.37537 | -0.22431 | -0.027465 | 123.7289 | 123.7564 | 61.9263 | -123.7335 | 123.6465 | 123.7015 | 61.9904 | -123.88
70.8906 | 124.0219 | -61.9949 | 61.7523 | -0.0085447 | 0.0051484 | 0.068526 | 0.0050393 | 0.066823 | -0.00029051 | -0.0022643 | 0.0067901 | -0.0015722 | 0.065995 | 0.068701 | -0.00087393 | -0.0059024 | 61.8164 | -61.8622 | -0.027466 | -62.0316 | 61.7111 | -62.0407 | -61.9537 | -62.3657 | 0.041199 | -62.2604 | 61.6287 | 61.6699 | -61.9308 | -62.1231 | -0.045776 | 0.041199 | -0.041198 | 0.13275 | -0.036621 | -0.07782 | 0.064087 | 0.064087 | -0.12817 | -0.1236 | -0.37079 | -0.2655 | -0.13733 | -0.082397 | 123.7061 | 123.8113 | 61.9675 | -123.7061 | 123.6237 | 123.6649 | 62.0361 | -123.8754
72.5938 | 123.8892 | -61.9949 | 61.8347 | -0.00091566 | 0.010703 | 0.067885 | 0.0063211 | 0.070028 | -0.0054175 | -0.0016235 | -0.00083936 | -0.0043494 | 0.065781 | 0.07041 | -0.0062145 | -0.0012026 | 61.9171 | -61.702 | 0.16022 | -61.9263 | 61.6974 | -61.9583 | -61.8896 | -62.2925 | 0.15106 | -62.178 | 61.6516 | 61.734 | -61.8484 | -62.0499 | 0.036621 | 0.10529 | -0.13733 | 0.29297 | 0.068664 | -0.036622 | 0.082397 | 0.14648 | -0.054932 | -0.18311 | -0.29755 | -0.18311 | -0.12817 | -0.10071 | 123.6923 | 123.912 | 62.1552 | -123.7244 | 123.6465 | 123.7289 | 62.146 | -123.8846
74.3125 | 124.0128 | -61.9812 | 61.7432 | 0.014343 | 0.0089936 | 0.065108 | 0.0046121 | 0.065328 | 0.0022729 | -0.0022643 | -0.0084684 | -0.0015722 | 0.064713 | 0.07041 | -0.0010875 | -0.0067568 | 61.8393 | -61.8256 | 0.09613 | -62.0224 | 61.7249 | -62.0453 | -61.9629 | -62.3566 | 0.10529 | -62.2971 | 61.6608 | 61.702 | -61.9308 | -62.0956 | -0.064087 | 0.01831 | -0.01831 | 0.15564 | -0.041199 | -0.059509 | 0.09613 | 0.050354 | -0.11444 | -0.082397 | -0.37537 | -0.31586 | -0.20142 | -0.041199 | 123.7061 | 123.8205 | 62.0773 | -123.7061 | 123.642 | 123.6832 | 62.0865 | -123.8388
75.9688 | 124.0173 | -61.9858 | 61.7477 | -0.00091566 | 0.0085664 | 0.066817 | 0.0073893 | 0.068319 | 0.0022729 | -0.0022643 | -0.00083936 | -0.0026404 | 0.06749 | 0.070624 | -0.0032237 | -0.0048342 | 61.8164 | -61.8439 | 0.09613 | -62.0041 | 61.7386 | -62.0544 | -61.9537 | -62.3749 | 0.082397 | -62.2879 | 61.6699 | 61.7203 | -61.9354 | -62.114 | -0.068664 | 0.032044 | -0.009156 | 0.14191 | -0.01831 | -0.050354 | 0.068664 | 0.050354 | -0.12817 | -0.07782 | -0.3891 | -0.30212 | -0.17395 | -0.027466 | 123.7244 | 123.8022 | 62.0819 | -123.7015 | 123.6557 | 123.7061 | 62.0682 | -123.8617
77.625 | 123.999 | -61.9858 | 61.7386 | -0.00091566 | 0.00878 | 0.065749 | 0.0035441 | 0.068319 | 0.00056389 | -0.0016235 | -0.00083936 | -0.0041358 | 0.067063 | 0.070624 | -0.0027965 | -0.0063296 | 61.7889 | -61.8439 | 0.068665 | -62.0041 | 61.7432 | -62.027 | -61.9446 | -62.3978 | 0.073242 | -62.3062 | 61.6653 | 61.6974 | -61.9492 | -62.1002 | -0.041199 | 0.041199 | 0.004578 | 0.14191 | -0.01831 | -0.059509 | 0.050354 | 0.036621 | -0.11444 | -0.073242 | -0.41199 | -0.32043 | -0.20599 | -0.041198 | 123.7289 | 123.7747 | 62.0544 | -123.6832 | 123.6511 | 123.6832 | 62.059 | -123.8388
79.2812 | 124.0128 | -61.9766 | 61.7615 | -0.00091566 | 0.0096344 | 0.064467 | 0.0058939 | 0.069387 | -0.0015723 | -0.00098272 | -0.00083936 | -0.0034948 | 0.066849 | 0.070837 | -0.0045055 | -0.0037662 | 61.7935 | -61.8439 | 0.086975 | -61.9995 | 61.734 | -62.0499 | -61.9492 | -62.3749 | 0.082397 | -62.2879 | 61.6608 | 61.702 | -61.9171 | -62.1185 | -0.073242 | 0.027466 | -0.027466 | 0.13275 | -0.022888 | -0.050354 | 0.032043 | 0.05951 | -0.14191 | -0.10071 | -0.39825 | -0.31128 | -0.16937 | -0.05951 | 123.7106 | 123.7701 | 62.0636 | -123.7106 | 123.6374 | 123.6786 | 62.059 | -123.88
80.9375 | 123.999 | -61.9766 | 61.7523 | -0.00091566 | 0.0060028 | 0.067671 | 0.0024759 | 0.06661 | -0.0024267 | -0.0029053 | -0.0084684 | -0.0024268 | 0.063431 | 0.07041 | -0.0013011 | -0.0035526 | 61.8668 | -61.7477 | 0.050354 | -61.9675 | 61.6974 | -62.0178 | -61.9217 | -62.3108 | 0.07782 | -62.2147 | 61.615 | 61.6425 | -61.9034 | -62.0728 | -0.041198 | 0.054932 | -0.054931 | 0.22888 | 0.009156 | -0.045776 | 0.11444 | 0.073243 | -0.09613 | -0.13733 | -0.33417 | -0.23804 | -0.14191 | -0.10986 | 123.674 | 123.8434 | 62.027 | -123.674 | 123.5916 | 123.6191 | 62.0544 | -123.8251
82.625 | 123.9944 | -61.9858 | 61.7706 | -0.0085447 | 0.0051484 | 0.067458 | 0.0011941 | 0.067464 | 0.00077749 | -0.0024779 | -0.00083936 | -0.001145 | 0.066422 | 0.070624 | -0.0023693 | -0.0035526 | 61.7386 | -61.9125 | -0.054932 | -62.0728 | 61.7111 | -62.0636 | -61.9492 | -62.4435 | -0.004578 | -62.3474 | 61.6516 | 61.6837 | -61.9263 | -62.1231 | -0.07782 | 0.036621 | -0.059509 | 0.073242 | -0.086975 | -0.1236 | -0.032044 | 0.059509 | -0.13733 | -0.11902 | -0.45776 | -0.36163 | -0.2243 | -0.086975 | 123.6969 | 123.7244 | 61.9308 | -123.7198 | 123.6374 | 123.6694 | 61.9812 | -123.8937
84.2812 | 123.999 | -61.9675 | 61.7477 | -0.00091566 | 0.0068574 | 0.069808 | 0.0052531 | 0.064474 | -0.00071771 | -0.0020507 | -0.00083936 | -0.0019996 | 0.065781 | 0.071265 | 0.00019427 | -0.0039798 | 61.8439 | -61.7889 | 0.018311 | -62.0041 | 61.6745 | -62.027 | -61.9217 | -62.3245 | 0.091553 | -62.2238 | 61.5967 | 61.6516 | -61.8713 | -62.0499 | -0.05951 | 0.045776 | -0.073242 | 0.17853 | -0.036621 | -0.082397 | 0.09613 | 0.09613 | -0.082398 | -0.15106 | -0.35706 | -0.25635 | -0.17395 | -0.096131 | 123.642 | 123.8113 | 61.9858 | -123.6694 | 123.5641 | 123.6191 | 62.059 | -123.7976
85.9375 | 124.0219 | -61.9675 | 61.7386 | 0.0067138 | 0.0072846 | 0.06639 | 0.0011941 | 0.066823 | 0.00077749 | -0.0016235 | 0.0067901 | -0.0024268 | 0.065354 | 0.068487 | -0.0025829 | -0.0054752 | 61.7889 | -61.8668 | -0.036621 | -62.0407 | 61.7249 | -62.0178 | -61.9308 | -62.3703 | 0.022888 | -62.2879 | 61.615 | 61.6928 | -61.9171 | -62.1048 | -0.050354 | 0.036621 | -0.013732 | 0.10071 | -0.073242 | -0.10986 | 0.050354 | 0.050354 | -0.13733 | -0.1236 | -0.40283 | -0.32044 | -0.18311 | -0.045776 | 123.6923 | 123.7564 | 61.9308 | -123.6694 | 123.5825 | 123.6603 | 61.9904 | -123.8434
87.6094 | 123.8617 | -61.9766 | 61.821 | -0.0085447 | 0.0025848 | 0.069594 | 0.0050393 | 0.064901 | -0.0049903 | -0.0024779 | -0.0084684 | -0.0047766 | 0.066422 | 0.068487 | -0.0038647 | -0.0056888 | 61.853 | -61.7477 | 0.022888 | -61.9812 | 61.6837 | -61.9812 | -61.8622 | -62.3428 | 0.027466 | -62.2009 | 61.6562 | 61.7065 | -61.8759 | -62.0453 | -0.004577 | 0.11444 | -0.13733 | 0.22888 | -0.004577 | -0.11902 | 0.032043 | 0.10071 | -0.068664 | -0.1648 | -0.36621 | -0.2243 | -0.15564 | -0.11444 | 123.6603 | 123.8297 | 61.9995 | -123.6832 | 123.6328 | 123.6832 | 62.0041 | -123.8663
89.2656 | 123.88 | -61.9858 | 61.7889 | -0.0085447 | 0.010916 | 0.065962 | 0.0080301 | 0.066183 | 0.00013669 | -0.0029053 | -0.00083936 | -0.002854 | 0.065995 | 0.071265 | -0.0062145 | -0.0065432 | 61.8118 | -61.821 | 0.068665 | -62.0178 | 61.7523 | -62.0132 | -61.9308 | -62.4115 | 0.036621 | -62.2971 | 61.7065 | 61.7294 | -61.9034 | -62.0453 | -0.027466 | 0.054932 | -0.036621 | 0.16479 | -0.032043 | -0.086975 | 0.022889 | 0.082398 | -0.059509 | -0.082397 | -0.42572 | -0.31128 | -0.25177 | -0.059509 | 123.7381 | 123.7976 | 62.0544 | -123.7198 | 123.6923 | 123.7152 | 62.0224 | -123.8342
90.9375 | 123.9944 | -61.972 | 61.7615 | -0.0085447 | 0.0068574 | 0.066176 | 0.0048257 | 0.068532 | 0.0014185 | -0.0024779 | -0.00083936 | -0.0030676 | 0.065354 | 0.069556 | -0.00087393 | -0.0073978 | 61.8439 | -61.7844 | 0.018311 | -61.9766 | 61.6837 | -62.0132 | -61.9171 | -62.2971 | 0.068665 | -62.2147 | 61.6196 | 61.6425 | -61.8851 | -62.0773 | -0.041199 | 0.054932 | -0.07782 | 0.18768 | -0.004578 | -0.05951 | 0.082397 | 0.086975 | -0.10529 | -0.14191 | -0.32501 | -0.24262 | -0.13733 | -0.11902 | 123.6557 | 123.8159 | 61.9904 | -123.6786 | 123.5916 | 123.6145 | 62.0407 | -123.8388
92.6719 | 123.8663 | -61.9629 | 61.8393 | -0.00091566 | 0.00087576 | 0.070235 | 0.0037577 | 0.065328 | -0.0043493 | -0.0041869 | 0.0067901 | -0.0052038 | 0.064499 | 0.07041 | -0.0023693 | -0.0059024 | 61.8576 | -61.7386 | 0.018311 | -61.972 | 61.7157 | -61.972 | -61.8622 | -62.3474 | 0.045776 | -62.2009 | 61.6333 | 61.702 | -61.8164 | -62.059 | -0.009155 | 0.10071 | -0.1236 | 0.22431 | -0.009155 | -0.10986 | 0.018311 | 0.14648 | -0.09613 | -0.20599 | -0.38452 | -0.23804 | -0.14191 | -0.13733 | 123.6786 | 123.8205 | 61.9812 | -123.7015 | 123.5962 | 123.6649 | 62.0087 | -123.8983
94.3594 | 123.8846 | -61.9583 | 61.8484 | -0.00091566 | 0.005362 | 0.070449 | 0.0063211 | 0.065969 | -0.0043493 | -0.0037597 | -0.00083936 | -0.0054174 | 0.065995 | 0.067847 | -0.0032237 | -0.0071842 | 61.8484 | -61.7432 | 0.041199 | -61.9492 | 61.7432 | -61.9766 | -61.8805 | -62.3245 | 0.041199 | -62.2055 | 61.6516 | 61.7157 | -61.8484 | -62.0132 | -0.018311 | 0.07782 | -0.10529 | 0.21515 | 0.009155 | -0.068665 | 0 | 0.10986 | -0.054932 | -0.19684 | -0.36621 | -0.24719 | -0.19226 | -0.13275 | 123.7015 | 123.8068 | 61.9995 | -123.7289 | 123.6099 | 123.674 | 61.9995 | -123.8617
96.0312 | 123.9853 | -61.9675 | 61.7386 | -0.00091566 | 0.0083526 | 0.066603 | 0.0026895 | 0.069387 | 0.0027003 | -0.0041869 | -0.016098 | -0.0022132 | 0.067276 | 0.071692 | -0.0023693 | -0.0091068 | 61.8256 | -61.8301 | 0.07782 | -62.0087 | 61.734 | -62.0453 | -61.9446 | -62.3337 | 0.07782 | -62.2925 | 61.6562 | 61.6837 | -61.8942 | -62.0911 | -0.07782 | 0.022888 | -0.004577 | 0.13733 | -0.041199 | -0.064087 | 0.086976 | 0.073242 | -0.1236 | -0.082397 | -0.36621 | -0.32501 | -0.20142 | -0.054931 | 123.7015 | 123.793 | 62.0453 | -123.6832 | 123.6237 | 123.6511 | 62.0453 | -123.8297
97.7031 | 123.8663 | -61.9904 | 61.7844 | 0.0067138 | 0.0057892 | 0.06639 | 0.0024759 | 0.06896 | -0.0030677 | -0.0026917 | -0.0084684 | -0.0039222 | 0.067704 | 0.067419 | -0.0053599 | -0.0052616 | 61.8759 | -61.7249 | 0.041199 | -61.9675 | 61.6791 | -61.972 | -61.8942 | -62.2879 | 0.073242 | -62.1918 | 61.6058 | 61.6699 | -61.853 | -62.0316 | 0.01831 | 0.09613 | -0.10529 | 0.2655 | 0.022888 | -0.073242 | 0.091553 | 0.13733 | -0.041199 | -0.17853 | -0.29755 | -0.20142 | -0.16022 | -0.11444 | 123.6694 | 123.8663 | 62.0316 | -123.6786 | 123.5962 | 123.6603 | 62.0636 | -123.8159
99.3594 | 123.912 | -61.9858 | 61.7844 | -0.0085447 | 0.0049348 | 0.067458 | 0.0011941 | 0.065969 | -0.0017859 | -0.0024779 | -0.00083936 | -0.0030676 | 0.061722 | 0.070624 | -0.0015147 | -0.0059024 | 61.8942 | -61.7294 | 0.050354 | -61.9492 | 61.6653 | -61.9995 | -61.908 | -62.2696 | 0.086975 | -62.1918 | 61.5967 | 61.6608 | -61.8713 | -62.0407 | -0.013733 | 0.07782 | -0.11902 | 0.25635 | 0.036621 | -0.041199 | 0.10986 | 0.11444 | -0.054931 | -0.18768 | -0.28381 | -0.20599 | -0.15106 | -0.1236 | 123.6511 | 123.88 | 62.0361 | -123.6923 | 123.5825 | 123.6465 | 62.0728 | -123.8251
101.0312 | 123.88 | -61.9949 | 61.7706 | -0.00091566 | 0.007071 | 0.066603 | 0.0065347 | 0.065969 | -0.0022131 | -0.0050415 | -0.0084684 | 0.0003504 | 0.067704 | 0.070196 | -0.0038647 | -0.006116 | 61.7981 | -61.8301 | 0.059509 | -62.0224 | 61.7569 | -62.0132 | -61.9171 | -62.3795 | 0.050354 | -62.3016 | 61.6882 | 61.7294 | -61.9034 | -62.059 | -0.018311 | 0.07782 | -0.013733 | 0.16479 | -0.027466 | -0.10529 | 0.027466 | 0.091553 | -0.064087 | -0.082398 | -0.38452 | -0.3067 | -0.24262 | -0.041199 | 123.7518 | 123.793 | 62.0544 | -123.6877 | 123.6832 | 123.7244 | 62.0453 | -123.8297
102.7188 | 123.848 | -62.0041 | 61.821 | 0.0067138 | 0.0077118 | 0.065322 | 0.0067483 | 0.068319 | -0.0017859 | -0.0033325 | -0.0084684 | -0.0049902 | 0.067704 | 0.070624 | -0.0057873 | -0.0063296 | 61.8622 | -61.7661 | 0.12817 | -61.9492 | 61.734 | -61.9995 | -61.8805 | -62.3383 | 0.059509 | -62.2696 | 61.6608 | 61.7432 | -61.8713 | -62.059 | 0.004577 | 0.1236 | -0.086975 | 0.23804 | 0.054931 | -0.068665 | 0.041199 | 0.13275 | -0.054932 | -0.16022 | -0.33417 | -0.2655 | -0.21057 | -0.07782 | 123.7381 | 123.8663 | 62.1323 | -123.7015 | 123.6649 | 123.7473 | 62.0636 | -123.88
104.375 | 123.9029 | -61.972 | 61.7935 | -0.0085447 | 0.0092072 | 0.066603 | 0.0046121 | 0.067251 | -0.0022131 | -0.0039733 | -0.0084684 | -0.0030676 | 0.065995 | 0.070196 | -0.0051463 | -0.0071842 | 61.9217 | -61.647 | 0.15564 | -61.8988 | 61.6928 | -61.9583 | -61.8347 | -62.2192 | 0.14648 | -62.1277 | 61.615 | 61.702 | -61.8301 | -62.0041 | 0.013733 | 0.13733 | -0.10071 | 0.32501 | 0.073242 | -0.064087 | 0.12817 | 0.14191 | -0.032043 | -0.17853 | -0.24719 | -0.15564 | -0.1236 | -0.091553 | 123.6649 | 123.8937 | 62.1277 | -123.6282 | 123.587 | 123.674 | 62.1185 | -123.7976
106.0469 | 123.967 | -61.9629 | 61.7386 | 0.0067138 | 0.007071 | 0.066603 | 0.0035441 | 0.0696 | 0.0035547 | -0.0024779 | -0.00083936 | -0.0017858 | 0.065567 | 0.072546 | -0.0015147 | -0.0073978 | 61.7661 | -61.8622 | -0.054932 | -62.0361 | 61.7203 | -62.0407 | -61.9354 | -62.3932 | -0.013733 | -62.3154 | 61.6379 | 61.6837 | -61.9217 | -62.0956 | -0.077819 | 0.027466 | -0.01831 | 0.10071 | -0.073242 | -0.10071 | 0.027466 | 0.041199 | -0.13275 | -0.10071 | -0.4303 | -0.35248 | -0.21973 | -0.054931 | 123.6832 | 123.7289 | 61.908 | -123.674 | 123.6008 | 123.6465 | 61.9492 | -123.8342
107.7344 | 123.9578 | -61.9537 | 61.7386 | -0.0085447 | 0.0057892 | 0.065749 | -0.0011557 | 0.068319 | 0.00099129 | -0.0018371 | -0.00083936 | -0.001145 | 0.063858 | 0.072333 | -0.00087393 | -0.0054752 | 61.7523 | -61.8759 | -0.036621 | -62.0499 | 61.6928 | -62.059 | -61.9492 | -62.4023 | -0.018311 | -62.352 | 61.6333 | 61.6928 | -61.8988 | -62.1048 | -0.10529 | 0.004577 | -0.045776 | 0.077819 | -0.096131 | -0.10071 | 0.013733 | 0.054931 | -0.15106 | -0.10528 | -0.44861 | -0.39825 | -0.24719 | -0.045776 | 123.6465 | 123.7061 | 61.9171 | -123.6877 | 123.587 | 123.6465 | 61.9354 | -123.8434
109.4219 | 123.9487 | -61.9675 | 61.7386 | -0.016174 | 0.00878 | 0.070876 | 0.0058939 | 0.06896 | -7.6908e-05 | -0.0033325 | -0.00083936 | -0.0030676 | 0.066636 | 0.068915 | -0.0025829 | -0.0059024 | 61.7844 | -61.8439 | 0.086975 | -61.9766 | 61.7523 | -62.027 | -61.9354 | -62.3703 | 0.045776 | -62.2833 | 61.6562 | 61.702 | -61.9034 | -62.0865 | -0.05951 | 0.032043 | 0.013733 | 0.1236 | -0.009156 | -0.041199 | 0.045777 | 0.064087 | -0.11902 | -0.082397 | -0.40283 | -0.31586 | -0.19684 | -0.036621 | 123.7198 | 123.7518 | 62.0544 | -123.674 | 123.6237 | 123.6694 | 62.0132 | -123.8251
111.0781 | 123.9441 | -61.9812 | 61.7111 | 0.0067138 | 0.0094208 | 0.06639 | 0.0056803 | 0.067678 | 0.0027003 | -0.0031189 | -0.0084684 | -0.0022132 | 0.066636 | 0.071692 | -0.0017283 | -0.0054752 | 61.7294 | -61.908 | -0.045776 | -62.0499 | 61.7157 | -62.0407 | -61.9446 | -62.3978 | -0.018311 | -62.3428 | 61.6287 | 61.6882 | -61.9034 | -62.1048 | -0.059509 | 0.036621 | 0.004577 | 0.073242 | -0.068665 | -0.10529 | 0.01831 | 0.07782 | -0.1236 | -0.082398 | -0.41656 | -0.36163 | -0.23804 | -0.022889 | 123.6969 | 123.7106 | 61.9354 | -123.6557 | 123.6099 | 123.6694 | 61.9629 | -123.8159
112.8125 | 123.9075 | -61.9766 | 61.7111 | -0.00091566 | 0.00878 | 0.066817 | 0.0046121 | 0.06426 | -0.00050411 | -0.00076912 | 0.01442 | -0.0017858 | 0.066636 | 0.072119 | -0.00066033 | -0.0039798 | 61.7249 | -61.8713 | 0.004578 | -62.0361 | 61.702 | -62.0453 | -61.9537 | -62.3886 | 0.018311 | -62.3337 | 61.6379 | 61.647 | -61.908 | -62.1231 | -0.068664 | 0.022889 | -0.009156 | 0.10529 | -0.059509 | -0.082398 | 0.013733 | 0.068665 | -0.14648 | -0.073243 | -0.41199 | -0.35705 | -0.21057 | -0.064087 | 123.6786 | 123.7015 | 61.9812 | -123.6649 | 123.6145 | 123.6237 | 61.9949 | -123.8342
114.5312 | 123.912 | -61.9949 | 61.7249 | -0.00091566 | 0.0083526 | 0.063826 | 0.0048257 | 0.067892 | 0.0014185 | 0.00051268 | -0.00083936 | -0.0009314 | 0.067276 | 0.069342 | 0.00040787 | -0.0056888 | 61.7615 | -61.8393 | 0.045776 | -62.0316 | 61.6974 | -62.0224 | -61.9354 | -62.4023 | 0.022888 | -62.3337 | 61.6104 | 61.6516 | -61.908 | -62.0911 | -0.027466 | 0.059509 | -0.027466 | 0.15564 | -0.036621 | -0.09613 | 0.036621 | 0.086975 | -0.09613 | -0.11444 | -0.40741 | -0.33874 | -0.24261 | -0.073243 | 123.6923 | 123.7564 | 62.0407 | -123.6603 | 123.6053 | 123.6465 | 62.0178 | -123.8159
116.1875 | 123.9304 | -61.94 | 61.7523 | 0.0067138 | 0.010062 | 0.067885 | 0.0080301 | 0.066823 | -0.0019995 | -0.0037597 | -0.00083936 | -0.0015722 | 0.068344 | 0.071051 | -0.0057873 | -0.005048 | 61.7569 | -61.8256 | 0.068665 | -61.9812 | 61.734 | -62.0041 | -61.94 | -62.384 | 0.045776 | -62.2787 | 61.6653 | 61.7111 | -61.9125 | -62.0636 | -0.064087 | 0 | -0.01831 | 0.11444 | -0.041199 | -0.041199 | 0.004578 | 0.027465 | -0.1236 | -0.086975 | -0.44403 | -0.33875 | -0.21515 | -0.041198 | 123.674 | 123.6969 | 62.0087 | -123.6923 | 123.6053 | 123.6511 | 61.9858 | -123.8159
117.8906 | 123.9624 | -61.9537 | 61.7203 | 0.0067138 | 0.009848 | 0.064253 | 0.0041849 | 0.065542 | 0.00056389 | -0.0011963 | -0.0084684 | -0.0017858 | 0.067917 | 0.07276 | -0.0038647 | -0.0048342 | 61.7203 | -61.8622 | -0.054932 | -62.0361 | 61.6928 | -62.0316 | -61.9537 | -62.4207 | -0.018311 | -62.3108 | 61.6379 | 61.6653 | -61.9171 | -62.0682 | -0.07782 | 0 | -0.027466 | 0.091552 | -0.082398 | -0.082398 | 0 | 0.036621 | -0.11444 | -0.082398 | -0.46692 | -0.35706 | -0.24262 | -0.054932 | 123.6465 | 123.674 | 61.8988 | -123.674 | 123.5916 | 123.6191 | 61.9354 | -123.7885
119.6094 | 123.8525 | -61.9354 | 61.8073 | -0.016174 | 0.005362 | 0.068312 | 0.0056803 | 0.066396 | -0.0064855 | -0.0026917 | -0.00083936 | -0.0052038 | 0.066636 | 0.069983 | -0.0053599 | -0.0059024 | 61.7935 | -61.7477 | 0.013733 | -61.94 | 61.7065 | -61.9492 | -61.8347 | -62.3062 | 0.054932 | -62.178 | 61.6287 | 61.6837 | -61.8027 | -62.0316 | -0.013733 | 0.10071 | -0.10071 | 0.18768 | -0.004577 | -0.10529 | -0.013733 | 0.13275 | -0.09613 | -0.17853 | -0.37079 | -0.24262 | -0.14649 | -0.1236 | 123.642 | 123.7289 | 61.9492 | -123.642 | 123.5641 | 123.6191 | 61.9904 | -123.8388
121.3125 | 123.9395 | -61.9354 | 61.7157 | -0.00091566 | 0.007071 | 0.066176 | 0.0026895 | 0.067678 | -0.00029051 | -0.0020507 | -0.00083936 | -0.0022132 | 0.064286 | 0.071692 | 0.00019427 | -0.0093204 | 61.8484 | -61.7477 | 0.045776 | -61.94 | 61.6653 | -61.9858 | -61.8851 | -62.2742 | 0.082397 | -62.1918 | 61.5921 | 61.6653 | -61.8622 | -62.0361 | -0.050354 | 0.050354 | -0.050354 | 0.18768 | -0.004577 | -0.054931 | 0.13275 | 0.073242 | -0.10071 | -0.1236 | -0.33874 | -0.25635 | -0.15564 | -0.050354 | 123.6008 | 123.7839 | 61.9812 | -123.6008 | 123.5275 | 123.6008 | 62.0178 | -123.7518
122.9844 | 123.8663 | -61.9354 | 61.7752 | -0.0085447 | 0.0068574 | 0.068526 | 0.0067483 | 0.068105 | -0.0058447 | -0.0054687 | -0.00083936 | -0.0054174 | 0.067063 | 0.069342 | -0.0049327 | -0.0069706 | 61.8942 | -61.6608 | 0.15106 | -61.8805 | 61.6928 | -61.94 | -61.8164 | -62.233 | 0.15106 | -62.0956 | 61.6241 | 61.6928 | -61.8347 | -61.9995 | -0.004577 | 0.11902 | -0.082398 | 0.27466 | 0.054932 | -0.064087 | 0.11902 | 0.10071 | -0.064087 | -0.15106 | -0.29755 | -0.16022 | -0.09613 | -0.082398 | 123.6282 | 123.8297 | 62.0865 | -123.5916 | 123.5596 | 123.6282 | 62.0865 | -123.7747
124.6562 | 123.8205 | -61.9858 | 61.7661 | -0.016174 | 0.005362 | 0.067031 | 0.0056803 | 0.070028 | -0.0015723 | -0.0041869 | -0.00083936 | -0.0026404 | 0.065567 | 0.071905 | -0.0030101 | -0.0071842 | 61.8256 | -61.7661 | 0.11444 | -61.9675 | 61.7203 | -61.9675 | -61.8942 | -62.3611 | 0.041199 | -62.2467 | 61.6562 | 61.7249 | -61.8439 | -62.0544 | 0.018311 | 0.091553 | -0.045776 | 0.21973 | 0.018311 | -0.073242 | 0.05951 | 0.14191 | -0.068664 | -0.10986 | -0.37537 | -0.26093 | -0.19226 | -0.041198 | 123.7061 | 123.8113 | 62.1002 | -123.6603 | 123.642 | 123.7106 | 62.027 | -123.8205
126.3281 | 123.8342 | -61.9492 | 61.7935 | 0.0067138 | 0.008139 | 0.068953 | 0.0052531 | 0.067678 | -0.0026403 | -0.0039733 | 0.0067901 | -0.0060584 | 0.064286 | 0.069128 | -0.0049327 | -0.0046206 | 61.8484 | -61.734 | 0.027466 | -61.94 | 61.7111 | -61.9263 | -61.8576 | -62.3154 | 0.032043 | -62.1918 | 61.6104 | 61.6928 | -61.821 | -62.0132 | 0.022888 | 0.091553 | -0.082397 | 0.21515 | 0.009156 | -0.082397 | 0.054932 | 0.12817 | -0.064087 | -0.1831 | -0.36621 | -0.24261 | -0.17853 | -0.10071 | 123.6603 | 123.7976 | 61.9766 | -123.6511 | 123.5596 | 123.642 | 61.9812 | -123.8068
128 | 123.9349 | -61.9537 | 61.7065 | 0.0067138 | 0.011343 | 0.066176 | 0.0037577 | 0.065542 | 0.0031275 | -0.0048279 | -0.00083936 | 0.0001368 | 0.066422 | 0.072333 | -1.9327e-05 | -0.0084658 | 61.8073 | -61.7935 | 0.10529 | -61.9904 | 61.6974 | -62.0178 | -61.908 | -62.3154 | 0.10529 | -62.2513 | 61.6196 | 61.6562 | -61.9125 | -62.0819 | -0.064087 | 0.045776 | -0.009155 | 0.16022 | -0.036621 | -0.082397 | 0.10071 | 0.041198 | -0.12817 | -0.086975 | -0.36163 | -0.29755 | -0.16937 | -0.050354 | 123.6511 | 123.761 | 62.059 | -123.6145 | 123.5733 | 123.6099 | 62.059 | -123.7885
129.6719 | 123.8709 | -61.9217 | 61.7981 | -0.00091566 | 0.0042938 | 0.068526 | 0.0065347 | 0.063619 | -0.0041357 | -0.0029053 | -0.0084684 | -0.0052038 | 0.067276 | 0.068487 | -0.0049327 | -0.0071842 | 61.8256 | -61.7294 | 0.050354 | -61.9171 | 61.6974 | -61.9492 | -61.8439 | -62.265 | 0.082397 | -62.1414 | 61.6333 | 61.6745 | -61.8301 | -61.9812 | -0.027466 | 0.07782 | -0.10071 | 0.19226 | 0.004578 | -0.073242 | 0.027466 | 0.091553 | -0.059509 | -0.16479 | -0.34332 | -0.21973 | -0.16022 | -0.1236 | 123.6191 | 123.7473 | 61.972 | -123.642 | 123.555 | 123.5962 | 62.0041 | -123.7793
131.3438 | 123.9578 | -61.972 | 61.7294 | 0.0067138 | 0.009848 | 0.067031 | 0.0039713 | 0.063833 | 0.0037683 | -0.0016235 | -0.016098 | -0.0002906 | 0.066208 | 0.070837 | 0.00062147 | -0.0046206 | 61.7432 | -61.8805 | -0.064087 | -62.0178 | 61.7111 | -62.0132 | -61.9263 | -62.3749 | -0.022888 | -62.3199 | 61.6379 | 61.6745 | -61.9217 | -62.0956 | -0.041199 | 0.045776 | -0.01831 | 0.091553 | -0.045776 | -0.091552 | 0.013733 | 0.050354 | -0.1236 | -0.091553 | -0.40283 | -0.3479 | -0.2243 | -0.054931 | 123.6832 | 123.7152 | 61.908 | -123.6557 | 123.6099 | 123.6465 | 61.9492 | -123.8251
133.0156 | 123.8068 | -61.9446 | 61.7935 | -0.0085447 | 0.0068574 | 0.067244 | 0.0050393 | 0.065114 | -0.0043493 | -0.0033325 | -0.0084684 | -0.0054174 | 0.06514 | 0.06806 | -0.0045055 | -0.0046206 | 61.8073 | -61.7203 | 0.022888 | -61.9217 | 61.7157 | -61.9675 | -61.8668 | -62.3062 | 0.032043 | -62.178 | 61.6196 | 61.6745 | -61.8164 | -61.9995 | -0.022888 | 0.07782 | -0.07782 | 0.2243 | 0.022888 | -0.054932 | 0.013733 | 0.12817 | -0.054932 | -0.17395 | -0.36163 | -0.23346 | -0.17853 | -0.11902 | 123.6603 | 123.7518 | 61.9675 | -123.6603 | 123.5641 | 123.6191 | 61.9766 | -123.793
134.7188 | 123.9532 | -61.94 | 61.702 | -0.00091566 | 0.0057892 | 0.066603 | 0.0014079 | 0.067678 | 0.0029139 | -0.0024779 | -0.00083936 | -0.0026404 | 0.062149 | 0.070196 | -0.0015147 | -0.0067568 | 61.7844 | -61.7981 | -0.013733 | -61.9858 | 61.6928 | -61.9949 | -61.9263 | -62.3062 | 0.050354 | -62.2238 | 61.6058 | 61.6379 | -61.8576 | -62.0316 | -0.054932 | 0.013732 | -0.009155 | 0.14191 | -0.045777 | -0.059509 | 0.082398 | 0.082397 | -0.091553 | -0.09613 | -0.36621 | -0.28381 | -0.19226 | -0.064087 | 123.6328 | 123.7244 | 61.9263 | -123.6282 | 123.5458 | 123.5779 | 61.9904 | -123.7335
136.4219 | 123.8251 | -61.9629 | 61.7569 | -0.0085447 | 0.008139 | 0.066817 | 0.0050393 | 0.064901 | 0.00056389 | -0.0035461 | -0.00083936 | -0.0017858 | 0.067917 | 0.070196 | -0.00087393 | -0.005048 | 61.7523 | -61.7889 | 0.073242 | -61.9766 | 61.7157 | -61.9812 | -61.8988 | -62.352 | 0.050354 | -62.2696 | 61.6699 | 61.6882 | -61.8668 | -62.0544 | -0.01831 | 0.064087 | -0.041199 | 0.17395 | -0.013733 | -0.07782 | -0.004578 | 0.096131 | -0.091552 | -0.086975 | -0.3891 | -0.3067 | -0.21515 | -0.068665 | 123.6786 | 123.7152 | 62.0361 | -123.6557 | 123.6328 | 123.6511 | 62.0132 | -123.8113
138.1094 | 123.8937 | -61.9675 | 61.7111 | -0.016174 | 0.0068574 | 0.065749 | 0.0029031 | 0.066396 | 0.0039819 | -0.00076912 | -0.00083936 | -0.0015722 | 0.068344 | 0.069769 | -0.0015147 | -0.0046206 | 61.7569 | -61.821 | 0.041199 | -62.027 | 61.6745 | -62.0132 | -61.9354 | -62.3795 | 0.013733 | -62.3245 | 61.5967 | 61.6333 | -61.9171 | -62.0865 | -0.045777 | 0.032043 | -0.036621 | 0.14648 | -0.05951 | -0.091553 | 0.045776 | 0.050354 | -0.11902 | -0.11444 | -0.41199 | -0.35706 | -0.23804 | -0.07782 | 123.642 | 123.7244 | 62.0087 | -123.6465 | 123.5641 | 123.6008 | 61.9812 | -123.7976
139.8281 | 123.9304 | -61.9308 | 61.7111 | -0.0085447 | 0.00878 | 0.064894 | 0.0056803 | 0.066396 | 0.0014185 | -0.0020507 | -0.016098 | -0.0024268 | 0.065995 | 0.069769 | -0.0032237 | -0.0052616 | 61.7889 | -61.7981 | 0.091553 | -61.9492 | 61.6928 | -61.9995 | -61.9171 | -62.3291 | 0.086975 | -62.2559 | 61.6013 | 61.647 | -61.8988 | -62.0865 | -0.068665 | 0.013733 | -0.018311 | 0.13275 | -0.018311 | -0.032044 | 0.077819 | 0.032043 | -0.15564 | -0.10986 | -0.39825 | -0.32501 | -0.16937 | -0.064087 | 123.6237 | 123.7198 | 62.0224 | -123.6282 | 123.5321 | 123.5779 | 62.0178 | -123.7976
141.5 | 123.8663 | -61.9629 | 61.702 | -0.00091566 | 0.0074982 | 0.06639 | 0.0056803 | 0.065969 | 0.0016321 | -0.00076912 | -0.0084684 | -0.0009314 | 0.065567 | 0.071478 | 0.00040787 | -0.0065432 | 61.7111 | -61.8393 | -0.018311 | -62.0132 | 61.6653 | -62.0041 | -61.9446 | -62.3749 | 0.018311 | -62.3245 | 61.6104 | 61.6653 | -61.8988 | -62.1002 | -0.041198 | 0.018311 | -0.036621 | 0.1236 | -0.050354 | -0.068665 | 0.009156 | 0.064087 | -0.13733 | -0.091552 | -0.41199 | -0.36163 | -0.2243 | -0.036621 | 123.6282 | 123.674 | 61.9446 | -123.6465 | 123.5733 | 123.6282 | 61.9812 | -123.8022
143.1719 | 123.7976 | -61.9446 | 61.8164 | -0.016174 | 0.0027984 | 0.068953 | 0.0052531 | 0.067892 | -0.0062719 | -0.0031189 | -0.0084684 | -0.0058448 | 0.065567 | 0.067206 | -0.0034373 | -0.0056888 | 61.8576 | -61.6058 | 0.16937 | -61.8759 | 61.6837 | -61.9354 | -61.821 | -62.2284 | 0.16479 | -62.1231 | 61.6013 | 61.6653 | -61.8073 | -62.0041 | 0.009155 | 0.1236 | -0.13275 | 0.33875 | 0.068664 | -0.054932 | 0.041199 | 0.13733 | -0.059509 | -0.21515 | -0.28381 | -0.17853 | -0.11902 | -0.15106 | 123.6282 | 123.8022 | 62.114 | -123.6374 | 123.5458 | 123.6099 | 62.1094 | -123.8205
144.875 | 123.7976 | -61.9354 | 61.7935 | -0.016174 | 0.00878 | 0.068099 | 0.0076029 | 0.068532 | -0.0022131 | -0.0024779 | -0.0084684 | -0.0034948 | 0.065354 | 0.071478 | -0.0057873 | -0.0054752 | 61.8073 | -61.702 | 0.13275 | -61.9171 | 61.6882 | -61.972 | -61.8668 | -62.3199 | 0.086975 | -62.1918 | 61.6745 | 61.6882 | -61.8256 | -62.027 | -0.036621 | 0.068665 | -0.10529 | 0.23346 | 0.018311 | -0.050354 | 0.013733 | 0.10986 | -0.091553 | -0.11902 | -0.38452 | -0.25635 | -0.16479 | -0.10529 | 123.6237 | 123.7427 | 62.0682 | -123.6603 | 123.6099 | 123.6237 | 62.0224 | -123.8205
146.5625 | 123.8297 | -61.9034 | 61.7844 | -0.016174 | 0.0060028 | 0.067671 | 0.0050393 | 0.067464 | -0.0017859 | -0.0048279 | 0.01442 | -0.0058448 | 0.065567 | 0.066992 | -0.0045055 | -0.0063296 | 61.8896 | -61.6013 | 0.16937 | -61.8713 | 61.6791 | -61.9263 | -61.8301 | -62.2192 | 0.16022 | -62.1048 | 61.6287 | 61.6562 | -61.7935 | -61.9858 | -0.022889 | 0.073242 | -0.10529 | 0.30212 | 0.032043 | -0.041199 | 0.10529 | 0.10986 | -0.082398 | -0.15564 | -0.31586 | -0.20142 | -0.11902 | -0.12817 | 123.5825 | 123.793 | 62.0728 | -123.6145 | 123.5321 | 123.5596 | 62.0636 | -123.7701
148.25 | 123.9258 | -61.9537 | 61.6974 | -0.0085447 | 0.0077118 | 0.065535 | -8.7544e-05 | 0.064687 | 0.00056389 | -0.0026917 | -0.023727 | 0.0007776 | 0.066636 | 0.070624 | 0.00062147 | -0.007825 | 61.7569 | -61.8027 | -0.032043 | -61.9949 | 61.6882 | -62.0041 | -61.9034 | -62.3154 | 0.027466 | -62.2147 | 61.5875 | 61.615 | -61.853 | -62.0407 | -0.050354 | 0.050354 | -0.009156 | 0.15106 | -0.041199 | -0.091553 | 0.059509 | 0.10071 | -0.086975 | -0.10986 | -0.36163 | -0.26093 | -0.17395 | -0.082398 | 123.642 | 123.7106 | 61.9217 | -123.6008 | 123.5413 | 123.5687 | 61.9812 | -123.7381
149.9375 | 123.8754 | -61.9675 | 61.6745 | -0.0085447 | 0.011343 | 0.066817 | 0.0041849 | 0.06661 | 0.0037683 | -0.0024779 | -0.0084684 | -0.0013586 | 0.065567 | 0.071905 | 0.00083507 | -0.0063296 | 61.7935 | -61.7615 | 0.10529 | -61.9583 | 61.6928 | -62.0041 | -61.9125 | -62.3108 | 0.09613 | -62.2559 | 61.5921 | 61.6241 | -61.8622 | -62.0316 | -0.036621 | 0.054931 | 0.01831 | 0.20599 | 0.009155 | -0.045776 | 0.11902 | 0.10528 | -0.064087 | -0.082398 | -0.34332 | -0.28839 | -0.2243 | -0.050354 | 123.6603 | 123.761 | 62.0728 | -123.587 | 123.5596 | 123.5916 | 62.0636 | -123.7061
151.6562 | 123.7885 | -61.9171 | 61.7981 | -0.00091566 | 0.008139 | 0.064894 | 0.0080301 | 0.069173 | -0.0041357 | -0.0046143 | -0.0084684 | -0.0064856 | 0.064499 | 0.070837 | -0.0055735 | -0.0046206 | 61.8439 | -61.647 | 0.16479 | -61.8713 | 61.6653 | -61.9446 | -61.8622 | -62.2513 | 0.15106 | -62.1277 | 61.6104 | 61.6562 | -61.8027 | -62.0041 | -0.027466 | 0.054931 | -0.13275 | 0.27008 | 0.045776 | -0.009155 | 0.045776 | 0.11444 | -0.086975 | -0.18768 | -0.33417 | -0.21057 | -0.1236 | -0.14191 | 123.5825 | 123.761 | 62.0819 | -123.6603 | 123.5275 | 123.5733 | 62.0682 | -123.8022
153.3281 | 123.8159 | -61.9217 | 61.7798 | -0.00091566 | 0.008139 | 0.068312 | 0.0071757 | 0.0696 | -0.0034949 | -0.0037597 | -0.00083936 | -0.0047766 | 0.066208 | 0.070624 | -0.0074961 | -0.0069706 | 61.8713 | -61.5875 | 0.14648 | -61.8576 | 61.6974 | -61.9171 | -61.821 | -62.2055 | 0.15106 | -62.0956 | 61.6196 | 61.6699 | -61.7935 | -61.9904 | 0.004578 | 0.10071 | -0.082397 | 0.33417 | 0.064087 | -0.036621 | 0.091553 | 0.12817 | -0.068664 | -0.16022 | -0.28381 | -0.17395 | -0.10529 | -0.10986 | 123.6191 | 123.793 | 62.0682 | -123.6008 | 123.5413 | 123.5916 | 62.0728 | -123.7701
155.0156 | 123.8434 | -61.9034 | 61.7661 | -0.0085447 | 0.0051484 | 0.065322 | 0.0056803 | 0.06661 | -0.0041357 | -0.0033325 | 0.0067901 | -0.0069128 | 0.065781 | 0.069556 | -0.0040783 | -0.0067568 | 61.8622 | -61.6241 | 0.13275 | -61.853 | 61.7203 | -61.9263 | -61.821 | -62.2101 | 0.1236 | -62.0865 | 61.6104 | 61.6196 | -61.7889 | -61.972 | -0.022889 | 0.082397 | -0.045776 | 0.27923 | 0.050354 | -0.032043 | 0.096131 | 0.11444 | -0.068665 | -0.15564 | -0.3067 | -0.18311 | -0.11444 | -0.14648 | 123.6237 | 123.7656 | 62.0361 | -123.587 | 123.5138 | 123.5229 | 62.027 | -123.7381
156.6719 | 123.9029 | -61.9492 | 61.6882 | -0.00091566 | 0.007071 | 0.067458 | 0.0033305 | 0.067037 | 0.0022729 | -0.0018371 | -0.0084684 | 0.000564 | 0.063858 | 0.069983 | -0.0013011 | -0.0088932 | 61.7203 | -61.853 | -0.045776 | -62.0132 | 61.702 | -62.0224 | -61.9217 | -62.3611 | -0.045776 | -62.3108 | 61.6013 | 61.6516 | -61.8622 | -62.0819 | -0.073242 | 0.027466 | 0.013733 | 0.096131 | -0.064087 | -0.091553 | 0.032044 | 0.086975 | -0.13275 | -0.086975 | -0.41199 | -0.36163 | -0.22888 | -0.036621 | 123.6511 | 123.6694 | 61.9034 | -123.6099 | 123.5504 | 123.6008 | 61.9034 | -123.7701
158.3281 | 123.7885 | -61.9217 | 61.7844 | 0.0067138 | 0.00643 | 0.067244 | 0.0078165 | 0.067251 | -0.0019995 | -0.0014099 | 0.0067901 | -0.0039222 | 0.065567 | 0.070196 | -0.0049327 | -0.0054752 | 61.8759 | -61.6196 | 0.17853 | -61.8713 | 61.7065 | -61.9125 | -61.8118 | -62.2147 | 0.16479 | -62.1094 | 61.6058 | 61.6425 | -61.7935 | -61.9858 | 0.009155 | 0.10986 | -0.07782 | 0.30212 | 0.050354 | -0.059509 | 0.091553 | 0.12817 | -0.064087 | -0.17853 | -0.29297 | -0.18768 | -0.1236 | -0.14191 | 123.6282 | 123.7976 | 62.1002 | -123.5962 | 123.5275 | 123.5641 | 62.0865 | -123.7701
160 | 123.8617 | -61.9217 | 61.7294 | -0.00091566 | 0.0057892 | 0.067885 | 0.0037577 | 0.065755 | -7.6908e-05 | -0.0029053 | -0.0084684 | -0.004563 | 0.064927 | 0.070624 | -0.0015147 | -0.0069706 | 61.8347 | -61.6791 | 0.032043 | -61.8988 | 61.6333 | -61.94 | -61.8622 | -62.2238 | 0.09613 | -62.1323 | 61.5601 | 61.6104 | -61.8073 | -62.0178 | -0.01831 | 0.059509 | -0.09613 | 0.24262 | 0.022888 | -0.036621 | 0.10529 | 0.11444 | -0.09613 | -0.16937 | -0.30212 | -0.21057 | -0.11444 | -0.11902 | 123.555 | 123.7564 | 61.9537 | -123.5916 | 123.4818 | 123.5321 | 62.0178 | -123.7473
161.6875 | 123.7701 | -61.9354 | 61.7752 | -0.00091566 | 0.0057892 | 0.069167 | 0.0063211 | 0.070028 | -0.0028539 | -0.0041869 | -0.00083936 | -0.0043494 | 0.064286 | 0.069342 | -0.0036509 | -0.0056888 | 61.8118 | -61.7157 | 0.013733 | -61.908 | 61.6974 | -61.9217 | -61.8301 | -62.2696 | 0.050354 | -62.1643 | 61.6058 | 61.6745 | -61.7889 | -62.0041 | 0.013733 | 0.10529 | -0.07782 | 0.21973 | 0.027466 | -0.07782 | 0.036621 | 0.14649 | -0.068664 | -0.16937 | -0.33417 | -0.22888 | -0.16022 | -0.10071 | 123.6328 | 123.7473 | 61.9492 | -123.6053 | 123.5413 | 123.6099 | 61.9858 | -123.7793
163.3594 | 123.8983 | -61.9308 | 61.6837 | -0.0085447 | 0.009848 | 0.064467 | 0.0035441 | 0.065755 | 0.0041955 | -0.0033325 | -0.0084684 | -0.0013586 | 0.06749 | 0.070837 | -0.0021557 | -0.007825 | 61.7798 | -61.7935 | 0.07782 | -61.9583 | 61.6974 | -61.9812 | -61.9034 | -62.3016 | 0.064087 | -62.2513 | 61.6241 | 61.6608 | -61.8576 | -62.0407 | -0.050354 | 0.027466 | 0.013733 | 0.13733 | -0.027466 | -0.054932 | 0.09613 | 0.073242 | -0.10986 | -0.059509 | -0.37079 | -0.32044 | -0.21057 | -0.022888 | 123.6282 | 123.7106 | 62.0087 | -123.587 | 123.555 | 123.5916 | 61.9949 | -123.7244
165.0625 | 123.848 | -61.9217 | 61.7203 | 0.0067138 | 0.0068574 | 0.064894 | 0.00055326 | 0.066396 | -7.6908e-05 | -0.0024779 | -0.00083936 | -0.0030676 | 0.065567 | 0.06806 | -0.0015147 | -0.0065432 | 61.8393 | -61.6699 | 0.054932 | -61.9125 | 61.6425 | -61.9629 | -61.8851 | -62.2147 | 0.10986 | -62.1414 | 61.5463 | 61.6058 | -61.8073 | -62.0316 | -0.041199 | 0.036621 | -0.07782 | 0.25177 | 0.009155 | -0.027466 | 0.11902 | 0.11444 | -0.10986 | -0.17395 | -0.29297 | -0.21973 | -0.10986 | -0.11444 | 123.5641 | 123.761 | 61.9766 | -123.6053 | 123.468 | 123.5275 | 62.0316 | -123.7518
166.7344 | 123.7747 | -61.9263 | 61.7615 | -0.00091566 | 0.0077118 | 0.067031 | 0.0046121 | 0.066183 | -0.0022131 | -0.0016235 | -0.00083936 | -0.0017858 | 0.065995 | 0.067847 | -0.0040783 | -0.006116 | 61.8393 | -61.6791 | 0.050354 | -61.908 | 61.6516 | -61.9217 | -61.8347 | -62.2467 | 0.054932 | -62.1597 | 61.5875 | 61.6287 | -61.8118 | -62.0041 | 0.004578 | 0.091553 | -0.10986 | 0.24719 | 0.018311 | -0.073242 | 0.077819 | 0.11444 | -0.077819 | -0.17395 | -0.32043 | -0.23346 | -0.15564 | -0.13275 | 123.5779 | 123.7656 | 61.9766 | -123.5962 | 123.5138 | 123.555 | 61.9812 | -123.7656
168.4062 | 123.8205 | -61.9034 | 61.7798 | -0.0085447 | 0.0068574 | 0.067244 | 0.0080301 | 0.064901 | -0.0030677 | -0.0033325 | -0.00083936 | -0.0041358 | 0.064499 | 0.071265 | -0.0042919 | -0.0071842 | 61.8576 | -61.6241 | 0.11902 | -61.8484 | 61.7111 | -61.9171 | -61.821 | -62.2101 | 0.12817 | -62.0911 | 61.6058 | 61.6333 | -61.7981 | -61.9812 | -0.013733 | 0.082397 | -0.068664 | 0.27923 | 0.054931 | -0.027466 | 0.07782 | 0.10529 | -0.07782 | -0.17395 | -0.3067 | -0.18768 | -0.10986 | -0.14648 | 123.6145 | 123.761 | 62.0224 | -123.6008 | 123.5092 | 123.5367 | 62.0316 | -123.761
170.0938 | 123.8754 | -61.908 | 61.7249 | -0.016174 | 0.0057892 | 0.067031 | 0.0014079 | 0.0696 | -7.6908e-05 | -0.0016235 | -0.0084684 | -0.0030676 | 0.061936 | 0.071051 | 0.00040787 | -0.0080386 | 61.8347 | -61.6837 | 0.050354 | -61.8942 | 61.6379 | -61.94 | -61.853 | -62.2192 | 0.086975 | -62.1368 | 61.5738 | 61.5921 | -61.8164 | -61.9949 | -0.032043 | 0.054932 | -0.086976 | 0.2243 | 0.013733 | -0.041199 | 0.10986 | 0.091553 | -0.086975 | -0.15106 | -0.31128 | -0.22888 | -0.14191 | -0.13275 | 123.5458 | 123.7427 | 61.9583 | -123.5779 | 123.4818 | 123.5001 | 61.9949 | -123.7198
171.8281 | 123.7656 | -61.94 | 61.7477 | -0.00091566 | 0.0079254 | 0.067244 | 0.0056803 | 0.06661 | -0.0024267 | -0.0029053 | 0.01442 | -0.002854 | 0.064713 | 0.07041 | -0.0053599 | -0.006116 | 61.8301 | -61.6608 | 0.15106 | -61.8942 | 61.6791 | -61.9583 | -61.8393 | -62.2742 | 0.091553 | -62.1964 | 61.6379 | 61.6699 | -61.8118 | -61.9949 | -0.018311 | 0.10071 | -0.068665 | 0.27923 | 0.045776 | -0.054932 | 0.082397 | 0.12817 | -0.054932 | -0.10986 | -0.33417 | -0.25635 | -0.20142 | -0.07782 | 123.6191 | 123.7701 | 62.0911 | -123.587 | 123.5779 | 123.6099 | 62.0316 | -123.7427
173.5 | 123.8892 | -61.9125 | 61.7157 | 0.0067138 | 0.0072846 | 0.065322 | 0.0043985 | 0.06896 | 0.0029139 | -0.0020507 | 0.0067901 | -0.001145 | 0.064713 | 0.07041 | -0.0023693 | -0.0076114 | 61.8073 | -61.702 | 0.045776 | -61.9034 | 61.6653 | -61.9492 | -61.853 | -62.2513 | 0.07782 | -62.1597 | 61.5417 | 61.5921 | -61.821 | -62.0178 | -0.036621 | 0.05951 | -0.050354 | 0.21057 | 0.009156 | -0.050354 | 0.091553 | 0.091553 | -0.10529 | -0.17395 | -0.33875 | -0.24719 | -0.14191 | -0.1236 | 123.5779 | 123.7198 | 61.9583 | -123.5687 | 123.4543 | 123.5046 | 61.9904 | -123.7335
175.1719 | 123.8846 | -61.8942 | 61.6699 | 0.0067138 | 0.0094208 | 0.06639 | 0.0067483 | 0.068105 | 0.0020593 | -0.0014099 | -0.0084684 | -0.0007178 | 0.067276 | 0.07041 | -0.0027965 | -0.0071842 | 61.7615 | -61.7889 | 0.07782 | -61.94 | 61.6837 | -61.972 | -61.9125 | -62.2833 | 0.086975 | -62.233 | 61.6333 | 61.6333 | -61.8439 | -62.0636 | -0.07782 | -0.018311 | 0.013733 | 0.10529 | -0.045776 | -0.027465 | 0.091553 | 0.050354 | -0.16937 | -0.036621 | -0.3891 | -0.33874 | -0.16937 | -0.036621 | 123.5779 | 123.6557 | 61.972 | -123.5825 | 123.5275 | 123.5275 | 61.9812 | -123.7335
176.875 | 123.7518 | -61.94 | 61.7432 | -0.0085447 | 0.007071 | 0.067031 | 0.0069621 | 0.064046 | -0.0045629 | -0.0014099 | -0.00083936 | -0.0043494 | 0.066208 | 0.069769 | -0.0036509 | -0.0052616 | 61.7935 | -61.6791 | 0.032043 | -61.9171 | 61.6608 | -61.9125 | -61.8393 | -62.2696 | 0.050354 | -62.1552 | 61.5784 | 61.6333 | -61.7935 | -61.9904 | 0.027465 | 0.10071 | -0.082397 | 0.26093 | 0.022888 | -0.07782 | 0.050354 | 0.14648 | -0.050354 | -0.16479 | -0.32959 | -0.21515 | -0.16479 | -0.10986 | 123.6008 | 123.7335 | 61.972 | -123.5825 | 123.5184 | 123.5733 | 61.9904 | -123.7335
178.5469 | 123.8251 | -61.9263 | 61.6928 | -0.00091566 | 0.0083526 | 0.068312 | -0.00072854 | 0.065114 | 0.0022729 | -0.0035461 | -0.00083936 | 0.0012048 | 0.064927 | 0.071051 | 0.00062147 | -0.0063296 | 61.734 | -61.8256 | -0.004578 | -61.9766 | 61.6882 | -61.9858 | -61.8851 | -62.3657 | -0.013733 | -62.3154 | 61.615 | 61.6562 | -61.8347 | -62.0453 | -0.059509 | 0.041199 | -0.004578 | 0.10071 | -0.050354 | -0.091553 | 0.041199 | 0.091553 | -0.11902 | -0.07782 | -0.43945 | -0.3891 | -0.27008 | -0.036621 | 123.6145 | 123.6603 | 61.9217 | -123.5779 | 123.5413 | 123.5825 | 61.9125 | -123.7381
180.2188 | 123.7289 | -61.8896 | 61.7798 | -0.0085447 | 0.0096344 | 0.067885 | 0.0073893 | 0.070241 | -0.0026403 | -0.0037597 | -0.0084684 | -0.0052038 | 0.065567 | 0.071265 | -0.0030101 | -0.005048 | 61.8439 | -61.615 | 0.16937 | -61.853 | 61.6791 | -61.8851 | -61.821 | -62.2238 | 0.16022 | -62.1094 | 61.5875 | 61.6333 | -61.7935 | -61.9812 | 0.004577 | 0.068664 | -0.10071 | 0.27466 | 0.036621 | -0.032043 | 0.064087 | 0.09613 | -0.091553 | -0.19226 | -0.33417 | -0.21973 | -0.12817 | -0.14648 | 123.5687 | 123.7335 | 62.059 | -123.6008 | 123.4772 | 123.5229 | 62.0499 | -123.761
181.9062 | 123.7381 | -61.9354 | 61.7706 | -0.00091566 | 0.0055756 | 0.067671 | 0.0016215 | 0.064474 | -0.0013587 | -0.0037597 | -0.016098 | -0.0058448 | 0.064286 | 0.071692 | -0.0010875 | -0.006116 | 61.7981 | -61.6699 | 0.022888 | -61.908 | 61.6562 | -61.8942 | -61.8073 | -62.2513 | 0.050354 | -62.1597 | 61.6058 | 61.6562 | -61.7706 | -61.9949 | 0.041199 | 0.12817 | -0.11444 | 0.2655 | 0.027466 | -0.10071 | 0.027466 | 0.1648 | -0.059509 | -0.16479 | -0.31586 | -0.2243 | -0.16479 | -0.11444 | 123.5916 | 123.7335 | 61.9583 | -123.5779 | 123.5413 | 123.5916 | 61.9858 | -123.7656
183.5781 | 123.7518 | -61.9171 | 61.7752 | 0.0067138 | 0.0074982 | 0.06639 | 0.0082437 | 0.065328 | -0.0024267 | -0.0046143 | -0.0084684 | -0.0019996 | 0.065995 | 0.069556 | -0.0053599 | -0.0099612 | 61.853 | -61.6333 | 0.16479 | -61.8393 | 61.6287 | -61.8805 | -61.7935 | -62.2055 | 0.14648 | -62.1048 | 61.5829 | 61.6287 | -61.7798 | -61.9904 | 0.036621 | 0.1236 | -0.14648 | 0.28381 | 0.07782 | -0.045776 | 0.077819 | 0.13733 | -0.073242 | -0.19226 | -0.28839 | -0.18768 | -0.11444 | -0.14648 | 123.5458 | 123.7701 | 62.0819 | -123.5687 | 123.5001 | 123.5458 | 62.0636 | -123.7656
185.25 | 123.8434 | -61.908 | 61.7157 | -0.00091566 | 0.00878 | 0.067031 | 0.0029031 | 0.065755 | 0.0022729 | -0.0037597 | -0.00083936 | -0.0026404 | 0.065567 | 0.069128 | -0.00087393 | -0.0073978 | 61.8164 | -61.7065 | 0.032043 | -61.8896 | 61.6333 | -61.9492 | -61.8393 | -62.2055 | 0.091553 | -62.146 | 61.5555 | 61.6058 | -61.8164 | -61.9949 | -0.041199 | 0.068665 | -0.082397 | 0.20142 | 0.018311 | -0.050354 | 0.10071 | 0.091553 | -0.086975 | -0.16022 | -0.29755 | -0.23804 | -0.15106 | -0.10986 | 123.5413 | 123.7244 | 61.94 | -123.555 | 123.4634 | 123.5138 | 61.9995 | -123.7106
186.9375 | 123.8159 | -61.9308 | 61.6837 | -0.0085447 | 0.0094208 | 0.065322 | 0.0022623 | 0.067251 | 0.0065455 | -0.00034172 | -0.00083936 | 0.000564 | 0.06514 | 0.070624 | -0.00087393 | -0.0063296 | 61.7523 | -61.7569 | 0.07782 | -61.9446 | 61.647 | -61.9766 | -61.8988 | -62.3154 | 0.022888 | -62.2833 | 61.5509 | 61.6287 | -61.8805 | -62.0544 | -0.045777 | 0.032043 | -0.036621 | 0.17395 | -0.013733 | -0.045776 | 0.068664 | 0.050354 | -0.1236 | -0.13275 | -0.38452 | -0.35248 | -0.22888 | -0.054932 | 123.5779 | 123.6832 | 62.0087 | -123.5825 | 123.4818 | 123.5596 | 61.9537 | -123.7381
188.6094 | 123.7701 | -61.8851 | 61.7523 | 0.0067138 | 0.0077118 | 0.067885 | 0.0069621 | 0.066823 | -0.0047765 | -0.0026917 | -0.0084684 | -0.0049902 | 0.066208 | 0.069769 | -0.0042919 | -0.0056888 | 61.8347 | -61.6013 | 0.13275 | -61.8576 | 61.6653 | -61.9034 | -61.8073 | -62.1872 | 0.16479 | -62.0499 | 61.5921 | 61.6333 | -61.7661 | -61.9629 | -0.01831 | 0.07782 | -0.086975 | 0.28381 | 0.027466 | -0.050354 | 0.082398 | 0.11902 | -0.07782 | -0.16022 | -0.30212 | -0.16479 | -0.086975 | -0.11902 | 123.5504 | 123.7198 | 62.0178 | -123.5596 | 123.4772 | 123.5184 | 62.0499 | -123.7152
190.2969 | 123.8709 | -61.9263 | 61.6699 | -0.0085447 | 0.0085664 | 0.067244 | 0.0016215 | 0.065114 | 0.0039819 | -0.0033325 | -0.0084684 | -0.001145 | 0.064927 | 0.070196 | -0.0010875 | -0.0065432 | 61.6928 | -61.8073 | -0.054932 | -61.972 | 61.6837 | -61.9766 | -61.8942 | -62.3337 | -0.009155 | -62.2696 | 61.5692 | 61.6104 | -61.8393 | -62.0499 | -0.050354 | 0.032044 | 0.013733 | 0.11902 | -0.045776 | -0.07782 | 0.022888 | 0.086976 | -0.1236 | -0.10071 | -0.40741 | -0.34332 | -0.21973 | -0.059509 | 123.6099 | 123.6191 | 61.8713 | -123.5641 | 123.4955 | 123.5367 | 61.9171 | -123.7198
191.9844 | 123.8571 | -61.9217 | 61.6699 | -0.0085447 | 0.0077118 | 0.067244 | 0.0014079 | 0.066823 | 0.00077749 | -0.0018371 | 0.01442 | -0.0030676 | 0.06514 | 0.070196 | 0.0012623 | -0.0052616 | 61.6837 | -61.8073 | -0.050354 | -61.9812 | 61.6745 | -61.9812 | -61.8988 | -62.3428 | -0.022888 | -62.2696 | 61.6013 | 61.615 | -61.8759 | -62.0407 | -0.059509 | 0.022888 | 0.004578 | 0.11444 | -0.059509 | -0.082397 | 0.013733 | 0.045776 | -0.11902 | -0.068665 | -0.42114 | -0.3479 | -0.22888 | -0.054932 | 123.5962 | 123.6053 | 61.8713 | -123.5687 | 123.5229 | 123.5367 | 61.8988 | -123.7106
193.7031 | 123.8754 | -61.8896 | 61.6882 | -0.016174 | 0.0068574 | 0.068953 | 0.0050393 | 0.067678 | 0.00013669 | -0.0020507 | -0.00083936 | -0.0030676 | 0.065995 | 0.068701 | -0.0021557 | -0.0067568 | 61.7569 | -61.7065 | 0.009155 | -61.9034 | 61.6379 | -61.9446 | -61.8439 | -62.233 | 0.082397 | -62.1597 | 61.5509 | 61.5921 | -61.8118 | -61.9995 | -0.054932 | 0.045776 | -0.050354 | 0.1831 | -0.013733 | -0.059509 | 0.068665 | 0.077819 | -0.10986 | -0.13733 | -0.34332 | -0.27008 | -0.16022 | -0.09613 | 123.5275 | 123.6465 | 61.8988 | -123.5321 | 123.4406 | 123.4818 | 61.972 | -123.6877
195.375 | 123.7335 | -61.9308 | 61.7477 | -0.00091566 | 0.010916 | 0.067031 | 0.0086709 | 0.066823 | -0.0026403 | -0.0020507 | -0.00083936 | -0.004563 | 0.066636 | 0.069983 | -0.0060009 | -0.0084658 | 61.7569 | -61.7065 | 0.091553 | -61.9263 | 61.6882 | -61.9217 | -61.853 | -62.3245 | 0.041199 | -62.2101 | 61.6287 | 61.6562 | -61.7935 | -62.0224 | 0.009155 | 0.07782 | -0.05951 | 0.2243 | 0.004577 | -0.073243 | 0.009155 | 0.13733 | -0.091553 | -0.11902 | -0.39368 | -0.27924 | -0.18768 | -0.091553 | 123.6191 | 123.6877 | 62.0224 | -123.6008 | 123.5596 | 123.587 | 61.972 | -123.7701
197.1875 | 123.8709 | -61.9171 | 61.6608 | -0.00091566 | 0.0066438 | 0.066176 | 0.0031167 | 0.067251 | 0.0014185 | -0.0022643 | 0.0067901 | -0.001145 | 0.065995 | 0.072333 | -0.00066033 | -0.007825 | 61.6928 | -61.8027 | -0.045776 | -61.9812 | 61.6516 | -61.9629 | -61.8576 | -62.3291 | 0.004578 | -62.2513 | 61.5875 | 61.615 | -61.8576 | -62.059 | -0.045777 | 0.059509 | -0.009156 | 0.11444 | -0.064087 | -0.1236 | 0.032043 | 0.059509 | -0.14191 | -0.073243 | -0.41199 | -0.33417 | -0.19226 | -0.045777 | 123.5687 | 123.6099 | 61.8713 | -123.5184 | 123.5046 | 123.5321 | 61.9217 | -123.7198
198.9375 | 123.7656 | -61.8851 | 61.7844 | -0.00091566 | 0.0040802 | 0.068099 | 0.0065347 | 0.068105 | -0.0056311 | -0.0020507 | 0.0067901 | -0.0066992 | 0.066636 | 0.068487 | -0.0047191 | -0.006116 | 61.7615 | -61.6837 | 0.027466 | -61.8759 | 61.6653 | -61.8942 | -61.8118 | -62.2696 | 0.041199 | -62.1277 | 61.5738 | 61.6196 | -61.7477 | -61.9858 | -0.009155 | 0.073242 | -0.11902 | 0.20142 | 0.009155 | -0.064087 | -0.022888 | 0.13733 | -0.10071 | -0.21057 | -0.38452 | -0.24261 | -0.14191 | -0.16479 | 123.5504 | 123.6465 | 61.9125 | -123.5962 | 123.4589 | 123.5046 | 61.9263 | -123.7701
200.7031 | 123.7198 | -61.908 | 61.7477 | -0.0085447 | 0.0089936 | 0.067671 | 0.0063211 | 0.067464 | -0.0024267 | -0.0014099 | -0.00083936 | -0.0039222 | 0.065354 | 0.069983 | -0.0025829 | -0.0067568 | 61.8256 | -61.5967 | 0.17395 | -61.8347 | 61.6562 | -61.9034 | -61.8027 | -62.2147 | 0.14191 | -62.0819 | 61.5829 | 61.6104 | -61.7615 | -61.9583 | 0.004578 | 0.10529 | -0.091553 | 0.31128 | 0.073242 | -0.032044 | 0.07782 | 0.14648 | -0.050354 | -0.1648 | -0.3067 | -0.17395 | -0.1236 | -0.13733 | 123.5641 | 123.7335 | 62.0819 | -123.5504 | 123.4909 | 123.5184 | 62.0499 | -123.7061
202.4062 | 123.7564 | -61.8896 | 61.7294 | -0.0085447 | 0.007071 | 0.068312 | 0.0050393 | 0.065328 | -0.0026403 | -0.0033325 | -0.0084684 | -0.006272 | 0.061081 | 0.06806 | -0.0023693 | -0.0063296 | 61.8484 | -61.5646 | 0.16937 | -61.8256 | 61.647 | -61.8988 | -61.8073 | -62.1735 | 0.16937 | -62.059 | 61.5646 | 61.647 | -61.7477 | -61.9537 | -0.009156 | 0.082397 | -0.082397 | 0.32501 | 0.064086 | -0.018311 | 0.11902 | 0.14191 | -0.064087 | -0.16479 | -0.28381 | -0.16937 | -0.10529 | -0.082397 | 123.5367 | 123.7381 | 62.059 | -123.5367 | 123.4543 | 123.5367 | 62.059 | -123.6832
204.1562 | 123.7244 | -61.9263 | 61.7523 | -0.00091566 | 0.0083526 | 0.067031 | 0.0052531 | 0.068105 | -0.0019995 | -0.0061095 | -0.0084684 | -0.001145 | 0.065354 | 0.068915 | -0.0025829 | -0.0086796 | 61.7935 | -61.6562 | 0.14191 | -61.8668 | 61.6608 | -61.9217 | -61.8118 | -62.2513 | 0.07782 | -62.1552 | 61.5967 | 61.647 | -61.7844 | -61.9904 | 0.004578 | 0.11444 | -0.091552 | 0.27008 | 0.05951 | -0.054931 | 0.041199 | 0.14191 | -0.064086 | -0.15564 | -0.32501 | -0.22888 | -0.16479 | -0.10529 | 123.587 | 123.7198 | 62.0682 | -123.5641 | 123.523 | 123.5733 | 62.0041 | -123.7427
205.9062 | 123.8205 | -61.8942 | 61.702 | -0.016174 | 0.0079254 | 0.067885 | 0.0037577 | 0.067678 | 0.0020593 | -0.0018371 | -0.00083936 | -0.0043494 | 0.064286 | 0.071051 | -0.00044673 | -0.0059024 | 61.7935 | -61.6425 | 0.050354 | -61.8622 | 61.615 | -61.9217 | -61.8118 | -62.1872 | 0.082397 | -62.1368 | 61.5372 | 61.5463 | -61.7844 | -61.9949 | -0.027466 | 0.082397 | -0.086975 | 0.25177 | 0.032043 | -0.050354 | 0.091553 | 0.10986 | -0.10071 | -0.16479 | -0.29297 | -0.24261 | -0.14191 | -0.15564 | 123.5092 | 123.6877 | 61.9446 | -123.5138 | 123.4314 | 123.4406 | 61.9766 | -123.6969
207.5938 | 123.7473 | -61.9034 | 61.7477 | -0.016174 | 0.00643 | 0.067671 | 0.0052531 | 0.065328 | -0.0013587 | -0.0035461 | -0.00083936 | -0.004563 | 0.065354 | 0.069556 | -0.0025829 | -0.0063296 | 61.8439 | -61.5417 | 0.15106 | -61.821 | 61.6608 | -61.8942 | -61.7981 | -62.1597 | 0.16937 | -62.0682 | 61.5784 | 61.6013 | -61.7569 | -61.9537 | 0.009155 | 0.10529 | -0.086975 | 0.36163 | 0.082397 | -0.022888 | 0.09613 | 0.14648 | -0.050354 | -0.16937 | -0.25635 | -0.16479 | -0.11444 | -0.14649 | 123.5641 | 123.7473 | 62.0544 | -123.5458 | 123.4818 | 123.5046 | 62.0728 | -123.7015
209.3281 | 123.7381 | -61.8851 | 61.7661 | 0.0067138 | 0.0057892 | 0.067885 | 0.00076686 | 0.066183 | -0.0032813 | -0.0061095 | -0.00083936 | -0.0034948 | 0.064286 | 0.069769 | -0.0025829 | -0.006116 | 61.7706 | -61.6425 | 0.027466 | -61.8668 | 61.6699 | -61.9034 | -61.7935 | -62.2467 | 0.027466 | -62.1414 | 61.5829 | 61.6013 | -61.7706 | -61.9766 | -0.01831 | 0.091553 | -0.09613 | 0.24262 | 0.018311 | -0.073242 | 0.004578 | 0.11444 | -0.091553 | -0.18311 | -0.36163 | -0.25635 | -0.16479 | -0.1648 | 123.555 | 123.6557 | 61.9125 | -123.5596 | 123.468 | 123.4863 | 61.9125 | -123.7427
211.0156 | 123.8434 | -61.8668 | 61.6837 | 0.0067138 | 0.0051484 | 0.064894 | 0.0031167 | 0.066823 | 0.0012049 | -0.0020507 | 0.0067901 | -0.0030676 | 0.068558 | 0.068701 | -0.0015147 | -0.006116 | 61.7844 | -61.6562 | 0.036621 | -61.8759 | 61.6013 | -61.9125 | -61.821 | -62.1872 | 0.091553 | -62.1277 | 61.5417 | 61.5555 | -61.7935 | -61.9583 | -0.045777 | 0.045776 | -0.082398 | 0.21057 | -0.009156 | -0.054932 | 0.10071 | 0.073242 | -0.091553 | -0.14191 | -0.32044 | -0.26093 | -0.16937 | -0.12817 | 123.468 | 123.6511 | 61.9034 | -123.5046 | 123.4085 | 123.4222 | 61.9583 | -123.642
212.7656 | 123.7152 | -61.9217 | 61.7157 | -0.00091566 | 0.00878 | 0.067244 | 0.0065347 | 0.066183 | 0.0016321 | -0.0050415 | -0.00083936 | -0.0019996 | 0.06749 | 0.068701 | -0.0032237 | -0.007825 | 61.7294 | -61.7203 | 0.073242 | -61.9354 | 61.6928 | -61.9492 | -61.853 | -62.2925 | 0.045776 | -62.2009 | 61.6333 | 61.647 | -61.7706 | -62.0178 | -0.027466 | 0.068665 | -0.022888 | 0.20142 | -0.013733 | -0.082398 | 0.013733 | 0.15106 | -0.09613 | -0.082397 | -0.37079 | -0.27924 | -0.18311 | -0.068664 | 123.6145 | 123.6511 | 61.9949 | -123.5687 | 123.555 | 123.5687 | 61.9675 | -123.7335
214.5156 | 123.8342 | -61.908 | 61.6745 | -0.0085447 | 0.0089936 | 0.068312 | 0.0024759 | 0.065969 | 0.0020593 | -0.0022643 | -0.00083936 | -0.0002906 | 0.065995 | 0.069128 | -0.00087393 | -0.0063296 | 61.7432 | -61.7065 | 0.022888 | -61.9125 | 61.6425 | -61.9171 | -61.8576 | -62.2147 | 0.073242 | -62.146 | 61.5326 | 61.5875 | -61.7889 | -61.972 | -0.009155 | 0.050354 | -0.032044 | 0.20142 | -0.004578 | -0.054932 | 0.068664 | 0.11902 | -0.064087 | -0.14191 | -0.3067 | -0.23804 | -0.17395 | -0.086976 | 123.5504 | 123.6511 | 61.9308 | -123.5321 | 123.4406 | 123.4955 | 61.9812 | -123.6465
216.25 | 123.7976 | -61.9308 | 61.6425 | -0.00091566 | 0.010062 | 0.068099 | 0.0084573 | 0.066396 | 0.0041955 | -0.00034172 | -0.0084684 | -0.0013586 | 0.067063 | 0.070837 | -0.0021557 | -0.0067568 | 61.7432 | -61.7111 | 0.10529 | -61.9217 | 61.6287 | -61.9446 | -61.8439 | -62.2513 | 0.09613 | -62.1964 | 61.5555 | 61.5829 | -61.8118 | -62.0224 | -0.013733 | 0.086975 | -0.013733 | 0.21973 | 0.009155 | -0.07782 | 0.10071 | 0.11902 | -0.091553 | -0.086975 | -0.32044 | -0.2655 | -0.17395 | -0.059509 | 123.5596 | 123.674 | 62.0361 | -123.4863 | 123.4863 | 123.5138 | 62.027 | -123.6649
218 | 123.8251 | -61.8942 | 61.6379 | 0.0067138 | 0.011984 | 0.064681 | 0.0063211 | 0.067037 | 0.0018457 | -0.00034172 | -0.0084684 | -0.0009314 | 0.066636 | 0.071051 | -0.0036509 | -0.0067568 | 61.7386 | -61.7157 | 0.09613 | -61.9171 | 61.6516 | -61.9354 | -61.8713 | -62.2513 | 0.09613 | -62.1918 | 61.5601 | 61.6379 | -61.8256 | -62.0407 | -0.041199 | 0.022888 | 0.013733 | 0.17853 | -0.022888 | -0.045776 | 0.10071 | 0.068664 | -0.14648 | -0.077819 | -0.35706 | -0.29755 | -0.15106 | 0 | 123.5458 | 123.6328 | 61.9904 | -123.5092 | 123.4543 | 123.5321 | 61.9904 | -123.6786
219.6875 | 123.7152 | -61.8896 | 61.734 | -0.0085447 | 0.005362 | 0.068953 | 0.0067483 | 0.068105 | -0.0041357 | -0.0037597 | 0.01442 | -0.0071264 | 0.068131 | 0.070837 | -0.0068553 | -0.0065432 | 61.7386 | -61.6608 | 0.013733 | -61.8622 | 61.6562 | -61.8896 | -61.7889 | -62.233 | 0.027466 | -62.1185 | 61.5601 | 61.615 | -61.7706 | -61.9812 | 0 | 0.10071 | -0.07782 | 0.22888 | 0.027465 | -0.073243 | 0.004577 | 0.11902 | -0.091553 | -0.17395 | -0.34332 | -0.22888 | -0.13733 | -0.11902 | 123.5458 | 123.6282 | 61.9034 | -123.5229 | 123.4497 | 123.5046 | 61.9171 | -123.7152
221.4375 | 123.7015 | -61.8851 | 61.734 | -0.00091566 | 0.0074982 | 0.065535 | 0.0061075 | 0.0696 | -0.0013587 | -0.0033325 | 0.0067901 | -0.0043494 | 0.067276 | 0.069983 | -0.0042919 | -0.0046206 | 61.7798 | -61.6104 | 0.045776 | -61.8713 | 61.6104 | -61.9034 | -61.8118 | -62.2192 | 0.064087 | -62.114 | 61.5417 | 61.5829 | -61.7432 | -61.9629 | -0.01831 | 0.073242 | -0.1236 | 0.27466 | 0.013733 | -0.059509 | 0.045776 | 0.14191 | -0.07782 | -0.19226 | -0.33417 | -0.22888 | -0.15106 | -0.15106 | 123.4955 | 123.6649 | 61.9308 | -123.5458 | 123.4268 | 123.468 | 61.9492 | -123.6969
223.125 | 123.7381 | -61.9125 | 61.6653 | 0.0067138 | 0.0094208 | 0.066603 | 0.0058939 | 0.065755 | -0.0011451 | -0.0014099 | -0.016098 | -0.0007178 | 0.063858 | 0.071051 | -0.0034373 | -0.0086796 | 61.7065 | -61.734 | 0.064087 | -61.9171 | 61.7065 | -61.9308 | -61.8347 | -62.3062 | 0.032043 | -62.2238 | 61.6241 | 61.615 | -61.7889 | -61.9949 | -0.01831 | 0.07782 | 0.041199 | 0.17853 | -0.004577 | -0.082397 | 0.041199 | 0.1236 | -0.082397 | -0.041198 | -0.39368 | -0.31128 | -0.22888 | -0.050354 | 123.6191 | 123.6191 | 61.9766 | -123.5001 | 123.5367 | 123.5275 | 61.9446 | -123.6603
224.8906 | 123.7747 | -61.9125 | 61.6516 | -0.00091566 | 0.0092072 | 0.066603 | -8.7544e-05 | 0.064901 | 0.0020593 | -0.0014099 | -0.00083936 | 0.0001368 | 0.067704 | 0.07276 | 0.00062147 | -0.0054752 | 61.6791 | -61.7798 | 0.004578 | -61.9446 | 61.6699 | -61.9583 | -61.8713 | -62.3291 | -0.013733 | -62.265 | 61.5601 | 61.5921 | -61.8256 | -62.0178 | -0.045776 | 0.041199 | 0.018311 | 0.13275 | -0.032043 | -0.073242 | 0.027466 | 0.086975 | -0.10529 | -0.091552 | -0.41656 | -0.35248 | -0.24719 | -0.059509 | 123.5825 | 123.5916 | 61.9171 | -123.5229 | 123.4726 | 123.5046 | 61.8988 | -123.6694
226.5625 | 123.7381 | -61.8576 | 61.734 | 0.0067138 | 0.0066438 | 0.067671 | 0.0061075 | 0.066823 | -0.0045629 | -0.0033325 | -0.0084684 | -0.0069128 | 0.064499 | 0.068701 | -0.0051463 | -0.0035526 | 61.734 | -61.6608 | 0.045776 | -61.8668 | 61.647 | -61.8988 | -61.8027 | -62.2192 | 0.054932 | -62.0956 | 61.5555 | 61.6196 | -61.7569 | -61.9263 | -0.041199 | 0.054932 | -0.086975 | 0.19684 | -0.009155 | -0.064087 | 0 | 0.10071 | -0.068665 | -0.17853 | -0.36163 | -0.23804 | -0.16937 | -0.11444 | 123.5046 | 123.5916 | 61.9034 | -123.5367 | 123.4131 | 123.4772 | 61.9125 | -123.6603
228.2969 | 123.7473 | -61.9034 | 61.7065 | -0.00091566 | 0.011343 | 0.06938 | 0.0058939 | 0.065969 | 0.00099129 | -0.0024779 | -0.00083936 | 0.0003504 | 0.067276 | 0.072119 | -0.0047191 | -0.0073978 | 61.6974 | -61.7203 | 0.082397 | -61.9217 | 61.6837 | -61.94 | -61.8347 | -62.2971 | 0.041199 | -62.2055 | 61.6058 | 61.6241 | -61.7981 | -61.9766 | -0.036621 | 0.068664 | -0.022888 | 0.18311 | -0.018311 | -0.086975 | -0.009155 | 0.10529 | -0.073243 | -0.10071 | -0.39368 | -0.30212 | -0.22888 | -0.082397 | 123.587 | 123.6008 | 61.9858 | -123.5413 | 123.5092 | 123.5275 | 61.9446 | -123.6832
230 | 123.7564 | -61.8759 | 61.7157 | -0.00091566 | 0.0085664 | 0.064681 | 0.0037577 | 0.066183 | -0.00029051 | -0.0020507 | -0.016098 | -0.0024268 | 0.06749 | 0.069556 | -0.0036509 | -0.0076114 | 61.7661 | -61.6241 | 0.059509 | -61.8622 | 61.6058 | -61.8942 | -61.8301 | -62.1964 | 0.10529 | -62.1094 | 61.5326 | 61.5601 | -61.7569 | -61.9904 | -0.01831 | 0.045777 | -0.10986 | 0.25177 | 0.013733 | -0.032044 | 0.050354 | 0.11902 | -0.11444 | -0.18311 | -0.32043 | -0.23346 | -0.11902 | -0.15564 | 123.4818 | 123.642 | 61.9354 | -123.5458 | 123.4085 | 123.436 | 61.9812 | -123.7061
231.75 | 123.8205 | -61.8668 | 61.6425 | -0.00091566 | 0.0079254 | 0.064681 | 0.00033966 | 0.064687 | 0.0029139 | -0.0035461 | 0.0067901 | 0.0003504 | 0.064499 | 0.07276 | -0.0013011 | -0.0082522 | 61.6745 | -61.7844 | -0.041199 | -61.9629 | 61.6562 | -61.9675 | -61.8805 | -62.3062 | -0.022888 | -62.2375 | 61.5921 | 61.6104 | -61.8256 | -62.0087 | -0.10071 | -0.013733 | 0.013733 | 0.082397 | -0.096131 | -0.082398 | 0.032044 | 0.041198 | -0.14191 | -0.050354 | -0.43945 | -0.37079 | -0.22888 | -0.032043 | 123.5229 | 123.5413 | 61.8256 | -123.5229 | 123.4589 | 123.4772 | 61.8439 | -123.6511
233.4375 | 123.761 | -61.8942 | 61.6562 | -0.00091566 | 0.009848 | 0.065322 | 0.0018351 | 0.067251 | 0.0044091 | -0.0011963 | 0.0067901 | -0.0015722 | 0.066636 | 0.072546 | -0.0015147 | -0.0073978 | 61.6974 | -61.7249 | 0.054932 | -61.9354 | 61.6104 | -61.94 | -61.8713 | -62.3154 | 0.009155 | -62.2604 | 61.5189 | 61.5646 | -61.8256 | -62.0499 | -0.045776 | 0.022888 | -0.045776 | 0.16937 | -0.041199 | -0.064087 | 0.041199 | 0.068664 | -0.15564 | -0.13733 | -0.42114 | -0.36621 | -0.21057 | -0.091553 | 123.5046 | 123.5916 | 61.9492 | -123.5275 | 123.4131 | 123.4589 | 61.9034 | -123.7061
235.1094 | 123.7335 | -61.8622 | 61.7477 | 0.014343 | 0.0051484 | 0.068099 | 0.0014079 | 0.065969 | -0.0058447 | -0.0037597 | -0.0084684 | -0.0054174 | 0.065781 | 0.069769 | -0.0032237 | -0.0035526 | 61.7294 | -61.6379 | 0.022888 | -61.8668 | 61.6608 | -61.8668 | -61.7706 | -62.233 | 0.050354 | -62.1048 | 61.5601 | 61.6058 | -61.7294 | -61.9446 | -0.004577 | 0.091553 | -0.086975 | 0.22431 | -0.004577 | -0.09613 | -0.018311 | 0.13275 | -0.082397 | -0.18768 | -0.37079 | -0.24261 | -0.16022 | -0.14191 | 123.523 | 123.5916 | 61.8851 | -123.5184 | 123.4222 | 123.468 | 61.9125 | -123.6923
236.8594 | 123.6923 | -61.8668 | 61.7203 | -0.00091566 | 0.0060028 | 0.06938 | 0.0048257 | 0.066823 | -0.0049903 | -0.0024779 | -0.0084684 | -0.0056312 | 0.066208 | 0.067633 | -0.0036509 | -0.0093204 | 61.8073 | -61.5372 | 0.16022 | -61.7844 | 61.6333 | -61.8668 | -61.7844 | -62.1735 | 0.15106 | -62.0453 | 61.5509 | 61.5875 | -61.7386 | -61.9354 | 0 | 0.082397 | -0.086975 | 0.32959 | 0.082397 | 0 | 0.086975 | 0.12817 | -0.068665 | -0.16937 | -0.3067 | -0.17853 | -0.10986 | -0.13275 | 123.5001 | 123.674 | 62.027 | -123.5046 | 123.4177 | 123.4543 | 62.0178 | -123.6557
238.5625 | 123.793 | -61.8484 | 61.6241 | -0.00091566 | 0.0089936 | 0.065322 | 0.0052531 | 0.066823 | -0.00029051 | -0.0022643 | -0.0084684 | 0.0007776 | 0.067276 | 0.070624 | -0.0025829 | -0.0076114 | 61.7111 | -61.7432 | 0.07782 | -61.8988 | 61.6516 | -61.9171 | -61.8301 | -62.2971 | 0.041199 | -62.1872 | 61.5921 | 61.6333 | -61.7798 | -61.9995 | -0.068664 | 0.018311 | 0.027465 | 0.10529 | -0.050354 | -0.068665 | 0.086975 | 0.068665 | -0.15106 | -0.032044 | -0.44861 | -0.33875 | -0.18768 | 0.009155 | 123.5001 | 123.5596 | 61.9263 | -123.4543 | 123.4406 | 123.4818 | 61.8896 | -123.6237
240.25 | 123.8297 | -61.8851 | 61.6333 | -0.00091566 | 0.0068574 | 0.067885 | 0.0026895 | 0.066823 | 0.00056389 | -0.0024779 | -0.00083936 | -0.001145 | 0.065781 | 0.069128 | -0.0010875 | -0.0059024 | 61.6882 | -61.7615 | -0.036621 | -61.9354 | 61.6333 | -61.94 | -61.8484 | -62.2513 | 0.027466 | -62.1689 | 61.5509 | 61.5829 | -61.7661 | -61.9812 | -0.054931 | 0.036621 | 0 | 0.1236 | -0.050354 | -0.086975 | 0.054931 | 0.11902 | -0.09613 | -0.082398 | -0.36621 | -0.28381 | -0.18768 | -0.050354 | 123.5184 | 123.5733 | 61.8485 | -123.4818 | 123.436 | 123.468 | 61.9125 | -123.6145
242.0156 | 123.7427 | -61.8988 | 61.6196 | -0.00091566 | 0.012839 | 0.064681 | 0.0067483 | 0.067251 | 0.0027003 | -0.00034172 | -0.0084684 | 0.0009912 | 0.067917 | 0.070624 | -0.00066033 | -0.0054752 | 61.6562 | -61.7844 | 0.018311 | -61.9537 | 61.6058 | -61.9308 | -61.8759 | -62.3108 | 0 | -62.2604 | 61.5326 | 61.615 | -61.7981 | -62.027 | -0.032043 | 0.022888 | -0.013733 | 0.11444 | -0.054931 | -0.077819 | 0.036621 | 0.10071 | -0.12817 | -0.086975 | -0.41199 | -0.36163 | -0.23346 | -0.004578 | 123.5046 | 123.555 | 61.9171 | -123.4955 | 123.4314 | 123.5138 | 61.8988 | -123.6465
243.7656 | 123.761 | -61.8988 | 61.647 | -0.00091566 | 0.0089936 | 0.065962 | 0.0035441 | 0.067464 | 0.0016321 | -0.0044007 | -0.0084684 | -0.0030676 | 0.065567 | 0.071051 | -0.0015147 | -0.005048 | 61.7203 | -61.7111 | 0.091553 | -61.908 | 61.6379 | -61.9217 | -61.8439 | -62.2787 | 0.064087 | -62.2101 | 61.5463 | 61.5921 | -61.7798 | -62.0178 | -0.022888 | 0.054932 | -0.009156 | 0.18768 | -0.009155 | -0.064087 | 0.073242 | 0.11902 | -0.11902 | -0.10071 | -0.37994 | -0.31128 | -0.19226 | -0.054932 | 123.5367 | 123.6191 | 61.9904 | -123.4909 | 123.4451 | 123.4909 | 61.9629 | -123.6649
245.4531 | 123.6649 | -61.8851 | 61.7065 | -0.00091566 | 0.010275 | 0.066817 | 0.0069621 | 0.066823 | -0.0043493 | -0.0026917 | -0.00083936 | -0.002854 | 0.067704 | 0.071265 | -0.0034373 | -0.0063296 | 61.7065 | -61.6928 | 0.09613 | -61.8942 | 61.6425 | -61.8668 | -61.8027 | -62.2925 | 0.064087 | -62.1735 | 61.5875 | 61.6379 | -61.7798 | -61.9812 | 0.018311 | 0.082398 | -0.064087 | 0.19226 | -0.009155 | -0.091553 | 0 | 0.10529 | -0.09613 | -0.11902 | -0.40741 | -0.28839 | -0.19226 | -0.068665 | 123.5275 | 123.5916 | 61.9812 | -123.5092 | 123.4726 | 123.5229 | 61.9492 | -123.6877
247.1406 | 123.7473 | -61.8851 | 61.6104 | -0.00091566 | 0.0094208 | 0.068526 | 0.0046121 | 0.067892 | 0.0022729 | 0.00072628 | -0.00083936 | -0.0022132 | 0.064286 | 0.072119 | -0.0030101 | -0.0069706 | 61.7294 | -61.702 | 0.10529 | -61.9171 | 61.615 | -61.9354 | -61.8484 | -62.2604 | 0.073242 | -62.178 | 61.5417 | 61.6013 | -61.7889 | -62.0132 | -0.050354 | 0.036621 | 0.004577 | 0.18311 | -0.032043 | -0.068664 | 0.11902 | 0.096131 | -0.12817 | -0.068665 | -0.37537 | -0.29297 | -0.1648 | -0.009156 | 123.5001 | 123.6145 | 61.9904 | -123.4589 | 123.4268 | 123.4863 | 61.9583 | -123.6237
248.8906 | 123.793 | -61.8851 | 61.6333 | -0.0085447 | 0.0072846 | 0.064681 | 0.0026895 | 0.067037 | -0.0019995 | -0.0029053 | -0.0084684 | -0.0024268 | 0.064927 | 0.069556 | -0.0034373 | -0.006116 | 61.6608 | -61.7706 | -0.036621 | -61.9354 | 61.6425 | -61.9583 | -61.8484 | -62.3154 | -0.004578 | -62.2238 | 61.5692 | 61.5829 | -61.7981 | -62.0041 | -0.073242 | 0.036621 | 0.009155 | 0.11444 | -0.050354 | -0.086975 | 0.027466 | 0.086975 | -0.11902 | -0.064087 | -0.4303 | -0.33874 | -0.21973 | -0.050354 | 123.5275 | 123.5458 | 61.8485 | -123.4818 | 123.4543 | 123.468 | 61.8805 | -123.6374
250.6406 | 123.642 | -61.8713 | 61.702 | -0.0085447 | 0.010489 | 0.070876 | 0.0058939 | 0.070669 | -0.0024267 | -0.0024779 | -0.0084684 | -0.0047766 | 0.067704 | 0.068487 | -0.0053599 | -0.0054752 | 61.7661 | -61.5921 | 0.15106 | -61.8118 | 61.6333 | -61.8713 | -61.7798 | -62.2284 | 0.1236 | -62.0956 | 61.5646 | 61.6562 | -61.7523 | -61.94 | 0 | 0.091553 | -0.068664 | 0.27924 | 0.059509 | -0.032044 | 0.064087 | 0.11902 | -0.068664 | -0.13733 | -0.35706 | -0.2243 | -0.15564 | -0.045776 | 123.5046 | 123.6374 | 62.0224 | -123.4818 | 123.436 | 123.5275 | 61.9949 | -123.642
252.3125 | 123.6969 | -61.8851 | 61.6837 | -0.00091566 | 0.0040802 | 0.065535 | 0.0048257 | 0.066396 | -0.0022131 | -0.0029053 | -0.0084684 | -0.0034948 | 0.06514 | 0.071478 | -0.0027965 | -0.0071842 | 61.7615 | -61.6287 | 0.054932 | -61.853 | 61.5646 | -61.8851 | -61.7935 | -62.1918 | 0.086975 | -62.0911 | 61.5372 | 61.5646 | -61.7661 | -61.9446 | 0 | 0.091553 | -0.11902 | 0.25635 | 0.032044 | -0.059509 | 0.07782 | 0.11902 | -0.059509 | -0.14648 | -0.3067 | -0.20599 | -0.14648 | -0.11902 | 123.4497 | 123.6465 | 61.94 | -123.4772 | 123.4222 | 123.4497 | 61.972 | -123.6282
254 | 123.7793 | -61.8622 | 61.6562 | -0.00091566 | 0.0072846 | 0.06639 | 0.0058939 | 0.067464 | 0.00077749 | -0.0037597 | -0.0084684 | -0.0013586 | 0.067704 | 0.069769 | 0.00040787 | -0.0082522 | 61.6837 | -61.734 | 0.07782 | -61.9034 | 61.6425 | -61.9308 | -61.821 | -62.2787 | 0.054932 | -62.1872 | 61.5875 | 61.6333 | -61.7798 | -62.0041 | -0.068664 | 0.041199 | -0.013733 | 0.12817 | -0.041198 | -0.082397 | 0.027466 | 0.082398 | -0.14191 | -0.068665 | -0.41656 | -0.32501 | -0.18311 | -0.022888 | 123.5046 | 123.5458 | 61.94 | -123.4772 | 123.4497 | 123.4955 | 61.9171 | -123.6603
255.75 | 123.7061 | -61.8622 | 61.6928 | -0.016174 | 0.0072846 | 0.066603 | 0.0082437 | 0.067037 | -0.0039221 | -0.0044007 | -0.00083936 | -0.0054174 | 0.066208 | 0.068274 | -0.0057873 | -0.0071842 | 61.8027 | -61.5646 | 0.11902 | -61.8118 | 61.6379 | -61.8484 | -61.7661 | -62.1597 | 0.14191 | -62.0178 | 61.5372 | 61.5921 | -61.6837 | -61.9125 | 0.013733 | 0.096131 | -0.054932 | 0.29755 | 0.050354 | -0.045777 | 0.10986 | 0.17853 | -0.050354 | -0.15564 | -0.29755 | -0.15564 | -0.10529 | -0.10071 | 123.5001 | 123.6649 | 61.9812 | -123.4589 | 123.3994 | 123.4543 | 62.0041 | -123.6053
257.4375 | 123.6511 | -61.8851 | 61.7065 | -0.016174 | 0.0096344 | 0.066176 | 0.0056803 | 0.06661 | -0.0011451 | -0.0052551 | -0.0084684 | -0.001145 | 0.06749 | 0.07041 | -0.0034373 | -0.0071842 | 61.7203 | -61.6653 | 0.10529 | -61.8576 | 61.6425 | -61.8896 | -61.8118 | -62.265 | 0.045776 | -62.178 | 61.5692 | 61.6379 | -61.7706 | -61.9766 | -0.004577 | 0.073242 | -0.064087 | 0.21973 | 0.027466 | -0.045776 | 0.013733 | 0.11444 | -0.091553 | -0.13733 | -0.37994 | -0.29297 | -0.20142 | -0.068665 | 123.5275 | 123.6053 | 61.9904 | -123.5184 | 123.4543 | 123.5229 | 61.9308 | -123.6832
259.1094 | 123.761 | -61.8622 | 61.6379 | 0.0067138 | 0.01348 | 0.065108 | 0.0054667 | 0.067892 | 0.0020593 | -0.0029053 | -0.0084684 | -0.0032812 | 0.068344 | 0.071265 | -0.0045055 | -0.0080386 | 61.6745 | -61.7157 | 0.07782 | -61.8805 | 61.6562 | -61.9034 | -61.8347 | -62.2559 | 0.059509 | -62.178 | 61.5738 | 61.6013 | -61.7844 | -61.9812 | -0.041198 | 0.027466 | 0.018311 | 0.14648 | -0.01831 | -0.045776 | 0.036622 | 0.07782 | -0.11902 | -0.064086 | -0.39368 | -0.31586 | -0.19684 | -0.036621 | 123.5184 | 123.5367 | 61.94 | -123.4726 | 123.436 | 123.4634 | 61.9217 | -123.6191
260.8438 | 123.7473 | -61.8484 | 61.6333 | 0.0067138 | 0.010275 | 0.064467 | 0.0067483 | 0.066396 | -0.00050411 | -0.0026917 | -0.0084684 | -0.0013586 | 0.068772 | 0.072974 | -0.0015147 | -0.0065432 | 61.6745 | -61.7157 | 0.068665 | -61.8896 | 61.6608 | -61.908 | -61.8073 | -62.265 | 0.059509 | -62.178 | 61.5555 | 61.6241 | -61.7935 | -62.0041 | -0.059509 | 0.041199 | 0.027466 | 0.13275 | -0.041198 | -0.082397 | 0.041199 | 0.054932 | -0.15564 | -0.07782 | -0.41656 | -0.32959 | -0.17395 | -0.009155 | 123.5092 | 123.523 | 61.9171 | -123.4406 | 123.4039 | 123.4726 | 61.908 | -123.6374
262.5938 | 123.6603 | -61.8805 | 61.702 | -0.00091566 | 0.0085664 | 0.06874 | 0.0024759 | 0.064901 | -0.0047765 | -0.0029053 | -0.00083936 | -0.0066992 | 0.068131 | 0.068701 | -0.0023693 | -0.006116 | 61.734 | -61.6379 | 0.027466 | -61.8439 | 61.6241 | -61.8393 | -61.7844 | -62.2055 | 0.050354 | -62.1094 | 61.5326 | 61.5967 | -61.7203 | -61.9354 | 0.041199 | 0.09613 | -0.077819 | 0.24262 | 0.036621 | -0.059509 | 0.032044 | 0.16022 | -0.054932 | -0.16937 | -0.32501 | -0.22888 | -0.17395 | -0.10529 | 123.5046 | 123.6145 | 61.908 | -123.4863 | 123.4131 | 123.4772 | 61.9308 | -123.6374
264.2812 | 123.761 | -61.8393 | 61.6425 | -0.00091566 | 0.009848 | 0.065535 | 0.0054667 | 0.067251 | 0.0014185 | -0.0039733 | -0.00083936 | 0.0003504 | 0.06984 | 0.06806 | 0.00019427 | -0.0076114 | 61.6882 | -61.6974 | 0.09613 | -61.8896 | 61.6379 | -61.8942 | -61.8301 | -62.2375 | 0.073242 | -62.1552 | 61.5463 | 61.5738 | -61.7844 | -61.9858 | -0.054932 | 0.009155 | -0.004578 | 0.14191 | -0.050354 | -0.059509 | 0.045776 | 0.054931 | -0.14648 | -0.09613 | -0.39825 | -0.31586 | -0.16937 | -0.068664 | 123.4772 | 123.5275 | 61.9354 | -123.4726 | 123.3856 | 123.4131 | 61.9125 | -123.6282
265.9688 | 123.6145 | -61.8484 | 61.6928 | -0.0085447 | 0.0079254 | 0.068526 | 0.0035441 | 0.068532 | -0.0039221 | -0.0029053 | -0.00083936 | -0.0032812 | 0.064713 | 0.070837 | -0.0038647 | -0.0076114 | 61.7706 | -61.5646 | 0.15106 | -61.7981 | 61.5829 | -61.8759 | -61.7981 | -62.1689 | 0.11902 | -62.0499 | 61.5372 | 61.6058 | -61.7203 | -61.9217 | -0.027466 | 0.050354 | -0.10986 | 0.28381 | 0.050354 | 0 | 0.07782 | 0.12817 | -0.073242 | -0.15564 | -0.32043 | -0.20142 | -0.12817 | -0.086975 | 123.4314 | 123.6191 | 61.9995 | -123.4909 | 123.3856 | 123.4543 | 61.9675 | -123.6145
267.7188 | 123.642 | -61.8576 | 61.7111 | -0.00091566 | 0.0094208 | 0.068953 | 0.0039713 | 0.066396 | -0.0043493 | -0.0035461 | -0.0084684 | -0.0039222 | 0.064927 | 0.068915 | -0.0010875 | -0.0069706 | 61.7798 | -61.5417 | 0.16479 | -61.7981 | 61.6379 | -61.8576 | -61.7569 | -62.1506 | 0.13733 | -62.0499 | 61.5372 | 61.5967 | -61.702 | -61.9034 | 0 | 0.10071 | -0.073243 | 0.31586 | 0.059509 | -0.041199 | 0.068664 | 0.15564 | -0.045776 | -0.17395 | -0.29297 | -0.19226 | -0.14648 | -0.11444 | 123.4955 | 123.6374 | 62.0224 | -123.468 | 123.3948 | 123.4543 | 61.9949 | -123.6145
269.4062 | 123.7427 | -61.8439 | 61.6287 | -0.00091566 | 0.0072846 | 0.066176 | 0.0037577 | 0.069173 | 0.0014185 | -0.0035461 | -0.0084684 | -0.002854 | 0.066849 | 0.069983 | -0.0025829 | -0.0080386 | 61.6699 | -61.702 | 0.073242 | -61.8896 | 61.647 | -61.9125 | -61.8118 | -62.2559 | 0.059509 | -62.1964 | 61.5601 | 61.6013 | -61.7889 | -61.9949 | -0.068665 | 0.032043 | 0.018311 | 0.14191 | -0.045776 | -0.077819 | 0.041199 | 0.054932 | -0.15106 | -0.068664 | -0.41199 | -0.35248 | -0.20142 | -0.027466 | 123.4909 | 123.5138 | 61.9171 | -123.4406 | 123.4039 | 123.4451 | 61.9034 | -123.6237
271.0938 | 123.7518 | -61.8668 | 61.6653 | -0.00091566 | 0.007071 | 0.06639 | 0.0020487 | 0.068105 | 0.0020593 | -0.00055532 | -0.0084684 | -0.0037086 | 0.064713 | 0.068915 | 0.00062147 | -0.006116 | 61.7477 | -61.6104 | 0.045776 | -61.8439 | 61.5784 | -61.8988 | -61.7752 | -62.1506 | 0.086975 | -62.0682 | 61.5143 | 61.5417 | -61.7477 | -61.9675 | -0.032044 | 0.091552 | -0.086975 | 0.25635 | 0.022888 | -0.068664 | 0.082398 | 0.11902 | -0.10071 | -0.15106 | -0.28381 | -0.20142 | -0.10071 | -0.1236 | 123.4451 | 123.6145 | 61.9125 | -123.4406 | 123.381 | 123.4085 | 61.9537 | -123.6328
272.8594 | 123.7381 | -61.8439 | 61.6653 | -0.00091566 | 0.0057892 | 0.064681 | 0.0039713 | 0.068105 | 0.00035029 | -0.0018371 | -0.00083936 | -0.0041358 | 0.064927 | 0.069556 | 0.00019427 | -0.0076114 | 61.7477 | -61.6104 | 0.045776 | -61.8484 | 61.5784 | -61.8942 | -61.7844 | -62.1552 | 0.09613 | -62.0682 | 61.5051 | 61.5189 | -61.7477 | -61.9446 | -0.050354 | 0.059509 | -0.086975 | 0.23346 | -0.004578 | -0.064087 | 0.082398 | 0.09613 | -0.10071 | -0.16022 | -0.31128 | -0.2243 | -0.1236 | -0.14648 | 123.4222 | 123.5916 | 61.8896 | -123.4497 | 123.349 | 123.3627 | 61.94 | -123.6099
274.625 | 123.6877 | -61.8759 | 61.6516 | -0.0085447 | 0.0079254 | 0.067031 | 0.0061075 | 0.064687 | 0.0035547 | -0.0018371 | -0.00083936 | -0.0007178 | 0.064499 | 0.071692 | -0.0017283 | -0.0065432 | 61.6333 | -61.7477 | 0.013733 | -61.9354 | 61.6241 | -61.9263 | -61.8256 | -62.2833 | 0 | -62.2238 | 61.5143 | 61.5784 | -61.7935 | -62.0041 | -0.050354 | 0.050354 | -0.027465 | 0.12817 | -0.059509 | -0.10986 | -0.01831 | 0.082398 | -0.12817 | -0.13733 | -0.40741 | -0.3479 | -0.21973 | -0.073242 | 123.5001 | 123.5092 | 61.8896 | -123.4772 | 123.3902 | 123.4543 | 61.8759 | -123.6557
276.3125 | 123.6969 | -61.8759 | 61.6379 | -0.00091566 | 0.0077118 | 0.065962 | 0.0039713 | 0.06426 | 0.0020593 | -0.00034172 | -0.0084684 | -0.0007178 | 0.064072 | 0.069983 | 0.00062147 | -0.0063296 | 61.6241 | -61.7706 | 0.009155 | -61.9263 | 61.6104 | -61.9263 | -61.8393 | -62.3062 | 0 | -62.2513 | 61.5417 | 61.5967 | -61.7844 | -61.9858 | -0.050354 | 0.036622 | -0.027465 | 0.10529 | -0.050354 | -0.086976 | -0.013732 | 0.091553 | -0.10986 | -0.09613 | -0.4303 | -0.37537 | -0.2655 | -0.041198 | 123.4863 | 123.5001 | 61.8851 | -123.4772 | 123.4177 | 123.4726 | 61.8759 | -123.6237
278.0781 | 123.6145 | -61.8484 | 61.702 | -0.016174 | 0.0094208 | 0.068953 | 0.0046121 | 0.065114 | -0.0056311 | -0.0035461 | -0.0084684 | -0.002854 | 0.065781 | 0.069556 | -0.0047191 | -0.0065432 | 61.7386 | -61.6013 | 0.13733 | -61.8164 | 61.6196 | -61.8759 | -61.7661 | -62.2238 | 0.086975 | -62.1002 | 61.5509 | 61.6287 | -61.734 | -61.9217 | -0.027466 | 0.082398 | -0.082397 | 0.24719 | 0.032044 | -0.050354 | 0.036621 | 0.11444 | -0.073242 | -0.15106 | -0.37537 | -0.25177 | -0.17853 | -0.073242 | 123.468 | 123.587 | 61.9858 | -123.468 | 123.3994 | 123.4772 | 61.9354 | -123.6237
279.8281 | 123.6923 | -61.8759 | 61.6379 | -0.0085447 | 0.0074982 | 0.06639 | 0.0018351 | 0.06661 | 0.0031275 | -0.0029053 | -0.0084684 | -0.0007178 | 0.06514 | 0.071692 | -0.0010875 | -0.0067568 | 61.6287 | -61.7477 | -0.013733 | -61.9308 | 61.6196 | -61.9171 | -61.8256 | -62.2925 | 0 | -62.233 | 61.5189 | 61.5784 | -61.7798 | -62.0087 | -0.041198 | 0.050354 | -0.01831 | 0.12817 | -0.054931 | -0.10529 | -0.009155 | 0.096131 | -0.13275 | -0.11902 | -0.41656 | -0.35706 | -0.2243 | -0.059509 | 123.4955 | 123.5046 | 61.8622 | -123.4634 | 123.3948 | 123.4543 | 61.8759 | -123.6465
281.5156 | 123.6145 | -61.8439 | 61.7249 | -0.0085447 | 0.0072846 | 0.067458 | 0.0043985 | 0.063619 | -0.0056311 | -0.0024779 | -0.00083936 | -0.0056312 | 0.067704 | 0.068487 | -0.0062145 | -0.0059024 | 61.7249 | -61.6013 | 0.018311 | -61.8484 | 61.5967 | -61.821 | -61.7477 | -62.1964 | 0.054932 | -62.059 | 61.5097 | 61.5829 | -61.6928 | -61.9354 | 0.022888 | 0.09613 | -0.12817 | 0.24262 | -0.004578 | -0.10071 | 0 | 0.15106 | -0.091553 | -0.21515 | -0.35248 | -0.21515 | -0.1236 | -0.14191 | 123.4406 | 123.5687 | 61.8622 | -123.4726 | 123.3536 | 123.4268 | 61.8988 | -123.6603
283.2656 | 123.7473 | -61.8347 | 61.6241 | -0.0085447 | 0.011557 | 0.065535 | 0.0061075 | 0.065969 | 0.00099129 | -0.0026917 | -0.00083936 | -0.001145 | 0.06749 | 0.072333 | -0.0027965 | -0.0088932 | 61.6928 | -61.6745 | 0.10071 | -61.8668 | 61.6196 | -61.8988 | -61.8073 | -62.2238 | 0.07782 | -62.1368 | 61.5372 | 61.5417 | -61.7844 | -61.9766 | -0.064087 | 0.027466 | -0.004578 | 0.16022 | -0.032043 | -0.059509 | 0.068664 | 0.050354 | -0.14191 | -0.086976 | -0.3891 | -0.30212 | -0.16022 | -0.082398 | 123.4543 | 123.5275 | 61.9354 | -123.4314 | 123.3719 | 123.3765 | 61.9125 | -123.6008
285 | 123.6374 | -61.8118 | 61.7065 | -0.0085447 | 0.009848 | 0.06938 | 0.0054667 | 0.066183 | -0.0039221 | -0.0024779 | -0.00083936 | -0.006272 | 0.065781 | 0.06806 | -0.0051463 | -0.0063296 | 61.6928 | -61.6196 | 0.032043 | -61.8256 | 61.6196 | -61.8301 | -61.7386 | -62.2055 | 0.041199 | -62.0636 | 61.5509 | 61.5921 | -61.702 | -61.9217 | -0.01831 | 0.073243 | -0.086975 | 0.19226 | -0.013733 | -0.086976 | -0.013733 | 0.10986 | -0.10986 | -0.15564 | -0.39368 | -0.25177 | -0.14191 | -0.11444 | 123.4314 | 123.5046 | 61.8439 | -123.4451 | 123.3627 | 123.4039 | 61.853 | -123.6282
286.6719 | 123.5916 | -61.853 | 61.702 | -0.00091566 | 0.010703 | 0.069808 | 0.0065347 | 0.067251 | -0.0015723 | -0.0033325 | 0.0067901 | -0.0013586 | 0.066208 | 0.07041 | -0.0040783 | -0.0059024 | 61.6928 | -61.6196 | 0.11444 | -61.8256 | 61.6058 | -61.8576 | -61.7844 | -62.2238 | 0.054932 | -62.1414 | 61.5738 | 61.6013 | -61.734 | -61.9629 | -0.004578 | 0.068664 | -0.09613 | 0.23346 | 0.027465 | -0.041199 | -0.009155 | 0.11902 | -0.10986 | -0.12817 | -0.37079 | -0.28839 | -0.17853 | -0.10071 | 123.4589 | 123.5458 | 61.9675 | -123.4863 | 123.4268 | 123.4543 | 61.908 | -123.6649
288.4219 | 123.7106 | -61.8301 | 61.647 | -0.0085447 | 0.0057892 | 0.066603 | 0.0037577 | 0.068319 | -0.00050411 | -0.0033325 | -0.00083936 | -0.0034948 | 0.064286 | 0.070624 | -0.00087393 | -0.0063296 | 61.7386 | -61.6013 | 0.045776 | -61.8301 | 61.5509 | -61.8713 | -61.7935 | -62.1506 | 0.09613 | -62.059 | 61.4914 | 61.528 | -61.7294 | -61.9446 | -0.041199 | 0.036621 | -0.096131 | 0.22888 | 0 | -0.036621 | 0.091552 | 0.10071 | -0.11444 | -0.15564 | -0.32043 | -0.22888 | -0.11444 | -0.11902 | 123.381 | 123.5687 | 61.8759 | -123.4406 | 123.3215 | 123.3582 | 61.9263 | -123.5916
290.1094 | 123.6603 | -61.8713 | 61.6241 | 0.0067138 | 0.0092072 | 0.066176 | 0.0048257 | 0.067251 | -7.6908e-05 | -0.0048279 | -0.00083936 | -0.0002906 | 0.06749 | 0.069556 | -0.0036509 | -0.0059024 | 61.6699 | -61.6837 | 0.068665 | -61.8759 | 61.6516 | -61.8668 | -61.7981 | -62.2604 | 0.036621 | -62.178 | 61.5601 | 61.6104 | -61.7615 | -61.9446 | 0.004578 | 0.073242 | 0.027465 | 0.18768 | -0.004578 | -0.07782 | 0.045776 | 0.10986 | -0.073242 | -0.064087 | -0.3891 | -0.3067 | -0.23346 | -0.013733 | 123.5229 | 123.5413 | 61.94 | -123.4222 | 123.4314 | 123.4818 | 61.908 | -123.5687
291.8438 | 123.6053 | -61.8439 | 61.6791 | -0.00091566 | 0.0085664 | 0.06639 | 0.0033305 | 0.06661 | -0.0028539 | -0.0044007 | 0.0067901 | -0.0039222 | 0.064713 | 0.068274 | -0.0010875 | -0.0069706 | 61.7523 | -61.5829 | 0.14191 | -61.8118 | 61.6196 | -61.853 | -61.7523 | -62.2055 | 0.073242 | -62.1048 | 61.5601 | 61.6013 | -61.702 | -61.9034 | -0.009155 | 0.091553 | -0.059509 | 0.26093 | 0.032043 | -0.05951 | 0.073242 | 0.14191 | -0.059509 | -0.11902 | -0.36163 | -0.26093 | -0.20142 | -0.07782 | 123.4634 | 123.5962 | 61.9858 | -123.4314 | 123.4039 | 123.4451 | 61.9171 | -123.5825
293.5938 | 123.6649 | -61.821 | 61.6791 | -0.00091566 | 0.0077118 | 0.069594 | 0.0067483 | 0.063405 | -0.0047765 | -0.0050415 | -0.0084684 | -0.0054174 | 0.064713 | 0.068701 | -0.0066417 | -0.0063296 | 61.7844 | -61.528 | 0.11902 | -61.7889 | 61.6104 | -61.8439 | -61.734 | -62.1185 | 0.14648 | -61.9904 | 61.5005 | 61.5875 | -61.6608 | -61.8988 | -0.022888 | 0.086975 | -0.068664 | 0.29297 | 0.032044 | -0.054931 | 0.10529 | 0.16022 | -0.07782 | -0.17853 | -0.29755 | -0.16937 | -0.091552 | -0.091553 | 123.4314 | 123.6053 | 61.94 | -123.4131 | 123.3215 | 123.4085 | 61.9675 | -123.5779
295.3281 | 123.642 | -61.8347 | 61.6699 | -0.0085447 | 0.0085664 | 0.064681 | 0.00098046 | 0.06661 | -0.0011451 | -0.0044007 | 0.0067901 | -0.0043494 | 0.06514 | 0.067847 | -0.00044673 | -0.0063296 | 61.7523 | -61.5875 | 0.036621 | -61.8256 | 61.5692 | -61.8759 | -61.7661 | -62.1597 | 0.086975 | -62.0544 | 61.5005 | 61.5234 | -61.7432 | -61.9446 | -0.041199 | 0.068665 | -0.10071 | 0.24719 | 0.009155 | -0.05951 | 0.082397 | 0.091553 | -0.10986 | -0.16937 | -0.32501 | -0.21973 | -0.10986 | -0.14648 | 123.4039 | 123.587 | 61.8713 | -123.436 | 123.3353 | 123.3582 | 61.9217 | -123.6145
297.0938 | 123.7656 | -61.8393 | 61.6013 | -0.0085447 | 0.008139 | 0.06639 | 0.0035441 | 0.065542 | 0.0016321 | -0.0016235 | -0.0084684 | -0.0002906 | 0.064927 | 0.071478 | -0.0019419 | -0.0071842 | 61.6653 | -61.7249 | -0.032043 | -61.9034 | 61.5967 | -61.9034 | -61.8118 | -62.2055 | 0.018311 | -62.1231 | 61.5189 | 61.5326 | -61.7249 | -61.9629 | -0.064087 | 0.027465 | -0.004577 | 0.11444 | -0.064087 | -0.091552 | 0.064087 | 0.11444 | -0.1236 | -0.082397 | -0.36621 | -0.28381 | -0.16022 | -0.068664 | 123.436 | 123.5046 | 61.8073 | -123.4131 | 123.3582 | 123.3719 | 61.8576 | -123.5641
298.8438 | 123.6786 | -61.8301 | 61.6196 | -0.023804 | 0.009848 | 0.064894 | 0.0037577 | 0.065542 | 0.0020593 | 0.00029908 | -0.016098 | -0.0009314 | 0.068772 | 0.07041 | -0.00023313 | -0.0084658 | 61.6974 | -61.6837 | 0.082397 | -61.8713 | 61.6058 | -61.8805 | -61.8164 | -62.233 | 0.041199 | -62.1872 | 61.5097 | 61.5326 | -61.7844 | -61.9766 | -0.050354 | 0.013733 | -0.013733 | 0.14648 | -0.041199 | -0.054932 | 0.07782 | 0.045776 | -0.14648 | -0.10986 | -0.40283 | -0.35706 | -0.21057 | -0.086975 | 123.436 | 123.5275 | 61.9125 | -123.436 | 123.3398 | 123.3627 | 61.8713 | -123.5962
300.5312 | 123.7152 | -61.8393 | 61.5921 | -0.016174 | 0.01113 | 0.065108 | 0.0082437 | 0.064901 | 0.0016321 | -0.00076912 | -0.0084684 | -0.0030676 | 0.065354 | 0.072119 | -0.0032237 | -0.006116 | 61.6562 | -61.6745 | 0.11444 | -61.8622 | 61.615 | -61.8759 | -61.8256 | -62.2009 | 0.082397 | -62.1231 | 61.528 | 61.5646 | -61.7661 | -61.9675 | -0.036622 | 0.013732 | 0.022888 | 0.16479 | -0.022889 | -0.036621 | 0.064087 | 0.073242 | -0.12817 | -0.064087 | -0.36163 | -0.28381 | -0.15564 | -0.027466 | 123.4543 | 123.4955 | 61.9537 | -123.4177 | 123.3673 | 123.4039 | 61.9217 | -123.5596
302.2656 | 123.6603 | -61.8484 | 61.6013 | -0.0085447 | 0.0092072 | 0.065322 | 0.0054667 | 0.065114 | 0.0020593 | -0.00098272 | -0.00083936 | -0.0007178 | 0.066636 | 0.072119 | -0.00087393 | -0.0071842 | 61.6104 | -61.7386 | 0.018311 | -61.9217 | 61.5738 | -61.9217 | -61.821 | -62.2559 | 0.013733 | -62.2192 | 61.5051 | 61.5601 | -61.7706 | -61.9629 | -0.073242 | 0.027466 | -0.027465 | 0.10986 | -0.073242 | -0.10071 | 0.009156 | 0.07782 | -0.11444 | -0.09613 | -0.40741 | -0.37079 | -0.25635 | -0.041198 | 123.4222 | 123.4589 | 61.8668 | -123.4222 | 123.3536 | 123.4085 | 61.8622 | -123.5641
304.0156 | 123.7198 | -61.8027 | 61.6013 | -0.00091566 | 0.010275 | 0.064681 | 0.0037577 | 0.069387 | -0.0013587 | -0.0024779 | -0.00083936 | -0.0047766 | 0.06514 | 0.068701 | -0.0027965 | -0.0048342 | 61.6928 | -61.615 | 0.032043 | -61.8256 | 61.5829 | -61.8576 | -61.7615 | -62.1735 | 0.086975 | -62.0682 | 61.4639 | 61.5326 | -61.734 | -61.9171 | -0.054932 | 0.041198 | -0.01831 | 0.18768 | -0.022889 | -0.064087 | 0.091553 | 0.068664 | -0.11444 | -0.13733 | -0.37079 | -0.2655 | -0.15106 | -0.068664 | 123.3856 | 123.4955 | 61.8347 | -123.3627 | 123.2666 | 123.3353 | 61.8896 | -123.5184
305.6875 | 123.6191 | -61.8256 | 61.6928 | 0.0067138 | 0.0072846 | 0.070235 | 0.0058939 | 0.06661 | -0.0049903 | -0.0035461 | -0.00083936 | -0.0039222 | 0.065781 | 0.069342 | -0.0057873 | -0.0076114 | 61.7615 | -61.4868 | 0.15564 | -61.7569 | 61.5829 | -61.8027 | -61.7294 | -62.1185 | 0.16022 | -61.9949 | 61.5097 | 61.5875 | -61.6791 | -61.908 | 0.022889 | 0.096131 | -0.10986 | 0.33875 | 0.068665 | -0.027466 | 0.068665 | 0.14648 | -0.082397 | -0.18311 | -0.29297 | -0.16937 | -0.086975 | -0.10529 | 123.4085 | 123.587 | 61.9812 | -123.4222 | 123.3353 | 123.4131 | 61.9858 | -123.6008
307.4375 | 123.6053 | -61.8622 | 61.6791 | -0.0085447 | 0.008139 | 0.065962 | 0.0041849 | 0.067037 | -0.00093131 | -0.0037597 | -0.00083936 | -0.0017858 | 0.066208 | 0.068487 | -0.0036509 | -0.0080386 | 61.6653 | -61.6425 | 0.07782 | -61.853 | 61.6379 | -61.8576 | -61.7706 | -62.2375 | 0.059509 | -62.1277 | 61.5646 | 61.5921 | -61.734 | -61.9354 | 0.004578 | 0.091553 | -0.041199 | 0.21973 | 0.009156 | -0.082397 | -0.013733 | 0.12817 | -0.073242 | -0.11444 | -0.37537 | -0.2655 | -0.19226 | -0.086975 | 123.5001 | 123.5275 | 61.94 | -123.4497 | 123.4268 | 123.4543 | 61.9217 | -123.6145
309.1875 | 123.6465 | -61.821 | 61.6745 | -0.0085447 | 0.0038666 | 0.067244 | 0.0054667 | 0.067251 | -0.0039221 | -0.0037597 | -0.00083936 | -0.0058448 | 0.063645 | 0.070196 | -0.0036509 | -0.0088932 | 61.7569 | -61.5509 | 0.082397 | -61.7661 | 61.615 | -61.8301 | -61.7249 | -62.1414 | 0.10986 | -61.9949 | 61.5189 | 61.5829 | -61.6699 | -61.9034 | -0.009155 | 0.09613 | -0.05951 | 0.27008 | 0.054932 | -0.041198 | 0.082397 | 0.15106 | -0.082397 | -0.15564 | -0.32043 | -0.17395 | -0.091553 | -0.091553 | 123.436 | 123.5779 | 61.9034 | -123.3994 | 123.3398 | 123.4039 | 61.9308 | -123.5779
310.8594 | 123.6923 | -61.8301 | 61.6196 | -0.016174 | 0.011557 | 0.06404 | 0.0071757 | 0.065969 | 0.0016321 | -0.0037597 | -0.00083936 | -0.0015722 | 0.066208 | 0.069983 | -0.0025829 | -0.0071842 | 61.6562 | -61.6882 | 0.073242 | -61.853 | 61.6058 | -61.8668 | -61.7935 | -62.2421 | 0.036621 | -62.1643 | 61.5372 | 61.5829 | -61.7432 | -61.9537 | -0.036621 | 0.036621 | -0.013733 | 0.14191 | -0.022888 | -0.059509 | 0.036621 | 0.086975 | -0.1236 | -0.082398 | -0.41199 | -0.33417 | -0.21057 | -0.036621 | 123.436 | 123.4863 | 61.9034 | -123.4131 | 123.3673 | 123.4131 | 61.8668 | -123.5733
312.6094 | 123.7061 | -61.8256 | 61.6196 | -0.0085447 | 0.0077118 | 0.064253 | 0.0063211 | 0.064687 | 0.0012049 | -0.0014099 | -0.0084684 | -0.0024268 | 0.064072 | 0.071692 | -0.0023693 | -0.0067568 | 61.6333 | -61.6745 | 0.07782 | -61.8576 | 61.6241 | -61.8576 | -61.7798 | -62.2238 | 0.059509 | -62.1506 | 61.5509 | 61.5463 | -61.7386 | -61.9675 | -0.032043 | 0.045777 | 0.004578 | 0.15106 | -0.032043 | -0.07782 | 0.013733 | 0.086976 | -0.14191 | -0.068665 | -0.39825 | -0.32501 | -0.18311 | -0.073242 | 123.4497 | 123.4589 | 61.9034 | -123.3994 | 123.3765 | 123.3719 | 61.8851 | -123.587
314.3594 | 123.7381 | -61.8347 | 61.6333 | -0.0085447 | 0.0072846 | 0.067031 | 0.0039713 | 0.067892 | 0.0014185 | -0.0014099 | 0.0067901 | -0.0030676 | 0.065781 | 0.070624 | 0.00019427 | -0.0039798 | 61.6196 | -61.702 | -0.041199 | -61.9034 | 61.5875 | -61.8896 | -61.7935 | -62.233 | -0.004578 | -62.1414 | 61.4914 | 61.5372 | -61.7249 | -61.9263 | -0.054931 | 0.041199 | -0.045777 | 0.13275 | -0.068664 | -0.10986 | -0.013733 | 0.10986 | -0.091553 | -0.14191 | -0.39825 | -0.3067 | -0.21515 | -0.096131 | 123.4222 | 123.4543 | 61.7935 | -123.4268 | 123.3261 | 123.3719 | 61.8301 | -123.5596
316.0625 | 123.6694 | -61.8347 | 61.6241 | -0.016174 | 0.0079254 | 0.066176 | 0.0031167 | 0.065542 | 0.0016321 | -0.0024779 | -0.00083936 | -0.001145 | 0.066636 | 0.069128 | -0.0027965 | -0.0052616 | 61.6058 | -61.7477 | -0.032043 | -61.9263 | 61.5829 | -61.8988 | -61.8073 | -62.2787 | -0.013733 | -62.2009 | 61.5143 | 61.5326 | -61.7706 | -61.972 | -0.064087 | 0.027466 | -0.041199 | 0.086975 | -0.091553 | -0.11902 | -0.018311 | 0.064087 | -0.13733 | -0.10986 | -0.44403 | -0.36621 | -0.22888 | -0.091553 | 123.4177 | 123.4406 | 61.8027 | -123.4314 | 123.349 | 123.3673 | 61.821 | -123.5962
317.8125 | 123.6603 | -61.8118 | 61.615 | -0.00091566 | 0.0085664 | 0.067031 | 0.0082437 | 0.066183 | -7.6908e-05 | -0.0031189 | -0.0084684 | -0.0024268 | 0.067917 | 0.07276 | -0.0025829 | -0.0063296 | 61.615 | -61.6699 | 0.064087 | -61.8622 | 61.6287 | -61.8576 | -61.8027 | -62.2421 | 0.045776 | -62.1414 | 61.5555 | 61.5738 | -61.734 | -61.94 | -0.045776 | 0.009156 | 0.013733 | 0.14191 | -0.050354 | -0.05951 | 0 | 0.07782 | -0.12817 | -0.059509 | -0.4303 | -0.32959 | -0.20142 | -0.041198 | 123.4406 | 123.4268 | 61.8759 | -123.4177 | 123.3673 | 123.3856 | 61.8576 | -123.555
319.5625 | 123.6923 | -61.8164 | 61.6241 | -0.016174 | 0.007071 | 0.064894 | 0.0054667 | 0.065755 | 0.0014185 | -0.0039733 | -0.0084684 | -0.0032812 | 0.06514 | 0.069769 | -0.00087393 | -0.0076114 | 61.7157 | -61.5921 | 0.045776 | -61.8027 | 61.5417 | -61.8118 | -61.7477 | -62.1368 | 0.091553 | -62.0361 | 61.4502 | 61.5189 | -61.7203 | -61.9034 | 0.004577 | 0.068664 | -0.082398 | 0.2243 | 0.013733 | -0.054931 | 0.091552 | 0.09613 | -0.086975 | -0.17395 | -0.32043 | -0.21973 | -0.13275 | -0.10529 | 123.3582 | 123.5321 | 61.8622 | -123.3719 | 123.2666 | 123.3353 | 61.908 | -123.5275
321.25 | 123.555 | -61.8256 | 61.6974 | -0.0085447 | 0.0060028 | 0.067671 | 0.0033305 | 0.063192 | -0.0047765 | -0.0022643 | 0.0067901 | -0.0052038 | 0.064499 | 0.068915 | -0.0040783 | -0.0069706 | 61.6974 | -61.5784 | 0.045776 | -61.8164 | 61.5463 | -61.821 | -61.7294 | -62.178 | 0.059509 | -62.0453 | 61.4868 | 61.5784 | -61.6882 | -61.9034 | 0.004578 | 0.096131 | -0.15106 | 0.24719 | 0.009156 | -0.086975 | 0 | 0.13733 | -0.077819 | -0.21057 | -0.35248 | -0.21973 | -0.14191 | -0.11902 | 123.3719 | 123.5229 | 61.8713 | -123.4268 | 123.3124 | 123.4039 | 61.8851 | -123.6008
323 | 123.6969 | -61.8073 | 61.5875 | -0.00091566 | 0.0055756 | 0.065108 | 0.0058939 | 0.067892 | 0.00077749 | -0.0031189 | -0.0084684 | -0.0007178 | 0.065354 | 0.072119 | -0.0032237 | -0.0071842 | 61.6562 | -61.6699 | -0.004578 | -61.8576 | 61.5967 | -61.8713 | -61.7889 | -62.178 | 0.054932 | -62.0682 | 61.4685 | 61.5372 | -61.7386 | -61.8988 | -0.064087 | 0.018311 | 0.009156 | 0.13733 | -0.050354 | -0.068665 | 0.068665 | 0.068665 | -0.091553 | -0.11902 | -0.37079 | -0.26093 | -0.16937 | -0.050354 | 123.4039 | 123.4634 | 61.8027 | -123.3765 | 123.2758 | 123.3444 | 61.8622 | -123.4863
324.6875 | 123.5458 | -61.8347 | 61.6745 | -0.00091566 | 0.009848 | 0.069167 | 0.0065347 | 0.068532 | -0.0022131 | -0.0041869 | -0.0084684 | -0.0043494 | 0.063218 | 0.069342 | -0.0023693 | -0.006116 | 61.734 | -61.5417 | 0.15564 | -61.7798 | 61.5784 | -61.8256 | -61.734 | -62.178 | 0.09613 | -62.059 | 61.4914 | 61.5875 | -61.7111 | -61.8988 | 0.009155 | 0.10071 | -0.096131 | 0.29297 | 0.054932 | -0.045776 | 0.059509 | 0.1236 | -0.064087 | -0.18311 | -0.34332 | -0.2243 | -0.16022 | -0.086976 | 123.4131 | 123.5687 | 61.9904 | -123.4085 | 123.3261 | 123.4222 | 61.9308 | -123.5733
326.4375 | 123.6099 | -61.8027 | 61.6928 | -0.00091566 | 0.0083526 | 0.067885 | 0.0065347 | 0.065542 | -0.0043493 | -0.0046143 | -0.023727 | -0.006272 | 0.06514 | 0.070196 | -0.0023693 | -0.0065432 | 61.7386 | -61.528 | 0.10986 | -61.7569 | 61.6379 | -61.7889 | -61.7157 | -62.1048 | 0.11902 | -61.9858 | 61.5189 | 61.5463 | -61.6653 | -61.8896 | 0.013733 | 0.086975 | -0.054932 | 0.27466 | 0.045776 | -0.041199 | 0.045776 | 0.13733 | -0.086975 | -0.17395 | -0.30212 | -0.18311 | -0.096131 | -0.14648 | 123.4406 | 123.5413 | 61.9125 | -123.4085 | 123.3215 | 123.349 | 61.9217 | -123.5825
328.1875 | 123.6969 | -61.8073 | 61.6241 | -0.0085447 | 0.011557 | 0.067244 | 0.0061075 | 0.064687 | 0.0024865 | -0.0029053 | -0.0084684 | -0.002854 | 0.067276 | 0.070624 | -0.0019419 | -0.0097476 | 61.7065 | -61.5829 | 0.041199 | -61.8073 | 61.5555 | -61.8439 | -61.7706 | -62.1185 | 0.07782 | -62.0407 | 61.4594 | 61.496 | -61.7386 | -61.9263 | -0.036621 | 0.036621 | -0.068665 | 0.2243 | 0 | -0.036621 | 0.082397 | 0.068665 | -0.11902 | -0.1648 | -0.31128 | -0.23346 | -0.11444 | -0.12817 | 123.3627 | 123.5138 | 61.8484 | -123.3948 | 123.2666 | 123.3032 | 61.8851 | -123.5504
329.875 | 123.6969 | -61.8118 | 61.615 | -0.016174 | 0.010916 | 0.065962 | 0.0037577 | 0.066183 | 0.0029139 | -0.0020507 | -0.00083936 | -0.0007178 | 0.066849 | 0.071051 | -1.9327e-05 | -0.0084658 | 61.6608 | -61.6287 | 0.091553 | -61.8484 | 61.6013 | -61.8713 | -61.7889 | -62.1826 | 0.091553 | -62.1277 | 61.5097 | 61.5005 | -61.7386 | -61.9629 | -0.059509 | 0.022889 | -0.013733 | 0.18311 | -0.036621 | -0.05951 | 0.045777 | 0.073243 | -0.15106 | -0.10529 | -0.37079 | -0.31586 | -0.16479 | -0.11444 | 123.4131 | 123.4726 | 61.9034 | -123.4039 | 123.3215 | 123.3124 | 61.9034 | -123.5779
331.625 | 123.6832 | -61.8027 | 61.6287 | -0.00091566 | 0.0055756 | 0.06639 | 0.0020487 | 0.069814 | 0.0014185 | -0.0016235 | -0.0084684 | -0.0043494 | 0.064072 | 0.069128 | -0.00023313 | -0.006116 | 61.702 | -61.5463 | 0.050354 | -61.7889 | 61.5326 | -61.821 | -61.7294 | -62.1277 | 0.082397 | -62.0407 | 61.4685 | 61.496 | -61.7111 | -61.9034 | -0.018311 | 0.073242 | -0.09613 | 0.25635 | 0.013733 | -0.059509 | 0.073242 | 0.091552 | -0.10071 | -0.16022 | -0.32501 | -0.23804 | -0.13733 | -0.13275 | 123.3353 | 123.5046 | 61.853 | -123.3582 | 123.2712 | 123.2986 | 61.8851 | -123.5321
333.375 | 123.6694 | -61.8027 | 61.5875 | -0.0085447 | 0.0092072 | 0.065962 | 0.0056803 | 0.065542 | 0.0024865 | -0.0022643 | -0.0084684 | -0.0015722 | 0.06514 | 0.069556 | -0.0023693 | -0.0084658 | 61.6333 | -61.6562 | 0.082397 | -61.8439 | 61.6013 | -61.8713 | -61.7706 | -62.2238 | 0.059509 | -62.1414 | 61.5234 | 61.5555 | -61.7249 | -61.9263 | -0.068665 | 0.032043 | 0.013733 | 0.14648 | -0.041199 | -0.073242 | 0.045777 | 0.077819 | -0.1236 | -0.064087 | -0.42114 | -0.33875 | -0.21515 | -0.032043 | 123.4039 | 123.436 | 61.8851 | -123.3582 | 123.3261 | 123.3582 | 61.8622 | -123.5138
335.0781 | 123.5367 | -61.8393 | 61.6653 | 0.0067138 | 0.00878 | 0.065962 | 0.0063211 | 0.068319 | -0.0058447 | -0.0048279 | -0.00083936 | -0.002854 | 0.064713 | 0.070624 | -0.0042919 | -0.005048 | 61.6287 | -61.6333 | 0.064087 | -61.8347 | 61.6104 | -61.8164 | -61.7569 | -62.2421 | 0.032043 | -62.114 | 61.5692 | 61.5829 | -61.7386 | -61.9125 | 0.022888 | 0.082397 | -0.054931 | 0.20599 | 0.004577 | -0.07782 | -0.036621 | 0.10071 | -0.073243 | -0.09613 | -0.40283 | -0.27466 | -0.20142 | -0.082397 | 123.4497 | 123.468 | 61.9034 | -123.4222 | 123.4085 | 123.4222 | 61.8713 | -123.5779
336.8125 | 123.6008 | -61.7935 | 61.6974 | -0.0085447 | 0.0040802 | 0.067885 | 0.0050393 | 0.067678 | -0.0058447 | -0.0054687 | -0.00083936 | -0.006272 | 0.063858 | 0.067847 | -0.0045055 | -0.006116 | 61.6791 | -61.5784 | 0.022888 | -61.8073 | 61.5967 | -61.8027 | -61.7065 | -62.178 | 0.041199 | -62.0361 | 61.496 | 61.5692 | -61.6928 | -61.8805 | -0.009155 | 0.086975 | -0.10071 | 0.21515 | -0.013733 | -0.10071 | -0.018311 | 0.10071 | -0.086975 | -0.20142 | -0.38452 | -0.24262 | -0.15564 | -0.12817 | 123.3902 | 123.4726 | 61.8164 | -123.4039 | 123.2895 | 123.3627 | 61.8347 | -123.5779
338.5781 | 123.6374 | -61.8027 | 61.5967 | -0.00091566 | 0.0083526 | 0.067031 | 0.0080301 | 0.067678 | 0.00035029 | -0.0046143 | 0.0067901 | -0.0015722 | 0.06749 | 0.069342 | -0.0021557 | -0.0069706 | 61.6287 | -61.6653 | 0.068665 | -61.8439 | 61.6241 | -61.8393 | -61.7661 | -62.2238 | 0.045776 | -62.1414 | 61.5326 | 61.5509 | -61.7249 | -61.9354 | -0.036621 | 0.036621 | 0.027466 | 0.13733 | -0.041199 | -0.07782 | 0.032043 | 0.077819 | -0.13275 | -0.064087 | -0.42114 | -0.33875 | -0.20599 | -0.045777 | 123.4268 | 123.4314 | 61.8713 | -123.3627 | 123.3353 | 123.3536 | 61.8484 | -123.5321
340.2656 | 123.6649 | -61.8118 | 61.5784 | -0.016174 | 0.0055756 | 0.063399 | 0.0026895 | 0.065755 | 0.00099129 | -0.0026917 | 0.01442 | -0.0007178 | 0.067276 | 0.071478 | -0.0010875 | -0.0063296 | 61.6196 | -61.6791 | -0.036621 | -61.8668 | 61.5555 | -61.853 | -61.7844 | -62.1643 | 0.041199 | -62.1048 | 61.4731 | 61.5097 | -61.7065 | -61.9217 | -0.041198 | 0.027466 | -0.022888 | 0.13275 | -0.054931 | -0.082397 | 0.041199 | 0.10529 | -0.10986 | -0.10529 | -0.35248 | -0.29297 | -0.1831 | -0.068664 | 123.3673 | 123.4314 | 61.7752 | -123.3627 | 123.2849 | 123.3215 | 61.853 | -123.5001
342.0156 | 123.5779 | -61.8027 | 61.6699 | -0.00091566 | 0.003653 | 0.067671 | 0.0037577 | 0.065114 | -0.0047765 | -0.0033325 | -0.0084684 | -0.0060584 | 0.063858 | 0.069769 | -0.0040783 | -0.0056888 | 61.6791 | -61.5784 | 0.009155 | -61.8027 | 61.5784 | -61.8118 | -61.7386 | -62.1689 | 0.032043 | -62.0453 | 61.5097 | 61.5692 | -61.6562 | -61.8759 | -0.009156 | 0.064087 | -0.091553 | 0.2243 | 0 | -0.064087 | 0.009155 | 0.14648 | -0.073243 | -0.16022 | -0.36621 | -0.24262 | -0.16937 | -0.10071 | 123.381 | 123.4818 | 61.8118 | -123.4085 | 123.3124 | 123.3719 | 61.8347 | -123.5458
343.7656 | 123.6649 | -61.8073 | 61.5875 | -0.00091566 | 0.008139 | 0.06639 | 0.0041849 | 0.068532 | 0.0020593 | -0.0011963 | -0.0084684 | -0.0002906 | 0.067276 | 0.070624 | -0.0017283 | -0.0082522 | 61.6058 | -61.702 | -0.050354 | -61.8851 | 61.5967 | -61.8805 | -61.7889 | -62.2375 | -0.018311 | -62.1689 | 61.4822 | 61.5234 | -61.7294 | -61.94 | -0.073242 | 0.018311 | 0.009156 | 0.10529 | -0.07782 | -0.096131 | 0.018311 | 0.07782 | -0.13275 | -0.10529 | -0.4303 | -0.36163 | -0.22888 | -0.064087 | 123.4039 | 123.4131 | 61.7569 | -123.3765 | 123.2895 | 123.3307 | 61.7889 | -123.5275
345.4531 | 123.5458 | -61.8118 | 61.6791 | -0.0085447 | 0.0083526 | 0.069808 | 0.0041849 | 0.067464 | -0.0032813 | -0.0020507 | -0.00083936 | -0.0060584 | 0.065567 | 0.070837 | -0.0025829 | -0.0059024 | 61.6928 | -61.5417 | 0.050354 | -61.7844 | 61.5784 | -61.8164 | -61.7249 | -62.1323 | 0.045776 | -62.0224 | 61.4639 | 61.5463 | -61.6791 | -61.8759 | -0.004577 | 0.086975 | -0.10071 | 0.27008 | 0.027466 | -0.059509 | 0.013733 | 0.13275 | -0.064087 | -0.21515 | -0.32043 | -0.21057 | -0.14648 | -0.13275 | 123.3902 | 123.5046 | 61.8622 | -123.4039 | 123.2758 | 123.3582 | 61.8576 | -123.555
347.2031 | 123.5779 | -61.7661 | 61.6562 | -0.00091566 | 0.0074982 | 0.067885 | 0.0046121 | 0.06661 | -0.0032813 | -0.0050415 | 0.0067901 | -0.0041358 | 0.065354 | 0.068274 | -0.0036509 | -0.0073978 | 61.7569 | -61.4685 | 0.14648 | -61.7294 | 61.5646 | -61.7706 | -61.702 | -62.0728 | 0.13733 | -61.9675 | 61.496 | 61.5326 | -61.6425 | -61.8759 | -0.004578 | 0.064087 | -0.091553 | 0.29755 | 0.036621 | -0.027466 | 0.10071 | 0.1236 | -0.10986 | -0.16022 | -0.3067 | -0.20142 | -0.091552 | -0.1236 | 123.3307 | 123.5229 | 61.9125 | -123.3582 | 123.262 | 123.2986 | 61.9034 | -123.5321
348.9062 | 123.5092 | -61.8073 | 61.6562 | -0.00091566 | 0.0079254 | 0.065749 | 0.0078165 | 0.066823 | -0.0011451 | -0.0029053 | -0.0084684 | -0.0049902 | 0.066849 | 0.069983 | -0.0036509 | -0.0071842 | 61.7249 | -61.5189 | 0.16479 | -61.7615 | 61.5829 | -61.7935 | -61.7294 | -62.1506 | 0.10529 | -62.0361 | 61.4914 | 61.5372 | -61.702 | -61.9125 | 0.013733 | 0.07782 | -0.073242 | 0.28839 | 0.045776 | -0.032044 | 0.068665 | 0.10529 | -0.10529 | -0.16479 | -0.34332 | -0.22888 | -0.1236 | -0.11902 | 123.3902 | 123.5321 | 61.972 | -123.3856 | 123.2986 | 123.3444 | 61.9125 | -123.5687
350.6562 | 123.5275 | -61.7889 | 61.6608 | -0.0085447 | 0.0094208 | 0.066176 | 0.0061075 | 0.069387 | -0.0017859 | -0.0050415 | -0.0084684 | -0.0060584 | 0.06514 | 0.067847 | -0.0025829 | -0.0082522 | 61.7477 | -61.4685 | 0.17853 | -61.7386 | 61.5555 | -61.8118 | -61.6882 | -62.0819 | 0.16022 | -61.9812 | 61.5051 | 61.5326 | -61.6653 | -61.8393 | -0.022889 | 0.10071 | -0.10529 | 0.32043 | 0.050354 | -0.050354 | 0.086975 | 0.1236 | -0.050354 | -0.15564 | -0.29297 | -0.19226 | -0.14191 | -0.12817 | 123.3444 | 123.5367 | 61.9675 | -123.349 | 123.2941 | 123.3215 | 61.9492 | -123.5001
352.4062 | 123.5184 | -61.8027 | 61.6562 | 0.0067138 | 0.009848 | 0.068526 | 0.0063211 | 0.067251 | 0.0020593 | -0.0039733 | -0.00083936 | -0.002854 | 0.066849 | 0.072333 | -0.0034373 | -0.0063296 | 61.6425 | -61.6058 | 0.091553 | -61.8164 | 61.6196 | -61.8164 | -61.7294 | -62.2055 | 0.059509 | -62.0956 | 61.5326 | 61.5555 | -61.6974 | -61.9171 | -0.013733 | 0.073242 | -0.036621 | 0.19684 | -0.013733 | -0.086975 | -0.013733 | 0.10529 | -0.11444 | -0.1236 | -0.40283 | -0.29297 | -0.17853 | -0.10071 | 123.4222 | 123.4451 | 61.8942 | -123.3856 | 123.3353 | 123.3582 | 61.8622 | -123.5733
354.1094 | 123.555 | -61.7844 | 61.6241 | -0.00091566 | 0.005362 | 0.068953 | 0.0039713 | 0.064046 | -0.0019995 | -0.0029053 | 0.01442 | -7.6996e-05 | 0.062363 | 0.070837 | -0.0015147 | -0.0086796 | 61.6241 | -61.6196 | 0.059509 | -61.8484 | 61.6104 | -61.8347 | -61.7752 | -62.2101 | 0.032043 | -62.1185 | 61.5463 | 61.5555 | -61.7111 | -61.908 | -0.050354 | 0.009155 | -0.013733 | 0.16479 | -0.064087 | -0.073242 | 0 | 0.073242 | -0.1236 | -0.07782 | -0.42572 | -0.33417 | -0.21057 | -0.068665 | 123.3948 | 123.4085 | 61.8439 | -123.3994 | 123.3307 | 123.3398 | 61.8164 | -123.5321
355.875 | 123.6465 | -61.7752 | 61.5784 | -0.00091566 | 0.010489 | 0.064681 | 0.0063211 | 0.068532 | 0.00099129 | -0.0033325 | -0.0084684 | -7.6996e-05 | 0.064286 | 0.071692 | -0.0023693 | -0.0082522 | 61.6196 | -61.647 | 0.059509 | -61.8301 | 61.6013 | -61.8484 | -61.7661 | -62.178 | 0.045776 | -62.1323 | 61.5143 | 61.5234 | -61.6882 | -61.9446 | -0.073242 | 0.009156 | 0.022888 | 0.12817 | -0.054931 | -0.064087 | 0.041199 | 0.086976 | -0.16937 | -0.064087 | -0.40283 | -0.35706 | -0.18768 | -0.054932 | 123.3765 | 123.3948 | 61.8347 | -123.3444 | 123.2895 | 123.2986 | 61.821 | -123.5229
357.6406 | 123.5458 | -61.7889 | 61.647 | -0.00091566 | 0.0083526 | 0.068526 | 0.0080301 | 0.068319 | -0.0034949 | -0.0020507 | -0.00083936 | -0.0049902 | 0.06514 | 0.071692 | -0.0070689 | -0.0065432 | 61.7294 | -61.4822 | 0.16022 | -61.7294 | 61.6013 | -61.7844 | -61.6882 | -62.0865 | 0.16022 | -61.9583 | 61.4822 | 61.5234 | -61.6516 | -61.853 | 0.004577 | 0.10071 | -0.045777 | 0.3067 | 0.059509 | -0.041199 | 0.082397 | 0.13733 | -0.064087 | -0.16479 | -0.29755 | -0.16937 | -0.10529 | -0.1236 | 123.3902 | 123.5184 | 61.9492 | -123.3353 | 123.2712 | 123.3124 | 61.9492 | -123.5001
359.3906 | 123.5962 | -61.8301 | 61.5646 | -0.016174 | 0.010489 | 0.065322 | -8.7544e-05 | 0.067251 | 0.0016321 | -0.0018371 | 0.0067901 | -0.0002906 | 0.06514 | 0.072974 | -0.00023313 | -0.0076114 | 61.5921 | -61.6974 | -0.013733 | -61.8713 | 61.5601 | -61.8759 | -61.7935 | -62.2284 | -0.009155 | -62.1735 | 61.496 | 61.5417 | -61.7386 | -61.9492 | -0.045777 | 0.036621 | -0.004577 | 0.13275 | -0.041199 | -0.07782 | 0.027466 | 0.091553 | -0.11902 | -0.068664 | -0.39825 | -0.34332 | -0.2243 | -0.022888 | 123.3902 | 123.4222 | 61.8164 | -123.3582 | 123.3261 | 123.3719 | 61.821 | -123.5138
361.0781 | 123.5184 | -61.7889 | 61.6196 | -0.00091566 | 0.0074982 | 0.067671 | 0.0046121 | 0.063405 | -0.0022131 | -0.0037597 | -0.00083936 | -0.0024268 | 0.063858 | 0.06806 | -0.0042919 | -0.0056888 | 61.6241 | -61.6058 | 0.086975 | -61.8256 | 61.5601 | -61.8439 | -61.7477 | -62.1964 | 0.050354 | -62.0911 | 61.5234 | 61.5875 | -61.6928 | -61.8942 | -0.054932 | 0.041198 | -0.059509 | 0.1831 | -0.036622 | -0.07782 | 0.004578 | 0.09613 | -0.10529 | -0.096131 | -0.40741 | -0.30212 | -0.19684 | -0.032044 | 123.349 | 123.4131 | 61.8759 | -123.3673 | 123.3124 | 123.3765 | 61.8393 | -123.5138
362.8438 | 123.5321 | -61.7844 | 61.6333 | -0.016174 | 0.0096344 | 0.065962 | 0.0063211 | 0.067251 | -0.0032813 | -0.0052551 | -0.00083936 | -0.0060584 | 0.064927 | 0.067419 | -0.0053599 | -0.006116 | 61.7294 | -61.4639 | 0.16479 | -61.7386 | 61.5646 | -61.7661 | -61.6745 | -62.0956 | 0.17395 | -61.9629 | 61.4777 | 61.5417 | -61.6653 | -61.8576 | 0.018311 | 0.10986 | -0.068665 | 0.32043 | 0.045777 | -0.064086 | 0.09613 | 0.11902 | -0.073242 | -0.15564 | -0.31128 | -0.17853 | -0.10529 | -0.091553 | 123.349 | 123.5138 | 61.9492 | -123.3078 | 123.262 | 123.3261 | 61.9583 | -123.4909
364.5938 | 123.5825 | -61.7935 | 61.6425 | -0.016174 | 0.0060028 | 0.067244 | 0.0029031 | 0.067464 | -0.0011451 | -0.0022643 | -0.00083936 | -0.0052038 | 0.063431 | 0.069342 | -0.0015147 | -0.006116 | 61.6837 | -61.5372 | 0.059509 | -61.7661 | 61.5234 | -61.8118 | -61.7523 | -62.1048 | 0.09613 | -62.0178 | 61.4548 | 61.4914 | -61.6974 | -61.8759 | -0.018311 | 0.041199 | -0.11902 | 0.25635 | 0.027466 | -0.013733 | 0.041199 | 0.09613 | -0.082398 | -0.18768 | -0.31128 | -0.2243 | -0.14191 | -0.15106 | 123.317 | 123.4772 | 61.853 | -123.3948 | 123.2483 | 123.2849 | 61.8896 | -123.5184
366.2656 | 123.5184 | -61.8027 | 61.6425 | -0.0085447 | 0.009848 | 0.067671 | 0.0071757 | 0.067037 | -0.00093131 | -0.0039733 | -0.0084684 | -0.0032812 | 0.066849 | 0.069128 | -0.0047191 | -0.0073978 | 61.6608 | -61.5738 | 0.11902 | -61.7844 | 61.5692 | -61.8027 | -61.7477 | -62.178 | 0.045776 | -62.0728 | 61.528 | 61.5372 | -61.6837 | -61.8942 | 0 | 0.054931 | -0.073242 | 0.22888 | 0.01831 | -0.036621 | 0.018311 | 0.11902 | -0.091553 | -0.11444 | -0.37537 | -0.27008 | -0.17853 | -0.10529 | 123.3719 | 123.4634 | 61.9217 | -123.3902 | 123.3307 | 123.3398 | 61.8484 | -123.5367
368.0156 | 123.5504 | -61.7706 | 61.6837 | -0.0085447 | 0.005362 | 0.067458 | 0.0056803 | 0.067037 | -0.0028539 | -0.0035461 | -0.0084684 | -0.0047766 | 0.064499 | 0.06806 | -0.0047191 | -0.0063296 | 61.6196 | -61.5555 | 0.018311 | -61.7752 | 61.5692 | -61.7935 | -61.7111 | -62.1414 | 0.032043 | -62.0224 | 61.4822 | 61.5189 | -61.6425 | -61.8713 | -0.022888 | 0.059509 | -0.11444 | 0.21515 | -0.004578 | -0.064087 | -0.064087 | 0.12817 | -0.10071 | -0.20142 | -0.37079 | -0.25177 | -0.15106 | -0.1648 | 123.3398 | 123.3902 | 61.7889 | -123.3948 | 123.2529 | 123.2895 | 61.8027 | -123.555
369.7031 | 123.6237 | -61.7844 | 61.6058 | -0.016174 | 0.010489 | 0.066817 | 0.0039713 | 0.066823 | 0.00077749 | -0.0039733 | -0.00083936 | -0.0043494 | 0.065781 | 0.068915 | -0.00087393 | -0.007825 | 61.6837 | -61.5555 | 0.045776 | -61.7661 | 61.5143 | -61.7981 | -61.7386 | -62.0956 | 0.086975 | -62.0087 | 61.4456 | 61.4639 | -61.6882 | -61.8942 | -0.013733 | 0.045777 | -0.091553 | 0.22888 | 0.018311 | -0.027466 | 0.07782 | 0.096131 | -0.10986 | -0.16022 | -0.31128 | -0.2243 | -0.11444 | -0.14191 | 123.2986 | 123.468 | 61.8301 | -123.3444 | 123.23 | 123.2483 | 61.8713 | -123.5001
371.4531 | 123.5687 | -61.7889 | 61.6333 | -0.0085447 | 0.0066438 | 0.065108 | 0.0018351 | 0.067251 | 0.00013669 | -0.0033325 | 0.0067901 | -0.0043494 | 0.061295 | 0.069342 | -0.0015147 | -0.0069706 | 61.702 | -61.528 | 0.059509 | -61.7706 | 61.5097 | -61.8118 | -61.7203 | -62.0911 | 0.086975 | -61.9995 | 61.4731 | 61.5005 | -61.6837 | -61.8805 | -0.022889 | 0.068664 | -0.1236 | 0.26092 | 0.01831 | -0.050354 | 0.068664 | 0.10528 | -0.091553 | -0.16022 | -0.30212 | -0.21057 | -0.11902 | -0.13275 | 123.2986 | 123.4909 | 61.8484 | -123.3536 | 123.262 | 123.2895 | 61.8759 | -123.5138
373.1562 | 123.5413 | -61.7569 | 61.647 | -0.0085447 | 0.010062 | 0.06938 | 0.0056803 | 0.068746 | -0.0019995 | -0.0054687 | -0.0084684 | -0.0056312 | 0.065995 | 0.067847 | -0.0032237 | -0.0080386 | 61.7386 | -61.441 | 0.13733 | -61.7203 | 61.5555 | -61.7752 | -61.6882 | -62.0682 | 0.15106 | -61.9446 | 61.4639 | 61.5234 | -61.6196 | -61.853 | -0.018311 | 0.068665 | -0.091553 | 0.31586 | 0.036621 | -0.032044 | 0.091552 | 0.13733 | -0.09613 | -0.18311 | -0.31128 | -0.18768 | -0.091553 | -0.1236 | 123.3124 | 123.4955 | 61.8942 | -123.3353 | 123.2208 | 123.2803 | 61.908 | -123.5001
374.9062 | 123.5413 | -61.7889 | 61.6333 | -0.0085447 | 0.003653 | 0.065535 | 0.0037577 | 0.068532 | 0.00035029 | -0.0035461 | -0.00083936 | -0.0064856 | 0.061722 | 0.07041 | -0.00023313 | -0.0076114 | 61.6974 | -61.5189 | 0.045776 | -61.7615 | 61.4868 | -61.8256 | -61.6928 | -62.0956 | 0.07782 | -61.9949 | 61.4731 | 61.4914 | -61.6791 | -61.8759 | -0.036622 | 0.09613 | -0.14649 | 0.27008 | 0.027465 | -0.068665 | 0.064087 | 0.10986 | -0.086976 | -0.16022 | -0.3067 | -0.20599 | -0.11902 | -0.14191 | 123.2758 | 123.4863 | 61.8347 | -123.3261 | 123.262 | 123.2803 | 61.8668 | -123.5092
376.5938 | 123.5321 | -61.7798 | 61.6241 | -0.00091566 | 0.0085664 | 0.066603 | 0.0061075 | 0.06661 | -0.0032813 | -0.0026917 | -0.0084684 | -0.0032812 | 0.064927 | 0.06806 | -0.0032237 | -0.0080386 | 61.734 | -61.4502 | 0.13275 | -61.7157 | 61.5555 | -61.7706 | -61.6837 | -62.0499 | 0.13275 | -61.9308 | 61.496 | 61.5372 | -61.647 | -61.8256 | 0.009155 | 0.09613 | -0.068665 | 0.32959 | 0.064087 | -0.032043 | 0.10986 | 0.13275 | -0.045777 | -0.12817 | -0.27008 | -0.15106 | -0.10529 | -0.086976 | 123.3353 | 123.5138 | 61.9125 | -123.3078 | 123.2758 | 123.317 | 61.9125 | -123.4497
378.3438 | 123.5458 | -61.7523 | 61.6425 | -0.00091566 | 0.0077118 | 0.067885 | 0.0088847 | 0.067037 | -0.0019995 | -0.0041869 | -0.0084684 | -0.0034948 | 0.065781 | 0.069769 | -0.0036509 | -0.009534 | 61.6699 | -61.5372 | 0.050354 | -61.7706 | 61.5829 | -61.8027 | -61.6837 | -62.1002 | 0.091553 | -61.9766 | 61.5005 | 61.5097 | -61.6379 | -61.8713 | -0.050354 | 0.068664 | -0.059509 | 0.21515 | -0.018311 | -0.086975 | 0.027466 | 0.11444 | -0.11902 | -0.14191 | -0.3479 | -0.22431 | -0.10529 | -0.13275 | 123.3353 | 123.4222 | 61.8027 | -123.3261 | 123.2529 | 123.262 | 61.8439 | -123.5138
380.0938 | 123.5229 | -61.7752 | 61.6516 | -0.00091566 | 0.008139 | 0.065962 | 0.0080301 | 0.067892 | 0.0027003 | -0.0050415 | -0.00083936 | -0.0007178 | 0.067276 | 0.071265 | -0.0032237 | -0.007825 | 61.615 | -61.6013 | 0.064087 | -61.8164 | 61.5921 | -61.8256 | -61.7477 | -62.1872 | 0.045776 | -62.1094 | 61.5326 | 61.5234 | -61.702 | -61.8988 | -0.050354 | 0.027466 | -0.059509 | 0.17395 | -0.041198 | -0.068664 | -0.036621 | 0.073243 | -0.1236 | -0.11902 | -0.41199 | -0.33417 | -0.21057 | -0.12817 | 123.3673 | 123.3902 | 61.8393 | -123.3994 | 123.3078 | 123.2986 | 61.821 | -123.5504
381.8438 | 123.6053 | -61.8027 | 61.5921 | -0.00091566 | 0.010703 | 0.066817 | 0.0039713 | 0.069387 | 0.0050501 | -0.0031189 | -0.0084684 | 0.0012048 | 0.067276 | 0.071478 | -0.00066033 | -0.0063296 | 61.5555 | -61.6928 | -0.032043 | -61.8484 | 61.5601 | -61.8347 | -61.7661 | -62.2284 | -0.018311 | -62.1597 | 61.4594 | 61.4868 | -61.7249 | -61.9308 | -0.032044 | 0.036621 | -0.032043 | 0.10986 | -0.045777 | -0.082398 | -0.036621 | 0.077819 | -0.12817 | -0.13275 | -0.42572 | -0.35706 | -0.22888 | -0.10529 | 123.3627 | 123.3582 | 61.7706 | -123.3582 | 123.262 | 123.2895 | 61.7844 | -123.5229
383.5156 | 123.4909 | -61.7615 | 61.6425 | -0.0085447 | 0.0077118 | 0.068953 | 0.0061075 | 0.065755 | -0.0045629 | -0.0031189 | 0.0067901 | -0.0060584 | 0.066208 | 0.069342 | -0.0025829 | -0.0048342 | 61.7203 | -61.4639 | 0.16937 | -61.7065 | 61.5463 | -61.7477 | -61.6745 | -62.0544 | 0.16479 | -61.9308 | 61.5005 | 61.5326 | -61.6562 | -61.8484 | 0.013733 | 0.086975 | -0.09613 | 0.29755 | 0.054932 | -0.032043 | 0.07782 | 0.10529 | -0.086975 | -0.14191 | -0.29297 | -0.16937 | -0.082397 | -0.10986 | 123.3078 | 123.4818 | 61.9308 | -123.317 | 123.262 | 123.2941 | 61.9263 | -123.4909
385.2656 | 123.4909 | -61.7752 | 61.6653 | -0.0085447 | 0.0072846 | 0.06639 | 0.00055326 | 0.068532 | -0.0026403 | -0.0031189 | -0.00083936 | -0.0043494 | 0.062149 | 0.068274 | -0.0019419 | -0.0069706 | 61.6837 | -61.496 | 0.041199 | -61.7569 | 61.5417 | -61.8027 | -61.6928 | -62.0682 | 0.07782 | -61.9995 | 61.441 | 61.4822 | -61.6333 | -61.853 | -0.027465 | 0.082398 | -0.1236 | 0.27924 | 0.018311 | -0.064087 | 0.018311 | 0.14191 | -0.077819 | -0.2243 | -0.29297 | -0.2243 | -0.14649 | -0.1831 | 123.317 | 123.4589 | 61.8164 | -123.3582 | 123.2162 | 123.2574 | 61.853 | -123.5184
387 | 123.5046 | -61.7889 | 61.615 | -0.00091566 | 0.0025848 | 0.064894 | 0.0061075 | 0.065114 | -0.0026403 | -0.0037597 | -0.00083936 | -0.0066992 | 0.063431 | 0.071265 | -0.0027965 | -0.0073978 | 61.6699 | -61.5372 | 0.022888 | -61.7661 | 61.5372 | -61.7661 | -61.7157 | -62.1094 | 0.032043 | -62.0316 | 61.4914 | 61.5097 | -61.6425 | -61.8668 | 0.022888 | 0.073242 | -0.07782 | 0.25177 | 0.022888 | -0.050354 | 0.054932 | 0.14648 | -0.07782 | -0.1236 | -0.32044 | -0.24262 | -0.16479 | -0.10529 | 123.3261 | 123.4589 | 61.8118 | -123.3307 | 123.2803 | 123.2986 | 61.821 | -123.4818
388.6719 | 123.5458 | -61.7523 | 61.647 | -0.00091566 | 0.00643 | 0.067458 | 0.0069621 | 0.066396 | -0.0026403 | -0.0052551 | -0.00083936 | -0.0047766 | 0.064499 | 0.068487 | -0.0038647 | -0.0056888 | 61.6562 | -61.5555 | 0.032043 | -61.7615 | 61.5875 | -61.7752 | -61.702 | -62.1277 | 0.054932 | -61.9949 | 61.4777 | 61.528 | -61.6196 | -61.8576 | -0.022889 | 0.050354 | -0.05951 | 0.19684 | -0.009156 | -0.05951 | 0.009155 | 0.13275 | -0.10529 | -0.16937 | -0.37537 | -0.24262 | -0.13733 | -0.11902 | 123.3398 | 123.4085 | 61.7844 | -123.349 | 123.23 | 123.2803 | 61.8073 | -123.5046
390.4219 | 123.6191 | -61.7798 | 61.5646 | 0.0067138 | 0.0094208 | 0.065962 | 0.0020487 | 0.06426 | 0.0046229 | -0.0037597 | -0.0084684 | 0.000564 | 0.063218 | 0.07041 | 0.00019427 | -0.0067568 | 61.5829 | -61.702 | -0.050354 | -61.8484 | 61.5326 | -61.853 | -61.7661 | -62.1918 | -0.027466 | -62.1277 | 61.4822 | 61.5234 | -61.6974 | -61.9034 | -0.073242 | 0.013733 | -0.032043 | 0.07782 | -0.068665 | -0.082398 | 0.018311 | 0.082397 | -0.1236 | -0.082397 | -0.41199 | -0.3479 | -0.2243 | -0.041199 | 123.3124 | 123.3627 | 61.7294 | -123.3307 | 123.262 | 123.3032 | 61.7523 | -123.468
392.1094 | 123.5046 | -61.8118 | 61.5967 | 0.0067138 | 0.0042938 | 0.068099 | 0.0026895 | 0.067464 | -0.0013587 | -0.0033325 | -0.0084684 | -0.0032812 | 0.061722 | 0.070196 | -0.0013011 | -0.0073978 | 61.6928 | -61.5143 | 0.054932 | -61.7569 | 61.5189 | -61.8118 | -61.6974 | -62.0682 | 0.10071 | -61.972 | 61.4182 | 61.4822 | -61.6653 | -61.8576 | 0 | 0.11444 | -0.07782 | 0.29755 | 0.054932 | -0.059509 | 0.09613 | 0.14649 | -0.045776 | -0.17853 | -0.25635 | -0.16022 | -0.11444 | -0.11444 | 123.3307 | 123.5046 | 61.8668 | -123.2941 | 123.23 | 123.2941 | 61.9125 | -123.4543
393.8594 | 123.5916 | -61.7935 | 61.5738 | -0.0085447 | 0.012198 | 0.067244 | 0.0065347 | 0.065542 | 0.0039819 | -0.0014099 | 0.0067901 | -0.0002906 | 0.067276 | 0.068487 | -0.00066033 | -0.0086796 | 61.5555 | -61.6974 | -0.032043 | -61.8484 | 61.5601 | -61.8484 | -61.7523 | -62.2192 | -0.022888 | -62.1552 | 61.4639 | 61.5051 | -61.7432 | -61.94 | -0.054932 | 0.041199 | -0.013733 | 0.09613 | -0.054932 | -0.096131 | -0.018311 | 0.050354 | -0.14648 | -0.10986 | -0.42572 | -0.36163 | -0.21515 | -0.068665 | 123.3536 | 123.349 | 61.7615 | -123.3261 | 123.2574 | 123.2986 | 61.7706 | -123.5138
395.5469 | 123.4726 | -61.7661 | 61.647 | -0.00091566 | 0.010916 | 0.06874 | 0.01038 | 0.0696 | -0.0026403 | -0.0029053 | -0.0084684 | -0.0039222 | 0.067917 | 0.071692 | -0.0051463 | -0.0082522 | 61.6882 | -61.4777 | 0.15564 | -61.7386 | 61.5509 | -61.7752 | -61.6928 | -62.1094 | 0.086975 | -62.0178 | 61.5005 | 61.5463 | -61.6837 | -61.8622 | -0.009156 | 0.073242 | -0.096131 | 0.28839 | 0.027466 | -0.045776 | 0.041198 | 0.082397 | -0.096131 | -0.14648 | -0.34332 | -0.25177 | -0.15564 | -0.10071 | 123.317 | 123.4543 | 61.9217 | -123.3398 | 123.2666 | 123.3124 | 61.853 | -123.5092
397.2969 | 123.555 | -61.7798 | 61.5967 | -0.00091566 | 0.007071 | 0.064894 | 0.0031167 | 0.067251 | -0.0011451 | -0.0018371 | -0.0084684 | -0.0049902 | 0.066636 | 0.07276 | -0.0038647 | -0.0065432 | 61.6608 | -61.5097 | 0.045776 | -61.7569 | 61.5005 | -61.7889 | -61.7111 | -62.059 | 0.091553 | -61.9858 | 61.4182 | 61.4685 | -61.6928 | -61.8622 | -0.009155 | 0.068664 | -0.096131 | 0.27008 | 0.022888 | -0.045776 | 0.064087 | 0.086975 | -0.082398 | -0.17853 | -0.27924 | -0.20599 | -0.1236 | -0.12817 | 123.2803 | 123.4406 | 61.8256 | -123.3078 | 123.1979 | 123.2483 | 61.8713 | -123.4589
399.0469 | 123.4726 | -61.7477 | 61.647 | 0.0067138 | 0.0072846 | 0.067885 | 0.0086709 | 0.064474 | -0.0037085 | -0.0046143 | -0.00083936 | -0.0060584 | 0.065567 | 0.069556 | -0.0027965 | -0.0067568 | 61.647 | -61.5417 | 0.032043 | -61.7386 | 61.5463 | -61.7706 | -61.6928 | -62.1277 | 0.032043 | -62.0041 | 61.4639 | 61.5372 | -61.6287 | -61.8484 | -0.022888 | 0.054932 | -0.10071 | 0.20599 | 0.009156 | -0.045776 | 0 | 0.11902 | -0.10071 | -0.18311 | -0.37994 | -0.25635 | -0.15564 | -0.10986 | 123.2941 | 123.3948 | 61.7798 | -123.3398 | 123.2117 | 123.2849 | 61.7798 | -123.4955
400.7969 | 123.468 | -61.7798 | 61.6013 | -0.0085447 | 0.0079254 | 0.067031 | 0.0071757 | 0.067678 | -0.00029051 | -0.0037597 | -0.00083936 | -0.0054174 | 0.064713 | 0.070624 | -0.0030101 | -0.0076114 | 61.6928 | -61.4914 | 0.14648 | -61.7111 | 61.5509 | -61.7615 | -61.702 | -62.1002 | 0.10986 | -61.9995 | 61.4731 | 61.496 | -61.647 | -61.8484 | 0.01831 | 0.07782 | -0.050354 | 0.28839 | 0.068664 | -0.009156 | 0.091553 | 0.13275 | -0.068665 | -0.12817 | -0.32044 | -0.21973 | -0.15106 | -0.10528 | 123.3307 | 123.4726 | 61.9263 | -123.3032 | 123.2529 | 123.2758 | 61.8896 | -123.4497
402.4844 | 123.5962 | -61.7569 | 61.5875 | -0.0085447 | 0.005362 | 0.067244 | 0.0022623 | 0.070669 | 0.00077749 | -0.0016235 | -0.00083936 | -0.0032812 | 0.065567 | 0.071478 | -0.0010875 | -0.0093204 | 61.6608 | -61.5143 | 0.050354 | -61.7432 | 61.496 | -61.7981 | -61.7157 | -62.0728 | 0.09613 | -62.0087 | 61.4365 | 61.4456 | -61.6882 | -61.8668 | -0.041199 | 0.041199 | -0.091552 | 0.24262 | 0.013733 | -0.027466 | 0.073243 | 0.068665 | -0.10986 | -0.15106 | -0.31586 | -0.25177 | -0.14191 | -0.14191 | 123.2529 | 123.4177 | 61.8073 | -123.3032 | 123.1934 | 123.2025 | 61.853 | -123.4543
404.2344 | 123.4772 | -61.7752 | 61.6241 | -0.00091566 | 0.0079254 | 0.067885 | 0.0056803 | 0.067892 | -0.00029051 | -0.0052551 | -0.00083936 | -0.0037086 | 0.063858 | 0.069769 | -0.00044673 | -0.007825 | 61.6699 | -61.4777 | 0.13733 | -61.7294 | 61.5555 | -61.7477 | -61.702 | -62.1185 | 0.09613 | -62.0132 | 61.4914 | 61.496 | -61.6608 | -61.8713 | 0.027466 | 0.073243 | -0.068665 | 0.29755 | 0.045777 | -0.027466 | 0.045776 | 0.11444 | -0.09613 | -0.13275 | -0.34332 | -0.23804 | -0.14191 | -0.12817 | 123.3307 | 123.4451 | 61.9125 | -123.3261 | 123.2666 | 123.2712 | 61.8713 | -123.4955
405.9844 | 123.5596 | -61.7386 | 61.5601 | -0.0085447 | 0.0083526 | 0.068312 | 0.0048257 | 0.066183 | 0.00077749 | -0.0037597 | -0.0084684 | -0.0005042 | 0.065567 | 0.071051 | -0.0013011 | -0.0080386 | 61.5875 | -61.6013 | 0.068665 | -61.7889 | 61.5829 | -61.8027 | -61.7386 | -62.1552 | 0.050354 | -62.0865 | 61.5005 | 61.5326 | -61.6837 | -61.9034 | -0.064087 | 0 | 0.022888 | 0.13733 | -0.050354 | -0.050354 | 0.027465 | 0.054931 | -0.1648 | -0.05951 | -0.41656 | -0.3479 | -0.18311 | -0.027466 | 123.3215 | 123.3261 | 61.8073 | -123.2986 | 123.2391 | 123.2712 | 61.7889 | -123.4634
407.6719 | 123.5916 | -61.7615 | 61.5097 | -0.0085447 | 0.010062 | 0.063399 | 0.0065347 | 0.065328 | 0.0014185 | -0.0018371 | -0.00083936 | 0.0003504 | 0.064286 | 0.070196 | -0.0010875 | -0.0097476 | 61.6058 | -61.5875 | 0.091553 | -61.7844 | 61.5921 | -61.8164 | -61.7432 | -62.1277 | 0.091553 | -62.0544 | 61.4868 | 61.5051 | -61.6974 | -61.9034 | -0.054931 | 0.018311 | 0.082397 | 0.17395 | -0.022888 | -0.041199 | 0.09613 | 0.064087 | -0.14191 | -0.022889 | -0.36621 | -0.29297 | -0.15106 | -0.004578 | 123.3536 | 123.3673 | 61.853 | -123.2529 | 123.2483 | 123.2666 | 61.853 | -123.4131
409.4219 | 123.5916 | -61.7569 | 61.5646 | 0.0067138 | 0.010275 | 0.065535 | 0.0020487 | 0.065114 | -0.0013587 | -0.0026917 | -0.00083936 | -7.6996e-05 | 0.065567 | 0.068701 | -0.0015147 | -0.006116 | 61.6196 | -61.5601 | 0.091553 | -61.7752 | 61.5509 | -61.8073 | -61.7432 | -62.1368 | 0.10986 | -62.0499 | 61.4594 | 61.5051 | -61.6791 | -61.8988 | -0.050354 | 0.013733 | -0.013733 | 0.19684 | -0.018311 | -0.032044 | 0.054932 | 0.07782 | -0.14191 | -0.10529 | -0.37994 | -0.29297 | -0.15106 | -0.059509 | 123.3078 | 123.3765 | 61.8484 | -123.3078 | 123.2162 | 123.262 | 61.8668 | -123.4634
411.1719 | 123.5184 | -61.734 | 61.6379 | -0.00091566 | 0.0057892 | 0.067671 | 0.0058939 | 0.065755 | -0.0062719 | -0.0048279 | -0.016098 | -0.0066992 | 0.064072 | 0.069769 | -0.0060009 | -0.0059024 | 61.702 | -61.4227 | 0.1236 | -61.702 | 61.5601 | -61.7386 | -61.6516 | -62.0499 | 0.14648 | -61.8851 | 61.4594 | 61.5005 | -61.6058 | -61.8164 | -0.004577 | 0.082398 | -0.077819 | 0.31128 | 0.032044 | -0.050354 | 0.064087 | 0.12817 | -0.082397 | -0.17853 | -0.31586 | -0.15106 | -0.068665 | -0.13733 | 123.2941 | 123.436 | 61.8576 | -123.2895 | 123.1934 | 123.2346 | 61.8805 | -123.4543
412.9062 | 123.468 | -61.7798 | 61.6058 | 0.0067138 | 0.010275 | 0.070235 | 0.0061075 | 0.067678 | -0.0022131 | -0.0044007 | -0.00083936 | -0.0032812 | 0.063645 | 0.069128 | -0.0040783 | -0.005048 | 61.5967 | -61.5692 | 0.082397 | -61.7706 | 61.5784 | -61.7752 | -61.6791 | -62.1643 | 0.054932 | -62.0499 | 61.5143 | 61.5646 | -61.6608 | -61.8622 | 0.004577 | 0.10071 | -0.027466 | 0.21057 | 0.009155 | -0.091553 | -0.009155 | 0.11902 | -0.082398 | -0.091553 | -0.38452 | -0.27008 | -0.18768 | -0.041199 | 123.3582 | 123.3765 | 61.8622 | -123.2849 | 123.2941 | 123.3444 | 61.8347 | -123.468
414.5781 | 123.5458 | -61.7706 | 61.5738 | 0.0067138 | 0.01113 | 0.063826 | 0.0065347 | 0.065755 | 0.0022729 | -0.0050415 | -0.00083936 | -0.0043494 | 0.066208 | 0.069342 | -0.0030101 | -0.006116 | 61.5417 | -61.6333 | -0.027466 | -61.8301 | 61.5738 | -61.8301 | -61.7432 | -62.2055 | -0.018311 | -62.1185 | 61.5005 | 61.5005 | -61.7249 | -61.8942 | -0.059509 | 0.027466 | 0 | 0.13733 | -0.059509 | -0.086975 | -0.032044 | 0.045776 | -0.1236 | -0.073243 | -0.43488 | -0.3479 | -0.2243 | -0.073243 | 123.3444 | 123.3124 | 61.7432 | -123.317 | 123.2712 | 123.2712 | 61.7523 | -123.468
416.3281 | 123.5916 | -61.7432 | 61.5555 | -0.00091566 | 0.0092072 | 0.064894 | 0.0041849 | 0.064687 | -0.00093131 | -0.0024779 | -0.00083936 | -0.0034948 | 0.065567 | 0.07041 | -0.0021557 | -0.0076114 | 61.6058 | -61.5738 | 0.004578 | -61.7706 | 61.5326 | -61.7935 | -61.702 | -62.0956 | 0.068665 | -61.9995 | 61.4273 | 61.4914 | -61.6425 | -61.8576 | -0.050354 | 0.041199 | -0.022888 | 0.16937 | -0.027466 | -0.068665 | 0.050354 | 0.10071 | -0.11444 | -0.12817 | -0.35248 | -0.25635 | -0.14191 | -0.064087 | 123.2758 | 123.349 | 61.7477 | -123.2574 | 123.1705 | 123.2346 | 61.8118 | -123.4131
418.0781 | 123.587 | -61.7615 | 61.5417 | -0.0085447 | 0.0089936 | 0.066603 | 0.0054667 | 0.063619 | -0.0015723 | -0.0031189 | 0.0067901 | -0.0032812 | 0.067704 | 0.07041 | -0.0030101 | -0.0056888 | 61.5463 | -61.6379 | -0.054932 | -61.8301 | 61.5509 | -61.8118 | -61.7294 | -62.1689 | -0.013733 | -62.0911 | 61.4731 | 61.5005 | -61.6837 | -61.8896 | -0.050354 | 0.032044 | 0.009155 | 0.1236 | -0.068664 | -0.10071 | 0.004578 | 0.07782 | -0.12817 | -0.068665 | -0.40741 | -0.32959 | -0.20142 | -0.041199 | 123.3124 | 123.3078 | 61.7065 | -123.2712 | 123.2346 | 123.262 | 61.7477 | -123.4314
419.8281 | 123.5779 | -61.7523 | 61.5326 | -0.00091566 | 0.010489 | 0.065322 | 0.0086709 | 0.065542 | 0.0020593 | -0.0022643 | -0.00083936 | 0.0001368 | 0.065567 | 0.07041 | -0.0030101 | -0.0073978 | 61.5967 | -61.5784 | 0.086975 | -61.7661 | 61.5692 | -61.8027 | -61.7294 | -62.146 | 0.086975 | -62.0453 | 61.4685 | 61.5417 | -61.6653 | -61.8713 | -0.050354 | 0.022888 | 0.036621 | 0.17395 | -0.013733 | -0.036621 | 0.064087 | 0.086975 | -0.11902 | -0.064087 | -0.39368 | -0.29297 | -0.17395 | 0.009155 | 123.3215 | 123.349 | 61.8393 | -123.262 | 123.2208 | 123.2941 | 61.8393 | -123.4039
421.5 | 123.5825 | -61.7523 | 61.5555 | -0.00091566 | 0.0077118 | 0.065535 | 0.0050393 | 0.068105 | 0.0018457 | -0.0016235 | -0.00083936 | -0.0032812 | 0.067276 | 0.070196 | -0.0036509 | -0.0056888 | 61.5372 | -61.647 | -0.050354 | -61.8256 | 61.5509 | -61.8164 | -61.7523 | -62.178 | -0.013733 | -62.1002 | 61.4868 | 61.5097 | -61.6974 | -61.8988 | -0.064087 | 0 | -0.004578 | 0.10529 | -0.073243 | -0.073243 | -0.018311 | 0.054931 | -0.14648 | -0.068665 | -0.42572 | -0.3479 | -0.20142 | -0.045776 | 123.3032 | 123.2895 | 61.702 | -123.3078 | 123.2391 | 123.262 | 61.7386 | -123.4543
423.25 | 123.4497 | -61.7477 | 61.6013 | -0.00091566 | 0.007071 | 0.067031 | 0.0058939 | 0.067464 | -0.0037085 | -0.0035461 | 0.01442 | -0.006272 | 0.064286 | 0.067206 | -0.0036509 | -0.0069706 | 61.6333 | -61.5051 | 0.045776 | -61.7386 | 61.5005 | -61.7523 | -61.6745 | -62.0911 | 0.082397 | -61.972 | 61.4502 | 61.4777 | -61.6241 | -61.853 | -0.004577 | 0.073242 | -0.10071 | 0.24262 | 0.009156 | -0.064086 | 0.032044 | 0.1236 | -0.10528 | -0.15106 | -0.34332 | -0.2243 | -0.11902 | -0.1236 | 123.2483 | 123.381 | 61.7935 | -123.2758 | 123.1979 | 123.2254 | 61.8301 | -123.4543
425.0156 | 123.436 | -61.734 | 61.6241 | 0.0067138 | 0.0085664 | 0.06938 | 0.0090983 | 0.066396 | -0.0045629 | -0.0046143 | -0.00083936 | -0.0058448 | 0.064072 | 0.070196 | -0.0045055 | -0.0093204 | 61.6196 | -61.5234 | 0.022888 | -61.7386 | 61.5417 | -61.7661 | -61.6562 | -62.114 | 0.032043 | -61.9812 | 61.4731 | 61.4868 | -61.6241 | -61.8256 | -0.032043 | 0.07782 | -0.082398 | 0.21057 | -0.004577 | -0.082397 | -0.004578 | 0.10986 | -0.091553 | -0.15106 | -0.37994 | -0.24719 | -0.15564 | -0.13733 | 123.2758 | 123.3536 | 61.7569 | -123.2803 | 123.2071 | 123.2208 | 61.7661 | -123.4497
426.7656 | 123.4497 | -61.7477 | 61.647 | -0.00091566 | 0.00878 | 0.068526 | 0.0071757 | 0.066823 | -0.0047765 | -0.0071777 | -0.00083936 | -0.0054174 | 0.064927 | 0.069556 | -0.0021557 | -0.0065432 | 61.6196 | -61.5097 | 0.036621 | -61.7386 | 61.528 | -61.734 | -61.647 | -62.1002 | 0.041199 | -61.9858 | 61.4822 | 61.496 | -61.6379 | -61.8301 | 0.013733 | 0.10071 | -0.11902 | 0.23804 | 0.009156 | -0.091552 | -0.027466 | 0.10986 | -0.082397 | -0.16479 | -0.35248 | -0.23804 | -0.15564 | -0.15106 | 123.2758 | 123.3673 | 61.7844 | -123.2941 | 123.23 | 123.2437 | 61.7889 | -123.4772
428.4531 | 123.4909 | -61.734 | 61.6241 | -0.00091566 | 0.00643 | 0.067458 | 0.0063211 | 0.06426 | -0.0032813 | -0.0058959 | -0.00083936 | -0.006272 | 0.064286 | 0.066565 | -0.0025829 | -0.007825 | 61.6241 | -61.4822 | 0.022888 | -61.7386 | 61.5555 | -61.7523 | -61.647 | -62.0728 | 0.050354 | -61.9537 | 61.4685 | 61.496 | -61.5967 | -61.8027 | -0.01831 | 0.086975 | -0.068665 | 0.25177 | -0.004577 | -0.091552 | 0 | 0.13733 | -0.068664 | -0.15564 | -0.33875 | -0.21973 | -0.15106 | -0.12817 | 123.2895 | 123.3582 | 61.7569 | -123.2712 | 123.2025 | 123.23 | 61.7844 | -123.4268
430.2188 | 123.4406 | -61.7752 | 61.6196 | -0.00091566 | 0.0062164 | 0.06938 | 0.0039713 | 0.067251 | 0.0018457 | -0.0029053 | -0.00083936 | -0.0034948 | 0.063645 | 0.068274 | -1.9327e-05 | -0.0086796 | 61.647 | -61.4731 | 0.045776 | -61.7386 | 61.5051 | -61.7615 | -61.6791 | -62.0636 | 0.073242 | -61.9583 | 61.4319 | 61.4502 | -61.6516 | -61.8439 | 0.013733 | 0.096131 | -0.11444 | 0.30212 | 0.036622 | -0.059509 | 0.027466 | 0.1236 | -0.068664 | -0.18768 | -0.28839 | -0.1831 | -0.11444 | -0.16937 | 123.2803 | 123.4222 | 61.821 | -123.2986 | 123.2071 | 123.2254 | 61.8484 | -123.4634
431.9531 | 123.5184 | -61.7661 | 61.5417 | 0.014343 | 0.011343 | 0.06404 | 0.0056803 | 0.065328 | 0.0073999 | -0.0029053 | -0.016098 | -0.0005042 | 0.064927 | 0.07041 | -0.0019419 | -0.0069706 | 61.5555 | -61.6562 | -0.013733 | -61.8118 | 61.5555 | -61.8118 | -61.7432 | -62.1872 | -0.036621 | -62.1323 | 61.4685 | 61.4685 | -61.6837 | -61.9034 | -0.045777 | 0.022888 | 0.013733 | 0.10986 | -0.045777 | -0.068665 | 0.013733 | 0.082397 | -0.13733 | -0.073242 | -0.42114 | -0.36621 | -0.22888 | -0.073242 | 123.3215 | 123.3215 | 61.7523 | -123.2849 | 123.2346 | 123.2346 | 61.7294 | -123.4451
433.625 | 123.436 | -61.734 | 61.6241 | 0.014343 | 0.0042938 | 0.068312 | 0.0052531 | 0.068746 | -0.0041357 | -0.0022643 | -0.016098 | -0.0064856 | 0.063645 | 0.069128 | -0.0021557 | -0.0071842 | 61.6241 | -61.5097 | 0.022888 | -61.734 | 61.5601 | -61.7661 | -61.647 | -62.1048 | 0.032043 | -61.9812 | 61.4548 | 61.528 | -61.5967 | -61.8301 | -0.032043 | 0.086975 | -0.064087 | 0.2243 | 0 | -0.086975 | 0 | 0.13733 | -0.09613 | -0.16937 | -0.37079 | -0.24719 | -0.15106 | -0.096131 | 123.2941 | 123.3582 | 61.7569 | -123.2712 | 123.1888 | 123.262 | 61.7661 | -123.4543
435.3594 | 123.468 | -61.7432 | 61.6379 | -0.00091566 | 0.00878 | 0.068099 | 0.0050393 | 0.06661 | -0.0032813 | -0.0031189 | 0.0067901 | -0.0052038 | 0.065354 | 0.069556 | -0.0025829 | -0.0080386 | 61.6287 | -61.4868 | 0.036621 | -61.7157 | 61.5463 | -61.7477 | -61.6699 | -62.0544 | 0.086975 | -61.9217 | 61.4822 | 61.4914 | -61.5921 | -61.7889 | -0.004578 | 0.073242 | -0.091552 | 0.25635 | 0.027466 | -0.045776 | -0.009155 | 0.15106 | -0.045776 | -0.15564 | -0.31128 | -0.17853 | -0.13275 | -0.14648 | 123.2895 | 123.3719 | 61.7798 | -123.3078 | 123.2254 | 123.2346 | 61.8301 | -123.4268
437.0938 | 123.4955 | -61.7157 | 61.6013 | -0.0085447 | 0.00643 | 0.065535 | 0.0052531 | 0.065328 | -0.0024267 | -0.0052551 | -0.00083936 | -0.0039222 | 0.064072 | 0.068915 | -0.0034373 | -0.0071842 | 61.7111 | -61.4227 | 0.11902 | -61.6791 | 61.5417 | -61.7203 | -61.6333 | -62.0316 | 0.11444 | -61.9034 | 61.4365 | 61.5005 | -61.5921 | -61.8027 | -0.004578 | 0.082397 | -0.059509 | 0.29297 | 0.036621 | -0.045776 | 0.10986 | 0.1236 | -0.086975 | -0.16479 | -0.31586 | -0.18768 | -0.10071 | -0.10071 | 123.2574 | 123.4268 | 61.8347 | -123.2346 | 123.1522 | 123.2162 | 61.8301 | -123.4039
438.8438 | 123.4085 | -61.734 | 61.6562 | -0.00091566 | 0.0085664 | 0.065749 | 0.0056803 | 0.068105 | -0.0011451 | -0.0022643 | -0.0084684 | -0.0049902 | 0.065354 | 0.069769 | -0.0032237 | -0.0080386 | 61.7065 | -61.4136 | 0.16022 | -61.6699 | 61.5372 | -61.7157 | -61.6241 | -62.0407 | 0.1236 | -61.9537 | 61.5005 | 61.5143 | -61.5967 | -61.8164 | 0.018311 | 0.10986 | -0.11902 | 0.32044 | 0.064087 | -0.045776 | 0.050354 | 0.13733 | -0.082397 | -0.15564 | -0.3067 | -0.21973 | -0.13733 | -0.14191 | 123.2712 | 123.4406 | 61.8942 | -123.2803 | 123.2346 | 123.2483 | 61.8576 | -123.4726
440.5312 | 123.4131 | -61.734 | 61.6241 | -0.00091566 | 0.011557 | 0.065962 | 0.0086709 | 0.067892 | 0.00056389 | -0.00098272 | 0.0067901 | -0.0013586 | 0.065354 | 0.069769 | -0.0030101 | -0.0076114 | 61.6425 | -61.4822 | 0.10529 | -61.7203 | 61.5601 | -61.7386 | -61.6562 | -62.1185 | 0.059509 | -62.0132 | 61.5189 | 61.528 | -61.6562 | -61.8118 | -0.004577 | 0.07782 | -0.064087 | 0.25177 | 0.013733 | -0.064087 | 0.01831 | 0.07782 | -0.07782 | -0.10529 | -0.38452 | -0.27924 | -0.20142 | -0.096131 | 123.2941 | 123.3765 | 61.8393 | -123.2803 | 123.2529 | 123.262 | 61.7935 | -123.436
442.2812 | 123.4131 | -61.702 | 61.6333 | -0.00091566 | 0.0092072 | 0.067244 | 0.0061075 | 0.068532 | 0.00077749 | -0.0033325 | -0.00083936 | -0.0041358 | 0.063858 | 0.06806 | -0.0023693 | -0.0084658 | 61.7111 | -61.377 | 0.16479 | -61.6562 | 61.5692 | -61.7203 | -61.615 | -62.0132 | 0.14191 | -61.908 | 61.4685 | 61.5326 | -61.5738 | -61.8027 | -0.018311 | 0.086975 | -0.064087 | 0.32501 | 0.045776 | -0.041199 | 0.07782 | 0.12817 | -0.10071 | -0.1648 | -0.31128 | -0.20599 | -0.10529 | -0.10071 | 123.2712 | 123.4131 | 61.8668 | -123.2483 | 123.1705 | 123.2346 | 61.8439 | -123.436
444.0312 | 123.4085 | -61.7157 | 61.6425 | -0.00091566 | 0.00878 | 0.067885 | 0.0061075 | 0.066823 | -0.0019995 | -0.0041869 | -0.0084684 | -0.0049902 | 0.064927 | 0.068915 | -0.0032237 | -0.0076114 | 61.6974 | -61.3632 | 0.16479 | -61.6562 | 61.5692 | -61.702 | -61.6196 | -62.0087 | 0.13275 | -61.9125 | 61.5005 | 61.5326 | -61.6287 | -61.8118 | 0.013733 | 0.09613 | -0.073242 | 0.35248 | 0.059509 | -0.036621 | 0.054932 | 0.086975 | -0.096131 | -0.14191 | -0.29297 | -0.19684 | -0.10071 | -0.10986 | 123.2849 | 123.4131 | 61.8805 | -123.262 | 123.2162 | 123.2483 | 61.8484 | -123.4543
445.7812 | 123.5504 | -61.6974 | 61.5784 | -0.00091566 | 0.0060028 | 0.064894 | 0.0014079 | 0.067037 | 0.0039819 | -0.00098272 | -0.00083936 | -0.0005042 | 0.061936 | 0.070837 | 0.0019033 | -0.0084658 | 61.6333 | -61.4868 | -0.013733 | -61.7294 | 61.5875 | -61.7294 | -61.6562 | -62.0407 | 0.059509 | -61.9675 | 61.4594 | 61.4822 | -61.6013 | -61.8118 | -0.032043 | 0.041199 | 0.009155 | 0.21057 | -0.032043 | -0.073242 | 0.054932 | 0.096131 | -0.11444 | -0.11902 | -0.34332 | -0.27008 | -0.15564 | -0.09613 | 123.2849 | 123.3307 | 61.6837 | -123.2346 | 123.1567 | 123.1796 | 61.7569 | -123.3902
447.4531 | 123.4406 | -61.6745 | 61.6653 | 0.0067138 | 0.005362 | 0.067244 | 0.0052531 | 0.067678 | -0.0034949 | -0.0037597 | -0.00083936 | -0.0052038 | 0.067276 | 0.068487 | -0.0047191 | -0.0065432 | 61.6333 | -61.4273 | 0.027466 | -61.6745 | 61.5829 | -61.6791 | -61.6058 | -62.0316 | 0.050354 | -61.908 | 61.4731 | 61.5463 | -61.5692 | -61.7706 | -0.004577 | 0.068665 | -0.082397 | 0.24719 | 0 | -0.068665 | -0.032043 | 0.10529 | -0.09613 | -0.19226 | -0.35705 | -0.23346 | -0.13733 | -0.11902 | 123.2574 | 123.3078 | 61.702 | -123.2712 | 123.1476 | 123.2208 | 61.7249 | -123.436
449.125 | 123.4863 | -61.702 | 61.5784 | -0.00091566 | 0.011771 | 0.064894 | 0.0054667 | 0.06896 | 0.0044091 | -0.0011963 | 0.0067901 | -7.6996e-05 | 0.066849 | 0.072119 | -0.0013011 | -0.01167 | 61.6699 | -61.4548 | 0.086975 | -61.7294 | 61.5829 | -61.7432 | -61.6699 | -62.0773 | 0.064087 | -62.0178 | 61.4731 | 61.496 | -61.6287 | -61.8347 | -0.041199 | 0.032043 | 0.004578 | 0.24719 | -0.027466 | -0.059509 | 0.091553 | 0.073242 | -0.13275 | -0.10529 | -0.37537 | -0.31586 | -0.18311 | -0.082397 | 123.2849 | 123.3719 | 61.7889 | -123.2483 | 123.175 | 123.1979 | 61.7661 | -123.4131
450.875 | 123.4222 | -61.7203 | 61.6104 | -0.00091566 | 0.0089936 | 0.069808 | 0.0046121 | 0.070028 | -0.0028539 | -0.0033325 | -0.00083936 | -0.0060584 | 0.066636 | 0.071051 | -0.0047191 | -0.0073978 | 61.6653 | -61.4273 | 0.13733 | -61.6791 | 61.5326 | -61.7065 | -61.6425 | -62.0728 | 0.086975 | -61.9629 | 61.4822 | 61.5372 | -61.5875 | -61.8027 | 0.013733 | 0.07782 | -0.07782 | 0.29297 | 0.041199 | -0.036621 | 0.054931 | 0.13275 | -0.082397 | -0.12817 | -0.35248 | -0.24262 | -0.16022 | -0.073243 | 123.2529 | 123.3856 | 61.8576 | -123.2529 | 123.2025 | 123.2574 | 61.8073 | -123.4131
452.6094 | 123.5138 | -61.7065 | 61.5601 | -0.00091566 | 0.014334 | 0.064894 | 0.0090983 | 0.065328 | 0.0033411 | -0.0031189 | 0.01442 | 0.0012048 | 0.067704 | 0.072333 | -0.0017283 | -0.010816 | 61.6333 | -61.496 | 0.10986 | -61.7249 | 61.5555 | -61.7432 | -61.6837 | -62.0544 | 0.09613 | -61.9995 | 61.496 | 61.496 | -61.6379 | -61.8393 | -0.036621 | 0.022888 | -0.004578 | 0.21057 | -0.018311 | -0.041199 | 0.073242 | 0.068665 | -0.13275 | -0.064087 | -0.3479 | -0.29297 | -0.16022 | -0.064087 | 123.262 | 123.3398 | 61.8164 | -123.2437 | 123.2025 | 123.2025 | 61.8027 | -123.3994
454.3438 | 123.4772 | -61.734 | 61.5738 | 0.014343 | 0.009848 | 0.067244 | 0.0056803 | 0.066183 | 0.0016321 | -0.0022643 | -0.0084684 | -0.0002906 | 0.06514 | 0.071692 | -0.0027965 | -0.0069706 | 61.5417 | -61.5463 | 0.009155 | -61.7706 | 61.5509 | -61.7752 | -61.7065 | -62.1414 | 0.009155 | -62.0956 | 61.4639 | 61.4868 | -61.6699 | -61.8668 | -0.041199 | 0.027466 | -0.022889 | 0.18768 | -0.036621 | -0.064087 | -0.032044 | 0.064087 | -0.13275 | -0.10986 | -0.40741 | -0.36163 | -0.22888 | -0.086976 | 123.2849 | 123.2758 | 61.7432 | -123.2803 | 123.1979 | 123.2208 | 61.7432 | -123.4406
456.0938 | 123.5458 | -61.7065 | 61.5646 | -0.00091566 | 0.0079254 | 0.06639 | 0.0039713 | 0.066183 | 0.00013669 | -0.00012812 | 0.0067901 | -0.001145 | 0.066422 | 0.071265 | -0.00023313 | -0.005048 | 61.5326 | -61.5555 | -0.054932 | -61.7706 | 61.5738 | -61.7661 | -61.6882 | -62.1368 | -0.032043 | -62.059 | 61.4822 | 61.5463 | -61.6608 | -61.8668 | -0.059509 | 0.018311 | 0.009156 | 0.15106 | -0.064087 | -0.082398 | -0.032043 | 0.045776 | -0.16022 | -0.082397 | -0.4303 | -0.35248 | -0.19226 | -0.01831 | 123.2803 | 123.2391 | 61.6516 | -123.2529 | 123.1888 | 123.2529 | 61.6745 | -123.4314
457.8438 | 123.5229 | -61.6974 | 61.5967 | -0.0085447 | 0.0079254 | 0.067244 | 0.0063211 | 0.065755 | -0.0028539 | -0.0029053 | -0.00083936 | -0.0049902 | 0.065354 | 0.069556 | 0.00019427 | -0.0065432 | 61.6562 | -61.409 | 0.027466 | -61.6699 | 61.4914 | -61.734 | -61.6379 | -62.027 | 0.091553 | -61.908 | 61.4365 | 61.4822 | -61.6196 | -61.7935 | -0.036621 | 0.05951 | -0.10529 | 0.28839 | 0.027466 | -0.032044 | 0.059509 | 0.07782 | -0.09613 | -0.16022 | -0.32959 | -0.21057 | -0.11444 | -0.11444 | 123.1888 | 123.3536 | 61.7249 | -123.2346 | 123.1338 | 123.1796 | 61.7889 | -123.3902
459.5312 | 123.4451 | -61.6379 | 61.6425 | -0.00091566 | 0.0074982 | 0.068312 | 0.0084573 | 0.067678 | -0.0069129 | -0.0033325 | -0.016098 | -0.006272 | 0.066422 | 0.068274 | -0.0083507 | -0.0071842 | 61.7111 | -61.3083 | 0.11444 | -61.6104 | 61.5921 | -61.6608 | -61.5875 | -61.9949 | 0.14191 | -61.8164 | 61.4822 | 61.528 | -61.528 | -61.7477 | -0.022889 | 0.050354 | -0.050354 | 0.32959 | 0.027465 | -0.022889 | 0.068665 | 0.10986 | -0.10986 | -0.16022 | -0.35706 | -0.17853 | -0.068664 | -0.11444 | 123.23 | 123.349 | 61.7523 | -123.23 | 123.1201 | 123.1659 | 61.7798 | -123.3902
461.2812 | 123.4177 | -61.6379 | 61.6333 | -0.0085447 | 0.0068574 | 0.067031 | 0.0022623 | 0.069814 | -0.0019995 | -0.0024779 | -0.016098 | -0.0047766 | 0.064286 | 0.069983 | -0.0019419 | -0.0093204 | 61.7111 | -61.3174 | 0.045776 | -61.6287 | 61.5555 | -61.6837 | -61.5921 | -61.972 | 0.073242 | -61.8851 | 61.4822 | 61.5234 | -61.5509 | -61.7615 | -0.045777 | 0.045776 | -0.07782 | 0.32043 | 0.009155 | -0.036621 | 0.07782 | 0.086975 | -0.1236 | -0.15106 | -0.33417 | -0.24719 | -0.1236 | -0.10986 | 123.1934 | 123.349 | 61.6837 | -123.2254 | 123.1201 | 123.1613 | 61.7111 | -123.3948
463.0312 | 123.5184 | -61.6974 | 61.5601 | -0.00091566 | 0.0096344 | 0.066176 | 0.0037577 | 0.066396 | 0.0016321 | -0.0033325 | -0.0084684 | -0.0005042 | 0.064499 | 0.070624 | -0.00044673 | -0.0088932 | 61.6287 | -61.4822 | 0.091553 | -61.7203 | 61.5601 | -61.7477 | -61.6837 | -62.0499 | 0.091553 | -61.9949 | 61.4456 | 61.5097 | -61.6196 | -61.8484 | -0.050354 | 0.013733 | 0 | 0.21515 | -0.022888 | -0.036621 | 0.068664 | 0.07782 | -0.15106 | -0.11444 | -0.35248 | -0.29755 | -0.14648 | -0.050354 | 123.2574 | 123.3261 | 61.7889 | -123.2437 | 123.143 | 123.2071 | 61.7889 | -123.4085
464.7812 | 123.4863 | -61.702 | 61.5784 | -0.0085447 | 0.007071 | 0.066603 | 0.0052531 | 0.067251 | -7.6908e-05 | -0.0024779 | 0.01442 | -0.0041358 | 0.063218 | 0.069983 | -0.0027965 | -0.0086796 | 61.6516 | -61.4365 | 0.050354 | -61.6745 | 61.4914 | -61.7157 | -61.6516 | -61.9949 | 0.091553 | -61.908 | 61.4227 | 61.4822 | -61.6058 | -61.7752 | -0.013733 | 0.050354 | -0.086975 | 0.2655 | 0.027465 | -0.022889 | 0.073242 | 0.09613 | -0.073243 | -0.15564 | -0.29297 | -0.20599 | -0.13275 | -0.09613 | 123.1934 | 123.3536 | 61.7523 | -123.23 | 123.1247 | 123.1842 | 61.7935 | -123.3536
466.4531 | 123.5504 | -61.6516 | 61.5692 | 0.0067138 | 0.0060028 | 0.067671 | 0.0071757 | 0.065542 | 0.00077749 | -0.00076912 | -0.00083936 | -0.0024268 | 0.06514 | 0.069983 | -0.0021557 | -0.0067568 | 61.6104 | -61.4868 | -0.032043 | -61.7203 | 61.5601 | -61.7157 | -61.6241 | -62.0544 | 0.041199 | -61.972 | 61.4868 | 61.5417 | -61.5784 | -61.8073 | -0.064087 | 0.027465 | -0.009155 | 0.1648 | -0.068665 | -0.09613 | 0.041199 | 0.073242 | -0.15564 | -0.082398 | -0.40283 | -0.32043 | -0.16479 | -0.027466 | 123.2117 | 123.262 | 61.6196 | -123.1934 | 123.1384 | 123.1934 | 61.6928 | -123.3765
468.1875 | 123.3856 | -61.6928 | 61.6287 | -0.0085447 | 0.0057892 | 0.067031 | 0.0082437 | 0.06426 | -0.0037085 | -0.0054687 | -0.00083936 | -0.004563 | 0.064072 | 0.069769 | -0.0030101 | -0.0080386 | 61.647 | -61.3998 | 0.032043 | -61.6791 | 61.5326 | -61.6928 | -61.6104 | -62.0453 | 0.045776 | -61.9171 | 61.4548 | 61.5234 | -61.5875 | -61.7615 | 0 | 0.082397 | -0.09613 | 0.29297 | 0.013733 | -0.068664 | 0.018311 | 0.10529 | -0.068665 | -0.17395 | -0.35248 | -0.2243 | -0.15564 | -0.10529 | 123.2254 | 123.3398 | 61.7249 | -123.2391 | 123.1476 | 123.2162 | 61.7386 | -123.3902
469.9375 | 123.3994 | -61.6882 | 61.6379 | -0.0085447 | 0.0045074 | 0.067244 | 0.0048257 | 0.065114 | -0.00050411 | -0.0039733 | -0.00083936 | -0.0041358 | 0.063858 | 0.069128 | -0.0034373 | -0.0073978 | 61.6882 | -61.3541 | 0.041199 | -61.6699 | 61.5234 | -61.6837 | -61.6196 | -61.9949 | 0.068665 | -61.8759 | 61.4548 | 61.5005 | -61.5829 | -61.7569 | 0.004577 | 0.068664 | -0.11444 | 0.33417 | 0.01831 | -0.050354 | 0.050354 | 0.10529 | -0.068665 | -0.1831 | -0.3067 | -0.18768 | -0.11902 | -0.13733 | 123.2117 | 123.3765 | 61.7294 | -123.2574 | 123.143 | 123.1888 | 61.7569 | -123.3948
471.6094 | 123.5184 | -61.6653 | 61.5738 | -0.00091566 | 0.0060028 | 0.063826 | 0.0026895 | 0.066396 | 0.0016321 | -0.0033325 | -0.0084684 | -0.0017858 | 0.06514 | 0.068915 | 0.00019427 | -0.0080386 | 61.5967 | -61.5189 | -0.07782 | -61.7294 | 61.5875 | -61.7203 | -61.6653 | -62.1002 | -0.041199 | -62.0178 | 61.5326 | 61.5372 | -61.6058 | -61.7981 | -0.054932 | 0 | 0.013732 | 0.14648 | -0.064087 | -0.064087 | 0.022888 | 0.059509 | -0.13275 | -0.041199 | -0.43488 | -0.35248 | -0.21973 | -0.036622 | 123.2529 | 123.262 | 61.5875 | -123.2391 | 123.1979 | 123.2025 | 61.6241 | -123.3719
473.375 | 123.3948 | -61.6425 | 61.6699 | 0.014343 | 0.0034394 | 0.067244 | 0.0048257 | 0.066183 | -0.0026403 | -0.0026917 | -0.0084684 | -0.0037086 | 0.064286 | 0.069769 | -0.0038647 | -0.0067568 | 61.7111 | -61.2991 | 0.045776 | -61.6196 | 61.5555 | -61.6425 | -61.5601 | -61.9537 | 0.07782 | -61.853 | 61.496 | 61.5738 | -61.5143 | -61.7203 | 0 | 0.082397 | -0.11444 | 0.34332 | 0.022888 | -0.059509 | 0.041199 | 0.12817 | -0.07782 | -0.17395 | -0.31128 | -0.21057 | -0.13275 | -0.09613 | 123.1979 | 123.3536 | 61.6882 | -123.23 | 123.1384 | 123.2162 | 61.7203 | -123.3902
475.0625 | 123.5001 | -61.6013 | 61.6104 | -0.016174 | 0.011984 | 0.065535 | 0.0056803 | 0.066396 | 0.0029139 | -0.00055532 | -0.00083936 | -0.0007178 | 0.06749 | 0.073401 | -0.0010875 | -0.009534 | 61.6974 | -61.3312 | 0.10071 | -61.6333 | 61.6196 | -61.6745 | -61.5875 | -61.9812 | 0.09613 | -61.9171 | 61.5189 | 61.5555 | -61.5509 | -61.7569 | -0.073243 | 0.013733 | 0.009155 | 0.27008 | -0.032044 | -0.045777 | 0.086975 | 0.050354 | -0.15564 | -0.091553 | -0.37994 | -0.31586 | -0.16022 | -0.054932 | 123.2208 | 123.2986 | 61.702 | -123.1979 | 123.1201 | 123.1567 | 61.6974 | -123.3673
476.8125 | 123.4497 | -61.5921 | 61.7065 | 0.0067138 | 0.005362 | 0.06639 | 0.0037577 | 0.068319 | -0.0011451 | -0.0041869 | -0.00083936 | -0.0049902 | 0.065995 | 0.070196 | -0.0023693 | -0.0071842 | 61.7432 | -61.235 | 0.054932 | -61.5829 | 61.5829 | -61.615 | -61.528 | -61.9171 | 0.073242 | -61.8118 | 61.5005 | 61.5555 | -61.5051 | -61.6837 | -0.022888 | 0.064087 | -0.1236 | 0.35706 | 0.009155 | -0.054932 | 0.036621 | 0.086975 | -0.091553 | -0.20599 | -0.32501 | -0.21973 | -0.12817 | -0.15106 | 123.175 | 123.3353 | 61.647 | -123.2346 | 123.0927 | 123.1476 | 61.6653 | -123.3902
478.5625 | 123.436 | -61.647 | 61.6562 | -0.00091566 | 0.0068574 | 0.069167 | 0.0050393 | 0.067464 | -0.0052039 | -0.0022643 | 0.0067901 | -0.0041358 | 0.063858 | 0.071051 | -0.0025829 | -0.0069706 | 61.7203 | -61.2991 | 0.11444 | -61.5967 | 61.6013 | -61.6104 | -61.5601 | -61.9675 | 0.11444 | -61.821 | 61.4868 | 61.5234 | -61.5097 | -61.7249 | 0.036621 | 0.086975 | -0.054932 | 0.3479 | 0.050354 | -0.036621 | 0.064087 | 0.13733 | -0.07782 | -0.16937 | -0.32043 | -0.17395 | -0.09613 | -0.13275 | 123.2483 | 123.3673 | 61.7615 | -123.2162 | 123.1338 | 123.1705 | 61.7615 | -123.381
480.2656 | 123.3765 | -61.5921 | 61.7249 | 0.0067138 | 0.0074982 | 0.067031 | 0.0069621 | 0.06661 | -0.0030677 | -0.0056823 | -0.0084684 | -0.0032812 | 0.063858 | 0.069128 | -0.0030101 | -0.0088932 | 61.7661 | -61.203 | 0.059509 | -61.5829 | 61.6013 | -61.6013 | -61.5189 | -61.908 | 0.068665 | -61.8118 | 61.5372 | 61.5692 | -61.4868 | -61.6699 | -0.009155 | 0.073242 | -0.1236 | 0.3891 | 0.009155 | -0.064087 | 0.041198 | 0.10529 | -0.07782 | -0.18768 | -0.31586 | -0.21973 | -0.14191 | -0.15564 | 123.1934 | 123.3582 | 61.6516 | -123.2437 | 123.1293 | 123.1613 | 61.6608 | -123.3948
482.0312 | 123.381 | -61.5738 | 61.7203 | -0.016174 | 0.011771 | 0.067244 | 0.0069621 | 0.066396 | 0.00056389 | -0.0031189 | 0.0067901 | -0.0039222 | 0.067704 | 0.072546 | -0.0040783 | -0.010602 | 61.7477 | -61.1984 | 0.11902 | -61.5509 | 61.6791 | -61.5967 | -61.5189 | -61.9537 | 0.054932 | -61.8576 | 61.6104 | 61.6379 | -61.496 | -61.6791 | -0.022888 | 0.054932 | -0.041199 | 0.37537 | 0.022889 | -0.032043 | 0.027466 | 0.07782 | -0.10529 | -0.10986 | -0.37994 | -0.28381 | -0.17853 | -0.082398 | 123.2529 | 123.3215 | 61.6928 | -123.2391 | 123.1842 | 123.2117 | 61.6287 | -123.3994
483.7812 | 123.4451 | -61.615 | 61.6104 | -0.00091566 | 0.0083526 | 0.065749 | 0.0031167 | 0.066823 | 0.0041955 | -0.0026917 | 0.01442 | -0.001145 | 0.063004 | 0.069556 | 0.0016895 | -0.0097476 | 61.647 | -61.3815 | -0.013733 | -61.6791 | 61.6333 | -61.6928 | -61.5875 | -62.0224 | -0.013733 | -62.0041 | 61.5463 | 61.5967 | -61.5555 | -61.7432 | -0.07782 | 0.027466 | 0.022888 | 0.23346 | -0.064087 | -0.091553 | 0.036621 | 0.059509 | -0.12817 | -0.064087 | -0.40741 | -0.3891 | -0.26093 | -0.013733 | 123.2483 | 123.262 | 61.6013 | -123.1979 | 123.1613 | 123.2117 | 61.6013 | -123.3536
485.4688 | 123.4222 | -61.5784 | 61.6928 | -0.016174 | 0.0062164 | 0.067244 | 0.0050393 | 0.067892 | -0.0024267 | -0.0035461 | -0.0084684 | -0.0041358 | 0.064499 | 0.069556 | -0.0049327 | -0.0063296 | 61.7615 | -61.2122 | 0.11444 | -61.5372 | 61.6241 | -61.6013 | -61.5051 | -61.908 | 0.13275 | -61.7798 | 61.5189 | 61.5921 | -61.4822 | -61.6745 | -0.022888 | 0.073242 | -0.068664 | 0.36621 | 0.041199 | -0.032043 | 0.068665 | 0.09613 | -0.096131 | -0.17395 | -0.32959 | -0.20142 | -0.10528 | -0.10071 | 123.2025 | 123.3398 | 61.6928 | -123.1979 | 123.0972 | 123.1705 | 61.7111 | -123.3673
487.2344 | 123.4222 | -61.6379 | 61.6287 | -0.016174 | 0.011557 | 0.067671 | 0.0046121 | 0.06896 | 0.0027003 | -0.0031189 | -0.00083936 | 0.0007776 | 0.064713 | 0.069983 | 0.00019427 | -0.010175 | 61.6379 | -61.3907 | 0.009155 | -61.6791 | 61.6013 | -61.6699 | -61.6196 | -62.027 | 0.004578 | -61.9949 | 61.5646 | 61.6013 | -61.5509 | -61.7477 | -0.032044 | 0.01831 | -0.027466 | 0.24719 | -0.041199 | -0.059509 | 0.009155 | 0.086975 | -0.10986 | -0.064087 | -0.3891 | -0.35706 | -0.24719 | -0.027466 | 123.2391 | 123.2758 | 61.647 | -123.2483 | 123.2025 | 123.2391 | 61.6425 | -123.3765
488.9219 | 123.349 | -61.6379 | 61.6333 | -0.0085447 | 0.0072846 | 0.067031 | 0.0065347 | 0.063833 | -0.0015723 | -0.0033325 | -0.00083936 | -0.0032812 | 0.062577 | 0.069769 | -0.0032237 | -0.006116 | 61.6516 | -61.3403 | 0.10071 | -61.6287 | 61.6013 | -61.6425 | -61.5555 | -62.0407 | 0.050354 | -61.9354 | 61.5189 | 61.5829 | -61.5509 | -61.7432 | -0.004578 | 0.082397 | -0.032044 | 0.29755 | 0.009155 | -0.073242 | 0.01831 | 0.086975 | -0.10529 | -0.11444 | -0.40283 | -0.29755 | -0.19226 | -0.050354 | 123.2391 | 123.2895 | 61.7386 | -123.1888 | 123.1567 | 123.2208 | 61.6882 | -123.3765
490.6094 | 123.4222 | -61.6013 | 61.6837 | -0.00091566 | 0.005362 | 0.067671 | 0.0071757 | 0.066396 | -0.0047765 | -0.0058959 | -0.00083936 | -0.0054174 | 0.064286 | 0.070196 | -0.0057873 | -0.0080386 | 61.6928 | -61.2442 | 0.036621 | -61.5646 | 61.647 | -61.5829 | -61.5097 | -61.9308 | 0.082397 | -61.7844 | 61.5509 | 61.5967 | -61.4456 | -61.6699 | 0.01831 | 0.091552 | -0.036621 | 0.35705 | 0.036621 | -0.054931 | 0.009155 | 0.15564 | -0.068665 | -0.13275 | -0.32959 | -0.18311 | -0.11444 | -0.086975 | 123.2483 | 123.2941 | 61.6379 | -123.1934 | 123.1522 | 123.1979 | 61.6837 | -123.3536
492.3594 | 123.4451 | -61.5875 | 61.6379 | -0.016174 | 0.010275 | 0.067885 | 0.0037577 | 0.068532 | 0.0039819 | -0.0020507 | -0.00083936 | -0.0007178 | 0.064072 | 0.071692 | 0.0014759 | -0.007825 | 61.6379 | -61.3998 | -0.036621 | -61.6882 | 61.6287 | -61.6699 | -61.5967 | -62.027 | -0.036621 | -61.9446 | 61.5555 | 61.5692 | -61.5417 | -61.7569 | -0.082398 | -0.009156 | -0.009155 | 0.18768 | -0.10071 | -0.091552 | 0 | 0.045776 | -0.16937 | -0.082397 | -0.43945 | -0.35706 | -0.18768 | -0.068664 | 123.2162 | 123.2254 | 61.5509 | -123.2346 | 123.143 | 123.1567 | 61.5509 | -123.3948
494.0938 | 123.3902 | -61.5509 | 61.7661 | 0.0067138 | 0.00643 | 0.067885 | 0.0069621 | 0.067037 | -0.0043493 | -0.0037597 | -0.00083936 | -0.0047766 | 0.066422 | 0.069556 | -0.0068553 | -0.007825 | 61.7249 | -61.1847 | 0.027466 | -61.5509 | 61.6791 | -61.528 | -61.4548 | -61.9125 | 0.027466 | -61.7752 | 61.5875 | 61.6196 | -61.4502 | -61.6562 | 0.022888 | 0.09613 | -0.086975 | 0.36621 | 0 | -0.09613 | -0.041198 | 0.10071 | -0.10529 | -0.17853 | -0.36163 | -0.22431 | -0.11902 | -0.14648 | 123.23 | 123.2758 | 61.5784 | -123.2208 | 123.1384 | 123.1705 | 61.5784 | -123.4222
495.8438 | 123.4589 | -61.441 | 61.8027 | -0.00091566 | 0.0066438 | 0.065535 | 0.0046121 | 0.068319 | 0.0018457 | -0.0041869 | -0.0084684 | -0.0049902 | 0.066208 | 0.069983 | -0.00023313 | -0.0093204 | 61.8668 | -60.997 | 0.032043 | -61.4502 | 61.7111 | -61.4914 | -61.4136 | -61.7752 | 0.091553 | -61.6653 | 61.6241 | 61.6608 | -61.3632 | -61.5921 | -0.050354 | 0.027466 | -0.091552 | 0.44403 | -0.009155 | -0.036621 | 0.064087 | 0.07782 | -0.15106 | -0.17853 | -0.33417 | -0.2243 | -0.073242 | -0.14191 | 123.1522 | 123.3078 | 61.4731 | -123.2162 | 123.0652 | 123.1018 | 61.5326 | -123.3948
497.5312 | 123.4085 | -61.4639 | 61.8118 | -0.0085447 | 0.0079254 | 0.067031 | 0.0048257 | 0.066396 | -0.0026403 | -0.0037597 | -0.0084684 | -0.0043494 | 0.065354 | 0.069128 | -0.0049327 | -0.0063296 | 61.821 | -60.9879 | 0.082397 | -61.4227 | 61.7569 | -61.4685 | -61.3724 | -61.7844 | 0.12817 | -61.6333 | 61.6791 | 61.6928 | -61.3312 | -61.5326 | -0.004578 | 0.091553 | -0.054932 | 0.47607 | 0.041199 | -0.050354 | 0.009155 | 0.13275 | -0.068665 | -0.13275 | -0.32043 | -0.16937 | -0.10071 | -0.11902 | 123.2208 | 123.2849 | 61.5463 | -123.1842 | 123.143 | 123.1567 | 61.5921 | -123.3444
499.2188 | 123.4543 | -61.4914 | 61.7157 | -0.016174 | 0.0094208 | 0.063399 | 0.0029031 | 0.064474 | 0.0039819 | -0.00098272 | -0.00083936 | -0.0007178 | 0.068558 | 0.071905 | -0.00044673 | -0.010816 | 61.8073 | -61.0794 | 0.10071 | -61.5051 | 61.7111 | -61.5326 | -61.4594 | -61.8576 | 0.07782 | -61.8027 | 61.6333 | 61.6379 | -61.4273 | -61.6287 | -0.041199 | 0.032043 | -0.004577 | 0.41199 | -0.013733 | -0.045776 | 0.091553 | 0.064087 | -0.13733 | -0.082397 | -0.36621 | -0.31128 | -0.17395 | -0.07782 | 123.2025 | 123.2986 | 61.5921 | -123.175 | 123.1247 | 123.1293 | 61.5692 | -123.3444
500.9844 | 123.4634 | -61.5555 | 61.6333 | -0.00091566 | 0.0083526 | 0.065322 | 0.0043985 | 0.065542 | 0.0020593 | -0.0024779 | -0.00083936 | -0.0019996 | 0.064499 | 0.07276 | 0.00040787 | -0.009534 | 61.6699 | -61.2717 | 0.086975 | -61.6013 | 61.6516 | -61.6379 | -61.5463 | -61.94 | 0.091553 | -61.8759 | 61.5784 | 61.5646 | -61.5189 | -61.7111 | -0.082397 | 0.009155 | 0.01831 | 0.28381 | -0.045776 | -0.054931 | 0.036621 | 0.036621 | -0.15564 | -0.054932 | -0.38452 | -0.32043 | -0.16479 | -0.068665 | 123.2071 | 123.2254 | 61.6425 | -123.1796 | 123.1338 | 123.1201 | 61.647 | -123.3444
502.6562 | 123.4543 | -61.5921 | 61.6333 | 0.0067138 | 0.00643 | 0.066603 | 0.0018351 | 0.067892 | -0.00029051 | -0.0014099 | -0.0084684 | -0.004563 | 0.063218 | 0.070837 | -0.00066033 | -0.0082522 | 61.7203 | -61.2167 | 0.050354 | -61.5646 | 61.5692 | -61.6333 | -61.528 | -61.8988 | 0.082397 | -61.8164 | 61.4914 | 61.5372 | -61.5234 | -61.6882 | -0.041199 | 0.064087 | -0.064087 | 0.37537 | 0.027466 | -0.036621 | 0.086975 | 0.068665 | -0.09613 | -0.14191 | -0.3067 | -0.2243 | -0.12817 | -0.096131 | 123.1613 | 123.3124 | 61.6425 | -123.1613 | 123.0835 | 123.1293 | 61.6745 | -123.3215
504.4062 | 123.4268 | -61.6013 | 61.615 | -0.0085447 | 0.010489 | 0.067244 | 0.0041849 | 0.06426 | 0.0014185 | -0.0016235 | -0.00083936 | -0.0022132 | 0.063004 | 0.071051 | -0.0010875 | -0.0067568 | 61.6013 | -61.3907 | -0.032043 | -61.6608 | 61.6241 | -61.6791 | -61.5784 | -62.0407 | -0.009155 | -61.9675 | 61.5097 | 61.6058 | -61.5509 | -61.7249 | -0.07782 | 0.022888 | 0.009156 | 0.21057 | -0.05951 | -0.082398 | -0.013733 | 0.050354 | -0.1236 | -0.10529 | -0.43945 | -0.36621 | -0.24261 | -0.009155 | 123.2254 | 123.2025 | 61.5692 | -123.1934 | 123.111 | 123.2071 | 61.5921 | -123.3398
506.0938 | 123.4634 | -61.5097 | 61.6974 | -0.0085447 | 0.005362 | 0.067885 | 0.0024759 | 0.065114 | -0.00050411 | -0.0033325 | -0.00083936 | -0.0019996 | 0.06514 | 0.070196 | -0.0013011 | -0.0069706 | 61.7661 | -61.1343 | 0.050354 | -61.5051 | 61.6241 | -61.5417 | -61.4777 | -61.8439 | 0.09613 | -61.7477 | 61.5829 | 61.5784 | -61.4456 | -61.6241 | -0.032043 | 0.032044 | -0.073242 | 0.37537 | 0.004578 | -0.027466 | 0.068664 | 0.064087 | -0.11444 | -0.11444 | -0.33417 | -0.23804 | -0.1236 | -0.11902 | 123.1339 | 123.2758 | 61.5601 | -123.175 | 123.0927 | 123.0881 | 61.6058 | -123.3215
507.8281 | 123.4589 | -61.5005 | 61.6791 | -0.00091566 | 0.007071 | 0.067244 | 0.0026895 | 0.065755 | 0.00077749 | -0.00098272 | -0.0084684 | -0.0032812 | 0.064927 | 0.071692 | -0.0030101 | -0.0093204 | 61.7661 | -61.116 | 0.013733 | -61.5051 | 61.6699 | -61.528 | -61.4685 | -61.8347 | 0.086975 | -61.7569 | 61.5646 | 61.615 | -61.4182 | -61.6058 | -0.027466 | 0.032043 | -0.009155 | 0.38452 | -0.004578 | -0.036621 | 0.086975 | 0.082397 | -0.10529 | -0.11444 | -0.33417 | -0.25635 | -0.15106 | -0.064087 | 123.1705 | 123.2666 | 61.5143 | -123.1476 | 123.0652 | 123.1155 | 61.5875 | -123.2849
509.5625 | 123.3398 | -61.4502 | 61.8164 | -0.0085447 | 0.0068574 | 0.069594 | 0.0033305 | 0.067037 | -0.0041357 | -0.0022643 | -0.00083936 | -0.004563 | 0.063004 | 0.069769 | -0.0030101 | -0.0069706 | 61.8668 | -60.9329 | 0.036621 | -61.4182 | 61.734 | -61.4365 | -61.3861 | -61.7523 | 0.059509 | -61.647 | 61.6241 | 61.7157 | -61.3449 | -61.528 | 0.013733 | 0.064087 | -0.082397 | 0.51727 | 0.032043 | -0.032044 | 0.050354 | 0.10529 | -0.07782 | -0.19226 | -0.30212 | -0.19684 | -0.11902 | -0.10071 | 123.1842 | 123.317 | 61.4868 | -123.2025 | 123.0743 | 123.1659 | 61.5097 | -123.3444
511.3281 | 123.4131 | -61.3449 | 61.8851 | -0.00091566 | 0.0085664 | 0.06874 | 0.0048257 | 0.067892 | -0.00071771 | -0.00076912 | -0.0084684 | -0.0049902 | 0.064713 | 0.07041 | -0.0027965 | -0.0073978 | 61.94 | -60.8002 | 0.059509 | -61.3358 | 61.8073 | -61.3815 | -61.3083 | -61.6562 | 0.091553 | -61.5509 | 61.7111 | 61.7386 | -61.2991 | -61.4639 | -0.036621 | 0.036621 | -0.07782 | 0.54474 | 0.009156 | -0.027465 | 0.054931 | 0.045777 | -0.11902 | -0.17395 | -0.31128 | -0.20599 | -0.086975 | -0.14649 | 123.1522 | 123.2849 | 61.4044 | -123.1934 | 123.056 | 123.0835 | 61.4365 | -123.349
513.0781 | 123.4909 | -61.2671 | 61.9171 | -0.0085447 | 0.0068574 | 0.067671 | 0.0031167 | 0.064687 | 0.0024865 | -0.0031189 | -0.0084684 | -0.0002906 | 0.06279 | 0.070837 | -0.0023693 | -0.0071842 | 61.9537 | -60.7544 | -0.036621 | -61.3403 | 61.9125 | -61.3266 | -61.2579 | -61.6562 | 0.032043 | -61.5738 | 61.8073 | 61.8805 | -61.2167 | -61.3998 | -0.059509 | 0.009155 | -0.004577 | 0.5127 | -0.073242 | -0.082397 | 0.036621 | 0.050354 | -0.13275 | -0.10986 | -0.3891 | -0.3067 | -0.17395 | -0.036621 | 123.1796 | 123.2208 | 61.2305 | -123.175 | 123.0743 | 123.1476 | 61.2991 | -123.317
514.8281 | 123.3856 | -61.2671 | 61.972 | -0.0085447 | 0.007071 | 0.067885 | 0.0063211 | 0.066396 | -0.0032813 | -0.0046143 | -0.0084684 | -0.0052038 | 0.065354 | 0.068487 | -0.0062145 | -0.0080386 | 62.0453 | -60.5988 | 0.13275 | -61.2167 | 61.9034 | -61.2854 | -61.1847 | -61.5875 | 0.14648 | -61.441 | 61.8073 | 61.8668 | -61.1481 | -61.3495 | -0.01831 | 0.082398 | -0.068665 | 0.66834 | 0.050354 | -0.032044 | 0.073242 | 0.11902 | -0.082397 | -0.16479 | -0.32043 | -0.17395 | -0.091553 | -0.10529 | 123.1705 | 123.3124 | 61.3998 | -123.1567 | 123.0743 | 123.1338 | 61.4136 | -123.3215
516.5312 | 123.3627 | -61.3266 | 61.9263 | -0.00091566 | 0.0089936 | 0.066176 | 0.0069621 | 0.066396 | -0.0037085 | -0.0046143 | -0.00083936 | -0.0052038 | 0.065567 | 0.07041 | -0.0060009 | -0.0091068 | 61.9125 | -60.8139 | 0.009155 | -61.3449 | 61.853 | -61.3358 | -61.2488 | -61.702 | 0.027466 | -61.5646 | 61.7432 | 61.8439 | -61.2396 | -61.4319 | -0.009155 | 0.07782 | -0.073243 | 0.5127 | -0.018311 | -0.096131 | -0.013733 | 0.086975 | -0.10529 | -0.18311 | -0.37537 | -0.23804 | -0.13275 | -0.082398 | 123.1796 | 123.2391 | 61.3358 | -123.175 | 123.0698 | 123.1705 | 61.3541 | -123.3582
518.2812 | 123.3261 | -61.3541 | 61.8805 | -0.0085447 | 0.0077118 | 0.069808 | 0.0054667 | 0.067892 | -0.0017859 | -0.0050415 | -0.00083936 | -0.0037086 | 0.065354 | 0.069342 | -0.0025829 | -0.0086796 | 61.9125 | -60.8551 | 0.086975 | -61.3541 | 61.8393 | -61.3632 | -61.3129 | -61.7386 | 0.036621 | -61.6562 | 61.7752 | 61.8347 | -61.2946 | -61.4731 | -0.009155 | 0.041199 | -0.041199 | 0.49896 | 0 | -0.041199 | 0.032044 | 0.059509 | -0.11902 | -0.10529 | -0.38452 | -0.30212 | -0.18311 | -0.045776 | 123.1934 | 123.2666 | 61.441 | -123.1934 | 123.1293 | 123.1888 | 61.3907 | -123.3536
520.0312 | 123.4543 | -61.3403 | 61.8393 | -0.00091566 | 0.00878 | 0.06404 | 0.0048257 | 0.067037 | 0.0018457 | -0.0026917 | 0.0067901 | -0.0034948 | 0.06514 | 0.070196 | 0.00019427 | -0.009534 | 61.9354 | -60.8047 | -0.004578 | -61.3541 | 61.8393 | -61.3495 | -61.3266 | -61.6562 | 0.068665 | -61.5738 | 61.7157 | 61.7798 | -61.2305 | -61.4365 | -0.009155 | 0.013733 | 0 | 0.53558 | -0.013733 | -0.027466 | 0.096131 | 0.10986 | -0.09613 | -0.1236 | -0.31586 | -0.23346 | -0.13733 | -0.059509 | 123.1796 | 123.2758 | 61.3358 | -123.1659 | 123.056 | 123.1201 | 61.409 | -123.2758
521.7188 | 123.4451 | -61.4868 | 61.6882 | -0.00091566 | 0.0096344 | 0.065749 | 0.0037577 | 0.067892 | 0.0018457 | -0.0037597 | -0.00083936 | -0.0030676 | 0.064286 | 0.07041 | -0.0010875 | -0.0097476 | 61.7752 | -61.1252 | -0.09613 | -61.5005 | 61.6425 | -61.5463 | -61.4502 | -61.8256 | -0.032043 | -61.7569 | 61.5738 | 61.5875 | -61.4456 | -61.6013 | -0.05951 | 0.036621 | -0.045776 | 0.36163 | -0.013733 | -0.050354 | 0.086976 | 0.041198 | -0.11444 | -0.11444 | -0.33875 | -0.27008 | -0.15564 | -0.10071 | 123.1293 | 123.262 | 61.3907 | -123.1384 | 123.0606 | 123.0743 | 61.4548 | -123.2895
523.4531 | 123.3215 | -61.2671 | 61.9812 | -0.00091566 | 0.0057892 | 0.067244 | 0.0018351 | 0.065542 | -0.0028539 | -0.0041869 | -0.00083936 | -0.0047766 | 0.064286 | 0.069769 | -0.00066033 | -0.0084658 | 62.0178 | -60.5942 | 0.027466 | -61.2442 | 61.8759 | -61.2259 | -61.1938 | -61.5829 | 0.054932 | -61.4914 | 61.8347 | 61.8713 | -61.1572 | -61.3449 | 0.041199 | 0.073242 | -0.10529 | 0.67291 | 0.022888 | -0.050354 | 0.036621 | 0.10986 | -0.07782 | -0.14648 | -0.31586 | -0.2243 | -0.14648 | -0.10986 | 123.143 | 123.2849 | 61.2946 | -123.175 | 123.1018 | 123.1384 | 61.322 | -123.3261
525.2031 | 123.4131 | -61.1938 | 61.9675 | 0.0067138 | 0.0092072 | 0.065108 | 0.0041849 | 0.067251 | 0.0044091 | -0.0035461 | -0.00083936 | 0.0003504 | 0.062577 | 0.069983 | -0.00087393 | -0.009534 | 62.0865 | -60.5026 | 0.09613 | -61.1893 | 61.9995 | -61.2259 | -61.1664 | -61.528 | 0.09613 | -61.4777 | 61.9263 | 61.972 | -61.1206 | -61.3174 | -0.032043 | 0.027466 | 0.032044 | 0.69122 | 0.004578 | -0.022888 | 0.11902 | 0.073243 | -0.1236 | -0.041198 | -0.33417 | -0.28381 | -0.16022 | 0.004578 | 123.1934 | 123.2803 | 61.29 | -123.1338 | 123.1201 | 123.1659 | 61.29 | -123.2849
526.9688 | 123.3215 | -61.2991 | 61.9583 | 0.0067138 | 0.0079254 | 0.066176 | 0.0086709 | 0.068105 | -0.0047765 | -0.0016235 | 0.0067901 | -0.0041358 | 0.065995 | 0.068701 | -0.0034373 | -0.0080386 | 61.9995 | -60.6491 | 0.17395 | -61.2671 | 61.8484 | -61.2991 | -61.2076 | -61.6013 | 0.14191 | -61.4822 | 61.7752 | 61.8576 | -61.2076 | -61.3815 | 0 | 0.091552 | -0.10986 | 0.65002 | 0.032043 | -0.059509 | 0.041199 | 0.091552 | -0.082398 | -0.1831 | -0.30212 | -0.18311 | -0.10071 | -0.10071 | 123.1476 | 123.2986 | 61.4731 | -123.1659 | 123.0743 | 123.1567 | 61.441 | -123.3398
528.6406 | 123.3307 | -61.2396 | 61.9766 | -0.0085447 | 0.012839 | 0.066817 | 0.0086709 | 0.065328 | -0.0022131 | -0.0050415 | -0.00083936 | -0.0022132 | 0.066208 | 0.072974 | -0.0042919 | -0.0086796 | 61.9583 | -60.6766 | 0.068665 | -61.2946 | 61.9766 | -61.2946 | -61.203 | -61.6562 | 0.041199 | -61.5509 | 61.9034 | 61.908 | -61.2122 | -61.3724 | -0.054932 | 0.036621 | 0 | 0.56305 | -0.054932 | -0.091553 | -0.018311 | 0.027466 | -0.13275 | -0.073243 | -0.41656 | -0.31128 | -0.17853 | -0.068665 | 123.2162 | 123.1979 | 61.3083 | -123.1796 | 123.143 | 123.1476 | 61.2808 | -123.349
530.4062 | 123.3902 | -61.3083 | 61.8759 | -0.016174 | 0.009848 | 0.065962 | 0.0041849 | 0.065969 | 0.0031275 | -0.0026917 | 0.0067901 | -0.0022132 | 0.066422 | 0.07276 | 0.0014759 | -0.0080386 | 61.9492 | -60.7727 | 0.045776 | -61.3312 | 61.8668 | -61.3449 | -61.2625 | -61.6837 | 0.018311 | -61.6516 | 61.7798 | 61.8256 | -61.2717 | -61.4594 | -0.036621 | 0.045777 | -0.009156 | 0.53558 | -0.022888 | -0.068665 | 0.073242 | 0.036622 | -0.15106 | -0.096131 | -0.37537 | -0.34332 | -0.19226 | -0.050354 | 123.175 | 123.2574 | 61.3541 | -123.1384 | 123.0881 | 123.1339 | 61.3266 | -123.3353
532.1719 | 123.3261 | -61.2808 | 61.9812 | 0.014343 | 0.0092072 | 0.068312 | 0.0088847 | 0.065755 | -0.0028539 | -0.0020507 | -0.0084684 | -0.0066992 | 0.064286 | 0.069556 | -0.0042919 | -0.0065432 | 62.0132 | -60.5759 | 0.16937 | -61.2167 | 61.908 | -61.2762 | -61.1893 | -61.5646 | 0.14191 | -61.4456 | 61.8027 | 61.853 | -61.1893 | -61.3541 | 0.004578 | 0.091553 | -0.073242 | 0.70496 | 0.064087 | -0.027466 | 0.032044 | 0.091553 | -0.073242 | -0.17853 | -0.28381 | -0.1648 | -0.091553 | -0.12817 | 123.1888 | 123.2941 | 61.4502 | -123.1705 | 123.0835 | 123.1338 | 61.4227 | -123.3353
533.9062 | 123.3353 | -62.4252 | 60.7773 | -0.00091566 | 0.08013 | 0.066603 | 0.0095255 | 0.1339 | -0.0026403 | -0.0037597 | -0.00083936 | -0.001145 | 0.06749 | 0.071051 | -0.0040783 | -0.007825 | 60.7819 | 60.8093 | 0.059509 | -62.4344 | 60.7864 | -62.439 | -62.3611 | -62.8326 | 0.036621 | -62.7365 | 60.704 | 60.7452 | -62.352 | -62.5534 | -0.013733 | 0.064087 | 0.009155 | 123.2346 | -0.009155 | -0.073242 | 0.004577 | 0.073242 | -0.12817 | -0.073242 | -0.40741 | -0.31128 | -0.1831 | -0.032044 | 123.2117 | 123.2071 | 62.4847 | -123.1384 | 123.1293 | 123.1705 | 62.4619 | -123.3307
535.5938 | 123.3032 | -62.2971 | 60.9283 | -0.00091566 | 0.073508 | 0.067458 | 0.0046121 | 0.13283 | -0.0049903 | -0.0046143 | 0.0067901 | -0.0060584 | 0.063004 | 0.069769 | -0.0030101 | -0.0069706 | 60.9375 | 60.9787 | 0.018311 | -62.265 | 60.8643 | -62.2879 | -62.2147 | -62.645 | 0.045776 | -62.5122 | 60.7864 | 60.8414 | -62.2055 | -62.4023 | 0.009155 | 0.082397 | -0.064087 | 123.2758 | 0.032043 | -0.050354 | 0.009155 | 0.091553 | -0.10529 | -0.14191 | -0.3479 | -0.21515 | -0.10986 | -0.086975 | 123.1613 | 123.2346 | 62.3154 | -123.143 | 123.0835 | 123.1384 | 62.3428 | -123.3307
537.3594 | 123.436 | -62.3291 | 60.7956 | -0.00091566 | 0.077353 | 0.065749 | 0.0041849 | 0.13711 | 0.0018457 | -0.0033325 | 0.0067901 | -0.0024268 | 0.064713 | 0.071692 | -0.0027965 | -0.0091068 | 60.8688 | 60.8826 | -0.004578 | -62.3428 | 60.8139 | -62.352 | -62.2971 | -62.6724 | 0.041199 | -62.59 | 60.6995 | 60.7544 | -62.2604 | -62.4298 | -0.022888 | 0.032044 | 0.018311 | 123.2117 | -0.013732 | -0.045776 | 0.073242 | 0.068665 | -0.10071 | -0.09613 | -0.34332 | -0.26093 | -0.16022 | -0.041198 | 123.143 | 123.1979 | 62.3245 | -123.0927 | 123.0286 | 123.0835 | 62.3703 | -123.2254
539.1094 | 123.317 | -62.3749 | 60.8414 | -0.00091566 | 0.077353 | 0.06639 | 0.0037577 | 0.13625 | -0.00093131 | -0.0050415 | 0.01442 | -0.0047766 | 0.064927 | 0.069342 | -0.0019419 | -0.0084658 | 60.8871 | 60.9467 | 0.068665 | -62.3383 | 60.7361 | -62.3749 | -62.3062 | -62.677 | 0.091553 | -62.5626 | 60.6674 | 60.7315 | -62.2833 | -62.4847 | 0 | 0.068665 | -0.10529 | 123.3215 | 0.036621 | -0.032044 | 0.045776 | 0.091553 | -0.10986 | -0.17395 | -0.30212 | -0.18768 | -0.07782 | -0.10986 | 123.111 | 123.262 | 62.4435 | -123.1476 | 123.0423 | 123.1064 | 62.4664 | -123.3261
540.875 | 123.2895 | -62.3428 | 60.91 | -0.00091566 | 0.073721 | 0.06639 | 0.0061075 | 0.13561 | -0.0049903 | -0.0041869 | 0.0067901 | -0.004563 | 0.064927 | 0.067419 | -0.0045055 | -0.009534 | 60.8917 | 60.9558 | 0.032043 | -62.3062 | 60.8093 | -62.3245 | -62.233 | -62.677 | 0.045776 | -62.5488 | 60.7452 | 60.7681 | -62.233 | -62.4115 | 0.01831 | 0.10986 | -0.10071 | 123.2986 | 0.036621 | -0.073242 | -0.01831 | 0.10986 | -0.068665 | -0.1648 | -0.33417 | -0.20599 | -0.13733 | -0.14191 | 123.1522 | 123.2346 | 62.3749 | -123.143 | 123.0881 | 123.111 | 62.3886 | -123.3215
542.625 | 123.3627 | -62.4344 | 60.7773 | -0.00091566 | 0.076498 | 0.06404 | 0.0020487 | 0.13497 | 0.0046229 | -0.0026917 | 0.01442 | 0.0007776 | 0.064286 | 0.070837 | 0.0019033 | -0.0091068 | 60.7727 | 60.7956 | 0.032043 | -62.4481 | 60.7452 | -62.4481 | -62.3749 | -62.8326 | 0.018311 | -62.7731 | 60.6628 | 60.6628 | -62.3657 | -62.5534 | -0.013733 | 0.059509 | -0.032044 | 123.23 | -0.013733 | -0.073242 | -0.004578 | 0.068664 | -0.11902 | -0.11444 | -0.39825 | -0.33874 | -0.21973 | -0.11444 | 123.1796 | 123.2071 | 62.4664 | -123.1522 | 123.0972 | 123.0972 | 62.4527 | -123.3307
544.3125 | 123.3536 | -62.4893 | 60.6583 | -0.0085447 | 0.076712 | 0.064681 | 0.0024759 | 0.13604 | 0.0020593 | -0.0024779 | -0.0084684 | -0.0002906 | 0.065995 | 0.069769 | -0.00044673 | -0.0080386 | 60.6445 | 60.6583 | -0.004578 | -62.5442 | 60.6491 | -62.5442 | -62.471 | -62.9288 | 0.004578 | -62.8555 | 60.5576 | 60.6079 | -62.4481 | -62.6358 | -0.054931 | 0.018311 | -0.009155 | 123.1476 | -0.054931 | -0.073242 | -0.013733 | 0.041199 | -0.14648 | -0.10071 | -0.43945 | -0.36621 | -0.21973 | -0.050354 | 123.1384 | 123.1338 | 62.4847 | -123.1293 | 123.0469 | 123.0972 | 62.4939 | -123.2941
546.0625 | 110.6277 | -118.5562 | 4.6051 | -0.0085447 | 0.10705 | 0.064894 | 0.0054667 | 0.13454 | 0.00099129 | -0.0016235 | -0.0084684 | -0.0015722 | 0.063858 | 0.072333 | -0.0010875 | -0.0073978 | 4.8294 | 4.7241 | -0.10529 | -118.2358 | 4.9118 | -118.5516 | -118.2907 | -118.9865 | -0.23804 | -118.6752 | 4.7241 | 4.7516 | -118.3731 | -118.4875 | 0.004577 | 0.2655 | 0.3067 | 123.2803 | 0.32043 | 0.054931 | 0.2243 | 0.1831 | 0.068664 | 0.11902 | -0.4303 | -0.11902 | -0.18768 | 0.14648 | 123.468 | 123.3856 | 118.4509 | -122.8958 | 123.2803 | 123.3078 | 118.3182 | -123.0927
547.8281 | 123.3353 | -120.3918 | 2.8244 | -0.00091566 | 0.10876 | 0.064894 | 0.0088847 | 0.13454 | -0.0028539 | -0.0041869 | 0.0067901 | -0.0019996 | 0.067917 | 0.073187 | -0.0055735 | -0.006116 | 2.7237 | 2.6962 | -0.022888 | -120.2271 | 2.8473 | -120.5658 | -120.3827 | -120.9366 | -0.09613 | -120.5933 | 2.7832 | 2.8061 | -120.3644 | -120.5704 | -0.17395 | 0.009156 | 0.022888 | 123.0881 | 0.16479 | 0.15564 | -0.10071 | 0.027466 | -0.17853 | -0.041199 | -0.54474 | -0.20142 | -0.022888 | -0.018311 | 123.2391 | 123.1155 | 120.369 | -123.2071 | 123.175 | 123.1979 | 120.2957 | -123.3948
549.5156 | 123.3765 | -120.7581 | 2.4857 | -0.00091566 | 0.1079 | 0.065535 | 0.0041849 | 0.13796 | 0.0029139 | -0.0016235 | 0.0067901 | 0.0003504 | 0.064499 | 0.072974 | 0.0019033 | -0.0076114 | 2.9068 | 2.8885 | -0.16022 | -120.2362 | 2.9068 | -120.5338 | -120.4468 | -120.8496 | 0.041199 | -120.4651 | 2.5955 | 2.6825 | -120.2454 | -120.433 | 0.2243 | 0.31128 | 0.42114 | 123.6465 | 0.52185 | 0.21057 | 0.42114 | 0.5127 | 0.32501 | 0.10986 | -0.091552 | 0.29297 | -0.032044 | 0.19684 | 123.6649 | 123.6649 | 120.5978 | -122.9324 | 123.3536 | 123.4406 | 120.7993 | -122.9187
551.2656 | 123.317 | -121.0831 | 2.2064 | -0.00091566 | 0.10534 | 0.066603 | 0.0071757 | 0.13668 | -0.0069129 | -0.0024779 | -0.00083936 | -0.0056312 | 0.06749 | 0.072546 | -0.0053599 | -0.0059024 | 1.5198 | 1.5747 | -0.059509 | -121.3303 | 1.6388 | -121.6324 | -121.463 | -122.0261 | -0.041199 | -121.6049 | 1.5793 | 1.6342 | -121.3715 | -121.4996 | -0.54932 | -0.37994 | -0.56763 | 122.6578 | -0.24719 | 0.13275 | -0.68665 | -0.28839 | -0.41657 | -0.62714 | -0.94299 | -0.52185 | -0.10528 | -0.57221 | 122.7219 | 122.6028 | 121.0236 | -123.6694 | 122.6624 | 122.7173 | 121.0419 | -123.7061
553.0156 | 123.3627 | -122.4518 | 0.7782 | -0.016174 | 0.10876 | 0.064253 | 0.0035441 | 0.13732 | 0.0041955 | -0.0029053 | -0.00083936 | -7.6996e-05 | 0.06514 | 0.072119 | 0.00083507 | -0.0082522 | 0.66376 | 0.61798 | -0.15564 | -122.2275 | 0.81482 | -122.5159 | -122.3282 | -122.9645 | -0.10986 | -122.6852 | 0.737 | 0.75073 | -122.3877 | -122.6395 | -0.064087 | 0.1236 | 0.036621 | 123.0698 | 0.2243 | 0.10071 | -0.11444 | 0.064087 | -0.18768 | -0.041198 | -0.5127 | -0.23346 | -0.045777 | -0.027466 | 123.2666 | 123.1155 | 122.2961 | -123.1064 | 123.1888 | 123.2025 | 122.3419 | -123.4177
554.6875 | 123.3582 | -122.4197 | 0.81482 | -0.0085447 | 0.10982 | 0.063826 | 0.0050393 | 0.13646 | 0.0029139 | -0.0011963 | 0.0067901 | -0.0017858 | 0.064713 | 0.073187 | 0.00062147 | -0.006116 | 0.67291 | 0.63171 | -0.086975 | -122.2412 | 0.77362 | -122.5433 | -122.3236 | -122.937 | 0.073242 | -122.5296 | 0.74158 | 0.78735 | -122.3099 | -122.58 | -0.1236 | 0.096131 | -0.041198 | 123.0515 | 0.17853 | 0.082397 | -0.14191 | 0.10986 | -0.16022 | -0.073242 | -0.51727 | -0.10986 | 0.050354 | -0.027465 | 123.1934 | 123.0927 | 122.3328 | -123.1384 | 123.1613 | 123.2071 | 122.493 | -123.3948
556.4531 | 123.3078 | -122.58 | 0.68207 | -0.016174 | 0.10747 | 0.069594 | 0.0080301 | 0.13283 | -0.0069129 | -0.0014099 | 0.0067901 | -0.0069128 | 0.067276 | 0.068701 | -0.0072825 | -0.0071842 | 0.65002 | 0.67291 | -0.018311 | -122.2824 | 0.62256 | -122.612 | -122.3877 | -122.9782 | 0.068665 | -122.58 | 0.55389 | 0.59967 | -122.4335 | -122.7081 | -0.032044 | 0.19226 | -0.059509 | 123.2529 | 0.29755 | 0.10528 | -0.032044 | 0.14648 | -0.12817 | -0.12817 | -0.39825 | 0 | 0.12817 | -0.082398 | 123.2025 | 123.23 | 122.5616 | -123.0698 | 123.1338 | 123.1796 | 122.6486 | -123.3902
558.2031 | 123.3261 | -122.2046 | 1.062 | -0.0085447 | 0.10235 | 0.067458 | 0.0069621 | 0.13476 | -0.0043493 | -0.0035461 | -0.0084684 | -0.0060584 | 0.064286 | 0.070624 | -0.0027965 | -0.007825 | 0.94757 | 0.9613 | -0.12817 | -121.962 | 1.0254 | -122.2366 | -122.0535 | -122.6807 | -0.041199 | -122.2733 | 0.92926 | 0.99335 | -122.1085 | -122.3236 | -0.032043 | 0.15106 | -0.036621 | 123.1659 | 0.24262 | 0.091553 | -0.11444 | 0.096131 | -0.11902 | -0.13275 | -0.47607 | -0.068664 | 0.050354 | -0.068665 | 123.23 | 123.1522 | 122.0764 | -123.1155 | 123.1338 | 123.1979 | 122.1634 | -123.3856
559.8906 | 123.4085 | -122.3053 | 0.93384 | -0.00091566 | 0.10811 | 0.06639 | 0.0063211 | 0.13924 | 0.0014185 | -0.0020507 | -0.0084684 | -0.0005042 | 0.065995 | 0.070624 | -0.00087393 | -0.0084658 | 0.76446 | 0.71411 | -0.19684 | -122.1771 | 0.90179 | -122.4243 | -122.2 | -122.8592 | -0.082397 | -122.5296 | 0.81024 | 0.85144 | -122.2458 | -122.5113 | -0.11902 | 0.10529 | -0.032044 | 123.0194 | 0.12817 | 0.022888 | -0.16937 | 0.059509 | -0.20599 | -0.1236 | -0.55389 | -0.2243 | -0.01831 | -0.082398 | 123.2071 | 123.0698 | 122.1085 | -123.1338 | 123.1155 | 123.1567 | 122.2229 | -123.4451
561.6406 | 123.2758 | -122.4014 | 0.88806 | -0.0085447 | 0.10384 | 0.067031 | 0.00012606 | 0.13454 | -0.0019995 | -0.0033325 | -0.00083936 | -0.002854 | 0.061936 | 0.071692 | -0.0023693 | -0.0054752 | 0.82855 | 0.82855 | -0.14191 | -122.1268 | 0.80566 | -122.4152 | -122.2321 | -122.8088 | -0.009155 | -122.4426 | 0.74158 | 0.78278 | -122.2366 | -122.4884 | -0.013733 | 0.16937 | -0.082398 | 123.23 | 0.27466 | 0.10529 | -0.05951 | 0.16479 | -0.086975 | -0.14648 | -0.40741 | -0.041199 | 0.045776 | -0.10529 | 123.2071 | 123.23 | 122.2595 | -123.1201 | 123.143 | 123.1842 | 122.3923 | -123.3765
563.3906 | 123.3673 | -122.3602 | 0.85144 | -0.00091566 | 0.10705 | 0.067244 | 0.0067483 | 0.13433 | -0.00071771 | -0.0033325 | 0.0067901 | -0.001145 | 0.067704 | 0.072119 | -0.0025829 | -0.0080386 | 0.72784 | 0.67749 | -0.10071 | -122.1725 | 0.85144 | -122.4518 | -122.2595 | -122.905 | -0.018311 | -122.5571 | 0.77362 | 0.82398 | -122.2778 | -122.5388 | -0.091553 | 0.10071 | 0 | 123.0377 | 0.18768 | 0.086975 | -0.1236 | 0.082397 | -0.17853 | -0.077819 | -0.54474 | -0.19684 | -0.018311 | -0.027465 | 123.2117 | 123.0881 | 122.2595 | -123.111 | 123.1339 | 123.1842 | 122.3419 | -123.3902
565.1406 | 123.3536 | -122.319 | 0.84686 | -0.00091566 | 0.10726 | 0.067244 | 0.0035441 | 0.13476 | 0.00013669 | -0.0039733 | -0.0084684 | -0.0017858 | 0.06514 | 0.073187 | -0.0021557 | -0.0073978 | 0.75531 | 0.70038 | -0.11902 | -122.1588 | 0.88806 | -122.4518 | -122.2412 | -122.8775 | -0.027466 | -122.5388 | 0.81482 | 0.83313 | -122.2687 | -122.5113 | -0.13275 | 0.07782 | 0.041199 | 123.0194 | 0.16022 | 0.082398 | -0.091553 | 0.050354 | -0.19226 | -0.032044 | -0.55847 | -0.21973 | -0.027465 | -0.013733 | 123.2071 | 123.0743 | 122.2 | -123.0881 | 123.1338 | 123.1522 | 122.2916 | -123.3582
566.8906 | 123.3261 | -122.438 | 0.77362 | -0.00091566 | 0.10384 | 0.064681 | 0.0037577 | 0.13625 | -0.0017859 | -0.0014099 | -0.00083936 | -0.0047766 | 0.065995 | 0.071265 | -0.0023693 | -0.0063296 | 0.74158 | 0.737 | -0.17853 | -122.1863 | 0.72784 | -122.4792 | -122.2961 | -122.8638 | -0.032043 | -122.5021 | 0.64087 | 0.67749 | -122.319 | -122.5708 | -0.041199 | 0.14191 | -0.045777 | 123.175 | 0.25177 | 0.10986 | -0.032044 | 0.11902 | -0.13275 | -0.13275 | -0.42572 | -0.064087 | 0.068665 | -0.096131 | 123.1659 | 123.1796 | 122.2595 | -123.0698 | 123.0789 | 123.1155 | 122.406 | -123.3444
568.5625 | 123.3627 | -122.2275 | 0.9613 | -0.00091566 | 0.10961 | 0.065749 | 0.0048257 | 0.1339 | 0.0027003 | -0.00012812 | -0.00083936 | -0.0009314 | 0.064286 | 0.072333 | -0.0015147 | -0.009534 | 0.86517 | 0.83313 | -0.068665 | -122.0398 | 0.93384 | -122.3419 | -122.1497 | -122.7264 | 0.050354 | -122.4106 | 0.86975 | 0.89722 | -122.1771 | -122.4243 | -0.11444 | 0.07782 | -0.027466 | 123.0606 | 0.18768 | 0.10986 | -0.096131 | 0.050354 | -0.19684 | -0.091553 | -0.49896 | -0.1831 | 0.013733 | -0.064087 | 123.1613 | 123.0927 | 122.1588 | -123.111 | 123.0972 | 123.1247 | 122.2778 | -123.3856
570.3125 | 123.2346 | -122.168 | 1.0712 | 0.0067138 | 0.11004 | 0.067885 | 0.0069621 | 0.13689 | -0.0015723 | -0.0044007 | 0.0067901 | -0.0066992 | 0.06749 | 0.073828 | -0.0030101 | -0.0082522 | 0.91553 | 0.91095 | -0.10071 | -121.9803 | 1.0391 | -122.2549 | -122.0444 | -122.699 | -0.022888 | -122.319 | 0.97961 | 1.0254 | -122.1039 | -122.2916 | -0.086975 | 0.1236 | -0.032043 | 123.0789 | 0.18768 | 0.064087 | -0.15564 | 0.064087 | -0.1236 | -0.091553 | -0.53101 | -0.15106 | -0.027466 | -0.045776 | 123.2071 | 123.0835 | 122.0673 | -123.1155 | 123.1476 | 123.1934 | 122.1451 | -123.3627
572.0625 | 123.2758 | -122.2366 | 0.99792 | -0.0085447 | 0.1047 | 0.068099 | 0.0071757 | 0.13497 | -0.0045629 | -0.0048279 | -0.00083936 | -0.0066992 | 0.065567 | 0.07041 | -0.0057873 | -0.0069706 | 0.88348 | 0.90179 | -0.16479 | -121.9849 | 0.95673 | -122.2687 | -122.0718 | -122.6944 | -0.004578 | -122.3007 | 0.86517 | 0.90179 | -122.1222 | -122.3557 | -0.032044 | 0.16479 | -0.041199 | 123.1384 | 0.25177 | 0.086975 | -0.11444 | 0.11444 | -0.11902 | -0.13275 | -0.45776 | -0.064087 | 0.054932 | -0.096131 | 123.1934 | 123.1201 | 122.0718 | -123.0698 | 123.1018 | 123.1384 | 122.2321 | -123.3536
573.7969 | 123.262 | -122.1909 | 1.0345 | -0.0085447 | 0.10918 | 0.064253 | 0.0086709 | 0.13347 | 0.00056389 | -0.0052551 | -0.00083936 | -0.0043494 | 0.066849 | 0.071692 | -0.0057873 | -0.0093204 | 0.87433 | 0.85602 | -0.1236 | -122.0123 | 1.03 | -122.2733 | -122.1039 | -122.7219 | -0.022888 | -122.3877 | 0.95215 | 0.97046 | -122.1313 | -122.3511 | -0.082397 | 0.086975 | -0.004578 | 123.0469 | 0.17853 | 0.091553 | -0.16022 | 0.059509 | -0.16022 | -0.082398 | -0.53101 | -0.19684 | -0.036621 | -0.064087 | 123.2208 | 123.0652 | 122.0673 | -123.1384 | 123.143 | 123.1613 | 122.168 | -123.3856
575.4844 | 123.381 | -121.9666 | 1.1993 | -0.00091566 | 0.10641 | 0.066603 | 0.0031167 | 0.13476 | 0.00077749 | -0.00098272 | -0.0084684 | -0.0034948 | 0.064286 | 0.071478 | 0.00040787 | -0.0056888 | 1.0941 | 1.0483 | -0.25177 | -121.8292 | 1.2085 | -122.0764 | -121.8567 | -122.493 | -0.082397 | -122.168 | 1.1169 | 1.1307 | -121.9025 | -122.1405 | -0.10986 | 0.10986 | 0.009155 | 123.0148 | 0.13733 | 0.027465 | -0.10529 | 0.064087 | -0.17395 | -0.082398 | -0.52643 | -0.20142 | -0.027466 | -0.068665 | 123.175 | 123.0606 | 121.7148 | -123.056 | 123.0835 | 123.0972 | 121.8842 | -123.3398
577.1875 | 123.3582 | -121.6095 | 1.5427 | -0.00091566 | 0.10598 | 0.065962 | 0.0035441 | 0.13604 | 0.00013669 | -0.0022643 | -0.00083936 | -0.0037086 | 0.064713 | 0.070837 | -1.9327e-05 | -0.0080386 | 1.4832 | 1.4786 | -0.1831 | -121.4264 | 1.5106 | -121.701 | -121.5088 | -122.0901 | -0.022888 | -121.7697 | 1.4099 | 1.442 | -121.5454 | -121.7743 | -0.091553 | 0.10071 | -0.032044 | 123.0881 | 0.1831 | 0.082397 | -0.05951 | 0.064087 | -0.16479 | -0.13275 | -0.48065 | -0.16022 | 0.004578 | -0.10071 | 123.1201 | 123.0927 | 121.4264 | -123.0515 | 123.0194 | 123.0515 | 121.5866 | -123.317
578.9375 | 123.2803 | -121.3989 | 1.767 | -0.00091566 | 0.10448 | 0.068312 | 0.0078165 | 0.13604 | -0.0069129 | -0.0052551 | -0.0084684 | -0.0066992 | 0.063858 | 0.070196 | -0.0042919 | -0.0073978 | 1.442 | 1.4648 | -0.10529 | -121.051 | 1.5427 | -121.4218 | -121.2662 | -122.1222 | -0.045776 | -121.756 | 1.5518 | 1.5564 | -121.4401 | -121.4951 | -0.022888 | 0.13275 | -0.2243 | 122.8638 | 0.3479 | 0.21515 | -0.32501 | -0.041199 | -0.09613 | -0.21515 | -0.72327 | -0.35706 | -0.26093 | -0.21057 | 122.9416 | 122.8409 | 121.2936 | -123.0331 | 122.9507 | 122.9553 | 121.3531 | -123.262
580.625 | 123.2254 | -122.0306 | 1.181 | 0.0067138 | 0.10918 | 0.067458 | 0.0080301 | 0.13476 | -0.00071771 | -0.0035461 | -0.0084684 | -0.0032812 | 0.065354 | 0.069556 | -0.0040783 | -0.0093204 | 1.1032 | 1.1398 | -0.041199 | -121.7789 | 1.0986 | -122.0901 | -121.9162 | -122.4792 | 0.073242 | -122.1176 | 1.0208 | 1.0574 | -121.9391 | -122.1725 | -0.059509 | 0.11444 | -0.082397 | 123.1705 | 0.25177 | 0.13733 | -0.07782 | 0.091553 | -0.14191 | -0.16022 | -0.44861 | -0.086975 | 0.054931 | -0.1236 | 123.1293 | 123.1339 | 121.9894 | -123.0972 | 123.0515 | 123.0881 | 122.1039 | -123.3536
582.3906 | 123.3353 | -121.7697 | 1.4465 | -0.0085447 | 0.10747 | 0.067244 | 0.0041849 | 0.13646 | 0.0018457 | -0.0016235 | -0.016098 | -0.0022132 | 0.065567 | 0.072119 | 0.00062147 | -0.0093204 | 1.1169 | 1.062 | -0.32959 | -121.7926 | 1.2405 | -122.0123 | -121.8338 | -122.4472 | -0.16022 | -122.1405 | 1.1902 | 1.2177 | -121.8658 | -122.0993 | -0.24262 | -0.064087 | -0.20599 | 122.8317 | -0.022889 | 0.041198 | -0.32959 | -0.096131 | -0.32959 | -0.25635 | -0.67749 | -0.37079 | -0.041199 | -0.22888 | 123.0103 | 122.8867 | 121.4401 | -123.2803 | 122.9599 | 122.9874 | 121.6095 | -123.5458
584.1406 | 123.2895 | -122.1634 | 1.0162 | -0.00091566 | 0.10854 | 0.067458 | 0.0061075 | 0.13476 | -0.00050411 | -0.0037597 | 0.0067901 | -0.0047766 | 0.064713 | 0.069983 | -0.0038647 | -0.0071842 | 1.0071 | 1.0025 | -0.16479 | -121.8979 | 0.98877 | -122.1954 | -122.0032 | -122.5754 | 0.018311 | -122.2137 | 0.91095 | 0.9201 | -122.0535 | -122.2595 | -0.032044 | 0.16022 | -0.027465 | 123.1659 | 0.2655 | 0.10529 | -0.009155 | 0.10986 | -0.09613 | -0.10528 | -0.41199 | -0.050354 | 0.045776 | -0.09613 | 123.1522 | 123.1705 | 121.9986 | -123.0194 | 123.0743 | 123.0835 | 122.1817 | -123.2758
585.8906 | 123.2803 | -122.1634 | 1.0208 | -0.00091566 | 0.11111 | 0.064681 | 0.0035441 | 0.13711 | 0.0027003 | -0.0014099 | -0.0084684 | -0.0024268 | 0.064927 | 0.072546 | -0.00044673 | -0.0076114 | 0.95215 | 0.91095 | -0.15106 | -121.9757 | 1.0025 | -122.2137 | -122.0444 | -122.6349 | 0.013733 | -122.3511 | 0.92468 | 0.96588 | -122.0764 | -122.319 | -0.050354 | 0.11902 | -0.018311 | 123.0743 | 0.18768 | 0.068665 | -0.068665 | 0.086975 | -0.15564 | -0.09613 | -0.4715 | -0.18768 | -0.032043 | -0.054932 | 123.1659 | 123.1155 | 122.0123 | -123.0652 | 123.0881 | 123.1293 | 122.1771 | -123.3398
587.5781 | 123.3032 | -122.287 | 0.87433 | -0.00091566 | 0.10726 | 0.06639 | 0.0039713 | 0.13753 | -0.0015723 | -0.0014099 | -0.0084684 | -0.0056312 | 0.063431 | 0.070837 | -0.0017283 | -0.0071842 | 0.85144 | 0.85144 | -0.17853 | -122.0444 | 0.82855 | -122.3557 | -122.1634 | -122.7219 | 0.027466 | -122.374 | 0.75073 | 0.78735 | -122.1954 | -122.4243 | -0.068665 | 0.1236 | -0.045777 | 123.1384 | 0.24261 | 0.11902 | -0.022889 | 0.091552 | -0.13733 | -0.1236 | -0.43488 | -0.086975 | 0.050354 | -0.086975 | 123.1155 | 123.1384 | 122.1085 | -123.0377 | 123.0377 | 123.0743 | 122.3145 | -123.2986
589.3281 | 123.2391 | -122.2504 | 0.95215 | -0.0085447 | 0.10747 | 0.068526 | 0.0095255 | 0.13476 | -0.0037085 | -0.0048279 | -0.0084684 | -0.0043494 | 0.064713 | 0.068487 | -0.0047191 | -0.0080386 | 0.9201 | 0.94757 | -0.086975 | -121.994 | 0.89264 | -122.2778 | -122.1176 | -122.6761 | 0.10071 | -122.2824 | 0.8194 | 0.84228 | -122.1313 | -122.3694 | -0.027466 | 0.13275 | -0.059509 | 123.1979 | 0.25635 | 0.1236 | -0.032043 | 0.11902 | -0.11902 | -0.13275 | -0.42572 | -0.032044 | 0.086975 | -0.10986 | 123.143 | 123.1705 | 122.1634 | -123.0698 | 123.0698 | 123.0927 | 122.3511 | -123.3215
591.0312 | 123.262 | -122.2641 | 0.9201 | -0.0085447 | 0.10619 | 0.066603 | 0.0080301 | 0.13476 | -0.0045629 | -0.0031189 | -0.00083936 | -0.0052038 | 0.063004 | 0.069769 | -0.0032237 | -0.0076114 | 0.8194 | 0.82855 | -0.19684 | -122.0398 | 0.86975 | -122.319 | -122.1359 | -122.7402 | -0.009155 | -122.3419 | 0.81482 | 0.83771 | -122.1405 | -122.3969 | -0.054932 | 0.12817 | -0.050354 | 123.0927 | 0.2243 | 0.09613 | -0.10071 | 0.1236 | -0.13275 | -0.10529 | -0.47607 | -0.07782 | 0.054932 | -0.082397 | 123.1338 | 123.0835 | 122.0673 | -123.056 | 123.0789 | 123.1018 | 122.2549 | -123.317
592.7812 | 123.175 | -122.3145 | 0.90179 | -0.0085447 | 0.10876 | 0.067031 | 0.0052531 | 0.13369 | 0.00013669 | -0.0035461 | -0.016098 | -0.0054174 | 0.064927 | 0.071051 | -0.0034373 | -0.0067568 | 0.83771 | 0.82398 | -0.091553 | -122.0581 | 0.83313 | -122.3785 | -122.1863 | -122.7676 | 0.050354 | -122.4106 | 0.76446 | 0.8194 | -122.2275 | -122.438 | -0.064087 | 0.12817 | -0.068664 | 123.1384 | 0.25635 | 0.12817 | -0.064086 | 0.086975 | -0.1236 | -0.13733 | -0.45319 | -0.09613 | 0.027466 | -0.082397 | 123.1476 | 123.1522 | 122.2229 | -123.0881 | 123.0789 | 123.1338 | 122.3648 | -123.3398
594.5312 | 123.3032 | -122.2458 | 0.86975 | -0.00091566 | 0.10982 | 0.067458 | 0.0061075 | 0.13711 | 0.0037683 | -0.0024779 | -0.00083936 | -0.0017858 | 0.065995 | 0.070624 | -0.0040783 | -0.010602 | 0.77362 | 0.71869 | -0.16937 | -122.113 | 0.87891 | -122.3648 | -122.2137 | -122.8226 | -0.004578 | -122.493 | 0.80566 | 0.82398 | -122.2504 | -122.4838 | -0.11902 | 0.032044 | 0.009155 | 122.9645 | 0.13275 | 0.10071 | -0.09613 | -0.004577 | -0.23804 | -0.064087 | -0.57678 | -0.24719 | -0.009155 | -0.045776 | 123.1247 | 123.0194 | 122.0764 | -123.0835 | 123.0515 | 123.0698 | 122.2412 | -123.3536
596.2188 | 123.2117 | -122.1863 | 1.0025 | -0.0085447 | 0.10876 | 0.067031 | 0.0063211 | 0.13411 | -0.0022131 | -0.0054687 | -0.00083936 | -0.0075538 | 0.065781 | 0.071051 | -0.0023693 | -0.0067568 | 0.96588 | 0.98877 | -0.082397 | -121.9254 | 0.95673 | -122.2046 | -122.0169 | -122.6028 | 0.091553 | -122.2366 | 0.86517 | 0.9201 | -122.0444 | -122.3145 | -0.018311 | 0.16937 | -0.045776 | 123.175 | 0.26093 | 0.091553 | -0.036621 | 0.14191 | -0.12817 | -0.13733 | -0.41657 | -0.050354 | 0.07782 | -0.082397 | 123.143 | 123.1522 | 122.1039 | -123.0194 | 123.0515 | 123.1064 | 122.2778 | -123.317
597.9688 | 123.3353 | -122.2321 | 0.86975 | -0.00091566 | 0.11004 | 0.065322 | 0.0043985 | 0.13369 | 0.0035547 | -0.0037597 | 0.0067901 | -0.0019996 | 0.066849 | 0.072974 | 0.00083507 | -0.0084658 | 0.81482 | 0.79193 | -0.12817 | -122.0627 | 0.89264 | -122.3373 | -122.1634 | -122.7402 | 0.045776 | -122.4152 | 0.82398 | 0.84686 | -122.1954 | -122.4335 | -0.10528 | 0.068665 | 0.022888 | 123.024 | 0.16937 | 0.10071 | -0.054932 | 0.036621 | -0.20142 | -0.045776 | -0.50812 | -0.1831 | 0.018311 | -0.022888 | 123.1247 | 123.0469 | 122.1039 | -123.0331 | 123.056 | 123.0789 | 122.2778 | -123.3032
599.6562 | 123.2666 | -122.2778 | 0.86975 | -0.0085447 | 0.1094 | 0.065535 | 0.0026895 | 0.13732 | 0.0020593 | -0.0026917 | -0.00083936 | -0.0007178 | 0.064286 | 0.070196 | 0.00062147 | -0.0080386 | 0.76904 | 0.737 | -0.22888 | -122.0993 | 0.87891 | -122.374 | -122.168 | -122.7859 | -0.041199 | -122.4976 | 0.7782 | 0.83771 | -122.1954 | -122.4564 | -0.09613 | 0.10986 | 0.009155 | 123.0148 | 0.17853 | 0.068665 | -0.10071 | 0.082397 | -0.17853 | -0.091553 | -0.50812 | -0.21973 | -0.041199 | -0.032043 | 123.1567 | 123.0469 | 122.049 | -123.0377 | 123.056 | 123.1155 | 122.2366 | -123.3261
601.4219 | 123.3124 | -122.0215 | 1.0849 | -0.0085447 | 0.10491 | 0.066603 | 0.0037577 | 0.13454 | -7.6908e-05 | -0.0031189 | 0.01442 | -0.001145 | 0.065567 | 0.069342 | -0.0023693 | -0.0065432 | 1.0162 | 0.97504 | -0.19226 | -121.8292 | 1.1581 | -122.1176 | -121.9482 | -122.5388 | 0.018311 | -122.1771 | 1.0437 | 1.1032 | -121.9482 | -122.1725 | -0.096131 | 0.073242 | 0.073242 | 122.9965 | 0.19226 | 0.11902 | -0.068665 | 0.073242 | -0.15106 | -0.041199 | -0.51727 | -0.15564 | -0.004578 | 0.01831 | 123.1796 | 123.0377 | 121.8292 | -123.0331 | 123.0652 | 123.1247 | 122.0398 | -123.2574
603.125 | 123.3307 | -122.1085 | 1.0025 | -0.00091566 | 0.10726 | 0.066176 | 0.0041849 | 0.13582 | -0.00071771 | -0.00034172 | 0.0067901 | -0.0024268 | 0.068131 | 0.072546 | -0.0027965 | -0.0063296 | 0.89722 | 0.83771 | -0.3067 | -121.9711 | 1.0162 | -122.2 | -122.0215 | -122.6578 | -0.064087 | -122.3236 | 0.93384 | 0.98419 | -122.081 | -122.287 | -0.091553 | 0.086975 | 0.013733 | 122.9462 | 0.13733 | 0.050354 | -0.10528 | 0.027465 | -0.17853 | -0.068664 | -0.54932 | -0.21515 | -0.036621 | -0.01831 | 123.1247 | 123.0057 | 121.8018 | -123.024 | 123.0423 | 123.0927 | 122.0444 | -123.2895
604.875 | 123.3124 | -122.3053 | 0.84686 | 0.0067138 | 0.11046 | 0.066176 | 0.0056803 | 0.13369 | 0.0037683 | -0.00076912 | -0.00083936 | -0.0017858 | 0.067063 | 0.071692 | -0.0010875 | -0.0065432 | 0.70953 | 0.65918 | -0.31586 | -122.1359 | 0.8606 | -122.3877 | -122.2046 | -122.8409 | -0.09613 | -122.5113 | 0.77362 | 0.81024 | -122.2366 | -122.4747 | -0.082397 | 0.10071 | 0.013733 | 122.9645 | 0.16937 | 0.068665 | -0.13733 | 0.068665 | -0.16937 | -0.073242 | -0.53558 | -0.20599 | -0.036622 | -0.036621 | 123.1659 | 123.0148 | 121.9894 | -123.0515 | 123.0789 | 123.1155 | 122.2092 | -123.3215
606.5625 | 123.2254 | -122.2321 | 0.91553 | -0.0085447 | 0.10662 | 0.06938 | 0.0065347 | 0.13518 | -0.0037085 | -0.0044007 | -0.0084684 | -0.0071264 | 0.065995 | 0.069769 | -0.0062145 | -0.0059024 | 0.86517 | 0.88806 | -0.14191 | -122.0032 | 0.8606 | -122.2961 | -122.1085 | -122.6852 | 0.068665 | -122.2733 | 0.77362 | 0.82398 | -122.1222 | -122.3923 | -0.064087 | 0.1236 | -0.054931 | 123.1201 | 0.22888 | 0.10528 | -0.050354 | 0.10986 | -0.16022 | -0.14191 | -0.45319 | -0.041198 | 0.11902 | -0.091552 | 123.0927 | 123.0972 | 122.0901 | -123.024 | 123.0057 | 123.056 | 122.3007 | -123.3078
608.3125 | 123.1888 | -122.2412 | 0.9613 | -0.00091566 | 0.10427 | 0.068312 | 0.00076686 | 0.13668 | -0.0043493 | -0.0046143 | -0.00083936 | -0.0054174 | 0.063431 | 0.070837 | -0.0047191 | -0.0054752 | 0.85602 | 0.84228 | -0.26093 | -122.0078 | 0.91095 | -122.2549 | -122.0856 | -122.7081 | -0.036621 | -122.3099 | 0.82855 | 0.87433 | -122.0993 | -122.3328 | -0.013733 | 0.15564 | -0.050354 | 123.0835 | 0.23346 | 0.07782 | -0.10529 | 0.14191 | -0.091553 | -0.13275 | -0.46692 | -0.068664 | 0.022889 | -0.086975 | 123.1522 | 123.0972 | 121.9803 | -123.0469 | 123.0698 | 123.1155 | 122.2046 | -123.2941
610.0625 | 123.2483 | -122.1909 | 0.95215 | -0.0085447 | 0.10961 | 0.066603 | 0.0039713 | 0.1339 | 0.0018457 | -0.0020507 | -0.0084684 | -7.6996e-05 | 0.065781 | 0.07041 | 0.00040787 | -0.0069706 | 0.83771 | 0.76446 | -0.22888 | -122.049 | 0.88806 | -122.3099 | -122.1085 | -122.731 | -0.032043 | -122.4152 | 0.8606 | 0.90179 | -122.1313 | -122.3694 | -0.11902 | 0.082398 | -0.064086 | 122.9553 | 0.14191 | 0.059509 | -0.11444 | 0.059509 | -0.17853 | -0.091552 | -0.54016 | -0.2243 | -0.045776 | -0.050354 | 123.0789 | 123.0286 | 121.962 | -123.0606 | 123.0515 | 123.0927 | 122.1588 | -123.3215
611.8125 | 123.1888 | -122.1359 | 1.0437 | -0.00091566 | 0.10726 | 0.067244 | 0.0037577 | 0.13561 | -0.0030677 | -0.0037597 | -0.0084684 | -0.0054174 | 0.061936 | 0.070837 | -0.0042919 | -0.0067568 | 1.0254 | 1.0071 | -0.27008 | -121.8796 | 1.0117 | -122.1222 | -121.962 | -122.5754 | -0.059509 | -122.2183 | 0.91095 | 0.95215 | -122.0169 | -122.2595 | 0.013733 | 0.17395 | -0.032043 | 123.143 | 0.25635 | 0.082397 | -0.01831 | 0.11902 | -0.1236 | -0.13275 | -0.43945 | -0.082398 | 0.041198 | -0.091553 | 123.1476 | 123.1613 | 121.8658 | -123.0057 | 123.0469 | 123.0881 | 122.0764 | -123.3032
613.5 | 123.2849 | -122.1817 | 0.92926 | 0.0067138 | 0.11175 | 0.066603 | 0.0061075 | 0.13604 | 0.0044091 | -0.0014099 | -0.0084684 | -0.0015722 | 0.065567 | 0.073187 | -1.9327e-05 | -0.0082522 | 0.87891 | 0.83313 | -0.16937 | -121.9894 | 0.92926 | -122.2687 | -122.0993 | -122.6624 | 0.041199 | -122.3328 | 0.85602 | 0.90179 | -122.1176 | -122.3557 | -0.086975 | 0.082398 | 0 | 123.0148 | 0.19226 | 0.10986 | -0.050354 | 0.064087 | -0.17395 | -0.073242 | -0.48065 | -0.15106 | 0.022888 | -0.027466 | 123.111 | 123.0606 | 122.0123 | -123.0286 | 123.0377 | 123.0835 | 122.2229 | -123.2849
615.25 | 123.2162 | -121.8567 | 1.2863 | -0.0085447 | 0.10961 | 0.067885 | 0.0076029 | 0.13411 | -0.0079809 | -0.0033325 | 0.0067901 | -0.0084082 | 0.064499 | 0.071478 | -0.0068553 | -0.0065432 | 1.3092 | 1.3138 | -0.15106 | -121.582 | 1.2589 | -121.8796 | -121.6873 | -122.287 | 0.091553 | -121.8704 | 1.1719 | 1.2085 | -121.7651 | -121.9894 | -0.022889 | 0.16937 | -0.027466 | 123.1705 | 0.27466 | 0.10529 | 0.022888 | 0.091552 | -0.13275 | -0.11444 | -0.4303 | -0.013733 | 0.11902 | -0.07782 | 123.1155 | 123.1659 | 121.7056 | -122.9736 | 123.0286 | 123.0652 | 121.9482 | -123.2758
617.0156 | 123.3307 | -121.8521 | 1.2726 | 0.0067138 | 0.10769 | 0.067885 | 0.0018351 | 0.13711 | 0.0027003 | -0.0022643 | -0.00083936 | -0.0022132 | 0.061722 | 0.07276 | 0.00040787 | -0.0086796 | 1.1765 | 1.1307 | -0.28839 | -121.6736 | 1.2863 | -121.9116 | -121.7148 | -122.2916 | 0.004578 | -121.9757 | 1.2177 | 1.2177 | -121.7468 | -121.9849 | -0.059509 | 0.13733 | 0.013733 | 122.9828 | 0.17853 | 0.041199 | -0.09613 | 0.10529 | -0.13275 | -0.054932 | -0.43945 | -0.1236 | 0.009155 | -0.054932 | 123.1384 | 123.0286 | 121.5637 | -122.9874 | 123.0698 | 123.0698 | 121.8567 | -123.2574
618.6875 | 123.2895 | -121.8842 | 1.2177 | -0.00091566 | 0.10769 | 0.066603 | 0.0020487 | 0.13689 | 0.00013669 | -0.0014099 | -0.00083936 | -0.0015722 | 0.063004 | 0.069556 | -0.0013011 | -0.009534 | 1.1536 | 1.1169 | -0.26093 | -121.6919 | 1.1581 | -121.9711 | -121.7789 | -122.3419 | 0.064087 | -121.9849 | 1.0941 | 1.149 | -121.7834 | -122.0169 | -0.086975 | 0.10529 | -0.059509 | 123.0011 | 0.19226 | 0.086975 | -0.064087 | 0.10071 | -0.13275 | -0.1236 | -0.45776 | -0.10071 | 0.032044 | -0.068664 | 123.0423 | 123.0377 | 121.6232 | -122.9965 | 122.9782 | 123.0331 | 121.9482 | -123.2346
620.4375 | 123.1613 | -121.0281 | 2.1423 | -0.0085447 | 0.10384 | 0.067885 | 0.0043985 | 0.13454 | -0.0037085 | -0.0046143 | -0.0084684 | -0.0054174 | 0.063431 | 0.068701 | -0.0034373 | -0.0071842 | 1.9363 | 1.9089 | -0.3479 | -120.9503 | 1.9409 | -121.2479 | -121.0739 | -121.8109 | -0.17853 | -121.4584 | 1.7029 | 1.7395 | -121.2433 | -121.4905 | -0.21973 | -0.045777 | -0.20142 | 122.937 | 0.07782 | 0.1236 | -0.20599 | -0.21515 | -0.46234 | -0.43945 | -0.78278 | -0.4303 | 0.032044 | -0.40283 | 122.9691 | 122.9645 | 120.6802 | -123.2162 | 122.731 | 122.7676 | 120.8496 | -123.6328
622.1875 | 123.1796 | -120.5154 | 2.417 | -0.0085447 | 0.1032 | 0.068526 | 0.0054667 | 0.13753 | -0.00071771 | -0.0048279 | -0.00083936 | -0.0071264 | 0.063858 | 0.071265 | -0.0045055 | -0.0069706 | 0.83313 | 0.82398 | -0.25635 | -122.0032 | 0.88348 | -122.2641 | -122.0718 | -122.644 | 0.07782 | -122.1817 | 0.84686 | 0.88348 | -122.0261 | -122.2687 | -1.7487 | -1.5564 | -1.5335 | 121.3394 | -1.4877 | 0.068664 | -1.5839 | -1.5106 | -1.7532 | -1.5701 | -2.1286 | -1.6663 | 0.086975 | -1.5335 | 121.3989 | 121.3486 | 120.2591 | -124.4888 | 121.3623 | 121.3989 | 120.5933 | -124.6857
623.875 | 123.2391 | -122.287 | 0.85144 | -0.0085447 | 0.11132 | 0.063826 | 0.0056803 | 0.13668 | 0.0061181 | -0.0018371 | 0.0067901 | -0.0017858 | 0.06514 | 0.073187 | -0.00066033 | -0.0088932 | 0.75073 | 0.69122 | -0.26093 | -122.0856 | 0.82855 | -122.3511 | -122.168 | -122.8134 | -0.082397 | -122.525 | 0.74616 | 0.77362 | -122.2366 | -122.4701 | -0.064087 | 0.11902 | -0.022888 | 122.9782 | 0.20142 | 0.082398 | -0.10071 | 0.050354 | -0.18311 | -0.10528 | -0.52643 | -0.23804 | -0.054931 | -0.077819 | 123.1155 | 123.0377 | 122.0261 | -123.0194 | 123.0331 | 123.0606 | 122.2046 | -123.3215
625.6094 | 123.1567 | -121.5225 | 1.8036 | -0.0085447 | 0.10726 | 0.067671 | 0.0080301 | 0.1354 | -0.0041357 | -0.0039733 | -0.00083936 | -0.0054174 | 0.064713 | 0.072119 | -0.0042919 | -0.0091068 | 1.442 | 1.4877 | -0.073242 | -121.3715 | 1.4236 | -121.6873 | -121.5088 | -122.0398 | 0.12817 | -121.7148 | 1.3687 | 1.4053 | -121.5637 | -121.8063 | -0.16479 | 0.013733 | -0.37994 | 123.0103 | 0.15106 | 0.13733 | -0.36163 | -0.041199 | -0.28381 | -0.43488 | -0.51727 | -0.19226 | 0.091552 | -0.39826 | 122.9462 | 122.9645 | 121.4493 | -123.3124 | 122.8912 | 122.9279 | 121.6507 | -123.6099
627.3594 | 123.1659 | -121.5179 | 1.6296 | 0.0067138 | 0.10555 | 0.065108 | 0.0033305 | 0.13988 | -7.6908e-05 | -0.0011963 | -0.00083936 | -0.0054174 | 0.063218 | 0.070196 | -0.0023693 | -0.0069706 | 1.5427 | 1.5518 | -0.23804 | -121.3028 | 1.5335 | -121.6049 | -121.3943 | -121.9849 | 0.009155 | -121.6095 | 1.4557 | 1.4877 | -121.4493 | -121.6965 | -0.086975 | 0.1236 | -0.096131 | 123.0698 | 0.21515 | 0.091553 | -0.086975 | 0.068664 | -0.17853 | -0.17395 | -0.46692 | -0.091553 | 0.086975 | -0.14191 | 123.0515 | 123.0606 | 121.2799 | -123.024 | 122.9736 | 123.0057 | 121.5271 | -123.3261
629.1094 | 123.2574 | -122.2366 | 0.85602 | -0.00091566 | 0.10982 | 0.065322 | 0.0035441 | 0.13903 | 0.0046229 | -0.0033325 | -0.00083936 | -0.0024268 | 0.063004 | 0.071478 | 0.0014759 | -0.0071842 | 0.82398 | 0.76446 | -0.18768 | -122.0581 | 0.83771 | -122.3419 | -122.1313 | -122.7173 | 0.036621 | -122.4014 | 0.76446 | 0.79193 | -122.1725 | -122.4014 | -0.10529 | 0.10528 | -0.01831 | 123.0011 | 0.17853 | 0.073243 | -0.032043 | 0.064087 | -0.16479 | -0.091553 | -0.48065 | -0.16479 | 0 | -0.064087 | 123.0743 | 123.0606 | 122.0489 | -122.9874 | 123.0011 | 123.0286 | 122.2733 | -123.2574
630.8594 | 123.2025 | -122.3236 | 0.81024 | -0.0085447 | 0.10534 | 0.06938 | 0.0056803 | 0.13903 | -0.0060583 | -0.0046143 | 0.0067901 | -0.0069128 | 0.061722 | 0.069556 | -0.0042919 | -0.0067568 | 0.75989 | 0.7782 | -0.19684 | -122.0627 | 0.75989 | -122.3511 | -122.1497 | -122.7585 | 0.064087 | -122.3511 | 0.67749 | 0.72327 | -122.2183 | -122.438 | -0.027466 | 0.17395 | -0.050354 | 123.1018 | 0.26092 | 0.086975 | -0.050354 | 0.10528 | -0.11444 | -0.13275 | -0.43488 | -0.027466 | 0.086975 | -0.086975 | 123.0835 | 123.0835 | 122.1268 | -122.9599 | 123.0011 | 123.0469 | 122.3877 | -123.2483
632.5625 | 123.2758 | -121.9894 | 1.0529 | -0.00091566 | 0.10811 | 0.064253 | 0.0046121 | 0.13625 | 0.0031275 | -0.0018371 | -0.0084684 | -0.0005042 | 0.062363 | 0.071265 | -1.9327e-05 | -0.0082522 | 1.0529 | 0.99792 | -0.20599 | -121.7926 | 1.1032 | -122.0673 | -121.8796 | -122.4838 | 0.027466 | -122.168 | 1.0162 | 1.0529 | -121.9482 | -122.1771 | -0.07782 | 0.10986 | 0.050354 | 122.9874 | 0.19684 | 0.086975 | 0 | 0.041199 | -0.18768 | -0.036621 | -0.49438 | -0.17853 | 0.009155 | 0 | 123.0927 | 123.0423 | 121.7834 | -122.9324 | 123.0057 | 123.0423 | 122.0169 | -123.23
634.3125 | 123.1934 | -121.0693 | 2.0737 | -0.0085447 | 0.10512 | 0.066817 | 0.0093119 | 0.1339 | -0.0064855 | -0.0026917 | -0.00083936 | -0.0069128 | 0.064286 | 0.070624 | -0.0062145 | -0.007825 | 2.005 | 1.9958 | -0.24719 | -120.7809 | 2.0187 | -121.0876 | -120.9183 | -121.5179 | 0.009155 | -121.1243 | 1.9135 | 1.9684 | -120.9641 | -121.1838 | -0.01831 | 0.15106 | -0.054931 | 123.0652 | 0.28839 | 0.13733 | -0.068664 | 0.10529 | -0.11444 | -0.16022 | -0.44861 | -0.054932 | 0.059509 | -0.10529 | 123.0881 | 123.0743 | 120.8221 | -122.9919 | 122.9828 | 123.0377 | 121.0785 | -123.2574
636.0625 | 123.1522 | -121.9711 | 1.2131 | -0.0085447 | 0.1032 | 0.067671 | 0.0039713 | 0.13283 | -0.0032813 | -0.0052551 | 0.0067901 | -0.0049902 | 0.063431 | 0.071905 | -0.0010875 | -0.0069706 | 1.1078 | 1.1032 | -0.29297 | -121.7285 | 1.1536 | -121.9803 | -121.7834 | -122.4289 | -0.050354 | -122.0398 | 1.0712 | 1.1078 | -121.8521 | -122.0673 | -0.009156 | 0.18768 | -0.05951 | 123.0743 | 0.24261 | 0.054931 | -0.10529 | 0.11902 | -0.096131 | -0.14191 | -0.45776 | -0.068665 | 0.027466 | -0.10529 | 123.1247 | 123.0789 | 121.6782 | -122.9965 | 123.0423 | 123.0789 | 121.9208 | -123.2803
637.8125 | 123.1934 | -121.9162 | 1.2177 | -0.00091566 | 0.10149 | 0.067885 | 0.0050393 | 0.13604 | -0.0015723 | -0.0050415 | 0.0067901 | -0.006272 | 0.063431 | 0.069983 | -0.0015147 | -0.0065432 | 1.1444 | 1.1169 | -0.29297 | -121.6736 | 1.1627 | -121.9757 | -121.7697 | -122.3694 | 0.018311 | -121.9894 | 1.0803 | 1.1261 | -121.8292 | -122.0627 | -0.059509 | 0.14649 | -0.054931 | 123.0331 | 0.24262 | 0.09613 | -0.073242 | 0.086975 | -0.14648 | -0.13733 | -0.45319 | -0.073242 | 0.073242 | -0.091552 | 123.0789 | 123.0606 | 121.6232 | -122.9874 | 122.9965 | 123.0423 | 121.9345 | -123.2803
639.5 | 123.1384 | -122.1085 | 1.0391 | -0.0085447 | 0.10662 | 0.066176 | 0.0056803 | 0.13817 | -0.0019995 | -0.00098272 | -0.0084684 | -0.0047766 | 0.065354 | 0.073614 | -0.0038647 | -0.010388 | 1.0071 | 0.97961 | -0.25635 | -121.8475 | 0.95673 | -122.1176 | -121.9528 | -122.5296 | 0 | -122.1771 | 0.88348 | 0.94757 | -122.0032 | -122.2321 | -0.009156 | 0.15564 | -0.082398 | 123.0881 | 0.26093 | 0.10529 | -0.032044 | 0.10528 | -0.1236 | -0.15564 | -0.42114 | -0.068665 | 0.054932 | -0.091553 | 123.0652 | 123.1155 | 121.8521 | -122.9919 | 122.9919 | 123.056 | 122.1085 | -123.2712
641.25 | 123.2483 | -120.9595 | 2.1286 | -0.00091566 | 0.11111 | 0.066603 | 0.0041849 | 0.13625 | 0.0035547 | -0.0050415 | -0.016098 | 0.0007776 | 0.065354 | 0.071692 | -0.0036509 | -0.009534 | 2.0554 | 1.973 | -0.22888 | -120.7901 | 2.1515 | -121.0281 | -120.8633 | -121.4722 | 0 | -121.1334 | 2.0691 | 2.1103 | -120.8862 | -121.1243 | -0.068664 | 0.096131 | 0.022888 | 122.9324 | 0.16937 | 0.073242 | -0.073242 | 0.073243 | -0.16479 | -0.059509 | -0.51269 | -0.17395 | -0.009155 | -0.01831 | 123.111 | 123.0148 | 120.7306 | -122.9919 | 123.0286 | 123.0698 | 120.9595 | -123.2529
643 | 123.1247 | -120.845 | 2.3117 | -0.00091566 | 0.10726 | 0.06938 | 0.0058939 | 0.13881 | -0.00029051 | -0.0018371 | -0.0084684 | -0.0032812 | 0.064499 | 0.070624 | -0.0051463 | -0.0073978 | 2.2202 | 2.1973 | -0.19226 | -120.6024 | 2.243 | -120.9 | -120.6894 | -121.3211 | -0.004578 | -120.9915 | 2.1606 | 2.2247 | -120.7718 | -120.9824 | -0.054931 | 0.15564 | -0.068665 | 123.0423 | 0.24262 | 0.086975 | -0.091553 | 0.073242 | -0.13733 | -0.15106 | -0.47607 | -0.14648 | -0.009155 | -0.086976 | 123.0881 | 123.0652 | 120.6528 | -123.0011 | 123.0057 | 123.0698 | 120.8405 | -123.2941
644.6719 | 123.2117 | -122.1497 | 0.96588 | -0.0085447 | 0.10961 | 0.066817 | 0.0039713 | 0.13582 | 0.0039819 | -0.0018371 | -0.00083936 | -0.001145 | 0.06514 | 0.072119 | 0.00019427 | -0.0086796 | 0.86975 | 0.7782 | -0.27924 | -121.9894 | 0.93384 | -122.2183 | -122.0581 | -122.6715 | -0.045776 | -122.3648 | 0.86975 | 0.91095 | -122.081 | -122.3053 | -0.068665 | 0.091553 | -0.032043 | 122.9279 | 0.16022 | 0.068664 | -0.09613 | 0.068664 | -0.15564 | -0.09613 | -0.52185 | -0.21515 | -0.059509 | -0.054931 | 123.0835 | 123.0194 | 121.8704 | -123.024 | 123.0194 | 123.0606 | 122.1039 | -123.2712
646.4219 | 123.1293 | -122.1359 | 1.0208 | -0.016174 | 0.10769 | 0.067244 | 0.0056803 | 0.13561 | -0.0039221 | -0.0026917 | -0.0084684 | -0.0058448 | 0.065567 | 0.070196 | -0.0036509 | -0.0059024 | 0.92468 | 0.91553 | -0.31128 | -121.9025 | 0.96588 | -122.1588 | -121.9757 | -122.6028 | -0.045776 | -122.2046 | 0.88348 | 0.91553 | -122.0261 | -122.2092 | -0.022888 | 0.16022 | -0.054932 | 123.0515 | 0.23346 | 0.073242 | -0.09613 | 0.10986 | -0.073242 | -0.13733 | -0.46692 | -0.068665 | 0.004577 | -0.10529 | 123.1018 | 123.0606 | 121.8246 | -122.9965 | 123.0194 | 123.0515 | 122.0901 | -123.23
648.1875 | 123.2483 | -121.6324 | 1.4282 | -0.00091566 | 0.10576 | 0.064253 | 0.00012606 | 0.13433 | 0.00013669 | -0.0018371 | 0.0067901 | -0.0034948 | 0.066422 | 0.070624 | -0.0010875 | -0.0097476 | 1.4969 | 1.4557 | -0.23804 | -121.3577 | 1.4511 | -121.6187 | -121.4584 | -122.049 | 0.009155 | -121.701 | 1.3321 | 1.3733 | -121.5408 | -121.7468 | 0.013733 | 0.17395 | 0.022888 | 123.0881 | 0.27466 | 0.10071 | 0.068664 | 0.091552 | -0.11444 | -0.096131 | -0.41657 | -0.068665 | 0.045776 | -0.054932 | 123.0835 | 123.1293 | 121.3943 | -122.8867 | 122.9645 | 123.0057 | 121.6415 | -123.175
649.9375 | 123.1796 | -121.6278 | 1.4694 | -0.016174 | 0.10576 | 0.068312 | 0.0078165 | 0.13561 | -0.0039221 | -0.0035461 | -0.016098 | -0.0060584 | 0.064072 | 0.071692 | -0.0055735 | -0.0065432 | 1.4099 | 1.4328 | -0.23346 | -121.3898 | 1.4328 | -121.6553 | -121.4859 | -122.0444 | 0.073242 | -121.6599 | 1.355 | 1.4053 | -121.5225 | -121.7606 | -0.027465 | 0.14191 | -0.036621 | 123.0606 | 0.23804 | 0.09613 | -0.059509 | 0.10529 | -0.13275 | -0.11444 | -0.41656 | -0.032043 | 0.10071 | -0.064087 | 123.0606 | 123.0377 | 121.3943 | -122.9553 | 122.9828 | 123.0331 | 121.701 | -123.23
651.6094 | 123.175 | -121.6461 | 1.4694 | -0.0085447 | 0.10555 | 0.068099 | 0.0086709 | 0.13604 | -0.0028539 | -0.0039733 | -0.00083936 | -0.0058448 | 0.065995 | 0.069769 | -0.0036509 | -0.007825 | 1.3779 | 1.3916 | -0.26093 | -121.4218 | 1.3733 | -121.6965 | -121.5088 | -122.0764 | 0.041199 | -121.701 | 1.3504 | 1.3641 | -121.5408 | -121.7834 | -0.050354 | 0.13733 | -0.09613 | 123.0377 | 0.2243 | 0.086975 | -0.091552 | 0.10528 | -0.13733 | -0.11902 | -0.4303 | -0.054932 | 0.082397 | -0.10529 | 123.0194 | 123.024 | 121.3852 | -122.9782 | 122.9965 | 123.0103 | 121.6873 | -123.2529
653.375 | 123.2025 | -121.6965 | 1.3641 | -0.00091566 | 0.11132 | 0.067885 | 0.0058939 | 0.13582 | 0.0018457 | -0.0033325 | -0.00083936 | -0.0007178 | 0.065567 | 0.069769 | -0.0015147 | -0.0084658 | 1.2497 | 1.2039 | -0.41657 | -121.5591 | 1.3458 | -121.8155 | -121.6232 | -122.2321 | -0.17395 | -121.9025 | 1.2863 | 1.3138 | -121.6644 | -121.875 | -0.11902 | 0.073242 | -0.018311 | 122.9004 | 0.13733 | 0.064087 | -0.11444 | 0.032043 | -0.17853 | -0.07782 | -0.53558 | -0.20599 | -0.027466 | -0.050354 | 123.0423 | 122.9462 | 121.2799 | -122.9874 | 122.9828 | 123.0103 | 121.5225 | -123.2391
655.0625 | 123.0972 | -122.5479 | 0.52643 | 0.0067138 | 0.013907 | 0.0020893 | 0.0056803 | 0.053579 | -0.0049903 | -0.0044007 | -0.00083936 | -0.0066992 | 0.097824 | 0.068274 | -0.0047191 | -0.0097476 | 0.13733 | 0.14648 | 0.11902 | 0.16479 | 0.13733 | 0.064087 | -0.054932 | -122.9279 | 0.07782 | -122.5388 | 0.40741 | 0.43488 | -122.4152 | -122.6578 | 122.612 | 122.493 | -0.3891 | 122.6944 | 122.7127 | 0.21973 | -0.3891 | 0.13275 | -0.10986 | -0.11902 | -0.37994 | 0.009156 | 0.11902 | -0.091553 | 122.6852 | 122.6852 | 122.6669 | -0.58136 | 122.9553 | 122.9828 | 122.6257 | -123.1842
656.8125 | 123.1979 | -122.5204 | 0.56305 | -0.0085447 | 0.015402 | 0.0016619 | 0.0014079 | 0.052297 | -7.6908e-05 | -0.0029053 | -0.00083936 | -0.004563 | 0.095475 | 0.068915 | -0.00044673 | -0.0088932 | 0.13733 | 0.10986 | 0.036621 | 0.16937 | 0.12817 | 0.068665 | -0.041199 | -122.9141 | 0.013733 | -122.5845 | 0.41657 | 0.46692 | -122.4426 | -122.6349 | 122.5891 | 122.4792 | -0.43488 | 122.6303 | 122.6898 | 0.21057 | -0.42572 | 0.07782 | -0.11444 | -0.14648 | -0.39368 | -0.064087 | 0.050354 | -0.09613 | 122.6486 | 122.6578 | 122.5571 | -0.60425 | 122.937 | 122.9874 | 122.5342 | -123.1979
658.5 | 123.1338 | -122.5616 | 0.54016 | -0.00091566 | 0.01113 | -0.00090151 | 0.0016215 | 0.052511 | -0.0017859 | -0.0044007 | -0.00083936 | -0.0075538 | 0.094834 | 0.069128 | -0.0019419 | -0.0088932 | 0.11902 | 0.15106 | 0.032043 | 0.15106 | 0.1236 | 0.054932 | -0.045776 | -122.9599 | 0.018311 | -122.5937 | 0.3891 | 0.45319 | -122.4655 | -122.6852 | 122.6166 | 122.5159 | -0.41657 | 122.7127 | 122.7127 | 0.19684 | -0.42114 | 0.096131 | -0.1236 | -0.15106 | -0.39825 | -0.032043 | 0.091553 | -0.086975 | 122.6852 | 122.6807 | 122.5937 | -0.58594 | 122.9507 | 123.0148 | 122.58 | -123.2254
660.25 | 123.0835 | -122.5662 | 0.54016 | -0.0085447 | 0.014121 | -4.6912e-05 | 0.0071757 | 0.052511 | -0.0028539 | -0.0037597 | -0.0084684 | -0.00734 | 0.096329 | 0.065924 | -0.0045055 | -0.0076114 | 0.11902 | 0.13275 | 0.16937 | 0.16937 | 0.1236 | 0.064087 | -0.059509 | -123.0148 | 0.07782 | -122.644 | 0.40283 | 0.43488 | -122.5067 | -122.7127 | 122.6303 | 122.5067 | -0.41657 | 122.699 | 122.7356 | 0.22888 | -0.42114 | 0.059509 | -0.14649 | -0.13733 | -0.44861 | -0.07782 | 0.068665 | -0.10529 | 122.6898 | 122.6852 | 122.7356 | -0.59967 | 122.9691 | 123.0011 | 122.644 | -123.2529
662 | 123.0927 | -122.5891 | 0.53101 | -0.016174 | 0.011343 | 0.00016669 | 0.0067483 | 0.055074 | -0.0030677 | -0.0035461 | -0.00083936 | -0.0056312 | 0.09462 | 0.070196 | -0.0017283 | -0.0082522 | 0.11444 | 0.12817 | 0.15564 | 0.17853 | 0.13733 | 0.045776 | -0.07782 | -123.024 | 0.073242 | -122.6486 | 0.41199 | 0.45319 | -122.4976 | -122.7264 | 122.6349 | 122.5113 | -0.39368 | 122.7173 | 122.7676 | 0.25635 | -0.41656 | 0.091552 | -0.13733 | -0.11902 | -0.43488 | -0.05951 | 0.077819 | -0.07782 | 122.7264 | 122.7036 | 122.7448 | -0.60883 | 123.0011 | 123.0423 | 122.6624 | -123.2574
663.6875 | 123.2712 | -122.5525 | 0.48065 | 0.0067138 | 0.011557 | -0.00090151 | 0.0031167 | 0.053579 | 0.00077749 | -0.0035461 | 0.0067901 | -0.0024268 | 0.095047 | 0.068487 | 0.0021169 | -0.0067568 | 0.050354 | -0.004578 | -0.036621 | 0.091553 | 0.17395 | 0.036621 | -0.073242 | -123.0652 | -0.036621 | -122.731 | 0.42114 | 0.43488 | -122.4976 | -122.731 | 122.5891 | 122.4792 | -0.3067 | 122.5479 | 122.644 | 0.16479 | -0.4303 | 0.054931 | -0.17853 | -0.059509 | -0.5127 | -0.17853 | 0 | -0.045777 | 122.7264 | 122.6028 | 122.5159 | -0.55389 | 122.9736 | 122.9874 | 122.5159 | -123.2117
665.4219 | 123.1888 | -122.5525 | 0.52643 | -0.0085447 | 0.016898 | -0.0013287 | 0.0022623 | 0.053365 | 0.0022729 | -0.0037597 | -0.0084684 | -0.0007178 | 0.096756 | 0.069342 | -1.9327e-05 | -0.0069706 | 0.009155 | -0.032043 | -0.004578 | 0.07782 | 0.17853 | 0.013733 | -0.10986 | -123.0927 | -0.064087 | -122.7859 | 0.43488 | 0.48981 | -122.5113 | -122.731 | 122.5662 | 122.4426 | -0.3479 | 122.5204 | 122.6303 | 0.18768 | -0.51727 | 0.041198 | -0.17853 | -0.091553 | -0.54016 | -0.23346 | -0.054932 | -0.036621 | 122.731 | 122.5616 | 122.5479 | -0.63629 | 122.9874 | 123.0423 | 122.4884 | -123.2574
667.1875 | 123.2574 | -122.5296 | 0.52185 | -0.0085447 | 0.010275 | -0.0019695 | 0.0063211 | 0.052083 | -7.6908e-05 | -0.0024779 | -0.00083936 | -0.0019996 | 0.098893 | 0.071265 | -0.0019419 | -0.0071842 | 0.018311 | -0.013733 | -0.045776 | 0.068665 | 0.1831 | 0.022888 | -0.1236 | -123.0698 | -0.07782 | -122.7402 | 0.46234 | 0.47607 | -122.5296 | -122.7768 | 122.5525 | 122.406 | -0.33875 | 122.5159 | 122.5983 | 0.19226 | -0.50354 | 0 | -0.24719 | -0.05951 | -0.54016 | -0.21057 | 0.036621 | -0.045777 | 122.7127 | 122.5479 | 122.4838 | -0.64545 | 122.9919 | 123.0057 | 122.4518 | -123.2986
668.9219 | 123.1338 | -122.5708 | 0.5722 | 0.0067138 | 0.00878 | 0.0012347 | 0.0061075 | 0.054647 | -0.0060583 | -0.0026917 | -0.016098 | -0.0075538 | 0.095047 | 0.071051 | -0.0038647 | -0.0065432 | 0.091553 | 0.13275 | 0.027466 | 0.14191 | 0.1236 | 0.054932 | -0.041199 | -123.0469 | -0.022888 | -122.6669 | 0.40283 | 0.44861 | -122.525 | -122.7219 | 122.6257 | 122.5296 | -0.44861 | 122.7036 | 122.7127 | 0.18311 | -0.48065 | 0.045777 | -0.15106 | -0.16937 | -0.47607 | -0.09613 | 0.054932 | -0.1236 | 122.6944 | 122.6624 | 122.5983 | -0.6134 | 122.9736 | 123.0194 | 122.5479 | -123.2941
670.5938 | 123.1247 | -122.5983 | 0.54474 | 0.014343 | 0.016043 | 0.0016619 | 0.010166 | 0.05187 | -0.0039221 | -0.0052551 | 0.0067901 | -0.0032812 | 0.097397 | 0.070624 | -0.0034373 | -0.0097476 | 0.086975 | 0.10529 | 0.15106 | 0.15106 | 0.14191 | 0.018311 | -0.07782 | -123.0789 | -0.022888 | -122.7036 | 0.42114 | 0.45319 | -122.5159 | -122.7676 | 122.6166 | 122.5204 | -0.40283 | 122.7036 | 122.7493 | 0.22888 | -0.45776 | 0.082398 | -0.16937 | -0.1236 | -0.48065 | -0.10528 | 0.064087 | -0.091553 | 122.7402 | 122.6852 | 122.7493 | -0.62256 | 123.0194 | 123.0515 | 122.5754 | -123.3124
672.3594 | 123.1567 | -122.4747 | 0.63171 | -0.0085447 | 0.010489 | -0.00047431 | 0.0035441 | 0.052083 | -0.0045629 | -0.0037597 | -0.00083936 | -0.0069128 | 0.097184 | 0.069128 | -0.0042919 | -0.007825 | 0.045776 | 0.07782 | -0.004578 | 0.14191 | 0.15106 | 0.059509 | -0.068665 | -122.9553 | 0 | -122.5388 | 0.49896 | 0.53101 | -122.4106 | -122.6166 | 122.5342 | 122.406 | -0.48065 | 122.5525 | 122.6166 | 0.21057 | -0.58594 | 0.064087 | -0.14191 | -0.13275 | -0.48065 | -0.064087 | 0.07782 | -0.10071 | 122.6257 | 122.5204 | 122.4701 | -0.70038 | 122.9736 | 123.0057 | 122.4747 | -123.2483
674.0469 | 123.2162 | -122.5937 | 0.50812 | -0.0085447 | 0.013907 | -4.6912e-05 | 0.0022623 | 0.051015 | 0.0012049 | -0.0037597 | 0.0067901 | -7.6996e-05 | 0.09697 | 0.072333 | 0.0010487 | -0.0099612 | 0.054932 | 0.022888 | 0.059509 | 0.09613 | 0.16022 | 0.027466 | -0.07782 | -123.0927 | -0.018311 | -122.7814 | 0.4303 | 0.45319 | -122.5342 | -122.7722 | 122.6212 | 122.5159 | -0.3479 | 122.6166 | 122.6898 | 0.17395 | -0.45319 | 0.059509 | -0.17853 | -0.07782 | -0.49896 | -0.18768 | -0.009155 | -0.054932 | 122.7539 | 122.6486 | 122.6532 | -0.58594 | 123.024 | 123.0469 | 122.5754 | -123.2803
675.7812 | 123.1293 | -122.525 | 0.61798 | -0.00091566 | 0.014761 | 0.0012347 | 0.0093119 | 0.052938 | -0.0054175 | -0.0052551 | -0.016098 | -0.0058448 | 0.098893 | 0.069128 | -0.0064281 | -0.0082522 | 0.10529 | 0.14191 | 0.16022 | 0.17395 | 0.1236 | 0.064087 | -0.068665 | -122.9416 | 0.09613 | -122.5891 | 0.47607 | 0.50354 | -122.4335 | -122.6578 | 122.5891 | 122.4564 | -0.49439 | 122.6669 | 122.699 | 0.24261 | -0.5127 | 0.091552 | -0.13275 | -0.14191 | -0.41656 | -0.064087 | 0.068665 | -0.11444 | 122.6486 | 122.6303 | 122.6852 | -0.68665 | 123.0011 | 123.0286 | 122.6212 | -123.2758
677.5469 | 123.2712 | -122.5067 | 0.54016 | -0.0085447 | 0.012625 | -0.00026071 | 0.0024759 | 0.052724 | 0.0024865 | -0.0037597 | -0.0084684 | -0.0017858 | 0.098252 | 0.069556 | -0.00087393 | -0.009534 | 0.036621 | 0.009155 | 0.073242 | 0.09613 | 0.17853 | 0.022888 | -0.11444 | -123.0148 | 0.018311 | -122.6807 | 0.48065 | 0.50812 | -122.4609 | -122.6944 | 122.5296 | 122.3923 | -0.36163 | 122.5159 | 122.6028 | 0.21057 | -0.50354 | 0.045777 | -0.18768 | -0.059509 | -0.50812 | -0.17395 | 0.013733 | -0.032043 | 122.6852 | 122.5433 | 122.58 | -0.6546 | 122.9874 | 123.0148 | 122.525 | -123.2346
679.2969 | 123.2208 | -122.2412 | 0.87891 | -0.00091566 | 0.014548 | -0.0019695 | 0.0018351 | 0.053152 | 0.0012049 | -0.0037597 | -0.016098 | -0.0017858 | 0.099533 | 0.070196 | 0.00019427 | -0.0088932 | 0.013733 | -0.018311 | -0.009155 | 0.086975 | 0.17395 | 0.027466 | -0.10529 | -122.7905 | -0.050354 | -122.4838 | 0.77362 | 0.80566 | -122.2046 | -122.4426 | 122.2687 | 122.1359 | -0.70496 | 122.2229 | 122.3282 | 0.19226 | -0.86517 | 0.036621 | -0.20142 | -0.10528 | -0.54932 | -0.24261 | -0.041199 | -0.073242 | 122.4152 | 122.2549 | 122.2321 | -0.98419 | 123.0148 | 123.0469 | 122.1909 | -123.3215
681.0625 | 123.2529 | -122.2549 | 0.82855 | 0.0067138 | 0.013693 | -0.00047431 | 0.0041849 | 0.054006 | -0.00050411 | -0.0035461 | 0.0067901 | -0.0019996 | 0.097824 | 0.070196 | -0.0027965 | -0.0093204 | 0.013733 | -0.004578 | 0.073242 | 0.10986 | 0.16479 | 0.018311 | -0.10071 | -122.7814 | 0.013733 | -122.4289 | 0.737 | 0.76446 | -122.2229 | -122.4518 | 122.2733 | 122.1542 | -0.66376 | 122.2504 | 122.3648 | 0.21057 | -0.81482 | 0.032044 | -0.19684 | -0.091552 | -0.52643 | -0.17395 | 0.022888 | -0.064087 | 122.4197 | 122.2687 | 122.3282 | -0.92926 | 122.9919 | 123.0194 | 122.2687 | -123.2803
682.8125 | 123.1064 | -122.0764 | 1.03 | -0.0085447 | 0.014334 | 0.0018757 | 0.0061075 | 0.055501 | -0.0060583 | -0.0054687 | -0.00083936 | -0.0039222 | 0.097611 | 0.070196 | -0.0034373 | -0.0076114 | 0.086975 | 0.09613 | 0.14191 | 0.14648 | 0.15106 | 0.050354 | -0.091553 | -122.6395 | -0.032043 | -122.2595 | 0.91095 | 0.94299 | -122.081 | -122.2412 | 122.1268 | 121.9849 | -0.87891 | 122.1725 | 122.2229 | 0.23804 | -0.94299 | -0.004578 | -0.1648 | -0.11902 | -0.56305 | -0.18311 | -0.01831 | -0.086975 | 122.2275 | 122.1634 | 122.2183 | -1.1215 | 122.9874 | 123.0194 | 122.0444 | -123.2712
684.5 | 123.1293 | -120.8679 | 2.243 | 0.0067138 | 0.013693 | 0.0025165 | 0.0052531 | 0.051656 | -0.0047765 | -0.0041869 | -0.00083936 | -0.00734 | 0.096329 | 0.067206 | -0.0023693 | -0.0084658 | 0.10529 | 0.13275 | 0.15106 | 0.16479 | 0.13275 | 0.041199 | -0.068665 | -121.3074 | 0.10071 | -120.9366 | 2.0737 | 2.1149 | -120.7901 | -121.0144 | 120.9091 | 120.7993 | -2.1103 | 121.0007 | 121.0327 | 0.23346 | -2.1378 | 0.07782 | -0.14648 | -0.16937 | -0.43945 | -0.068664 | 0.07782 | -0.12817 | 121.0007 | 120.9732 | 121.019 | -2.3117 | 122.9416 | 122.9828 | 120.9686 | -123.2574
686.2344 | 123.2162 | -122.2321 | 0.86975 | -0.00091566 | 0.01348 | -0.0036785 | 0.0046121 | 0.052511 | 0.00099129 | -0.0020507 | -0.00083936 | -0.0002906 | 0.097397 | 0.072546 | 0.00019427 | -0.007825 | 0.032043 | -0.054932 | -0.004578 | 0.07782 | 0.16937 | 0.041199 | -0.10529 | -122.7814 | -0.068665 | -122.4609 | 0.76446 | 0.81024 | -122.2137 | -122.438 | 122.2733 | 122.1268 | -0.70038 | 122.1771 | 122.3099 | 0.18311 | -0.83771 | 0.018311 | -0.20599 | -0.10529 | -0.54932 | -0.22888 | -0.022888 | -0.059509 | 122.4014 | 122.2641 | 122.2275 | -0.97504 | 122.9965 | 123.0423 | 122.1634 | -123.3078
687.9844 | 123.2254 | -122.2641 | 0.81024 | -0.00091566 | 0.018393 | -0.0011151 | 0.0071757 | 0.052938 | -0.00029051 | -0.0024779 | -0.0084684 | -0.0039222 | 0.098252 | 0.069769 | -0.0010875 | -0.0086796 | 0.091553 | 0.073242 | 0.10986 | 0.1236 | 0.16479 | 0.027466 | -0.064087 | -122.7905 | 0.041199 | -122.4289 | 0.70038 | 0.75531 | -122.2595 | -122.4609 | 122.2916 | 122.2 | -0.64545 | 122.3373 | 122.3877 | 0.18768 | -0.71869 | 0.004578 | -0.19684 | -0.10986 | -0.52643 | -0.16479 | 0.032043 | -0.054932 | 122.4289 | 122.3557 | 122.374 | -0.87433 | 122.9645 | 123.0194 | 122.3053 | -123.2712
689.6562 | 123.2346 | -122.3511 | 0.74616 | -0.00091566 | 0.011343 | -0.00068791 | 0.0016215 | 0.054006 | -0.0034949 | -0.0014099 | -0.00083936 | -0.0047766 | 0.096115 | 0.071478 | -0.00087393 | -0.006116 | 0.11902 | 0.11444 | 0.036621 | 0.1831 | 0.13733 | 0.064087 | -0.054932 | -122.7951 | 0.022888 | -122.406 | 0.59509 | 0.63629 | -122.2778 | -122.4838 | 122.4152 | 122.2961 | -0.60883 | 122.4655 | 122.5342 | 0.23804 | -0.62714 | 0.073242 | -0.13275 | -0.15106 | -0.44403 | -0.054932 | 0.07782 | -0.10986 | 122.4884 | 122.4701 | 122.3877 | -0.80109 | 122.9462 | 122.9874 | 122.374 | -123.23
691.4062 | 123.1247 | -121.8018 | 1.3367 | -0.0085447 | 0.013907 | -4.6912e-05 | 0.0050393 | 0.05486 | -0.0062719 | -0.0069641 | -0.0084684 | -0.0043494 | 0.098465 | 0.069983 | -0.0045055 | -0.0059024 | 0.10529 | 0.14191 | 0.15564 | 0.16479 | 0.12817 | 0.064087 | -0.068665 | -122.2366 | 0.10071 | -121.843 | 1.1902 | 1.2497 | -121.6965 | -121.9025 | 121.8658 | 121.7331 | -1.2085 | 121.9437 | 121.9666 | 0.23346 | -1.2314 | 0.10529 | -0.10071 | -0.14648 | -0.43487 | -0.041199 | 0.059509 | -0.086975 | 121.9299 | 121.907 | 121.9574 | -1.4053 | 122.9919 | 123.0515 | 121.9025 | -123.2391
693.1094 | 123.2391 | -120.4468 | 2.5864 | 0.0067138 | 0.015189 | 0.0010211 | 0.0052531 | 0.052083 | -7.6908e-05 | -0.0035461 | -0.00083936 | -0.0007178 | 0.096756 | 0.069342 | -0.0021557 | -0.0091068 | 0.022888 | -0.009155 | 0.091553 | 0.10529 | 0.16479 | 0.022888 | -0.091553 | -120.845 | -0.10071 | -120.4788 | 2.7008 | 2.7328 | -120.2637 | -120.4834 | 120.4697 | 120.3552 | -2.4216 | 120.4376 | 120.5521 | 0.19684 | -2.5635 | 0.1831 | -0.036621 | 0.11444 | -0.39826 | -0.032044 | 0.004577 | 0.14648 | 120.6116 | 120.4697 | 120.5383 | -2.6779 | 123.1476 | 123.1796 | 120.3461 | -123.0698
694.8438 | 123.1796 | -121.7056 | 1.3962 | -0.00091566 | 0.0077118 | 0.0020893 | 0.0041849 | 0.054433 | -0.0062719 | -0.0065369 | -0.0084684 | -0.0056312 | 0.095261 | 0.068915 | -0.0055735 | -0.0082522 | 0.068665 | 0.09613 | 0.041199 | 0.15106 | 0.13733 | 0.050354 | -0.068665 | -122.1863 | 0.045776 | -121.7834 | 1.2497 | 1.3092 | -121.6461 | -121.8613 | 121.756 | 121.637 | -1.2589 | 121.8018 | 121.8567 | 0.21973 | -1.3275 | 0.059509 | -0.15564 | -0.14648 | -0.48065 | -0.07782 | 0.07782 | -0.086975 | 121.843 | 121.7743 | 121.7468 | -1.4648 | 122.9553 | 123.0148 | 121.7514 | -123.2574
696.5938 | 123.1155 | -120.9366 | 2.1835 | -0.00091566 | 0.013693 | -0.00026071 | 0.0078165 | 0.052724 | -0.0032813 | -0.0029053 | -0.00083936 | -0.0024268 | 0.097824 | 0.071051 | -0.0027965 | -0.0091068 | 0.11902 | 0.1236 | 0.17395 | 0.1831 | 0.12817 | 0.050354 | -0.054932 | -121.3669 | 0.082397 | -120.9869 | 2.037 | 2.092 | -120.8496 | -121.0602 | 120.9869 | 120.8817 | -2.0554 | 121.0602 | 121.1197 | 0.23804 | -2.0645 | 0.086975 | -0.1236 | -0.14649 | -0.4303 | -0.050354 | 0.073243 | -0.091553 | 121.0648 | 121.0556 | 121.1105 | -2.2385 | 122.9736 | 123.0286 | 121.019 | -123.2437
698.3594 | 123.1384 | -121.994 | 1.1398 | -0.0085447 | 0.013907 | 0.0010211 | 0.0046121 | 0.052297 | -0.0034949 | -0.0056823 | -0.0084684 | -0.0024268 | 0.098252 | 0.070837 | -0.0038647 | -0.009534 | 0.027466 | 0 | 0.07782 | 0.07782 | 0.16937 | 0.022888 | -0.082397 | -122.5388 | -0.027466 | -122.1634 | 1.0391 | 1.0757 | -121.9574 | -122.168 | 122.0169 | 121.9116 | -0.97046 | 121.994 | 122.0718 | 0.16022 | -1.1124 | 0.036622 | -0.17395 | -0.10071 | -0.54474 | -0.16937 | 0.004578 | -0.064087 | 122.1634 | 122.0215 | 122.0718 | -1.2222 | 123.0331 | 123.0698 | 121.9666 | -123.3078
700.0625 | 123.2071 | -122.1313 | 0.90637 | -0.0085447 | 0.015189 | 0.0010211 | 0.0041849 | 0.052297 | 0.0027003 | -0.0033325 | -0.0084684 | 0.0003504 | 0.098038 | 0.072119 | -0.00023313 | -0.011884 | 0.10529 | 0.054932 | 0.12817 | 0.1236 | 0.16022 | 0.045776 | -0.091553 | -122.6395 | 0.032043 | -122.3007 | 0.82855 | 0.87433 | -122.0901 | -122.3099 | 122.1771 | 122.0398 | -0.74615 | 122.1863 | 122.2549 | 0.21515 | -0.80109 | 0.041199 | -0.17853 | -0.07782 | -0.50812 | -0.16937 | 0.009155 | -0.032043 | 122.2916 | 122.2366 | 122.2595 | -0.99792 | 122.9599 | 123.0057 | 122.1634 | -123.2162
701.7969 | 123.1796 | -122.1817 | 0.90637 | -0.00091566 | 0.013693 | 0.0014483 | 0.0063211 | 0.051656 | -0.0069129 | -0.0056823 | -0.00083936 | -0.0069128 | 0.097611 | 0.071478 | -0.0049327 | -0.0073978 | 0.11444 | 0.13733 | 0.10529 | 0.16479 | 0.11902 | 0.054932 | -0.045776 | -122.6257 | 0.059509 | -122.2183 | 0.79193 | 0.8194 | -122.1085 | -122.3373 | 122.2366 | 122.1359 | -0.78735 | 122.319 | 122.3465 | 0.21057 | -0.79193 | 0.073243 | -0.15564 | -0.11444 | -0.44403 | -0.036621 | 0.11902 | -0.086975 | 122.3007 | 122.2961 | 122.287 | -0.95215 | 122.9736 | 123.0011 | 122.2412 | -123.2437
703.5469 | 123.1293 | -122.3465 | 0.80566 | -0.00091566 | 0.010703 | 0.0014483 | 0.0029031 | 0.053365 | -0.0054175 | -0.0050415 | -0.00083936 | -0.0041358 | 0.095902 | 0.067847 | -0.0034373 | -0.0063296 | 0.073242 | 0.09613 | -0.009155 | 0.13275 | 0.13275 | 0.073242 | -0.059509 | -122.8043 | -0.036621 | -122.4152 | 0.65918 | 0.68665 | -122.2641 | -122.4747 | 122.4197 | 122.287 | -0.67291 | 122.4426 | 122.4792 | 0.19226 | -0.73242 | 0.082398 | -0.12817 | -0.14648 | -0.45776 | -0.068664 | 0.059509 | -0.11902 | 122.4792 | 122.4197 | 122.3373 | -0.86517 | 123.0057 | 123.0331 | 122.3099 | -123.2803
705.2969 | 123.2712 | -122.0764 | 0.97504 | -0.00091566 | 0.01348 | 0.00016669 | 0.0033305 | 0.052938 | 0.00056389 | -0.0011963 | -0.0084684 | -0.0002906 | 0.096756 | 0.071265 | -0.00044673 | -0.0080386 | 0.045776 | -0.013733 | -0.050354 | 0.07782 | 0.16479 | 0.027466 | -0.082397 | -122.5937 | -0.068665 | -122.2595 | 0.85602 | 0.9201 | -122.0444 | -122.2687 | 122.1039 | 121.994 | -0.81024 | 122.0627 | 122.1542 | 0.16022 | -0.92926 | 0.032043 | -0.19226 | -0.11902 | -0.51727 | -0.18311 | 0.009156 | -0.054932 | 122.2412 | 122.1222 | 122.0261 | -1.0574 | 122.9324 | 122.9965 | 122.0078 | -123.2437
707.0469 | 123.2666 | -121.9025 | 1.149 | -0.0085447 | 0.014761 | -0.0013287 | 0.0016215 | 0.053365 | -7.6908e-05 | -0.0039733 | -0.0084684 | 0.0012048 | 0.097397 | 0.069983 | -0.00066033 | -0.0063296 | 0.045776 | 0 | -0.027466 | 0.091553 | 0.16022 | 0.041199 | -0.082397 | -122.3831 | -0.050354 | -122.049 | 1.0712 | 1.1124 | -121.8201 | -122.0535 | 121.9437 | 121.8201 | -0.98877 | 121.9025 | 121.994 | 0.17395 | -1.1032 | 0.082398 | -0.15106 | -0.07782 | -0.48065 | -0.14648 | 0.004578 | -0.036621 | 122.0627 | 121.9482 | 121.875 | -1.2314 | 122.9736 | 123.0148 | 121.8521 | -123.2025
708.7812 | 123.1659 | -121.7789 | 1.3092 | -0.0085447 | 0.011984 | 0.0029437 | 0.0095255 | 0.055501 | -0.0071265 | -0.0048279 | -0.00083936 | -0.0054174 | 0.097824 | 0.06806 | -0.0060009 | -0.0080386 | 0.09613 | 0.11902 | 0.09613 | 0.16479 | 0.12817 | 0.064087 | -0.086975 | -122.2275 | 0.054932 | -121.8384 | 1.1581 | 1.2039 | -121.7194 | -121.9437 | 121.843 | 121.6919 | -1.181 | 121.8979 | 121.9437 | 0.25177 | -1.2131 | 0.05951 | -0.16479 | -0.15106 | -0.44861 | -0.059509 | 0.10529 | -0.10529 | 121.907 | 121.875 | 121.875 | -1.3962 | 122.937 | 122.9828 | 121.8338 | -123.2529
710.4688 | 123.1567 | -121.2479 | 1.8723 | -0.00091566 | 0.011343 | 0.0010211 | 0.0073893 | 0.054647 | -0.0039221 | -0.0050415 | -0.00083936 | -0.006272 | 0.098679 | 0.068701 | -0.0042919 | -0.007825 | 0.050354 | 0.054932 | -0.013733 | 0.13275 | 0.13733 | 0.050354 | -0.068665 | -121.7331 | -0.032043 | -121.3486 | 1.7075 | 1.7532 | -121.1838 | -121.4172 | 121.2982 | 121.1792 | -1.7349 | 121.3028 | 121.3806 | 0.20142 | -1.8219 | 0.064087 | -0.16937 | -0.1648 | -0.48523 | -0.10071 | 0.068664 | -0.11902 | 121.3852 | 121.2982 | 121.2341 | -1.9409 | 122.9553 | 123.0011 | 121.2158 | -123.2895
712.2188 | 123.1842 | -121.6736 | 1.4008 | -0.0085447 | 0.016257 | -0.00090151 | 0.00012606 | 0.052083 | 0.0022729 | -0.0041869 | -0.00083936 | 0.0003504 | 0.096543 | 0.070837 | 0.00062147 | -0.0097476 | 0.082397 | 0.013733 | 0.064087 | 0.11444 | 0.15564 | 0.032043 | -0.086975 | -122.0444 | -0.036621 | -121.7331 | 1.4786 | 1.4877 | -121.4767 | -121.7194 | 121.7056 | 121.5866 | -1.2451 | 121.6873 | 121.788 | 0.20142 | -1.3184 | 0.19684 | -0.045776 | 0.07782 | -0.37079 | -0.059509 | -0.013733 | 0.086975 | 121.8292 | 121.756 | 121.7377 | -1.4877 | 123.1522 | 123.1613 | 121.637 | -123.1201
713.9688 | 123.1476 | -121.582 | 1.5244 | -0.00091566 | 0.013693 | 0.0033709 | 0.0054667 | 0.055929 | -0.0054175 | -0.0046143 | 0.0067901 | -0.006272 | 0.098679 | 0.069128 | -0.0040783 | -0.0080386 | 0.1236 | 0.14648 | 0.14191 | 0.16022 | 0.13733 | 0.073242 | -0.068665 | -121.9437 | 0.07782 | -121.5637 | 1.4145 | 1.4832 | -121.4539 | -121.6599 | 121.6553 | 121.5134 | -1.387 | 121.7285 | 121.7422 | 0.22888 | -1.4008 | 0.12817 | -0.07782 | -0.10986 | -0.36163 | 0.01831 | 0.09613 | -0.041199 | 121.7194 | 121.7056 | 121.7239 | -1.593 | 122.9965 | 123.0652 | 121.6599 | -123.1842
715.6406 | 123.2208 | -121.8109 | 1.2177 | -0.0085447 | 0.016257 | -0.00047431 | 0.0050393 | 0.05187 | 0.0018457 | -0.0033325 | -0.00083936 | -0.0026404 | 0.098465 | 0.070837 | -1.9327e-05 | -0.0099612 | 0.091553 | 0.045776 | 0.1236 | 0.14191 | 0.16022 | 0.036621 | -0.082397 | -122.2641 | 0.10529 | -121.9482 | 1.1719 | 1.1993 | -121.7422 | -121.9574 | 121.8475 | 121.7285 | -1.0574 | 121.8567 | 121.9528 | 0.2243 | -1.1261 | 0.068664 | -0.14648 | -0.045776 | -0.45319 | -0.13733 | 0.009155 | -0.01831 | 121.9711 | 121.9025 | 121.9345 | -1.3 | 122.9828 | 123.0103 | 121.9162 | -123.175
717.3906 | 123.1338 | -121.7697 | 1.3321 | -0.0085447 | 0.015189 | -4.6912e-05 | 0.0099527 | 0.054006 | -0.0019995 | -0.0058959 | -0.00083936 | -0.0041358 | 0.098252 | 0.070837 | -0.0013011 | -0.0071842 | 0.022888 | -0.004578 | 0.068665 | 0.082397 | 0.17853 | 0.022888 | -0.09613 | -122.3099 | -0.022888 | -121.9345 | 1.2405 | 1.268 | -121.7285 | -121.9116 | 121.7926 | 121.6736 | -1.1536 | 121.7651 | 121.8521 | 0.17853 | -1.3092 | 0.041198 | -0.14191 | -0.091552 | -0.54016 | -0.1648 | -0.022888 | -0.064087 | 121.9482 | 121.7926 | 121.8384 | -1.4282 | 123.0103 | 123.0377 | 121.7468 | -123.2437
719.0781 | 123.1979 | -121.9116 | 1.1215 | -0.00091566 | 0.017752 | 0.00059389 | 0.0043985 | 0.054433 | 0.00013669 | -0.0033325 | -0.0084684 | 0.0001368 | 0.098252 | 0.069128 | -0.0030101 | -0.0084658 | 0.013733 | -0.013733 | 0.050354 | 0.09613 | 0.17853 | 0.027466 | -0.10529 | -122.4609 | 0 | -122.113 | 1.062 | 1.1078 | -121.8933 | -122.1176 | 121.9391 | 121.8063 | -0.94299 | 121.8979 | 122.0078 | 0.20142 | -1.1078 | 0.01831 | -0.20599 | -0.059509 | -0.54932 | -0.20142 | 0.004578 | -0.013733 | 122.0901 | 121.9254 | 121.962 | -1.2268 | 122.9736 | 123.0194 | 121.9116 | -123.2391
720.8125 | 123.1842 | -121.9986 | 1.0483 | -0.0085447 | 0.01647 | 0.0018757 | 0.0052531 | 0.05422 | -0.0011451 | -0.0022643 | -0.0084684 | -0.0030676 | 0.1006 | 0.071905 | -0.0027965 | -0.007825 | 0.009155 | -0.013733 | 0.068665 | 0.07782 | 0.16022 | 0.032043 | -0.10071 | -122.5571 | 0.004578 | -122.1954 | 0.97504 | 1.0391 | -121.962 | -122.1771 | 122.0306 | 121.8979 | -0.88806 | 121.9849 | 122.0764 | 0.17853 | -1.0391 | 0.036621 | -0.17853 | -0.073242 | -0.55847 | -0.19684 | -0.018311 | -0.009155 | 122.1588 | 122.0078 | 122.0673 | -1.149 | 122.9736 | 123.0377 | 122.0032 | -123.2254
722.5 | 123.1201 | -121.9482 | 1.149 | -0.00091566 | 0.0094208 | 0.0029437 | 0.0043985 | 0.054647 | -0.0052039 | -0.0033325 | -0.00083936 | -0.0052038 | 0.095261 | 0.068701 | -0.0034373 | -0.0065432 | 0.073242 | 0.07782 | -0.009155 | 0.12817 | 0.14191 | 0.068665 | -0.059509 | -122.4335 | -0.041199 | -122.0306 | 1.0071 | 1.0391 | -121.8704 | -122.0947 | 122.0169 | 121.8887 | -1.0071 | 122.0261 | 122.0764 | 0.18768 | -1.0757 | 0.07782 | -0.14649 | -0.14191 | -0.48523 | -0.082398 | 0.064087 | -0.10986 | 122.0901 | 122.0215 | 121.9391 | -1.2085 | 122.9553 | 122.9874 | 121.907 | -123.2437
724.2656 | 123.1201 | -121.9025 | 1.2131 | -0.00091566 | 0.011771 | 0.00059389 | 0.0050393 | 0.052938 | -0.0064855 | -0.0069641 | -0.0084684 | -0.0043494 | 0.096543 | 0.068487 | -0.0049327 | -0.0073978 | 0.068665 | 0.041199 | -0.004578 | 0.12817 | 0.13733 | 0.050354 | -0.054932 | -122.3785 | -0.059509 | -121.9986 | 1.0849 | 1.1169 | -121.8246 | -122.0215 | 121.9528 | 121.8475 | -1.0757 | 121.9437 | 122.0306 | 0.18311 | -1.1444 | 0.07782 | -0.11902 | -0.12817 | -0.47607 | -0.09613 | 0.022888 | -0.096131 | 122.0398 | 121.9711 | 121.8979 | -1.268 | 122.9874 | 123.0194 | 121.843 | -123.2346
725.9531 | 123.2346 | -122.3053 | 0.74616 | -0.016174 | 0.014761 | -0.0026105 | 0.0048257 | 0.052083 | 0.0022729 | -0.0048279 | -0.00083936 | -0.0030676 | 0.095475 | 0.070837 | -0.00044673 | -0.0086796 | 0.073242 | 0.009155 | -0.032043 | 0.10529 | 0.15564 | 0.050354 | -0.086975 | -122.7814 | -0.027466 | -122.4197 | 0.6546 | 0.66376 | -122.2595 | -122.4701 | 122.3557 | 122.2183 | -0.59052 | 122.3145 | 122.4106 | 0.19226 | -0.67291 | 0.045777 | -0.1648 | -0.091553 | -0.47607 | -0.11444 | 0.050354 | -0.082398 | 122.4609 | 122.3785 | 122.2733 | -0.83313 | 122.9599 | 122.9691 | 122.2778 | -123.2162
727.6875 | 123.2162 | -122.3373 | 0.70496 | -0.00091566 | 0.014975 | 0.0010211 | 0.0039713 | 0.052297 | 0.00099129 | -0.0029053 | -0.00083936 | -0.0009314 | 0.097824 | 0.071692 | -0.0010875 | -0.010602 | 0.086975 | 0.036621 | 0.10986 | 0.13275 | 0.17395 | 0.050354 | -0.082397 | -122.8088 | 0.041199 | -122.4884 | 0.62256 | 0.65918 | -122.3099 | -122.5204 | 122.3877 | 122.2549 | -0.53101 | 122.374 | 122.4701 | 0.21515 | -0.61798 | 0.027466 | -0.18311 | -0.082397 | -0.4715 | -0.15106 | 0.032044 | -0.045776 | 122.5113 | 122.4243 | 122.4472 | -0.78735 | 122.9599 | 122.9965 | 122.3785 | -123.2254
729.4531 | 123.1796 | -122.2916 | 0.75989 | -0.00091566 | 0.014761 | -0.00090151 | 0.0029031 | 0.053152 | -0.00029051 | -0.0026917 | -0.0084684 | 0.0007776 | 0.097184 | 0.071265 | 0.0014759 | -0.007825 | 0.036621 | -0.041199 | -0.018311 | 0.091553 | 0.17395 | 0.045776 | -0.09613 | -122.8592 | -0.15106 | -122.5433 | 0.66834 | 0.72327 | -122.2824 | -122.5113 | 122.3373 | 122.1954 | -0.58594 | 122.2504 | 122.3831 | 0.18768 | -0.72327 | 0.009155 | -0.21973 | -0.091553 | -0.56763 | -0.25177 | -0.032043 | -0.036621 | 122.4655 | 122.3282 | 122.2733 | -0.85602 | 122.9599 | 123.0148 | 122.1405 | -123.2712
731.1875 | 123.2254 | -122.113 | 0.89264 | -0.0085447 | 0.012412 | 0.00038029 | 0.0046121 | 0.053579 | -0.0028539 | -0.0024779 | -0.0084684 | -0.0009314 | 0.095047 | 0.069128 | -0.0042919 | -0.0035526 | 0.018311 | -0.022888 | 0.068665 | 0.11444 | 0.16022 | 0.036621 | -0.09613 | -122.6578 | 0.013733 | -122.2961 | 0.8194 | 0.88348 | -122.1268 | -122.319 | 122.1497 | 122.0169 | -0.73242 | 122.0901 | 122.2275 | 0.21057 | -0.87433 | -0.013733 | -0.20599 | -0.073242 | -0.54474 | -0.18311 | 0.022888 | -0.009155 | 122.2733 | 122.1313 | 122.1817 | -0.98877 | 122.9324 | 122.9965 | 122.1268 | -123.2117
732.875 | 123.23 | -122.0993 | 0.90637 | -0.0085447 | 0.013052 | -0.00090151 | 0.0026895 | 0.053579 | -0.00029051 | -0.0031189 | -0.016098 | -0.0037086 | 0.096543 | 0.069983 | 0.00019427 | -0.0071842 | 0.022888 | -0.036621 | -0.050354 | 0.082397 | 0.16022 | 0.027466 | -0.091553 | -122.6624 | -0.086975 | -122.3053 | 0.83771 | 0.89264 | -122.1176 | -122.2916 | 122.1268 | 122.0078 | -0.74615 | 122.0627 | 122.1817 | 0.17395 | -0.88348 | -0.018311 | -0.19226 | -0.068664 | -0.56305 | -0.20599 | -0.013733 | -0.013733 | 122.2595 | 122.1222 | 122.049 | -0.99792 | 122.937 | 122.9919 | 122.0123 | -123.1979
734.625 | 123.0927 | -122.2549 | 0.84686 | -0.00091566 | 0.015189 | 0.0029437 | 0.010807 | 0.052083 | -0.0060583 | -0.0050415 | -0.016098 | -0.0054174 | 0.098252 | 0.068274 | -0.0053599 | -0.0082522 | 0.10529 | 0.13733 | 0.16479 | 0.16937 | 0.14648 | 0.068665 | -0.059509 | -122.6852 | 0.086975 | -122.287 | 0.70496 | 0.73242 | -122.1817 | -122.3785 | 122.3236 | 122.1954 | -0.70038 | 122.3923 | 122.4243 | 0.22888 | -0.74158 | 0.073242 | -0.1236 | -0.14191 | -0.4303 | -0.032043 | 0.091553 | -0.11444 | 122.4014 | 122.3602 | 122.4197 | -0.90637 | 122.9599 | 122.9874 | 122.3419 | -123.2254
736.375 | 123.1018 | -122.2321 | 0.87433 | -0.0085447 | 0.010703 | -0.00047431 | 0.0088847 | 0.052724 | -0.0049903 | -0.0052551 | -0.00083936 | -0.0037086 | 0.098465 | 0.069556 | -0.0057873 | -0.0076114 | 0.059509 | 0.068665 | -0.009155 | 0.13733 | 0.14191 | 0.068665 | -0.064087 | -122.7219 | -0.059509 | -122.3053 | 0.75531 | 0.77362 | -122.168 | -122.3602 | 122.3007 | 122.168 | -0.73242 | 122.3007 | 122.3694 | 0.20142 | -0.81482 | 0.064087 | -0.12817 | -0.11902 | -0.48981 | -0.073242 | 0.054931 | -0.10071 | 122.374 | 122.2916 | 122.2229 | -0.93842 | 122.9874 | 123.0057 | 122.1725 | -123.2346
738.0625 | 123.0972 | -122.2229 | 0.86975 | -0.023804 | 0.0092072 | -0.00090151 | 0.0035441 | 0.055074 | -0.0052039 | -0.0037597 | -0.0084684 | -0.0041358 | 0.097184 | 0.069769 | -0.0021557 | -0.0084658 | 0.082397 | 0.09613 | 0.13275 | 0.14191 | 0.13275 | 0.050354 | -0.068665 | -122.699 | 0.009155 | -122.3511 | 0.74616 | 0.79651 | -122.1817 | -122.4197 | 122.2733 | 122.1542 | -0.737 | 122.319 | 122.3648 | 0.21057 | -0.78735 | 0.041198 | -0.19684 | -0.1236 | -0.47608 | -0.12817 | 0.068665 | -0.073242 | 122.3557 | 122.3053 | 122.3557 | -0.93842 | 122.9691 | 123.0194 | 122.2321 | -123.2895
739.8125 | 123.1155 | -122.2733 | 0.83313 | -0.0085447 | 0.013693 | 0.00059389 | 0.0037577 | 0.053365 | -0.0037085 | -0.0065369 | -0.00083936 | -0.0058448 | 0.096115 | 0.06571 | -0.0021557 | -0.010175 | 0.1236 | 0.10986 | 0.032043 | 0.15106 | 0.1236 | 0.059509 | -0.059509 | -122.6944 | -0.013733 | -122.3282 | 0.67749 | 0.72784 | -122.1771 | -122.406 | 122.3328 | 122.2137 | -0.70953 | 122.3831 | 122.4243 | 0.21057 | -0.70953 | 0.09613 | -0.13275 | -0.15564 | -0.42114 | -0.054932 | 0.07782 | -0.10529 | 122.3969 | 122.3969 | 122.3053 | -0.89264 | 122.9507 | 123.0011 | 122.2595 | -123.2391
741.5156 | 123.1018 | -122.3282 | 0.79193 | -0.0085447 | 0.014121 | -0.00026071 | 0.0056803 | 0.053365 | -0.0049903 | -0.0076049 | -0.00083936 | -0.0054174 | 0.099961 | 0.068487 | -0.0036509 | -0.0076114 | 0.073242 | 0.068665 | 0 | 0.14191 | 0.13275 | 0.07782 | -0.054932 | -122.7814 | -0.064087 | -122.4152 | 0.6546 | 0.67291 | -122.2595 | -122.4609 | 122.406 | 122.2733 | -0.65918 | 122.3969 | 122.4701 | 0.19684 | -0.71869 | 0.068665 | -0.13275 | -0.13733 | -0.45319 | -0.086975 | 0.045776 | -0.11902 | 122.4609 | 122.4014 | 122.3282 | -0.84686 | 122.9828 | 123.0011 | 122.2641 | -123.2529
743.2812 | 123.1796 | -122.3465 | 0.6958 | -0.00091566 | 0.015402 | -0.0030377 | 0.0050393 | 0.05422 | 0.0027003 | -0.0050415 | -0.016098 | 0.0018456 | 0.098252 | 0.071692 | 0.00083507 | -0.0099612 | 0.1236 | 0.059509 | 0.11444 | 0.11902 | 0.17395 | 0.041199 | -0.064087 | -122.7997 | 0.036621 | -122.5067 | 0.62256 | 0.65002 | -122.3053 | -122.525 | 122.3877 | 122.2824 | -0.52185 | 122.406 | 122.4655 | 0.18311 | -0.5722 | 0.041199 | -0.17853 | -0.073242 | -0.45319 | -0.16022 | 0.01831 | -0.045777 | 122.5204 | 122.4701 | 122.4609 | -0.75989 | 122.9691 | 122.9965 | 122.3831 | -123.2208
745.0781 | 123.1842 | -122.3145 | 0.71869 | -0.0085447 | 0.017538 | -0.00047431 | 0.0069621 | 0.051656 | -0.0043493 | -0.0033325 | -0.00083936 | -0.0015722 | 0.099747 | 0.07041 | -0.0021557 | -0.0084658 | 0.022888 | -0.009155 | 0.073242 | 0.086975 | 0.19226 | 0.036621 | -0.09613 | -122.8455 | -0.004578 | -122.5021 | 0.65002 | 0.70496 | -122.3099 | -122.4884 | 122.3511 | 122.2183 | -0.52643 | 122.3053 | 122.4014 | 0.1831 | -0.6958 | 0.004578 | -0.17395 | -0.068665 | -0.53101 | -0.18768 | -0.013733 | -0.013733 | 122.5067 | 122.3373 | 122.3877 | -0.81482 | 122.9645 | 123.0194 | 122.3099 | -123.2071
746.8281 | 123.1247 | -122.3145 | 0.76446 | -0.0085447 | 0.01583 | 0.00038029 | 0.0071757 | 0.052297 | -0.0026403 | -0.0052551 | 0.0067901 | -0.0037086 | 0.098893 | 0.069769 | -0.0030101 | -0.0076114 | 0.027466 | -0.013733 | 0.068665 | 0.086975 | 0.18768 | 0.018311 | -0.091553 | -122.8409 | -0.022888 | -122.4838 | 0.68665 | 0.71411 | -122.2549 | -122.4701 | 122.3328 | 122.2229 | -0.57678 | 122.3007 | 122.4014 | 0.17853 | -0.737 | 0.059509 | -0.15564 | -0.077819 | -0.52643 | -0.16937 | -0.013733 | -0.050354 | 122.5021 | 122.3419 | 122.3831 | -0.85602 | 123.0011 | 123.0286 | 122.2916 | -123.2346
748.5938 | 123.1384 | -122.2687 | 0.80109 | -0.00091566 | 0.01348 | 0.00059389 | 0.0054667 | 0.052297 | -0.0058447 | -0.0037597 | -0.00083936 | -0.0041358 | 0.097824 | 0.070196 | -0.0038647 | -0.0041934 | 0.1236 | 0.1236 | 0.086975 | 0.16022 | 0.14191 | 0.068665 | -0.054932 | -122.6898 | 0.054932 | -122.2778 | 0.67291 | 0.72784 | -122.2 | -122.4152 | 122.3373 | 122.2137 | -0.65918 | 122.3923 | 122.4289 | 0.21515 | -0.67749 | 0.068665 | -0.14648 | -0.12817 | -0.42114 | -0.009155 | 0.13733 | -0.073242 | 122.4106 | 122.3923 | 122.3557 | -0.85602 | 122.9416 | 122.9965 | 122.3236 | -123.2162
750.2812 | 123.0835 | -122.3419 | 0.75073 | -0.00091566 | 0.010489 | 0.0027301 | 0.0069621 | 0.051015 | -0.0030677 | -0.0041869 | -0.0084684 | -0.0032812 | 0.097397 | 0.06806 | -0.0017283 | -0.0091068 | 0.073242 | 0.091553 | 0.013733 | 0.1236 | 0.15106 | 0.068665 | -0.054932 | -122.7859 | -0.041199 | -122.4197 | 0.60883 | 0.65918 | -122.2595 | -122.4747 | 122.4106 | 122.287 | -0.59967 | 122.4335 | 122.4655 | 0.17853 | -0.67749 | 0.082398 | -0.13275 | -0.14191 | -0.44403 | -0.07782 | 0.054931 | -0.091552 | 122.493 | 122.4152 | 122.3557 | -0.80566 | 122.9507 | 123.0011 | 122.3007 | -123.2254
752.0312 | 123.0698 | -122.2549 | 0.85602 | -0.00091566 | 0.013693 | 0.0018757 | 0.0048257 | 0.051656 | -0.0054175 | -0.0054687 | -0.00083936 | -0.001145 | 0.097184 | 0.06806 | -0.0025829 | -0.007825 | 0.11444 | 0.11444 | 0.13275 | 0.15564 | 0.14648 | 0.045776 | -0.07782 | -122.6944 | 0.041199 | -122.3282 | 0.72327 | 0.7782 | -122.2 | -122.4197 | 122.3007 | 122.1771 | -0.70953 | 122.3694 | 122.4106 | 0.23346 | -0.74158 | 0.054932 | -0.1648 | -0.13275 | -0.43945 | -0.073242 | 0.091553 | -0.07782 | 122.4014 | 122.3694 | 122.3877 | -0.93384 | 122.9782 | 123.0331 | 122.2961 | -123.2758
753.7812 | 123.1064 | -121.9574 | 1.1078 | -0.00091566 | 0.013266 | 0.00059389 | 0.0058939 | 0.055501 | -0.0028539 | -0.0071777 | -0.016098 | -0.0022132 | 0.096756 | 0.068915 | -0.0036509 | -0.0071842 | 0.15106 | 0.15106 | 0.14191 | 0.17395 | 0.11902 | 0.054932 | -0.073242 | -122.374 | 0.07782 | -121.9894 | 0.9613 | 1.0254 | -121.8796 | -122.1085 | 122.0123 | 121.8842 | -0.98877 | 122.1085 | 122.1313 | 0.24719 | -0.95673 | 0.077819 | -0.15106 | -0.14648 | -0.41657 | -0.032044 | 0.11902 | -0.082397 | 122.0764 | 122.1085 | 122.0993 | -1.181 | 122.9187 | 122.9828 | 122.0352 | -123.2162
755.4688 | 123.1201 | -122.1863 | 0.88806 | 0.0067138 | 0.012839 | 0.0012347 | 0.0090983 | 0.053152 | -0.0071265 | -0.0061095 | -0.00083936 | -0.0043494 | 0.098679 | 0.068701 | -0.0066417 | -0.0080386 | 0.07782 | 0.054932 | 0.013733 | 0.13275 | 0.13733 | 0.064087 | -0.054932 | -122.6074 | -0.027466 | -122.2504 | 0.76446 | 0.80109 | -122.1313 | -122.3328 | 122.2504 | 122.1313 | -0.75073 | 122.2412 | 122.319 | 0.18768 | -0.81024 | 0.054931 | -0.14648 | -0.1236 | -0.42114 | -0.064087 | 0.082398 | -0.086976 | 122.3236 | 122.2641 | 122.2 | -0.94299 | 122.9507 | 122.9874 | 122.1588 | -123.2208
757.1719 | 123.1201 | -122.1725 | 0.94299 | -0.0085447 | 0.015189 | 0.00059389 | 0.0067483 | 0.053579 | -0.0026403 | -0.0050415 | 0.0067901 | -0.0043494 | 0.097184 | 0.068274 | -0.0038647 | -0.0097476 | 0.068665 | 0.054932 | -0.018311 | 0.13275 | 0.13275 | 0.064087 | -0.07782 | -122.6028 | -0.054932 | -122.2595 | 0.81024 | 0.8194 | -122.0901 | -122.287 | 122.2366 | 122.0947 | -0.81024 | 122.2275 | 122.3053 | 0.21057 | -0.87433 | 0.082397 | -0.11444 | -0.13275 | -0.4303 | -0.086975 | 0.027466 | -0.1236 | 122.3053 | 122.2412 | 122.1542 | -1.0208 | 122.9828 | 122.9919 | 122.1176 | -123.23
758.9219 | 123.0743 | -122.168 | 0.93384 | -0.00091566 | 0.013052 | -0.00026071 | 0.0022623 | 0.053792 | -0.00071771 | -0.0050415 | -0.00083936 | -0.0032812 | 0.09697 | 0.069769 | -0.0019419 | -0.0097476 | 0.14191 | 0.13275 | 0.032043 | 0.16022 | 0.12817 | 0.07782 | -0.059509 | -122.5525 | -0.013733 | -122.2275 | 0.79193 | 0.80109 | -122.0718 | -122.2824 | 122.2458 | 122.1085 | -0.80566 | 122.3007 | 122.3282 | 0.21973 | -0.79193 | 0.096131 | -0.11444 | -0.14191 | -0.38452 | -0.059509 | 0.054932 | -0.13275 | 122.2961 | 122.3099 | 122.2 | -0.99335 | 122.9599 | 122.9691 | 122.1542 | -123.2162
760.6719 | 123.1522 | -122.1634 | 0.86517 | -0.00091566 | 0.01647 | 0.00059389 | 0.0016215 | 0.055715 | 0.0039819 | -0.0029053 | -0.00083936 | 0.001632 | 0.097184 | 0.069342 | 0.0014759 | -0.0084658 | 0.045776 | -0.009155 | -0.004578 | 0.086975 | 0.16937 | 0.045776 | -0.086975 | -122.6944 | -0.064087 | -122.3969 | 0.78278 | 0.81482 | -122.1497 | -122.374 | 122.2092 | 122.0764 | -0.6958 | 122.1542 | 122.2504 | 0.17395 | -0.8194 | 0.013733 | -0.21057 | -0.082397 | -0.53101 | -0.23346 | -0.022889 | -0.050354 | 122.3328 | 122.2092 | 122.1588 | -0.95215 | 122.9462 | 122.9782 | 122.0993 | -123.2391
762.3594 | 123.0881 | -122.2412 | 0.83771 | 0.0067138 | 0.014334 | 0.00016669 | 0.0039713 | 0.051443 | -0.0019995 | -0.0050415 | -0.016098 | -0.0030676 | 0.097824 | 0.06806 | -0.0010875 | -0.0080386 | 0.027466 | 0.004578 | 0.059509 | 0.073242 | 0.18768 | 0.009155 | -0.10986 | -122.7356 | -0.018311 | -122.3923 | 0.74616 | 0.7782 | -122.2092 | -122.4014 | 122.2504 | 122.1313 | -0.65003 | 122.2458 | 122.3145 | 0.18311 | -0.81024 | 0.032044 | -0.16022 | -0.091553 | -0.49438 | -0.15106 | 0.009155 | -0.05951 | 122.4289 | 122.2687 | 122.3007 | -0.94757 | 122.9874 | 123.0194 | 122.2229 | -123.2391
764.1094 | 123.1155 | -122.2778 | 0.81482 | 0.0067138 | 0.011984 | -4.6912e-05 | 0.0056803 | 0.053579 | -0.0034949 | -0.0063233 | -0.0084684 | -0.0056312 | 0.098465 | 0.068274 | -0.0030101 | -0.005048 | 0.050354 | 0.059509 | 0 | 0.1236 | 0.14191 | 0.050354 | -0.068665 | -122.7219 | -0.027466 | -122.3328 | 0.66376 | 0.6958 | -122.2229 | -122.4014 | 122.3282 | 122.2092 | -0.67291 | 122.3373 | 122.4014 | 0.19226 | -0.76446 | 0.054932 | -0.1236 | -0.15106 | -0.44403 | -0.054932 | 0.068664 | -0.11902 | 122.4197 | 122.3282 | 122.2778 | -0.88348 | 122.9416 | 122.9736 | 122.2504 | -123.2162
765.7812 | 123.1293 | -122.2687 | 0.80109 | -0.016174 | 0.010916 | 0.0018757 | 0.0058939 | 0.053792 | -0.0041357 | -0.0031189 | -0.016098 | -0.006272 | 0.095688 | 0.069556 | -0.0047191 | -0.0097476 | 0.07782 | 0.09613 | 0.036621 | 0.15564 | 0.14191 | 0.059509 | -0.064087 | -122.7081 | 0.022888 | -122.3236 | 0.67291 | 0.71869 | -122.2092 | -122.4014 | 122.3282 | 122.2046 | -0.65918 | 122.3648 | 122.4243 | 0.21973 | -0.72327 | 0.05951 | -0.13275 | -0.12817 | -0.43945 | -0.054931 | 0.07782 | -0.082397 | 122.4106 | 122.3465 | 122.3053 | -0.86517 | 122.9416 | 122.9874 | 122.2916 | -123.2025
767.5312 | 123.2117 | -122.1451 | 0.85144 | 0.0067138 | 0.013266 | -0.0017559 | 0.0050393 | 0.052511 | 0.00056389 | -0.0022643 | -0.00083936 | -7.6996e-05 | 0.097611 | 0.07041 | -0.0013011 | -0.0088932 | 0.045776 | 0.004578 | -0.045776 | 0.091553 | 0.1831 | 0.050354 | -0.07782 | -122.6532 | -0.073242 | -122.3328 | 0.78735 | 0.80566 | -122.1451 | -122.3373 | 122.1954 | 122.0673 | -0.66834 | 122.1497 | 122.2366 | 0.16937 | -0.80566 | 0 | -0.19226 | -0.064086 | -0.50812 | -0.18768 | 0.004577 | -0.045776 | 122.3282 | 122.1909 | 122.0993 | -0.92926 | 122.9324 | 122.9507 | 122.0718 | -123.1888
769.2344 | 123.2254 | -122.1817 | 0.8194 | -0.0085447 | 0.014121 | -0.0017559 | 0.0054667 | 0.051229 | 0.0020593 | -0.0033325 | -0.016098 | -0.001145 | 0.097824 | 0.071692 | -0.00044673 | -0.0082522 | 0.050354 | 0.004578 | -0.045776 | 0.09613 | 0.16937 | 0.041199 | -0.091553 | -122.6395 | -0.064087 | -122.3419 | 0.74616 | 0.78278 | -122.1954 | -122.3465 | 122.2229 | 122.0901 | -0.65002 | 122.1863 | 122.2778 | 0.18768 | -0.76904 | -0.013733 | -0.16479 | -0.073242 | -0.45776 | -0.16022 | 0.004578 | -0.036621 | 122.3511 | 122.2321 | 122.1359 | -0.91095 | 122.9279 | 122.9645 | 122.1176 | -123.1659
770.9844 | 123.2208 | -122.0764 | 0.89264 | -0.00091566 | 0.014761 | -0.00068791 | 0.0058939 | 0.052297 | -0.00029051 | -0.0048279 | -0.0084684 | -0.0013586 | 0.098252 | 0.072546 | -0.0010875 | -0.0093204 | 0.036621 | 0.018311 | -0.050354 | 0.091553 | 0.17395 | 0.054932 | -0.091553 | -122.5708 | -0.036621 | -122.2595 | 0.80566 | 0.85144 | -122.0856 | -122.2778 | 122.1313 | 121.9849 | -0.71869 | 122.0947 | 122.168 | 0.18311 | -0.85602 | -0.009155 | -0.20142 | -0.086975 | -0.49439 | -0.18311 | 0.018311 | -0.041199 | 122.2504 | 122.113 | 122.0261 | -0.98419 | 122.8821 | 122.9279 | 122.0398 | -123.1705
772.6719 | 123.111 | -122.1725 | 0.89722 | -0.00091566 | 0.014334 | 0.0018757 | 0.0067483 | 0.051229 | -0.0045629 | -0.0067505 | -0.00083936 | -0.0043494 | 0.096329 | 0.070837 | -0.0055735 | -0.0086796 | 0.032043 | 0.068665 | 0.004578 | 0.12817 | 0.13733 | 0.054932 | -0.059509 | -122.6395 | -0.018311 | -122.2321 | 0.737 | 0.76446 | -122.1359 | -122.3419 | 122.2275 | 122.113 | -0.75989 | 122.2412 | 122.3007 | 0.18768 | -0.86517 | 0.036621 | -0.16937 | -0.16022 | -0.46692 | -0.05951 | 0.10986 | -0.13275 | 122.3099 | 122.2046 | 122.1771 | -0.95673 | 122.9095 | 122.937 | 122.1542 | -123.2391
774.4375 | 123.1888 | -122.0215 | 0.99792 | -0.00091566 | 0.01348 | 0.00038029 | 0.0039713 | 0.053792 | 0.0014185 | -0.0022643 | -0.00083936 | -0.0017858 | 0.098893 | 0.072119 | -0.0015147 | -0.0099612 | 0.11902 | 0.13275 | 0.045776 | 0.16937 | 0.13733 | 0.073242 | -0.064087 | -122.4472 | 0.009155 | -122.1222 | 0.8606 | 0.87891 | -122.0169 | -122.168 | 122.0947 | 121.9574 | -0.8606 | 122.1542 | 122.1909 | 0.23346 | -0.87891 | 0.004577 | -0.14648 | -0.13733 | -0.42572 | -0.10071 | 0.045777 | -0.11902 | 122.1588 | 122.1405 | 122.0673 | -1.062 | 122.8821 | 122.9004 | 122.0306 | -123.1659
776.1875 | 123.1888 | -122.081 | 0.91553 | -0.0085447 | 0.015402 | -0.0032513 | 0.0067483 | 0.055501 | -0.00093131 | -0.0050415 | -0.00083936 | 0.0027002 | 0.098252 | 0.071478 | -0.0010875 | -0.0082522 | 0.032043 | 0.004578 | 0.082397 | 0.11902 | 0.16479 | 0.036621 | -0.10529 | -122.5479 | 0.009155 | -122.2504 | 0.84686 | 0.86975 | -122.0856 | -122.2824 | 122.1176 | 121.9757 | -0.75073 | 122.0856 | 122.2 | 0.22431 | -0.88348 | -0.004577 | -0.20142 | -0.068664 | -0.46692 | -0.16937 | 0.032044 | -0.045776 | 122.2458 | 122.113 | 122.1634 | -1.0208 | 122.9279 | 122.9507 | 122.0901 | -123.1979
777.875 | 123.2071 | -122.1909 | 0.81024 | -0.0085447 | 0.014121 | 0.00059389 | 0.0022623 | 0.050802 | -0.00050411 | -0.00098272 | -0.0084684 | -0.0017858 | 0.096756 | 0.071051 | -0.00044673 | -0.0091068 | 0.027466 | -0.018311 | -0.059509 | 0.07782 | 0.16937 | 0.027466 | -0.10529 | -122.7081 | -0.07782 | -122.3877 | 0.74616 | 0.7782 | -122.168 | -122.3648 | 122.2183 | 122.0856 | -0.64087 | 122.1725 | 122.2687 | 0.18311 | -0.78278 | 0.022888 | -0.17395 | -0.064087 | -0.51727 | -0.19684 | -0.022888 | -0.032044 | 122.3602 | 122.2183 | 122.1313 | -0.91553 | 122.937 | 122.9691 | 122.113 | -123.175
779.625 | 123.0698 | -122.1542 | 0.91553 | -0.0085447 | 0.012625 | -0.00026071 | 0.0054667 | 0.052083 | -0.0073401 | -0.0037597 | 0.0067901 | -0.0030676 | 0.096543 | 0.068915 | -0.0042919 | -0.005048 | 0.07782 | 0.09613 | -0.004578 | 0.1236 | 0.11902 | 0.068665 | -0.054932 | -122.5983 | -0.027466 | -122.2412 | 0.78278 | 0.81024 | -122.0764 | -122.287 | 122.2229 | 122.0993 | -0.79651 | 122.2504 | 122.2778 | 0.17853 | -0.83771 | 0.07782 | -0.13275 | -0.13275 | -0.44403 | -0.086975 | 0.045776 | -0.10528 | 122.2733 | 122.2321 | 122.1497 | -0.97046 | 122.937 | 122.9645 | 122.1268 | -123.2025
781.3906 | 123.0606 | -122.2641 | 0.79193 | 0.0067138 | 0.01583 | 0.0016619 | 0.010593 | 0.055074 | -0.0041357 | -0.0020507 | -0.00083936 | -0.001145 | 0.098465 | 0.071051 | -0.0040783 | -0.0080386 | 0.091553 | 0.10529 | 0.12817 | 0.16479 | 0.15106 | 0.045776 | -0.073242 | -122.7127 | 0.009155 | -122.3465 | 0.67749 | 0.72784 | -122.2183 | -122.3877 | 122.3099 | 122.1909 | -0.64087 | 122.3694 | 122.4289 | 0.23804 | -0.70038 | 0.045776 | -0.1236 | -0.11444 | -0.44861 | -0.082398 | 0.041198 | -0.064087 | 122.4152 | 122.3557 | 122.3923 | -0.86517 | 122.9416 | 122.9919 | 122.2733 | -123.1796
783.0781 | 123.1384 | -122.2092 | 0.78278 | -0.00091566 | 0.016257 | -0.0011151 | 0.0031167 | 0.05486 | 0.0020593 | -0.0020507 | -0.00083936 | -0.001145 | 0.098893 | 0.071265 | 0.0019033 | -0.010175 | 0.022888 | -0.018311 | 0.004578 | 0.091553 | 0.17395 | 0.032043 | -0.091553 | -122.7585 | -0.073242 | -122.4426 | 0.70496 | 0.737 | -122.2229 | -122.4472 | 122.2412 | 122.1176 | -0.60883 | 122.1909 | 122.3007 | 0.18311 | -0.75989 | -0.013733 | -0.23804 | -0.07782 | -0.54932 | -0.23346 | 0.004578 | -0.045776 | 122.3831 | 122.2321 | 122.2137 | -0.87433 | 122.9141 | 122.9462 | 122.1359 | -123.23
784.8281 | 123.0652 | -122.3511 | 0.73242 | -0.00091566 | 0.011984 | 0.0014483 | 0.0061075 | 0.05187 | -0.0052039 | -0.0044007 | -0.00083936 | -0.0032812 | 0.096756 | 0.068701 | -0.0051463 | -0.0067568 | 0.045776 | 0.082397 | -0.004578 | 0.11902 | 0.13275 | 0.059509 | -0.054932 | -122.7722 | -0.054932 | -122.3969 | 0.60883 | 0.65002 | -122.2641 | -122.4701 | 122.4106 | 122.2961 | -0.59967 | 122.4335 | 122.4701 | 0.17395 | -0.68665 | 0.086975 | -0.11902 | -0.1236 | -0.42114 | -0.045777 | 0.073242 | -0.082398 | 122.4838 | 122.3969 | 122.3465 | -0.78735 | 122.9599 | 123.0011 | 122.2961 | -123.2025
786.5156 | 123.056 | -122.3831 | 0.68665 | 0.0067138 | 0.010489 | 0.0020893 | 0.0016215 | 0.05486 | -0.0034949 | -0.0058959 | -0.00083936 | -0.0043494 | 0.095688 | 0.072119 | -0.0023693 | -0.0076114 | 0.10529 | 0.11444 | 0.004578 | 0.15106 | 0.13275 | 0.054932 | -0.050354 | -122.8134 | -0.032043 | -122.4518 | 0.54016 | 0.57678 | -122.319 | -122.5616 | 122.438 | 122.3328 | -0.5539 | 122.4976 | 122.5342 | 0.20142 | -0.58136 | 0.064087 | -0.17853 | -0.14648 | -0.4303 | -0.068664 | 0.10986 | -0.10986 | 122.5159 | 122.4884 | 122.3877 | -0.737 | 122.9233 | 122.9599 | 122.3511 | -123.2483
788.2656 | 123.0789 | -122.3282 | 0.70953 | -0.0085447 | 0.015616 | 0.00016669 | 0.0046121 | 0.051229 | -0.0024267 | -0.0069641 | -0.0084684 | -0.0030676 | 0.097611 | 0.07041 | -0.0019419 | -0.0067568 | 0.036621 | 0.032043 | 0.073242 | 0.086975 | 0.16022 | 0.036621 | -0.07782 | -122.8455 | -0.041199 | -122.4838 | 0.61798 | 0.67291 | -122.3419 | -122.5296 | 122.3648 | 122.2504 | -0.54932 | 122.3602 | 122.4152 | 0.16479 | -0.67291 | -0.013733 | -0.20142 | -0.091553 | -0.51727 | -0.15564 | 0.045776 | -0.036621 | 122.4884 | 122.3648 | 122.4014 | -0.78735 | 122.9462 | 123.0011 | 122.287 | -123.2391
790.0312 | 123.0469 | -122.2961 | 0.7782 | -0.016174 | 0.013693 | 0.00038029 | 0.0024759 | 0.05187 | -0.0043493 | -0.0063233 | 0.0067901 | -0.0034948 | 0.096329 | 0.069983 | -0.0027965 | -0.0088932 | 0.082397 | 0.064087 | -0.013733 | 0.13275 | 0.13275 | 0.064087 | -0.050354 | -122.7448 | -0.050354 | -122.3648 | 0.6134 | 0.66376 | -122.2412 | -122.4197 | 122.3602 | 122.2458 | -0.64545 | 122.3602 | 122.4289 | 0.18311 | -0.6958 | 0.054932 | -0.1236 | -0.16479 | -0.44861 | -0.068664 | 0.054932 | -0.11444 | 122.4289 | 122.3785 | 122.2824 | -0.82855 | 122.9095 | 122.9599 | 122.2458 | -123.1979
791.7031 | 123.0515 | -122.3053 | 0.74616 | -0.00091566 | 0.014548 | 0.0010211 | 0.0093119 | 0.053579 | -0.0041357 | -0.0052551 | -0.0084684 | 0.038802 | 0.056168 | 0.070196 | -0.0038647 | -0.0084658 | 0.13733 | 0.14648 | 0.14648 | 0.18768 | 0.1236 | 0.054932 | -0.041199 | -122.7173 | 0.082397 | -122.3465 | 0.58136 | 0.63629 | -122.2504 | -122.4655 | 122.3602 | 122.2641 | -0.62256 | 122.4518 | 122.493 | 0.22888 | -0.60883 | 0.054932 | -0.16022 | -0.1648 | -0.41199 | -0.041199 | 0.11902 | -0.10986 | 122.4289 | 122.4426 | 122.4518 | -0.78735 | 122.8867 | 122.9416 | 122.3877 | -123.2117
793.4531 | 123.0423 | -122.3923 | 0.67291 | -0.016174 | 0.013907 | 0.0020893 | 0.0018351 | 0.053579 | -0.0030677 | -0.0056823 | -0.0084684 | 0.040511 | 0.049759 | 0.070196 | 0.00062147 | -0.0091068 | 0.13733 | 0.1236 | 0.032043 | 0.15106 | 0.1236 | 0.068665 | -0.045776 | -122.7951 | -0.022888 | -122.4472 | 0.53101 | 0.55847 | -122.3419 | -122.5021 | 122.4609 | 122.3465 | -0.54932 | 122.5159 | 122.5433 | 0.19684 | -0.53558 | 0.050354 | -0.10986 | -0.14191 | -0.40283 | -0.054932 | 0.054931 | -0.11444 | 122.5159 | 122.5296 | 122.4243 | -0.71869 | 122.9233 | 122.9507 | 122.3694 | -123.175
795.2188 | 123.0515 | -122.3831 | 0.67291 | -0.00091566 | 0.013907 | -0.00026071 | 0.0088847 | 0.051443 | -0.0037085 | -0.0044007 | -0.016098 | 0.043075 | 0.053391 | 0.070196 | -0.0019419 | -0.0097476 | 0.091553 | 0.10986 | 0.13275 | 0.16022 | 0.15106 | 0.041199 | -0.054932 | -122.85 | 0.004578 | -122.525 | 0.52643 | 0.57678 | -122.374 | -122.5662 | 122.4243 | 122.3282 | -0.52185 | 122.493 | 122.5433 | 0.21515 | -0.58136 | 0.009156 | -0.1831 | -0.14648 | -0.46692 | -0.14191 | 0.041199 | -0.096131 | 122.5342 | 122.4747 | 122.5159 | -0.72784 | 122.9095 | 122.9599 | 122.3877 | -123.2391
796.9531 | 123.0377 | -122.3969 | 0.65918 | -0.016174 | 0.013693 | -0.00026071 | 0.0043985 | 0.05187 | -0.0030677 | -0.0054687 | -0.0084684 | 0.044357 | 0.050827 | 0.069342 | -0.0023693 | -0.0088932 | 0.13275 | 0.14648 | 0.15106 | 0.16937 | 0.13733 | 0.059509 | -0.073242 | -122.7951 | 0.073242 | -122.438 | 0.49896 | 0.56305 | -122.3419 | -122.5204 | 122.4564 | 122.3236 | -0.52185 | 122.5433 | 122.5662 | 0.24261 | -0.52643 | 0.054932 | -0.1236 | -0.16022 | -0.39825 | -0.041198 | 0.082398 | -0.096131 | 122.5342 | 122.5296 | 122.5479 | -0.73242 | 122.8958 | 122.9599 | 122.4701 | -123.1796
798.6406 | 123.0515 | -122.4335 | 0.64545 | -0.0085447 | 0.0079254 | 0.0010211 | 0.0014079 | 0.052083 | -0.0030677 | -0.0061095 | -0.0084684 | 0.039016 | 0.051896 | 0.069556 | -0.0027965 | -0.0069706 | 0.082397 | 0.064087 | -0.004578 | 0.12817 | 0.13275 | 0.054932 | -0.064087 | -122.8638 | -0.054932 | -122.4976 | 0.5127 | 0.52643 | -122.3511 | -122.5754 | 122.4884 | 122.3694 | -0.5127 | 122.4976 | 122.5616 | 0.19226 | -0.56305 | 0.082398 | -0.14191 | -0.13275 | -0.4303 | -0.064087 | 0.077819 | -0.11902 | 122.5662 | 122.5159 | 122.4289 | -0.70953 | 122.9462 | 122.9599 | 122.3785 | -123.2208
800.3906 | 123.0469 | -122.4106 | 0.67291 | -0.0085447 | 0.010489 | 0.0016619 | 0.0058939 | 0.052511 | -0.0045629 | -0.0041869 | -0.0084684 | 0.039443 | 0.051255 | 0.070837 | -0.0032237 | -0.007825 | 0.07782 | 0.059509 | -0.013733 | 0.12817 | 0.15106 | 0.073242 | -0.050354 | -122.8363 | -0.059509 | -122.4747 | 0.51727 | 0.55389 | -122.3694 | -122.5342 | 122.4838 | 122.3602 | -0.52185 | 122.4701 | 122.5388 | 0.17853 | -0.59509 | 0.041198 | -0.1236 | -0.15564 | -0.42572 | -0.064087 | 0.05951 | -0.11902 | 122.5616 | 122.4884 | 122.3969 | -0.72327 | 122.9279 | 122.9645 | 122.3511 | -123.2071
802.1406 | 123.1338 | -122.3923 | 0.6134 | -0.016174 | 0.017538 | -0.00090151 | 0.0035441 | 0.053579 | 0.0054773 | -0.0041869 | -0.00083936 | 0.045211 | 0.051468 | 0.071478 | 0.0023305 | -0.010816 | 0.09613 | 0.036621 | 0.064087 | 0.10986 | 0.16479 | 0.054932 | -0.073242 | -122.8409 | -0.022888 | -122.5662 | 0.54474 | 0.57678 | -122.3831 | -122.5845 | 122.4472 | 122.319 | -0.44861 | 122.4289 | 122.5021 | 0.18311 | -0.51727 | 0.009155 | -0.19226 | -0.068664 | -0.44861 | -0.17395 | 0.018311 | -0.036621 | 122.5571 | 122.4884 | 122.4564 | -0.68665 | 122.937 | 122.9691 | 122.3694 | -123.1979
803.8906 | 123.0469 | -122.3923 | 0.6546 | -0.00091566 | 0.015616 | 0.00038029 | 0.0054667 | 0.050588 | -0.0028539 | -0.0050415 | -0.0084684 | 0.040084 | 0.056809 | 0.071265 | -0.0027965 | -0.0084658 | 0.045776 | 0.009155 | 0.068665 | 0.091553 | 0.17853 | 0.027466 | -0.09613 | -122.8729 | -0.018311 | -122.5388 | 0.54932 | 0.59509 | -122.3831 | -122.5342 | 122.4197 | 122.2961 | -0.47607 | 122.4014 | 122.4838 | 0.18768 | -0.60883 | 0.009155 | -0.14191 | -0.10529 | -0.48065 | -0.14648 | -0.004577 | -0.059509 | 122.5708 | 122.438 | 122.4609 | -0.75073 | 122.9416 | 122.9874 | 122.374 | -123.1888
805.5938 | 123.175 | -122.3282 | 0.64087 | -0.0085447 | 0.014121 | -0.00026071 | 0.0024759 | 0.05187 | 0.00013669 | -0.0016235 | -0.0084684 | 0.0001368 | 0.097824 | 0.070196 | 0.00040787 | -0.0056888 | 0.032043 | -0.013733 | -0.045776 | 0.068665 | 0.16479 | 0.045776 | -0.09613 | -122.8455 | -0.086975 | -122.5296 | 0.5722 | 0.61798 | -122.3694 | -122.5342 | 122.374 | 122.2321 | -0.47607 | 122.3145 | 122.3969 | 0.16479 | -0.60883 | -0.041199 | -0.20599 | -0.068664 | -0.51727 | -0.20142 | 0.004578 | -0.022888 | 122.493 | 122.3602 | 122.2824 | -0.737 | 122.9004 | 122.9462 | 122.2412 | -123.175
807.3438 | 123.1384 | -122.3877 | 0.62714 | -0.016174 | 0.016684 | -0.00090151 | 0.0039713 | 0.053365 | 0.00056389 | -0.00055532 | -0.00083936 | 0.038802 | 0.060013 | 0.070837 | 0.00019427 | -0.0071842 | 0.086975 | -0.10986 | 0.064087 | 0.11902 | 0.14648 | 0.041199 | -0.091553 | -122.8455 | -0.009155 | -122.5754 | 0.53101 | 0.57678 | -122.3694 | -122.5845 | 122.4289 | 122.2961 | -0.48065 | 122.2778 | 122.5067 | 0.21057 | -0.54016 | 0.01831 | -0.19684 | -0.09613 | -0.45776 | -0.18768 | 0.009156 | -0.050354 | 122.5342 | 122.4747 | 122.4518 | -0.71869 | 122.9187 | 122.9645 | 122.3785 | -123.2117
809.0469 | 123.1888 | -122.3785 | 0.59509 | -0.0085447 | 0.014334 | -0.00068791 | 0.0043985 | 0.052511 | -0.0011451 | -0.0031189 | -0.00083936 | 0.040725 | 0.050827 | 0.070837 | -0.00066033 | -0.0067568 | 0.032043 | -0.018311 | -0.059509 | 0.073242 | 0.18768 | 0.036621 | -0.073242 | -122.8958 | -0.064087 | -122.5616 | 0.53558 | 0.58594 | -122.3969 | -122.5754 | 122.4152 | 122.3053 | -0.40741 | 122.3602 | 122.4518 | 0.14648 | -0.56305 | -0.018311 | -0.19684 | -0.05951 | -0.51727 | -0.18311 | 0.013732 | -0.009156 | 122.5662 | 122.4106 | 122.319 | -0.66834 | 122.9141 | 122.9645 | 122.3145 | -123.1705
810.7812 | 123.1613 | -122.4014 | 0.5722 | -0.00091566 | 0.018393 | -0.0015423 | 0.0058939 | 0.050588 | -0.00029051 | -0.0024779 | 0.0067901 | 0.044998 | 0.051896 | 0.070624 | -0.0021557 | -0.0093204 | 0.068665 | 0.050354 | 0.10071 | 0.12817 | 0.16937 | 0.036621 | -0.086975 | -122.8546 | 0.054932 | -122.5433 | 0.49896 | 0.53558 | -122.4289 | -122.58 | 122.438 | 122.3145 | -0.40283 | 122.4518 | 122.5296 | 0.21515 | -0.50354 | -0.027466 | -0.17853 | -0.073243 | -0.45319 | -0.14191 | 0.036621 | -0.036622 | 122.5708 | 122.4701 | 122.5021 | -0.65918 | 122.9004 | 122.937 | 122.4564 | -123.1522
812.5312 | 123.0698 | -122.406 | 0.63171 | -0.00091566 | 0.014975 | 0.0012347 | 0.0082437 | 0.05486 | -0.0039221 | -0.0037597 | -0.0084684 | 0.043716 | 0.053604 | 0.069983 | -0.0032237 | -0.0080386 | -0.013733 | -0.009155 | 0.054932 | 0.086975 | 0.16937 | 0.032043 | -0.10071 | -122.9233 | -0.018311 | -122.5616 | 0.52643 | 0.5722 | -122.4197 | -122.5891 | 122.438 | 122.3053 | -0.46234 | 122.3969 | 122.493 | 0.18768 | -0.64545 | -0.013733 | -0.1831 | -0.10529 | -0.51727 | -0.15564 | 0.027465 | -0.059509 | 122.5754 | 122.3923 | 122.4609 | -0.73242 | 122.9324 | 122.9782 | 122.3877 | -123.2208
814.2812 | 123.1522 | -122.3785 | 0.59967 | -0.0085447 | 0.015402 | -4.6912e-05 | 0.0073893 | 0.055715 | -0.0030677 | -0.0041869 | -0.00083936 | 0.04158 | 0.052964 | 0.067633 | -0.0027965 | -0.0086796 | 0.10529 | 0.11902 | 0.045776 | 0.17395 | 0.12817 | 0.073242 | -0.050354 | -122.7768 | 0.013733 | -122.4564 | 0.48065 | 0.5127 | -122.3785 | -122.5571 | 122.4518 | 122.3282 | -0.4715 | 122.4976 | 122.5525 | 0.2243 | -0.49438 | 0 | -0.17853 | -0.11902 | -0.39825 | -0.07782 | 0.10071 | -0.086975 | 122.5067 | 122.4838 | 122.4243 | -0.65002 | 122.8592 | 122.8912 | 122.3923 | -123.1567
816.0312 | 123.0789 | -122.4335 | 0.60425 | 0.0067138 | 0.012625 | 0.0023029 | 0.0052531 | 0.049947 | -0.0054175 | -0.0044007 | -0.00083936 | 0.020645 | 0.072617 | 0.069128 | -0.0038647 | -0.0073978 | 0.027466 | 0.045776 | -0.018311 | 0.12817 | 0.15564 | 0.07782 | -0.059509 | -122.8867 | -0.045776 | -122.5067 | 0.46692 | 0.50812 | -122.3648 | -122.5845 | 122.5113 | 122.374 | -0.44861 | 122.4792 | 122.5616 | 0.18768 | -0.57678 | 0.068665 | -0.15106 | -0.13733 | -0.45319 | -0.073242 | 0.07782 | -0.09613 | 122.5891 | 122.4609 | 122.4152 | -0.66376 | 122.9004 | 122.9416 | 122.3877 | -123.1888
817.7188 | 123.1155 | -122.406 | 0.59052 | -0.00091566 | 0.015616 | -0.00068791 | 0.0050393 | 0.05187 | 0.00056389 | -0.0031189 | -0.00083936 | 0.0071862 | 0.088425 | 0.069983 | -0.00087393 | -0.0088932 | 0.10071 | 0.050354 | 0.10529 | 0.13275 | 0.16022 | 0.059509 | -0.086975 | -122.8455 | 0.009155 | -122.5479 | 0.52185 | 0.54932 | -122.3831 | -122.5983 | 122.4655 | 122.319 | -0.4303 | 122.4564 | 122.5388 | 0.21973 | -0.48981 | 0.022888 | -0.19226 | -0.068664 | -0.43945 | -0.14191 | 0.050354 | -0.041199 | 122.5662 | 122.5067 | 122.5113 | -0.67749 | 122.9279 | 122.9553 | 122.4152 | -123.1888
819.4688 | 122.8867 | -121.6644 | 1.2314 | -0.0085447 | 0.012198 | 0.0025165 | 0.0052531 | 0.051015 | -0.0073401 | -0.0046143 | 0.0067901 | 1.8431 | 1.6156 | 0.067633 | 3.3562 | -0.0071842 | 0.064087 | 0.059509 | -0.013733 | 0.12817 | 0.12817 | 0.073242 | -0.054932 | -121.8475 | -0.022888 | -0.55847 | 0.8606 | 0.86975 | -121.3486 | -121.5225 | 121.7377 | 121.6095 | -1.1032 | 121.7239 | 121.7926 | 0.18311 | -1.1673 | 0.31586 | 0.14191 | -0.37079 | -0.1831 | 121.106 | 120.9641 | -0.36163 | 121.7926 | 121.7285 | 121.6507 | -1.2863 | 122.525 | 122.5342 | 121.6415 | -122.7539
821.2188 | 122.7036 | -121.4172 | 1.2589 | -0.016174 | 0.013907 | 0.0035847 | 0.0063211 | 0.053152 | -0.0047765 | -0.0063233 | -0.00083936 | 1.8905 | 1.788 | 0.069983 | 3.5767 | -0.0088932 | 0.11444 | 0.15564 | 0.12817 | 0.17853 | 0.16479 | 0.068665 | -0.059509 | -121.5408 | 0.10071 | -0.21515 | 0.8606 | 0.8606 | -121.1151 | -121.3165 | 121.4859 | 121.3577 | -1.0941 | 121.5729 | 121.5958 | 0.23804 | -1.1444 | 0.30212 | 0.10071 | -0.39825 | -0.1236 | 121.2021 | 121.1014 | -0.39825 | 121.582 | 121.5317 | 121.5454 | -1.3184 | 122.2778 | 122.2778 | 121.5179 | -122.5754
822.9688 | 122.5983 | -121.3623 | 1.2543 | 0.0067138 | 0.01348 | -0.00047431 | 0.0082437 | 0.052724 | -0.0028539 | -0.0050415 | -0.00083936 | 1.908 | 1.7647 | 0.069556 | 3.5718 | -0.009534 | 0.12817 | 0.13275 | 0.15564 | 0.1831 | 0.12817 | 0.07782 | -0.059509 | -121.4447 | 0.10071 | -0.24261 | 0.8606 | 0.8606 | -121.051 | -121.2479 | 121.4401 | 121.3028 | -1.1261 | 121.4951 | 121.5454 | 0.24261 | -1.1261 | 0.31128 | 0.11444 | -0.39368 | -0.082397 | 121.1197 | 121.0052 | -0.39368 | 121.4905 | 121.4905 | 121.5179 | -1.3138 | 122.2229 | 122.2229 | 121.463 | -122.5021
824.7344 | 122.5616 | -121.3074 | 1.268 | 0.0067138 | 0.012625 | 0.00038029 | 0.0014079 | 0.051443 | -0.0028539 | -0.0037597 | -0.0084684 | 1.9033 | 1.753 | 0.070837 | 3.5589 | -0.0080386 | 0.12817 | 0.1236 | 0.022888 | 0.16022 | 0.1236 | 0.07782 | -0.041199 | -121.4127 | -0.009155 | -0.9201 | 0.90179 | 0.90179 | -120.9915 | -121.1609 | 121.3852 | 121.2662 | -1.1444 | 121.431 | 121.4676 | 0.20142 | -1.1398 | 0.31586 | 0.14648 | -0.36621 | -0.10529 | 120.3873 | 120.2408 | -0.36621 | 121.431 | 121.4355 | 121.3303 | -1.3092 | 122.2092 | 122.2092 | 121.2982 | -122.4289
826.4219 | 122.5296 | -121.1975 | 1.3138 | -0.00091566 | 0.011771 | 0.00059389 | 0.0052531 | 0.050588 | -0.0043493 | -0.0046143 | 0.0067901 | 2.1793 | 1.4874 | 0.069769 | 3.5641 | -0.007825 | 0.064087 | 0.068665 | -0.022888 | 0.11902 | 0.14191 | 0.068665 | -0.059509 | -121.3623 | -0.045776 | -0.29755 | 0.92926 | 0.94299 | -120.9045 | -121.0876 | 121.2662 | 121.138 | -1.1719 | 121.2662 | 121.3165 | 0.17853 | -1.2497 | 0.29297 | 0.10986 | -0.38452 | -0.1648 | 120.9 | 120.7901 | -0.37079 | 121.3394 | 121.2616 | 121.1746 | -1.3733 | 122.1268 | 122.1405 | 121.1517 | -122.4014
828.1719 | 122.5983 | -121.1929 | 1.2131 | -0.0085447 | 0.014761 | -0.0023969 | 0.0050393 | 0.052511 | 0.0014185 | -0.0056823 | -0.00083936 | 1.8918 | 1.7803 | 0.071905 | 3.5681 | -0.0097476 | 0.041199 | -0.004578 | 0.059509 | 0.10986 | 0.18768 | 0.036621 | -0.10986 | -121.4218 | -0.004578 | -0.39368 | 0.90637 | 0.92468 | -120.9778 | -121.1151 | 121.2296 | 121.0831 | -1.0254 | 121.1884 | 121.3028 | 0.21973 | -1.1719 | 0.21515 | 0.07782 | -0.3067 | -0.22888 | 120.7993 | 120.7214 | -0.28839 | 121.3806 | 121.2341 | 121.2524 | -1.3229 | 122.0993 | 122.1176 | 121.1884 | -122.3282
829.9219 | 122.5113 | -121.225 | 1.2314 | -0.00091566 | 0.0083526 | 0.0074299 | 0.0024759 | 0.05422 | -0.0047765 | -0.0041869 | -0.00083936 | 1.8627 | 1.7989 | 0.067847 | 3.5604 | -0.0063296 | 0.09613 | 0.10071 | 0.036621 | 0.15564 | 0.15106 | 0.07782 | -0.059509 | -121.3531 | 0.027466 | -0.31586 | 0.86517 | 0.85144 | -120.9229 | -121.1243 | 121.3028 | 121.1655 | -1.0803 | 121.3257 | 121.3806 | 0.21515 | -1.1353 | 0.30212 | 0.10071 | -0.36621 | -0.12817 | 120.9091 | 120.8084 | -0.37994 | 121.376 | 121.3211 | 121.2616 | -1.2909 | 122.0901 | 122.0764 | 121.2524 | -122.3557
831.6094 | 122.4426 | -121.1929 | 1.2405 | -0.00091566 | 0.014121 | 0.0014483 | 0.0086709 | 0.052938 | -0.0049903 | -0.0037597 | -0.0084684 | 1.8676 | 1.8015 | 0.07041 | 3.5604 | -0.010816 | 0.068665 | 0.073242 | 0.10529 | 0.14191 | 0.15564 | 0.045776 | -0.064087 | -121.3852 | 0 | -0.36163 | 0.89722 | 0.87891 | -120.9274 | -121.0876 | 121.2387 | 121.1288 | -1.0849 | 121.2662 | 121.3348 | 0.20599 | -1.1719 | 0.2655 | 0.10529 | -0.34332 | -0.19226 | 120.8313 | 120.726 | -0.36163 | 121.3486 | 121.2616 | 121.2982 | -1.3046 | 122.0901 | 122.0718 | 121.1929 | -122.3282
833.3594 | 122.4014 | -121.17 | 1.2405 | -0.00091566 | 0.013266 | 0.0025165 | 0.0063211 | 0.052724 | -0.0043493 | -0.0044007 | 0.0067901 | 1.8764 | 1.7872 | 0.070624 | 3.5617 | -0.0080386 | 0.13275 | 0.15564 | 0.13733 | 0.16022 | 0.12817 | 0.082397 | -0.059509 | -121.2845 | 0.068665 | -0.22888 | 0.86975 | 0.84686 | -120.845 | -121.0373 | 121.2524 | 121.1105 | -1.1124 | 121.3257 | 121.3303 | 0.21973 | -1.1078 | 0.32501 | 0.13275 | -0.37079 | -0.11444 | 120.9412 | 120.8084 | -0.39368 | 121.2982 | 121.3028 | 121.3074 | -1.3 | 122.0398 | 122.0169 | 121.2387 | -122.2778
835.125 | 122.438 | -121.2479 | 1.0941 | -0.00091566 | 0.013052 | 0.0016619 | 0.0078165 | 0.054647 | -0.0030677 | -0.0063233 | 0.01442 | 2.2709 | 1.389 | 0.069128 | 3.5542 | -0.0082522 | 0.15106 | 0.15564 | 0.1236 | 0.1831 | 0.14648 | 0.07782 | -0.054932 | -121.3531 | 0.068665 | -0.41199 | 0.71411 | 0.75073 | -120.9412 | -121.1334 | 121.3257 | 121.1929 | -0.94757 | 121.4035 | 121.431 | 0.23804 | -0.94299 | 0.3067 | 0.11444 | -0.37994 | -0.10528 | 120.8359 | 120.7214 | -0.34332 | 121.3943 | 121.3989 | 121.3715 | -1.149 | 121.962 | 121.9986 | 121.3165 | -122.2275
836.875 | 122.3557 | -121.1884 | 1.1902 | -0.00091566 | 0.01113 | 0.0033709 | 0.00076686 | 0.051443 | -0.0026403 | -0.0048279 | -0.016098 | 1.921 | 1.7404 | 0.06806 | 3.5555 | -0.0086796 | 0.13275 | 0.11902 | 0.009155 | 0.14191 | 0.14191 | 0.068665 | -0.045776 | -121.3074 | -0.041199 | -0.32501 | 0.79193 | 0.81482 | -120.8725 | -121.0602 | 121.257 | 121.1426 | -1.0483 | 121.3074 | 121.3303 | 0.18768 | -1.0574 | 0.31586 | 0.12817 | -0.39825 | -0.11902 | 120.8633 | 120.7352 | -0.37537 | 121.3303 | 121.3211 | 121.1975 | -1.236 | 121.9803 | 122.0032 | 121.1472 | -122.2504
838.5625 | 122.4335 | -121.1334 | 1.149 | 0.0067138 | 0.01348 | -0.0019695 | 0.0052531 | 0.053152 | 0.0041955 | -0.0024779 | -0.0084684 | 1.9249 | 1.7412 | 0.07276 | 3.5587 | -0.0093204 | 0.036621 | -0.041199 | -0.027466 | 0.091553 | 0.17395 | 0.059509 | -0.07782 | -121.3394 | -0.091553 | -0.46692 | 0.83313 | 0.83771 | -120.8908 | -121.0556 | 121.1929 | 121.0556 | -0.97504 | 121.0922 | 121.225 | 0.16937 | -1.1124 | 0.24261 | 0.07782 | -0.31586 | -0.20599 | 120.6665 | 120.5887 | -0.31128 | 121.3074 | 121.17 | 121.106 | -1.2268 | 121.9666 | 121.9711 | 121.0419 | -122.2046
840.3125 | 122.3328 | -121.0831 | 1.1856 | -0.0085447 | 0.01583 | -0.00026071 | 0.0069621 | 0.055501 | -0.0011451 | -0.0020507 | -0.00083936 | 1.8693 | 1.7919 | 0.069556 | 3.5521 | -0.007825 | 0.036621 | 0.013733 | 0.059509 | 0.073242 | 0.16479 | 0.018311 | -0.11444 | -121.3165 | -0.027466 | -0.41199 | 0.85144 | 0.8606 | -120.8359 | -121.019 | 121.1014 | 120.9686 | -1.0208 | 121.0968 | 121.1563 | 0.18768 | -1.149 | 0.24719 | 0.064087 | -0.33417 | -0.23346 | 120.6711 | 120.607 | -0.32501 | 121.2479 | 121.1197 | 121.1426 | -1.3 | 121.9345 | 121.9437 | 121.0556 | -122.2046
841.9844 | 122.3602 | -121.0373 | 1.1948 | -0.0085447 | 0.012412 | 0.0014483 | 0.0014079 | 0.053365 | -0.0028539 | -0.0056823 | -0.0084684 | 1.9512 | 1.7047 | 0.070196 | 3.5517 | -0.0073978 | 0.1236 | 0.1236 | 0.16937 | 0.17853 | 0.10986 | 0.091553 | -0.059509 | -121.1655 | 0.027466 | -0.27466 | 0.81482 | 0.81482 | -120.7764 | -120.9595 | 121.1288 | 120.9778 | -1.0849 | 121.1609 | 121.2158 | 0.23804 | -1.0712 | 0.26093 | 0.077819 | -0.37994 | -0.12817 | 120.7626 | 120.6848 | -0.37994 | 121.1472 | 121.1609 | 121.2067 | -1.2543 | 121.8521 | 121.8521 | 121.0648 | -122.1542
843.7344 | 122.287 | -121.0876 | 1.1581 | -0.0085447 | 0.014121 | 0.0016619 | 0.0041849 | 0.055715 | -0.0034949 | -0.0026917 | 0.0067901 | 2.0302 | 1.6233 | 0.068274 | 3.5498 | -0.0086796 | 0.13275 | 0.1236 | 0.17853 | 0.16937 | 0.13275 | 0.073242 | -0.036621 | -121.2021 | 0.022888 | -0.33417 | 0.78278 | 0.78735 | -120.7764 | -120.9595 | 121.1609 | 121.051 | -1.0254 | 121.2112 | 121.257 | 0.20599 | -1.0254 | 0.31128 | 0.12817 | -0.37537 | -0.11444 | 120.7535 | 120.6253 | -0.37079 | 121.2204 | 121.2204 | 121.2662 | -1.1948 | 121.8704 | 121.875 | 121.1105 | -122.1176
845.5 | 122.2275 | -121.0556 | 1.1673 | -0.00091566 | 0.013693 | 0.0018757 | 0.0052531 | 0.052938 | -0.0049903 | -0.0044007 | -0.00083936 | 2.0533 | 1.5932 | 0.069769 | 3.5459 | -0.0082522 | 0.086975 | 0.054932 | 0.11902 | 0.12817 | 0.14191 | 0.068665 | -0.041199 | -121.2524 | -0.050354 | -0.40283 | 0.76446 | 0.81024 | -120.7626 | -120.9778 | 121.1243 | 121.0144 | -1.0254 | 121.1105 | 121.1838 | 0.16937 | -1.0803 | 0.29297 | 0.07782 | -0.40283 | -0.19684 | 120.6528 | 120.575 | -0.35706 | 121.1975 | 121.1426 | 121.1746 | -1.2085 | 121.8201 | 121.8658 | 121.0052 | -122.1451
847.25 | 122.3373 | -120.9778 | 1.1261 | -0.00091566 | 0.017966 | 0.0025165 | 0.0035441 | 0.053365 | 0.0029139 | -0.0018371 | -0.0084684 | 1.9189 | 1.7359 | 0.07041 | 3.5472 | -0.0097476 | 0.064087 | 0.004578 | 0.032043 | 0.10986 | 0.16479 | 0.027466 | -0.10071 | -121.1929 | 0.018311 | -0.40283 | 0.84228 | 0.82855 | -120.7535 | -120.9503 | 121.0052 | 120.8771 | -0.9613 | 120.9824 | 121.0876 | 0.21057 | -1.062 | 0.2243 | 0.027466 | -0.28381 | -0.21515 | 120.575 | 120.5475 | -0.29755 | 121.1426 | 121.0419 | 121.0098 | -1.2268 | 121.8201 | 121.8063 | 120.9961 | -122.0764
848.9844 | 122.2504 | -120.9915 | 1.1673 | 0.0067138 | 0.017538 | 0.0042255 | 0.0084573 | 0.053579 | -0.00050411 | -0.0037597 | -0.00083936 | 1.8828 | 1.7724 | 0.070196 | 3.544 | -0.0086796 | 0.013733 | -0.004578 | 0.027466 | 0.073242 | 0.16937 | 0.018311 | -0.10071 | -121.2204 | -0.018311 | -0.4303 | 0.82855 | 0.83313 | -120.7809 | -120.9183 | 121.0098 | 120.8908 | -0.99792 | 120.9869 | 121.0648 | 0.17395 | -1.1536 | 0.21057 | 0.073242 | -0.33875 | -0.22888 | 120.5612 | 120.488 | -0.33417 | 121.1609 | 121.0052 | 121.019 | -1.268 | 121.8201 | 121.8246 | 120.9732 | -122.0856
850.6719 | 122.2321 | -120.9732 | 1.1307 | -0.00091566 | 0.014975 | -0.00047431 | 0.0031167 | 0.05187 | 0.0027003 | -0.0018371 | 0.0067901 | 1.8792 | 1.7733 | 0.069769 | 3.5457 | -0.0073978 | 0.041199 | -0.013733 | 0.022888 | 0.10071 | 0.17395 | 0.041199 | -0.09613 | -121.2112 | -0.054932 | -0.46692 | 0.80566 | 0.82398 | -120.7352 | -120.932 | 121.0144 | 120.8771 | -0.95673 | 120.9595 | 121.0739 | 0.19684 | -1.0895 | 0.23804 | 0.041199 | -0.32501 | -0.23804 | 120.5063 | 120.4651 | -0.3067 | 121.1472 | 121.0144 | 120.9961 | -1.2268 | 121.7789 | 121.7972 | 120.9183 | -122.0627
852.4219 | 122.1176 | -120.9549 | 1.1673 | -0.00091566 | 0.014334 | 0.0018757 | 0.0082437 | 0.052511 | -0.0037085 | -0.0035461 | -0.00083936 | 1.8851 | 1.7624 | 0.069128 | 3.5386 | -0.007825 | 0.091553 | 0.13733 | 0.15564 | 0.17395 | 0.1236 | 0.064087 | -0.050354 | -121.106 | 0.068665 | -0.32501 | 0.80109 | 0.79651 | -120.6894 | -120.8679 | 121.019 | 120.9045 | -1.0437 | 121.0922 | 121.1288 | 0.2243 | -1.0757 | 0.2655 | 0.086975 | -0.36621 | -0.15106 | 120.6299 | 120.5429 | -0.37079 | 121.0785 | 121.0464 | 121.1105 | -1.2177 | 121.756 | 121.7514 | 121.0236 | -122.0352
854.1875 | 122.1313 | -121.0281 | 1.1124 | 0.0067138 | 0.013907 | -0.0011151 | 0.0054667 | 0.051443 | -0.0041357 | -0.0039733 | -0.016098 | 2.1097 | 1.5332 | 0.068701 | 3.5365 | -0.0082522 | 0.10986 | 0.12817 | 0.16479 | 0.16022 | 0.10986 | 0.073242 | -0.054932 | -121.1334 | -0.009155 | -0.4303 | 0.73242 | 0.71869 | -120.7123 | -120.9091 | 121.1014 | 120.9732 | -1.0025 | 121.1563 | 121.1884 | 0.21515 | -1.0025 | 0.31586 | 0.11902 | -0.37994 | -0.10529 | 120.5978 | 120.4788 | -0.39368 | 121.138 | 121.138 | 121.1929 | -1.1673 | 121.7606 | 121.7468 | 121.019 | -122.0215
855.9375 | 122.2458 | -120.9137 | 1.1078 | -0.0085447 | 0.017966 | -0.00047431 | 0.0039713 | 0.052297 | 0.0027003 | -0.0014099 | 0.0067901 | 1.9612 | 1.6859 | 0.070624 | 3.5389 | -0.011457 | 0.059509 | 0.045776 | 0.068665 | 0.11902 | 0.16479 | 0.050354 | -0.09613 | -121.0876 | 0.036621 | -0.42572 | 0.78278 | 0.7782 | -120.7031 | -120.8771 | 120.9641 | 120.8176 | -0.94299 | 120.9595 | 121.0327 | 0.21515 | -1.0483 | 0.21057 | 0.036621 | -0.32501 | -0.17395 | 120.488 | 120.4514 | -0.32959 | 121.0785 | 120.9732 | 120.9824 | -1.2039 | 121.6965 | 121.6919 | 120.9503 | -121.9849
857.6875 | 122.1313 | -120.9091 | 1.0895 | -0.0085447 | 0.015616 | -4.6912e-05 | 0.0069621 | 0.052724 | -0.0015723 | -0.0031189 | -0.0084684 | 1.9285 | 1.7156 | 0.069342 | 3.5367 | -0.010175 | -0.004578 | 0 | 0.018311 | 0.091553 | 0.18768 | 0.036621 | -0.091553 | -121.1563 | -0.022888 | -0.53558 | 0.78735 | 0.79193 | -120.6757 | -120.8817 | 120.9457 | 120.8176 | -0.90179 | 120.9091 | 121.0007 | 0.18311 | -1.0941 | 0.23346 | 0.027466 | -0.30212 | -0.24719 | 120.3735 | 120.3461 | -0.29755 | 121.0968 | 120.9045 | 120.9274 | -1.181 | 121.6965 | 121.7011 | 120.8862 | -121.9711
859.375 | 122.0993 | -120.9229 | 1.1307 | -0.0085447 | 0.013266 | 0.0025165 | 0.0048257 | 0.052297 | -0.0081945 | -0.0063233 | -0.0084684 | 1.9499 | 1.6882 | 0.066992 | 3.5314 | -0.007825 | 0.068665 | 0.11444 | 0.13733 | 0.15564 | 0.1236 | 0.054932 | -0.050354 | -121.0464 | 0.027466 | -0.33417 | 0.74616 | 0.76446 | -120.6253 | -120.8038 | 120.9778 | 120.8725 | -1.0071 | 121.0373 | 121.0785 | 0.20599 | -1.062 | 0.29755 | 0.11902 | -0.38452 | -0.1236 | 120.5887 | 120.4697 | -0.36621 | 121.0464 | 120.9915 | 121.0602 | -1.181 | 121.669 | 121.6873 | 120.9503 | -121.9345
861.0781 | 122.0764 | -120.8679 | 1.1261 | -0.00091566 | 0.011771 | 0.0018757 | 0.0037577 | 0.055074 | -0.0039221 | -0.0061095 | -0.00083936 | 1.877 | 1.7607 | 0.067847 | 3.5327 | -0.0086796 | 0.10986 | 0.13275 | 0.16022 | 0.16937 | 0.13733 | 0.073242 | -0.050354 | -120.9915 | 0.054932 | -0.32044 | 0.76446 | 0.76904 | -120.6024 | -120.7489 | 120.9412 | 120.8176 | -0.98877 | 121.0007 | 121.0373 | 0.21973 | -1.0162 | 0.2655 | 0.11902 | -0.36163 | -0.1236 | 120.5475 | 120.4285 | -0.35706 | 121.0052 | 120.9778 | 121.0281 | -1.1765 | 121.6324 | 121.637 | 120.9229 | -121.875
862.8125 | 122.0169 | -120.8908 | 1.1444 | 0.0067138 | 0.010275 | 0.00059389 | 0.0029031 | 0.052297 | -0.0041357 | -0.0048279 | -0.00083936 | 1.9033 | 1.7305 | 0.068915 | 3.5307 | -0.0099612 | 0.10071 | 0.10986 | 0.14191 | 0.15564 | 0.1236 | 0.073242 | -0.050354 | -121.0098 | -0.054932 | -0.43945 | 0.77362 | 0.74158 | -120.5704 | -120.7443 | 120.9641 | 120.8405 | -1.0208 | 121.0007 | 121.0464 | 0.20599 | -1.0437 | 0.32043 | 0.14648 | -0.37079 | -0.11902 | 120.4514 | 120.3049 | -0.40283 | 121.0144 | 120.9915 | 121.0327 | -1.1948 | 121.6644 | 121.6324 | 120.8359 | -121.8887
864.5469 | 122.0078 | -120.8725 | 1.1307 | 0.0067138 | 0.013907 | 0.0014483 | 0.0046121 | 0.056142 | -0.0049903 | -0.0069641 | -0.00083936 | 1.8877 | 1.7478 | 0.066138 | 3.529 | -0.0082522 | 0.13275 | 0.15106 | 0.17853 | 0.17395 | 0.14191 | 0.07782 | -0.059509 | -120.9412 | 0.086975 | -0.35248 | 0.75531 | 0.76446 | -120.5566 | -120.7214 | 120.9503 | 120.813 | -0.98877 | 121.0236 | 121.0464 | 0.23346 | -0.99792 | 0.31586 | 0.15106 | -0.37537 | -0.068664 | 120.52 | 120.369 | -0.36621 | 121.0144 | 121.0052 | 121.051 | -1.1902 | 121.6278 | 121.637 | 120.9595 | -121.8521
866.2969 | 121.9757 | -120.8633 | 1.1307 | -0.00091566 | 0.010703 | -0.0015423 | 0.0043985 | 0.053792 | -0.0032813 | -0.0024779 | 0.0067901 | 1.8869 | 1.7474 | 0.067206 | 3.5292 | -0.0099612 | 0.13275 | 0.1236 | 0.17853 | 0.16937 | 0.11902 | 0.059509 | -0.050354 | -120.9457 | -0.004578 | -0.37079 | 0.75073 | 0.75531 | -120.5246 | -120.7306 | 120.9229 | 120.813 | -1.0117 | 120.9869 | 121.0327 | 0.21973 | -0.99792 | 0.33875 | 0.13275 | -0.37994 | -0.082398 | 120.4926 | 120.3598 | -0.37537 | 120.9824 | 120.9961 | 121.0419 | -1.181 | 121.6141 | 121.6187 | 120.8588 | -121.8613
868.0312 | 121.9757 | -120.7947 | 1.1261 | -0.00091566 | 0.0092072 | 0.0023029 | 0.0061075 | 0.052297 | -0.0045629 | -0.0063233 | -0.0084684 | 1.851 | 1.7778 | 0.06806 | 3.5271 | -0.010175 | 0.050354 | 0.054932 | 0.09613 | 0.13275 | 0.13275 | 0.059509 | -0.054932 | -120.9686 | -0.054932 | -0.42572 | 0.74616 | 0.75073 | -120.52 | -120.7352 | 120.8542 | 120.7397 | -0.99335 | 120.8496 | 120.9274 | 0.18768 | -1.0757 | 0.27466 | 0.05951 | -0.37994 | -0.17395 | 120.369 | 120.3094 | -0.37537 | 120.9274 | 120.845 | 120.8908 | -1.181 | 121.5408 | 121.5454 | 120.7397 | -121.8613
869.7812 | 121.9162 | -120.8084 | 1.1398 | 0.0067138 | 0.013693 | 0.0012347 | 0.0076029 | 0.052297 | -0.0028539 | -0.0056823 | -0.00083936 | 1.8499 | 1.7848 | 0.071051 | 3.525 | -0.0099612 | 0.13275 | 0.13275 | 0.16479 | 0.1831 | 0.1236 | 0.064087 | -0.041199 | -120.8771 | 0.059509 | -0.36163 | 0.77362 | 0.76446 | -120.4971 | -120.6757 | 120.8725 | 120.7672 | -1.0162 | 120.9412 | 120.9915 | 0.2243 | -1.0071 | 0.31128 | 0.13275 | -0.36621 | -0.068664 | 120.4468 | 120.314 | -0.37537 | 120.932 | 120.9412 | 120.9732 | -1.181 | 121.582 | 121.5729 | 120.8679 | -121.8155
871.4688 | 121.9666 | -120.7214 | 1.1765 | -0.016174 | 0.013052 | 0.0027301 | 0.0067483 | 0.057638 | -0.0047765 | -0.0048279 | -0.016098 | 1.8448 | 1.7852 | 0.070624 | 3.5243 | -0.011243 | 0.13275 | 0.13275 | 0.16022 | 0.17853 | 0.1236 | 0.064087 | -0.054932 | -120.7947 | 0.041199 | -0.25635 | 0.82398 | 0.81482 | -120.401 | -120.5933 | 120.7855 | 120.6665 | -1.0529 | 120.8542 | 120.9 | 0.23346 | -1.0437 | 0.32044 | 0.12817 | -0.35248 | -0.073242 | 120.4651 | 120.3369 | -0.36163 | 120.845 | 120.8542 | 120.8817 | -1.2314 | 121.5454 | 121.5363 | 120.7626 | -121.7697
873.2188 | 122.0215 | -120.6802 | 1.1124 | -0.0085447 | 0.014334 | 0.0027301 | 0.0033305 | 0.052511 | 0.0044091 | -0.0024779 | -0.00083936 | 1.8715 | 1.759 | 0.070624 | 3.5271 | -0.0088932 | 0.068665 | 0.022888 | 0.045776 | 0.11902 | 0.16937 | 0.041199 | -0.09613 | -120.8542 | 0.018311 | -0.40741 | 0.8194 | 0.80109 | -120.4422 | -120.6482 | 120.7214 | 120.5841 | -0.94299 | 120.7031 | 120.7993 | 0.21515 | -1.0437 | 0.23804 | 0.032044 | -0.29297 | -0.17395 | 120.2728 | 120.2408 | -0.31128 | 120.8496 | 120.7489 | 120.726 | -1.2085 | 121.4996 | 121.4813 | 120.6985 | -121.7606
874.9688 | 121.8704 | -120.607 | 1.2863 | -0.0085447 | 0.010703 | 0.0010211 | 0.0054667 | 0.051443 | -0.0028539 | -0.0024779 | -0.00083936 | 1.8396 | 1.7893 | 0.069769 | 3.5216 | -0.0076114 | 0.10986 | 0.12817 | 0.14648 | 0.14191 | 0.1236 | 0.064087 | -0.059509 | -120.7123 | -0.036621 | -0.2243 | 0.88806 | 0.88806 | -120.3232 | -120.4697 | 120.6711 | 120.5475 | -1.1627 | 120.7352 | 120.7489 | 0.20142 | -1.1765 | 0.28381 | 0.13733 | -0.39825 | -0.10529 | 120.3827 | 120.2454 | -0.39825 | 120.7306 | 120.7169 | 120.7535 | -1.3458 | 121.4951 | 121.4951 | 120.5704 | -121.756
876.6406 | 121.9391 | -120.5978 | 1.2039 | -0.00091566 | 0.018607 | -0.0019695 | 0.0071757 | 0.052724 | 0.0024865 | -0.00098272 | -0.00083936 | 1.8478 | 1.7842 | 0.070624 | 3.5263 | -0.0084658 | 0.11444 | 0.073242 | 0.086975 | 0.1236 | 0.14648 | 0.059509 | -0.073242 | -120.7306 | 0.032043 | -0.31128 | 0.86975 | 0.86517 | -120.3644 | -120.5292 | 120.6573 | 120.5246 | -1.0574 | 120.6711 | 120.7214 | 0.19684 | -1.0895 | 0.23346 | 0.068664 | -0.33417 | -0.13275 | 120.2866 | 120.2179 | -0.33875 | 120.7443 | 120.7123 | 120.6848 | -1.2772 | 121.4676 | 121.463 | 120.6299 | -121.7331
878.3906 | 121.9666 | -120.5429 | 1.181 | -0.0085447 | 0.012839 | -0.0019695 | 0.0061075 | 0.053365 | 0.0012049 | 8.548e-05 | 0.0067901 | 1.8437 | 1.7863 | 0.072333 | 3.5218 | -0.0086796 | 0.041199 | 0.018311 | 0.027466 | 0.07782 | 0.16022 | 0.045776 | -0.073242 | -120.7581 | -0.068665 | -0.34332 | 0.85144 | 0.85144 | -120.3552 | -120.5383 | 120.5887 | 120.4697 | -1.0208 | 120.5612 | 120.6207 | 0.15106 | -1.1398 | 0.18768 | 0.004578 | -0.32959 | -0.21515 | 120.1996 | 120.195 | -0.32959 | 120.7031 | 120.5841 | 120.5704 | -1.2543 | 121.3943 | 121.3943 | 120.4742 | -121.7194
880.1562 | 121.875 | -120.5338 | 1.2222 | -0.016174 | 0.015189 | 0.00038029 | 0.0037577 | 0.054647 | 0.00099129 | -0.00098272 | 0.0067901 | 1.8416 | 1.7859 | 0.071478 | 3.5213 | -0.0088932 | 0.027466 | -0.013733 | 0.022888 | 0.09613 | 0.17395 | 0.041199 | -0.091553 | -120.726 | -0.07782 | -0.37537 | 0.90179 | 0.89722 | -120.2866 | -120.4971 | 120.575 | 120.4422 | -1.0483 | 120.52 | 120.6299 | 0.18768 | -1.1948 | 0.24719 | 0.036621 | -0.32044 | -0.19226 | 120.1584 | 120.1218 | -0.32501 | 120.7077 | 120.5612 | 120.5566 | -1.3138 | 121.4355 | 121.431 | 120.4559 | -121.7194
881.9062 | 121.8018 | -120.5704 | 1.1993 | -0.00091566 | 0.0096344 | 0.0016619 | 0.0029031 | 0.051015 | -0.0054175 | -0.0033325 | 0.0067901 | 1.8251 | 1.7966 | 0.068487 | 3.5169 | -0.0071842 | 0.1236 | 0.15564 | 0.17853 | 0.16937 | 0.12817 | 0.07782 | -0.041199 | -120.6528 | 0.068665 | -0.22888 | 0.8194 | 0.80566 | -120.2911 | -120.4559 | 120.6482 | 120.5292 | -1.0712 | 120.726 | 120.7397 | 0.21057 | -1.0757 | 0.27924 | 0.11444 | -0.37994 | -0.082397 | 120.3415 | 120.2271 | -0.39368 | 120.6985 | 120.694 | 120.7489 | -1.2405 | 121.3898 | 121.376 | 120.639 | -121.6553
883.5781 | 121.8475 | -120.575 | 1.1581 | -0.0085447 | 0.017111 | -0.0015423 | 0.0067483 | 0.052297 | 0.0024865 | -0.0031189 | -0.00083936 | 1.8251 | 1.8023 | 0.070837 | 3.5169 | -0.0091068 | 0.054932 | -0.013733 | 0.022888 | 0.11444 | 0.1831 | 0.054932 | -0.082397 | -120.7306 | -0.050354 | -0.41657 | 0.81482 | 0.84228 | -120.3278 | -120.5154 | 120.6299 | 120.4926 | -0.97504 | 120.5612 | 120.6894 | 0.19684 | -1.1032 | 0.24719 | 0.059509 | -0.34332 | -0.15564 | 120.1584 | 120.0989 | -0.31586 | 120.7581 | 120.6299 | 120.5978 | -1.2405 | 121.3898 | 121.4172 | 120.5246 | -121.6736
885.3281 | 121.8704 | -120.575 | 1.1169 | -0.016174 | 0.011557 | 0.0012347 | 0.0037577 | 0.052724 | -0.0041357 | -0.0020507 | 0.0067901 | 1.8226 | 1.7976 | 0.068915 | 3.516 | -0.0073978 | 0.1236 | 0.11444 | 0.14648 | 0.16937 | 0.11902 | 0.086975 | -0.050354 | -120.6436 | 0.009155 | -0.29755 | 0.76904 | 0.75531 | -120.3094 | -120.4651 | 120.6619 | 120.5246 | -0.99792 | 120.6894 | 120.7443 | 0.21973 | -0.99335 | 0.2655 | 0.10986 | -0.3479 | -0.068665 | 120.2774 | 120.1675 | -0.36163 | 120.694 | 120.6985 | 120.7214 | -1.1673 | 121.344 | 121.3303 | 120.5841 | -121.582
887.0781 | 121.7697 | -120.5933 | 1.1032 | -0.00091566 | 0.0085664 | 0.0020893 | 0.0065347 | 0.052511 | -0.0058447 | -0.0035461 | -0.00083936 | 1.849 | 1.7664 | 0.067633 | 3.5107 | -0.0076114 | 0.10529 | 0.11444 | 0.14191 | 0.16479 | 0.12817 | 0.059509 | -0.059509 | -120.6757 | 0.022888 | -0.3067 | 0.737 | 0.737 | -120.3186 | -120.4971 | 120.6528 | 120.5338 | -0.97504 | 120.7077 | 120.7581 | 0.2243 | -0.99792 | 0.27466 | 0.096131 | -0.36621 | -0.082397 | 120.2866 | 120.1904 | -0.36621 | 120.7214 | 120.6985 | 120.7352 | -1.1627 | 121.3303 | 121.3303 | 120.6161 | -121.6003
888.8281 | 121.6965 | -120.6024 | 1.0986 | -0.0085447 | 0.012198 | -0.00090151 | 0.0084573 | 0.05486 | -0.0039221 | -0.0058959 | -0.0084684 | 1.8508 | 1.7684 | 0.07041 | 3.5104 | -0.0099612 | 0.10529 | 0.091553 | 0.13733 | 0.17395 | 0.13275 | 0.059509 | -0.082397 | -120.6757 | 0 | -0.38452 | 0.75531 | 0.74616 | -120.3232 | -120.4926 | 120.6619 | 120.52 | -0.96588 | 120.694 | 120.7764 | 0.25635 | -0.99335 | 0.27924 | 0.10986 | -0.34332 | -0.073242 | 120.2179 | 120.108 | -0.35248 | 120.7352 | 120.7077 | 120.7397 | -1.181 | 121.3577 | 121.3486 | 120.6024 | -121.5912
890.5469 | 121.6827 | -120.5704 | 1.1169 | 0.0067138 | 0.014761 | 0.00016669 | 0.0067483 | 0.051443 | -0.0034949 | -0.0041869 | -0.0084684 | 1.8407 | 1.7784 | 0.069556 | 3.5113 | -0.011029 | 0.09613 | 0.11444 | 0.15106 | 0.16479 | 0.13275 | 0.050354 | -0.068665 | -120.7077 | 0.027466 | -0.37537 | 0.75531 | 0.76446 | -120.3049 | -120.4697 | 120.6207 | 120.5017 | -0.98419 | 120.6848 | 120.7352 | 0.23346 | -1.0208 | 0.2655 | 0.10071 | -0.36163 | -0.13733 | 120.195 | 120.0943 | -0.35248 | 120.7031 | 120.6665 | 120.7214 | -1.1856 | 121.3257 | 121.3348 | 120.5978 | -121.5866
892.2969 | 121.7194 | -120.5566 | 1.1078 | -0.0085447 | 0.011984 | -0.0013287 | 0.0046121 | 0.05422 | -0.00050411 | -0.0046143 | 0.0067901 | 1.8332 | 1.7812 | 0.070624 | 3.5087 | -0.0071842 | 0.11902 | 0.14648 | 0.16479 | 0.18768 | 0.1236 | 0.07782 | -0.045776 | -120.6528 | 0.004578 | -0.37079 | 0.72784 | 0.73242 | -120.282 | -120.4514 | 120.6345 | 120.5109 | -0.98419 | 120.7031 | 120.7443 | 0.23346 | -0.98877 | 0.27466 | 0.10529 | -0.37994 | -0.09613 | 120.1859 | 120.0806 | -0.37537 | 120.6802 | 120.6757 | 120.7214 | -1.1536 | 121.2845 | 121.2891 | 120.5612 | -121.5591
893.9688 | 121.6507 | -120.4926 | 1.1581 | -0.00091566 | 0.014761 | 0.00059389 | 0.0050393 | 0.052511 | -0.0015723 | -0.0048279 | -0.00083936 | 1.8369 | 1.7778 | 0.06806 | 3.5072 | -0.0093204 | 0.064087 | 0.050354 | 0.068665 | 0.10529 | 0.15106 | 0.027466 | -0.09613 | -120.6802 | -0.045776 | -0.40741 | 0.8194 | 0.82855 | -120.2545 | -120.401 | 120.52 | 120.3964 | -1.0071 | 120.5429 | 120.5978 | 0.20142 | -1.0941 | 0.23804 | 0.091553 | -0.33874 | -0.18768 | 120.0851 | 119.9936 | -0.32959 | 120.6436 | 120.5566 | 120.5612 | -1.2543 | 121.312 | 121.3211 | 120.4468 | -121.5591
895.7188 | 121.7239 | -120.4971 | 1.1032 | -0.00091566 | 0.01113 | 0.0020893 | 0.0024759 | 0.052297 | -0.0013587 | -0.0031189 | -0.00083936 | 1.9242 | 1.6878 | 0.068701 | 3.5081 | -0.0093204 | 0.13733 | 0.11444 | 0.16937 | 0.17395 | 0.11444 | 0.073242 | -0.041199 | -120.5429 | -0.009155 | -0.36163 | 0.73242 | 0.737 | -120.1996 | -120.4056 | 120.5704 | 120.4559 | -0.98877 | 120.6116 | 120.6711 | 0.21515 | -0.96588 | 0.29755 | 0.091552 | -0.37079 | -0.045777 | 120.1355 | 120.0439 | -0.36621 | 120.6116 | 120.6345 | 120.6665 | -1.1444 | 121.2296 | 121.2341 | 120.488 | -121.5088
897.4688 | 121.6965 | -120.4742 | 1.1032 | -0.016174 | 0.014334 | -0.0019695 | 0.0020487 | 0.054006 | 0.0041955 | -0.0020507 | -0.00083936 | 1.9529 | 1.7284 | 0.13471 | 3.5064 | -0.0082522 | 0.041199 | 0.004578 | 0.013733 | 0.09613 | 0.15564 | 0.045776 | -0.073242 | 0.20142 | -0.045776 | -0.55389 | 0.78278 | 0.76446 | -120.2225 | -120.4422 | 120.52 | 120.401 | -0.94757 | 120.4788 | 120.5704 | 0.16937 | -1.062 | 0.25177 | 0.032043 | -0.32043 | 120.6757 | 119.9203 | 119.8883 | -0.33875 | 120.6299 | 120.5154 | 120.488 | -1.1765 | 121.257 | 121.2387 | 120.4285 | -121.5454
899.2188 | 121.6049 | -120.4834 | 1.1307 | -0.0085447 | 0.009848 | 0.0029437 | 0.0048257 | 0.052938 | -0.0047765 | -0.0039733 | 0.01442 | 1.8625 | 1.8094 | 0.13407 | 3.4996 | -0.0073978 | 0.10071 | 0.10986 | 0.15106 | 0.15564 | 0.14191 | 0.07782 | -0.054932 | 0.23346 | -0.009155 | -0.40741 | 0.75073 | 0.74616 | -120.1584 | -120.3461 | 120.5612 | 120.4285 | -0.98877 | 120.5933 | 120.639 | 0.21057 | -1.03 | 0.32501 | 0.13733 | -0.37994 | 120.7169 | 120.076 | 119.9387 | -0.38452 | 120.6253 | 120.5841 | 120.6345 | -1.1856 | 121.2341 | 121.2296 | 120.4742 | -121.4767
900.9688 | 121.5958 | -120.433 | 1.1307 | -0.0085447 | 0.01583 | 0.0025165 | 0.0088847 | 0.054006 | 0.00077749 | -0.0026917 | -0.00083936 | 1.883 | 1.7929 | 0.13492 | 3.5013 | -0.0076114 | 0.018311 | 0.004578 | 0.022888 | 0.082397 | 0.16022 | 0.032043 | -0.09613 | 0.23804 | -0.027466 | -0.45319 | 0.81482 | 0.8194 | -120.2042 | -120.369 | 120.4651 | 120.3369 | -0.97046 | 120.4376 | 120.5154 | 0.17853 | -1.1124 | 0.22888 | 0.064086 | -0.31586 | 120.6711 | 119.9799 | 119.9158 | -0.31128 | 120.5933 | 120.4514 | 120.4559 | -1.2268 | 121.2479 | 121.2524 | 120.4056 | -121.4996
902.6562 | 121.637 | -120.3735 | 1.1765 | 0.0067138 | 0.01113 | 0.0027301 | 0.0071757 | 0.05187 | -0.0058447 | -0.0044007 | 0.0067901 | 1.8804 | 1.7878 | 0.13386 | 3.4978 | -0.007825 | 0.045776 | 0.073242 | 0.10529 | 0.14191 | 0.14648 | 0.068665 | -0.045776 | 0.29297 | -0.009155 | -0.3891 | 0.81482 | 0.81024 | -120.0943 | -120.282 | 120.4422 | 120.3278 | -1.03 | 120.4468 | 120.5154 | 0.18768 | -1.1307 | 0.27924 | 0.091553 | -0.36163 | 120.6665 | 119.9844 | 119.8929 | -0.36621 | 120.52 | 120.4193 | 120.4788 | -1.2222 | 121.1884 | 121.1838 | 120.3644 | -121.4584
904.3906 | 121.5363 | -120.4102 | 1.1169 | -0.00091566 | 0.014975 | 0.0016619 | 0.0050393 | 0.05422 | -0.0026403 | -0.0039733 | -0.0084684 | 1.8777 | 1.7946 | 0.13471 | 3.4981 | -0.010175 | 0.11444 | 0.13733 | 0.15564 | 0.16937 | 0.14191 | 0.068665 | -0.073242 | 0.29755 | 0.045776 | -0.39825 | 0.76446 | 0.76904 | -120.1218 | -120.3094 | 120.4788 | 120.3369 | -0.97504 | 120.5475 | 120.5795 | 0.24261 | -1.0025 | 0.28839 | 0.10071 | -0.35248 | 120.7077 | 120.0119 | 119.9112 | -0.3479 | 120.5521 | 120.5246 | 120.5658 | -1.1902 | 121.1746 | 121.1792 | 120.4559 | -121.4264
906.1406 | 121.6141 | -120.3873 | 1.0941 | 0.0067138 | 0.01348 | -0.0013287 | 0.0031167 | 0.05486 | 0.0018457 | -0.0050415 | -0.00083936 | 1.8544 | 1.8203 | 0.13642 | 3.5023 | -0.012525 | 0.032043 | -0.036621 | 0.013733 | 0.09613 | 0.19226 | 0.036621 | -0.091553 | 0.23346 | -0.10071 | -0.53558 | 0.78735 | 0.75073 | -120.108 | -120.3415 | 120.4239 | 120.2957 | -0.90179 | 120.3506 | 120.4834 | 0.18768 | -1.062 | 0.27924 | 0.045776 | -0.3067 | 120.6207 | 119.8517 | 119.8059 | -0.34332 | 120.5795 | 120.4193 | 120.401 | -1.1856 | 121.1746 | 121.138 | 120.2866 | -121.4355
907.8906 | 121.6415 | -120.3873 | 1.0712 | -0.0085447 | 0.014548 | 0.00059389 | 0.0031167 | 0.054006 | 0.00099129 | -0.0033325 | 0.0067901 | 1.8508 | 1.8211 | 0.13557 | 3.4976 | -0.009534 | 0.041199 | -0.027466 | 0.018311 | 0.086975 | 0.16479 | 0.045776 | -0.10529 | 0.26093 | -0.086975 | -0.48523 | 0.76446 | 0.77362 | -120.1401 | -120.314 | 120.433 | 120.282 | -0.90637 | 120.3598 | 120.4742 | 0.19226 | -1.03 | 0.24719 | 0.073242 | -0.3067 | 120.6482 | 119.902 | 119.8288 | -0.29755 | 120.5521 | 120.4285 | 120.4056 | -1.1765 | 121.1517 | 121.1609 | 120.3003 | -121.3852
909.5781 | 121.7239 | -0.25177 | 121.5591 | -0.00091566 | 0.015189 | 0.0012347 | 0.0065347 | 0.05486 | -0.0043493 | -0.0050415 | -0.00083936 | -0.001145 | -0.032058 | 0.037085 | 0.0078847 | -0.015515 | -0.054932 | -0.073242 | -0.032043 | 0.004578 | 0.068665 | -0.045776 | -0.17853 | -0.13275 | 0.059509 | -0.19226 | 0 | 0.013733 | -0.20599 | -0.3067 | 0.20599 | 0.073242 | -121.4905 | 0.17853 | 0.25635 | 0.18311 | -121.6141 | 0.045776 | -0.054932 | -121.5591 | 0.11902 | 0.059509 | 0.11444 | -121.5454 | 0.32044 | 0.19684 | 0.21973 | -121.7377 | 0.25177 | 0.2655 | 0.31128 | -121.8658
911.3281 | 121.9574 | -0.23804 | 121.6003 | -0.0085447 | 0.013693 | -0.0028241 | 0.0056803 | 0.053365 | -0.00093131 | -0.0035461 | 0.0067901 | -0.0013586 | -0.032272 | 0.037939 | 0.0076711 | -0.017865 | -0.045776 | -0.086975 | -0.018311 | 0.004578 | 0.09613 | -0.022888 | -0.16937 | -0.064087 | 0.045776 | -0.13275 | -0.027466 | -0.027466 | -0.17395 | -0.27924 | 0.21515 | 0.068664 | -121.5042 | 0.15106 | 0.24261 | 0.17395 | -121.6461 | 0.064087 | -0.041199 | -121.6278 | 0.17395 | 0.10529 | 0.14648 | -121.6278 | 0.33417 | 0.19226 | 0.21973 | -121.7697 | 0.21057 | 0.21057 | 0.28381 | -121.8796
913.0781 | 121.8933 | -0.25177 | 121.6827 | -0.00091566 | 0.0072846 | 0.0031573 | 0.0024759 | 0.052083 | -0.0071265 | -0.0039733 | -0.00083936 | -0.0034948 | -0.035476 | 0.034949 | 0.0080983 | -0.016797 | 0.027466 | 0.073242 | 0.1236 | 0.086975 | 0.050354 | 0.013733 | -0.11902 | -0.013733 | 0.14648 | -0.045776 | -0.045776 | -0.036621 | -0.16479 | -0.25177 | 0.2655 | 0.13275 | -121.6324 | 0.32501 | 0.33874 | 0.20599 | -121.6553 | 0.086975 | 0 | -121.7285 | 0.23804 | 0.20599 | 0.20599 | -121.7194 | 0.30212 | 0.27924 | 0.37537 | -121.8018 | 0.20599 | 0.21515 | 0.39825 | -121.9345
914.8281 | 121.9208 | -0.28381 | 121.7102 | -0.0085447 | 0.012412 | 0.00059389 | 0.0065347 | 0.050802 | -0.0062719 | -0.0050415 | -0.016098 | -0.0054174 | -0.03334 | 0.03559 | 0.0083119 | -0.017011 | -0.041199 | -0.027466 | 0.018311 | 0.050354 | 0.059509 | -0.022888 | -0.15564 | -0.091553 | 0.018311 | -0.10529 | -0.036621 | -0.032043 | -0.16479 | -0.27466 | 0.26092 | 0.12817 | -121.6507 | 0.25635 | 0.33417 | 0.20599 | -121.7514 | 0.11902 | 0.009155 | -121.7468 | 0.19226 | 0.17853 | 0.16937 | -121.7422 | 0.34332 | 0.24261 | 0.30212 | -121.8658 | 0.24719 | 0.25177 | 0.30212 | -121.9849
916.5312 | 121.8979 | -0.2655 | 121.7148 | -0.0085447 | 0.013266 | 0.00038029 | 0.0063211 | 0.057424 | -0.0041357 | -0.0063233 | 0.0067901 | -0.0024268 | -0.033126 | 0.037298 | 0.0076711 | -0.019574 | 0.050354 | 0.059509 | 0.086975 | 0.086975 | 0.041199 | -0.022888 | -0.14191 | -0.013733 | 0.1236 | -0.068665 | -0.041199 | -0.054932 | -0.16937 | -0.24719 | 0.24261 | 0.1236 | -121.6736 | 0.32501 | 0.35248 | 0.22888 | -121.6644 | 0.09613 | 0.018311 | -121.756 | 0.25177 | 0.19684 | 0.17853 | -121.7697 | 0.3067 | 0.31586 | 0.35248 | -121.8567 | 0.2243 | 0.21057 | 0.3891 | -121.962
918.2812 | 121.9894 | -0.25177 | 121.6965 | -0.0085447 | 0.01583 | -0.00047431 | 0.0031167 | 0.05187 | 0.0029139 | -0.0050415 | -0.00083936 | 0.0029138 | -0.035476 | 0.03858 | 0.013866 | -0.016584 | 0.027466 | -0.050354 | -0.018311 | 0.041199 | 0.068665 | -0.032043 | -0.17395 | -0.045776 | 0.032043 | -0.17853 | -0.022888 | -0.004578 | -0.21057 | -0.28839 | 0.21973 | 0.07782 | -121.6278 | 0.20142 | 0.29297 | 0.21515 | -121.669 | 0.041199 | -0.036621 | -121.7194 | 0.20599 | 0.073242 | 0.10986 | -121.701 | 0.32044 | 0.27924 | 0.23346 | -121.8704 | 0.22888 | 0.24719 | 0.28381 | -121.9849
920.0156 | 122.049 | -0.27008 | 121.7102 | -0.00091566 | 0.01348 | -0.0021833 | 0.0031167 | 0.054433 | -0.00093131 | -0.0022643 | 0.0067901 | 0.000564 | -0.033981 | 0.037726 | 0.011943 | -0.018079 | -0.068665 | -0.11902 | -0.07782 | 0.004578 | 0.10071 | -0.050354 | -0.17853 | -0.11444 | -0.059509 | -0.21973 | 0 | -0.013733 | -0.2243 | -0.3067 | 0.21973 | 0.091553 | -121.6095 | 0.15106 | 0.27466 | 0.18311 | -121.7789 | 0.045777 | -0.036621 | -121.7102 | 0.15564 | 0.050354 | 0.086975 | -121.7239 | 0.37079 | 0.20142 | 0.19226 | -121.8887 | 0.27008 | 0.25635 | 0.21057 | -122.0169
921.7188 | 122.0306 | -0.26093 | 121.7239 | -0.00091566 | 0.015189 | -0.00047431 | 0.0050393 | 0.054006 | 0.00035029 | -0.0029053 | -0.00083936 | 0.0014184 | -0.03334 | 0.036017 | 0.01173 | -0.016584 | -0.073242 | -0.11444 | -0.068665 | -0.009155 | 0.07782 | -0.041199 | -0.16937 | -0.13733 | -0.050354 | -0.21973 | 0.004578 | 0 | -0.21515 | -0.29297 | 0.21973 | 0.091552 | -121.6461 | 0.14648 | 0.25177 | 0.16022 | -121.7972 | 0.045776 | -0.032044 | -121.7194 | 0.1236 | 0.041198 | 0.073242 | -121.7239 | 0.33875 | 0.18768 | 0.19226 | -121.8933 | 0.2655 | 0.26093 | 0.21057 | -122.0169
923.4531 | 122.049 | -0.25177 | 121.7651 | -0.016174 | 0.01583 | -0.0028241 | 0.0065347 | 0.05486 | 0.00035029 | -0.0024779 | -0.00083936 | 0.0012048 | -0.031845 | 0.037085 | 0.011516 | -0.013593 | -0.082397 | -0.12817 | -0.068665 | -0.004578 | 0.086975 | -0.054932 | -0.16022 | -0.14191 | -0.059509 | -0.2243 | -0.004578 | -0.013733 | -0.21515 | -0.30212 | 0.19684 | 0.091553 | -121.6782 | 0.1236 | 0.24719 | 0.15564 | -121.8475 | 0.036621 | -0.050354 | -121.7697 | 0.10986 | 0.027466 | 0.07782 | -121.7789 | 0.33874 | 0.16937 | 0.1831 | -121.9254 | 0.24719 | 0.23804 | 0.19226 | -122.0673
925.2031 | 121.9803 | -0.27924 | 121.7697 | -0.0085447 | 0.011771 | 0.0016619 | 0.0058939 | 0.053792 | -0.0056311 | -0.0031189 | 0.0067901 | -0.0005042 | -0.035476 | 0.03559 | 0.0095937 | -0.014875 | -0.082397 | -0.091553 | -0.032043 | 0 | 0.07782 | -0.054932 | -0.16937 | -0.13733 | 0.022888 | -0.19226 | -0.018311 | -0.013733 | -0.21515 | -0.30212 | 0.2243 | 0.10986 | -121.6919 | 0.18768 | 0.27924 | 0.16937 | -121.8521 | 0.064087 | -0.022888 | -121.788 | 0.14191 | 0.086975 | 0.10986 | -121.7834 | 0.35706 | 0.19684 | 0.24719 | -121.9391 | 0.26092 | 0.2655 | 0.30212 | -122.0718
926.9531 | 122.1085 | -0.22888 | 121.7743 | -0.0085447 | 0.012839 | -0.0011151 | 0.0048257 | 0.051656 | -0.0028539 | -0.0044007 | 0.0067901 | -0.0024268 | -0.036117 | 0.034094 | 0.011089 | -0.01637 | 0.018311 | 0.009155 | 0.036621 | 0.064087 | 0.041199 | -0.009155 | -0.14191 | -0.018311 | 0.045776 | -0.10071 | -0.036621 | -0.041199 | -0.15106 | -0.2655 | 0.21973 | 0.086975 | -121.7331 | 0.23804 | 0.29297 | 0.20599 | -121.756 | 0.07782 | -0.036621 | -121.8109 | 0.21057 | 0.12817 | 0.16479 | -121.8155 | 0.27008 | 0.24719 | 0.2655 | -121.9162 | 0.19226 | 0.18768 | 0.27466 | -122.0398
928.6406 | 121.9803 | -0.28381 | 121.8155 | -0.023804 | 0.012625 | 0.00038029 | 0.0046121 | 0.05486 | -0.0066993 | -0.0061095 | 0.0067901 | -0.0022132 | -0.03334 | 0.03559 | 0.0098073 | -0.014447 | 0.022888 | 0.050354 | 0.086975 | 0.086975 | 0.050354 | -0.009155 | -0.12817 | -0.050354 | 0.10529 | -0.068665 | -0.059509 | -0.027466 | -0.1831 | -0.27924 | 0.27466 | 0.15564 | -121.7651 | 0.33417 | 0.37079 | 0.21515 | -121.7926 | 0.10071 | 0.004577 | -121.875 | 0.23346 | 0.21515 | 0.21057 | -121.843 | 0.33417 | 0.3067 | 0.37079 | -121.9437 | 0.2243 | 0.25635 | 0.3891 | -122.0947
930.3906 | 122.0169 | -0.28381 | 121.8201 | -0.0085447 | 0.0083526 | 0.00059389 | 0.0061075 | 0.054006 | -0.0058447 | -0.0052551 | 0.0067901 | -0.0037086 | -0.037826 | 0.037085 | 0.0074575 | -0.017652 | -0.013733 | -0.036621 | 0.027466 | 0.050354 | 0.059509 | 0 | -0.13275 | -0.091553 | -0.027466 | -0.11902 | -0.036621 | -0.036621 | -0.18768 | -0.26093 | 0.28381 | 0.15106 | -121.7606 | 0.24719 | 0.33417 | 0.18311 | -121.8338 | 0.09613 | 0.022888 | -121.8567 | 0.19226 | 0.16479 | 0.14191 | -121.8567 | 0.34332 | 0.27008 | 0.31128 | -121.9528 | 0.24719 | 0.24719 | 0.25635 | -122.081
932.1562 | 122.0123 | -0.27466 | 121.8384 | -0.0085447 | 0.012839 | 0.0025165 | 0.0056803 | 0.054006 | -0.0058447 | -0.0044007 | -0.0084684 | -0.0009314 | -0.034835 | 0.035376 | 0.0074575 | -0.017438 | 0.032043 | 0.041199 | 0.07782 | 0.09613 | 0.045776 | -0.018311 | -0.13733 | -0.027466 | 0.10071 | -0.073242 | -0.064087 | -0.064087 | -0.17853 | -0.26093 | 0.25635 | 0.13733 | -121.7926 | 0.31586 | 0.37079 | 0.23346 | -121.8063 | 0.09613 | 0.013733 | -121.9025 | 0.24719 | 0.20142 | 0.18768 | -121.9025 | 0.32043 | 0.3067 | 0.35248 | -121.9757 | 0.21057 | 0.21057 | 0.37537 | -122.0993
933.8906 | 122.1268 | -0.24719 | 121.788 | -0.0085447 | 0.019247 | 0.00016669 | 0.0061075 | 0.053152 | 0.0027003 | -0.0050415 | -0.0084684 | 0.0012048 | -0.033554 | 0.037726 | 0.011303 | -0.018933 | 0.009155 | -0.027466 | 0 | 0.054932 | 0.073242 | -0.050354 | -0.16937 | -0.045776 | 0.082397 | -0.14648 | -0.032043 | -0.032043 | -0.19684 | -0.30212 | 0.19684 | 0.077819 | -121.7148 | 0.21973 | 0.30212 | 0.22431 | -121.7789 | 0.050354 | -0.054932 | -121.8201 | 0.20142 | 0.10071 | 0.15564 | -121.8201 | 0.32043 | 0.25635 | 0.24719 | -121.9574 | 0.21515 | 0.21515 | 0.32959 | -122.0901
935.5938 | 122.0032 | -0.29297 | 121.843 | -0.0085447 | 0.013693 | 0.0027301 | 0.0061075 | 0.05422 | -0.0049903 | -0.0037597 | 0.0067901 | -0.0026404 | -0.034195 | 0.036871 | 0.0068165 | -0.015729 | 0.018311 | 0.045776 | 0.09613 | 0.082397 | 0.036621 | -0.036621 | -0.13275 | -0.036621 | 0.11444 | -0.10071 | -0.032043 | -0.050354 | -0.1831 | -0.27466 | 0.25635 | 0.16022 | -121.8063 | 0.33874 | 0.37537 | 0.21515 | -121.8246 | 0.10986 | 0.018311 | -121.875 | 0.25635 | 0.19226 | 0.17395 | -121.8933 | 0.32959 | 0.31128 | 0.3891 | -121.9757 | 0.26093 | 0.24261 | 0.40741 | -122.1176
937.3438 | 122.0764 | -0.28381 | 121.8658 | -0.0085447 | 0.00878 | 0.0035847 | 0.0052531 | 0.05187 | -0.0058447 | -0.0054687 | -0.0084684 | -0.0034948 | -0.035049 | 0.035376 | 0.0091665 | -0.01637 | 0 | -0.013733 | 0.027466 | 0.050354 | 0.068665 | -0.013733 | -0.15564 | -0.059509 | 0.022888 | -0.086975 | -0.059509 | -0.032043 | -0.17853 | -0.28381 | 0.27008 | 0.12817 | -121.7972 | 0.27008 | 0.33417 | 0.20599 | -121.8658 | 0.10528 | 0 | -121.9254 | 0.2243 | 0.19684 | 0.19684 | -121.8979 | 0.35248 | 0.28381 | 0.31128 | -122.0215 | 0.2243 | 0.25177 | 0.3067 | -122.1497
939.0781 | 122.049 | -0.31128 | 121.8384 | -0.00091566 | 0.015616 | -4.6912e-05 | 0.0054667 | 0.055501 | -0.0030677 | -0.0058959 | 0.01442 | -0.0015722 | -0.035263 | 0.036017 | 0.0083119 | -0.018933 | -0.032043 | -0.054932 | -0.036621 | 0.022888 | 0.068665 | -0.050354 | -0.1831 | -0.11444 | 0 | -0.1831 | -0.022888 | -0.018311 | -0.23804 | -0.31128 | 0.26092 | 0.12817 | -121.7697 | 0.25635 | 0.33417 | 0.20599 | -121.8704 | 0.073242 | 0 | -121.8613 | 0.19684 | 0.12817 | 0.12817 | -121.8567 | 0.37994 | 0.27924 | 0.27466 | -122.0215 | 0.28839 | 0.29297 | 0.31128 | -122.1497
940.8281 | 122.0306 | -0.3067 | 121.8246 | -0.0085447 | 0.015616 | 0.0012347 | 0.0067483 | 0.049947 | -0.0028539 | -0.0037597 | -0.0084684 | -0.0013586 | -0.033981 | 0.034735 | 0.010875 | -0.017438 | 0.013733 | 0.032043 | 0.059509 | 0.073242 | 0.041199 | -0.027466 | -0.14191 | -0.073242 | 0.064087 | -0.10986 | -0.032043 | -0.022888 | -0.2243 | -0.31128 | 0.27924 | 0.16479 | -121.7834 | 0.33874 | 0.37994 | 0.21515 | -121.8109 | 0.082398 | -0.004577 | -121.8567 | 0.23346 | 0.19684 | 0.20142 | -121.8475 | 0.3479 | 0.32043 | 0.36621 | -121.9666 | 0.27466 | 0.28381 | 0.37079 | -122.1359
942.5156 | 122.049 | -0.32044 | 121.8384 | -0.00091566 | 0.013266 | 0.0014483 | 0.0050393 | 0.054647 | -0.0019995 | -0.0046143 | 0.0067901 | -0.0024268 | -0.03569 | 0.034521 | 0.011303 | -0.016584 | 0.036621 | 0.027466 | 0.064087 | 0.082397 | 0.032043 | -0.004578 | -0.13733 | -0.032043 | 0.004578 | -0.068665 | -0.050354 | -0.032043 | -0.21973 | -0.29297 | 0.31586 | 0.18311 | -121.8063 | 0.3479 | 0.40283 | 0.21973 | -121.8018 | 0.10071 | 0.027466 | -121.8887 | 0.28839 | 0.25177 | 0.2243 | -121.8704 | 0.35248 | 0.35706 | 0.38452 | -121.9757 | 0.27008 | 0.28839 | 0.32501 | -122.1313
944.2656 | 122.0764 | -0.31128 | 121.8384 | -0.00091566 | 0.015402 | 0.0025165 | 0.0043985 | 0.054647 | -0.00050411 | -0.0035461 | -0.0084684 | 0.000564 | -0.034622 | 0.036017 | 0.010875 | -0.017652 | -0.054932 | -0.068665 | 0.036621 | 0.004578 | 0.073242 | -0.059509 | -0.17853 | -0.14648 | -0.009155 | -0.19684 | -0.009155 | 0.004578 | -0.27008 | -0.33875 | 0.25177 | 0.13275 | -121.7651 | 0.24261 | 0.31586 | 0.18311 | -121.8933 | 0.041198 | -0.027466 | -121.8475 | 0.16479 | 0.11444 | 0.14191 | -121.8338 | 0.38452 | 0.25635 | 0.3479 | -122.0169 | 0.30212 | 0.31586 | 0.30212 | -122.1771
946.0156 | 122.1405 | -0.28839 | 121.8063 | -0.00091566 | 0.013907 | -0.00068791 | 0.0016215 | 0.052511 | 0.0046229 | -0.00076912 | -0.0084684 | 0.0024866 | -0.035904 | 0.038153 | 0.014293 | -0.018079 | -0.004578 | -0.073242 | -0.027466 | 0.004578 | 0.082397 | -0.041199 | -0.16479 | -0.086975 | -0.004578 | -0.2243 | -0.009155 | -0.004578 | -0.25635 | -0.33875 | 0.24719 | 0.1236 | -121.7239 | 0.21515 | 0.29297 | 0.16937 | -121.8109 | 0.032043 | -0.050354 | -121.8155 | 0.20142 | 0.064087 | 0.11444 | -121.8109 | 0.37079 | 0.28381 | 0.26093 | -121.9711 | 0.27924 | 0.28381 | 0.28381 | -122.1451
947.7031 | 122.2183 | -0.30212 | 121.7651 | -0.00091566 | 0.012839 | 0.0012347 | 0.0043985 | 0.052511 | 0.0016321 | -0.0041869 | -0.016098 | -0.0009314 | -0.034622 | 0.035376 | 0.013012 | -0.017011 | -0.036621 | -0.073242 | -0.027466 | 0.022888 | 0.073242 | -0.022888 | -0.16479 | -0.064087 | -0.013733 | -0.14648 | -0.041199 | -0.041199 | -0.23804 | -0.32501 | 0.27924 | 0.13733 | -121.6919 | 0.22888 | 0.32501 | 0.18768 | -121.8018 | 0.064087 | -0.022888 | -121.8063 | 0.23804 | 0.15564 | 0.17853 | -121.8063 | 0.37537 | 0.2655 | 0.27466 | -121.9299 | 0.26093 | 0.26093 | 0.28839 | -122.0901
949.4531 | 122.0535 | -0.35248 | 121.8475 | -0.00091566 | 0.015616 | 0.0018757 | 0.0082437 | 0.052511 | -0.0019995 | -0.0029053 | -0.00083936 | 0.0001368 | -0.033554 | 0.033667 | 0.010448 | -0.015302 | 0.009155 | 0.036621 | 0.07782 | 0.082397 | 0.027466 | -0.018311 | -0.1236 | -0.045776 | 0.10071 | -0.10986 | -0.059509 | -0.045776 | -0.24261 | -0.32501 | 0.33417 | 0.22888 | -121.8201 | 0.3891 | 0.43488 | 0.20599 | -121.8384 | 0.10986 | 0.027466 | -121.907 | 0.3067 | 0.24262 | 0.21515 | -121.8933 | 0.37994 | 0.36163 | 0.4303 | -121.9711 | 0.29297 | 0.3067 | 0.45319 | -122.1725
951.2031 | 122.168 | -0.3067 | 121.8475 | -0.00091566 | 0.012412 | -0.0013287 | 0.0052531 | 0.051015 | 0.00035029 | -0.0046143 | -0.016098 | -0.0009314 | -0.035049 | 0.034949 | 0.011303 | -0.017438 | 0.045776 | 0.013733 | 0.082397 | 0.091553 | 0.032043 | 0.004578 | -0.14648 | -0.004578 | 0.032043 | -0.068665 | -0.073242 | -0.054932 | -0.22888 | -0.29297 | 0.31128 | 0.16022 | -121.8155 | 0.32043 | 0.39825 | 0.23804 | -121.8018 | 0.07782 | 0.013733 | -121.9208 | 0.30212 | 0.23804 | 0.2243 | -121.9025 | 0.33874 | 0.35248 | 0.3891 | -121.994 | 0.23346 | 0.25177 | 0.33874 | -122.1405
952.9531 | 122.2137 | -0.31128 | 121.7972 | -0.0085447 | 0.013907 | 0.0010211 | 0.0016215 | 0.05422 | 0.0014185 | -0.00098272 | -0.0084684 | -0.0005042 | -0.034835 | 0.03623 | 0.014934 | -0.017224 | -0.054932 | -0.11902 | -0.086975 | -0.009155 | 0.07782 | -0.059509 | -0.17395 | -0.11444 | -0.068665 | -0.23804 | -0.022888 | -0.027466 | -0.27008 | -0.34332 | 0.25177 | 0.13733 | -121.7194 | 0.19226 | 0.30212 | 0.16479 | -121.8521 | 0.041198 | -0.032044 | -121.8201 | 0.19684 | 0.073242 | 0.10529 | -121.8246 | 0.3891 | 0.25635 | 0.2243 | -121.9711 | 0.28839 | 0.28381 | 0.24261 | -122.1405
954.6406 | 122.1497 | -0.32501 | 121.8292 | -0.0085447 | 0.011771 | 0.00016669 | 0.0078165 | 0.054647 | -0.0064855 | -0.0058959 | 0.0067901 | -0.0037086 | -0.033767 | 0.032812 | 0.0091665 | -0.017652 | 0.004578 | 0.018311 | 0.064087 | 0.068665 | 0.045776 | -0.032043 | -0.15106 | -0.027466 | 0.054932 | -0.059509 | -0.068665 | -0.059509 | -0.2243 | -0.33417 | 0.29297 | 0.17395 | -121.7834 | 0.34332 | 0.39368 | 0.21973 | -121.8246 | 0.10071 | -0.009155 | -121.8979 | 0.29755 | 0.2655 | 0.27466 | -121.8887 | 0.37079 | 0.32959 | 0.3891 | -121.9803 | 0.25635 | 0.2655 | 0.37994 | -122.1634
956.4062 | 122.1451 | -0.34332 | 121.8567 | -0.0085447 | 0.012412 | 0.0014483 | 0.0054667 | 0.050588 | -0.0077673 | -0.0044007 | -0.00083936 | -0.0022132 | -0.036972 | 0.031317 | 0.010448 | -0.017438 | -0.004578 | -0.013733 | 0.041199 | 0.064087 | 0.068665 | -0.036621 | -0.14648 | -0.050354 | 0.032043 | -0.073242 | -0.054932 | -0.050354 | -0.21973 | -0.31128 | 0.3067 | 0.19684 | -121.788 | 0.32959 | 0.40741 | 0.21057 | -121.8613 | 0.1236 | 0.032044 | -121.9116 | 0.29297 | 0.27008 | 0.23804 | -121.907 | 0.41199 | 0.33874 | 0.38452 | -122.0032 | 0.28839 | 0.29297 | 0.37537 | -122.168
958.1562 | 122.2275 | -0.31128 | 121.8338 | -0.00091566 | 0.010916 | 0.00016669 | 0.0041849 | 0.053152 | 0.0022729 | -0.0046143 | 0.0067901 | 0.0007776 | -0.033554 | 0.034521 | 0.012371 | -0.018079 | -0.032043 | -0.10986 | -0.064087 | -0.009155 | 0.07782 | -0.027466 | -0.19226 | -0.09613 | -0.050354 | -0.20142 | -0.027466 | -0.027466 | -0.26093 | -0.32044 | 0.28381 | 0.11902 | -121.756 | 0.20142 | 0.30212 | 0.18311 | -121.8658 | 0.050354 | -0.009156 | -121.8613 | 0.21515 | 0.10986 | 0.11902 | -121.8613 | 0.3891 | 0.27924 | 0.24719 | -122.0261 | 0.28381 | 0.28381 | 0.26092 | -122.1542
959.8906 | 122.2229 | -0.29755 | 121.8292 | -0.0085447 | 0.018393 | -0.0015423 | 0.0058939 | 0.054433 | 0.0016321 | -0.0011963 | -0.00083936 | 0.0018456 | -0.032913 | 0.034949 | 0.012798 | -0.02107 | 0 | -0.032043 | -0.009155 | 0.036621 | 0.091553 | -0.050354 | -0.17395 | -0.045776 | 0.050354 | -0.16479 | -0.036621 | -0.018311 | -0.23346 | -0.33417 | 0.24719 | 0.1236 | -121.7377 | 0.2655 | 0.33417 | 0.21057 | -121.8292 | 0.064087 | -0.036621 | -121.8658 | 0.25177 | 0.13275 | 0.16937 | -121.8475 | 0.3891 | 0.29755 | 0.28839 | -122.0032 | 0.26092 | 0.27923 | 0.3479 | -122.1634
961.6406 | 122.2275 | -0.3067 | 121.8613 | -0.0085447 | 0.015616 | 0.0012347 | 0.0084573 | 0.053579 | -0.00050411 | -0.0033325 | -0.00083936 | 0.0001368 | -0.031417 | 0.033667 | 0.011943 | -0.018079 | -0.050354 | -0.10071 | -0.059509 | 0.004578 | 0.068665 | -0.059509 | -0.16479 | -0.11902 | 0.013733 | -0.20142 | -0.018311 | 0.004578 | -0.26093 | -0.34332 | 0.24719 | 0.14191 | -121.7926 | 0.20599 | 0.31128 | 0.16937 | -121.9116 | 0.045777 | -0.036621 | -121.8796 | 0.18768 | 0.10529 | 0.14191 | -121.8567 | 0.37537 | 0.25635 | 0.24719 | -122.0261 | 0.28839 | 0.31128 | 0.32043 | -122.2046
963.3906 | 122.2321 | -0.30212 | 121.8384 | -0.023804 | 0.016043 | 0.00059389 | 0.0067483 | 0.05422 | -0.0017859 | -0.0041869 | -0.016098 | 0.0012048 | -0.033554 | 0.034735 | 0.012584 | -0.017865 | -0.059509 | -0.09613 | -0.045776 | 0.027466 | 0.059509 | -0.041199 | -0.16022 | -0.10986 | 0.027466 | -0.18768 | -0.027466 | -0.009155 | -0.24719 | -0.3479 | 0.26093 | 0.14191 | -121.7789 | 0.20599 | 0.32959 | 0.18768 | -121.8979 | 0.054932 | -0.045776 | -121.8658 | 0.19226 | 0.11444 | 0.16022 | -121.8475 | 0.36163 | 0.24261 | 0.25635 | -121.9986 | 0.27466 | 0.29297 | 0.32959 | -122.1863
965.0781 | 122.1588 | -0.32044 | 121.8796 | -0.016174 | 0.013052 | 0.0018757 | 0.0050393 | 0.052938 | -0.0071265 | -0.0052551 | -0.00083936 | -0.002854 | -0.034622 | 0.035376 | 0.0098073 | -0.015515 | -0.041199 | -0.022888 | 0.032043 | 0.045776 | 0.050354 | -0.013733 | -0.14191 | -0.09613 | -0.032043 | -0.12817 | -0.054932 | -0.036621 | -0.23346 | -0.29755 | 0.3067 | 0.17853 | -121.8292 | 0.29755 | 0.36621 | 0.18768 | -121.9208 | 0.086976 | 0.022889 | -121.9345 | 0.22431 | 0.19226 | 0.16937 | -121.9162 | 0.37079 | 0.27924 | 0.35248 | -122.0215 | 0.2655 | 0.28381 | 0.28839 | -122.1771
966.8594 | 122.1359 | -0.34332 | 121.8704 | -0.0085447 | 0.012625 | 0.00038029 | 0.0046121 | 0.052724 | -0.0034949 | -0.0033325 | 0.0067901 | -0.001145 | -0.034835 | 0.032812 | 0.010448 | -0.017224 | 0.032043 | 0.027466 | 0.073242 | 0.073242 | 0.041199 | -0.022888 | -0.12817 | -0.022888 | 0.013733 | -0.07782 | -0.068665 | -0.068665 | -0.2243 | -0.30212 | 0.32043 | 0.21515 | -121.8292 | 0.37079 | 0.41656 | 0.20142 | -121.8384 | 0.11902 | 0.041199 | -121.9391 | 0.32043 | 0.2655 | 0.2243 | -121.9391 | 0.38452 | 0.37537 | 0.41656 | -121.9986 | 0.27466 | 0.27466 | 0.35706 | -122.1725
968.5469 | 122.2595 | -0.30212 | 121.8521 | -0.00091566 | 0.013907 | -0.00026071 | 0.0029031 | 0.052511 | -0.00050411 | -0.0054687 | -0.0084684 | 0.0035546 | -0.034835 | 0.035376 | 0.013652 | -0.017011 | -0.050354 | -0.11444 | -0.07782 | -0.009155 | 0.091553 | -0.036621 | -0.17853 | -0.1236 | -0.068665 | -0.20599 | -0.018311 | 0 | -0.25177 | -0.34332 | 0.2655 | 0.1236 | -121.7606 | 0.18768 | 0.29297 | 0.16937 | -121.9025 | 0.050354 | -0.041199 | -121.8704 | 0.17853 | 0.09613 | 0.13733 | -121.8521 | 0.39368 | 0.25177 | 0.2243 | -122.0306 | 0.28381 | 0.30212 | 0.23346 | -122.1954
970.2969 | 122.1771 | -0.32044 | 121.9162 | -0.00091566 | 0.012412 | 0.0012347 | 0.0078165 | 0.050588 | -0.0071265 | -0.0037597 | -0.00083936 | -0.0026404 | -0.033981 | 0.033453 | 0.0091665 | -0.017011 | 0.027466 | 0.068665 | 0.073242 | 0.09613 | 0.041199 | -0.013733 | -0.13275 | -0.009155 | 0.09613 | -0.045776 | -0.045776 | -0.059509 | -0.23346 | -0.31586 | 0.3067 | 0.18768 | -121.875 | 0.3891 | 0.41657 | 0.22888 | -121.8887 | 0.086976 | 0.004578 | -121.962 | 0.31128 | 0.27466 | 0.27008 | -121.9757 | 0.36163 | 0.3479 | 0.39368 | -122.049 | 0.27466 | 0.26093 | 0.41657 | -122.2321
972.0469 | 122.1405 | -0.3479 | 121.9025 | -0.00091566 | 0.012412 | 0.0018757 | 0.0026895 | 0.052511 | -0.0024267 | -0.0041869 | -0.00083936 | -0.0043494 | -0.035263 | 0.034308 | 0.011303 | -0.017224 | 0.027466 | 0.032043 | 0.073242 | 0.073242 | 0.022888 | -0.004578 | -0.11902 | -0.041199 | -0.009155 | -0.10529 | -0.064087 | -0.059509 | -0.21057 | -0.32044 | 0.34332 | 0.22888 | -121.8796 | 0.37994 | 0.42114 | 0.19226 | -121.875 | 0.13733 | 0.027465 | -121.9666 | 0.3067 | 0.24261 | 0.21515 | -121.962 | 0.37079 | 0.37537 | 0.42114 | -122.0215 | 0.28381 | 0.28839 | 0.33874 | -122.2229
973.8125 | 122.1954 | -0.33417 | 121.9208 | -0.00091566 | 0.012198 | 0.0016619 | 0.0073893 | 0.053579 | -0.0045629 | -0.0039733 | -0.00083936 | -0.0041358 | -0.034408 | 0.034094 | 0.0093801 | -0.019788 | -0.004578 | 0.004578 | 0.032043 | 0.059509 | 0.054932 | -0.018311 | -0.14191 | -0.050354 | 0.022888 | -0.086975 | -0.045776 | -0.064087 | -0.21515 | -0.30212 | 0.31586 | 0.19226 | -121.8658 | 0.33875 | 0.39368 | 0.20142 | -121.9254 | 0.11902 | 0.032043 | -121.9666 | 0.28381 | 0.24719 | 0.21515 | -121.9849 | 0.3891 | 0.32959 | 0.36621 | -122.0627 | 0.28839 | 0.27008 | 0.35706 | -122.2229
975.5156 | 122.287 | -0.29297 | 121.8658 | -0.0085447 | 0.011771 | -0.00026071 | 0.0039713 | 0.053792 | 0.00035029 | -0.0031189 | -0.00083936 | -0.0005042 | -0.032699 | 0.034949 | 0.013866 | -0.017011 | -0.059509 | -0.09613 | -0.059509 | -0.004578 | 0.086975 | -0.027466 | -0.17395 | -0.10529 | -0.068665 | -0.19684 | -0.027466 | -0.027466 | -0.25635 | -0.32501 | 0.2655 | 0.11902 | -121.7789 | 0.19684 | 0.28839 | 0.16937 | -121.9254 | 0.036621 | -0.032043 | -121.8933 | 0.18768 | 0.096131 | 0.12817 | -121.8933 | 0.37994 | 0.23346 | 0.23346 | -122.0398 | 0.2655 | 0.2655 | 0.2243 | -122.1909
977.2656 | 122.2641 | -0.29755 | 121.8704 | -0.00091566 | 0.014121 | -0.00090151 | 0.0035441 | 0.05422 | 0.00013669 | -0.0041869 | -0.016098 | -0.0022132 | -0.034408 | 0.037298 | 0.012798 | -0.018506 | 0.032043 | 0.027466 | 0.059509 | 0.09613 | 0.050354 | -0.018311 | -0.13275 | 0.004578 | 0.009155 | -0.091553 | -0.050354 | -0.045776 | -0.21057 | -0.31586 | 0.27923 | 0.16479 | -121.8201 | 0.32501 | 0.39368 | 0.22888 | -121.8384 | 0.086975 | -0.018311 | -121.9208 | 0.30212 | 0.20599 | 0.2243 | -121.9162 | 0.3479 | 0.32959 | 0.35705 | -122.0032 | 0.24719 | 0.25177 | 0.3067 | -122.1863
979 | 122.168 | -0.34332 | 121.9162 | -0.0085447 | 0.0092072 | 0.0012347 | 0.0039713 | 0.052724 | -0.0060583 | -0.0052551 | -0.00083936 | -0.0024268 | -0.034195 | 0.034308 | 0.010875 | -0.015729 | -0.013733 | -0.009155 | 0.022888 | 0.041199 | 0.036621 | -0.004578 | -0.15106 | -0.086975 | -0.036621 | -0.1236 | -0.041199 | -0.054932 | -0.24261 | -0.31586 | 0.33874 | 0.19226 | -121.8796 | 0.33417 | 0.38452 | 0.19226 | -121.9299 | 0.10071 | 0.027466 | -121.9574 | 0.25635 | 0.21973 | 0.19226 | -121.9711 | 0.37994 | 0.32959 | 0.36621 | -122.0673 | 0.30212 | 0.28839 | 0.3067 | -122.2321
980.6875 | 122.2687 | -0.29297 | 121.875 | -0.0085447 | 0.014334 | -0.0021833 | 0.0052531 | 0.05422 | 0.0020593 | -0.0018371 | -0.0084684 | 0.001632 | -0.032699 | 0.034521 | 0.013012 | -0.017865 | 0 | -0.032043 | -0.004578 | 0.054932 | 0.068665 | -0.045776 | -0.17395 | -0.064087 | 0.054932 | -0.17395 | -0.041199 | -0.032043 | -0.25635 | -0.33875 | 0.24719 | 0.11902 | -121.8063 | 0.26093 | 0.3479 | 0.22888 | -121.875 | 0.036621 | -0.045776 | -121.9162 | 0.22888 | 0.11902 | 0.1648 | -121.907 | 0.36163 | 0.29297 | 0.28839 | -122.049 | 0.25177 | 0.26093 | 0.3479 | -122.2137
982.4531 | 122.3007 | -0.31128 | 121.8796 | 0.0067138 | 0.015616 | 0.00016669 | 0.0056803 | 0.052724 | 0.00035029 | -0.0022643 | 0.0067901 | 0.002273 | -0.036331 | 0.034521 | 0.012584 | -0.018293 | -0.041199 | -0.09613 | -0.068665 | 0.004578 | 0.10071 | -0.064087 | -0.15564 | -0.082397 | -0.054932 | -0.18768 | -0.036621 | -0.032043 | -0.24719 | -0.32044 | 0.24719 | 0.15564 | -121.7789 | 0.21515 | 0.31586 | 0.16022 | -121.9208 | 0.064087 | -0.009156 | -121.9162 | 0.22888 | 0.1236 | 0.13275 | -121.9116 | 0.41199 | 0.27008 | 0.24261 | -122.0352 | 0.27466 | 0.27924 | 0.25635 | -122.2
984.1875 | 122.1451 | -0.35248 | 121.9208 | -0.00091566 | 0.011557 | 0.00059389 | 0.0050393 | 0.054647 | -0.0056311 | -0.0022643 | 0.0067901 | -0.0007178 | -0.035049 | 0.031744 | 0.0098073 | -0.015302 | 0.032043 | 0.045776 | 0.091553 | 0.09613 | 0.036621 | -0.009155 | -0.15106 | -0.032043 | 0.082397 | -0.073242 | -0.064087 | -0.068665 | -0.21515 | -0.3067 | 0.34332 | 0.20142 | -121.8842 | 0.39825 | 0.44861 | 0.24719 | -121.8887 | 0.13733 | 0.045776 | -121.9849 | 0.32044 | 0.27924 | 0.23346 | -121.9894 | 0.3891 | 0.38452 | 0.44403 | -122.0718 | 0.28839 | 0.28381 | 0.43488 | -122.2275
985.9375 | 122.2046 | -0.34332 | 121.9162 | -0.0085447 | 0.015189 | 0.0014483 | 0.0069621 | 0.054647 | -0.0026403 | -0.0041869 | -0.0084684 | -0.0015722 | -0.032272 | 0.03623 | 0.01173 | -0.017224 | -0.059509 | -0.10071 | -0.064087 | -0.013733 | 0.091553 | -0.059509 | -0.15564 | -0.14648 | -0.2243 | -0.19684 | -0.009155 | -0.018311 | -0.27008 | -0.33875 | 0.28381 | 0.18768 | -121.8246 | 0.24261 | 0.32959 | 0.14191 | -121.9757 | 0.073242 | 0.004578 | -121.9254 | 0.19684 | 0.14648 | 0.14191 | -121.9345 | 0.43488 | 0.28381 | 0.27924 | -122.0718 | 0.33417 | 0.32501 | 0.11902 | -122.2549
987.6406 | 122.287 | -0.28839 | 121.8796 | -0.0085447 | 0.014975 | 0.0010211 | 0.0050393 | 0.055929 | 0.00035029 | -0.0033325 | -0.00083936 | 0.0014184 | -0.03569 | 0.034521 | 0.01173 | -0.017865 | -0.032043 | -0.086975 | -0.045776 | 0.018311 | 0.07782 | -0.059509 | -0.17853 | -0.086975 | -0.19226 | -0.17853 | -0.013733 | -0.027466 | -0.27924 | -0.33875 | 0.22888 | 0.10986 | -121.8018 | 0.20142 | 0.3067 | 0.19684 | -121.9116 | 0.009155 | -0.050354 | -121.8933 | 0.20142 | 0.10986 | 0.16022 | -121.907 | 0.36621 | 0.25635 | 0.24262 | -122.0581 | 0.27466 | 0.26093 | 0.09613 | -122.2183
989.4062 | 122.2137 | -0.33875 | 121.9116 | -0.00091566 | 0.013907 | 0.0012347 | 0.0067483 | 0.055074 | -0.0037085 | -0.0054687 | -0.00083936 | -7.6996e-05 | -0.033554 | 0.034094 | 0.011303 | -0.015729 | -0.064087 | -0.091553 | -0.059509 | -0.013733 | 0.082397 | -0.068665 | -0.17853 | -0.15106 | -0.21973 | -0.21515 | -0.018311 | -0.004578 | -0.26093 | -0.35248 | 0.27008 | 0.16022 | -121.8292 | 0.24719 | 0.32501 | 0.16479 | -121.9757 | 0.07782 | -0.013733 | -121.9299 | 0.18768 | 0.1236 | 0.13733 | -121.9162 | 0.42114 | 0.27466 | 0.27924 | -122.0901 | 0.32043 | 0.33417 | 0.11902 | -122.2641
991.0938 | 122.2733 | -0.33875 | 121.8796 | -0.016174 | 0.012412 | -0.00047431 | 0.0058939 | 0.053792 | -0.0024267 | -0.0035461 | -0.00083936 | 0.0001368 | -0.035476 | 0.033026 | 0.012798 | -0.018293 | 0.041199 | 0.027466 | 0.068665 | 0.091553 | 0.032043 | -0.018311 | -0.13733 | 0 | -0.13733 | -0.073242 | -0.07782 | -0.045776 | -0.22888 | -0.28839 | 0.32043 | 0.20142 | -121.8475 | 0.36621 | 0.4303 | 0.22888 | -121.8384 | 0.10986 | 0.050354 | -121.9574 | 0.33875 | 0.2655 | 0.21515 | -121.9254 | 0.37079 | 0.37994 | 0.40741 | -122.0169 | 0.26093 | 0.29297 | 0.20142 | -122.168
992.875 | 122.1542 | -0.35706 | 121.9345 | -0.00091566 | 0.01583 | 0.0035847 | 0.0054667 | 0.05486 | -0.0043493 | -0.0044007 | -0.0084684 | -0.0015722 | -0.03569 | 0.032599 | 0.0085255 | -0.017652 | 0.027466 | 0.050354 | 0.082397 | 0.09613 | 0.036621 | -0.022888 | -0.1236 | -0.050354 | -0.09613 | -0.086975 | -0.050354 | -0.036621 | -0.21973 | -0.31128 | 0.33417 | 0.23346 | -121.8979 | 0.40741 | 0.45319 | 0.21973 | -121.907 | 0.13733 | 0.045777 | -121.9849 | 0.3067 | 0.27008 | 0.2243 | -121.9711 | 0.39368 | 0.38452 | 0.43945 | -122.0581 | 0.3067 | 0.32043 | 0.26093 | -122.2458
994.5625 | 122.1909 | -0.36621 | 121.9208 | 0.0067138 | 0.011984 | 0.0025165 | 0.0037577 | 0.054433 | -0.0028539 | -0.0050415 | -0.00083936 | -0.0030676 | -0.036331 | 0.033881 | 0.012798 | -0.017438 | 0.036621 | 0.041199 | 0.07782 | 0.064087 | 0.036621 | -0.004578 | -0.14191 | -0.027466 | -0.12817 | -0.068665 | -0.059509 | -0.086975 | -0.23804 | -0.32044 | 0.36163 | 0.2243 | -121.8842 | 0.40741 | 0.4303 | 0.20599 | -121.8842 | 0.12817 | 0.045776 | -121.9803 | 0.33875 | 0.29755 | 0.25177 | -122.0078 | 0.40283 | 0.40283 | 0.44403 | -122.0627 | 0.3067 | 0.27924 | 0.23804 | -122.2412
996.3281 | 122.3145 | -0.29755 | 121.8842 | -0.0085447 | 0.01882 | -0.00068791 | 0.0056803 | 0.05486 | 0.0031275 | -0.0035461 | -0.016098 | 0.0041956 | -0.036117 | 0.034308 | 0.012798 | -0.018933 | -0.032043 | -0.064087 | -0.018311 | 0.045776 | 0.07782 | -0.054932 | -0.1831 | -0.059509 | -0.18768 | -0.16022 | -0.018311 | -0.027466 | -0.25635 | -0.35248 | 0.24261 | 0.11444 | -121.8063 | 0.23346 | 0.34332 | 0.22888 | -121.9162 | 0.041198 | -0.054932 | -121.9025 | 0.23804 | 0.13733 | 0.19226 | -121.9116 | 0.37537 | 0.2655 | 0.27923 | -122.0673 | 0.27923 | 0.27008 | 0.10986 | -122.2366
998.0781 | 122.168 | -0.34332 | 121.9574 | -0.00091566 | 0.015402 | 0.0016619 | 0.0080301 | 0.054006 | -0.0045629 | -0.0044007 | -0.0084684 | -0.0017858 | -0.038467 | 0.033667 | 0.0091665 | -0.015515 | 0 | 0.041199 | 0.07782 | 0.082397 | 0.059509 | 0 | -0.14191 | -0.059509 | -0.1236 | -0.11444 | -0.064087 | -0.041199 | -0.25635 | -0.32044 | 0.34332 | 0.20142 | -121.8979 | 0.38452 | 0.42572 | 0.2243 | -121.9574 | 0.086975 | 0.022888 | -122.0215 | 0.28381 | 0.22888 | 0.20599 | -121.9986 | 0.40283 | 0.34332 | 0.42114 | -122.0993 | 0.27924 | 0.30212 | 0.21973 | -122.2778
999.8438 | 122.287 | -0.3067 | 121.8933 | -0.00091566 | 0.014334 | -0.0021833 | 0.0031167 | 0.05422 | 0.0020593 | -0.0031189 | -0.00083936 | 0.003341 | -0.037185 | 0.035376 | 0.013225 | -0.017011 | 0.009155 | -0.022888 | -0.004578 | 0.054932 | 0.068665 | -0.041199 | -0.17853 | -0.068665 | -0.17853 | -0.16479 | -0.022888 | -0.018311 | -0.24719 | -0.34332 | 0.2655 | 0.12817 | -121.8246 | 0.28381 | 0.36163 | 0.23346 | -121.8842 | 0.05951 | -0.036621 | -121.9162 | 0.23804 | 0.14191 | 0.17853 | -121.9116 | 0.37537 | 0.31586 | 0.30212 | -122.0718 | 0.28381 | 0.28839 | 0.12817 | -122.2366
1001.5469 | 122.2961 | -0.33875 | 121.8979 | -0.00091566 | 0.015402 | -0.00090151 | 0.0011941 | 0.054433 | -0.0017859 | -0.0026917 | -0.00083936 | 0.006759 | -0.036972 | 0.038367 | 0.015361 | -0.015943 | -0.073242 | -0.11902 | -0.07782 | 0.004578 | 0.068665 | -0.054932 | -0.17853 | -0.13733 | -0.27466 | -0.23346 | -0.032043 | -0.022888 | -0.28839 | -0.3479 | 0.28381 | 0.16022 | -121.8292 | 0.21973 | 0.34332 | 0.18311 | -121.9711 | 0.050354 | -0.009155 | -121.9299 | 0.20142 | 0.10529 | 0.11444 | -121.9208 | 0.40741 | 0.2655 | 0.26093 | -122.0764 | 0.3067 | 0.31586 | 0.064087 | -122.2458
1003.2344 | 122.3236 | -0.30212 | 121.8933 | -0.00091566 | 0.016684 | 0.0012347 | 0.0061075 | 0.052724 | -0.0013587 | -0.0033325 | -0.00083936 | 0.0046228 | -0.036331 | 0.036444 | 0.014507 | -0.017224 | -0.018311 | -0.041199 | -0.009155 | 0.050354 | 0.054932 | -0.045776 | -0.17853 | -0.073242 | -0.17853 | -0.15106 | -0.041199 | -0.018311 | -0.23804 | -0.33417 | 0.25635 | 0.1236 | -121.8384 | 0.26093 | 0.35248 | 0.22888 | -121.9116 | 0.064087 | -0.032043 | -121.9345 | 0.22888 | 0.15106 | 0.1831 | -121.9116 | 0.35706 | 0.28381 | 0.29297 | -122.0718 | 0.26093 | 0.28381 | 0.1236 | -122.2275
1004.9844 | 122.1909 | -0.35706 | 121.9345 | 0.0067138 | 0.013052 | 0.0020893 | 0.0048257 | 0.054006 | -0.0073401 | -0.0044007 | -0.0084684 | -0.0005042 | -0.037399 | 0.033026 | 0.013012 | -0.015302 | 0.018311 | 0.027466 | 0.073242 | 0.059509 | 0.036621 | 0 | -0.1236 | -0.064087 | -0.14648 | -0.10071 | -0.064087 | -0.041199 | -0.22888 | -0.32044 | 0.35706 | 0.23346 | -121.8979 | 0.38452 | 0.41656 | 0.1831 | -121.9162 | 0.12817 | 0.036621 | -121.9986 | 0.29297 | 0.25635 | 0.21973 | -121.9757 | 0.39368 | 0.37537 | 0.4303 | -122.0581 | 0.29297 | 0.31586 | 0.21057 | -122.2549
1006.6719 | 122.3373 | -0.30212 | 121.9116 | -0.00091566 | 0.012412 | 0.0010211 | 0.0046121 | 0.053152 | 0.00035029 | -0.0037597 | -0.016098 | 0.000564 | -0.038681 | 0.035376 | 0.013012 | -0.016797 | -0.004578 | -0.022888 | 0.018311 | 0.054932 | 0.050354 | -0.013733 | -0.15106 | -0.036621 | -0.12817 | -0.10986 | -0.054932 | -0.045776 | -0.23346 | -0.3067 | 0.28839 | 0.15106 | -121.8613 | 0.27924 | 0.35706 | 0.20599 | -121.9162 | 0.068665 | -0.004578 | -121.9666 | 0.2655 | 0.19226 | 0.19684 | -121.9574 | 0.35248 | 0.29755 | 0.32044 | -122.0627 | 0.24719 | 0.25635 | 0.17395 | -122.2183
1008.4219 | 122.3099 | -0.31586 | 121.9345 | 0.0067138 | 0.012839 | 0.0010211 | 0.0046121 | 0.053365 | -0.00071771 | -0.0035461 | 0.0067901 | 0.0007776 | -0.037399 | 0.036017 | 0.013012 | -0.015943 | 0.018311 | -0.013733 | 0.022888 | 0.054932 | 0.064087 | -0.013733 | -0.15106 | -0.027466 | -0.15106 | -0.091553 | -0.064087 | -0.068665 | -0.21515 | -0.28839 | 0.30212 | 0.16479 | -121.8704 | 0.30212 | 0.37079 | 0.20599 | -121.9162 | 0.10071 | 0.027466 | -121.9986 | 0.28839 | 0.2243 | 0.19684 | -122.0032 | 0.37994 | 0.33417 | 0.33875 | -122.0856 | 0.25177 | 0.24719 | 0.16479 | -122.2229
1010.1094 | 122.3007 | -0.30212 | 121.9162 | -0.016174 | 0.014548 | -4.6912e-05 | 0.0037577 | 0.055288 | -0.00029051 | -0.0020507 | -0.00083936 | 0.0044092 | -0.036117 | 0.035162 | 0.013225 | -0.01637 | -0.059509 | -0.13733 | -0.073242 | 0 | 0.09613 | -0.050354 | -0.16937 | -0.13733 | -0.27924 | -0.24261 | -0.022888 | -0.022888 | -0.2655 | -0.3479 | 0.25177 | 0.13275 | -121.8201 | 0.16479 | 0.30212 | 0.16937 | -121.9757 | 0.036621 | -0.045776 | -121.9391 | 0.16479 | 0.059509 | 0.10528 | -121.9391 | 0.39825 | 0.24261 | 0.22888 | -122.0856 | 0.27924 | 0.27924 | 0.022888 | -122.2641
1011.8594 | 122.2412 | -0.35248 | 121.9391 | -0.016174 | 0.009848 | 0.0010211 | 0.0063211 | 0.052938 | -0.0088355 | -0.0046143 | -0.00083936 | -0.001145 | -0.036331 | 0.035803 | 0.0076711 | -0.01637 | -0.041199 | -0.027466 | 0.018311 | 0.064087 | 0.041199 | -0.013733 | -0.15106 | -0.10986 | -0.16022 | -0.1236 | -0.054932 | -0.036621 | -0.25635 | -0.32501 | 0.33875 | 0.20142 | -121.8979 | 0.32501 | 0.41657 | 0.21515 | -121.9803 | 0.09613 | 0.027466 | -121.994 | 0.24262 | 0.22888 | 0.20142 | -121.9757 | 0.39368 | 0.31128 | 0.37079 | -122.0901 | 0.29755 | 0.31586 | 0.19226 | -122.2641
1013.5469 | 122.3099 | -0.33417 | 121.907 | -0.00091566 | 0.015402 | -0.0011151 | 0.0048257 | 0.055288 | 0.0014185 | -0.0037597 | -0.0084684 | 0.003982 | -0.036117 | 0.037726 | 0.014721 | -0.017011 | 0.013733 | -0.059509 | -0.013733 | 0.054932 | 0.068665 | -0.045776 | -0.16937 | -0.050354 | -0.17395 | -0.15106 | -0.022888 | -0.027466 | -0.24719 | -0.32044 | 0.28839 | 0.16479 | -121.8384 | 0.27466 | 0.3891 | 0.22431 | -121.8933 | 0.086975 | 0.013732 | -121.9299 | 0.28381 | 0.1831 | 0.16937 | -121.9345 | 0.40283 | 0.3479 | 0.32043 | -122.0764 | 0.31128 | 0.3067 | 0.16022 | -122.2275
1015.2344 | 122.3145 | -0.3067 | 121.9299 | 0.0067138 | 0.018393 | -0.00047431 | 0.0058939 | 0.055074 | -0.00029051 | -0.0022643 | -0.0084684 | 0.0044092 | -0.036117 | 0.036444 | 0.011303 | -0.016584 | 0.004578 | -0.050354 | -0.004578 | 0.036621 | 0.082397 | -0.032043 | -0.16479 | -0.07782 | -0.17395 | -0.16937 | -0.018311 | 0 | -0.25177 | -0.32044 | 0.27466 | 0.14191 | -121.8475 | 0.25635 | 0.34332 | 0.20142 | -121.9254 | 0.054932 | -0.013733 | -121.9482 | 0.22888 | 0.13733 | 0.15106 | -121.9299 | 0.3891 | 0.31128 | 0.30212 | -122.0947 | 0.28839 | 0.3067 | 0.13275 | -122.2504
1017 | 122.287 | -0.32501 | 121.962 | -0.00091566 | 0.013266 | -0.00047431 | 0.0024759 | 0.056783 | 0.00056389 | -0.0026917 | -0.00083936 | 0.0041956 | -0.037826 | 0.036017 | 0.013652 | -0.017865 | -0.027466 | -0.091553 | -0.027466 | 0.022888 | 0.068665 | -0.054932 | -0.16937 | -0.10986 | -0.23346 | -0.2243 | -0.041199 | -0.013733 | -0.2655 | -0.32501 | 0.27008 | 0.15564 | -121.8933 | 0.23346 | 0.3479 | 0.19226 | -121.9894 | 0.059509 | 0 | -122.0032 | 0.21515 | 0.10071 | 0.10071 | -121.9757 | 0.39368 | 0.29755 | 0.29755 | -122.1313 | 0.28381 | 0.31128 | 0.091553 | -122.287
1018.6875 | 122.319 | -0.32044 | 121.9116 | -0.0085447 | 0.016043 | -0.00047431 | 0.0056803 | 0.055715 | -0.0032813 | -0.0018371 | -0.00083936 | 0.003341 | -0.035904 | 0.034308 | 0.012157 | -0.014875 | -0.022888 | -0.068665 | -0.032043 | 0.045776 | 0.086975 | -0.036621 | -0.17395 | -0.10529 | -0.19226 | -0.16937 | -0.041199 | -0.018311 | -0.27008 | -0.3479 | 0.28381 | 0.14649 | -121.8246 | 0.25177 | 0.36621 | 0.21973 | -121.9345 | 0.050354 | -0.027465 | -121.9528 | 0.21515 | 0.15106 | 0.17853 | -121.9299 | 0.40741 | 0.29755 | 0.28839 | -122.0856 | 0.27924 | 0.30212 | 0.12817 | -122.2595
1020.4375 | 122.2412 | -0.35248 | 121.9666 | -0.00091566 | 0.015402 | 0.0018757 | 0.0082437 | 0.053152 | -0.0041357 | -0.0048279 | -0.00083936 | -0.0007178 | -0.030777 | 0.035376 | 0.0087391 | -0.017224 | -0.073242 | -0.091553 | -0.059509 | 0 | 0.064087 | -0.059509 | -0.19226 | -0.16479 | -0.23804 | -0.20599 | -0.022888 | 0 | -0.2655 | -0.33875 | 0.29297 | 0.16022 | -121.9025 | 0.26093 | 0.35248 | 0.19226 | -122.0398 | 0.086975 | 0.013733 | -121.9894 | 0.18768 | 0.14648 | 0.13275 | -121.9666 | 0.41657 | 0.27924 | 0.29297 | -122.1588 | 0.32959 | 0.35248 | 0.11444 | -122.3053
1022.1875 | 122.2321 | -0.35248 | 121.9574 | -0.0085447 | 0.012198 | 0.0016619 | 0.0063211 | 0.054433 | -0.0054175 | -0.0052551 | -0.00083936 | 0.000564 | -0.032913 | 0.035162 | 0.011089 | -0.016797 | 0.027466 | 0.027466 | 0.07782 | 0.068665 | 0.032043 | 0 | -0.13275 | -0.036621 | -0.14191 | -0.082397 | -0.068665 | -0.041199 | -0.23804 | -0.31586 | 0.35248 | 0.21973 | -121.9254 | 0.37994 | 0.42114 | 0.20142 | -121.9299 | 0.11444 | 0.036621 | -122.0261 | 0.31586 | 0.27008 | 0.23346 | -121.9986 | 0.38452 | 0.37994 | 0.4303 | -122.0901 | 0.28381 | 0.31128 | 0.21057 | -122.2733
1023.9375 | 122.2183 | -0.36163 | 121.9299 | -0.00091566 | 0.011771 | 0.0033709 | 0.0043985 | 0.055929 | -0.0045629 | -0.0065369 | -0.023727 | -0.0026404 | -0.036758 | 0.035803 | 0.0091665 | -0.017011 | 0.032043 | 0.045776 | 0.082397 | 0.086975 | 0.022888 | -0.009155 | -0.15106 | -0.041199 | -0.086975 | -0.059509 | -0.068665 | -0.050354 | -0.21973 | -0.33417 | 0.35248 | 0.21057 | -121.907 | 0.40741 | 0.44861 | 0.23804 | -121.8979 | 0.14191 | 0.027466 | -121.9986 | 0.32043 | 0.30212 | 0.27466 | -121.9803 | 0.38452 | 0.39368 | 0.44403 | -122.081 | 0.29297 | 0.31128 | 0.27466 | -122.2641
1025.625 | 122.3099 | -0.32501 | 121.9482 | -0.00091566 | 0.012839 | 0.00080749 | 0.0011941 | 0.055288 | -0.00093131 | -0.0041869 | -0.00083936 | 0.0003504 | -0.037613 | 0.032812 | 0.013866 | -0.017224 | 0.059509 | 0.018311 | 0.073242 | 0.09613 | 0.036621 | 0 | -0.1236 | -0.018311 | -0.14191 | -0.091553 | -0.068665 | -0.064087 | -0.22888 | -0.30212 | 0.32501 | 0.20142 | -121.9116 | 0.34332 | 0.42114 | 0.21973 | -121.8887 | 0.09613 | 0.022888 | -122.0169 | 0.3067 | 0.23346 | 0.21057 | -122.0123 | 0.36163 | 0.38452 | 0.39825 | -122.0718 | 0.25635 | 0.26093 | 0.18311 | -122.2504
1027.3906 | 122.2092 | -0.36621 | 121.962 | -0.0085447 | 0.012839 | -0.00090151 | 0.0069621 | 0.052083 | -0.0049903 | -0.0058959 | -0.016098 | -0.0019996 | -0.035049 | 0.031531 | 0.0093801 | -0.017011 | 0.027466 | 0.027466 | 0.07782 | 0.086975 | 0.027466 | -0.027466 | -0.13275 | -0.041199 | -0.12817 | -0.091553 | -0.073242 | -0.036621 | -0.2243 | -0.32501 | 0.33875 | 0.23346 | -121.9345 | 0.39368 | 0.45319 | 0.21973 | -121.9345 | 0.14191 | 0.041199 | -122.0352 | 0.32501 | 0.27466 | 0.23346 | -121.9986 | 0.39368 | 0.39368 | 0.44403 | -122.0947 | 0.29297 | 0.32959 | 0.23804 | -122.287
1029.1406 | 122.3236 | -0.32959 | 121.9482 | 0.0067138 | 0.014761 | 0.00016669 | 0.0020487 | 0.053152 | 0.00056389 | -0.0048279 | -0.00083936 | 0.0007776 | -0.033981 | 0.036017 | 0.012371 | -0.019147 | -0.064087 | -0.12817 | -0.073242 | 0.004578 | 0.07782 | -0.032043 | -0.17853 | -0.12817 | -0.30212 | -0.23346 | -0.018311 | -0.013733 | -0.27008 | -0.37994 | 0.29755 | 0.15106 | -121.8704 | 0.20142 | 0.33417 | 0.18311 | -122.0123 | 0.059509 | -0.050354 | -121.9666 | 0.20142 | 0.096131 | 0.14649 | -121.962 | 0.40741 | 0.2655 | 0.25635 | -122.1268 | 0.31128 | 0.31586 | 0.027466 | -122.3282
1030.9062 | 122.3007 | -0.35248 | 121.9482 | -0.00091566 | 0.0057892 | 0.0029437 | 0.00076686 | 0.054433 | -0.0066993 | -0.0048279 | -0.0084684 | -0.0022132 | -0.036972 | 0.034094 | 0.0089527 | -0.015943 | 0.022888 | 0.041199 | 0.064087 | 0.086975 | 0.036621 | -0.022888 | -0.13733 | -0.018311 | -0.10529 | -0.064087 | -0.068665 | -0.050354 | -0.21973 | -0.32501 | 0.32959 | 0.21515 | -121.9116 | 0.39368 | 0.43945 | 0.2243 | -121.9254 | 0.13275 | 0.027466 | -122.0169 | 0.33417 | 0.28839 | 0.26093 | -121.9986 | 0.3891 | 0.37537 | 0.41657 | -122.0856 | 0.28381 | 0.30212 | 0.24719 | -122.2733
1032.5938 | 122.2412 | -0.37537 | 121.994 | -0.016174 | 0.015189 | 0.0035847 | 0.0067483 | 0.052511 | -0.0058447 | -0.0039733 | -0.0084684 | 0.0001368 | -0.035476 | 0.033667 | 0.010234 | -0.016584 | -0.004578 | -0.013733 | 0.027466 | 0.045776 | 0.041199 | -0.004578 | -0.14191 | -0.082397 | -0.19226 | -0.12817 | -0.045776 | -0.032043 | -0.24261 | -0.32044 | 0.37079 | 0.23346 | -121.9528 | 0.36163 | 0.42114 | 0.18768 | -121.9986 | 0.13275 | 0.054931 | -122.0398 | 0.29297 | 0.24719 | 0.19226 | -122.0261 | 0.41656 | 0.37079 | 0.40283 | -122.1359 | 0.32959 | 0.34332 | 0.1831 | -122.3145
1034.3438 | 122.3007 | -0.33417 | 121.9162 | -0.00091566 | 0.016257 | -0.00026071 | 0.0020487 | 0.055074 | 0.0037683 | -0.0067505 | -0.00083936 | 0.0031274 | -0.034408 | 0.034308 | 0.016429 | -0.019574 | -0.009155 | -0.059509 | -0.022888 | 0.032043 | 0.082397 | -0.032043 | -0.16022 | -0.09613 | -0.25177 | -0.21515 | -0.036621 | -0.036621 | -0.25635 | -0.35706 | 0.30212 | 0.17395 | -121.8338 | 0.27466 | 0.36621 | 0.19226 | -121.9254 | 0.077819 | -0.022889 | -121.9528 | 0.23804 | 0.11902 | 0.14191 | -121.9528 | 0.41656 | 0.32501 | 0.31128 | -122.0764 | 0.29755 | 0.29755 | 0.082397 | -122.2733
1036.0938 | 122.2549 | -0.37537 | 121.9986 | -0.00091566 | 0.012839 | 0.0025165 | 0.0043985 | 0.052297 | -0.0071265 | -0.0052551 | -0.00083936 | -0.002854 | -0.033767 | 0.033026 | 0.010875 | -0.017011 | -0.032043 | -0.045776 | 0.004578 | 0.041199 | 0.041199 | -0.009155 | -0.13275 | -0.082397 | -0.19684 | -0.13275 | -0.041199 | -0.050354 | -0.25635 | -0.32044 | 0.36621 | 0.24261 | -121.9574 | 0.32959 | 0.41656 | 0.17395 | -122.0306 | 0.11902 | 0.054931 | -122.0398 | 0.29297 | 0.24261 | 0.18768 | -122.049 | 0.41656 | 0.34332 | 0.37994 | -122.1313 | 0.33417 | 0.32501 | 0.17853 | -122.319
1037.875 | 122.2412 | -0.37537 | 121.9437 | -0.00091566 | 0.014975 | 0.0016619 | 0.0076029 | 0.051229 | -0.0026403 | -0.0041869 | -0.00083936 | 0.0014184 | -0.034408 | 0.034308 | 0.01173 | -0.017011 | -0.036621 | -0.07782 | -0.022888 | -0.009155 | 0.064087 | -0.045776 | -0.1831 | -0.13733 | -0.27008 | -0.20142 | -0.022888 | -0.022888 | -0.28381 | -0.35248 | 0.32959 | 0.19226 | -121.8796 | 0.29755 | 0.36621 | 0.17395 | -121.9803 | 0.091553 | 0.022888 | -121.9666 | 0.23804 | 0.17395 | 0.15106 | -121.9666 | 0.43945 | 0.33874 | 0.35248 | -122.1268 | 0.35248 | 0.35248 | 0.10528 | -122.2961
1039.5625 | 122.2504 | -0.39368 | 121.9803 | -0.0085447 | 0.014975 | 0.0010211 | 0.0054667 | 0.053792 | -0.0032813 | -0.0033325 | -0.0084684 | -0.0015722 | -0.034408 | 0.033026 | 0.012157 | -0.017865 | 0.018311 | 0.018311 | 0.059509 | 0.068665 | 0.041199 | -0.004578 | -0.1236 | -0.059509 | -0.20142 | -0.11902 | -0.054932 | -0.059509 | -0.24719 | -0.32959 | 0.3891 | 0.27008 | -121.9391 | 0.41199 | 0.46234 | 0.19226 | -121.962 | 0.14649 | 0.064087 | -122.0352 | 0.33417 | 0.27466 | 0.21057 | -122.0398 | 0.43488 | 0.41199 | 0.45319 | -122.1039 | 0.33875 | 0.33417 | 0.19226 | -122.3099
1041.3125 | 122.3831 | -0.33417 | 121.9528 | 0.014343 | 0.012198 | 0.00016669 | 0.0035441 | 0.054433 | 0.00013669 | -0.0035461 | -0.0084684 | 0.0003504 | -0.032486 | 0.036017 | 0.015361 | -0.019574 | -0.009155 | -0.036621 | 0.013733 | 0.041199 | 0.064087 | -0.018311 | -0.14648 | -0.036621 | -0.16937 | -0.10986 | -0.073242 | -0.073242 | -0.21973 | -0.32501 | 0.31586 | 0.18768 | -121.8887 | 0.29755 | 0.37537 | 0.18768 | -121.962 | 0.11444 | 0.009155 | -122.0261 | 0.29755 | 0.2243 | 0.21515 | -122.0261 | 0.39825 | 0.32501 | 0.3479 | -122.0993 | 0.26092 | 0.26092 | 0.16479 | -122.2778
1043.0781 | 122.3877 | -0.32501 | 121.9528 | 0.0067138 | 0.014761 | 0.0023029 | 0.0022623 | 0.054433 | 0.00099129 | -0.0033325 | -0.00083936 | 0.0027002 | -0.034408 | 0.034735 | 0.013225 | -0.016156 | -0.054932 | -0.09613 | -0.082397 | -0.013733 | 0.082397 | -0.041199 | -0.1831 | -0.11902 | -0.2655 | -0.21057 | -0.032043 | -0.032043 | -0.27008 | -0.3479 | 0.28381 | 0.14191 | -121.8704 | 0.22888 | 0.31128 | 0.16937 | -122.0078 | 0.054931 | -0.022888 | -121.9849 | 0.20599 | 0.11444 | 0.13733 | -121.9849 | 0.40741 | 0.27008 | 0.24262 | -122.1359 | 0.29297 | 0.29297 | 0.059509 | -122.3007
1044.8281 | 122.3373 | -0.32501 | 121.9528 | 0.0067138 | 0.014548 | -0.00026071 | 0.0037577 | 0.052297 | -7.6908e-05 | -0.0024779 | -0.00083936 | 0.0027002 | -0.034835 | 0.036658 | 0.014507 | -0.016797 | -0.082397 | -0.13275 | -0.091553 | -0.004578 | 0.068665 | -0.041199 | -0.1831 | -0.11902 | -0.28381 | -0.23804 | -0.045776 | -0.022888 | -0.27466 | -0.35706 | 0.28381 | 0.14191 | -121.8842 | 0.19226 | 0.32043 | 0.17853 | -122.0352 | 0.050354 | -0.032044 | -121.9986 | 0.20599 | 0.086975 | 0.11902 | -121.9757 | 0.39368 | 0.24262 | 0.23346 | -122.1359 | 0.27924 | 0.30212 | 0.041199 | -122.3099
1046.5156 | 122.319 | -0.33417 | 121.9391 | -0.00091566 | 0.014334 | -0.00090151 | 0.0033305 | 0.05187 | 0.00013669 | -0.0024779 | -0.00083936 | 0.0027002 | -0.033981 | 0.033667 | 0.013225 | -0.016156 | -0.054932 | -0.068665 | -0.059509 | 0.018311 | 0.091553 | -0.022888 | -0.18768 | -0.11444 | -0.2655 | -0.2243 | -0.027466 | 0.009155 | -0.26093 | -0.33875 | 0.31128 | 0.14648 | -121.8475 | 0.2655 | 0.35248 | 0.20599 | -121.994 | 0.073242 | -0.004578 | -121.9666 | 0.21973 | 0.10986 | 0.11444 | -121.9299 | 0.42572 | 0.27924 | 0.27466 | -122.1268 | 0.3067 | 0.34332 | 0.068664 | -122.2778
1048.2656 | 122.3831 | -0.32044 | 121.9711 | -0.016174 | 0.0096344 | -0.0011151 | 0.0052531 | 0.053792 | -0.0037085 | -0.0022643 | -0.0084684 | -0.002854 | -0.033554 | 0.033453 | 0.011516 | -0.017438 | 0.013733 | 0.022888 | 0.045776 | 0.068665 | 0.022888 | -0.004578 | -0.13275 | -0.027466 | -0.14191 | -0.09613 | -0.09613 | -0.064087 | -0.21973 | -0.32501 | 0.31586 | 0.18768 | -121.9482 | 0.34332 | 0.3891 | 0.20142 | -121.9574 | 0.10071 | -0.004577 | -122.0673 | 0.29297 | 0.22431 | 0.22888 | -122.0352 | 0.34332 | 0.33417 | 0.36621 | -122.1039 | 0.22431 | 0.25635 | 0.17853 | -122.2961
1050.0156 | 122.2321 | -0.37994 | 121.994 | -0.0085447 | 0.014975 | 0.0023029 | 0.0086709 | 0.054647 | -0.0049903 | -0.0048279 | -0.00083936 | -0.0019996 | -0.035263 | 0.035162 | 0.0083119 | -0.01637 | -0.013733 | 0.018311 | 0.041199 | 0.054932 | 0.068665 | -0.041199 | -0.15106 | -0.11444 | -0.20142 | -0.15564 | -0.041199 | -0.009155 | -0.2655 | -0.33417 | 0.33875 | 0.22888 | -121.9254 | 0.39826 | 0.43488 | 0.20599 | -122.0078 | 0.11444 | 0.045777 | -122.0352 | 0.2655 | 0.2243 | 0.17853 | -122.0032 | 0.44861 | 0.36621 | 0.42114 | -122.1451 | 0.33875 | 0.37079 | 0.17853 | -122.3282
1051.7031 | 122.3145 | -0.37079 | 121.962 | 0.0067138 | 0.012198 | 0.0023029 | 0.0056803 | 0.052297 | -0.0073401 | -0.0041869 | -0.00083936 | -0.0017858 | -0.033126 | 0.034094 | 0.0091665 | -0.01637 | 0.009155 | 0.027466 | 0.045776 | 0.086975 | 0.036621 | -0.004578 | -0.15564 | -0.054932 | -0.11902 | -0.054932 | -0.064087 | -0.045776 | -0.24719 | -0.3479 | 0.36621 | 0.21515 | -121.9254 | 0.39825 | 0.45776 | 0.24261 | -121.9528 | 0.1236 | 0.022889 | -122.0261 | 0.31586 | 0.31586 | 0.29297 | -122.0078 | 0.40741 | 0.37994 | 0.41656 | -122.1176 | 0.3067 | 0.32501 | 0.25177 | -122.3099
1053.4688 | 122.3831 | -0.32959 | 121.907 | 0.0067138 | 0.013907 | -0.00068791 | 0.0022623 | 0.054433 | 0.00099129 | -0.0016235 | -0.00083936 | 0.002273 | -0.034622 | 0.034735 | 0.01408 | -0.019361 | -0.009155 | -0.054932 | -0.022888 | 0.036621 | 0.086975 | -0.036621 | -0.16022 | -0.082397 | -0.20599 | -0.17395 | -0.054932 | -0.004578 | -0.25635 | -0.36163 | 0.29297 | 0.16937 | -121.8201 | 0.27466 | 0.36621 | 0.19684 | -121.9162 | 0.073242 | -0.032043 | -121.962 | 0.24719 | 0.15564 | 0.18768 | -121.9116 | 0.41656 | 0.32043 | 0.3067 | -122.0673 | 0.27466 | 0.32501 | 0.1236 | -122.2687
1055.2344 | 122.2916 | -0.37079 | 121.9757 | 0.0067138 | 0.0072846 | 0.0046527 | 0.0033305 | 0.052297 | -0.0064855 | -0.0052551 | -0.016098 | -0.0034948 | -0.036972 | 0.031744 | 0.011943 | -0.015729 | 0.045776 | 0.073242 | 0.086975 | 0.086975 | 0.036621 | -0.009155 | -0.14191 | -0.022888 | -0.10529 | -0.059509 | -0.091553 | -0.059509 | -0.25177 | -0.32959 | 0.36163 | 0.22888 | -121.9391 | 0.44403 | 0.45776 | 0.22888 | -121.9299 | 0.11902 | 0.041199 | -122.0673 | 0.3479 | 0.31128 | 0.27008 | -122.0352 | 0.40741 | 0.41656 | 0.45776 | -122.1176 | 0.27924 | 0.31128 | 0.2655 | -122.3053
1057 | 122.3007 | -0.36163 | 121.9849 | -0.016174 | 0.011984 | 0.0012347 | 0.0071757 | 0.053792 | -0.0052039 | -0.0054687 | -0.0084684 | -0.0017858 | -0.035049 | 0.034308 | 0.0098073 | -0.016797 | 0.041199 | 0.059509 | 0.07782 | 0.086975 | 0.041199 | -0.027466 | -0.13275 | -0.018311 | -0.10071 | -0.064087 | -0.064087 | -0.059509 | -0.25177 | -0.33875 | 0.33417 | 0.22888 | -121.9437 | 0.42114 | 0.44861 | 0.21973 | -121.9437 | 0.10986 | 0.022888 | -122.049 | 0.34332 | 0.29755 | 0.27466 | -122.0444 | 0.40283 | 0.40283 | 0.43945 | -122.1176 | 0.29755 | 0.30212 | 0.26092 | -122.3236
1058.6875 | 122.3969 | -0.20599 | 122.0856 | -0.00091566 | 0.015402 | 0.0020893 | 0.0037577 | 0.052724 | 0.0027003 | -0.0046143 | -0.0084684 | 0.0014184 | -0.034835 | 0.036658 | 0.012371 | -0.019361 | -0.045776 | -0.064087 | -0.050354 | 0.022888 | 0.068665 | -0.054932 | -0.1831 | -0.12817 | -0.10986 | -0.23346 | -0.073242 | -0.068665 | -0.15564 | -0.23346 | 0.15106 | 0.022889 | -122.0169 | 0.14191 | 0.22888 | 0.20599 | -122.1313 | 0.050354 | -0.027465 | -122.1588 | 0.07782 | -0.027465 | 0 | -122.1542 | 0.27466 | 0.16022 | 0.15564 | -122.2687 | 0.13275 | 0.13733 | 0.096131 | -122.319
1060.4531 | 122.2824 | -0.22888 | 122.1451 | 0.0067138 | 0.012412 | 0.0033709 | 0.0039713 | 0.05187 | -0.0054175 | -0.0050415 | -0.016098 | -0.001145 | -0.035049 | 0.037512 | 0.0051075 | -0.016584 | 0.032043 | 0.059509 | 0.07782 | 0.09613 | 0.032043 | -0.018311 | -0.13733 | -0.073242 | 0.032043 | -0.1236 | -0.10529 | -0.11902 | -0.1236 | -0.21515 | 0.21057 | 0.091553 | -122.113 | 0.28839 | 0.32501 | 0.23346 | -122.113 | 0.10529 | 0.013733 | -122.2504 | 0.15564 | 0.10529 | 0.091553 | -122.2641 | 0.26093 | 0.26093 | 0.3067 | -122.2824 | 0.1236 | 0.10986 | 0.26093 | -122.3602
1062.2031 | 122.3831 | -0.21057 | 122.0856 | -0.00091566 | 0.012412 | -4.6912e-05 | 0.0033305 | 0.051015 | 0.00077749 | -0.0029053 | -0.00083936 | 0.0009912 | -0.035263 | 0.042639 | 0.010021 | -0.016584 | -0.009155 | -0.036621 | 0.004578 | 0.027466 | 0.059509 | -0.004578 | -0.16022 | -0.086975 | -0.050354 | -0.16937 | -0.10986 | -0.11902 | -0.12817 | -0.21057 | 0.20599 | 0.050354 | -122.0261 | 0.17395 | 0.23804 | 0.18768 | -122.0947 | 0.082397 | 0 | -122.1954 | 0.1236 | 0.041198 | 0.041198 | -122.2046 | 0.27008 | 0.20142 | 0.21515 | -122.2458 | 0.10071 | 0.091552 | 0.16022 | -122.2961
1063.9375 | 122.2916 | -0.2243 | 122.113 | -0.0085447 | 0.011557 | 0.0010211 | 0.0054667 | 0.050588 | -0.0060583 | -0.0048279 | 0.0067901 | -0.001145 | -0.035904 | 0.037298 | 0.0061757 | -0.01637 | 0.064087 | 0.068665 | 0.091553 | 0.086975 | 0.036621 | -0.004578 | -0.15564 | -0.068665 | 0.027466 | -0.10071 | -0.10071 | -0.10529 | -0.11444 | -0.21515 | 0.21973 | 0.068664 | -122.0764 | 0.29297 | 0.31128 | 0.24261 | -122.049 | 0.10986 | 0.009155 | -122.2137 | 0.15564 | 0.1236 | 0.11444 | -122.2183 | 0.26093 | 0.28839 | 0.31586 | -122.2687 | 0.1236 | 0.11902 | 0.25177 | -122.3282
1065.625 | 122.3007 | -0.25177 | 122.1268 | -0.00091566 | 0.010703 | 0.0037983 | 0.0043985 | 0.053365 | -0.0041357 | -0.0039733 | -0.00083936 | -0.0013586 | -0.036972 | 0.039862 | 0.0078847 | -0.01637 | -0.041199 | -0.027466 | 0.018311 | 0.059509 | 0.059509 | -0.013733 | -0.15106 | -0.13275 | -0.073242 | -0.16479 | -0.091553 | -0.10071 | -0.11444 | -0.19226 | 0.23804 | 0.10071 | -122.0673 | 0.2243 | 0.31128 | 0.21057 | -122.168 | 0.13733 | 0.059509 | -122.2183 | 0.11902 | 0.086975 | 0.027466 | -122.2275 | 0.31128 | 0.21057 | 0.27008 | -122.2778 | 0.16022 | 0.15106 | 0.17853 | -122.319
1067.375 | 122.2778 | -0.25177 | 122.1451 | -0.0085447 | 0.010489 | 0.0042255 | 0.0031167 | 0.05721 | -0.0054175 | -0.0050415 | -0.0084684 | -0.0024268 | -0.037613 | 0.037939 | 0.0087391 | -0.017652 | -0.018311 | -0.022888 | 0.022888 | 0.036621 | 0.045776 | -0.013733 | -0.13733 | -0.12817 | -0.07782 | -0.19684 | -0.09613 | -0.10529 | -0.11902 | -0.20599 | 0.23804 | 0.11444 | -122.0993 | 0.22888 | 0.28839 | 0.17395 | -122.1634 | 0.13275 | 0.045776 | -122.2412 | 0.1236 | 0.054932 | 0.009156 | -122.2504 | 0.29755 | 0.23346 | 0.27466 | -122.2824 | 0.15564 | 0.14648 | 0.17395 | -122.3511
1069.125 | 122.3602 | -0.21515 | 122.0947 | 0.0067138 | 0.014761 | 0.00038029 | 0.0067483 | 0.055288 | 0.0018457 | -0.0037597 | -0.00083936 | 0.0035546 | -0.034408 | 0.039648 | 0.0061757 | -0.018506 | -0.059509 | -0.091553 | -0.064087 | 0.027466 | 0.09613 | -0.059509 | -0.17395 | -0.16022 | -0.13733 | -0.27924 | -0.068665 | -0.059509 | -0.15564 | -0.24261 | 0.15564 | 0.041199 | -121.9986 | 0.1236 | 0.24261 | 0.20142 | -122.1542 | 0.059509 | -0.027466 | -122.1634 | 0.054932 | -0.064087 | -0.036621 | -122.1542 | 0.31128 | 0.15564 | 0.15106 | -122.2687 | 0.14648 | 0.15564 | 0.07782 | -122.3373
1070.875 | 122.3282 | -0.2243 | 122.1085 | 0.0067138 | 0.010062 | 0.0014483 | 0.0065347 | 0.05187 | -0.0039221 | -0.0046143 | -0.0084684 | -0.0024268 | -0.037613 | 0.038794 | 0.0040395 | -0.018079 | 0.032043 | 0.041199 | 0.068665 | 0.082397 | 0.045776 | -0.018311 | -0.14648 | -0.07782 | 0.018311 | -0.10529 | -0.10986 | -0.13275 | -0.11902 | -0.19684 | 0.20599 | 0.07782 | -122.0627 | 0.2655 | 0.3067 | 0.22888 | -122.0764 | 0.10529 | 0.027466 | -122.2183 | 0.14648 | 0.11902 | 0.091552 | -122.2412 | 0.27008 | 0.25635 | 0.29297 | -122.2549 | 0.11444 | 0.091553 | 0.24261 | -122.3053
1072.6406 | 122.3969 | -0.20599 | 122.0947 | -0.0085447 | 0.016043 | 0.00038029 | 0.0022623 | 0.056356 | 0.0033411 | -0.0052551 | -0.0084684 | 0.0035546 | -0.036544 | 0.039648 | 0.0089527 | -0.020215 | -0.032043 | -0.050354 | -0.018311 | 0.045776 | 0.07782 | -0.050354 | -0.17395 | -0.11444 | -0.073242 | -0.23346 | -0.086975 | -0.091553 | -0.14648 | -0.22888 | 0.15564 | 0.032044 | -122.0169 | 0.15564 | 0.25177 | 0.21973 | -122.1268 | 0.05951 | -0.022888 | -122.1817 | 0.091553 | -0.027465 | -0.004577 | -122.1863 | 0.28381 | 0.17395 | 0.18768 | -122.2687 | 0.11902 | 0.11444 | 0.13275 | -122.3236
1074.3281 | 122.2824 | -0.23804 | 122.1497 | 0.0067138 | 0.01348 | 0.0025165 | 0.0041849 | 0.053365 | -0.0047765 | -0.0039733 | -0.0084684 | -0.0019996 | -0.035263 | 0.037726 | 0.0051075 | -0.018506 | 0.027466 | 0.059509 | 0.073242 | 0.10529 | 0.041199 | -0.009155 | -0.15106 | -0.07782 | 0.027466 | -0.13733 | -0.11444 | -0.09613 | -0.10529 | -0.19684 | 0.22888 | 0.086975 | -122.1085 | 0.29755 | 0.34332 | 0.25635 | -122.1222 | 0.13275 | 0.041199 | -122.2641 | 0.16022 | 0.10071 | 0.059509 | -122.2458 | 0.27924 | 0.2655 | 0.31128 | -122.3007 | 0.1236 | 0.14191 | 0.2655 | -122.3465
1076.0625 | 122.2733 | -0.25635 | 122.1542 | -0.00091566 | 0.015189 | 0.0018757 | 0.0063211 | 0.052297 | -0.0022131 | -0.0052551 | -0.00083936 | 0.000564 | -0.032913 | 0.037512 | 0.0051075 | -0.017652 | 0.004578 | -0.009155 | 0.013733 | 0.059509 | 0.068665 | -0.036621 | -0.16937 | -0.16022 | -0.082397 | -0.2243 | -0.073242 | -0.064087 | -0.13733 | -0.23804 | 0.21973 | 0.086975 | -122.0856 | 0.24719 | 0.31586 | 0.22888 | -122.1497 | 0.11902 | 0.018311 | -122.2275 | 0.096131 | 0.032044 | 0.013733 | -122.2183 | 0.32501 | 0.26093 | 0.27008 | -122.3236 | 0.18311 | 0.19226 | 0.17395 | -122.3923
1077.8125 | 122.2916 | -0.23804 | 122.1588 | -0.0085447 | 0.014548 | 0.0018757 | 0.0054667 | 0.054647 | -0.0043493 | -0.0052551 | -0.00083936 | -0.0039222 | -0.033554 | 0.040289 | 0.0063893 | -0.017438 | 0.054932 | 0.073242 | 0.091553 | 0.086975 | 0.045776 | 0 | -0.12817 | -0.064087 | 0.036621 | -0.10986 | -0.10529 | -0.10529 | -0.11444 | -0.18768 | 0.23804 | 0.10986 | -122.113 | 0.31128 | 0.32501 | 0.21515 | -122.1039 | 0.1236 | 0.050354 | -122.2641 | 0.17395 | 0.12817 | 0.07782 | -122.2641 | 0.28381 | 0.29297 | 0.32959 | -122.287 | 0.13275 | 0.13275 | 0.27466 | -122.3465
1079.5625 | 122.3694 | -0.21973 | 122.0993 | -0.00091566 | 0.015189 | -0.00068791 | 0.0048257 | 0.053365 | 0.0031275 | -0.0035461 | -0.00083936 | 0.0024866 | -0.032699 | 0.040289 | 0.0085255 | -0.018079 | -0.050354 | -0.07782 | -0.059509 | 0 | 0.073242 | -0.054932 | -0.17853 | -0.1831 | -0.12817 | -0.2655 | -0.068665 | -0.073242 | -0.16479 | -0.21973 | 0.16479 | 0.041199 | -122.0261 | 0.14191 | 0.21973 | 0.17853 | -122.1497 | 0.054932 | 0 | -122.168 | 0.036622 | -0.045776 | -0.045776 | -122.1725 | 0.29297 | 0.16937 | 0.16022 | -122.2778 | 0.15106 | 0.14649 | 0.091553 | -122.319
1081.25 | 122.2687 | -0.25177 | 122.1451 | -0.00091566 | 0.010275 | 0.0016619 | 0.0031167 | 0.052724 | -0.0037085 | -0.0037597 | -0.00083936 | -0.001145 | -0.037399 | 0.039862 | 0.0089527 | -0.017865 | 0.032043 | 0.041199 | 0.054932 | 0.068665 | 0.041199 | -0.013733 | -0.14191 | -0.073242 | -0.032043 | -0.14648 | -0.10071 | -0.086975 | -0.09613 | -0.18768 | 0.23804 | 0.10986 | -122.1039 | 0.29297 | 0.32044 | 0.21057 | -122.113 | 0.15564 | 0.064087 | -122.2458 | 0.17853 | 0.10529 | 0.041199 | -122.2321 | 0.29297 | 0.28381 | 0.3067 | -122.287 | 0.15106 | 0.16479 | 0.21973 | -122.3328
1083.0156 | 122.3419 | -0.22888 | 122.1359 | -0.00091566 | 0.017111 | 0.0012347 | 0.0084573 | 0.056569 | -0.0015723 | -0.0058959 | -0.0084684 | 0.002273 | -0.031204 | 0.039648 | 0.0053211 | -0.017224 | -0.073242 | -0.07782 | -0.064087 | 0 | 0.082397 | -0.059509 | -0.20599 | -0.17395 | -0.12817 | -0.2655 | -0.045776 | -0.068665 | -0.15564 | -0.22888 | 0.16937 | 0.022888 | -122.0535 | 0.15106 | 0.22888 | 0.20599 | -122.2092 | 0.073242 | 0 | -122.1817 | 0.054932 | -0.036621 | -0.036621 | -122.2046 | 0.31128 | 0.15564 | 0.16479 | -122.3419 | 0.18311 | 0.16022 | 0.10071 | -122.3648
1084.7656 | 122.4289 | -0.19226 | 122.1222 | -0.0085447 | 0.013907 | 0.0010211 | 0.0018351 | 0.054433 | 0.00035029 | -0.0050415 | 0.0067901 | 0.002273 | -0.033767 | 0.040503 | 0.0085255 | -0.01637 | -0.041199 | -0.073242 | -0.059509 | 0.013733 | 0.082397 | -0.050354 | -0.16022 | -0.1236 | -0.11902 | -0.21973 | -0.09613 | -0.059509 | -0.1236 | -0.2243 | 0.14191 | 0.032044 | -122.0398 | 0.11902 | 0.20599 | 0.17395 | -122.1634 | 0.068665 | -0.032043 | -122.2183 | 0.068665 | -0.027466 | 0.004577 | -122.1817 | 0.27466 | 0.15106 | 0.13275 | -122.2824 | 0.096131 | 0.13275 | 0.073242 | -122.3465
1086.4688 | 122.4243 | -0.19684 | 122.1451 | -0.00091566 | 0.013266 | 0.0018757 | 0.0052531 | 0.052297 | -0.00029051 | -0.00055532 | -0.0084684 | 0.003982 | -0.033981 | 0.041571 | 0.0080983 | -0.016584 | -0.050354 | -0.073242 | -0.027466 | 0.022888 | 0.07782 | -0.032043 | -0.16022 | -0.10071 | -0.073242 | -0.19226 | -0.10529 | -0.091553 | -0.10071 | -0.19226 | 0.1648 | 0.036621 | -122.0673 | 0.1236 | 0.21973 | 0.1831 | -122.1954 | 0.09613 | 0.004577 | -122.2504 | 0.09613 | 0.004577 | 0 | -122.2366 | 0.27466 | 0.14648 | 0.16937 | -122.3053 | 0.091552 | 0.10529 | 0.1236 | -122.3373
1088.2188 | 122.4197 | -0.19226 | 122.1313 | -0.00091566 | 0.013907 | 0.0018757 | 0.0026895 | 0.053792 | 0.00035029 | -0.0033325 | -0.00083936 | 0.0035546 | -0.032913 | 0.041785 | 0.0061757 | -0.018079 | -0.068665 | -0.10986 | -0.068665 | 0 | 0.086975 | -0.041199 | -0.16479 | -0.14648 | -0.13275 | -0.24261 | -0.059509 | -0.059509 | -0.1236 | -0.21057 | 0.15106 | 0.027466 | -122.0444 | 0.082398 | 0.19226 | 0.16479 | -122.2 | 0.068665 | -0.01831 | -122.1909 | 0.045777 | -0.050354 | -0.032044 | -122.1909 | 0.27924 | 0.1236 | 0.1236 | -122.2961 | 0.13275 | 0.13275 | 0.05951 | -122.3419
1089.9688 | 122.3465 | -0.2243 | 122.1451 | -0.016174 | 0.010916 | 0.0018757 | 0.0069621 | 0.052938 | -0.0071265 | -0.0065369 | 0.0067901 | -0.001145 | -0.036544 | 0.039221 | 0.0033985 | -0.015515 | 0.009155 | 0.022888 | 0.059509 | 0.082397 | 0.032043 | -0.022888 | -0.14191 | -0.07782 | 0.032043 | -0.10071 | -0.10529 | -0.091553 | -0.10529 | -0.17853 | 0.20142 | 0.082397 | -122.113 | 0.24719 | 0.3067 | 0.2243 | -122.1359 | 0.11902 | 0.045776 | -122.2504 | 0.14648 | 0.1236 | 0.07782 | -122.2366 | 0.25635 | 0.23346 | 0.28381 | -122.287 | 0.11902 | 0.13275 | 0.25635 | -122.3236
1091.6562 | 122.4472 | -0.17395 | 122.1222 | 0.0067138 | 0.011771 | -0.00047431 | 0.0046121 | 0.054647 | 0.0039819 | -0.0022643 | -0.0084684 | 0.0031274 | -0.036758 | 0.039648 | 0.0089527 | -0.01872 | -0.045776 | -0.091553 | -0.064087 | 0.004578 | 0.086975 | -0.041199 | -0.16479 | -0.11902 | -0.10529 | -0.20599 | -0.07782 | -0.07782 | -0.10986 | -0.19684 | 0.13275 | 0.009155 | -122.0352 | 0.082397 | 0.17853 | 0.16937 | -122.168 | 0.064087 | -0.022888 | -122.2 | 0.054931 | -0.032044 | -0.009156 | -122.2 | 0.26092 | 0.12817 | 0.10986 | -122.287 | 0.09613 | 0.09613 | 0.068664 | -122.319
1093.4062 | 122.3785 | -0.19684 | 122.1497 | -0.0085447 | 0.01348 | -0.0013287 | 0.0029031 | 0.052083 | 0.0020593 | -0.0037597 | -0.00083936 | 0.0029138 | -0.037613 | 0.040716 | 0.011303 | -0.015943 | -0.068665 | -0.1236 | -0.086975 | -0.004578 | 0.068665 | -0.050354 | -0.1831 | -0.16937 | -0.16479 | -0.27008 | -0.045776 | -0.050354 | -0.12817 | -0.21057 | 0.14648 | 0.013733 | -122.081 | 0.073242 | 0.19226 | 0.17853 | -122.2183 | 0.068664 | -0.013733 | -122.1954 | 0.027465 | -0.073243 | -0.05951 | -122.2 | 0.2655 | 0.12817 | 0.10986 | -122.3328 | 0.15106 | 0.14648 | 0.032043 | -122.3602
1095.1562 | 122.2824 | -0.23346 | 122.2137 | -0.0085447 | 0.013693 | 0.0018757 | 0.0052531 | 0.052083 | -0.0058447 | -0.0024779 | -0.016098 | -0.0022132 | -0.035263 | 0.039435 | 0.0046803 | -0.01402 | -0.018311 | 0.018311 | 0.041199 | 0.050354 | 0.032043 | 0.004578 | -0.15106 | -0.091553 | -0.032043 | -0.16022 | -0.086975 | -0.086975 | -0.09613 | -0.17395 | 0.23804 | 0.082397 | -122.1817 | 0.25177 | 0.28381 | 0.20142 | -122.2321 | 0.13733 | 0.059509 | -122.3007 | 0.14191 | 0.073242 | 0.013733 | -122.3007 | 0.2655 | 0.21515 | 0.27466 | -122.3648 | 0.14648 | 0.14648 | 0.20142 | -122.3877
1096.9219 | 122.3282 | -0.23804 | 122.2 | -0.0085447 | 0.007071 | 0.0055073 | 0.0035441 | 0.052724 | -0.0058447 | -0.0065369 | -0.00083936 | -0.0030676 | -0.038894 | 0.038367 | 0.0061757 | -0.015729 | -0.045776 | -0.018311 | 0 | 0.041199 | 0.032043 | -0.022888 | -0.15564 | -0.12817 | -0.032043 | -0.14191 | -0.073242 | -0.086975 | -0.10529 | -0.17853 | 0.21515 | 0.082397 | -122.168 | 0.21973 | 0.27924 | 0.19684 | -122.2458 | 0.13275 | 0.059509 | -122.2733 | 0.10986 | 0.09613 | 0.036621 | -122.287 | 0.27008 | 0.19226 | 0.23804 | -122.3557 | 0.16479 | 0.15106 | 0.20599 | -122.3785
1098.625 | 122.3007 | -0.21515 | 122.1588 | -0.0085447 | 0.011343 | 0.0035847 | 0.0061075 | 0.05187 | -0.0039221 | -0.0046143 | -0.00083936 | -0.0022132 | -0.037185 | 0.036444 | 0.0061757 | -0.018293 | 0.050354 | 0.054932 | 0.086975 | 0.091553 | 0.036621 | -0.018311 | -0.15106 | -0.045776 | 0.054932 | -0.082397 | -0.10986 | -0.09613 | -0.07782 | -0.16937 | 0.19684 | 0.064087 | -122.1222 | 0.27008 | 0.3067 | 0.24261 | -122.1085 | 0.13733 | 0.045776 | -122.2687 | 0.16937 | 0.13275 | 0.086976 | -122.2549 | 0.25177 | 0.2655 | 0.30212 | -122.3099 | 0.10529 | 0.11902 | 0.27008 | -122.3282
1100.375 | 122.3923 | -0.16937 | 122.1542 | -0.016174 | 0.016898 | -0.0032513 | 0.0041849 | 0.055074 | 0.0027003 | -0.0031189 | -0.0084684 | 0.0035546 | -0.03804 | 0.041357 | 0.0087391 | -0.02107 | 0.032043 | -0.045776 | 0 | 0.036621 | 0.064087 | -0.027466 | -0.16479 | -0.068665 | -0.045776 | -0.1831 | -0.050354 | -0.07782 | -0.10529 | -0.20599 | 0.14191 | 0.004578 | -122.0901 | 0.1236 | 0.20599 | 0.20142 | -122.1222 | 0.064087 | -0.036621 | -122.2046 | 0.10071 | -0.013732 | 0.022889 | -122.2321 | 0.23346 | 0.20142 | 0.16937 | -122.319 | 0.11902 | 0.091553 | 0.1236 | -122.3602
1102.1094 | 122.3877 | -0.21515 | 122.1634 | 0.0067138 | 0.015402 | 0.00016669 | 0.0041849 | 0.052938 | 0.0022729 | -0.0024779 | 0.0067901 | 0.0020594 | -0.036117 | 0.03858 | 0.0091665 | -0.018293 | 0.004578 | -0.045776 | -0.009155 | 0.041199 | 0.07782 | -0.050354 | -0.16022 | -0.10529 | -0.07782 | -0.2243 | -0.068665 | -0.050354 | -0.11902 | -0.17853 | 0.16479 | 0.054932 | -122.0856 | 0.16937 | 0.25635 | 0.20142 | -122.1588 | 0.09613 | 0.036621 | -122.2321 | 0.10986 | -0.009155 | -0.045776 | -122.2137 | 0.29297 | 0.21973 | 0.20599 | -122.3236 | 0.14648 | 0.16479 | 0.13733 | -122.3419
1103.875 | 122.4197 | -0.18768 | 122.1497 | -0.0085447 | 0.014761 | 0.0010211 | 0.0054667 | 0.056569 | -0.0013587 | -0.00076912 | 0.0067901 | -0.0009314 | -0.034835 | 0.037939 | 0.0078847 | -0.015515 | 0.018311 | 0.036621 | 0.032043 | 0.091553 | 0.036621 | 0 | -0.13733 | -0.054932 | -0.018311 | -0.14191 | -0.11902 | -0.11444 | -0.086975 | -0.16937 | 0.18768 | 0.050354 | -122.113 | 0.2243 | 0.27924 | 0.22888 | -122.1313 | 0.10071 | 0.01831 | -122.2687 | 0.13275 | 0.045776 | 0.027466 | -122.2641 | 0.2243 | 0.20599 | 0.21973 | -122.287 | 0.068664 | 0.073242 | 0.16937 | -122.319
1105.5781 | 122.3511 | -0.21515 | 122.1909 | -0.0085447 | 0.012198 | 0.0037983 | 0.0086709 | 0.053152 | -0.0069129 | -0.0029053 | 0.0067901 | -0.0002906 | -0.036117 | 0.036871 | 0.0031849 | -0.014447 | -0.032043 | -0.027466 | 0.018311 | 0.073242 | 0.059509 | -0.018311 | -0.15106 | -0.11444 | -0.032043 | -0.14191 | -0.082397 | -0.09613 | -0.086975 | -0.18768 | 0.19684 | 0.064087 | -122.1313 | 0.18768 | 0.28839 | 0.2243 | -122.2229 | 0.12817 | 0.027466 | -122.2733 | 0.10071 | 0.073242 | 0.045776 | -122.287 | 0.27466 | 0.18311 | 0.23346 | -122.3419 | 0.13275 | 0.11902 | 0.18311 | -122.3785
1107.3281 | 122.4426 | -0.18768 | 122.1313 | -0.00091566 | 0.016684 | -0.00026071 | 0.0058939 | 0.055288 | 0.0029139 | -0.0029053 | -0.00083936 | 0.001632 | -0.036758 | 0.04093 | 0.0095937 | -0.01872 | 0.004578 | -0.059509 | -0.018311 | 0.013733 | 0.07782 | -0.032043 | -0.18768 | -0.11444 | -0.054932 | -0.21973 | -0.073242 | -0.059509 | -0.13275 | -0.20599 | 0.15564 | 0 | -122.0535 | 0.12817 | 0.20142 | 0.20142 | -122.1268 | 0.054932 | -0.018311 | -122.2046 | 0.073242 | -0.032044 | -0.013733 | -122.1909 | 0.2655 | 0.19226 | 0.16937 | -122.319 | 0.11444 | 0.12817 | 0.13275 | -122.3373
1109.0625 | 122.3831 | -0.2243 | 122.1634 | -0.00091566 | 0.012412 | 0.0023029 | 0.0029031 | 0.053792 | -0.0039221 | -0.0033325 | -0.0084684 | 0.0029138 | -0.039108 | 0.039862 | 0.0089527 | -0.017011 | 0.036621 | 0.036621 | 0.07782 | 0.082397 | 0.032043 | -0.018311 | -0.12817 | -0.082397 | -0.009155 | -0.1236 | -0.12817 | -0.10986 | -0.11444 | -0.19226 | 0.20599 | 0.09613 | -122.1313 | 0.26093 | 0.3067 | 0.21057 | -122.1268 | 0.10986 | 0.032043 | -122.2916 | 0.14191 | 0.10071 | 0.068665 | -122.2733 | 0.25635 | 0.26093 | 0.30212 | -122.2916 | 0.09613 | 0.11444 | 0.21515 | -122.3557
1110.8125 | 122.4335 | -0.19226 | 122.1222 | -0.00091566 | 0.011343 | 0.00038029 | 0.0039713 | 0.052511 | -0.00050411 | -0.0024779 | -0.00083936 | -0.001145 | -0.037399 | 0.041998 | 0.0085255 | -0.020002 | 0.022888 | 0.013733 | 0.064087 | 0.068665 | 0.045776 | -0.009155 | -0.13733 | -0.073242 | -0.022888 | -0.15106 | -0.10986 | -0.12817 | -0.10071 | -0.19226 | 0.18311 | 0.054932 | -122.0764 | 0.20599 | 0.26093 | 0.20599 | -122.0993 | 0.091553 | 0 | -122.2321 | 0.11902 | 0.041199 | 0.041199 | -122.2504 | 0.23804 | 0.21515 | 0.25635 | -122.2595 | 0.082398 | 0.064087 | 0.16937 | -122.3145
1112.5156 | 122.3145 | -0.23346 | 122.2046 | -0.0085447 | 0.01348 | -4.6912e-05 | 0.0080301 | 0.052724 | -0.0041357 | -0.0041869 | -0.00083936 | -0.001145 | -0.035049 | 0.040076 | 0.0048939 | -0.017224 | 0.032043 | 0.032043 | 0.086975 | 0.09613 | 0.036621 | -0.004578 | -0.13733 | -0.10071 | 0.009155 | -0.13733 | -0.10529 | -0.10071 | -0.091553 | -0.19226 | 0.22888 | 0.09613 | -122.168 | 0.2655 | 0.32959 | 0.23346 | -122.1725 | 0.14191 | 0.041198 | -122.3099 | 0.13275 | 0.09613 | 0.054932 | -122.3053 | 0.27008 | 0.2655 | 0.32043 | -122.3419 | 0.12817 | 0.13275 | 0.24261 | -122.3969
1114.2656 | 122.3465 | -0.23346 | 122.2 | -0.00091566 | 0.0068574 | 0.0033709 | 0.0043985 | 0.053365 | -0.0052039 | -0.0061095 | 0.0067901 | -0.0015722 | -0.036758 | 0.039221 | 0.0068165 | -0.014875 | -0.027466 | -0.013733 | 0.004578 | 0.054932 | 0.050354 | -0.022888 | -0.13275 | -0.10986 | -0.022888 | -0.14648 | -0.091553 | -0.091553 | -0.12817 | -0.1831 | 0.21057 | 0.10071 | -122.1497 | 0.21973 | 0.28839 | 0.18768 | -122.2275 | 0.10528 | 0.050354 | -122.2916 | 0.1236 | 0.086975 | 0.036621 | -122.2916 | 0.28381 | 0.20599 | 0.23804 | -122.3328 | 0.14191 | 0.14191 | 0.21057 | -122.3831
1116.0156 | 122.287 | -0.23804 | 122.2 | -0.00091566 | 0.011343 | 0.0059345 | 0.0031167 | 0.051656 | -0.0041357 | -0.0044007 | 0.0067901 | 0.0012048 | -0.036544 | 0.03858 | 0.0072437 | -0.01872 | 0.027466 | 0.009155 | 0.041199 | 0.041199 | 0.059509 | -0.004578 | -0.13733 | -0.09613 | -0.054932 | -0.16937 | -0.086975 | -0.086975 | -0.091553 | -0.19684 | 0.23346 | 0.10071 | -122.1405 | 0.24719 | 0.27924 | 0.17853 | -122.1725 | 0.14648 | 0.041199 | -122.287 | 0.14191 | 0.068664 | 0.027465 | -122.287 | 0.29755 | 0.2655 | 0.27924 | -122.3373 | 0.15106 | 0.15106 | 0.1831 | -122.3969
1117.7031 | 122.3465 | -0.21057 | 122.1771 | -0.00091566 | 0.014334 | 0.0012347 | 0.0033305 | 0.05486 | -0.0015723 | -0.0044007 | -0.016098 | 0.0018456 | -0.035263 | 0.039221 | 0.0072437 | -0.019574 | 0.054932 | 0.036621 | 0.086975 | 0.07782 | 0.032043 | 0 | -0.1236 | -0.045776 | -0.013733 | -0.13733 | -0.11444 | -0.10529 | -0.10071 | -0.16022 | 0.21057 | 0.086975 | -122.1451 | 0.24719 | 0.28839 | 0.20142 | -122.1222 | 0.10986 | 0.050354 | -122.2916 | 0.1648 | 0.073242 | 0.022888 | -122.2824 | 0.24261 | 0.2655 | 0.29755 | -122.3007 | 0.09613 | 0.10529 | 0.19684 | -122.3373
1119.4531 | 122.3465 | -0.2243 | 122.168 | -0.016174 | 0.012412 | 0.0027301 | 0.0037577 | 0.053152 | -0.0039221 | -0.0071777 | -0.0084684 | -0.0017858 | -0.035476 | 0.040076 | 0.0068165 | -0.018506 | 0.064087 | 0.068665 | 0.091553 | 0.086975 | 0.032043 | -0.013733 | -0.13275 | -0.054932 | 0.036621 | -0.10071 | -0.1236 | -0.09613 | -0.09613 | -0.16022 | 0.21057 | 0.091553 | -122.1359 | 0.29297 | 0.31128 | 0.21973 | -122.1039 | 0.12817 | 0.064087 | -122.2916 | 0.16937 | 0.1236 | 0.059509 | -122.2641 | 0.25635 | 0.28839 | 0.31586 | -122.3007 | 0.10071 | 0.12817 | 0.26093 | -122.3282
1121.1875 | 122.3419 | -0.24261 | 122.1863 | -0.00091566 | 0.014334 | 0.0023029 | 0.0033305 | 0.054647 | -0.0047765 | -0.0058959 | -0.00083936 | -0.0017858 | -0.034835 | 0.03858 | 0.0078847 | -0.017224 | 0.059509 | 0.059509 | 0.086975 | 0.091553 | 0.054932 | 0.004578 | -0.13733 | -0.050354 | 0.022888 | -0.11444 | -0.09613 | -0.09613 | -0.086975 | -0.1831 | 0.24719 | 0.10529 | -122.1313 | 0.30212 | 0.33417 | 0.22888 | -122.1268 | 0.15564 | 0.05951 | -122.2824 | 0.19226 | 0.12817 | 0.068664 | -122.2824 | 0.29755 | 0.30212 | 0.32959 | -122.3236 | 0.14649 | 0.14649 | 0.2655 | -122.3694
1122.9531 | 122.2916 | -0.21515 | 122.1909 | -0.00091566 | 0.014761 | 0.00038029 | 0.0039713 | 0.05422 | -0.0019995 | -0.0050415 | -0.00083936 | -7.6996e-05 | -0.034195 | 0.038367 | 0.0083119 | -0.016584 | 0.041199 | 0.027466 | 0.041199 | 0.064087 | 0.054932 | -0.009155 | -0.16022 | -0.11902 | -0.041199 | -0.18768 | -0.091553 | -0.091553 | -0.13275 | -0.2243 | 0.20599 | 0.054932 | -122.1359 | 0.24261 | 0.27924 | 0.2243 | -122.1497 | 0.082398 | -0.009155 | -122.2824 | 0.09613 | 0.027466 | 0.036621 | -122.2824 | 0.27008 | 0.25635 | 0.25635 | -122.3511 | 0.1236 | 0.1236 | 0.17395 | -122.4152
1124.6406 | 122.2961 | -0.23804 | 122.2092 | -0.0085447 | 0.012625 | 0.0016619 | 0.0054667 | 0.053365 | -0.0022131 | -0.0046143 | -0.00083936 | -0.0007178 | -0.034408 | 0.03559 | 0.0078847 | -0.017438 | 0.050354 | 0.054932 | 0.091553 | 0.07782 | 0.050354 | -0.013733 | -0.14648 | -0.054932 | 0 | -0.13275 | -0.10529 | -0.09613 | -0.10071 | -0.1831 | 0.2243 | 0.091553 | -122.1588 | 0.29297 | 0.31586 | 0.2243 | -122.1588 | 0.13733 | 0.054932 | -122.3145 | 0.1831 | 0.10529 | 0.050354 | -122.3053 | 0.28839 | 0.28839 | 0.32959 | -122.3557 | 0.13275 | 0.14191 | 0.23804 | -122.3923
1126.3906 | 122.4014 | -0.20599 | 122.1863 | -0.00091566 | 0.014334 | 0.00038029 | 0.0039713 | 0.054647 | 0.00056389 | -0.0033325 | 0.0067901 | 0.0014184 | -0.033981 | 0.040503 | 0.0087391 | -0.018293 | 0.045776 | -0.045776 | -0.013733 | 0.022888 | 0.073242 | -0.041199 | -0.16022 | -0.10986 | -0.09613 | -0.25177 | -0.09613 | -0.073242 | -0.12817 | -0.21057 | 0.1648 | 0.045777 | -122.113 | 0.16022 | 0.22888 | 0.1831 | -122.1405 | 0.07782 | -0.004577 | -122.2824 | 0.096131 | -0.045776 | -0.041199 | -122.2595 | 0.27924 | 0.25177 | 0.19226 | -122.3465 | 0.10986 | 0.13275 | 0.10986 | -122.3969
1128.1406 | 122.3648 | -0.23346 | 122.168 | -0.00091566 | 0.013052 | 0.0031573 | 0.0076029 | 0.052938 | -0.0064855 | -0.0037597 | -0.016098 | -0.0047766 | -0.035476 | 0.039435 | 0.0059621 | -0.017865 | 0.022888 | 0.064087 | 0.082397 | 0.082397 | 0.045776 | -0.013733 | -0.15106 | -0.068665 | 0.022888 | -0.10529 | -0.11902 | -0.11902 | -0.11444 | -0.19684 | 0.21973 | 0.082397 | -122.1222 | 0.29755 | 0.31586 | 0.23346 | -122.1451 | 0.11902 | 0.036621 | -122.287 | 0.16479 | 0.12817 | 0.091552 | -122.287 | 0.27924 | 0.25635 | 0.31586 | -122.319 | 0.11444 | 0.11444 | 0.25635 | -122.3648
1129.8906 | 122.4609 | -0.1831 | 122.1634 | -0.00091566 | 0.011557 | -0.00090151 | 0.0050393 | 0.052511 | 0.0018457 | -0.0020507 | -0.0084684 | 0.000564 | -0.034195 | 0.039435 | 0.0083119 | -0.017652 | -0.027466 | -0.07782 | -0.045776 | 0.013733 | 0.07782 | -0.032043 | -0.16937 | -0.1236 | -0.091553 | -0.20599 | -0.086975 | -0.09613 | -0.13733 | -0.20599 | 0.15106 | 0.013732 | -122.0856 | 0.10528 | 0.19684 | 0.18311 | -122.1909 | 0.045776 | -0.022889 | -122.2504 | 0.059509 | -0.022889 | 0 | -122.2595 | 0.26092 | 0.15564 | 0.13733 | -122.3328 | 0.09613 | 0.086975 | 0.091552 | -122.3694
1131.5938 | 122.4014 | -0.21515 | 122.1725 | -0.00091566 | 0.015402 | 0.00016669 | 0.0046121 | 0.055501 | 0.0039819 | -0.0016235 | -0.00083936 | 0.003982 | -0.034622 | 0.040716 | 0.0098073 | -0.019147 | 0.013733 | -0.018311 | -0.004578 | 0.027466 | 0.082397 | -0.032043 | -0.16937 | -0.1236 | -0.11444 | -0.23804 | -0.086975 | -0.086975 | -0.14191 | -0.21973 | 0.18311 | 0.045776 | -122.0901 | 0.19684 | 0.24261 | 0.19684 | -122.1588 | 0.073242 | -0.004578 | -122.2595 | 0.091553 | -0.022888 | -0.01831 | -122.2595 | 0.29755 | 0.22888 | 0.21057 | -122.3419 | 0.12817 | 0.12817 | 0.10071 | -122.3923
1133.3438 | 122.3694 | -0.24719 | 122.168 | -0.00091566 | 0.016257 | 0.0040119 | 0.0086709 | 0.053792 | -0.00029051 | -0.0033325 | -0.00083936 | 0.0009912 | -0.033981 | 0.040503 | 0.0074575 | -0.017011 | -0.07782 | -0.09613 | -0.059509 | 0 | 0.068665 | -0.064087 | -0.20599 | -0.18768 | -0.1236 | -0.26093 | -0.07782 | -0.073242 | -0.14191 | -0.23804 | 0.1831 | 0.041198 | -122.0993 | 0.15106 | 0.24719 | 0.20599 | -122.2458 | 0.10528 | 0.009155 | -122.2458 | 0.059509 | -0.013733 | -0.022888 | -122.2412 | 0.31586 | 0.16937 | 0.18768 | -122.374 | 0.16937 | 0.17395 | 0.1236 | -122.406
1135.0938 | 122.4609 | -0.20142 | 122.1497 | 0.0067138 | 0.014121 | 0.0012347 | 0.0041849 | 0.058278 | 0.00013669 | -0.00098272 | -0.016098 | 0.0018456 | -0.033554 | 0.042639 | 0.0068165 | -0.017865 | -0.036621 | -0.032043 | -0.027466 | 0.050354 | 0.07782 | -0.045776 | -0.17395 | -0.11902 | -0.068665 | -0.21057 | -0.082397 | -0.091553 | -0.11902 | -0.21515 | 0.15564 | 0.027466 | -122.0718 | 0.16937 | 0.25177 | 0.2243 | -122.1863 | 0.082397 | -0.013733 | -122.2321 | 0.082397 | -0.009155 | 0.004578 | -122.2412 | 0.27924 | 0.1648 | 0.17395 | -122.3236 | 0.11902 | 0.10986 | 0.13275 | -122.3648
1136.8438 | 122.3694 | -0.21515 | 122.1909 | -0.0085447 | 0.011557 | 0.0020893 | 0.0043985 | 0.054433 | -0.0075537 | -0.0033325 | -0.0084684 | -0.0032812 | -0.035904 | 0.039862 | 0.0040395 | -0.015302 | -0.018311 | 0.013733 | 0.054932 | 0.064087 | 0.054932 | -0.013733 | -0.15106 | -0.09613 | 0.004578 | -0.11444 | -0.10529 | -0.09613 | -0.10071 | -0.18768 | 0.20142 | 0.064087 | -122.1359 | 0.22888 | 0.27924 | 0.21515 | -122.2092 | 0.11444 | 0.027466 | -122.2961 | 0.11902 | 0.10071 | 0.073242 | -122.287 | 0.27008 | 0.19684 | 0.27008 | -122.3419 | 0.10986 | 0.11902 | 0.21973 | -122.3785
1138.5469 | 122.4152 | -0.21973 | 122.168 | -0.00091566 | 0.012412 | 0.0037983 | 0.0033305 | 0.052297 | -0.0022131 | -0.0022643 | -0.016098 | -0.0015722 | -0.034622 | 0.040716 | 0.0091665 | -0.01872 | 0.022888 | 0.036621 | 0.073242 | 0.086975 | 0.018311 | -0.013733 | -0.13275 | -0.059509 | -0.009155 | -0.11444 | -0.1236 | -0.11444 | -0.10529 | -0.17395 | 0.20599 | 0.086976 | -122.1497 | 0.25635 | 0.3067 | 0.21973 | -122.1451 | 0.11444 | 0.045777 | -122.2916 | 0.16022 | 0.10529 | 0.059509 | -122.2824 | 0.23804 | 0.24261 | 0.29297 | -122.3007 | 0.096131 | 0.10529 | 0.21057 | -122.3419
1140.2969 | 122.4426 | -0.18768 | 122.168 | -0.0085447 | 0.015616 | 0.0031573 | 0.0037577 | 0.053579 | 0.00035029 | -0.0041869 | -0.00083936 | 0.001632 | -0.030563 | 0.039221 | 0.0083119 | -0.017865 | -0.045776 | -0.082397 | -0.054932 | 0.018311 | 0.073242 | -0.064087 | -0.17853 | -0.16479 | -0.10986 | -0.23346 | -0.059509 | -0.050354 | -0.1236 | -0.21515 | 0.1236 | 0.009155 | -122.0947 | 0.10529 | 0.20599 | 0.19684 | -122.2137 | 0.064087 | -0.027466 | -122.2275 | 0.022888 | -0.045776 | -0.01831 | -122.2183 | 0.26092 | 0.14191 | 0.13275 | -122.3465 | 0.12817 | 0.13733 | 0.07782 | -122.3831
1142.0312 | 122.4197 | -0.20142 | 122.1634 | -0.00091566 | 0.015402 | 0.00016669 | 0.0035441 | 0.05486 | -7.6908e-05 | -0.0033325 | -0.0084684 | 0.0009912 | -0.033554 | 0.04093 | 0.0098073 | -0.017652 | -0.082397 | -0.12817 | -0.086975 | -0.018311 | 0.086975 | -0.041199 | -0.16937 | -0.16022 | -0.14191 | -0.27008 | -0.064087 | -0.054932 | -0.13733 | -0.23346 | 0.16022 | 0.032043 | -122.0764 | 0.073242 | 0.18311 | 0.15106 | -122.2458 | 0.064087 | -0.032043 | -122.2275 | 0.041199 | -0.068665 | -0.036622 | -122.2183 | 0.28839 | 0.11902 | 0.11444 | -122.3328 | 0.13733 | 0.14648 | 0.059509 | -122.3969
1143.7812 | 122.4106 | -0.18768 | 122.1909 | -0.016174 | 0.015402 | -0.00026071 | 0.0078165 | 0.05187 | -0.0011451 | -0.00076912 | -0.0084684 | 0.003341 | -0.032272 | 0.043066 | 0.0074575 | -0.015515 | -0.027466 | -0.050354 | -0.027466 | 0.032043 | 0.073242 | -0.032043 | -0.17395 | -0.14648 | -0.10986 | -0.24719 | -0.054932 | -0.073242 | -0.1236 | -0.2243 | 0.15564 | 0.013733 | -122.1176 | 0.13733 | 0.21973 | 0.20599 | -122.2183 | 0.064087 | -0.036621 | -122.2458 | 0.041199 | -0.059509 | -0.022888 | -122.2641 | 0.26092 | 0.16022 | 0.16022 | -122.3648 | 0.13275 | 0.11444 | 0.07782 | -122.4152
1145.4688 | 122.4289 | -0.22888 | 122.1588 | -0.00091566 | 0.01647 | 0.00038029 | 0.0039713 | 0.053365 | -0.00029051 | -0.0022643 | -0.00083936 | 0.002273 | -0.033981 | 0.040076 | 0.0083119 | -0.01637 | -0.013733 | -0.018311 | 0.004578 | 0.054932 | 0.068665 | -0.027466 | -0.14648 | -0.11444 | -0.054932 | -0.20142 | -0.082397 | -0.068665 | -0.10529 | -0.19684 | 0.20142 | 0.082398 | -122.0901 | 0.21057 | 0.28381 | 0.20142 | -122.1725 | 0.1236 | 0.032044 | -122.2412 | 0.11444 | 0.027466 | -0.004578 | -122.2275 | 0.29755 | 0.21515 | 0.23346 | -122.3053 | 0.14649 | 0.16022 | 0.17395 | -122.3557
1147.2031 | 122.4701 | -0.1831 | 122.1771 | -0.00091566 | 0.01348 | -0.0013287 | 0.0058939 | 0.053579 | -0.0045629 | -0.0033325 | -0.0084684 | -7.6996e-05 | -0.03334 | 0.039435 | 0.0078847 | -0.015515 | -0.036621 | -0.032043 | 0.013733 | 0.032043 | 0.054932 | -0.018311 | -0.15106 | -0.091553 | -0.045776 | -0.16022 | -0.11444 | -0.10529 | -0.10529 | -0.17395 | 0.16479 | 0.032043 | -122.1222 | 0.15106 | 0.21515 | 0.18311 | -122.2137 | 0.077819 | 0.009155 | -122.2916 | 0.091552 | 0.022888 | 0.013733 | -122.2824 | 0.23804 | 0.14648 | 0.19684 | -122.3282 | 0.068664 | 0.077819 | 0.13733 | -122.3511
1148.9688 | 122.3282 | -0.23804 | 122.2321 | -0.00091566 | 0.014334 | 0.0040119 | 0.0076029 | 0.053365 | -0.0077673 | -0.0037597 | -0.00083936 | -0.0041358 | -0.033767 | 0.039862 | 0.0040395 | -0.014661 | -0.032043 | 0.009155 | 0.036621 | 0.045776 | 0.027466 | -0.009155 | -0.15564 | -0.13275 | -0.036621 | -0.16937 | -0.11444 | -0.082397 | -0.11444 | -0.20599 | 0.22888 | 0.082397 | -122.2046 | 0.24719 | 0.28381 | 0.20142 | -122.2641 | 0.1236 | 0.032043 | -122.3465 | 0.10529 | 0.068664 | 0.036621 | -122.3145 | 0.2655 | 0.20599 | 0.27466 | -122.3877 | 0.1236 | 0.15564 | 0.20142 | -122.4381
1150.6562 | 122.4609 | -0.16937 | 122.1863 | -0.0085447 | 0.016898 | 0.00038029 | 0.0069621 | 0.05486 | 0.00099129 | -0.0056823 | -0.0084684 | 0.000564 | -0.032486 | 0.041571 | 0.0091665 | -0.018506 | -0.027466 | -0.050354 | -0.027466 | 0.027466 | 0.07782 | -0.054932 | -0.18768 | -0.11902 | -0.068665 | -0.19684 | -0.064087 | -0.064087 | -0.11444 | -0.21057 | 0.11444 | -0.01831 | -122.1085 | 0.11902 | 0.19684 | 0.21515 | -122.2137 | 0.054932 | -0.041198 | -122.2504 | 0.050354 | -0.027465 | 0.013733 | -122.2504 | 0.24719 | 0.14191 | 0.14191 | -122.374 | 0.10529 | 0.10529 | 0.10071 | -122.3969
1152.4062 | 122.3694 | -0.21057 | 122.2137 | -0.00091566 | 0.010916 | 0.0033709 | 0.0054667 | 0.054433 | -0.0081945 | -0.0035461 | -0.016098 | -0.0030676 | -0.033981 | 0.039007 | 0.0040395 | -0.017865 | -0.036621 | 0 | 0.036621 | 0.064087 | 0.041199 | -0.013733 | -0.15106 | -0.10529 | 0.009155 | -0.10986 | -0.10529 | -0.086975 | -0.086975 | -0.18768 | 0.19684 | 0.059509 | -122.1725 | 0.21057 | 0.27466 | 0.21515 | -122.2504 | 0.1236 | 0.022888 | -122.319 | 0.10529 | 0.10071 | 0.07782 | -122.3007 | 0.25177 | 0.17395 | 0.24719 | -122.3648 | 0.10529 | 0.1236 | 0.21973 | -122.4014
1154.1562 | 122.4518 | -0.18768 | 122.1863 | -0.00091566 | 0.013693 | 0.0016619 | 0.0058939 | 0.054647 | 0.00056389 | -0.0037597 | 0.0067901 | 0.0007776 | -0.033554 | 0.040289 | 0.0070301 | -0.017865 | -0.07782 | -0.082397 | -0.059509 | 0.027466 | 0.059509 | -0.073242 | -0.18768 | -0.14648 | -0.082397 | -0.23804 | -0.064087 | -0.059509 | -0.14191 | -0.20599 | 0.11444 | 0 | -122.1268 | 0.10529 | 0.21515 | 0.21515 | -122.2641 | 0.045776 | -0.018311 | -122.2504 | 0.041199 | -0.050354 | -0.032043 | -122.2458 | 0.24719 | 0.10986 | 0.12817 | -122.374 | 0.1236 | 0.12817 | 0.10529 | -122.3923
1155.9219 | 122.3969 | -0.20599 | 122.2275 | -0.00091566 | 0.016898 | 0.0010211 | 0.0073893 | 0.05187 | -0.0011451 | -0.0024779 | -0.00083936 | 0.0018456 | -0.034622 | 0.039435 | 0.0083119 | -0.017865 | -0.086975 | -0.082397 | -0.07782 | 0.004578 | 0.073242 | -0.082397 | -0.20142 | -0.17395 | -0.10529 | -0.2655 | -0.036621 | -0.059509 | -0.15106 | -0.21515 | 0.1236 | 0.004578 | -122.1542 | 0.1236 | 0.21057 | 0.20599 | -122.3145 | 0.054932 | -0.009155 | -122.2641 | 0.032044 | -0.059509 | -0.050354 | -122.287 | 0.27924 | 0.11902 | 0.12817 | -122.4289 | 0.16937 | 0.14649 | 0.10071 | -122.4426
1157.6094 | 122.3282 | -0.2243 | 122.2458 | -0.0085447 | 0.014548 | 0.0029437 | 0.0048257 | 0.051656 | -0.0052039 | -0.0041869 | -0.0084684 | -0.0022132 | -0.034408 | 0.036658 | 0.0051075 | -0.016797 | 0.009155 | 0.073242 | 0.07782 | 0.091553 | 0.027466 | -0.027466 | -0.14191 | -0.059509 | 0.050354 | -0.11444 | -0.10529 | -0.10071 | -0.086975 | -0.16937 | 0.19684 | 0.082397 | -122.2183 | 0.29755 | 0.31586 | 0.23346 | -122.2366 | 0.13733 | 0.054931 | -122.3511 | 0.16479 | 0.10986 | 0.054932 | -122.3465 | 0.25177 | 0.23346 | 0.30212 | -122.3877 | 0.11902 | 0.1236 | 0.27466 | -122.4152
1159.3594 | 122.3831 | -0.21515 | 122.2366 | -0.00091566 | 0.010062 | 0.0037983 | 0.0037577 | 0.055074 | -0.0060583 | -0.0054687 | -0.0084684 | -0.0047766 | -0.034408 | 0.039007 | 0.0068165 | -0.018079 | -0.050354 | -0.004578 | 0.018311 | 0.054932 | 0.059509 | -0.041199 | -0.14191 | -0.10071 | -0.013733 | -0.12817 | -0.07782 | -0.068665 | -0.09613 | -0.1831 | 0.17395 | 0.073242 | -122.1771 | 0.21057 | 0.27008 | 0.19684 | -122.287 | 0.11902 | 0.032044 | -122.3145 | 0.11444 | 0.086975 | 0.054931 | -122.3053 | 0.27466 | 0.16479 | 0.23346 | -122.3785 | 0.13733 | 0.14648 | 0.20142 | -122.4197
1161.0938 | 122.3282 | -0.22888 | 122.2458 | -0.00091566 | 0.013266 | 0.0031573 | 0.0054667 | 0.055501 | -0.0017859 | -0.0052551 | 0.0067901 | 0.0009912 | -0.033554 | 0.03858 | 0.0072437 | -0.018079 | 0.009155 | 0.022888 | 0.022888 | 0.059509 | 0.045776 | -0.041199 | -0.15106 | -0.10529 | -0.022888 | -0.17395 | -0.07782 | -0.050354 | -0.09613 | -0.20599 | 0.18768 | 0.07782 | -122.2 | 0.25177 | 0.28839 | 0.21057 | -122.2366 | 0.13275 | 0.022888 | -122.3236 | 0.1236 | 0.054932 | 0.032044 | -122.2961 | 0.27466 | 0.23804 | 0.25177 | -122.3969 | 0.15106 | 0.17853 | 0.20599 | -122.4518
1162.8438 | 122.3969 | -0.20142 | 122.2229 | 0.0067138 | 0.014334 | 0.0033709 | 0.0065347 | 0.054006 | -0.0062719 | -0.0044007 | -0.00083936 | -0.0005042 | -0.036117 | 0.037726 | 0.0044667 | -0.017865 | 0.018311 | 0.050354 | 0.068665 | 0.07782 | 0.050354 | -0.009155 | -0.13275 | -0.045776 | 0.041199 | -0.064087 | -0.07782 | -0.091553 | -0.068665 | -0.16937 | 0.19226 | 0.068665 | -122.1725 | 0.25177 | 0.27924 | 0.21057 | -122.2046 | 0.13275 | 0.032043 | -122.3007 | 0.15564 | 0.13733 | 0.10529 | -122.3145 | 0.25177 | 0.21973 | 0.27008 | -122.3557 | 0.1236 | 0.10986 | 0.24262 | -122.3923
1164.5312 | 122.4701 | -0.18768 | 122.1863 | -0.00091566 | 0.020102 | -0.0011151 | 0.0065347 | 0.050374 | 0.00056389 | -0.0041869 | -0.00083936 | 0.0031274 | -0.034408 | 0.039862 | 0.0078847 | -0.016584 | -0.032043 | -0.086975 | -0.054932 | 0.013733 | 0.064087 | -0.050354 | -0.18768 | -0.11444 | -0.064087 | -0.20599 | -0.050354 | -0.059509 | -0.1236 | -0.21515 | 0.13733 | 0 | -122.1222 | 0.10071 | 0.20142 | 0.20142 | -122.2183 | 0.064087 | -0.027466 | -122.2366 | 0.073242 | -0.018311 | 0.009155 | -122.2458 | 0.25177 | 0.15564 | 0.13275 | -122.374 | 0.13733 | 0.12817 | 0.1236 | -122.4014
1166.2656 | 122.4106 | -0.19684 | 122.1954 | -0.0085447 | 0.017752 | -0.0015423 | 0.0058939 | 0.051656 | 0.0018457 | -0.0026917 | 0.0067901 | 0.0027002 | -0.032486 | 0.041144 | 0.0083119 | -0.015943 | -0.064087 | -0.11902 | -0.086975 | 0 | 0.059509 | -0.045776 | -0.19226 | -0.14648 | -0.14648 | -0.27466 | -0.054932 | -0.045776 | -0.1236 | -0.19226 | 0.15106 | 0.004577 | -122.1359 | 0.077819 | 0.19684 | 0.19226 | -122.2595 | 0.073242 | 0.004577 | -122.2504 | 0.050354 | -0.07782 | -0.082397 | -122.2412 | 0.25635 | 0.13275 | 0.10986 | -122.3877 | 0.14191 | 0.15106 | 0.050354 | -122.3877
1168.0156 | 122.4197 | -0.19226 | 122.2092 | 0.0067138 | 0.015402 | -0.00090151 | 0.0076029 | 0.052083 | 0.0022729 | -0.0018371 | -0.00083936 | 0.001632 | -0.033126 | 0.033667 | 0.0093801 | -0.0084658 | -0.009155 | -0.022888 | -0.004578 | 0.036621 | 0.054932 | -0.045776 | -0.17853 | -0.068665 | -0.064087 | -0.20599 | -0.068665 | -0.068665 | -0.11902 | -0.21057 | 0.14648 | 0.013733 | -122.1542 | 0.16937 | 0.22888 | 0.21515 | -122.2183 | 0.073242 | -0.01831 | -122.2778 | 0.1236 | -0.013733 | 0.004577 | -122.2778 | 0.24719 | 0.18311 | 0.18768 | -122.3877 | 0.1236 | 0.1236 | 0.12817 | -122.4197
1169.7031 | 122.4655 | -0.15564 | 122.1817 | 0.0067138 | 0.012198 | 0.0020893 | 0.0052531 | 0.055715 | -0.0028539 | -0.0029053 | 0.0067901 | -0.0005042 | -0.035049 | 0.029181 | 0.0098073 | -0.0054752 | -0.041199 | -0.041199 | -0.018311 | 0.009155 | 0.050354 | -0.027466 | -0.13733 | -0.064087 | -0.018311 | -0.14191 | -0.091553 | -0.086975 | -0.091553 | -0.17395 | 0.12817 | 0.018311 | -122.1313 | 0.11444 | 0.16479 | 0.14648 | -122.2229 | 0.064087 | -0.01831 | -122.2733 | 0.091553 | 0.013733 | 0.032043 | -122.2687 | 0.20599 | 0.11444 | 0.13733 | -122.319 | 0.064087 | 0.068665 | 0.13733 | -122.3557
1171.4531 | 122.3373 | -0.22888 | 122.2458 | 0.0067138 | 0.011557 | 0.0025165 | 0.0065347 | 0.050374 | -0.0047765 | -0.0016235 | 0.0067901 | -0.0015722 | -0.035263 | 0.024695 | 0.0042531 | -0.0024844 | -0.013733 | 0.032043 | 0.050354 | 0.064087 | 0.027466 | -0.004578 | -0.13275 | -0.091553 | -0.027466 | -0.13733 | -0.086975 | -0.10071 | -0.082397 | -0.17853 | 0.2243 | 0.096131 | -122.2183 | 0.26093 | 0.29297 | 0.19684 | -122.2595 | 0.14649 | 0.050354 | -122.3328 | 0.13733 | 0.091553 | 0.041199 | -122.3465 | 0.25635 | 0.21515 | 0.27924 | -122.3785 | 0.14191 | 0.12817 | 0.20142 | -122.4243
1173.2031 | 122.4197 | -0.17853 | 122.2183 | 0.014343 | 0.016257 | 0.00059389 | 0.0039713 | 0.052938 | 0.0018457 | -0.0020507 | 0.0067901 | 0.0024866 | -0.035049 | 0.027258 | 0.0080983 | -0.0048342 | -0.059509 | -0.064087 | -0.045776 | 0.009155 | 0.054932 | -0.050354 | -0.1831 | -0.13733 | -0.10071 | -0.25635 | -0.050354 | -0.045776 | -0.10986 | -0.19226 | 0.12817 | -0.004577 | -122.1634 | 0.11444 | 0.18768 | 0.19226 | -122.2778 | 0.068665 | -0.013733 | -122.2687 | 0.041199 | -0.07782 | -0.064087 | -122.2641 | 0.23346 | 0.11902 | 0.13275 | -122.4014 | 0.12817 | 0.13275 | 0.07782 | -122.4106
1174.8906 | 122.4792 | -0.16022 | 122.2092 | -0.016174 | 0.017325 | 0.00059389 | 0.0063211 | 0.055929 | -0.0024267 | -0.0029053 | -0.0084684 | 0.0012048 | -0.032699 | 0.027258 | 0.0070301 | -0.0035526 | -0.050354 | -0.054932 | -0.027466 | 0.022888 | 0.064087 | -0.041199 | -0.20142 | -0.10071 | -0.050354 | -0.19226 | -0.059509 | -0.054932 | -0.10071 | -0.21057 | 0.11902 | -0.041199 | -122.1451 | 0.10528 | 0.1831 | 0.2243 | -122.2595 | 0.059509 | -0.050354 | -122.2687 | 0.059509 | -0.032044 | 0.01831 | -122.2641 | 0.2243 | 0.10986 | 0.13275 | -122.4106 | 0.10071 | 0.10528 | 0.10986 | -122.4197
1176.6406 | 122.3373 | -0.2243 | 122.2549 | -0.0085447 | 0.010062 | 0.0037983 | 0.0052531 | 0.05422 | -0.0077673 | -0.0035461 | -0.016098 | -0.0024268 | -0.034835 | 0.025122 | 0.0061757 | -0.0029116 | -0.064087 | -0.009155 | 0.022888 | 0.045776 | 0.041199 | -0.018311 | -0.14191 | -0.13275 | -0.027466 | -0.14191 | -0.086975 | -0.07782 | -0.086975 | -0.16479 | 0.20599 | 0.082397 | -122.2137 | 0.21515 | 0.27008 | 0.18768 | -122.319 | 0.13733 | 0.059509 | -122.3419 | 0.091553 | 0.082397 | 0.022888 | -122.3328 | 0.2655 | 0.16022 | 0.24719 | -122.3969 | 0.13733 | 0.14648 | 0.19684 | -122.4197
1178.3906 | 122.4747 | -0.16937 | 122.2366 | -0.0085447 | 0.012839 | -0.00026071 | 0.0058939 | 0.054433 | -0.0013587 | -0.0024779 | -0.00083936 | 0.0027002 | -0.034622 | 0.02619 | 0.0087391 | -0.0035526 | -0.045776 | -0.041199 | -0.027466 | 0.041199 | 0.050354 | -0.050354 | -0.16479 | -0.07782 | -0.022888 | -0.14191 | -0.091553 | -0.082397 | -0.064087 | -0.1831 | 0.11902 | 0.004578 | -122.1863 | 0.12817 | 0.21057 | 0.20599 | -122.2824 | 0.10529 | -0.013732 | -122.3282 | 0.091553 | 0.027466 | 0.041198 | -122.319 | 0.21973 | 0.1236 | 0.14191 | -122.4014 | 0.07782 | 0.086976 | 0.14649 | -122.4197
1180.0781 | 122.374 | -0.20599 | 122.2687 | -0.0085447 | 0.010489 | 0.00038029 | 0.0065347 | 0.051443 | -0.0071265 | -0.0061095 | -0.0084684 | -0.002854 | -0.034835 | 0.025763 | 0.0038259 | -0.0037662 | -0.059509 | -0.022888 | 0.022888 | 0.032043 | 0.032043 | 0 | -0.14648 | -0.11444 | -0.045776 | -0.15106 | -0.073242 | -0.07782 | -0.091553 | -0.19684 | 0.20599 | 0.05951 | -122.2366 | 0.18311 | 0.23804 | 0.17853 | -122.3282 | 0.11444 | 0.009156 | -122.3419 | 0.091553 | 0.054932 | 0.045776 | -122.3465 | 0.23804 | 0.14649 | 0.22888 | -122.4152 | 0.13275 | 0.12817 | 0.16022 | -122.4655
1181.8281 | 122.4655 | -0.14648 | 122.2366 | -0.00091566 | 0.014761 | 0.0010211 | 0.0069621 | 0.05422 | 0.0024865 | -0.0050415 | -0.016098 | 0.0027002 | -0.032272 | 0.028967 | 0.0091665 | -0.0048342 | -0.050354 | -0.054932 | -0.041199 | 0.027466 | 0.068665 | -0.054932 | -0.17395 | -0.10529 | -0.045776 | -0.18768 | -0.064087 | -0.068665 | -0.07782 | -0.17853 | 0.091552 | -0.027466 | -122.168 | 0.091552 | 0.17395 | 0.20142 | -122.287 | 0.068664 | -0.032044 | -122.3007 | 0.041198 | -0.041199 | -0.009155 | -122.3053 | 0.21515 | 0.09613 | 0.10529 | -122.4106 | 0.082397 | 0.077819 | 0.10071 | -122.4152
1183.5312 | 122.3877 | -0.22888 | 122.2595 | -0.00091566 | 0.011771 | 0.0029437 | 0.0041849 | 0.053152 | -0.0081945 | -0.0026917 | 0.0067901 | -0.0024268 | -0.033126 | 0.028967 | 0.0029713 | -0.0024844 | -0.059509 | -0.032043 | 0.004578 | 0.041199 | 0.018311 | -0.018311 | -0.14191 | -0.10986 | -0.036621 | -0.13275 | -0.082397 | -0.082397 | -0.086975 | -0.16937 | 0.21057 | 0.086975 | -122.2412 | 0.19684 | 0.27008 | 0.18311 | -122.319 | 0.14191 | 0.059509 | -122.3419 | 0.11902 | 0.096131 | 0.036622 | -122.3419 | 0.24719 | 0.16937 | 0.23346 | -122.4014 | 0.14649 | 0.14649 | 0.19226 | -122.4289
1185.2812 | 122.4564 | -0.16937 | 122.2137 | -0.00091566 | 0.01647 | 0.0040119 | 0.0020487 | 0.056142 | -0.0022131 | -0.0044007 | -0.0084684 | 0.0024866 | -0.036117 | 0.028967 | 0.0093801 | -0.0056888 | -0.064087 | -0.10529 | -0.073242 | 0.009155 | 0.082397 | -0.054932 | -0.19226 | -0.15106 | -0.07782 | -0.21515 | -0.064087 | -0.041199 | -0.10071 | -0.21057 | 0.11444 | -0.022888 | -122.1313 | 0.064087 | 0.17853 | 0.20142 | -122.2778 | 0.068665 | -0.041198 | -122.2778 | 0.018311 | -0.045776 | -0.004578 | -122.2549 | 0.25177 | 0.10529 | 0.096131 | -122.406 | 0.10529 | 0.12817 | 0.091553 | -122.4243
1187.0312 | 122.3282 | -0.21515 | 122.2549 | -0.0085447 | 0.014121 | 0.0014483 | 0.0054667 | 0.055074 | -0.0043493 | -0.0056823 | 0.0067901 | -0.0017858 | -0.032272 | 0.025336 | 0.0055349 | -0.0056888 | -0.022888 | -0.041199 | -0.009155 | 0.050354 | 0.059509 | -0.059509 | -0.1831 | -0.15106 | -0.059509 | -0.20142 | -0.045776 | -0.032043 | -0.10529 | -0.18768 | 0.15564 | 0.032044 | -122.1954 | 0.17395 | 0.2655 | 0.23346 | -122.2778 | 0.10986 | 0.027466 | -122.3007 | 0.064087 | 0.013733 | -0.013733 | -122.287 | 0.27466 | 0.19226 | 0.20599 | -122.438 | 0.16937 | 0.18311 | 0.15564 | -122.4426
1188.7188 | 122.4426 | -0.16479 | 122.2092 | -0.016174 | 0.01647 | 0.00059389 | 0.0020487 | 0.053792 | 0.0020593 | -0.0011963 | -0.0084684 | 0.0020594 | -0.033554 | 0.027258 | 0.010875 | -0.0052616 | 0 | -0.013733 | -0.013733 | 0.041199 | 0.050354 | -0.027466 | -0.17395 | -0.073242 | -0.036621 | -0.1831 | -0.073242 | -0.054932 | -0.091553 | -0.19226 | 0.13733 | -0.009155 | -122.1588 | 0.15106 | 0.20599 | 0.21515 | -122.2092 | 0.073242 | -0.027466 | -122.2824 | 0.091553 | -0.01831 | 0.009156 | -122.2641 | 0.21515 | 0.16479 | 0.15106 | -122.3831 | 0.091553 | 0.10986 | 0.12817 | -122.4014
1190.4688 | 122.4014 | -0.19684 | 122.2504 | -0.00091566 | 0.012198 | 0.0029437 | 0.0061075 | 0.050374 | -0.0062719 | -0.0050415 | -0.0084684 | -0.001145 | -0.033981 | 0.02619 | 0.0051075 | -0.0046206 | 0 | 0.022888 | 0.064087 | 0.07782 | 0.032043 | -0.009155 | -0.12817 | -0.041199 | 0.054932 | -0.054932 | -0.10071 | -0.091553 | -0.059509 | -0.14191 | 0.18768 | 0.068664 | -122.2183 | 0.21973 | 0.27466 | 0.20599 | -122.2504 | 0.13733 | 0.054931 | -122.3511 | 0.15564 | 0.14191 | 0.086975 | -122.3419 | 0.22888 | 0.19684 | 0.26093 | -122.3785 | 0.09613 | 0.10529 | 0.25177 | -122.3923
1192.2031 | 122.3877 | -0.1831 | 122.2412 | -0.016174 | 0.015402 | 0.0018757 | 0.0080301 | 0.055715 | -0.0022131 | -0.0041869 | -0.016098 | 0.0018456 | -0.033126 | 0.02619 | 0.0068165 | -0.0052616 | -0.068665 | -0.09613 | -0.054932 | -0.018311 | 0.10529 | -0.068665 | -0.17853 | -0.16479 | -0.091553 | -0.22888 | -0.032043 | -0.027466 | -0.10071 | -0.19226 | 0.11444 | 0.004577 | -122.1359 | 0.086975 | 0.16479 | 0.16022 | -122.3099 | 0.082397 | -0.009156 | -122.2733 | 0.01831 | -0.045777 | -0.036621 | -122.2687 | 0.28839 | 0.11444 | 0.12817 | -122.4197 | 0.15106 | 0.15564 | 0.091552 | -122.4335
1193.9688 | 122.4472 | -0.16937 | 122.2183 | -0.00091566 | 0.015402 | -0.0023969 | 0.0029031 | 0.052724 | 0.0022729 | -0.0024779 | -0.00083936 | 0.0020594 | -0.034195 | 0.03089 | 0.010021 | -0.004407 | 0 | -0.009155 | -0.009155 | 0.036621 | 0.07782 | -0.045776 | -0.17395 | -0.068665 | -0.045776 | -0.17395 | -0.059509 | -0.054932 | -0.09613 | -0.17395 | 0.1236 | -0.004577 | -122.1405 | 0.16022 | 0.20599 | 0.21057 | -122.2183 | 0.073243 | -0.004577 | -122.2778 | 0.10071 | -0.004577 | 0 | -122.2733 | 0.24719 | 0.16937 | 0.16022 | -122.3923 | 0.10986 | 0.11444 | 0.1236 | -122.3923
1195.7188 | 122.4014 | -0.19226 | 122.2504 | -0.00091566 | 0.012412 | 0.0027301 | 0.0052531 | 0.052938 | -0.0071265 | -0.0020507 | -0.00083936 | -0.0026404 | -0.034835 | 0.022986 | 0.0055349 | -0.0037662 | 0.032043 | 0.059509 | 0.086975 | 0.082397 | 0.022888 | -0.022888 | -0.12817 | -0.027466 | 0.073242 | -0.050354 | -0.082397 | -0.082397 | -0.059509 | -0.15564 | 0.16937 | 0.064087 | -122.2275 | 0.25177 | 0.27466 | 0.21057 | -122.2183 | 0.13275 | 0.036621 | -122.3328 | 0.16479 | 0.14191 | 0.10529 | -122.3328 | 0.21515 | 0.2243 | 0.27924 | -122.3785 | 0.10986 | 0.10986 | 0.2655 | -122.406
1197.4062 | 122.4655 | -0.1831 | 122.2366 | -0.00091566 | 0.015616 | 0.0023029 | 0.0082437 | 0.053579 | -0.00029051 | -0.0039733 | 0.0067901 | 0.002273 | -0.030349 | 0.028113 | 0.0066029 | -0.0054752 | -0.059509 | -0.10071 | -0.068665 | 0.004578 | 0.073242 | -0.059509 | -0.18768 | -0.14191 | -0.073242 | -0.21515 | -0.045776 | -0.041199 | -0.10529 | -0.1831 | 0.1236 | -0.004578 | -122.1634 | 0.082397 | 0.18768 | 0.19226 | -122.2961 | 0.077819 | 0 | -122.2824 | 0.041198 | -0.032044 | -0.032044 | -122.2778 | 0.25635 | 0.1236 | 0.11444 | -122.4243 | 0.13733 | 0.14191 | 0.10986 | -122.4197
1199.1562 | 122.3557 | -0.20599 | 122.2824 | -0.0085447 | 0.014334 | 0.0020893 | 0.0041849 | 0.053792 | -0.0045629 | -0.0058959 | -0.0084684 | -0.0039222 | -0.034408 | 0.027258 | 0.0057485 | -0.0037662 | -0.041199 | -0.004578 | 0.022888 | 0.041199 | 0.022888 | -0.018311 | -0.15106 | -0.10529 | -0.032043 | -0.13275 | -0.073242 | -0.07782 | -0.068665 | -0.15106 | 0.18768 | 0.054932 | -122.2595 | 0.20142 | 0.24719 | 0.19226 | -122.3236 | 0.13733 | 0.054932 | -122.3557 | 0.10071 | 0.073243 | 0.018311 | -122.3602 | 0.22888 | 0.1648 | 0.22888 | -122.4335 | 0.13275 | 0.12817 | 0.17395 | -122.4335
1200.9062 | 122.406 | -0.19684 | 122.2641 | -0.016174 | 0.015402 | 0.0018757 | 0.0050393 | 0.052511 | -0.00093131 | -0.0029053 | -0.00083936 | -0.0007178 | -0.035049 | 0.026831 | 0.0085255 | -0.0065432 | -0.082397 | -0.07782 | -0.068665 | -0.013733 | 0.09613 | -0.054932 | -0.17853 | -0.14648 | -0.086975 | -0.21973 | -0.027466 | -0.036621 | -0.09613 | -0.20142 | 0.14191 | 0.01831 | -122.168 | 0.11902 | 0.18311 | 0.16479 | -122.3465 | 0.10071 | -0.004578 | -122.2916 | 0.050354 | -0.022889 | -0.018311 | -122.3007 | 0.29297 | 0.11444 | 0.12817 | -122.4426 | 0.16937 | 0.16022 | 0.10986 | -122.4655
1202.5938 | 122.4243 | -0.18768 | 122.2366 | -0.00091566 | 0.016043 | 0.0016619 | 0.0024759 | 0.052511 | 0.0022729 | -0.0029053 | -0.00083936 | 0.0003504 | -0.032913 | 0.028754 | 0.011089 | -0.0071842 | -0.059509 | -0.07782 | -0.059509 | 0.009155 | 0.073242 | -0.041199 | -0.16479 | -0.13275 | -0.11444 | -0.25177 | -0.036621 | -0.032043 | -0.10986 | -0.20599 | 0.14648 | 0.022888 | -122.1634 | 0.10986 | 0.19684 | 0.17395 | -122.2961 | 0.07782 | -0.018311 | -122.2733 | 0.054932 | -0.064087 | -0.045776 | -122.2687 | 0.26092 | 0.12817 | 0.12817 | -122.4014 | 0.15106 | 0.15564 | 0.073242 | -122.4426
1204.3438 | 122.3648 | -0.20142 | 122.2504 | -0.00091566 | 0.013266 | 0.0031573 | 0.0067483 | 0.053579 | -0.0056311 | -0.0033325 | 0.0067901 | -0.0024268 | -0.03569 | 0.026617 | 0.0040395 | -0.006116 | 0.022888 | 0.073242 | 0.086975 | 0.091553 | 0.032043 | -0.032043 | -0.14648 | -0.041199 | 0.054932 | -0.07782 | -0.073242 | -0.073242 | -0.073242 | -0.14191 | 0.16937 | 0.054932 | -122.2183 | 0.27466 | 0.29297 | 0.23804 | -122.2275 | 0.12817 | 0.059509 | -122.3236 | 0.16022 | 0.1236 | 0.064087 | -122.3236 | 0.23346 | 0.2243 | 0.28839 | -122.3969 | 0.12817 | 0.12817 | 0.25635 | -122.3923
1206.0938 | 122.4792 | -0.16479 | 122.2458 | -0.0085447 | 0.014334 | 0.0012347 | 0.0050393 | 0.052938 | 0.0012049 | -0.0026917 | -0.00083936 | -0.0002906 | -0.034408 | 0.027685 | 0.0098073 | -0.0046206 | -0.045776 | -0.12817 | -0.091553 | -0.004578 | 0.07782 | -0.059509 | -0.17395 | -0.14191 | -0.12817 | -0.25177 | -0.027466 | -0.027466 | -0.10529 | -0.16022 | 0.10529 | -0.009155 | -122.168 | 0.036621 | 0.16022 | 0.16937 | -122.2916 | 0.059509 | 0.004578 | -122.2733 | 0.022888 | -0.086975 | -0.091553 | -122.2733 | 0.24261 | 0.11902 | 0.073242 | -122.4197 | 0.13733 | 0.13733 | 0.036621 | -122.406
1207.8438 | 122.4335 | -0.17853 | 122.2366 | -0.00091566 | 0.016684 | -0.0019695 | 0.0011941 | 0.053365 | 0.00013669 | -0.00098272 | -0.00083936 | 0.0031274 | -0.034622 | 0.03858 | 0.0093801 | -0.014447 | -0.068665 | -0.11902 | -0.086975 | -0.009155 | 0.059509 | -0.050354 | -0.16937 | -0.14648 | -0.12817 | -0.25177 | -0.045776 | -0.041199 | -0.10071 | -0.20142 | 0.12817 | 0.009155 | -122.1771 | 0.059509 | 0.16937 | 0.16022 | -122.3053 | 0.07782 | -0.022888 | -122.2824 | 0.032044 | -0.073242 | -0.050354 | -122.2778 | 0.23804 | 0.10986 | 0.091553 | -122.406 | 0.13275 | 0.13733 | 0.050354 | -122.438
1209.6094 | 122.3511 | -0.2243 | 122.2733 | 0.0067138 | 0.012625 | 0.0018757 | 0.0095255 | 0.053792 | -0.0062719 | -0.0029053 | -0.0084684 | -0.0041358 | -0.034622 | 0.033453 | 0.0031849 | -0.010175 | -0.009155 | 0.045776 | 0.086975 | 0.07782 | 0.041199 | -0.013733 | -0.15106 | -0.073242 | 0.041199 | -0.10986 | -0.073242 | -0.068665 | -0.068665 | -0.18768 | 0.21057 | 0.073242 | -122.2321 | 0.27008 | 0.30212 | 0.22888 | -122.2824 | 0.15564 | 0.036621 | -122.3465 | 0.15106 | 0.11444 | 0.07782 | -122.3419 | 0.2655 | 0.21515 | 0.31128 | -122.4243 | 0.15106 | 0.15564 | 0.2655 | -122.4609
1211.2969 | 122.3602 | -0.21057 | 122.2778 | -0.0085447 | 0.011557 | 0.0020893 | 0.0037577 | 0.052297 | -0.0037085 | -0.0024779 | 0.0067901 | -0.0009314 | -0.035049 | 0.027685 | 0.0051075 | -0.0063296 | 0 | 0.032043 | 0.073242 | 0.054932 | 0.032043 | -0.009155 | -0.12817 | -0.050354 | 0.004578 | -0.09613 | -0.082397 | -0.09613 | -0.073242 | -0.16022 | 0.20142 | 0.082397 | -122.2458 | 0.24261 | 0.2655 | 0.18311 | -122.2778 | 0.13733 | 0.050354 | -122.3602 | 0.16022 | 0.11444 | 0.064087 | -122.374 | 0.24261 | 0.21057 | 0.28381 | -122.406 | 0.12817 | 0.11444 | 0.21515 | -122.438
1213 | 122.438 | -0.1831 | 122.2366 | -0.00091566 | 0.015189 | 0.00080749 | 0.0078165 | 0.05422 | 0.00013669 | -0.0048279 | -0.0084684 | 0.001632 | -0.03334 | 0.039221 | 0.0063893 | -0.014661 | -0.059509 | -0.10986 | -0.068665 | 0.004578 | 0.086975 | -0.050354 | -0.18768 | -0.15564 | -0.091553 | -0.23804 | -0.032043 | -0.041199 | -0.11902 | -0.1831 | 0.13275 | -0.004578 | -122.1497 | 0.073242 | 0.18768 | 0.19226 | -122.2961 | 0.064086 | 0 | -122.2687 | 0.027465 | -0.054932 | -0.054932 | -122.2778 | 0.27008 | 0.1236 | 0.11444 | -122.4243 | 0.15106 | 0.14191 | 0.091552 | -122.4197
1214.7656 | 122.3831 | -0.19226 | 122.2504 | -0.0085447 | 0.014121 | 0.0018757 | 0.0069621 | 0.054433 | -0.0015723 | -0.0056823 | -0.00083936 | 0.0003504 | -0.032913 | 0.03089 | 0.0059621 | -0.0056888 | -0.073242 | -0.086975 | -0.054932 | -0.004578 | 0.073242 | -0.073242 | -0.19226 | -0.16479 | -0.091553 | -0.21973 | -0.032043 | -0.032043 | -0.10529 | -0.17853 | 0.11902 | 0 | -122.1771 | 0.10529 | 0.18768 | 0.18768 | -122.3236 | 0.086975 | 0.013733 | -122.2824 | 0.027466 | -0.027466 | -0.041199 | -122.2824 | 0.2655 | 0.11902 | 0.13733 | -122.4426 | 0.16022 | 0.16022 | 0.10071 | -122.4289
1216.5156 | 122.3785 | -0.21515 | 122.287 | -0.00091566 | 0.010916 | 0.0029437 | 0.0050393 | 0.054006 | -0.0054175 | -0.0046143 | -0.0084684 | -0.0034948 | -0.036331 | 0.028754 | 0.0053211 | -0.0052616 | -0.032043 | -0.022888 | 0.018311 | 0.032043 | 0.032043 | -0.018311 | -0.15106 | -0.10529 | -0.036621 | -0.14191 | -0.073242 | -0.07782 | -0.068665 | -0.15564 | 0.19684 | 0.064087 | -122.2549 | 0.19226 | 0.24719 | 0.18311 | -122.319 | 0.14648 | 0.059509 | -122.3602 | 0.10986 | 0.073242 | 0.013733 | -122.3648 | 0.24719 | 0.18311 | 0.23346 | -122.438 | 0.14191 | 0.13733 | 0.17853 | -122.4426
1218.2031 | 122.4792 | -0.16022 | 122.2595 | 0.0067138 | 0.012839 | 0.0023029 | 0.0026895 | 0.051443 | -0.00093131 | -0.0041869 | -0.00083936 | -7.6996e-05 | -0.032913 | 0.026831 | 0.0076711 | -0.0059024 | 0.027466 | 0.036621 | 0.059509 | 0.07782 | 0.027466 | 0 | -0.14648 | -0.036621 | 0.022888 | -0.09613 | -0.091553 | -0.073242 | -0.064087 | -0.14191 | 0.16022 | 0.013733 | -122.2321 | 0.19684 | 0.23804 | 0.2243 | -122.2321 | 0.09613 | 0.01831 | -122.3511 | 0.1236 | 0.064087 | 0.045777 | -122.3328 | 0.18768 | 0.18768 | 0.21973 | -122.406 | 0.068664 | 0.086975 | 0.1831 | -122.4014
1219.9688 | 122.4152 | -0.19226 | 122.2916 | -0.00091566 | 0.010916 | 0.0023029 | 0.0084573 | 0.053152 | -0.0073401 | -0.0044007 | -0.00083936 | -0.0043494 | -0.035049 | 0.027258 | 0.0061757 | -0.0046206 | -0.041199 | -0.018311 | 0.022888 | 0.050354 | 0.050354 | -0.041199 | -0.14191 | -0.07782 | 0.013733 | -0.10986 | -0.07782 | -0.07782 | -0.059509 | -0.16022 | 0.15106 | 0.050354 | -122.2412 | 0.17395 | 0.24261 | 0.19226 | -122.3328 | 0.13275 | 0.032044 | -122.3694 | 0.11444 | 0.082398 | 0.050354 | -122.3694 | 0.24261 | 0.15106 | 0.21515 | -122.4335 | 0.11444 | 0.11444 | 0.20599 | -122.4518
1221.7031 | 122.3831 | -0.21057 | 122.2595 | -0.00091566 | 0.01583 | 0.0027301 | 0.0061075 | 0.056142 | 0.00035029 | -0.0044007 | -0.0084684 | 0.0027002 | -0.032272 | 0.040076 | 0.0068165 | -0.017652 | -0.068665 | -0.086975 | -0.045776 | -0.013733 | 0.086975 | -0.036621 | -0.18768 | -0.15564 | -0.09613 | -0.22888 | -0.032043 | -0.041199 | -0.11902 | -0.19226 | 0.17395 | 0.022888 | -122.1725 | 0.1236 | 0.19684 | 0.17395 | -122.3282 | 0.091552 | 0.01831 | -122.2916 | 0.054931 | -0.018311 | -0.036621 | -122.3007 | 0.29755 | 0.14191 | 0.1648 | -122.4472 | 0.17853 | 0.16937 | 0.11444 | -122.4518
1223.3906 | 122.3877 | -0.19226 | 122.2961 | 0.0067138 | 0.0068574 | 0.0023029 | 0.00033966 | 0.052511 | -0.0052039 | -0.0048279 | -0.0084684 | -0.002854 | -0.037399 | 0.026404 | 0.0085255 | -0.0039798 | -0.036621 | -0.013733 | 0.018311 | 0.045776 | 0.050354 | -0.018311 | -0.14648 | -0.086975 | -0.045776 | -0.13733 | -0.064087 | -0.054932 | -0.073242 | -0.16479 | 0.17395 | 0.045777 | -122.2458 | 0.17853 | 0.23804 | 0.19226 | -122.3328 | 0.11902 | 0.027466 | -122.3602 | 0.10529 | 0.054932 | 0.027466 | -122.3511 | 0.24261 | 0.15564 | 0.21057 | -122.4426 | 0.12817 | 0.13733 | 0.14648 | -122.4609
1225.0938 | 122.3602 | -0.21973 | 122.2687 | -0.00091566 | 0.013693 | 0.0018757 | 0.0050393 | 0.053365 | -0.0024267 | -0.0061095 | -0.00083936 | 0.002273 | -0.035049 | 0.025122 | 0.0080983 | -0.0046206 | -0.018311 | -0.027466 | 0 | 0.036621 | 0.064087 | -0.059509 | -0.17853 | -0.13733 | -0.054932 | -0.1831 | -0.045776 | -0.041199 | -0.09613 | -0.17853 | 0.16022 | 0.041199 | -122.2046 | 0.19226 | 0.25635 | 0.21515 | -122.287 | 0.1236 | 0.041199 | -122.3145 | 0.082398 | 0.036622 | -0.004577 | -122.3099 | 0.28381 | 0.20142 | 0.21973 | -122.4472 | 0.17395 | 0.17853 | 0.16479 | -122.4472
1226.8594 | 122.438 | -0.1831 | 122.2595 | -0.00091566 | 0.014121 | -4.6912e-05 | 0.0039713 | 0.053579 | -0.00050411 | -0.0044007 | -0.016098 | -0.0002906 | -0.033981 | 0.026404 | 0.0085255 | -0.0035526 | 0.036621 | 0.022888 | 0.073242 | 0.07782 | 0.036621 | 0.004578 | -0.11444 | -0.022888 | 0.032043 | -0.09613 | -0.082397 | -0.07782 | -0.068665 | -0.13275 | 0.18768 | 0.068664 | -122.2229 | 0.20599 | 0.26092 | 0.19226 | -122.2229 | 0.11444 | 0.050354 | -122.3419 | 0.16022 | 0.086975 | 0.036621 | -122.3373 | 0.21973 | 0.21973 | 0.25635 | -122.374 | 0.10071 | 0.10528 | 0.21515 | -122.3923
1228.6094 | 122.4838 | -0.16937 | 122.2458 | -0.0085447 | 0.011557 | -0.00090151 | 0.0018351 | 0.05422 | 0.00056389 | -0.0037597 | -0.00083936 | 0.002273 | -0.034195 | 0.02854 | 0.0091665 | -0.0039798 | -0.036621 | -0.10986 | -0.082397 | -0.009155 | 0.07782 | -0.054932 | -0.17853 | -0.11902 | -0.11444 | -0.22888 | -0.041199 | -0.045776 | -0.09613 | -0.16937 | 0.11444 | -0.009155 | -122.168 | 0.05951 | 0.16022 | 0.16937 | -122.2824 | 0.073243 | 0 | -122.287 | 0.050354 | -0.059509 | -0.059509 | -122.2916 | 0.24719 | 0.13275 | 0.086976 | -122.4243 | 0.12817 | 0.1236 | 0.054932 | -122.4152
1230.2969 | 122.4838 | -0.15564 | 122.2687 | 0.0067138 | 0.014334 | -0.00068791 | 0.0039713 | 0.05187 | 0.00035029 | -0.0035461 | -0.0084684 | 0.0035546 | -0.034408 | 0.028754 | 0.0087391 | -0.004407 | -0.018311 | -0.054932 | -0.022888 | 0.027466 | 0.059509 | -0.041199 | -0.16937 | -0.082397 | -0.027466 | -0.18768 | -0.036621 | -0.032043 | -0.07782 | -0.1831 | 0.11444 | -0.013733 | -122.2092 | 0.10071 | 0.18311 | 0.19684 | -122.287 | 0.07782 | -0.027465 | -122.3053 | 0.073243 | -0.032043 | -0.004578 | -122.3007 | 0.21515 | 0.13733 | 0.13275 | -122.438 | 0.11902 | 0.1236 | 0.12817 | -122.4518
1232.0469 | 122.4335 | -0.19684 | 122.287 | -0.00091566 | 0.010489 | 0.0035847 | 0.0067483 | 0.051229 | -0.0056311 | -0.0035461 | -0.00083936 | -0.0030676 | -0.034622 | 0.025336 | 0.0048939 | -0.004407 | 0.018311 | 0.073242 | 0.073242 | 0.068665 | 0.032043 | -0.009155 | -0.13275 | -0.036621 | 0.068665 | -0.054932 | -0.091553 | -0.091553 | -0.068665 | -0.13275 | 0.18768 | 0.064087 | -122.2549 | 0.27008 | 0.2655 | 0.20142 | -122.2687 | 0.12817 | 0.064087 | -122.3785 | 0.16022 | 0.14191 | 0.077819 | -122.3785 | 0.22888 | 0.21515 | 0.27008 | -122.4197 | 0.10529 | 0.10529 | 0.2655 | -122.4197
1233.7969 | 122.438 | -0.16479 | 122.2595 | -0.00091566 | 0.013693 | 0.0014483 | 0.0054667 | 0.052938 | 0.0016321 | -0.0033325 | -0.00083936 | 0.003341 | -0.033126 | 0.027472 | 0.0098073 | -0.005048 | 0.018311 | -0.027466 | -0.009155 | 0.050354 | 0.050354 | -0.041199 | -0.17395 | -0.073242 | -0.018311 | -0.16022 | -0.050354 | -0.068665 | -0.091553 | -0.16022 | 0.1236 | -0.009155 | -122.2092 | 0.13733 | 0.21515 | 0.2243 | -122.2412 | 0.073242 | 0.004578 | -122.3099 | 0.091553 | 0.004578 | 0 | -122.3282 | 0.21515 | 0.18311 | 0.15564 | -122.4335 | 0.11444 | 0.09613 | 0.14648 | -122.4197
1235.5 | 122.4106 | -0.1831 | 122.2961 | 0.0067138 | 0.010489 | 0.0029437 | 0.0063211 | 0.052724 | -0.0069129 | -0.0039733 | -0.016098 | -0.0007178 | -0.033126 | 0.02619 | 0.0048939 | -0.0007754 | 0.027466 | 0.086975 | 0.086975 | 0.082397 | 0.027466 | -0.018311 | -0.13733 | -0.032043 | 0.091553 | -0.054932 | -0.068665 | -0.068665 | -0.059509 | -0.13733 | 0.16479 | 0.045776 | -122.2687 | 0.27008 | 0.2655 | 0.21973 | -122.2687 | 0.1236 | 0.045776 | -122.3648 | 0.15106 | 0.12817 | 0.082397 | -122.3648 | 0.21057 | 0.21057 | 0.27008 | -122.4335 | 0.11444 | 0.11444 | 0.27466 | -122.4335
1237.2344 | 122.3877 | -0.18768 | 122.3053 | -0.00091566 | 0.015189 | 0.0033709 | 0.0090983 | 0.052724 | -0.0013587 | -0.0037597 | -0.00083936 | -0.0002906 | -0.03334 | 0.026831 | 0.0040395 | -0.0048342 | -0.068665 | -0.09613 | -0.059509 | -0.013733 | 0.064087 | -0.041199 | -0.19226 | -0.15564 | -0.068665 | -0.22888 | -0.018311 | -0.013733 | -0.10071 | -0.17853 | 0.14648 | -0.004578 | -122.2412 | 0.091553 | 0.17395 | 0.17853 | -122.374 | 0.086975 | 0.009155 | -122.3236 | 0.032043 | -0.041199 | -0.050354 | -122.319 | 0.25177 | 0.11902 | 0.12817 | -122.4976 | 0.16937 | 0.17395 | 0.11902 | -122.4838
1238.9844 | 122.3969 | -0.20142 | 122.2961 | -0.0085447 | 0.012412 | 0.00080749 | 0.0035441 | 0.053579 | -0.0041357 | -0.0035461 | -0.0084684 | -0.0017858 | -0.034835 | 0.025336 | 0.0070301 | -0.0029116 | 0.027466 | 0.050354 | 0.068665 | 0.082397 | 0.036621 | -0.004578 | -0.1236 | -0.022888 | 0.013733 | -0.086975 | -0.07782 | -0.073242 | -0.07782 | -0.14648 | 0.19684 | 0.07782 | -122.2595 | 0.25177 | 0.28381 | 0.20599 | -122.2687 | 0.1236 | 0.054932 | -122.374 | 0.17853 | 0.11444 | 0.059509 | -122.3694 | 0.23804 | 0.22888 | 0.27008 | -122.4197 | 0.1236 | 0.12817 | 0.21515 | -122.4426
1240.6719 | 122.4289 | -0.19226 | 122.2733 | -0.00091566 | 0.013693 | 0.0033709 | 0.0039713 | 0.053365 | -0.0022131 | -0.0044007 | -0.0084684 | 0.000564 | -0.035476 | 0.027045 | 0.0085255 | -0.0059024 | 0.032043 | 0.045776 | 0.064087 | 0.091553 | 0.018311 | -0.004578 | -0.13275 | -0.013733 | 0.032043 | -0.091553 | -0.086975 | -0.086975 | -0.064087 | -0.12817 | 0.18768 | 0.05951 | -122.2549 | 0.23804 | 0.28381 | 0.2243 | -122.2412 | 0.12817 | 0.064087 | -122.3602 | 0.17853 | 0.10071 | 0.036621 | -122.3602 | 0.21057 | 0.2243 | 0.25635 | -122.406 | 0.10529 | 0.10529 | 0.2243 | -122.4014
1242.4219 | 122.4518 | -0.16022 | 122.2504 | -0.00091566 | 0.019461 | 0.00038029 | 0.0039713 | 0.053579 | 0.0027003 | -0.0029053 | -0.0084684 | 0.0024866 | -0.03334 | 0.027899 | 0.0087391 | -0.0052616 | 0.009155 | -0.027466 | -0.009155 | 0.050354 | 0.064087 | -0.041199 | -0.19226 | -0.07782 | -0.032043 | -0.19226 | -0.041199 | -0.036621 | -0.09613 | -0.16479 | 0.11902 | -0.032044 | -122.1863 | 0.13275 | 0.21057 | 0.24261 | -122.2412 | 0.064087 | -0.004578 | -122.2916 | 0.082397 | -0.032044 | -0.027466 | -122.287 | 0.2243 | 0.16937 | 0.15106 | -122.4426 | 0.11902 | 0.1236 | 0.12817 | -122.4152
1244.1094 | 122.3785 | -0.2243 | 122.287 | -0.00091566 | 0.012198 | 0.0031573 | 0.0020487 | 0.052083 | -0.0041357 | -0.0011963 | -0.0084684 | 0.0003504 | -0.036544 | 0.026831 | 0.0057485 | -0.0029116 | 0.027466 | 0.036621 | 0.054932 | 0.064087 | 0.032043 | -0.009155 | -0.1236 | -0.045776 | 0.009155 | -0.1236 | -0.068665 | -0.082397 | -0.059509 | -0.12817 | 0.21515 | 0.10071 | -122.2549 | 0.26093 | 0.28839 | 0.18768 | -122.2595 | 0.16479 | 0.09613 | -122.3557 | 0.17853 | 0.10071 | 0.004578 | -122.3694 | 0.25635 | 0.25177 | 0.27924 | -122.4106 | 0.15564 | 0.14191 | 0.23346 | -122.4152
1245.8594 | 122.4518 | -0.16022 | 122.2504 | -0.00091566 | 0.017325 | -0.00090151 | 0.0048257 | 0.053579 | 0.00035029 | -0.0031189 | -0.00083936 | 0.0035546 | -0.033554 | 0.027685 | 0.0095937 | -0.0054752 | 0.018311 | -0.036621 | -0.013733 | 0.032043 | 0.054932 | -0.036621 | -0.16937 | -0.059509 | -0.022888 | -0.18768 | -0.041199 | -0.054932 | -0.091553 | -0.15106 | 0.1236 | -0.009156 | -122.1954 | 0.1236 | 0.19226 | 0.20142 | -122.2321 | 0.068664 | 0.009155 | -122.2916 | 0.10071 | -0.027466 | -0.036621 | -122.3053 | 0.21515 | 0.17853 | 0.14648 | -122.4197 | 0.11902 | 0.10528 | 0.13733 | -122.4014
1247.6094 | 122.5159 | -0.15564 | 122.2824 | -0.00091566 | 0.013907 | -0.0013287 | 0.0061075 | 0.055074 | -0.0024267 | -0.0011963 | 0.0067901 | -7.6996e-05 | -0.032272 | 0.027685 | 0.0074575 | -0.0041934 | -0.004578 | -0.004578 | 0.027466 | 0.064087 | 0.054932 | -0.018311 | -0.14191 | -0.027466 | 0.022888 | -0.086975 | -0.073242 | -0.086975 | -0.045776 | -0.12817 | 0.13733 | 0.013733 | -122.2275 | 0.15106 | 0.21973 | 0.20599 | -122.287 | 0.10986 | 0.027466 | -122.3557 | 0.12817 | 0.068665 | 0.041199 | -122.3694 | 0.21057 | 0.15106 | 0.18311 | -122.4243 | 0.082398 | 0.068665 | 0.17853 | -122.4106
1249.3594 | 122.4609 | -0.16022 | 122.2916 | 0.0067138 | 0.020102 | 0.00016669 | 0.0043985 | 0.053152 | -0.00071771 | -0.0014099 | 0.01442 | 0.0044092 | -0.033126 | 0.02854 | 0.0089527 | -0.004407 | -0.013733 | -0.082397 | -0.045776 | 0.013733 | 0.059509 | -0.064087 | -0.16022 | -0.10986 | -0.068665 | -0.21057 | -0.032043 | -0.032043 | -0.082397 | -0.16937 | 0.09613 | 0 | -122.2321 | 0.07782 | 0.17395 | 0.17395 | -122.3053 | 0.07782 | -0.009156 | -122.3236 | 0.050354 | -0.050354 | -0.041198 | -122.3236 | 0.21973 | 0.14648 | 0.11444 | -122.4518 | 0.12817 | 0.12817 | 0.091552 | -122.4609
1251.1094 | 122.4106 | -0.17853 | 122.2641 | -0.00091566 | 0.012625 | 0.0057209 | 0.0052531 | 0.055288 | -0.0084081 | -0.0054687 | -0.00083936 | -0.0015722 | -0.033981 | 0.02619 | 0.0051075 | -0.0024844 | -0.018311 | 0.013733 | 0.036621 | 0.068665 | 0.045776 | -0.032043 | -0.15564 | -0.054932 | 0.064087 | -0.064087 | -0.054932 | -0.054932 | -0.059509 | -0.1236 | 0.14648 | 0.022888 | -122.2183 | 0.19226 | 0.24719 | 0.22431 | -122.2824 | 0.11902 | 0.054932 | -122.319 | 0.1236 | 0.11444 | 0.059509 | -122.319 | 0.2243 | 0.16022 | 0.21515 | -122.4197 | 0.1236 | 0.1236 | 0.24261 | -122.3877
1252.8906 | 122.3602 | -0.18768 | 122.3007 | -0.00091566 | 0.016257 | 0.0044391 | 0.0073893 | 0.053365 | -0.0052039 | -0.0031189 | 0.0067901 | -0.0009314 | -0.036117 | 0.030035 | 0.0055349 | -0.0091068 | 0.009155 | 0.027466 | 0.050354 | 0.082397 | 0.032043 | -0.022888 | -0.15106 | -0.07782 | 0.022888 | -0.10986 | -0.054932 | -0.045776 | -0.054932 | -0.15106 | 0.16479 | 0.036621 | -122.2687 | 0.21515 | 0.27008 | 0.23346 | -122.2916 | 0.13275 | 0.036621 | -122.3557 | 0.10986 | 0.07782 | 0.041199 | -122.3465 | 0.21973 | 0.19684 | 0.23804 | -122.4518 | 0.13275 | 0.14191 | 0.21057 | -122.4518
1254.6562 | 122.493 | -0.15106 | 122.2961 | -0.00091566 | 0.01348 | 0.0014483 | 0.0041849 | 0.053152 | -0.0024267 | -0.0031189 | -0.0084684 | 0.0003504 | -0.035263 | 0.030035 | 0.0074575 | -0.0046206 | 0.036621 | 0.036621 | 0.07782 | 0.068665 | 0.050354 | 0 | -0.12817 | 0.004578 | 0.027466 | -0.07782 | -0.064087 | -0.07782 | -0.041199 | -0.13733 | 0.15106 | 0.022888 | -122.2458 | 0.18768 | 0.21973 | 0.19684 | -122.2595 | 0.10986 | 0.013733 | -122.3602 | 0.15564 | 0.073242 | 0.059509 | -122.374 | 0.20142 | 0.18768 | 0.22888 | -122.4243 | 0.086975 | 0.073242 | 0.17853 | -122.4335
1256.4062 | 122.4426 | -0.16022 | 122.287 | -0.0085447 | 0.021597 | -0.00026071 | 0.0073893 | 0.052724 | 0.0014185 | -0.0039733 | 0.0067901 | 0.0009912 | -0.029922 | 0.02619 | 0.0078847 | -0.006116 | -0.004578 | -0.045776 | -0.027466 | -0.032043 | 0.073242 | -0.032043 | -0.17853 | -0.091553 | -0.054932 | -0.19226 | -0.027466 | -0.022888 | -0.09613 | -0.16022 | 0.12817 | -0.018311 | -122.2137 | 0.11444 | 0.12817 | 0.14648 | -122.2916 | 0.064087 | 0 | -122.3145 | 0.068664 | -0.032044 | -0.032044 | -122.3099 | 0.23346 | 0.15564 | 0.13275 | -122.4655 | 0.13275 | 0.13733 | 0.10528 | -122.4472
1258.1094 | 122.374 | -0.1831 | 122.3099 | -0.00091566 | 0.013693 | 0.0027301 | 0.0050393 | 0.053579 | -0.0049903 | -0.0031189 | -0.00083936 | 0.0027002 | -0.034195 | 0.02619 | 0.0053211 | -0.0035526 | -0.050354 | -0.045776 | -0.032043 | 0.018311 | 0.068665 | -0.045776 | -0.18768 | -0.13733 | -0.054932 | -0.17395 | -0.032043 | -0.009155 | -0.073242 | -0.16479 | 0.13733 | -0.004578 | -122.2412 | 0.13733 | 0.20142 | 0.20599 | -122.3602 | 0.10986 | 0.01831 | -122.3419 | 0.045776 | 0.009155 | -0.009155 | -122.319 | 0.25177 | 0.13275 | 0.15106 | -122.4976 | 0.15106 | 0.17395 | 0.12817 | -122.4747
1259.8594 | 122.3877 | -0.20142 | 122.3007 | -0.00091566 | 0.013693 | 0.0029437 | 0.0050393 | 0.052938 | -0.0047765 | -0.0035461 | -0.0084684 | -0.001145 | -0.034835 | 0.025549 | 0.0031849 | -0.003339 | -0.036621 | -0.018311 | 0.018311 | 0.050354 | 0.027466 | -0.036621 | -0.15564 | -0.082397 | -0.009155 | -0.13275 | -0.059509 | -0.032043 | -0.054932 | -0.1236 | 0.1648 | 0.045776 | -122.2733 | 0.18311 | 0.25177 | 0.20599 | -122.3373 | 0.14648 | 0.07782 | -122.3602 | 0.11902 | 0.068665 | -0.009155 | -122.3328 | 0.22888 | 0.1648 | 0.21973 | -122.4564 | 0.14191 | 0.16937 | 0.19226 | -122.4243
1261.5469 | 122.4014 | -0.18768 | 122.3099 | -0.0085447 | 0.01348 | 0.0025165 | 0.0029031 | 0.05422 | -0.0030677 | -0.0041869 | 0.0067901 | -0.0017858 | -0.03804 | 0.027899 | 0.010021 | -0.003339 | 0.036621 | 0.050354 | 0.073242 | 0.073242 | 0.045776 | -0.009155 | -0.12817 | -0.018311 | 0.032043 | -0.091553 | -0.041199 | -0.059509 | -0.041199 | -0.14191 | 0.17853 | 0.059509 | -122.2641 | 0.23804 | 0.26092 | 0.20142 | -122.2733 | 0.14648 | 0.045776 | -122.3511 | 0.16937 | 0.09613 | 0.050354 | -122.3694 | 0.23346 | 0.2243 | 0.26092 | -122.438 | 0.14648 | 0.12817 | 0.21973 | -122.4518
1263.2344 | 122.374 | -0.1831 | 122.3282 | -0.0085447 | 0.013693 | 0.0029437 | 0.0088847 | 0.05187 | -0.0037085 | -0.0065369 | 0.0067901 | -0.002854 | -0.03334 | 0.03089 | 0.0063893 | -0.0086796 | 0.032043 | 0.059509 | 0.07782 | 0.073242 | 0.027466 | -0.018311 | -0.14648 | -0.013733 | 0.086975 | -0.073242 | -0.068665 | -0.059509 | -0.054932 | -0.13733 | 0.16479 | 0.036621 | -122.3007 | 0.24261 | 0.25635 | 0.21973 | -122.2961 | 0.12817 | 0.045776 | -122.3969 | 0.16937 | 0.10986 | 0.064087 | -122.3877 | 0.21057 | 0.21515 | 0.26092 | -122.4747 | 0.11444 | 0.1236 | 0.27008 | -122.4655
1264.9844 | 122.3785 | -0.19684 | 122.287 | -0.00091566 | 0.010275 | 0.0029437 | 0.0018351 | 0.053365 | -0.0024267 | -0.0029053 | -0.00083936 | 0.000564 | -0.035904 | 0.032172 | 0.0089527 | -0.0086796 | 0.041199 | 0.022888 | 0.064087 | 0.064087 | 0.027466 | 0.004578 | -0.1236 | -0.036621 | 0.009155 | -0.10071 | -0.073242 | -0.041199 | -0.054932 | -0.1236 | 0.20142 | 0.073242 | -122.2595 | 0.21973 | 0.26093 | 0.18768 | -122.2458 | 0.14191 | 0.073242 | -122.3602 | 0.16022 | 0.09613 | 0.022888 | -122.3282 | 0.2243 | 0.23804 | 0.26093 | -122.4106 | 0.1236 | 0.15564 | 0.20599 | -122.4106
1266.6562 | 122.4747 | -0.13733 | 122.2961 | -0.0085447 | 0.014548 | 0.0025165 | 0.0078165 | 0.053792 | -0.00071771 | -0.0050415 | -0.0084684 | 0.002273 | -0.033767 | 0.032599 | 0.0072437 | -0.0099612 | -0.032043 | -0.11902 | -0.082397 | 0.009155 | 0.086975 | -0.059509 | -0.1831 | -0.12817 | -0.073242 | -0.20142 | -0.018311 | -0.013733 | -0.10529 | -0.16479 | 0.07782 | -0.045776 | -122.2092 | 0.01831 | 0.14648 | 0.19226 | -122.3282 | 0.032043 | -0.027466 | -122.3145 | 0.009155 | -0.064087 | -0.036621 | -122.3099 | 0.2243 | 0.10529 | 0.054932 | -122.4792 | 0.11902 | 0.1236 | 0.064087 | -122.4609
1268.4062 | 122.5204 | -0.14648 | 122.2549 | 0.0067138 | 0.013907 | 0.0018757 | 0.00098046 | 0.057424 | 0.00099129 | -0.0046143 | -0.00083936 | 0.0009912 | -0.034835 | 0.034308 | 0.010021 | -0.012097 | -0.004578 | -0.059509 | -0.013733 | 0.022888 | 0.054932 | -0.018311 | -0.16022 | -0.050354 | -0.013733 | -0.11444 | -0.091553 | -0.054932 | -0.050354 | -0.12817 | 0.12817 | -0.013733 | -122.2 | 0.086975 | 0.16937 | 0.1831 | -122.2595 | 0.09613 | 0.01831 | -122.3465 | 0.09613 | 0.032043 | 0.013733 | -122.3099 | 0.20142 | 0.14191 | 0.13275 | -122.4152 | 0.054931 | 0.091552 | 0.13275 | -122.3831
1270.1094 | 122.3785 | -0.19226 | 122.2916 | -0.00091566 | 0.014334 | 0.0014483 | 0.0084573 | 0.052083 | -0.0045629 | -0.0024779 | -0.00083936 | 0.0007776 | -0.032699 | 0.03089 | 0.0031849 | -0.0086796 | 0.041199 | 0.050354 | 0.086975 | 0.073242 | 0.032043 | -0.013733 | -0.13733 | -0.022888 | 0.07782 | -0.064087 | -0.059509 | -0.045776 | -0.041199 | -0.1236 | 0.17853 | 0.054932 | -122.2595 | 0.24261 | 0.2655 | 0.21057 | -122.2504 | 0.15106 | 0.068665 | -122.3511 | 0.16937 | 0.12817 | 0.059509 | -122.3373 | 0.2243 | 0.23346 | 0.27924 | -122.4289 | 0.13275 | 0.14648 | 0.27008 | -122.4152
1271.8438 | 122.4609 | -0.17395 | 122.2916 | -0.00091566 | 0.015616 | 0.00038029 | 0.0046121 | 0.05422 | 0.0020593 | -0.0020507 | -0.00083936 | 0.000564 | -0.033554 | 0.03324 | 0.0095937 | -0.012952 | -0.050354 | -0.10529 | -0.073242 | -0.009155 | 0.073242 | -0.045776 | -0.17395 | -0.11902 | -0.11902 | -0.24719 | -0.022888 | -0.013733 | -0.068665 | -0.17395 | 0.12817 | 0 | -122.2183 | 0.068664 | 0.16479 | 0.16479 | -122.3419 | 0.10528 | 0 | -122.3145 | 0.054931 | -0.073242 | -0.073242 | -122.3053 | 0.24719 | 0.1236 | 0.10071 | -122.4655 | 0.15106 | 0.16022 | 0.054931 | -122.4655
1273.5312 | 122.5021 | -0.14648 | 122.2733 | -0.00091566 | 0.012198 | 0.0010211 | 0.0022623 | 0.05486 | -0.0024267 | -0.0022643 | -0.00083936 | 0.0003504 | -0.036331 | 0.030035 | 0.0078847 | -0.0063296 | 0.036621 | 0.018311 | 0.041199 | 0.086975 | 0.036621 | -0.013733 | -0.13733 | 0 | 0.045776 | -0.09613 | -0.073242 | -0.073242 | -0.036621 | -0.13733 | 0.13275 | 0.009155 | -122.2366 | 0.16479 | 0.23346 | 0.2243 | -122.2366 | 0.10986 | 0.009155 | -122.3465 | 0.14648 | 0.050354 | 0.041199 | -122.3465 | 0.18311 | 0.18311 | 0.18768 | -122.4106 | 0.073242 | 0.073242 | 0.19226 | -122.4106
1275.2188 | 122.5113 | -0.15106 | 122.2733 | 0.0067138 | 0.012839 | 0.0010211 | 0.0035441 | 0.053365 | 0.00099129 | -0.0014099 | 0.0067901 | 0.0012048 | -0.034195 | 0.029608 | 0.0074575 | -0.0065432 | -0.082397 | -0.1236 | -0.086975 | -0.009155 | 0.064087 | -0.041199 | -0.17395 | -0.11902 | -0.10071 | -0.21973 | -0.027466 | -0.018311 | -0.086975 | -0.1831 | 0.10986 | -0.022888 | -122.2092 | 0.027466 | 0.14191 | 0.16479 | -122.3557 | 0.064087 | -0.032043 | -122.3007 | 0.032043 | -0.068665 | -0.036622 | -122.2916 | 0.21515 | 0.068665 | 0.064087 | -122.4472 | 0.1236 | 0.13275 | 0.050354 | -122.4564
1276.9688 | 122.3785 | -0.19226 | 122.3145 | -0.016174 | 0.013693 | 0.0040119 | 0.0050393 | 0.053792 | -0.0052039 | -0.0048279 | -0.00083936 | -0.0015722 | -0.035904 | 0.027258 | 0.0038259 | -0.0056888 | 0.009155 | 0.027466 | 0.050354 | 0.082397 | 0.054932 | -0.027466 | -0.14648 | -0.086975 | 0.022888 | -0.14191 | -0.064087 | -0.032043 | -0.073242 | -0.15106 | 0.16479 | 0.045777 | -122.2595 | 0.21973 | 0.27466 | 0.22888 | -122.3053 | 0.11902 | 0.041199 | -122.3785 | 0.10529 | 0.050354 | 0.009155 | -122.3465 | 0.24719 | 0.20142 | 0.24261 | -122.4609 | 0.12817 | 0.16022 | 0.21515 | -122.4655
1278.7188 | 122.3785 | -0.19684 | 122.2961 | -0.00091566 | 0.014761 | 0.0035847 | 0.0050393 | 0.054006 | -0.0034949 | -0.0031189 | 0.0067901 | -0.0026404 | -0.033981 | 0.029181 | 0.0074575 | -0.0052616 | -0.013733 | 0.004578 | 0.027466 | 0.054932 | 0.064087 | -0.027466 | -0.15564 | -0.09613 | -0.013733 | -0.15564 | -0.032043 | -0.032043 | -0.086975 | -0.16479 | 0.16937 | 0.041198 | -122.2321 | 0.20142 | 0.25177 | 0.21057 | -122.3099 | 0.10986 | 0.032043 | -122.3282 | 0.10071 | 0.041198 | 0.009155 | -122.3282 | 0.26093 | 0.18311 | 0.2243 | -122.4518 | 0.1648 | 0.1648 | 0.18311 | -122.4609
1280.4219 | 122.3923 | -0.17853 | 122.3007 | 0.0067138 | 0.0083526 | 0.0031573 | 0.0058939 | 0.052083 | -0.0041357 | -0.0044007 | -0.00083936 | -0.0017858 | -0.033981 | 0.026831 | 0.0053211 | -0.0035526 | 0.041199 | 0.064087 | 0.073242 | 0.073242 | 0.036621 | -0.004578 | -0.15564 | -0.013733 | 0.09613 | -0.064087 | -0.050354 | -0.064087 | -0.045776 | -0.14648 | 0.17395 | 0.022888 | -122.2641 | 0.24261 | 0.25177 | 0.22888 | -122.2595 | 0.13275 | 0.032044 | -122.3511 | 0.16479 | 0.11444 | 0.082397 | -122.3648 | 0.21515 | 0.21973 | 0.25177 | -122.4564 | 0.12817 | 0.11444 | 0.27466 | -122.4472
1282.1094 | 122.374 | -0.19226 | 122.319 | 0.0067138 | 0.016898 | 0.0014483 | 0.0065347 | 0.052083 | -0.0013587 | -0.0054687 | -0.00083936 | 0.0007776 | -0.032699 | 0.025976 | 0.0063893 | -0.0048342 | -0.022888 | -0.041199 | -0.032043 | 0.013733 | 0.050354 | -0.045776 | -0.16937 | -0.13275 | -0.054932 | -0.1831 | -0.013733 | -0.018311 | -0.082397 | -0.17395 | 0.14648 | 0.022888 | -122.2687 | 0.15106 | 0.20599 | 0.18311 | -122.3419 | 0.10986 | 0.018311 | -122.3328 | 0.05951 | 0.009156 | -0.009155 | -122.3373 | 0.24261 | 0.16937 | 0.16022 | -122.4884 | 0.17853 | 0.17395 | 0.13733 | -122.493
1283.8594 | 122.4472 | -0.16022 | 122.3053 | -0.0085447 | 0.01647 | 0.00038029 | 0.0024759 | 0.051656 | 0.0027003 | -0.0029053 | -0.00083936 | 0.0024866 | -0.033554 | 0.029608 | 0.0098073 | -0.0065432 | -0.050354 | -0.11444 | -0.073242 | 0.009155 | 0.082397 | -0.045776 | -0.1831 | -0.12817 | -0.09613 | -0.24261 | -0.022888 | -0.027466 | -0.073242 | -0.15564 | 0.11444 | -0.022888 | -122.2229 | 0.045776 | 0.16937 | 0.19226 | -122.3557 | 0.086975 | 0.004577 | -122.3282 | 0.032043 | -0.082398 | -0.086975 | -122.3328 | 0.24261 | 0.10986 | 0.086975 | -122.4884 | 0.13733 | 0.13275 | 0.064087 | -122.4609
1285.625 | 122.4152 | -0.16479 | 122.3373 | -0.00091566 | 0.010703 | 0.0027301 | 0.0029031 | 0.05187 | -0.0041357 | -0.0044007 | -0.00083936 | -0.0017858 | -0.033126 | 0.025549 | 0.0085255 | -0.002698 | 0.018311 | 0.059509 | 0.091553 | 0.082397 | 0.022888 | 0 | -0.1236 | -0.022888 | 0.041199 | -0.082397 | -0.068665 | -0.059509 | -0.036621 | -0.13275 | 0.16479 | 0.041199 | -122.3145 | 0.2243 | 0.24719 | 0.20599 | -122.319 | 0.12817 | 0.032044 | -122.406 | 0.14191 | 0.082398 | 0.050354 | -122.3969 | 0.18768 | 0.18311 | 0.25635 | -122.4609 | 0.09613 | 0.10529 | 0.20599 | -122.4701
1287.3594 | 122.3877 | -0.19226 | 122.3099 | -0.00091566 | 0.01647 | 0.0048663 | 0.0076029 | 0.053579 | -0.0011451 | -0.0056823 | 0.0067901 | 0.000564 | -0.033126 | 0.02619 | 0.0072437 | -0.0041934 | -0.050354 | -0.054932 | -0.022888 | 0.018311 | 0.064087 | -0.032043 | -0.17395 | -0.13733 | -0.054932 | -0.19226 | -0.018311 | -0.013733 | -0.082397 | -0.15564 | 0.16022 | 0.018311 | -122.2458 | 0.13733 | 0.21057 | 0.19226 | -122.3602 | 0.10986 | 0.036621 | -122.3282 | 0.054932 | 0 | -0.036621 | -122.3236 | 0.25635 | 0.14191 | 0.16937 | -122.4838 | 0.17395 | 0.17853 | 0.13733 | -122.4655
1289.1094 | 122.5204 | -0.13733 | 122.2916 | 0.014343 | 0.014121 | 0.0012347 | 0.0050393 | 0.056569 | -0.00071771 | -0.0031189 | -0.00083936 | 0.0012048 | -0.031631 | 0.028967 | 0.0068165 | -0.0071842 | -0.027466 | -0.091553 | -0.036621 | 0.045776 | 0.059509 | -0.050354 | -0.16937 | -0.068665 | -0.022888 | -0.17395 | -0.032043 | -0.013733 | -0.086975 | -0.17395 | 0.086975 | -0.032044 | -122.2321 | 0.045776 | 0.18311 | 0.21515 | -122.319 | 0.050354 | -0.036621 | -122.3236 | 0.068664 | -0.036621 | 0 | -122.3053 | 0.19684 | 0.10986 | 0.10071 | -122.4609 | 0.10529 | 0.1236 | 0.11444 | -122.4655
1290.875 | 122.4655 | -0.16937 | 122.2961 | 0.0067138 | 0.019461 | -0.00047431 | 0.0050393 | 0.053792 | -0.00029051 | -0.0035461 | -0.00083936 | 0.0031274 | -0.032486 | 0.028754 | 0.0078847 | -0.0052616 | -0.045776 | -0.091553 | -0.054932 | 0.013733 | 0.054932 | -0.032043 | -0.17853 | -0.11444 | -0.082397 | -0.22888 | -0.036621 | -0.018311 | -0.07782 | -0.16022 | 0.13733 | -0.009155 | -122.2412 | 0.07782 | 0.18311 | 0.19226 | -122.3419 | 0.091553 | 0.009156 | -122.3328 | 0.054932 | -0.059509 | -0.068665 | -122.3145 | 0.22431 | 0.1236 | 0.11444 | -122.4747 | 0.13275 | 0.15106 | 0.086976 | -122.4564
1292.6406 | 122.493 | -0.15564 | 122.2778 | 0.0067138 | 0.01583 | 0.0012347 | 0.0041849 | 0.054006 | 0.00056389 | -0.00055532 | 0.0067901 | 0.0007776 | -0.035049 | 0.025549 | 0.0089527 | -0.0039798 | -0.07782 | -0.11444 | -0.07782 | -0.004578 | 0.073242 | -0.032043 | -0.17395 | -0.12817 | -0.10529 | -0.21973 | -0.045776 | -0.027466 | -0.09613 | -0.16022 | 0.1236 | -0.01831 | -122.2046 | 0.041199 | 0.15106 | 0.16937 | -122.3557 | 0.05951 | -0.004577 | -122.3236 | 0.027466 | -0.064087 | -0.05951 | -122.3053 | 0.22888 | 0.07782 | 0.07782 | -122.4518 | 0.10986 | 0.12817 | 0.050354 | -122.438
1294.3281 | 122.5113 | -0.14648 | 122.2824 | -0.0085447 | 0.012625 | 0.0010211 | 0.0041849 | 0.052938 | -0.0019995 | -0.0014099 | -0.0084684 | 0.0009912 | -0.034408 | 0.028967 | 0.0070301 | -0.003339 | -0.07782 | -0.10529 | -0.091553 | 0 | 0.086975 | -0.054932 | -0.19226 | -0.12817 | -0.10071 | -0.19684 | -0.027466 | -0.027466 | -0.064087 | -0.16022 | 0.091552 | -0.045777 | -122.1954 | 0.041198 | 0.14648 | 0.19226 | -122.3602 | 0.082397 | -0.013733 | -122.3099 | 0.01831 | -0.050354 | -0.036621 | -122.3099 | 0.23346 | 0.068664 | 0.054931 | -122.4747 | 0.11902 | 0.11902 | 0.045776 | -122.4426
1296.0938 | 122.4014 | -0.17853 | 122.3007 | -0.0085447 | 0.010489 | 0.0020893 | 0.0061075 | 0.053365 | -0.0075537 | -0.0018371 | -0.00083936 | -0.0013586 | -0.034622 | 0.026831 | 0.0074575 | -0.0014164 | 0.009155 | 0.045776 | 0.068665 | 0.059509 | 0.027466 | -0.004578 | -0.13275 | -0.050354 | 0.022888 | -0.07782 | -0.064087 | -0.064087 | -0.032043 | -0.14191 | 0.17395 | 0.045777 | -122.2733 | 0.2243 | 0.23804 | 0.19226 | -122.2916 | 0.14648 | 0.036621 | -122.3648 | 0.12817 | 0.10071 | 0.064087 | -122.3648 | 0.20599 | 0.18768 | 0.24719 | -122.4335 | 0.11444 | 0.11444 | 0.20142 | -122.4426
1297.8438 | 122.4747 | -0.16937 | 122.3099 | -0.0085447 | 0.015189 | 0.0027301 | 0.0041849 | 0.055929 | 0.0016321 | -0.0016235 | -0.00083936 | 0.0029138 | -0.035049 | 0.027472 | 0.0078847 | -0.0069706 | 0 | -0.082397 | -0.027466 | 0.018311 | 0.068665 | -0.032043 | -0.15106 | -0.09613 | -0.059509 | -0.20142 | -0.009155 | -0.022888 | -0.068665 | -0.17853 | 0.13733 | 0.018311 | -122.2412 | 0.086976 | 0.18768 | 0.16937 | -122.3099 | 0.10071 | -0.009155 | -122.319 | 0.073243 | -0.032043 | -0.022888 | -122.3328 | 0.23804 | 0.16937 | 0.14191 | -122.4609 | 0.16022 | 0.14649 | 0.10986 | -122.4884
1299.6094 | 122.3557 | -0.1831 | 122.3419 | -0.00091566 | 0.014548 | 0.0027301 | 0.0082437 | 0.053365 | -0.0064855 | -0.0048279 | -0.00083936 | -7.6996e-05 | -0.035904 | 0.026617 | 0.0042531 | -0.0048342 | 0.009155 | 0.022888 | 0.059509 | 0.082397 | 0.041199 | -0.018311 | -0.14191 | -0.073242 | 0.032043 | -0.10986 | -0.064087 | -0.036621 | -0.059509 | -0.13733 | 0.16479 | 0.041198 | -122.3007 | 0.20599 | 0.2655 | 0.2243 | -122.3328 | 0.1236 | 0.045776 | -122.406 | 0.10986 | 0.073242 | 0.027466 | -122.3785 | 0.2243 | 0.19226 | 0.24261 | -122.4838 | 0.11902 | 0.14648 | 0.21515 | -122.4792
1301.3594 | 122.3877 | -0.19684 | 122.3282 | -0.016174 | 0.0096344 | 0.0040119 | 0.0026895 | 0.054647 | -0.0058447 | -0.0039733 | -0.0084684 | -0.0013586 | -0.033767 | 0.025336 | 0.0059621 | -0.00163 | -0.018311 | -0.004578 | 0.041199 | 0.050354 | 0.041199 | 0.004578 | -0.13733 | -0.086975 | -0.004578 | -0.11902 | -0.059509 | -0.036621 | -0.036621 | -0.12817 | 0.20142 | 0.059509 | -122.287 | 0.19226 | 0.24719 | 0.18768 | -122.3465 | 0.16022 | 0.068664 | -122.3877 | 0.10986 | 0.077819 | 0.009155 | -122.3648 | 0.23804 | 0.17853 | 0.23804 | -122.4655 | 0.13733 | 0.16022 | 0.19226 | -122.4564
1303.0469 | 122.5021 | -0.14191 | 122.2916 | -0.00091566 | 0.01583 | 0.00059389 | 0.0054667 | 0.052511 | 0.00077749 | -0.0044007 | -0.00083936 | 0.0031274 | -0.035904 | 0.02854 | 0.010662 | -0.0056888 | 0.013733 | -0.041199 | -0.018311 | 0.041199 | 0.07782 | -0.036621 | -0.17853 | -0.068665 | -0.022888 | -0.15106 | -0.045776 | -0.018311 | -0.050354 | -0.14191 | 0.10529 | -0.036621 | -122.2137 | 0.10071 | 0.18311 | 0.21973 | -122.2778 | 0.091553 | 0 | -122.3373 | 0.073242 | -0.009155 | -0.009155 | -122.3099 | 0.21973 | 0.15564 | 0.1236 | -122.4701 | 0.096131 | 0.1236 | 0.11902 | -122.4335
1304.7969 | 122.406 | -0.19226 | 122.3099 | -0.00091566 | 0.0096344 | 0.0035847 | 0.0039713 | 0.052724 | -0.0077673 | -0.0022643 | -0.0084684 | -0.0030676 | -0.037399 | 0.024695 | 0.0046803 | -0.0029116 | -0.032043 | -0.041199 | 0.013733 | 0.041199 | 0.045776 | -0.013733 | -0.15564 | -0.09613 | -0.009155 | -0.1236 | -0.050354 | -0.032043 | -0.045776 | -0.14191 | 0.17853 | 0.036621 | -122.2641 | 0.15106 | 0.23346 | 0.19684 | -122.3419 | 0.14648 | 0.050354 | -122.3602 | 0.096131 | 0.068665 | 0.018311 | -122.3419 | 0.23804 | 0.16022 | 0.20599 | -122.4655 | 0.14191 | 0.16022 | 0.18311 | -122.4518
1306.4844 | 122.4655 | -0.16479 | 122.2824 | -0.00091566 | 0.016257 | 0.0029437 | 0.0046121 | 0.05422 | -0.0026403 | -0.0029053 | -0.0084684 | 0.0041956 | -0.031204 | 0.028754 | 0.0068165 | -0.0041934 | -0.032043 | -0.10071 | -0.082397 | 0 | 0.07782 | -0.068665 | -0.16937 | -0.14648 | -0.07782 | -0.21973 | -0.018311 | -0.022888 | -0.07782 | -0.17853 | 0.09613 | -0.004578 | -122.2046 | 0.064087 | 0.16479 | 0.16937 | -122.3145 | 0.086975 | -0.013733 | -122.3007 | 0.018311 | -0.054932 | -0.041199 | -122.3053 | 0.24261 | 0.13275 | 0.082398 | -122.4518 | 0.14648 | 0.14191 | 0.086975 | -122.4609
1308.2344 | 122.4655 | -0.15564 | 122.2961 | -0.0085447 | 0.018393 | 0.00059389 | 0.0058939 | 0.051443 | 0.0014185 | -0.0037597 | -0.00083936 | 0.0012048 | -0.031204 | 0.029394 | 0.0083119 | -0.0020572 | 0 | -0.082397 | -0.036621 | 0.027466 | 0.054932 | -0.032043 | -0.16937 | -0.09613 | -0.068665 | -0.21057 | -0.045776 | -0.022888 | -0.086975 | -0.16937 | 0.1236 | -0.013733 | -122.2412 | 0.073243 | 0.18311 | 0.19684 | -122.2961 | 0.068665 | -0.013733 | -122.3419 | 0.05951 | -0.054931 | -0.041198 | -122.319 | 0.21057 | 0.15564 | 0.11902 | -122.4655 | 0.10986 | 0.13275 | 0.086975 | -122.4655
1310 | 122.5204 | -0.15106 | 122.2549 | -0.00091566 | 0.015189 | 0.0027301 | 0.0063211 | 0.052511 | -0.0019995 | -0.0024779 | -0.00083936 | 0.0014184 | -0.033767 | 0.026404 | 0.0080983 | -0.004407 | -0.050354 | -0.10071 | -0.050354 | 0.036621 | 0.073242 | -0.050354 | -0.16022 | -0.09613 | -0.041199 | -0.17853 | -0.032043 | -0.013733 | -0.068665 | -0.15106 | 0.10071 | -0.009155 | -122.1817 | 0.050354 | 0.18768 | 0.19684 | -122.3053 | 0.082397 | 0 | -122.287 | 0.054932 | -0.027466 | -0.027466 | -122.2687 | 0.2243 | 0.10071 | 0.10071 | -122.4152 | 0.11902 | 0.13733 | 0.10986 | -122.406
1311.6875 | 122.4564 | -0.15564 | 122.287 | -0.0085447 | 0.017538 | 0.0010211 | 0.0069621 | 0.052938 | -0.0037085 | -0.0048279 | 0.0067901 | 0.0003504 | -0.03099 | 0.028967 | 0.0057485 | -0.00163 | -0.068665 | -0.09613 | -0.059509 | 0.004578 | 0.091553 | -0.068665 | -0.19684 | -0.13733 | -0.073242 | -0.21515 | -0.018311 | -0.013733 | -0.068665 | -0.16479 | 0.086975 | -0.041198 | -122.1954 | 0.05951 | 0.16022 | 0.20142 | -122.3557 | 0.086975 | -0.009155 | -122.3053 | 0.018311 | -0.059509 | -0.050354 | -122.3007 | 0.24719 | 0.086975 | 0.096131 | -122.4838 | 0.13733 | 0.14191 | 0.082398 | -122.4518
1313.4219 | 122.4976 | -0.13733 | 122.2733 | -0.0085447 | 0.017752 | -0.00026071 | 0.0063211 | 0.054433 | 0.00035029 | -0.0041869 | -0.00083936 | 0.0031274 | -0.032058 | 0.027258 | 0.0076711 | -0.0046206 | -0.013733 | -0.054932 | -0.013733 | 0.045776 | 0.059509 | -0.036621 | -0.16937 | -0.082397 | -0.013733 | -0.16022 | -0.041199 | -0.022888 | -0.082397 | -0.16022 | 0.10071 | -0.032044 | -122.2137 | 0.082397 | 0.18311 | 0.21515 | -122.287 | 0.054932 | -0.022888 | -122.3145 | 0.054932 | -0.022888 | 0 | -122.2961 | 0.19684 | 0.1236 | 0.1236 | -122.4426 | 0.09613 | 0.11444 | 0.1236 | -122.4335
1315.1094 | 122.3831 | -0.21057 | 122.3328 | -0.00091566 | 0.010275 | 0.00016669 | 0.0043985 | 0.052083 | -0.0081945 | -0.0026917 | -0.00083936 | -0.0007178 | -0.034622 | 0.028326 | 0.0057485 | -0.0012026 | 0.018311 | 0.022888 | 0.054932 | 0.068665 | 0.032043 | 0.004578 | -0.13733 | -0.045776 | 0.036621 | -0.09613 | -0.082397 | -0.050354 | -0.027466 | -0.1236 | 0.21515 | 0.073242 | -122.3007 | 0.23346 | 0.27924 | 0.20599 | -122.3145 | 0.18311 | 0.086975 | -122.4152 | 0.1648 | 0.11444 | 0.027466 | -122.3831 | 0.24261 | 0.22888 | 0.2655 | -122.4701 | 0.12817 | 0.16022 | 0.24719 | -122.4564
1316.8594 | 122.5067 | -0.17395 | 122.3007 | -0.0085447 | 0.012412 | 0.0018757 | 0.0022623 | 0.055288 | -0.00071771 | -0.0041869 | 0.0067901 | 0.001632 | -0.03334 | 0.027045 | 0.0091665 | -0.003339 | -0.073242 | -0.11902 | -0.073242 | 0.013733 | 0.086975 | -0.041199 | -0.17395 | -0.14191 | -0.10986 | -0.21515 | -0.032043 | -0.022888 | -0.07782 | -0.15564 | 0.13275 | 0 | -122.2137 | 0.054931 | 0.18768 | 0.18768 | -122.374 | 0.09613 | 0.01831 | -122.3328 | 0.032043 | -0.041199 | -0.059509 | -122.3236 | 0.26092 | 0.10071 | 0.10071 | -122.4747 | 0.14191 | 0.15106 | 0.064087 | -122.4564
1318.6094 | 122.4243 | -0.17853 | 122.2916 | -0.0085447 | 0.014121 | 0.0023029 | 0.0061075 | 0.053792 | -0.0090491 | -0.0063233 | 0.0067901 | -0.0026404 | -0.03334 | 0.025122 | 0.0046803 | -0.0024844 | -0.045776 | -0.032043 | 0.032043 | 0.059509 | 0.050354 | -0.004578 | -0.14191 | -0.064087 | 0.032043 | -0.082397 | -0.054932 | -0.041199 | -0.036621 | -0.1236 | 0.17395 | 0.036621 | -122.2412 | 0.14648 | 0.23804 | 0.20142 | -122.3373 | 0.14191 | 0.054932 | -122.3465 | 0.11444 | 0.096131 | 0.041199 | -122.3328 | 0.22888 | 0.13275 | 0.21057 | -122.4335 | 0.1236 | 0.13733 | 0.21057 | -122.4152
1320.375 | 122.5525 | -0.16022 | 122.2778 | -0.0085447 | 0.012198 | 0.0016619 | 0.0056803 | 0.052083 | 0.0012049 | -0.0022643 | -0.0084684 | 0.0029138 | -0.031845 | 0.027472 | 0.0083119 | -0.0052616 | -0.027466 | -0.09613 | -0.054932 | 0.004578 | 0.050354 | -0.045776 | -0.16022 | -0.073242 | -0.068665 | -0.16937 | -0.054932 | -0.032043 | -0.054932 | -0.13733 | 0.11444 | 0 | -122.2275 | 0.064087 | 0.16479 | 0.16479 | -122.3053 | 0.10528 | 0.022888 | -122.3328 | 0.086975 | -0.009156 | -0.032044 | -122.3099 | 0.21057 | 0.13275 | 0.10528 | -122.438 | 0.10528 | 0.12817 | 0.091552 | -122.4152
1322.125 | 122.438 | -0.14191 | 122.2961 | 0.0067138 | 0.016898 | 0.0025165 | 0.0086709 | 0.055929 | -0.0015723 | -0.0071777 | 0.0067901 | -0.0009314 | -0.031631 | 0.026617 | 0.0063893 | -0.0039798 | -0.068665 | -0.091553 | -0.050354 | -0.013733 | 0.07782 | -0.059509 | -0.18768 | -0.14648 | -0.082397 | -0.21057 | -0.027466 | -0.018311 | -0.086975 | -0.16937 | 0.082398 | -0.045776 | -122.2183 | 0.050354 | 0.12817 | 0.17395 | -122.3648 | 0.054932 | -0.027466 | -122.3236 | -0.004577 | -0.068664 | -0.041198 | -122.3145 | 0.21973 | 0.073242 | 0.091553 | -122.4838 | 0.11444 | 0.1236 | 0.05951 | -122.4655
1323.875 | 122.3923 | -0.18768 | 122.3373 | -0.00091566 | 0.010062 | 0.0031573 | 0.0031167 | 0.052724 | -0.0052039 | -0.0020507 | -0.00083936 | -0.0026404 | -0.035476 | 0.024481 | 0.0063893 | -0.0022708 | 0.027466 | 0.032043 | 0.050354 | 0.059509 | 0.036621 | -0.009155 | -0.14648 | -0.068665 | 0.004578 | -0.10529 | -0.068665 | -0.045776 | -0.045776 | -0.15564 | 0.17853 | 0.041199 | -122.3007 | 0.21973 | 0.24719 | 0.20599 | -122.3099 | 0.14191 | 0.032043 | -122.406 | 0.11902 | 0.082397 | 0.050354 | -122.3831 | 0.2243 | 0.21515 | 0.23804 | -122.4838 | 0.11902 | 0.14191 | 0.19226 | -122.493
1325.6406 | 122.4838 | -0.14191 | 122.3053 | -0.0085447 | 0.015402 | 0.00059389 | 0.0069621 | 0.053152 | -0.0015723 | -0.0046143 | -0.00083936 | 0.0027002 | -0.032272 | 0.036871 | 0.0087391 | -0.015515 | -0.059509 | -0.09613 | -0.068665 | 0.009155 | 0.073242 | -0.068665 | -0.19684 | -0.13275 | -0.059509 | -0.19684 | -0.013733 | -0.027466 | -0.091553 | -0.16022 | 0.073242 | -0.054931 | -122.2321 | 0.045777 | 0.15106 | 0.20599 | -122.3648 | 0.050354 | -0.01831 | -122.319 | 0.009156 | -0.054931 | -0.036621 | -122.3328 | 0.21515 | 0.082398 | 0.073242 | -122.5021 | 0.12817 | 0.11444 | 0.082398 | -122.4655
1327.375 | 122.5159 | -0.14648 | 122.2778 | 0.0067138 | 0.018607 | 0.0027301 | 0.0052531 | 0.055074 | 0.00099129 | -0.0037597 | 0.0067901 | 0.0009912 | -0.033126 | 0.029394 | 0.0091665 | -0.0086796 | -0.022888 | -0.050354 | -0.032043 | 0.027466 | 0.068665 | -0.036621 | -0.16937 | -0.068665 | -0.013733 | -0.16479 | -0.032043 | -0.027466 | -0.07782 | -0.15564 | 0.10986 | -0.022889 | -122.2092 | 0.09613 | 0.17395 | 0.19684 | -122.3007 | 0.068664 | -0.009156 | -122.3099 | 0.077819 | -0.018311 | -0.009155 | -122.3053 | 0.21515 | 0.1236 | 0.11444 | -122.4472 | 0.11444 | 0.11902 | 0.13275 | -122.4335
1329.0625 | 122.5296 | -0.13733 | 122.2778 | -0.00091566 | 0.012412 | 0.00059389 | 0.0046121 | 0.052511 | 0.00077749 | -0.0020507 | -0.00083936 | 0.0037684 | -0.034835 | 0.028967 | 0.0087391 | -0.0059024 | -0.059509 | -0.10071 | -0.064087 | 0.013733 | 0.086975 | -0.045776 | -0.17395 | -0.12817 | -0.09613 | -0.20599 | -0.022888 | -0.018311 | -0.068665 | -0.15106 | 0.091553 | -0.036621 | -122.1909 | 0.036621 | 0.15106 | 0.18768 | -122.3373 | 0.068664 | -0.013733 | -122.3007 | 0.009155 | -0.068665 | -0.054932 | -122.2961 | 0.2243 | 0.07782 | 0.073242 | -122.4518 | 0.11444 | 0.11902 | 0.041199 | -122.4289
1330.8281 | 122.4426 | -0.15564 | 122.3282 | -0.016174 | 0.014975 | 0.0020893 | 0.0054667 | 0.054647 | -0.0088355 | -0.0054687 | -0.0084684 | -0.0032812 | -0.034408 | 0.036871 | 0.0021169 | -0.012738 | 0.032043 | 0.068665 | 0.068665 | 0.09613 | 0.041199 | -0.004578 | -0.14191 | -0.009155 | 0.07782 | -0.032043 | -0.054932 | -0.050354 | -0.032043 | -0.14191 | 0.15106 | 0.013733 | -122.287 | 0.22431 | 0.25177 | 0.23804 | -122.2961 | 0.1236 | 0.013733 | -122.3831 | 0.14649 | 0.1236 | 0.10986 | -122.3785 | 0.19684 | 0.18768 | 0.22431 | -122.4701 | 0.10071 | 0.10529 | 0.23346 | -122.4701
1332.5156 | 122.3785 | -0.19226 | 122.3419 | -0.0085447 | 0.010062 | 0.0029437 | 0.00055326 | 0.052938 | -0.0052039 | -0.0058959 | -0.00083936 | -0.0005042 | -0.038253 | 0.024481 | 0.0072437 | -0.002698 | -0.009155 | -0.013733 | 0.036621 | 0.036621 | 0.045776 | 0 | -0.14648 | -0.086975 | -0.004578 | -0.1236 | -0.050354 | -0.041199 | -0.036621 | -0.11902 | 0.19226 | 0.045777 | -122.2961 | 0.17853 | 0.22888 | 0.18311 | -122.3511 | 0.15564 | 0.073242 | -122.3923 | 0.10529 | 0.068665 | -0.004577 | -122.3831 | 0.23804 | 0.18311 | 0.22888 | -122.4884 | 0.14191 | 0.15106 | 0.18768 | -122.4609
1334.2656 | 122.3923 | -0.16937 | 122.3465 | -0.016174 | 0.011984 | 0.0031573 | 0.0061075 | 0.053792 | -0.0052039 | -0.0071777 | -0.00083936 | -0.0007178 | -0.033554 | 0.02384 | 0.0044667 | -0.0039798 | 0.064087 | 0.054932 | 0.07782 | 0.082397 | 0.041199 | -0.009155 | -0.13275 | -0.013733 | 0.07782 | -0.045776 | -0.068665 | -0.059509 | -0.041199 | -0.11902 | 0.16022 | 0.036622 | -122.3053 | 0.22431 | 0.25177 | 0.21515 | -122.2824 | 0.12817 | 0.050354 | -122.4152 | 0.15564 | 0.1236 | 0.073243 | -122.406 | 0.21057 | 0.23346 | 0.24719 | -122.4792 | 0.10071 | 0.10986 | 0.24719 | -122.4655
1336.0156 | 122.4243 | -0.19226 | 122.319 | -0.00091566 | 0.011557 | 0.0037983 | 0.0058939 | 0.053792 | -0.0026403 | -0.0061095 | -0.00083936 | -0.0005042 | -0.036117 | 0.034308 | 0.0059621 | -0.010816 | -0.018311 | -0.045776 | 0.004578 | 0.036621 | 0.041199 | -0.009155 | -0.15106 | -0.07782 | -0.004578 | -0.10529 | -0.045776 | -0.027466 | -0.045776 | -0.12817 | 0.18311 | 0.041199 | -122.2778 | 0.14648 | 0.22888 | 0.18768 | -122.3373 | 0.14648 | 0.064087 | -122.3648 | 0.11444 | 0.086975 | 0.022888 | -122.3465 | 0.23346 | 0.17395 | 0.19684 | -122.4701 | 0.14648 | 0.16479 | 0.18768 | -122.4472
1337.7031 | 122.406 | -0.1831 | 122.3511 | 0.014343 | 0.01113 | 0.0031573 | 0.0043985 | 0.052297 | -0.0032813 | -0.0063233 | -0.0084684 | -0.0009314 | -0.034408 | 0.027258 | 0.0080983 | -0.0046206 | -0.004578 | -0.018311 | 0.013733 | 0.041199 | 0.045776 | -0.013733 | -0.13275 | -0.07782 | 0.004578 | -0.12817 | -0.041199 | -0.045776 | -0.050354 | -0.13275 | 0.16937 | 0.050354 | -122.3053 | 0.16479 | 0.2243 | 0.17395 | -122.3557 | 0.13275 | 0.050354 | -122.3923 | 0.10528 | 0.054931 | 0.004577 | -122.3969 | 0.22888 | 0.17853 | 0.19684 | -122.4838 | 0.14191 | 0.13733 | 0.18768 | -122.4838
1339.4375 | 117.7597 | -92.363 | 25.2365 | -0.016174 | 0.013693 | 0.0027301 | 0.0054667 | 0.055074 | -0.0032813 | -0.0056823 | -0.00083936 | -0.0054174 | -0.031417 | 0.037726 | 0.0023305 | 0.0030698 | 0.11902 | 0.10986 | 0.15106 | 0.16022 | 0.10071 | 0.050354 | -0.082397 | 0.068665 | 0.15106 | 0 | 0.032043 | 0.027466 | 0.041199 | -0.027466 | 92.4133 | 92.2806 | -25.1358 | 92.4728 | 92.5232 | 0.24261 | -25.1175 | 92.4042 | 92.3355 | -25.2045 | 92.4316 | 92.363 | 0.027466 | -25.209 | 92.4637 | 92.482 | 92.514 | -25.3189 | 92.395 | 92.3904 | 92.514 | -25.264
1341.1875 | 117.2836 | -92.0242 | 25.0305 | 0.0067138 | 0.0092072 | 0.0023029 | 0.0050393 | 0.050588 | -0.0017859 | -0.0048279 | -0.0084684 | -0.0034948 | -0.031631 | 0.041144 | 0.0068165 | 0.0049924 | 0.022888 | -0.027466 | 0.009155 | 0.059509 | 0.15564 | 0.018311 | -0.10986 | -0.041199 | 0.022888 | -0.12817 | 0.064087 | 0.064087 | 0.004578 | -0.091553 | 92.0425 | 91.9144 | -24.8749 | 91.9968 | 92.0837 | 0.16937 | -25.0076 | 92.0288 | 91.9327 | -24.9664 | 91.983 | 91.8961 | -0.036621 | -24.9664 | 92.1799 | 92.0471 | 92.0334 | -25.1404 | 92.0883 | 92.0883 | 92.0471 | -25.1221
1342.875 | 116.7892 | -91.7358 | 24.9481 | -0.0085447 | 0.016043 | 0.0020893 | 0.0063211 | 0.053579 | -0.0019995 | -0.0050415 | -0.0084684 | -0.0024268 | -0.032913 | 0.039007 | 0.0044667 | 0.0045652 | 0.022888 | 0 | 0.032043 | 0.07782 | 0.16022 | 0.022888 | -0.11444 | -0.045776 | 0.013733 | -0.11902 | 0.064087 | 0.082397 | 0.009155 | -0.082397 | 91.7587 | 91.6214 | -24.7879 | 91.7358 | 91.8137 | 0.19226 | -24.9252 | 91.745 | 91.6534 | -24.884 | 91.6901 | 91.6168 | -0.036622 | -24.8657 | 91.8961 | 91.7587 | 91.7679 | -25.0626 | 91.7999 | 91.8182 | 91.7496 | -25.0305
1344.625 | 116.5009 | -91.4886 | 24.852 | -0.016174 | 0.01348 | 0.0023029 | 0.0026895 | 0.054433 | -0.0024267 | -0.0039733 | -0.00083936 | -0.0037086 | -0.033554 | 0.040289 | 0.0053211 | 0.0060604 | 0.10986 | 0.12817 | 0.15106 | 0.14648 | 0.091553 | 0.054932 | -0.059509 | 0.082397 | 0.1236 | -0.004578 | 0.022888 | 0.022888 | 0.045776 | -0.045776 | 91.5436 | 91.4291 | -24.7604 | 91.6168 | 91.6351 | 0.20599 | -24.7421 | 91.5344 | 91.4429 | -24.8291 | 91.571 | 91.4841 | 0.041198 | -24.8291 | 91.5802 | 91.5985 | 91.6397 | -24.9115 | 91.5115 | 91.5115 | 91.6122 | -24.8978
1346.375 | 116.2949 | -91.2872 | 24.7513 | -0.0085447 | 0.017325 | 0.00080749 | 0.0065347 | 0.054647 | 0.0027003 | -0.0033325 | -0.00083936 | -0.001145 | -0.028854 | 0.041357 | 0.0057485 | 0.0039242 | 0.068665 | 0.036621 | 0.054932 | 0.11444 | 0.15564 | 0.022888 | -0.11902 | 0.036621 | 0.064087 | -0.07782 | 0.054932 | 0.036621 | 0.022888 | -0.073242 | 91.3101 | 91.1682 | -24.5956 | 91.3239 | 91.4017 | 0.23346 | -24.6826 | 91.3101 | 91.214 | -24.6963 | 91.3239 | 91.2094 | -0.004578 | -24.7147 | 91.4429 | 91.3559 | 91.3422 | -24.8703 | 91.3422 | 91.3239 | 91.3513 | -24.8245
1348.0625 | 116.0706 | -91.1179 | 24.7055 | -0.0085447 | 0.016043 | 0.0018757 | 0.0056803 | 0.054647 | -7.6908e-05 | -0.0024779 | 0.0067901 | -0.0002906 | -0.030777 | 0.039862 | 0.0061757 | 0.0049924 | 0.068665 | 0.032043 | 0.050354 | 0.086975 | 0.1236 | 0.045776 | -0.10529 | 0.018311 | 0.054932 | -0.09613 | 0.054932 | 0.064087 | 0.022888 | -0.064087 | 91.1636 | 91.0126 | -24.5819 | 91.1499 | 91.2048 | 0.19226 | -24.6368 | 91.1407 | 91.0538 | -24.6506 | 91.1362 | 91.0217 | -0.032043 | -24.6414 | 91.2415 | 91.1865 | 91.1682 | -24.8108 | 91.1728 | 91.1819 | 91.1728 | -24.7696
1349.7969 | 115.8875 | -91.0309 | 24.6506 | 0.014343 | 0.015189 | -0.00090151 | 0.0033305 | 0.053579 | 0.0033411 | -0.0014099 | -0.00083936 | 0.0007776 | -0.029068 | 0.041357 | 0.0055349 | 0.0058468 | 0.004578 | -0.022888 | 0.013733 | 0.082397 | 0.14191 | 0.009155 | -0.11902 | -0.041199 | 0 | -0.16022 | 0.082397 | 0.07782 | 0.013733 | -0.086975 | 91.04 | 90.9119 | -24.5087 | 91.008 | 91.1133 | 0.20142 | -24.646 | 91.0446 | 90.9439 | -24.5682 | 90.9897 | 90.8707 | -0.073242 | -24.5728 | 91.1728 | 91.0355 | 91.0446 | -24.7696 | 91.1133 | 91.1087 | 91.0309 | -24.7375
1351.5469 | 115.7959 | -90.8844 | 24.5865 | 0.0067138 | 0.013052 | 0.0012347 | 0.0031167 | 0.055074 | -0.00071771 | -0.0024779 | 0.0067901 | -0.0024268 | -0.03099 | 0.041998 | 0.0033985 | 0.0064878 | 0.009155 | -0.009155 | 0.041199 | 0.07782 | 0.15106 | 0.041199 | -0.09613 | 0.018311 | 0.054932 | -0.050354 | 0.032043 | 0.032043 | 0.032043 | -0.050354 | 90.9256 | 90.7883 | -24.4354 | 90.8752 | 90.9622 | 0.17395 | -24.5773 | 90.9164 | 90.834 | -24.5544 | 90.9027 | 90.834 | 0 | -24.5544 | 91.0355 | 90.8936 | 90.9256 | -24.6826 | 90.9164 | 90.9164 | 90.9393 | -24.6368
1353.2969 | 114.8621 | -29.4479 | 85.4691 | -0.0085447 | 0.013052 | 0.0025165 | 0.0061075 | 0.054647 | -0.0077673 | -0.0033325 | -0.0084684 | -0.0052038 | -0.031845 | 0.038794 | 0.00019427 | 0.0064878 | 0.009155 | 0.032043 | 0.07782 | 0.10071 | 0.068665 | 0.018311 | -0.10986 | -0.032043 | 0.091553 | -0.036621 | -0.013733 | -0.004578 | -0.009155 | -0.082397 | 29.4662 | 29.3381 | -85.4004 | 29.48 | 29.5486 | 0.21057 | -85.4599 | 29.4388 | 29.3655 | -85.4828 | 29.4159 | 29.4113 | 0.045776 | -85.4736 | 29.5166 | 29.4571 | 29.5258 | -85.5789 | 29.4342 | 29.4434 | 29.5395 | -85.5515
1355 | 119.0094 | -0.16937 | 118.9087 | 0.0067138 | 0.013907 | 0.00038029 | 0.0035441 | 0.053365 | 0.0020593 | -0.0031189 | -0.00083936 | 0.0007776 | -0.031417 | 0.039435 | 0.0063893 | 0.0043516 | -0.059509 | -0.10986 | -0.073242 | 0 | 0.068665 | -0.045776 | -0.17853 | -0.1236 | -0.10529 | -0.22888 | -0.009155 | -0.004578 | -0.050354 | -0.16479 | 0.1236 | -0.009155 | -118.84 | 0.05951 | 0.16937 | 0.17853 | -118.9682 | 0.11902 | 0.004578 | -118.9178 | 0.045777 | -0.059509 | -0.064087 | -118.9133 | 0.23804 | 0.10986 | 0.096131 | -119.0872 | 0.16022 | 0.16479 | 0.064087 | -119.0735
1356.75 | 115.7547 | -24.6185 | 91.301 | 0.0067138 | 0.015189 | 0.00038029 | 0.0084573 | 0.055074 | -0.0043493 | -0.0022643 | -0.00083936 | -0.0026404 | -0.029281 | 0.03858 | 0.0029713 | 0.0054196 | -0.022888 | -0.041199 | -0.004578 | 0.036621 | 0.086975 | -0.013733 | -0.15564 | -0.10986 | -0.009155 | -0.16022 | 0 | 0.004578 | -0.059509 | -0.1236 | 24.6048 | 24.4629 | -91.214 | 24.5773 | 24.6552 | 0.19226 | -91.3239 | 24.559 | 24.4949 | -91.301 | 24.5087 | 24.4583 | -0.036621 | -91.2964 | 24.7055 | 24.5956 | 24.614 | -91.4566 | 24.6185 | 24.6231 | 24.6094 | -91.4246
1358.5 | 119.101 | -0.15564 | 118.9362 | -0.0085447 | 0.017538 | 0.00059389 | 0.0041849 | 0.053365 | -7.6908e-05 | -0.0033325 | -0.00083936 | 0.0003504 | -0.030563 | 0.043494 | 0.0087391 | 0.0054196 | -0.022888 | -0.09613 | -0.064087 | 0 | 0.068665 | -0.045776 | -0.17395 | -0.09613 | -0.068665 | -0.20599 | -0.013733 | -0.009155 | -0.068665 | -0.14191 | 0.10986 | -0.01831 | -118.8675 | 0.05951 | 0.15564 | 0.17395 | -118.959 | 0.086975 | 0.013733 | -118.9499 | 0.05951 | -0.050354 | -0.064087 | -118.9453 | 0.22431 | 0.13275 | 0.091553 | -119.1101 | 0.14191 | 0.14649 | 0.086975 | -119.0781
1360.1875 | 119.2932 | -0.14191 | 119.0735 | 0.0067138 | 0.01348 | 0.00059389 | 0.0037577 | 0.050161 | -0.00093131 | -0.0016235 | 0.01442 | -0.0022132 | -0.030563 | 0.04093 | 0.0057485 | 0.0041378 | -0.082397 | -0.11444 | -0.086975 | 0 | 0.073242 | -0.059509 | -0.15564 | -0.10071 | -0.086975 | -0.19226 | -0.027466 | -0.013733 | -0.059509 | -0.14648 | 0.082398 | -0.013733 | -119.0002 | 0.027466 | 0.14191 | 0.15564 | -119.1559 | 0.082398 | -0.004577 | -119.101 | 0.041199 | -0.050354 | -0.045777 | -119.0872 | 0.21515 | 0.05951 | 0.054932 | -119.2291 | 0.11444 | 0.12817 | 0.054932 | -119.22
1361.9375 | 119.3024 | -0.20142 | 119.1925 | 0.0067138 | 0.010489 | 0.0040119 | 0.0078165 | 0.052938 | -0.0092627 | -0.0022643 | 0.0067901 | -0.0071264 | -0.030563 | 0.038794 | -0.0013011 | 0.006915 | -0.068665 | -0.036621 | 0.004578 | 0.032043 | 0.032043 | -0.027466 | -0.14648 | -0.09613 | 0 | -0.07782 | -0.050354 | -0.041199 | -0.045776 | -0.1236 | 0.17395 | 0.054932 | -119.1605 | 0.1648 | 0.23346 | 0.17853 | -119.2612 | 0.15564 | 0.07782 | -119.2429 | 0.10529 | 0.1236 | 0.045776 | -119.2337 | 0.23346 | 0.13275 | 0.20599 | -119.339 | 0.15106 | 0.16022 | 0.20142 | -119.3161
1363.6875 | 116.2582 | -26.7105 | 89.209 | -0.0085447 | 0.016043 | 0.0025165 | 0.0063211 | 0.054006 | 0.0022729 | -0.0037597 | -0.00083936 | 0.0020594 | -0.02864 | 0.039007 | 0.0061757 | 0.0045652 | -0.004578 | -0.027466 | -0.022888 | 0.041199 | 0.082397 | -0.013733 | -0.13733 | -0.073242 | -0.036621 | -0.17853 | 0 | 0.027466 | -0.045776 | -0.11444 | 26.6968 | 26.5732 | -89.1266 | 26.683 | 26.7517 | 0.17853 | -89.2136 | 26.6647 | 26.5961 | -89.209 | 26.6373 | 26.532 | -0.064087 | -89.1815 | 26.7929 | 26.7059 | 26.6876 | -89.3463 | 26.7105 | 26.738 | 26.6739 | -89.3234
1365.4219 | 119.3344 | -0.1831 | 119.2383 | 0.0067138 | 0.010916 | 0.0027301 | 0.0052531 | 0.054647 | -0.0064855 | -0.0041869 | 0.0067901 | -0.0054174 | -0.032699 | 0.039648 | 0.0021169 | 0.006915 | -0.041199 | -0.013733 | 0.018311 | 0.054932 | 0.027466 | -0.018311 | -0.15564 | -0.054932 | 0.032043 | -0.068665 | -0.059509 | -0.054932 | -0.054932 | -0.1236 | 0.16479 | 0.027465 | -119.2108 | 0.16937 | 0.23804 | 0.21057 | -119.2795 | 0.12817 | 0.059509 | -119.2978 | 0.12817 | 0.11444 | 0.054931 | -119.2932 | 0.21057 | 0.14191 | 0.20142 | -119.3939 | 0.1236 | 0.12817 | 0.21515 | -119.3619
1367.1094 | 119.4168 | -0.19226 | 119.3024 | -0.0085447 | 0.0092072 | 0.0044391 | 0.0052531 | 0.053579 | -0.0066993 | -0.0048279 | -0.0084684 | -0.0032812 | -0.03099 | 0.037298 | 0.0023305 | 0.0054196 | -0.022888 | -0.032043 | 0.027466 | 0.041199 | 0.036621 | -0.032043 | -0.16479 | -0.050354 | 0.041199 | -0.07782 | -0.054932 | -0.054932 | -0.041199 | -0.13733 | 0.16022 | 0.027466 | -119.2657 | 0.16022 | 0.23346 | 0.20599 | -119.3253 | 0.15106 | 0.054932 | -119.3573 | 0.14191 | 0.11444 | 0.059509 | -119.3573 | 0.22888 | 0.16937 | 0.21973 | -119.4672 | 0.13733 | 0.13733 | 0.23346 | -119.4397
1368.8594 | 119.4946 | -0.17853 | 119.3665 | -0.0085447 | 0.010916 | 0.0023029 | 0.0061075 | 0.056142 | -0.0039221 | -0.0063233 | -0.0084684 | -0.0049902 | -0.030136 | 0.037939 | 0.0025441 | 0.005206 | 0 | 0.018311 | 0.045776 | 0.07782 | 0.036621 | -0.050354 | -0.13275 | -0.027466 | 0.064087 | -0.054932 | -0.036621 | -0.054932 | -0.036621 | -0.10986 | 0.12817 | 0.045777 | -119.3298 | 0.19684 | 0.25635 | 0.21057 | -119.3665 | 0.14191 | 0.068665 | -119.4031 | 0.15106 | 0.1236 | 0.054931 | -119.4214 | 0.21515 | 0.17853 | 0.2243 | -119.4992 | 0.14191 | 0.1236 | 0.24261 | -119.4763
1370.625 | 119.6091 | -0.16937 | 119.4214 | -0.016174 | 0.013693 | 0.0025165 | 0.0052531 | 0.056142 | 0.0018457 | -0.0035461 | -0.00083936 | -7.6996e-05 | -0.030349 | 0.039221 | 0.0055349 | 0.0015744 | -0.064087 | -0.09613 | -0.07782 | -0.004578 | 0.068665 | -0.064087 | -0.1831 | -0.11902 | -0.064087 | -0.21057 | -0.013733 | -0.018311 | -0.068665 | -0.16937 | 0.10529 | -0.013732 | -119.3527 | 0.073243 | 0.16479 | 0.17853 | -119.4855 | 0.10071 | 0 | -119.4351 | 0.050354 | -0.041198 | -0.041198 | -119.4397 | 0.23804 | 0.10529 | 0.091553 | -119.6045 | 0.15564 | 0.15106 | 0.10529 | -119.5908
1372.3281 | 119.6869 | -0.17853 | 119.4305 | -0.0085447 | 0.015402 | 0.0014483 | 0.0048257 | 0.054647 | 0.00077749 | -0.0041869 | -0.0084684 | 0.000564 | -0.030136 | 0.040716 | 0.0040395 | 0.0032834 | -0.027466 | -0.045776 | -0.036621 | 0.036621 | 0.07782 | -0.050354 | -0.19226 | -0.050354 | -0.009155 | -0.16479 | -0.027466 | -0.009155 | -0.064087 | -0.14191 | 0.12817 | -0.013733 | -119.3527 | 0.13275 | 0.21515 | 0.22888 | -119.458 | 0.11444 | 0.036621 | -119.458 | 0.12817 | 0.013733 | -0.022888 | -119.4397 | 0.25635 | 0.15106 | 0.14191 | -119.6228 | 0.15106 | 0.16937 | 0.16937 | -119.5724
1374.0156 | 119.7327 | -0.13733 | 119.4717 | -0.00091566 | 0.016684 | -4.6912e-05 | 0.0054667 | 0.052724 | 0.0022729 | -0.0022643 | -0.00083936 | 0.0007776 | -0.031417 | 0.039435 | 0.0070301 | 0.0030698 | -0.032043 | -0.036621 | -0.013733 | 0.022888 | 0.059509 | -0.027466 | -0.17853 | -0.054932 | 0 | -0.16479 | -0.036621 | -0.032043 | -0.050354 | -0.15106 | 0.10986 | -0.041199 | -119.4122 | 0.10071 | 0.16022 | 0.20142 | -119.5038 | 0.086975 | -0.013733 | -119.5084 | 0.082397 | -0.027466 | -0.013733 | -119.5038 | 0.19684 | 0.10529 | 0.1236 | -119.6503 | 0.10071 | 0.10529 | 0.13733 | -119.6228
1375.7656 | 119.7784 | -0.17853 | 119.5358 | 0.014343 | 0.012412 | 0.0029437 | 0.0046121 | 0.052511 | -0.0028539 | -0.0020507 | 0.01442 | -0.0017858 | -0.032272 | 0.037726 | 0.0042531 | 0.0075558 | 0.009155 | 0.027466 | 0.050354 | 0.07782 | 0.027466 | -0.027466 | -0.14191 | -0.004578 | 0.054932 | -0.073242 | -0.068665 | -0.064087 | -0.009155 | -0.10529 | 0.15106 | 0.036621 | -119.5084 | 0.20599 | 0.25635 | 0.21973 | -119.5267 | 0.16937 | 0.073242 | -119.6045 | 0.17395 | 0.10529 | 0.032044 | -119.5999 | 0.20599 | 0.18768 | 0.22888 | -119.6777 | 0.10986 | 0.11444 | 0.23346 | -119.6411
1377.5312 | 119.6869 | -0.21515 | 119.5953 | -0.0085447 | 0.0085664 | 0.0035847 | 0.0043985 | 0.055288 | -0.0064855 | -0.0031189 | 0.0067901 | -0.004563 | -0.033554 | 0.037085 | 0.0036123 | 0.0071286 | -0.009155 | 0.009155 | 0.041199 | 0.027466 | 0.022888 | -0.009155 | -0.13733 | -0.064087 | 0.009155 | -0.11444 | -0.064087 | -0.045776 | -0.041199 | -0.1236 | 0.20599 | 0.07782 | -119.5724 | 0.2243 | 0.24261 | 0.16479 | -119.6045 | 0.17395 | 0.091553 | -119.6594 | 0.15106 | 0.10071 | 0.009155 | -119.6411 | 0.23804 | 0.20599 | 0.25635 | -119.7327 | 0.15106 | 0.16937 | 0.2243 | -119.7189
1379.2188 | 119.8746 | -0.17853 | 119.632 | -0.016174 | 0.014334 | 0.0010211 | 0.0046121 | 0.052511 | -0.0015723 | -0.0041869 | -0.016098 | -0.001145 | -0.031417 | 0.040289 | 0.0051075 | 0.0056332 | 0 | -0.050354 | 0 | 0.027466 | 0.064087 | -0.041199 | -0.16022 | -0.022888 | 0.009155 | -0.091553 | -0.045776 | -0.036621 | -0.013733 | -0.1236 | 0.13733 | 0.018311 | -119.5679 | 0.12817 | 0.20599 | 0.18768 | -119.632 | 0.16479 | 0.054932 | -119.6777 | 0.15564 | 0.086975 | 0.032043 | -119.6686 | 0.24261 | 0.17853 | 0.17853 | -119.7922 | 0.13275 | 0.14191 | 0.18768 | -119.7556
1380.9688 | 119.8791 | -0.1831 | 119.6777 | 0.0067138 | 0.020529 | 0.00080749 | 0.0063211 | 0.054647 | 0.0031275 | -0.0037597 | -0.00083936 | -0.0009314 | -0.029708 | 0.039648 | 0.0044667 | 0.0037106 | -0.068665 | -0.15564 | -0.07782 | -0.009155 | 0.068665 | -0.050354 | -0.16479 | -0.11444 | -0.09613 | -0.21515 | -0.022888 | -0.018311 | -0.059509 | -0.16937 | 0.13275 | 0.01831 | -119.6091 | 0.027465 | 0.17395 | 0.15564 | -119.7464 | 0.1236 | 0.013732 | -119.7006 | 0.068664 | -0.032044 | -0.045776 | -119.696 | 0.25177 | 0.11444 | 0.10528 | -119.8425 | 0.16022 | 0.16479 | 0.086975 | -119.8471
1382.7344 | 119.8746 | -0.17395 | 119.7189 | -0.00091566 | 0.014548 | 0.0050799 | 0.0063211 | 0.053579 | -0.0077673 | -0.0039733 | -0.0084684 | -0.004563 | -0.029708 | 0.039862 | 0.0010487 | 0.0047788 | 0.022888 | 0.054932 | 0.059509 | 0.07782 | 0.022888 | -0.032043 | -0.15106 | -0.022888 | 0.086975 | -0.032043 | -0.073242 | -0.059509 | -0.027466 | -0.11902 | 0.14191 | 0.022888 | -119.696 | 0.22888 | 0.25177 | 0.22888 | -119.696 | 0.14648 | 0.054931 | -119.7922 | 0.15106 | 0.14191 | 0.086976 | -119.7784 | 0.19684 | 0.19684 | 0.23346 | -119.87 | 0.10071 | 0.11444 | 0.26092 | -119.838
1384.4219 | 119.8608 | -0.2243 | 119.7601 | -0.00091566 | 0.0096344 | 0.0035847 | 0.0046121 | 0.053792 | -0.0058447 | -0.0044007 | -0.00083936 | -0.0043494 | -0.031204 | 0.037939 | 0.0038259 | 0.0067014 | -0.009155 | -0.013733 | 0.018311 | 0.036621 | 0.022888 | -0.018311 | -0.14648 | -0.082397 | -0.009155 | -0.11902 | -0.054932 | -0.059509 | -0.032043 | -0.13733 | 0.20599 | 0.07782 | -119.7372 | 0.21057 | 0.26093 | 0.18311 | -119.7693 | 0.19226 | 0.086975 | -119.8151 | 0.14191 | 0.10529 | 0.01831 | -119.8196 | 0.24719 | 0.21515 | 0.24261 | -119.9066 | 0.16937 | 0.16479 | 0.21515 | -119.8975
1386.125 | 119.9936 | -0.18768 | 119.783 | -0.0085447 | 0.016043 | 0.0023029 | 0.0061075 | 0.055288 | 0.00013669 | -0.0033325 | -0.0084684 | 0.0009912 | -0.030136 | 0.041998 | 0.0031849 | 0.0028562 | -0.073242 | -0.10529 | -0.064087 | -0.004578 | 0.073242 | -0.064087 | -0.20599 | -0.11902 | -0.054932 | -0.20142 | -0.013733 | -0.022888 | -0.064087 | -0.16022 | 0.1236 | -0.018311 | -119.7098 | 0.082397 | 0.1831 | 0.20142 | -119.8563 | 0.1236 | 0.027466 | -119.7968 | 0.068664 | -0.013733 | -0.041199 | -119.8059 | 0.26092 | 0.11444 | 0.1236 | -119.989 | 0.17395 | 0.16479 | 0.13275 | -119.9432
1387.875 | 119.9249 | -0.2243 | 119.8608 | -0.0085447 | 0.01113 | 0.0025165 | 0.0039713 | 0.053792 | -0.0054175 | -0.0048279 | -0.00083936 | -0.0052038 | -0.031204 | 0.039221 | 0.0031849 | 0.0064878 | -0.018311 | 0.004578 | 0.022888 | 0.041199 | 0.036621 | -0.013733 | -0.14648 | -0.082397 | -0.004578 | -0.11902 | -0.041199 | -0.036621 | -0.036621 | -0.11444 | 0.21057 | 0.07782 | -119.8242 | 0.22888 | 0.2655 | 0.18768 | -119.8792 | 0.18768 | 0.10986 | -119.902 | 0.14191 | 0.10529 | -0.004578 | -119.8975 | 0.26093 | 0.20599 | 0.24719 | -120.0073 | 0.18311 | 0.18768 | 0.21973 | -119.9753
1389.625 | 120.0806 | -0.19226 | 119.8563 | -0.0085447 | 0.009848 | 0.0037983 | 0.0031167 | 0.052938 | -0.0026403 | -0.0048279 | -0.0084684 | -0.0034948 | -0.032272 | 0.037939 | 0.0061757 | 0.0049924 | 0.022888 | 0.018311 | 0.054932 | 0.086975 | 0.027466 | 0 | -0.13733 | 0.004578 | 0.041199 | -0.086975 | -0.054932 | -0.054932 | -0.027466 | -0.1236 | 0.19226 | 0.054932 | -119.8288 | 0.21057 | 0.27924 | 0.2243 | -119.8334 | 0.16479 | 0.068665 | -119.9112 | 0.19684 | 0.10529 | 0.036621 | -119.9112 | 0.21973 | 0.21515 | 0.24719 | -119.9936 | 0.13733 | 0.13733 | 0.23346 | -119.9799
1391.3125 | 120.0577 | -0.20142 | 119.9203 | 0.0067138 | 0.011557 | 0.0020893 | 0.0071757 | 0.05187 | -0.0056311 | -0.0058959 | -0.00083936 | -0.0064856 | -0.031204 | 0.03858 | 0.0016895 | 0.005206 | 0 | 0.022888 | 0.059509 | 0.068665 | 0.045776 | -0.018311 | -0.14191 | -0.027466 | 0.064087 | -0.045776 | -0.050354 | -0.064087 | -0.027466 | -0.1236 | 0.18311 | 0.059509 | -119.8746 | 0.2243 | 0.27008 | 0.21057 | -119.9203 | 0.17395 | 0.07782 | -119.9707 | 0.17395 | 0.15564 | 0.07782 | -119.9844 | 0.24719 | 0.20142 | 0.26093 | -120.0623 | 0.15106 | 0.13733 | 0.2655 | -120.0439
1393 | 120.0439 | -0.23804 | 119.9478 | -0.0085447 | 0.013052 | 0.0035847 | 0.0069621 | 0.054006 | -0.0022131 | -0.0035461 | 0.0067901 | -0.0030676 | -0.030349 | 0.042212 | 0.0021169 | 0.0041378 | 0.013733 | 0.027466 | 0.073242 | 0.050354 | 0.013733 | -0.013733 | -0.15106 | -0.022888 | 0.013733 | -0.10529 | -0.068665 | -0.054932 | -0.022888 | -0.11902 | 0.2243 | 0.086975 | -119.9341 | 0.2655 | 0.28839 | 0.20142 | -119.9341 | 0.21515 | 0.11902 | -120.0165 | 0.21515 | 0.13275 | 0.013733 | -120.0027 | 0.25177 | 0.25177 | 0.31128 | -120.0989 | 0.16937 | 0.1831 | 0.25177 | -120.0668
1394.75 | 120.1355 | -0.19684 | 119.9615 | -0.016174 | 0.017752 | 0.0020893 | 0.0076029 | 0.053365 | 0.0018457 | -0.0037597 | -0.0084684 | 0.0007776 | -0.029495 | 0.041998 | 0.0053211 | 0.0026426 | -0.082397 | -0.086975 | -0.064087 | -0.004578 | 0.068665 | -0.073242 | -0.18768 | -0.10986 | -0.073242 | -0.20599 | -0.009155 | -0.009155 | -0.054932 | -0.17395 | 0.1236 | 0.009155 | -119.8929 | 0.10986 | 0.19226 | 0.1831 | -120.0439 | 0.14191 | 0.022888 | -119.9707 | 0.086975 | -0.009156 | -0.032044 | -119.9707 | 0.2655 | 0.11444 | 0.13275 | -120.1492 | 0.18768 | 0.18768 | 0.1236 | -120.1355
1396.5 | 120.2316 | -0.18768 | 119.9707 | -0.00091566 | 0.013907 | -0.00068791 | 0.0041849 | 0.052724 | 0.00099129 | -0.0031189 | -0.016098 | -0.002854 | -0.031204 | 0.04093 | 0.0072437 | 0.0045652 | -0.036621 | -0.064087 | -0.013733 | 0.022888 | 0.068665 | -0.041199 | -0.17395 | -0.022888 | 0.009155 | -0.1236 | -0.032043 | -0.059509 | -0.036621 | -0.12817 | 0.14648 | 0.013733 | -119.902 | 0.1236 | 0.21057 | 0.19684 | -120.0073 | 0.15106 | 0.059509 | -120.0027 | 0.16479 | 0.064087 | 0.004578 | -120.0302 | 0.25635 | 0.15106 | 0.17395 | -120.1447 | 0.15564 | 0.12817 | 0.19684 | -120.0989
1398.2031 | 120.2179 | -0.19226 | 120.0302 | 0.0067138 | 0.014975 | 0.0033709 | 0.0029031 | 0.055288 | 0.00056389 | -0.00012812 | -0.016098 | 0.0020594 | -0.031204 | 0.039435 | 0.0083119 | 0.0060604 | -0.07782 | -0.1236 | -0.086975 | -0.022888 | 0.059509 | -0.054932 | -0.17853 | -0.11444 | -0.10071 | -0.23804 | -0.018311 | -0.013733 | -0.064087 | -0.15106 | 0.13733 | 0.013733 | -119.9707 | 0.068665 | 0.16937 | 0.15564 | -120.108 | 0.12817 | 0.041199 | -120.0485 | 0.07782 | -0.045776 | -0.086975 | -120.0439 | 0.25177 | 0.11444 | 0.10529 | -120.2087 | 0.17395 | 0.17853 | 0.091553 | -120.1813
1399.9531 | 120.1447 | -0.21515 | 120.0577 | -0.00091566 | 0.014548 | 0.0048663 | 0.0080301 | 0.056997 | -0.0054175 | -0.0046143 | -0.016098 | -0.004563 | -0.030777 | 0.039007 | 0.0036123 | 0.0045652 | 0.004578 | 0.064087 | 0.068665 | 0.073242 | 0.036621 | -0.022888 | -0.15564 | -0.009155 | 0.07782 | -0.082397 | -0.059509 | -0.050354 | -0.036621 | -0.1236 | 0.19226 | 0.059509 | -120.0211 | 0.27924 | 0.28839 | 0.22888 | -120.0531 | 0.17853 | 0.091553 | -120.1172 | 0.20599 | 0.13275 | 0.041199 | -120.108 | 0.25177 | 0.21973 | 0.28381 | -120.2133 | 0.15564 | 0.16479 | 0.29297 | -120.1813
1401.6562 | 120.1904 | -0.21515 | 120.1035 | -0.0085447 | 0.016043 | 0.0050799 | 0.0082437 | 0.053792 | -0.0056311 | -0.0041869 | -0.00083936 | -0.0039222 | -0.032058 | 0.037939 | 0.0012623 | 0.0043516 | 0.027466 | 0.059509 | 0.07782 | 0.059509 | 0.045776 | -0.032043 | -0.14191 | -0.004578 | 0.09613 | -0.068665 | -0.068665 | -0.045776 | -0.032043 | -0.10529 | 0.18311 | 0.073242 | -120.0577 | 0.27466 | 0.27466 | 0.20142 | -120.076 | 0.18311 | 0.10986 | -120.1721 | 0.21057 | 0.14648 | 0.036621 | -120.1492 | 0.26093 | 0.24261 | 0.29297 | -120.2454 | 0.14648 | 0.16937 | 0.31128 | -120.2087
1403.4062 | 120.3598 | -0.15564 | 120.1035 | -0.00091566 | 0.015402 | 0.0018757 | 0.0024759 | 0.054433 | 0.00056389 | -0.0039733 | -0.0084684 | 0.0020594 | -0.029708 | 0.039007 | 0.0070301 | 0.0037106 | -0.036621 | -0.032043 | -0.032043 | 0.036621 | 0.064087 | -0.054932 | -0.20142 | -0.054932 | 0.004578 | -0.15564 | -0.022888 | -0.036621 | -0.068665 | -0.15106 | 0.10071 | -0.045776 | -120.0394 | 0.1236 | 0.19226 | 0.23804 | -120.1401 | 0.086975 | 0.004578 | -120.1263 | 0.10071 | 0 | -0.004578 | -120.1401 | 0.21973 | 0.11902 | 0.1236 | -120.3049 | 0.13275 | 0.11902 | 0.16022 | -120.2545
1405.1094 | 120.3873 | -0.16022 | 120.1263 | -0.00091566 | 0.013266 | 0.0020893 | 0.0024759 | 0.054006 | -7.6908e-05 | -0.0011963 | -0.00083936 | -0.0009314 | -0.030563 | 0.040716 | 0.0036123 | 0.0032834 | -0.059509 | -0.073242 | -0.045776 | 0.013733 | 0.064087 | -0.045776 | -0.20142 | -0.050354 | -0.027466 | -0.16022 | -0.018311 | -0.022888 | -0.07782 | -0.15564 | 0.11444 | -0.041199 | -120.0623 | 0.086975 | 0.17395 | 0.21515 | -120.1859 | 0.082397 | 0.004577 | -120.1447 | 0.10986 | 0 | -0.004577 | -120.1492 | 0.2243 | 0.10071 | 0.11444 | -120.3278 | 0.14191 | 0.13733 | 0.13275 | -120.282
1406.875 | 120.3049 | -0.2243 | 120.1996 | 0.014343 | 0.0089936 | 0.0057209 | 0.0035441 | 0.052511 | -0.0064855 | -0.0031189 | 0.0067901 | -0.0039222 | -0.030777 | 0.039007 | 0.0029713 | 0.0071286 | -0.036621 | -0.022888 | 0 | 0.027466 | 0.032043 | -0.027466 | -0.14191 | -0.10071 | -0.009155 | -0.12817 | -0.050354 | -0.036621 | -0.036621 | -0.13275 | 0.19684 | 0.082397 | -120.1675 | 0.20142 | 0.25177 | 0.16937 | -120.2362 | 0.18768 | 0.091553 | -120.2499 | 0.1236 | 0.09613 | 0.004577 | -120.2362 | 0.25635 | 0.18768 | 0.2243 | -120.3415 | 0.17395 | 0.18768 | 0.21515 | -120.3323
1408.625 | 120.314 | -0.23346 | 120.2225 | 0.0067138 | 0.0083526 | 0.0042255 | 0.0046121 | 0.053792 | -0.0056311 | -0.0048279 | -0.0084684 | -0.0043494 | -0.033554 | 0.040076 | 0.0055349 | 0.0047788 | -0.036621 | -0.009155 | 0.009155 | 0.013733 | 0.045776 | -0.018311 | -0.14648 | -0.068665 | 0 | -0.10986 | -0.064087 | -0.050354 | -0.027466 | -0.12817 | 0.21515 | 0.086975 | -120.1767 | 0.2243 | 0.24719 | 0.16022 | -120.2591 | 0.20599 | 0.10528 | -120.2866 | 0.16479 | 0.1236 | 0.018311 | -120.2728 | 0.27924 | 0.19684 | 0.24261 | -120.369 | 0.16937 | 0.1831 | 0.23346 | -120.3506
1410.3125 | 120.3781 | -0.21057 | 120.2545 | -0.00091566 | 0.010916 | 0.0048663 | 0.0031167 | 0.050161 | -0.0043493 | -0.0041869 | -0.0084684 | -0.0056312 | -0.031845 | 0.039221 | 0.0016895 | 0.0047788 | -0.036621 | -0.032043 | -0.004578 | 0.041199 | 0.027466 | -0.032043 | -0.15106 | -0.068665 | 0.009155 | -0.11902 | -0.027466 | -0.054932 | -0.050354 | -0.12817 | 0.17853 | 0.059509 | -120.2271 | 0.17853 | 0.25177 | 0.19226 | -120.2911 | 0.16022 | 0.082397 | -120.282 | 0.14191 | 0.091552 | 0.009155 | -120.3094 | 0.23804 | 0.17395 | 0.20599 | -120.4056 | 0.18311 | 0.15564 | 0.21973 | -120.3827
1412 | 120.3644 | -0.21515 | 120.2957 | -0.0085447 | 0.014761 | 0.0048663 | 0.0076029 | 0.054006 | -0.0022131 | -0.0050415 | -0.00083936 | -0.0047766 | -0.032272 | 0.037726 | 0.0036123 | 0.0028562 | 0 | -0.004578 | 0.004578 | 0.041199 | 0.045776 | -0.050354 | -0.17853 | -0.09613 | -0.018311 | -0.16937 | -0.022888 | -0.032043 | -0.059509 | -0.14648 | 0.16479 | 0.036621 | -120.2499 | 0.21057 | 0.25635 | 0.21973 | -120.2957 | 0.15564 | 0.068665 | -120.3186 | 0.11902 | 0.045776 | -0.022889 | -120.3278 | 0.26093 | 0.21515 | 0.21973 | -120.4742 | 0.19226 | 0.18311 | 0.19684 | -120.4422
1413.75 | 120.5109 | -0.16479 | 120.2545 | -0.00091566 | 0.012839 | -4.6912e-05 | 0.0022623 | 0.053579 | 0.0031275 | -0.0037597 | -0.0084684 | -0.0022132 | -0.03099 | 0.040503 | 0.0072437 | 0.0032834 | -0.032043 | -0.050354 | -0.013733 | 0.013733 | 0.054932 | -0.036621 | -0.15564 | -0.022888 | -0.009155 | -0.1236 | -0.059509 | -0.050354 | -0.027466 | -0.11902 | 0.12817 | 0.009155 | -120.1996 | 0.11444 | 0.17853 | 0.16937 | -120.2866 | 0.13733 | 0.045776 | -120.314 | 0.14191 | 0.041199 | -0.004577 | -120.3049 | 0.21973 | 0.13275 | 0.15106 | -120.4102 | 0.10529 | 0.11444 | 0.15564 | -120.3735
1415.5156 | 120.5429 | -0.19226 | 120.2728 | -0.00091566 | 0.012625 | 0.0025165 | 0.0043985 | 0.05486 | -0.00050411 | -0.0033325 | -0.00083936 | -0.0013586 | -0.03099 | 0.040289 | 0.0046803 | 0.0043516 | -0.068665 | -0.10986 | -0.07782 | -0.013733 | 0.064087 | -0.059509 | -0.17853 | -0.10529 | -0.091553 | -0.21515 | -0.022888 | -0.027466 | -0.059509 | -0.15106 | 0.13275 | 0.013733 | -120.2087 | 0.082398 | 0.17853 | 0.16479 | -120.3415 | 0.13275 | 0.041199 | -120.2957 | 0.086975 | -0.022888 | -0.064087 | -120.3003 | 0.25635 | 0.1236 | 0.11444 | -120.4514 | 0.16937 | 0.16479 | 0.10071 | -120.4239
1417.2812 | 120.433 | -0.21057 | 120.3506 | -0.00091566 | 0.014121 | 0.0031573 | 0.0088847 | 0.055288 | -0.0030677 | -0.0061095 | 0.0067901 | -0.0013586 | -0.02864 | 0.039862 | 0.00019427 | 0.0058468 | -0.07782 | -0.050354 | -0.036621 | 0.009155 | 0.07782 | -0.041199 | -0.17853 | -0.1236 | -0.041199 | -0.1831 | -0.009155 | -0.013733 | -0.068665 | -0.16022 | 0.16937 | 0.032043 | -120.2728 | 0.16022 | 0.21973 | 0.18768 | -120.4285 | 0.14191 | 0.050354 | -120.3598 | 0.086975 | 0.027466 | -0.022888 | -120.3644 | 0.28839 | 0.13275 | 0.17395 | -120.5292 | 0.20142 | 0.19684 | 0.16937 | -120.5109
1418.9688 | 120.4605 | -0.21057 | 120.3644 | -0.00091566 | 0.016898 | 0.0037983 | 0.0063211 | 0.053365 | -0.0028539 | -0.0046143 | -0.0084684 | -0.001145 | -0.03099 | 0.040289 | 0.0025441 | 0.0030698 | -0.054932 | -0.036621 | -0.032043 | 0.018311 | 0.059509 | -0.050354 | -0.17853 | -0.1236 | -0.032043 | -0.17395 | -0.018311 | -0.018311 | -0.050354 | -0.15106 | 0.16022 | 0.032043 | -120.3049 | 0.17395 | 0.22888 | 0.19684 | -120.4193 | 0.16022 | 0.059509 | -120.3827 | 0.086975 | 0.036621 | -0.022888 | -120.3827 | 0.27008 | 0.15564 | 0.17853 | -120.5429 | 0.19226 | 0.19226 | 0.17853 | -120.5154
1420.7031 | 120.5704 | -0.19684 | 120.3506 | -0.00091566 | 0.014334 | 0.0023029 | 0.0020487 | 0.053579 | -7.6908e-05 | -0.0031189 | 0.0067901 | 0.002273 | -0.030563 | 0.039862 | 0.010021 | 0.0047788 | -0.082397 | -0.13733 | -0.091553 | -0.009155 | 0.07782 | -0.059509 | -0.20142 | -0.11902 | -0.10986 | -0.22888 | -0.022888 | 0.004578 | -0.041199 | -0.14648 | 0.13733 | -0.004578 | -120.2728 | 0.059509 | 0.18768 | 0.19226 | -120.433 | 0.15564 | 0.050354 | -120.3735 | 0.077819 | -0.032044 | -0.082398 | -120.3461 | 0.27466 | 0.11444 | 0.10529 | -120.5521 | 0.17395 | 0.20142 | 0.086975 | -120.4971
1422.4531 | 120.5063 | -0.21515 | 120.4147 | -0.00091566 | 0.014121 | 0.0027301 | 0.0095255 | 0.054433 | -0.0047765 | -0.0022643 | -0.00083936 | -0.002854 | -0.02864 | 0.039435 | 0.0019033 | 0.0064878 | -0.036621 | -0.009155 | 0.009155 | 0.036621 | 0.045776 | -0.045776 | -0.16022 | -0.10986 | -0.022888 | -0.16479 | -0.013733 | -0.022888 | -0.045776 | -0.15106 | 0.16937 | 0.054932 | -120.369 | 0.20599 | 0.25177 | 0.19684 | -120.4514 | 0.16937 | 0.064087 | -120.4285 | 0.10529 | 0.050354 | -0.013733 | -120.4376 | 0.26093 | 0.17853 | 0.2243 | -120.575 | 0.20142 | 0.19226 | 0.19226 | -120.5658
1424.1406 | 120.5017 | -0.21515 | 120.3278 | -0.0085447 | 0.015402 | 0.0020893 | 0.0048257 | 0.052724 | -0.0064855 | -0.0046143 | -0.00083936 | -0.0054174 | -0.032699 | 0.037939 | 0.0014759 | 0.0058468 | -0.059509 | -0.027466 | 0.004578 | 0.027466 | 0.041199 | -0.041199 | -0.13275 | -0.068665 | 0 | -0.09613 | -0.064087 | -0.068665 | -0.041199 | -0.13275 | 0.17395 | 0.082398 | -120.2866 | 0.18768 | 0.24261 | 0.16022 | -120.3873 | 0.17395 | 0.082398 | -120.3918 | 0.14648 | 0.11902 | 0.036621 | -120.3964 | 0.25635 | 0.15564 | 0.21973 | -120.4605 | 0.15106 | 0.14648 | 0.21515 | -120.4605
1425.8906 | 120.6573 | -0.16022 | 120.3964 | -0.00091566 | 0.018179 | 0.0033709 | 0.0058939 | 0.05486 | 0.0018457 | -0.0018371 | -0.00083936 | 0.0009912 | -0.031204 | 0.040716 | 0.0068165 | 0.0026426 | -0.050354 | -0.07782 | -0.082397 | 0.013733 | 0.054932 | -0.059509 | -0.19226 | -0.068665 | -0.022888 | -0.16937 | -0.032043 | -0.032043 | -0.059509 | -0.15106 | 0.10071 | -0.032044 | -120.3415 | 0.082397 | 0.17395 | 0.20599 | -120.4468 | 0.10071 | 0.009155 | -120.4285 | 0.091552 | -0.009156 | -0.018311 | -120.4285 | 0.21515 | 0.10986 | 0.07782 | -120.5887 | 0.12817 | 0.12817 | 0.13733 | -120.5475
1427.5781 | 120.5383 | -0.21973 | 120.4285 | 0.0067138 | 0.015402 | 0.0027301 | 0.0067483 | 0.053365 | -0.0043493 | -0.0037597 | 0.0067901 | -0.0034948 | -0.030349 | 0.039007 | 0.0023305 | 0.0043516 | 0.004578 | 0.013733 | 0.022888 | 0.064087 | 0.032043 | -0.054932 | -0.16937 | -0.073242 | 0.041199 | -0.11902 | -0.036621 | -0.050354 | -0.050354 | -0.15564 | 0.16479 | 0.050354 | -120.3964 | 0.23346 | 0.28381 | 0.23346 | -120.4239 | 0.16937 | 0.064087 | -120.4651 | 0.14649 | 0.10071 | 0.036621 | -120.4788 | 0.25177 | 0.22431 | 0.24261 | -120.5978 | 0.18311 | 0.16937 | 0.26093 | -120.5841
1429.2812 | 120.4376 | -0.23346 | 120.4193 | -0.00091566 | 0.013693 | 0.0018757 | 0.0050393 | 0.057424 | -0.0058447 | -0.0033325 | -0.0084684 | -0.004563 | -0.03099 | 0.04093 | 0.0016895 | 0.0049924 | 0.009155 | 0.032043 | 0.068665 | 0.082397 | 0.022888 | -0.032043 | -0.15106 | -0.054932 | 0.059509 | -0.10986 | -0.054932 | -0.045776 | -0.050354 | -0.14648 | 0.20142 | 0.082397 | -120.3964 | 0.2655 | 0.31586 | 0.23346 | -120.4102 | 0.1831 | 0.086975 | -120.4742 | 0.17853 | 0.1236 | 0.036621 | -120.4651 | 0.25635 | 0.24261 | 0.30212 | -120.5704 | 0.17853 | 0.18768 | 0.29297 | -120.5658
1431.0312 | 120.7077 | -0.17395 | 120.4605 | -0.016174 | 0.012625 | 0.0023029 | 0.0020487 | 0.052297 | 0.00056389 | -0.0026917 | -0.00083936 | -0.0002906 | -0.031631 | 0.041571 | 0.0070301 | 0.0056332 | -0.036621 | -0.091553 | -0.054932 | 0.004578 | 0.068665 | -0.045776 | -0.16022 | -0.059509 | -0.036621 | -0.13733 | -0.054932 | -0.032043 | -0.045776 | -0.11902 | 0.12817 | 0.013733 | -120.3918 | 0.082397 | 0.17853 | 0.16479 | -120.4971 | 0.12817 | 0.054931 | -120.5154 | 0.11444 | 0.036621 | -0.01831 | -120.4926 | 0.24261 | 0.13733 | 0.11902 | -120.6207 | 0.11902 | 0.14191 | 0.13733 | -120.5795
1432.7188 | 120.5063 | -0.16022 | 120.282 | 0.0067138 | 0.013907 | 0.0029437 | 0.0043985 | 0.055715 | 0.0016321 | -0.0035461 | -0.00083936 | -0.0007178 | -0.029068 | 0.041785 | 0.0063893 | 0.0043516 | 0 | -0.032043 | -0.004578 | 0.032043 | 0.059509 | -0.050354 | -0.1831 | -0.032043 | 0 | -0.15564 | -0.036621 | -0.032043 | -0.045776 | -0.1236 | 0.10986 | -0.022888 | -120.2225 | 0.12817 | 0.19226 | 0.21515 | -120.282 | 0.11444 | 0.036621 | -120.3186 | 0.12817 | 0.004577 | -0.032044 | -120.314 | 0.21973 | 0.16022 | 0.15564 | -120.4651 | 0.1236 | 0.12817 | 0.16022 | -120.4056
1434.4688 | 120.6116 | -0.19226 | 120.5292 | -0.00091566 | 0.014334 | 0.0018757 | 0.0078165 | 0.055288 | -0.0037085 | -0.0029053 | -0.016098 | -0.0013586 | -0.028 | 0.04328 | 0.0016895 | 0.0049924 | -0.082397 | -0.086975 | -0.068665 | -0.013733 | 0.064087 | -0.073242 | -0.18768 | -0.13275 | -0.054932 | -0.19226 | -0.027466 | -0.018311 | -0.082397 | -0.14648 | 0.11902 | 0.004578 | -120.4651 | 0.10529 | 0.17853 | 0.17395 | -120.6116 | 0.10986 | 0.045777 | -120.5566 | 0.05951 | 0 | -0.045777 | -120.5475 | 0.25635 | 0.10986 | 0.1236 | -120.7169 | 0.16479 | 0.17395 | 0.13733 | -120.6757
1436.2188 | 120.7352 | -0.15106 | 120.5292 | -0.00091566 | 0.017752 | -0.00026071 | 0.0054667 | 0.056142 | -0.0030677 | -0.0020507 | 0.0067901 | -0.0024268 | -0.029922 | 0.040076 | 0.0051075 | 0.0037106 | 0.004578 | 0.013733 | 0.032043 | 0.054932 | 0.036621 | -0.018311 | -0.14191 | -0.009155 | 0.059509 | -0.07782 | -0.059509 | -0.050354 | -0.022888 | -0.10986 | 0.13275 | 0.009155 | -120.4926 | 0.16479 | 0.20599 | 0.19684 | -120.5246 | 0.12817 | 0.041199 | -120.5887 | 0.14191 | 0.073242 | 0.032043 | -120.5795 | 0.18768 | 0.15564 | 0.18311 | -120.6711 | 0.091553 | 0.10071 | 0.21057 | -120.639
1437.9062 | 120.6711 | -0.19226 | 120.5795 | -0.0085447 | 0.015616 | 0.00080749 | 0.0069621 | 0.054006 | -0.0024267 | -0.0052551 | -0.0084684 | -0.0009314 | -0.030136 | 0.040716 | 0.0025441 | 0.0054196 | -0.091553 | -0.086975 | -0.068665 | -0.004578 | 0.086975 | -0.054932 | -0.20599 | -0.13275 | -0.073242 | -0.20142 | -0.022888 | 0 | -0.07782 | -0.13733 | 0.13733 | -0.013733 | -120.4926 | 0.10529 | 0.18768 | 0.20142 | -120.6711 | 0.11444 | 0.054932 | -120.6024 | 0.05951 | -0.009155 | -0.064087 | -120.5795 | 0.27924 | 0.10071 | 0.1236 | -120.7855 | 0.16937 | 0.19226 | 0.11902 | -120.7169
1439.6562 | 120.7855 | -0.14191 | 120.5521 | -0.0085447 | 0.016257 | 0.0016619 | 0.0041849 | 0.055501 | -0.0015723 | -0.0031189 | -0.016098 | 0.0001368 | -0.031631 | 0.040503 | 0.0057485 | 0.0047788 | -0.082397 | -0.086975 | -0.068665 | 0.004578 | 0.059509 | -0.068665 | -0.1831 | -0.10071 | -0.027466 | -0.17853 | -0.022888 | 0.004578 | -0.059509 | -0.13733 | 0.073242 | -0.041198 | -120.4926 | 0.054932 | 0.14649 | 0.18768 | -120.6345 | 0.082398 | 0.004578 | -120.575 | 0.041199 | -0.036621 | -0.041199 | -120.5475 | 0.20142 | 0.05951 | 0.073242 | -120.7352 | 0.11902 | 0.14649 | 0.11444 | -120.6894
1441.3438 | 120.7901 | -0.16022 | 120.5978 | -0.00091566 | 0.014548 | 0.00038029 | 0.0024759 | 0.053365 | -0.00071771 | -0.0061095 | -0.00083936 | -7.6996e-05 | -0.030563 | 0.040076 | 0.0059621 | 0.0049924 | -0.082397 | -0.11902 | -0.091553 | -0.004578 | 0.059509 | -0.054932 | -0.18768 | -0.11902 | -0.10986 | -0.23804 | -0.018311 | -0.013733 | -0.045776 | -0.16479 | 0.10528 | -0.027466 | -120.5383 | 0.041198 | 0.15564 | 0.1831 | -120.6802 | 0.11444 | -0.004578 | -120.6161 | 0.041198 | -0.07782 | -0.073242 | -120.6116 | 0.21973 | 0.07782 | 0.068664 | -120.7855 | 0.14191 | 0.14648 | 0.050354 | -120.7626
1443.1094 | 120.7993 | -0.17853 | 120.6116 | -0.0085447 | 0.014975 | 0.0012347 | 0.0031167 | 0.050588 | -7.6908e-05 | -0.0020507 | -0.0084684 | 0.0018456 | -0.031204 | 0.041144 | 0.0078847 | 0.0049924 | -0.10986 | -0.14648 | -0.11902 | -0.009155 | 0.082397 | -0.050354 | -0.16937 | -0.13275 | -0.11444 | -0.20599 | -0.022888 | -0.009155 | -0.073242 | -0.15106 | 0.12817 | 0.009155 | -120.5292 | 0.032044 | 0.16937 | 0.16022 | -120.7214 | 0.10529 | 0.027466 | -120.6345 | 0.045777 | -0.027466 | -0.054932 | -120.6207 | 0.26092 | 0.068665 | 0.059509 | -120.7809 | 0.15564 | 0.16937 | 0.064087 | -120.7626
1444.8594 | 120.7214 | -0.19226 | 120.6253 | -0.00091566 | 0.014975 | 0.0018757 | 0.0061075 | 0.054006 | -0.0064855 | -0.0058959 | -0.016098 | -0.0043494 | -0.032486 | 0.037298 | 0.0012623 | 0.005206 | 0.013733 | 0.054932 | 0.073242 | 0.086975 | 0.032043 | -0.022888 | -0.15564 | -0.032043 | 0.07782 | -0.059509 | -0.059509 | -0.036621 | -0.022888 | -0.10986 | 0.16937 | 0.036621 | -120.5933 | 0.24719 | 0.27924 | 0.24261 | -120.6116 | 0.16937 | 0.082398 | -120.6848 | 0.16022 | 0.13275 | 0.050354 | -120.6619 | 0.2243 | 0.20599 | 0.2655 | -120.7809 | 0.13275 | 0.15564 | 0.27008 | -120.7352
1446.5469 | 120.8862 | -0.16479 | 120.6345 | -0.00091566 | 0.012198 | 0.00038029 | 0.0031167 | 0.056997 | -0.00050411 | -0.0020507 | -0.00083936 | -0.0017858 | -0.030349 | 0.038794 | 0.0066029 | 0.0041378 | -0.045776 | -0.064087 | -0.032043 | 0.018311 | 0.045776 | -0.041199 | -0.16479 | -0.050354 | 0.018311 | -0.10071 | -0.068665 | -0.054932 | -0.022888 | -0.1236 | 0.1236 | 0 | -120.5887 | 0.10071 | 0.18311 | 0.18311 | -120.6802 | 0.14191 | 0.041199 | -120.7031 | 0.11444 | 0.064087 | 0.022888 | -120.6894 | 0.21057 | 0.11902 | 0.13275 | -120.7993 | 0.09613 | 0.10986 | 0.18311 | -120.7581
1448.25 | 120.8817 | -0.15564 | 120.6757 | -0.00091566 | 0.010916 | 0.0018757 | 0.0058939 | 0.055501 | -0.0026403 | -0.0044007 | 0.0067901 | -0.0005042 | -0.031417 | 0.040503 | 0.0042531 | 0.0037106 | 0.022888 | 0.018311 | 0.050354 | 0.07782 | 0.032043 | -0.009155 | -0.16479 | -0.009155 | 0.045776 | -0.07782 | -0.068665 | -0.064087 | -0.027466 | -0.10529 | 0.14649 | -0.009155 | -120.6436 | 0.17395 | 0.23346 | 0.24261 | -120.6528 | 0.12817 | 0.050354 | -120.7443 | 0.14649 | 0.07782 | 0.027466 | -120.7397 | 0.18768 | 0.17853 | 0.20599 | -120.8405 | 0.086975 | 0.091553 | 0.20142 | -120.7809
1450 | 120.9274 | -0.14191 | 120.6802 | -0.00091566 | 0.015616 | 0.0014483 | 0.0054667 | 0.055074 | -0.00029051 | -0.0031189 | -0.00083936 | -0.0013586 | -0.029495 | 0.040076 | 0.0055349 | 0.0043516 | -0.050354 | -0.082397 | -0.045776 | 0.022888 | 0.068665 | -0.045776 | -0.17853 | -0.091553 | -0.018311 | -0.16479 | -0.041199 | -0.004578 | -0.054932 | -0.14648 | 0.096131 | -0.036621 | -120.6116 | 0.05951 | 0.16479 | 0.20142 | -120.7306 | 0.086975 | -0.004577 | -120.7214 | 0.050354 | -0.022888 | -0.018311 | -120.6848 | 0.21057 | 0.091553 | 0.096131 | -120.8588 | 0.10071 | 0.13733 | 0.1236 | -120.8267
1451.6875 | 120.8771 | -0.17853 | 120.6802 | -0.00091566 | 0.015616 | 0.0010211 | 0.0052531 | 0.05187 | 0.0012049 | -0.0033325 | -0.00083936 | 0.000564 | -0.030349 | 0.042853 | 0.0051075 | 0.0054196 | -0.059509 | -0.1236 | -0.064087 | -0.009155 | 0.050354 | -0.036621 | -0.19684 | -0.11902 | -0.10529 | -0.23346 | -0.027466 | -0.009155 | -0.059509 | -0.15106 | 0.14191 | -0.01831 | -120.6299 | 0.054932 | 0.16937 | 0.18768 | -120.7397 | 0.11902 | 0.027466 | -120.7077 | 0.059509 | -0.054931 | -0.082397 | -120.6894 | 0.22888 | 0.11902 | 0.11444 | -120.8771 | 0.15106 | 0.16937 | 0.073242 | -120.8313
1453.4531 | 120.9549 | -0.13733 | 120.694 | 0.0067138 | 0.01583 | -0.00068791 | 0.0054667 | 0.05486 | -0.0028539 | -0.0044007 | -0.0084684 | -0.0022132 | -0.030349 | 0.042639 | 0.0038259 | 0.0043516 | -0.041199 | -0.068665 | -0.027466 | 0.027466 | 0.064087 | -0.073242 | -0.19684 | -0.07782 | -0.013733 | -0.14191 | -0.027466 | -0.013733 | -0.054932 | -0.13275 | 0.064087 | -0.059509 | -120.6299 | 0.068664 | 0.16479 | 0.2243 | -120.7352 | 0.082397 | 0.004578 | -120.7214 | 0.059509 | -0.004578 | -0.009156 | -120.7077 | 0.20142 | 0.09613 | 0.10986 | -120.8908 | 0.10986 | 0.1236 | 0.1236 | -120.8267
1455.2188 | 120.9045 | -0.17853 | 120.726 | -0.00091566 | 0.016684 | 0.0018757 | 0.0065347 | 0.05422 | -0.0034949 | -0.0029053 | -0.0084684 | -0.002854 | -0.032272 | 0.039648 | 0.0031849 | 0.0090512 | -0.086975 | -0.10986 | -0.068665 | -0.004578 | 0.054932 | -0.054932 | -0.20142 | -0.15106 | -0.068665 | -0.19684 | -0.004578 | 0.009155 | -0.064087 | -0.15106 | 0.1236 | -0.022888 | -120.6711 | 0.068665 | 0.17395 | 0.19684 | -120.813 | 0.11444 | 0.027466 | -120.7306 | 0.027466 | -0.01831 | -0.045776 | -120.7169 | 0.23346 | 0.091553 | 0.10986 | -120.9274 | 0.17395 | 0.18768 | 0.10986 | -120.8771
1456.9062 | 120.8267 | -0.19226 | 120.7764 | 0.0067138 | 0.013052 | 0.0023029 | 0.0065347 | 0.056142 | -0.0066993 | -0.0052551 | -0.0084684 | -0.0047766 | -0.030349 | 0.036871 | 0.0010487 | 0.0047788 | -0.004578 | 0.009155 | 0.050354 | 0.068665 | 0.018311 | -0.032043 | -0.15564 | -0.054932 | 0.022888 | -0.11902 | -0.054932 | -0.032043 | -0.050354 | -0.12817 | 0.16022 | 0.036621 | -120.7581 | 0.20142 | 0.26093 | 0.22431 | -120.7809 | 0.14191 | 0.064087 | -120.8313 | 0.13733 | 0.073242 | 0.009155 | -120.8084 | 0.21057 | 0.18768 | 0.24261 | -120.932 | 0.13733 | 0.16022 | 0.21515 | -120.9045
1458.6562 | 120.9045 | -0.20142 | 120.8313 | -0.00091566 | 0.013052 | 0.0046527 | 0.0046121 | 0.052724 | -0.0060583 | -0.0056823 | -0.0084684 | -0.0032812 | -0.031204 | 0.037298 | 0.0012623 | 0.0060604 | -0.064087 | -0.036621 | 0.009155 | 0.036621 | 0.022888 | -0.036621 | -0.14648 | -0.082397 | -0.009155 | -0.12817 | -0.054932 | -0.050354 | -0.041199 | -0.11444 | 0.1648 | 0.054932 | -120.8084 | 0.1648 | 0.23804 | 0.18311 | -120.8954 | 0.16022 | 0.086975 | -120.8862 | 0.11902 | 0.073242 | -0.013733 | -120.8817 | 0.2243 | 0.13733 | 0.21057 | -120.9778 | 0.14648 | 0.15106 | 0.19226 | -120.9457
1460.4062 | 121.0236 | -0.13275 | 120.7809 | -0.00091566 | 0.016257 | 0.0012347 | 0.0043985 | 0.053152 | 0.00099129 | -0.0052551 | -0.0084684 | 0.0001368 | -0.030136 | 0.039862 | 0.0046803 | 0.0049924 | -0.041199 | -0.086975 | -0.059509 | 0.018311 | 0.064087 | -0.068665 | -0.16937 | -0.09613 | -0.036621 | -0.17395 | -0.027466 | -0.013733 | -0.068665 | -0.14191 | 0.064086 | -0.036622 | -120.7169 | 0.045776 | 0.15106 | 0.18768 | -120.8221 | 0.064086 | -0.009156 | -120.8084 | 0.036621 | -0.041199 | -0.032043 | -120.7947 | 0.19684 | 0.091552 | 0.073242 | -120.9503 | 0.10529 | 0.11902 | 0.09613 | -120.9229
1462.1562 | 116.954 | -22.7234 | 94.1071 | -0.0085447 | 0.014548 | -0.00047431 | 0.0082437 | 0.055501 | -0.0037085 | -0.0035461 | -0.0084684 | -0.0005042 | -0.03099 | 0.041357 | 0.0031849 | 0.0058468 | -0.064087 | -0.082397 | -0.027466 | 0.022888 | 0.086975 | -0.041199 | -0.15106 | -0.11444 | -0.027466 | -0.16937 | 0.018311 | 0.018311 | -0.041199 | -0.13275 | 22.6822 | 22.5723 | -94.0201 | 22.641 | 22.7463 | 0.17395 | -94.1711 | 22.6822 | 22.5906 | -94.0887 | 22.6089 | 22.554 | -0.036622 | -94.0887 | 22.8104 | 22.6593 | 22.6959 | -94.2581 | 22.7417 | 22.7417 | 22.6959 | -94.2398
1463.9062 | 120.6848 | -0.1831 | 120.575 | -0.00091566 | 0.00878 | 0.00080749 | 0.0046121 | 0.055288 | -0.0045629 | -0.0058959 | -0.00083936 | -0.004563 | -0.03334 | 0.038794 | 0.0027577 | 0.0049924 | 0.032043 | 0.059509 | 0.086975 | 0.073242 | 0.022888 | -0.027466 | -0.15564 | -0.027466 | 0.086975 | -0.050354 | -0.054932 | -0.064087 | -0.045776 | -0.10529 | 0.15564 | 0.027465 | -120.5521 | 0.24261 | 0.25635 | 0.22888 | -120.5429 | 0.13733 | 0.077819 | -120.6299 | 0.15564 | 0.13275 | 0.054932 | -120.639 | 0.20599 | 0.21515 | 0.27008 | -120.7306 | 0.12817 | 0.11902 | 0.27008 | -120.6802
1465.5938 | 120.8221 | -0.16937 | 120.6528 | -0.00091566 | 0.014334 | 0.0018757 | 0.0041849 | 0.053792 | -0.00050411 | -0.0039733 | -0.0084684 | -0.0024268 | -0.030777 | 0.040503 | 0.0051075 | 0.0043516 | 0.022888 | 0.027466 | 0.059509 | 0.07782 | 0.027466 | -0.041199 | -0.1236 | 0.004578 | 0.041199 | -0.073242 | -0.068665 | -0.059509 | -0.036621 | -0.09613 | 0.12817 | 0.045777 | -120.6253 | 0.19684 | 0.24719 | 0.20142 | -120.6299 | 0.13275 | 0.073243 | -120.7214 | 0.17395 | 0.096131 | 0.022888 | -120.7123 | 0.19684 | 0.19226 | 0.22888 | -120.7764 | 0.10071 | 0.10986 | 0.21057 | -120.7489
1467.3594 | 120.575 | -0.1831 | 120.4971 | -0.0085447 | 0.015189 | 0.00080749 | 0.0067483 | 0.055929 | -0.0032813 | -0.0041869 | -0.016098 | -0.0039222 | -0.028213 | 0.038367 | 0.0031849 | 0.0032834 | 0 | 0.009155 | 0.022888 | 0.064087 | 0.032043 | -0.032043 | -0.16022 | -0.082397 | 0.018311 | -0.13275 | -0.032043 | -0.022888 | -0.059509 | -0.13733 | 0.15106 | 0.022888 | -120.4651 | 0.19226 | 0.24719 | 0.2243 | -120.4971 | 0.1236 | 0.045776 | -120.5292 | 0.10071 | 0.050354 | 0.004578 | -120.52 | 0.21515 | 0.1831 | 0.20599 | -120.6573 | 0.15106 | 0.16022 | 0.20142 | -120.6345
1469.1094 | 120.7031 | -0.19684 | 120.639 | -0.00091566 | 0.01583 | 0.0027301 | 0.0069621 | 0.055929 | -0.0028539 | -0.0050415 | -0.0084684 | -0.0022132 | -0.028854 | 0.040716 | 0.0031849 | 0.0049924 | -0.064087 | -0.050354 | -0.045776 | 0 | 0.050354 | -0.064087 | -0.18768 | -0.1236 | -0.041199 | -0.19684 | -0.027466 | -0.018311 | -0.07782 | -0.14648 | 0.13275 | 0.009155 | -120.5887 | 0.14648 | 0.19684 | 0.18768 | -120.7031 | 0.11902 | 0.050354 | -120.6665 | 0.073242 | 0 | -0.050354 | -120.6573 | 0.24719 | 0.13275 | 0.15106 | -120.8267 | 0.16937 | 0.17853 | 0.15564 | -120.7855
1470.8594 | 120.7718 | -0.21515 | 120.6757 | -0.00091566 | 0.012839 | 0.0031573 | 0.0058939 | 0.05422 | -0.0047765 | -0.0035461 | -0.00083936 | -0.002854 | -0.03099 | 0.039007 | 0.0051075 | 0.0077694 | -0.036621 | -0.013733 | 0.009155 | 0.036621 | 0.036621 | -0.018311 | -0.15106 | -0.07782 | -0.013733 | -0.12817 | -0.045776 | -0.041199 | -0.027466 | -0.11902 | 0.19684 | 0.064087 | -120.639 | 0.20142 | 0.25177 | 0.18768 | -120.7123 | 0.18768 | 0.09613 | -120.7214 | 0.13733 | 0.086975 | -0.009155 | -120.7169 | 0.25177 | 0.17853 | 0.2243 | -120.8267 | 0.16937 | 0.17395 | 0.20142 | -120.7947
1472.5625 | 120.8359 | -0.21515 | 120.726 | -0.0085447 | 0.012839 | 0.0046527 | 0.0029031 | 0.054647 | -0.0056311 | -0.0037597 | 0.0067901 | -0.0030676 | -0.030349 | 0.039221 | 0.00040787 | 0.0037106 | -0.036621 | -0.041199 | -0.009155 | 0.018311 | 0.041199 | -0.054932 | -0.16937 | -0.068665 | -0.004578 | -0.11444 | -0.054932 | -0.036621 | -0.041199 | -0.12817 | 0.16022 | 0.045776 | -120.6848 | 0.17395 | 0.23346 | 0.18768 | -120.7626 | 0.17395 | 0.086975 | -120.7809 | 0.14648 | 0.10071 | 0.013733 | -120.7626 | 0.25635 | 0.17853 | 0.20599 | -120.8954 | 0.16022 | 0.17853 | 0.21057 | -120.8542
1474.3281 | 120.8908 | -0.15564 | 120.5978 | -0.00091566 | 0.015189 | 0.00016669 | 0.0041849 | 0.054006 | -0.00050411 | -0.0035461 | -0.00083936 | -7.6996e-05 | -0.030136 | 0.041998 | 0.0055349 | 0.0020016 | 0 | -0.032043 | -0.018311 | 0.032043 | 0.059509 | -0.036621 | -0.17853 | -0.036621 | -0.022888 | -0.15564 | -0.022888 | -0.036621 | -0.045776 | -0.15106 | 0.11902 | -0.022888 | -120.5383 | 0.1236 | 0.18768 | 0.21057 | -120.5978 | 0.10986 | 0.004578 | -120.6207 | 0.11902 | 0 | -0.004578 | -120.6345 | 0.21515 | 0.15564 | 0.13733 | -120.7764 | 0.13275 | 0.11902 | 0.13275 | -120.7489
1476.0781 | 120.8084 | -0.21057 | 120.7535 | -0.0085447 | 0.015616 | 0.0044391 | 0.0071757 | 0.055074 | -0.0039221 | -0.0024779 | -0.016098 | -0.0047766 | -0.029708 | 0.038794 | 0.0036123 | 0.0067014 | -0.004578 | 0.022888 | 0.041199 | 0.068665 | 0.036621 | -0.041199 | -0.17853 | -0.07782 | 0.022888 | -0.13733 | -0.036621 | -0.027466 | -0.059509 | -0.13733 | 0.16937 | 0.032043 | -120.7169 | 0.23346 | 0.27924 | 0.24719 | -120.7581 | 0.15106 | 0.073242 | -120.7901 | 0.13275 | 0.073242 | 0 | -120.7809 | 0.24719 | 0.20599 | 0.25177 | -120.932 | 0.17395 | 0.18311 | 0.23346 | -120.8908
1477.8281 | 120.9732 | -0.16479 | 120.7169 | 0.0067138 | 0.013907 | 0.0025165 | 0.0037577 | 0.054647 | 0.0014185 | -0.0039733 | -0.0084684 | 0.0001368 | -0.029708 | 0.042639 | 0.0066029 | 0.0054196 | -0.064087 | -0.10529 | -0.091553 | -0.004578 | 0.082397 | -0.059509 | -0.19226 | -0.10071 | -0.10071 | -0.21057 | -0.018311 | -0.022888 | -0.050354 | -0.13733 | 0.10529 | -0.027466 | -120.6345 | 0.059509 | 0.16022 | 0.18768 | -120.7809 | 0.11444 | 0.027466 | -120.7352 | 0.064087 | -0.045776 | -0.073242 | -120.7397 | 0.24719 | 0.10071 | 0.073242 | -120.9091 | 0.14648 | 0.14191 | 0.064087 | -120.8542
1479.5156 | 120.9595 | -0.17395 | 120.7809 | -0.0085447 | 0.01647 | 0.00080749 | 0.0043985 | 0.055288 | 0.0014185 | -0.0011963 | -0.00083936 | -0.0002906 | -0.031631 | 0.043921 | 0.0083119 | 0.005206 | -0.045776 | -0.054932 | -0.041199 | 0.018311 | 0.073242 | -0.041199 | -0.1831 | -0.086975 | -0.068665 | -0.21057 | -0.032043 | -0.022888 | -0.045776 | -0.13275 | 0.13275 | -0.009155 | -120.7077 | 0.11902 | 0.19226 | 0.20142 | -120.8267 | 0.12817 | 0.041199 | -120.813 | 0.086975 | -0.036621 | -0.07782 | -120.8038 | 0.24719 | 0.12817 | 0.13275 | -120.9641 | 0.14191 | 0.15106 | 0.10528 | -120.9137
1481.2656 | 120.9091 | -0.20599 | 120.8084 | -0.0085447 | 0.013052 | 0.0055073 | 0.0069621 | 0.055715 | -0.0079809 | -0.0031189 | -0.016098 | -0.0069128 | -0.030563 | 0.037726 | 0.0021169 | 0.0071286 | -0.068665 | -0.027466 | 0.004578 | 0.027466 | 0.036621 | -0.018311 | -0.15564 | -0.086975 | 0.009155 | -0.10986 | -0.068665 | -0.050354 | -0.041199 | -0.11902 | 0.18768 | 0.050354 | -120.7718 | 0.17853 | 0.23346 | 0.18311 | -120.8771 | 0.1648 | 0.086975 | -120.8771 | 0.11902 | 0.096131 | 0.009156 | -120.8588 | 0.24262 | 0.13733 | 0.21057 | -120.9641 | 0.13733 | 0.15564 | 0.21515 | -120.9274
1483.0312 | 120.8633 | -0.19226 | 120.7397 | -0.00091566 | 0.014334 | 0.0027301 | 0.0048257 | 0.050802 | -0.0054175 | -0.0046143 | 0.0067901 | -0.0037086 | -0.029495 | 0.039007 | 0.0036123 | 0.0064878 | 0.027466 | 0.041199 | 0.064087 | 0.068665 | 0.032043 | -0.004578 | -0.1236 | -0.036621 | 0.041199 | -0.10529 | -0.041199 | -0.059509 | -0.013733 | -0.11444 | 0.18768 | 0.068665 | -120.7077 | 0.23346 | 0.26093 | 0.19226 | -120.7123 | 0.17853 | 0.07782 | -120.7809 | 0.15564 | 0.086975 | 0.009155 | -120.7993 | 0.2243 | 0.21973 | 0.25635 | -120.8633 | 0.15106 | 0.13275 | 0.23346 | -120.8542
1484.7188 | 121.0144 | -0.15106 | 120.7535 | -0.016174 | 0.015189 | 0.0014483 | 0.0052531 | 0.052938 | 0.0014185 | -0.0029053 | -0.0084684 | 0.0001368 | -0.032058 | 0.041998 | 0.0036123 | 0.0026426 | -0.059509 | -0.086975 | -0.073242 | 0.009155 | 0.07782 | -0.054932 | -0.19226 | -0.10529 | -0.050354 | -0.19684 | -0.022888 | 0.004578 | -0.054932 | -0.13733 | 0.09613 | -0.041199 | -120.6757 | 0.064087 | 0.16022 | 0.20142 | -120.813 | 0.09613 | 0.013733 | -120.7764 | 0.045776 | -0.045776 | -0.059509 | -120.7489 | 0.22888 | 0.091553 | 0.07782 | -120.9457 | 0.12817 | 0.15564 | 0.10071 | -120.8908
1486.4688 | 121.0419 | -0.14191 | 120.7809 | 0.0067138 | 0.012839 | 0.0029437 | 0.0050393 | 0.055501 | -0.0011451 | -0.00076912 | -0.00083936 | 0.000564 | -0.031204 | 0.041785 | 0.0053211 | 0.0039242 | 0.004578 | 0.004578 | 0.027466 | 0.068665 | 0.045776 | -0.009155 | -0.14648 | -0.004578 | 0.041199 | -0.07782 | -0.059509 | -0.036621 | -0.009155 | -0.086975 | 0.13275 | -0.004577 | -120.7352 | 0.14649 | 0.21057 | 0.21515 | -120.7764 | 0.13275 | 0.054932 | -120.8405 | 0.13733 | 0.064087 | 0.009155 | -120.8176 | 0.18768 | 0.14649 | 0.16937 | -120.9274 | 0.082398 | 0.10529 | 0.18311 | -120.8679
1488.2188 | 120.932 | -0.18768 | 120.8588 | -0.0085447 | 0.010489 | 0.00080749 | 0.0054667 | 0.055929 | -0.0052039 | -0.0046143 | -0.00083936 | -0.0054174 | -0.030563 | 0.039648 | 0.0027577 | 0.006915 | 0.009155 | 0.027466 | 0.041199 | 0.054932 | 0.036621 | -0.009155 | -0.13733 | -0.041199 | 0.013733 | -0.091553 | -0.059509 | -0.054932 | -0.013733 | -0.10071 | 0.17853 | 0.050354 | -120.8221 | 0.21515 | 0.24261 | 0.19226 | -120.8496 | 0.17395 | 0.086975 | -120.9183 | 0.14648 | 0.09613 | 0.009155 | -120.9137 | 0.2243 | 0.19684 | 0.22888 | -120.9961 | 0.12817 | 0.13275 | 0.20142 | -120.9595
1489.9688 | 120.9961 | -0.1831 | 120.845 | -0.00091566 | 0.011984 | 0.0072161 | 0.0050393 | 0.057424 | -0.0039221 | -0.0069641 | -0.0084684 | -0.0019996 | -0.033554 | 0.038794 | 0.0025441 | 0.0037106 | 0.045776 | 0.073242 | 0.086975 | 0.07782 | 0.045776 | -0.018311 | -0.1236 | -0.013733 | 0.086975 | -0.036621 | -0.050354 | -0.045776 | -0.022888 | -0.10529 | 0.16479 | 0.059509 | -120.7993 | 0.25635 | 0.26092 | 0.20142 | -120.7993 | 0.16022 | 0.077819 | -120.8954 | 0.16937 | 0.14648 | 0.068665 | -120.8908 | 0.22888 | 0.22888 | 0.27008 | -120.9686 | 0.13275 | 0.13733 | 0.27008 | -120.9503
1491.6562 | 120.9686 | -0.20599 | 120.8908 | -0.0085447 | 0.009848 | 0.0031573 | 0.0033305 | 0.056142 | -0.0030677 | -0.0056823 | -0.0084684 | -0.0041358 | -0.032486 | 0.037726 | 0.0046803 | 0.0073422 | 0.004578 | 0.013733 | 0.032043 | 0.041199 | 0.041199 | -0.022888 | -0.13275 | -0.045776 | -0.009155 | -0.10986 | -0.036621 | -0.041199 | -0.009155 | -0.11902 | 0.18311 | 0.073243 | -120.8496 | 0.21973 | 0.24719 | 0.17395 | -120.8862 | 0.19684 | 0.086975 | -120.9274 | 0.16022 | 0.096131 | 0.009156 | -120.932 | 0.24719 | 0.21057 | 0.23804 | -121.0236 | 0.16937 | 0.1648 | 0.19684 | -121.0098
1493.4062 | 121.0968 | -0.14648 | 120.8771 | -0.016174 | 0.015189 | 0.00038029 | 0.0031167 | 0.055715 | 0.0037683 | -0.0046143 | -0.0084684 | 0.0012048 | -0.032272 | 0.039862 | 0.0072437 | 0.0030698 | -0.009155 | -0.018311 | -0.009155 | 0.036621 | 0.073242 | -0.054932 | -0.19684 | -0.036621 | -0.004578 | -0.16022 | -0.018311 | -0.022888 | -0.054932 | -0.12817 | 0.091552 | -0.050354 | -120.8038 | 0.12817 | 0.18311 | 0.23346 | -120.8862 | 0.091552 | 0.01831 | -120.8954 | 0.10986 | -0.013733 | -0.032043 | -120.9 | 0.21973 | 0.13733 | 0.13733 | -121.0739 | 0.12817 | 0.1236 | 0.14191 | -121.0052
1495.1719 | 121.0648 | -0.16937 | 120.9457 | 0.014343 | 0.012412 | 0.0035847 | 0.0088847 | 0.052724 | -0.0064855 | -0.0031189 | -0.00083936 | -0.0049902 | -0.031417 | 0.040503 | -0.00044673 | 0.0067014 | -0.022888 | -0.004578 | 0.041199 | 0.050354 | 0.050354 | -0.027466 | -0.15106 | -0.036621 | 0.050354 | -0.054932 | -0.059509 | -0.032043 | -0.027466 | -0.11444 | 0.14191 | 0.018311 | -120.8954 | 0.16479 | 0.21973 | 0.20142 | -120.9686 | 0.14191 | 0.054932 | -121.0052 | 0.13275 | 0.11444 | 0.059509 | -120.9778 | 0.21973 | 0.14649 | 0.21057 | -121.0968 | 0.10986 | 0.13733 | 0.21973 | -121.0602
1496.9375 | 121.0602 | -0.17395 | 120.9549 | -0.0085447 | 0.01348 | 0.0016619 | 0.0050393 | 0.05721 | -0.0069129 | -0.0054687 | -0.00083936 | -0.0030676 | -0.031631 | 0.039862 | 0.0029713 | 0.0047788 | 0.022888 | 0.068665 | 0.07782 | 0.07782 | 0.022888 | -0.013733 | -0.14648 | -0.004578 | 0.11444 | -0.041199 | -0.045776 | -0.054932 | -0.022888 | -0.10986 | 0.16022 | 0.027466 | -120.932 | 0.24261 | 0.25177 | 0.2243 | -120.932 | 0.15106 | 0.064087 | -121.0007 | 0.16937 | 0.13275 | 0.068664 | -121.0098 | 0.19684 | 0.19684 | 0.25177 | -121.1014 | 0.12817 | 0.11902 | 0.28839 | -121.0648
1498.625 | 121.0556 | -0.21057 | 120.9824 | -0.0085447 | 0.011343 | 0.0042255 | 0.0022623 | 0.052938 | -0.0032813 | -0.0048279 | -0.0084684 | -0.0017858 | -0.033981 | 0.039648 | 0.0044667 | 0.0060604 | 0.027466 | 0.032043 | 0.050354 | 0.059509 | 0.045776 | -0.013733 | -0.13733 | -0.027466 | 0.018311 | -0.10071 | -0.059509 | -0.027466 | -0.018311 | -0.11444 | 0.19684 | 0.073242 | -120.9366 | 0.24261 | 0.27008 | 0.19684 | -120.9549 | 0.19226 | 0.09613 | -121.0419 | 0.18311 | 0.10986 | 0.013733 | -121.0098 | 0.25635 | 0.23804 | 0.26093 | -121.1197 | 0.15106 | 0.18311 | 0.22888 | -121.0968
1500.375 | 121.1655 | -0.14648 | 120.9229 | -0.00091566 | 0.013693 | 0.0010211 | 0.0024759 | 0.054006 | 0.00013669 | -0.0018371 | -0.023727 | 0.0018456 | -0.031845 | 0.040716 | 0.0063893 | 0.0037106 | -0.036621 | -0.086975 | -0.068665 | 0.018311 | 0.059509 | -0.068665 | -0.17853 | -0.07782 | -0.018311 | -0.16022 | -0.004578 | -0.022888 | -0.059509 | -0.13733 | 0.077819 | -0.032044 | -120.8633 | 0.059509 | 0.16479 | 0.19684 | -120.9595 | 0.086975 | 0.009155 | -120.9274 | 0.068664 | -0.013733 | -0.022888 | -120.9457 | 0.20599 | 0.10986 | 0.077819 | -121.1014 | 0.14191 | 0.1236 | 0.12817 | -121.0602
1502.1406 | 121.0876 | -0.18768 | 120.9595 | -0.0085447 | 0.012625 | 0.0031573 | 0.0063211 | 0.054433 | -0.0049903 | -0.0052551 | -0.016098 | -0.0047766 | -0.030563 | 0.037512 | 0.0021169 | 0.0075558 | 0.022888 | 0.050354 | 0.059509 | 0.07782 | 0.041199 | -0.027466 | -0.15106 | 0 | 0.10529 | -0.041199 | -0.054932 | -0.054932 | -0.027466 | -0.10986 | 0.16022 | 0.036621 | -120.9183 | 0.23804 | 0.2655 | 0.22888 | -120.9366 | 0.16022 | 0.07782 | -121.0144 | 0.18768 | 0.14648 | 0.068664 | -121.0144 | 0.22888 | 0.21057 | 0.24719 | -121.1105 | 0.13275 | 0.13275 | 0.29297 | -121.0693
1503.9062 | 121.0464 | -0.18768 | 120.9137 | -0.00091566 | 0.013907 | 0.0029437 | 0.0058939 | 0.053152 | -0.0019995 | -0.0052551 | -0.00083936 | -0.0002906 | -0.031204 | 0.039221 | 0.0040395 | 0.0047788 | -0.068665 | -0.09613 | -0.082397 | -0.032043 | 0.059509 | -0.059509 | -0.18768 | -0.12817 | -0.059509 | -0.20142 | -0.013733 | -0.027466 | -0.059509 | -0.16479 | 0.12817 | 0 | -120.8542 | 0.091553 | 0.15564 | 0.15564 | -120.9824 | 0.12817 | 0.022888 | -120.9274 | 0.059509 | -0.013733 | -0.036621 | -120.9412 | 0.24719 | 0.11902 | 0.10529 | -121.1014 | 0.17395 | 0.16022 | 0.12817 | -121.0785
1505.6094 | 120.9961 | -0.14191 | 120.813 | -0.00091566 | 0.01647 | 0.0044391 | 0.0061075 | 0.056356 | -0.00050411 | -0.0041869 | -0.00083936 | 0.0007776 | -0.030777 | 0.040716 | 0.0036123 | 0.005206 | -0.073242 | -0.09613 | -0.082397 | 0 | 0.073242 | -0.064087 | -0.18768 | -0.10529 | -0.068665 | -0.20142 | -0.009155 | -0.032043 | -0.068665 | -0.16479 | 0.07782 | -0.045776 | -120.7397 | 0.045777 | 0.14191 | 0.18768 | -120.8862 | 0.073242 | -0.022888 | -120.8221 | 0.036621 | -0.059509 | -0.036621 | -120.845 | 0.21515 | 0.068665 | 0.05951 | -121.0007 | 0.13275 | 0.10986 | 0.073242 | -120.9778
1507.375 | 121.0098 | -0.19684 | 120.8771 | -0.00091566 | 0.011771 | 0.0044391 | 0.0046121 | 0.054006 | -0.0060583 | -0.0050415 | 0.0067901 | -0.0056312 | -0.03099 | 0.039435 | 0.00019427 | 0.0064878 | -0.036621 | -0.009155 | 0.009155 | 0.045776 | 0.032043 | -0.036621 | -0.15106 | -0.054932 | 0.032043 | -0.07782 | -0.050354 | -0.050354 | -0.041199 | -0.11444 | 0.16022 | 0.045776 | -120.845 | 0.18768 | 0.24261 | 0.19684 | -120.9137 | 0.15564 | 0.082397 | -120.9274 | 0.14191 | 0.11902 | 0.036621 | -120.9274 | 0.22888 | 0.16022 | 0.20599 | -121.0281 | 0.14648 | 0.14648 | 0.22888 | -120.9915
1509.0781 | 121.1014 | -0.12817 | 120.8633 | -0.0085447 | 0.013052 | 0.0014483 | 0.0020487 | 0.05422 | 0.0012049 | -0.0035461 | -0.00083936 | -0.0002906 | -0.032913 | 0.040076 | 0.0061757 | 0.0020016 | -0.018311 | -0.073242 | -0.041199 | 0.022888 | 0.064087 | -0.050354 | -0.18768 | -0.054932 | -0.009155 | -0.17395 | -0.041199 | -0.032043 | -0.059509 | -0.14648 | 0.07782 | -0.059509 | -120.7993 | 0.054932 | 0.15106 | 0.21057 | -120.8817 | 0.068665 | -0.01831 | -120.9045 | 0.073242 | -0.045776 | -0.027466 | -120.8954 | 0.19226 | 0.10986 | 0.086975 | -121.051 | 0.086975 | 0.096131 | 0.11902 | -121.0098
1510.8438 | 121.106 | -0.14191 | 120.9229 | -0.00091566 | 0.016257 | 0.0014483 | 0.0071757 | 0.052083 | 0.00077749 | -0.0037597 | -0.0084684 | -0.0009314 | -0.029922 | 0.043066 | 0.0046803 | 0.0039242 | -0.068665 | -0.09613 | -0.086975 | -0.009155 | 0.07782 | -0.064087 | -0.20599 | -0.11902 | -0.054932 | -0.19684 | -0.027466 | -0.013733 | -0.07782 | -0.15106 | 0.07782 | -0.064087 | -120.845 | 0.045777 | 0.13275 | 0.19684 | -120.9915 | 0.064087 | -0.009155 | -120.9503 | 0.022888 | -0.054931 | -0.045776 | -120.9366 | 0.21973 | 0.073242 | 0.054932 | -121.1288 | 0.11444 | 0.12817 | 0.086975 | -121.0739
1512.5938 | 121.0556 | -0.18768 | 120.9366 | 0.0067138 | 0.0096344 | 0.0027301 | 0.0058939 | 0.05422 | -0.0081945 | -0.0029053 | 0.0067901 | -0.0056312 | -0.031631 | 0.03858 | 0.0031849 | 0.0064878 | -0.059509 | -0.009155 | 0.009155 | 0.045776 | 0.041199 | -0.041199 | -0.15106 | -0.064087 | 0.032043 | -0.086975 | -0.064087 | -0.059509 | -0.041199 | -0.12817 | 0.14648 | 0.036621 | -120.8954 | 0.17853 | 0.23346 | 0.19684 | -120.9961 | 0.14648 | 0.059509 | -121.0007 | 0.1236 | 0.10071 | 0.041199 | -120.9961 | 0.22888 | 0.12817 | 0.19684 | -121.0876 | 0.1236 | 0.12817 | 0.21973 | -121.0648
1514.3438 | 121.1288 | -0.14191 | 120.9229 | 0.0067138 | 0.013907 | 0.0020893 | 0.0048257 | 0.055074 | 0.00099129 | -0.0041869 | -0.00083936 | -0.0007178 | -0.029922 | 0.042212 | 0.0044667 | 0.0030698 | -0.073242 | -0.09613 | -0.082397 | -0.004578 | 0.073242 | -0.073242 | -0.20142 | -0.11444 | -0.054932 | -0.19684 | -0.013733 | -0.013733 | -0.068665 | -0.14191 | 0.068665 | -0.059509 | -120.8496 | 0.045777 | 0.13733 | 0.19684 | -120.9961 | 0.073242 | 0 | -120.9366 | 0.027466 | -0.054931 | -0.054931 | -120.9366 | 0.21515 | 0.068665 | 0.05951 | -121.1243 | 0.12817 | 0.12817 | 0.086975 | -121.0648
1516.0938 | 121.1609 | -0.13733 | 120.9412 | 0.0067138 | 0.017752 | 0.0023029 | 0.0052531 | 0.056997 | 0.00035029 | -0.0052551 | -0.0084684 | -7.6996e-05 | -0.031204 | 0.04093 | 0.0053211 | 0.0043516 | -0.054932 | -0.086975 | -0.054932 | 0.022888 | 0.07782 | -0.059509 | -0.19226 | -0.091553 | -0.022888 | -0.16937 | -0.022888 | -0.013733 | -0.059509 | -0.15106 | 0.07782 | -0.054932 | -120.8633 | 0.050354 | 0.16022 | 0.21515 | -120.9961 | 0.07782 | -0.013733 | -120.9641 | 0.045776 | -0.032044 | -0.018311 | -120.9549 | 0.21515 | 0.082397 | 0.082397 | -121.1334 | 0.11444 | 0.1236 | 0.11444 | -121.0922
1517.8594 | 121.1426 | -0.14648 | 120.9412 | -0.00091566 | 0.014761 | -0.00047431 | 0.0011941 | 0.053365 | 0.00013669 | -0.0014099 | -0.00083936 | -7.6996e-05 | -0.030563 | 0.041571 | 0.0070301 | 0.005206 | -0.09613 | -0.14191 | -0.10529 | -0.032043 | 0.064087 | -0.059509 | -0.17853 | -0.11902 | -0.11444 | -0.22888 | -0.018311 | -0.018311 | -0.064087 | -0.15564 | 0.086975 | -0.032044 | -120.8771 | 0.004577 | 0.11444 | 0.14648 | -121.0373 | 0.082397 | -0.009156 | -120.9595 | 0.027465 | -0.082398 | -0.073242 | -120.9595 | 0.21057 | 0.050354 | 0.041198 | -121.1197 | 0.12817 | 0.12817 | 0.032043 | -121.0968
1519.5938 | 121.1151 | -0.17853 | 121.0236 | -0.0085447 | 0.010916 | 0.0027301 | 0.0050393 | 0.054647 | -0.0073401 | -0.0050415 | -0.0084684 | -0.0049902 | -0.030777 | 0.038367 | -0.0013011 | 0.0060604 | -0.004578 | 0.027466 | 0.045776 | 0.059509 | 0.027466 | -0.045776 | -0.15106 | -0.041199 | 0.073242 | -0.054932 | -0.059509 | -0.064087 | -0.036621 | -0.10071 | 0.13275 | 0.027466 | -120.9961 | 0.20599 | 0.23804 | 0.21057 | -121.0281 | 0.14191 | 0.07782 | -121.0831 | 0.13733 | 0.1236 | 0.045776 | -121.0876 | 0.20599 | 0.17395 | 0.2243 | -121.1746 | 0.11902 | 0.11444 | 0.25177 | -121.1243
1521.3594 | 121.0693 | -0.19684 | 121.0098 | -0.00091566 | 0.014548 | 0.0040119 | 0.0052531 | 0.055288 | -0.0028539 | -0.0048279 | -0.00083936 | -0.0013586 | -0.031845 | 0.038794 | 0.0023305 | 0.0060604 | 0.004578 | 0.041199 | 0.059509 | 0.073242 | 0.022888 | -0.054932 | -0.16479 | -0.032043 | 0.064087 | -0.086975 | -0.073242 | -0.050354 | -0.041199 | -0.12817 | 0.14191 | 0.032043 | -120.9869 | 0.23804 | 0.27008 | 0.23804 | -121.0052 | 0.15564 | 0.068664 | -121.0831 | 0.1648 | 0.10986 | 0.041199 | -121.0602 | 0.21973 | 0.20142 | 0.25635 | -121.1746 | 0.1236 | 0.14648 | 0.26093 | -121.138
1523.0625 | 121.1288 | -0.19684 | 121.019 | 0.0067138 | 0.011771 | 0.0023029 | 0.0037577 | 0.05721 | -0.0047765 | -0.0052551 | -0.00083936 | -0.0043494 | -0.033126 | 0.038794 | 0.0055349 | 0.005206 | -0.068665 | -0.045776 | -0.004578 | 0.027466 | 0.036621 | -0.022888 | -0.16937 | -0.068665 | 0.009155 | -0.10071 | -0.045776 | -0.059509 | -0.059509 | -0.11902 | 0.17395 | 0.027465 | -120.9824 | 0.15106 | 0.2243 | 0.19684 | -121.0876 | 0.13733 | 0.077819 | -121.0648 | 0.12817 | 0.09613 | 0.018311 | -121.0785 | 0.23346 | 0.12817 | 0.19226 | -121.1884 | 0.15106 | 0.13733 | 0.20599 | -121.138
1524.7969 | 121.138 | -0.16022 | 121.019 | -0.00091566 | 0.01583 | 0.0012347 | 0.0086709 | 0.058919 | 0.0016321 | -0.0044007 | 0.0067901 | -0.0005042 | -0.031417 | 0.041998 | 0.0031849 | 0.0015744 | -0.07782 | -0.10529 | -0.073242 | -0.004578 | 0.086975 | -0.050354 | -0.1831 | -0.12817 | -0.091553 | -0.20142 | -0.027466 | -0.009155 | -0.068665 | -0.16937 | 0.10986 | -0.022888 | -120.932 | 0.054931 | 0.15564 | 0.17853 | -121.0968 | 0.091552 | -0.009156 | -121.0464 | 0.032043 | -0.041199 | -0.032043 | -121.0281 | 0.24719 | 0.082397 | 0.086975 | -121.2021 | 0.13275 | 0.15106 | 0.068664 | -121.1884
1526.5469 | 121.1517 | -0.18768 | 121.019 | 0.0067138 | 0.010489 | 0.0046527 | 0.0071757 | 0.053579 | -0.0071265 | -0.0039733 | -0.00083936 | -0.0034948 | -0.03099 | 0.041144 | 0.0027577 | 0.0058468 | 0.004578 | 0.036621 | 0.045776 | 0.073242 | 0.018311 | -0.022888 | -0.15106 | -0.036621 | 0.068665 | -0.036621 | -0.068665 | -0.059509 | -0.027466 | -0.10529 | 0.16479 | 0.036621 | -121.0007 | 0.2243 | 0.26092 | 0.2243 | -121.0144 | 0.16022 | 0.082397 | -121.0876 | 0.15106 | 0.15106 | 0.068665 | -121.0785 | 0.20599 | 0.19226 | 0.23346 | -121.17 | 0.11902 | 0.12817 | 0.25635 | -121.1243
1528.2344 | 121.1975 | -0.13733 | 121.0098 | -0.00091566 | 0.01882 | 0.00038029 | 0.0041849 | 0.054647 | 0.0014185 | -0.00034172 | -0.0084684 | 0.0031274 | -0.031845 | 0.041571 | 0.0066029 | 0.0030698 | 0.009155 | -0.036621 | -0.022888 | 0.022888 | 0.050354 | -0.036621 | -0.17853 | -0.07782 | -0.036621 | -0.1831 | -0.027466 | -0.032043 | -0.064087 | -0.14648 | 0.10071 | -0.041199 | -120.9595 | 0.10071 | 0.16022 | 0.20142 | -121.0007 | 0.073242 | -0.009155 | -121.0373 | 0.059509 | -0.045776 | -0.036621 | -121.0419 | 0.18768 | 0.14648 | 0.11444 | -121.1884 | 0.10986 | 0.10529 | 0.10071 | -121.1563
1529.9844 | 121.2296 | -0.13733 | 121.0098 | -0.00091566 | 0.017325 | 0.0029437 | 0.0031167 | 0.056356 | -7.6908e-05 | -0.0011963 | -0.00083936 | 0.0001368 | -0.029068 | 0.04093 | 0.0059621 | 0.0026426 | -0.050354 | -0.054932 | -0.045776 | 0.032043 | 0.054932 | -0.050354 | -0.19226 | -0.059509 | -0.004578 | -0.15564 | -0.032043 | -0.032043 | -0.054932 | -0.14648 | 0.086975 | -0.054932 | -120.9549 | 0.082397 | 0.16937 | 0.2243 | -121.0602 | 0.082397 | -0.009155 | -121.0419 | 0.07782 | -0.018311 | -0.009156 | -121.0419 | 0.19226 | 0.086975 | 0.091553 | -121.2021 | 0.10529 | 0.10529 | 0.13275 | -121.1563
1531.7344 | 121.2524 | -0.14648 | 121.0327 | -0.00091566 | 0.014975 | 0.0023029 | 0.0050393 | 0.054647 | -0.0032813 | -0.0026917 | -0.0084684 | -0.0009314 | -0.029708 | 0.040503 | 0.0059621 | 0.0056332 | 0.004578 | -0.004578 | 0.027466 | 0.064087 | 0.032043 | -0.027466 | -0.14648 | -0.013733 | 0.022888 | -0.086975 | -0.07782 | -0.064087 | -0.022888 | -0.11444 | 0.11902 | 0 | -121.0007 | 0.14191 | 0.21057 | 0.21057 | -121.0281 | 0.1236 | 0.032043 | -121.1105 | 0.13275 | 0.059509 | 0.027466 | -121.0968 | 0.17853 | 0.15106 | 0.17395 | -121.1792 | 0.068664 | 0.082397 | 0.16937 | -121.1472
1533.4375 | 121.2982 | -0.1236 | 121.051 | -0.0085447 | 0.011984 | 0.0027301 | 0.0024759 | 0.053792 | -0.0037085 | -0.0050415 | -0.0084684 | -0.0039222 | -0.032913 | 0.03858 | 0.0068165 | 0.0060604 | 0.013733 | 0.032043 | 0.045776 | 0.086975 | 0.022888 | 0 | -0.12817 | -0.018311 | 0.054932 | -0.073242 | -0.091553 | -0.050354 | -0.013733 | -0.091553 | 0.1236 | -0.004578 | -121.0281 | 0.15564 | 0.21057 | 0.21515 | -121.0373 | 0.10986 | 0.032043 | -121.1426 | 0.10528 | 0.050354 | 0.018311 | -121.1014 | 0.14648 | 0.13733 | 0.16937 | -121.1792 | 0.032043 | 0.073242 | 0.17853 | -121.1426
1535.1406 | 121.1014 | -0.14191 | 121.0831 | -0.00091566 | 0.015189 | 0.0025165 | 0.0046121 | 0.053152 | -0.0037085 | -0.0016235 | -0.0084684 | -0.0017858 | -0.028427 | 0.039435 | 0.0053211 | 0.0030698 | 0.022888 | 0.045776 | 0.07782 | 0.07782 | 0.009155 | -0.013733 | -0.13275 | -0.013733 | 0.050354 | -0.086975 | -0.054932 | -0.07782 | -0.022888 | -0.11444 | 0.12817 | 0.009156 | -121.0739 | 0.18768 | 0.21973 | 0.21057 | -121.0602 | 0.11902 | 0.027466 | -121.138 | 0.12817 | 0.054932 | 0.027466 | -121.1609 | 0.15106 | 0.16479 | 0.21973 | -121.2158 | 0.086975 | 0.064087 | 0.19226 | -121.1975
1536.8906 | 121.3028 | -0.15106 | 121.0602 | 0.0067138 | 0.014975 | 0.0023029 | 0.0043985 | 0.05486 | -0.00029051 | -0.0033325 | -0.00083936 | -0.0017858 | -0.032486 | 0.04093 | 0.0051075 | 0.0039242 | -0.041199 | -0.054932 | -0.022888 | 0.018311 | 0.050354 | -0.018311 | -0.17395 | -0.036621 | -0.004578 | -0.1236 | -0.068665 | -0.054932 | -0.036621 | -0.12817 | 0.13275 | -0.022888 | -121.0098 | 0.09613 | 0.16937 | 0.19226 | -121.1014 | 0.11444 | 0.022888 | -121.1288 | 0.11444 | 0.027466 | 0.004578 | -121.1151 | 0.20142 | 0.10986 | 0.12817 | -121.2341 | 0.082397 | 0.09613 | 0.14648 | -121.1884
1538.6406 | 121.2982 | -0.14648 | 121.0831 | -0.0085447 | 0.016257 | 0.0014483 | 0.0067483 | 0.054433 | -0.00029051 | -0.0026917 | -0.00083936 | 0.0007776 | -0.031845 | 0.040503 | 0.0040395 | 0.0024288 | -0.036621 | -0.050354 | -0.022888 | 0.022888 | 0.064087 | -0.068665 | -0.17853 | -0.054932 | -0.004578 | -0.16479 | -0.022888 | -0.032043 | -0.059509 | -0.13733 | 0.077819 | -0.032044 | -121.019 | 0.09613 | 0.16937 | 0.20142 | -121.1197 | 0.086975 | 0.009155 | -121.106 | 0.091552 | -0.018311 | -0.027466 | -121.1151 | 0.21057 | 0.10986 | 0.1236 | -121.2616 | 0.1236 | 0.11444 | 0.14191 | -121.2204
1540.3281 | 121.1655 | -0.12817 | 121.1014 | -0.023804 | 0.010275 | 0.0029437 | 0.0052531 | 0.051443 | -0.0054175 | -0.0039733 | -0.00083936 | -0.0037086 | -0.032699 | 0.039862 | -1.9327e-05 | 0.0058468 | -0.054932 | -0.027466 | 0.022888 | 0.041199 | 0.027466 | 0.018311 | -0.10529 | -0.073242 | 0 | -0.1236 | -0.045776 | -0.050354 | 0.013733 | -0.07782 | 0.14649 | 0.022888 | -121.0739 | 0.10071 | 0.16937 | 0.14649 | -121.1563 | 0.14191 | 0.050354 | -121.1472 | 0.054932 | 0.004578 | -0.045776 | -121.1517 | 0.15564 | 0.073242 | 0.15106 | -121.2067 | 0.082398 | 0.07782 | 0.12817 | -121.1792
1542.0156 | 121.3028 | -0.16022 | 121.1014 | -0.0085447 | 0.014548 | -0.00047431 | 0.0039713 | 0.052297 | -7.6908e-05 | -0.0037597 | -0.016098 | -7.6996e-05 | -0.029281 | 0.043066 | 0.0066029 | 0.003497 | -0.073242 | -0.1236 | -0.09613 | -0.018311 | 0.073242 | -0.082397 | -0.18768 | -0.1236 | -0.10529 | -0.20142 | -0.032043 | -0.013733 | -0.054932 | -0.12817 | 0.07782 | -0.027466 | -121.0281 | 0.036621 | 0.14191 | 0.16937 | -121.1746 | 0.10528 | 0.032043 | -121.1334 | 0.036621 | -0.041199 | -0.073242 | -121.1151 | 0.23346 | 0.086975 | 0.064087 | -121.2891 | 0.12817 | 0.14648 | 0.054931 | -121.2296
1543.7812 | 121.2936 | -0.14191 | 121.0693 | -0.0085447 | 0.016684 | 0.0012347 | 0.00055326 | 0.053579 | 0.0020593 | -0.0022643 | -0.00083936 | -7.6996e-05 | -0.031631 | 0.03858 | 0.0068165 | 0.0028562 | -0.018311 | -0.027466 | -0.045776 | 0.022888 | 0.050354 | -0.032043 | -0.20142 | -0.054932 | -0.004578 | -0.16479 | -0.032043 | -0.036621 | -0.050354 | -0.14648 | 0.10986 | -0.059509 | -121.019 | 0.11444 | 0.16479 | 0.2243 | -121.0876 | 0.091553 | -0.004577 | -121.1014 | 0.086975 | -0.022888 | -0.018311 | -121.106 | 0.19226 | 0.1236 | 0.096131 | -121.2708 | 0.10986 | 0.10529 | 0.13733 | -121.2158
1545.4688 | 121.1838 | -0.20599 | 121.1288 | -0.0085447 | 0.015616 | 0.0029437 | 0.0073893 | 0.055288 | -0.0064855 | -0.0033325 | 0.0067901 | -0.0022132 | -0.031631 | 0.039007 | 0.00040787 | 0.005206 | -0.032043 | -0.013733 | 0 | 0.041199 | 0.032043 | -0.059509 | -0.1831 | -0.13733 | -0.018311 | -0.17395 | -0.027466 | -0.022888 | -0.07782 | -0.16479 | 0.14649 | 0.022889 | -121.0968 | 0.19226 | 0.24719 | 0.2243 | -121.1609 | 0.12817 | 0.041199 | -121.1563 | 0.068665 | 0.032044 | -0.009155 | -121.1517 | 0.23804 | 0.17395 | 0.20599 | -121.3119 | 0.17853 | 0.18311 | 0.18768 | -121.2936
1547.2188 | 121.2936 | -0.16479 | 121.1197 | -0.00091566 | 0.012625 | 0.00016669 | 0.0043985 | 0.05486 | -0.00093131 | -0.0033325 | -0.0084684 | 0.0012048 | -0.030563 | 0.040503 | 0.0072437 | 0.0060604 | -0.018311 | -0.032043 | -0.027466 | 0.032043 | 0.064087 | -0.045776 | -0.19226 | -0.086975 | -0.027466 | -0.16937 | -0.036621 | -0.036621 | -0.068665 | -0.14648 | 0.11902 | -0.027466 | -121.0556 | 0.13275 | 0.19684 | 0.2243 | -121.138 | 0.09613 | 0.018311 | -121.1563 | 0.07782 | -0.004578 | -0.022889 | -121.1563 | 0.22888 | 0.14648 | 0.13733 | -121.312 | 0.12817 | 0.12817 | 0.13733 | -121.2662
1548.9688 | 121.2296 | -0.1831 | 121.106 | -0.00091566 | 0.015189 | 0.0057209 | 0.0061075 | 0.05422 | -0.0026403 | -0.0046143 | -0.00083936 | -0.0007178 | -0.030349 | 0.041357 | 0.0027577 | 0.0067014 | -0.086975 | -0.07782 | -0.068665 | -0.018311 | 0.073242 | -0.086975 | -0.20142 | -0.17395 | -0.064087 | -0.19226 | -0.004578 | -0.013733 | -0.07782 | -0.16937 | 0.09613 | -0.018311 | -121.0327 | 0.10528 | 0.16479 | 0.18311 | -121.1929 | 0.10528 | 0.013732 | -121.1105 | 0.009155 | -0.009156 | -0.022888 | -121.1197 | 0.25635 | 0.09613 | 0.11444 | -121.3074 | 0.17853 | 0.16937 | 0.11902 | -121.2753
1550.6406 | 121.2982 | -0.16479 | 121.106 | -0.00091566 | 0.014121 | -0.00090151 | 0.0033305 | 0.057638 | 0.00099129 | -0.0035461 | -0.00083936 | -0.0007178 | -0.031417 | 0.040716 | 0.0046803 | 0.0037106 | -0.09613 | -0.13275 | -0.086975 | -0.013733 | 0.050354 | -0.050354 | -0.1831 | -0.14191 | -0.10071 | -0.24261 | -0.032043 | -0.027466 | -0.073242 | -0.14648 | 0.11444 | -0.01831 | -121.0556 | 0.032044 | 0.15106 | 0.16937 | -121.2021 | 0.091553 | 0.018311 | -121.138 | 0.022888 | -0.07782 | -0.096131 | -121.1334 | 0.21515 | 0.068665 | 0.07782 | -121.2891 | 0.13275 | 0.13733 | 0.064087 | -121.2524
1552.3906 | 121.3257 | -0.16022 | 121.1243 | -0.00091566 | 0.012198 | 0.0023029 | 0.0041849 | 0.054647 | -0.0034949 | -0.0026917 | -0.00083936 | -0.0024268 | -0.031417 | 0.038153 | 0.0053211 | 0.0075558 | 0.013733 | 0.022888 | 0.054932 | 0.059509 | 0.022888 | -0.018311 | -0.13733 | -0.009155 | 0.041199 | -0.064087 | -0.07782 | -0.073242 | -0.022888 | -0.10986 | 0.14191 | 0.022888 | -121.1014 | 0.1831 | 0.21973 | 0.19684 | -121.1105 | 0.13733 | 0.050354 | -121.2021 | 0.15106 | 0.09613 | 0.045776 | -121.1975 | 0.1831 | 0.17395 | 0.21515 | -121.2616 | 0.082397 | 0.086975 | 0.20142 | -121.2341
1554.1562 | 121.2204 | -0.19684 | 121.1472 | -0.00091566 | 0.014975 | 0.0014483 | 0.0082437 | 0.051656 | -0.0058447 | -0.0041869 | -0.0084684 | -0.002854 | -0.03099 | 0.037726 | 0.0031849 | 0.0060604 | -0.050354 | -0.022888 | -0.009155 | 0.022888 | 0.050354 | -0.050354 | -0.15564 | -0.14191 | -0.041199 | -0.16479 | -0.032043 | -0.022888 | -0.059509 | -0.15564 | 0.14648 | 0.041198 | -121.0968 | 0.17395 | 0.21973 | 0.17853 | -121.1975 | 0.13733 | 0.041198 | -121.1792 | 0.054931 | 0.032043 | -0.009155 | -121.17 | 0.24719 | 0.14648 | 0.18768 | -121.3028 | 0.1648 | 0.17395 | 0.15564 | -121.3028
1555.9062 | 121.2479 | -0.1831 | 121.1884 | -0.00091566 | 0.0060028 | 0.0029437 | 0.0020487 | 0.052724 | -0.0075537 | -0.0031189 | -0.00083936 | -0.0032812 | -0.031417 | 0.040503 | 0.0023305 | 0.0071286 | -0.027466 | -0.004578 | 0.032043 | 0.032043 | 0.041199 | -0.009155 | -0.15106 | -0.09613 | -0.004578 | -0.11444 | -0.041199 | -0.032043 | -0.027466 | -0.10071 | 0.17395 | 0.032043 | -121.1472 | 0.17853 | 0.21515 | 0.18311 | -121.2158 | 0.15564 | 0.082397 | -121.2296 | 0.086975 | 0.068664 | -0.013733 | -121.2204 | 0.2243 | 0.15564 | 0.21515 | -121.3394 | 0.14191 | 0.15106 | 0.17853 | -121.2891
1557.5938 | 121.3394 | -0.14648 | 121.138 | -0.016174 | 0.017752 | 0.0023029 | 0.0041849 | 0.056142 | 0.0018457 | -0.0041869 | 0.0067901 | 0.0007776 | -0.030777 | 0.041785 | 0.0068165 | 0.0022152 | -0.004578 | -0.059509 | -0.013733 | 0.018311 | 0.054932 | -0.045776 | -0.16479 | -0.07782 | -0.045776 | -0.18768 | -0.022888 | -0.018311 | -0.059509 | -0.14648 | 0.10071 | -0.018311 | -121.0831 | 0.086975 | 0.16479 | 0.18311 | -121.1426 | 0.086975 | 0 | -121.1609 | 0.068664 | -0.041199 | -0.041199 | -121.1563 | 0.20142 | 0.14191 | 0.13275 | -121.3028 | 0.1236 | 0.12817 | 0.10071 | -121.2845
1559.3594 | 121.2936 | -0.15564 | 121.1929 | -0.0085447 | 0.01348 | 0.0048663 | 0.0065347 | 0.053792 | -0.0079809 | -0.0054687 | -0.00083936 | -0.004563 | -0.029922 | 0.038367 | 0.0019033 | 0.0049924 | 0.041199 | 0.068665 | 0.07782 | 0.07782 | 0.036621 | -0.018311 | -0.13275 | -0.022888 | 0.07782 | -0.054932 | -0.050354 | -0.050354 | -0.018311 | -0.11444 | 0.13733 | 0.022889 | -121.1563 | 0.22431 | 0.23346 | 0.21057 | -121.1517 | 0.13733 | 0.041199 | -121.2433 | 0.13275 | 0.10071 | 0.059509 | -121.2433 | 0.19226 | 0.19684 | 0.23346 | -121.3257 | 0.10529 | 0.10529 | 0.23346 | -121.3074
1561.0625 | 121.2845 | -0.17853 | 121.2158 | -0.00091566 | 0.014548 | 0.0035847 | 0.0071757 | 0.052724 | -0.0052039 | -0.0048279 | -0.016098 | -0.006272 | -0.030777 | 0.039221 | 0.0023305 | 0.0049924 | -0.036621 | -0.018311 | 0.013733 | 0.045776 | 0.041199 | 0 | -0.14191 | -0.073242 | -0.004578 | -0.1236 | -0.059509 | -0.045776 | -0.022888 | -0.11444 | 0.17853 | 0.036621 | -121.1746 | 0.16022 | 0.2243 | 0.18768 | -121.2524 | 0.15564 | 0.064087 | -121.2753 | 0.10529 | 0.054932 | -0.009155 | -121.2616 | 0.21973 | 0.14191 | 0.19226 | -121.3577 | 0.11902 | 0.13275 | 0.17395 | -121.3303
1562.8125 | 121.3943 | -0.10986 | 121.1517 | -0.00091566 | 0.019888 | 0.00059389 | 0.0050393 | 0.053365 | 0.0031275 | -0.0058959 | -0.016098 | 0.001632 | -0.032272 | 0.043921 | 0.0057485 | 0.001788 | -0.013733 | -0.045776 | -0.027466 | 0.041199 | 0.091553 | -0.059509 | -0.17853 | -0.045776 | 0.009155 | -0.15564 | -0.022888 | -0.018311 | -0.054932 | -0.14648 | 0.050354 | -0.068665 | -121.0602 | 0.064087 | 0.15106 | 0.21973 | -121.1655 | 0.054931 | -0.036621 | -121.1746 | 0.064087 | -0.045777 | -0.009156 | -121.17 | 0.20142 | 0.09613 | 0.082397 | -121.3303 | 0.086975 | 0.091552 | 0.11902 | -121.2982
1564.5625 | 121.3806 | -0.15106 | 121.1838 | -0.0085447 | 0.015616 | 0.00059389 | 0.0031167 | 0.055074 | -0.0032813 | -0.0033325 | -0.016098 | -0.0034948 | -0.029922 | 0.042212 | 0.0051075 | 0.0047788 | 0.032043 | 0.027466 | 0.059509 | 0.082397 | 0.013733 | -0.004578 | -0.13275 | 0 | 0.041199 | -0.068665 | -0.073242 | -0.064087 | -0.018311 | -0.10071 | 0.14648 | 0.018311 | -121.17 | 0.17853 | 0.23346 | 0.21515 | -121.1517 | 0.13275 | 0.050354 | -121.257 | 0.15106 | 0.082397 | 0.032043 | -121.2479 | 0.16479 | 0.18311 | 0.21057 | -121.3165 | 0.07782 | 0.086975 | 0.19226 | -121.2845
1566.3125 | 121.3669 | -0.15564 | 121.1838 | -0.023804 | 0.016043 | 0.00038029 | 0.0022623 | 0.054647 | 0.0033411 | -0.0037597 | -0.0084684 | -0.0005042 | -0.030349 | 0.040503 | 0.0076711 | 0.0039242 | 0.018311 | -0.036621 | -0.004578 | 0.032043 | 0.064087 | -0.041199 | -0.16479 | -0.036621 | -0.009155 | -0.14648 | -0.041199 | 0 | -0.032043 | -0.11902 | 0.11444 | -0.009155 | -121.1197 | 0.11902 | 0.18768 | 0.19684 | -121.1655 | 0.1236 | 0.036621 | -121.225 | 0.11902 | 0.009156 | -0.027465 | -121.1838 | 0.21973 | 0.17395 | 0.15106 | -121.3486 | 0.11444 | 0.15564 | 0.14649 | -121.3028
1568 | 121.4172 | -0.13275 | 121.1929 | 0.0067138 | 0.014334 | 0.0037983 | 0.0031167 | 0.055501 | -0.00029051 | -0.0020507 | -0.0084684 | 0.0003504 | -0.032486 | 0.041998 | 0.0046803 | 0.0030698 | -0.073242 | -0.068665 | -0.050354 | 0.022888 | 0.054932 | -0.073242 | -0.1831 | -0.068665 | -0.018311 | -0.16479 | -0.022888 | -0.004578 | -0.064087 | -0.14648 | 0.059509 | -0.050354 | -121.138 | 0.064086 | 0.15564 | 0.20599 | -121.2662 | 0.068664 | -0.013733 | -121.2158 | 0.064086 | -0.032044 | -0.018311 | -121.1975 | 0.18768 | 0.059509 | 0.082397 | -121.376 | 0.10986 | 0.12817 | 0.11444 | -121.3394
1569.75 | 121.312 | -0.19226 | 121.2387 | 0.0067138 | 0.0094208 | 0.0035847 | 0.0043985 | 0.054006 | -0.0069129 | -0.0031189 | -0.00083936 | -0.002854 | -0.031417 | 0.038794 | 0.0031849 | 0.0081968 | 0.013733 | 0.050354 | 0.054932 | 0.068665 | 0.032043 | -0.022888 | -0.14648 | -0.041199 | 0.036621 | -0.082397 | -0.054932 | -0.068665 | -0.022888 | -0.10986 | 0.16937 | 0.045777 | -121.2067 | 0.24261 | 0.26093 | 0.21515 | -121.225 | 0.16937 | 0.082398 | -121.2936 | 0.15106 | 0.10986 | 0.027466 | -121.3074 | 0.2243 | 0.20599 | 0.24719 | -121.3852 | 0.13733 | 0.1236 | 0.22888 | -121.3486
1571.5 | 121.4355 | -0.15106 | 121.2296 | -0.0085447 | 0.010275 | 0.00038029 | 0.0061075 | 0.053365 | -0.0024267 | -0.0018371 | -0.00083936 | -0.0013586 | -0.03099 | 0.040716 | 0.0027577 | 0.0043516 | 0.032043 | 0.022888 | 0.036621 | 0.082397 | 0.018311 | -0.004578 | -0.14191 | 0.004578 | 0.041199 | -0.07782 | -0.07782 | -0.054932 | -0.018311 | -0.10986 | 0.14648 | 0.009155 | -121.2112 | 0.17395 | 0.23346 | 0.2243 | -121.1975 | 0.13275 | 0.041199 | -121.3074 | 0.15564 | 0.073242 | 0.032043 | -121.2845 | 0.16937 | 0.18311 | 0.18768 | -121.3715 | 0.073242 | 0.09613 | 0.19226 | -121.3394
1573.1875 | 121.3348 | -0.1831 | 121.257 | -0.00091566 | 0.014975 | 0.0023029 | 0.0090983 | 0.053579 | -0.0056311 | -0.0063233 | 0.0067901 | -0.0019996 | -0.031417 | 0.039435 | 0.00083507 | 0.0039242 | 0.036621 | 0.059509 | 0.073242 | 0.07782 | 0.032043 | -0.027466 | -0.15106 | -0.022888 | 0.10529 | -0.059509 | -0.068665 | -0.050354 | -0.022888 | -0.09613 | 0.15564 | 0.032043 | -121.225 | 0.24261 | 0.26092 | 0.22888 | -121.2204 | 0.16022 | 0.086975 | -121.3257 | 0.16022 | 0.1236 | 0.036621 | -121.3074 | 0.21515 | 0.21973 | 0.25635 | -121.4081 | 0.11444 | 0.13275 | 0.28839 | -121.3531
1574.9375 | 120.9 | -0.16479 | 120.8725 | -0.016174 | 0.010275 | 0.0048663 | 0.0058939 | 0.052724 | -0.0030677 | -0.0052551 | -0.00083936 | -0.0058448 | -0.033981 | 0.038367 | 0.0055349 | 0.0039242 | 0.022888 | 0.050354 | 0.07782 | 0.09613 | 0.022888 | -0.004578 | -0.15106 | -0.013733 | 0.082397 | -0.054932 | -0.064087 | -0.050354 | -0.009155 | -0.10529 | 0.16022 | 0.013733 | -120.8496 | 0.21515 | 0.26092 | 0.24719 | -120.8496 | 0.15564 | 0.059509 | -120.9366 | 0.15106 | 0.10986 | 0.050354 | -120.9229 | 0.18768 | 0.18768 | 0.24261 | -121.0236 | 0.10071 | 0.11444 | 0.24719 | -120.9778
1576.625 | 121.2067 | -0.15106 | 121.0648 | -0.00091566 | 0.014975 | 0.0033709 | 0.0022623 | 0.055929 | 0.0031275 | -0.0020507 | -0.00083936 | 0.0014184 | -0.029495 | 0.039648 | 0.0091665 | 0.005206 | -0.059509 | -0.12817 | -0.082397 | -0.009155 | 0.086975 | -0.054932 | -0.17853 | -0.11444 | -0.09613 | -0.23804 | -0.009155 | -0.013733 | -0.054932 | -0.13275 | 0.09613 | -0.027466 | -120.9778 | 0.022888 | 0.14191 | 0.16937 | -121.1243 | 0.09613 | 0.018311 | -121.0739 | 0.036621 | -0.086975 | -0.10529 | -121.0785 | 0.23804 | 0.091553 | 0.068665 | -121.2433 | 0.14191 | 0.13733 | 0.054932 | -121.1975
1578.3906 | 121.312 | -0.15564 | 121.106 | -0.00091566 | 0.015189 | 0.0023029 | 0.0041849 | 0.053579 | -0.0028539 | -0.0029053 | -0.00083936 | -0.0002906 | -0.03099 | 0.041571 | 0.0048939 | 0.0062742 | -0.050354 | -0.10529 | -0.082397 | -0.009155 | 0.091553 | -0.050354 | -0.1831 | -0.1236 | -0.091553 | -0.21973 | -0.009155 | -0.009155 | -0.064087 | -0.13733 | 0.10529 | -0.027465 | -121.0144 | 0.050354 | 0.14649 | 0.17395 | -121.1563 | 0.091553 | 0.018311 | -121.1151 | 0.032044 | -0.064087 | -0.082398 | -121.1151 | 0.24719 | 0.10529 | 0.073243 | -121.2891 | 0.14649 | 0.14649 | 0.064087 | -121.2433
1580.0781 | 121.3074 | -0.13733 | 121.1334 | -0.0085447 | 0.015189 | 0.0025165 | 0.0052531 | 0.056356 | 0.0014185 | -0.0033325 | -0.0084684 | 0.0009912 | -0.02864 | 0.041998 | 0.0057485 | 0.0060604 | -0.004578 | -0.059509 | -0.036621 | 0.013733 | 0.073242 | -0.036621 | -0.16937 | -0.091553 | -0.059509 | -0.19684 | -0.009155 | -0.013733 | -0.054932 | -0.15106 | 0.10071 | -0.032044 | -121.0602 | 0.07782 | 0.15106 | 0.18311 | -121.138 | 0.082397 | -0.013733 | -121.1426 | 0.045776 | -0.059509 | -0.045776 | -121.1472 | 0.21057 | 0.13275 | 0.10071 | -121.3028 | 0.12817 | 0.1236 | 0.07782 | -121.2845
1581.8281 | 121.3257 | -0.14191 | 121.1929 | -0.00091566 | 0.01647 | 0.0029437 | 0.0078165 | 0.054433 | -0.0032813 | -0.0044007 | -0.00083936 | -0.0009314 | -0.029495 | 0.039862 | 0.0012623 | 0.005206 | -0.068665 | -0.10986 | -0.082397 | -0.013733 | 0.068665 | -0.050354 | -0.20599 | -0.14191 | -0.059509 | -0.19684 | 0.004578 | 0.004578 | -0.059509 | -0.13275 | 0.091553 | -0.064087 | -121.1243 | 0.032044 | 0.12817 | 0.19226 | -121.2616 | 0.082398 | 0.009156 | -121.1884 | 0 | -0.054931 | -0.064087 | -121.1884 | 0.21057 | 0.073242 | 0.05951 | -121.3989 | 0.14649 | 0.14649 | 0.082398 | -121.3257
1583.5156 | 121.3531 | -0.15106 | 121.2021 | -0.0085447 | 0.016043 | 0.0014483 | 0.0067483 | 0.053792 | -0.00071771 | -0.0031189 | -0.00083936 | 0.0014184 | -0.02864 | 0.041785 | 0.0042531 | 0.0032834 | -0.073242 | -0.12817 | -0.07782 | -0.009155 | 0.059509 | -0.045776 | -0.19226 | -0.1236 | -0.09613 | -0.22888 | -0.009155 | 0.004578 | -0.036621 | -0.16022 | 0.10529 | -0.041199 | -121.1426 | 0.022888 | 0.14191 | 0.18311 | -121.2753 | 0.11444 | -0.009155 | -121.2112 | 0.027466 | -0.07782 | -0.068665 | -121.1975 | 0.21057 | 0.07782 | 0.073242 | -121.3943 | 0.14191 | 0.15564 | 0.054932 | -121.3623
1585.2656 | 121.3028 | -0.16479 | 121.2753 | -0.00091566 | 0.013266 | 0.0016619 | 0.0052531 | 0.053792 | -0.0060583 | -0.0048279 | 0.0067901 | -0.0049902 | -0.030563 | 0.04093 | 0.00019427 | 0.0056332 | 0.009155 | 0.068665 | 0.07782 | 0.086975 | 0.036621 | -0.009155 | -0.12817 | -0.027466 | 0.091553 | -0.064087 | -0.054932 | -0.041199 | -0.054932 | -0.07782 | 0.15564 | 0.036621 | -121.2387 | 0.23346 | 0.25177 | 0.21515 | -121.2662 | 0.10986 | 0.086975 | -121.3303 | 0.13733 | 0.10071 | 0.013733 | -121.3165 | 0.20142 | 0.17395 | 0.24261 | -121.4035 | 0.10986 | 0.1236 | 0.25635 | -121.3531
1587.0156 | 121.4401 | -0.12817 | 121.2341 | -0.0085447 | 0.016257 | 0.0025165 | 0.0048257 | 0.054006 | 0.00099129 | -0.0046143 | -0.0084684 | 0.000564 | -0.031204 | 0.040716 | 0.0055349 | 0.0030698 | 0 | -0.036621 | -0.004578 | 0.036621 | 0.064087 | -0.036621 | -0.17395 | -0.054932 | 0.004578 | -0.15106 | -0.036621 | -0.004578 | -0.045776 | -0.14191 | 0.091553 | -0.045776 | -121.17 | 0.091553 | 0.1648 | 0.21057 | -121.2341 | 0.082398 | -0.013733 | -121.2708 | 0.073242 | -0.022888 | -0.009155 | -121.2387 | 0.19226 | 0.12817 | 0.1236 | -121.4081 | 0.091553 | 0.1236 | 0.13275 | -121.376
1588.7031 | 120.5063 | -46.0876 | 74.7528 | 0.0067138 | 0.012198 | 0.0023029 | 0.0063211 | 0.055929 | -0.0064855 | -0.0033325 | -0.00083936 | -0.0034948 | -0.031631 | 0.039862 | 0.0025441 | 0.0064878 | 0.054932 | 0.091553 | 0.11902 | 0.12817 | 0.073242 | 0.009155 | -0.07782 | 0.004578 | 0.14191 | -0.032043 | 0 | -0.013733 | 0.027466 | -0.059509 | 46.0968 | 46.0098 | -74.6796 | 46.1792 | 46.2158 | 0.20599 | -74.6979 | 46.1151 | 46.0281 | -74.7528 | 46.0922 | 46.0556 | 0.027466 | -74.7665 | 46.1609 | 46.1426 | 46.2067 | -74.8306 | 46.0876 | 46.0739 | 46.2296 | -74.8123
1590.4688 | 121.1975 | -45.7718 | 75.4074 | 0.0067138 | 0.013693 | 0.0018757 | 0.0071757 | 0.05422 | -0.0075537 | -0.0044007 | -0.00083936 | -0.0041358 | -0.03099 | 0.039221 | 0.0029713 | 0.0064878 | 0.07782 | 0.11444 | 0.12817 | 0.13275 | 0.082397 | 0.027466 | -0.1236 | 0.032043 | 0.14648 | 0 | -0.013733 | -0.004578 | 0.018311 | -0.068665 | 45.7993 | 45.6482 | -75.325 | 45.8862 | 45.9045 | 0.25635 | -75.3296 | 45.7901 | 45.7031 | -75.4211 | 45.8038 | 45.7718 | 0.068665 | -75.412 | 45.8542 | 45.8496 | 45.9 | -75.531 | 45.7581 | 45.7672 | 45.9183 | -75.4761
1592.1562 | 121.2433 | -45.6665 | 75.5493 | -0.00091566 | 0.014334 | 0.0027301 | 0.0041849 | 0.053365 | -0.0054175 | -0.0063233 | -0.00083936 | -0.0032812 | -0.032272 | 0.039221 | 0.0019033 | 0.0047788 | 0.068665 | 0.09613 | 0.12817 | 0.13275 | 0.07782 | 0.018311 | -0.091553 | 0.036621 | 0.14191 | 0 | -0.022888 | -0.013733 | 0.018311 | -0.073242 | 45.6848 | 45.575 | -75.4715 | 45.7626 | 45.7993 | 0.2243 | -75.4807 | 45.6848 | 45.5933 | -75.5722 | 45.7031 | 45.6665 | 0.073242 | -75.563 | 45.7443 | 45.7352 | 45.7947 | -75.6409 | 45.6436 | 45.6528 | 45.8084 | -75.6226
1593.9219 | 121.3669 | -45.4559 | 75.7233 | -0.0085447 | 0.019888 | 0.0010211 | 0.0071757 | 0.056356 | 0.0016321 | -0.0039733 | -0.016098 | 0.0018456 | -0.027786 | 0.042425 | 0.0040395 | -0.0003482 | 0.036621 | -0.013733 | 0.032043 | 0.10071 | 0.10986 | -0.004578 | -0.12817 | 0.009155 | 0.050354 | -0.10529 | 0.041199 | 0.013733 | 0 | -0.10529 | 45.4514 | 45.3278 | -75.6134 | 45.4422 | 45.5566 | 0.22888 | -75.6866 | 45.4559 | 45.3506 | -75.6821 | 45.4651 | 45.3506 | 0 | -75.7095 | 45.5658 | 45.4926 | 45.488 | -75.8514 | 45.4971 | 45.4697 | 45.5063 | -75.8286
1595.6094 | 121.3577 | -121.1014 | 0.20599 | -0.0085447 | 0.011771 | 0.0020893 | 0.0016215 | 0.055501 | -0.0052039 | -0.0024779 | 0.0067901 | -0.0039222 | -0.033981 | 0.041571 | 0.0066029 | 0.0056332 | 0.13733 | 0.15106 | 0.17853 | 0.18768 | 0.13275 | 0.10986 | -0.027466 | 0.091553 | 0.16022 | 0.054932 | 0.036621 | 0.045776 | 0.086975 | 0 | 121.2112 | 121.0739 | -0.073243 | 121.2524 | 121.2891 | 0.21515 | -0.068665 | 121.1884 | 121.1014 | -0.16937 | 121.1929 | 121.1563 | 0.054932 | -0.16022 | 121.2341 | 121.2387 | 121.2799 | -0.23346 | 121.138 | 121.1472 | 121.2616 | -0.20599
1597.3594 | 121.4539 | -121.0648 | 0.16022 | -0.00091566 | 0.017752 | -0.00026071 | 0.0071757 | 0.054433 | 0.0016321 | -0.0050415 | 0.0067901 | 0.001632 | -0.029495 | 0.040289 | 0.0033985 | 0.0026426 | 0.059509 | 0.018311 | 0.050354 | 0.11902 | 0.17395 | 0.050354 | -0.07782 | 0 | 0.064087 | -0.086975 | 0.09613 | 0.10986 | 0.045776 | -0.032043 | 121.1151 | 120.9869 | 0.013733 | 121.0831 | 121.1838 | 0.19684 | -0.10071 | 121.1105 | 121.0327 | -0.064087 | 121.0648 | 120.9778 | -0.054932 | -0.050354 | 121.2387 | 121.1243 | 121.1151 | -0.23804 | 121.1609 | 121.1746 | 121.1288 | -0.19226
1599.0625 | 121.4859 | -121.0831 | 0.17853 | -0.0085447 | 0.014121 | 0.0018757 | 0.0046121 | 0.052511 | -0.00050411 | -0.00055532 | -0.00083936 | -0.0007178 | -0.032058 | 0.040076 | 0.0078847 | 0.0054196 | 0.15564 | 0.12817 | 0.17853 | 0.19226 | 0.15106 | 0.086975 | -0.036621 | 0.10529 | 0.15564 | 0.036621 | 0.027466 | 0.073242 | 0.082397 | 0.027466 | 121.17 | 121.0464 | -0.027466 | 121.2112 | 121.2753 | 0.22888 | -0.022888 | 121.1655 | 121.1105 | -0.15106 | 121.1884 | 121.1197 | 0.009155 | -0.10529 | 121.2341 | 121.2387 | 121.2616 | -0.21515 | 121.1105 | 121.1563 | 121.2387 | -0.15106
1600.75 | 121.376 | -121.1334 | 0.23346 | -0.016174 | 0.017325 | 0.0035847 | 0.0073893 | 0.054647 | -0.0017859 | -0.0031189 | -0.0084684 | -0.002854 | -0.030136 | 0.03858 | 0.0016895 | 0.0049924 | 0.082397 | 0.068665 | 0.10529 | 0.13275 | 0.17853 | 0.073242 | -0.073242 | 0 | 0.07782 | -0.059509 | 0.091553 | 0.10986 | 0.032043 | -0.036621 | 121.2067 | 121.0602 | -0.054931 | 121.2021 | 121.2662 | 0.20599 | -0.15106 | 121.1655 | 121.0968 | -0.14191 | 121.1334 | 121.0739 | -0.022888 | -0.1236 | 121.312 | 121.2158 | 121.2387 | -0.3067 | 121.225 | 121.2433 | 121.2112 | -0.27008
1602.5 | 121.5225 | -121.17 | 0.18768 | -0.00091566 | 0.014548 | -4.6912e-05 | 0.0035441 | 0.053152 | -7.6908e-05 | -0.0035461 | 0.0067901 | -0.0005042 | -0.030777 | 0.041144 | 0.0057485 | 0.0047788 | 0.041199 | -0.018311 | 0.018311 | 0.10071 | 0.17395 | 0.050354 | -0.064087 | 0.004578 | 0.013733 | -0.10986 | 0.10529 | 0.091553 | 0.059509 | -0.027466 | 121.2204 | 121.106 | -0.013733 | 121.1517 | 121.2708 | 0.1648 | -0.14648 | 121.2296 | 121.1426 | -0.082397 | 121.1746 | 121.0602 | -0.082397 | -0.09613 | 121.344 | 121.2112 | 121.1884 | -0.25177 | 121.2753 | 121.2616 | 121.1838 | -0.21515
1604.25 | 121.4355 | -121.1746 | 0.19226 | -0.0085447 | 0.011557 | 0.0025165 | 0.0076029 | 0.057424 | -0.0071265 | -0.0033325 | 0.0067901 | -0.0043494 | -0.031631 | 0.041144 | 0.0025441 | 0.0058468 | 0.068665 | 0.086975 | 0.12817 | 0.15564 | 0.15564 | 0.091553 | -0.041199 | 0.059509 | 0.16022 | 0.027466 | 0.054932 | 0.086975 | 0.064087 | 0.018311 | 121.2662 | 121.1334 | -0.036621 | 121.2616 | 121.3303 | 0.19684 | -0.1236 | 121.2387 | 121.1929 | -0.13733 | 121.2341 | 121.2021 | 0.009155 | -0.10529 | 121.3303 | 121.2433 | 121.3028 | -0.23346 | 121.2296 | 121.2616 | 121.3348 | -0.17395
1606 | 121.4493 | -121.1838 | 0.20599 | 0.0067138 | 0.013907 | 0.0048663 | 0.0043985 | 0.055715 | -0.0052039 | -0.0054687 | 0.0067901 | -0.002854 | -0.033126 | 0.039862 | 0.0036123 | 0.0060604 | 0.091553 | 0.091553 | 0.13733 | 0.16479 | 0.15106 | 0.07782 | -0.045776 | 0.059509 | 0.16479 | 0.027466 | 0.059509 | 0.064087 | 0.082397 | -0.018311 | 121.2616 | 121.138 | -0.054932 | 121.2753 | 121.3486 | 0.21057 | -0.11444 | 121.2662 | 121.1655 | -0.14649 | 121.2433 | 121.2112 | 0.045777 | -0.14191 | 121.3348 | 121.2753 | 121.3211 | -0.25177 | 121.2433 | 121.2479 | 121.3486 | -0.22431
1607.6719 | 121.5317 | -121.1792 | 0.16937 | -0.00091566 | 0.016257 | 0.0012347 | 0.0063211 | 0.053365 | -7.6908e-05 | -0.0050415 | -0.00083936 | 0.0003504 | -0.030349 | 0.039648 | 0.0046803 | 0.0022152 | 0.086975 | 0.059509 | 0.07782 | 0.15106 | 0.17853 | 0.073242 | -0.082397 | 0.059509 | 0.10071 | -0.041199 | 0.07782 | 0.10071 | 0.041199 | -0.027466 | 121.2524 | 121.0968 | 0.009155 | 121.2387 | 121.3303 | 0.23346 | -0.082398 | 121.2204 | 121.1517 | -0.091553 | 121.2387 | 121.138 | -0.013733 | -0.068665 | 121.3577 | 121.2662 | 121.257 | -0.25177 | 121.257 | 121.2799 | 121.2799 | -0.19684
1609.4375 | 121.4813 | -121.2204 | 0.21057 | -0.016174 | 0.010062 | 0.0035847 | 0.0048257 | 0.054433 | -0.0084081 | -0.0054687 | 0.0067901 | -0.0058448 | -0.03099 | 0.03858 | 0.0038259 | 0.0062742 | 0.07782 | 0.10986 | 0.13275 | 0.15564 | 0.14648 | 0.082397 | -0.036621 | 0.050354 | 0.16022 | 0.036621 | 0.059509 | 0.068665 | 0.082397 | 0 | 121.3028 | 121.1838 | -0.064087 | 121.3303 | 121.376 | 0.19226 | -0.13275 | 121.3028 | 121.2204 | -0.15106 | 121.2708 | 121.257 | 0.036621 | -0.14191 | 121.3669 | 121.2982 | 121.3531 | -0.24719 | 121.2799 | 121.2891 | 121.3806 | -0.21057
1611.1875 | 121.5591 | -121.2341 | 0.16022 | 0.0067138 | 0.016043 | 0.0027301 | 0.0037577 | 0.053579 | 0.00035029 | -0.0031189 | 0.0067901 | 0.0012048 | -0.030777 | 0.042425 | 0.0057485 | 0.0028562 | 0.073242 | 0.027466 | 0.068665 | 0.12817 | 0.16479 | 0.068665 | -0.07782 | 0.041199 | 0.07782 | -0.054932 | 0.10071 | 0.086975 | 0.050354 | -0.022888 | 121.3028 | 121.1563 | 0.004578 | 121.2616 | 121.3623 | 0.20599 | -0.086975 | 121.2845 | 121.2112 | -0.059509 | 121.2753 | 121.1792 | -0.032044 | -0.073242 | 121.3989 | 121.3074 | 121.3028 | -0.23804 | 121.3348 | 121.3211 | 121.312 | -0.1831
1612.9375 | 121.4584 | -121.2662 | 0.20599 | -0.0085447 | 0.016898 | 0.0033709 | 0.0071757 | 0.056356 | -0.0034949 | -0.0056823 | -0.016098 | -0.0002906 | -0.030563 | 0.039007 | 0.0040395 | 0.0060604 | 0.032043 | 0.041199 | 0.054932 | 0.10529 | 0.16479 | 0.045776 | -0.073242 | -0.027466 | 0.068665 | -0.073242 | 0.091553 | 0.09613 | 0.050354 | -0.054932 | 121.312 | 121.1929 | -0.041199 | 121.3074 | 121.3715 | 0.17853 | -0.17395 | 121.3165 | 121.2112 | -0.11444 | 121.2387 | 121.1929 | -0.01831 | -0.10986 | 121.431 | 121.2982 | 121.3211 | -0.27924 | 121.3577 | 121.3623 | 121.3348 | -0.26093
1614.625 | 121.4584 | -121.2433 | 0.21057 | -0.0085447 | 0.016898 | 0.0031573 | 0.0071757 | 0.056142 | -0.0032813 | -0.0048279 | -0.0084684 | -0.0034948 | -0.031417 | 0.040076 | 0.0029713 | 0.0056332 | 0.14648 | 0.14191 | 0.1831 | 0.18768 | 0.14191 | 0.086975 | -0.032043 | 0.064087 | 0.17395 | 0.027466 | 0.059509 | 0.059509 | 0.082397 | 0.009155 | 121.3303 | 121.2112 | -0.068664 | 121.3852 | 121.431 | 0.21973 | -0.064087 | 121.3257 | 121.2524 | -0.15106 | 121.3074 | 121.2708 | 0.018311 | -0.15106 | 121.3852 | 121.3898 | 121.4264 | -0.24261 | 121.3028 | 121.3028 | 121.4172 | -0.20142
1616.3594 | 121.5958 | -121.2341 | 0.16022 | -0.00091566 | 0.015616 | 0.0016619 | 0.00055326 | 0.055501 | 0.0024865 | -0.0031189 | -0.0084684 | 0.0018456 | -0.031204 | 0.04328 | 0.0066029 | 0.0056332 | 0.054932 | -0.022888 | 0.022888 | 0.10529 | 0.19226 | 0.054932 | -0.068665 | 0.004578 | 0.004578 | -0.09613 | 0.082397 | 0.09613 | 0.050354 | -0.032043 | 121.2891 | 121.1655 | 0.032044 | 121.2112 | 121.3394 | 0.17395 | -0.10528 | 121.2845 | 121.2021 | -0.07782 | 121.2387 | 121.138 | -0.064087 | -0.064087 | 121.4264 | 121.2891 | 121.257 | -0.22888 | 121.3165 | 121.3303 | 121.2387 | -0.19226
1618.1094 | 121.5637 | -121.2524 | 0.17853 | -0.00091566 | 0.01647 | 0.0023029 | 0.00098046 | 0.052724 | -0.00050411 | -0.0031189 | -0.0084684 | 0.0009912 | -0.032699 | 0.040289 | 0.0087391 | 0.0043516 | 0.041199 | -0.009155 | 0.036621 | 0.10986 | 0.19226 | 0.054932 | -0.07782 | -0.004578 | 0.022888 | -0.12817 | 0.10986 | 0.091553 | 0.050354 | -0.032043 | 121.3074 | 121.1746 | 0.013733 | 121.2433 | 121.3623 | 0.18768 | -0.13733 | 121.3028 | 121.2204 | -0.068665 | 121.2479 | 121.1243 | -0.096131 | -0.086975 | 121.4447 | 121.2936 | 121.2891 | -0.25635 | 121.3623 | 121.344 | 121.2753 | -0.21057
1619.8594 | 121.5591 | -121.2753 | 0.19226 | 0.0067138 | 0.016684 | 0.0033709 | 0.0080301 | 0.056356 | -0.0041357 | -0.0041869 | -0.00083936 | -0.001145 | -0.030563 | 0.041357 | 0.0031849 | 0.0056332 | 0.013733 | 0.009155 | 0.032043 | 0.10986 | 0.17395 | 0.054932 | -0.073242 | -0.027466 | 0.059509 | -0.086975 | 0.09613 | 0.10529 | 0.045776 | -0.032043 | 121.3303 | 121.2021 | -0.018311 | 121.2845 | 121.3852 | 0.18311 | -0.17853 | 121.3211 | 121.2433 | -0.096131 | 121.2479 | 121.1884 | -0.054932 | -0.086975 | 121.4493 | 121.2891 | 121.3074 | -0.2655 | 121.3715 | 121.3806 | 121.3348 | -0.2243
1621.5469 | 121.5179 | -121.2936 | 0.20142 | -0.0085447 | 0.014975 | 0.0029437 | 0.0063211 | 0.053365 | -0.0039221 | -0.0031189 | -0.00083936 | -0.0017858 | -0.030563 | 0.040503 | 0.0023305 | 0.0067014 | 0.050354 | 0.059509 | 0.07782 | 0.13733 | 0.17853 | 0.064087 | -0.073242 | -0.013733 | 0.07782 | -0.068665 | 0.10529 | 0.09613 | 0.054932 | -0.032043 | 121.3577 | 121.2204 | -0.022888 | 121.3531 | 121.431 | 0.21057 | -0.15106 | 121.3486 | 121.2616 | -0.09613 | 121.2799 | 121.225 | -0.036622 | -0.10529 | 121.4722 | 121.344 | 121.3715 | -0.27466 | 121.3989 | 121.3898 | 121.3715 | -0.23346
1623.3125 | 121.5683 | -121.3211 | 0.18768 | -0.0085447 | 0.014334 | 0.0048663 | 0.0071757 | 0.053579 | -0.0079809 | -0.0037597 | -0.00083936 | -0.0054174 | -0.028213 | 0.040076 | -0.0015147 | 0.0056332 | 0.11902 | 0.14191 | 0.17853 | 0.19684 | 0.13733 | 0.09613 | -0.032043 | 0.082397 | 0.20599 | 0.054932 | 0.036621 | 0.073242 | 0.068665 | 0 | 121.4172 | 121.2891 | -0.050354 | 121.463 | 121.5179 | 0.22888 | -0.068664 | 121.3898 | 121.3211 | -0.15106 | 121.4035 | 121.376 | 0.054932 | -0.11444 | 121.4584 | 121.4401 | 121.4996 | -0.21973 | 121.3577 | 121.3943 | 121.5271 | -0.18768
1625.0781 | 121.6553 | -121.2845 | 0.16479 | 0.0067138 | 0.016043 | 0.0027301 | 0.0046121 | 0.05422 | 0.0024865 | -0.0033325 | -0.00083936 | 0.0003504 | -0.030349 | 0.040503 | 0.0061757 | 0.0039242 | 0.07782 | 0.036621 | 0.064087 | 0.14191 | 0.17853 | 0.073242 | -0.07782 | 0.036621 | 0.086975 | -0.045776 | 0.07782 | 0.10071 | 0.045776 | -0.022888 | 121.3577 | 121.2067 | 0.013733 | 121.3211 | 121.4264 | 0.21973 | -0.086975 | 121.3303 | 121.2616 | -0.086975 | 121.3211 | 121.2387 | -0.022888 | -0.064087 | 121.463 | 121.3623 | 121.3486 | -0.24261 | 121.3623 | 121.3852 | 121.3715 | -0.18768
1626.8125 | 121.582 | -121.3394 | 0.20599 | -0.0085447 | 0.010489 | 0.0023029 | 0.00055326 | 0.054647 | -0.0041357 | -0.0048279 | 0.0067901 | -0.002854 | -0.033981 | 0.039648 | 0.0038259 | 0.0056332 | 0.1236 | 0.15564 | 0.17853 | 0.1831 | 0.13275 | 0.11902 | -0.032043 | 0.09613 | 0.16479 | 0.036621 | 0.050354 | 0.059509 | 0.10071 | 0.009155 | 121.4584 | 121.3074 | -0.073243 | 121.4951 | 121.5225 | 0.21515 | -0.082398 | 121.4401 | 121.3486 | -0.15564 | 121.4355 | 121.376 | 0.027466 | -0.14649 | 121.4722 | 121.463 | 121.5179 | -0.23804 | 121.3898 | 121.3989 | 121.5042 | -0.19684
1628.5 | 121.5454 | -121.3165 | 0.20142 | -0.00091566 | 0.01583 | 0.0031573 | 0.0029031 | 0.054647 | -0.0049903 | -0.0063233 | -0.0084684 | -0.0022132 | -0.030136 | 0.040503 | 0.0023305 | 0.005206 | 0.13733 | 0.1831 | 0.18768 | 0.19226 | 0.13733 | 0.091553 | -0.050354 | 0.10529 | 0.19684 | 0.059509 | 0.041199 | 0.054932 | 0.10529 | 0.013733 | 121.4081 | 121.2662 | -0.064087 | 121.4996 | 121.5088 | 0.24261 | -0.064087 | 121.4218 | 121.3303 | -0.16022 | 121.4218 | 121.376 | 0.045776 | -0.14648 | 121.4539 | 121.4539 | 121.5042 | -0.25177 | 121.3577 | 121.3715 | 121.5134 | -0.18768
1630.25 | 121.6187 | -121.3303 | 0.19684 | -0.00091566 | 0.012198 | 0.0033709 | 0.0018351 | 0.053579 | -0.0047765 | -0.0069641 | -0.00083936 | -0.0037086 | -0.030777 | 0.040716 | 0.0031849 | 0.0039242 | 0.10986 | 0.1236 | 0.13733 | 0.17853 | 0.15106 | 0.091553 | -0.045776 | 0.07782 | 0.17853 | 0.054932 | 0.050354 | 0.050354 | 0.086975 | 0.004578 | 121.4218 | 121.2845 | -0.045776 | 121.4539 | 121.5088 | 0.2243 | -0.086975 | 121.4172 | 121.3348 | -0.14648 | 121.4081 | 121.3852 | 0.050354 | -0.14648 | 121.4813 | 121.4401 | 121.4676 | -0.24261 | 121.3806 | 121.3806 | 121.5088 | -0.19226
1631.9375 | 121.6187 | -121.344 | 0.18768 | -0.00091566 | 0.013266 | 0.0048663 | 0.0037577 | 0.055288 | -0.0028539 | -0.0041869 | -0.00083936 | -0.0047766 | -0.031204 | 0.039648 | 0.0025441 | 0.0056332 | 0.12817 | 0.15106 | 0.16479 | 0.17853 | 0.14648 | 0.082397 | -0.050354 | 0.086975 | 0.19226 | 0.054932 | 0.064087 | 0.054932 | 0.09613 | 0.009155 | 121.4264 | 121.2936 | -0.041199 | 121.4951 | 121.5225 | 0.22888 | -0.059509 | 121.4401 | 121.3531 | -0.1236 | 121.431 | 121.3989 | 0.045777 | -0.13275 | 121.4905 | 121.4722 | 121.5088 | -0.23804 | 121.4081 | 121.3989 | 121.5363 | -0.17853
1633.6719 | 121.582 | -121.3623 | 0.19684 | 0.0067138 | 0.01583 | 0.0029437 | 0.0058939 | 0.051443 | -0.0013587 | -0.0058959 | -0.00083936 | -0.0037086 | -0.028 | 0.04093 | 0.0038259 | 0.0037106 | 0.10071 | 0.086975 | 0.10071 | 0.16479 | 0.16937 | 0.068665 | -0.064087 | 0.022888 | 0.082397 | -0.064087 | 0.091553 | 0.07782 | 0.059509 | -0.050354 | 121.431 | 121.2982 | -0.027465 | 121.4493 | 121.5271 | 0.22888 | -0.09613 | 121.4218 | 121.312 | -0.10529 | 121.3852 | 121.2982 | -0.013733 | -0.11902 | 121.5317 | 121.463 | 121.463 | -0.26093 | 121.4539 | 121.4401 | 121.4447 | -0.24719
1635.4375 | 121.6278 | -121.3623 | 0.21515 | -0.00091566 | 0.0096344 | 0.0031573 | 0.0039713 | 0.055929 | -0.0037085 | -0.0046143 | -0.0084684 | -0.0041358 | -0.032058 | 0.039862 | 0.0042531 | 0.0064878 | 0.082397 | 0.082397 | 0.12817 | 0.14648 | 0.16022 | 0.07782 | -0.032043 | 0.050354 | 0.11902 | -0.004578 | 0.073242 | 0.07782 | 0.054932 | -0.013733 | 121.4401 | 121.3303 | -0.054932 | 121.4447 | 121.5088 | 0.17853 | -0.13275 | 121.4172 | 121.3486 | -0.14191 | 121.4127 | 121.3577 | 0.009155 | -0.13733 | 121.5225 | 121.4447 | 121.4905 | -0.24719 | 121.4355 | 121.4401 | 121.4813 | -0.22888
1637.1875 | 121.669 | -121.3394 | 0.20599 | -0.00091566 | 0.015616 | 0.0027301 | 0.0016215 | 0.052724 | 0.0035547 | -0.0022643 | -0.0084684 | 0.0027002 | -0.030777 | 0.041785 | 0.0087391 | 0.0026426 | 0.13275 | 0.082397 | 0.082397 | 0.13733 | 0.16022 | 0.059509 | -0.073242 | 0.068665 | 0.09613 | -0.054932 | 0.073242 | 0.09613 | 0.050354 | -0.032043 | 121.3989 | 121.2662 | -0.045777 | 121.4218 | 121.4767 | 0.21057 | -0.073243 | 121.3898 | 121.3074 | -0.13275 | 121.4081 | 121.2845 | -0.022889 | -0.10986 | 121.4996 | 121.4722 | 121.4218 | -0.27924 | 121.4127 | 121.4355 | 121.4355 | -0.23804
1638.9375 | 121.6049 | -121.3577 | 0.22888 | -0.00091566 | 0.014121 | 0.0040119 | 0.0052531 | 0.054433 | -0.0054175 | -0.0026917 | -0.0084684 | -0.0043494 | -0.03099 | 0.037726 | 0.0023305 | 0.0062742 | 0.12817 | 0.17853 | 0.19226 | 0.17853 | 0.13275 | 0.07782 | -0.032043 | 0.10529 | 0.20142 | 0.050354 | 0.045776 | 0.059509 | 0.054932 | 0 | 121.4355 | 121.3257 | -0.096131 | 121.5363 | 121.5363 | 0.21057 | -0.10071 | 121.4127 | 121.3577 | -0.18311 | 121.463 | 121.4081 | 0.050354 | -0.16937 | 121.4905 | 121.4859 | 121.55 | -0.26093 | 121.4035 | 121.4172 | 121.5591 | -0.22888
1640.625 | 121.6965 | -121.3577 | 0.20599 | -0.0085447 | 0.011771 | 0.0020893 | 0.00098046 | 0.053579 | -0.0017859 | -0.0035461 | -0.00083936 | -0.0013586 | -0.031631 | 0.042212 | 0.0072437 | 0.0047788 | 0.15564 | 0.14648 | 0.16479 | 0.19226 | 0.12817 | 0.082397 | -0.022888 | 0.11902 | 0.15106 | 0.032043 | 0.045776 | 0.036621 | 0.073242 | -0.004578 | 121.4401 | 121.3348 | -0.07782 | 121.5042 | 121.55 | 0.21515 | -0.050354 | 121.431 | 121.3531 | -0.16022 | 121.4767 | 121.3898 | 0.036621 | -0.16937 | 121.4859 | 121.5134 | 121.5225 | -0.22888 | 121.4035 | 121.3943 | 121.5088 | -0.21057
1642.375 | 121.6232 | -121.3669 | 0.21973 | -0.0085447 | 0.014548 | 0.0040119 | 0.0052531 | 0.055288 | -0.0017859 | -0.0029053 | -0.0084684 | 0.0007776 | -0.030136 | 0.039862 | 0.0048939 | 0.0058468 | 0.045776 | 0.022888 | 0.045776 | 0.09613 | 0.16479 | 0.045776 | -0.082397 | -0.022888 | 0.059509 | -0.091553 | 0.10071 | 0.10986 | 0.041199 | -0.050354 | 121.4127 | 121.2845 | -0.054932 | 121.3898 | 121.463 | 0.17853 | -0.17395 | 121.4081 | 121.3165 | -0.11902 | 121.344 | 121.2753 | -0.041199 | -0.10986 | 121.5317 | 121.4127 | 121.4127 | -0.30212 | 121.4676 | 121.4767 | 121.4264 | -0.27008
1644.125 | 121.7056 | -121.3623 | 0.21057 | -0.00091566 | 0.015616 | 0.00016669 | 0.0029031 | 0.05422 | 0.0022729 | -0.0026917 | 0.0067901 | 0.000564 | -0.030136 | 0.042425 | 0.0053211 | 0.0056332 | 0.032043 | -0.009155 | 0.022888 | 0.10529 | 0.19226 | 0.045776 | -0.073242 | 0.009155 | 0.009155 | -0.14648 | 0.086975 | 0.086975 | 0.045776 | -0.041199 | 121.4081 | 121.2891 | -0.01831 | 121.3531 | 121.4676 | 0.17853 | -0.17853 | 121.4081 | 121.3211 | -0.1236 | 121.3715 | 121.2158 | -0.10529 | -0.1236 | 121.5546 | 121.3943 | 121.3852 | -0.28381 | 121.4493 | 121.4493 | 121.3715 | -0.25177
1645.8906 | 121.6644 | -121.3943 | 0.2243 | 0.0067138 | 0.0062164 | 0.0050799 | 0.0046121 | 0.05486 | -0.0066993 | -0.0041869 | -0.0084684 | -0.004563 | -0.031417 | 0.039221 | 0.0029713 | 0.0060604 | 0.059509 | 0.11444 | 0.1236 | 0.16022 | 0.13275 | 0.07782 | -0.064087 | 0.054932 | 0.17395 | 0.027466 | 0.054932 | 0.054932 | 0.064087 | -0.022888 | 121.4722 | 121.3303 | -0.091553 | 121.5088 | 121.5546 | 0.2243 | -0.16479 | 121.4584 | 121.3715 | -0.16937 | 121.4493 | 121.4218 | 0.050354 | -0.16937 | 121.5271 | 121.4539 | 121.5179 | -0.28839 | 121.4493 | 121.4493 | 121.5683 | -0.24719
1647.5625 | 121.7468 | -121.3531 | 0.16937 | -0.00091566 | 0.015616 | 0.00080749 | 0.0076029 | 0.05422 | 0.0033411 | -0.0029053 | 0.01442 | -0.0007178 | -0.030136 | 0.040076 | 0.0051075 | 0.0026426 | 0.10529 | 0.059509 | 0.07782 | 0.15106 | 0.17395 | 0.041199 | -0.073242 | 0.059509 | 0.10071 | -0.050354 | 0.059509 | 0.07782 | 0.054932 | -0.027466 | 121.3943 | 121.2799 | 0.004577 | 121.4127 | 121.5042 | 0.2243 | -0.064087 | 121.4081 | 121.3257 | -0.10986 | 121.4127 | 121.3028 | -0.022888 | -0.091553 | 121.5271 | 121.4584 | 121.431 | -0.24261 | 121.4127 | 121.431 | 121.4539 | -0.19684
1649.3125 | 121.701 | -121.3943 | 0.20142 | -0.00091566 | 0.022025 | 0.0037983 | 0.0043985 | 0.053152 | 0.0018457 | -0.00055532 | -0.00083936 | 0.0024866 | -0.03099 | 0.040503 | 0.0078847 | 0.003497 | 0.050354 | 0.013733 | 0.032043 | 0.10071 | 0.17395 | 0.064087 | -0.073242 | 0.009155 | 0.022888 | -0.10529 | 0.07782 | 0.086975 | 0.045776 | -0.041199 | 121.4584 | 121.3211 | -0.027466 | 121.4081 | 121.4951 | 0.17395 | -0.15106 | 121.4401 | 121.3531 | -0.1236 | 121.4035 | 121.2891 | -0.064087 | -0.11444 | 121.5683 | 121.4447 | 121.4264 | -0.27466 | 121.4722 | 121.4813 | 121.4172 | -0.24262
1651 | 121.7194 | -121.463 | 0.16937 | -0.0085447 | 0.016684 | 0.0025165 | 0.0031167 | 0.055501 | -0.00071771 | -0.00055532 | 0.0067901 | -0.0013586 | -0.030777 | 0.043066 | 0.0055349 | 0.0060604 | 0.036621 | -0.013733 | 0.018311 | 0.11444 | 0.19226 | 0.045776 | -0.068665 | -0.013733 | -0.004578 | -0.11902 | 0.091553 | 0.10529 | 0.068665 | -0.027466 | 121.5088 | 121.3943 | 0.022888 | 121.4493 | 121.5775 | 0.18311 | -0.13275 | 121.5317 | 121.4355 | -0.07782 | 121.4493 | 121.344 | -0.091553 | -0.064087 | 121.6553 | 121.4996 | 121.4813 | -0.23804 | 121.5546 | 121.5683 | 121.4584 | -0.19684
1652.7344 | 121.7514 | -121.4447 | 0.16479 | -0.00091566 | 0.014121 | 0.0033709 | 0.0018351 | 0.052297 | 0.00013669 | -0.0018371 | -0.00083936 | -0.0005042 | -0.031204 | 0.041144 | 0.0063893 | 0.006915 | 0.032043 | -0.013733 | 0.027466 | 0.10529 | 0.17395 | 0.050354 | -0.091553 | -0.013733 | 0.013733 | -0.10071 | 0.10071 | 0.09613 | 0.050354 | -0.022888 | 121.4951 | 121.3531 | 0.009155 | 121.431 | 121.55 | 0.19684 | -0.13275 | 121.4951 | 121.4218 | -0.064087 | 121.431 | 121.344 | -0.07782 | -0.068665 | 121.6187 | 121.4767 | 121.4722 | -0.25635 | 121.5454 | 121.5408 | 121.4584 | -0.18768
1654.5 | 121.6965 | -121.4722 | 0.16479 | -0.00091566 | 0.01583 | 0.0025165 | 0.0063211 | 0.053792 | -0.0077673 | -0.0058959 | -0.0084684 | -0.0043494 | -0.03099 | 0.03858 | -0.00023313 | 0.0067014 | 0.082397 | 0.10071 | 0.13733 | 0.16479 | 0.13733 | 0.07782 | -0.050354 | 0.041199 | 0.16479 | 0.036621 | 0.041199 | 0.050354 | 0.082397 | -0.004578 | 121.55 | 121.4218 | -0.027466 | 121.5729 | 121.637 | 0.21515 | -0.082398 | 121.5546 | 121.4676 | -0.1236 | 121.5134 | 121.5088 | 0.041199 | -0.11444 | 121.6095 | 121.5546 | 121.6095 | -0.21515 | 121.5134 | 121.5225 | 121.637 | -0.16937
1656.2656 | 121.701 | -121.4767 | 0.19226 | -0.00091566 | 0.013907 | 0.0031573 | 0.0071757 | 0.05422 | -0.0056311 | -0.0054687 | -0.0084684 | -0.0054174 | -0.029922 | 0.040076 | 0.00083507 | 0.0064878 | 0.054932 | 0.082397 | 0.1236 | 0.14648 | 0.14648 | 0.082397 | -0.045776 | 0.036621 | 0.14648 | 0.022888 | 0.054932 | 0.054932 | 0.059509 | -0.027466 | 121.5591 | 121.431 | -0.045777 | 121.5591 | 121.6232 | 0.19226 | -0.13733 | 121.5363 | 121.4493 | -0.13733 | 121.5134 | 121.4996 | 0.050354 | -0.13733 | 121.6232 | 121.5317 | 121.6003 | -0.23804 | 121.5317 | 121.5317 | 121.6232 | -0.21973
1658.0312 | 121.7972 | -121.4447 | 0.13733 | -0.00091566 | 0.012839 | 0.0014483 | 0.0052531 | 0.054006 | -0.0015723 | -0.0050415 | -0.00083936 | -0.0007178 | -0.032058 | 0.041144 | 0.0059621 | 0.0022152 | 0.13733 | 0.091553 | 0.16022 | 0.1831 | 0.13733 | 0.09613 | -0.032043 | 0.11444 | 0.14191 | 0.004578 | 0.036621 | 0.064087 | 0.068665 | 0.013733 | 121.5408 | 121.4127 | 0 | 121.5363 | 121.6278 | 0.21515 | 0 | 121.5134 | 121.4584 | -0.10071 | 121.5591 | 121.4493 | -0.009155 | -0.073242 | 121.582 | 121.582 | 121.6049 | -0.16937 | 121.4813 | 121.5088 | 121.5866 | -0.1236
1659.7188 | 121.7377 | -121.5134 | 0.15564 | 0.0067138 | 0.014121 | 0.0016619 | 0.0056803 | 0.05187 | 0.0022729 | -0.0016235 | -0.00083936 | 0.0012048 | -0.030136 | 0.040716 | 0.0074575 | 0.0043516 | 0.036621 | -0.032043 | 0.032043 | 0.091553 | 0.17853 | 0.068665 | -0.082397 | -0.018311 | -0.013733 | -0.14191 | 0.086975 | 0.10529 | 0.054932 | -0.027466 | 121.582 | 121.431 | 0.022888 | 121.4813 | 121.6049 | 0.17395 | -0.11902 | 121.5683 | 121.4859 | -0.068665 | 121.4951 | 121.3715 | -0.11444 | -0.050354 | 121.6919 | 121.55 | 121.5454 | -0.23804 | 121.6003 | 121.6187 | 121.4996 | -0.18311
1661.4688 | 121.8109 | -121.4676 | 0.15564 | -0.0085447 | 0.018179 | 0.00059389 | 0.0080301 | 0.05422 | -0.00029051 | -0.0029053 | 0.0067901 | -0.0005042 | -0.029708 | 0.041785 | 0.0038259 | 0.0067014 | 0.036621 | 0.027466 | 0.036621 | 0.11902 | 0.16937 | 0.059509 | -0.09613 | 0.045776 | 0.086975 | -0.050354 | 0.086975 | 0.091553 | 0.036621 | -0.041199 | 121.5271 | 121.3715 | 0.013733 | 121.4951 | 121.5866 | 0.21515 | -0.11902 | 121.5042 | 121.4264 | -0.068665 | 121.5134 | 121.4172 | -0.009155 | -0.064087 | 121.637 | 121.5042 | 121.5042 | -0.25177 | 121.5546 | 121.5591 | 121.5546 | -0.19684
1663.2031 | 121.7697 | -121.4905 | 0.16937 | -0.0085447 | 0.009848 | 0.00059389 | 0.0041849 | 0.055501 | -0.0030677 | -0.0037597 | -0.0084684 | -0.0032812 | -0.031204 | 0.041144 | 0.0038259 | 0.0060604 | 0.11902 | 0.14191 | 0.16479 | 0.17395 | 0.13275 | 0.10529 | -0.041199 | 0.10071 | 0.15564 | 0.050354 | 0.054932 | 0.054932 | 0.068665 | -0.004578 | 121.5958 | 121.4493 | -0.036622 | 121.6324 | 121.6644 | 0.21515 | -0.050354 | 121.5591 | 121.4859 | -0.11444 | 121.5912 | 121.5408 | 0.054932 | -0.11444 | 121.6232 | 121.6095 | 121.6553 | -0.21057 | 121.5454 | 121.5454 | 121.6461 | -0.17395
1664.9531 | 121.8292 | -121.4813 | 0.14191 | -0.00091566 | 0.01113 | 0.0010211 | 0.0054667 | 0.05422 | -0.0039221 | -0.0033325 | -0.0084684 | -0.0024268 | -0.033981 | 0.040716 | 0.0053211 | 0.0056332 | 0.13733 | 0.1236 | 0.13733 | 0.1831 | 0.1236 | 0.091553 | -0.045776 | 0.11444 | 0.15106 | 0.027466 | 0.036621 | 0.045776 | 0.07782 | 0.004578 | 121.5729 | 121.4355 | -0.018311 | 121.6049 | 121.6644 | 0.22888 | -0.004578 | 121.5591 | 121.4859 | -0.10529 | 121.5958 | 121.5088 | 0.022888 | -0.096131 | 121.6049 | 121.6187 | 121.6187 | -0.18768 | 121.5179 | 121.5271 | 121.6324 | -0.13733
1666.625 | 121.6919 | -97.8378 | 23.8266 | -0.0085447 | 0.0096344 | 0.0042255 | 0.0016215 | 0.053792 | -0.0079809 | -0.0058959 | -0.016098 | -0.0034948 | -0.033554 | 0.038153 | 0.0012623 | 0.0060604 | 0.032043 | 0.068665 | 0.10986 | 0.12817 | 0.14648 | 0.054932 | -0.068665 | 0.022888 | 0.10529 | -0.009155 | 0.027466 | 0.050354 | 0.050354 | -0.036621 | 97.8928 | 97.7692 | -23.6801 | 97.9065 | 97.966 | 0.19684 | -23.7946 | 97.8882 | 97.8012 | -23.7991 | 97.8607 | 97.8287 | 0.027466 | -23.7762 | 97.9843 | 97.8699 | 97.9477 | -23.8953 | 97.8653 | 97.8882 | 97.9431 | -23.8632
1668.375 | 121.7834 | -97.7737 | 23.8083 | 0.0067138 | 0.010916 | 0.0023029 | 0.0014079 | 0.056142 | -0.0037085 | -0.0044007 | -0.0084684 | -0.001145 | -0.034195 | 0.040503 | 0.0042531 | 0.0058468 | 0.14191 | 0.10986 | 0.11902 | 0.16937 | 0.11902 | 0.068665 | -0.059509 | 0.10071 | 0.12817 | 0.013733 | 0.013733 | 0.032043 | 0.064087 | -0.004578 | 97.8424 | 97.7142 | -23.6893 | 97.8836 | 97.9431 | 0.22888 | -23.6664 | 97.8378 | 97.7692 | -23.7946 | 97.8745 | 97.7875 | 0.018311 | -23.7762 | 97.8928 | 97.9156 | 97.8928 | -23.8678 | 97.7875 | 97.8058 | 97.9019 | -23.8129
1670.125 | 121.7468 | -97.7783 | 23.8495 | -0.0085447 | 0.011984 | 0.0057209 | 0.0054667 | 0.053579 | -0.0058447 | -0.0041869 | -0.0084684 | -0.0041358 | -0.031845 | 0.039007 | 0.0046803 | 0.0043516 | 0.068665 | 0.045776 | 0.091553 | 0.11902 | 0.14648 | 0.050354 | -0.064087 | 0.004578 | 0.09613 | -0.032043 | 0.032043 | 0.045776 | 0.050354 | -0.045776 | 97.8287 | 97.7142 | -23.703 | 97.8241 | 97.8973 | 0.18311 | -23.7808 | 97.8287 | 97.7325 | -23.8174 | 97.7829 | 97.7463 | 0.013733 | -23.8037 | 97.9248 | 97.847 | 97.8699 | -23.9136 | 97.8104 | 97.8241 | 97.8744 | -23.8953
1671.875 | 121.843 | -97.7371 | 23.8495 | -0.00091566 | 0.014975 | 0.0025165 | 0.0076029 | 0.054006 | 0.00077749 | -0.0035461 | 0.0067901 | -0.0007178 | -0.031845 | 0.042425 | 0.0061757 | 0.0039242 | 0.045776 | 0.004578 | 0.022888 | 0.11444 | 0.17395 | 0.022888 | -0.10071 | 0.004578 | 0.050354 | -0.086975 | 0.059509 | 0.073242 | 0.027466 | -0.050354 | 97.76 | 97.6364 | -23.6755 | 97.7417 | 97.8516 | 0.21515 | -23.8037 | 97.7646 | 97.6868 | -23.79 | 97.7417 | 97.6501 | -0.036621 | -23.7762 | 97.9111 | 97.7829 | 97.76 | -23.9502 | 97.7966 | 97.8104 | 97.7875 | -23.8998
1673.5625 | 121.7468 | -97.7509 | 23.8953 | -0.0085447 | 0.0092072 | 0.0027301 | 0.00098046 | 0.05486 | -0.0028539 | -0.0016235 | -0.00083936 | -0.0026404 | -0.029708 | 0.039007 | 0.0053211 | 0.005206 | 0.10986 | 0.11444 | 0.16022 | 0.15564 | 0.091553 | 0.064087 | -0.064087 | 0.068665 | 0.13275 | 0.009155 | 0.013733 | 0.032043 | 0.050354 | -0.018311 | 97.8149 | 97.6868 | -23.8037 | 97.8653 | 97.9065 | 0.21973 | -23.7854 | 97.8012 | 97.7325 | -23.8815 | 97.8195 | 97.76 | 0.027466 | -23.8632 | 97.8424 | 97.8607 | 97.9111 | -23.9594 | 97.7646 | 97.7829 | 97.8836 | -23.9136
1675.3281 | 121.8292 | -97.7142 | 23.8724 | -0.00091566 | 0.015189 | 0.0014483 | 0.0039713 | 0.052511 | 0.0014185 | -0.0041869 | 0.0067901 | 0.0014184 | -0.029708 | 0.043066 | 0.0066029 | 0.0032834 | 0.013733 | -0.050354 | 0.004578 | 0.086975 | 0.16479 | 0.050354 | -0.086975 | -0.018311 | -0.018311 | -0.14191 | 0.050354 | 0.064087 | 0.036621 | -0.068665 | 97.7646 | 97.6273 | -23.7076 | 97.6639 | 97.8012 | 0.17395 | -23.8586 | 97.7509 | 97.6456 | -23.822 | 97.6959 | 97.5723 | -0.073242 | -23.8083 | 97.879 | 97.728 | 97.7188 | -23.9594 | 97.7646 | 97.7783 | 97.6959 | -23.941
1677.0938 | 121.8201 | -97.7188 | 23.9227 | -0.0085447 | 0.015189 | 0.0018757 | 0.0037577 | 0.054006 | -7.6908e-05 | -0.00012812 | -0.00083936 | 0.0046228 | -0.030136 | 0.042425 | 0.0083119 | 0.006915 | 0.059509 | 0.032043 | 0.045776 | 0.10529 | 0.15564 | 0.032043 | -0.07782 | -0.009155 | 0.027466 | -0.11902 | 0.045776 | 0.064087 | 0.032043 | -0.050354 | 97.7509 | 97.641 | -23.7671 | 97.7509 | 97.8241 | 0.18311 | -23.8632 | 97.7509 | 97.6685 | -23.877 | 97.7097 | 97.5998 | -0.068665 | -23.8586 | 97.8745 | 97.7783 | 97.7646 | -24.0005 | 97.7646 | 97.7829 | 97.7463 | -23.9731
1678.8438 | 121.8063 | -121.5042 | 0.17395 | -0.00091566 | 0.012412 | 0.0031573 | 0.0037577 | 0.051656 | -0.0049903 | -0.0044007 | -0.0084684 | -0.0009314 | -0.031204 | 0.041998 | 0.0021169 | 0.0073422 | 0.045776 | 0.050354 | 0.054932 | 0.10986 | 0.16937 | 0.045776 | -0.07782 | -0.041199 | 0.059509 | -0.082397 | 0.082397 | 0.09613 | 0.022888 | -0.022888 | 121.55 | 121.4264 | -0.004577 | 121.5546 | 121.6141 | 0.18768 | -0.12817 | 121.5271 | 121.4813 | -0.091553 | 121.463 | 121.4218 | -0.059509 | -0.07782 | 121.6736 | 121.55 | 121.5591 | -0.25177 | 121.5866 | 121.6003 | 121.5637 | -0.19684
1680.5469 | 121.8475 | -121.5179 | 0.16479 | 0.0067138 | 0.011771 | 0.0042255 | 0.0058939 | 0.052297 | -0.0084081 | -0.0054687 | -0.0084684 | -0.0039222 | -0.032913 | 0.037085 | 0.0023305 | 0.0058468 | 0.10529 | 0.13733 | 0.15564 | 0.16479 | 0.16479 | 0.086975 | -0.045776 | 0.064087 | 0.16479 | 0.050354 | 0.045776 | 0.068665 | 0.086975 | -0.009155 | 121.6049 | 121.4722 | 0 | 121.6553 | 121.6827 | 0.21057 | -0.059509 | 121.6049 | 121.5088 | -0.11902 | 121.582 | 121.5683 | 0.059509 | -0.09613 | 121.6827 | 121.6232 | 121.6736 | -0.21057 | 121.5637 | 121.5866 | 121.6827 | -0.17395
1682.2969 | 121.7834 | -121.6003 | 0.17395 | -0.00091566 | 0.013907 | 0.0055073 | 0.0058939 | 0.052938 | -0.0056311 | -0.0050415 | -0.0084684 | -0.0041358 | -0.032058 | 0.038794 | 0.0021169 | 0.005206 | 0.12817 | 0.13275 | 0.16479 | 0.1831 | 0.14191 | 0.068665 | -0.050354 | 0.050354 | 0.16022 | 0.004578 | 0.054932 | 0.073242 | 0.07782 | -0.018311 | 121.669 | 121.55 | -0.032043 | 121.7331 | 121.7834 | 0.23346 | -0.045776 | 121.6782 | 121.582 | -0.11902 | 121.6507 | 121.6049 | 0.022889 | -0.10071 | 121.7422 | 121.7285 | 121.7651 | -0.2243 | 121.6553 | 121.6736 | 121.7606 | -0.19226
1684.0625 | 121.9208 | -121.5408 | 0.13275 | -0.0085447 | 0.013266 | 0.0033709 | 0.0046121 | 0.05486 | 0.00035029 | -0.0048279 | -0.0084684 | 0.0012048 | -0.032058 | 0.041571 | 0.0072437 | 0.0056332 | 0.059509 | 0.004578 | 0.059509 | 0.1236 | 0.17853 | 0.045776 | -0.064087 | 0 | 0.068665 | -0.07782 | 0.07782 | 0.082397 | 0.059509 | -0.022888 | 121.5866 | 121.4767 | 0.045777 | 121.5454 | 121.6644 | 0.18768 | -0.073242 | 121.6003 | 121.5179 | -0.054931 | 121.5408 | 121.463 | -0.054932 | -0.050354 | 121.7194 | 121.6003 | 121.6003 | -0.19684 | 121.6187 | 121.6232 | 121.6095 | -0.15564
1685.8125 | 121.8384 | -121.5912 | 0.16937 | 0.0067138 | 0.011771 | 0.0046527 | 0.0043985 | 0.054006 | -0.0064855 | -0.0033325 | -0.0084684 | -0.002854 | -0.031417 | 0.037512 | 0.0031849 | 0.0056332 | 0.10529 | 0.11902 | 0.15564 | 0.18768 | 0.15564 | 0.082397 | -0.045776 | 0.07782 | 0.16937 | 0.045776 | 0.059509 | 0.064087 | 0.064087 | 0.004578 | 121.6736 | 121.5454 | -0.013733 | 121.7102 | 121.7789 | 0.23346 | -0.064087 | 121.6553 | 121.5958 | -0.10986 | 121.669 | 121.637 | 0.041198 | -0.10529 | 121.7468 | 121.6965 | 121.7468 | -0.21515 | 121.6507 | 121.6553 | 121.7606 | -0.16479
1687.5781 | 121.8018 | -119.3665 | 2.4033 | -0.00091566 | 0.014975 | 0.0040119 | 0.0080301 | 0.052297 | -0.0032813 | -0.0029053 | 0.0067901 | -0.0030676 | -0.029922 | 0.040289 | 0.0019033 | 0.0060604 | 0.10529 | 0.10071 | 0.1236 | 0.15564 | 0.14191 | 0.073242 | -0.068665 | 0.018311 | 0.10529 | -0.045776 | 0.086975 | 0.07782 | 0.059509 | -0.027466 | 119.4397 | 119.2978 | -2.2614 | 119.4672 | 119.5221 | 0.22431 | -2.298 | 119.426 | 119.339 | -2.3163 | 119.3848 | 119.3207 | -0.01831 | -2.3254 | 119.5084 | 119.4717 | 119.4901 | -2.4719 | 119.4534 | 119.4443 | 119.4717 | -2.4307
1689.2656 | 121.8338 | -119.0918 | 2.6779 | -0.00091566 | 0.012412 | 0.0052935 | 0.0071757 | 0.055501 | -0.0062719 | -0.0046143 | -0.00083936 | -0.0054174 | -0.030349 | 0.037726 | 0.00083507 | 0.0054196 | 0.16022 | 0.21057 | 0.17395 | 0.19684 | 0.14191 | 0.073242 | -0.041199 | 0.082397 | 0.1831 | 0.045776 | 0.054932 | 0.022888 | 0.082397 | 0 | 119.165 | 119.0506 | -2.536 | 119.3024 | 119.2886 | 0.23804 | -2.5177 | 119.1742 | 119.0918 | -2.623 | 119.1742 | 119.1376 | 0.045776 | -2.655 | 119.2337 | 119.252 | 119.2657 | -2.7191 | 119.1467 | 119.1147 | 119.2749 | -2.6779
1691.0156 | 121.7606 | -97.7463 | 24.0509 | -0.00091566 | 0.013907 | 0.0025165 | 0.0069621 | 0.055288 | -0.0028539 | -0.0050415 | 0.0067901 | -0.0009314 | -0.032058 | 0.040503 | 0.0042531 | 0.0030698 | 0.10071 | 0.16022 | 0.15564 | 0.16479 | 0.1236 | 0.050354 | -0.073242 | 0.07782 | 0.1831 | 0.018311 | 0.013733 | 0.032043 | 0.059509 | -0.027466 | 97.7966 | 97.673 | -23.9273 | 97.9065 | 97.9111 | 0.23804 | -23.9502 | 97.8058 | 97.7188 | -24.0372 | 97.8241 | 97.7646 | 0.045777 | -24.0189 | 97.8699 | 97.847 | 97.9019 | -24.1241 | 97.76 | 97.7783 | 97.9294 | -24.0784
1692.6875 | 121.9025 | -97.673 | 24.0005 | -0.00091566 | 0.015616 | -4.6912e-05 | 0.0063211 | 0.055501 | 0.0033411 | -0.0039733 | -0.0084684 | 0.001632 | -0.029708 | 0.040716 | 0.0057485 | 0.003497 | 0.027466 | 0.022888 | 0.018311 | 0.10986 | 0.16022 | 0.032043 | -0.10071 | 0.009155 | 0.059509 | -0.086975 | 0.068665 | 0.059509 | 0.041199 | -0.059509 | 97.7051 | 97.5723 | -23.8403 | 97.6959 | 97.7829 | 0.21057 | -23.9731 | 97.7142 | 97.6135 | -23.9319 | 97.6822 | 97.5861 | -0.027466 | -23.941 | 97.8333 | 97.7005 | 97.6913 | -24.1013 | 97.7417 | 97.7325 | 97.7325 | -24.0601
1694.4531 | 121.9437 | -121.5591 | 0.14191 | -0.00091566 | 0.014334 | 0.0031573 | 0.0024759 | 0.05486 | -0.0013587 | -0.0026917 | 0.0067901 | -0.0007178 | -0.032699 | 0.041571 | 0.0033985 | 0.0039242 | 0.15106 | 0.14191 | 0.16479 | 0.19684 | 0.13733 | 0.091553 | -0.032043 | 0.1236 | 0.15106 | 0.022888 | 0.032043 | 0.022888 | 0.09613 | 0.004578 | 121.6507 | 121.5271 | -0.004578 | 121.7011 | 121.756 | 0.22888 | 0.009155 | 121.6553 | 121.5637 | -0.10986 | 121.6827 | 121.582 | 0.01831 | -0.11902 | 121.6965 | 121.7102 | 121.7239 | -0.17395 | 121.5912 | 121.582 | 121.7102 | -0.13733
1696.1562 | 121.9162 | -121.582 | 0.15564 | 0.0067138 | 0.01647 | 0.0027301 | 0.0058939 | 0.053792 | 0.0022729 | -0.00055532 | -0.00083936 | 0.001632 | -0.032272 | 0.041357 | 0.0083119 | 0.0047788 | 0.10986 | 0.059509 | 0.064087 | 0.14648 | 0.14648 | 0.064087 | -0.07782 | 0.032043 | 0.068665 | -0.082397 | 0.07782 | 0.10071 | 0.050354 | -0.036621 | 121.6461 | 121.5042 | -0.009156 | 121.6415 | 121.7285 | 0.2243 | -0.045777 | 121.6324 | 121.5454 | -0.07782 | 121.6141 | 121.4996 | -0.045776 | -0.054932 | 121.7285 | 121.6919 | 121.6461 | -0.23346 | 121.6599 | 121.6827 | 121.6507 | -0.19226
1697.9062 | 121.9803 | -121.6232 | 0.13275 | -0.00091566 | 0.014548 | 0.0016619 | 0.0039713 | 0.055074 | -0.00029051 | -0.0041869 | -0.0084684 | -0.0005042 | -0.03099 | 0.039862 | 0.0063893 | 0.0064878 | 0.041199 | -0.004578 | 0.027466 | 0.091553 | 0.17853 | 0.054932 | -0.064087 | 0.004578 | 0.009155 | -0.10071 | 0.09613 | 0.091553 | 0.054932 | -0.027466 | 121.6782 | 121.5591 | 0.045777 | 121.6187 | 121.7148 | 0.15564 | -0.091552 | 121.6782 | 121.5958 | -0.036621 | 121.6278 | 121.5225 | -0.073242 | -0.041198 | 121.8018 | 121.6644 | 121.6507 | -0.19684 | 121.7194 | 121.7148 | 121.6324 | -0.16022
1699.5938 | 121.8567 | -121.6461 | 0.17395 | -0.016174 | 0.013266 | 0.0052935 | 0.0082437 | 0.055501 | -0.0086219 | -0.0033325 | -0.0084684 | -0.0022132 | -0.030136 | 0.037939 | -0.00044673 | 0.0037106 | 0.13733 | 0.16479 | 0.17853 | 0.19226 | 0.13733 | 0.073242 | -0.045776 | 0.09613 | 0.2243 | 0.041199 | 0.054932 | 0.054932 | 0.091553 | -0.004578 | 121.7194 | 121.6003 | -0.036621 | 121.8109 | 121.8384 | 0.23804 | -0.036621 | 121.7377 | 121.6415 | -0.11902 | 121.7422 | 121.6873 | 0.045777 | -0.11902 | 121.7834 | 121.7834 | 121.8246 | -0.21973 | 121.701 | 121.701 | 121.8704 | -0.17853
1701.3594 | 121.8521 | -121.6553 | 0.17853 | -0.0085447 | 0.013052 | 0.0061481 | 0.0050393 | 0.054647 | -0.0060583 | -0.0039733 | -0.0084684 | -0.0030676 | -0.031845 | 0.039862 | 0.0042531 | 0.0056332 | 0.11902 | 0.14648 | 0.17853 | 0.19226 | 0.1236 | 0.091553 | -0.032043 | 0.073242 | 0.17853 | 0.013733 | 0.045776 | 0.073242 | 0.059509 | -0.009155 | 121.7468 | 121.6232 | -0.054932 | 121.8018 | 121.8475 | 0.2243 | -0.059509 | 121.7148 | 121.6461 | -0.13275 | 121.7285 | 121.669 | 0.022888 | -0.10529 | 121.7789 | 121.7743 | 121.8338 | -0.21057 | 121.701 | 121.7285 | 121.8338 | -0.18768
1703.125 | 121.907 | -121.669 | 0.16937 | -0.00091566 | 0.012839 | 0.0020893 | 0.0052531 | 0.054647 | -0.0073401 | -0.0037597 | -0.00083936 | -0.0030676 | -0.031417 | 0.040503 | 0.0019033 | 0.0064878 | 0.068665 | 0.073242 | 0.11444 | 0.14648 | 0.14648 | 0.068665 | -0.041199 | 0.041199 | 0.10986 | 0.004578 | 0.068665 | 0.059509 | 0.082397 | 0 | 121.7377 | 121.6278 | -0.022889 | 121.7422 | 121.8155 | 0.18768 | -0.10071 | 121.7514 | 121.669 | -0.10071 | 121.7102 | 121.6736 | 0.004578 | -0.10986 | 121.8155 | 121.7377 | 121.7834 | -0.21057 | 121.7377 | 121.7285 | 121.7789 | -0.16937
1704.875 | 121.8567 | -121.6782 | 0.20599 | -0.0085447 | 0.012625 | 0.0059345 | 0.0031167 | 0.054433 | -0.0026403 | -0.0056823 | -0.016098 | -0.0024268 | -0.032486 | 0.04093 | 0.0027577 | 0.0045652 | 0.13733 | 0.15106 | 0.15564 | 0.19226 | 0.14191 | 0.082397 | -0.036621 | 0.064087 | 0.17853 | 0.018311 | 0.054932 | 0.073242 | 0.082397 | 0 | 121.7606 | 121.6415 | -0.064087 | 121.8292 | 121.8704 | 0.22888 | -0.068665 | 121.7606 | 121.6782 | -0.15106 | 121.7422 | 121.6965 | 0.018311 | -0.13275 | 121.8201 | 121.8155 | 121.8338 | -0.24262 | 121.7331 | 121.7514 | 121.8567 | -0.20599
1706.5781 | 121.9391 | -121.6599 | 0.15564 | -0.00091566 | 0.016043 | 0.0016619 | 0.0039713 | 0.053152 | 0.0039819 | -0.0020507 | -0.0084684 | 0.001632 | -0.031631 | 0.041357 | 0.0091665 | 0.0026426 | 0.082397 | 0.013733 | 0.041199 | 0.11902 | 0.16479 | 0.050354 | -0.068665 | 0.018311 | 0.018311 | -0.11902 | 0.10529 | 0.09613 | 0.032043 | -0.036621 | 121.7102 | 121.5912 | 0.009155 | 121.6736 | 121.7789 | 0.18768 | -0.073243 | 121.6919 | 121.6232 | -0.050354 | 121.6782 | 121.5408 | -0.082398 | -0.05951 | 121.8246 | 121.7422 | 121.7011 | -0.22431 | 121.7651 | 121.756 | 121.6782 | -0.19226
1708.3281 | 121.9528 | -121.5317 | 0.25177 | -0.00091566 | 0.016257 | 0.0025165 | 0.0031167 | 0.053152 | 0.0027003 | 0.00093988 | -0.00083936 | 0.000564 | -0.030349 | 0.039648 | 0.0057485 | 0.0039242 | 0.086975 | 0.10529 | 0.07782 | 0.1236 | 0.16937 | 0.064087 | -0.073242 | 0.032043 | 0.054932 | -0.07782 | 0.068665 | 0.068665 | 0.036621 | -0.036621 | 121.5958 | 121.4584 | -0.082397 | 121.637 | 121.6553 | 0.19684 | -0.16479 | 121.5683 | 121.4951 | -0.1831 | 121.5637 | 121.4539 | -0.041199 | -0.1831 | 121.701 | 121.6187 | 121.6095 | -0.32501 | 121.6003 | 121.6003 | 121.5866 | -0.28839
1710.0156 | 121.962 | -121.582 | 0.21973 | -0.00091566 | 0.01647 | 0.0016619 | 0.0039713 | 0.056783 | -7.6908e-05 | -0.0026917 | -0.00083936 | -0.0007178 | -0.029495 | 0.040289 | 0.0053211 | 0.0045652 | 0.10071 | 0.091553 | 0.10071 | 0.14648 | 0.17395 | 0.054932 | -0.073242 | 0.036621 | 0.09613 | -0.045776 | 0.068665 | 0.091553 | 0.045776 | -0.050354 | 121.637 | 121.5088 | -0.045777 | 121.6736 | 121.7285 | 0.21973 | -0.11902 | 121.6278 | 121.5317 | -0.15106 | 121.6187 | 121.5363 | 0.004578 | -0.12817 | 121.756 | 121.6827 | 121.6827 | -0.29297 | 121.6507 | 121.6736 | 121.6782 | -0.27008
1711.7812 | 121.9437 | -121.6644 | 0.1831 | -0.00091566 | 0.013907 | 0.0035847 | 0.0078165 | 0.052938 | -0.0086219 | -0.0046143 | -0.00083936 | -0.0047766 | -0.030563 | 0.041571 | 0.00040787 | 0.0060604 | 0.09613 | 0.12817 | 0.17395 | 0.16022 | 0.15106 | 0.073242 | -0.045776 | 0.068665 | 0.17853 | 0.059509 | 0.050354 | 0.045776 | 0.07782 | -0.022888 | 121.7377 | 121.6187 | -0.032043 | 121.7926 | 121.8246 | 0.20599 | -0.086975 | 121.7422 | 121.6415 | -0.13275 | 121.7331 | 121.7239 | 0.082397 | -0.13733 | 121.8155 | 121.7606 | 121.8384 | -0.22888 | 121.7148 | 121.7102 | 121.843 | -0.20599
1713.5469 | 121.8979 | -121.5637 | 0.34332 | -0.00091566 | 0.011557 | 0.0035847 | 0.00098046 | 0.051656 | -0.0032813 | -0.0035461 | -0.016098 | -0.0024268 | -0.031631 | 0.041785 | 0.0044667 | 0.0075558 | 0.082397 | 0.10529 | 0.12817 | 0.1236 | 0.13733 | 0.07782 | -0.041199 | 0.036621 | 0.091553 | 0 | 0.045776 | 0.064087 | 0.073242 | 0.013733 | 121.6415 | 121.5225 | -0.20599 | 121.669 | 121.6873 | 0.16479 | -0.26093 | 121.637 | 121.5775 | -0.29755 | 121.6003 | 121.5637 | -0.013733 | -0.27924 | 121.701 | 121.6461 | 121.6919 | -0.38452 | 121.6095 | 121.6278 | 121.6553 | -0.32959
1715.3125 | 122.0215 | -119.3024 | 2.4582 | -0.00091566 | 0.01583 | 0.00059389 | 0.0048257 | 0.055929 | 0.00077749 | -0.0033325 | -0.00083936 | 0.0027002 | -0.029281 | 0.04093 | 0.0070301 | 0.0041378 | 0.10986 | 0.054932 | 0.068665 | 0.14648 | 0.15564 | 0.054932 | -0.073242 | 0.041199 | 0.086975 | -0.059509 | 0.086975 | 0.09613 | 0.045776 | -0.013733 | 119.3573 | 119.2291 | -2.3026 | 119.3573 | 119.4489 | 0.21973 | -2.3483 | 119.3481 | 119.2886 | -2.3712 | 119.3436 | 119.2429 | -0.045776 | -2.3621 | 119.458 | 119.4122 | 119.371 | -2.5314 | 119.3893 | 119.3985 | 119.3893 | -2.4719
1717.0625 | 121.9437 | -118.8629 | 2.9709 | -0.0085447 | 0.013907 | 0.0044391 | 0.0069621 | 0.05721 | -0.0052039 | -0.0039733 | -0.00083936 | -0.0054174 | -0.031204 | 0.040503 | -1.9327e-05 | 0.0056332 | 0.10529 | 0.14191 | 0.17853 | 0.17853 | 0.15564 | 0.086975 | -0.050354 | 0.086975 | 0.18768 | 0.064087 | 0.045776 | 0.050354 | 0.07782 | -0.009155 | 118.9499 | 118.8126 | -2.8152 | 119.0048 | 119.0414 | 0.22888 | -2.8656 | 118.9407 | 118.8538 | -2.9251 | 118.9499 | 118.927 | 0.073242 | -2.9205 | 119.0186 | 118.9682 | 119.0414 | -3.0212 | 118.9087 | 118.9133 | 119.0506 | -2.98
1718.8125 | 122.0306 | -118.6707 | 3.1265 | -0.0085447 | 0.014334 | 0.0014483 | 0.0037577 | 0.054433 | -0.0013587 | -0.0052551 | -0.00083936 | 0.0009912 | -0.031845 | 0.041357 | 0.0042531 | 0.005206 | 0.086975 | 0.050354 | 0.086975 | 0.14191 | 0.16937 | 0.07782 | -0.045776 | 0.086975 | 0.10986 | -0.009155 | 0.036621 | 0.059509 | 0.050354 | 0 | 118.7485 | 118.6249 | -2.9572 | 118.721 | 118.8126 | 0.18768 | -3.0396 | 118.721 | 118.6707 | -3.0899 | 118.7576 | 118.6615 | -0.009155 | -3.067 | 118.84 | 118.7576 | 118.7576 | -3.1723 | 118.7073 | 118.7302 | 118.7805 | -3.1265
1720.5156 | 121.9666 | -121.6965 | 0.17395 | -0.016174 | 0.011557 | 0.00059389 | 0.0033305 | 0.054647 | -0.0043493 | -0.0018371 | -0.0084684 | -0.0030676 | -0.03099 | 0.038367 | 0.0044667 | 0.0039242 | 0.12817 | 0.13733 | 0.16937 | 0.17853 | 0.13733 | 0.10529 | -0.018311 | 0.082397 | 0.15106 | 0.022888 | 0.027466 | 0.045776 | 0.068665 | -0.004578 | 121.8018 | 121.6782 | -0.036621 | 121.8338 | 121.875 | 0.19684 | -0.045776 | 121.7651 | 121.6919 | -0.14648 | 121.7789 | 121.7194 | 0.027466 | -0.12817 | 121.8338 | 121.8246 | 121.8658 | -0.19226 | 121.7239 | 121.7422 | 121.8475 | -0.17853
1722.2656 | 121.9482 | -121.6919 | 0.16479 | -0.016174 | 0.013693 | 0.0046527 | 0.0065347 | 0.05486 | -0.0058447 | -0.0046143 | -0.00083936 | -0.0039222 | -0.032058 | 0.036658 | 0.0025441 | 0.0062742 | 0.12817 | 0.17395 | 0.16937 | 0.19226 | 0.13275 | 0.10529 | -0.041199 | 0.10071 | 0.21515 | 0.064087 | 0.050354 | 0.050354 | 0.086975 | 0.004578 | 121.7972 | 121.6507 | -0.032044 | 121.8658 | 121.8842 | 0.23346 | -0.036621 | 121.7789 | 121.6965 | -0.11444 | 121.7926 | 121.756 | 0.059509 | -0.11444 | 121.8246 | 121.8201 | 121.8613 | -0.20599 | 121.7422 | 121.7422 | 121.907 | -0.16022
1724.0156 | 122.0078 | -121.7102 | 0.14648 | -0.00091566 | 0.016257 | 0.00038029 | 0.0026895 | 0.053365 | 0.0027003 | -0.0037597 | -0.0084684 | 0.0035546 | -0.033126 | 0.042639 | 0.0078847 | 0.0037106 | 0.064087 | -0.018311 | 0.013733 | 0.10071 | 0.19226 | 0.059509 | -0.082397 | 0.013733 | 0 | -0.1236 | 0.09613 | 0.09613 | 0.054932 | -0.041199 | 121.7697 | 121.6278 | 0.045777 | 121.6919 | 121.8109 | 0.18311 | -0.082397 | 121.7651 | 121.669 | -0.050354 | 121.7239 | 121.5866 | -0.082397 | -0.050354 | 121.9025 | 121.7743 | 121.7239 | -0.22888 | 121.8063 | 121.8063 | 121.7102 | -0.18768
1725.7031 | 122.0535 | -121.6736 | 0.13275 | -0.0085447 | 0.014975 | 0.0012347 | 0.0041849 | 0.054006 | -0.0011451 | -0.0035461 | -0.00083936 | 0.0012048 | -0.031417 | 0.042639 | 0.0046803 | 0.0030698 | 0.10071 | 0.073242 | 0.07782 | 0.15106 | 0.16479 | 0.045776 | -0.091553 | 0.054932 | 0.11444 | -0.050354 | 0.064087 | 0.086975 | 0.064087 | -0.041199 | 121.7194 | 121.582 | 0.032044 | 121.7468 | 121.8246 | 0.24261 | -0.032043 | 121.7377 | 121.6324 | -0.068664 | 121.7285 | 121.6232 | -0.009155 | -0.045776 | 121.8384 | 121.7743 | 121.7514 | -0.2243 | 121.7377 | 121.7606 | 121.788 | -0.17395
1727.4688 | 122.0398 | -121.6965 | 0.14191 | -0.00091566 | 0.01583 | 0.0025165 | 0.0058939 | 0.05422 | -0.0022131 | -0.0020507 | -0.00083936 | 0.000564 | -0.030777 | 0.041571 | 0.0048939 | 0.0064878 | 0.068665 | 0.068665 | 0.082397 | 0.12817 | 0.18768 | 0.045776 | -0.07782 | 0.054932 | 0.086975 | -0.045776 | 0.082397 | 0.07782 | 0.054932 | -0.050354 | 121.7422 | 121.6187 | 0.045776 | 121.7651 | 121.8246 | 0.20599 | -0.073242 | 121.7514 | 121.6461 | -0.05951 | 121.7514 | 121.6507 | 0.004578 | -0.064087 | 121.8842 | 121.7651 | 121.7789 | -0.21973 | 121.7789 | 121.7743 | 121.7834 | -0.19226
1729.2344 | 122.0215 | -121.6782 | 0.1236 | 0.014343 | 0.015189 | 0.00059389 | 0.0035441 | 0.052938 | -0.0045629 | -0.0035461 | -0.016098 | 0.0009912 | -0.031417 | 0.039221 | 0.0063893 | 0.0041378 | 0.032043 | 0.022888 | 0.032043 | 0.10986 | 0.16937 | 0.054932 | -0.09613 | -0.018311 | 0.064087 | -0.086975 | 0.082397 | 0.086975 | 0.032043 | -0.041199 | 121.7331 | 121.582 | 0.045777 | 121.701 | 121.788 | 0.20599 | -0.091553 | 121.7102 | 121.637 | -0.041199 | 121.6599 | 121.5912 | -0.045776 | -0.036621 | 121.8475 | 121.7102 | 121.7102 | -0.21973 | 121.7606 | 121.7651 | 121.7422 | -0.16479
1731 | 122.0123 | -121.6873 | 0.16022 | -0.0085447 | 0.014975 | 0.0048663 | 0.0043985 | 0.056783 | -0.0043493 | -0.0022643 | -0.0084684 | -0.001145 | -0.029281 | 0.041998 | 0.0061757 | 0.006915 | 0.027466 | 0 | 0.027466 | 0.10071 | 0.19226 | 0.018311 | -0.091553 | -0.032043 | 0.050354 | -0.073242 | 0.091553 | 0.10986 | 0.041199 | -0.036621 | 121.7056 | 121.5958 | 0.032044 | 121.6873 | 121.788 | 0.19226 | -0.13275 | 121.7285 | 121.6507 | -0.068664 | 121.6553 | 121.6141 | -0.036621 | -0.050354 | 121.8796 | 121.7148 | 121.7148 | -0.25177 | 121.7789 | 121.7972 | 121.7377 | -0.19684
1732.7031 | 121.9437 | -121.7285 | 0.16937 | -0.00091566 | 0.012198 | 0.0037983 | 0.0071757 | 0.055074 | -0.0088355 | -0.0035461 | -0.00083936 | -0.0032812 | -0.03099 | 0.038794 | -0.00087393 | 0.0064878 | 0.10071 | 0.16937 | 0.18768 | 0.1831 | 0.1236 | 0.07782 | -0.045776 | 0.064087 | 0.19684 | 0.054932 | 0.036621 | 0.036621 | 0.091553 | -0.009155 | 121.8063 | 121.6827 | -0.045777 | 121.8979 | 121.9116 | 0.22888 | -0.068665 | 121.8201 | 121.7194 | -0.13275 | 121.7926 | 121.7834 | 0.064087 | -0.13275 | 121.8521 | 121.8292 | 121.9162 | -0.21515 | 121.7651 | 121.7651 | 121.9254 | -0.17853
1734.4531 | 121.8475 | -121.8063 | 0.1831 | -0.00091566 | 0.013907 | 0.0023029 | 0.0065347 | 0.054433 | -0.0054175 | -0.0044007 | -0.00083936 | 0.0001368 | -0.03099 | 0.043921 | 0.0029713 | 0.0058468 | 0.036621 | 0.004578 | 0.050354 | 0.091553 | 0.17395 | 0.064087 | -0.07782 | -0.032043 | 0.050354 | -0.091553 | 0.059509 | 0.10071 | 0.022888 | -0.050354 | 121.8704 | 121.7285 | -0.009155 | 121.8109 | 121.8979 | 0.16937 | -0.14648 | 121.8292 | 121.756 | -0.1236 | 121.7743 | 121.7148 | -0.041199 | -0.082397 | 121.9803 | 121.843 | 121.8567 | -0.26092 | 121.8658 | 121.907 | 121.8567 | -0.23346
1736.2188 | 121.9025 | -121.8292 | 0.16479 | 0.0067138 | 0.013907 | 0.0037983 | 0.0041849 | 0.054647 | -0.0039221 | -0.0061095 | -0.0084684 | -0.0019996 | -0.030777 | 0.03858 | 0.0042531 | 0.0062742 | 0.050354 | 0.059509 | 0.07782 | 0.12817 | 0.16479 | 0.050354 | -0.07782 | -0.036621 | 0.059509 | -0.07782 | 0.073242 | 0.082397 | 0.045776 | -0.041199 | 121.8796 | 121.7514 | 0 | 121.8887 | 121.9574 | 0.20599 | -0.11444 | 121.875 | 121.788 | -0.091553 | 121.7926 | 121.7514 | -0.036621 | -0.082398 | 121.994 | 121.8796 | 121.907 | -0.24261 | 121.9025 | 121.9116 | 121.8887 | -0.20599
1737.9688 | 122.0627 | -121.7377 | 0.14191 | -0.00091566 | 0.016898 | 0.0031573 | 0.0029031 | 0.053152 | 0.0012049 | -0.0024779 | -0.00083936 | 0.0003504 | -0.030349 | 0.040289 | 0.0046803 | 0.0045652 | 0.068665 | 0.027466 | 0.07782 | 0.13733 | 0.17395 | 0.073242 | -0.054932 | 0.064087 | 0.086975 | -0.013733 | 0.036621 | 0.059509 | 0.073242 | -0.004578 | 121.8109 | 121.6827 | 0.032043 | 121.7651 | 121.875 | 0.19226 | -0.073242 | 121.8109 | 121.7331 | -0.10529 | 121.8018 | 121.7239 | -0.009155 | -0.082398 | 121.9116 | 121.8063 | 121.8155 | -0.19684 | 121.7743 | 121.7972 | 121.8246 | -0.14649
1739.6406 | 121.9482 | -121.7789 | 0.17395 | -0.0085447 | 0.012412 | 0.0027301 | 0.0086709 | 0.05721 | -0.0064855 | -0.0046143 | 0.0067901 | -0.0041358 | -0.032058 | 0.039435 | 0.00083507 | 0.0062742 | 0.14648 | 0.17853 | 0.18768 | 0.20142 | 0.14648 | 0.091553 | -0.041199 | 0.091553 | 0.18768 | 0.059509 | 0.027466 | 0.050354 | 0.068665 | -0.009155 | 121.8704 | 121.7377 | -0.027466 | 121.9574 | 121.9803 | 0.24262 | -0.027466 | 121.8475 | 121.7697 | -0.14648 | 121.8704 | 121.8384 | 0.068664 | -0.1236 | 121.9254 | 121.9254 | 121.9666 | -0.21515 | 121.8063 | 121.8292 | 121.9666 | -0.1831
1741.4219 | 122.0627 | -121.7331 | 0.12817 | -0.00091566 | 0.015616 | 0.0018757 | 0.0048257 | 0.05422 | -0.0013587 | -0.0024779 | 0.0067901 | 0.000564 | -0.029068 | 0.041144 | 0.0074575 | 0.0005062 | 0.073242 | 0.036621 | 0.045776 | 0.14191 | 0.16937 | 0.059509 | -0.064087 | 0.036621 | 0.082397 | -0.064087 | 0.07782 | 0.091553 | 0.041199 | -0.036621 | 121.7926 | 121.669 | 0.041199 | 121.7697 | 121.875 | 0.20599 | -0.054932 | 121.7743 | 121.6965 | -0.050354 | 121.7697 | 121.669 | -0.027466 | -0.036621 | 121.9025 | 121.8063 | 121.7789 | -0.19226 | 121.8109 | 121.8246 | 121.8155 | -0.1648
1743.1094 | 122.081 | -121.7331 | 0.1236 | 0.0067138 | 0.016898 | 0.0023029 | 0.0056803 | 0.05486 | -0.00093131 | -0.0033325 | 0.0067901 | 0.0020594 | -0.03099 | 0.040076 | 0.0066029 | 0.0037106 | 0.041199 | 0.013733 | 0.045776 | 0.1236 | 0.17395 | 0.054932 | -0.091553 | 0.022888 | 0.07782 | -0.07782 | 0.068665 | 0.064087 | 0.027466 | -0.036621 | 121.788 | 121.6415 | 0.050354 | 121.7468 | 121.8567 | 0.21515 | -0.082397 | 121.7606 | 121.6965 | -0.054931 | 121.756 | 121.6553 | -0.041199 | -0.059509 | 121.907 | 121.7743 | 121.7789 | -0.21515 | 121.8018 | 121.7972 | 121.8109 | -0.16022
1744.8594 | 121.9666 | -121.8201 | 0.15564 | -0.0085447 | 0.016257 | 0.0027301 | 0.0093119 | 0.056356 | -0.0047765 | -0.0039733 | -0.00083936 | -0.0015722 | -0.02864 | 0.044348 | 0.0021169 | 0.0037106 | 0.032043 | 0.022888 | 0.041199 | 0.091553 | 0.17853 | 0.050354 | -0.07782 | -0.022888 | 0.054932 | -0.082397 | 0.086975 | 0.10529 | 0.041199 | -0.050354 | 121.8704 | 121.7422 | 0.022888 | 121.843 | 121.9116 | 0.16937 | -0.1236 | 121.8613 | 121.7697 | -0.068665 | 121.7972 | 121.7377 | -0.032043 | -0.050354 | 121.9986 | 121.8521 | 121.8613 | -0.23346 | 121.907 | 121.9254 | 121.875 | -0.20599
1746.5781 | 122.0993 | -121.7743 | 0.14648 | -0.00091566 | 0.013266 | 0.0012347 | 0.0018351 | 0.052724 | -0.0022131 | -0.0033325 | -0.00083936 | -0.0013586 | -0.029708 | 0.041571 | 0.0053211 | 0.0071286 | 0.13275 | 0.11902 | 0.15564 | 0.17853 | 0.13275 | 0.086975 | -0.027466 | 0.091553 | 0.15106 | 0.009155 | 0.036621 | 0.050354 | 0.07782 | -0.009155 | 121.8613 | 121.7468 | -0.013733 | 121.8933 | 121.9528 | 0.20599 | -0.013733 | 121.8521 | 121.7651 | -0.10986 | 121.8658 | 121.7834 | 0.01831 | -0.09613 | 121.907 | 121.907 | 121.9299 | -0.17395 | 121.8109 | 121.8246 | 121.9254 | -0.15564
1748.2812 | 121.9986 | -121.8063 | 0.17395 | -0.00091566 | 0.014121 | 0.0042255 | 0.0082437 | 0.05486 | -0.0060583 | -0.0063233 | 0.0067901 | -0.0041358 | -0.03099 | 0.041571 | 0.0016895 | 0.0060604 | 0.13275 | 0.16479 | 0.17853 | 0.16937 | 0.13733 | 0.068665 | -0.041199 | 0.09613 | 0.19684 | 0.050354 | 0.032043 | 0.036621 | 0.068665 | -0.013733 | 121.875 | 121.7651 | -0.036621 | 121.9711 | 121.9757 | 0.21057 | -0.041199 | 121.875 | 121.7926 | -0.14191 | 121.9025 | 121.8567 | 0.064087 | -0.13733 | 121.9437 | 121.9391 | 121.9849 | -0.21515 | 121.8384 | 121.843 | 122.0032 | -0.18768
1750.0156 | 122.0673 | -121.7697 | 0.13733 | -0.0085447 | 0.016257 | 0.0014483 | 0.0048257 | 0.053792 | 0.00077749 | -0.0018371 | -0.00083936 | -0.0002906 | -0.029068 | 0.04093 | 0.0068165 | 0.003497 | 0.022888 | -0.027466 | 0.018311 | 0.09613 | 0.18768 | 0.050354 | -0.091553 | 0.004578 | 0.004578 | -0.13275 | 0.07782 | 0.086975 | 0.032043 | -0.041199 | 121.8201 | 121.6782 | 0.050354 | 121.7422 | 121.8658 | 0.18768 | -0.11444 | 121.8018 | 121.7285 | -0.059509 | 121.7743 | 121.637 | -0.091552 | -0.050354 | 121.9574 | 121.7926 | 121.788 | -0.22888 | 121.8475 | 121.8567 | 121.7743 | -0.17853
1751.7031 | 122.081 | -121.788 | 0.13275 | 0.0067138 | 0.017538 | 0.0018757 | 0.0063211 | 0.057424 | 0.00013669 | -0.0026917 | -0.0084684 | 0.0020594 | -0.031631 | 0.041785 | 0.0061757 | 0.0039242 | 0.091553 | 0.086975 | 0.086975 | 0.14648 | 0.15564 | 0.054932 | -0.086975 | 0.050354 | 0.086975 | -0.059509 | 0.082397 | 0.082397 | 0.054932 | -0.041199 | 121.843 | 121.7011 | 0.022889 | 121.875 | 121.9345 | 0.23346 | -0.041198 | 121.843 | 121.7468 | -0.050354 | 121.8384 | 121.7285 | -0.01831 | -0.050354 | 121.9437 | 121.8796 | 121.875 | -0.21973 | 121.8704 | 121.8704 | 121.875 | -0.17395
1753.4531 | 121.994 | -121.8292 | 0.16479 | -0.0085447 | 0.01113 | 0.0029437 | 0.0050393 | 0.052297 | -0.0066993 | -0.0033325 | 0.0067901 | -0.0024268 | -0.031417 | 0.041571 | 0.0012623 | 0.007983 | 0.082397 | 0.086975 | 0.11902 | 0.13733 | 0.14191 | 0.07782 | -0.050354 | 0.032043 | 0.10071 | -0.013733 | 0.045776 | 0.064087 | 0.059509 | -0.018311 | 121.907 | 121.7789 | -0.022888 | 121.9162 | 121.9666 | 0.18768 | -0.082398 | 121.8887 | 121.8109 | -0.11902 | 121.8613 | 121.8155 | 0.004578 | -0.10071 | 121.9711 | 121.9116 | 121.9482 | -0.21515 | 121.875 | 121.8933 | 121.9299 | -0.18311
1755.1406 | 122.0718 | -121.8246 | 0.16479 | -0.00091566 | 0.011557 | 0.0037983 | 0.0076029 | 0.056142 | -0.0060583 | -0.0056823 | -0.0084684 | -0.0039222 | -0.03099 | 0.038153 | 0.0029713 | 0.006915 | 0.091553 | 0.15106 | 0.15564 | 0.18768 | 0.14648 | 0.064087 | -0.036621 | 0.064087 | 0.17853 | 0.045776 | 0.022888 | 0.064087 | 0.086975 | -0.013733 | 121.8887 | 121.788 | -0.018311 | 121.9757 | 122.0123 | 0.2243 | -0.073242 | 121.9116 | 121.8109 | -0.14191 | 121.8887 | 121.8704 | 0.059509 | -0.10071 | 121.9711 | 121.9162 | 121.9803 | -0.20142 | 121.8475 | 121.8887 | 122.0032 | -0.17853
1756.8906 | 122.1542 | -121.8018 | 0.15106 | -0.0085447 | 0.018393 | 0.0016619 | 0.0058939 | 0.053365 | 0.00035029 | -0.0037597 | 0.0067901 | 0.0009912 | -0.030136 | 0.041785 | 0.0055349 | 0.003497 | 0.036621 | -0.018311 | 0.022888 | 0.09613 | 0.17853 | 0.054932 | -0.073242 | -0.004578 | 0.004578 | -0.10529 | 0.082397 | 0.086975 | 0.045776 | -0.045776 | 121.8567 | 121.7285 | 0.027466 | 121.7834 | 121.8979 | 0.16937 | -0.11444 | 121.8475 | 121.756 | -0.068665 | 121.7972 | 121.6965 | -0.05951 | -0.064087 | 121.9803 | 121.8384 | 121.8246 | -0.2243 | 121.8842 | 121.8887 | 121.8063 | -0.19684
1758.6562 | 122.0627 | -121.8475 | 0.16937 | -0.0085447 | 0.01348 | 0.0027301 | 0.0063211 | 0.05486 | -0.0060583 | -0.0037597 | -0.0084684 | -0.0034948 | -0.032486 | 0.039648 | 0.00083507 | 0.0060604 | 0.064087 | 0.07782 | 0.10986 | 0.16022 | 0.14648 | 0.073242 | -0.036621 | 0.041199 | 0.11444 | 0.009155 | 0.036621 | 0.073242 | 0.07782 | 0.009155 | 121.9208 | 121.8109 | -0.022889 | 121.9254 | 122.0078 | 0.19684 | -0.10529 | 121.9254 | 121.8567 | -0.13275 | 121.8887 | 121.8567 | 0 | -0.096131 | 121.994 | 121.9116 | 121.9574 | -0.20599 | 121.8842 | 121.9208 | 121.962 | -0.16022
1760.4219 | 121.9986 | -121.8704 | 0.15564 | -0.016174 | 0.011557 | 0.0055073 | 0.0050393 | 0.051229 | -0.0056311 | -0.0044007 | -0.0084684 | -0.0019996 | -0.033767 | 0.03858 | 0.0042531 | 0.0064878 | 0.068665 | 0.082397 | 0.09613 | 0.1236 | 0.1236 | 0.068665 | -0.050354 | 0.013733 | 0.073242 | -0.018311 | 0.032043 | 0.050354 | 0.054932 | -0.032043 | 121.9391 | 121.8201 | -0.032044 | 121.9528 | 121.994 | 0.17395 | -0.086975 | 121.9254 | 121.8384 | -0.1236 | 121.8842 | 121.8521 | 0.013732 | -0.10529 | 121.994 | 121.9391 | 121.9666 | -0.20599 | 121.9025 | 121.9208 | 121.9437 | -0.18768
1762.125 | 122.0215 | -121.8384 | 0.15564 | -0.0085447 | 0.013907 | 0.0048663 | 0.0050393 | 0.054006 | -0.0032813 | -0.0048279 | -0.0084684 | -0.0007178 | -0.031204 | 0.03858 | 0.0042531 | 0.0049924 | 0.1236 | 0.15564 | 0.16937 | 0.16937 | 0.12817 | 0.07782 | -0.045776 | 0.086975 | 0.19684 | 0.036621 | 0.032043 | 0.041199 | 0.064087 | -0.013733 | 121.9162 | 121.7926 | -0.027466 | 121.994 | 122.0078 | 0.21515 | -0.032044 | 121.9025 | 121.8246 | -0.1236 | 121.9254 | 121.875 | 0.050354 | -0.11444 | 121.9666 | 121.962 | 122.0078 | -0.20142 | 121.8704 | 121.8796 | 122.0352 | -0.16937
1763.875 | 122.0352 | -121.843 | 0.15564 | -0.00091566 | 0.014334 | 0.0029437 | 0.0071757 | 0.055501 | -0.0015723 | -0.0044007 | 0.0067901 | 0.0014184 | -0.031845 | 0.040289 | 0.0036123 | 0.0032834 | 0.004578 | 0.027466 | 0.032043 | 0.086975 | 0.16937 | 0.032043 | -0.086975 | -0.036621 | 0.032043 | -0.10986 | 0.091553 | 0.073242 | 0.022888 | -0.073242 | 121.875 | 121.756 | 0.013733 | 121.8704 | 121.9299 | 0.17395 | -0.15106 | 121.8658 | 121.7697 | -0.064087 | 121.8063 | 121.7331 | -0.036621 | -0.082398 | 122.0123 | 121.8475 | 121.875 | -0.24261 | 121.9345 | 121.9162 | 121.875 | -0.22888
1765.625 | 121.3715 | -121.1288 | 0.16022 | 0.014343 | 0.010062 | 0.0037983 | 0.0033305 | 0.052297 | -0.0024267 | -0.0037597 | -0.0084684 | -0.0041358 | -0.03099 | 0.039648 | 0.0048939 | 0.0056332 | 0.11902 | 0.13733 | 0.16937 | 0.15106 | 0.11444 | 0.091553 | -0.054932 | 0.082397 | 0.1236 | 0.004578 | 0.027466 | 0.032043 | 0.050354 | -0.009155 | 121.2204 | 121.0739 | -0.045776 | 121.2662 | 121.2799 | 0.20599 | -0.041198 | 121.1792 | 121.1197 | -0.13275 | 121.2112 | 121.1334 | 0.013733 | -0.12817 | 121.2433 | 121.2479 | 121.2982 | -0.21515 | 121.1563 | 121.1609 | 121.2524 | -0.16937
1767.4062 | 121.9391 | -121.6965 | 0.15106 | -0.00091566 | 0.013693 | 0.0046527 | 0.0058939 | 0.051443 | -0.0064855 | -0.0050415 | -0.0084684 | -0.0017858 | -0.032486 | 0.03858 | 0.0033985 | 0.0043516 | 0.10529 | 0.16479 | 0.16937 | 0.17853 | 0.14648 | 0.07782 | -0.032043 | 0.086975 | 0.17395 | 0.041199 | 0.041199 | 0.022888 | 0.059509 | -0.018311 | 121.7743 | 121.6644 | -0.004578 | 121.8613 | 121.875 | 0.21057 | -0.045776 | 121.756 | 121.6782 | -0.10986 | 121.7834 | 121.7377 | 0.05951 | -0.12817 | 121.843 | 121.8018 | 121.8658 | -0.18311 | 121.7377 | 121.7194 | 121.8704 | -0.16937
1769.1094 | 121.8933 | -121.7377 | 0.14191 | -0.016174 | 0.015189 | 0.0055073 | 0.0046121 | 0.054433 | -0.0034949 | -0.0048279 | 0.0067901 | -0.0022132 | -0.032058 | 0.037085 | 0.0042531 | 0.0047788 | 0.10529 | 0.16479 | 0.16479 | 0.16937 | 0.10986 | 0.073242 | -0.059509 | 0.086975 | 0.15106 | 0.013733 | 0.032043 | 0.036621 | 0.068665 | -0.022888 | 121.8109 | 121.6782 | -0.032044 | 121.9025 | 121.907 | 0.22888 | -0.036621 | 121.8063 | 121.7148 | -0.10986 | 121.8246 | 121.7514 | 0.036621 | -0.10529 | 121.8475 | 121.843 | 121.9025 | -0.20142 | 121.7697 | 121.7743 | 121.8887 | -0.16479
1770.8594 | 122.081 | -121.7606 | 0.13275 | -0.00091566 | 0.021384 | 0.00059389 | 0.0073893 | 0.053365 | 0.0039819 | -0.0041869 | -0.00083936 | 0.0012048 | -0.028427 | 0.043494 | 0.0059621 | 0.00072 | 0.036621 | -0.022888 | 0.013733 | 0.086975 | 0.17395 | 0.041199 | -0.091553 | -0.018311 | -0.004578 | -0.1236 | 0.059509 | 0.068665 | 0.018311 | -0.050354 | 121.8018 | 121.669 | 0.041199 | 121.7377 | 121.8475 | 0.17853 | -0.09613 | 121.7789 | 121.7102 | -0.073242 | 121.7422 | 121.637 | -0.073242 | -0.064086 | 121.9345 | 121.7972 | 121.7743 | -0.2243 | 121.8201 | 121.8292 | 121.756 | -0.18311
1772.625 | 121.994 | -121.7743 | 0.15106 | -0.00091566 | 0.011771 | 0.0052935 | 0.0061075 | 0.053152 | -0.0058447 | -0.0029053 | 0.0067901 | -0.0037086 | -0.032058 | 0.039648 | 0.0036123 | 0.0062742 | 0.059509 | 0.091553 | 0.10986 | 0.13733 | 0.14191 | 0.054932 | -0.073242 | 0.041199 | 0.13275 | 0 | 0.041199 | 0.059509 | 0.059509 | -0.022888 | 121.8292 | 121.7011 | -0.009155 | 121.8658 | 121.9116 | 0.21057 | -0.091553 | 121.8338 | 121.7514 | -0.10986 | 121.8155 | 121.7743 | 0.022888 | -0.091553 | 121.9162 | 121.8338 | 121.8842 | -0.2243 | 121.8155 | 121.8338 | 121.907 | -0.17395
1774.3906 | 122.0901 | -121.7651 | 0.1236 | -0.00091566 | 0.014121 | 0.0044391 | 0.0026895 | 0.05422 | -0.00071771 | -0.0014099 | -0.016098 | 0.0009912 | -0.033554 | 0.041785 | 0.0059621 | 0.0047788 | 0.027466 | -0.004578 | 0.004578 | 0.086975 | 0.16022 | 0.050354 | -0.091553 | 0 | 0.004578 | -0.1236 | 0.082397 | 0.054932 | 0.032043 | -0.068665 | 121.8155 | 121.6736 | 0.036621 | 121.7606 | 121.8521 | 0.17853 | -0.09613 | 121.7972 | 121.6965 | -0.041199 | 121.7651 | 121.6415 | -0.054931 | -0.068664 | 121.9254 | 121.7926 | 121.7697 | -0.21515 | 121.8475 | 121.8201 | 121.7697 | -0.19226
1776.0781 | 122.0169 | -121.8018 | 0.15564 | 0.0067138 | 0.013266 | 0.0042255 | 0.0078165 | 0.053792 | -0.0058447 | -0.0022643 | -0.00083936 | -0.002854 | -0.032699 | 0.040289 | 0.0019033 | 0.0037106 | 0.11902 | 0.17395 | 0.17853 | 0.16937 | 0.13275 | 0.082397 | -0.059509 | 0.086975 | 0.18768 | 0.032043 | 0.045776 | 0.032043 | 0.07782 | -0.022888 | 121.8842 | 121.7422 | -0.022889 | 121.9757 | 121.9711 | 0.22888 | -0.036621 | 121.8796 | 121.7789 | -0.10986 | 121.8887 | 121.8338 | 0.054931 | -0.1236 | 121.9345 | 121.9208 | 121.9803 | -0.21515 | 121.8475 | 121.8338 | 121.9894 | -0.17853
1777.8281 | 122.0627 | -121.8018 | 0.15106 | 0.0067138 | 0.013907 | 0.0020893 | 0.0031167 | 0.055074 | 0.00077749 | -0.0029053 | -0.0084684 | 0.0027002 | -0.031631 | 0.039648 | 0.0076711 | 0.0037106 | 0.11444 | 0.07782 | 0.07782 | 0.11902 | 0.16022 | 0.050354 | -0.068665 | 0.032043 | 0.068665 | -0.091553 | 0.059509 | 0.086975 | 0.050354 | -0.045776 | 121.8521 | 121.7331 | 0.009155 | 121.8796 | 121.9208 | 0.18768 | -0.036621 | 121.8521 | 121.756 | -0.091553 | 121.8338 | 121.7102 | -0.045777 | -0.064087 | 121.962 | 121.9162 | 121.8796 | -0.21973 | 121.8613 | 121.8887 | 121.8704 | -0.19684
1779.5938 | 122.0352 | -121.8155 | 0.14648 | -0.00091566 | 0.00878 | 0.0063617 | 0.0084573 | 0.053152 | -0.0077673 | -0.0050415 | 0.01442 | -0.0026404 | -0.030563 | 0.039648 | 0.00019427 | 0.0056332 | 0.064087 | 0.10071 | 0.13275 | 0.15564 | 0.13733 | 0.07782 | -0.07782 | 0.050354 | 0.15564 | 0.018311 | 0.032043 | 0.045776 | 0.050354 | -0.032043 | 121.8933 | 121.7377 | -0.009155 | 121.9162 | 121.9711 | 0.23346 | -0.082397 | 121.8658 | 121.7834 | -0.11444 | 121.8658 | 121.8338 | 0.050354 | -0.10071 | 121.9528 | 121.8796 | 121.9482 | -0.2243 | 121.8475 | 121.8613 | 121.9711 | -0.17853
1781.3594 | 122.1451 | -121.8063 | 0.11902 | -0.0085447 | 0.015402 | 0.0046527 | 0.0014079 | 0.052083 | 0.00099129 | -0.0014099 | -0.00083936 | 0.0018456 | -0.033126 | 0.039007 | 0.0070301 | 0.0049924 | 0.082397 | 0.059509 | 0.082397 | 0.13733 | 0.13733 | 0.054932 | -0.07782 | 0.059509 | 0.11444 | -0.022888 | 0.027466 | 0.036621 | 0.07782 | -0.018311 | 121.8613 | 121.7285 | 0.01831 | 121.8658 | 121.9437 | 0.21515 | -0.036622 | 121.8842 | 121.788 | -0.091553 | 121.8658 | 121.7834 | -0.004577 | -0.082398 | 121.9437 | 121.8887 | 121.8887 | -0.19684 | 121.8338 | 121.843 | 121.9208 | -0.13733
1783.0469 | 122.0078 | -121.8658 | 0.16479 | -0.00091566 | 0.010062 | 0.0042255 | 0.0048257 | 0.051656 | -0.0066993 | -0.0048279 | -0.0084684 | -0.0022132 | -0.031417 | 0.039007 | 0.0012623 | 0.0058468 | 0.064087 | 0.073242 | 0.10986 | 0.12817 | 0.14648 | 0.059509 | -0.059509 | 0.027466 | 0.10071 | -0.027466 | 0.032043 | 0.050354 | 0.064087 | -0.009155 | 121.9254 | 121.8063 | -0.018311 | 121.9391 | 121.994 | 0.18768 | -0.10071 | 121.9299 | 121.8567 | -0.13275 | 121.8933 | 121.8384 | -0.018311 | -0.11444 | 122.0123 | 121.9299 | 121.9757 | -0.2243 | 121.8979 | 121.9162 | 121.9666 | -0.17395
1784.7812 | 122.0169 | -121.8613 | 0.14191 | -0.0085447 | 0.015189 | 0.0031573 | 0.0071757 | 0.054006 | -0.0019995 | -0.0044007 | -0.00083936 | 0.0009912 | -0.030349 | 0.040289 | 0.00083507 | 0.006915 | 0.027466 | 0.022888 | 0.050354 | 0.086975 | 0.16022 | 0.041199 | -0.091553 | -0.027466 | 0.032043 | -0.10071 | 0.082397 | 0.086975 | 0.027466 | -0.050354 | 121.9025 | 121.7697 | 0.01831 | 121.8842 | 121.9482 | 0.17853 | -0.11444 | 121.8887 | 121.8109 | -0.05951 | 121.8338 | 121.7606 | -0.050354 | -0.054932 | 122.0215 | 121.8887 | 121.9116 | -0.23346 | 121.9437 | 121.9482 | 121.8933 | -0.19226
1786.5469 | 122.1497 | -121.8292 | 0.12817 | -0.00091566 | 0.014761 | 0.0031573 | 0.0020487 | 0.052297 | 0.0020593 | -0.0041869 | -0.00083936 | 0.000564 | -0.031845 | 0.039862 | 0.0080983 | 0.0054196 | 0.041199 | -0.018311 | 0.013733 | 0.09613 | 0.16479 | 0.054932 | -0.07782 | -0.009155 | -0.018311 | -0.13275 | 0.07782 | 0.064087 | 0.018311 | -0.032043 | 121.8842 | 121.7514 | 0.036621 | 121.8109 | 121.9254 | 0.17395 | -0.086975 | 121.8475 | 121.7972 | -0.050354 | 121.8201 | 121.6965 | -0.10071 | -0.064087 | 121.994 | 121.8704 | 121.843 | -0.20599 | 121.907 | 121.8933 | 121.8109 | -0.16022
1788.25 | 122.0993 | -121.8338 | 0.1236 | -0.00091566 | 0.015616 | 0.0040119 | 0.0031167 | 0.057424 | 0.0014185 | -0.0011963 | 0.0067901 | 0.0012048 | -0.031204 | 0.041144 | 0.0080983 | 0.0060604 | 0.045776 | 0.018311 | 0.027466 | 0.10529 | 0.16479 | 0.054932 | -0.086975 | -0.009155 | 0.027466 | -0.12817 | 0.068665 | 0.068665 | 0.022888 | -0.045776 | 121.8887 | 121.7468 | 0.041199 | 121.8521 | 121.9391 | 0.19226 | -0.07782 | 121.8567 | 121.788 | -0.054931 | 121.8246 | 121.7056 | -0.082398 | -0.054931 | 121.9986 | 121.8796 | 121.8613 | -0.21057 | 121.9025 | 121.9025 | 121.8613 | -0.16937
1789.9375 | 122.0032 | -121.8796 | 0.16479 | -0.00091566 | 0.015402 | 0.0031573 | 0.0069621 | 0.056783 | -0.0054175 | -0.0048279 | -0.00083936 | -0.004563 | -0.031631 | 0.039221 | 0.0014759 | 0.0056332 | 0.10071 | 0.13275 | 0.14648 | 0.17395 | 0.12817 | 0.064087 | -0.050354 | 0.032043 | 0.16022 | 0.009155 | 0.036621 | 0.050354 | 0.059509 | -0.022888 | 121.9437 | 121.8292 | -0.036621 | 122.0123 | 122.0535 | 0.2243 | -0.064087 | 121.9391 | 121.8567 | -0.12817 | 121.9116 | 121.8887 | 0.032043 | -0.11444 | 122.0078 | 121.9803 | 122.0261 | -0.21515 | 121.9162 | 121.9299 | 122.0398 | -0.18768
1791.6875 | 122.0581 | -121.8842 | 0.13733 | -0.00091566 | 0.015616 | 0.0029437 | 0.0076029 | 0.052724 | -0.00071771 | -0.0058959 | 0.0067901 | 0.0012048 | -0.027786 | 0.041357 | 0.0027577 | 0.0064878 | 0.027466 | 0.022888 | 0.032043 | 0.082397 | 0.17853 | 0.022888 | -0.091553 | -0.054932 | 0.036621 | -0.10986 | 0.086975 | 0.068665 | 0.032043 | -0.059509 | 121.907 | 121.7926 | 0.041199 | 121.907 | 121.9666 | 0.17395 | -0.10986 | 121.9162 | 121.8246 | -0.050354 | 121.8292 | 121.7743 | -0.050354 | -0.068664 | 122.0627 | 121.9116 | 121.9162 | -0.22888 | 121.9711 | 121.9528 | 121.9208 | -0.19684
1793.4375 | 122.1176 | -121.875 | 0.13275 | -0.00091566 | 0.017752 | 0.0031573 | 0.0020487 | 0.054433 | 0.00035029 | -0.0024779 | 0.0067901 | 0.002273 | -0.032486 | 0.039862 | 0.0059621 | 0.0043516 | 0.10529 | 0.07782 | 0.059509 | 0.1236 | 0.15564 | 0.045776 | -0.086975 | 0.022888 | 0.059509 | -0.07782 | 0.041199 | 0.073242 | 0.045776 | -0.032043 | 121.9208 | 121.788 | 0.022889 | 121.9528 | 121.9986 | 0.21057 | -0.027465 | 121.9208 | 121.843 | -0.091552 | 121.8979 | 121.7972 | -0.045777 | -0.059509 | 122.0306 | 121.9803 | 121.9345 | -0.21973 | 121.9162 | 121.9482 | 121.9345 | -0.16479
1795.125 | 122.1817 | -121.843 | 0.10529 | -0.0085447 | 0.01647 | 0.0020893 | 0.0031167 | 0.055288 | -0.0015723 | -0.0029053 | -0.0084684 | -7.6996e-05 | -0.029495 | 0.040076 | 0.0042531 | 0.005206 | 0.050354 | 0.018311 | 0.032043 | 0.11444 | 0.16937 | 0.032043 | -0.091553 | 0.013733 | 0.073242 | -0.082397 | 0.07782 | 0.068665 | 0.032043 | -0.032043 | 121.875 | 121.7514 | 0.064087 | 121.8613 | 121.9574 | 0.20599 | -0.054932 | 121.875 | 121.8109 | -0.027466 | 121.8567 | 121.7606 | -0.050354 | -0.036621 | 122.0123 | 121.8933 | 121.875 | -0.19684 | 121.9208 | 121.9116 | 121.9162 | -0.13733
1796.875 | 122.168 | -121.8613 | 0.1236 | -0.0085447 | 0.012839 | 0.0057209 | 0.0029031 | 0.054433 | -0.0032813 | -0.0039733 | -0.016098 | -0.0024268 | -0.033981 | 0.039648 | 0.0031849 | 0.005206 | 0.11902 | 0.11444 | 0.15106 | 0.17853 | 0.10986 | 0.07782 | -0.059509 | 0.068665 | 0.13733 | 0.018311 | 0.018311 | 0.054932 | 0.07782 | -0.009155 | 121.9391 | 121.8018 | -0.013733 | 121.9757 | 122.0398 | 0.23804 | -0.004577 | 121.9391 | 121.8521 | -0.10528 | 121.9299 | 121.8796 | 0.027466 | -0.068664 | 121.9711 | 121.9803 | 122.0123 | -0.1831 | 121.8796 | 121.9162 | 121.9986 | -0.13275
1798.5625 | 122.1085 | -121.8475 | 0.15564 | -0.0085447 | 0.01348 | 0.0046527 | 0.0054667 | 0.055288 | -0.0075537 | -0.0048279 | -0.0084684 | -0.0034948 | -0.033767 | 0.039648 | 0.0014759 | 0.0075558 | 0.10986 | 0.16022 | 0.15106 | 0.16022 | 0.12817 | 0.073242 | -0.064087 | 0.064087 | 0.17395 | 0.050354 | 0.041199 | 0.022888 | 0.07782 | -0.018311 | 121.9208 | 121.7834 | -0.027466 | 122.0078 | 122.0078 | 0.2243 | -0.045777 | 121.9254 | 121.8292 | -0.11444 | 121.9116 | 121.8979 | 0.068665 | -0.13275 | 121.9757 | 121.9574 | 121.9986 | -0.21973 | 121.8887 | 121.8704 | 122.0215 | -0.17395
1800.3125 | 122.0901 | -121.9025 | 0.15564 | -0.0085447 | 0.01113 | 0.0048663 | 0.0056803 | 0.052297 | -0.0032813 | -0.0056823 | -0.0084684 | -0.0041358 | -0.029708 | 0.03858 | 0.0033985 | 0.0062742 | 0.059509 | 0.073242 | 0.091553 | 0.13275 | 0.14648 | 0.050354 | -0.054932 | 0.004578 | 0.091553 | -0.009155 | 0.054932 | 0.059509 | 0.059509 | -0.036621 | 121.9528 | 121.8475 | -0.009156 | 121.9757 | 122.0352 | 0.18768 | -0.096131 | 121.962 | 121.8658 | -0.10071 | 121.907 | 121.8933 | 0.027466 | -0.096131 | 122.049 | 121.962 | 121.994 | -0.21057 | 121.9574 | 121.962 | 121.994 | -0.19226
1802 | 122.081 | -121.9162 | 0.14648 | -0.00091566 | 0.01583 | 0.0035847 | 0.0082437 | 0.053365 | -0.0011451 | -0.0029053 | 0.0067901 | -7.6996e-05 | -0.031204 | 0.041571 | 0.0033985 | 0.0049924 | 0.027466 | 0 | 0.041199 | 0.07782 | 0.16937 | 0.027466 | -0.09613 | -0.041199 | 0.036621 | -0.10529 | 0.091553 | 0.07782 | 0.013733 | -0.050354 | 121.9437 | 121.8201 | 0.022889 | 121.9162 | 121.994 | 0.17395 | -0.11902 | 121.9299 | 121.8658 | -0.054931 | 121.875 | 121.8109 | -0.054932 | -0.068664 | 122.0856 | 121.9437 | 121.9574 | -0.24261 | 122.0078 | 121.994 | 121.9528 | -0.19684
1803.75 | 122.1771 | -121.8933 | 0.1236 | -0.0085447 | 0.01583 | 0.0031573 | 0.0026895 | 0.052724 | 0.0048365 | -0.0024779 | -0.016098 | 0.0018456 | -0.030563 | 0.042639 | 0.0072437 | 0.0045652 | 0.032043 | -0.036621 | 0 | 0.086975 | 0.16479 | 0.050354 | -0.082397 | -0.018311 | -0.004578 | -0.1236 | 0.086975 | 0.082397 | 0.032043 | -0.054932 | 121.9437 | 121.8109 | 0.041199 | 121.8567 | 121.9803 | 0.16937 | -0.091553 | 121.9254 | 121.8384 | -0.036621 | 121.875 | 121.7697 | -0.068664 | -0.041199 | 122.0581 | 121.9254 | 121.8933 | -0.20599 | 121.9803 | 121.9757 | 121.8887 | -0.17853
1805.4531 | 122.1817 | -121.8933 | 0.12817 | 0.0067138 | 0.015189 | 0.0025165 | 0.0048257 | 0.054433 | 0.00013669 | -0.0035461 | 0.0067901 | 0.0027002 | -0.030777 | 0.042639 | 0.0053211 | 0.0064878 | 0.022888 | -0.022888 | 0.009155 | 0.091553 | 0.16937 | 0.036621 | -0.07782 | -0.013733 | -0.009155 | -0.11902 | 0.073242 | 0.07782 | 0.018311 | -0.050354 | 121.9299 | 121.8155 | 0.041199 | 121.8704 | 121.9849 | 0.16937 | -0.10529 | 121.9116 | 121.843 | -0.054932 | 121.8796 | 121.7743 | -0.068665 | -0.050354 | 122.0627 | 121.9162 | 121.9025 | -0.20599 | 121.9666 | 121.9711 | 121.8842 | -0.17853
1807.2188 | 122.1634 | -121.907 | 0.13275 | 0.014343 | 0.017752 | 0.0031573 | 0.0039713 | 0.054433 | 0.00077749 | -0.0026917 | 0.0067901 | 0.0009912 | -0.030136 | 0.041998 | 0.0072437 | 0.0064878 | 0.018311 | -0.050354 | -0.004578 | 0.091553 | 0.16479 | 0.050354 | -0.07782 | -0.022888 | -0.009155 | -0.13275 | 0.068665 | 0.086975 | 0.036621 | -0.041199 | 121.9574 | 121.8292 | 0.032044 | 121.8567 | 121.9986 | 0.16937 | -0.11444 | 121.9437 | 121.8658 | -0.064086 | 121.8842 | 121.7743 | -0.091552 | -0.045776 | 122.0718 | 121.9254 | 121.9025 | -0.21057 | 121.9757 | 121.994 | 121.8979 | -0.17395
1808.9688 | 122.2046 | -121.8933 | 0.11902 | -0.0085447 | 0.019888 | 0.0025165 | 0.0058939 | 0.052724 | 0.0014185 | -0.0020507 | -0.00083936 | -7.6996e-05 | -0.027786 | 0.040503 | 0.0033985 | 0.0047788 | 0.018311 | -0.036621 | 0.013733 | 0.082397 | 0.17395 | 0.059509 | -0.09613 | -0.036621 | -0.013733 | -0.1236 | 0.064087 | 0.082397 | 0.041199 | -0.045776 | 121.9528 | 121.7972 | 0.054931 | 121.8567 | 121.9757 | 0.17853 | -0.10071 | 121.9345 | 121.8475 | -0.054932 | 121.8567 | 121.7697 | -0.07782 | -0.036622 | 122.0673 | 121.9116 | 121.907 | -0.21515 | 121.9574 | 121.9757 | 121.8796 | -0.16479
1810.6562 | 122.0947 | -121.9391 | 0.14191 | -0.0085447 | 0.01113 | 0.0037983 | 0.0048257 | 0.050802 | -0.0088355 | -0.0052551 | 0.0067901 | -0.004563 | -0.02864 | 0.040503 | 0.00040787 | 0.007983 | 0.036621 | 0.054932 | 0.11444 | 0.13275 | 0.1236 | 0.07782 | -0.045776 | 0.009155 | 0.091553 | -0.032043 | 0.041199 | 0.050354 | 0.054932 | -0.022888 | 122.0169 | 121.8933 | -0.018311 | 121.994 | 122.0718 | 0.17853 | -0.10529 | 121.994 | 121.9162 | -0.10071 | 121.9482 | 121.907 | -0.009155 | -0.091553 | 122.0627 | 121.9757 | 122.0535 | -0.18768 | 121.9803 | 121.9894 | 122.0306 | -0.16479
1812.4219 | 122.1725 | -121.9025 | 0.1236 | 0.0067138 | 0.01583 | 0.0020893 | 0.00055326 | 0.05422 | 0.00056389 | -0.0031189 | -0.0084684 | 0.002273 | -0.031417 | 0.042212 | 0.0059621 | 0.0056332 | 0.027466 | -0.018311 | 0.018311 | 0.09613 | 0.15564 | 0.032043 | -0.11902 | -0.022888 | -0.009155 | -0.13733 | 0.073242 | 0.068665 | 0.027466 | -0.050354 | 121.9345 | 121.7834 | 0.032044 | 121.8842 | 121.9986 | 0.21515 | -0.09613 | 121.9299 | 121.8521 | -0.050354 | 121.8796 | 121.7651 | -0.086975 | -0.054931 | 122.0581 | 121.9299 | 121.9208 | -0.24261 | 121.9757 | 121.9711 | 121.8933 | -0.17395
1814.1719 | 122.2046 | -121.8933 | 0.09613 | -0.00091566 | 0.01583 | 0.0035847 | 0.0071757 | 0.051443 | -0.0026403 | -0.0035461 | -0.0084684 | 0.0009912 | -0.030136 | 0.040503 | 0.0055349 | 0.0056332 | 0.013733 | 0.004578 | 0.027466 | 0.10986 | 0.15564 | 0.032043 | -0.10071 | -0.027466 | 0.059509 | -0.11444 | 0.073242 | 0.068665 | 0.041199 | -0.041199 | 121.9254 | 121.7926 | 0.05951 | 121.8979 | 122.0032 | 0.21057 | -0.082397 | 121.9345 | 121.8521 | -0.022888 | 121.8658 | 121.7789 | -0.073242 | -0.027465 | 122.049 | 121.907 | 121.9208 | -0.19684 | 121.9666 | 121.962 | 121.9528 | -0.13733
1815.9219 | 122.0718 | -121.9254 | 0.15564 | 0.0067138 | 0.014975 | 0.0027301 | 0.0048257 | 0.055715 | -0.0062719 | -0.0056823 | -0.00083936 | -0.0030676 | -0.031204 | 0.039007 | 0.0010487 | 0.0062742 | 0.073242 | 0.13275 | 0.16022 | 0.16937 | 0.13275 | 0.07782 | -0.059509 | 0.013733 | 0.12817 | -0.032043 | 0.036621 | 0.054932 | 0.045776 | -0.045776 | 122.0032 | 121.8658 | -0.022889 | 122.0581 | 122.0947 | 0.22888 | -0.082398 | 121.9711 | 121.8796 | -0.11902 | 121.9391 | 121.8933 | 0.013733 | -0.10071 | 122.0581 | 121.9986 | 122.0856 | -0.21515 | 121.962 | 121.9803 | 122.0535 | -0.20142
1817.625 | 122.0856 | -121.9482 | 0.15564 | -0.0085447 | 0.014548 | 0.0033709 | 0.0088847 | 0.05187 | -0.0069129 | -0.0039733 | -0.00083936 | -0.0037086 | -0.028 | 0.038794 | 0.0014759 | 0.0054196 | 0.073242 | 0.11444 | 0.1236 | 0.15564 | 0.14191 | 0.082397 | -0.068665 | 0 | 0.091553 | -0.050354 | 0.050354 | 0.064087 | 0.050354 | -0.027466 | 122.0306 | 121.8796 | -0.013733 | 122.0627 | 122.1039 | 0.22431 | -0.082398 | 121.9986 | 121.9208 | -0.10529 | 121.9482 | 121.8979 | -0.022888 | -0.091553 | 122.0901 | 122.0215 | 122.0718 | -0.22431 | 121.9986 | 122.0123 | 122.0398 | -0.18311
1819.375 | 122.2 | -121.9254 | 0.11444 | 0.0067138 | 0.017325 | 0.0016619 | 0.0046121 | 0.052511 | 0.0033411 | 0.00051268 | -0.00083936 | 0.0014184 | -0.030349 | 0.041144 | 0.0066029 | 0.0032834 | 0.07782 | 0.073242 | 0.068665 | 0.14648 | 0.16479 | 0.036621 | -0.10071 | 0.036621 | 0.07782 | -0.073242 | 0.041199 | 0.068665 | 0.041199 | -0.041199 | 121.962 | 121.8246 | 0.050354 | 121.9986 | 122.0718 | 0.24719 | -0.036621 | 121.9666 | 121.8842 | -0.073242 | 121.962 | 121.8521 | -0.032043 | -0.045776 | 122.0901 | 122.0032 | 121.994 | -0.21515 | 121.9666 | 121.994 | 122.0032 | -0.15564
1821.0781 | 122.2412 | -121.907 | 0.11444 | -0.00091566 | 0.012625 | 0.0010211 | 0.0039713 | 0.055288 | -0.00093131 | -0.0024779 | -0.00083936 | -0.0024268 | -0.032913 | 0.042639 | 0.0038259 | 0.0047788 | 0.064087 | 0.054932 | 0.082397 | 0.13733 | 0.14191 | 0.073242 | -0.064087 | 0.07782 | 0.091553 | -0.009155 | 0.032043 | 0.050354 | 0.091553 | -0.013733 | 121.9803 | 121.843 | 0.027466 | 121.962 | 122.0444 | 0.20142 | -0.050354 | 121.9986 | 121.8933 | -0.082398 | 121.9849 | 121.8979 | 0.004578 | -0.064087 | 122.049 | 121.9711 | 121.9894 | -0.17853 | 121.9391 | 121.9574 | 121.9986 | -0.12817
1822.8281 | 122.2549 | -121.9208 | 0.12817 | -0.00091566 | 0.019034 | 0.0016619 | 0.0033305 | 0.056142 | 0.00035029 | -0.0035461 | -0.00083936 | 0.000564 | -0.029068 | 0.043707 | 0.0046803 | 0.0028562 | 0.064087 | 0.059509 | 0.068665 | 0.13275 | 0.15564 | 0.045776 | -0.09613 | 0.036621 | 0.086975 | -0.059509 | 0.073242 | 0.07782 | 0.050354 | -0.041199 | 121.9666 | 121.8246 | 0.027466 | 121.9803 | 122.0535 | 0.22888 | -0.064087 | 121.9711 | 121.8796 | -0.054932 | 121.9574 | 121.8613 | -0.01831 | -0.050354 | 122.0764 | 121.9849 | 121.9894 | -0.2243 | 121.994 | 121.9986 | 122.0078 | -0.16937
1824.5938 | 122.2046 | -121.9437 | 0.11902 | -0.00091566 | 0.016898 | 0.0040119 | 0.0024759 | 0.05422 | 0.00013669 | -0.0039733 | 0.0067901 | 0.0014184 | -0.02864 | 0.043921 | 0.0076711 | 0.005206 | 0.054932 | 0.027466 | 0.050354 | 0.11444 | 0.16022 | 0.041199 | -0.091553 | -0.009155 | 0.022888 | -0.11902 | 0.059509 | 0.091553 | 0.027466 | -0.050354 | 121.9849 | 121.8521 | 0.041198 | 121.9711 | 122.0581 | 0.20599 | -0.064087 | 121.9711 | 121.8933 | -0.05951 | 121.9345 | 121.8246 | -0.068665 | -0.027466 | 122.1039 | 121.9986 | 121.994 | -0.21057 | 122.0032 | 122.0352 | 121.9666 | -0.16937
1826.2969 | 122.1497 | -121.9711 | 0.14648 | -0.00091566 | 0.014761 | 0.0050799 | 0.0086709 | 0.053792 | -0.0086219 | -0.0037597 | -0.00083936 | -0.0043494 | -0.030349 | 0.040076 | 0.00019427 | 0.0064878 | 0.12817 | 0.15106 | 0.16022 | 0.16479 | 0.13733 | 0.068665 | -0.068665 | 0.064087 | 0.18768 | 0.050354 | 0.013733 | 0.054932 | 0.073242 | -0.018311 | 122.0398 | 121.9025 | -0.009155 | 122.1222 | 122.1359 | 0.23346 | -0.01831 | 122.0444 | 121.9528 | -0.13275 | 122.0352 | 122.0215 | 0.068665 | -0.091552 | 122.1085 | 122.0993 | 122.1313 | -0.21515 | 121.9849 | 122.0261 | 122.1588 | -0.16479
1829.4688 | 122.2687 | -121.9254 | 0.12817 | -0.00091566 | 0.018607 | 0.0035847 | 0.0063211 | 0.05486 | -0.00071771 | -0.0014099 | 0.01442 | -7.6996e-05 | -0.030136 | 0.041357 | 0.0066029 | 0.0039242 | 0.054932 | 0.022888 | 0.059509 | 0.14191 | 0.17395 | 0.032043 | -0.07782 | 0.032043 | 0.082397 | -0.073242 | 0.059509 | 0.059509 | 0.032043 | -0.041199 | 121.9574 | 121.8475 | 0.045776 | 121.9482 | 122.0673 | 0.21973 | -0.073242 | 121.9574 | 121.8842 | -0.068665 | 121.9574 | 121.8521 | -0.032043 | -0.068665 | 122.0993 | 121.9803 | 121.9849 | -0.20599 | 121.9849 | 121.9849 | 122.0078 | -0.16937
1833.4531 | 122.2458 | -121.962 | 0.1236 | -0.00091566 | 0.022025 | 0.0012347 | 0.0080301 | 0.053365 | 0.0018457 | -0.0022643 | -0.00083936 | 0.000564 | -0.029922 | 0.041571 | 0.0033985 | 0.0030698 | 0.09613 | 0.073242 | 0.073242 | 0.13733 | 0.16479 | 0.045776 | -0.10529 | 0.027466 | 0.082397 | -0.073242 | 0.064087 | 0.068665 | 0.022888 | -0.036621 | 122.0078 | 121.8567 | 0.041199 | 122.0352 | 122.0993 | 0.24262 | -0.027466 | 121.9849 | 121.9254 | -0.059509 | 121.9894 | 121.8887 | -0.036621 | -0.054931 | 122.1268 | 122.0581 | 122.0352 | -0.22888 | 122.0261 | 122.0306 | 122.0444 | -0.16022
1839.6406 | 122.1634 | -122.0032 | 0.16937 | -0.00091566 | 0.012839 | 0.0059345 | 0.0056803 | 0.052511 | -0.0073401 | -0.0046143 | 0.0067901 | -0.0043494 | -0.032272 | 0.038794 | 0.0021169 | 0.007983 | 0.064087 | 0.091553 | 0.11444 | 0.11902 | 0.11444 | 0.059509 | -0.064087 | 0.004578 | 0.09613 | -0.009155 | 0.050354 | 0.036621 | 0.041199 | 0 | 122.0627 | 121.9391 | -0.054932 | 122.0947 | 122.1222 | 0.18311 | -0.10529 | 122.0444 | 122.0032 | -0.11902 | 122.0078 | 121.994 | -0.009155 | -0.13275 | 122.1176 | 122.0673 | 122.1176 | -0.23346 | 122.0535 | 122.0398 | 122.0993 | -0.16937
1841.4844 | 122.1588 | -121.994 | 0.1236 | -0.00091566 | 0.014121 | 0.0063617 | 0.0046121 | 0.055074 | -0.0030677 | -0.0061095 | -0.0084684 | -0.0022132 | -0.031204 | 0.039648 | 0.0029713 | 0.0060604 | 0.064087 | 0.073242 | 0.068665 | 0.1236 | 0.15106 | 0.068665 | -0.07782 | -0.027466 | 0.045776 | -0.082397 | 0.050354 | 0.082397 | 0.027466 | -0.054932 | 122.0627 | 121.9162 | 0.027466 | 122.0673 | 122.1176 | 0.20142 | -0.059509 | 122.0215 | 121.9391 | -0.073242 | 121.9666 | 121.9116 | -0.027465 | -0.041199 | 122.1451 | 122.0581 | 122.0627 | -0.20142 | 122.0444 | 122.0764 | 122.0398 | -0.17853
1843.1875 | 122.1771 | -122.0169 | 0.14648 | 0.0067138 | 0.011771 | 0.0048663 | 0.0046121 | 0.05187 | -0.0047765 | -0.0031189 | -0.00083936 | -0.0037086 | -0.030136 | 0.037298 | 0.0040395 | 0.0073422 | 0.054932 | 0.091553 | 0.10986 | 0.11902 | 0.13275 | 0.068665 | -0.054932 | 0.013733 | 0.09613 | -0.013733 | 0.045776 | 0.050354 | 0.064087 | -0.027466 | 122.0856 | 121.962 | -0.013733 | 122.1085 | 122.1359 | 0.17395 | -0.091552 | 122.081 | 121.9894 | -0.10071 | 122.0306 | 122.0032 | 0.013733 | -0.09613 | 122.1497 | 122.0718 | 122.1268 | -0.20142 | 122.0627 | 122.0673 | 122.113 | -0.17395
1844.9375 | 122.2092 | -122.0261 | 0.16022 | -0.0085447 | 0.0094208 | 0.0050799 | 0.0026895 | 0.052724 | -0.0045629 | -0.0052551 | 0.0067901 | -0.0039222 | -0.033554 | 0.037939 | 0.0027577 | 0.0073422 | 0.050354 | 0.073242 | 0.10071 | 0.15106 | 0.14191 | 0.059509 | -0.073242 | 0.009155 | 0.07782 | -0.032043 | 0.027466 | 0.050354 | 0.050354 | -0.027466 | 122.0856 | 121.9528 | -0.01831 | 122.0993 | 122.1771 | 0.2243 | -0.10986 | 122.0764 | 121.9986 | -0.13275 | 122.0352 | 121.994 | -0.004577 | -0.10986 | 122.168 | 122.0764 | 122.1268 | -0.23346 | 122.0535 | 122.0764 | 122.1039 | -0.18768
1846.7031 | 122.2595 | -121.9894 | 0.1236 | -0.00091566 | 0.015616 | 0.0050799 | 0.0029031 | 0.052724 | -0.0015723 | -0.0054687 | 0.0067901 | 0.0001368 | -0.029922 | 0.040289 | 0.0055349 | 0.0060604 | 0.022888 | 0 | 0.022888 | 0.09613 | 0.18768 | 0.045776 | -0.10529 | -0.018311 | 0.036621 | -0.1236 | 0.082397 | 0.064087 | 0.022888 | -0.054932 | 122.0352 | 121.8842 | 0.064087 | 121.9894 | 122.0856 | 0.20142 | -0.10071 | 122.0123 | 121.9345 | -0.041199 | 121.9711 | 121.8658 | -0.068664 | -0.059509 | 122.1771 | 122.0123 | 122.0123 | -0.22888 | 122.0718 | 122.0535 | 122.0261 | -0.17853
1848.4688 | 122.2046 | -122.0078 | 0.13733 | 0.0067138 | 0.013907 | 0.0033709 | 0.0065347 | 0.055929 | -0.0047765 | -0.0039733 | -0.0084684 | -0.0015722 | -0.032272 | 0.039862 | 0.0038259 | 0.0056332 | 0.1236 | 0.14191 | 0.16022 | 0.16479 | 0.1236 | 0.07782 | -0.064087 | 0.07782 | 0.11444 | 0.022888 | 0.022888 | 0.050354 | 0.073242 | 0.004578 | 122.0856 | 121.9437 | -0.013733 | 122.1497 | 122.1725 | 0.22888 | -0.013733 | 122.081 | 122.0123 | -0.11444 | 122.0856 | 122.0306 | 0.01831 | -0.086975 | 122.1313 | 122.1313 | 122.168 | -0.20142 | 122.0306 | 122.0581 | 122.1222 | -0.13275
1850.1562 | 122.168 | -122.0352 | 0.14191 | -0.0085447 | 0.014121 | 0.0078571 | 0.0050393 | 0.052938 | -0.0047765 | -0.0063233 | -0.00083936 | -0.0017858 | -0.030349 | 0.039435 | 0.0033985 | 0.0056332 | 0.11902 | 0.14191 | 0.16022 | 0.17853 | 0.13275 | 0.086975 | -0.054932 | 0.068665 | 0.17853 | 0.022888 | 0.036621 | 0.027466 | 0.073242 | -0.009155 | 122.1222 | 121.9803 | -0.009156 | 122.1771 | 122.2137 | 0.23346 | -0.022888 | 122.1085 | 122.0261 | -0.10529 | 122.1039 | 122.0581 | 0.032043 | -0.11444 | 122.168 | 122.1542 | 122.1954 | -0.19684 | 122.0718 | 122.0627 | 122.2137 | -0.15106
1851.8438 | 122.2321 | -122.0398 | 0.16022 | 0.0067138 | 0.015402 | 0.0057209 | 0.0061075 | 0.052511 | -0.0039221 | -0.0041869 | -0.00083936 | -0.0032812 | -0.03334 | 0.039007 | 0.0023305 | 0.005206 | 0.036621 | 0.07782 | 0.09613 | 0.13733 | 0.1236 | 0.064087 | -0.073242 | 0.018311 | 0.10071 | -0.018311 | 0.041199 | 0.050354 | 0.045776 | -0.032043 | 122.1039 | 121.9666 | -0.036621 | 122.1176 | 122.1771 | 0.21057 | -0.1236 | 122.0856 | 122.0078 | -0.11902 | 122.0581 | 122.0215 | 0.013732 | -0.10986 | 122.1634 | 122.0764 | 122.1359 | -0.23346 | 122.081 | 122.0901 | 122.1405 | -0.19226
1853.5938 | 122.2641 | -122.0078 | 0.13275 | -0.0085447 | 0.017325 | 0.0061481 | 0.0061075 | 0.051229 | -0.00050411 | -0.0046143 | -0.00083936 | -0.0005042 | -0.029068 | 0.039435 | 0.0063893 | 0.0032834 | 0.032043 | 0.013733 | 0.009155 | 0.09613 | 0.18768 | 0.027466 | -0.091553 | -0.018311 | 0.027466 | -0.11444 | 0.07782 | 0.073242 | 0.018311 | -0.050354 | 122.0352 | 121.9162 | 0.054932 | 122.0215 | 122.1039 | 0.18768 | -0.10071 | 122.0261 | 121.9574 | -0.054931 | 121.9894 | 121.8933 | -0.064087 | -0.059509 | 122.1954 | 122.0398 | 122.0169 | -0.2243 | 122.0856 | 122.081 | 122.0352 | -0.18311
1855.2812 | 122.287 | -121.994 | 0.12817 | -0.0085447 | 0.017111 | 0.0023029 | 0.0048257 | 0.05486 | 0.0014185 | -0.0022643 | -0.00083936 | 0.003341 | -0.030136 | 0.041785 | 0.0051075 | 0.0045652 | 0.082397 | 0.073242 | 0.07782 | 0.14191 | 0.16937 | 0.045776 | -0.082397 | 0.036621 | 0.082397 | -0.073242 | 0.050354 | 0.082397 | 0.050354 | -0.036621 | 122.0398 | 121.9116 | 0.041199 | 122.0673 | 122.1359 | 0.2243 | -0.045777 | 122.0444 | 121.9574 | -0.07782 | 122.0306 | 121.9208 | -0.036621 | -0.045777 | 122.1634 | 122.0764 | 122.0718 | -0.21057 | 122.0444 | 122.0764 | 122.0764 | -0.1648
1857.0312 | 122.3373 | -122.0306 | 0.11444 | -0.00091566 | 0.014761 | 0.0023029 | 0.0033305 | 0.053365 | -7.6908e-05 | -0.00055532 | -0.00083936 | -0.0005042 | -0.028213 | 0.040503 | 0.0063893 | 0.0049924 | 0.050354 | 0.054932 | 0.073242 | 0.11902 | 0.15106 | 0.068665 | -0.073242 | 0.073242 | 0.10529 | -0.022888 | 0.054932 | 0.041199 | 0.068665 | -0.018311 | 122.0993 | 121.9574 | 0.036621 | 122.0856 | 122.1497 | 0.19226 | -0.064087 | 122.0993 | 122.0123 | -0.059509 | 122.1039 | 122.0078 | -0.004577 | -0.073242 | 122.1817 | 122.081 | 122.1039 | -0.18768 | 122.0856 | 122.0718 | 122.1359 | -0.13275
1858.7969 | 122.3282 | -122.0718 | 0.11902 | -0.00091566 | 0.014975 | 0.0042255 | 0.0056803 | 0.054647 | -0.00071771 | -0.00098272 | -0.023727 | 0.0003504 | -0.030777 | 0.039648 | 0.0057485 | 0.0043516 | 0.041199 | 0.022888 | 0.036621 | 0.10529 | 0.16479 | 0.045776 | -0.073242 | 0.045776 | 0.064087 | -0.032043 | 0.050354 | 0.050354 | 0.050354 | -0.032043 | 122.1176 | 121.9986 | 0.045776 | 122.0947 | 122.1771 | 0.17853 | -0.07782 | 122.1222 | 122.0398 | -0.068665 | 122.1176 | 122.0398 | 0 | -0.068665 | 122.2366 | 122.113 | 122.1085 | -0.19226 | 122.1222 | 122.1222 | 122.1359 | -0.15106
1860.5625 | 122.3053 | -122.0764 | 0.1236 | -0.0085447 | 0.013693 | 0.0031573 | 0.0088847 | 0.054433 | -0.0028539 | -0.0048279 | 0.0067901 | -0.0002906 | -0.029495 | 0.039435 | 0.0025441 | 0.0073422 | 0.018311 | 0.004578 | 0.027466 | 0.10071 | 0.14648 | 0.041199 | -0.10071 | -0.036621 | 0.036621 | -0.10529 | 0.064087 | 0.073242 | 0.022888 | -0.059509 | 122.1176 | 121.9757 | 0.022888 | 122.081 | 122.1771 | 0.20142 | -0.10528 | 122.0993 | 122.0169 | -0.059509 | 122.0398 | 121.9711 | -0.045777 | -0.050354 | 122.2229 | 122.0947 | 122.1039 | -0.2243 | 122.1405 | 122.1497 | 122.113 | -0.1831
1862.2656 | 122.3099 | -122.0306 | 0.11902 | -0.0085447 | 0.015402 | 0.0016619 | 0.0048257 | 0.054647 | -0.0034949 | -0.0039733 | -0.00083936 | -0.0039222 | -0.029495 | 0.041998 | 0.0053211 | 0.0054196 | 0.1236 | 0.11444 | 0.14191 | 0.17395 | 0.11444 | 0.068665 | -0.054932 | 0.09613 | 0.12817 | 0.022888 | 0.022888 | 0.045776 | 0.068665 | -0.004578 | 122.0993 | 121.9757 | -0.004578 | 122.1451 | 122.2046 | 0.22888 | 0.004577 | 122.0993 | 122.0261 | -0.096131 | 122.1268 | 122.0535 | 0.027466 | -0.073243 | 122.1451 | 122.1542 | 122.1725 | -0.17395 | 122.0535 | 122.0764 | 122.1588 | -0.1236
1864.0156 | 122.3511 | -122.0306 | 0.10986 | -0.00091566 | 0.016257 | 0.0027301 | 0.0061075 | 0.054647 | 0.00099129 | -0.0033325 | -0.00083936 | 0.0024866 | -0.02864 | 0.041785 | 0.0031849 | 0.0028562 | 0.045776 | 0.036621 | 0.041199 | 0.11902 | 0.16937 | 0.022888 | -0.10529 | 0.022888 | 0.068665 | -0.07782 | 0.082397 | 0.059509 | 0.036621 | -0.050354 | 122.0535 | 121.9254 | 0.05951 | 122.0673 | 122.1497 | 0.22431 | -0.064087 | 122.0673 | 121.9803 | -0.027466 | 122.0535 | 121.9528 | -0.027466 | -0.050354 | 122.2 | 122.0764 | 122.0718 | -0.21515 | 122.113 | 122.0901 | 122.0993 | -0.16022
1865.7031 | 122.3007 | -122.0764 | 0.11902 | -0.0085447 | 0.01647 | 0.0050799 | 0.0035441 | 0.052511 | 0.0020593 | -0.0014099 | -0.00083936 | 0.0024866 | -0.029281 | 0.040503 | 0.0059621 | 0.0058468 | 0.013733 | -0.022888 | 0.013733 | 0.09613 | 0.14648 | 0.032043 | -0.091553 | -0.036621 | -0.013733 | -0.13733 | 0.07782 | 0.07782 | 0.027466 | -0.041199 | 122.1085 | 121.9849 | 0.027465 | 122.0535 | 122.1725 | 0.18768 | -0.10529 | 122.1039 | 122.0352 | -0.041199 | 122.0398 | 121.9391 | -0.09613 | -0.041199 | 122.2229 | 122.0901 | 122.0901 | -0.21057 | 122.1542 | 122.1542 | 122.0627 | -0.16022
1867.4688 | 122.2412 | -122.0993 | 0.15106 | 0.0067138 | 0.012839 | 0.0040119 | 0.0073893 | 0.051656 | -0.0064855 | -0.0029053 | -0.00083936 | -0.0034948 | -0.030136 | 0.040289 | 0.0016895 | 0.0064878 | 0.086975 | 0.10986 | 0.13275 | 0.15564 | 0.10986 | 0.064087 | -0.054932 | 0.045776 | 0.1236 | -0.004578 | 0.027466 | 0.032043 | 0.064087 | -0.004578 | 122.1634 | 122.0444 | -0.041199 | 122.2092 | 122.2549 | 0.21057 | -0.064087 | 122.1634 | 122.0947 | -0.1236 | 122.1451 | 122.0947 | 0 | -0.11902 | 122.2092 | 122.1863 | 122.2321 | -0.20599 | 122.1268 | 122.1313 | 122.2229 | -0.15564
1869.1719 | 122.3145 | -122.0352 | 0.1236 | -0.016174 | 0.018179 | 0.0035847 | 0.0039713 | 0.052938 | -0.00071771 | -0.0029053 | -0.00083936 | 0.0027002 | -0.03099 | 0.042212 | 0.0089527 | 0.0028562 | 0.082397 | 0.059509 | 0.059509 | 0.1236 | 0.14191 | 0.032043 | -0.086975 | 0.022888 | 0.07782 | -0.073242 | 0.059509 | 0.068665 | 0.036621 | -0.041199 | 122.0673 | 121.9482 | 0.018311 | 122.0947 | 122.1588 | 0.21057 | -0.041199 | 122.0718 | 121.994 | -0.064087 | 122.0581 | 121.962 | -0.032043 | -0.054931 | 122.1771 | 122.1176 | 122.0947 | -0.21057 | 122.0947 | 122.1039 | 122.113 | -0.16479
1870.9219 | 122.2412 | -122.0764 | 0.14648 | -0.00091566 | 0.0085664 | 0.0059345 | 0.0043985 | 0.052724 | -0.0077673 | -0.0031189 | -0.00083936 | -0.0049902 | -0.032913 | 0.038794 | 0.0051075 | 0.0064878 | 0.091553 | 0.15106 | 0.17853 | 0.16937 | 0.11444 | 0.059509 | -0.064087 | 0.068665 | 0.18768 | 0.032043 | 0.027466 | 0.027466 | 0.054932 | -0.013733 | 122.1359 | 122.0123 | -0.032043 | 122.2275 | 122.2458 | 0.23346 | -0.054931 | 122.1313 | 122.0627 | -0.11902 | 122.1451 | 122.1085 | 0.045776 | -0.11902 | 122.1909 | 122.168 | 122.2549 | -0.21057 | 122.1039 | 122.1039 | 122.2641 | -0.16022
1872.625 | 122.3694 | -122.0581 | 0.13275 | -0.016174 | 0.014548 | 0.0014483 | 0.0054667 | 0.056569 | -0.0011451 | -0.0039733 | -0.00083936 | -7.6996e-05 | -0.029281 | 0.041571 | 0.0033985 | 0.005206 | 0.018311 | 0.004578 | 0.013733 | 0.10529 | 0.16479 | 0.022888 | -0.10529 | -0.018311 | 0.054932 | -0.09613 | 0.07782 | 0.073242 | 0.027466 | -0.045776 | 122.081 | 121.9528 | 0.032044 | 122.0627 | 122.1634 | 0.21057 | -0.11444 | 122.0856 | 122.0123 | -0.054931 | 122.0398 | 121.962 | -0.050354 | -0.059509 | 122.2229 | 122.0764 | 122.0718 | -0.23804 | 122.1359 | 122.1313 | 122.113 | -0.17853
1874.3906 | 122.3557 | -122.0856 | 0.11902 | -0.00091566 | 0.013266 | 0.0035847 | 0.0048257 | 0.05486 | -0.00029051 | -0.0014099 | -0.00083936 | 0.0003504 | -0.032913 | 0.039862 | 0.0044667 | 0.005206 | -0.009155 | 0.009155 | 0.027466 | 0.09613 | 0.17395 | 0.032043 | -0.10529 | -0.032043 | 0.027466 | -0.10529 | 0.068665 | 0.064087 | 0.013733 | -0.059509 | 122.1176 | 121.9803 | 0.054931 | 122.0947 | 122.1817 | 0.20142 | -0.12817 | 122.0993 | 122.0261 | -0.050354 | 122.0535 | 121.9803 | -0.045777 | -0.054932 | 122.2595 | 122.0764 | 122.113 | -0.22431 | 122.1542 | 122.1497 | 122.113 | -0.17853
1876.1562 | 122.2641 | -122.0764 | 0.16937 | -0.00091566 | 0.013907 | 0.0059345 | 0.0063211 | 0.054006 | -0.0060583 | -0.0058959 | 0.0067901 | -0.0056312 | -0.030563 | 0.038153 | 0.0033985 | 0.0077694 | 0.09613 | 0.16479 | 0.16022 | 0.1831 | 0.13733 | 0.064087 | -0.059509 | 0.064087 | 0.1831 | 0.036621 | 0.032043 | 0.032043 | 0.050354 | -0.022888 | 122.1405 | 122.0169 | -0.032044 | 122.2412 | 122.2595 | 0.24261 | -0.073243 | 122.1268 | 122.0535 | -0.13733 | 122.1405 | 122.113 | 0.059509 | -0.13733 | 122.2137 | 122.1725 | 122.2366 | -0.22888 | 122.1085 | 122.1085 | 122.2595 | -0.19226
1877.9219 | 122.4014 | -122.0627 | 0.11902 | -0.00091566 | 0.013907 | 0.0025165 | 0.0043985 | 0.053792 | -0.0015723 | -0.0033325 | -0.0084684 | -0.0009314 | -0.031204 | 0.038367 | 0.0061757 | 0.0058468 | 0.07782 | 0.091553 | 0.10986 | 0.13733 | 0.13275 | 0.068665 | -0.073242 | 0.07782 | 0.11902 | 0 | 0.022888 | 0.045776 | 0.068665 | -0.022888 | 122.1313 | 121.9894 | 0.013732 | 122.1542 | 122.2 | 0.21057 | -0.041199 | 122.1313 | 122.0398 | -0.096131 | 122.1405 | 122.0627 | 0.022888 | -0.073243 | 122.1954 | 122.1405 | 122.1725 | -0.19226 | 122.0856 | 122.1085 | 122.1817 | -0.14191
1879.6875 | 122.4014 | -122.0627 | 0.10529 | -0.00091566 | 0.016898 | 0.0012347 | 0.0056803 | 0.055929 | 0.0012049 | -0.0037597 | 0.0067901 | 0.0031274 | -0.030136 | 0.043494 | 0.0063893 | 0.0013608 | 0.059509 | 0.045776 | 0.054932 | 0.12817 | 0.15564 | 0.050354 | -0.086975 | 0.027466 | 0.068665 | -0.073242 | 0.059509 | 0.059509 | 0.027466 | -0.041199 | 122.113 | 121.9757 | 0.050354 | 122.1085 | 122.1909 | 0.21515 | -0.045777 | 122.0901 | 122.0215 | -0.045777 | 122.0901 | 121.9894 | -0.032043 | -0.045777 | 122.2183 | 122.1222 | 122.1176 | -0.19226 | 122.1222 | 122.1222 | 122.1313 | -0.14649
1881.4375 | 122.3785 | -122.0673 | 0.15106 | -0.00091566 | 0.015616 | 0.0023029 | 0.0056803 | 0.052083 | -0.0028539 | -0.0024779 | 0.01442 | -0.0032812 | -0.031631 | 0.042639 | 0.0029713 | 0.0045652 | 0.1236 | 0.1236 | 0.14191 | 0.18768 | 0.10529 | 0.068665 | -0.045776 | 0.082397 | 0.13275 | 0.013733 | 0 | 0.018311 | 0.064087 | -0.013733 | 122.1359 | 122.0215 | -0.045776 | 122.1909 | 122.2549 | 0.23346 | -0.027466 | 122.1313 | 122.0535 | -0.15106 | 122.1497 | 122.081 | 0.027466 | -0.13275 | 122.1725 | 122.1909 | 122.2092 | -0.19684 | 122.0673 | 122.0856 | 122.2 | -0.16479
1883.1406 | 122.4014 | -122.081 | 0.1236 | -0.00091566 | 0.016257 | 0.0029437 | 0.0067483 | 0.052724 | 0.0018457 | -0.0041869 | 0.0067901 | -0.0005042 | -0.030563 | 0.040289 | 0.0070301 | 0.0041378 | 0.018311 | 0.022888 | 0.032043 | 0.1236 | 0.16479 | 0.036621 | -0.10529 | -0.009155 | 0.054932 | -0.086975 | 0.059509 | 0.073242 | 0.032043 | -0.045776 | 122.1176 | 121.9757 | 0.041199 | 122.1039 | 122.2046 | 0.22888 | -0.10528 | 122.113 | 122.0352 | -0.064087 | 122.0718 | 121.994 | -0.041199 | -0.050354 | 122.2458 | 122.0993 | 122.113 | -0.22888 | 122.1405 | 122.1542 | 122.1359 | -0.16937
1884.8906 | 122.3785 | -122.0947 | 0.11902 | -0.016174 | 0.018393 | 0.0014483 | 0.0058939 | 0.052724 | -0.0028539 | -0.0026917 | 0.0067901 | 0.0009912 | -0.028213 | 0.04328 | 0.0040395 | 0.0054196 | 0.018311 | -0.036621 | 0.009155 | 0.091553 | 0.17395 | 0.032043 | -0.10071 | -0.036621 | 0 | -0.11902 | 0.073242 | 0.068665 | 0.027466 | -0.059509 | 122.1268 | 121.994 | 0.054931 | 122.0581 | 122.1863 | 0.19226 | -0.10071 | 122.1222 | 122.0352 | -0.045777 | 122.0581 | 121.9757 | -0.05951 | -0.050354 | 122.2687 | 122.113 | 122.1039 | -0.21973 | 122.168 | 122.1634 | 122.0947 | -0.17853
1886.5781 | 122.4152 | -122.1222 | 0.1236 | -0.00091566 | 0.015402 | 0.0031573 | 0.00076686 | 0.055929 | -0.0032813 | -0.0035461 | 0.0067901 | -0.001145 | -0.032058 | 0.039435 | 0.0076711 | 0.0058468 | 0.082397 | 0.068665 | 0.082397 | 0.13733 | 0.12817 | 0.059509 | -0.07782 | 0.068665 | 0.11444 | -0.013733 | 0.032043 | 0.036621 | 0.064087 | -0.004578 | 122.1817 | 122.0444 | 0.004578 | 122.1909 | 122.2595 | 0.21515 | -0.041199 | 122.1863 | 122.1176 | -0.091553 | 122.1909 | 122.1085 | -0.009155 | -0.086975 | 122.2504 | 122.2046 | 122.2046 | -0.20142 | 122.1542 | 122.1588 | 122.2366 | -0.12817
1888.2656 | 122.3236 | -122.1222 | 0.14191 | -0.00091566 | 0.011771 | 0.0061481 | 0.0054667 | 0.050161 | -0.0086219 | -0.0020507 | -0.00083936 | -0.0037086 | -0.032913 | 0.03858 | 0.0016895 | 0.0064878 | 0.054932 | 0.10071 | 0.1236 | 0.14191 | 0.16022 | 0.068665 | -0.073242 | 0.032043 | 0.14191 | 0.018311 | 0.036621 | 0.032043 | 0.059509 | -0.027466 | 122.1909 | 122.049 | 0.01831 | 122.2229 | 122.2641 | 0.21515 | -0.086975 | 122.1817 | 122.0947 | -0.10529 | 122.1542 | 122.1405 | 0.045777 | -0.10986 | 122.2824 | 122.1771 | 122.2458 | -0.21515 | 122.1588 | 122.1542 | 122.2641 | -0.16937
1890.0312 | 122.3465 | -122.1313 | 0.13733 | -0.00091566 | 0.013266 | 0.0052935 | 0.0058939 | 0.053365 | -0.0073401 | -0.0073913 | 0.0067901 | -0.0030676 | -0.030349 | 0.037512 | 0.0014759 | 0.0041378 | 0.086975 | 0.11902 | 0.14648 | 0.16479 | 0.15106 | 0.068665 | -0.068665 | 0.054932 | 0.15564 | 0.036621 | 0.045776 | 0.032043 | 0.059509 | 0 | 122.2 | 122.0627 | 0.013733 | 122.2504 | 122.2961 | 0.23346 | -0.050354 | 122.1909 | 122.1313 | -0.091553 | 122.1863 | 122.168 | 0.036621 | -0.10529 | 122.2824 | 122.2183 | 122.2778 | -0.20599 | 122.1771 | 122.1634 | 122.287 | -0.13733
1891.7969 | 122.4655 | -122.1039 | 0.10529 | -0.0085447 | 0.014334 | 0.0031573 | 0.0043985 | 0.055929 | 0.00013669 | -0.0024779 | -0.00083936 | 0.0003504 | -0.030563 | 0.040503 | 0.0063893 | 0.0045652 | 0.041199 | 0.018311 | 0.022888 | 0.11444 | 0.16937 | 0.059509 | -0.064087 | 0.036621 | 0.045776 | -0.059509 | 0.045776 | 0.059509 | 0.054932 | -0.013733 | 122.1634 | 122.0398 | 0.064087 | 122.1222 | 122.2183 | 0.17853 | -0.064087 | 122.1588 | 122.0901 | -0.05951 | 122.1405 | 122.0444 | -0.045776 | -0.045777 | 122.2733 | 122.1451 | 122.1268 | -0.16937 | 122.1497 | 122.1634 | 122.1497 | -0.11902
1893.5469 | 122.3785 | -122.1268 | 0.1236 | -0.0085447 | 0.01583 | 0.0027301 | 0.0050393 | 0.054006 | 0.0014185 | -0.0033325 | 0.0067901 | 0.0029138 | -0.028427 | 0.038794 | 0.0059621 | 0.0064878 | 0.032043 | -0.036621 | 0.009155 | 0.091553 | 0.15564 | 0.036621 | -0.091553 | -0.036621 | -0.018311 | -0.15106 | 0.07782 | 0.10071 | 0.032043 | -0.050354 | 122.1634 | 122.0352 | 0.032044 | 122.0901 | 122.2183 | 0.18311 | -0.091553 | 122.1588 | 122.0764 | -0.045776 | 122.0901 | 121.9757 | -0.10071 | -0.022888 | 122.2824 | 122.1588 | 122.1359 | -0.21515 | 122.2046 | 122.2275 | 122.1085 | -0.17395
1895.25 | 122.438 | -122.1222 | 0.10986 | -0.00091566 | 0.017111 | 0.0014483 | 0.00012606 | 0.055929 | 0.00013669 | -0.0026917 | 0.01442 | 0.001632 | -0.033126 | 0.043066 | 0.0070301 | 0.0064878 | 0.073242 | 0.068665 | 0.059509 | 0.13275 | 0.14191 | 0.032043 | -0.10071 | 0.027466 | 0.082397 | -0.068665 | 0.045776 | 0.064087 | 0.050354 | -0.050354 | 122.1542 | 122.0215 | 0.032044 | 122.1909 | 122.2549 | 0.23346 | -0.036621 | 122.1725 | 122.0718 | -0.064087 | 122.1497 | 122.0535 | -0.018311 | -0.045776 | 122.2641 | 122.1954 | 122.1817 | -0.21057 | 122.168 | 122.1863 | 122.2046 | -0.16022
1897 | 122.3373 | -122.1817 | 0.15106 | -0.00091566 | 0.011343 | 0.0059345 | 0.0046121 | 0.05422 | -0.0084081 | -0.0061095 | -0.00083936 | -0.0026404 | -0.031845 | 0.03858 | 0.00062147 | 0.0075558 | 0.036621 | 0.073242 | 0.11902 | 0.13733 | 0.12817 | 0.054932 | -0.073242 | 0.013733 | 0.082397 | -0.027466 | 0.045776 | 0.050354 | 0.059509 | -0.022888 | 122.2366 | 122.1085 | -0.022888 | 122.2549 | 122.319 | 0.21057 | -0.11444 | 122.2412 | 122.1588 | -0.10529 | 122.1954 | 122.1542 | -0.004578 | -0.10071 | 122.3099 | 122.2183 | 122.3007 | -0.2243 | 122.2275 | 122.2321 | 122.2641 | -0.17395
1898.6875 | 122.3785 | -122.1359 | 0.14191 | -0.00091566 | 0.0083526 | 0.0044391 | 0.0043985 | 0.053792 | -0.0073401 | -0.0050415 | 0.0067901 | -0.0030676 | -0.034835 | 0.040289 | 0.0038259 | 0.0073422 | 0.11444 | 0.16022 | 0.14648 | 0.17853 | 0.14648 | 0.068665 | -0.054932 | 0.068665 | 0.16937 | 0.064087 | 0.041199 | 0.050354 | 0.073242 | -0.013733 | 122.2046 | 122.081 | 0.004577 | 122.2961 | 122.3145 | 0.23346 | -0.027466 | 122.2092 | 122.1222 | -0.10071 | 122.2046 | 122.2 | 0.07782 | -0.091553 | 122.2824 | 122.2504 | 122.2824 | -0.19684 | 122.1771 | 122.1863 | 122.3053 | -0.15564
1900.4375 | 122.3648 | -122.1588 | 0.15106 | -0.00091566 | 0.010062 | 0.0055073 | 0.0043985 | 0.052297 | -0.0066993 | -0.0039733 | -0.00083936 | -0.0015722 | -0.031845 | 0.038153 | 0.0027577 | 0.0062742 | 0.059509 | 0.073242 | 0.091553 | 0.12817 | 0.14191 | 0.068665 | -0.068665 | 0.004578 | 0.07782 | -0.027466 | 0.054932 | 0.054932 | 0.045776 | -0.036621 | 122.2275 | 122.0901 | -0.009155 | 122.2321 | 122.287 | 0.19684 | -0.091553 | 122.2046 | 122.1222 | -0.09613 | 122.1634 | 122.1313 | 0.009155 | -0.09613 | 122.3007 | 122.2183 | 122.2504 | -0.21973 | 122.2137 | 122.2137 | 122.2366 | -0.18768
1902.1562 | 122.4335 | -122.1313 | 0.11902 | -0.00091566 | 0.011984 | 0.0044391 | 0.0020487 | 0.056142 | -0.0013587 | -0.0022643 | -0.00083936 | -0.0009314 | -0.031631 | 0.039862 | 0.0074575 | 0.0020016 | 0.11444 | 0.086975 | 0.11444 | 0.16479 | 0.13733 | 0.07782 | -0.064087 | 0.082397 | 0.1236 | -0.004578 | 0.018311 | 0.041199 | 0.064087 | 0.004578 | 122.2092 | 122.0673 | 0.01831 | 122.2183 | 122.2961 | 0.22888 | -0.004578 | 122.1954 | 122.1359 | -0.10071 | 122.2137 | 122.1268 | -0.009156 | -0.07782 | 122.2687 | 122.2458 | 122.2458 | -0.18311 | 122.1497 | 122.1725 | 122.2549 | -0.11444
1903.875 | 122.3511 | -122.168 | 0.14191 | -0.00091566 | 0.011557 | 0.0031573 | 0.0052531 | 0.056142 | -0.0043493 | -0.0041869 | -0.00083936 | -0.0015722 | -0.030136 | 0.039007 | 0.0046803 | 0.0047788 | 0.1236 | 0.15106 | 0.15564 | 0.16479 | 0.11902 | 0.082397 | -0.041199 | 0.07782 | 0.11444 | 0.013733 | 0.036621 | 0.032043 | 0.054932 | -0.018311 | 122.2504 | 122.1268 | -0.022888 | 122.319 | 122.3328 | 0.20599 | -0.018311 | 122.2229 | 122.1497 | -0.10529 | 122.2458 | 122.1817 | 0.032044 | -0.10986 | 122.287 | 122.2916 | 122.3236 | -0.18311 | 122.2046 | 122.2 | 122.2824 | -0.16022
1905.6406 | 122.3236 | -122.168 | 0.15106 | -0.00091566 | 0.012412 | 0.0014483 | 0.0080301 | 0.053792 | -0.0032813 | -0.0044007 | -0.00083936 | -0.0022132 | -0.032913 | 0.040076 | 0.0010487 | 0.0071286 | 0.1236 | 0.14191 | 0.16479 | 0.17395 | 0.12817 | 0.07782 | -0.059509 | 0.082397 | 0.16479 | 0.009155 | 0.036621 | 0.036621 | 0.041199 | -0.013733 | 122.2458 | 122.1085 | -0.022888 | 122.3099 | 122.3419 | 0.23346 | -0.027466 | 122.2092 | 122.1542 | -0.11444 | 122.2504 | 122.1771 | 0.022888 | -0.11444 | 122.2961 | 122.2916 | 122.3328 | -0.21057 | 122.2046 | 122.2046 | 122.3328 | -0.16479
1907.3906 | 122.3373 | -122.1771 | 0.11902 | 0.0067138 | 0.01647 | 0.0031573 | 0.0069621 | 0.05486 | -0.0011451 | -0.0041869 | 0.0067901 | 0.001632 | -0.029495 | 0.04093 | 0.0029713 | 0.0030698 | 0.036621 | 0.022888 | 0.032043 | 0.07782 | 0.16022 | 0.022888 | -0.11902 | -0.032043 | 0.050354 | -0.10071 | 0.086975 | 0.07782 | 0.004578 | -0.068665 | 122.2 | 122.0581 | 0.041198 | 122.2 | 122.2549 | 0.19684 | -0.082398 | 122.1817 | 122.1085 | -0.032044 | 122.1451 | 122.0764 | -0.032043 | -0.041199 | 122.3373 | 122.2137 | 122.2092 | -0.23804 | 122.2641 | 122.2549 | 122.2275 | -0.18768
1909.0938 | 122.3328 | -122.2183 | 0.14191 | -0.00091566 | 0.011771 | 0.0040119 | 0.0041849 | 0.053579 | -0.0041357 | -0.0035461 | 0.01442 | -0.0034948 | -0.032272 | 0.038367 | 0.0044667 | 0.0062742 | 0.086975 | 0.10071 | 0.10986 | 0.13275 | 0.13275 | 0.07782 | -0.073242 | 0.027466 | 0.091553 | -0.032043 | 0.027466 | 0.050354 | 0.064087 | -0.036621 | 122.2961 | 122.1451 | -0.009156 | 122.319 | 122.3511 | 0.20599 | -0.054932 | 122.2824 | 122.1817 | -0.11444 | 122.2458 | 122.1863 | 0.004578 | -0.091553 | 122.3511 | 122.3053 | 122.3282 | -0.21515 | 122.2458 | 122.2687 | 122.3099 | -0.17853
1910.8438 | 122.3236 | -122.1588 | 0.14191 | -0.0085447 | 0.012412 | 0.0050799 | 0.0086709 | 0.055074 | -0.0024267 | -0.0039733 | -0.00083936 | 0.0012048 | -0.029922 | 0.041357 | 0.0033985 | 0.0039242 | 0.1236 | 0.14648 | 0.16479 | 0.16937 | 0.11902 | 0.073242 | -0.068665 | 0.07782 | 0.16937 | 0.009155 | 0.032043 | 0.036621 | 0.059509 | -0.027466 | 122.2321 | 122.0901 | -0.022888 | 122.3053 | 122.3282 | 0.23804 | -0.018311 | 122.2183 | 122.1313 | -0.10986 | 122.2366 | 122.168 | 0.036621 | -0.10529 | 122.2778 | 122.2824 | 122.3236 | -0.21057 | 122.1909 | 122.1954 | 122.3282 | -0.16937
1912.6094 | 122.406 | -122.1725 | 0.13275 | -0.00091566 | 0.01113 | 0.0061481 | 0.0056803 | 0.053792 | -0.0041357 | -0.0033325 | -0.0084684 | -0.0030676 | -0.030777 | 0.039862 | 0.0023305 | 0.0047788 | 0.1236 | 0.13275 | 0.15106 | 0.16022 | 0.1236 | 0.073242 | -0.068665 | 0.07782 | 0.16479 | 0.054932 | 0.032043 | 0.032043 | 0.073242 | 0.004578 | 122.2458 | 122.1039 | -0.009155 | 122.3053 | 122.3328 | 0.22888 | -0.009155 | 122.2458 | 122.1771 | -0.10071 | 122.2504 | 122.2275 | 0.050354 | -0.10071 | 122.2961 | 122.2961 | 122.3236 | -0.20142 | 122.2046 | 122.2046 | 122.3373 | -0.12817
1914.375 | 122.4426 | -122.1771 | 0.11902 | 0.0067138 | 0.016257 | 0.0033709 | 0.0035441 | 0.055929 | -7.6908e-05 | -0.0039733 | -0.00083936 | 0.0046228 | -0.031204 | 0.041144 | 0.0087391 | 0.0047788 | 0.041199 | -0.041199 | -0.004578 | 0.07782 | 0.17853 | 0.022888 | -0.09613 | -0.009155 | -0.009155 | -0.14191 | 0.073242 | 0.059509 | 0.022888 | -0.064087 | 122.2 | 122.081 | 0.059509 | 122.1359 | 122.2549 | 0.17395 | -0.07782 | 122.2 | 122.113 | -0.045777 | 122.168 | 122.0352 | -0.07782 | -0.05951 | 122.3557 | 122.2183 | 122.1725 | -0.21515 | 122.2504 | 122.2366 | 122.168 | -0.18311
1916.0625 | 122.4792 | -122.1405 | 0.10071 | 0.0067138 | 0.016257 | 0.0027301 | 0.0058939 | 0.055288 | 0.0024865 | -0.0024779 | -0.0084684 | 0.0031274 | -0.02864 | 0.043707 | 0.0059621 | 0.0030698 | 0.059509 | 0.041199 | 0.054932 | 0.1236 | 0.14648 | 0.032043 | -0.10986 | 0.032043 | 0.07782 | -0.068665 | 0.059509 | 0.07782 | 0.045776 | -0.050354 | 122.1725 | 122.0306 | 0.045776 | 122.1817 | 122.2641 | 0.23346 | -0.041199 | 122.1863 | 122.0901 | -0.041199 | 122.1725 | 122.0718 | -0.018311 | -0.022888 | 122.287 | 122.2 | 122.1954 | -0.21057 | 122.2 | 122.2183 | 122.2183 | -0.15106
1917.8125 | 122.3694 | -122.2275 | 0.16022 | -0.0085447 | 0.017325 | 0.0044391 | 0.0090983 | 0.054433 | -0.0022131 | -0.0046143 | -0.00083936 | 0.000564 | -0.02864 | 0.043494 | 0.0023305 | 0.0056332 | 0.036621 | 0.036621 | 0.045776 | 0.09613 | 0.16479 | 0.050354 | -0.10071 | -0.032043 | 0.045776 | -0.10986 | 0.073242 | 0.082397 | 0.045776 | -0.045776 | 122.2778 | 122.1268 | 0.004578 | 122.2641 | 122.3236 | 0.19684 | -0.1236 | 122.2733 | 122.1817 | -0.086975 | 122.1954 | 122.1176 | -0.064087 | -0.07782 | 122.3923 | 122.2641 | 122.2733 | -0.26093 | 122.3007 | 122.3099 | 122.2733 | -0.20599
1919.5781 | 122.3602 | -122.2183 | 0.15564 | -0.016174 | 0.01348 | 0.0067889 | 0.0029031 | 0.053579 | -0.0056311 | -0.0052551 | -0.016098 | -0.0017858 | -0.030563 | 0.039007 | 0.0010487 | 0.0058468 | 0.068665 | 0.091553 | 0.10071 | 0.12817 | 0.1236 | 0.064087 | -0.068665 | 0.022888 | 0.091553 | -0.022888 | 0.045776 | 0.050354 | 0.059509 | -0.022888 | 122.2824 | 122.1497 | -0.032044 | 122.3099 | 122.3465 | 0.19684 | -0.086975 | 122.2778 | 122.1954 | -0.10986 | 122.2412 | 122.1954 | 0 | -0.10529 | 122.3419 | 122.287 | 122.319 | -0.22431 | 122.2641 | 122.2687 | 122.3099 | -0.17853
1921.3438 | 122.4518 | -122.1909 | 0.11444 | -0.00091566 | 0.017538 | 0.0031573 | 0.0043985 | 0.05422 | 0.0027003 | -0.0029053 | 0.0067901 | 0.0029138 | -0.031417 | 0.04093 | 0.0087391 | 0.0024288 | 0.09613 | 0.059509 | 0.073242 | 0.13733 | 0.15564 | 0.036621 | -0.082397 | 0.018311 | 0.059509 | -0.091553 | 0.068665 | 0.07782 | 0.041199 | -0.032043 | 122.2275 | 122.1085 | 0.041199 | 122.2504 | 122.3282 | 0.21973 | -0.018311 | 122.2321 | 122.1588 | -0.045776 | 122.2092 | 122.0993 | -0.05951 | -0.036621 | 122.3465 | 122.287 | 122.2641 | -0.19684 | 122.2595 | 122.2687 | 122.2504 | -0.14648
1923.0312 | 122.4976 | -122.1909 | 0.12817 | -0.00091566 | 0.01647 | -4.6912e-05 | 0.0039713 | 0.053365 | -0.00071771 | -0.0024779 | 0.01442 | -0.0007178 | -0.029281 | 0.040503 | 0.0066029 | 0.0062742 | 0.009155 | -0.027466 | 0.009155 | 0.09613 | 0.17395 | 0.036621 | -0.086975 | -0.032043 | 0 | -0.13733 | 0.086975 | 0.073242 | 0.041199 | -0.059509 | 122.2275 | 122.1039 | 0.045776 | 122.1634 | 122.287 | 0.1831 | -0.11902 | 122.2321 | 122.1313 | -0.041199 | 122.1588 | 122.0535 | -0.07782 | -0.054932 | 122.3648 | 122.2 | 122.2 | -0.21515 | 122.2778 | 122.2641 | 122.1909 | -0.18768
1924.7969 | 122.3785 | -122.2412 | 0.14648 | -0.0085447 | 0.013266 | 0.0033709 | 0.0041849 | 0.051443 | -0.0058447 | -0.0031189 | -0.00083936 | -0.0022132 | -0.032699 | 0.040503 | 0.0033985 | 0.0088376 | 0.10071 | 0.12817 | 0.15106 | 0.15106 | 0.12817 | 0.059509 | -0.064087 | 0.068665 | 0.11902 | 0.004578 | 0.022888 | 0.032043 | 0.050354 | -0.027466 | 122.3007 | 122.1771 | -0.01831 | 122.3694 | 122.3923 | 0.21515 | -0.045776 | 122.2916 | 122.2137 | -0.1236 | 122.3099 | 122.2458 | 0.032044 | -0.11444 | 122.3694 | 122.3419 | 122.3923 | -0.21057 | 122.2641 | 122.2733 | 122.3602 | -0.17395
1926.5625 | 122.4426 | -122.1954 | 0.12817 | -0.00091566 | 0.016684 | 0.0048663 | 0.0093119 | 0.05422 | -0.0026403 | -0.0041869 | -0.00083936 | -7.6996e-05 | -0.028 | 0.041571 | 0.0025441 | 0.0030698 | 0.009155 | 0.022888 | 0.009155 | 0.086975 | 0.16937 | 0.018311 | -0.091553 | -0.045776 | 0.027466 | -0.091553 | 0.086975 | 0.086975 | 0.013733 | -0.068665 | 122.2137 | 122.1039 | 0.041199 | 122.2183 | 122.2824 | 0.17853 | -0.11902 | 122.2092 | 122.1268 | -0.041199 | 122.1497 | 122.1039 | -0.022888 | -0.041199 | 122.3648 | 122.2046 | 122.2046 | -0.21973 | 122.2824 | 122.2824 | 122.2229 | -0.19684
1928.25 | 122.4106 | -122.2183 | 0.14191 | -0.00091566 | 0.013052 | 0.0020893 | 0.0061075 | 0.05422 | -0.0030677 | -0.0037597 | -0.00083936 | -0.0013586 | -0.032486 | 0.039435 | 0.0033985 | 0.005206 | 0.009155 | 0.009155 | 0.018311 | 0.073242 | 0.16937 | 0.018311 | -0.10986 | -0.054932 | 0.041199 | -0.11444 | 0.091553 | 0.07782 | 0.018311 | -0.045776 | 122.2366 | 122.1085 | 0.027466 | 122.2275 | 122.2916 | 0.18311 | -0.13275 | 122.2366 | 122.1725 | -0.050354 | 122.1634 | 122.1039 | -0.068665 | -0.064087 | 122.3877 | 122.2275 | 122.2366 | -0.25177 | 122.3099 | 122.2961 | 122.2595 | -0.18768
1930 | 122.4014 | -122.2229 | 0.14191 | -0.00091566 | 0.010062 | 0.0018757 | 0.0022623 | 0.056783 | -0.0024267 | -0.0029053 | -0.00083936 | -0.0030676 | -0.032913 | 0.039435 | 0.0048939 | 0.0064878 | 0.09613 | 0.13275 | 0.14648 | 0.16479 | 0.11902 | 0.064087 | -0.054932 | 0.054932 | 0.1236 | 0.018311 | 0.036621 | 0.050354 | 0.054932 | -0.018311 | 122.287 | 122.168 | -0.022888 | 122.3557 | 122.3877 | 0.21973 | -0.045777 | 122.2778 | 122.2046 | -0.10529 | 122.2778 | 122.2412 | 0.036622 | -0.091553 | 122.3419 | 122.319 | 122.3694 | -0.19684 | 122.2595 | 122.2733 | 122.3465 | -0.16022
1931.7031 | 122.4518 | -122.2183 | 0.13275 | -0.00091566 | 0.014975 | 0.0044391 | 0.0071757 | 0.052938 | -0.0077673 | -0.0046143 | -0.00083936 | -0.0030676 | -0.031845 | 0.040716 | 0.0019033 | 0.0064878 | 0.09613 | 0.12817 | 0.14191 | 0.17395 | 0.13733 | 0.07782 | -0.059509 | 0.07782 | 0.16937 | 0.050354 | 0.027466 | 0.050354 | 0.064087 | -0.013733 | 122.2961 | 122.1588 | 0.004578 | 122.3465 | 122.3923 | 0.23346 | -0.036621 | 122.2824 | 122.2046 | -0.10529 | 122.2961 | 122.2687 | 0.064087 | -0.082397 | 122.3557 | 122.3145 | 122.3602 | -0.19226 | 122.2458 | 122.2687 | 122.3877 | -0.14648
1933.3906 | 122.406 | -122.2229 | 0.16022 | 0.0067138 | 0.014121 | 0.0055073 | 0.0071757 | 0.056142 | -0.0064855 | -0.0065369 | -0.00083936 | -0.0017858 | -0.032272 | 0.038153 | 0.0033985 | 0.0032834 | 0.11444 | 0.16479 | 0.15564 | 0.17395 | 0.11902 | 0.068665 | -0.073242 | 0.082397 | 0.18768 | 0.045776 | 0.045776 | 0.041199 | 0.068665 | -0.013733 | 122.2916 | 122.1497 | -0.041198 | 122.3877 | 122.3969 | 0.24719 | -0.045776 | 122.2916 | 122.2092 | -0.11444 | 122.3053 | 122.2687 | 0.059509 | -0.11902 | 122.3419 | 122.3373 | 122.3785 | -0.23346 | 122.2687 | 122.2641 | 122.4106 | -0.17395
1935.0938 | 122.5342 | -122.2046 | 0.11902 | 0.0067138 | 0.012839 | 0.0040119 | 0.0035441 | 0.05486 | 0.0018457 | -0.0052551 | 0.0067901 | 0.0029138 | -0.031845 | 0.039648 | 0.0061757 | 0.0047788 | 0.036621 | -0.027466 | 0.013733 | 0.10071 | 0.16479 | 0.022888 | -0.10071 | -0.018311 | -0.022888 | -0.13275 | 0.064087 | 0.059509 | 0.059509 | -0.064087 | 122.2275 | 122.1039 | 0.045776 | 122.1771 | 122.3053 | 0.20142 | -0.082398 | 122.2641 | 122.1405 | -0.054932 | 122.1863 | 122.0718 | -0.068664 | -0.05951 | 122.3694 | 122.2412 | 122.2183 | -0.21973 | 122.2687 | 122.2641 | 122.1817 | -0.18311
1936.8125 | 122.5159 | -122.2092 | 0.1236 | -0.0085447 | 0.01647 | 0.0035847 | 0.0018351 | 0.054647 | 0.00077749 | -0.0016235 | 0.0067901 | 0.0035546 | -0.032058 | 0.040076 | 0.0048939 | 0.0045652 | 0.041199 | -0.045776 | -0.009155 | 0.07782 | 0.16022 | 0.050354 | -0.09613 | -0.013733 | -0.009155 | -0.11444 | 0.064087 | 0.091553 | 0.027466 | -0.041199 | 122.2595 | 122.113 | 0.036621 | 122.1634 | 122.287 | 0.17395 | -0.082397 | 122.2366 | 122.168 | -0.059509 | 122.1954 | 122.0947 | -0.073242 | -0.032043 | 122.3694 | 122.2504 | 122.2 | -0.21973 | 122.2733 | 122.3007 | 122.2 | -0.16479
1938.5781 | 122.3923 | -122.2321 | 0.15106 | -0.00091566 | 0.014761 | 0.0044391 | 0.0076029 | 0.053152 | -0.0060583 | -0.0048279 | -0.00083936 | -0.0030676 | -0.031845 | 0.038367 | 0.0031849 | 0.003497 | 0.10071 | 0.14191 | 0.13733 | 0.1831 | 0.14648 | 0.064087 | -0.068665 | 0.045776 | 0.17853 | 0.004578 | 0.022888 | 0.045776 | 0.059509 | -0.022888 | 122.2961 | 122.1634 | -0.004578 | 122.374 | 122.4152 | 0.25177 | -0.050354 | 122.2916 | 122.2092 | -0.12817 | 122.2778 | 122.2366 | 0.027466 | -0.10529 | 122.3785 | 122.3328 | 122.3694 | -0.21973 | 122.2549 | 122.2778 | 122.4106 | -0.17395
1940.3438 | 122.4014 | -122.2824 | 0.14191 | -0.00091566 | 0.014761 | 0.0037983 | 0.0065347 | 0.05187 | -0.0034949 | -0.0054687 | -0.00083936 | -0.0032812 | -0.029708 | 0.040503 | 0.00062147 | 0.0062742 | 0.086975 | 0.09613 | 0.10529 | 0.14648 | 0.15106 | 0.045776 | -0.09613 | -0.004578 | 0.064087 | -0.059509 | 0.059509 | 0.068665 | 0.050354 | -0.050354 | 122.3282 | 122.1863 | 0.009155 | 122.3785 | 122.4289 | 0.24261 | -0.054932 | 122.3328 | 122.2321 | -0.082398 | 122.2778 | 122.2229 | -0.009155 | -0.073242 | 122.4335 | 122.3694 | 122.3877 | -0.23804 | 122.3419 | 122.3511 | 122.3465 | -0.19226
1942.0312 | 122.4884 | -122.2366 | 0.11444 | 0.0067138 | 0.017538 | 0.00080749 | 0.0048257 | 0.056142 | 0.0022729 | -0.0035461 | -0.00083936 | 0.003982 | -0.030349 | 0.040076 | 0.0063893 | 0.0039242 | 0.07782 | 0.041199 | 0.041199 | 0.11444 | 0.15564 | 0.041199 | -0.09613 | 0.009155 | 0.013733 | -0.12817 | 0.064087 | 0.068665 | 0.027466 | -0.041199 | 122.2778 | 122.1405 | 0.041199 | 122.2778 | 122.3511 | 0.21057 | -0.036621 | 122.2641 | 122.1954 | -0.050354 | 122.2458 | 122.1085 | -0.086975 | -0.045776 | 122.3923 | 122.3145 | 122.2778 | -0.21057 | 122.3007 | 122.3053 | 122.2504 | -0.15564
1943.7969 | 122.5388 | -122.2183 | 0.10986 | -0.0085447 | 0.014761 | 0.0042255 | 0.0022623 | 0.05187 | -0.0017859 | -0.0016235 | 0.0067901 | 0.003341 | -0.032699 | 0.041571 | 0.0042531 | 0.0058468 | 0.027466 | -0.032043 | 0.004578 | 0.086975 | 0.14648 | 0.032043 | -0.091553 | -0.018311 | -0.004578 | -0.10529 | 0.064087 | 0.07782 | 0.032043 | -0.054932 | 122.2504 | 122.1268 | 0.036621 | 122.1863 | 122.3053 | 0.17853 | -0.082397 | 122.2504 | 122.1634 | -0.045776 | 122.2 | 122.113 | -0.050354 | -0.032043 | 122.3648 | 122.2458 | 122.2229 | -0.20142 | 122.2824 | 122.2961 | 122.2137 | -0.16479
1945.5781 | 122.4884 | -122.2321 | 0.13275 | 0.0067138 | 0.01583 | 0.0010211 | 0.0020487 | 0.054433 | -7.6908e-05 | -0.0024779 | -0.016098 | 0.0027002 | -0.029922 | 0.041785 | 0.0040395 | 0.0058468 | 0.041199 | 0.022888 | 0.032043 | 0.10071 | 0.16022 | 0.045776 | -0.086975 | 0 | 0.018311 | -0.1236 | 0.064087 | 0.091553 | 0.036621 | -0.059509 | 122.2778 | 122.1451 | 0.027466 | 122.2549 | 122.3328 | 0.18768 | -0.091552 | 122.2687 | 122.1725 | -0.068664 | 122.2321 | 122.1085 | -0.064087 | -0.041198 | 122.3923 | 122.2733 | 122.2641 | -0.21973 | 122.2961 | 122.3236 | 122.2504 | -0.19226
1947.3438 | 122.4609 | -122.2687 | 0.14648 | -0.0085447 | 0.010703 | 0.0061481 | 0.0076029 | 0.053152 | -0.0071265 | -0.0044007 | -0.00083936 | -0.0047766 | -0.031631 | 0.041357 | 0.00083507 | 0.0058468 | 0.059509 | 0.091553 | 0.13733 | 0.15564 | 0.13733 | 0.059509 | -0.059509 | 0.036621 | 0.16479 | 0.032043 | 0.032043 | 0.050354 | 0.064087 | -0.013733 | 122.3282 | 122.2092 | -0.009155 | 122.3602 | 122.4243 | 0.21515 | -0.086975 | 122.3328 | 122.2549 | -0.11444 | 122.3053 | 122.3007 | 0.045776 | -0.09613 | 122.406 | 122.3282 | 122.406 | -0.20599 | 122.3007 | 122.319 | 122.4335 | -0.16022
1949.0312 | 122.3969 | -122.287 | 0.14191 | -0.00091566 | 0.014121 | 0.0035847 | 0.0035441 | 0.050588 | -0.0060583 | -0.0054687 | -0.0084684 | -0.0026404 | -0.029922 | 0.038794 | 0.0023305 | 0.0062742 | 0.09613 | 0.1236 | 0.12817 | 0.16022 | 0.12817 | 0.050354 | -0.068665 | 0.013733 | 0.13275 | -0.027466 | 0.054932 | 0.045776 | 0.054932 | -0.041199 | 122.3373 | 122.2183 | -0.013733 | 122.4106 | 122.4472 | 0.22888 | -0.045777 | 122.3419 | 122.2458 | -0.086975 | 122.3007 | 122.2595 | 0.013733 | -0.096131 | 122.4152 | 122.3831 | 122.4152 | -0.21057 | 122.3419 | 122.3328 | 122.4197 | -0.18311
1950.7969 | 122.4335 | -122.2778 | 0.14191 | 0.0067138 | 0.011771 | 0.0050799 | 0.0033305 | 0.055501 | -0.0045629 | -0.0054687 | -0.016098 | -0.0030676 | -0.03099 | 0.038794 | 0.00062147 | 0.0060604 | 0.068665 | 0.068665 | 0.10071 | 0.12817 | 0.13275 | 0.054932 | -0.064087 | 0.022888 | 0.086975 | -0.027466 | 0.050354 | 0.032043 | 0.073242 | -0.018311 | 122.3328 | 122.2137 | -0.009156 | 122.3465 | 122.406 | 0.19226 | -0.073242 | 122.3511 | 122.2595 | -0.091553 | 122.3007 | 122.2504 | -0.009155 | -0.10986 | 122.4106 | 122.3465 | 122.3785 | -0.20599 | 122.3282 | 122.3099 | 122.3648 | -0.16022
1952.5469 | 122.4243 | -122.2641 | 0.15106 | -0.0085447 | 0.016898 | 0.0048663 | 0.0080301 | 0.055288 | -0.0030677 | -0.0046143 | -0.00083936 | -7.6996e-05 | -0.028854 | 0.040503 | 0.0016895 | 0.0032834 | 0.054932 | 0.059509 | 0.059509 | 0.13733 | 0.14191 | 0.018311 | -0.086975 | -0.018311 | 0.054932 | -0.082397 | 0.059509 | 0.064087 | 0.032043 | -0.041199 | 122.2824 | 122.1771 | -0.009155 | 122.3236 | 122.4014 | 0.2243 | -0.09613 | 122.2961 | 122.2229 | -0.091553 | 122.2458 | 122.1817 | -0.041198 | -0.086975 | 122.406 | 122.319 | 122.3236 | -0.23804 | 122.3236 | 122.3282 | 122.319 | -0.19226
1954.25 | 122.5159 | -122.2687 | 0.10529 | 0.0067138 | 0.015616 | 0.0042255 | 0.00055326 | 0.053365 | 0.0018457 | -0.0058959 | -0.0084684 | 0.0001368 | -0.03099 | 0.043921 | 0.0070301 | 0.0054196 | 0.027466 | -0.018311 | -0.009155 | 0.082397 | 0.16022 | 0.022888 | -0.09613 | -0.022888 | -0.018311 | -0.13733 | 0.059509 | 0.068665 | 0.036621 | -0.059509 | 122.2916 | 122.1725 | 0.054931 | 122.2504 | 122.3511 | 0.17853 | -0.07782 | 122.3053 | 122.2092 | -0.045777 | 122.2458 | 122.1313 | -0.07782 | -0.036621 | 122.4289 | 122.2961 | 122.2595 | -0.20142 | 122.3282 | 122.3373 | 122.2504 | -0.16479
1956.0156 | 122.5204 | -122.2733 | 0.10529 | 0.0067138 | 0.015189 | 0.00059389 | 0.0043985 | 0.055929 | 0.00035029 | -0.0024779 | -0.0084684 | 0.0035546 | -0.029281 | 0.044348 | 0.0072437 | 0.0041378 | 0.07782 | 0.082397 | 0.059509 | 0.12817 | 0.16479 | 0.032043 | -0.10529 | 0.032043 | 0.07782 | -0.082397 | 0.041199 | 0.07782 | 0.041199 | -0.059509 | 122.3053 | 122.168 | 0.059509 | 122.3557 | 122.4014 | 0.23346 | -0.027466 | 122.3145 | 122.2137 | -0.064087 | 122.3053 | 122.1909 | -0.022888 | -0.027466 | 122.438 | 122.3511 | 122.3328 | -0.21057 | 122.3145 | 122.3511 | 122.3511 | -0.16479
1957.7812 | 122.58 | -122.2549 | 0.10986 | -0.00091566 | 0.013907 | 0.0014483 | 0.0073893 | 0.054006 | -0.00093131 | -0.00034172 | -0.0084684 | 0.001632 | -0.03099 | 0.042425 | 0.0066029 | 0.0056332 | 0.013733 | 0 | 0.009155 | 0.082397 | 0.16479 | 0.027466 | -0.07782 | 0.004578 | 0.018311 | -0.10529 | 0.07782 | 0.068665 | 0.050354 | -0.027466 | 122.2824 | 122.1771 | 0.054932 | 122.2549 | 122.3373 | 0.16022 | -0.09613 | 122.3053 | 122.2275 | -0.032043 | 122.2595 | 122.1497 | -0.07782 | -0.041198 | 122.4197 | 122.2687 | 122.2641 | -0.18768 | 122.3328 | 122.3236 | 122.2733 | -0.13733
1959.5625 | 122.438 | -122.2824 | 0.13733 | -0.00091566 | 0.010275 | 0.0018757 | 0.0067483 | 0.054006 | -0.0060583 | -0.0041869 | 0.0067901 | -0.0037086 | -0.032913 | 0.040716 | 0.0019033 | 0.0084104 | 0.07782 | 0.10071 | 0.11444 | 0.14191 | 0.12817 | 0.068665 | -0.050354 | 0.018311 | 0.091553 | -0.013733 | 0.018311 | 0.045776 | 0.059509 | -0.009155 | 122.3511 | 122.2321 | -0.009155 | 122.3831 | 122.4243 | 0.19226 | -0.059509 | 122.3419 | 122.2733 | -0.11902 | 122.3007 | 122.2687 | -0.004578 | -0.091553 | 122.4106 | 122.3602 | 122.3969 | -0.18768 | 122.3007 | 122.3282 | 122.374 | -0.14648
1961.25 | 122.5204 | -122.2687 | 0.1236 | -0.00091566 | 0.014761 | 0.0035847 | 0.0043985 | 0.05422 | 0.0022729 | -0.0026917 | -0.00083936 | 0.000564 | -0.028427 | 0.040076 | 0.0055349 | 0.0047788 | 0.041199 | -0.004578 | 0.009155 | 0.091553 | 0.15106 | 0.041199 | -0.09613 | -0.013733 | -0.004578 | -0.14191 | 0.059509 | 0.068665 | 0.027466 | -0.050354 | 122.3099 | 122.1725 | 0.027466 | 122.2641 | 122.3602 | 0.18768 | -0.082397 | 122.2961 | 122.2183 | -0.064087 | 122.2549 | 122.1268 | -0.091553 | -0.054931 | 122.4197 | 122.3099 | 122.2778 | -0.21973 | 122.3282 | 122.3373 | 122.2641 | -0.17395
1963 | 122.4472 | -122.2916 | 0.13275 | -0.0085447 | 0.015402 | 0.0044391 | 0.0071757 | 0.052938 | -0.0022131 | -0.0024779 | -0.00083936 | 0.0007776 | -0.03099 | 0.044989 | 0.0021169 | 0.0056332 | 0.009155 | -0.004578 | 0.027466 | 0.086975 | 0.16479 | 0.018311 | -0.11444 | -0.050354 | 0.041199 | -0.10986 | 0.086975 | 0.10529 | 0.027466 | -0.054932 | 122.3099 | 122.1771 | 0.032044 | 122.287 | 122.3785 | 0.20142 | -0.1236 | 122.319 | 122.2366 | -0.045776 | 122.2412 | 122.1817 | -0.054931 | -0.027465 | 122.4564 | 122.3007 | 122.319 | -0.24719 | 122.3785 | 122.3969 | 122.3328 | -0.18768
1964.7656 | 122.5113 | -122.2549 | 0.11902 | 0.0067138 | 0.013907 | 0.0048663 | 0.0082437 | 0.052511 | -0.0086219 | -0.0048279 | -0.0084684 | -0.0052038 | -0.033126 | 0.038367 | 0.00040787 | 0.005206 | 0.10071 | 0.14191 | 0.16479 | 0.16937 | 0.12817 | 0.064087 | -0.054932 | 0.068665 | 0.17395 | 0.054932 | 0.018311 | 0.032043 | 0.068665 | -0.004578 | 122.319 | 122.2 | 0.009155 | 122.3969 | 122.4243 | 0.22431 | -0.018311 | 122.3236 | 122.2504 | -0.10071 | 122.3236 | 122.3099 | 0.05951 | -0.086976 | 122.3831 | 122.3557 | 122.4197 | -0.17395 | 122.2733 | 122.287 | 122.4289 | -0.1236
1966.5312 | 122.5342 | -122.2961 | 0.1236 | -0.00091566 | 0.015189 | 0.0040119 | 0.0026895 | 0.051229 | 0.0024865 | -0.0026917 | -0.00083936 | 0.0029138 | -0.029922 | 0.041357 | 0.0091665 | 0.0045652 | 0.068665 | 0.022888 | 0.018311 | 0.11444 | 0.15564 | 0.022888 | -0.09613 | 0.004578 | 0.032043 | -0.12817 | 0.068665 | 0.073242 | 0.041199 | -0.036621 | 122.319 | 122.2 | 0.032044 | 122.319 | 122.4106 | 0.21057 | -0.054931 | 122.3373 | 122.2595 | -0.054931 | 122.3007 | 122.168 | -0.091553 | -0.050354 | 122.4518 | 122.3648 | 122.3145 | -0.21973 | 122.3648 | 122.3694 | 122.3282 | -0.16022
1968.2969 | 122.5983 | -122.2687 | 0.10529 | 0.0067138 | 0.014334 | 0.0035847 | 0.0031167 | 0.052511 | -0.00029051 | -0.00076912 | -0.00083936 | 0.0020594 | -0.032699 | 0.041998 | 0.0059621 | 0.0039242 | 0.027466 | -0.004578 | 0.009155 | 0.086975 | 0.16479 | 0.032043 | -0.091553 | 0 | 0.013733 | -0.082397 | 0.068665 | 0.068665 | 0.022888 | -0.032043 | 122.3007 | 122.1771 | 0.059509 | 122.2641 | 122.3557 | 0.17853 | -0.07782 | 122.2916 | 122.2366 | -0.036621 | 122.2687 | 122.1863 | -0.050354 | -0.036621 | 122.4335 | 122.2961 | 122.2778 | -0.19684 | 122.3373 | 122.3373 | 122.2824 | -0.13733
1969.9844 | 122.4564 | -122.3236 | 0.15564 | -0.00091566 | 0.0092072 | 0.0031573 | 0.0052531 | 0.051229 | -0.0056311 | -0.0033325 | -0.0084684 | -0.0022132 | -0.030563 | 0.042425 | 0.0029713 | 0.005206 | 0.09613 | 0.10986 | 0.13275 | 0.13275 | 0.10529 | 0.068665 | -0.041199 | 0.032043 | 0.11444 | 0.004578 | 0.032043 | 0.059509 | 0.041199 | -0.022888 | 122.3923 | 122.2824 | -0.050354 | 122.4335 | 122.4564 | 0.17395 | -0.05951 | 122.3648 | 122.3007 | -0.1236 | 122.3557 | 122.3282 | 0.027466 | -0.096131 | 122.4289 | 122.4197 | 122.4564 | -0.19684 | 122.3557 | 122.3831 | 122.438 | -0.17853
1971.7344 | 122.5616 | -122.2824 | 0.11444 | -0.0085447 | 0.011557 | 0.0020893 | 0.0026895 | 0.055929 | 0.0016321 | -0.0033325 | -0.0084684 | 0.0018456 | -0.029495 | 0.041998 | 0.0061757 | 0.005206 | 0.032043 | -0.022888 | 0 | 0.082397 | 0.16479 | 0.050354 | -0.10071 | -0.009155 | -0.018311 | -0.14191 | 0.07782 | 0.091553 | 0.018311 | -0.036621 | 122.3328 | 122.1817 | 0.050354 | 122.2595 | 122.3648 | 0.18311 | -0.082398 | 122.3007 | 122.2458 | -0.036621 | 122.2733 | 122.1405 | -0.10529 | -0.022888 | 122.4472 | 122.3145 | 122.2824 | -0.21515 | 122.3602 | 122.374 | 122.2641 | -0.15106
1973.5 | 122.493 | -122.319 | 0.15106 | -0.00091566 | 0.01113 | 0.0059345 | 0.0052531 | 0.050802 | -0.0058447 | -0.00098272 | 0.0067901 | -0.0022132 | -0.033126 | 0.039221 | 0.0027577 | 0.0056332 | 0.041199 | 0.045776 | 0.10529 | 0.13275 | 0.14191 | 0.054932 | -0.073242 | 0.018311 | 0.091553 | -0.036621 | 0.041199 | 0.064087 | 0.064087 | -0.027466 | 122.374 | 122.2458 | -0.009155 | 122.3648 | 122.4518 | 0.20599 | -0.10986 | 122.3831 | 122.2916 | -0.10986 | 122.3373 | 122.2824 | -0.009155 | -0.086975 | 122.4609 | 122.3602 | 122.4243 | -0.2243 | 122.3602 | 122.3831 | 122.4106 | -0.17853
1975.1875 | 122.5708 | -122.2824 | 0.1236 | 0.014343 | 0.022238 | 0.0018757 | 0.0069621 | 0.050588 | 0.00056389 | -0.0054687 | -0.0084684 | 0.0027002 | -0.028854 | 0.041571 | 0.0044667 | 0.0030698 | 0.032043 | -0.041199 | 0.013733 | 0.091553 | 0.17395 | 0.064087 | -0.09613 | -0.027466 | -0.013733 | -0.13275 | 0.07782 | 0.086975 | 0.022888 | -0.050354 | 122.3465 | 122.1863 | 0.050354 | 122.2412 | 122.374 | 0.18768 | -0.091553 | 122.3053 | 122.2321 | -0.045776 | 122.2549 | 122.1497 | -0.082397 | -0.036621 | 122.4564 | 122.3145 | 122.2961 | -0.21973 | 122.3602 | 122.3694 | 122.2687 | -0.17395
1976.9531 | 122.5113 | -122.3282 | 0.13733 | -0.016174 | 0.012625 | 0.0061481 | 0.0058939 | 0.054433 | -0.0090491 | -0.0065369 | -0.00083936 | -0.002854 | -0.031417 | 0.03858 | 0.0027577 | 0.0058468 | 0.045776 | 0.073242 | 0.10986 | 0.14648 | 0.14191 | 0.045776 | -0.082397 | 0.013733 | 0.11902 | 0.013733 | 0.054932 | 0.059509 | 0.07782 | -0.022888 | 122.374 | 122.2458 | 0.004578 | 122.4014 | 122.4747 | 0.22888 | -0.091553 | 122.406 | 122.3053 | -0.082397 | 122.3419 | 122.3419 | 0.036621 | -0.07782 | 122.4701 | 122.374 | 122.438 | -0.21973 | 122.3831 | 122.3877 | 122.4472 | -0.16022
1978.7031 | 122.4564 | -122.3145 | 0.15564 | -0.016174 | 0.013052 | 0.0061481 | 0.0067483 | 0.056783 | -0.0047765 | -0.0035461 | 0.0067901 | -0.0034948 | -0.028427 | 0.03858 | 0.0048939 | 0.007983 | 0.10529 | 0.12817 | 0.13275 | 0.16479 | 0.13275 | 0.054932 | -0.064087 | 0.022888 | 0.10986 | -0.036621 | 0.050354 | 0.050354 | 0.059509 | -0.045776 | 122.3694 | 122.2504 | -0.022889 | 122.4426 | 122.4792 | 0.22888 | -0.050354 | 122.374 | 122.2687 | -0.10529 | 122.3373 | 122.2778 | 0.009155 | -0.10529 | 122.4472 | 122.4197 | 122.4472 | -0.21973 | 122.3648 | 122.3648 | 122.4243 | -0.20142
1980.4062 | 122.6074 | -122.2778 | 0.10986 | -0.00091566 | 0.017111 | 0.0042255 | 0.0035441 | 0.055501 | 0.0014185 | -0.0058959 | -0.0084684 | 0.0014184 | -0.030136 | 0.039435 | 0.0068165 | 0.003497 | 0.032043 | 0.004578 | 0.013733 | 0.10529 | 0.17395 | 0.027466 | -0.12817 | -0.013733 | 0.041199 | -0.10529 | 0.064087 | 0.082397 | 0.036621 | -0.059509 | 122.3053 | 122.1497 | 0.064087 | 122.2824 | 122.3831 | 0.23346 | -0.07782 | 122.3145 | 122.2183 | -0.045776 | 122.2641 | 122.1725 | -0.045777 | -0.027466 | 122.4518 | 122.3099 | 122.2916 | -0.23804 | 122.3419 | 122.3602 | 122.319 | -0.16937
1982.1094 | 122.4655 | -122.319 | 0.13275 | -0.00091566 | 0.016898 | 0.0027301 | 0.0063211 | 0.05422 | -0.0022131 | -0.0041869 | -0.00083936 | -0.0002906 | -0.02864 | 0.040289 | 0.0046803 | 0.0060604 | 0.041199 | 0.032043 | 0.045776 | 0.11444 | 0.13275 | 0.036621 | -0.086975 | -0.027466 | 0.054932 | -0.091553 | 0.068665 | 0.073242 | 0.013733 | -0.07782 | 122.3557 | 122.2321 | 0 | 122.3511 | 122.4335 | 0.20142 | -0.091552 | 122.3328 | 122.2412 | -0.064086 | 122.2916 | 122.2275 | -0.013733 | -0.059509 | 122.4518 | 122.3602 | 122.3648 | -0.21973 | 122.3877 | 122.3923 | 122.374 | -0.21057
1983.8594 | 122.5571 | -122.2961 | 0.1236 | -0.00091566 | 0.015189 | 0.0025165 | 0.0026895 | 0.055074 | 0.0020593 | -0.0026917 | -0.00083936 | 0.002273 | -0.028213 | 0.041144 | 0.0066029 | 0.0041378 | 0.032043 | -0.004578 | 0.013733 | 0.091553 | 0.16937 | 0.032043 | -0.09613 | -0.018311 | 0.004578 | -0.14191 | 0.064087 | 0.064087 | 0.027466 | -0.064087 | 122.3282 | 122.2 | 0.045777 | 122.2916 | 122.3877 | 0.18768 | -0.091553 | 122.3236 | 122.2321 | -0.059509 | 122.2778 | 122.1542 | -0.07782 | -0.059509 | 122.4655 | 122.3282 | 122.3099 | -0.21973 | 122.3602 | 122.3602 | 122.3007 | -0.18768
1985.5625 | 122.4701 | -122.3236 | 0.13275 | -0.00091566 | 0.012625 | 0.0040119 | 0.0082437 | 0.052297 | -0.0071265 | -0.0022643 | -0.00083936 | -0.0022132 | -0.029922 | 0.041144 | 0.0016895 | 0.0060604 | 0.086975 | 0.15106 | 0.14648 | 0.17395 | 0.1236 | 0.073242 | -0.082397 | 0.059509 | 0.16022 | 0 | 0.027466 | 0.041199 | 0.064087 | -0.018311 | 122.3968 | 122.2412 | -0.009155 | 122.4747 | 122.4976 | 0.25635 | -0.045776 | 122.3877 | 122.3053 | -0.10529 | 122.3831 | 122.3236 | 0.018311 | -0.091552 | 122.4472 | 122.4106 | 122.4701 | -0.21515 | 122.3511 | 122.3648 | 122.4838 | -0.15106
1987.2656 | 122.5708 | -122.3099 | 0.10071 | 0.0067138 | 0.018179 | -0.00047431 | 0.0014079 | 0.05486 | 0.0018457 | -0.0024779 | -0.0084684 | 0.000564 | -0.03099 | 0.04328 | 0.0063893 | 0.0058468 | 0.064087 | 0.050354 | 0.050354 | 0.10529 | 0.14648 | 0.054932 | -0.10529 | -0.004578 | 0.032043 | -0.11902 | 0.050354 | 0.064087 | 0.032043 | -0.045776 | 122.3648 | 122.2046 | 0.045776 | 122.3602 | 122.4152 | 0.21057 | -0.036621 | 122.3419 | 122.2641 | -0.050354 | 122.3053 | 122.1909 | -0.073243 | -0.036621 | 122.4564 | 122.374 | 122.3602 | -0.20599 | 122.3602 | 122.374 | 122.3419 | -0.14648
1988.9531 | 122.6028 | -122.3145 | 0.12817 | -0.00091566 | 0.015402 | 0.0018757 | 0.0050393 | 0.056142 | -0.00071771 | -0.0024779 | 0.0067901 | 0.002273 | -0.030563 | 0.041357 | 0.0070301 | 0.0056332 | -0.013733 | -0.041199 | 0 | 0.073242 | 0.16937 | 0.022888 | -0.10529 | -0.027466 | -0.013733 | -0.12817 | 0.054932 | 0.082397 | 0.032043 | -0.045776 | 122.3373 | 122.2092 | 0.041199 | 122.2733 | 122.3877 | 0.17853 | -0.14191 | 122.3465 | 122.2687 | -0.073242 | 122.287 | 122.1863 | -0.082398 | -0.045777 | 122.4838 | 122.3007 | 122.3145 | -0.23346 | 122.3694 | 122.3969 | 122.3007 | -0.17395
1990.7344 | 122.5433 | -122.3373 | 0.10986 | -0.0085447 | 0.014334 | 0.0042255 | 0.0063211 | 0.052511 | -0.010117 | -0.0046143 | 0.0067901 | -0.0047766 | -0.032058 | 0.037726 | 0.00062147 | 0.006915 | 0.073242 | 0.14191 | 0.15106 | 0.16937 | 0.11902 | 0.068665 | -0.068665 | 0.068665 | 0.1831 | 0.041199 | 0.022888 | 0.027466 | 0.068665 | -0.013733 | 122.406 | 122.2687 | 0.009156 | 122.4792 | 122.5067 | 0.23804 | -0.036621 | 122.406 | 122.3236 | -0.086975 | 122.406 | 122.3785 | 0.054932 | -0.082397 | 122.4564 | 122.4106 | 122.4884 | -0.17853 | 122.3602 | 122.3648 | 122.5204 | -0.1236
1992.5 | 122.5983 | -122.3236 | 0.13275 | -0.00091566 | 0.013266 | 0.0048663 | -0.00072854 | 0.055074 | -0.0034949 | -0.0031189 | -0.0084684 | 0.0001368 | -0.031845 | 0.039221 | 0.0046803 | 0.0071286 | 0.10986 | 0.13275 | 0.15106 | 0.18768 | 0.12817 | 0.086975 | -0.054932 | 0.09613 | 0.14191 | 0.013733 | 0.022888 | 0.027466 | 0.059509 | 0 | 122.4106 | 122.2687 | -0.004577 | 122.4564 | 122.5113 | 0.24261 | -0.022888 | 122.3831 | 122.3236 | -0.10986 | 122.4197 | 122.3373 | 0.013733 | -0.10529 | 122.4518 | 122.4335 | 122.4747 | -0.18768 | 122.3465 | 122.3511 | 122.4655 | -0.13275
1994.25 | 122.5159 | -122.3694 | 0.14648 | 0.0067138 | 0.0096344 | 0.0037983 | 0.0056803 | 0.054006 | -0.0060583 | -0.0037597 | -0.0084684 | -0.0005042 | -0.034195 | 0.039435 | 0.00062147 | 0.007983 | 0.064087 | 0.086975 | 0.10986 | 0.12817 | 0.13733 | 0.073242 | -0.050354 | 0.018311 | 0.082397 | -0.013733 | 0.036621 | 0.045776 | 0.059509 | -0.027466 | 122.4426 | 122.319 | -0.009155 | 122.4564 | 122.4976 | 0.17853 | -0.082397 | 122.4289 | 122.3419 | -0.10986 | 122.3877 | 122.3557 | 0.013733 | -0.10071 | 122.5067 | 122.4335 | 122.4792 | -0.19684 | 122.406 | 122.4152 | 122.4518 | -0.17395
1995.9531 | 122.5067 | -122.3419 | 0.14191 | 0.014343 | 0.011771 | 0.0055073 | 0.0069621 | 0.056356 | -0.0019995 | -0.0048279 | 0.0067901 | 0.000564 | -0.029495 | 0.041144 | 0.0012623 | 0.0049924 | 0.036621 | 0.022888 | 0.041199 | 0.086975 | 0.15106 | 0.045776 | -0.09613 | -0.036621 | 0.036621 | -0.10071 | 0.068665 | 0.059509 | 0.032043 | -0.054932 | 122.3877 | 122.2458 | 0.009155 | 122.3648 | 122.4289 | 0.1831 | -0.10529 | 122.374 | 122.287 | -0.073242 | 122.3053 | 122.2412 | -0.045776 | -0.082398 | 122.493 | 122.3785 | 122.3831 | -0.23804 | 122.4106 | 122.4014 | 122.3785 | -0.19684
1997.7031 | 122.493 | -122.3648 | 0.15106 | -0.0085447 | 0.011557 | 0.0050799 | 0.0031167 | 0.052724 | -0.0047765 | -0.0048279 | 0.0067901 | -0.0022132 | -0.032486 | 0.038367 | 0.0063893 | 0.0060604 | 0.10986 | 0.13275 | 0.13275 | 0.14191 | 0.13733 | 0.091553 | -0.045776 | 0.068665 | 0.10529 | 0.004578 | 0.022888 | 0.022888 | 0.054932 | -0.041199 | 122.4564 | 122.319 | -0.013733 | 122.4976 | 122.5067 | 0.18768 | -0.041199 | 122.4197 | 122.3236 | -0.12817 | 122.4335 | 122.3694 | 0.045777 | -0.12817 | 122.5021 | 122.4747 | 122.4976 | -0.19684 | 122.3877 | 122.3877 | 122.4701 | -0.19226
1999.4688 | 122.5021 | -122.374 | 0.14191 | -0.0085447 | 0.014334 | 0.0040119 | 0.0069621 | 0.053152 | -0.0032813 | -0.0056823 | -0.0084684 | -0.001145 | -0.031845 | 0.039221 | 0.0031849 | 0.005206 | 0.11444 | 0.16937 | 0.16479 | 0.17853 | 0.13733 | 0.09613 | -0.064087 | 0.068665 | 0.17395 | 0.022888 | 0.032043 | 0.022888 | 0.045776 | -0.013733 | 122.4701 | 122.3099 | -0.004578 | 122.5433 | 122.5525 | 0.24261 | -0.027466 | 122.4197 | 122.3602 | -0.10986 | 122.4426 | 122.3969 | 0.036621 | -0.11902 | 122.5113 | 122.4884 | 122.5388 | -0.20599 | 122.406 | 122.3969 | 122.5479 | -0.15564
2001.2344 | 122.6532 | -122.3145 | 0.10071 | -0.0085447 | 0.014334 | 0.0023029 | 0.0020487 | 0.053365 | 0.00056389 | -0.0024779 | 0.0067901 | 0.001632 | -0.030349 | 0.040289 | 0.0031849 | 0.005206 | 0.082397 | 0.027466 | 0.073242 | 0.1236 | 0.13275 | 0.059509 | -0.068665 | 0.059509 | 0.09613 | -0.022888 | 0.022888 | 0.054932 | 0.068665 | -0.009155 | 122.374 | 122.2458 | 0.032043 | 122.3419 | 122.438 | 0.19226 | -0.018311 | 122.3831 | 122.3053 | -0.07782 | 122.374 | 122.2916 | -0.013733 | -0.045776 | 122.4472 | 122.3969 | 122.3877 | -0.16937 | 122.3373 | 122.3694 | 122.4106 | -0.10986
2003 | 122.5204 | -122.3923 | 0.14648 | -0.0085447 | 0.014975 | 0.0070025 | 0.0033305 | 0.052083 | -0.0039221 | -0.0046143 | -0.00083936 | -0.0024268 | -0.033767 | 0.039862 | 0.0055349 | 0.006915 | 0.09613 | 0.11444 | 0.1236 | 0.13275 | 0.12817 | 0.068665 | -0.064087 | 0.045776 | 0.086975 | -0.004578 | 0.041199 | 0.036621 | 0.059509 | -0.013733 | 122.4609 | 122.3282 | -0.01831 | 122.5067 | 122.525 | 0.19684 | -0.050354 | 122.4518 | 122.3785 | -0.10529 | 122.438 | 122.3877 | 0.009155 | -0.10986 | 122.5204 | 122.4884 | 122.5159 | -0.21057 | 122.4335 | 122.4289 | 122.4792 | -0.16022
2004.7031 | 122.5708 | -122.3694 | 0.14648 | -0.0085447 | 0.01348 | 0.0052935 | 0.0058939 | 0.053792 | -0.0077673 | -0.0078185 | -0.0084684 | -0.002854 | -0.032058 | 0.038153 | 0.0023305 | 0.003497 | 0.082397 | 0.11902 | 0.1236 | 0.16937 | 0.1236 | 0.07782 | -0.059509 | 0.064087 | 0.16022 | 0.032043 | 0.041199 | 0.045776 | 0.064087 | -0.009155 | 122.4472 | 122.3099 | -0.022888 | 122.4884 | 122.5388 | 0.22888 | -0.064087 | 122.4335 | 122.3602 | -0.10529 | 122.4335 | 122.4014 | 0.041198 | -0.10071 | 122.493 | 122.4518 | 122.493 | -0.20599 | 122.4106 | 122.4152 | 122.5296 | -0.15564
2006.4688 | 122.6212 | -122.3694 | 0.11902 | 0.0067138 | 0.014334 | 0.0033709 | 0.0024759 | 0.055074 | 0.00099129 | -0.0020507 | -0.0084684 | 0.0027002 | -0.030563 | 0.039648 | 0.0072437 | 0.0060604 | 0.032043 | -0.027466 | 0 | 0.09613 | 0.16022 | 0.036621 | -0.10071 | -0.004578 | -0.013733 | -0.13275 | 0.068665 | 0.059509 | 0.018311 | -0.054932 | 122.406 | 122.2687 | 0.041198 | 122.3419 | 122.4655 | 0.19684 | -0.086976 | 122.3877 | 122.3145 | -0.050354 | 122.3648 | 122.2366 | -0.077819 | -0.05951 | 122.5296 | 122.4014 | 122.3694 | -0.21973 | 122.438 | 122.4289 | 122.3557 | -0.17395
2008.2188 | 122.6486 | -122.3099 | 0.11444 | -0.0085447 | 0.016898 | 0.0048663 | 0.0071757 | 0.052083 | 0.0014185 | -0.0020507 | -0.0084684 | -0.0002906 | -0.029281 | 0.040716 | 0.0061757 | 0.0054196 | 0.068665 | 0.054932 | 0.064087 | 0.12817 | 0.17853 | 0.050354 | -0.082397 | 0.045776 | 0.091553 | -0.064087 | 0.054932 | 0.073242 | 0.041199 | -0.032043 | 122.3602 | 122.2275 | 0.064087 | 122.3648 | 122.438 | 0.21057 | -0.045776 | 122.3511 | 122.2778 | -0.059509 | 122.3557 | 122.2458 | -0.032044 | -0.041199 | 122.4884 | 122.3785 | 122.374 | -0.19684 | 122.3648 | 122.3831 | 122.4014 | -0.14648
2009.9688 | 122.5113 | -122.3923 | 0.12817 | -0.00091566 | 0.014548 | 0.0046527 | 0.0065347 | 0.052297 | -0.0060583 | -0.0035461 | -0.0084684 | -0.0002906 | -0.030563 | 0.040716 | -0.00044673 | 0.0060604 | 0.068665 | 0.10071 | 0.11444 | 0.14191 | 0.14191 | 0.032043 | -0.082397 | -0.009155 | 0.073242 | -0.068665 | 0.050354 | 0.073242 | 0.032043 | -0.054932 | 122.4243 | 122.3099 | 0.013733 | 122.493 | 122.5342 | 0.2243 | -0.059509 | 122.4243 | 122.3373 | -0.07782 | 122.3831 | 122.3236 | -0.013733 | -0.054932 | 122.5342 | 122.4609 | 122.5067 | -0.21057 | 122.4426 | 122.4655 | 122.4655 | -0.18311
2011.6719 | 122.6578 | -122.319 | 0.09613 | -0.0085447 | 0.014761 | 0.0016619 | 0.0052531 | 0.053579 | 0.0014185 | -0.00055532 | 0.0067901 | 0.0024866 | -0.029495 | 0.042425 | 0.0059621 | 0.0028562 | 0.064087 | 0.045776 | 0.045776 | 0.14191 | 0.16479 | 0.027466 | -0.10529 | 0.041199 | 0.082397 | -0.054932 | 0.064087 | 0.059509 | 0.050354 | -0.032043 | 122.3465 | 122.2137 | 0.068665 | 122.3648 | 122.4609 | 0.24719 | -0.032043 | 122.3694 | 122.287 | -0.032043 | 122.3602 | 122.2641 | -0.022889 | -0.036621 | 122.4838 | 122.3831 | 122.3648 | -0.20142 | 122.3831 | 122.3785 | 122.4014 | -0.12817
2013.4219 | 122.5433 | -122.3648 | 0.14648 | -0.0085447 | 0.0096344 | 0.0050799 | 0.0058939 | 0.05187 | -0.0075537 | -0.0048279 | -0.00083936 | -0.0052038 | -0.030349 | 0.038794 | 0.0051075 | 0.0081968 | 0.041199 | 0.07782 | 0.10071 | 0.13275 | 0.14191 | 0.073242 | -0.045776 | 0.018311 | 0.09613 | -0.022888 | 0.041199 | 0.045776 | 0.059509 | -0.018311 | 122.438 | 122.319 | -0.004577 | 122.4426 | 122.4976 | 0.17853 | -0.10529 | 122.4243 | 122.3465 | -0.10529 | 122.3831 | 122.3419 | -0.004577 | -0.10071 | 122.5067 | 122.406 | 122.4655 | -0.19226 | 122.406 | 122.4106 | 122.4609 | -0.16479
2015.1719 | 122.6669 | -122.3328 | 0.10986 | -0.00091566 | 0.015189 | 0.0037983 | 0.0050393 | 0.055074 | 0.00099129 | -0.0031189 | -0.00083936 | 0.0012048 | -0.031417 | 0.041571 | 0.0072437 | 0.0060604 | 0.018311 | -0.004578 | 0.009155 | 0.091553 | 0.16022 | 0.027466 | -0.10529 | -0.009155 | 0 | -0.10071 | 0.068665 | 0.082397 | 0.036621 | -0.050354 | 122.3602 | 122.2275 | 0.050354 | 122.3282 | 122.4243 | 0.19684 | -0.091552 | 122.3694 | 122.2824 | -0.041198 | 122.3236 | 122.2321 | -0.050354 | -0.027466 | 122.493 | 122.3511 | 122.3419 | -0.21515 | 122.4014 | 122.4152 | 122.3328 | -0.16022
2016.9375 | 122.6807 | -122.3328 | 0.10986 | 0.014343 | 0.016257 | 0.0014483 | 0.0033305 | 0.055074 | 0.00013669 | -0.0046143 | 0.0067901 | 0.0020594 | -0.031417 | 0.039862 | 0.0078847 | 0.0062742 | 0.018311 | 0 | 0.018311 | 0.091553 | 0.16022 | 0.036621 | -0.086975 | 0.004578 | 0 | -0.086975 | 0.050354 | 0.064087 | 0.045776 | -0.054932 | 122.3694 | 122.2458 | 0.050354 | 122.3328 | 122.4243 | 0.17853 | -0.091552 | 122.3785 | 122.2778 | -0.059509 | 122.3373 | 122.2458 | -0.032043 | -0.045776 | 122.493 | 122.3511 | 122.3511 | -0.19684 | 122.3831 | 122.3969 | 122.3328 | -0.16479
2018.625 | 122.5388 | -122.4014 | 0.11902 | 0.0067138 | 0.010275 | 0.0033709 | 0.0031167 | 0.052938 | -0.0088355 | -0.0044007 | 0.0067901 | -0.0032812 | -0.033767 | 0.039648 | 0.0016895 | 0.0071286 | 0.068665 | 0.07782 | 0.10071 | 0.12817 | 0.1236 | 0.082397 | -0.050354 | 0.009155 | 0.10986 | -0.032043 | 0.041199 | 0.064087 | 0.059509 | -0.027466 | 122.4838 | 122.3511 | 0.004577 | 122.4792 | 122.5296 | 0.17853 | -0.050354 | 122.4609 | 122.374 | -0.07782 | 122.4106 | 122.3694 | -0.004577 | -0.054932 | 122.525 | 122.4701 | 122.5021 | -0.16937 | 122.4426 | 122.4655 | 122.5113 | -0.14649
2020.3906 | 122.525 | -122.4152 | 0.1236 | 0.0067138 | 0.015402 | 0.0042255 | 0.0078165 | 0.05422 | -0.0032813 | -0.0054687 | 0.01442 | -0.0009314 | -0.032058 | 0.039648 | 0.0027577 | 0.0071286 | 0.11444 | 0.11444 | 0.13733 | 0.17395 | 0.13275 | 0.073242 | -0.050354 | 0.041199 | 0.1236 | -0.018311 | 0.041199 | 0.050354 | 0.041199 | -0.036621 | 122.4884 | 122.3648 | 0.009155 | 122.5296 | 122.5891 | 0.2243 | -0.009155 | 122.4564 | 122.3785 | -0.082397 | 122.4564 | 122.3969 | 0.01831 | -0.073242 | 122.5479 | 122.5296 | 122.5525 | -0.17395 | 122.4564 | 122.4655 | 122.5388 | -0.16022
2022.1562 | 122.5891 | -122.3969 | 0.14191 | -0.0085447 | 0.01348 | 0.0055073 | 0.0046121 | 0.053792 | -0.0058447 | -0.0044007 | -0.0084684 | -0.0024268 | -0.032486 | 0.037939 | 0.00019427 | 0.0058468 | 0.054932 | 0.086975 | 0.10071 | 0.14191 | 0.12817 | 0.064087 | -0.068665 | 0.032043 | 0.1236 | -0.004578 | 0.041199 | 0.032043 | 0.068665 | -0.032043 | 122.4609 | 122.3282 | -0.013733 | 122.4838 | 122.5388 | 0.21057 | -0.086975 | 122.4655 | 122.3648 | -0.10071 | 122.4289 | 122.3923 | 0.027465 | -0.10986 | 122.525 | 122.4518 | 122.4976 | -0.21057 | 122.4381 | 122.4289 | 122.5204 | -0.17395
2023.9375 | 122.493 | -122.2549 | 0.10529 | -0.016174 | 0.020529 | 0.0033709 | 0.0058939 | 0.054647 | 0.0016321 | -0.0037597 | -0.00083936 | 0.001632 | -0.028854 | 0.042212 | 0.0048939 | 0.0037106 | 0.064087 | 0.036621 | 0.041199 | 0.1236 | 0.15106 | 0.036621 | -0.10529 | 0.013733 | 0.064087 | -0.07782 | 0.059509 | 0.041199 | 0.009155 | -0.050354 | 122.2916 | 122.1497 | 0.045776 | 122.2916 | 122.3785 | 0.22888 | -0.041199 | 122.2641 | 122.2046 | -0.045777 | 122.2687 | 122.1771 | -0.027466 | -0.064087 | 122.406 | 122.319 | 122.2961 | -0.21057 | 122.3145 | 122.2961 | 122.319 | -0.15564
2025.7031 | 122.5525 | -122.4335 | 0.13275 | -0.0085447 | 0.012839 | 0.0048663 | 0.0063211 | 0.053792 | -0.0062719 | -0.0050415 | -0.00083936 | -0.0030676 | -0.029495 | 0.038794 | 0.0010487 | 0.0056332 | 0.036621 | 0.064087 | 0.10071 | 0.13275 | 0.14191 | 0.050354 | -0.059509 | 0.009155 | 0.09613 | -0.022888 | 0.009155 | 0.045776 | 0.041199 | -0.022888 | 122.4838 | 122.374 | 0.009156 | 122.4976 | 122.5662 | 0.19226 | -0.09613 | 122.4747 | 122.4106 | -0.1236 | 122.4426 | 122.4106 | 0 | -0.086975 | 122.5754 | 122.4701 | 122.5342 | -0.19226 | 122.4426 | 122.4792 | 122.5296 | -0.15564
2027.4062 | 122.612 | -122.3831 | 0.10071 | -0.00091566 | 0.012839 | 0.0046527 | 0.0016215 | 0.055074 | 0.0033411 | -0.0041869 | -0.00083936 | 0.0020594 | -0.031204 | 0.04093 | 0.0083119 | 0.0054196 | 0.009155 | -0.022888 | -0.004578 | 0.073242 | 0.15106 | 0.027466 | -0.09613 | -0.032043 | -0.022888 | -0.16479 | 0.068665 | 0.068665 | 0.022888 | -0.036621 | 122.4106 | 122.287 | 0.050354 | 122.3602 | 122.4564 | 0.16937 | -0.091553 | 122.406 | 122.3465 | -0.032043 | 122.3511 | 122.2183 | -0.12817 | -0.032043 | 122.5342 | 122.3923 | 122.3785 | -0.19684 | 122.4518 | 122.4518 | 122.3602 | -0.13733
2029.0938 | 122.6898 | -122.3831 | 0.10529 | 0.0067138 | 0.012625 | 0.0031573 | 0.0039713 | 0.052938 | -0.0017859 | -0.0031189 | -0.00083936 | 0.000564 | -0.03099 | 0.041144 | 0.0057485 | 0.0056332 | 0.036621 | -0.004578 | 0.022888 | 0.07782 | 0.14191 | 0.032043 | -0.082397 | 0.009155 | 0.027466 | -0.073242 | 0.050354 | 0.050354 | 0.036621 | -0.018311 | 122.4152 | 122.3007 | 0.036621 | 122.3785 | 122.4609 | 0.16022 | -0.068665 | 122.4197 | 122.3648 | -0.054932 | 122.3923 | 122.3099 | -0.054931 | -0.054932 | 122.525 | 122.4197 | 122.406 | -0.18768 | 122.4335 | 122.4335 | 122.4106 | -0.1236
2030.8594 | 122.58 | -122.3923 | 0.11902 | -0.00091566 | 0.01583 | 0.0059345 | 0.0078165 | 0.05422 | -0.0071265 | -0.0058959 | -0.016098 | -0.0013586 | -0.031204 | 0.041571 | -0.00023313 | 0.0060604 | 0.10986 | 0.16479 | 0.14648 | 0.17853 | 0.12817 | 0.064087 | -0.073242 | 0.059509 | 0.1831 | 0.041199 | 0.013733 | 0.032043 | 0.050354 | -0.022888 | 122.4564 | 122.319 | 0.009155 | 122.5571 | 122.5708 | 0.25177 | -0.009156 | 122.4426 | 122.3694 | -0.10529 | 122.4518 | 122.4335 | 0.064087 | -0.086976 | 122.5204 | 122.5021 | 122.5388 | -0.19226 | 122.406 | 122.4243 | 122.5754 | -0.14191
2032.625 | 122.6807 | -122.3602 | 0.11444 | 0.0067138 | 0.017752 | 0.0031573 | 0.0065347 | 0.055929 | 0.0020593 | -0.0031189 | -0.016098 | 0.0018456 | -0.029281 | 0.041785 | 0.0063893 | 0.001788 | 0.059509 | 0.032043 | 0.050354 | 0.1236 | 0.16479 | 0.036621 | -0.10986 | 0.036621 | 0.064087 | -0.073242 | 0.045776 | 0.045776 | 0.036621 | -0.059509 | 122.3969 | 122.2504 | 0.050354 | 122.3923 | 122.4838 | 0.23346 | -0.054932 | 122.3969 | 122.3007 | -0.068665 | 122.3969 | 122.287 | -0.013733 | -0.068665 | 122.525 | 122.4197 | 122.4106 | -0.2243 | 122.406 | 122.406 | 122.4243 | -0.17395
2034.375 | 122.6349 | -122.3923 | 0.09613 | -0.00091566 | 0.016898 | 0.0018757 | 0.0020487 | 0.054647 | 0.0033411 | -0.0018371 | 0.0067901 | 0.0029138 | -0.032486 | 0.04093 | 0.0083119 | 0.0064878 | 0.032043 | 0.009155 | 0.018311 | 0.086975 | 0.14191 | 0.022888 | -0.11444 | -0.013733 | 0.009155 | -0.12817 | 0.050354 | 0.068665 | 0.022888 | -0.054932 | 122.4152 | 122.2778 | 0.045777 | 122.4014 | 122.4792 | 0.20142 | -0.064087 | 122.4152 | 122.3373 | -0.045776 | 122.3785 | 122.2641 | -0.073242 | -0.027465 | 122.5342 | 122.4243 | 122.4106 | -0.21057 | 122.4426 | 122.4609 | 122.4014 | -0.15106
2036.0781 | 122.5891 | -122.4197 | 0.12817 | -0.00091566 | 0.013693 | 0.0052935 | 0.0048257 | 0.052938 | -0.0084081 | -0.0058959 | -0.0084684 | -0.002854 | -0.029495 | 0.039221 | 0.0014759 | 0.007983 | 0.013733 | 0.064087 | 0.086975 | 0.11902 | 0.12817 | 0.050354 | -0.073242 | 0.009155 | 0.10986 | -0.022888 | 0.036621 | 0.036621 | 0.050354 | -0.036621 | 122.4701 | 122.3465 | 0 | 122.4838 | 122.5388 | 0.19226 | -0.11444 | 122.4701 | 122.3831 | -0.091553 | 122.4289 | 122.3969 | 0.013733 | -0.091553 | 122.5479 | 122.4335 | 122.5067 | -0.20142 | 122.4564 | 122.4564 | 122.5296 | -0.1648
2037.8281 | 122.1176 | -121.9025 | 0.11902 | -0.0085447 | 0.016898 | 0.0027301 | 0.0048257 | 0.053152 | 0.0022729 | -0.0014099 | 0.0067901 | 0.0037684 | -0.030349 | 0.041571 | 0.0083119 | 0.0028562 | 0.064087 | 0.032043 | 0.018311 | 0.10529 | 0.15106 | 0.022888 | -0.091553 | 0 | 0.032043 | -0.11444 | 0.050354 | 0.07782 | 0.032043 | -0.054932 | 121.9254 | 121.8109 | 0.032043 | 121.9345 | 122.0078 | 0.19684 | -0.054932 | 121.9345 | 121.8475 | -0.068665 | 121.9025 | 121.788 | -0.059509 | -0.041199 | 122.0535 | 121.9666 | 121.9208 | -0.21057 | 121.9528 | 121.9803 | 121.9345 | -0.17395
2039.5938 | 122.4609 | -122.1863 | 0.10071 | -0.00091566 | 0.014761 | 0.0040119 | 0.0022623 | 0.055074 | -0.0043493 | -0.0020507 | -0.00083936 | -0.0009314 | -0.032058 | 0.041357 | 0.0061757 | 0.006915 | 0.091553 | 0.086975 | 0.10529 | 0.16022 | 0.13275 | 0.064087 | -0.082397 | 0.073242 | 0.11902 | 0 | 0.009155 | 0.045776 | 0.073242 | -0.013733 | 122.2504 | 122.1039 | 0.032043 | 122.2733 | 122.3465 | 0.24261 | -0.009155 | 122.2595 | 122.1725 | -0.091553 | 122.2595 | 122.1863 | 0.013733 | -0.054932 | 122.319 | 122.2778 | 122.2916 | -0.18311 | 122.1954 | 122.2321 | 122.3053 | -0.11444
2041.3594 | 122.5021 | -122.1954 | 0.11902 | -0.0085447 | 0.017538 | 0.0033709 | 0.0050393 | 0.055715 | -0.0011451 | -0.0020507 | -0.00083936 | 0.0020594 | -0.031845 | 0.041571 | 0.0066029 | 0.0049924 | 0.064087 | 0.050354 | 0.064087 | 0.13275 | 0.15106 | 0.032043 | -0.082397 | 0.027466 | 0.082397 | -0.050354 | 0.050354 | 0.073242 | 0.045776 | -0.050354 | 122.2275 | 122.113 | 0.032043 | 122.2458 | 122.3282 | 0.21515 | -0.054932 | 122.2412 | 122.1451 | -0.068665 | 122.2229 | 122.1451 | 0 | -0.045777 | 122.3465 | 122.2595 | 122.2595 | -0.20142 | 122.2458 | 122.2687 | 122.2778 | -0.16937
2043.0312 | 122.4609 | -122.2366 | 0.1236 | -0.00091566 | 0.010916 | 0.0050799 | 0.0046121 | 0.053152 | -0.0099035 | -0.0056823 | 0.0067901 | -0.0041358 | -0.032913 | 0.039007 | 0.0021169 | 0.0073422 | 0.041199 | 0.068665 | 0.11444 | 0.14191 | 0.12817 | 0.073242 | -0.064087 | 0.022888 | 0.11902 | 0.013733 | 0.032043 | 0.032043 | 0.050354 | -0.018311 | 122.3099 | 122.1725 | 0.004578 | 122.3053 | 122.3785 | 0.20599 | -0.082397 | 122.287 | 122.2183 | -0.091553 | 122.2595 | 122.2504 | 0.032044 | -0.091553 | 122.3648 | 122.2778 | 122.3511 | -0.18768 | 122.2687 | 122.2687 | 122.3557 | -0.14191
2044.7812 | 122.4243 | -122.2824 | 0.14648 | -0.00091566 | 0.009848 | 0.0057209 | 0.0037577 | 0.05486 | -0.0069129 | -0.0037597 | -0.0084684 | -0.0019996 | -0.032272 | 0.038153 | 0.0029713 | 0.0049924 | 0.07782 | 0.082397 | 0.10529 | 0.12817 | 0.13275 | 0.073242 | -0.064087 | 0.018311 | 0.082397 | -0.022888 | 0.032043 | 0.045776 | 0.054932 | -0.018311 | 122.3557 | 122.2183 | -0.013733 | 122.3648 | 122.4106 | 0.19226 | -0.068664 | 122.3373 | 122.2641 | -0.11444 | 122.3007 | 122.2595 | -0.004577 | -0.10071 | 122.4152 | 122.3602 | 122.3877 | -0.21057 | 122.3145 | 122.3282 | 122.3648 | -0.16479
2046.5469 | 122.5571 | -122.2458 | 0.10529 | -0.016174 | 0.015402 | 0.0061481 | 0.0039713 | 0.054006 | 0.00099129 | -0.0037597 | 0.01442 | 0.0018456 | -0.031631 | 0.041357 | 0.0055349 | 0.0064878 | 0.045776 | 0 | 0.027466 | 0.11444 | 0.15564 | 0.036621 | -0.10071 | 0 | 0.064087 | -0.09613 | 0.068665 | 0.07782 | 0.018311 | -0.041199 | 122.2824 | 122.1451 | 0.050354 | 122.2458 | 122.3602 | 0.21515 | -0.05951 | 122.2641 | 122.2046 | -0.036621 | 122.2458 | 122.1497 | -0.054931 | -0.027466 | 122.4014 | 122.2916 | 122.2733 | -0.20599 | 122.3145 | 122.3236 | 122.3099 | -0.14649
2048.2344 | 122.5754 | -122.2458 | 0.10529 | -0.016174 | 0.018393 | 0.0040119 | 0.0061075 | 0.053365 | -0.0017859 | -0.0041869 | -0.00083936 | 0.0003504 | -0.026291 | 0.041357 | 0.0048939 | 0.0037106 | 0.032043 | 0.018311 | 0.036621 | 0.10986 | 0.16937 | 0.027466 | -0.10071 | 0.018311 | 0.068665 | -0.082397 | 0.064087 | 0.073242 | 0.045776 | -0.045776 | 122.2733 | 122.1451 | 0.064087 | 122.2641 | 122.3557 | 0.21057 | -0.073243 | 122.2916 | 122.2 | -0.041199 | 122.2641 | 122.1634 | -0.036621 | -0.032044 | 122.4152 | 122.2778 | 122.2824 | -0.20599 | 122.3099 | 122.319 | 122.3145 | -0.15106
2050 | 122.5113 | -122.2916 | 0.13733 | -0.016174 | 0.01348 | 0.0048663 | 0.0067483 | 0.052938 | -0.0077673 | -0.0046143 | -0.00083936 | -0.0043494 | -0.029922 | 0.041144 | 0.0044667 | 0.0056332 | 0.10071 | 0.15564 | 0.16022 | 0.16479 | 0.12817 | 0.054932 | -0.054932 | 0.054932 | 0.17853 | 0.045776 | 0.032043 | 0.027466 | 0.07782 | -0.013733 | 122.3465 | 122.2366 | -0.009155 | 122.4472 | 122.4564 | 0.21973 | -0.036621 | 122.3694 | 122.2778 | -0.10529 | 122.3465 | 122.3373 | 0.059509 | -0.10986 | 122.4197 | 122.3923 | 122.4518 | -0.19226 | 122.3236 | 122.319 | 122.4701 | -0.15106
2051.75 | 122.4747 | -122.3236 | 0.15106 | -0.00091566 | 0.010703 | 0.0037983 | 0.0033305 | 0.053792 | -0.0052039 | -0.0039733 | 0.0067901 | -0.0034948 | -0.031631 | 0.040076 | 0.0019033 | 0.0077694 | 0.09613 | 0.10529 | 0.10986 | 0.12817 | 0.1236 | 0.091553 | -0.07782 | 0.027466 | 0.082397 | -0.027466 | 0.022888 | 0.045776 | 0.059509 | -0.022888 | 122.4152 | 122.2458 | -0.027466 | 122.4289 | 122.4518 | 0.20599 | -0.054932 | 122.3831 | 122.3007 | -0.12817 | 122.3511 | 122.2961 | -0.004578 | -0.10529 | 122.4472 | 122.4197 | 122.4335 | -0.22888 | 122.3465 | 122.3694 | 122.406 | -0.17395
2053.5 | 117.1783 | -78.3966 | 38.5025 | -0.00091566 | 0.016257 | 0.0042255 | 0.0046121 | 0.052297 | -0.0037085 | -0.0050415 | -0.0084684 | 0.0014184 | -0.033767 | 0.039862 | 0.0038259 | 0.0024288 | 0 | -0.004578 | 0 | 0.050354 | 0.13275 | 0 | -0.1236 | -0.07782 | 0 | -0.13275 | 0.054932 | 0.059509 | -0.009155 | -0.086975 | 78.3966 | 78.273 | -38.3698 | 78.392 | 78.447 | 0.17395 | -38.5025 | 78.3875 | 78.3096 | -38.4476 | 78.3188 | 78.2639 | -0.045776 | -38.443 | 78.5294 | 78.3966 | 78.3966 | -38.6261 | 78.4515 | 78.4561 | 78.3966 | -38.5895
2055.25 | 122.3511 | -122.081 | 0.09613 | -0.0085447 | 0.019034 | 0.0014483 | 0.0056803 | 0.055715 | -0.00093131 | -0.0048279 | -0.00083936 | 0.003982 | -0.029708 | 0.040716 | 0.0031849 | 0.0026426 | 0.032043 | 0.004578 | 0.018311 | 0.10529 | 0.16937 | 0.022888 | -0.10986 | 0.004578 | 0.050354 | -0.09613 | 0.059509 | 0.068665 | 0.018311 | -0.050354 | 122.1039 | 121.9711 | 0.073243 | 122.0856 | 122.1863 | 0.21515 | -0.064087 | 122.0993 | 122.0306 | -0.036621 | 122.0856 | 121.9849 | -0.045776 | -0.027465 | 122.2504 | 122.113 | 122.0993 | -0.20599 | 122.1405 | 122.1497 | 122.1313 | -0.14648
2056.9688 | 122.1588 | -121.7194 | 0.10071 | -0.00091566 | 0.015402 | 0.0040119 | 0.0039713 | 0.052297 | 0.0012049 | -0.0020507 | -0.00083936 | 0.003341 | -0.029495 | 0.042212 | 0.0051075 | 0.0043516 | 0.054932 | 0.050354 | 0.045776 | 0.10529 | 0.17853 | 0.036621 | -0.09613 | 0.018311 | 0.091553 | -0.07782 | 0.050354 | 0.07782 | 0.032043 | -0.059509 | 121.756 | 121.6232 | 0.07782 | 121.7697 | 121.8246 | 0.20142 | -0.045776 | 121.7514 | 121.6599 | -0.050354 | 121.7377 | 121.6415 | -0.018311 | -0.022888 | 121.8979 | 121.7743 | 121.7651 | -0.19684 | 121.7697 | 121.7972 | 121.8109 | -0.16022
2058.7344 | 122.0673 | -121.6644 | 0.091553 | 0.0067138 | 0.017752 | 0.0023029 | 0.0029031 | 0.053365 | -7.6908e-05 | -0.0031189 | -0.0084684 | 0.003982 | -0.030563 | 0.041571 | 0.0066029 | 0.005206 | 0.073242 | 0.022888 | 0.050354 | 0.11444 | 0.15564 | 0.022888 | -0.10071 | 0.018311 | 0.09613 | -0.073242 | 0.050354 | 0.068665 | 0.050354 | -0.059509 | 121.6873 | 121.5637 | 0.064087 | 121.6873 | 121.7789 | 0.21515 | -0.018311 | 121.7148 | 121.6049 | -0.041199 | 121.6827 | 121.5912 | -0.013733 | -0.022888 | 121.8201 | 121.7377 | 121.7148 | -0.19226 | 121.7148 | 121.7331 | 121.7606 | -0.15106
2060.4375 | 121.8201 | -121.431 | 0.10529 | -0.00091566 | 0.010489 | 0.0031573 | 0.0024759 | 0.053152 | -0.0026403 | -0.0039733 | -0.00083936 | -0.001145 | -0.032486 | 0.04093 | 0.0044667 | 0.0067014 | 0.11902 | 0.1236 | 0.14648 | 0.1831 | 0.11444 | 0.07782 | -0.07782 | 0.082397 | 0.12817 | 0.013733 | 0.018311 | 0.027466 | 0.059509 | -0.018311 | 121.5088 | 121.3531 | 0.009155 | 121.5546 | 121.6141 | 0.26092 | 0.013733 | 121.4905 | 121.4127 | -0.086975 | 121.5134 | 121.4447 | 0.032044 | -0.07782 | 121.5454 | 121.55 | 121.5775 | -0.18311 | 121.4493 | 121.4584 | 121.5591 | -0.1236
2062.1875 | 121.9849 | -121.7697 | 0.14191 | -0.0085447 | 0.012412 | 0.0048663 | 0.0054667 | 0.053365 | -0.0056311 | -0.0041869 | 0.0067901 | -0.0032812 | -0.031204 | 0.039007 | 0.0038259 | 0.0077694 | 0.10071 | 0.15106 | 0.15564 | 0.17395 | 0.1236 | 0.064087 | -0.068665 | 0.054932 | 0.16479 | 0.004578 | 0.013733 | 0.027466 | 0.054932 | -0.032043 | 121.8338 | 121.701 | -0.018311 | 121.9208 | 121.9437 | 0.24261 | -0.041199 | 121.8246 | 121.7377 | -0.12817 | 121.8246 | 121.7743 | 0.036621 | -0.11444 | 121.8933 | 121.8704 | 121.9254 | -0.21057 | 121.7834 | 121.7972 | 121.9345 | -0.17395
2063.9531 | 122.0352 | -121.8613 | 0.13275 | -0.00091566 | 0.011343 | 0.0042255 | 0.0058939 | 0.054647 | -0.0054175 | -0.0037597 | -0.00083936 | -0.0019996 | -0.031204 | 0.041357 | 0.0016895 | 0.0043516 | 0.11444 | 0.13733 | 0.16022 | 0.16479 | 0.1236 | 0.073242 | -0.068665 | 0.064087 | 0.16022 | 0.027466 | 0.018311 | 0.054932 | 0.064087 | -0.009155 | 121.9345 | 121.7926 | -0.009155 | 121.9986 | 122.0261 | 0.23346 | -0.01831 | 121.9254 | 121.8521 | -0.11444 | 121.9254 | 121.8887 | 0.036621 | -0.077819 | 121.9849 | 121.9757 | 122.0215 | -0.20142 | 121.8796 | 121.9162 | 122.0215 | -0.14191
2065.7031 | 122.1725 | -121.8613 | 0.10986 | -0.016174 | 0.013907 | 0.0029437 | 0.0020487 | 0.057638 | -0.0028539 | -0.0020507 | 0.0067901 | 0.0001368 | -0.033554 | 0.039862 | 0.0074575 | 0.0060604 | 0.1236 | 0.10986 | 0.13733 | 0.16937 | 0.14191 | 0.073242 | -0.073242 | 0.091553 | 0.11444 | 0 | 0.027466 | 0.013733 | 0.059509 | -0.004578 | 121.9345 | 121.788 | 0.032044 | 121.9711 | 122.0306 | 0.24261 | 0.013733 | 121.9208 | 121.8567 | -0.082397 | 121.9528 | 121.8613 | 0.004578 | -0.09613 | 122.0032 | 121.9849 | 121.9986 | -0.18311 | 121.8887 | 121.875 | 121.9757 | -0.11444
2067.4062 | 122.0673 | -121.9299 | 0.13733 | -0.00091566 | 0.011343 | 0.0023029 | 0.0048257 | 0.053792 | -0.0024267 | -0.0046143 | -0.00083936 | -0.0019996 | -0.029495 | 0.039435 | 0.0016895 | 0.0037106 | 0.11902 | 0.1236 | 0.14648 | 0.13733 | 0.12817 | 0.064087 | -0.050354 | 0.059509 | 0.10986 | 0.009155 | 0.027466 | 0.032043 | 0.041199 | -0.036621 | 121.994 | 121.8796 | -0.009155 | 122.0535 | 122.0673 | 0.18768 | -0.01831 | 121.9711 | 121.8933 | -0.10986 | 121.9894 | 121.9391 | 0.045776 | -0.10529 | 122.0581 | 122.049 | 122.0764 | -0.18768 | 121.9574 | 121.962 | 122.0398 | -0.17395
2069.0938 | 121.9574 | -121.9345 | 0.15106 | -0.0085447 | 0.01647 | 0.0057209 | 0.0078165 | 0.055501 | -0.0047765 | -0.0061095 | 0.01442 | -0.0024268 | -0.031631 | 0.040289 | 0.0066029 | 0.005206 | 0.068665 | 0.073242 | 0.082397 | 0.12817 | 0.15106 | 0.050354 | -0.07782 | -0.032043 | 0.059509 | -0.07782 | 0.07782 | 0.064087 | 0.004578 | -0.068665 | 121.9849 | 121.8567 | 0 | 122.0078 | 122.0627 | 0.20599 | -0.082397 | 121.9391 | 121.8658 | -0.073242 | 121.9025 | 121.8567 | -0.009155 | -0.086975 | 122.0856 | 122.0032 | 122.0169 | -0.22888 | 122.0123 | 121.9986 | 121.994 | -0.21973
2070.8438 | 122.2366 | -121.9162 | 0.10529 | 0.0067138 | 0.011771 | 0.0037983 | 0.0014079 | 0.051656 | -0.0019995 | -0.0035461 | -0.00083936 | 0.0012048 | -0.029495 | 0.041357 | 0.0059621 | 0.0041378 | 0.091553 | 0.07782 | 0.09613 | 0.14191 | 0.11902 | 0.054932 | -0.059509 | 0.07782 | 0.10529 | -0.013733 | 0.018311 | 0.032043 | 0.064087 | -0.009155 | 121.9711 | 121.8567 | 0.013733 | 121.994 | 122.0581 | 0.20142 | -0.013733 | 121.9803 | 121.907 | -0.086975 | 121.994 | 121.9025 | -0.004578 | -0.073243 | 122.0352 | 122.0078 | 122.0123 | -0.16479 | 121.9345 | 121.9482 | 122.0215 | -0.11444
2072.625 | 122.1863 | -121.9437 | 0.10986 | 0.014343 | 0.017752 | 0.0016619 | 0.0029031 | 0.055074 | 0.0012049 | -0.0033325 | -0.0084684 | 0.0031274 | -0.029708 | 0.042853 | 0.0061757 | 0.0043516 | 0.027466 | -0.022888 | 0.018311 | 0.09613 | 0.16479 | 0.032043 | -0.10529 | -0.050354 | -0.018311 | -0.15106 | 0.064087 | 0.073242 | 0.050354 | -0.059509 | 121.9757 | 121.8384 | 0.054932 | 121.9208 | 122.0398 | 0.20142 | -0.082397 | 121.994 | 121.8842 | -0.045776 | 121.8933 | 121.7926 | -0.091553 | -0.036621 | 122.1085 | 121.9711 | 121.962 | -0.21515 | 122.0078 | 122.0169 | 121.9254 | -0.16937
2074.3906 | 122.2229 | -121.9345 | 0.12817 | 0.0067138 | 0.01647 | 0.0010211 | 0.0022623 | 0.05486 | -0.00029051 | -0.0029053 | 0.0067901 | 0.0001368 | -0.030777 | 0.042212 | 0.0085255 | 0.0056332 | 0.022888 | -0.041199 | 0.004578 | 0.086975 | 0.15106 | 0.018311 | -0.10071 | -0.032043 | -0.009155 | -0.1236 | 0.073242 | 0.073242 | 0.027466 | -0.054932 | 121.9528 | 121.8338 | 0.022888 | 121.8933 | 122.0215 | 0.18768 | -0.10529 | 121.962 | 121.8796 | -0.054932 | 121.9025 | 121.8109 | -0.068664 | -0.054932 | 122.0856 | 121.9574 | 121.9391 | -0.22888 | 122.0078 | 122.0078 | 121.9254 | -0.18311
2076.0938 | 121.4493 | -121.4951 | 0.14648 | -0.016174 | 0.014761 | 0.0052935 | 0.0086709 | 0.05422 | -0.0079809 | -0.0044007 | -0.0084684 | -0.0030676 | -0.031845 | 0.039221 | 0.0014759 | 0.0039242 | 0.11902 | 0.15564 | 0.15564 | 0.17395 | 0.10529 | 0.068665 | -0.068665 | 0.068665 | 0.18768 | 0.032043 | 0.018311 | 0.050354 | 0.068665 | -0.013733 | 121.5637 | 121.4264 | -0.041198 | 121.6507 | 121.669 | 0.24261 | -0.027465 | 121.5637 | 121.4813 | -0.12817 | 121.5637 | 121.5271 | 0.045776 | -0.09613 | 121.6003 | 121.6141 | 121.6507 | -0.21515 | 121.5134 | 121.5454 | 121.6827 | -0.16022
2077.8438 | 121.5546 | -121.5317 | 0.12817 | -0.00091566 | 0.01113 | 0.0067889 | 0.0043985 | 0.05422 | -0.0054175 | -0.0039733 | 0.0067901 | -0.0043494 | -0.031417 | 0.03858 | 0.0025441 | 0.006915 | 0.068665 | 0.091553 | 0.1236 | 0.13275 | 0.15106 | 0.045776 | -0.054932 | 0.032043 | 0.13733 | 0.022888 | 0.022888 | 0.036621 | 0.068665 | -0.032043 | 121.5775 | 121.4767 | 0.022888 | 121.6232 | 121.6644 | 0.18768 | -0.059509 | 121.6003 | 121.4996 | -0.10529 | 121.5637 | 121.5546 | 0.054931 | -0.091553 | 121.6827 | 121.6003 | 121.6553 | -0.18311 | 121.5546 | 121.5683 | 121.669 | -0.16022
2079.6094 | 122.2412 | -121.9849 | 0.11444 | -0.00091566 | 0.016043 | 0.0016619 | 0.0043985 | 0.052724 | 0.0024865 | -0.0029053 | 0.0067901 | 0.0020594 | -0.028 | 0.043066 | 0.0066029 | 0.0060604 | -0.004578 | -0.050354 | 0 | 0.073242 | 0.15564 | 0.018311 | -0.10529 | -0.022888 | -0.018311 | -0.14191 | 0.041199 | 0.073242 | 0.018311 | -0.086975 | 122.0032 | 121.8796 | 0.041199 | 121.9345 | 122.0581 | 0.17853 | -0.11902 | 122.0032 | 121.8979 | -0.073242 | 121.962 | 121.843 | -0.054932 | -0.041199 | 122.1405 | 121.9803 | 121.9849 | -0.21973 | 122.0261 | 122.0581 | 121.9666 | -0.20142
2081.3125 | 122.2321 | -122.0169 | 0.12817 | -0.0085447 | 0.018607 | 0.0025165 | 0.0058939 | 0.053365 | 0.0018457 | -0.0026917 | -0.0084684 | 0.0007776 | -0.028427 | 0.042212 | 0.0076711 | 0.0045652 | 0.018311 | -0.036621 | 0 | 0.086975 | 0.16479 | 0.045776 | -0.10529 | -0.032043 | -0.027466 | -0.15106 | 0.059509 | 0.068665 | 0.022888 | -0.054932 | 122.0627 | 121.9116 | 0.036621 | 121.9803 | 122.1039 | 0.19226 | -0.10986 | 122.0398 | 121.962 | -0.068665 | 121.9849 | 121.8658 | -0.09613 | -0.059509 | 122.1817 | 122.0352 | 122.0169 | -0.23346 | 122.0764 | 122.0856 | 121.9894 | -0.18311
2083 | 122.2641 | -122.0169 | 0.10529 | -0.0085447 | 0.016257 | 0.0020893 | 0.0035441 | 0.053365 | 0.0014185 | -0.0016235 | -0.0084684 | 0.0014184 | -0.029922 | 0.042853 | 0.0059621 | 0.0067014 | 0.004578 | -0.036621 | -0.004578 | 0.07782 | 0.15564 | 0.036621 | -0.086975 | -0.036621 | -0.009155 | -0.13733 | 0.073242 | 0.086975 | 0.018311 | -0.050354 | 122.0535 | 121.9299 | 0.050354 | 121.9803 | 122.0947 | 0.16479 | -0.10071 | 122.0352 | 121.9666 | -0.032044 | 121.9803 | 121.8796 | -0.086975 | -0.018311 | 122.1725 | 122.0215 | 122.0123 | -0.19226 | 122.0901 | 122.1039 | 122.0078 | -0.15564
2084.75 | 121.8384 | -121.5637 | 0.13275 | -0.0085447 | 0.011557 | 0.0061481 | 0.0073893 | 0.052083 | -0.0077673 | -0.0035461 | -0.0084684 | -0.0032812 | -0.029495 | 0.037939 | 0.0025441 | 0.0081968 | 0.022888 | 0.082397 | 0.09613 | 0.13275 | 0.14191 | 0.059509 | -0.068665 | 0.009155 | 0.10986 | -0.009155 | 0.022888 | 0.050354 | 0.054932 | -0.013733 | 121.6232 | 121.4951 | 0.009156 | 121.6461 | 121.6965 | 0.20142 | -0.10986 | 121.6187 | 121.55 | -0.10986 | 121.5729 | 121.5546 | 0.004578 | -0.082397 | 121.7056 | 121.5866 | 121.6599 | -0.20142 | 121.5866 | 121.6141 | 121.6736 | -0.14648
2086.5312 | 122.3099 | -121.9894 | 0.10071 | 0.0067138 | 0.014761 | 0.0035847 | 0.0016215 | 0.056997 | -0.00050411 | -0.0026917 | -0.00083936 | 0.0003504 | -0.031845 | 0.040503 | 0.0063893 | 0.0056332 | 0.050354 | 0.045776 | 0.068665 | 0.10071 | 0.1236 | 0.050354 | -0.09613 | 0.068665 | 0.09613 | -0.013733 | 0.045776 | 0.027466 | 0.045776 | -0.018311 | 122.0398 | 121.8933 | 0.022888 | 122.0352 | 122.0901 | 0.19684 | -0.050354 | 122.0352 | 121.9711 | -0.054932 | 122.0581 | 121.9757 | 0.004578 | -0.073242 | 122.113 | 122.0398 | 122.0581 | -0.19684 | 122.0352 | 122.0169 | 122.0856 | -0.11902
2088.2188 | 122.3099 | -122.0215 | 0.10986 | -0.00091566 | 0.016043 | 0.0029437 | 0.0020487 | 0.052938 | 0.00077749 | -0.0029053 | -0.0084684 | 0.0024866 | -0.028427 | 0.043921 | 0.0053211 | 0.0045652 | 0.009155 | -0.032043 | -0.009155 | 0.082397 | 0.15564 | 0.027466 | -0.10986 | -0.045776 | -0.013733 | -0.13275 | 0.059509 | 0.068665 | 0.041199 | -0.054932 | 122.049 | 121.9116 | 0.045777 | 121.9894 | 122.1039 | 0.19226 | -0.10071 | 122.0627 | 121.9666 | -0.050354 | 121.9757 | 121.8887 | -0.077819 | -0.041198 | 122.1771 | 122.0306 | 122.0123 | -0.21973 | 122.081 | 122.0901 | 122.0078 | -0.16479
2089.9688 | 122.2595 | -122.0123 | 0.10071 | -0.00091566 | 0.01583 | 0.0025165 | 0.0065347 | 0.054647 | -0.00029051 | -0.0041869 | -0.00083936 | 0.002273 | -0.029068 | 0.044134 | 0.0061757 | 0.0041378 | 0.059509 | 0.073242 | 0.054932 | 0.10529 | 0.15106 | 0.041199 | -0.10071 | 0.018311 | 0.045776 | -0.10529 | 0.054932 | 0.054932 | 0.036621 | -0.059509 | 122.0535 | 121.9116 | 0.050354 | 122.0856 | 122.1176 | 0.20599 | -0.041199 | 122.0489 | 121.9528 | -0.045776 | 122.0306 | 121.907 | -0.045777 | -0.045776 | 122.1634 | 122.0718 | 122.0673 | -0.20142 | 122.0673 | 122.0673 | 122.0581 | -0.16022
2091.6719 | 122.3236 | -122.0261 | 0.10986 | -0.00091566 | 0.015402 | 0.0018757 | 0.0058939 | 0.055074 | 0.00035029 | -0.0026917 | -0.00083936 | 0.003341 | -0.029495 | 0.041571 | 0.0048939 | 0.0056332 | 0.068665 | 0.059509 | 0.064087 | 0.13275 | 0.16479 | 0.041199 | -0.10071 | 0.027466 | 0.10071 | -0.082397 | 0.064087 | 0.073242 | 0.032043 | -0.036621 | 122.0673 | 121.9254 | 0.054932 | 122.0856 | 122.1588 | 0.23346 | -0.041198 | 122.0581 | 121.9894 | -0.045776 | 122.0535 | 121.9437 | -0.045776 | -0.036621 | 122.1909 | 122.0947 | 122.0901 | -0.21057 | 122.0901 | 122.0993 | 122.1268 | -0.14648
2093.4375 | 122.2229 | -122.0856 | 0.13275 | -0.00091566 | 0.0089936 | 0.0029437 | 0.0046121 | 0.054433 | -0.0071265 | -0.0026917 | -0.00083936 | -0.0007178 | -0.030563 | 0.040716 | 0.0019033 | 0.0075558 | 0.091553 | 0.13275 | 0.15106 | 0.15564 | 0.10529 | 0.068665 | -0.054932 | 0.041199 | 0.10986 | 0.009155 | 0 | 0.041199 | 0.064087 | -0.022888 | 122.1542 | 122.0306 | -0.027465 | 122.2183 | 122.2412 | 0.21057 | -0.041198 | 122.1497 | 122.0627 | -0.13275 | 122.1268 | 122.0947 | 0.032043 | -0.091552 | 122.1909 | 122.1771 | 122.2366 | -0.18768 | 122.0856 | 122.1268 | 122.1954 | -0.15564
2095.125 | 122.2137 | -122.0947 | 0.13733 | -0.00091566 | 0.01113 | 0.0048663 | 0.0029031 | 0.054006 | -0.0054175 | -0.0035461 | 0.0067901 | -0.0022132 | -0.031845 | 0.041144 | 0.0029713 | 0.005206 | 0.086975 | 0.11444 | 0.13275 | 0.14648 | 0.10071 | 0.073242 | -0.073242 | 0.027466 | 0.10071 | 0 | 0.036621 | 0.041199 | 0.064087 | -0.032043 | 122.168 | 122.0215 | -0.036621 | 122.2092 | 122.2412 | 0.21973 | -0.050354 | 122.1588 | 122.0627 | -0.10071 | 122.1222 | 122.0947 | 0.032043 | -0.09613 | 122.1954 | 122.1817 | 122.2275 | -0.21057 | 122.1313 | 122.1359 | 122.1954 | -0.16937
2096.8281 | 122.3602 | -122.0718 | 0.10529 | -0.00091566 | 0.012839 | 0.0037983 | 0.0029031 | 0.054006 | -0.00029051 | -0.0035461 | -0.0084684 | -0.0007178 | -0.032486 | 0.039648 | 0.0055349 | 0.0073422 | 0.027466 | -0.013733 | 0.013733 | 0.091553 | 0.15564 | 0.032043 | -0.09613 | -0.009155 | 0.004578 | -0.091553 | 0.064087 | 0.054932 | 0.032043 | -0.045776 | 122.1039 | 121.9757 | 0.050354 | 122.0581 | 122.1634 | 0.18768 | -0.07782 | 122.1039 | 122.0261 | -0.041199 | 122.0627 | 121.9803 | -0.045777 | -0.050354 | 122.2275 | 122.0993 | 122.0856 | -0.20142 | 122.1359 | 122.1268 | 122.0764 | -0.15106
2098.5938 | 122.2366 | -122.0535 | 0.13733 | -0.00091566 | 0.013907 | 0.0027301 | 0.0078165 | 0.055074 | -0.0058447 | -0.0054687 | 0.0067901 | -0.0034948 | -0.030563 | 0.037939 | 0.00062147 | 0.0045652 | 0.10986 | 0.16022 | 0.16022 | 0.16937 | 0.11444 | 0.054932 | -0.068665 | 0.059509 | 0.17395 | 0.027466 | 0.009155 | 0.032043 | 0.050354 | -0.022888 | 122.1085 | 121.9849 | -0.022888 | 122.2137 | 122.2229 | 0.23804 | -0.027466 | 122.1039 | 122.0306 | -0.12817 | 122.113 | 122.081 | 0.050354 | -0.10529 | 122.168 | 122.1634 | 122.2137 | -0.20599 | 122.0627 | 122.0856 | 122.2275 | -0.16022
2100.3438 | 122.3694 | -122.0444 | 0.10071 | 0.0067138 | 0.013052 | -0.00047431 | 0.0041849 | 0.054647 | 0.00056389 | -0.0037597 | 0.0067901 | -7.6996e-05 | -0.030563 | 0.041571 | 0.0036123 | 0.0060604 | 0.045776 | 0.009155 | 0.045776 | 0.10071 | 0.16479 | 0.032043 | -0.086975 | 0.041199 | 0.064087 | -0.050354 | 0.041199 | 0.032043 | 0.036621 | -0.027466 | 122.0764 | 121.9574 | 0.064087 | 122.0535 | 122.1451 | 0.18768 | -0.054932 | 122.081 | 122.0169 | -0.059509 | 122.0856 | 121.994 | -0.022888 | -0.068665 | 122.2092 | 122.0901 | 122.0901 | -0.18768 | 122.0856 | 122.0764 | 122.1085 | -0.12817
2102.1094 | 122.2412 | -122.0993 | 0.13275 | -0.0085447 | 0.015402 | 0.0052935 | 0.0080301 | 0.053365 | -0.0052039 | -0.0031189 | -0.00083936 | -0.0017858 | -0.029708 | 0.039862 | 0.0027577 | 0.0067014 | 0.09613 | 0.15106 | 0.15106 | 0.17395 | 0.11902 | 0.064087 | -0.068665 | 0.064087 | 0.16937 | 0.013733 | 0.022888 | 0.022888 | 0.045776 | -0.013733 | 122.1634 | 122.0306 | -0.013732 | 122.2504 | 122.2733 | 0.24261 | -0.036621 | 122.1451 | 122.0856 | -0.10986 | 122.1634 | 122.113 | 0.027466 | -0.10986 | 122.2183 | 122.1954 | 122.2504 | -0.20142 | 122.1222 | 122.1222 | 122.2687 | -0.14648
2103.8594 | 122.2961 | -122.0901 | 0.1236 | -0.0085447 | 0.012198 | 0.0070025 | 0.0037577 | 0.053365 | -0.0064855 | -0.0061095 | -0.00083936 | -0.0034948 | -0.031631 | 0.039007 | 0.0016895 | 0.0060604 | 0.073242 | 0.10986 | 0.1236 | 0.14191 | 0.1236 | 0.032043 | -0.07782 | 0.045776 | 0.13733 | 0.013733 | 0.032043 | 0.041199 | 0.059509 | -0.041199 | 122.1222 | 122.0123 | 0 | 122.2 | 122.2321 | 0.21973 | -0.050354 | 122.1497 | 122.0489 | -0.091553 | 122.1359 | 122.1039 | 0.054932 | -0.082397 | 122.2137 | 122.1634 | 122.2137 | -0.20142 | 122.1222 | 122.1313 | 122.2275 | -0.16479
2105.625 | 122.3419 | -122.081 | 0.11902 | 0.0067138 | 0.015189 | 0.0027301 | 0.0073893 | 0.056783 | -0.00093131 | -0.0044007 | -0.0084684 | 0.0018456 | -0.030349 | 0.043066 | 0.0066029 | 0.0039242 | 0.013733 | 0.009155 | 0.027466 | 0.086975 | 0.17395 | 0.022888 | -0.10529 | -0.036621 | 0.027466 | -0.11444 | 0.073242 | 0.059509 | 0.009155 | -0.064087 | 122.1039 | 121.9757 | 0.054931 | 122.0901 | 122.168 | 0.19226 | -0.10529 | 122.0901 | 122.0169 | -0.045777 | 122.0444 | 121.9666 | -0.050354 | -0.05951 | 122.2549 | 122.0947 | 122.1085 | -0.22431 | 122.1542 | 122.1405 | 122.1085 | -0.18311
2107.3281 | 122.3145 | -122.1085 | 0.1236 | 0.0067138 | 0.014761 | 0.0072161 | 0.0052531 | 0.05486 | -0.0022131 | -0.0024779 | -0.00083936 | 0.0007776 | -0.029495 | 0.043066 | 0.0042531 | 0.0028562 | 0.013733 | 0 | 0.013733 | 0.086975 | 0.16479 | 0.032043 | -0.10986 | -0.036621 | 0.013733 | -0.1236 | 0.064087 | 0.059509 | 0.022888 | -0.059509 | 122.1405 | 121.9986 | 0.041199 | 122.1085 | 122.1954 | 0.19684 | -0.10986 | 122.1313 | 122.0489 | -0.059509 | 122.0718 | 121.9849 | -0.064087 | -0.064087 | 122.2733 | 122.1222 | 122.1222 | -0.23346 | 122.1725 | 122.168 | 122.1222 | -0.1831
2109.0156 | 122.3282 | -122.1222 | 0.12817 | -0.0085447 | 0.01583 | 0.00016669 | 0.0048257 | 0.05486 | 0.0041955 | -0.00055532 | -0.00083936 | 0.0020594 | -0.029281 | 0.041144 | 0.0080983 | 0.0062742 | 0.013733 | -0.009155 | 0 | 0.073242 | 0.16479 | 0.022888 | -0.11902 | -0.027466 | -0.018311 | -0.15106 | 0.050354 | 0.064087 | 0.022888 | -0.07782 | 122.1451 | 122.0032 | 0.036621 | 122.113 | 122.1954 | 0.19226 | -0.11444 | 122.1451 | 122.0444 | -0.07782 | 122.0947 | 121.9711 | -0.073242 | -0.064087 | 122.287 | 122.1359 | 122.1222 | -0.24719 | 122.1725 | 122.1863 | 122.1039 | -0.20599
2110.7656 | 122.319 | -122.1176 | 0.1236 | -0.0085447 | 0.014334 | 0.0035847 | 0.0099527 | 0.052938 | -0.0077673 | -0.0037597 | -0.00083936 | -0.0030676 | -0.029068 | 0.038367 | -1.9327e-05 | 0.0062742 | 0.09613 | 0.16479 | 0.17853 | 0.16479 | 0.1236 | 0.068665 | -0.059509 | 0.059509 | 0.19226 | 0.032043 | 0.027466 | 0.036621 | 0.059509 | -0.032043 | 122.1863 | 122.0581 | 0 | 122.2824 | 122.2824 | 0.2243 | -0.027466 | 122.1771 | 122.0856 | -0.09613 | 122.1771 | 122.1497 | 0.064086 | -0.086975 | 122.2412 | 122.2137 | 122.2961 | -0.1831 | 122.1451 | 122.1542 | 122.3099 | -0.15564
2112.4844 | 122.3282 | -122.1451 | 0.14191 | -0.00091566 | 0.011984 | 0.0044391 | 0.0050393 | 0.052724 | -0.0071265 | -0.0033325 | -0.00083936 | -0.0032812 | -0.030349 | 0.040503 | 0.0044667 | 0.0064878 | 0.041199 | 0.073242 | 0.09613 | 0.11902 | 0.14191 | 0.064087 | -0.064087 | 0.004578 | 0.086975 | -0.013733 | 0.027466 | 0.045776 | 0.064087 | -0.054932 | 122.2092 | 122.081 | 0 | 122.2183 | 122.2641 | 0.18311 | -0.10071 | 122.2092 | 122.0901 | -0.11444 | 122.1497 | 122.1313 | 0.041199 | -0.096131 | 122.287 | 122.1863 | 122.2412 | -0.20599 | 122.1725 | 122.1909 | 122.2321 | -0.19684
2114.25 | 122.2916 | -122.1588 | 0.12817 | -0.00091566 | 0.011984 | 0.0050799 | 0.0035441 | 0.056356 | -0.0034949 | -0.0056823 | -0.00083936 | -0.0007178 | -0.029922 | 0.040076 | 0.0046803 | 0.0067014 | 0.11444 | 0.13275 | 0.14191 | 0.15106 | 0.1236 | 0.050354 | -0.054932 | 0.050354 | 0.086975 | 0 | 0.032043 | 0.041199 | 0.054932 | -0.027466 | 122.2092 | 122.1039 | -0.004578 | 122.2916 | 122.3099 | 0.20599 | -0.013733 | 122.2137 | 122.1313 | -0.096131 | 122.2092 | 122.1588 | 0.027466 | -0.086975 | 122.2824 | 122.2733 | 122.3007 | -0.18311 | 122.1909 | 122.2 | 122.2458 | -0.15564
2116.0156 | 122.4014 | -122.1039 | 0.10071 | -0.016174 | 0.017538 | 0.0018757 | 0.0052531 | 0.057424 | 0.0033411 | -0.0035461 | -0.016098 | 0.0037684 | -0.028 | 0.043707 | 0.0061757 | 0.0020016 | 0.082397 | 0.059509 | 0.064087 | 0.13733 | 0.16479 | 0.022888 | -0.10071 | 0.045776 | 0.086975 | -0.086975 | 0.068665 | 0.054932 | 0.045776 | -0.045776 | 122.1268 | 122.0032 | 0.064087 | 122.1634 | 122.2412 | 0.23804 | -0.018311 | 122.1497 | 122.0581 | -0.032043 | 122.1497 | 122.0169 | -0.041199 | -0.045776 | 122.2687 | 122.1863 | 122.168 | -0.20142 | 122.1725 | 122.1588 | 122.1909 | -0.14648
2117.7188 | 122.2916 | -122.1497 | 0.13733 | -0.00091566 | 0.01113 | 0.0031573 | 0.0043985 | 0.054006 | -0.0058447 | -0.0044007 | -0.00083936 | -0.0037086 | -0.030777 | 0.038794 | 0.0023305 | 0.0064878 | 0.054932 | 0.11902 | 0.10071 | 0.11902 | 0.1236 | 0.064087 | -0.073242 | 0.013733 | 0.091553 | -0.032043 | 0.032043 | 0.045776 | 0.054932 | -0.013733 | 122.2137 | 122.0764 | -0.013733 | 122.2687 | 122.2687 | 0.19226 | -0.082397 | 122.2046 | 122.1359 | -0.10529 | 122.1634 | 122.1176 | -0.01831 | -0.091553 | 122.2733 | 122.2046 | 122.2504 | -0.21057 | 122.1817 | 122.1954 | 122.2412 | -0.15106
2119.4688 | 122.3373 | -122.168 | 0.11902 | -0.0085447 | 0.011343 | 0.00038029 | 0.0050393 | 0.052724 | -0.00093131 | -0.0039733 | -0.00083936 | -0.0024268 | -0.032272 | 0.040503 | 0.0042531 | 0.005206 | 0.1236 | 0.14191 | 0.15106 | 0.16022 | 0.10529 | 0.073242 | -0.054932 | 0.073242 | 0.12817 | 0.004578 | 0.018311 | 0.018311 | 0.054932 | -0.018311 | 122.2412 | 122.113 | -0.013733 | 122.3099 | 122.3282 | 0.21515 | 0.004577 | 122.2229 | 122.1497 | -0.10071 | 122.2412 | 122.1725 | 0.022889 | -0.10071 | 122.2733 | 122.2916 | 122.319 | -0.17395 | 122.1863 | 122.1863 | 122.2961 | -0.13733
2121.2188 | 122.4289 | -122.1268 | 0.1236 | -0.00091566 | 0.012839 | 0.0031573 | 0.0046121 | 0.053792 | -0.0017859 | -0.0033325 | -0.0084684 | 0.0003504 | -0.032913 | 0.039435 | 0.0078847 | 0.0039242 | 0.11902 | 0.10529 | 0.1236 | 0.16937 | 0.13733 | 0.064087 | -0.068665 | 0.086975 | 0.11444 | 0 | 0.013733 | 0.022888 | 0.064087 | -0.004578 | 122.1909 | 122.0581 | 0.013733 | 122.2321 | 122.2961 | 0.23804 | -0.004577 | 122.1909 | 122.1222 | -0.10986 | 122.2137 | 122.1268 | 0.004578 | -0.10071 | 122.2641 | 122.2458 | 122.2504 | -0.19226 | 122.1405 | 122.1497 | 122.2412 | -0.12817
2122.9219 | 122.4335 | -122.1405 | 0.09613 | -0.00091566 | 0.019888 | 0.0025165 | 0.0076029 | 0.055929 | 0.0016321 | -0.0048279 | -0.0084684 | 0.0037684 | -0.030349 | 0.04093 | 0.0055349 | 0.0054196 | 0.086975 | 0.064087 | 0.073242 | 0.11902 | 0.15106 | 0.036621 | -0.11902 | 0.036621 | 0.086975 | -0.073242 | 0.068665 | 0.041199 | 0.045776 | -0.054932 | 122.1771 | 122.0215 | 0.054932 | 122.2046 | 122.2595 | 0.23804 | -0.009155 | 122.1863 | 122.0856 | -0.027465 | 122.1771 | 122.0673 | -0.01831 | -0.054931 | 122.2916 | 122.2275 | 122.2137 | -0.21515 | 122.2092 | 122.1817 | 122.2275 | -0.15106
2124.6875 | 122.4014 | -122.1634 | 0.1236 | -0.0085447 | 0.016257 | 0.0031573 | 0.0039713 | 0.052724 | 0.0022729 | -0.0016235 | -0.00083936 | 0.0012048 | -0.030563 | 0.043494 | 0.0072437 | 0.0071286 | 0.027466 | 0.009155 | 0.027466 | 0.07782 | 0.15564 | 0.032043 | -0.10071 | -0.004578 | -0.004578 | -0.13275 | 0.068665 | 0.054932 | 0.013733 | -0.041199 | 122.1954 | 122.0627 | 0.032044 | 122.1725 | 122.2412 | 0.17853 | -0.09613 | 122.1771 | 122.1222 | -0.054931 | 122.1588 | 122.0306 | -0.091552 | -0.068664 | 122.319 | 122.1909 | 122.1909 | -0.2243 | 122.2321 | 122.2183 | 122.1588 | -0.16479
2126.4375 | 122.4564 | -122.113 | 0.082397 | 0.0067138 | 0.013907 | 0.0020893 | 0.0082437 | 0.05422 | -0.0019995 | -0.0048279 | 0.0067901 | -7.6996e-05 | -0.031631 | 0.042853 | 0.0036123 | 0.0056332 | 0.022888 | 0.009155 | 0.032043 | 0.10071 | 0.14648 | 0.036621 | -0.10986 | -0.004578 | 0.068665 | -0.086975 | 0.054932 | 0.07782 | 0.022888 | -0.054932 | 122.1497 | 122.0032 | 0.064087 | 122.1222 | 122.2137 | 0.21057 | -0.059509 | 122.1359 | 122.0581 | -0.027465 | 122.1085 | 122.0261 | -0.032043 | -0.004577 | 122.2595 | 122.1359 | 122.1451 | -0.19226 | 122.168 | 122.1909 | 122.1817 | -0.13733
2128.1406 | 122.319 | -122.1909 | 0.13275 | 0.014343 | 0.009848 | 0.0035847 | 0.0039713 | 0.05486 | -0.0058447 | -0.0033325 | -0.0084684 | -0.0037086 | -0.033767 | 0.039648 | 0.0031849 | 0.0081968 | 0.082397 | 0.1236 | 0.13275 | 0.15106 | 0.10986 | 0.082397 | -0.059509 | 0.036621 | 0.11444 | -0.004578 | 0.022888 | 0.050354 | 0.068665 | -0.009155 | 122.2733 | 122.1313 | -0.022888 | 122.3145 | 122.3419 | 0.21057 | -0.050354 | 122.2595 | 122.1817 | -0.10986 | 122.2275 | 122.1863 | 0.004577 | -0.082397 | 122.3007 | 122.2733 | 122.3236 | -0.19226 | 122.2137 | 122.2412 | 122.3053 | -0.14191
2129.8906 | 122.4106 | -122.1588 | 0.11444 | -0.00091566 | 0.014334 | 0.0044391 | 0.0039713 | 0.055074 | -0.0028539 | -0.0029053 | -0.0084684 | 0.0014184 | -0.030777 | 0.040289 | 0.0048939 | 0.0049924 | 0.009155 | 0.013733 | 0.013733 | 0.064087 | 0.16479 | 0.018311 | -0.1236 | -0.036621 | 0.032043 | -0.11444 | 0.073242 | 0.068665 | 0.013733 | -0.054932 | 122.1771 | 122.0352 | 0.050354 | 122.1725 | 122.2229 | 0.18768 | -0.10529 | 122.1725 | 122.1039 | -0.041199 | 122.1222 | 122.0444 | -0.059509 | -0.045776 | 122.3236 | 122.168 | 122.1725 | -0.23804 | 122.2321 | 122.2275 | 122.1909 | -0.16937
2131.5938 | 122.4106 | -122.168 | 0.086975 | -0.00091566 | 0.015616 | 0.0040119 | 0.0035441 | 0.056783 | 0.00077749 | -0.0014099 | 0.0067901 | 0.0018456 | -0.030349 | 0.042212 | 0.0074575 | 0.0062742 | 0.068665 | 0.059509 | 0.073242 | 0.12817 | 0.15106 | 0.036621 | -0.10071 | 0.018311 | 0.054932 | -0.086975 | 0.050354 | 0.059509 | 0.036621 | -0.050354 | 122.2046 | 122.0673 | 0.064087 | 122.2275 | 122.2961 | 0.22888 | -0.01831 | 122.2046 | 122.1176 | -0.036621 | 122.1863 | 122.081 | -0.036621 | -0.027466 | 122.319 | 122.2366 | 122.2412 | -0.18768 | 122.2183 | 122.2275 | 122.2229 | -0.13733
2133.3594 | 122.3831 | -122.1863 | 0.11902 | -0.00091566 | 0.010275 | -0.076097 | 0.0031167 | 0.053792 | -0.0077673 | -0.0056823 | -0.0084684 | -0.0026404 | -0.03569 | 0.039435 | 0.0012623 | 0.0084104 | 0.032043 | 0.09613 | 0.09613 | 0.14191 | 0.13275 | 0.054932 | -0.064087 | 0.013733 | 0.11902 | 0.013733 | 0.022888 | 0.041199 | 0.050354 | -0.013733 | 122.2412 | 122.1222 | 0.013732 | 122.2824 | 122.3282 | 0.20599 | -0.086976 | 122.2366 | 122.1725 | -0.096131 | 122.2 | 122.2 | 0.027466 | -0.07782 | 122.319 | 122.2183 | 122.2824 | -0.18311 | 122.2092 | 122.2275 | 122.3053 | -0.13275
2135.0625 | 122.4884 | -122.1634 | 0.10071 | -0.00091566 | 0.011771 | 0.0061481 | 0.0054667 | 0.055074 | -0.0019995 | -0.0035461 | -0.00083936 | -0.0002906 | -0.02864 | 0.039221 | 0.0070301 | 0.0032834 | 0.036621 | 0.027466 | 0.045776 | 0.09613 | 0.16937 | 0.050354 | -0.073242 | 0.036621 | 0.059509 | -0.050354 | 0.036621 | 0.036621 | 0.054932 | -0.032043 | 122.2137 | 122.0901 | 0.068665 | 122.1909 | 122.2595 | 0.16937 | -0.064087 | 122.2183 | 122.1313 | -0.064087 | 122.2 | 122.113 | -0.018311 | -0.064087 | 122.3328 | 122.2 | 122.2092 | -0.17395 | 122.2 | 122.2 | 122.2229 | -0.13275
2136.8281 | 122.374 | -122.1817 | 0.13733 | -0.0085447 | 0.013693 | 0.0059345 | 0.0088847 | 0.051229 | -0.0094763 | -0.0044007 | -0.00083936 | -0.0032812 | -0.031417 | 0.03858 | 0.0012623 | 0.006915 | 0.086975 | 0.16479 | 0.16479 | 0.16479 | 0.11444 | 0.064087 | -0.07782 | 0.064087 | 0.17853 | 0.032043 | 0.022888 | 0.032043 | 0.064087 | -0.041199 | 122.2458 | 122.1039 | -0.022888 | 122.3465 | 122.3465 | 0.24261 | -0.050354 | 122.2458 | 122.1405 | -0.11444 | 122.2458 | 122.2137 | 0.073242 | -0.10529 | 122.2961 | 122.2687 | 122.3465 | -0.21515 | 122.2046 | 122.2137 | 122.3602 | -0.17853
2138.5938 | 122.4747 | -122.1863 | 0.10529 | 0.0067138 | 0.016257 | 0.00080749 | 0.0061075 | 0.052724 | 0.0022729 | -0.0031189 | -0.00083936 | 0.0027002 | -0.03099 | 0.041998 | 0.0072437 | 0.0013608 | 0.073242 | 0.050354 | 0.059509 | 0.1236 | 0.16479 | 0.013733 | -0.10071 | 0.036621 | 0.07782 | -0.064087 | 0.045776 | 0.068665 | 0.032043 | -0.050354 | 122.2 | 122.0856 | 0.059509 | 122.2366 | 122.3099 | 0.2243 | -0.032044 | 122.2183 | 122.1359 | -0.05951 | 122.2229 | 122.1222 | -0.013733 | -0.036621 | 122.3511 | 122.2595 | 122.2458 | -0.20599 | 122.2321 | 122.2549 | 122.2641 | -0.15564
2140.3594 | 122.3831 | -122.2046 | 0.13275 | -0.0085447 | 0.0074982 | 0.0042255 | 0.0016215 | 0.053365 | -0.0075537 | -0.0054687 | -0.00083936 | -0.0026404 | -0.032913 | 0.040716 | 0.0021169 | 0.0064878 | 0.054932 | 0.064087 | 0.09613 | 0.1236 | 0.1236 | 0.054932 | -0.073242 | 0.009155 | 0.082397 | -0.022888 | 0.022888 | 0.036621 | 0.064087 | -0.004578 | 122.2595 | 122.1313 | -0.009155 | 122.2687 | 122.3282 | 0.19684 | -0.077819 | 122.2687 | 122.2 | -0.10986 | 122.2137 | 122.1817 | -0.01831 | -0.09613 | 122.3282 | 122.2595 | 122.3007 | -0.20599 | 122.2275 | 122.2412 | 122.287 | -0.13733
2142.0625 | 122.4106 | -122.2183 | 0.14648 | -0.00091566 | 0.010916 | 0.0035847 | 0.0067483 | 0.055929 | -0.0054175 | -0.0048279 | 0.0067901 | -0.001145 | -0.029495 | 0.042425 | 0.0023305 | 0.0062742 | 0.064087 | 0.054932 | 0.09613 | 0.12817 | 0.15106 | 0.059509 | -0.068665 | 0.036621 | 0.11444 | -0.018311 | 0.045776 | 0.041199 | 0.059509 | -0.022888 | 122.2778 | 122.1497 | 0.004578 | 122.2733 | 122.3465 | 0.19684 | -0.082397 | 122.2778 | 122.1954 | -0.10071 | 122.2549 | 122.2 | 0.004577 | -0.10529 | 122.3694 | 122.2824 | 122.3145 | -0.21515 | 122.2641 | 122.2595 | 122.3328 | -0.16937
2143.8125 | 122.4564 | -122.2046 | 0.11902 | -0.00091566 | 0.016043 | -0.0019695 | 0.0022623 | 0.053579 | 0.0022729 | -0.0029053 | -0.00083936 | 0.00505 | -0.030563 | 0.041998 | 0.0057485 | 0.0026426 | 0.091553 | 0.045776 | 0.036621 | 0.10529 | 0.13275 | 0.036621 | -0.10986 | -0.004578 | 0.027466 | -0.13275 | 0.064087 | 0.068665 | 0.027466 | -0.059509 | 122.2412 | 122.0947 | 0.013732 | 122.2504 | 122.3099 | 0.21515 | -0.027466 | 122.2321 | 122.1451 | -0.054932 | 122.2 | 122.0718 | -0.073242 | -0.050354 | 122.3373 | 122.2961 | 122.2412 | -0.22888 | 122.2687 | 122.2733 | 122.2321 | -0.17853
2145.5 | 122.5067 | -122.1863 | 0.082397 | 0.0067138 | 0.014121 | 0.00080749 | 0.0052531 | 0.055715 | -0.00093131 | -0.00076912 | 0.0067901 | 0.002273 | -0.032058 | 0.043921 | 0.0066029 | 0.0062742 | 0.054932 | -0.018311 | 0.004578 | 0.082397 | 0.15564 | 0.032043 | -0.10529 | 0.004578 | 0.018311 | -0.10071 | 0.045776 | 0.059509 | 0.027466 | -0.032043 | 122.2183 | 122.081 | 0.073243 | 122.168 | 122.2687 | 0.18768 | -0.027465 | 122.2137 | 122.1542 | -0.036621 | 122.1909 | 122.0856 | -0.068665 | -0.022888 | 122.3419 | 122.2412 | 122.1909 | -0.18768 | 122.2321 | 122.2458 | 122.2046 | -0.11444
2147.2031 | 122.3694 | -122.2549 | 0.13275 | -0.016174 | 0.011343 | 0.0033709 | 0.0052531 | 0.052938 | -0.0088355 | -0.0056823 | -0.00083936 | -0.0007178 | -0.032486 | 0.040289 | 0.00083507 | 0.0084104 | 0.068665 | 0.073242 | 0.10529 | 0.1236 | 0.13733 | 0.068665 | -0.054932 | 0.013733 | 0.07782 | -0.032043 | 0.032043 | 0.050354 | 0.068665 | -0.018311 | 122.3236 | 122.2 | 0.004578 | 122.3282 | 122.3785 | 0.17853 | -0.064086 | 122.3236 | 122.2366 | -0.10071 | 122.2687 | 122.2229 | -0.013732 | -0.082397 | 122.3923 | 122.3236 | 122.3602 | -0.18768 | 122.287 | 122.3053 | 122.3328 | -0.15106
2148.9688 | 122.4564 | -122.1954 | 0.10071 | 0.0067138 | 0.01882 | 0.0014483 | 0.0046121 | 0.054006 | 0.0022729 | -0.0035461 | -0.00083936 | 0.003341 | -0.031631 | 0.043707 | 0.0063893 | 0.0047788 | 0.09613 | 0.041199 | 0.054932 | 0.10986 | 0.15106 | 0.027466 | -0.09613 | 0.013733 | 0.022888 | -0.10986 | 0.064087 | 0.068665 | 0.022888 | -0.054932 | 122.2229 | 122.0993 | 0.050354 | 122.2366 | 122.3053 | 0.20599 | -0.004578 | 122.2183 | 122.1405 | -0.036621 | 122.2092 | 122.0856 | -0.054931 | -0.032043 | 122.3465 | 122.2916 | 122.2504 | -0.19684 | 122.2595 | 122.2641 | 122.2183 | -0.15564
2150.7188 | 122.4609 | -122.2366 | 0.10529 | 0.0067138 | 0.016043 | 0.00038029 | 0.0035441 | 0.055715 | -0.0024267 | -0.00076912 | -0.00083936 | 0.0012048 | -0.03099 | 0.04328 | 0.0070301 | 0.0071286 | 0.032043 | -0.018311 | 0.004578 | 0.07782 | 0.14648 | 0.041199 | -0.11902 | -0.032043 | -0.018311 | -0.14648 | 0.07782 | 0.082397 | 0.032043 | -0.059509 | 122.2778 | 122.1176 | 0.041198 | 122.2183 | 122.3145 | 0.19684 | -0.073243 | 122.2687 | 122.1771 | -0.027466 | 122.2046 | 122.0901 | -0.086975 | -0.022889 | 122.3831 | 122.2687 | 122.2412 | -0.22431 | 122.3145 | 122.319 | 122.2183 | -0.16479
2152.4219 | 122.4106 | -122.2504 | 0.11902 | -0.00091566 | 0.014121 | 0.0027301 | 0.0065347 | 0.054647 | -0.0045629 | -0.0029053 | -0.00083936 | 0.0001368 | -0.030563 | 0.04328 | 0.0016895 | 0.0077694 | 0.022888 | 0 | 0.022888 | 0.086975 | 0.15106 | 0.032043 | -0.10986 | -0.059509 | 0.050354 | -0.10071 | 0.073242 | 0.091553 | 0.009155 | -0.041199 | 122.2824 | 122.1405 | 0.032043 | 122.2504 | 122.3373 | 0.19684 | -0.096131 | 122.2595 | 122.2092 | -0.045777 | 122.1909 | 122.1497 | -0.059509 | -0.027466 | 122.4014 | 122.2733 | 122.2733 | -0.22888 | 122.3236 | 122.3419 | 122.3007 | -0.16022
2154.1719 | 122.4747 | -122.2549 | 0.10986 | -0.00091566 | 0.017325 | 0.0031573 | 0.0061075 | 0.052083 | 0.00035029 | -0.0024779 | 0.0067901 | 0.0003504 | -0.029068 | 0.043707 | 0.0072437 | 0.0039242 | 0 | -0.041199 | 0 | 0.064087 | 0.16937 | 0.022888 | -0.10071 | -0.041199 | -0.027466 | -0.15106 | 0.059509 | 0.059509 | 0.018311 | -0.045776 | 122.2778 | 122.1542 | 0.05951 | 122.2137 | 122.319 | 0.1648 | -0.10986 | 122.2733 | 122.2092 | -0.050354 | 122.2137 | 122.1039 | -0.10529 | -0.050354 | 122.4243 | 122.2549 | 122.2549 | -0.21057 | 122.3145 | 122.3145 | 122.2275 | -0.15564
2155.875 | 122.5159 | -122.2046 | 0.091553 | 0.0067138 | 0.011771 | 0.00059389 | 0.0029031 | 0.05486 | -0.0032813 | -0.0037597 | 0.0067901 | -0.0009314 | -0.029922 | 0.039648 | 0.0048939 | 0.006915 | 0.09613 | 0.09613 | 0.11444 | 0.17395 | 0.11902 | 0.064087 | -0.068665 | 0.07782 | 0.11902 | 0 | 0.013733 | 0.018311 | 0.064087 | -0.018311 | 122.2687 | 122.1359 | 0.027466 | 122.3007 | 122.3785 | 0.24261 | 0.004577 | 122.2687 | 122.1863 | -0.07782 | 122.2824 | 122.2046 | 0.018311 | -0.073242 | 122.3236 | 122.3007 | 122.319 | -0.16022 | 122.2183 | 122.2229 | 122.3236 | -0.10986
2157.6406 | 122.4609 | -122.2549 | 0.13733 | 0.0067138 | 0.01113 | 0.0065753 | 0.0056803 | 0.053579 | -0.0077673 | -0.0056823 | -0.0084684 | -0.0026404 | -0.031845 | 0.040076 | 0.0021169 | 0.0071286 | 0.11444 | 0.14648 | 0.15564 | 0.16022 | 0.10071 | 0.064087 | -0.073242 | 0.082397 | 0.17853 | 0.059509 | 0.009155 | 0.050354 | 0.059509 | -0.022888 | 122.319 | 122.1817 | -0.036621 | 122.4014 | 122.4152 | 0.23346 | -0.022888 | 122.3145 | 122.2321 | -0.12817 | 122.3373 | 122.3145 | 0.082397 | -0.086975 | 122.3557 | 122.3694 | 122.4106 | -0.21057 | 122.2641 | 122.3053 | 122.4335 | -0.16022
2159.4062 | 122.525 | -122.2 | 0.10986 | -0.00091566 | 0.017111 | 0.0044391 | 0.0026895 | 0.055501 | -0.0022131 | -0.0031189 | -0.00083936 | -0.0013586 | -0.032058 | 0.038153 | 0.0076711 | 0.0049924 | 0.11902 | 0.11444 | 0.11444 | 0.17853 | 0.12817 | 0.086975 | -0.054932 | 0.07782 | 0.14191 | 0 | 0.022888 | 0.027466 | 0.064087 | -0.013733 | 122.287 | 122.1451 | 0.018311 | 122.3145 | 122.3785 | 0.23346 | 0.009156 | 122.2641 | 122.1863 | -0.086975 | 122.2778 | 122.2 | 0.013733 | -0.082397 | 122.3282 | 122.319 | 122.3145 | -0.16479 | 122.2229 | 122.2275 | 122.3419 | -0.1236
2161.0938 | 122.4106 | -122.2641 | 0.13275 | -0.00091566 | 0.013266 | 0.0059345 | 0.0050393 | 0.054006 | -0.0090491 | -0.0054687 | -0.0084684 | -0.0013586 | -0.033126 | 0.041144 | 0.0048939 | 0.0062742 | 0.064087 | 0.068665 | 0.10986 | 0.1236 | 0.11902 | 0.068665 | -0.086975 | 0.022888 | 0.082397 | -0.041199 | 0.041199 | 0.027466 | 0.068665 | -0.022888 | 122.3328 | 122.1771 | -0.013732 | 122.3328 | 122.3877 | 0.21057 | -0.068664 | 122.3328 | 122.2412 | -0.091552 | 122.287 | 122.2229 | -0.018311 | -0.10529 | 122.3831 | 122.3282 | 122.374 | -0.21973 | 122.3053 | 122.2916 | 122.3465 | -0.15564
2162.8438 | 122.5342 | -122.2366 | 0.10529 | -0.0085447 | 0.014761 | 0.0037983 | 0.0035441 | 0.05187 | 0.00013669 | -0.0033325 | 0.0067901 | 0.0018456 | -0.031845 | 0.042212 | 0.0078847 | 0.0067014 | 0.018311 | -0.032043 | -0.004578 | 0.064087 | 0.17395 | 0.022888 | -0.09613 | -0.032043 | -0.018311 | -0.13275 | 0.064087 | 0.073242 | 0.027466 | -0.059509 | 122.2595 | 122.1405 | 0.068664 | 122.2046 | 122.3007 | 0.16022 | -0.086975 | 122.2641 | 122.1771 | -0.041199 | 122.2046 | 122.1039 | -0.073242 | -0.032044 | 122.4106 | 122.2549 | 122.2321 | -0.20142 | 122.3007 | 122.3099 | 122.2183 | -0.16479
2164.6094 | 122.3923 | -122.2961 | 0.14191 | 0.0067138 | 0.014548 | 0.0067889 | 0.0082437 | 0.055074 | -0.0066993 | -0.0065369 | -0.0084684 | -0.0026404 | -0.030136 | 0.038367 | 0.0029713 | 0.006915 | 0.09613 | 0.12817 | 0.14648 | 0.1831 | 0.13733 | 0.050354 | -0.07782 | 0.041199 | 0.13733 | -0.009155 | 0.041199 | 0.036621 | 0.064087 | -0.036621 | 122.3465 | 122.2183 | -0.004578 | 122.4243 | 122.4792 | 0.26092 | -0.045777 | 122.3602 | 122.2595 | -0.10071 | 122.3373 | 122.287 | 0.027466 | -0.10529 | 122.4335 | 122.3923 | 122.4426 | -0.21973 | 122.3373 | 122.3328 | 122.4335 | -0.17853
2166.3594 | 122.5342 | -122.2275 | 0.091553 | -0.00091566 | 0.01583 | 0.0020893 | 0.0050393 | 0.055288 | 0.0016321 | -0.0026917 | -0.00083936 | 0.0031274 | -0.029068 | 0.041785 | 0.0072437 | 0.0026426 | 0.082397 | 0.054932 | 0.059509 | 0.13275 | 0.16022 | 0.041199 | -0.10071 | 0.032043 | 0.082397 | -0.082397 | 0.059509 | 0.064087 | 0.032043 | -0.050354 | 122.2687 | 122.1268 | 0.068664 | 122.2824 | 122.3602 | 0.23346 | -0.009156 | 122.2595 | 122.1771 | -0.032044 | 122.2595 | 122.1451 | -0.032043 | -0.027466 | 122.3877 | 122.3099 | 122.287 | -0.19226 | 122.287 | 122.2916 | 122.3099 | -0.14191
2168.125 | 122.5433 | -122.2458 | 0.10071 | -0.00091566 | 0.013266 | 0.0046527 | 0.0020487 | 0.054433 | -0.0011451 | -0.0014099 | -0.0084684 | -0.0017858 | -0.031845 | 0.041998 | 0.0066029 | 0.0071286 | 0.1236 | 0.11444 | 0.14191 | 0.15106 | 0.11902 | 0.068665 | -0.036621 | 0.086975 | 0.12817 | -0.004578 | 0.004578 | 0.041199 | 0.064087 | -0.032043 | 122.3145 | 122.2092 | 0.018311 | 122.3602 | 122.3969 | 0.18768 | 0.022888 | 122.3099 | 122.2137 | -0.09613 | 122.3328 | 122.2412 | 0.027465 | -0.059509 | 122.3648 | 122.3694 | 122.3877 | -0.13733 | 122.2504 | 122.287 | 122.374 | -0.13275
2169.875 | 122.5204 | -122.2549 | 0.10986 | -0.0085447 | 0.014334 | 0.0033709 | 0.0035441 | 0.052511 | -0.0024267 | -0.0035461 | -0.0084684 | 0.000564 | -0.03099 | 0.041144 | 0.0036123 | 0.0064878 | 0.11902 | 0.12817 | 0.14191 | 0.16022 | 0.1236 | 0.059509 | -0.068665 | 0.07782 | 0.12817 | 0.022888 | 0.009155 | 0.036621 | 0.064087 | -0.018311 | 122.3145 | 122.1863 | 0.013733 | 122.3831 | 122.4152 | 0.22888 | 0.009156 | 122.319 | 122.2366 | -0.10071 | 122.3328 | 122.2778 | 0.041199 | -0.073242 | 122.3785 | 122.374 | 122.3969 | -0.17853 | 122.2641 | 122.2916 | 122.3831 | -0.12817
2171.5625 | 122.4243 | -122.2961 | 0.13275 | 0.0067138 | 0.01647 | 0.0059345 | 0.0090983 | 0.053792 | -0.0032813 | -0.0054687 | 0.0067901 | 0.0012048 | -0.03099 | 0.039648 | 0.0014759 | 0.0060604 | 0.018311 | 0.018311 | 0.032043 | 0.073242 | 0.16479 | 0.018311 | -0.10986 | -0.059509 | 0.027466 | -0.10986 | 0.068665 | 0.086975 | 0.009155 | -0.07782 | 122.3145 | 122.1863 | 0.032044 | 122.3145 | 122.3694 | 0.18311 | -0.11444 | 122.3053 | 122.2183 | -0.064086 | 122.2366 | 122.1863 | -0.032043 | -0.045776 | 122.4609 | 122.3145 | 122.3282 | -0.24261 | 122.3648 | 122.3831 | 122.3236 | -0.21057
2173.3281 | 122.4518 | -122.2824 | 0.12817 | -0.00091566 | 0.016684 | 0.0033709 | 0.0061075 | 0.051443 | -0.0062719 | -0.0050415 | -0.0084684 | -0.0039222 | -0.030563 | 0.03858 | 0.0038259 | 0.0071286 | 0.10071 | 0.15564 | 0.16479 | 0.17853 | 0.11902 | 0.054932 | -0.059509 | 0.073242 | 0.17395 | 0.027466 | 0.027466 | 0.032043 | 0.064087 | -0.018311 | 122.3373 | 122.2229 | -0.009155 | 122.4381 | 122.4609 | 0.23804 | -0.027466 | 122.3465 | 122.2641 | -0.10071 | 122.3557 | 122.3099 | 0.045777 | -0.096131 | 122.4014 | 122.3831 | 122.4472 | -0.18768 | 122.3099 | 122.3145 | 122.4564 | -0.14649
2175.0781 | 122.438 | -122.319 | 0.13275 | -0.00091566 | 0.011557 | 0.0063617 | 0.0043985 | 0.050802 | -0.0043493 | -0.0054687 | -0.00083936 | -0.004563 | -0.032913 | 0.039435 | 0.0051075 | 0.0073422 | 0.068665 | 0.091553 | 0.10071 | 0.13733 | 0.1236 | 0.068665 | -0.068665 | 0.013733 | 0.073242 | -0.027466 | 0.013733 | 0.045776 | 0.050354 | -0.022888 | 122.3877 | 122.2504 | -0.009155 | 122.4106 | 122.4564 | 0.20599 | -0.064086 | 122.3694 | 122.2961 | -0.11902 | 122.3328 | 122.2916 | -0.004578 | -0.086975 | 122.4426 | 122.3877 | 122.4197 | -0.20142 | 122.3328 | 122.3648 | 122.3923 | -0.15564
2176.8281 | 122.5708 | -122.2641 | 0.10071 | -0.0085447 | 0.016898 | 0.0040119 | 0.0029031 | 0.055501 | 0.0031275 | -0.0031189 | -0.00083936 | 0.0048364 | -0.03099 | 0.042639 | 0.0074575 | 0.0026426 | 0.082397 | 0.073242 | 0.064087 | 0.13275 | 0.16479 | 0.032043 | -0.11444 | 0.036621 | 0.068665 | -0.073242 | 0.041199 | 0.059509 | 0.032043 | -0.068665 | 122.2961 | 122.1497 | 0.064087 | 122.3373 | 122.3969 | 0.24719 | -0.018311 | 122.2961 | 122.1954 | -0.059509 | 122.3007 | 122.1909 | -0.004577 | -0.041199 | 122.4289 | 122.3465 | 122.3282 | -0.21515 | 122.3053 | 122.3236 | 122.3328 | -0.16937
2178.5312 | 122.5342 | -122.2366 | 0.10529 | -0.0085447 | 0.015616 | 0.0035847 | 0.0061075 | 0.052297 | -0.00071771 | -0.0020507 | -0.00083936 | 0.0012048 | -0.029281 | 0.04328 | 0.0048939 | 0.0054196 | 0.018311 | -0.013733 | 0.018311 | 0.086975 | 0.16022 | 0.022888 | -0.10529 | -0.018311 | 0.041199 | -0.10986 | 0.068665 | 0.07782 | 0.018311 | -0.064087 | 122.2595 | 122.1313 | 0.054931 | 122.2229 | 122.3236 | 0.19226 | -0.086975 | 122.2549 | 122.1725 | -0.036621 | 122.2183 | 122.1268 | -0.045776 | -0.027466 | 122.3969 | 122.2549 | 122.2549 | -0.21057 | 122.3053 | 122.3145 | 122.2778 | -0.16937
2180.2969 | 122.5479 | -122.2687 | 0.09613 | -0.0085447 | 0.01583 | 0.0029437 | 0.0069621 | 0.054647 | -0.00093131 | -0.0037597 | -0.0084684 | 0.0003504 | -0.028 | 0.04093 | 0.0025441 | 0.0062742 | 0.022888 | 0.009155 | 0.013733 | 0.09613 | 0.17853 | 0.036621 | -0.09613 | -0.022888 | 0.027466 | -0.10986 | 0.059509 | 0.07782 | 0.027466 | -0.045776 | 122.3053 | 122.1725 | 0.082398 | 122.2778 | 122.3648 | 0.19226 | -0.073242 | 122.2961 | 122.2229 | -0.036621 | 122.2458 | 122.1588 | -0.064087 | -0.01831 | 122.4472 | 122.2916 | 122.2824 | -0.19226 | 122.3282 | 122.3465 | 122.2961 | -0.14191
2182 | 122.4518 | -122.2961 | 0.11902 | -0.0085447 | 0.015402 | 0.0063617 | 0.0071757 | 0.054647 | -0.0060583 | -0.0048279 | -0.0084684 | -0.002854 | -0.030349 | 0.038367 | 0.0033985 | 0.0054196 | 0.10986 | 0.15564 | 0.16479 | 0.16022 | 0.13733 | 0.064087 | -0.073242 | 0.082397 | 0.20142 | 0.041199 | 0.022888 | 0.041199 | 0.054932 | -0.022888 | 122.3602 | 122.2229 | 0.01831 | 122.4518 | 122.4564 | 0.23346 | -0.009156 | 122.3511 | 122.2733 | -0.096131 | 122.3785 | 122.3373 | 0.064087 | -0.07782 | 122.4335 | 122.406 | 122.4609 | -0.19226 | 122.319 | 122.3373 | 122.4976 | -0.14191
2183.7656 | 122.4792 | -122.2961 | 0.1236 | -0.00091566 | 0.012625 | 0.0046527 | 0.0058939 | 0.054647 | -0.0030677 | -0.0041869 | -0.00083936 | 0.001632 | -0.029495 | 0.041144 | 0.0040395 | 0.0060604 | 0.027466 | 0 | 0.013733 | 0.07782 | 0.16937 | 0.013733 | -0.10071 | -0.045776 | 0.022888 | -0.1236 | 0.07782 | 0.054932 | 0.018311 | -0.068665 | 122.3099 | 122.1954 | 0.045777 | 122.2961 | 122.374 | 0.17853 | -0.09613 | 122.3145 | 122.2275 | -0.045776 | 122.2504 | 122.1725 | -0.054931 | -0.068664 | 122.4655 | 122.3236 | 122.3099 | -0.2243 | 122.374 | 122.3511 | 122.319 | -0.19226
2185.5312 | 122.4472 | -122.3282 | 0.13733 | -0.00091566 | 0.013266 | 0.0035847 | 0.0071757 | 0.053152 | -0.0041357 | -0.0016235 | 0.0067901 | 0.000564 | -0.028 | 0.040503 | 0.0031849 | 0.006915 | 0.073242 | 0.1236 | 0.12817 | 0.14648 | 0.13733 | 0.041199 | -0.068665 | 0.009155 | 0.086975 | -0.068665 | 0.054932 | 0.050354 | 0.032043 | -0.073242 | 122.3694 | 122.2595 | 0 | 122.4518 | 122.4747 | 0.21515 | -0.064087 | 122.3602 | 122.2549 | -0.082397 | 122.3373 | 122.2595 | 0.004577 | -0.086975 | 122.4655 | 122.4014 | 122.4564 | -0.20599 | 122.3831 | 122.3785 | 122.4152 | -0.21057
2187.2812 | 122.5159 | -122.3236 | 0.11902 | -0.00091566 | 0.009848 | 0.0070025 | 0.0073893 | 0.053152 | -0.0077673 | -0.0041869 | -0.00083936 | -0.0022132 | -0.03099 | 0.038794 | 0.0031849 | 0.007983 | 0.09613 | 0.15106 | 0.14191 | 0.16937 | 0.12817 | 0.068665 | -0.050354 | 0.07782 | 0.15564 | 0.036621 | 0.018311 | 0.027466 | 0.054932 | -0.018311 | 122.3923 | 122.2733 | 0.009155 | 122.4747 | 122.493 | 0.21973 | -0.022889 | 122.3785 | 122.3053 | -0.10071 | 122.4014 | 122.3602 | 0.054932 | -0.091553 | 122.4518 | 122.4197 | 122.4655 | -0.16937 | 122.3419 | 122.3511 | 122.4792 | -0.13733
2189.0469 | 122.5204 | -122.3099 | 0.10986 | -0.00091566 | 0.011557 | 0.0057209 | 0.0041849 | 0.05422 | -0.0060583 | -0.0058959 | 0.0067901 | -0.0019996 | -0.030563 | 0.038794 | 0.0033985 | 0.0077694 | 0.082397 | 0.10986 | 0.14191 | 0.16022 | 0.1236 | 0.068665 | -0.082397 | 0.064087 | 0.15564 | 0.032043 | 0.013733 | 0.036621 | 0.036621 | 0 | 122.3785 | 122.2275 | 0.013733 | 122.4197 | 122.4701 | 0.24261 | -0.027466 | 122.3465 | 122.3099 | -0.09613 | 122.374 | 122.3419 | 0.032043 | -0.073242 | 122.4335 | 122.3923 | 122.4518 | -0.19226 | 122.3236 | 122.3465 | 122.4655 | -0.10986
2190.8125 | 122.4564 | -122.3145 | 0.13733 | -0.00091566 | 0.013907 | 0.0027301 | 0.0029031 | 0.054433 | -0.0030677 | -0.0039733 | -0.0084684 | 0.0020594 | -0.03334 | 0.041357 | 0.0070301 | 0.005206 | 0.086975 | 0.13275 | 0.11444 | 0.16022 | 0.13733 | 0.059509 | -0.082397 | 0.018311 | 0.091553 | -0.054932 | 0.041199 | 0.050354 | 0.036621 | -0.054932 | 122.374 | 122.2321 | 0 | 122.4472 | 122.4747 | 0.24261 | -0.050354 | 122.3511 | 122.2595 | -0.09613 | 122.3328 | 122.2595 | 0 | -0.086975 | 122.4518 | 122.4014 | 122.4289 | -0.21973 | 122.3557 | 122.3648 | 122.406 | -0.19226
2192.5312 | 122.5433 | -122.3099 | 0.10529 | 0.0067138 | 0.014975 | 0.0020893 | 0.0041849 | 0.054006 | -7.6908e-05 | -0.0058959 | -0.016098 | 0.002273 | -0.032058 | 0.040289 | 0.0078847 | 0.0041378 | 0.045776 | 0.009155 | 0.004578 | 0.07782 | 0.16479 | 0.018311 | -0.11444 | -0.036621 | 0.018311 | -0.1236 | 0.059509 | 0.059509 | 0.022888 | -0.059509 | 122.3282 | 122.1954 | 0.059509 | 122.319 | 122.3877 | 0.19226 | -0.05951 | 122.3328 | 122.2504 | -0.045777 | 122.2733 | 122.1863 | -0.064087 | -0.045777 | 122.4747 | 122.3557 | 122.3145 | -0.21973 | 122.3694 | 122.3694 | 122.3282 | -0.16479
2194.2969 | 122.4884 | -122.319 | 0.11444 | -0.0085447 | 0.013266 | 0.0076435 | 0.0043985 | 0.056356 | -0.0045629 | -0.0029053 | -0.0084684 | -0.0019996 | -0.032486 | 0.039648 | 0.0042531 | 0.0054196 | 0.12817 | 0.15564 | 0.15564 | 0.16937 | 0.14191 | 0.050354 | -0.068665 | 0.07782 | 0.17395 | 0.027466 | 0.036621 | 0.022888 | 0.073242 | -0.032043 | 122.3694 | 122.2504 | 0.027466 | 122.4747 | 122.4884 | 0.23804 | 0.013733 | 122.3923 | 122.287 | -0.07782 | 122.3969 | 122.3465 | 0.059509 | -0.091553 | 122.4609 | 122.4472 | 122.4747 | -0.18311 | 122.3557 | 122.3419 | 122.493 | -0.14648
2196.0625 | 122.5433 | -122.3328 | 0.091553 | 0.0067138 | 0.015616 | 0.0023029 | 0.0048257 | 0.054006 | 0.0020593 | -0.0011963 | -0.0084684 | 0.0024866 | -0.029922 | 0.042639 | 0.0076711 | 0.0056332 | 0.045776 | -0.022888 | 0.009155 | 0.086975 | 0.15564 | 0.041199 | -0.09613 | -0.018311 | -0.009155 | -0.16479 | 0.064087 | 0.068665 | 0.027466 | -0.068665 | 122.374 | 122.2366 | 0.064087 | 122.3099 | 122.4197 | 0.1831 | -0.045777 | 122.3602 | 122.2641 | -0.027466 | 122.3145 | 122.168 | -0.09613 | -0.022888 | 122.4884 | 122.3785 | 122.3419 | -0.18768 | 122.3969 | 122.4014 | 122.3236 | -0.16022
2197.75 | 122.5571 | -122.3328 | 0.10071 | -0.0085447 | 0.013052 | 0.0042255 | 0.0048257 | 0.05187 | -0.0028539 | -0.0024779 | -0.0084684 | 0.0001368 | -0.031845 | 0.04093 | 0.0031849 | 0.0062742 | 0.1236 | 0.12817 | 0.15106 | 0.16479 | 0.09613 | 0.059509 | -0.059509 | 0.10529 | 0.14191 | 0.032043 | 0.018311 | 0.041199 | 0.07782 | -0.018311 | 122.3923 | 122.2733 | -0.004578 | 122.4609 | 122.4976 | 0.2243 | 0.022888 | 122.4106 | 122.3145 | -0.082397 | 122.4381 | 122.3648 | 0.050354 | -0.059509 | 122.4289 | 122.4564 | 122.4838 | -0.16022 | 122.3511 | 122.374 | 122.4747 | -0.11902
2199.5 | 122.5479 | -122.3465 | 0.1236 | -0.0085447 | 0.010916 | 0.0025165 | 0.0054667 | 0.051443 | -0.0034949 | -0.0035461 | 0.0067901 | -0.0017858 | -0.032913 | 0.04093 | 0.0033985 | 0.0075558 | 0.12817 | 0.13733 | 0.14191 | 0.17853 | 0.11444 | 0.068665 | -0.064087 | 0.086975 | 0.14191 | 0.009155 | 0 | 0.027466 | 0.064087 | -0.013733 | 122.4152 | 122.2824 | -0.009155 | 122.4838 | 122.525 | 0.24261 | 0.004578 | 122.4106 | 122.3328 | -0.1236 | 122.4335 | 122.3557 | 0.022888 | -0.09613 | 122.4609 | 122.4747 | 122.4884 | -0.18768 | 122.3465 | 122.374 | 122.4884 | -0.13733
2201.25 | 122.612 | -122.3053 | 0.09613 | 0.014343 | 0.016684 | 0.0025165 | 0.0046121 | 0.05422 | 0.00035029 | -0.0022643 | -0.00083936 | 0.003982 | -0.032699 | 0.041785 | 0.0089527 | 0.0054196 | 0.091553 | 0.054932 | 0.041199 | 0.13275 | 0.16022 | 0.022888 | -0.091553 | 0.036621 | 0.07782 | -0.073242 | 0.045776 | 0.059509 | 0.050354 | -0.045776 | 122.3282 | 122.2137 | 0.064087 | 122.3602 | 122.438 | 0.2243 | -0.004577 | 122.3557 | 122.2595 | -0.050354 | 122.3419 | 122.2321 | -0.027466 | -0.036621 | 122.4655 | 122.3969 | 122.3465 | -0.18768 | 122.3511 | 122.3648 | 122.3831 | -0.14191
2202.9531 | 122.493 | -122.3465 | 0.1236 | -0.016174 | 0.01583 | 0.0035847 | 0.0078165 | 0.053365 | -0.0037085 | -0.0035461 | -0.00083936 | -0.001145 | -0.029281 | 0.039648 | 0.0040395 | 0.0060604 | 0.018311 | 0.032043 | 0.036621 | 0.10071 | 0.15564 | 0.032043 | -0.086975 | -0.050354 | 0.041199 | -0.091553 | 0.064087 | 0.091553 | 0.027466 | -0.073242 | 122.3785 | 122.2595 | 0.032044 | 122.3785 | 122.4472 | 0.18768 | -0.10528 | 122.374 | 122.2733 | -0.059509 | 122.2961 | 122.2549 | -0.018311 | -0.032043 | 122.5021 | 122.3648 | 122.3831 | -0.21057 | 122.4106 | 122.4381 | 122.3877 | -0.19684
2204.7031 | 122.5021 | -122.3557 | 0.12817 | -0.0085447 | 0.01583 | 0.0048663 | 0.0071757 | 0.055929 | -0.0054175 | -0.0048279 | -0.0084684 | -0.002854 | -0.031845 | 0.039435 | 0.0029713 | 0.0054196 | 0.10071 | 0.16937 | 0.16022 | 0.17853 | 0.11902 | 0.07782 | -0.068665 | 0.064087 | 0.19226 | 0.009155 | 0.022888 | 0.022888 | 0.07782 | -0.022888 | 122.4335 | 122.287 | -0.009155 | 122.525 | 122.5342 | 0.24719 | -0.027466 | 122.4335 | 122.3328 | -0.10529 | 122.4197 | 122.3648 | 0.032043 | -0.10529 | 122.4747 | 122.4564 | 122.5159 | -0.19684 | 122.3785 | 122.3785 | 122.5479 | -0.15106
2206.4531 | 122.5388 | -122.3419 | 0.10986 | -0.016174 | 0.0085664 | 0.0067889 | 0.0035441 | 0.052938 | -0.0079809 | -0.0050415 | -0.0084684 | -0.0039222 | -0.03334 | 0.04093 | 0.0048939 | 0.0071286 | 0.11444 | 0.14648 | 0.13733 | 0.1831 | 0.11902 | 0.064087 | -0.068665 | 0.07782 | 0.16479 | 0.045776 | 0.018311 | 0.032043 | 0.07782 | -0.032043 | 122.406 | 122.2733 | 0.009156 | 122.4884 | 122.525 | 0.25177 | 0.004578 | 122.4197 | 122.3099 | -0.091552 | 122.4197 | 122.3877 | 0.077819 | -0.07782 | 122.4609 | 122.4564 | 122.4792 | -0.17853 | 122.3602 | 122.374 | 122.5067 | -0.14191
2208.2031 | 122.5525 | -122.3602 | 0.10529 | -0.0085447 | 0.011557 | 0.0063617 | 0.0067483 | 0.053579 | -0.0069129 | -0.0044007 | -0.0084684 | -0.0007178 | -0.030349 | 0.039007 | -0.00044673 | 0.005206 | 0.13275 | 0.13275 | 0.14191 | 0.16479 | 0.12817 | 0.045776 | -0.064087 | 0.07782 | 0.17395 | 0.054932 | 0.032043 | 0.022888 | 0.050354 | -0.027466 | 122.406 | 122.2961 | 0.022888 | 122.493 | 122.525 | 0.22888 | 0.027465 | 122.4106 | 122.3328 | -0.073243 | 122.438 | 122.4152 | 0.082398 | -0.082398 | 122.4884 | 122.493 | 122.5021 | -0.16937 | 122.3923 | 122.3831 | 122.5342 | -0.13275
2209.9531 | 122.5479 | -122.3511 | 0.1236 | -0.00091566 | 0.012412 | 0.0052935 | 0.0050393 | 0.052511 | -0.0041357 | -0.0048279 | -0.00083936 | -7.6996e-05 | -0.032486 | 0.040503 | 0.0021169 | 0.0047788 | 0.10529 | 0.11444 | 0.13733 | 0.16479 | 0.14191 | 0.054932 | -0.054932 | 0.059509 | 0.16479 | 0.045776 | 0.027466 | 0.027466 | 0.036621 | -0.013733 | 122.406 | 122.2961 | 0.018311 | 122.4655 | 122.5159 | 0.21973 | -0.01831 | 122.3877 | 122.3373 | -0.09613 | 122.4106 | 122.3969 | 0.059509 | -0.09613 | 122.493 | 122.4564 | 122.4884 | -0.17853 | 122.3785 | 122.3785 | 122.5159 | -0.13733
2211.6562 | 122.6257 | -122.3145 | 0.10071 | -0.00091566 | 0.013693 | 0.0023029 | 0.0058939 | 0.053579 | 0.00056389 | -0.0063233 | -0.00083936 | 0.0031274 | -0.030136 | 0.041785 | 0.0083119 | 0.0026426 | 0.041199 | 0.018311 | 0.018311 | 0.091553 | 0.16022 | 0.018311 | -0.1236 | 0 | 0.032043 | -0.10529 | 0.068665 | 0.059509 | 0.018311 | -0.050354 | 122.3328 | 122.1909 | 0.059509 | 122.3328 | 122.406 | 0.21515 | -0.059509 | 122.3328 | 122.2641 | -0.032043 | 122.3145 | 122.2092 | -0.054932 | -0.041199 | 122.4747 | 122.3557 | 122.3328 | -0.2243 | 122.3831 | 122.374 | 122.3465 | -0.15106
2213.4219 | 122.5891 | -122.3511 | 0.10529 | 0.0067138 | 0.019675 | -0.0011151 | 0.0065347 | 0.056356 | 0.0037683 | -0.0026917 | -0.0084684 | 0.0029138 | -0.029281 | 0.043066 | 0.0070301 | 0.0032834 | 0.059509 | 0.018311 | 0.027466 | 0.09613 | 0.14191 | 0.018311 | -0.091553 | -0.018311 | 0 | -0.12817 | 0.064087 | 0.059509 | 0.013733 | -0.054932 | 122.3694 | 122.2595 | 0.036621 | 122.3694 | 122.4472 | 0.18768 | -0.045777 | 122.3648 | 122.2961 | -0.041199 | 122.3328 | 122.2229 | -0.073242 | -0.045777 | 122.493 | 122.4106 | 122.3785 | -0.19684 | 122.4152 | 122.4106 | 122.3511 | -0.16022
2215.1875 | 122.5204 | -122.374 | 0.11902 | -0.0085447 | 0.013907 | 0.0035847 | 0.0086709 | 0.05187 | -0.0060583 | -0.0039733 | -0.00083936 | -0.0024268 | -0.031417 | 0.037085 | 0.0029713 | 0.0073422 | 0.09613 | 0.1831 | 0.18768 | 0.19226 | 0.10529 | 0.059509 | -0.068665 | 0.07782 | 0.1831 | 0.032043 | 0.022888 | 0.036621 | 0.041199 | -0.018311 | 122.4335 | 122.3053 | -0.013733 | 122.5571 | 122.5662 | 0.26093 | -0.022889 | 122.4152 | 122.3557 | -0.096131 | 122.4518 | 122.406 | 0.050354 | -0.082398 | 122.4792 | 122.4701 | 122.5616 | -0.18768 | 122.3969 | 122.4106 | 122.5571 | -0.13733
2216.9531 | 122.58 | -122.374 | 0.1236 | -0.00091566 | 0.013266 | 0.0029437 | 0.0065347 | 0.05486 | -0.0062719 | -0.0054687 | -0.00083936 | -0.0015722 | -0.028854 | 0.040076 | 0.00040787 | 0.0064878 | 0.073242 | 0.1236 | 0.12817 | 0.14191 | 0.14648 | 0.068665 | -0.07782 | 0.068665 | 0.16022 | 0.022888 | 0.036621 | 0.041199 | 0.045776 | -0.032043 | 122.4426 | 122.2961 | 0.022888 | 122.4976 | 122.5159 | 0.21973 | -0.050354 | 122.4197 | 122.3419 | -0.086975 | 122.4426 | 122.3969 | 0.054931 | -0.082397 | 122.5204 | 122.4472 | 122.5021 | -0.20142 | 122.4106 | 122.4152 | 122.5342 | -0.15564
2218.6562 | 122.6212 | -122.3465 | 0.10986 | -0.00091566 | 0.016684 | 0.00080749 | 0.0035441 | 0.053792 | 0.0014185 | -0.0039733 | -0.00083936 | 0.0041956 | -0.030349 | 0.042212 | 0.0068165 | 0.0041378 | 0.082397 | 0.045776 | 0.073242 | 0.11902 | 0.16022 | 0.032043 | -0.091553 | 0.050354 | 0.082397 | -0.064087 | 0.054932 | 0.054932 | 0.027466 | -0.054932 | 122.3785 | 122.2549 | 0.050354 | 122.3923 | 122.4655 | 0.21057 | -0.027466 | 122.374 | 122.2916 | -0.054931 | 122.3969 | 122.2824 | -0.009155 | -0.054931 | 122.5067 | 122.4289 | 122.4197 | -0.20142 | 122.4014 | 122.4014 | 122.4289 | -0.16479
2220.4219 | 122.644 | -122.3831 | 0.09613 | -0.0085447 | 0.02117 | 0.00080749 | 0.0065347 | 0.053365 | -0.00029051 | -0.00098272 | 0.0067901 | 0.001632 | -0.029068 | 0.043066 | 0.0059621 | 0.0041378 | 0.013733 | -0.013733 | 0 | 0.082397 | 0.16937 | 0.027466 | -0.10071 | -0.013733 | -0.018311 | -0.12817 | 0.059509 | 0.050354 | 0.022888 | -0.07782 | 122.4106 | 122.2824 | 0.073243 | 122.3694 | 122.4655 | 0.18311 | -0.082397 | 122.406 | 122.3053 | -0.036621 | 122.3694 | 122.2549 | -0.050354 | -0.045776 | 122.5525 | 122.3969 | 122.3831 | -0.19684 | 122.4426 | 122.4335 | 122.3648 | -0.17395
2222.1719 | 122.6761 | -122.3648 | 0.09613 | -0.00091566 | 0.013907 | 0.0033709 | 0.0020487 | 0.053152 | 0.00099129 | -0.0022643 | -0.0084684 | 0.003341 | -0.030349 | 0.041998 | 0.0059621 | 0.0049924 | 0.022888 | 0 | 0.009155 | 0.07782 | 0.16022 | 0.018311 | -0.10071 | -0.004578 | -0.004578 | -0.10071 | 0.068665 | 0.068665 | 0.027466 | -0.050354 | 122.3831 | 122.2641 | 0.064087 | 122.3648 | 122.4426 | 0.17853 | -0.073242 | 122.3923 | 122.3145 | -0.027465 | 122.3602 | 122.2641 | -0.050354 | -0.027465 | 122.525 | 122.3877 | 122.374 | -0.19684 | 122.4335 | 122.4335 | 122.3602 | -0.14648
2223.9219 | 122.5067 | -122.4152 | 0.11902 | -0.00091566 | 0.01113 | 0.0059345 | 0.0031167 | 0.053365 | -0.0049903 | -0.0056823 | -0.00083936 | -0.0002906 | -0.031417 | 0.037085 | 0.0044667 | 0.0071286 | 0.068665 | 0.13733 | 0.11444 | 0.16022 | 0.12817 | 0.041199 | -0.068665 | 0.018311 | 0.11444 | -0.036621 | 0.050354 | 0.054932 | 0.027466 | -0.032043 | 122.4564 | 122.3465 | 0.009155 | 122.5525 | 122.5754 | 0.22888 | -0.050354 | 122.4426 | 122.3831 | -0.068665 | 122.4335 | 122.3785 | -0.004578 | -0.064087 | 122.5433 | 122.4838 | 122.5296 | -0.18768 | 122.4655 | 122.4701 | 122.5296 | -0.15106
2225.6875 | 122.6212 | -122.3511 | 0.1236 | -0.0085447 | 0.017752 | 0.00059389 | 0.0052531 | 0.052297 | 0.0018457 | -0.0011963 | -0.00083936 | 0.0037684 | -0.029495 | 0.04328 | 0.0061757 | 0.0047788 | 0.027466 | 0 | 0.013733 | 0.086975 | 0.16937 | 0.041199 | -0.10071 | -0.032043 | 0.004578 | -0.14648 | 0.059509 | 0.050354 | 0.018311 | -0.050354 | 122.3923 | 122.2504 | 0.045777 | 122.3511 | 122.438 | 0.18768 | -0.09613 | 122.3694 | 122.3007 | -0.064087 | 122.319 | 122.2046 | -0.09613 | -0.073242 | 122.5204 | 122.3785 | 122.3648 | -0.2243 | 122.4106 | 122.4014 | 122.3557 | -0.17395
2227.375 | 122.5342 | -122.4243 | 0.11902 | 0.0067138 | 0.009848 | 0.0040119 | 0.0024759 | 0.054006 | -0.0077673 | -0.0054687 | -0.00083936 | -0.0024268 | -0.033126 | 0.039648 | 0.0044667 | 0.0090512 | 0.073242 | 0.10071 | 0.1236 | 0.12817 | 0.10986 | 0.050354 | -0.045776 | 0.027466 | 0.091553 | -0.027466 | 0.027466 | 0.050354 | 0.041199 | -0.032043 | 122.4747 | 122.3785 | -0.009156 | 122.525 | 122.5525 | 0.17395 | -0.045777 | 122.4655 | 122.3923 | -0.091553 | 122.4518 | 122.3969 | 0.004577 | -0.068665 | 122.5342 | 122.4976 | 122.5479 | -0.16479 | 122.4518 | 122.4747 | 122.5159 | -0.15106
2229.1562 | 122.5388 | -122.4197 | 0.13275 | -0.0085447 | 0.012839 | 0.0033709 | 0.0080301 | 0.051229 | -0.0047765 | -0.0037597 | -0.0084684 | 0.000564 | -0.030563 | 0.04093 | 0.0044667 | 0.0067014 | 0.11444 | 0.11444 | 0.13275 | 0.15564 | 0.12817 | 0.064087 | -0.054932 | 0.036621 | 0.09613 | -0.009155 | 0.022888 | 0.036621 | 0.050354 | -0.018311 | 122.4838 | 122.3648 | -0.004577 | 122.5342 | 122.5754 | 0.21057 | -0.01831 | 122.4701 | 122.4014 | -0.10986 | 122.4564 | 122.4106 | 0.009156 | -0.09613 | 122.5479 | 122.5342 | 122.5525 | -0.18768 | 122.4426 | 122.4564 | 122.5159 | -0.15106
2230.9219 | 122.58 | -122.406 | 0.11902 | -0.00091566 | 0.010489 | 0.0033709 | 0.0050393 | 0.054006 | -0.0026403 | -0.0039733 | 0.0067901 | -7.6996e-05 | -0.031631 | 0.042212 | 0.0068165 | 0.0049924 | 0.11902 | 0.13275 | 0.14191 | 0.16479 | 0.10986 | 0.059509 | -0.059509 | 0.07782 | 0.13275 | 0.009155 | 0.018311 | 0.041199 | 0.045776 | -0.022888 | 122.4655 | 122.3465 | -0.009156 | 122.5388 | 122.5708 | 0.2243 | 0 | 122.4518 | 122.3831 | -0.10071 | 122.4838 | 122.4152 | 0.032043 | -0.07782 | 122.5159 | 122.525 | 122.5479 | -0.17853 | 122.4243 | 122.4472 | 122.5388 | -0.14191
2232.625 | 122.6028 | -122.406 | 0.1236 | -0.0085447 | 0.014548 | 0.0042255 | 0.0041849 | 0.051656 | -0.0028539 | -0.0033325 | 0.0067901 | -0.0026404 | -0.03099 | 0.039435 | 0.0046803 | 0.0062742 | 0.12817 | 0.13733 | 0.15106 | 0.15564 | 0.10529 | 0.07782 | -0.07782 | 0.064087 | 0.14191 | 0.013733 | 0.018311 | 0.027466 | 0.050354 | -0.022888 | 122.4838 | 122.3282 | -0.01831 | 122.5433 | 122.5616 | 0.23346 | 0.004578 | 122.4564 | 122.3831 | -0.10528 | 122.4701 | 122.4197 | 0.036621 | -0.09613 | 122.5113 | 122.5342 | 122.5571 | -0.20142 | 122.4243 | 122.4335 | 122.5479 | -0.14648
2234.3906 | 122.6761 | -122.3923 | 0.09613 | -0.016174 | 0.015402 | 0.0029437 | 0.0082437 | 0.053365 | 0.0014185 | -0.0035461 | -0.00083936 | 0.0001368 | -0.027572 | 0.041785 | 0.0048939 | 0.0030698 | 0.018311 | 0.004578 | 0.022888 | 0.086975 | 0.15564 | 0.036621 | -0.11902 | -0.018311 | 0.045776 | -0.10529 | 0.054932 | 0.073242 | 0.027466 | -0.054932 | 122.4289 | 122.2733 | 0.05951 | 122.3969 | 122.4792 | 0.20599 | -0.077819 | 122.4197 | 122.3373 | -0.041198 | 122.374 | 122.287 | -0.050354 | -0.022888 | 122.5479 | 122.4106 | 122.4152 | -0.21515 | 122.4472 | 122.4655 | 122.438 | -0.15106
2236.0938 | 122.58 | -122.4197 | 0.10986 | -0.016174 | 0.01348 | 0.0042255 | 0.0048257 | 0.053792 | -0.0032813 | -0.0024779 | 0.0067901 | -0.0009314 | -0.030777 | 0.040716 | 0.0053211 | 0.0077694 | 0.12817 | 0.13733 | 0.15106 | 0.16937 | 0.11444 | 0.07782 | -0.073242 | 0.073242 | 0.13733 | 0 | 0.013733 | 0.032043 | 0.064087 | -0.013733 | 122.4976 | 122.3465 | 0.004578 | 122.5571 | 122.5891 | 0.24261 | 0.018311 | 122.4838 | 122.406 | -0.09613 | 122.493 | 122.4197 | 0.013733 | -0.07782 | 122.5342 | 122.5479 | 122.5708 | -0.18311 | 122.4335 | 122.4518 | 122.5571 | -0.1236
2237.8438 | 122.6807 | -122.3694 | 0.10529 | 0.0067138 | 0.015189 | 0.0040119 | 0.0048257 | 0.054647 | 0.00035029 | -0.0031189 | 0.0067901 | 0.002273 | -0.029922 | 0.042212 | 0.0044667 | 0.0058468 | 0.041199 | -0.022888 | 0 | 0.091553 | 0.16937 | 0.027466 | -0.09613 | -0.022888 | -0.004578 | -0.14191 | 0.059509 | 0.07782 | 0.032043 | -0.045776 | 122.3969 | 122.2733 | 0.064087 | 122.3465 | 122.4609 | 0.18768 | -0.064087 | 122.4014 | 122.3236 | -0.045777 | 122.3465 | 122.2275 | -0.096131 | -0.027466 | 122.5388 | 122.4106 | 122.3694 | -0.20142 | 122.4289 | 122.4472 | 122.3648 | -0.15106
2239.5625 | 122.5571 | -122.4243 | 0.13275 | -0.016174 | 0.013693 | 0.0020893 | 0.0058939 | 0.054647 | -0.0052039 | -0.0016235 | 0.022049 | -0.0009314 | -0.030563 | 0.041144 | 0.0038259 | 0.0060604 | 0.091553 | 0.13275 | 0.13733 | 0.14648 | 0.11444 | 0.059509 | -0.054932 | 0.064087 | 0.12817 | 0.013733 | 0.032043 | 0.027466 | 0.068665 | -0.018311 | 122.4838 | 122.3694 | -0.01831 | 122.5571 | 122.5708 | 0.20142 | -0.041198 | 122.493 | 122.406 | -0.10071 | 122.4884 | 122.438 | 0.032044 | -0.10529 | 122.5388 | 122.5159 | 122.5616 | -0.18768 | 122.4564 | 122.4518 | 122.5525 | -0.15106
2241.3125 | 122.6303 | -122.3831 | 0.10529 | -0.016174 | 0.017325 | 0.0035847 | 0.0052531 | 0.054647 | 0.00035029 | -0.00098272 | 0.0067901 | 0.0027002 | -0.029281 | 0.04328 | 0.0091665 | 0.0043516 | 0.041199 | 0 | 0.009155 | 0.091553 | 0.15564 | 0.018311 | -0.09613 | -0.018311 | -0.004578 | -0.14191 | 0.068665 | 0.086975 | 0.013733 | -0.041199 | 122.4014 | 122.287 | 0.050354 | 122.3831 | 122.4747 | 0.18768 | -0.064087 | 122.3969 | 122.3419 | -0.036621 | 122.3648 | 122.2412 | -0.10071 | -0.018311 | 122.5388 | 122.4243 | 122.3923 | -0.20142 | 122.4518 | 122.4701 | 122.3785 | -0.14649
2243.0625 | 122.6761 | -122.3557 | 0.091553 | 0.014343 | 0.015616 | 0.0010211 | 0.0050393 | 0.052083 | 0.00013669 | -0.0029053 | -0.00083936 | -0.0005042 | -0.029068 | 0.04093 | 0.0078847 | 0.0071286 | 0.073242 | 0.07782 | 0.073242 | 0.1236 | 0.15564 | 0.032043 | -0.10986 | 0.018311 | 0.07782 | -0.07782 | 0.050354 | 0.059509 | 0.050354 | -0.041199 | 122.3877 | 122.2458 | 0.064087 | 122.4335 | 122.4792 | 0.23346 | -0.018311 | 122.406 | 122.3145 | -0.041199 | 122.374 | 122.2778 | -0.036621 | -0.032044 | 122.5113 | 122.4289 | 122.4289 | -0.20142 | 122.406 | 122.4152 | 122.4335 | -0.13275
2244.8281 | 122.6807 | -122.3969 | 0.10529 | -0.00091566 | 0.015616 | 0.0018757 | 0.0031167 | 0.053792 | -0.0032813 | -0.0033325 | -0.00083936 | 0.0001368 | -0.030136 | 0.042639 | 0.0078847 | 0.0062742 | 0.032043 | 0.032043 | 0.045776 | 0.09613 | 0.14648 | 0.036621 | -0.10529 | 0.045776 | 0.07782 | -0.036621 | 0.041199 | 0.050354 | 0.036621 | -0.027466 | 122.4335 | 122.2916 | 0.041198 | 122.4289 | 122.493 | 0.20142 | -0.073243 | 122.4335 | 122.3694 | -0.064087 | 122.4426 | 122.3602 | -0.009155 | -0.054932 | 122.5433 | 122.4289 | 122.4426 | -0.21057 | 122.4381 | 122.4472 | 122.4747 | -0.13275
2246.5312 | 122.5479 | -122.4289 | 0.12817 | 0.0067138 | 0.015189 | 0.0044391 | 0.0078165 | 0.051443 | -0.0056311 | -0.0046143 | 0.01442 | -0.0022132 | -0.029922 | 0.038794 | 0.0010487 | 0.0062742 | 0.073242 | 0.11902 | 0.12817 | 0.15106 | 0.13275 | 0.050354 | -0.086975 | 0 | 0.10986 | -0.027466 | 0.045776 | 0.054932 | 0.041199 | -0.036621 | 122.4792 | 122.3419 | 0.004577 | 122.5479 | 122.58 | 0.23804 | -0.054932 | 122.4701 | 122.3923 | -0.082398 | 122.4289 | 122.4014 | 0.009155 | -0.073242 | 122.5616 | 122.5021 | 122.5571 | -0.21515 | 122.4747 | 122.4838 | 122.5388 | -0.1648
2248.2969 | 122.612 | -122.3831 | 0.11902 | -0.00091566 | 0.011343 | 0.0057209 | 0.0073893 | 0.052938 | -0.0073401 | -0.0056823 | -0.016098 | -0.0043494 | -0.032486 | 0.039862 | 0.0016895 | 0.008624 | 0.041199 | 0.082397 | 0.09613 | 0.13275 | 0.1236 | 0.064087 | -0.082397 | 0.013733 | 0.1236 | 0 | 0.022888 | 0.050354 | 0.050354 | -0.018311 | 122.4472 | 122.3007 | 0.004577 | 122.4655 | 122.5159 | 0.21515 | -0.07782 | 122.4335 | 122.3648 | -0.096131 | 122.3969 | 122.3831 | 0.018311 | -0.068665 | 122.5067 | 122.4243 | 122.4792 | -0.20142 | 122.406 | 122.4335 | 122.5067 | -0.13733
2250 | 122.5616 | -122.438 | 0.13733 | -0.00091566 | 0.0094208 | 0.0044391 | 0.0056803 | 0.053152 | -0.0047765 | -0.0048279 | -0.0084684 | -0.0039222 | -0.030563 | 0.039007 | 0.0031849 | 0.0064878 | 0.059509 | 0.10071 | 0.10529 | 0.14191 | 0.11444 | 0.068665 | -0.054932 | 0.018311 | 0.07782 | -0.027466 | 0.036621 | 0.036621 | 0.045776 | -0.018311 | 122.5067 | 122.3831 | -0.022888 | 122.5388 | 122.58 | 0.19684 | -0.07782 | 122.4838 | 122.4197 | -0.10071 | 122.4564 | 122.4106 | -0.009155 | -0.10071 | 122.5525 | 122.4976 | 122.5433 | -0.19226 | 122.4747 | 122.4747 | 122.5159 | -0.15564
2251.7656 | 122.699 | -122.4014 | 0.10071 | -0.0085447 | 0.014975 | 0.0023029 | 0.0052531 | 0.05486 | -0.00029051 | -0.0033325 | -0.00083936 | 0.0003504 | -0.031417 | 0.041357 | 0.0040395 | 0.0054196 | 0.12817 | 0.11444 | 0.1236 | 0.16937 | 0.13733 | 0.07782 | -0.064087 | 0.09613 | 0.1236 | 0.018311 | 0.027466 | 0.027466 | 0.059509 | 0 | 122.4792 | 122.3373 | 0.036621 | 122.5159 | 122.5708 | 0.23346 | 0.027466 | 122.4609 | 122.4014 | -0.073242 | 122.4976 | 122.4197 | 0.018311 | -0.073242 | 122.5388 | 122.5296 | 122.525 | -0.1648 | 122.4289 | 122.4289 | 122.525 | -0.10071
2253.5312 | 122.6852 | -122.406 | 0.091553 | -0.0085447 | 0.01583 | 0.0027301 | 0.0035441 | 0.05422 | 0.0027003 | -0.0033325 | -0.016098 | 0.0031274 | -0.032058 | 0.041357 | 0.0091665 | 0.0047788 | 0.027466 | -0.027466 | -0.013733 | 0.082397 | 0.16479 | 0.018311 | -0.11902 | -0.013733 | -0.022888 | -0.13275 | 0.054932 | 0.082397 | 0.022888 | -0.054932 | 122.4243 | 122.287 | 0.073242 | 122.3785 | 122.4884 | 0.20142 | -0.064087 | 122.4289 | 122.3511 | -0.036621 | 122.3923 | 122.2733 | -0.077819 | -0.009156 | 122.5708 | 122.4335 | 122.3923 | -0.21057 | 122.4609 | 122.4884 | 122.3831 | -0.14649
2255.2812 | 122.5845 | -122.287 | 0.07782 | -0.023804 | 0.017325 | 0.0035847 | 0.0086709 | 0.051443 | 0.00099129 | -0.0018371 | -0.0084684 | 0.0009912 | -0.028 | 0.042212 | 0.0044667 | 0.0039242 | 0.045776 | 0.036621 | 0.054932 | 0.11444 | 0.13733 | 0.050354 | -0.091553 | 0.009155 | 0.068665 | -0.073242 | 0.059509 | 0.07782 | 0.036621 | -0.059509 | 122.3373 | 122.1954 | 0.059509 | 122.3236 | 122.4014 | 0.20599 | -0.032044 | 122.3236 | 122.2275 | -0.018311 | 122.2961 | 122.2137 | -0.013733 | 0 | 122.4243 | 122.3328 | 122.3419 | -0.16937 | 122.3465 | 122.3648 | 122.3557 | -0.13733
2257.0312 | 122.4335 | -122.0901 | 0.091553 | -0.00091566 | 0.01647 | 0.0031573 | 0.0031167 | 0.051443 | -0.0024267 | -0.00055532 | 0.0067901 | 0.001632 | -0.030777 | 0.042212 | 0.0055349 | 0.0054196 | 0.022888 | 0 | 0.009155 | 0.086975 | 0.14648 | 0.032043 | -0.10986 | -0.027466 | -0.009155 | -0.11902 | 0.064087 | 0.073242 | 0.036621 | -0.059509 | 122.1222 | 121.9803 | 0.054931 | 122.0901 | 122.1771 | 0.19684 | -0.068665 | 122.1268 | 122.0306 | -0.027466 | 122.0627 | 121.9711 | -0.05951 | -0.018311 | 122.2366 | 122.113 | 122.0993 | -0.20142 | 122.1542 | 122.1634 | 122.081 | -0.15106
2258.7188 | 122.3694 | -122.2229 | 0.12817 | -0.00091566 | 0.0089936 | 0.0040119 | 0.0061075 | 0.050588 | -0.0075537 | -0.0033325 | -0.00083936 | -0.0019996 | -0.031631 | 0.041144 | 0.0019033 | 0.0075558 | 0.054932 | 0.09613 | 0.10529 | 0.14191 | 0.11902 | 0.07782 | -0.068665 | 0.027466 | 0.091553 | -0.027466 | 0.022888 | 0.036621 | 0.068665 | -0.022888 | 122.3007 | 122.1542 | -0.009155 | 122.319 | 122.3648 | 0.21057 | -0.073242 | 122.2916 | 122.2 | -0.10529 | 122.2504 | 122.1954 | -0.004578 | -0.091553 | 122.3419 | 122.2778 | 122.3282 | -0.19684 | 122.2458 | 122.2595 | 122.3145 | -0.15106
2260.4688 | 122.4976 | -122.2 | 0.082397 | -0.00091566 | 0.017538 | 0.0018757 | 0.0080301 | 0.054006 | 0.00056389 | -0.0018371 | -0.00083936 | 0.001632 | -0.029068 | 0.042853 | 0.0048939 | 0.0030698 | 0.022888 | -0.032043 | 0.009155 | 0.086975 | 0.14648 | 0.036621 | -0.086975 | -0.022888 | -0.027466 | -0.13275 | 0.054932 | 0.082397 | 0.036621 | -0.045776 | 122.2366 | 122.113 | 0.064087 | 122.168 | 122.287 | 0.17395 | -0.059509 | 122.2366 | 122.1542 | -0.027465 | 122.1771 | 122.0673 | -0.086975 | 0 | 122.3465 | 122.2229 | 122.2092 | -0.16937 | 122.2549 | 122.2824 | 122.1725 | -0.12817
2262.2188 | 122.5388 | -122.2137 | 0.091553 | -0.00091566 | 0.013052 | 0.0025165 | 0.0016215 | 0.053579 | -0.0037085 | -0.0014099 | -0.0084684 | -0.0015722 | -0.031631 | 0.039862 | 0.0048939 | 0.0067014 | 0.11902 | 0.10986 | 0.13275 | 0.17853 | 0.13275 | 0.082397 | -0.064087 | 0.082397 | 0.13733 | 0.013733 | 0.018311 | 0.032043 | 0.073242 | -0.004578 | 122.2961 | 122.1497 | 0.041198 | 122.3236 | 122.3923 | 0.24261 | 0.027466 | 122.287 | 122.2092 | -0.073242 | 122.2961 | 122.2275 | 0.018311 | -0.05951 | 122.3465 | 122.3328 | 122.3465 | -0.15564 | 122.2321 | 122.2458 | 122.3511 | -0.096131
2263.9844 | 122.5113 | -122.2641 | 0.09613 | -0.00091566 | 0.016257 | 0.0033709 | 0.0095255 | 0.054433 | -0.0022131 | -0.0054687 | 0.0067901 | 0.0027002 | -0.028213 | 0.042853 | 0.0031849 | 0.0049924 | 0.022888 | 0 | 0.009155 | 0.082397 | 0.16022 | 0.027466 | -0.10986 | -0.050354 | 0.027466 | -0.10529 | 0.059509 | 0.086975 | 0.027466 | -0.073242 | 122.2916 | 122.1542 | 0.064087 | 122.2641 | 122.3465 | 0.19226 | -0.073242 | 122.2916 | 122.1909 | -0.036621 | 122.2137 | 122.1588 | -0.032044 | -0.009155 | 122.4243 | 122.287 | 122.2733 | -0.20599 | 122.3236 | 122.3511 | 122.2916 | -0.16937
2265.6719 | 122.5113 | -122.2549 | 0.10986 | -0.00091566 | 0.016898 | 0.0027301 | 0.0037577 | 0.053579 | 0.00077749 | -0.0020507 | 0.01442 | 0.0012048 | -0.029281 | 0.041357 | 0.0061757 | 0.0047788 | 0.004578 | -0.018311 | 0.009155 | 0.07782 | 0.15106 | 0.036621 | -0.10986 | -0.022888 | -0.009155 | -0.14648 | 0.059509 | 0.07782 | 0.018311 | -0.073242 | 122.2916 | 122.1451 | 0.041199 | 122.2366 | 122.3328 | 0.18768 | -0.10529 | 122.2733 | 122.1817 | -0.050354 | 122.2321 | 122.1085 | -0.073242 | -0.032043 | 122.406 | 122.2595 | 122.2641 | -0.21973 | 122.3145 | 122.3328 | 122.2458 | -0.18311
2267.4219 | 122.5479 | -122.3007 | 0.10986 | 0.0067138 | 0.01583 | 0.0025165 | 0.0065347 | 0.055288 | -0.0052039 | -0.0029053 | -0.0084684 | 0.0001368 | -0.028854 | 0.042425 | 0.0044667 | 0.0058468 | -0.013733 | -0.009155 | 0.004578 | 0.10071 | 0.19226 | 0.018311 | -0.11902 | -0.022888 | 0.027466 | -0.11444 | 0.064087 | 0.068665 | 0.027466 | -0.068665 | 122.319 | 122.1817 | 0.082398 | 122.2916 | 122.4014 | 0.21973 | -0.1236 | 122.3282 | 122.2321 | -0.045776 | 122.2778 | 122.1863 | -0.045776 | -0.041198 | 122.493 | 122.287 | 122.3053 | -0.22888 | 122.3648 | 122.3694 | 122.3282 | -0.17853
2269.1875 | 122.5983 | -122.2641 | 0.10071 | 0.0067138 | 0.014548 | 0.0020893 | 0.00098046 | 0.052297 | -0.0037085 | -0.0037597 | -0.00083936 | 0.0001368 | -0.029708 | 0.042639 | 0.0053211 | 0.0064878 | 0.036621 | 0.032043 | 0.050354 | 0.10986 | 0.15564 | 0.041199 | -0.09613 | 0.045776 | 0.091553 | -0.027466 | 0.041199 | 0.036621 | 0.059509 | -0.032043 | 122.3053 | 122.168 | 0.054932 | 122.2961 | 122.374 | 0.20599 | -0.064087 | 122.3236 | 122.2321 | -0.059509 | 122.3099 | 122.2366 | 0.004577 | -0.064087 | 122.4197 | 122.3007 | 122.3145 | -0.19684 | 122.3053 | 122.3007 | 122.3557 | -0.13275
2270.9375 | 122.5388 | -122.3328 | 0.11444 | -0.00091566 | 0.013693 | 0.0044391 | 0.0014079 | 0.053365 | -0.0043493 | -0.0029053 | 0.0067901 | -0.0017858 | -0.032699 | 0.040289 | 0.0053211 | 0.0067014 | 0.10071 | 0.14191 | 0.14648 | 0.16479 | 0.11902 | 0.091553 | -0.059509 | 0.086975 | 0.14191 | 0.022888 | 0.009155 | 0.022888 | 0.059509 | -0.009155 | 122.4243 | 122.2733 | 0.004578 | 122.4747 | 122.4976 | 0.2243 | -0.013733 | 122.3923 | 122.3236 | -0.10529 | 122.4197 | 122.3557 | 0.032043 | -0.091553 | 122.4518 | 122.4335 | 122.4792 | -0.17395 | 122.3419 | 122.3557 | 122.4747 | -0.1236
2272.625 | 122.5021 | -122.3145 | 0.11444 | 0.0067138 | 0.011771 | 0.0055073 | 0.0026895 | 0.055074 | -0.0052039 | -0.0033325 | 0.0067901 | -0.0005042 | -0.030349 | 0.041144 | 0.0040395 | 0.0060604 | 0.10986 | 0.13275 | 0.13733 | 0.17395 | 0.10986 | 0.07782 | -0.054932 | 0.059509 | 0.12817 | 0.009155 | 0.013733 | 0.036621 | 0.082397 | -0.004578 | 122.3923 | 122.2595 | -0.004578 | 122.4472 | 122.4884 | 0.22888 | -0.004578 | 122.3969 | 122.3099 | -0.10071 | 122.374 | 122.3236 | 0.013733 | -0.07782 | 122.4243 | 122.4243 | 122.4518 | -0.16937 | 122.3282 | 122.3511 | 122.4426 | -0.11902
2274.375 | 122.5296 | -122.3145 | 0.12817 | -0.00091566 | 0.010916 | 0.0042255 | 0.0080301 | 0.053152 | -0.0049903 | -0.0044007 | 0.0067901 | 0.0001368 | -0.031845 | 0.040716 | 0.0014759 | 0.0056332 | 0.086975 | 0.1236 | 0.14191 | 0.15564 | 0.13275 | 0.059509 | -0.068665 | 0.064087 | 0.16022 | 0.045776 | 0.036621 | 0.064087 | 0.07782 | -0.018311 | 122.374 | 122.2458 | 0.004577 | 122.438 | 122.4701 | 0.22431 | -0.041199 | 122.3923 | 122.2961 | -0.091553 | 122.3785 | 122.3602 | 0.064087 | -0.064087 | 122.4472 | 122.4014 | 122.4564 | -0.19684 | 122.3511 | 122.3785 | 122.4747 | -0.14649
2276.1406 | 122.6166 | -122.3007 | 0.09613 | -0.00091566 | 0.016257 | 0.0042255 | 0.0058939 | 0.053579 | 0.0018457 | -0.0031189 | -0.00083936 | 0.0027002 | -0.029922 | 0.040503 | 0.0063893 | 0.0024288 | 0.082397 | 0.036621 | 0.050354 | 0.11902 | 0.14648 | 0.032043 | -0.082397 | 0.018311 | 0.068665 | -0.073242 | 0.068665 | 0.086975 | 0.050354 | -0.059509 | 122.3328 | 122.2183 | 0.050354 | 122.3373 | 122.4197 | 0.20142 | -0.013733 | 122.3511 | 122.2412 | -0.027465 | 122.319 | 122.2275 | -0.013733 | -0.009155 | 122.4472 | 122.3831 | 122.3511 | -0.17853 | 122.3694 | 122.3877 | 122.3694 | -0.15564
2277.9062 | 122.493 | -122.3557 | 0.11444 | -0.00091566 | 0.0096344 | 0.0065753 | 0.0020487 | 0.052297 | -0.0056311 | -0.0052551 | -0.00083936 | -0.0024268 | -0.035049 | 0.040716 | 0.0036123 | 0.007983 | 0.10529 | 0.13275 | 0.13275 | 0.15106 | 0.11902 | 0.073242 | -0.064087 | 0.041199 | 0.11444 | -0.009155 | 0.045776 | 0.036621 | 0.041199 | -0.022888 | 122.4289 | 122.2916 | 0.004578 | 122.4884 | 122.5067 | 0.21515 | -0.009155 | 122.3969 | 122.3328 | -0.068665 | 122.3969 | 122.3465 | 0.013733 | -0.07782 | 122.4747 | 122.4609 | 122.4884 | -0.17853 | 122.4014 | 122.3923 | 122.4701 | -0.13733
2279.625 | 122.5021 | -122.3511 | 0.14191 | 0.0067138 | 0.014548 | 0.0014483 | 0.0080301 | 0.053365 | -0.0043493 | -0.0058959 | -0.00083936 | -0.0005042 | -0.029922 | 0.040716 | 0.0038259 | 0.0064878 | 0.059509 | 0.068665 | 0.082397 | 0.11444 | 0.13733 | 0.041199 | -0.082397 | -0.013733 | 0.041199 | -0.082397 | 0.059509 | 0.07782 | 0.022888 | -0.036621 | 122.3923 | 122.2687 | -0.004578 | 122.4197 | 122.4655 | 0.19684 | -0.082398 | 122.374 | 122.3145 | -0.082398 | 122.3373 | 122.2687 | -0.045776 | -0.064087 | 122.4884 | 122.4106 | 122.4335 | -0.2243 | 122.4106 | 122.4289 | 122.3923 | -0.17853
2281.3906 | 122.5479 | -122.3511 | 0.10529 | -0.00091566 | 0.012625 | 0.0055073 | 0.0090983 | 0.055715 | -0.0075537 | -0.0058959 | -0.00083936 | -0.0039222 | -0.03099 | 0.039862 | 0.0012623 | 0.0067014 | 0.10071 | 0.14648 | 0.14191 | 0.16022 | 0.13275 | 0.059509 | -0.059509 | 0.073242 | 0.16022 | 0.041199 | 0.032043 | 0.027466 | 0.068665 | -0.027466 | 122.4106 | 122.2916 | 0.027465 | 122.4976 | 122.5113 | 0.21973 | -0.004578 | 122.4197 | 122.3236 | -0.073243 | 122.4243 | 122.3923 | 0.068665 | -0.07782 | 122.4838 | 122.4518 | 122.493 | -0.16479 | 122.3831 | 122.3785 | 122.5113 | -0.13275
2283.0938 | 122.4747 | -122.3602 | 0.14648 | -0.00091566 | 0.01647 | 0.0072161 | 0.0061075 | 0.052083 | -0.0043493 | -0.0035461 | -0.00083936 | -0.0032812 | -0.029922 | 0.039221 | 0.0027577 | 0.0058468 | 0.11444 | 0.15106 | 0.16937 | 0.16479 | 0.12817 | 0.059509 | -0.068665 | 0.064087 | 0.16022 | 0.013733 | 0.013733 | 0.032043 | 0.073242 | -0.022888 | 122.4197 | 122.2916 | -0.01831 | 122.5113 | 122.525 | 0.23346 | -0.032043 | 122.4335 | 122.3373 | -0.13275 | 122.4243 | 122.374 | 0.036621 | -0.11444 | 122.4884 | 122.4747 | 122.5296 | -0.21515 | 122.374 | 122.3923 | 122.5204 | -0.16937
2284.8594 | 122.644 | -122.3236 | 0.07782 | 0.0067138 | 0.014548 | 0.0040119 | 0.0039713 | 0.055074 | 0.00035029 | -0.0044007 | -0.00083936 | 0.0031274 | -0.030349 | 0.042639 | 0.0061757 | 0.0026426 | 0.036621 | 0.009155 | 0.022888 | 0.10529 | 0.16022 | 0.032043 | -0.11902 | 0.009155 | 0.054932 | -0.10529 | 0.073242 | 0.07782 | 0.036621 | -0.059509 | 122.3557 | 122.2046 | 0.082397 | 122.3328 | 122.4289 | 0.22431 | -0.041199 | 122.3602 | 122.2641 | -0.004578 | 122.3328 | 122.2183 | -0.045777 | 0 | 122.4838 | 122.3602 | 122.3465 | -0.19684 | 122.3968 | 122.4014 | 122.3785 | -0.13733
2286.5625 | 122.6624 | -122.3373 | 0.09613 | -0.0085447 | 0.013907 | 0.0040119 | 0.0031167 | 0.054647 | 0.00013669 | -0.0039733 | -0.00083936 | 0.0035546 | -0.032272 | 0.041785 | 0.0068165 | 0.0060604 | 0.036621 | 0.022888 | 0.036621 | 0.10529 | 0.1831 | 0.041199 | -0.10071 | 0.027466 | 0.050354 | -0.073242 | 0.045776 | 0.054932 | 0.054932 | -0.027466 | 122.3785 | 122.2366 | 0.086975 | 122.3602 | 122.4426 | 0.20599 | -0.059509 | 122.3923 | 122.3099 | -0.050354 | 122.3648 | 122.2641 | -0.045776 | -0.041198 | 122.5204 | 122.374 | 122.374 | -0.19684 | 122.3831 | 122.3923 | 122.3877 | -0.1236
2288.2656 | 122.6486 | -122.3465 | 0.10986 | -0.00091566 | 0.012839 | 0.0025165 | 0.0018351 | 0.05422 | 0.00013669 | -0.0024779 | -0.00083936 | -0.0005042 | -0.031845 | 0.041357 | 0.0072437 | 0.0067014 | 0.11444 | 0.10071 | 0.11902 | 0.16479 | 0.11902 | 0.059509 | -0.068665 | 0.091553 | 0.1236 | 0 | 0.018311 | 0.050354 | 0.050354 | -0.018311 | 122.406 | 122.2778 | 0.009156 | 122.4472 | 122.5113 | 0.23346 | 0.004578 | 122.3969 | 122.3282 | -0.091552 | 122.4381 | 122.3465 | 0.018311 | -0.059509 | 122.4655 | 122.4609 | 122.4655 | -0.17853 | 122.3648 | 122.3969 | 122.4701 | -0.12817
2290.0312 | 122.6349 | -122.3602 | 0.086975 | -0.00091566 | 0.016898 | 0.0044391 | 0.0043985 | 0.054433 | 0.00099129 | -0.0014099 | 0.0067901 | 0.0014184 | -0.031631 | 0.041998 | 0.0053211 | 0.003497 | 0.10071 | 0.054932 | 0.064087 | 0.11902 | 0.16937 | 0.041199 | -0.091553 | 0.041199 | 0.086975 | -0.073242 | 0.054932 | 0.059509 | 0.041199 | -0.036621 | 122.4014 | 122.2687 | 0.082398 | 122.4152 | 122.4792 | 0.21057 | 0.013733 | 122.4014 | 122.3236 | -0.032043 | 122.4014 | 122.287 | -0.036621 | -0.027466 | 122.5296 | 122.4609 | 122.4243 | -0.17853 | 122.4152 | 122.4197 | 122.4472 | -0.1236
2291.7969 | 122.6578 | -122.3282 | 0.10529 | 0.0067138 | 0.015402 | 0.0016619 | 0.0043985 | 0.054647 | -0.0017859 | -0.0026917 | -0.00083936 | 0.0027002 | -0.029281 | 0.045416 | 0.0057485 | 0.0054196 | 0.073242 | 0.036621 | 0.041199 | 0.12817 | 0.15564 | 0.036621 | -0.10986 | 0.022888 | 0.082397 | -0.064087 | 0.041199 | 0.050354 | 0.027466 | -0.054932 | 122.3648 | 122.2183 | 0.050354 | 122.3648 | 122.4564 | 0.23804 | -0.032044 | 122.3557 | 122.2733 | -0.064087 | 122.3511 | 122.2641 | -0.009155 | -0.054932 | 122.4838 | 122.4014 | 122.3694 | -0.21515 | 122.3694 | 122.3785 | 122.4106 | -0.16022
2293.5469 | 122.5433 | -122.3877 | 0.13275 | -0.00091566 | 0.014975 | 0.0046527 | 0.0078165 | 0.052511 | -0.0045629 | -0.0031189 | 0.0067901 | -0.0013586 | -0.029281 | 0.04093 | 0.0023305 | 0.0058468 | 0.009155 | 0.009155 | 0.027466 | 0.07782 | 0.17853 | 0.022888 | -0.11902 | -0.059509 | 0.041199 | -0.091553 | 0.059509 | 0.082397 | 0.022888 | -0.059509 | 122.4106 | 122.2687 | 0.045777 | 122.3969 | 122.4655 | 0.19684 | -0.1236 | 122.4106 | 122.3282 | -0.073242 | 122.3282 | 122.2961 | -0.032044 | -0.050354 | 122.5662 | 122.3969 | 122.4152 | -0.25177 | 122.4472 | 122.4701 | 122.4289 | -0.19226
2295.25 | 122.6349 | -122.3648 | 0.10071 | -0.0085447 | 0.01348 | 0.0027301 | 0.0033305 | 0.052297 | -0.0034949 | -0.0024779 | -0.00083936 | -0.0030676 | -0.031417 | 0.039648 | 0.0048939 | 0.0058468 | 0.10529 | 0.1236 | 0.13275 | 0.1831 | 0.10986 | 0.073242 | -0.068665 | 0.07782 | 0.14648 | 0.027466 | 0.004578 | 0.022888 | 0.086975 | -0.041199 | 122.438 | 122.2961 | 0.009155 | 122.4884 | 122.5479 | 0.25177 | 0.004578 | 122.4518 | 122.3236 | -0.09613 | 122.4426 | 122.3923 | 0.068665 | -0.07782 | 122.4747 | 122.4701 | 122.4976 | -0.16937 | 122.3694 | 122.3877 | 122.5113 | -0.14191
2297.0156 | 122.5525 | -122.3923 | 0.14191 | -0.0085447 | 0.015189 | 0.0027301 | 0.0022623 | 0.05422 | -0.0060583 | -0.0039733 | -0.0084684 | -7.6996e-05 | -0.030349 | 0.039221 | 0.0027577 | 0.0058468 | 0.1236 | 0.11902 | 0.14191 | 0.15106 | 0.11444 | 0.068665 | -0.064087 | 0.054932 | 0.11444 | 0.004578 | 0.036621 | 0.041199 | 0.054932 | -0.032043 | 122.4609 | 122.3282 | -0.027466 | 122.5113 | 122.5433 | 0.21515 | -0.018311 | 122.4472 | 122.3602 | -0.10529 | 122.4472 | 122.3969 | 0.036621 | -0.10071 | 122.5067 | 122.5159 | 122.5342 | -0.20599 | 122.4289 | 122.4335 | 122.5067 | -0.17395
2298.7188 | 122.5616 | -122.3923 | 0.13733 | -0.0085447 | 0.012839 | 0.0050799 | 0.0035441 | 0.052724 | -0.0037085 | -0.0044007 | -0.00083936 | -0.0024268 | -0.032699 | 0.040503 | 0.0048939 | 0.006915 | 0.1236 | 0.12817 | 0.14648 | 0.15564 | 0.10529 | 0.064087 | -0.064087 | 0.068665 | 0.13733 | 0.013733 | 0.022888 | 0.036621 | 0.059509 | -0.027466 | 122.4564 | 122.3282 | -0.032043 | 122.5204 | 122.5479 | 0.21973 | -0.013733 | 122.4518 | 122.3648 | -0.11444 | 122.4609 | 122.406 | 0.041199 | -0.10071 | 122.4976 | 122.5159 | 122.5388 | -0.20142 | 122.4152 | 122.4289 | 122.5296 | -0.16479
2300.4844 | 122.5937 | -122.3831 | 0.12817 | -0.00091566 | 0.012412 | 0.0042255 | 0.0090983 | 0.053579 | -0.0066993 | -0.0080321 | -0.0084684 | -0.0017858 | -0.030777 | 0.039435 | 0.0036123 | 0.005206 | 0.050354 | 0.073242 | 0.09613 | 0.14191 | 0.12817 | 0.064087 | -0.07782 | 0.027466 | 0.09613 | -0.004578 | 0.027466 | 0.045776 | 0.064087 | -0.013733 | 122.4472 | 122.3053 | 0 | 122.4564 | 122.525 | 0.21973 | -0.07782 | 122.4472 | 122.3694 | -0.10071 | 122.4106 | 122.3785 | 0.009155 | -0.082398 | 122.5113 | 122.4335 | 122.4792 | -0.20599 | 122.4106 | 122.4289 | 122.4792 | -0.14191
2302.2031 | 122.6349 | -122.3831 | 0.11902 | -0.0085447 | 0.017752 | 0.0044391 | 0.0086709 | 0.049306 | -0.00093131 | -0.0063233 | 0.0067901 | 0.0029138 | -0.028854 | 0.041571 | 0.0053211 | 0.005206 | 0.032043 | 0.013733 | 0 | 0.10071 | 0.16479 | 0.027466 | -0.10071 | -0.018311 | 0.027466 | -0.10986 | 0.054932 | 0.059509 | 0.018311 | -0.050354 | 122.4106 | 122.2824 | 0.045776 | 122.3969 | 122.4838 | 0.20142 | -0.086976 | 122.4014 | 122.3328 | -0.064087 | 122.3648 | 122.2733 | -0.059509 | -0.05951 | 122.5479 | 122.4152 | 122.3831 | -0.21973 | 122.438 | 122.4426 | 122.4106 | -0.16937
2303.9688 | 122.5525 | -122.4243 | 0.11902 | -0.00091566 | 0.012625 | 0.0055073 | 0.0014079 | 0.055929 | -0.0039221 | -0.0048279 | 0.0067901 | -0.0017858 | -0.030563 | 0.037939 | 0.0053211 | 0.0058468 | 0.10529 | 0.13275 | 0.15564 | 0.13275 | 0.13733 | 0.068665 | -0.073242 | 0.07782 | 0.11902 | 0.009155 | 0.027466 | 0.036621 | 0.054932 | -0.009155 | 122.493 | 122.3511 | 0.01831 | 122.5571 | 122.5571 | 0.20599 | -0.013733 | 122.4792 | 122.4152 | -0.091553 | 122.5021 | 122.4335 | 0.01831 | -0.082398 | 122.5616 | 122.5296 | 122.58 | -0.19226 | 122.4518 | 122.4609 | 122.5433 | -0.12817
2305.7344 | 122.6028 | -122.4106 | 0.10986 | -0.0085447 | 0.012839 | 0.0042255 | 0.0041849 | 0.051656 | -0.0043493 | -0.0054687 | -0.00083936 | -0.0019996 | -0.033126 | 0.037726 | 0.0059621 | 0.0071286 | 0.11444 | 0.15564 | 0.15564 | 0.15106 | 0.11902 | 0.064087 | -0.045776 | 0.068665 | 0.13275 | 0.013733 | 0.027466 | 0.027466 | 0.064087 | -0.009155 | 122.4747 | 122.3648 | 0.009156 | 122.5662 | 122.5616 | 0.19684 | 0.004578 | 122.4747 | 122.4014 | -0.082397 | 122.4792 | 122.4243 | 0.022888 | -0.082397 | 122.5296 | 122.525 | 122.5662 | -0.15564 | 122.438 | 122.438 | 122.5433 | -0.11902
2307.4844 | 122.6624 | -122.4152 | 0.10529 | 0.0067138 | 0.014548 | 0.0046527 | 0.0037577 | 0.053365 | 0.00077749 | -0.0024779 | -0.0084684 | 0.0024866 | -0.031845 | 0.040289 | 0.0078847 | 0.0062742 | 0.013733 | -0.027466 | 0 | 0.073242 | 0.16479 | 0.032043 | -0.09613 | -0.018311 | -0.004578 | -0.12817 | 0.068665 | 0.07782 | 0.022888 | -0.041199 | 122.4472 | 122.319 | 0.059509 | 122.3877 | 122.4884 | 0.16937 | -0.091553 | 122.438 | 122.374 | -0.036621 | 122.3969 | 122.287 | -0.086975 | -0.027466 | 122.58 | 122.4289 | 122.4152 | -0.20142 | 122.4838 | 122.493 | 122.4106 | -0.14649
2309.2656 | 122.6395 | -122.3831 | 0.10986 | 0.0067138 | 0.017752 | 0.0044391 | 0.0029031 | 0.055715 | 0.0020593 | -0.0022643 | -0.00083936 | 0.003341 | -0.03099 | 0.04093 | 0.0061757 | 0.0049924 | 0.036621 | 0.009155 | 0.009155 | 0.10071 | 0.14648 | 0.041199 | -0.10529 | -0.004578 | -0.004578 | -0.12817 | 0.064087 | 0.068665 | 0.041199 | -0.041199 | 122.4243 | 122.2778 | 0.036621 | 122.3923 | 122.4838 | 0.20599 | -0.073242 | 122.4243 | 122.3419 | -0.045776 | 122.3785 | 122.2549 | -0.086975 | -0.041198 | 122.5296 | 122.4197 | 122.3923 | -0.21515 | 122.4472 | 122.4518 | 122.3785 | -0.15106
2310.9688 | 122.6624 | -122.4014 | 0.10071 | -0.00091566 | 0.015189 | 0.0044391 | 0.0056803 | 0.05422 | -0.0037085 | -0.0048279 | -0.00083936 | 0.0012048 | -0.029281 | 0.04093 | 0.0031849 | 0.0058468 | 0.013733 | -0.009155 | 0.004578 | 0.086975 | 0.15106 | 0.027466 | -0.09613 | -0.018311 | 0.041199 | -0.11902 | 0.082397 | 0.064087 | 0.027466 | -0.059509 | 122.4289 | 122.3053 | 0.050354 | 122.3923 | 122.4884 | 0.1831 | -0.086975 | 122.4289 | 122.3419 | -0.018311 | 122.3831 | 122.2824 | -0.05951 | -0.036621 | 122.5525 | 122.4152 | 122.406 | -0.19684 | 122.4838 | 122.4655 | 122.4426 | -0.16022
2312.7344 | 122.6486 | -122.4152 | 0.10986 | -0.00091566 | 0.016257 | 0.0029437 | 0.0048257 | 0.053792 | 0.0014185 | -0.0046143 | -0.00083936 | 0.003341 | -0.02864 | 0.044348 | 0.0055349 | 0.0047788 | 0.009155 | -0.036621 | 0 | 0.082397 | 0.16937 | 0.032043 | -0.10071 | -0.027466 | -0.004578 | -0.12817 | 0.064087 | 0.086975 | 0.027466 | -0.045776 | 122.4472 | 122.3145 | 0.05951 | 122.3785 | 122.4976 | 0.18311 | -0.10071 | 122.4426 | 122.3694 | -0.045776 | 122.3877 | 122.287 | -0.082398 | -0.022888 | 122.5845 | 122.4243 | 122.4152 | -0.21057 | 122.4792 | 122.5021 | 122.4106 | -0.15564
2314.4375 | 122.6212 | -122.4197 | 0.10986 | -0.00091566 | 0.014548 | 0.0037983 | 0.0084573 | 0.053365 | -0.0088355 | -0.0029053 | -0.016098 | -0.0024268 | -0.029068 | 0.040716 | -0.0015147 | 0.0062742 | 0.068665 | 0.091553 | 0.10529 | 0.15106 | 0.12817 | 0.059509 | -0.073242 | 0.041199 | 0.14191 | 0.032043 | 0.022888 | 0.045776 | 0.064087 | -0.022888 | 122.4792 | 122.3465 | 0.018311 | 122.5113 | 122.5708 | 0.2243 | -0.041198 | 122.4838 | 122.3969 | -0.086975 | 122.4609 | 122.4518 | 0.054931 | -0.064087 | 122.5479 | 122.4884 | 122.525 | -0.18311 | 122.4426 | 122.4655 | 122.5616 | -0.13275
2316.2031 | 122.6898 | -122.3877 | 0.073242 | -0.0085447 | 0.011984 | 0.0046527 | 0.0050393 | 0.053579 | -0.00071771 | -0.0039733 | -0.00083936 | 0.0012048 | -0.032272 | 0.043494 | 0.0068165 | 0.0032834 | 0.045776 | 0.022888 | 0.041199 | 0.11902 | 0.16479 | 0.032043 | -0.10529 | 0.013733 | 0.059509 | -0.064087 | 0.054932 | 0.064087 | 0.022888 | -0.059509 | 122.4197 | 122.2824 | 0.091553 | 122.4106 | 122.5067 | 0.22431 | -0.027466 | 122.4106 | 122.3282 | -0.01831 | 122.4014 | 122.3236 | -0.004578 | -0.009155 | 122.5525 | 122.4335 | 122.4289 | -0.17853 | 122.4426 | 122.4518 | 122.4472 | -0.13275
2317.8906 | 122.7127 | -122.3785 | 0.091553 | -0.0085447 | 0.017325 | 0.0040119 | 0.0056803 | 0.053152 | 0.00035029 | -0.0018371 | -0.00083936 | -0.0013586 | -0.028854 | 0.040716 | 0.0059621 | 0.0058468 | 0.009155 | 0 | 0.009155 | 0.086975 | 0.16937 | 0.032043 | -0.086975 | -0.009155 | 0.013733 | -0.10071 | 0.054932 | 0.064087 | 0.032043 | -0.045776 | 122.4106 | 122.2916 | 0.07782 | 122.3785 | 122.4655 | 0.17395 | -0.082398 | 122.4106 | 122.3328 | -0.036621 | 122.3694 | 122.2778 | -0.054932 | -0.027466 | 122.5479 | 122.3877 | 122.3877 | -0.17853 | 122.4335 | 122.4426 | 122.3923 | -0.13733
2319.6406 | 122.7219 | -122.4197 | 0.10529 | -0.00091566 | 0.014121 | 0.0046527 | 0.0046121 | 0.052938 | -0.0022131 | -0.0018371 | -0.0084684 | 0.0012048 | -0.029495 | 0.044989 | 0.0087391 | 0.006915 | 0.036621 | -0.004578 | 0.013733 | 0.086975 | 0.16022 | 0.036621 | -0.091553 | 0.004578 | 0.004578 | -0.091553 | 0.050354 | 0.082397 | 0.027466 | -0.045776 | 122.4564 | 122.3282 | 0.054931 | 122.4152 | 122.5067 | 0.17853 | -0.068665 | 122.4472 | 122.374 | -0.054932 | 122.4243 | 122.3282 | -0.045777 | -0.022889 | 122.58 | 122.4564 | 122.4335 | -0.19684 | 122.4701 | 122.5021 | 122.4243 | -0.15106
2321.3906 | 122.7081 | -122.4197 | 0.082397 | 0.014343 | 0.019675 | 0.0012347 | 0.0076029 | 0.050802 | -0.0015723 | -0.0026917 | -0.00083936 | 0.0007776 | -0.029068 | 0.042639 | 0.0040395 | 0.0039242 | 0.036621 | 0.022888 | 0.041199 | 0.13275 | 0.14648 | 0.036621 | -0.11444 | -0.004578 | 0.068665 | -0.086975 | 0.068665 | 0.07782 | 0.022888 | -0.059509 | 122.4564 | 122.3053 | 0.064087 | 122.4426 | 122.5525 | 0.24719 | -0.045776 | 122.4426 | 122.3602 | -0.013732 | 122.4152 | 122.3328 | -0.027466 | -0.004577 | 122.5662 | 122.4564 | 122.4609 | -0.19684 | 122.4884 | 122.4976 | 122.4884 | -0.14191
2323.0938 | 122.6349 | -122.4289 | 0.10529 | -0.00091566 | 0.014761 | 0.0042255 | 0.0080301 | 0.052083 | -0.010117 | -0.0035461 | 0.0067901 | -0.0017858 | -0.029281 | 0.041357 | -1.9327e-05 | 0.0077694 | 0.032043 | 0.073242 | 0.09613 | 0.13275 | 0.13275 | 0.050354 | -0.068665 | 0 | 0.10986 | -0.004578 | 0.032043 | 0.054932 | 0.045776 | -0.022888 | 122.4792 | 122.3602 | 0.027465 | 122.5021 | 122.5616 | 0.20142 | -0.073243 | 122.4747 | 122.406 | -0.073243 | 122.4289 | 122.4243 | 0.01831 | -0.050354 | 122.5616 | 122.4609 | 122.525 | -0.17395 | 122.4609 | 122.4838 | 122.5388 | -0.12817
2324.8594 | 122.6807 | -122.4289 | 0.10071 | -0.016174 | 0.01647 | -0.00026071 | 0.0035441 | 0.053579 | 0.0016321 | -0.0031189 | 0.0067901 | 0.0048364 | -0.029068 | 0.044775 | 0.0063893 | 0.005206 | 0.022888 | -0.041199 | 0 | 0.091553 | 0.16022 | 0.027466 | -0.09613 | -0.022888 | -0.022888 | -0.13275 | 0.059509 | 0.07782 | 0.022888 | -0.054932 | 122.4564 | 122.3328 | 0.059509 | 122.3877 | 122.5204 | 0.18768 | -0.07782 | 122.4518 | 122.374 | -0.041199 | 122.406 | 122.2961 | -0.077819 | -0.022888 | 122.5891 | 122.4518 | 122.4289 | -0.19684 | 122.4884 | 122.5067 | 122.406 | -0.15564
2326.625 | 122.7356 | -122.4014 | 0.07782 | -0.00091566 | 0.015189 | 0.0018757 | 0.0024759 | 0.053152 | -0.0034949 | -0.0044007 | -0.0084684 | 0.0014184 | -0.031417 | 0.041785 | 0.0057485 | 0.0081968 | 0.036621 | -0.018311 | 0 | 0.07782 | 0.16479 | 0.036621 | -0.082397 | 0.004578 | 0.013733 | -0.073242 | 0.054932 | 0.064087 | 0.036621 | -0.036621 | 122.438 | 122.319 | 0.086975 | 122.3831 | 122.4792 | 0.16022 | -0.041199 | 122.438 | 122.3648 | -0.022888 | 122.406 | 122.3282 | -0.036621 | -0.013733 | 122.5662 | 122.438 | 122.4014 | -0.16022 | 122.4564 | 122.4655 | 122.4152 | -0.11444
2328.375 | 122.6669 | -122.4609 | 0.10529 | -0.00091566 | 0.01647 | 0.0016619 | 0.0035441 | 0.053365 | -0.0019995 | -0.0033325 | -0.00083936 | 0.002273 | -0.029495 | 0.042212 | 0.0083119 | 0.0039242 | 0.032043 | -0.027466 | -0.004578 | 0.07782 | 0.17395 | 0.036621 | -0.10529 | -0.027466 | -0.022888 | -0.16022 | 0.059509 | 0.082397 | 0.032043 | -0.045776 | 122.4976 | 122.3557 | 0.068664 | 122.4335 | 122.5388 | 0.18311 | -0.073243 | 122.493 | 122.4152 | -0.045777 | 122.4335 | 122.3007 | -0.11444 | -0.022889 | 122.6349 | 122.493 | 122.4564 | -0.21057 | 122.5204 | 122.5433 | 122.438 | -0.15106
2330.0781 | 122.6303 | -122.4335 | 0.11902 | -0.00091566 | 0.01647 | 0.0048663 | 0.0082437 | 0.055715 | -0.0056311 | -0.0061095 | -0.0084684 | -0.0024268 | -0.029708 | 0.040716 | 0.0029713 | 0.0060604 | 0.013733 | 0.004578 | 0.032043 | 0.073242 | 0.17853 | 0.027466 | -0.13275 | -0.050354 | 0.022888 | -0.11444 | 0.073242 | 0.091553 | 0.013733 | -0.054932 | 122.4609 | 122.3007 | 0.059509 | 122.438 | 122.5067 | 0.20599 | -0.10529 | 122.4472 | 122.3785 | -0.045777 | 122.3831 | 122.319 | -0.059509 | -0.027466 | 122.612 | 122.4472 | 122.4655 | -0.25177 | 122.5067 | 122.525 | 122.4564 | -0.17395
2331.8281 | 122.731 | -122.4197 | 0.11444 | -0.00091566 | 0.013266 | 0.0014483 | 0.0043985 | 0.051656 | -0.0037085 | -0.0024779 | -0.00083936 | -0.0015722 | -0.032058 | 0.042425 | 0.0040395 | 0.005206 | 0.073242 | 0.073242 | 0.10071 | 0.13733 | 0.14191 | 0.041199 | -0.086975 | 0.054932 | 0.11902 | 0 | 0.036621 | 0.045776 | 0.059509 | -0.013733 | 122.4609 | 122.3328 | 0.027466 | 122.493 | 122.5571 | 0.2243 | -0.041199 | 122.4792 | 122.406 | -0.07782 | 122.4747 | 122.4197 | 0.013733 | -0.068665 | 122.5616 | 122.493 | 122.5204 | -0.20142 | 122.4564 | 122.4655 | 122.5388 | -0.12817
2333.5156 | 122.6349 | -122.4747 | 0.13275 | -0.00091566 | 0.012412 | 0.0040119 | 0.0061075 | 0.05187 | -0.0077673 | -0.0054687 | 0.0067901 | -0.0049902 | -0.031631 | 0.040076 | 0.0010487 | 0.0090512 | 0.045776 | 0.059509 | 0.10071 | 0.1236 | 0.13275 | 0.050354 | -0.068665 | -0.004578 | 0.10529 | -0.018311 | 0.036621 | 0.059509 | 0.054932 | -0.027466 | 122.525 | 122.406 | 0 | 122.5342 | 122.5983 | 0.19226 | -0.086975 | 122.5296 | 122.4472 | -0.09613 | 122.4701 | 122.4564 | 0.009155 | -0.073242 | 122.6074 | 122.5204 | 122.5754 | -0.20142 | 122.5113 | 122.5342 | 122.58 | -0.16022
2335.2812 | 122.7356 | -122.438 | 0.10071 | -0.00091566 | 0.014121 | 0.0048663 | 0.0022623 | 0.052511 | -0.0017859 | -0.0050415 | -0.00083936 | 0.0029138 | -0.030349 | 0.041785 | 0.0063893 | 0.0041378 | 0.07782 | 0.036621 | 0.064087 | 0.10986 | 0.14648 | 0.041199 | -0.068665 | 0.059509 | 0.09613 | -0.018311 | 0.036621 | 0.050354 | 0.07782 | -0.013733 | 122.4792 | 122.3694 | 0.045776 | 122.4747 | 122.5479 | 0.17853 | -0.022888 | 122.5159 | 122.4243 | -0.064087 | 122.4976 | 122.4197 | -0.004578 | -0.050354 | 122.5845 | 122.5159 | 122.5021 | -0.16937 | 122.4747 | 122.4884 | 122.5342 | -0.11444
2336.9688 | 122.6028 | -122.4792 | 0.11902 | -0.0085447 | 0.01113 | 0.0055073 | 0.0043985 | 0.055074 | -0.0062719 | -0.0061095 | -0.00083936 | -0.0009314 | -0.03099 | 0.039648 | 0.0025441 | 0.0073422 | 0.082397 | 0.07782 | 0.10529 | 0.12817 | 0.11902 | 0.073242 | -0.068665 | 0.004578 | 0.082397 | -0.009155 | 0.036621 | 0.036621 | 0.059509 | -0.022888 | 122.5525 | 122.4106 | 0 | 122.5571 | 122.6074 | 0.19684 | -0.036622 | 122.5388 | 122.4564 | -0.082398 | 122.4838 | 122.4701 | 0.013733 | -0.082398 | 122.5983 | 122.5616 | 122.5845 | -0.18768 | 122.5159 | 122.5159 | 122.5616 | -0.14191
2338.7188 | 122.6578 | -122.4426 | 0.10986 | -0.00091566 | 0.012198 | 0.0061481 | 0.0054667 | 0.055929 | -0.0054175 | -0.0052551 | -0.00083936 | -0.0007178 | -0.030349 | 0.036017 | 0.0014759 | 0.0056332 | 0.10986 | 0.14191 | 0.14191 | 0.16022 | 0.14191 | 0.07782 | -0.073242 | 0.064087 | 0.15106 | 0.050354 | 0.041199 | 0.022888 | 0.059509 | -0.027466 | 122.5204 | 122.3694 | 0.032044 | 122.5845 | 122.6028 | 0.23346 | 0 | 122.5021 | 122.4152 | -0.068664 | 122.5067 | 122.493 | 0.07782 | -0.086975 | 122.5845 | 122.5525 | 122.5845 | -0.18311 | 122.4838 | 122.4655 | 122.5937 | -0.13733
2340.4844 | 122.6486 | -122.438 | 0.10529 | -0.0085447 | 0.015189 | 0.0044391 | 0.0061075 | 0.052724 | -0.0011451 | -0.0048279 | -0.00083936 | 0.0014184 | -0.030349 | 0.041998 | 0.0029713 | 0.0043516 | 0.032043 | -0.004578 | 0 | 0.086975 | 0.16022 | 0.004578 | -0.11444 | -0.036621 | 0.013733 | -0.11444 | 0.07782 | 0.09613 | 0.022888 | -0.064087 | 122.4426 | 122.3236 | 0.054931 | 122.4335 | 122.525 | 0.20142 | -0.073243 | 122.4609 | 122.374 | -0.027466 | 122.4014 | 122.3236 | -0.050354 | -0.009156 | 122.5983 | 122.4701 | 122.438 | -0.21973 | 122.5159 | 122.5342 | 122.4518 | -0.16937
2342.25 | 122.699 | -122.4472 | 0.10071 | 0.0067138 | 0.017325 | 0.0031573 | 0.0037577 | 0.054006 | 0.0029139 | -0.0054687 | -0.0084684 | 0.0046228 | -0.029495 | 0.042853 | 0.0055349 | 0.0041378 | 0.086975 | 0.022888 | 0.041199 | 0.11444 | 0.14648 | 0.018311 | -0.10529 | 0.004578 | 0.013733 | -0.13275 | 0.041199 | 0.073242 | 0.022888 | -0.059509 | 122.4655 | 122.3419 | 0.045776 | 122.4701 | 122.5616 | 0.21973 | -0.013733 | 122.4701 | 122.3877 | -0.059509 | 122.4518 | 122.3145 | -0.073242 | -0.027466 | 122.5937 | 122.5342 | 122.4884 | -0.20599 | 122.4884 | 122.5204 | 122.4609 | -0.16022
2343.9375 | 122.7081 | -122.4655 | 0.082397 | 0.0067138 | 0.018607 | 0.00059389 | 0.0069621 | 0.05187 | 0.00077749 | -0.0011963 | -0.00083936 | 0.0020594 | -0.028 | 0.042425 | 0.0070301 | 0.006915 | 0.032043 | -0.036621 | 0 | 0.09613 | 0.16022 | 0.032043 | -0.10071 | -0.032043 | -0.009155 | -0.16937 | 0.054932 | 0.091553 | 0.032043 | -0.054932 | 122.4976 | 122.3648 | 0.07782 | 122.4289 | 122.5616 | 0.19684 | -0.050354 | 122.4976 | 122.4106 | -0.027465 | 122.4335 | 122.2961 | -0.11444 | 0.009156 | 122.6257 | 122.4976 | 122.4655 | -0.18311 | 122.5204 | 122.5571 | 122.4564 | -0.13733
2345.7031 | 122.6028 | -122.4747 | 0.14648 | -0.00091566 | 0.0089936 | 0.0065753 | 0.0050393 | 0.052083 | -0.0058447 | -0.0046143 | -0.00083936 | -0.0015722 | -0.030563 | 0.04093 | 0.0066029 | 0.0073422 | 0.10071 | 0.13733 | 0.13733 | 0.13733 | 0.10529 | 0.064087 | -0.068665 | 0.036621 | 0.10071 | -0.009155 | 0.027466 | 0.036621 | 0.059509 | -0.018311 | 122.5388 | 122.406 | -0.041198 | 122.612 | 122.612 | 0.20599 | -0.045776 | 122.5342 | 122.4564 | -0.11902 | 122.5113 | 122.4655 | 0.009156 | -0.10986 | 122.58 | 122.5754 | 122.612 | -0.21515 | 122.5021 | 122.5113 | 122.5754 | -0.16479
2347.3906 | 122.6578 | -122.4609 | 0.14191 | -0.016174 | 0.012198 | 0.0059345 | 0.0093119 | 0.053579 | -0.0081945 | -0.0044007 | 0.0067901 | -0.0032812 | -0.032272 | 0.038367 | 0.0031849 | 0.0075558 | 0.082397 | 0.10986 | 0.12817 | 0.13275 | 0.12817 | 0.050354 | -0.07782 | 0.068665 | 0.14648 | 0.032043 | 0.036621 | 0.032043 | 0.050354 | -0.018311 | 122.5113 | 122.3831 | -0.013733 | 122.5708 | 122.5937 | 0.21057 | -0.05951 | 122.5113 | 122.4426 | -0.10529 | 122.5296 | 122.493 | 0.050354 | -0.10986 | 122.5891 | 122.5433 | 122.5891 | -0.21973 | 122.4976 | 122.493 | 122.6074 | -0.16022
2349.0938 | 122.7356 | -122.4152 | 0.09613 | -0.0085447 | 0.016257 | 0.0033709 | 0.0041849 | 0.053792 | -7.6908e-05 | -0.0016235 | -0.0084684 | -0.0002906 | -0.031417 | 0.039435 | 0.0053211 | 0.0062742 | 0.10529 | 0.10529 | 0.10986 | 0.15106 | 0.13733 | 0.068665 | -0.073242 | 0.086975 | 0.10986 | 0 | 0.013733 | 0.032043 | 0.068665 | -0.018311 | 122.4838 | 122.3419 | 0.041199 | 122.5204 | 122.5662 | 0.2243 | 0.009156 | 122.4838 | 122.3969 | -0.082397 | 122.5021 | 122.4152 | 0.018311 | -0.064087 | 122.5525 | 122.5204 | 122.525 | -0.16937 | 122.4289 | 122.4472 | 122.525 | -0.11444
2350.8594 | 122.6349 | -122.4564 | 0.14648 | -0.0085447 | 0.01348 | 0.0048663 | 0.0076029 | 0.053792 | -0.0049903 | -0.0041869 | -0.00083936 | -0.0009314 | -0.030136 | 0.039435 | 0.0027577 | 0.0062742 | 0.050354 | 0.082397 | 0.09613 | 0.12817 | 0.13733 | 0.050354 | -0.059509 | 0.018311 | 0.064087 | -0.022888 | 0.036621 | 0.041199 | 0.054932 | -0.027466 | 122.5067 | 122.3969 | -0.009155 | 122.5388 | 122.5845 | 0.18768 | -0.09613 | 122.5113 | 122.4289 | -0.10986 | 122.4747 | 122.4335 | 0.004578 | -0.10529 | 122.5937 | 122.5067 | 122.5525 | -0.20599 | 122.493 | 122.4976 | 122.5204 | -0.17395
2352.625 | 122.7356 | -122.4701 | 0.10529 | 0.0067138 | 0.014548 | 0.0037983 | 0.0039713 | 0.053152 | 0.00077749 | -0.0014099 | -0.00083936 | 0.0018456 | -0.028854 | 0.041357 | 0.0068165 | 0.0043516 | 0.004578 | -0.041199 | -0.004578 | 0.07782 | 0.16022 | 0.027466 | -0.09613 | -0.022888 | -0.032043 | -0.14191 | 0.054932 | 0.064087 | 0.041199 | -0.059509 | 122.4976 | 122.374 | 0.054931 | 122.4289 | 122.5479 | 0.17395 | -0.10071 | 122.5113 | 122.4106 | -0.050354 | 122.4472 | 122.3282 | -0.082398 | -0.041199 | 122.6303 | 122.4747 | 122.4655 | -0.20142 | 122.525 | 122.5342 | 122.4381 | -0.16479
2354.3281 | 122.6395 | -122.4701 | 0.10529 | -0.00091566 | 0.014548 | 0.0048663 | 0.0065347 | 0.053152 | -0.0077673 | -0.0052551 | -0.0084684 | 0.0014184 | -0.028213 | 0.038367 | 0.0044667 | 0.0071286 | 0.09613 | 0.16022 | 0.17395 | 0.16937 | 0.11444 | 0.07782 | -0.059509 | 0.07782 | 0.1831 | 0.018311 | 0.009155 | 0.027466 | 0.059509 | -0.013733 | 122.5479 | 122.4106 | 0.009155 | 122.6303 | 122.6395 | 0.22888 | -0.009156 | 122.5296 | 122.4564 | -0.096131 | 122.5479 | 122.4884 | 0.032044 | -0.07782 | 122.5845 | 122.5662 | 122.644 | -0.16479 | 122.4792 | 122.4976 | 122.6532 | -0.11902
2356.0938 | 122.7219 | -122.4792 | 0.091553 | 0.0067138 | 0.016898 | 0.0044391 | 0.0061075 | 0.052724 | 0.00035029 | -0.0086731 | -0.00083936 | 0.0012048 | -0.030563 | 0.041785 | 0.0036123 | 0.0049924 | 0.013733 | 0 | 0.027466 | 0.082397 | 0.16022 | 0.054932 | -0.09613 | -0.032043 | 0.022888 | -0.10986 | 0.064087 | 0.073242 | 0.032043 | -0.059509 | 122.5342 | 122.3831 | 0.068664 | 122.4792 | 122.5616 | 0.17853 | -0.07782 | 122.5113 | 122.4197 | -0.027466 | 122.4472 | 122.3694 | -0.050354 | -0.018311 | 122.6395 | 122.493 | 122.5067 | -0.18768 | 122.5433 | 122.5525 | 122.5021 | -0.15106
2357.8438 | 122.7402 | -122.4655 | 0.10071 | 0.0067138 | 0.015616 | 0.0029437 | 0.0033305 | 0.053579 | -0.00029051 | -0.0026917 | 0.0067901 | 0.0024866 | -0.029922 | 0.041571 | 0.0057485 | 0.0047788 | 0.009155 | -0.027466 | 0.004578 | 0.082397 | 0.17395 | 0.022888 | -0.09613 | -0.013733 | -0.022888 | -0.14191 | 0.073242 | 0.086975 | 0.045776 | -0.054932 | 122.4884 | 122.3694 | 0.073242 | 122.438 | 122.5479 | 0.17853 | -0.091553 | 122.5113 | 122.4106 | -0.027466 | 122.4518 | 122.3236 | -0.086975 | -0.013733 | 122.6395 | 122.4747 | 122.4701 | -0.19684 | 122.5388 | 122.5525 | 122.4426 | -0.15564
2359.5469 | 122.6532 | -122.4976 | 0.11902 | -0.0085447 | 0.014548 | 0.0046527 | 0.0065347 | 0.053579 | -0.0075537 | -0.0048279 | -0.00083936 | -0.0030676 | -0.033981 | 0.041144 | 0.0025441 | 0.0077694 | 0.10529 | 0.15564 | 0.16022 | 0.16479 | 0.14191 | 0.059509 | -0.059509 | 0.086975 | 0.17395 | 0.018311 | 0.036621 | 0.041199 | 0.064087 | -0.022888 | 122.5571 | 122.438 | 0.022888 | 122.6532 | 122.6624 | 0.2243 | -0.013733 | 122.5616 | 122.4747 | -0.082398 | 122.5845 | 122.5159 | 0.041199 | -0.07782 | 122.6395 | 122.6028 | 122.6578 | -0.17853 | 122.5342 | 122.5388 | 122.6715 | -0.14191
2361.3125 | 122.7676 | -122.4609 | 0.073242 | 0.0067138 | 0.014975 | 0.00016669 | 0.0031167 | 0.055074 | 0.00077749 | -0.0033325 | -0.0084684 | 0.0029138 | -0.030349 | 0.042425 | 0.0057485 | 0.003497 | 0.041199 | -0.004578 | 0.009155 | 0.07782 | 0.17853 | 0.036621 | -0.10529 | -0.013733 | 0.004578 | -0.11444 | 0.064087 | 0.064087 | 0.018311 | -0.059509 | 122.4976 | 122.3557 | 0.10529 | 122.4564 | 122.5388 | 0.18311 | -0.032043 | 122.4792 | 122.4014 | -0.009155 | 122.4472 | 122.3465 | -0.054932 | -0.009155 | 122.6395 | 122.5021 | 122.4701 | -0.17853 | 122.525 | 122.525 | 122.4655 | -0.13275
2363.0625 | 122.7676 | -122.4792 | 0.091553 | 0.014343 | 0.014975 | 0.0023029 | 0.0035441 | 0.053365 | -0.0013587 | -0.0031189 | -0.0084684 | 0.002273 | -0.029068 | 0.042425 | 0.0038259 | 0.0064878 | 0.022888 | -0.009155 | 0.009155 | 0.091553 | 0.17395 | 0.027466 | -0.091553 | -0.013733 | -0.013733 | -0.10986 | 0.07782 | 0.07782 | 0.045776 | -0.054932 | 122.5067 | 122.3877 | 0.082397 | 122.4701 | 122.5708 | 0.18311 | -0.068665 | 122.525 | 122.4243 | -0.013733 | 122.4655 | 122.3694 | -0.054931 | -0.013733 | 122.6532 | 122.5021 | 122.4884 | -0.18311 | 122.5571 | 122.5571 | 122.4655 | -0.14649
2364.8281 | 122.6532 | -122.5067 | 0.12817 | -0.00091566 | 0.012839 | 0.0037983 | 0.0078165 | 0.055288 | -0.0084081 | -0.0050415 | -0.00083936 | -0.0019996 | -0.029922 | 0.04093 | 0.0023305 | 0.0084104 | 0.054932 | 0.07782 | 0.091553 | 0.1236 | 0.1236 | 0.059509 | -0.059509 | 0.009155 | 0.073242 | -0.018311 | 0.032043 | 0.041199 | 0.045776 | -0.018311 | 122.5662 | 122.4472 | -0.004578 | 122.5845 | 122.6303 | 0.1831 | -0.073242 | 122.5525 | 122.4884 | -0.096131 | 122.5159 | 122.4884 | 0 | -0.086975 | 122.6303 | 122.5616 | 122.5983 | -0.18768 | 122.5388 | 122.5479 | 122.58 | -0.14649
2366.5312 | 122.644 | -122.5204 | 0.13275 | 0.0067138 | 0.014761 | 0.0067889 | 0.0069621 | 0.052938 | -0.0052039 | -0.0029053 | -0.00083936 | -0.0015722 | -0.030563 | 0.041785 | 0.00083507 | 0.007983 | 0.091553 | 0.10071 | 0.10071 | 0.14191 | 0.14648 | 0.054932 | -0.07782 | -0.009155 | 0.086975 | -0.082397 | 0.068665 | 0.059509 | 0.045776 | -0.045776 | 122.5754 | 122.4426 | 0.013733 | 122.6212 | 122.6624 | 0.21973 | -0.041198 | 122.5662 | 122.4747 | -0.064086 | 122.5113 | 122.4381 | -0.036621 | -0.073242 | 122.6669 | 122.612 | 122.6212 | -0.21057 | 122.5891 | 122.58 | 122.6074 | -0.17853
2368.3125 | 122.644 | -122.5296 | 0.13733 | -0.00091566 | 0.013693 | 0.0033709 | 0.0048257 | 0.053792 | -0.0034949 | -0.0033325 | 0.0067901 | -0.001145 | -0.032486 | 0.040289 | 0.0066029 | 0.006915 | 0.10986 | 0.14191 | 0.13275 | 0.14191 | 0.11902 | 0.073242 | -0.064087 | 0.045776 | 0.11444 | -0.009155 | 0.041199 | 0.032043 | 0.064087 | -0.009155 | 122.6028 | 122.4655 | -0.01831 | 122.6715 | 122.6715 | 0.20599 | -0.027466 | 122.5937 | 122.5204 | -0.09613 | 122.5754 | 122.5204 | 0 | -0.10529 | 122.6486 | 122.6395 | 122.6624 | -0.20142 | 122.5708 | 122.5616 | 122.644 | -0.14648
2370.0156 | 122.7768 | -122.5113 | 0.09613 | -0.0085447 | 0.013052 | 0.0052935 | 0.0018351 | 0.051656 | 0.0012049 | -0.0039733 | -0.00083936 | 0.0027002 | -0.031417 | 0.040716 | 0.0072437 | 0.0058468 | 0.022888 | -0.018311 | -0.009155 | 0.07782 | 0.17395 | 0.027466 | -0.10529 | -0.018311 | -0.013733 | -0.11902 | 0.068665 | 0.07782 | 0.045776 | -0.041199 | 122.5388 | 122.406 | 0.07782 | 122.493 | 122.5891 | 0.18311 | -0.073242 | 122.5571 | 122.4701 | -0.027465 | 122.493 | 122.3923 | -0.07782 | -0.01831 | 122.6852 | 122.5342 | 122.5021 | -0.20142 | 122.58 | 122.5891 | 122.4976 | -0.13733
2371.7656 | 122.6624 | -122.5067 | 0.13275 | -0.0085447 | 0.010489 | 0.0012347 | 0.0046121 | 0.050588 | -0.0064855 | -0.0041869 | -0.00083936 | -0.0017858 | -0.030563 | 0.040503 | 0.0010487 | 0.0075558 | 0.11902 | 0.10986 | 0.14191 | 0.15106 | 0.11444 | 0.073242 | -0.07782 | 0.054932 | 0.10529 | 0 | 0.027466 | 0.022888 | 0.050354 | -0.022888 | 122.58 | 122.4289 | -0.01831 | 122.6166 | 122.6578 | 0.22888 | -0.013732 | 122.5571 | 122.4838 | -0.10529 | 122.5616 | 122.5067 | 0.022888 | -0.10986 | 122.6212 | 122.6257 | 122.6486 | -0.21057 | 122.5342 | 122.5296 | 122.612 | -0.15564
2373.5156 | 122.6532 | -122.5067 | 0.12817 | 0.0067138 | 0.011984 | 0.0052935 | 0.0050393 | 0.050802 | -0.0049903 | -0.0048279 | 0.0067901 | -0.0013586 | -0.031417 | 0.03858 | 0.0040395 | 0.0058468 | 0.09613 | 0.11444 | 0.1236 | 0.12817 | 0.10986 | 0.054932 | -0.045776 | 0.045776 | 0.086975 | -0.032043 | 0.032043 | 0.036621 | 0.059509 | -0.013733 | 122.5616 | 122.4609 | -0.018311 | 122.6212 | 122.6349 | 0.17395 | -0.032044 | 122.5662 | 122.493 | -0.096131 | 122.5525 | 122.4747 | -0.01831 | -0.091553 | 122.6166 | 122.6028 | 122.6303 | -0.17395 | 122.5388 | 122.5433 | 122.5937 | -0.14191
2375.2188 | 122.7539 | -122.5021 | 0.11444 | -0.00091566 | 0.016898 | 0.0042255 | 0.0052531 | 0.05422 | 0.00099129 | -0.0044007 | -0.00083936 | 0.0029138 | -0.03099 | 0.043707 | 0.0066029 | 0.0062742 | 0.041199 | -0.041199 | -0.009155 | 0.091553 | 0.15564 | 0.022888 | -0.09613 | 0 | -0.018311 | -0.13275 | 0.050354 | 0.054932 | 0.045776 | -0.050354 | 122.525 | 122.406 | 0.041199 | 122.4609 | 122.5937 | 0.18768 | -0.073242 | 122.5479 | 122.4518 | -0.064087 | 122.5021 | 122.3694 | -0.082397 | -0.059509 | 122.6578 | 122.5433 | 122.493 | -0.21057 | 122.5525 | 122.5571 | 122.4838 | -0.16479
2376.9688 | 122.7859 | -122.4747 | 0.09613 | 0.0067138 | 0.014121 | 0.0037983 | 0.00098046 | 0.052724 | -0.0037085 | -0.0046143 | -0.00083936 | 0.000564 | -0.031631 | 0.039435 | 0.0063893 | 0.0062742 | 0.10529 | 0.12817 | 0.13733 | 0.16479 | 0.1236 | 0.059509 | -0.050354 | 0.091553 | 0.12817 | -0.004578 | 0.022888 | 0.032043 | 0.064087 | -0.022888 | 122.5342 | 122.4243 | 0.027466 | 122.6028 | 122.6395 | 0.21515 | 0.009156 | 122.5388 | 122.4518 | -0.073242 | 122.5662 | 122.4701 | 0.01831 | -0.064087 | 122.5983 | 122.58 | 122.612 | -0.14648 | 122.4976 | 122.5067 | 122.6028 | -0.11902
2378.6562 | 122.6669 | -122.5525 | 0.12817 | -0.00091566 | 0.01113 | 0.0067889 | 0.0037577 | 0.052511 | -0.0043493 | -0.0037597 | -0.0084684 | -7.6996e-05 | -0.031417 | 0.039648 | 0.0038259 | 0.0077694 | 0.07782 | 0.11902 | 0.10529 | 0.12817 | 0.13275 | 0.059509 | -0.064087 | 0.036621 | 0.082397 | -0.009155 | 0.027466 | 0.045776 | 0.064087 | -0.032043 | 122.612 | 122.4884 | 0.004577 | 122.6715 | 122.6807 | 0.19226 | -0.050354 | 122.6166 | 122.5204 | -0.10071 | 122.5891 | 122.5433 | 0.022888 | -0.082398 | 122.6852 | 122.6303 | 122.6578 | -0.19226 | 122.58 | 122.5983 | 122.6349 | -0.16022
2380.4062 | 122.731 | -122.5159 | 0.10071 | -0.00091566 | 0.011343 | 0.0048663 | 0.0056803 | 0.053365 | -0.0052039 | -0.0041869 | -0.00083936 | -0.0019996 | -0.031417 | 0.041785 | 0.0021169 | 0.0049924 | 0.09613 | 0.1236 | 0.12817 | 0.16479 | 0.14191 | 0.068665 | -0.064087 | 0.059509 | 0.14648 | 0.032043 | 0.013733 | 0.045776 | 0.064087 | -0.013733 | 122.5845 | 122.4518 | 0.041199 | 122.6395 | 122.6807 | 0.22888 | -0.004578 | 122.58 | 122.5021 | -0.086975 | 122.5754 | 122.5479 | 0.045776 | -0.054932 | 122.6578 | 122.612 | 122.644 | -0.1648 | 122.5296 | 122.5616 | 122.6624 | -0.11444
2382.1562 | 122.6852 | -122.5067 | 0.13733 | -0.0085447 | 0.013693 | 0.0044391 | 0.0073893 | 0.055288 | -0.0045629 | -0.0054687 | -0.00083936 | 0.0001368 | -0.031845 | 0.037726 | 0.00062147 | 0.0073422 | 0.13733 | 0.15106 | 0.16479 | 0.17395 | 0.12817 | 0.054932 | -0.07782 | 0.091553 | 0.16937 | 0.022888 | 0.027466 | 0.036621 | 0.064087 | -0.022888 | 122.5616 | 122.4289 | -0.009155 | 122.6578 | 122.6807 | 0.25177 | 0 | 122.5708 | 122.4838 | -0.10986 | 122.5983 | 122.5296 | 0.045776 | -0.10071 | 122.6349 | 122.644 | 122.6715 | -0.21515 | 122.5342 | 122.5433 | 122.6761 | -0.16022
2383.9219 | 122.7768 | -122.5113 | 0.10071 | -0.00091566 | 0.017538 | 0.0023029 | 0.0052531 | 0.055288 | 0.00077749 | -0.0033325 | -0.00083936 | 0.001632 | -0.029708 | 0.039862 | 0.0059621 | 0.0043516 | 0.14648 | 0.10986 | 0.1236 | 0.16479 | 0.1236 | 0.054932 | -0.064087 | 0.10986 | 0.11444 | 0.004578 | 0.009155 | 0.022888 | 0.050354 | 0.004578 | 122.5662 | 122.4472 | 0.022888 | 122.6212 | 122.6761 | 0.22888 | 0.045776 | 122.5616 | 122.5159 | -0.091553 | 122.6212 | 122.5159 | 0 | -0.07782 | 122.6349 | 122.6578 | 122.6349 | -0.1648 | 122.5204 | 122.5342 | 122.6257 | -0.09613
2385.6094 | 122.7036 | -122.5479 | 0.13275 | 0.0067138 | 0.0074982 | 0.0044391 | 0.0037577 | 0.054647 | -0.0062719 | -0.0035461 | -0.016098 | -7.6996e-05 | -0.032486 | 0.042212 | 0.0029713 | 0.0062742 | 0.073242 | 0.073242 | 0.10071 | 0.12817 | 0.13733 | 0.045776 | -0.054932 | 0.022888 | 0.082397 | -0.036621 | 0.045776 | 0.059509 | 0.032043 | -0.027466 | 122.5937 | 122.493 | 0.004578 | 122.6212 | 122.6761 | 0.18311 | -0.059509 | 122.58 | 122.5204 | -0.086975 | 122.5708 | 122.5113 | -0.009155 | -0.073242 | 122.6852 | 122.6212 | 122.6486 | -0.18768 | 122.5937 | 122.6074 | 122.6303 | -0.16022
2387.4062 | 122.7722 | -122.5067 | 0.10529 | -0.00091566 | 0.014975 | 0.0048663 | 0.0069621 | 0.054433 | 0.0016321 | -0.0056823 | -0.00083936 | 0.0031274 | -0.03099 | 0.04328 | 0.0040395 | 0.0045652 | 0.045776 | -0.004578 | 0 | 0.09613 | 0.16022 | 0.032043 | -0.10986 | -0.009155 | 0.027466 | -0.10071 | 0.050354 | 0.091553 | 0.022888 | -0.032043 | 122.5388 | 122.3969 | 0.054931 | 122.5021 | 122.6028 | 0.20599 | -0.05951 | 122.5296 | 122.4747 | -0.054932 | 122.4976 | 122.406 | -0.068665 | -0.013733 | 122.6669 | 122.5525 | 122.5067 | -0.21515 | 122.5571 | 122.5983 | 122.5342 | -0.13733
2389.1094 | 122.7814 | -122.5113 | 0.10071 | -0.016174 | 0.016043 | 0.0025165 | 0.0031167 | 0.054006 | 0.0018457 | -0.0031189 | -0.0084684 | 0.0014184 | -0.028854 | 0.041571 | 0.0074575 | 0.0058468 | 0.041199 | -0.022888 | 0 | 0.09613 | 0.16937 | 0.036621 | -0.091553 | -0.009155 | -0.027466 | -0.13275 | 0.064087 | 0.086975 | 0.022888 | -0.073242 | 122.5479 | 122.4197 | 0.068665 | 122.4884 | 122.6074 | 0.18768 | -0.059509 | 122.5342 | 122.4381 | -0.036621 | 122.5021 | 122.3785 | -0.059509 | -0.013733 | 122.6807 | 122.5525 | 122.5113 | -0.19226 | 122.5754 | 122.5983 | 122.4838 | -0.17395
2390.875 | 122.7676 | -122.5296 | 0.09613 | -0.0085447 | 0.016043 | 0.00038029 | 0.0029031 | 0.056569 | 0.00099129 | -0.0031189 | -0.0084684 | 0.0007776 | -0.030777 | 0.04563 | 0.0063893 | 0.0060604 | 0.068665 | 0.041199 | 0.045776 | 0.11444 | 0.15564 | 0.041199 | -0.10071 | 0.022888 | 0.045776 | -0.10071 | 0.073242 | 0.054932 | 0.036621 | -0.050354 | 122.5708 | 122.4289 | 0.05951 | 122.5708 | 122.644 | 0.21515 | -0.027465 | 122.5662 | 122.4792 | -0.022888 | 122.5525 | 122.4289 | -0.050354 | -0.041198 | 122.6852 | 122.5983 | 122.5754 | -0.19684 | 122.6028 | 122.5845 | 122.5754 | -0.14648
2392.6406 | 122.8134 | -122.5204 | 0.10071 | -0.00091566 | 0.013052 | 0.0025165 | 0.0031167 | 0.055715 | -0.0049903 | -0.00034172 | -0.00083936 | 0.0003504 | -0.032913 | 0.039648 | 0.0068165 | 0.0090512 | 0.11444 | 0.10986 | 0.12817 | 0.16479 | 0.11444 | 0.07782 | -0.050354 | 0.10529 | 0.12817 | 0.018311 | 0.018311 | 0.022888 | 0.064087 | -0.018311 | 122.5983 | 122.4701 | 0.013733 | 122.6303 | 122.6852 | 0.21515 | 0.013733 | 122.5845 | 122.5021 | -0.082397 | 122.6257 | 122.5388 | 0.036622 | -0.07782 | 122.6349 | 122.6349 | 122.6486 | -0.15106 | 122.5388 | 122.5433 | 122.6486 | -0.11902
2394.4062 | 122.6578 | -122.5296 | 0.11444 | -0.0085447 | 0.01583 | 0.0048663 | 0.0086709 | 0.05486 | -0.0064855 | -0.0048279 | 0.0067901 | 0.0001368 | -0.031845 | 0.039221 | 0.0010487 | 0.0062742 | 0.10986 | 0.14648 | 0.13733 | 0.16479 | 0.12817 | 0.041199 | -0.068665 | 0.032043 | 0.14191 | -0.013733 | 0.050354 | 0.054932 | 0.045776 | -0.032043 | 122.5708 | 122.4609 | 0.013733 | 122.6761 | 122.6944 | 0.23346 | -0.004578 | 122.5754 | 122.4976 | -0.064087 | 122.5616 | 122.5159 | 0.01831 | -0.059509 | 122.6578 | 122.6395 | 122.6669 | -0.18311 | 122.58 | 122.5845 | 122.6715 | -0.14648
2396.1094 | 122.6898 | -122.5616 | 0.11902 | -0.0085447 | 0.011984 | 0.0031573 | 0.0039713 | 0.055288 | -0.0062719 | -0.0041869 | -0.0084684 | -0.0007178 | -0.03099 | 0.039007 | 0.0036123 | 0.0084104 | 0.13275 | 0.11444 | 0.13275 | 0.15564 | 0.10529 | 0.07782 | -0.059509 | 0.059509 | 0.11444 | 0.013733 | 0.027466 | 0.045776 | 0.059509 | -0.022888 | 122.6395 | 122.5021 | -0.013733 | 122.6761 | 122.7173 | 0.21515 | 0.013732 | 122.6212 | 122.5388 | -0.091553 | 122.6212 | 122.5754 | 0.036621 | -0.073243 | 122.6669 | 122.6944 | 122.6944 | -0.17853 | 122.5891 | 122.6074 | 122.6761 | -0.14191
2397.875 | 122.7859 | -122.5159 | 0.10529 | -0.00091566 | 0.016257 | 0.0061481 | 0.0065347 | 0.05422 | -0.0013587 | -0.0056823 | -0.00083936 | 0.0020594 | -0.030349 | 0.041785 | 0.0059621 | 0.0043516 | 0.027466 | 0.013733 | 0.013733 | 0.10071 | 0.16479 | 0.018311 | -0.10071 | -0.027466 | 0.036621 | -0.10986 | 0.068665 | 0.068665 | 0.022888 | -0.064087 | 122.5342 | 122.4152 | 0.059509 | 122.5296 | 122.6166 | 0.20142 | -0.07782 | 122.5388 | 122.4518 | -0.036621 | 122.4884 | 122.406 | -0.045776 | -0.036621 | 122.6807 | 122.5433 | 122.5296 | -0.20599 | 122.5845 | 122.5845 | 122.5525 | -0.16937
2399.5781 | 122.7356 | -122.5388 | 0.11444 | 0.0067138 | 0.013907 | 0.0050799 | 0.0054667 | 0.052511 | -0.0066993 | -0.0039733 | -0.00083936 | -0.0017858 | -0.02864 | 0.041357 | 0.00019427 | 0.005206 | 0.09613 | 0.11444 | 0.13733 | 0.16022 | 0.15106 | 0.064087 | -0.073242 | 0.068665 | 0.16022 | 0.032043 | 0.027466 | 0.050354 | 0.041199 | -0.022888 | 122.6028 | 122.4655 | 0.036621 | 122.6532 | 122.699 | 0.23346 | -0.018311 | 122.58 | 122.5159 | -0.086975 | 122.6074 | 122.5708 | 0.054931 | -0.064087 | 122.6898 | 122.6349 | 122.6761 | -0.18768 | 122.5662 | 122.5891 | 122.699 | -0.13733
2401.3438 | 122.8226 | -122.5067 | 0.091553 | -0.0085447 | 0.019034 | 0.0044391 | 0.0056803 | 0.052297 | 0.00056389 | -0.0031189 | -0.00083936 | 0.002273 | -0.028427 | 0.042425 | 0.0048939 | 0.0026426 | 0.054932 | 0.032043 | 0.018311 | 0.11902 | 0.16022 | 0.032043 | -0.07782 | 0.027466 | 0.082397 | -0.07782 | 0.073242 | 0.059509 | 0.045776 | -0.059509 | 122.5388 | 122.4289 | 0.068664 | 122.5388 | 122.6257 | 0.19684 | -0.036621 | 122.5525 | 122.4472 | -0.018311 | 122.5342 | 122.4289 | -0.018311 | -0.032044 | 122.6669 | 122.5616 | 122.525 | -0.16937 | 122.58 | 122.5662 | 122.5891 | -0.15106
2403.0938 | 122.7997 | -122.5296 | 0.10071 | 0.0067138 | 0.016257 | 0.0027301 | 0.0016215 | 0.05486 | 0.0016321 | 0.00072628 | -0.0084684 | 0.0024866 | -0.029922 | 0.042212 | 0.0074575 | 0.0039242 | 0.027466 | -0.018311 | 0.009155 | 0.09613 | 0.15106 | 0.018311 | -0.09613 | -0.022888 | -0.009155 | -0.13275 | 0.050354 | 0.064087 | 0.027466 | -0.059509 | 122.5479 | 122.4335 | 0.050354 | 122.5113 | 122.6257 | 0.19226 | -0.073242 | 122.5571 | 122.4701 | -0.050354 | 122.5067 | 122.3969 | -0.073242 | -0.036621 | 122.6807 | 122.5571 | 122.5388 | -0.19684 | 122.58 | 122.5937 | 122.5204 | -0.16022
2404.9531 | 122.7539 | -122.5616 | 0.11902 | -0.0085447 | 0.012839 | 0.0037983 | 0.0031167 | 0.053579 | -0.0086219 | -0.0048279 | -0.0084684 | -0.0009314 | -0.029495 | 0.038794 | 0.00040787 | 0.006915 | 0.041199 | 0.12817 | 0.11444 | 0.13733 | 0.12817 | 0.068665 | -0.064087 | 0.036621 | 0.12817 | 0.018311 | 0.041199 | 0.041199 | 0.064087 | -0.022888 | 122.6303 | 122.4976 | 0.009155 | 122.6898 | 122.699 | 0.20142 | -0.07782 | 122.6257 | 122.5388 | -0.07782 | 122.5983 | 122.58 | 0.041199 | -0.07782 | 122.6898 | 122.6028 | 122.6761 | -0.18311 | 122.6028 | 122.6028 | 122.6898 | -0.14191
2407.1719 | 122.8134 | -122.525 | 0.091553 | 0.0067138 | 0.014334 | 0.0027301 | 0.0043985 | 0.057638 | -0.00071771 | -0.0044007 | -0.0084684 | 0.0020594 | -0.029495 | 0.039648 | 0.0061757 | 0.0041378 | 0.036621 | 0.013733 | 0.027466 | 0.11444 | 0.16479 | 0.013733 | -0.10529 | -0.009155 | 0.050354 | -0.10529 | 0.064087 | 0.07782 | 0.045776 | -0.041199 | 122.5388 | 122.4197 | 0.073242 | 122.5388 | 122.6395 | 0.21973 | -0.054932 | 122.5708 | 122.4838 | -0.027466 | 122.5159 | 122.4197 | -0.064087 | -0.013733 | 122.6898 | 122.5616 | 122.5525 | -0.19684 | 122.5891 | 122.6028 | 122.5754 | -0.13275
2409.8125 | 122.8592 | -122.5067 | 0.11444 | -0.0085447 | 0.01348 | 0.0037983 | 0.0016215 | 0.053579 | -0.0013587 | -0.0018371 | 0.0067901 | 0.001632 | -0.02864 | 0.043494 | 0.0057485 | 0.0049924 | 0.050354 | 0.018311 | 0.036621 | 0.091553 | 0.16937 | 0.027466 | -0.082397 | 0.032043 | 0.064087 | -0.059509 | 0.036621 | 0.032043 | 0.045776 | -0.027466 | 122.5342 | 122.4243 | 0.054932 | 122.525 | 122.5983 | 0.17395 | -0.064087 | 122.5525 | 122.4792 | -0.07782 | 122.5388 | 122.4472 | -0.032043 | -0.082398 | 122.6761 | 122.5571 | 122.5433 | -0.19684 | 122.5433 | 122.5388 | 122.5708 | -0.14191
2412.8906 | 122.7585 | -122.5662 | 0.11444 | 0.0067138 | 0.0074982 | 0.0048663 | 0.0033305 | 0.053152 | -0.0069129 | -0.0037597 | -0.0084684 | -0.0034948 | -0.033767 | 0.041144 | 0.0021169 | 0.0090512 | 0.09613 | 0.15564 | 0.16937 | 0.15106 | 0.13275 | 0.07782 | -0.059509 | 0.068665 | 0.17853 | 0.054932 | 0.013733 | 0.045776 | 0.041199 | -0.022888 | 122.644 | 122.5067 | 0.01831 | 122.7219 | 122.7173 | 0.21057 | -0.018311 | 122.6074 | 122.5433 | -0.10071 | 122.6349 | 122.6212 | 0.07782 | -0.068665 | 122.699 | 122.6624 | 122.7356 | -0.17395 | 122.58 | 122.612 | 122.7448 | -0.13733
2414.6875 | 122.7173 | -122.5708 | 0.13275 | -0.00091566 | 0.011343 | 0.0059345 | 0.0041849 | 0.05486 | -0.0013587 | -0.0046143 | -0.00083936 | -7.6996e-05 | -0.033126 | 0.042212 | 0.0044667 | 0.006915 | 0.009155 | 0.027466 | 0.036621 | 0.082397 | 0.16022 | 0.022888 | -0.11902 | -0.036621 | 0.050354 | -0.10071 | 0.064087 | 0.068665 | 0.027466 | -0.036621 | 122.5937 | 122.4518 | 0.027466 | 122.5983 | 122.6532 | 0.20142 | -0.1236 | 122.5983 | 122.5342 | -0.068664 | 122.5342 | 122.4701 | -0.064087 | -0.064086 | 122.731 | 122.58 | 122.6074 | -0.25177 | 122.6349 | 122.6395 | 122.6212 | -0.16937
2416.4844 | 122.731 | -122.5708 | 0.11902 | -0.00091566 | 0.014548 | 0.0014483 | 0.0076029 | 0.053152 | -0.0032813 | -0.0037597 | 0.01442 | 0.0018456 | -0.030777 | 0.042425 | 0.0033985 | 0.005206 | 0.032043 | 0.013733 | 0.018311 | 0.086975 | 0.17395 | 0.022888 | -0.1236 | -0.059509 | 0.022888 | -0.09613 | 0.086975 | 0.091553 | 0.032043 | -0.059509 | 122.5937 | 122.4472 | 0.054931 | 122.5845 | 122.6578 | 0.21057 | -0.086976 | 122.6028 | 122.5113 | -0.032044 | 122.5113 | 122.4747 | -0.036621 | -0.027466 | 122.7448 | 122.6028 | 122.5891 | -0.24261 | 122.6578 | 122.6624 | 122.5937 | -0.17853
2418.25 | 122.7676 | -122.5571 | 0.11902 | -0.0085447 | 0.016684 | 0.0059345 | 0.0097391 | 0.050802 | -0.0052039 | -0.0061095 | -0.0084684 | -0.002854 | -0.030563 | 0.040503 | 0.0012623 | 0.0058468 | 0.054932 | 0.10071 | 0.10529 | 0.14648 | 0.16022 | 0.045776 | -0.064087 | 0.045776 | 0.12817 | 0.013733 | 0.032043 | 0.036621 | 0.059509 | -0.018311 | 122.6028 | 122.493 | 0.041198 | 122.6578 | 122.7036 | 0.21057 | -0.064087 | 122.6166 | 122.5388 | -0.086976 | 122.6028 | 122.5708 | 0.032044 | -0.082398 | 122.7173 | 122.612 | 122.6624 | -0.18311 | 122.5891 | 122.5937 | 122.6852 | -0.13733
2420.0312 | 122.7036 | -122.5708 | 0.13275 | -0.0085447 | 0.013907 | 0.0050799 | 0.0043985 | 0.053792 | -0.0045629 | -0.0050415 | -0.016098 | 0.0003504 | -0.030136 | 0.039648 | 0.0012623 | 0.0054196 | 0.09613 | 0.16022 | 0.15106 | 0.17395 | 0.10986 | 0.059509 | -0.054932 | 0.059509 | 0.16022 | 0.018311 | 0.022888 | 0.050354 | 0.064087 | -0.027466 | 122.6303 | 122.5159 | -0.022888 | 122.731 | 122.7448 | 0.22888 | -0.036621 | 122.6349 | 122.5433 | -0.10986 | 122.6303 | 122.5891 | 0.045777 | -0.082397 | 122.6807 | 122.6669 | 122.7219 | -0.18768 | 122.5937 | 122.6212 | 122.731 | -0.16022
2421.7188 | 122.699 | -122.5845 | 0.12817 | -0.016174 | 0.014975 | 0.0023029 | 0.0067483 | 0.055288 | -0.0013587 | -0.0031189 | -0.00083936 | -7.6996e-05 | -0.030136 | 0.038794 | 0.0051075 | 0.0054196 | 0.10986 | 0.12817 | 0.13733 | 0.17395 | 0.12817 | 0.050354 | -0.073242 | 0.059509 | 0.13275 | -0.009155 | 0.041199 | 0.059509 | 0.045776 | -0.032043 | 122.6349 | 122.5113 | 0 | 122.7127 | 122.7585 | 0.24719 | -0.018311 | 122.6303 | 122.5525 | -0.086975 | 122.644 | 122.5754 | 0.022888 | -0.068665 | 122.7127 | 122.6944 | 122.7219 | -0.20142 | 122.6257 | 122.644 | 122.7173 | -0.16022
2423.4688 | 122.731 | -122.5845 | 0.12817 | 0.0067138 | 0.0085664 | 0.0044391 | 0.0014079 | 0.053365 | -0.0019995 | -0.0033325 | 0.0067901 | -0.0009314 | -0.033554 | 0.039648 | 0.0053211 | 0.0071286 | 0.1236 | 0.13275 | 0.15564 | 0.16479 | 0.11902 | 0.059509 | -0.073242 | 0.07782 | 0.11444 | 0.004578 | 0.027466 | 0.041199 | 0.064087 | -0.004578 | 122.644 | 122.5113 | -0.009155 | 122.7173 | 122.7493 | 0.23804 | -0.004578 | 122.6486 | 122.58 | -0.10071 | 122.6624 | 122.5891 | 0.009156 | -0.086975 | 122.7036 | 122.7081 | 122.7402 | -0.20142 | 122.612 | 122.6257 | 122.699 | -0.13275
2425.25 | 122.8592 | -122.5433 | 0.086975 | -0.00091566 | 0.016684 | 0.0040119 | 0.00076686 | 0.053792 | -0.00071771 | -0.00012812 | 0.0067901 | 0.0014184 | -0.032058 | 0.04093 | 0.0095937 | 0.005206 | 0.068665 | 0.050354 | 0.064087 | 0.10071 | 0.14648 | 0.054932 | -0.082397 | 0.059509 | 0.064087 | -0.013733 | 0.036621 | 0.032043 | 0.054932 | -0.009155 | 122.5983 | 122.4609 | 0.059509 | 122.5937 | 122.644 | 0.18311 | -0.01831 | 122.5983 | 122.5342 | -0.050354 | 122.6028 | 122.5296 | -0.004578 | -0.054932 | 122.6898 | 122.612 | 122.6074 | -0.16937 | 122.58 | 122.5754 | 122.6074 | -0.09613
2427.0156 | 122.7951 | -122.5708 | 0.10986 | 0.0067138 | 0.01348 | 0.0035847 | 0.0035441 | 0.05422 | 0.0033411 | -0.0018371 | -0.00083936 | 0.0018456 | -0.030777 | 0.041571 | 0.0083119 | 0.0054196 | 0.036621 | 0.004578 | 0.013733 | 0.10529 | 0.15106 | 0.022888 | -0.10986 | -0.018311 | -0.009155 | -0.14648 | 0.09613 | 0.07782 | 0.032043 | -0.036621 | 122.5937 | 122.4609 | 0.041199 | 122.5754 | 122.6761 | 0.21515 | -0.073242 | 122.6028 | 122.5342 | -0.013733 | 122.5525 | 122.4243 | -0.10986 | -0.032043 | 122.7219 | 122.6074 | 122.5845 | -0.21973 | 122.6669 | 122.6486 | 122.5616 | -0.14648
2428.7031 | 122.8455 | -122.58 | 0.082397 | -0.016174 | 0.016684 | 0.0035847 | 0.0039713 | 0.052938 | -0.0011451 | -0.0020507 | 0.01442 | 0.00505 | -0.03099 | 0.042212 | 0.0046803 | 0.0073422 | 0.027466 | -0.018311 | -0.004578 | 0.07782 | 0.16479 | 0.036621 | -0.11444 | -0.027466 | -0.009155 | -0.13275 | 0.054932 | 0.086975 | 0.032043 | -0.041199 | 122.6166 | 122.4655 | 0.082398 | 122.5616 | 122.6578 | 0.19226 | -0.054931 | 122.612 | 122.5388 | -0.027465 | 122.5525 | 122.4472 | -0.091552 | 0.004578 | 122.7448 | 122.6074 | 122.5754 | -0.19684 | 122.6349 | 122.6669 | 122.5708 | -0.1236
2430.4531 | 122.7081 | -122.5891 | 0.14191 | -0.00091566 | 0.014121 | 0.0044391 | 0.0086709 | 0.055929 | -0.0073401 | -0.0033325 | -0.0084684 | -0.0024268 | -0.028 | 0.038153 | 0.0021169 | 0.0075558 | 0.091553 | 0.14191 | 0.15564 | 0.17853 | 0.13275 | 0.068665 | -0.068665 | 0.045776 | 0.16937 | 0.004578 | 0.032043 | 0.032043 | 0.064087 | -0.027466 | 122.6578 | 122.5204 | -0.009156 | 122.731 | 122.7676 | 0.24719 | -0.050354 | 122.6532 | 122.5616 | -0.10986 | 122.6349 | 122.5937 | 0.032044 | -0.10986 | 122.7219 | 122.6807 | 122.7448 | -0.21057 | 122.6212 | 122.6212 | 122.7585 | -0.16937
2432.2344 | 122.6944 | -122.6028 | 0.11444 | -0.0085447 | 0.015616 | 0.0042255 | 0.0086709 | 0.052083 | -0.0047765 | -0.0044007 | -0.00083936 | -0.0007178 | -0.028213 | 0.039648 | 0.0019033 | 0.0060604 | 0.082397 | 0.1236 | 0.1236 | 0.16022 | 0.10986 | 0.045776 | -0.064087 | 0.009155 | 0.091553 | -0.041199 | 0.059509 | 0.054932 | 0.045776 | -0.045776 | 122.6486 | 122.5388 | -0.004578 | 122.7264 | 122.7631 | 0.2243 | -0.032044 | 122.6486 | 122.5571 | -0.054932 | 122.612 | 122.5616 | 0.004577 | -0.059509 | 122.7127 | 122.6852 | 122.7264 | -0.17853 | 122.6624 | 122.6578 | 122.6944 | -0.16022
2434 | 122.7081 | -122.6028 | 0.11902 | 0.014343 | 0.016043 | 0.0035847 | 0.0082437 | 0.053152 | -0.0045629 | -0.0041869 | 0.0067901 | 0.002273 | -0.030563 | 0.041144 | -0.0013011 | 0.006915 | 0.11444 | 0.13733 | 0.14191 | 0.16937 | 0.12817 | 0.064087 | -0.064087 | 0.045776 | 0.15564 | -0.018311 | 0.041199 | 0.054932 | 0.036621 | -0.027466 | 122.6669 | 122.5388 | 0.009155 | 122.7402 | 122.7722 | 0.23346 | -0.004578 | 122.6395 | 122.5754 | -0.07782 | 122.6486 | 122.5845 | 0.009155 | -0.064087 | 122.731 | 122.7173 | 122.7448 | -0.18311 | 122.644 | 122.6578 | 122.7585 | -0.14649
2435.7031 | 122.7997 | -122.5983 | 0.10071 | -0.0085447 | 0.010916 | 0.0035847 | -8.7544e-05 | 0.055288 | -0.0011451 | -0.0037597 | -0.00083936 | -0.0002906 | -0.032699 | 0.039435 | 0.0046803 | 0.0062742 | 0.14191 | 0.12817 | 0.14191 | 0.17395 | 0.12817 | 0.086975 | -0.045776 | 0.086975 | 0.14648 | 0.018311 | 0.013733 | 0.022888 | 0.07782 | -0.013733 | 122.6852 | 122.5525 | 0.027466 | 122.7264 | 122.7722 | 0.21973 | 0.041199 | 122.6761 | 122.5845 | -0.086975 | 122.6852 | 122.6166 | 0.032044 | -0.07782 | 122.7264 | 122.7402 | 122.7402 | -0.14648 | 122.612 | 122.6212 | 122.7448 | -0.11444
2437.4688 | 122.8271 | -122.5754 | 0.073242 | -0.00091566 | 0.016898 | 0.0016619 | 0.0069621 | 0.052083 | 0.00099129 | -0.0035461 | 0.0067901 | 0.0031274 | -0.030349 | 0.043066 | 0.0048939 | 0.0030698 | 0.11444 | 0.050354 | 0.050354 | 0.11444 | 0.15106 | 0.027466 | -0.09613 | 0.027466 | 0.054932 | -0.091553 | 0.059509 | 0.073242 | 0.013733 | -0.050354 | 122.6028 | 122.4792 | 0.07782 | 122.6257 | 122.6898 | 0.21057 | 0.041199 | 122.5891 | 122.525 | -0.013733 | 122.6028 | 122.4838 | -0.041199 | 0 | 122.7264 | 122.6898 | 122.6257 | -0.16937 | 122.6349 | 122.6486 | 122.6303 | -0.1236
2439.2344 | 122.7585 | -122.6074 | 0.11902 | -0.0085447 | 0.015616 | 0.0059345 | 0.0093119 | 0.052511 | -0.0024267 | -0.0031189 | 0.0067901 | -0.0015722 | -0.03099 | 0.041571 | 0.0029713 | 0.0056332 | 0.022888 | 0.022888 | 0.032043 | 0.091553 | 0.16937 | 0.027466 | -0.10071 | -0.036621 | 0.041199 | -0.10071 | 0.073242 | 0.068665 | 0.009155 | -0.059509 | 122.6349 | 122.5067 | 0.050354 | 122.6303 | 122.699 | 0.19226 | -0.096131 | 122.6166 | 122.5479 | -0.045777 | 122.5708 | 122.5067 | -0.041199 | -0.050354 | 122.7768 | 122.6303 | 122.6395 | -0.21973 | 122.6807 | 122.6761 | 122.6486 | -0.17853
2440.9219 | 122.8729 | -122.5708 | 0.091553 | -0.00091566 | 0.013907 | 0.0033709 | 0.0033305 | 0.055501 | -0.0011451 | -0.0039733 | -0.00083936 | 0.0027002 | -0.030136 | 0.042639 | 0.0061757 | 0.005206 | 0.041199 | -0.009155 | -0.004578 | 0.082397 | 0.17395 | 0.050354 | -0.10529 | -0.004578 | -0.013733 | -0.11902 | 0.054932 | 0.054932 | 0.036621 | -0.032043 | 122.6212 | 122.4655 | 0.082397 | 122.5616 | 122.6532 | 0.18768 | -0.050354 | 122.6074 | 122.5388 | -0.036621 | 122.5662 | 122.4518 | -0.086976 | -0.036621 | 122.7448 | 122.612 | 122.5662 | -0.19684 | 122.6257 | 122.6257 | 122.5571 | -0.1236
2442.6719 | 122.7585 | -122.5891 | 0.1236 | -0.0085447 | 0.0096344 | 0.0061481 | 0.0033305 | 0.05486 | -0.0084081 | -0.0048279 | -0.0084684 | -0.0041358 | -0.032486 | 0.038153 | 0.0038259 | 0.0090512 | 0.032043 | 0.07782 | 0.086975 | 0.11902 | 0.13733 | 0.050354 | -0.07782 | 0.004578 | 0.091553 | -0.013733 | 0.032043 | 0.032043 | 0.064087 | -0.022888 | 122.6395 | 122.5113 | 0.013733 | 122.6669 | 122.7081 | 0.19684 | -0.091553 | 122.6532 | 122.5662 | -0.091553 | 122.5937 | 122.5754 | 0.009155 | -0.091553 | 122.7264 | 122.6212 | 122.6761 | -0.20142 | 122.6212 | 122.6212 | 122.6807 | -0.14648
2444.4531 | 122.8409 | -122.5845 | 0.10071 | 0.0067138 | 0.012412 | 0.0048663 | 0.0063211 | 0.054647 | -0.0034949 | -0.0044007 | -0.0084684 | 0.0009912 | -0.031417 | 0.04093 | 0.0055349 | 0.0060604 | 0.12817 | 0.1236 | 0.14648 | 0.16479 | 0.11444 | 0.064087 | -0.059509 | 0.09613 | 0.1236 | 0.004578 | 0.018311 | 0.032043 | 0.064087 | -0.013733 | 122.6486 | 122.525 | 0.013733 | 122.7081 | 122.7493 | 0.2243 | 0.027466 | 122.6486 | 122.5708 | -0.082397 | 122.6807 | 122.5891 | 0.018311 | -0.068665 | 122.699 | 122.7127 | 122.731 | -0.16022 | 122.6028 | 122.6166 | 122.7081 | -0.11444
2446.2344 | 122.8134 | -122.5937 | 0.091553 | 0.0067138 | 0.01583 | 0.0042255 | 0.0033305 | 0.052724 | 0.0018457 | -0.0029053 | -0.00083936 | 0.0020594 | -0.029495 | 0.039435 | 0.0080983 | 0.003497 | 0.018311 | 0 | 0.009155 | 0.086975 | 0.16479 | 0.022888 | -0.11902 | -0.013733 | -0.009155 | -0.12817 | 0.082397 | 0.073242 | 0.022888 | -0.050354 | 122.6166 | 122.4747 | 0.073242 | 122.5937 | 122.6807 | 0.20599 | -0.073242 | 122.6166 | 122.5433 | -0.009156 | 122.58 | 122.4655 | -0.07782 | -0.018311 | 122.7585 | 122.612 | 122.6028 | -0.21057 | 122.6761 | 122.6669 | 122.5845 | -0.14191
2447.9375 | 122.7997 | -122.5937 | 0.11444 | -0.00091566 | 0.013907 | 0.0078571 | 0.0069621 | 0.053365 | -0.0088355 | -0.0058959 | -0.0084684 | -0.0039222 | -0.03099 | 0.039648 | 0.00083507 | 0.007983 | 0.07782 | 0.13275 | 0.14191 | 0.15564 | 0.13733 | 0.068665 | -0.082397 | 0.059509 | 0.15564 | 0.027466 | 0.018311 | 0.045776 | 0.050354 | -0.032043 | 122.6624 | 122.5113 | 0.022888 | 122.7264 | 122.7493 | 0.23804 | -0.036621 | 122.644 | 122.5616 | -0.09613 | 122.6532 | 122.6212 | 0.059509 | -0.068665 | 122.731 | 122.6715 | 122.7356 | -0.19684 | 122.612 | 122.6395 | 122.7493 | -0.14648
2449.625 | 122.818 | -122.5754 | 0.10529 | -0.016174 | 0.011557 | 0.0061481 | 0.0052531 | 0.05486 | -7.6908e-05 | -0.0031189 | -0.016098 | 0.001632 | -0.032058 | 0.041785 | 0.0046803 | 0.0058468 | 0.041199 | 0 | 0.018311 | 0.086975 | 0.17853 | 0.027466 | -0.10529 | -0.045776 | 0.018311 | -0.1236 | 0.082397 | 0.082397 | 0.027466 | -0.059509 | 122.6028 | 122.4701 | 0.073242 | 122.5754 | 122.6624 | 0.19226 | -0.064087 | 122.6028 | 122.5159 | -0.022889 | 122.5296 | 122.4518 | -0.064087 | -0.022889 | 122.7539 | 122.6166 | 122.5937 | -0.21057 | 122.6578 | 122.6578 | 122.5937 | -0.16479
2451.3906 | 122.8592 | -122.5845 | 0.10986 | -0.0085447 | 0.014121 | 0.0061481 | 0.0022623 | 0.050802 | -0.0030677 | -0.0026917 | -0.016098 | -0.0005042 | -0.032699 | 0.039862 | 0.0048939 | 0.0047788 | 0.1236 | 0.12817 | 0.14191 | 0.17853 | 0.11444 | 0.07782 | -0.045776 | 0.10529 | 0.14648 | 0.009155 | 0.018311 | 0.018311 | 0.059509 | -0.018311 | 122.6624 | 122.5388 | 0.004578 | 122.7127 | 122.7631 | 0.2243 | 0.013733 | 122.644 | 122.5662 | -0.091552 | 122.6898 | 122.5937 | 0.027466 | -0.091552 | 122.699 | 122.7081 | 122.7264 | -0.15564 | 122.6028 | 122.6028 | 122.731 | -0.12817
2453.1562 | 122.8363 | -122.6074 | 0.10529 | -0.00091566 | 0.017538 | 0.0046527 | 0.0039713 | 0.05486 | -0.00050411 | -0.0022643 | 0.0067901 | 0.0027002 | -0.029495 | 0.039648 | 0.0063893 | 0.0045652 | 0.07782 | 0.045776 | 0.064087 | 0.15106 | 0.15564 | 0.045776 | -0.09613 | 0.018311 | 0.045776 | -0.09613 | 0.068665 | 0.054932 | 0.036621 | -0.027466 | 122.6532 | 122.5113 | 0.050354 | 122.6532 | 122.7585 | 0.24719 | -0.027466 | 122.644 | 122.58 | -0.036621 | 122.6257 | 122.5113 | -0.068664 | -0.050354 | 122.7631 | 122.6852 | 122.6715 | -0.20142 | 122.6761 | 122.6624 | 122.6532 | -0.13275
2454.8438 | 122.8409 | -122.5754 | 0.10071 | -0.00091566 | 0.018179 | 0.0035847 | 0.0041849 | 0.05187 | -0.00029051 | -0.0050415 | 0.0067901 | 0.002273 | -0.029495 | 0.041571 | 0.0048939 | 0.006915 | 0.032043 | -0.004578 | 0.013733 | 0.082397 | 0.16022 | 0.036621 | -0.07782 | -0.041199 | 0 | -0.13733 | 0.064087 | 0.07782 | 0.018311 | -0.050354 | 122.612 | 122.4976 | 0.059509 | 122.5708 | 122.6578 | 0.16022 | -0.068665 | 122.5937 | 122.525 | -0.036621 | 122.5342 | 122.438 | -0.086975 | -0.022888 | 122.7356 | 122.6074 | 122.5891 | -0.17853 | 122.6395 | 122.6532 | 122.5754 | -0.15106
2456.5469 | 122.8455 | -122.5845 | 0.10071 | -0.016174 | 0.015402 | 0.0063617 | 0.0088847 | 0.053792 | -0.0047765 | -0.0020507 | -0.00083936 | 0.0003504 | -0.031845 | 0.041785 | 0.0048939 | 0.0067014 | 0.022888 | 0.004578 | 0.009155 | 0.082397 | 0.16022 | 0.013733 | -0.10986 | -0.036621 | 0.027466 | -0.10986 | 0.064087 | 0.09613 | 0 | -0.045776 | 122.5983 | 122.4747 | 0.059509 | 122.5891 | 122.6669 | 0.19226 | -0.07782 | 122.5845 | 122.5388 | -0.036621 | 122.5479 | 122.4747 | -0.064087 | -0.004578 | 122.7448 | 122.6074 | 122.5937 | -0.21057 | 122.6486 | 122.6807 | 122.612 | -0.14648
2458.3125 | 122.7676 | -122.6303 | 0.10986 | -0.0085447 | 0.0085664 | 0.0063617 | 0.0035441 | 0.053579 | -0.0066993 | -0.0037597 | -0.016098 | -0.0030676 | -0.033554 | 0.040289 | 0.0014759 | 0.0084104 | 0.054932 | 0.086975 | 0.10071 | 0.13733 | 0.13275 | 0.064087 | -0.064087 | 0.009155 | 0.091553 | -0.022888 | 0.036621 | 0.054932 | 0.045776 | -0.027466 | 122.6944 | 122.5662 | 0.022888 | 122.7173 | 122.7676 | 0.20142 | -0.054931 | 122.6761 | 122.6028 | -0.073242 | 122.6395 | 122.6074 | 0.004578 | -0.054931 | 122.7631 | 122.6852 | 122.731 | -0.17395 | 122.6669 | 122.6852 | 122.7219 | -0.13733
2460 | 122.7585 | -122.612 | 0.1236 | -0.0085447 | 0.016257 | 0.0033709 | 0.0093119 | 0.053792 | -0.0015723 | -0.0039733 | -0.00083936 | 0.0018456 | -0.030349 | 0.041357 | 0.0033985 | 0.005206 | 0.018311 | 0.032043 | 0.022888 | 0.082397 | 0.16479 | 0.022888 | -0.10986 | -0.036621 | 0.022888 | -0.10986 | 0.064087 | 0.068665 | 0.027466 | -0.054932 | 122.6349 | 122.5021 | 0.041199 | 122.644 | 122.6944 | 0.19226 | -0.10528 | 122.6395 | 122.5571 | -0.059509 | 122.5754 | 122.5021 | -0.054931 | -0.054931 | 122.7768 | 122.6303 | 122.6349 | -0.23346 | 122.6761 | 122.6807 | 122.6349 | -0.17853
2461.6875 | 122.7493 | -122.612 | 0.11444 | -0.00091566 | 0.014334 | 0.0070025 | 0.0067483 | 0.053792 | -0.0037085 | -0.0044007 | 0.0067901 | -0.0007178 | -0.029708 | 0.040076 | 0.00040787 | 0.0060604 | 0.082397 | 0.12817 | 0.11902 | 0.15106 | 0.12817 | 0.054932 | -0.086975 | 0.004578 | 0.10529 | -0.054932 | 0.050354 | 0.064087 | 0.022888 | -0.041199 | 122.6669 | 122.525 | 0.013733 | 122.7402 | 122.7631 | 0.23804 | -0.032044 | 122.6349 | 122.5708 | -0.064087 | 122.6166 | 122.5571 | -0.013733 | -0.050354 | 122.7402 | 122.6944 | 122.731 | -0.20142 | 122.6624 | 122.6761 | 122.7173 | -0.15564
2463.4531 | 122.8088 | -122.6028 | 0.12817 | -0.0085447 | 0.014121 | 0.0065753 | 0.0069621 | 0.05422 | -0.0058447 | -0.0041869 | -0.00083936 | -0.0019996 | -0.032272 | 0.039648 | 0.0029713 | 0.0041378 | 0.032043 | 0.073242 | 0.10529 | 0.11902 | 0.13733 | 0.073242 | -0.059509 | 0.009155 | 0.091553 | 0 | 0.050354 | 0.045776 | 0.054932 | -0.032043 | 122.6761 | 122.5433 | 0.009155 | 122.6761 | 122.7219 | 0.17853 | -0.096131 | 122.6578 | 122.5708 | -0.07782 | 122.612 | 122.6028 | 0.032043 | -0.082398 | 122.7402 | 122.6349 | 122.7081 | -0.18768 | 122.6532 | 122.6486 | 122.6944 | -0.16022
2465.1719 | 122.7814 | -122.6303 | 0.13275 | 0.014343 | 0.011557 | 0.0055073 | 0.0058939 | 0.054647 | -0.0054175 | -0.0035461 | -0.00083936 | -0.0019996 | -0.030777 | 0.038794 | 0.0029713 | 0.005206 | 0.050354 | 0.073242 | 0.10986 | 0.11902 | 0.1236 | 0.059509 | -0.059509 | 0.022888 | 0.068665 | -0.018311 | 0.009155 | 0.054932 | 0.054932 | -0.036621 | 122.6898 | 122.5708 | -0.009155 | 122.7036 | 122.7493 | 0.17853 | -0.082397 | 122.6852 | 122.5937 | -0.1236 | 122.6532 | 122.612 | 0.01831 | -0.077819 | 122.7539 | 122.6807 | 122.7402 | -0.19226 | 122.6395 | 122.6852 | 122.699 | -0.16937
2466.9531 | 122.7585 | -122.6532 | 0.13733 | -0.00091566 | 0.0068574 | 0.0046527 | 0.0031167 | 0.053579 | -0.0039221 | -0.0044007 | 0.0067901 | -0.0013586 | -0.032058 | 0.040289 | 0.0046803 | 0.0058468 | 0.09613 | 0.14648 | 0.12817 | 0.14648 | 0.1236 | 0.064087 | -0.073242 | 0.050354 | 0.09613 | -0.013733 | 0.013733 | 0.018311 | 0.064087 | -0.027466 | 122.7173 | 122.58 | -0.013733 | 122.7997 | 122.7997 | 0.21973 | -0.041199 | 122.7173 | 122.6257 | -0.1236 | 122.7036 | 122.6395 | 0.013733 | -0.11902 | 122.7768 | 122.7493 | 122.7814 | -0.21057 | 122.6669 | 122.6715 | 122.7493 | -0.16479
2468.7031 | 122.8088 | -122.6212 | 0.11444 | -0.00091566 | 0.008139 | 0.0076435 | 0.0029031 | 0.055074 | -0.0045629 | -0.0056823 | -0.0084684 | -0.0005042 | -0.035049 | 0.038794 | 0.0053211 | 0.0032834 | 0.12817 | 0.19226 | 0.16479 | 0.17853 | 0.13275 | 0.059509 | -0.068665 | 0.07782 | 0.17395 | 0.032043 | 0.027466 | 0.027466 | 0.064087 | -0.018311 | 122.6807 | 122.5525 | 0.01831 | 122.8134 | 122.7997 | 0.24719 | 0.013733 | 122.6852 | 122.6028 | -0.086975 | 122.699 | 122.6532 | 0.050354 | -0.086975 | 122.7539 | 122.7493 | 122.7859 | -0.18311 | 122.6486 | 122.6486 | 122.7951 | -0.13275
2470.4844 | 122.8134 | -122.6212 | 0.11444 | -0.00091566 | 0.01647 | 0.0044391 | 0.0090983 | 0.05486 | 0.0012049 | -0.0033325 | -0.00083936 | 0.0024866 | -0.028 | 0.040289 | 0.0042531 | 0.0030698 | 0.032043 | 0.004578 | 0.018311 | 0.082397 | 0.16022 | 0.018311 | -0.10986 | -0.032043 | 0.009155 | -0.11902 | 0.073242 | 0.082397 | 0.036621 | -0.059509 | 122.6395 | 122.5113 | 0.045776 | 122.6257 | 122.7036 | 0.19226 | -0.082398 | 122.6578 | 122.5616 | -0.041199 | 122.5891 | 122.5021 | -0.05951 | -0.032044 | 122.7814 | 122.6532 | 122.6395 | -0.2243 | 122.6944 | 122.7036 | 122.6303 | -0.17395
2472.2656 | 122.818 | -122.6486 | 0.1236 | -0.00091566 | 0.014761 | 0.0044391 | 0.0058939 | 0.05422 | -0.0052039 | -0.0050415 | -0.0084684 | -0.0026404 | -0.031417 | 0.038794 | 0.0019033 | 0.0071286 | 0.036621 | 0.082397 | 0.09613 | 0.13275 | 0.12817 | 0.064087 | -0.082397 | 0.032043 | 0.10986 | -0.009155 | 0.045776 | 0.041199 | 0.050354 | -0.027466 | 122.7127 | 122.5662 | 0.004578 | 122.731 | 122.7814 | 0.21515 | -0.086975 | 122.699 | 122.6212 | -0.07782 | 122.6807 | 122.6395 | 0.018311 | -0.082397 | 122.7768 | 122.6852 | 122.7448 | -0.20599 | 122.6944 | 122.6898 | 122.7585 | -0.15106
2473.9688 | 122.8729 | -122.5983 | 0.09613 | -0.00091566 | 0.017538 | 0.0042255 | 0.0046121 | 0.05422 | 0.0018457 | -0.0020507 | -0.00083936 | 0.0031274 | -0.030349 | 0.040716 | 0.0074575 | 0.003497 | 0.09613 | 0.07782 | 0.068665 | 0.11444 | 0.16937 | 0.036621 | -0.09613 | 0.050354 | 0.050354 | -0.10529 | 0.068665 | 0.068665 | 0.027466 | -0.064087 | 122.6349 | 122.5021 | 0.073243 | 122.6761 | 122.7127 | 0.21057 | 0 | 122.6257 | 122.5342 | -0.027465 | 122.6486 | 122.493 | -0.041199 | -0.027465 | 122.7676 | 122.6944 | 122.6669 | -0.19226 | 122.6669 | 122.6669 | 122.6486 | -0.16022
2475.7188 | 122.7859 | -122.6624 | 0.1236 | -0.016174 | 0.0089936 | 0.0046527 | 0.0048257 | 0.051656 | -0.0060583 | -0.00055532 | 0.0067901 | -0.0017858 | -0.032913 | 0.037939 | 0.0059621 | 0.0062742 | 0.064087 | 0.082397 | 0.10529 | 0.12817 | 0.14191 | 0.068665 | -0.054932 | 0.032043 | 0.091553 | -0.018311 | 0.045776 | 0.036621 | 0.059509 | -0.027466 | 122.731 | 122.6074 | 0.018311 | 122.7448 | 122.7905 | 0.18311 | -0.059509 | 122.7219 | 122.6349 | -0.07782 | 122.6944 | 122.644 | 0.009155 | -0.086975 | 122.8043 | 122.7264 | 122.7676 | -0.17853 | 122.7081 | 122.699 | 122.7539 | -0.15106
2477.5 | 122.8134 | -122.6486 | 0.12817 | -0.016174 | 0.014548 | 0.0050799 | 0.0065347 | 0.053365 | -0.0017859 | -0.0011963 | -0.016098 | -0.0022132 | -0.031204 | 0.041357 | 0.0040395 | 0.0075558 | 0.13733 | 0.14648 | 0.15564 | 0.17395 | 0.11444 | 0.064087 | -0.041199 | 0.082397 | 0.12817 | 0.009155 | 0.022888 | 0.050354 | 0.054932 | -0.009155 | 122.7127 | 122.6074 | -0.013733 | 122.7951 | 122.8226 | 0.21515 | 0.009155 | 122.7036 | 122.6395 | -0.10529 | 122.731 | 122.6578 | 0.01831 | -0.07782 | 122.7631 | 122.7859 | 122.8043 | -0.16937 | 122.6715 | 122.699 | 122.7768 | -0.13733
2479.2031 | 122.8363 | -122.612 | 0.10529 | -0.0085447 | 0.016898 | 0.0050799 | 0.0069621 | 0.053792 | -0.00029051 | -0.0037597 | -0.016098 | 0.0035546 | -0.030777 | 0.038794 | 0.0051075 | 0.0056332 | 0.018311 | 0.022888 | 0.022888 | 0.082397 | 0.1831 | 0.032043 | -0.10529 | -0.036621 | 0.027466 | -0.11902 | 0.068665 | 0.086975 | 0.027466 | -0.041199 | 122.644 | 122.5067 | 0.077819 | 122.6349 | 122.6944 | 0.18768 | -0.086975 | 122.6395 | 122.5708 | -0.036621 | 122.5754 | 122.493 | -0.07782 | -0.018311 | 122.7951 | 122.6303 | 122.6349 | -0.21057 | 122.6807 | 122.699 | 122.6395 | -0.14649
2480.9844 | 122.7768 | -122.6807 | 0.1236 | -0.00091566 | 0.014761 | 0.0044391 | 0.0052531 | 0.05187 | -0.0030677 | -0.0024779 | -0.0084684 | -7.6996e-05 | -0.030349 | 0.041571 | 0.0019033 | 0.006915 | 0.12817 | 0.13275 | 0.14191 | 0.13733 | 0.13275 | 0.07782 | -0.068665 | 0.073242 | 0.10986 | 0.004578 | 0.013733 | 0.041199 | 0.086975 | -0.004578 | 122.7585 | 122.612 | 0.009155 | 122.8134 | 122.818 | 0.20599 | 0.004578 | 122.7676 | 122.6761 | -0.10986 | 122.7539 | 122.6852 | 0.009156 | -0.082397 | 122.8134 | 122.8088 | 122.8226 | -0.19226 | 122.6944 | 122.7219 | 122.7905 | -0.12817
2482.75 | 122.8683 | -122.6166 | 0.10986 | 0.0067138 | 0.01348 | 0.0037983 | 0.0024759 | 0.052511 | -0.00050411 | -0.0035461 | -0.00083936 | 0.0007776 | -0.032913 | 0.037939 | 0.0063893 | 0.006915 | 0.13275 | 0.14648 | 0.14648 | 0.16479 | 0.11444 | 0.07782 | -0.073242 | 0.091553 | 0.13733 | 0.009155 | 0 | 0.032043 | 0.068665 | -0.013733 | 122.6944 | 122.5433 | 0.004578 | 122.7631 | 122.7814 | 0.23804 | 0.022888 | 122.6852 | 122.6028 | -0.10986 | 122.7081 | 122.6257 | 0.022888 | -0.07782 | 122.731 | 122.7493 | 122.7631 | -0.18311 | 122.6166 | 122.6486 | 122.7539 | -0.1236
2484.5 | 122.9416 | -122.612 | 0.073242 | -0.00091566 | 0.017111 | 0.0046527 | 0.0039713 | 0.052297 | 0.00056389 | -0.0029053 | -0.00083936 | 0.0020594 | -0.03334 | 0.040289 | 0.0061757 | 0.005206 | 0.041199 | 0.013733 | 0.013733 | 0.07782 | 0.16937 | 0.041199 | -0.10986 | 0.022888 | 0.004578 | -0.091553 | 0.059509 | 0.041199 | 0.045776 | -0.059509 | 122.6532 | 122.5021 | 0.096131 | 122.6257 | 122.6898 | 0.18768 | -0.032043 | 122.6578 | 122.5525 | -0.013733 | 122.6349 | 122.5204 | -0.032044 | -0.032043 | 122.7814 | 122.6532 | 122.6257 | -0.18311 | 122.6715 | 122.6532 | 122.6166 | -0.13275
2486.2031 | 122.7814 | -122.644 | 0.11902 | -0.0085447 | 0.013693 | 0.0057209 | 0.0067483 | 0.054433 | -0.0022131 | -0.0016235 | 0.0067901 | 0.0001368 | -0.030777 | 0.039435 | 0.0046803 | 0.0064878 | 0.091553 | 0.1236 | 0.10986 | 0.15106 | 0.12817 | 0.050354 | -0.07782 | 0 | 0.10986 | -0.041199 | 0.050354 | 0.059509 | 0.045776 | -0.041199 | 122.6944 | 122.5662 | 0.009155 | 122.7676 | 122.7951 | 0.22888 | -0.027466 | 122.6898 | 122.6028 | -0.068665 | 122.644 | 122.6028 | 0 | -0.05951 | 122.7722 | 122.7356 | 122.7539 | -0.19684 | 122.6944 | 122.7036 | 122.7539 | -0.16022
2487.9688 | 122.905 | -122.6257 | 0.10071 | 0.0067138 | 0.015189 | 0.0040119 | 0.0031167 | 0.05422 | 0.00077749 | -0.00012812 | -0.0084684 | 0.0035546 | -0.028854 | 0.040503 | 0.0072437 | 0.005206 | 0.032043 | -0.018311 | 0.004578 | 0.082397 | 0.19684 | 0.036621 | -0.12817 | -0.018311 | -0.013733 | -0.13275 | 0.07782 | 0.07782 | 0.018311 | -0.054932 | 122.6624 | 122.4976 | 0.09613 | 122.6074 | 122.7081 | 0.21057 | -0.068665 | 122.644 | 122.5708 | -0.022888 | 122.6074 | 122.493 | -0.077819 | -0.022888 | 122.8226 | 122.6578 | 122.6303 | -0.22888 | 122.7036 | 122.7036 | 122.612 | -0.15564
2489.7188 | 122.8867 | -122.644 | 0.10071 | 0.0067138 | 0.017111 | 0.0031573 | 0.0048257 | 0.051443 | 0.0012049 | -0.0011963 | -0.00083936 | 0.0031274 | -0.02864 | 0.041357 | 0.0066029 | 0.0056332 | 0.018311 | -0.045776 | -0.009155 | 0.064087 | 0.16937 | 0.032043 | -0.1236 | -0.013733 | -0.004578 | -0.13733 | 0.064087 | 0.07782 | 0.022888 | -0.041199 | 122.6761 | 122.5204 | 0.068665 | 122.5983 | 122.7081 | 0.18768 | -0.082397 | 122.6669 | 122.6028 | -0.036621 | 122.6303 | 122.5067 | -0.09613 | -0.022888 | 122.8134 | 122.6624 | 122.6349 | -0.2243 | 122.7081 | 122.7219 | 122.6395 | -0.14191
2491.4844 | 122.7905 | -122.6486 | 0.13275 | -0.016174 | 0.017325 | 0.0063617 | 0.0080301 | 0.053365 | -0.0052039 | -0.0037597 | 0.0067901 | -0.0007178 | -0.02864 | 0.039862 | 0.0023305 | 0.0077694 | 0.068665 | 0.11444 | 0.11902 | 0.15106 | 0.14191 | 0.045776 | -0.091553 | -0.004578 | 0.07782 | -0.059509 | 0.050354 | 0.073242 | 0.041199 | -0.041199 | 122.6944 | 122.5571 | 0.009156 | 122.7631 | 122.7997 | 0.24261 | -0.064086 | 122.6898 | 122.6074 | -0.082397 | 122.644 | 122.5891 | -0.01831 | -0.059509 | 122.7905 | 122.7173 | 122.7676 | -0.2243 | 122.699 | 122.7219 | 122.7264 | -0.17395
2493.2656 | 122.8592 | -122.6578 | 0.09613 | -0.00091566 | 0.014334 | 0.0023029 | 0.0041849 | 0.054006 | -0.0037085 | -0.0026917 | 0.0067901 | -0.0017858 | -0.031204 | 0.038794 | 0.0027577 | 0.0056332 | 0.1236 | 0.12817 | 0.15564 | 0.16937 | 0.10986 | 0.068665 | -0.059509 | 0.091553 | 0.14191 | 0.013733 | 0.027466 | 0.032043 | 0.073242 | 0 | 122.7264 | 122.5983 | 0.013733 | 122.7859 | 122.8271 | 0.22888 | 0.027466 | 122.731 | 122.6578 | -0.068664 | 122.7493 | 122.6715 | 0.013733 | -0.064087 | 122.7676 | 122.7814 | 122.8134 | -0.15564 | 122.6852 | 122.6898 | 122.7997 | -0.09613
2494.9688 | 122.9324 | -122.5983 | 0.082397 | -0.00091566 | 0.015616 | 0.0042255 | 0.0035441 | 0.055288 | -7.6908e-05 | -0.0054687 | -0.0084684 | 0.001632 | -0.030563 | 0.041998 | 0.0076711 | 0.006915 | 0.032043 | -0.009155 | 0.009155 | 0.082397 | 0.16022 | 0.018311 | -0.13275 | 0.009155 | 0.013733 | -0.09613 | 0.054932 | 0.068665 | 0.045776 | -0.045776 | 122.6166 | 122.4655 | 0.07782 | 122.5891 | 122.6807 | 0.21515 | -0.050354 | 122.644 | 122.5525 | -0.027465 | 122.6074 | 122.5021 | -0.050354 | -0.013732 | 122.7585 | 122.6303 | 122.6074 | -0.21515 | 122.6532 | 122.6669 | 122.612 | -0.12817
2496.7188 | 122.8088 | -122.6761 | 0.10529 | -0.00091566 | 0.0085664 | 0.0080707 | 0.0043985 | 0.053365 | -0.0075537 | -0.0044007 | 0.0067901 | -0.0026404 | -0.031845 | 0.038153 | 0.0038259 | 0.0088376 | 0.073242 | 0.11444 | 0.10986 | 0.12817 | 0.12817 | 0.059509 | -0.050354 | 0.027466 | 0.091553 | -0.018311 | 0.032043 | 0.050354 | 0.045776 | -0.022888 | 122.7356 | 122.6257 | 0.022888 | 122.7905 | 122.8043 | 0.17853 | -0.032044 | 122.7219 | 122.6532 | -0.073243 | 122.7036 | 122.6578 | 0.004577 | -0.054932 | 122.8043 | 122.7493 | 122.7859 | -0.15564 | 122.7081 | 122.7264 | 122.7676 | -0.12817
2498.4219 | 122.9187 | -122.6166 | 0.091553 | -0.00091566 | 0.019247 | 0.0023029 | 0.0073893 | 0.054647 | 0.0024865 | -0.0033325 | -0.00083936 | 0.0020594 | -0.030777 | 0.039862 | 0.0046803 | 0.0039242 | 0.059509 | 0.064087 | 0.068665 | 0.13733 | 0.15564 | 0.041199 | -0.091553 | 0.032043 | 0.07782 | -0.059509 | 0.054932 | 0.054932 | 0.027466 | -0.059509 | 122.6578 | 122.525 | 0.064087 | 122.6807 | 122.7539 | 0.22888 | -0.032044 | 122.644 | 122.5571 | -0.036621 | 122.6486 | 122.5571 | 0 | -0.036621 | 122.7722 | 122.6761 | 122.6852 | -0.18311 | 122.6715 | 122.6715 | 122.6944 | -0.15106
2500.1875 | 122.7997 | -122.6578 | 0.12817 | -0.0085447 | 0.009848 | 0.0048663 | 0.0052531 | 0.055929 | -0.0094763 | -0.0029053 | -0.0084684 | -0.001145 | -0.030349 | 0.041357 | 0.0016895 | 0.0073422 | 0.045776 | 0.07782 | 0.10529 | 0.1236 | 0.13275 | 0.050354 | -0.068665 | 0.009155 | 0.068665 | -0.018311 | 0.036621 | 0.059509 | 0.054932 | -0.022888 | 122.7081 | 122.5891 | 0.004577 | 122.7356 | 122.7814 | 0.19226 | -0.082398 | 122.7127 | 122.6349 | -0.091553 | 122.6669 | 122.6395 | 0.004577 | -0.068665 | 122.7905 | 122.7036 | 122.7631 | -0.19684 | 122.6944 | 122.7173 | 122.7264 | -0.15106
2501.8906 | 122.9233 | -122.6212 | 0.068665 | -0.016174 | 0.016257 | 0.0025165 | 0.0016215 | 0.055929 | 0.00099129 | -0.0046143 | -0.00083936 | 0.0031274 | -0.03099 | 0.041144 | 0.0074575 | 0.0037106 | 0.064087 | 0.054932 | 0.050354 | 0.12817 | 0.17395 | 0.022888 | -0.11902 | 0.036621 | 0.068665 | -0.07782 | 0.054932 | 0.068665 | 0.036621 | -0.045776 | 122.644 | 122.5021 | 0.10528 | 122.6761 | 122.7493 | 0.24719 | -0.004578 | 122.6578 | 122.5754 | -0.013733 | 122.6578 | 122.5433 | -0.032044 | 0 | 122.7951 | 122.6852 | 122.6715 | -0.18768 | 122.6761 | 122.6898 | 122.6898 | -0.11444
2503.6562 | 122.8592 | -122.644 | 0.10986 | -0.0085447 | 0.014761 | 0.0052935 | 0.01038 | 0.053152 | -0.0052039 | -0.0046143 | -0.0084684 | -0.0017858 | -0.028427 | 0.042639 | 0.00019427 | 0.006915 | 0.091553 | 0.11444 | 0.13275 | 0.16022 | 0.14191 | 0.073242 | -0.07782 | 0.054932 | 0.16937 | 0.036621 | 0.036621 | 0.027466 | 0.054932 | -0.009155 | 122.7173 | 122.5662 | 0.032044 | 122.7585 | 122.8043 | 0.23804 | -0.01831 | 122.699 | 122.6349 | -0.073242 | 122.699 | 122.6807 | 0.045776 | -0.082397 | 122.7859 | 122.7356 | 122.7768 | -0.18768 | 122.6807 | 122.6715 | 122.8134 | -0.11902
2505.4375 | 122.905 | -122.6807 | 0.086975 | -0.0085447 | 0.017538 | 0.0035847 | 0.0026895 | 0.05422 | 0.0029139 | -0.0031189 | -0.0084684 | 0.0054772 | -0.031631 | 0.040076 | 0.0066029 | 0.0054196 | 0.027466 | -0.027466 | -0.018311 | 0.073242 | 0.16937 | 0.032043 | -0.10986 | -0.045776 | -0.036621 | -0.13275 | 0.068665 | 0.082397 | 0.027466 | -0.054932 | 122.7127 | 122.5708 | 0.082398 | 122.6532 | 122.7539 | 0.18311 | -0.059509 | 122.7081 | 122.6257 | -0.01831 | 122.6349 | 122.5479 | -0.077819 | -0.004578 | 122.85 | 122.7081 | 122.6624 | -0.19684 | 122.7493 | 122.7631 | 122.644 | -0.14191
2507.1406 | 122.8134 | -122.6761 | 0.11444 | -0.00091566 | 0.010062 | 0.0042255 | 0.0039713 | 0.052511 | -0.0062719 | -0.0052551 | -0.00083936 | -0.0024268 | -0.032913 | 0.041357 | 0.0038259 | 0.0071286 | 0.10071 | 0.12817 | 0.13275 | 0.14648 | 0.12817 | 0.086975 | -0.050354 | 0.059509 | 0.09613 | -0.013733 | 0.036621 | 0.054932 | 0.045776 | -0.013733 | 122.7631 | 122.6257 | 0.013733 | 122.8043 | 122.8226 | 0.19684 | -0.013733 | 122.7219 | 122.6624 | -0.07782 | 122.7356 | 122.6624 | 0 | -0.059509 | 122.8043 | 122.7768 | 122.8088 | -0.16479 | 122.7127 | 122.731 | 122.7722 | -0.12817
2508.8906 | 122.9416 | -122.6257 | 0.09613 | 0.0067138 | 0.016898 | 0.0037983 | 0.0061075 | 0.054433 | -0.00050411 | -0.0050415 | -0.0084684 | 0.0024866 | -0.029922 | 0.042212 | 0.0023305 | 0.0045652 | 0.027466 | -0.032043 | 0.004578 | 0.082397 | 0.1831 | 0.045776 | -0.11444 | -0.018311 | -0.009155 | -0.091553 | 0.064087 | 0.068665 | 0.041199 | -0.050354 | 122.6715 | 122.5113 | 0.086975 | 122.5937 | 122.7081 | 0.19684 | -0.068664 | 122.6669 | 122.5754 | -0.032043 | 122.6074 | 122.5342 | -0.041199 | -0.027465 | 122.8088 | 122.6532 | 122.6303 | -0.21057 | 122.6898 | 122.6944 | 122.6166 | -0.14648
2510.5781 | 122.9233 | -122.644 | 0.09613 | -0.00091566 | 0.017538 | 0.0035847 | 0.0020487 | 0.052297 | 0.00013669 | -0.0020507 | 0.0067901 | 0.003982 | -0.029708 | 0.041785 | 0.0085255 | 0.0081968 | 0.018311 | -0.013733 | -0.004578 | 0.091553 | 0.15106 | 0.041199 | -0.09613 | -0.027466 | -0.004578 | -0.13275 | 0.059509 | 0.068665 | 0.018311 | -0.045776 | 122.6852 | 122.5479 | 0.054932 | 122.6303 | 122.7356 | 0.18768 | -0.077819 | 122.6624 | 122.5983 | -0.036621 | 122.6166 | 122.5113 | -0.086975 | -0.027465 | 122.7951 | 122.6624 | 122.6395 | -0.19226 | 122.7036 | 122.7127 | 122.6395 | -0.14191
2512.3438 | 122.7905 | -122.6532 | 0.1236 | -0.00091566 | 0.016257 | 0.0042255 | 0.0063211 | 0.055288 | -0.0066993 | -0.0037597 | -0.00083936 | 0.0007776 | -0.030136 | 0.038794 | 0.0029713 | 0.0071286 | 0.082397 | 0.11444 | 0.1236 | 0.15106 | 0.1236 | 0.054932 | -0.082397 | 0.018311 | 0.10986 | -0.036621 | 0.054932 | 0.059509 | 0.045776 | -0.041199 | 122.7081 | 122.5708 | 0 | 122.7676 | 122.8043 | 0.23346 | -0.041199 | 122.699 | 122.612 | -0.068664 | 122.6715 | 122.6166 | 0.004578 | -0.064087 | 122.7768 | 122.7356 | 122.7768 | -0.20599 | 122.7081 | 122.7127 | 122.7631 | -0.16479
2514.0938 | 122.7905 | -122.6807 | 0.13733 | -0.0085447 | 0.015616 | 0.0020893 | 0.0078165 | 0.054647 | -0.0062719 | -0.0020507 | -0.00083936 | 0.0014184 | -0.031204 | 0.040503 | 0.00062147 | 0.0039242 | 0.10529 | 0.1236 | 0.14648 | 0.15564 | 0.11902 | 0.050354 | -0.059509 | 0.041199 | 0.15106 | -0.004578 | 0.045776 | 0.050354 | 0.054932 | -0.027466 | 122.731 | 122.6212 | -0.01831 | 122.8043 | 122.8363 | 0.21515 | -0.032043 | 122.7356 | 122.6532 | -0.091553 | 122.7219 | 122.6761 | 0.022888 | -0.086975 | 122.7997 | 122.7859 | 122.8271 | -0.19684 | 122.7264 | 122.731 | 122.8317 | -0.16479
2515.8438 | 122.818 | -122.7081 | 0.1236 | -0.0085447 | 0.009848 | 0.0048663 | 0.0014079 | 0.052511 | -0.0019995 | -0.0065369 | -0.0084684 | -7.6996e-05 | -0.034195 | 0.039862 | 0.0044667 | 0.006915 | 0.11902 | 0.13275 | 0.14191 | 0.15106 | 0.10529 | 0.068665 | -0.059509 | 0.054932 | 0.12817 | 0.009155 | 0.036621 | 0.050354 | 0.059509 | -0.013733 | 122.7768 | 122.6486 | -0.01831 | 122.8409 | 122.8592 | 0.21057 | -0.004577 | 122.7676 | 122.6944 | -0.086975 | 122.7631 | 122.7173 | 0.022888 | -0.073242 | 122.8134 | 122.8271 | 122.85 | -0.1831 | 122.7448 | 122.7585 | 122.8363 | -0.13733
2517.6094 | 122.8867 | -122.644 | 0.10529 | -0.0085447 | 0.010916 | 0.0027301 | 0.0033305 | 0.052511 | -0.0013587 | -0.0046143 | -0.0084684 | 0.0003504 | -0.033126 | 0.040289 | 0.0048939 | 0.0060604 | 0.14191 | 0.1236 | 0.14648 | 0.16937 | 0.1236 | 0.064087 | -0.054932 | 0.082397 | 0.12817 | 0.022888 | 0.027466 | 0.027466 | 0.054932 | -0.009155 | 122.7081 | 122.5891 | 0.01831 | 122.7676 | 122.8134 | 0.22431 | 0.036621 | 122.699 | 122.6349 | -0.07782 | 122.7264 | 122.6669 | 0.032043 | -0.07782 | 122.7676 | 122.7859 | 122.7905 | -0.16022 | 122.6715 | 122.6715 | 122.7722 | -0.11444
2519.375 | 122.9416 | -122.6395 | 0.09613 | 0.0067138 | 0.016257 | 0.0052935 | 0.0046121 | 0.052297 | -0.00050411 | -0.0063233 | -0.016098 | 0.0031274 | -0.02864 | 0.041571 | 0.0076711 | 0.0043516 | 0.027466 | -0.004578 | 0 | 0.09613 | 0.15106 | 0.009155 | -0.10986 | -0.009155 | 0.041199 | -0.11444 | 0.07782 | 0.082397 | 0.032043 | -0.045776 | 122.6486 | 122.5296 | 0.054932 | 122.6349 | 122.7356 | 0.20599 | -0.068664 | 122.6715 | 122.5937 | -0.01831 | 122.6303 | 122.525 | -0.068665 | -0.013733 | 122.7905 | 122.6669 | 122.6395 | -0.20599 | 122.7173 | 122.7219 | 122.6807 | -0.14191
2521.1406 | 122.9141 | -122.6395 | 0.07782 | -0.0085447 | 0.016898 | 0.0010211 | 0.0058939 | 0.056356 | 0.0020593 | -0.0031189 | -0.016098 | 0.003982 | -0.029708 | 0.04328 | 0.0057485 | 0.0039242 | 0.10071 | 0.073242 | 0.054932 | 0.12817 | 0.15564 | 0.036621 | -0.086975 | 0.045776 | 0.082397 | -0.068665 | 0.059509 | 0.068665 | 0.027466 | -0.027466 | 122.6761 | 122.5525 | 0.07782 | 122.7127 | 122.7676 | 0.21515 | 0.022888 | 122.6669 | 122.612 | -0.018311 | 122.6852 | 122.5708 | -0.041199 | -0.009155 | 122.7951 | 122.7402 | 122.6944 | -0.16479 | 122.699 | 122.7081 | 122.7219 | -0.10529
2522.8438 | 122.8592 | -122.6807 | 0.1236 | 0.0067138 | 0.012412 | 0.0074299 | 0.0041849 | 0.053152 | -0.0086219 | -0.0029053 | -0.0084684 | -0.0039222 | -0.031204 | 0.037939 | 0.00019427 | 0.0060604 | 0.050354 | 0.11444 | 0.11902 | 0.15106 | 0.13733 | 0.064087 | -0.073242 | 0.036621 | 0.13275 | 0.022888 | 0.032043 | 0.032043 | 0.059509 | -0.027466 | 122.7448 | 122.6074 | 0.013733 | 122.7951 | 122.8317 | 0.2243 | -0.073242 | 122.7402 | 122.6532 | -0.091553 | 122.7173 | 122.7036 | 0.050354 | -0.091553 | 122.818 | 122.731 | 122.7997 | -0.19684 | 122.7127 | 122.7127 | 122.8134 | -0.15106
2524.5938 | 122.8226 | -122.6852 | 0.12817 | 0.0067138 | 0.011771 | 0.0044391 | 0.0043985 | 0.052938 | -0.0058447 | -0.0054687 | -0.0084684 | -0.0034948 | -0.032272 | 0.037726 | 0.0046803 | 0.0056332 | 0.082397 | 0.11444 | 0.11902 | 0.14191 | 0.13733 | 0.064087 | -0.082397 | 0.032043 | 0.082397 | -0.032043 | 0.045776 | 0.032043 | 0.059509 | -0.022888 | 122.7493 | 122.6028 | 0.009155 | 122.7997 | 122.8271 | 0.2243 | -0.045777 | 122.7448 | 122.6624 | -0.082398 | 122.7173 | 122.6532 | -0.009155 | -0.096131 | 122.8226 | 122.7676 | 122.8043 | -0.21057 | 122.731 | 122.7173 | 122.7676 | -0.15106
2526.3594 | 122.9462 | -122.6349 | 0.07782 | -0.0085447 | 0.014548 | 0.0037983 | 0.0056803 | 0.050802 | 0.00056389 | -0.0031189 | -0.00083936 | 0.0031274 | -0.031204 | 0.040289 | 0.0059621 | 0.0039242 | 0.032043 | 0.032043 | 0.022888 | 0.11444 | 0.17395 | 0.027466 | -0.10986 | 0 | 0.059509 | -0.09613 | 0.082397 | 0.064087 | 0.018311 | -0.054932 | 122.6624 | 122.525 | 0.09613 | 122.6669 | 122.7493 | 0.2243 | -0.045777 | 122.6532 | 122.58 | 0.004577 | 122.6349 | 122.5388 | -0.041198 | -0.013733 | 122.8088 | 122.6669 | 122.6578 | -0.18768 | 122.7173 | 122.699 | 122.6944 | -0.13275
2528.0625 | 122.8455 | -122.6944 | 0.12817 | 0.0067138 | 0.014975 | 0.0070025 | 0.0065347 | 0.053365 | -0.0062719 | -0.0052551 | -0.00083936 | -0.0030676 | -0.028854 | 0.039221 | 0.0033985 | 0.0060604 | 0.10986 | 0.16022 | 0.16479 | 0.16937 | 0.13275 | 0.059509 | -0.068665 | 0.082397 | 0.18768 | 0.045776 | 0.022888 | 0.022888 | 0.064087 | -0.004578 | 122.7539 | 122.6257 | 0.004577 | 122.8546 | 122.8638 | 0.23804 | -0.018311 | 122.7585 | 122.6898 | -0.10529 | 122.7768 | 122.7402 | 0.050354 | -0.10529 | 122.8271 | 122.8043 | 122.8592 | -0.19684 | 122.7173 | 122.7173 | 122.8821 | -0.13275
2529.8125 | 122.8867 | -122.6944 | 0.11444 | 0.0067138 | 0.010275 | 0.0040119 | 0.0041849 | 0.051229 | -0.0047765 | -0.0031189 | -0.00083936 | -0.002854 | -0.029708 | 0.041357 | 0.00083507 | 0.0039242 | 0.091553 | 0.13733 | 0.14191 | 0.16022 | 0.11902 | 0.059509 | -0.082397 | 0.073242 | 0.15106 | 0.045776 | 0.032043 | 0.009155 | 0.064087 | -0.013733 | 122.7539 | 122.612 | 0.004578 | 122.8317 | 122.8546 | 0.24261 | -0.022888 | 122.7585 | 122.6807 | -0.082398 | 122.7676 | 122.7402 | 0.059509 | -0.10529 | 122.8134 | 122.7859 | 122.8363 | -0.19684 | 122.7264 | 122.7036 | 122.8455 | -0.12817
2531.5 | 122.9507 | -122.6715 | 0.068665 | -0.0085447 | 0.018607 | 0.0014483 | 0.0061075 | 0.054433 | 0.0018457 | -0.0031189 | 0.0067901 | 0.0044092 | -0.027359 | 0.042639 | 0.0057485 | 0.0032834 | 0.082397 | 0.07782 | 0.050354 | 0.12817 | 0.16022 | 0.032043 | -0.11444 | 0.050354 | 0.10071 | -0.068665 | 0.059509 | 0.059509 | 0.032043 | -0.022888 | 122.7036 | 122.5571 | 0.091552 | 122.7493 | 122.7997 | 0.24262 | 0.013732 | 122.7036 | 122.6486 | -0.009156 | 122.7219 | 122.6028 | -0.045777 | -0.009156 | 122.8317 | 122.7539 | 122.7219 | -0.18311 | 122.731 | 122.731 | 122.7722 | -0.091553
2533.25 | 122.937 | -122.6669 | 0.10529 | -0.0085447 | 0.015402 | 0.00080749 | 0.0048257 | 0.053579 | -7.6908e-05 | -0.0014099 | -0.0084684 | 0.0014184 | -0.029708 | 0.042639 | 0.0057485 | 0.0045652 | 0.022888 | -0.018311 | 0 | 0.091553 | 0.16479 | 0.022888 | -0.091553 | -0.004578 | -0.022888 | -0.13275 | 0.064087 | 0.064087 | 0.050354 | -0.059509 | 122.6898 | 122.5754 | 0.059509 | 122.6486 | 122.7585 | 0.18311 | -0.082398 | 122.7173 | 122.6074 | -0.041199 | 122.6624 | 122.5342 | -0.073242 | -0.041199 | 122.8317 | 122.6898 | 122.6669 | -0.19684 | 122.731 | 122.731 | 122.644 | -0.16479
2535.0156 | 122.8363 | -122.7173 | 0.11902 | -0.00091566 | 0.014975 | 0.0044391 | 0.0048257 | 0.054006 | -0.0047765 | -0.0024779 | 0.0067901 | -0.001145 | -0.03099 | 0.040716 | 0.0042531 | 0.0073422 | 0.09613 | 0.12817 | 0.13733 | 0.15106 | 0.11902 | 0.059509 | -0.073242 | 0.045776 | 0.10986 | -0.013733 | 0.032043 | 0.022888 | 0.059509 | -0.027466 | 122.7768 | 122.644 | 0 | 122.8455 | 122.8683 | 0.2243 | -0.022889 | 122.7768 | 122.6898 | -0.086976 | 122.7631 | 122.7036 | 0.013733 | -0.096131 | 122.8363 | 122.8134 | 122.8546 | -0.19226 | 122.7493 | 122.7402 | 122.8271 | -0.14649
2536.7812 | 122.9599 | -122.6349 | 0.086975 | -0.0085447 | 0.02117 | 0.0035847 | 0.0076029 | 0.055288 | 0.0016321 | -0.0044007 | -0.0084684 | 0.0024866 | -0.029281 | 0.042639 | 0.0068165 | 0.0039242 | 0.068665 | 0.064087 | 0.050354 | 0.13275 | 0.16479 | 0.041199 | -0.10986 | 0.041199 | 0.07782 | -0.07782 | 0.064087 | 0.045776 | 0.032043 | -0.054932 | 122.6761 | 122.525 | 0.07782 | 122.699 | 122.7676 | 0.24261 | -0.01831 | 122.6669 | 122.58 | -0.022888 | 122.6761 | 122.5571 | -0.022888 | -0.041199 | 122.7997 | 122.7036 | 122.6852 | -0.19684 | 122.699 | 122.6807 | 122.7127 | -0.14191
2538.5469 | 122.8271 | -122.6807 | 0.13275 | 0.0067138 | 0.015189 | 0.0061481 | 0.0071757 | 0.05486 | -0.0084081 | -0.0052551 | -0.0084684 | -0.0017858 | -0.029708 | 0.04093 | 0.0014759 | 0.0062742 | 0.10529 | 0.16022 | 0.16022 | 0.16937 | 0.11444 | 0.059509 | -0.068665 | 0.068665 | 0.1831 | 0.032043 | 0.032043 | 0.036621 | 0.068665 | -0.027466 | 122.7402 | 122.612 | -0.01831 | 122.8409 | 122.85 | 0.23804 | -0.027465 | 122.7493 | 122.6532 | -0.10071 | 122.7493 | 122.7127 | 0.059509 | -0.09613 | 122.7951 | 122.7859 | 122.8409 | -0.20142 | 122.7127 | 122.7173 | 122.8638 | -0.16022
2540.2344 | 122.9599 | -122.6669 | 0.082397 | -0.00091566 | 0.012625 | 0.0018757 | 0.0039713 | 0.05486 | -0.0022131 | -0.0031189 | 0.0067901 | 0.001632 | -0.03099 | 0.041357 | 0.0063893 | 0.0064878 | 0.1236 | 0.13275 | 0.14648 | 0.18768 | 0.10986 | 0.086975 | -0.068665 | 0.10529 | 0.13733 | 0.018311 | 0.022888 | 0.032043 | 0.059509 | -0.009155 | 122.7539 | 122.5983 | 0.027466 | 122.7997 | 122.8546 | 0.25635 | 0.041199 | 122.7264 | 122.6578 | -0.059509 | 122.7722 | 122.6852 | 0.027466 | -0.050354 | 122.7768 | 122.7905 | 122.8134 | -0.15106 | 122.6898 | 122.699 | 122.8043 | -0.091552
2541.9844 | 122.9233 | -122.6669 | 0.10529 | -0.00091566 | 0.017752 | 0.0016619 | 0.0063211 | 0.057851 | 0.00035029 | -0.0018371 | -0.00083936 | 0.0048364 | -0.027572 | 0.044562 | 0.0051075 | 0.005206 | 0.09613 | 0.09613 | 0.059509 | 0.1236 | 0.16022 | 0.018311 | -0.10529 | 0.036621 | 0.068665 | -0.086975 | 0.050354 | 0.054932 | 0.036621 | -0.036621 | 122.6852 | 122.5616 | 0.054931 | 122.7631 | 122.7905 | 0.22888 | -0.009156 | 122.7036 | 122.6303 | -0.054932 | 122.7036 | 122.58 | -0.050354 | -0.050354 | 122.8271 | 122.7631 | 122.7264 | -0.21057 | 122.7173 | 122.7219 | 122.7356 | -0.14191
2543.6719 | 122.9828 | -122.6807 | 0.086975 | -0.00091566 | 0.016684 | 0.0059345 | 0.0020487 | 0.052511 | 0.0016321 | -0.0022643 | 0.0067901 | 0.0018456 | -0.031845 | 0.041357 | 0.0055349 | 0.0084104 | 0.022888 | -0.013733 | 0.004578 | 0.073242 | 0.16022 | 0.032043 | -0.10071 | -0.032043 | -0.009155 | -0.12817 | 0.068665 | 0.082397 | 0.022888 | -0.041199 | 122.7127 | 122.58 | 0.073242 | 122.6669 | 122.7539 | 0.17395 | -0.064087 | 122.7036 | 122.6395 | -0.01831 | 122.6486 | 122.5525 | -0.086975 | -0.004578 | 122.8409 | 122.7036 | 122.6852 | -0.18768 | 122.7493 | 122.7631 | 122.6715 | -0.12817
2545.4531 | 122.8363 | -122.6898 | 0.14191 | -0.00091566 | 0.012839 | 0.0046527 | 0.0071757 | 0.055074 | -0.0071265 | -0.0054687 | -0.00083936 | -0.0005042 | -0.030777 | 0.037939 | 0.0012623 | 0.0064878 | 0.091553 | 0.16022 | 0.16479 | 0.17395 | 0.10529 | 0.068665 | -0.07782 | 0.059509 | 0.1831 | 0.027466 | 0.027466 | 0.027466 | 0.050354 | -0.022888 | 122.7585 | 122.612 | -0.036621 | 122.85 | 122.8638 | 0.25177 | -0.050354 | 122.7402 | 122.6669 | -0.11444 | 122.7493 | 122.7173 | 0.050354 | -0.11444 | 122.7951 | 122.7814 | 122.8546 | -0.21973 | 122.7173 | 122.7173 | 122.8729 | -0.16479
2547.2188 | 122.9004 | -122.6807 | 0.10986 | -0.00091566 | 0.014761 | 0.0052935 | 0.0054667 | 0.05486 | -0.0024267 | -0.0056823 | 0.0067901 | 0.0012048 | -0.031845 | 0.040503 | 0.0053211 | 0.0062742 | 0.004578 | 0.004578 | 0.013733 | 0.091553 | 0.16479 | 0.022888 | -0.11902 | -0.041199 | 0.027466 | -0.11902 | 0.064087 | 0.064087 | 0.041199 | -0.032043 | 122.7036 | 122.5616 | 0.054932 | 122.6852 | 122.7722 | 0.21057 | -0.10529 | 122.7219 | 122.6486 | -0.045776 | 122.6395 | 122.5616 | -0.086976 | -0.045776 | 122.8455 | 122.6852 | 122.6944 | -0.22888 | 122.7448 | 122.7448 | 122.7081 | -0.14191
2548.9844 | 122.9874 | -122.6807 | 0.10071 | 0.0067138 | 0.01348 | 0.0031573 | 0.00098046 | 0.055715 | 0.00013669 | -0.0024779 | -0.00083936 | -0.0009314 | -0.030349 | 0.041785 | 0.0055349 | 0.0056332 | 0.07782 | 0.086975 | 0.10071 | 0.1236 | 0.14191 | 0.059509 | -0.064087 | 0.07782 | 0.10529 | -0.013733 | 0.036621 | 0.041199 | 0.064087 | -0.013733 | 122.7402 | 122.6166 | 0.041199 | 122.7676 | 122.8043 | 0.18768 | -0.022888 | 122.7448 | 122.6669 | -0.064087 | 122.7585 | 122.6669 | 0 | -0.059509 | 122.8226 | 122.7585 | 122.7814 | -0.1648 | 122.7173 | 122.7219 | 122.7859 | -0.11444
2550.6719 | 122.9599 | -122.6761 | 0.10071 | -0.0085447 | 0.014334 | 0.0042255 | 0.0031167 | 0.053579 | -0.0032813 | -0.0020507 | 0.0067901 | 0.0003504 | -0.032058 | 0.038794 | 0.0057485 | 0.0058468 | 0.11902 | 0.11902 | 0.13733 | 0.16937 | 0.11902 | 0.068665 | -0.059509 | 0.07782 | 0.14191 | 0.022888 | 0.018311 | 0.041199 | 0.054932 | -0.013733 | 122.7448 | 122.6166 | 0.018311 | 122.7951 | 122.8455 | 0.22888 | 0.018311 | 122.731 | 122.6624 | -0.082397 | 122.7539 | 122.699 | 0.036621 | -0.059509 | 122.7951 | 122.7951 | 122.8134 | -0.16022 | 122.6944 | 122.7173 | 122.818 | -0.11444
2552.4375 | 122.9187 | -122.6898 | 0.082397 | -0.00091566 | 0.016898 | 0.0016619 | 0.0063211 | 0.053792 | 0.0014185 | -0.0029053 | -0.0084684 | 0.0046228 | -0.029281 | 0.041785 | 0.0051075 | 0.0067014 | 0.064087 | 0.050354 | 0.059509 | 0.1236 | 0.14191 | 0.032043 | -0.086975 | -0.004578 | 0.041199 | -0.10529 | 0.068665 | 0.068665 | 0.045776 | -0.045776 | 122.7219 | 122.6028 | 0.05951 | 122.7402 | 122.8134 | 0.21057 | -0.01831 | 122.7356 | 122.644 | -0.013732 | 122.6852 | 122.5845 | -0.05951 | -0.013732 | 122.8317 | 122.7539 | 122.7493 | -0.16937 | 122.7585 | 122.7585 | 122.731 | -0.12817
2554.2188 | 122.8775 | -122.6898 | 0.10529 | -0.00091566 | 0.012625 | 0.0061481 | 0.0080301 | 0.054006 | -0.0084081 | -0.0050415 | -0.00083936 | -0.0039222 | -0.032272 | 0.036871 | -1.9327e-05 | 0.0064878 | 0.09613 | 0.16937 | 0.15106 | 0.15564 | 0.12817 | 0.068665 | -0.068665 | 0.064087 | 0.18768 | 0.032043 | 0.004578 | 0.027466 | 0.050354 | -0.018311 | 122.7585 | 122.6212 | 0.022888 | 122.8592 | 122.8455 | 0.22431 | -0.009156 | 122.7402 | 122.6715 | -0.10071 | 122.7539 | 122.7219 | 0.050354 | -0.07782 | 122.818 | 122.7859 | 122.8409 | -0.17395 | 122.6944 | 122.7173 | 122.8775 | -0.1236
2555.9844 | 122.9233 | -122.6852 | 0.09613 | 0.0067138 | 0.017111 | -0.00068791 | 0.0058939 | 0.053792 | 0.0022729 | -0.0026917 | -0.016098 | 0.0041956 | -0.028213 | 0.041144 | 0.0074575 | 0.0039242 | 0.068665 | 0.041199 | 0.041199 | 0.10529 | 0.16022 | 0.041199 | -0.09613 | 0 | 0.022888 | -0.1236 | 0.050354 | 0.064087 | 0.022888 | -0.045776 | 122.7264 | 122.5891 | 0.064087 | 122.7264 | 122.7905 | 0.20142 | -0.027465 | 122.7081 | 122.6395 | -0.045776 | 122.6852 | 122.5616 | -0.07782 | -0.032043 | 122.8455 | 122.7539 | 122.7264 | -0.19226 | 122.7356 | 122.7493 | 122.7081 | -0.14191
2557.6719 | 122.8592 | -122.699 | 0.1236 | -0.00091566 | 0.012839 | 0.0044391 | 0.0086709 | 0.053365 | -0.0084081 | -0.0018371 | -0.00083936 | -0.0030676 | -0.030563 | 0.041785 | 0.0021169 | 0.0060604 | 0.086975 | 0.16022 | 0.16479 | 0.17853 | 0.11902 | 0.064087 | -0.054932 | 0.059509 | 0.18768 | 0.018311 | 0.013733 | 0.032043 | 0.07782 | -0.022888 | 122.7631 | 122.644 | -0.004577 | 122.8592 | 122.8775 | 0.23346 | -0.036621 | 122.7768 | 122.6761 | -0.10986 | 122.7585 | 122.7173 | 0.041199 | -0.091553 | 122.818 | 122.7859 | 122.8638 | -0.17853 | 122.7127 | 122.731 | 122.8867 | -0.14648
2559.4375 | 122.8958 | -122.7127 | 0.082397 | -0.0085447 | 0.013266 | 0.0055073 | 0.0061075 | 0.05486 | -0.0090491 | -0.0067505 | -0.016098 | -0.004563 | -0.032913 | 0.038367 | 0.0019033 | 0.0064878 | 0.10529 | 0.16022 | 0.16022 | 0.16479 | 0.1236 | 0.054932 | -0.073242 | 0.068665 | 0.1831 | 0.059509 | 0.018311 | 0.036621 | 0.059509 | -0.018311 | 122.7676 | 122.6395 | 0.041199 | 122.8729 | 122.8775 | 0.23804 | 0.022889 | 122.7722 | 122.6944 | -0.064086 | 122.7814 | 122.7722 | 0.07782 | -0.045776 | 122.8363 | 122.818 | 122.8729 | -0.15564 | 122.731 | 122.7493 | 122.8958 | -0.10071
2561.1875 | 122.9416 | -122.7036 | 0.091553 | 0.0067138 | 0.013693 | 0.0050799 | 0.0014079 | 0.052938 | -0.00029051 | -0.0033325 | 0.0067901 | -0.0007178 | -0.031204 | 0.039435 | 0.0066029 | 0.0049924 | 0.11902 | 0.1236 | 0.15106 | 0.16937 | 0.11444 | 0.068665 | -0.059509 | 0.10529 | 0.12817 | 0.018311 | 0.018311 | 0.032043 | 0.073242 | -0.013733 | 122.7722 | 122.644 | 0.022888 | 122.8271 | 122.8729 | 0.22888 | 0.027466 | 122.7768 | 122.6898 | -0.073242 | 122.8088 | 122.7219 | 0.032044 | -0.05951 | 122.818 | 122.8226 | 122.8546 | -0.15106 | 122.7219 | 122.7356 | 122.8317 | -0.10529
2562.8906 | 122.9095 | -122.7173 | 0.11444 | 0.0067138 | 0.012625 | 0.0040119 | 0.0018351 | 0.055288 | -0.0026403 | -0.0026917 | -0.00083936 | -0.0015722 | -0.033126 | 0.037085 | 0.0074575 | 0.0049924 | 0.10986 | 0.13733 | 0.15106 | 0.16479 | 0.10986 | 0.059509 | -0.059509 | 0.073242 | 0.13275 | 0.022888 | 0.027466 | 0.032043 | 0.064087 | -0.027466 | 122.7768 | 122.6578 | -0.004578 | 122.8546 | 122.8821 | 0.2243 | -0.004578 | 122.7814 | 122.6898 | -0.086975 | 122.7905 | 122.7402 | 0.050354 | -0.082398 | 122.8271 | 122.8271 | 122.8683 | -0.17395 | 122.7448 | 122.7493 | 122.85 | -0.14191
2564.5781 | 122.905 | -122.6807 | 0.10529 | -0.0085447 | 0.017325 | 0.0037983 | 0.0093119 | 0.052938 | -0.00050411 | -0.0039733 | -0.0084684 | 0.001632 | -0.029068 | 0.040716 | 0.0038259 | 0.005206 | 0.032043 | -0.004578 | 0.009155 | 0.07782 | 0.15106 | 0.009155 | -0.09613 | -0.027466 | 0.009155 | -0.11444 | 0.073242 | 0.09613 | 0.022888 | -0.050354 | 122.6898 | 122.5845 | 0.045776 | 122.6761 | 122.7585 | 0.17395 | -0.073243 | 122.7036 | 122.6303 | -0.032044 | 122.6532 | 122.5662 | -0.064087 | -0.009156 | 122.8317 | 122.7127 | 122.6898 | -0.20142 | 122.7539 | 122.7768 | 122.6898 | -0.15564
2566.3438 | 122.9462 | -122.6715 | 0.059509 | -0.00091566 | 0.016898 | 0.0023029 | 0.0052531 | 0.056356 | 0.0039819 | -0.0031189 | -0.00083936 | 0.001632 | -0.031204 | 0.042212 | 0.0059621 | 0.0077694 | 0.10986 | 0.064087 | 0.064087 | 0.12817 | 0.14191 | 0.041199 | -0.086975 | 0.036621 | 0.073242 | -0.07782 | 0.032043 | 0.045776 | 0.054932 | -0.032043 | 122.7127 | 122.5845 | 0.082398 | 122.7356 | 122.7997 | 0.21515 | 0.050354 | 122.7264 | 122.6395 | -0.027466 | 122.7081 | 122.5937 | -0.045777 | -0.013733 | 122.8134 | 122.7814 | 122.7356 | -0.14648 | 122.7036 | 122.7173 | 122.7448 | -0.091552
2568.125 | 122.8775 | -122.7127 | 0.1236 | -0.00091566 | 0.016043 | 0.0055073 | 0.0071757 | 0.052297 | -0.0037085 | -0.0039733 | -0.00083936 | 0.0012048 | -0.029281 | 0.041785 | 0.0025441 | 0.0062742 | 0.009155 | 0 | 0.009155 | 0.064087 | 0.16937 | 0.013733 | -0.11902 | -0.050354 | 0.018311 | -0.11444 | 0.068665 | 0.07782 | 0.018311 | -0.032043 | 122.7264 | 122.5937 | 0.045777 | 122.7127 | 122.7768 | 0.18311 | -0.11444 | 122.731 | 122.6807 | -0.054931 | 122.6624 | 122.5983 | -0.082398 | -0.045776 | 122.8821 | 122.7219 | 122.7219 | -0.24261 | 122.7814 | 122.7905 | 122.731 | -0.15564
2569.8125 | 122.9507 | -122.6898 | 0.073242 | 0.0067138 | 0.020956 | 0.0027301 | 0.0086709 | 0.052511 | -7.6908e-05 | -0.0044007 | -0.0084684 | 0.0029138 | -0.029281 | 0.041785 | 0.0042531 | 0.0037106 | 0.091553 | 0.073242 | 0.082397 | 0.13275 | 0.16479 | 0.054932 | -0.09613 | 0.036621 | 0.091553 | -0.086975 | 0.054932 | 0.07782 | 0.022888 | -0.022888 | 122.7448 | 122.5937 | 0.091553 | 122.7631 | 122.8226 | 0.22888 | 0.018311 | 122.7127 | 122.6669 | -0.01831 | 122.7264 | 122.6028 | -0.064087 | 0.004578 | 122.8546 | 122.7814 | 122.7722 | -0.16937 | 122.7448 | 122.7676 | 122.7814 | -0.09613
2571.5156 | 122.9965 | -122.6944 | 0.07782 | -0.00091566 | 0.013693 | 0.0020893 | 0.0014079 | 0.053579 | -0.0017859 | -0.0016235 | -0.00083936 | 0.0024866 | -0.030136 | 0.042425 | 0.0066029 | 0.0081968 | 0.036621 | 0.004578 | 0.009155 | 0.086975 | 0.14191 | 0.041199 | -0.10529 | -0.004578 | 0.013733 | -0.07782 | 0.045776 | 0.073242 | 0.041199 | -0.036621 | 122.7356 | 122.5891 | 0.064087 | 122.699 | 122.7814 | 0.19226 | -0.041199 | 122.7356 | 122.6578 | -0.032044 | 122.6898 | 122.6166 | -0.041199 | -0.004578 | 122.8363 | 122.731 | 122.7036 | -0.18311 | 122.7402 | 122.7676 | 122.7081 | -0.11444
2573.2188 | 123.0057 | -122.6807 | 0.091553 | 0.0067138 | 0.013266 | 0.0031573 | 0.0018351 | 0.052511 | -0.00093131 | -0.0039733 | -0.00083936 | 0.0003504 | -0.03099 | 0.040289 | 0.0057485 | 0.0075558 | 0.041199 | 0.022888 | 0.050354 | 0.10529 | 0.14648 | 0.032043 | -0.09613 | 0.032043 | 0.086975 | -0.054932 | 0.041199 | 0.059509 | 0.064087 | -0.036621 | 122.7127 | 122.5845 | 0.054931 | 122.7036 | 122.7859 | 0.20142 | -0.050354 | 122.7448 | 122.644 | -0.050354 | 122.7127 | 122.6257 | -0.018311 | -0.032044 | 122.8271 | 122.7219 | 122.731 | -0.18768 | 122.7219 | 122.7402 | 122.7676 | -0.12817
2574.9844 | 122.9874 | -122.6944 | 0.10071 | -0.0085447 | 0.015402 | 0.0018757 | 0.0029031 | 0.053152 | -0.0028539 | -0.0046143 | -0.0084684 | -0.0007178 | -0.030136 | 0.040076 | 0.0044667 | 0.008624 | 0.10071 | 0.10071 | 0.10529 | 0.16479 | 0.1236 | 0.068665 | -0.064087 | 0.073242 | 0.13733 | 0 | 0.018311 | 0.027466 | 0.068665 | -0.018311 | 122.7631 | 122.6303 | 0.022888 | 122.7951 | 122.8592 | 0.22888 | 0 | 122.7631 | 122.6761 | -0.082397 | 122.7676 | 122.6944 | 0.018311 | -0.073242 | 122.818 | 122.7951 | 122.7997 | -0.1648 | 122.7127 | 122.7219 | 122.8317 | -0.11902
2576.6719 | 122.9919 | -122.6944 | 0.09613 | 0.0067138 | 0.014975 | 0.0040119 | 0.0050393 | 0.053579 | -0.0019995 | -0.0031189 | -0.00083936 | 0.000564 | -0.029495 | 0.040076 | 0.0038259 | 0.0056332 | 0.022888 | 0.013733 | 0.022888 | 0.09613 | 0.16022 | 0.018311 | -0.10071 | -0.004578 | 0.054932 | -0.09613 | 0.068665 | 0.07782 | 0.022888 | -0.045776 | 122.7127 | 122.5937 | 0.064087 | 122.7081 | 122.7905 | 0.19684 | -0.073242 | 122.7173 | 122.6486 | -0.027465 | 122.6898 | 122.5983 | -0.050354 | -0.01831 | 122.8546 | 122.7173 | 122.7173 | -0.19684 | 122.7631 | 122.7722 | 122.7493 | -0.14191
2578.4531 | 123.0103 | -122.6807 | 0.09613 | 0.0067138 | 0.015189 | 0.0052935 | 0.0037577 | 0.050374 | -0.0024267 | -0.0050415 | -0.00083936 | 0.0003504 | -0.031417 | 0.041357 | 0.0068165 | 0.0060604 | 0.064087 | 0.050354 | 0.064087 | 0.10529 | 0.13733 | 0.041199 | -0.091553 | 0.068665 | 0.082397 | -0.013733 | 0.036621 | 0.045776 | 0.073242 | -0.018311 | 122.7219 | 122.5891 | 0.041199 | 122.731 | 122.7859 | 0.19684 | -0.032043 | 122.7539 | 122.6624 | -0.059509 | 122.7493 | 122.6669 | 0.004578 | -0.050354 | 122.818 | 122.7448 | 122.7448 | -0.18768 | 122.7173 | 122.7264 | 122.7631 | -0.11444
2580.2188 | 122.9187 | -122.7539 | 0.10071 | -0.00091566 | 0.013266 | 0.0055073 | 0.0086709 | 0.053365 | -0.010117 | -0.0044007 | 0.0067901 | -0.0041358 | -0.030563 | 0.04093 | -0.00044673 | 0.0060604 | 0.064087 | 0.082397 | 0.11902 | 0.14191 | 0.13275 | 0.059509 | -0.07782 | 0.036621 | 0.14191 | 0.013733 | 0.032043 | 0.045776 | 0.054932 | -0.018311 | 122.8134 | 122.6761 | 0.032043 | 122.8363 | 122.8958 | 0.21973 | -0.036621 | 122.8088 | 122.7356 | -0.068665 | 122.7905 | 122.7676 | 0.032044 | -0.054932 | 122.8867 | 122.818 | 122.8729 | -0.17853 | 122.7859 | 122.7997 | 122.8958 | -0.11902
2581.9062 | 122.9645 | -122.6669 | 0.091553 | -0.0085447 | 0.013693 | 0.0046527 | 0.0020487 | 0.05486 | 0.00013669 | -0.0029053 | -0.0084684 | 0.0018456 | -0.031631 | 0.042853 | 0.0053211 | 0.0056332 | 0.041199 | -0.013733 | 0.022888 | 0.086975 | 0.16479 | 0.027466 | -0.12817 | -0.032043 | 0.022888 | -0.10529 | 0.068665 | 0.082397 | 0.013733 | -0.064087 | 122.6944 | 122.5388 | 0.073242 | 122.6532 | 122.7539 | 0.21515 | -0.050354 | 122.6807 | 122.6028 | -0.022888 | 122.6349 | 122.5616 | -0.041199 | -0.009156 | 122.8317 | 122.7081 | 122.6898 | -0.21973 | 122.7356 | 122.7493 | 122.6898 | -0.15564
2583.6719 | 122.8729 | -122.7127 | 0.14191 | -0.0085447 | 0.014121 | 0.0067889 | 0.0078165 | 0.051015 | -0.0056311 | -0.0037597 | 0.0067901 | -0.0022132 | -0.029708 | 0.04093 | 0.0044667 | 0.006915 | 0.10529 | 0.13275 | 0.15564 | 0.17853 | 0.10529 | 0.073242 | -0.073242 | 0.073242 | 0.16479 | 0.027466 | 0.018311 | 0.050354 | 0.068665 | -0.013733 | 122.7859 | 122.6395 | -0.036621 | 122.8455 | 122.8912 | 0.25177 | -0.036621 | 122.7814 | 122.699 | -0.1236 | 122.7859 | 122.7402 | 0.041199 | -0.091553 | 122.818 | 122.818 | 122.8683 | -0.21515 | 122.731 | 122.7631 | 122.8775 | -0.15564
2585.4531 | 122.9874 | -122.7264 | 0.07782 | -0.016174 | 0.018393 | 0.0042255 | 0.0058939 | 0.055288 | -0.0017859 | -0.0050415 | -0.00083936 | 0.003982 | -0.030136 | 0.041571 | 0.0053211 | 0.0039242 | 0.022888 | -0.009155 | 0.027466 | 0.086975 | 0.16479 | 0.018311 | -0.11444 | -0.013733 | 0.041199 | -0.11444 | 0.086975 | 0.073242 | 0.022888 | -0.045776 | 122.7448 | 122.612 | 0.086975 | 122.7173 | 122.8134 | 0.20142 | -0.054932 | 122.7493 | 122.6807 | 0.009155 | 122.7127 | 122.612 | -0.068665 | -0.004578 | 122.8912 | 122.7493 | 122.7539 | -0.19226 | 122.8134 | 122.7997 | 122.7676 | -0.1236
2587.2031 | 123.0194 | -122.7081 | 0.07782 | -0.00091566 | 0.01583 | 0.0018757 | 0.0020487 | 0.052297 | -7.6908e-05 | -0.0024779 | 0.0067901 | 0.0027002 | -0.029068 | 0.045416 | 0.0074575 | 0.0054196 | 0.018311 | 0.004578 | 0.022888 | 0.07782 | 0.16022 | 0.018311 | -0.10071 | 0 | 0.018311 | -0.09613 | 0.054932 | 0.054932 | 0.036621 | -0.027466 | 122.7264 | 122.6074 | 0.082397 | 122.7127 | 122.7859 | 0.17853 | -0.059509 | 122.7448 | 122.6807 | -0.022888 | 122.7081 | 122.612 | -0.068664 | -0.022888 | 122.8683 | 122.7264 | 122.731 | -0.17853 | 122.7631 | 122.7631 | 122.7264 | -0.10529
2588.9688 | 123.0103 | -122.699 | 0.082397 | -0.00091566 | 0.017538 | 0.0029437 | 0.0048257 | 0.056569 | -0.0022131 | -0.00098272 | -0.0084684 | 0.0018456 | -0.030349 | 0.041998 | 0.0053211 | 0.003497 | 0.022888 | 0.022888 | 0.045776 | 0.10986 | 0.16479 | 0.009155 | -0.09613 | 0.004578 | 0.068665 | -0.068665 | 0.054932 | 0.059509 | 0.045776 | -0.050354 | 122.7081 | 122.6028 | 0.082398 | 122.7219 | 122.8088 | 0.20599 | -0.059509 | 122.7448 | 122.6486 | -0.027465 | 122.7036 | 122.6303 | -0.018311 | -0.022888 | 122.8638 | 122.7219 | 122.7448 | -0.17853 | 122.7539 | 122.7585 | 122.7676 | -0.13275
2590.6562 | 122.8546 | -122.7127 | 0.10986 | -0.00091566 | 0.014975 | 0.0033709 | 0.0071757 | 0.053152 | -0.0066993 | -0.0046143 | -0.00083936 | -0.0013586 | -0.029281 | 0.040503 | 0.0010487 | 0.0077694 | 0.07782 | 0.10529 | 0.13275 | 0.17853 | 0.1236 | 0.059509 | -0.064087 | 0.013733 | 0.13275 | -0.013733 | 0.041199 | 0.064087 | 0.059509 | -0.045776 | 122.7722 | 122.6486 | 0.013733 | 122.818 | 122.8912 | 0.24261 | -0.032043 | 122.7722 | 122.6669 | -0.068664 | 122.7264 | 122.699 | 0.032043 | -0.045776 | 122.8363 | 122.7905 | 122.8455 | -0.17395 | 122.7539 | 122.7768 | 122.8455 | -0.15564
2592.4375 | 122.9004 | -122.7219 | 0.10529 | 0.0067138 | 0.013693 | 0.0042255 | 0.0076029 | 0.054006 | -0.0084081 | -0.0039733 | 0.0067901 | -0.0019996 | -0.031631 | 0.04093 | 0.0010487 | 0.0058468 | 0.1236 | 0.1831 | 0.16937 | 0.17395 | 0.11444 | 0.064087 | -0.073242 | 0.059509 | 0.19684 | 0.027466 | 0.027466 | 0.036621 | 0.073242 | -0.018311 | 122.7859 | 122.6486 | 0.009155 | 122.905 | 122.8958 | 0.24719 | 0.01831 | 122.7951 | 122.7036 | -0.07782 | 122.7814 | 122.7493 | 0.045777 | -0.068665 | 122.8363 | 122.8455 | 122.8912 | -0.17853 | 122.7493 | 122.7585 | 122.9187 | -0.1236
2594.1562 | 122.2641 | -122.1588 | 0.11902 | 0.0067138 | 0.011984 | 0.0042255 | 0.0056803 | 0.052083 | -0.0062719 | -0.0076049 | 0.0067901 | -0.0002906 | -0.029281 | 0.041357 | 0.0014759 | 0.0056332 | 0.10529 | 0.1236 | 0.14191 | 0.15106 | 0.1236 | 0.050354 | -0.07782 | 0.082397 | 0.16022 | 0.050354 | 0.022888 | 0.050354 | 0.068665 | -0.018311 | 122.2092 | 122.081 | 0.004577 | 122.2824 | 122.3099 | 0.22888 | -0.013733 | 122.2275 | 122.1405 | -0.096131 | 122.2412 | 122.2092 | 0.068665 | -0.068665 | 122.2824 | 122.2641 | 122.3007 | -0.19684 | 122.1817 | 122.2092 | 122.319 | -0.13733
2595.9219 | 122.3465 | -122.2275 | 0.10986 | -0.0085447 | 0.013693 | 0.0033709 | 0.0022623 | 0.055074 | -0.0052039 | -0.0048279 | -0.00083936 | -0.0009314 | -0.032058 | 0.041357 | 0.0036123 | 0.0058468 | 0.10529 | 0.16022 | 0.15564 | 0.16937 | 0.13275 | 0.054932 | -0.064087 | 0.091553 | 0.17395 | 0.022888 | 0.018311 | 0.036621 | 0.064087 | -0.013733 | 122.2824 | 122.1634 | 0.022888 | 122.3877 | 122.3969 | 0.23346 | -0.004577 | 122.2916 | 122.2137 | -0.091552 | 122.319 | 122.2504 | 0.036621 | -0.073242 | 122.3602 | 122.3328 | 122.3831 | -0.17395 | 122.2458 | 122.2641 | 122.4014 | -0.1236
2597.625 | 122.5479 | -122.3236 | 0.091553 | -0.0085447 | 0.017538 | 0.0046527 | 0.0016215 | 0.055074 | 0.0031275 | -0.0039733 | -0.0084684 | 0.003982 | -0.03099 | 0.041998 | 0.0078847 | 0.0045652 | 0.10529 | 0.07782 | 0.059509 | 0.12817 | 0.16022 | 0.036621 | -0.091553 | 0.036621 | 0.064087 | -0.09613 | 0.068665 | 0.064087 | 0.050354 | -0.041199 | 122.3602 | 122.2321 | 0.068664 | 122.4014 | 122.4518 | 0.21973 | 0.013733 | 122.374 | 122.2824 | -0.022888 | 122.3602 | 122.2275 | -0.054931 | -0.027466 | 122.4838 | 122.4289 | 122.3831 | -0.18311 | 122.3923 | 122.3877 | 122.3877 | -0.13275
2599.4062 | 122.5571 | -122.3648 | 0.10529 | -0.0085447 | 0.014121 | 0.0052935 | 0.0078165 | 0.053792 | -0.0071265 | -0.0037597 | 0.0067901 | -0.0024268 | -0.03099 | 0.039007 | 0.00062147 | 0.0056332 | 0.082397 | 0.12817 | 0.13733 | 0.15106 | 0.13275 | 0.050354 | -0.082397 | 0.064087 | 0.16022 | 0.041199 | 0.054932 | 0.045776 | 0.064087 | -0.022888 | 122.4152 | 122.2824 | 0.027465 | 122.493 | 122.5159 | 0.23346 | -0.022889 | 122.4289 | 122.3419 | -0.050354 | 122.4289 | 122.406 | 0.064087 | -0.05951 | 122.4976 | 122.4472 | 122.5021 | -0.18768 | 122.4197 | 122.4106 | 122.525 | -0.12817
2601.0938 | 122.5708 | -122.3831 | 0.13275 | -0.00091566 | 0.012839 | 0.0078571 | 0.0033305 | 0.053152 | -0.0079809 | -0.0063233 | -0.0084684 | -0.0009314 | -0.031204 | 0.03858 | 0.0027577 | 0.0058468 | 0.12817 | 0.15106 | 0.14648 | 0.16937 | 0.12817 | 0.073242 | -0.054932 | 0.086975 | 0.17395 | 0.054932 | 0.022888 | 0.036621 | 0.064087 | -0.013733 | 122.4564 | 122.3282 | -0.004577 | 122.5342 | 122.5525 | 0.22431 | -0.004577 | 122.4472 | 122.3694 | -0.10986 | 122.4701 | 122.438 | 0.068665 | -0.09613 | 122.5113 | 122.5113 | 122.5296 | -0.18768 | 122.406 | 122.4197 | 122.5571 | -0.14648
2602.8438 | 122.6074 | -122.4014 | 0.10986 | 0.0067138 | 0.012839 | 0.0042255 | 0.0082437 | 0.053152 | -0.0013587 | -0.0058959 | -0.00083936 | 0.001632 | -0.029495 | 0.040503 | 0.0051075 | 0.0047788 | 0.036621 | 0.018311 | 0.018311 | 0.09613 | 0.18768 | 0.018311 | -0.09613 | -0.027466 | 0.027466 | -0.11444 | 0.086975 | 0.073242 | 0.009155 | -0.068665 | 122.4197 | 122.3053 | 0.07782 | 122.4197 | 122.4976 | 0.19226 | -0.073242 | 122.4106 | 122.3328 | -0.022888 | 122.374 | 122.287 | -0.045776 | -0.036621 | 122.5891 | 122.438 | 122.4197 | -0.20599 | 122.4884 | 122.4747 | 122.4289 | -0.17853
2604.5469 | 122.6624 | -122.3969 | 0.10071 | 0.014343 | 0.011771 | 0.0059345 | 0.0014079 | 0.053365 | -0.0011451 | -0.0026917 | -0.0084684 | -0.0005042 | -0.032272 | 0.041357 | 0.0068165 | 0.006915 | 0.13733 | 0.12817 | 0.13275 | 0.16937 | 0.11444 | 0.068665 | -0.045776 | 0.10071 | 0.12817 | 0.009155 | 0.018311 | 0.045776 | 0.064087 | -0.018311 | 122.4655 | 122.3511 | 0.013733 | 122.525 | 122.5662 | 0.21515 | 0.036621 | 122.4609 | 122.3785 | -0.082397 | 122.4976 | 122.406 | 0.027466 | -0.054932 | 122.5113 | 122.5342 | 122.5296 | -0.14648 | 122.4152 | 122.4426 | 122.525 | -0.11902
2606.3125 | 122.5845 | -122.4243 | 0.1236 | -0.00091566 | 0.015616 | 0.0046527 | 0.0067483 | 0.055929 | -0.0058447 | -0.0041869 | 0.0067901 | -0.0013586 | -0.030349 | 0.040503 | 0.0014759 | 0.0056332 | 0.12817 | 0.16022 | 0.16022 | 0.16479 | 0.12817 | 0.041199 | -0.07782 | 0.091553 | 0.18768 | 0.018311 | 0.004578 | 0.050354 | 0.082397 | -0.036621 | 122.4655 | 122.3465 | 0.004578 | 122.5845 | 122.5891 | 0.24261 | 0.004578 | 122.5067 | 122.3877 | -0.11902 | 122.5159 | 122.4426 | 0.054932 | -0.073242 | 122.5525 | 122.5525 | 122.5845 | -0.20142 | 122.4289 | 122.4747 | 122.612 | -0.16022
2608.0156 | 122.7127 | -122.4152 | 0.082397 | 0.0067138 | 0.014761 | 0.0025165 | 0.0033305 | 0.056783 | 0.0014185 | -0.0018371 | -0.00083936 | 0.003982 | -0.029922 | 0.044134 | 0.0072437 | 0.0049924 | 0.041199 | -0.027466 | -0.004578 | 0.091553 | 0.17853 | 0.036621 | -0.091553 | -0.004578 | 0 | -0.1236 | 0.059509 | 0.068665 | 0.041199 | -0.050354 | 122.4518 | 122.3236 | 0.096131 | 122.3877 | 122.5067 | 0.18311 | -0.041198 | 122.4564 | 122.3648 | -0.022888 | 122.4106 | 122.2916 | -0.073242 | -0.013732 | 122.5937 | 122.4564 | 122.4106 | -0.17395 | 122.4747 | 122.4838 | 122.4152 | -0.13275
2609.7656 | 122.6898 | -122.4335 | 0.09613 | -0.00091566 | 0.014548 | 0.0044391 | 0.0022623 | 0.053152 | 0.0024865 | -0.0024779 | -0.00083936 | 0.0027002 | -0.032058 | 0.041785 | 0.0080983 | 0.006915 | 0.041199 | -0.022888 | 0 | 0.082397 | 0.15106 | 0.045776 | -0.10529 | -0.013733 | -0.004578 | -0.14648 | 0.073242 | 0.073242 | 0.041199 | -0.054932 | 122.4792 | 122.3282 | 0.054932 | 122.4106 | 122.5159 | 0.18768 | -0.054931 | 122.4747 | 122.3785 | -0.022888 | 122.4197 | 122.287 | -0.091552 | -0.022888 | 122.5845 | 122.4747 | 122.4335 | -0.20142 | 122.5067 | 122.5067 | 122.4289 | -0.15106
2611.5312 | 122.6257 | -122.4609 | 0.11902 | -0.016174 | 0.014761 | 0.0063617 | 0.0078165 | 0.056569 | -0.0043493 | -0.0039733 | -0.00083936 | -0.0015722 | -0.029281 | 0.040503 | 0.00040787 | 0.0056332 | 0.009155 | 0.009155 | 0.032043 | 0.07782 | 0.17395 | 0.009155 | -0.1236 | -0.050354 | 0.036621 | -0.10529 | 0.073242 | 0.086975 | 0.013733 | -0.059509 | 122.4701 | 122.3373 | 0.054931 | 122.4701 | 122.5388 | 0.20142 | -0.10986 | 122.4747 | 122.4014 | -0.045777 | 122.4106 | 122.3557 | -0.045777 | -0.032044 | 122.6349 | 122.4701 | 122.493 | -0.24261 | 122.5342 | 122.5479 | 122.4976 | -0.17853
2613.2969 | 122.6028 | -122.5204 | 0.12817 | 0.0067138 | 0.015616 | 0.0023029 | 0.0071757 | 0.053579 | -0.0045629 | -0.0046143 | -0.0084684 | -0.0017858 | -0.031845 | 0.040289 | 0.0031849 | 0.0054196 | 0.09613 | 0.11902 | 0.14191 | 0.15564 | 0.13733 | 0.07782 | -0.054932 | 0.036621 | 0.10529 | -0.009155 | 0.013733 | 0.032043 | 0.068665 | -0.009155 | 122.5983 | 122.4655 | 0.009155 | 122.6395 | 122.6761 | 0.21057 | -0.032044 | 122.5891 | 122.5113 | -0.11444 | 122.5571 | 122.5113 | 0 | -0.096131 | 122.6578 | 122.6166 | 122.6624 | -0.18311 | 122.5342 | 122.5525 | 122.6257 | -0.13733
2615.0156 | 122.6395 | -122.4976 | 0.10071 | -0.00091566 | 0.017538 | 0.0033709 | 0.0084573 | 0.05422 | -0.0045629 | -0.0029053 | 0.0067901 | 0.0018456 | -0.027359 | 0.042212 | 0.0055349 | 0.0043516 | 0.022888 | 0.009155 | 0.018311 | 0.07782 | 0.18768 | 0.045776 | -0.11902 | -0.041199 | 0.041199 | -0.11444 | 0.07782 | 0.064087 | 0.027466 | -0.068665 | 122.5433 | 122.3785 | 0.086975 | 122.5067 | 122.5754 | 0.19684 | -0.07782 | 122.525 | 122.4289 | -0.022888 | 122.4564 | 122.3831 | -0.045776 | -0.036621 | 122.6852 | 122.5204 | 122.5159 | -0.21973 | 122.5754 | 122.5616 | 122.5388 | -0.16937
2616.7656 | 122.6303 | -122.5113 | 0.13275 | -0.0085447 | 0.013907 | 0.0050799 | 0.0031167 | 0.053365 | -0.0064855 | -0.0018371 | -0.00083936 | -7.6996e-05 | -0.031845 | 0.040289 | 0.0014759 | 0.0056332 | 0.064087 | 0.09613 | 0.10986 | 0.12817 | 0.1236 | 0.082397 | -0.073242 | 0.027466 | 0.086975 | -0.018311 | 0.036621 | 0.050354 | 0.059509 | -0.018311 | 122.5937 | 122.4381 | -0.009155 | 122.6074 | 122.6395 | 0.20142 | -0.068664 | 122.5708 | 122.493 | -0.09613 | 122.5388 | 122.493 | 0 | -0.082397 | 122.6349 | 122.5754 | 122.6212 | -0.20599 | 122.5479 | 122.5616 | 122.5983 | -0.15106
2618.5469 | 122.7631 | -122.4518 | 0.09613 | -0.0085447 | 0.014121 | 0.0018757 | 0.0022623 | 0.054006 | -0.0022131 | -0.0024779 | -0.0084684 | 0.0029138 | -0.032699 | 0.041357 | 0.0055349 | 0.003497 | 0.09613 | 0.073242 | 0.09613 | 0.14191 | 0.11444 | 0.064087 | -0.068665 | 0.086975 | 0.11902 | 0.009155 | 0.027466 | 0.032043 | 0.07782 | -0.013733 | 122.5159 | 122.3831 | 0.018311 | 122.525 | 122.5937 | 0.21057 | 0 | 122.5296 | 122.438 | -0.068664 | 122.5388 | 122.4609 | 0.022888 | -0.064087 | 122.5662 | 122.5479 | 122.5479 | -0.16479 | 122.4792 | 122.4838 | 122.5708 | -0.10986
2620.2656 | 122.7814 | -122.5021 | 0.082397 | -0.00091566 | 0.014975 | 0.0037983 | 0.0033305 | 0.051443 | -0.00050411 | -0.0061095 | 0.0067901 | 0.0029138 | -0.030777 | 0.042639 | 0.0087391 | 0.0071286 | 0.032043 | -0.018311 | -0.004578 | 0.064087 | 0.17395 | 0.032043 | -0.09613 | -0.022888 | 0.004578 | -0.10071 | 0.059509 | 0.064087 | 0.036621 | -0.045776 | 122.5342 | 122.406 | 0.091553 | 122.4838 | 122.5662 | 0.16022 | -0.050354 | 122.5388 | 122.4564 | -0.022888 | 122.4792 | 122.4014 | -0.054932 | -0.01831 | 122.6761 | 122.5342 | 122.4976 | -0.17853 | 122.5616 | 122.5662 | 122.5067 | -0.12817
2622.0312 | 122.6532 | -122.5204 | 0.10986 | -0.00091566 | 0.01583 | 0.0059345 | 0.0056803 | 0.053152 | -0.0034949 | -0.0022643 | -0.00083936 | 0.0020594 | -0.032272 | 0.041357 | 0.0044667 | 0.006915 | 0.068665 | 0.07782 | 0.073242 | 0.12817 | 0.14648 | 0.041199 | -0.09613 | -0.013733 | 0.054932 | -0.073242 | 0.054932 | 0.07782 | 0.013733 | -0.054932 | 122.5616 | 122.4243 | 0.036621 | 122.5983 | 122.6486 | 0.2243 | -0.041198 | 122.5342 | 122.4655 | -0.054931 | 122.5067 | 122.4472 | -0.01831 | -0.032043 | 122.6669 | 122.5891 | 122.5937 | -0.20599 | 122.5754 | 122.5983 | 122.5754 | -0.16479
2623.7812 | 122.7859 | -122.4838 | 0.09613 | -0.0085447 | 0.013907 | 0.0033709 | 0.0029031 | 0.055288 | -0.00093131 | -0.0024779 | -0.0084684 | 0.0014184 | -0.03099 | 0.040716 | 0.0061757 | 0.0062742 | 0.07782 | 0.068665 | 0.10071 | 0.14648 | 0.14648 | 0.059509 | -0.086975 | 0.068665 | 0.11902 | -0.013733 | 0.032043 | 0.022888 | 0.068665 | -0.004578 | 122.5433 | 122.3969 | 0.050354 | 122.5525 | 122.6303 | 0.23346 | -0.01831 | 122.5525 | 122.4792 | -0.064087 | 122.5525 | 122.4701 | -0.009155 | -0.073242 | 122.6303 | 122.5616 | 122.5845 | -0.1831 | 122.5159 | 122.5067 | 122.6028 | -0.10071
2625.5 | 122.7905 | -122.4838 | 0.091553 | 0.0067138 | 0.017538 | 0.0018757 | 0.0076029 | 0.053365 | 0.00013669 | -0.0029053 | -0.00083936 | 0.0014184 | -0.03099 | 0.041571 | 0.0059621 | 0.0067014 | 0.068665 | 0.045776 | 0.064087 | 0.12817 | 0.16022 | 0.041199 | -0.10071 | 0.027466 | 0.10071 | -0.054932 | 0.059509 | 0.054932 | 0.041199 | -0.054932 | 122.525 | 122.3831 | 0.068664 | 122.5296 | 122.612 | 0.22888 | -0.022888 | 122.525 | 122.4289 | -0.032044 | 122.5113 | 122.4289 | 0 | -0.036621 | 122.644 | 122.5525 | 122.5479 | -0.19226 | 122.5433 | 122.5388 | 122.5845 | -0.14649
2627.25 | 122.7356 | -122.5021 | 0.10529 | -0.00091566 | 0.015402 | 0.0029437 | 0.0018351 | 0.056356 | 0.0014185 | -0.0037597 | 0.0067901 | 0.0035546 | -0.03099 | 0.041571 | 0.0087391 | 0.0067014 | 0.032043 | -0.004578 | 0 | 0.09613 | 0.15106 | 0.022888 | -0.09613 | -0.027466 | 0.004578 | -0.14191 | 0.050354 | 0.064087 | 0.013733 | -0.064087 | 122.525 | 122.406 | 0.045776 | 122.4976 | 122.5983 | 0.19226 | -0.073243 | 122.5159 | 122.438 | -0.054932 | 122.4747 | 122.3602 | -0.07782 | -0.041199 | 122.6532 | 122.5342 | 122.5021 | -0.20142 | 122.5525 | 122.5662 | 122.5067 | -0.16937
2628.9531 | 122.7264 | -122.525 | 0.11902 | -0.0085447 | 0.012412 | 0.0050799 | 0.0084573 | 0.053365 | -0.0084081 | -0.0058959 | -0.00083936 | -0.002854 | -0.032272 | 0.039221 | 0.0014759 | 0.0092648 | 0.050354 | 0.082397 | 0.1236 | 0.15106 | 0.14191 | 0.045776 | -0.086975 | 0.027466 | 0.11444 | 0 | 0.022888 | 0.050354 | 0.059509 | -0.022888 | 122.5708 | 122.438 | 0.022888 | 122.6074 | 122.6761 | 0.23804 | -0.068665 | 122.5845 | 122.5021 | -0.096131 | 122.5525 | 122.525 | 0.022888 | -0.068665 | 122.6669 | 122.5754 | 122.6486 | -0.20599 | 122.5479 | 122.5754 | 122.6395 | -0.14191
2630.7188 | 122.8134 | -122.493 | 0.082397 | -0.00091566 | 0.015402 | 0.0020893 | 0.0048257 | 0.053792 | -0.00071771 | -0.0039733 | -0.00083936 | 0.0007776 | -0.029281 | 0.041144 | 0.0040395 | 0.0047788 | 0.10529 | 0.11444 | 0.11902 | 0.17395 | 0.10529 | 0.064087 | -0.068665 | 0.07782 | 0.13275 | 0 | 0.027466 | 0.027466 | 0.059509 | -0.009155 | 122.5571 | 122.4243 | 0.022889 | 122.6074 | 122.6669 | 0.24261 | 0.022889 | 122.5525 | 122.4838 | -0.054931 | 122.5708 | 122.493 | 0.009155 | -0.054931 | 122.5983 | 122.5983 | 122.612 | -0.15106 | 122.5204 | 122.5204 | 122.6257 | -0.091552
2632.4844 | 122.6898 | -122.5113 | 0.11902 | -0.016174 | 0.017111 | 0.0018757 | 0.0073893 | 0.052511 | -0.0037085 | -0.0014099 | -0.00083936 | 0.003341 | -0.030777 | 0.04328 | 0.0031849 | 0.0039242 | 0.022888 | 0.009155 | 0.032043 | 0.07782 | 0.16479 | 0 | -0.1236 | -0.041199 | 0.027466 | -0.10986 | 0.073242 | 0.086975 | 0.022888 | -0.050354 | 122.5113 | 122.3877 | 0.045776 | 122.5204 | 122.5891 | 0.20142 | -0.096131 | 122.5342 | 122.4609 | -0.045777 | 122.4701 | 122.4014 | -0.059509 | -0.032044 | 122.6761 | 122.5342 | 122.5433 | -0.24261 | 122.5845 | 122.5983 | 122.5388 | -0.16937
2634.2344 | 122.8271 | -122.5021 | 0.086975 | 0.0067138 | 0.019461 | 0.0035847 | 0.0031167 | 0.053365 | 0.00013669 | -0.0033325 | -0.0084684 | 0.003341 | -0.028427 | 0.042639 | 0.0068165 | 0.0060604 | 0.082397 | 0.045776 | 0.054932 | 0.12817 | 0.16479 | 0.027466 | -0.10529 | 0.032043 | 0.073242 | -0.073242 | 0.054932 | 0.073242 | 0.041199 | -0.027466 | 122.5296 | 122.3968 | 0.07782 | 122.5479 | 122.6303 | 0.23346 | -0.004578 | 122.5433 | 122.4747 | -0.032043 | 122.5342 | 122.4289 | -0.045776 | -0.013733 | 122.6669 | 122.5845 | 122.5571 | -0.19226 | 122.5571 | 122.5754 | 122.5754 | -0.11444
2635.9844 | 122.8043 | -122.4976 | 0.073242 | -0.00091566 | 0.017325 | 0.0040119 | 0.0086709 | 0.053365 | -7.6908e-05 | -0.0011963 | -0.00083936 | 0.003341 | -0.029708 | 0.041998 | 0.0040395 | 0.0067014 | 0.041199 | 0.027466 | 0.041199 | 0.11902 | 0.14648 | 0.041199 | -0.091553 | 0.032043 | 0.082397 | -0.064087 | 0.068665 | 0.082397 | 0.027466 | -0.050354 | 122.5388 | 122.406 | 0.073242 | 122.525 | 122.6166 | 0.21057 | -0.032043 | 122.525 | 122.4472 | -0.004577 | 122.5296 | 122.4335 | -0.013733 | 0.009155 | 122.644 | 122.5388 | 122.5388 | -0.16479 | 122.5662 | 122.58 | 122.58 | -0.1236
2637.7344 | 122.8134 | -122.5113 | 0.07782 | -0.00091566 | 0.014334 | 0.0029437 | 0.0067483 | 0.053365 | -0.0034949 | -0.00055532 | 0.0067901 | 0.0020594 | -0.032699 | 0.041144 | 0.0053211 | 0.0056332 | 0.004578 | 0.013733 | 0.022888 | 0.10071 | 0.13733 | 0.018311 | -0.11444 | -0.013733 | 0.054932 | -0.07782 | 0.086975 | 0.091553 | 0.036621 | -0.068665 | 122.5296 | 122.3969 | 0.059509 | 122.525 | 122.612 | 0.21515 | -0.073242 | 122.5479 | 122.4426 | 0.009155 | 122.4976 | 122.4335 | -0.009155 | 0.013733 | 122.6486 | 122.5159 | 122.5342 | -0.19226 | 122.5983 | 122.6028 | 122.5662 | -0.14649
2639.4375 | 122.7264 | -122.5571 | 0.10986 | -0.0085447 | 0.017538 | 0.0042255 | 0.0078165 | 0.052938 | -0.0064855 | -0.0029053 | -0.00083936 | -0.0002906 | -0.028213 | 0.039862 | 0.00019427 | 0.0077694 | 0.004578 | 0.009155 | 0.027466 | 0.082397 | 0.17395 | 0.032043 | -0.11902 | -0.054932 | 0.036621 | -0.10071 | 0.059509 | 0.091553 | 0.013733 | -0.054932 | 122.5891 | 122.438 | 0.064087 | 122.5662 | 122.6395 | 0.20142 | -0.10529 | 122.5708 | 122.5021 | -0.050354 | 122.5021 | 122.4564 | -0.045776 | -0.01831 | 122.731 | 122.5616 | 122.5845 | -0.22888 | 122.6166 | 122.6486 | 122.5937 | -0.16479
2641.1875 | 122.7356 | -122.5616 | 0.10071 | 0.0067138 | 0.014334 | 0.0076435 | 0.0084573 | 0.050588 | -0.0069129 | -0.0050415 | -0.00083936 | -0.0013586 | -0.033554 | 0.036871 | -0.00044673 | 0.006915 | 0.091553 | 0.15564 | 0.16022 | 0.16937 | 0.1236 | 0.068665 | -0.068665 | 0.059509 | 0.18768 | 0.036621 | 0.027466 | 0.032043 | 0.064087 | -0.013733 | 122.6303 | 122.493 | 0.022888 | 122.7173 | 122.731 | 0.23804 | -0.009155 | 122.6257 | 122.5479 | -0.073242 | 122.6212 | 122.5983 | 0.050354 | -0.068665 | 122.6852 | 122.6532 | 122.7219 | -0.16937 | 122.5891 | 122.5937 | 122.7493 | -0.11444

## Thermal Data
Fire Time | B Position - Tray - Middle
-0.8083 | 8.5995
0.1917 | 8.6097
1.1917 | 8.6122
2.1917 | 8.5995
3.1917 | 8.6119
4.1917 | 8.6006
5.1917 | 8.6892
6.1917 | 9.2513
7.1917 | 10.2877
8.1917 | 13.2324
9.1917 | 15.108
10.1917 | 18.0364
11.2073 | 21.7408
12.1917 | 24.9041
13.1917 | 27.3131
14.1917 | 31.0136
15.1917 | 33.5944
16.1917 | 36.9124
17.1917 | 39.1349
18.1917 | 41.8994
19.1917 | 44.3829
20.1917 | 46.4948
21.1917 | 49.0312
22.1917 | 51.7551
23.1917 | 54.185
24.1917 | 57.1338
25.1917 | 58.9554
26.1917 | 61.8986
27.1917 | 64.3171
28.1917 | 67.5503
29.1917 | 69.6307
30.1917 | 73.7012
31.1917 | 76.1895
32.1917 | 78.8943
33.1917 | 81.0493
34.1917 | 84.2199
35.1917 | 85.3259
36.1917 | 86.7142
37.1917 | 88.6684
38.1917 | 90.4437
39.1917 | 91.9353
40.1917 | 94.051
41.2073 | 96.5869
42.1917 | 98.5021
43.1917 | 100.481
44.1917 | 102.4681
45.1917 | 103.2748
46.1917 | 103.9767
47.1917 | 104.7947
48.1917 | 105.9509
49.1917 | 108.7622
50.1917 | 109.4611
51.1917 | 110.4703
52.1917 | 111.0193
53.1917 | 112.3446
54.1917 | 114.1025
55.1917 | 115.4078
56.1917 | 117.2042
57.1917 | 118.2651
58.1917 | 119.9243
59.1917 | 121.2776
60.1917 | 122.218
61.1917 | 122.8764
62.1917 | 123.4141
63.1917 | 124.2145
64.1917 | 124.505
65.1917 | 124.6988
66.1917 | 124.802
67.1917 | 124.9606
68.1917 | 126.0489
69.2073 | 127.1387
70.1917 | 127.422
71.1917 | 128.0179
72.1917 | 128.723
73.1917 | 129.5682
74.1917 | 130.2056
75.1917 | 130.8949
76.1917 | 131.3399
77.1917 | 131.6098
78.1917 | 131.8026
79.1917 | 131.6452
80.1917 | 132.4236
81.1917 | 132.8869
82.1917 | 132.934
83.1917 | 133.6431
84.1917 | 133.7936
85.1917 | 133.9784
86.1917 | 134.0114
87.1917 | 133.8296
88.1917 | 133.8977
89.1917 | 134.4386
90.1917 | 135.2711
91.1917 | 136.0183
92.1917 | 136.5136
93.2073 | 136.8696
94.1917 | 137.1043
95.1917 | 137.2039
96.1917 | 137.074
97.2073 | 137.2649
98.1917 | 138.2573
99.2073 | 139.6622
100.1917 | 139.9557
101.1917 | 140.7706
102.1917 | 141.2307
103.1917 | 141.4144
104.1917 | 142.0661
105.1917 | 141.7623
106.1917 | 141.2134
107.1917 | 141.0979
108.1917 | 141.4175
109.1917 | 141.5723
110.1917 | 141.8339
111.1917 | 142.4634
112.1917 | 142.503
113.1917 | 143.8448
114.1917 | 144.8039
115.1917 | 145.1183
116.1917 | 145.5693
117.1917 | 145.6038
118.1917 | 146.0182
119.1917 | 146.1465
120.1917 | 146.1506
121.1917 | 146.7408
122.1917 | 147.0606
123.1917 | 147.4949
124.1917 | 148.3506
125.1917 | 148.2444
126.1917 | 148.3107
127.1917 | 148.8905
128.1917 | 149.6255
129.1917 | 150.5992
130.1917 | 150.6684
131.1917 | 150.7992
132.1917 | 151.4253
133.1917 | 151.5189
134.1917 | 152.3164
135.1917 | 152.4445
136.1917 | 152.4096
137.1917 | 152.7672
138.1917 | 152.9977
139.1917 | 152.8088
140.1917 | 152.5744
141.1917 | 152.2764
142.1917 | 152.2814
143.1917 | 152.0483
144.1917 | 151.9458
145.1917 | 151.8445
146.1917 | 151.9753
147.1917 | 152.0279
148.1917 | 152.8868
149.1917 | 152.9737
150.1917 | 153.3311
151.1917 | 153.7842
152.1917 | 154.862
153.1917 | 156.1106
154.1917 | 156.6195
155.1917 | 157.3767
156.1917 | 157.4114
157.1917 | 157.2364
158.1917 | 157.2415
159.1917 | 157.9302
160.1917 | 159.1812
161.1917 | 158.2532
162.2073 | 158.8829
163.1917 | 159.8206
164.1917 | 160.2697
165.1917 | 159.8186
166.1917 | 160.0038
167.1917 | 159.567
168.1917 | 160.1343
169.1917 | 160.3692
170.1917 | 161.2173
171.1917 | 161.8505
172.1917 | 162.092
173.1917 | 161.6584
174.1917 | 161.2078
175.1917 | 161.1775
176.1917 | 162.3538
177.1917 | 162.3842
178.1917 | 162.6749
179.1917 | 162.4164
180.1917 | 162.4195
181.1917 | 162.567
182.1917 | 162.8959
183.1917 | 163.2285
184.1917 | 163.2057
185.1917 | 163.9298
186.1917 | 164.9233
187.1917 | 164.9517
188.1917 | 165.1683
189.1917 | 165.3068
190.1917 | 166.4321
191.1917 | 167.1778
192.1917 | 167.6261
193.1917 | 167.5175
194.1917 | 167.8243
195.1917 | 167.5993
196.1917 | 167.4964
197.1917 | 167.6916
198.1917 | 167.5015
199.1917 | 168.5812
200.1917 | 169.18
201.1917 | 169.5382
202.1917 | 169.0905
203.1917 | 169.3206
204.1917 | 168.5509
205.1917 | 168.1411
206.1917 | 168.6738
207.1917 | 169.1658
208.1917 | 168.8457
209.1917 | 168.8285
210.1917 | 168.7492
211.1917 | 168.7249
212.1917 | 169.1269
213.1917 | 169.1293
214.1917 | 168.999
215.1917 | 168.7764
216.1917 | 169.146
217.1917 | 169.4133
218.1917 | 169.6437
219.1917 | 170.0802
220.1917 | 169.8148
221.1917 | 171.4202
222.1917 | 172.5385
223.1917 | 173.0233
224.1917 | 173.7516
225.1917 | 174.2969
226.1917 | 174.272
227.1917 | 174.5007
228.1917 | 174.5522
229.1917 | 175.1004
230.1917 | 175.2653
231.1917 | 174.5868
232.1917 | 174.5379
233.1917 | 174.9033
234.1917 | 175.0336
235.1917 | 175.1301
236.1917 | 174.9884
237.1917 | 174.6003
238.1917 | 174.5782
239.1917 | 175.5979
240.1917 | 175.9571
241.1917 | 175.8859
242.1917 | 176.4498
243.1917 | 176.9383
244.1917 | 177.0164
245.1917 | 178.9743
246.1917 | 179.9859
247.1917 | 180.6225
248.1917 | 180.5
249.1917 | 179.8253
250.1917 | 179.2164
251.1917 | 179.2287
252.1917 | 180.6536
253.1917 | 180.5963
254.1917 | 180.9502
255.1917 | 182.146
256.1917 | 183.0703
257.1917 | 183.3533
258.1917 | 183.422
259.1917 | 184.0584
260.1917 | 184.3446
261.1917 | 184.6684
262.1917 | 185.019
263.1917 | 185.3588
264.1917 | 186.0739
265.1917 | 186.0679
266.1917 | 185.8934
267.1917 | 185.0524
268.1917 | 184.8063
269.1917 | 184.2418
270.1917 | 183.8295
271.1917 | 183.6141
272.1917 | 184.3532
273.1917 | 183.9646
274.1917 | 184.633
275.1917 | 185.2322
276.1917 | 185.3861
277.1917 | 185.5043
278.1917 | 185.9917
279.1917 | 186.0821
280.1917 | 186.9855
281.1917 | 186.9151
282.1917 | 186.725
283.1917 | 187.4635
284.1917 | 186.8961
285.1917 | 187.169
286.1917 | 187.1353
287.1917 | 187.4844
288.1917 | 187.6659
289.1917 | 187.9916
290.1917 | 188.1627
291.1917 | 188.7324
292.1917 | 188.637
293.1917 | 188.952
294.1917 | 189.1496
295.1917 | 189.6447
296.1917 | 190.4362
297.1917 | 190.7916
298.1917 | 190.9282
299.1917 | 191.7945
300.1917 | 193.0604
301.1917 | 193.3864
302.1917 | 193.2771
303.1917 | 193.1955
304.1917 | 193.0384
305.2073 | 193.4369
306.1917 | 194.0406
307.1917 | 194.4034
308.1917 | 194.8979
309.1917 | 195.5761
310.1917 | 195.384
311.2073 | 196.3009
312.1917 | 197.3129
313.1917 | 197.4794
314.1917 | 197.8925
315.1917 | 198.151
316.1917 | 198.09
317.1917 | 198.1507
318.1917 | 197.8466
319.1917 | 198.7138
320.1917 | 198.8186
321.1917 | 198.5314
322.1917 | 198.7214
323.1917 | 199.2226
324.1917 | 198.6054
325.1917 | 198.4556
326.1917 | 198.1796
327.1917 | 197.7876
328.1917 | 196.6965
329.1917 | 196.8298
330.1917 | 196.4792
331.1917 | 196.3659
332.1917 | 195.9985
333.1917 | 195.9477
334.1917 | 195.6756
335.1917 | 195.322
336.1917 | 194.7531
337.1917 | 194.3444
338.1917 | 194.3295
339.1917 | 194.8741
340.1917 | 194.8523
341.1917 | 196.5473
342.1917 | 196.942
343.1917 | 196.5173
344.1917 | 195.9756
345.1917 | 196.2943
346.1917 | 196.3215
347.1917 | 195.7575
348.1917 | 195.5983
349.1917 | 195.9326
350.1917 | 196.3421
351.1917 | 196.3135
352.1917 | 197.0419
353.1917 | 197.156
354.1917 | 198.0273
355.1917 | 198.4085
356.1917 | 198.492
357.1917 | 198.288
358.1917 | 197.9013
359.1917 | 198.3337
360.1917 | 198.3946
361.1917 | 199.5316
362.1917 | 199.9897
363.1917 | 201.4936
364.1917 | 201.9392
365.1917 | 201.7088
366.1917 | 201.9837
367.1917 | 201.5142
368.1917 | 201.1886
369.1917 | 200.9344
370.1917 | 201.003
371.1917 | 200.9557
372.1917 | 201.8017
373.1917 | 202.1404
374.1917 | 202.3862
375.1917 | 202.5818
376.1917 | 201.5175
377.1917 | 202.5881
378.1917 | 203.2003
379.1917 | 202.4525
380.1917 | 202.1923
381.1917 | 202.2141
382.1917 | 201.4134
383.1917 | 201.1398
384.1917 | 201.1884
385.1917 | 200.972
386.1917 | 200.5797
387.1917 | 200.1757
388.1917 | 200.6851
389.1917 | 201.203
390.1917 | 200.7335
391.1917 | 200.5556
392.1917 | 200.7826
393.1917 | 200.8083
394.1917 | 201.0176
395.1917 | 201.5762
396.1917 | 202.1756
397.1917 | 202.8866
398.1917 | 202.1897
399.1917 | 201.8278
400.1917 | 201.7701
401.1917 | 201.7986
402.1917 | 201.5775
403.1917 | 201.5867
404.1917 | 201.9116
405.1917 | 202.2137
406.1917 | 202.1592
407.1917 | 201.9275
408.1917 | 202.6014
409.1917 | 202.8855
410.1917 | 202.7837
411.1917 | 202.8759
412.1917 | 202.7915
413.1917 | 202.6953
414.1917 | 202.8245
415.1917 | 203.3438
416.1917 | 204.4289
417.1917 | 204.2195
418.1917 | 203.8109
419.1917 | 203.7135
420.1917 | 204.3113
421.1917 | 204.134
422.1917 | 204.0707
423.1917 | 204.1808
424.1917 | 204.0901
425.2073 | 203.9812
426.1917 | 204.1163
427.1917 | 203.0955
428.1917 | 203.1218
429.1917 | 203.0382
430.1917 | 203.2893
431.1917 | 203.0472
432.1917 | 202.681
433.1917 | 202.1239
434.1917 | 201.6053
435.1917 | 201.1695
436.1917 | 200.8715
437.1917 | 200.751
438.1917 | 200.6083
439.1917 | 200.1912
440.1917 | 200.0001
441.1917 | 199.9408
442.1917 | 200.3322
443.1917 | 200.2025
444.1917 | 199.9629
445.1917 | 199.9273
446.1917 | 200.0362
447.1917 | 201.0145
448.1917 | 201.9682
449.1917 | 202.7709
450.1917 | 202.4878
451.1917 | 202.421
452.1917 | 202.7546
453.1917 | 202.8426
454.1917 | 204.2123
455.1917 | 205.1209
456.1917 | 204.7334
457.1917 | 205.4122
458.1917 | 205.5305
459.1917 | 206.1495
460.1917 | 205.9748
461.1917 | 205.7485
462.1917 | 205.8646
463.1917 | 205.0297
464.1917 | 204.5674
465.1917 | 205.8599
466.1917 | 206.1291
467.1917 | 206.7172
468.1917 | 207.7068
469.1917 | 208.3613
470.1917 | 209.2606
471.1917 | 209.768
472.1917 | 210.4429
473.1917 | 211.1251
474.1917 | 211.7692
475.1917 | 211.8934
476.1917 | 212.2302
477.1917 | 213.1531
478.1917 | 212.7316
479.1917 | 212.5755
480.1917 | 212.4722
481.1917 | 211.7603
482.1917 | 212.2526
483.1917 | 212.0668
484.1917 | 212.1069
485.1917 | 211.6501
486.1917 | 211.7798
487.1917 | 211.7332
488.1917 | 212.5589
489.1917 | 213.2253
490.1917 | 212.9909
491.1917 | 212.4362
492.1917 | 212.1012
493.1917 | 212.4943
494.1917 | 211.7981
495.1917 | 212.1214
496.1917 | 211.941
497.1917 | 212.6204
498.1917 | 213.5522
499.1917 | 214.2896
500.1917 | 215.158
501.1917 | 215.6885
502.1917 | 215.6796
503.1917 | 216.1117
504.1917 | 216.1835
505.1917 | 216.3115
506.1917 | 217.0189
507.1917 | 216.5136
508.1917 | 215.9767
509.1917 | 215.5071
510.1917 | 214.9758
511.1917 | 214.5609
512.1917 | 214.405
513.1917 | 213.915
514.1917 | 214.5224
515.1917 | 215.8581
516.1917 | 215.6088
517.1917 | 215.6102
518.1917 | 216.7886
519.1917 | 217.6802
520.1917 | 217.819
521.1917 | 217.827
522.1917 | 218.176
523.1917 | 217.7178
524.1917 | 217.9252
525.1917 | 217.8071
526.1917 | 218.3215
527.1917 | 218.0965
528.1917 | 218.2851
529.1917 | 217.8612
530.1917 | 217.7568
531.1917 | 217.8701
532.1917 | 218.5369
533.1917 | 218.9098
534.1917 | 218.0869
535.1917 | 218.4155
536.1917 | 218.9641
537.1917 | 219.0759
538.1917 | 218.6542
539.1917 | 219.708
540.1917 | 220.3146
541.1917 | 221.3295
542.1917 | 222.2358
543.1917 | 222.7524
544.1917 | 222.5466
545.1917 | 222.4725
546.1917 | 222.5604
547.1917 | 222.2239
548.1917 | 221.1993
549.1917 | 220.4528
550.1917 | 218.7768
551.1917 | 217.8344
552.1917 | 217.6809
553.1917 | 217.6107
554.1917 | 217.732
555.1917 | 217.4622
556.1917 | 217.5067
557.1917 | 217.3324
558.1917 | 217.2496
559.1917 | 217.2128
560.1917 | 216.6317
561.1917 | 215.7977
562.1917 | 215.2284
563.1917 | 215.1898
564.1917 | 214.8542
565.1917 | 215.1634
566.1917 | 214.9141
567.1917 | 214.6025
568.1917 | 214.0946
569.1917 | 214.1933
570.1917 | 214.7239
571.1917 | 214.4496
572.1917 | 214.1466
573.1917 | 215.1446
574.1917 | 214.952
575.1917 | 214.871
576.1917 | 214.9343
577.1917 | 214.6179
578.1917 | 215.1995
579.1917 | 215.1259
580.1917 | 214.7529
581.1917 | 214.6919
582.1917 | 215.069
583.1917 | 214.772
584.1917 | 215.4917
585.1917 | 215.8343
586.1917 | 216.1423
587.1917 | 215.9334
588.1917 | 215.8903
589.1917 | 215.5436
590.1917 | 215.5668
591.1917 | 214.6728
592.1917 | 214.4677
593.1917 | 215.9138
594.1917 | 216.8546
595.1917 | 219.4689
596.1917 | 220.3317
597.1917 | 219.6716
598.1917 | 220.2219
599.1917 | 221.1361
600.1917 | 221.0592
601.1917 | 221.3707
602.1917 | 220.9104
603.1917 | 220.2934
604.1917 | 219.7498
605.1917 | 219.1121
606.1917 | 218.7502
607.1917 | 218.2438
608.1917 | 218.1173
609.1917 | 217.7232
610.1917 | 217.356
611.1917 | 216.9872
612.1917 | 217.1546
613.1917 | 217.6023
614.1917 | 217.1935
615.1917 | 217.1628
616.1917 | 217.2122
617.1917 | 217.1442
618.1917 | 217.6671
619.1917 | 218.1621
620.1917 | 218.7025
621.1917 | 218.7049
622.1917 | 219.0266
623.1917 | 219.1588
624.1917 | 218.5244
625.1917 | 218.2636
626.1917 | 218.3173
627.1917 | 218.0634
628.1917 | 217.809
629.1917 | 218.1944
630.1917 | 218.2016
631.1917 | 218.0921
632.1917 | 217.467
633.1917 | 217.4007
634.1917 | 217.1474
635.1917 | 216.6502
636.1917 | 216.9231
637.1917 | 217.3067
638.1917 | 217.4822
639.1917 | 217.0276
640.1917 | 218.0933
641.1917 | 217.7204
642.1917 | 217.0414
643.1917 | 216.5306
644.1917 | 216.0355
645.1917 | 215.3547
646.1917 | 215.8335
647.1917 | 216.2633
648.1917 | 216.4219
649.1917 | 216.9944
650.1917 | 217.0126
651.1917 | 216.9966
652.1917 | 216.9887
653.1917 | 216.7925
654.1917 | 216.7068
655.1917 | 216.5184
656.1917 | 216.9757
657.1917 | 217.0678
658.1917 | 216.5569
659.1917 | 216.9431
660.1917 | 217.9283
661.1917 | 217.4713
662.1917 | 217.647
663.1917 | 217.7031
664.1917 | 217.6024
665.2073 | 218.3473
666.1917 | 218.075
667.1917 | 218.3633
668.1917 | 218.1068
669.1917 | 218.3292
670.1917 | 218.6862
671.1917 | 218.7346
672.1917 | 218.7944
673.1917 | 219.2649
674.1917 | 219.5049
675.1917 | 219.3848
676.1917 | 219.4502
677.1917 | 219.5166
678.1917 | 219.0505
679.1917 | 219.2038
680.1917 | 219.7433
681.1917 | 219.2524
682.1917 | 219.3375
683.1917 | 219.8167
684.1917 | 220.0823
685.1917 | 220.2997
686.1917 | 221.4903
687.2073 | 221.0163
688.1917 | 220.8624
689.1917 | 220.7735
690.1917 | 220.766
691.2073 | 220.8154
692.1917 | 220.81
693.1917 | 220.7703
694.1917 | 221.1341
695.1917 | 221.4437
696.1917 | 221.4251
697.2073 | 220.9123
698.1917 | 220.4745
699.1917 | 220.3794
700.1917 | 220.6865
701.1917 | 221.8179
702.1917 | 222.7528
703.2073 | 223.3952
704.1917 | 223.6
705.1917 | 223.8697
706.1917 | 224.1338
707.2073 | 223.3906
708.1917 | 222.8407
709.2073 | 222.7549
710.1917 | 223.2206
711.2073 | 224.2583
712.1917 | 223.8153
713.1917 | 223.8088
714.1917 | 223.2176
715.1917 | 222.7665
716.1917 | 222.3974
717.1917 | 222.5843
718.1917 | 222.991
719.1917 | 223.069
720.1917 | 224.151
721.1917 | 225.1724
722.1917 | 225.1406
723.1917 | 224.4617
724.1917 | 224.6609
725.2073 | 224.3031
726.1917 | 224.2383
727.1917 | 224.922
728.1917 | 224.001
729.1917 | 224.0771
730.1917 | 224.3063
731.1917 | 224.5424
732.1917 | 224.9927
733.1917 | 226.2397
734.1917 | 226.0253
735.1917 | 225.3148
736.1917 | 224.3295
737.1917 | 225.0186
738.1917 | 226.1348
739.1917 | 226.8913
740.1917 | 227.3533
741.1917 | 228.0506
742.1917 | 228.8904
743.1917 | 229.0999
744.1917 | 229.1855
745.1917 | 228.5373
746.1917 | 228.4974
747.1917 | 226.6815
748.1917 | 224.6882
749.1917 | 223.1793
750.1917 | 223.1186
751.1917 | 223.6833
752.1917 | 224.1318
753.1917 | 223.0466
754.1917 | 222.2767
755.1917 | 221.3747
756.1917 | 220.4977
757.1917 | 219.792
758.1917 | 219.5943
759.1917 | 218.4278
760.1917 | 217.8694
761.1917 | 217.9251
762.1917 | 219.0805
763.1917 | 219.4033
764.1917 | 219.1238
765.1917 | 219.0951
766.1917 | 218.78
767.1917 | 217.9269
768.1917 | 218.3865
769.1917 | 219.8126
770.1917 | 220.3788
771.1917 | 220.685
772.1917 | 221.9606
773.1917 | 221.8491
774.1917 | 221.6252
775.1917 | 221.6307
776.1917 | 221.8554
777.1917 | 222.6388
778.1917 | 223.4676
779.1917 | 223.5441
780.1917 | 224.4039
781.1917 | 225.297
782.1917 | 227.2165
783.1917 | 228.8912
784.1917 | 229.4937
785.1917 | 229.3301
786.1917 | 229.1132
787.1917 | 228.7062
788.1917 | 228.3304
789.1917 | 228.0626
790.1917 | 228.0897
791.1917 | 227.9459
792.1917 | 228.0573
793.1917 | 228.8626
794.1917 | 229.165
795.1917 | 229.5715
796.1917 | 228.9118
797.1917 | 228.7408
798.1917 | 230.0864
799.1917 | 231.2113
800.1917 | 232.2263
801.1917 | 232.6491
802.1917 | 232.4159
803.1917 | 231.9841
804.1917 | 231.3551
805.1917 | 230.7141
806.1917 | 230.6731
807.1917 | 231.4931
808.1917 | 231.3963
809.1917 | 231.4426
810.1917 | 232.5992
811.1917 | 232.0649
812.1917 | 231.5805
813.1917 | 230.879
814.1917 | 229.8765
815.1917 | 229.0319
816.1917 | 229.4577
817.1917 | 229.3218
818.1917 | 228.6845
819.1917 | 228.6579
820.1917 | 229.253
821.1917 | 229.9419
822.1917 | 230.8208
823.1917 | 231.9584
824.1917 | 231.9745
825.1917 | 231.0776
826.1917 | 230.6801
827.1917 | 231.1098
828.1917 | 230.9652
829.1917 | 230.529
830.1917 | 230.4155
831.1917 | 230.8721
832.1917 | 230.0014
833.1917 | 229.9195
834.1917 | 229.907
835.1917 | 230.6323
836.1917 | 231.324
837.1917 | 232.0143
838.1917 | 231.3183
839.1917 | 230.8947
840.1917 | 230.7379
841.1917 | 230.2051
842.1917 | 230.2408
843.1917 | 230.0244
844.1917 | 230.0284
845.2073 | 230.1082
846.1917 | 230.1299
847.1917 | 230.2774
848.1917 | 230.6876
849.1917 | 231.0565
850.1917 | 231.9068
851.1917 | 233.5118
852.1917 | 232.9603
853.1917 | 234.0777
854.1917 | 234.5393
855.1917 | 235.0809
856.1917 | 235.0941
857.1917 | 235.2349
858.1917 | 235.9713
859.1917 | 236.504
860.1917 | 236.5899
861.1917 | 236.5652
862.1917 | 235.6633
863.1917 | 235.8298
864.1917 | 236.1298
865.1917 | 237.0359
866.1917 | 237.2337
867.1917 | 237.539
868.1917 | 236.6538
869.1917 | 235.2105
870.1917 | 234.8011
871.1917 | 234.2761
872.1917 | 234.6214
873.1917 | 234.5418
874.1917 | 235.0049
875.1917 | 235.7318
876.1917 | 236.8168
877.1917 | 237.2011
878.1917 | 237.5576
879.1917 | 237.3154
880.1917 | 236.6184
881.1917 | 236.4342
882.2073 | 236.546
883.1917 | 237.2401
884.1917 | 237.0905
885.1917 | 236.5528
886.1917 | 236.3174
887.1917 | 235.9265
888.1917 | 234.9064
889.1917 | 234.6296
890.1917 | 234.5131
891.1917 | 234.0632
892.1917 | 233.404
893.1917 | 233.0945
894.1917 | 233.7789
895.1917 | 235.2323
896.1917 | 234.8927
897.1917 | 234.5251
898.1917 | 235.129
899.1917 | 234.6188
900.1917 | 234.2777
901.1917 | 234.8582
902.1917 | 236.0662
903.1917 | 237.7997
904.1917 | 237.9138
905.1917 | 239.3426
906.1917 | 239.9455
907.1917 | 240.4467
908.1917 | 240.8125
909.1917 | 241.6165
910.1917 | 243.4834
911.1917 | 243.9445
912.2073 | 244.6832
913.1917 | 244.3514
914.1917 | 245.5936
915.1917 | 248.0392
916.1917 | 249.0145
917.1917 | 249.8246
918.1917 | 250.859
919.1917 | 250.9162
920.1917 | 251.7787
921.1917 | 252.2529
922.1917 | 252.5145
923.1917 | 251.9604
924.1917 | 252.265
925.1917 | 252.0152
926.1917 | 252.1311
927.1917 | 251.934
928.1917 | 252.1689
929.1917 | 252.762
930.1917 | 253.7953
931.1917 | 254.6409
932.1917 | 254.5874
933.1917 | 255.6624
934.1917 | 256.7969
935.1917 | 258.7836
936.1917 | 260.1194
937.1917 | 261.5767
938.1917 | 262.5808
939.1917 | 264.2629
940.1917 | 264.967
941.1917 | 267.0857
942.1917 | 269.1333
943.1917 | 270.8602
944.1917 | 271.2708
945.1917 | 272.8894
946.1917 | 273.5138
947.1917 | 274.6564
948.1917 | 275.8079
949.1917 | 275.4672
950.1917 | 275.1458
951.1917 | 274.9364
952.1917 | 274.7305
953.1917 | 275.7337
954.1917 | 276.3213
955.1917 | 278.4346
956.1917 | 278.9949
957.1917 | 279.1605
958.1917 | 278.0973
959.1917 | 277.1374
960.1917 | 276.2194
961.1917 | 275.5932
962.1917 | 276.9001
963.1917 | 277.8586
964.1917 | 276.2775
965.1917 | 276.5243
966.1917 | 275.0919
967.1917 | 272.9514
968.1917 | 272.334
969.1917 | 272.6303
970.1917 | 274.3275
971.1917 | 274.5397
972.2073 | 275.67
973.1917 | 275.937
974.1917 | 276.0921
975.1917 | 276.2293
976.1917 | 277.0869
977.1917 | 277.4034
978.1917 | 276.5463
979.1917 | 275.9289
980.1917 | 275.8086
981.1917 | 275.3452
982.1917 | 275.2849
983.1917 | 274.3882
984.1917 | 273.5427
985.1917 | 273.684
986.1917 | 273.5599
987.1917 | 272.6658
988.1917 | 271.8913
989.1917 | 271.6583
990.1917 | 272.1089
991.1917 | 271.6337
992.1917 | 272.2065
993.1917 | 271.7088
994.1917 | 271.6653
995.1917 | 271.7315
996.1917 | 272.6096
997.1917 | 272.3616
998.1917 | 272.6585
999.1917 | 272.543
1000.1917 | 272.2464
1001.1917 | 271.971
1002.1917 | 271.8579
1003.1917 | 271.9206
1004.1917 | 273.1774
1005.1917 | 272.9033
1006.1917 | 271.8837
1007.1917 | 272.8466
1008.1917 | 274.0765
1009.1917 | 273.625
1010.1917 | 273.1901
1011.1917 | 272.403
1012.1917 | 272.2997
1013.1917 | 272.6154
1014.1917 | 272.8532
1015.1917 | 273.8702
1016.1917 | 274.0341
1017.1917 | 275.1938
1018.1917 | 276.4983
1019.1917 | 277.5828
1020.1917 | 279.5619
1021.1917 | 279.8673
1022.1917 | 279.4464
1023.1917 | 279.2274
1024.1917 | 279.2286
1025.1917 | 280.0026
1026.1917 | 280.6202
1027.1917 | 281.165
1028.1917 | 279.9548
1029.1917 | 278.8625
1030.1917 | 279.0121
1031.1917 | 279.568
1032.2073 | 279.7025
1033.1917 | 279.9058
1034.1917 | 278.8127
1035.1917 | 277.9507
1036.1917 | 278.8587
1037.1917 | 279.6154
1038.1917 | 279.7384
1039.1917 | 281.2905
1040.1917 | 280.8974
1041.1917 | 281.3277
1042.1917 | 283.4403
1043.2073 | 285.2866
1044.1917 | 287.2977
1045.1917 | 287.1684
1046.1917 | 287.6258
1047.1917 | 288.0652
1048.1917 | 287.5878
1049.1917 | 286.9212
1050.1917 | 286.518
1051.1917 | 287.0835
1052.1917 | 289.3318
1053.2073 | 290.1318
1054.1917 | 289.9031
1055.1917 | 290.0934
1056.1917 | 290.7691
1057.1917 | 291.1462
1058.1917 | 292.8378
1059.1917 | 294.0809
1060.1917 | 293.6685
1061.1917 | 292.3151
1062.1917 | 292.5821
1063.2073 | 292.9174
1064.1917 | 292.9304
1065.1917 | 293.539
1066.1917 | 296.819
1067.1917 | 298.844
1068.1917 | 300.7122
1069.1917 | 303.2751
1070.1917 | 306.2479
1071.1917 | 307.3351
1072.1917 | 308.4214
1073.1917 | 308.6481
1074.1917 | 307.7322
1075.1917 | 307.7371
1076.1917 | 307.9751
1077.1917 | 307.9717
1078.1917 | 307.9416
1079.1917 | 307.3441
1080.1917 | 308.8756
1081.1917 | 310.1847
1082.1917 | 309.4973
1083.1917 | 310.6058
1084.1917 | 312.4013
1085.1917 | 315.161
1086.1917 | 314.4745
1087.1917 | 315.3844
1088.1917 | 315.666
1089.1917 | 314.9539
1090.1917 | 313.6346
1091.1917 | 313.8355
1092.2073 | 312.8016
1093.1917 | 311.828
1094.1917 | 312.2386
1095.1917 | 311.4055
1096.1917 | 309.6571
1097.1917 | 309.3278
1098.1917 | 307.882
1099.1917 | 310.1153
1100.1917 | 310.9219
1101.1917 | 311.1529
1102.1917 | 309.7974
1103.1917 | 308.9617
1104.1917 | 308.703
1105.1917 | 308.8066
1106.1917 | 309.0553
1107.1917 | 311.0666
1108.1917 | 311.5191
1109.1917 | 311.4179
1110.1917 | 311.3938
1111.1917 | 311.6069
1112.1917 | 312.7364
1113.1917 | 311.2984
1114.1917 | 314.5015
1115.1917 | 314.0495
1116.1917 | 315.1056
1117.1917 | 316.5308
1118.1917 | 315.9386
1119.1917 | 315.1235
1120.1917 | 315.2378
1121.1917 | 314.5394
1122.1917 | 313.1848
1123.1917 | 312.4095
1124.1917 | 311.1979
1125.1917 | 311.8969
1126.1917 | 311.3116
1127.1917 | 309.3406
1128.1917 | 309.4106
1129.1917 | 310.5141
1130.1917 | 311.4886
1131.1917 | 312.7385
1132.1917 | 316.9947
1133.1917 | 317.2556
1134.1917 | 317.8897
1135.1917 | 320.0964
1136.1917 | 322.4383
1137.1917 | 323.1026
1138.1917 | 332.7259
1139.1917 | 335.1306
1140.1917 | 334.5
1141.1917 | 333.9875
1142.1917 | 334.0423
1143.1917 | 331.8141
1144.1917 | 333.6644
1145.1917 | 336.06
1146.1917 | 336.1348
1147.1917 | 334.2408
1148.1917 | 333.1442
1149.1917 | 335.107
1150.1917 | 334.0727
1151.1917 | 333.5573
1152.1917 | 332.7387
1153.1917 | 330.1949
1154.1917 | 328.8611
1155.1917 | 329.2594
1156.1917 | 328.5772
1157.1917 | 326.7481
1158.1917 | 327.0451
1159.1917 | 328.3535
1160.1917 | 327.3414
1161.1917 | 326.9493
1162.1917 | 327.0126
1163.1917 | 324.2707
1164.1917 | 324.3711
1165.1917 | 324.5608
1166.1917 | 325.1417
1167.1917 | 324.3131
1168.1917 | 326.0527
1169.1917 | 329.0447
1170.1917 | 329.544
1171.1917 | 330.9706
1172.1917 | 330.0827
1173.1917 | 330.3922
1174.1917 | 330.96
1175.1917 | 330.8642
1176.1917 | 330.5043
1177.1917 | 330.77
1178.1917 | 331.5543
1179.1917 | 331.9094
1180.1917 | 330.6303
1181.1917 | 330.2278
1182.1917 | 329.8532
1183.1917 | 329.3373
1184.1917 | 329.4463
1185.1917 | 329.4984
1186.1917 | 329.7859
1187.1917 | 330.1302
1188.1917 | 331.3782
1189.1917 | 330.3558
1190.1917 | 330.0696
1191.1917 | 329.7314
1192.1917 | 329.6939
1193.1917 | 329.9614
1194.1917 | 330.2158
1195.1917 | 330.9346
1196.1917 | 330.8092
1197.1917 | 330.8317
1198.1917 | 330.671
1199.1917 | 332.9241
1200.1917 | 333.8741
1201.1917 | 334.3831
1202.1917 | 334.7766
1203.1917 | 334.9239
1204.1917 | 335.0009
1205.1917 | 339.1287
1206.1917 | 340.4675
1207.1917 | 340.6615
1208.1917 | 338.0378
1209.1917 | 339.624
1210.1917 | 338.5779
1211.1917 | 337.2807
1212.1917 | 338.1138
1213.1917 | 338.4192
1214.1917 | 339.2705
1215.1917 | 339.2679
1216.1917 | 340.2339
1217.1917 | 340.3678
1218.1917 | 341.0712
1219.1917 | 343.876
1220.1917 | 345.0938
1221.1917 | 346.6064
1222.1917 | 346.0383
1223.1917 | 349.1246
1224.1917 | 348.9292
1225.1917 | 348.6115
1226.1917 | 349.0721
1227.1917 | 348.0738
1228.1917 | 346.1752
1229.1917 | 345.7793
1230.1917 | 345.6869
1231.1917 | 343.8436
1232.1917 | 344.5525
1233.1917 | 344.1253
1234.1917 | 343.378
1235.1917 | 344.6997
1236.1917 | 343.6452
1237.1917 | 343.1605
1238.1917 | 343.1445
1239.1917 | 343.1836
1240.1917 | 344.8571
1241.1917 | 350.6391
1242.1917 | 353.7946
1243.1917 | 354.6572
1244.1917 | 354.1447
1245.1917 | 354.5472
1246.1917 | 355.1519
1247.1917 | 359.8657
1248.1917 | 362.584
1249.1917 | 367.7308
1250.1917 | 367.1368
1251.1917 | 372.333
1252.1917 | 370.2024
1253.1917 | 369.8906
1254.1917 | 368.309
1255.1917 | 367.8325
1256.1917 | 369.0934
1257.1917 | 368.6844
1258.1917 | 367.2205
1259.1917 | 366.5032
1260.1917 | 365.1423
1261.1917 | 365.3237
1262.1917 | 364.1167
1263.1917 | 362.8747
1264.1917 | 363.2313
1265.1917 | 362.5712
1266.1917 | 362.4229
1267.1917 | 362.0856
1268.1917 | 362.3782
1269.1917 | 363.8923
1270.1917 | 364.7307
1271.1917 | 367.9644
1272.1917 | 365.4568
1273.1917 | 366.527
1274.1917 | 371.6235
1275.1917 | 380.9401
1276.1917 | 393.2927
1277.1917 | 411.6506
1278.1917 | 428.6966
1279.1917 | 430.0469
1280.1917 | 430.7152
1281.1917 | 431.2696
1282.1917 | 434.2297
1283.1917 | 439.0372
1284.1917 | 431.7553
1285.1917 | 427.6724
1286.1917 | 428.4393
1287.1917 | 423.3849
1288.1917 | 418.9574
1289.1917 | 418.3154
1290.1917 | 415.6027
1291.1917 | 413.1242
1292.1917 | 413.7752
1293.1917 | 425.4375
1294.1917 | 426.652
1295.1917 | 422.8756
1296.1917 | 423.1945
1297.1917 | 418.8527
1298.1917 | 417.1918
1299.1917 | 426.7892
1300.1917 | 428.6171
1301.1917 | 429.4235
1302.1917 | 428.2471
1303.1917 | 425.8533
1304.1917 | 427.1122
1305.1917 | 422.3519
1306.1917 | 417.8306
1307.1917 | 415.6192
1308.1917 | 413.4296
1309.1917 | 409.9745
1310.1917 | 408.2682
1311.1917 | 409.8563
1312.1917 | 415.7308
1313.1917 | 414.6924
1314.1917 | 414.2952
1315.1917 | 420.2071
1316.1917 | 441.1618
1317.1917 | 445.7049
1318.1917 | 450.8987
1319.1917 | 459.8828
1320.1917 | 472.4991
1321.1917 | 473.0624
1322.1917 | 483.837
1323.1917 | 490.8865
1324.1917 | 487.4793
1325.1917 | 485.8629
1326.1917 | 490.5394
1327.1917 | 494.0394
1328.1917 | 487.4931
1329.1917 | 480.9652
1330.1917 | 477.3263
1331.1917 | 477.5417
1332.1917 | 470.3344
1333.1917 | 464.8865
1334.1917 | 461.3883
1335.1917 | 456.0999
1336.1917 | 453.3833
1337.1917 | 450.4618
1338.1917 | 449.9482
1339.1917 | 444.317
1340.1917 | 457.0212
1341.1917 | 452.1074
1342.1917 | 446.9878
1343.1917 | 444.9299
1344.1917 | 444.9374
1345.1917 | 440.9866
1346.1917 | 441.0531
1347.1917 | 447.7834
1348.1917 | 445.8726
1349.1917 | 447.5268
1350.1917 | 449.6466
1351.1917 | 448.0939
1352.1917 | 444.1933
1353.1917 | 440.0616
1354.1917 | 437.923
1355.1917 | 442.7986
1356.1917 | 436.7907
1357.1917 | 440.7063
1358.1917 | 434.3051
1359.1917 | 433.6785
1360.1917 | 437.9267
1361.1917 | 438.1186
1362.1917 | 443.5981
1363.1917 | 440.3797
1364.1917 | 442.0279
1365.1917 | 442.8871
1366.1917 | 446.4756
1367.1917 | 444.0761
1368.1917 | 443.389
1369.1917 | 443.8417
1370.1917 | 444.0548
1371.1917 | 446.1878
1372.1917 | 449.2472
1373.1917 | 454.9904
1374.1917 | 455.9552
1375.1917 | 458.6956
1376.1917 | 458.954
1377.1917 | 460.0847
1378.1917 | 464.4743
1379.1917 | 465.55
1380.1917 | 465.0664
1381.1917 | 467.8959
1382.1917 | 467.5624
1383.1917 | 465.4487
1384.1917 | 468.8097
1385.1917 | 462.666
1386.1917 | 464.7289
1387.1917 | 464.8256
1388.1917 | 464.2056
1389.1917 | 469.957
1390.1917 | 480.3641
1391.1917 | 486.943
1392.1917 | 483.2956
1393.1917 | 478.781
1394.1917 | 480.9302
1395.1917 | 487.0293
1396.1917 | 488.0553
1397.1917 | 493.9291
1398.1917 | 497.0895
1399.1917 | 496.1714
1400.1917 | 498.7098
1401.1917 | 505.7814
1402.1917 | 515.0221
1403.1917 | 513.4079
1404.1917 | 517.9094
1405.1917 | 517.0229
1406.1917 | 513.2173
1407.1917 | 520.25
1408.1917 | 519.7013
1409.1917 | 514.186
1410.1917 | 508.7639
1411.1917 | 506.5737
1412.1917 | 510.9376
1413.1917 | 508.9666
1414.1917 | 506.725
1415.1917 | 507.8071
1416.1917 | 510.1111
1417.1917 | 510.9911
1418.1917 | 511.2021
1419.1917 | 507.6841
1420.1917 | 506.3569
1421.1917 | 506.994
1422.1917 | 509.9071
1423.1917 | 522.7817
1424.1917 | 519.6418
1425.1917 | 524.1865
1426.1917 | 528.9967
1427.1917 | 527.9757
1428.1917 | 524.008
1429.1917 | 521.8046
1430.1917 | 522.4049
1431.1917 | 520.2019
1432.1917 | 522.7103
1433.1917 | 523.0945
1434.1917 | 527.3552
1435.1917 | 524.6985
1436.1917 | 519.6315
1437.1917 | 517.4068
1438.1917 | 518.0298
1439.1917 | 528.8696
1440.1917 | 530.0392
1441.1917 | 527.7821
1442.1917 | 537.4578
1443.1917 | 535.2672
1444.1917 | 542.5762
1445.1917 | 569.2448
1446.1917 | 593.3445
1447.1917 | 598.4925
1448.1917 | 601.8372
1449.1917 | 607.8813
1450.1917 | 602.5618
1451.1917 | 602.0055
1452.1917 | 619.2214
1453.1917 | 638.7148
1454.1917 | 652.4565
1455.1917 | 655.2602
1456.1917 | 663.2596
1457.1917 | 654.266
1458.1917 | 648.2711
1459.1917 | 635.1623
1460.1917 | 622.4161
1461.1917 | 609.6486
1462.1917 | 601.708
1463.1917 | 603.0299
1464.1917 | 593.1355
1465.1917 | 634.8583
1466.1917 | 640.9202
1467.1917 | 625.6471
1468.1917 | 614.6941
1469.1917 | 606.5368
1470.1917 | 607.8795
1471.1917 | 623.4898
1472.1917 | 622.2722
1473.1917 | 620.6418
1474.1917 | 631.0153
1475.1917 | 661.8891
1476.1917 | 649.3691
1477.1917 | 646.0695
1478.1917 | 635.3486
1479.1917 | 621.0277
1480.1917 | 613.5618
1481.1917 | 605.3824
1482.1917 | 603.9221
1483.1917 | 600.6342
1484.1917 | 593.1451
1485.1917 | 593.3735
1486.1917 | 597.2594
1487.1917 | 588.4081
1488.1917 | 584.5144
1489.1917 | 578.9329
1490.1917 | 576.8891
1491.1917 | 573.1779
1492.1917 | 573.004
1493.1917 | 567.8119
1494.1917 | 572.091
1495.1917 | 574.996
1496.1917 | 588.6641
1497.1917 | 602.3498
1498.1917 | 595.8517
1499.1917 | 588.4345
1500.1917 | 595.9079
1501.1917 | 601.3133
1502.1917 | 616.6827
1503.1917 | 629.8106
1504.1917 | 627.7174
1505.1917 | 632.5952
1506.1917 | 627.8148
1507.1917 | 641.7673
1508.1917 | 655.2362
1509.1917 | 648.2833
1510.1917 | 650.9036
1511.1917 | 666.7777
1512.1917 | 666.209
1513.1917 | 656.5655
1514.1917 | 651.065
1515.1917 | 639.2272
1516.1917 | 647.7963
1517.1917 | 659.8028
1518.1917 | 673.8232
1519.1917 | 678.6239
1520.1917 | 680.778
1521.1917 | 670.2752
1522.1917 | 676.7823
1523.1917 | 686.4011
1524.1917 | 695.7124
1525.1917 | 694.6954
1526.1917 | 709.9918
1527.1917 | 697.3633
1528.1917 | 686.1089
1529.1917 | 707.858
1530.1917 | 700.7044
1531.1917 | 699.7978
1532.1917 | 684.6696
1533.1917 | 683.0867
1534.1917 | 687.4298
1535.1917 | 680.7526
1536.1917 | 691.6869
1537.1917 | 699.4672
1538.1917 | 730.793
1539.1917 | 716.8924
1540.1917 | 712.7741
1541.1917 | 712.9344
1542.1917 | 702.5218
1543.1917 | 684.1646
1544.1917 | 687.5925
1545.1917 | 678.7278
1546.1917 | 674.9028
1547.1917 | 674.0395
1548.1917 | 698.4795
1549.1917 | 683.9313
1550.1917 | 681.4171
1551.1917 | 684.379
1552.1917 | 691.753
1553.1917 | 697.4083
1554.1917 | 691.1898
1555.1917 | 695.056
1556.1917 | 687.6914
1557.1917 | 691.7701
1558.1917 | 685.9314
1559.1917 | 674.8477
1560.1917 | 687.0449
1561.1917 | 693.5436
1562.1917 | 717.289
1563.1917 | 716.3251
1564.1917 | 714.381
1565.2073 | 728.4938
1566.1917 | 733.6007
1567.1917 | 745.6385
1568.1917 | 757.4868
1569.1917 | 754.6091
1570.1917 | 758.789
1571.1917 | 770.7494
1572.1917 | 773.6856
1573.1917 | 769.4616
1574.1917 | 764.3302
1575.1917 | 758.9428
1576.1917 | 767.9895
1577.1917 | 771.3824
1578.1917 | 760.9145
1579.1917 | 758.8233
1580.1917 | 743.1765
1581.1917 | 734.6753
1582.1917 | 729.9083
1583.1917 | 728.9751
1584.1917 | 731.6026
1585.1917 | 737.6302
1586.1917 | 745.9369
1587.1917 | 756.9226
1588.1917 | 773.1822
1589.1917 | 779.2591
1590.1917 | 786.2205
1591.1917 | 783.0416
1592.1917 | 778.4653
1593.1917 | 781.3357
1594.1917 | 780.1842
1595.1917 | 789.9764
1596.1917 | 784.4197
1597.1917 | 790.8393
1598.1917 | 786.9969
1599.1917 | 789.8321
1600.1917 | 791.2745
1601.1917 | 791.8236
1602.1917 | 787.8031
1603.1917 | 778.734
1604.1917 | 787.0076
1605.1917 | 774.858
1606.1917 | 774.5418
1607.1917 | 771.1848
1608.1917 | 773.1076
1609.1917 | 772.181
1610.1917 | 772.6468
1611.1917 | 770.7024
1612.1917 | 766.9209
1613.1917 | 770.3615
1614.1917 | 772.5669
1615.1917 | 775.4687
1616.1917 | 778.7967
1617.1917 | 780.5777
1618.1917 | 782.2631
1619.1917 | 778.362
1620.1917 | 769.2184
1621.1917 | 782.8436
1622.1917 | 789.3327
1623.1917 | 783.4871
1624.1917 | 785.415
1625.1917 | 788.9345
1626.1917 | 789.4196
1627.1917 | 785.6225
1628.1917 | 784.6128
1629.1917 | 793.9623
1630.1917 | 795.2689
1631.1917 | 785.5181
1632.1917 | 782.3735
1633.1917 | 772.985
1634.1917 | 772.9544
1635.1917 | 767.562
1636.1917 | 767.534
1637.1917 | 762.2573
1638.1917 | 761.4076
1639.1917 | 763.0477
1640.1917 | 759.3621
1641.1917 | 754.3974
1642.1917 | 747.5061
1643.1917 | 736.8068
1644.1917 | 731.0672
1645.1917 | 728.1425
1646.1917 | 745.2748
1647.1917 | 749.3122
1648.1917 | 752.7993
1649.1917 | 749.5201
1650.1917 | 742.0411
1651.1917 | 735.6665
1652.1917 | 730.4998
1653.1917 | 727.7857
1654.1917 | 737.8807
1655.1917 | 751.6129
1656.1917 | 756.8241
1657.1917 | 755.5016
1658.1917 | 756.4828
1659.1917 | 759.6303
1660.1917 | 758.7048
1661.1917 | 763.0845
1662.1917 | 769.9251
1663.1917 | 757.7648
1664.1917 | 750.2483
1665.1917 | 738.2855
1666.1917 | 734.7351
1667.1917 | 733.0687
1668.1917 | 731.9987
1669.1917 | 735.6479
1670.1917 | 737.2123
1671.1917 | 736.9192
1672.1917 | 746.8499
1673.1917 | 765.8977
1674.1917 | 777.0646
1675.1917 | 781.9736
1676.1917 | 771.1044
1677.1917 | 761.0446
1678.1917 | 755.461
1679.1917 | 747.5798
1680.1917 | 738.3221
1681.1917 | 736.6378
1682.1917 | 728.8345
1683.1917 | 721.8649
1684.1917 | 719.6673
1685.1917 | 713.4656
1686.1917 | 715.7697
1687.1917 | 716.7912
1688.1917 | 717.0849
1689.1917 | 714.6568
1690.1917 | 709.0269
1691.1917 | 706.282
1692.1917 | 702.0637
1693.1917 | 708.9062
1694.1917 | 707.3643
1695.1917 | 710.8169
1696.1917 | 715.0229
1697.1917 | 719.2364
1698.1917 | 719.674
1699.1917 | 728.1937
1700.1917 | 726.5427
1701.1917 | 718.2659
1702.1917 | 716.2211
1703.1917 | 714.2904
1704.1917 | 712.5704
1705.1917 | 711.999
1706.1917 | 714.0201
1707.1917 | 724.1009
1708.1917 | 719.6661
1709.1917 | 721.4725
1710.1917 | 720.0576
1711.1917 | 722.5593
1712.1917 | 724.0535
1713.1917 | 719.1243
1714.1917 | 719.8188
1715.1917 | 720.4997
1716.1917 | 736.5044
1717.1917 | 738.8496
1718.1917 | 745.5021
1719.1917 | 741.6711
1720.1917 | 738.926
1721.1917 | 749.3312
1722.1917 | 741.9704
1723.1917 | 744.0586
1724.1917 | 739.5898
1725.1917 | 731.1011
1726.1917 | 736.6509
1727.1917 | 734.6917
1728.1917 | 729.9619
1729.1917 | 725.3983
1730.1917 | 717.9291
1731.1917 | 714.5241
1732.1917 | 726.5292
1733.1917 | 719.536
1734.1917 | 716.4319
1735.1917 | 714.1244
1736.1917 | 711.1731
1737.1917 | 717.9093
1738.1917 | 712.4907
1739.1917 | 709.9414
1740.1917 | 712.626
1741.1917 | 716.76
1742.1917 | 715.3439
1743.1917 | 728.827
1744.1917 | 728.2736
1745.1917 | 725.2784
1746.1917 | 725.4726
1747.1917 | 726.3681
1748.1917 | 724.4217
1749.1917 | 719.5349
1750.1917 | 721.5106
1751.1917 | 727.5779
1752.1917 | 725.0096
1753.1917 | 721.6389
1754.1917 | 719.571
1755.1917 | 717.9823
1756.1917 | 713.8
1757.1917 | 713.546
1758.1917 | 708.7001
1759.1917 | 706.9676
1760.1917 | 707.8991
1761.1917 | 712.1591
1762.1917 | 710.7949
1763.1917 | 713.264
1764.1917 | 710.9935
1765.1917 | 708.068
1766.1917 | 709.8148
1767.1917 | 719.1675
1768.1917 | 728.037
1769.1917 | 725.5896
1770.1917 | 721.9605
1771.1917 | 721.1696
1772.1917 | 722.2286
1773.1917 | 725.2712
1774.1917 | 718.564
1775.1917 | 713.338
1776.1917 | 713.7003
1777.1917 | 711.1196
1778.1917 | 707.5843
1779.1917 | 703.3226
1780.1917 | 700.878
1781.1917 | 698.4816
1782.1917 | 704.4599
1783.1917 | 722.4715
1784.1917 | 736.9466
1785.1917 | 749.7397
1786.1917 | 750.3388
1787.1917 | 746.801
1788.1917 | 756.4028
1789.1917 | 765.3459
1790.1917 | 769.1479
1791.1917 | 757.9844
1792.1917 | 752.3436
1793.1917 | 756.1045
1794.1917 | 752.3716
1795.1917 | 746.3734
1796.1917 | 742.1939
1797.1917 | 739.665
1798.1917 | 750.4286
1799.1917 | 752.7908
1800.1917 | 744.7033
1801.1917 | 747.6875
1802.1917 | 753.3774
1803.1917 | 755.8027
1804.1917 | 753.1513
1805.1917 | 754.5215
1806.1917 | 756.3582
1807.1917 | 762.417
1808.1917 | 776.0135
1809.1917 | 773.0739
1810.1917 | 767.9918
1811.1917 | 757.01
1812.1917 | 752.9398
1813.1917 | 754.7755
1814.1917 | 753.413
1815.1917 | 745.482
1816.1917 | 751.938
1817.1917 | 745.4284
1818.1917 | 741.0898
1819.1917 | 751.0773
1820.1917 | 759.6327
1821.1917 | 755.3515
1822.1917 | 759.6778
1823.1917 | 770.2237
1824.1917 | 780.8435
1825.1917 | 784.9442
1826.1917 | 774.7104
1827.1917 | 767.7913
1828.1917 | 759.1425
1829.1917 | 765.3531
1830.1917 | 772.9596
1831.1917 | 774.3826
1832.1917 | 771.9336
1833.1917 | 777.5731
1834.1917 | 777.4729
1835.1917 | 776.8827
1836.1917 | 777.0352
1837.1917 | 765.0093
1838.1917 | 761.1023
1839.1917 | 756.9499
1840.1917 | 764.7154
1841.1917 | 755.6074
1842.1917 | 747.7579
1843.1917 | 752.3024
1844.1917 | 744.8578
1845.1917 | 737.8068
1846.1917 | 734.3387
1847.1917 | 731.7681
1848.1917 | 729.6632
1849.1917 | 726.8934
1850.1917 | 727.224
1851.1917 | 736.3922
1852.1917 | 733.2544
1853.1917 | 731.4297
1854.1917 | 733.1681
1855.1917 | 736.9614
1856.1917 | 740.8109
1857.1917 | 743.3488
1858.1917 | 752.1091
1859.1917 | 748.1198
1860.1917 | 748.1449
1861.2073 | 751.8259
1862.1917 | 748.9044
1863.2073 | 740.5167
1864.1917 | 737.5712
1865.1917 | 737.9598
1866.1917 | 738.1714
1867.1917 | 737.859
1868.1917 | 737.4155
1869.1917 | 734.6016
1870.1917 | 734.2459
1871.1917 | 738.8684
1872.1917 | 741.1611
1873.1917 | 736.7634
1874.1917 | 735.403
1875.1917 | 733.472
1876.1917 | 739.327
1877.1917 | 743.5929
1878.1917 | 740.5102
1879.1917 | 740.0497
1880.1917 | 742.6969
1881.1917 | 740.9246
1882.1917 | 739.532
1883.1917 | 734.0227
1884.1917 | 731.4065
1885.1917 | 730.67
1886.1917 | 731.1693
1887.1917 | 736.2623
1888.1917 | 739.1087
1889.1917 | 734.9122
1890.1917 | 732.6428
1891.1917 | 734.1557
1892.1917 | 734.4568
1893.1917 | 730.0173
1894.1917 | 732.7247
1895.1917 | 739.8725
1896.1917 | 737.3778
1897.1917 | 737.0327
1898.1917 | 735.0276
1899.1917 | 733.5643
1900.1917 | 733.5969
1901.1917 | 727.9777
1902.1917 | 724.5565
1903.1917 | 730.412
1904.1917 | 732.4629
1905.1917 | 731.5701
1906.1917 | 736.9782
1907.1917 | 740.0911
1908.1917 | 743.8953
1909.1917 | 747.661
1910.1917 | 742.5942
1911.1917 | 737.9648
1912.1917 | 745.6166
1913.1917 | 757.0739
1914.1917 | 752.6138
1915.1917 | 754.678
1916.1917 | 755.7786
1917.1917 | 747.9922
1918.1917 | 753.0265
1919.1917 | 763.5017
1920.1917 | 762.8713
1921.1917 | 759.6847
1922.1917 | 758.046
1923.1917 | 751.2226
1924.1917 | 756.7304
1925.1917 | 767.8487
1926.1917 | 775.0176
1927.1917 | 770.8085
1928.1917 | 764.5067
1929.1917 | 763.0258
1930.1917 | 761.3579
1931.1917 | 767.2996
1932.1917 | 766.7311
1933.1917 | 759.8744
1934.1917 | 754.8063
1935.1917 | 750.0082
1936.1917 | 749.3512
1937.1917 | 746.3086
1938.1917 | 741.9592
1939.1917 | 739.4069
1940.1917 | 735.6028
1941.1917 | 736.2122
1942.1917 | 738.7566
1943.1917 | 735.1765
1944.1917 | 733.9042
1945.1917 | 736.8279
1946.1917 | 742.2818
1947.1917 | 742.9808
1948.1917 | 740.9553
1949.1917 | 740.7631
1950.1917 | 742.6649
1951.1917 | 746.179
1952.1917 | 748.9525
1953.1917 | 756.9572
1954.1917 | 758.6628
1955.1917 | 761.8373
1956.1917 | 754.7569
1957.1917 | 763.3685
1958.1917 | 768.0444
1959.1917 | 766.7112
1960.1917 | 765.5067
1961.1917 | 768.9649
1962.1917 | 761.7938
1963.2073 | 769.4025
1964.1917 | 768.8844
1965.1917 | 763.1022
1966.1917 | 759.4243
1967.1917 | 760.0807
1968.1917 | 759.2638
1969.1917 | 757.464
1970.1917 | 755.8173
1971.1917 | 752.4308
1972.1917 | 754.6952
1973.1917 | 761.9099
1974.1917 | 757.2218
1975.1917 | 756.4055
1976.1917 | 748.9266
1977.1917 | 743.6949
1978.1917 | 752.6295
1979.1917 | 747.7215
1980.1917 | 745.5317
1981.1917 | 741.3209
1982.1917 | 740.7317
1983.1917 | 739.8375
1984.1917 | 738.7941
1985.1917 | 747.8206
1986.1917 | 751.0261
1987.1917 | 749.5523
1988.1917 | 748.3614
1989.1917 | 746.0134
1990.1917 | 746.4383
1991.1917 | 745.0566
1992.1917 | 741.3307
1993.2073 | 738.2409
1994.1917 | 738.5708
1995.1917 | 746.2055
1996.1917 | 742.2652
1997.1917 | 740.8565
1998.1917 | 739.5332
1999.1917 | 732.6136
2000.1917 | 732.5734
2001.1917 | 731.4711
2002.1917 | 734.3934
2003.1917 | 738.399
2004.1917 | 739.5192
2005.1917 | 747.6332
2006.1917 | 748.1854
2007.1917 | 743.0998
2008.1917 | 743.0537
2009.1917 | 738.4123
2010.1917 | 741.9879
2011.1917 | 744.4548
2012.1917 | 745.9201
2013.1917 | 742.2402
2014.1917 | 744.0407
2015.1917 | 747.4114
2016.1917 | 745.1733
2017.1917 | 751.5162
2018.1917 | 753.0557
2019.1917 | 747.2819
2020.1917 | 752.0374
2021.1917 | 748.0212
2022.1917 | 746.1279
2023.2073 | 751.292
2024.1917 | 754.7791
2025.1917 | 754.866
2026.1917 | 753.6863
2027.1917 | 757.2093
2028.1917 | 758.0877
2029.1917 | 751.8742
2030.1917 | 755.7305
2031.1917 | 753.085
2032.1917 | 758.6685
2033.1917 | 758.7278
2034.1917 | 753.5282
2035.1917 | 750.2337
2036.1917 | 746.3718
2037.1917 | 744.2243
2038.1917 | 739.302
2039.1917 | 746.0469
2040.1917 | 756.6208
2041.1917 | 754.0673
2042.1917 | 748.8549
2043.1917 | 744.87
2044.1917 | 743.3825
2045.1917 | 743.6567
2046.1917 | 752.5633
2047.1917 | 754.5908
2048.1917 | 747.513
2049.1917 | 741.9864
2050.1917 | 736.0152
2051.1917 | 735.0134
2052.1917 | 732.1843
2053.1917 | 730.9001
2054.1917 | 728.7013
2055.1917 | 735.0689
2056.1917 | 733.8171
2057.1917 | 729.6517
2058.1917 | 731.5362
2059.1917 | 729.4184
2060.1917 | 725.9939
2061.1917 | 724.2027
2062.1917 | 728.5874
2063.1917 | 735.3095
2064.1917 | 747.4094
2065.1917 | 749.672
2066.1917 | 742.0082
2067.1917 | 742.0714
2068.1917 | 734.6215
2069.1917 | 734.4153
2070.1917 | 731.2294
2071.1917 | 732.8021
2072.1917 | 733.801
2073.1917 | 738.3493
2074.1917 | 734.0281
2075.1917 | 732.0885
2076.1917 | 736.6119
2077.1917 | 740.3859
2078.1917 | 747.4823
2079.1917 | 749.3274
2080.1917 | 746.3956
2081.1917 | 747.2435
2082.2073 | 744.0013
2083.2073 | 740.9771
2084.1917 | 737.9155
2085.1917 | 736.2573
2086.2073 | 729.8382
2087.1917 | 725.274
2088.2073 | 723.5168
2089.1917 | 718.7628
2090.1917 | 718.288
2091.1917 | 717.4412
2092.1917 | 717.9399
2093.1917 | 718.1499
2094.1917 | 715.6267
2095.1917 | 721.7563
2096.1917 | 721.7061
2097.1917 | 721.6667
2098.1917 | 720.1856
2099.1917 | 723.1992
2100.1917 | 723.7527
2101.1917 | 721.27
2102.1917 | 723.5049
2103.1917 | 722.4234
2104.1917 | 721.4863
2105.1917 | 718.0734
2106.1917 | 717.033
2107.1917 | 718.0085
2108.1917 | 713.8554
2109.1917 | 713.4539
2110.1917 | 715.6604
2111.1917 | 716.4206
2112.1917 | 725.0304
2113.2073 | 719.6014
2114.1917 | 722.0174
2115.1917 | 720.282
2116.1917 | 718.8338
2117.1917 | 715.5375
2118.1917 | 714.906
2119.1917 | 712.4354
2120.1917 | 713.2939
2121.1917 | 714.8695
2122.1917 | 714.3584
2123.1917 | 714.5715
2124.1917 | 718.752
2125.1917 | 715.7897
2126.1917 | 718.6763
2127.1917 | 717.7163
2128.1917 | 720.6849
2129.1917 | 724.5032
2130.1917 | 723.1302
2131.1917 | 731.6358
2132.1917 | 737.3902
2133.2073 | 734.1543
2134.1917 | 735.6996
2135.1917 | 736.5938
2136.1917 | 741.6053
2137.1917 | 752.175
2138.1917 | 751.2588
2139.1917 | 751.2571
2140.1917 | 752.836
2141.1917 | 749.052
2142.1917 | 743.7582
2143.2073 | 739.738
2144.1917 | 742.5498
2145.1917 | 736.7668
2146.1917 | 739.5541
2147.1917 | 740.6715
2148.1917 | 736.4827
2149.1917 | 739.7066
2150.1917 | 749.3065
2151.1917 | 744.2405
2152.1917 | 740.6105
2153.1917 | 736.3919
2154.1917 | 740.5231
2155.1917 | 747.6801
2156.1917 | 747.9982
2157.1917 | 740.6448
2158.1917 | 740.3091
2159.1917 | 746.8517
2160.1917 | 756.1945
2161.1917 | 754.4888
2162.1917 | 758.7479
2163.1917 | 751.9703
2164.1917 | 744.846
2165.1917 | 742.035
2166.1917 | 736.1378
2167.1917 | 741.3946
2168.1917 | 753.3202
2169.1917 | 756.5685
2170.1917 | 750.883
2171.1917 | 758.4643
2172.1917 | 757.811
2173.1917 | 756.8879
2174.1917 | 750.9166
2175.1917 | 751.0842
2176.1917 | 757.542
2177.1917 | 751.4957
2178.1917 | 762.6418
2179.1917 | 760.9957
2180.1917 | 756.8571
2181.1917 | 762.2591
2182.1917 | 763.4328
2183.1917 | 753.5951
2184.1917 | 756.3757
2185.1917 | 746.4503
2186.1917 | 744.5233
2187.1917 | 742.8564
2188.1917 | 739.773
2189.1917 | 733.6442
2190.1917 | 729.6702
2191.1917 | 736.1328
2192.1917 | 736.2081
2193.1917 | 735.1371
2194.1917 | 733.1149
2195.1917 | 733.3047
2196.1917 | 740.7595
2197.1917 | 735.0513
2198.1917 | 736.6456
2199.1917 | 730.3565
2200.1917 | 727.739
2201.1917 | 731.9919
2202.1917 | 727.7269
2203.1917 | 726.0671
2204.1917 | 730.3953
2205.1917 | 730.077
2206.1917 | 729.7973
2207.1917 | 728.7722
2208.1917 | 726.8293
2209.1917 | 724.4704
2210.1917 | 722.7293
2211.1917 | 723.1834
2212.1917 | 725.1155
2213.1917 | 728.5906
2214.1917 | 728.8462
2215.1917 | 727.6207
2216.1917 | 726.3201
2217.1917 | 726.1955
2218.1917 | 721.8421
2219.1917 | 720.545
2220.1917 | 720.8241
2221.1917 | 720.1849
2222.1917 | 733.9676
2223.1917 | 744.9887
2224.1917 | 748.1135
2225.1917 | 741.491
2226.1917 | 742.7947
2227.1917 | 741.3946
2228.1917 | 738.4817
2229.1917 | 734.9029
2230.1917 | 737.6044
2231.1917 | 734.7158
2232.1917 | 733.4822
2233.2073 | 730.546
2234.1917 | 725.527
2235.1917 | 721.3707
2236.1917 | 721.5623
2237.1917 | 719.7426
2238.1917 | 720.7998
2239.1917 | 722.9561
2240.1917 | 725.3539
2241.1917 | 725.4538
2242.1917 | 729.5384
2243.1917 | 733.2837
2244.1917 | 734.1991
2245.1917 | 732.8646
2246.1917 | 731.5188
2247.1917 | 727.1708
2248.1917 | 725.2959
2249.1917 | 726.6399
2250.1917 | 726.31
2251.1917 | 722.195
2252.1917 | 722.0922
2253.1917 | 725.6399
2254.1917 | 725.8471
2255.1917 | 725.074
2256.1917 | 737.6019
2257.1917 | 735.2401
2258.1917 | 736.1004
2259.1917 | 748.0047
2260.1917 | 752.3962
2261.1917 | 746.5015
2262.1917 | 743.7439
2263.2073 | 751.085
2264.1917 | 750.7215
2265.1917 | 751.1593
2266.1917 | 748.3298
2267.1917 | 753.6028
2268.1917 | 749.9438
2269.1917 | 750.5088
2270.1917 | 749.3972
2271.1917 | 751.8461
2272.1917 | 749.8498
2273.1917 | 743.9603
2274.1917 | 742.0929
2275.1917 | 748.0555
2276.1917 | 745.5783
2277.1917 | 752.4125
2278.1917 | 749.5137
2279.1917 | 753.5878
2280.1917 | 748.8592
2281.1917 | 743.6387
2282.1917 | 742.6219
2283.1917 | 746.3263
2284.1917 | 747.6119
2285.1917 | 747.3162
2286.1917 | 750.3829
2287.1917 | 749.5034
2288.1917 | 751.69
2289.1917 | 750.47
2290.1917 | 743.9359
2291.1917 | 741.4466
2292.1917 | 739.098
2293.1917 | 740.5205
2294.1917 | 736.9432
2295.1917 | 736.3507
2296.1917 | 743.4169
2297.1917 | 748.3075
2298.1917 | 760.8222
2299.1917 | 760.3313
2300.1917 | 763.5393
2301.1917 | 768.2133
2302.1917 | 759.2006
2303.1917 | 759.4555
2304.1917 | 756.0373
2305.1917 | 757.7888
2306.1917 | 755.1113
2307.1917 | 754.757
2308.1917 | 751.8702
2309.1917 | 754.1059
2310.1917 | 751.3979
2311.1917 | 753.8033
2312.1917 | 757.4395
2313.2073 | 757.5967
2314.1917 | 751.759
2315.1917 | 746.8096
2316.1917 | 746.2131
2317.1917 | 749.0567
2318.1917 | 753.1349
2319.1917 | 748.7417
2320.1917 | 744.6049
2321.1917 | 743.9997
2322.1917 | 743.9999
2323.2073 | 746.4436
2324.1917 | 748.2968
2325.1917 | 746.4231
2326.1917 | 740.9144
2327.1917 | 736.4005
2328.1917 | 733.2738
2329.1917 | 730.7889
2330.1917 | 732.4588
2331.1917 | 739.0957
2332.1917 | 738.6921
2333.1917 | 735.695
2334.1917 | 737.7597
2335.1917 | 734.0006
2336.1917 | 732.5264
2337.1917 | 732.1855
2338.1917 | 729.422
2339.1917 | 737.5078
2340.1917 | 742.8426
2341.1917 | 738.1879
2342.1917 | 734.8023
2343.1917 | 733.5339
2344.1917 | 730.53
2345.1917 | 726.6754
2346.1917 | 721.9921
2347.1917 | 720.6366
2348.1917 | 718.0714
2349.1917 | 715.3374
2350.1917 | 717.7
2351.1917 | 716.3452
2352.1917 | 715.8908
2353.1917 | 716.0469
2354.1917 | 716.4836
2355.1917 | 716.4795
2356.1917 | 721.857
2357.1917 | 727.3181
2358.1917 | 729.3802
2359.1917 | 727.6723
2360.1917 | 722.7979
2361.1917 | 726.1992
2362.1917 | 728.2959
2363.1917 | 731.8476
2364.1917 | 728.6402
2365.1917 | 743.6181
2366.1917 | 745.0254
2367.1917 | 748.8614
2368.1917 | 747.0996
2369.1917 | 748.4287
2370.1917 | 743.3853
2371.1917 | 741.4466
2372.1917 | 735.1306
2373.1917 | 730.58
2374.1917 | 729.5102
2375.1917 | 732.4203
2376.1917 | 729.4414
2377.1917 | 729.6911
2378.1917 | 729.0117
2379.1917 | 724.2678
2380.1917 | 718.22
2381.1917 | 722.0065
2382.1917 | 726.568
2383.1917 | 728.3923
2384.1917 | 731.9916
2385.1917 | 743.2289
2386.1917 | 743.3334
2387.1917 | 737.8456
2388.1917 | 737.2218
2389.1917 | 729.9098
2390.1917 | 723.4183
2391.1917 | 721.9762
2392.1917 | 721.838
2393.1917 | 720.3649
2394.1917 | 718.9991
2395.1917 | 716.2145
2396.1917 | 711.2712
2397.1917 | 707.6098
2398.1917 | 703.9258
2399.1917 | 699.0927
2400.1917 | 694.9422
2401.1917 | 695.6927
2402.1917 | 693.2919
2403.1917 | 692.7529
2404.1917 | 692.3032
2405.1917 | 692.9419
2406.1917 | 692.2651
2407.1917 | 693.7144
2408.1917 | 691.0854
2409.1917 | 689.3377
2410.1917 | 686.7219
2411.1917 | 689.3857
2412.1917 | 689.252
2413.1917 | 690.7745
2414.1917 | 689.6244
2415.1917 | 689.0931
2416.1917 | 690.9171
2417.1917 | 691.4555
2418.1917 | 691.9206
2419.1917 | 689.6775
2420.1917 | 683.4048
2421.1917 | 682.3271
2422.1917 | 681.632
2423.1917 | 683.0967
2424.1917 | 684.5829
2425.1917 | 681.4242
2426.1917 | 683.0077
2427.1917 | 680.5825
2428.1917 | 678.0154
2429.1917 | 674.9514
2430.1917 | 672.4797
2431.1917 | 671.9266
2432.1917 | 670.7104
2433.1917 | 672.2076
2434.1917 | 672.4544
2435.1917 | 676.7255
2436.1917 | 676.3784
2437.1917 | 685.159
2438.1917 | 682.5254
2439.1917 | 684.7422
2440.1917 | 683.9805
2441.1917 | 684.3512
2442.1917 | 682.5643
2443.1917 | 682.1083
2444.1917 | 683.6795
2445.1917 | 679.104
2446.1917 | 676.8154
2447.1917 | 674.9594
2448.1917 | 672.1318
2449.1917 | 670.2723
2450.1917 | 672.5541
2451.1917 | 674.3567
2452.1917 | 681.7144
2453.1917 | 679.5879
2454.1917 | 673.7124
2455.1917 | 671.5889
2456.1917 | 674.3266
2457.1917 | 675.1749
2458.1917 | 672.9043
2459.1917 | 674.0557
2460.1917 | 676.1454
2461.1917 | 679.5195
2462.1917 | 678.3981
2463.1917 | 680.3384
2464.1917 | 679.6874
2465.1917 | 678.3618
2466.1917 | 681.247
2467.1917 | 681.5375
2468.1917 | 681.5184
2469.1917 | 680.8744
2470.1917 | 678.5085
2471.1917 | 680.243
2472.1917 | 678.941
2473.1917 | 680.5173
2474.1917 | 681.7082
2475.1917 | 681.6077
2476.1917 | 677.4012
2477.1917 | 672.7774
2478.1917 | 673.3842
2479.1917 | 671.9815
2480.1917 | 672.2769
2481.1917 | 678.3201
2482.1917 | 684.8484
2483.1917 | 686.5819
2484.1917 | 683.5934
2485.1917 | 680.5072
2486.1917 | 679.2351
2487.1917 | 678.0941
2488.1917 | 675.6256
2489.1917 | 672.5172
2490.1917 | 669.4306
2491.1917 | 670.497
2492.1917 | 672.6788
2493.1917 | 668.6483
2494.1917 | 665.6766
2495.1917 | 663.939
2496.1917 | 662.7339
2497.1917 | 659.8383
2498.1917 | 660.1428
2499.1917 | 660.6496
2500.1917 | 658.9135
2501.1917 | 659.7439
2502.1917 | 662.394
2503.1917 | 659.4226
2504.1917 | 657.45
2505.1917 | 658.5133
2506.1917 | 658.2731
2507.1917 | 658.9235
2508.1917 | 653.1986
2509.1917 | 647.4203
2510.1917 | 645.5171
2511.1917 | 645.7963
2512.1917 | 644.9011
2513.1917 | 643.0884
2514.1917 | 644.7246
2515.1917 | 650.3116
2516.1917 | 649.0277
2517.1917 | 646.3343
2518.1917 | 641.6732
2519.1917 | 639.7158
2520.1917 | 637.3338
2521.1917 | 637.4855
2522.1917 | 634.6086
2523.1917 | 631.2204
2524.1917 | 631.1434
2525.1917 | 628.8377
2526.1917 | 627.7606
2527.1917 | 626.1099
2528.1917 | 625.8225
2529.1917 | 626.0622
2530.1917 | 625.5903
2531.1917 | 624.7157
2532.1917 | 624.046
2533.1917 | 622.9646
2534.1917 | 625.6324
2535.1917 | 625.5041
2536.1917 | 627.6686
2537.1917 | 628.4263
2538.1917 | 627.0572
2539.1917 | 626.3667
2540.2073 | 621.7547
2541.1917 | 623.0322
2542.1917 | 625.1851
2543.1917 | 626.1966
2544.2073 | 626.2806
2545.1917 | 623.8678
2546.1917 | 620.0438
2547.1917 | 619.1627
2548.1917 | 617.373
2549.1917 | 616.5835
2550.1917 | 615.7773
2551.1917 | 613.1766
2552.1917 | 612.757
2553.1917 | 614.9673
2554.1917 | 616.1325
2555.1917 | 616.8991
2556.1917 | 617.7544
2557.1917 | 616.0935
2558.1917 | 614.0519
2559.1917 | 612.1963
2560.1917 | 612.6966
2561.1917 | 614.2407
2562.1917 | 612.9435
2563.1917 | 612.4449
2564.1917 | 614.0949
2565.1917 | 619.2956
2566.1917 | 622.6544
2567.1917 | 625.4552
2568.1917 | 626.9556
2569.1917 | 627.6419
2570.1917 | 628.3467
2571.1917 | 629.8267
2572.1917 | 632.1835
2573.1917 | 632.8054
2574.1917 | 630.283
2575.1917 | 628.734
2576.1917 | 630.2141
2577.1917 | 629.7867
2578.1917 | 629.3277
2579.1917 | 628.2086
2580.1917 | 628.3452
2581.1917 | 628.3341
2582.1917 | 630.6593
2583.1917 | 632.8375
2584.1917 | 633.7804
2585.1917 | 633.0083
2586.1917 | 628.5654
2587.1917 | 627.9118
2588.1917 | 628.5982
2589.1917 | 629.4333
2590.1917 | 630.357
2591.1917 | 631.4065
2592.1917 | 630.7177
2593.1917 | 628.2209
2594.1917 | 623.316
2595.1917 | 619.8094
2596.1917 | 618.1995
2597.1917 | 617.2148
2598.1917 | 613.8237
2599.1917 | 611.7929
2600.1917 | 609.3325
2601.1917 | 611.0574
2602.1917 | 609.83
2603.1917 | 608.5338
2604.1917 | 608.1414
2605.1917 | 609.9121
2606.1917 | 609.7232
2607.1917 | 610.1653
2608.1917 | 611.9592
2609.1917 | 613.577
2610.1917 | 615.6127
2611.1917 | 615.7136
2612.1917 | 615.7544
2613.1917 | 613.5582
2614.1917 | 610.5347
2615.1917 | 611.0791
2616.1917 | 608.6168
2617.1917 | 605.967
2618.1917 | 605.0162
2619.1917 | 600.5015
2620.1917 | 597.419
2621.1917 | 597.9743
2622.1917 | 599.5958
2623.1917 | 603.5572
2624.1917 | 605.6475
2625.1917 | 601.2436
2626.1917 | 599.7772
2627.1917 | 597.5465
2628.1917 | 598.2401
2629.1917 | 600.2644
2630.1917 | 601.831
2631.1917 | 598.1929
2632.1917 | 597.4093
2633.1917 | 599.7926
2634.1917 | 603.9543
2635.1917 | 607.7599
2636.1917 | 610.1351
2637.1917 | 610.8646
2638.1917 | 609.9042
2639.1917 | 606.8366
2640.1917 | 604.3205