## Test Conditions
DESIREE-FIRE Intermediate Scale Test Number 5 - Circuit Simulator Data Only
Test Date: | 2010-03-01
DCSim DAQ Start Time | 13:30
DCSim Time for Synchronization | 13:42
Heat Source Synchronization | 0:01 | hour:minutes:seconds
Heat Source DAQ Start Time | 13:41
Fire Time | 14:02
Offset | 0:32 | hour:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 1920 | seconds
Heat Source Offset | 0:21 | hour:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 1288 | seconds
Heat Source Stop Time | 14:46
Test Duration | 0:44 | hour:minutes:seconds
| 2640 | seconds
CT500 turns | 2 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 turns | 5 | 1 or 5
Pre-Test Baseline: | Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit number | Cable Type |  | Cable TC channel | Air TC Channel
MOV 1 | PE/PVC, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 2, 3, and 4 represents the conduit temperature 3', 5', and 7' down the conduit located in B Position. These are labeled as "B Position - Conduit - 3'", "B Position - Conduit - Middle", " B Position - Conduit - 7'", respectively.
MOV 2 | PE/PVC, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 8, 9, and 10 represents the air temperature 3', 5', and 7' down the tray located in D Position. These are labeled as "D Position - 3'", "D Position - Middle", " D Position - 7'", respectively.
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
2 | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | MOV-1_CT500 | MOV-1a_CT35_1_P | MOV-1a_CT35_2_N | MOV-1b_CT35_1_G | MOV-1b_CT35_2_R | MOV-1b_CT35_3_YO | MOV-1b_CT35_4_YC | MOV-2_CT500 | MOV-2a_CT35_1_P | MOV-2a_CT35_2_N | MOV-2b_CT35_1_G | MOV-2b_CT35_2_R | MOV-2b_CT35_3_YO | 2b_CT35_4_YC1 | MOV-1a_VT7_1_SP | MOV-1a_VTU_1_P | MOV-1a_VTU_2_N | MOV-1b_VT7_1_G | MOV-1b_VT7_2_R | MOV-1b_VT7_3_YO1 | MOV-1b_VT7_4_YC1 | MOV-2a_VT7_1_SP | MOV-2a_VTU_1_P | MOV-2a_VTU_2_N | MOV-2b_VT7_1_G | MOV-2b_VT7_2_R | 2b_VT7_3_YO1 | MOV-2b_VT7_4_YC1 | {MOV1} V(N) - V(Batt -) | {MOV1} V(P) - V(Batt +) | {MOV1} V(G) - V(Batt +) | {MOV1} V(R) - V(Batt -) | {MOV1} V(YC1) - V(Batt -) | {MOV1} V(YO1) - V(Batt -) | {MOV1} V(YC1) - V(N) | {MOV1} V(YO1) - V(N) | {MOV2} V(N) - V(Batt -) | {MOV2} V(P) - V(Batt +) | {MOV2} V(G) - V(Batt +) | {MOV2} V(R) - V(Batt -) | {MOV2} V(YC1) - V(Batt -) | {MOV2} V(YO1) - V(Batt -) | {MOV2} V(YC1) - V(N) | {MOV2} V(YO1) - V(N) | {MOV-1} V(R) - V(N) | {MOV-1} V(G) - V(N) | {MOV-2} V(R) - V(N) | {MOV-2} V(G) - V(N) | {MOV-1} V(P) - V(N) | {MOV-2} V(P) - V(N) | {MOV-1} V(P) - V(Batt -) | {MOV-2} V(P) - V(Batt -) | {MOV-1} V(N) - V(Batt +) | {MOV-2} V(N) - V(Batt +) | {MOV-1} V(G) - V(Batt -) | {MOV2} V(G) - V(Batt-) | {MOV1} V(SP) - V(Batt -) | {MOV2} V(SP) - V(Batt -)
-1.6094 | 124.0173 | -62.0407 | 61.8759 | -0.0020601 | 0.0038857 | 0.068712 | 0.065443 | -0.0018649 | -0.00059378 | -0.0012434 | 0.0018005 | 0.0045865 | 0.069128 | 0.066227 | -0.0039348 | 0.0094549 | -0.0044968 | -0.009155 | 61.8622 | -62.146 | 61.8439 | -61.7752 | -62.1735 | -62.2009 | -0.013733 | 61.7706 | -62.0865 | 61.8027 | -62.0041 | -62.0224 | -62.027 | -0.10529 | -0.013733 | -0.032044 | 0.2655 | -0.16022 | -0.13275 | -0.054932 | -0.027466 | -0.045777 | -0.10529 | -0.073243 | 0.036621 | 0.013732 | 0.01831 | 0.059509 | 0.064087 | 0.37079 | 123.9899 | 0.082398 | 123.8892 | 124.0082 | 123.8571 | 123.9029 | 123.8113 | -124.0219 | -123.9624 | 123.8846 | 123.8434 | 62.0316 | 62.027
0.0625 | 123.9944 | -62.0316 | 61.908 | -0.0096891 | 0.0019631 | 0.066362 | 0.066512 | 0.0015529 | -0.0048664 | -0.00081595 | -0.0012513 | 0.0056545 | 0.068915 | 0.067936 | -0.0047894 | 0.012873 | 0.0010574 | -0.045776 | 61.908 | -62.178 | 61.7752 | -61.8347 | -62.2375 | -62.2513 | -0.059509 | 61.8073 | -62.0728 | 61.8027 | -62.0178 | -62.0361 | -62.0407 | -0.14649 | 0 | -0.13275 | 0.19684 | -0.21973 | -0.20599 | -0.073242 | -0.059509 | -0.041199 | -0.10071 | -0.10529 | 0.013733 | -0.009155 | -0.004578 | 0.032044 | 0.036621 | 0.34332 | 123.9532 | 0.054932 | 123.8754 | 124.086 | 123.88 | 123.9395 | 123.8388 | -124.086 | -123.9807 | 123.8068 | 123.8342 | 61.9858 | 61.972
1.8125 | 124.1272 | -62.0544 | 61.8256 | -0.0020601 | 0.0030313 | 0.068285 | 0.063735 | -0.0018649 | -0.0010212 | 3.8448e-05 | -0.0012513 | 0.0045865 | 0.068701 | 0.06345 | 0.00012397 | 0.010096 | -0.0002244 | -0.032043 | 61.8118 | -62.1597 | 61.8988 | -61.6928 | -62.1048 | -62.1414 | 0.064087 | 61.7065 | -62.0682 | 61.8896 | -61.908 | -61.9263 | -61.9675 | -0.10529 | -0.013733 | 0.073242 | 0.36163 | -0.086975 | -0.050354 | 0.018311 | 0.054932 | -0.013733 | -0.11902 | 0.064086 | 0.14648 | 0.086975 | 0.12817 | 0.10071 | 0.14191 | 0.46692 | 124.0585 | 0.16022 | 123.9578 | 123.9716 | 123.7747 | 123.8663 | 123.761 | -123.9853 | -123.8937 | 123.9532 | 123.9441 | 62.0224 | 62.1185
3.4844 | 123.9853 | -62.0773 | 61.8988 | -0.0096891 | 0.0030313 | 0.068071 | 0.066084 | -0.00079686 | -0.0048664 | 0.00067925 | -0.0012513 | 0.0054409 | 0.069983 | 0.064305 | -0.0039348 | 0.01095 | -0.001506 | -0.050354 | 61.8759 | -62.1826 | 61.7935 | -61.8118 | -62.2101 | -62.2375 | -0.059509 | 61.7981 | -62.0819 | 61.7844 | -62.0087 | -62.0499 | -62.0178 | -0.10529 | -0.022888 | -0.10529 | 0.2655 | -0.16022 | -0.13275 | -0.054932 | -0.027466 | -0.004577 | -0.10071 | -0.11444 | 0.068665 | 0.05951 | 0.027466 | 0.064087 | 0.032043 | 0.37079 | 123.9761 | 0.073242 | 123.8663 | 124.0585 | 123.88 | 123.9532 | 123.8754 | -124.0814 | -123.9807 | 123.8708 | 123.8617 | 62.027 | 62.0178
5.2344 | 124.0723 | -62.0499 | 61.8073 | 0.051346 | 0.0051675 | 0.071275 | 0.067152 | 0.00027134 | -0.0014484 | 0.0011066 | 0.0079041 | 0.0052273 | 0.068488 | 0.066868 | -0.0020122 | 0.012232 | -0.0027878 | -0.10071 | 61.7981 | -62.2055 | 61.8393 | -61.7569 | -62.1918 | -62.2192 | -0.032043 | 61.7111 | -62.1094 | 61.8393 | -61.9812 | -61.9995 | -61.9904 | -0.15564 | -0.009155 | 0.032043 | 0.29297 | -0.16937 | -0.14191 | -0.013733 | 0.013733 | -0.059509 | -0.09613 | 0.032043 | 0.068665 | 0.05951 | 0.050354 | 0.11902 | 0.10986 | 0.44861 | 124.0448 | 0.12817 | 123.9487 | 124.0036 | 123.8205 | 123.848 | 123.761 | -124.0128 | -123.9166 | 123.8892 | 123.8892 | 61.9492 | 62.0178
6.9688 | 124.0082 | -62.027 | 61.9034 | 0.043716 | 0.0021769 | 0.068712 | 0.06758 | 0.0041165 | -0.0018756 | 0.00067925 | 0.0079041 | 0.0073635 | 0.071478 | 0.061955 | -0.0041486 | 0.012659 | -1.0598e-05 | -0.013733 | 61.9171 | -62.1964 | 61.7981 | -61.8164 | -62.1826 | -62.2284 | -0.032043 | 61.8301 | -62.1048 | 61.8393 | -61.9812 | -62.0132 | -61.9766 | -0.16937 | 0.013733 | -0.10529 | 0.21057 | -0.20142 | -0.15564 | -0.032044 | 0.013733 | -0.077819 | -0.073242 | -0.064087 | 0.045777 | 0.050354 | 0.013733 | 0.12817 | 0.091552 | 0.37994 | 123.9944 | 0.1236 | 123.9441 | 124.1135 | 123.9349 | 123.9441 | 123.8571 | -124.0997 | -124.0082 | 123.8251 | 123.8663 | 62.0132 | 61.9949
8.6406 | 124.1135 | -62.059 | 61.7706 | 0.0055694 | 0.0019631 | 0.068498 | 0.063094 | -0.0027195 | -0.0027302 | -0.0016706 | 0.0018005 | 0.0022367 | 0.067633 | 0.067082 | -0.0013714 | 0.01095 | 0.000203 | -0.086975 | 61.821 | -62.1689 | 61.853 | -61.734 | -62.1414 | -62.1735 | 0.013733 | 61.7249 | -62.0773 | 61.8851 | -61.908 | -61.9171 | -61.9583 | -0.10986 | 0.050354 | 0.082397 | 0.32501 | -0.11444 | -0.082397 | -0.004578 | 0.027466 | -0.018311 | -0.045776 | 0.11444 | 0.15106 | 0.10071 | 0.14191 | 0.11902 | 0.16022 | 0.43487 | 124.0219 | 0.16937 | 123.9624 | 123.9899 | 123.8022 | 123.88 | 123.7839 | -123.9395 | -123.848 | 123.912 | 123.9441 | 61.972 | 62.0728
10.3906 | 123.9807 | -62.059 | 61.8668 | -0.0020601 | 0.0058083 | 0.068712 | 0.066512 | 0.0028347 | -0.0040118 | -0.0044476 | -0.0043029 | 0.0067227 | 0.069556 | 0.06046 | -0.0020122 | 0.015009 | -0.002147 | -0.068665 | 61.8805 | -62.1643 | 61.7569 | -61.8759 | -62.265 | -62.2971 | -0.14191 | 61.7889 | -62.0865 | 61.7981 | -62.0453 | -62.0636 | -62.0132 | -0.10529 | 0.013733 | -0.10986 | 0.18311 | -0.23804 | -0.20599 | -0.13275 | -0.10071 | -0.027466 | -0.07782 | -0.068664 | 0.013733 | 0.045776 | -0.004578 | 0.073242 | 0.022888 | 0.28839 | 123.9212 | 0.041199 | 123.8846 | 124.0448 | 123.8754 | 123.9395 | 123.848 | -124.0311 | -123.9532 | 123.8159 | 123.8571 | 61.9904 | 61.9171
12.1406 | 123.9578 | -62.0224 | 61.8805 | -0.0020601 | 0.0030313 | 0.069994 | 0.066725 | -0.0012241 | -0.0048664 | -0.00017515 | -0.0043029 | 0.0045865 | 0.070624 | 0.0658 | -0.0020122 | 0.011377 | -0.0064194 | -0.07782 | 61.8988 | -62.1368 | 61.7798 | -61.8484 | -62.2467 | -62.265 | -0.10529 | 61.7981 | -62.0682 | 61.7981 | -62.0453 | -62.0773 | -62.027 | -0.11444 | 0.018311 | -0.10071 | 0.17395 | -0.24262 | -0.2243 | -0.12817 | -0.10986 | -0.045776 | -0.082397 | -0.082397 | -0.022888 | -0.004578 | -0.054932 | 0.041198 | -0.009156 | 0.28839 | 123.9166 | 0.022888 | 123.8663 | 124.0356 | 123.8663 | 123.9212 | 123.8205 | -124.0173 | -123.9487 | 123.8022 | 123.8205 | 61.9446 | 61.9171
13.875 | 123.967 | -62.0361 | 61.8851 | -0.0020601 | 0.0064493 | 0.068285 | 0.065657 | -0.00036966 | -0.0023028 | -0.0018842 | -0.0012513 | 0.0037319 | 0.069769 | 0.061528 | -0.0017986 | 0.012232 | -0.003215 | -0.07782 | 61.8759 | -62.1597 | 61.7798 | -61.8439 | -62.2513 | -62.2742 | -0.11444 | 61.7844 | -62.0544 | 61.7706 | -62.0407 | -62.0773 | -62.0361 | -0.1236 | -0.009155 | -0.10529 | 0.19226 | -0.23804 | -0.21515 | -0.11444 | -0.091553 | -0.01831 | -0.10071 | -0.11444 | -0.004577 | 0 | -0.041199 | 0.01831 | -0.022889 | 0.31586 | 123.9395 | 0.013733 | 123.8251 | 124.0356 | 123.8388 | 123.912 | 123.8205 | -124.0448 | -123.9395 | 123.8159 | 123.8068 | 61.9583 | 61.9217
15.5469 | 123.9899 | -62.0132 | 61.8988 | -0.017319 | 0.0053811 | 0.069139 | 0.067152 | 0.0036893 | -0.0010212 | 0.00067925 | 0.014008 | 0.0054409 | 0.068488 | 0.060673 | -0.005003 | 0.010737 | -0.0006516 | -0.036621 | 61.9217 | -62.1643 | 61.7935 | -61.7981 | -62.1872 | -62.2147 | -0.036621 | 61.821 | -62.0911 | 61.8118 | -61.9858 | -62.0132 | -61.9949 | -0.15106 | 0.022888 | -0.10529 | 0.21515 | -0.20142 | -0.17395 | -0.050354 | -0.022888 | -0.077819 | -0.07782 | -0.086975 | 0.027466 | 0.018311 | 0 | 0.09613 | 0.077819 | 0.36621 | 123.9578 | 0.10529 | 123.9029 | 124.086 | 123.912 | 123.9349 | 123.8342 | -124.0631 | -123.9899 | 123.8068 | 123.8251 | 61.9766 | 61.9766
17.2969 | 123.9853 | -62.0316 | 61.9034 | -0.0096891 | 0.0030313 | 0.067857 | 0.06758 | 0.0019803 | -0.00080758 | 3.8448e-05 | 0.0018005 | 0.0054409 | 0.068274 | 0.056187 | -0.0039348 | 0.011164 | -0.000438 | -0.068665 | 61.9034 | -62.1689 | 61.7569 | -61.8301 | -62.1964 | -62.2284 | -0.064087 | 61.8118 | -62.0682 | 61.7844 | -62.0041 | -62.027 | -62.0132 | -0.13733 | 0 | -0.14648 | 0.20142 | -0.19684 | -0.1648 | -0.05951 | -0.027466 | -0.036621 | -0.091552 | -0.11902 | 0.027466 | 0.01831 | 0.004577 | 0.054931 | 0.041198 | 0.33874 | 123.9258 | 0.064087 | 123.8525 | 124.0723 | 123.88 | 123.9349 | 123.8434 | -124.0723 | -123.9716 | 123.7885 | 123.8159 | 61.9629 | 61.9675
18.9688 | 124.0997 | -62.0132 | 61.7981 | -0.0020601 | 0.0026041 | 0.070207 | 0.065871 | 0.0039029 | -0.0020892 | -0.00017515 | -0.0043029 | 0.0024503 | 0.068274 | 0.060032 | 0.0014056 | 0.011164 | 0.0008438 | -0.073242 | 61.7889 | -62.1552 | 61.8484 | -61.7386 | -62.1735 | -62.1964 | 0 | 61.6928 | -62.059 | 61.8851 | -61.9308 | -61.9629 | -61.94 | -0.14191 | -0.009156 | 0.050354 | 0.27466 | -0.18311 | -0.16022 | -0.041199 | -0.018311 | -0.045776 | -0.10529 | 0.086975 | 0.082398 | 0.073243 | 0.050354 | 0.11902 | 0.09613 | 0.41656 | 124.0036 | 0.12817 | 123.9441 | 123.9441 | 123.7518 | 123.8022 | 123.7061 | -123.9532 | -123.8571 | 123.8617 | 123.8983 | 61.94 | 62.0132
20.7188 | 123.9853 | -62.0132 | 61.8805 | 0.013199 | 0.0049539 | 0.069994 | 0.066298 | 0.0032619 | -0.0020892 | -0.0010298 | 0.0048523 | 0.0041593 | 0.067633 | 0.054905 | -0.0017986 | 0.012232 | -0.0062058 | 0.009155 | 61.8851 | -62.1277 | 61.853 | -61.7569 | -62.1735 | -62.1964 | -0.009155 | 61.7798 | -62.059 | 61.8301 | -61.9629 | -62.0041 | -61.9858 | -0.11444 | 0.004578 | -0.027466 | 0.25635 | -0.18311 | -0.16022 | -0.068664 | -0.045776 | -0.045776 | -0.10071 | -0.050354 | 0.050354 | 0.027466 | 0.009156 | 0.073242 | 0.054932 | 0.37079 | 123.9807 | 0.09613 | 123.8892 | 124.0128 | 123.8388 | 123.8983 | 123.793 | -124.0082 | -123.9395 | 123.8663 | 123.8434 | 62.0224 | 62.0041
22.4531 | 123.9761 | -62.0178 | 61.853 | -0.0020601 | 0.0049539 | 0.070207 | 0.066512 | 0.0024075 | -0.0020892 | 0.00046565 | 0.0018005 | 0.0045865 | 0.069769 | 0.058751 | 0.00055117 | 0.011377 | -0.0030014 | 0.004578 | 61.8759 | -62.146 | 61.8256 | -61.7661 | -62.1689 | -62.2009 | -0.004578 | 61.7935 | -62.027 | 61.8164 | -61.9812 | -62.0132 | -61.9858 | -0.12817 | 0.022889 | -0.027465 | 0.25177 | -0.18311 | -0.15106 | -0.054932 | -0.022888 | -0.009156 | -0.059509 | -0.036621 | 0.036621 | 0.032043 | 0.004577 | 0.041199 | 0.013733 | 0.37994 | 123.9716 | 0.045777 | 123.8434 | 124.0219 | 123.8205 | 123.8937 | 123.8113 | -123.999 | -123.88 | 123.8434 | 123.8342 | 62.0224 | 62.0132
24.1875 | 123.9578 | -62.0361 | 61.8668 | -0.0020601 | 0.0026041 | 0.069139 | 0.067152 | 0.0058255 | -0.001662 | -0.00017515 | -0.0043029 | 0.0056545 | 0.070624 | 0.063023 | -0.0024396 | 0.013086 | 0.0006302 | -0.07782 | 61.8988 | -62.1597 | 61.7569 | -61.8301 | -62.2513 | -62.2696 | -0.11444 | 61.7844 | -62.0453 | 61.7706 | -62.0499 | -62.059 | -62.027 | -0.1236 | 0.032044 | -0.10986 | 0.20599 | -0.23346 | -0.21515 | -0.10986 | -0.091553 | -0.009155 | -0.082397 | -0.09613 | -0.013733 | 0.009155 | -0.022888 | 0.01831 | -0.013733 | 0.32959 | 123.9166 | -0.004578 | 123.8159 | 124.0585 | 123.8297 | 123.9349 | 123.8205 | -124.0265 | -123.912 | 123.793 | 123.8068 | 61.9583 | 61.9217
25.9219 | 124.0265 | -62.0407 | 61.8164 | -0.0020601 | 0.0047403 | 0.06978 | 0.065871 | 0.00027134 | -0.0029438 | -0.001457 | -0.0012513 | 0.0035183 | 0.069128 | 0.061955 | -0.001585 | 0.015436 | -0.003856 | -0.12817 | 61.8805 | -62.1506 | 61.7432 | -61.8256 | -62.2467 | -62.265 | -0.10529 | 61.7615 | -62.0728 | 61.8256 | -62.0041 | -62.0087 | -61.9812 | -0.10986 | 0.064087 | -0.073242 | 0.21515 | -0.22431 | -0.20599 | -0.11444 | -0.09613 | -0.032044 | -0.054931 | 0.009156 | 0.036621 | 0.059509 | 0.032043 | 0.091553 | 0.064087 | 0.32501 | 123.8937 | 0.068665 | 123.8983 | 124.0311 | 123.8342 | 123.9212 | 123.8022 | -123.967 | -123.8892 | 123.7839 | 123.8663 | 61.9125 | 61.9354
27.5938 | 123.9899 | -62.0087 | 61.8988 | 0.043716 | 0.0038857 | 0.069139 | 0.067366 | 0.0019803 | -0.0029438 | 0.0011066 | 0.010956 | 0.0060819 | 0.070624 | 0.061741 | -0.0039348 | 0.011377 | 0.0004166 | -0.009155 | 61.9263 | -62.178 | 61.7844 | -61.7981 | -62.1689 | -62.1964 | -0.027466 | 61.8164 | -62.027 | 61.8164 | -61.94 | -61.9766 | -61.9583 | -0.16937 | 0.027466 | -0.11444 | 0.21057 | -0.18768 | -0.16022 | -0.01831 | 0.009156 | -0.018311 | -0.082398 | -0.082398 | 0.068665 | 0.050354 | 0.032043 | 0.068665 | 0.050354 | 0.37994 | 123.9624 | 0.086976 | 123.8434 | 124.1043 | 123.8434 | 123.9349 | 123.8251 | -124.0768 | -123.9258 | 123.793 | 123.8251 | 61.9995 | 61.9812
29.3438 | 124.0402 | -62.0361 | 61.7889 | 0.028458 | 0.0047403 | 0.068925 | 0.065016 | 0.0036893 | -0.0012348 | -0.00038875 | 0.0018005 | 0.0028775 | 0.069769 | 0.070713 | -0.0011578 | 0.012018 | -0.0006516 | -0.11444 | 61.8073 | -62.1643 | 61.7661 | -61.7935 | -62.2055 | -62.2192 | -0.082397 | 61.6837 | -62.0911 | 61.8027 | -61.9675 | -61.9812 | -61.9629 | -0.12817 | 0.018311 | -0.022888 | 0.24262 | -0.1831 | -0.16937 | -0.054931 | -0.041198 | -0.054931 | -0.10528 | 0.013733 | 0.068665 | 0.073242 | 0.054932 | 0.12817 | 0.10986 | 0.37079 | 123.9304 | 0.1236 | 123.8937 | 123.9716 | 123.7747 | 123.8434 | 123.7198 | -123.9532 | -123.88 | 123.8022 | 123.8388 | 61.9217 | 61.9537
31.0781 | 124.0219 | -62.0544 | 61.7844 | 0.020828 | 0.0021769 | 0.070421 | 0.064589 | -0.0031467 | -0.0037982 | -0.00060235 | 0.0018005 | 0.0048001 | 0.070196 | 0.065159 | -0.0037212 | 0.011805 | -0.0006516 | -0.091553 | 61.8347 | -62.1506 | 61.7661 | -61.7706 | -62.1826 | -62.2009 | -0.068665 | 61.6791 | -62.0865 | 61.8073 | -61.9995 | -62.0041 | -61.9858 | -0.096131 | 0.050354 | -0.018311 | 0.28381 | -0.14648 | -0.12817 | -0.050354 | -0.032043 | -0.032044 | -0.10529 | 0.022888 | 0.054931 | 0.068664 | 0.050354 | 0.10071 | 0.082398 | 0.37994 | 123.9166 | 0.086975 | 123.8937 | 123.9853 | 123.7656 | 123.8892 | 123.7335 | -123.9349 | -123.8708 | 123.8205 | 123.8617 | 61.9629 | 61.9858
32.8281 | 124.0723 | -62.0041 | 61.7615 | 0.0055694 | 0.0053811 | 0.069139 | 0.066084 | -0.0012241 | -0.0020892 | 0.00046565 | -0.0043029 | 0.0033047 | 0.068915 | 0.065587 | 0.0024738 | 0.014368 | 0.0006302 | -0.054932 | 61.7981 | -62.1231 | 61.8393 | -61.7203 | -62.1552 | -62.1735 | -0.009155 | 61.7111 | -62.0407 | 61.8713 | -61.9171 | -61.9446 | -61.9308 | -0.11902 | 0.036621 | 0.077819 | 0.28381 | -0.16937 | -0.15106 | -0.050354 | -0.032043 | -0.036621 | -0.050354 | 0.10986 | 0.086975 | 0.073242 | 0.059509 | 0.10986 | 0.09613 | 0.40283 | 123.9624 | 0.1236 | 123.912 | 123.9212 | 123.7518 | 123.8022 | 123.7152 | -123.8846 | -123.8022 | 123.8434 | 123.8754 | 61.9492 | 61.9949
34.5156 | 123.9258 | -62.0087 | 61.8439 | -0.0020601 | 0.0034585 | 0.069566 | 0.068007 | 0.0013393 | -0.0012348 | -0.001457 | -0.0012513 | 0.0058683 | 0.06806 | 0.062382 | -0.003294 | 0.011377 | 0.001271 | -0.054932 | 61.8759 | -62.1552 | 61.7249 | -61.8576 | -62.2559 | -62.2696 | -0.14648 | 61.7844 | -62.0682 | 61.7615 | -62.0407 | -62.0544 | -61.9995 | -0.14648 | 0.032044 | -0.11902 | 0.15106 | -0.26093 | -0.24719 | -0.11444 | -0.10071 | -0.059509 | -0.059509 | -0.082397 | -0.032043 | 0.009155 | -0.045776 | 0.068664 | 0.013733 | 0.29755 | 123.88 | 0.027466 | 123.8297 | 124.0311 | 123.8525 | 123.8846 | 123.793 | -123.999 | -123.912 | 123.7335 | 123.7701 | 61.9537 | 61.8622
36.2656 | 124.0036 | -62.0041 | 61.7844 | -0.0020601 | 0.0019631 | 0.071062 | 0.065016 | -0.00036966 | -0.003371 | 0.0021746 | -0.0043029 | 0.0037319 | 0.07041 | 0.061528 | -0.00094423 | 0.012873 | -0.0002244 | -0.1236 | 61.8713 | -62.178 | 61.734 | -61.8347 | -62.2559 | -62.2513 | -0.09613 | 61.7569 | -62.0636 | 61.8118 | -62.0087 | -62.0316 | -61.9812 | -0.17395 | 0.086975 | -0.050354 | 0.16937 | -0.24719 | -0.25177 | -0.073242 | -0.077819 | -0.05951 | -0.027466 | 0.027466 | -0.004578 | 0.022888 | -0.027466 | 0.082398 | 0.032044 | 0.34332 | 123.912 | 0.054932 | 123.8754 | 124.0494 | 123.8205 | 123.8754 | 123.761 | -123.9624 | -123.848 | 123.7381 | 123.8159 | 61.8805 | 61.908
38 | 123.9807 | -61.9858 | 61.8851 | 0.043716 | 0.0040995 | 0.069994 | 0.067152 | 0.0013393 | -0.0029438 | 0.001961 | 0.014008 | 0.0058683 | 0.071905 | 0.062169 | -0.0028668 | 0.011591 | -0.0036422 | -0.032043 | 61.9125 | -62.1826 | 61.7752 | -61.7981 | -62.1689 | -62.1918 | -0.022888 | 61.8164 | -62.0865 | 61.8073 | -61.9492 | -61.9583 | -61.94 | -0.19684 | 0.027466 | -0.10986 | 0.18768 | -0.20599 | -0.1831 | -0.009155 | 0.013733 | -0.10071 | -0.068665 | -0.07782 | 0.036621 | 0.045777 | 0.027466 | 0.14648 | 0.12817 | 0.38452 | 123.9578 | 0.13733 | 123.8937 | 124.0952 | 123.9029 | 123.8983 | 123.8022 | -124.0677 | -123.9716 | 123.761 | 123.793 | 61.9537 | 61.9629
39.6719 | 123.9532 | -62.0087 | 61.8851 | -0.0096891 | 0.0030313 | 0.06743 | 0.065657 | -0.00015586 | -0.0044392 | 3.8448e-05 | -0.0012513 | 0.0045865 | 0.07041 | 0.062382 | -0.0073528 | 0.010523 | -0.0023606 | -0.068665 | 61.8759 | -62.1643 | 61.734 | -61.8073 | -62.2009 | -62.2009 | -0.059509 | 61.7889 | -62.0773 | 61.7661 | -61.9949 | -62.0178 | -62.0041 | -0.15564 | -0.009155 | -0.15106 | 0.20142 | -0.19226 | -0.19226 | -0.036621 | -0.036621 | -0.068665 | -0.096131 | -0.11902 | 0.013733 | 0.004578 | -0.009155 | 0.073243 | 0.05951 | 0.35706 | 123.8983 | 0.082398 | 123.8434 | 124.0402 | 123.8663 | 123.8846 | 123.7976 | -124.0494 | -123.9624 | 123.7427 | 123.7747 | 61.94 | 61.9492
41.4062 | 123.967 | -62.0453 | 61.8393 | -0.0096891 | 0.0049539 | 0.068712 | 0.066725 | 0.0053983 | -0.00016658 | 0.00089285 | -0.0012513 | 0.0043729 | 0.070196 | 0.057255 | -0.0011578 | 0.012659 | 0.0010574 | -0.10071 | 61.8759 | -62.1506 | 61.7203 | -61.821 | -62.2467 | -62.2467 | -0.11444 | 61.7661 | -62.0499 | 61.7798 | -62.0224 | -62.0361 | -61.9949 | -0.10529 | 0.036622 | -0.11902 | 0.2243 | -0.20142 | -0.20142 | -0.09613 | -0.09613 | -0.004578 | -0.073242 | -0.059509 | 0.022888 | 0.050354 | 0.009155 | 0.054932 | 0.013733 | 0.32959 | 123.8708 | 0.027466 | 123.8297 | 124.0265 | 123.8159 | 123.9212 | 123.8113 | -123.9899 | -123.8892 | 123.7656 | 123.8251 | 61.9446 | 61.9308
43.1406 | 123.912 | -62.0087 | 61.853 | 0.0055694 | 0.0047403 | 0.069353 | 0.066939 | 0.00027134 | 0.00090142 | -0.0012434 | -0.0043029 | 0.0054409 | 0.068915 | 0.060887 | -0.002226 | 0.011591 | -0.0023606 | -0.086975 | 61.8805 | -62.146 | 61.7386 | -61.8393 | -62.2375 | -62.2513 | -0.13733 | 61.7844 | -62.0728 | 61.7477 | -62.0407 | -62.0636 | -61.9995 | -0.13733 | 0.027466 | -0.11444 | 0.16937 | -0.24262 | -0.22888 | -0.10529 | -0.091553 | -0.064087 | -0.068664 | -0.10528 | -0.032043 | 0.009155 | -0.054932 | 0.073242 | 0.009155 | 0.3067 | 123.8846 | 0.032044 | 123.8205 | 124.0265 | 123.8571 | 123.8892 | 123.793 | -123.999 | -123.9258 | 123.7473 | 123.7564 | 61.9217 | 61.8713
44.9062 | 123.9487 | -62.0224 | 61.8713 | -0.0096891 | 0.0038857 | 0.068925 | 0.065657 | 0.0011257 | -0.0031574 | -0.00038875 | -0.0043029 | 0.0037319 | 0.070196 | 0.063664 | -0.0056438 | 0.011164 | -1.0598e-05 | -0.064087 | 61.9034 | -62.1506 | 61.734 | -61.7935 | -62.1826 | -62.2009 | -0.064087 | 61.7706 | -62.0499 | 61.7569 | -61.9995 | -62.0087 | -61.9995 | -0.12817 | 0.032043 | -0.13733 | 0.22888 | -0.17853 | -0.16022 | -0.050354 | -0.032043 | -0.027466 | -0.10071 | -0.11444 | 0.022888 | 0.022888 | 0.013733 | 0.050354 | 0.041199 | 0.35706 | 123.8846 | 0.050354 | 123.8068 | 124.054 | 123.8205 | 123.9258 | 123.793 | -124.0219 | -123.9212 | 123.7564 | 123.7793 | 61.9583 | 61.9583
46.5625 | 123.9944 | -62.0361 | 61.7615 | 0.028458 | 0.0028177 | 0.06978 | 0.066298 | 5.774e-05 | -0.0010212 | -0.0016706 | 0.0048523 | 0.0037319 | 0.069983 | 0.062809 | -0.00051703 | 0.011377 | -0.002147 | -0.10529 | 61.7844 | -62.1552 | 61.7889 | -61.7615 | -62.178 | -62.1735 | -0.064087 | 61.7203 | -62.0773 | 61.7935 | -61.9629 | -61.9766 | -61.9766 | -0.11902 | 0.022888 | 0.027465 | 0.27466 | -0.13733 | -0.14191 | -0.018311 | -0.022889 | -0.041199 | -0.041199 | 0.032043 | 0.073242 | 0.059509 | 0.059509 | 0.10071 | 0.10071 | 0.39368 | 123.9441 | 0.11444 | 123.8708 | 123.9395 | 123.7976 | 123.8205 | 123.7564 | -123.9166 | -123.8388 | 123.8251 | 123.8297 | 61.9308 | 61.972
48.2969 | 124.0494 | -62.0178 | 61.7661 | 0.0055694 | 0.0019631 | 0.068925 | 0.064589 | -0.00079686 | -0.0025166 | -0.0018842 | 0.0018005 | 0.0033047 | 0.069128 | 0.066014 | -0.001585 | 0.014368 | 0.0034072 | -0.10529 | 61.8027 | -62.1689 | 61.7615 | -61.7706 | -62.1597 | -62.1872 | -0.050354 | 61.6882 | -62.0499 | 61.8164 | -61.9171 | -61.9354 | -61.9537 | -0.15106 | 0.036621 | -0.004577 | 0.24719 | -0.16937 | -0.14191 | -0.018311 | 0.009155 | -0.032044 | -0.07782 | 0.050354 | 0.10071 | 0.064087 | 0.082397 | 0.096131 | 0.11444 | 0.39825 | 123.9304 | 0.13275 | 123.8663 | 123.9716 | 123.7381 | 123.8205 | 123.7061 | -123.9349 | -123.8159 | 123.7793 | 123.8342 | 61.9125 | 61.9675
49.9688 | 124.0128 | -62.0132 | 61.7386 | 0.036087 | 0.0040995 | 0.069566 | 0.065657 | 0.00091214 | -0.0018756 | 0.00046565 | 0.010956 | 0.0052273 | 0.067847 | 0.072636 | -0.0030804 | 0.013514 | 0.0010574 | -0.073242 | 61.8027 | -62.1689 | 61.821 | -61.6837 | -62.1414 | -62.1506 | -0.009155 | 61.6928 | -62.0773 | 61.8164 | -61.9675 | -61.9812 | -61.9629 | -0.15564 | 0.064087 | 0.082398 | 0.32959 | -0.13733 | -0.12817 | 0.01831 | 0.027466 | -0.064087 | -0.045776 | 0.07782 | 0.045777 | 0.050354 | 0.032044 | 0.11444 | 0.096131 | 0.48523 | 123.9899 | 0.10986 | 123.8937 | 123.9716 | 123.7701 | 123.8159 | 123.7061 | -123.9075 | -123.8159 | 123.8342 | 123.8297 | 61.94 | 62.0041
51.7344 | 123.9899 | -61.9949 | 61.8027 | 0.0055694 | 0.0032449 | 0.068285 | 0.063735 | 0.0019803 | -0.0031574 | -0.00060235 | -0.0043029 | 0.0039457 | 0.069128 | 0.058964 | -0.0045758 | 0.013514 | -0.0006516 | 0 | 61.8164 | -62.1231 | 61.8256 | -61.6928 | -62.0956 | -62.1414 | 0.032043 | 61.7157 | -62.0132 | 61.8393 | -61.908 | -61.908 | -61.9308 | -0.12817 | 0.013733 | 0.022889 | 0.30212 | -0.14648 | -0.10071 | -0.01831 | 0.027466 | -0.018311 | -0.086975 | 0.036621 | 0.086975 | 0.064087 | 0.086975 | 0.082398 | 0.10529 | 0.4303 | 123.9487 | 0.10529 | 123.8525 | 123.9395 | 123.7289 | 123.8113 | 123.7106 | -123.9258 | -123.8159 | 123.8205 | 123.8342 | 61.9949 | 62.027
53.6719 | 123.9212 | -61.9949 | 61.8576 | 0.036087 | 0.0023905 | 0.069994 | 0.066298 | 0.00048494 | -0.001662 | -0.00081595 | 0.0079041 | 0.0069363 | 0.069983 | 0.055119 | -0.0041486 | 0.011377 | -0.0027878 | -0.027466 | 61.9217 | -62.1552 | 61.7615 | -61.7752 | -62.1643 | -62.2055 | -0.054932 | 61.8073 | -62.0499 | 61.7661 | -61.9675 | -61.9858 | -61.9492 | -0.16022 | 0.064087 | -0.09613 | 0.21973 | -0.21057 | -0.16937 | -0.050354 | -0.009156 | -0.054932 | -0.050354 | -0.091553 | 0.027466 | 0.045776 | 0.009155 | 0.10071 | 0.064087 | 0.37994 | 123.9166 | 0.082398 | 123.8159 | 124.0768 | 123.8571 | 123.9166 | 123.8022 | -124.0128 | -123.9075 | 123.7564 | 123.761 | 61.9675 | 61.94
55.3594 | 124.0082 | -62.0132 | 61.7752 | 0.028458 | 0.0026041 | 0.06978 | 0.066512 | -0.00015586 | 0.0026104 | -0.0038068 | 0.014008 | 0.0045865 | 0.06806 | 0.063664 | -0.00030343 | 0.013514 | -0.0040696 | -0.086975 | 61.8027 | -62.178 | 61.7844 | -61.7203 | -62.1643 | -62.1964 | -0.027466 | 61.6837 | -62.0728 | 61.8118 | -61.9446 | -61.9537 | -61.94 | -0.1648 | 0.027465 | 0.009155 | 0.29297 | -0.18311 | -0.15106 | -0.01831 | 0.013733 | -0.059509 | -0.091553 | 0.036621 | 0.068665 | 0.073243 | 0.05951 | 0.13275 | 0.11902 | 0.45776 | 123.9624 | 0.12817 | 123.8846 | 123.9807 | 123.7564 | 123.8159 | 123.6969 | -123.9532 | -123.848 | 123.7976 | 123.8251 | 61.9263 | 61.9858
57.0312 | 123.9578 | -61.9812 | 61.853 | 0.013199 | 0.0060221 | 0.069566 | 0.068861 | 0.0028347 | -0.0018756 | -0.00017515 | -0.0012513 | 0.0054409 | 0.069556 | 0.060887 | -0.0020122 | 0.011805 | -0.0074874 | 0.027466 | 61.8805 | -62.114 | 61.8301 | -61.7065 | -62.1231 | -62.146 | 0.050354 | 61.7889 | -62.0224 | 61.8439 | -61.9354 | -61.9583 | -61.9354 | -0.13275 | 0.027466 | -0.022888 | 0.27466 | -0.16479 | -0.14191 | -0.032043 | -0.009155 | -0.041199 | -0.064087 | -0.009155 | 0.045776 | 0.045776 | 0.022888 | 0.086975 | 0.064087 | 0.40741 | 123.9441 | 0.086975 | 123.8663 | 123.9944 | 123.8113 | 123.8617 | 123.7701 | -123.967 | -123.8754 | 123.8113 | 123.8251 | 62.0087 | 62.0316
58.6875 | 123.9578 | -61.9904 | 61.853 | 0.036087 | 0.0043131 | 0.067857 | 0.066298 | 0.0045437 | 0.00026062 | 0.00067925 | 0.0048523 | 0.0039457 | 0.071692 | 0.059391 | -0.0026532 | 0.013086 | -0.0006516 | 0.013733 | 61.8713 | -62.146 | 61.8073 | -61.7111 | -62.1231 | -62.1735 | 0.032043 | 61.7798 | -62.0178 | 61.8164 | -61.9171 | -61.9492 | -61.9308 | -0.15564 | 0.018311 | -0.045776 | 0.27923 | -0.18311 | -0.13275 | -0.027466 | 0.022888 | -0.027466 | -0.073242 | -0.036621 | 0.073242 | 0.059509 | 0.041198 | 0.086975 | 0.068664 | 0.43487 | 123.9532 | 0.10071 | 123.8342 | 124.0173 | 123.7976 | 123.8617 | 123.7701 | -123.999 | -123.8708 | 123.7976 | 123.8068 | 62.0041 | 62.0224
60.3438 | 123.9716 | -62.0178 | 61.7798 | 0.0055694 | 0.0047403 | 0.069353 | 0.065657 | -0.0031467 | -0.0025166 | -0.00017515 | -0.0043029 | 0.0020231 | 0.069342 | 0.063664 | -0.0026532 | 0.011805 | 0.0031936 | -0.10986 | 61.853 | -62.1323 | 61.7294 | -61.8118 | -62.2101 | -62.2559 | -0.082397 | 61.7294 | -62.0728 | 61.8073 | -61.9629 | -61.9904 | -61.9446 | -0.11444 | 0.073242 | -0.050354 | 0.20599 | -0.23804 | -0.19226 | -0.1236 | -0.07782 | -0.054932 | -0.050354 | 0.027466 | 0.054931 | 0.073242 | 0.027466 | 0.12817 | 0.082398 | 0.32043 | 123.8617 | 0.10986 | 123.88 | 123.9853 | 123.8022 | 123.8708 | 123.7473 | -123.912 | -123.8525 | 123.7473 | 123.8251 | 61.908 | 61.9354
62.0156 | 123.9487 | -61.9858 | 61.8439 | 0.036087 | 0.0073037 | 0.067644 | 0.065657 | -0.00015586 | -0.0042254 | 0.00025205 | 0.010956 | 0.0062955 | 0.070196 | 0.065159 | -0.0041486 | 0.011164 | -0.0008652 | 0.004578 | 61.8942 | -62.1231 | 61.7889 | -61.7294 | -62.1277 | -62.1689 | -0.009155 | 61.7661 | -62.0544 | 61.8027 | -61.9171 | -61.9446 | -61.9125 | -0.13733 | 0.050354 | -0.054932 | 0.25635 | -0.1831 | -0.14191 | -0.045776 | -0.004578 | -0.068664 | -0.07782 | -0.041199 | 0.068665 | 0.073242 | 0.041199 | 0.14191 | 0.10986 | 0.39368 | 123.912 | 0.13733 | 123.8571 | 124.0173 | 123.8205 | 123.88 | 123.7518 | -123.967 | -123.8983 | 123.7747 | 123.7885 | 61.9904 | 61.9766
64.0469 | 124.0448 | -62.0087 | 61.7569 | -0.024948 | 0.0047403 | 0.069566 | 0.06288 | 0.0013393 | -0.0044392 | -0.00038875 | 0.0018005 | 0.0026639 | 0.067206 | 0.060246 | -0.002226 | 0.014368 | -0.0010788 | -0.10071 | 61.7889 | -62.1368 | 61.7706 | -61.7294 | -62.1231 | -62.146 | 0.004578 | 61.6928 | -62.0544 | 61.8301 | -61.8851 | -61.8988 | -61.8942 | -0.12817 | 0.032043 | 0.013733 | 0.27924 | -0.13733 | -0.11444 | -0.009155 | 0.013733 | -0.045776 | -0.064087 | 0.073242 | 0.1236 | 0.11444 | 0.10986 | 0.16022 | 0.15564 | 0.40741 | 123.9075 | 0.16937 | 123.8846 | 123.9258 | 123.7473 | 123.7976 | 123.7015 | -123.8937 | -123.8113 | 123.7793 | 123.8388 | 61.908 | 62.0132
65.8438 | 124.0356 | -61.9904 | 61.7523 | -0.0096891 | 0.0034585 | 0.069566 | 0.065871 | 0.0043301 | -0.0018756 | -0.001457 | -0.0043029 | 0.0045865 | 0.066992 | 0.064305 | -0.0013714 | 0.015436 | -0.0040696 | -0.091553 | 61.7935 | -62.1231 | 61.7889 | -61.702 | -62.1414 | -62.1552 | -0.013733 | 61.6745 | -62.0178 | 61.8439 | -61.9125 | -61.9171 | -61.8942 | -0.13275 | 0.041199 | 0.036621 | 0.28839 | -0.16479 | -0.15106 | -0.032043 | -0.01831 | -0.027466 | -0.077819 | 0.091553 | 0.077819 | 0.09613 | 0.073242 | 0.1236 | 0.10071 | 0.42114 | 123.912 | 0.10529 | 123.8617 | 123.9166 | 123.6923 | 123.7839 | 123.6649 | -123.8754 | -123.7701 | 123.7793 | 123.8342 | 61.8988 | 61.9766
67.5156 | 124.0356 | -61.9995 | 61.7615 | -0.0020601 | 0.0019631 | 0.069139 | 0.063307 | -0.0014377 | -0.0012348 | 3.8448e-05 | -0.0043029 | 0.0028775 | 0.069556 | 0.069432 | -0.0020122 | 0.012659 | 0.0004166 | -0.091553 | 61.7798 | -62.1185 | 61.7798 | -61.7249 | -62.1277 | -62.1597 | -0.013733 | 61.6928 | -62.0453 | 61.8347 | -61.8759 | -61.8988 | -61.9125 | -0.11902 | 0.01831 | 0.01831 | 0.27466 | -0.16022 | -0.12817 | -0.041199 | -0.009156 | -0.045776 | -0.068665 | 0.073242 | 0.1236 | 0.086975 | 0.10071 | 0.13275 | 0.14648 | 0.39368 | 123.8983 | 0.16937 | 123.88 | 123.8983 | 123.7381 | 123.7793 | 123.6923 | -123.88 | -123.8068 | 123.7793 | 123.8342 | 61.908 | 61.9858
69.2031 | 124.0494 | -61.9904 | 61.7386 | 0.0055694 | 0.0021769 | 0.067003 | 0.065443 | -0.00036966 | -0.003371 | -0.004234 | 0.0018005 | 0.0018093 | 0.068701 | 0.06345 | -0.0011578 | 0.015009 | -0.0019332 | -0.082397 | 61.7798 | -62.1277 | 61.7752 | -61.7157 | -62.114 | -62.146 | 0.004578 | 61.6882 | -62.0407 | 61.8393 | -61.8713 | -61.8896 | -61.8896 | -0.13733 | 0.041199 | 0.036622 | 0.27466 | -0.15564 | -0.1236 | -0.01831 | 0.013733 | -0.050354 | -0.050354 | 0.10071 | 0.11902 | 0.10071 | 0.10071 | 0.15106 | 0.15106 | 0.41199 | 123.9029 | 0.16937 | 123.88 | 123.9075 | 123.7289 | 123.7701 | 123.6786 | -123.8663 | -123.7793 | 123.7656 | 123.8297 | 61.908 | 61.9949
70.8906 | 124.0219 | -61.9949 | 61.7523 | -0.0020601 | 0.00089511 | 0.066362 | 0.064589 | -0.0022923 | -0.0044392 | -0.0012434 | -0.0043029 | 0.0045865 | 0.069769 | 0.06345 | -0.0041486 | 0.0133 | -0.003856 | -0.041199 | 61.7523 | -62.114 | 61.8393 | -61.647 | -62.0682 | -62.1094 | 0.050354 | 61.6608 | -62.0361 | 61.8256 | -61.8622 | -61.8805 | -61.9034 | -0.11902 | 0 | 0.086975 | 0.3479 | -0.11444 | -0.073242 | 0.004578 | 0.045777 | -0.041199 | -0.091552 | 0.073243 | 0.13275 | 0.091553 | 0.11444 | 0.13275 | 0.15564 | 0.46692 | 123.9532 | 0.17395 | 123.8617 | 123.8663 | 123.6969 | 123.7473 | 123.6557 | -123.8663 | -123.7885 | 123.8342 | 123.8205 | 61.9537 | 62.0453
72.5938 | 123.8892 | -61.9949 | 61.8347 | -0.0020601 | 0.0051675 | 0.068712 | 0.068007 | 0.0011257 | -0.0037982 | 0.001961 | -0.0012513 | 0.0043729 | 0.069128 | 0.056187 | -0.0026532 | 0.011805 | -1.0598e-05 | -0.036621 | 61.8439 | -62.1048 | 61.7706 | -61.7615 | -62.2101 | -62.2055 | -0.064087 | 61.7569 | -62.0453 | 61.7706 | -61.9766 | -62.0178 | -61.9675 | -0.10986 | 0.009155 | -0.064087 | 0.23346 | -0.21057 | -0.21515 | -0.10071 | -0.10529 | -0.050354 | -0.07782 | -0.064087 | 0.01831 | 0.027466 | -0.022888 | 0.07782 | 0.027466 | 0.34332 | 123.8754 | 0.068664 | 123.8159 | 123.9487 | 123.8022 | 123.8388 | 123.7518 | -123.9395 | -123.88 | 123.7656 | 123.7656 | 61.9583 | 61.9308
74.3125 | 124.0128 | -61.9812 | 61.7432 | -0.0020601 | 0.0040995 | 0.067003 | 0.065443 | 0.00069854 | 4.7018e-05 | -0.0038068 | 0.017059 | 0.0043729 | 0.071265 | 0.060887 | 0.001192 | 0.0133 | -0.0053512 | -0.091553 | 61.7844 | -62.1277 | 61.853 | -61.6608 | -62.1002 | -62.1231 | 0.022888 | 61.6882 | -62.0499 | 61.8301 | -61.9034 | -61.9217 | -61.9125 | -0.14648 | 0.041199 | 0.10986 | 0.32043 | -0.14191 | -0.11902 | 0.004578 | 0.027466 | -0.068665 | -0.054932 | 0.086975 | 0.07782 | 0.068664 | 0.059509 | 0.13733 | 0.12817 | 0.46692 | 123.9807 | 0.14648 | 123.88 | 123.912 | 123.7381 | 123.7656 | 123.6694 | -123.8708 | -123.793 | 123.8342 | 123.8113 | 61.8896 | 62.0041
75.9688 | 124.0173 | -61.9858 | 61.7477 | -0.0020601 | 0.0026041 | 0.070634 | 0.066298 | 0.0026211 | -0.0012348 | -0.0010298 | -0.0073547 | 0.0039457 | 0.067419 | 0.070927 | -0.0028668 | 0.013086 | -0.0006516 | -0.059509 | 61.7615 | -62.1231 | 61.8027 | -61.7065 | -62.1323 | -62.1506 | 0.009155 | 61.7157 | -62.0224 | 61.8393 | -61.8851 | -61.9217 | -61.9034 | -0.13733 | 0.013733 | 0.054931 | 0.27924 | -0.16479 | -0.14648 | -0.027466 | -0.009155 | -0.036621 | -0.032044 | 0.091552 | 0.10071 | 0.082398 | 0.064087 | 0.11902 | 0.10071 | 0.41656 | 123.9258 | 0.13733 | 123.8617 | 123.8846 | 123.7381 | 123.7473 | 123.7015 | -123.8709 | -123.7701 | 123.7885 | 123.8251 | 61.9263 | 61.9949
77.625 | 123.999 | -61.9858 | 61.7386 | -0.0020601 | 0.0060221 | 0.073412 | 0.064803 | 0.00027134 | -0.00059378 | -0.00038875 | -0.0012513 | 0.0035183 | 0.07041 | 0.073491 | -8.9634e-05 | 0.014155 | -0.0040696 | -0.073242 | 61.8256 | -62.1048 | 61.7935 | -61.6974 | -62.1368 | -62.1643 | -0.004578 | 61.6745 | -62.0316 | 61.8393 | -61.9034 | -61.9217 | -61.8851 | -0.11902 | 0.086976 | 0.054932 | 0.28839 | -0.17853 | -0.15106 | -0.05951 | -0.032044 | -0.045776 | -0.064086 | 0.10071 | 0.082398 | 0.10071 | 0.064087 | 0.14648 | 0.10986 | 0.40741 | 123.8983 | 0.12817 | 123.8708 | 123.9304 | 123.7061 | 123.8113 | 123.6603 | -123.8434 | -123.7701 | 123.7793 | 123.8251 | 61.9125 | 61.9812
79.2812 | 124.0128 | -61.9766 | 61.7615 | 0.0055694 | 0.0049539 | 0.070207 | 0.066512 | 0.0028347 | -0.001662 | 0.00025205 | -0.0012513 | 0.0048001 | 0.067633 | 0.063237 | -0.0030804 | 0.013941 | -0.001506 | -0.059509 | 61.7661 | -62.1002 | 61.8027 | -61.6928 | -62.1277 | -62.146 | 0.018311 | 61.6928 | -62.027 | 61.8393 | -61.8942 | -61.908 | -61.8805 | -0.1236 | 0.004577 | 0.041198 | 0.28381 | -0.16937 | -0.15106 | -0.045776 | -0.027466 | -0.050354 | -0.068665 | 0.077819 | 0.082398 | 0.096131 | 0.068665 | 0.14648 | 0.11902 | 0.40741 | 123.9029 | 0.13275 | 123.8663 | 123.8663 | 123.7198 | 123.7427 | 123.6694 | -123.8617 | -123.7885 | 123.7793 | 123.8159 | 61.9171 | 61.9949
80.9375 | 123.999 | -61.9766 | 61.7523 | 0.0055694 | 0.0021769 | 0.067644 | 0.063094 | -0.0029331 | -0.0023028 | -0.0035932 | -0.0012513 | 0.0039457 | 0.069556 | 0.063023 | -0.0047894 | 0.012446 | -0.0044968 | -0.027466 | 61.7569 | -62.1185 | 61.8164 | -61.6608 | -62.0728 | -62.1185 | 0.059509 | 61.6745 | -62.0224 | 61.8164 | -61.853 | -61.8622 | -61.8805 | -0.14191 | 0.004578 | 0.064087 | 0.31586 | -0.14191 | -0.09613 | 0 | 0.045776 | -0.045776 | -0.077819 | 0.064087 | 0.1236 | 0.096131 | 0.11444 | 0.14191 | 0.16022 | 0.45776 | 123.9349 | 0.16937 | 123.8388 | 123.8754 | 123.6969 | 123.7335 | 123.6511 | -123.8708 | -123.7747 | 123.793 | 123.793 | 61.9492 | 62.0361
82.625 | 123.9944 | -61.9858 | 61.7706 | -0.0020601 | 0.0040995 | 0.066148 | 0.063948 | 0.0034755 | -0.0031574 | -0.0010298 | -0.0043029 | 0.0037319 | 0.069769 | 0.064305 | -0.0028668 | 0.013941 | -0.0051376 | -0.10529 | 61.7706 | -62.1368 | 61.7661 | -61.7111 | -62.1185 | -62.1414 | -0.004578 | 61.6608 | -62.0544 | 61.821 | -61.8759 | -61.8851 | -61.8851 | -0.15106 | 0 | -0.004578 | 0.27466 | -0.15564 | -0.13275 | -0.004577 | 0.018311 | -0.068664 | -0.10986 | 0.050354 | 0.10986 | 0.10071 | 0.10071 | 0.16937 | 0.16937 | 0.42572 | 123.9029 | 0.17853 | 123.8754 | 123.9075 | 123.7152 | 123.7564 | 123.6465 | -123.9075 | -123.8251 | 123.7518 | 123.8068 | 61.8805 | 61.9812
84.2812 | 123.999 | -61.9675 | 61.7477 | -0.0020601 | 0.0028177 | 0.067857 | 0.065016 | 0.0034755 | -0.0040118 | -0.0023114 | 0.0018005 | 0.0033047 | 0.068488 | 0.069218 | -0.0017986 | 0.013727 | 0.0006302 | -0.032043 | 61.7752 | -62.114 | 61.8256 | -61.6516 | -62.0453 | -62.1002 | 0.059509 | 61.702 | -62.0361 | 61.8256 | -61.8393 | -61.8668 | -61.8805 | -0.14649 | 0.027466 | 0.07782 | 0.31586 | -0.13275 | -0.07782 | 0.013733 | 0.068665 | -0.068665 | -0.045777 | 0.07782 | 0.12817 | 0.086975 | 0.10071 | 0.15564 | 0.16937 | 0.46234 | 123.9395 | 0.19684 | 123.8617 | 123.8892 | 123.7381 | 123.7427 | 123.6694 | -123.8617 | -123.7839 | 123.793 | 123.793 | 61.9354 | 62.027
85.9375 | 124.0219 | -61.9675 | 61.7386 | -0.0020601 | 0.0023905 | 0.068925 | 0.064589 | 0.00048494 | -0.0035846 | -0.0033796 | -0.0043029 | 0.0054409 | 0.069769 | 0.066655 | -0.002226 | 0.011377 | -0.0017196 | -0.050354 | 61.7661 | -62.114 | 61.8118 | -61.6379 | -62.0544 | -62.0773 | 0.073242 | 61.6791 | -62.0087 | 61.8347 | -61.8347 | -61.8439 | -61.8759 | -0.14649 | 0.027466 | 0.073243 | 0.32959 | -0.10986 | -0.086975 | 0.036621 | 0.05951 | -0.041199 | -0.059509 | 0.096131 | 0.13275 | 0.091552 | 0.1236 | 0.13275 | 0.1648 | 0.47608 | 123.9258 | 0.17395 | 123.8434 | 123.88 | 123.6877 | 123.7335 | 123.6465 | -123.8525 | -123.7473 | 123.7793 | 123.8022 | 61.9171 | 62.0407
87.6094 | 123.8617 | -61.9766 | 61.821 | -0.0096891 | 0.0015359 | 0.069994 | 0.068434 | -0.0031467 | -0.0044392 | -0.0016706 | -0.0043029 | 0.0035183 | 0.072119 | 0.056187 | -0.0071392 | 0.010523 | -0.0012924 | -0.050354 | 61.8393 | -62.1185 | 61.7157 | -61.7569 | -62.1552 | -62.1964 | -0.064087 | 61.7752 | -62.0407 | 61.7294 | -61.972 | -61.9949 | -61.9446 | -0.14191 | 0.01831 | -0.10529 | 0.21973 | -0.21973 | -0.17853 | -0.07782 | -0.036621 | -0.064086 | -0.045776 | -0.091553 | 0.004578 | 0.032044 | -0.01831 | 0.09613 | 0.045776 | 0.36163 | 123.8342 | 0.068664 | 123.7701 | 123.9578 | 123.8159 | 123.8159 | 123.7518 | -123.9395 | -123.8617 | 123.6923 | 123.7061 | 61.9263 | 61.9125
89.2656 | 123.88 | -61.9858 | 61.7889 | -0.0020601 | 0.0030313 | 0.066789 | 0.06523 | 0.0013393 | -0.0037982 | 3.8448e-05 | -0.0043029 | 0.0062955 | 0.068915 | 0.061314 | -0.0013714 | 0.01095 | -1.0598e-05 | -0.11902 | 61.8622 | -62.1231 | 61.6882 | -61.7844 | -62.2009 | -62.2192 | -0.10529 | 61.7386 | -62.0316 | 61.7477 | -61.9766 | -62.0087 | -61.9492 | -0.13733 | 0.073243 | -0.10071 | 0.20142 | -0.23346 | -0.21515 | -0.09613 | -0.07782 | -0.045776 | -0.050354 | -0.041198 | 0.009155 | 0.036621 | -0.022888 | 0.082397 | 0.022888 | 0.33875 | 123.8113 | 0.054931 | 123.7793 | 123.9853 | 123.7701 | 123.848 | 123.7244 | -123.912 | -123.8205 | 123.674 | 123.7335 | 61.8668 | 61.8805
90.9375 | 123.9944 | -61.972 | 61.7615 | -0.0020601 | 0.0028177 | 0.066362 | 0.065443 | 5.774e-05 | -0.0012348 | -0.0023114 | -0.0012513 | 0.0033047 | 0.067847 | 0.063023 | -0.0035076 | 0.012446 | -0.002147 | -0.032043 | 61.7706 | -62.114 | 61.8164 | -61.6241 | -62.059 | -62.1094 | 0.059509 | 61.6699 | -62.0316 | 61.821 | -61.8393 | -61.853 | -61.8805 | -0.14191 | 0.009155 | 0.054931 | 0.3479 | -0.13733 | -0.086975 | 0.004578 | 0.054932 | -0.059509 | -0.091553 | 0.059509 | 0.13275 | 0.091553 | 0.11902 | 0.15106 | 0.17853 | 0.48981 | 123.9304 | 0.19226 | 123.8525 | 123.8846 | 123.7015 | 123.7427 | 123.642 | -123.8754 | -123.793 | 123.7885 | 123.793 | 61.94 | 62.0316
92.6719 | 123.8663 | -61.9629 | 61.8393 | -0.0020601 | 0.0023905 | 0.06743 | 0.066939 | -0.0012241 | -0.003371 | -0.0010298 | 0.017059 | 0.0071499 | 0.07041 | 0.055119 | -0.0045758 | 0.010523 | -0.0002244 | -0.073242 | 61.8347 | -62.1277 | 61.6928 | -61.7661 | -62.1552 | -62.1826 | -0.032043 | 61.7981 | -62.0316 | 61.734 | -61.9492 | -61.9904 | -61.9446 | -0.16479 | -0.004577 | -0.14648 | 0.19684 | -0.21973 | -0.19226 | -0.054931 | -0.027465 | -0.068664 | -0.041198 | -0.10529 | 0.013733 | 0.018311 | -0.027465 | 0.086975 | 0.041199 | 0.36163 | 123.8205 | 0.082397 | 123.7656 | 123.9624 | 123.8297 | 123.7976 | 123.761 | -123.967 | -123.8708 | 123.6557 | 123.6969 | 61.8896 | 61.9308
94.3594 | 123.8846 | -61.9583 | 61.8484 | 0.036087 | 0.0055947 | 0.070207 | 0.066084 | 0.00091214 | -0.0023028 | -0.0010298 | 0.017059 | 0.0056545 | 0.070624 | 0.05811 | -0.002226 | 0.014155 | -0.0064194 | -0.018311 | 61.8851 | -62.0956 | 61.7569 | -61.7249 | -62.0911 | -62.1368 | 0.013733 | 61.7935 | -62.0087 | 61.7844 | -61.9171 | -61.9446 | -61.8988 | -0.13733 | 0.036621 | -0.091553 | 0.23346 | -0.17853 | -0.13275 | -0.041199 | 0.004578 | -0.050354 | -0.054932 | -0.064087 | 0.041199 | 0.059509 | 0.013733 | 0.10986 | 0.064087 | 0.37079 | 123.8525 | 0.091553 | 123.793 | 123.9807 | 123.8022 | 123.8434 | 123.7518 | -123.9441 | -123.8571 | 123.7152 | 123.7427 | 61.94 | 61.972
96.0312 | 123.9853 | -61.9675 | 61.7386 | 0.0055694 | 0.0026041 | 0.069994 | 0.068648 | 0.0026211 | -0.0029438 | -0.0012434 | -0.0043029 | 0.0024503 | 0.069342 | 0.057682 | -0.0011578 | 0.014155 | -0.0006516 | -0.064087 | 61.7798 | -62.1002 | 61.7844 | -61.6791 | -62.1094 | -62.1231 | -0.004578 | 61.6516 | -62.0132 | 61.8301 | -61.8851 | -61.9034 | -61.8713 | -0.13275 | 0.041199 | 0.045777 | 0.28839 | -0.15564 | -0.14191 | -0.022888 | -0.009155 | -0.045777 | -0.086975 | 0.091553 | 0.082397 | 0.09613 | 0.064087 | 0.14191 | 0.10986 | 0.42114 | 123.8846 | 0.12817 | 123.8434 | 123.88 | 123.6649 | 123.7473 | 123.6191 | -123.8388 | -123.7518 | 123.7518 | 123.7976 | 61.9034 | 61.9629
97.7031 | 123.8663 | -61.9904 | 61.7844 | 0.0055694 | 0.0030313 | 0.06978 | 0.063948 | -0.0010105 | -0.00508 | -0.0016706 | 0.0018005 | 0.0035183 | 0.070837 | 0.059819 | -0.0028668 | 0.011591 | -0.0072738 | -0.027466 | 61.7981 | -62.1094 | 61.7432 | -61.7157 | -62.1094 | -62.1506 | -0.022888 | 61.7065 | -61.9995 | 61.7477 | -61.94 | -61.9446 | -61.9354 | -0.11902 | 0.013733 | -0.041199 | 0.27466 | -0.16022 | -0.11902 | -0.041199 | 0 | -0.009156 | -0.07782 | -0.036621 | 0.050354 | 0.054931 | 0.045776 | 0.064087 | 0.054932 | 0.39368 | 123.8525 | 0.05951 | 123.7473 | 123.9075 | 123.7061 | 123.7885 | 123.6969 | -123.8937 | -123.7839 | 123.7335 | 123.7381 | 61.9629 | 61.9675
99.3594 | 123.912 | -61.9858 | 61.7844 | -0.0096891 | 0.0049539 | 0.069566 | 0.064375 | -0.0014377 | -0.0027302 | -0.0012434 | -0.0012513 | 0.0048001 | 0.068488 | 0.061314 | -0.0035076 | 0.012659 | -0.0017196 | -0.013733 | 61.8027 | -62.1094 | 61.7935 | -61.6653 | -62.0682 | -62.1185 | 0.018311 | 61.6974 | -61.9995 | 61.7935 | -61.8759 | -61.8988 | -61.8805 | -0.1236 | 0.01831 | 0.009155 | 0.32044 | -0.13275 | -0.082397 | -0.009155 | 0.041199 | -0.013733 | -0.086975 | 0.009155 | 0.10986 | 0.10529 | 0.086975 | 0.11902 | 0.10071 | 0.44403 | 123.9029 | 0.1236 | 123.793 | 123.912 | 123.6969 | 123.7885 | 123.6832 | -123.8937 | -123.7839 | 123.7793 | 123.7793 | 61.972 | 62.0041
101.0312 | 123.88 | -61.9949 | 61.7706 | -0.0020601 | 0.0036721 | 0.069566 | 0.066725 | 0.00027134 | -0.0044392 | -0.00060235 | -0.0043029 | 0.0050137 | 0.071692 | 0.059605 | -0.00073063 | 0.013727 | -0.003215 | -0.1236 | 61.8713 | -62.1048 | 61.6837 | -61.7935 | -62.1964 | -62.2147 | -0.1236 | 61.7386 | -62.0087 | 61.7432 | -61.972 | -61.9949 | -61.9446 | -0.10986 | 0.10071 | -0.086975 | 0.20142 | -0.21973 | -0.20142 | -0.10986 | -0.091553 | -0.013733 | -0.032044 | -0.027466 | 0.022888 | 0.050354 | 0 | 0.064087 | 0.013733 | 0.31128 | 123.7885 | 0.036621 | 123.7518 | 123.9761 | 123.7473 | 123.8663 | 123.7335 | -123.8754 | -123.7793 | 123.6786 | 123.7381 | 61.8713 | 61.8713
102.7188 | 123.848 | -62.0041 | 61.821 | -0.0020601 | 0.0060221 | 0.070848 | 0.066298 | 0.00048494 | -0.0037982 | -0.00060235 | -0.0012513 | 0.0054409 | 0.071478 | 0.056614 | -0.00051703 | 0.013086 | -0.0008652 | -0.091553 | 61.8622 | -62.1094 | 61.6699 | -61.8347 | -62.233 | -62.2284 | -0.10986 | 61.7477 | -61.9995 | 61.7386 | -61.972 | -61.9995 | -61.9492 | -0.10529 | 0.041199 | -0.15106 | 0.16937 | -0.22431 | -0.22888 | -0.11902 | -0.1236 | 0.004577 | -0.073242 | -0.082398 | 0.032043 | 0.054931 | 0.004577 | 0.050354 | 0 | 0.27466 | 123.7793 | 0.027466 | 123.7381 | 123.9716 | 123.7473 | 123.8663 | 123.7518 | -123.9304 | -123.8205 | 123.674 | 123.7427 | 61.9125 | 61.8942
104.375 | 123.9029 | -61.972 | 61.7935 | 0.013199 | 0.0064493 | 0.07213 | 0.068007 | 0.0058255 | -0.0018756 | -0.00060235 | 0.0018005 | 0.0060819 | 0.069983 | 0.062809 | -0.0024396 | 0.013514 | 0.0006302 | 0.009155 | 61.8576 | -62.0819 | 61.7706 | -61.6745 | -62.0911 | -62.1231 | 0.013733 | 61.7386 | -62.0041 | 61.7889 | -61.8988 | -61.9263 | -61.908 | -0.10986 | 0.064087 | -0.022888 | 0.29755 | -0.15106 | -0.11902 | -0.041199 | -0.009155 | -0.032043 | -0.054932 | -0.004578 | 0.073242 | 0.064087 | 0.045776 | 0.09613 | 0.077819 | 0.40741 | 123.8525 | 0.10529 | 123.793 | 123.9395 | 123.7427 | 123.8297 | 123.7106 | -123.8754 | -123.7976 | 123.7427 | 123.761 | 61.9812 | 61.9858
106.0469 | 123.967 | -61.9629 | 61.7386 | -0.0096891 | 0.0034585 | 0.068071 | 0.065657 | 5.774e-05 | -0.0010212 | -0.0029524 | -0.0043029 | 0.0020231 | 0.070624 | 0.066441 | -0.0020122 | 0.014582 | 0.0025528 | -0.086975 | 61.7706 | -62.0865 | 61.7615 | -61.6516 | -62.0728 | -62.1048 | 0.027466 | 61.6608 | -62.0178 | 61.8164 | -61.8484 | -61.8622 | -61.8668 | -0.1236 | 0.032044 | 0.022889 | 0.31128 | -0.14191 | -0.10986 | -0.01831 | 0.013733 | -0.054931 | -0.077819 | 0.07782 | 0.11444 | 0.096131 | 0.10071 | 0.15106 | 0.15564 | 0.43488 | 123.848 | 0.16937 | 123.8342 | 123.8571 | 123.6786 | 123.7335 | 123.6237 | -123.8251 | -123.7564 | 123.7244 | 123.7793 | 61.8759 | 61.9904
107.7344 | 123.9578 | -61.9537 | 61.7386 | -0.0020601 | 0.0032449 | 0.070207 | 0.064589 | 0.00048494 | -0.0023028 | -0.0020978 | -0.0012513 | 0.0024503 | 0.068488 | 0.0658 | -0.002226 | 0.014795 | -0.003215 | -0.11444 | 61.7523 | -62.114 | 61.7294 | -61.7157 | -62.1185 | -62.1414 | -0.032043 | 61.647 | -62.0132 | 61.7706 | -61.8622 | -61.8668 | -61.8713 | -0.16022 | 0.013733 | -0.009155 | 0.23804 | -0.18768 | -0.16479 | -0.027465 | -0.004577 | -0.05951 | -0.091552 | 0.032044 | 0.091552 | 0.082397 | 0.086975 | 0.14191 | 0.14648 | 0.39825 | 123.8434 | 0.15106 | 123.7839 | 123.8663 | 123.6603 | 123.7061 | 123.6008 | -123.8525 | -123.7518 | 123.6832 | 123.7244 | 61.8393 | 61.9217
109.4219 | 123.9487 | -61.9675 | 61.7386 | -0.0020601 | 0.0028177 | 0.068712 | 0.067366 | 0.0021939 | -0.0027302 | 0.00025205 | -0.0012513 | 0.0052273 | 0.067847 | 0.065159 | 0.001192 | 0.012659 | 0.0010574 | -0.10986 | 61.8118 | -62.1185 | 61.7157 | -61.734 | -62.1643 | -62.1735 | -0.045776 | 61.6745 | -61.9995 | 61.8073 | -61.8759 | -61.9125 | -61.8576 | -0.15106 | 0.073243 | -0.022888 | 0.23346 | -0.20599 | -0.19684 | -0.054932 | -0.045777 | -0.032044 | -0.064086 | 0.068665 | 0.091552 | 0.10986 | 0.054931 | 0.14191 | 0.086975 | 0.38452 | 123.8342 | 0.1236 | 123.8068 | 123.9304 | 123.674 | 123.7793 | 123.642 | -123.8571 | -123.7381 | 123.6832 | 123.7747 | 61.8576 | 61.9217
111.0781 | 123.9441 | -61.9812 | 61.7111 | 0.0055694 | 0.0038857 | 0.066789 | 0.064375 | -0.0012241 | -0.0018756 | -0.0010298 | 0.0018005 | 0.0011685 | 0.069342 | 0.060673 | -0.0011578 | 0.0133 | -0.0012924 | -0.1236 | 61.7386 | -62.1094 | 61.702 | -61.7249 | -62.1277 | -62.146 | -0.064087 | 61.6882 | -62.027 | 61.7798 | -61.8805 | -61.8942 | -61.9034 | -0.12817 | 0.027465 | -0.009156 | 0.25635 | -0.16479 | -0.14648 | -0.036621 | -0.018311 | -0.045777 | -0.022889 | 0.068664 | 0.10071 | 0.07782 | 0.086975 | 0.1236 | 0.13275 | 0.38452 | 123.8113 | 0.14648 | 123.8068 | 123.848 | 123.7152 | 123.7198 | 123.6694 | -123.8205 | -123.7381 | 123.6832 | 123.761 | 61.8576 | 61.9171
112.8125 | 123.9075 | -61.9766 | 61.7111 | 0.028458 | 0.0047403 | 0.071062 | 0.065657 | 0.00048494 | -0.0025166 | -0.00017515 | 0.0048523 | 0.0060819 | 0.070624 | 0.065587 | -0.001585 | 0.013514 | -0.0008652 | -0.10986 | 61.7661 | -62.0911 | 61.7294 | -61.7111 | -62.1231 | -62.1506 | -0.064087 | 61.6699 | -62.0407 | 61.7523 | -61.9354 | -61.94 | -61.9217 | -0.11444 | 0.054931 | 0.01831 | 0.2655 | -0.17395 | -0.14648 | -0.05951 | -0.032044 | -0.064086 | -0.041199 | 0.041198 | 0.041199 | 0.054932 | 0.036622 | 0.11902 | 0.10071 | 0.37994 | 123.8205 | 0.10528 | 123.793 | 123.8571 | 123.7106 | 123.7427 | 123.6465 | -123.8022 | -123.7518 | 123.7061 | 123.7289 | 61.8668 | 61.9125
114.5312 | 123.912 | -61.9949 | 61.7249 | 0.020828 | 0.0045267 | 0.070634 | 0.068221 | 0.0028347 | -0.0025166 | -0.00060235 | 0.0048523 | 0.0058683 | 0.068915 | 0.068577 | -0.00073063 | 0.013727 | 0.0004166 | -0.11444 | 61.7203 | -62.1368 | 61.7615 | -61.6928 | -62.114 | -62.1231 | -0.045776 | 61.6653 | -62.0316 | 61.734 | -61.9308 | -61.94 | -61.9034 | -0.14191 | -0.004578 | 0.036621 | 0.30212 | -0.12817 | -0.11902 | 0.013733 | 0.022888 | -0.036621 | -0.05951 | 0.009155 | 0.064087 | 0.091553 | 0.054932 | 0.12817 | 0.091553 | 0.44403 | 123.8983 | 0.10071 | 123.7656 | 123.8571 | 123.6969 | 123.7152 | 123.6603 | -123.8617 | -123.7564 | 123.7564 | 123.7289 | 61.8805 | 61.9492
116.1875 | 123.9304 | -61.94 | 61.7523 | -0.0020601 | 0.0043131 | 0.068925 | 0.066084 | -0.0012241 | -0.0010212 | -0.001457 | -0.0043029 | 0.0054409 | 0.069983 | 0.066014 | -0.00094423 | 0.012446 | -0.0047104 | -0.10529 | 61.8118 | -62.1094 | 61.7111 | -61.7661 | -62.1826 | -62.1826 | -0.082397 | 61.702 | -62.0178 | 61.7798 | -61.8942 | -61.9171 | -61.8759 | -0.16937 | 0.05951 | -0.041198 | 0.17395 | -0.24262 | -0.24262 | -0.073242 | -0.073242 | -0.07782 | -0.050354 | 0.027466 | 0.045776 | 0.064086 | 0.022888 | 0.14191 | 0.10071 | 0.34332 | 123.8205 | 0.1236 | 123.7976 | 123.9212 | 123.7198 | 123.7518 | 123.642 | -123.8617 | -123.7701 | 123.6511 | 123.7198 | 61.8347 | 61.8576
117.8906 | 123.9624 | -61.9537 | 61.7203 | -0.0020601 | 0.00046791 | 0.068071 | 0.06523 | 0.00048494 | -0.0029438 | -0.00017515 | -0.0012513 | 0.0026639 | 0.069769 | 0.071782 | -0.0028668 | 0.013086 | 0.0006302 | -0.091553 | 61.7477 | -62.0956 | 61.7432 | -61.6837 | -62.0682 | -62.1277 | -0.004578 | 61.6653 | -62.0178 | 61.8027 | -61.8484 | -61.8484 | -61.8576 | -0.14191 | 0.027466 | 0.022888 | 0.27008 | -0.17395 | -0.11444 | -0.032044 | 0.027466 | -0.064087 | -0.054932 | 0.082397 | 0.10529 | 0.09613 | 0.10529 | 0.16022 | 0.16937 | 0.41199 | 123.8388 | 0.16937 | 123.8205 | 123.8434 | 123.6832 | 123.7015 | 123.6191 | -123.8159 | -123.7381 | 123.6969 | 123.7564 | 61.8622 | 61.9492
119.6094 | 123.8525 | -61.9354 | 61.8073 | 0.028458 | 0.0064493 | 0.069566 | 0.066512 | 0.0030483 | -0.0027302 | 0.0017474 | 0.020111 | 0.0071499 | 0.070837 | 0.059605 | -0.0056438 | 0.012659 | 0.0016982 | -0.022888 | 61.8484 | -62.1323 | 61.7615 | -61.7111 | -62.0819 | -62.1185 | -0.009155 | 61.7935 | -61.9583 | 61.7523 | -61.9034 | -61.9171 | -61.8759 | -0.19684 | 0.041199 | -0.045776 | 0.2243 | -0.1831 | -0.14648 | 0.013733 | 0.050354 | -0.022888 | -0.013733 | -0.054932 | 0.032044 | 0.059509 | 0.018311 | 0.082397 | 0.041199 | 0.42114 | 123.8937 | 0.054932 | 123.7106 | 123.9807 | 123.7518 | 123.7839 | 123.7289 | -123.9395 | -123.7656 | 123.6969 | 123.6877 | 61.9125 | 61.9263
121.3125 | 123.9395 | -61.9354 | 61.7157 | -0.0096891 | 0.0019631 | 0.069566 | 0.065443 | -0.0018649 | -0.0029438 | 3.8448e-05 | -0.0012513 | 0.0041593 | 0.06806 | 0.060032 | -0.0041486 | 0.011805 | -1.0598e-05 | -0.050354 | 61.7569 | -62.1048 | 61.7981 | -61.615 | -62.0499 | -62.0728 | 0.064087 | 61.647 | -61.9766 | 61.8027 | -61.821 | -61.853 | -61.8576 | -0.16937 | 0.041199 | 0.082398 | 0.32044 | -0.13733 | -0.11444 | 0.032043 | 0.054931 | -0.041199 | -0.068664 | 0.086975 | 0.11444 | 0.07782 | 0.082398 | 0.11902 | 0.1236 | 0.48981 | 123.9029 | 0.15564 | 123.7793 | 123.8617 | 123.6237 | 123.6923 | 123.5825 | -123.8205 | -123.6923 | 123.7335 | 123.7381 | 61.8851 | 61.9995
122.9844 | 123.8663 | -61.9354 | 61.7752 | 0.020828 | 0.0047403 | 0.06978 | 0.068007 | 0.0043301 | -0.0025166 | -0.0023114 | 0.0048523 | 0.0065091 | 0.069769 | 0.058964 | -0.0011578 | 0.01095 | -0.001506 | -0.009155 | 61.8576 | -62.0956 | 61.7935 | -61.6562 | -62.0773 | -62.1048 | 0.022888 | 61.7569 | -61.9766 | 61.7752 | -61.8851 | -61.9217 | -61.8668 | -0.16022 | 0.082397 | 0.01831 | 0.27924 | -0.16937 | -0.14191 | -0.009155 | 0.01831 | -0.041199 | -0.018311 | 0 | 0.050354 | 0.068665 | 0.013733 | 0.10986 | 0.054932 | 0.43945 | 123.8892 | 0.091553 | 123.7518 | 123.9532 | 123.7335 | 123.793 | 123.6923 | -123.8708 | -123.7518 | 123.7289 | 123.7106 | 61.9263 | 61.9583
124.6562 | 123.8205 | -61.9858 | 61.7661 | -0.0020601 | 0.0049539 | 0.070421 | 0.067366 | -0.0016513 | -0.0012348 | -0.0012434 | 0.0018005 | 0.0067227 | 0.072546 | 0.058537 | -0.001585 | 0.014368 | 0.0006302 | -0.091553 | 61.8301 | -62.0956 | 61.6745 | -61.7935 | -62.1872 | -62.2101 | -0.11902 | 61.7294 | -62.0041 | 61.6928 | -61.9583 | -61.9904 | -61.9354 | -0.10986 | 0.064087 | -0.091552 | 0.19226 | -0.2243 | -0.20142 | -0.11444 | -0.091553 | -0.01831 | -0.036621 | -0.073242 | 0.027466 | 0.050354 | -0.004577 | 0.068664 | 0.013733 | 0.30212 | 123.7701 | 0.045776 | 123.6969 | 123.9258 | 123.7335 | 123.8159 | 123.7152 | -123.8617 | -123.7701 | 123.6603 | 123.6786 | 61.8942 | 61.8668
126.3281 | 123.8342 | -61.9492 | 61.7935 | -0.0020601 | 0.0028177 | 0.066789 | 0.064803 | 0.0068935 | -0.0029438 | 3.8448e-05 | 0.014008 | 0.0071499 | 0.070837 | 0.051701 | -0.0047894 | 0.011377 | 0.000203 | -0.068665 | 61.8073 | -62.0911 | 61.7111 | -61.7203 | -62.1002 | -62.1368 | -0.045776 | 61.7661 | -62.0224 | 61.7111 | -61.9217 | -61.94 | -61.9034 | -0.14191 | 0.013733 | -0.082397 | 0.22888 | -0.18768 | -0.15106 | -0.045777 | -0.009156 | -0.073242 | -0.027466 | -0.082397 | 0.027466 | 0.045777 | 0.009156 | 0.11902 | 0.082398 | 0.37079 | 123.8022 | 0.10071 | 123.7335 | 123.8983 | 123.7885 | 123.7564 | 123.7152 | -123.8846 | -123.8159 | 123.6603 | 123.6603 | 61.8805 | 61.9034
128 | 123.9349 | -61.9537 | 61.7065 | -0.0020601 | 0.0043131 | 0.070421 | 0.064803 | 0.00048494 | -0.0012348 | 0.0021746 | 0.010956 | 0.0030911 | 0.069769 | 0.065159 | 0.00033757 | 0.014368 | 0.0004166 | -0.082397 | 61.7569 | -62.0728 | 61.7844 | -61.6196 | -62.0316 | -62.0865 | 0.018311 | 61.6745 | -62.0087 | 61.7935 | -61.8347 | -61.8759 | -61.8393 | -0.11902 | 0.050354 | 0.07782 | 0.33417 | -0.13275 | -0.07782 | -0.013733 | 0.041199 | -0.054932 | -0.032043 | 0.086975 | 0.11902 | 0.11444 | 0.077819 | 0.16937 | 0.13275 | 0.45319 | 123.8571 | 0.17395 | 123.8022 | 123.8297 | 123.6832 | 123.7106 | 123.6282 | -123.7793 | -123.7152 | 123.7381 | 123.7473 | 61.8713 | 61.972
129.6719 | 123.8709 | -61.9217 | 61.7981 | 0.028458 | 0.0034585 | 0.069353 | 0.065443 | -0.0010105 | -0.00059378 | 0.0023882 | 0.0079041 | 0.0060819 | 0.069342 | 0.064305 | -0.0030804 | 0.012873 | 0.001912 | 0.009155 | 61.8713 | -62.0865 | 61.7477 | -61.6882 | -62.0773 | -62.1002 | 0.004578 | 61.7477 | -61.972 | 61.7477 | -61.8713 | -61.8942 | -61.8576 | -0.16479 | 0.073242 | -0.050354 | 0.23346 | -0.17853 | -0.15564 | -0.013733 | 0.009155 | -0.050354 | -0.050354 | -0.050354 | 0.050354 | 0.064087 | 0.027466 | 0.11444 | 0.07782 | 0.39825 | 123.8342 | 0.10071 | 123.7198 | 123.9578 | 123.7198 | 123.793 | 123.6694 | -123.8846 | -123.7701 | 123.6694 | 123.6694 | 61.9308 | 61.9263
131.3438 | 123.9578 | -61.972 | 61.7294 | 0.013199 | 0.0043131 | 0.067644 | 0.062666 | 0.0024075 | -0.0029438 | -0.0020978 | -0.0012513 | 0.0033047 | 0.069342 | 0.065587 | -0.005003 | 0.014582 | -0.0019332 | -0.10071 | 61.7432 | -62.1002 | 61.7249 | -61.6791 | -62.0773 | -62.1048 | -0.018311 | 61.6425 | -61.9995 | 61.7889 | -61.8393 | -61.8622 | -61.853 | -0.12817 | 0.013733 | -0.004577 | 0.29297 | -0.13275 | -0.10529 | -0.004577 | 0.022888 | -0.027466 | -0.086975 | 0.059509 | 0.13275 | 0.11902 | 0.10986 | 0.14649 | 0.13733 | 0.42114 | 123.8251 | 0.16022 | 123.7885 | 123.8434 | 123.642 | 123.7152 | 123.6145 | -123.8297 | -123.7289 | 123.6969 | 123.761 | 61.8713 | 61.9537
133.0156 | 123.8068 | -61.9446 | 61.7935 | -0.0020601 | 0.0055947 | 0.06743 | 0.067793 | 0.00069854 | -0.0035846 | 0.0026018 | 0.0079041 | 0.0060819 | 0.069342 | 0.060246 | -0.0064984 | 0.011164 | 0.0006302 | -0.059509 | 61.8027 | -62.0682 | 61.702 | -61.7203 | -62.1048 | -62.1277 | -0.054932 | 61.7569 | -61.9949 | 61.702 | -61.9354 | -61.9537 | -61.8988 | -0.1236 | 0.009155 | -0.091553 | 0.2243 | -0.18311 | -0.16022 | -0.05951 | -0.036621 | -0.050354 | -0.036621 | -0.091553 | 0.009155 | 0.045776 | -0.009155 | 0.09613 | 0.041199 | 0.3479 | 123.7701 | 0.059509 | 123.6969 | 123.8708 | 123.7518 | 123.7473 | 123.7015 | -123.8617 | -123.7885 | 123.6465 | 123.6465 | 61.8851 | 61.8896
134.7188 | 123.9532 | -61.94 | 61.702 | -0.0096891 | 0.0019631 | 0.070634 | 0.063307 | 0.0047573 | -0.0029438 | -0.00060235 | -0.0012513 | 0.0022367 | 0.070837 | 0.064518 | -0.002226 | 0.013086 | -0.0012924 | -0.054932 | 61.734 | -62.0819 | 61.7889 | -61.5967 | -62.027 | -62.059 | 0.064087 | 61.6333 | -61.9629 | 61.7889 | -61.8164 | -61.8393 | -61.853 | -0.14191 | 0.032044 | 0.086975 | 0.34332 | -0.11902 | -0.086976 | 0.022888 | 0.054931 | -0.022889 | -0.068664 | 0.086975 | 0.1236 | 0.086975 | 0.10071 | 0.10986 | 0.1236 | 0.48523 | 123.8708 | 0.14648 | 123.7518 | 123.8159 | 123.5962 | 123.674 | 123.5733 | -123.7839 | -123.6649 | 123.7289 | 123.7289 | 61.8851 | 62.0041
136.4219 | 123.8251 | -61.9629 | 61.7569 | 0.0055694 | 0.0045267 | 0.068498 | 0.065443 | 0.0034755 | -0.0029438 | -0.001457 | -0.0043029 | 0.0058683 | 0.067847 | 0.061314 | -0.00030343 | 0.014582 | 0.000203 | -0.10529 | 61.8301 | -62.0773 | 61.6562 | -61.7752 | -62.1735 | -62.1872 | -0.10071 | 61.7111 | -61.9812 | 61.7065 | -61.94 | -61.9766 | -61.8942 | -0.11444 | 0.073242 | -0.10071 | 0.18768 | -0.2243 | -0.21057 | -0.10986 | -0.09613 | -0.01831 | -0.045776 | -0.050354 | 0.022889 | 0.068665 | -0.013733 | 0.086975 | 0.004577 | 0.30212 | 123.7335 | 0.041199 | 123.6877 | 123.9075 | 123.6923 | 123.793 | 123.674 | -123.8342 | -123.7381 | 123.6191 | 123.6694 | 61.8576 | 61.8622
138.1094 | 123.8937 | -61.9675 | 61.7111 | 0.020828 | 0.0036721 | 0.069994 | 0.064803 | 0.0026211 | -0.00038018 | 0.00046565 | 0.010956 | 0.0026639 | 0.069128 | 0.070073 | -0.001585 | 0.013941 | -0.0023606 | -0.11902 | 61.7294 | -62.1094 | 61.7203 | -61.6837 | -62.0956 | -62.1277 | -0.045776 | 61.6653 | -61.9995 | 61.734 | -61.8942 | -61.908 | -61.908 | -0.14191 | 0.01831 | 0.009155 | 0.28381 | -0.16022 | -0.12817 | -0.018311 | 0.013733 | -0.032044 | -0.045777 | 0.022888 | 0.073242 | 0.059509 | 0.059509 | 0.091553 | 0.091553 | 0.42572 | 123.8297 | 0.10529 | 123.7335 | 123.8388 | 123.6649 | 123.6969 | 123.6328 | -123.8205 | -123.7106 | 123.6877 | 123.7015 | 61.8484 | 61.9217
139.8281 | 123.9304 | -61.9308 | 61.7111 | -0.0020601 | 0.0055947 | 0.069353 | 0.064375 | 0.00027134 | -0.003371 | 0.00089285 | -0.0073547 | 0.0052273 | 0.069769 | 0.060887 | -0.00051703 | 0.014795 | -0.0027878 | -0.064087 | 61.7432 | -62.0682 | 61.7615 | -61.6425 | -62.0819 | -62.114 | 0.013733 | 61.6287 | -61.9812 | 61.7935 | -61.8393 | -61.8576 | -61.8347 | -0.13733 | 0.032043 | 0.050354 | 0.28839 | -0.18311 | -0.15106 | -0.045777 | -0.013733 | -0.050354 | -0.082398 | 0.082397 | 0.091553 | 0.09613 | 0.073242 | 0.14648 | 0.1236 | 0.42572 | 123.8297 | 0.14191 | 123.7747 | 123.8113 | 123.6099 | 123.674 | 123.5596 | -123.7793 | -123.6923 | 123.6923 | 123.7244 | 61.8668 | 61.9446
141.5 | 123.8663 | -61.9629 | 61.702 | 0.020828 | 0.0032449 | 0.069353 | 0.065657 | 0.0015529 | -0.0018756 | -0.0018842 | 0.0048523 | 0.0056545 | 0.070837 | 0.0658 | -0.0020122 | 0.013086 | -0.002147 | -0.1236 | 61.7432 | -62.0865 | 61.7065 | -61.7157 | -62.1277 | -62.1368 | -0.07782 | 61.6425 | -62.0087 | 61.7157 | -61.9125 | -61.9263 | -61.9034 | -0.1236 | 0.041199 | 0.004578 | 0.24719 | -0.17395 | -0.16479 | -0.050354 | -0.041199 | -0.045776 | -0.059509 | 0.013733 | 0.050354 | 0.05951 | 0.036621 | 0.10529 | 0.082397 | 0.37079 | 123.793 | 0.09613 | 123.7244 | 123.8297 | 123.6511 | 123.7061 | 123.6053 | -123.7885 | -123.7106 | 123.6694 | 123.6786 | 61.8393 | 61.8851
143.1719 | 123.7976 | -61.9446 | 61.8164 | 0.0055694 | 0.0032449 | 0.068925 | 0.066084 | 0.0047573 | -0.0035846 | -0.00017515 | -0.0043029 | 0.0054409 | 0.068274 | 0.052128 | -0.0026532 | 0.013514 | -0.003215 | -0.032043 | 61.7935 | -62.0956 | 61.7065 | -61.7065 | -62.1185 | -62.1368 | -0.022888 | 61.7065 | -61.9583 | 61.7386 | -61.9354 | -61.972 | -61.9125 | -0.15106 | -0.022888 | -0.10986 | 0.23804 | -0.19226 | -0.17395 | -0.041199 | -0.022888 | -0.013733 | -0.10986 | -0.07782 | 0.009155 | 0.032043 | -0.027466 | 0.045776 | -0.013733 | 0.3891 | 123.8022 | 0.022888 | 123.6969 | 123.8892 | 123.6649 | 123.7381 | 123.6511 | -123.912 | -123.7747 | 123.6511 | 123.6832 | 61.9125 | 61.9217
144.875 | 123.7976 | -61.9354 | 61.7935 | -0.0020601 | 0.0049539 | 0.069139 | 0.067366 | 0.0045437 | -0.003371 | 0.00025205 | -0.0073547 | 0.0054409 | 0.069556 | 0.062809 | -0.002226 | 0.012873 | -0.0012924 | -0.086975 | 61.8256 | -62.0819 | 61.6608 | -61.7798 | -62.1689 | -62.1964 | -0.1236 | 61.7294 | -61.9858 | 61.6928 | -61.9492 | -61.9766 | -61.8942 | -0.14648 | 0.032044 | -0.13275 | 0.15564 | -0.26093 | -0.23346 | -0.11444 | -0.086975 | -0.050354 | -0.064087 | -0.10071 | -0.013733 | 0.041199 | -0.041199 | 0.091553 | 0.009155 | 0.30212 | 123.7427 | 0.036621 | 123.6786 | 123.9075 | 123.7152 | 123.761 | 123.6649 | -123.8754 | -123.7793 | 123.5962 | 123.6282 | 61.8484 | 61.8118
146.5625 | 123.8297 | -61.9034 | 61.7844 | 0.013199 | 0.0049539 | 0.068925 | 0.06758 | -0.00079686 | -0.0031574 | 0.00025205 | 0.0018005 | 0.0050137 | 0.069983 | 0.061314 | -0.003294 | 0.013941 | -0.003215 | 0 | 61.821 | -62.0636 | 61.7523 | -61.6562 | -62.0773 | -62.1094 | 0.009155 | 61.7111 | -61.9583 | 61.7569 | -61.8713 | -61.908 | -61.8622 | -0.16022 | 0.036621 | -0.032044 | 0.24719 | -0.20599 | -0.17395 | -0.045776 | -0.013733 | -0.054932 | -0.073242 | -0.027466 | 0.032043 | 0.041198 | -0.004578 | 0.09613 | 0.050354 | 0.40741 | 123.8159 | 0.086975 | 123.7152 | 123.8846 | 123.6694 | 123.7244 | 123.6145 | -123.848 | -123.7427 | 123.6557 | 123.6603 | 61.9034 | 61.9125
148.25 | 123.9258 | -61.9537 | 61.6974 | -0.0020601 | 0.0013223 | 0.068071 | 0.065016 | -0.0020787 | -0.0018756 | -0.0012434 | -0.0043029 | 0.0018093 | 0.068701 | 0.065373 | -0.0052166 | 0.013514 | 0.0027664 | -0.064087 | 61.7065 | -62.0636 | 61.7615 | -61.5692 | -62.0316 | -62.0407 | 0.068665 | 61.6196 | -61.9904 | 61.7798 | -61.7981 | -61.8347 | -61.853 | -0.10986 | 0.009155 | 0.064087 | 0.38452 | -0.086975 | -0.07782 | 0.022889 | 0.032044 | -0.036621 | -0.07782 | 0.082397 | 0.15564 | 0.10071 | 0.11902 | 0.13733 | 0.15564 | 0.49439 | 123.8251 | 0.19226 | 123.7701 | 123.7701 | 123.6099 | 123.6603 | 123.5733 | -123.761 | -123.6877 | 123.7152 | 123.7335 | 61.8896 | 62.0224
149.9375 | 123.8754 | -61.9675 | 61.6745 | 0.036087 | 0.0070901 | 0.068071 | 0.067793 | 0.0053983 | -0.0020892 | -0.0010298 | 0.010956 | 0.0041593 | 0.07276 | 0.064732 | -0.002226 | 0.012659 | -0.0006516 | -0.073242 | 61.7477 | -62.0636 | 61.7432 | -61.6379 | -62.0636 | -62.0956 | 0.013733 | 61.6333 | -62.0087 | 61.7386 | -61.8896 | -61.8942 | -61.8896 | -0.096131 | 0.073242 | 0.068664 | 0.32959 | -0.12817 | -0.096131 | -0.032043 | 0 | -0.041199 | -0.041199 | 0.064086 | 0.07782 | 0.07782 | 0.073242 | 0.11902 | 0.11444 | 0.42572 | 123.8068 | 0.11902 | 123.7473 | 123.8113 | 123.642 | 123.7152 | 123.6008 | -123.7381 | -123.6832 | 123.7106 | 123.7061 | 61.8942 | 61.9812
151.6562 | 123.7885 | -61.9171 | 61.7981 | 0.0055694 | 0.0049539 | 0.070848 | 0.068434 | 0.0015529 | -0.0023028 | -0.0027386 | -0.0043029 | 0.0035183 | 0.07041 | 0.05811 | -0.0047894 | 0.011164 | -0.0027878 | -0.064087 | 61.8073 | -62.059 | 61.6608 | -61.7523 | -62.146 | -62.1643 | -0.10071 | 61.7203 | -61.9492 | 61.6791 | -61.94 | -61.9675 | -61.908 | -0.14191 | 0.009155 | -0.13733 | 0.16479 | -0.24719 | -0.22888 | -0.10529 | -0.086975 | -0.032044 | -0.07782 | -0.11902 | -0.022888 | 0.009155 | -0.050354 | 0.041199 | -0.01831 | 0.3067 | 123.7198 | 0.009156 | 123.6282 | 123.8663 | 123.6694 | 123.7244 | 123.6374 | -123.8571 | -123.7473 | 123.5779 | 123.5962 | 61.853 | 61.8164
153.3281 | 123.8159 | -61.9217 | 61.7798 | -0.0020601 | 0.0032449 | 0.071703 | 0.065871 | 0.0071071 | -0.003371 | -0.0018842 | -0.0012513 | 0.0056545 | 0.066779 | 0.05811 | -0.002226 | 0.013514 | 0.0010574 | -0.018311 | 61.8073 | -62.0728 | 61.734 | -61.6699 | -62.0728 | -62.1094 | -0.004578 | 61.7157 | -61.94 | 61.734 | -61.8759 | -61.9171 | -61.853 | -0.15106 | 0.027466 | -0.045776 | 0.25177 | -0.18768 | -0.15106 | -0.036621 | 0 | -0.01831 | -0.064087 | -0.045776 | 0.045776 | 0.068665 | 0.004578 | 0.086975 | 0.022888 | 0.40283 | 123.8068 | 0.064086 | 123.674 | 123.88 | 123.6557 | 123.7289 | 123.6374 | -123.8525 | -123.7198 | 123.6557 | 123.6557 | 61.9034 | 61.9171
155.0156 | 123.8434 | -61.9034 | 61.7661 | 0.013199 | 0.0058083 | 0.070634 | 0.067366 | 0.0064663 | -0.00038018 | 0.0013202 | 0.010956 | 0.0052273 | 0.069128 | 0.063023 | -0.0035076 | 0.012659 | 0.000203 | 0.004578 | 61.8256 | -62.0636 | 61.7294 | -61.647 | -62.0682 | -62.0773 | 0.036621 | 61.734 | -61.9492 | 61.7615 | -61.8164 | -61.8668 | -61.8301 | -0.16022 | 0.05951 | -0.036621 | 0.25635 | -0.17395 | -0.16479 | -0.013733 | -0.004577 | -0.045777 | -0.032043 | -0.004577 | 0.086975 | 0.073242 | 0.036621 | 0.11902 | 0.082398 | 0.41657 | 123.793 | 0.13275 | 123.7106 | 123.8892 | 123.6832 | 123.7289 | 123.6374 | -123.8297 | -123.7152 | 123.6328 | 123.6649 | 61.908 | 61.94
156.6719 | 123.9029 | -61.9492 | 61.6882 | 0.0055694 | 0.0021769 | 0.069353 | 0.064803 | -0.0010105 | -0.0031574 | -0.0010298 | 0.0018005 | 0.0030911 | 0.069983 | 0.071782 | -0.002226 | 0.013514 | 0.0016982 | -0.11444 | 61.7523 | -62.0636 | 61.702 | -61.6653 | -62.0728 | -62.0911 | -0.045776 | 61.6425 | -61.9858 | 61.7432 | -61.8439 | -61.8439 | -61.8393 | -0.11444 | 0.064087 | 0.013733 | 0.28381 | -0.14191 | -0.1236 | -0.027465 | -0.009155 | -0.036621 | -0.045776 | 0.054932 | 0.10529 | 0.10986 | 0.10529 | 0.14648 | 0.14191 | 0.39826 | 123.7656 | 0.14191 | 123.7289 | 123.8159 | 123.6282 | 123.7015 | 123.5916 | -123.7518 | -123.674 | 123.6511 | 123.6923 | 61.8347 | 61.9034
158.3281 | 123.7885 | -61.9217 | 61.7844 | -0.0020601 | 0.0053811 | 0.068071 | 0.06758 | 0.0056119 | -0.003371 | -0.0027386 | -0.0012513 | 0.0048001 | 0.069769 | 0.058323 | -0.0028668 | 0.012232 | -0.003856 | -0.032043 | 61.8073 | -62.0682 | 61.6882 | -61.6974 | -62.1094 | -62.1368 | -0.013733 | 61.7203 | -61.9446 | 61.702 | -61.9125 | -61.9354 | -61.8896 | -0.14648 | 0.022888 | -0.096131 | 0.2243 | -0.21515 | -0.18768 | -0.068665 | -0.041199 | -0.022888 | -0.064087 | -0.082398 | 0.009155 | 0.032044 | -0.013733 | 0.054932 | 0.009155 | 0.37079 | 123.7564 | 0.032043 | 123.6465 | 123.8754 | 123.6649 | 123.7289 | 123.642 | -123.8525 | -123.7289 | 123.6099 | 123.6237 | 61.8896 | 61.908
160 | 123.8617 | -61.9217 | 61.7294 | 0.0055694 | 0.0028177 | 0.068498 | 0.064803 | 0.00027134 | -0.0037982 | 0.00025205 | -0.0043029 | 0.0024503 | 0.066565 | 0.063664 | -0.0039348 | 0.015864 | -0.001506 | -0.027466 | 61.7157 | -62.0636 | 61.7477 | -61.6104 | -62.0178 | -62.059 | 0.036621 | 61.6516 | -61.972 | 61.7615 | -61.8118 | -61.8347 | -61.8256 | -0.14191 | -0.013733 | 0.018311 | 0.31128 | -0.13733 | -0.09613 | 0.004578 | 0.045777 | -0.050354 | -0.07782 | 0.032044 | 0.10986 | 0.09613 | 0.086975 | 0.14648 | 0.13733 | 0.45319 | 123.8113 | 0.16022 | 123.7335 | 123.7793 | 123.6237 | 123.6374 | 123.5733 | -123.793 | -123.7015 | 123.6694 | 123.6832 | 61.8942 | 61.9583
161.6875 | 123.7701 | -61.9354 | 61.7752 | -0.0096891 | 0.0028177 | 0.069566 | 0.067793 | -0.0016513 | -0.001662 | -0.00060235 | 0.0048523 | 0.0069363 | 0.069128 | 0.058537 | -0.0047894 | 0.0133 | -0.0002244 | -0.032043 | 61.8393 | -62.1002 | 61.6699 | -61.7065 | -62.0865 | -62.1002 | -0.045776 | 61.7065 | -61.9995 | 61.6974 | -61.8942 | -61.9125 | -61.8713 | -0.16479 | 0.064086 | -0.10529 | 0.22888 | -0.16479 | -0.15106 | 0 | 0.013733 | -0.064087 | -0.068665 | -0.07782 | 0.041199 | 0.064087 | 0.022888 | 0.12817 | 0.086975 | 0.39368 | 123.7701 | 0.10529 | 123.6969 | 123.9395 | 123.7061 | 123.7747 | 123.642 | -123.8754 | -123.7747 | 123.6053 | 123.6328 | 61.9034 | 61.8896
163.3594 | 123.8983 | -61.9308 | 61.6837 | -0.0020601 | 0.0047403 | 0.071489 | 0.066512 | 0.0028347 | -0.001662 | -0.003166 | -0.0043029 | 0.0035183 | 0.071478 | 0.058964 | 0.00012397 | 0.015436 | -0.0025742 | -0.11444 | 61.7523 | -62.0773 | 61.7065 | -61.6608 | -62.0819 | -62.114 | -0.009155 | 61.6013 | -61.9904 | 61.7752 | -61.8164 | -61.8484 | -61.821 | -0.14648 | 0.068664 | 0.022888 | 0.27008 | -0.18311 | -0.15106 | -0.036621 | -0.004577 | -0.059509 | -0.082398 | 0.091553 | 0.11444 | 0.10986 | 0.082397 | 0.16937 | 0.14191 | 0.41656 | 123.7839 | 0.17395 | 123.7656 | 123.8297 | 123.5916 | 123.6832 | 123.5321 | -123.761 | -123.674 | 123.6374 | 123.7061 | 61.8164 | 61.9217
165.0625 | 123.848 | -61.9217 | 61.7203 | -0.0020601 | 0.0030313 | 0.066362 | 0.06523 | -0.0010105 | -0.0025166 | -0.0012434 | -0.0043029 | 0.0033047 | 0.068274 | 0.0611 | -0.0013714 | 0.0133 | -0.0008652 | -0.036621 | 61.7432 | -62.0682 | 61.7386 | -61.6013 | -62.0178 | -62.0636 | 0.036621 | 61.6241 | -61.9629 | 61.7523 | -61.8073 | -61.8301 | -61.821 | -0.14648 | 0.022888 | 0.01831 | 0.32044 | -0.14191 | -0.09613 | 0.004577 | 0.050354 | -0.041199 | -0.09613 | 0.032043 | 0.11444 | 0.10071 | 0.091553 | 0.14191 | 0.13275 | 0.46692 | 123.8068 | 0.15564 | 123.7152 | 123.8113 | 123.587 | 123.6649 | 123.5458 | -123.7885 | -123.6832 | 123.6603 | 123.674 | 61.8851 | 61.9583
166.7344 | 123.7747 | -61.9263 | 61.7615 | 0.0055694 | 0.0032449 | 0.068285 | 0.066084 | 0.0017667 | -0.0029438 | -0.0029524 | -0.0012513 | 0.0052273 | 0.066138 | 0.054265 | -0.0045758 | 0.012232 | -0.0023606 | -0.07782 | 61.8027 | -62.0453 | 61.6608 | -61.702 | -62.1002 | -62.114 | -0.054932 | 61.7111 | -61.9537 | 61.6699 | -61.9034 | -61.9263 | -61.8896 | -0.11902 | 0.041198 | -0.10071 | 0.22431 | -0.18768 | -0.17395 | -0.068665 | -0.054932 | -0.027465 | -0.050354 | -0.091553 | 0.022889 | 0.036622 | 0 | 0.064087 | 0.027465 | 0.34332 | 123.7061 | 0.050354 | 123.6237 | 123.848 | 123.6649 | 123.7289 | 123.6374 | -123.8068 | -123.7152 | 123.587 | 123.5962 | 61.8484 | 61.8713
168.4062 | 123.8205 | -61.9034 | 61.7798 | 0.013199 | 0.0047403 | 0.069994 | 0.06758 | 0.00091214 | -0.0023028 | -0.0018842 | 0.010956 | 0.0056545 | 0.069983 | 0.0611 | -0.0045758 | 0.012659 | -0.000438 | 0.004578 | 61.8301 | -62.0544 | 61.7203 | -61.6379 | -62.059 | -62.0636 | 0.032043 | 61.7203 | -61.9308 | 61.7661 | -61.821 | -61.8484 | -61.8073 | -0.15106 | 0.050354 | -0.059509 | 0.2655 | -0.16022 | -0.15564 | -0.009156 | -0.004578 | -0.027466 | -0.059509 | -0.013733 | 0.082397 | 0.09613 | 0.054931 | 0.1236 | 0.082397 | 0.41656 | 123.7747 | 0.10986 | 123.6969 | 123.8846 | 123.6511 | 123.7335 | 123.6237 | -123.8342 | -123.7106 | 123.6237 | 123.6694 | 61.908 | 61.9354
170.0938 | 123.8754 | -61.908 | 61.7249 | -0.0020601 | 0.0026041 | 0.070634 | 0.06523 | 5.774e-05 | -0.0023028 | -0.0029524 | -0.0043029 | 0.0020231 | 0.068915 | 0.060246 | -0.0030804 | 0.013514 | -0.0025742 | -0.036621 | 61.6837 | -62.0544 | 61.7569 | -61.6104 | -62.0132 | -62.059 | 0.045776 | 61.6196 | -61.9537 | 61.7615 | -61.7935 | -61.8073 | -61.8164 | -0.14648 | -0.041199 | 0.032043 | 0.29755 | -0.15106 | -0.10529 | -0.004578 | 0.041198 | -0.045776 | -0.10529 | 0.036621 | 0.11444 | 0.091553 | 0.10071 | 0.13733 | 0.14648 | 0.44403 | 123.8113 | 0.16022 | 123.7152 | 123.7381 | 123.5733 | 123.5916 | 123.5275 | -123.7793 | -123.6786 | 123.6649 | 123.6694 | 61.8713 | 61.9537
171.8281 | 123.7656 | -61.94 | 61.7477 | -0.0020601 | 0.0070901 | 0.068712 | 0.068648 | 0.00027134 | -0.0023028 | -0.00060235 | -0.0012513 | 0.0060819 | 0.070624 | 0.057469 | 0.00097837 | 0.012873 | -0.001506 | -0.091553 | 61.8347 | -62.0773 | 61.6287 | -61.7706 | -62.1689 | -62.1826 | -0.10529 | 61.7157 | -61.9583 | 61.6791 | -61.94 | -61.94 | -61.8851 | -0.13733 | 0.086975 | -0.11902 | 0.16937 | -0.24262 | -0.22888 | -0.10529 | -0.091552 | -0.018311 | -0.032044 | -0.068665 | 0 | 0.054931 | 0 | 0.073242 | 0.018311 | 0.3067 | 123.7061 | 0.018311 | 123.6374 | 123.912 | 123.674 | 123.7747 | 123.6557 | -123.8251 | -123.7061 | 123.5687 | 123.6191 | 61.8484 | 61.8347
173.5 | 123.8892 | -61.9125 | 61.7157 | -0.0020601 | 0.0017495 | 0.069353 | 0.063735 | -0.00015586 | -0.008498 | -0.0012434 | -0.0012513 | 0.0035183 | 0.06806 | 0.061528 | -0.0035076 | 0.014155 | -0.000438 | -0.050354 | 61.7065 | -62.0544 | 61.7432 | -61.5829 | -61.9904 | -62.0453 | 0.064087 | 61.6196 | -61.9766 | 61.7569 | -61.7752 | -61.7981 | -61.7981 | -0.14191 | -0.009155 | 0.027466 | 0.32959 | -0.13275 | -0.077819 | 0.009155 | 0.064087 | -0.064087 | -0.09613 | 0.041199 | 0.13733 | 0.11444 | 0.11444 | 0.17853 | 0.17853 | 0.4715 | 123.7976 | 0.20142 | 123.7335 | 123.761 | 123.5962 | 123.6191 | 123.5321 | -123.7701 | -123.6923 | 123.6557 | 123.6694 | 61.8622 | 61.9766
175.1719 | 123.8846 | -61.8942 | 61.6699 | -0.0020601 | 0.0021769 | 0.070634 | 0.065657 | 0.0047573 | -0.0020892 | -0.0018842 | -0.0012513 | 0.0043729 | 0.066565 | 0.054905 | -0.0011578 | 0.014795 | -0.0047104 | -0.068665 | 61.7294 | -62.0407 | 61.7294 | -61.6287 | -62.0636 | -62.0773 | 0 | 61.5967 | -61.9675 | 61.7752 | -61.821 | -61.8439 | -61.7981 | -0.14648 | 0.059509 | 0.059509 | 0.2655 | -0.18311 | -0.16937 | -0.036622 | -0.022889 | -0.073242 | -0.073242 | 0.10529 | 0.073242 | 0.09613 | 0.050354 | 0.16937 | 0.1236 | 0.41199 | 123.7701 | 0.14648 | 123.7427 | 123.7701 | 123.5641 | 123.6237 | 123.4909 | -123.7106 | -123.6374 | 123.6237 | 123.6694 | 61.8256 | 61.8942
176.875 | 123.7518 | -61.94 | 61.7432 | -0.0020601 | 0.0032449 | 0.068285 | 0.065443 | 0.0017667 | -0.003371 | 0.00025205 | 0.0018005 | 0.0048001 | 0.071905 | 0.061955 | -0.0028668 | 0.011591 | 0.0014846 | -0.073242 | 61.7935 | -62.0682 | 61.6287 | -61.7294 | -62.0956 | -62.114 | -0.027466 | 61.7432 | -61.9995 | 61.6608 | -61.8942 | -61.9034 | -61.8759 | -0.12817 | 0.050354 | -0.11444 | 0.21057 | -0.17395 | -0.15564 | -0.045777 | -0.027466 | -0.05951 | 0 | -0.082397 | 0.045776 | 0.064086 | 0.036621 | 0.1236 | 0.096131 | 0.33875 | 123.6969 | 0.10529 | 123.6603 | 123.8617 | 123.7427 | 123.7335 | 123.6832 | -123.8113 | -123.7427 | 123.5687 | 123.6008 | 61.8668 | 61.9125
178.5469 | 123.8251 | -61.9263 | 61.6928 | 0.020828 | 0.0023905 | 0.069139 | 0.065016 | 0.0015529 | -0.0025166 | -0.002525 | 0.0018005 | 0.0050137 | 0.070837 | 0.06815 | -0.0030804 | 0.016291 | -0.0034286 | -0.1236 | 61.734 | -62.0819 | 61.6608 | -61.6791 | -62.0911 | -62.1094 | -0.07782 | 61.6196 | -61.9995 | 61.6837 | -61.8759 | -61.8805 | -61.8484 | -0.15564 | 0.041199 | -0.032043 | 0.24719 | -0.1831 | -0.16479 | -0.027466 | -0.009155 | -0.073242 | -0.073242 | -0.009155 | 0.050354 | 0.07782 | 0.045777 | 0.15106 | 0.11902 | 0.40283 | 123.7427 | 0.1236 | 123.6832 | 123.8159 | 123.6191 | 123.6603 | 123.5458 | -123.7747 | -123.6923 | 123.587 | 123.6099 | 61.8027 | 61.8484
180.2188 | 123.7289 | -61.8896 | 61.7798 | -0.0020601 | 0.0070901 | 0.068498 | 0.065016 | 0.00091214 | -0.0014484 | -0.0020978 | -0.0012513 | 0.0069363 | 0.07041 | 0.057682 | -8.9634e-05 | 0.012659 | -0.003215 | -0.041199 | 61.7889 | -62.0544 | 61.6745 | -61.7065 | -62.1185 | -62.1414 | -0.068665 | 61.702 | -61.9583 | 61.6699 | -61.908 | -61.9446 | -61.8622 | -0.16479 | 0.009155 | -0.10528 | 0.1831 | -0.25177 | -0.22888 | -0.086975 | -0.064087 | -0.068665 | -0.07782 | -0.10986 | -0.018311 | 0.027465 | -0.054932 | 0.09613 | 0.013733 | 0.3479 | 123.7289 | 0.050354 | 123.6282 | 123.8434 | 123.6603 | 123.6786 | 123.5916 | -123.8342 | -123.7381 | 123.5641 | 123.5596 | 61.8484 | 61.821
181.9062 | 123.7381 | -61.9354 | 61.7706 | -0.0020601 | 0.0011087 | 0.067857 | 0.066725 | 0.00048494 | -0.0018756 | -0.001457 | -0.0043029 | 0.0039457 | 0.070624 | 0.062169 | -0.0058576 | 0.011591 | 0.0040482 | -0.068665 | 61.8118 | -62.0682 | 61.6333 | -61.7157 | -62.0819 | -62.1002 | -0.054932 | 61.6928 | -61.9446 | 61.6562 | -61.8851 | -61.9125 | -61.8668 | -0.13275 | 0.041199 | -0.13733 | 0.21973 | -0.16479 | -0.14648 | -0.032044 | -0.013733 | -0.009155 | -0.07782 | -0.11444 | 0.050354 | 0.068665 | 0.022888 | 0.07782 | 0.032043 | 0.35248 | 123.7015 | 0.059509 | 123.6008 | 123.88 | 123.6374 | 123.7473 | 123.6282 | -123.8388 | -123.7152 | 123.5687 | 123.5916 | 61.8668 | 61.8805
183.5781 | 123.7518 | -61.9171 | 61.7752 | -0.0020601 | 0.0060221 | 0.069353 | 0.066512 | 0.00027134 | -0.0037982 | -0.001457 | -0.0012513 | 0.0048001 | 0.069769 | 0.058964 | -0.0028668 | 0.013086 | -0.0036422 | -0.041199 | 61.7889 | -62.0407 | 61.6608 | -61.702 | -62.1048 | -62.1323 | -0.073242 | 61.6974 | -61.9308 | 61.6745 | -61.8942 | -61.9217 | -61.8668 | -0.1236 | 0.013732 | -0.11444 | 0.21515 | -0.21515 | -0.18768 | -0.091553 | -0.064087 | -0.013733 | -0.07782 | -0.10071 | 0.022888 | 0.050354 | -0.004578 | 0.064087 | 0.009155 | 0.33874 | 123.7015 | 0.036621 | 123.6053 | 123.8296 | 123.6282 | 123.7061 | 123.6145 | -123.8159 | -123.7061 | 123.5779 | 123.5916 | 61.8759 | 61.8439
185.25 | 123.8434 | -61.908 | 61.7157 | -0.0020601 | 0.0038857 | 0.068071 | 0.064162 | -0.0025059 | -0.0042254 | -0.00081595 | -0.0043029 | 0.0052273 | 0.068915 | 0.065159 | -0.0039348 | 0.013514 | -1.0598e-05 | -0.036621 | 61.6928 | -62.0682 | 61.7477 | -61.5875 | -61.9858 | -62.0316 | 0.041199 | 61.615 | -61.9446 | 61.7477 | -61.7615 | -61.7981 | -61.7752 | -0.16022 | -0.022888 | 0.032044 | 0.32043 | -0.1236 | -0.07782 | 0.036621 | 0.082397 | -0.036621 | -0.10071 | 0.032044 | 0.14648 | 0.13275 | 0.10986 | 0.16937 | 0.14648 | 0.48065 | 123.8159 | 0.18311 | 123.6923 | 123.761 | 123.5596 | 123.6008 | 123.5229 | -123.7839 | -123.6603 | 123.6557 | 123.6557 | 61.8713 | 61.9492
186.9375 | 123.8159 | -61.9308 | 61.6837 | 0.028458 | 0.0060221 | 0.070421 | 0.065871 | -0.00079686 | -0.0012348 | -0.0029524 | 0.014008 | 0.0054409 | 0.068915 | 0.064732 | 0.00012397 | 0.014155 | 0.0023392 | -0.11444 | 61.7203 | -62.0773 | 61.6791 | -61.6425 | -62.0728 | -62.0773 | -0.036621 | 61.6104 | -61.9949 | 61.6837 | -61.8668 | -61.8622 | -61.8484 | -0.14648 | 0.036621 | -0.004578 | 0.28839 | -0.14648 | -0.14191 | 0 | 0.004578 | -0.064087 | -0.073242 | 0 | 0.064087 | 0.082397 | 0.068664 | 0.14648 | 0.13275 | 0.43488 | 123.7564 | 0.12817 | 123.6786 | 123.7976 | 123.6053 | 123.6511 | 123.5413 | -123.761 | -123.6786 | 123.6099 | 123.6145 | 61.8164 | 61.8942
188.6094 | 123.7701 | -61.8851 | 61.7523 | 0.020828 | 0.0062357 | 0.070848 | 0.066512 | 0.0028347 | -0.0012348 | 3.8448e-05 | 0.0079041 | 0.0048001 | 0.070196 | 0.061955 | -0.0020122 | 0.012659 | -0.0044968 | 0 | 61.8301 | -62.0453 | 61.7294 | -61.6196 | -62.027 | -62.0636 | 0.036621 | 61.7111 | -61.94 | 61.7157 | -61.8256 | -61.8484 | -61.7981 | -0.16022 | 0.07782 | -0.022888 | 0.2655 | -0.17853 | -0.14191 | -0.018311 | 0.01831 | -0.054931 | -0.041198 | -0.036621 | 0.059509 | 0.086975 | 0.036621 | 0.14191 | 0.091552 | 0.42572 | 123.7747 | 0.11444 | 123.6557 | 123.8754 | 123.6511 | 123.7152 | 123.5962 | -123.7976 | -123.6923 | 123.6145 | 123.6008 | 61.8851 | 61.9217
190.2969 | 123.8709 | -61.9263 | 61.6699 | -0.0020601 | 0.0023905 | 0.067217 | 0.064803 | 0.00027134 | -0.0042254 | -0.003166 | -0.0073547 | 0.0037319 | 0.067847 | 0.06345 | 0.00012397 | 0.014368 | 0.001912 | -0.10071 | 61.6974 | -62.0544 | 61.7065 | -61.615 | -61.9995 | -62.0453 | 0.018311 | 61.6196 | -61.9766 | 61.7386 | -61.7752 | -61.8073 | -61.7981 | -0.12817 | 0.027466 | 0.036621 | 0.31128 | -0.11902 | -0.073242 | 0.009155 | 0.054931 | -0.050354 | -0.050354 | 0.068664 | 0.15106 | 0.12817 | 0.11902 | 0.17853 | 0.16937 | 0.43945 | 123.761 | 0.20142 | 123.7152 | 123.7518 | 123.5962 | 123.6237 | 123.5458 | -123.7244 | -123.6465 | 123.6328 | 123.6649 | 61.8256 | 61.9446
191.9844 | 123.8571 | -61.9217 | 61.6699 | -0.0020601 | 0.0034585 | 0.068285 | 0.064162 | 0.00027134 | 0.0015424 | -0.0033796 | 0.0018005 | 0.0041593 | 0.069769 | 0.058964 | -0.0013714 | 0.015009 | -0.0002244 | -0.091553 | 61.6837 | -62.0682 | 61.6791 | -61.6379 | -62.0316 | -62.0499 | 0.004578 | 61.6196 | -61.9537 | 61.7203 | -61.8073 | -61.8027 | -61.7935 | -0.14648 | 0.013733 | 0.009155 | 0.28381 | -0.12817 | -0.10986 | 0.01831 | 0.036621 | -0.032043 | -0.050354 | 0.050354 | 0.11444 | 0.12817 | 0.11902 | 0.16022 | 0.15106 | 0.4303 | 123.7473 | 0.14648 | 123.674 | 123.7518 | 123.5733 | 123.6053 | 123.5413 | -123.7381 | -123.6237 | 123.6008 | 123.642 | 61.8301 | 61.9263
193.7031 | 123.8754 | -61.8896 | 61.6882 | -0.0096891 | 0.0013223 | 0.068071 | 0.064162 | -0.0033603 | -0.0023028 | -0.00060235 | -0.0012513 | 0.0056545 | 0.069128 | 0.069432 | -0.0047894 | 0.016291 | -0.0027878 | -0.036621 | 61.6837 | -62.0499 | 61.7386 | -61.5738 | -61.9812 | -62.0224 | 0.068665 | 61.5921 | -61.9217 | 61.7249 | -61.7615 | -61.7889 | -61.7889 | -0.16022 | -0.004577 | 0.050354 | 0.31586 | -0.13275 | -0.091553 | 0.027466 | 0.068665 | -0.032044 | -0.09613 | 0.036622 | 0.12817 | 0.10071 | 0.10071 | 0.13275 | 0.13275 | 0.47607 | 123.7885 | 0.16022 | 123.6465 | 123.7335 | 123.5138 | 123.5733 | 123.4818 | -123.7381 | -123.6099 | 123.6282 | 123.6145 | 61.853 | 61.9583
195.375 | 123.7335 | -61.9308 | 61.7477 | -0.0020601 | 0.0019631 | 0.070207 | 0.066298 | -0.0025059 | -0.0031574 | -0.0016706 | -0.0012513 | 0.0065091 | 0.068701 | 0.059605 | -0.001585 | 0.0133 | -0.0010788 | -0.086975 | 61.7752 | -62.0499 | 61.6287 | -61.7523 | -62.1368 | -62.1368 | -0.14191 | 61.6928 | -61.9583 | 61.6425 | -61.9125 | -61.94 | -61.853 | -0.11902 | 0.027466 | -0.11902 | 0.17853 | -0.20599 | -0.20599 | -0.086975 | -0.086975 | -0.027466 | -0.054932 | -0.10529 | 0.01831 | 0.07782 | -0.009155 | 0.10529 | 0.018311 | 0.29755 | 123.6786 | 0.045776 | 123.6008 | 123.8251 | 123.6511 | 123.7061 | 123.6237 | -123.7976 | -123.7061 | 123.5596 | 123.5733 | 61.8439 | 61.7889
197.1875 | 123.8709 | -61.9171 | 61.6608 | -0.0020601 | 0.0013223 | 0.070634 | 0.063948 | 0.0013393 | -0.0014484 | -0.00081595 | -0.0043029 | 0.0037319 | 0.06806 | 0.063878 | -0.0020122 | 0.014368 | -0.0017196 | -0.07782 | 61.6882 | -62.059 | 61.7065 | -61.6013 | -62.0041 | -62.0224 | 0.027466 | 61.6058 | -61.9492 | 61.7294 | -61.7844 | -61.7935 | -61.7844 | -0.14191 | 0.027465 | 0.045776 | 0.31586 | -0.10529 | -0.086975 | 0.036621 | 0.054932 | -0.032044 | -0.054932 | 0.068664 | 0.13275 | 0.13275 | 0.1236 | 0.16479 | 0.15564 | 0.45776 | 123.7656 | 0.16479 | 123.6786 | 123.7473 | 123.555 | 123.6053 | 123.5229 | -123.7198 | -123.6099 | 123.6237 | 123.6465 | 61.8393 | 61.9446
198.9375 | 123.7656 | -61.8851 | 61.7844 | 0.028458 | 0.0055947 | 0.068071 | 0.067152 | 0.0015529 | -0.0020892 | -0.00060235 | 0.0079041 | 0.0071499 | 0.070196 | 0.061741 | -0.0028668 | 0.012446 | -0.0047104 | -0.009155 | 61.8118 | -62.0636 | 61.6745 | -61.6791 | -62.0499 | -62.0682 | -0.013733 | 61.7249 | -61.9354 | 61.6745 | -61.8256 | -61.853 | -61.8164 | -0.17853 | 0.027466 | -0.10986 | 0.20599 | -0.1831 | -0.16479 | -0.004577 | 0.013733 | -0.050354 | -0.059509 | -0.10986 | 0.059509 | 0.068665 | 0.032044 | 0.11902 | 0.082398 | 0.38452 | 123.7381 | 0.10986 | 123.6099 | 123.8754 | 123.6603 | 123.6969 | 123.6099 | -123.848 | -123.7198 | 123.5596 | 123.5596 | 61.8759 | 61.8713
200.7031 | 123.7198 | -61.908 | 61.7477 | -0.0096891 | 0.0073037 | 0.067217 | 0.068007 | 0.0019803 | -0.0027302 | -0.0010298 | -0.0012513 | 0.0045865 | 0.069128 | 0.054478 | -0.0011578 | 0.014155 | -0.0036422 | -0.054932 | 61.8027 | -62.0224 | 61.6333 | -61.7203 | -62.1277 | -62.1368 | -0.091553 | 61.6653 | -61.9446 | 61.6287 | -61.8942 | -61.9263 | -61.8439 | -0.11444 | 0.054931 | -0.11444 | 0.18768 | -0.22888 | -0.21973 | -0.11444 | -0.10529 | -0.036621 | -0.082398 | -0.11902 | 0.013733 | 0.064087 | -0.018311 | 0.10071 | 0.01831 | 0.30212 | 123.6557 | 0.050354 | 123.5733 | 123.8251 | 123.6099 | 123.7106 | 123.5733 | -123.7701 | -123.6923 | 123.5413 | 123.5367 | 61.853 | 61.8164
202.4062 | 123.7564 | -61.8896 | 61.7294 | 0.013199 | 0.0043131 | 0.070634 | 0.065016 | -0.0014377 | 0.00068782 | -0.0046614 | -0.0012513 | 0.0058683 | 0.069128 | 0.060887 | -0.0045758 | 0.013941 | -0.000438 | 0.009155 | 61.8027 | -62.0087 | 61.7157 | -61.6196 | -62.0316 | -62.0819 | 0 | 61.6791 | -61.9217 | 61.6608 | -61.8256 | -61.8713 | -61.8164 | -0.11902 | 0.073242 | -0.013733 | 0.27008 | -0.19226 | -0.14191 | -0.073242 | -0.022888 | -0.032044 | -0.050354 | -0.068664 | 0.064086 | 0.073242 | 0.01831 | 0.10529 | 0.050354 | 0.3891 | 123.7244 | 0.09613 | 123.5825 | 123.8113 | 123.6008 | 123.6923 | 123.5687 | -123.7381 | -123.6511 | 123.6053 | 123.5504 | 61.8988 | 61.8896
204.1562 | 123.7244 | -61.9263 | 61.7523 | 0.0055694 | 0.0043131 | 0.070848 | 0.06523 | 0.00091214 | -0.001662 | 0.001961 | -0.0012513 | 0.0052273 | 0.069983 | 0.055973 | -0.001585 | 0.013941 | -0.001506 | -0.09613 | 61.7844 | -62.0361 | 61.6013 | -61.7432 | -62.1414 | -62.146 | -0.1236 | 61.6974 | -61.9446 | 61.6058 | -61.9034 | -61.9308 | -61.8393 | -0.10986 | 0.032044 | -0.15106 | 0.18311 | -0.21973 | -0.21515 | -0.10986 | -0.10529 | -0.01831 | -0.054931 | -0.14648 | 0.022889 | 0.086976 | -0.004577 | 0.10529 | 0.013733 | 0.29297 | 123.6374 | 0.041199 | 123.5504 | 123.8205 | 123.642 | 123.7106 | 123.6237 | -123.7885 | -123.6969 | 123.5275 | 123.5321 | 61.8301 | 61.8027
205.9062 | 123.8205 | -61.8942 | 61.702 | -0.017319 | 0.0034585 | 0.068071 | 0.063094 | 0.0017667 | -0.0046528 | 0.0013202 | 0.0048523 | 0.0035183 | 0.068701 | 0.06046 | -0.0045758 | 0.0133 | -0.0002244 | -0.022888 | 61.7111 | -62.0407 | 61.7157 | -61.5646 | -61.9949 | -62.0178 | 0.054932 | 61.5921 | -61.9171 | 61.6699 | -61.7569 | -61.7844 | -61.7844 | -0.14648 | 0.009156 | 0.013733 | 0.32959 | -0.1236 | -0.10071 | 0.022888 | 0.045776 | -0.022888 | -0.10986 | -0.032043 | 0.13733 | 0.10986 | 0.10986 | 0.13275 | 0.13275 | 0.47607 | 123.7564 | 0.16022 | 123.587 | 123.7518 | 123.5092 | 123.6053 | 123.4863 | -123.7427 | -123.6191 | 123.6099 | 123.5641 | 61.8713 | 61.9492
207.5938 | 123.7473 | -61.9034 | 61.7477 | 0.0055694 | 0.0064493 | 0.068925 | 0.067366 | 0.00091214 | -0.0010212 | -0.0020978 | 0.0018005 | 0.0080045 | 0.071051 | 0.065159 | -0.0011578 | 0.011377 | -0.0010788 | 0 | 61.7935 | -62.0407 | 61.6745 | -61.615 | -62.027 | -62.0773 | 0.009155 | 61.6699 | -61.9217 | 61.6287 | -61.8484 | -61.8668 | -61.8164 | -0.13733 | 0.045776 | -0.073242 | 0.28839 | -0.17395 | -0.1236 | -0.036622 | 0.013732 | -0.018311 | -0.07782 | -0.11902 | 0.054931 | 0.086975 | 0.036621 | 0.10529 | 0.054932 | 0.42572 | 123.7152 | 0.073242 | 123.5504 | 123.8342 | 123.5916 | 123.6969 | 123.5733 | -123.7885 | -123.6694 | 123.5779 | 123.5321 | 61.9034 | 61.9125
209.3281 | 123.7381 | -61.8851 | 61.7661 | 0.036087 | 0.0036721 | 0.069353 | 0.066298 | -0.00079686 | -0.00080758 | 0.001961 | 0.0079041 | 0.0060819 | 0.072974 | 0.056401 | -0.0056438 | 0.013941 | -0.0023606 | -0.032043 | 61.821 | -62.0728 | 61.6379 | -61.6928 | -62.0316 | -62.0773 | -0.032043 | 61.702 | -61.9675 | 61.5921 | -61.853 | -61.8759 | -61.8164 | -0.18768 | 0.054932 | -0.12817 | 0.19226 | -0.19226 | -0.14648 | -0.004578 | 0.041199 | -0.082397 | -0.064087 | -0.17395 | 0.032044 | 0.068665 | 0.009155 | 0.15106 | 0.091552 | 0.37994 | 123.7106 | 0.11444 | 123.5596 | 123.8937 | 123.6694 | 123.7061 | 123.587 | -123.8388 | -123.7335 | 123.5229 | 123.4772 | 61.853 | 61.853
211.0156 | 123.8434 | -61.8668 | 61.6837 | -0.017319 | 0.0030313 | 0.069353 | 0.064162 | 0.0019803 | -0.0029438 | -0.00081595 | -0.0012513 | 0.0041593 | 0.069556 | 0.060887 | -0.002226 | 0.015009 | -0.0036422 | -0.041199 | 61.6745 | -62.0132 | 61.7157 | -61.5463 | -61.9675 | -62.027 | 0.059509 | 61.6058 | -61.9217 | 61.6699 | -61.7432 | -61.7844 | -61.7706 | -0.14648 | -0.009155 | 0.032043 | 0.32043 | -0.16022 | -0.10071 | -0.013733 | 0.045777 | -0.054932 | -0.07782 | -0.013733 | 0.1236 | 0.09613 | 0.082397 | 0.15106 | 0.13733 | 0.46692 | 123.7289 | 0.17853 | 123.5916 | 123.6877 | 123.5275 | 123.5413 | 123.4726 | -123.6969 | -123.6053 | 123.5825 | 123.5367 | 61.8256 | 61.9263
212.7656 | 123.7152 | -61.9217 | 61.7157 | 0.0055694 | 0.0051675 | 0.068071 | 0.065871 | 0.0017667 | -0.0027302 | -0.00038875 | -0.0012513 | 0.0056545 | 0.069983 | 0.064305 | -0.00030343 | 0.014155 | -0.0010788 | -0.10986 | 61.7935 | -62.0087 | 61.6058 | -61.7294 | -62.1094 | -62.1414 | -0.11444 | 61.6653 | -61.9354 | 61.5921 | -61.8942 | -61.9217 | -61.8622 | -0.086975 | 0.07782 | -0.10986 | 0.19226 | -0.21973 | -0.18768 | -0.13275 | -0.10071 | -0.013733 | -0.050354 | -0.1236 | 0.027466 | 0.059509 | 0 | 0.073242 | 0.013733 | 0.27924 | 123.6145 | 0.041199 | 123.5275 | 123.8022 | 123.6008 | 123.7152 | 123.587 | -123.7244 | -123.6511 | 123.5275 | 123.5138 | 61.8118 | 61.8073
214.5156 | 123.8342 | -61.908 | 61.6745 | 0.0055694 | 0.0015359 | 0.069139 | 0.063948 | 0.00069854 | -0.0044392 | -0.0012434 | -0.0012513 | 0.0045865 | 0.068488 | 0.066441 | -0.001585 | 0.01565 | -0.001506 | -0.036621 | 61.6791 | -62.0544 | 61.7203 | -61.5738 | -61.9675 | -62.0178 | 0.045776 | 61.5967 | -61.908 | 61.6882 | -61.7386 | -61.7752 | -61.7661 | -0.14648 | 0.004577 | 0.045776 | 0.33417 | -0.10986 | -0.059509 | 0.036621 | 0.086975 | 0 | -0.07782 | 0.013732 | 0.16937 | 0.14191 | 0.13275 | 0.14191 | 0.13275 | 0.48065 | 123.7747 | 0.16937 | 123.5962 | 123.7335 | 123.5046 | 123.587 | 123.5046 | -123.7289 | -123.5825 | 123.6282 | 123.5962 | 61.8713 | 61.9537
216.25 | 123.7976 | -61.9308 | 61.6425 | 0.036087 | 0.0060221 | 0.069139 | 0.066298 | 0.00069854 | -0.00016658 | -0.00038875 | 0.023163 | 0.0045865 | 0.07041 | 0.064305 | -0.00030343 | 0.015223 | 0.000203 | -0.064087 | 61.6928 | -62.0453 | 61.7111 | -61.5646 | -62.0132 | -62.0499 | 0.004578 | 61.5921 | -61.9583 | 61.6653 | -61.8256 | -61.8484 | -61.821 | -0.11444 | 0.050354 | 0.068665 | 0.36621 | -0.11902 | -0.082398 | -0.004578 | 0.032043 | -0.027466 | -0.050354 | 0.022888 | 0.10529 | 0.10986 | 0.082397 | 0.13733 | 0.10986 | 0.48065 | 123.7564 | 0.13275 | 123.6237 | 123.7381 | 123.5504 | 123.6237 | 123.5229 | -123.6877 | -123.6008 | 123.642 | 123.5962 | 61.8668 | 61.9354
218 | 123.8251 | -61.8942 | 61.6379 | 0.066604 | 0.0053811 | 0.072343 | 0.069075 | 0.0036893 | 4.7018e-05 | 0.0011066 | 0.014008 | 0.0062955 | 0.071051 | 0.064518 | -0.00073063 | 0.015436 | -1.0598e-05 | -0.054932 | 61.7249 | -62.0499 | 61.7386 | -61.5555 | -61.9949 | -62.0132 | 0.027466 | 61.5921 | -61.9492 | 61.6699 | -61.8027 | -61.8073 | -61.7844 | -0.15564 | 0.086976 | 0.10071 | 0.33875 | -0.11902 | -0.10071 | 0.036621 | 0.054932 | -0.054932 | -0.045776 | 0.032044 | 0.091553 | 0.10986 | 0.086975 | 0.16479 | 0.14191 | 0.49439 | 123.7885 | 0.14648 | 123.6191 | 123.7747 | 123.5413 | 123.6191 | 123.4863 | -123.6877 | -123.587 | 123.6328 | 123.5641 | 61.8393 | 61.9217
219.6875 | 123.7152 | -61.8896 | 61.734 | 0.058975 | 0.0026041 | 0.069566 | 0.067152 | -0.00079686 | -0.00080758 | 0.0028154 | 0.010956 | 0.0052273 | 0.070837 | 0.061741 | -0.0041486 | 0.014582 | -0.000438 | -0.036621 | 61.8027 | -62.0819 | 61.6379 | -61.6745 | -62.0407 | -62.0819 | -0.041199 | 61.6791 | -61.9583 | 61.5967 | -61.8347 | -61.8851 | -61.821 | -0.19226 | 0.068664 | -0.096131 | 0.21515 | -0.19226 | -0.15106 | 0 | 0.041199 | -0.068665 | -0.054932 | -0.13733 | 0.054931 | 0.068664 | 0.004577 | 0.13733 | 0.073242 | 0.40741 | 123.7198 | 0.1236 | 123.555 | 123.8846 | 123.6374 | 123.6923 | 123.5687 | -123.8159 | -123.6923 | 123.5275 | 123.4863 | 61.853 | 61.8484
221.4375 | 123.7015 | -61.8851 | 61.734 | -0.0020601 | 0.0026041 | 0.06743 | 0.063735 | 0.0041165 | -0.0027302 | -0.0012434 | -0.0012513 | 0.0058683 | 0.071265 | 0.058537 | -0.0075664 | 0.012446 | -0.0036422 | -0.054932 | 61.7523 | -62.0316 | 61.6333 | -61.6516 | -62.0453 | -62.0728 | -0.054932 | 61.6745 | -61.9492 | 61.5829 | -61.853 | -61.8713 | -61.8439 | -0.14648 | 0.01831 | -0.10071 | 0.23346 | -0.18768 | -0.16022 | -0.041199 | -0.013733 | -0.064087 | -0.059509 | -0.15106 | 0.032044 | 0.041199 | 0.013733 | 0.10529 | 0.07782 | 0.37994 | 123.6649 | 0.096131 | 123.5321 | 123.7839 | 123.6237 | 123.6374 | 123.5596 | -123.7656 | -123.6832 | 123.5184 | 123.468 | 61.8301 | 61.8301
223.125 | 123.7381 | -61.9125 | 61.6653 | -0.0020601 | 0.0036721 | 0.070421 | 0.065657 | -0.0031467 | -0.0025166 | -0.001457 | -0.0012513 | 0.0037319 | 0.069128 | 0.067723 | 0.00012397 | 0.012018 | -0.0002244 | -0.11902 | 61.7706 | -62.0499 | 61.5967 | -61.6928 | -62.1002 | -62.1323 | -0.10071 | 61.6425 | -61.9308 | 61.615 | -61.8713 | -61.8851 | -61.8256 | -0.13733 | 0.10529 | -0.068664 | 0.21973 | -0.21973 | -0.18768 | -0.082397 | -0.050354 | -0.01831 | -0.022888 | -0.050354 | 0.041199 | 0.086975 | 0.027466 | 0.10529 | 0.045776 | 0.35706 | 123.6465 | 0.059509 | 123.5458 | 123.8205 | 123.5733 | 123.6832 | 123.555 | -123.7152 | -123.5962 | 123.5092 | 123.5275 | 61.7935 | 61.8118
224.8906 | 123.7747 | -61.9125 | 61.6516 | 0.013199 | 0.0032449 | 0.069566 | 0.065657 | -0.0027195 | -0.00016658 | -0.00017515 | 0.0048523 | 0.0026639 | 0.069556 | 0.060673 | -0.0024396 | 0.014155 | -0.0019332 | -0.1236 | 61.7111 | -62.0453 | 61.6058 | -61.6562 | -62.059 | -62.0819 | -0.091553 | 61.5967 | -61.9766 | 61.6058 | -61.8576 | -61.8668 | -61.8301 | -0.13275 | 0.05951 | -0.045776 | 0.25635 | -0.16937 | -0.14648 | -0.036621 | -0.013733 | -0.064087 | -0.054931 | -0.045776 | 0.054932 | 0.082398 | 0.045777 | 0.14648 | 0.10986 | 0.3891 | 123.6511 | 0.11902 | 123.5825 | 123.7564 | 123.5733 | 123.6237 | 123.5092 | -123.6969 | -123.6282 | 123.5184 | 123.5184 | 61.7889 | 61.821
226.5625 | 123.7381 | -61.8576 | 61.734 | 0.043716 | 0.0064493 | 0.06978 | 0.067366 | 0.0041165 | -0.0012348 | 3.8448e-05 | 0.017059 | 0.0065091 | 0.07041 | 0.060032 | -0.0043622 | 0.0133 | -0.0012924 | -0.013733 | 61.7889 | -62.0407 | 61.6745 | -61.6241 | -61.9812 | -62.0224 | 0 | 61.7065 | -61.8988 | 61.6241 | -61.8118 | -61.8484 | -61.7981 | -0.1831 | 0.054931 | -0.059509 | 0.23346 | -0.16479 | -0.1236 | 0.01831 | 0.059509 | -0.041199 | -0.027466 | -0.10986 | 0.045776 | 0.059509 | 0.009155 | 0.10071 | 0.050354 | 0.41656 | 123.7152 | 0.086975 | 123.523 | 123.8296 | 123.6053 | 123.6465 | 123.5641 | -123.7747 | -123.6328 | 123.5321 | 123.4818 | 61.8439 | 61.8576
228.2969 | 123.7473 | -61.9034 | 61.7065 | -0.0020601 | 0.0055947 | 0.067857 | 0.066725 | 0.00027134 | -0.003371 | -0.00060235 | 0.0018005 | 0.0067227 | 0.071051 | 0.058537 | -0.00051703 | 0.0133 | -0.0017196 | -0.1236 | 61.7523 | -62.0361 | 61.5967 | -61.702 | -62.114 | -62.114 | -0.10071 | 61.647 | -61.9354 | 61.6058 | -61.8622 | -61.8896 | -61.8073 | -0.13275 | 0.045776 | -0.10986 | 0.20142 | -0.21057 | -0.21057 | -0.07782 | -0.07782 | -0.032044 | -0.059509 | -0.10071 | 0.041198 | 0.09613 | 0.013733 | 0.12817 | 0.045777 | 0.33417 | 123.6328 | 0.073242 | 123.5413 | 123.7885 | 123.5825 | 123.6557 | 123.5504 | -123.7427 | -123.642 | 123.5001 | 123.5092 | 61.7798 | 61.8027
230 | 123.7564 | -61.8759 | 61.7157 | -0.0020601 | 0.0060221 | 0.068712 | 0.063307 | 0.0032619 | -0.0025166 | -0.0018842 | -0.0043029 | 0.0037319 | 0.067419 | 0.063664 | -0.0041486 | 0.014368 | -0.0002244 | -0.032043 | 61.6882 | -62.0178 | 61.7111 | -61.5738 | -61.9766 | -62.0132 | 0.018311 | 61.6196 | -61.9171 | 61.6287 | -61.7844 | -61.8073 | -61.7844 | -0.14191 | -0.027466 | -0.004577 | 0.30212 | -0.13733 | -0.10071 | 0.004577 | 0.041198 | -0.041198 | -0.09613 | -0.086975 | 0.091553 | 0.091553 | 0.068665 | 0.13275 | 0.10986 | 0.44403 | 123.7289 | 0.13275 | 123.5458 | 123.7061 | 123.5367 | 123.5641 | 123.4955 | -123.7335 | -123.6328 | 123.587 | 123.5046 | 61.8439 | 61.8942
231.75 | 123.8205 | -61.8668 | 61.6425 | -0.0020601 | 0.0028177 | 0.068285 | 0.064162 | -0.0044285 | -0.0048664 | 0.0026018 | -0.0043029 | 0.0048001 | 0.069128 | 0.064518 | -8.9634e-05 | 0.016291 | -0.0017196 | -0.09613 | 61.6882 | -62.0316 | 61.6653 | -61.615 | -62.0132 | -62.027 | -0.018311 | 61.5784 | -61.9675 | 61.6699 | -61.7523 | -61.7752 | -61.7615 | -0.16479 | 0.045776 | 0.022888 | 0.25177 | -0.16022 | -0.14648 | 0.004577 | 0.01831 | -0.10071 | -0.064087 | 0.027466 | 0.11444 | 0.10529 | 0.091552 | 0.20599 | 0.19226 | 0.41656 | 123.6969 | 0.21515 | 123.6374 | 123.7198 | 123.5458 | 123.555 | 123.4451 | -123.674 | -123.6099 | 123.5321 | 123.5367 | 61.7706 | 61.8484
233.4375 | 123.761 | -61.8942 | 61.6562 | 0.043716 | 0.0034585 | 0.067857 | 0.066298 | 0.0030483 | -0.00059378 | 0.00089285 | 0.0079041 | 0.0052273 | 0.070624 | 0.062596 | -0.001585 | 0.0133 | 0.001912 | -0.10986 | 61.6745 | -62.027 | 61.6653 | -61.6058 | -62.0453 | -62.0361 | -0.045776 | 61.5921 | -61.9537 | 61.6058 | -61.8301 | -61.8576 | -61.8073 | -0.13275 | 0.018311 | 0.009155 | 0.28839 | -0.14191 | -0.15106 | -0.009155 | -0.01831 | -0.059509 | -0.064087 | -0.050354 | 0.064087 | 0.086975 | 0.036621 | 0.14648 | 0.09613 | 0.42114 | 123.6923 | 0.1236 | 123.5596 | 123.7015 | 123.5458 | 123.5687 | 123.4863 | -123.6832 | -123.6099 | 123.5596 | 123.5001 | 61.7844 | 61.8485
235.1094 | 123.7335 | -61.8622 | 61.7477 | 0.036087 | 0.0079447 | 0.070207 | 0.066512 | 0.0019803 | -0.0029438 | -0.0018842 | 0.020111 | 0.0080045 | 0.069342 | 0.056401 | -0.0024396 | 0.014582 | -0.0012924 | -0.027466 | 61.7661 | -62.0361 | 61.6562 | -61.6516 | -62.0132 | -62.0407 | -0.013733 | 61.7294 | -61.908 | 61.6196 | -61.8118 | -61.8347 | -61.7752 | -0.17395 | 0.01831 | -0.091553 | 0.21057 | -0.17853 | -0.15106 | -0.004577 | 0.022888 | -0.045776 | -0.018311 | -0.12817 | 0.050354 | 0.086975 | 0.027466 | 0.13275 | 0.073242 | 0.38452 | 123.6923 | 0.09613 | 123.5275 | 123.8022 | 123.6374 | 123.6282 | 123.5916 | -123.7839 | -123.6557 | 123.5184 | 123.4818 | 61.8347 | 61.8484
236.8594 | 123.6923 | -61.8668 | 61.7203 | 0.028458 | 0.0038857 | 0.070634 | 0.068861 | 0.0021939 | -0.0014484 | -0.00081595 | 0.0018005 | 0.0058683 | 0.071051 | 0.060887 | -0.0024396 | 0.015436 | -0.0010788 | 0.009155 | 61.7706 | -61.9949 | 61.6837 | -61.615 | -62.0316 | -62.0453 | 0.013733 | 61.6608 | -61.9125 | 61.6241 | -61.8118 | -61.8439 | -61.7798 | -0.12817 | 0.050354 | -0.036621 | 0.25177 | -0.17853 | -0.16479 | -0.050354 | -0.036621 | -0.045777 | -0.059509 | -0.09613 | 0.054931 | 0.086975 | 0.022888 | 0.13275 | 0.068665 | 0.37994 | 123.6786 | 0.10071 | 123.5367 | 123.7656 | 123.5733 | 123.6374 | 123.5275 | -123.7152 | -123.6328 | 123.5504 | 123.4909 | 61.8759 | 61.8805
238.5625 | 123.793 | -61.8484 | 61.6241 | -0.0020601 | 0.0023905 | 0.069566 | 0.06523 | 0.0045437 | -0.0042254 | 0.0015338 | -0.0012513 | 0.0050137 | 0.068274 | 0.065587 | -0.00094423 | 0.016077 | -1.0598e-05 | -0.11902 | 61.6974 | -62.0178 | 61.647 | -61.6241 | -62.0407 | -62.059 | -0.036621 | 61.5829 | -61.9125 | 61.6837 | -61.7889 | -61.8164 | -61.7432 | -0.16937 | 0.073242 | 0.022888 | 0.2243 | -0.21057 | -0.19226 | -0.041199 | -0.022888 | -0.064087 | -0.041199 | 0.059509 | 0.05951 | 0.10529 | 0.032044 | 0.16937 | 0.096131 | 0.39368 | 123.6649 | 0.1236 | 123.5962 | 123.7152 | 123.4955 | 123.5458 | 123.4314 | -123.642 | -123.5367 | 123.4955 | 123.5321 | 61.7294 | 61.8118
240.25 | 123.8297 | -61.8851 | 61.6333 | -0.0020601 | 0.0013223 | 0.068925 | 0.063735 | -0.0014377 | -0.0044392 | 0.00025205 | -0.0043029 | 0.0037319 | 0.06806 | 0.064946 | -0.0020122 | 0.013941 | 0.0004166 | -0.064087 | 61.6837 | -62.0224 | 61.702 | -61.528 | -61.94 | -61.9995 | 0.07782 | 61.5829 | -61.908 | 61.7065 | -61.7065 | -61.7386 | -61.7294 | -0.13733 | 0.050354 | 0.068664 | 0.35706 | -0.11444 | -0.054931 | 0.022888 | 0.082398 | -0.022888 | -0.050354 | 0.073242 | 0.17853 | 0.15564 | 0.14649 | 0.17853 | 0.16937 | 0.49438 | 123.7244 | 0.20142 | 123.6145 | 123.7061 | 123.4909 | 123.5687 | 123.468 | -123.6557 | -123.5413 | 123.587 | 123.5916 | 61.821 | 61.9629
242.0156 | 123.7427 | -61.8988 | 61.6196 | 0.028458 | 0.0038857 | 0.069353 | 0.065016 | 0.0019803 | -0.00059378 | 0.00067925 | 0.0048523 | 0.0048001 | 0.07041 | 0.062382 | -0.0017986 | 0.015223 | -0.0047104 | -0.11444 | 61.6837 | -62.0316 | 61.6379 | -61.6379 | -62.0499 | -62.0682 | -0.068665 | 61.5921 | -61.9308 | 61.6013 | -61.8347 | -61.8668 | -61.8073 | -0.13275 | 0.064087 | 0.01831 | 0.26093 | -0.16937 | -0.15106 | -0.036621 | -0.018311 | -0.032043 | -0.027466 | -0.018311 | 0.064087 | 0.091553 | 0.032044 | 0.1236 | 0.064087 | 0.39368 | 123.6694 | 0.09613 | 123.5321 | 123.7152 | 123.5229 | 123.5825 | 123.4909 | -123.6511 | -123.5504 | 123.5367 | 123.5001 | 61.7844 | 61.8301
243.7656 | 123.761 | -61.8988 | 61.647 | 0.036087 | 0.0043131 | 0.068712 | 0.066939 | 0.0026211 | -0.00080758 | -0.00060235 | 0.0079041 | 0.0050137 | 0.070624 | 0.063878 | -0.002226 | 0.015223 | -0.0023606 | -0.11902 | 61.6837 | -62.0544 | 61.6562 | -61.5921 | -62.0316 | -62.0453 | -0.022888 | 61.5875 | -61.9537 | 61.6425 | -61.8073 | -61.8073 | -61.7889 | -0.15564 | 0.036621 | 0.009155 | 0.3067 | -0.14648 | -0.13275 | 0.009155 | 0.022888 | -0.054931 | -0.05951 | -0.004578 | 0.091553 | 0.10986 | 0.091553 | 0.1648 | 0.14648 | 0.46234 | 123.7106 | 0.14648 | 123.5962 | 123.7381 | 123.5413 | 123.5825 | 123.4863 | -123.7015 | -123.6008 | 123.555 | 123.5413 | 61.7798 | 61.8759
245.4531 | 123.6649 | -61.8851 | 61.7065 | -0.017319 | 0.0045267 | 0.068712 | 0.068861 | 0.0024075 | -0.0020892 | 0.0015338 | -0.0012513 | 0.0056545 | 0.069769 | 0.060887 | -0.0017986 | 0.015009 | 0.0021256 | -0.091553 | 61.7615 | -62.0087 | 61.5784 | -61.702 | -62.1048 | -62.1094 | -0.10986 | 61.6608 | -61.9034 | 61.5784 | -61.8713 | -61.8988 | -61.8164 | -0.1236 | 0.054932 | -0.12817 | 0.18311 | -0.2243 | -0.21973 | -0.10071 | -0.09613 | -0.01831 | -0.045776 | -0.12817 | 0.013733 | 0.068665 | -0.013733 | 0.086975 | 0.004577 | 0.3067 | 123.587 | 0.032043 | 123.4818 | 123.7701 | 123.5641 | 123.6465 | 123.5458 | -123.7152 | -123.6099 | 123.4634 | 123.4634 | 61.7935 | 61.7752
247.1406 | 123.7473 | -61.8851 | 61.6104 | 0.0055694 | 0.0066629 | 0.070848 | 0.066298 | -0.0025059 | 0.001115 | 0.0026018 | 0.010956 | 0.0056545 | 0.069983 | 0.068577 | -0.00073063 | 0.01565 | -0.0008652 | -0.086975 | 61.6974 | -62.0316 | 61.6837 | -61.5555 | -62.0087 | -62.0132 | -0.013733 | 61.5738 | -61.94 | 61.6425 | -61.8118 | -61.8301 | -61.7981 | -0.14648 | 0.086975 | 0.073242 | 0.32959 | -0.12817 | -0.1236 | 0.01831 | 0.022888 | -0.054931 | -0.036621 | 0.032043 | 0.073242 | 0.086975 | 0.054932 | 0.14191 | 0.10986 | 0.47607 | 123.7152 | 0.12817 | 123.5825 | 123.7289 | 123.5138 | 123.5825 | 123.4589 | -123.642 | -123.5504 | 123.5687 | 123.5275 | 61.7981 | 61.8713
248.8906 | 123.793 | -61.8851 | 61.6333 | -0.0020601 | 0.0015359 | 0.068071 | 0.063735 | 0.0051845 | -0.0018756 | -0.0012434 | -0.0012513 | 0.0037319 | 0.068488 | 0.063878 | -0.002226 | 0.012446 | 0.000203 | -0.09613 | 61.6837 | -62.027 | 61.6882 | -61.5738 | -61.9675 | -62.0041 | 0.027466 | 61.5829 | -61.908 | 61.6882 | -61.7477 | -61.7615 | -61.7432 | -0.14191 | 0.050354 | 0.054931 | 0.31128 | -0.11902 | -0.082397 | 0.022889 | 0.05951 | -0.022888 | -0.050354 | 0.054931 | 0.13733 | 0.14191 | 0.1236 | 0.16479 | 0.14648 | 0.45319 | 123.7152 | 0.16022 | 123.5962 | 123.7106 | 123.4909 | 123.5687 | 123.468 | -123.6603 | -123.5413 | 123.5733 | 123.5733 | 61.7889 | 61.9125
250.6406 | 123.642 | -61.8713 | 61.702 | -0.0020601 | 0.0047403 | 0.070421 | 0.066939 | 0.0039029 | -0.00080758 | -0.00060235 | -0.0012513 | 0.0058683 | 0.070196 | 0.062169 | -0.0013714 | 0.013727 | -0.0064194 | -0.082397 | 61.7661 | -62.0224 | 61.5875 | -61.6837 | -62.0819 | -62.0865 | -0.11444 | 61.647 | -61.9034 | 61.5646 | -61.8988 | -61.9125 | -61.8301 | -0.15106 | 0.064087 | -0.11444 | 0.18768 | -0.21515 | -0.21057 | -0.064087 | -0.059509 | -0.032043 | -0.054931 | -0.13733 | -0.027466 | 0.041199 | -0.041199 | 0.073242 | -0.009156 | 0.33874 | 123.6099 | 0.004577 | 123.468 | 123.7885 | 123.5504 | 123.6374 | 123.5184 | -123.7244 | -123.6053 | 123.4589 | 123.436 | 61.7889 | 61.7569
252.3125 | 123.6969 | -61.8851 | 61.6837 | -0.0096891 | 0.0051675 | 0.069566 | 0.06288 | 0.0015529 | -0.00016658 | -0.00038875 | -0.0043029 | 0.0056545 | 0.066992 | 0.072209 | -0.0058576 | 0.011591 | 0.0004166 | -0.022888 | 61.7065 | -62.0178 | 61.6653 | -61.5646 | -61.9629 | -62.0041 | 0.027466 | 61.6562 | -61.9217 | 61.6196 | -61.7981 | -61.8118 | -61.7935 | -0.13275 | 0.022888 | -0.018311 | 0.32044 | -0.11902 | -0.07782 | 0.013733 | 0.054931 | -0.036621 | -0.027466 | -0.064087 | 0.086975 | 0.091553 | 0.073242 | 0.12817 | 0.10986 | 0.45319 | 123.6832 | 0.1236 | 123.5413 | 123.7244 | 123.5779 | 123.5916 | 123.5413 | -123.7015 | -123.6053 | 123.5504 | 123.5046 | 61.8622 | 61.9125
254 | 123.7793 | -61.8622 | 61.6562 | 0.0055694 | 0.0023905 | 0.070421 | 0.065443 | 0.0011257 | -0.001662 | 0.0015338 | 0.0018005 | 0.0045865 | 0.070196 | 0.065587 | 0.00012397 | 0.013086 | -0.001506 | -0.10529 | 61.6974 | -62.0132 | 61.647 | -61.615 | -62.0316 | -62.0453 | -0.022888 | 61.5829 | -61.8851 | 61.6699 | -61.7661 | -61.8118 | -61.7386 | -0.15106 | 0.041199 | -0.009155 | 0.24719 | -0.1831 | -0.16937 | -0.032043 | -0.01831 | -0.022888 | -0.073242 | 0.013733 | 0.096131 | 0.1236 | 0.050354 | 0.14649 | 0.073242 | 0.39825 | 123.6603 | 0.11902 | 123.555 | 123.7106 | 123.468 | 123.5596 | 123.4451 | -123.6694 | -123.5413 | 123.5092 | 123.5321 | 61.7569 | 61.8393
255.75 | 123.7061 | -61.8622 | 61.6928 | 0.013199 | 0.0066629 | 0.069353 | 0.06523 | 0.0034755 | -0.0025166 | -0.0035932 | 0.0048523 | 0.0075771 | 0.068915 | 0.062809 | -0.0013714 | 0.012446 | 0.0023392 | 0 | 61.7706 | -62.0041 | 61.6791 | -61.5646 | -61.9904 | -62.0041 | 0.050354 | 61.6425 | -61.8851 | 61.6562 | -61.7844 | -61.7889 | -61.7569 | -0.14191 | 0.07782 | -0.013733 | 0.29755 | -0.14191 | -0.12817 | 0 | 0.013733 | -0.022888 | -0.050354 | -0.036621 | 0.07782 | 0.10529 | 0.073243 | 0.12817 | 0.096131 | 0.43945 | 123.6832 | 0.10071 | 123.5413 | 123.7747 | 123.5275 | 123.6328 | 123.5046 | -123.6969 | -123.5779 | 123.5413 | 123.5184 | 61.8622 | 61.9125
257.4375 | 123.6511 | -61.8851 | 61.7065 | -0.0096891 | 0.0043131 | 0.070848 | 0.068861 | 0.0041165 | -0.0027302 | -0.002525 | -0.0012513 | 0.0041593 | 0.071905 | 0.067296 | -0.0011578 | 0.0133 | -0.0002244 | -0.09613 | 61.7386 | -62.0087 | 61.5692 | -61.6974 | -62.0956 | -62.1094 | -0.1236 | 61.6333 | -61.9171 | 61.5784 | -61.8851 | -61.8942 | -61.821 | -0.1236 | 0.032043 | -0.13733 | 0.18768 | -0.2243 | -0.21057 | -0.10071 | -0.086975 | -0.032043 | -0.073242 | -0.12817 | 0 | 0.064087 | -0.009155 | 0.09613 | 0.022888 | 0.31128 | 123.5779 | 0.032043 | 123.4955 | 123.7473 | 123.5504 | 123.6237 | 123.5184 | -123.7152 | -123.6237 | 123.4543 | 123.4634 | 61.7889 | 61.7615
259.1094 | 123.761 | -61.8622 | 61.6379 | -0.0020601 | 0.0053811 | 0.071062 | 0.06758 | 0.0011257 | -0.0029438 | -0.003166 | -0.0012513 | 0.0048001 | 0.06806 | 0.060246 | -0.001585 | 0.016718 | -0.0047104 | -0.10986 | 61.702 | -61.9858 | 61.6287 | -61.6196 | -62.0224 | -62.0499 | -0.022888 | 61.5738 | -61.9125 | 61.6608 | -61.7798 | -61.8118 | -61.7249 | -0.1236 | 0.064087 | -0.009155 | 0.24262 | -0.18768 | -0.16022 | -0.064087 | -0.036621 | -0.050354 | -0.064086 | 0.022889 | 0.082398 | 0.13733 | 0.050354 | 0.18768 | 0.10071 | 0.36621 | 123.6145 | 0.13275 | 123.5733 | 123.6877 | 123.4863 | 123.5641 | 123.436 | -123.6237 | -123.5504 | 123.4909 | 123.523 | 61.7523 | 61.8393
260.8438 | 123.7473 | -61.8484 | 61.6333 | -0.0096891 | 0.0049539 | 0.069139 | 0.065443 | -0.0042149 | -0.0018756 | -0.00017515 | 0.0018005 | 0.0056545 | 0.068915 | 0.065159 | -0.0013714 | 0.015009 | 0.0004166 | -0.1236 | 61.7203 | -62.0087 | 61.6379 | -61.6013 | -62.0224 | -62.0407 | -0.032043 | 61.5921 | -61.8988 | 61.6653 | -61.7615 | -61.7889 | -61.7294 | -0.16022 | 0.086975 | 0.004577 | 0.24719 | -0.19226 | -0.17395 | -0.032043 | -0.013733 | -0.050354 | -0.041199 | 0.032043 | 0.086975 | 0.11902 | 0.05951 | 0.16937 | 0.10986 | 0.40741 | 123.6465 | 0.13733 | 123.5641 | 123.7289 | 123.4909 | 123.5687 | 123.4406 | -123.642 | -123.5321 | 123.4863 | 123.5138 | 61.7249 | 61.8164
262.5938 | 123.6603 | -61.8805 | 61.702 | -0.0020601 | 0.0043131 | 0.068285 | 0.065016 | -0.0020787 | -0.0020892 | -0.00038875 | -0.0073547 | 0.0082181 | 0.069983 | 0.061741 | -0.0073528 | 0.012232 | -0.0017196 | -0.07782 | 61.7523 | -62.0087 | 61.5921 | -61.6516 | -62.0224 | -62.0499 | -0.036621 | 61.6974 | -61.9263 | 61.5692 | -61.8439 | -61.8576 | -61.7889 | -0.12817 | 0.050354 | -0.10986 | 0.22888 | -0.16937 | -0.14191 | -0.041199 | -0.013733 | -0.045777 | -0.004577 | -0.13275 | 0.036621 | 0.091553 | 0.022888 | 0.13733 | 0.068665 | 0.35706 | 123.6008 | 0.082398 | 123.4955 | 123.761 | 123.6237 | 123.6328 | 123.5779 | -123.7106 | -123.6282 | 123.4726 | 123.4497 | 61.8027 | 61.8439
264.2812 | 123.761 | -61.8393 | 61.6425 | -0.0020601 | 0.0040995 | 0.06978 | 0.064589 | 0.0043301 | -0.0027302 | -0.0027386 | -0.0012513 | 0.0045865 | 0.068488 | 0.065373 | 0.00076477 | 0.013514 | -0.0027878 | -0.07782 | 61.6699 | -61.972 | 61.647 | -61.5692 | -61.9904 | -62.0178 | 0 | 61.5555 | -61.9034 | 61.6837 | -61.7477 | -61.7981 | -61.7203 | -0.13275 | 0.027466 | 0.004578 | 0.27008 | -0.17853 | -0.15106 | -0.045776 | -0.01831 | -0.064087 | -0.086975 | 0.041199 | 0.091552 | 0.11902 | 0.041198 | 0.18311 | 0.10529 | 0.40283 | 123.6191 | 0.15564 | 123.587 | 123.642 | 123.4589 | 123.5092 | 123.3948 | -123.6145 | -123.5458 | 123.4863 | 123.5229 | 61.7615 | 61.8393
265.9688 | 123.6145 | -61.8484 | 61.6928 | 0.0055694 | 0.0036721 | 0.070634 | 0.066084 | 0.0049709 | -0.0012348 | -0.0016706 | -0.0012513 | 0.0062955 | 0.070196 | 0.061955 | -0.0041486 | 0.0133 | -0.002147 | -0.059509 | 61.7844 | -61.9949 | 61.5829 | -61.6699 | -62.0682 | -62.0911 | -0.09613 | 61.6608 | -61.9034 | 61.5692 | -61.8576 | -61.8851 | -61.8073 | -0.14648 | 0.091553 | -0.10986 | 0.17853 | -0.24261 | -0.21973 | -0.09613 | -0.073242 | -0.054931 | -0.032043 | -0.1236 | -0.009155 | 0.041199 | -0.036621 | 0.09613 | 0.01831 | 0.32501 | 123.5779 | 0.045776 | 123.4726 | 123.7793 | 123.5641 | 123.6328 | 123.5092 | -123.6877 | -123.5962 | 123.4314 | 123.4177 | 61.7889 | 61.7523
267.7188 | 123.642 | -61.8576 | 61.7111 | -0.0020601 | 0.0038857 | 0.068712 | 0.067366 | 0.0017667 | 0.00068782 | 0.001961 | -0.0043029 | 0.0056545 | 0.068915 | 0.054692 | -0.0024396 | 0.013514 | -0.003856 | -0.050354 | 61.7386 | -61.9995 | 61.6104 | -61.6379 | -62.027 | -62.0636 | -0.064087 | 61.6699 | -61.8942 | 61.5738 | -61.8484 | -61.8622 | -61.7844 | -0.14191 | 0.027465 | -0.10071 | 0.21973 | -0.20599 | -0.16937 | -0.064087 | -0.027466 | -0.036621 | -0.041199 | -0.13733 | 0.009155 | 0.073242 | -0.004578 | 0.10986 | 0.032043 | 0.36163 | 123.6099 | 0.045776 | 123.468 | 123.7381 | 123.5641 | 123.5962 | 123.5275 | -123.7106 | -123.6053 | 123.468 | 123.4314 | 61.8073 | 61.7935
269.4062 | 123.7427 | -61.8439 | 61.6287 | -0.0096891 | 0.0036721 | 0.069994 | 0.065443 | -0.00036966 | -0.0023028 | 0.00067925 | -0.0043029 | 0.0045865 | 0.069342 | 0.063023 | -0.00073063 | 0.015436 | -0.0023606 | -0.1236 | 61.734 | -62.0132 | 61.615 | -61.6013 | -62.0224 | -62.0316 | -0.027466 | 61.5738 | -61.9217 | 61.6562 | -61.7661 | -61.7844 | -61.7432 | -0.16937 | 0.10529 | -0.013733 | 0.24262 | -0.18768 | -0.17853 | -0.01831 | -0.009155 | -0.07782 | -0.054931 | 0.027466 | 0.07782 | 0.10071 | 0.059509 | 0.17853 | 0.13733 | 0.41199 | 123.6282 | 0.15564 | 123.5779 | 123.7473 | 123.4955 | 123.5779 | 123.4177 | -123.642 | -123.5504 | 123.4589 | 123.5001 | 61.7203 | 61.8164
271.0938 | 123.7518 | -61.8668 | 61.6653 | -0.0020601 | 0.0030313 | 0.069353 | 0.061385 | 0.0024075 | -0.0025166 | 0.00025205 | 0.0048523 | 0.0035183 | 0.067847 | 0.062382 | -0.005003 | 0.012659 | -0.000438 | -0.022888 | 61.6745 | -61.9995 | 61.6653 | -61.5372 | -61.9308 | -61.9629 | 0.068665 | 61.5829 | -61.8896 | 61.6516 | -61.7203 | -61.7477 | -61.7294 | -0.13275 | 0.009156 | 0 | 0.32959 | -0.096131 | -0.064087 | 0.036621 | 0.068665 | -0.022888 | -0.082397 | -0.013733 | 0.14648 | 0.13733 | 0.11902 | 0.16022 | 0.14191 | 0.46234 | 123.6649 | 0.16937 | 123.5413 | 123.674 | 123.4726 | 123.5413 | 123.4497 | -123.6649 | -123.555 | 123.5321 | 123.5184 | 61.8439 | 61.9354
272.8594 | 123.7381 | -61.8439 | 61.6653 | -0.0020601 | 0.0036721 | 0.068285 | 0.062239 | -0.00036966 | -0.0052936 | 0.00025205 | -0.0043029 | 0.0045865 | 0.068274 | 0.057896 | -0.0039348 | 0.013941 | 0.0006302 | -0.032043 | 61.6333 | -62.0178 | 61.6837 | -61.5189 | -61.9263 | -61.9629 | 0.045776 | 61.5555 | -61.8851 | 61.647 | -61.734 | -61.7386 | -61.7203 | -0.17395 | -0.032043 | 0.018311 | 0.32501 | -0.11902 | -0.082398 | 0.054931 | 0.091552 | -0.041199 | -0.10986 | -0.01831 | 0.10986 | 0.1236 | 0.10529 | 0.1648 | 0.14649 | 0.49896 | 123.7015 | 0.15106 | 123.5321 | 123.6511 | 123.4406 | 123.4772 | 123.3994 | -123.6832 | -123.5504 | 123.5275 | 123.4909 | 61.8118 | 61.8896
274.625 | 123.6877 | -61.8759 | 61.6516 | 0.020828 | 0.0045267 | 0.068071 | 0.063521 | 0.0013393 | -0.001662 | -0.00081595 | 0.0048523 | 0.0056545 | 0.071692 | 0.058964 | -0.00094423 | 0.014368 | 0.0031936 | -0.10986 | 61.6745 | -62.0361 | 61.6013 | -61.6287 | -61.9904 | -62.0316 | -0.064087 | 61.5417 | -61.9125 | 61.6013 | -61.821 | -61.8301 | -61.7889 | -0.16022 | 0.022889 | -0.050354 | 0.24719 | -0.15564 | -0.11444 | 0.004578 | 0.045777 | -0.036621 | -0.10986 | -0.050354 | 0.054932 | 0.086976 | 0.045777 | 0.1236 | 0.082398 | 0.40741 | 123.6374 | 0.091553 | 123.5138 | 123.7106 | 123.4543 | 123.5504 | 123.4177 | -123.6877 | -123.5641 | 123.4772 | 123.4772 | 61.7661 | 61.8118
276.3125 | 123.6969 | -61.8759 | 61.6379 | 0.020828 | 0.0045267 | 0.068285 | 0.066725 | -0.0020787 | -0.0025166 | -0.00038875 | 0.0018005 | 0.0039457 | 0.071265 | 0.06345 | 0.00012397 | 0.014368 | -0.000438 | -0.10986 | 61.6882 | -62.0316 | 61.5921 | -61.6333 | -62.0041 | -62.0453 | -0.07782 | 61.5784 | -61.8988 | 61.5875 | -61.8027 | -61.8164 | -61.7889 | -0.15564 | 0.050354 | -0.045776 | 0.24261 | -0.16937 | -0.12817 | -0.013733 | 0.027466 | -0.022888 | -0.059509 | -0.050354 | 0.073243 | 0.086976 | 0.05951 | 0.10986 | 0.082398 | 0.39825 | 123.6237 | 0.096131 | 123.4863 | 123.7198 | 123.4772 | 123.5641 | 123.4543 | -123.6694 | -123.5367 | 123.468 | 123.4634 | 61.7661 | 61.7981
278.0781 | 123.6145 | -61.8484 | 61.702 | -0.0096891 | 0.0051675 | 0.070634 | 0.065657 | 5.774e-05 | -0.0010212 | -0.0038068 | -0.0043029 | 0.0050137 | 0.069342 | 0.056187 | -0.0024396 | 0.013941 | 0.000203 | -0.07782 | 61.7706 | -61.9949 | 61.5509 | -61.7111 | -62.0819 | -62.1002 | -0.10529 | 61.6425 | -61.8896 | 61.5829 | -61.8668 | -61.8713 | -61.7889 | -0.14648 | 0.068665 | -0.15106 | 0.13733 | -0.25177 | -0.23346 | -0.10529 | -0.086975 | -0.041198 | -0.059509 | -0.11902 | -0.01831 | 0.05951 | -0.022888 | 0.10071 | 0.01831 | 0.28381 | 123.5458 | 0.022888 | 123.4726 | 123.7656 | 123.5321 | 123.6191 | 123.4909 | -123.6969 | -123.5916 | 123.3994 | 123.4314 | 61.7706 | 61.7432
279.8281 | 123.6923 | -61.8759 | 61.6379 | 0.013199 | 0.0036721 | 0.069139 | 0.064162 | 0.00048494 | -0.0014484 | -0.0010298 | 0.0018005 | 0.0043729 | 0.069556 | 0.065373 | -0.002226 | 0.014368 | 0.0016982 | -0.10529 | 61.6562 | -62.0407 | 61.6013 | -61.6104 | -62.0087 | -62.0407 | -0.091553 | 61.5555 | -61.9583 | 61.5875 | -61.8164 | -61.8073 | -61.7752 | -0.16479 | 0.018311 | -0.036621 | 0.2655 | -0.16479 | -0.13275 | 0 | 0.032043 | -0.082397 | -0.082397 | -0.050354 | 0.05951 | 0.10071 | 0.068665 | 0.1831 | 0.15106 | 0.4303 | 123.642 | 0.14191 | 123.5458 | 123.6969 | 123.5138 | 123.5321 | 123.4314 | -123.6786 | -123.5962 | 123.4772 | 123.4634 | 61.7706 | 61.7844
281.5156 | 123.6145 | -61.8439 | 61.7249 | -0.0020601 | 0.0028177 | 0.066576 | 0.06523 | 0.0019803 | -0.0029438 | -0.001457 | -0.0012513 | 0.0067227 | 0.071692 | 0.062596 | -0.0054302 | 0.014368 | -0.0019332 | -0.059509 | 61.7477 | -61.9904 | 61.5829 | -61.6425 | -62.0178 | -62.0407 | -0.064087 | 61.6516 | -61.9034 | 61.5509 | -61.8164 | -61.8301 | -61.7889 | -0.14648 | 0.022888 | -0.14191 | 0.20142 | -0.19684 | -0.17395 | -0.050354 | -0.027466 | -0.059509 | -0.073243 | -0.17395 | 0.027466 | 0.054932 | 0.013733 | 0.11444 | 0.073242 | 0.3479 | 123.5733 | 0.086975 | 123.4543 | 123.7381 | 123.555 | 123.5916 | 123.4955 | -123.7152 | -123.6282 | 123.4268 | 123.3948 | 61.7844 | 61.7798
283.2656 | 123.7473 | -61.8347 | 61.6241 | -0.0020601 | 0.0038857 | 0.070848 | 0.064803 | -0.00036966 | -0.0031574 | 0.00025205 | -0.0012513 | 0.0028775 | 0.068915 | 0.067936 | 0.0031146 | 0.013941 | -0.000438 | -0.054932 | 61.6516 | -61.9675 | 61.6608 | -61.5417 | -61.972 | -62.0087 | 0.009155 | 61.5509 | -61.9583 | 61.6745 | -61.734 | -61.7569 | -61.7111 | -0.13275 | 0.027465 | 0.036621 | 0.29297 | -0.17395 | -0.13733 | -0.041199 | -0.004578 | -0.1236 | -0.073243 | 0.050354 | 0.10071 | 0.1236 | 0.07782 | 0.24719 | 0.20142 | 0.42572 | 123.6282 | 0.2243 | 123.6328 | 123.6191 | 123.5092 | 123.4863 | 123.3856 | -123.5916 | -123.5825 | 123.4955 | 123.5092 | 61.7798 | 61.8439
285 | 123.6374 | -61.8118 | 61.7065 | 0.028458 | 0.0049539 | 0.068925 | 0.068861 | 0.0043301 | -0.0042254 | 0.00089285 | 0.014008 | 0.0071499 | 0.071051 | 0.056614 | -0.0039348 | 0.013086 | -0.0025742 | -0.022888 | 61.7798 | -62.0316 | 61.6104 | -61.6196 | -61.9583 | -61.9995 | -0.009155 | 61.6928 | -61.8942 | 61.6058 | -61.7661 | -61.7981 | -61.7477 | -0.21973 | 0.073242 | -0.09613 | 0.19226 | -0.18768 | -0.14648 | 0.032043 | 0.073242 | -0.082397 | -0.013733 | -0.10071 | 0.045777 | 0.064087 | 0.013733 | 0.14648 | 0.09613 | 0.41199 | 123.642 | 0.12817 | 123.5001 | 123.8113 | 123.587 | 123.5916 | 123.5046 | -123.7381 | -123.6008 | 123.4222 | 123.4177 | 61.7889 | 61.8027
286.6719 | 123.5916 | -61.853 | 61.702 | -0.0020601 | 0.0068765 | 0.068498 | 0.066084 | 0.0032619 | -0.0037982 | -0.0035932 | -0.0043029 | 0.0045865 | 0.069128 | 0.061314 | -0.0024396 | 0.013514 | 0.0010574 | -0.10071 | 61.7386 | -61.9858 | 61.5463 | -61.6837 | -62.0682 | -62.0773 | -0.11444 | 61.647 | -61.9125 | 61.5692 | -61.8576 | -61.8759 | -61.7798 | -0.13275 | 0.036621 | -0.15564 | 0.16937 | -0.22431 | -0.21515 | -0.091553 | -0.082397 | -0.05951 | -0.054931 | -0.13275 | -0.004578 | 0.073242 | -0.022889 | 0.13275 | 0.036621 | 0.30212 | 123.5321 | 0.054932 | 123.4818 | 123.7244 | 123.5596 | 123.5916 | 123.5001 | -123.6877 | -123.6145 | 123.3994 | 123.4222 | 61.7523 | 61.7386
288.4219 | 123.7106 | -61.8301 | 61.647 | 0.0055694 | 0.0045267 | 0.071916 | 0.064375 | 0.0011257 | -0.0035846 | -0.0016706 | -0.0043029 | 0.0030911 | 0.067419 | 0.060246 | -0.0028668 | 0.013941 | -0.0055648 | -0.022888 | 61.647 | -61.9949 | 61.6653 | -61.5234 | -61.9125 | -61.9629 | 0.032043 | 61.5738 | -61.8713 | 61.6287 | -61.7203 | -61.7386 | -61.7294 | -0.16479 | 0 | 0.01831 | 0.3067 | -0.13275 | -0.082398 | 0.032043 | 0.082397 | -0.041199 | -0.073242 | -0.018311 | 0.10986 | 0.10071 | 0.091553 | 0.14191 | 0.13275 | 0.4715 | 123.6603 | 0.15106 | 123.5001 | 123.642 | 123.4451 | 123.4772 | 123.4039 | -123.642 | -123.5184 | 123.4955 | 123.4589 | 61.8073 | 61.8622
290.1094 | 123.6603 | -61.8713 | 61.6241 | -0.0020601 | 0.0049539 | 0.069139 | 0.066298 | 0.0039029 | -0.0014484 | -0.0033796 | 0.0048523 | 0.0048001 | 0.069983 | 0.0611 | -0.0011578 | 0.012873 | -0.0002244 | -0.1236 | 61.7203 | -61.9675 | 61.5692 | -61.6425 | -62.0636 | -62.0819 | -0.091553 | 61.6013 | -61.8805 | 61.5875 | -61.8118 | -61.8347 | -61.7661 | -0.09613 | 0.09613 | -0.054932 | 0.22888 | -0.21057 | -0.19226 | -0.11444 | -0.096131 | -0.009155 | -0.022889 | -0.036622 | 0.059509 | 0.10529 | 0.036621 | 0.11444 | 0.045776 | 0.32501 | 123.5367 | 0.068664 | 123.468 | 123.6877 | 123.4818 | 123.5916 | 123.4726 | -123.5916 | -123.5046 | 123.4406 | 123.4589 | 61.7477 | 61.7798
291.8438 | 123.6053 | -61.8439 | 61.6791 | -0.017319 | 0.0060221 | 0.072557 | 0.065016 | 0.0026211 | -0.003371 | -0.004875 | -0.0073547 | 0.0062955 | 0.068915 | 0.063023 | -0.0024396 | 0.015223 | -0.0006516 | -0.07782 | 61.7615 | -61.9858 | 61.5463 | -61.6837 | -62.0773 | -62.1002 | -0.1236 | 61.6241 | -61.9125 | 61.5692 | -61.8439 | -61.8622 | -61.7706 | -0.14191 | 0.082398 | -0.13275 | 0.16022 | -0.25635 | -0.23346 | -0.11444 | -0.091553 | -0.068665 | -0.054931 | -0.10986 | 0 | 0.073242 | -0.018311 | 0.14191 | 0.050354 | 0.30212 | 123.5321 | 0.068665 | 123.4818 | 123.7473 | 123.5367 | 123.6053 | 123.468 | -123.6649 | -123.5916 | 123.3902 | 123.4131 | 61.7661 | 61.7203
293.5938 | 123.6649 | -61.821 | 61.6791 | 0.020828 | 0.0058083 | 0.069566 | 0.067366 | -0.0010105 | -0.001662 | 0.0011066 | 0.0018005 | 0.0060819 | 0.070196 | 0.066227 | -0.0020122 | 0.015009 | -0.003215 | 0.004578 | 61.7798 | -61.9949 | 61.647 | -61.5555 | -61.9492 | -61.9858 | 0.027466 | 61.647 | -61.8439 | 61.6379 | -61.7661 | -61.7752 | -61.7294 | -0.17395 | 0.10071 | -0.032043 | 0.2655 | -0.16479 | -0.12817 | 0.009155 | 0.045776 | -0.022888 | -0.032043 | -0.041199 | 0.054932 | 0.091553 | 0.045776 | 0.11444 | 0.068664 | 0.43945 | 123.642 | 0.07782 | 123.4818 | 123.7747 | 123.4909 | 123.6008 | 123.468 | -123.674 | -123.5229 | 123.468 | 123.4589 | 61.8256 | 61.8484
295.3281 | 123.642 | -61.8347 | 61.6699 | -0.017319 | 0.0034585 | 0.070421 | 0.061812 | -0.00079686 | -0.0029438 | -0.00038875 | -0.0012513 | 0.0033047 | 0.069556 | 0.066014 | -0.0041486 | 0.011377 | -0.001506 | -0.032043 | 61.6699 | -61.9904 | 61.6425 | -61.5326 | -61.9217 | -61.9766 | 0.027466 | 61.6013 | -61.853 | 61.6104 | -61.7523 | -61.7615 | -61.7569 | -0.15564 | 0 | -0.027466 | 0.30212 | -0.14191 | -0.086975 | 0.013732 | 0.068664 | -0.01831 | -0.068665 | -0.059509 | 0.082398 | 0.07782 | 0.073242 | 0.09613 | 0.091552 | 0.45776 | 123.6328 | 0.10071 | 123.4634 | 123.6603 | 123.4543 | 123.5046 | 123.436 | -123.6603 | -123.5229 | 123.4772 | 123.4451 | 61.8027 | 61.8622
297.0938 | 123.7656 | -61.8393 | 61.6013 | -0.017319 | 0.0030313 | 0.068071 | 0.063307 | 0.00048494 | -0.0035846 | -0.00060235 | 0.0048523 | 0.0020231 | 0.070196 | 0.0658 | -0.0020122 | 0.014368 | -0.0036422 | -0.073242 | 61.6425 | -61.9858 | 61.6562 | -61.5051 | -61.9171 | -61.9354 | 0.059509 | 61.5417 | -61.8896 | 61.6837 | -61.6837 | -61.7065 | -61.6928 | -0.14648 | 0.041199 | 0.054932 | 0.33417 | -0.096131 | -0.07782 | 0.050354 | 0.068665 | -0.050354 | -0.059509 | 0.082398 | 0.15564 | 0.14648 | 0.13275 | 0.19684 | 0.1831 | 0.48065 | 123.642 | 0.20599 | 123.5733 | 123.6282 | 123.4314 | 123.4818 | 123.381 | -123.587 | -123.4909 | 123.4955 | 123.5229 | 61.7661 | 61.8988
298.8438 | 123.6786 | -61.8301 | 61.6196 | 0.036087 | 0.0049539 | 0.070848 | 0.065657 | -0.0010105 | 0.00068782 | 0.00067925 | 0.010956 | 0.0037319 | 0.069983 | 0.066655 | -0.0011578 | 0.016291 | -0.0023606 | -0.10529 | 61.6562 | -62.0407 | 61.6058 | -61.5555 | -61.9858 | -62.0132 | -0.027466 | 61.5463 | -61.8988 | 61.615 | -61.7661 | -61.7935 | -61.7615 | -0.21057 | 0.036621 | -0.013733 | 0.27466 | -0.18311 | -0.15564 | 0.027465 | 0.054931 | -0.068665 | -0.073242 | -0.004578 | 0.064087 | 0.068664 | 0.036621 | 0.13733 | 0.10529 | 0.48523 | 123.6465 | 0.13275 | 123.5138 | 123.6969 | 123.4451 | 123.4863 | 123.3765 | -123.6603 | -123.5184 | 123.436 | 123.4451 | 61.7249 | 61.8027
300.5312 | 123.7152 | -61.8393 | 61.5921 | -0.0020601 | 0.0013223 | 0.070207 | 0.066298 | 0.0041165 | -0.0018756 | -0.004234 | -0.0012513 | 0.0043729 | 0.069556 | 0.059391 | 0.00076477 | 0.01565 | -0.000438 | -0.054932 | 61.6425 | -61.9629 | 61.6516 | -61.5463 | -61.972 | -62.0041 | 0.009155 | 61.5372 | -61.8805 | 61.6562 | -61.7294 | -61.7432 | -61.6928 | -0.1236 | 0.050354 | 0.059509 | 0.29297 | -0.16479 | -0.13275 | -0.041198 | -0.009155 | -0.041199 | -0.054932 | 0.064087 | 0.10986 | 0.14648 | 0.09613 | 0.18768 | 0.13733 | 0.41656 | 123.6145 | 0.15106 | 123.5367 | 123.6053 | 123.4177 | 123.4818 | 123.3765 | -123.555 | -123.4726 | 123.4909 | 123.4955 | 61.7844 | 61.8484
302.2656 | 123.6603 | -61.8484 | 61.6013 | 0.013199 | 0.0053811 | 0.070848 | 0.064589 | -0.0022923 | -0.00038018 | -0.0035932 | 0.0048523 | 0.0035183 | 0.071478 | 0.062382 | -0.0024396 | 0.014795 | -0.0006516 | -0.10071 | 61.6699 | -61.9995 | 61.5967 | -61.5967 | -61.9858 | -62.0453 | -0.073242 | 61.5738 | -61.908 | 61.5875 | -61.7981 | -61.821 | -61.7706 | -0.15106 | 0.068665 | -0.004577 | 0.25177 | -0.19684 | -0.13733 | -0.045776 | 0.013733 | -0.059509 | -0.027465 | -0.013733 | 0.050354 | 0.07782 | 0.027466 | 0.13733 | 0.086975 | 0.40283 | 123.5962 | 0.10986 | 123.4955 | 123.6694 | 123.4818 | 123.5184 | 123.4222 | -123.6008 | -123.5092 | 123.4451 | 123.436 | 61.7477 | 61.7752
304.0156 | 123.7198 | -61.8027 | 61.6013 | -0.0096891 | 0.0040995 | 0.068285 | 0.061385 | -0.0018649 | -0.00508 | 3.8448e-05 | -0.0073547 | 0.0043729 | 0.067633 | 0.065587 | -0.0037212 | 0.013727 | -0.0002244 | -0.036621 | 61.6104 | -61.972 | 61.6699 | -61.5189 | -61.908 | -61.94 | 0.054932 | 61.5509 | -61.8759 | 61.6653 | -61.6791 | -61.702 | -61.6882 | -0.16937 | 0.009156 | 0.068665 | 0.28381 | -0.13733 | -0.10529 | 0.032044 | 0.064087 | -0.073243 | -0.050354 | 0.064087 | 0.1236 | 0.11444 | 0.10071 | 0.18768 | 0.17395 | 0.45319 | 123.642 | 0.19684 | 123.5413 | 123.5825 | 123.4268 | 123.4131 | 123.3536 | -123.5733 | -123.4772 | 123.4726 | 123.468 | 61.7661 | 61.8576
305.6875 | 123.6191 | -61.8256 | 61.6928 | -0.0020601 | 0.0043131 | 0.069139 | 0.066725 | 0.0013393 | 4.7018e-05 | -0.00081595 | 0.0018005 | 0.0054409 | 0.071265 | 0.061314 | -0.0026532 | 0.013086 | -0.0012924 | 0.018311 | 61.7432 | -61.972 | 61.6287 | -61.5509 | -61.9629 | -61.9995 | 0.009155 | 61.6241 | -61.8759 | 61.6058 | -61.7661 | -61.8027 | -61.734 | -0.14648 | 0.050354 | -0.064087 | 0.27466 | -0.17395 | -0.13733 | -0.027466 | 0.009155 | -0.050354 | -0.068664 | -0.086975 | 0.05951 | 0.091553 | 0.022889 | 0.14191 | 0.073243 | 0.42114 | 123.6008 | 0.10986 | 123.4818 | 123.7152 | 123.5001 | 123.5687 | 123.4497 | -123.6649 | -123.5687 | 123.4543 | 123.4314 | 61.8439 | 61.8347
307.4375 | 123.6053 | -61.8622 | 61.6791 | -0.0020601 | 0.0036721 | 0.069139 | 0.06758 | 0.0015529 | -0.0027302 | -0.0016706 | 0.0018005 | 0.0056545 | 0.070196 | 0.064732 | -0.0030804 | 0.016504 | -0.0008652 | -0.091553 | 61.7432 | -61.972 | 61.5417 | -61.6653 | -62.059 | -62.0636 | -0.10071 | 61.6104 | -61.9171 | 61.5509 | -61.8301 | -61.8668 | -61.7844 | -0.10986 | 0.064087 | -0.13733 | 0.19684 | -0.20142 | -0.19684 | -0.091553 | -0.086975 | -0.054931 | -0.068664 | -0.12817 | 0.032044 | 0.07782 | -0.004577 | 0.13275 | 0.050354 | 0.3067 | 123.5138 | 0.086975 | 123.468 | 123.7152 | 123.5275 | 123.6053 | 123.4726 | -123.6511 | -123.5962 | 123.4039 | 123.4131 | 61.7706 | 61.7615
309.1875 | 123.6465 | -61.821 | 61.6745 | 0.013199 | 0.0047403 | 0.070634 | 0.066298 | 0.0024075 | -0.00080758 | 0.001961 | 0.0048523 | 0.0082181 | 0.068915 | 0.058751 | -0.0041486 | 0.011591 | -0.0030014 | -0.004578 | 61.7569 | -61.9766 | 61.6333 | -61.5601 | -61.9675 | -61.9858 | 0.041199 | 61.6379 | -61.853 | 61.615 | -61.7294 | -61.7661 | -61.7111 | -0.15564 | 0.082397 | -0.041199 | 0.26093 | -0.16479 | -0.14648 | -0.009155 | 0.009156 | -0.032043 | -0.036622 | -0.05951 | 0.091553 | 0.10986 | 0.054932 | 0.14191 | 0.086975 | 0.41656 | 123.6099 | 0.1236 | 123.468 | 123.7335 | 123.4909 | 123.5779 | 123.4589 | -123.6511 | -123.5275 | 123.4543 | 123.436 | 61.8164 | 61.8622
310.8594 | 123.6923 | -61.8301 | 61.6196 | -0.0020601 | 0.0028177 | 0.068071 | 0.065657 | 0.00027134 | -0.0027302 | 0.0011066 | -0.0012513 | 0.0058683 | 0.069128 | 0.06345 | -8.9634e-05 | 0.013514 | -0.0025742 | -0.10986 | 61.702 | -61.9812 | 61.5601 | -61.6104 | -62.0361 | -62.0407 | -0.07782 | 61.5784 | -61.8851 | 61.6241 | -61.7523 | -61.7661 | -61.7065 | -0.15106 | 0.082397 | -0.059509 | 0.21973 | -0.21057 | -0.20599 | -0.059509 | -0.054932 | -0.054932 | -0.041199 | 0.004578 | 0.07782 | 0.1236 | 0.064087 | 0.17853 | 0.11902 | 0.37079 | 123.5413 | 0.13275 | 123.5092 | 123.6832 | 123.4634 | 123.5321 | 123.4085 | -123.6008 | -123.5046 | 123.3902 | 123.4543 | 61.7203 | 61.7523
312.6094 | 123.7061 | -61.8256 | 61.6196 | -0.0020601 | 0.0026041 | 0.070634 | 0.064803 | 0.0049709 | -0.0010212 | -0.0027386 | 0.0018005 | 0.0039457 | 0.068701 | 0.061741 | -0.00073063 | 0.014795 | -0.0010788 | -0.11444 | 61.6745 | -61.9812 | 61.615 | -61.5646 | -61.9812 | -62.0041 | -0.022888 | 61.5097 | -61.8896 | 61.6425 | -61.7203 | -61.7477 | -61.6837 | -0.15564 | 0.054932 | -0.004578 | 0.26093 | -0.17853 | -0.15564 | -0.022888 | 0 | -0.064086 | -0.10986 | 0.022888 | 0.10529 | 0.14191 | 0.07782 | 0.20599 | 0.14191 | 0.41656 | 123.5962 | 0.16937 | 123.5321 | 123.6557 | 123.3994 | 123.5001 | 123.3353 | -123.6008 | -123.5092 | 123.4406 | 123.468 | 61.7111 | 61.8027
314.3594 | 123.7381 | -61.8347 | 61.6333 | 0.0055694 | 0.0043131 | 0.069566 | 0.064375 | 0.0013393 | -0.0020892 | -0.001457 | -0.0012513 | 0.0048001 | 0.070624 | 0.061528 | -0.0045758 | 0.013514 | -0.0055648 | -0.059509 | 61.6287 | -61.9904 | 61.6287 | -61.5097 | -61.9125 | -61.94 | 0.054932 | 61.5372 | -61.8713 | 61.6653 | -61.6791 | -61.6882 | -61.6882 | -0.15564 | -0.004578 | -0.004578 | 0.32501 | -0.10529 | -0.07782 | 0.050354 | 0.077819 | -0.036621 | -0.096131 | 0.032043 | 0.15564 | 0.14648 | 0.14648 | 0.18311 | 0.18311 | 0.48065 | 123.6191 | 0.19226 | 123.5367 | 123.6191 | 123.4085 | 123.4634 | 123.3719 | -123.6237 | -123.5046 | 123.4634 | 123.5001 | 61.7752 | 61.8896
316.0625 | 123.6694 | -61.8347 | 61.6241 | 0.020828 | 0.0019631 | 0.068071 | 0.064589 | -0.00058326 | -0.0020892 | -0.00060235 | -0.0043029 | 0.0033047 | 0.06806 | 0.064732 | -0.0024396 | 0.017145 | 0.000203 | -0.11444 | 61.6425 | -62.0087 | 61.5509 | -61.6013 | -61.9949 | -62.0132 | -0.073242 | 61.5463 | -61.908 | 61.5921 | -61.7661 | -61.7752 | -61.7386 | -0.17395 | 0.01831 | -0.073243 | 0.23346 | -0.17853 | -0.16022 | -0.004578 | 0.013733 | -0.073242 | -0.07782 | -0.032044 | 0.068665 | 0.096131 | 0.059509 | 0.16937 | 0.13275 | 0.40741 | 123.5596 | 0.14191 | 123.5001 | 123.6511 | 123.4543 | 123.4772 | 123.381 | -123.6328 | -123.5321 | 123.3856 | 123.4268 | 61.7203 | 61.7615
317.8125 | 123.6603 | -61.8118 | 61.615 | -0.0020601 | 0.0058083 | 0.067644 | 0.066512 | -0.00058326 | -0.00059378 | -0.0016706 | 0.0018005 | 0.0069363 | 0.06806 | 0.067082 | -0.0020122 | 0.013727 | -0.0040696 | -0.11902 | 61.6791 | -61.9858 | 61.5601 | -61.6241 | -62.0361 | -62.0453 | -0.073242 | 61.5555 | -61.8576 | 61.5967 | -61.7661 | -61.7889 | -61.7157 | -0.17395 | 0.064087 | -0.054931 | 0.18768 | -0.23346 | -0.2243 | -0.059509 | -0.050354 | -0.045776 | -0.059509 | -0.01831 | 0.045777 | 0.096131 | 0.022889 | 0.14191 | 0.068665 | 0.36163 | 123.5458 | 0.091553 | 123.4543 | 123.6649 | 123.4131 | 123.4909 | 123.3673 | -123.6008 | -123.4726 | 123.3719 | 123.4085 | 61.6928 | 61.7386
319.5625 | 123.6923 | -61.8164 | 61.6241 | -0.0096891 | 0.0030313 | 0.069566 | 0.06523 | 0.0015529 | -0.0031574 | -0.001457 | 0.0018005 | 0.0035183 | 0.067633 | 0.0658 | -0.002226 | 0.013941 | -0.0012924 | -0.027466 | 61.6241 | -61.9766 | 61.647 | -61.4868 | -61.8988 | -61.9354 | 0.050354 | 61.5463 | -61.8759 | 61.647 | -61.702 | -61.7157 | -61.6837 | -0.16022 | 0 | 0.022888 | 0.32959 | -0.11902 | -0.082398 | 0.041199 | 0.07782 | -0.05951 | -0.07782 | 0.022888 | 0.11444 | 0.13275 | 0.10071 | 0.19226 | 0.16022 | 0.48981 | 123.6237 | 0.17395 | 123.5229 | 123.6008 | 123.4222 | 123.4406 | 123.3627 | -123.6008 | -123.5001 | 123.4634 | 123.4634 | 61.7889 | 61.8668
321.25 | 123.555 | -61.8256 | 61.6974 | -0.0020601 | 0.0040995 | 0.067644 | 0.065443 | 0.00091214 | -0.0042254 | -0.0016706 | -0.0043029 | 0.0039457 | 0.069556 | 0.061528 | -0.0052166 | 0.013727 | -0.003856 | -0.059509 | 61.6882 | -61.9812 | 61.5463 | -61.615 | -61.9858 | -62.0316 | -0.073242 | 61.615 | -61.8668 | 61.5326 | -61.7798 | -61.8164 | -61.7661 | -0.15564 | -0.009156 | -0.15106 | 0.21057 | -0.20599 | -0.16022 | -0.050354 | -0.004578 | -0.041198 | -0.082398 | -0.16479 | 0.045777 | 0.05951 | 0.009156 | 0.10071 | 0.050354 | 0.36621 | 123.5275 | 0.086975 | 123.3994 | 123.6694 | 123.4818 | 123.5138 | 123.4406 | -123.6786 | -123.5641 | 123.3719 | 123.3582 | 61.7661 | 61.7523
323 | 123.6969 | -61.8073 | 61.5875 | -0.0096891 | 0.00089511 | 0.067857 | 0.06288 | -0.00015586 | -0.0020892 | -0.0023114 | -0.0012513 | 0.0050137 | 0.067847 | 0.069645 | -0.0028668 | 0.012446 | -0.001506 | -0.036621 | 61.6104 | -61.9492 | 61.6425 | -61.4685 | -61.9034 | -61.9217 | 0.050354 | 61.5463 | -61.8759 | 61.6379 | -61.6837 | -61.6882 | -61.6928 | -0.14191 | 0.022889 | 0.054932 | 0.33875 | -0.11444 | -0.09613 | 0.027466 | 0.045777 | -0.068665 | -0.041198 | 0.050354 | 0.1236 | 0.11444 | 0.11902 | 0.18311 | 0.18768 | 0.48065 | 123.5916 | 0.19226 | 123.5138 | 123.5596 | 123.4222 | 123.4177 | 123.3536 | -123.5367 | -123.4634 | 123.4497 | 123.4451 | 61.7706 | 61.8576
324.6875 | 123.5458 | -61.8347 | 61.6745 | 0.013199 | 0.0051675 | 0.06978 | 0.067366 | 5.774e-05 | -0.0023028 | -0.00038875 | -0.0012513 | 0.0073635 | 0.07041 | 0.064518 | -0.0011578 | 0.014155 | -0.003215 | -0.082397 | 61.734 | -61.9537 | 61.5326 | -61.6653 | -62.0407 | -62.0682 | -0.12817 | 61.6058 | -61.8896 | 61.5189 | -61.8576 | -61.8713 | -61.7798 | -0.11902 | 0.059509 | -0.14191 | 0.16937 | -0.23346 | -0.20599 | -0.11444 | -0.086975 | -0.054931 | -0.068665 | -0.15564 | -0.022888 | 0.054932 | -0.036621 | 0.10986 | 0.01831 | 0.28839 | 123.4863 | 0.032043 | 123.4085 | 123.6877 | 123.4955 | 123.5687 | 123.4406 | -123.6282 | -123.5641 | 123.3673 | 123.3536 | 61.7523 | 61.7065
326.4375 | 123.6099 | -61.8027 | 61.6928 | 0.020828 | 0.0047403 | 0.068285 | 0.065016 | 0.0030483 | -0.0044392 | -0.001457 | 0.0048523 | 0.0048001 | 0.07041 | 0.065373 | -0.001585 | 0.014795 | -0.000438 | 0 | 61.7386 | -61.9812 | 61.615 | -61.5326 | -61.9354 | -61.9629 | 0.041199 | 61.6287 | -61.8576 | 61.6104 | -61.7111 | -61.7523 | -61.6882 | -0.17853 | 0.045776 | -0.07782 | 0.27008 | -0.16022 | -0.13275 | 0.01831 | 0.045776 | -0.054932 | -0.064087 | -0.082397 | 0.091552 | 0.11444 | 0.050354 | 0.16937 | 0.10529 | 0.44861 | 123.5962 | 0.14648 | 123.468 | 123.7198 | 123.4863 | 123.5413 | 123.4314 | -123.674 | -123.5504 | 123.4177 | 123.4131 | 61.8027 | 61.8439
328.1875 | 123.6969 | -61.8073 | 61.6241 | -0.017319 | 0.0075173 | 0.067644 | 0.063094 | 0.0019803 | -0.0020892 | -0.0027386 | -0.0012513 | 0.0041593 | 0.07041 | 0.067723 | -0.0026532 | 0.01565 | -0.0059922 | -0.045776 | 61.6196 | -61.9675 | 61.6425 | -61.4914 | -61.9034 | -61.9354 | 0.073242 | 61.528 | -61.8576 | 61.6287 | -61.6791 | -61.6928 | -61.6791 | -0.16022 | -0.004578 | 0.01831 | 0.31586 | -0.12817 | -0.09613 | 0.032043 | 0.064087 | -0.050354 | -0.096131 | 0.004577 | 0.12817 | 0.12817 | 0.11444 | 0.17853 | 0.16479 | 0.47607 | 123.6099 | 0.17853 | 123.4863 | 123.587 | 123.3856 | 123.4268 | 123.3353 | -123.5916 | -123.4818 | 123.4497 | 123.436 | 61.7615 | 61.8805
329.875 | 123.6969 | -61.8118 | 61.615 | 0.0055694 | 0.0062357 | 0.070421 | 0.065657 | 0.0026211 | -0.0014484 | 3.8448e-05 | 0.014008 | 0.0043729 | 0.069342 | 0.071995 | -0.0020122 | 0.015223 | -0.0008652 | -0.068665 | 61.647 | -61.9537 | 61.6333 | -61.4914 | -61.9308 | -61.9446 | 0.050354 | 61.528 | -61.8942 | 61.6241 | -61.6974 | -61.7294 | -61.6837 | -0.14191 | 0.032044 | 0.018311 | 0.32044 | -0.13275 | -0.11902 | 0.009155 | 0.022888 | -0.082397 | -0.086975 | 0.009156 | 0.11444 | 0.12817 | 0.082398 | 0.21057 | 0.1648 | 0.46234 | 123.587 | 0.19684 | 123.5184 | 123.6008 | 123.4222 | 123.4589 | 123.3398 | -123.5687 | -123.5092 | 123.4451 | 123.436 | 61.7432 | 61.8622
331.625 | 123.6832 | -61.8027 | 61.6287 | 0.0055694 | 0.0047403 | 0.069139 | 0.063521 | 0.0024075 | -0.0037982 | -0.0020978 | 0.0018005 | 0.0024503 | 0.071265 | 0.067723 | -0.0041486 | 0.015864 | -0.001506 | -0.022888 | 61.6196 | -61.9629 | 61.647 | -61.5051 | -61.908 | -61.94 | 0.050354 | 61.528 | -61.8576 | 61.6287 | -61.6837 | -61.7065 | -61.6608 | -0.16022 | -0.009155 | 0.018311 | 0.29755 | -0.13733 | -0.10529 | 0.022889 | 0.054932 | -0.054932 | -0.10071 | 0 | 0.11902 | 0.14191 | 0.09613 | 0.19684 | 0.15106 | 0.45776 | 123.6099 | 0.17395 | 123.4863 | 123.5825 | 123.3856 | 123.4222 | 123.3307 | -123.5916 | -123.4863 | 123.4497 | 123.4314 | 61.7798 | 61.853
333.375 | 123.6694 | -61.8027 | 61.5875 | 0.0055694 | 0.0030313 | 0.069353 | 0.068434 | 0.0049709 | -0.0025166 | -0.00060235 | 0.0018005 | 0.0050137 | 0.06806 | 0.063664 | -0.0013714 | 0.013514 | -0.0010788 | -0.10986 | 61.702 | -61.9629 | 61.5738 | -61.5875 | -61.9858 | -62.0041 | -0.027466 | 61.5417 | -61.8576 | 61.615 | -61.734 | -61.7615 | -61.6745 | -0.16022 | 0.11444 | -0.013732 | 0.21515 | -0.20142 | -0.18311 | -0.041198 | -0.022888 | -0.054932 | -0.045776 | 0.027466 | 0.068664 | 0.12817 | 0.041198 | 0.1831 | 0.09613 | 0.37537 | 123.5367 | 0.1236 | 123.4726 | 123.6649 | 123.3994 | 123.5046 | 123.3444 | -123.5504 | -123.4451 | 123.3765 | 123.4177 | 61.6928 | 61.7752
335.0781 | 123.5367 | -61.8393 | 61.6653 | -0.0096891 | 0.0040995 | 0.071062 | 0.066298 | 0.0026211 | -0.0035846 | 0.0015338 | 0.0018005 | 0.0037319 | 0.071051 | 0.0611 | -0.002226 | 0.014795 | -0.0002244 | -0.09613 | 61.7294 | -61.9629 | 61.528 | -61.647 | -62.0316 | -62.0453 | -0.11902 | 61.5875 | -61.8393 | 61.5372 | -61.821 | -61.8393 | -61.7477 | -0.1236 | 0.064087 | -0.13733 | 0.19226 | -0.20599 | -0.19226 | -0.082397 | -0.068664 | 0 | -0.07782 | -0.12817 | 0.01831 | 0.091552 | 0 | 0.091552 | 0 | 0.31586 | 123.4909 | 0.01831 | 123.3765 | 123.6923 | 123.4268 | 123.5687 | 123.4268 | -123.6282 | -123.5046 | 123.3673 | 123.3765 | 61.7432 | 61.7203
336.8125 | 123.6008 | -61.7935 | 61.6974 | 0.028458 | 0.0058083 | 0.069353 | 0.067793 | -0.00058326 | -0.0031574 | 0.0026018 | 0.010956 | 0.0075771 | 0.069983 | 0.058751 | -0.0045758 | 0.014582 | -0.0010788 | -0.036621 | 61.7157 | -61.9949 | 61.5692 | -61.5829 | -61.94 | -61.9858 | -0.018311 | 61.6379 | -61.8484 | 61.5692 | -61.734 | -61.7661 | -61.702 | -0.20142 | 0.01831 | -0.12817 | 0.21057 | -0.19226 | -0.14648 | 0.009155 | 0.054932 | -0.054932 | -0.05951 | -0.12817 | 0.059509 | 0.091553 | 0.027466 | 0.14648 | 0.082398 | 0.41199 | 123.5641 | 0.11444 | 123.4177 | 123.7106 | 123.4863 | 123.5092 | 123.4314 | -123.6923 | -123.5458 | 123.3627 | 123.3627 | 61.7569 | 61.7752
338.5781 | 123.6374 | -61.8027 | 61.5967 | -0.0020601 | 0.0049539 | 0.068925 | 0.063307 | 5.774e-05 | -0.003371 | -0.0020978 | -0.0043029 | 0.0065091 | 0.071265 | 0.060032 | -0.00094423 | 0.013727 | -0.0055648 | -0.1236 | 61.7111 | -61.9858 | 61.5417 | -61.5921 | -62.0224 | -62.0361 | -0.068665 | 61.5555 | -61.8713 | 61.5875 | -61.7386 | -61.7661 | -61.6928 | -0.18311 | 0.11444 | -0.054932 | 0.21057 | -0.23346 | -0.21973 | -0.050354 | -0.036621 | -0.068665 | -0.041199 | -0.009156 | 0.064087 | 0.10986 | 0.036621 | 0.17853 | 0.10529 | 0.39368 | 123.5275 | 0.13275 | 123.4589 | 123.6969 | 123.4268 | 123.5138 | 123.3582 | -123.5825 | -123.468 | 123.3444 | 123.3902 | 61.6791 | 61.734
340.2656 | 123.6649 | -61.8118 | 61.5784 | -0.017319 | 0.0049539 | 0.069994 | 0.064803 | 0.00069854 | -0.0037982 | -0.00060235 | 0.0018005 | 0.0056545 | 0.068915 | 0.064946 | -0.0043622 | 0.013514 | -0.0044968 | -0.064087 | 61.6013 | -61.9858 | 61.6287 | -61.4685 | -61.8759 | -61.8988 | 0.064087 | 61.528 | -61.853 | 61.6379 | -61.6608 | -61.6974 | -61.6745 | -0.17395 | 0.022888 | 0.050354 | 0.34332 | -0.086975 | -0.064087 | 0.086975 | 0.10986 | -0.041198 | -0.050354 | 0.059509 | 0.15106 | 0.13733 | 0.11444 | 0.17853 | 0.15564 | 0.51727 | 123.6145 | 0.19226 | 123.4909 | 123.587 | 123.381 | 123.4131 | 123.3398 | -123.5641 | -123.4314 | 123.4406 | 123.4497 | 61.7477 | 61.8759
342.0156 | 123.5779 | -61.8027 | 61.6699 | 0.043716 | 0.0049539 | 0.069139 | 0.068648 | 0.0030483 | -0.0010212 | 0.0028154 | 0.0079041 | 0.0054409 | 0.069769 | 0.055973 | -0.0037212 | 0.012873 | -0.0044968 | -0.018311 | 61.7477 | -62.0224 | 61.5509 | -61.5967 | -61.9583 | -61.972 | -0.018311 | 61.6196 | -61.853 | 61.5509 | -61.7249 | -61.7615 | -61.7111 | -0.21973 | 0.07782 | -0.11902 | 0.20599 | -0.16937 | -0.15564 | 0.050354 | 0.064087 | -0.050354 | -0.050354 | -0.11902 | 0.077819 | 0.091552 | 0.041198 | 0.14191 | 0.091552 | 0.42572 | 123.5733 | 0.12817 | 123.4039 | 123.7701 | 123.4726 | 123.5504 | 123.4222 | -123.6923 | -123.5229 | 123.3536 | 123.3536 | 61.7844 | 61.7844
343.7656 | 123.6649 | -61.8073 | 61.5875 | -0.0096891 | 0.0028177 | 0.069139 | 0.065657 | 0.0011257 | -0.0025166 | -0.0012434 | -0.0012513 | 0.0041593 | 0.069983 | 0.068364 | -0.003294 | 0.013941 | 0.00298 | -0.09613 | 61.615 | -61.9537 | 61.5967 | -61.5051 | -61.8988 | -61.94 | 0.022888 | 61.5189 | -61.8713 | 61.6333 | -61.6791 | -61.6974 | -61.6608 | -0.14648 | 0.027466 | 0.009156 | 0.30212 | -0.13275 | -0.091553 | 0.013733 | 0.054931 | -0.064087 | -0.068664 | 0.045777 | 0.12817 | 0.14648 | 0.10986 | 0.21057 | 0.17395 | 0.44861 | 123.5504 | 0.19226 | 123.5046 | 123.5687 | 123.3902 | 123.4222 | 123.3261 | -123.5413 | -123.4589 | 123.4039 | 123.4406 | 61.7111 | 61.8301
345.4531 | 123.5458 | -61.8118 | 61.6791 | -0.0020601 | 0.0043131 | 0.068498 | 0.066084 | 0.0019803 | -0.0044392 | -0.00017515 | -0.0012513 | 0.0039457 | 0.070624 | 0.06046 | -0.0037212 | 0.012232 | 0.0008438 | -0.064087 | 61.6699 | -61.9583 | 61.5372 | -61.5921 | -61.9675 | -61.9949 | -0.041199 | 61.5692 | -61.8484 | 61.5143 | -61.7752 | -61.7935 | -61.734 | -0.14648 | -0.009155 | -0.14191 | 0.21973 | -0.1831 | -0.15564 | -0.036621 | -0.009155 | -0.036621 | -0.10986 | -0.16479 | 0.036621 | 0.07782 | 0.018311 | 0.11444 | 0.054932 | 0.36621 | 123.4955 | 0.073242 | 123.3627 | 123.6282 | 123.4177 | 123.4818 | 123.381 | -123.6374 | -123.5275 | 123.349 | 123.3261 | 61.7477 | 61.7706
347.2031 | 123.5779 | -61.7661 | 61.6562 | 0.0055694 | 0.0064493 | 0.070634 | 0.066084 | 0.0083889 | -0.0035846 | 0.0011066 | 0.0048523 | 0.0080045 | 0.072546 | 0.058964 | -0.0011578 | 0.012873 | 0.0025528 | -0.013733 | 61.7157 | -61.9446 | 61.615 | -61.5234 | -61.908 | -61.9446 | 0.041199 | 61.5921 | -61.821 | 61.5784 | -61.7294 | -61.7661 | -61.6928 | -0.17853 | 0.059509 | -0.041199 | 0.24262 | -0.17853 | -0.14191 | 0 | 0.036621 | -0.054932 | -0.064087 | -0.07782 | 0.036621 | 0.073242 | 0 | 0.12817 | 0.054932 | 0.42114 | 123.5596 | 0.091553 | 123.3994 | 123.6603 | 123.4131 | 123.4818 | 123.3582 | -123.6008 | -123.4772 | 123.381 | 123.3444 | 61.7523 | 61.8073
348.9062 | 123.5092 | -61.8073 | 61.6562 | -0.0020601 | 0.0068765 | 0.070207 | 0.066298 | 0.0036893 | -0.0035846 | -0.001457 | -0.0012513 | 0.0069363 | 0.070624 | 0.067936 | -0.0011578 | 0.015009 | -0.0006516 | -0.09613 | 61.6837 | -61.9583 | 61.5051 | -61.6425 | -62.0132 | -62.0499 | -0.14191 | 61.5921 | -61.853 | 61.4731 | -61.8164 | -61.8301 | -61.7386 | -0.15106 | 0.027466 | -0.15106 | 0.16479 | -0.24262 | -0.20599 | -0.091553 | -0.054932 | -0.045776 | -0.064087 | -0.18311 | -0.009155 | 0.068665 | -0.022888 | 0.11444 | 0.022888 | 0.31586 | 123.4634 | 0.036621 | 123.3261 | 123.642 | 123.4451 | 123.4909 | 123.3994 | -123.6145 | -123.5092 | 123.3124 | 123.2803 | 61.7111 | 61.6653
350.6562 | 123.5275 | -61.7889 | 61.6608 | -0.0096891 | 0.0036721 | 0.068498 | 0.068221 | 0.0049709 | -0.0037982 | -0.0020978 | 0.0018005 | 0.0026639 | 0.069342 | 0.054692 | -0.002226 | 0.013086 | -0.003856 | -0.022888 | 61.7203 | -61.9446 | 61.5555 | -61.5646 | -61.9812 | -62.0041 | -0.018311 | 61.6104 | -61.8301 | 61.5189 | -61.7752 | -61.8027 | -61.734 | -0.15564 | 0.059509 | -0.10529 | 0.2243 | -0.21515 | -0.19226 | -0.059509 | -0.036621 | -0.041199 | -0.050354 | -0.14191 | 0.013732 | 0.054931 | -0.013733 | 0.09613 | 0.027466 | 0.37994 | 123.5001 | 0.054931 | 123.349 | 123.6649 | 123.4406 | 123.5092 | 123.3994 | -123.6053 | -123.4909 | 123.3444 | 123.3078 | 61.7661 | 61.7706
352.4062 | 123.5184 | -61.8027 | 61.6562 | 0.0055694 | 0.0036721 | 0.069994 | 0.066512 | 0.0030483 | -0.0023028 | 0.00089285 | -0.0043029 | 0.0058683 | 0.068488 | 0.062809 | 0.00076477 | 0.015009 | -0.0002244 | -0.068665 | 61.6837 | -61.9492 | 61.5051 | -61.6379 | -62.0224 | -62.0316 | -0.11902 | 61.5692 | -61.8439 | 61.4914 | -61.7981 | -61.8393 | -61.734 | -0.14648 | 0.027466 | -0.15106 | 0.16479 | -0.22888 | -0.21973 | -0.082397 | -0.073242 | -0.041199 | -0.086975 | -0.16479 | 0.004577 | 0.068664 | -0.036621 | 0.10986 | 0.004578 | 0.31128 | 123.4543 | 0.045776 | 123.3353 | 123.6328 | 123.4131 | 123.4863 | 123.3719 | -123.6053 | -123.5001 | 123.3078 | 123.2941 | 61.734 | 61.6837
354.1094 | 123.555 | -61.7844 | 61.6241 | -0.0020601 | 0.0040995 | 0.069353 | 0.066725 | 0.0045437 | -0.0052936 | 0.0023882 | -0.0043029 | 0.0052273 | 0.06806 | 0.060887 | -0.0013714 | 0.014368 | -0.0019332 | -0.11444 | 61.7065 | -61.9354 | 61.5234 | -61.6104 | -62.0178 | -62.0224 | -0.09613 | 61.5738 | -61.8484 | 61.5097 | -61.7889 | -61.8256 | -61.7249 | -0.15106 | 0.082397 | -0.10071 | 0.17395 | -0.23804 | -0.23346 | -0.086975 | -0.082397 | -0.064087 | -0.050354 | -0.11444 | -0.004577 | 0.059509 | -0.041199 | 0.1236 | 0.022888 | 0.32501 | 123.4589 | 0.05951 | 123.3582 | 123.642 | 123.4222 | 123.4909 | 123.3582 | -123.5596 | -123.4726 | 123.3078 | 123.2941 | 61.6699 | 61.6882
355.875 | 123.6465 | -61.7752 | 61.5784 | -0.0096891 | 0.0034585 | 0.068498 | 0.066512 | 0.0019803 | -0.00038018 | -0.0040204 | 0.0018005 | 0.0050137 | 0.069983 | 0.063023 | -0.0017986 | 0.014795 | 0.000203 | -0.10529 | 61.6653 | -61.9263 | 61.5646 | -61.5372 | -61.94 | -61.9675 | -0.013733 | 61.5189 | -61.8301 | 61.5875 | -61.702 | -61.7294 | -61.647 | -0.15106 | 0.086975 | -0.013733 | 0.23804 | -0.19226 | -0.16479 | -0.041198 | -0.013732 | -0.054931 | -0.059509 | 0.009155 | 0.073243 | 0.12817 | 0.045777 | 0.18311 | 0.10071 | 0.3891 | 123.4909 | 0.12817 | 123.4177 | 123.5916 | 123.349 | 123.4406 | 123.2941 | -123.5046 | -123.4085 | 123.3398 | 123.3627 | 61.6699 | 61.7615
357.6406 | 123.5458 | -61.7889 | 61.647 | 0.0055694 | 0.0055947 | 0.070848 | 0.067366 | 0.0043301 | -0.00059378 | -0.002525 | -0.0012513 | 0.0054409 | 0.068701 | 0.058537 | -0.0039348 | 0.01565 | -0.0019332 | -0.018311 | 61.6837 | -61.9263 | 61.5601 | -61.5463 | -61.9537 | -61.9858 | -0.009155 | 61.5921 | -61.8393 | 61.5143 | -61.7477 | -61.7844 | -61.7065 | -0.13733 | 0.036621 | -0.086975 | 0.24261 | -0.19684 | -0.1648 | -0.059509 | -0.027465 | -0.050354 | -0.054932 | -0.13275 | 0.041198 | 0.082397 | 0.004577 | 0.13275 | 0.054931 | 0.37994 | 123.4863 | 0.091552 | 123.3536 | 123.6099 | 123.4314 | 123.4726 | 123.381 | -123.5733 | -123.4863 | 123.349 | 123.3032 | 61.7706 | 61.7798
359.3906 | 123.5962 | -61.8301 | 61.5646 | 0.0055694 | 0.0038857 | 0.068071 | 0.064803 | -0.00058326 | -0.0027302 | 0.001961 | 0.0048523 | 0.0041593 | 0.071265 | 0.065373 | -0.0020122 | 0.015864 | 0.0006302 | -0.12817 | 61.6379 | -61.972 | 61.5417 | -61.5692 | -61.9446 | -61.9812 | -0.082397 | 61.5097 | -61.8805 | 61.4868 | -61.7477 | -61.7706 | -61.7111 | -0.14191 | 0.073242 | -0.022888 | 0.26093 | -0.15106 | -0.11444 | -0.009155 | 0.027466 | -0.050354 | -0.054931 | -0.07782 | 0.082397 | 0.11902 | 0.059509 | 0.16937 | 0.10986 | 0.40283 | 123.5138 | 0.13275 | 123.3673 | 123.6099 | 123.3902 | 123.468 | 123.3398 | -123.5367 | -123.4451 | 123.3719 | 123.317 | 61.702 | 61.7477
361.0781 | 123.5184 | -61.7889 | 61.6196 | -0.0020601 | 0.0023905 | 0.068925 | 0.067366 | -0.00058326 | -0.00080758 | 0.00025205 | 0.0048523 | 0.0060819 | 0.069769 | 0.055119 | -0.0013714 | 0.015223 | 0.0004166 | -0.10071 | 61.7065 | -61.9308 | 61.5097 | -61.6287 | -62.0224 | -62.0224 | -0.11444 | 61.5784 | -61.8301 | 61.4548 | -61.8073 | -61.8256 | -61.7249 | -0.14191 | 0.086975 | -0.10986 | 0.16022 | -0.23346 | -0.23346 | -0.091553 | -0.091553 | -0.041199 | -0.041199 | -0.16479 | -0.018311 | 0.064086 | -0.036622 | 0.10529 | 0.004577 | 0.30212 | 123.4406 | 0.022888 | 123.2849 | 123.6374 | 123.4085 | 123.4955 | 123.3673 | -123.5504 | -123.4497 | 123.2986 | 123.2437 | 61.6882 | 61.6745
362.8438 | 123.5321 | -61.7844 | 61.6333 | -0.0020601 | 0.0051675 | 0.071275 | 0.066298 | 0.0019803 | -0.00080758 | -0.003166 | -0.0012513 | 0.0058683 | 0.069983 | 0.062596 | -0.0028668 | 0.013514 | -0.0012924 | -0.018311 | 61.7157 | -61.9492 | 61.5738 | -61.5372 | -61.9537 | -61.9766 | -0.009155 | 61.5738 | -61.821 | 61.496 | -61.7523 | -61.7844 | -61.702 | -0.16479 | 0.082397 | -0.059509 | 0.24719 | -0.19226 | -0.16937 | -0.027466 | -0.004577 | -0.036621 | -0.059509 | -0.13733 | 0.032044 | 0.082398 | 0 | 0.11902 | 0.036621 | 0.41199 | 123.5229 | 0.068665 | 123.317 | 123.6649 | 123.3948 | 123.5001 | 123.3582 | -123.5825 | -123.4543 | 123.3582 | 123.2803 | 61.7661 | 61.7752
364.5938 | 123.5825 | -61.7935 | 61.6425 | 0.0055694 | 0.0043131 | 0.068712 | 0.064803 | -0.0018649 | -0.001662 | 0.00046565 | 0.0048523 | 0.0041593 | 0.068488 | 0.05811 | -0.0052166 | 0.013941 | 0.0016982 | -0.032043 | 61.6379 | -61.9217 | 61.5967 | -61.4822 | -61.8668 | -61.9263 | 0.041199 | 61.5143 | -61.8027 | 61.5326 | -61.6791 | -61.7065 | -61.6791 | -0.12817 | -0.004578 | -0.045776 | 0.31128 | -0.13275 | -0.073242 | -0.004578 | 0.054932 | -0.009155 | -0.12817 | -0.10986 | 0.11444 | 0.11444 | 0.086975 | 0.1236 | 0.09613 | 0.43945 | 123.5184 | 0.1236 | 123.3353 | 123.5596 | 123.317 | 123.4314 | 123.3078 | -123.5641 | -123.4451 | 123.3902 | 123.3261 | 61.7615 | 61.8347
366.2656 | 123.5184 | -61.8027 | 61.6425 | -0.0096891 | 0.0051675 | 0.069353 | 0.067366 | 0.0028347 | -0.0020892 | -0.00017515 | 0.0018005 | 0.0062955 | 0.071265 | 0.053837 | -0.0013714 | 0.015436 | -0.0002244 | -0.10529 | 61.6928 | -61.9675 | 61.4731 | -61.6379 | -62.0178 | -62.0224 | -0.10071 | 61.5601 | -61.8484 | 61.4777 | -61.8073 | -61.8256 | -61.7111 | -0.16479 | 0.050354 | -0.16937 | 0.16479 | -0.21973 | -0.21515 | -0.054932 | -0.050354 | -0.045777 | -0.082397 | -0.1648 | -0.004578 | 0.091552 | -0.022889 | 0.13733 | 0.022888 | 0.32959 | 123.4406 | 0.041199 | 123.3261 | 123.6603 | 123.4085 | 123.4955 | 123.3627 | -123.6099 | -123.4909 | 123.2758 | 123.2803 | 61.6974 | 61.702
368.0156 | 123.5504 | -61.7706 | 61.6837 | 0.028458 | 0.0062357 | 0.069566 | 0.06523 | 0.0011257 | -0.0012348 | 0.0015338 | 0.017059 | 0.0045865 | 0.07041 | 0.055119 | -0.0030804 | 0.011805 | -0.0025742 | -0.032043 | 61.7157 | -61.9812 | 61.5463 | -61.5601 | -61.9034 | -61.9492 | -0.013733 | 61.6379 | -61.8301 | 61.5005 | -61.7111 | -61.7294 | -61.6699 | -0.21057 | 0.032043 | -0.13733 | 0.21057 | -0.17853 | -0.13275 | 0.032043 | 0.07782 | -0.059509 | -0.045777 | -0.18311 | 0.059509 | 0.10071 | 0.041199 | 0.16022 | 0.10071 | 0.42114 | 123.5275 | 0.11902 | 123.3307 | 123.6969 | 123.468 | 123.4863 | 123.4085 | -123.6649 | -123.5138 | 123.317 | 123.2712 | 61.7386 | 61.7569
369.7031 | 123.6237 | -61.7844 | 61.6058 | 0.0055694 | 0.0028177 | 0.069353 | 0.062453 | -0.00058326 | -0.0031574 | -0.00017515 | -0.0043029 | 0.0018093 | 0.06806 | 0.057896 | -0.0030804 | 0.015436 | -0.0064194 | -0.045776 | 61.5875 | -61.9354 | 61.5967 | -61.4594 | -61.8622 | -61.9034 | 0.045776 | 61.528 | -61.8393 | 61.5509 | -61.647 | -61.6745 | -61.6425 | -0.15106 | -0.018311 | -0.009155 | 0.32501 | -0.11902 | -0.07782 | 0.032044 | 0.073242 | -0.054931 | -0.07782 | -0.054932 | 0.13733 | 0.14191 | 0.10986 | 0.19684 | 0.16479 | 0.47607 | 123.5321 | 0.19226 | 123.3902 | 123.5229 | 123.3673 | 123.3719 | 123.3124 | -123.5413 | -123.4451 | 123.381 | 123.3353 | 61.7386 | 61.8301
371.4531 | 123.5687 | -61.7889 | 61.6333 | 0.0055694 | 0.0049539 | 0.068925 | 0.063094 | 0.0047573 | -0.0031574 | 3.8448e-05 | -0.0012513 | 0.0030911 | 0.068274 | 0.066014 | -0.0026532 | 0.010737 | -0.0008652 | -0.013733 | 61.6241 | -61.9354 | 61.6013 | -61.4822 | -61.8713 | -61.9125 | 0.027466 | 61.5372 | -61.7935 | 61.5234 | -61.6928 | -61.7157 | -61.6837 | -0.14649 | -0.009155 | -0.032044 | 0.3067 | -0.1236 | -0.082398 | 0.022888 | 0.064087 | -0.004578 | -0.096131 | -0.10986 | 0.09613 | 0.10528 | 0.073242 | 0.10986 | 0.07782 | 0.45319 | 123.5367 | 0.10071 | 123.317 | 123.5596 | 123.3307 | 123.4131 | 123.3261 | -123.5687 | -123.4268 | 123.3902 | 123.3124 | 61.7752 | 61.8164
373.1562 | 123.5413 | -61.7569 | 61.647 | 0.0055694 | 0.0060221 | 0.06978 | 0.065871 | 0.0024075 | -0.0020892 | -0.0016706 | 0.0079041 | 0.0037319 | 0.070624 | 0.059391 | -0.00030343 | 0.013727 | -0.001506 | 0.004578 | 61.6974 | -61.94 | 61.5967 | -61.496 | -61.8896 | -61.9263 | 0.036621 | 61.5921 | -61.8164 | 61.5326 | -61.7065 | -61.7432 | -61.6745 | -0.1831 | 0.050354 | -0.050354 | 0.26093 | -0.16937 | -0.13275 | 0.013732 | 0.050354 | -0.059509 | -0.054932 | -0.11444 | 0.050354 | 0.082397 | 0.013733 | 0.14191 | 0.073242 | 0.44403 | 123.5367 | 0.10986 | 123.349 | 123.6374 | 123.4085 | 123.4543 | 123.349 | -123.587 | -123.4634 | 123.3536 | 123.2895 | 61.7615 | 61.7935
374.9062 | 123.5413 | -61.7889 | 61.6333 | -0.0096891 | 0.0043131 | 0.068925 | 0.064162 | -0.00036966 | -0.0031574 | -0.00081595 | -0.0043029 | 0.0028775 | 0.069128 | 0.060673 | -0.003294 | 0.012446 | -0.0006516 | -0.022888 | 61.6333 | -61.9354 | 61.5692 | -61.4914 | -61.8713 | -61.9263 | -0.004578 | 61.5555 | -61.8164 | 61.4731 | -61.7203 | -61.7386 | -61.702 | -0.14649 | 0 | -0.064087 | 0.29755 | -0.13733 | -0.082398 | 0.009155 | 0.064087 | -0.027466 | -0.07782 | -0.16022 | 0.068664 | 0.086975 | 0.050354 | 0.11444 | 0.07782 | 0.44403 | 123.5046 | 0.09613 | 123.2895 | 123.5687 | 123.3719 | 123.4222 | 123.3444 | -123.5687 | -123.4497 | 123.3582 | 123.262 | 61.7661 | 61.7844
376.5938 | 123.5321 | -61.7798 | 61.6241 | 0.013199 | 0.0077311 | 0.071275 | 0.065657 | 0.00069854 | -0.003371 | -0.00038875 | 0.0048523 | 0.0056545 | 0.067847 | 0.057042 | -0.0013714 | 0.013941 | -0.0019332 | 0.004578 | 61.6974 | -61.9125 | 61.5784 | -61.4868 | -61.8896 | -61.9537 | 0.027466 | 61.5738 | -61.8027 | 61.5189 | -61.6882 | -61.7294 | -61.6516 | -0.13275 | 0.073242 | -0.045777 | 0.29297 | -0.17395 | -0.10986 | -0.041198 | 0.022889 | -0.022888 | -0.050354 | -0.10529 | 0.091553 | 0.12817 | 0.050354 | 0.15106 | 0.073242 | 0.42572 | 123.4909 | 0.11444 | 123.3215 | 123.6099 | 123.3765 | 123.4772 | 123.3536 | -123.5367 | -123.4268 | 123.3582 | 123.2986 | 61.7844 | 61.8073
378.3438 | 123.5458 | -61.7523 | 61.6425 | 0.036087 | 0.0038857 | 0.069566 | 0.065871 | 0.0041165 | -0.0014484 | 0.00067925 | 0.010956 | 0.0062955 | 0.069556 | 0.0658 | -0.003294 | 0.014582 | -0.0010788 | 0.004578 | 61.7477 | -61.9263 | 61.5784 | -61.5372 | -61.8805 | -61.94 | 0 | 61.5921 | -61.8301 | 61.5097 | -61.6974 | -61.734 | -61.647 | -0.17395 | 0.10529 | -0.064087 | 0.21515 | -0.18768 | -0.12817 | -0.013732 | 0.045777 | -0.07782 | -0.050354 | -0.13275 | 0.054931 | 0.10529 | 0.01831 | 0.18311 | 0.09613 | 0.3891 | 123.5046 | 0.13275 | 123.3398 | 123.674 | 123.4222 | 123.5001 | 123.3444 | -123.5687 | -123.4726 | 123.3307 | 123.262 | 61.7569 | 61.7523
380.0938 | 123.5229 | -61.7752 | 61.6516 | -0.0020601 | 0.0047403 | 0.068712 | 0.067793 | -0.00036966 | -0.001662 | -0.0020978 | 0.0018005 | 0.0037319 | 0.067847 | 0.062809 | -0.0017986 | 0.013086 | -0.0017196 | -0.10529 | 61.702 | -61.9171 | 61.4731 | -61.615 | -62.0087 | -62.0178 | -0.10529 | 61.5738 | -61.8439 | 61.4731 | -61.7752 | -61.7935 | -61.7294 | -0.14191 | 0.050354 | -0.17853 | 0.16022 | -0.24261 | -0.23346 | -0.10071 | -0.091553 | -0.068664 | -0.077819 | -0.17853 | 0 | 0.045777 | -0.01831 | 0.11444 | 0.050354 | 0.30212 | 123.3902 | 0.068664 | 123.317 | 123.6191 | 123.4177 | 123.4772 | 123.349 | -123.5687 | -123.4955 | 123.2483 | 123.2483 | 61.6699 | 61.6699
381.8438 | 123.6053 | -61.8027 | 61.5921 | 0.020828 | 0.0049539 | 0.070634 | 0.064162 | 0.0017667 | -0.0010212 | 0.001961 | -0.0012513 | 0.0022367 | 0.069342 | 0.069645 | -0.0013714 | 0.014368 | -0.0055648 | -0.1236 | 61.6058 | -61.9492 | 61.5372 | -61.5509 | -61.9537 | -61.9675 | -0.059509 | 61.4822 | -61.8576 | 61.5005 | -61.7203 | -61.7203 | -61.6837 | -0.14648 | 0.013733 | -0.054932 | 0.25177 | -0.16479 | -0.15106 | -0.01831 | -0.004577 | -0.054932 | -0.10986 | -0.091553 | 0.082397 | 0.11902 | 0.082397 | 0.17395 | 0.13733 | 0.39825 | 123.4863 | 0.13733 | 123.3582 | 123.555 | 123.3398 | 123.4085 | 123.2849 | -123.5413 | -123.4497 | 123.3398 | 123.3032 | 61.6791 | 61.7432
383.5156 | 123.4909 | -61.7615 | 61.6425 | 0.013199 | 0.0036721 | 0.068712 | 0.065443 | 0.00091214 | -0.0037982 | 0.00089285 | 0.0018005 | 0.0045865 | 0.068488 | 0.061741 | -0.0017986 | 0.015436 | 0.0008438 | -0.018311 | 61.6837 | -61.9217 | 61.5509 | -61.5189 | -61.9492 | -61.972 | -0.013733 | 61.5829 | -61.8164 | 61.496 | -61.7294 | -61.7661 | -61.6882 | -0.16022 | 0.041199 | -0.091553 | 0.24262 | -0.21057 | -0.18768 | -0.050354 | -0.027466 | -0.054931 | -0.059509 | -0.14648 | 0.032044 | 0.073243 | -0.004577 | 0.12817 | 0.050354 | 0.40283 | 123.4726 | 0.086975 | 123.3124 | 123.6053 | 123.3994 | 123.4451 | 123.3444 | -123.5641 | -123.4589 | 123.3124 | 123.2574 | 61.7432 | 61.7477
385.2656 | 123.4909 | -61.7752 | 61.6653 | -0.0096891 | 0.00068151 | 0.068925 | 0.06523 | -0.00058326 | -0.0029438 | 0.00067925 | -0.0043029 | 0.0069363 | 0.068701 | 0.059391 | -0.0028668 | 0.015864 | -0.0025742 | -0.027466 | 61.6562 | -61.9263 | 61.528 | -61.5372 | -61.8988 | -61.9583 | -0.045776 | 61.5555 | -61.8301 | 61.4731 | -61.7294 | -61.7615 | -61.7157 | -0.15106 | -0.009155 | -0.13733 | 0.23804 | -0.1831 | -0.1236 | -0.032043 | 0.027466 | -0.054931 | -0.10986 | -0.19226 | 0.045777 | 0.05951 | 0.013733 | 0.11444 | 0.068664 | 0.3891 | 123.4543 | 0.10071 | 123.3032 | 123.5825 | 123.3856 | 123.4314 | 123.3307 | -123.5916 | -123.4955 | 123.3032 | 123.2483 | 61.7477 | 61.7294
387 | 123.5046 | -61.7889 | 61.615 | -0.0096891 | 0.0047403 | 0.066362 | 0.063521 | -0.0029331 | -0.0037982 | -0.0033796 | 0.020111 | 0.0067227 | 0.070624 | 0.055546 | -0.0058576 | 0.012446 | 0.00298 | -0.082397 | 61.6653 | -61.9217 | 61.496 | -61.5646 | -61.94 | -61.9583 | -0.036621 | 61.6104 | -61.8668 | 61.4639 | -61.7477 | -61.7615 | -61.6928 | -0.13275 | 0.050354 | -0.11902 | 0.2243 | -0.16937 | -0.15106 | -0.036621 | -0.01831 | -0.07782 | -0.004577 | -0.15106 | 0.041198 | 0.09613 | 0.027465 | 0.17395 | 0.10529 | 0.35706 | 123.4177 | 0.11902 | 123.3307 | 123.587 | 123.4772 | 123.4543 | 123.3994 | -123.5367 | -123.4818 | 123.2849 | 123.2529 | 61.7065 | 61.7523
388.6719 | 123.5458 | -61.7523 | 61.647 | 0.020828 | 0.0051675 | 0.067857 | 0.067152 | 0.0026211 | -0.0027302 | 0.00367 | 0.010956 | 0.0054409 | 0.068915 | 0.057896 | -0.0026532 | 0.014795 | -0.0006516 | -0.009155 | 61.7111 | -61.9492 | 61.5509 | -61.5372 | -61.8896 | -61.9217 | -0.013733 | 61.6196 | -61.8164 | 61.496 | -61.6791 | -61.7294 | -61.6562 | -0.19684 | 0.064087 | -0.096131 | 0.21515 | -0.16937 | -0.13733 | 0.027466 | 0.05951 | -0.064087 | -0.027466 | -0.15106 | 0.073242 | 0.09613 | 0.022888 | 0.16022 | 0.086975 | 0.41199 | 123.5001 | 0.13733 | 123.3124 | 123.6603 | 123.436 | 123.4634 | 123.3719 | -123.5962 | -123.4634 | 123.3032 | 123.2483 | 61.7432 | 61.7386
390.4219 | 123.6191 | -61.7798 | 61.5646 | -0.0020601 | 0.0034585 | 0.069139 | 0.063094 | -0.0025059 | -0.0042254 | -0.0020978 | -0.0012513 | 0.0026639 | 0.068488 | 0.061314 | 0.00076477 | 0.013941 | -0.0012924 | -0.10529 | 61.6196 | -61.9217 | 61.5372 | -61.5189 | -61.8851 | -61.9217 | -0.009155 | 61.4868 | -61.8393 | 61.5417 | -61.6608 | -61.647 | -61.6196 | -0.14191 | 0.054932 | -0.027466 | 0.26093 | -0.14191 | -0.10529 | 0 | 0.036621 | -0.059509 | -0.07782 | -0.022888 | 0.11902 | 0.16022 | 0.13275 | 0.21973 | 0.19226 | 0.40283 | 123.4589 | 0.17853 | 123.381 | 123.5413 | 123.3261 | 123.3994 | 123.2666 | -123.4863 | -123.4039 | 123.317 | 123.3215 | 61.6745 | 61.7706
392.1094 | 123.5046 | -61.8118 | 61.5967 | 0.0055694 | 0.0049539 | 0.067644 | 0.063521 | -0.00015586 | -0.0025166 | -0.0023114 | -0.0012513 | 0.0037319 | 0.07041 | 0.058751 | -0.003294 | 0.012446 | -0.0025742 | -0.022888 | 61.6653 | -61.9125 | 61.5601 | -61.496 | -61.8668 | -61.9125 | 0.018311 | 61.5463 | -61.7981 | 61.4914 | -61.702 | -61.7294 | -61.6882 | -0.10071 | 0.068664 | -0.036621 | 0.31586 | -0.10071 | -0.054931 | 0 | 0.045777 | 0.013733 | -0.050354 | -0.10529 | 0.10986 | 0.1236 | 0.082398 | 0.10986 | 0.068665 | 0.41656 | 123.4726 | 0.096131 | 123.2895 | 123.5779 | 123.3444 | 123.4772 | 123.3582 | -123.5092 | -123.3948 | 123.3719 | 123.3032 | 61.7889 | 61.8301
393.8594 | 123.5916 | -61.7935 | 61.5738 | -0.0020601 | 0.0043131 | 0.070848 | 0.064803 | -0.0016513 | -0.0020892 | -0.00081595 | -0.0012513 | 0.0035183 | 0.065924 | 0.066655 | -0.00094423 | 0.014155 | 0.001271 | -0.11902 | 61.5921 | -61.9446 | 61.5189 | -61.5509 | -61.9217 | -61.9583 | -0.059509 | 61.5005 | -61.8347 | 61.5097 | -61.702 | -61.702 | -61.6745 | -0.15106 | 0.01831 | -0.054932 | 0.24262 | -0.16479 | -0.12817 | -0.013733 | 0.022888 | -0.041199 | -0.073243 | -0.064087 | 0.091553 | 0.11902 | 0.091553 | 0.16022 | 0.13275 | 0.39368 | 123.4634 | 0.13275 | 123.3444 | 123.5367 | 123.3353 | 123.3856 | 123.2941 | -123.5184 | -123.4085 | 123.3124 | 123.3032 | 61.6745 | 61.734
395.5469 | 123.4726 | -61.7661 | 61.647 | -0.0020601 | 0.0043131 | 0.068712 | 0.067152 | 0.0011257 | -0.0037982 | 3.8448e-05 | -0.0043029 | 0.0060819 | 0.068488 | 0.060887 | -0.0013714 | 0.014368 | -0.0017196 | -0.07782 | 61.6791 | -61.908 | 61.4868 | -61.615 | -62.0041 | -62.027 | -0.13275 | 61.5921 | -61.8164 | 61.4548 | -61.7706 | -61.7798 | -61.6928 | -0.14191 | 0.032043 | -0.16022 | 0.15106 | -0.26093 | -0.23804 | -0.11902 | -0.09613 | -0.050354 | -0.054932 | -0.19226 | -0.004578 | 0.073242 | -0.013733 | 0.1236 | 0.036621 | 0.29297 | 123.3948 | 0.045776 | 123.2712 | 123.587 | 123.4085 | 123.4451 | 123.3582 | -123.555 | -123.4634 | 123.2529 | 123.2208 | 61.6882 | 61.6333
397.2969 | 123.555 | -61.7798 | 61.5967 | -0.0096891 | 0.0047403 | 0.068712 | 0.065443 | -0.0035739 | -0.0031574 | 0.0017474 | -0.0012513 | 0.0033047 | 0.068915 | 0.063237 | -0.002226 | 0.016291 | -0.0036422 | -0.022888 | 61.5967 | -61.9354 | 61.5875 | -61.4594 | -61.8393 | -61.9034 | 0.050354 | 61.5189 | -61.8073 | 61.5051 | -61.6699 | -61.6837 | -61.6333 | -0.15564 | 0 | -0.009156 | 0.32043 | -0.1236 | -0.059509 | 0.032044 | 0.096131 | -0.027466 | -0.07782 | -0.091553 | 0.10986 | 0.14648 | 0.09613 | 0.17395 | 0.1236 | 0.47607 | 123.5229 | 0.13733 | 123.3124 | 123.5321 | 123.3261 | 123.3765 | 123.2986 | -123.5321 | -123.4039 | 123.3673 | 123.2849 | 61.7569 | 61.8301
399.0469 | 123.4726 | -61.7477 | 61.647 | 0.051346 | 0.0062357 | 0.069353 | 0.066512 | -0.00015586 | -0.003371 | -0.00038875 | 0.010956 | 0.0056545 | 0.07041 | 0.068364 | -0.0039348 | 0.0133 | -0.0006516 | -0.018311 | 61.6928 | -61.9492 | 61.5005 | -61.5509 | -61.9308 | -61.9446 | -0.036621 | 61.5875 | -61.8347 | 61.4822 | -61.7249 | -61.7523 | -61.6699 | -0.20142 | 0.045776 | -0.14648 | 0.19684 | -0.19684 | -0.1831 | 0.004578 | 0.018311 | -0.086975 | -0.05951 | -0.16479 | 0.022888 | 0.07782 | -0.004577 | 0.16479 | 0.082398 | 0.39825 | 123.4497 | 0.10986 | 123.317 | 123.642 | 123.4222 | 123.4406 | 123.3353 | -123.5962 | -123.4818 | 123.2483 | 123.23 | 61.7294 | 61.7111
400.7969 | 123.468 | -61.7798 | 61.6013 | 0.0055694 | 0.0070901 | 0.070634 | 0.065443 | -0.00036966 | -0.0035846 | -0.0012434 | -0.0073547 | 0.0041593 | 0.069769 | 0.058323 | -0.0017986 | 0.01565 | -0.0055648 | -0.068665 | 61.6974 | -61.8851 | 61.4914 | -61.6013 | -61.9904 | -62.0224 | -0.1236 | 61.5829 | -61.8576 | 61.4365 | -61.7844 | -61.8164 | -61.7111 | -0.10529 | 0.096131 | -0.10986 | 0.17853 | -0.24262 | -0.21057 | -0.13733 | -0.10528 | -0.07782 | -0.01831 | -0.16479 | -0.004578 | 0.068664 | -0.036621 | 0.14648 | 0.041199 | 0.28381 | 123.3765 | 0.073242 | 123.2941 | 123.5825 | 123.4406 | 123.4772 | 123.3627 | -123.4863 | -123.4589 | 123.2712 | 123.2162 | 61.7111 | 61.6562
402.4844 | 123.5962 | -61.7569 | 61.5875 | 0.0055694 | 0.0023905 | 0.069353 | 0.062239 | 0.00048494 | -0.007857 | 3.8448e-05 | -0.0043029 | 0.0039457 | 0.068488 | 0.064091 | -0.0035076 | 0.016718 | 0.0025528 | -0.032043 | 61.5875 | -61.8942 | 61.5921 | -61.4365 | -61.8484 | -61.8942 | 0.050354 | 61.4868 | -61.8301 | 61.5601 | -61.6425 | -61.6516 | -61.6287 | -0.13733 | 0 | 0.004578 | 0.32044 | -0.13733 | -0.091553 | 0 | 0.045776 | -0.073242 | -0.10071 | -0.027465 | 0.11444 | 0.12817 | 0.10529 | 0.20142 | 0.17853 | 0.45776 | 123.4863 | 0.18768 | 123.3902 | 123.4818 | 123.317 | 123.3444 | 123.2437 | -123.4818 | -123.4177 | 123.349 | 123.317 | 61.7249 | 61.8073
404.2344 | 123.4772 | -61.7752 | 61.6241 | -0.0020601 | 0.0053811 | 0.069994 | 0.067793 | 0.0011257 | -0.00080758 | 3.8448e-05 | -0.0012513 | 0.0039457 | 0.069556 | 0.056828 | -0.0028668 | 0.014795 | -0.0027878 | -0.073242 | 61.6928 | -61.8988 | 61.4731 | -61.6058 | -61.9949 | -62.0178 | -0.12817 | 61.5509 | -61.7981 | 61.4685 | -61.7661 | -61.7844 | -61.6882 | -0.1236 | 0.068664 | -0.15106 | 0.16937 | -0.24261 | -0.21973 | -0.11902 | -0.09613 | -0.022888 | -0.073243 | -0.15564 | 0.009156 | 0.086976 | -0.009155 | 0.10986 | 0.013733 | 0.29297 | 123.3719 | 0.032044 | 123.2666 | 123.5916 | 123.349 | 123.468 | 123.3261 | -123.523 | -123.4222 | 123.2483 | 123.2437 | 61.702 | 61.647
405.9844 | 123.5596 | -61.7386 | 61.5601 | -0.017319 | 0.0030313 | 0.069994 | 0.065871 | 0.0017667 | -0.003371 | -0.00060235 | -0.010406 | 0.0050137 | 0.067847 | 0.061528 | 0.00055117 | 0.016504 | -0.0036422 | -0.10986 | 61.6425 | -61.9125 | 61.5143 | -61.528 | -61.9492 | -61.9537 | -0.027466 | 61.496 | -61.7981 | 61.5372 | -61.6928 | -61.6974 | -61.615 | -0.17395 | 0.082397 | -0.045777 | 0.21057 | -0.21515 | -0.21057 | -0.041198 | -0.036621 | -0.05951 | -0.064087 | -0.022889 | 0.045776 | 0.1236 | 0.041198 | 0.18311 | 0.10071 | 0.38452 | 123.4268 | 0.10529 | 123.3353 | 123.555 | 123.2941 | 123.381 | 123.2346 | -123.4726 | -123.3582 | 123.2529 | 123.2758 | 61.6287 | 61.7111
407.6719 | 123.5916 | -61.7615 | 61.5097 | -0.017319 | 0.0051675 | 0.069139 | 0.064162 | 0.0017667 | -0.0040118 | -0.002525 | -0.0043029 | 0.0035183 | 0.071905 | 0.066014 | -8.9634e-05 | 0.018427 | -0.002147 | -0.068665 | 61.5967 | -61.8942 | 61.5784 | -61.4548 | -61.8896 | -61.9125 | 0.013733 | 61.4777 | -61.8027 | 61.5738 | -61.6562 | -61.6745 | -61.6196 | -0.13275 | 0.086975 | 0.068664 | 0.3067 | -0.15106 | -0.12817 | -0.018311 | 0.004578 | -0.041198 | -0.032044 | 0.064087 | 0.10529 | 0.14191 | 0.086975 | 0.1831 | 0.12817 | 0.43945 | 123.4726 | 0.14648 | 123.3765 | 123.4909 | 123.2803 | 123.3582 | 123.2391 | -123.4039 | -123.3124 | 123.3398 | 123.3353 | 61.6928 | 61.7752
409.4219 | 123.5916 | -61.7569 | 61.5646 | -0.0096891 | 0.0040995 | 0.070848 | 0.063307 | 0.00027134 | -0.0023028 | 0.00067925 | 0.014008 | 0.0060819 | 0.069983 | 0.065159 | -0.00030343 | 0.016932 | -0.0047104 | -0.059509 | 61.5921 | -61.9171 | 61.5784 | -61.4777 | -61.8622 | -61.8851 | 0.041199 | 61.5005 | -61.8301 | 61.5646 | -61.6333 | -61.6699 | -61.6287 | -0.16022 | 0.027466 | 0.013733 | 0.27924 | -0.12817 | -0.10529 | 0.032043 | 0.054931 | -0.073242 | -0.064087 | 0 | 0.1236 | 0.12817 | 0.086975 | 0.20142 | 0.16022 | 0.43945 | 123.4955 | 0.19684 | 123.3948 | 123.5092 | 123.3307 | 123.349 | 123.2574 | -123.4818 | -123.3948 | 123.3353 | 123.3215 | 61.6974 | 61.7981
411.1719 | 123.5184 | -61.734 | 61.6379 | 0.020828 | 0.0045267 | 0.070634 | 0.066084 | 0.0034755 | -0.0023028 | -0.0038068 | 0.0079041 | 0.0060819 | 0.067419 | 0.061314 | -0.0011578 | 0.016077 | -0.0002244 | -0.004578 | 61.6928 | -61.908 | 61.5784 | -61.4639 | -61.8622 | -61.8988 | 0.050354 | 61.5967 | -61.7981 | 61.5326 | -61.6608 | -61.6928 | -61.6196 | -0.17395 | 0.054932 | -0.059509 | 0.27008 | -0.16479 | -0.12817 | 0.009155 | 0.045776 | -0.064087 | -0.041198 | -0.10529 | 0.073242 | 0.11444 | 0.041199 | 0.17853 | 0.10529 | 0.44403 | 123.4863 | 0.13733 | 123.3307 | 123.6008 | 123.3948 | 123.4268 | 123.3307 | -123.5458 | -123.436 | 123.3124 | 123.2666 | 61.7294 | 61.7844
412.9062 | 123.468 | -61.7798 | 61.6058 | -0.0020601 | 0.0026041 | 0.070848 | 0.065871 | 0.0028347 | -0.0029438 | 3.8448e-05 | -0.0012513 | 0.0060819 | 0.068488 | 0.064732 | -0.00094423 | 0.016077 | -0.0002244 | -0.09613 | 61.6516 | -61.908 | 61.4548 | -61.5738 | -61.9766 | -61.9949 | -0.1236 | 61.5555 | -61.8256 | 61.4594 | -61.7661 | -61.7935 | -61.6928 | -0.12817 | 0.045776 | -0.15106 | 0.20599 | -0.21515 | -0.19684 | -0.086975 | -0.068665 | -0.045777 | -0.050354 | -0.14648 | 0.013733 | 0.086975 | -0.013733 | 0.13275 | 0.032044 | 0.33417 | 123.3627 | 0.05951 | 123.2849 | 123.5596 | 123.381 | 123.4314 | 123.3353 | -123.5138 | -123.4314 | 123.2346 | 123.2391 | 61.6837 | 61.6562
414.5781 | 123.5458 | -61.7706 | 61.5738 | 0.013199 | 0.0038857 | 0.070848 | 0.065657 | 0.0021939 | -0.0029438 | -0.0010298 | -0.0043029 | 0.0026639 | 0.068915 | 0.064732 | -0.002226 | 0.016077 | -0.0023606 | -0.11902 | 61.6196 | -61.9446 | 61.496 | -61.528 | -61.9217 | -61.9446 | -0.07782 | 61.5097 | -61.7844 | 61.5005 | -61.6837 | -61.702 | -61.6608 | -0.17395 | 0.045776 | -0.07782 | 0.24261 | -0.17395 | -0.15106 | 0 | 0.022888 | -0.013733 | -0.064087 | -0.073243 | 0.086975 | 0.10986 | 0.068665 | 0.1236 | 0.082398 | 0.41656 | 123.4406 | 0.10071 | 123.2849 | 123.5641 | 123.2941 | 123.3902 | 123.2803 | -123.5184 | -123.3582 | 123.2666 | 123.2712 | 61.6516 | 61.6928
416.3281 | 123.5916 | -61.7432 | 61.5555 | 0.0055694 | 0.0032449 | 0.067857 | 0.064803 | -0.0033603 | -0.0018756 | -0.0044476 | -0.0012513 | 0.0037319 | 0.069769 | 0.064946 | -0.0020122 | 0.014368 | -0.0064194 | -0.050354 | 61.6013 | -61.8942 | 61.6013 | -61.3907 | -61.7935 | -61.8484 | 0.050354 | 61.5005 | -61.8301 | 61.5646 | -61.6058 | -61.6241 | -61.6013 | -0.15106 | 0.045776 | 0.045776 | 0.35248 | -0.10529 | -0.050354 | 0.045776 | 0.10071 | -0.086975 | -0.054932 | 0.009155 | 0.13733 | 0.14191 | 0.11902 | 0.22888 | 0.20599 | 0.50354 | 123.4955 | 0.2243 | 123.3948 | 123.4955 | 123.3307 | 123.3444 | 123.2437 | -123.4497 | -123.3856 | 123.3444 | 123.3078 | 61.6928 | 61.7935
418.0781 | 123.587 | -61.7615 | 61.5417 | -0.0020601 | 0.0023905 | 0.069139 | 0.064162 | -0.0027195 | -0.003371 | 0.0011066 | -0.0073547 | 0.0030911 | 0.069128 | 0.061741 | -0.0028668 | 0.014368 | -0.0053512 | -0.068665 | 61.5692 | -61.8988 | 61.5692 | -61.4548 | -61.8484 | -61.8851 | 0.027466 | 61.5005 | -61.7981 | 61.5601 | -61.6241 | -61.6196 | -61.6013 | -0.13733 | 0.027466 | 0.027466 | 0.3067 | -0.1236 | -0.086975 | 0.013733 | 0.050354 | -0.036621 | -0.041199 | 0.018311 | 0.13733 | 0.16022 | 0.14191 | 0.19684 | 0.17853 | 0.44403 | 123.468 | 0.17395 | 123.3582 | 123.468 | 123.2986 | 123.3307 | 123.262 | -123.4406 | -123.3398 | 123.3307 | 123.3215 | 61.6928 | 61.7889
419.8281 | 123.5779 | -61.7523 | 61.5326 | -0.0096891 | 0.0047403 | 0.06978 | 0.063948 | -0.0012241 | -0.0014484 | -0.0023114 | -0.0012513 | 0.0060819 | 0.069556 | 0.060887 | 0.00033757 | 0.014155 | -0.003215 | -0.068665 | 61.6104 | -61.8942 | 61.5738 | -61.4456 | -61.8805 | -61.9034 | -0.004578 | 61.496 | -61.7889 | 61.5601 | -61.647 | -61.6745 | -61.6013 | -0.14191 | 0.07782 | 0.041199 | 0.3067 | -0.15106 | -0.12817 | -0.009155 | 0.013733 | -0.036621 | -0.036621 | 0.027466 | 0.10529 | 0.15106 | 0.077819 | 0.18768 | 0.11444 | 0.44861 | 123.468 | 0.14191 | 123.349 | 123.5046 | 123.2849 | 123.3627 | 123.2483 | -123.4268 | -123.3215 | 123.3261 | 123.3124 | 61.6837 | 61.7477
421.5 | 123.5825 | -61.7523 | 61.5555 | -0.0096891 | 0.0049539 | 0.067644 | 0.062026 | 0.0034755 | -0.0023028 | -0.00081595 | 0.0018005 | 0.0035183 | 0.069342 | 0.068791 | -0.0045758 | 0.014582 | 0.0010574 | -0.082397 | 61.5829 | -61.9034 | 61.5555 | -61.4594 | -61.8393 | -61.8851 | 0.027466 | 61.4914 | -61.8027 | 61.5372 | -61.6333 | -61.6287 | -61.6196 | -0.15106 | 0.027466 | 0 | 0.29297 | -0.13275 | -0.086975 | 0.01831 | 0.064087 | -0.050354 | -0.064087 | -0.018311 | 0.11902 | 0.13275 | 0.1236 | 0.1831 | 0.17395 | 0.44403 | 123.4589 | 0.16937 | 123.3398 | 123.4863 | 123.2941 | 123.3353 | 123.2437 | -123.4589 | -123.3582 | 123.3078 | 123.2895 | 61.6699 | 61.7798
423.25 | 123.4497 | -61.7477 | 61.6013 | 0.0055694 | 0.0060221 | 0.068712 | 0.066298 | -0.0012241 | -0.00508 | -0.00038875 | -0.0073547 | 0.0045865 | 0.07041 | 0.047429 | -0.0062848 | 0.0133 | -0.0010788 | -0.018311 | 61.6058 | -61.908 | 61.528 | -61.5143 | -61.8851 | -61.9354 | -0.018311 | 61.5509 | -61.7889 | 61.4365 | -61.7203 | -61.734 | -61.6837 | -0.16022 | 0.004578 | -0.073242 | 0.23346 | -0.18768 | -0.13733 | -0.027466 | 0.022888 | -0.041198 | -0.050354 | -0.16479 | 0.027466 | 0.064087 | 0.013733 | 0.10528 | 0.054931 | 0.39368 | 123.436 | 0.068664 | 123.2254 | 123.5138 | 123.3398 | 123.3536 | 123.2986 | -123.5092 | -123.3902 | 123.2758 | 123.1842 | 61.7294 | 61.7294
425.0156 | 123.436 | -61.734 | 61.6241 | 0.013199 | 0.0040995 | 0.070207 | 0.066725 | 0.0039029 | -0.0029438 | 0.00067925 | 0.017059 | 0.0067227 | 0.069342 | 0.062382 | -0.0041486 | 0.013941 | -0.0012924 | -0.022888 | 61.6699 | -61.9492 | 61.496 | -61.5326 | -61.9034 | -61.9446 | -0.045776 | 61.5875 | -61.8256 | 61.4502 | -61.7249 | -61.7386 | -61.6562 | -0.21515 | 0.045776 | -0.12817 | 0.20142 | -0.21057 | -0.16937 | 0.004578 | 0.045777 | -0.091553 | -0.036622 | -0.17395 | 0.009155 | 0.07782 | -0.004577 | 0.16937 | 0.086976 | 0.41656 | 123.4451 | 0.10071 | 123.2758 | 123.6191 | 123.4131 | 123.4039 | 123.3215 | -123.5733 | -123.4497 | 123.23 | 123.1842 | 61.7111 | 61.6882
426.7656 | 123.4497 | -61.7477 | 61.647 | 0.058975 | 0.0047403 | 0.069566 | 0.068007 | 0.0019803 | -0.0020892 | -0.00060235 | 0.010956 | 0.0069363 | 0.068915 | 0.059178 | -0.0024396 | 0.013514 | -0.0036422 | -0.022888 | 61.7294 | -61.9217 | 61.4822 | -61.5326 | -61.9034 | -61.9034 | -0.036621 | 61.5829 | -61.8393 | 61.4502 | -61.7111 | -61.7249 | -61.6562 | -0.17395 | 0.082397 | -0.16479 | 0.21515 | -0.15564 | -0.15564 | 0.018311 | 0.018311 | -0.091552 | -0.064087 | -0.19684 | 0.036621 | 0.091553 | 0.022888 | 0.18311 | 0.11444 | 0.3891 | 123.4039 | 0.12817 | 123.2895 | 123.6511 | 123.4222 | 123.4772 | 123.3307 | -123.5687 | -123.4863 | 123.23 | 123.1979 | 61.7249 | 61.7111
428.4531 | 123.4909 | -61.734 | 61.6241 | 0.036087 | 0.0043131 | 0.06978 | 0.068221 | 0.0032619 | -0.0027302 | -0.00060235 | 0.014008 | 0.0073635 | 0.069342 | 0.053837 | -0.0039348 | 0.015436 | 0.0014846 | 0 | 61.7065 | -61.908 | 61.5601 | -61.4777 | -61.8347 | -61.8942 | 0.009155 | 61.5738 | -61.8118 | 61.4777 | -61.6745 | -61.7065 | -61.6287 | -0.17395 | 0.082397 | -0.064087 | 0.25635 | -0.16022 | -0.10071 | 0.013733 | 0.073242 | -0.07782 | -0.050354 | -0.14649 | 0.059509 | 0.10529 | 0.027466 | 0.18311 | 0.10529 | 0.4303 | 123.468 | 0.13733 | 123.2895 | 123.6145 | 123.3856 | 123.4406 | 123.3078 | -123.5321 | -123.436 | 123.2941 | 123.2117 | 61.734 | 61.7432
430.2188 | 123.4406 | -61.7752 | 61.6196 | 0.0055694 | 0.0036721 | 0.069566 | 0.064375 | 0.00048494 | -0.0027302 | -0.001457 | -0.0012513 | 0.0035183 | 0.069983 | 0.062382 | -0.0020122 | 0.013941 | -0.0019332 | -0.022888 | 61.615 | -61.8805 | 61.5417 | -61.4777 | -61.8439 | -61.8851 | -0.004578 | 61.5326 | -61.7706 | 61.4548 | -61.6791 | -61.6974 | -61.6562 | -0.10529 | -0.004578 | -0.07782 | 0.29755 | -0.10986 | -0.068664 | -0.004578 | 0.036621 | 0.004578 | -0.086975 | -0.16479 | 0.096131 | 0.11902 | 0.07782 | 0.11444 | 0.073242 | 0.40283 | 123.4222 | 0.091553 | 123.2254 | 123.4955 | 123.3032 | 123.3902 | 123.3078 | -123.5001 | -123.3902 | 123.317 | 123.23 | 61.7523 | 61.7706
431.9531 | 123.5184 | -61.7661 | 61.5417 | 0.013199 | 0.0047403 | 0.070421 | 0.066512 | 0.00048494 | -0.0031574 | -0.00017515 | -0.0012513 | 0.0045865 | 0.068701 | 0.073918 | -0.0011578 | 0.01565 | -0.0012924 | -0.12817 | 61.5921 | -61.8942 | 61.496 | -61.5189 | -61.9171 | -61.9354 | -0.073242 | 61.496 | -61.8256 | 61.4548 | -61.702 | -61.702 | -61.6562 | -0.12817 | 0.050354 | -0.045776 | 0.24719 | -0.16937 | -0.15106 | -0.041199 | -0.022888 | -0.05951 | -0.045776 | -0.086975 | 0.064087 | 0.10986 | 0.064087 | 0.16937 | 0.1236 | 0.37537 | 123.3902 | 0.1236 | 123.2803 | 123.4863 | 123.3215 | 123.3582 | 123.262 | -123.436 | -123.3673 | 123.262 | 123.2208 | 61.6379 | 61.6928
433.625 | 123.436 | -61.734 | 61.6241 | 0.020828 | 0.0055947 | 0.068712 | 0.066298 | 0.0024075 | -0.0020892 | -0.00081595 | 0.017059 | 0.0067227 | 0.070837 | 0.066227 | -0.0043622 | 0.014155 | -0.001506 | -0.022888 | 61.6837 | -61.9308 | 61.5005 | -61.5326 | -61.8622 | -61.9125 | -0.027466 | 61.6058 | -61.8073 | 61.4639 | -61.6653 | -61.6974 | -61.6196 | -0.19684 | 0.059509 | -0.1236 | 0.20142 | -0.17853 | -0.12817 | 0.01831 | 0.068664 | -0.073242 | -0.018311 | -0.16022 | 0.068665 | 0.11444 | 0.036621 | 0.18768 | 0.10986 | 0.39825 | 123.4314 | 0.14191 | 123.2712 | 123.6145 | 123.4131 | 123.4177 | 123.3398 | -123.555 | -123.4314 | 123.2346 | 123.1979 | 61.7111 | 61.7065
435.3594 | 123.468 | -61.7432 | 61.6379 | 0.020828 | 0.0060221 | 0.071703 | 0.066939 | 0.0013393 | -0.0031574 | -0.001457 | 0.014008 | 0.0077909 | 0.06806 | 0.061955 | -0.0013714 | 0.013514 | -0.0030014 | 0.009155 | 61.6928 | -61.9034 | 61.5601 | -61.4731 | -61.8393 | -61.9034 | 0.009155 | 61.5738 | -61.7615 | 61.4914 | -61.6425 | -61.6882 | -61.615 | -0.16022 | 0.054932 | -0.077819 | 0.27008 | -0.16022 | -0.09613 | 0 | 0.064087 | -0.018311 | -0.064086 | -0.14648 | 0.10071 | 0.12817 | 0.054932 | 0.14648 | 0.073243 | 0.4303 | 123.4634 | 0.11902 | 123.2529 | 123.5962 | 123.3353 | 123.436 | 123.317 | -123.5413 | -123.3994 | 123.3032 | 123.2346 | 61.7523 | 61.7523
437.0938 | 123.4955 | -61.7157 | 61.6013 | 0.013199 | 0.0058083 | 0.068285 | 0.066725 | 0.00069854 | -0.0025166 | -0.0018842 | 0.010956 | 0.0043729 | 0.067847 | 0.062382 | -0.0024396 | 0.013941 | -0.001506 | -0.004578 | 61.6745 | -61.8668 | 61.5372 | -61.4548 | -61.8622 | -61.8759 | 0.068665 | 61.5692 | -61.7615 | 61.5372 | -61.6333 | -61.6608 | -61.5829 | -0.15106 | 0.073243 | -0.064087 | 0.26093 | -0.16022 | -0.14648 | -0.009156 | 0.004577 | -0.045777 | -0.032043 | -0.064087 | 0.082397 | 0.13275 | 0.054931 | 0.17853 | 0.10071 | 0.41199 | 123.4039 | 0.12817 | 123.2986 | 123.5413 | 123.3307 | 123.3902 | 123.2849 | -123.468 | -123.3627 | 123.2529 | 123.2529 | 61.7111 | 61.7844
438.8438 | 123.4085 | -61.734 | 61.6562 | 0.0055694 | 0.0051675 | 0.068498 | 0.065443 | 0.0053983 | -0.0044392 | 0.00089285 | 0.0018005 | 0.0060819 | 0.070624 | 0.059391 | -0.001585 | 0.015009 | -0.0036422 | -0.068665 | 61.6928 | -61.8668 | 61.4777 | -61.5463 | -61.9263 | -61.9537 | -0.12817 | 61.5921 | -61.7432 | 61.4502 | -61.7386 | -61.7615 | -61.6653 | -0.13275 | 0.036621 | -0.17853 | 0.18768 | -0.21973 | -0.19226 | -0.086975 | -0.05951 | -0.009155 | -0.064087 | -0.20599 | -0.004577 | 0.068665 | -0.027466 | 0.07782 | -0.018311 | 0.32043 | 123.3444 | 0.004578 | 123.1934 | 123.5596 | 123.3353 | 123.4268 | 123.3261 | -123.5229 | -123.3994 | 123.2117 | 123.1842 | 61.6653 | 61.6058
440.5312 | 123.4131 | -61.734 | 61.6241 | 0.013199 | 0.0062357 | 0.070634 | 0.067793 | -0.0031467 | -0.0025166 | -0.0029524 | -0.0012513 | 0.0071499 | 0.071051 | 0.057896 | -0.00094423 | 0.015436 | -0.0036422 | -0.1236 | 61.6699 | -61.8759 | 61.4548 | -61.5555 | -61.9308 | -61.9446 | -0.12817 | 61.5555 | -61.7752 | 61.4456 | -61.7386 | -61.7477 | -61.6516 | -0.14191 | 0.045776 | -0.16937 | 0.17853 | -0.21057 | -0.19684 | -0.068664 | -0.054931 | -0.041199 | -0.068665 | -0.17853 | -0.004577 | 0.082398 | -0.013733 | 0.1236 | 0.027466 | 0.32043 | 123.3307 | 0.036622 | 123.2208 | 123.5458 | 123.3307 | 123.4039 | 123.2895 | -123.5001 | -123.3994 | 123.1888 | 123.1796 | 61.6104 | 61.6058
442.2812 | 123.4131 | -61.702 | 61.6333 | 0.0055694 | 0.0058083 | 0.067644 | 0.06758 | 0.0017667 | -0.0020892 | -0.0012434 | -0.0012513 | 0.0043729 | 0.069983 | 0.054692 | -0.0026532 | 0.014582 | 0.000203 | -0.09613 | 61.702 | -61.8759 | 61.496 | -61.5372 | -61.9034 | -61.94 | -0.10529 | 61.5784 | -61.7615 | 61.4502 | -61.7111 | -61.7294 | -61.6562 | -0.17395 | 0.068664 | -0.13733 | 0.16479 | -0.23804 | -0.20142 | -0.064086 | -0.027465 | -0.05951 | -0.054932 | -0.18311 | -0.009156 | 0.045776 | -0.027466 | 0.10529 | 0.032044 | 0.33875 | 123.3719 | 0.050354 | 123.2117 | 123.5779 | 123.3398 | 123.4039 | 123.2803 | -123.5092 | -123.3948 | 123.1979 | 123.1522 | 61.6058 | 61.5967
444.0312 | 123.4085 | -61.7157 | 61.6425 | -0.0020601 | 0.0038857 | 0.070207 | 0.065871 | -0.0025059 | -0.0012348 | -0.0029524 | -0.0012513 | 0.0054409 | 0.070196 | 0.05811 | -0.0017986 | 0.015009 | -0.002147 | -0.07782 | 61.6791 | -61.8668 | 61.4868 | -61.5189 | -61.908 | -61.94 | -0.1236 | 61.5875 | -61.7432 | 61.4502 | -61.7111 | -61.7523 | -61.6241 | -0.15106 | 0.036621 | -0.15564 | 0.19684 | -0.2243 | -0.19226 | -0.073242 | -0.041199 | -0.027466 | -0.054932 | -0.19226 | 0.004577 | 0.091552 | -0.036621 | 0.11902 | -0.009155 | 0.3479 | 123.3536 | 0.032043 | 123.1934 | 123.5458 | 123.3307 | 123.3948 | 123.3032 | -123.5092 | -123.3856 | 123.2025 | 123.1659 | 61.6379 | 61.5921
445.7812 | 123.5504 | -61.6974 | 61.5784 | -0.0020601 | 0.0017495 | 0.069139 | 0.062239 | 0.0043301 | -0.0018756 | -0.0027386 | 0.0018005 | 0.0026639 | 0.068488 | 0.060032 | -0.003294 | 0.016077 | -0.0012924 | -0.054932 | 61.615 | -61.8576 | 61.5967 | -61.3449 | -61.7615 | -61.8027 | 0.059509 | 61.5005 | -61.7477 | 61.5555 | -61.5509 | -61.5738 | -61.5509 | -0.16022 | 0.036621 | 0.018311 | 0.35248 | -0.10529 | -0.064087 | 0.054932 | 0.09613 | -0.050354 | -0.07782 | -0.022888 | 0.14648 | 0.14648 | 0.1236 | 0.19684 | 0.17395 | 0.5127 | 123.4543 | 0.19684 | 123.3032 | 123.4726 | 123.2483 | 123.3124 | 123.1979 | -123.436 | -123.3261 | 123.2941 | 123.2529 | 61.6425 | 61.7569
447.4531 | 123.4406 | -61.6745 | 61.6653 | 0.013199 | 0.0058083 | 0.068712 | 0.067366 | 5.774e-05 | -0.0040118 | -0.00017515 | 0.010956 | 0.0048001 | 0.068488 | 0.060887 | -0.0024396 | 0.015864 | -0.0017196 | -0.009155 | 61.7294 | -61.8576 | 61.5738 | -61.4365 | -61.8073 | -61.8301 | -0.004578 | 61.615 | -61.734 | 61.4914 | -61.6104 | -61.6379 | -61.5601 | -0.1831 | 0.064087 | -0.091552 | 0.23804 | -0.15564 | -0.13275 | 0.027466 | 0.050354 | -0.059509 | -0.050354 | -0.17395 | 0.064087 | 0.11444 | 0.036622 | 0.17395 | 0.096131 | 0.42114 | 123.4314 | 0.1236 | 123.2254 | 123.587 | 123.349 | 123.4039 | 123.2895 | -123.5229 | -123.3994 | 123.2483 | 123.1659 | 61.6653 | 61.6699
449.125 | 123.4863 | -61.702 | 61.5784 | 0.036087 | 0.0036721 | 0.071703 | 0.064803 | 0.00091214 | -0.0025166 | 0.00089285 | 0.0079041 | 0.0030911 | 0.071265 | 0.069004 | -0.00030343 | 0.016718 | 0.000203 | -0.10071 | 61.6745 | -61.8851 | 61.5555 | -61.3953 | -61.821 | -61.8393 | -0.018311 | 61.528 | -61.7889 | 61.5097 | -61.6287 | -61.615 | -61.5738 | -0.18311 | 0.096131 | -0.022888 | 0.3067 | -0.13733 | -0.11902 | 0.045777 | 0.064087 | -0.086975 | -0.050354 | -0.068664 | 0.073242 | 0.12817 | 0.086975 | 0.21515 | 0.17395 | 0.48981 | 123.4406 | 0.16022 | 123.2986 | 123.5596 | 123.317 | 123.3765 | 123.23 | -123.4634 | -123.3673 | 123.2574 | 123.2117 | 61.6013 | 61.6837
450.875 | 123.4222 | -61.7203 | 61.6104 | -0.0020601 | 0.0060221 | 0.068712 | 0.067366 | 0.0041165 | -0.0020892 | -0.00060235 | -0.0043029 | 0.0067227 | 0.069556 | 0.0611 | 0.00033757 | 0.013514 | -0.002147 | -0.086975 | 61.6882 | -61.8759 | 61.4685 | -61.5646 | -61.9446 | -61.9675 | -0.10529 | 61.5417 | -61.7523 | 61.441 | -61.7157 | -61.7386 | -61.6196 | -0.15564 | 0.077819 | -0.14191 | 0.15564 | -0.24719 | -0.2243 | -0.091552 | -0.068664 | -0.032043 | -0.068665 | -0.16937 | 0.004578 | 0.10071 | -0.01831 | 0.13275 | 0.013733 | 0.31128 | 123.3444 | 0.036621 | 123.1934 | 123.5641 | 123.2941 | 123.4085 | 123.262 | -123.4863 | -123.3627 | 123.1888 | 123.1613 | 61.6333 | 61.615
452.6094 | 123.5138 | -61.7065 | 61.5601 | 0.036087 | 0.0085855 | 0.071703 | 0.066725 | -0.0010105 | -0.0035846 | -0.0016706 | 0.014008 | 0.0043729 | 0.070837 | 0.060673 | 0.00033757 | 0.016504 | -0.0030014 | -0.064087 | 61.6013 | -61.8484 | 61.5921 | -61.3815 | -61.7981 | -61.8301 | 0.018311 | 61.5234 | -61.7477 | 61.5326 | -61.5967 | -61.6196 | -61.5784 | -0.14191 | 0.041198 | 0.032043 | 0.32501 | -0.1236 | -0.091553 | 0.018311 | 0.050354 | -0.041199 | -0.036622 | -0.027466 | 0.10986 | 0.12817 | 0.086975 | 0.16937 | 0.12817 | 0.46692 | 123.4406 | 0.15106 | 123.2803 | 123.4497 | 123.2712 | 123.3078 | 123.23 | -123.4085 | -123.3078 | 123.2986 | 123.2391 | 61.6425 | 61.7249
454.3438 | 123.4772 | -61.734 | 61.5738 | 0.028458 | 0.0034585 | 0.068925 | 0.065443 | -0.00079686 | -0.001662 | -0.0018842 | 0.0018005 | 0.0035183 | 0.069769 | 0.061741 | -0.001585 | 0.014368 | -0.0012924 | -0.1236 | 61.6241 | -61.8713 | 61.5189 | -61.4548 | -61.8805 | -61.8896 | -0.064087 | 61.5005 | -61.7798 | 61.4777 | -61.6653 | -61.6699 | -61.6241 | -0.13733 | 0.050354 | -0.054932 | 0.27924 | -0.15564 | -0.14648 | -0.01831 | -0.009155 | -0.045776 | -0.073243 | -0.096131 | 0.068665 | 0.10986 | 0.064087 | 0.15564 | 0.10986 | 0.41656 | 123.3902 | 0.11444 | 123.2574 | 123.4955 | 123.2803 | 123.3582 | 123.2346 | -123.4451 | -123.3536 | 123.2529 | 123.2117 | 61.6104 | 61.6699
456.0938 | 123.5458 | -61.7065 | 61.5646 | 0.0055694 | 0.0030313 | 0.071062 | 0.064162 | -0.0012241 | -0.0020892 | 0.0013202 | -0.0043029 | 0.0030911 | 0.066992 | 0.060032 | -0.0013714 | 0.015223 | -0.0008652 | -0.09613 | 61.6333 | -61.8851 | 61.5326 | -61.4365 | -61.8164 | -61.8576 | -0.022888 | 61.5097 | -61.7569 | 61.528 | -61.5829 | -61.5784 | -61.5417 | -0.17853 | 0.068665 | -0.032043 | 0.27008 | -0.15106 | -0.10986 | 0.027466 | 0.068665 | -0.050354 | -0.054931 | -0.036621 | 0.1236 | 0.1648 | 0.12817 | 0.21515 | 0.17853 | 0.44861 | 123.4177 | 0.17395 | 123.2849 | 123.5184 | 123.2666 | 123.3398 | 123.2162 | -123.4497 | -123.3215 | 123.2391 | 123.2346 | 61.6104 | 61.6837
457.8438 | 123.5229 | -61.6974 | 61.5967 | 0.0055694 | 0.0040995 | 0.069353 | 0.065016 | 0.00048494 | -0.0025166 | -0.00060235 | -0.0073547 | 0.0060819 | 0.069128 | 0.06046 | -0.0028668 | 0.015009 | -0.0012924 | -0.027466 | 61.5784 | -61.8347 | 61.5875 | -61.377 | -61.7706 | -61.821 | 0.068665 | 61.5189 | -61.7294 | 61.5326 | -61.5829 | -61.5875 | -61.5417 | -0.13733 | -0.018311 | -0.009156 | 0.32043 | -0.1236 | -0.073242 | 0.013733 | 0.064087 | -0.032043 | -0.07782 | -0.064087 | 0.11444 | 0.15564 | 0.10986 | 0.18768 | 0.14191 | 0.45776 | 123.4222 | 0.14648 | 123.262 | 123.4131 | 123.2483 | 123.2758 | 123.2162 | -123.4314 | -123.3261 | 123.2849 | 123.23 | 61.6699 | 61.7661
459.5312 | 123.4451 | -61.6379 | 61.6425 | 0.013199 | 0.0058083 | 0.070421 | 0.065443 | 0.0021939 | -0.0012348 | -0.0012434 | 0.0048523 | 0.0082181 | 0.068915 | 0.065159 | -0.0039348 | 0.012446 | -0.0027878 | 0.013733 | 61.7203 | -61.8393 | 61.5829 | -61.3953 | -61.8027 | -61.8118 | 0.036621 | 61.6104 | -61.7157 | 61.528 | -61.5875 | -61.6058 | -61.5509 | -0.20142 | 0.07782 | -0.059509 | 0.24261 | -0.17395 | -0.16479 | 0.027465 | 0.036621 | -0.07782 | -0.032043 | -0.11444 | 0.050354 | 0.086975 | 0.032043 | 0.1648 | 0.10986 | 0.44403 | 123.4222 | 0.12817 | 123.2437 | 123.5596 | 123.3261 | 123.3582 | 123.2483 | -123.4818 | -123.3582 | 123.2208 | 123.1659 | 61.6516 | 61.6745
461.2812 | 123.4177 | -61.6379 | 61.6333 | -0.0020601 | 0.0040995 | 0.06978 | 0.064375 | 5.774e-05 | -0.0035846 | -0.00060235 | -0.0043029 | 0.0041593 | 0.06806 | 0.056187 | -0.0056438 | 0.013514 | -0.0030014 | -0.018311 | 61.6379 | -61.8347 | 61.5829 | -61.3907 | -61.7889 | -61.821 | -0.004578 | 61.5738 | -61.7203 | 61.496 | -61.6058 | -61.6241 | -61.5829 | -0.19684 | 0.004577 | -0.050354 | 0.24719 | -0.18311 | -0.15106 | 0.013733 | 0.045777 | -0.082398 | -0.059509 | -0.13733 | 0.032043 | 0.054931 | 0.013732 | 0.13733 | 0.09613 | 0.44403 | 123.4177 | 0.11444 | 123.2162 | 123.4726 | 123.2941 | 123.2758 | 123.2117 | -123.468 | -123.3536 | 123.2208 | 123.1338 | 61.6196 | 61.6333
463.0312 | 123.5184 | -61.6974 | 61.5601 | -0.0020601 | 0.0060221 | 0.06978 | 0.063735 | 0.0017667 | -0.001662 | -0.0016706 | 0.023163 | 0.0030911 | 0.069769 | 0.064732 | 0.0016194 | 0.016504 | -0.0025742 | -0.073242 | 61.6058 | -61.8256 | 61.5921 | -61.3724 | -61.7889 | -61.8164 | 0.041199 | 61.496 | -61.7706 | 61.5417 | -61.5829 | -61.6058 | -61.5417 | -0.12817 | 0.045776 | 0.032043 | 0.32501 | -0.11902 | -0.091552 | 0.009156 | 0.036622 | -0.073242 | -0.064087 | -0.018311 | 0.11444 | 0.15564 | 0.091553 | 0.22888 | 0.16479 | 0.45319 | 123.4177 | 0.18768 | 123.3124 | 123.4314 | 123.2666 | 123.3032 | 123.1934 | -123.3856 | -123.3307 | 123.2895 | 123.2391 | 61.6241 | 61.7386
464.7812 | 123.4863 | -61.702 | 61.5784 | -0.0096891 | 0.0045267 | 0.068498 | 0.062666 | 0.0043301 | -0.0040118 | -0.00081595 | -0.0012513 | 0.0033047 | 0.069556 | 0.069218 | -0.0028668 | 0.013727 | 0.0004166 | -0.018311 | 61.6013 | -61.853 | 61.5784 | -61.3724 | -61.7752 | -61.821 | 0.045776 | 61.5234 | -61.7477 | 61.5234 | -61.5692 | -61.5738 | -61.5463 | -0.15106 | 0.022888 | 0 | 0.32959 | -0.11902 | -0.073243 | 0.032043 | 0.077819 | -0.045777 | -0.054932 | -0.054932 | 0.13275 | 0.15564 | 0.12817 | 0.20142 | 0.17395 | 0.48065 | 123.4314 | 0.17853 | 123.2712 | 123.4543 | 123.2712 | 123.3032 | 123.2254 | -123.4314 | -123.3261 | 123.2803 | 123.2254 | 61.6837 | 61.7477
466.4531 | 123.5504 | -61.6516 | 61.5692 | -0.017319 | 0.0011087 | 0.068071 | 0.064589 | 0.0013393 | -0.0020892 | -0.0027386 | -0.0012513 | 0.0022367 | 0.07041 | 0.064305 | -0.0039348 | 0.013727 | -0.001506 | -0.082397 | 61.5967 | -61.8073 | 61.6058 | -61.3358 | -61.7249 | -61.7706 | 0.073242 | 61.5051 | -61.702 | 61.5692 | -61.5463 | -61.5646 | -61.528 | -0.15564 | 0.027466 | 0.036621 | 0.31586 | -0.11902 | -0.073243 | 0.036621 | 0.082397 | -0.050354 | -0.064087 | 0 | 0.10529 | 0.1236 | 0.086975 | 0.17395 | 0.13733 | 0.4715 | 123.4131 | 0.15564 | 123.2712 | 123.4039 | 123.2071 | 123.2483 | 123.1567 | -123.3765 | -123.2712 | 123.2574 | 123.2208 | 61.5692 | 61.7249
468.1875 | 123.3856 | -61.6928 | 61.6287 | -0.017319 | 0.0030313 | 0.06743 | 0.064162 | 0.0017667 | -0.0046528 | -0.0035932 | -0.0073547 | 0.0045865 | 0.068488 | 0.060246 | -0.0045758 | 0.011805 | -0.0008652 | -0.07782 | 61.6333 | -61.8393 | 61.4822 | -61.4822 | -61.8484 | -61.8896 | -0.054932 | 61.5692 | -61.7523 | 61.4319 | -61.6562 | -61.6745 | -61.615 | -0.14648 | 0.004578 | -0.14648 | 0.21057 | -0.19684 | -0.15564 | -0.050354 | -0.009156 | -0.059509 | -0.059509 | -0.19684 | 0.036621 | 0.07782 | 0.01831 | 0.13733 | 0.077819 | 0.35706 | 123.3215 | 0.09613 | 123.1842 | 123.4726 | 123.3215 | 123.3261 | 123.262 | -123.468 | -123.381 | 123.175 | 123.1247 | 61.615 | 61.6379
469.9375 | 123.3994 | -61.6882 | 61.6379 | -0.0020601 | 0.0026041 | 0.070634 | 0.065016 | -0.0022923 | -0.0042254 | 0.0017474 | -0.0043029 | 0.0030911 | 0.068701 | 0.05576 | -0.0039348 | 0.0133 | -0.0002244 | -0.027466 | 61.6287 | -61.8393 | 61.5646 | -61.3907 | -61.7798 | -61.821 | -0.018311 | 61.5646 | -61.7065 | 61.4868 | -61.6333 | -61.6379 | -61.5738 | -0.15106 | -0.009155 | -0.073242 | 0.29755 | -0.13275 | -0.091553 | 0.01831 | 0.059509 | -0.018311 | -0.073242 | -0.15106 | 0.054931 | 0.11444 | 0.050354 | 0.13275 | 0.068665 | 0.44861 | 123.4039 | 0.073242 | 123.1934 | 123.468 | 123.2712 | 123.317 | 123.2529 | -123.4772 | -123.3444 | 123.2529 | 123.175 | 61.6608 | 61.6699
471.6094 | 123.5184 | -61.6653 | 61.5738 | -0.0020601 | 0.0026041 | 0.067217 | 0.06523 | 0.0026211 | -0.003371 | -0.0027386 | -0.0012513 | 0.0037319 | 0.069769 | 0.06815 | -0.0020122 | 0.013086 | -1.0598e-05 | -0.10986 | 61.5875 | -61.8347 | 61.5601 | -61.3998 | -61.7752 | -61.821 | -0.027466 | 61.5005 | -61.7249 | 61.5646 | -61.5509 | -61.5509 | -61.5234 | -0.16937 | 0.013732 | -0.013733 | 0.2655 | -0.15564 | -0.10986 | 0.013733 | 0.059509 | -0.05951 | -0.073243 | -0.009156 | 0.11444 | 0.14191 | 0.11444 | 0.20142 | 0.17395 | 0.43488 | 123.3948 | 0.17395 | 123.2895 | 123.4222 | 123.2254 | 123.2529 | 123.1659 | -123.4085 | -123.2986 | 123.2254 | 123.23 | 61.5555 | 61.6379
473.375 | 123.3948 | -61.6425 | 61.6699 | 0.0055694 | 0.0030313 | 0.068925 | 0.064375 | 0.0015529 | -0.0037982 | -0.00038875 | 0.0018005 | 0.0026639 | 0.069769 | 0.053196 | -0.003294 | 0.013727 | -0.001506 | -0.022888 | 61.6928 | -61.7752 | 61.6013 | -61.3541 | -61.7477 | -61.7889 | -0.013733 | 61.5875 | -61.6837 | 61.5005 | -61.5829 | -61.6104 | -61.5509 | -0.13275 | 0.022888 | -0.068665 | 0.28839 | -0.14648 | -0.10529 | -0.013732 | 0.027466 | -0.041199 | -0.082398 | -0.16937 | 0.059509 | 0.091553 | 0.032043 | 0.13275 | 0.073242 | 0.42114 | 123.3765 | 0.10071 | 123.1842 | 123.468 | 123.2712 | 123.3353 | 123.23 | -123.4451 | -123.3536 | 123.2437 | 123.143 | 61.6196 | 61.6287
475.0625 | 123.5001 | -61.6013 | 61.6104 | 0.0055694 | 0.0079447 | 0.071062 | 0.064803 | -0.0016513 | -0.00080758 | -0.00060235 | 0.014008 | 0.0039457 | 0.069983 | 0.060887 | 0.001192 | 0.01565 | -0.0025742 | -0.027466 | 61.6745 | -61.7706 | 61.6791 | -61.2762 | -61.7065 | -61.7386 | 0.032043 | 61.5692 | -61.6653 | 61.6104 | -61.5097 | -61.528 | -61.5051 | -0.16937 | 0.064087 | 0.068664 | 0.32501 | -0.13733 | -0.10529 | 0.032044 | 0.064087 | -0.064087 | -0.041199 | 0 | 0.091552 | 0.09613 | 0.073242 | 0.16022 | 0.13733 | 0.49438 | 123.4497 | 0.15564 | 123.2758 | 123.4451 | 123.2346 | 123.2758 | 123.1705 | -123.381 | -123.2758 | 123.2803 | 123.2117 | 61.5738 | 61.6333
476.8125 | 123.4497 | -61.5921 | 61.7065 | -0.0096891 | 0.0032449 | 0.06978 | 0.064803 | -0.00079686 | -0.0035846 | 0.00067925 | -0.0012513 | 0.0033047 | 0.066992 | 0.064518 | -0.0037212 | 0.014155 | 0.0006302 | -0.027466 | 61.7157 | -61.7569 | 61.6653 | -61.2991 | -61.6837 | -61.7203 | 0.027466 | 61.5967 | -61.6379 | 61.5829 | -61.4868 | -61.5097 | -61.4594 | -0.1648 | 0.009155 | -0.041199 | 0.29297 | -0.12817 | -0.091553 | 0.036621 | 0.073242 | -0.045776 | -0.10986 | -0.1236 | 0.10529 | 0.13275 | 0.082397 | 0.17853 | 0.12817 | 0.45776 | 123.4222 | 0.15106 | 123.2208 | 123.4726 | 123.2346 | 123.3078 | 123.1888 | -123.4634 | -123.3444 | 123.2574 | 123.175 | 61.5646 | 61.6196
478.5625 | 123.436 | -61.647 | 61.6562 | 0.051346 | 0.0060221 | 0.068498 | 0.067152 | -0.00036966 | -0.00059378 | -0.00038875 | 0.010956 | 0.0069363 | 0.069128 | 0.055546 | -0.0024396 | 0.013941 | -0.001506 | 0.009155 | 61.6791 | -61.8301 | 61.5829 | -61.3815 | -61.7752 | -61.7981 | 0.050354 | 61.6013 | -61.6974 | 61.5234 | -61.5646 | -61.6013 | -61.528 | -0.18311 | 0.022888 | -0.073242 | 0.2655 | -0.15106 | -0.12817 | 0.032043 | 0.054931 | -0.050354 | -0.054932 | -0.13275 | 0.082398 | 0.11902 | 0.045777 | 0.16937 | 0.096131 | 0.44861 | 123.4131 | 0.13275 | 123.2208 | 123.5092 | 123.2986 | 123.3261 | 123.2483 | -123.4863 | -123.3536 | 123.23 | 123.1705 | 61.6562 | 61.6974
480.2656 | 123.3765 | -61.5921 | 61.7249 | -0.0020601 | 0.0047403 | 0.067857 | 0.062666 | 0.0021939 | -0.0042254 | -0.0023114 | -0.0073547 | 0.0041593 | 0.071265 | 0.061955 | -0.0058576 | 0.013086 | -0.0017196 | -0.032043 | 61.7157 | -61.734 | 61.6104 | -61.3403 | -61.7523 | -61.7523 | -0.032043 | 61.6333 | -61.6196 | 61.5326 | -61.5463 | -61.5601 | -61.5051 | -0.14191 | -0.009156 | -0.11444 | 0.25177 | -0.16022 | -0.16022 | -0.01831 | -0.01831 | -0.027466 | -0.091553 | -0.19226 | 0.045776 | 0.086975 | 0.032043 | 0.11444 | 0.059509 | 0.39368 | 123.3444 | 0.073242 | 123.1522 | 123.4497 | 123.2529 | 123.3078 | 123.2254 | -123.4589 | -123.3444 | 123.2025 | 123.1247 | 61.5601 | 61.5601
482.0312 | 123.381 | -61.5738 | 61.7203 | -0.0096891 | 0.0034585 | 0.071275 | 0.067366 | 0.0017667 | -0.0044392 | -0.00060235 | -0.0012513 | 0.0050137 | 0.07041 | 0.067082 | -0.00030343 | 0.015436 | -0.0047104 | -0.086975 | 61.7844 | -61.7157 | 61.5875 | -61.3998 | -61.7706 | -61.7889 | -0.10986 | 61.6882 | -61.6058 | 61.5509 | -61.5509 | -61.5967 | -61.4822 | -0.14191 | 0.064087 | -0.13275 | 0.17395 | -0.21515 | -0.19684 | -0.073242 | -0.054932 | -0.032043 | -0.032044 | -0.16937 | 0.022889 | 0.091553 | -0.022888 | 0.1236 | 0.009155 | 0.31586 | 123.3032 | 0.054932 | 123.1567 | 123.5001 | 123.2941 | 123.3582 | 123.262 | -123.436 | -123.3261 | 123.1613 | 123.1247 | 61.4868 | 61.4639
483.7812 | 123.4451 | -61.615 | 61.6104 | 0.0055694 | 0.0034585 | 0.071916 | 0.066939 | 0.0017667 | -0.0020892 | -0.0020978 | 0.0048523 | 0.0028775 | 0.072333 | 0.065159 | -0.0017986 | 0.015223 | -0.0023606 | -0.12817 | 61.6928 | -61.7706 | 61.5784 | -61.3678 | -61.7432 | -61.7889 | -0.082397 | 61.5738 | -61.6974 | 61.5509 | -61.5463 | -61.5646 | -61.5051 | -0.15564 | 0.082397 | -0.032044 | 0.24719 | -0.17395 | -0.12817 | -0.01831 | 0.027466 | -0.082398 | -0.036621 | -0.05951 | 0.068664 | 0.10986 | 0.050354 | 0.19226 | 0.13275 | 0.40283 | 123.349 | 0.15106 | 123.2483 | 123.4634 | 123.2712 | 123.3078 | 123.1888 | -123.381 | -123.3078 | 123.1934 | 123.1659 | 61.4868 | 61.5326
485.4688 | 123.4222 | -61.5784 | 61.6928 | 0.020828 | 0.0060221 | 0.069139 | 0.066725 | 0.0011257 | -0.0018756 | 0.00025205 | 0.0048523 | 0.0082181 | 0.070624 | 0.060673 | -0.0017986 | 0.014795 | -0.0030014 | 0.009155 | 61.7523 | -61.7477 | 61.6196 | -61.3174 | -61.7203 | -61.7477 | 0.050354 | 61.6425 | -61.6196 | 61.5692 | -61.5189 | -61.528 | -61.4731 | -0.16937 | 0.059509 | -0.073242 | 0.26093 | -0.16937 | -0.14191 | 0 | 0.027466 | -0.041199 | -0.050354 | -0.1236 | 0.059509 | 0.10529 | 0.050354 | 0.14648 | 0.091553 | 0.4303 | 123.3673 | 0.10071 | 123.1888 | 123.5001 | 123.262 | 123.3307 | 123.2208 | -123.4406 | -123.3124 | 123.1979 | 123.1476 | 61.5875 | 61.6287
487.2344 | 123.4222 | -61.6379 | 61.6287 | 0.020828 | 0.0053811 | 0.068925 | 0.064589 | 0.00091214 | 4.7018e-05 | -0.0010298 | 0.0048523 | 0.0037319 | 0.069128 | 0.0658 | -0.0017986 | 0.015223 | -0.0019332 | -0.12817 | 61.6791 | -61.7844 | 61.5738 | -61.3632 | -61.7615 | -61.7935 | -0.064087 | 61.5555 | -61.6974 | 61.5372 | -61.5692 | -61.5738 | -61.5005 | -0.14648 | 0.050354 | -0.054931 | 0.27466 | -0.15564 | -0.1236 | -0.009155 | 0.022888 | -0.05951 | -0.073242 | -0.091553 | 0.068664 | 0.13733 | 0.064086 | 0.19684 | 0.1236 | 0.42114 | 123.3582 | 0.12817 | 123.2346 | 123.4634 | 123.2529 | 123.317 | 123.1934 | -123.4131 | -123.3261 | 123.2117 | 123.175 | 61.5097 | 61.5738
488.9219 | 123.349 | -61.6379 | 61.6333 | -0.0020601 | 0.0045267 | 0.069353 | 0.065443 | -0.00058326 | -0.001662 | 0.00089285 | -0.0073547 | 0.0050137 | 0.070196 | 0.064732 | -0.0011578 | 0.013086 | -0.0008652 | -0.11902 | 61.7065 | -61.8118 | 61.4914 | -61.4639 | -61.8576 | -61.8622 | -0.11444 | 61.6013 | -61.6928 | 61.4777 | -61.647 | -61.6653 | -61.5463 | -0.17395 | 0.073242 | -0.14191 | 0.17395 | -0.22431 | -0.21973 | -0.050354 | -0.045776 | -0.054932 | -0.032044 | -0.15564 | -0.009156 | 0.091552 | -0.027466 | 0.14648 | 0.027466 | 0.3479 | 123.3032 | 0.045776 | 123.1705 | 123.5184 | 123.2941 | 123.3444 | 123.2391 | -123.4451 | -123.3261 | 123.1293 | 123.1155 | 61.5189 | 61.5234
490.6094 | 123.4222 | -61.6013 | 61.6837 | 0.036087 | 0.0047403 | 0.071916 | 0.067366 | 0.0030483 | -0.0020892 | -0.0016706 | 0.010956 | 0.0073635 | 0.069769 | 0.057255 | -0.002226 | 0.016077 | -0.0030014 | -0.022888 | 61.7706 | -61.7523 | 61.6379 | -61.3312 | -61.6974 | -61.7386 | -0.009155 | 61.6837 | -61.647 | 61.5646 | -61.5097 | -61.5463 | -61.4639 | -0.15106 | 0.086975 | -0.045777 | 0.27008 | -0.13733 | -0.096131 | 0.013733 | 0.054931 | -0.045777 | 0 | -0.11902 | 0.091552 | 0.13733 | 0.054931 | 0.18311 | 0.10071 | 0.42114 | 123.3902 | 0.13733 | 123.2117 | 123.5229 | 123.3307 | 123.3719 | 123.2849 | -123.436 | -123.3307 | 123.2391 | 123.1659 | 61.5784 | 61.5921
492.3594 | 123.4451 | -61.5875 | 61.6379 | 0.028458 | 0.0026041 | 0.069139 | 0.065443 | 0.0013393 | -0.0012348 | 0.0011066 | 0.0079041 | 0.0045865 | 0.069128 | 0.067509 | -0.0017986 | 0.013727 | -0.0019332 | -0.1236 | 61.6608 | -61.7615 | 61.5601 | -61.3495 | -61.7569 | -61.7752 | -0.064087 | 61.5738 | -61.647 | 61.5646 | -61.5189 | -61.5326 | -61.4731 | -0.17395 | 0.022889 | -0.077819 | 0.23804 | -0.18768 | -0.16937 | -0.013733 | 0.004578 | -0.05951 | -0.064086 | -0.073242 | 0.068664 | 0.11444 | 0.054931 | 0.17395 | 0.11444 | 0.41199 | 123.3215 | 0.12817 | 123.2117 | 123.4222 | 123.2208 | 123.2483 | 123.1613 | -123.3994 | -123.2849 | 123.1476 | 123.1522 | 61.4639 | 61.5234
494.0938 | 123.3902 | -61.5509 | 61.7661 | 0.051346 | 0.0051675 | 0.069994 | 0.06523 | 0.00069854 | -0.0025166 | 0.0015338 | 0.010956 | 0.0086453 | 0.07041 | 0.064946 | -0.005003 | 0.015223 | -0.0006516 | -0.027466 | 61.8073 | -61.7157 | 61.6241 | -61.3358 | -61.6974 | -61.7386 | -0.045776 | 61.7111 | -61.6241 | 61.5646 | -61.496 | -61.5234 | -61.441 | -0.1648 | 0.041199 | -0.14191 | 0.21515 | -0.18768 | -0.14648 | -0.022888 | 0.01831 | -0.073243 | -0.054931 | -0.20142 | 0.054931 | 0.10986 | 0.027466 | 0.18311 | 0.10071 | 0.37994 | 123.3398 | 0.12817 | 123.1888 | 123.5229 | 123.3353 | 123.3582 | 123.262 | -123.4818 | -123.3902 | 123.175 | 123.1155 | 61.5234 | 61.5051
495.8438 | 123.4589 | -61.441 | 61.8027 | -0.0096891 | 0.0051675 | 0.068285 | 0.063948 | -0.00036966 | -0.0042254 | 0.0011066 | -0.0043029 | 0.0037319 | 0.068488 | 0.05811 | -0.0035076 | 0.014368 | -0.0027878 | -0.041199 | 61.7798 | -61.6104 | 61.7569 | -61.1481 | -61.5509 | -61.5784 | 0.041199 | 61.6608 | -61.5189 | 61.7111 | -61.3266 | -61.3541 | -61.322 | -0.16937 | -0.022888 | -0.045776 | 0.29297 | -0.13733 | -0.10986 | 0.032044 | 0.05951 | -0.07782 | -0.14191 | -0.091552 | 0.11444 | 0.11902 | 0.086975 | 0.19684 | 0.16479 | 0.46234 | 123.3673 | 0.19226 | 123.23 | 123.3902 | 123.1796 | 123.2208 | 123.1018 | -123.4131 | -123.3215 | 123.1979 | 123.1522 | 61.3998 | 61.4822
497.5312 | 123.4085 | -61.4639 | 61.8118 | 0.036087 | 0.0038857 | 0.068925 | 0.064589 | 0.0011257 | -0.0012348 | -0.002525 | 0.0079041 | 0.0058683 | 0.070624 | 0.063237 | -0.0026532 | 0.016077 | -1.0598e-05 | 0.013733 | 61.8942 | -61.6241 | 61.734 | -61.203 | -61.5829 | -61.6379 | 0.032043 | 61.7615 | -61.5417 | 61.6653 | -61.3907 | -61.4273 | -61.3312 | -0.16022 | 0.082397 | -0.07782 | 0.26093 | -0.17395 | -0.11902 | -0.013732 | 0.041199 | -0.07782 | -0.050354 | -0.14649 | 0.073242 | 0.13275 | 0.036621 | 0.21057 | 0.11444 | 0.42114 | 123.3582 | 0.15106 | 123.2071 | 123.5184 | 123.3032 | 123.3582 | 123.2254 | -123.436 | -123.3536 | 123.1979 | 123.1293 | 61.4777 | 61.496
499.2188 | 123.4543 | -61.4914 | 61.7157 | 0.013199 | 0.0051675 | 0.071275 | 0.064375 | -0.00079686 | -0.00080758 | -0.0010298 | 0.014008 | 0.0048001 | 0.071265 | 0.069432 | -0.00051703 | 0.016291 | 0.0016982 | -0.07782 | 61.7706 | -61.6608 | 61.7157 | -61.1801 | -61.6104 | -61.6379 | 0 | 61.6562 | -61.5738 | 61.6653 | -61.4136 | -61.4319 | -61.3724 | -0.16937 | 0.054932 | 0 | 0.31128 | -0.14648 | -0.11902 | 0.022889 | 0.050354 | -0.082398 | -0.059509 | -0.050354 | 0.07782 | 0.11902 | 0.059509 | 0.20142 | 0.14191 | 0.48065 | 123.3765 | 0.16022 | 123.2391 | 123.4314 | 123.23 | 123.262 | 123.1476 | -123.3765 | -123.2895 | 123.2071 | 123.1567 | 61.4136 | 61.4914
500.9844 | 123.4634 | -61.5555 | 61.6333 | -0.0020601 | 0.0038857 | 0.070848 | 0.065016 | 0.0026211 | -0.0012348 | -0.00017515 | -0.0043029 | 0.0050137 | 0.069556 | 0.065587 | 0.001192 | 0.015223 | -0.0017196 | -0.064087 | 61.6837 | -61.7157 | 61.647 | -61.2762 | -61.6974 | -61.7386 | 0 | 61.5646 | -61.6013 | 61.6241 | -61.4639 | -61.4822 | -61.4136 | -0.16022 | 0.050354 | 0.013733 | 0.27924 | -0.1831 | -0.14191 | -0.022888 | 0.01831 | -0.045776 | -0.068665 | -0.009155 | 0.091553 | 0.14191 | 0.073242 | 0.18768 | 0.11902 | 0.43945 | 123.3627 | 0.13733 | 123.2254 | 123.3994 | 123.1659 | 123.2391 | 123.1201 | -123.349 | -123.2346 | 123.2025 | 123.1796 | 61.4914 | 61.5555
502.6562 | 123.4543 | -61.5921 | 61.6333 | -0.0096891 | 0.0045267 | 0.067003 | 0.064589 | 0.00091214 | -0.0052936 | -0.00081595 | -0.0012513 | 0.0043729 | 0.07041 | 0.054692 | -0.0041486 | 0.015009 | -0.0047104 | -0.022888 | 61.6745 | -61.7203 | 61.6608 | -61.2488 | -61.647 | -61.7111 | 0.064087 | 61.5601 | -61.6196 | 61.6058 | -61.4502 | -61.4685 | -61.4227 | -0.12817 | 0.041199 | 0.027466 | 0.34332 | -0.11902 | -0.054932 | 0.009155 | 0.073242 | -0.027466 | -0.073242 | -0.027466 | 0.14191 | 0.16937 | 0.1236 | 0.19684 | 0.15106 | 0.4715 | 123.381 | 0.16937 | 123.2254 | 123.3948 | 123.1796 | 123.2666 | 123.1522 | -123.3536 | -123.2529 | 123.2529 | 123.1979 | 61.5692 | 61.6562
504.4062 | 123.4268 | -61.6013 | 61.615 | 0.013199 | 0.0040995 | 0.069353 | 0.067152 | -0.0044285 | -0.00038018 | 0.00046565 | 0.0018005 | 0.0037319 | 0.069983 | 0.06345 | -0.0013714 | 0.016291 | 0.0053298 | -0.11902 | 61.6608 | -61.7661 | 61.5646 | -61.3678 | -61.7432 | -61.7798 | -0.073242 | 61.5692 | -61.6562 | 61.5463 | -61.5189 | -61.5417 | -61.4685 | -0.1648 | 0.045777 | -0.050354 | 0.23346 | -0.17853 | -0.14191 | -0.013733 | 0.022888 | -0.054932 | -0.045776 | -0.068664 | 0.082397 | 0.13275 | 0.059509 | 0.18768 | 0.11444 | 0.39825 | 123.3307 | 0.13733 | 123.2025 | 123.4268 | 123.2254 | 123.262 | 123.1705 | -123.381 | -123.2712 | 123.1659 | 123.1476 | 61.4822 | 61.528
506.0938 | 123.4634 | -61.5097 | 61.6974 | -0.0020601 | 0.0051675 | 0.06743 | 0.065016 | -0.00079686 | -0.0048664 | -0.001457 | -0.0043029 | 0.0056545 | 0.068701 | 0.056614 | -0.0030804 | 0.014795 | 0.0034072 | -0.045776 | 61.7065 | -61.6882 | 61.7065 | -61.1984 | -61.6013 | -61.6608 | 0.054932 | 61.6333 | -61.5463 | 61.6516 | -61.3907 | -61.4044 | -61.3678 | -0.17853 | 0.009155 | 0.009155 | 0.31128 | -0.15106 | -0.091552 | 0.027465 | 0.086975 | -0.036621 | -0.064087 | -0.045777 | 0.11902 | 0.14191 | 0.10529 | 0.17853 | 0.14191 | 0.48981 | 123.3948 | 0.15564 | 123.1979 | 123.3948 | 123.1796 | 123.2162 | 123.143 | -123.3856 | -123.2437 | 123.2162 | 123.1613 | 61.4639 | 61.5646
507.8281 | 123.4589 | -61.5005 | 61.6791 | 0.0055694 | 0.0036721 | 0.066789 | 0.065871 | 0.0015529 | -0.00080758 | -0.0020978 | -0.0043029 | 0.0035183 | 0.068701 | 0.073491 | -0.0039348 | 0.014368 | -0.0044968 | -0.027466 | 61.7386 | -61.6608 | 61.7203 | -61.1664 | -61.5829 | -61.6241 | 0.050354 | 61.6425 | -61.5601 | 61.6837 | -61.3678 | -61.3815 | -61.3541 | -0.16022 | 0.059509 | 0.041199 | 0.33417 | -0.1236 | -0.082398 | 0.036621 | 0.07782 | -0.05951 | -0.036621 | 0.004578 | 0.13275 | 0.14648 | 0.11902 | 0.20599 | 0.17853 | 0.49439 | 123.381 | 0.19226 | 123.2437 | 123.3994 | 123.2025 | 123.2391 | 123.143 | -123.3398 | -123.2391 | 123.2208 | 123.1842 | 61.4731 | 61.5509
509.5625 | 123.3398 | -61.4502 | 61.8164 | -0.0020601 | 0.0040995 | 0.069353 | 0.064803 | -0.0022923 | -0.0048664 | -0.00038875 | -0.0012513 | 0.0043729 | 0.070624 | 0.060032 | -0.0052166 | 0.013941 | 0.0010574 | -0.050354 | 61.8118 | -61.5784 | 61.7432 | -61.1755 | -61.5463 | -61.6013 | -0.036621 | 61.7386 | -61.5097 | 61.647 | -61.3907 | -61.4136 | -61.3403 | -0.12817 | -0.004577 | -0.073242 | 0.27466 | -0.15106 | -0.096131 | -0.022888 | 0.032043 | -0.05951 | -0.07782 | -0.16937 | 0.059509 | 0.10986 | 0.036621 | 0.16937 | 0.096131 | 0.40283 | 123.3215 | 0.11902 | 123.1567 | 123.3902 | 123.2483 | 123.262 | 123.1888 | -123.3948 | -123.3261 | 123.1934 | 123.0972 | 61.3998 | 61.4136
511.3281 | 123.4131 | -61.3449 | 61.8851 | -0.0020601 | 0.0021769 | 0.071062 | 0.062239 | 0.0011257 | -0.0044392 | 0.00046565 | -0.0073547 | 0.0039457 | 0.068274 | 0.057896 | -0.0028668 | 0.013727 | -0.0044968 | -0.036621 | 61.8713 | -61.496 | 61.8576 | -61.0428 | -61.4227 | -61.4639 | 0.032043 | 61.8164 | -61.3907 | 61.7844 | -61.2579 | -61.2671 | -61.2167 | -0.15106 | -0.013733 | -0.027466 | 0.30212 | -0.11902 | -0.077819 | 0.032044 | 0.073243 | -0.045776 | -0.068665 | -0.10071 | 0.086975 | 0.12817 | 0.07782 | 0.17395 | 0.1236 | 0.45319 | 123.3536 | 0.13275 | 123.175 | 123.3673 | 123.2071 | 123.2162 | 123.1613 | -123.381 | -123.2758 | 123.2025 | 123.1293 | 61.3083 | 61.377
513.0781 | 123.4909 | -61.2671 | 61.9171 | -0.0020601 | 0.0034585 | 0.06743 | 0.063948 | 0.00091214 | -0.003371 | -0.0038068 | -0.0012513 | 0.0045865 | 0.068701 | 0.06046 | -0.002226 | 0.014155 | -0.0042832 | -0.064087 | 61.9858 | -61.4182 | 61.9537 | -60.9329 | -61.3312 | -61.3815 | 0.073242 | 61.8668 | -61.3403 | 61.908 | -61.1252 | -61.1435 | -61.0977 | -0.15106 | 0.068665 | 0.036621 | 0.33417 | -0.11444 | -0.064087 | 0.036621 | 0.086975 | -0.073242 | -0.050354 | -0.009155 | 0.14191 | 0.16937 | 0.1236 | 0.24261 | 0.19684 | 0.48523 | 123.3719 | 0.21515 | 123.2483 | 123.4039 | 123.2071 | 123.2529 | 123.1338 | -123.3353 | -123.2574 | 123.2208 | 123.175 | 61.203 | 61.3403
514.8281 | 123.3856 | -61.2671 | 61.972 | 0.013199 | 0.0064493 | 0.070634 | 0.065443 | 0.0021939 | -0.0010212 | -0.00017515 | 0.0048523 | 0.0054409 | 0.069342 | 0.054905 | -0.001585 | 0.013086 | -0.0034286 | 0.018311 | 62.0361 | -61.4365 | 61.9125 | -61.0107 | -61.3907 | -61.441 | 0.050354 | 61.9492 | -61.322 | 61.8713 | -61.1938 | -61.2259 | -61.1526 | -0.16937 | 0.064087 | -0.059509 | 0.25635 | -0.17395 | -0.1236 | -0.004578 | 0.045776 | -0.054931 | -0.022888 | -0.10071 | 0.073242 | 0.11444 | 0.041199 | 0.16937 | 0.09613 | 0.42572 | 123.349 | 0.12817 | 123.1934 | 123.4726 | 123.2712 | 123.3032 | 123.2162 | -123.4085 | -123.2941 | 123.1796 | 123.1384 | 61.2854 | 61.3174
516.5312 | 123.3627 | -61.3266 | 61.9263 | 0.028458 | 0.0051675 | 0.069353 | 0.066725 | 0.0011257 | -0.0012348 | 0.00089285 | 0.014008 | 0.0069363 | 0.069556 | 0.060246 | -0.0030804 | 0.016718 | -0.0030014 | -0.041199 | 61.9858 | -61.528 | 61.8164 | -61.1298 | -61.4685 | -61.5189 | -0.013733 | 61.9034 | -61.3998 | 61.7706 | -61.2717 | -61.2808 | -61.2076 | -0.20142 | 0.059509 | -0.10986 | 0.19684 | -0.19226 | -0.14191 | 0.009155 | 0.059509 | -0.073242 | -0.022889 | -0.15564 | 0.054932 | 0.11902 | 0.045776 | 0.19226 | 0.11902 | 0.39825 | 123.3444 | 0.12817 | 123.1705 | 123.5138 | 123.3032 | 123.3124 | 123.23 | -123.4543 | -123.3261 | 123.143 | 123.0972 | 61.2854 | 61.3129
518.2812 | 123.3261 | -61.3541 | 61.8805 | -0.017319 | 0.0045267 | 0.068925 | 0.068007 | -0.00079686 | -0.0031574 | -0.0016706 | -0.0012513 | 0.0067227 | 0.070196 | 0.066014 | -0.0030804 | 0.016504 | -0.0017196 | -0.10529 | 61.9629 | -61.4914 | 61.734 | -61.1938 | -61.5692 | -61.5921 | -0.11902 | 61.8256 | -61.4319 | 61.702 | -61.3632 | -61.3907 | -61.2808 | -0.13733 | 0.082398 | -0.14648 | 0.16022 | -0.23804 | -0.21515 | -0.10071 | -0.07782 | -0.07782 | -0.054931 | -0.17853 | -0.009155 | 0.073242 | -0.036621 | 0.15106 | 0.041199 | 0.29755 | 123.2254 | 0.068665 | 123.1338 | 123.4543 | 123.2574 | 123.317 | 123.1796 | -123.3719 | -123.3124 | 123.0881 | 123.056 | 61.2488 | 61.235
520.0312 | 123.4543 | -61.3403 | 61.8393 | 0.0055694 | 0.0047403 | 0.06508 | 0.063521 | 0.0011257 | -0.0027302 | -0.0020978 | -0.0043029 | 0.0026639 | 0.072333 | 0.056614 | -0.0026532 | 0.01565 | -0.002147 | -0.054932 | 61.8851 | -61.5097 | 61.9125 | -60.965 | -61.3861 | -61.4548 | 0.050354 | 61.8027 | -61.377 | 61.8347 | -61.1938 | -61.1984 | -61.171 | -0.16937 | 0.045777 | 0.073243 | 0.37537 | -0.11444 | -0.045776 | 0.054932 | 0.1236 | -0.036621 | -0.036621 | -0.004577 | 0.14648 | 0.16937 | 0.14191 | 0.20599 | 0.17853 | 0.54474 | 123.4222 | 0.1831 | 123.2117 | 123.3948 | 123.1796 | 123.2254 | 123.143 | -123.349 | -123.2162 | 123.2529 | 123.175 | 61.2854 | 61.3907
521.7188 | 123.4451 | -61.4868 | 61.6882 | -0.0096891 | 0.0013223 | 0.067857 | 0.063521 | 0.0015529 | -0.0048664 | -0.00017515 | -0.0043029 | 0.0056545 | 0.07041 | 0.059605 | -0.0011578 | 0.015223 | -0.0010788 | -0.1831 | 61.7203 | -61.6608 | 61.7111 | -61.1526 | -61.5646 | -61.615 | -0.054932 | 61.6104 | -61.5417 | 61.647 | -61.3632 | -61.3907 | -61.3312 | -0.17395 | 0.032044 | 0.022889 | 0.33417 | -0.12817 | -0.07782 | 0.045777 | 0.096131 | -0.054932 | -0.077819 | -0.041198 | 0.1236 | 0.15564 | 0.09613 | 0.21057 | 0.15106 | 0.50812 | 123.3719 | 0.17853 | 123.1888 | 123.381 | 123.1522 | 123.2071 | 123.0972 | -123.349 | -123.23 | 123.1979 | 123.1338 | 61.3037 | 61.4319
523.4531 | 123.3215 | -61.2671 | 61.9812 | 0.013199 | 0.0058083 | 0.068712 | 0.063521 | -0.00079686 | -0.0012348 | 0.0011066 | 0.0018005 | 0.0050137 | 0.069769 | 0.056187 | -0.0086346 | 0.015009 | -0.0017196 | -0.073242 | 62.0407 | -61.4273 | 61.8484 | -61.0428 | -61.4227 | -61.4548 | -0.050354 | 61.9263 | -61.3266 | 61.7935 | -61.2442 | -61.2488 | -61.1801 | -0.16022 | 0.059509 | -0.13275 | 0.2243 | -0.18768 | -0.15564 | -0.027466 | 0.004578 | -0.059509 | -0.054931 | -0.18768 | 0.022888 | 0.086975 | 0.018311 | 0.14648 | 0.07782 | 0.38452 | 123.2758 | 0.082397 | 123.1201 | 123.468 | 123.2529 | 123.3078 | 123.1934 | -123.4085 | -123.3078 | 123.1155 | 123.0606 | 61.1938 | 61.2167
525.2031 | 123.4131 | -61.1938 | 61.9675 | 0.028458 | 0.0051675 | 0.071916 | 0.066725 | -0.0014377 | -0.0018756 | 0.00025205 | 0.014008 | 0.0060819 | 0.071478 | 0.065159 | 0.00055117 | 0.013514 | -0.0027878 | -0.054932 | 62.0728 | -61.3403 | 62.0544 | -60.8322 | -61.2579 | -61.2808 | 0.032043 | 61.9629 | -61.2396 | 61.9766 | -61.0886 | -61.116 | -61.0428 | -0.14648 | 0.10529 | 0.086975 | 0.36163 | -0.086975 | -0.064087 | 0.059509 | 0.082397 | -0.045776 | -0.004577 | 0.009156 | 0.10529 | 0.15106 | 0.07782 | 0.19684 | 0.1236 | 0.50812 | 123.3948 | 0.15106 | 123.2162 | 123.4131 | 123.2025 | 123.2666 | 123.1567 | -123.3078 | -123.2071 | 123.2483 | 123.1705 | 61.1389 | 61.2259
526.9688 | 123.3215 | -61.2991 | 61.9583 | 0.0055694 | 0.0047403 | 0.069353 | 0.068861 | -0.0018649 | -0.001662 | -0.0016706 | 0.0018005 | 0.0060819 | 0.071051 | 0.056828 | -0.00094423 | 0.017573 | -0.0057786 | -0.036621 | 62.0224 | -61.4548 | 61.821 | -61.0886 | -61.5051 | -61.5189 | -0.054932 | 61.8713 | -61.3266 | 61.7661 | -61.2854 | -61.3266 | -61.2167 | -0.15564 | 0.064087 | -0.13733 | 0.21057 | -0.21973 | -0.20599 | -0.064087 | -0.050354 | -0.027466 | -0.086975 | -0.19226 | 0.013733 | 0.082397 | -0.027466 | 0.10986 | 0 | 0.36621 | 123.2758 | 0.041199 | 123.0927 | 123.4772 | 123.1979 | 123.3215 | 123.1705 | -123.4131 | -123.2849 | 123.1201 | 123.0652 | 61.2625 | 61.2442
528.6406 | 123.3307 | -61.2396 | 61.9766 | 0.0055694 | 0.0036721 | 0.068071 | 0.066084 | 0.0015529 | -0.001662 | -0.001457 | -0.0012513 | 0.0050137 | 0.071265 | 0.06345 | -0.0024396 | 0.01565 | -0.003856 | -0.10529 | 62.0636 | -61.409 | 61.8393 | -61.0703 | -61.4777 | -61.4731 | -0.11444 | 61.9354 | -61.2946 | 61.8164 | -61.2442 | -61.2762 | -61.1572 | -0.16937 | 0.086975 | -0.13733 | 0.16937 | -0.23346 | -0.23804 | -0.064086 | -0.068664 | -0.054932 | -0.041199 | -0.16022 | -0.004578 | 0.082397 | -0.036621 | 0.13733 | 0.018311 | 0.33875 | 123.2483 | 0.050354 | 123.111 | 123.4726 | 123.23 | 123.3032 | 123.175 | -123.3856 | -123.2712 | 123.0789 | 123.056 | 61.1343 | 61.1252
530.4062 | 123.3902 | -61.3083 | 61.8759 | 0.043716 | 0.0030313 | 0.070207 | 0.066084 | 0.00027134 | -0.0018756 | 0.0013202 | 0.0079041 | 0.0052273 | 0.069983 | 0.061741 | -0.0028668 | 0.016077 | -0.0010788 | -0.12817 | 61.9217 | -61.4777 | 61.8484 | -61.0199 | -61.4136 | -61.4502 | -0.041199 | 61.8484 | -61.3449 | 61.8118 | -61.2305 | -61.2442 | -61.171 | -0.16937 | 0.045776 | -0.027466 | 0.28839 | -0.14191 | -0.10528 | 0.027466 | 0.064087 | -0.036621 | -0.027466 | -0.064087 | 0.07782 | 0.13733 | 0.064087 | 0.17395 | 0.10071 | 0.45776 | 123.3261 | 0.11444 | 123.1567 | 123.3994 | 123.1934 | 123.23 | 123.1567 | -123.3536 | -123.2208 | 123.1567 | 123.1201 | 61.1801 | 61.2671
532.1719 | 123.3261 | -61.2808 | 61.9812 | -0.0096891 | 0.0055947 | 0.068498 | 0.066084 | 0.0034755 | -0.0025166 | 0.00067925 | 0.0048523 | 0.0048001 | 0.071692 | 0.056614 | -0.0030804 | 0.017145 | -0.0002244 | -0.045776 | 62.0224 | -61.4182 | 61.8576 | -61.0382 | -61.4502 | -61.5005 | -0.073242 | 61.8942 | -61.3174 | 61.7798 | -61.2717 | -61.3129 | -61.1893 | -0.13733 | 0.041199 | -0.1236 | 0.24262 | -0.21973 | -0.16937 | -0.082397 | -0.032043 | -0.036621 | -0.086975 | -0.20142 | 0.009156 | 0.091553 | -0.032043 | 0.12817 | 0.004578 | 0.37994 | 123.2758 | 0.045777 | 123.0972 | 123.4406 | 123.2117 | 123.3032 | 123.175 | -123.3994 | -123.2986 | 123.1384 | 123.0606 | 61.235 | 61.2076
533.9062 | 123.3353 | -62.4252 | 60.7773 | -0.0020601 | 0.0053811 | 0.069566 | 0.066084 | 0.0011257 | -0.0040118 | -0.0012434 | -0.0012513 | 0.0058683 | 0.070837 | 0.061955 | -0.00094423 | 0.015223 | 0.0006302 | -0.12817 | 60.8597 | -62.5626 | 60.6537 | -62.2192 | -62.6266 | -62.6312 | -0.10986 | 60.7224 | -62.4985 | 60.6628 | -62.3978 | -62.4161 | -62.3154 | -0.13733 | 0.082397 | -0.1236 | 0.20599 | -0.20599 | -0.20142 | -0.068665 | -0.064087 | -0.073242 | -0.054932 | -0.11444 | 0.027466 | 0.10986 | 0.009155 | 0.18311 | 0.082397 | 0.34332 | 123.2162 | 0.10071 | 123.1613 | 123.4222 | 123.2208 | 123.2849 | 123.1476 | -123.3398 | -123.2758 | 123.0789 | 123.0881 | 62.2971 | 62.3154
535.5938 | 123.3032 | -62.2971 | 60.9283 | -0.0096891 | 0.0045267 | 0.068712 | 0.064162 | -0.00015586 | -0.0035846 | -0.0016706 | -0.0073547 | 0.0062955 | 0.069769 | 0.060887 | -0.0052166 | 0.015436 | -0.0010788 | -0.086975 | 60.997 | -62.4527 | 60.7819 | -62.0682 | -62.4527 | -62.4893 | -0.032043 | 60.9146 | -62.3657 | 60.7269 | -62.265 | -62.2879 | -62.2055 | -0.15564 | 0.068664 | -0.14648 | 0.22888 | -0.19226 | -0.15564 | -0.036621 | 0 | -0.068665 | -0.013733 | -0.20142 | 0.032043 | 0.091553 | 0.009155 | 0.16022 | 0.07782 | 0.38452 | 123.2346 | 0.10071 | 123.0927 | 123.4497 | 123.2803 | 123.2941 | 123.2117 | -123.381 | -123.2941 | 123.0789 | 123.024 | 62.2101 | 62.265
537.3594 | 123.436 | -62.3291 | 60.7956 | -0.0020601 | 0.0045267 | 0.067217 | 0.064803 | 0.0032619 | -0.0027302 | -0.00081595 | -0.0012513 | 0.0030911 | 0.069769 | 0.061955 | -0.0030804 | 0.014795 | -0.0036422 | -0.054932 | 60.8505 | -62.5122 | 60.8643 | -61.9675 | -62.3703 | -62.4207 | 0.032043 | 60.7956 | -62.3703 | 60.8047 | -62.1689 | -62.1918 | -62.1643 | -0.1831 | 0.054932 | 0.068665 | 0.36163 | -0.091552 | -0.041198 | 0.091553 | 0.14191 | -0.041198 | 0 | 0.009156 | 0.16022 | 0.16479 | 0.13733 | 0.20599 | 0.17853 | 0.54474 | 123.3765 | 0.20142 | 123.175 | 123.3627 | 123.1659 | 123.1796 | 123.1247 | -123.3078 | -123.1659 | 123.1934 | 123.1339 | 62.2742 | 62.3611
539.1094 | 123.317 | -62.3749 | 60.8414 | 0.0055694 | 0.0049539 | 0.068498 | 0.062239 | 0.0011257 | -0.0037982 | -0.00081595 | -0.0012513 | 0.0041593 | 0.069556 | 0.060673 | -0.0030804 | 0.014582 | -0.0040696 | -0.032043 | 60.8505 | -62.5076 | 60.7819 | -62.0636 | -62.4481 | -62.4939 | 0.009155 | 60.7727 | -62.4298 | 60.6949 | -62.2971 | -62.3062 | -62.2513 | -0.13275 | 0.009155 | -0.05951 | 0.31128 | -0.11902 | -0.073242 | 0.013733 | 0.059509 | -0.054932 | -0.068665 | -0.14648 | 0.07782 | 0.1236 | 0.068665 | 0.17853 | 0.1236 | 0.44403 | 123.2895 | 0.13275 | 123.1247 | 123.3582 | 123.2025 | 123.2254 | 123.1476 | -123.349 | -123.2712 | 123.1567 | 123.0698 | 62.3428 | 62.384
540.875 | 123.2895 | -62.3428 | 60.91 | 0.0055694 | 0.0032449 | 0.069566 | 0.068007 | -0.0018649 | -0.003371 | -0.00017515 | 0.017059 | 0.0077909 | 0.070624 | 0.064732 | -0.0043622 | 0.013727 | -0.0019332 | -0.022888 | 60.9787 | -62.5351 | 60.7773 | -62.0911 | -62.4527 | -62.471 | -0.045776 | 60.8643 | -62.4207 | 60.7178 | -62.2787 | -62.2971 | -62.2055 | -0.19226 | 0.068665 | -0.13275 | 0.25177 | -0.12817 | -0.10986 | 0.064087 | 0.082397 | -0.07782 | -0.045776 | -0.19226 | 0.064086 | 0.13733 | 0.045776 | 0.21515 | 0.1236 | 0.44403 | 123.3124 | 0.14191 | 123.1384 | 123.5138 | 123.2849 | 123.3215 | 123.2071 | -123.4451 | -123.3307 | 123.1201 | 123.0606 | 62.3199 | 62.2971
542.625 | 123.3627 | -62.4344 | 60.7773 | 0.028458 | 0.0038857 | 0.069353 | 0.066298 | 0.00027134 | -0.003371 | -0.001457 | 0.0079041 | 0.0030911 | 0.070837 | 0.062596 | -0.0017986 | 0.015223 | -0.0059922 | -0.11902 | 60.8093 | -62.5671 | 60.7269 | -62.114 | -62.5305 | -62.5534 | -0.059509 | 60.704 | -62.471 | 60.672 | -62.3474 | -62.3474 | -62.2833 | -0.13275 | 0.032043 | -0.050354 | 0.32043 | -0.11902 | -0.096131 | 0.013733 | 0.036621 | -0.036621 | -0.073242 | -0.10529 | 0.086975 | 0.15106 | 0.086975 | 0.18768 | 0.1236 | 0.45319 | 123.2941 | 0.1236 | 123.143 | 123.3765 | 123.175 | 123.2437 | 123.1384 | -123.3444 | -123.2483 | 123.1613 | 123.1064 | 62.3154 | 62.3749
544.3125 | 123.3536 | -62.4893 | 60.6583 | 0.020828 | 0.0043131 | 0.070421 | 0.066298 | 0.0019803 | -0.0023028 | -0.0027386 | 0.0048523 | 0.0020231 | 0.069983 | 0.063023 | -0.001585 | 0.015009 | -1.0598e-05 | -0.12817 | 60.7132 | -62.6587 | 60.6171 | -62.2421 | -62.6358 | -62.6587 | -0.059509 | 60.6308 | -62.5763 | 60.5896 | -62.4207 | -62.4344 | -62.3611 | -0.16937 | 0.054932 | -0.041199 | 0.24719 | -0.16937 | -0.14648 | 0 | 0.022888 | -0.086975 | -0.027466 | -0.068664 | 0.068665 | 0.12817 | 0.054932 | 0.21515 | 0.14191 | 0.41656 | 123.2758 | 0.15564 | 123.1659 | 123.3719 | 123.2071 | 123.2025 | 123.1201 | -123.317 | -123.2346 | 123.1064 | 123.0789 | 62.3611 | 62.4298
546.0625 | 110.6277 | -118.5562 | 4.6051 | -0.0020601 | 0.00089511 | 0.070848 | 0.06523 | 0.00048494 | -0.0027302 | 0.0017474 | -0.0012513 | 0.0022367 | 0.069556 | 0.05811 | -0.0020122 | 0.017359 | -0.0012924 | -0.31586 | 4.8798 | -118.5333 | 4.7974 | -117.6636 | -118.3777 | -118.5928 | -0.45776 | 4.747 | -118.6249 | 4.5776 | -118.1763 | -118.2678 | -118.1671 | 0.022888 | 0.27466 | 0.19226 | 0.89264 | -0.036621 | 0.17853 | -0.059509 | 0.15564 | -0.068665 | 0.14191 | -0.027466 | 0.37994 | 0.3891 | 0.28839 | 0.45776 | 0.35706 | 0.86975 | 123.3307 | 0.44861 | 123.2025 | 123.4131 | 123.3719 | 123.436 | 123.3032 | -123.1384 | -123.23 | 123.3536 | 123.1338 | 118.2404 | 118.0984
547.8281 | 123.3353 | -120.3918 | 2.8244 | -0.0096891 | 0.0040995 | 0.071275 | 0.068221 | 0.0021939 | -0.0027302 | -0.0012434 | -0.0043029 | 0.0071499 | 0.068488 | 0.050633 | -0.001585 | 0.016291 | -0.0036422 | -0.32501 | 2.8748 | -120.575 | 2.5818 | -119.8471 | -120.4605 | -120.5292 | -0.37079 | 2.7878 | -120.5475 | 2.6825 | -120.1035 | -120.1721 | -120.0348 | -0.1831 | 0.050354 | -0.24262 | 0.54474 | -0.13733 | -0.068664 | 0.045776 | 0.11444 | -0.15564 | -0.036621 | -0.14191 | 0.28839 | 0.35706 | 0.21973 | 0.51269 | 0.37537 | 0.72784 | 123.1567 | 0.44403 | 123.23 | 123.4497 | 123.3353 | 123.2666 | 123.1796 | -123.3994 | -123.3719 | 122.9736 | 123.0743 | 120.0668 | 120.0211
549.5156 | 123.3765 | -120.7581 | 2.4857 | 0.028458 | 0.0053811 | 0.072984 | 0.066084 | -0.0012241 | -0.0025166 | -0.001457 | 0.0048523 | 0.0043729 | 0.071905 | 0.064518 | -0.00051703 | 0.018 | -0.0057786 | -0.52643 | 2.8152 | -120.7581 | 2.4307 | -119.989 | -120.5933 | -120.6848 | -0.50354 | 2.5406 | -120.7489 | 2.4216 | -120.3278 | -120.4147 | -120.3278 | 0 | 0.32959 | -0.054932 | 0.76904 | 0.073243 | 0.16479 | 0.073243 | 0.16479 | 0.009156 | 0.054931 | -0.064087 | 0.4303 | 0.4303 | 0.34332 | 0.42114 | 0.33417 | 0.76904 | 123.1888 | 0.42114 | 123.1705 | 123.5733 | 123.2895 | 123.5733 | 123.2986 | -123.2437 | -123.2346 | 123.1888 | 123.1796 | 120.2316 | 120.2545
551.2656 | 123.317 | -121.0831 | 2.2064 | 0.058975 | 0.0034585 | 0.072557 | 0.067366 | -0.00015586 | -0.0018756 | 0.00025205 | 0.0079041 | 0.0060819 | 0.068701 | 0.058751 | -0.0037212 | 0.012018 | -0.0025742 | 0.48523 | 2.0554 | -121.2296 | 1.5747 | -120.7718 | -121.2387 | -121.1151 | 0.14648 | 2.0828 | -121.2341 | 1.9684 | -120.7397 | -120.7352 | -120.6024 | -0.14648 | -0.15106 | -0.63171 | 0.31128 | -0.032043 | -0.15564 | 0.11444 | -0.009155 | -0.15106 | -0.1236 | -0.23804 | 0.34332 | 0.48065 | 0.3479 | 0.63171 | 0.49896 | 0.45776 | 122.8043 | 0.49439 | 123.2025 | 123.2849 | 123.317 | 123.1384 | 123.1659 | -123.436 | -123.4406 | 122.6578 | 123.0515 | 121.5683 | 121.2296
553.0156 | 123.3627 | -122.4518 | 0.7782 | 0.020828 | 0.0017495 | 0.069566 | 0.066725 | 0.0034755 | -0.0027302 | -0.00060235 | 0.0079041 | 0.0039457 | 0.069983 | 0.063237 | -0.0020122 | 0.015223 | 0.0006302 | -0.2655 | 0.82855 | -122.6028 | 0.6546 | -121.7697 | -122.3648 | -122.4472 | -0.24719 | 0.77362 | -122.5296 | 0.69122 | -122.049 | -122.1039 | -121.9894 | -0.15106 | 0.050354 | -0.1236 | 0.68207 | 0.004577 | 0.086975 | 0.15564 | 0.23804 | -0.07782 | -0.004577 | -0.086975 | 0.40283 | 0.46234 | 0.3479 | 0.54016 | 0.42572 | 0.83313 | 123.2574 | 0.48065 | 123.2208 | 123.4314 | 123.3032 | 123.2803 | 123.2254 | -123.381 | -123.3078 | 123.1064 | 123.143 | 122.1863 | 122.2046
554.6875 | 123.3582 | -122.4197 | 0.81482 | 0.028458 | 0.0053811 | 0.070634 | 0.065871 | 0.0041165 | -0.0027302 | -0.00038875 | 0.0048523 | 0.0041593 | 0.070196 | 0.069859 | 0.00012397 | 0.014795 | -1.0598e-05 | -0.22888 | 0.84228 | -122.6212 | 0.71869 | -121.6965 | -122.3465 | -122.4106 | -0.14648 | 0.80109 | -122.4838 | 0.6958 | -122.0352 | -122.0261 | -121.9528 | -0.20142 | 0.027466 | -0.09613 | 0.72327 | 0.009156 | 0.073242 | 0.21057 | 0.27466 | -0.064087 | -0.013733 | -0.11902 | 0.38452 | 0.46692 | 0.39368 | 0.53101 | 0.45776 | 0.92468 | 123.3398 | 0.44861 | 123.1796 | 123.4634 | 123.2849 | 123.262 | 123.2208 | -123.436 | -123.2986 | 123.1384 | 123.1155 | 122.1909 | 122.2733
556.4531 | 123.3078 | -122.58 | 0.68207 | 0.013199 | 0.0053811 | 0.071275 | 0.06758 | 0.00027134 | -0.0025166 | -0.0010298 | 0.0018005 | 0.0048001 | 0.072546 | 0.061314 | -0.0039348 | 0.015436 | -1.0598e-05 | -0.14648 | 0.68207 | -122.7585 | 0.52185 | -121.8704 | -122.4976 | -122.6028 | -0.13275 | 0.65002 | -122.6257 | 0.57678 | -122.168 | -122.2504 | -122.1085 | -0.17853 | 0 | -0.16022 | 0.70953 | -0.022888 | 0.082397 | 0.15564 | 0.26093 | -0.045776 | -0.032044 | -0.10529 | 0.41199 | 0.4715 | 0.32959 | 0.51727 | 0.37537 | 0.88806 | 123.2803 | 0.45776 | 123.2025 | 123.4406 | 123.2758 | 123.262 | 123.23 | -123.4406 | -123.3078 | 123.1018 | 123.1567 | 122.4335 | 122.4472
558.2031 | 123.3261 | -122.2046 | 1.062 | 0.028458 | 0.0066629 | 0.069566 | 0.065657 | 0.0017667 | -0.0035846 | 0.0015338 | 0.0048523 | 0.0039457 | 0.06806 | 0.067723 | -0.002226 | 0.014368 | -0.0002244 | -0.19684 | 1.0803 | -122.4655 | 0.84686 | -121.5363 | -122.1222 | -122.2366 | -0.1831 | 1.0437 | -122.2824 | 0.91553 | -121.7926 | -121.8658 | -121.7331 | -0.26093 | 0.01831 | -0.21515 | 0.66833 | -0.032043 | 0.082398 | 0.22888 | 0.34332 | -0.07782 | -0.018311 | -0.14648 | 0.41199 | 0.4715 | 0.33875 | 0.54932 | 0.41657 | 0.92926 | 123.3124 | 0.48981 | 123.1979 | 123.5458 | 123.3261 | 123.2849 | 123.2483 | -123.5275 | -123.3444 | 123.0515 | 123.1201 | 122.0078 | 122.0215
559.8906 | 123.4085 | -122.3053 | 0.93384 | -0.0096891 | 0.0036721 | 0.069353 | 0.063307 | 0.0034755 | -0.0025166 | 0.00025205 | -0.0012513 | 0.0018093 | 0.068915 | 0.056828 | -0.0035076 | 0.015436 | 0.0008438 | -0.21515 | 0.86517 | -122.4792 | 0.77362 | -121.5958 | -122.2 | -122.3099 | -0.11902 | 0.85602 | -122.3969 | 0.88806 | -121.8292 | -121.875 | -121.7743 | -0.17395 | -0.068665 | -0.16022 | 0.70953 | -0.004577 | 0.10529 | 0.16937 | 0.27924 | -0.091553 | -0.07782 | -0.045776 | 0.47607 | 0.53101 | 0.4303 | 0.62256 | 0.52185 | 0.88348 | 123.2529 | 0.56763 | 123.2849 | 123.3444 | 123.2529 | 123.1705 | 123.1613 | -123.4131 | -123.3307 | 123.0789 | 123.1934 | 122.0901 | 122.1863
561.6406 | 123.2758 | -122.4014 | 0.88806 | -0.0020601 | 0.0040995 | 0.072771 | 0.063521 | 0.0015529 | -0.0044392 | 0.0017474 | -0.0043029 | 0.0048001 | 0.071051 | 0.057469 | -0.0047894 | 0.015223 | -0.0017196 | -0.17853 | 0.84228 | -122.5616 | 0.68665 | -121.6782 | -122.2824 | -122.4014 | -0.18768 | 0.84228 | -122.438 | 0.6958 | -121.994 | -122.0581 | -121.962 | -0.16022 | -0.045777 | -0.20142 | 0.72327 | 0 | 0.11902 | 0.16022 | 0.27924 | -0.036621 | -0.045777 | -0.19226 | 0.40741 | 0.43945 | 0.34332 | 0.47607 | 0.37994 | 0.88348 | 123.2483 | 0.44403 | 123.1339 | 123.4039 | 123.2803 | 123.2437 | 123.2437 | -123.4497 | -123.3261 | 123.0881 | 123.0972 | 122.2229 | 122.2137
563.3906 | 123.3673 | -122.3602 | 0.85144 | -0.0020601 | 0.0036721 | 0.068925 | 0.066084 | 0.0049709 | -0.0027302 | -0.00081595 | -0.0012513 | 0.0067227 | 0.07041 | 0.061741 | 0.00097837 | 0.015436 | -0.0036422 | -0.25177 | 0.8606 | -122.5845 | 0.67291 | -121.7102 | -122.3602 | -122.4426 | -0.1831 | 0.8194 | -122.4335 | 0.80566 | -121.9391 | -122.0078 | -121.875 | -0.22431 | 0.009156 | -0.17853 | 0.65002 | -0.082398 | 0 | 0.14191 | 0.22431 | -0.073243 | -0.032043 | -0.045776 | 0.42114 | 0.48523 | 0.35248 | 0.55847 | 0.42572 | 0.87433 | 123.2574 | 0.49438 | 123.2391 | 123.4451 | 123.2529 | 123.2208 | 123.1796 | -123.436 | -123.2849 | 123.0331 | 123.1659 | 122.1085 | 122.1771
565.1406 | 123.3536 | -122.319 | 0.84686 | -0.0096891 | 0.0026041 | 0.069994 | 0.066939 | 0.0041165 | -0.00080758 | -0.0010298 | -0.0012513 | 0.0060819 | 0.069556 | 0.060246 | -8.9634e-05 | 0.018427 | 0.000203 | -0.23804 | 0.90179 | -122.5113 | 0.69122 | -121.6873 | -122.3053 | -122.3831 | -0.16479 | 0.8194 | -122.4152 | 0.82398 | -121.907 | -121.9803 | -121.8201 | -0.19226 | 0.054931 | -0.15564 | 0.63171 | -0.064087 | 0.013733 | 0.12817 | 0.20599 | -0.09613 | -0.027466 | -0.022888 | 0.41199 | 0.49896 | 0.33874 | 0.59509 | 0.43487 | 0.82398 | 123.2025 | 0.50812 | 123.2391 | 123.4131 | 123.2346 | 123.2208 | 123.1384 | -123.3582 | -123.262 | 123.0103 | 123.143 | 122.081 | 122.1542
566.8906 | 123.3261 | -122.438 | 0.77362 | -0.0020601 | 0.0045267 | 0.070634 | 0.063735 | 0.0045437 | -0.0035846 | 0.00046565 | -0.0012513 | 0.0035183 | 0.06806 | 0.058537 | -0.0054302 | 0.014368 | -0.001506 | -0.21515 | 0.75531 | -122.6166 | 0.6546 | -121.6965 | -122.3053 | -122.4426 | -0.15106 | 0.737 | -122.5159 | 0.67749 | -121.9986 | -122.0627 | -121.9803 | -0.17853 | -0.018311 | -0.11902 | 0.74158 | -0.004578 | 0.13275 | 0.17395 | 0.31128 | -0.07782 | -0.036621 | -0.096131 | 0.43945 | 0.45776 | 0.37537 | 0.53558 | 0.45319 | 0.92011 | 123.2712 | 0.51727 | 123.1934 | 123.3719 | 123.2529 | 123.1934 | 123.175 | -123.3902 | -123.2895 | 123.0927 | 123.1155 | 122.2229 | 122.287
568.5625 | 123.3627 | -122.2275 | 0.9613 | 0.043716 | 0.0043131 | 0.074052 | 0.066298 | 0.0047573 | 0.00068782 | -0.00038875 | 0.014008 | 0.0043729 | 0.072974 | 0.065159 | -0.001585 | 0.015223 | -0.0030014 | -0.15106 | 0.94757 | -122.4289 | 0.89722 | -121.4722 | -122.1313 | -122.2366 | -0.07782 | 0.91095 | -122.3419 | 0.93384 | -121.7789 | -121.843 | -121.7377 | -0.20142 | -0.013733 | -0.064087 | 0.75531 | -0.009155 | 0.09613 | 0.19226 | 0.29755 | -0.11444 | -0.050354 | -0.027466 | 0.44861 | 0.48981 | 0.38452 | 0.60425 | 0.49896 | 0.95673 | 123.3261 | 0.56305 | 123.2758 | 123.3765 | 123.2529 | 123.175 | 123.1384 | -123.3902 | -123.3032 | 123.1247 | 123.1613 | 122.0764 | 122.1497
570.3125 | 123.2346 | -122.168 | 1.0712 | -0.0020601 | 0.0047403 | 0.070421 | 0.064803 | 0.0066799 | -0.0020892 | 0.00067925 | 0.0018005 | 0.0056545 | 0.069342 | 0.054692 | -0.00094423 | 0.017145 | -1.0598e-05 | -0.21973 | 1.0666 | -122.3694 | 0.81024 | -121.5729 | -122.1771 | -122.2641 | -0.24261 | 1.0574 | -122.2092 | 0.90179 | -121.8338 | -121.8979 | -121.7285 | -0.20142 | -0.004578 | -0.26092 | 0.59509 | -0.09613 | -0.009155 | 0.10529 | 0.19226 | -0.041198 | -0.013733 | -0.16937 | 0.33417 | 0.43945 | 0.27008 | 0.48065 | 0.31128 | 0.79651 | 123.1796 | 0.37537 | 123.111 | 123.436 | 123.2666 | 123.2346 | 123.2254 | -123.4406 | -123.2803 | 122.9782 | 123.0698 | 121.9482 | 121.9254
572.0625 | 123.2758 | -122.2366 | 0.99792 | 0.043716 | 0.0051675 | 0.072343 | 0.06758 | 0.0011257 | -0.0031574 | 0.00089285 | 0.010956 | 0.0075771 | 0.067847 | 0.057682 | -0.0028668 | 0.01565 | -0.0012924 | -0.14648 | 1.03 | -122.4701 | 0.79651 | -121.55 | -122.1588 | -122.2595 | -0.14648 | 0.98877 | -122.319 | 0.8606 | -121.8292 | -121.8933 | -121.7606 | -0.23346 | 0.032043 | -0.20142 | 0.68664 | -0.022888 | 0.07782 | 0.21057 | 0.31128 | -0.082398 | -0.009155 | -0.13733 | 0.40741 | 0.47607 | 0.34332 | 0.55847 | 0.42572 | 0.92011 | 123.2666 | 0.48981 | 123.1796 | 123.5001 | 123.3078 | 123.2666 | 123.2254 | -123.468 | -123.317 | 123.0331 | 123.0972 | 122.0901 | 122.0901
573.7969 | 123.262 | -122.1909 | 1.0345 | 0.0055694 | 0.0047403 | 0.06978 | 0.064375 | 0.00069854 | -0.0025166 | -0.004875 | -0.0012513 | 0.0052273 | 0.071051 | 0.064305 | -0.0020122 | 0.01565 | -0.000438 | -0.24261 | 1.0391 | -122.3785 | 0.77362 | -121.5912 | -122.2092 | -122.2961 | -0.23346 | 1.0071 | -122.3007 | 0.88348 | -121.8475 | -121.8979 | -121.7514 | -0.18768 | 0.004578 | -0.26092 | 0.59967 | -0.10529 | -0.01831 | 0.082397 | 0.16937 | -0.10986 | -0.027466 | -0.15106 | 0.34332 | 0.43945 | 0.29297 | 0.54932 | 0.40283 | 0.78735 | 123.1522 | 0.45319 | 123.1842 | 123.4177 | 123.3078 | 123.23 | 123.1979 | -123.4131 | -123.3353 | 122.9645 | 123.0743 | 121.9482 | 121.9574
575.4844 | 123.381 | -121.9666 | 1.1993 | -0.0096891 | 0.0030313 | 0.06978 | 0.064589 | 0.00027134 | -0.0048664 | -0.003166 | -0.0012513 | 0.0022367 | 0.069983 | 0.063023 | -0.0026532 | 0.017359 | -0.0010788 | -0.21515 | 1.1627 | -122.1771 | 1.0895 | -121.2296 | -121.8613 | -121.9666 | -0.068665 | 1.1444 | -122.0398 | 1.1993 | -121.4584 | -121.5271 | -121.4401 | -0.21057 | -0.036621 | -0.10986 | 0.737 | 0 | 0.10529 | 0.21057 | 0.31586 | -0.073242 | -0.054932 | 0 | 0.50812 | 0.52643 | 0.43945 | 0.59967 | 0.51269 | 0.94757 | 123.2666 | 0.58136 | 123.2391 | 123.3398 | 123.1842 | 123.1293 | 123.111 | -123.3765 | -123.2391 | 123.056 | 123.1659 | 121.7514 | 121.8979
577.1875 | 123.3582 | -121.6095 | 1.5427 | -0.0020601 | 0.0038857 | 0.069566 | 0.064162 | 0.0047573 | -0.0031574 | -0.0016706 | 0.0018005 | 0.0054409 | 0.067847 | 0.061741 | -0.0024396 | 0.015436 | -0.0042832 | -0.20142 | 1.4877 | -121.8109 | 1.4328 | -120.8725 | -121.4859 | -121.6187 | -0.09613 | 1.4923 | -121.701 | 1.4969 | -121.138 | -121.1792 | -121.0922 | -0.20142 | -0.054932 | -0.10986 | 0.737 | -0.009155 | 0.1236 | 0.19226 | 0.32501 | -0.091553 | -0.050354 | -0.045777 | 0.4715 | 0.51727 | 0.4303 | 0.60883 | 0.52185 | 0.93842 | 123.2437 | 0.56305 | 123.1979 | 123.2986 | 123.1934 | 123.0972 | 123.1018 | -123.3536 | -123.2437 | 123.0423 | 123.1064 | 121.4081 | 121.5134
578.9375 | 123.2803 | -121.3989 | 1.767 | 0.0055694 | 0.0049539 | 0.068925 | 0.066512 | 5.774e-05 | -0.00059378 | 0.0017474 | 0.023163 | 0.0069363 | 0.070837 | 0.054478 | -0.00094423 | 0.011805 | -0.0023606 | -0.29297 | 1.8448 | -121.8063 | 1.2772 | -121.1014 | -121.6644 | -121.7789 | -0.26093 | 1.442 | -121.8292 | 1.6113 | -121.1792 | -121.2845 | -120.8679 | -0.40741 | 0.07782 | -0.48981 | 0.29755 | -0.37994 | -0.2655 | 0.027465 | 0.14191 | -0.4303 | -0.32501 | -0.15564 | 0.21973 | 0.53101 | 0.11444 | 0.9613 | 0.54474 | 0.70496 | 123.0835 | 0.65002 | 123.4406 | 123.6511 | 123.2712 | 123.2437 | 122.8409 | -123.5733 | -123.5962 | 122.6761 | 123.0103 | 121.106 | 121.138
580.625 | 123.2254 | -122.0306 | 1.181 | -0.0020601 | 0.0066629 | 0.070421 | 0.066939 | 0.0075345 | -0.0020892 | -0.0023114 | -0.0073547 | 0.0048001 | 0.07276 | 0.063023 | -0.0020122 | 0.015436 | -0.001506 | -0.17395 | 1.1581 | -122.2458 | 0.97046 | -121.4081 | -122.0444 | -122.113 | -0.16937 | 1.1444 | -122.1222 | 1.0208 | -121.6965 | -121.7606 | -121.6232 | -0.21515 | -0.022888 | -0.21057 | 0.62256 | -0.082397 | -0.013733 | 0.13275 | 0.20142 | -0.091552 | -0.036621 | -0.16022 | 0.33417 | 0.40741 | 0.27008 | 0.49896 | 0.36163 | 0.83771 | 123.2162 | 0.42572 | 123.143 | 123.4039 | 123.2666 | 123.1888 | 123.175 | -123.4268 | -123.3032 | 123.0011 | 123.0515 | 121.8567 | 121.8613
582.3906 | 123.3353 | -121.7697 | 1.4465 | 0.013199 | 0.0034585 | 0.069994 | 0.06523 | 0.0026211 | -0.0031574 | -0.0029524 | -0.0012513 | 0.0022367 | 0.068915 | 0.066014 | -0.003294 | 0.016291 | -0.0017196 | -0.28839 | 1.2543 | -122.0718 | 1.0986 | -121.2296 | -121.8384 | -121.8842 | 0.07782 | 1.3 | -121.6553 | 1.3733 | -121.2662 | -121.3165 | -121.2387 | -0.30212 | -0.19226 | -0.3479 | 0.54016 | -0.11444 | -0.068665 | 0.18768 | 0.23346 | 0.11444 | -0.14648 | -0.073242 | 0.50354 | 0.53101 | 0.45319 | 0.41656 | 0.33874 | 0.84229 | 123.1705 | 0.3891 | 123.0286 | 123.3261 | 122.9553 | 123.024 | 123.0698 | -123.5184 | -123.1018 | 122.8683 | 123.143 | 121.4813 | 121.8475
584.1406 | 123.2895 | -122.1634 | 1.0162 | -0.0096891 | 0.0060221 | 0.069994 | 0.062026 | 0.00091214 | -0.0023028 | -0.0012434 | -0.0012513 | 0.0037319 | 0.069983 | 0.063023 | -0.0028668 | 0.014155 | -0.0030014 | -0.16022 | 1.0025 | -122.3419 | 0.91553 | -121.4081 | -122.0215 | -122.1497 | -0.10986 | 0.97961 | -122.2366 | 0.93384 | -121.7056 | -121.7697 | -121.669 | -0.17853 | -0.013733 | -0.10071 | 0.75531 | 0.013733 | 0.14191 | 0.19226 | 0.32044 | -0.073242 | -0.036621 | -0.082397 | 0.45776 | 0.49439 | 0.39368 | 0.56763 | 0.46692 | 0.93384 | 123.2574 | 0.53101 | 123.1705 | 123.3444 | 123.2162 | 123.1659 | 123.143 | -123.3582 | -123.2529 | 123.0789 | 123.0972 | 122.0032 | 122.0535
585.8906 | 123.2803 | -122.1634 | 1.0208 | 0.036087 | 0.0045267 | 0.069566 | 0.064803 | 0.0015529 | -0.00059378 | -0.0023114 | 0.0079041 | 0.0039457 | 0.068488 | 0.06046 | -0.0013714 | 0.015864 | -0.0019332 | -0.19226 | 1.0208 | -122.3602 | 0.89722 | -121.431 | -122.0764 | -122.1497 | -0.15106 | 0.97504 | -122.2412 | 0.95673 | -121.7514 | -121.8109 | -121.6736 | -0.19684 | 0 | -0.1236 | 0.73242 | 0.013733 | 0.086975 | 0.21057 | 0.28381 | -0.07782 | -0.045776 | -0.064087 | 0.41199 | 0.48981 | 0.35248 | 0.56763 | 0.4303 | 0.92926 | 123.2574 | 0.48981 | 123.1979 | 123.381 | 123.2162 | 123.1842 | 123.1384 | -123.381 | -123.262 | 123.0606 | 123.1201 | 121.9711 | 122.0123
587.5781 | 123.3032 | -122.287 | 0.87433 | -0.0020601 | 0.0030313 | 0.071062 | 0.064375 | 0.0030483 | -0.0025166 | 0.00025205 | -0.0043029 | 0.0039457 | 0.069128 | 0.063237 | -0.0039348 | 0.013514 | -0.0040696 | -0.16937 | 0.84228 | -122.4884 | 0.77362 | -121.5775 | -122.168 | -122.2778 | -0.10529 | 0.83313 | -122.374 | 0.81024 | -121.8613 | -121.9162 | -121.8155 | -0.20142 | -0.032044 | -0.10071 | 0.70953 | 0.009155 | 0.11902 | 0.21057 | 0.32043 | -0.086975 | -0.041199 | -0.064087 | 0.42572 | 0.4715 | 0.37079 | 0.55847 | 0.45776 | 0.91095 | 123.262 | 0.5127 | 123.1842 | 123.3307 | 123.2071 | 123.1293 | 123.1201 | -123.3627 | -123.2483 | 123.0606 | 123.0972 | 122.1176 | 122.1817
589.3281 | 123.2391 | -122.2504 | 0.95215 | -0.0020601 | 0.0043131 | 0.071062 | 0.06758 | 0.0024075 | -0.0010212 | -0.003166 | 0.0018005 | 0.0071499 | 0.071692 | 0.063237 | -0.0011578 | 0.013941 | -0.0036422 | -0.11902 | 0.97046 | -122.4426 | 0.77362 | -121.5546 | -122.1954 | -122.3007 | -0.12817 | 0.92468 | -122.3236 | 0.81482 | -121.8704 | -121.9437 | -121.7834 | -0.19226 | 0.018311 | -0.17853 | 0.6958 | -0.050354 | 0.054931 | 0.14191 | 0.24719 | -0.073242 | -0.027465 | -0.13733 | 0.37994 | 0.46692 | 0.3067 | 0.54016 | 0.37994 | 0.88806 | 123.2162 | 0.45319 | 123.1384 | 123.4131 | 123.2483 | 123.2208 | 123.175 | -123.3948 | -123.2758 | 123.024 | 123.0652 | 122.1313 | 122.1222
591.0312 | 123.262 | -122.2641 | 0.9201 | 0.036087 | 0.0066629 | 0.071703 | 0.066725 | 0.0030483 | -0.0018756 | -0.0012434 | 0.010956 | 0.0026639 | 0.069342 | 0.053624 | -0.002226 | 0.014155 | -0.0036422 | -0.14648 | 0.94757 | -122.4838 | 0.71869 | -121.6187 | -122.2092 | -122.3007 | -0.15564 | 0.91553 | -122.3511 | 0.79651 | -121.8796 | -121.9299 | -121.8018 | -0.21973 | 0.027466 | -0.20142 | 0.64545 | -0.036621 | 0.054932 | 0.18311 | 0.27466 | -0.086975 | -0.004578 | -0.1236 | 0.38452 | 0.46234 | 0.33417 | 0.54932 | 0.42114 | 0.86517 | 123.2025 | 0.4715 | 123.1476 | 123.4314 | 123.2666 | 123.2117 | 123.1796 | -123.4039 | -123.2712 | 122.9828 | 123.0606 | 122.1176 | 122.1085
592.7812 | 123.175 | -122.3145 | 0.90179 | -0.0020601 | 0.0049539 | 0.06978 | 0.066084 | 0.0030483 | -0.001662 | -0.00060235 | -0.0073547 | 0.0050137 | 0.068701 | 0.054905 | -0.0013714 | 0.014155 | -0.0012924 | -0.20599 | 0.89264 | -122.5067 | 0.63629 | -121.7285 | -122.3328 | -122.4197 | -0.27008 | 0.86517 | -122.4152 | 0.72327 | -122.0123 | -122.0627 | -121.8887 | -0.19226 | -0.009155 | -0.2655 | 0.58594 | -0.10529 | -0.018311 | 0.086975 | 0.17395 | -0.10071 | -0.036621 | -0.17853 | 0.30212 | 0.42572 | 0.25177 | 0.52643 | 0.35248 | 0.7782 | 123.143 | 0.40283 | 123.1384 | 123.3994 | 123.2803 | 123.2071 | 123.1796 | -123.4085 | -123.317 | 122.9507 | 123.0377 | 122.1085 | 122.0444
594.5312 | 123.3032 | -122.2458 | 0.86975 | 0.013199 | 0.0032449 | 0.070207 | 0.065443 | 0.00027134 | -0.0012348 | -0.001457 | 0.0018005 | 0.0045865 | 0.072974 | 0.059605 | 0.00076477 | 0.016291 | -0.0019332 | -0.21515 | 0.88348 | -122.4518 | 0.70953 | -121.6232 | -122.2641 | -122.3419 | -0.16479 | 0.85602 | -122.3694 | 0.82398 | -121.843 | -121.907 | -121.7789 | -0.20599 | 0.013733 | -0.16022 | 0.62256 | -0.09613 | -0.01831 | 0.10986 | 0.18768 | -0.1236 | -0.013733 | -0.045776 | 0.40283 | 0.46692 | 0.33875 | 0.59051 | 0.46234 | 0.82855 | 123.1613 | 0.52643 | 123.1934 | 123.3353 | 123.2254 | 123.1293 | 123.1018 | -123.3215 | -123.2391 | 122.9553 | 123.0698 | 122.0306 | 122.081
596.2188 | 123.2117 | -122.1863 | 1.0025 | 0.0055694 | 0.0064493 | 0.070207 | 0.069075 | 0.0034755 | -0.003371 | -0.00081595 | -0.0012513 | 0.0045865 | 0.071905 | 0.06345 | -0.0026532 | 0.016718 | -0.003856 | -0.16937 | 1.0117 | -122.4014 | 0.76904 | -121.55 | -122.1909 | -122.2733 | -0.21057 | 0.96588 | -122.2824 | 0.83771 | -121.8521 | -121.8979 | -121.7422 | -0.21515 | 0.009156 | -0.23346 | 0.63629 | -0.086975 | -0.004578 | 0.12817 | 0.21057 | -0.096131 | -0.036621 | -0.16479 | 0.33417 | 0.44403 | 0.28839 | 0.54016 | 0.38452 | 0.85144 | 123.1705 | 0.4303 | 123.1201 | 123.4131 | 123.2483 | 123.1979 | 123.1522 | -123.4039 | -123.2849 | 122.9553 | 123.024 | 122.0169 | 121.9757
597.9688 | 123.3353 | -122.2321 | 0.86975 | -0.0020601 | 0.0064493 | 0.071916 | 0.065016 | 5.774e-05 | -0.0025166 | -0.0018842 | 0.020111 | 0.0060819 | 0.072546 | 0.064091 | -0.00030343 | 0.017786 | -0.0025742 | -0.18768 | 0.86975 | -122.4197 | 0.79193 | -121.4859 | -122.1268 | -122.2321 | -0.086975 | 0.88348 | -122.3877 | 0.88806 | -121.788 | -121.8475 | -121.7285 | -0.18768 | 0 | -0.07782 | 0.74616 | 0 | 0.10529 | 0.18768 | 0.29297 | -0.15564 | 0.013733 | 0.018311 | 0.44403 | 0.50354 | 0.38452 | 0.65918 | 0.54016 | 0.93384 | 123.2117 | 0.59967 | 123.2758 | 123.2895 | 123.2712 | 123.1018 | 123.1155 | -123.2895 | -123.2574 | 123.024 | 123.1201 | 122.0444 | 122.1451
599.6562 | 123.2666 | -122.2778 | 0.86975 | 0.028458 | 0.0030313 | 0.070848 | 0.063521 | 0.0068935 | 0.00068782 | 3.8448e-05 | 0.0048523 | 0.0028775 | 0.072119 | 0.062809 | -0.003294 | 0.017573 | -0.001506 | -0.23804 | 0.88348 | -122.4564 | 0.72784 | -121.582 | -122.1909 | -122.2961 | -0.19226 | 0.85144 | -122.3648 | 0.80109 | -121.8613 | -121.9254 | -121.7972 | -0.17853 | 0.013733 | -0.14191 | 0.6958 | -0.018311 | 0.086975 | 0.16022 | 0.2655 | -0.086975 | -0.018311 | -0.068665 | 0.41657 | 0.48065 | 0.35248 | 0.56763 | 0.43945 | 0.87433 | 123.1842 | 0.50354 | 123.1659 | 123.3398 | 123.2162 | 123.1613 | 123.1293 | -123.3261 | -123.2346 | 123.0057 | 123.0789 | 122.0398 | 122.0856
601.4219 | 123.3124 | -122.0215 | 1.0849 | 0.013199 | 0.0036721 | 0.071275 | 0.068434 | 0.0026211 | -0.0035846 | 0.00046565 | -0.0043029 | 0.0026639 | 0.069556 | 0.061528 | -0.0024396 | 0.0133 | -0.0010788 | -0.22888 | 1.1124 | -122.2046 | 0.96588 | -121.3623 | -121.9803 | -122.0627 | -0.16479 | 1.0757 | -122.1268 | 1.0574 | -121.6003 | -121.6782 | -121.5225 | -0.18311 | 0.027466 | -0.11902 | 0.65918 | -0.041199 | 0.041198 | 0.14191 | 0.2243 | -0.10529 | -0.009155 | -0.027466 | 0.42114 | 0.49896 | 0.34332 | 0.60425 | 0.44861 | 0.84228 | 123.1705 | 0.52643 | 123.1842 | 123.317 | 123.2025 | 123.1338 | 123.0972 | -123.2895 | -123.2117 | 122.9874 | 123.0789 | 121.7926 | 121.8567
603.125 | 123.3307 | -122.1085 | 1.0025 | -0.0096891 | 0.0043131 | 0.071062 | 0.064589 | 5.774e-05 | -0.00038018 | -0.00060235 | -0.0012513 | 0.0039457 | 0.070837 | 0.059819 | -0.0026532 | 0.012873 | 0.0008438 | -0.21973 | 0.99335 | -122.3328 | 0.90179 | -121.3898 | -121.9986 | -122.1085 | -0.10986 | 0.97961 | -122.2 | 1.0071 | -121.6507 | -121.6827 | -121.6003 | -0.22431 | -0.009155 | -0.10071 | 0.71869 | 0 | 0.10986 | 0.22431 | 0.33417 | -0.091553 | -0.022888 | 0.004578 | 0.45776 | 0.50812 | 0.42572 | 0.59967 | 0.51727 | 0.94299 | 123.2346 | 0.54932 | 123.2071 | 123.3261 | 123.1796 | 123.1018 | 123.0881 | -123.3353 | -123.2025 | 123.0103 | 123.1155 | 121.8887 | 121.9986
604.875 | 123.3124 | -122.3053 | 0.84686 | -0.0020601 | 0.0058083 | 0.069566 | 0.063521 | -0.0016513 | -0.001662 | -0.0027386 | -0.0043029 | 0.0030911 | 0.068488 | 0.060246 | -0.0041486 | 0.015436 | -0.0006516 | -0.25177 | 0.8194 | -122.4792 | 0.71411 | -121.5958 | -122.2092 | -122.3053 | -0.16022 | 0.80109 | -122.3694 | 0.80109 | -121.8475 | -121.8842 | -121.7743 | -0.17395 | -0.027466 | -0.13275 | 0.70953 | 0 | 0.096131 | 0.17395 | 0.27008 | -0.064087 | -0.045777 | -0.045777 | 0.45776 | 0.53101 | 0.42114 | 0.59509 | 0.48523 | 0.88348 | 123.1934 | 0.52185 | 123.1705 | 123.2986 | 123.1705 | 123.1247 | 123.1064 | -123.3261 | -123.2162 | 123.0194 | 123.1064 | 122.0535 | 122.1451
606.5625 | 123.2254 | -122.2321 | 0.91553 | 0.0055694 | 0.0070901 | 0.067003 | 0.066512 | 0.0043301 | -0.0031574 | 0.00046565 | 0.0018005 | 0.0052273 | 0.071692 | 0.057469 | -0.0013714 | 0.015223 | -0.0010788 | -0.14648 | 0.91553 | -122.4747 | 0.75073 | -121.582 | -122.1863 | -122.287 | -0.1236 | 0.88806 | -122.3557 | 0.81024 | -121.8567 | -121.9162 | -121.7697 | -0.24261 | 0 | -0.1648 | 0.65002 | -0.054931 | 0.045777 | 0.18768 | 0.28839 | -0.1236 | -0.027465 | -0.10528 | 0.37537 | 0.46234 | 0.31586 | 0.58594 | 0.43945 | 0.89264 | 123.2254 | 0.49896 | 123.1659 | 123.3902 | 123.2437 | 123.1476 | 123.1201 | -123.3902 | -123.2712 | 122.9828 | 123.0423 | 122.0856 | 122.1085
608.3125 | 123.1888 | -122.2412 | 0.9613 | -0.017319 | 0.0043131 | 0.069353 | 0.068007 | -0.0014377 | -0.0018756 | -0.00081595 | 0.017059 | 0.0058683 | 0.071692 | 0.054692 | -0.0045758 | 0.014795 | -0.001506 | -0.2243 | 0.94757 | -122.4564 | 0.737 | -121.5591 | -122.1542 | -122.2458 | -0.15106 | 0.96588 | -122.3053 | 0.7782 | -121.8384 | -121.8842 | -121.7606 | -0.21515 | -0.013733 | -0.2243 | 0.68207 | -0.004578 | 0.086975 | 0.21057 | 0.30212 | -0.064087 | 0.004577 | -0.18311 | 0.40283 | 0.48065 | 0.35706 | 0.54474 | 0.42114 | 0.89722 | 123.1934 | 0.46692 | 123.0835 | 123.4039 | 123.2712 | 123.1888 | 123.2071 | -123.4177 | -123.2666 | 122.9782 | 123.0194 | 122.0169 | 122.0901
610.0625 | 123.2483 | -122.1909 | 0.95215 | 0.020828 | 0.0026041 | 0.072557 | 0.064162 | 0.00048494 | -0.0010212 | -0.00017515 | 0.0048523 | 0.0039457 | 0.069769 | 0.067936 | -0.0017986 | 0.015864 | -0.0008652 | -0.21973 | 0.94757 | -122.4014 | 0.80109 | -121.5042 | -122.1313 | -122.2092 | -0.16937 | 0.90179 | -122.2916 | 0.8606 | -121.7926 | -121.8292 | -121.6919 | -0.21057 | -0.004577 | -0.15106 | 0.68665 | -0.01831 | 0.059509 | 0.19226 | 0.27008 | -0.10071 | -0.050354 | -0.091552 | 0.39825 | 0.49896 | 0.36163 | 0.59967 | 0.46234 | 0.89722 | 123.2025 | 0.49896 | 123.1522 | 123.349 | 123.1934 | 123.1384 | 123.0927 | -123.3536 | -123.2437 | 122.9919 | 123.0515 | 121.9711 | 122.0215
611.8125 | 123.1888 | -122.1359 | 1.0437 | 0.013199 | 0.0038857 | 0.068925 | 0.064803 | -0.0010105 | -0.0018756 | 0.0011066 | -0.0073547 | 0.0048001 | 0.072119 | 0.054692 | -0.0054302 | 0.0133 | -0.0023606 | -0.23346 | 1.0208 | -122.3099 | 0.81024 | -121.4905 | -122.081 | -122.1863 | -0.24261 | 1.0117 | -122.2137 | 0.84686 | -121.7789 | -121.8292 | -121.6965 | -0.17395 | -0.022888 | -0.23346 | 0.64545 | -0.050354 | 0.054931 | 0.1236 | 0.22888 | -0.07782 | -0.032043 | -0.19684 | 0.35706 | 0.43945 | 0.3067 | 0.51727 | 0.38452 | 0.8194 | 123.1201 | 0.43488 | 123.0606 | 123.3307 | 123.2254 | 123.1567 | 123.1476 | -123.3536 | -123.2574 | 122.9462 | 122.9828 | 121.9025 | 121.8933
613.5 | 123.2849 | -122.1817 | 0.92926 | 0.020828 | 0.0047403 | 0.073198 | 0.067152 | 0.0043301 | 0.001756 | -0.0012434 | 0.010956 | 0.0058683 | 0.068701 | 0.060887 | -0.0013714 | 0.016504 | -0.0027878 | -0.17853 | 0.94299 | -122.3831 | 0.86975 | -121.4127 | -122.0581 | -122.1725 | -0.10986 | 0.94299 | -122.2778 | 0.92468 | -121.7468 | -121.8201 | -121.669 | -0.20142 | 0.013733 | -0.059509 | 0.76904 | 0.009156 | 0.1236 | 0.21057 | 0.32501 | -0.09613 | 0.013733 | -0.004577 | 0.43488 | 0.5127 | 0.36163 | 0.60883 | 0.45776 | 0.97046 | 123.2529 | 0.53101 | 123.2025 | 123.3261 | 123.2208 | 123.1247 | 123.1247 | -123.3124 | -123.2071 | 123.0515 | 123.1064 | 122.0032 | 122.0718
615.25 | 123.2162 | -121.8567 | 1.2863 | 0.0055694 | 0.0073037 | 0.06978 | 0.066298 | 0.0028347 | -0.0027302 | 0.0021746 | 0.0048523 | 0.0050137 | 0.071905 | 0.0611 | -0.0045758 | 0.016291 | -0.0017196 | -0.1236 | 1.3 | -122.081 | 1.1627 | -121.1426 | -121.7743 | -121.8933 | -0.10071 | 1.2772 | -121.9666 | 1.1673 | -121.4676 | -121.5363 | -121.3943 | -0.22431 | 0.013733 | -0.1236 | 0.71411 | -0.036622 | 0.082397 | 0.18768 | 0.3067 | -0.10986 | -0.009155 | -0.11902 | 0.3891 | 0.46234 | 0.32043 | 0.57221 | 0.4303 | 0.93842 | 123.2437 | 0.49896 | 123.1339 | 123.381 | 123.2437 | 123.1567 | 123.1339 | -123.3673 | -123.2529 | 123.0194 | 123.024 | 121.7331 | 121.756
617.0156 | 123.3307 | -121.8521 | 1.2726 | -0.0020601 | 0.0019631 | 0.068925 | 0.063094 | -0.0018649 | -0.0018756 | 0.0021746 | -0.0043029 | 0.0026639 | 0.07041 | 0.06345 | -0.0020122 | 0.015864 | 0.000203 | -0.15106 | 1.2772 | -122.0032 | 1.1902 | -121.0739 | -121.6965 | -121.8201 | -0.059509 | 1.2451 | -121.9254 | 1.2177 | -121.3577 | -121.4127 | -121.3028 | -0.15106 | 0.004578 | -0.082397 | 0.7782 | 0.032044 | 0.15564 | 0.18311 | 0.3067 | -0.073242 | -0.027466 | -0.054932 | 0.49439 | 0.54932 | 0.43945 | 0.62256 | 0.51269 | 0.92926 | 123.1934 | 0.56763 | 123.143 | 123.2803 | 123.1705 | 123.1293 | 123.0972 | -123.2758 | -123.1979 | 123.0423 | 123.0698 | 121.7011 | 121.7926
618.6875 | 123.2895 | -121.8842 | 1.2177 | -0.0096891 | 0.0043131 | 0.067857 | 0.063521 | 0.0013393 | -0.0029438 | -0.00038875 | -0.0043029 | 0.0037319 | 0.069128 | 0.063664 | -0.0020122 | 0.016718 | -0.0023606 | -0.1831 | 1.1993 | -122.113 | 1.1215 | -121.1517 | -121.7697 | -121.8979 | -0.064087 | 1.1627 | -121.9528 | 1.2085 | -121.431 | -121.4676 | -121.376 | -0.22888 | -0.01831 | -0.09613 | 0.73242 | -0.013733 | 0.11444 | 0.21515 | 0.34332 | -0.068665 | -0.054931 | -0.009155 | 0.45319 | 0.50812 | 0.41657 | 0.57678 | 0.48523 | 0.9613 | 123.2346 | 0.52185 | 123.1613 | 123.3124 | 123.1155 | 123.0835 | 123.0469 | -123.3307 | -123.1705 | 123.0057 | 123.0927 | 121.7011 | 121.8201
620.4375 | 123.1613 | -121.0281 | 2.1423 | -0.0020601 | 0.0011087 | 0.069139 | 0.065443 | 0.0028347 | -0.0035846 | -0.001457 | -0.0043029 | 0.0052273 | 0.069769 | 0.064732 | -0.0037212 | 0.016077 | -0.0019332 | -0.3479 | 1.7899 | -121.5591 | 1.6205 | -120.6253 | -121.2204 | -121.3394 | -0.27008 | 1.8448 | -121.3348 | 1.9958 | -120.6299 | -120.7077 | -120.6024 | -0.53101 | -0.35248 | -0.52185 | 0.40283 | -0.31128 | -0.19226 | 0.21973 | 0.33875 | -0.3067 | -0.29755 | -0.14648 | 0.39825 | 0.42572 | 0.32043 | 0.73242 | 0.62714 | 0.93384 | 123.1796 | 0.70496 | 123.3307 | 123.349 | 123.1796 | 122.818 | 122.8729 | -123.7015 | -123.4772 | 122.6486 | 123.024 | 120.6802 | 120.7581
622.1875 | 123.1796 | -120.5154 | 2.417 | 0.036087 | 0.0043131 | 0.069994 | 0.064803 | 0.0021939 | 0.00047422 | 0.0017474 | 0.014008 | 0.0058683 | 0.071265 | 0.055546 | -0.0017986 | 0.014368 | -0.0042832 | -0.10986 | 1.0208 | -122.3648 | 0.88806 | -121.3806 | -122.0444 | -122.1954 | 0.004578 | 1.0345 | -122.1771 | 2.0096 | -120.8908 | -121.2067 | -119.9478 | -1.8494 | -1.3962 | -1.5289 | -0.86517 | -1.68 | -1.5289 | 0.16937 | 0.32043 | -1.6617 | -1.3824 | -0.40741 | -0.37537 | 0.56763 | -0.69122 | 2.2293 | 0.97046 | 0.98419 | 123.2529 | 1.2863 | 124.1867 | 123.3856 | 123.2117 | 121.5363 | 121.55 | -124.7818 | -124.5941 | 121.4035 | 122.525 | 120.4056 | 120.52
623.875 | 123.2391 | -122.287 | 0.85144 | 0.028458 | 0.0058083 | 0.072771 | 0.062453 | 0.0017667 | -0.0012348 | -0.0016706 | 0.0048523 | 0.0024503 | 0.073401 | 0.066227 | -0.0026532 | 0.016718 | 0.0006302 | -0.26093 | 0.81024 | -122.5113 | 0.68665 | -121.6049 | -122.2229 | -122.3236 | -0.21515 | 0.7782 | -122.3877 | 0.75073 | -121.9025 | -121.9299 | -121.7834 | -0.22431 | -0.041198 | -0.16479 | 0.68207 | -0.036621 | 0.064087 | 0.18768 | 0.28839 | -0.10071 | -0.073242 | -0.10071 | 0.38452 | 0.50354 | 0.35706 | 0.60425 | 0.45776 | 0.90637 | 123.1979 | 0.48523 | 123.1384 | 123.3215 | 123.1659 | 123.0972 | 123.0652 | -123.3627 | -123.2391 | 122.9736 | 123.0377 | 122.0261 | 122.0718
625.6094 | 123.1567 | -121.5225 | 1.8036 | 0.0055694 | 0.0047403 | 0.070848 | 0.066725 | 0.0051845 | -0.0025166 | -0.0020978 | -0.0012513 | 0.0062955 | 0.068915 | 0.061741 | -0.001585 | 0.013727 | -0.0008652 | -0.11444 | 1.5106 | -121.8384 | 1.2222 | -121.0556 | -121.6782 | -121.7697 | -0.13275 | 1.3824 | -121.7514 | 2.1835 | -120.9045 | -121.2891 | -121.1563 | -0.31586 | -0.29297 | -0.58136 | 0.46692 | -0.24719 | -0.15564 | 0.068665 | 0.16022 | -0.22888 | -0.42114 | 0.37994 | 0.61798 | 0.36621 | 0.23346 | 0.59509 | 0.46234 | 0.78278 | 123.0606 | 0.84686 | 123.9349 | 123.349 | 123.1338 | 123.0331 | 122.905 | -123.642 | -123.555 | 122.7448 | 123.7061 | 121.4081 | 121.3898
627.3594 | 123.1659 | -121.5179 | 1.6296 | -0.0020601 | 0.0043131 | 0.06978 | 0.066725 | 0.0013393 | -0.0040118 | 0.00025205 | -0.0043029 | 0.0045865 | 0.069342 | 0.058964 | -0.0041486 | 0.012659 | 0.0006302 | -0.1831 | 1.5564 | -121.7331 | 1.4328 | -120.8359 | -121.4401 | -121.5546 | -0.15106 | 1.5701 | -121.6095 | 1.442 | -121.1426 | -121.1746 | -121.0281 | -0.21515 | -0.073243 | -0.19684 | 0.68207 | -0.036621 | 0.077819 | 0.17853 | 0.29297 | -0.091553 | -0.05951 | -0.18768 | 0.37537 | 0.48981 | 0.34332 | 0.58136 | 0.43488 | 0.89722 | 123.1659 | 0.46692 | 123.0515 | 123.2895 | 123.1796 | 123.0743 | 123.0881 | -123.3627 | -123.2391 | 122.9507 | 122.9599 | 121.3348 | 121.3669
629.1094 | 123.2574 | -122.2366 | 0.85602 | 0.043716 | 0.0055947 | 0.070634 | 0.064589 | 0.0043301 | -0.00080758 | 3.8448e-05 | 0.010956 | 0.0062955 | 0.070837 | 0.068577 | -8.9634e-05 | 0.016504 | -0.0002244 | -0.19226 | 0.86517 | -122.4335 | 0.76904 | -121.4813 | -122.1542 | -122.2458 | -0.082397 | 0.82855 | -122.3236 | 0.82855 | -121.8292 | -121.8887 | -121.7468 | -0.19684 | 0.009155 | -0.086975 | 0.75531 | -0.009156 | 0.082397 | 0.18768 | 0.27924 | -0.086975 | -0.027466 | -0.027466 | 0.40741 | 0.48981 | 0.3479 | 0.57678 | 0.43487 | 0.95215 | 123.2025 | 0.49438 | 123.1522 | 123.2986 | 123.1522 | 123.1018 | 123.0652 | -123.2895 | -123.1796 | 123.0057 | 123.0652 | 122.0444 | 122.1542
630.8594 | 123.2025 | -122.3236 | 0.81024 | 0.013199 | 0.0051675 | 0.071916 | 0.067152 | 0.0019803 | -0.0025166 | -0.001457 | 0.0018005 | 0.0050137 | 0.069342 | 0.06046 | -0.0041486 | 0.015223 | -0.0023606 | -0.15106 | 0.85602 | -122.5571 | 0.64087 | -121.6278 | -122.2458 | -122.3648 | -0.11444 | 0.80566 | -122.4152 | 0.70953 | -121.9116 | -121.9711 | -121.8201 | -0.23346 | 0.045776 | -0.16937 | 0.6958 | -0.041199 | 0.077819 | 0.19226 | 0.31128 | -0.091553 | -0.004578 | -0.10071 | 0.41199 | 0.50354 | 0.35248 | 0.59509 | 0.44403 | 0.92926 | 123.1979 | 0.50354 | 123.1247 | 123.4131 | 123.2208 | 123.1796 | 123.1293 | -123.3673 | -123.2254 | 122.9645 | 123.0331 | 122.1725 | 122.2092
632.5625 | 123.2758 | -121.9894 | 1.0529 | 0.051346 | 0.0049539 | 0.072984 | 0.065016 | 0.0028347 | 0.00090142 | 0.0011066 | 0.014008 | 0.0037319 | 0.071905 | 0.063664 | 0.0014056 | 0.016504 | -0.0047104 | -0.19226 | 1.1032 | -122.1863 | 1.03 | -121.2387 | -121.8796 | -121.9849 | -0.11902 | 1.0574 | -122.0947 | 1.0757 | -121.5546 | -121.6141 | -121.4584 | -0.19684 | 0.050354 | -0.022888 | 0.75073 | 0.004578 | 0.10986 | 0.20142 | 0.3067 | -0.10529 | 0.004578 | 0.022889 | 0.43488 | 0.53101 | 0.37537 | 0.63629 | 0.48065 | 0.94757 | 123.2162 | 0.54016 | 123.1705 | 123.2895 | 123.1522 | 123.0927 | 123.0469 | -123.2391 | -123.1476 | 123.0194 | 123.0652 | 121.7972 | 121.8704
634.3125 | 123.1934 | -121.0693 | 2.0737 | 0.028458 | 0.0055947 | 0.071062 | 0.066725 | 0.0032619 | 0.00047422 | -0.0018842 | 0.0048523 | 0.0048001 | 0.070196 | 0.0611 | -0.0024396 | 0.016504 | -0.0002244 | -0.17395 | 2.0462 | -121.312 | 1.9043 | -120.401 | -121.0052 | -121.1105 | -0.13275 | 2.0508 | -121.1334 | 1.9318 | -120.6757 | -120.726 | -120.5612 | -0.24261 | -0.027465 | -0.16937 | 0.66834 | -0.041199 | 0.064087 | 0.20142 | 0.3067 | -0.064087 | -0.022888 | -0.14191 | 0.39368 | 0.50812 | 0.34332 | 0.5722 | 0.40741 | 0.91095 | 123.2162 | 0.45776 | 123.0652 | 123.3582 | 123.1842 | 123.1155 | 123.1201 | -123.3856 | -123.2071 | 122.9736 | 123.0011 | 120.8954 | 120.9366
636.0625 | 123.1522 | -121.9711 | 1.2131 | 0.043716 | 0.0060221 | 0.068285 | 0.065443 | 0.0034755 | -0.0031574 | -0.0033796 | 0.010956 | 0.0058683 | 0.072546 | 0.060887 | -0.0043622 | 0.0133 | -0.0012924 | -0.1831 | 1.2039 | -122.1725 | 0.97961 | -121.3074 | -121.8887 | -121.9711 | -0.19684 | 1.1902 | -122.0535 | 1.0208 | -121.5729 | -121.637 | -121.4584 | -0.20142 | -0.009156 | -0.23346 | 0.66376 | 0 | 0.082397 | 0.20142 | 0.28381 | -0.082398 | -0.022888 | -0.19226 | 0.39825 | 0.5127 | 0.33417 | 0.59509 | 0.41657 | 0.86517 | 123.1522 | 0.48065 | 123.0743 | 123.3765 | 123.2437 | 123.175 | 123.1613 | -123.3856 | -123.2666 | 122.9507 | 122.9919 | 121.788 | 121.7743
637.8125 | 123.1934 | -121.9162 | 1.2177 | 0.036087 | 0.0040995 | 0.070421 | 0.066939 | 0.00027134 | -0.0014484 | 0.001961 | 0.010956 | 0.0052273 | 0.070624 | 0.059819 | -0.002226 | 0.014368 | -0.0036422 | -0.17853 | 1.2268 | -122.1405 | 1.0391 | -121.2479 | -121.8521 | -121.9574 | -0.16022 | 1.2039 | -122.0169 | 1.0895 | -121.5134 | -121.5637 | -121.4081 | -0.2243 | 0.009156 | -0.17853 | 0.66833 | -0.041198 | 0.064087 | 0.18311 | 0.28839 | -0.10071 | -0.013733 | -0.12817 | 0.40283 | 0.50812 | 0.35248 | 0.60883 | 0.45319 | 0.89264 | 123.1796 | 0.50354 | 123.1064 | 123.3673 | 123.2208 | 123.143 | 123.1201 | -123.3582 | -123.2346 | 122.9553 | 123.0057 | 121.7377 | 121.756
639.5 | 123.1384 | -122.1085 | 1.0391 | -0.0096891 | 0.0043131 | 0.070207 | 0.063307 | 0.00069854 | -0.0042254 | -0.00038875 | -0.0073547 | 0.0022367 | 0.071905 | 0.057896 | -0.0060712 | 0.013727 | -0.0030014 | -0.20142 | 1.0162 | -122.2916 | 0.83771 | -121.4355 | -122.0352 | -122.1588 | -0.20599 | 0.98419 | -122.1588 | 0.87433 | -121.7285 | -121.7743 | -121.6507 | -0.18311 | -0.022889 | -0.20142 | 0.67291 | -0.050354 | 0.073242 | 0.13275 | 0.25635 | -0.050354 | -0.054932 | -0.16479 | 0.37994 | 0.45776 | 0.33417 | 0.50812 | 0.38452 | 0.85602 | 123.1293 | 0.4303 | 123.0331 | 123.3078 | 123.143 | 123.1247 | 123.0927 | -123.3307 | -123.1979 | 122.9462 | 122.9828 | 121.907 | 121.9025
641.25 | 123.2483 | -120.9595 | 2.1286 | -0.0020601 | 0.0034585 | 0.069994 | 0.06523 | 0.0047573 | -0.001662 | -0.0010298 | -0.0012513 | 0.0043729 | 0.069128 | 0.067509 | 0.00097837 | 0.017359 | -0.003215 | -0.21057 | 2.1423 | -121.1517 | 1.9592 | -120.3186 | -120.9274 | -121.0052 | -0.17395 | 2.1149 | -121.0327 | 2.092 | -120.5246 | -120.5933 | -120.433 | -0.19226 | 0.013733 | -0.16937 | 0.64087 | -0.045776 | 0.032044 | 0.14648 | 0.2243 | -0.073242 | -0.013733 | -0.036621 | 0.43488 | 0.52643 | 0.36621 | 0.59967 | 0.43945 | 0.83313 | 123.111 | 0.50812 | 123.1247 | 123.2941 | 123.1476 | 123.1018 | 123.0743 | -123.2803 | -123.1613 | 122.9187 | 123.0515 | 120.7489 | 120.7855
643 | 123.1247 | -120.845 | 2.3117 | -0.0020601 | 0.0051675 | 0.071275 | 0.064162 | -0.00079686 | -0.0018756 | 0.0023882 | -0.0043029 | 0.0043729 | 0.071905 | 0.057042 | -0.0039348 | 0.017573 | -0.0010788 | -0.21973 | 2.2842 | -121.019 | 2.0279 | -120.2545 | -120.8221 | -120.9 | -0.23804 | 2.2842 | -120.9137 | 2.1149 | -120.5017 | -120.5475 | -120.3552 | -0.17395 | -0.027466 | -0.28381 | 0.59051 | -0.054931 | 0.022888 | 0.11902 | 0.19684 | -0.068664 | -0.027466 | -0.19684 | 0.34332 | 0.48981 | 0.29755 | 0.55847 | 0.36621 | 0.76446 | 123.0469 | 0.41199 | 123.0286 | 123.3032 | 123.1979 | 123.1293 | 123.1293 | -123.3307 | -123.2254 | 122.8729 | 122.9599 | 120.6253 | 120.607
644.6719 | 123.2117 | -122.1497 | 0.96588 | 0.020828 | 0.0038857 | 0.070848 | 0.063948 | 0.0013393 | -0.001662 | 0.0013202 | 0.0048523 | 0.0020231 | 0.07041 | 0.061314 | -0.00073063 | 0.016932 | 0.0006302 | -0.23804 | 0.95215 | -122.3373 | 0.78278 | -121.4539 | -122.0764 | -122.1725 | -0.20142 | 0.91553 | -122.2275 | 0.8606 | -121.7514 | -121.7789 | -121.6553 | -0.18768 | -0.013733 | -0.1831 | 0.6958 | -0.022888 | 0.073242 | 0.16479 | 0.26093 | -0.07782 | -0.050354 | -0.10528 | 0.39825 | 0.49439 | 0.37079 | 0.57221 | 0.44861 | 0.88348 | 123.1201 | 0.47607 | 123.0881 | 123.2895 | 123.143 | 123.1018 | 123.0652 | -123.3032 | -123.1934 | 122.9324 | 123.0103 | 121.9116 | 121.9482
646.4219 | 123.1293 | -122.1359 | 1.0208 | -0.0096891 | 0.0051675 | 0.067644 | 0.064803 | -0.0025059 | -0.0020892 | -0.002525 | 0.020111 | 0.0054409 | 0.069556 | 0.054478 | -0.0043622 | 0.012446 | -0.0019332 | -0.2243 | 1.0025 | -122.3419 | 0.7782 | -121.463 | -122.0581 | -122.1497 | -0.21515 | 1.0117 | -122.2321 | 0.82398 | -121.7697 | -121.8018 | -121.6507 | -0.20599 | -0.018311 | -0.24262 | 0.67291 | -0.013733 | 0.07782 | 0.19226 | 0.28381 | -0.096131 | -0.009155 | -0.19684 | 0.36621 | 0.48523 | 0.33417 | 0.58136 | 0.4303 | 0.87891 | 123.1201 | 0.46234 | 123.056 | 123.3444 | 123.2437 | 123.1384 | 123.1476 | -123.3627 | -123.2529 | 122.9141 | 122.9599 | 121.9116 | 121.9208
648.1875 | 123.2483 | -121.6324 | 1.4282 | -0.0096891 | 0.0032449 | 0.069994 | 0.062666 | -0.0016513 | -0.0037982 | -0.0016706 | -0.0043029 | 0.0020231 | 0.071478 | 0.062169 | -0.002226 | 0.015009 | 0.0006302 | -0.21057 | 1.4236 | -121.8201 | 1.3687 | -120.8679 | -121.4722 | -121.6141 | -0.10529 | 1.4053 | -121.701 | 1.4191 | -121.1609 | -121.2067 | -121.0831 | -0.18768 | -0.004578 | -0.05951 | 0.76447 | 0.01831 | 0.16022 | 0.20599 | 0.3479 | -0.068665 | -0.022889 | -0.009156 | 0.4715 | 0.54932 | 0.42572 | 0.61798 | 0.49438 | 0.95215 | 123.1888 | 0.54016 | 123.1201 | 123.2437 | 123.1064 | 123.056 | 123.0377 | -123.2483 | -123.1293 | 123.0011 | 123.0515 | 121.4218 | 121.5271
649.9375 | 123.1796 | -121.6278 | 1.4694 | 0.028458 | 0.0049539 | 0.071703 | 0.067152 | -0.0010105 | -0.00038018 | 0.0011066 | 0.0079041 | 0.0067227 | 0.07041 | 0.064946 | -0.0037212 | 0.014795 | -0.0006516 | -0.12817 | 1.474 | -121.8658 | 1.2909 | -120.9595 | -121.582 | -121.6644 | -0.11444 | 1.4328 | -121.7422 | 1.3687 | -121.2158 | -121.2753 | -121.1151 | -0.23804 | 0.004578 | -0.17853 | 0.66833 | -0.036621 | 0.045777 | 0.20142 | 0.28381 | -0.11444 | -0.036621 | -0.10071 | 0.41199 | 0.5127 | 0.35248 | 0.62714 | 0.46692 | 0.90637 | 123.1567 | 0.52643 | 123.111 | 123.3398 | 123.175 | 123.1018 | 123.0606 | -123.3353 | -123.2117 | 122.9187 | 122.9965 | 121.4996 | 121.5134
651.6094 | 123.175 | -121.6461 | 1.4694 | 0.020828 | 0.0049539 | 0.070634 | 0.06758 | 0.0041165 | -0.0018756 | 3.8448e-05 | 0.0048523 | 0.0054409 | 0.070837 | 0.06345 | -0.0024396 | 0.016077 | -0.0027878 | -0.13733 | 1.4603 | -121.8796 | 1.2955 | -120.9641 | -121.5454 | -121.669 | -0.10071 | 1.442 | -121.7285 | 1.3367 | -121.225 | -121.2845 | -121.1197 | -0.23346 | -0.009155 | -0.17395 | 0.68207 | -0.022888 | 0.10071 | 0.21057 | 0.33417 | -0.082398 | -0.027465 | -0.13275 | 0.42114 | 0.52643 | 0.36163 | 0.60883 | 0.44403 | 0.91553 | 123.175 | 0.50354 | 123.0652 | 123.3398 | 123.1705 | 123.1064 | 123.0881 | -123.349 | -123.1979 | 122.9416 | 122.9828 | 121.5088 | 121.5454
653.375 | 123.2025 | -121.6965 | 1.3641 | -0.0020601 | 0.0045267 | 0.070848 | 0.065443 | 0.0032619 | -0.0040118 | -0.00081595 | -0.0043029 | 0.0030911 | 0.071692 | 0.063023 | 0.00055117 | 0.016932 | -0.0017196 | -0.3891 | 1.3779 | -121.9162 | 1.1673 | -121.0785 | -121.7056 | -121.788 | -0.32044 | 1.355 | -121.7834 | 1.3138 | -121.2936 | -121.3303 | -121.1746 | -0.21973 | 0.013733 | -0.19684 | 0.61798 | -0.091553 | -0.009155 | 0.12817 | 0.21057 | -0.086975 | -0.009156 | -0.050354 | 0.40283 | 0.52185 | 0.36621 | 0.60882 | 0.45319 | 0.83771 | 123.0835 | 0.48981 | 123.0972 | 123.2941 | 123.1384 | 123.0743 | 123.0515 | -123.2803 | -123.1476 | 122.8638 | 123.0103 | 121.3074 | 121.376
655.0625 | 123.0972 | -122.5479 | 0.52643 | 0.013199 | 0.0073037 | 0.069566 | 0.06523 | 0.0015529 | -0.0014484 | -0.0012434 | 0.0079041 | 0.0050137 | 0.074683 | 0.06046 | -0.002226 | 0.01565 | -0.002147 | -0.14648 | 0.54932 | -122.7585 | 0.37994 | -121.8109 | -122.4289 | -122.5479 | -0.10529 | 0.51727 | -122.5845 | 0.42114 | -122.1039 | -122.1588 | -122.0078 | -0.21057 | 0.022888 | -0.14648 | 0.737 | 0 | 0.11902 | 0.21057 | 0.32959 | -0.036621 | -0.009155 | -0.10529 | 0.44403 | 0.54016 | 0.3891 | 0.57678 | 0.42572 | 0.94757 | 123.1384 | 0.48065 | 123.0057 | 123.3078 | 123.1018 | 123.0972 | 123.0652 | -123.2849 | -123.111 | 122.9279 | 122.9691 | 122.4014 | 122.4426
656.8125 | 123.1979 | -122.5204 | 0.56305 | -0.0096891 | 0.0023905 | 0.06978 | 0.063094 | 0.0019803 | -0.001662 | -0.00038875 | -0.0012513 | 0.0028775 | 0.070624 | 0.06345 | -0.0054302 | 0.013941 | 0.001912 | -0.16937 | 0.53101 | -122.6761 | 0.4715 | -121.7651 | -122.3694 | -122.4838 | -0.10071 | 0.52643 | -122.5937 | 0.49439 | -122.0215 | -122.0901 | -121.962 | -0.15564 | -0.032043 | -0.091552 | 0.75531 | 0.036621 | 0.15106 | 0.19226 | 0.3067 | -0.073242 | -0.036621 | -0.068664 | 0.49896 | 0.55847 | 0.4303 | 0.63171 | 0.50354 | 0.91095 | 123.1476 | 0.5722 | 123.0881 | 123.2071 | 123.1201 | 123.0515 | 123.0469 | -123.2391 | -123.1567 | 122.9919 | 123.0148 | 122.3511 | 122.4197
658.5 | 123.1338 | -122.5616 | 0.54016 | 0.0055694 | 0.0045267 | 0.069994 | 0.062239 | -0.00079686 | -0.0018756 | -0.002525 | 0.0048523 | 0.0048001 | 0.070837 | 0.065587 | -0.001585 | 0.013727 | -0.001506 | -0.16022 | 0.50812 | -122.7402 | 0.41199 | -121.8201 | -122.4106 | -122.5525 | -0.15106 | 0.51727 | -122.6074 | 0.4303 | -122.1313 | -122.1771 | -122.049 | -0.17853 | -0.032043 | -0.12817 | 0.74158 | 0.009156 | 0.15106 | 0.18768 | 0.32959 | -0.045776 | -0.022888 | -0.10986 | 0.4303 | 0.5127 | 0.38452 | 0.55847 | 0.4303 | 0.9201 | 123.1522 | 0.47607 | 123.0377 | 123.2483 | 123.1247 | 123.0698 | 123.0789 | -123.2803 | -123.1476 | 122.9736 | 122.9919 | 122.4014 | 122.4106
660.25 | 123.0835 | -122.5662 | 0.54016 | -0.0020601 | 0.0062357 | 0.071275 | 0.065657 | 0.0032619 | -0.0010212 | 3.8448e-05 | -0.0043029 | 0.0045865 | 0.071478 | 0.057896 | -0.00030343 | 0.015436 | -0.006633 | -0.21515 | 0.54474 | -122.7585 | 0.29297 | -121.962 | -122.5891 | -122.6852 | -0.27008 | 0.5127 | -122.6395 | 0.36163 | -122.2504 | -122.2916 | -122.1085 | -0.19226 | 0.004578 | -0.24719 | 0.60425 | -0.11902 | -0.022888 | 0.073242 | 0.16937 | -0.073242 | -0.027466 | -0.17853 | 0.31586 | 0.45776 | 0.27466 | 0.53101 | 0.3479 | 0.79651 | 123.0515 | 0.3891 | 123.0011 | 123.3032 | 123.1522 | 123.111 | 123.0789 | -123.2986 | -123.1796 | 122.8592 | 122.9279 | 122.3511 | 122.2961
662 | 123.0927 | -122.5891 | 0.53101 | -0.0096891 | 0.0049539 | 0.070634 | 0.068861 | 0.0056119 | -0.0023028 | -0.0010298 | -0.0043029 | 0.0043729 | 0.071051 | 0.057255 | -0.00051703 | 0.014582 | -0.003215 | -0.21057 | 0.52643 | -122.7859 | 0.27924 | -121.9666 | -122.5754 | -122.6898 | -0.25177 | 0.49439 | -122.6532 | 0.3479 | -122.2641 | -122.3053 | -122.1085 | -0.19684 | -0.004578 | -0.25177 | 0.62256 | -0.10071 | 0.013733 | 0.096131 | 0.21057 | -0.064087 | -0.036621 | -0.18311 | 0.32501 | 0.48065 | 0.28381 | 0.54474 | 0.3479 | 0.8194 | 123.0652 | 0.3891 | 123.0011 | 123.3124 | 123.1476 | 123.1155 | 123.0835 | -123.317 | -123.1842 | 122.8683 | 122.937 | 122.3785 | 122.3373
663.6875 | 123.2712 | -122.5525 | 0.48065 | -0.0096891 | 0.0019631 | 0.06978 | 0.065443 | -0.0031467 | -0.0029438 | -0.0033796 | -0.0043029 | 0.0013821 | 0.068274 | 0.064946 | -8.9634e-05 | 0.015009 | -0.0006516 | -0.19684 | 0.48065 | -122.7768 | 0.39825 | -121.8018 | -122.4472 | -122.5388 | -0.07782 | 0.46234 | -122.6349 | 0.49896 | -122.081 | -122.1176 | -121.9894 | -0.2243 | 0 | -0.082398 | 0.75073 | 0.013733 | 0.10529 | 0.23804 | 0.32959 | -0.082398 | -0.018311 | 0.01831 | 0.4715 | 0.56305 | 0.43488 | 0.64545 | 0.51727 | 0.97504 | 123.175 | 0.55389 | 123.1339 | 123.2574 | 123.0972 | 123.0331 | 123.0148 | -123.2574 | -123.1155 | 122.9507 | 123.0515 | 122.3557 | 122.4747
665.4219 | 123.1888 | -122.5525 | 0.52643 | 0.0055694 | 0.0040995 | 0.069566 | 0.063948 | 0.0026211 | -0.001662 | -0.001457 | 0.0048523 | 0.0037319 | 0.069342 | 0.059178 | 0.00033757 | 0.013727 | 0.0004166 | -0.24719 | 0.5127 | -122.7676 | 0.36621 | -121.875 | -122.4884 | -122.58 | -0.21515 | 0.5127 | -122.644 | 0.44403 | -122.1588 | -122.2 | -122.0352 | -0.21515 | -0.013733 | -0.16022 | 0.67749 | -0.027466 | 0.064087 | 0.18768 | 0.27924 | -0.091553 | -0.013733 | -0.082397 | 0.39368 | 0.51727 | 0.35248 | 0.60883 | 0.44403 | 0.89264 | 123.1339 | 0.48523 | 123.0881 | 123.2803 | 123.1567 | 123.0652 | 123.0652 | -123.2941 | -123.1705 | 122.9187 | 122.9965 | 122.3053 | 122.3373
667.1875 | 123.2574 | -122.5296 | 0.52185 | -0.0020601 | 0.0021769 | 0.067857 | 0.061171 | -0.0031467 | -0.0031574 | -0.00081595 | -0.0043029 | 0.0037319 | 0.070624 | 0.064305 | -0.0028668 | 0.014582 | -0.0023606 | -0.23346 | 0.49896 | -122.7631 | 0.40283 | -121.8338 | -122.4335 | -122.5342 | -0.13275 | 0.49439 | -122.6166 | 0.50812 | -122.0764 | -122.1176 | -121.9894 | -0.23346 | -0.022889 | -0.11902 | 0.6958 | -0.004578 | 0.09613 | 0.22888 | 0.32959 | -0.086975 | -0.027466 | -0.013733 | 0.45319 | 0.54016 | 0.41199 | 0.62714 | 0.49896 | 0.92926 | 123.1659 | 0.54016 | 123.1247 | 123.262 | 123.111 | 123.0286 | 123.024 | -123.2849 | -123.1384 | 122.9324 | 123.0377 | 122.2961 | 122.3969
668.9219 | 123.1338 | -122.5708 | 0.5722 | -0.0020601 | 0.0015359 | 0.071489 | 0.065016 | 0.00027134 | -0.0029438 | 0.0021746 | 0.0018005 | 0.0041593 | 0.069556 | 0.059819 | -0.005003 | 0.015223 | -0.0006516 | -0.21515 | 0.54474 | -122.7997 | 0.34332 | -121.9391 | -122.5159 | -122.6212 | -0.21973 | 0.55389 | -122.6532 | 0.37079 | -122.2046 | -122.2504 | -122.0947 | -0.22888 | -0.027466 | -0.22888 | 0.63171 | -0.050354 | 0.054932 | 0.17853 | 0.28381 | -0.082397 | -0.018311 | -0.20142 | 0.36621 | 0.47607 | 0.32044 | 0.55847 | 0.40283 | 0.8606 | 123.143 | 0.44861 | 123.024 | 123.3444 | 123.2071 | 123.1155 | 123.1247 | -123.3719 | -123.2254 | 122.9141 | 122.9416 | 122.3557 | 122.3511
670.5938 | 123.1247 | -122.5983 | 0.54474 | 0.0055694 | 0.0058083 | 0.072557 | 0.066298 | 0.0026211 | -0.0020892 | -0.0020978 | 0.0018005 | 0.0035183 | 0.070624 | 0.069004 | -0.0028668 | 0.014368 | 0.000203 | -0.25177 | 0.52185 | -122.7676 | 0.2655 | -121.994 | -122.6074 | -122.6898 | -0.29755 | 0.52185 | -122.6624 | 0.37079 | -122.2778 | -122.2961 | -122.1222 | -0.16937 | -0.022888 | -0.27924 | 0.60425 | -0.091552 | -0.009155 | 0.07782 | 0.16022 | -0.064087 | -0.022888 | -0.17395 | 0.32044 | 0.47608 | 0.30212 | 0.54016 | 0.36621 | 0.77362 | 123.0331 | 0.38452 | 123.0331 | 123.2895 | 123.1842 | 123.1201 | 123.1201 | -123.3124 | -123.2071 | 122.8638 | 122.9691 | 122.3465 | 122.3007
672.3594 | 123.1567 | -122.4747 | 0.63171 | 0.036087 | 0.0051675 | 0.069994 | 0.066512 | 0.0066799 | -0.0018756 | -0.0010298 | 0.0079041 | 0.0045865 | 0.069769 | 0.061741 | -0.0030804 | 0.016291 | -0.0027878 | -0.15564 | 0.66376 | -122.7081 | 0.44403 | -121.8109 | -122.3877 | -122.493 | -0.15106 | 0.64087 | -122.5891 | 0.49896 | -122.0718 | -122.1451 | -121.9666 | -0.23346 | 0.032043 | -0.18768 | 0.66376 | -0.018311 | 0.086975 | 0.21515 | 0.32044 | -0.11444 | 0.009155 | -0.13275 | 0.40283 | 0.50812 | 0.32959 | 0.62256 | 0.44403 | 0.89722 | 123.1522 | 0.51727 | 123.0881 | 123.3719 | 123.23 | 123.1384 | 123.1155 | -123.3398 | -123.2208 | 122.9187 | 122.9736 | 122.319 | 122.3236
674.0469 | 123.2162 | -122.5937 | 0.50812 | 0.036087 | 0.0034585 | 0.072984 | 0.06523 | 0.0021939 | -0.0029438 | -0.001457 | 0.0079041 | 0.0039457 | 0.069983 | 0.063237 | -0.00094423 | 0.015436 | -0.0017196 | -0.22888 | 0.49439 | -122.7951 | 0.37079 | -121.8704 | -122.5113 | -122.6074 | -0.19226 | 0.48981 | -122.6669 | 0.42572 | -122.1817 | -122.2137 | -122.0444 | -0.20142 | -0.013733 | -0.13733 | 0.72327 | -0.013733 | 0.082397 | 0.18768 | 0.28381 | -0.073242 | -0.018311 | -0.082398 | 0.41199 | 0.54932 | 0.37994 | 0.62256 | 0.45319 | 0.92468 | 123.1659 | 0.48523 | 123.0927 | 123.2895 | 123.1567 | 123.0881 | 123.0835 | -123.3032 | -123.175 | 122.9645 | 123.0194 | 122.3648 | 122.4014
675.7812 | 123.1293 | -122.525 | 0.61798 | -0.0020601 | 0.0058083 | 0.070207 | 0.068434 | 5.774e-05 | -0.0037982 | -0.0029524 | 0.0018005 | 0.0054409 | 0.069128 | 0.055546 | 0.00012397 | 0.016077 | -0.0053512 | -0.18768 | 0.59967 | -122.7402 | 0.37537 | -121.8887 | -122.525 | -122.6028 | -0.21057 | 0.58594 | -122.5754 | 0.43488 | -122.1909 | -122.2366 | -122.0444 | -0.21515 | -0.018311 | -0.24262 | 0.63629 | -0.07782 | 0 | 0.13733 | 0.21515 | -0.050354 | -0.032044 | -0.18311 | 0.33417 | 0.48065 | 0.28839 | 0.53101 | 0.33875 | 0.85144 | 123.1155 | 0.38452 | 123.0103 | 123.3398 | 123.1613 | 123.1247 | 123.111 | -123.3582 | -123.1934 | 122.9004 | 122.9599 | 122.3373 | 122.3145
677.5469 | 123.2712 | -122.5067 | 0.54016 | -0.0020601 | 0.0040995 | 0.070848 | 0.064803 | 0.0034755 | -0.0014484 | -0.0029524 | -0.0043029 | 0.0050137 | 0.07041 | 0.066014 | 0.00012397 | 0.016504 | -0.0047104 | -0.20142 | 0.54016 | -122.7036 | 0.45319 | -121.8201 | -122.4335 | -122.5342 | -0.1236 | 0.52185 | -122.5845 | 0.56763 | -122.0718 | -122.1222 | -121.9437 | -0.19684 | 0 | -0.086975 | 0.68665 | -0.027466 | 0.073242 | 0.16937 | 0.27008 | -0.07782 | -0.01831 | 0.027466 | 0.43488 | 0.56305 | 0.38452 | 0.64087 | 0.46234 | 0.88348 | 123.1567 | 0.5127 | 123.1522 | 123.2437 | 123.1064 | 123.0469 | 123.0286 | -123.2437 | -123.1247 | 122.9599 | 123.0743 | 122.3053 | 122.3831
679.2969 | 123.2208 | -122.2412 | 0.87891 | 0.013199 | 0.0026041 | 0.069994 | 0.066939 | -0.0016513 | -0.0018756 | -0.00017515 | 0.0079041 | 0.0033047 | 0.071265 | 0.06815 | -0.0041486 | 0.015864 | 0.000203 | -0.23804 | 0.8194 | -122.4564 | 0.6958 | -121.5683 | -122.168 | -122.2687 | -0.18768 | 0.82398 | -122.3053 | 0.76904 | -121.8338 | -121.8842 | -121.7239 | -0.21515 | -0.059509 | -0.1831 | 0.67291 | -0.027466 | 0.073242 | 0.18768 | 0.28839 | -0.064087 | -0.054931 | -0.10986 | 0.40741 | 0.51727 | 0.35706 | 0.58136 | 0.42114 | 0.88806 | 123.1522 | 0.4715 | 123.0743 | 123.2758 | 123.1293 | 123.0606 | 123.0652 | -123.3353 | -123.1842 | 122.937 | 123.0103 | 122.0032 | 122.0535
681.0625 | 123.2529 | -122.2549 | 0.82855 | 0.0055694 | 0.0051675 | 0.070848 | 0.065871 | 0.00048494 | 0.001115 | 0.00089285 | -0.0012513 | 0.0041593 | 0.069983 | 0.057682 | 0.001833 | 0.015223 | -0.0042832 | -0.20142 | 0.79193 | -122.4701 | 0.70953 | -121.55 | -122.2 | -122.2824 | -0.1236 | 0.78278 | -122.3236 | 0.81482 | -121.8201 | -121.8796 | -121.6873 | -0.21515 | -0.036621 | -0.11902 | 0.70496 | -0.027466 | 0.054932 | 0.18768 | 0.27008 | -0.068664 | -0.045776 | -0.013733 | 0.43488 | 0.56763 | 0.37537 | 0.63629 | 0.44403 | 0.92011 | 123.1796 | 0.50354 | 123.1384 | 123.262 | 123.1064 | 123.0469 | 123.0377 | -123.2986 | -123.1522 | 122.9645 | 123.0698 | 122.0535 | 122.1313
682.8125 | 123.1064 | -122.0764 | 1.03 | -0.0020601 | 0.0060221 | 0.071489 | 0.065657 | 0.0041165 | -0.0010212 | -0.003166 | -0.0043029 | 0.0045865 | 0.072333 | 0.062596 | -0.003294 | 0.016718 | -0.001506 | -0.21515 | 1.0254 | -122.3282 | 0.71411 | -121.5546 | -122.1085 | -122.1954 | -0.32959 | 0.96588 | -122.1634 | 0.86975 | -121.7422 | -121.8063 | -121.6415 | -0.25177 | -0.004577 | -0.31586 | 0.52185 | -0.11902 | -0.032043 | 0.13275 | 0.21973 | -0.086975 | -0.064087 | -0.16022 | 0.33417 | 0.43487 | 0.27008 | 0.52185 | 0.35706 | 0.77362 | 123.0423 | 0.42114 | 123.0331 | 123.3536 | 123.1293 | 123.1018 | 123.0423 | -123.3582 | -123.1934 | 122.7905 | 122.9462 | 121.8613 | 121.7468
684.5 | 123.1293 | -120.8679 | 2.243 | 0.0055694 | 0.0081583 | 0.070207 | 0.067152 | 0.0064663 | -0.0023028 | 0.00046565 | -0.0043029 | 0.0052273 | 0.069128 | 0.065159 | -0.0030804 | 0.015223 | -0.0010788 | -0.20142 | 2.1973 | -121.1014 | 1.9318 | -120.3644 | -120.9686 | -121.0281 | -0.20599 | 2.124 | -121.0052 | 2.0325 | -120.5704 | -120.5887 | -120.3735 | -0.23346 | -0.045776 | -0.31128 | 0.50354 | -0.16022 | -0.10071 | 0.073242 | 0.13275 | -0.13733 | -0.11902 | -0.21057 | 0.29755 | 0.49438 | 0.27924 | 0.63171 | 0.41657 | 0.737 | 123.0331 | 0.43488 | 123.0377 | 123.2986 | 123.1293 | 123.0652 | 122.9919 | -123.3444 | -123.2483 | 122.7997 | 122.9004 | 120.6665 | 120.6619
686.2344 | 123.2162 | -122.2321 | 0.86975 | 0.020828 | 0.0017495 | 0.070848 | 0.065443 | -0.00058326 | -0.0014484 | -0.00038875 | 0.0018005 | 0.0041593 | 0.071265 | 0.067936 | -0.0028668 | 0.01565 | 0.0010574 | -0.25177 | 0.83771 | -122.438 | 0.6958 | -121.5591 | -122.1634 | -122.2595 | -0.21057 | 0.80566 | -122.3328 | 0.75073 | -121.8384 | -121.8842 | -121.7056 | -0.20599 | -0.032043 | -0.17395 | 0.67291 | -0.027465 | 0.068665 | 0.17853 | 0.27466 | -0.10071 | -0.064087 | -0.11902 | 0.39368 | 0.52643 | 0.3479 | 0.62714 | 0.44861 | 0.87891 | 123.1339 | 0.49438 | 123.0835 | 123.2758 | 123.1384 | 123.0698 | 123.0377 | -123.3078 | -123.2025 | 122.9279 | 122.9828 | 121.9803 | 122.0215
687.9844 | 123.2254 | -122.2641 | 0.81024 | 0.0055694 | 0.0058083 | 0.073839 | 0.064803 | 0.0049709 | -0.0012348 | 0.0013202 | 0.010956 | 0.0028775 | 0.07276 | 0.064305 | -0.0030804 | 0.015864 | -0.0002244 | -0.17853 | 0.7782 | -122.4838 | 0.71869 | -121.5271 | -122.1863 | -122.2595 | -0.09613 | 0.79193 | -122.3557 | 0.75073 | -121.8704 | -121.907 | -121.7651 | -0.21973 | -0.032044 | -0.091553 | 0.737 | 0.004578 | 0.07782 | 0.2243 | 0.29755 | -0.091553 | -0.018311 | -0.05951 | 0.39368 | 0.49896 | 0.35706 | 0.59052 | 0.44861 | 0.95673 | 123.2025 | 0.48523 | 123.1064 | 123.262 | 123.1476 | 123.0423 | 123.056 | -123.2941 | -123.1659 | 122.9828 | 123.0148 | 122.0856 | 122.168
689.6562 | 123.2346 | -122.3511 | 0.74616 | -0.0020601 | 0.0019631 | 0.069139 | 0.063094 | 0.0034755 | -0.0048664 | -0.0023114 | -0.0012513 | 0.0045865 | 0.072546 | 0.06046 | -0.0062848 | 0.016504 | 0.0014846 | -0.17853 | 0.6958 | -122.5571 | 0.64545 | -121.5912 | -122.2137 | -122.3328 | -0.086975 | 0.69122 | -122.374 | 0.67749 | -121.8887 | -121.9254 | -121.788 | -0.20599 | -0.050354 | -0.10071 | 0.75989 | 0.01831 | 0.13733 | 0.2243 | 0.34332 | -0.022888 | -0.054932 | -0.068665 | 0.46234 | 0.56305 | 0.42572 | 0.58594 | 0.44861 | 0.96588 | 123.2025 | 0.48523 | 123.0515 | 123.2529 | 123.0652 | 123.0469 | 123.0423 | -123.3032 | -123.1201 | 122.9965 | 123.0286 | 122.1725 | 122.2641
691.4062 | 123.1247 | -121.8018 | 1.3367 | -0.0020601 | 0.0064493 | 0.069353 | 0.067793 | 0.00069854 | -0.0025166 | -0.0010298 | -0.0012513 | 0.0048001 | 0.070624 | 0.056187 | -0.00073063 | 0.015864 | -0.0025742 | -0.17395 | 1.2863 | -121.9757 | 1.1078 | -121.1609 | -121.7972 | -121.8704 | -0.21515 | 1.2955 | -121.843 | 1.1627 | -121.463 | -121.5179 | -121.3028 | -0.17395 | -0.050354 | -0.22888 | 0.64087 | -0.068664 | 0.004578 | 0.10529 | 0.17853 | -0.041199 | -0.041199 | -0.17395 | 0.33875 | 0.49896 | 0.28381 | 0.54016 | 0.32501 | 0.81482 | 123.0835 | 0.37994 | 123.0057 | 123.262 | 123.1384 | 123.0881 | 123.0972 | -123.3124 | -123.1796 | 122.9095 | 122.9645 | 121.6278 | 121.5866
693.1094 | 123.2391 | -120.4468 | 2.5864 | -0.0096891 | 0.0026041 | 0.070421 | 0.066084 | 0.0017667 | -0.0027302 | -0.0016706 | -0.0012513 | 0.0035183 | 0.066565 | 0.066868 | 0.0016194 | 0.014582 | -0.0059922 | -0.28839 | 2.7512 | -120.4468 | 2.6596 | -119.664 | -120.2591 | -120.3506 | -0.2655 | 2.6825 | -120.4468 | 2.6138 | -120.0348 | -120.076 | -119.8791 | 0 | 0.1648 | 0.073242 | 0.78278 | 0.09613 | 0.18768 | 0.09613 | 0.18768 | 0 | 0.09613 | 0.027466 | 0.41199 | 0.56763 | 0.37079 | 0.56763 | 0.37079 | 0.78278 | 123.1064 | 0.41199 | 123.0606 | 123.1979 | 123.1293 | 123.1979 | 123.1293 | -123.0331 | -123.0331 | 123.1064 | 123.0606 | 120.1584 | 120.1813
694.8438 | 123.1796 | -121.7056 | 1.3962 | 0.043716 | 0.0040995 | 0.072984 | 0.065016 | 0.0013393 | -0.0010212 | 0.00025205 | 0.010956 | 0.0048001 | 0.068701 | 0.0611 | -0.0043622 | 0.014368 | 0.0014846 | -0.11902 | 1.4053 | -121.9482 | 1.236 | -120.9961 | -121.6187 | -121.7102 | -0.10529 | 1.4053 | -121.7789 | 1.2772 | -121.2708 | -121.3531 | -121.1792 | -0.24261 | 0.009155 | -0.16022 | 0.70953 | -0.004578 | 0.086975 | 0.23804 | 0.32959 | -0.073243 | 0.009155 | -0.11902 | 0.43488 | 0.52643 | 0.35248 | 0.59967 | 0.42572 | 0.95215 | 123.1842 | 0.50812 | 123.056 | 123.3536 | 123.1842 | 123.111 | 123.111 | -123.3444 | -123.175 | 122.9416 | 122.9828 | 121.5866 | 121.6003
696.5938 | 123.1155 | -120.9366 | 2.1835 | 0.0055694 | 0.0055947 | 0.068498 | 0.06523 | 0.00027134 | -0.0040118 | -0.0020978 | -0.0043029 | 0.0035183 | 0.070837 | 0.056401 | -0.0011578 | 0.016718 | -0.002147 | -0.21515 | 2.179 | -121.1334 | 1.973 | -120.3232 | -120.9229 | -121.0098 | -0.21515 | 2.1606 | -120.9778 | 2.0233 | -120.5841 | -120.6757 | -120.4193 | -0.19684 | -0.004578 | -0.21057 | 0.6134 | -0.073243 | 0.013732 | 0.1236 | 0.21057 | -0.041199 | -0.022888 | -0.16022 | 0.35248 | 0.51727 | 0.26093 | 0.55847 | 0.30212 | 0.81024 | 123.1064 | 0.39368 | 123.0011 | 123.3124 | 123.1384 | 123.1155 | 123.0972 | -123.317 | -123.1613 | 122.9095 | 122.9599 | 120.7214 | 120.7214
698.3594 | 123.1384 | -121.994 | 1.1398 | -0.0020601 | 0.0060221 | 0.07213 | 0.065016 | 0.0041165 | 4.7018e-05 | -0.0016706 | -0.0012513 | 0.0035183 | 0.071692 | 0.05811 | -0.0013714 | 0.016718 | -0.0010788 | -0.25177 | 1.1307 | -122.1725 | 0.87433 | -121.4035 | -121.9894 | -122.0718 | -0.25177 | 1.0757 | -122.0673 | 0.98419 | -121.637 | -121.6919 | -121.4859 | -0.17853 | -0.009156 | -0.2655 | 0.59052 | -0.077819 | 0.004578 | 0.10071 | 0.1831 | -0.073242 | -0.064087 | -0.15564 | 0.35706 | 0.50812 | 0.30212 | 0.58136 | 0.37537 | 0.76904 | 123.0469 | 0.4303 | 123.0515 | 123.3032 | 123.143 | 123.1247 | 123.0698 | -123.3124 | -123.2071 | 122.8683 | 122.9782 | 121.7422 | 121.7422
700.0625 | 123.2071 | -122.1313 | 0.90637 | 0.020828 | 0.0038857 | 0.071703 | 0.064375 | 0.0039029 | -0.0012348 | 0.0011066 | 0.014008 | 0.0052273 | 0.070196 | 0.067296 | -0.001585 | 0.016077 | -0.0034286 | -0.19226 | 0.9201 | -122.3694 | 0.84686 | -121.3806 | -122.049 | -122.1222 | -0.11444 | 0.90637 | -122.2321 | 0.88348 | -121.7239 | -121.7743 | -121.6095 | -0.23804 | 0.013733 | -0.059509 | 0.75073 | 0.009156 | 0.082398 | 0.24719 | 0.32043 | -0.10071 | 0 | -0.022888 | 0.40741 | 0.52185 | 0.35706 | 0.62256 | 0.45776 | 0.98877 | 123.2162 | 0.50812 | 123.1155 | 123.2895 | 123.1384 | 123.0515 | 123.0377 | -123.2758 | -123.1384 | 122.9782 | 123.0148 | 121.9391 | 122.0169
701.7969 | 123.1796 | -122.1817 | 0.90637 | 0.036087 | 0.0051675 | 0.071275 | 0.064375 | 0.0045437 | -0.0018756 | 0.0030292 | 0.0079041 | 0.0065091 | 0.070837 | 0.06046 | -0.0020122 | 0.015009 | 0.0004166 | -0.13275 | 0.9201 | -122.4243 | 0.75073 | -121.4905 | -122.113 | -122.2092 | -0.11902 | 0.90637 | -122.2687 | 0.8194 | -121.7789 | -121.843 | -121.669 | -0.24261 | 0.013733 | -0.15564 | 0.69122 | -0.027465 | 0.068665 | 0.21515 | 0.31128 | -0.086975 | 0 | -0.086975 | 0.40283 | 0.5127 | 0.33875 | 0.59967 | 0.42572 | 0.93384 | 123.175 | 0.48981 | 123.0881 | 123.3444 | 123.175 | 123.1018 | 123.0881 | -123.3307 | -123.175 | 122.9324 | 123.0011 | 122.049 | 122.0627
703.5469 | 123.1293 | -122.3465 | 0.80566 | -0.0096891 | 0.0047403 | 0.070634 | 0.06288 | 0.0019803 | -0.0027302 | -0.00081595 | 0.020111 | 0.0043729 | 0.069983 | 0.05811 | -0.0039348 | 0.013727 | -0.0019332 | -0.21973 | 0.7782 | -122.525 | 0.52643 | -121.7056 | -122.2778 | -122.374 | -0.20142 | 0.81482 | -122.4243 | 0.60425 | -121.9757 | -122.0123 | -121.8384 | -0.17853 | -0.027466 | -0.27924 | 0.64087 | -0.027465 | 0.068665 | 0.15106 | 0.24719 | -0.077819 | 0.009155 | -0.20142 | 0.37079 | 0.50812 | 0.33417 | 0.58594 | 0.41199 | 0.8194 | 123.0515 | 0.44861 | 123.0286 | 123.3032 | 123.2391 | 123.1247 | 123.1613 | -123.3307 | -123.23 | 122.8729 | 122.9507 | 122.1268 | 122.1451
705.2969 | 123.2712 | -122.0764 | 0.97504 | -0.0096891 | 0.0045267 | 0.069353 | 0.062239 | -0.00058326 | -0.0025166 | -0.0029524 | -0.0012513 | 0.0020231 | 0.07276 | 0.064518 | -0.001585 | 0.01565 | -0.0042832 | -0.19226 | 0.95673 | -122.2824 | 0.87891 | -121.3394 | -121.9711 | -122.0535 | -0.07782 | 0.94299 | -122.1588 | 0.94757 | -121.6095 | -121.6553 | -121.5179 | -0.20599 | -0.018311 | -0.096131 | 0.737 | 0.022888 | 0.10529 | 0.22888 | 0.31128 | -0.082397 | -0.032044 | -0.027466 | 0.46692 | 0.55847 | 0.42114 | 0.64087 | 0.50354 | 0.94299 | 123.1613 | 0.54932 | 123.1064 | 123.2391 | 123.1018 | 123.0331 | 123.0194 | -123.2574 | -123.1338 | 122.9553 | 123.024 | 121.8842 | 121.9986
707.0469 | 123.2666 | -121.9025 | 1.149 | -0.0020601 | 0.0043131 | 0.071062 | 0.065657 | -0.0016513 | -0.0040118 | -0.0018842 | -0.0012513 | 0.0030911 | 0.070624 | 0.063664 | -0.002226 | 0.013727 | -0.0023606 | -0.19684 | 1.1444 | -122.0947 | 1.0986 | -121.1243 | -121.7422 | -121.8567 | -0.068665 | 1.1398 | -121.9528 | 1.1627 | -121.3943 | -121.4401 | -121.3074 | -0.19226 | -0.004578 | -0.050354 | 0.7782 | 0.045777 | 0.16022 | 0.23804 | 0.35248 | -0.050354 | -0.009155 | 0.013733 | 0.50812 | 0.59509 | 0.46234 | 0.64545 | 0.5127 | 0.97046 | 123.1934 | 0.55847 | 123.1155 | 123.2391 | 123.0927 | 123.0469 | 123.0423 | -123.2437 | -123.1018 | 123.0011 | 123.0652 | 121.7056 | 121.8338
708.7812 | 123.1659 | -121.7789 | 1.3092 | 0.028458 | 0.0038857 | 0.06978 | 0.065016 | 0.0030483 | -0.0035846 | -0.001457 | -0.0012513 | 0.0052273 | 0.069983 | 0.056828 | -0.0020122 | 0.015009 | 0.0008438 | -0.13733 | 1.3046 | -122.0352 | 1.149 | -121.1014 | -121.7148 | -121.8109 | -0.10529 | 1.3 | -121.8613 | 1.2085 | -121.3806 | -121.4355 | -121.2662 | -0.25635 | -0.004578 | -0.16022 | 0.67749 | -0.032043 | 0.064087 | 0.2243 | 0.32043 | -0.082397 | -0.009155 | -0.10071 | 0.39825 | 0.5127 | 0.34332 | 0.59509 | 0.42572 | 0.93384 | 123.1842 | 0.48065 | 123.0698 | 123.3398 | 123.1613 | 123.0835 | 123.0789 | -123.3444 | -123.1705 | 122.9279 | 122.9874 | 121.6415 | 121.6736
710.4688 | 123.1567 | -121.2479 | 1.8723 | 0.036087 | 0.0047403 | 0.070848 | 0.068221 | 0.0034755 | -0.0018756 | 0.00089285 | 0.014008 | 0.0054409 | 0.071905 | 0.058964 | -0.001585 | 0.014368 | -0.0017196 | -0.17853 | 1.8402 | -121.5225 | 1.6434 | -120.5887 | -121.1655 | -121.257 | -0.16022 | 1.8448 | -121.3211 | 1.7349 | -120.8267 | -120.9 | -120.7306 | -0.27466 | -0.032043 | -0.22888 | 0.65918 | -0.009155 | 0.082398 | 0.2655 | 0.35706 | -0.073242 | -0.027465 | -0.13733 | 0.42114 | 0.51727 | 0.3479 | 0.59051 | 0.42114 | 0.93384 | 123.1659 | 0.49438 | 123.056 | 123.3627 | 123.1659 | 123.0881 | 123.0927 | -123.3948 | -123.1934 | 122.8912 | 122.9828 | 121.0693 | 121.0876
712.2188 | 123.1842 | -121.6736 | 1.4008 | 0.013199 | 0.0019631 | 0.071703 | 0.063735 | -0.0016513 | -0.0025166 | -0.0020978 | 0.0079041 | 0.0048001 | 0.071905 | 0.065587 | -0.00030343 | 0.014155 | -0.0012924 | -0.23346 | 1.5289 | -121.7331 | 1.4145 | -120.8359 | -121.4584 | -121.5775 | -0.31128 | 1.4511 | -121.7056 | 1.3458 | -121.2524 | -121.2936 | -121.1288 | -0.059509 | 0.12817 | 0.013733 | 0.83771 | 0.09613 | 0.21515 | 0.15564 | 0.27466 | -0.032043 | 0.050354 | -0.054932 | 0.42114 | 0.54474 | 0.37994 | 0.57678 | 0.41199 | 0.89722 | 123.1476 | 0.45319 | 123.0515 | 123.262 | 123.1567 | 123.2025 | 123.1247 | -123.1338 | -123.1064 | 123.0881 | 123.0194 | 121.4401 | 121.3623
713.9688 | 123.1476 | -121.582 | 1.5244 | 0.013199 | 0.0070901 | 0.070207 | 0.066512 | 0.0021939 | -0.0035846 | -0.0012434 | 0.0048523 | 0.0043729 | 0.069769 | 0.060673 | -0.0024396 | 0.017359 | -0.0042832 | -0.16479 | 1.5472 | -121.7468 | 1.355 | -120.8954 | -121.5134 | -121.6003 | -0.17853 | 1.506 | -121.6141 | 1.4236 | -121.1975 | -121.2524 | -121.0419 | -0.16479 | 0.022888 | -0.16937 | 0.68664 | -0.018311 | 0.068664 | 0.14648 | 0.23346 | -0.032044 | -0.018311 | -0.10071 | 0.38452 | 0.54016 | 0.32959 | 0.5722 | 0.36163 | 0.85144 | 123.1018 | 0.41657 | 123.0377 | 123.2941 | 123.1201 | 123.1293 | 123.0881 | -123.2712 | -123.1384 | 122.937 | 123.0057 | 121.4172 | 121.4035
715.6406 | 123.2208 | -121.8109 | 1.2177 | 0.028458 | 0.0053811 | 0.072984 | 0.066084 | 0.00027134 | -0.00059378 | 0.0017474 | 0.010956 | 0.0030911 | 0.072119 | 0.064946 | 0.00055117 | 0.016718 | -0.004924 | -0.13275 | 1.2497 | -122.0032 | 1.1673 | -121.0464 | -121.6827 | -121.7834 | -0.082397 | 1.2314 | -121.907 | 1.1993 | -121.3943 | -121.4493 | -121.2753 | -0.19226 | 0.032044 | -0.050354 | 0.76447 | 0.027466 | 0.12817 | 0.21973 | 0.32044 | -0.09613 | 0.013733 | -0.01831 | 0.41657 | 0.53558 | 0.36163 | 0.63171 | 0.45776 | 0.95673 | 123.1705 | 0.5127 | 123.1064 | 123.2529 | 123.1384 | 123.0606 | 123.0423 | -123.2208 | -123.1247 | 122.9782 | 123.0103 | 121.6782 | 121.7285
717.3906 | 123.1338 | -121.7697 | 1.3321 | -0.0096891 | 0.0051675 | 0.071489 | 0.068221 | 0.0030483 | -0.0037982 | -0.0027386 | -0.0012513 | 0.0056545 | 0.070624 | 0.0611 | 0.001833 | 0.015223 | -1.0598e-05 | -0.23346 | 1.3412 | -121.9482 | 1.0803 | -121.1792 | -121.7789 | -121.8475 | -0.24719 | 1.3046 | -121.843 | 1.1765 | -121.4264 | -121.4767 | -121.257 | -0.17853 | 0.009156 | -0.25177 | 0.59051 | -0.07782 | -0.009156 | 0.10071 | 0.16937 | -0.073243 | -0.027466 | -0.15564 | 0.34332 | 0.51269 | 0.29297 | 0.58594 | 0.36621 | 0.76904 | 123.0286 | 0.41656 | 123.0194 | 123.2895 | 123.1476 | 123.111 | 123.0743 | -123.2803 | -123.175 | 122.85 | 122.9462 | 121.5363 | 121.5225
719.0781 | 123.1979 | -121.9116 | 1.1215 | 0.0055694 | 0.0036721 | 0.068925 | 0.067152 | 0.0021939 | -0.0012348 | 0.0026018 | -0.0043029 | 0.0043729 | 0.068915 | 0.062169 | -0.0011578 | 0.01565 | -0.0023606 | -0.23804 | 1.1627 | -122.1634 | 0.96588 | -121.3074 | -121.9208 | -121.994 | -0.18768 | 1.1215 | -122.0032 | 1.0941 | -121.5225 | -121.5454 | -121.3531 | -0.25177 | 0.041199 | -0.15564 | 0.60425 | -0.082398 | -0.009155 | 0.16937 | 0.24262 | -0.091553 | 0 | -0.027466 | 0.3891 | 0.55847 | 0.36621 | 0.65002 | 0.45776 | 0.85602 | 123.1293 | 0.48065 | 123.0972 | 123.3261 | 123.1247 | 123.0743 | 123.0331 | -123.2849 | -123.1247 | 122.8775 | 123.0057 | 121.6736 | 121.7239
720.8125 | 123.1842 | -121.9986 | 1.0483 | -0.0096891 | 0.0051675 | 0.071062 | 0.067152 | -0.0018649 | -0.0027302 | -0.0012434 | -0.0043029 | 0.0030911 | 0.069342 | 0.066014 | 0.00033757 | 0.015009 | -0.0034286 | -0.23804 | 1.062 | -122.2321 | 0.84686 | -121.3898 | -122.0261 | -122.081 | -0.1831 | 1.0162 | -122.0993 | 0.99792 | -121.6141 | -121.6461 | -121.4584 | -0.23346 | 0.013733 | -0.20142 | 0.60883 | -0.082398 | -0.027466 | 0.15106 | 0.20599 | -0.10071 | -0.032044 | -0.050354 | 0.38452 | 0.54016 | 0.35248 | 0.64087 | 0.45319 | 0.84229 | 123.0789 | 0.48523 | 123.0972 | 123.2941 | 123.1155 | 123.0606 | 123.0148 | -123.2803 | -123.1476 | 122.8455 | 122.9965 | 121.7606 | 121.8155
722.5 | 123.1201 | -121.9482 | 1.149 | -0.0020601 | 0.0043131 | 0.069353 | 0.065016 | -0.00058326 | -0.0023028 | 0.0013202 | 0.014008 | 0.0062955 | 0.071905 | 0.05341 | -0.0054302 | 0.014155 | 0.0006302 | -0.24261 | 1.1627 | -122.1954 | 0.88348 | -121.312 | -121.875 | -121.9757 | -0.21057 | 1.181 | -122.049 | 0.96588 | -121.5958 | -121.637 | -121.4493 | -0.24719 | 0.013733 | -0.2655 | 0.63629 | -0.027466 | 0.073242 | 0.21973 | 0.32044 | -0.10071 | 0.032043 | -0.18311 | 0.35248 | 0.49896 | 0.31128 | 0.59967 | 0.41199 | 0.88348 | 123.0789 | 0.45319 | 123.0148 | 123.3582 | 123.23 | 123.111 | 123.1293 | -123.3444 | -123.1979 | 122.8317 | 122.9141 | 121.7056 | 121.7377
724.2656 | 123.1201 | -121.9025 | 1.2131 | 0.043716 | 0.0036721 | 0.071703 | 0.066725 | -0.00036966 | -0.0029438 | 0.00025205 | 0.014008 | 0.0065091 | 0.074683 | 0.060673 | -0.0045758 | 0.015009 | -0.001506 | -0.21057 | 1.2177 | -122.1405 | 0.99335 | -121.2479 | -121.8201 | -121.9482 | -0.20599 | 1.2177 | -121.994 | 1.0391 | -121.5363 | -121.5683 | -121.376 | -0.23804 | 0.004577 | -0.21973 | 0.6546 | -0.045776 | 0.082398 | 0.19226 | 0.32043 | -0.091553 | 0.004577 | -0.17395 | 0.36621 | 0.52643 | 0.33417 | 0.61798 | 0.42572 | 0.89264 | 123.1338 | 0.45776 | 123.0331 | 123.3582 | 123.2117 | 123.1201 | 123.1201 | -123.3536 | -123.2071 | 122.8958 | 122.9416 | 121.6919 | 121.6965
725.9531 | 123.2346 | -122.3053 | 0.74616 | -0.0020601 | 0.00089511 | 0.071062 | 0.061598 | 0.0032619 | -0.001662 | -0.00017515 | -0.0073547 | 0.0022367 | 0.068701 | 0.067509 | -0.0037212 | 0.015223 | -0.0019332 | -0.19226 | 0.72784 | -122.5113 | 0.67291 | -121.5317 | -122.1817 | -122.2595 | -0.07782 | 0.71411 | -122.3557 | 0.73242 | -121.7926 | -121.8338 | -121.6965 | -0.20599 | -0.018311 | -0.073242 | 0.77362 | 0.045777 | 0.1236 | 0.25177 | 0.32959 | -0.050354 | -0.032044 | -0.013733 | 0.51269 | 0.60883 | 0.4715 | 0.65918 | 0.52185 | 0.97961 | 123.1842 | 0.56305 | 123.0881 | 123.2391 | 123.0698 | 123.0331 | 123.0194 | -123.2574 | -123.1018 | 122.9782 | 123.0377 | 122.113 | 122.2275
727.6875 | 123.2162 | -122.3373 | 0.70496 | 0.0055694 | 0.0043131 | 0.071916 | 0.067366 | 0.0047573 | 0.00068782 | 0.0013202 | 0.010956 | 0.0052273 | 0.073614 | 0.061314 | 0.00012397 | 0.015223 | -0.002147 | -0.15564 | 0.71869 | -122.5525 | 0.65002 | -121.5775 | -122.2229 | -122.3099 | -0.091553 | 0.69122 | -122.4197 | 0.69122 | -121.8842 | -121.9345 | -121.7606 | -0.21515 | 0.013733 | -0.054932 | 0.75989 | 0.027466 | 0.11444 | 0.24262 | 0.32959 | -0.082398 | -0.013733 | -0.013733 | 0.45319 | 0.57678 | 0.40283 | 0.65918 | 0.48523 | 0.97504 | 123.2025 | 0.53558 | 123.111 | 123.2712 | 123.111 | 123.056 | 123.0286 | -123.2574 | -123.1247 | 122.9874 | 123.0286 | 122.1817 | 122.2458
729.4531 | 123.1796 | -122.2916 | 0.75989 | 0.028458 | 0.0032449 | 0.071489 | 0.06523 | 0.0015529 | -0.0025166 | 0.00025205 | 0.0079041 | 0.0041593 | 0.071051 | 0.071141 | 0.001192 | 0.017786 | -0.0008652 | -0.32044 | 0.72784 | -122.5113 | 0.59967 | -121.6507 | -122.2504 | -122.3373 | -0.27924 | 0.72784 | -122.3877 | 0.65002 | -121.9162 | -121.9437 | -121.7697 | -0.21973 | -0.032044 | -0.16022 | 0.64087 | -0.045776 | 0.041199 | 0.17395 | 0.26093 | -0.09613 | -0.032044 | -0.10986 | 0.37537 | 0.52185 | 0.3479 | 0.61798 | 0.44403 | 0.8606 | 123.111 | 0.4715 | 123.0377 | 123.2391 | 123.1155 | 123.0194 | 123.0194 | -123.2712 | -123.1476 | 122.8912 | 122.9416 | 121.9711 | 122.0123
731.1875 | 123.2254 | -122.113 | 0.89264 | -0.0020601 | 0.0017495 | 0.069353 | 0.064589 | 0.0019803 | -0.0014484 | -0.0020978 | -0.0012513 | 0.0035183 | 0.069769 | 0.064305 | -8.9634e-05 | 0.014582 | -0.003856 | -0.24261 | 0.90179 | -122.3602 | 0.7782 | -121.4493 | -122.0718 | -122.1817 | -0.14648 | 0.87891 | -122.2 | 0.89722 | -121.701 | -121.7422 | -121.55 | -0.24719 | 0.009155 | -0.11444 | 0.66376 | -0.068665 | 0.041199 | 0.17853 | 0.28839 | -0.086975 | -0.013733 | 0.004578 | 0.41199 | 0.56305 | 0.37079 | 0.65002 | 0.45776 | 0.91095 | 123.1384 | 0.49896 | 123.0972 | 123.262 | 123.0789 | 123.0148 | 122.9919 | -123.2529 | -123.0927 | 122.8912 | 123.0103 | 121.8704 | 121.9666
732.875 | 123.23 | -122.0993 | 0.90637 | -0.0020601 | 0.0019631 | 0.070848 | 0.066298 | 0.0024075 | -0.003371 | -0.0010298 | -0.0043029 | 0.0035183 | 0.071478 | 0.063664 | -0.0039348 | 0.016291 | -0.002147 | -0.22888 | 0.90637 | -122.3511 | 0.82398 | -121.4035 | -122.0078 | -122.0856 | -0.11902 | 0.88806 | -122.1909 | 0.91095 | -121.6644 | -121.6965 | -121.5271 | -0.25177 | 0 | -0.082397 | 0.6958 | 0.013733 | 0.091553 | 0.2655 | 0.34332 | -0.091553 | -0.01831 | 0.004578 | 0.43488 | 0.5722 | 0.40283 | 0.66376 | 0.49438 | 0.94757 | 123.175 | 0.52643 | 123.1018 | 123.2574 | 123.0789 | 123.0057 | 122.9874 | -123.2574 | -123.0972 | 122.9233 | 123.0103 | 121.8704 | 121.9803
734.625 | 123.0927 | -122.2549 | 0.84686 | -0.0096891 | 0.0062357 | 0.069994 | 0.066298 | 0.00027134 | -0.0010212 | 0.00089285 | 0.0018005 | 0.0065091 | 0.071051 | 0.062809 | 0.00055117 | 0.01565 | -0.0034286 | -0.19226 | 0.82855 | -122.4792 | 0.63171 | -121.6187 | -122.2412 | -122.3419 | -0.2243 | 0.82398 | -122.3236 | 0.67749 | -121.9208 | -121.9482 | -121.7422 | -0.2243 | -0.018311 | -0.21515 | 0.63629 | -0.086975 | 0.013733 | 0.13733 | 0.23804 | -0.068664 | -0.022888 | -0.16937 | 0.33417 | 0.51269 | 0.3067 | 0.58136 | 0.37537 | 0.8606 | 123.111 | 0.40283 | 123.0011 | 123.3078 | 123.1476 | 123.0835 | 123.0789 | -123.3261 | -123.1705 | 122.8867 | 122.9324 | 122.0627 | 122.0306
736.375 | 123.1018 | -122.2321 | 0.87433 | 0.051346 | 0.0047403 | 0.070848 | 0.06523 | 0.0011257 | -0.0025166 | -0.003166 | 0.0079041 | 0.0069363 | 0.071478 | 0.058537 | -0.0028668 | 0.015009 | 0.0010574 | -0.20142 | 0.88806 | -122.4564 | 0.65918 | -121.582 | -122.168 | -122.2595 | -0.21515 | 0.87433 | -122.3099 | 0.71411 | -121.8704 | -121.8933 | -121.6965 | -0.2243 | 0.013733 | -0.21515 | 0.65002 | -0.027465 | 0.064087 | 0.19684 | 0.28839 | -0.077819 | 0 | -0.16022 | 0.36163 | 0.53558 | 0.33875 | 0.6134 | 0.41656 | 0.87433 | 123.1155 | 0.43945 | 123.024 | 123.3444 | 123.1842 | 123.1201 | 123.1064 | -123.3307 | -123.1842 | 122.8912 | 122.9462 | 122.0306 | 122.0169
738.0625 | 123.0972 | -122.2229 | 0.86975 | -0.0020601 | 0.0053811 | 0.071916 | 0.065657 | 0.0017667 | -0.0029438 | 3.8448e-05 | -0.0012513 | 0.0062955 | 0.070624 | 0.058964 | -0.00073063 | 0.017145 | -0.0042832 | -0.2243 | 0.84686 | -122.4335 | 0.6134 | -121.6507 | -122.2458 | -122.3373 | -0.28381 | 0.83313 | -122.3053 | 0.70038 | -121.9162 | -121.9666 | -121.7331 | -0.21057 | -0.022888 | -0.25635 | 0.5722 | -0.11444 | -0.022889 | 0.096131 | 0.18768 | -0.082398 | -0.036621 | -0.16937 | 0.3067 | 0.48981 | 0.25635 | 0.5722 | 0.33874 | 0.78278 | 123.0469 | 0.3891 | 123.0057 | 123.2803 | 123.1384 | 123.0698 | 123.056 | -123.3032 | -123.175 | 122.8363 | 122.9233 | 121.9986 | 121.9391
739.8125 | 123.1155 | -122.2733 | 0.83313 | -0.0020601 | 0.0053811 | 0.070848 | 0.063521 | -0.0040013 | -0.0025166 | -0.003166 | -0.0073547 | 0.0052273 | 0.071692 | 0.060673 | -0.0056438 | 0.013727 | -1.0598e-05 | -0.19684 | 0.80109 | -122.4472 | 0.63171 | -121.5912 | -122.1771 | -122.287 | -0.21057 | 0.80109 | -122.3328 | 0.66834 | -121.8887 | -121.9299 | -121.7606 | -0.17395 | -0.032044 | -0.20142 | 0.68207 | -0.013733 | 0.09613 | 0.16022 | 0.27008 | -0.05951 | -0.032044 | -0.1648 | 0.38452 | 0.51269 | 0.34332 | 0.5722 | 0.40283 | 0.85602 | 123.0789 | 0.44403 | 123.0011 | 123.2483 | 123.1338 | 123.0743 | 123.0743 | -123.2803 | -123.1659 | 122.905 | 122.9416 | 122.0764 | 122.0627
741.5156 | 123.1018 | -122.3282 | 0.79193 | 0.043716 | 0.0055947 | 0.070848 | 0.065657 | 0.0043301 | -0.0031574 | -0.002525 | 0.0079041 | 0.0045865 | 0.07041 | 0.05811 | -0.0039348 | 0.015009 | -0.0030014 | -0.19226 | 0.80109 | -122.5433 | 0.5722 | -121.6736 | -122.2366 | -122.3557 | -0.20599 | 0.77362 | -122.4014 | 0.60883 | -121.9528 | -121.9757 | -121.7789 | -0.21515 | 0.009155 | -0.21973 | 0.6546 | -0.027466 | 0.091553 | 0.18768 | 0.3067 | -0.073242 | -0.01831 | -0.18311 | 0.37537 | 0.54932 | 0.35248 | 0.62256 | 0.42572 | 0.86975 | 123.1155 | 0.44861 | 123.0103 | 123.3444 | 123.175 | 123.1293 | 123.1018 | -123.3353 | -123.1934 | 122.9004 | 122.937 | 122.1359 | 122.1222
743.2812 | 123.1796 | -122.3465 | 0.6958 | 0.036087 | 0.0053811 | 0.071489 | 0.064803 | 0.0026211 | -0.0012348 | -0.001457 | 0.014008 | 0.0041593 | 0.070624 | 0.065159 | 0.00033757 | 0.015009 | -0.0025742 | -0.1831 | 0.68665 | -122.5479 | 0.60425 | -121.5912 | -122.2458 | -122.3236 | -0.09613 | 0.67749 | -122.3877 | 0.67749 | -121.9208 | -121.9666 | -121.788 | -0.20142 | -0.009155 | -0.091553 | 0.75531 | 0.022889 | 0.10071 | 0.22431 | 0.30212 | -0.041198 | -0.018311 | -0.018311 | 0.42572 | 0.55847 | 0.37994 | 0.59967 | 0.42114 | 0.95673 | 123.1522 | 0.46692 | 123.0652 | 123.2346 | 123.0652 | 123.0331 | 123.024 | -123.2437 | -123.0835 | 122.9507 | 123.024 | 122.1634 | 122.2504
745.0781 | 123.1842 | -122.3145 | 0.71869 | -0.0020601 | 0.0036721 | 0.071703 | 0.066725 | 0.0019803 | -0.0025166 | -0.003166 | 0.0018005 | 0.0050137 | 0.069342 | 0.056187 | 0.0014056 | 0.018 | -0.0025742 | -0.24261 | 0.737 | -122.5159 | 0.54932 | -121.6919 | -122.3282 | -122.4014 | -0.19226 | 0.72327 | -122.3969 | 0.67291 | -121.907 | -121.9437 | -121.7422 | -0.20142 | 0.018311 | -0.16937 | 0.62256 | -0.086975 | -0.013733 | 0.11444 | 0.18768 | -0.082398 | 0.004578 | -0.045776 | 0.40741 | 0.5722 | 0.37079 | 0.6546 | 0.45319 | 0.82397 | 123.0652 | 0.48981 | 123.0698 | 123.2529 | 123.1201 | 123.0515 | 123.0377 | -123.2346 | -123.1155 | 122.8638 | 122.9874 | 122.0718 | 122.1222
746.8281 | 123.1247 | -122.3145 | 0.76446 | -0.0020601 | 0.0051675 | 0.071703 | 0.066512 | 0.0049709 | -0.003371 | 0.0013202 | -0.0012513 | 0.0045865 | 0.070624 | 0.055546 | -0.00051703 | 0.016504 | -0.0044968 | -0.2655 | 0.75531 | -122.525 | 0.53558 | -121.6965 | -122.3328 | -122.3923 | -0.22888 | 0.74616 | -122.3785 | 0.64545 | -121.9482 | -121.994 | -121.7743 | -0.21057 | -0.009155 | -0.22888 | 0.61798 | -0.07782 | -0.018311 | 0.13275 | 0.19226 | -0.064087 | -0.01831 | -0.11902 | 0.36621 | 0.54016 | 0.32043 | 0.60425 | 0.38452 | 0.82855 | 123.0606 | 0.4303 | 123.024 | 123.2803 | 123.1247 | 123.0698 | 123.0606 | -123.2895 | -123.143 | 122.85 | 122.9599 | 122.049 | 122.0856
748.5938 | 123.1384 | -122.2687 | 0.80109 | 0.020828 | 0.0055947 | 0.072771 | 0.066298 | 0.00069854 | -0.0020892 | -0.0023114 | 0.0048523 | 0.0043729 | 0.069983 | 0.06046 | -0.0030804 | 0.016504 | -0.0025742 | -0.15564 | 0.80109 | -122.4976 | 0.64087 | -121.5683 | -122.1817 | -122.2824 | -0.1236 | 0.80109 | -122.3328 | 0.70953 | -121.843 | -121.907 | -121.7194 | -0.22888 | 0 | -0.16022 | 0.70038 | -0.013733 | 0.086975 | 0.21515 | 0.31586 | -0.064087 | 0 | -0.091552 | 0.42572 | 0.54932 | 0.36163 | 0.6134 | 0.42572 | 0.92926 | 123.1384 | 0.48981 | 123.0423 | 123.2986 | 123.1338 | 123.0698 | 123.0698 | -123.2986 | -123.1338 | 122.9095 | 122.9782 | 122.113 | 122.1451
750.2812 | 123.0835 | -122.3419 | 0.75073 | -0.0020601 | 0.0026041 | 0.068498 | 0.064375 | 0.0011257 | -0.0025166 | -0.0010298 | -0.0043029 | 0.0028775 | 0.070837 | 0.055546 | -0.0047894 | 0.013514 | -0.0040696 | -0.23804 | 0.72784 | -122.5662 | 0.51727 | -121.6873 | -122.2916 | -122.3831 | -0.24261 | 0.75989 | -122.4289 | 0.56763 | -121.9666 | -122.0032 | -121.8155 | -0.2243 | -0.022888 | -0.23346 | 0.6546 | -0.041199 | 0.050354 | 0.1831 | 0.27466 | -0.086975 | 0.009156 | -0.1831 | 0.37537 | 0.52643 | 0.33875 | 0.6134 | 0.42572 | 0.87891 | 123.0835 | 0.46234 | 122.9965 | 123.2941 | 123.1888 | 123.0698 | 123.1018 | -123.317 | -123.1796 | 122.8592 | 122.9095 | 122.1039 | 122.0993
752.0312 | 123.0698 | -122.2549 | 0.85602 | -0.0096891 | 0.0036721 | 0.073412 | 0.065443 | -0.0027195 | -0.0044392 | -0.00038875 | -0.0012513 | 0.0037319 | 0.07041 | 0.063878 | 0.00012397 | 0.016504 | -0.0008652 | -0.21057 | 0.84228 | -122.4472 | 0.57678 | -121.6461 | -122.2641 | -122.3373 | -0.27008 | 0.81482 | -122.319 | 0.68665 | -121.9208 | -121.9803 | -121.7468 | -0.19226 | -0.013733 | -0.27924 | 0.60883 | -0.082397 | -0.009155 | 0.10986 | 0.18311 | -0.064087 | -0.041199 | -0.16937 | 0.33417 | 0.50812 | 0.27466 | 0.5722 | 0.33874 | 0.80109 | 123.024 | 0.39825 | 123.0057 | 123.2895 | 123.1338 | 123.0972 | 123.0698 | -123.3032 | -123.175 | 122.8317 | 122.9416 | 122.0444 | 121.9849
753.7812 | 123.1064 | -121.9574 | 1.1078 | 0.020828 | 0.0066629 | 0.071916 | 0.066725 | -0.0012241 | -0.0012348 | -0.002525 | -0.0012513 | 0.0056545 | 0.07041 | 0.054051 | -0.001585 | 0.015223 | -0.003856 | -0.14648 | 1.0941 | -122.2183 | 0.92926 | -121.2845 | -121.9116 | -122.0169 | -0.13733 | 1.0529 | -122.0398 | 0.97961 | -121.5683 | -121.6232 | -121.4218 | -0.26093 | -0.013733 | -0.17853 | 0.67291 | -0.05951 | 0.045776 | 0.20142 | 0.3067 | -0.082398 | -0.054932 | -0.12817 | 0.3891 | 0.53558 | 0.33417 | 0.61798 | 0.41656 | 0.93384 | 123.1476 | 0.4715 | 123.0194 | 123.3124 | 123.0927 | 123.0515 | 123.0103 | -123.3261 | -123.1476 | 122.8867 | 122.937 | 121.8109 | 121.8201
755.4688 | 123.1201 | -122.1863 | 0.88806 | 0.036087 | 0.0073037 | 0.069994 | 0.066298 | 0.0045437 | 0.00068782 | 0.00089285 | 0.0079041 | 0.0050137 | 0.071692 | 0.063237 | -0.001585 | 0.015223 | -0.001506 | -0.15564 | 0.91095 | -122.4335 | 0.69122 | -121.5271 | -122.113 | -122.2092 | -0.16479 | 0.87433 | -122.2549 | 0.75989 | -121.7789 | -121.8338 | -121.6324 | -0.24719 | 0.022888 | -0.19684 | 0.65918 | -0.022888 | 0.073242 | 0.22431 | 0.32043 | -0.068665 | -0.013733 | -0.12817 | 0.40741 | 0.55389 | 0.35248 | 0.62256 | 0.42114 | 0.90637 | 123.1247 | 0.47607 | 123.0148 | 123.3444 | 123.1293 | 123.0972 | 123.0606 | -123.3215 | -123.143 | 122.8775 | 122.9462 | 122.0306 | 122.0215
757.1719 | 123.1201 | -122.1725 | 0.94299 | 0.036087 | 0.0034585 | 0.068498 | 0.065657 | 0.0030483 | -0.0010212 | 0.00067925 | 0.017059 | 0.0062955 | 0.071905 | 0.059178 | -0.0056438 | 0.013727 | -0.0012924 | -0.18768 | 0.9613 | -122.4014 | 0.70496 | -121.4951 | -122.0856 | -122.2 | -0.2243 | 0.92926 | -122.2549 | 0.77362 | -121.7834 | -121.8155 | -121.6141 | -0.22888 | 0.018311 | -0.23804 | 0.67749 | -0.027466 | 0.086975 | 0.20142 | 0.31586 | -0.082398 | -0.013733 | -0.16937 | 0.3891 | 0.55847 | 0.35706 | 0.64087 | 0.43945 | 0.90637 | 123.1064 | 0.4715 | 123.0286 | 123.3627 | 123.1842 | 123.1338 | 123.1018 | -123.3444 | -123.1979 | 122.8775 | 122.9462 | 121.9849 | 121.9482
758.9219 | 123.0743 | -122.168 | 0.93384 | -0.0096891 | 0.0053811 | 0.070634 | 0.064375 | 0.00027134 | -0.001662 | -0.001457 | -0.0012513 | 0.0024503 | 0.071692 | 0.0611 | -0.005003 | 0.015223 | -0.0040696 | -0.19226 | 0.88806 | -122.3373 | 0.70038 | -121.4539 | -122.0673 | -122.1863 | -0.20599 | 0.86975 | -122.1954 | 0.75531 | -121.7834 | -121.8063 | -121.6461 | -0.16937 | -0.045776 | -0.23346 | 0.71411 | -0.01831 | 0.10071 | 0.15106 | 0.27008 | -0.027466 | -0.064087 | -0.17853 | 0.38452 | 0.52185 | 0.36163 | 0.54932 | 0.3891 | 0.88348 | 123.0377 | 0.41199 | 122.9507 | 123.2254 | 123.0652 | 123.056 | 123.0377 | -123.2712 | -123.1293 | 122.8683 | 122.9233 | 121.9757 | 121.962
760.6719 | 123.1522 | -122.1634 | 0.86517 | 0.020828 | 0.0032449 | 0.070207 | 0.064375 | 0.0036893 | -0.0023028 | -0.001457 | 0.0048523 | 0.0015957 | 0.071692 | 0.0658 | -0.00094423 | 0.016932 | -0.0023606 | -0.24719 | 0.8606 | -122.3877 | 0.6958 | -121.4951 | -122.1085 | -122.2 | -0.21515 | 0.84686 | -122.2458 | 0.77362 | -121.7743 | -121.8109 | -121.637 | -0.2243 | -0.004577 | -0.16937 | 0.66833 | -0.036621 | 0.054932 | 0.18768 | 0.27924 | -0.082398 | -0.01831 | -0.091552 | 0.3891 | 0.52643 | 0.35248 | 0.60883 | 0.43488 | 0.89264 | 123.0835 | 0.4715 | 123.0194 | 123.2483 | 123.0927 | 123.024 | 123.0103 | -123.2529 | -123.111 | 122.8592 | 122.937 | 121.9162 | 121.9482
762.3594 | 123.0881 | -122.2412 | 0.83771 | -0.0096891 | 0.0060221 | 0.071489 | 0.066512 | 0.0032619 | -0.0025166 | -0.0018842 | -0.0073547 | 0.0062955 | 0.068701 | 0.057682 | 0.00055117 | 0.014795 | -0.0042832 | -0.23346 | 0.82398 | -122.4564 | 0.58136 | -121.6415 | -122.2641 | -122.3236 | -0.24719 | 0.81482 | -122.3053 | 0.69122 | -121.8887 | -121.9437 | -121.7056 | -0.21515 | -0.013733 | -0.25635 | 0.59967 | -0.082397 | -0.022888 | 0.13275 | 0.19226 | -0.064087 | -0.022889 | -0.14648 | 0.35248 | 0.53558 | 0.29755 | 0.59967 | 0.36163 | 0.81482 | 123.0377 | 0.41656 | 122.9965 | 123.2803 | 123.1201 | 123.0652 | 123.056 | -123.2941 | -123.143 | 122.8226 | 122.9324 | 122.0078 | 121.994
764.1094 | 123.1155 | -122.2778 | 0.81482 | 0.028458 | 0.0036721 | 0.070848 | 0.068221 | 0.00027134 | -0.0037982 | 0.0023882 | 0.020111 | 0.0069363 | 0.072119 | 0.058751 | -0.002226 | 0.015009 | -0.0040696 | -0.19226 | 0.82855 | -122.5021 | 0.58594 | -121.6003 | -122.1909 | -122.287 | -0.20142 | 0.79193 | -122.3511 | 0.67291 | -121.843 | -121.9254 | -121.7148 | -0.2243 | 0.013733 | -0.22888 | 0.67749 | -0.009155 | 0.086975 | 0.21515 | 0.31128 | -0.073242 | -0.022888 | -0.14191 | 0.43488 | 0.56305 | 0.35248 | 0.63629 | 0.42572 | 0.90179 | 123.0881 | 0.50812 | 123.024 | 123.3307 | 123.143 | 123.1064 | 123.0698 | -123.317 | -123.1659 | 122.8638 | 122.9507 | 122.0856 | 122.0764
765.7812 | 123.1293 | -122.2687 | 0.80109 | 0.043716 | 0.0053811 | 0.070207 | 0.065657 | 0.0019803 | -0.001662 | 0.001961 | 0.0018005 | 0.0067227 | 0.069769 | 0.055973 | -0.0017986 | 0.01565 | -0.0025742 | -0.16022 | 0.80566 | -122.5067 | 0.6134 | -121.5775 | -122.1909 | -122.2733 | -0.15106 | 0.78735 | -122.3373 | 0.68665 | -121.8613 | -121.907 | -121.7056 | -0.23804 | 0.004578 | -0.18768 | 0.69122 | -0.004577 | 0.07782 | 0.23346 | 0.31586 | -0.068664 | -0.013732 | -0.11444 | 0.40741 | 0.56305 | 0.36163 | 0.63171 | 0.4303 | 0.92926 | 123.1201 | 0.47607 | 123.024 | 123.3124 | 123.1247 | 123.0743 | 123.056 | -123.3078 | -123.1384 | 122.8821 | 122.9553 | 122.1085 | 122.1176
767.5312 | 123.2117 | -122.1451 | 0.85144 | -0.0020601 | 0.0032449 | 0.069139 | 0.063307 | 5.774e-05 | -0.0044392 | -0.001457 | -0.0012513 | 0.0022367 | 0.069983 | 0.069218 | -0.0030804 | 0.016077 | -1.0598e-05 | -0.21057 | 0.83771 | -122.3419 | 0.7782 | -121.4218 | -122.0352 | -122.1268 | -0.10986 | 0.83313 | -122.2092 | 0.85602 | -121.6873 | -121.7148 | -121.5546 | -0.19684 | -0.013732 | -0.073242 | 0.72327 | 0.018311 | 0.10986 | 0.21515 | 0.3067 | -0.064086 | -0.01831 | 0.004578 | 0.45776 | 0.59052 | 0.4303 | 0.6546 | 0.49438 | 0.92011 | 123.1201 | 0.52185 | 123.0652 | 123.1796 | 123.0423 | 122.9828 | 122.9782 | -123.1934 | -123.0606 | 122.9233 | 123.0011 | 121.9345 | 122.0352
769.2344 | 123.2254 | -122.1817 | 0.8194 | -0.017319 | 0.0028177 | 0.070634 | 0.06288 | 0.0026211 | -0.0023028 | -0.0020978 | -0.010406 | 0.0033047 | 0.07041 | 0.0658 | 0.00033757 | 0.01565 | 0.0023392 | -0.20142 | 0.8194 | -122.4014 | 0.73242 | -121.431 | -122.0398 | -122.1405 | -0.10071 | 0.81482 | -122.2275 | 0.84228 | -121.6965 | -121.7331 | -121.5775 | -0.21973 | 0 | -0.086975 | 0.75073 | 0.041199 | 0.14191 | 0.26093 | 0.36163 | -0.045776 | -0.004578 | 0.022888 | 0.48523 | 0.60425 | 0.44861 | 0.65002 | 0.49439 | 0.97046 | 123.1338 | 0.53101 | 123.0698 | 123.2208 | 123.0423 | 123.0011 | 122.9965 | -123.2208 | -123.0469 | 122.9141 | 123.024 | 121.9803 | 122.081
770.9844 | 123.2208 | -122.0764 | 0.89264 | -0.0096891 | 0.0028177 | 0.070421 | 0.063948 | 0.00048494 | -0.0042254 | -0.00060235 | -0.0073547 | 0.0024503 | 0.071265 | 0.060246 | -0.0011578 | 0.015223 | -0.0017196 | -0.19226 | 0.87433 | -122.319 | 0.83313 | -121.3486 | -121.9711 | -122.0535 | -0.082397 | 0.83771 | -122.1542 | 0.89264 | -121.6278 | -121.669 | -121.4996 | -0.24262 | -0.01831 | -0.059509 | 0.72784 | 0.022888 | 0.10529 | 0.2655 | 0.3479 | -0.07782 | -0.054931 | 0 | 0.44861 | 0.57678 | 0.40741 | 0.6546 | 0.48523 | 0.97046 | 123.1522 | 0.52643 | 123.0469 | 123.1934 | 122.9919 | 122.9507 | 122.9141 | -123.2117 | -123.0469 | 122.9095 | 122.9691 | 121.8842 | 121.994
772.6719 | 123.111 | -122.1725 | 0.89722 | 0.043716 | 0.0034585 | 0.071489 | 0.068434 | 0.0047573 | -0.0023028 | 0.0026018 | 0.010956 | 0.0056545 | 0.070196 | 0.060673 | -0.0030804 | 0.016718 | -0.001506 | -0.14648 | 0.87891 | -122.4106 | 0.68207 | -121.5317 | -122.0993 | -122.1909 | -0.1831 | 0.87433 | -122.2641 | 0.73242 | -121.7834 | -121.8246 | -121.637 | -0.23804 | -0.018311 | -0.21515 | 0.64087 | -0.018311 | 0.073242 | 0.21973 | 0.31128 | -0.091553 | -0.022888 | -0.1648 | 0.3891 | 0.53558 | 0.3479 | 0.62714 | 0.43945 | 0.87891 | 123.0927 | 0.48065 | 122.9965 | 123.2895 | 123.1384 | 123.0515 | 123.0469 | -123.3078 | -123.1613 | 122.8546 | 122.905 | 122.0261 | 121.9894
774.4375 | 123.1888 | -122.0215 | 0.99792 | -0.0020601 | 0.0060221 | 0.070207 | 0.063948 | -0.00058326 | -0.0029438 | 0.00089285 | 0.0018005 | 0.0011685 | 0.070837 | 0.062382 | -0.0030804 | 0.017359 | -0.003856 | -0.16937 | 0.94299 | -122.2458 | 0.91095 | -121.2799 | -121.907 | -122.0215 | -0.10529 | 0.93842 | -122.081 | 0.93842 | -121.5637 | -121.6232 | -121.463 | -0.22431 | -0.054932 | -0.086975 | 0.74158 | 0 | 0.11444 | 0.22431 | 0.33875 | -0.05951 | -0.059509 | -0.059509 | 0.45776 | 0.55847 | 0.39825 | 0.61798 | 0.45776 | 0.96588 | 123.1567 | 0.51727 | 123.0194 | 123.1888 | 123.0194 | 122.9645 | 122.9599 | -123.2437 | -123.0789 | 122.9324 | 122.9599 | 121.8521 | 121.9162
776.1875 | 123.1888 | -122.081 | 0.91553 | -0.0020601 | 0.0030313 | 0.070421 | 0.065871 | -0.00079686 | -0.0042254 | -0.001457 | -0.0012513 | 0.0043729 | 0.069769 | 0.060887 | 0.003542 | 0.016718 | -0.0023606 | -0.20142 | 0.89264 | -122.2961 | 0.81482 | -121.3898 | -121.9894 | -122.113 | -0.14648 | 0.89264 | -122.1451 | 0.9201 | -121.6278 | -121.6919 | -121.4767 | -0.21515 | -0.022888 | -0.10071 | 0.69122 | -0.032043 | 0.091553 | 0.18311 | 0.3067 | -0.064087 | -0.022888 | 0.004578 | 0.45319 | 0.60425 | 0.3891 | 0.66833 | 0.45319 | 0.90637 | 123.111 | 0.51727 | 123.0652 | 123.1888 | 123.0377 | 122.9736 | 122.9736 | -123.2117 | -123.0606 | 122.8958 | 123.0011 | 121.8796 | 121.9345
777.875 | 123.2071 | -122.1909 | 0.81024 | -0.0020601 | 0.0013223 | 0.070848 | 0.064375 | 0.0015529 | -0.003371 | -0.0020978 | -0.0012513 | 0.0018093 | 0.069769 | 0.063664 | 0.00012397 | 0.016504 | -0.0025742 | -0.23804 | 0.81024 | -122.4014 | 0.70496 | -121.4722 | -122.081 | -122.1634 | -0.1236 | 0.76904 | -122.2321 | 0.80109 | -121.7285 | -121.7743 | -121.5958 | -0.21057 | 0 | -0.10529 | 0.71869 | 0.027466 | 0.10986 | 0.23804 | 0.32043 | -0.041199 | -0.041199 | -0.009156 | 0.46234 | 0.59509 | 0.41656 | 0.63629 | 0.45776 | 0.92926 | 123.1064 | 0.50354 | 123.0331 | 123.2117 | 123.0011 | 123.0011 | 122.9599 | -123.2117 | -123.0423 | 122.8958 | 122.9919 | 121.9528 | 122.0673
779.625 | 123.0698 | -122.1542 | 0.91553 | -0.0020601 | 0.0045267 | 0.068498 | 0.063948 | 0.0034755 | -0.0029438 | -0.0035932 | -0.0012513 | 0.0069363 | 0.073828 | 0.050847 | -0.0060712 | 0.015009 | -0.0002244 | -0.24261 | 0.88806 | -122.3694 | 0.66376 | -121.5271 | -122.1176 | -122.2183 | -0.21515 | 0.92468 | -122.2504 | 0.72784 | -121.7926 | -121.8338 | -121.6232 | -0.21515 | -0.027465 | -0.25177 | 0.62714 | -0.064087 | 0.036621 | 0.15106 | 0.25177 | -0.09613 | 0.009156 | -0.18768 | 0.36163 | 0.53101 | 0.32044 | 0.62714 | 0.41657 | 0.84228 | 123.0331 | 0.45776 | 122.9782 | 123.2574 | 123.175 | 123.0423 | 123.0789 | -123.2849 | -123.1659 | 122.818 | 122.8821 | 121.9116 | 121.9391
781.3906 | 123.0606 | -122.2641 | 0.79193 | 0.0055694 | 0.0051675 | 0.072343 | 0.065871 | 0.0013393 | -0.0035846 | -0.00060235 | -0.0043029 | 0.0045865 | 0.068915 | 0.054051 | -0.0017986 | 0.014582 | -0.0023606 | -0.21973 | 0.78735 | -122.4609 | 0.54932 | -121.6782 | -122.2778 | -122.3648 | -0.26093 | 0.7782 | -122.3236 | 0.63629 | -121.9299 | -121.9849 | -121.7331 | -0.19684 | -0.004577 | -0.24262 | 0.58594 | -0.10071 | -0.013733 | 0.09613 | 0.1831 | -0.059509 | -0.013733 | -0.15564 | 0.33417 | 0.53101 | 0.27924 | 0.59051 | 0.33874 | 0.78278 | 123.0103 | 0.39368 | 122.9599 | 123.2483 | 123.1018 | 123.0515 | 123.0423 | -123.2529 | -123.1155 | 122.8134 | 122.9004 | 122.0444 | 122.0032
783.0781 | 123.1384 | -122.2092 | 0.78278 | 0.0055694 | 0.0026041 | 0.069353 | 0.06523 | 0.0011257 | -0.0035846 | -0.0012434 | 0.0048523 | 0.0039457 | 0.070837 | 0.061314 | 0.00033757 | 0.017359 | -0.0051376 | -0.24719 | 0.7782 | -122.438 | 0.63171 | -121.55 | -122.1542 | -122.2504 | -0.21515 | 0.75989 | -122.3053 | 0.71411 | -121.8292 | -121.8567 | -121.6736 | -0.22888 | -0.004578 | -0.15106 | 0.65918 | -0.041199 | 0.054931 | 0.18768 | 0.28381 | -0.096131 | -0.022888 | -0.068665 | 0.37994 | 0.53558 | 0.35248 | 0.63171 | 0.44861 | 0.88806 | 123.0698 | 0.47607 | 123.0194 | 123.2162 | 123.0652 | 122.9874 | 122.9691 | -123.2208 | -123.0881 | 122.8409 | 122.9233 | 121.962 | 121.994
784.8281 | 123.0652 | -122.3511 | 0.73242 | 0.043716 | 0.0051675 | 0.06978 | 0.068221 | 0.0032619 | -0.003371 | -0.0020978 | 0.010956 | 0.0067227 | 0.071692 | 0.05811 | -0.0045758 | 0.014795 | -0.002147 | -0.20142 | 0.76446 | -122.5937 | 0.53101 | -121.6736 | -122.2595 | -122.3557 | -0.21515 | 0.72784 | -122.3785 | 0.58594 | -121.9528 | -121.9894 | -121.7834 | -0.24262 | 0.032043 | -0.20142 | 0.67749 | -0.004578 | 0.091553 | 0.23804 | 0.33417 | -0.027466 | -0.004578 | -0.14648 | 0.39825 | 0.56763 | 0.36163 | 0.59509 | 0.3891 | 0.9201 | 123.1247 | 0.42572 | 122.9645 | 123.3582 | 123.1064 | 123.1155 | 123.0789 | -123.3261 | -123.111 | 122.8821 | 122.937 | 122.1497 | 122.1359
786.5156 | 123.056 | -122.3831 | 0.68665 | -0.0020601 | 0.0064493 | 0.06978 | 0.064589 | -0.0040013 | -0.0048664 | -0.0016706 | -0.0043029 | 0.0033047 | 0.071051 | 0.068364 | -0.0028668 | 0.013727 | -1.0598e-05 | -0.21973 | 0.63629 | -122.5983 | 0.44403 | -121.7285 | -122.3282 | -122.4289 | -0.23346 | 0.6546 | -122.4335 | 0.49896 | -122.0169 | -122.049 | -121.8796 | -0.21515 | -0.050354 | -0.24261 | 0.6546 | -0.045776 | 0.054932 | 0.16937 | 0.27008 | -0.050354 | -0.032044 | -0.18768 | 0.36621 | 0.50354 | 0.33417 | 0.55389 | 0.38452 | 0.86975 | 123.0423 | 0.41656 | 122.9324 | 123.2346 | 123.0881 | 123.0194 | 123.0377 | -123.2849 | -123.1201 | 122.8271 | 122.8821 | 122.1634 | 122.1497
788.2656 | 123.0789 | -122.3282 | 0.70953 | 0.0055694 | 0.0023905 | 0.07213 | 0.066725 | 0.0068935 | -0.0048664 | -0.00038875 | -0.0043029 | 0.0043729 | 0.071692 | 0.059178 | -0.001585 | 0.01565 | -0.0027878 | -0.23346 | 0.6958 | -122.5296 | 0.46692 | -121.756 | -122.3557 | -122.4289 | -0.25635 | 0.70038 | -122.4014 | 0.55389 | -122.0169 | -122.0673 | -121.8155 | -0.20142 | -0.013733 | -0.24262 | 0.5722 | -0.10071 | -0.027466 | 0.10071 | 0.17395 | -0.073242 | -0.009156 | -0.15564 | 0.31128 | 0.5127 | 0.26093 | 0.58594 | 0.33417 | 0.77362 | 122.9965 | 0.38452 | 122.9553 | 123.2254 | 123.1018 | 123.024 | 123.0286 | -123.2391 | -123.111 | 122.7951 | 122.8821 | 122.0947 | 122.0718
790.0312 | 123.0469 | -122.2961 | 0.7782 | -0.0096891 | 0.0047403 | 0.06978 | 0.064803 | 0.0041165 | -0.003371 | -0.00017515 | 0.014008 | 0.0058683 | 0.068915 | 0.059391 | -0.0039348 | 0.014795 | -0.0008652 | -0.24719 | 0.75989 | -122.4747 | 0.56305 | -121.6415 | -122.2183 | -122.3053 | -0.20599 | 0.78278 | -122.3923 | 0.58594 | -121.9345 | -121.9711 | -121.7606 | -0.17853 | -0.01831 | -0.21515 | 0.6546 | -0.009155 | 0.07782 | 0.16937 | 0.25635 | -0.09613 | 0.004578 | -0.19226 | 0.36163 | 0.53558 | 0.32501 | 0.63171 | 0.42114 | 0.83313 | 123.0377 | 0.45776 | 122.9782 | 123.2346 | 123.175 | 123.056 | 123.0789 | -123.2529 | -123.1705 | 122.8592 | 122.8821 | 122.049 | 122.0901
791.7031 | 123.0515 | -122.3053 | 0.74616 | -0.0020601 | 0.0053811 | 0.07213 | 0.06523 | 0.0049709 | -0.003371 | 0.0017474 | 0.0018005 | 0.0062955 | 0.072333 | 0.064732 | -8.9634e-05 | 0.016718 | -0.0027878 | -0.16937 | 0.6958 | -122.5296 | 0.53558 | -121.6736 | -122.287 | -122.3831 | -0.19684 | 0.71869 | -122.3877 | 0.59052 | -121.9666 | -122.0261 | -121.788 | -0.2243 | -0.050354 | -0.21057 | 0.63171 | -0.07782 | 0.018311 | 0.14648 | 0.24262 | -0.082397 | -0.027466 | -0.15564 | 0.33874 | 0.51727 | 0.27924 | 0.59967 | 0.36163 | 0.85602 | 123.0652 | 0.42114 | 122.9782 | 123.2254 | 123.1064 | 123.0011 | 123.024 | -123.2758 | -123.1338 | 122.8409 | 122.8958 | 122.1359 | 122.1085
793.4531 | 123.0423 | -122.3923 | 0.67291 | -0.0020601 | 0.0026041 | 0.06978 | 0.06523 | 0.00091214 | -0.0029438 | -0.0010298 | -0.0012513 | 0.0030911 | 0.070196 | 0.0658 | -0.0017986 | 0.015436 | -0.0017196 | -0.21973 | 0.64087 | -122.612 | 0.44861 | -121.7285 | -122.3282 | -122.4197 | -0.23804 | 0.64087 | -122.4838 | 0.49896 | -122.0306 | -122.0581 | -121.8704 | -0.21973 | -0.032044 | -0.2243 | 0.66376 | -0.027466 | 0.064087 | 0.19226 | 0.28381 | -0.091553 | -0.032044 | -0.17395 | 0.36163 | 0.52185 | 0.33417 | 0.6134 | 0.42572 | 0.88348 | 123.0606 | 0.45319 | 122.9828 | 123.2529 | 123.1247 | 123.0331 | 123.0331 | -123.2849 | -123.1567 | 122.8409 | 122.8912 | 122.1725 | 122.1542
795.2188 | 123.0515 | -122.3831 | 0.67291 | 0.0055694 | 0.0064493 | 0.069566 | 0.065657 | 0.0015529 | -0.00038018 | -0.0016706 | -0.0012513 | 0.0030911 | 0.070624 | 0.060887 | -0.0013714 | 0.016077 | -0.0025742 | -0.2243 | 0.6546 | -122.5983 | 0.37994 | -121.8201 | -122.4106 | -122.5067 | -0.27924 | 0.62256 | -122.4655 | 0.48065 | -122.0673 | -122.1313 | -121.8842 | -0.21515 | -0.018311 | -0.29297 | 0.56305 | -0.1236 | -0.027465 | 0.091553 | 0.18768 | -0.082397 | -0.050354 | -0.19226 | 0.31586 | 0.49896 | 0.25177 | 0.58136 | 0.33417 | 0.7782 | 122.9782 | 0.39825 | 122.9462 | 123.2529 | 123.0881 | 123.0377 | 123.0057 | -123.2712 | -123.1384 | 122.7631 | 122.8638 | 122.1588 | 122.1039
796.9531 | 123.0377 | -122.3969 | 0.65918 | -0.017319 | 0.0047403 | 0.070207 | 0.067793 | 0.0028347 | -0.0040118 | -0.0027386 | -0.0043029 | 0.0056545 | 0.072333 | 0.059178 | 0.00033757 | 0.017145 | -0.0019332 | -0.19226 | 0.63629 | -122.6166 | 0.41199 | -121.7697 | -122.3923 | -122.4884 | -0.23804 | 0.63171 | -122.4518 | 0.48981 | -122.0581 | -122.1039 | -121.875 | -0.21973 | -0.022888 | -0.24719 | 0.62714 | -0.091552 | 0.004578 | 0.12817 | 0.2243 | -0.054931 | -0.027466 | -0.16937 | 0.33875 | 0.52185 | 0.29297 | 0.57678 | 0.3479 | 0.84686 | 123.0286 | 0.39368 | 122.9416 | 123.2529 | 123.0835 | 123.0331 | 123.0286 | -123.2758 | -123.111 | 122.8088 | 122.8867 | 122.2046 | 122.1588
798.6406 | 123.0515 | -122.4335 | 0.64545 | 0.051346 | 0.0032449 | 0.070848 | 0.06523 | 0.0041165 | -0.0040118 | -0.004234 | 0.014008 | 0.0058683 | 0.070196 | 0.058323 | -0.0045758 | 0.015223 | -0.0012924 | -0.20599 | 0.6546 | -122.6624 | 0.39825 | -121.7651 | -122.3511 | -122.4701 | -0.21057 | 0.6134 | -122.5067 | 0.47607 | -122.049 | -122.081 | -121.8796 | -0.22888 | 0.009155 | -0.24719 | 0.66833 | -0.036621 | 0.082398 | 0.19226 | 0.31128 | -0.073242 | -0.032044 | -0.16937 | 0.38452 | 0.55389 | 0.35248 | 0.62714 | 0.42572 | 0.89722 | 123.0606 | 0.45776 | 122.9828 | 123.317 | 123.1201 | 123.0881 | 123.0469 | -123.3078 | -123.1522 | 122.8317 | 122.9095 | 122.2275 | 122.2229
800.3906 | 123.0469 | -122.4106 | 0.67291 | -0.0020601 | 0.0038857 | 0.068925 | 0.065016 | -0.00036966 | -0.00059378 | 0.00025205 | 0.014008 | 0.0050137 | 0.072546 | 0.058964 | -0.0020122 | 0.013514 | -0.0019332 | -0.20599 | 0.66376 | -122.6349 | 0.42114 | -121.7422 | -122.3282 | -122.4197 | -0.20142 | 0.65918 | -122.5067 | 0.48065 | -122.0352 | -122.0718 | -121.8613 | -0.22431 | -0.009156 | -0.25177 | 0.66833 | -0.009156 | 0.082397 | 0.21515 | 0.3067 | -0.096131 | -0.013733 | -0.19226 | 0.37537 | 0.54932 | 0.33875 | 0.64545 | 0.43488 | 0.89264 | 123.056 | 0.4715 | 122.9874 | 123.2986 | 123.1659 | 123.0743 | 123.0698 | -123.3078 | -123.1796 | 122.8317 | 122.8912 | 122.2046 | 122.2092
802.1406 | 123.1338 | -122.3923 | 0.6134 | 0.036087 | 0.0034585 | 0.071275 | 0.066512 | 0.00048494 | -0.0014484 | -0.001457 | 0.010956 | 0.0028775 | 0.068701 | 0.06345 | 0.00033757 | 0.016077 | -1.0598e-05 | -0.23346 | 0.6134 | -122.5983 | 0.49439 | -121.669 | -122.3007 | -122.3831 | -0.17853 | 0.59509 | -122.4152 | 0.54932 | -121.9574 | -122.0306 | -121.8109 | -0.20599 | 0 | -0.11902 | 0.72327 | 0.009155 | 0.091553 | 0.21515 | 0.29755 | -0.022888 | -0.01831 | -0.064087 | 0.43488 | 0.58136 | 0.36163 | 0.60425 | 0.38452 | 0.92926 | 123.0927 | 0.45776 | 122.9645 | 123.2117 | 123.0103 | 123.0057 | 122.9874 | -123.2117 | -123.0286 | 122.8867 | 122.9416 | 122.1588 | 122.2137
803.8906 | 123.0469 | -122.3923 | 0.6546 | 0.0055694 | 0.0047403 | 0.06978 | 0.065443 | -0.00036966 | -0.0027302 | 0.00025205 | -0.0012513 | 0.0052273 | 0.070837 | 0.060887 | -8.9634e-05 | 0.013727 | 0.0010574 | -0.25177 | 0.64545 | -122.612 | 0.40283 | -121.788 | -122.3831 | -122.4701 | -0.25635 | 0.62714 | -122.4426 | 0.49439 | -122.0581 | -122.1039 | -121.8521 | -0.21973 | -0.009155 | -0.25177 | 0.60425 | -0.07782 | 0.009155 | 0.14191 | 0.22888 | -0.050354 | -0.027466 | -0.16022 | 0.33417 | 0.54016 | 0.28839 | 0.59051 | 0.33875 | 0.82397 | 123.0148 | 0.38452 | 122.937 | 123.2574 | 123.0698 | 123.0377 | 123.0194 | -123.2666 | -123.0972 | 122.7951 | 122.8867 | 122.1405 | 122.1359
805.5938 | 123.175 | -122.3282 | 0.64087 | -0.017319 | 0.0019631 | 0.070207 | 0.06288 | 0.00048494 | -0.0020892 | 0.0013202 | -0.0043029 | 0.00074131 | 0.071478 | 0.065373 | -0.00073063 | 0.016291 | -1.0598e-05 | -0.24719 | 0.63171 | -122.5388 | 0.53101 | -121.6232 | -122.2366 | -122.3328 | -0.14191 | 0.60883 | -122.3969 | 0.63629 | -121.8842 | -121.9116 | -121.7422 | -0.21057 | -0.009155 | -0.10986 | 0.70496 | -0.004578 | 0.091553 | 0.20599 | 0.30212 | -0.068665 | -0.032043 | -0.004577 | 0.44403 | 0.58594 | 0.41657 | 0.6546 | 0.48523 | 0.91553 | 123.0698 | 0.5127 | 123.0331 | 123.1705 | 123.0057 | 122.9599 | 122.937 | -123.1796 | -123.0377 | 122.8592 | 122.9645 | 122.081 | 122.1863
807.3438 | 123.1384 | -122.3877 | 0.62714 | 0.036087 | 0.0049539 | 0.071489 | 0.066298 | 0.0015529 | -0.0029438 | -0.0016706 | 0.0079041 | 0.0026639 | 0.071905 | 0.070286 | -0.0028668 | 0.014368 | -0.0017196 | -0.22888 | 0.6134 | -122.5708 | 0.50812 | -121.6507 | -122.287 | -122.3969 | -0.1831 | 0.60425 | -122.4472 | 0.5722 | -121.9757 | -122.0032 | -121.8063 | -0.18311 | -0.013733 | -0.11902 | 0.737 | -0.009156 | 0.10071 | 0.17395 | 0.28381 | -0.05951 | -0.022888 | -0.054931 | 0.41199 | 0.58136 | 0.38452 | 0.64087 | 0.44403 | 0.92011 | 123.0789 | 0.4715 | 123.0194 | 123.1842 | 123.0515 | 123.0011 | 122.9919 | -123.1979 | -123.0743 | 122.8958 | 122.9599 | 122.1588 | 122.2046
809.0469 | 123.1888 | -122.3785 | 0.59509 | -0.0096891 | 0.0045267 | 0.071489 | 0.065443 | 0.0011257 | -0.0042254 | -0.003166 | -0.0073547 | 0.0033047 | 0.068915 | 0.061955 | -0.00030343 | 0.016504 | -0.0027878 | -0.23804 | 0.58594 | -122.6074 | 0.50812 | -121.637 | -122.2412 | -122.3465 | -0.10986 | 0.5722 | -122.4243 | 0.59509 | -121.8979 | -121.9345 | -121.7651 | -0.22888 | -0.009156 | -0.086975 | 0.74158 | 0.032043 | 0.13733 | 0.26093 | 0.36621 | -0.045776 | -0.022888 | 0 | 0.48065 | 0.6134 | 0.44403 | 0.65918 | 0.48981 | 0.97046 | 123.1155 | 0.52643 | 123.0194 | 123.1934 | 122.9965 | 122.9645 | 122.9507 | -123.2025 | -123.0194 | 122.8867 | 122.9736 | 122.1405 | 122.2687
810.7812 | 123.1613 | -122.4014 | 0.5722 | 0.066604 | 0.0060221 | 0.071275 | 0.069716 | 0.0068935 | -0.00059378 | 3.8448e-05 | 0.017059 | 0.0060819 | 0.07276 | 0.066868 | 0.0020466 | 0.017145 | -0.0023606 | -0.15106 | 0.5722 | -122.6532 | 0.52643 | -121.6324 | -122.2778 | -122.3831 | -0.10071 | 0.57678 | -122.4747 | 0.56305 | -121.9574 | -122.0078 | -121.8018 | -0.25177 | 0 | -0.045777 | 0.76904 | 0.01831 | 0.1236 | 0.27008 | 0.37537 | -0.073242 | 0.004577 | -0.009156 | 0.44403 | 0.59967 | 0.39368 | 0.67291 | 0.46692 | 1.0208 | 123.1796 | 0.51727 | 123.0377 | 123.2254 | 123.0515 | 122.9736 | 122.9782 | -123.2254 | -123.0469 | 122.9279 | 122.9645 | 122.2504 | 122.3007
812.5312 | 123.0698 | -122.406 | 0.63171 | -0.0096891 | 0.0030313 | 0.070421 | 0.066084 | 0.0024075 | -0.0023028 | -0.00060235 | -0.0043029 | 0.0045865 | 0.070196 | 0.056828 | -0.0013714 | 0.017573 | -0.0025742 | -0.23804 | 0.59509 | -122.6212 | 0.37079 | -121.8246 | -122.4243 | -122.493 | -0.24719 | 0.59509 | -122.4564 | 0.48523 | -122.0764 | -122.1085 | -121.8704 | -0.21515 | -0.036621 | -0.26093 | 0.58136 | -0.086975 | -0.01831 | 0.12817 | 0.19684 | -0.050354 | -0.036621 | -0.14648 | 0.32959 | 0.53558 | 0.29755 | 0.58594 | 0.3479 | 0.79651 | 122.9919 | 0.37994 | 122.9416 | 123.2162 | 123.0515 | 123.0011 | 123.0011 | -123.2529 | -123.0881 | 122.7768 | 122.8912 | 122.168 | 122.1588
814.2812 | 123.1522 | -122.3785 | 0.59967 | -0.0096891 | 0.0038857 | 0.068498 | 0.061812 | 0.0015529 | -0.003371 | 0.00089285 | -0.0043029 | 0.0024503 | 0.069769 | 0.056828 | -0.0011578 | 0.015864 | -0.0017196 | -0.1831 | 0.56763 | -122.6074 | 0.52185 | -121.6324 | -122.2458 | -122.3648 | -0.11444 | 0.58594 | -122.438 | 0.5722 | -121.9162 | -121.962 | -121.788 | -0.22888 | -0.032043 | -0.077819 | 0.74616 | 0.013733 | 0.13275 | 0.24262 | 0.36163 | -0.059509 | -0.013733 | -0.027465 | 0.46234 | 0.59051 | 0.41657 | 0.65002 | 0.47607 | 0.97504 | 123.1293 | 0.52185 | 123.0103 | 123.175 | 123.024 | 122.9462 | 122.9645 | -123.2071 | -123.0377 | 122.9004 | 122.9507 | 122.1954 | 122.2641
816.0312 | 123.0789 | -122.4335 | 0.60425 | 0.020828 | 0.0051675 | 0.069994 | 0.067366 | 0.0030483 | -0.0057208 | 0.00025205 | 0.010956 | 0.0062955 | 0.071905 | 0.058537 | -0.003294 | 0.015223 | -0.002147 | -0.16937 | 0.59967 | -122.6852 | 0.39825 | -121.788 | -122.3511 | -122.4701 | -0.19226 | 0.62256 | -122.5204 | 0.45776 | -122.0352 | -122.0856 | -121.843 | -0.25177 | -0.004578 | -0.20599 | 0.64545 | -0.036621 | 0.082398 | 0.21515 | 0.33417 | -0.086975 | 0.018311 | -0.14648 | 0.39825 | 0.59051 | 0.3479 | 0.67749 | 0.43488 | 0.89722 | 123.0835 | 0.48523 | 122.9782 | 123.2849 | 123.143 | 123.0331 | 123.056 | -123.2895 | -123.1247 | 122.8317 | 122.8912 | 122.2641 | 122.2412
817.7188 | 123.1155 | -122.406 | 0.59052 | 0.028458 | 0.0066629 | 0.06978 | 0.066084 | 0.0049709 | -0.0012348 | 3.8448e-05 | 0.0048523 | 0.0035183 | 0.07276 | 0.065373 | 0.00033757 | 0.017573 | -0.0030014 | -0.21515 | 0.59052 | -122.5983 | 0.49439 | -121.6553 | -122.3099 | -122.3969 | -0.13733 | 0.57678 | -122.4701 | 0.53558 | -121.9666 | -122.0032 | -121.8155 | -0.19226 | 0 | -0.09613 | 0.75073 | 0.009155 | 0.096131 | 0.20142 | 0.28839 | -0.064087 | -0.013733 | -0.054932 | 0.43945 | 0.59052 | 0.40283 | 0.6546 | 0.46692 | 0.94299 | 123.0927 | 0.50354 | 123.0057 | 123.1888 | 123.0469 | 122.9965 | 122.9828 | -123.1888 | -123.0606 | 122.9004 | 122.9416 | 122.1909 | 122.2687
819.4688 | 122.8867 | -121.6644 | 1.2314 | -0.0020601 | 0.0047403 | 0.068712 | 0.067366 | 0.00027134 | -0.0025166 | -0.0010298 | 0.014008 | 0.0026639 | 0.072119 | 0.060673 | -0.0028668 | 0.01565 | -0.0044968 | -0.23346 | 1.2268 | -121.907 | 1.0162 | -121.0098 | -121.5683 | -121.6873 | -0.21057 | 1.2131 | -121.7377 | 1.0574 | -121.2799 | -121.3303 | -121.1105 | -0.24261 | -0.004577 | -0.21515 | 0.6546 | -0.022888 | 0.096131 | 0.21973 | 0.33875 | -0.073242 | -0.01831 | -0.17395 | 0.38452 | 0.55389 | 0.33417 | 0.62714 | 0.40741 | 0.89722 | 122.9233 | 0.45776 | 122.7951 | 123.1338 | 122.9507 | 122.8912 | 122.8775 | -123.1384 | -122.9691 | 122.6807 | 122.7219 | 121.431 | 121.4539
821.2188 | 122.7036 | -121.4172 | 1.2589 | -0.0020601 | 0.0038857 | 0.069353 | 0.064803 | 0.0028347 | -0.00038018 | -0.0033796 | -0.0012513 | 0.0048001 | 0.069983 | 0.055119 | 0.00012397 | 0.016504 | -0.0027878 | -0.15564 | 1.2314 | -121.6095 | 1.0574 | -120.7397 | -121.3715 | -121.4722 | -0.16022 | 1.2039 | -121.4905 | 1.1078 | -121.0648 | -121.0922 | -120.8817 | -0.19226 | -0.027466 | -0.20142 | 0.67749 | -0.054932 | 0.045776 | 0.13733 | 0.23804 | -0.073243 | -0.054932 | -0.15106 | 0.35248 | 0.53558 | 0.32501 | 0.60883 | 0.39825 | 0.86975 | 122.6669 | 0.42572 | 122.5983 | 122.8409 | 122.6944 | 122.6486 | 122.6212 | -122.8683 | -122.7493 | 122.4747 | 122.525 | 121.2616 | 121.257
822.9688 | 122.5983 | -121.3623 | 1.2543 | -0.0020601 | 0.0066629 | 0.070634 | 0.064162 | 0.0013393 | -0.0035846 | -0.002525 | -0.0012513 | 0.0048001 | 0.071905 | 0.060246 | -0.00030343 | 0.015864 | -0.0006516 | -0.20142 | 1.2451 | -121.5637 | 1.0391 | -120.7123 | -121.3165 | -121.4172 | -0.21973 | 1.2131 | -121.3898 | 1.0757 | -121.0052 | -121.0648 | -120.813 | -0.20142 | -0.009155 | -0.21515 | 0.65002 | -0.054931 | 0.045777 | 0.14648 | 0.24719 | -0.027466 | -0.041198 | -0.17853 | 0.35706 | 0.54932 | 0.29755 | 0.57678 | 0.32501 | 0.85144 | 122.6028 | 0.38452 | 122.4655 | 122.8088 | 122.6028 | 122.6074 | 122.5754 | -122.818 | -122.644 | 122.4014 | 122.4381 | 121.1609 | 121.1426
824.7344 | 122.5616 | -121.3074 | 1.268 | 0.013199 | 0.0036721 | 0.070634 | 0.062453 | -0.0018649 | -0.0046528 | -0.0023114 | -0.0012513 | 0.0033047 | 0.069128 | 0.064946 | -0.003294 | 0.016718 | -0.0034286 | -0.20599 | 1.2314 | -121.5088 | 1.0666 | -120.6024 | -121.2021 | -121.312 | -0.21057 | 1.2543 | -121.3257 | 1.1032 | -120.9045 | -120.9366 | -120.7581 | -0.20142 | -0.036621 | -0.20142 | 0.70496 | -0.004578 | 0.10529 | 0.19684 | 0.3067 | -0.018311 | -0.013733 | -0.1648 | 0.40283 | 0.54932 | 0.37079 | 0.56763 | 0.3891 | 0.90637 | 122.5754 | 0.42114 | 122.4289 | 122.7402 | 122.58 | 122.5388 | 122.5616 | -122.7768 | -122.5937 | 122.374 | 122.4106 | 121.1014 | 121.0968
826.4219 | 122.5296 | -121.1975 | 1.3138 | 0.020828 | 0.0051675 | 0.071703 | 0.065016 | 0.0075345 | -0.0025166 | 0.00025205 | 0.020111 | 0.0058683 | 0.071905 | 0.051701 | -0.0045758 | 0.014582 | 0.0016982 | -0.21057 | 1.3321 | -121.4539 | 1.0849 | -120.5521 | -121.1563 | -121.2387 | -0.21973 | 1.3275 | -121.2891 | 1.1444 | -120.8359 | -120.8908 | -120.6528 | -0.25635 | 0.01831 | -0.22888 | 0.64545 | -0.041198 | 0.041199 | 0.21515 | 0.29755 | -0.091552 | 0.013733 | -0.16937 | 0.36163 | 0.54474 | 0.3067 | 0.63629 | 0.39825 | 0.90179 | 122.5388 | 0.45319 | 122.4335 | 122.7859 | 122.6166 | 122.5296 | 122.525 | -122.7676 | -122.6028 | 122.2824 | 122.3419 | 120.9869 | 120.9778
828.1719 | 122.5983 | -121.1929 | 1.2131 | -0.0020601 | 0.0043131 | 0.072343 | 0.065871 | 0.00091214 | -0.0014484 | -0.0016706 | -0.0043029 | 0.0058683 | 0.070837 | 0.067296 | 0.0022602 | 0.015864 | -0.0030014 | -0.23346 | 1.2314 | -121.431 | 1.062 | -120.5566 | -121.17 | -121.2708 | -0.16937 | 1.181 | -121.2708 | 1.1948 | -120.7993 | -120.845 | -120.6116 | -0.23804 | 0.01831 | -0.15106 | 0.63629 | -0.07782 | 0.022888 | 0.16022 | 0.26093 | -0.07782 | -0.032044 | -0.018311 | 0.39368 | 0.58136 | 0.3479 | 0.65918 | 0.42572 | 0.87433 | 122.493 | 0.4715 | 122.4655 | 122.6624 | 122.4518 | 122.4243 | 122.374 | -122.644 | -122.4838 | 122.2549 | 122.3877 | 120.9595 | 121.0236
829.9219 | 122.5113 | -121.225 | 1.2314 | 0.028458 | 0.0068765 | 0.071062 | 0.065016 | 0.0021939 | -0.0027302 | -0.00081595 | 0.0048523 | 0.0056545 | 0.070837 | 0.064091 | -0.00030343 | 0.015009 | -0.0025742 | -0.16022 | 1.2222 | -121.4584 | 1.062 | -120.5521 | -121.1243 | -121.2204 | -0.14191 | 1.2039 | -121.2845 | 1.1261 | -120.8267 | -120.8542 | -120.639 | -0.23346 | -0.009155 | -0.16937 | 0.67291 | 0.004578 | 0.10071 | 0.23804 | 0.33417 | -0.059509 | -0.027466 | -0.10529 | 0.39825 | 0.58594 | 0.37079 | 0.64545 | 0.4303 | 0.90637 | 122.5204 | 0.45776 | 122.4106 | 122.6807 | 122.4884 | 122.4472 | 122.4289 | -122.6898 | -122.5159 | 122.287 | 122.3511 | 121.0648 | 121.0831
831.6094 | 122.4426 | -121.1929 | 1.2405 | -0.0020601 | 0.0038857 | 0.071275 | 0.065016 | 0.0019803 | -0.0023028 | -0.001457 | -0.0012513 | 0.0043729 | 0.068274 | 0.060246 | 0.00097837 | 0.014582 | -0.0030014 | -0.22888 | 1.2314 | -121.4127 | 1.0025 | -120.607 | -121.1975 | -121.2845 | -0.27008 | 1.2268 | -121.2433 | 1.0757 | -120.8542 | -120.9091 | -120.6436 | -0.21973 | -0.009156 | -0.23804 | 0.58594 | -0.091553 | -0.004578 | 0.12817 | 0.21515 | -0.050354 | -0.013733 | -0.1648 | 0.33875 | 0.54932 | 0.28381 | 0.59967 | 0.33417 | 0.80566 | 122.4152 | 0.3891 | 122.319 | 122.644 | 122.4701 | 122.4243 | 122.4197 | -122.6532 | -122.4838 | 122.1954 | 122.2687 | 120.9641 | 120.9229
833.3594 | 122.4014 | -121.17 | 1.2405 | -0.0020601 | 0.0047403 | 0.070634 | 0.06758 | 0.0028347 | -0.0031574 | 0.00046565 | -0.0012513 | 0.0041593 | 0.071051 | 0.055119 | -0.00094423 | 0.01565 | -0.0040696 | -0.18768 | 1.2039 | -121.3577 | 1.0483 | -120.52 | -121.138 | -121.2433 | -0.20142 | 1.1993 | -121.2021 | 1.0941 | -120.8221 | -120.8817 | -120.6299 | -0.18768 | -0.036622 | -0.19226 | 0.65002 | -0.073242 | 0.032044 | 0.11444 | 0.21973 | -0.032043 | -0.041199 | -0.14648 | 0.3479 | 0.54016 | 0.28839 | 0.5722 | 0.32043 | 0.83771 | 122.406 | 0.37994 | 122.2961 | 122.5616 | 122.4014 | 122.374 | 122.3694 | -122.5983 | -122.4426 | 122.2183 | 122.2641 | 120.9824 | 120.9686
835.125 | 122.438 | -121.2479 | 1.0941 | 0.013199 | 0.0038857 | 0.071703 | 0.065871 | 0.0058255 | -0.0029438 | -0.00038875 | 0.0048523 | 0.0052273 | 0.070196 | 0.059605 | -8.9634e-05 | 0.01565 | -0.001506 | -0.15106 | 1.0941 | -121.463 | 0.96588 | -120.5612 | -121.17 | -121.2616 | -0.12817 | 1.0941 | -121.3028 | 1.0208 | -120.8496 | -120.9 | -120.6711 | -0.21515 | 0 | -0.12817 | 0.68665 | -0.013733 | 0.07782 | 0.20142 | 0.29297 | -0.054931 | 0 | -0.073242 | 0.39826 | 0.57678 | 0.3479 | 0.63171 | 0.40283 | 0.9018 | 122.4289 | 0.45319 | 122.3236 | 122.5571 | 122.3969 | 122.3419 | 122.3419 | -122.5571 | -122.3969 | 122.2137 | 122.2687 | 121.0968 | 121.1197
836.875 | 122.3557 | -121.1884 | 1.1902 | -0.0096891 | 0.0023905 | 0.068925 | 0.064589 | 0.00069854 | -0.0031574 | -0.00060235 | -0.0012513 | 0.0026639 | 0.069128 | 0.056187 | -0.0041486 | 0.016504 | -0.001506 | -0.25177 | 1.1673 | -121.3943 | 0.95215 | -120.5292 | -121.1197 | -121.2112 | -0.22888 | 1.1627 | -121.1929 | 1.0162 | -120.813 | -120.8496 | -120.6436 | -0.20599 | -0.022889 | -0.23804 | 0.65918 | -0.022889 | 0.068664 | 0.1831 | 0.27466 | -0.004578 | -0.027466 | -0.17395 | 0.37537 | 0.54474 | 0.33875 | 0.54932 | 0.34332 | 0.86517 | 122.3465 | 0.37994 | 122.2092 | 122.5616 | 122.3557 | 122.3557 | 122.3511 | -122.5845 | -122.3831 | 122.1405 | 122.2046 | 120.9366 | 120.9595
838.5625 | 122.4335 | -121.1334 | 1.149 | 0.0055694 | 0.0021769 | 0.071703 | 0.062026 | -0.0016513 | -0.0027302 | -0.0018842 | -0.0043029 | 0.0022367 | 0.071478 | 0.056828 | 0.00033757 | 0.01565 | -0.0030014 | -0.25635 | 1.1627 | -121.3531 | 0.98419 | -120.4422 | -121.051 | -121.138 | -0.20599 | 1.1261 | -121.1655 | 1.1032 | -120.7077 | -120.7306 | -120.5246 | -0.21973 | 0.013733 | -0.1648 | 0.69122 | -0.004577 | 0.082398 | 0.21515 | 0.30212 | -0.032043 | -0.022888 | -0.045777 | 0.42572 | 0.60883 | 0.40283 | 0.64087 | 0.43487 | 0.91095 | 122.3373 | 0.45776 | 122.2687 | 122.5159 | 122.2916 | 122.2961 | 122.2595 | -122.5021 | -122.3145 | 122.1176 | 122.2366 | 120.8771 | 120.9274
840.3125 | 122.3328 | -121.0831 | 1.1856 | -0.0096891 | 0.0055947 | 0.071916 | 0.06523 | 0.0021939 | -0.0042254 | -0.0010298 | -0.0043029 | 0.0043729 | 0.069983 | 0.060887 | 0.00076477 | 0.015864 | -0.002147 | -0.24719 | 1.1902 | -121.3165 | 0.93842 | -120.5063 | -121.0876 | -121.1884 | -0.25177 | 1.1581 | -121.1792 | 1.0574 | -120.7581 | -120.7993 | -120.5612 | -0.23346 | 0.004578 | -0.24719 | 0.57678 | -0.10529 | -0.004577 | 0.12817 | 0.22888 | -0.09613 | -0.027466 | -0.12817 | 0.32501 | 0.52185 | 0.28381 | 0.61798 | 0.37994 | 0.81024 | 122.2549 | 0.42114 | 122.2366 | 122.5067 | 122.3373 | 122.2733 | 122.2412 | -122.5021 | -122.3648 | 122.0215 | 122.1405 | 120.8359 | 120.8313
841.9844 | 122.3602 | -121.0373 | 1.1948 | -0.0020601 | 0.0047403 | 0.070634 | 0.065016 | -0.00058326 | -0.0031574 | 0.00046565 | -0.0012513 | 0.0030911 | 0.06806 | 0.061955 | -0.001585 | 0.013941 | 0.000203 | -0.17395 | 1.1398 | -121.257 | 1.0803 | -120.3232 | -120.9183 | -121.0281 | -0.13733 | 1.149 | -121.0876 | 1.1169 | -120.6299 | -120.6573 | -120.4742 | -0.21973 | -0.054931 | -0.11444 | 0.71411 | 0.009155 | 0.11902 | 0.22888 | 0.33875 | -0.050354 | -0.045776 | -0.07782 | 0.40741 | 0.56305 | 0.37994 | 0.6134 | 0.4303 | 0.93384 | 122.3373 | 0.45776 | 122.2046 | 122.3969 | 122.2366 | 122.1771 | 122.1863 | -122.4518 | -122.2824 | 122.1176 | 122.1542 | 120.8633 | 120.9
843.7344 | 122.287 | -121.0876 | 1.1581 | -0.0020601 | 0.0053811 | 0.069994 | 0.064803 | -0.00036966 | -0.0037982 | 3.8448e-05 | -0.0012513 | 0.0043729 | 0.068701 | 0.058751 | -0.003294 | 0.015223 | -0.0008652 | -0.1831 | 1.1353 | -121.2936 | 1.0025 | -120.3735 | -120.9641 | -121.0831 | -0.17853 | 1.1124 | -121.1426 | 1.0345 | -120.7031 | -120.7169 | -120.5292 | -0.20599 | -0.022888 | -0.15564 | 0.71411 | 0.004577 | 0.1236 | 0.21057 | 0.32959 | -0.054932 | -0.045776 | -0.1236 | 0.38452 | 0.55847 | 0.37079 | 0.6134 | 0.42572 | 0.9201 | 122.2961 | 0.43945 | 122.1771 | 122.4289 | 122.2549 | 122.2229 | 122.2 | -122.4518 | -122.3007 | 122.0901 | 122.1222 | 120.9045 | 120.9091
845.5 | 122.2275 | -121.0556 | 1.1673 | 0.051346 | 0.0060221 | 0.071062 | 0.067793 | -0.0018649 | -0.0057208 | 0.00025205 | 0.017059 | 0.0050137 | 0.073187 | 0.064091 | -0.0028668 | 0.015009 | -0.003215 | -0.19226 | 1.1856 | -121.3303 | 0.94299 | -120.4285 | -121.019 | -121.1151 | -0.24261 | 1.1719 | -121.1334 | 0.99335 | -120.7123 | -120.7489 | -120.5338 | -0.27466 | 0.018311 | -0.2243 | 0.62714 | -0.059509 | 0.036621 | 0.21515 | 0.31128 | -0.07782 | 0.004578 | -0.17395 | 0.34332 | 0.52185 | 0.3067 | 0.59967 | 0.38452 | 0.90179 | 122.2733 | 0.42114 | 122.1268 | 122.5159 | 122.3053 | 122.2412 | 122.2275 | -122.4976 | -122.3007 | 121.9986 | 122.049 | 120.8633 | 120.813
847.25 | 122.3373 | -120.9778 | 1.1261 | -0.0020601 | 0.0051675 | 0.071062 | 0.066084 | 0.0013393 | -0.0035846 | 0.00089285 | -0.0043029 | 0.0037319 | 0.07276 | 0.063237 | 0.0016194 | 0.016932 | -0.0040696 | -0.2243 | 1.1444 | -121.2021 | 1.0345 | -120.3049 | -120.9366 | -121.0236 | -0.13733 | 1.1261 | -121.0419 | 1.1536 | -120.5566 | -120.6024 | -120.3781 | -0.2243 | 0.01831 | -0.091553 | 0.67291 | -0.045777 | 0.041199 | 0.17853 | 0.2655 | -0.064087 | 0 | 0.027465 | 0.42114 | 0.59967 | 0.37537 | 0.66376 | 0.43945 | 0.89722 | 122.2366 | 0.48523 | 122.1954 | 122.3465 | 122.168 | 122.1222 | 122.1039 | -122.3282 | -122.168 | 122.0123 | 122.1313 | 120.7535 | 120.8405
848.9844 | 122.2504 | -120.9915 | 1.1673 | -0.0020601 | 0.0038857 | 0.067857 | 0.066298 | 0.00048494 | -0.0010212 | 3.8448e-05 | -0.0043029 | 0.0050137 | 0.071905 | 0.060887 | -0.00094423 | 0.016504 | -0.003856 | -0.26093 | 1.1398 | -121.2204 | 0.94299 | -120.401 | -121.0007 | -121.0739 | -0.22888 | 1.1307 | -121.0556 | 1.0712 | -120.6162 | -120.6619 | -120.4193 | -0.22888 | -0.027465 | -0.2243 | 0.59052 | -0.082398 | -0.009155 | 0.14648 | 0.21973 | -0.064087 | -0.036621 | -0.09613 | 0.37537 | 0.5722 | 0.32959 | 0.63629 | 0.39368 | 0.8194 | 122.1634 | 0.43945 | 122.1268 | 122.3602 | 122.1863 | 122.1313 | 122.1222 | -122.3877 | -122.2229 | 121.9345 | 122.0627 | 120.7306 | 120.7626
850.6719 | 122.2321 | -120.9732 | 1.1307 | 0.0055694 | 0.0043131 | 0.072984 | 0.065016 | 0.0019803 | -0.0010212 | -0.00060235 | 0.0018005 | 0.0028775 | 0.068701 | 0.06046 | 0.00097837 | 0.015864 | -0.0025742 | -0.24261 | 1.1124 | -121.1746 | 0.99792 | -120.2866 | -120.8954 | -121.0052 | -0.20599 | 1.1124 | -121.0327 | 1.062 | -120.5887 | -120.6024 | -120.4056 | -0.20142 | -0.01831 | -0.13275 | 0.68665 | -0.032043 | 0.07782 | 0.16937 | 0.27924 | -0.059509 | -0.01831 | -0.068664 | 0.38452 | 0.56763 | 0.37079 | 0.62714 | 0.4303 | 0.88806 | 122.1725 | 0.44403 | 122.0947 | 122.287 | 122.1451 | 122.0856 | 122.0856 | -122.3053 | -122.1634 | 121.9711 | 122.0352 | 120.7306 | 120.7672
852.4219 | 122.1176 | -120.9549 | 1.1673 | -0.0020601 | 0.0049539 | 0.071062 | 0.066512 | 0.00069854 | -0.0025166 | -0.002525 | -0.0073547 | 0.0056545 | 0.069769 | 0.060673 | 0.00033757 | 0.015009 | -0.0010788 | -0.22888 | 1.1673 | -121.1655 | 0.92926 | -120.3827 | -120.9686 | -121.0556 | -0.27008 | 1.149 | -120.9961 | 0.97961 | -120.6528 | -120.694 | -120.4468 | -0.21057 | 0 | -0.23804 | 0.5722 | -0.10071 | -0.013733 | 0.10986 | 0.19684 | -0.041199 | -0.01831 | -0.18768 | 0.30212 | 0.50812 | 0.26093 | 0.54932 | 0.30212 | 0.78278 | 122.0947 | 0.34332 | 121.9757 | 122.3328 | 122.1451 | 122.1222 | 122.1039 | -122.3328 | -122.1634 | 121.8842 | 121.9345 | 120.726 | 120.6848
854.1875 | 122.1313 | -121.0281 | 1.1124 | -0.0096891 | 0.0038857 | 0.06978 | 0.06523 | 0.0036893 | -0.0040118 | -0.0029524 | 0.0018005 | 0.0028775 | 0.073614 | 0.052769 | -0.005003 | 0.012659 | -1.0598e-05 | -0.2243 | 1.1032 | -121.2158 | 0.86975 | -120.3598 | -120.9503 | -121.0373 | -0.22888 | 1.0757 | -121.0739 | 0.94757 | -120.6436 | -120.6848 | -120.4559 | -0.18768 | -0.009156 | -0.24261 | 0.66833 | -0.009155 | 0.07782 | 0.17853 | 0.2655 | -0.045777 | -0.036621 | -0.16479 | 0.38452 | 0.5722 | 0.34332 | 0.61798 | 0.3891 | 0.85602 | 122.0856 | 0.4303 | 122.0215 | 122.319 | 122.1497 | 122.1313 | 122.1039 | -122.3282 | -122.1863 | 121.8979 | 121.9757 | 120.8038 | 120.7993
855.9375 | 122.2458 | -120.9137 | 1.1078 | -0.0096891 | 0.0030313 | 0.06978 | 0.06523 | 0.0028347 | -0.0023028 | -0.0033796 | 0.020111 | 0.0050137 | 0.070196 | 0.066014 | 0.0020466 | 0.016504 | -0.0019332 | -0.1831 | 1.0803 | -121.1151 | 1.0208 | -120.2133 | -120.813 | -120.8908 | -0.091553 | 1.0986 | -121.0052 | 1.0986 | -120.4742 | -120.52 | -120.3003 | -0.20142 | -0.027466 | -0.086975 | 0.70038 | 0.022888 | 0.10071 | 0.2243 | 0.30212 | -0.091553 | -0.009155 | -0.009155 | 0.43945 | 0.6134 | 0.39368 | 0.70496 | 0.48523 | 0.90179 | 122.1359 | 0.53101 | 122.1039 | 122.1954 | 122.1039 | 121.994 | 122.0123 | -122.2229 | -122.113 | 121.9345 | 122.0123 | 120.7306 | 120.8221
857.6875 | 122.1313 | -120.9091 | 1.0895 | 0.0055694 | 0.0043131 | 0.06978 | 0.066298 | 0.0032619 | -0.0023028 | 0.00025205 | -0.0012513 | 0.0043729 | 0.068701 | 0.064732 | 0.00033757 | 0.016932 | -0.0019332 | -0.24719 | 1.1215 | -121.1563 | 0.91095 | -120.3094 | -120.9366 | -121.0007 | -0.21057 | 1.0986 | -120.9915 | 1.0345 | -120.5612 | -120.5704 | -120.3506 | -0.24719 | 0.032043 | -0.17853 | 0.59967 | -0.091552 | -0.027465 | 0.15564 | 0.21973 | -0.082397 | 0.009155 | -0.054932 | 0.3479 | 0.55847 | 0.33875 | 0.64087 | 0.42114 | 0.84686 | 122.0673 | 0.4303 | 122.0261 | 122.2778 | 122.0901 | 122.0306 | 122.0078 | -122.2458 | -122.081 | 121.8201 | 121.9437 | 120.6619 | 120.6985
859.375 | 122.0993 | -120.9229 | 1.1307 | 0.028458 | 0.0066629 | 0.071489 | 0.066512 | 0.0043301 | 0.00047422 | -0.002525 | 0.0048523 | 0.0054409 | 0.071692 | 0.053837 | -0.0035076 | 0.016504 | -0.001506 | -0.14191 | 1.1215 | -121.1609 | 0.9613 | -120.2316 | -120.845 | -120.932 | -0.12817 | 1.1215 | -120.9778 | 1.0071 | -120.52 | -120.5429 | -120.3094 | -0.23804 | -0.009155 | -0.16937 | 0.69122 | -0.009155 | 0.07782 | 0.22888 | 0.31586 | -0.054931 | -0.009155 | -0.1236 | 0.40283 | 0.6134 | 0.37994 | 0.66833 | 0.43488 | 0.92926 | 122.1222 | 0.45776 | 121.9849 | 122.2824 | 122.0993 | 122.0444 | 122.0444 | -122.2916 | -122.1085 | 121.8842 | 121.9299 | 120.7809 | 120.7947
861.0781 | 122.0764 | -120.8679 | 1.1261 | 0.020828 | 0.0049539 | 0.069994 | 0.066298 | 0.0015529 | 0.00047422 | -0.0012434 | 0.0048523 | 0.0045865 | 0.072333 | 0.057469 | -0.0024396 | 0.016718 | 0.0059708 | -0.15564 | 1.1581 | -121.1105 | 0.96588 | -120.1904 | -120.7672 | -120.8908 | -0.12817 | 1.1215 | -120.9274 | 1.0437 | -120.4514 | -120.5063 | -120.2866 | -0.24262 | 0.032043 | -0.16022 | 0.67749 | -0.022888 | 0.10071 | 0.21973 | 0.34332 | -0.059509 | -0.004578 | -0.082398 | 0.41656 | 0.58136 | 0.36163 | 0.64087 | 0.42114 | 0.9201 | 122.0764 | 0.47607 | 121.9711 | 122.2687 | 122.049 | 122.0261 | 121.9894 | -122.2366 | -122.0535 | 121.8338 | 121.9116 | 120.7123 | 120.7397
862.8125 | 122.0169 | -120.8908 | 1.1444 | -0.0020601 | 0.0028177 | 0.067857 | 0.065657 | -0.0014377 | -0.0040118 | -0.0018842 | 0.0018005 | 0.0050137 | 0.071265 | 0.065587 | -0.0030804 | 0.016077 | -0.002147 | -0.24261 | 1.1261 | -121.0831 | 0.88806 | -120.2179 | -120.8221 | -120.9137 | -0.24719 | 1.1169 | -120.9091 | 0.97504 | -120.5109 | -120.5383 | -120.3278 | -0.19226 | -0.01831 | -0.25635 | 0.67291 | -0.022888 | 0.068664 | 0.16937 | 0.26093 | -0.018311 | -0.027466 | -0.16937 | 0.37994 | 0.56305 | 0.35248 | 0.58136 | 0.37079 | 0.86517 | 121.9711 | 0.39826 | 121.8842 | 122.2092 | 122.0261 | 122.0169 | 122.0078 | -122.2275 | -122.0535 | 121.7789 | 121.8658 | 120.6482 | 120.6436
864.5469 | 122.0078 | -120.8725 | 1.1307 | 0.0055694 | 0.0062357 | 0.06978 | 0.066512 | 0.0030483 | -0.001662 | -0.0012434 | -0.0043029 | 0.0028775 | 0.069556 | 0.057255 | -0.002226 | 0.015436 | -0.002147 | -0.16479 | 1.1124 | -121.0327 | 0.94299 | -120.1859 | -120.8038 | -120.8817 | -0.16937 | 1.1124 | -120.8908 | 1.0071 | -120.4926 | -120.5383 | -120.2957 | -0.16022 | -0.01831 | -0.18768 | 0.68665 | -0.009155 | 0.068665 | 0.15106 | 0.22888 | -0.01831 | -0.01831 | -0.1236 | 0.37994 | 0.57678 | 0.33417 | 0.59509 | 0.35248 | 0.84686 | 121.9757 | 0.39825 | 121.8979 | 122.1451 | 122.0032 | 121.9849 | 121.9849 | -122.1634 | -122.0215 | 121.8155 | 121.8796 | 120.7077 | 120.7031
866.2969 | 121.9757 | -120.8633 | 1.1307 | -0.0020601 | 0.0038857 | 0.071062 | 0.063094 | -0.0016513 | -0.001662 | -0.0010298 | 0.0018005 | 0.0022367 | 0.071265 | 0.065373 | -0.002226 | 0.016504 | -0.0002244 | -0.20599 | 1.0712 | -121.0373 | 0.94757 | -120.1355 | -120.7397 | -120.8496 | -0.21057 | 1.0986 | -120.8862 | 0.97504 | -120.4514 | -120.4926 | -120.2774 | -0.17395 | -0.059509 | -0.1831 | 0.72784 | 0.013733 | 0.1236 | 0.18768 | 0.29755 | -0.022888 | -0.032043 | -0.15564 | 0.41199 | 0.58594 | 0.37079 | 0.60882 | 0.39368 | 0.90179 | 121.9849 | 0.43487 | 121.8613 | 122.1085 | 121.9849 | 121.9345 | 121.962 | -122.168 | -122.0169 | 121.8109 | 121.8384 | 120.6573 | 120.6528
868.0312 | 121.9757 | -120.7947 | 1.1261 | 0.043716 | 0.0070901 | 0.071489 | 0.065016 | -0.0014377 | -0.0020892 | -0.00017515 | 0.0079041 | 0.0052273 | 0.070196 | 0.054478 | 0.00012397 | 0.01565 | -0.0053512 | -0.1831 | 1.149 | -121.051 | 0.92468 | -120.1859 | -120.7443 | -120.8588 | -0.21973 | 1.1307 | -120.8954 | 0.98419 | -120.4285 | -120.4605 | -120.2362 | -0.25635 | 0.022888 | -0.20142 | 0.60883 | -0.064087 | 0.050354 | 0.19226 | 0.3067 | -0.10071 | 0.004577 | -0.14191 | 0.36621 | 0.55847 | 0.33417 | 0.65918 | 0.43488 | 0.86517 | 121.9757 | 0.46692 | 121.8796 | 122.2 | 122.0261 | 121.9437 | 121.9254 | -122.1771 | -122.0215 | 121.7194 | 121.7789 | 120.6116 | 120.575
869.7812 | 121.9162 | -120.8084 | 1.1398 | 0.0055694 | 0.0040995 | 0.069353 | 0.066725 | 0.0011257 | 0.00047422 | -0.0016706 | 0.0018005 | 0.0048001 | 0.069128 | 0.0611 | -8.9634e-05 | 0.015009 | -0.0006516 | -0.21057 | 1.1215 | -121.0052 | 0.89264 | -120.163 | -120.7672 | -120.8771 | -0.25635 | 1.1261 | -120.8221 | 0.98877 | -120.4559 | -120.488 | -120.2408 | -0.19684 | -0.018311 | -0.24719 | 0.64545 | -0.068664 | 0.041199 | 0.12817 | 0.23804 | -0.013733 | -0.013733 | -0.15106 | 0.35248 | 0.56763 | 0.32044 | 0.58136 | 0.33417 | 0.84229 | 121.8979 | 0.36621 | 121.8109 | 122.1268 | 121.9482 | 121.9299 | 121.9345 | -122.1451 | -121.962 | 121.7011 | 121.7972 | 120.5978 | 120.5521
871.4688 | 121.9666 | -120.7214 | 1.1765 | 0.013199 | 0.0060221 | 0.069566 | 0.066512 | 0.0015529 | -0.00080758 | -0.001457 | 0.010956 | 0.0054409 | 0.069342 | 0.064732 | -0.00094423 | 0.014582 | -0.0027878 | -0.16937 | 1.1765 | -120.9183 | 1.0254 | -120.0027 | -120.6162 | -120.7123 | -0.13275 | 1.1765 | -120.7672 | 1.0895 | -120.2911 | -120.3369 | -120.1172 | -0.19684 | 0 | -0.15106 | 0.71869 | 0.009156 | 0.10529 | 0.20599 | 0.30212 | -0.045776 | 0 | -0.086975 | 0.4303 | 0.60425 | 0.38452 | 0.65002 | 0.4303 | 0.91553 | 121.9437 | 0.47607 | 121.8567 | 122.0947 | 121.9437 | 121.8979 | 121.8979 | -122.0947 | -121.9437 | 121.7468 | 121.8109 | 120.5521 | 120.5887
873.2188 | 122.0215 | -120.6802 | 1.1124 | -0.0020601 | 0.0058083 | 0.071703 | 0.064162 | 0.0013393 | -0.0025166 | -0.0012434 | -0.0012513 | 0.0024503 | 0.070624 | 0.062809 | 0.0014056 | 0.016504 | -0.0019332 | -0.20142 | 1.0986 | -120.8633 | 1.0208 | -119.9844 | -120.607 | -120.694 | -0.14191 | 1.0941 | -120.7214 | 1.1307 | -120.2454 | -120.2957 | -120.0623 | -0.1831 | -0.013733 | -0.091553 | 0.6958 | -0.013733 | 0.073242 | 0.16937 | 0.25635 | -0.041199 | -0.018311 | 0.01831 | 0.43488 | 0.61798 | 0.38452 | 0.65918 | 0.42572 | 0.87891 | 121.8842 | 0.47607 | 121.8521 | 121.962 | 121.8155 | 121.7789 | 121.7743 | -121.9757 | -121.8338 | 121.7011 | 121.8109 | 120.4788 | 120.5383
874.9688 | 121.8704 | -120.607 | 1.2863 | -0.0096891 | 0.0036721 | 0.070848 | 0.063307 | -0.00079686 | -0.00508 | -0.0016706 | -0.0012513 | 0.0037319 | 0.069983 | 0.057255 | -0.0035076 | 0.015436 | -0.0006516 | -0.22888 | 1.2543 | -120.7855 | 1.0345 | -119.9524 | -120.5383 | -120.6299 | -0.24261 | 1.2451 | -120.639 | 1.0803 | -120.2316 | -120.2682 | -120.0485 | -0.17853 | -0.032044 | -0.25177 | 0.6546 | -0.022888 | 0.068665 | 0.15564 | 0.24719 | -0.032043 | -0.041199 | -0.20599 | 0.37537 | 0.55847 | 0.33875 | 0.59051 | 0.37079 | 0.83313 | 121.8201 | 0.40741 | 121.7194 | 122.0398 | 121.8842 | 121.8613 | 121.8521 | -122.0718 | -121.9254 | 121.6415 | 121.6873 | 120.3781 | 120.3644
876.6406 | 121.9391 | -120.5978 | 1.2039 | 0.043716 | 0.0066629 | 0.071062 | 0.063094 | 0.0045437 | -0.00059378 | -0.00017515 | 0.014008 | 0.0033047 | 0.072119 | 0.066441 | 0.0020466 | 0.017359 | 0.0006302 | -0.19684 | 1.1902 | -120.8176 | 1.0986 | -119.8425 | -120.4788 | -120.5704 | -0.12817 | 1.181 | -120.639 | 1.1765 | -120.1767 | -120.2225 | -120.0027 | -0.21973 | -0.013732 | -0.10529 | 0.75531 | 0.027465 | 0.11902 | 0.24719 | 0.33875 | -0.041199 | -0.022888 | -0.027465 | 0.42114 | 0.59509 | 0.37537 | 0.63629 | 0.41657 | 0.97504 | 121.9162 | 0.46234 | 121.8155 | 122.0078 | 121.8201 | 121.788 | 121.7789 | -122.0215 | -121.843 | 121.6965 | 121.7743 | 120.401 | 120.4697
878.3906 | 121.9666 | -120.5429 | 1.181 | -0.0096891 | 0.0021769 | 0.069566 | 0.064375 | 0.0051845 | -0.0031574 | -0.0012434 | -0.0073547 | 0.0028775 | 0.067206 | 0.063878 | -0.00051703 | 0.015223 | -0.0036422 | -0.21515 | 1.149 | -120.8038 | 1.0849 | -119.8471 | -120.4514 | -120.5475 | -0.09613 | 1.1398 | -120.6299 | 1.1856 | -120.1035 | -120.1172 | -119.9524 | -0.26093 | -0.032043 | -0.09613 | 0.6958 | -0.004577 | 0.091553 | 0.25635 | 0.35248 | -0.086975 | -0.041198 | 0.004578 | 0.43945 | 0.59051 | 0.42572 | 0.67749 | 0.5127 | 0.95673 | 121.8887 | 0.52643 | 121.8155 | 121.9528 | 121.7697 | 121.6919 | 121.6827 | -121.9849 | -121.8109 | 121.6278 | 121.7285 | 120.3278 | 120.4468
880.1562 | 121.875 | -120.5338 | 1.2222 | 0.013199 | 0.0047403 | 0.071062 | 0.063521 | -0.00036966 | -0.0018756 | -0.0020978 | 0.0048523 | 0.0018093 | 0.068915 | 0.057896 | 0.00012397 | 0.015864 | 0.0006302 | -0.25635 | 1.2222 | -120.7581 | 1.0666 | -119.8608 | -120.4788 | -120.5521 | -0.2243 | 1.1902 | -120.6207 | 1.1398 | -120.1538 | -120.1859 | -119.9661 | -0.2243 | 0 | -0.15564 | 0.67291 | -0.018311 | 0.054931 | 0.20599 | 0.27924 | -0.086976 | -0.032043 | -0.082397 | 0.37994 | 0.56763 | 0.3479 | 0.6546 | 0.43488 | 0.89722 | 121.8246 | 0.46692 | 121.7606 | 121.9803 | 121.8109 | 121.756 | 121.7239 | -121.9803 | -121.843 | 121.6003 | 121.6736 | 120.2774 | 120.3094
881.9062 | 121.8018 | -120.5704 | 1.1993 | -0.0020601 | 0.0055947 | 0.071275 | 0.067793 | 0.0011257 | -0.0037982 | -0.0023114 | 0.0018005 | 0.0075771 | 0.069556 | 0.059391 | 0.00097837 | 0.012659 | -0.0047104 | -0.17395 | 1.1765 | -120.8176 | 1.0071 | -119.9112 | -120.5292 | -120.639 | -0.17395 | 1.1581 | -120.6299 | 1.062 | -120.2225 | -120.2728 | -120.0211 | -0.24719 | -0.022888 | -0.19226 | 0.65918 | -0.068664 | 0.041199 | 0.17853 | 0.28839 | -0.059509 | -0.041199 | -0.13733 | 0.3479 | 0.54932 | 0.29755 | 0.60883 | 0.35706 | 0.90637 | 121.8246 | 0.40741 | 121.6919 | 121.994 | 121.788 | 121.7468 | 121.7285 | -122.0169 | -121.8292 | 121.5775 | 121.6324 | 120.3964 | 120.3964
883.5781 | 121.8475 | -120.575 | 1.1581 | 0.028458 | 0.0045267 | 0.070207 | 0.06523 | 0.0036893 | -0.0037982 | -0.002525 | 0.010956 | 0.0039457 | 0.071478 | 0.063237 | -0.00051703 | 0.017786 | -0.000438 | -0.24261 | 1.1444 | -120.7993 | 1.0117 | -119.8883 | -120.4834 | -120.575 | -0.21057 | 1.1307 | -120.6253 | 1.0849 | -120.195 | -120.195 | -119.9844 | -0.2243 | -0.013733 | -0.14648 | 0.68664 | 0 | 0.091553 | 0.2243 | 0.31586 | -0.050354 | -0.027466 | -0.073242 | 0.37994 | 0.59051 | 0.37994 | 0.64087 | 0.4303 | 0.91095 | 121.8109 | 0.4303 | 121.7102 | 121.9437 | 121.756 | 121.7194 | 121.7056 | -121.9574 | -121.7834 | 121.5866 | 121.6599 | 120.3323 | 120.3644
885.3281 | 121.8704 | -120.575 | 1.1169 | 0.0055694 | 0.0040995 | 0.068712 | 0.063307 | -0.0025059 | -0.003371 | -0.0027386 | -0.0073547 | 0.0024503 | 0.069983 | 0.063878 | -0.0017986 | 0.014795 | -0.003856 | -0.19684 | 1.1032 | -120.7947 | 1.0529 | -119.8196 | -120.4285 | -120.5475 | -0.11444 | 1.0986 | -120.6162 | 1.1078 | -120.1172 | -120.1218 | -119.9661 | -0.21973 | -0.013733 | -0.064087 | 0.75531 | 0.027466 | 0.14648 | 0.24719 | 0.36621 | -0.041199 | -0.01831 | -0.009155 | 0.45776 | 0.60883 | 0.45319 | 0.65002 | 0.49439 | 0.97504 | 121.8475 | 0.49896 | 121.7239 | 121.8979 | 121.7148 | 121.6782 | 121.6736 | -121.9116 | -121.7331 | 121.6278 | 121.6827 | 120.3781 | 120.4605
887.0781 | 121.7697 | -120.5933 | 1.1032 | 0.036087 | 0.0047403 | 0.068498 | 0.065443 | 0.0045437 | -0.0010212 | 0.00067925 | 0.0079041 | 0.0062955 | 0.07041 | 0.062382 | -0.0017986 | 0.014368 | -0.0017196 | -0.16022 | 1.1169 | -120.845 | 0.95673 | -119.9158 | -120.5338 | -120.6116 | -0.13733 | 1.0986 | -120.6528 | 1.0254 | -120.1996 | -120.2316 | -120.0165 | -0.25177 | 0.013733 | -0.14648 | 0.67749 | -0.01831 | 0.05951 | 0.23346 | 0.31128 | -0.059509 | -0.004577 | -0.077819 | 0.39368 | 0.57678 | 0.36163 | 0.63629 | 0.42114 | 0.92926 | 121.8018 | 0.45319 | 121.6782 | 121.962 | 121.7514 | 121.7102 | 121.6919 | -121.9482 | -121.756 | 121.55 | 121.6187 | 120.433 | 120.4559
888.8281 | 121.6965 | -120.6024 | 1.0986 | -0.0020601 | 0.0060221 | 0.069994 | 0.066512 | 0.00027134 | -0.0025166 | 0.00046565 | 0.0018005 | 0.0030911 | 0.070837 | 0.059178 | -8.9634e-05 | 0.016504 | 0.0021256 | -0.23346 | 1.1032 | -120.8038 | 0.86975 | -119.9982 | -120.607 | -120.6757 | -0.28381 | 1.0849 | -120.6482 | 0.97504 | -120.2911 | -120.314 | -120.0668 | -0.20142 | 0.004577 | -0.22888 | 0.60425 | -0.073242 | -0.004578 | 0.12817 | 0.19684 | -0.045776 | -0.013733 | -0.1236 | 0.31128 | 0.53558 | 0.28839 | 0.58136 | 0.33417 | 0.80566 | 121.6736 | 0.35706 | 121.6232 | 121.907 | 121.7331 | 121.7056 | 121.6873 | -121.9025 | -121.7468 | 121.4722 | 121.5775 | 120.369 | 120.3186
890.5469 | 121.6827 | -120.5704 | 1.1169 | -0.0096891 | 0.0070901 | 0.071062 | 0.065443 | 0.0013393 | -0.0025166 | -0.0040204 | -0.0043029 | 0.0043729 | 0.069128 | 0.054905 | 0.00055117 | 0.016504 | -0.0036422 | -0.2243 | 1.1307 | -120.7993 | 0.88348 | -119.9799 | -120.5704 | -120.6711 | -0.28839 | 1.1124 | -120.6436 | 0.97046 | -120.2591 | -120.3003 | -120.0394 | -0.22888 | 0.013733 | -0.23346 | 0.59052 | -0.10071 | 0 | 0.12817 | 0.22888 | -0.073242 | -0.004577 | -0.14648 | 0.31128 | 0.53101 | 0.27008 | 0.60425 | 0.34332 | 0.8194 | 121.6827 | 0.38452 | 121.6141 | 121.9299 | 121.756 | 121.701 | 121.6827 | -121.9162 | -121.7606 | 121.4539 | 121.5408 | 120.3461 | 120.282
892.2969 | 121.7194 | -120.5566 | 1.1078 | -0.0096891 | 0.0043131 | 0.070848 | 0.060103 | 0.0024075 | -0.0027302 | 0.0011066 | 0.0018005 | 0.0020231 | 0.072119 | 0.057469 | -0.005003 | 0.014368 | -0.0085556 | -0.18768 | 1.0574 | -120.7352 | 0.97961 | -119.8288 | -120.4285 | -120.5292 | -0.16937 | 1.0666 | -120.5978 | 0.99792 | -120.1309 | -120.1813 | -119.9799 | -0.17853 | -0.050354 | -0.12817 | 0.72785 | 0.027466 | 0.12817 | 0.20599 | 0.3067 | -0.041198 | -0.041199 | -0.10986 | 0.42572 | 0.57678 | 0.37537 | 0.61798 | 0.41656 | 0.90637 | 121.7148 | 0.46692 | 121.5958 | 121.7926 | 121.6644 | 121.6141 | 121.6232 | -121.843 | -121.7056 | 121.5363 | 121.5546 | 120.369 | 120.3873
893.9688 | 121.6507 | -120.4926 | 1.1581 | -0.017319 | 0.0055947 | 0.071703 | 0.066725 | 0.0017667 | -0.0027302 | -0.0016706 | -0.0012513 | 0.0035183 | 0.072119 | 0.055119 | 0.00012397 | 0.0133 | -0.0036422 | -0.24261 | 1.1398 | -120.6985 | 0.91095 | -119.9203 | -120.4971 | -120.5933 | -0.27924 | 1.1536 | -120.575 | 0.99335 | -120.1859 | -120.2179 | -119.9478 | -0.20599 | -0.01831 | -0.24719 | 0.5722 | -0.10071 | -0.004577 | 0.10529 | 0.20142 | -0.082397 | -0.004578 | -0.1648 | 0.3067 | 0.54474 | 0.27466 | 0.62714 | 0.35706 | 0.7782 | 121.6095 | 0.3891 | 121.5683 | 121.8384 | 121.7285 | 121.6324 | 121.6461 | -121.8567 | -121.7331 | 121.4035 | 121.4859 | 120.2499 | 120.2133
895.7188 | 121.7239 | -120.4971 | 1.1032 | 0.0055694 | 0.0028177 | 0.069566 | 0.060744 | -0.00015586 | -0.0020892 | 3.8448e-05 | -0.0073547 | 0.0011685 | 0.071051 | 0.059605 | -0.0030804 | 0.015009 | -0.0006516 | -0.1831 | 1.0666 | -120.6985 | 1.0117 | -119.7556 | -120.3598 | -120.4742 | -0.14191 | 1.0666 | -120.5429 | 1.0483 | -120.0531 | -120.076 | -119.8929 | -0.20142 | -0.036621 | -0.091552 | 0.74158 | 0.022888 | 0.13733 | 0.2243 | 0.33875 | -0.045777 | -0.036621 | -0.054931 | 0.44403 | 0.60425 | 0.42114 | 0.65002 | 0.46692 | 0.94299 | 121.7102 | 0.48981 | 121.5912 | 121.7651 | 121.6095 | 121.5637 | 121.5637 | -121.8018 | -121.6461 | 121.5088 | 121.5454 | 120.314 | 120.3552
897.4688 | 121.6965 | -120.4742 | 1.1032 | 0.013199 | 0.0043131 | 0.068712 | 0.065016 | 0.0032619 | -0.001662 | -0.0029524 | 0.0079041 | 0.0033047 | 0.068488 | 0.064305 | -0.00073063 | 0.015436 | -0.0027878 | -0.26093 | 1.0757 | -120.6985 | 0.95673 | -119.8013 | -120.3964 | -120.4926 | -0.21973 | 1.062 | -120.5475 | 1.0117 | -120.0989 | -120.1126 | -119.9066 | -0.2243 | -0.027465 | -0.14648 | 0.67291 | -0.018311 | 0.07782 | 0.20599 | 0.30212 | -0.073242 | -0.041198 | -0.091552 | 0.37537 | 0.56763 | 0.36163 | 0.64087 | 0.43487 | 0.89722 | 121.6553 | 0.44861 | 121.5591 | 121.7743 | 121.6095 | 121.55 | 121.5363 | -121.8018 | -121.6507 | 121.431 | 121.4859 | 120.2133 | 120.2545
899.2188 | 121.6049 | -120.4834 | 1.1307 | 0.013199 | 0.0045267 | 0.068925 | 0.066084 | 0.0039029 | -0.0029438 | 0.00046565 | 0.0018005 | 0.0052273 | 0.068274 | 0.058751 | -0.0054302 | 0.015223 | 0.0006302 | -0.24261 | 1.1124 | -120.7077 | 0.90637 | -119.8288 | -120.4102 | -120.4971 | -0.2243 | 1.1032 | -120.5017 | 0.95673 | -120.0989 | -120.1355 | -119.9249 | -0.22431 | -0.01831 | -0.2243 | 0.6546 | -0.013733 | 0.073242 | 0.21057 | 0.29755 | -0.018311 | -0.027466 | -0.17395 | 0.38452 | 0.55847 | 0.3479 | 0.57678 | 0.36621 | 0.87891 | 121.6141 | 0.40283 | 121.4584 | 121.8201 | 121.6049 | 121.5958 | 121.5866 | -121.8384 | -121.6324 | 121.3898 | 121.4401 | 120.2408 | 120.2591
900.9688 | 121.5958 | -120.433 | 1.1307 | -0.0020601 | 0.0043131 | 0.071062 | 0.068007 | 0.0017667 | -0.0025166 | -0.0023114 | 0.0018005 | 0.0058683 | 0.071905 | 0.063878 | 0.0014056 | 0.016291 | -0.0025742 | -0.25635 | 1.1398 | -120.639 | 0.89264 | -119.8334 | -120.433 | -120.5109 | -0.27008 | 1.1078 | -120.4742 | 1.0025 | -120.0943 | -120.1309 | -119.8837 | -0.20599 | 0.009156 | -0.23804 | 0.59967 | -0.07782 | 0 | 0.12817 | 0.20599 | -0.041199 | -0.022888 | -0.12817 | 0.33874 | 0.54932 | 0.30212 | 0.59051 | 0.34332 | 0.80566 | 121.5317 | 0.37994 | 121.4767 | 121.7789 | 121.582 | 121.5729 | 121.5408 | -121.7697 | -121.6049 | 121.3257 | 121.4355 | 120.1767 | 120.163
902.6562 | 121.637 | -120.3735 | 1.1765 | 0.043716 | 0.0060221 | 0.070634 | 0.067793 | 0.0053983 | -0.0023028 | -0.0016706 | 0.010956 | 0.0082181 | 0.071265 | 0.058964 | -0.0013714 | 0.014795 | -0.0010788 | -0.16937 | 1.1948 | -120.6207 | 0.98877 | -119.7006 | -120.2728 | -120.3964 | -0.1831 | 1.1902 | -120.4559 | 1.062 | -119.9844 | -120.0119 | -119.7922 | -0.24719 | 0.01831 | -0.18768 | 0.67291 | -0.022888 | 0.10071 | 0.22431 | 0.3479 | -0.082398 | 0.013733 | -0.11444 | 0.3891 | 0.58136 | 0.36163 | 0.66376 | 0.44403 | 0.92011 | 121.6095 | 0.4715 | 121.5179 | 121.8155 | 121.6461 | 121.5683 | 121.5637 | -121.7972 | -121.6324 | 121.3623 | 121.4355 | 120.2042 | 120.1904
904.3906 | 121.5363 | -120.4102 | 1.1169 | -0.0096891 | 0.0051675 | 0.070848 | 0.065657 | 0.0021939 | -0.00080758 | -0.0020978 | -0.0012513 | 0.0048001 | 0.070837 | 0.060673 | 0.00012397 | 0.016718 | -0.002147 | -0.21515 | 1.1032 | -120.6162 | 0.89264 | -119.8196 | -120.4239 | -120.5063 | -0.27924 | 1.1078 | -120.4559 | 0.9613 | -120.0897 | -120.1584 | -119.8654 | -0.20599 | -0.013733 | -0.2243 | 0.59051 | -0.096131 | -0.013733 | 0.10986 | 0.19226 | -0.045777 | -0.009155 | -0.15564 | 0.32043 | 0.54474 | 0.25177 | 0.59052 | 0.29755 | 0.79651 | 121.5088 | 0.36621 | 121.4172 | 121.7194 | 121.5637 | 121.5134 | 121.5179 | -121.7331 | -121.5729 | 121.3028 | 121.3715 | 120.195 | 120.1309
906.1406 | 121.6141 | -120.3873 | 1.0941 | 0.028458 | 0.0023905 | 0.067217 | 0.064375 | -0.00058326 | -0.00080758 | 0.0032428 | 0.0018005 | 0.0030911 | 0.067633 | 0.064946 | -0.001585 | 0.014582 | -1.0598e-05 | -0.24719 | 1.0712 | -120.6116 | 0.93384 | -119.7189 | -120.3415 | -120.401 | -0.23804 | 1.0666 | -120.4468 | 1.0071 | -119.9936 | -120.0165 | -119.8013 | -0.2243 | -0.022888 | -0.16022 | 0.66833 | -0.013733 | 0.045776 | 0.21057 | 0.27008 | -0.059509 | -0.027466 | -0.086975 | 0.39368 | 0.58594 | 0.37079 | 0.64545 | 0.4303 | 0.89264 | 121.5454 | 0.45319 | 121.4539 | 121.6827 | 121.5134 | 121.4584 | 121.4539 | -121.7056 | -121.5408 | 121.3211 | 121.3943 | 120.1401 | 120.1492
907.8906 | 121.6415 | -120.3873 | 1.0712 | -0.024948 | 0.0047403 | 0.068071 | 0.063307 | 0.0041165 | -0.0031574 | 0.00089285 | -0.0043029 | 0.0039457 | 0.071478 | 0.067936 | 0.00012397 | 0.016504 | -0.0012924 | -0.2243 | 1.062 | -120.575 | 0.98419 | -119.6411 | -120.2454 | -120.3415 | -0.12817 | 1.0208 | -120.4376 | 1.0666 | -119.8975 | -119.9295 | -119.7418 | -0.18768 | -0.009155 | -0.086975 | 0.74616 | 0.045776 | 0.14191 | 0.23346 | 0.32959 | -0.050354 | -0.050354 | -0.004578 | 0.48981 | 0.64545 | 0.45776 | 0.6958 | 0.50812 | 0.93384 | 121.5591 | 0.54016 | 121.5042 | 121.637 | 121.4584 | 121.4493 | 121.4081 | -121.6461 | -121.5088 | 121.3715 | 121.4539 | 120.163 | 120.2591
909.5781 | 121.7239 | -0.25177 | 121.5591 | -0.0020601 | 0.0081583 | 0.068712 | 0.063307 | -0.00079686 | -0.0014484 | -0.0010298 | 0.0048523 | 0.0056545 | 0.069769 | 0.060887 | -0.0030804 | 0.015436 | -0.002147 | 0.25635 | 121.6278 | -0.3891 | 121.2021 | -0.13275 | -0.26093 | -0.2243 | 0.23804 | 121.4859 | -0.32501 | 121.3531 | -0.1236 | -0.20599 | -0.064087 | -0.13733 | 0.068665 | -0.35706 | 0.11902 | 0.027466 | -0.009155 | 0.16479 | 0.12817 | -0.073242 | -0.073242 | -0.20599 | 0.12817 | 0.18768 | 0.045776 | 0.26093 | 0.11902 | 0.25635 | 121.5912 | 0.20142 | 121.6782 | 122.0169 | 121.8109 | 121.8796 | 121.7377 | -121.9482 | -121.8842 | 121.4539 | 121.6049 | 0.50812 | 0.48981
911.3281 | 121.9574 | -0.23804 | 121.6003 | 0.0055694 | 0.0030313 | 0.068925 | 0.061812 | 5.774e-05 | -0.0042254 | 0.00025205 | -0.0043029 | 0.0035183 | 0.071265 | 0.070286 | -0.0041486 | 0.014155 | 0.0006302 | 0.20599 | 121.6415 | -0.34332 | 121.4355 | 0.059509 | -0.091553 | -0.073242 | 0.35706 | 121.4996 | -0.29755 | 121.55 | 0.022888 | -0.045776 | 0.032043 | -0.10529 | 0.041199 | -0.16479 | 0.29755 | 0.16479 | 0.14648 | 0.27008 | 0.25177 | -0.059509 | -0.10071 | -0.050354 | 0.26093 | 0.27008 | 0.19226 | 0.32959 | 0.25177 | 0.40283 | 121.7789 | 0.32043 | 121.8475 | 121.9849 | 121.7972 | 121.8796 | 121.7377 | -121.9437 | -121.8979 | 121.6736 | 121.788 | 0.44403 | 0.59509
913.0781 | 121.8933 | -0.25177 | 121.6827 | 0.013199 | 0.0038857 | 0.069353 | 0.063948 | 0.0017667 | -0.0027302 | 0.0032428 | 0.0048523 | 0.0056545 | 0.069769 | 0.064091 | 0.00076477 | 0.014155 | -0.0023606 | 0.2243 | 121.701 | -0.37994 | 121.4127 | -0.027466 | -0.1831 | -0.14191 | 0.2655 | 121.5729 | -0.32501 | 121.5225 | -0.064087 | -0.16937 | -0.032043 | -0.12817 | 0.018311 | -0.27008 | 0.2243 | 0.10986 | 0.068665 | 0.23804 | 0.19684 | -0.073242 | -0.10986 | -0.16022 | 0.18768 | 0.21973 | 0.082397 | 0.29297 | 0.15564 | 0.35248 | 121.7926 | 0.26093 | 121.8475 | 122.081 | 121.8979 | 121.9528 | 121.8246 | -122.0627 | -122.0078 | 121.6644 | 121.7743 | 0.47607 | 0.51727
914.8281 | 121.9208 | -0.28381 | 121.7102 | 0.051346 | 0.0073037 | 0.070207 | 0.065657 | 0.00091214 | -0.0031574 | -0.0012434 | 0.014008 | 0.0058683 | 0.07041 | 0.059178 | 0.00012397 | 0.017786 | -0.0025742 | 0.17853 | 121.7926 | -0.41199 | 121.3943 | -0.086975 | -0.19684 | -0.17395 | 0.19684 | 121.6553 | -0.35248 | 121.5179 | -0.086975 | -0.19684 | -0.027466 | -0.12817 | 0.082398 | -0.31586 | 0.19684 | 0.10986 | 0.086975 | 0.23804 | 0.21515 | -0.068665 | -0.054932 | -0.19226 | 0.19684 | 0.25635 | 0.086975 | 0.32501 | 0.15564 | 0.32501 | 121.8063 | 0.2655 | 121.8704 | 122.2046 | 122.0078 | 122.0764 | 121.9391 | -122.1222 | -122.0627 | 121.6782 | 121.8018 | 0.46234 | 0.48065
916.5312 | 121.8979 | -0.2655 | 121.7148 | -0.0020601 | 0.0060221 | 0.068498 | 0.066939 | 0.00069854 | -0.0020892 | 0.00046565 | -0.0012513 | 0.0043729 | 0.068274 | 0.058537 | 0.0016194 | 0.017359 | -0.0053512 | 0.17395 | 121.8246 | -0.37079 | 121.4218 | -0.07782 | -0.22888 | -0.20599 | 0.17853 | 121.6095 | -0.33875 | 121.5408 | -0.11902 | -0.23346 | -0.068665 | -0.10529 | 0.10986 | -0.29297 | 0.18768 | 0.059509 | 0.036621 | 0.16479 | 0.14191 | -0.073242 | -0.10529 | -0.17395 | 0.14648 | 0.19684 | 0.032044 | 0.27008 | 0.10529 | 0.29297 | 121.7926 | 0.21973 | 121.8796 | 122.1954 | 121.9482 | 122.0901 | 121.875 | -122.0856 | -122.0535 | 121.6873 | 121.8063 | 0.43945 | 0.44403
918.2812 | 121.9894 | -0.25177 | 121.6965 | 0.043716 | 0.0062357 | 0.070421 | 0.064375 | 0.0034755 | -0.00016658 | -0.00017515 | 0.020111 | 0.0039457 | 0.071051 | 0.065587 | 0.00033757 | 0.014795 | -0.0002244 | 0.1236 | 121.8201 | -0.36621 | 121.5134 | 0.013733 | -0.14648 | -0.10986 | 0.20142 | 121.6141 | -0.32959 | 121.6049 | -0.036621 | -0.1236 | -0.018311 | -0.11444 | 0.1236 | -0.1831 | 0.2655 | 0.14191 | 0.10529 | 0.25635 | 0.21973 | -0.07782 | -0.082397 | -0.091553 | 0.21515 | 0.23346 | 0.12817 | 0.31128 | 0.20599 | 0.37994 | 121.8796 | 0.29297 | 121.9345 | 122.1863 | 121.9437 | 122.0718 | 121.8658 | -122.0627 | -122.0261 | 121.7651 | 121.8567 | 0.37537 | 0.45319
920.0156 | 122.049 | -0.27008 | 121.7102 | 0.020828 | 0.0049539 | 0.069566 | 0.064589 | -0.0035739 | -0.00080758 | -0.0010298 | -0.0012513 | 0.0043729 | 0.068701 | 0.065159 | -0.001585 | 0.016932 | -0.0017196 | 0.073242 | 121.8109 | -0.37537 | 121.4859 | -0.054932 | -0.16479 | -0.13733 | 0.16022 | 121.6415 | -0.32959 | 121.6187 | -0.018311 | -0.082397 | 0.009155 | -0.10528 | 0.10071 | -0.2243 | 0.21515 | 0.13275 | 0.10529 | 0.23804 | 0.21057 | -0.059509 | -0.068664 | -0.091553 | 0.25177 | 0.27924 | 0.18768 | 0.33875 | 0.24719 | 0.32043 | 121.8613 | 0.31128 | 121.9482 | 122.1863 | 121.9711 | 122.081 | 121.9116 | -122.0856 | -122.0398 | 121.756 | 121.8887 | 0.34332 | 0.4303
921.7188 | 122.0306 | -0.26093 | 121.7239 | 0.0055694 | 0.0066629 | 0.068712 | 0.062453 | 0.00091214 | -0.0010212 | -0.00038875 | 0.0048523 | 0.0045865 | 0.070837 | 0.069004 | 0.00055117 | 0.0133 | -0.0002244 | 0.068665 | 121.843 | -0.37537 | 121.4996 | -0.064087 | -0.19684 | -0.15106 | 0.14191 | 121.669 | -0.32959 | 121.6141 | -0.054932 | -0.14648 | -0.032043 | -0.11444 | 0.11902 | -0.2243 | 0.19684 | 0.10986 | 0.064087 | 0.2243 | 0.17853 | -0.068665 | -0.054932 | -0.10986 | 0.20599 | 0.22888 | 0.11444 | 0.29755 | 0.18311 | 0.31128 | 121.875 | 0.27466 | 121.9437 | 122.2183 | 121.9986 | 122.1039 | 121.9299 | -122.0993 | -122.0535 | 121.7606 | 121.875 | 0.32959 | 0.40283
923.4531 | 122.049 | -0.25177 | 121.7651 | 0.013199 | 0.0077311 | 0.070634 | 0.065016 | -0.00036966 | -0.0027302 | -0.0012434 | 0.0048523 | 0.0062955 | 0.069128 | 0.061314 | -8.9634e-05 | 0.016504 | -0.0030014 | 0.086975 | 121.8292 | -0.36163 | 121.5134 | -0.054932 | -0.19684 | -0.14191 | 0.13275 | 121.6736 | -0.33875 | 121.6278 | -0.054932 | -0.14648 | -0.022888 | -0.10986 | 0.064087 | -0.25177 | 0.19684 | 0.10986 | 0.054932 | 0.21973 | 0.16479 | -0.086975 | -0.091553 | -0.13733 | 0.19684 | 0.22888 | 0.10529 | 0.31586 | 0.19226 | 0.3067 | 121.875 | 0.28381 | 121.9666 | 122.1909 | 122.0123 | 122.081 | 121.9254 | -122.1268 | -122.1039 | 121.7651 | 121.8796 | 0.33874 | 0.38452
925.2031 | 121.9803 | -0.27924 | 121.7697 | 0.013199 | 0.0053811 | 0.069566 | 0.068221 | -0.0035739 | -0.0046528 | -0.00081595 | 0.0018005 | 0.0065091 | 0.068701 | 0.060246 | -8.9634e-05 | 0.01565 | -0.0010788 | 0.07782 | 121.8887 | -0.38452 | 121.4584 | -0.13275 | -0.28839 | -0.21973 | 0.086975 | 121.7422 | -0.35248 | 121.5866 | -0.13733 | -0.23346 | -0.07782 | -0.10529 | 0.11902 | -0.31128 | 0.14648 | 0.059509 | -0.009155 | 0.16479 | 0.09613 | -0.073242 | -0.027465 | -0.1831 | 0.14191 | 0.20142 | 0.045777 | 0.27466 | 0.11902 | 0.25177 | 121.843 | 0.21515 | 121.9391 | 122.2733 | 122.0947 | 122.168 | 122.0215 | -122.1542 | -122.1222 | 121.7377 | 121.8658 | 0.35706 | 0.36621
926.9531 | 122.1085 | -0.22888 | 121.7743 | 0.013199 | 0.0058083 | 0.068925 | 0.064589 | -0.0018649 | -0.0048664 | 0.0011066 | 0.0018005 | 0.0041593 | 0.068488 | 0.070073 | -0.001585 | 0.014795 | -0.0025742 | 0.11902 | 121.8246 | -0.35706 | 121.6095 | 0.041199 | -0.10529 | -0.091553 | 0.23346 | 121.6919 | -0.30212 | 121.7148 | 0.022888 | -0.059509 | 0.013733 | -0.12817 | 0.050354 | -0.16479 | 0.27008 | 0.13733 | 0.1236 | 0.2655 | 0.25177 | -0.073242 | -0.082397 | -0.059509 | 0.25177 | 0.24261 | 0.16937 | 0.31586 | 0.24261 | 0.39825 | 121.9666 | 0.32501 | 122.0169 | 122.1817 | 121.994 | 122.0535 | 121.9208 | -122.1313 | -122.0764 | 121.8384 | 121.9437 | 0.3479 | 0.46234
928.6406 | 121.9803 | -0.28381 | 121.8155 | 0.0055694 | 0.0070901 | 0.068712 | 0.068221 | 0.0011257 | -0.0029438 | -0.0033796 | 0.0018005 | 0.0071499 | 0.066992 | 0.061955 | 0.00055117 | 0.014368 | -0.0017196 | 0.1236 | 121.907 | -0.37994 | 121.4951 | -0.1236 | -0.27466 | -0.22888 | 0.11902 | 121.756 | -0.36621 | 121.6095 | -0.14191 | -0.23804 | -0.091553 | -0.096131 | 0.091552 | -0.32043 | 0.16022 | 0.054931 | 0.009155 | 0.15106 | 0.10529 | -0.082398 | -0.05951 | -0.20599 | 0.14191 | 0.19226 | 0.045776 | 0.27466 | 0.12817 | 0.25635 | 121.875 | 0.2243 | 121.9757 | 122.287 | 122.1222 | 122.1909 | 122.0398 | -122.1954 | -122.1817 | 121.7789 | 121.8933 | 0.40741 | 0.40283
930.3906 | 122.0169 | -0.28381 | 121.8201 | 0.051346 | 0.0043131 | 0.071275 | 0.067793 | -0.0027195 | -0.0035846 | 0.00067925 | 0.0079041 | 0.0077909 | 0.069556 | 0.057469 | -0.0035076 | 0.016932 | -0.0034286 | 0.10986 | 121.9391 | -0.4303 | 121.4996 | -0.091553 | -0.20599 | -0.20142 | 0.1236 | 121.8063 | -0.36621 | 121.6049 | -0.12817 | -0.21057 | -0.07782 | -0.14649 | 0.11902 | -0.32043 | 0.19226 | 0.082397 | 0.077819 | 0.22888 | 0.2243 | -0.082398 | -0.013733 | -0.21515 | 0.15564 | 0.20599 | 0.073242 | 0.28839 | 0.15564 | 0.33875 | 121.9299 | 0.23804 | 121.9711 | 122.3694 | 122.1725 | 122.2229 | 122.0901 | -122.2504 | -122.1863 | 121.7834 | 121.8887 | 0.39368 | 0.40741
932.1562 | 122.0123 | -0.27466 | 121.8384 | -0.0020601 | 0.0070901 | 0.071916 | 0.06758 | 0.0011257 | -0.00508 | -0.0020978 | -0.0012513 | 0.0062955 | 0.069128 | 0.064305 | 0.0014056 | 0.013727 | -0.0010788 | 0.10986 | 121.9482 | -0.38452 | 121.5042 | -0.11444 | -0.26093 | -0.23804 | 0.10529 | 121.7468 | -0.35706 | 121.6049 | -0.13275 | -0.25177 | -0.082397 | -0.10986 | 0.10986 | -0.33417 | 0.16022 | 0.036621 | 0.013733 | 0.14648 | 0.1236 | -0.082398 | -0.091553 | -0.23346 | 0.14191 | 0.19226 | 0.022888 | 0.27466 | 0.10529 | 0.27008 | 121.8887 | 0.2243 | 121.962 | 122.3328 | 122.1039 | 122.2229 | 122.0215 | -122.2229 | -122.1954 | 121.7789 | 121.8796 | 0.38452 | 0.37994
933.8906 | 122.1268 | -0.24719 | 121.788 | 0.036087 | 0.0070901 | 0.071916 | 0.065871 | 0.0062527 | -0.003371 | 0.00089285 | 0.0018005 | 0.0062955 | 0.071051 | 0.069859 | 0.00097837 | 0.016932 | -0.0030014 | 0.11902 | 121.9025 | -0.35706 | 121.6324 | 0.032043 | -0.12817 | -0.10071 | 0.22888 | 121.7377 | -0.33875 | 121.7285 | -0.004578 | -0.11902 | 0.009155 | -0.10986 | 0.11444 | -0.15564 | 0.27924 | 0.14648 | 0.11902 | 0.25635 | 0.22888 | -0.091553 | -0.050354 | -0.059509 | 0.24261 | 0.25635 | 0.12817 | 0.3479 | 0.21973 | 0.3891 | 121.9894 | 0.33417 | 122.0673 | 122.2595 | 122.0764 | 122.1497 | 121.9849 | -122.1451 | -122.1268 | 121.8796 | 121.9757 | 0.36621 | 0.47607
935.5938 | 122.0032 | -0.29297 | 121.843 | -0.0020601 | 0.0077311 | 0.068498 | 0.065016 | 0.0019803 | -0.001662 | 3.8448e-05 | -0.0043029 | 0.0073635 | 0.072119 | 0.06345 | -0.0017986 | 0.015223 | -0.0087692 | 0.091553 | 121.9574 | -0.37079 | 121.5179 | -0.1236 | -0.2655 | -0.24261 | 0.082397 | 121.7926 | -0.32959 | 121.6187 | -0.15564 | -0.27008 | -0.091553 | -0.07782 | 0.11444 | -0.32501 | 0.16937 | 0.050354 | 0.027466 | 0.12817 | 0.10529 | -0.036621 | -0.050354 | -0.22431 | 0.13733 | 0.20142 | 0.022888 | 0.23804 | 0.059509 | 0.24719 | 121.8887 | 0.17395 | 121.9482 | 122.3282 | 122.1222 | 122.2504 | 122.0856 | -122.2137 | -122.1725 | 121.8109 | 121.9116 | 0.38452 | 0.37537
937.3438 | 122.0764 | -0.28381 | 121.8658 | 0.043716 | 0.0051675 | 0.069139 | 0.066512 | 0.0062527 | -0.0020892 | 0.00367 | 0.010956 | 0.0058683 | 0.071478 | 0.065373 | -0.0024396 | 0.014368 | -0.003215 | 0.14191 | 121.9711 | -0.41657 | 121.5637 | -0.086975 | -0.19226 | -0.16937 | 0.16937 | 121.7972 | -0.36621 | 121.669 | -0.082397 | -0.16937 | -0.059509 | -0.13275 | 0.10529 | -0.30212 | 0.19684 | 0.11444 | 0.091552 | 0.24719 | 0.2243 | -0.082398 | -0.068665 | -0.19684 | 0.20142 | 0.2243 | 0.11444 | 0.3067 | 0.19684 | 0.32959 | 121.9803 | 0.28381 | 122.0352 | 122.3877 | 122.1634 | 122.2549 | 122.081 | -122.2824 | -122.2321 | 121.8475 | 121.9528 | 0.42572 | 0.45319
939.0781 | 122.049 | -0.31128 | 121.8384 | -0.0020601 | 0.0043131 | 0.069994 | 0.066298 | 0.0066799 | -0.0046528 | 0.00046565 | -0.0012513 | 0.0054409 | 0.070196 | 0.070286 | -8.9634e-05 | 0.01565 | -0.0036422 | 0.073242 | 121.9803 | -0.39825 | 121.4996 | -0.17395 | -0.29297 | -0.26093 | 0.064087 | 121.7972 | -0.3479 | 121.6232 | -0.15106 | -0.25177 | -0.086975 | -0.086975 | 0.14191 | -0.33875 | 0.13733 | 0.050354 | 0.01831 | 0.13733 | 0.10529 | -0.036621 | -0.041199 | -0.21515 | 0.16022 | 0.2243 | 0.059509 | 0.26092 | 0.09613 | 0.2243 | 121.8979 | 0.19684 | 121.9711 | 122.3785 | 122.1451 | 122.2916 | 122.1085 | -122.2366 | -122.1863 | 121.8109 | 121.9345 | 0.38452 | 0.37537
940.8281 | 122.0306 | -0.3067 | 121.8246 | -0.0096891 | 0.0070901 | 0.070421 | 0.065016 | 0.0043301 | -0.0037982 | 0.0023882 | -0.0073547 | 0.0056545 | 0.069769 | 0.063023 | -0.00051703 | 0.016291 | -0.0019332 | 0.050354 | 121.9711 | -0.42114 | 121.4951 | -0.1831 | -0.31586 | -0.27924 | 0.045776 | 121.7926 | -0.37079 | 121.5958 | -0.18768 | -0.27466 | -0.11902 | -0.11444 | 0.14648 | -0.32959 | 0.1236 | 0.027466 | -0.009155 | 0.14191 | 0.10529 | -0.064087 | -0.032043 | -0.22888 | 0.11902 | 0.18768 | 0.032044 | 0.25177 | 0.096131 | 0.23804 | 121.9162 | 0.18311 | 121.9666 | 122.3923 | 122.1634 | 122.2778 | 122.0993 | -122.2458 | -122.1954 | 121.8018 | 121.9025 | 0.35706 | 0.35248
942.5156 | 122.049 | -0.32044 | 121.8384 | 0.013199 | 0.0049539 | 0.069139 | 0.063521 | -0.0010105 | -0.0035846 | -0.00081595 | -0.0043029 | 0.0045865 | 0.068274 | 0.064091 | -0.003294 | 0.01565 | -0.0008652 | 0.10986 | 121.9254 | -0.3891 | 121.5042 | -0.10986 | -0.24719 | -0.20142 | 0.12817 | 121.7743 | -0.37537 | 121.6187 | -0.15106 | -0.23346 | -0.13733 | -0.068664 | 0.086975 | -0.33417 | 0.21057 | 0.11902 | 0.073243 | 0.18768 | 0.14191 | -0.054931 | -0.064087 | -0.21973 | 0.16937 | 0.18311 | 0.086976 | 0.23804 | 0.14191 | 0.27924 | 121.8933 | 0.2243 | 121.994 | 122.3145 | 122.1497 | 122.2458 | 122.0947 | -122.2275 | -122.2137 | 121.8246 | 121.9391 | 0.4303 | 0.44861
944.2656 | 122.0764 | -0.31128 | 121.8384 | -0.0020601 | 0.0058083 | 0.069566 | 0.06523 | 0.00069854 | -0.003371 | -0.0018842 | -0.0073547 | 0.0058683 | 0.071692 | 0.060887 | 0.001192 | 0.016718 | 0.0021256 | 0.064087 | 121.9574 | -0.42114 | 121.4859 | -0.1831 | -0.32501 | -0.26093 | 0.068665 | 121.7926 | -0.38452 | 121.6324 | -0.16937 | -0.27924 | -0.10986 | -0.10986 | 0.11902 | -0.35248 | 0.12817 | 0.050354 | -0.013733 | 0.16022 | 0.096131 | -0.073242 | -0.045776 | -0.20599 | 0.14191 | 0.20142 | 0.032043 | 0.27466 | 0.10529 | 0.23804 | 121.907 | 0.21515 | 122.0169 | 122.3785 | 122.1771 | 122.2687 | 122.1039 | -122.2595 | -122.2229 | 121.7972 | 121.9437 | 0.37537 | 0.37994
946.0156 | 122.1405 | -0.28839 | 121.8063 | 0.028458 | 0.0064493 | 0.070634 | 0.066298 | 0.0021939 | -0.0010212 | -0.0010298 | 0.0079041 | 0.0060819 | 0.071051 | 0.068577 | 0.00055117 | 0.017145 | -0.001506 | 0.059509 | 121.9208 | -0.41199 | 121.5775 | -0.068665 | -0.20599 | -0.1831 | 0.14191 | 121.756 | -0.3891 | 121.6919 | -0.10986 | -0.20142 | -0.07782 | -0.1236 | 0.11444 | -0.22888 | 0.21973 | 0.10529 | 0.082397 | 0.22888 | 0.20599 | -0.10071 | -0.050354 | -0.11444 | 0.17853 | 0.21057 | 0.086975 | 0.31128 | 0.18768 | 0.34332 | 121.9894 | 0.27924 | 122.081 | 122.3328 | 122.1451 | 122.2092 | 122.0444 | -122.2183 | -122.1954 | 121.8658 | 121.9803 | 0.3479 | 0.4303
947.7031 | 122.2183 | -0.30212 | 121.7651 | 0.0055694 | 0.0058083 | 0.068498 | 0.064803 | 0.00069854 | -0.0023028 | 0.00089285 | -0.0043029 | 0.0043729 | 0.071478 | 0.063878 | -0.0035076 | 0.013727 | -0.003215 | 0.09613 | 121.8796 | -0.41657 | 121.6187 | 0 | -0.15106 | -0.13275 | 0.2655 | 121.7285 | -0.35706 | 121.7422 | -0.032043 | -0.12817 | -0.045776 | -0.11444 | 0.11444 | -0.14648 | 0.30212 | 0.16937 | 0.15106 | 0.28381 | 0.2655 | -0.054932 | -0.036621 | -0.022888 | 0.27008 | 0.25635 | 0.17395 | 0.31128 | 0.22888 | 0.41657 | 122.0352 | 0.32501 | 122.0993 | 122.2961 | 122.0856 | 122.1817 | 122.0306 | -122.1817 | -122.1222 | 121.9208 | 122.0444 | 0.39825 | 0.56763
949.4531 | 122.0535 | -0.35248 | 121.8475 | 0.0055694 | 0.0079447 | 0.071062 | 0.066298 | 0.0041165 | -0.0029438 | -0.0023114 | 0.0018005 | 0.0067227 | 0.071265 | 0.061955 | -8.9634e-05 | 0.017573 | -0.0012924 | 0.086975 | 121.9574 | -0.43945 | 121.4996 | -0.19684 | -0.32501 | -0.32501 | 0.068665 | 121.788 | -0.39368 | 121.6003 | -0.21973 | -0.31128 | -0.14648 | -0.086975 | 0.10986 | -0.3479 | 0.15564 | 0.027466 | 0.027466 | 0.11444 | 0.11444 | -0.041199 | -0.059509 | -0.24719 | 0.13275 | 0.20599 | 0.041199 | 0.24719 | 0.082398 | 0.24261 | 121.9391 | 0.17395 | 121.994 | 122.3969 | 122.1817 | 122.3099 | 122.1405 | -122.287 | -122.2412 | 121.8521 | 121.9528 | 0.43945 | 0.42114
951.2031 | 122.168 | -0.3067 | 121.8475 | -0.0096891 | 0.0060221 | 0.067644 | 0.062453 | 0.0026211 | 4.7018e-05 | 0.00025205 | -0.0012513 | 0.0024503 | 0.067419 | 0.062809 | -0.0026532 | 0.013514 | -0.0030014 | 0.12817 | 121.9025 | -0.39825 | 121.6003 | -0.041199 | -0.17853 | -0.16937 | 0.19684 | 121.756 | -0.35706 | 121.7056 | -0.073242 | -0.15564 | -0.073242 | -0.091552 | 0.054932 | -0.24719 | 0.2655 | 0.13733 | 0.12817 | 0.22888 | 0.21973 | -0.050354 | -0.091553 | -0.14191 | 0.23346 | 0.23346 | 0.15106 | 0.28381 | 0.20142 | 0.35706 | 121.9986 | 0.28381 | 122.0627 | 122.3007 | 122.113 | 122.2092 | 122.0627 | -122.2458 | -122.2046 | 121.907 | 122.0123 | 0.43488 | 0.50354
952.9531 | 122.2137 | -0.31128 | 121.7972 | -0.0020601 | 0.0034585 | 0.069353 | 0.063094 | -0.0020787 | -0.0029438 | 3.8448e-05 | 0.0018005 | 0.0045865 | 0.068701 | 0.066227 | 0.001833 | 0.015223 | -0.002147 | 0.050354 | 121.9208 | -0.42114 | 121.5683 | -0.086975 | -0.2243 | -0.18768 | 0.13733 | 121.7651 | -0.37994 | 121.7331 | -0.082397 | -0.14648 | -0.054932 | -0.10986 | 0.1236 | -0.22888 | 0.2243 | 0.1236 | 0.086975 | 0.23346 | 0.19684 | -0.068665 | -0.032043 | -0.064087 | 0.22888 | 0.25635 | 0.16479 | 0.32501 | 0.23346 | 0.33417 | 121.9894 | 0.29755 | 122.113 | 122.3419 | 122.1451 | 122.2321 | 122.0764 | -122.2183 | -122.1771 | 121.8796 | 122.0444 | 0.36163 | 0.44861
954.6406 | 122.1497 | -0.32501 | 121.8292 | 0.028458 | 0.0079447 | 0.071703 | 0.066084 | 0.00091214 | -0.00080758 | -0.0029524 | 0.0079041 | 0.0077909 | 0.070624 | 0.0611 | 0.001192 | 0.015223 | -1.0598e-05 | 0.16479 | 121.9528 | -0.46692 | 121.5683 | -0.1236 | -0.24261 | -0.23804 | 0.21057 | 121.8018 | -0.39368 | 121.669 | -0.13275 | -0.2243 | -0.10071 | -0.14191 | 0.1236 | -0.26093 | 0.20142 | 0.086975 | 0.082397 | 0.22888 | 0.2243 | -0.068665 | -0.027466 | -0.16022 | 0.19226 | 0.2243 | 0.10071 | 0.29297 | 0.16937 | 0.34332 | 122.0352 | 0.26093 | 122.0627 | 122.4197 | 122.1954 | 122.2778 | 122.1268 | -122.2961 | -122.2229 | 121.8933 | 121.994 | 0.48981 | 0.53558
956.4062 | 122.1451 | -0.34332 | 121.8567 | 0.028458 | 0.0064493 | 0.068925 | 0.067793 | 0.0013393 | -0.00080758 | -0.00038875 | 0.010956 | 0.0088589 | 0.07041 | 0.06046 | -0.00051703 | 0.017145 | -0.002147 | 0.15106 | 122.0261 | -0.45776 | 121.5775 | -0.1236 | -0.25177 | -0.23346 | 0.20599 | 121.8155 | -0.40283 | 121.6873 | -0.13733 | -0.23804 | -0.10071 | -0.11444 | 0.16937 | -0.27923 | 0.21973 | 0.10986 | 0.091553 | 0.22431 | 0.20599 | -0.059509 | -0.041198 | -0.16937 | 0.20599 | 0.24261 | 0.10529 | 0.30212 | 0.1648 | 0.33417 | 122.0352 | 0.2655 | 122.0901 | 122.4838 | 122.2183 | 122.3694 | 122.1588 | -122.3145 | -122.2595 | 121.9208 | 122.0306 | 0.49438 | 0.54932
958.1562 | 122.2275 | -0.31128 | 121.8338 | 0.0055694 | 0.0043131 | 0.066576 | 0.064589 | -0.0031467 | -0.001662 | -0.0020978 | -0.0043029 | 0.0041593 | 0.067847 | 0.058537 | -0.001585 | 0.016932 | -0.003215 | 0.086975 | 121.9345 | -0.40283 | 121.6324 | -0.032043 | -0.16937 | -0.15106 | 0.2243 | 121.7743 | -0.37537 | 121.7514 | -0.036621 | -0.13275 | -0.036621 | -0.091553 | 0.10071 | -0.20142 | 0.27924 | 0.16022 | 0.14191 | 0.25177 | 0.23346 | -0.064087 | -0.059509 | -0.082397 | 0.27466 | 0.27466 | 0.17853 | 0.33874 | 0.24261 | 0.37079 | 122.0352 | 0.33874 | 122.1268 | 122.3373 | 122.1497 | 122.2458 | 122.0856 | -122.2366 | -122.2092 | 121.9437 | 122.0627 | 0.39825 | 0.53558
959.8906 | 122.2229 | -0.29755 | 121.8292 | 0.066604 | 0.0087991 | 0.073412 | 0.068648 | 0.0051845 | 0.00090142 | -0.00060235 | 0.014008 | 0.0052273 | 0.070196 | 0.068364 | 0.00033757 | 0.015864 | -0.0019332 | 0.13275 | 121.9711 | -0.41199 | 121.6782 | -0.022888 | -0.1831 | -0.14648 | 0.22888 | 121.7743 | -0.39368 | 121.7606 | -0.059509 | -0.16937 | -0.050354 | -0.11444 | 0.14191 | -0.15106 | 0.27466 | 0.15106 | 0.11444 | 0.2655 | 0.22888 | -0.096131 | -0.054932 | -0.068665 | 0.23804 | 0.24719 | 0.12817 | 0.34332 | 0.2243 | 0.3891 | 122.0901 | 0.33417 | 122.1542 | 122.3831 | 122.168 | 122.2687 | 122.0718 | -122.2412 | -122.2229 | 121.9757 | 122.0581 | 0.4303 | 0.52643
961.6406 | 122.2275 | -0.3067 | 121.8613 | -0.0096891 | 0.0051675 | 0.069994 | 0.066512 | -0.0010105 | -0.001662 | -0.0016706 | -0.0012513 | 0.0071499 | 0.069769 | 0.065587 | -0.00030343 | 0.020136 | -0.0019332 | 0.073242 | 121.9711 | -0.40283 | 121.5912 | -0.13275 | -0.2655 | -0.22888 | 0.16022 | 121.7972 | -0.36621 | 121.7606 | -0.073242 | -0.17853 | -0.054932 | -0.09613 | 0.10986 | -0.27008 | 0.17395 | 0.07782 | 0.041199 | 0.17395 | 0.13733 | -0.059509 | -0.064087 | -0.10071 | 0.23346 | 0.25177 | 0.12817 | 0.31128 | 0.18768 | 0.27008 | 121.994 | 0.29297 | 122.1268 | 122.374 | 122.1634 | 122.2778 | 122.1039 | -122.2641 | -122.2275 | 121.8979 | 122.0673 | 0.37994 | 0.46692
963.3906 | 122.2321 | -0.30212 | 121.8384 | -0.017319 | 0.0047403 | 0.071275 | 0.064162 | 0.0043301 | -0.0040118 | -0.0012434 | -0.0012513 | 0.0052273 | 0.068488 | 0.062809 | -0.00030343 | 0.018213 | -0.0019332 | 0.10986 | 121.994 | -0.40283 | 121.637 | -0.07782 | -0.22888 | -0.20142 | 0.19684 | 121.7743 | -0.36163 | 121.7834 | -0.054932 | -0.16479 | -0.032043 | -0.10071 | 0.15564 | -0.20142 | 0.2243 | 0.10071 | 0.073242 | 0.20142 | 0.17395 | -0.059509 | -0.064087 | -0.054932 | 0.24719 | 0.27008 | 0.13733 | 0.32959 | 0.19684 | 0.32501 | 122.0398 | 0.3067 | 122.1451 | 122.3969 | 122.1359 | 122.2961 | 122.0764 | -122.2412 | -122.2 | 121.9391 | 122.0856 | 0.41199 | 0.49896
965.0781 | 122.1588 | -0.32044 | 121.8796 | 0.051346 | 0.0077311 | 0.070421 | 0.068434 | 0.0021939 | -0.0031574 | -0.00038875 | 0.014008 | 0.0075771 | 0.071905 | 0.058964 | -0.0041486 | 0.015223 | -0.0044968 | 0.11902 | 122.0261 | -0.46692 | 121.55 | -0.16022 | -0.27924 | -0.25177 | 0.11902 | 121.8796 | -0.41199 | 121.6827 | -0.17853 | -0.25177 | -0.13275 | -0.14648 | 0.14648 | -0.32959 | 0.16022 | 0.068665 | 0.041199 | 0.21515 | 0.18768 | -0.091552 | 0 | -0.19684 | 0.14191 | 0.18768 | 0.068665 | 0.27924 | 0.16022 | 0.3067 | 122.0169 | 0.23346 | 122.0947 | 122.493 | 122.2916 | 122.3465 | 122.2 | -122.3465 | -122.2916 | 121.8704 | 122.0032 | 0.43945 | 0.43945
966.8594 | 122.1359 | -0.34332 | 121.8704 | -0.0096891 | 0.0055947 | 0.06743 | 0.06288 | 0.0064663 | -0.0042254 | 0.00046565 | 0.0048523 | 0.0048001 | 0.068701 | 0.064732 | -0.0020122 | 0.014582 | -0.0034286 | 0.11902 | 121.9482 | -0.42114 | 121.6049 | -0.10071 | -0.21515 | -0.20599 | 0.14191 | 121.8246 | -0.39368 | 121.6782 | -0.15106 | -0.23346 | -0.13275 | -0.07782 | 0.07782 | -0.2655 | 0.24261 | 0.13733 | 0.12817 | 0.21515 | 0.20599 | -0.050354 | -0.045776 | -0.19226 | 0.19226 | 0.21057 | 0.10986 | 0.26093 | 0.16022 | 0.32043 | 122.0261 | 0.24261 | 122.0718 | 122.3694 | 122.2183 | 122.2916 | 122.168 | -122.2916 | -122.2641 | 121.9482 | 122.0215 | 0.46234 | 0.48523
968.5469 | 122.2595 | -0.30212 | 121.8521 | -0.0020601 | 0.0045267 | 0.069566 | 0.064589 | -0.0012241 | -0.0023028 | 0.00025205 | 0.0018005 | 0.0052273 | 0.067847 | 0.066655 | -0.0017986 | 0.015009 | -0.0012924 | 0.082397 | 121.9666 | -0.40283 | 121.6553 | -0.073242 | -0.19684 | -0.16937 | 0.16937 | 121.7789 | -0.36621 | 121.788 | -0.036621 | -0.12817 | -0.027466 | -0.10071 | 0.11444 | -0.19684 | 0.22888 | 0.13275 | 0.10529 | 0.23346 | 0.20599 | -0.064087 | -0.073242 | -0.064087 | 0.2655 | 0.27466 | 0.17395 | 0.33875 | 0.23804 | 0.32959 | 122.0581 | 0.32959 | 122.1542 | 122.3694 | 122.1451 | 122.2687 | 122.081 | -122.2549 | -122.2183 | 121.9574 | 122.0901 | 0.38452 | 0.4715
970.2969 | 122.1771 | -0.32044 | 121.9162 | 0.013199 | 0.0090127 | 0.071916 | 0.068221 | 0.0028347 | -0.0020892 | -0.0033796 | 0.0079041 | 0.0073635 | 0.068488 | 0.061314 | -0.00051703 | 0.014155 | -0.0025742 | 0.16022 | 122.0215 | -0.42572 | 121.6232 | -0.082397 | -0.24719 | -0.21515 | 0.19684 | 121.8475 | -0.37994 | 121.7239 | -0.13275 | -0.2243 | -0.10071 | -0.10528 | 0.10528 | -0.29297 | 0.23804 | 0.10529 | 0.073243 | 0.21057 | 0.17853 | -0.059509 | -0.068665 | -0.19226 | 0.18768 | 0.21973 | 0.096131 | 0.27924 | 0.15564 | 0.34332 | 122.049 | 0.24719 | 122.1039 | 122.4472 | 122.2275 | 122.3419 | 122.168 | -122.3419 | -122.2961 | 121.9437 | 122.0444 | 0.48065 | 0.51727
972.0469 | 122.1405 | -0.3479 | 121.9025 | 0.0055694 | 0.0043131 | 0.069139 | 0.063307 | 0.0024075 | -0.0057208 | 0.0013202 | 0.0018005 | 0.0056545 | 0.072333 | 0.058964 | -0.0035076 | 0.014582 | -0.0012924 | 0.09613 | 121.994 | -0.42114 | 121.5775 | -0.16022 | -0.2655 | -0.25177 | 0.10986 | 121.843 | -0.38452 | 121.6644 | -0.1831 | -0.27466 | -0.16937 | -0.073243 | 0.091553 | -0.32501 | 0.18768 | 0.09613 | 0.082397 | 0.16937 | 0.15564 | -0.036621 | -0.059509 | -0.23804 | 0.16479 | 0.17853 | 0.073242 | 0.21515 | 0.10986 | 0.26093 | 121.9986 | 0.20142 | 122.049 | 122.4152 | 122.2275 | 122.3419 | 122.1909 | -122.3236 | -122.287 | 121.9254 | 122.0123 | 0.44403 | 0.45776
973.8125 | 122.1954 | -0.33417 | 121.9208 | 0.043716 | 0.0090127 | 0.068498 | 0.066298 | 0.0053983 | -0.0020892 | -0.00038875 | 0.010956 | 0.0065091 | 0.06806 | 0.060032 | -0.00030343 | 0.014368 | -0.0040696 | 0.16022 | 122.0215 | -0.43945 | 121.6187 | -0.12817 | -0.23804 | -0.23346 | 0.1831 | 121.8567 | -0.39368 | 121.7285 | -0.12817 | -0.23804 | -0.09613 | -0.10529 | 0.10071 | -0.30212 | 0.20599 | 0.10071 | 0.09613 | 0.20599 | 0.20142 | -0.05951 | -0.064087 | -0.19226 | 0.20599 | 0.23804 | 0.09613 | 0.29755 | 0.15564 | 0.31128 | 122.0581 | 0.2655 | 122.1222 | 122.4609 | 122.2504 | 122.3557 | 122.1909 | -122.3602 | -122.3145 | 121.9528 | 122.0627 | 0.49438 | 0.51727
975.5156 | 122.287 | -0.29297 | 121.8658 | -0.0096891 | 0.0043131 | 0.070634 | 0.064589 | 0.0015529 | -0.001662 | -0.00017515 | 0.0018005 | 0.0041593 | 0.069342 | 0.060887 | -0.00094423 | 0.015223 | -0.0012924 | 0.09613 | 121.9711 | -0.40741 | 121.6736 | -0.032043 | -0.17395 | -0.15106 | 0.21973 | 121.7972 | -0.36621 | 121.8201 | -0.032043 | -0.10986 | -0.045776 | -0.11444 | 0.10529 | -0.19226 | 0.26093 | 0.14191 | 0.11902 | 0.25635 | 0.23346 | -0.073242 | -0.068665 | -0.045777 | 0.26093 | 0.24719 | 0.18311 | 0.32044 | 0.25635 | 0.37537 | 122.081 | 0.33417 | 122.1863 | 122.3785 | 122.1634 | 122.2641 | 122.0901 | -122.2733 | -122.2321 | 121.9666 | 122.113 | 0.3891 | 0.5127
977.2656 | 122.2641 | -0.29755 | 121.8704 | 0.0055694 | 0.0036721 | 0.068925 | 0.065657 | 0.0024075 | -0.0035846 | -0.0010298 | -0.0043029 | 0.0035183 | 0.067206 | 0.067723 | -0.0011578 | 0.014795 | -0.006633 | 0.1236 | 121.9666 | -0.39368 | 121.6827 | -0.013733 | -0.16937 | -0.15564 | 0.23804 | 121.8338 | -0.35248 | 121.7972 | -0.032043 | -0.13733 | -0.050354 | -0.096131 | 0.096131 | -0.18768 | 0.28381 | 0.14191 | 0.12817 | 0.23804 | 0.2243 | -0.054932 | -0.036621 | -0.073242 | 0.2655 | 0.24719 | 0.16022 | 0.30212 | 0.21515 | 0.37994 | 122.0764 | 0.32044 | 122.1497 | 122.3602 | 122.1863 | 122.2641 | 122.1313 | -122.2641 | -122.2229 | 121.9803 | 122.0947 | 0.42114 | 0.53558
979 | 122.168 | -0.34332 | 121.9162 | 0.058975 | 0.0090127 | 0.069994 | 0.065871 | 0.00027134 | -0.0037982 | 0.00046565 | 0.017059 | 0.0067227 | 0.069128 | 0.066227 | -0.0043622 | 0.015009 | 0.0008438 | 0.10071 | 122.0627 | -0.48065 | 121.5729 | -0.16937 | -0.27466 | -0.25635 | 0.13275 | 121.9025 | -0.42572 | 121.6736 | -0.19226 | -0.27466 | -0.15106 | -0.13733 | 0.14648 | -0.34332 | 0.17395 | 0.086975 | 0.068665 | 0.2243 | 0.20599 | -0.082397 | -0.013733 | -0.24262 | 0.15106 | 0.19226 | 0.068665 | 0.27466 | 0.15106 | 0.31128 | 122.0535 | 0.23346 | 122.0993 | 122.5433 | 122.3282 | 122.406 | 122.2458 | -122.3969 | -122.3419 | 121.9162 | 122.0169 | 0.44403 | 0.47607
980.6875 | 122.2687 | -0.29297 | 121.875 | -0.0096891 | 0.0055947 | 0.069139 | 0.06523 | 0.0030483 | 0.0019696 | -0.00081595 | 0.023163 | 0.0069363 | 0.069983 | 0.060887 | 0.0026874 | 0.016077 | 0.0006302 | 0.13275 | 122.0123 | -0.3891 | 121.7194 | -0.022888 | -0.1831 | -0.14191 | 0.23804 | 121.843 | -0.39368 | 121.8201 | -0.064087 | -0.15564 | -0.036621 | -0.09613 | 0.13733 | -0.15564 | 0.27008 | 0.15106 | 0.10986 | 0.24719 | 0.20599 | -0.10071 | -0.032043 | -0.054932 | 0.22888 | 0.25635 | 0.13733 | 0.35706 | 0.23804 | 0.36621 | 122.1085 | 0.32959 | 122.2137 | 122.4014 | 122.2366 | 122.3053 | 122.1359 | -122.2641 | -122.2687 | 122.0123 | 122.113 | 0.42572 | 0.53101
982.4531 | 122.3007 | -0.31128 | 121.8796 | 0.013199 | 0.0058083 | 0.069566 | 0.064803 | 0.00048494 | -0.0031574 | -0.0016706 | 0.0018005 | 0.0033047 | 0.068274 | 0.071568 | -0.0011578 | 0.017359 | 0.000203 | 0.10529 | 122.0123 | -0.40741 | 121.6736 | -0.041199 | -0.19684 | -0.16022 | 0.22888 | 121.843 | -0.35248 | 121.8384 | -0.022888 | -0.1236 | -0.045776 | -0.096131 | 0.13275 | -0.20599 | 0.27008 | 0.15106 | 0.11444 | 0.24719 | 0.21057 | -0.041199 | -0.036621 | -0.041199 | 0.28839 | 0.2655 | 0.18768 | 0.3067 | 0.22888 | 0.36621 | 122.081 | 0.32959 | 122.1909 | 122.4197 | 122.1954 | 122.3236 | 122.1542 | -122.287 | -122.2321 | 121.9849 | 122.1497 | 0.41656 | 0.54016
984.1875 | 122.1451 | -0.35248 | 121.9208 | -0.0096891 | 0.0055947 | 0.069566 | 0.068648 | 0.0011257 | -0.00059378 | 0.00067925 | -0.0012513 | 0.0071499 | 0.069556 | 0.05811 | -0.00051703 | 0.014582 | 0.0006302 | 0.1236 | 122.0352 | -0.41657 | 121.5912 | -0.1831 | -0.31586 | -0.27924 | 0.11902 | 121.8933 | -0.3891 | 121.7056 | -0.20142 | -0.31128 | -0.14191 | -0.064087 | 0.11444 | -0.32959 | 0.16937 | 0.073242 | 0.036621 | 0.13733 | 0.10071 | -0.036621 | -0.027465 | -0.21515 | 0.15106 | 0.21057 | 0.041199 | 0.24719 | 0.07782 | 0.23346 | 122.0078 | 0.18768 | 122.0947 | 122.4518 | 122.2824 | 122.3877 | 122.2458 | -122.3373 | -122.3099 | 121.9437 | 122.0581 | 0.47607 | 0.4715
985.9375 | 122.2046 | -0.34332 | 121.9162 | 0.0055694 | 0.0030313 | 0.070848 | 0.065871 | 0.0017667 | -0.00080758 | -0.0016706 | -0.0012513 | 0.0062955 | 0.072119 | 0.062596 | 0.00076477 | 0.017786 | -0.0012924 | 0.059509 | 122.0627 | -0.42572 | 121.5591 | -0.18768 | -0.32959 | -0.29755 | 0.09613 | 121.8887 | -0.40283 | 121.7377 | -0.16022 | -0.25635 | -0.1236 | -0.082397 | 0.14648 | -0.35706 | 0.15564 | 0.045777 | 0.013733 | 0.12817 | 0.09613 | -0.059509 | -0.027466 | -0.17853 | 0.18311 | 0.21973 | 0.086975 | 0.27924 | 0.14648 | 0.23804 | 121.9849 | 0.24262 | 122.1405 | 122.4884 | 122.2916 | 122.406 | 122.2321 | -122.3419 | -122.319 | 121.9025 | 122.081 | 0.40283 | 0.43945
987.6406 | 122.287 | -0.28839 | 121.8796 | 0.013199 | 0.0055947 | 0.068498 | 0.065871 | -0.0012241 | -0.0031574 | 0.0013202 | -0.0073547 | 0.0033047 | 0.067419 | 0.060673 | 0.0033282 | 0.017786 | -0.0012924 | 0.10529 | 122.0215 | -0.41199 | 121.6736 | -0.082397 | -0.23346 | -0.20142 | 0.20599 | 121.843 | -0.35706 | 121.8475 | -0.064087 | -0.16479 | -0.032043 | -0.1236 | 0.14191 | -0.20599 | 0.20599 | 0.086975 | 0.054932 | 0.21057 | 0.17853 | -0.068665 | -0.036621 | -0.032044 | 0.2243 | 0.25635 | 0.1236 | 0.32501 | 0.19226 | 0.32959 | 122.0856 | 0.29297 | 122.2046 | 122.4335 | 122.2 | 122.3099 | 122.1313 | -122.2916 | -122.2366 | 121.962 | 122.1359 | 0.39368 | 0.49439
989.4062 | 122.2137 | -0.33875 | 121.9116 | -0.0020601 | 0.0060221 | 0.067857 | 0.065657 | 0.00048494 | -0.0020892 | -0.0018842 | -0.0043029 | 0.0033047 | 0.071265 | 0.061314 | -0.00073063 | 0.018427 | 0.0010574 | 0.059509 | 122.0535 | -0.44403 | 121.5683 | -0.19684 | -0.3479 | -0.30212 | 0.086975 | 121.8796 | -0.37994 | 121.7422 | -0.18768 | -0.28381 | -0.1236 | -0.10529 | 0.14191 | -0.34332 | 0.14191 | 0.036621 | -0.009155 | 0.14191 | 0.096131 | -0.041199 | -0.032043 | -0.16937 | 0.15106 | 0.21515 | 0.054932 | 0.25635 | 0.096131 | 0.24719 | 122.0123 | 0.19226 | 122.1222 | 122.4976 | 122.2595 | 122.3923 | 122.2183 | -122.3557 | -122.2916 | 121.907 | 122.081 | 0.39825 | 0.42572
991.0938 | 122.2733 | -0.33875 | 121.8796 | -0.0020601 | 0.0051675 | 0.069566 | 0.06523 | 0.0017667 | -0.0029438 | -0.0020978 | -0.0043029 | 0.0037319 | 0.069983 | 0.060032 | -0.002226 | 0.015223 | 0.000203 | 0.13733 | 121.994 | -0.39825 | 121.6965 | -0.054932 | -0.19226 | -0.16022 | 0.2243 | 121.8063 | -0.34332 | 121.7972 | -0.059509 | -0.15564 | -0.073242 | -0.059509 | 0.11444 | -0.18311 | 0.28381 | 0.17853 | 0.14648 | 0.23804 | 0.20599 | -0.004578 | -0.073243 | -0.082398 | 0.27924 | 0.2655 | 0.18311 | 0.27008 | 0.18768 | 0.34332 | 122.0947 | 0.28381 | 122.1405 | 122.3923 | 122.1497 | 122.3328 | 122.1451 | -122.2778 | -122.2229 | 122.0352 | 122.1359 | 0.47607 | 0.56305
992.875 | 122.1542 | -0.35706 | 121.9345 | 0.0055694 | 0.0070901 | 0.068925 | 0.066298 | 0.0032619 | -0.003371 | -0.0020978 | 0.0018005 | 0.0058683 | 0.068701 | 0.061955 | -0.00051703 | 0.016932 | -0.001506 | 0.10071 | 122.0535 | -0.43488 | 121.5866 | -0.20142 | -0.34332 | -0.31586 | 0.082397 | 121.8796 | -0.41657 | 121.6919 | -0.2243 | -0.32959 | -0.16022 | -0.077819 | 0.11902 | -0.3479 | 0.15564 | 0.041199 | 0.013733 | 0.11902 | 0.091552 | -0.059509 | -0.054931 | -0.24261 | 0.13275 | 0.19684 | 0.027466 | 0.25635 | 0.086975 | 0.23346 | 122.0215 | 0.19226 | 122.1085 | 122.4884 | 122.2961 | 122.4106 | 122.2366 | -122.3694 | -122.3511 | 121.9437 | 122.049 | 0.45776 | 0.43945
994.5625 | 122.1909 | -0.36621 | 121.9208 | -0.0096891 | 0.0055947 | 0.06978 | 0.064803 | -0.00015586 | -0.0029438 | -0.00081595 | -0.0012513 | 0.0048001 | 0.071905 | 0.060673 | -0.0035076 | 0.01565 | -0.0040696 | 0.13733 | 122.0261 | -0.41199 | 121.6507 | -0.11902 | -0.24719 | -0.2243 | 0.13733 | 121.8567 | -0.39825 | 121.7239 | -0.16937 | -0.26093 | -0.14648 | -0.045776 | 0.10529 | -0.27008 | 0.24719 | 0.14191 | 0.11902 | 0.18768 | 0.16479 | -0.032043 | -0.064087 | -0.19684 | 0.19684 | 0.21973 | 0.10529 | 0.25177 | 0.13733 | 0.29297 | 122.0627 | 0.22888 | 122.1222 | 122.438 | 122.2549 | 122.3923 | 122.2229 | -122.3328 | -122.319 | 122.0169 | 122.0901 | 0.50354 | 0.50354
996.3281 | 122.3145 | -0.29755 | 121.8842 | -0.0020601 | 0.0040995 | 0.06978 | 0.064162 | 0.0013393 | -0.0027302 | -0.0010298 | -0.0043029 | 0.0050137 | 0.068488 | 0.069859 | 0.0031146 | 0.017145 | -0.0053512 | 0.11902 | 122.0169 | -0.3891 | 121.701 | -0.068665 | -0.23346 | -0.18768 | 0.23346 | 121.8933 | -0.39368 | 121.8475 | -0.073242 | -0.16479 | -0.041199 | -0.091553 | 0.13275 | -0.18311 | 0.22888 | 0.10986 | 0.064087 | 0.20142 | 0.15564 | -0.096131 | 0.009156 | -0.036621 | 0.2243 | 0.25635 | 0.13275 | 0.35248 | 0.22888 | 0.32043 | 122.0901 | 0.32044 | 122.2412 | 122.406 | 122.287 | 122.3145 | 122.1909 | -122.2733 | -122.2778 | 121.9986 | 122.1451 | 0.41656 | 0.531
998.0781 | 122.168 | -0.34332 | 121.9574 | 0.013199 | 0.0075173 | 0.069353 | 0.066725 | 0.0030483 | -0.0037982 | -0.003166 | -0.0012513 | 0.0065091 | 0.069769 | 0.064091 | -0.00030343 | 0.019068 | -0.0027878 | 0.082397 | 122.0535 | -0.43488 | 121.5866 | -0.21057 | -0.3479 | -0.32501 | 0.064087 | 121.907 | -0.3891 | 121.7102 | -0.23346 | -0.33875 | -0.16479 | -0.091552 | 0.096131 | -0.37079 | 0.13275 | 0.018311 | -0.004577 | 0.10986 | 0.086975 | -0.045776 | -0.050354 | -0.24719 | 0.10986 | 0.17853 | 0.004578 | 0.2243 | 0.050354 | 0.2243 | 122.0215 | 0.15564 | 122.0993 | 122.4884 | 122.2961 | 122.3969 | 122.2504 | -122.3923 | -122.3465 | 121.9299 | 122.0535 | 0.42572 | 0.40741
999.8438 | 122.287 | -0.3067 | 121.8933 | 0.036087 | 0.0075173 | 0.072984 | 0.066512 | 0.0026211 | -0.001662 | -0.00081595 | 0.020111 | 0.0058683 | 0.070837 | 0.072422 | 0.00097837 | 0.016291 | -0.0059922 | 0.11444 | 122.0352 | -0.40283 | 121.7194 | -0.036621 | -0.21057 | -0.17395 | 0.21057 | 121.8887 | -0.38452 | 121.8246 | -0.091553 | -0.17853 | -0.068665 | -0.09613 | 0.14191 | -0.17395 | 0.27008 | 0.13275 | 0.096131 | 0.22888 | 0.19226 | -0.077819 | -0.004578 | -0.068665 | 0.21515 | 0.23804 | 0.12817 | 0.31586 | 0.20599 | 0.36621 | 122.1222 | 0.29297 | 122.2092 | 122.438 | 122.2733 | 122.3419 | 122.1954 | -122.2961 | -122.2778 | 122.0261 | 122.1313 | 0.42114 | 0.51727
1001.5469 | 122.2961 | -0.33875 | 121.8979 | 0.020828 | 0.0011087 | 0.066576 | 0.063094 | -0.00036966 | -0.0048664 | 0.00089285 | 0.0048523 | 0.0033047 | 0.068274 | 0.070073 | -0.0026532 | 0.016077 | 0.001271 | 0.059509 | 122.0444 | -0.42114 | 121.637 | -0.1236 | -0.24719 | -0.21973 | 0.12817 | 121.8613 | -0.37994 | 121.8155 | -0.091553 | -0.20599 | -0.082397 | -0.082398 | 0.14648 | -0.26093 | 0.21515 | 0.11902 | 0.091553 | 0.20142 | 0.17395 | -0.041199 | -0.036621 | -0.082397 | 0.24719 | 0.25635 | 0.13275 | 0.29755 | 0.17395 | 0.29755 | 122.0581 | 0.28839 | 122.1954 | 122.4655 | 122.2412 | 122.3831 | 122.2 | -122.319 | -122.2778 | 121.9757 | 122.1542 | 0.39825 | 0.46692
1003.2344 | 122.3236 | -0.30212 | 121.8933 | 0.058975 | 0.0064493 | 0.071916 | 0.066725 | 0.0013393 | -0.0014484 | 0.00089285 | 0.023163 | 0.0052273 | 0.07041 | 0.061528 | 0.0048236 | 0.015436 | -0.0023606 | 0.14191 | 122.0627 | -0.43945 | 121.7331 | -0.018311 | -0.20599 | -0.16022 | 0.25177 | 121.8979 | -0.37537 | 121.8384 | -0.068665 | -0.1831 | -0.050354 | -0.13733 | 0.16937 | -0.16022 | 0.28381 | 0.14191 | 0.09613 | 0.27924 | 0.23346 | -0.073242 | 0.004577 | -0.054932 | 0.23346 | 0.25177 | 0.11902 | 0.32501 | 0.19226 | 0.42114 | 122.1725 | 0.3067 | 122.2137 | 122.5021 | 122.2733 | 122.3648 | 122.2 | -122.3328 | -122.2687 | 122.0352 | 122.1405 | 0.44403 | 0.55389
1004.9844 | 122.1909 | -0.35706 | 121.9345 | 0.0055694 | 0.0053811 | 0.069994 | 0.064375 | 0.0021939 | -0.0014484 | -0.0023114 | 0.0018005 | 0.0054409 | 0.069556 | 0.059178 | -0.005003 | 0.013514 | -0.0027878 | 0.091553 | 122.0627 | -0.41657 | 121.6324 | -0.16022 | -0.27466 | -0.26093 | 0.10986 | 121.9299 | -0.40283 | 121.7194 | -0.19226 | -0.27466 | -0.16022 | -0.059509 | 0.12817 | -0.30212 | 0.19684 | 0.096131 | 0.082398 | 0.15564 | 0.14191 | -0.045776 | -0.004577 | -0.21515 | 0.16479 | 0.19684 | 0.082398 | 0.24262 | 0.12817 | 0.25635 | 122.049 | 0.21057 | 122.1222 | 122.4792 | 122.3328 | 122.4197 | 122.287 | -122.3511 | -122.3373 | 121.9894 | 122.0764 | 0.44861 | 0.46692
1006.6719 | 122.3373 | -0.30212 | 121.9116 | -0.0096891 | 0.0034585 | 0.069353 | 0.064803 | -0.0010105 | -0.0040118 | 0.00089285 | -0.0012513 | 0.0030911 | 0.066992 | 0.06345 | -0.001585 | 0.015436 | -0.0017196 | 0.13275 | 122.0215 | -0.39825 | 121.756 | -0.022888 | -0.16937 | -0.15564 | 0.22888 | 121.8613 | -0.34332 | 121.8658 | -0.045776 | -0.13275 | -0.050354 | -0.09613 | 0.10986 | -0.15564 | 0.27924 | 0.14648 | 0.13275 | 0.24261 | 0.22888 | -0.041199 | -0.050354 | -0.045776 | 0.25635 | 0.25177 | 0.16937 | 0.29297 | 0.21057 | 0.37537 | 122.1542 | 0.29755 | 122.2092 | 122.4197 | 122.2046 | 122.3236 | 122.1634 | -122.3099 | -122.2549 | 122.0581 | 122.168 | 0.43488 | 0.53101
1008.4219 | 122.3099 | -0.31586 | 121.9345 | -0.0020601 | 0.0043131 | 0.068712 | 0.063948 | -0.0012241 | -0.0046528 | -0.002525 | -0.0012513 | 0.0052273 | 0.069128 | 0.063664 | -0.0030804 | 0.016077 | -0.003215 | 0.09613 | 122.049 | -0.39825 | 121.7422 | -0.036621 | -0.18768 | -0.16022 | 0.22888 | 121.8704 | -0.36621 | 121.8613 | -0.045776 | -0.13733 | -0.050354 | -0.082397 | 0.11444 | -0.19226 | 0.27924 | 0.15564 | 0.12817 | 0.23804 | 0.21057 | -0.050354 | -0.064087 | -0.073242 | 0.27008 | 0.2655 | 0.17853 | 0.31586 | 0.22888 | 0.36163 | 122.1405 | 0.32044 | 122.2275 | 122.4472 | 122.2366 | 122.3648 | 122.1863 | -122.3328 | -122.3007 | 122.0581 | 122.1771 | 0.41199 | 0.54474
1010.1094 | 122.3007 | -0.30212 | 121.9162 | 0.028458 | 0.0055947 | 0.070634 | 0.064162 | -0.0018649 | -0.0029438 | -0.0029524 | -0.0012513 | 0.0041593 | 0.07041 | 0.070073 | -8.9634e-05 | 0.014368 | -0.000438 | 0.059509 | 122.049 | -0.4303 | 121.6736 | -0.10529 | -0.23346 | -0.20599 | 0.13733 | 121.8842 | -0.36163 | 121.8063 | -0.09613 | -0.19684 | -0.073242 | -0.12817 | 0.13275 | -0.24262 | 0.19684 | 0.09613 | 0.068665 | 0.2243 | 0.19684 | -0.059509 | -0.032044 | -0.10986 | 0.20599 | 0.22888 | 0.10529 | 0.28839 | 0.16479 | 0.32501 | 122.1039 | 0.2655 | 122.168 | 122.4792 | 122.2458 | 122.3511 | 122.1863 | -122.3465 | -122.2778 | 121.9757 | 122.1085 | 0.36163 | 0.43945
1011.8594 | 122.2412 | -0.35248 | 121.9391 | 0.043716 | 0.0062357 | 0.069139 | 0.067793 | 0.0017667 | -0.00059378 | -0.0012434 | 0.020111 | 0.0080045 | 0.073614 | 0.064732 | -0.0017986 | 0.014582 | -0.0042832 | 0.12817 | 122.1039 | -0.4715 | 121.6599 | -0.16937 | -0.26093 | -0.24261 | 0.15106 | 121.9803 | -0.42114 | 121.7606 | -0.16022 | -0.27466 | -0.11902 | -0.11902 | 0.16479 | -0.27924 | 0.18311 | 0.10986 | 0.091553 | 0.22888 | 0.21057 | -0.068665 | 0.041199 | -0.17853 | 0.19226 | 0.23346 | 0.07782 | 0.30212 | 0.14648 | 0.30212 | 122.1313 | 0.26093 | 122.1817 | 122.5754 | 122.4014 | 122.4564 | 122.3328 | -122.4106 | -122.3602 | 122.0123 | 122.113 | 0.48065 | 0.50354
1013.5469 | 122.3099 | -0.33417 | 121.907 | 0.043716 | 0.0066629 | 0.071275 | 0.06523 | 0.0030483 | 4.7018e-05 | 0.00067925 | 0.017059 | 0.0065091 | 0.07041 | 0.061955 | 0.00033757 | 0.016504 | -0.0010788 | 0.12817 | 122.0901 | -0.40741 | 121.756 | -0.022888 | -0.20142 | -0.17395 | 0.2243 | 121.9391 | -0.37079 | 121.8521 | -0.07782 | -0.1831 | -0.068665 | -0.073243 | 0.18311 | -0.15106 | 0.31128 | 0.16022 | 0.13275 | 0.23346 | 0.20599 | -0.036622 | 0.032044 | -0.054931 | 0.25635 | 0.2655 | 0.15106 | 0.30212 | 0.18768 | 0.38452 | 122.1634 | 0.29297 | 122.2229 | 122.4976 | 122.3099 | 122.4243 | 122.2733 | -122.3145 | -122.2778 | 122.0901 | 122.1863 | 0.46234 | 0.55847
1015.2344 | 122.3145 | -0.3067 | 121.9299 | 0.051346 | 0.0060221 | 0.072343 | 0.065871 | 0.0030483 | -0.00016658 | -0.0018842 | 0.020111 | 0.0056545 | 0.069983 | 0.0658 | 0.00012397 | 0.017786 | -0.0017196 | 0.16022 | 122.0856 | -0.43945 | 121.7651 | -0.027466 | -0.18768 | -0.16479 | 0.2243 | 121.9025 | -0.37994 | 121.8658 | -0.082397 | -0.16937 | -0.050354 | -0.13275 | 0.15564 | -0.16479 | 0.27924 | 0.14191 | 0.11902 | 0.27466 | 0.25177 | -0.073242 | -0.027466 | -0.064087 | 0.2243 | 0.25635 | 0.13733 | 0.32959 | 0.21057 | 0.41199 | 122.2046 | 0.29755 | 122.2458 | 122.525 | 122.2824 | 122.3923 | 122.2092 | -122.3694 | -122.3099 | 122.0718 | 122.1725 | 0.46692 | 0.53101
1017 | 122.287 | -0.32501 | 121.962 | 0.036087 | 0.0062357 | 0.071062 | 0.06523 | 0.0021939 | -0.0025166 | -0.0010298 | 0.010956 | 0.0035183 | 0.070196 | 0.0658 | -0.001585 | 0.015864 | -0.0019332 | 0.068665 | 122.0856 | -0.41199 | 121.701 | -0.09613 | -0.2243 | -0.20599 | 0.13275 | 121.9162 | -0.40283 | 121.8109 | -0.11902 | -0.21515 | -0.09613 | -0.086975 | 0.1236 | -0.26093 | 0.22888 | 0.11902 | 0.10071 | 0.20599 | 0.18768 | -0.07782 | -0.045776 | -0.15106 | 0.20599 | 0.22888 | 0.10986 | 0.3067 | 0.18768 | 0.31586 | 122.113 | 0.28381 | 122.2137 | 122.4976 | 122.319 | 122.4106 | 122.2412 | -122.374 | -122.3648 | 122.0261 | 122.1359 | 0.39368 | 0.45776
1018.6875 | 122.319 | -0.32044 | 121.9116 | 0.0055694 | 0.0058083 | 0.070634 | 0.066298 | 0.0051845 | -0.00080758 | -0.0055158 | -0.0012513 | 0.0060819 | 0.068701 | 0.076695 | 0.00033757 | 0.017359 | -0.000438 | 0.1236 | 122.0718 | -0.3891 | 121.7285 | -0.054932 | -0.22888 | -0.1831 | 0.25177 | 121.9437 | -0.39825 | 121.8887 | -0.073242 | -0.16479 | -0.045776 | -0.068664 | 0.16022 | -0.1831 | 0.2655 | 0.13733 | 0.091553 | 0.20599 | 0.16022 | -0.077819 | 0.032044 | -0.022888 | 0.24719 | 0.27466 | 0.15564 | 0.35248 | 0.23346 | 0.33417 | 122.1176 | 0.32501 | 122.287 | 122.4609 | 122.3419 | 122.3923 | 122.2641 | -122.3007 | -122.3099 | 122.049 | 122.2092 | 0.44403 | 0.57221
1020.4375 | 122.2412 | -0.35248 | 121.9666 | 0.0055694 | 0.0051675 | 0.069353 | 0.067152 | 0.00069854 | -0.003371 | -0.0033796 | -0.0012513 | 0.0071499 | 0.067847 | 0.059391 | 0.00033757 | 0.018427 | -0.0034286 | 0.064087 | 122.1039 | -0.43488 | 121.6003 | -0.20142 | -0.3479 | -0.29755 | 0.10071 | 121.9162 | -0.39368 | 121.7789 | -0.20142 | -0.29297 | -0.14648 | -0.082397 | 0.13733 | -0.36621 | 0.15106 | 0.054932 | 0.004578 | 0.13733 | 0.086975 | -0.041199 | -0.050354 | -0.18768 | 0.15106 | 0.20599 | 0.059509 | 0.24719 | 0.10071 | 0.23346 | 122.0352 | 0.19226 | 122.1725 | 122.5388 | 122.3099 | 122.4564 | 122.2687 | -122.4014 | -122.3602 | 121.9528 | 122.1313 | 0.41657 | 0.45319
1022.1875 | 122.2321 | -0.35248 | 121.9574 | 0.013199 | 0.0066629 | 0.070207 | 0.064803 | -0.0010105 | -0.0029438 | 0.00046565 | -0.0012513 | 0.0052273 | 0.07041 | 0.061314 | -0.0062848 | 0.014795 | -0.0047104 | 0.13275 | 122.0673 | -0.42572 | 121.6644 | -0.13275 | -0.27008 | -0.25177 | 0.14191 | 121.9345 | -0.3891 | 121.7606 | -0.1831 | -0.26093 | -0.16022 | -0.073242 | 0.10986 | -0.29297 | 0.21973 | 0.10071 | 0.082397 | 0.17395 | 0.15564 | -0.036621 | -0.022888 | -0.19684 | 0.16937 | 0.19226 | 0.091553 | 0.22888 | 0.12817 | 0.29297 | 122.0901 | 0.20599 | 122.1497 | 122.493 | 122.3236 | 122.4197 | 122.287 | -122.3831 | -122.3465 | 122.0169 | 122.113 | 0.48523 | 0.49439
1023.9375 | 122.2183 | -0.36163 | 121.9299 | -0.0020601 | 0.0073037 | 0.069353 | 0.068648 | 0.0011257 | -0.0014484 | 0.00025205 | -0.0012513 | 0.0056545 | 0.071265 | 0.060887 | -0.00051703 | 0.014155 | -0.000438 | 0.13275 | 122.1085 | -0.4303 | 121.6415 | -0.16937 | -0.32044 | -0.28381 | 0.14191 | 121.9345 | -0.40283 | 121.756 | -0.20142 | -0.31586 | -0.16479 | -0.068665 | 0.17853 | -0.28839 | 0.19226 | 0.07782 | 0.041198 | 0.14649 | 0.10986 | -0.041199 | 0.004577 | -0.17395 | 0.16022 | 0.19684 | 0.045776 | 0.23804 | 0.086975 | 0.26093 | 122.0718 | 0.20142 | 122.1588 | 122.5388 | 122.3373 | 122.4701 | 122.2961 | -122.3602 | -122.3328 | 122.0032 | 122.1176 | 0.49438 | 0.50354
1025.625 | 122.3099 | -0.32501 | 121.9482 | -0.0020601 | 0.0058083 | 0.070421 | 0.063521 | 0.0026211 | -0.0023028 | 0.00025205 | -0.0012513 | 0.0050137 | 0.067633 | 0.061741 | -0.0030804 | 0.0133 | -0.0017196 | 0.13275 | 122.0535 | -0.40283 | 121.7422 | -0.064087 | -0.19226 | -0.1831 | 0.21515 | 121.9025 | -0.37994 | 121.8246 | -0.082397 | -0.1831 | -0.10071 | -0.07782 | 0.10529 | -0.20599 | 0.26093 | 0.14191 | 0.13275 | 0.21973 | 0.21057 | -0.054932 | -0.045776 | -0.1236 | 0.24262 | 0.2243 | 0.14191 | 0.27924 | 0.19684 | 0.33875 | 122.1451 | 0.29755 | 122.2046 | 122.4564 | 122.2824 | 122.3785 | 122.2275 | -122.3511 | -122.3282 | 122.0673 | 122.1497 | 0.45776 | 0.54016
1027.3906 | 122.2092 | -0.36621 | 121.962 | -0.0020601 | 0.0079447 | 0.069566 | 0.064162 | -0.0022923 | -0.0020892 | -0.003166 | -0.0073547 | 0.0077909 | 0.070837 | 0.057255 | -0.0017986 | 0.014582 | -0.0081284 | 0.10986 | 122.1039 | -0.44861 | 121.6187 | -0.21515 | -0.32501 | -0.32044 | 0.09613 | 121.9528 | -0.40283 | 121.7468 | -0.23346 | -0.33875 | -0.1831 | -0.082397 | 0.14191 | -0.34332 | 0.15106 | 0.045776 | 0.041199 | 0.12817 | 0.1236 | -0.036621 | -0.009155 | -0.21515 | 0.13275 | 0.18311 | 0.027466 | 0.21973 | 0.064087 | 0.23346 | 122.0673 | 0.16937 | 122.1497 | 122.5525 | 122.3557 | 122.4701 | 122.319 | -122.4106 | -122.3648 | 121.9849 | 122.113 | 0.47607 | 0.46234
1029.1406 | 122.3236 | -0.32959 | 121.9482 | -0.0020601 | 0.0051675 | 0.070634 | 0.062239 | 0.0028347 | -0.0029438 | 0.00046565 | -0.0012513 | 0.0035183 | 0.070837 | 0.063237 | 0.00076477 | 0.015436 | 0.0006302 | 0.059509 | 122.0764 | -0.43488 | 121.6827 | -0.1236 | -0.25177 | -0.22888 | 0.13275 | 121.8979 | -0.40283 | 121.8384 | -0.10529 | -0.19684 | -0.086975 | -0.10529 | 0.12817 | -0.2655 | 0.20599 | 0.10071 | 0.07782 | 0.20599 | 0.18311 | -0.073242 | -0.050354 | -0.10986 | 0.2243 | 0.24261 | 0.13275 | 0.31586 | 0.20599 | 0.31128 | 122.1176 | 0.29755 | 122.2412 | 122.5113 | 122.3007 | 122.406 | 122.2275 | -122.3831 | -122.3511 | 122.0123 | 122.168 | 0.3891 | 0.46234
1030.9062 | 122.3007 | -0.35248 | 121.9482 | 0.013199 | 0.0070901 | 0.06978 | 0.067366 | 0.0021939 | -0.0023028 | -0.0027386 | 0.010956 | 0.0080045 | 0.071692 | 0.057682 | -0.0017986 | 0.0133 | -0.003856 | 0.16022 | 122.113 | -0.44861 | 121.6873 | -0.1236 | -0.25635 | -0.23804 | 0.21973 | 121.9299 | -0.41199 | 121.8246 | -0.13733 | -0.23346 | -0.11444 | -0.09613 | 0.1648 | -0.26093 | 0.22888 | 0.11444 | 0.09613 | 0.21057 | 0.19226 | -0.059509 | -0.01831 | -0.1236 | 0.21515 | 0.23804 | 0.11902 | 0.29755 | 0.17853 | 0.32501 | 122.1359 | 0.27466 | 122.2366 | 122.5616 | 122.3419 | 122.4655 | 122.2824 | -122.3968 | -122.3602 | 122.0398 | 122.1771 | 0.5127 | 0.57221
1032.5938 | 122.2412 | -0.37537 | 121.994 | -0.0020601 | 0.0045267 | 0.068071 | 0.064375 | 0.00091214 | -0.001662 | 0.0015338 | 0.029266 | 0.0056545 | 0.073614 | 0.057042 | -0.0060712 | 0.014795 | -0.0036422 | 0.059509 | 122.1039 | -0.45319 | 121.6232 | -0.16937 | -0.27924 | -0.27008 | 0.13275 | 121.9757 | -0.4303 | 121.7422 | -0.21057 | -0.29755 | -0.17395 | -0.07782 | 0.10986 | -0.37079 | 0.20599 | 0.10528 | 0.09613 | 0.1831 | 0.17395 | -0.054932 | -0.018311 | -0.25177 | 0.16479 | 0.20142 | 0.07782 | 0.25635 | 0.13275 | 0.28381 | 122.0764 | 0.21973 | 122.1725 | 122.5571 | 122.406 | 122.4792 | 122.3511 | -122.4472 | -122.4243 | 121.9986 | 122.1176 | 0.43487 | 0.50812
1034.3438 | 122.3007 | -0.33417 | 121.9162 | 0.036087 | 0.0062357 | 0.070848 | 0.066512 | 0.0024075 | -0.0040118 | -0.00081595 | 0.010956 | 0.0045865 | 0.068274 | 0.06046 | -0.00051703 | 0.015864 | -0.0030014 | 0.086975 | 122.0947 | -0.4303 | 121.701 | -0.086975 | -0.24261 | -0.2243 | 0.15564 | 121.9254 | -0.3891 | 121.8292 | -0.1236 | -0.21515 | -0.11444 | -0.096131 | 0.17853 | -0.21515 | 0.24719 | 0.10986 | 0.091552 | 0.20599 | 0.18768 | -0.054932 | 0.009155 | -0.086975 | 0.21057 | 0.21973 | 0.11902 | 0.27466 | 0.17395 | 0.34332 | 122.1313 | 0.2655 | 122.2183 | 122.525 | 122.3145 | 122.4289 | 122.2595 | -122.3465 | -122.3053 | 122.0352 | 122.1634 | 0.42114 | 0.48981
1036.0938 | 122.2549 | -0.37537 | 121.9986 | 0.043716 | 0.0083719 | 0.06978 | 0.066939 | 0.00048494 | -0.00080758 | 0.0015338 | 0.010956 | 0.0067227 | 0.068701 | 0.056401 | -0.0030804 | 0.013727 | -0.0040696 | 0.1236 | 122.1359 | -0.49439 | 121.6187 | -0.20599 | -0.29755 | -0.28381 | 0.13275 | 121.962 | -0.43945 | 121.7606 | -0.18768 | -0.27924 | -0.15564 | -0.11902 | 0.13733 | -0.37994 | 0.16937 | 0.091553 | 0.07782 | 0.21057 | 0.19684 | -0.064087 | -0.036621 | -0.23804 | 0.18768 | 0.21973 | 0.09613 | 0.28381 | 0.16022 | 0.28839 | 122.113 | 0.25177 | 122.2 | 122.6303 | 122.4014 | 122.5113 | 122.3373 | -122.493 | -122.438 | 121.994 | 122.1359 | 0.49896 | 0.50812
1037.875 | 122.2412 | -0.37537 | 121.9437 | 0.0055694 | 0.0062357 | 0.069994 | 0.066725 | 0.0011257 | -0.001662 | -0.00081595 | -0.0073547 | 0.0048001 | 0.071265 | 0.063237 | 0.0016194 | 0.0133 | -1.0598e-05 | 0.086975 | 122.1176 | -0.47607 | 121.5958 | -0.25177 | -0.3891 | -0.34332 | 0.068665 | 121.962 | -0.41199 | 121.7651 | -0.23346 | -0.32959 | -0.16479 | -0.10071 | 0.17395 | -0.3479 | 0.1236 | 0.032043 | -0.013733 | 0.13275 | 0.086975 | -0.036621 | 0.01831 | -0.17853 | 0.14191 | 0.21057 | 0.045776 | 0.24719 | 0.082397 | 0.2243 | 122.0718 | 0.17853 | 122.1771 | 122.5937 | 122.374 | 122.493 | 122.3373 | -122.4197 | -122.3557 | 121.9711 | 122.1405 | 0.46234 | 0.44403
1039.5625 | 122.2504 | -0.39368 | 121.9803 | 0.0055694 | 0.0049539 | 0.067857 | 0.065443 | -0.0014377 | -0.0027302 | -0.0012434 | -0.0012513 | 0.0043729 | 0.070624 | 0.057042 | -0.0041486 | 0.014155 | -0.0010788 | 0.07782 | 122.1085 | -0.45319 | 121.6141 | -0.20142 | -0.32959 | -0.29755 | 0.10529 | 121.9528 | -0.41199 | 121.7377 | -0.20599 | -0.29755 | -0.1831 | -0.059509 | 0.12817 | -0.36621 | 0.19226 | 0.096131 | 0.064087 | 0.15564 | 0.1236 | -0.01831 | -0.027466 | -0.24262 | 0.18768 | 0.21057 | 0.096131 | 0.22888 | 0.11444 | 0.25177 | 122.0673 | 0.20599 | 122.1497 | 122.5616 | 122.3648 | 122.5021 | 122.3465 | -122.4335 | -122.3923 | 122.0078 | 122.1313 | 0.4715 | 0.49896
1041.3125 | 122.3831 | -0.33417 | 121.9528 | -0.0096891 | 0.0043131 | 0.06978 | 0.065657 | -0.00015586 | -0.003371 | 0.00089285 | -0.0012513 | 0.0022367 | 0.067633 | 0.069859 | 0.00033757 | 0.016504 | -0.0025742 | 0.13733 | 122.0535 | -0.40741 | 121.756 | -0.050354 | -0.19226 | -0.16937 | 0.24261 | 121.9025 | -0.37537 | 121.8887 | -0.041199 | -0.14191 | -0.068665 | -0.073243 | 0.10071 | -0.19684 | 0.28381 | 0.16479 | 0.14191 | 0.23804 | 0.21515 | -0.041199 | -0.050354 | -0.064087 | 0.29297 | 0.2655 | 0.19226 | 0.3067 | 0.23346 | 0.35706 | 122.1634 | 0.33417 | 122.2641 | 122.4609 | 122.2778 | 122.3877 | 122.2366 | -122.3602 | -122.3282 | 122.0901 | 122.2229 | 0.4715 | 0.57678
1043.0781 | 122.3877 | -0.32501 | 121.9528 | -0.0096891 | 0.0032449 | 0.069353 | 0.063948 | -0.0018649 | -0.0044392 | -0.0020978 | -0.0073547 | 0.0039457 | 0.069769 | 0.058323 | 0.0016194 | 0.016932 | -0.0002244 | 0.09613 | 122.0627 | -0.42572 | 121.7285 | -0.07782 | -0.19226 | -0.1831 | 0.21515 | 121.907 | -0.37537 | 121.8842 | -0.050354 | -0.14191 | -0.050354 | -0.10071 | 0.10986 | -0.2243 | 0.24719 | 0.14191 | 0.13275 | 0.24261 | 0.23346 | -0.050354 | -0.045777 | -0.068665 | 0.27466 | 0.27466 | 0.18311 | 0.32501 | 0.23346 | 0.3479 | 122.1542 | 0.32501 | 122.2595 | 122.4884 | 122.2824 | 122.3877 | 122.2321 | -122.3785 | -122.3282 | 122.0535 | 122.2092 | 0.42114 | 0.54016
1044.8281 | 122.3373 | -0.32501 | 121.9528 | 0.013199 | 0.0066629 | 0.069566 | 0.063735 | 0.00027134 | -0.00038018 | -0.0012434 | 0.0048523 | 0.0056545 | 0.06806 | 0.064518 | -8.9634e-05 | 0.016291 | 0.0040482 | 0.07782 | 122.0993 | -0.42114 | 121.6827 | -0.14191 | -0.2655 | -0.23804 | 0.13275 | 121.9391 | -0.41657 | 121.8338 | -0.12817 | -0.21515 | -0.10529 | -0.096131 | 0.14648 | -0.27008 | 0.18311 | 0.086975 | 0.059509 | 0.18311 | 0.15564 | -0.091553 | -0.013733 | -0.11902 | 0.19684 | 0.21973 | 0.10986 | 0.31128 | 0.20142 | 0.27924 | 122.1039 | 0.28839 | 122.2504 | 122.5204 | 122.3557 | 122.4243 | 122.2641 | -122.374 | -122.3694 | 122.0078 | 122.1588 | 0.40283 | 0.45776
1046.5156 | 122.319 | -0.33417 | 121.9391 | 0.013199 | 0.0064493 | 0.06978 | 0.06523 | 0.00027134 | -0.00059378 | 0.00067925 | 0.0048523 | 0.0037319 | 0.067633 | 0.063878 | -8.9634e-05 | 0.01565 | -0.003856 | 0.064087 | 122.1039 | -0.44403 | 121.6965 | -0.1236 | -0.24719 | -0.23346 | 0.1236 | 121.962 | -0.39368 | 121.8246 | -0.14648 | -0.23346 | -0.1236 | -0.10986 | 0.16479 | -0.24262 | 0.21057 | 0.10071 | 0.086975 | 0.21057 | 0.19684 | -0.05951 | 0.022888 | -0.11444 | 0.18768 | 0.21057 | 0.10071 | 0.27008 | 0.16022 | 0.32044 | 122.1405 | 0.24719 | 122.2183 | 122.5479 | 122.3557 | 122.438 | 122.2961 | -122.3831 | -122.3328 | 122.0306 | 122.1588 | 0.39825 | 0.45776
1048.2656 | 122.3831 | -0.32044 | 121.9711 | 0.0055694 | 0.0053811 | 0.069139 | 0.062239 | 5.774e-05 | -0.006148 | -0.0016706 | -0.0073547 | 0.0033047 | 0.067847 | 0.056828 | -0.00030343 | 0.014795 | -0.0036422 | 0.1236 | 122.049 | -0.41199 | 121.756 | -0.068665 | -0.19226 | -0.18768 | 0.23346 | 121.9299 | -0.38452 | 121.8842 | -0.059509 | -0.16022 | -0.068665 | -0.091552 | 0.07782 | -0.21515 | 0.25177 | 0.13275 | 0.12817 | 0.2243 | 0.21973 | -0.064086 | -0.041198 | -0.086975 | 0.26093 | 0.25177 | 0.16022 | 0.31586 | 0.2243 | 0.34332 | 122.168 | 0.32501 | 122.2687 | 122.4609 | 122.3145 | 122.3694 | 122.2504 | -122.3831 | -122.3557 | 122.0764 | 122.2046 | 0.44403 | 0.55389
1050.0156 | 122.2321 | -0.37994 | 121.994 | 0.0055694 | 0.0096537 | 0.068925 | 0.06758 | 0.0041165 | -0.001662 | 0.0021746 | -0.0012513 | 0.0067227 | 0.070624 | 0.067723 | 0.00076477 | 0.014795 | -0.0070602 | 0.091553 | 122.113 | -0.44861 | 121.6187 | -0.27008 | -0.3891 | -0.3479 | 0.07782 | 121.9666 | -0.41657 | 121.7606 | -0.23804 | -0.32959 | -0.16937 | -0.068664 | 0.11902 | -0.37537 | 0.10986 | 0.032044 | -0.009155 | 0.10071 | 0.059509 | -0.036621 | -0.027466 | -0.23346 | 0.14191 | 0.21057 | 0.050354 | 0.24719 | 0.086975 | 0.17853 | 122.0673 | 0.17853 | 122.1771 | 122.5616 | 122.3831 | 122.493 | 122.3465 | -122.4426 | -122.4106 | 121.9986 | 122.1405 | 0.4715 | 0.45776
1051.7031 | 122.3145 | -0.37079 | 121.962 | 0.028458 | 0.0064493 | 0.070848 | 0.065871 | 0.0013393 | -0.0040118 | 0.00025205 | 0.0079041 | 0.0060819 | 0.068488 | 0.057682 | -0.0026532 | 0.015864 | -0.0019332 | 0.17395 | 122.1405 | -0.45776 | 121.6873 | -0.15564 | -0.27466 | -0.2655 | 0.21515 | 121.9666 | -0.42114 | 121.8246 | -0.15564 | -0.2655 | -0.11902 | -0.086975 | 0.17853 | -0.27466 | 0.21515 | 0.10529 | 0.096131 | 0.19226 | 0.18311 | -0.050354 | 0.004578 | -0.13733 | 0.21515 | 0.25177 | 0.10529 | 0.30212 | 0.15564 | 0.30212 | 122.1451 | 0.2655 | 122.2458 | 122.5983 | 122.3877 | 122.5113 | 122.3373 | -122.4197 | -122.3831 | 122.0581 | 122.1954 | 0.54474 | 0.58594
1053.4688 | 122.3831 | -0.32959 | 121.907 | -0.0020601 | 0.0038857 | 0.072771 | 0.06523 | -0.00015586 | -0.0027302 | 0.00046565 | -0.0043029 | 0.0039457 | 0.069342 | 0.068364 | 0.00076477 | 0.016932 | -0.0023606 | 0.13275 | 122.0718 | -0.42572 | 121.7468 | -0.082397 | -0.23804 | -0.21515 | 0.23804 | 121.9528 | -0.4303 | 121.9116 | -0.10529 | -0.19226 | -0.068665 | -0.09613 | 0.16479 | -0.16022 | 0.24719 | 0.11444 | 0.091553 | 0.21057 | 0.18768 | -0.10071 | 0.045777 | 0.004578 | 0.2243 | 0.26092 | 0.13733 | 0.36163 | 0.23804 | 0.34332 | 122.1725 | 0.32501 | 122.3419 | 122.4976 | 122.3831 | 122.4014 | 122.2824 | -122.3328 | -122.3373 | 122.0764 | 122.2412 | 0.46234 | 0.56763
1055.2344 | 122.2916 | -0.37079 | 121.9757 | 0.0055694 | 0.0068765 | 0.06978 | 0.066512 | 0.0047573 | -0.00059378 | 0.0011066 | 0.0018005 | 0.0075771 | 0.069128 | 0.058751 | -0.001585 | 0.01565 | -0.0025742 | 0.16479 | 122.1085 | -0.46234 | 121.6965 | -0.11902 | -0.27466 | -0.26093 | 0.21515 | 121.962 | -0.40741 | 121.8246 | -0.15106 | -0.27924 | -0.12817 | -0.091552 | 0.13275 | -0.27924 | 0.25177 | 0.10986 | 0.096131 | 0.20142 | 0.18768 | -0.036621 | -0.013733 | -0.15106 | 0.21973 | 0.24261 | 0.091553 | 0.27924 | 0.12817 | 0.34332 | 122.1588 | 0.25635 | 122.2321 | 122.5708 | 122.3694 | 122.4792 | 122.3328 | -122.438 | -122.3831 | 122.0673 | 122.1954 | 0.53558 | 0.58594
1057 | 122.3007 | -0.36163 | 121.9849 | 0.020828 | 0.0079447 | 0.071489 | 0.066939 | 5.774e-05 | -0.0029438 | -0.0020978 | 0.0048523 | 0.0062955 | 0.070624 | 0.05811 | -0.0013714 | 0.016077 | -0.001506 | 0.16022 | 122.1268 | -0.44403 | 121.7148 | -0.13733 | -0.27466 | -0.25177 | 0.22888 | 121.9894 | -0.4303 | 121.8475 | -0.14648 | -0.26093 | -0.13733 | -0.082398 | 0.14191 | -0.27008 | 0.2243 | 0.10986 | 0.086975 | 0.19226 | 0.16937 | -0.068665 | 0.004578 | -0.13733 | 0.21515 | 0.2243 | 0.10071 | 0.29297 | 0.16937 | 0.3067 | 122.1588 | 0.28381 | 122.2778 | 122.5708 | 122.4197 | 122.4884 | 122.3511 | -122.4289 | -122.4152 | 122.0764 | 122.2092 | 0.52185 | 0.59052
1058.6875 | 122.3969 | -0.20599 | 122.0856 | 0.0055694 | 0.0075173 | 0.069994 | 0.065657 | 0.0034755 | -0.00016658 | -0.00060235 | 0.0048523 | 0.0039457 | 0.070624 | 0.071568 | 0.00076477 | 0.016291 | -0.0044968 | 0.12817 | 122.2366 | -0.31586 | 121.843 | 0.009155 | -0.13733 | -0.11444 | 0.22888 | 122.0123 | -0.2655 | 122.0261 | 0.022888 | -0.07782 | 0.041199 | -0.10986 | 0.15106 | -0.24261 | 0.21515 | 0.091553 | 0.068665 | 0.20142 | 0.17853 | -0.059509 | -0.073242 | -0.059509 | 0.22888 | 0.24719 | 0.12817 | 0.3067 | 0.18768 | 0.32501 | 122.1588 | 0.28839 | 122.2916 | 122.5525 | 122.2778 | 122.4426 | 122.2183 | -122.4014 | -122.3511 | 122.049 | 122.2321 | 0.33417 | 0.43488
1060.4531 | 122.2824 | -0.22888 | 122.1451 | 0.0055694 | 0.0058083 | 0.070207 | 0.066939 | 0.0028347 | -0.001662 | -0.001457 | -0.0012513 | 0.0062955 | 0.069983 | 0.060246 | -0.002226 | 0.016077 | -0.0010788 | 0.16937 | 122.2641 | -0.33875 | 121.8201 | -0.032043 | -0.17395 | -0.16479 | 0.17853 | 122.0856 | -0.28839 | 121.9391 | -0.068665 | -0.17853 | -0.027466 | -0.10986 | 0.11902 | -0.32501 | 0.19684 | 0.064087 | 0.054932 | 0.17395 | 0.1648 | -0.059509 | -0.05951 | -0.20599 | 0.16022 | 0.20142 | 0.050354 | 0.26093 | 0.10986 | 0.3067 | 122.1588 | 0.21973 | 122.2275 | 122.6028 | 122.374 | 122.493 | 122.3145 | -122.4838 | -122.4335 | 122.049 | 122.168 | 0.39826 | 0.40741
1062.2031 | 122.3831 | -0.21057 | 122.0856 | -0.0096891 | 0.0058083 | 0.068285 | 0.063735 | 0.0026211 | -0.0018756 | 0.0017474 | -0.0012513 | 0.0035183 | 0.070837 | 0.067509 | -0.0024396 | 0.015223 | 0.0025528 | 0.10986 | 122.2 | -0.31128 | 121.8887 | 0.086975 | -0.068665 | -0.068665 | 0.24261 | 122.0764 | -0.26093 | 122.0169 | 0.068665 | -0.009155 | 0.045776 | -0.10071 | 0.11444 | -0.19684 | 0.29755 | 0.14191 | 0.14191 | 0.24261 | 0.24261 | -0.050354 | -0.009155 | -0.068664 | 0.27924 | 0.25635 | 0.20142 | 0.3067 | 0.25177 | 0.39825 | 122.2 | 0.32959 | 122.2778 | 122.5113 | 122.3373 | 122.4106 | 122.287 | -122.3969 | -122.3465 | 122.0993 | 122.2275 | 0.32043 | 0.45319
1063.9375 | 122.2916 | -0.2243 | 122.113 | 0.013199 | 0.0045267 | 0.070207 | 0.066939 | 0.0043301 | -0.0040118 | 0.0013202 | 0.0048523 | 0.0058683 | 0.069342 | 0.061955 | -0.0020122 | 0.015009 | -0.0023606 | 0.16022 | 122.2595 | -0.33417 | 121.8246 | 0.004578 | -0.15106 | -0.13733 | 0.19684 | 122.0993 | -0.28839 | 121.9574 | -0.041199 | -0.14648 | -0.009155 | -0.10986 | 0.14648 | -0.28839 | 0.22888 | 0.086975 | 0.073242 | 0.19684 | 0.1831 | -0.064087 | -0.013733 | -0.15564 | 0.18311 | 0.21515 | 0.07782 | 0.27924 | 0.14191 | 0.33875 | 122.1588 | 0.24719 | 122.2458 | 122.5937 | 122.3877 | 122.4838 | 122.3236 | -122.4472 | -122.4014 | 122.049 | 122.1817 | 0.38452 | 0.42114
1065.625 | 122.3007 | -0.25177 | 122.1268 | 0.051346 | 0.0043131 | 0.070634 | 0.067152 | 0.0017667 | -0.0014484 | 0.0011066 | 0.010956 | 0.0092861 | 0.068915 | 0.06345 | -0.0043622 | 0.016504 | -0.0055648 | 0.13275 | 122.2916 | -0.36163 | 121.788 | -0.073242 | -0.17395 | -0.14648 | 0.15106 | 122.1634 | -0.32501 | 121.9437 | -0.064087 | -0.15106 | -0.032043 | -0.10986 | 0.1648 | -0.33874 | 0.17853 | 0.10529 | 0.07782 | 0.21515 | 0.18768 | -0.073242 | 0.036621 | -0.1831 | 0.18768 | 0.21973 | 0.10071 | 0.29297 | 0.17395 | 0.28839 | 122.1497 | 0.26093 | 122.2687 | 122.6532 | 122.4884 | 122.5433 | 122.4152 | -122.4884 | -122.4518 | 122.0398 | 122.1954 | 0.38452 | 0.40283
1067.375 | 122.2778 | -0.25177 | 122.1451 | 0.058975 | 0.0053811 | 0.070634 | 0.066298 | -0.0022923 | -0.0020892 | 0.0026018 | 0.020111 | 0.0050137 | 0.069769 | 0.061955 | -0.0024396 | 0.014368 | 0.000203 | 0.11444 | 122.3007 | -0.33875 | 121.7697 | -0.064087 | -0.17853 | -0.14648 | 0.12817 | 122.1268 | -0.32501 | 121.9208 | -0.073242 | -0.16022 | -0.032043 | -0.086975 | 0.15564 | -0.37537 | 0.18768 | 0.10529 | 0.073242 | 0.19226 | 0.16022 | -0.073242 | -0.018311 | -0.22431 | 0.17853 | 0.21973 | 0.091553 | 0.29297 | 0.1648 | 0.27466 | 122.1085 | 0.25177 | 122.2458 | 122.6395 | 122.4518 | 122.5525 | 122.3785 | -122.4838 | -122.4701 | 122.0215 | 122.1725 | 0.36621 | 0.37994
1069.125 | 122.3602 | -0.21515 | 122.0947 | -0.0096891 | 0.0049539 | 0.068498 | 0.066298 | 0.0028347 | -0.001662 | -0.001457 | -0.0012513 | 0.0050137 | 0.068488 | 0.065373 | 0.0022602 | 0.014582 | -0.0034286 | 0.059509 | 122.287 | -0.31586 | 121.788 | -0.036621 | -0.19684 | -0.16022 | 0.13733 | 122.113 | -0.27466 | 121.994 | -0.004578 | -0.091553 | 0.036621 | -0.10071 | 0.19226 | -0.3067 | 0.17853 | 0.054932 | 0.018311 | 0.15564 | 0.11902 | -0.059509 | 0.01831 | -0.10071 | 0.21057 | 0.25177 | 0.1236 | 0.31128 | 0.18311 | 0.27924 | 122.1039 | 0.27008 | 122.2687 | 122.6028 | 122.3877 | 122.5021 | 122.3282 | -122.4106 | -122.3694 | 122.0032 | 122.2092 | 0.27466 | 0.35248
1070.875 | 122.3282 | -0.2243 | 122.1085 | 0.020828 | 0.0066629 | 0.069566 | 0.066512 | 0.0013393 | -0.003371 | 0.00089285 | 0.0079041 | 0.0037319 | 0.071692 | 0.062596 | -0.00094423 | 0.014582 | -0.0036422 | 0.16022 | 122.2824 | -0.33875 | 121.8246 | -0.004578 | -0.15106 | -0.12817 | 0.21057 | 122.1359 | -0.27924 | 121.9803 | -0.013733 | -0.11902 | 0.004578 | -0.11444 | 0.17395 | -0.28381 | 0.21973 | 0.09613 | 0.073242 | 0.21057 | 0.18768 | -0.054932 | 0.027466 | -0.12817 | 0.21057 | 0.22888 | 0.10529 | 0.28381 | 0.16022 | 0.33417 | 122.1634 | 0.2655 | 122.2595 | 122.6212 | 122.4152 | 122.5067 | 122.3602 | -122.4472 | -122.3877 | 122.049 | 122.2046 | 0.38452 | 0.43488
1072.6406 | 122.3969 | -0.20599 | 122.0947 | 0.0055694 | 0.0055947 | 0.069566 | 0.065016 | 0.0032619 | -0.0012348 | -0.0012434 | 0.0018005 | 0.0043729 | 0.068915 | 0.063664 | 0.0026874 | 0.017145 | -0.0027878 | 0.14191 | 122.2275 | -0.28381 | 121.8796 | 0.036621 | -0.11444 | -0.082397 | 0.23346 | 122.0673 | -0.27008 | 122.0398 | 0.032043 | -0.054932 | 0.068665 | -0.077819 | 0.13275 | -0.21515 | 0.24262 | 0.1236 | 0.091553 | 0.20142 | 0.16937 | -0.064087 | -0.027466 | -0.054932 | 0.23804 | 0.27466 | 0.15106 | 0.33875 | 0.21515 | 0.32043 | 122.1634 | 0.30212 | 122.3099 | 122.5113 | 122.3373 | 122.4335 | 122.2733 | -122.3785 | -122.3648 | 122.0856 | 122.2458 | 0.3479 | 0.43945
1074.3281 | 122.2824 | -0.23804 | 122.1497 | -0.0096891 | 0.0079447 | 0.071489 | 0.06758 | 0.0015529 | -0.0020892 | -0.002525 | -0.0012513 | 0.0062955 | 0.068701 | 0.060673 | 0.00076477 | 0.015864 | -0.0017196 | 0.1236 | 122.2824 | -0.29755 | 121.788 | -0.07782 | -0.21973 | -0.20142 | 0.13275 | 122.1222 | -0.28839 | 121.9254 | -0.091553 | -0.20142 | -0.045776 | -0.059509 | 0.13275 | -0.36163 | 0.16022 | 0.036621 | 0.01831 | 0.09613 | 0.077819 | -0.050354 | -0.027466 | -0.2243 | 0.14648 | 0.19226 | 0.036621 | 0.24262 | 0.086975 | 0.21973 | 122.0856 | 0.19684 | 122.2137 | 122.58 | 122.4106 | 122.5204 | 122.3602 | -122.4472 | -122.438 | 122.0261 | 122.1634 | 0.36163 | 0.37079
1076.0625 | 122.2733 | -0.25635 | 122.1542 | -0.0096891 | 0.0049539 | 0.071703 | 0.066084 | 0.0024075 | -0.003371 | 0.0017474 | -0.0012513 | 0.0067227 | 0.070624 | 0.067296 | -0.00094423 | 0.016932 | -0.0036422 | 0.082397 | 122.2961 | -0.32959 | 121.7468 | -0.14648 | -0.27466 | -0.20142 | 0.07782 | 122.1313 | -0.29755 | 121.9482 | -0.11444 | -0.20599 | -0.041199 | -0.073242 | 0.14191 | -0.40741 | 0.10986 | 0.054932 | -0.01831 | 0.12817 | 0.054932 | -0.041198 | -0.022888 | -0.20599 | 0.14191 | 0.21515 | 0.050354 | 0.25635 | 0.091552 | 0.18311 | 122.0764 | 0.1831 | 122.2458 | 122.6257 | 122.4289 | 122.5525 | 122.3877 | -122.4838 | -122.4518 | 122.0032 | 122.2046 | 0.33875 | 0.33417
1077.8125 | 122.2916 | -0.23804 | 122.1588 | 0.0055694 | 0.0081583 | 0.070421 | 0.063307 | 0.0068935 | -0.0037982 | -0.0012434 | -0.0012513 | 0.0045865 | 0.069556 | 0.062169 | -0.0011578 | 0.01565 | -0.0010788 | 0.15564 | 122.3053 | -0.31586 | 121.8201 | -0.032043 | -0.16479 | -0.14648 | 0.17395 | 122.1222 | -0.28381 | 121.9757 | -0.050354 | -0.15564 | -0.018311 | -0.07782 | 0.14648 | -0.33874 | 0.20599 | 0.091553 | 0.073242 | 0.16937 | 0.15106 | -0.045776 | -0.036621 | -0.1831 | 0.18768 | 0.21973 | 0.082397 | 0.2655 | 0.12817 | 0.28381 | 122.1359 | 0.23346 | 122.2595 | 122.6212 | 122.406 | 122.5433 | 122.3602 | -122.4747 | -122.4426 | 122.0581 | 122.2137 | 0.39368 | 0.41199
1079.5625 | 122.3694 | -0.21973 | 122.0993 | -0.0020601 | 0.0047403 | 0.07213 | 0.06523 | 0.0041165 | -0.0037982 | 0.0021746 | -0.0012513 | 0.0052273 | 0.072119 | 0.057469 | 0.00097837 | 0.014795 | -0.003215 | 0.050354 | 122.2961 | -0.32044 | 121.7834 | -0.059509 | -0.21057 | -0.16937 | 0.13733 | 122.1222 | -0.27008 | 122.0032 | -0.013733 | -0.10529 | 0.027466 | -0.10071 | 0.19684 | -0.31586 | 0.16022 | 0.050354 | 0.009156 | 0.15106 | 0.10986 | -0.050354 | 0.022888 | -0.09613 | 0.20599 | 0.24719 | 0.11444 | 0.29755 | 0.1648 | 0.26093 | 122.1039 | 0.25635 | 122.2733 | 122.6166 | 122.3923 | 122.5159 | 122.3419 | -122.4197 | -122.3694 | 122.0032 | 122.2229 | 0.27008 | 0.35706
1081.25 | 122.2687 | -0.25177 | 122.1451 | -0.0020601 | 0.0051675 | 0.068285 | 0.064803 | -0.00079686 | -0.0042254 | -0.0018842 | -0.0012513 | 0.0039457 | 0.069128 | 0.059178 | -0.0037212 | 0.014795 | 0.0044754 | 0.10529 | 122.2733 | -0.31128 | 121.8063 | -0.059509 | -0.16937 | -0.14648 | 0.12817 | 122.1313 | -0.27466 | 121.9116 | -0.068665 | -0.16937 | -0.041199 | -0.059509 | 0.12817 | -0.33875 | 0.19226 | 0.10529 | 0.082397 | 0.16479 | 0.14191 | -0.022888 | -0.013733 | -0.23346 | 0.1831 | 0.21057 | 0.082397 | 0.23346 | 0.10529 | 0.25177 | 122.1176 | 0.20599 | 122.1863 | 122.5845 | 122.406 | 122.525 | 122.3831 | -122.4564 | -122.4197 | 122.0581 | 122.1634 | 0.35706 | 0.37994
1083.0156 | 122.3419 | -0.22888 | 122.1359 | -0.0096891 | 0.0062357 | 0.072557 | 0.066512 | 0.0045437 | -0.001662 | -0.001457 | 0.0048523 | 0.0056545 | 0.07041 | 0.065159 | 0.0014056 | 0.014155 | -0.0023606 | 0.07782 | 122.3007 | -0.31128 | 121.7743 | -0.073242 | -0.21057 | -0.19226 | 0.10529 | 122.1222 | -0.27466 | 121.9986 | -0.054932 | -0.14648 | 0.009155 | -0.082397 | 0.16479 | -0.36163 | 0.15564 | 0.036621 | 0.018311 | 0.11902 | 0.10071 | -0.045776 | -0.013733 | -0.13733 | 0.17395 | 0.23804 | 0.082398 | 0.28381 | 0.12817 | 0.23804 | 122.0856 | 0.21973 | 122.2733 | 122.612 | 122.3969 | 122.5296 | 122.3511 | -122.4472 | -122.4106 | 122.0032 | 122.2275 | 0.3067 | 0.33417
1084.7656 | 122.4289 | -0.19226 | 122.1222 | -0.0020601 | 0.0060221 | 0.069139 | 0.063948 | 0.0011257 | -0.0023028 | -0.0020978 | 0.0018005 | 0.0028775 | 0.068915 | 0.061314 | -0.0017986 | 0.016077 | -0.0036422 | 0.10071 | 122.2595 | -0.28381 | 121.8887 | 0.07782 | -0.054932 | -0.054932 | 0.25177 | 122.1039 | -0.25177 | 122.0764 | 0.086975 | -0.009155 | 0.073242 | -0.091552 | 0.13733 | -0.23346 | 0.27008 | 0.13733 | 0.13733 | 0.22888 | 0.22888 | -0.059509 | -0.01831 | -0.045776 | 0.27924 | 0.2655 | 0.18311 | 0.32501 | 0.24261 | 0.36163 | 122.1725 | 0.33874 | 122.3282 | 122.5433 | 122.3557 | 122.4518 | 122.2961 | -122.406 | -122.374 | 122.081 | 122.2687 | 0.29297 | 0.44403
1086.4688 | 122.4243 | -0.19684 | 122.1451 | -0.0020601 | 0.0028177 | 0.068712 | 0.062026 | -0.00015586 | -0.0025166 | -0.0023114 | -0.0043029 | 0.0039457 | 0.069128 | 0.06815 | -0.0020122 | 0.016077 | -0.001506 | 0.1236 | 122.2504 | -0.27924 | 121.9391 | 0.10071 | -0.036621 | -0.022888 | 0.27008 | 122.0718 | -0.23346 | 122.0764 | 0.073242 | -0.013733 | 0.054932 | -0.082398 | 0.10528 | -0.20599 | 0.29755 | 0.17395 | 0.16022 | 0.25635 | 0.24261 | -0.036621 | -0.073243 | -0.068665 | 0.27008 | 0.25177 | 0.18311 | 0.28839 | 0.21973 | 0.37994 | 122.2183 | 0.3067 | 122.3099 | 122.5296 | 122.3053 | 122.4472 | 122.2687 | -122.4243 | -122.3785 | 122.1359 | 122.2733 | 0.32043 | 0.46692
1088.2188 | 122.4197 | -0.19226 | 122.1313 | -0.0020601 | 0.0023905 | 0.069566 | 0.064375 | 0.0015529 | -0.0037982 | -0.00060235 | -0.0012513 | 0.0054409 | 0.068701 | 0.063664 | 0.00033757 | 0.015009 | -0.001506 | 0.10529 | 122.2641 | -0.27008 | 121.8979 | 0.059509 | -0.07782 | -0.041199 | 0.2243 | 122.1222 | -0.22888 | 122.081 | 0.07782 | -0.027466 | 0.082397 | -0.07782 | 0.13275 | -0.23346 | 0.25177 | 0.15106 | 0.11444 | 0.22888 | 0.19226 | -0.036621 | -0.009156 | -0.050354 | 0.27008 | 0.27466 | 0.16479 | 0.31128 | 0.20142 | 0.32959 | 122.168 | 0.3067 | 122.3099 | 122.5342 | 122.3511 | 122.4564 | 122.3145 | -122.4014 | -122.3602 | 122.0901 | 122.2733 | 0.29755 | 0.41656
1089.9688 | 122.3465 | -0.2243 | 122.1451 | 0.0055694 | 0.0077311 | 0.06978 | 0.06758 | 0.0017667 | -0.0035846 | -0.0012434 | 0.010956 | 0.0082181 | 0.069983 | 0.058323 | -0.0020122 | 0.014582 | -0.0010788 | 0.17395 | 122.3328 | -0.3067 | 121.8658 | -0.004578 | -0.1236 | -0.11902 | 0.21973 | 122.1588 | -0.26093 | 122.0078 | -0.018311 | -0.11444 | 0.018311 | -0.082398 | 0.18768 | -0.27924 | 0.21973 | 0.10529 | 0.10071 | 0.18768 | 0.18311 | -0.036621 | 0.013732 | -0.13733 | 0.20599 | 0.24261 | 0.10986 | 0.27924 | 0.14648 | 0.30212 | 122.1725 | 0.24261 | 122.2687 | 122.6395 | 122.4197 | 122.5571 | 122.3831 | -122.4518 | -122.406 | 122.0901 | 122.2321 | 0.39825 | 0.44403
1091.6562 | 122.4472 | -0.17395 | 122.1222 | -0.0020601 | 0.0038857 | 0.06978 | 0.063307 | 0.0019803 | -0.0042254 | -0.0040204 | 0.0018005 | 0.0043729 | 0.070837 | 0.057255 | -0.002226 | 0.015436 | -0.0008652 | 0.11444 | 122.2824 | -0.27008 | 121.9208 | 0.082397 | -0.045776 | -0.036621 | 0.24719 | 122.0993 | -0.21515 | 122.0764 | 0.10071 | 0.004578 | 0.10986 | -0.096131 | 0.16022 | -0.20142 | 0.25635 | 0.13733 | 0.12817 | 0.23346 | 0.22431 | -0.041199 | -0.022888 | -0.045776 | 0.27466 | 0.28381 | 0.17853 | 0.32501 | 0.21973 | 0.35248 | 122.1909 | 0.31586 | 122.2916 | 122.5525 | 122.3145 | 122.4564 | 122.2733 | -122.3923 | -122.3373 | 122.0947 | 122.2504 | 0.28839 | 0.42114
1093.4062 | 122.3785 | -0.19684 | 122.1497 | 0.013199 | 0.0023905 | 0.069353 | 0.065657 | 0.0013393 | -0.0018756 | -0.00060235 | 0.010956 | 0.0048001 | 0.071478 | 0.066655 | 0.00055117 | 0.016077 | -0.002147 | 0.082397 | 122.2916 | -0.27466 | 121.8796 | 0.013733 | -0.11902 | -0.091553 | 0.13275 | 122.1634 | -0.26093 | 122.0169 | 0.009155 | -0.082397 | 0.036621 | -0.07782 | 0.14191 | -0.27008 | 0.21057 | 0.10529 | 0.077819 | 0.18311 | 0.15564 | -0.064087 | 0.013733 | -0.13275 | 0.20599 | 0.23346 | 0.11444 | 0.29755 | 0.17853 | 0.28839 | 122.1542 | 0.27008 | 122.2778 | 122.5662 | 122.4243 | 122.4884 | 122.3602 | -122.4243 | -122.4106 | 122.0764 | 122.2137 | 0.27924 | 0.32959
1095.1562 | 122.2824 | -0.23346 | 122.2137 | -0.0096891 | 0.0038857 | 0.067644 | 0.064375 | -0.00036966 | -0.0035846 | -0.0033796 | 0.0018005 | 0.0060819 | 0.068915 | 0.05576 | -0.0041486 | 0.016291 | -0.0070602 | 0.091553 | 122.3099 | -0.29755 | 121.8155 | -0.068665 | -0.17853 | -0.14648 | 0.10071 | 122.1588 | -0.27466 | 121.9437 | -0.068665 | -0.15106 | -0.027466 | -0.064087 | 0.09613 | -0.39825 | 0.16479 | 0.086975 | 0.054931 | 0.15106 | 0.11902 | -0.041199 | -0.054932 | -0.27008 | 0.16479 | 0.20599 | 0.082397 | 0.24719 | 0.1236 | 0.22888 | 122.113 | 0.20599 | 122.2183 | 122.6074 | 122.4335 | 122.5433 | 122.3923 | -122.5113 | -122.4884 | 122.0489 | 122.1771 | 0.32501 | 0.33417
1096.9219 | 122.3282 | -0.23804 | 122.2 | 0.020828 | 0.0073037 | 0.069994 | 0.067793 | 0.0011257 | -0.0031574 | 0.0011066 | 0.014008 | 0.0065091 | 0.070196 | 0.048924 | -0.0017986 | 0.015009 | -0.0023606 | 0.13275 | 122.3373 | -0.32501 | 121.8613 | -0.036621 | -0.14648 | -0.11444 | 0.16937 | 122.1954 | -0.29755 | 122.0078 | -0.032043 | -0.12817 | 0.004578 | -0.086975 | 0.13733 | -0.33875 | 0.20142 | 0.1236 | 0.091553 | 0.21057 | 0.17853 | -0.059509 | -0.004577 | -0.19226 | 0.20599 | 0.24261 | 0.10986 | 0.30212 | 0.16937 | 0.28839 | 122.1863 | 0.2655 | 122.3053 | 122.6624 | 122.493 | 122.5754 | 122.4335 | -122.525 | -122.4976 | 122.0993 | 122.2458 | 0.37079 | 0.40741
1098.625 | 122.3007 | -0.21515 | 122.1588 | 0.013199 | 0.0077311 | 0.068925 | 0.068007 | -0.0010105 | -0.00016658 | -0.00038875 | 0.0079041 | 0.0060819 | 0.067419 | 0.06046 | -8.9634e-05 | 0.015009 | -0.0025742 | 0.17395 | 122.3373 | -0.28381 | 121.8796 | 0 | -0.15106 | -0.1236 | 0.19684 | 122.1909 | -0.23804 | 122.0123 | -0.027466 | -0.13733 | -0.004578 | -0.068664 | 0.17853 | -0.27923 | 0.21515 | 0.091553 | 0.064087 | 0.16022 | 0.13275 | -0.022888 | 0.032044 | -0.14648 | 0.18768 | 0.21057 | 0.07782 | 0.23346 | 0.10071 | 0.28381 | 122.1634 | 0.21057 | 122.2504 | 122.6212 | 122.4289 | 122.5525 | 122.406 | -122.4426 | -122.3969 | 122.0947 | 122.2275 | 0.3891 | 0.41199
1100.375 | 122.3923 | -0.16937 | 122.1542 | 0.051346 | 0.0049539 | 0.071703 | 0.064589 | 0.0034755 | 4.7018e-05 | 0.00089285 | 0.017059 | 0.0052273 | 0.070837 | 0.063878 | 0.0024738 | 0.016077 | -0.0010788 | 0.14648 | 122.3236 | -0.27008 | 121.9437 | 0.10986 | -0.064087 | -0.036621 | 0.23804 | 122.1313 | -0.23346 | 122.081 | 0.045776 | -0.050354 | 0.054932 | -0.10071 | 0.16937 | -0.21057 | 0.27924 | 0.13275 | 0.10529 | 0.23346 | 0.20599 | -0.064086 | -0.022888 | -0.073242 | 0.21515 | 0.22431 | 0.11902 | 0.28839 | 0.1831 | 0.37994 | 122.2137 | 0.27924 | 122.3145 | 122.5937 | 122.3648 | 122.493 | 122.3007 | -122.4243 | -122.3877 | 122.113 | 122.2504 | 0.31586 | 0.40741
1102.1094 | 122.3877 | -0.21515 | 122.1634 | 0.043716 | 0.0066629 | 0.06978 | 0.066725 | 0.0011257 | -0.0031574 | 0.0017474 | 0.014008 | 0.0048001 | 0.071478 | 0.061528 | 0.0020466 | 0.017145 | 0.000203 | 0.12817 | 122.3145 | -0.28839 | 121.9116 | 0.073242 | -0.10071 | -0.073242 | 0.1831 | 122.1542 | -0.24719 | 122.0398 | 0.018311 | -0.073242 | 0.036621 | -0.073242 | 0.15106 | -0.25177 | 0.28839 | 0.14191 | 0.11444 | 0.21515 | 0.18768 | -0.032043 | -0.009155 | -0.1236 | 0.23346 | 0.25177 | 0.14191 | 0.28381 | 0.17395 | 0.36163 | 122.2 | 0.2655 | 122.287 | 122.6028 | 122.4014 | 122.5296 | 122.3694 | -122.4518 | -122.4106 | 122.1268 | 122.2549 | 0.34332 | 0.39825
1103.875 | 122.4197 | -0.18768 | 122.1497 | -0.0020601 | 0.0064493 | 0.069994 | 0.064162 | 0.00069854 | -0.0048664 | -0.0027386 | 0.0018005 | 0.0041593 | 0.068701 | 0.065159 | -0.0024396 | 0.015223 | 0.0021256 | 0.13733 | 122.2595 | -0.27008 | 121.9345 | 0.09613 | -0.041199 | -0.036621 | 0.26093 | 122.1268 | -0.23346 | 122.081 | 0.07782 | -0.009155 | 0.07782 | -0.082398 | 0.10986 | -0.21515 | 0.28381 | 0.15106 | 0.14648 | 0.23346 | 0.22888 | -0.045776 | -0.022888 | -0.068664 | 0.2655 | 0.2655 | 0.17853 | 0.31128 | 0.2243 | 0.36621 | 122.2046 | 0.31128 | 122.3145 | 122.5296 | 122.3602 | 122.4472 | 122.3145 | -122.4197 | -122.3831 | 122.1222 | 122.2687 | 0.32501 | 0.44861
1105.5781 | 122.3511 | -0.21515 | 122.1909 | 0.051346 | 0.0079447 | 0.069139 | 0.067152 | 0.0015529 | 4.7018e-05 | -0.0023114 | 0.017059 | 0.0062955 | 0.06806 | 0.058751 | 0.00012397 | 0.015009 | -0.0053512 | 0.16937 | 122.3465 | -0.33417 | 121.8704 | -0.041199 | -0.15564 | -0.11902 | 0.19684 | 122.1954 | -0.2655 | 122.0078 | -0.027466 | -0.12817 | 0.009155 | -0.11902 | 0.15564 | -0.32043 | 0.17395 | 0.09613 | 0.059509 | 0.21515 | 0.17853 | -0.050354 | 0.004578 | -0.18311 | 0.18768 | 0.2243 | 0.086975 | 0.27466 | 0.13733 | 0.29297 | 122.2046 | 0.23804 | 122.2733 | 122.6807 | 122.4609 | 122.5616 | 122.4106 | -122.525 | -122.4564 | 122.0856 | 122.2229 | 0.38452 | 0.41199
1107.3281 | 122.4426 | -0.18768 | 122.1313 | -0.0096891 | 0.0064493 | 0.071489 | 0.064589 | 0.0028347 | -0.0031574 | -0.0020978 | 0.026215 | 0.0054409 | 0.070196 | 0.061528 | 0.0039692 | 0.013727 | -0.0040696 | 0.12817 | 122.2916 | -0.26093 | 121.9254 | 0.050354 | -0.10529 | -0.054932 | 0.2655 | 122.168 | -0.27924 | 122.1085 | 0.054932 | -0.045776 | 0.086975 | -0.073242 | 0.16022 | -0.20599 | 0.23804 | 0.13275 | 0.082397 | 0.20599 | 0.15564 | -0.091553 | 0.036621 | -0.022889 | 0.24261 | 0.27466 | 0.14191 | 0.36621 | 0.23346 | 0.31128 | 122.1863 | 0.33417 | 122.3877 | 122.5525 | 122.4472 | 122.4792 | 122.3557 | -122.3923 | -122.4106 | 122.113 | 122.2961 | 0.31586 | 0.45319
1109.0625 | 122.3831 | -0.2243 | 122.1634 | -0.0020601 | 0.0066629 | 0.068712 | 0.065443 | 0.0019803 | -0.0023028 | 0.00025205 | -0.0043029 | 0.0033047 | 0.069342 | 0.063237 | -0.0026532 | 0.015223 | -0.004924 | 0.15564 | 122.2549 | -0.28839 | 121.9025 | 0.032043 | -0.082397 | -0.07782 | 0.21973 | 122.0993 | -0.26093 | 122.0123 | 0.004578 | -0.091553 | 0 | -0.064087 | 0.091553 | -0.26093 | 0.25635 | 0.14648 | 0.14191 | 0.21057 | 0.20599 | -0.036621 | -0.064087 | -0.15106 | 0.22888 | 0.2243 | 0.13275 | 0.26093 | 0.16937 | 0.32043 | 122.1909 | 0.2655 | 122.2733 | 122.5433 | 122.3602 | 122.4792 | 122.3236 | -122.4518 | -122.4243 | 122.1268 | 122.2366 | 0.37994 | 0.44403
1110.8125 | 122.4335 | -0.19226 | 122.1222 | -0.0096891 | 0.0038857 | 0.06743 | 0.062666 | 0.0015529 | -0.0042254 | -0.0020978 | -0.0012513 | 0.0024503 | 0.068274 | 0.064732 | -0.0017986 | 0.01565 | -0.0030014 | 0.12817 | 122.2504 | -0.27466 | 121.9299 | 0.07782 | -0.064087 | -0.054932 | 0.25635 | 122.1039 | -0.26093 | 122.0581 | 0.050354 | -0.036621 | 0.050354 | -0.082397 | 0.12817 | -0.19226 | 0.27008 | 0.13733 | 0.12817 | 0.21973 | 0.21057 | -0.068664 | -0.01831 | -0.064087 | 0.24261 | 0.24261 | 0.15564 | 0.31128 | 0.2243 | 0.35248 | 122.2046 | 0.31128 | 122.319 | 122.525 | 122.3648 | 122.4426 | 122.2961 | -122.3969 | -122.3831 | 122.1222 | 122.2504 | 0.32044 | 0.44861
1112.5156 | 122.3145 | -0.23346 | 122.2046 | 0.0055694 | 0.0064493 | 0.070848 | 0.068648 | 0.0060391 | -0.00038018 | 0.00046565 | 0.0018005 | 0.0043729 | 0.071051 | 0.064946 | -0.00030343 | 0.015436 | -0.0034286 | 0.10986 | 122.3282 | -0.31128 | 121.8155 | -0.10071 | -0.2243 | -0.20142 | 0.10071 | 122.1771 | -0.27008 | 121.9345 | -0.10529 | -0.21973 | -0.045776 | -0.07782 | 0.1236 | -0.3891 | 0.13275 | 0.032043 | 0.009155 | 0.10986 | 0.086975 | -0.036622 | -0.027466 | -0.27008 | 0.12817 | 0.18768 | 0.013732 | 0.22431 | 0.050354 | 0.21057 | 122.1268 | 0.1648 | 122.2046 | 122.6395 | 122.4472 | 122.5616 | 122.4106 | -122.5159 | -122.4747 | 122.0489 | 122.168 | 0.34332 | 0.33417
1114.2656 | 122.3465 | -0.23346 | 122.2 | 0.036087 | 0.0066629 | 0.072343 | 0.066939 | 0.0017667 | -0.0025166 | -0.0027386 | 0.014008 | 0.0056545 | 0.070624 | 0.063878 | -0.0013714 | 0.01565 | 0.0010574 | 0.16022 | 122.3602 | -0.3479 | 121.8613 | -0.041199 | -0.13733 | -0.14191 | 0.16937 | 122.1817 | -0.28839 | 122.0078 | -0.032043 | -0.13275 | 0.018311 | -0.11444 | 0.16022 | -0.33875 | 0.19226 | 0.091552 | 0.09613 | 0.20599 | 0.21057 | -0.054932 | -0.01831 | -0.19226 | 0.20142 | 0.25177 | 0.10071 | 0.3067 | 0.15564 | 0.3067 | 122.2092 | 0.25635 | 122.2961 | 122.7081 | 122.4701 | 122.5937 | 122.4152 | -122.5479 | -122.4884 | 122.0947 | 122.2412 | 0.39368 | 0.40283
1116.0156 | 122.287 | -0.23804 | 122.2 | -0.0020601 | 0.0064493 | 0.068498 | 0.066298 | -0.00036966 | -0.0035846 | -0.003166 | -0.0043029 | 0.0045865 | 0.071051 | 0.068364 | -0.0028668 | 0.014795 | -0.0044968 | 0.086975 | 122.3236 | -0.3067 | 121.7926 | -0.064087 | -0.17853 | -0.16479 | 0.11444 | 122.1863 | -0.27466 | 121.9528 | -0.082397 | -0.15564 | -0.041199 | -0.068665 | 0.1236 | -0.40741 | 0.17395 | 0.073242 | 0.059509 | 0.14191 | 0.12817 | -0.036621 | -0.013733 | -0.24719 | 0.15564 | 0.19684 | 0.082397 | 0.23346 | 0.11902 | 0.24261 | 122.0993 | 0.19226 | 122.2275 | 122.6303 | 122.4609 | 122.5616 | 122.4243 | -122.5067 | -122.4747 | 122.0306 | 122.1909 | 0.32501 | 0.35248
1117.7031 | 122.3465 | -0.21057 | 122.1771 | -0.0096891 | 0.0068765 | 0.069566 | 0.065443 | 0.0011257 | -0.001662 | 0.00046565 | -0.0012513 | 0.0054409 | 0.069983 | 0.062809 | -0.001585 | 0.014582 | -0.0017196 | 0.16022 | 122.319 | -0.25635 | 121.907 | 0.041199 | -0.09613 | -0.068665 | 0.19684 | 122.1497 | -0.24719 | 122.0078 | 0 | -0.10986 | 0 | -0.045777 | 0.14191 | -0.27008 | 0.25177 | 0.14191 | 0.11444 | 0.18768 | 0.16022 | -0.036621 | -0.027466 | -0.16937 | 0.21057 | 0.21057 | 0.10071 | 0.24719 | 0.13733 | 0.29755 | 122.1634 | 0.24719 | 122.2549 | 122.5754 | 122.3969 | 122.5296 | 122.3602 | -122.4335 | -122.4243 | 122.1176 | 122.2183 | 0.37079 | 0.40741
1119.4531 | 122.3465 | -0.2243 | 122.168 | 0.028458 | 0.0077311 | 0.071275 | 0.066512 | 0.0039029 | -0.0025166 | -0.001457 | 0.0048523 | 0.0090725 | 0.070196 | 0.061741 | 0.0016194 | 0.015864 | -0.0010788 | 0.17853 | 122.3282 | -0.29755 | 121.8933 | 0 | -0.1236 | -0.10529 | 0.23346 | 122.1817 | -0.25635 | 122.0535 | -0.004578 | -0.1236 | 0 | -0.073242 | 0.16022 | -0.27466 | 0.2243 | 0.11902 | 0.10071 | 0.19226 | 0.17395 | -0.032044 | 0.013733 | -0.11444 | 0.21973 | 0.2243 | 0.10071 | 0.25635 | 0.13275 | 0.29755 | 122.1909 | 0.25177 | 122.3099 | 122.6257 | 122.4381 | 122.5525 | 122.406 | -122.4655 | -122.4243 | 122.1176 | 122.2778 | 0.40283 | 0.45776
1121.1875 | 122.3419 | -0.24261 | 122.1863 | 0.013199 | 0.0053811 | 0.071062 | 0.066298 | 0.0041165 | -0.0020892 | -0.00017515 | 0.0048523 | 0.0073635 | 0.071692 | 0.057042 | 0.0016194 | 0.013514 | -0.0072738 | 0.16479 | 122.3602 | -0.31128 | 121.8979 | -0.004578 | -0.13275 | -0.10529 | 0.21973 | 122.168 | -0.27466 | 122.0261 | -0.032043 | -0.10986 | 0.013733 | -0.068664 | 0.17395 | -0.28839 | 0.23804 | 0.13733 | 0.10986 | 0.20599 | 0.17853 | -0.032043 | -0.01831 | -0.16022 | 0.21057 | 0.25635 | 0.13275 | 0.28839 | 0.1648 | 0.3067 | 122.2092 | 0.24262 | 122.3007 | 122.6715 | 122.4426 | 122.6028 | 122.4106 | -122.4976 | -122.4609 | 122.1405 | 122.2687 | 0.40741 | 0.46234
1122.9531 | 122.2916 | -0.21515 | 122.1909 | 0.0055694 | 0.0079447 | 0.070634 | 0.064803 | 0.0015529 | -0.0044392 | -0.0016706 | -0.0043029 | 0.0062955 | 0.070837 | 0.062169 | -8.9634e-05 | 0.016077 | -0.003215 | 0.091553 | 122.3557 | -0.32959 | 121.7926 | -0.13275 | -0.25635 | -0.19226 | 0.059509 | 122.1817 | -0.28381 | 121.9711 | -0.10529 | -0.20142 | -0.041199 | -0.11444 | 0.1648 | -0.39825 | 0.082398 | 0.022888 | -0.041199 | 0.13733 | 0.073242 | -0.068664 | -0.009155 | -0.21973 | 0.10986 | 0.17395 | 0.013733 | 0.24261 | 0.082397 | 0.19684 | 122.1222 | 0.17853 | 122.2549 | 122.6852 | 122.4655 | 122.5708 | 122.3969 | -122.5204 | -122.4747 | 122.0078 | 122.1863 | 0.3067 | 0.27466
1124.6406 | 122.2961 | -0.23804 | 122.2092 | 0.0055694 | 0.0051675 | 0.070421 | 0.065657 | -0.00058326 | -0.0044392 | 0.0011066 | 0.0079041 | 0.0048001 | 0.069769 | 0.067936 | 0.0026874 | 0.014795 | -0.004924 | 0.11902 | 122.3236 | -0.30212 | 121.8246 | -0.068665 | -0.22888 | -0.18768 | 0.12817 | 122.1588 | -0.2655 | 122.0032 | -0.082397 | -0.18768 | -0.045776 | -0.064087 | 0.11444 | -0.38452 | 0.16937 | 0.050354 | 0.009155 | 0.11444 | 0.073242 | -0.027466 | -0.050354 | -0.20599 | 0.15564 | 0.19226 | 0.050354 | 0.21973 | 0.07782 | 0.23346 | 122.1268 | 0.18311 | 122.2687 | 122.6257 | 122.4243 | 122.5616 | 122.3969 | -122.5113 | -122.4747 | 122.0627 | 122.2412 | 0.35706 | 0.36621
1126.3906 | 122.4014 | -0.20599 | 122.1863 | 0.028458 | 0.0058083 | 0.069994 | 0.06758 | 0.0028347 | 0.00068782 | -0.0010298 | 0.010956 | 0.0052273 | 0.071051 | 0.06046 | 0.0020466 | 0.016291 | -0.0034286 | 0.11444 | 122.3419 | -0.31128 | 121.8979 | 0.068665 | -0.091553 | -0.082397 | 0.20142 | 122.1313 | -0.27466 | 122.0444 | 0.009155 | -0.064087 | 0.018311 | -0.10528 | 0.15564 | -0.28839 | 0.27466 | 0.1236 | 0.11444 | 0.22888 | 0.21973 | -0.068664 | -0.054931 | -0.14191 | 0.21515 | 0.22431 | 0.14191 | 0.29297 | 0.21057 | 0.37994 | 122.2092 | 0.28381 | 122.319 | 122.6532 | 122.406 | 122.5479 | 122.3373 | -122.4976 | -122.4609 | 122.1039 | 122.2504 | 0.32044 | 0.40741
1128.1406 | 122.3648 | -0.23346 | 122.168 | 0.028458 | 0.0077311 | 0.071916 | 0.064162 | 5.774e-05 | -0.0020892 | 0.0023882 | 0.0079041 | 0.0041593 | 0.068488 | 0.061314 | -0.0013714 | 0.014795 | -0.0042832 | 0.17395 | 122.3557 | -0.32044 | 121.875 | -0.004578 | -0.14191 | -0.11902 | 0.23346 | 122.1863 | -0.27466 | 122.0352 | -0.013733 | -0.11902 | 0.013733 | -0.086976 | 0.18768 | -0.29297 | 0.22888 | 0.11444 | 0.091552 | 0.20142 | 0.17853 | -0.041199 | 0.01831 | -0.13275 | 0.21973 | 0.24719 | 0.11444 | 0.28839 | 0.15564 | 0.31586 | 122.1954 | 0.26093 | 122.3099 | 122.6761 | 122.4609 | 122.5891 | 122.4197 | -122.4884 | -122.4426 | 122.1085 | 122.2687 | 0.40741 | 0.46692
1129.8906 | 122.4609 | -0.1831 | 122.1634 | 0.0055694 | 0.0053811 | 0.069566 | 0.063735 | -0.0029331 | -0.0023028 | -0.00060235 | 0.0018005 | 0.0020231 | 0.068915 | 0.061528 | -0.0028668 | 0.016718 | -0.0030014 | 0.11902 | 122.287 | -0.27008 | 121.9391 | 0.082397 | -0.050354 | -0.036621 | 0.26093 | 122.1313 | -0.23346 | 122.1085 | 0.068665 | -0.027466 | 0.059509 | -0.086976 | 0.1236 | -0.2243 | 0.2655 | 0.14648 | 0.13275 | 0.23346 | 0.21973 | -0.050354 | -0.032043 | -0.054932 | 0.25177 | 0.24261 | 0.15564 | 0.29297 | 0.20599 | 0.35248 | 122.2092 | 0.30212 | 122.3419 | 122.5571 | 122.3648 | 122.4701 | 122.3145 | -122.4335 | -122.3969 | 122.1222 | 122.2916 | 0.30212 | 0.44403
1131.5938 | 122.4014 | -0.21515 | 122.1725 | 0.043716 | 0.0062357 | 0.071062 | 0.066939 | -0.0016513 | -0.0027302 | -0.0044476 | 0.014008 | 0.0048001 | 0.071051 | 0.072636 | 0.0031146 | 0.018213 | 0.001912 | 0.1236 | 122.3053 | -0.31586 | 121.9162 | 0.054932 | -0.11902 | -0.082397 | 0.20599 | 122.1497 | -0.27924 | 122.0581 | 0.009155 | -0.09613 | 0.022888 | -0.10071 | 0.13275 | -0.25635 | 0.27008 | 0.13275 | 0.09613 | 0.23346 | 0.19684 | -0.064087 | -0.022888 | -0.11444 | 0.2243 | 0.23804 | 0.11902 | 0.30212 | 0.18311 | 0.37079 | 122.2321 | 0.28839 | 122.3373 | 122.6212 | 122.4289 | 122.5204 | 122.3648 | -122.4884 | -122.4518 | 122.1313 | 122.2733 | 0.33875 | 0.42114
1133.3438 | 122.3694 | -0.24719 | 122.168 | -0.0096891 | 0.0049539 | 0.070634 | 0.066298 | 0.0024075 | -0.0029438 | -0.0020978 | -0.0012513 | 0.0060819 | 0.069769 | 0.060673 | 0.0041828 | 0.018 | -0.001506 | 0.07782 | 122.3557 | -0.32044 | 121.8063 | -0.091553 | -0.24719 | -0.1831 | 0.12817 | 122.1725 | -0.28381 | 122.0306 | -0.059509 | -0.14648 | -0.004578 | -0.073243 | 0.18768 | -0.36163 | 0.15564 | 0.064087 | 0 | 0.13733 | 0.073243 | -0.036621 | 0.004577 | -0.13733 | 0.18768 | 0.24261 | 0.10071 | 0.27923 | 0.13733 | 0.22888 | 122.1268 | 0.2243 | 122.3145 | 122.6761 | 122.4564 | 122.6028 | 122.4197 | -122.4884 | -122.4518 | 122.0535 | 122.2778 | 0.32501 | 0.37537
1135.0938 | 122.4609 | -0.20142 | 122.1497 | -0.0020601 | 0.0043131 | 0.068925 | 0.064803 | 0.0051845 | -0.00016658 | -0.00081595 | 0.017059 | 0.0069363 | 0.070837 | 0.059605 | 0.001833 | 0.018213 | -0.0012924 | 0.14648 | 122.2961 | -0.2655 | 121.9345 | 0.041199 | -0.10071 | -0.050354 | 0.27466 | 122.1954 | -0.27466 | 122.1039 | 0.050354 | -0.050354 | 0.068665 | -0.064087 | 0.14648 | -0.21515 | 0.24262 | 0.15106 | 0.10071 | 0.21515 | 0.16479 | -0.073242 | 0.045777 | -0.045776 | 0.25177 | 0.27008 | 0.15106 | 0.34332 | 0.2243 | 0.3067 | 122.2 | 0.32501 | 122.3785 | 122.5616 | 122.4701 | 122.4976 | 122.3969 | -122.4152 | -122.4243 | 122.1359 | 122.3053 | 0.3479 | 0.47607
1136.8438 | 122.3694 | -0.21515 | 122.1909 | 0.036087 | 0.0053811 | 0.069994 | 0.065657 | 0.0030483 | -0.0020892 | 0.00367 | 0.010956 | 0.0071499 | 0.068488 | 0.057469 | -0.0013714 | 0.015436 | -0.003215 | 0.17395 | 122.3465 | -0.32959 | 121.8796 | -0.013733 | -0.14648 | -0.13275 | 0.2243 | 122.1954 | -0.27924 | 122.0261 | -0.013733 | -0.11902 | 0.013733 | -0.11444 | 0.15564 | -0.31128 | 0.20142 | 0.082398 | 0.068665 | 0.19684 | 0.18311 | -0.064087 | 0.004578 | -0.16479 | 0.20142 | 0.22888 | 0.09613 | 0.29297 | 0.16022 | 0.31586 | 122.2092 | 0.2655 | 122.3053 | 122.6761 | 122.4747 | 122.5616 | 122.4106 | -122.5204 | -122.4701 | 122.0947 | 122.2412 | 0.3891 | 0.43945
1138.5469 | 122.4152 | -0.21973 | 122.168 | -0.0020601 | 0.0066629 | 0.06978 | 0.063948 | 0.0011257 | -0.0055072 | 0.00067925 | -0.0012513 | 0.0041593 | 0.068701 | 0.058323 | -0.0017986 | 0.015223 | -0.0017196 | 0.14648 | 122.3007 | -0.27008 | 121.9437 | 0.064087 | -0.064087 | -0.059509 | 0.23804 | 122.1451 | -0.23346 | 122.0718 | 0.041199 | -0.050354 | 0.054932 | -0.050354 | 0.13275 | -0.2243 | 0.28381 | 0.16022 | 0.15564 | 0.21057 | 0.20599 | -0.013732 | -0.022888 | -0.096131 | 0.26093 | 0.27466 | 0.16937 | 0.28839 | 0.1831 | 0.33417 | 122.2137 | 0.27466 | 122.3053 | 122.5708 | 122.3785 | 122.5204 | 122.3648 | -122.4381 | -122.4014 | 122.1634 | 122.2916 | 0.36621 | 0.45776
1140.2969 | 122.4426 | -0.18768 | 122.168 | -0.0096891 | 0.0049539 | 0.071275 | 0.068007 | -0.0016513 | -0.0029438 | 0.0015338 | -0.0043029 | 0.0045865 | 0.07041 | 0.063664 | 0.00076477 | 0.015864 | -0.0012924 | 0.10529 | 122.3282 | -0.29297 | 121.875 | -0.013733 | -0.16022 | -0.11902 | 0.18768 | 122.1725 | -0.23346 | 122.0947 | 0.027466 | -0.068665 | 0.059509 | -0.10529 | 0.16022 | -0.29297 | 0.17395 | 0.068664 | 0.027466 | 0.17395 | 0.13275 | -0.045776 | 0.004577 | -0.073242 | 0.21515 | 0.24719 | 0.11902 | 0.29297 | 0.16479 | 0.27924 | 122.168 | 0.26093 | 122.3282 | 122.6212 | 122.406 | 122.5159 | 122.3602 | -122.4609 | -122.4014 | 122.0627 | 122.2824 | 0.29297 | 0.37537
1142.0312 | 122.4197 | -0.20142 | 122.1634 | 0.028458 | 0.0051675 | 0.06978 | 0.064803 | 0.00091214 | -0.0035846 | -0.0012434 | 0.0018005 | 0.0024503 | 0.069128 | 0.067936 | 0.00012397 | 0.014795 | -0.0002244 | 0.07782 | 122.3145 | -0.28839 | 121.8887 | 0 | -0.1236 | -0.091553 | 0.15106 | 122.1634 | -0.25177 | 122.049 | 0.018311 | -0.086975 | 0.018311 | -0.086975 | 0.15106 | -0.27466 | 0.20142 | 0.10986 | 0.07782 | 0.19684 | 0.1648 | -0.050354 | 0 | -0.11444 | 0.21973 | 0.21973 | 0.11444 | 0.27008 | 0.16479 | 0.28839 | 122.1771 | 0.27008 | 122.3007 | 122.6028 | 122.4152 | 122.5159 | 122.3648 | -122.4518 | -122.4152 | 122.0901 | 122.2504 | 0.27924 | 0.35248
1143.7812 | 122.4106 | -0.18768 | 122.1909 | 0.028458 | 0.0062357 | 0.070207 | 0.066298 | 0.00069854 | -0.0031574 | -0.00038875 | 0.0079041 | 0.0041593 | 0.070624 | 0.066441 | 0.0014056 | 0.017573 | -0.0002244 | 0.11902 | 122.3145 | -0.29297 | 121.9299 | 0.041199 | -0.1236 | -0.07782 | 0.16022 | 122.1817 | -0.27466 | 122.0535 | -0.009155 | -0.086975 | 0.013733 | -0.10529 | 0.1236 | -0.26093 | 0.22888 | 0.10986 | 0.064087 | 0.21515 | 0.16937 | -0.086975 | -0.009155 | -0.13733 | 0.17853 | 0.20142 | 0.10071 | 0.28839 | 0.18768 | 0.33417 | 122.2229 | 0.2655 | 122.3282 | 122.6074 | 122.4564 | 122.5021 | 122.3694 | -122.4838 | -122.4655 | 122.1176 | 122.2412 | 0.3067 | 0.3479
1145.4688 | 122.4289 | -0.22888 | 122.1588 | 0.028458 | 0.0047403 | 0.071703 | 0.065016 | 5.774e-05 | -0.0020892 | 0.00046565 | 0.014008 | 0.0041593 | 0.070837 | 0.066014 | -8.9634e-05 | 0.014368 | -0.0008652 | 0.15564 | 122.3419 | -0.29755 | 121.9666 | 0.07782 | -0.073242 | -0.045776 | 0.24261 | 122.1817 | -0.28839 | 122.081 | 0.027466 | -0.059509 | 0.059509 | -0.068664 | 0.18311 | -0.19226 | 0.3067 | 0.18311 | 0.15564 | 0.25177 | 0.2243 | -0.059509 | 0.022889 | -0.077819 | 0.25635 | 0.28839 | 0.16937 | 0.3479 | 0.22888 | 0.37537 | 122.2641 | 0.31586 | 122.3694 | 122.6395 | 122.4701 | 122.5708 | 122.4106 | -122.4564 | -122.4472 | 122.1954 | 122.3099 | 0.38452 | 0.4715
1147.2031 | 122.4701 | -0.1831 | 122.1771 | 0.0055694 | 0.0055947 | 0.068712 | 0.064589 | 0.0015529 | -0.0014484 | -0.0016706 | -0.0012513 | 0.0035183 | 0.069128 | 0.063664 | -0.001585 | 0.015009 | -0.0019332 | 0.15564 | 122.2961 | -0.28381 | 121.9803 | 0.07782 | -0.073242 | -0.054932 | 0.27008 | 122.1817 | -0.26093 | 122.0947 | 0.068665 | -0.018311 | 0.050354 | -0.10071 | 0.11902 | -0.19684 | 0.26092 | 0.12817 | 0.10986 | 0.22888 | 0.21057 | -0.07782 | 0.004578 | -0.082397 | 0.25177 | 0.23346 | 0.16479 | 0.31128 | 0.24261 | 0.36163 | 122.2641 | 0.32959 | 122.3557 | 122.58 | 122.4426 | 122.4792 | 122.3648 | -122.4609 | -122.438 | 122.1634 | 122.2778 | 0.33874 | 0.45319
1148.9688 | 122.3282 | -0.23804 | 122.2321 | 0.0055694 | 0.0049539 | 0.069139 | 0.065443 | 0.0017667 | -0.0023028 | -0.00081595 | 0.023163 | 0.0097135 | 0.071692 | 0.0658 | -0.0052166 | 0.013727 | -1.0598e-05 | 0.10071 | 122.3557 | -0.32959 | 121.8201 | -0.086975 | -0.18768 | -0.14191 | 0.16022 | 122.2229 | -0.32501 | 121.9666 | -0.086975 | -0.16937 | -0.054932 | -0.091553 | 0.1236 | -0.41199 | 0.15106 | 0.09613 | 0.050354 | 0.18768 | 0.14191 | -0.086975 | -0.009156 | -0.2655 | 0.15106 | 0.1831 | 0.068664 | 0.27008 | 0.15564 | 0.24261 | 122.1497 | 0.23804 | 122.2916 | 122.6852 | 122.5479 | 122.5937 | 122.4609 | -122.5616 | -122.5571 | 122.0581 | 122.2046 | 0.33875 | 0.39825
1150.6562 | 122.4609 | -0.16937 | 122.1863 | -0.0020601 | 0.0075173 | 0.070634 | 0.06758 | 0.0041165 | -0.00080758 | -0.0023114 | 0.023163 | 0.0037319 | 0.071265 | 0.071568 | 0.0031146 | 0.014582 | -0.004924 | 0.15106 | 122.3145 | -0.2655 | 121.9528 | 0.064087 | -0.10071 | -0.059509 | 0.2655 | 122.2137 | -0.26093 | 122.1268 | 0.045776 | -0.050354 | 0.086975 | -0.09613 | 0.12817 | -0.23346 | 0.23346 | 0.10986 | 0.068665 | 0.20599 | 0.16479 | -0.091552 | 0.027466 | -0.059509 | 0.21515 | 0.25635 | 0.11902 | 0.3479 | 0.21057 | 0.32959 | 122.2183 | 0.3067 | 122.3877 | 122.58 | 122.4747 | 122.4838 | 122.3831 | -122.4518 | -122.4472 | 122.1222 | 122.2961 | 0.32044 | 0.43488
1152.4062 | 122.3694 | -0.21057 | 122.2137 | 0.028458 | 0.0062357 | 0.069994 | 0.065657 | -0.00079686 | -0.0037982 | 3.8448e-05 | 0.014008 | 0.0084317 | 0.070196 | 0.057042 | -0.00030343 | 0.016077 | -0.0051376 | 0.18768 | 122.3557 | -0.32501 | 121.8933 | -0.013733 | -0.13275 | -0.11444 | 0.21515 | 122.2275 | -0.27924 | 122.0444 | -0.022888 | -0.1236 | 0.013733 | -0.11444 | 0.14191 | -0.32043 | 0.19684 | 0.09613 | 0.07782 | 0.21057 | 0.19226 | -0.068665 | 0.013733 | -0.16937 | 0.18768 | 0.2243 | 0.086975 | 0.29297 | 0.15564 | 0.31128 | 122.2183 | 0.25635 | 122.3236 | 122.6807 | 122.5067 | 122.5662 | 122.438 | -122.5388 | -122.493 | 122.1039 | 122.2549 | 0.39825 | 0.42572
1154.1562 | 122.4518 | -0.18768 | 122.1863 | -0.017319 | 0.0047403 | 0.070848 | 0.065871 | 0.0015529 | -0.00059378 | -0.00017515 | -0.0043029 | 0.0033047 | 0.070837 | 0.070713 | -8.9634e-05 | 0.016932 | -0.003215 | 0.1236 | 122.374 | -0.29297 | 121.9345 | 0.050354 | -0.1236 | -0.082397 | 0.22888 | 122.1497 | -0.24719 | 122.1222 | 0.050354 | -0.050354 | 0.073242 | -0.10529 | 0.18768 | -0.25177 | 0.23804 | 0.10529 | 0.064087 | 0.21057 | 0.16937 | -0.059509 | -0.036621 | -0.064087 | 0.23804 | 0.26092 | 0.13733 | 0.32043 | 0.19684 | 0.34332 | 122.2275 | 0.29755 | 122.3694 | 122.6669 | 122.3969 | 122.5616 | 122.3373 | -122.4792 | -122.4335 | 122.1222 | 122.3099 | 0.31128 | 0.41656
1155.9219 | 122.3969 | -0.20599 | 122.2275 | -0.0020601 | 0.0068765 | 0.070207 | 0.068221 | 0.0015529 | 0.00026062 | -0.00017515 | 0.0018005 | 0.0069363 | 0.07041 | 0.067082 | 0.00076477 | 0.015223 | -0.0030014 | 0.09613 | 122.3877 | -0.28839 | 121.8521 | -0.073242 | -0.22888 | -0.17395 | 0.13733 | 122.1954 | -0.24719 | 122.0581 | -0.050354 | -0.13733 | 0.004578 | -0.082397 | 0.16022 | -0.37537 | 0.13275 | 0.032044 | -0.022888 | 0.11444 | 0.059509 | -0.041198 | -0.032043 | -0.16937 | 0.15564 | 0.21057 | 0.068665 | 0.25177 | 0.10986 | 0.21515 | 122.1405 | 0.19684 | 122.3053 | 122.6761 | 122.4426 | 122.5937 | 122.4014 | -122.5159 | -122.4747 | 122.0581 | 122.2641 | 0.30212 | 0.34332
1157.6094 | 122.3282 | -0.2243 | 122.2458 | -0.0096891 | 0.0079447 | 0.06978 | 0.068007 | 0.0039029 | -0.0014484 | 0.00067925 | -0.0043029 | 0.0062955 | 0.070837 | 0.057469 | 0.00097837 | 0.015009 | -0.003215 | 0.17395 | 122.3648 | -0.30212 | 121.8796 | -0.041199 | -0.20142 | -0.15106 | 0.15564 | 122.2229 | -0.24261 | 122.0169 | -0.064087 | -0.17853 | -0.032043 | -0.07782 | 0.11902 | -0.36621 | 0.18311 | 0.073242 | 0.022888 | 0.15106 | 0.10071 | -0.018311 | -0.022889 | -0.22888 | 0.16022 | 0.19226 | 0.045776 | 0.21057 | 0.064087 | 0.26093 | 122.1817 | 0.17853 | 122.2595 | 122.6669 | 122.4655 | 122.5891 | 122.4472 | -122.5479 | -122.4884 | 122.1039 | 122.2412 | 0.39825 | 0.37994
1159.3594 | 122.3831 | -0.21515 | 122.2366 | 0.058975 | 0.0081583 | 0.071489 | 0.066725 | 0.0017667 | -0.0018756 | 0.0032428 | 0.0079041 | 0.0080045 | 0.071478 | 0.061741 | 0.00012397 | 0.017359 | -0.002147 | 0.1831 | 122.3694 | -0.3067 | 121.9025 | -0.022888 | -0.14191 | -0.10071 | 0.20142 | 122.2229 | -0.27466 | 122.049 | -0.018311 | -0.10986 | 0.032043 | -0.091553 | 0.13275 | -0.33417 | 0.19226 | 0.11444 | 0.073242 | 0.20599 | 0.16479 | -0.059509 | -0.013733 | -0.18768 | 0.19684 | 0.24719 | 0.10529 | 0.3067 | 0.1648 | 0.28381 | 122.2092 | 0.25635 | 122.3236 | 122.6761 | 122.4976 | 122.5845 | 122.438 | -122.5433 | -122.5113 | 122.1176 | 122.2641 | 0.39825 | 0.41657
1161.0938 | 122.3282 | -0.22888 | 122.2458 | 0.013199 | 0.0058083 | 0.070848 | 0.066298 | 0.0024075 | -0.001662 | 0.001961 | 0.0018005 | 0.0052273 | 0.069342 | 0.067082 | -8.9634e-05 | 0.015436 | -0.0030014 | 0.1236 | 122.3969 | -0.27466 | 121.8292 | -0.10529 | -0.2243 | -0.19226 | 0.086975 | 122.2275 | -0.25635 | 122.0032 | -0.07782 | -0.19684 | -0.018311 | -0.045776 | 0.15106 | -0.41657 | 0.1236 | 0.036621 | 0.004578 | 0.082397 | 0.050354 | -0.027466 | -0.018311 | -0.24262 | 0.15106 | 0.21057 | 0.032044 | 0.23804 | 0.05951 | 0.16937 | 122.1039 | 0.17853 | 122.2595 | 122.6715 | 122.4838 | 122.6257 | 122.4564 | -122.5204 | -122.5021 | 122.0581 | 122.2321 | 0.35248 | 0.31586
1162.8438 | 122.3969 | -0.20142 | 122.2229 | 0.013199 | 0.0070901 | 0.072771 | 0.067152 | 0.0019803 | 0.00047422 | 0.001961 | 0.0048523 | 0.0041593 | 0.072119 | 0.057682 | -0.0013714 | 0.0133 | -0.0012924 | 0.20599 | 122.3923 | -0.28381 | 121.9254 | 0.027466 | -0.1236 | -0.091553 | 0.23804 | 122.2321 | -0.26093 | 122.081 | 0.004578 | -0.10529 | 0.032043 | -0.082397 | 0.16937 | -0.29755 | 0.22888 | 0.10986 | 0.07782 | 0.19226 | 0.16022 | -0.059509 | 0.009156 | -0.14191 | 0.20599 | 0.23346 | 0.09613 | 0.29297 | 0.15564 | 0.31128 | 122.2092 | 0.2655 | 122.3419 | 122.6761 | 122.493 | 122.5937 | 122.4335 | -122.5067 | -122.4838 | 122.1268 | 122.2824 | 0.40741 | 0.43945
1164.5312 | 122.4701 | -0.18768 | 122.1863 | -0.0096891 | 0.0058083 | 0.071916 | 0.064375 | 0.00069854 | -0.0023028 | 0.00025205 | -0.0012513 | 0.0048001 | 0.068701 | 0.064305 | 0.001192 | 0.017359 | -0.0027878 | 0.16479 | 122.3602 | -0.25635 | 121.9299 | 0.050354 | -0.10529 | -0.086975 | 0.23804 | 122.1588 | -0.2243 | 122.1497 | 0.050354 | -0.041199 | 0.082397 | -0.068665 | 0.17395 | -0.25635 | 0.23804 | 0.10071 | 0.082397 | 0.16937 | 0.15106 | -0.036621 | -0.027466 | -0.036621 | 0.23804 | 0.27008 | 0.14648 | 0.3067 | 0.18311 | 0.3067 | 122.1863 | 0.27466 | 122.374 | 122.6166 | 122.3831 | 122.5479 | 122.3465 | -122.4426 | -122.4106 | 122.1176 | 122.3373 | 0.35248 | 0.42572
1166.2656 | 122.4106 | -0.19684 | 122.1954 | 0.020828 | 0.0064493 | 0.067857 | 0.064803 | 0.00048494 | -0.0020892 | 0.0015338 | 0.0048523 | 0.0028775 | 0.070624 | 0.061314 | -0.0011578 | 0.015436 | -0.0002244 | 0.10529 | 122.3648 | -0.27466 | 121.8979 | 0.009155 | -0.11902 | -0.091553 | 0.12817 | 122.2046 | -0.26093 | 122.081 | 0 | -0.07782 | 0.018311 | -0.07782 | 0.16937 | -0.29755 | 0.20599 | 0.10529 | 0.077819 | 0.18311 | 0.15564 | -0.064087 | 0.009155 | -0.11444 | 0.19684 | 0.21515 | 0.11902 | 0.27924 | 0.18311 | 0.28381 | 122.1725 | 0.26093 | 122.3419 | 122.6395 | 122.4655 | 122.5616 | 122.4014 | -122.4701 | -122.4564 | 122.0947 | 122.2778 | 0.30212 | 0.32501
1168.0156 | 122.4197 | -0.19226 | 122.2092 | 0.028458 | 0.0070901 | 0.071916 | 0.064589 | 0.00069854 | 0.0013288 | -0.0016706 | 0.017059 | 0.0060819 | 0.071905 | 0.067509 | -8.9634e-05 | 0.016932 | -0.0010788 | 0.16937 | 122.3648 | -0.27924 | 121.962 | 0.091553 | -0.086975 | -0.045776 | 0.23346 | 122.2092 | -0.26093 | 122.0993 | 0.032043 | -0.054932 | 0.045776 | -0.086975 | 0.15564 | -0.24719 | 0.28381 | 0.14648 | 0.10529 | 0.23346 | 0.19226 | -0.068664 | 0 | -0.10986 | 0.2243 | 0.23804 | 0.13733 | 0.3067 | 0.20599 | 0.37079 | 122.2412 | 0.29297 | 122.3602 | 122.644 | 122.4701 | 122.5571 | 122.4014 | -122.4884 | -122.4701 | 122.1542 | 122.2916 | 0.36163 | 0.42572
1169.7031 | 122.4655 | -0.15564 | 122.1817 | -0.0096891 | 0.0021769 | 0.068071 | 0.064375 | 0.00048494 | -0.0014484 | 0.0015338 | 0.0048523 | 0.0030911 | 0.072119 | 0.062382 | -0.0030804 | 0.016504 | -0.0002244 | 0.16937 | 122.319 | -0.24719 | 121.9986 | 0.09613 | -0.041199 | -0.027466 | 0.25635 | 122.1909 | -0.21973 | 122.1359 | 0.082397 | 0 | 0.086975 | -0.091552 | 0.13733 | -0.18311 | 0.25177 | 0.12817 | 0.11444 | 0.21973 | 0.20599 | -0.064087 | 0.009155 | -0.045777 | 0.23804 | 0.24261 | 0.15564 | 0.3067 | 0.21973 | 0.34332 | 122.2458 | 0.30212 | 122.3557 | 122.5662 | 122.4106 | 122.4747 | 122.3465 | -122.4289 | -122.4014 | 122.1542 | 122.2916 | 0.32501 | 0.41199
1171.4531 | 122.3373 | -0.22888 | 122.2458 | 0.0055694 | 0.0051675 | 0.068712 | 0.066084 | 0.0036893 | -0.0029438 | -0.0020978 | 0.0018005 | 0.0030911 | 0.070624 | 0.063237 | -0.0039348 | 0.013086 | -0.000438 | 0.14648 | 122.3373 | -0.28839 | 121.8613 | -0.050354 | -0.16479 | -0.12817 | 0.13275 | 122.2366 | -0.25635 | 122.0078 | -0.045776 | -0.14648 | -0.027466 | -0.059509 | 0.091552 | -0.38452 | 0.17853 | 0.10071 | 0.064087 | 0.16022 | 0.1236 | -0.027466 | -0.009156 | -0.23804 | 0.18311 | 0.20142 | 0.082398 | 0.22888 | 0.10986 | 0.23804 | 122.1497 | 0.21057 | 122.2641 | 122.6257 | 122.493 | 122.5662 | 122.4655 | -122.5342 | -122.5021 | 122.0901 | 122.2366 | 0.37537 | 0.36163
1173.2031 | 122.4197 | -0.17853 | 122.2183 | 0.020828 | 0.0066629 | 0.071703 | 0.065443 | 0.0021939 | -0.0018756 | -0.0016706 | 0.0018005 | 0.0058683 | 0.069128 | 0.069645 | 0.00055117 | 0.016504 | -0.0008652 | 0.15106 | 122.3648 | -0.27466 | 121.9437 | 0.041199 | -0.10529 | -0.059509 | 0.16479 | 122.2183 | -0.24719 | 122.0901 | 0.013733 | -0.086975 | 0.036621 | -0.09613 | 0.14648 | -0.27466 | 0.21973 | 0.11902 | 0.073242 | 0.21515 | 0.16937 | -0.068664 | 0 | -0.12817 | 0.19226 | 0.21515 | 0.091553 | 0.28381 | 0.16022 | 0.31586 | 122.2183 | 0.26093 | 122.3373 | 122.6395 | 122.4655 | 122.5433 | 122.3969 | -122.493 | -122.4655 | 122.1222 | 122.2687 | 0.32959 | 0.34332
1174.8906 | 122.4792 | -0.16022 | 122.2092 | -0.0020601 | 0.0053811 | 0.06978 | 0.066084 | 0.0051845 | -0.0029438 | 3.8448e-05 | 0.0018005 | 0.0030911 | 0.069983 | 0.064518 | 0.00055117 | 0.016291 | -0.0023606 | 0.19226 | 122.374 | -0.26093 | 121.9757 | 0.07782 | -0.082397 | -0.041199 | 0.23346 | 122.1909 | -0.21515 | 122.1588 | 0.068665 | -0.027466 | 0.10071 | -0.10071 | 0.1648 | -0.23346 | 0.23804 | 0.11902 | 0.07782 | 0.21973 | 0.17853 | -0.054932 | -0.01831 | -0.050354 | 0.22888 | 0.26093 | 0.13275 | 0.31586 | 0.18768 | 0.33875 | 122.2366 | 0.28381 | 122.374 | 122.6349 | 122.406 | 122.5342 | 122.3511 | -122.4701 | -122.4243 | 122.1359 | 122.319 | 0.35248 | 0.39368
1176.6406 | 122.3373 | -0.2243 | 122.2549 | 0.058975 | 0.0066629 | 0.068285 | 0.067152 | 0.0030483 | -0.0052936 | 0.00025205 | 0.023163 | 0.0071499 | 0.069342 | 0.061741 | -0.0030804 | 0.013514 | -0.0059922 | 0.18768 | 122.4289 | -0.31586 | 121.8887 | -0.050354 | -0.14191 | -0.1236 | 0.15106 | 122.2916 | -0.29297 | 122.0261 | -0.045776 | -0.14191 | -0.004578 | -0.091553 | 0.17395 | -0.36621 | 0.17395 | 0.10071 | 0.082397 | 0.19226 | 0.17395 | -0.068665 | 0.036621 | -0.22888 | 0.17853 | 0.21973 | 0.082397 | 0.28839 | 0.15106 | 0.2655 | 122.2046 | 0.24719 | 122.319 | 122.7448 | 122.5845 | 122.6532 | 122.5159 | -122.5708 | -122.5479 | 122.113 | 122.2504 | 0.41199 | 0.37537
1178.3906 | 122.4747 | -0.16937 | 122.2366 | 0.0055694 | 0.0047403 | 0.069566 | 0.065016 | -0.00058326 | -0.0040118 | -0.0029524 | -0.0012513 | 0.0039457 | 0.069128 | 0.067082 | -0.0011578 | 0.01565 | -0.0017196 | 0.18768 | 122.3419 | -0.23346 | 122.0032 | 0.10986 | -0.022888 | -0.013733 | 0.27924 | 122.1909 | -0.21515 | 122.1542 | 0.10529 | 0.004578 | 0.086975 | -0.064086 | 0.10529 | -0.23346 | 0.27924 | 0.15564 | 0.14649 | 0.21973 | 0.21057 | -0.045776 | -0.045776 | -0.082397 | 0.27466 | 0.25635 | 0.17395 | 0.30212 | 0.21973 | 0.34332 | 122.2366 | 0.32044 | 122.3694 | 122.5754 | 122.406 | 122.5113 | 122.3602 | -122.4701 | -122.4518 | 122.1725 | 122.3236 | 0.35706 | 0.44861
1180.0781 | 122.374 | -0.20599 | 122.2687 | 0.058975 | 0.0064493 | 0.070421 | 0.067366 | 5.774e-05 | -0.0046528 | 0.0034564 | 0.03537 | 0.0067227 | 0.070837 | 0.056187 | -0.0020122 | 0.013727 | -0.0036422 | 0.1831 | 122.4197 | -0.31586 | 121.8887 | -0.032043 | -0.15564 | -0.11902 | 0.17853 | 122.2778 | -0.2655 | 122.0352 | -0.032043 | -0.11444 | 0 | -0.10986 | 0.15106 | -0.37994 | 0.17395 | 0.086975 | 0.050354 | 0.19684 | 0.16022 | -0.059509 | 0.009155 | -0.23346 | 0.17395 | 0.20599 | 0.091553 | 0.2655 | 0.15106 | 0.28381 | 122.2046 | 0.23346 | 122.3007 | 122.7356 | 122.5433 | 122.6257 | 122.4838 | -122.5845 | -122.5342 | 122.0947 | 122.2412 | 0.3891 | 0.38452
1181.8281 | 122.4655 | -0.14648 | 122.2366 | -0.0020601 | 0.0051675 | 0.069994 | 0.065016 | -0.0012241 | -0.0023028 | -0.00081595 | -0.0012513 | 0.0037319 | 0.070196 | 0.067509 | 0.0016194 | 0.016932 | -0.0019332 | 0.20599 | 122.3328 | -0.23346 | 121.994 | 0.068665 | -0.07782 | -0.054932 | 0.23346 | 122.2 | -0.21515 | 122.168 | 0.07782 | -0.036621 | 0.091553 | -0.086975 | 0.096131 | -0.24261 | 0.21515 | 0.091552 | 0.068664 | 0.17853 | 0.15564 | -0.068665 | -0.036621 | -0.068664 | 0.2243 | 0.23804 | 0.10986 | 0.3067 | 0.17853 | 0.30212 | 122.2275 | 0.29297 | 122.3831 | 122.5662 | 122.4152 | 122.4792 | 122.3465 | -122.4701 | -122.4518 | 122.1405 | 122.3145 | 0.35248 | 0.37994
1183.5312 | 122.3877 | -0.22888 | 122.2595 | 0.043716 | 0.0090127 | 0.070848 | 0.065871 | -0.0020787 | -0.003371 | 0.00025205 | 0.010956 | 0.0077909 | 0.072119 | 0.064518 | -0.00051703 | 0.014155 | -0.0019332 | 0.19684 | 122.4106 | -0.31128 | 121.9025 | -0.032043 | -0.13733 | -0.10071 | 0.17853 | 122.287 | -0.27008 | 122.0627 | -0.032043 | -0.11902 | 0.009155 | -0.082397 | 0.15106 | -0.35706 | 0.19684 | 0.12817 | 0.091553 | 0.21057 | 0.17395 | -0.041199 | 0.027466 | -0.19684 | 0.19684 | 0.23804 | 0.10986 | 0.27924 | 0.15106 | 0.27924 | 122.2137 | 0.23804 | 122.3328 | 122.7219 | 122.5571 | 122.6395 | 122.5159 | -122.5708 | -122.5296 | 122.1313 | 122.2916 | 0.42572 | 0.40741
1185.2812 | 122.4564 | -0.16937 | 122.2137 | 0.0055694 | 0.0062357 | 0.070421 | 0.066725 | 0.0043301 | -0.0027302 | 0.00067925 | 0.0018005 | 0.0037319 | 0.07041 | 0.057255 | 0.001833 | 0.017573 | -0.002147 | 0.14648 | 122.406 | -0.27466 | 121.9254 | 0.004578 | -0.14648 | -0.09613 | 0.20599 | 122.2046 | -0.2243 | 122.168 | 0.050354 | -0.045776 | 0.07782 | -0.10529 | 0.19226 | -0.28839 | 0.17395 | 0.073243 | 0.022889 | 0.17853 | 0.12817 | -0.054931 | -0.009155 | -0.045776 | 0.21973 | 0.24719 | 0.1236 | 0.30212 | 0.17853 | 0.27924 | 122.2 | 0.27466 | 122.3923 | 122.6807 | 122.4289 | 122.5754 | 122.374 | -122.4884 | -122.438 | 122.0947 | 122.3373 | 0.31586 | 0.37537
1187.0312 | 122.3282 | -0.21515 | 122.2549 | 0.0055694 | 0.0058083 | 0.071916 | 0.068434 | 0.0013393 | -0.0027302 | -0.0010298 | 0.0048523 | 0.0058683 | 0.07041 | 0.06815 | 0.00055117 | 0.015009 | -0.003856 | 0.14191 | 122.4106 | -0.27924 | 121.8338 | -0.082397 | -0.21515 | -0.16937 | 0.09613 | 122.2733 | -0.23804 | 122.0444 | -0.082397 | -0.16479 | -0.009155 | -0.064087 | 0.15564 | -0.42114 | 0.13275 | 0.045776 | 0 | 0.10986 | 0.064087 | -0.022888 | 0.01831 | -0.21057 | 0.13275 | 0.20599 | 0.050354 | 0.22888 | 0.073242 | 0.19684 | 122.113 | 0.15564 | 122.2824 | 122.6898 | 122.5113 | 122.6257 | 122.4884 | -122.5342 | -122.493 | 122.0489 | 122.2595 | 0.35706 | 0.31128
1188.7188 | 122.4426 | -0.16479 | 122.2092 | 0.051346 | 0.0081583 | 0.073198 | 0.066298 | 0.0043301 | -0.003371 | 3.8448e-05 | 0.010956 | 0.0039457 | 0.06806 | 0.070927 | 0.0024738 | 0.018 | -0.001506 | 0.19226 | 122.3969 | -0.2655 | 122.0078 | 0.091553 | -0.059509 | -0.032043 | 0.27466 | 122.2366 | -0.23346 | 122.1588 | 0.064087 | -0.036621 | 0.07782 | -0.10071 | 0.18768 | -0.20142 | 0.25635 | 0.13275 | 0.10529 | 0.23346 | 0.20599 | -0.068664 | 0.027466 | -0.050354 | 0.22888 | 0.24261 | 0.12817 | 0.31128 | 0.19684 | 0.35706 | 122.2733 | 0.29755 | 122.3923 | 122.6624 | 122.4701 | 122.5616 | 122.4014 | -122.4747 | -122.4426 | 122.1725 | 122.3236 | 0.35706 | 0.43945
1190.4688 | 122.4014 | -0.19684 | 122.2504 | 0.020828 | 0.0070901 | 0.071062 | 0.066298 | 0.0047573 | -0.0023028 | 0.00025205 | 0.010956 | 0.0054409 | 0.07041 | 0.065587 | -0.002226 | 0.015864 | -0.0002244 | 0.22888 | 122.406 | -0.29755 | 121.9437 | 0.018311 | -0.10529 | -0.091553 | 0.25177 | 122.2687 | -0.23804 | 122.0993 | 0.009155 | -0.082397 | 0.041199 | -0.10071 | 0.15564 | -0.3067 | 0.21515 | 0.10529 | 0.091552 | 0.20599 | 0.19226 | -0.041199 | 0.018311 | -0.15106 | 0.20599 | 0.23804 | 0.11444 | 0.27924 | 0.15564 | 0.31586 | 122.2412 | 0.24719 | 122.3373 | 122.7036 | 122.5067 | 122.6028 | 122.4655 | -122.5479 | -122.4884 | 122.1405 | 122.2961 | 0.42572 | 0.44861
1192.2031 | 122.3877 | -0.1831 | 122.2412 | 0.013199 | 0.0070901 | 0.070207 | 0.064803 | -0.00058326 | -0.0042254 | -0.0020978 | -0.0043029 | 0.0069363 | 0.072333 | 0.067296 | -0.0020122 | 0.014582 | -0.0042832 | 0.13733 | 122.4289 | -0.28839 | 121.8658 | -0.059509 | -0.20142 | -0.16022 | 0.13275 | 122.2458 | -0.24261 | 122.0947 | -0.027466 | -0.11444 | 0.018311 | -0.10529 | 0.18768 | -0.37537 | 0.1236 | 0.022888 | -0.018311 | 0.12817 | 0.086975 | -0.05951 | 0.004578 | -0.14648 | 0.15564 | 0.20142 | 0.068664 | 0.26093 | 0.12817 | 0.22888 | 122.1542 | 0.21515 | 122.3373 | 122.7173 | 122.4884 | 122.612 | 122.4289 | -122.5296 | -122.4838 | 122.0489 | 122.2778 | 0.32043 | 0.31586
1193.9688 | 122.4472 | -0.16937 | 122.2183 | 0.051346 | 0.0092263 | 0.071916 | 0.062453 | 0.00069854 | -0.0014484 | -0.00081595 | 0.017059 | 0.0045865 | 0.072333 | 0.065587 | -8.9634e-05 | 0.017786 | -0.0017196 | 0.17395 | 122.406 | -0.26093 | 121.9894 | 0.10529 | -0.064087 | -0.013733 | 0.26093 | 122.2183 | -0.2243 | 122.1451 | 0.045776 | -0.050354 | 0.073242 | -0.091552 | 0.18768 | -0.22888 | 0.27466 | 0.15564 | 0.10529 | 0.24719 | 0.19684 | -0.054931 | 0 | -0.073242 | 0.21515 | 0.24261 | 0.11902 | 0.29755 | 0.17395 | 0.36621 | 122.2504 | 0.27008 | 122.3694 | 122.6669 | 122.4426 | 122.5754 | 122.3877 | -122.4792 | -122.4426 | 122.1588 | 122.3145 | 0.34332 | 0.4303
1195.7188 | 122.4014 | -0.19226 | 122.2504 | 0.013199 | 0.0092263 | 0.071703 | 0.065016 | 0.0056119 | -0.0040118 | -0.00038875 | 0.0048523 | 0.0045865 | 0.071478 | 0.057042 | -8.9634e-05 | 0.015009 | -0.0017196 | 0.25177 | 122.406 | -0.26093 | 121.9482 | 0.022888 | -0.10071 | -0.086975 | 0.24719 | 122.2824 | -0.23804 | 122.0947 | 0.013733 | -0.07782 | 0.032043 | -0.068664 | 0.15564 | -0.30212 | 0.21515 | 0.10529 | 0.091553 | 0.17395 | 0.16022 | -0.045776 | 0.032044 | -0.15564 | 0.20599 | 0.2243 | 0.11444 | 0.27008 | 0.16022 | 0.28381 | 122.2092 | 0.25177 | 122.3328 | 122.6669 | 122.5204 | 122.5983 | 122.4747 | -122.5113 | -122.4884 | 122.1405 | 122.287 | 0.44403 | 0.43945
1197.4062 | 122.4655 | -0.1831 | 122.2366 | 0.0055694 | 0.0055947 | 0.070634 | 0.064375 | 0.0045437 | -0.00038018 | -0.0010298 | -0.0012513 | 0.0065091 | 0.07041 | 0.062382 | 0.0026874 | 0.016291 | -0.0036422 | 0.14648 | 122.3831 | -0.26093 | 121.9208 | 0.009155 | -0.15106 | -0.10071 | 0.20142 | 122.2183 | -0.22888 | 122.1634 | 0.041199 | -0.027466 | 0.091553 | -0.07782 | 0.14648 | -0.31586 | 0.19226 | 0.082397 | 0.032043 | 0.16022 | 0.10986 | -0.045777 | -0.01831 | -0.073242 | 0.2243 | 0.27466 | 0.15564 | 0.32044 | 0.20142 | 0.27008 | 122.1817 | 0.27008 | 122.3923 | 122.644 | 122.4472 | 122.5662 | 122.4014 | -122.4976 | -122.4655 | 122.1039 | 122.3465 | 0.32959 | 0.38452
1199.1562 | 122.3557 | -0.20599 | 122.2824 | -0.0020601 | 0.0062357 | 0.070207 | 0.064803 | 0.0017667 | -0.00508 | -0.00060235 | 0.020111 | 0.0062955 | 0.070624 | 0.0611 | -0.0037212 | 0.014368 | -0.003856 | 0.15564 | 122.4152 | -0.29297 | 121.8887 | -0.022888 | -0.13275 | -0.09613 | 0.16479 | 122.287 | -0.28839 | 122.0352 | -0.059509 | -0.14648 | 0 | -0.086975 | 0.13275 | -0.39368 | 0.18311 | 0.10986 | 0.073243 | 0.19684 | 0.16022 | -0.082397 | 0.004577 | -0.24719 | 0.14649 | 0.20599 | 0.05951 | 0.28839 | 0.14191 | 0.27008 | 122.1817 | 0.22888 | 122.3236 | 122.7081 | 122.5754 | 122.6212 | 122.493 | -122.5754 | -122.5708 | 122.0947 | 122.2412 | 0.36163 | 0.37079
1200.9062 | 122.406 | -0.19684 | 122.2641 | -0.0020601 | 0.0051675 | 0.069994 | 0.068007 | 0.0032619 | -0.0040118 | 3.8448e-05 | -0.0012513 | 0.0060819 | 0.069556 | 0.06345 | -0.00030343 | 0.016504 | -0.000438 | 0.12817 | 122.406 | -0.27466 | 121.8658 | -0.064087 | -0.19684 | -0.15106 | 0.1236 | 122.287 | -0.22888 | 122.0718 | -0.032043 | -0.14191 | 0.022888 | -0.07782 | 0.14191 | -0.39825 | 0.13275 | 0.045776 | 0 | 0.1236 | 0.07782 | -0.032044 | 0.022888 | -0.19226 | 0.1648 | 0.21973 | 0.054931 | 0.25177 | 0.086975 | 0.21057 | 122.1405 | 0.19684 | 122.3007 | 122.6807 | 122.5159 | 122.6028 | 122.4838 | -122.5388 | -122.493 | 122.0627 | 122.2687 | 0.32501 | 0.32043
1202.5938 | 122.4243 | -0.18768 | 122.2366 | 0.013199 | 0.0062357 | 0.071489 | 0.06523 | 0.0030483 | -0.0010212 | 0.00067925 | 0.0079041 | 0.0043729 | 0.071692 | 0.064946 | -0.00094423 | 0.016718 | 0.0010574 | 0.13733 | 122.374 | -0.27466 | 121.9437 | 0.041199 | -0.09613 | -0.073242 | 0.16479 | 122.2366 | -0.23346 | 122.1085 | 0.027466 | -0.059509 | 0.045776 | -0.086975 | 0.13733 | -0.29297 | 0.22888 | 0.11444 | 0.091553 | 0.20142 | 0.17853 | -0.045776 | 0 | -0.12817 | 0.21515 | 0.23346 | 0.12817 | 0.27924 | 0.17395 | 0.31586 | 122.2183 | 0.26093 | 122.3419 | 122.6486 | 122.4701 | 122.5616 | 122.4243 | -122.5113 | -122.4701 | 122.1313 | 122.2961 | 0.32501 | 0.35248
1204.3438 | 122.3648 | -0.20142 | 122.2504 | 0.0055694 | 0.0083719 | 0.072343 | 0.063735 | 0.0019803 | -0.0029438 | -0.00081595 | 0.0018005 | 0.0056545 | 0.070624 | 0.057682 | 0.0014056 | 0.014582 | -0.002147 | 0.21973 | 122.4472 | -0.2655 | 121.9299 | -0.009155 | -0.15564 | -0.14191 | 0.20142 | 122.2458 | -0.21973 | 122.0901 | -0.036621 | -0.14191 | 0 | -0.064087 | 0.19684 | -0.32043 | 0.19226 | 0.059509 | 0.045776 | 0.1236 | 0.10986 | -0.018311 | -0.004577 | -0.16022 | 0.1648 | 0.20142 | 0.059509 | 0.21973 | 0.07782 | 0.25635 | 122.1954 | 0.18311 | 122.3099 | 122.7127 | 122.4655 | 122.6486 | 122.4472 | -122.5159 | -122.4701 | 122.1313 | 122.2916 | 0.42114 | 0.40283
1206.0938 | 122.4792 | -0.16479 | 122.2458 | 0.0055694 | 0.0036721 | 0.068071 | 0.065016 | 0.0024075 | -0.001662 | -0.0033796 | -0.0012513 | 0.0035183 | 0.070624 | 0.068364 | 0.00012397 | 0.01565 | 0.0025528 | 0.14191 | 122.406 | -0.25177 | 121.9482 | 0.045776 | -0.082397 | -0.059509 | 0.19226 | 122.2183 | -0.21057 | 122.1634 | 0.082397 | 0.004578 | 0.091553 | -0.086975 | 0.16022 | -0.29755 | 0.21057 | 0.10529 | 0.082398 | 0.19226 | 0.16937 | -0.045776 | -0.027466 | -0.082398 | 0.24719 | 0.25635 | 0.16937 | 0.30212 | 0.21515 | 0.29755 | 122.2 | 0.29297 | 122.374 | 122.6578 | 122.4289 | 122.5708 | 122.3831 | -122.4976 | -122.4564 | 122.113 | 122.3282 | 0.3067 | 0.35706
1207.8438 | 122.4335 | -0.17853 | 122.2366 | 0.036087 | 0.0060221 | 0.070207 | 0.064162 | -0.0010105 | -0.0037982 | 0.00067925 | 0.0048523 | 0.0039457 | 0.067633 | 0.069218 | 0.001192 | 0.016504 | -0.000438 | 0.16479 | 122.3969 | -0.25635 | 121.9482 | 0.036621 | -0.10986 | -0.054932 | 0.16479 | 122.2504 | -0.2243 | 122.0947 | 0.004578 | -0.068665 | 0.036621 | -0.07782 | 0.16022 | -0.28839 | 0.21515 | 0.1236 | 0.068665 | 0.20142 | 0.14649 | -0.045776 | 0.013733 | -0.14191 | 0.18311 | 0.21515 | 0.10986 | 0.26093 | 0.15564 | 0.29297 | 122.2046 | 0.22888 | 122.319 | 122.6532 | 122.4747 | 122.5754 | 122.4289 | -122.493 | -122.4609 | 122.1268 | 122.2733 | 0.34332 | 0.34332
1209.6094 | 122.3511 | -0.2243 | 122.2733 | -0.0020601 | 0.0077311 | 0.070848 | 0.066298 | 0.0034755 | -0.0042254 | -0.00060235 | -0.0012513 | 0.0054409 | 0.070837 | 0.064091 | 0.00055117 | 0.014368 | -0.0070602 | 0.20599 | 122.4152 | -0.27008 | 121.8842 | -0.064087 | -0.20599 | -0.16022 | 0.11902 | 122.287 | -0.21973 | 122.049 | -0.068665 | -0.1831 | -0.027466 | -0.045777 | 0.14191 | -0.3891 | 0.16022 | 0.064087 | 0.01831 | 0.10986 | 0.064087 | 0.004577 | 0.013733 | -0.2243 | 0.15564 | 0.19684 | 0.041199 | 0.19226 | 0.036622 | 0.20599 | 122.1542 | 0.15106 | 122.2687 | 122.6852 | 122.5067 | 122.6395 | 122.5113 | -122.5433 | -122.493 | 122.1085 | 122.2733 | 0.4303 | 0.34332
1211.2969 | 122.3602 | -0.21057 | 122.2778 | -0.0020601 | 0.0053811 | 0.068071 | 0.064162 | -0.00079686 | -0.003371 | 0.00025205 | -0.0012513 | 0.0039457 | 0.069128 | 0.062596 | -0.0028668 | 0.013514 | -0.0023606 | 0.2243 | 122.374 | -0.24261 | 121.9299 | 0.013733 | -0.12817 | -0.10071 | 0.17395 | 122.2504 | -0.24719 | 122.0535 | -0.036621 | -0.11902 | -0.018311 | -0.032044 | 0.09613 | -0.3479 | 0.2243 | 0.10986 | 0.082397 | 0.14191 | 0.11444 | -0.036621 | -0.027466 | -0.2243 | 0.17395 | 0.19226 | 0.091552 | 0.22888 | 0.12817 | 0.25635 | 122.1725 | 0.21057 | 122.3007 | 122.6166 | 122.4976 | 122.5845 | 122.4609 | -122.5204 | -122.525 | 122.1405 | 122.2641 | 0.43488 | 0.38452
1213 | 122.438 | -0.1831 | 122.2366 | -0.0020601 | 0.0051675 | 0.070207 | 0.065871 | 0.0030483 | -0.0031574 | -0.0023114 | 0.0018005 | 0.0054409 | 0.07041 | 0.058751 | 0.003542 | 0.016077 | -0.0030014 | 0.16937 | 122.4335 | -0.27924 | 121.8887 | -0.041199 | -0.17395 | -0.14191 | 0.15106 | 122.2549 | -0.23346 | 122.1313 | 0.022888 | -0.082397 | 0.059509 | -0.096131 | 0.19684 | -0.3479 | 0.14191 | 0.041198 | 0.009155 | 0.13733 | 0.10529 | -0.050354 | 0.018311 | -0.10528 | 0.20599 | 0.24261 | 0.10071 | 0.29297 | 0.15106 | 0.23804 | 122.168 | 0.25635 | 122.3648 | 122.7127 | 122.4884 | 122.6166 | 122.438 | -122.5159 | -122.4701 | 122.0718 | 122.3145 | 0.35248 | 0.33417
1214.7656 | 122.3831 | -0.19226 | 122.2504 | -0.0020601 | 0.0068765 | 0.069353 | 0.066084 | 0.0043301 | -0.0027302 | 0.00046565 | -0.0043029 | 0.0048001 | 0.07041 | 0.059819 | 0.00055117 | 0.014582 | -1.0598e-05 | 0.1831 | 122.4243 | -0.28839 | 121.8613 | -0.068665 | -0.20599 | -0.14191 | 0.1236 | 122.2687 | -0.24261 | 122.0764 | -0.059509 | -0.14648 | -0.009155 | -0.09613 | 0.17395 | -0.3891 | 0.1236 | 0.050354 | -0.013733 | 0.14648 | 0.082397 | -0.050354 | 0.018311 | -0.17395 | 0.13275 | 0.18311 | 0.045777 | 0.23346 | 0.096131 | 0.21973 | 122.1497 | 0.18311 | 122.319 | 122.7127 | 122.5113 | 122.6166 | 122.4609 | -122.5388 | -122.493 | 122.0535 | 122.2687 | 0.37537 | 0.31586
1216.5156 | 122.3785 | -0.21515 | 122.287 | 0.051346 | 0.0060221 | 0.070421 | 0.066298 | 0.0011257 | -0.00059378 | -0.00038875 | 0.010956 | 0.0062955 | 0.069983 | 0.062169 | -0.0028668 | 0.015436 | -0.0010788 | 0.25177 | 122.4472 | -0.30212 | 121.875 | -0.036621 | -0.13733 | -0.091553 | 0.16479 | 122.319 | -0.27008 | 122.0627 | -0.027466 | -0.14191 | -0.009155 | -0.086975 | 0.16022 | -0.41199 | 0.17853 | 0.1236 | 0.07782 | 0.21057 | 0.16479 | -0.054932 | 0.032044 | -0.2243 | 0.18768 | 0.20599 | 0.073242 | 0.26093 | 0.12817 | 0.2655 | 122.1771 | 0.24262 | 122.3328 | 122.7493 | 122.5891 | 122.6624 | 122.5342 | -122.5891 | -122.5571 | 122.0901 | 122.2778 | 0.46692 | 0.37994
1218.2031 | 122.4792 | -0.16022 | 122.2595 | -0.0020601 | 0.0055947 | 0.068925 | 0.064162 | 0.0034755 | -0.0029438 | -0.00017515 | 0.0018005 | 0.0028775 | 0.066992 | 0.061741 | -0.0013714 | 0.015009 | 0.0014846 | 0.26093 | 122.3557 | -0.24719 | 122.0078 | 0.091553 | -0.045776 | -0.036621 | 0.2655 | 122.2504 | -0.21515 | 122.1451 | 0.09613 | -0.018311 | 0.082397 | -0.086975 | 0.096131 | -0.25177 | 0.25177 | 0.1236 | 0.11444 | 0.21057 | 0.20142 | -0.054932 | -0.009155 | -0.11444 | 0.25635 | 0.24261 | 0.14191 | 0.29755 | 0.19684 | 0.33874 | 122.2549 | 0.31128 | 122.3602 | 122.6028 | 122.4655 | 122.5159 | 122.4106 | -122.5067 | -122.4747 | 122.168 | 122.3053 | 0.42114 | 0.42572
1219.9688 | 122.4152 | -0.19226 | 122.2916 | 0.051346 | 0.0055947 | 0.069994 | 0.066725 | 0.0028347 | -0.0027302 | 0.00089285 | 0.010956 | 0.0075771 | 0.07041 | 0.058323 | 0.00012397 | 0.015223 | -0.0062058 | 0.28839 | 122.438 | -0.28839 | 121.9299 | 0 | -0.11444 | -0.07782 | 0.20599 | 122.2916 | -0.25635 | 122.1039 | 0.009155 | -0.09613 | 0.032043 | -0.09613 | 0.14648 | -0.36163 | 0.19226 | 0.11444 | 0.07782 | 0.21057 | 0.17395 | -0.064087 | 0 | -0.18768 | 0.20142 | 0.2243 | 0.096131 | 0.28839 | 0.16022 | 0.28839 | 122.2183 | 0.2655 | 122.3602 | 122.7264 | 122.5479 | 122.6303 | 122.4838 | -122.58 | -122.5479 | 122.1222 | 122.2961 | 0.48065 | 0.39826
1221.7031 | 122.3831 | -0.21057 | 122.2595 | -0.0096891 | 0.0062357 | 0.069566 | 0.067366 | 0.0032619 | -0.0018756 | 0.0021746 | -0.0012513 | 0.0050137 | 0.071051 | 0.063237 | -0.00051703 | 0.015223 | -0.0017196 | 0.21057 | 122.4289 | -0.27008 | 121.8567 | -0.059509 | -0.19684 | -0.16022 | 0.1236 | 122.2687 | -0.23804 | 122.0856 | -0.059509 | -0.16479 | 0.004578 | -0.05951 | 0.16937 | -0.40283 | 0.15106 | 0.050354 | 0.013733 | 0.10986 | 0.073243 | -0.027466 | 0.009156 | -0.17395 | 0.15106 | 0.21515 | 0.045776 | 0.24261 | 0.073242 | 0.21057 | 122.1268 | 0.17853 | 122.3236 | 122.699 | 122.5067 | 122.6395 | 122.4792 | -122.5296 | -122.4976 | 122.0673 | 122.2961 | 0.42114 | 0.33417
1223.3906 | 122.3877 | -0.19226 | 122.2961 | 0.058975 | 0.0051675 | 0.070634 | 0.066725 | 0.0011257 | -0.0027302 | 0.0021746 | 0.010956 | 0.0065091 | 0.073401 | 0.060246 | -0.0013714 | 0.015223 | -0.0027878 | 0.28381 | 122.4472 | -0.30212 | 121.8933 | -0.013733 | -0.1236 | -0.10986 | 0.17853 | 122.2961 | -0.26093 | 122.0673 | -0.013733 | -0.12817 | 0.009155 | -0.10986 | 0.15106 | -0.40283 | 0.17853 | 0.082398 | 0.068665 | 0.19226 | 0.17853 | -0.068664 | 0 | -0.22888 | 0.17853 | 0.20142 | 0.064087 | 0.27008 | 0.13275 | 0.28839 | 122.1954 | 0.24719 | 122.3282 | 122.7493 | 122.5571 | 122.6395 | 122.4884 | -122.5983 | -122.5571 | 122.0856 | 122.2595 | 0.47607 | 0.37079
1225.0938 | 122.3602 | -0.21973 | 122.2687 | -0.0020601 | 0.0066629 | 0.072343 | 0.066298 | 0.00091214 | -0.0023028 | -0.0020978 | 0.0018005 | 0.0050137 | 0.070196 | 0.057469 | 0.00097837 | 0.014582 | -0.0017196 | 0.24261 | 122.4564 | -0.25635 | 121.8658 | -0.073242 | -0.19684 | -0.15564 | 0.11902 | 122.3053 | -0.23804 | 122.0718 | -0.073242 | -0.16022 | 0.013733 | -0.036621 | 0.18768 | -0.40283 | 0.14649 | 0.064087 | 0.022889 | 0.10071 | 0.05951 | -0.01831 | 0.036621 | -0.19684 | 0.14649 | 0.23346 | 0.05951 | 0.25177 | 0.07782 | 0.18311 | 122.1222 | 0.16479 | 122.3099 | 122.7127 | 122.5433 | 122.6761 | 122.525 | -122.525 | -122.5067 | 122.0856 | 122.2916 | 0.46234 | 0.33875
1226.8594 | 122.438 | -0.1831 | 122.2595 | -0.0020601 | 0.0064493 | 0.06978 | 0.063735 | 0.0024075 | -0.0027302 | 0.0015338 | -0.0012513 | 0.0033047 | 0.068701 | 0.065373 | -0.0013714 | 0.016932 | -0.0023606 | 0.32044 | 122.4106 | -0.22888 | 121.994 | 0.086975 | -0.032043 | -0.036621 | 0.23804 | 122.2321 | -0.21057 | 122.1405 | 0.064087 | -0.041199 | 0.064087 | -0.045777 | 0.15106 | -0.2655 | 0.27008 | 0.14648 | 0.15106 | 0.19226 | 0.19684 | -0.027466 | -0.027465 | -0.11902 | 0.24719 | 0.24719 | 0.14191 | 0.27466 | 0.16937 | 0.31586 | 122.2229 | 0.27466 | 122.3511 | 122.6395 | 122.4426 | 122.5937 | 122.4152 | -122.4884 | -122.4701 | 122.1771 | 122.3236 | 0.50354 | 0.42114
1228.6094 | 122.4838 | -0.16937 | 122.2458 | -0.0020601 | 0.0034585 | 0.06978 | 0.063948 | -0.0014377 | -0.001662 | 0.00067925 | -0.0012513 | 0.0033047 | 0.069769 | 0.064091 | -0.00030343 | 0.015436 | 0.000203 | 0.27924 | 122.3923 | -0.24261 | 121.9849 | 0.073242 | -0.036621 | -0.018311 | 0.26093 | 122.2412 | -0.20142 | 122.1863 | 0.09613 | 0.013733 | 0.10529 | -0.073242 | 0.14648 | -0.26093 | 0.24261 | 0.15106 | 0.13275 | 0.2243 | 0.20599 | -0.032043 | -0.004578 | -0.05951 | 0.2655 | 0.27466 | 0.18311 | 0.3067 | 0.21515 | 0.31586 | 122.2275 | 0.29755 | 122.3877 | 122.6349 | 122.4426 | 122.5616 | 122.4106 | -122.4884 | -122.4472 | 122.1542 | 122.3557 | 0.44861 | 0.4303
1230.2969 | 122.4838 | -0.15564 | 122.2687 | -0.0020601 | 0.0062357 | 0.070207 | 0.06523 | 0.0017667 | -0.003371 | -0.0012434 | -0.0012513 | 0.0037319 | 0.069342 | 0.070286 | 0.0037556 | 0.016718 | -0.0051376 | 0.33875 | 122.3969 | -0.22888 | 122.0123 | 0.091553 | -0.068665 | -0.032043 | 0.28381 | 122.3053 | -0.23346 | 122.2092 | 0.09613 | -0.022888 | 0.091553 | -0.073242 | 0.12817 | -0.25635 | 0.24719 | 0.1236 | 0.086975 | 0.19684 | 0.16022 | -0.077819 | 0.036621 | -0.05951 | 0.25177 | 0.24719 | 0.13275 | 0.32501 | 0.21057 | 0.32044 | 122.2412 | 0.32959 | 122.4426 | 122.6257 | 122.5388 | 122.5525 | 122.4609 | -122.4976 | -122.5021 | 122.168 | 122.3648 | 0.49439 | 0.43945
1232.0469 | 122.4335 | -0.19684 | 122.287 | 0.028458 | 0.0068765 | 0.071275 | 0.067366 | 0.0036893 | -0.0018756 | -0.00081595 | 0.014008 | 0.0060819 | 0.069556 | 0.059178 | -8.9634e-05 | 0.014795 | -0.0019332 | 0.3891 | 122.4564 | -0.28381 | 121.962 | 0.022888 | -0.11444 | -0.07782 | 0.27924 | 122.3007 | -0.21515 | 122.1313 | 0.013733 | -0.073242 | 0.041199 | -0.086975 | 0.16937 | -0.32501 | 0.21973 | 0.11902 | 0.082397 | 0.20599 | 0.16937 | -0.018311 | 0.013733 | -0.15564 | 0.21057 | 0.23804 | 0.1236 | 0.25635 | 0.14191 | 0.3067 | 122.2458 | 0.22888 | 122.3465 | 122.7402 | 122.5159 | 122.6532 | 122.4976 | -122.5708 | -122.5021 | 122.1588 | 122.3282 | 0.58594 | 0.47607
1233.7969 | 122.438 | -0.16479 | 122.2595 | 0.036087 | 0.0081583 | 0.073625 | 0.06758 | 0.0030483 | -0.00059378 | -0.0018842 | 0.017059 | 0.0045865 | 0.071478 | 0.062596 | -0.00030343 | 0.017359 | -0.0027878 | 0.35248 | 122.4243 | -0.24719 | 122.0169 | 0.1236 | -0.045776 | -0.018311 | 0.27924 | 122.2916 | -0.23346 | 122.168 | 0.068665 | -0.027466 | 0.086975 | -0.082397 | 0.16479 | -0.24261 | 0.28839 | 0.14648 | 0.11902 | 0.22888 | 0.20142 | -0.068664 | 0.032044 | -0.091552 | 0.23346 | 0.25177 | 0.13733 | 0.32043 | 0.20599 | 0.37079 | 122.2641 | 0.30212 | 122.4014 | 122.6715 | 122.525 | 122.5891 | 122.4564 | -122.5067 | -122.493 | 122.1817 | 122.3328 | 0.51727 | 0.44403
1235.5 | 122.4106 | -0.1831 | 122.2961 | 0.028458 | 0.0073037 | 0.071489 | 0.069075 | 0.00027134 | -0.003371 | 0.00046565 | 0.0079041 | 0.0077909 | 0.070624 | 0.061314 | 0.00097837 | 0.013941 | -0.0053512 | 0.40741 | 122.4335 | -0.27466 | 121.962 | 0.032043 | -0.10529 | -0.073242 | 0.25635 | 122.3053 | -0.23346 | 122.1176 | 0.018311 | -0.082397 | 0.036621 | -0.091553 | 0.13733 | -0.33417 | 0.21515 | 0.10986 | 0.077819 | 0.20142 | 0.16937 | -0.050354 | 0.009155 | -0.17853 | 0.20142 | 0.21973 | 0.10071 | 0.27008 | 0.15106 | 0.3067 | 122.2366 | 0.25177 | 122.3511 | 122.7081 | 122.5388 | 122.6166 | 122.4884 | -122.5708 | -122.5296 | 122.1451 | 122.3007 | 0.59052 | 0.43945
1237.2344 | 122.3877 | -0.18768 | 122.3053 | 0.0055694 | 0.0053811 | 0.070634 | 0.065443 | 0.0013393 | -0.0031574 | -0.00017515 | -0.0012513 | 0.0054409 | 0.071265 | 0.061741 | 0.001192 | 0.016718 | -0.000438 | 0.31586 | 122.438 | -0.26093 | 121.8796 | -0.059509 | -0.18768 | -0.15564 | 0.12817 | 122.3099 | -0.23804 | 122.0856 | -0.045776 | -0.16022 | 0.013733 | -0.073242 | 0.13275 | -0.42572 | 0.12817 | 0.032043 | 0 | 0.10529 | 0.073242 | -0.050354 | 0.004577 | -0.21973 | 0.14191 | 0.20142 | 0.027466 | 0.25177 | 0.07782 | 0.20142 | 122.1405 | 0.19226 | 122.3236 | 122.699 | 122.5479 | 122.6257 | 122.4976 | -122.5662 | -122.5433 | 122.0673 | 122.2733 | 0.50354 | 0.31586
1238.9844 | 122.3969 | -0.20142 | 122.2961 | -0.0096891 | 0.0049539 | 0.069353 | 0.064375 | -0.00015586 | -0.0037982 | -0.001457 | -0.0043029 | 0.0033047 | 0.069128 | 0.063237 | -0.0017986 | 0.014795 | -0.0030014 | 0.40283 | 122.4243 | -0.22888 | 121.9666 | 0.054932 | -0.068665 | -0.064087 | 0.21057 | 122.2916 | -0.23346 | 122.0947 | 0 | -0.09613 | 0.009155 | -0.027466 | 0.12817 | -0.32959 | 0.25635 | 0.13733 | 0.13275 | 0.16479 | 0.16022 | -0.032043 | -0.004578 | -0.20142 | 0.20142 | 0.21057 | 0.10529 | 0.24261 | 0.13733 | 0.28381 | 122.1954 | 0.23346 | 122.3282 | 122.6532 | 122.525 | 122.6257 | 122.493 | -122.525 | -122.5296 | 122.168 | 122.2961 | 0.60425 | 0.41199
1240.6719 | 122.4289 | -0.19226 | 122.2733 | -0.0020601 | 0.0043131 | 0.068498 | 0.063735 | 0.0034755 | -0.00508 | -0.003166 | -0.0043029 | 0.0039457 | 0.067419 | 0.060887 | -0.002226 | 0.016932 | -0.0044968 | 0.44861 | 122.3877 | -0.22888 | 121.9986 | 0.086975 | -0.045776 | -0.022888 | 0.25635 | 122.2687 | -0.19684 | 122.1313 | 0.045776 | -0.045776 | 0.059509 | -0.036621 | 0.11444 | -0.27466 | 0.27924 | 0.16937 | 0.14648 | 0.20599 | 0.18311 | -0.004577 | -0.004577 | -0.14191 | 0.23804 | 0.25177 | 0.14648 | 0.25635 | 0.15106 | 0.31586 | 122.2275 | 0.24261 | 122.3282 | 122.6166 | 122.4655 | 122.58 | 122.4609 | -122.5021 | -122.4701 | 122.1909 | 122.3236 | 0.64087 | 0.44861
1242.4219 | 122.4518 | -0.16022 | 122.2504 | 0.051346 | 0.0062357 | 0.072343 | 0.066084 | 0.0028347 | -0.00016658 | 0.0023882 | 0.017059 | 0.0039457 | 0.072546 | 0.073063 | 0.0037556 | 0.01565 | -0.001506 | 0.44403 | 122.3923 | -0.24261 | 122.0078 | 0.10986 | -0.059509 | -0.022888 | 0.24719 | 122.2961 | -0.2243 | 122.1725 | 0.054932 | -0.036621 | 0.073242 | -0.082398 | 0.14191 | -0.24262 | 0.27008 | 0.13733 | 0.10071 | 0.21973 | 0.18311 | -0.064087 | 0.045777 | -0.07782 | 0.21515 | 0.23346 | 0.1236 | 0.29755 | 0.18768 | 0.35248 | 122.2504 | 0.27924 | 122.3969 | 122.6349 | 122.5204 | 122.5525 | 122.4564 | -122.493 | -122.4747 | 122.168 | 122.3328 | 0.60425 | 0.40741
1244.1094 | 122.3785 | -0.2243 | 122.287 | -0.0020601 | 0.0053811 | 0.070207 | 0.066512 | 0.0015529 | -0.0057208 | -0.001457 | -0.0043029 | 0.0067227 | 0.069556 | 0.057682 | -0.003294 | 0.017145 | -0.0027878 | 0.45776 | 122.4014 | -0.24261 | 121.9208 | -0.013733 | -0.11902 | -0.10071 | 0.17395 | 122.2916 | -0.23346 | 122.0718 | -0.022888 | -0.11444 | -0.018311 | -0.018311 | 0.11444 | -0.36621 | 0.21057 | 0.1236 | 0.10529 | 0.14191 | 0.1236 | -0.009155 | 0.004578 | -0.21515 | 0.20142 | 0.20599 | 0.10986 | 0.21515 | 0.11902 | 0.22888 | 122.1634 | 0.21057 | 122.3053 | 122.644 | 122.525 | 122.6257 | 122.5159 | -122.5296 | -122.5204 | 122.1451 | 122.2961 | 0.68207 | 0.39825
1245.8594 | 122.4518 | -0.16022 | 122.2504 | 0.043716 | 0.0062357 | 0.071062 | 0.067366 | 0.0015529 | -0.0010212 | 0.00067925 | 0.023163 | 0.0058683 | 0.071265 | 0.065373 | 0.0026874 | 0.015223 | -0.0062058 | 0.49896 | 122.4106 | -0.23346 | 122.0306 | 0.11902 | -0.054932 | -0.018311 | 0.27466 | 122.287 | -0.23346 | 122.1588 | 0.054932 | -0.041199 | 0.07782 | -0.073242 | 0.16022 | -0.21973 | 0.27924 | 0.14191 | 0.10528 | 0.21515 | 0.17853 | -0.073242 | 0.036621 | -0.091553 | 0.21515 | 0.23804 | 0.11902 | 0.31128 | 0.19226 | 0.35248 | 122.2641 | 0.28839 | 122.3923 | 122.644 | 122.5204 | 122.5708 | 122.4472 | -122.4838 | -122.4838 | 122.1909 | 122.319 | 0.65918 | 0.43488
1247.6094 | 122.5159 | -0.15564 | 122.2824 | -0.0020601 | 0.0051675 | 0.069353 | 0.064803 | -0.0020787 | -0.0044392 | -0.0029524 | 0.0048523 | 0.0052273 | 0.068274 | 0.058537 | -0.0017986 | 0.016504 | -0.0010788 | 0.52185 | 122.3877 | -0.2243 | 122.0352 | 0.13275 | -0.013733 | 0.004578 | 0.28381 | 122.2595 | -0.18768 | 122.2 | 0.10986 | 0.032043 | 0.11444 | -0.068664 | 0.10528 | -0.24719 | 0.28839 | 0.16022 | 0.14191 | 0.22888 | 0.21057 | -0.032043 | -0.022889 | -0.082398 | 0.2655 | 0.27008 | 0.18768 | 0.30212 | 0.21973 | 0.35706 | 122.2595 | 0.29755 | 122.3877 | 122.612 | 122.4472 | 122.5433 | 122.4152 | -122.5067 | -122.4701 | 122.1909 | 122.3557 | 0.67749 | 0.43945
1249.3594 | 122.4609 | -0.16022 | 122.2916 | 0.036087 | 0.0068765 | 0.07213 | 0.064375 | -0.00036966 | -0.0025166 | 0.0013202 | 0.010956 | 0.0048001 | 0.071051 | 0.063023 | 0.0014056 | 0.014368 | 0.0023392 | 0.5127 | 122.4335 | -0.22888 | 121.9894 | 0.059509 | -0.086975 | -0.041199 | 0.1831 | 122.2824 | -0.21515 | 122.168 | 0.032043 | -0.054932 | 0.059509 | -0.068665 | 0.14191 | -0.30212 | 0.21973 | 0.11902 | 0.073242 | 0.18768 | 0.14191 | -0.054932 | -0.009155 | -0.1236 | 0.19226 | 0.21973 | 0.10528 | 0.27466 | 0.16022 | 0.28839 | 122.2183 | 0.24719 | 122.3831 | 122.6624 | 122.4976 | 122.5937 | 122.4426 | -122.5204 | -122.5067 | 122.1497 | 122.3282 | 0.67291 | 0.34332
1251.1094 | 122.4106 | -0.17853 | 122.2641 | 0.036087 | 0.0083719 | 0.070848 | 0.067152 | -0.00036966 | -0.0023028 | -0.00038875 | 0.0079041 | 0.0050137 | 0.067847 | 0.062169 | 0.00033757 | 0.012873 | 0.0008438 | 0.62714 | 122.4747 | -0.28381 | 121.9894 | 0.032043 | -0.086975 | -0.07782 | 0.2655 | 122.3236 | -0.21973 | 122.1176 | 0.022888 | -0.07782 | 0.050354 | -0.10528 | 0.21057 | -0.27466 | 0.21057 | 0.10071 | 0.091553 | 0.20599 | 0.19684 | -0.041199 | 0.059509 | -0.14648 | 0.20142 | 0.22888 | 0.10071 | 0.27008 | 0.14191 | 0.31586 | 122.2733 | 0.24261 | 122.3373 | 122.7585 | 122.5433 | 122.6532 | 122.5021 | -122.5479 | -122.4838 | 122.168 | 122.2961 | 0.80566 | 0.44403
1252.8906 | 122.3602 | -0.18768 | 122.3007 | 0.0055694 | 0.0062357 | 0.071489 | 0.065657 | 0.0015529 | -0.0027302 | -0.00060235 | -0.0043029 | 0.0048001 | 0.070196 | 0.056401 | 0.00033757 | 0.016077 | -0.0034286 | 0.63629 | 122.4426 | -0.23804 | 121.9025 | -0.073242 | -0.20599 | -0.17395 | 0.13275 | 122.319 | -0.23804 | 122.0947 | -0.086975 | -0.16022 | -0.004578 | -0.050354 | 0.14191 | -0.39825 | 0.11444 | 0.013733 | -0.018311 | 0.064087 | 0.032043 | -0.050354 | 0.018311 | -0.20599 | 0.10071 | 0.1831 | 0.027466 | 0.23346 | 0.07782 | 0.16479 | 122.1405 | 0.15106 | 122.3328 | 122.6807 | 122.5571 | 122.6303 | 122.5067 | -122.5388 | -122.5388 | 122.0901 | 122.2824 | 0.82397 | 0.32043
1254.6562 | 122.493 | -0.15106 | 122.2961 | -0.0020601 | 0.0060221 | 0.070207 | 0.06288 | 0.0026211 | -0.0035846 | 0.0011066 | -0.0012513 | 0.0041593 | 0.070196 | 0.061314 | -0.0017986 | 0.014368 | -0.003856 | 0.737 | 122.3923 | -0.19684 | 122.0352 | 0.1236 | -0.027466 | 0.004578 | 0.28381 | 122.2458 | -0.1831 | 122.1817 | 0.10986 | 0.013733 | 0.082397 | -0.045776 | 0.09613 | -0.26093 | 0.27466 | 0.15564 | 0.1236 | 0.20142 | 0.16937 | -0.032043 | -0.050354 | -0.11444 | 0.26093 | 0.23346 | 0.16479 | 0.2655 | 0.19684 | 0.32043 | 122.2321 | 0.29297 | 122.3648 | 122.5891 | 122.4289 | 122.5433 | 122.3969 | -122.493 | -122.4792 | 122.1863 | 122.3328 | 0.88806 | 0.43488
1256.4062 | 122.4426 | -0.16022 | 122.287 | 0.043716 | 0.0081583 | 0.072771 | 0.064803 | 0.0062527 | -0.0020892 | -0.0016706 | 0.010956 | 0.0045865 | 0.072333 | 0.067296 | -8.9634e-05 | 0.016077 | 0.001271 | 0.7782 | 122.438 | -0.24719 | 122.0078 | 0.11444 | -0.050354 | -0.027466 | 0.22888 | 122.2961 | -0.20599 | 122.1634 | 0.050354 | -0.032043 | 0.073242 | -0.086975 | 0.15106 | -0.27924 | 0.27466 | 0.13275 | 0.10986 | 0.21973 | 0.19684 | -0.045777 | 0.009156 | -0.1236 | 0.21057 | 0.23346 | 0.12817 | 0.27924 | 0.17395 | 0.36163 | 122.2549 | 0.25635 | 122.3694 | 122.6852 | 122.5021 | 122.5983 | 122.4564 | -122.5342 | -122.493 | 122.168 | 122.3236 | 0.93841 | 0.3891
1258.1094 | 122.374 | -0.1831 | 122.3099 | -0.0020601 | 0.0053811 | 0.070207 | 0.070357 | 0.0039029 | -0.0029438 | -0.00017515 | 0.0018005 | 0.0062955 | 0.07041 | 0.059178 | -0.00094423 | 0.016077 | -0.0006516 | 0.85602 | 122.4747 | -0.25635 | 121.8979 | -0.064087 | -0.20142 | -0.15106 | 0.11902 | 122.3373 | -0.23346 | 122.1085 | -0.059509 | -0.15106 | 0.004578 | -0.073243 | 0.16479 | -0.41199 | 0.11902 | 0.032043 | -0.018311 | 0.10529 | 0.054932 | -0.050354 | 0.027466 | -0.20142 | 0.1236 | 0.18768 | 0.032043 | 0.23804 | 0.082397 | 0.19226 | 122.1542 | 0.17395 | 122.3419 | 122.731 | 122.5708 | 122.6578 | 122.5204 | -122.5662 | -122.5433 | 122.081 | 122.2916 | 1.0391 | 0.30212
1259.8594 | 122.3877 | -0.20142 | 122.3007 | 0.058975 | 0.0068765 | 0.070848 | 0.064803 | 0.0028347 | -0.0012348 | 0.0021746 | 0.014008 | 0.0054409 | 0.071265 | 0.068577 | -0.0024396 | 0.015436 | -0.003215 | 1.0117 | 122.493 | -0.3067 | 121.9345 | -0.004578 | -0.1236 | -0.082397 | 0.17853 | 122.3465 | -0.26093 | 122.0856 | -0.022888 | -0.12817 | 0.009155 | -0.10529 | 0.19226 | -0.36621 | 0.19684 | 0.11902 | 0.07782 | 0.2243 | 0.18311 | -0.059509 | 0.045777 | -0.21515 | 0.17853 | 0.21057 | 0.073242 | 0.27008 | 0.13275 | 0.30212 | 122.2412 | 0.23804 | 122.3465 | 122.7997 | 122.6074 | 122.6944 | 122.5479 | -122.6074 | -122.5616 | 122.1359 | 122.287 | 1.2131 | 0.37994
1261.5469 | 122.4014 | -0.18768 | 122.3099 | 0.0055694 | 0.0049539 | 0.071489 | 0.064162 | -0.00015586 | -0.0046528 | -0.0010298 | -0.0012513 | 0.0033047 | 0.071905 | 0.064305 | -0.0028668 | 0.01565 | -0.0030014 | 1.149 | 122.4243 | -0.2243 | 121.9803 | 0.073242 | -0.059509 | -0.041199 | 0.21515 | 122.2778 | -0.20142 | 122.1222 | 0.018311 | -0.068665 | 0.036621 | -0.036621 | 0.11444 | -0.32959 | 0.26092 | 0.14648 | 0.12817 | 0.18311 | 0.16479 | -0.013733 | -0.032043 | -0.18768 | 0.20599 | 0.2243 | 0.11902 | 0.23804 | 0.13275 | 0.29755 | 122.2046 | 0.21973 | 122.3236 | 122.6486 | 122.4792 | 122.612 | 122.4655 | -122.5342 | -122.5113 | 122.168 | 122.3099 | 1.3367 | 0.40283
1263.2344 | 122.374 | -0.1831 | 122.3282 | 0.013199 | 0.0055947 | 0.070634 | 0.068007 | -0.00036966 | -0.0027302 | 0.0013202 | -0.0012513 | 0.0075771 | 0.068915 | 0.062809 | 0.00012397 | 0.015009 | -0.0068466 | 1.3229 | 122.4609 | -0.23804 | 121.9482 | 0.013733 | -0.15564 | -0.11902 | 0.18768 | 122.3328 | -0.21515 | 122.113 | -0.022888 | -0.14191 | 0.009155 | -0.054932 | 0.13275 | -0.37994 | 0.19684 | 0.064086 | 0.027465 | 0.11902 | 0.082397 | -0.032044 | 0.004578 | -0.21515 | 0.16022 | 0.19226 | 0.041198 | 0.2243 | 0.073242 | 0.25177 | 122.1863 | 0.19226 | 122.3282 | 122.699 | 122.5479 | 122.644 | 122.5159 | -122.5662 | -122.5433 | 122.1313 | 122.2961 | 1.506 | 0.37079
1264.9844 | 122.3785 | -0.19684 | 122.287 | 0.0055694 | 0.0045267 | 0.070207 | 0.065657 | -0.0014377 | -0.0029438 | 0.00046565 | -0.0012513 | 0.0069363 | 0.068274 | 0.05576 | -0.0011578 | 0.016504 | -0.0040696 | 1.3458 | 122.4472 | -0.25177 | 121.9208 | -0.009155 | -0.12817 | -0.10071 | 0.16022 | 122.3099 | -0.22888 | 122.0856 | -0.027466 | -0.10986 | -0.013733 | -0.054932 | 0.16022 | -0.36621 | 0.18768 | 0.09613 | 0.068664 | 0.15106 | 0.1236 | -0.032044 | 0.022888 | -0.20142 | 0.16937 | 0.18311 | 0.086975 | 0.21515 | 0.11902 | 0.24261 | 122.1725 | 0.20142 | 122.3145 | 122.699 | 122.5388 | 122.644 | 122.5067 | -122.5388 | -122.5159 | 122.1176 | 122.2824 | 1.5427 | 0.35706
1266.6562 | 122.4747 | -0.13733 | 122.2961 | -0.0096891 | 0.0066629 | 0.071916 | 0.065871 | 0.0028347 | -0.0052936 | -0.002525 | -0.0043029 | 0.0071499 | 0.068701 | 0.074772 | 0.0048236 | 0.01565 | -0.0047104 | 1.387 | 122.4518 | -0.24719 | 121.9711 | 0.009155 | -0.14191 | -0.086975 | 0.21057 | 122.3053 | -0.21057 | 122.2 | 0.068665 | -0.041199 | 0.10529 | -0.10986 | 0.15564 | -0.32501 | 0.14648 | 0.050354 | -0.004578 | 0.16022 | 0.10528 | -0.073242 | 0.009155 | -0.096131 | 0.20599 | 0.24262 | 0.09613 | 0.31586 | 0.16937 | 0.25635 | 122.2183 | 0.27924 | 122.4106 | 122.699 | 122.5159 | 122.5891 | 122.4426 | -122.5433 | -122.5067 | 122.1085 | 122.3373 | 1.5244 | 0.3479
1268.4062 | 122.5204 | -0.14648 | 122.2549 | 0.0055694 | 0.0038857 | 0.068925 | 0.062666 | -0.0040013 | -0.0044392 | -0.00038875 | -0.0012513 | 0.0035183 | 0.066992 | 0.063664 | -0.0011578 | 0.015009 | -0.0006516 | 1.474 | 122.4197 | -0.21973 | 122.0398 | 0.15106 | -0.004578 | 0.009155 | 0.29755 | 122.2733 | -0.1831 | 122.2 | 0.13275 | 0.027466 | 0.10986 | -0.073243 | 0.1648 | -0.21515 | 0.29755 | 0.15564 | 0.14191 | 0.22888 | 0.21515 | -0.036621 | 0.01831 | -0.054932 | 0.27924 | 0.25635 | 0.17395 | 0.29297 | 0.21057 | 0.37079 | 122.2595 | 0.31586 | 122.3831 | 122.6395 | 122.4564 | 122.5662 | 122.4197 | -122.4747 | -122.438 | 122.1863 | 122.3465 | 1.6205 | 0.44403
1270.1094 | 122.3785 | -0.19226 | 122.2916 | 0.0055694 | 0.0068765 | 0.067644 | 0.069502 | 0.0024075 | -0.003371 | 0.00089285 | 0.0018005 | 0.0062955 | 0.070624 | 0.058537 | 0.00076477 | 0.015223 | -0.0023606 | 1.5518 | 122.4426 | -0.26093 | 121.9208 | -0.009155 | -0.17395 | -0.13275 | 0.17853 | 122.3419 | -0.22888 | 122.113 | -0.036621 | -0.13733 | 0.009155 | -0.068664 | 0.15106 | -0.37079 | 0.18311 | 0.05951 | 0.018311 | 0.12817 | 0.086975 | -0.036621 | 0.050354 | -0.17853 | 0.15564 | 0.20142 | 0.054932 | 0.23804 | 0.091553 | 0.25177 | 122.1817 | 0.19226 | 122.3419 | 122.7036 | 122.5708 | 122.6349 | 122.5342 | -122.5525 | -122.5204 | 122.113 | 122.3053 | 1.7441 | 0.37079
1271.8438 | 122.4609 | -0.17395 | 122.2916 | 0.0055694 | 0.0043131 | 0.071062 | 0.066084 | -0.00036966 | 0.00068782 | -0.0012434 | 0.010956 | 0.0039457 | 0.070624 | 0.058964 | 0.00055117 | 0.015864 | 0.0025528 | 1.561 | 122.4335 | -0.24261 | 121.9757 | 0.050354 | -0.09613 | -0.054932 | 0.17853 | 122.287 | -0.21973 | 122.1405 | 0.036621 | -0.068665 | 0.073242 | -0.068665 | 0.14191 | -0.31586 | 0.2243 | 0.11902 | 0.07782 | 0.18768 | 0.14649 | -0.045777 | -0.004578 | -0.15106 | 0.21057 | 0.24719 | 0.10528 | 0.29297 | 0.15106 | 0.29297 | 122.2183 | 0.25635 | 122.3602 | 122.6761 | 122.5067 | 122.6074 | 122.4609 | -122.5342 | -122.5113 | 122.1497 | 122.3145 | 1.7349 | 0.35248
1273.5312 | 122.5021 | -0.14648 | 122.2733 | -0.0020601 | 0.0055947 | 0.069353 | 0.065016 | -0.0012241 | -0.0035846 | -0.0012434 | -0.0012513 | 0.0024503 | 0.067847 | 0.069004 | -0.0011578 | 0.015223 | -0.0008652 | 1.712 | 122.374 | -0.22888 | 122.0398 | 0.14648 | -0.027466 | -0.013733 | 0.29755 | 122.287 | -0.19226 | 122.2092 | 0.10529 | 0.027466 | 0.10986 | -0.082398 | 0.10071 | -0.23346 | 0.29297 | 0.13275 | 0.11902 | 0.21515 | 0.20142 | -0.045777 | 0.013733 | -0.064087 | 0.25177 | 0.25635 | 0.17395 | 0.30212 | 0.21973 | 0.37537 | 122.2687 | 0.29755 | 122.4014 | 122.6028 | 122.4792 | 122.5204 | 122.4335 | -122.5021 | -122.4655 | 122.1863 | 122.3557 | 1.8585 | 0.44403
1275.2188 | 122.5113 | -0.15106 | 122.2733 | -0.0020601 | 0.0053811 | 0.068712 | 0.062239 | -0.0016513 | -0.00080758 | -0.00060235 | 0.0079041 | 0.0050137 | 0.069983 | 0.069645 | -8.9634e-05 | 0.013514 | -0.0010788 | 1.7166 | 122.4243 | -0.22888 | 121.9894 | 0.064087 | -0.064087 | -0.032043 | 0.2243 | 122.287 | -0.19226 | 122.1954 | 0.09613 | 0.013733 | 0.10986 | -0.07782 | 0.15106 | -0.28381 | 0.21515 | 0.11902 | 0.086975 | 0.19684 | 0.16479 | -0.041199 | 0.013733 | -0.077819 | 0.24719 | 0.26093 | 0.16479 | 0.30212 | 0.20599 | 0.29297 | 122.2183 | 0.28839 | 122.3877 | 122.6532 | 122.4792 | 122.5754 | 122.438 | -122.5021 | -122.4655 | 122.1405 | 122.3465 | 1.8677 | 0.37537
1276.9688 | 122.3785 | -0.19226 | 122.3145 | -0.0096891 | 0.0077311 | 0.070848 | 0.068007 | -0.00058326 | -0.0031574 | 0.00046565 | -0.0012513 | 0.0065091 | 0.070837 | 0.059178 | 0.0033282 | 0.014155 | -0.0012924 | 1.7487 | 122.4792 | -0.25177 | 121.9025 | -0.064087 | -0.21057 | -0.15106 | 0.1236 | 122.3419 | -0.2243 | 122.0856 | -0.054932 | -0.16022 | 0.004578 | -0.059509 | 0.16479 | -0.41199 | 0.12817 | 0.041199 | -0.01831 | 0.10071 | 0.041199 | -0.032043 | 0.027466 | -0.22888 | 0.13733 | 0.19684 | 0.032044 | 0.22888 | 0.064087 | 0.18768 | 122.1542 | 0.16937 | 122.3099 | 122.731 | 122.5662 | 122.6715 | 122.5342 | -122.5662 | -122.5388 | 122.0947 | 122.2778 | 1.9409 | 0.31586
1278.7188 | 122.3785 | -0.19684 | 122.2961 | 0.0055694 | 0.0081583 | 0.073625 | 0.066939 | 0.0051845 | -0.0018756 | -0.001457 | 0.0018005 | 0.0073635 | 0.071692 | 0.062382 | 0.00097837 | 0.015009 | -0.0023606 | 1.8814 | 122.493 | -0.26093 | 121.8979 | -0.07782 | -0.20599 | -0.16479 | 0.15564 | 122.3328 | -0.21057 | 122.0993 | -0.059509 | -0.15564 | 0 | -0.064087 | 0.19684 | -0.39826 | 0.11902 | 0.032043 | -0.009156 | 0.09613 | 0.054931 | -0.013733 | 0.036621 | -0.19684 | 0.13733 | 0.19684 | 0.041198 | 0.21057 | 0.054931 | 0.18311 | 122.1588 | 0.15106 | 122.3099 | 122.7539 | 122.5433 | 122.6898 | 122.5296 | -122.5571 | -122.5067 | 122.0947 | 122.2961 | 2.0782 | 0.35248
1280.4219 | 122.3923 | -0.17853 | 122.3007 | 0.013199 | 0.0068765 | 0.071275 | 0.065657 | 0.0041165 | -0.0014484 | 0.0015338 | 0.0018005 | 0.0054409 | 0.072119 | 0.057255 | 0.00076477 | 0.015436 | -0.001506 | 1.9272 | 122.438 | -0.26093 | 121.9666 | 0.022888 | -0.10986 | -0.086975 | 0.21515 | 122.3236 | -0.21515 | 122.1359 | -0.009155 | -0.11902 | 0.032043 | -0.082397 | 0.13733 | -0.33417 | 0.20142 | 0.091553 | 0.068665 | 0.17395 | 0.15106 | -0.036621 | 0.022888 | -0.16479 | 0.16937 | 0.21057 | 0.059509 | 0.24719 | 0.09613 | 0.28381 | 122.2275 | 0.20599 | 122.3511 | 122.699 | 122.5388 | 122.6166 | 122.5021 | -122.5616 | -122.5159 | 122.1451 | 122.3145 | 2.1057 | 0.39368
1282.1094 | 122.374 | -0.19226 | 122.319 | -0.0020601 | 0.0073037 | 0.071275 | 0.069716 | 0.0019803 | -0.0014484 | 0.00046565 | -0.0043029 | 0.0054409 | 0.07041 | 0.063023 | 0.001192 | 0.015223 | -1.0598e-05 | 2.0004 | 122.5067 | -0.25635 | 121.907 | -0.064087 | -0.19226 | -0.13733 | 0.14191 | 122.3419 | -0.2243 | 122.1176 | -0.059509 | -0.15106 | 0 | -0.064087 | 0.18768 | -0.41199 | 0.12817 | 0.054932 | 0 | 0.11902 | 0.064087 | -0.032043 | 0.022888 | -0.20142 | 0.13275 | 0.19226 | 0.041199 | 0.2243 | 0.073242 | 0.19226 | 122.1634 | 0.16479 | 122.3419 | 122.7631 | 122.5662 | 122.699 | 122.5342 | -122.5754 | -122.5433 | 122.0993 | 122.3099 | 2.1927 | 0.33417
1283.8594 | 122.4472 | -0.16022 | 122.3053 | 0.0055694 | 0.0040995 | 0.071275 | 0.064803 | 0.0041165 | -0.0046528 | 3.8448e-05 | 0.0048523 | 0.0030911 | 0.06806 | 0.060246 | 0.00097837 | 0.017573 | -0.0023606 | 2.0874 | 122.4152 | -0.23346 | 121.9849 | 0.036621 | -0.082397 | -0.050354 | 0.19226 | 122.3145 | -0.21057 | 122.1497 | 0.045776 | -0.054932 | 0.050354 | -0.073242 | 0.10986 | -0.32043 | 0.19684 | 0.10986 | 0.07782 | 0.1831 | 0.15106 | -0.050354 | 0.009155 | -0.15564 | 0.20599 | 0.21057 | 0.10528 | 0.26093 | 0.15564 | 0.27008 | 122.2183 | 0.25635 | 122.3602 | 122.6486 | 122.525 | 122.5754 | 122.4747 | -122.5388 | -122.5159 | 122.1451 | 122.3099 | 2.2476 | 0.35248
1285.625 | 122.4152 | -0.16479 | 122.3373 | -0.0020601 | 0.0055947 | 0.069353 | 0.065443 | -0.0029331 | -0.0023028 | 3.8448e-05 | -0.0012513 | 0.0033047 | 0.068488 | 0.062169 | -0.0013714 | 0.014368 | -0.0019332 | 2.2156 | 122.4106 | -0.23804 | 122.0032 | 0.086975 | -0.050354 | -0.032043 | 0.25635 | 122.3053 | -0.19226 | 122.1405 | 0.036621 | -0.064087 | 0.041199 | -0.073242 | 0.073242 | -0.33417 | 0.25177 | 0.13275 | 0.11444 | 0.20599 | 0.18768 | -0.027466 | -0.032043 | -0.19684 | 0.20142 | 0.20599 | 0.10071 | 0.23346 | 0.12817 | 0.32501 | 122.2412 | 0.22888 | 122.3328 | 122.6486 | 122.4976 | 122.5754 | 122.4701 | -122.5754 | -122.5296 | 122.168 | 122.3053 | 2.3804 | 0.42114
1287.3594 | 122.3877 | -0.19226 | 122.3099 | 0.0055694 | 0.0073037 | 0.068498 | 0.067793 | 0.0013393 | -0.0029438 | -0.00017515 | 0.0018005 | 0.0056545 | 0.070837 | 0.062169 | 0.001833 | 0.015009 | -0.0010788 | 2.2202 | 122.4655 | -0.25635 | 121.8933 | -0.059509 | -0.1831 | -0.13733 | 0.13275 | 122.3328 | -0.21057 | 122.1039 | -0.059509 | -0.15106 | 0.004578 | -0.064087 | 0.15564 | -0.41656 | 0.13275 | 0.054932 | 0.009156 | 0.11902 | 0.073243 | -0.01831 | 0.022889 | -0.20599 | 0.13275 | 0.19684 | 0.041199 | 0.21515 | 0.059509 | 0.19684 | 122.1497 | 0.15106 | 122.3145 | 122.7219 | 122.5433 | 122.6578 | 122.525 | -122.5662 | -122.5204 | 122.0856 | 122.2961 | 2.4124 | 0.32501
1289.1094 | 122.5204 | -0.13733 | 122.2916 | 0.0055694 | 0.0053811 | 0.071916 | 0.065657 | 0.0032619 | -0.0010212 | -0.0023114 | -0.0012513 | 0.0043729 | 0.068915 | 0.062596 | 0.0037556 | 0.017359 | -0.0010788 | 2.2476 | 122.4335 | -0.21515 | 122.0261 | 0.10071 | -0.064087 | -0.036621 | 0.27466 | 122.3099 | -0.17853 | 122.2275 | 0.091553 | -0.004578 | 0.10986 | -0.07782 | 0.14191 | -0.2655 | 0.23804 | 0.10071 | 0.073242 | 0.17853 | 0.15106 | -0.041199 | 0.01831 | -0.064087 | 0.22888 | 0.24719 | 0.13275 | 0.28839 | 0.17395 | 0.31586 | 122.2412 | 0.27008 | 122.406 | 122.6486 | 122.4884 | 122.5708 | 122.4472 | -122.5067 | -122.4701 | 122.1634 | 122.3648 | 2.3849 | 0.41199
1290.875 | 122.4655 | -0.16937 | 122.2961 | 0.020828 | 0.0045267 | 0.070207 | 0.066725 | 0.0021939 | -0.0029438 | -0.0012434 | 0.010956 | 0.0050137 | 0.069556 | 0.057682 | 0.002901 | 0.017145 | -0.0036422 | 2.3804 | 122.4609 | -0.21973 | 121.994 | 0.073242 | -0.082397 | -0.032043 | 0.20599 | 122.3099 | -0.22888 | 122.168 | 0.041199 | -0.050354 | 0.059509 | -0.050354 | 0.16479 | -0.30212 | 0.24261 | 0.13733 | 0.086976 | 0.18768 | 0.13733 | -0.059509 | 0.013732 | -0.12817 | 0.21057 | 0.22888 | 0.11902 | 0.28839 | 0.17853 | 0.29297 | 122.2137 | 0.27008 | 122.3969 | 122.6807 | 122.5388 | 122.6303 | 122.4792 | -122.5159 | -122.525 | 122.1634 | 122.3373 | 2.5497 | 0.37537
1292.6406 | 122.493 | -0.15564 | 122.2778 | -0.0020601 | 0.0066629 | 0.069994 | 0.066084 | -0.0010105 | -0.0048664 | -0.00017515 | -0.0043029 | 0.0035183 | 0.069342 | 0.0658 | -0.0020122 | 0.014795 | 0.0042618 | 2.3804 | 122.4243 | -0.22888 | 121.9849 | 0.050354 | -0.059509 | -0.032043 | 0.22888 | 122.3053 | -0.21515 | 122.1954 | 0.082397 | 0.004578 | 0.10071 | -0.073242 | 0.14648 | -0.29297 | 0.20599 | 0.1236 | 0.096131 | 0.19684 | 0.16937 | -0.059509 | 0.027466 | -0.082397 | 0.23804 | 0.25635 | 0.16022 | 0.31586 | 0.21973 | 0.27924 | 122.2137 | 0.29755 | 122.4106 | 122.6532 | 122.5204 | 122.58 | 122.4609 | -122.5067 | -122.493 | 122.1405 | 122.3511 | 2.536 | 0.38452
1294.3281 | 122.5113 | -0.14648 | 122.2824 | -0.0020601 | 0.0055947 | 0.070421 | 0.064803 | -0.0031467 | -0.0037982 | -0.0010298 | -0.0012513 | 0.0045865 | 0.068488 | 0.067082 | -0.001585 | 0.018213 | 0.0010574 | 2.4811 | 122.406 | -0.2243 | 121.9986 | 0.082397 | -0.032043 | -0.018311 | 0.26093 | 122.3053 | -0.18768 | 122.2183 | 0.082397 | 0.013733 | 0.10071 | -0.07782 | 0.1236 | -0.28381 | 0.22888 | 0.12817 | 0.11444 | 0.20599 | 0.19226 | -0.041199 | 0.022888 | -0.064087 | 0.22888 | 0.24719 | 0.16022 | 0.28839 | 0.20142 | 0.3067 | 122.2229 | 0.27008 | 122.406 | 122.6303 | 122.493 | 122.5525 | 122.4518 | -122.5067 | -122.4701 | 122.1451 | 122.3648 | 2.6276 | 0.40741
1296.0938 | 122.4014 | -0.17853 | 122.3007 | 0.0055694 | 0.0066629 | 0.069353 | 0.063735 | -0.00058326 | -0.0029438 | -0.0016706 | -0.0012513 | 0.0041593 | 0.069556 | 0.069859 | -0.0024396 | 0.015009 | -0.002147 | 2.7145 | 122.4197 | -0.2243 | 121.9894 | 0.059509 | -0.07782 | -0.064087 | 0.21973 | 122.3053 | -0.22888 | 122.113 | -0.004578 | -0.09613 | -0.009155 | -0.045776 | 0.11902 | -0.31128 | 0.23804 | 0.11444 | 0.10071 | 0.16022 | 0.14648 | -0.050354 | 0.004578 | -0.18768 | 0.17395 | 0.16937 | 0.082398 | 0.21973 | 0.13275 | 0.28381 | 122.2137 | 0.2243 | 122.3419 | 122.644 | 122.5342 | 122.5983 | 122.4838 | -122.525 | -122.5296 | 122.168 | 122.2916 | 2.8931 | 0.39826
1297.8438 | 122.4747 | -0.16937 | 122.3099 | 0.036087 | 0.0060221 | 0.07213 | 0.065657 | -0.0010105 | -0.003371 | -0.0018842 | 0.014008 | 0.0043729 | 0.071051 | 0.064946 | -0.00051703 | 0.017145 | 0.001271 | 2.8244 | 122.4197 | -0.25635 | 122.0215 | 0.09613 | -0.073242 | -0.027466 | 0.2243 | 122.319 | -0.2243 | 122.168 | 0.045776 | -0.045776 | 0.068665 | -0.086975 | 0.10986 | -0.28839 | 0.2655 | 0.14191 | 0.096131 | 0.22888 | 0.18311 | -0.054931 | 0.009156 | -0.14191 | 0.21515 | 0.23804 | 0.1236 | 0.29297 | 0.17853 | 0.35248 | 122.2778 | 0.27008 | 122.3923 | 122.6761 | 122.5433 | 122.5891 | 122.4884 | -122.5662 | -122.5342 | 122.1909 | 122.3373 | 2.9938 | 0.39368
1299.6094 | 122.3557 | -0.1831 | 122.3419 | 0.0055694 | 0.0055947 | 0.072557 | 0.068648 | 0.0032619 | -0.003371 | -0.0040204 | 0.0048523 | 0.0065091 | 0.070837 | 0.05341 | 0.0020466 | 0.014795 | -0.0040696 | 2.9663 | 122.5021 | -0.24261 | 121.9208 | -0.045776 | -0.1831 | -0.15564 | 0.12817 | 122.3373 | -0.21515 | 122.0901 | -0.064087 | -0.16479 | -0.013733 | -0.05951 | 0.16022 | -0.42114 | 0.13733 | 0.027465 | 0 | 0.086975 | 0.05951 | -0.032044 | -0.004578 | -0.25177 | 0.11902 | 0.16937 | 0.01831 | 0.20142 | 0.050354 | 0.19684 | 122.1634 | 0.15106 | 122.3053 | 122.7448 | 122.5525 | 122.6852 | 122.5204 | -122.5845 | -122.5571 | 122.1039 | 122.2733 | 3.1494 | 0.31128
1301.3594 | 122.3877 | -0.19684 | 122.3282 | -0.0020601 | 0.0036721 | 0.068925 | 0.06523 | 0.0039029 | -0.0057208 | 0.00025205 | 0.0018005 | 0.0062955 | 0.068488 | 0.067509 | -0.0043622 | 0.015009 | -0.0017196 | 3.0762 | 122.4655 | -0.23804 | 121.9162 | -0.013733 | -0.13275 | -0.10986 | 0.20599 | 122.3877 | -0.27008 | 122.0856 | -0.041199 | -0.10986 | -0.009155 | -0.041199 | 0.13733 | -0.41199 | 0.18311 | 0.086975 | 0.064087 | 0.12817 | 0.10529 | -0.073243 | 0.059509 | -0.24262 | 0.15564 | 0.18768 | 0.086975 | 0.26093 | 0.16022 | 0.2243 | 122.1542 | 0.22888 | 122.3557 | 122.7036 | 122.6578 | 122.6624 | 122.5845 | -122.5662 | -122.5983 | 122.113 | 122.2824 | 3.273 | 0.40283
1303.0469 | 122.5021 | -0.14191 | 122.2916 | 0.066604 | 0.0049539 | 0.071489 | 0.067793 | 0.0047573 | -0.00080758 | 0.0017474 | 0.014008 | 0.0056545 | 0.070837 | 0.068577 | 0.00097837 | 0.016504 | 0.000203 | 3.4698 | 122.4701 | -0.25635 | 122.0673 | 0.16022 | -0.022888 | 0 | 0.32501 | 122.3328 | -0.21515 | 122.2321 | 0.10529 | -0.009155 | 0.10986 | -0.11444 | 0.17853 | -0.2243 | 0.30212 | 0.14191 | 0.11902 | 0.25635 | 0.23346 | -0.073242 | 0.041199 | -0.059509 | 0.24719 | 0.25177 | 0.13275 | 0.32501 | 0.20599 | 0.41657 | 122.3236 | 0.32044 | 122.4472 | 122.7264 | 122.5479 | 122.612 | 122.4747 | -122.5479 | -122.5067 | 122.2092 | 122.374 | 3.6118 | 0.46692
1304.7969 | 122.406 | -0.19226 | 122.3099 | 0.028458 | 0.0073037 | 0.069994 | 0.068861 | -0.0025059 | -0.0023028 | -0.0016706 | 0.010956 | 0.0069363 | 0.070837 | 0.058323 | 0.00055117 | 0.012873 | -0.0044968 | 3.8269 | 122.5021 | -0.29755 | 121.9299 | 0.013733 | -0.11444 | -0.091553 | 0.20142 | 122.3648 | -0.25177 | 122.1268 | -0.013733 | -0.11444 | 0.022888 | -0.10528 | 0.19226 | -0.37994 | 0.20599 | 0.10071 | 0.07782 | 0.20599 | 0.1831 | -0.059509 | 0.054932 | -0.18311 | 0.17853 | 0.21515 | 0.07782 | 0.27466 | 0.13733 | 0.31128 | 122.2275 | 0.23804 | 122.3785 | 122.7997 | 122.6166 | 122.6944 | 122.5571 | -122.6074 | -122.5616 | 122.1222 | 122.319 | 4.0192 | 0.39368
1306.4844 | 122.4655 | -0.16479 | 122.2824 | -0.0020601 | 0.0047403 | 0.070634 | 0.067366 | -0.00058326 | -0.0031574 | -0.003166 | -0.0012513 | 0.0065091 | 0.071478 | 0.059819 | 0.0014056 | 0.015864 | -0.0034286 | 4.1519 | 122.4838 | -0.25635 | 121.9437 | -0.009155 | -0.16479 | -0.10071 | 0.20142 | 122.2961 | -0.20142 | 122.1817 | 0.032043 | -0.059509 | 0.073242 | -0.091553 | 0.20142 | -0.33875 | 0.15564 | 0.064087 | 0 | 0.15564 | 0.091553 | -0.036621 | 0.013733 | -0.10071 | 0.19684 | 0.23804 | 0.10529 | 0.27466 | 0.14191 | 0.24719 | 122.2 | 0.23346 | 122.3831 | 122.7402 | 122.4976 | 122.6486 | 122.4609 | -122.5388 | -122.4838 | 122.1085 | 122.3465 | 4.3167 | 0.36621
1308.2344 | 122.4655 | -0.15564 | 122.2961 | 0.036087 | 0.0068765 | 0.071062 | 0.068221 | 5.774e-05 | -0.0025166 | -0.00081595 | 0.010956 | 0.0045865 | 0.071051 | 0.062382 | 0.001192 | 0.017359 | -0.0017196 | 4.66 | 122.4335 | -0.24261 | 122.0032 | 0.091553 | -0.045776 | -0.041199 | 0.22888 | 122.3328 | -0.21973 | 122.1771 | 0.050354 | -0.036621 | 0.064087 | -0.086975 | 0.13733 | -0.29297 | 0.24719 | 0.11444 | 0.10986 | 0.20142 | 0.19684 | -0.064087 | 0.036621 | -0.11902 | 0.20599 | 0.21973 | 0.11902 | 0.28381 | 0.18311 | 0.33417 | 122.2458 | 0.27008 | 122.3969 | 122.6761 | 122.5525 | 122.5891 | 122.4884 | -122.5388 | -122.5159 | 122.1588 | 122.3328 | 4.8157 | 0.38452
1310 | 122.5204 | -0.15106 | 122.2549 | -0.0096891 | 0.0058083 | 0.071703 | 0.065016 | 0.00048494 | -0.0042254 | -0.0020978 | 0.0048523 | 0.0026639 | 0.069556 | 0.074559 | 0.00461 | 0.015864 | -0.0053512 | 5.2734 | 122.4747 | -0.23804 | 122.0169 | 0.09613 | -0.073242 | -0.036621 | 0.28839 | 122.2916 | -0.1831 | 122.2458 | 0.07782 | -0.013733 | 0.1236 | -0.086975 | 0.21973 | -0.23804 | 0.24719 | 0.11444 | 0.07782 | 0.20142 | 0.16479 | -0.032043 | 0.036621 | -0.009155 | 0.22888 | 0.27466 | 0.13733 | 0.3067 | 0.16937 | 0.33417 | 122.2549 | 0.26092 | 122.4289 | 122.7127 | 122.4747 | 122.6257 | 122.4426 | -122.493 | -122.438 | 122.168 | 122.3969 | 5.4245 | 0.43945
1311.6875 | 122.4564 | -0.15564 | 122.287 | -0.0020601 | 0.0064493 | 0.070207 | 0.065443 | 0.00091214 | -0.00080758 | -0.001457 | -0.0073547 | 0.0054409 | 0.067847 | 0.066014 | 0.00012397 | 0.016718 | -0.0081284 | 5.3009 | 122.4838 | -0.23346 | 121.9437 | -0.004578 | -0.15564 | -0.10986 | 0.1831 | 122.3373 | -0.21057 | 122.1634 | 0.009155 | -0.09613 | 0.064087 | -0.077819 | 0.19684 | -0.34332 | 0.15106 | 0.045777 | 0 | 0.1236 | 0.077819 | -0.054931 | 0.050354 | -0.1236 | 0.16479 | 0.21973 | 0.05951 | 0.27466 | 0.11444 | 0.22888 | 122.1771 | 0.21973 | 122.374 | 122.7173 | 122.5479 | 122.6395 | 122.493 | -122.5204 | -122.4976 | 122.0993 | 122.319 | 5.4565 | 0.33874
1313.4219 | 122.4976 | -0.13733 | 122.2733 | 0.043716 | 0.0077311 | 0.071703 | 0.066512 | 0.0036893 | 0.00090142 | -0.0018842 | 0.017059 | 0.0056545 | 0.07041 | 0.063023 | 0.0026874 | 0.018 | 0.000203 | 5.7312 | 122.4518 | -0.24261 | 122.0856 | 0.15564 | -0.018311 | 0.004578 | 0.32501 | 122.319 | -0.21515 | 122.2183 | 0.10071 | -0.009155 | 0.10986 | -0.10529 | 0.17853 | -0.18768 | 0.29297 | 0.14191 | 0.11902 | 0.24719 | 0.2243 | -0.07782 | 0.045777 | -0.054931 | 0.23804 | 0.24719 | 0.12817 | 0.32501 | 0.20599 | 0.39826 | 122.3282 | 0.31586 | 122.4335 | 122.6944 | 122.5342 | 122.5891 | 122.4564 | -122.5159 | -122.4884 | 122.2229 | 122.3557 | 5.8685 | 0.46234
1315.1094 | 122.3831 | -0.21057 | 122.3328 | -0.0096891 | 0.0066629 | 0.069353 | 0.064803 | 0.0013393 | -0.0048664 | 0.00067925 | 0.0018005 | 0.0048001 | 0.070624 | 0.066655 | -0.0035076 | 0.013514 | -0.0064194 | 5.7724 | 122.4655 | -0.2243 | 121.962 | 0.027466 | -0.10529 | -0.091553 | 0.1831 | 122.3373 | -0.21515 | 122.1039 | -0.027466 | -0.09613 | 0 | -0.013733 | 0.13275 | -0.37079 | 0.23804 | 0.11902 | 0.10529 | 0.13275 | 0.11902 | -0.004578 | 0.004577 | -0.22888 | 0.18311 | 0.21057 | 0.11444 | 0.21515 | 0.11902 | 0.25177 | 122.1863 | 0.18768 | 122.319 | 122.6898 | 122.5525 | 122.6761 | 122.5479 | -122.5571 | -122.5479 | 122.1725 | 122.3145 | 5.983 | 0.39368
1316.8594 | 122.5067 | -0.17395 | 122.3007 | 0.0055694 | 0.0051675 | 0.070848 | 0.064162 | -0.0018649 | -0.0020892 | -0.0012434 | -0.0012513 | 0.0039457 | 0.069983 | 0.070286 | 0.00012397 | 0.016504 | -1.0598e-05 | 5.7816 | 122.438 | -0.2243 | 122.0032 | 0.086975 | -0.041199 | -0.027466 | 0.24719 | 122.3099 | -0.19684 | 122.1817 | 0.086975 | 0 | 0.10986 | -0.050354 | 0.13733 | -0.29755 | 0.26092 | 0.14648 | 0.13275 | 0.19684 | 0.18311 | -0.022888 | 0.009155 | -0.11902 | 0.26092 | 0.28381 | 0.17395 | 0.3067 | 0.19684 | 0.31128 | 122.2275 | 0.28381 | 122.3785 | 122.6624 | 122.5067 | 122.612 | 122.4838 | -122.525 | -122.4976 | 122.1771 | 122.3557 | 5.9555 | 0.42114
1318.6094 | 122.4243 | -0.17853 | 122.2916 | 0.036087 | 0.0073037 | 0.072984 | 0.066512 | 0.00069854 | -0.0020892 | 3.8448e-05 | 0.014008 | 0.0048001 | 0.071265 | 0.061741 | -0.0013714 | 0.016077 | -0.0027878 | 6.0974 | 122.4838 | -0.28381 | 121.994 | 0.041199 | -0.082397 | -0.073242 | 0.27924 | 122.3602 | -0.22888 | 122.1634 | 0.032043 | -0.073242 | 0.068665 | -0.10528 | 0.19226 | -0.29755 | 0.21973 | 0.10529 | 0.096131 | 0.21057 | 0.20142 | -0.050354 | 0.068664 | -0.12817 | 0.21057 | 0.24719 | 0.10529 | 0.29755 | 0.15564 | 0.32501 | 122.2778 | 0.26093 | 122.3923 | 122.7676 | 122.5891 | 122.6624 | 122.5388 | -122.5754 | -122.5204 | 122.1725 | 122.3419 | 6.2759 | 0.45776
1320.375 | 122.5525 | -0.16022 | 122.2778 | -0.0096891 | 0.0047403 | 0.069353 | 0.062453 | 0.0024075 | -0.0025166 | -0.0016706 | -0.0012513 | 0.0048001 | 0.070837 | 0.067936 | -8.9634e-05 | 0.015223 | -0.0030014 | 6.4774 | 122.3969 | -0.20599 | 122.049 | 0.16937 | 0 | 0.022888 | 0.32959 | 122.319 | -0.19226 | 122.2504 | 0.13733 | 0.022888 | 0.10986 | -0.045777 | 0.11902 | -0.22888 | 0.32959 | 0.1831 | 0.16022 | 0.22888 | 0.20599 | -0.032044 | 0.041199 | -0.027466 | 0.29755 | 0.27008 | 0.1831 | 0.30212 | 0.21515 | 0.37537 | 122.2549 | 0.32959 | 122.4426 | 122.6028 | 122.5113 | 122.5571 | 122.4792 | -122.4838 | -122.4701 | 122.2092 | 122.4106 | 6.6376 | 0.48981
1322.125 | 122.438 | -0.14191 | 122.2961 | 0.0055694 | 0.0058083 | 0.071703 | 0.065871 | 0.0015529 | -0.0025166 | -0.0016706 | -0.0012513 | 0.0071499 | 0.070837 | 0.062809 | 0.001192 | 0.015223 | -0.0023606 | 6.6422 | 122.493 | -0.25635 | 121.9437 | -0.004578 | -0.16479 | -0.11444 | 0.18768 | 122.3282 | -0.21057 | 122.168 | -0.004578 | -0.10986 | 0.045776 | -0.11444 | 0.19684 | -0.35248 | 0.13733 | 0.027466 | -0.022888 | 0.14191 | 0.091553 | -0.068664 | 0.032043 | -0.12817 | 0.13733 | 0.18768 | 0.032044 | 0.25635 | 0.10071 | 0.25177 | 122.2 | 0.20599 | 122.3785 | 122.7493 | 122.5388 | 122.6349 | 122.4701 | -122.5525 | -122.5067 | 122.0856 | 122.3099 | 6.7841 | 0.32959
1323.875 | 122.3923 | -0.18768 | 122.3373 | -0.0020601 | 0.0060221 | 0.06978 | 0.065016 | 0.0024075 | -0.0027302 | -0.001457 | 0.0048523 | 0.0052273 | 0.069769 | 0.061314 | -0.0020122 | 0.0133 | -0.0010788 | 7.0908 | 122.4426 | -0.26093 | 121.9345 | 0.018311 | -0.1236 | -0.10529 | 0.19684 | 122.3511 | -0.20142 | 122.0947 | -0.032043 | -0.11444 | 0 | -0.073242 | 0.10529 | -0.40283 | 0.20599 | 0.082397 | 0.064087 | 0.15564 | 0.13733 | -0.013733 | 0.013733 | -0.24261 | 0.15564 | 0.18768 | 0.073242 | 0.20142 | 0.086975 | 0.27924 | 122.1954 | 0.16937 | 122.2961 | 122.7036 | 122.5525 | 122.6303 | 122.5388 | -122.5983 | -122.5388 | 122.1222 | 122.2824 | 7.2784 | 0.38452
1325.6406 | 122.4838 | -0.14191 | 122.3053 | -0.0096891 | 0.0062357 | 0.069566 | 0.066939 | 0.0043301 | -0.0035846 | 0.0011066 | 0.0018005 | 0.0048001 | 0.071692 | 0.069432 | 0.0033282 | 0.01565 | 0.0021256 | 7.2693 | 122.493 | -0.23804 | 121.9528 | 0.027466 | -0.14648 | -0.10529 | 0.23346 | 122.3328 | -0.20142 | 122.1954 | 0.050354 | -0.054932 | 0.082397 | -0.09613 | 0.18768 | -0.35248 | 0.16937 | 0.036621 | -0.004577 | 0.13275 | 0.091553 | -0.059509 | 0.027466 | -0.10986 | 0.19226 | 0.2243 | 0.086975 | 0.28381 | 0.14648 | 0.2655 | 122.1909 | 0.25177 | 122.3969 | 122.731 | 122.5342 | 122.6349 | 122.4747 | -122.5433 | -122.5067 | 122.0947 | 122.3373 | 7.4112 | 0.37537
1327.375 | 122.5159 | -0.14648 | 122.2778 | -0.0020601 | 0.0062357 | 0.072557 | 0.064162 | 0.00091214 | -0.0029438 | 0.0011066 | 0.026215 | 0.0073635 | 0.069769 | 0.064305 | 0.0020466 | 0.016718 | -0.0059922 | 7.5623 | 122.4152 | -0.20599 | 122.0444 | 0.12817 | -0.022888 | 0.013733 | 0.34332 | 122.3511 | -0.21515 | 122.2412 | 0.09613 | -0.004578 | 0.11444 | -0.05951 | 0.13733 | -0.23346 | 0.27466 | 0.16022 | 0.1236 | 0.21973 | 0.18311 | -0.068665 | 0.073242 | -0.036621 | 0.24261 | 0.26093 | 0.14191 | 0.32959 | 0.21057 | 0.33417 | 122.2504 | 0.31128 | 122.4564 | 122.6212 | 122.5662 | 122.5616 | 122.4976 | -122.4838 | -122.493 | 122.1909 | 122.3877 | 7.7087 | 0.48981
1329.0625 | 122.5296 | -0.13733 | 122.2778 | 0.0055694 | 0.0034585 | 0.06978 | 0.06523 | -0.0012241 | -0.0029438 | -0.0016706 | -0.0012513 | 0.0030911 | 0.071692 | 0.068364 | 0.00055117 | 0.014795 | -0.0034286 | 7.5989 | 122.4197 | -0.20599 | 122.0306 | 0.14191 | -0.018311 | 0 | 0.3067 | 122.2916 | -0.19226 | 122.2366 | 0.10986 | 0.018311 | 0.11444 | -0.068665 | 0.14191 | -0.24719 | 0.27924 | 0.13733 | 0.11902 | 0.20599 | 0.18768 | -0.054932 | 0.013733 | -0.041199 | 0.24719 | 0.25177 | 0.15564 | 0.3067 | 0.21057 | 0.3479 | 122.2366 | 0.30212 | 122.4289 | 122.6257 | 122.4838 | 122.5571 | 122.4289 | -122.4838 | -122.4701 | 122.168 | 122.374 | 7.7362 | 0.44403
1330.8281 | 122.4426 | -0.15564 | 122.3282 | 0.020828 | 0.0077311 | 0.069994 | 0.068221 | 0.0030483 | -0.0023028 | -0.00081595 | 0.0079041 | 0.0062955 | 0.069769 | 0.055333 | -0.002226 | 0.012659 | -0.003215 | 8.0383 | 122.4838 | -0.25177 | 121.9894 | 0.09613 | -0.082397 | -0.059509 | 0.3067 | 122.3694 | -0.21057 | 122.1863 | 0.027466 | -0.082397 | 0.050354 | -0.09613 | 0.15564 | -0.33875 | 0.25177 | 0.096131 | 0.073243 | 0.19226 | 0.16937 | -0.054931 | 0.041199 | -0.14191 | 0.18311 | 0.20599 | 0.073243 | 0.26093 | 0.12817 | 0.3479 | 122.2412 | 0.23804 | 122.3969 | 122.7356 | 122.58 | 122.6395 | 122.525 | -122.58 | -122.5388 | 122.1451 | 122.3419 | 8.194 | 0.46234
1332.5156 | 122.3785 | -0.19226 | 122.3419 | 0.0055694 | 0.0030313 | 0.069566 | 0.065016 | -0.00036966 | -0.0042254 | -0.00017515 | 0.017059 | 0.0054409 | 0.071478 | 0.056401 | -0.002226 | 0.013514 | -0.0006516 | 8.139 | 122.4976 | -0.26093 | 121.9437 | 0.036621 | -0.091553 | -0.059509 | 0.2243 | 122.4152 | -0.24719 | 122.1085 | -0.032043 | -0.11902 | 0.009155 | -0.068664 | 0.15564 | -0.39825 | 0.22888 | 0.13275 | 0.10071 | 0.20142 | 0.16937 | -0.054931 | 0.073242 | -0.23346 | 0.16022 | 0.20142 | 0.073242 | 0.25635 | 0.12817 | 0.29755 | 122.2046 | 0.21515 | 122.3557 | 122.7585 | 122.6624 | 122.6898 | 122.6074 | -122.6028 | -122.5891 | 122.1359 | 122.3007 | 8.3313 | 0.41656
1334.2656 | 122.3923 | -0.16937 | 122.3465 | -0.0020601 | 0.010508 | 0.070421 | 0.068221 | 0.00069854 | -0.0029438 | 0.001961 | 0.0018005 | 0.0067227 | 0.070196 | 0.063878 | -0.00073063 | 0.013086 | -0.0034286 | 8.4183 | 122.4884 | -0.25177 | 121.9803 | 0.059509 | -0.11444 | -0.09613 | 0.25177 | 122.3557 | -0.21057 | 122.1588 | -0.009155 | -0.1236 | 0.018311 | -0.082397 | 0.14191 | -0.36621 | 0.22888 | 0.073243 | 0.054932 | 0.15564 | 0.13733 | -0.041198 | 0.009155 | -0.18768 | 0.16022 | 0.18768 | 0.045777 | 0.22888 | 0.086975 | 0.31128 | 122.2321 | 0.20142 | 122.3694 | 122.7402 | 122.5662 | 122.6578 | 122.525 | -122.5983 | -122.5571 | 122.1497 | 122.3282 | 8.5876 | 0.42114
1336.0156 | 122.4243 | -0.19226 | 122.319 | 0.036087 | 0.0068765 | 0.068498 | 0.066939 | 0.00027134 | -0.0018756 | 0.00025205 | 0.017059 | 0.0060819 | 0.069983 | 0.057042 | -0.00030343 | 0.015223 | -0.0034286 | 8.6014 | 122.5388 | -0.2655 | 121.9666 | 0.050354 | -0.09613 | -0.064087 | 0.25177 | 122.3923 | -0.22888 | 122.1542 | 0.013733 | -0.09613 | 0.036621 | -0.073242 | 0.21973 | -0.35248 | 0.24261 | 0.12817 | 0.096131 | 0.20142 | 0.16937 | -0.036621 | 0.073242 | -0.16479 | 0.20599 | 0.22888 | 0.096131 | 0.2655 | 0.13275 | 0.31586 | 122.2321 | 0.24261 | 122.3831 | 122.8043 | 122.6212 | 122.731 | 122.5845 | -122.5845 | -122.5479 | 122.1588 | 122.3465 | 8.7936 | 0.44403
1337.7031 | 122.406 | -0.1831 | 122.3511 | 0.0055694 | 0.0064493 | 0.06978 | 0.066084 | 0.00027134 | -0.0037982 | 0.0023882 | 0.020111 | 0.0030911 | 0.072546 | 0.052983 | 0.00012397 | 0.014795 | -0.0025742 | 8.9905 | 122.5067 | -0.28839 | 121.9528 | 0.050354 | -0.086975 | -0.050354 | 0.21515 | 122.3923 | -0.25177 | 122.1176 | -0.036621 | -0.11444 | 0.022888 | -0.10529 | 0.15564 | -0.39825 | 0.23346 | 0.13275 | 0.09613 | 0.23804 | 0.20142 | -0.068665 | 0.041199 | -0.23346 | 0.14648 | 0.20599 | 0.068664 | 0.27466 | 0.13733 | 0.33875 | 122.2412 | 0.21515 | 122.3694 | 122.7951 | 122.644 | 122.6898 | 122.5754 | -122.6395 | -122.6028 | 122.1359 | 122.3007 | 9.1736 | 0.39825
1339.4375 | 117.7597 | -92.363 | 25.2365 | -0.0020601 | 0.0053811 | 0.069353 | 0.066725 | 0.0019803 | -0.0040118 | -0.00060235 | 0.0018005 | 0.0054409 | 0.069128 | 0.060032 | 0.0014056 | 0.016718 | -0.0027878 | -12.6572 | 25.3372 | -92.569 | 25.1129 | -91.9006 | -92.5003 | -92.5507 | -0.94299 | 25.2548 | -92.4957 | 25.2411 | -92.2348 | -92.2623 | -92.0929 | -0.20599 | 0.10071 | -0.1236 | 0.46234 | -0.18768 | -0.13733 | 0.018311 | 0.068665 | -0.13275 | 0.018311 | 0.004578 | 0.12817 | 0.27008 | 0.10071 | 0.40283 | 0.23346 | 0.66833 | 117.6819 | 0.26093 | 117.7368 | 117.9062 | 117.7506 | 117.7002 | 117.6178 | -117.8055 | -117.7322 | 117.4759 | 117.6041 | 79.7058 | 91.42
1341.1875 | 117.2836 | -92.0242 | 25.0305 | 0.0055694 | 0.0045267 | 0.065721 | 0.065657 | 0.0019803 | -0.0029438 | 0.0017474 | -0.0012513 | 0.0045865 | 0.066565 | 0.060246 | 0.0014056 | 0.016291 | -0.0012924 | -12.4878 | 25.1404 | -92.2165 | 24.9435 | -91.5573 | -92.1432 | -92.1707 | -0.82855 | 25.0717 | -92.1158 | 25.1175 | -91.8091 | -91.8274 | -91.6809 | -0.19226 | 0.10986 | -0.086976 | 0.46692 | -0.14648 | -0.11902 | 0.045777 | 0.073242 | -0.091553 | 0.041198 | 0.086975 | 0.21515 | 0.34332 | 0.19684 | 0.43488 | 0.28839 | 0.65918 | 117.16 | 0.3067 | 117.2333 | 117.3569 | 117.1875 | 117.1646 | 117.0959 | -117.247 | -117.1463 | 116.9678 | 117.1417 | 79.5364 | 91.1957
1342.875 | 116.7892 | -91.7358 | 24.9481 | -0.0096891 | 0.0051675 | 0.068498 | 0.063735 | 0.0032619 | -0.0035846 | -0.00081595 | 0.0018005 | 0.0045865 | 0.068915 | 0.053624 | 0.001192 | 0.016291 | 0.0010574 | -13.6826 | 25.0305 | -91.9373 | 24.8062 | -91.2872 | -91.8549 | -91.9006 | -0.83771 | 24.971 | -91.8457 | 24.9527 | -91.5619 | -91.6031 | -91.42 | -0.20142 | 0.082398 | -0.14191 | 0.44861 | -0.16479 | -0.11902 | 0.036621 | 0.082398 | -0.10986 | 0.022888 | 0.004578 | 0.17395 | 0.31586 | 0.13275 | 0.42572 | 0.24262 | 0.65002 | 116.7435 | 0.28381 | 116.7984 | 116.9678 | 116.8167 | 116.7664 | 116.7068 | -116.8854 | -116.7938 | 116.5421 | 116.6885 | 78.0533 | 90.8981
1344.625 | 116.5009 | -91.4886 | 24.852 | -0.0096891 | 0.0045267 | 0.06978 | 0.062666 | -0.0010105 | -0.00508 | -0.0010298 | 0.0018005 | 0.0033047 | 0.067847 | 0.063023 | -0.001585 | 0.016504 | -0.0036422 | -13.9801 | 24.8978 | -91.6443 | 24.8108 | -90.9119 | -91.4429 | -91.5436 | -0.71411 | 24.852 | -91.5619 | 24.8703 | -91.2598 | -91.2735 | -91.1591 | -0.15564 | 0.045776 | -0.041199 | 0.57678 | -0.054932 | 0.045776 | 0.10071 | 0.20142 | -0.073243 | 0 | 0.01831 | 0.22888 | 0.32959 | 0.21515 | 0.40283 | 0.28839 | 0.73242 | 116.4551 | 0.30212 | 116.4322 | 116.5421 | 116.4139 | 116.3864 | 116.3406 | -116.4963 | -116.4139 | 116.2994 | 116.3589 | 77.5085 | 90.7745
1346.375 | 116.2949 | -91.2872 | 24.7513 | 0.036087 | 0.0079447 | 0.070848 | 0.064589 | 0.0030483 | -0.0012348 | 0.0023882 | 0.010956 | 0.0030911 | 0.069556 | 0.054265 | 0.003542 | 0.016077 | 0.001271 | -14.3509 | 24.8474 | -91.4658 | 24.8199 | -90.6509 | -91.2415 | -91.3101 | -0.65918 | 24.7971 | -91.3467 | 24.8978 | -90.9897 | -91.0172 | -90.889 | -0.17853 | 0.09613 | 0.068664 | 0.63629 | -0.022889 | 0.045776 | 0.15564 | 0.2243 | -0.05951 | 0.045776 | 0.14648 | 0.29755 | 0.39825 | 0.27008 | 0.45776 | 0.32959 | 0.81482 | 116.2857 | 0.35706 | 116.2445 | 116.3132 | 116.1438 | 116.1346 | 116.0843 | -116.217 | -116.098 | 116.1072 | 116.185 | 76.9363 | 90.6281
1348.0625 | 116.0706 | -91.1179 | 24.7055 | 0.028458 | 0.0060221 | 0.069353 | 0.063094 | 0.0045437 | 0.001756 | 0.00046565 | 0.0048523 | 0.0048001 | 0.06571 | 0.059178 | 0.0014056 | 0.014368 | -0.0019332 | -15.4312 | 24.7787 | -91.3055 | 24.7009 | -90.5411 | -91.1453 | -91.1819 | -0.68665 | 24.7238 | -91.2415 | 24.7971 | -90.8936 | -90.9119 | -90.7791 | -0.18768 | 0.073243 | -0.004577 | 0.57678 | -0.064087 | -0.027466 | 0.1236 | 0.16022 | -0.1236 | 0.018311 | 0.091553 | 0.2243 | 0.33874 | 0.20599 | 0.46234 | 0.32959 | 0.76447 | 116.0065 | 0.3479 | 116.0385 | 116.0843 | 115.9653 | 115.8966 | 115.8417 | -116.011 | -115.947 | 115.8188 | 115.9149 | 75.6866 | 90.4312
1349.7969 | 115.8875 | -91.0309 | 24.6506 | 0.013199 | 0.0038857 | 0.068071 | 0.063948 | -0.0010105 | -0.0029438 | 0.0017474 | 0.0048523 | 0.0043729 | 0.066138 | 0.061314 | -0.00051703 | 0.016932 | 0.0006302 | -16.6214 | 24.7238 | -91.1957 | 24.6277 | -90.4999 | -91.0446 | -91.095 | -0.75531 | 24.678 | -91.1087 | 24.7375 | -90.7883 | -90.8157 | -90.683 | -0.16479 | 0.073242 | -0.022888 | 0.53101 | -0.064087 | -0.013733 | 0.10071 | 0.15106 | -0.07782 | 0.027466 | 0.086975 | 0.24262 | 0.3479 | 0.21515 | 0.42572 | 0.29297 | 0.6958 | 115.8234 | 0.32044 | 115.8463 | 115.9195 | 115.7867 | 115.7547 | 115.7089 | -115.8463 | -115.7593 | 115.6586 | 115.7684 | 74.4095 | 90.2756
1351.5469 | 115.7959 | -90.8844 | 24.5865 | -0.0020601 | 0.0030313 | 0.067003 | 0.064162 | -0.00015586 | -0.0035846 | -0.001457 | -0.0073547 | 0.0022367 | 0.065924 | 0.059605 | -0.00073063 | 0.014795 | -0.0010788 | -17.7429 | 24.6368 | -91.1087 | 24.6414 | -90.2802 | -90.8707 | -90.9485 | -0.62714 | 24.6323 | -90.9851 | 24.7421 | -90.5777 | -90.6143 | -90.509 | -0.22431 | 0.050354 | 0.054931 | 0.60425 | -0.064087 | 0.013732 | 0.16022 | 0.23804 | -0.10071 | 0.045776 | 0.15564 | 0.3067 | 0.37537 | 0.27008 | 0.47607 | 0.37079 | 0.82855 | 115.7501 | 0.40741 | 115.7272 | 115.7455 | 115.6174 | 115.5212 | 115.5167 | -115.6952 | -115.5716 | 115.5258 | 115.6265 | 73.1415 | 90.2573
1353.2969 | 114.8621 | -29.4479 | 85.4691 | 0.028458 | 0.0085855 | 0.064226 | 0.062453 | 0.0021939 | -0.0023028 | 0.00046565 | 0.0048523 | 0.0060819 | 0.066351 | 0.05576 | -0.0013714 | 0.015864 | -0.002147 | 3.2318 | 85.1395 | -29.9332 | 85.2127 | -29.3838 | -29.6448 | -29.7272 | 2.2018 | 85.881 | -29.1504 | 84.9518 | -29.5898 | -29.512 | -29.3838 | -0.48523 | -0.32959 | -0.25635 | 0.064087 | -0.27924 | -0.19684 | 0.20599 | 0.28839 | 0.29755 | 0.41199 | -0.51727 | -0.14191 | 0.064087 | -0.064087 | -0.23346 | -0.36163 | 0.54932 | 115.1459 | -0.43945 | 114.1022 | 115.0726 | 115.0314 | 114.5874 | 115.329 | -115.4022 | -114.6194 | 114.6606 | 114.3997 | 32.6797 | 31.6498
1355 | 119.0094 | -0.16937 | 118.9087 | 0.043716 | 0.0064493 | 0.071275 | 0.059889 | 0.0015529 | -0.0023028 | -0.0012434 | 0.010956 | 0.0035183 | 0.069556 | 0.064091 | -0.00051703 | 0.017573 | -0.0023606 | 12.236 | 119.0369 | -0.22888 | 118.5928 | 0.086975 | -0.050354 | -0.032043 | 0.32501 | 118.9087 | -0.20142 | 118.7576 | 0.050354 | -0.045776 | 0.082397 | -0.059509 | 0.12817 | -0.31586 | 0.25635 | 0.13733 | 0.11902 | 0.19684 | 0.17853 | -0.032043 | 0 | -0.15106 | 0.21973 | 0.25177 | 0.1236 | 0.28381 | 0.15564 | 0.31586 | 118.8217 | 0.25177 | 118.959 | 119.2657 | 119.1101 | 119.2062 | 119.0781 | -119.1376 | -119.1101 | 118.7622 | 118.927 | 12.4054 | 0.49439
1356.75 | 115.7547 | -24.6185 | 91.301 | -0.0020601 | 0.0066629 | 0.066362 | 0.061812 | 0.0036893 | -0.0012348 | -0.00060235 | -0.0012513 | 0.0052273 | 0.067847 | 0.059178 | -0.00051703 | 0.015436 | -0.0055648 | 2.948 | 91.3284 | -24.6826 | 91.0629 | -24.5041 | -24.5773 | -24.5224 | -1.6388 | 91.452 | -24.4629 | 91.1499 | -24.8062 | -24.678 | -24.7147 | -0.064087 | 0.027466 | -0.23804 | 0.11444 | 0.09613 | 0.041198 | 0.16022 | 0.10529 | 0.15564 | 0.15106 | -0.15106 | -0.18768 | -0.096131 | -0.05951 | -0.25177 | -0.21515 | 0.17853 | 115.7455 | -0.34332 | 115.6128 | 116.011 | 115.9149 | 115.947 | 116.0706 | -115.9836 | -115.7639 | 115.6815 | 115.7684 | 27.5665 | 22.9797
1358.5 | 119.101 | -0.15564 | 118.9362 | 0.028458 | 0.0051675 | 0.069353 | 0.062453 | -0.0010105 | -0.00038018 | -0.00060235 | 0.010956 | 0.0048001 | 0.070196 | 0.067082 | 0.0020466 | 0.017145 | -0.0010788 | 12.7075 | 119.0643 | -0.23804 | 118.6798 | 0.10071 | -0.07782 | -0.032043 | 0.28839 | 118.9819 | -0.2243 | 118.8263 | 0.032043 | -0.064087 | 0.050354 | -0.082397 | 0.12817 | -0.25635 | 0.25635 | 0.1236 | 0.07782 | 0.20599 | 0.16022 | -0.068664 | 0.045777 | -0.10986 | 0.18768 | 0.20599 | 0.091553 | 0.27466 | 0.16022 | 0.33875 | 118.9178 | 0.25635 | 119.0506 | 119.3024 | 119.2062 | 119.22 | 119.1376 | -119.1742 | -119.1605 | 118.8355 | 118.9819 | 12.8632 | 0.44403
1360.1875 | 119.2932 | -0.14191 | 119.0735 | -0.017319 | 0.0049539 | 0.065935 | 0.062026 | -0.0033603 | -0.0012348 | -0.0020978 | 0.0048523 | 0.0020231 | 0.068915 | 0.061955 | -8.9634e-05 | 0.014582 | 0.0010574 | 12.7121 | 119.1742 | -0.21973 | 118.8034 | 0.1236 | -0.036621 | -0.013733 | 0.32959 | 119.0552 | -0.20142 | 119.0002 | 0.086975 | -0.004578 | 0.09613 | -0.07782 | 0.10071 | -0.27008 | 0.2655 | 0.12817 | 0.10529 | 0.20599 | 0.18311 | -0.059509 | -0.01831 | -0.073242 | 0.22888 | 0.23804 | 0.13733 | 0.29755 | 0.19684 | 0.34332 | 119.0231 | 0.28839 | 119.2017 | 119.3939 | 119.2566 | 119.3161 | 119.1971 | -119.2932 | -119.2749 | 118.9453 | 119.1422 | 12.854 | 0.4715
1361.9375 | 119.3024 | -0.20142 | 119.1925 | 0.036087 | 0.0064493 | 0.068712 | 0.064375 | 0.0013393 | -0.0023028 | 0.00025205 | 0.023163 | 0.0071499 | 0.070196 | 0.057042 | -0.0026532 | 0.016504 | -0.004924 | 12.941 | 119.339 | -0.29297 | 118.84 | 0.041199 | -0.09613 | -0.10071 | 0.26093 | 119.2429 | -0.25635 | 119.014 | -0.004578 | -0.11444 | 0.022888 | -0.091553 | 0.14648 | -0.35248 | 0.24262 | 0.10071 | 0.10529 | 0.19226 | 0.19684 | -0.054932 | 0.050354 | -0.17853 | 0.19684 | 0.2243 | 0.086975 | 0.27924 | 0.14191 | 0.33417 | 119.133 | 0.25177 | 119.2703 | 119.632 | 119.4992 | 119.5404 | 119.4443 | -119.4855 | -119.4489 | 119.0414 | 119.2154 | 13.1424 | 0.46234
1363.6875 | 116.2582 | -26.7105 | 89.209 | -0.0020601 | 0.0090127 | 0.068712 | 0.064162 | -0.00036966 | -0.0025166 | -0.0023114 | 0.014008 | 0.0056545 | 0.070196 | 0.069004 | 0.00055117 | 0.016932 | 0.0008438 | 2.9663 | 89.3921 | -27.1957 | 88.6276 | -27.1362 | -27.2461 | -27.2552 | -0.027466 | 89.1678 | -27.0721 | 89.3463 | -26.7929 | -26.738 | -26.5961 | -0.48523 | 0.18311 | -0.58136 | -0.42572 | -0.54474 | -0.53558 | -0.059509 | -0.050354 | -0.36163 | -0.041198 | 0.13733 | -0.082398 | 0.11444 | -0.027466 | 0.47608 | 0.33417 | 0.05951 | 115.8234 | 0.27924 | 116.4185 | 116.5878 | 116.2399 | 116.1026 | 115.8783 | -116.4047 | -116.2811 | 115.3381 | 116.0568 | 29.6768 | 26.683
1365.4219 | 119.3344 | -0.1831 | 119.2383 | 0.043716 | 0.0087991 | 0.069566 | 0.066298 | 0.0034755 | -0.0010212 | 0.00025205 | 0.010956 | 0.0071499 | 0.071051 | 0.061314 | -0.0011578 | 0.014582 | -0.006633 | 13.092 | 119.3756 | -0.29297 | 118.8995 | 0.045776 | -0.064087 | -0.07782 | 0.31586 | 119.2841 | -0.23346 | 119.0689 | 0.013733 | -0.10071 | 0.041199 | -0.10986 | 0.13733 | -0.33875 | 0.22888 | 0.10528 | 0.11902 | 0.21515 | 0.22888 | -0.050354 | 0.045777 | -0.16937 | 0.19684 | 0.2243 | 0.082397 | 0.27466 | 0.13275 | 0.33874 | 119.1925 | 0.24719 | 119.3024 | 119.6686 | 119.5175 | 119.5587 | 119.4672 | -119.5312 | -119.4717 | 119.0826 | 119.252 | 13.2751 | 0.49896
1367.1094 | 119.4168 | -0.19226 | 119.3024 | 0.043716 | 0.0066629 | 0.069994 | 0.066725 | 0.0039029 | -0.0014484 | 0.0013202 | 0.0048523 | 0.0052273 | 0.070196 | 0.058323 | -8.9634e-05 | 0.015436 | -0.0040696 | 13.7146 | 119.4626 | -0.26093 | 118.9774 | 0.073242 | -0.086975 | -0.073242 | 0.31586 | 119.3527 | -0.24719 | 119.1513 | 0.018311 | -0.091553 | 0.027466 | -0.068664 | 0.16022 | -0.32501 | 0.2655 | 0.11902 | 0.10529 | 0.18768 | 0.17395 | -0.054931 | 0.050354 | -0.15106 | 0.21057 | 0.21973 | 0.10071 | 0.27466 | 0.15564 | 0.33417 | 119.2383 | 0.2655 | 119.3985 | 119.7235 | 119.5999 | 119.6548 | 119.545 | -119.5633 | -119.5496 | 119.1696 | 119.3436 | 13.9069 | 0.50812
1368.8594 | 119.4946 | -0.17853 | 119.3665 | 0.020828 | 0.0073037 | 0.069353 | 0.06523 | 0.0015529 | -0.0023028 | -0.00060235 | 0.014008 | 0.0058683 | 0.070624 | 0.057682 | 0.0022602 | 0.013941 | -0.0036422 | 14.4974 | 119.5404 | -0.28381 | 119.0689 | 0.10529 | -0.10071 | -0.07782 | 0.32959 | 119.3848 | -0.23346 | 119.2383 | 0.018311 | -0.073242 | 0.036621 | -0.10528 | 0.17395 | -0.29755 | 0.28381 | 0.10071 | 0.07782 | 0.20599 | 0.1831 | -0.054931 | 0.018311 | -0.12817 | 0.19684 | 0.21515 | 0.10529 | 0.27008 | 0.16022 | 0.3891 | 119.3527 | 0.25177 | 119.4717 | 119.8242 | 119.6182 | 119.7189 | 119.5633 | -119.6503 | -119.5999 | 119.2474 | 119.4168 | 14.6759 | 0.50812
1370.625 | 119.6091 | -0.16937 | 119.4214 | 0.013199 | 0.0058083 | 0.071489 | 0.067793 | 0.0028347 | -0.0018756 | -0.0038068 | 0.0018005 | 0.0056545 | 0.066992 | 0.057042 | 0.001833 | 0.015864 | -0.0027878 | 14.5386 | 119.5679 | -0.28839 | 119.0826 | 0.036621 | -0.16022 | -0.1236 | 0.2655 | 119.3893 | -0.23804 | 119.3024 | 0.032043 | -0.07782 | 0.068665 | -0.11902 | 0.14648 | -0.33874 | 0.20599 | 0.045777 | 0.009156 | 0.1648 | 0.12817 | -0.068664 | -0.032044 | -0.11902 | 0.20142 | 0.23804 | 0.091553 | 0.3067 | 0.16022 | 0.32501 | 119.371 | 0.27008 | 119.5404 | 119.8563 | 119.6274 | 119.7372 | 119.5587 | -119.7098 | -119.6594 | 119.252 | 119.4717 | 14.7079 | 0.43488
1372.3281 | 119.6869 | -0.17853 | 119.4305 | -0.0020601 | 0.0058083 | 0.070634 | 0.064589 | 0.0030483 | -0.0023028 | -0.0012434 | 0.017059 | 0.0065091 | 0.069983 | 0.062596 | 0.002901 | 0.014795 | 0.0006302 | 14.7446 | 119.5908 | -0.28839 | 119.2291 | 0.17853 | -0.036621 | -0.018311 | 0.36621 | 119.4489 | -0.24261 | 119.3939 | 0.082397 | -0.018311 | 0.086975 | -0.10986 | 0.16022 | -0.20142 | 0.35706 | 0.16022 | 0.14191 | 0.27008 | 0.25177 | -0.064087 | 0.018311 | -0.036621 | 0.26092 | 0.2655 | 0.16022 | 0.32959 | 0.2243 | 0.46692 | 119.5175 | 0.32501 | 119.6365 | 119.8792 | 119.6915 | 119.7693 | 119.6274 | -119.7189 | -119.6732 | 119.4077 | 119.5724 | 14.9231 | 0.54474
1374.0156 | 119.7327 | -0.13733 | 119.4717 | 0.051346 | 0.0073037 | 0.072984 | 0.066939 | 0.0015529 | -0.001662 | 0.0021746 | 0.014008 | 0.0037319 | 0.07041 | 0.067936 | 0.003542 | 0.016932 | 0.0014846 | 14.9872 | 119.6594 | -0.28381 | 119.2795 | 0.19226 | -0.050354 | -0.004578 | 0.35706 | 119.5175 | -0.23346 | 119.4214 | 0.07782 | -0.022888 | 0.07782 | -0.14648 | 0.18768 | -0.19226 | 0.32959 | 0.13275 | 0.086975 | 0.27923 | 0.23346 | -0.09613 | 0.045776 | -0.050354 | 0.21515 | 0.21515 | 0.11444 | 0.31128 | 0.21057 | 0.47607 | 119.5633 | 0.31128 | 119.6548 | 119.9432 | 119.751 | 119.7968 | 119.6548 | -119.7556 | -119.7052 | 119.4168 | 119.5587 | 15.1245 | 0.49438
1375.7656 | 119.7784 | -0.17853 | 119.5358 | 0.0055694 | 0.0040995 | 0.068071 | 0.06288 | -0.00015586 | -0.0020892 | -0.0018842 | -0.0012513 | 0.0022367 | 0.068488 | 0.062809 | -0.00073063 | 0.012873 | 0.0008438 | 15.358 | 119.6732 | -0.23804 | 119.2886 | 0.16022 | -0.018311 | -0.022888 | 0.35248 | 119.5358 | -0.19684 | 119.4489 | 0.086975 | -0.004578 | 0.073242 | -0.059509 | 0.13733 | -0.24719 | 0.33874 | 0.15564 | 0.16022 | 0.21515 | 0.21973 | -0.01831 | 0 | -0.086975 | 0.2655 | 0.25177 | 0.17395 | 0.27008 | 0.19226 | 0.39825 | 119.5267 | 0.28381 | 119.6457 | 119.9112 | 119.7327 | 119.8517 | 119.7144 | -119.7739 | -119.7327 | 119.4672 | 119.6274 | 15.5365 | 0.53101
1377.5312 | 119.6869 | -0.21515 | 119.5953 | 0.0055694 | 0.0068765 | 0.067857 | 0.065443 | 0.00091214 | -0.0040118 | 0.00025205 | 0.0018005 | 0.0058683 | 0.069556 | 0.059819 | -0.001585 | 0.013941 | -0.0023606 | 15.2847 | 119.7281 | -0.29297 | 119.2108 | 0.009155 | -0.15564 | -0.12817 | 0.24261 | 119.6136 | -0.25635 | 119.3802 | -0.045776 | -0.13733 | -0.032043 | -0.07782 | 0.13275 | -0.38452 | 0.2243 | 0.086975 | 0.059509 | 0.16479 | 0.13733 | -0.041199 | 0.01831 | -0.21515 | 0.16937 | 0.18311 | 0.07782 | 0.22431 | 0.11902 | 0.30212 | 119.5038 | 0.21057 | 119.6365 | 120.0211 | 119.87 | 119.9432 | 119.8288 | -119.8883 | -119.8517 | 119.426 | 119.5953 | 15.4999 | 0.45776
1379.2188 | 119.8746 | -0.17853 | 119.632 | -0.0020601 | 0.0055947 | 0.06743 | 0.063307 | 0.0028347 | -0.0031574 | 0.00046565 | -0.0043029 | 0.0024503 | 0.068915 | 0.059178 | -0.0024396 | 0.013941 | -0.0025742 | 15.7333 | 119.7327 | -0.26093 | 119.3939 | 0.1831 | -0.013733 | -0.013733 | 0.36621 | 119.6228 | -0.21515 | 119.5541 | 0.10529 | 0.009155 | 0.082397 | -0.082397 | 0.10071 | -0.23804 | 0.36163 | 0.16479 | 0.16479 | 0.24719 | 0.24719 | -0.036621 | -0.009155 | -0.07782 | 0.28381 | 0.26092 | 0.18768 | 0.29755 | 0.2243 | 0.44403 | 119.6548 | 0.32044 | 119.7693 | 119.9936 | 119.838 | 119.9112 | 119.8013 | -119.8929 | -119.8471 | 119.5724 | 119.7327 | 15.9119 | 0.54474
1380.9688 | 119.8791 | -0.1831 | 119.6777 | 0.013199 | 0.0045267 | 0.069566 | 0.066084 | -0.0033603 | -0.0042254 | -0.00038875 | 0.0018005 | 0.0035183 | 0.070196 | 0.063023 | 0.00097837 | 0.016077 | -0.002147 | 15.5914 | 119.8242 | -0.25177 | 119.3665 | 0.07782 | -0.09613 | -0.064087 | 0.25635 | 119.6594 | -0.23804 | 119.545 | 0.018311 | -0.068665 | 0.050354 | -0.068665 | 0.14648 | -0.31128 | 0.26092 | 0.11902 | 0.086975 | 0.18768 | 0.15564 | -0.054932 | -0.01831 | -0.13275 | 0.20142 | 0.23346 | 0.11444 | 0.28839 | 0.16937 | 0.32959 | 119.6182 | 0.25635 | 119.783 | 120.076 | 119.8975 | 120.0073 | 119.8425 | -119.9295 | -119.9158 | 119.5496 | 119.7281 | 15.7745 | 0.43945
1382.7344 | 119.8746 | -0.17395 | 119.7189 | 0.013199 | 0.0064493 | 0.070634 | 0.068221 | 0.0036893 | -0.001662 | 0.0026018 | 0.010956 | 0.0056545 | 0.067206 | 0.061955 | 0.0026874 | 0.015223 | -0.0023606 | 15.9164 | 119.8791 | -0.26093 | 119.4214 | 0.068665 | -0.091553 | -0.082397 | 0.3479 | 119.7464 | -0.25635 | 119.5862 | 0.013733 | -0.09613 | 0.018311 | -0.086975 | 0.16022 | -0.29755 | 0.24261 | 0.091553 | 0.082397 | 0.17853 | 0.16937 | -0.082398 | 0.027466 | -0.13275 | 0.18768 | 0.19226 | 0.07782 | 0.27466 | 0.16022 | 0.32959 | 119.6823 | 0.27008 | 119.8425 | 120.1401 | 120.0027 | 120.0531 | 119.9203 | -119.9799 | -119.9753 | 119.5953 | 119.7601 | 16.0904 | 0.52185
1384.4219 | 119.8608 | -0.2243 | 119.7601 | -0.0096891 | 0.0062357 | 0.069353 | 0.06758 | 0.0032619 | 0.001756 | 0.001961 | 0.026215 | 0.0069363 | 0.070624 | 0.057469 | -0.0011578 | 0.013514 | -0.0019332 | 16.333 | 119.9707 | -0.32044 | 119.3939 | 0.045776 | -0.11902 | -0.10529 | 0.25177 | 119.8151 | -0.27924 | 119.545 | -0.059509 | -0.13733 | -0.018311 | -0.096131 | 0.21057 | -0.36621 | 0.27008 | 0.11902 | 0.10529 | 0.21515 | 0.20142 | -0.054932 | 0.054931 | -0.21515 | 0.16479 | 0.20599 | 0.086975 | 0.26092 | 0.14191 | 0.36621 | 119.7144 | 0.21973 | 119.8242 | 120.2911 | 120.0943 | 120.195 | 120.0394 | -120.0806 | -120.0394 | 119.6182 | 119.7693 | 16.5573 | 0.47607
1386.125 | 119.9936 | -0.18768 | 119.783 | 0.0055694 | 0.0055947 | 0.070634 | 0.066084 | 0.0034755 | -0.0014484 | 0.00046565 | 0.0018005 | 0.0058683 | 0.06806 | 0.0611 | 0.0033282 | 0.015864 | -0.0006516 | 16.4017 | 119.9387 | -0.27008 | 119.4534 | 0.068665 | -0.14648 | -0.11444 | 0.27008 | 119.7922 | -0.24261 | 119.696 | 0.041199 | -0.054932 | 0.064087 | -0.082398 | 0.15564 | -0.32959 | 0.25635 | 0.073242 | 0.041199 | 0.15564 | 0.1236 | -0.054932 | 0.009155 | -0.086975 | 0.22888 | 0.25177 | 0.13275 | 0.3067 | 0.18768 | 0.33875 | 119.7235 | 0.28381 | 119.9387 | 120.2087 | 120.0348 | 120.1263 | 119.9799 | -120.0531 | -120.0256 | 119.6411 | 119.8837 | 16.5894 | 0.45776
1387.875 | 119.9249 | -0.2243 | 119.8608 | 0.0055694 | 0.0058083 | 0.068925 | 0.066298 | 0.0015529 | -0.003371 | -0.001457 | 0.014008 | 0.0075771 | 0.069769 | 0.054051 | -0.0028668 | 0.014582 | -0.0025742 | 17.5781 | 119.9936 | -0.29755 | 119.4443 | 0.027466 | -0.13733 | -0.082397 | 0.26093 | 119.8883 | -0.29755 | 119.6045 | -0.050354 | -0.14648 | -0.032043 | -0.073242 | 0.13275 | -0.41656 | 0.25177 | 0.14191 | 0.086975 | 0.21515 | 0.16022 | -0.073242 | 0.027466 | -0.25635 | 0.17395 | 0.19226 | 0.07782 | 0.2655 | 0.15106 | 0.32501 | 119.7418 | 0.24719 | 119.902 | 120.2911 | 120.1859 | 120.2179 | 120.1126 | -120.1584 | -120.1584 | 119.6686 | 119.8288 | 17.8024 | 0.48523
1389.625 | 120.0806 | -0.19226 | 119.8563 | -0.0020601 | 0.0053811 | 0.069566 | 0.06523 | -0.0022923 | -0.0059344 | -0.0020978 | 0.0048523 | 0.0045865 | 0.068274 | 0.065373 | -0.00094423 | 0.015436 | 0.0006302 | 18.4021 | 119.9661 | -0.24261 | 119.6045 | 0.17853 | -0.022888 | -0.027466 | 0.36621 | 119.8975 | -0.21515 | 119.7693 | 0.073242 | -0.018311 | 0.068665 | -0.050354 | 0.10986 | -0.25177 | 0.37079 | 0.16479 | 0.16937 | 0.21515 | 0.21973 | -0.022888 | 0.041199 | -0.086975 | 0.2655 | 0.26093 | 0.17395 | 0.28381 | 0.19684 | 0.42114 | 119.8471 | 0.28839 | 119.9844 | 120.2087 | 120.1126 | 120.1584 | 120.0897 | -120.0989 | -120.0714 | 119.7968 | 119.9615 | 18.5944 | 0.55847
1391.3125 | 120.0577 | -0.20142 | 119.9203 | 0.028458 | 0.0090127 | 0.070207 | 0.06758 | 0.0032619 | -0.0025166 | 0.00046565 | 0.0048523 | 0.0062955 | 0.069128 | 0.054692 | 0.0022602 | 0.01565 | -0.006633 | 18.5898 | 120.0806 | -0.29297 | 119.5862 | 0.10071 | -0.10529 | -0.086975 | 0.32959 | 119.9387 | -0.24719 | 119.7601 | 0.004578 | -0.09613 | 0.032043 | -0.091553 | 0.16022 | -0.33417 | 0.30212 | 0.11444 | 0.09613 | 0.20599 | 0.18768 | -0.045776 | 0.018311 | -0.16022 | 0.20599 | 0.23346 | 0.10529 | 0.27924 | 0.15106 | 0.39368 | 119.8792 | 0.25177 | 120.0073 | 120.3735 | 120.1859 | 120.282 | 120.1401 | -120.2133 | -120.1675 | 119.7876 | 119.9615 | 18.7912 | 0.53101
1393 | 120.0439 | -0.23804 | 119.9478 | 0.0055694 | 0.0068765 | 0.067217 | 0.065871 | 0.0021939 | -0.0027302 | 0.00067925 | -0.0012513 | 0.0039457 | 0.071265 | 0.057896 | -8.9634e-05 | 0.015009 | -0.0023606 | 18.6813 | 120.0714 | -0.2655 | 119.5862 | 0.059509 | -0.11902 | -0.10986 | 0.24261 | 119.9341 | -0.22888 | 119.7327 | -0.036621 | -0.15106 | -0.013733 | -0.027466 | 0.1236 | -0.36163 | 0.29755 | 0.12817 | 0.11902 | 0.15564 | 0.14648 | 0.009155 | -0.013733 | -0.21515 | 0.20142 | 0.2243 | 0.086975 | 0.21515 | 0.07782 | 0.32501 | 119.8517 | 0.19226 | 119.9615 | 120.3369 | 120.163 | 120.3094 | 120.1721 | -120.2133 | -120.1767 | 119.8242 | 119.9707 | 18.9194 | 0.48065
1394.75 | 120.1355 | -0.19684 | 119.9615 | -0.0020601 | 0.0068765 | 0.069139 | 0.064803 | 0.00069854 | -0.001662 | -0.002525 | -0.0012513 | 0.0039457 | 0.070837 | 0.064305 | 0.0043964 | 0.016291 | -0.0025742 | 17.3401 | 120.1401 | -0.27466 | 119.5862 | 0.041199 | -0.19226 | -0.14191 | 0.25177 | 119.9524 | -0.23804 | 119.8425 | -0.022888 | -0.10071 | 0.032043 | -0.07782 | 0.17853 | -0.37537 | 0.23804 | 0.054931 | 0.004577 | 0.13275 | 0.082397 | -0.041199 | -0.009155 | -0.11902 | 0.17395 | 0.22888 | 0.09613 | 0.27008 | 0.13733 | 0.31586 | 119.8608 | 0.21515 | 120.0806 | 120.4147 | 120.1904 | 120.3369 | 120.1492 | -120.2362 | -120.1996 | 119.783 | 120.0394 | 17.5369 | 0.44861
1396.5 | 120.2316 | -0.18768 | 119.9707 | -0.0020601 | 0.0060221 | 0.068925 | 0.064589 | -0.00015586 | -0.0031574 | -0.0023114 | 0.0048523 | 0.0028775 | 0.06806 | 0.059819 | -0.001585 | 0.013727 | 0.001271 | 16.7313 | 120.0943 | -0.24261 | 119.7647 | 0.20599 | -0.009155 | 0.004578 | 0.38452 | 119.9844 | -0.21515 | 119.9203 | 0.10071 | 0.009155 | 0.07782 | -0.054932 | 0.1236 | -0.20599 | 0.39368 | 0.19226 | 0.17853 | 0.24719 | 0.23346 | -0.027466 | 0.013733 | -0.050354 | 0.28839 | 0.2655 | 0.19684 | 0.29297 | 0.2243 | 0.44861 | 120.0073 | 0.31586 | 120.1355 | 120.3369 | 120.1996 | 120.282 | 120.1721 | -120.2133 | -120.1859 | 119.9524 | 120.108 | 16.9189 | 0.5722
1398.2031 | 120.2179 | -0.19226 | 120.0302 | 0.028458 | 0.0060221 | 0.069139 | 0.066725 | -0.00036966 | -0.0048664 | -0.0020978 | 0.0079041 | 0.0026639 | 0.069556 | 0.070073 | 0.00076477 | 0.016291 | -0.0017196 | 17.2852 | 120.1904 | -0.25635 | 119.696 | 0.10071 | -0.09613 | -0.068665 | 0.24719 | 120.0348 | -0.22888 | 119.8929 | 0.004578 | -0.068665 | 0.045776 | -0.064087 | 0.16022 | -0.33417 | 0.29297 | 0.1236 | 0.096131 | 0.18768 | 0.16022 | -0.036621 | 0.004578 | -0.13733 | 0.19684 | 0.23804 | 0.1236 | 0.27466 | 0.16022 | 0.35706 | 119.9524 | 0.23346 | 120.1218 | 120.4468 | 120.2637 | 120.3827 | 120.2271 | -120.2866 | -120.2591 | 119.8883 | 120.0851 | 17.4774 | 0.43945
1399.9531 | 120.1447 | -0.21515 | 120.0577 | -0.0020601 | 0.0075173 | 0.071916 | 0.069289 | 0.0049709 | -0.0014484 | -0.00060235 | 0.0018005 | 0.0056545 | 0.068488 | 0.061741 | 0.00012397 | 0.014368 | -0.0057786 | 18.3014 | 120.2225 | -0.27924 | 119.696 | 0.041199 | -0.1831 | -0.15564 | 0.2655 | 120.0806 | -0.23804 | 119.8791 | -0.068665 | -0.16937 | -0.032043 | -0.064087 | 0.16479 | -0.36163 | 0.25635 | 0.059509 | 0.032044 | 0.1236 | 0.096131 | -0.022888 | 0.022888 | -0.17853 | 0.14648 | 0.18311 | 0.045776 | 0.20599 | 0.068664 | 0.32043 | 119.9753 | 0.16937 | 120.1172 | 120.5017 | 120.3186 | 120.4376 | 120.2957 | -120.3369 | -120.2957 | 119.9112 | 120.0943 | 18.5165 | 0.48065
1401.6562 | 120.1904 | -0.21515 | 120.1035 | 0.0055694 | 0.0090127 | 0.069139 | 0.065871 | 0.00091214 | -0.0048664 | 0.0021746 | 0.0048523 | 0.0054409 | 0.068915 | 0.058964 | 0.0016194 | 0.015223 | -0.0040696 | 19.1025 | 120.2682 | -0.27008 | 119.7281 | 0.068665 | -0.16937 | -0.12817 | 0.28839 | 120.1035 | -0.24261 | 119.9112 | -0.050354 | -0.16479 | -0.013733 | -0.054932 | 0.16479 | -0.37537 | 0.28381 | 0.086975 | 0.045776 | 0.14191 | 0.10071 | -0.027466 | 0 | -0.19226 | 0.16479 | 0.20142 | 0.050354 | 0.22888 | 0.07782 | 0.33875 | 119.9982 | 0.19226 | 120.1538 | 120.5383 | 120.3461 | 120.4834 | 120.3186 | -120.3735 | -120.3461 | 119.9432 | 120.1263 | 19.3176 | 0.50354
1403.4062 | 120.3598 | -0.15564 | 120.1035 | 0.013199 | 0.0066629 | 0.068071 | 0.065016 | 0.0041165 | -0.00038018 | 0.00067925 | 0.020111 | 0.0050137 | 0.072119 | 0.065373 | 0.002901 | 0.016077 | -0.0002244 | 19.0659 | 120.2179 | -0.21515 | 119.8929 | 0.21515 | -0.022888 | -0.009155 | 0.40741 | 120.1035 | -0.24261 | 120.0394 | 0.07782 | -0.032043 | 0.086975 | -0.059509 | 0.11444 | -0.21057 | 0.37079 | 0.14649 | 0.13275 | 0.20599 | 0.19226 | -0.086975 | 0 | -0.064087 | 0.23346 | 0.24261 | 0.1236 | 0.32959 | 0.21057 | 0.4303 | 120.108 | 0.32044 | 120.282 | 120.433 | 120.3461 | 120.3735 | 120.2591 | -120.3186 | -120.3461 | 120.0485 | 120.195 | 19.2215 | 0.56305
1405.1094 | 120.3873 | -0.16022 | 120.1263 | 0.013199 | 0.0073037 | 0.068498 | 0.066084 | 0.0015529 | -0.0018756 | 0.00089285 | -0.0012513 | 0.0048001 | 0.071051 | 0.069218 | 0.0024738 | 0.016718 | -0.000438 | 19.3359 | 120.2637 | -0.24719 | 119.8563 | 0.17395 | -0.054932 | -0.045776 | 0.36163 | 120.1538 | -0.20599 | 120.0897 | 0.064087 | -0.022888 | 0.09613 | -0.086975 | 0.13733 | -0.27008 | 0.33417 | 0.11444 | 0.10528 | 0.20142 | 0.19226 | -0.045777 | 0.027466 | -0.036621 | 0.2243 | 0.25635 | 0.13733 | 0.30212 | 0.18311 | 0.42114 | 120.1035 | 0.27008 | 120.2957 | 120.5109 | 120.3598 | 120.4239 | 120.314 | -120.3735 | -120.3323 | 120.0165 | 120.2499 | 19.4962 | 0.52185
1406.875 | 120.3049 | -0.2243 | 120.1996 | 0.058975 | 0.0075173 | 0.071062 | 0.068861 | -0.0020787 | -0.0018756 | -0.0016706 | 0.010956 | 0.0071499 | 0.070837 | 0.048069 | -0.00073063 | 0.016077 | -0.0074874 | 19.0201 | 120.369 | -0.31586 | 119.8013 | 0.068665 | -0.12817 | -0.10986 | 0.28839 | 120.195 | -0.27466 | 119.9844 | -0.018311 | -0.14648 | -0.013733 | -0.091553 | 0.16937 | -0.39825 | 0.29297 | 0.11444 | 0.09613 | 0.20599 | 0.18768 | -0.050354 | -0.004578 | -0.21515 | 0.20599 | 0.21057 | 0.07782 | 0.26093 | 0.12817 | 0.38452 | 120.1172 | 0.25635 | 120.2591 | 120.6848 | 120.4697 | 120.5933 | 120.4193 | -120.5154 | -120.4742 | 120.0256 | 120.2087 | 19.2444 | 0.5127
1408.625 | 120.314 | -0.23346 | 120.2225 | 0.0055694 | 0.0049539 | 0.068925 | 0.067793 | 0.00069854 | -0.00038018 | 0.00025205 | 0.023163 | 0.0043729 | 0.070837 | 0.060673 | -0.0013714 | 0.015009 | -0.006633 | 20.5215 | 120.3278 | -0.29297 | 119.838 | 0.10529 | -0.11444 | -0.10529 | 0.28839 | 120.2728 | -0.28381 | 119.9982 | -0.068665 | -0.16022 | -0.022888 | -0.05951 | 0.10529 | -0.38452 | 0.33875 | 0.12817 | 0.11902 | 0.18768 | 0.17853 | -0.050354 | 0.050354 | -0.2243 | 0.16479 | 0.21057 | 0.073242 | 0.26092 | 0.1236 | 0.39825 | 120.1309 | 0.21515 | 120.282 | 120.6207 | 120.5566 | 120.5612 | 120.5063 | -120.5154 | -120.5063 | 120.0714 | 120.2316 | 20.755 | 0.52185
1410.3125 | 120.3781 | -0.21057 | 120.2545 | 0.036087 | 0.0066629 | 0.068925 | 0.065016 | 0.00091214 | -0.0035846 | 0.00046565 | 0.014008 | 0.0065091 | 0.068274 | 0.061528 | 0.00076477 | 0.013727 | -0.0017196 | 20.5902 | 120.3964 | -0.3067 | 119.8608 | 0.082397 | -0.11444 | -0.10529 | 0.31128 | 120.282 | -0.26093 | 120.0531 | -0.041199 | -0.12817 | 0.004578 | -0.096131 | 0.14191 | -0.39368 | 0.29297 | 0.10529 | 0.09613 | 0.20142 | 0.19226 | -0.050354 | 0.027465 | -0.20142 | 0.16937 | 0.21515 | 0.082397 | 0.2655 | 0.13275 | 0.3891 | 120.1675 | 0.21973 | 120.314 | 120.7031 | 120.5429 | 120.607 | 120.4926 | -120.5612 | -120.5154 | 120.0714 | 120.2637 | 20.8008 | 0.52185
1412 | 120.3644 | -0.21515 | 120.2957 | 0.013199 | 0.0068765 | 0.071489 | 0.066512 | 0.0011257 | -0.0027302 | 0.00025205 | -0.0012513 | 0.0056545 | 0.070837 | 0.065587 | 0.0022602 | 0.015864 | -0.0070602 | 21.1624 | 120.4422 | -0.26093 | 119.8288 | 0.004578 | -0.21973 | -0.17395 | 0.21973 | 120.2728 | -0.25635 | 120.0714 | -0.07782 | -0.17853 | -0.013733 | -0.045776 | 0.14648 | -0.46692 | 0.21973 | 0.041199 | -0.004578 | 0.086975 | 0.041198 | -0.041199 | -0.022888 | -0.2243 | 0.13733 | 0.20142 | 0.036621 | 0.24262 | 0.07782 | 0.2655 | 120.0897 | 0.17853 | 120.3278 | 120.7031 | 120.5292 | 120.6573 | 120.488 | -120.5566 | -120.5521 | 120.0439 | 120.2866 | 21.3776 | 0.43488
1413.75 | 120.5109 | -0.16479 | 120.2545 | -0.0020601 | 0.0047403 | 0.066576 | 0.062666 | 0.00091214 | -0.0046528 | -0.0012434 | -0.0012513 | 0.0024503 | 0.066992 | 0.070073 | -0.0013714 | 0.015223 | -0.0042832 | 21.6385 | 120.3644 | -0.23804 | 120.0256 | 0.25177 | -0.009155 | 0 | 0.39825 | 120.2499 | -0.20142 | 120.1996 | 0.091553 | 0.013733 | 0.07782 | -0.073242 | 0.10986 | -0.22888 | 0.41656 | 0.16479 | 0.15564 | 0.23804 | 0.22888 | -0.036621 | -0.004578 | -0.054932 | 0.25635 | 0.24261 | 0.17853 | 0.27924 | 0.21515 | 0.48981 | 120.2637 | 0.29297 | 120.401 | 120.6024 | 120.4514 | 120.5292 | 120.4147 | -120.4926 | -120.4559 | 120.1904 | 120.3644 | 21.8033 | 0.56305
1415.5156 | 120.5429 | -0.19226 | 120.2728 | -0.0020601 | 0.0019631 | 0.068285 | 0.062239 | 0.0024075 | -0.0044392 | -0.00081595 | 0.0048523 | 0.0037319 | 0.06806 | 0.0658 | -0.001585 | 0.015009 | -0.0030014 | 20.7825 | 120.401 | -0.27466 | 119.9982 | 0.16022 | -0.073242 | -0.027466 | 0.32044 | 120.2911 | -0.21973 | 120.2087 | 0.064087 | -0.027466 | 0.073242 | -0.082397 | 0.12817 | -0.27466 | 0.35248 | 0.16479 | 0.11902 | 0.24719 | 0.20142 | -0.027466 | 0.018311 | -0.064087 | 0.25635 | 0.2655 | 0.16479 | 0.29297 | 0.19226 | 0.43488 | 120.2728 | 0.28381 | 120.4285 | 120.6757 | 120.5109 | 120.5933 | 120.4834 | -120.5475 | -120.4926 | 120.1904 | 120.401 | 20.9747 | 0.5127
1417.2812 | 120.433 | -0.21057 | 120.3506 | -0.0020601 | 0.0055947 | 0.069353 | 0.067366 | 0.00069854 | -0.0037982 | -0.00081595 | 0.0018005 | 0.0048001 | 0.071478 | 0.059178 | 0.0020466 | 0.016077 | 0.0004166 | 21.4325 | 120.5154 | -0.28381 | 119.9341 | 0.059509 | -0.19684 | -0.16022 | 0.2243 | 120.3598 | -0.25177 | 120.1309 | -0.086975 | -0.19226 | -0.009155 | -0.073242 | 0.16479 | -0.41656 | 0.27008 | 0.050354 | 0.013733 | 0.1236 | 0.086975 | -0.041199 | 0.009155 | -0.21973 | 0.1236 | 0.20142 | 0.01831 | 0.24261 | 0.059509 | 0.34332 | 120.2179 | 0.16479 | 120.3827 | 120.7993 | 120.6116 | 120.726 | 120.5704 | -120.6345 | -120.6024 | 120.1447 | 120.3415 | 21.6431 | 0.43488
1418.9688 | 120.4605 | -0.21057 | 120.3644 | 0.0055694 | 0.0055947 | 0.070207 | 0.066939 | 0.00091214 | -0.0031574 | 3.8448e-05 | -0.0012513 | 0.0075771 | 0.06806 | 0.068791 | 0.001192 | 0.017145 | 0.0031936 | 21.5652 | 120.5383 | -0.27466 | 119.9432 | 0.036621 | -0.16937 | -0.16022 | 0.21973 | 120.3873 | -0.24261 | 120.1813 | -0.09613 | -0.1831 | -0.022888 | -0.064087 | 0.17395 | -0.42114 | 0.24719 | 0.050354 | 0.041198 | 0.11444 | 0.10529 | -0.032044 | 0.022888 | -0.18311 | 0.11444 | 0.18768 | 0.027466 | 0.21973 | 0.05951 | 0.31128 | 120.2179 | 0.14649 | 120.4239 | 120.813 | 120.6299 | 120.7489 | 120.5978 | -120.639 | -120.607 | 120.1538 | 120.3918 | 21.7758 | 0.4303
1420.7031 | 120.5704 | -0.19684 | 120.3506 | 0.028458 | 0.0055947 | 0.068498 | 0.065871 | 0.0026211 | -0.00016658 | 3.8448e-05 | 0.0079041 | 0.0026639 | 0.070837 | 0.063023 | -0.00051703 | 0.017786 | -0.0036422 | 21.048 | 120.5475 | -0.24261 | 120.0485 | 0.16937 | -0.091553 | -0.07782 | 0.29297 | 120.3735 | -0.23346 | 120.2316 | 0.013733 | -0.07782 | 0.032043 | -0.045777 | 0.19684 | -0.30212 | 0.36621 | 0.11902 | 0.10529 | 0.16479 | 0.15106 | -0.036621 | 0.022888 | -0.11902 | 0.21057 | 0.22888 | 0.11902 | 0.2655 | 0.15564 | 0.41199 | 120.2911 | 0.24719 | 120.4651 | 120.7901 | 120.607 | 120.7443 | 120.5704 | -120.5933 | -120.5841 | 120.2454 | 120.4285 | 21.2448 | 0.48981
1422.4531 | 120.5063 | -0.21515 | 120.4147 | -0.0020601 | 0.0081583 | 0.068498 | 0.066512 | -0.0010105 | -0.0018756 | -0.0010298 | -0.0012513 | 0.0084317 | 0.070196 | 0.062809 | 0.0024738 | 0.016504 | -0.0017196 | 21.8811 | 120.5566 | -0.27466 | 120.0027 | 0.050354 | -0.21515 | -0.16022 | 0.24261 | 120.4605 | -0.25177 | 120.2087 | -0.07782 | -0.17853 | -0.027466 | -0.059509 | 0.14191 | -0.41199 | 0.2655 | 0.054932 | 0 | 0.11444 | 0.059509 | -0.036621 | 0.045776 | -0.20599 | 0.13733 | 0.18768 | 0.036621 | 0.2243 | 0.073242 | 0.32501 | 120.2774 | 0.17395 | 120.4605 | 120.8313 | 120.7123 | 120.7718 | 120.6757 | -120.6894 | -120.6665 | 120.2179 | 120.4239 | 22.0963 | 0.45776
1424.1406 | 120.5017 | -0.21515 | 120.3278 | 0.043716 | 0.0066629 | 0.070207 | 0.067366 | 0.00091214 | -0.0029438 | 0.0017474 | 0.017059 | 0.0065091 | 0.071051 | 0.060673 | -0.002226 | 0.013941 | 0.000203 | 22.3068 | 120.5292 | -0.29297 | 119.9936 | 0.12817 | -0.10986 | -0.10986 | 0.3479 | 120.3873 | -0.27008 | 120.1767 | -0.032043 | -0.11902 | 0.009155 | -0.07782 | 0.20142 | -0.33417 | 0.34332 | 0.10529 | 0.10529 | 0.18311 | 0.18311 | -0.054932 | 0.059509 | -0.15106 | 0.18311 | 0.2243 | 0.09613 | 0.27924 | 0.15106 | 0.42114 | 120.2866 | 0.23804 | 120.4468 | 120.8221 | 120.6573 | 120.7443 | 120.6024 | -120.6207 | -120.5978 | 120.2087 | 120.3918 | 22.522 | 0.56305
1425.8906 | 120.6573 | -0.16022 | 120.3964 | 0.0055694 | 0.0075173 | 0.071275 | 0.065657 | 0.0043301 | -0.0044392 | 0.00089285 | -0.0012513 | 0.0041593 | 0.069769 | 0.064946 | 0.0039692 | 0.017786 | 0.0021256 | 21.6705 | 120.5338 | -0.24261 | 120.1263 | 0.21057 | -0.082397 | -0.059509 | 0.41199 | 120.3781 | -0.20599 | 120.3415 | 0.059509 | -0.041199 | 0.091553 | -0.082398 | 0.13733 | -0.27008 | 0.37079 | 0.10071 | 0.07782 | 0.18311 | 0.16022 | -0.045777 | -0.01831 | -0.054931 | 0.21973 | 0.25177 | 0.11902 | 0.29755 | 0.1648 | 0.45319 | 120.369 | 0.2655 | 120.5475 | 120.7764 | 120.5841 | 120.694 | 120.5383 | -120.639 | -120.6024 | 120.2866 | 120.5017 | 21.8307 | 0.5722
1427.5781 | 120.5383 | -0.21973 | 120.4285 | -0.0020601 | 0.0064493 | 0.071275 | 0.065443 | 0.0013393 | -0.0025166 | -0.0016706 | 0.0018005 | 0.0060819 | 0.069556 | 0.057469 | 0.001192 | 0.016504 | -0.0030014 | 21.6614 | 120.5841 | -0.27466 | 120.0394 | 0.07782 | -0.21515 | -0.17395 | 0.25177 | 120.4422 | -0.27466 | 120.2042 | -0.09613 | -0.21057 | -0.036621 | -0.054931 | 0.15564 | -0.3891 | 0.29755 | 0.045777 | 0.004578 | 0.10071 | 0.059509 | -0.054931 | 0.013733 | -0.2243 | 0.1236 | 0.18311 | 0.009156 | 0.23804 | 0.064087 | 0.35248 | 120.314 | 0.17853 | 120.4788 | 120.8588 | 120.7169 | 120.8038 | 120.6619 | -120.7031 | -120.7031 | 120.2591 | 120.4239 | 21.8811 | 0.4715
1429.2812 | 120.4376 | -0.23346 | 120.4193 | -0.0020601 | 0.0081583 | 0.070421 | 0.066725 | 0.00069854 | -0.0018756 | 0.00046565 | -0.0012513 | 0.0056545 | 0.069128 | 0.059605 | 0.001833 | 0.015009 | -0.0002244 | 21.0571 | 120.5658 | -0.26093 | 120.0027 | 0.10071 | -0.20142 | -0.16937 | 0.23804 | 120.4239 | -0.23804 | 120.1813 | -0.091553 | -0.20142 | -0.022888 | -0.027466 | 0.14648 | -0.41657 | 0.33417 | 0.064086 | 0.032043 | 0.091552 | 0.059509 | -0.004578 | 0.004577 | -0.23804 | 0.14191 | 0.21057 | 0.032043 | 0.21515 | 0.036621 | 0.36163 | 120.2637 | 0.14648 | 120.4193 | 120.8267 | 120.6619 | 120.7993 | 120.6573 | -120.6802 | -120.6573 | 120.2362 | 120.4147 | 21.2906 | 0.4715
1431.0312 | 120.7077 | -0.17395 | 120.4605 | -0.0096891 | 0.0036721 | 0.069139 | 0.063735 | 0.00027134 | -0.0014484 | -0.001457 | -0.0012513 | 0.0011685 | 0.067633 | 0.071995 | -0.0013714 | 0.015223 | 0.0008438 | 21.6522 | 120.5795 | -0.24261 | 120.2225 | 0.29297 | -0.009155 | -0.004578 | 0.44861 | 120.4422 | -0.21515 | 120.4193 | 0.09613 | 0.004578 | 0.086975 | -0.068665 | 0.11902 | -0.23804 | 0.46692 | 0.16937 | 0.16479 | 0.23804 | 0.23346 | -0.041199 | -0.01831 | -0.041198 | 0.27008 | 0.26092 | 0.17853 | 0.30212 | 0.21973 | 0.53558 | 120.4651 | 0.31128 | 120.6345 | 120.8221 | 120.6573 | 120.7535 | 120.6162 | -120.7031 | -120.6757 | 120.3964 | 120.5933 | 21.8262 | 0.62256
1432.7188 | 120.5063 | -0.16022 | 120.282 | 0.058975 | 0.0085855 | 0.070634 | 0.066939 | 0.0058255 | -0.00080758 | -0.0018842 | 0.014008 | 0.0045865 | 0.069342 | 0.0658 | 0.0033282 | 0.015436 | -0.0030014 | 22.1558 | 120.4285 | -0.25635 | 120.0302 | 0.32501 | -0.045776 | -0.013733 | 0.44861 | 120.314 | -0.21057 | 120.2087 | 0.068665 | -0.032043 | 0.09613 | -0.096131 | 0.14648 | -0.25177 | 0.48523 | 0.14648 | 0.11444 | 0.24262 | 0.21057 | -0.050354 | 0.032044 | -0.073242 | 0.22888 | 0.25635 | 0.12817 | 0.3067 | 0.17853 | 0.58136 | 120.2866 | 0.27924 | 120.4193 | 120.6848 | 120.5246 | 120.5887 | 120.4742 | -120.5383 | -120.4926 | 120.1904 | 120.369 | 22.316 | 0.60882
1434.4688 | 120.6116 | -0.19226 | 120.5292 | 0.0055694 | 0.0085855 | 0.069566 | 0.065871 | 0.0058255 | 0.00047422 | -0.0018842 | -0.0012513 | 0.0069363 | 0.069769 | 0.0611 | 0.0016194 | 0.01565 | -0.0002244 | 21.5744 | 120.6436 | -0.2655 | 120.0943 | 0.13275 | -0.16937 | -0.13733 | 0.31586 | 120.52 | -0.23346 | 120.314 | -0.036621 | -0.13275 | 0.013733 | -0.073242 | 0.11444 | -0.43488 | 0.32501 | 0.054932 | 0.022888 | 0.12817 | 0.09613 | -0.041198 | -0.009155 | -0.21515 | 0.15564 | 0.20599 | 0.05951 | 0.24719 | 0.10071 | 0.39825 | 120.3598 | 0.19684 | 120.5475 | 120.9091 | 120.7535 | 120.8359 | 120.7123 | -120.7947 | -120.7626 | 120.2866 | 120.5063 | 21.7667 | 0.50812
1436.2188 | 120.7352 | -0.15106 | 120.5292 | 0.0055694 | 0.0034585 | 0.068071 | 0.063307 | 0.0028347 | -0.0027302 | -0.0016706 | -0.0012513 | 0.0035183 | 0.07041 | 0.062809 | -0.0020122 | 0.015009 | -0.0008652 | 21.0617 | 120.6345 | -0.21057 | 120.2774 | 0.3067 | -0.004578 | 0 | 0.46692 | 120.5063 | -0.19684 | 120.4468 | 0.11444 | 0.018311 | 0.09613 | -0.059509 | 0.10529 | -0.25177 | 0.45776 | 0.15106 | 0.14648 | 0.21057 | 0.20599 | -0.045776 | -0.022888 | -0.082398 | 0.2655 | 0.24719 | 0.16937 | 0.29297 | 0.21515 | 0.51727 | 120.488 | 0.31128 | 120.6436 | 120.845 | 120.7031 | 120.7855 | 120.6573 | -120.7397 | -120.726 | 120.4285 | 120.5978 | 21.2128 | 0.61798
1437.9062 | 120.6711 | -0.19226 | 120.5795 | -0.0020601 | 0.0045267 | 0.071062 | 0.066298 | 0.0011257 | -0.0035846 | -0.0010298 | -0.0012513 | 0.0054409 | 0.071051 | 0.061955 | 0.00076477 | 0.016291 | -0.0053512 | 21.0983 | 120.7169 | -0.25635 | 120.1721 | 0.1236 | -0.17395 | -0.14191 | 0.32044 | 120.6024 | -0.23346 | 120.3873 | -0.022888 | -0.14191 | 0.018311 | -0.064087 | 0.13733 | -0.40741 | 0.31586 | 0.050354 | 0.018311 | 0.11444 | 0.082398 | -0.041198 | 0.022888 | -0.19226 | 0.16937 | 0.21057 | 0.050354 | 0.25177 | 0.091552 | 0.37994 | 120.4285 | 0.21057 | 120.6207 | 120.9732 | 120.8359 | 120.9091 | 120.7947 | -120.8359 | -120.813 | 120.3644 | 120.5795 | 21.2906 | 0.5127
1439.6562 | 120.7855 | -0.14191 | 120.5521 | -0.0020601 | 0.0062357 | 0.070421 | 0.06288 | 0.0053983 | -0.0014484 | -0.0010298 | -0.0012513 | 0.0045865 | 0.067419 | 0.064732 | 0.0043964 | 0.016291 | -0.0034286 | 20.5444 | 120.7169 | -0.23804 | 120.2957 | 0.24719 | -0.068665 | -0.036621 | 0.45776 | 120.5521 | -0.18768 | 120.5063 | 0.091553 | -0.022888 | 0.11444 | -0.09613 | 0.16479 | -0.25635 | 0.3891 | 0.10529 | 0.073242 | 0.20142 | 0.16937 | -0.045776 | 0 | -0.045776 | 0.23346 | 0.25635 | 0.11902 | 0.30212 | 0.16479 | 0.48523 | 120.5338 | 0.27924 | 120.694 | 120.9549 | 120.7397 | 120.8588 | 120.694 | -120.7901 | -120.7397 | 120.4376 | 120.6482 | 20.6863 | 0.59967
1441.3438 | 120.7901 | -0.16022 | 120.5978 | 0.020828 | 0.0058083 | 0.070634 | 0.061812 | 0.00048494 | -0.0020892 | -0.002525 | -0.0012513 | 0.0041593 | 0.069556 | 0.071354 | -0.00094423 | 0.016932 | -0.0055648 | 20.6131 | 120.7214 | -0.24261 | 120.2957 | 0.23804 | -0.064087 | -0.036621 | 0.3891 | 120.6116 | -0.21515 | 120.4697 | 0.050354 | -0.022888 | 0.07782 | -0.082398 | 0.1236 | -0.30212 | 0.39825 | 0.1236 | 0.09613 | 0.20599 | 0.17853 | -0.054932 | 0.013733 | -0.12817 | 0.21057 | 0.23804 | 0.13733 | 0.29297 | 0.19226 | 0.48065 | 120.5383 | 0.2655 | 120.6848 | 120.9641 | 120.8267 | 120.8817 | 120.7718 | -120.8405 | -120.813 | 120.4559 | 120.6299 | 20.7733 | 0.54932
1443.1094 | 120.7993 | -0.17853 | 120.6116 | 0.013199 | 0.0040995 | 0.072771 | 0.064803 | 5.774e-05 | -0.0037982 | -0.00017515 | -0.0012513 | 0.0011685 | 0.070196 | 0.065587 | 0.0024738 | 0.01565 | -1.0598e-05 | 20.8969 | 120.7397 | -0.24719 | 120.3094 | 0.22888 | -0.073242 | -0.041199 | 0.37994 | 120.6116 | -0.2243 | 120.4926 | 0.054932 | -0.036621 | 0.068665 | -0.068664 | 0.12817 | -0.30212 | 0.40741 | 0.13733 | 0.10529 | 0.20599 | 0.17395 | -0.045776 | 0 | -0.11902 | 0.23346 | 0.24719 | 0.14191 | 0.29297 | 0.18768 | 0.47607 | 120.5566 | 0.27924 | 120.7169 | 120.9869 | 120.8359 | 120.9183 | 120.7901 | -120.8588 | -120.8359 | 120.488 | 120.6711 | 21.0754 | 0.55847
1444.8594 | 120.7214 | -0.19226 | 120.6253 | 0.0055694 | 0.0079447 | 0.070634 | 0.066512 | 0.0036893 | -0.0012348 | -0.001457 | -0.0012513 | 0.0054409 | 0.067847 | 0.061314 | 0.00033757 | 0.014795 | 0.0038346 | 20.4987 | 120.8176 | -0.2655 | 120.282 | 0.16022 | -0.16022 | -0.14648 | 0.36163 | 120.6802 | -0.22888 | 120.4422 | -0.041199 | -0.15564 | -0.018311 | -0.073242 | 0.19226 | -0.34332 | 0.35248 | 0.045777 | 0.032044 | 0.11902 | 0.10529 | -0.036621 | 0.054932 | -0.1831 | 0.15106 | 0.17395 | 0.036621 | 0.21057 | 0.073242 | 0.42572 | 120.5475 | 0.18768 | 120.6711 | 121.0831 | 120.9091 | 121.0098 | 120.8725 | -120.8908 | -120.8542 | 120.4742 | 120.6345 | 20.6909 | 0.55389
1446.5469 | 120.8862 | -0.16479 | 120.6345 | 0.0055694 | 0.0051675 | 0.070421 | 0.062666 | 0.0019803 | -0.0023028 | 0.00046565 | -0.0012513 | 0.0030911 | 0.069128 | 0.068577 | -0.00051703 | 0.016077 | -0.0034286 | 20.3934 | 120.7764 | -0.2243 | 120.4147 | 0.31586 | 0.013733 | 0 | 0.48981 | 120.6619 | -0.19684 | 120.5612 | 0.12817 | 0.018311 | 0.086975 | -0.059509 | 0.14191 | -0.21973 | 0.48065 | 0.16479 | 0.17853 | 0.2243 | 0.23804 | -0.032043 | 0.027466 | -0.073242 | 0.29297 | 0.25177 | 0.18311 | 0.28381 | 0.21515 | 0.54016 | 120.639 | 0.32501 | 120.7581 | 121.0007 | 120.8588 | 120.9412 | 120.8267 | -120.8588 | -120.8313 | 120.5795 | 120.726 | 20.5582 | 0.6546
1448.25 | 120.8817 | -0.15564 | 120.6757 | -0.0096891 | 0.0073037 | 0.068498 | 0.065016 | 0.0019803 | -0.0018756 | -0.00060235 | -0.0043029 | 0.0018093 | 0.069128 | 0.062809 | -0.0041486 | 0.014155 | -0.0019332 | 19.5602 | 120.7993 | -0.21515 | 120.4147 | 0.29755 | -0.009155 | -0.004578 | 0.50812 | 120.6711 | -0.19684 | 120.5795 | 0.10529 | 0.009155 | 0.09613 | -0.059509 | 0.1236 | -0.26093 | 0.45319 | 0.15106 | 0.14649 | 0.21057 | 0.20599 | -0.041198 | -0.004577 | -0.09613 | 0.26093 | 0.25177 | 0.16479 | 0.29297 | 0.20599 | 0.5127 | 120.6299 | 0.30212 | 120.7764 | 121.0144 | 120.8679 | 120.9549 | 120.8267 | -120.8908 | -120.8725 | 120.5704 | 120.7352 | 19.7159 | 0.66376
1450 | 120.9274 | -0.14191 | 120.6802 | 0.0055694 | 0.0066629 | 0.070848 | 0.065443 | 0.0036893 | -0.0014484 | -0.0027386 | -0.0012513 | 0.0052273 | 0.069342 | 0.059178 | 0.00461 | 0.014795 | -0.0008652 | 19.2123 | 120.845 | -0.22888 | 120.4239 | 0.26093 | -0.050354 | -0.022888 | 0.50354 | 120.6848 | -0.18768 | 120.6299 | 0.07782 | 0.004578 | 0.11902 | -0.086975 | 0.16479 | -0.25635 | 0.40283 | 0.11902 | 0.091553 | 0.20599 | 0.17853 | -0.045776 | 0.004577 | -0.050354 | 0.21973 | 0.26093 | 0.14649 | 0.3067 | 0.19226 | 0.48981 | 120.6528 | 0.2655 | 120.8176 | 121.0739 | 120.8725 | 120.9869 | 120.8267 | -120.9091 | -120.8679 | 120.5658 | 120.7718 | 19.3542 | 0.64545
1451.6875 | 120.8771 | -0.17853 | 120.6802 | 0.028458 | 0.0068765 | 0.070848 | 0.065443 | -0.00015586 | -0.0035846 | -0.0010298 | 0.0079041 | 0.0039457 | 0.07041 | 0.076909 | 0.0020466 | 0.0133 | -0.0025742 | 18.9102 | 120.845 | -0.26093 | 120.4056 | 0.21973 | -0.082397 | -0.050354 | 0.42114 | 120.7306 | -0.21973 | 120.5566 | 0.022888 | -0.064087 | 0.054932 | -0.082397 | 0.16479 | -0.27466 | 0.39826 | 0.12817 | 0.096131 | 0.21057 | 0.17853 | -0.041199 | 0.050354 | -0.1236 | 0.20142 | 0.23346 | 0.11444 | 0.27466 | 0.15564 | 0.48065 | 120.6665 | 0.24261 | 120.7764 | 121.106 | 120.9503 | 121.0236 | 120.9091 | -120.9412 | -120.9 | 120.5841 | 120.7352 | 19.0887 | 0.59967
1453.4531 | 120.9549 | -0.13733 | 120.694 | 0.0055694 | 0.0077311 | 0.071916 | 0.06523 | 0.0049709 | -0.0018756 | -0.0012434 | 0.023163 | 0.0062955 | 0.072333 | 0.069218 | 0.0043964 | 0.016291 | -0.0027878 | 18.5532 | 120.8862 | -0.21515 | 120.5063 | 0.30212 | -0.036621 | 0.009155 | 0.52643 | 120.7626 | -0.23346 | 120.6573 | 0.086975 | -0.013733 | 0.10529 | -0.07782 | 0.19226 | -0.18768 | 0.43945 | 0.14648 | 0.10071 | 0.2243 | 0.17853 | -0.09613 | 0.068664 | -0.036621 | 0.2243 | 0.24262 | 0.1236 | 0.33875 | 0.21973 | 0.51727 | 120.7214 | 0.32043 | 120.8908 | 121.1014 | 120.9961 | 121.0236 | 120.9 | -120.9091 | -120.9274 | 120.6436 | 120.7947 | 18.6905 | 0.66376
1455.2188 | 120.9045 | -0.17853 | 120.726 | 0.0055694 | 0.0047403 | 0.07213 | 0.065657 | 0.0030483 | -0.0023028 | -0.00038875 | -0.0043029 | 0.0069363 | 0.071051 | 0.061741 | -0.0013714 | 0.016718 | -0.0034286 | 18.1046 | 120.932 | -0.25635 | 120.3918 | 0.14648 | -0.15106 | -0.09613 | 0.43488 | 120.7855 | -0.21057 | 120.6253 | 0.027466 | -0.073242 | 0.059509 | -0.07782 | 0.20599 | -0.33417 | 0.32501 | 0.082398 | 0.027466 | 0.16022 | 0.10529 | -0.032043 | 0.059509 | -0.10071 | 0.20599 | 0.23804 | 0.10529 | 0.27008 | 0.13733 | 0.40283 | 120.6482 | 0.23804 | 120.8359 | 121.1884 | 120.9961 | 121.1105 | 120.9641 | -120.9824 | -120.9366 | 120.5704 | 120.8038 | 18.2831 | 0.6134
1456.9062 | 120.8267 | -0.19226 | 120.7764 | -0.0020601 | 0.0060221 | 0.070634 | 0.06758 | 0.0024075 | -0.0023028 | -0.0044476 | -0.0012513 | 0.0048001 | 0.072119 | 0.057469 | -0.0020122 | 0.017359 | 0.0010574 | 18.3655 | 120.9457 | -0.25177 | 120.3644 | 0.082397 | -0.1831 | -0.15564 | 0.37994 | 120.8221 | -0.23346 | 120.5521 | -0.07782 | -0.17853 | -0.022888 | -0.059509 | 0.16937 | -0.41199 | 0.27466 | 0.036621 | 0.009156 | 0.09613 | 0.068665 | -0.041198 | 0.045777 | -0.2243 | 0.11444 | 0.16937 | 0.013733 | 0.21057 | 0.054931 | 0.33417 | 120.6161 | 0.15564 | 120.7855 | 121.1975 | 121.0556 | 121.138 | 121.0144 | -121.0281 | -121.0098 | 120.5566 | 120.7443 | 18.5577 | 0.5722
1458.6562 | 120.9045 | -0.20142 | 120.8313 | 0.043716 | 0.0079447 | 0.071916 | 0.066298 | 0.0060391 | -0.0014484 | 0.00046565 | 0.017059 | 0.0069363 | 0.071265 | 0.058323 | -0.0030804 | 0.014795 | -0.0012924 | 18.7225 | 120.9641 | -0.28839 | 120.4285 | 0.1236 | -0.11444 | -0.086975 | 0.45319 | 120.8496 | -0.25635 | 120.5978 | -0.004578 | -0.1236 | 0 | -0.086975 | 0.13275 | -0.40283 | 0.32501 | 0.11444 | 0.086975 | 0.20142 | 0.17395 | -0.054932 | 0.01831 | -0.23346 | 0.19684 | 0.20142 | 0.07782 | 0.25635 | 0.13275 | 0.41199 | 120.7169 | 0.25177 | 120.8542 | 121.2524 | 121.106 | 121.1655 | 121.051 | -121.1197 | -121.0876 | 120.6299 | 120.7993 | 18.9239 | 0.6546
1460.4062 | 121.0236 | -0.13275 | 120.7809 | -0.0020601 | 0.0051675 | 0.070421 | 0.063948 | 0.0028347 | -0.0012348 | -0.004234 | -0.0043029 | 0.0052273 | 0.069983 | 0.069859 | 0.002901 | 0.016077 | -0.0030014 | 17.9398 | 120.9595 | -0.22888 | 120.5246 | 0.24261 | -0.064087 | -0.022888 | 0.54016 | 120.7901 | -0.1831 | 120.7397 | 0.086975 | -0.027466 | 0.10986 | -0.096131 | 0.17853 | -0.25635 | 0.37537 | 0.10986 | 0.068664 | 0.20599 | 0.16479 | -0.050354 | 0.009155 | -0.041199 | 0.21973 | 0.24261 | 0.10529 | 0.29297 | 0.15564 | 0.4715 | 120.7535 | 0.27008 | 120.9229 | 121.1884 | 120.9732 | 121.0922 | 120.9229 | -121.0098 | -120.9641 | 120.6573 | 120.8725 | 18.0725 | 0.67291
1462.1562 | 116.954 | -22.7234 | 94.1071 | -0.0020601 | 0.0073037 | 0.068498 | 0.064162 | 0.0049709 | -0.0046528 | -0.0016706 | 0.0018005 | 0.0039457 | 0.06806 | 0.054905 | 0.001192 | 0.016077 | 0.0010574 | 7.6904 | 92.4545 | -24.7284 | 92.9718 | -23.2956 | -23.3597 | -23.3276 | 1.8539 | 94.2627 | -22.8287 | 94.2123 | -22.8973 | -22.5037 | -22.348 | -2.005 | -1.6525 | -1.1353 | -0.5722 | -0.60425 | -0.63629 | 1.4008 | 1.3687 | -0.10528 | 0.15564 | 0.10528 | -0.17395 | 0.37537 | 0.21973 | 0.48065 | 0.32501 | 1.4328 | 117.7002 | -0.068665 | 117.041 | 117.1829 | 117.0914 | 115.1779 | 116.9861 | -118.8355 | -116.9357 | 115.6952 | 116.9357 | 30.4138 | 24.5773
1463.9062 | 120.6848 | -0.1831 | 120.575 | 0.028458 | 0.0075173 | 0.068498 | 0.067793 | 0.00091214 | -0.0029438 | 0.0015338 | 0.0048523 | 0.0069363 | 0.069983 | 0.05341 | 0.0016194 | 0.013514 | -0.0019332 | 18.2785 | 120.7169 | -0.2655 | 120.2499 | 0.19684 | -0.082397 | -0.045776 | 0.59967 | 120.5887 | -0.22888 | 120.4239 | 0.009155 | -0.10071 | 0.041199 | -0.082398 | 0.14191 | -0.32501 | 0.37994 | 0.13733 | 0.10071 | 0.21973 | 0.18311 | -0.045777 | 0.013733 | -0.15106 | 0.19226 | 0.2243 | 0.082397 | 0.27008 | 0.12817 | 0.46234 | 120.5154 | 0.23804 | 120.6528 | 120.9824 | 120.8176 | 120.9 | 120.7718 | -120.8405 | -120.8038 | 120.433 | 120.607 | 18.4616 | 0.78277
1465.5938 | 120.8221 | -0.16937 | 120.6528 | 0.0055694 | 0.0060221 | 0.068498 | 0.064589 | 0.00069854 | -0.0044392 | -0.00017515 | -0.0012513 | 0.0052273 | 0.068701 | 0.073491 | 0.00097837 | 0.015009 | -0.0002244 | 18.1412 | 120.7581 | -0.24719 | 120.3644 | 0.24719 | -0.036621 | -0.022888 | 0.65002 | 120.6162 | -0.20599 | 120.5338 | 0.082397 | -0.022888 | 0.059509 | -0.077819 | 0.10529 | -0.28839 | 0.41656 | 0.14649 | 0.13275 | 0.2243 | 0.21057 | -0.036621 | -0.036621 | -0.11902 | 0.25177 | 0.22888 | 0.14649 | 0.2655 | 0.18311 | 0.49438 | 120.6116 | 0.28839 | 120.7397 | 121.0052 | 120.8221 | 120.9274 | 120.7855 | -120.9 | -120.8588 | 120.5338 | 120.7031 | 18.3105 | 0.8194
1467.3594 | 120.575 | -0.1831 | 120.4971 | -0.017319 | 0.0079447 | 0.071703 | 0.064803 | 0.0011257 | -0.001662 | -0.00060235 | -0.0043029 | 0.0043729 | 0.07041 | 0.063878 | 0.0020466 | 0.013514 | -0.000438 | 17.9672 | 120.639 | -0.26093 | 120.0989 | 0.059509 | -0.19684 | -0.15564 | 0.50812 | 120.5154 | -0.23804 | 120.2911 | -0.064087 | -0.16937 | -0.004578 | -0.07782 | 0.14191 | -0.39825 | 0.24261 | 0.027465 | -0.013733 | 0.10529 | 0.064087 | -0.054932 | 0.018311 | -0.20599 | 0.11902 | 0.17853 | 0.013732 | 0.23346 | 0.068664 | 0.32043 | 120.3598 | 0.17395 | 120.5292 | 120.9 | 120.7535 | 120.8221 | 120.6985 | -120.7581 | -120.7352 | 120.282 | 120.4742 | 18.1503 | 0.69122
1469.1094 | 120.7031 | -0.19684 | 120.639 | 0.013199 | 0.0066629 | 0.070207 | 0.065657 | 0.0021939 | -0.0027302 | 0.0011066 | 0.0018005 | 0.0041593 | 0.070837 | 0.063023 | 0.0041828 | 0.015436 | -0.0019332 | 17.7155 | 120.7901 | -0.26093 | 120.2271 | 0.068665 | -0.1831 | -0.15106 | 0.50812 | 120.6482 | -0.23804 | 120.4147 | -0.064087 | -0.16479 | 0.004578 | -0.064087 | 0.15106 | -0.41199 | 0.2655 | 0.045776 | 0.013733 | 0.10986 | 0.07782 | -0.041199 | 0.009155 | -0.2243 | 0.13275 | 0.20142 | 0.032043 | 0.24261 | 0.073242 | 0.32959 | 120.488 | 0.17395 | 120.6528 | 121.051 | 120.8862 | 120.9869 | 120.845 | -120.9 | -120.8771 | 120.4239 | 120.6116 | 17.9123 | 0.70496
1470.8594 | 120.7718 | -0.21515 | 120.6757 | 0.066604 | 0.0073037 | 0.070848 | 0.065871 | -0.00036966 | -0.0010212 | -0.00038875 | 0.020111 | 0.0065091 | 0.071692 | 0.062809 | -0.0013714 | 0.015436 | -0.003215 | 18.5806 | 120.8496 | -0.28381 | 120.3003 | 0.10986 | -0.09613 | -0.091553 | 0.59052 | 120.7031 | -0.27008 | 120.4651 | -0.018311 | -0.1236 | 0.004578 | -0.068664 | 0.17395 | -0.37537 | 0.32501 | 0.1236 | 0.11902 | 0.19226 | 0.18768 | -0.054932 | 0.027466 | -0.21057 | 0.19684 | 0.21973 | 0.091553 | 0.27466 | 0.14649 | 0.39368 | 120.5841 | 0.25177 | 120.7352 | 121.1334 | 120.9732 | 121.0648 | 120.9183 | -120.9595 | -120.9457 | 120.5154 | 120.6802 | 18.7958 | 0.80566
1472.5625 | 120.8359 | -0.21515 | 120.726 | 0.028458 | 0.0081583 | 0.071916 | 0.068648 | 0.0011257 | -0.0014484 | 0.001961 | 0.020111 | 0.0052273 | 0.07276 | 0.060887 | -0.0013714 | 0.015223 | -0.0036422 | 18.544 | 120.8862 | -0.27924 | 120.3506 | 0.1236 | -0.09613 | -0.086975 | 0.62256 | 120.7352 | -0.26093 | 120.5383 | 0 | -0.10071 | 0.036621 | -0.064087 | 0.16022 | -0.37537 | 0.33875 | 0.12817 | 0.11902 | 0.19226 | 0.18311 | -0.045776 | 0.009155 | -0.18768 | 0.21515 | 0.25177 | 0.11444 | 0.29755 | 0.16022 | 0.40283 | 120.6299 | 0.26093 | 120.7993 | 121.1655 | 120.9961 | 121.1014 | 120.9503 | -121.0052 | -120.9869 | 120.5658 | 120.7535 | 18.7592 | 0.83771
1474.3281 | 120.8908 | -0.15564 | 120.5978 | -0.0020601 | 0.0062357 | 0.072557 | 0.066725 | 0.0056119 | 0.0021832 | 0.0051654 | 0.020111 | 0.0043729 | 0.07041 | 0.069218 | 0.0052508 | 0.016504 | 0.001271 | 19.1803 | 120.7947 | -0.25635 | 120.4147 | 0.2655 | -0.022888 | 0.009155 | 0.76904 | 120.6573 | -0.24261 | 120.5841 | 0.09613 | -0.009155 | 0.09613 | -0.10071 | 0.19684 | -0.1831 | 0.42114 | 0.16479 | 0.13275 | 0.2655 | 0.23346 | -0.086975 | 0.05951 | -0.013733 | 0.25177 | 0.25177 | 0.14649 | 0.33874 | 0.23346 | 0.52185 | 120.6711 | 0.33874 | 120.8267 | 121.051 | 120.9 | 120.9503 | 120.813 | -120.8542 | -120.8405 | 120.5704 | 120.7397 | 19.3359 | 0.92468
1476.0781 | 120.8084 | -0.21057 | 120.7535 | 0.0055694 | 0.0053811 | 0.070421 | 0.066084 | 0.0026211 | -0.0037982 | -0.002525 | -0.0012513 | 0.0062955 | 0.071905 | 0.067723 | 0.0033282 | 0.015223 | -0.003215 | 19.1071 | 120.9091 | -0.2655 | 120.3232 | 0.054932 | -0.17395 | -0.16022 | 0.59509 | 120.7214 | -0.23346 | 120.5246 | -0.059509 | -0.16022 | 0 | -0.054932 | 0.15564 | -0.4303 | 0.2655 | 0.050354 | 0.036621 | 0.10529 | 0.091553 | -0.022888 | -0.032043 | -0.22888 | 0.15106 | 0.21057 | 0.050354 | 0.23346 | 0.073242 | 0.32043 | 120.5887 | 0.17395 | 120.7581 | 121.1746 | 120.9549 | 121.1197 | 120.932 | -121.019 | -120.9869 | 120.5338 | 120.7352 | 19.3176 | 0.80566
1477.8281 | 120.9732 | -0.16479 | 120.7169 | 0.0055694 | 0.0051675 | 0.070207 | 0.065657 | 5.774e-05 | -0.0020892 | 3.8448e-05 | 0.0079041 | 0.0013821 | 0.069342 | 0.067296 | 0.00012397 | 0.01565 | -0.0044968 | 19.7021 | 120.9 | -0.23346 | 120.4514 | 0.17853 | -0.041199 | -0.022888 | 0.75989 | 120.7077 | -0.21973 | 120.6665 | 0.086975 | 0.018311 | 0.10071 | -0.068664 | 0.1831 | -0.2655 | 0.34332 | 0.14191 | 0.1236 | 0.21057 | 0.19226 | -0.054932 | -0.009155 | -0.050354 | 0.25177 | 0.2655 | 0.18311 | 0.32044 | 0.23804 | 0.41199 | 120.6848 | 0.3067 | 120.8862 | 121.1334 | 120.9274 | 121.0648 | 120.8725 | -120.9503 | -120.9366 | 120.6162 | 120.8313 | 19.8669 | 0.92468
1479.5156 | 120.9595 | -0.17395 | 120.7809 | 0.043716 | 0.0064493 | 0.071703 | 0.066512 | 0.0036893 | -0.0018756 | 0.00046565 | 0.014008 | 0.0050137 | 0.069556 | 0.067509 | 0.0033282 | 0.016291 | 0.001912 | 18.9514 | 120.9091 | -0.25177 | 120.4697 | 0.19684 | -0.059509 | -0.041199 | 0.75531 | 120.7809 | -0.21515 | 120.6482 | 0.022888 | -0.068665 | 0.050354 | -0.07782 | 0.12817 | -0.31128 | 0.37079 | 0.13275 | 0.11444 | 0.21057 | 0.19226 | -0.041199 | 0 | -0.13275 | 0.19684 | 0.2243 | 0.10528 | 0.2655 | 0.14648 | 0.44861 | 120.7214 | 0.23804 | 120.8633 | 121.1609 | 120.9961 | 121.0831 | 120.9549 | -121.0327 | -120.9961 | 120.6436 | 120.8221 | 19.1254 | 0.92926
1481.2656 | 120.9091 | -0.20599 | 120.8084 | 0.051346 | 0.0077311 | 0.071489 | 0.068434 | -0.0022923 | -0.0025166 | 0.0015338 | 0.010956 | 0.0082181 | 0.07041 | 0.066441 | -0.0030804 | 0.014795 | -0.0040696 | 19.2215 | 120.9778 | -0.28839 | 120.433 | 0.073242 | -0.10986 | -0.09613 | 0.74616 | 120.8496 | -0.27008 | 120.6116 | -0.032043 | -0.12817 | 0.009155 | -0.082397 | 0.16937 | -0.37537 | 0.27924 | 0.10986 | 0.096131 | 0.19226 | 0.17853 | -0.064087 | 0.041198 | -0.19684 | 0.17395 | 0.21515 | 0.07782 | 0.27924 | 0.14191 | 0.36163 | 120.7214 | 0.23804 | 120.8817 | 121.2662 | 121.1197 | 121.1838 | 121.0556 | -121.0968 | -121.0785 | 120.639 | 120.8176 | 19.4275 | 0.95215
1483.0312 | 120.8633 | -0.19226 | 120.7397 | -0.0096891 | 0.0051675 | 0.067644 | 0.064803 | -0.00015586 | -0.0037982 | -0.0016706 | -0.0012513 | 0.0041593 | 0.071905 | 0.063237 | -0.001585 | 0.012446 | -0.0042832 | 19.5007 | 120.9274 | -0.25177 | 120.3781 | 0.09613 | -0.091553 | -0.07782 | 0.737 | 120.7855 | -0.2243 | 120.5566 | -0.032043 | -0.11444 | 0.004578 | -0.059509 | 0.18768 | -0.36163 | 0.28839 | 0.11444 | 0.10071 | 0.17395 | 0.16022 | -0.032043 | 0.045776 | -0.1831 | 0.16022 | 0.19684 | 0.07782 | 0.22888 | 0.10986 | 0.3479 | 120.6299 | 0.19226 | 120.7809 | 121.1792 | 121.0098 | 121.1197 | 120.9778 | -120.9915 | -120.9641 | 120.5704 | 120.7489 | 19.693 | 0.92926
1484.7188 | 121.0144 | -0.15106 | 120.7535 | -0.0020601 | 0.0043131 | 0.071275 | 0.067152 | 0.0056119 | -0.0040118 | 0.0013202 | -0.0012513 | 0.0043729 | 0.071478 | 0.06046 | 0.00461 | 0.015223 | -0.004924 | 19.5099 | 120.9732 | -0.23346 | 120.4651 | 0.10986 | -0.11902 | -0.086975 | 0.80109 | 120.8084 | -0.21515 | 120.7306 | 0.059509 | -0.027466 | 0.09613 | -0.082397 | 0.21973 | -0.28839 | 0.26093 | 0.064087 | 0.032043 | 0.14648 | 0.11444 | -0.064087 | 0.054932 | -0.022888 | 0.21057 | 0.24719 | 0.1236 | 0.31128 | 0.18768 | 0.34332 | 120.6985 | 0.27466 | 120.9457 | 121.2067 | 121.0236 | 121.1243 | 120.9595 | -120.9869 | -120.9686 | 120.6161 | 120.8817 | 19.6609 | 0.95215
1486.4688 | 121.0419 | -0.14191 | 120.7809 | 0.0055694 | 0.0043131 | 0.070421 | 0.063307 | -0.00058326 | -0.0037982 | 0.0017474 | -0.0012513 | 0.0030911 | 0.068488 | 0.069004 | 0.00033757 | 0.016718 | 0.0016982 | 20.3476 | 120.9274 | -0.21515 | 120.5704 | 0.2243 | 0.009155 | -0.009155 | 0.91095 | 120.8221 | -0.19226 | 120.7672 | 0.12817 | 0.013733 | 0.10071 | -0.073242 | 0.14648 | -0.21057 | 0.36621 | 0.13275 | 0.15106 | 0.20599 | 0.2243 | -0.050354 | 0.041199 | -0.013733 | 0.27008 | 0.24262 | 0.15564 | 0.29297 | 0.20599 | 0.43945 | 120.7855 | 0.32044 | 120.9595 | 121.1426 | 121.0144 | 121.0693 | 120.9641 | -120.9961 | -120.9732 | 120.7123 | 120.9091 | 20.4895 | 1.0529
1488.2188 | 120.932 | -0.18768 | 120.8588 | 0.013199 | 0.0062357 | 0.069353 | 0.064803 | -0.00015586 | -0.001662 | 0.0034564 | 0.0079041 | 0.0050137 | 0.068274 | 0.059178 | -0.0035076 | 0.015223 | -0.0044968 | 19.8029 | 120.9824 | -0.25177 | 120.4605 | 0.082397 | -0.1236 | -0.10529 | 0.79193 | 120.9 | -0.24261 | 120.6436 | -0.036621 | -0.1236 | -0.013733 | -0.064087 | 0.1236 | -0.39826 | 0.27008 | 0.082397 | 0.064087 | 0.14648 | 0.12817 | -0.054932 | 0.041198 | -0.21515 | 0.15106 | 0.17395 | 0.064087 | 0.22888 | 0.11902 | 0.33417 | 120.7123 | 0.20599 | 120.8862 | 121.2341 | 121.1426 | 121.17 | 121.0876 | -121.1105 | -121.1014 | 120.6482 | 120.8313 | 19.9905 | 0.97961
1489.9688 | 120.9961 | -0.1831 | 120.845 | 0.020828 | 0.0083719 | 0.071062 | 0.065657 | 0.0024075 | -0.0020892 | -0.00038875 | 0.0048523 | 0.0075771 | 0.068274 | 0.064305 | 0.00012397 | 0.015009 | -0.0027878 | 20.1736 | 121.0419 | -0.24719 | 120.5521 | 0.13275 | -0.073242 | -0.064087 | 0.79651 | 120.8954 | -0.21057 | 120.7397 | 0.018311 | -0.082397 | 0.041199 | -0.064087 | 0.19684 | -0.29297 | 0.31586 | 0.11902 | 0.10986 | 0.1831 | 0.17395 | -0.027466 | 0.050354 | -0.10529 | 0.20142 | 0.2243 | 0.10071 | 0.25177 | 0.12817 | 0.37994 | 120.7993 | 0.22888 | 120.9503 | 121.2891 | 121.106 | 121.225 | 121.0785 | -121.0922 | -121.0556 | 120.7352 | 120.9229 | 20.3568 | 0.97961
1491.6562 | 120.9686 | -0.20599 | 120.8908 | -0.0096891 | 0.0053811 | 0.071275 | 0.066084 | -0.00036966 | -0.0029438 | -0.001457 | 0.0018005 | 0.0058683 | 0.071051 | 0.064518 | -0.0017986 | 0.014368 | -0.0025742 | 20.0592 | 121.0419 | -0.24261 | 120.4926 | 0.064087 | -0.11444 | -0.11902 | 0.74616 | 120.9778 | -0.27466 | 120.6848 | -0.022888 | -0.12817 | 0 | -0.036621 | 0.15106 | -0.39825 | 0.27008 | 0.086975 | 0.091553 | 0.1236 | 0.12817 | -0.068664 | 0.086975 | -0.20599 | 0.18311 | 0.20599 | 0.07782 | 0.27466 | 0.14648 | 0.3067 | 120.7352 | 0.25177 | 120.9595 | 121.2845 | 121.2524 | 121.2479 | 121.1838 | -121.1334 | -121.1655 | 120.6985 | 120.8908 | 20.2652 | 0.95215
1493.4062 | 121.0968 | -0.14648 | 120.8771 | 0.051346 | 0.0085855 | 0.072343 | 0.069502 | 0.0062527 | -0.0018756 | 0.0026018 | 0.0048523 | 0.0060819 | 0.07041 | 0.067296 | 0.0037556 | 0.015009 | -0.0019332 | 20.6268 | 121.0556 | -0.23804 | 120.6436 | 0.21973 | -0.013733 | 0 | 0.86975 | 120.8954 | -0.20599 | 120.8221 | 0.086975 | -0.018311 | 0.10071 | -0.091553 | 0.17853 | -0.23346 | 0.36621 | 0.14648 | 0.13275 | 0.23804 | 0.2243 | -0.05951 | 0.018311 | -0.054931 | 0.23346 | 0.24719 | 0.12817 | 0.3067 | 0.18768 | 0.45776 | 120.8817 | 0.29297 | 121.0281 | 121.2936 | 121.1014 | 121.2021 | 121.0419 | -121.1151 | -121.0831 | 120.7901 | 120.9686 | 20.7733 | 1.0162
1495.1719 | 121.0648 | -0.16937 | 120.9457 | 0.058975 | 0.0087991 | 0.070848 | 0.06758 | 0.0043301 | -0.001662 | 0.00089285 | 0.014008 | 0.0067227 | 0.066779 | 0.065159 | -0.00051703 | 0.01565 | -0.004924 | 20.6131 | 121.106 | -0.27466 | 120.5978 | 0.10071 | -0.073242 | -0.073242 | 0.83771 | 120.9641 | -0.21515 | 120.7947 | 0.036621 | -0.064087 | 0.036621 | -0.10529 | 0.16022 | -0.3479 | 0.27008 | 0.096131 | 0.096131 | 0.20142 | 0.20142 | -0.045776 | 0.01831 | -0.15106 | 0.20599 | 0.20599 | 0.10529 | 0.25177 | 0.15106 | 0.37537 | 120.8725 | 0.25177 | 121.0098 | 121.3806 | 121.1792 | 121.2753 | 121.1334 | -121.2204 | -121.1609 | 120.7672 | 120.9641 | 20.7825 | 1.0071
1496.9375 | 121.0602 | -0.17395 | 120.9549 | 0.013199 | 0.0070901 | 0.068498 | 0.067366 | 0.0013393 | -0.001662 | -0.0033796 | 0.0048523 | 0.0056545 | 0.07041 | 0.06046 | 0.001192 | 0.016504 | -0.001506 | 21.0434 | 121.0831 | -0.25177 | 120.6024 | 0.10529 | -0.09613 | -0.086975 | 0.8606 | 120.9686 | -0.21973 | 120.7947 | 0 | -0.10529 | 0.032043 | -0.07782 | 0.12817 | -0.35248 | 0.27924 | 0.086975 | 0.07782 | 0.16479 | 0.15564 | -0.045777 | 0.013733 | -0.16022 | 0.17395 | 0.20599 | 0.068664 | 0.25177 | 0.11444 | 0.35706 | 120.8542 | 0.21973 | 121.0144 | 121.3348 | 121.1884 | 121.257 | 121.1426 | -121.2067 | -121.1746 | 120.7764 | 120.9686 | 21.2173 | 1.0345
1498.625 | 121.0556 | -0.21057 | 120.9824 | -0.0020601 | 0.0070901 | 0.067857 | 0.064803 | 0.0013393 | -0.0031574 | 0.0021746 | -0.0012513 | 0.0026639 | 0.070624 | 0.060032 | -0.0013714 | 0.013086 | -0.001506 | 21.1212 | 121.1014 | -0.24719 | 120.5795 | 0.073242 | -0.11444 | -0.10529 | 0.79651 | 120.9778 | -0.23346 | 120.7443 | -0.032043 | -0.10986 | -0.004578 | -0.036621 | 0.11902 | -0.40283 | 0.28381 | 0.10529 | 0.09613 | 0.14191 | 0.13275 | -0.022888 | -0.004578 | -0.23804 | 0.17853 | 0.20599 | 0.10071 | 0.22888 | 0.1236 | 0.32043 | 120.8267 | 0.20142 | 120.9778 | 121.3486 | 121.2112 | 121.3119 | 121.1884 | -121.2296 | -121.2158 | 120.7901 | 120.9549 | 21.3318 | 1.0071
1500.375 | 121.1655 | -0.14648 | 120.9229 | -0.0020601 | 0.0068765 | 0.071489 | 0.066512 | -0.0014377 | -0.0029438 | 0.00046565 | -0.0012513 | 0.75013 | 0.069769 | 0.063237 | 0.0061054 | 0.016291 | 0.74254 | 21.9543 | 121.0922 | -0.22888 | 120.6711 | 0.14648 | -0.054932 | -0.050354 | 3.2639 | 120.8633 | -0.10529 | 120.8313 | 0.19226 | 0.064087 | 120.7077 | -0.082398 | 0.16937 | -0.25177 | 0.29297 | 0.09613 | 0.091552 | 0.17853 | 0.17395 | 0.041198 | -0.05951 | -0.091553 | 0.33874 | 120.8542 | 0.21057 | 120.813 | 0.16937 | 0.37537 | 120.9 | 0.29755 | 120.9366 | 121.3211 | 120.9686 | 121.2387 | 121.0098 | -121.1517 | -121.0281 | 120.8176 | 120.9778 | 22.1008 | 3.4103
1502.1406 | 121.0876 | -0.18768 | 120.9595 | 0.028458 | 0.0081583 | 0.070421 | 0.068861 | 0.0030483 | -0.001662 | -0.001457 | 0.010956 | 0.76872 | 0.071051 | 0.059391 | 0.001833 | 0.016291 | 0.75899 | 22.3206 | 121.1105 | -0.25635 | 120.5978 | 0.10529 | -0.064087 | -0.064087 | 3.1265 | 120.9 | -0.16022 | 120.7352 | 0.12817 | 0.022888 | 120.6024 | -0.068665 | 0.15106 | -0.36163 | 0.29297 | 0.1236 | 0.1236 | 0.19226 | 0.19226 | 0.027466 | -0.05951 | -0.22431 | 0.31586 | 120.7901 | 0.21057 | 120.7626 | 0.1831 | 0.36163 | 120.8542 | 0.28839 | 120.8954 | 121.3669 | 121.0602 | 121.2982 | 121.0876 | -121.2158 | -121.1197 | 120.7855 | 120.9229 | 22.5082 | 3.3142
1503.9062 | 121.0464 | -0.18768 | 120.9137 | -0.0020601 | 0.0070901 | 0.071062 | 0.066084 | 0.0036893 | -0.0012348 | 0.0013202 | -0.0012513 | 0.76701 | 0.06806 | 0.061741 | 0.003542 | 0.01565 | 0.75814 | 22.1008 | 121.0922 | -0.25177 | 120.5154 | 0.032043 | -0.17395 | -0.14191 | 3.0716 | 120.9 | -0.17853 | 120.6985 | 0.054932 | -0.027466 | 120.5978 | -0.064087 | 0.17853 | -0.39825 | 0.21973 | 0.045776 | 0.013733 | 0.10986 | 0.07782 | 0.009155 | -0.013733 | -0.21515 | 0.24261 | 120.7855 | 0.16022 | 120.7764 | 0.15106 | 0.28381 | 120.7672 | 0.23346 | 120.8771 | 121.344 | 121.0785 | 121.2799 | 121.0876 | -121.1655 | -121.0922 | 120.7031 | 120.8862 | 22.2885 | 3.2593
1505.6094 | 120.9961 | -0.14191 | 120.813 | 0.013199 | 0.0070901 | 0.070634 | 0.066939 | -0.0014377 | -0.0023028 | -0.00060235 | -0.0012513 | 0.76444 | 0.067847 | 0.070286 | 0.003542 | 0.017145 | 0.74938 | 22.0917 | 120.9869 | -0.2243 | 120.4468 | 0.059509 | -0.14648 | -0.10071 | 3.2501 | 120.7718 | -0.14191 | 120.6436 | 0.10986 | 0.013733 | 120.5338 | -0.082397 | 0.17395 | -0.36621 | 0.20142 | 0.041199 | -0.004577 | 0.1236 | 0.07782 | 0 | -0.041198 | -0.16937 | 0.25177 | 120.6757 | 0.15564 | 120.6757 | 0.15564 | 0.28381 | 120.6711 | 0.25177 | 120.7855 | 121.2112 | 120.9137 | 121.1288 | 120.9137 | -121.0373 | -120.9549 | 120.5887 | 120.7855 | 22.2336 | 3.392
1507.375 | 121.0098 | -0.19684 | 120.8771 | 0.028458 | 0.0073037 | 0.07213 | 0.064803 | 0.0021939 | 0.00090142 | 0.0017474 | 0.017059 | 0.76124 | 0.068488 | 0.059391 | -0.00030343 | 0.015223 | 0.74596 | 22.8012 | 121.0693 | -0.2655 | 120.5338 | 0.09613 | -0.059509 | -0.068665 | 3.5339 | 120.8542 | -0.16022 | 120.6757 | 0.11444 | 0.013733 | 120.5795 | -0.068665 | 0.19226 | -0.34332 | 0.29297 | 0.12817 | 0.13733 | 0.19684 | 0.20599 | 0.036621 | -0.022888 | -0.20142 | 0.31128 | 120.7764 | 0.21057 | 120.7397 | 0.17395 | 0.36163 | 120.7993 | 0.27466 | 120.8359 | 121.3348 | 121.0144 | 121.2662 | 121.051 | -121.1426 | -121.0373 | 120.7306 | 120.8725 | 22.998 | 3.7308
1509.0781 | 121.1014 | -0.12817 | 120.8633 | -0.0020601 | 0.0066629 | 0.070207 | 0.06523 | 0.0041165 | -0.0029438 | 0.0028154 | 0.029266 | 0.75932 | 0.072333 | 0.063023 | 0.0037556 | 0.019495 | 0.74703 | 23.2956 | 121.0556 | -0.19684 | 120.6162 | 0.16937 | -0.027466 | -0.032043 | 3.685 | 120.8679 | -0.15564 | 120.7718 | 0.19684 | 0.091553 | 120.6802 | -0.068664 | 0.19226 | -0.24719 | 0.29755 | 0.096131 | 0.10071 | 0.1648 | 0.16937 | -0.027466 | 0.004578 | -0.091552 | 0.32501 | 120.8084 | 0.21973 | 120.8359 | 0.24719 | 0.36621 | 120.813 | 0.35248 | 120.9274 | 121.2524 | 121.0236 | 121.1838 | 120.9961 | -121.0602 | -121.019 | 120.7443 | 120.9 | 23.4238 | 3.8132
1510.8438 | 121.106 | -0.14191 | 120.9229 | -0.0020601 | 0.0051675 | 0.071275 | 0.065871 | 5.774e-05 | -0.0025166 | -0.00038875 | 0.0018005 | 0.8531 | 0.069769 | 0.059819 | 0.0026874 | 0.11563 | 0.7419 | 22.728 | 121.0785 | -0.22888 | 120.575 | 0.09613 | -0.11902 | -0.091553 | 7.5851 | 120.8405 | -0.12817 | 120.7535 | 0.16479 | 120.5292 | 120.6528 | -0.086975 | 0.15564 | -0.3479 | 0.23804 | 0.050354 | 0.022888 | 0.13733 | 0.10986 | 0.013733 | -0.082398 | -0.16937 | 0.3067 | 120.7947 | 120.6711 | 120.7809 | 120.6573 | 0.32501 | 120.8038 | 0.29297 | 120.8817 | 121.3074 | 120.9686 | 121.2204 | 120.9824 | -121.1517 | -121.051 | 120.7169 | 120.8954 | 22.8699 | 7.7271
1512.5938 | 121.0556 | -0.18768 | 120.9366 | 0.051346 | 0.0068765 | 0.071062 | 0.068007 | 0.00069854 | -0.0020892 | 0.0021746 | 0.0079041 | 0.85117 | 0.068488 | 0.06046 | -0.001585 | 0.11755 | 0.73272 | 23.1674 | 121.1334 | -0.26093 | 120.5933 | 0.10071 | -0.068665 | -0.086975 | 7.608 | 120.8908 | -0.15564 | 120.7031 | 0.15564 | 120.5063 | 120.6116 | -0.073242 | 0.19684 | -0.34332 | 0.28839 | 0.10071 | 0.11902 | 0.17395 | 0.19226 | 0.032043 | -0.045776 | -0.23346 | 0.34332 | 120.7993 | 120.694 | 120.7672 | 120.6619 | 0.36163 | 120.8542 | 0.31128 | 120.8588 | 121.3943 | 121.0464 | 121.3211 | 121.0785 | -121.1975 | -121.0922 | 120.7809 | 120.8908 | 23.3551 | 7.7957
1514.3438 | 121.1288 | -0.14191 | 120.9229 | -0.0020601 | 0.0038857 | 0.069994 | 0.066939 | 0.00069854 | -0.0018756 | 0.00089285 | -0.0012513 | 0.84541 | 0.066992 | 0.066014 | 0.0020466 | 0.11605 | 0.72759 | 22.8745 | 121.1014 | -0.25635 | 120.6024 | 0.10529 | -0.07782 | -0.068665 | 7.6813 | 120.8908 | -0.11444 | 120.7901 | 0.17853 | 120.575 | 120.6985 | -0.11444 | 0.17853 | -0.32044 | 0.24719 | 0.073242 | 0.064087 | 0.18768 | 0.17853 | 0.027466 | -0.032044 | -0.13275 | 0.32044 | 120.8405 | 120.7169 | 120.813 | 120.6894 | 0.36163 | 120.8588 | 0.29297 | 120.9045 | 121.3577 | 121.0052 | 121.2433 | 121.0327 | -121.1792 | -121.0373 | 120.7443 | 120.932 | 23.0164 | 7.8232
1516.0938 | 121.1609 | -0.13733 | 120.9412 | 0.0055694 | 0.0079447 | 0.068712 | 0.067793 | 0.0053983 | -0.003371 | -0.00017515 | -0.0012513 | 0.84049 | 0.068701 | 0.062382 | 0.0020466 | 0.11798 | 0.73037 | 22.6776 | 121.106 | -0.19684 | 120.6802 | 0.16022 | -0.022888 | -0.032043 | 7.8598 | 120.8817 | -0.11444 | 120.8176 | 0.21057 | 120.575 | 120.7214 | -0.059509 | 0.16479 | -0.26093 | 0.29755 | 0.10529 | 0.11444 | 0.1648 | 0.17395 | 0.022888 | -0.059509 | -0.1236 | 0.3479 | 120.8588 | 120.7123 | 120.8359 | 120.6894 | 0.35706 | 120.8771 | 0.32501 | 120.932 | 121.3028 | 120.9961 | 121.2433 | 121.019 | -121.138 | -121.0556 | 120.8176 | 120.9549 | 22.8149 | 7.9971
1517.8594 | 121.1426 | -0.14648 | 120.9412 | -0.0020601 | 0.0055947 | 0.070207 | 0.066512 | 0.0011257 | -0.0018756 | -0.00038875 | 0.0079041 | 0.83814 | 0.07041 | 0.064305 | -0.0017986 | 0.11627 | 0.72503 | 23.053 | 121.1197 | -0.23346 | 120.6299 | 0.13275 | -0.054932 | -0.036621 | 7.7957 | 120.9 | -0.14648 | 120.7626 | 0.17853 | 120.5887 | 120.6894 | -0.086975 | 0.17853 | -0.31128 | 0.27924 | 0.10986 | 0.091552 | 0.19684 | 0.17853 | 0 | -0.041199 | -0.17853 | 0.32501 | 120.8359 | 120.7352 | 120.8359 | 120.7352 | 0.36621 | 120.8633 | 0.32501 | 120.9091 | 121.3531 | 121.0464 | 121.2662 | 121.0464 | -121.1746 | -121.0876 | 120.7764 | 120.9091 | 23.1995 | 7.9422
1519.5938 | 121.1151 | -0.17853 | 121.0236 | 0.020828 | 0.0077311 | 0.070634 | 0.068434 | 0.0024075 | -0.0035846 | 0.00025205 | 0.014008 | 0.83622 | 0.068488 | 0.061528 | 0.00076477 | 0.11285 | 0.72225 | 22.2198 | 121.1563 | -0.25177 | 120.6665 | 0.13275 | -0.059509 | -0.059509 | 7.6309 | 120.9457 | -0.14648 | 120.7626 | 0.13275 | 120.5338 | 120.6757 | -0.073242 | 0.13275 | -0.35706 | 0.31128 | 0.11902 | 0.11902 | 0.19226 | 0.19226 | 0.032044 | -0.07782 | -0.26093 | 0.31128 | 120.8542 | 120.7123 | 120.8221 | 120.6802 | 0.38452 | 120.9183 | 0.27924 | 120.9091 | 121.4081 | 121.0922 | 121.3348 | 121.1243 | -121.2753 | -121.17 | 120.845 | 120.9412 | 22.3984 | 7.8094
1521.3594 | 121.0693 | -0.19684 | 121.0098 | -0.0020601 | 0.0066629 | 0.069994 | 0.068007 | 0.00091214 | -0.0012348 | 0.00025205 | -0.0012513 | 0.83323 | 0.069983 | 0.058964 | 0.00012397 | 0.11648 | 0.71947 | 22.1237 | 121.1746 | -0.22888 | 120.6024 | 0.036621 | -0.15564 | -0.12817 | 111.2823 | 120.9595 | -0.15106 | 120.7214 | 0.045776 | 120.4788 | 120.6253 | -0.032044 | 0.16479 | -0.40741 | 0.23346 | 0.068664 | 0.041198 | 0.10071 | 0.073242 | 0.045776 | -0.050354 | -0.28839 | 0.24261 | 120.8221 | 120.6757 | 120.7764 | 120.6299 | 0.2655 | 120.8313 | 0.19684 | 120.8725 | 121.4035 | 121.1105 | 121.3715 | 121.1563 | -121.2387 | -121.1609 | 120.7993 | 120.9183 | 22.3206 | 111.4792
1523.0625 | 121.1288 | -0.19684 | 121.019 | 0.043716 | 0.0062357 | 0.068925 | 0.063307 | -0.0016513 | -0.0040118 | 0.00089285 | 0.020111 | 0.82874 | 0.069983 | 0.060673 | -0.00030343 | 0.11392 | 0.71413 | 22.3984 | 121.2021 | -0.30212 | 120.639 | 0.064087 | -0.10986 | -0.07782 | 120.4239 | 120.9686 | -0.17853 | 120.7626 | 0.11444 | 120.4285 | 120.6802 | -0.10529 | 0.18311 | -0.37994 | 0.26093 | 0.11902 | 0.086975 | 0.2243 | 0.19226 | 0.01831 | -0.050354 | -0.25635 | 0.31128 | 120.8771 | 120.6253 | 120.8588 | 120.607 | 0.36621 | 120.9412 | 0.29297 | 120.9412 | 121.5042 | 121.1472 | 121.3989 | 121.1655 | -121.3211 | -121.1975 | 120.8359 | 120.9595 | 22.5952 | 120.6207
1524.7969 | 121.138 | -0.16022 | 121.019 | 0.0055694 | 0.0062357 | 0.071275 | 0.065871 | 0.0043301 | -0.0042254 | 0.001961 | 0.0018005 | 0.82426 | 0.069769 | 0.060032 | 0.0031146 | 0.11627 | 0.71071 | 22.1008 | 121.1975 | -0.24719 | 120.6253 | 0.064087 | -0.15564 | -0.11444 | 120.4376 | 120.9595 | -0.16022 | 120.7947 | 0.11902 | 120.5795 | 120.726 | -0.086975 | 0.17853 | -0.39368 | 0.2243 | 0.045776 | 0.004577 | 0.13275 | 0.091552 | 0 | -0.059509 | -0.2243 | 0.27924 | 120.8862 | 120.7397 | 120.8862 | 120.7397 | 0.31128 | 120.8725 | 0.27924 | 120.9549 | 121.4447 | 121.1197 | 121.3577 | 121.1197 | -121.2662 | -121.1792 | 120.7855 | 120.9549 | 22.261 | 120.5978
1526.5469 | 121.1517 | -0.18768 | 121.019 | 0.020828 | 0.0060221 | 0.07213 | 0.068221 | -0.0016513 | -0.00080758 | 0.0015338 | 0.0079041 | 0.82447 | 0.072974 | 0.052769 | 0.00012397 | 0.11392 | 0.70516 | 21.6202 | 121.1838 | -0.25177 | 120.7031 | 0.11902 | -0.064087 | -0.073242 | 120.5017 | 120.9915 | -0.14648 | 120.813 | 0.14648 | 120.6024 | 120.6985 | -0.064087 | 0.1648 | -0.31586 | 0.3067 | 0.11444 | 0.1236 | 0.17853 | 0.18768 | 0.041199 | -0.027466 | -0.20599 | 0.33417 | 120.8862 | 120.7901 | 120.845 | 120.7489 | 0.37079 | 120.9549 | 0.29297 | 120.9595 | 121.4355 | 121.138 | 121.3715 | 121.1792 | -121.2708 | -121.1655 | 120.8908 | 121.0007 | 21.8079 | 120.6894
1528.2344 | 121.1975 | -0.13733 | 121.0098 | 0.036087 | 0.0079447 | 0.072557 | 0.063948 | 0.0077481 | -0.00038018 | -0.00038875 | 0.014008 | 0.81678 | 0.071905 | 0.06345 | 0.0026874 | 0.11712 | 0.70559 | 20.961 | 121.17 | -0.24261 | 120.7443 | 0.18768 | -0.036621 | -0.009155 | 120.5521 | 120.9549 | -0.13275 | 120.8405 | 0.17853 | 119.1147 | 120.7214 | -0.10529 | 0.16022 | -0.2655 | 0.32501 | 0.12817 | 0.10071 | 0.23346 | 0.20599 | 0.004578 | -0.054932 | -0.16937 | 0.31586 | 120.8588 | 119.252 | 120.8542 | 119.2474 | 0.4303 | 120.9869 | 0.31128 | 120.9732 | 121.4127 | 121.0876 | 121.3074 | 121.0922 | -121.2524 | -121.1426 | 120.8817 | 120.9778 | 21.0983 | 120.6894
1529.9844 | 121.2296 | -0.13733 | 121.0098 | -0.0096891 | 0.0058083 | 0.070207 | 0.063948 | 0.0028347 | -0.00080758 | 0.0011066 | 0.026215 | 0.81315 | 0.071478 | 0.056401 | 0.0043964 | 0.11648 | 0.70217 | 21.4874 | 121.1517 | -0.20599 | 120.8038 | 0.21057 | 0.004578 | -0.004578 | 120.639 | 120.9778 | -0.15564 | 120.9 | 0.21515 | 119.1284 | 120.7672 | -0.068665 | 0.14191 | -0.20599 | 0.3479 | 0.13275 | 0.14191 | 0.20142 | 0.21057 | -0.018311 | -0.032044 | -0.10986 | 0.35248 | 120.9045 | 119.2657 | 120.9229 | 119.2841 | 0.41657 | 121.0098 | 0.37079 | 121.0556 | 121.3577 | 121.1334 | 121.2891 | 121.1151 | -121.2158 | -121.1655 | 120.9412 | 121.0373 | 21.6248 | 120.7764
1531.7344 | 121.2524 | -0.14648 | 121.0327 | 0.0055694 | 0.0075173 | 0.06978 | 0.063521 | -0.0018649 | -0.0029438 | 3.8448e-05 | 0.0018005 | 0.81165 | 0.069983 | 0.056401 | -0.00094423 | 0.11434 | 0.69918 | 20.6726 | 121.1609 | -0.21515 | 120.7764 | 0.20142 | 0.013733 | 0.009155 | 120.607 | 120.9686 | -0.13275 | 120.8908 | 0.22888 | 119.1193 | 120.7809 | -0.068665 | 0.12817 | -0.25635 | 0.3479 | 0.15564 | 0.16022 | 0.2243 | 0.22888 | 0.013733 | -0.064087 | -0.14191 | 0.37537 | 120.9274 | 119.2657 | 120.9137 | 119.252 | 0.41657 | 120.9915 | 0.36163 | 121.0236 | 121.376 | 121.1014 | 121.3074 | 121.1151 | -121.2479 | -121.1655 | 120.9229 | 121.0373 | 20.8191 | 120.7535
1533.4375 | 121.2982 | -0.1236 | 121.051 | 0.0055694 | 0.0073037 | 0.062517 | 0.06523 | -0.00036966 | -0.0044392 | -0.0010298 | 0.0018005 | 0.73603 | 0.067633 | 0.064946 | 0.02704 | 0.06457 | 0.69533 | 19.9173 | 121.1426 | -0.17853 | 120.7993 | 0.19684 | -0.027466 | -0.032043 | 121.1975 | 120.9915 | 4.2526 | 120.8817 | 0.29297 | 49.8642 | 121.1105 | -0.054932 | 0.091553 | -0.25177 | 0.32043 | 0.091553 | 0.09613 | 0.14648 | 0.15106 | 4.3762 | -0.059509 | -0.16937 | 0.41656 | 121.2341 | 49.9878 | 116.8579 | 45.6116 | 0.37537 | 120.9778 | -3.9597 | 116.629 | 121.3211 | 116.7389 | 121.2662 | 121.1151 | -121.2296 | -116.7984 | 120.9229 | 121.0052 | 20.0409 | 121.3211
1535.1406 | 121.1014 | -0.14191 | 121.0831 | -0.0096891 | 0.0090127 | 0.064012 | 0.063521 | 0.0028347 | -0.0027302 | -0.00038875 | -0.0012513 | 0.78645 | 0.066565 | 0.074986 | 0.001833 | 0.043421 | 0.70324 | 19.5007 | 121.1792 | -0.19226 | 120.7855 | 0.13733 | -0.022888 | 0.004578 | 120.9137 | 121.0373 | 1.3641 | 120.8817 | 0.50354 | 60.6857 | 120.9595 | -0.050354 | 0.09613 | -0.29755 | 0.27924 | 0.14649 | 0.11902 | 0.19684 | 0.16937 | 1.506 | -0.045777 | -0.20142 | 0.64545 | 121.1014 | 60.8276 | 119.5953 | 59.3216 | 0.32959 | 120.9778 | -0.8606 | 119.5175 | 121.3715 | 119.6732 | 121.3211 | 121.1792 | -121.2753 | -119.7189 | 120.9274 | 121.0236 | 19.6426 | 121.0556
1536.8906 | 121.3028 | -0.15106 | 121.0602 | 0.013199 | 0.0075173 | 0.069566 | 0.066725 | 5.774e-05 | -0.0023028 | -0.003166 | -0.0012513 | 0.70484 | 0.068274 | 0.070286 | 0.00033757 | 0.016718 | 0.69213 | 18.837 | 121.1884 | -0.19684 | 120.8267 | 0.21515 | 0.027466 | 0.013733 | 120.7031 | 121.0052 | -0.11902 | 120.9457 | 0.21057 | 0.16937 | 120.8542 | -0.045776 | 0.12817 | -0.23346 | 0.36621 | 0.16479 | 0.17853 | 0.21057 | 0.2243 | 0.032043 | -0.054932 | -0.11444 | 0.36163 | 121.0052 | 0.32044 | 120.9732 | 0.28839 | 0.41199 | 121.0236 | 0.32959 | 121.0648 | 121.3852 | 121.1243 | 121.3394 | 121.1563 | -121.257 | -121.1792 | 120.9778 | 121.0968 | 18.988 | 120.8542
1538.6406 | 121.2982 | -0.14648 | 121.0831 | 0.043716 | 0.0094399 | 0.073839 | 0.066939 | 0.0017667 | 0.00090142 | 3.8448e-05 | 0.020111 | 0.76893 | 0.13407 | 0.062596 | 0.002901 | 0.016932 | 0.6917 | 19.0887 | 121.2479 | -0.22888 | 120.8588 | 0.19226 | -0.022888 | 0.004578 | 120.6894 | 121.0602 | -0.15564 | 120.9457 | 120.8725 | 0.14191 | 120.845 | -0.082398 | 0.1648 | -0.2243 | 0.33874 | 0.15106 | 0.1236 | 0.23346 | 0.20599 | -0.009156 | -0.022888 | -0.13733 | 121.019 | 120.9915 | 0.28839 | 121.0007 | 0.29755 | 0.42114 | 121.0876 | 121.0281 | 121.1014 | 121.4767 | 121.2158 | 121.3943 | 121.2067 | -121.312 | -121.2387 | 121.0052 | 121.0922 | 19.2352 | 120.8359
1540.3281 | 121.1655 | -0.12817 | 121.1014 | -0.0096891 | 0.0079447 | 0.068285 | 0.068007 | -0.00015586 | -0.0037982 | -0.004234 | -0.0012513 | 0.78004 | 0.13428 | 0.082676 | -0.0043622 | 0.034235 | 0.68999 | 18.631 | 121.2433 | -0.21057 | 120.7077 | 0.009155 | -0.064087 | -0.086975 | 121.1929 | 121.0693 | 0.022888 | 120.8221 | 121.0281 | 38.6856 | 120.9915 | -0.082397 | 0.14191 | -0.39368 | 0.13733 | 0.041199 | 0.064087 | 0.1236 | 0.14648 | 0.15106 | -0.032043 | -0.27923 | 121.1563 | 121.1197 | 38.8138 | 120.9686 | 38.6627 | 0.21973 | 120.9183 | 121.0052 | 120.7993 | 121.4539 | 121.0464 | 121.3715 | 121.1975 | -121.3119 | -121.0785 | 120.8359 | 120.9503 | 18.7592 | 121.3211
1542.0156 | 121.3028 | -0.16022 | 121.1014 | -0.0020601 | 0.0036721 | 0.069994 | 0.064803 | 0.0056119 | -0.0040118 | -0.0035932 | -0.0012513 | 0.86442 | 0.13492 | 0.061528 | 0.00076477 | 0.11648 | 0.68657 | 18.718 | 121.2524 | -0.23346 | 120.7855 | 0.14648 | -0.032043 | -0.013733 | 120.5933 | 121.0098 | -0.13733 | 120.9503 | 120.9045 | 120.7031 | 120.845 | -0.073242 | 0.15106 | -0.31586 | 0.3067 | 0.14648 | 0.12817 | 0.21973 | 0.20142 | 0.022888 | -0.091552 | -0.15106 | 121.0648 | 121.0052 | 120.8633 | 120.9824 | 120.8405 | 0.37994 | 121.019 | 121.0419 | 121.0876 | 121.4859 | 121.1472 | 121.4127 | 121.17 | -121.3348 | -121.2387 | 120.9457 | 121.1105 | 18.8782 | 120.7535
1543.7812 | 121.2936 | -0.14191 | 121.0693 | 0.036087 | 0.0085855 | 0.072343 | 0.067152 | 0.0021939 | -0.0012348 | -0.0012434 | 0.017059 | 0.86271 | 0.13792 | 0.061955 | 0.00033757 | 0.11605 | 0.68059 | 18.956 | 121.2296 | -0.21515 | 120.8588 | 0.19684 | -0.009155 | 0 | 120.6482 | 121.0648 | -0.14191 | 120.9457 | 120.8954 | 120.7352 | 120.8221 | -0.073242 | 0.16022 | -0.21057 | 0.33875 | 0.14191 | 0.13275 | 0.21515 | 0.20599 | 0 | -0.004578 | -0.1236 | 121.0373 | 120.9641 | 120.8771 | 120.9641 | 120.8771 | 0.41199 | 121.0739 | 121.0373 | 121.0876 | 121.4447 | 121.2067 | 121.3715 | 121.2067 | -121.2845 | -121.2112 | 121.0007 | 121.0876 | 19.0979 | 120.7901
1545.4688 | 121.1838 | -0.20599 | 121.1288 | 0.013199 | 0.0073037 | 0.071275 | 0.066298 | 0.0026211 | -0.0027302 | 0.001961 | -0.0012513 | 0.86015 | 0.13535 | 0.0611 | 0.001833 | 0.1152 | 0.68145 | 19.2352 | 121.2799 | -0.23804 | 120.7169 | -0.004578 | -0.17853 | -0.15564 | 120.4651 | 121.0785 | -0.15564 | 120.8359 | 120.7672 | 120.6207 | 120.7489 | -0.032043 | 0.15106 | -0.41199 | 0.20142 | 0.050354 | 0.027466 | 0.082397 | 0.059509 | 0.050354 | -0.050354 | -0.29297 | 120.9732 | 120.9549 | 120.8267 | 120.9045 | 120.7764 | 0.23346 | 120.9549 | 120.9229 | 120.9915 | 121.5179 | 121.2341 | 121.4859 | 121.2845 | -121.3669 | -121.2845 | 120.9229 | 121.0419 | 19.4412 | 120.6711
1547.2188 | 121.2936 | -0.16479 | 121.1197 | 0.036087 | 0.0081583 | 0.069566 | 0.06758 | 0.0062527 | -0.0027302 | 0.00046565 | 0.010956 | 0.85694 | 0.13428 | 0.067509 | 0.001192 | 0.11712 | 0.67653 | 20.018 | 121.2662 | -0.24261 | 120.8359 | 0.20599 | -0.013733 | -0.013733 | 120.639 | 121.0556 | -0.15564 | 120.9229 | 120.8862 | 120.7352 | 120.8405 | -0.07782 | 0.14648 | -0.28381 | 0.37079 | 0.15106 | 0.15106 | 0.22888 | 0.22888 | 0.009155 | -0.064087 | -0.19684 | 121.051 | 121.0052 | 120.9 | 120.9961 | 120.8908 | 0.44861 | 121.0785 | 121.0419 | 121.0785 | 121.5088 | 121.2112 | 121.431 | 121.2204 | -121.3623 | -121.2753 | 121.0007 | 121.0876 | 20.1828 | 120.8038
1548.9688 | 121.2296 | -0.1831 | 121.106 | -0.0020601 | 0.0064493 | 0.068071 | 0.067152 | 5.774e-05 | -0.0020892 | 0.001961 | -0.0043029 | 0.8563 | 0.13642 | 0.063023 | 0.00076477 | 0.11349 | 0.67739 | 19.7388 | 121.3257 | -0.23804 | 120.7169 | 0.018311 | -0.15564 | -0.14648 | 120.5154 | 121.0922 | -0.14191 | 120.8771 | 120.8176 | 120.6528 | 120.7855 | -0.054932 | 0.21973 | -0.3891 | 0.20142 | 0.036621 | 0.027465 | 0.091553 | 0.082397 | 0.041198 | -0.013733 | -0.22888 | 121.0007 | 120.9686 | 120.8359 | 120.9274 | 120.7947 | 0.25635 | 120.9549 | 120.9595 | 121.019 | 121.5637 | 121.2341 | 121.5088 | 121.2753 | -121.344 | -121.2479 | 120.9 | 121.0602 | 19.9219 | 120.6985
1550.6406 | 121.2982 | -0.16479 | 121.106 | 0.020828 | 0.0055947 | 0.073198 | 0.066298 | 0.0019803 | -0.00059378 | -0.00017515 | 0.0079041 | 0.85331 | 0.1377 | 0.064305 | -8.9634e-05 | 0.11669 | 0.67376 | 19.5236 | 121.2708 | -0.23346 | 120.8221 | 0.091553 | -0.068665 | -0.045776 | 120.6024 | 121.0876 | -0.13275 | 120.9091 | 120.8862 | 120.7489 | 120.8405 | -0.068664 | 0.16479 | -0.28381 | 0.25635 | 0.11902 | 0.09613 | 0.18768 | 0.16479 | 0.032044 | -0.018311 | -0.19684 | 121.051 | 121.0052 | 120.9137 | 120.9732 | 120.8817 | 0.32501 | 121.0556 | 121.019 | 121.0419 | 121.5042 | 121.2204 | 121.4355 | 121.2524 | -121.3394 | -121.2387 | 120.9869 | 121.0739 | 19.6884 | 120.7672
1552.3906 | 121.3257 | -0.16022 | 121.1243 | -0.0020601 | 0.0070901 | 0.070848 | 0.064375 | 0.0015529 | -0.0029438 | -0.0018842 | -0.0043029 | 0.84947 | 0.13535 | 0.051274 | -0.0017986 | 0.1152 | 0.67269 | 19.1345 | 121.2387 | -0.20599 | 120.8725 | 0.18768 | -0.009155 | -0.004578 | 120.6665 | 121.106 | -0.11444 | 120.9686 | 120.9686 | 120.8084 | 120.8771 | -0.045777 | 0.11444 | -0.25177 | 0.3479 | 0.15564 | 0.15106 | 0.20142 | 0.19684 | 0.045776 | -0.018311 | -0.15564 | 121.1288 | 121.0373 | 120.9686 | 120.9915 | 120.9229 | 0.39368 | 121.0785 | 121.0831 | 121.0831 | 121.4447 | 121.2204 | 121.3989 | 121.2662 | -121.3303 | -121.2387 | 121.0327 | 121.1288 | 19.2947 | 120.8267
1554.1562 | 121.2204 | -0.19684 | 121.1472 | -0.0020601 | 0.0058083 | 0.06978 | 0.066725 | -0.00036966 | -0.0027302 | -0.00038875 | -0.0012513 | 0.85075 | 0.13535 | 0.058537 | 0.0031146 | 0.11392 | 0.67034 | 18.5303 | 121.344 | -0.25177 | 120.7214 | -0.004578 | -0.17395 | -0.15106 | 120.5429 | 121.1197 | -0.14648 | 120.8817 | 120.8267 | 120.6619 | 120.7993 | -0.054932 | 0.19684 | -0.42572 | 0.19226 | 0.045776 | 0.022888 | 0.10071 | 0.07782 | 0.050354 | -0.027466 | -0.2655 | 121.0236 | 120.9961 | 120.8588 | 120.9457 | 120.8084 | 0.24719 | 120.9732 | 120.9732 | 121.0281 | 121.5958 | 121.2662 | 121.5408 | 121.3165 | -121.3989 | -121.2936 | 120.9183 | 121.0785 | 18.7271 | 120.7397
1555.9062 | 121.2479 | -0.1831 | 121.1884 | -0.017319 | 0.0038857 | 0.070207 | 0.068434 | 0.0019803 | -0.0031574 | 0.0021746 | 0.017059 | 0.84754 | 0.13727 | 0.057896 | -0.0020122 | 0.1137 | 0.66863 | 14.9918 | 121.3806 | -0.26093 | 120.7947 | 0.054932 | -0.091553 | -0.064087 | 120.5704 | 121.1746 | -0.17853 | 120.8908 | 120.8725 | 120.7123 | 120.8267 | -0.07782 | 0.19226 | -0.39368 | 0.23804 | 0.11902 | 0.091552 | 0.19684 | 0.16937 | 0.004577 | -0.013732 | -0.29755 | 121.0556 | 121.0098 | 120.8954 | 121.0052 | 120.8908 | 0.31586 | 121.0556 | 121.051 | 121.0693 | 121.6415 | 121.3531 | 121.5637 | 121.3577 | -121.4493 | -121.3669 | 120.9778 | 121.0739 | 15.1749 | 120.7535
1557.5938 | 121.3394 | -0.14648 | 121.138 | 0.043716 | 0.0081583 | 0.072771 | 0.065657 | 0.0077481 | -0.0010212 | 0.00046565 | 0.0079041 | 0.84605 | 0.13514 | 0.0658 | 0.002901 | 0.1152 | 0.66414 | 15.6372 | 121.3486 | -0.21973 | 120.8862 | 0.14648 | -0.022888 | -0.022888 | 120.6894 | 121.106 | -0.1236 | 120.9961 | 120.9366 | 120.7993 | 120.8954 | -0.073243 | 0.21057 | -0.25177 | 0.29297 | 0.1236 | 0.1236 | 0.19684 | 0.19684 | 0.022888 | -0.032043 | -0.14191 | 121.0831 | 121.0419 | 120.9457 | 121.019 | 120.9229 | 0.36621 | 121.106 | 121.0602 | 121.1197 | 121.5683 | 121.2296 | 121.4951 | 121.2524 | -121.3577 | -121.2616 | 121.0327 | 121.1426 | 15.7837 | 120.8359
1559.3594 | 121.2936 | -0.15564 | 121.1929 | 0.0055694 | 0.0079447 | 0.071275 | 0.065657 | 0.00027134 | -0.0014484 | 0.00089285 | 0.0079041 | 0.84605 | 0.1345 | 0.058751 | 0.00012397 | 0.11434 | 0.66436 | 15.1611 | 121.3715 | -0.22888 | 120.8771 | 0.10986 | -0.073242 | -0.059509 | 120.6802 | 121.1609 | -0.13275 | 120.9778 | 120.9229 | 120.7718 | 120.8679 | -0.073242 | 0.17853 | -0.31586 | 0.2655 | 0.096131 | 0.082398 | 0.16937 | 0.15564 | 0.022889 | -0.032043 | -0.21515 | 121.0785 | 121.0236 | 120.9274 | 121.0007 | 120.9045 | 0.33875 | 121.106 | 121.0556 | 121.1105 | 121.6003 | 121.2936 | 121.5271 | 121.3165 | -121.4218 | -121.3257 | 121.0327 | 121.1334 | 15.3168 | 120.8359
1561.0625 | 121.2845 | -0.17853 | 121.2158 | 0.058975 | 0.0087991 | 0.069139 | 0.068007 | 0.0032619 | -0.0037982 | -0.00017515 | 0.017059 | 0.84391 | 0.13813 | 0.055546 | -0.0017986 | 0.11584 | 0.66286 | 15.1337 | 121.3989 | -0.27008 | 120.8267 | 0.041199 | -0.082397 | -0.07782 | 120.5978 | 121.2021 | -0.16937 | 120.9274 | 120.9 | 120.7397 | 120.8542 | -0.091553 | 0.18311 | -0.3891 | 0.21973 | 0.10071 | 0.096131 | 0.19226 | 0.18768 | 0.009155 | -0.013733 | -0.28839 | 121.0785 | 121.0327 | 120.9183 | 121.0236 | 120.9091 | 0.31128 | 121.0968 | 121.0693 | 121.0968 | 121.669 | 121.3715 | 121.5775 | 121.3806 | -121.4859 | -121.3852 | 121.0052 | 121.106 | 15.3122 | 120.7764
1562.8125 | 121.3943 | -0.10986 | 121.1517 | 0.0055694 | 0.0075173 | 0.071489 | 0.066512 | 0.0034755 | 4.7018e-05 | 0.00067925 | 0.026215 | 0.839 | 0.13685 | 0.065587 | 0.00461 | 0.11477 | 0.65624 | 15.0375 | 121.3577 | -0.21515 | 120.9595 | 0.19684 | -0.004578 | 0.013733 | 120.7764 | 121.1426 | -0.14648 | 121.0602 | 121.0327 | 120.8633 | 120.9686 | -0.10529 | 0.20599 | -0.19226 | 0.3067 | 0.1236 | 0.10529 | 0.22888 | 0.21057 | -0.036621 | -0.009155 | -0.091552 | 121.1426 | 121.0785 | 120.9732 | 121.1151 | 121.0098 | 0.41199 | 121.1746 | 121.1792 | 121.2067 | 121.5729 | 121.2891 | 121.4676 | 121.2524 | -121.3669 | -121.2982 | 121.0693 | 121.17 | 15.1474 | 120.8862
1564.5625 | 121.3806 | -0.15106 | 121.1838 | -0.0020601 | 0.0064493 | 0.070207 | 0.065657 | -0.0012241 | -0.0029438 | -0.0016706 | 0.0018005 | 0.83772 | 0.1345 | 0.059605 | -0.00073063 | 0.11392 | 0.65773 | 14.6118 | 121.3303 | -0.21973 | 120.9366 | 0.16022 | 0 | -0.004578 | 120.7169 | 121.17 | -0.1236 | 121.0236 | 121.0007 | 120.8771 | 120.932 | -0.068665 | 0.14648 | -0.24719 | 0.31128 | 0.14648 | 0.15106 | 0.21515 | 0.21973 | 0.027466 | -0.013733 | -0.16022 | 121.1517 | 121.0831 | 121.0281 | 121.0556 | 121.0007 | 0.37994 | 121.1563 | 121.1243 | 121.1472 | 121.55 | 121.2936 | 121.4813 | 121.3211 | -121.4035 | -121.3074 | 121.0876 | 121.1746 | 14.7629 | 120.8679
1566.3125 | 121.3669 | -0.15564 | 121.1838 | 0.043716 | 0.0062357 | 0.074693 | 0.065016 | -0.00015586 | -0.00080758 | 0.0026018 | 0.017059 | 0.83579 | 0.1345 | 0.057469 | 0.0041828 | 0.11563 | 0.65731 | 14.1541 | 121.376 | -0.21057 | 120.9549 | 0.18768 | -0.004578 | 0.009155 | 120.7764 | 121.17 | -0.11444 | 121.0419 | 121.0007 | 120.8633 | 120.9457 | -0.054931 | 0.19226 | -0.22888 | 0.34332 | 0.16479 | 0.15106 | 0.21973 | 0.20599 | 0.041199 | -0.013733 | -0.14191 | 121.1563 | 121.1014 | 121.019 | 121.0602 | 120.9778 | 0.39825 | 121.1655 | 121.1151 | 121.1563 | 121.5866 | 121.2845 | 121.5317 | 121.3257 | -121.3943 | -121.2982 | 121.1105 | 121.1975 | 14.3097 | 120.932
1568 | 121.4172 | -0.13275 | 121.1929 | 0.0055694 | 0.0058083 | 0.071489 | 0.065443 | 0.0043301 | -0.0035846 | -0.00038875 | -0.0012513 | 0.83344 | 0.13578 | 0.068577 | 0.0054646 | 0.11456 | 0.65432 | 14.003 | 121.3852 | -0.19226 | 120.9366 | 0.14191 | -0.045776 | -0.018311 | 120.7764 | 121.1197 | -0.11444 | 121.0922 | 121.0419 | 120.8725 | 121.0098 | -0.05951 | 0.19226 | -0.25635 | 0.27466 | 0.11444 | 0.086975 | 0.17395 | 0.14648 | 0.01831 | -0.073242 | -0.10071 | 121.1746 | 121.1426 | 121.0052 | 121.1243 | 120.9869 | 0.33417 | 121.1288 | 121.1563 | 121.2067 | 121.5775 | 121.2341 | 121.5179 | 121.2524 | -121.3852 | -121.3074 | 121.0693 | 121.225 | 14.1357 | 120.9091
1569.75 | 121.312 | -0.19226 | 121.2387 | -0.0020601 | 0.0092263 | 0.068925 | 0.066298 | -0.0035739 | -0.0044392 | 0.00067925 | 0.0048523 | 0.83216 | 0.13578 | 0.055119 | -0.002226 | 0.11349 | 0.65645 | 14.1861 | 121.3623 | -0.22888 | 120.8817 | 0.059509 | -0.086975 | -0.09613 | 120.639 | 121.2067 | -0.13733 | 120.9549 | 120.9457 | 120.7809 | 120.8771 | -0.036621 | 0.1236 | -0.35706 | 0.25177 | 0.096131 | 0.10529 | 0.13275 | 0.14191 | 0.054932 | -0.032043 | -0.28381 | 121.138 | 121.0693 | 120.9732 | 121.0144 | 120.9183 | 0.28839 | 121.1105 | 121.0831 | 121.0922 | 121.5912 | 121.344 | 121.5546 | 121.3989 | -121.4676 | -121.376 | 121.0739 | 121.1472 | 14.3784 | 120.8313
1571.5 | 121.4355 | -0.15106 | 121.2296 | -0.0096891 | 0.0053811 | 0.068712 | 0.064375 | -0.00015586 | -0.0029438 | 0.00025205 | -0.0012513 | 0.82853 | 0.13471 | 0.059178 | -0.00051703 | 0.11498 | 0.64919 | 13.6505 | 121.3531 | -0.19684 | 120.9641 | 0.17853 | 0.009155 | 0.013733 | 120.7809 | 121.1929 | -0.1236 | 121.0968 | 121.0785 | 120.9366 | 120.9961 | -0.045776 | 0.1236 | -0.2655 | 0.32959 | 0.16479 | 0.16022 | 0.21057 | 0.20599 | 0.027466 | -0.036621 | -0.13275 | 121.2296 | 121.1472 | 121.0876 | 121.1197 | 121.0602 | 0.37537 | 121.1609 | 121.2021 | 121.2204 | 121.55 | 121.3165 | 121.5042 | 121.344 | -121.4264 | -121.3531 | 121.1151 | 121.2479 | 13.8016 | 120.932
1573.1875 | 121.3348 | -0.1831 | 121.257 | 0.028458 | 0.0066629 | 0.071916 | 0.066512 | 0.0043301 | -0.0037982 | 0.001961 | -0.0012513 | 0.82896 | 0.13578 | 0.063237 | 0.00012397 | 0.11392 | 0.64834 | 13.3301 | 121.431 | -0.23346 | 120.8954 | 0.082397 | -0.1236 | -0.082397 | 120.6894 | 121.2158 | -0.12817 | 121.0144 | 120.9595 | 120.7901 | 120.9183 | -0.050354 | 0.17395 | -0.36163 | 0.2655 | 0.10071 | 0.059509 | 0.15106 | 0.10986 | 0.054931 | -0.041199 | -0.24262 | 121.1426 | 121.1014 | 120.9732 | 121.0464 | 120.9183 | 0.31586 | 121.1288 | 121.0876 | 121.1426 | 121.6644 | 121.344 | 121.6141 | 121.3989 | -121.4905 | -121.3852 | 121.0785 | 121.1975 | 13.5132 | 120.8725
1574.9375 | 120.9 | -0.16479 | 120.8725 | -0.0020601 | 0.0064493 | 0.06978 | 0.066725 | 0.0036893 | -0.001662 | -0.00081595 | -0.0012513 | 0.051797 | 0.0078186 | -0.0068316 | 0.0024738 | 0.017786 | -0.0027878 | 13.1516 | 121.0052 | -0.21515 | 120.4651 | 0.054932 | -0.13733 | -0.11444 | 0.64545 | 0.89264 | 0.6134 | 0.6546 | 0.72784 | 0.62714 | 0.76904 | -0.050354 | 0.13275 | -0.40741 | 0.21973 | 0.050354 | 0.027466 | 0.10071 | 0.07782 | 0.7782 | -119.9799 | -120.2179 | 0.89264 | 0.93384 | 0.79193 | 0.15564 | 0.013733 | 0.27008 | 120.6802 | 0.11444 | 0.041199 | 121.2204 | 0.27924 | 121.17 | 1.0574 | -121.0876 | -120.2591 | 120.6299 | 0.8194 | 13.3163 | 0.81024
1576.625 | 121.2067 | -0.15106 | 121.0648 | 0.0055694 | 0.0040995 | 0.070421 | 0.061598 | -0.0014377 | -0.0018756 | -0.00060235 | -0.0012513 | 0.050729 | 0.0073914 | 0.0017132 | 0.00012397 | 0.01565 | 0.0023392 | 12.7945 | 121.2158 | -0.20599 | 120.7306 | 0.09613 | -0.07782 | -0.059509 | 0.43945 | 0.63629 | 0.38452 | 0.5127 | 0.60425 | 0.49896 | 0.63171 | -0.054932 | 0.15106 | -0.33417 | 0.24719 | 0.091553 | 0.073242 | 0.14649 | 0.12817 | 0.53558 | -120.4285 | -120.5521 | 0.75531 | 0.78278 | 0.65002 | 0.24719 | 0.11444 | 0.30212 | 120.9366 | 0.21973 | 0.12817 | 121.4218 | 0.25177 | 121.3669 | 0.78735 | -121.2708 | -120.6802 | 120.8817 | 0.66376 | 12.9456 | 0.59052
1578.3906 | 121.312 | -0.15564 | 121.106 | 0.0055694 | 0.0064493 | 0.068071 | 0.064375 | -0.0018649 | -0.0027302 | 0.00025205 | -0.0012513 | 0.04902 | 0.0065368 | 0.0038494 | 0.00033757 | 0.016504 | 0.00298 | 13.2202 | 121.2387 | -0.20599 | 120.813 | 0.1236 | -0.045776 | -0.022888 | 0.48523 | 0.62714 | 0.39368 | 0.54016 | 0.62714 | 0.55389 | 0.65918 | -0.050354 | 0.13275 | -0.29297 | 0.27924 | 0.13275 | 0.10986 | 0.18311 | 0.16022 | 0.54932 | -120.4788 | -120.5658 | 0.78278 | 0.81482 | 0.70953 | 0.2655 | 0.16022 | 0.32959 | 121.019 | 0.23346 | 0.14648 | 121.4447 | 0.23346 | 121.3943 | 0.78278 | -121.312 | -120.7123 | 120.9686 | 0.6958 | 13.3759 | 0.64087
1580.0781 | 121.3074 | -0.13733 | 121.1334 | -0.0096891 | 0.0070901 | 0.071062 | 0.065016 | 0.00069854 | -0.0031574 | -0.002525 | -0.0012513 | 0.050943 | 0.0063232 | 0.0027814 | 0.00033757 | 0.015436 | -0.0008652 | 13.1516 | 121.344 | -0.17853 | 120.8359 | 0.11902 | -0.07782 | -0.041199 | 0.4303 | 0.56305 | 0.36621 | 0.4715 | 0.56763 | 0.46692 | 0.59509 | -0.041199 | 0.21057 | -0.29755 | 0.25635 | 0.09613 | 0.059509 | 0.13733 | 0.10071 | 0.50354 | -120.5704 | -120.6619 | 0.70496 | 0.73242 | 0.60425 | 0.22888 | 0.10071 | 0.29755 | 121.0144 | 0.20142 | 0.10529 | 121.5225 | 0.19684 | 121.4813 | 0.70038 | -121.312 | -120.7672 | 120.9732 | 0.60883 | 13.2889 | 0.56763
1581.8281 | 121.3257 | -0.14191 | 121.1929 | 0.0055694 | 0.0053811 | 0.071489 | 0.065657 | 0.0019803 | -0.0031574 | -0.0010298 | -0.0012513 | 0.052225 | 0.0065368 | 0.002995 | 0.0048236 | 0.016291 | -0.0010788 | 13.2935 | 121.3943 | -0.23346 | 120.8267 | 0.045776 | -0.13275 | -0.10071 | 0.3891 | 0.62714 | 0.34332 | 0.45776 | 0.5127 | 0.4303 | 0.56305 | -0.091552 | 0.20142 | -0.36621 | 0.18768 | 0.041199 | 0.009156 | 0.13275 | 0.10071 | 0.48523 | -120.5658 | -120.7352 | 0.6546 | 0.70496 | 0.57221 | 0.21973 | 0.086975 | 0.27924 | 121.0602 | 0.16937 | 0.11444 | 121.6278 | 0.28381 | 121.5363 | 0.76904 | -121.4264 | -120.8496 | 120.9686 | 0.59967 | 13.4354 | 0.53101
1583.5156 | 121.3531 | -0.15106 | 121.2021 | -0.0096891 | 0.0040995 | 0.069353 | 0.063094 | 0.00048494 | -0.0048664 | 0.00046565 | -0.0012513 | 0.049234 | 0.0067504 | -0.003841 | -8.9634e-05 | 0.016077 | 0.0008438 | 13.0234 | 121.3486 | -0.19684 | 120.8771 | 0.091553 | -0.086975 | -0.054932 | 0.43945 | 0.63629 | 0.41199 | 0.50354 | 0.59509 | 0.51727 | 0.63171 | -0.045776 | 0.14648 | -0.32501 | 0.24261 | 0.09613 | 0.064087 | 0.14191 | 0.10986 | 0.56305 | -120.5658 | -120.6985 | 0.74616 | 0.78278 | 0.66834 | 0.21973 | 0.10529 | 0.28839 | 121.0739 | 0.18311 | 0.091553 | 121.5454 | 0.2243 | 121.4996 | 0.78735 | -121.3989 | -120.7901 | 121.0281 | 0.6546 | 13.1744 | 0.59052
1585.2656 | 121.3028 | -0.16479 | 121.2753 | -0.0020601 | 0.0073037 | 0.073625 | 0.066512 | 0.0036893 | -0.0010212 | 0.00025205 | 0.0048523 | 0.052438 | 0.0048278 | -0.008327 | -0.00073063 | 0.01565 | -0.001506 | 12.4146 | 121.431 | -0.22888 | 120.8954 | 0.059509 | -0.11902 | -0.10529 | 0.47607 | 0.72327 | 0.4303 | 0.48981 | 0.53558 | 0.46692 | 0.61798 | -0.064087 | 0.15564 | -0.37994 | 0.2243 | 0.059509 | 0.045776 | 0.1236 | 0.10986 | 0.59509 | -120.5521 | -120.7855 | 0.70038 | 0.78278 | 0.63171 | 0.18768 | 0.036621 | 0.28839 | 121.1243 | 0.10529 | 0.059509 | 121.6599 | 0.29297 | 121.5958 | 0.88806 | -121.5042 | -120.845 | 121.0602 | 0.6546 | 12.5793 | 0.64087
1587.0156 | 121.4401 | -0.12817 | 121.2341 | -0.0096891 | 0.0066629 | 0.06978 | 0.064803 | 0.0034755 | -0.0020892 | 0.00025205 | -0.010406 | 0.050302 | 0.0088866 | -0.00063659 | 0.001192 | 0.016718 | -0.0008652 | 12.0255 | 121.3852 | -0.1831 | 120.9778 | 0.15564 | -0.032043 | -0.018311 | 0.55389 | 0.64545 | 0.45319 | 0.5722 | 0.65002 | 0.55847 | 0.66376 | -0.054931 | 0.15106 | -0.25635 | 0.28381 | 0.10986 | 0.096131 | 0.16479 | 0.15106 | 0.58136 | -120.5887 | -120.6619 | 0.7782 | 0.79193 | 0.68665 | 0.21057 | 0.10529 | 0.33874 | 121.1609 | 0.19684 | 0.11902 | 121.5683 | 0.19226 | 121.5134 | 0.77362 | -121.4172 | -120.7809 | 121.106 | 0.70038 | 12.1536 | 0.68207
1588.7031 | 120.5063 | -46.0876 | 74.7528 | -0.0020601 | 0.0070901 | 0.07213 | 0.068221 | 0.0030483 | -0.0042254 | -0.003166 | -0.0043029 | 0.052652 | 0.0080322 | -0.004909 | 0.00033757 | 0.015436 | 0.000203 | -5.5435 | 74.8993 | -46.1563 | 74.5789 | -45.8084 | -46.2753 | -46.2799 | -0.21515 | 0.045776 | -0.22888 | -0.19684 | -0.11902 | -0.21057 | -0.064087 | -0.068665 | 0.14648 | -0.17395 | 0.27923 | -0.19226 | -0.18768 | -0.1236 | -0.11902 | 45.8588 | -74.707 | -74.9496 | 45.9686 | 46.0236 | 45.8771 | 0.16479 | 0.018311 | 0.3479 | 120.7352 | 0.10986 | 0.032044 | 121.0556 | 0.27466 | 120.9869 | 46.1334 | -120.9091 | -74.9817 | 120.6665 | 45.8908 | 40.5441 | 45.8725
1590.4688 | 121.1975 | -45.7718 | 75.4074 | -0.0096891 | 0.0040995 | 0.068498 | 0.068007 | 0.0024075 | -0.0012348 | -0.00060235 | -0.0012513 | 0.053506 | 0.0080322 | -0.012386 | 0.00076477 | 0.014795 | -0.0008652 | -5.397 | 75.5219 | -45.8359 | 75.2197 | -45.4834 | -45.9183 | -45.9457 | -0.12817 | 0.064087 | -0.19684 | -0.13275 | -0.027466 | -0.14648 | -0.004578 | -0.064086 | 0.11444 | -0.18768 | 0.28839 | -0.17395 | -0.14648 | -0.10986 | -0.082398 | 45.575 | -75.3433 | -75.5402 | 45.7443 | 45.7672 | 45.6253 | 0.19226 | 0.050354 | 0.35248 | 121.0556 | 0.16937 | 0.064087 | 121.3577 | 0.26093 | 121.2936 | 45.8359 | -121.2433 | -75.6042 | 120.9915 | 45.639 | 40.3748 | 45.6436
1592.1562 | 121.2433 | -45.6665 | 75.5493 | -0.0020601 | 0.0081583 | 0.071489 | 0.066512 | 0.0053983 | -0.0025166 | -0.004234 | -0.0012513 | 0.051156 | 0.0095276 | -0.0078998 | 0.00012397 | 0.016077 | 0.0008438 | -5.1819 | 75.6729 | -45.7581 | 75.3479 | -45.4056 | -45.8588 | -45.8633 | -0.15564 | 0.036621 | -0.18768 | -0.15564 | -0.07782 | -0.16937 | -0.018311 | -0.091553 | 0.1236 | -0.20142 | 0.26093 | -0.19684 | -0.19226 | -0.10529 | -0.10071 | 45.4788 | -75.5127 | -75.705 | 45.5887 | 45.6482 | 45.4971 | 0.16937 | 0.01831 | 0.35248 | 121.106 | 0.10986 | 0.032043 | 121.431 | 0.2243 | 121.3394 | 45.7031 | -121.3074 | -75.737 | 121.0144 | 45.5109 | 40.4846 | 45.5109
1593.9219 | 121.3669 | -45.4559 | 75.7233 | -0.024948 | 0.0038857 | 0.069353 | 0.064375 | 0.00069854 | -0.0012348 | -0.00017515 | -0.0043029 | 0.050729 | 0.007605 | -0.0010638 | -0.00051703 | 0.016504 | -0.000438 | -5.4108 | 75.8057 | -45.5521 | 75.5997 | -45.163 | -45.6482 | -45.6573 | -0.11444 | -0.064087 | -0.24261 | -0.10071 | 0 | -0.10986 | 0.013733 | -0.09613 | 0.082397 | -0.1236 | 0.29297 | -0.20142 | -0.19226 | -0.10529 | -0.09613 | 45.2133 | -75.7874 | -75.824 | 45.4559 | 45.4697 | 45.3461 | 0.25635 | 0.13275 | 0.3891 | 121.1517 | 0.24261 | 0.14191 | 121.3577 | 0.17853 | 121.2616 | 45.3918 | -121.2753 | -75.9659 | 121.0556 | 45.3552 | 40.0452 | 45.3415
1595.6094 | 121.3577 | -121.1014 | 0.20599 | 0.0055694 | 0.0051675 | 0.073198 | 0.065657 | -0.00015586 | -0.0031574 | 0.0028154 | -0.0012513 | 0.05137 | 0.0082458 | 0.006413 | -0.0026532 | 0.014795 | 0.0014846 | -37.381 | 0.23804 | -121.2341 | -0.013733 | -120.1675 | -120.9824 | -121.0876 | -1.3687 | -1.149 | -1.387 | -1.3504 | -1.236 | -1.3275 | -1.2268 | -0.13275 | 0.032043 | -0.21973 | 0.93384 | 0.013733 | 0.11902 | 0.14648 | 0.25177 | 119.7144 | -1.355 | -1.5564 | 119.8654 | 119.8746 | 119.7739 | 0.16022 | 0.059509 | 1.0666 | 121.2204 | 0.15106 | 0.036621 | 121.4722 | 0.23804 | 121.3394 | 119.9524 | -121.4401 | -1.593 | 121.0876 | 119.751 | 83.7204 | 119.7327
1597.3594 | 121.4539 | -121.0648 | 0.16022 | -0.0020601 | 0.0055947 | 0.074052 | 0.065871 | 0.0015529 | 0.0015424 | -0.0029524 | -0.0043029 | 0.05137 | 0.008673 | -0.007259 | 0.002901 | 0.017786 | -0.0006516 | -35.9848 | 0.21515 | -121.2616 | -0.027466 | -120.2179 | -121.0373 | -121.106 | -1.4236 | -1.3138 | -1.506 | -1.3916 | -1.3046 | -1.3824 | -1.2497 | -0.19684 | 0.054932 | -0.18768 | 0.84686 | -0.041199 | 0.027466 | 0.15564 | 0.22431 | 119.5587 | -1.474 | -1.5518 | 119.7601 | 119.8151 | 119.6823 | 0.25635 | 0.1236 | 1.0437 | 121.2341 | 0.20142 | 0.11444 | 121.4767 | 0.19226 | 121.2799 | 119.751 | -121.4218 | -1.6663 | 121.0373 | 119.6732 | 85.08 | 119.6411
1599.0625 | 121.4859 | -121.0831 | 0.17853 | -0.0020601 | 0.0038857 | 0.072557 | 0.062666 | 0.0026211 | -0.0025166 | -0.00081595 | -0.0012513 | 0.047952 | 0.0050414 | -0.0017048 | -0.0020122 | 0.01565 | 0.0025528 | -34.964 | 0.23346 | -121.2845 | 0.041199 | -120.1492 | -120.9732 | -121.0831 | -1.3504 | -1.2497 | -1.442 | -1.3641 | -1.2268 | -1.2955 | -1.2177 | -0.20142 | 0.054931 | -0.13733 | 0.93384 | 0 | 0.10986 | 0.20142 | 0.31128 | 119.6411 | -1.4282 | -1.5427 | 119.8563 | 119.8654 | 119.7876 | 0.2243 | 0.14648 | 1.1353 | 121.3257 | 0.21515 | 0.07782 | 121.5179 | 0.19226 | 121.3165 | 119.8334 | -121.463 | -1.6205 | 121.1243 | 119.7189 | 86.1191 | 119.7327
1600.75 | 121.376 | -121.1334 | 0.23346 | -0.0020601 | 0.0075173 | 0.072771 | 0.067366 | 0.0032619 | 0.0013288 | 0.00089285 | -0.0043029 | 0.05372 | 0.0071776 | -0.008327 | 0.001192 | 0.014155 | -0.0027878 | -34.6298 | 0.25635 | -121.3211 | -0.10986 | -120.3873 | -121.1792 | -121.2616 | -1.5701 | -1.2817 | -1.5518 | -1.5198 | -1.4694 | -1.5564 | -1.3779 | -0.18768 | 0.022889 | -0.34332 | 0.74615 | -0.12817 | -0.045776 | 0.059509 | 0.14191 | 119.5816 | -1.5152 | -1.7532 | 119.664 | 119.7556 | 119.577 | 0.17395 | -0.004577 | 0.93384 | 121.2112 | 0.082398 | 0.032044 | 121.5775 | 0.27008 | 121.3898 | 119.8517 | -121.5546 | -1.7853 | 121.0236 | 119.6136 | 86.5036 | 119.5633
1602.5 | 121.5225 | -121.17 | 0.18768 | -0.0096891 | 0.0038857 | 0.073198 | 0.064162 | -0.00079686 | -0.001662 | 0.0013202 | 0.0018005 | 0.050088 | 0.0080322 | -0.0040546 | 0.00055117 | 0.014368 | -0.000438 | -34.8358 | 0.21057 | -121.3028 | -0.009155 | -120.2408 | -121.0464 | -121.1243 | -1.4328 | -1.2817 | -1.4786 | -1.3412 | -1.2497 | -1.3092 | -1.2222 | -0.13275 | 0.022888 | -0.19684 | 0.92926 | 0.045776 | 0.1236 | 0.17853 | 0.25635 | 119.6915 | -1.4694 | -1.5289 | 119.9203 | 119.9478 | 119.8608 | 0.25635 | 0.16937 | 1.062 | 121.2936 | 0.22888 | 0.13733 | 121.5134 | 0.19684 | 121.3806 | 119.8883 | -121.4905 | -1.6663 | 121.1609 | 119.8288 | 86.3342 | 119.7372
1604.25 | 121.4355 | -121.1746 | 0.19226 | -0.0020601 | 0.0036721 | 0.071916 | 0.065871 | 0.00069854 | -0.0020892 | 0.00067925 | -0.0043029 | 0.052865 | 0.006964 | -0.0068316 | -8.9634e-05 | 0.015223 | -0.0010788 | -33.8608 | 0.23346 | -121.3531 | -0.073242 | -120.3369 | -121.1288 | -121.2204 | -1.4465 | -1.1993 | -1.4511 | -1.3916 | -1.3229 | -1.3916 | -1.2634 | -0.17853 | 0.041198 | -0.2655 | 0.83771 | -0.045776 | 0.045777 | 0.13275 | 0.2243 | 119.7235 | -1.3916 | -1.5839 | 119.8517 | 119.9112 | 119.783 | 0.18768 | 0.059509 | 1.0162 | 121.2799 | 0.12817 | 0.059509 | 121.5866 | 0.25177 | 121.4081 | 119.9753 | -121.5454 | -1.6434 | 121.1014 | 119.783 | 87.3138 | 119.7281
1606 | 121.4493 | -121.1838 | 0.20599 | -0.017319 | 0.0060221 | 0.069353 | 0.064375 | 0.0056119 | -0.0025166 | -0.0010298 | -0.0043029 | 0.050302 | 0.0065368 | -0.0025592 | 0.001833 | 0.015436 | 0.0042618 | -33.1192 | 0.23346 | -121.3394 | -0.064087 | -120.3369 | -121.1243 | -121.225 | -1.4282 | -1.2131 | -1.4465 | -1.3916 | -1.3138 | -1.4008 | -1.268 | -0.15564 | 0.027465 | -0.27008 | 0.84686 | -0.041199 | 0.059509 | 0.11444 | 0.21515 | 119.7372 | -1.4191 | -1.5976 | 119.87 | 119.9158 | 119.783 | 0.17853 | 0.045776 | 1.0025 | 121.2753 | 0.13275 | 0.054931 | 121.5729 | 0.23346 | 121.4172 | 119.9707 | -121.5454 | -1.6525 | 121.1197 | 119.7922 | 88.0646 | 119.7556
1607.6719 | 121.5317 | -121.1792 | 0.16937 | -0.0020601 | 0.0053811 | 0.07213 | 0.064162 | 0.0011257 | 4.7018e-05 | 0.00067925 | -0.010406 | 0.049661 | 0.0065368 | -0.0014912 | 0.0016194 | 0.017145 | 0.000203 | -32.3044 | 0.19684 | -121.3165 | 0.041199 | -120.2362 | -121.0785 | -121.1838 | -1.4557 | -1.3779 | -1.5472 | -1.4053 | -1.3412 | -1.4191 | -1.3046 | -0.13733 | 0.027465 | -0.12817 | 0.94299 | -0.004578 | 0.10071 | 0.13275 | 0.23804 | 119.632 | -1.5472 | -1.5747 | 119.838 | 119.8746 | 119.7601 | 0.24262 | 0.12817 | 1.0803 | 121.3577 | 0.20599 | 0.14191 | 121.5134 | 0.16937 | 121.376 | 119.8013 | -121.4859 | -1.7166 | 121.2204 | 119.7739 | 88.8748 | 119.7235
1609.4375 | 121.4813 | -121.2204 | 0.21057 | -0.017319 | 0.0030313 | 0.073839 | 0.067793 | 0.0013393 | -0.0055072 | -0.0012434 | -0.0012513 | 0.049661 | 0.0067504 | -0.006618 | -0.0013714 | 0.013941 | -0.0006516 | -32.7072 | 0.20599 | -121.3669 | -0.064087 | -120.3598 | -121.1517 | -121.2479 | -1.4374 | -1.1993 | -1.4648 | -1.3916 | -1.3138 | -1.4008 | -1.2772 | -0.14648 | -0.004577 | -0.27466 | 0.8606 | -0.027466 | 0.068665 | 0.11902 | 0.21515 | 119.7556 | -1.4099 | -1.6022 | 119.9066 | 119.9432 | 119.8196 | 0.18768 | 0.064087 | 1.0071 | 121.3028 | 0.15106 | 0.073242 | 121.5729 | 0.2655 | 121.4264 | 120.0211 | -121.5775 | -1.6754 | 121.1563 | 119.8288 | 88.5132 | 119.783
1611.1875 | 121.5591 | -121.2341 | 0.16022 | -0.0096891 | 0.0051675 | 0.073625 | 0.066084 | 5.774e-05 | -0.0018756 | 0.00025205 | -0.0012513 | 0.049234 | 0.005255 | 0.0051312 | 0.0037556 | 0.017145 | 0.003621 | -32.3868 | 0.19226 | -121.3486 | 0.013733 | -120.2911 | -121.1151 | -121.2204 | -1.4511 | -1.3733 | -1.5518 | -1.4053 | -1.3458 | -1.4374 | -1.2863 | -0.11444 | 0.032044 | -0.14648 | 0.94299 | 0.013733 | 0.11902 | 0.12817 | 0.23346 | 119.6823 | -1.5335 | -1.5656 | 119.8883 | 119.9478 | 119.7968 | 0.2655 | 0.11444 | 1.0574 | 121.3623 | 0.20599 | 0.14648 | 121.5408 | 0.17853 | 121.4264 | 119.8608 | -121.5088 | -1.712 | 121.2479 | 119.8288 | 88.8474 | 119.783
1612.9375 | 121.4584 | -121.2662 | 0.20599 | -0.0020601 | 0.0060221 | 0.072343 | 0.068007 | -0.0029331 | -0.0020892 | -0.00017515 | -0.0012513 | 0.052438 | 0.006964 | -0.00063659 | 0.0020466 | 0.016504 | -0.003215 | -32.0435 | 0.23346 | -121.4081 | -0.10986 | -120.4514 | -121.257 | -121.3211 | -1.6022 | -1.3275 | -1.5701 | -1.5244 | -1.4786 | -1.5701 | -1.3824 | -0.14191 | 0.027465 | -0.31586 | 0.81482 | -0.054932 | 0.009155 | 0.086975 | 0.15106 | 119.696 | -1.5335 | -1.7303 | 119.7876 | 119.8837 | 119.696 | 0.18768 | 0 | 0.95673 | 121.2982 | 0.091552 | 0.045776 | 121.6415 | 0.24261 | 121.4996 | 119.9387 | -121.6141 | -1.7761 | 121.1563 | 119.7418 | 89.2227 | 119.664
1614.625 | 121.4584 | -121.2433 | 0.21057 | -0.0096891 | 0.0055947 | 0.071703 | 0.067152 | 0.0026211 | -0.0018756 | -0.0016706 | -0.0012513 | 0.04902 | 0.0084594 | -0.0076862 | 0.00097837 | 0.013941 | -0.0012924 | -31.9748 | 0.2243 | -121.3943 | -0.073242 | -120.4468 | -121.257 | -121.3531 | -1.6205 | -1.3092 | -1.5518 | -1.5472 | -1.5015 | -1.5839 | -1.4191 | -0.15106 | 0.013733 | -0.28381 | 0.79651 | -0.10986 | -0.013733 | 0.041199 | 0.13733 | 119.6915 | -1.5198 | -1.7578 | 119.7418 | 119.8242 | 119.6594 | 0.13275 | -0.032043 | 0.94757 | 121.3211 | 0.050354 | 0.004578 | 121.6187 | 0.24262 | 121.4676 | 119.9341 | -121.6049 | -1.7624 | 121.17 | 119.696 | 89.2685 | 119.6228
1616.3594 | 121.5958 | -121.2341 | 0.16022 | -0.0020601 | 0.0017495 | 0.071062 | 0.063735 | 5.774e-05 | -0.0027302 | -0.00060235 | -0.0073547 | 0.049234 | 0.007605 | 0.00085881 | 0.00097837 | 0.015436 | 0.0014846 | -31.7368 | 0.19226 | -121.3852 | -0.027466 | -120.3644 | -121.1426 | -121.2296 | -1.5106 | -1.3687 | -1.5747 | -1.4282 | -1.3229 | -1.4008 | -1.3046 | -0.15106 | 0.032044 | -0.18768 | 0.86975 | 0.004578 | 0.091553 | 0.15564 | 0.24262 | 119.6594 | -1.5289 | -1.5884 | 119.9112 | 119.9295 | 119.8334 | 0.27008 | 0.17395 | 1.0208 | 121.3577 | 0.25177 | 0.14648 | 121.5775 | 0.20599 | 121.4264 | 119.8654 | -121.5454 | -1.7349 | 121.2067 | 119.8059 | 89.4974 | 119.7235
1618.1094 | 121.5637 | -121.2524 | 0.17853 | -0.0096891 | 0.0036721 | 0.074693 | 0.064375 | 0.00091214 | -0.00059378 | -0.0035932 | -0.0012513 | 0.050729 | 0.0073914 | -0.0034138 | -0.0011578 | 0.015223 | 0.0016982 | -32.0435 | 0.18768 | -121.3852 | -0.041199 | -120.4193 | -121.2067 | -121.2936 | -1.6479 | -1.4374 | -1.6571 | -1.5884 | -1.4877 | -1.5839 | -1.442 | -0.13275 | 0.009155 | -0.21973 | 0.83313 | -0.041199 | 0.045776 | 0.091553 | 0.17853 | 119.5953 | -1.6159 | -1.767 | 119.7647 | 119.8105 | 119.6686 | 0.21515 | 0.073242 | 0.96588 | 121.344 | 0.16937 | 0.068664 | 121.5729 | 0.21973 | 121.4401 | 119.8151 | -121.5637 | -1.8356 | 121.2112 | 119.664 | 89.209 | 119.6045
1619.8594 | 121.5591 | -121.2753 | 0.19226 | 0.020828 | 0.0049539 | 0.071062 | 0.066725 | 0.00069854 | -0.0023028 | -0.00017515 | -0.0012513 | 0.051584 | 0.0080322 | 4.214e-06 | 0.0037556 | 0.016718 | -0.0008652 | -31.2927 | 0.21515 | -121.4355 | -0.064087 | -120.4651 | -121.2662 | -121.344 | -1.7166 | -1.5152 | -1.7395 | -1.6617 | -1.5839 | -1.68 | -1.5198 | -0.16022 | 0.022888 | -0.25635 | 0.81024 | -0.068664 | 0.009156 | 0.091553 | 0.16937 | 119.5358 | -1.7075 | -1.8539 | 119.6915 | 119.7556 | 119.5953 | 0.21973 | 0.059509 | 0.97046 | 121.3715 | 0.15564 | 0.07782 | 121.6507 | 0.2243 | 121.4905 | 119.7601 | -121.6278 | -1.9318 | 121.2112 | 119.6136 | 89.9826 | 119.5587
1621.5469 | 121.5179 | -121.2936 | 0.20142 | 0.0055694 | 0.0073037 | 0.070848 | 0.06758 | 0.0058255 | -0.0025166 | -0.002525 | -0.0012513 | 0.053934 | 0.0067504 | -0.004909 | 0.002901 | 0.014795 | -0.0023606 | -30.8762 | 0.22888 | -121.4722 | -0.10986 | -120.5292 | -121.3028 | -121.3898 | -1.8585 | -1.5701 | -1.8311 | -1.7944 | -1.7349 | -1.8219 | -1.6434 | -0.17853 | 0.027466 | -0.31128 | 0.76447 | -0.096131 | -0.009155 | 0.082397 | 0.16937 | 119.4626 | -1.7715 | -1.9959 | 119.5587 | 119.6503 | 119.4717 | 0.18768 | 0.009156 | 0.94299 | 121.3623 | 0.096131 | 0.036621 | 121.701 | 0.26093 | 121.5225 | 119.7235 | -121.6736 | -2.0325 | 121.1838 | 119.4992 | 90.4175 | 119.4351
1623.3125 | 121.5683 | -121.3211 | 0.18768 | -0.0096891 | 0.0047403 | 0.071703 | 0.063948 | 0.0013393 | -0.0025166 | -0.00017515 | -0.0073547 | 0.049661 | 0.0061096 | -0.011959 | 0.00097837 | 0.015223 | -0.0023606 | -30.6198 | 0.21057 | -121.4539 | -0.032043 | -120.4514 | -121.2204 | -121.3211 | -1.6891 | -1.506 | -1.7303 | -1.6571 | -1.5701 | -1.6525 | -1.5198 | -0.13275 | 0.022888 | -0.21973 | 0.86975 | 0 | 0.10071 | 0.13275 | 0.23346 | 119.5908 | -1.6937 | -1.8448 | 119.751 | 119.8013 | 119.6686 | 0.21057 | 0.07782 | 1.0025 | 121.4218 | 0.16022 | 0.073243 | 121.6644 | 0.2243 | 121.5317 | 119.8151 | -121.6415 | -1.918 | 121.2891 | 119.664 | 90.7013 | 119.632
1625.0781 | 121.6553 | -121.2845 | 0.16479 | -0.0020601 | 0.0058083 | 0.071916 | 0.065016 | 5.774e-05 | -0.0014484 | -0.00038875 | -0.0012513 | 0.04902 | 0.0071776 | -0.0076862 | 0.0031146 | 0.018213 | 0.0006302 | -30.8212 | 0.19684 | -121.4218 | 0.009155 | -120.3873 | -121.1975 | -121.2799 | -1.7532 | -1.6663 | -1.8494 | -1.7349 | -1.6434 | -1.7441 | -1.6159 | -0.13733 | 0.032043 | -0.15564 | 0.89722 | 0.004578 | 0.086975 | 0.14191 | 0.2243 | 119.4351 | -1.8311 | -1.8997 | 119.6411 | 119.6686 | 119.5404 | 0.23346 | 0.10528 | 1.0345 | 121.431 | 0.20599 | 0.11444 | 121.6187 | 0.1831 | 121.4813 | 119.6182 | -121.5866 | -2.0142 | 121.2936 | 119.5496 | 90.4633 | 119.5312
1626.8125 | 121.582 | -121.3394 | 0.20599 | -0.0020601 | 0.0055947 | 0.069139 | 0.063948 | -0.00079686 | -0.00059378 | 0.00046565 | -0.0043029 | 0.050302 | 0.0044006 | -0.0032 | -0.0026532 | 0.013941 | 0.0008438 | -30.4962 | 0.17853 | -121.4813 | 0.004578 | -120.4239 | -121.1929 | -121.2891 | -1.6067 | -1.4374 | -1.6754 | -1.6022 | -1.506 | -1.593 | -1.474 | -0.14191 | -0.027466 | -0.20142 | 0.91553 | 0.050355 | 0.14648 | 0.19226 | 0.28839 | 119.664 | -1.6434 | -1.8082 | 119.8334 | 119.8654 | 119.7464 | 0.20142 | 0.082397 | 1.0574 | 121.4859 | 0.16937 | 0.073242 | 121.6599 | 0.23804 | 121.5179 | 119.902 | -121.6873 | -1.8814 | 121.344 | 119.7372 | 90.8432 | 119.7327
1628.5 | 121.5454 | -121.3165 | 0.20142 | -0.0020601 | 0.0064493 | 0.072343 | 0.066298 | 0.0049709 | -0.0018756 | 0.0017474 | -0.0043029 | 0.05372 | 0.0080322 | -0.0093952 | 0.00033757 | 0.015864 | -0.0006516 | -30.3543 | 0.22888 | -121.5179 | -0.050354 | -120.488 | -121.2891 | -121.3898 | -1.6663 | -1.4465 | -1.6891 | -1.6571 | -1.5839 | -1.6983 | -1.5518 | -0.20142 | 0.027466 | -0.25177 | 0.82855 | -0.073243 | 0.027466 | 0.12817 | 0.22888 | 119.6274 | -1.6479 | -1.8585 | 119.7327 | 119.7647 | 119.6182 | 0.13733 | -0.009155 | 1.03 | 121.4676 | 0.10529 | 0.032044 | 121.7468 | 0.24262 | 121.5454 | 119.87 | -121.7194 | -1.8906 | 121.2662 | 119.6594 | 90.9622 | 119.6503
1630.25 | 121.6187 | -121.3303 | 0.19684 | -0.0096891 | 0.0070901 | 0.071489 | 0.064589 | 0.00069854 | -0.003371 | -0.0018842 | -0.0012513 | 0.051156 | 0.0088866 | -0.008968 | -0.00030343 | 0.013727 | -0.0023606 | -29.5761 | 0.23346 | -121.5042 | -0.054932 | -120.4834 | -121.2799 | -121.3669 | -1.6663 | -1.4694 | -1.6983 | -1.6296 | -1.5472 | -1.6479 | -1.506 | -0.17395 | 0.036621 | -0.25177 | 0.84686 | -0.036621 | 0.050354 | 0.13733 | 0.2243 | 119.632 | -1.6663 | -1.8265 | 119.783 | 119.8242 | 119.6823 | 0.19226 | 0.050354 | 1.0208 | 121.4493 | 0.15106 | 0.068664 | 121.7377 | 0.22888 | 121.5637 | 119.8608 | -121.701 | -1.8951 | 121.2753 | 119.7006 | 91.7541 | 119.664
1631.9375 | 121.6187 | -121.344 | 0.18768 | -0.0096891 | 0.0053811 | 0.071703 | 0.066725 | 0.0032619 | -0.0029438 | -0.00060235 | -0.0043029 | 0.05137 | 0.0097412 | -0.0057636 | -0.00051703 | 0.016932 | 0.0014846 | -28.6331 | 0.21515 | -121.5088 | -0.064087 | -120.5109 | -121.2799 | -121.3669 | -1.6159 | -1.4236 | -1.6479 | -1.5793 | -1.4877 | -1.5884 | -1.4465 | -0.16479 | 0.027466 | -0.25177 | 0.83313 | -0.022888 | 0.064087 | 0.14191 | 0.22888 | 119.696 | -1.6113 | -1.767 | 119.8563 | 119.8975 | 119.7556 | 0.20142 | 0.059509 | 0.99792 | 121.4447 | 0.16022 | 0.068664 | 121.7239 | 0.2243 | 121.5591 | 119.9203 | -121.6965 | -1.8356 | 121.2799 | 119.7647 | 92.7109 | 119.7281
1633.6719 | 121.582 | -121.3623 | 0.19684 | 0.013199 | 0.0064493 | 0.072557 | 0.066084 | -0.0010105 | -0.001662 | 0.0015338 | -0.0012513 | 0.053293 | 0.0050414 | -0.0032 | -0.00030343 | 0.015223 | -0.0006516 | -27.8961 | 0.23346 | -121.55 | -0.11444 | -120.6162 | -121.3989 | -121.4584 | -1.7807 | -1.4877 | -1.7441 | -1.7075 | -1.6663 | -1.7349 | -1.561 | -0.18768 | 0.036621 | -0.31128 | 0.74616 | -0.09613 | -0.036621 | 0.091553 | 0.15106 | 119.6182 | -1.6846 | -1.9043 | 119.696 | 119.8013 | 119.6274 | 0.18311 | 0.009156 | 0.93384 | 121.4355 | 0.07782 | 0.036622 | 121.7834 | 0.25635 | 121.5958 | 119.8746 | -121.7468 | -1.9409 | 121.2479 | 119.6548 | 93.4662 | 119.5816
1635.4375 | 121.6278 | -121.3623 | 0.21515 | -0.017319 | 0.0051675 | 0.071703 | 0.06758 | -0.0018649 | -0.0029438 | 0.00067925 | -0.0073547 | 0.051797 | 0.005896 | -0.0098224 | -8.9634e-05 | 0.013086 | 0.0016982 | -27.919 | 0.20599 | -121.5591 | -0.09613 | -120.5704 | -121.3348 | -121.4127 | -1.68 | -1.3962 | -1.6479 | -1.6022 | -1.5015 | -1.5839 | -1.4557 | -0.19684 | -0.009155 | -0.31128 | 0.79193 | -0.050354 | 0.027466 | 0.14648 | 0.2243 | 119.7144 | -1.6113 | -1.8173 | 119.8608 | 119.9066 | 119.7784 | 0.19226 | 0.064087 | 0.98877 | 121.463 | 0.14648 | 0.045776 | 121.7651 | 0.25177 | 121.5683 | 119.9661 | -121.7743 | -1.8631 | 121.2662 | 119.7601 | 93.4433 | 119.6823
1637.1875 | 121.669 | -121.3394 | 0.20599 | -0.0020601 | 0.0034585 | 0.071916 | 0.065016 | -0.00058326 | -0.00059378 | -0.0012434 | -0.010406 | 0.047525 | 0.005255 | -0.0068316 | 0.0020466 | 0.016291 | 0.0023392 | -25.5569 | 0.19684 | -121.4584 | 0.022888 | -120.401 | -121.2341 | -121.3303 | -1.68 | -1.593 | -1.7395 | -1.6479 | -1.5701 | -1.6708 | -1.5472 | -0.11902 | -0.009156 | -0.18311 | 0.93842 | 0.009156 | 0.10529 | 0.12817 | 0.2243 | 119.5999 | -1.799 | -1.8539 | 119.7693 | 119.7922 | 119.6686 | 0.19226 | 0.068665 | 1.0574 | 121.4813 | 0.16937 | 0.091553 | 121.6553 | 0.14648 | 121.5363 | 119.7464 | -121.6644 | -1.9455 | 121.3623 | 119.6915 | 95.7825 | 119.6594
1638.9375 | 121.6049 | -121.3577 | 0.22888 | -0.0020601 | 0.0075173 | 0.072343 | 0.067152 | 0.0017667 | -0.0042254 | -0.00081595 | 0.0018005 | 0.052438 | 0.005896 | -0.0012774 | 0.0014056 | 0.016504 | -0.001506 | -25.0351 | 0.25177 | -121.5271 | -0.022888 | -120.4834 | -121.3074 | -121.3943 | -1.7578 | -1.5335 | -1.7807 | -1.7441 | -1.6663 | -1.767 | -1.6113 | -0.16937 | 0.022888 | -0.25177 | 0.87433 | -0.036621 | 0.050354 | 0.13275 | 0.21973 | 119.577 | -1.7624 | -1.973 | 119.6915 | 119.7464 | 119.5908 | 0.16937 | 0.013733 | 1.0437 | 121.5042 | 0.11444 | 0.036621 | 121.7789 | 0.24719 | 121.6095 | 119.8242 | -121.756 | -2.0096 | 121.3348 | 119.6136 | 96.3226 | 119.5999
1640.625 | 121.6965 | -121.3577 | 0.20599 | 0.0055694 | 0.0043131 | 0.071703 | 0.063094 | 0.0024075 | -0.0023028 | -0.0016706 | 0.0018005 | 0.051156 | 0.007605 | -0.0019184 | -0.0024396 | 0.016077 | -0.0006516 | -24.3622 | 0.21057 | -121.4813 | 0.045776 | -120.3918 | -121.2021 | -121.3257 | -1.6754 | -1.5747 | -1.7761 | -1.6663 | -1.5564 | -1.6342 | -1.5381 | -0.1236 | 0.004577 | -0.16022 | 0.96588 | 0.032043 | 0.15564 | 0.15564 | 0.27924 | 119.5816 | -1.7807 | -1.8723 | 119.8013 | 119.8196 | 119.7235 | 0.23804 | 0.14191 | 1.0895 | 121.5271 | 0.21973 | 0.10986 | 121.6919 | 0.20142 | 121.5683 | 119.783 | -121.6873 | -1.9821 | 121.4035 | 119.6915 | 96.9955 | 119.6823
1642.375 | 121.6232 | -121.3669 | 0.21973 | 0.0055694 | 0.0055947 | 0.073412 | 0.066725 | 0.0015529 | -0.0031574 | -0.00038875 | -0.0043029 | 0.051797 | 0.010168 | -0.0093952 | 0.001833 | 0.014795 | -0.0012924 | -24.6506 | 0.23346 | -121.5637 | -0.086975 | -120.5704 | -121.376 | -121.4584 | -1.8906 | -1.6159 | -1.8723 | -1.8494 | -1.7853 | -1.8677 | -1.7029 | -0.19684 | 0.013732 | -0.3067 | 0.79651 | -0.091553 | -0.009156 | 0.10529 | 0.18768 | 119.4946 | -1.8356 | -2.0691 | 119.5816 | 119.664 | 119.4992 | 0.16937 | 0.004577 | 0.99335 | 121.4767 | 0.086975 | 0.022888 | 121.7972 | 0.25635 | 121.6003 | 119.751 | -121.7834 | -2.092 | 121.2799 | 119.5175 | 96.7163 | 119.4763
1644.125 | 121.7056 | -121.3623 | 0.21057 | -0.017319 | 0.0030313 | 0.071275 | 0.063094 | -0.00015586 | -0.0040118 | 3.8448e-05 | -0.0012513 | 0.050516 | 0.0073914 | -0.0046954 | -8.9634e-05 | 0.016504 | -0.0027878 | -24.8337 | 0.20599 | -121.5225 | -0.018311 | -120.4834 | -121.3211 | -121.3898 | -1.8723 | -1.68 | -1.8906 | -1.8173 | -1.7029 | -1.7944 | -1.68 | -0.16022 | -0.004577 | -0.22888 | 0.87891 | -0.027466 | 0.041199 | 0.13275 | 0.20142 | 119.4717 | -1.8906 | -2.0279 | 119.6594 | 119.6823 | 119.5679 | 0.21057 | 0.09613 | 1.0391 | 121.5042 | 0.18768 | 0.073242 | 121.7285 | 0.21057 | 121.5683 | 119.6823 | -121.7331 | -2.1011 | 121.344 | 119.545 | 96.5286 | 119.4901
1645.8906 | 121.6644 | -121.3943 | 0.2243 | -0.0096891 | 0.0073037 | 0.070848 | 0.064375 | 0.0015529 | -0.003371 | -0.0012434 | -0.0012513 | 0.052438 | 0.0065368 | -0.0126 | -0.0011578 | 0.014795 | 0.0025528 | -24.0555 | 0.23346 | -121.5683 | -0.032043 | -120.5154 | -121.312 | -121.4172 | -1.4832 | -1.2772 | -1.506 | -1.442 | -1.3687 | -1.4511 | -1.3046 | -0.17395 | 0.009155 | -0.25635 | 0.87891 | -0.022888 | 0.082397 | 0.15106 | 0.25635 | 119.8883 | -1.5015 | -1.6663 | 120.0256 | 120.0897 | 119.9432 | 0.20142 | 0.054931 | 1.0529 | 121.5363 | 0.13733 | 0.064086 | 121.8018 | 0.22888 | 121.6278 | 120.1172 | -121.7926 | -1.7303 | 121.3623 | 119.9524 | 97.3389 | 119.9112
1647.5625 | 121.7468 | -121.3531 | 0.16937 | -0.0020601 | 0.0055947 | 0.071703 | 0.064162 | -0.00015586 | -0.001662 | -0.0018842 | -0.010406 | 0.050088 | 0.006964 | 0.0027814 | 0.0033282 | 0.015864 | 0.0008438 | -23.6618 | 0.19226 | -121.4905 | 0.059509 | -120.433 | -121.2845 | -121.3715 | -1.5244 | -1.4603 | -1.6067 | -1.474 | -1.3962 | -1.4877 | -1.3824 | -0.13733 | 0.022888 | -0.10986 | 0.92011 | -0.018311 | 0.068664 | 0.11902 | 0.20599 | 119.7464 | -1.6296 | -1.6434 | 119.957 | 119.9707 | 119.8654 | 0.2243 | 0.11902 | 1.0574 | 121.55 | 0.21057 | 0.13275 | 121.6827 | 0.14648 | 121.5454 | 119.8929 | -121.6599 | -1.7761 | 121.4127 | 119.8791 | 97.6913 | 119.8288
1649.3125 | 121.701 | -121.3943 | 0.20142 | -0.0020601 | 0.0068765 | 0.071489 | 0.065657 | 0.0013393 | -0.0023028 | -0.0027386 | -0.0043029 | 0.047525 | 0.006964 | -0.0051226 | -0.00051703 | 0.016291 | 0.000203 | -23.5657 | 0.19684 | -121.5317 | 0 | -120.488 | -121.3165 | -121.4081 | -1.5747 | -1.4328 | -1.6159 | -1.5381 | -1.442 | -1.5472 | -1.4053 | -0.13733 | -0.004578 | -0.20142 | 0.90637 | -0.013733 | 0.07782 | 0.1236 | 0.21515 | 119.7784 | -1.6342 | -1.7395 | 119.9524 | 119.989 | 119.8471 | 0.21057 | 0.068665 | 1.0437 | 121.5317 | 0.17395 | 0.07782 | 121.7285 | 0.18311 | 121.5912 | 119.9615 | -121.7331 | -1.8173 | 121.3943 | 119.8563 | 97.8287 | 119.8196
1651 | 121.7194 | -121.463 | 0.16937 | -0.0096891 | 0.0036721 | 0.071916 | 0.064803 | -0.0016513 | -0.0014484 | -0.0016706 | -0.0073547 | 0.051156 | 0.0063232 | -0.0036274 | 0.00012397 | 0.016077 | 0.003621 | -22.316 | 0.16937 | -121.5866 | -0.041199 | -120.5109 | -121.3348 | -121.4081 | -1.5976 | -1.4511 | -1.6342 | -1.5381 | -1.4465 | -1.5289 | -1.3962 | -0.1236 | 0 | -0.21057 | 0.95215 | 0.054932 | 0.12817 | 0.17853 | 0.25177 | 119.8288 | -1.6205 | -1.7075 | 120.0165 | 120.0668 | 119.9341 | 0.23804 | 0.10528 | 1.0757 | 121.5454 | 0.18768 | 0.09613 | 121.756 | 0.1831 | 121.6324 | 120.0119 | -121.756 | -1.8036 | 121.4218 | 119.9249 | 99.147 | 119.8654
1652.7344 | 121.7514 | -121.4447 | 0.16479 | -0.0020601 | 0.0038857 | 0.072343 | 0.06523 | 0.0017667 | -0.0044392 | -0.0020978 | -0.0043029 | 0.04902 | 0.0071776 | 0.00085881 | -0.0017986 | 0.015009 | 0.0008438 | -21.9452 | 0.18768 | -121.5912 | -0.045776 | -120.5154 | -121.3531 | -121.4355 | -1.6159 | -1.4694 | -1.6754 | -1.5747 | -1.474 | -1.5472 | -1.4282 | -0.14648 | 0.022888 | -0.21057 | 0.92926 | 0.009155 | 0.091553 | 0.15564 | 0.23804 | 119.7693 | -1.6342 | -1.7395 | 119.9707 | 120.0165 | 119.8975 | 0.24719 | 0.12817 | 1.0757 | 121.5454 | 0.20142 | 0.10071 | 121.7789 | 0.20599 | 121.6324 | 119.9753 | -121.756 | -1.8402 | 121.3989 | 119.87 | 99.4995 | 119.8288
1654.5 | 121.6965 | -121.4722 | 0.16479 | -0.0096891 | 0.0077311 | 0.071916 | 0.066298 | 0.00048494 | -0.0027302 | -0.0023114 | -0.0043029 | 0.051156 | 0.0078186 | -0.014736 | -0.00073063 | 0.014155 | -0.0040696 | -21.7255 | 0.19684 | -121.6415 | -0.059509 | -120.5383 | -121.3852 | -121.4813 | -1.6113 | -1.4191 | -1.6434 | -1.5976 | -1.5015 | -1.6067 | -1.4557 | -0.16937 | 0.032043 | -0.2243 | 0.93384 | -0.009155 | 0.086975 | 0.16022 | 0.25635 | 119.8288 | -1.5839 | -1.7624 | 119.9707 | 120.0165 | 119.8654 | 0.18768 | 0.036622 | 1.1032 | 121.582 | 0.14191 | 0.045777 | 121.8384 | 0.2243 | 121.669 | 120.0531 | -121.8063 | -1.8082 | 121.4127 | 119.8746 | 99.7467 | 119.8608
1656.2656 | 121.701 | -121.4767 | 0.19226 | -0.017319 | 0.0051675 | 0.072557 | 0.065016 | -0.0018649 | -0.0029438 | 3.8448e-05 | -0.0073547 | 0.054361 | 0.0067504 | -0.0087542 | -0.001585 | 0.012232 | 0.001271 | -22.6181 | 0.19684 | -121.637 | -0.07782 | -120.5429 | -121.3989 | -121.4951 | -1.6754 | -1.442 | -1.6846 | -1.6388 | -1.5289 | -1.6342 | -1.4923 | -0.16022 | 0.004577 | -0.27008 | 0.93384 | -0.01831 | 0.07782 | 0.14191 | 0.23804 | 119.7922 | -1.6342 | -1.8311 | 119.9478 | 119.9844 | 119.8425 | 0.19226 | 0.050354 | 1.0941 | 121.5591 | 0.15564 | 0.045776 | 121.8338 | 0.24261 | 121.6736 | 120.0348 | -121.8292 | -1.8768 | 121.3989 | 119.838 | 98.8586 | 119.8013
1658.0312 | 121.7972 | -121.4447 | 0.13733 | -0.0020601 | 0.0015359 | 0.072984 | 0.064375 | -0.0027195 | -0.0018756 | -0.00060235 | 0.0018005 | 0.04902 | 0.005896 | -0.0085406 | 0.00076477 | 0.015223 | 0.0042618 | -22.2565 | 0.16937 | -121.6278 | 0.022888 | -120.4285 | -121.312 | -121.4172 | -1.6342 | -1.5472 | -1.7258 | -1.6296 | -1.4923 | -1.5884 | -1.4877 | -0.18311 | 0.032044 | -0.11444 | 1.0162 | 0.027466 | 0.13275 | 0.21057 | 0.31586 | 119.7189 | -1.6846 | -1.767 | 119.9524 | 119.957 | 119.8563 | 0.23804 | 0.13733 | 1.1993 | 121.6507 | 0.23346 | 0.09613 | 121.7972 | 0.17853 | 121.6141 | 119.8975 | -121.7651 | -1.8631 | 121.4676 | 119.8151 | 99.1882 | 119.8105
1659.7188 | 121.7377 | -121.5134 | 0.15564 | -0.017319 | 0.0019631 | 0.072343 | 0.063094 | -0.0025059 | -0.0052936 | 0.00089285 | -0.0073547 | 0.048166 | 0.0084594 | -0.0017048 | 0.0014056 | 0.014368 | 0.000203 | -22.2473 | 0.16479 | -121.637 | -0.054932 | -120.5429 | -121.4035 | -121.4996 | -2.2659 | -2.0691 | -2.2568 | -2.2156 | -2.1011 | -2.1881 | -2.0462 | -0.1236 | 0.009155 | -0.21057 | 0.97046 | 0.013733 | 0.10986 | 0.13733 | 0.23346 | 119.2566 | -2.2247 | -2.3712 | 119.4122 | 119.4672 | 119.3253 | 0.21057 | 0.068665 | 1.0941 | 121.582 | 0.15564 | 0.041199 | 121.8018 | 0.18768 | 121.6782 | 119.4443 | -121.7926 | -2.4124 | 121.4584 | 119.2978 | 99.2661 | 119.2474
1661.4688 | 121.8109 | -121.4676 | 0.15564 | -0.0020601 | 0.0062357 | 0.072984 | 0.067366 | 0.0017667 | -0.00508 | -0.0023114 | -0.0043029 | 0.052865 | 0.0029052 | -0.0017048 | 0.0014056 | 0.015864 | -0.0044968 | -22.229 | 0.17395 | -121.637 | 0.009155 | -120.4971 | -121.3852 | -121.4767 | -2.2385 | -2.1423 | -2.3392 | -2.211 | -2.1286 | -2.211 | -2.0691 | -0.16937 | 0.01831 | -0.14649 | 0.97046 | -0.009156 | 0.082397 | 0.16022 | 0.25177 | 119.1284 | -2.298 | -2.3666 | 119.339 | 119.3985 | 119.2566 | 0.27008 | 0.12817 | 1.1398 | 121.6461 | 0.21057 | 0.12817 | 121.8109 | 0.19684 | 121.6415 | 119.3253 | -121.7926 | -2.4948 | 121.4767 | 119.2566 | 99.2386 | 119.2291
1663.2031 | 121.7697 | -121.4905 | 0.16937 | 0.0055694 | 0.0040995 | 0.071916 | 0.063735 | 0.00069854 | -0.0027302 | 0.0013202 | -0.0043029 | 0.049661 | 0.0067504 | -0.004909 | -0.0013714 | 0.013086 | 0.00298 | -22.7371 | 0.17395 | -121.6644 | 0.022888 | -120.4788 | -121.3669 | -121.4584 | -2.1698 | -2.0645 | -2.2614 | -2.1881 | -2.0416 | -2.1423 | -2.0325 | -0.17395 | 0.004577 | -0.14649 | 1.0117 | 0.032044 | 0.1236 | 0.20599 | 0.29755 | 119.2291 | -2.2339 | -2.3575 | 119.4489 | 119.458 | 119.3481 | 0.22888 | 0.11902 | 1.1856 | 121.6873 | 0.21973 | 0.073243 | 121.8384 | 0.19684 | 121.6644 | 119.426 | -121.8338 | -2.4307 | 121.5134 | 119.3024 | 98.7534 | 119.3207
1664.9531 | 121.8292 | -121.4813 | 0.14191 | 0.0055694 | 0.0049539 | 0.071489 | 0.06523 | 0.0021939 | -0.0037982 | 0.00067925 | -0.0012513 | 0.04902 | 0.0063232 | -0.0017048 | -0.00051703 | 0.012873 | 0.00298 | -23.0347 | 0.15106 | -121.6553 | 0.027466 | -120.4742 | -121.3303 | -121.4401 | -2.1881 | -2.0874 | -2.2659 | -2.1744 | -2.0462 | -2.1378 | -2.037 | -0.17395 | 0.009155 | -0.11444 | 1.0071 | 0.041198 | 0.15106 | 0.21515 | 0.32501 | 119.2154 | -2.2293 | -2.3163 | 119.4351 | 119.4443 | 119.3436 | 0.22888 | 0.12817 | 1.181 | 121.6827 | 0.21973 | 0.091553 | 121.8063 | 0.17853 | 121.6324 | 119.3939 | -121.7972 | -2.4078 | 121.5088 | 119.3069 | 98.4467 | 119.2932
1666.625 | 121.6919 | -97.8378 | 23.8266 | -0.024948 | 0.0058083 | 0.070634 | 0.065871 | 0.0051845 | -0.0035846 | -0.00017515 | -0.0012513 | 0.051797 | 0.0099548 | -0.007259 | 0.0014056 | 0.012446 | 0.0014846 | -16.7999 | 23.8495 | -97.9706 | 23.7259 | -97.0779 | -97.8058 | -97.8653 | -1.0849 | -0.82855 | -1.0803 | -1.0483 | -0.91095 | -1.0208 | -0.88348 | -0.13275 | 0.022888 | -0.10071 | 0.75989 | -0.027465 | 0.032044 | 0.10529 | 0.16479 | 96.7575 | -24.6552 | -24.8749 | 96.9269 | 96.9543 | 96.817 | 0.19684 | 0.059509 | 0.89264 | 121.6965 | 0.16937 | 0.032043 | 121.8201 | 0.25177 | 121.6873 | 97.0093 | -121.7972 | -24.9069 | 121.5637 | 96.7896 | 81.0379 | 96.7529
1668.375 | 121.7834 | -97.7737 | 23.8083 | -0.0096891 | 0.0043131 | 0.072557 | 0.064589 | -0.0076329 | -0.0020892 | 0.0013202 | 0.0018005 | 0.050516 | 0.0054688 | -0.0064044 | -0.0011578 | 0.012018 | -0.0012924 | -17.0151 | 23.822 | -97.9156 | 23.8312 | -96.9452 | -97.7005 | -97.7875 | -0.97504 | -0.89264 | -1.0803 | -0.97504 | -0.83771 | -0.9201 | -0.82398 | -0.14191 | 0.013732 | 0.022888 | 0.82855 | -0.013733 | 0.073243 | 0.12817 | 0.21515 | 96.6934 | -24.7009 | -24.7833 | 96.936 | 96.9498 | 96.8536 | 0.25635 | 0.16022 | 0.97046 | 121.7468 | 0.24261 | 0.10528 | 121.7377 | 0.18768 | 121.5958 | 96.8811 | -121.7239 | -24.8886 | 121.6049 | 96.7987 | 80.7587 | 96.7987
1670.125 | 121.7468 | -97.7783 | 23.8495 | -0.0020601 | 0.0066629 | 0.071916 | 0.067152 | 0.0015529 | -0.0014484 | 0.00025205 | -0.0043029 | 0.050088 | 0.0061096 | -0.01025 | 0.0016194 | 0.015009 | -0.0051376 | -17.5552 | 23.8815 | -97.9477 | 23.7442 | -97.0596 | -97.7875 | -97.8378 | -1.0895 | -0.85602 | -1.0666 | -1.03 | -0.91095 | -1.0162 | -0.88348 | -0.16937 | 0.032044 | -0.10528 | 0.71869 | -0.05951 | -0.009156 | 0.10986 | 0.16022 | 96.7117 | -24.7055 | -24.8795 | 96.8674 | 96.8948 | 96.7621 | 0.1831 | 0.050354 | 0.88806 | 121.6919 | 0.15564 | 0.036621 | 121.8292 | 0.21057 | 121.6599 | 96.9223 | -121.7972 | -24.9161 | 121.5225 | 96.7484 | 80.2231 | 96.6888
1671.875 | 121.843 | -97.7371 | 23.8495 | 0.013199 | 0.0060221 | 0.073625 | 0.066298 | 0.0015529 | -0.0037982 | 0.00089285 | -0.0012513 | 0.049447 | 0.0071776 | 0.0042768 | 0.0031146 | 0.017573 | -0.001506 | -18.0496 | 23.8678 | -97.9294 | 23.8266 | -96.9543 | -97.7463 | -97.7921 | -1.0712 | -0.98419 | -1.1627 | -1.03 | -0.94757 | -1.0345 | -0.89722 | -0.19226 | 0.018311 | -0.022888 | 0.78278 | -0.054931 | -0.009155 | 0.13733 | 0.1831 | 96.5744 | -24.8337 | -24.8795 | 96.7896 | 96.8399 | 96.7026 | 0.2655 | 0.12817 | 0.97504 | 121.756 | 0.21515 | 0.13275 | 121.7972 | 0.17853 | 121.6049 | 96.7529 | -121.7789 | -25.0122 | 121.5637 | 96.7072 | 79.6875 | 96.666
1673.5625 | 121.7468 | -97.7509 | 23.8953 | -0.017319 | 0.0070901 | 0.071062 | 0.064803 | -0.0052829 | -0.0035846 | 3.8448e-05 | -0.0012513 | 0.049234 | 0.0080322 | -0.011745 | -0.0037212 | 0.014795 | -0.0047104 | -18.013 | 23.8953 | -97.9019 | 23.8403 | -96.9177 | -97.7097 | -97.7646 | -1.0345 | -0.85144 | -1.0574 | -1.0345 | -0.89722 | -0.98419 | -0.88348 | -0.15106 | 0 | -0.054932 | 0.83313 | -0.013733 | 0.041198 | 0.13733 | 0.19226 | 96.6934 | -24.7467 | -24.9298 | 96.8536 | 96.8674 | 96.7667 | 0.17395 | 0.073242 | 0.98419 | 121.7422 | 0.16022 | 0.022888 | 121.7972 | 0.20599 | 121.6461 | 96.8994 | -121.7972 | -24.9527 | 121.5912 | 96.7163 | 79.7379 | 96.7163
1675.3281 | 121.8292 | -97.7142 | 23.8724 | -0.0096891 | 0.0030313 | 0.073198 | 0.065016 | 0.00048494 | -0.0035846 | -0.00038875 | -0.0043029 | 0.050729 | 0.0050414 | 0.0023542 | 0.00055117 | 0.016077 | 0.0014846 | -18.5532 | 23.9044 | -97.934 | 23.8037 | -96.9543 | -97.728 | -97.7737 | -1.1124 | -0.9613 | -1.1444 | -1.062 | -0.93842 | -1.0208 | -0.90637 | -0.21973 | 0.032044 | -0.068664 | 0.75989 | -0.05951 | -0.013733 | 0.16022 | 0.20599 | 96.5698 | -24.8337 | -24.9344 | 96.7758 | 96.8079 | 96.6934 | 0.23804 | 0.1236 | 0.97961 | 121.7377 | 0.20599 | 0.082397 | 121.8384 | 0.1831 | 121.6187 | 96.7529 | -121.8063 | -25.0168 | 121.5179 | 96.6522 | 79.1611 | 96.6019
1677.0938 | 121.8201 | -97.7188 | 23.9227 | -0.017319 | 0.0064493 | 0.071916 | 0.067366 | 0.0032619 | -0.0029438 | -0.001457 | -0.0043029 | 0.050302 | 0.007605 | -0.0036274 | 0.002901 | 0.016291 | 0.0034072 | -18.75 | 23.9136 | -97.8607 | 23.8586 | -96.9269 | -97.7188 | -97.76 | -1.0941 | -0.97046 | -1.1398 | -1.062 | -0.96588 | -1.0437 | -0.92468 | -0.14191 | -0.009155 | -0.064086 | 0.79193 | -0.041199 | 0 | 0.10071 | 0.14191 | 96.579 | -24.8932 | -24.9847 | 96.7529 | 96.7941 | 96.6751 | 0.21515 | 0.096131 | 0.93384 | 121.7194 | 0.17395 | 0.07782 | 121.7743 | 0.16937 | 121.6324 | 96.7484 | -121.7834 | -25.0626 | 121.5775 | 96.6568 | 78.9688 | 96.6248
1678.8438 | 121.8063 | -121.5042 | 0.17395 | -0.0096891 | 0.0038857 | 0.073412 | 0.066512 | 0.00069854 | -0.0031574 | 0.0013202 | 0.0048523 | 0.051797 | 0.01145 | -0.0046954 | 0.00012397 | 0.014582 | 0.0006302 | -26.3123 | 0.19226 | -121.756 | -0.10986 | -120.6573 | -121.5408 | -121.6232 | -2.0737 | -1.7761 | -2.0187 | -2.0004 | -1.9455 | -2.005 | -1.8448 | -0.25177 | 0.018311 | -0.28381 | 0.84686 | -0.11902 | -0.036622 | 0.13275 | 0.21515 | 119.4855 | -1.9501 | -2.1744 | 119.5587 | 119.6594 | 119.4992 | 0.17395 | 0.013733 | 1.0986 | 121.6461 | 0.073242 | 0.018311 | 121.9482 | 0.24262 | 121.6965 | 119.7281 | -121.9299 | -2.1927 | 121.3943 | 119.5038 | 95.192 | 119.4305
1680.5469 | 121.8475 | -121.5179 | 0.16479 | -0.0096891 | 0.0032449 | 0.07213 | 0.069289 | 0.0041165 | -0.0042254 | 0.00025205 | 0.0018005 | 0.052438 | 0.0065368 | -0.006618 | -0.0024396 | 0.014582 | 0.0021256 | -25.7492 | 0.20599 | -121.7377 | -0.068665 | -120.5795 | -121.4676 | -121.5683 | -1.8997 | -1.6983 | -1.9318 | -1.8723 | -1.7761 | -1.8494 | -1.7258 | -0.21973 | 0.041199 | -0.23346 | 0.93842 | -0.050354 | 0.050354 | 0.16937 | 0.27008 | 119.5862 | -1.8631 | -2.037 | 119.7418 | 119.7922 | 119.6686 | 0.20599 | 0.082398 | 1.1581 | 121.669 | 0.15564 | 0.05951 | 121.9437 | 0.23346 | 121.7239 | 119.8196 | -121.9025 | -2.0966 | 121.4493 | 119.6457 | 95.7687 | 119.6182
1682.2969 | 121.7834 | -121.6003 | 0.17395 | 0.0055694 | 0.0066629 | 0.072771 | 0.066084 | 0.0026211 | -0.0029438 | 0.00089285 | -0.0073547 | 0.051797 | 0.0078186 | -0.006618 | 0.0037556 | 0.016504 | 0.00298 | -26.5457 | 0.19684 | -121.7834 | -0.09613 | -120.6665 | -121.5683 | -121.6507 | -2.0325 | -1.7303 | -1.9501 | -1.973 | -1.9089 | -1.9958 | -1.8219 | -0.1831 | 0.022888 | -0.27008 | 0.93384 | -0.050354 | 0.032044 | 0.13275 | 0.21515 | 119.6503 | -1.9043 | -2.1469 | 119.6915 | 119.7784 | 119.6045 | 0.12817 | -0.045777 | 1.1169 | 121.6873 | 0.041198 | -0.022888 | 121.9803 | 0.21973 | 121.7972 | 119.87 | -121.9574 | -2.124 | 121.5042 | 119.6274 | 95.0546 | 119.5679
1684.0625 | 121.9208 | -121.5408 | 0.13275 | -0.0096891 | 0.0064493 | 0.072557 | 0.065657 | 0.0034755 | -0.0023028 | -0.00081595 | -0.0012513 | 0.050516 | 0.0080322 | -0.0036274 | 0.00033757 | 0.016291 | -0.002147 | -26.532 | 0.17395 | -121.7697 | -0.013733 | -120.5475 | -121.4813 | -121.5408 | -1.9089 | -1.8311 | -1.9821 | -1.8631 | -1.7853 | -1.8585 | -1.7395 | -0.22888 | 0.041199 | -0.14648 | 0.99335 | 0 | 0.05951 | 0.22888 | 0.28839 | 119.5587 | -1.9638 | -1.9958 | 119.7556 | 119.8013 | 119.6823 | 0.24261 | 0.1236 | 1.2222 | 121.756 | 0.19684 | 0.11902 | 121.9437 | 0.15106 | 121.7148 | 119.7098 | -121.9025 | -2.1149 | 121.5271 | 119.6777 | 95.0089 | 119.632
1685.8125 | 121.8384 | -121.5912 | 0.16937 | -0.0020601 | 0.0064493 | 0.073625 | 0.066725 | 0.0062527 | -0.0037982 | 0.00046565 | -0.0043029 | 0.051797 | 0.0054688 | -0.0053364 | -0.00030343 | 0.014368 | 0.0027664 | -26.7426 | 0.18768 | -121.7834 | -0.064087 | -120.6024 | -121.5134 | -121.5866 | -1.886 | -1.6937 | -1.9089 | -1.8402 | -1.7807 | -1.8448 | -1.7166 | -0.19226 | 0.01831 | -0.23346 | 0.98877 | 0.004578 | 0.07782 | 0.19684 | 0.27008 | 119.6823 | -1.8631 | -2.0096 | 119.8105 | 119.8746 | 119.7464 | 0.19226 | 0.064087 | 1.181 | 121.7194 | 0.12817 | 0.068665 | 121.9711 | 0.21515 | 121.7789 | 119.8975 | -121.9528 | -2.0782 | 121.5271 | 119.751 | 94.8486 | 119.7052
1687.5781 | 121.8018 | -119.3665 | 2.4033 | 0.013199 | 0.0051675 | 0.072343 | 0.067152 | 0.0066799 | -0.0027302 | 0.0045244 | -0.0012513 | 0.05137 | 0.009314 | -0.0044818 | 0.0024738 | 0.016718 | 0.0006302 | -25.708 | 2.4399 | -119.5312 | 2.1332 | -118.4784 | -119.3573 | -119.4214 | -1.9592 | -1.6479 | -1.8997 | -1.8768 | -1.8311 | -1.918 | -1.7258 | -0.16479 | 0.036621 | -0.27008 | 0.88806 | -0.054932 | 0.009155 | 0.10986 | 0.17395 | 117.4667 | -4.0512 | -4.2801 | 117.5354 | 117.6407 | 117.4484 | 0.17395 | -0.018311 | 1.0529 | 121.6644 | 0.068664 | 0.022888 | 121.9711 | 0.25177 | 121.8063 | 117.7185 | -121.9345 | -4.303 | 121.4996 | 117.4896 | 93.6584 | 117.4072
1689.2656 | 121.8338 | -119.0918 | 2.6779 | 0.013199 | 0.0083719 | 0.073412 | 0.06758 | 0.0024075 | -0.0035846 | 0.0011066 | -0.0012513 | 0.052652 | 0.0091002 | -0.008968 | -0.00094423 | 0.015009 | -0.0059922 | -25.6531 | 2.7283 | -119.2429 | 2.4719 | -118.1168 | -119.0414 | -119.1101 | -1.8082 | -1.6251 | -1.8539 | -1.7899 | -1.7349 | -1.8173 | -1.6617 | -0.15106 | 0.050354 | -0.20599 | 0.97504 | -0.01831 | 0.050354 | 0.13275 | 0.20142 | 117.2379 | -4.303 | -4.4678 | 117.3569 | 117.4301 | 117.2745 | 0.19226 | 0.036621 | 1.1261 | 121.7148 | 0.11902 | 0.064087 | 121.9711 | 0.22888 | 121.8201 | 117.4667 | -121.9208 | -4.5319 | 121.5637 | 117.3019 | 93.4387 | 117.2836
1691.0156 | 121.7606 | -97.7463 | 24.0509 | -0.0020601 | 0.0068765 | 0.070634 | 0.064162 | 0.0041165 | -0.0040118 | -0.00038875 | -0.0012513 | 0.05372 | 0.010382 | -0.013454 | 0.00055117 | 0.016504 | 0.0008438 | -18.8782 | 24.1013 | -97.8241 | 23.9502 | -96.8811 | -97.6501 | -97.7097 | -1.0529 | -0.84228 | -1.0574 | -1.03 | -0.95673 | -1.0574 | -0.91095 | -0.07782 | 0.050354 | -0.10071 | 0.86517 | 0.036621 | 0.096131 | 0.11444 | 0.17395 | 96.6888 | -24.8932 | -25.0809 | 96.7896 | 96.8353 | 96.6888 | 0.14648 | 0 | 0.94299 | 121.7743 | 0.10071 | 0.027466 | 121.9254 | 0.21515 | 121.8475 | 96.904 | -121.875 | -25.1083 | 121.6965 | 96.7163 | 78.8681 | 96.6934
1692.6875 | 121.9025 | -97.673 | 24.0005 | -0.0096891 | 0.0053811 | 0.07213 | 0.066298 | 0.0021939 | -0.0010212 | 0.0013202 | -0.0012513 | 0.049234 | 0.0099548 | 0.0017132 | 0.0020466 | 0.018427 | -0.003215 | -18.9423 | 24.0601 | -97.8287 | 24.0097 | -96.8124 | -97.6364 | -97.6593 | -1.0254 | -0.9613 | -1.1261 | -0.98877 | -0.91095 | -1.0025 | -0.87433 | -0.15564 | 0.05951 | 0.009156 | 0.8606 | 0.013733 | 0.036621 | 0.16937 | 0.19226 | 96.5469 | -24.9619 | -24.9893 | 96.7621 | 96.7987 | 96.6705 | 0.25177 | 0.1236 | 1.0162 | 121.8384 | 0.21515 | 0.13733 | 121.8887 | 0.16479 | 121.7331 | 96.7117 | -121.8292 | -25.1266 | 121.6827 | 96.6843 | 78.7308 | 96.6476
1694.4531 | 121.9437 | -121.5591 | 0.14191 | -0.0020601 | 0.0043131 | 0.07213 | 0.064589 | -0.00058326 | -0.0018756 | 0.00089285 | -0.0043029 | 0.050516 | 0.0095276 | -0.0034138 | -0.0011578 | 0.01565 | 0.0027664 | -25.8179 | 0.15564 | -121.8018 | 0.027466 | -120.5017 | -121.4584 | -121.5088 | -1.7853 | -1.7029 | -1.886 | -1.7944 | -1.6754 | -1.7395 | -1.6571 | -0.24262 | 0.013733 | -0.11444 | 1.0574 | 0.050354 | 0.10071 | 0.29297 | 0.34332 | 119.6732 | -1.8448 | -1.9363 | 119.8837 | 119.902 | 119.8196 | 0.22888 | 0.14648 | 1.3 | 121.8292 | 0.21057 | 0.091552 | 121.9574 | 0.1831 | 121.7148 | 119.8563 | -121.9437 | -2.0279 | 121.5866 | 119.7647 | 95.7413 | 119.7739
1696.1562 | 121.9162 | -121.582 | 0.15564 | -0.0020601 | 0.0055947 | 0.07213 | 0.063094 | -0.0027195 | -0.0037982 | 0.0013202 | -0.0043029 | 0.05137 | 0.0056824 | -0.0078998 | 0.00097837 | 0.016718 | 0.00298 | -25.0671 | 0.14191 | -121.756 | -0.013733 | -120.5658 | -121.5225 | -121.5775 | -1.9913 | -1.886 | -2.0279 | -1.9547 | -1.8723 | -1.9455 | -1.8173 | -0.17395 | -0.013733 | -0.16937 | 1.0162 | 0.004577 | 0.059509 | 0.17853 | 0.23346 | 119.5541 | -2.0416 | -2.1103 | 119.7098 | 119.7647 | 119.6365 | 0.21057 | 0.082397 | 1.1902 | 121.7422 | 0.15564 | 0.073242 | 121.8979 | 0.14191 | 121.7239 | 119.696 | -121.9116 | -2.1835 | 121.5683 | 119.6274 | 96.5149 | 119.5908
1697.9062 | 121.9803 | -121.6232 | 0.13275 | -0.0096891 | 0.0045267 | 0.072557 | 0.065443 | -0.0029331 | -0.001662 | -0.002525 | 0.0018005 | 0.050088 | 0.0073914 | -0.0023456 | 0.001833 | 0.015864 | -0.0008652 | -25.3922 | 0.16022 | -121.7834 | -0.022888 | -120.575 | -121.4859 | -121.5317 | -1.9455 | -1.8402 | -2.0325 | -1.9135 | -1.799 | -1.8585 | -1.7532 | -0.16022 | 0.027466 | -0.15564 | 1.0483 | 0.091553 | 0.13733 | 0.25177 | 0.29755 | 119.5908 | -1.973 | -2.0462 | 119.8242 | 119.87 | 119.7647 | 0.27924 | 0.17395 | 1.2085 | 121.7606 | 0.23346 | 0.11902 | 121.9437 | 0.19226 | 121.7834 | 119.783 | -121.9162 | -2.1652 | 121.6003 | 119.7098 | 96.2311 | 119.6777
1699.5938 | 121.8567 | -121.6461 | 0.17395 | -0.0020601 | 0.0053811 | 0.074693 | 0.067152 | 0.0026211 | -0.0031574 | -0.0016706 | -0.0012513 | 0.053934 | 0.0078186 | -0.0057636 | 0.00012397 | 0.015864 | -0.001506 | -25.1587 | 0.19226 | -121.8109 | -0.050354 | -120.6299 | -121.5637 | -121.6095 | -2.037 | -1.8265 | -2.0691 | -2.0325 | -1.9547 | -2.0691 | -1.8997 | -0.16479 | 0.018311 | -0.2243 | 1.0162 | 0.036621 | 0.082397 | 0.20142 | 0.24719 | 119.577 | -2.0004 | -2.2064 | 119.6915 | 119.7464 | 119.577 | 0.16937 | 0 | 1.181 | 121.7606 | 0.11444 | 0.036621 | 122.0032 | 0.24262 | 121.8384 | 119.8196 | -121.9849 | -2.243 | 121.5958 | 119.6136 | 96.4874 | 119.6091
1701.3594 | 121.8521 | -121.6553 | 0.17853 | -0.0020601 | 0.0058083 | 0.073839 | 0.066512 | 0.0043301 | -0.0025166 | 0.00025205 | -0.0043029 | 0.052865 | 0.007605 | -0.0061908 | 0.00097837 | 0.016077 | -1.0598e-05 | -25.2594 | 0.1831 | -121.8246 | -0.11444 | -120.6757 | -121.6278 | -121.6507 | -2.1515 | -1.8723 | -2.1011 | -2.0966 | -2.0416 | -2.1332 | -1.9684 | -0.16937 | 0.004577 | -0.29297 | 0.97961 | 0.004577 | 0.027465 | 0.17395 | 0.19684 | 119.5541 | -2.0508 | -2.2751 | 119.6136 | 119.6869 | 119.5221 | 0.13275 | -0.032044 | 1.149 | 121.7102 | 0.059509 | 0.004577 | 122.0078 | 0.22888 | 121.8384 | 119.783 | -122.0032 | -2.2797 | 121.5408 | 119.5587 | 96.3959 | 119.5038
1703.125 | 121.907 | -121.669 | 0.16937 | -0.0096891 | 0.0053811 | 0.069139 | 0.066939 | 5.774e-05 | -0.0031574 | 0.0011066 | -0.0073547 | 0.051797 | 0.0063232 | -0.0053364 | -0.0013714 | 0.014368 | -0.000438 | -24.4629 | 0.18768 | -121.843 | -0.09613 | -120.6757 | -121.5683 | -121.6049 | -2.0554 | -1.8173 | -2.0279 | -1.9821 | -1.8906 | -1.9867 | -1.8356 | -0.17395 | 0.01831 | -0.2655 | 0.99335 | 0.064087 | 0.10071 | 0.23804 | 0.27466 | 119.6411 | -1.9867 | -2.1515 | 119.7784 | 119.8334 | 119.6823 | 0.19226 | 0.041199 | 1.1673 | 121.7468 | 0.13733 | 0.045776 | 122.0306 | 0.21057 | 121.8567 | 119.8517 | -122.0123 | -2.1973 | 121.5729 | 119.6869 | 97.2061 | 119.6136
1704.875 | 121.8567 | -121.6782 | 0.20599 | 0.013199 | 0.0064493 | 0.073839 | 0.06523 | 0.0032619 | -0.00080758 | 0.00089285 | 0.0018005 | 0.052225 | 0.0097412 | -0.0059772 | 0.00055117 | 0.015009 | -0.0008652 | -0.036621 | 0.20599 | -121.8658 | -0.11902 | -120.6573 | -121.6232 | -121.6507 | -2.1606 | -1.8494 | -2.0966 | -2.0828 | -2.0325 | -2.1149 | -1.9455 | -0.18768 | 0 | -0.32501 | 1.0208 | 0.027466 | 0.054932 | 0.21515 | 0.24261 | 119.5816 | -2.0554 | -2.2888 | 119.6457 | 119.7327 | 119.5633 | 0.15106 | -0.01831 | 1.2085 | 121.7468 | 0.064087 | 0.013733 | 122.0718 | 0.24719 | 121.8842 | 119.8288 | -122.0718 | -2.3026 | 121.5591 | 119.5953 | 121.6415 | 119.5175
1706.5781 | 121.9391 | -121.6599 | 0.15564 | 0.0055694 | 0.0055947 | 0.071489 | 0.063307 | 0.0015529 | -0.0027302 | -0.00017515 | -0.0043029 | 0.050943 | 0.0063232 | -0.0036274 | 0.002901 | 0.01565 | 0.0004166 | -0.041199 | 0.15564 | -121.8292 | -0.050354 | -120.5704 | -121.5591 | -121.5591 | -2.1011 | -1.9363 | -2.1194 | -2.0645 | -1.973 | -2.0325 | -1.9089 | -0.16937 | 0 | -0.20599 | 1.0895 | 0.10071 | 0.10071 | 0.27008 | 0.27008 | 119.5404 | -2.092 | -2.2202 | 119.6869 | 119.751 | 119.6274 | 0.21057 | 0.086975 | 1.2588 | 121.7789 | 0.14648 | 0.054932 | 121.9849 | 0.18311 | 121.8155 | 119.7235 | -121.9849 | -2.2751 | 121.6095 | 119.5953 | 121.6187 | 119.5587
1708.3281 | 121.9528 | -121.5317 | 0.25177 | -0.0096891 | 0.0047403 | 0.073625 | 0.064375 | 0.00048494 | -0.0010212 | -0.0029524 | -0.0043029 | 0.04902 | 0.007605 | -0.0064044 | 0.001833 | 0.014368 | 0.0004166 | 0.091553 | 0.26093 | -121.7056 | 0.073242 | -120.4514 | -121.4539 | -121.4676 | -2.1103 | -2.005 | -2.1561 | -2.0691 | -1.9913 | -2.092 | -1.9501 | -0.17395 | 0.009155 | -0.17853 | 1.0803 | 0.064087 | 0.07782 | 0.23804 | 0.25177 | 119.3756 | -2.2568 | -2.3209 | 119.5404 | 119.5816 | 119.4397 | 0.20599 | 0.064087 | 1.2543 | 121.7789 | 0.1648 | 0.086975 | 121.9666 | 0.15106 | 121.7926 | 119.5267 | -121.9574 | -2.4078 | 121.6049 | 119.4626 | 121.6232 | 119.4214
1710.0156 | 121.962 | -121.582 | 0.21973 | -0.0096891 | 0.0047403 | 0.072557 | 0.064803 | 0.0028347 | -0.0031574 | 0.0015338 | -0.0012513 | 0.049875 | 0.0065368 | -0.0012774 | -0.00094423 | 0.0133 | 0.0023392 | 0.054932 | 0.19684 | -121.7697 | 0.045776 | -120.4605 | -121.4996 | -121.4767 | -2.092 | -1.9958 | -2.1652 | -2.0828 | -2.005 | -2.0782 | -1.9638 | -0.18768 | -0.022889 | -0.17395 | 1.1215 | 0.10528 | 0.082397 | 0.29297 | 0.27008 | 119.4168 | -2.2156 | -2.3026 | 119.577 | 119.6182 | 119.5038 | 0.20142 | 0.086975 | 1.3092 | 121.8155 | 0.16022 | 0.082397 | 121.9666 | 0.16937 | 121.7789 | 119.5862 | -121.9894 | -2.3849 | 121.6278 | 119.4992 | 121.637 | 119.4901
1711.7812 | 121.9437 | -121.6644 | 0.1831 | -0.0020601 | 0.0068765 | 0.071489 | 0.068007 | -0.00015586 | -0.0020892 | 0.0023882 | -0.010406 | 0.051584 | 0.005255 | -0.0087542 | -0.0030804 | 0.015223 | 0.0014846 | 0 | 0.20599 | -121.843 | -0.022888 | -120.5658 | -121.5546 | -121.5637 | -2.0187 | -1.8585 | -2.0599 | -1.9821 | -1.8997 | -2.0004 | -1.8631 | -0.17853 | 0.022889 | -0.20599 | 1.0986 | 0.10071 | 0.10986 | 0.27924 | 0.28839 | 119.6045 | -2.0416 | -2.1652 | 119.7647 | 119.8013 | 119.664 | 0.19684 | 0.05951 | 1.2772 | 121.8201 | 0.16022 | 0.07782 | 122.049 | 0.20142 | 121.8704 | 119.8059 | -122.0261 | -2.243 | 121.6415 | 119.6823 | 121.6644 | 119.6457
1713.5469 | 121.8979 | -121.5637 | 0.34332 | -0.0096891 | 0.0055947 | 0.069994 | 0.063521 | 0.0045437 | -0.0042254 | -0.0010298 | -0.0043029 | 0.050088 | 0.0067504 | -0.0044818 | -0.0026532 | 0.014368 | 0.0016982 | 0.073242 | 0.35248 | -121.7377 | 0.022888 | -120.4742 | -121.4584 | -121.4539 | -2.0828 | -1.799 | -2.0233 | -2.0233 | -1.9226 | -2.005 | -1.8723 | -0.17395 | 0.009155 | -0.32043 | 1.0895 | 0.10986 | 0.10529 | 0.28381 | 0.27924 | 119.5404 | -2.1423 | -2.3666 | 119.6411 | 119.6915 | 119.5587 | 0.15106 | 0.01831 | 1.2634 | 121.7606 | 0.10071 | 0 | 122.0901 | 0.2243 | 121.9162 | 119.7647 | -122.081 | -2.3666 | 121.5866 | 119.5404 | 121.637 | 119.4809
1715.3125 | 122.0215 | -119.3024 | 2.4582 | -0.0020601 | 0.0049539 | 0.073198 | 0.067366 | -0.00079686 | -0.0031574 | 0.0032428 | -0.010406 | 0.047738 | 0.0054688 | 0.0017132 | 0.002901 | 0.017145 | 0.001271 | 2.3529 | 2.4811 | -119.4672 | 2.3666 | -118.1442 | -119.1971 | -119.1559 | -1.9409 | -1.8951 | -2.0279 | -1.8951 | -1.8082 | -1.9043 | -1.767 | -0.16479 | 0.022888 | -0.091553 | 1.1581 | 0.14648 | 0.10528 | 0.31128 | 0.27008 | 117.2745 | -4.3533 | -4.3533 | 117.4942 | 117.5354 | 117.3981 | 0.26093 | 0.1236 | 1.3229 | 121.8338 | 0.21973 | 0.13275 | 121.9482 | 0.13275 | 121.7834 | 117.4072 | -121.9254 | -4.4861 | 121.669 | 117.4072 | 121.6553 | 117.3615
1717.0625 | 121.9437 | -118.8629 | 2.9709 | -0.017319 | 0.11048 | 0.073625 | -0.0020615 | 0.069272 | 0.10173 | -0.0029524 | -0.0012513 | 0.051156 | 0.006964 | -0.0023456 | 0.00076477 | 0.017359 | -0.0010788 | 2.7969 | 3.0121 | -119.0186 | -116.4642 | 2.9434 | 1.886 | -45.6207 | -2.0142 | -1.8402 | -2.0508 | -1.9958 | -1.9135 | -1.9958 | -1.8402 | -0.15564 | 0.041199 | -119.4351 | 121.8063 | 73.2422 | 120.7489 | 73.3978 | 120.9045 | 116.8121 | -4.8111 | -4.9667 | 116.9495 | 117.0227 | 116.8671 | 0.21057 | 0.054931 | 121.962 | 2.5543 | 0.13733 | 0.054931 | 122.0306 | 0.21057 | 121.875 | 117.0227 | -121.9894 | -5.0217 | 2.3987 | 116.8671 | 121.6599 | 116.8488
1718.8125 | 122.0306 | -118.6707 | 3.1265 | -0.0020601 | 0.10664 | 0.075548 | -0.0033433 | 0.068417 | 0.10066 | -0.00060235 | -0.0012513 | 0.049234 | 0.006964 | -0.0029864 | 0.00097837 | 0.017145 | 0.0031936 | 2.9617 | 3.1174 | -118.8583 | -116.3361 | 3.2181 | 1.506 | -46.9208 | -1.8539 | -1.8173 | -1.9867 | -1.8723 | -1.7441 | -1.8219 | -1.7303 | -0.18768 | -0.009155 | -119.4626 | 121.8887 | 71.7499 | 120.1767 | 71.9376 | 120.3644 | 116.684 | -4.9438 | -4.9988 | 116.9266 | 116.9403 | 116.8488 | 0.25635 | 0.1648 | 122.0764 | 2.5223 | 0.24261 | 0.11444 | 121.9757 | 0.16937 | 121.788 | 116.8533 | -121.9849 | -5.1132 | 2.3346 | 116.7984 | 121.6324 | 116.8167
1720.5156 | 121.9666 | -121.6965 | 0.17395 | 0.0055694 | 0.10942 | 0.074052 | -0.0016343 | 0.06564 | 0.10024 | 0.00046565 | 0.0018005 | 0.050729 | 0.0048278 | -0.0040546 | -0.0013714 | 0.013727 | 0.000203 | -0.009155 | 0.13733 | -121.843 | -118.84 | 0.18768 | -1.506 | -49.7681 | -1.8951 | -1.7899 | -1.9638 | -1.9043 | -1.799 | -1.8768 | -1.7624 | -0.14648 | -0.036621 | -119.014 | 121.8842 | 71.9284 | 120.1904 | 72.0749 | 120.3369 | 119.7327 | -1.9638 | -2.0782 | 119.8975 | 119.9341 | 119.8196 | 0.20142 | 0.086975 | 122.0306 | 3.0029 | 0.1648 | 0.059509 | 121.9803 | 0.17395 | 121.8338 | 119.9066 | -122.0169 | -2.1378 | 2.8564 | 119.7922 | 121.6873 | 119.8013
1722.2656 | 121.9482 | -121.6919 | 0.16479 | -0.0096891 | 0.17115 | 0.13771 | 7.473e-05 | 0.067563 | 0.1013 | 0.0011066 | -0.0012513 | 0.051156 | 0.0091002 | -0.0085406 | 0.00097837 | 0.014368 | 0.0010574 | -0.050354 | 0.16937 | -121.8842 | -3.2639 | 0.10986 | -1.5656 | -1.7212 | -1.9135 | -1.7441 | -1.973 | -1.8906 | -1.8127 | -1.9135 | -1.7715 | -0.19226 | 0.004578 | -3.4286 | 121.8018 | 119.9707 | 120.1263 | 120.163 | 120.3186 | 119.7189 | -1.9089 | -2.0554 | 119.8792 | 119.9203 | 119.7784 | 0.20142 | 0.059509 | 121.994 | 118.6203 | 0.16022 | 0.082397 | 122.0535 | 0.22888 | 121.8613 | 119.9478 | -122.049 | -2.1378 | 118.428 | 119.8013 | 121.6415 | 119.7784
1724.0156 | 122.0078 | -121.7102 | 0.14648 | -0.0020601 | 0.17158 | 0.13622 | -0.0035569 | 0.067135 | 0.099382 | -0.00060235 | -0.0012513 | 0.050729 | 0.007605 | 0.0025678 | -0.00051703 | 0.017786 | 0.0008438 | -0.091553 | 0.15106 | -121.875 | -2.9755 | 0.12817 | -1.5198 | -1.593 | -1.8723 | -1.7395 | -1.918 | -1.8265 | -1.7075 | -1.7899 | -1.6937 | -0.16479 | 0.004578 | -3.1219 | 121.8384 | 120.1172 | 120.1904 | 120.282 | 120.3552 | 119.7922 | -1.886 | -1.973 | 120.0027 | 120.0165 | 119.9203 | 0.2243 | 0.12817 | 122.0032 | 118.8995 | 0.21057 | 0.091553 | 122.0261 | 0.17853 | 121.8613 | 119.9707 | -122.0215 | -2.0645 | 118.7347 | 119.8837 | 121.6187 | 119.838
1725.7031 | 122.0535 | -121.6736 | 0.13275 | -0.017319 | 0.1359 | 0.13835 | -0.00056607 | 0.1073 | 0.099595 | -0.00038875 | -0.010406 | 0.049234 | 0.0065368 | -0.00085019 | 0.0031146 | 0.015436 | -0.002147 | -0.009155 | 0.1236 | -121.8384 | -2.5543 | 0.16022 | -1.6022 | -1.5335 | -1.9501 | -1.8997 | -2.005 | -1.8997 | -1.8265 | -1.918 | -1.7899 | -0.16479 | -0.009155 | -2.6871 | 121.8338 | 120.1401 | 120.0714 | 120.3049 | 120.2362 | 119.6686 | -2.0325 | -2.0325 | 119.8471 | 119.8837 | 119.7556 | 0.21515 | 0.086975 | 121.9986 | 119.2841 | 0.17853 | 0.10529 | 121.962 | 0.10529 | 121.7972 | 119.7739 | -121.9711 | -2.1378 | 119.1193 | 119.7739 | 121.6644 | 119.7235
1727.4688 | 122.0398 | -121.6965 | 0.14191 | -0.0020601 | 0.13655 | 0.1375 | -0.0029159 | 0.10858 | 0.098527 | -0.00017515 | -0.0043029 | 0.050516 | 0.005255 | -0.0029864 | 0.0056782 | 0.015864 | 0.0008438 | 0.004578 | 0.14648 | -121.875 | -2.4536 | 0.15564 | -1.7487 | -1.4511 | -1.9409 | -1.886 | -2.0142 | -1.9089 | -1.8219 | -1.9135 | -1.7853 | -0.17853 | 0.004577 | -2.5955 | 121.8521 | 120.2454 | 119.9478 | 120.4239 | 120.1263 | 119.6823 | -2.0279 | -2.0508 | 119.8746 | 119.9112 | 119.783 | 0.22888 | 0.10071 | 122.0306 | 119.4214 | 0.19226 | 0.10528 | 122.0215 | 0.12817 | 121.843 | 119.8105 | -122.0169 | -2.1561 | 119.2429 | 119.7876 | 121.701 | 119.7556
1729.2344 | 122.0215 | -121.6782 | 0.1236 | -0.0020601 | 0.13697 | 0.13793 | -0.0020615 | 0.10516 | 0.10066 | -0.0035932 | -0.0012513 | 0.050088 | 0.005255 | -0.0027728 | 0.0014056 | 0.014795 | 0.0031936 | -0.07782 | 0.16479 | -121.8887 | -2.5772 | 0.091553 | -1.8036 | -1.4969 | -1.8906 | -1.7761 | -1.9547 | -1.8265 | -1.7715 | -1.8585 | -1.7075 | -0.21057 | 0.041199 | -2.7008 | 121.7697 | 120.1813 | 119.8746 | 120.3918 | 120.0851 | 119.7235 | -1.8997 | -1.9501 | 119.9066 | 119.9707 | 119.8196 | 0.24719 | 0.09613 | 121.9803 | 119.3115 | 0.18311 | 0.12817 | 122.0535 | 0.17853 | 121.843 | 119.902 | -122.0123 | -2.0782 | 119.101 | 119.8517 | 121.6003 | 119.7876
1731 | 122.0123 | -121.6873 | 0.16022 | 0.0055694 | 0.13569 | 0.13728 | 0.00092933 | 0.11371 | 0.099382 | 0.0011066 | -0.0043029 | 0.050088 | 0.007605 | 0.0010724 | 0.0026874 | 0.01565 | 0.0038346 | -0.082397 | 0.17853 | -121.9025 | -2.5314 | 0.073242 | -1.9135 | -1.4465 | -1.918 | -1.767 | -1.9638 | -1.8494 | -1.7853 | -1.8539 | -1.712 | -0.21515 | 0.018311 | -2.6916 | 121.7606 | 120.2408 | 119.7739 | 120.4559 | 119.989 | 119.7235 | -1.9272 | -2.0096 | 119.902 | 119.9753 | 119.8334 | 0.25177 | 0.10986 | 121.9757 | 119.371 | 0.17853 | 0.11444 | 122.081 | 0.19684 | 121.8658 | 119.9203 | -122.0627 | -2.124 | 119.1559 | 119.838 | 121.6049 | 119.7693
1732.7031 | 121.9437 | -121.7285 | 0.16937 | 0.013199 | 0.13441 | 0.13728 | -0.00077967 | 0.10794 | 0.099382 | 0.001961 | -0.0012513 | 0.050943 | 0.0061096 | -0.0057636 | -0.00030343 | 0.014795 | 0.0014846 | -0.068665 | 0.14648 | -121.8933 | -2.6459 | 0.086975 | -1.8951 | -1.474 | -1.8631 | -1.6525 | -1.8906 | -1.8539 | -1.7761 | -1.8723 | -1.7258 | -0.16479 | -0.022889 | -2.8152 | 121.8155 | 120.2545 | 119.8334 | 120.4193 | 119.9982 | 119.838 | -1.8219 | -2.0233 | 119.9524 | 120.0027 | 119.8563 | 0.16479 | 0.018311 | 121.9803 | 119.2474 | 0.11444 | 0.036621 | 122.0398 | 0.23804 | 121.875 | 120.076 | -122.0627 | -2.0599 | 119.0826 | 119.8746 | 121.6599 | 119.8654
1734.4531 | 121.8475 | -121.8063 | 0.1831 | 0.0055694 | 0.016703 | 0.012315 | -0.0031297 | 0.021206 | 0.0015424 | -0.00060235 | -0.0043029 | 0.050516 | 0.0091002 | -0.0070454 | 0.0022602 | 0.015864 | 0.000203 | 0.050354 | 0.036621 | -0.30212 | -0.27008 | -0.13275 | -0.24719 | -0.19226 | -1.9775 | -1.7029 | -1.9455 | -1.918 | -1.8585 | -1.9455 | -1.7761 | 121.5042 | -0.14648 | -0.45319 | 121.6736 | 121.6141 | 121.5591 | 0.10986 | 0.054932 | 119.8608 | -1.886 | -2.1011 | 119.9478 | 120.0302 | 119.8608 | 0.16937 | 0 | 0.16937 | 0.032043 | 0.086975 | 0.027466 | 0.33875 | 0.24261 | 121.843 | 120.1035 | -0.48523 | -2.1286 | 121.5363 | 119.8883 | 121.8567 | 119.8288
1736.2188 | 121.9025 | -121.8292 | 0.16479 | -0.0020601 | 0.017985 | 0.011888 | -0.0018479 | 0.015011 | -0.00059378 | 0.00067925 | -0.0043029 | 0.053506 | 0.0082458 | -0.0057636 | 0.001192 | 0.014582 | 0.0025528 | -0.022888 | 0.091553 | -0.26093 | -0.22888 | -0.073242 | -0.18768 | -0.14648 | -1.9913 | -1.6937 | -1.9501 | -1.9226 | -1.8494 | -1.9409 | -1.767 | 121.5683 | -0.073242 | -0.39368 | 121.756 | 121.6827 | 121.6415 | 0.11444 | 0.073242 | 119.8792 | -1.8585 | -2.0874 | 119.9799 | 120.0623 | 119.8883 | 0.1831 | 0.009155 | 0.18768 | 0.032043 | 0.10071 | 0.027466 | 0.35248 | 0.25635 | 121.9208 | 120.1355 | -0.42572 | -2.1149 | 121.6003 | 119.9066 | 121.8063 | 119.838
1737.9688 | 122.0627 | -121.7377 | 0.14191 | -0.017319 | 0.014994 | 0.0093246 | -0.0037705 | 0.018643 | -0.003371 | -0.00038875 | -0.0043029 | 0.049447 | 0.0078186 | -0.0025592 | -0.001585 | 0.014368 | 0.004689 | 0.050354 | 0.10529 | -0.13733 | -0.018311 | 0.19684 | 0.064087 | 0.07782 | -1.7395 | -1.6708 | -1.8265 | -1.7258 | -1.5884 | -1.6891 | -1.5884 | 121.6003 | -0.036621 | -0.16022 | 121.9345 | 121.8155 | 121.8018 | 0.21515 | 0.20142 | 119.9112 | -1.8127 | -1.8677 | 120.1492 | 120.1492 | 120.0485 | 0.23804 | 0.13733 | 0.33417 | 0.11902 | 0.23804 | 0.10071 | 0.24262 | 0.15564 | 121.843 | 120.0668 | -0.27924 | -1.9684 | 121.7194 | 120.0119 | 121.788 | 119.9982
1739.6406 | 121.9482 | -121.7789 | 0.17395 | -0.017319 | 0.019267 | 0.011888 | -0.0012069 | 0.021634 | -0.0020892 | -0.00081595 | -0.0043029 | 0.052438 | 0.007605 | -0.01025 | -0.00030343 | 0.015436 | 0.0006302 | 0.022888 | 0.1236 | -0.16937 | -0.10529 | 0.068665 | -0.054932 | -0.041199 | -1.8585 | -1.6617 | -1.8677 | -1.8402 | -1.7395 | -1.8539 | -1.6983 | 121.6095 | -0.050354 | -0.27924 | 121.8475 | 121.7377 | 121.7239 | 0.12817 | 0.11444 | 119.9112 | -1.8356 | -2.0142 | 120.0394 | 120.0806 | 119.9249 | 0.16937 | 0.013733 | 0.23804 | 0.064087 | 0.12817 | 0.027466 | 0.29297 | 0.20599 | 121.9025 | 120.1172 | -0.34332 | -2.0416 | 121.6736 | 119.9387 | 121.8018 | 119.9203
1741.4219 | 122.0627 | -121.7331 | 0.12817 | -0.0020601 | 0.017131 | 0.011247 | -0.0018479 | 0.022702 | -0.00038018 | -0.00081595 | -0.0012513 | 0.050516 | 0.0080322 | -0.0068316 | 0.0058918 | 0.017145 | 0.001912 | 0.013733 | 0.073242 | -0.19226 | -0.073242 | 0.11444 | -0.032043 | -0.009155 | -1.8082 | -1.7441 | -1.9089 | -1.8036 | -1.6846 | -1.7807 | -1.6663 | 121.5408 | -0.054932 | -0.20142 | 121.8475 | 121.7239 | 121.701 | 0.18311 | 0.16022 | 119.8242 | -1.8723 | -1.9318 | 120.0485 | 120.0668 | 119.9524 | 0.24262 | 0.12817 | 0.3067 | 0.11902 | 0.22431 | 0.10529 | 0.2655 | 0.1648 | 121.8063 | 119.989 | -0.32044 | -2.037 | 121.6599 | 119.9295 | 121.7468 | 119.9249
1743.1094 | 122.081 | -121.7331 | 0.1236 | 0.0055694 | 0.016062 | 0.012315 | -0.0029159 | 0.021634 | 0.00026062 | -0.00081595 | -0.0012513 | 0.051156 | 0.0067504 | -0.0040546 | 0.0033282 | 0.015436 | 0.0040482 | -0.013733 | 0.073242 | -0.18768 | -0.086975 | 0.073242 | -0.045776 | -0.004578 | -1.6251 | -1.561 | -1.7075 | -1.6067 | -1.5244 | -1.6022 | -1.474 | 121.5454 | -0.050354 | -0.21057 | 121.8063 | 121.7285 | 121.6873 | 0.1831 | 0.14191 | 120.0256 | -1.6846 | -1.7303 | 120.2087 | 120.2591 | 120.1309 | 0.23346 | 0.10528 | 0.26092 | 0.10071 | 0.1831 | 0.10071 | 0.26092 | 0.14648 | 121.8063 | 120.1721 | -0.31128 | -1.8311 | 121.6461 | 120.1263 | 121.7194 | 120.108
1744.8594 | 121.9666 | -121.8201 | 0.15564 | 0.0055694 | 0.017558 | 0.010179 | -0.0020615 | 0.024411 | -0.00016658 | -0.00060235 | 0.0048523 | 0.049234 | 0.0082458 | -0.0036274 | -0.0011578 | 0.015009 | 0.0014846 | -0.086975 | 0.1236 | -0.19684 | -0.17853 | -0.018311 | -0.14191 | -0.11444 | -1.799 | -1.5381 | -1.7715 | -1.7487 | -1.6617 | -1.7715 | -1.5839 | 121.6232 | -0.032044 | -0.33417 | 121.8018 | 121.7056 | 121.6782 | 0.082397 | 0.054931 | 120.0485 | -1.6937 | -1.9043 | 120.1584 | 120.2362 | 120.0485 | 0.18768 | 0 | 0.17853 | 0.01831 | 0.10986 | 0.022888 | 0.32043 | 0.23346 | 121.9437 | 120.282 | -0.35248 | -1.9272 | 121.6415 | 120.0714 | 121.7331 | 120.0211
1746.5781 | 122.0993 | -121.7743 | 0.14648 | -0.0020601 | 0.015422 | 0.01082 | -0.0035569 | 0.019497 | -0.0031574 | -0.0018842 | -0.0043029 | 0.049234 | 0.0056824 | -0.0010638 | 0.00033757 | 0.014368 | 0.0021256 | 0.036621 | 0.13733 | -0.10986 | 0.009155 | 0.20599 | 0.09613 | 0.07782 | -1.5518 | -1.4603 | -1.6525 | -1.5472 | -1.4053 | -1.506 | -1.4008 | 121.6644 | -0.009155 | -0.13733 | 121.9803 | 121.8521 | 121.8704 | 0.18768 | 0.20599 | 120.1218 | -1.6068 | -1.6937 | 120.369 | 120.3735 | 120.2683 | 0.25177 | 0.14648 | 0.31586 | 0.11902 | 0.24719 | 0.10529 | 0.24719 | 0.19226 | 121.9116 | 120.314 | -0.25635 | -1.799 | 121.7834 | 120.2271 | 121.8109 | 120.2225
1748.2812 | 121.9986 | -121.8063 | 0.17395 | -0.017319 | 0.015422 | 0.011247 | -0.0020615 | 0.020138 | -0.0044392 | 0.00046565 | -0.0073547 | 0.053506 | 0.0084594 | -0.011531 | 0.00076477 | 0.014155 | -0.0010788 | -0.018311 | 0.13733 | -0.15106 | -0.082397 | 0.086975 | -0.032043 | -0.022888 | -1.6342 | -1.4374 | -1.6663 | -1.6296 | -1.5381 | -1.6525 | -1.4877 | 121.6553 | -0.036621 | -0.25635 | 121.8933 | 121.7834 | 121.7743 | 0.12817 | 0.11902 | 120.1401 | -1.6113 | -1.8036 | 120.2682 | 120.3186 | 120.1538 | 0.17853 | 0.013733 | 0.23804 | 0.068665 | 0.12817 | 0.036621 | 0.28839 | 0.22888 | 121.9437 | 120.369 | -0.32501 | -1.8402 | 121.7239 | 120.1767 | 121.788 | 120.1721
1750.0156 | 122.0673 | -121.7697 | 0.13733 | -0.017319 | 0.015635 | 0.010606 | -0.0039841 | 0.019497 | -0.00038018 | -0.0018842 | -0.0012513 | 0.050088 | 0.0082458 | -0.0046954 | -8.9634e-05 | 0.015009 | 0.0006302 | -0.091553 | 0.10986 | -0.13275 | -0.07782 | 0.082397 | -0.036621 | 0.009155 | -1.506 | -1.3458 | -1.5244 | -1.4465 | -1.3367 | -1.4145 | -1.2955 | 121.637 | -0.027466 | -0.21515 | 121.8521 | 121.7789 | 121.7331 | 0.14191 | 0.09613 | 120.2454 | -1.4832 | -1.5839 | 120.433 | 120.4742 | 120.3552 | 0.22888 | 0.10986 | 0.21515 | 0.054931 | 0.18768 | 0.07782 | 0.24261 | 0.17853 | 121.8796 | 120.4239 | -0.27008 | -1.6617 | 121.6919 | 120.3232 | 121.6782 | 120.2637
1751.7031 | 122.081 | -121.788 | 0.13275 | -0.017319 | 0.017985 | 0.0099656 | -0.0020615 | 0.022275 | -0.0031574 | 3.8448e-05 | -0.0043029 | 0.050088 | 0.0063232 | 0.0036358 | 0.0031146 | 0.016932 | 0.0021256 | -0.064087 | 0.091553 | -0.1236 | -0.050354 | 0.12817 | -0.022888 | 0.027466 | -1.4236 | -1.3779 | -1.5198 | -1.4236 | -1.3367 | -1.4328 | -1.2863 | 121.6644 | -0.041198 | -0.18311 | 121.9162 | 121.8155 | 121.7651 | 0.15106 | 0.10071 | 120.2683 | -1.5106 | -1.5564 | 120.4514 | 120.5017 | 120.3552 | 0.23346 | 0.086975 | 0.25177 | 0.073242 | 0.18311 | 0.09613 | 0.21515 | 0.14191 | 121.8796 | 120.4102 | -0.25635 | -1.6525 | 121.7377 | 120.3644 | 121.7239 | 120.3644
1753.4531 | 121.994 | -121.8292 | 0.16479 | -0.0096891 | 0.017771 | 0.0078294 | -0.00056607 | 0.020138 | -0.0020892 | -0.0038068 | -0.0073547 | 0.05372 | 0.0078186 | -0.007259 | -0.0028668 | 0.013514 | 0.001912 | -0.045776 | 0.20599 | -0.10071 | -0.086975 | 0.082397 | -0.018311 | -0.004578 | -1.5152 | -1.2405 | -1.4694 | -1.4832 | -1.3824 | -1.4557 | -1.3092 | 121.7285 | 0.041199 | -0.25177 | 121.9116 | 121.8246 | 121.8109 | 0.09613 | 0.082397 | 120.3598 | -1.4053 | -1.6479 | 120.4468 | 120.52 | 120.3735 | 0.16022 | 0.013733 | 0.18311 | 0.013733 | 0.086975 | -0.013733 | 0.3067 | 0.22888 | 122.0352 | 120.5887 | -0.2655 | -1.6342 | 121.7422 | 120.3461 | 121.7834 | 120.314
1755.1406 | 122.0718 | -121.8246 | 0.16479 | 0.0055694 | 0.017985 | 0.014452 | 0.00028833 | 0.019284 | -0.00016658 | -0.0018842 | -0.0073547 | 0.050943 | 0.0084594 | -0.0057636 | 0.001192 | 0.0133 | -0.003215 | -0.018311 | 0.17853 | -0.11902 | -0.050354 | 0.10071 | 0 | 0.018311 | -1.4603 | -1.3092 | -1.5106 | -1.4603 | -1.355 | -1.4557 | -1.3092 | 121.7056 | 0.013733 | -0.21515 | 121.9254 | 121.843 | 121.8246 | 0.13733 | 0.11902 | 120.314 | -1.474 | -1.6251 | 120.4697 | 120.5154 | 120.369 | 0.20142 | 0.054932 | 0.21973 | 0.068665 | 0.15564 | 0.050354 | 0.29755 | 0.20142 | 122.0032 | 120.5154 | -0.28381 | -1.6754 | 121.7743 | 120.3644 | 121.8063 | 120.3644
1756.8906 | 122.1542 | -121.8018 | 0.15106 | 0.0055694 | 0.016062 | 0.010606 | -0.00035247 | 0.02377 | -0.0027302 | -0.0012434 | 0.0018005 | 0.049447 | 0.0056824 | -0.004909 | -8.9634e-05 | 0.014368 | 0.003621 | -0.036621 | 0.12817 | -0.10529 | -0.036621 | 0.15564 | 0.054932 | 0.059509 | -1.4191 | -1.3412 | -1.5152 | -1.3916 | -1.2863 | -1.355 | -1.2497 | 121.6965 | -0.022888 | -0.18768 | 121.9574 | 121.8613 | 121.8567 | 0.16479 | 0.16022 | 120.2866 | -1.4923 | -1.5427 | 120.5154 | 120.5521 | 120.4468 | 0.2655 | 0.16022 | 0.26093 | 0.068665 | 0.22888 | 0.1236 | 0.23346 | 0.17395 | 121.9299 | 120.4605 | -0.25635 | -1.6663 | 121.7651 | 120.4102 | 121.7651 | 120.3827
1758.6562 | 122.0627 | -121.8475 | 0.16937 | -0.0096891 | 0.018412 | 0.010179 | -0.0014207 | 0.022915 | -0.0018756 | 0.0013202 | -0.0043029 | 0.050943 | 0.0084594 | -0.0093952 | -0.00094423 | 0.014155 | 0.0008438 | -0.050354 | 0.17395 | -0.09613 | -0.059509 | 0.07782 | -0.022888 | 0.004578 | -1.5244 | -1.3046 | -1.5152 | -1.474 | -1.387 | -1.4969 | -1.3412 | 121.7514 | 0.004577 | -0.22888 | 121.9254 | 121.8521 | 121.8246 | 0.10071 | 0.073242 | 120.3323 | -1.474 | -1.6434 | 120.4605 | 120.5063 | 120.3506 | 0.17395 | 0.018311 | 0.17395 | 0.036621 | 0.12817 | 0.041199 | 0.27008 | 0.21057 | 122.0215 | 120.5429 | -0.2655 | -1.6846 | 121.788 | 120.3735 | 121.7972 | 120.3232
1760.4219 | 121.9986 | -121.8704 | 0.15564 | -0.0096891 | 0.017131 | 0.0099656 | -0.0024887 | 0.021206 | -0.0031574 | -0.0033796 | -0.013458 | 0.050302 | 0.009314 | -0.014095 | -0.0017986 | 0.016291 | -0.0010788 | -0.059509 | 0.20599 | -0.10986 | -0.07782 | 0.068665 | -0.013733 | -0.009155 | -1.6113 | -1.3367 | -1.5472 | -1.5472 | -1.4465 | -1.5381 | -1.3824 | 121.7606 | 0.050354 | -0.23346 | 121.9391 | 121.8613 | 121.8567 | 0.10071 | 0.09613 | 120.3232 | -1.4923 | -1.7029 | 120.4239 | 120.488 | 120.3323 | 0.1648 | 0.009155 | 0.17853 | 0.032043 | 0.10071 | 0 | 0.31586 | 0.21057 | 122.0764 | 120.5338 | -0.2655 | -1.7029 | 121.7926 | 120.3232 | 121.8109 | 120.2591
1762.125 | 122.0215 | -121.8384 | 0.15564 | 0.0055694 | 0.01649 | 0.01082 | 0.00050193 | 0.022061 | -0.0037982 | 0.0013202 | -0.0012513 | 0.053506 | 0.0097412 | -0.0068316 | 0.0022602 | 0.014155 | -0.002147 | -0.032043 | 0.16022 | -0.12817 | -0.07782 | 0.086975 | -0.036621 | -0.013733 | -1.6022 | -1.4099 | -1.6251 | -1.5793 | -1.506 | -1.6113 | -1.4557 | 121.7102 | 0.004577 | -0.23346 | 121.9254 | 121.8246 | 121.8018 | 0.11444 | 0.091553 | 120.2133 | -1.5656 | -1.7349 | 120.3323 | 120.3827 | 120.2271 | 0.16937 | 0.013733 | 0.21515 | 0.050354 | 0.11902 | 0.045776 | 0.28839 | 0.21515 | 121.9986 | 120.4285 | -0.28381 | -1.7807 | 121.7606 | 120.2591 | 121.8063 | 120.2362
1763.875 | 122.0352 | -121.843 | 0.15564 | -0.0020601 | 0.018626 | 0.010179 | -0.00099327 | 0.024411 | -0.0031574 | -0.00038875 | 0.0018005 | 0.053506 | 0.0071776 | -0.004909 | 0.001192 | 0.014582 | -0.0019332 | -0.10071 | 0.12817 | -0.15106 | -0.13733 | 0.013733 | -0.11444 | -0.064087 | -1.6708 | -1.4191 | -1.6617 | -1.6067 | -1.5289 | -1.6434 | -1.474 | 121.6919 | -0.027466 | -0.29297 | 121.8567 | 121.7789 | 121.7285 | 0.086975 | 0.036621 | 120.1813 | -1.5747 | -1.7624 | 120.314 | 120.369 | 120.1996 | 0.18768 | 0.01831 | 0.16479 | 0.013733 | 0.13275 | 0.054932 | 0.27924 | 0.24262 | 121.9711 | 120.4239 | -0.3067 | -1.8173 | 121.7056 | 120.2362 | 121.7422 | 120.1721
1765.625 | 121.3715 | -121.1288 | 0.16022 | 0.0055694 | 0.017131 | 0.0086838 | -0.0041977 | 0.018643 | -0.0031574 | 0.0015338 | -0.0012513 | 0.04902 | 0.0061096 | -0.0029864 | -0.0024396 | 0.014368 | -0.0023606 | 0.009155 | 0.14191 | -0.10071 | 0.004578 | 0.19226 | 0.086975 | 0.064087 | -1.4969 | -1.3504 | -1.5472 | -1.506 | -1.4008 | -1.474 | -1.355 | 121.0281 | -0.01831 | -0.15564 | 121.3211 | 121.1929 | 121.2158 | 0.1648 | 0.18768 | 119.5816 | -1.5106 | -1.6663 | 119.7281 | 119.7739 | 119.6548 | 0.19226 | 0.073242 | 0.29297 | 0.10529 | 0.14648 | 0.041199 | 0.24262 | 0.19684 | 121.2708 | 119.7784 | -0.26093 | -1.7075 | 121.1334 | 119.6228 | 121.138 | 119.632
1767.4062 | 121.9391 | -121.6965 | 0.15106 | -0.0096891 | 0.01884 | 0.012743 | -0.0012069 | 0.021847 | -0.0023028 | -0.0016706 | -0.0012513 | 0.050943 | 0.0065368 | -0.0087542 | 0.00097837 | 0.014155 | -0.001506 | -0.018311 | 0.16479 | -0.12817 | -0.045776 | 0.1236 | 0.009155 | 0.022888 | -1.4648 | -1.3321 | -1.561 | -1.4603 | -1.3779 | -1.474 | -1.3596 | 121.5683 | 0.013733 | -0.19684 | 121.8201 | 121.7194 | 121.7056 | 0.15106 | 0.13733 | 120.1355 | -1.4832 | -1.6113 | 120.3186 | 120.3369 | 120.2225 | 0.20142 | 0.086975 | 0.25177 | 0.082398 | 0.18311 | 0.10071 | 0.29297 | 0.22888 | 121.8613 | 120.3644 | -0.27924 | -1.712 | 121.6507 | 120.2362 | 121.6782 | 120.2316
1769.1094 | 121.8933 | -121.7377 | 0.14191 | -0.0096891 | 0.018412 | 0.012956 | -0.00035247 | 0.024197 | 0.00047422 | 3.8448e-05 | 0.0018005 | 0.052011 | 0.0082458 | -0.0036274 | 0.0020466 | 0.01565 | 0.0066116 | -0.045776 | 0.17395 | -0.13275 | -0.10071 | 0.064087 | -0.082397 | -0.032043 | -1.6022 | -1.355 | -1.5839 | -1.5656 | -1.4877 | -1.5976 | -1.4374 | 121.6049 | 0.032043 | -0.24262 | 121.8018 | 121.7056 | 121.6553 | 0.10071 | 0.050354 | 120.1538 | -1.4969 | -1.7075 | 120.2499 | 120.3003 | 120.1401 | 0.14648 | -0.013733 | 0.19684 | 0.032043 | 0.09613 | 0.01831 | 0.3067 | 0.22888 | 121.9116 | 120.3827 | -0.27466 | -1.7258 | 121.637 | 120.1721 | 121.6919 | 120.1355
1770.8594 | 122.081 | -121.7606 | 0.13275 | 0.0055694 | 0.019694 | 0.009752 | -0.0031297 | 0.018002 | -0.0012348 | 0.00046565 | -0.0012513 | 0.048807 | 0.0084594 | 0.0034222 | 0.001192 | 0.015223 | 0.0027664 | -0.036621 | 0.14648 | -0.09613 | -0.004578 | 0.17853 | 0.059509 | 0.091553 | -1.4648 | -1.387 | -1.5564 | -1.4236 | -1.3138 | -1.3962 | -1.2863 | 121.6644 | 0.013733 | -0.13733 | 121.9391 | 121.8521 | 121.8201 | 0.18768 | 0.15564 | 120.2042 | -1.5198 | -1.5564 | 120.4468 | 120.4742 | 120.3644 | 0.27008 | 0.16022 | 0.27466 | 0.091552 | 0.24261 | 0.13275 | 0.24261 | 0.16937 | 121.907 | 120.3735 | -0.22888 | -1.6891 | 121.756 | 120.3369 | 121.7239 | 120.2957
1772.625 | 121.994 | -121.7743 | 0.15106 | -0.017319 | 0.017344 | 0.010393 | -0.0016343 | 0.022061 | -0.0029438 | -0.0012434 | -0.0012513 | 0.050729 | 0.008673 | 0.00043161 | -0.0013714 | 0.016077 | 0.0010574 | -0.036621 | 0.20142 | -0.09613 | -0.068665 | 0.086975 | -0.004578 | 0.018311 | -1.5564 | -1.3367 | -1.5701 | -1.5015 | -1.4008 | -1.5106 | -1.3687 | 121.6782 | 0.050354 | -0.21973 | 121.8613 | 121.7926 | 121.7697 | 0.11444 | 0.091552 | 120.2042 | -1.4877 | -1.6525 | 120.3735 | 120.4056 | 120.2637 | 0.20142 | 0.059509 | 0.1831 | 0.027465 | 0.16937 | 0.068664 | 0.29755 | 0.23346 | 121.9757 | 120.4376 | -0.24719 | -1.7212 | 121.7056 | 120.2728 | 121.7377 | 120.2179
1774.3906 | 122.0901 | -121.7651 | 0.1236 | -0.0020601 | 0.016703 | 0.012102 | -0.0020615 | 0.022061 | -0.0042254 | -0.0040204 | -0.0012513 | 0.050088 | 0.0095276 | 0.001286 | 0.00012397 | 0.015009 | -0.0012924 | -0.045776 | 0.16022 | -0.091553 | -0.022888 | 0.17853 | 0.050354 | 0.09613 | -1.5381 | -1.4465 | -1.6251 | -1.4786 | -1.3733 | -1.442 | -1.3504 | 121.6736 | 0.036621 | -0.14648 | 121.9437 | 121.8613 | 121.8155 | 0.18768 | 0.14191 | 120.1401 | -1.5701 | -1.6022 | 120.3918 | 120.4147 | 120.3232 | 0.27466 | 0.18311 | 0.27008 | 0.068665 | 0.25177 | 0.14648 | 0.25177 | 0.17853 | 121.9254 | 120.3186 | -0.21515 | -1.7487 | 121.7422 | 120.2866 | 121.7194 | 120.2271
1776.0781 | 122.0169 | -121.8018 | 0.15564 | -0.0020601 | 0.017771 | 0.010179 | 0.00028833 | 0.023556 | -0.0020892 | -0.00038875 | -0.0012513 | 0.053506 | 0.0080322 | -0.0074726 | 0.0024738 | 0.014795 | -0.0008652 | -0.013733 | 0.16479 | -0.091553 | -0.041199 | 0.13275 | 0.009155 | 0.022888 | -1.5564 | -1.387 | -1.5976 | -1.5381 | -1.474 | -1.5656 | -1.4191 | 121.7102 | 0.009155 | -0.19684 | 121.9345 | 121.8246 | 121.8109 | 0.11444 | 0.10071 | 120.2042 | -1.5427 | -1.6937 | 120.3278 | 120.3827 | 120.2362 | 0.17853 | 0.032043 | 0.2243 | 0.050354 | 0.1236 | 0.059509 | 0.25635 | 0.21057 | 121.9666 | 120.4147 | -0.24719 | -1.7532 | 121.7606 | 120.2637 | 121.788 | 120.2454
1777.8281 | 122.0627 | -121.8018 | 0.15106 | -0.0096891 | 0.017344 | 0.009111 | -0.0018479 | 0.023556 | -0.00059378 | 0.00046565 | -0.0073547 | 0.050943 | 0.0082458 | -0.0057636 | 0.00012397 | 0.016291 | -1.0598e-05 | -0.050354 | 0.11902 | -0.091553 | -0.027466 | 0.17395 | 0.009155 | 0.050354 | -1.6251 | -1.5472 | -1.6937 | -1.5884 | -1.4877 | -1.5839 | -1.474 | 121.7102 | -0.032043 | -0.17853 | 121.9757 | 121.8521 | 121.8109 | 0.14191 | 0.10071 | 120.108 | -1.6983 | -1.7395 | 120.314 | 120.3278 | 120.2179 | 0.21973 | 0.10986 | 0.2655 | 0.064087 | 0.20599 | 0.10529 | 0.21057 | 0.14648 | 121.9208 | 120.2545 | -0.24261 | -1.8448 | 121.7743 | 120.2133 | 121.7514 | 120.1767
1779.5938 | 122.0352 | -121.8155 | 0.14648 | -0.017319 | 0.018412 | 0.0093246 | -0.0014207 | 0.020779 | -0.0035846 | -0.00038875 | -0.0043029 | 0.052865 | 0.005896 | -0.0098224 | 0.00012397 | 0.014368 | 0.0034072 | -0.013733 | 0.18768 | -0.09613 | -0.054932 | 0.10529 | 0.009155 | 0.027466 | -1.4557 | -1.2634 | -1.4786 | -1.4099 | -1.3138 | -1.4282 | -1.2863 | 121.7194 | 0.041199 | -0.20142 | 121.9208 | 121.843 | 121.8246 | 0.1236 | 0.10528 | 120.3369 | -1.4099 | -1.5564 | 120.5017 | 120.5292 | 120.3873 | 0.19226 | 0.050354 | 0.20142 | 0.041198 | 0.1648 | 0.068665 | 0.28381 | 0.21515 | 122.0032 | 120.5521 | -0.24261 | -1.6251 | 121.7606 | 120.4056 | 121.8018 | 120.3598
1781.3594 | 122.1451 | -121.8063 | 0.11902 | 0.0055694 | 0.015849 | 0.0099656 | -0.0041977 | 0.022702 | -0.0014484 | 0.00067925 | 0.0018005 | 0.046884 | 0.0080322 | -0.0029864 | -0.0017986 | 0.013514 | -0.003215 | 0.009155 | 0.15106 | -0.073242 | 0.032043 | 0.23346 | 0.091553 | 0.11444 | -1.3596 | -1.3138 | -1.474 | -1.355 | -1.2222 | -1.3138 | -1.2222 | 121.7331 | 0.032043 | -0.086976 | 122.0398 | 121.9208 | 121.8979 | 0.18768 | 0.16479 | 120.3323 | -1.4328 | -1.474 | 120.5841 | 120.5841 | 120.4926 | 0.25177 | 0.16022 | 0.3067 | 0.10529 | 0.25177 | 0.11902 | 0.2243 | 0.16022 | 121.9574 | 120.4926 | -0.19226 | -1.593 | 121.8384 | 120.4514 | 121.8155 | 120.4468
1783.0469 | 122.0078 | -121.8658 | 0.16479 | -0.040207 | 0.015422 | 0.0084702 | -0.0024887 | 0.026547 | -0.0065754 | -0.001457 | -0.010406 | 0.050729 | 0.0078186 | -0.002132 | 0.00033757 | 0.014368 | -0.0002244 | -0.064087 | 0.1831 | -0.10529 | -0.10529 | 0.068665 | -0.027466 | 0.009155 | -1.5244 | -1.2726 | -1.4557 | -1.4694 | -1.3779 | -1.4603 | -1.3138 | 121.7606 | 0.01831 | -0.27008 | 121.9345 | 121.875 | 121.8384 | 0.11444 | 0.07782 | 120.4102 | -1.4374 | -1.6342 | 120.488 | 120.5521 | 120.4056 | 0.14191 | -0.004578 | 0.17395 | 0 | 0.077819 | -0.013733 | 0.28839 | 0.18311 | 122.0489 | 120.5933 | -0.27008 | -1.6205 | 121.7606 | 120.3964 | 121.8018 | 120.3415
1784.7812 | 122.0169 | -121.8613 | 0.14191 | -0.0020601 | 0.019053 | 0.011034 | 7.473e-05 | 0.023984 | -0.00059378 | -0.001457 | 0.0018005 | 0.052225 | 0.0067504 | -0.0091816 | 0.0033282 | 0.013727 | 0.0031936 | -0.064087 | 0.16937 | -0.11902 | -0.12817 | 0.018311 | -0.073242 | -0.050354 | -1.5976 | -1.3412 | -1.5656 | -1.5472 | -1.474 | -1.5564 | -1.387 | 121.7422 | 0.027466 | -0.27008 | 121.8796 | 121.8109 | 121.788 | 0.068665 | 0.045777 | 120.2957 | -1.4832 | -1.6891 | 120.3873 | 120.4742 | 120.3049 | 0.17853 | 0.009156 | 0.13733 | -0.009155 | 0.091553 | 0.018311 | 0.28839 | 0.2243 | 122.0306 | 120.52 | -0.26093 | -1.7075 | 121.7331 | 120.314 | 121.7972 | 120.2637
1786.5469 | 122.1497 | -121.8292 | 0.12817 | -0.0020601 | 0.014567 | 0.010179 | -0.0035569 | 0.020352 | -0.0025166 | -0.00017515 | -0.0012513 | 0.049875 | 0.0073914 | -0.00085019 | 0.00033757 | 0.014368 | 0.0021256 | -0.045776 | 0.15564 | -0.10529 | -0.018311 | 0.14648 | 0.032043 | 0.068665 | -1.5518 | -1.4236 | -1.593 | -1.4786 | -1.3916 | -1.4648 | -1.3504 | 121.7239 | 0.027466 | -0.14649 | 121.9757 | 121.8979 | 121.8613 | 0.17395 | 0.13733 | 120.2362 | -1.5518 | -1.6068 | 120.4376 | 120.4788 | 120.3644 | 0.24262 | 0.12817 | 0.25177 | 0.086975 | 0.20142 | 0.11444 | 0.26093 | 0.16937 | 121.9849 | 120.4056 | -0.23346 | -1.7212 | 121.8109 | 120.3506 | 121.7834 | 120.2774
1788.25 | 122.0993 | -121.8338 | 0.1236 | 0.0055694 | 0.015422 | 0.009111 | 0.00028833 | 0.020779 | -0.0014484 | -0.0016706 | -0.0012513 | 0.049875 | 0.007605 | -0.0023456 | 0.001192 | 0.01565 | -0.000438 | -0.050354 | 0.12817 | -0.082397 | -0.032043 | 0.14648 | 0.004578 | 0.045776 | -1.6067 | -1.474 | -1.6296 | -1.5564 | -1.4832 | -1.5564 | -1.4328 | 121.7514 | 0.004578 | -0.15564 | 121.9803 | 121.8796 | 121.8384 | 0.12817 | 0.086975 | 120.2042 | -1.5976 | -1.68 | 120.3506 | 120.401 | 120.2774 | 0.19684 | 0.073243 | 0.22888 | 0.050354 | 0.14648 | 0.073243 | 0.21057 | 0.15564 | 121.962 | 120.3598 | -0.20599 | -1.7532 | 121.8018 | 120.2774 | 121.7834 | 120.2271
1789.9375 | 122.0032 | -121.8796 | 0.16479 | -0.0096891 | 0.018199 | 0.012102 | -0.00056607 | 0.026333 | -0.0018756 | 0.0011066 | -0.0043029 | 0.050943 | 0.0082458 | -0.0087542 | -8.9634e-05 | 0.013727 | 0.001271 | -0.045776 | 0.17853 | -0.10529 | -0.09613 | 0.041199 | -0.07782 | -0.032043 | -1.6891 | -1.4053 | -1.6434 | -1.6159 | -1.5747 | -1.6663 | -1.474 | 121.7743 | 0.013733 | -0.26092 | 121.9208 | 121.8475 | 121.8018 | 0.073243 | 0.027466 | 120.2362 | -1.5701 | -1.7807 | 120.3049 | 120.4056 | 120.2133 | 0.16937 | -0.022888 | 0.14649 | 0.009156 | 0.068665 | 0.027466 | 0.28381 | 0.23804 | 122.0581 | 120.4742 | -0.27008 | -1.8082 | 121.7834 | 120.2637 | 121.8338 | 120.1904
1791.6875 | 122.0581 | -121.8842 | 0.13733 | -0.0020601 | 0.019053 | 0.011034 | 0.00050193 | 0.023343 | 0.0015424 | -0.0023114 | -0.0012513 | 0.050729 | 0.0071776 | 0.00085881 | 0.001192 | 0.01565 | 0.001912 | -0.059509 | 0.17853 | -0.12817 | -0.091553 | 0.045776 | -0.073242 | -0.036621 | -1.6525 | -1.4191 | -1.6479 | -1.6067 | -1.5427 | -1.6388 | -1.4603 | 121.756 | 0.041199 | -0.22888 | 121.9299 | 121.8475 | 121.8109 | 0.091553 | 0.054932 | 120.2362 | -1.5564 | -1.7441 | 120.3415 | 120.4239 | 120.2454 | 0.18768 | 0.009155 | 0.17395 | 0.036621 | 0.10529 | 0.041199 | 0.3067 | 0.22888 | 122.0627 | 120.4651 | -0.2655 | -1.7853 | 121.7926 | 120.2774 | 121.8246 | 120.2316
1793.4375 | 122.1176 | -121.875 | 0.13275 | -0.0096891 | 0.017985 | 0.01082 | -0.00056607 | 0.020993 | -0.0010212 | 0.0026018 | -0.010406 | 0.049875 | 0.009314 | -0.0032 | 0.0020466 | 0.015436 | 0.0008438 | -0.032043 | 0.11444 | -0.050354 | -0.013733 | 0.17853 | 0.018311 | 0.059509 | -1.6022 | -1.5198 | -1.6617 | -1.5656 | -1.4832 | -1.5793 | -1.4557 | 121.8246 | -0.01831 | -0.14648 | 122.0535 | 121.9345 | 121.8933 | 0.10986 | 0.068665 | 120.2133 | -1.6525 | -1.6983 | 120.3918 | 120.4193 | 120.2957 | 0.20599 | 0.082397 | 0.22888 | 0.036621 | 0.17853 | 0.09613 | 0.16479 | 0.14191 | 121.9894 | 120.3552 | -0.18311 | -1.7944 | 121.8613 | 120.3094 | 121.843 | 120.2728
1795.125 | 122.1817 | -121.843 | 0.10529 | -0.0096891 | 0.016276 | 0.012102 | -0.0024887 | 0.025052 | -0.0014484 | 0.00089285 | -0.0012513 | 0.050302 | 0.0065368 | -0.0042682 | 0.0037556 | 0.016932 | -0.000438 | 0.013733 | 0.14191 | -0.068665 | 0.018311 | 0.19226 | 0.041199 | 0.086975 | -1.5656 | -1.5015 | -1.6342 | -1.5152 | -1.442 | -1.5335 | -1.4008 | 121.7743 | 0.036621 | -0.086975 | 122.0352 | 121.9299 | 121.8842 | 0.15564 | 0.10986 | 120.2087 | -1.6068 | -1.6205 | 120.401 | 120.4422 | 120.3094 | 0.23346 | 0.10071 | 0.26093 | 0.086976 | 0.19226 | 0.11902 | 0.21057 | 0.13275 | 121.9849 | 120.3415 | -0.17395 | -1.7395 | 121.8613 | 120.3278 | 121.8567 | 120.2774
1796.875 | 122.168 | -121.8613 | 0.1236 | -0.0096891 | 0.018199 | 0.010393 | -0.0018479 | 0.017575 | -0.003371 | -0.00017515 | 0.0018005 | 0.04902 | 0.0078186 | 0.0032086 | 0.00033757 | 0.013514 | -1.0598e-05 | 0.009155 | 0.15106 | -0.073242 | 0.036621 | 0.22888 | 0.11444 | 0.11444 | -1.4557 | -1.4053 | -1.5656 | -1.4603 | -1.3229 | -1.4236 | -1.3275 | 121.788 | 0.027466 | -0.086975 | 122.0901 | 121.9757 | 121.9757 | 0.18768 | 0.18768 | 120.2957 | -1.5289 | -1.5839 | 120.5383 | 120.5338 | 120.4376 | 0.23804 | 0.14191 | 0.30212 | 0.10986 | 0.24262 | 0.10529 | 0.2243 | 0.16022 | 122.0123 | 120.4559 | -0.19684 | -1.6891 | 121.8979 | 120.401 | 121.8704 | 120.4056
1798.5625 | 122.1085 | -121.8475 | 0.15564 | -0.0096891 | 0.018626 | 0.010393 | -0.0012069 | 0.019284 | -0.0025166 | -0.0012434 | 0.0018005 | 0.053293 | 0.006964 | -0.0029864 | -8.9634e-05 | 0.015436 | -0.0019332 | -0.009155 | 0.17853 | -0.09613 | -0.022888 | 0.13275 | 0.013733 | 0.032043 | -1.5472 | -1.4008 | -1.5976 | -1.5198 | -1.4328 | -1.5472 | -1.4008 | 121.7514 | 0.022888 | -0.17853 | 121.9803 | 121.8796 | 121.8613 | 0.12817 | 0.10986 | 120.2499 | -1.5564 | -1.6754 | 120.4147 | 120.4468 | 120.3003 | 0.19684 | 0.050354 | 0.22888 | 0.073242 | 0.1648 | 0.07782 | 0.27466 | 0.19684 | 122.0261 | 120.4468 | -0.25177 | -1.7532 | 121.8246 | 120.3278 | 121.8384 | 120.3003
1800.3125 | 122.0901 | -121.9025 | 0.15564 | -0.0096891 | 0.017131 | 0.0082566 | -0.0022751 | 0.022061 | -0.0023028 | -0.0016706 | -0.0073547 | 0.05137 | 0.0080322 | -0.0034138 | -0.00073063 | 0.014582 | -0.003215 | -0.059509 | 0.17853 | -0.091553 | -0.086975 | 0.050354 | -0.022888 | -0.004578 | -1.6251 | -1.3916 | -1.6067 | -1.5747 | -1.4648 | -1.5564 | -1.4053 | 121.8109 | 0.022888 | -0.24261 | 121.9528 | 121.8979 | 121.8796 | 0.086975 | 0.068665 | 120.2957 | -1.5472 | -1.7303 | 120.4376 | 120.4971 | 120.3461 | 0.20142 | 0.050354 | 0.14191 | 0.004578 | 0.14191 | 0.032043 | 0.27008 | 0.21515 | 122.081 | 120.5109 | -0.24719 | -1.7624 | 121.8155 | 120.3278 | 121.843 | 120.2774
1802 | 122.081 | -121.9162 | 0.14648 | 0.0055694 | 0.017985 | 0.01317 | 0.00092933 | 0.022488 | -0.0018756 | 3.8448e-05 | 0.0048523 | 0.050088 | 0.007605 | -0.0085406 | 0.0024738 | 0.01565 | 0.000203 | -0.054932 | 0.19226 | -0.10986 | -0.10986 | 0.045776 | -0.07782 | -0.027466 | -1.7075 | -1.442 | -1.6983 | -1.6479 | -1.5884 | -1.6754 | -1.5198 | 121.8063 | 0.045777 | -0.25635 | 121.962 | 121.8887 | 121.8384 | 0.082397 | 0.032043 | 120.2179 | -1.5884 | -1.7944 | 120.3278 | 120.3964 | 120.2408 | 0.17853 | 0.022888 | 0.15564 | 0 | 0.10986 | 0.050354 | 0.30212 | 0.25635 | 122.1085 | 120.4742 | -0.25635 | -1.8448 | 121.8063 | 120.2683 | 121.8613 | 120.2087
1803.75 | 122.1771 | -121.8933 | 0.1236 | -0.0096891 | 0.015849 | 0.010393 | -0.0035569 | 0.017575 | -0.00080758 | 3.8448e-05 | -0.0073547 | 0.049447 | 0.008673 | 4.214e-06 | 0.00055117 | 0.015223 | 0.0016982 | -0.050354 | 0.13275 | -0.086975 | -0.041199 | 0.11902 | 0.009155 | 0.045776 | -1.5976 | -1.4374 | -1.6205 | -1.5427 | -1.4328 | -1.5152 | -1.3916 | 121.8063 | 0.009155 | -0.16479 | 122.0123 | 121.9391 | 121.9025 | 0.13275 | 0.09613 | 120.2728 | -1.561 | -1.6663 | 120.4605 | 120.5017 | 120.3781 | 0.22888 | 0.10528 | 0.20599 | 0.045776 | 0.18768 | 0.077819 | 0.21973 | 0.1831 | 122.0261 | 120.4559 | -0.21057 | -1.7441 | 121.8521 | 120.3506 | 121.843 | 120.2957
1805.4531 | 122.1817 | -121.8933 | 0.12817 | 0.0055694 | 0.016062 | 0.011034 | -0.0031297 | 0.020779 | -0.0020892 | 0.00067925 | 0.0048523 | 0.050943 | 0.0061096 | 0.001286 | -0.0013714 | 0.015864 | 0.0014846 | -0.045776 | 0.13733 | -0.086975 | -0.022888 | 0.14648 | 0.041199 | 0.073242 | -1.5884 | -1.4603 | -1.6159 | -1.5472 | -1.4282 | -1.5015 | -1.4099 | 121.8063 | 0.009155 | -0.15106 | 122.0398 | 121.9666 | 121.9345 | 0.16022 | 0.12817 | 120.2774 | -1.5884 | -1.6754 | 120.4651 | 120.4834 | 120.3918 | 0.20599 | 0.11444 | 0.23346 | 0.064087 | 0.18768 | 0.068665 | 0.2243 | 0.15564 | 122.0306 | 120.433 | -0.21515 | -1.7441 | 121.8704 | 120.3461 | 121.8475 | 120.3049
1807.2188 | 122.1634 | -121.907 | 0.13275 | -0.017319 | 0.013926 | 0.008043 | -0.0024887 | 0.022275 | -0.0040118 | -0.0033796 | -0.0012513 | 0.049875 | 0.005255 | 0.00064521 | -0.0011578 | 0.013941 | -0.001506 | -0.050354 | 0.13733 | -0.091553 | -0.032043 | 0.14191 | 0.032043 | 0.059509 | -1.5976 | -1.4465 | -1.6205 | -1.5381 | -1.4374 | -1.5289 | -1.4099 | 121.8155 | 0.004578 | -0.16479 | 122.049 | 121.9666 | 121.9391 | 0.15106 | 0.1236 | 120.2866 | -1.5793 | -1.6708 | 120.4697 | 120.4971 | 120.3781 | 0.21057 | 0.091552 | 0.23346 | 0.05951 | 0.1831 | 0.082397 | 0.22888 | 0.17395 | 122.0444 | 120.4605 | -0.2243 | -1.7532 | 121.875 | 120.369 | 121.8567 | 120.3094
1808.9688 | 122.2046 | -121.8933 | 0.11902 | -0.0096891 | 0.016703 | 0.011888 | -0.0029159 | 0.020138 | -0.0010212 | 0.0021746 | 0.0018005 | 0.050088 | 0.007605 | -0.0040546 | -8.9634e-05 | 0.014795 | 0.0008438 | -0.027466 | 0.15106 | -0.086975 | -0.004578 | 0.15106 | 0.050354 | 0.086975 | -1.5381 | -1.4465 | -1.6067 | -1.4832 | -1.3733 | -1.442 | -1.3412 | 121.8063 | 0.032043 | -0.1236 | 122.0444 | 121.9803 | 121.9437 | 0.17395 | 0.13733 | 120.2866 | -1.5656 | -1.6022 | 120.52 | 120.5521 | 120.4514 | 0.2655 | 0.16479 | 0.23804 | 0.082397 | 0.23346 | 0.1236 | 0.23804 | 0.16022 | 122.0444 | 120.4468 | -0.20599 | -1.7258 | 121.8887 | 120.4102 | 121.8658 | 120.3552
1810.6562 | 122.0947 | -121.9391 | 0.14191 | -0.017319 | 0.017985 | 0.010179 | -0.0012069 | 0.017361 | -0.0027302 | 0.00089285 | -0.0043029 | 0.05372 | 0.006964 | -0.0096088 | -0.00094423 | 0.011591 | -1.0598e-05 | -0.064087 | 0.17853 | -0.091553 | -0.09613 | 0.045776 | -0.032043 | -0.004578 | -1.6617 | -1.387 | -1.6296 | -1.6022 | -1.4969 | -1.5976 | -1.442 | 121.8475 | 0.036621 | -0.23804 | 121.9849 | 121.9345 | 121.907 | 0.086975 | 0.05951 | 120.3094 | -1.5289 | -1.7441 | 120.4422 | 120.4971 | 120.3415 | 0.18768 | 0.032044 | 0.13733 | -0.004577 | 0.13275 | 0.027466 | 0.27008 | 0.24262 | 122.1176 | 120.5521 | -0.23346 | -1.7715 | 121.843 | 120.3369 | 121.875 | 120.2774
1812.4219 | 122.1725 | -121.9025 | 0.1236 | -0.0020601 | 0.016276 | 0.0076156 | -0.0014207 | 0.018643 | -0.0025166 | -0.00017515 | -0.010406 | 0.04902 | 0.0071776 | 0.0019268 | 0.0020466 | 0.016077 | 0.000203 | -0.054932 | 0.1236 | -0.054932 | -0.041199 | 0.12817 | 0.018311 | 0.050354 | -1.7532 | -1.5701 | -1.7441 | -1.6846 | -1.5839 | -1.6663 | -1.5381 | 121.8475 | 0 | -0.16479 | 122.0306 | 121.9528 | 121.9208 | 0.10529 | 0.073243 | 120.1584 | -1.6937 | -1.8082 | 120.3186 | 120.3644 | 120.2362 | 0.20599 | 0.07782 | 0.18311 | 0.013733 | 0.16022 | 0.05951 | 0.17853 | 0.17395 | 122.0261 | 120.3323 | -0.17853 | -1.8677 | 121.8613 | 120.2179 | 121.8475 | 120.1492
1814.1719 | 122.2046 | -121.8933 | 0.09613 | 0.0055694 | 0.017771 | 0.011247 | -0.00013887 | 0.019711 | -0.00059378 | -0.0012434 | 0.0018005 | 0.050729 | 0.0065368 | -0.0012774 | 0.0039692 | 0.015864 | 0.000203 | -0.027466 | 0.14648 | -0.09613 | -0.013733 | 0.15106 | 0.009155 | 0.054932 | -1.6708 | -1.5793 | -1.7303 | -1.6296 | -1.5381 | -1.6342 | -1.4923 | 121.7972 | 0.050354 | -0.10986 | 122.0444 | 121.9482 | 121.9025 | 0.15106 | 0.10528 | 120.163 | -1.6754 | -1.7258 | 120.3552 | 120.401 | 120.2591 | 0.23804 | 0.096131 | 0.24719 | 0.082397 | 0.19226 | 0.10071 | 0.24261 | 0.15106 | 122.0398 | 120.314 | -0.19226 | -1.8265 | 121.8796 | 120.2637 | 121.8658 | 120.2225
1815.9219 | 122.0718 | -121.9254 | 0.15564 | 0.0055694 | 0.018412 | 0.012102 | -0.0014207 | 0.025692 | -0.0020892 | -0.001457 | -0.0043029 | 0.053506 | 0.0065368 | -0.01025 | 0.00097837 | 0.01565 | -0.0008652 | -0.054932 | 0.17395 | -0.10071 | -0.091553 | 0.050354 | -0.086975 | -0.054932 | -1.8265 | -1.5335 | -1.7715 | -1.7578 | -1.6983 | -1.7899 | -1.6205 | 121.8246 | 0.01831 | -0.24719 | 121.9757 | 121.8704 | 121.8384 | 0.045776 | 0.013733 | 120.1538 | -1.6891 | -1.9135 | 120.2271 | 120.3049 | 120.1355 | 0.15106 | -0.018311 | 0.15106 | 0.009155 | 0.073242 | 0.013733 | 0.27466 | 0.23804 | 122.0993 | 120.3918 | -0.25635 | -1.9272 | 121.8338 | 120.1675 | 121.8704 | 120.0989
1817.625 | 122.0856 | -121.9482 | 0.15564 | -0.0020601 | 0.017771 | 0.010393 | -0.0018479 | 0.02612 | -0.0014484 | -0.0023114 | -0.0012513 | 0.052225 | 0.0071776 | -0.0085406 | 0.00033757 | 0.015009 | 0.000203 | -0.054932 | 0.1831 | -0.11902 | -0.10986 | 0.018311 | -0.086975 | -0.064087 | -1.799 | -1.5015 | -1.7303 | -1.6891 | -1.6388 | -1.7349 | -1.561 | 121.8292 | 0.027465 | -0.2655 | 121.9666 | 121.8842 | 121.8613 | 0.054932 | 0.032044 | 120.2179 | -1.6571 | -1.8448 | 120.3094 | 120.3873 | 120.2133 | 0.16937 | -0.004577 | 0.13733 | 0.009156 | 0.091553 | 0.041199 | 0.30212 | 0.22888 | 122.1313 | 120.4468 | -0.27466 | -1.886 | 121.8384 | 120.2591 | 121.8933 | 120.1492
1819.375 | 122.2 | -121.9254 | 0.11444 | -0.017319 | 0.018626 | 0.012743 | -0.0027023 | 0.023129 | -0.0020892 | -0.0020978 | -0.0073547 | 0.048807 | 0.0067504 | 0.00085881 | 0.003542 | 0.015436 | -0.0017196 | -0.013733 | 0.12817 | -0.045776 | 0.018311 | 0.20142 | 0.045776 | 0.059509 | -1.6617 | -1.593 | -1.7258 | -1.6434 | -1.5747 | -1.6525 | -1.5289 | 121.8796 | 0.013733 | -0.09613 | 122.1268 | 121.9849 | 121.9711 | 0.10528 | 0.091552 | 120.1996 | -1.7075 | -1.7578 | 120.3506 | 120.3964 | 120.2728 | 0.19684 | 0.073242 | 0.24719 | 0.064087 | 0.15106 | 0.082397 | 0.17395 | 0.13275 | 122.0535 | 120.3323 | -0.16022 | -1.8402 | 121.9437 | 120.282 | 121.9116 | 120.2637
1821.0781 | 122.2412 | -121.907 | 0.11444 | 0.013199 | 0.014994 | 0.0095382 | -0.0029159 | 0.018857 | -0.003371 | -0.00060235 | 0.0018005 | 0.049661 | 0.0088866 | -0.010677 | -0.00094423 | 0.01565 | 0.000203 | 0.004578 | 0.13275 | -0.07782 | 0.041199 | 0.24261 | 0.10071 | 0.1236 | -1.6296 | -1.5884 | -1.7487 | -1.6296 | -1.4832 | -1.5793 | -1.506 | 121.8292 | 0.01831 | -0.073242 | 122.1497 | 122.0306 | 122.0078 | 0.20142 | 0.17853 | 120.1584 | -1.7029 | -1.7441 | 120.4239 | 120.401 | 120.3278 | 0.24261 | 0.16937 | 0.32044 | 0.11902 | 0.2655 | 0.11902 | 0.21057 | 0.16022 | 122.0398 | 120.3186 | -0.19226 | -1.8631 | 121.9482 | 120.2774 | 121.9116 | 120.2774
1822.8281 | 122.2549 | -121.9208 | 0.12817 | -0.017319 | 0.017344 | 0.011461 | -0.0014207 | 0.020779 | -0.001662 | 0.00067925 | -0.0012513 | 0.050516 | 0.0088866 | -0.0017048 | 0.0043964 | 0.016718 | -0.0027878 | 0.009155 | 0.13275 | -0.050354 | 0.022888 | 0.19684 | 0.041199 | 0.073242 | -1.7487 | -1.7029 | -1.8265 | -1.7212 | -1.6388 | -1.7303 | -1.6113 | 121.8704 | 0.004577 | -0.10529 | 122.1176 | 121.994 | 121.962 | 0.1236 | 0.091553 | 120.0943 | -1.8311 | -1.8494 | 120.282 | 120.3094 | 120.1904 | 0.21515 | 0.09613 | 0.24719 | 0.073242 | 0.18768 | 0.10529 | 0.18311 | 0.1236 | 122.0535 | 120.2179 | -0.17853 | -1.9547 | 121.9437 | 120.1996 | 121.9299 | 120.1721
1824.5938 | 122.2046 | -121.9437 | 0.11902 | -0.017319 | 0.01884 | 0.011461 | -0.0029159 | 0.020138 | -0.0027302 | -0.00038875 | 0.0018005 | 0.049234 | 0.0084594 | 0.00085881 | 0.0014056 | 0.014368 | 0.0004166 | -0.050354 | 0.12817 | -0.059509 | -0.018311 | 0.13733 | 0.018311 | 0.050354 | -1.7944 | -1.7075 | -1.8356 | -1.7853 | -1.6937 | -1.7624 | -1.6296 | 121.8842 | 0.009155 | -0.13733 | 122.081 | 121.994 | 121.962 | 0.10986 | 0.07782 | 120.108 | -1.8265 | -1.9043 | 120.2499 | 120.314 | 120.1813 | 0.20599 | 0.073242 | 0.19684 | 0.041198 | 0.14191 | 0.050354 | 0.18768 | 0.12817 | 122.0718 | 120.2362 | -0.17853 | -1.9547 | 121.9254 | 120.1584 | 121.8933 | 120.1492
1826.2969 | 122.1497 | -121.9711 | 0.14648 | -0.0020601 | 0.018199 | 0.010393 | 7.473e-05 | 0.023129 | -0.0012348 | 0.00089285 | 0.0018005 | 0.051797 | 0.0067504 | -0.0044818 | -0.00073063 | 0.014582 | 0.0010574 | -0.013733 | 0.15106 | -0.086975 | -0.032043 | 0.13275 | 0.009155 | 0.027466 | -1.7349 | -1.5884 | -1.7715 | -1.7212 | -1.6388 | -1.7395 | -1.5976 | 121.8842 | 0.004578 | -0.17853 | 122.1039 | 121.9986 | 121.9803 | 0.11444 | 0.09613 | 120.1996 | -1.7349 | -1.8677 | 120.3323 | 120.3735 | 120.2316 | 0.17395 | 0.032043 | 0.21973 | 0.054932 | 0.13275 | 0.050354 | 0.23804 | 0.1831 | 122.1222 | 120.3827 | -0.23346 | -1.918 | 121.9391 | 120.2499 | 121.9574 | 120.2362
1829.4688 | 122.2687 | -121.9254 | 0.12817 | -0.0020601 | 0.01884 | 0.01082 | -0.0035569 | 0.022488 | -0.0014484 | -0.00060235 | 0.0018005 | 0.051584 | 0.0084594 | 4.214e-06 | 0.0050372 | 0.016932 | 0.0010574 | 0.013733 | 0.10986 | -0.073242 | 0.032043 | 0.19226 | 0.045776 | 0.073242 | -1.8402 | -1.8036 | -1.9089 | -1.8036 | -1.7212 | -1.8173 | -1.6937 | 121.8521 | -0.018311 | -0.096131 | 122.1176 | 121.9986 | 121.9711 | 0.14648 | 0.11902 | 120.0165 | -1.9318 | -1.9318 | 120.2042 | 120.2316 | 120.108 | 0.21515 | 0.091553 | 0.2655 | 0.10529 | 0.18768 | 0.10529 | 0.18311 | 0.10529 | 122.0352 | 120.1218 | -0.20142 | -2.037 | 121.9574 | 120.1218 | 121.9391 | 120.0851
1833.4531 | 122.2458 | -121.962 | 0.1236 | -0.0020601 | 0.015208 | 0.011034 | -0.00099327 | 0.019925 | -0.0012348 | 0.00025205 | -0.0073547 | 0.050729 | 0.0082458 | 0.001286 | 0.00033757 | 0.015223 | -0.0006516 | -0.018311 | 0.11902 | -0.059509 | 0.013733 | 0.19226 | 0.041199 | 0.059509 | -2.0508 | -1.973 | -2.1149 | -2.0233 | -1.9501 | -2.0279 | -1.9043 | 121.9025 | -0.004577 | -0.10986 | 122.1542 | 122.0215 | 122.0032 | 0.11902 | 0.10071 | 119.8471 | -2.0966 | -2.1469 | 120.0119 | 120.0577 | 119.9341 | 0.21057 | 0.086975 | 0.25177 | 0.073242 | 0.1648 | 0.091553 | 0.17853 | 0.14191 | 122.081 | 119.989 | -0.1831 | -2.2385 | 121.9757 | 119.9387 | 121.9437 | 119.9112
1839.6406 | 122.1634 | -122.0032 | 0.16937 | -0.0020601 | 0.017344 | 0.011461 | -0.0022751 | 0.021206 | -0.001662 | 3.8448e-05 | -0.0073547 | 0.052225 | 0.0063232 | -0.0061908 | -0.0035076 | 0.012659 | -1.0598e-05 | -0.07782 | 0.1831 | -0.10529 | -0.10986 | 0.059509 | -0.036621 | -0.022888 | -2.1423 | -1.8356 | -2.0691 | -2.0782 | -1.9775 | -2.0416 | -1.9226 | 121.8979 | 0.013732 | -0.27924 | 122.0627 | 121.9803 | 121.9666 | 0.082398 | 0.068665 | 119.9341 | -2.005 | -2.2476 | 120.0256 | 120.0806 | 119.9615 | 0.14648 | 0.027466 | 0.16479 | -0.004577 | 0.091553 | -0.009155 | 0.28839 | 0.23346 | 122.1863 | 120.1675 | -0.27466 | -2.2385 | 121.8933 | 119.9249 | 121.9254 | 119.8608
1841.4844 | 122.1588 | -121.994 | 0.1236 | -0.0096891 | 0.018199 | 0.011247 | -0.00035247 | 0.021847 | -0.0027302 | 0.0011066 | 0.0018005 | 0.053079 | 0.010168 | -0.0051226 | 0.00097837 | 0.014795 | -0.0019332 | -0.073242 | 0.17853 | -0.10986 | -0.10986 | 0.032043 | -0.068665 | -0.027466 | -2.2385 | -1.9821 | -2.1973 | -2.1652 | -2.1011 | -2.2156 | -2.0233 | 121.8842 | 0.054932 | -0.23346 | 122.0261 | 121.9666 | 121.9254 | 0.082397 | 0.041198 | 119.7968 | -2.1057 | -2.2888 | 119.8929 | 119.9707 | 119.7784 | 0.17395 | -0.01831 | 0.14191 | 0 | 0.096131 | 0.032044 | 0.28839 | 0.21515 | 122.1725 | 120.0119 | -0.23346 | -2.3209 | 121.8842 | 119.8288 | 121.9208 | 119.7556
1843.1875 | 122.1771 | -122.0169 | 0.14648 | -0.0020601 | 0.016062 | 0.009111 | -0.0031297 | 0.020993 | -0.006148 | -0.0020978 | -0.0073547 | 0.049447 | 0.0078186 | -0.0057636 | -0.001585 | 0.014155 | -0.0008652 | -0.086975 | 0.16479 | -0.10071 | -0.10986 | 0.041199 | -0.027466 | -0.018311 | -2.2156 | -1.9318 | -2.1698 | -2.1561 | -2.0462 | -2.1332 | -2.0096 | 121.9162 | 0.018311 | -0.25635 | 122.0581 | 121.9986 | 121.9894 | 0.082397 | 0.073242 | 119.8471 | -2.0782 | -2.3026 | 119.9707 | 120.0073 | 119.8837 | 0.16022 | 0.036621 | 0.14191 | -0.009155 | 0.1236 | 0.013733 | 0.2655 | 0.23804 | 122.1817 | 120.0851 | -0.24719 | -2.3163 | 121.907 | 119.8608 | 121.9299 | 119.8013
1844.9375 | 122.2092 | -122.0261 | 0.16022 | -0.017319 | 0.01649 | 0.01082 | -0.0016343 | 0.017361 | -0.0046528 | -0.00017515 | -0.010406 | 0.050088 | 0.0071776 | -0.008968 | 0.00055117 | 0.013086 | -0.0036422 | -0.068665 | 0.17395 | -0.091553 | -0.11902 | 0.054932 | -0.032043 | -0.013733 | -2.1881 | -1.9318 | -2.1515 | -2.1332 | -2.0096 | -2.1194 | -1.9638 | 121.9345 | 0.013733 | -0.27924 | 122.081 | 122.0123 | 121.994 | 0.07782 | 0.05951 | 119.8746 | -2.092 | -2.2934 | 120.0165 | 120.0623 | 119.9066 | 0.18768 | 0.032043 | 0.14649 | -0.027466 | 0.14191 | 0.01831 | 0.2655 | 0.21973 | 122.2 | 120.0943 | -0.25177 | -2.3117 | 121.907 | 119.8929 | 121.9574 | 119.838
1846.7031 | 122.2595 | -121.9894 | 0.1236 | 0.0055694 | 0.017131 | 0.012315 | -0.00077967 | 0.022061 | -0.00016658 | -0.0027386 | 0.0048523 | 0.052438 | 0.0099548 | -0.0057636 | 0.0024738 | 0.01565 | 0.0034072 | -0.064087 | 0.16022 | -0.086975 | -0.068665 | 0.086975 | -0.050354 | 0 | -2.179 | -2.0096 | -2.1835 | -2.1103 | -2.0233 | -2.1149 | -1.9638 | 121.9025 | 0.036621 | -0.19226 | 122.0764 | 121.9894 | 121.9391 | 0.086975 | 0.036621 | 119.8059 | -2.1332 | -2.2339 | 119.9661 | 120.0256 | 119.8746 | 0.21973 | 0.068665 | 0.17395 | 0.01831 | 0.16022 | 0.073242 | 0.24719 | 0.17395 | 122.1497 | 119.9799 | -0.21057 | -2.3071 | 121.9208 | 119.8791 | 121.9254 | 119.8105
1848.4688 | 122.2046 | -122.0078 | 0.13733 | 0.0055694 | 0.016062 | 0.010179 | -0.00099327 | 0.020566 | -0.0048664 | -0.001457 | 0.0018005 | 0.050516 | 0.0078186 | 0.0014996 | -0.00030343 | 0.014155 | -0.003856 | -0.004578 | 0.12817 | -0.07782 | -0.036621 | 0.13275 | 0.036621 | 0.027466 | -2.1378 | -1.9638 | -2.1469 | -2.124 | -2.005 | -2.092 | -2.0096 | 121.9299 | -0.009155 | -0.17395 | 122.1405 | 122.0352 | 122.0444 | 0.10529 | 0.11444 | 119.8608 | -2.1011 | -2.2614 | 120.0027 | 119.9982 | 119.9158 | 0.13733 | 0.054932 | 0.21057 | 0.041199 | 0.14191 | 0.022889 | 0.20599 | 0.18311 | 122.1359 | 120.0439 | -0.21515 | -2.2842 | 121.9711 | 119.8837 | 122.0032 | 119.87
1850.1562 | 122.168 | -122.0352 | 0.14191 | -0.017319 | 0.019053 | 0.013597 | -0.0012069 | 0.022061 | -0.00059378 | 0.00067925 | -0.0012513 | 0.051797 | 0.0071776 | -0.0044818 | 0.0033282 | 0.013941 | -0.0010788 | -0.032043 | 0.16937 | -0.09613 | -0.07782 | 0.082397 | -0.068665 | -0.013733 | -2.2614 | -2.0142 | -2.2568 | -2.2339 | -2.1652 | -2.2705 | -2.0966 | 121.9391 | 0.027466 | -0.21973 | 122.1176 | 122.0215 | 121.9666 | 0.082397 | 0.027465 | 119.7784 | -2.1561 | -2.3758 | 119.87 | 119.9387 | 119.7647 | 0.16022 | -0.013733 | 0.17853 | 0.01831 | 0.091553 | 0.022888 | 0.2655 | 0.24262 | 122.2046 | 120.0211 | -0.23804 | -2.3987 | 121.9574 | 119.8013 | 122.0032 | 119.7739
1851.8438 | 122.2321 | -122.0398 | 0.16022 | -0.0096891 | 0.013499 | 0.009111 | -0.0018479 | 0.017148 | -0.0023028 | 3.8448e-05 | -0.0073547 | 0.049875 | 0.0067504 | -0.008327 | 0.001833 | 0.014582 | 0.000203 | -0.050354 | 0.16937 | -0.091553 | -0.09613 | 0.064087 | -0.027466 | 0 | -2.2064 | -1.9638 | -2.1881 | -2.1423 | -2.0233 | -2.1423 | -1.9958 | 121.9482 | 0.009156 | -0.25635 | 122.1039 | 122.0398 | 122.0123 | 0.091553 | 0.064087 | 119.8517 | -2.124 | -2.3026 | 120.0165 | 120.0439 | 119.8975 | 0.19226 | 0.045776 | 0.15564 | -0.004577 | 0.16479 | 0.045776 | 0.26093 | 0.2243 | 122.2092 | 120.076 | -0.25177 | -2.3483 | 121.9437 | 119.8975 | 121.9894 | 119.8334
1853.5938 | 122.2641 | -122.0078 | 0.13275 | -0.0096891 | 0.018199 | 0.011034 | -0.00013887 | 0.025052 | -0.00038018 | -0.00060235 | 0.0048523 | 0.052438 | 0.0080322 | -0.0027728 | 0.0043964 | 0.016077 | -0.000438 | -0.059509 | 0.16479 | -0.07782 | -0.082397 | 0.068665 | -0.054932 | -0.004578 | -2.2614 | -2.0508 | -2.2568 | -2.1744 | -2.1194 | -2.1973 | -2.0554 | 121.9299 | 0.032044 | -0.21515 | 122.0764 | 122.0032 | 121.9528 | 0.073242 | 0.022888 | 119.751 | -2.1835 | -2.3071 | 119.8883 | 119.9524 | 119.8105 | 0.20142 | 0.059509 | 0.14649 | -0.004577 | 0.13733 | 0.082398 | 0.24261 | 0.20599 | 122.1725 | 119.957 | -0.21057 | -2.3895 | 121.9254 | 119.8334 | 121.9482 | 119.7464
1855.2812 | 122.287 | -121.994 | 0.12817 | -0.024948 | 0.01414 | 0.013597 | -0.0024887 | 0.016934 | -0.001662 | 3.8448e-05 | -0.0043029 | 0.050516 | 0.008673 | 0.0032086 | 0.0039692 | 0.016504 | 0.001912 | 0 | 0.11902 | -0.064087 | 0.009155 | 0.1831 | 0.041199 | 0.073242 | -2.1927 | -2.1515 | -2.2568 | -2.1652 | -2.0691 | -2.179 | -2.0462 | 121.9299 | -0.009155 | -0.11902 | 122.1771 | 122.0673 | 122.0352 | 0.13733 | 0.10529 | 119.7372 | -2.2797 | -2.2934 | 119.9249 | 119.9478 | 119.8151 | 0.21057 | 0.07782 | 0.24719 | 0.073242 | 0.18768 | 0.091553 | 0.18311 | 0.10529 | 122.113 | 119.8425 | -0.19226 | -2.3849 | 122.0032 | 119.8288 | 121.994 | 119.8013
1857.0312 | 122.3373 | -122.0306 | 0.11444 | -0.0020601 | 0.017771 | 0.009752 | -0.0027023 | 0.02142 | -0.0023028 | -0.0027386 | -0.0012513 | 0.052011 | 0.0080322 | 0.0036358 | -0.0017986 | 0.016932 | -1.0598e-05 | 0.013733 | 0.13275 | -0.064087 | 0.045776 | 0.25635 | 0.11444 | 0.13275 | -2.1423 | -2.1103 | -2.2797 | -2.1515 | -2.0233 | -2.1011 | -2.005 | 121.9666 | 0.01831 | -0.068665 | 122.287 | 122.1634 | 122.1451 | 0.19684 | 0.17853 | 119.751 | -2.2247 | -2.2659 | 120.0073 | 120.0256 | 119.9295 | 0.27466 | 0.17853 | 0.32044 | 0.10986 | 0.25635 | 0.12817 | 0.19684 | 0.16937 | 122.1634 | 119.9203 | -0.17853 | -2.3941 | 122.0764 | 119.8792 | 122.0444 | 119.8883
1858.7969 | 122.3282 | -122.0718 | 0.11902 | -0.0096891 | 0.016062 | 0.011888 | -0.0033433 | 0.019925 | 0.00068782 | -0.00017515 | -0.0012513 | 0.048807 | 0.0054688 | 0.0019268 | 0.00097837 | 0.013514 | 0.003621 | 0.009155 | 0.1236 | -0.068665 | 0.041199 | 0.23804 | 0.09613 | 0.11902 | -0.17853 | -0.17853 | -0.35248 | -0.20142 | -0.09613 | -0.16479 | -0.086975 | 122.0032 | 0.004577 | -0.07782 | 122.3099 | 122.1909 | 122.168 | 0.18768 | 0.16479 | 121.7194 | -0.29755 | -0.32044 | 121.9757 | 121.9849 | 121.907 | 0.2655 | 0.18768 | 0.3067 | 0.10986 | 0.25635 | 0.15106 | 0.19226 | 0.17395 | 122.1954 | 121.8933 | -0.18768 | -0.4715 | 122.113 | 121.8704 | 122.081 | 121.8933
1860.5625 | 122.3053 | -122.0764 | 0.1236 | -0.0020601 | 0.015422 | 0.011034 | -0.0020615 | 0.02142 | -0.001662 | 0.0013202 | 0.0018005 | 0.050516 | 0.0050414 | -0.0017048 | 0.002901 | 0.016291 | 0.003621 | -0.050354 | 0.14648 | -0.10986 | -0.050354 | 0.086975 | -0.032043 | -0.009155 | -0.33875 | -0.23346 | -0.40741 | -0.27008 | -0.20142 | -0.27924 | -0.14191 | 121.9666 | 0.022888 | -0.17395 | 122.1634 | 122.0673 | 122.0444 | 0.10071 | 0.07782 | 121.669 | -0.35706 | -0.39368 | 121.875 | 121.9345 | 121.7972 | 0.2655 | 0.12817 | 0.19684 | 0.059509 | 0.20599 | 0.13733 | 0.25635 | 0.17395 | 122.2229 | 121.843 | -0.23346 | -0.53101 | 122.0261 | 121.8063 | 122.0261 | 121.7377
1862.2656 | 122.3099 | -122.0306 | 0.11902 | -0.024948 | 0.017131 | 0.009752 | -0.0016343 | 0.018643 | -0.0035846 | 0.0021746 | -0.0012513 | 0.050516 | 0.0048278 | -0.0061908 | -0.0026532 | 0.01565 | 0.0010574 | 0 | 0.1236 | -0.064087 | 0.018311 | 0.20142 | 0.086975 | 0.10529 | -0.14191 | -0.10071 | -0.22888 | -0.12817 | -0.004578 | -0.10071 | 0 | 121.9666 | 0.004577 | -0.10071 | 122.2321 | 122.1359 | 122.1176 | 0.16937 | 0.15106 | 121.8018 | -0.21973 | -0.24719 | 122.0261 | 122.0306 | 121.9299 | 0.22888 | 0.12817 | 0.2655 | 0.082398 | 0.2243 | 0.10071 | 0.18768 | 0.12817 | 122.1542 | 121.9299 | -0.18311 | -0.3479 | 122.049 | 121.9025 | 122.0306 | 121.8887
1864.0156 | 122.3511 | -122.0306 | 0.10986 | -0.0020601 | 0.018199 | 0.012956 | 7.473e-05 | 0.02377 | -0.00038018 | -0.00060235 | -0.0043029 | 0.048379 | 0.0067504 | 0.00021781 | 0.0039692 | 0.015864 | 0.0023392 | 0.022888 | 0.13733 | -0.07782 | 0.018311 | 0.1831 | 0.041199 | 0.068665 | -0.18768 | -0.15106 | -0.30212 | -0.17395 | -0.082397 | -0.19684 | -0.050354 | 121.9528 | 0.027466 | -0.091552 | 122.2137 | 122.0993 | 122.0718 | 0.14649 | 0.11902 | 121.7285 | -0.26093 | -0.28381 | 121.9482 | 121.9803 | 121.8338 | 0.25177 | 0.10529 | 0.26092 | 0.096131 | 0.21973 | 0.12817 | 0.21515 | 0.15106 | 122.168 | 121.8796 | -0.18768 | -0.41199 | 122.049 | 121.8567 | 122.0535 | 121.843
1865.7031 | 122.3007 | -122.0764 | 0.11902 | -0.0020601 | 0.015208 | 0.01082 | -0.0022751 | 0.019711 | -0.0010212 | -0.0018842 | -0.0043029 | 0.048807 | 0.0091002 | -0.004909 | -0.00030343 | 0.017359 | -0.0030014 | -0.050354 | 0.13733 | -0.07782 | -0.059509 | 0.10529 | 0 | 0.045776 | -0.25635 | -0.14191 | -0.3067 | -0.21057 | -0.11902 | -0.20599 | -0.07782 | 121.9986 | 0.01831 | -0.17853 | 122.1817 | 122.1222 | 122.0764 | 0.1236 | 0.07782 | 121.7697 | -0.26093 | -0.32959 | 121.9574 | 121.9986 | 121.8704 | 0.22888 | 0.10071 | 0.18311 | 0.018311 | 0.18768 | 0.096131 | 0.21515 | 0.16479 | 122.2137 | 121.9345 | -0.19684 | -0.42572 | 122.0169 | 121.8658 | 122.0261 | 121.8201
1867.4688 | 122.2412 | -122.0993 | 0.15106 | -0.0096891 | 0.01649 | 0.0093246 | -0.0035569 | 0.022702 | 0.00026062 | -0.001457 | 0.0018005 | 0.049447 | 0.008673 | -0.0070454 | -0.0026532 | 0.013941 | 0.0023392 | -0.045776 | 0.13275 | -0.086975 | -0.073242 | 0.091553 | -0.018311 | -0.004578 | -0.22888 | -0.018311 | -0.25635 | -0.2243 | -0.10986 | -0.20599 | -0.064087 | 122.0123 | -0.018311 | -0.2243 | 122.1909 | 122.0947 | 122.081 | 0.082397 | 0.068664 | 121.843 | -0.16937 | -0.37537 | 121.9894 | 122.0352 | 121.8933 | 0.19226 | 0.050354 | 0.17853 | 0.013733 | 0.14649 | 0.032044 | 0.21973 | 0.23804 | 122.2321 | 122.081 | -0.23804 | -0.40741 | 122.0261 | 121.875 | 122.0535 | 121.8704
1869.1719 | 122.3145 | -122.0352 | 0.1236 | -0.0096891 | 0.014567 | 0.012315 | -0.0018479 | 0.020138 | -0.001662 | -0.003166 | -0.0012513 | 0.048166 | 0.0084594 | -0.0057636 | 0.0016194 | 0.013086 | 0.000203 | -0.009155 | 0.11444 | -0.045776 | 0 | 0.19684 | 0.036621 | 0.064087 | -0.16937 | -0.15106 | -0.27008 | -0.16022 | -0.086975 | -0.16937 | -0.068665 | 121.9894 | -0.009155 | -0.1236 | 122.2321 | 122.0993 | 122.0718 | 0.10986 | 0.082397 | 121.7651 | -0.27466 | -0.28381 | 121.9482 | 121.9666 | 121.8658 | 0.20142 | 0.10071 | 0.24261 | 0.045776 | 0.18311 | 0.10986 | 0.16022 | 0.11902 | 122.1497 | 121.8842 | -0.16937 | -0.39368 | 122.0352 | 121.875 | 122.0261 | 121.8658
1870.9219 | 122.2412 | -122.0764 | 0.14648 | 0.0055694 | 0.019694 | 0.009752 | -0.00077967 | 0.020566 | -0.0029438 | -0.0023114 | -0.0012513 | 0.051797 | 0.005896 | -0.016872 | 0.00097837 | 0.013514 | 0.0023392 | -0.027466 | 0.16479 | -0.10986 | -0.073242 | 0.059509 | -0.050354 | -0.018311 | -0.25177 | -0.054932 | -0.28381 | -0.23804 | -0.16937 | -0.27924 | -0.09613 | 121.9666 | 0.018311 | -0.21973 | 122.1359 | 122.0581 | 122.0261 | 0.091552 | 0.059509 | 121.7926 | -0.20142 | -0.38452 | 121.907 | 121.9803 | 121.7972 | 0.18768 | 0.004577 | 0.16937 | 0.036621 | 0.11444 | 0.045776 | 0.27466 | 0.22888 | 122.2412 | 122.0215 | -0.25635 | -0.4303 | 122.0032 | 121.8384 | 122.0489 | 121.8246
1872.625 | 122.3694 | -122.0581 | 0.13275 | -0.0020601 | 0.01649 | 0.010606 | -0.0014207 | 0.024411 | -0.00038018 | -0.00017515 | -0.0012513 | 0.050302 | 0.0091002 | -0.0040546 | 0.0016194 | 0.016077 | -0.0002244 | -0.036621 | 0.15564 | -0.09613 | -0.027466 | 0.13733 | -0.013733 | 0.050354 | -0.20142 | -0.13733 | -0.28839 | -0.16022 | -0.10071 | -0.17853 | -0.041199 | 121.962 | 0.022889 | -0.16022 | 122.1954 | 122.1085 | 122.0444 | 0.14648 | 0.082397 | 121.7697 | -0.27008 | -0.29297 | 121.9574 | 122.0169 | 121.8796 | 0.24719 | 0.10986 | 0.23346 | 0.068664 | 0.18768 | 0.12817 | 0.25177 | 0.15106 | 122.2137 | 121.9208 | -0.22888 | -0.42114 | 122.0306 | 121.8979 | 122.0215 | 121.8567
1874.3906 | 122.3557 | -122.0856 | 0.11902 | -0.0096891 | 0.016703 | 0.011247 | 0.00071573 | 0.022061 | -0.0025166 | 0.00025205 | -0.0012513 | 0.050302 | 0.007605 | 0.00043161 | 0.0050372 | 0.014582 | 0.00298 | -0.041199 | 0.15106 | -0.10071 | -0.068665 | 0.07782 | -0.036621 | 0.009155 | -0.24719 | -0.10986 | -0.27466 | -0.15564 | -0.10986 | -0.19226 | -0.045776 | 121.9849 | 0.032043 | -0.18768 | 122.1634 | 122.0947 | 122.049 | 0.10986 | 0.064087 | 121.8109 | -0.22888 | -0.27466 | 121.9757 | 122.0398 | 121.8933 | 0.22888 | 0.082397 | 0.17853 | 0.032043 | 0.1648 | 0.11902 | 0.25177 | 0.1648 | 122.2366 | 121.9757 | -0.21973 | -0.39368 | 122.0169 | 121.9299 | 122.0444 | 121.8384
1876.1562 | 122.2641 | -122.0764 | 0.16937 | -0.0020601 | 0.017131 | 0.011247 | 0.00050193 | 0.027188 | -0.00016658 | -0.0020978 | 0.0018005 | 0.052225 | 0.0088866 | -0.0034138 | -8.9634e-05 | 0.01565 | 0.0004166 | -0.013733 | 0.14648 | -0.091553 | -0.064087 | 0.09613 | -0.018311 | 0 | -0.19226 | -0.036621 | -0.26093 | -0.19684 | -0.1236 | -0.2243 | -0.082397 | 121.9849 | -0.022889 | -0.23346 | 122.1725 | 122.0764 | 122.0581 | 0.091553 | 0.073242 | 121.8155 | -0.20599 | -0.36621 | 121.9528 | 121.994 | 121.8521 | 0.17853 | 0.036621 | 0.18768 | 0.027466 | 0.13733 | 0.064087 | 0.23804 | 0.2243 | 122.2229 | 122.0398 | -0.26093 | -0.4303 | 122.0123 | 121.8796 | 122.0627 | 121.8842
1877.9219 | 122.4014 | -122.0627 | 0.11902 | -0.0020601 | 0.014994 | 0.011034 | -0.0024887 | 0.02377 | -0.0025166 | 3.8448e-05 | 0.0018005 | 0.049447 | 0.0082458 | -0.0010638 | -0.00030343 | 0.013941 | -0.0008652 | 0.004578 | 0.1236 | -0.059509 | 0.032043 | 0.2243 | 0.09613 | 0.10986 | -0.07782 | -0.07782 | -0.21057 | -0.091553 | 0.041199 | -0.050354 | 0.032043 | 122.0032 | 0.004577 | -0.086976 | 122.287 | 122.1725 | 122.1588 | 0.16937 | 0.15564 | 121.8521 | -0.19684 | -0.21057 | 122.1039 | 122.0947 | 122.0123 | 0.24261 | 0.16022 | 0.28381 | 0.091552 | 0.25177 | 0.11902 | 0.1831 | 0.13275 | 122.1863 | 121.9849 | -0.17853 | -0.32959 | 122.0947 | 121.9711 | 122.0673 | 121.9849
1879.6875 | 122.4014 | -122.0627 | 0.10529 | -0.0020601 | 0.018199 | 0.011675 | -0.0016343 | 0.025479 | -0.0012348 | 0.00025205 | -0.010406 | 0.051156 | 0.0082458 | -0.0040546 | 0.001833 | 0.013727 | 0.001271 | 0.027466 | 0.10071 | -0.059509 | 0.018311 | 0.17395 | 0.027466 | 0.059509 | -0.16937 | -0.14648 | -0.25177 | -0.11902 | -0.050354 | -0.14648 | -0.009155 | 122.0032 | -0.004578 | -0.086975 | 122.2366 | 122.1222 | 122.0901 | 0.11902 | 0.086975 | 121.8109 | -0.25177 | -0.22431 | 122.0123 | 122.0535 | 121.9162 | 0.24261 | 0.10529 | 0.23346 | 0.07782 | 0.20142 | 0.13275 | 0.16022 | 0.10529 | 122.1634 | 121.9162 | -0.16479 | -0.35706 | 122.081 | 121.9437 | 122.0901 | 121.8933
1881.4375 | 122.3785 | -122.0673 | 0.15106 | -0.0096891 | 0.019908 | 0.010393 | -0.0027023 | 0.021206 | -0.00508 | -0.00060235 | -0.0043029 | 0.052652 | 0.0073914 | -0.0010638 | 0.00012397 | 0.013727 | 0.000203 | -0.004578 | 0.11444 | -0.064087 | 0.036621 | 0.20142 | 0.07782 | 0.091553 | -0.10071 | -0.054932 | -0.21515 | -0.073242 | 0.022888 | -0.054932 | 0.036621 | 122.0032 | -0.036621 | -0.11444 | 122.2687 | 122.1588 | 122.1451 | 0.15564 | 0.14191 | 121.8521 | -0.20599 | -0.2243 | 122.0901 | 122.1039 | 122.0123 | 0.25177 | 0.16022 | 0.2655 | 0.10071 | 0.23804 | 0.14191 | 0.17853 | 0.16022 | 122.1817 | 122.0123 | -0.21515 | -0.36621 | 122.1039 | 121.994 | 122.0627 | 121.9666
1883.1406 | 122.4014 | -122.081 | 0.1236 | -0.0020601 | 0.01948 | 0.014452 | -0.00099327 | 0.02142 | -0.0018756 | -0.00017515 | 0.0048523 | 0.050943 | 0.0067504 | -0.0044818 | 0.0037556 | 0.015009 | -0.0042832 | 0.013733 | 0.12817 | -0.07782 | 0.013733 | 0.16937 | 0.013733 | 0.059509 | -0.15564 | -0.10986 | -0.25177 | -0.1236 | -0.050354 | -0.14648 | 0 | 122.0032 | 0.004578 | -0.10986 | 122.2504 | 122.1405 | 122.0947 | 0.13733 | 0.091553 | 121.8292 | -0.23346 | -0.24719 | 122.0306 | 122.081 | 121.9345 | 0.25177 | 0.10529 | 0.24719 | 0.091553 | 0.20142 | 0.12817 | 0.20599 | 0.14191 | 122.2092 | 121.9711 | -0.20142 | -0.37537 | 122.0947 | 121.9574 | 122.0947 | 121.9254
1884.8906 | 122.3785 | -122.0947 | 0.11902 | -0.0096891 | 0.016276 | 0.013597 | -0.0041977 | 0.019711 | -0.0031574 | 0.0023882 | -0.0012513 | 0.049234 | 0.008673 | 0.0042768 | -0.002226 | 0.01565 | -0.0002244 | -0.045776 | 0.14191 | -0.086975 | -0.036621 | 0.14648 | 0.032043 | 0.068665 | -0.17853 | -0.073242 | -0.23804 | -0.10529 | -0.013733 | -0.086975 | 0.027466 | 122.0078 | 0.022888 | -0.15564 | 122.2412 | 122.1634 | 122.1268 | 0.15564 | 0.11902 | 121.8567 | -0.19226 | -0.22431 | 122.081 | 122.1222 | 122.0078 | 0.2655 | 0.15106 | 0.23346 | 0.050354 | 0.2243 | 0.13275 | 0.22888 | 0.16479 | 122.2366 | 122.0215 | -0.20599 | -0.35706 | 122.0581 | 121.9894 | 122.049 | 121.9162
1886.5781 | 122.4152 | -122.1222 | 0.1236 | -0.0096891 | 0.017344 | 0.010179 | -0.0048385 | 0.022915 | -0.0027302 | -0.0023114 | -0.0043029 | 0.050729 | 0.0063232 | -0.0023456 | -0.00094423 | 0.015864 | 0.001912 | 0.009155 | 0.10986 | -0.086975 | 0.032043 | 0.21973 | 0.09613 | 0.10529 | -0.041199 | -0.050354 | -0.17395 | -0.050354 | 0.07782 | -0.027466 | 0.068665 | 122.0352 | -0.013733 | -0.091553 | 122.3419 | 122.2275 | 122.2183 | 0.19226 | 0.1831 | 121.9482 | -0.17395 | -0.17395 | 122.2 | 122.1909 | 122.0947 | 0.24261 | 0.14648 | 0.3067 | 0.11902 | 0.25177 | 0.1236 | 0.19684 | 0.1236 | 122.2321 | 122.0718 | -0.21057 | -0.29755 | 122.1542 | 122.0718 | 122.1313 | 122.081
1888.2656 | 122.3236 | -122.1222 | 0.14191 | -0.017319 | 0.018199 | 0.014024 | 0.00028833 | 0.023984 | -0.0018756 | 0.00089285 | -0.0073547 | 0.052011 | 0.007605 | -0.013454 | 0.001192 | 0.0133 | 0.0025528 | -0.032043 | 0.14648 | -0.10986 | -0.064087 | 0.091553 | -0.013733 | 0.013733 | -0.13733 | 0.004578 | -0.20599 | -0.11902 | -0.050354 | -0.13733 | 0.004578 | 122.0123 | 0.004577 | -0.20599 | 122.2137 | 122.1359 | 122.1085 | 0.1236 | 0.09613 | 121.9162 | -0.13733 | -0.26093 | 122.0718 | 122.1268 | 121.9849 | 0.21057 | 0.068665 | 0.20142 | 0.045776 | 0.15564 | 0.086975 | 0.25635 | 0.21057 | 122.2687 | 122.1268 | -0.25177 | -0.3479 | 122.0581 | 122.0032 | 122.0901 | 121.9849
1890.0312 | 122.3465 | -122.1313 | 0.13733 | -0.0096891 | 0.018199 | 0.011888 | 0.00071573 | 0.022915 | -0.0018756 | 0.0015338 | -0.0043029 | 0.049661 | 0.008673 | -0.0081134 | 0.00055117 | 0.014582 | -0.0010788 | -0.027466 | 0.14191 | -0.07782 | -0.045776 | 0.11444 | -0.004578 | -0.013733 | -0.13275 | -0.013733 | -0.21057 | -0.11444 | -0.036621 | -0.1236 | -0.004578 | 122.0535 | 0.004578 | -0.18311 | 122.2458 | 122.1176 | 122.1268 | 0.064087 | 0.073242 | 121.9208 | -0.15106 | -0.25177 | 122.0947 | 122.1268 | 122.0078 | 0.20599 | 0.086975 | 0.19226 | 0.032044 | 0.17395 | 0.09613 | 0.21973 | 0.19684 | 122.2733 | 122.1176 | -0.21515 | -0.3479 | 122.0856 | 122.0169 | 122.1039 | 121.9986
1891.7969 | 122.4655 | -122.1039 | 0.10529 | -0.0020601 | 0.015422 | 0.010179 | -0.0020615 | 0.018429 | -0.0023028 | -0.00060235 | -0.0012513 | 0.049234 | 0.0084594 | 0.0049176 | 0.00033757 | 0.014582 | 0.0014846 | 0.013733 | 0.10986 | -0.082397 | 0.027466 | 0.2243 | 0.09613 | 0.12817 | -0.041199 | -0.041199 | -0.19684 | -0.059509 | 0.054932 | -0.027466 | 0.064087 | 122.0215 | 0.004577 | -0.07782 | 122.3282 | 122.2321 | 122.2 | 0.21057 | 0.17853 | 121.907 | -0.14649 | -0.16479 | 122.1588 | 122.168 | 122.0764 | 0.26093 | 0.16937 | 0.3067 | 0.10986 | 0.25177 | 0.13733 | 0.19226 | 0.15564 | 122.2137 | 122.0627 | -0.18768 | -0.30212 | 122.1313 | 122.0444 | 122.1176 | 122.0627
1893.5469 | 122.3785 | -122.1268 | 0.1236 | -0.017319 | 0.016917 | 0.0095382 | -0.0022751 | 0.019925 | -0.0029438 | -0.0016706 | -0.0043029 | 0.04902 | 0.0063232 | -0.0027728 | -0.00051703 | 0.015223 | -0.0010788 | -0.059509 | 0.11444 | -0.07782 | -0.045776 | 0.10986 | 0 | 0.036621 | -0.19226 | -0.082397 | -0.23346 | -0.13733 | -0.059509 | -0.13275 | 0 | 122.0489 | -0.009155 | -0.16937 | 122.2366 | 122.1634 | 122.1268 | 0.11444 | 0.07782 | 121.8933 | -0.20599 | -0.26093 | 122.0673 | 122.1268 | 121.994 | 0.23346 | 0.10071 | 0.18768 | 0.032044 | 0.17395 | 0.09613 | 0.19226 | 0.15106 | 122.2412 | 122.0444 | -0.20142 | -0.35706 | 122.081 | 121.9894 | 122.0673 | 121.9345
1895.25 | 122.438 | -122.1222 | 0.10986 | 0.0055694 | 0.017344 | 0.010179 | -0.0027023 | 0.02142 | -0.0014484 | 0.0015338 | -0.0012513 | 0.04902 | 0.0067504 | -0.00020939 | 0.0037556 | 0.015009 | -0.000438 | 0 | 0.09613 | -0.041199 | 0.022888 | 0.1831 | 0.045776 | 0.068665 | -0.14191 | -0.13733 | -0.24261 | -0.10986 | -0.041199 | -0.13733 | 0 | 122.081 | -0.013733 | -0.086975 | 122.3053 | 122.1909 | 122.168 | 0.10986 | 0.086975 | 121.8796 | -0.24719 | -0.21973 | 122.081 | 122.1222 | 121.9849 | 0.24261 | 0.10529 | 0.2243 | 0.064087 | 0.20142 | 0.13275 | 0.13733 | 0.10529 | 122.2183 | 121.9849 | -0.15106 | -0.35248 | 122.1451 | 122.0123 | 122.1222 | 121.9803
1897 | 122.3373 | -122.1817 | 0.15106 | -0.0096891 | 0.017344 | 0.011461 | -0.0012069 | 0.020138 | -0.0048664 | -0.00060235 | -0.0043029 | 0.050943 | 0.0088866 | -0.0076862 | 0.00097837 | 0.013941 | -0.0019332 | -0.073242 | 0.15564 | -0.10071 | -0.11444 | 0.036621 | -0.054932 | -0.022888 | -0.21515 | -0.013733 | -0.20142 | -0.16937 | -0.054932 | -0.14648 | -0.018311 | 122.081 | 0.004578 | -0.2655 | 122.2183 | 122.1588 | 122.1268 | 0.07782 | 0.045776 | 121.9803 | -0.16479 | -0.32044 | 122.1268 | 122.1634 | 122.0352 | 0.18311 | 0.054932 | 0.13733 | -0.013733 | 0.14648 | 0.032043 | 0.25635 | 0.18768 | 122.3373 | 122.168 | -0.25177 | -0.35248 | 122.0673 | 122.0123 | 122.1085 | 121.9666
1898.6875 | 122.3785 | -122.1359 | 0.14191 | -0.0020601 | 0.017131 | 0.012315 | -0.0014207 | 0.026761 | -0.001662 | -0.00081595 | -0.0012513 | 0.054147 | 0.005255 | -0.0076862 | 0.002901 | 0.013727 | 0.0004166 | -0.022888 | 0.15106 | -0.091553 | -0.032043 | 0.11444 | -0.004578 | 0.022888 | -0.13275 | -0.022888 | -0.20142 | -0.11444 | -0.050354 | -0.13733 | -0.022888 | 122.0444 | 0.009155 | -0.17395 | 122.2504 | 122.1588 | 122.1313 | 0.11444 | 0.086975 | 121.9345 | -0.16479 | -0.25635 | 122.0856 | 122.113 | 121.9986 | 0.17853 | 0.064087 | 0.20599 | 0.05951 | 0.15106 | 0.086975 | 0.24261 | 0.17853 | 122.287 | 122.113 | -0.23346 | -0.34332 | 122.1039 | 122.0215 | 122.113 | 122.0032
1900.4375 | 122.3648 | -122.1588 | 0.15106 | -0.0020601 | 0.016703 | 0.011034 | -0.00077967 | 0.022061 | -0.0020892 | 0.00067925 | -0.010406 | 0.050088 | 0.008673 | -0.007259 | -0.0011578 | 0.014368 | 0.0008438 | -0.073242 | 0.14191 | -0.086975 | -0.10529 | 0.050354 | -0.032043 | -0.009155 | -0.22888 | 0.004578 | -0.18768 | -0.15564 | -0.036621 | -0.13733 | 0.004578 | 122.0718 | -0.009155 | -0.25635 | 122.2092 | 122.1497 | 122.1268 | 0.07782 | 0.054932 | 121.9711 | -0.14648 | -0.3067 | 122.1222 | 122.1634 | 122.0215 | 0.19226 | 0.050354 | 0.13733 | -0.018311 | 0.15106 | 0.032043 | 0.22888 | 0.19226 | 122.3007 | 122.1634 | -0.23804 | -0.33874 | 122.0535 | 122.0032 | 122.0856 | 121.9299
1902.1562 | 122.4335 | -122.1313 | 0.11902 | -0.0020601 | 0.017131 | 0.011461 | -0.0018479 | 0.025265 | -0.0040118 | -0.0023114 | -0.0043029 | 0.05137 | 0.0084594 | -0.0046954 | -0.001585 | 0.013941 | -0.0012924 | -0.004578 | 0.11444 | -0.064087 | 0.036621 | 0.21973 | 0.091553 | 0.10529 | -0.068665 | -0.059509 | -0.20142 | -0.068665 | 0.050354 | -0.027466 | 0.041199 | 122.0673 | -0.004578 | -0.082398 | 122.3511 | 122.2366 | 122.2229 | 0.16937 | 0.15564 | 121.9299 | -0.17853 | -0.18768 | 122.1817 | 122.1725 | 122.1039 | 0.24262 | 0.17395 | 0.28381 | 0.10071 | 0.25177 | 0.13275 | 0.17853 | 0.14191 | 122.2458 | 122.0718 | -0.18311 | -0.32044 | 122.168 | 122.0627 | 122.1268 | 122.0627
1903.875 | 122.3511 | -122.168 | 0.14191 | -0.0020601 | 0.016703 | 0.011034 | -0.0027023 | 0.017788 | -0.00080758 | 0.00067925 | -0.0012513 | 0.051584 | 0.007605 | -0.0091816 | -0.0011578 | 0.014368 | -0.0023606 | 0 | 0.12817 | -0.07782 | -0.022888 | 0.15106 | 0.041199 | 0.045776 | -0.16937 | -0.022888 | -0.20599 | -0.16479 | -0.059509 | -0.14648 | -0.032043 | 122.0901 | -0.013733 | -0.16479 | 122.319 | 122.2137 | 122.2092 | 0.1236 | 0.11902 | 121.962 | -0.16479 | -0.3067 | 122.1085 | 122.1359 | 122.0215 | 0.17395 | 0.05951 | 0.22888 | 0.054932 | 0.14649 | 0.041199 | 0.20599 | 0.18311 | 122.2961 | 122.1451 | -0.21973 | -0.3479 | 122.1451 | 122.0032 | 122.168 | 121.9986
1905.6406 | 122.3236 | -122.168 | 0.15106 | -0.0020601 | 0.01884 | 0.012529 | -0.0022751 | 0.021634 | -0.0031574 | 0.0015338 | -0.0012513 | 0.052438 | 0.0080322 | -0.008327 | 0.003542 | 0.014368 | 0.0040482 | -0.041199 | 0.14648 | -0.07782 | -0.09613 | 0.082397 | -0.073242 | -0.036621 | -0.29297 | -0.073242 | -0.2655 | -0.23346 | -0.16479 | -0.27008 | -0.11444 | 122.0901 | -0.004578 | -0.24719 | 122.2504 | 122.1313 | 122.0947 | 0.041199 | 0.004578 | 121.9025 | -0.2243 | -0.38452 | 122.0032 | 122.0535 | 121.8979 | 0.15106 | -0.004578 | 0.16022 | -0.01831 | 0.10071 | 0.032044 | 0.2243 | 0.19226 | 122.3145 | 122.0947 | -0.22888 | -0.41656 | 122.0718 | 121.9345 | 122.1268 | 121.875
1907.3906 | 122.3373 | -122.1771 | 0.11902 | 0.0055694 | 0.016703 | 0.012315 | -0.0014207 | 0.021847 | -0.0037982 | 0.0011066 | 0.0048523 | 0.053079 | 0.0097412 | -0.00020939 | 0.0022602 | 0.016504 | 0.0021256 | -0.054932 | 0.16022 | -0.11902 | -0.13275 | 0.027466 | -0.07782 | -0.036621 | -0.3067 | -0.059509 | -0.28381 | -0.25177 | -0.1831 | -0.27008 | -0.1236 | 122.0581 | 0.041198 | -0.25177 | 122.2046 | 122.1405 | 122.0993 | 0.082398 | 0.041199 | 121.8933 | -0.17853 | -0.37079 | 121.994 | 122.0535 | 121.907 | 0.16022 | 0.013732 | 0.14649 | -0.013732 | 0.10071 | 0.032043 | 0.27924 | 0.2243 | 122.3373 | 122.1176 | -0.23804 | -0.40283 | 122.0444 | 121.9254 | 122.1222 | 121.8704
1909.0938 | 122.3328 | -122.2183 | 0.14191 | -0.0096891 | 0.017985 | 0.0082566 | -0.0027023 | 0.023984 | -0.0042254 | 0.0013202 | -0.0073547 | 0.048807 | 0.005255 | -0.0044818 | -0.0026532 | 0.011164 | 0.0034072 | -0.10071 | 0.16479 | -0.11444 | -0.11444 | 0.045776 | -0.036621 | -0.013733 | -0.26093 | -0.036621 | -0.21973 | -0.19226 | -0.10071 | -0.19226 | -0.054932 | 122.1039 | 0.022888 | -0.25635 | 122.2641 | 122.2046 | 122.1817 | 0.10071 | 0.07782 | 121.9986 | -0.17853 | -0.33417 | 122.1176 | 122.1634 | 122.0261 | 0.16479 | 0.027466 | 0.16022 | 0 | 0.11902 | 0.027466 | 0.27924 | 0.18311 | 122.3831 | 122.1817 | -0.25635 | -0.36163 | 122.1039 | 122.0261 | 122.1176 | 121.9574
1910.8438 | 122.3236 | -122.1588 | 0.14191 | 0.0055694 | 0.017985 | 0.011034 | 0.0024245 | 0.022915 | -0.0040118 | 0.00046565 | -0.0012513 | 0.052438 | 0.0061096 | -0.0042682 | 0.00033757 | 0.013727 | 0.0010574 | -0.045776 | 0.13733 | -0.10986 | -0.09613 | 0.059509 | -0.07782 | -0.036621 | -0.30212 | -0.064087 | -0.25635 | -0.25177 | -0.19226 | -0.28839 | -0.11902 | 122.0489 | -0.004578 | -0.23804 | 122.2183 | 122.1222 | 122.081 | 0.073242 | 0.032043 | 121.9025 | -0.20599 | -0.39368 | 121.9666 | 122.0398 | 121.8704 | 0.13733 | -0.032043 | 0.16937 | 0.013733 | 0.064087 | 0.004578 | 0.24719 | 0.19226 | 122.2961 | 122.0947 | -0.25177 | -0.39826 | 122.0627 | 121.907 | 122.113 | 121.8567
1912.6094 | 122.406 | -122.1725 | 0.13275 | -0.0020601 | 0.017131 | 0.011034 | -0.0033433 | 0.024624 | -0.0014484 | -0.001457 | -0.0012513 | 0.052865 | 0.0073914 | -0.0076862 | 0.00033757 | 0.013086 | 0.0010574 | -0.027466 | 0.14648 | -0.07782 | -0.045776 | 0.11902 | -0.004578 | 0.022888 | -0.19684 | -0.050354 | -0.25635 | -0.14648 | -0.068665 | -0.17853 | -0.022888 | 122.0947 | 0.013733 | -0.17853 | 122.2916 | 122.1954 | 122.168 | 0.10071 | 0.073242 | 121.9162 | -0.18311 | -0.27924 | 122.1039 | 122.1497 | 121.994 | 0.23346 | 0.07782 | 0.19684 | 0.032044 | 0.18768 | 0.10986 | 0.2243 | 0.20599 | 122.319 | 122.1222 | -0.21057 | -0.3891 | 122.1268 | 122.0261 | 122.1451 | 121.9757
1914.375 | 122.4426 | -122.1771 | 0.11902 | -0.0020601 | 0.015635 | 0.01082 | -0.0022751 | 0.017361 | -0.0031574 | 3.8448e-05 | -0.0043029 | 0.049875 | 0.0073914 | -0.0046954 | 0.00076477 | 0.015436 | -0.0012924 | -0.059509 | 0.11902 | -0.059509 | -0.054932 | 0.11444 | 0.004578 | 0.050354 | -0.21973 | -0.091553 | -0.26093 | -0.15106 | -0.059509 | -0.13275 | -0.036621 | 122.1176 | 0 | -0.17395 | 122.2916 | 122.2275 | 122.1817 | 0.10986 | 0.064087 | 121.9162 | -0.21057 | -0.27008 | 122.1176 | 122.1405 | 122.0444 | 0.2243 | 0.12817 | 0.17395 | 0.004577 | 0.20142 | 0.10986 | 0.17853 | 0.16937 | 122.2961 | 122.0856 | -0.17853 | -0.37994 | 122.1222 | 122.0261 | 122.1176 | 121.9574
1916.0625 | 122.4792 | -122.1405 | 0.10071 | -0.0020601 | 0.019053 | 0.013597 | -0.00099327 | 0.02142 | -0.0012348 | 0.0017474 | -0.0012513 | 0.049661 | 0.0073914 | -0.00555 | 0.00461 | 0.016504 | 0.0038346 | 0.022888 | 0.10986 | -0.07782 | 0.009155 | 0.16937 | 0.045776 | 0.07782 | -0.16937 | -0.13733 | -0.28839 | -0.1236 | -0.045776 | -0.14648 | -0.022888 | 122.0627 | 0.009155 | -0.091553 | 122.3099 | 122.2183 | 122.1863 | 0.15564 | 0.1236 | 121.8521 | -0.23804 | -0.2243 | 122.0947 | 122.1176 | 121.994 | 0.2655 | 0.14191 | 0.24719 | 0.086975 | 0.24262 | 0.1648 | 0.18768 | 0.15106 | 122.2504 | 122.0032 | -0.17853 | -0.3891 | 122.1497 | 122.0169 | 122.1634 | 121.9711
1917.8125 | 122.3694 | -122.2275 | 0.16022 | 0.0055694 | 0.017344 | 0.011888 | -0.00013887 | 0.021206 | -0.001662 | 0.00067925 | 0.0018005 | 0.052438 | 0.0078186 | -0.0061908 | -0.00094423 | 0.014582 | -0.0027878 | -0.059509 | 0.16022 | -0.10071 | -0.10529 | 0.022888 | -0.086975 | -0.032043 | -0.31128 | -0.082397 | -0.30212 | -0.23804 | -0.18768 | -0.29755 | -0.10986 | 122.1268 | 0 | -0.2655 | 122.2504 | 122.1954 | 122.1405 | 0.068665 | 0.013733 | 121.9254 | -0.24261 | -0.39825 | 122.0398 | 122.1176 | 121.9299 | 0.19226 | 0.004578 | 0.1236 | -0.004578 | 0.11444 | 0.064087 | 0.26093 | 0.21973 | 122.3877 | 122.1451 | -0.26093 | -0.46234 | 122.1222 | 121.9894 | 122.168 | 121.9162
1919.5781 | 122.3602 | -122.2183 | 0.15564 | -0.0020601 | 0.017558 | 0.0082566 | -0.0022751 | 0.019284 | -0.0042254 | -0.0012434 | -0.0043029 | 0.050943 | 0.0054688 | -0.0034138 | -0.00094423 | 0.015009 | -0.0012924 | -0.09613 | 0.16022 | -0.12817 | -0.12817 | 0.041199 | -0.036621 | -0.013733 | -0.25177 | -0.013733 | -0.22888 | -0.21057 | -0.1236 | -0.21057 | -0.068665 | 122.0901 | 0.004577 | -0.28381 | 122.2595 | 122.2046 | 122.1817 | 0.11444 | 0.091553 | 121.9894 | -0.16937 | -0.36621 | 122.0947 | 122.1497 | 122.0078 | 0.16022 | 0.018311 | 0.16937 | 0 | 0.10529 | 0.018311 | 0.28839 | 0.21515 | 122.3785 | 122.2046 | -0.28381 | -0.38452 | 122.0901 | 122.0078 | 122.1222 | 121.9666
1921.3438 | 122.4518 | -122.1909 | 0.11444 | -0.017319 | 0.018412 | 0.011675 | -0.0033433 | 0.023129 | -0.0014484 | -0.00060235 | -0.0043029 | 0.047098 | 0.0097412 | -0.0068316 | 0.0026874 | 0.016504 | -0.000438 | -0.009155 | 0.10529 | -0.064087 | -0.013733 | 0.17853 | 0.032043 | 0.050354 | -0.20599 | -0.13733 | -0.28381 | -0.19226 | -0.10071 | -0.18768 | -0.068665 | 122.1268 | -0.009155 | -0.12817 | 122.3694 | 122.2412 | 122.2229 | 0.11444 | 0.09613 | 121.907 | -0.25177 | -0.3067 | 122.0901 | 122.1222 | 122.0032 | 0.21515 | 0.09613 | 0.24261 | 0.050354 | 0.1831 | 0.091552 | 0.16937 | 0.14648 | 122.2961 | 122.0535 | -0.17853 | -0.39825 | 122.1771 | 121.9986 | 122.1817 | 121.9849
1923.0312 | 122.4976 | -122.1909 | 0.12817 | -0.0020601 | 0.015422 | 0.0099656 | -0.0020615 | 0.019711 | -0.0020892 | -0.001457 | 0.0018005 | 0.049875 | 0.0067504 | -0.0068316 | 0.0014056 | 0.014368 | 0.0027664 | -0.036621 | 0.14191 | -0.082397 | -0.027466 | 0.12817 | 0.027466 | 0.059509 | -0.21515 | -0.13275 | -0.28381 | -0.16479 | -0.064087 | -0.13733 | -0.027466 | 122.1085 | 0.013733 | -0.15564 | 122.319 | 122.2504 | 122.2183 | 0.14191 | 0.10986 | 121.907 | -0.26093 | -0.29297 | 122.1268 | 122.1634 | 122.0535 | 0.25635 | 0.14648 | 0.21057 | 0.054931 | 0.21973 | 0.11902 | 0.2243 | 0.15106 | 122.3328 | 122.0581 | -0.21057 | -0.41199 | 122.1634 | 122.0261 | 122.1542 | 121.9757
1924.7969 | 122.3785 | -122.2412 | 0.14648 | 0.0055694 | 0.017771 | 0.009752 | -0.0014207 | 0.021206 | -0.0020892 | 0.0030292 | -0.0012513 | 0.052652 | 0.0071776 | -0.0076862 | -8.9634e-05 | 0.016291 | -0.0036422 | -0.027466 | 0.13275 | -0.082397 | -0.073242 | 0.09613 | -0.013733 | 0.004578 | -0.24719 | -0.054932 | -0.2655 | -0.2243 | -0.12817 | -0.21515 | -0.09613 | 122.1588 | -0.013733 | -0.21973 | 122.3373 | 122.2458 | 122.2275 | 0.086975 | 0.068664 | 121.9757 | -0.20142 | -0.37079 | 122.113 | 122.1451 | 122.0261 | 0.16937 | 0.050354 | 0.17853 | 0.009155 | 0.13733 | 0.041199 | 0.21515 | 0.21057 | 122.374 | 122.1863 | -0.22888 | -0.41199 | 122.168 | 122.0169 | 122.2137 | 121.994
1926.5625 | 122.4426 | -122.1954 | 0.12817 | -0.0096891 | 0.018199 | 0.011888 | -0.0018479 | 0.025052 | -0.0025166 | 0.0013202 | 0.0018005 | 0.051156 | 0.0065368 | -0.0044818 | 0.00461 | 0.015223 | 0.0051162 | -0.059509 | 0.16022 | -0.1236 | -0.086975 | 0.050354 | -0.068665 | -0.027466 | -0.27466 | -0.11444 | -0.31128 | -0.21973 | -0.17395 | -0.24719 | -0.11444 | 122.0718 | 0.032043 | -0.21515 | 122.2458 | 122.168 | 122.1268 | 0.09613 | 0.054931 | 121.8842 | -0.24262 | -0.3479 | 122.0215 | 122.081 | 121.9482 | 0.19684 | 0.064087 | 0.17395 | 0.036621 | 0.13733 | 0.091552 | 0.28381 | 0.19684 | 122.3557 | 122.081 | -0.25177 | -0.43945 | 122.1085 | 121.9757 | 122.1359 | 121.9208
1928.25 | 122.4106 | -122.2183 | 0.14191 | -0.0020601 | 0.017131 | 0.010606 | -0.0022751 | 0.023129 | -0.001662 | -0.00060235 | 0.0018005 | 0.054361 | 0.0088866 | -0.0017048 | 0.0022602 | 0.015223 | 0.0040482 | -0.068665 | 0.17395 | -0.09613 | -0.12817 | 0.045776 | -0.07782 | -0.036621 | -0.27924 | -0.07782 | -0.27924 | -0.2243 | -0.17395 | -0.26093 | -0.10529 | 122.1222 | 0.032043 | -0.27008 | 122.2641 | 122.1817 | 122.1405 | 0.059509 | 0.01831 | 121.9391 | -0.21973 | -0.36621 | 122.0444 | 122.113 | 121.9574 | 0.17395 | 0.018311 | 0.14191 | -0.032044 | 0.10529 | 0.054932 | 0.27008 | 0.20142 | 122.3923 | 122.1405 | -0.23804 | -0.42114 | 122.0901 | 121.994 | 122.1497 | 121.9391
1930 | 122.4014 | -122.2229 | 0.14191 | 0.013199 | 0.017558 | 0.012102 | -0.0022751 | 0.020352 | -0.001662 | -0.003166 | -0.0012513 | 0.050302 | 0.0088866 | -0.0064044 | -0.00094423 | 0.016077 | 0.000203 | -0.027466 | 0.15106 | -0.073242 | -0.059509 | 0.10986 | 0.018311 | 0.027466 | -0.1831 | -0.027466 | -0.21973 | -0.16937 | -0.07782 | -0.17395 | -0.068665 | 122.1497 | 0.009155 | -0.20142 | 122.3328 | 122.2504 | 122.2412 | 0.10071 | 0.091553 | 122.0032 | -0.16937 | -0.31128 | 122.1451 | 122.1542 | 122.0489 | 0.15106 | 0.045777 | 0.18311 | 0.013733 | 0.14191 | 0.050354 | 0.2243 | 0.19226 | 122.374 | 122.1954 | -0.21515 | -0.36163 | 122.1634 | 122.0535 | 122.1954 | 122.0398
1931.7031 | 122.4518 | -122.2183 | 0.13275 | -0.0020601 | 0.019267 | 0.010393 | -0.00056607 | 0.020138 | -0.00016658 | -0.001457 | -0.0043029 | 0.052652 | 0.0078186 | -0.011531 | 0.0031146 | 0.014795 | 0.0014846 | -0.013733 | 0.14191 | -0.09613 | -0.050354 | 0.10986 | -0.009155 | 0.018311 | -0.15564 | -0.050354 | -0.23346 | -0.14191 | -0.050354 | -0.16937 | -0.022888 | 122.1222 | 0.009156 | -0.18311 | 122.3282 | 122.2366 | 122.2092 | 0.11444 | 0.086975 | 121.9849 | -0.18311 | -0.27466 | 122.168 | 122.1954 | 122.049 | 0.21057 | 0.064086 | 0.20599 | 0.045776 | 0.1831 | 0.091552 | 0.23804 | 0.1831 | 122.3602 | 122.168 | -0.22888 | -0.36621 | 122.168 | 122.0764 | 122.2046 | 122.0627
1933.3906 | 122.406 | -122.2229 | 0.16022 | -0.017319 | 0.019908 | 0.012956 | -0.00077967 | 0.022275 | -0.0031574 | -0.00017515 | 0.0018005 | 0.050943 | 0.0082458 | -0.006618 | 0.00012397 | 0.014155 | 0.0006302 | -0.032043 | 0.13733 | -0.09613 | -0.064087 | 0.091553 | -0.032043 | 0 | -0.17853 | -0.045776 | -0.23804 | -0.17853 | -0.10071 | -0.21515 | -0.059509 | 122.1268 | -0.022888 | -0.2243 | 122.3145 | 122.2229 | 122.1909 | 0.09613 | 0.064087 | 121.9849 | -0.20599 | -0.33874 | 122.1222 | 122.1634 | 122.0078 | 0.17853 | 0.022888 | 0.18768 | 0.032043 | 0.13733 | 0.059509 | 0.23346 | 0.19226 | 122.3602 | 122.1771 | -0.25635 | -0.39825 | 122.1588 | 122.0444 | 122.1909 | 122.0444
1935.0938 | 122.5342 | -122.2046 | 0.11902 | 0.0055694 | 0.017344 | 0.009752 | -0.0033433 | 0.022915 | -0.0035846 | -0.0016706 | -0.0012513 | 0.04902 | 0.0056824 | 0.0010724 | 0.0014056 | 0.014795 | 0.0021256 | -0.041199 | 0.1236 | -0.082397 | -0.036621 | 0.13733 | 0.041199 | 0.064087 | -0.13733 | -0.054932 | -0.21057 | -0.07782 | 0.022888 | -0.050354 | 0.054932 | 122.1222 | 0.004577 | -0.15564 | 122.3419 | 122.2687 | 122.2458 | 0.14648 | 0.1236 | 121.994 | -0.17395 | -0.19684 | 122.2275 | 122.2595 | 122.1542 | 0.2655 | 0.16022 | 0.21973 | 0.045776 | 0.23346 | 0.13275 | 0.20599 | 0.15564 | 122.3282 | 122.1497 | -0.20142 | -0.32959 | 122.168 | 122.1268 | 122.1634 | 122.0673
1936.8125 | 122.5159 | -122.2092 | 0.1236 | 0.0055694 | 0.016917 | 0.011247 | -0.0018479 | 0.020566 | -0.0020892 | 0.0032428 | -0.0012513 | 0.049875 | 0.0065368 | 0.0019268 | 0.00012397 | 0.015009 | 0.0027664 | -0.045776 | 0.11902 | -0.064087 | -0.041199 | 0.1236 | 0.013733 | 0.064087 | -0.15564 | -0.054932 | -0.21515 | -0.09613 | -0.004578 | -0.091553 | 0.032043 | 122.1451 | -0.004577 | -0.16479 | 122.3328 | 122.2733 | 122.2229 | 0.12817 | 0.07782 | 121.994 | -0.17853 | -0.21973 | 122.2046 | 122.2412 | 122.1176 | 0.24719 | 0.1236 | 0.18768 | 0.022888 | 0.21057 | 0.11902 | 0.18311 | 0.16022 | 122.3282 | 122.1542 | -0.18768 | -0.33875 | 122.168 | 122.113 | 122.1634 | 122.0535
1938.5781 | 122.3923 | -122.2321 | 0.15106 | -0.0020601 | 0.019267 | 0.010179 | -0.00035247 | 0.023556 | -0.0014484 | -0.002525 | 0.0018005 | 0.052652 | 0.0071776 | -0.0074726 | 0.0014056 | 0.012659 | 0.0006302 | -0.050354 | 0.15106 | -0.09613 | -0.091553 | 0.045776 | -0.07782 | -0.045776 | -0.27466 | -0.032043 | -0.2243 | -0.21515 | -0.15106 | -0.24261 | -0.07782 | 122.1359 | 0 | -0.24261 | 122.2778 | 122.1863 | 122.1542 | 0.050354 | 0.01831 | 122.0078 | -0.18311 | -0.36621 | 122.081 | 122.1542 | 121.9894 | 0.14648 | -0.018311 | 0.14191 | 0.004577 | 0.073242 | 0.009155 | 0.24719 | 0.19226 | 122.3831 | 122.2 | -0.24719 | -0.37537 | 122.1405 | 122.0169 | 122.1817 | 121.9574
1940.3438 | 122.4014 | -122.2824 | 0.14191 | -0.0096891 | 0.01884 | 0.01082 | -0.0016343 | 0.020993 | -0.0010212 | 0.0015338 | 0.0018005 | 0.053079 | 0.010596 | -0.0012774 | 0.0026874 | 0.01565 | 0.0008438 | -0.07782 | 0.15564 | -0.10986 | -0.1236 | -0.009155 | -0.086975 | -0.064087 | -0.25635 | -0.022888 | -0.25635 | -0.19226 | -0.13275 | -0.22888 | -0.059509 | 122.1725 | 0.013733 | -0.2655 | 122.2733 | 122.2183 | 122.1954 | 0.045776 | 0.022888 | 122.0261 | -0.16479 | -0.33417 | 122.1497 | 122.2229 | 122.0535 | 0.19684 | 0.027466 | 0.10071 | -0.013733 | 0.1236 | 0.064087 | 0.2655 | 0.23346 | 122.4381 | 122.2595 | -0.25177 | -0.39826 | 122.1588 | 122.0901 | 122.2046 | 122.0261
1942.0312 | 122.4884 | -122.2366 | 0.11444 | -0.017319 | 0.016703 | 0.01082 | -0.0016343 | 0.018216 | -0.0027302 | -0.0020978 | -0.0012513 | 0.050516 | 0.0061096 | 0.00043161 | -8.9634e-05 | 0.014368 | 0.00298 | -0.059509 | 0.10071 | -0.086975 | -0.022888 | 0.16022 | 0.022888 | 0.041199 | -0.16022 | -0.07782 | -0.20142 | -0.11902 | -0.036621 | -0.11444 | 0.004578 | 122.1497 | -0.013733 | -0.13733 | 122.3969 | 122.2778 | 122.2595 | 0.12817 | 0.10986 | 122.0352 | -0.19226 | -0.23346 | 122.2 | 122.2412 | 122.1222 | 0.20599 | 0.086975 | 0.24719 | 0.064087 | 0.1648 | 0.082397 | 0.18768 | 0.1236 | 122.3373 | 122.1588 | -0.20142 | -0.31586 | 122.2137 | 122.1176 | 122.1771 | 122.0764
1943.7969 | 122.5388 | -122.2183 | 0.10986 | -0.0020601 | 0.015635 | 0.011247 | -0.0037705 | 0.019711 | -0.0020892 | 0.00089285 | -0.0012513 | 0.05137 | 0.0078186 | -0.0027728 | 0.00097837 | 0.013086 | -0.0017196 | -0.013733 | 0.10071 | -0.07782 | 0.004578 | 0.18768 | 0.064087 | 0.10529 | -0.059509 | -0.027466 | -0.17853 | -0.027466 | 0.054932 | 0 | 0.086975 | 122.1405 | -0.009155 | -0.10529 | 122.406 | 122.3236 | 122.2824 | 0.18311 | 0.14191 | 122.0398 | -0.13733 | -0.13733 | 122.2733 | 122.3053 | 122.2183 | 0.2655 | 0.17853 | 0.2655 | 0.082398 | 0.23346 | 0.15106 | 0.17853 | 0.15106 | 122.319 | 122.1909 | -0.18768 | -0.28839 | 122.2229 | 122.1909 | 122.2046 | 122.1588
1945.5781 | 122.4884 | -122.2321 | 0.13275 | -0.0096891 | 0.017771 | 0.011888 | -0.0039841 | 0.024197 | -0.0046528 | -0.00038875 | -0.0073547 | 0.04902 | 0.0078186 | -0.0017048 | 0.001833 | 0.015864 | -0.003215 | -0.064087 | 0.12817 | -0.054932 | -0.045776 | 0.12817 | 0 | 0.027466 | -0.16022 | -0.059509 | -0.20599 | -0.10986 | -0.041199 | -0.11902 | 0.013733 | 122.1771 | -0.004577 | -0.17853 | 122.3602 | 122.2595 | 122.2321 | 0.082398 | 0.054932 | 122.0261 | -0.19226 | -0.24261 | 122.1909 | 122.2458 | 122.113 | 0.21973 | 0.086975 | 0.18311 | 0.009156 | 0.1648 | 0.096131 | 0.18311 | 0.14649 | 122.3602 | 122.1725 | -0.18768 | -0.33875 | 122.1863 | 122.1222 | 122.168 | 122.0718
1947.3438 | 122.4609 | -122.2687 | 0.14648 | -0.017319 | 0.014994 | 0.009111 | -0.0012069 | 0.019711 | -0.0029438 | -0.00038875 | -0.0043029 | 0.051584 | 0.0067504 | -0.0076862 | -0.00030343 | 0.015436 | -0.0006516 | -0.041199 | 0.16479 | -0.091553 | -0.054932 | 0.086975 | -0.027466 | 0.013733 | -0.1236 | 0.022888 | -0.16479 | -0.09613 | -0.004578 | -0.10986 | 0.050354 | 122.1771 | 0.018311 | -0.20142 | 122.3557 | 122.2824 | 122.2412 | 0.10529 | 0.064087 | 122.1039 | -0.1236 | -0.24261 | 122.2641 | 122.319 | 122.1588 | 0.21515 | 0.054932 | 0.17853 | 0.036621 | 0.16022 | 0.068665 | 0.25635 | 0.18768 | 122.4335 | 122.2916 | -0.23804 | -0.31128 | 122.2137 | 122.1725 | 122.2275 | 122.1451
1949.0312 | 122.3969 | -122.287 | 0.14191 | 0.013199 | 0.017558 | 0.012315 | 0.00028833 | 0.020352 | -0.0020892 | -0.00017515 | -0.0012513 | 0.052438 | 0.007605 | -0.006618 | 0.00076477 | 0.01565 | -0.0023606 | -0.064087 | 0.14648 | -0.10529 | -0.1236 | 0.018311 | -0.09613 | -0.059509 | -0.2655 | -0.004578 | -0.21515 | -0.19684 | -0.12817 | -0.22888 | -0.054932 | 122.1817 | 0.004577 | -0.2655 | 122.3053 | 122.2275 | 122.1909 | 0.045777 | 0.009156 | 122.0718 | -0.14649 | -0.33875 | 122.1588 | 122.2321 | 122.0581 | 0.16022 | -0.013733 | 0.1236 | -0.01831 | 0.086975 | 0.018311 | 0.25177 | 0.21057 | 122.4335 | 122.2824 | -0.24719 | -0.35706 | 122.1634 | 122.0901 | 122.2229 | 122.0215
1950.7969 | 122.4335 | -122.2778 | 0.14191 | -0.017319 | 0.017131 | 0.009752 | -0.0035569 | 0.020779 | -0.001662 | 0.0013202 | -0.0073547 | 0.052225 | 0.0067504 | -0.010463 | -0.00030343 | 0.013727 | 0.000203 | -0.086975 | 0.14191 | -0.091553 | -0.11902 | 0.036621 | -0.036621 | -0.027466 | -0.21057 | 0.054932 | -0.15564 | -0.13275 | -0.059509 | -0.1236 | 0.004578 | 122.1863 | 0 | -0.26093 | 122.3145 | 122.2504 | 122.2412 | 0.064087 | 0.054932 | 122.1222 | -0.086975 | -0.27466 | 122.2183 | 122.2824 | 122.1542 | 0.16022 | 0.032044 | 0.12817 | -0.027466 | 0.096131 | 0.022889 | 0.23346 | 0.21057 | 122.4197 | 122.3328 | -0.23346 | -0.29755 | 122.1588 | 122.1451 | 122.1909 | 122.0673
1952.5469 | 122.4243 | -122.2641 | 0.15106 | -0.0020601 | 0.017771 | 0.012102 | -0.0016343 | 0.023129 | -0.0029438 | -0.0016706 | 0.0018005 | 0.050943 | 0.0073914 | -0.0061908 | 0.00461 | 0.014582 | 0.004689 | -0.073242 | 0.16022 | -0.091553 | -0.11444 | 0.018311 | -0.091553 | -0.050354 | -0.23804 | -0.018311 | -0.23346 | -0.16479 | -0.10986 | -0.20142 | -0.054932 | 122.1725 | 0.009155 | -0.2655 | 122.2824 | 122.2137 | 122.1725 | 0.041199 | 0 | 122.0306 | -0.16937 | -0.31586 | 122.1542 | 122.2092 | 122.0627 | 0.17853 | 0.032043 | 0.10986 | -0.022888 | 0.1236 | 0.068664 | 0.25177 | 0.21515 | 122.4243 | 122.2458 | -0.24261 | -0.38452 | 122.1497 | 122.0993 | 122.1909 | 122.0261
1954.25 | 122.5159 | -122.2687 | 0.10529 | 0.0055694 | 0.014781 | 0.011247 | -0.0033433 | 0.019925 | -0.0044392 | 0.0013202 | -0.0012513 | 0.048166 | 0.0095276 | -0.00063659 | 0.0014056 | 0.015009 | 0.003621 | -0.068665 | 0.12817 | -0.07782 | -0.059509 | 0.12817 | 0.009155 | 0.041199 | -0.11902 | -0.013733 | -0.17853 | -0.050354 | 0.041199 | -0.032043 | 0.07782 | 122.1909 | 0.022888 | -0.16479 | 122.3969 | 122.3099 | 122.2778 | 0.11902 | 0.086975 | 122.0901 | -0.11902 | -0.15564 | 122.3099 | 122.3465 | 122.2366 | 0.25635 | 0.14648 | 0.20599 | 0.018311 | 0.21973 | 0.12817 | 0.20599 | 0.16479 | 122.3969 | 122.2549 | -0.18311 | -0.28381 | 122.2092 | 122.2183 | 122.2 | 122.1497
1956.0156 | 122.5204 | -122.2733 | 0.10529 | -0.0020601 | 0.017131 | 0.014024 | -0.0022751 | 0.022915 | -0.0010212 | -0.003166 | -0.0043029 | 0.050516 | 0.0078186 | -0.0032 | 0.00012397 | 0.01565 | 0.001271 | -0.009155 | 0.10986 | -0.054932 | 0.009155 | 0.17853 | 0.036621 | 0.064087 | -0.073242 | -0.054932 | -0.16937 | -0.050354 | 0.009155 | -0.064087 | 0.050354 | 122.2183 | 0.004577 | -0.096131 | 122.4518 | 122.3373 | 122.3099 | 0.11902 | 0.091553 | 122.1039 | -0.16022 | -0.15564 | 122.2824 | 122.3236 | 122.2092 | 0.21973 | 0.10529 | 0.23346 | 0.064087 | 0.17853 | 0.11902 | 0.16479 | 0.11444 | 122.3831 | 122.2183 | -0.16022 | -0.27466 | 122.2824 | 122.2229 | 122.2641 | 122.2
1957.7812 | 122.58 | -122.2549 | 0.10986 | -0.0020601 | 0.015635 | 0.0095382 | -0.0027023 | 0.023556 | -0.0020892 | -0.001457 | -0.0012513 | 0.05137 | 0.007605 | -0.0012774 | 0.00076477 | 0.015223 | -0.003215 | -0.009155 | 0.11902 | -0.064087 | 0.018311 | 0.20142 | 0.082397 | 0.10529 | -0.004578 | 0.004578 | -0.13733 | 0.022888 | 0.13733 | 0.045776 | 0.13733 | 122.1909 | 0.009156 | -0.091552 | 122.4564 | 122.3602 | 122.3373 | 0.16937 | 0.14648 | 122.1176 | -0.10529 | -0.086975 | 122.3923 | 122.3923 | 122.3007 | 0.27466 | 0.18311 | 0.2655 | 0.082398 | 0.27466 | 0.16022 | 0.18311 | 0.14191 | 122.374 | 122.2595 | -0.17395 | -0.24719 | 122.2733 | 122.2778 | 122.2458 | 122.2504
1959.5625 | 122.438 | -122.2824 | 0.13733 | -0.0096891 | 0.019694 | 0.01082 | -0.00099327 | 0.019497 | -0.0027302 | 3.8448e-05 | -0.0012513 | 0.054147 | 0.0084594 | -0.0059772 | -0.0030804 | 0.014155 | 0.0023392 | -0.091553 | 0.14648 | -0.09613 | -0.10986 | 0.054932 | -0.032043 | -0.013733 | -0.15564 | 0.086975 | -0.11444 | -0.086975 | 0.009155 | -0.082397 | 0.041199 | 122.1863 | 0.009155 | -0.24719 | 122.3373 | 122.2687 | 122.2504 | 0.082397 | 0.064087 | 122.168 | -0.050354 | -0.2243 | 122.2916 | 122.3236 | 122.2 | 0.15564 | 0.032044 | 0.15106 | -0.013733 | 0.1236 | 0.027466 | 0.24261 | 0.20142 | 122.4289 | 122.3694 | -0.23346 | -0.25177 | 122.1725 | 122.1954 | 122.1909 | 122.1268
1961.25 | 122.5204 | -122.2687 | 0.1236 | -0.0096891 | 0.01649 | 0.010179 | -0.0035569 | 0.024838 | -0.003371 | -0.00081595 | -0.010406 | 0.04902 | 0.0061096 | -0.002132 | 0.0014056 | 0.013941 | 0.0014846 | -0.064087 | 0.10986 | -0.068665 | -0.027466 | 0.11902 | -0.009155 | 0.036621 | -0.13275 | -0.022888 | -0.16479 | -0.068665 | -0.004578 | -0.09613 | 0.045776 | 122.2 | -0.013733 | -0.15106 | 122.3877 | 122.3053 | 122.2595 | 0.10529 | 0.05951 | 122.1039 | -0.14648 | -0.19226 | 122.2641 | 122.3145 | 122.1725 | 0.21057 | 0.068665 | 0.18768 | 0.041199 | 0.16022 | 0.09613 | 0.17853 | 0.14191 | 122.3785 | 122.2458 | -0.19226 | -0.28839 | 122.2412 | 122.2 | 122.2046 | 122.1359
1963 | 122.4472 | -122.2916 | 0.13275 | -0.0096891 | 0.016276 | 0.011888 | 0.00028833 | 0.018216 | -0.0020892 | -0.0020978 | -0.0012513 | 0.050302 | 0.0080322 | -0.0040546 | 0.0020466 | 0.013086 | 0.00298 | -0.054932 | 0.14191 | -0.10986 | -0.10986 | 0.036621 | -0.09613 | -0.045776 | -0.20142 | 0.018311 | -0.18768 | -0.12817 | -0.07782 | -0.18768 | -0.004578 | 122.1817 | 0.009156 | -0.24261 | 122.3282 | 122.2458 | 122.1954 | 0.064087 | 0.013733 | 122.1039 | -0.11444 | -0.26093 | 122.2137 | 122.287 | 122.1039 | 0.1831 | 0 | 0.14648 | 0 | 0.10986 | 0.059509 | 0.25177 | 0.20599 | 122.4335 | 122.3099 | -0.24261 | -0.32043 | 122.1817 | 122.1634 | 122.2366 | 122.0901
1964.7656 | 122.5113 | -122.2549 | 0.11902 | -0.0020601 | 0.017771 | 0.012315 | 0.00050193 | 0.02377 | -0.001662 | 0.00067925 | -0.0012513 | 0.053079 | 0.007605 | -0.0025592 | 0.001192 | 0.013727 | -1.0598e-05 | -0.027466 | 0.15106 | -0.086975 | -0.045776 | 0.10529 | -0.004578 | 0.013733 | -0.064087 | 0.050354 | -0.13733 | -0.036621 | 0.041199 | -0.041199 | 0.064087 | 122.168 | 0.032043 | -0.16479 | 122.3602 | 122.2687 | 122.2504 | 0.10071 | 0.082397 | 122.1176 | -0.068665 | -0.15564 | 122.2961 | 122.319 | 122.2137 | 0.20142 | 0.09613 | 0.19226 | 0.041199 | 0.17853 | 0.10071 | 0.23804 | 0.18768 | 122.406 | 122.3053 | -0.20599 | -0.25635 | 122.2092 | 122.2183 | 122.2275 | 122.1909
1966.5312 | 122.5342 | -122.2961 | 0.1236 | -0.0020601 | 0.01414 | 0.013384 | -0.0022751 | 0.022702 | -0.0014484 | -0.00060235 | -0.0012513 | 0.047952 | 0.005896 | 0.002995 | 0.0016194 | 0.016077 | 0.0008438 | -0.045776 | 0.11902 | -0.082397 | -0.050354 | 0.14191 | 0 | 0.032043 | -0.11444 | -0.004578 | -0.16937 | -0.082397 | 0.027466 | -0.068665 | 0.050354 | 122.2137 | -0.004577 | -0.17395 | 122.4381 | 122.3282 | 122.2961 | 0.11444 | 0.082397 | 122.1268 | -0.12817 | -0.20599 | 122.3236 | 122.3465 | 122.2275 | 0.21973 | 0.10071 | 0.2243 | 0.032043 | 0.19684 | 0.086976 | 0.20142 | 0.16479 | 122.4152 | 122.2916 | -0.20599 | -0.29297 | 122.2458 | 122.2137 | 122.2504 | 122.1817
1968.2969 | 122.5983 | -122.2687 | 0.10529 | -0.0020601 | 0.016276 | 0.010179 | -0.0018479 | 0.017575 | -0.0035846 | -0.0029524 | -0.0012513 | 0.048807 | 0.009314 | 0.0010724 | 0.0014056 | 0.012873 | 0.0016982 | -0.013733 | 0.13275 | -0.073242 | 0.018311 | 0.19684 | 0.068665 | 0.10529 | 0.004578 | 0.018311 | -0.1236 | 0.041199 | 0.13733 | 0.054932 | 0.14648 | 122.1954 | 0.027465 | -0.086975 | 122.4655 | 122.374 | 122.3373 | 0.17853 | 0.14191 | 122.1451 | -0.086975 | -0.064087 | 122.406 | 122.4152 | 122.3236 | 0.27008 | 0.17853 | 0.27008 | 0.091553 | 0.26093 | 0.16479 | 0.20599 | 0.14191 | 122.4014 | 122.287 | -0.17853 | -0.22888 | 122.287 | 122.3099 | 122.2549 | 122.2733
1969.9844 | 122.4564 | -122.3236 | 0.15564 | -0.0020601 | 0.017558 | 0.0093246 | -0.0020615 | 0.020138 | -0.0025166 | 0.00025205 | 0.0018005 | 0.051584 | 0.0080322 | -0.0044818 | -0.001585 | 0.011164 | -0.0006516 | -0.064087 | 0.15106 | -0.091553 | -0.082397 | 0.059509 | -0.032043 | -0.009155 | -0.11902 | 0.10529 | -0.11902 | -0.07782 | 0.027466 | -0.054932 | 0.064087 | 122.2321 | -0.004578 | -0.23804 | 122.3831 | 122.3145 | 122.2916 | 0.082398 | 0.05951 | 122.2046 | -0.050354 | -0.23346 | 122.3511 | 122.3877 | 122.2687 | 0.18311 | 0.064087 | 0.15106 | 0.009156 | 0.14649 | 0.041199 | 0.24261 | 0.22431 | 122.4747 | 122.4289 | -0.24719 | -0.27466 | 122.2412 | 122.2458 | 122.2595 | 122.2046
1971.7344 | 122.5616 | -122.2824 | 0.11444 | -0.017319 | 0.016917 | 0.011461 | -0.0039841 | 0.022275 | 4.7018e-05 | -0.00017515 | -0.0012513 | 0.049447 | 0.0084594 | -0.0019184 | 0.0026874 | 0.013086 | 0.0010574 | -0.054932 | 0.10071 | -0.082397 | -0.041199 | 0.13733 | 0.032043 | 0.050354 | -0.068665 | 0.045776 | -0.11444 | 0 | 0.10529 | 0.022888 | 0.1236 | 122.2 | -0.013733 | -0.15564 | 122.4197 | 122.3328 | 122.3145 | 0.13275 | 0.11444 | 122.168 | -0.068665 | -0.11444 | 122.3877 | 122.406 | 122.3053 | 0.23804 | 0.13733 | 0.21973 | 0.041198 | 0.21973 | 0.11444 | 0.18311 | 0.16022 | 122.3831 | 122.3282 | -0.19684 | -0.22888 | 122.2412 | 122.2824 | 122.2275 | 122.2137
1973.5 | 122.493 | -122.319 | 0.15106 | -0.017319 | 0.01649 | 0.0082566 | -0.00013887 | 0.01907 | -0.0037982 | -0.001457 | -0.0043029 | 0.051584 | 0.0054688 | -0.0053364 | -8.9634e-05 | 0.012446 | 0.00298 | -0.086975 | 0.12817 | -0.11902 | -0.10529 | 0.032043 | -0.045776 | -0.041199 | -0.11444 | 0.10986 | -0.091553 | -0.054932 | 0.027466 | -0.059509 | 0.07782 | 122.2 | -0.022888 | -0.25635 | 122.3511 | 122.2778 | 122.2733 | 0.07782 | 0.073243 | 122.2275 | -0.041199 | -0.20599 | 122.3465 | 122.3969 | 122.2595 | 0.16937 | 0.032044 | 0.15106 | 0.013733 | 0.11902 | 0.036621 | 0.24719 | 0.20142 | 122.4472 | 122.4289 | -0.27008 | -0.24261 | 122.2137 | 122.2641 | 122.2321 | 122.2046
1975.1875 | 122.5708 | -122.2824 | 0.1236 | -0.0096891 | 0.017985 | 0.01082 | -0.0018479 | 0.021206 | -0.0018756 | -0.00038875 | 0.0048523 | 0.049661 | 0.0080322 | -0.0046954 | 0.00097837 | 0.015009 | -0.0023606 | -0.050354 | 0.12817 | -0.073242 | -0.032043 | 0.12817 | 0.018311 | 0.050354 | -0.073242 | 0.032043 | -0.12817 | -0.004578 | 0.082397 | -0.004578 | 0.11902 | 122.2092 | 0.004578 | -0.15564 | 122.4106 | 122.3328 | 122.3007 | 0.1236 | 0.091553 | 122.1542 | -0.091553 | -0.12817 | 122.3648 | 122.4014 | 122.2778 | 0.24719 | 0.1236 | 0.20142 | 0.041199 | 0.21057 | 0.1236 | 0.20142 | 0.16022 | 122.4106 | 122.3145 | -0.19684 | -0.25177 | 122.2504 | 122.2778 | 122.2321 | 122.2092
1976.9531 | 122.5113 | -122.3282 | 0.13733 | -0.0096891 | 0.01649 | 0.012315 | 0.00028833 | 0.020779 | -0.0046528 | -0.00060235 | -0.0073547 | 0.052011 | 0.0039734 | -0.011104 | -0.00030343 | 0.015009 | 0.0016982 | -0.045776 | 0.14191 | -0.10071 | -0.082397 | 0.059509 | -0.027466 | -0.009155 | -0.10986 | 0.09613 | -0.10071 | -0.045776 | 0.027466 | -0.059509 | 0.086975 | 122.2275 | 0.004578 | -0.21973 | 122.3877 | 122.319 | 122.3007 | 0.091553 | 0.073242 | 122.2275 | -0.041199 | -0.18311 | 122.3557 | 122.4152 | 122.2687 | 0.18768 | 0.041199 | 0.16022 | 0.018311 | 0.12817 | 0.054932 | 0.24262 | 0.19684 | 122.4701 | 122.4243 | -0.23804 | -0.23804 | 122.2458 | 122.2824 | 122.2824 | 122.2183
1978.7031 | 122.4564 | -122.3145 | 0.15564 | 0.0055694 | 0.018199 | 0.011461 | 0.0022109 | 0.021847 | -0.0020892 | 0.001961 | -0.0012513 | 0.053506 | 0.0073914 | -0.006618 | 0.0014056 | 0.01565 | -0.0017196 | -0.064087 | 0.14191 | -0.09613 | -0.10529 | 0.009155 | -0.086975 | -0.059509 | -0.23804 | 0.027466 | -0.20599 | -0.14648 | -0.086975 | -0.18768 | -0.013733 | 122.2183 | -0.013733 | -0.26093 | 122.3236 | 122.2549 | 122.2275 | 0.036621 | 0.009155 | 122.1085 | -0.12817 | -0.30212 | 122.2275 | 122.3007 | 122.1268 | 0.19226 | 0.018311 | 0.10528 | -0.009156 | 0.11902 | 0.05951 | 0.23804 | 0.23346 | 122.4564 | 122.3419 | -0.25177 | -0.36163 | 122.2092 | 122.168 | 122.2504 | 122.0764
1980.4062 | 122.6074 | -122.2778 | 0.10986 | -0.0020601 | 0.017771 | 0.012315 | -0.00099327 | 0.023343 | -0.0035846 | -0.002525 | -0.0043029 | 0.052225 | 0.007605 | -0.0081134 | 0.0033282 | 0.013727 | -1.0598e-05 | -0.045776 | 0.1236 | -0.064087 | -0.036621 | 0.11902 | -0.018311 | 0.018311 | -0.09613 | -0.036621 | -0.19226 | -0.064087 | 0.013733 | -0.073242 | 0.068665 | 122.2137 | 0.013733 | -0.14648 | 122.3969 | 122.2961 | 122.2595 | 0.082398 | 0.045776 | 122.0856 | -0.14648 | -0.17395 | 122.2916 | 122.3465 | 122.2046 | 0.26093 | 0.11902 | 0.18311 | 0.027466 | 0.20599 | 0.12817 | 0.18768 | 0.15564 | 122.4014 | 122.2412 | -0.17395 | -0.30212 | 122.2412 | 122.2137 | 122.2321 | 122.1817
1982.1094 | 122.4655 | -122.319 | 0.13275 | -0.0096891 | 0.017131 | 0.012102 | -0.00056607 | 0.022061 | -0.0010212 | -0.0010298 | 0.0048523 | 0.050088 | 0.0078186 | -0.0012774 | 0.001192 | 0.014582 | -0.000438 | -0.054932 | 0.13733 | -0.07782 | -0.11902 | 0.013733 | -0.086975 | -0.050354 | -0.21973 | 0.009155 | -0.20599 | -0.16022 | -0.09613 | -0.1831 | -0.022888 | 122.2412 | 0.004578 | -0.25177 | 122.3328 | 122.2687 | 122.2321 | 0.027466 | -0.009155 | 122.113 | -0.1236 | -0.29297 | 122.2229 | 122.2961 | 122.1359 | 0.18311 | 0.022889 | 0.091553 | -0.041199 | 0.10986 | 0.045777 | 0.21515 | 0.21515 | 122.4564 | 122.3282 | -0.21057 | -0.33875 | 122.2 | 122.1588 | 122.2641 | 122.0993
1983.8594 | 122.5571 | -122.2961 | 0.1236 | -0.0096891 | 0.016276 | 0.0095382 | -0.0022751 | 0.019711 | -0.00059378 | -0.004875 | -0.0012513 | 0.050943 | 0.0071776 | -0.0027728 | 0.00055117 | 0.017145 | 0.0004166 | -0.068665 | 0.13275 | -0.054932 | -0.041199 | 0.11444 | -0.009155 | 0.032043 | -0.10071 | 0.004578 | -0.16937 | -0.086975 | 0.013733 | -0.068665 | 0.050354 | 122.2412 | 0.009155 | -0.16479 | 122.4106 | 122.3282 | 122.287 | 0.086975 | 0.045777 | 122.1268 | -0.11902 | -0.21057 | 122.3099 | 122.3465 | 122.2275 | 0.21973 | 0.10071 | 0.16937 | 0.013733 | 0.18311 | 0.082398 | 0.18768 | 0.17395 | 122.4289 | 122.3007 | -0.17853 | -0.29297 | 122.2549 | 122.2092 | 122.2275 | 122.1954
1985.5625 | 122.4701 | -122.3236 | 0.13275 | 0.0055694 | 0.017131 | 0.009752 | 0.00028833 | 0.022488 | -0.0012348 | 0.00046565 | -0.0012513 | 0.053293 | 0.0073914 | -0.010036 | 0.00097837 | 0.015009 | 0.0004166 | -0.050354 | 0.13733 | -0.10071 | -0.09613 | 0.050354 | -0.068665 | -0.045776 | -0.18768 | 0.036621 | -0.1831 | -0.14648 | -0.073242 | -0.16479 | -0.022888 | 122.2229 | 0.004578 | -0.22888 | 122.374 | 122.2778 | 122.2549 | 0.054932 | 0.032043 | 122.1405 | -0.09613 | -0.27924 | 122.2504 | 122.3007 | 122.1588 | 0.16022 | 0.01831 | 0.15106 | 0.004578 | 0.10986 | 0.036621 | 0.23804 | 0.21973 | 122.4609 | 122.3602 | -0.23346 | -0.31586 | 122.2275 | 122.1771 | 122.2733 | 122.1359
1987.2656 | 122.5708 | -122.3099 | 0.10071 | -0.0020601 | 0.013926 | 0.0093246 | -0.0031297 | 0.020566 | -0.0025166 | 0.00025205 | -0.0012513 | 0.048593 | 0.0067504 | -0.0036274 | 0.00033757 | 0.015009 | -0.001506 | -0.054932 | 0.1236 | -0.07782 | -0.022888 | 0.15106 | 0 | 0.032043 | -0.11444 | -0.022888 | -0.17853 | -0.068665 | -0.004578 | -0.082397 | 0.032043 | 122.2321 | 0.022888 | -0.1236 | 122.4609 | 122.3419 | 122.3099 | 0.10986 | 0.07782 | 122.1313 | -0.1236 | -0.16937 | 122.3053 | 122.3419 | 122.2275 | 0.21057 | 0.096131 | 0.22888 | 0.054932 | 0.17395 | 0.10986 | 0.20142 | 0.15564 | 122.4335 | 122.287 | -0.17853 | -0.27924 | 122.287 | 122.2412 | 122.2549 | 122.1954
1988.9531 | 122.6028 | -122.3145 | 0.12817 | -0.0096891 | 0.015849 | 0.011247 | -0.0022751 | 0.018216 | -0.0023028 | -0.00081595 | -0.0043029 | 0.050302 | 0.006964 | -0.0091816 | 0.0016194 | 0.014155 | 0.000203 | -0.059509 | 0.10071 | -0.068665 | -0.050354 | 0.11444 | 0.013733 | 0.045776 | -0.12817 | 0.009155 | -0.17853 | -0.050354 | 0.036621 | -0.041199 | 0.064087 | 122.2458 | -0.027466 | -0.17853 | 122.4289 | 122.3602 | 122.3282 | 0.11444 | 0.082398 | 122.1359 | -0.11902 | -0.17853 | 122.3511 | 122.3785 | 122.2733 | 0.24261 | 0.13733 | 0.18311 | 0.018311 | 0.21515 | 0.12817 | 0.16937 | 0.18768 | 122.4152 | 122.3236 | -0.19684 | -0.3067 | 122.2641 | 122.2641 | 122.2549 | 122.1863
1990.7344 | 122.5433 | -122.3373 | 0.10986 | -0.0096891 | 0.01884 | 0.0086838 | -0.0016343 | 0.026761 | -0.0014484 | 0.00089285 | -0.0043029 | 0.051156 | 0.008673 | -0.008327 | -8.9634e-05 | 0.014795 | 0.003621 | -0.004578 | 0.14191 | -0.091553 | -0.036621 | 0.12817 | -0.009155 | 0.013733 | -0.068665 | 0.032043 | -0.12817 | -0.045776 | 0.009155 | -0.064087 | 0.054932 | 122.2458 | 0.032044 | -0.14648 | 122.4655 | 122.3511 | 122.3282 | 0.10529 | 0.082398 | 122.2092 | -0.07782 | -0.15564 | 122.3465 | 122.3923 | 122.2733 | 0.18311 | 0.064087 | 0.21973 | 0.054932 | 0.13733 | 0.082398 | 0.23346 | 0.16022 | 122.4792 | 122.3694 | -0.20142 | -0.23804 | 122.3007 | 122.2916 | 122.3328 | 122.2687
1992.5 | 122.5983 | -122.3236 | 0.13275 | -0.0096891 | 0.017771 | 0.0095382 | -0.0016343 | 0.020138 | -0.0020892 | -0.0027386 | 0.0018005 | 0.050088 | 0.0065368 | 0.00064521 | -8.9634e-05 | 0.017145 | 0.00298 | -0.009155 | 0.10529 | -0.07782 | 0.022888 | 0.19226 | 0.068665 | 0.086975 | -0.032043 | 0.013733 | -0.14648 | -0.022888 | 0.10071 | 0.013733 | 0.11444 | 122.2458 | -0.027465 | -0.10986 | 122.5159 | 122.4106 | 122.3923 | 0.16479 | 0.14649 | 122.1771 | -0.11902 | -0.15564 | 122.4243 | 122.438 | 122.3373 | 0.26093 | 0.16022 | 0.27008 | 0.10071 | 0.24719 | 0.1236 | 0.18311 | 0.16022 | 122.4289 | 122.3373 | -0.21057 | -0.27924 | 122.3465 | 122.3007 | 122.3145 | 122.2916
1994.25 | 122.5159 | -122.3694 | 0.14648 | -0.024948 | 0.01414 | 0.0065476 | -0.0014207 | 0.015866 | -0.0027302 | -0.00017515 | -0.0043029 | 0.051156 | 0.0054688 | -0.010463 | -0.0020122 | 0.012873 | -0.000438 | -0.082397 | 0.14648 | -0.09613 | -0.11444 | 0.036621 | -0.059509 | -0.018311 | -0.18768 | 0.054932 | -0.13275 | -0.10529 | -0.041199 | -0.11902 | 0.022888 | 122.2733 | 0 | -0.26093 | 122.406 | 122.3511 | 122.3099 | 0.077819 | 0.036621 | 122.2366 | -0.091552 | -0.25177 | 122.3282 | 122.3923 | 122.2504 | 0.15564 | 0.013732 | 0.13275 | -0.018311 | 0.091552 | 0.027465 | 0.24261 | 0.18768 | 122.5159 | 122.4243 | -0.24261 | -0.27924 | 122.2549 | 122.2641 | 122.287 | 122.1817
1995.9531 | 122.5067 | -122.3419 | 0.14191 | -0.0020601 | 0.016276 | 0.012529 | 0.00071573 | 0.021634 | -0.00080758 | -0.0035932 | -0.0012513 | 0.050729 | 0.006964 | -0.0042682 | 0.0033282 | 0.01565 | 0.0023392 | -0.073242 | 0.12817 | -0.11444 | -0.1236 | 0.032043 | -0.10071 | -0.041199 | -0.22888 | 0.004578 | -0.21515 | -0.15564 | -0.1236 | -0.1831 | -0.036621 | 122.2275 | -0.013733 | -0.2655 | 122.374 | 122.3007 | 122.2412 | 0.073242 | 0.013733 | 122.1268 | -0.13733 | -0.29755 | 122.2183 | 122.3053 | 122.1588 | 0.17853 | 0.032044 | 0.14648 | -0.009155 | 0.091553 | 0.059509 | 0.24262 | 0.21973 | 122.4701 | 122.3465 | -0.25635 | -0.35706 | 122.2183 | 122.1863 | 122.2687 | 122.113
1997.7031 | 122.493 | -122.3648 | 0.15106 | -0.0020601 | 0.018626 | 0.0084702 | -0.0024887 | 0.022702 | -0.0031574 | 0.00067925 | 0.0018005 | 0.050302 | 0.0082458 | -0.0032 | -0.00073063 | 0.014795 | 0.001912 | -0.054932 | 0.14648 | -0.091553 | -0.091553 | 0.091553 | -0.022888 | 0.004578 | -0.12817 | 0.064087 | -0.13275 | -0.091553 | 0.004578 | -0.086975 | 0.027466 | 122.2733 | -0.004578 | -0.24261 | 122.4564 | 122.3694 | 122.3419 | 0.096131 | 0.068665 | 122.2321 | -0.086975 | -0.24261 | 122.3694 | 122.3923 | 122.2778 | 0.16022 | 0.045776 | 0.18311 | 0 | 0.13733 | 0.041198 | 0.23804 | 0.19684 | 122.5113 | 122.4289 | -0.24261 | -0.28381 | 122.2733 | 122.2733 | 122.3099 | 122.2366
1999.4688 | 122.5021 | -122.374 | 0.14191 | -0.0096891 | 0.020976 | 0.01082 | -0.00035247 | 0.022702 | -0.0037982 | -0.00060235 | 0.0018005 | 0.052011 | 0.010168 | -0.011531 | 0.0016194 | 0.015223 | -0.0012924 | -0.036621 | 0.15106 | -0.086975 | -0.07782 | 0.068665 | -0.050354 | -0.032043 | -0.16022 | 0.022888 | -0.17395 | -0.10986 | -0.059509 | -0.16022 | -0.004578 | 122.287 | 0.009155 | -0.21973 | 122.4426 | 122.3419 | 122.3236 | 0.054932 | 0.036621 | 122.2 | -0.11902 | -0.25177 | 122.3145 | 122.3694 | 122.2137 | 0.16937 | 0.013733 | 0.15564 | 0.009155 | 0.11444 | 0.064087 | 0.23804 | 0.19684 | 122.525 | 122.3969 | -0.22888 | -0.31586 | 122.2961 | 122.2641 | 122.3373 | 122.2137
2001.2344 | 122.6532 | -122.3145 | 0.10071 | -0.0020601 | 0.017771 | 0.011461 | -0.0027023 | 0.022061 | -0.0031574 | -0.003166 | -0.0043029 | 0.050302 | 0.0088866 | -0.0061908 | 0.00076477 | 0.014368 | 0.0016982 | 0 | 0.11444 | -0.068665 | 0.018311 | 0.23804 | 0.086975 | 0.091553 | 0.013733 | 0 | -0.13275 | 0.032043 | 0.12817 | 0.041199 | 0.13275 | 122.2458 | 0.013733 | -0.082397 | 122.5525 | 122.406 | 122.4014 | 0.16022 | 0.15564 | 122.1817 | -0.10071 | -0.068665 | 122.4426 | 122.4472 | 122.3557 | 0.2655 | 0.17395 | 0.3067 | 0.086976 | 0.26093 | 0.16479 | 0.18311 | 0.13275 | 122.4289 | 122.3145 | -0.16937 | -0.23346 | 122.3328 | 122.3465 | 122.3145 | 122.3282
2003 | 122.5204 | -122.3923 | 0.14648 | 0.0055694 | 0.016062 | 0.0099656 | -0.00099327 | 0.01907 | -0.0035846 | 0.00089285 | -0.0043029 | 0.050943 | 0.0063232 | -0.0046954 | -0.003294 | 0.012873 | 0.001912 | -0.07782 | 0.13733 | -0.11444 | -0.10986 | 0.068665 | -0.045776 | -0.013733 | -0.12817 | 0.07782 | -0.1236 | -0.082397 | 0.009155 | -0.07782 | 0.045776 | 122.2778 | -0.009155 | -0.25635 | 122.4609 | 122.3785 | 122.3465 | 0.10071 | 0.068665 | 122.2687 | -0.068664 | -0.22888 | 122.4014 | 122.438 | 122.3145 | 0.16937 | 0.045776 | 0.18311 | 0.004578 | 0.13275 | 0.041199 | 0.25177 | 0.20142 | 122.5296 | 122.4701 | -0.26093 | -0.27008 | 122.2824 | 122.3099 | 122.3145 | 122.2641
2004.7031 | 122.5708 | -122.3694 | 0.14648 | -0.0096891 | 0.01948 | 0.01082 | -0.00077967 | 0.023984 | -0.0014484 | 0.00046565 | -0.0073547 | 0.052225 | 0.0067504 | -0.010463 | 0.0022602 | 0.014795 | 0.0014846 | -0.027466 | 0.14648 | -0.086975 | -0.054932 | 0.09613 | -0.004578 | 0.009155 | -0.082397 | 0.064087 | -0.13275 | -0.045776 | 0.027466 | -0.064087 | 0.082397 | 122.2824 | 0 | -0.20142 | 122.4655 | 122.3785 | 122.3648 | 0.09613 | 0.082397 | 122.2366 | -0.082397 | -0.19226 | 122.3969 | 122.4518 | 122.3053 | 0.21515 | 0.068664 | 0.1831 | 0.032043 | 0.16022 | 0.086975 | 0.23346 | 0.19684 | 122.5159 | 122.4335 | -0.23346 | -0.27924 | 122.3145 | 122.3236 | 122.3419 | 122.287
2006.4688 | 122.6212 | -122.3694 | 0.11902 | -0.0096891 | 0.014994 | 0.011675 | -0.0041977 | 0.020993 | -0.00080758 | -0.0016706 | -0.0012513 | 0.047738 | 0.0078186 | -0.0051226 | 0.00055117 | 0.015436 | 0.0006302 | -0.054932 | 0.11444 | -0.086975 | -0.059509 | 0.11902 | 0.004578 | 0.041199 | -0.10071 | -0.004578 | -0.16479 | -0.054932 | 0.041199 | -0.050354 | 0.068665 | 122.2824 | -0.004578 | -0.17853 | 122.4884 | 122.4106 | 122.374 | 0.12817 | 0.091553 | 122.2046 | -0.1236 | -0.17395 | 122.4106 | 122.438 | 122.319 | 0.23346 | 0.11444 | 0.20599 | 0.027466 | 0.20599 | 0.10986 | 0.20142 | 0.16022 | 122.4838 | 122.3648 | -0.20599 | -0.28381 | 122.3099 | 122.3145 | 122.3145 | 122.2687
2008.2188 | 122.6486 | -122.3099 | 0.11444 | -0.017319 | 0.016703 | 0.012102 | -0.0037705 | 0.021847 | -0.0012348 | -0.00017515 | -0.010406 | 0.051797 | 0.0063232 | -0.0014912 | 0.0041828 | 0.016291 | -1.0598e-05 | 0.009155 | 0.082397 | -0.041199 | 0.027466 | 0.17853 | 0.036621 | 0.068665 | -0.050354 | -0.045776 | -0.15564 | -0.013733 | 0.064087 | -0.036621 | 0.068665 | 122.2687 | -0.032044 | -0.086975 | 122.4884 | 122.3785 | 122.3465 | 0.10986 | 0.07782 | 122.1542 | -0.16022 | -0.12817 | 122.374 | 122.3785 | 122.2733 | 0.22431 | 0.11902 | 0.21973 | 0.068665 | 0.21973 | 0.14191 | 0.1236 | 0.10986 | 122.3923 | 122.2641 | -0.15564 | -0.27008 | 122.3373 | 122.2961 | 122.319 | 122.2595
2009.9688 | 122.5113 | -122.3923 | 0.12817 | -0.0020601 | 0.019053 | 0.011675 | 7.473e-05 | 0.020566 | -0.00038018 | -0.00060235 | -0.0012513 | 0.052225 | 0.0078186 | -0.0087542 | 0.00461 | 0.01565 | -0.0006516 | -0.059509 | 0.14191 | -0.10071 | -0.12817 | 0.004578 | -0.082397 | -0.041199 | -0.20599 | 0.036621 | -0.17395 | -0.13733 | -0.091553 | -0.17395 | -0.009155 | 122.2916 | 0.013733 | -0.25635 | 122.3969 | 122.3511 | 122.3099 | 0.059509 | 0.018311 | 122.2183 | -0.091553 | -0.2655 | 122.3007 | 122.3831 | 122.2183 | 0.16479 | 0 | 0.10529 | -0.027466 | 0.082397 | 0.036621 | 0.24262 | 0.21057 | 122.5342 | 122.4289 | -0.22888 | -0.30212 | 122.2641 | 122.2549 | 122.3328 | 122.1863
2011.6719 | 122.6578 | -122.319 | 0.09613 | 0.0055694 | 0.017131 | 0.011675 | -0.0027023 | 0.025052 | 0.00047422 | 0.00025205 | -0.010406 | 0.048807 | 0.0073914 | -0.0019184 | 0.0041828 | 0.016291 | -0.0027878 | 0.009155 | 0.091553 | -0.059509 | 0 | 0.1831 | 0.036621 | 0.059509 | -0.064087 | -0.054932 | -0.14648 | -0.022888 | 0.068665 | -0.036621 | 0.10071 | 122.2595 | -0.004577 | -0.09613 | 122.5021 | 122.3785 | 122.3557 | 0.11902 | 0.09613 | 122.1725 | -0.15106 | -0.11902 | 122.3877 | 122.4197 | 122.2824 | 0.24719 | 0.10986 | 0.24261 | 0.059509 | 0.21515 | 0.1236 | 0.15106 | 0.091552 | 122.4106 | 122.2641 | -0.15564 | -0.24261 | 122.319 | 122.2961 | 122.3282 | 122.2549
2013.4219 | 122.5433 | -122.3648 | 0.14648 | -0.024948 | 0.015422 | 0.010179 | -0.0022751 | 0.016507 | -0.0059344 | 3.8448e-05 | -0.010406 | 0.050302 | 0.0067504 | -0.0059772 | -0.0017986 | 0.013514 | 0.0021256 | -0.091553 | 0.13733 | -0.10529 | -0.1236 | 0.027466 | -0.054932 | -0.036621 | -0.13275 | 0.11902 | -0.091553 | -0.041199 | 0.004578 | -0.073242 | 0.064087 | 122.2595 | -0.009155 | -0.27008 | 122.3923 | 122.3282 | 122.3099 | 0.068665 | 0.050354 | 122.2733 | -0.027465 | -0.18768 | 122.3694 | 122.4289 | 122.2916 | 0.15564 | 0.018311 | 0.13275 | -0.01831 | 0.096131 | 0.050354 | 0.24262 | 0.21057 | 122.5021 | 122.4838 | -0.25177 | -0.23804 | 122.2412 | 122.3236 | 122.2733 | 122.2321
2015.1719 | 122.6669 | -122.3328 | 0.10986 | -0.0096891 | 0.016703 | 0.0095382 | -0.0041977 | 0.021634 | -0.0042254 | 3.8448e-05 | -0.0012513 | 0.047525 | 0.0056824 | -0.0029864 | 0.0014056 | 0.015223 | -0.001506 | -0.032043 | 0.10529 | -0.068665 | -0.009155 | 0.15106 | 0.050354 | 0.082397 | -0.009155 | 0.032043 | -0.10986 | 0.041199 | 0.12817 | 0.054932 | 0.15106 | 122.2641 | -0.004577 | -0.11902 | 122.4838 | 122.4152 | 122.3831 | 0.15106 | 0.11902 | 122.2229 | -0.07782 | -0.068664 | 122.4609 | 122.4838 | 122.3877 | 0.26093 | 0.16479 | 0.21973 | 0.05951 | 0.23804 | 0.15106 | 0.17395 | 0.14191 | 122.4381 | 122.3648 | -0.17853 | -0.21973 | 122.3236 | 122.374 | 122.3007 | 122.3236
2016.9375 | 122.6807 | -122.3328 | 0.10986 | -0.0096891 | 0.017131 | 0.01082 | -0.0044113 | 0.023129 | -0.0012348 | -0.00038875 | -0.0012513 | 0.049234 | 0.0063232 | 0.0023542 | -0.0011578 | 0.015223 | 0.00298 | -0.018311 | 0.10529 | -0.082397 | 0.013733 | 0.20599 | 0.07782 | 0.091553 | 0.054932 | 0.032043 | -0.086975 | 0.054932 | 0.14648 | 0.068665 | 0.16022 | 122.2504 | -0.004577 | -0.09613 | 122.5388 | 122.4243 | 122.4106 | 0.17395 | 0.16022 | 122.2458 | -0.07782 | -0.054931 | 122.4792 | 122.493 | 122.4014 | 0.24719 | 0.15564 | 0.28839 | 0.09613 | 0.23346 | 0.14191 | 0.18768 | 0.11902 | 122.4381 | 122.3648 | -0.19226 | -0.19684 | 122.3465 | 122.3877 | 122.3145 | 122.3877
2018.625 | 122.5388 | -122.4014 | 0.11902 | 0.0055694 | 0.01414 | 0.0084702 | -0.00035247 | 0.017788 | -0.0052936 | -0.0035932 | -0.013458 | 0.049234 | 0.0084594 | -0.0029864 | -0.0028668 | 0.0133 | -1.0598e-05 | -0.09613 | 0.13733 | -0.10071 | -0.10986 | 0.041199 | -0.054932 | -0.013733 | -0.086975 | 0.10529 | -0.09613 | -0.050354 | 0.032043 | -0.068665 | 0.082397 | 122.3007 | 0.01831 | -0.22888 | 122.4426 | 122.3877 | 122.3465 | 0.086975 | 0.045776 | 122.3053 | -0.013733 | -0.16937 | 122.4335 | 122.4838 | 122.3328 | 0.17853 | 0.027465 | 0.14191 | -0.009155 | 0.12817 | 0.045776 | 0.23804 | 0.20142 | 122.5388 | 122.5067 | -0.21973 | -0.21515 | 122.2916 | 122.3511 | 122.3053 | 122.3145
2020.3906 | 122.525 | -122.4152 | 0.1236 | 0.0055694 | 0.017985 | 0.011034 | 0.00050193 | 0.020352 | -0.0010212 | -0.0018842 | -0.0012513 | 0.05372 | 0.0097412 | -0.0036274 | 0.0048236 | 0.015009 | 0.000203 | -0.054932 | 0.14191 | -0.10529 | -0.10071 | 0.022888 | -0.09613 | -0.059509 | -0.1831 | 0.086975 | -0.15564 | -0.10986 | -0.059509 | -0.14648 | 0.009155 | 122.3099 | 0.018311 | -0.2243 | 122.438 | 122.3557 | 122.319 | 0.045777 | 0.009156 | 122.2595 | -0.036621 | -0.23346 | 122.3557 | 122.4243 | 122.2687 | 0.16479 | 0.009156 | 0.12817 | 0.004578 | 0.096131 | 0.045777 | 0.24719 | 0.24261 | 122.5571 | 122.5021 | -0.22888 | -0.27924 | 122.3145 | 122.3053 | 122.3602 | 122.2321
2022.1562 | 122.5891 | -122.3969 | 0.14191 | -0.017319 | 0.017131 | 0.010393 | -0.0016343 | 0.021634 | -0.001662 | -0.0016706 | -0.0073547 | 0.053079 | 0.0091002 | -0.014522 | 0.00097837 | 0.014368 | -0.0006516 | -0.064087 | 0.14648 | -0.10529 | -0.09613 | 0.050354 | -0.018311 | -0.004578 | -0.07782 | 0.10986 | -0.068665 | -0.027466 | 0.073242 | -0.022888 | 0.09613 | 122.2916 | 0.004577 | -0.23804 | 122.4472 | 122.3923 | 122.3785 | 0.10071 | 0.086975 | 122.3282 | -0.032044 | -0.16937 | 122.4701 | 122.493 | 122.374 | 0.16479 | 0.045777 | 0.15564 | 0.009156 | 0.14191 | 0.041199 | 0.25177 | 0.17853 | 122.5433 | 122.5067 | -0.24719 | -0.21057 | 122.3007 | 122.3694 | 122.3328 | 122.319
2023.9375 | 122.493 | -122.2549 | 0.10529 | -0.0020601 | 0.019908 | 0.009752 | -0.0039841 | 0.022915 | -0.0046528 | 0.00089285 | -0.0012513 | 0.04902 | 0.0071776 | -0.0044818 | 0.0065326 | 0.015223 | 0.0021256 | 0.036621 | 0.07782 | -0.086975 | 0.004578 | 0.16479 | 0.036621 | 0.059509 | -0.032043 | -0.018311 | -0.11444 | 0.013733 | 0.082397 | -0.022888 | 0.11902 | 122.168 | -0.027466 | -0.10071 | 122.4197 | 122.3145 | 122.2916 | 0.14648 | 0.1236 | 122.1405 | -0.1236 | -0.091553 | 122.3373 | 122.374 | 122.2321 | 0.23346 | 0.091553 | 0.25177 | 0.091553 | 0.19684 | 0.12817 | 0.16479 | 0.09613 | 122.3328 | 122.2366 | -0.19226 | -0.21973 | 122.2595 | 122.2687 | 122.2916 | 122.2229
2025.7031 | 122.5525 | -122.4335 | 0.13275 | -0.0096891 | 0.018199 | 0.0099656 | -0.00056607 | 0.020352 | -0.0025166 | 0.00067925 | -0.0043029 | 0.052225 | 0.007605 | -0.0023456 | -0.00030343 | 0.013941 | -0.0017196 | -0.082397 | 0.12817 | -0.11444 | -0.11444 | 0.032043 | -0.041199 | -0.036621 | -0.10071 | 0.10529 | -0.082397 | -0.036621 | 0.068665 | -0.027466 | 0.10529 | 122.319 | -0.004577 | -0.24719 | 122.4655 | 122.3969 | 122.3923 | 0.07782 | 0.073242 | 122.3511 | -0.027465 | -0.16937 | 122.5021 | 122.5388 | 122.406 | 0.18768 | 0.054931 | 0.14648 | 0 | 0.15106 | 0.045776 | 0.24262 | 0.18768 | 122.5616 | 122.5388 | -0.24719 | -0.21515 | 122.319 | 122.3969 | 122.3511 | 122.3328
2027.4062 | 122.612 | -122.3831 | 0.10071 | -0.0096891 | 0.017344 | 0.010393 | -0.00099327 | 0.020352 | -0.0031574 | -0.0010298 | -0.0012513 | 0.048379 | 0.010168 | -0.0010638 | -8.9634e-05 | 0.015223 | 0.0010574 | -0.050354 | 0.10986 | -0.07782 | -0.059509 | 0.11444 | -0.013733 | 0.018311 | -0.10071 | 0.045776 | -0.11444 | -0.027466 | 0.07782 | -0.004578 | 0.10986 | 122.3053 | 0.009155 | -0.16022 | 122.4976 | 122.4014 | 122.3694 | 0.096131 | 0.064087 | 122.2687 | -0.054932 | -0.12817 | 122.4609 | 122.493 | 122.3785 | 0.2243 | 0.10986 | 0.19226 | 0.018311 | 0.19226 | 0.086975 | 0.18768 | 0.16022 | 122.493 | 122.4289 | -0.17853 | -0.21515 | 122.3236 | 122.3557 | 122.3328 | 122.2824
2029.0938 | 122.6898 | -122.3831 | 0.10529 | -0.0020601 | 0.01649 | 0.011034 | -0.0029159 | 0.02142 | -0.003371 | -0.0012434 | -0.0043029 | 0.047952 | 0.0067504 | -0.0019184 | 0.001192 | 0.016077 | -1.0598e-05 | -0.013733 | 0.09613 | -0.091553 | 0.022888 | 0.20142 | 0.07782 | 0.10071 | 0.064087 | 0.059509 | -0.10986 | 0.073242 | 0.18768 | 0.10071 | 0.18768 | 122.2916 | -0.009156 | -0.082398 | 122.5845 | 122.4838 | 122.4609 | 0.19226 | 0.16937 | 122.2733 | -0.045777 | -0.032044 | 122.5708 | 122.5708 | 122.4838 | 0.29755 | 0.21057 | 0.29297 | 0.11444 | 0.29755 | 0.18311 | 0.18768 | 0.16937 | 122.4792 | 122.4426 | -0.19684 | -0.21515 | 122.406 | 122.4564 | 122.3694 | 122.4472
2030.8594 | 122.58 | -122.3923 | 0.11902 | -0.017319 | 0.020121 | 0.011461 | -0.00099327 | 0.022488 | -0.0027302 | -0.0016706 | -0.0043029 | 0.052652 | 0.01145 | -0.014095 | 0.0031146 | 0.015009 | -0.0017196 | -0.018311 | 0.1236 | -0.10986 | -0.036621 | 0.11902 | -0.009155 | 0.004578 | -0.041199 | 0.086975 | -0.10071 | -0.027466 | 0.041199 | -0.045776 | 0.091553 | 122.2824 | 0.004577 | -0.15564 | 122.5113 | 122.3969 | 122.3831 | 0.11444 | 0.10071 | 122.2916 | -0.032044 | -0.14649 | 122.4335 | 122.4838 | 122.3465 | 0.19226 | 0.054932 | 0.22888 | 0.073242 | 0.14191 | 0.073242 | 0.23346 | 0.18768 | 122.5159 | 122.4792 | -0.22888 | -0.21973 | 122.3557 | 122.3648 | 122.374 | 122.3511
2032.625 | 122.6807 | -122.3602 | 0.11444 | 0.0055694 | 0.015422 | 0.012956 | -0.0039841 | 0.02377 | 4.7018e-05 | 0.0013202 | -0.0073547 | 0.050088 | 0.0080322 | -0.00555 | 0.0061054 | 0.016718 | 0.0006302 | 0.022888 | 0.091553 | -0.054932 | 0.018311 | 0.16937 | 0.027466 | 0.050354 | -0.036621 | -0.022888 | -0.16022 | -0.004578 | 0.09613 | -0.018311 | 0.10529 | 122.3053 | -0.022888 | -0.09613 | 122.5296 | 122.4106 | 122.3877 | 0.10529 | 0.082398 | 122.2 | -0.13733 | -0.11902 | 122.4564 | 122.4655 | 122.3419 | 0.2655 | 0.14191 | 0.22431 | 0.073243 | 0.25635 | 0.15564 | 0.14649 | 0.13733 | 122.4518 | 122.3373 | -0.16937 | -0.27466 | 122.3785 | 122.3557 | 122.3831 | 122.3236
2034.375 | 122.6349 | -122.3923 | 0.09613 | -0.0096891 | 0.016703 | 0.011034 | -0.0018479 | 0.021634 | -0.0027302 | -0.0018842 | -0.0012513 | 0.050729 | 0.006964 | -0.0059772 | 0.0039692 | 0.015009 | -0.0002244 | -0.064087 | 0.11444 | -0.064087 | -0.036621 | 0.11444 | -0.018311 | 0.022888 | -0.10071 | 0.022888 | -0.14648 | -0.036621 | 0.045776 | -0.036621 | 0.10071 | 122.3282 | 0.018311 | -0.13275 | 122.5067 | 122.4152 | 122.374 | 0.086975 | 0.045776 | 122.2458 | -0.073242 | -0.13275 | 122.438 | 122.493 | 122.3557 | 0.24719 | 0.10986 | 0.17853 | 0.027466 | 0.19226 | 0.10986 | 0.17853 | 0.16937 | 122.5067 | 122.4152 | -0.16022 | -0.24261 | 122.3557 | 122.3557 | 122.3282 | 122.2916
2036.0781 | 122.5891 | -122.4197 | 0.12817 | -0.0020601 | 0.016276 | 0.011034 | -0.0016343 | 0.022061 | -0.0014484 | -0.001457 | -0.0043029 | 0.051584 | 0.005896 | -0.0093952 | 0.00097837 | 0.014155 | 0.000203 | -0.068665 | 0.13733 | -0.10986 | -0.10071 | 0.027466 | -0.032043 | -0.027466 | -0.10529 | 0.086975 | -0.091553 | -0.041199 | 0.050354 | -0.036621 | 0.10529 | 122.3099 | 0.009155 | -0.22888 | 122.4472 | 122.3923 | 122.3877 | 0.082397 | 0.07782 | 122.3282 | -0.041199 | -0.16937 | 122.4701 | 122.525 | 122.3831 | 0.19684 | 0.054932 | 0.13733 | 0.009155 | 0.14191 | 0.050354 | 0.24719 | 0.17853 | 122.5571 | 122.5067 | -0.23804 | -0.21973 | 122.319 | 122.3785 | 122.3511 | 122.3145
2037.8281 | 122.1176 | -121.9025 | 0.11902 | -0.017319 | 0.015635 | 0.009752 | -0.0022751 | 0.023129 | -0.00038018 | -0.00038875 | -0.0012513 | 0.049447 | 0.010382 | -0.0023456 | 0.00461 | 0.014155 | 0.0021256 | -0.041199 | 0.091553 | -0.054932 | -0.041199 | 0.14648 | 0.004578 | 0.032043 | -0.004578 | 0.091553 | -0.032043 | 0.036621 | 0.13275 | 0.036621 | 0.16479 | 121.8475 | -0.027466 | -0.16022 | 122.049 | 121.9345 | 121.907 | 0.086975 | 0.05951 | 121.8704 | -0.027466 | -0.082398 | 122.0352 | 122.0673 | 121.9391 | 0.19684 | 0.068664 | 0.20142 | 0.013733 | 0.16479 | 0.068664 | 0.14649 | 0.1236 | 121.994 | 121.994 | -0.17395 | -0.15106 | 121.8613 | 121.9391 | 121.8613 | 121.8979
2039.5938 | 122.4609 | -122.1863 | 0.10071 | -0.0020601 | 0.017344 | 0.010393 | -0.0033433 | 0.021206 | -0.0023028 | -0.0018842 | -0.0043029 | 0.048593 | 0.0082458 | -0.0023456 | -0.00073063 | 0.016291 | 0.0021256 | -0.009155 | 0.11902 | -0.068665 | 0.032043 | 0.21973 | 0.10071 | 0.082397 | 0.13275 | 0.13733 | 0 | 0.11902 | 0.25177 | 0.14191 | 0.24719 | 122.1176 | 0.018311 | -0.068665 | 122.406 | 122.2687 | 122.287 | 0.15106 | 0.16937 | 122.1863 | 0.036621 | 0.018311 | 122.438 | 122.4335 | 122.3282 | 0.24719 | 0.14191 | 0.28839 | 0.10071 | 0.25177 | 0.11902 | 0.18768 | 0.13733 | 122.3053 | 122.3236 | -0.16937 | -0.10071 | 122.2183 | 122.3053 | 122.1771 | 122.319
2041.3594 | 122.5021 | -122.1954 | 0.11902 | 0.0055694 | 0.017131 | 0.01317 | -0.0016343 | 0.026333 | -0.0014484 | -0.0020978 | -0.01651 | 0.05137 | 0.0084594 | 4.214e-06 | 0.0056782 | 0.014795 | 0.0004166 | 0.004578 | 0.059509 | -0.041199 | 0.022888 | 0.1831 | 0.027466 | 0.068665 | 0.059509 | 0.050354 | -0.054932 | 0.086975 | 0.15564 | 0.050354 | 0.18768 | 122.1542 | -0.05951 | -0.096131 | 122.3785 | 122.2641 | 122.2229 | 0.10986 | 0.068665 | 122.1405 | -0.068665 | -0.032044 | 122.3511 | 122.3831 | 122.2458 | 0.24261 | 0.10529 | 0.2243 | 0.064087 | 0.21057 | 0.14191 | 0.10071 | 0.10529 | 122.2549 | 122.2458 | -0.16022 | -0.17395 | 122.2183 | 122.2824 | 122.2 | 122.2549
2043.0312 | 122.4609 | -122.2366 | 0.1236 | -0.0020601 | 0.018626 | 0.0099656 | -0.00099327 | 0.020138 | -0.0023028 | -0.00038875 | -0.0043029 | 0.052865 | 0.0080322 | -0.010463 | -0.001585 | 0.014795 | -0.0019332 | -0.064087 | 0.1236 | -0.10986 | -0.07782 | 0.07782 | -0.022888 | 0 | 0.009155 | 0.17853 | -0.009155 | 0.050354 | 0.14191 | 0.041199 | 0.18768 | 122.1268 | 0 | -0.20142 | 122.3145 | 122.2366 | 122.2137 | 0.10986 | 0.086975 | 122.2275 | 0.054932 | -0.073242 | 122.3785 | 122.4243 | 122.2778 | 0.19684 | 0.050354 | 0.18768 | 0.032043 | 0.15106 | 0.059509 | 0.23346 | 0.18768 | 122.3602 | 122.4152 | -0.23346 | -0.13275 | 122.1588 | 122.287 | 122.1725 | 122.2458
2044.7812 | 122.4243 | -122.2824 | 0.14648 | -0.0096891 | 0.016276 | 0.010606 | -0.0039841 | 0.02142 | -0.0020892 | -0.001457 | -0.0043029 | 0.052011 | 0.0080322 | -0.008327 | -0.002226 | 0.013086 | 0.0021256 | -0.09613 | 0.14191 | -0.10986 | -0.10529 | 0.064087 | -0.041199 | -0.045776 | -0.041199 | 0.19226 | -0.013733 | 0.004578 | 0.10986 | 0.018311 | 0.14648 | 122.1725 | -0.004577 | -0.25177 | 122.3465 | 122.2366 | 122.2412 | 0.064087 | 0.068664 | 122.2687 | 0.045777 | -0.14191 | 122.3923 | 122.4289 | 122.3007 | 0.16022 | 0.032044 | 0.17395 | 0.004577 | 0.1236 | 0.018311 | 0.25177 | 0.20599 | 122.4243 | 122.4747 | -0.25635 | -0.16022 | 122.1771 | 122.287 | 122.1863 | 122.2412
2046.5469 | 122.5571 | -122.2458 | 0.10529 | -0.0020601 | 0.019694 | 0.012956 | -0.00099327 | 0.018857 | -0.0018756 | -0.001457 | -0.0012513 | 0.049875 | 0.0082458 | -0.0019184 | 0.0041828 | 0.017145 | -0.000438 | -0.004578 | 0.10071 | -0.068665 | 0.013733 | 0.18768 | 0.027466 | 0.050354 | 0.054932 | 0.07782 | -0.064087 | 0.07782 | 0.14191 | 0.050354 | 0.18768 | 122.1771 | -0.004578 | -0.091553 | 122.4335 | 122.2961 | 122.2733 | 0.11902 | 0.096131 | 122.1817 | -0.027466 | -0.027466 | 122.3877 | 122.4335 | 122.2961 | 0.25177 | 0.11444 | 0.25635 | 0.082398 | 0.20599 | 0.14191 | 0.16937 | 0.14191 | 122.3465 | 122.3236 | -0.17395 | -0.16937 | 122.2595 | 122.3236 | 122.2412 | 122.3007
2048.2344 | 122.5754 | -122.2458 | 0.10529 | 0.0055694 | 0.017771 | 0.012956 | -0.0022751 | 0.020993 | -0.0029438 | 0.0017474 | -0.0012513 | 0.050516 | 0.0067504 | -0.00555 | 0.003542 | 0.016504 | -0.0030014 | -0.009155 | 0.091553 | -0.07782 | 0.018311 | 0.17395 | 0.032043 | 0.050354 | 0.045776 | 0.059509 | -0.050354 | 0.086975 | 0.15564 | 0.054932 | 0.19684 | 122.168 | -0.013733 | -0.086975 | 122.4197 | 122.2961 | 122.2778 | 0.12817 | 0.10986 | 122.1954 | -0.045777 | -0.018311 | 122.4014 | 122.4426 | 122.3007 | 0.24719 | 0.10529 | 0.25177 | 0.096131 | 0.20599 | 0.13733 | 0.16937 | 0.10986 | 122.3373 | 122.3053 | -0.18311 | -0.15564 | 122.2641 | 122.3328 | 122.2366 | 122.2916
2050 | 122.5113 | -122.2916 | 0.13733 | -0.0020601 | 0.018412 | 0.012315 | -0.00099327 | 0.024197 | -0.003371 | 0.0023882 | 0.0048523 | 0.050729 | 0.007605 | -0.011104 | 0.0014056 | 0.014155 | -0.0002244 | -0.022888 | 0.14191 | -0.10071 | -0.059509 | 0.10529 | -0.009155 | 0 | 0.027466 | 0.15106 | -0.027466 | 0.064087 | 0.14191 | 0.054932 | 0.18768 | 122.1909 | 0.004578 | -0.19684 | 122.3969 | 122.2916 | 122.2824 | 0.10071 | 0.091553 | 122.2641 | 0.013733 | -0.073242 | 122.4335 | 122.4792 | 122.3465 | 0.21515 | 0.082398 | 0.20599 | 0.041199 | 0.16937 | 0.091553 | 0.24262 | 0.17853 | 122.4335 | 122.4426 | -0.23804 | -0.16479 | 122.2321 | 122.3557 | 122.2687 | 122.319
2051.75 | 122.4747 | -122.3236 | 0.15106 | 0.0055694 | 0.016703 | 0.010393 | -0.0018479 | 0.022061 | -0.0029438 | 0.00089285 | -0.010406 | 0.051156 | 0.0099548 | -0.0046954 | -0.0030804 | 0.0133 | 0.0016982 | -0.10071 | 0.15106 | -0.1236 | -0.10986 | 0.045776 | -0.059509 | -0.045776 | -0.050354 | 0.17853 | -0.018311 | 0.004578 | 0.10529 | 0.018311 | 0.15564 | 122.2 | 0 | -0.26093 | 122.3694 | 122.2778 | 122.2641 | 0.07782 | 0.064087 | 122.3053 | 0.027466 | -0.14648 | 122.4289 | 122.4792 | 122.3419 | 0.17395 | 0.036622 | 0.16937 | 0.013733 | 0.1236 | 0.022889 | 0.27466 | 0.19684 | 122.4747 | 122.5021 | -0.27466 | -0.16937 | 122.2137 | 122.3282 | 122.2229 | 122.2733
2053.5 | 117.1783 | -78.3966 | 38.5025 | 0.0055694 | 0.019053 | 0.009752 | -0.00056607 | 0.020352 | -0.0018756 | 0.00067925 | 0.0018005 | 0.05137 | 0.0099548 | -0.0087542 | 0.00076477 | 0.014795 | 0.001912 | -0.091553 | 0.10529 | -0.14648 | -0.13275 | 0.027466 | -0.10071 | -0.064087 | 1.9913 | 2.1423 | 1.918 | 1.9913 | 2.0325 | 1.9547 | 2.1286 | 78.2501 | -38.3972 | -38.6353 | 78.4241 | 78.3325 | 78.2959 | 0.082397 | 0.045776 | 80.3146 | -36.3602 | -36.5112 | 80.4291 | 80.5252 | 80.3513 | 0.21057 | 0.036621 | 0.17395 | 0.013733 | 0.11444 | 0.073242 | 0.25177 | 0.2243 | 78.5019 | 80.5389 | -38.649 | -36.5845 | 78.2639 | 80.3879 | 78.3051 | 80.3879
2055.25 | 122.3511 | -122.081 | 0.09613 | 0.013199 | 0.016703 | 0.012102 | -0.0012069 | 0.026547 | 0.00068782 | -0.001457 | 0.0018005 | 0.049661 | 0.008673 | 0.0034222 | 0.003542 | 0.015864 | -0.0002244 | -0.009155 | 0.10529 | -0.073242 | 0.004578 | 0.16479 | 0.018311 | 0.045776 | 0.027466 | 0.07782 | -0.050354 | 0.082397 | 0.14648 | 0.059509 | 0.21057 | 122.0078 | 0.009156 | -0.091552 | 122.2458 | 122.1268 | 122.0993 | 0.11902 | 0.091553 | 122.0306 | -0.01831 | -0.013733 | 122.2275 | 122.2916 | 122.1405 | 0.26093 | 0.10986 | 0.23804 | 0.07782 | 0.19684 | 0.13275 | 0.17853 | 0.12817 | 122.1863 | 122.1588 | -0.16937 | -0.14648 | 122.0856 | 122.1634 | 122.0718 | 122.1085
2056.9688 | 122.1588 | -121.7194 | 0.10071 | 0.11238 | 0.015422 | 0.012315 | -0.0041977 | 0.023556 | -0.0012348 | -0.0012434 | -0.0012513 | 0.050516 | 0.0091002 | -0.00042299 | 0.0041828 | 0.018 | -0.0006516 | -0.10529 | 0.09613 | 0.15106 | 0 | 0.13733 | 0.041199 | 0.054932 | 0.027466 | -0.21057 | 0.21057 | 0.064087 | 0.054932 | -0.041199 | 0.086975 | 121.8704 | -0.004578 | -0.10071 | 121.8567 | 121.7743 | 121.7606 | -0.09613 | -0.10986 | 121.9299 | -0.31128 | -0.036621 | 121.7743 | 121.8063 | 121.6782 | -0.1236 | -0.25177 | -0.013733 | -0.15106 | -0.15564 | -0.14648 | -0.054932 | -0.42114 | 121.8155 | 121.5088 | 0.050354 | 0.10986 | 121.7194 | 121.7834 | 121.6141 | 121.7468
2058.7344 | 122.0673 | -121.6644 | 0.091553 | 0.0055694 | 0.017131 | 0.014238 | -0.00013887 | 0.020779 | 4.7018e-05 | -0.0027386 | -0.013458 | 0.048379 | 0.0084594 | 0.00043161 | 0.003542 | 0.016932 | 0.0023392 | 0.004578 | 0.09613 | -0.045776 | -0.050354 | 0.013733 | -0.10986 | -0.15106 | 0.041199 | -0.027466 | 0.09613 | 0.086975 | 0.1236 | -0.013733 | 0.10986 | 121.6187 | 0.004577 | -0.14191 | 121.6782 | 121.5134 | 121.5546 | -0.10529 | -0.064087 | 121.7606 | -0.11902 | -0.004578 | 121.788 | 121.7743 | 121.6507 | 0.013733 | -0.10986 | 0.059509 | -0.004578 | 0.027466 | -0.009155 | 0.14191 | -0.1236 | 121.7606 | 121.637 | -0.13733 | 0.004577 | 121.6141 | 121.7514 | 121.669 | 121.7056
2060.4375 | 121.8201 | -121.431 | 0.10529 | 0.0055694 | 0.016276 | 0.014452 | -0.0046249 | 0.022488 | -0.0029438 | 0.00046565 | -0.025665 | 0.049661 | 0.0073914 | 0.0021404 | -8.9634e-05 | 0.014368 | 0.0016982 | -0.027466 | 0.045776 | 0.24261 | 0.004578 | 0.07782 | -0.068665 | -0.10986 | 0.086975 | -0.13733 | 0.32044 | 0.10529 | 0.091553 | -0.013733 | 0.091553 | 121.6736 | -0.05951 | -0.10071 | 121.5088 | 121.3211 | 121.3623 | -0.35248 | -0.31128 | 121.7514 | -0.24262 | 0 | 121.5225 | 121.5225 | 121.4172 | -0.22888 | -0.33417 | -0.16479 | -0.23804 | -0.22888 | -0.21515 | -0.19684 | -0.45776 | 121.4767 | 121.2936 | 0.13733 | 0.21515 | 121.4355 | 121.5363 | 121.4035 | 121.5179
2062.1875 | 121.9849 | -121.7697 | 0.14191 | 0.0055694 | 0.0092263 | 0.12938 | -0.0031297 | 0.034451 | 0.066911 | 0.055367 | 0.044525 | 0.060342 | 0.0061096 | -0.011959 | -0.015684 | -0.0014397 | -0.017101 | -0.21973 | 0.15564 | -0.013733 | -0.47607 | 0.086975 | 0.082397 | 0.07782 | -0.064087 | -0.073242 | 0.29297 | -0.11444 | -0.032043 | 0.082397 | 0.086975 | 121.756 | 0.013733 | -0.61798 | 121.8567 | 121.8475 | 121.8521 | 0.091553 | 0.09613 | 122.0627 | -0.21515 | -0.25635 | 121.7377 | 121.8567 | 121.8521 | -0.20599 | -0.21057 | 0.10071 | -0.46234 | -0.32501 | -0.40741 | 0.16937 | -0.36621 | 121.9254 | 121.6965 | -0.15564 | 0.15106 | 121.2936 | 121.6553 | 121.55 | 121.7056
2063.9531 | 122.0352 | -121.8613 | 0.13275 | 0.013199 | 0.018412 | 0.0016342 | -0.012529 | 0.018857 | -0.021102 | 0.057717 | 0.050629 | 0.062051 | -0.0058534 | -0.019649 | -0.013762 | -0.0012261 | -0.012614 | -0.15106 | 0.14191 | -0.11444 | -0.42572 | -0.068665 | -0.2243 | 0.086975 | -0.045776 | 0.041199 | 0.20142 | -0.018311 | -0.32044 | -0.19226 | 0.073242 | 121.7468 | 0.009156 | -0.55847 | 121.7926 | 121.9482 | 121.637 | 0.20142 | -0.10986 | 122.0627 | -0.091552 | -0.15106 | 121.5408 | 121.9345 | 121.669 | -0.12817 | -0.39368 | 0.045776 | -0.31128 | -0.52185 | -0.21973 | 0.25635 | -0.16022 | 122.0032 | 121.9025 | -0.24719 | 0.068665 | 121.4355 | 121.843 | 121.7102 | 121.8155
2065.7031 | 122.1725 | -121.8613 | 0.10986 | 0.013199 | 0.01649 | 0.012529 | -0.0035569 | 0.020779 | -0.0037982 | 0.00046565 | -0.037872 | 0.04902 | 0.007605 | -0.0040546 | 0.00076477 | 0.015223 | 0.0014846 | -0.027466 | 0.091553 | -0.073242 | 0.013733 | 0.20142 | 0.086975 | 0.041199 | 0.11444 | 0.13275 | -0.018311 | 0.11444 | 0.21057 | 0.14648 | 0.2243 | 121.788 | -0.01831 | -0.09613 | 122.0627 | 121.9025 | 121.9482 | 0.11444 | 0.16022 | 121.843 | 0.022888 | 0.004578 | 122.0718 | 122.0856 | 122.0078 | 0.24261 | 0.16479 | 0.27466 | 0.086975 | 0.22888 | 0.13275 | 0.16479 | 0.15106 | 121.9528 | 121.994 | -0.18311 | -0.12817 | 121.875 | 121.9757 | 121.8338 | 121.9757
2067.4062 | 122.0673 | -121.9299 | 0.13733 | 0.013199 | 0.017344 | 0.013384 | -0.00099327 | 0.022275 | -0.0014484 | 0.00067925 | -0.074493 | 0.049661 | 0.0078186 | 0.0032086 | -0.0020122 | 0.012873 | 0.0027664 | -0.045776 | 0.11444 | -0.10071 | -0.07782 | 0.091553 | -0.022888 | -0.12817 | 0.004578 | 0.16022 | -0.032043 | 0.018311 | 0.082397 | -0.032043 | -0.009155 | 121.8292 | -0.022888 | -0.21515 | 122.0215 | 121.8018 | 121.907 | -0.027466 | 0.07782 | 121.8979 | 0.022888 | -0.11902 | 122.0123 | 121.9208 | 121.8979 | 0.022888 | 0 | 0.19226 | 0.022888 | 0.11444 | 0.050354 | 0.21515 | 0.19226 | 122.0444 | 122.0901 | -0.23804 | -0.16937 | 121.8521 | 121.9482 | 121.8842 | 121.9345
2069.0938 | 121.9574 | -121.9345 | 0.15106 | 0.0055694 | 0.016703 | 0.013597 | 0.0011429 | 0.01373 | -0.0025166 | -0.0029524 | -0.18436 | 0.037698 | 0.0067504 | -0.00042299 | 0.0041828 | 0.014795 | -0.0012924 | -0.07782 | 0.12817 | -0.10986 | -0.13275 | -0.082397 | -0.24719 | -0.3891 | -0.091553 | 0.11902 | -0.086975 | -0.032043 | 0 | -0.21973 | -0.18768 | 121.8246 | -0.022888 | -0.28381 | 121.8521 | 121.5454 | 121.6873 | -0.27924 | -0.13733 | 121.8475 | -0.032043 | -0.18311 | 121.9345 | 121.7468 | 121.7148 | -0.10071 | -0.13275 | 0.027466 | -0.022888 | 0.086975 | 0.054932 | 0.23804 | 0.20599 | 122.0627 | 122.0535 | -0.26093 | -0.23804 | 121.8018 | 121.9025 | 121.8567 | 121.843
2070.8438 | 122.2366 | -121.9162 | 0.10529 | 0.013199 | 0.014994 | 0.012102 | -0.0031297 | 0.019711 | -0.0035846 | -0.00081595 | 0.0048523 | 0.049661 | 0.005896 | -0.0036274 | -0.0013714 | 0.014155 | 0.0027664 | -0.018311 | 0.086975 | -0.07782 | 0.027466 | 0.21515 | 0.10529 | 0.086975 | 0.12817 | 0.11444 | -0.004578 | 0.13275 | 0.23346 | 0.12817 | 0.25635 | 121.8384 | -0.018311 | -0.07782 | 122.1313 | 122.0032 | 122.0215 | 0.16479 | 0.18311 | 121.9116 | 0.009155 | 0.027465 | 122.1497 | 122.1725 | 122.0444 | 0.26093 | 0.13275 | 0.29297 | 0.10529 | 0.23804 | 0.13733 | 0.16479 | 0.11902 | 122.0032 | 122.0306 | -0.18311 | -0.10986 | 121.9437 | 122.049 | 121.8979 | 122.0444
2072.625 | 122.1863 | -121.9437 | 0.10986 | -0.0020601 | 0.016703 | 0.011675 | -0.0022751 | 0.019497 | -0.0020892 | -0.00081595 | 0.0048523 | 0.050302 | 0.0067504 | 0.0051312 | -0.00094423 | 0.016077 | -0.0017196 | -0.059509 | 0.10529 | -0.10986 | -0.059509 | 0.10071 | -0.004578 | 0.004578 | -0.018311 | 0.09613 | -0.059509 | 0.022888 | 0.10071 | 0.018311 | 0.16479 | 121.8338 | -0.004577 | -0.16937 | 122.0444 | 121.9482 | 121.9391 | 0.11444 | 0.10529 | 121.8842 | -0.013733 | -0.086975 | 122.0444 | 122.1085 | 121.962 | 0.2243 | 0.07782 | 0.21057 | 0.050354 | 0.16022 | 0.082397 | 0.21515 | 0.15564 | 122.049 | 122.0398 | -0.21973 | -0.16937 | 121.8842 | 121.9666 | 121.8842 | 121.9254
2074.3906 | 122.2229 | -121.9345 | 0.12817 | 0.0055694 | 0.017985 | 0.011888 | -0.00099327 | 0.020779 | -0.0010212 | -0.001457 | 0.0048523 | 0.05137 | 0.0033324 | 0.0014996 | 0.0037556 | 0.016291 | 0.0016982 | -0.068665 | 0.11902 | -0.09613 | -0.022888 | 0.11444 | 0.009155 | 0.041199 | 0.013733 | 0.11902 | -0.036621 | 0.073242 | 0.17395 | 0.091553 | 0.19684 | 121.8384 | -0.009155 | -0.15106 | 122.049 | 121.9757 | 121.9437 | 0.13733 | 0.10528 | 121.8979 | -0.009155 | -0.054932 | 122.1085 | 122.1313 | 122.0261 | 0.23346 | 0.12817 | 0.21057 | 0.073242 | 0.21057 | 0.10986 | 0.21515 | 0.15564 | 122.0535 | 122.0535 | -0.2243 | -0.1648 | 121.9116 | 122.0078 | 121.8658 | 121.9482
2076.0938 | 121.4493 | -121.4951 | 0.14648 | -0.0020601 | 0.017771 | 0.011247 | 0.00028833 | 0.016934 | -0.0014484 | 0.0047382 | -0.065338 | 0.037485 | 0.0071776 | -0.00555 | -0.0013714 | 0.011805 | 0.0034072 | -0.022888 | 0.13275 | -0.10529 | -0.059509 | 0.10529 | -0.027466 | -0.17853 | 0.018311 | 0.16479 | -0.041199 | 0.013733 | 0.086975 | -0.004578 | -0.064087 | 121.3898 | -0.013733 | -0.20599 | 121.6003 | 121.3165 | 121.4676 | -0.073242 | 0.07782 | 121.4539 | 0.018311 | -0.13275 | 121.582 | 121.431 | 121.4905 | -0.022888 | 0.036621 | 0.21057 | 0.045777 | 0.12817 | 0.054932 | 0.23804 | 0.20599 | 121.6278 | 121.6599 | -0.25177 | -0.18768 | 121.4355 | 121.5088 | 121.4722 | 121.5134
2077.8438 | 121.5546 | -121.5317 | 0.12817 | -0.0020601 | 0.017771 | 0.010393 | 0.0015701 | 0.023984 | -0.0018756 | 0.0030292 | -0.037872 | 0.049447 | 0.006964 | -0.0068316 | -0.0011578 | 0.015864 | 0.0004166 | -0.041199 | 0.14191 | -0.09613 | -0.068665 | 0.082397 | -0.018311 | -0.068665 | 0.022888 | 0.16022 | -0.045776 | 0.050354 | 0.14191 | 0.018311 | 0.059509 | 121.4355 | 0.013733 | -0.19684 | 121.6141 | 121.463 | 121.5134 | 0.027465 | 0.077819 | 121.4859 | 0.032043 | -0.07782 | 121.6736 | 121.5912 | 121.55 | 0.10528 | 0.064087 | 0.17853 | 0.027465 | 0.18768 | 0.09613 | 0.23804 | 0.20599 | 121.6736 | 121.6919 | -0.2243 | -0.17395 | 121.463 | 121.582 | 121.4905 | 121.5546
2079.6094 | 122.2412 | -121.9849 | 0.11444 | -0.0020601 | 0.016276 | 0.012529 | -0.0022751 | 0.020352 | -0.0027302 | 0.00067925 | 0.0048523 | 0.050302 | 0.0088866 | 0.0017132 | 0.0031146 | 0.016291 | -0.0006516 | -0.07782 | 0.10986 | -0.091553 | -0.036621 | 0.10986 | 0.009155 | 0.022888 | 0.013733 | 0.09613 | -0.032043 | 0.050354 | 0.14191 | 0.07782 | 0.19226 | 121.8933 | -0.004578 | -0.15106 | 122.0947 | 122.0078 | 121.994 | 0.11444 | 0.10071 | 121.9528 | -0.018311 | -0.064087 | 122.1268 | 122.1771 | 122.0627 | 0.2243 | 0.10986 | 0.20142 | 0.054932 | 0.17395 | 0.082397 | 0.20142 | 0.12817 | 122.0947 | 122.081 | -0.20599 | -0.14648 | 121.9482 | 122.0352 | 121.907 | 121.9986
2081.3125 | 122.2321 | -122.0169 | 0.12817 | -0.0020601 | 0.017558 | 0.010393 | -0.0033433 | 0.023984 | -0.0023028 | 0.00067925 | -0.0012513 | 0.049447 | 0.005896 | -0.0014912 | 0.001833 | 0.014368 | 0.0031936 | -0.068665 | 0.082397 | -0.073242 | -0.045776 | 0.091553 | -0.009155 | 0.013733 | -0.022888 | 0.091553 | -0.073242 | 0.027466 | 0.10986 | 0.045776 | 0.17395 | 121.9437 | -0.045777 | -0.17395 | 122.1085 | 122.0306 | 122.0078 | 0.086975 | 0.064087 | 121.9437 | -0.036621 | -0.10071 | 122.1268 | 122.1909 | 122.0627 | 0.24719 | 0.11902 | 0.16479 | 0.027466 | 0.18311 | 0.10071 | 0.15564 | 0.16479 | 122.0993 | 122.1085 | -0.20142 | -0.20142 | 121.9711 | 122.0444 | 121.9482 | 121.994
2083 | 122.2641 | -122.0169 | 0.10529 | -0.0096891 | 0.017131 | 0.011034 | 0.00071573 | 0.019497 | -0.0031574 | 0.0026018 | 0.0018005 | 0.049447 | 0.0050414 | 0.0061994 | 0.0020466 | 0.015223 | -0.0017196 | -0.050354 | 0.10986 | -0.091553 | -0.045776 | 0.10529 | -0.004578 | 0.041199 | 0 | 0.10986 | -0.050354 | 0.045776 | 0.14648 | 0.050354 | 0.17853 | 121.9254 | 0.004577 | -0.15106 | 122.1222 | 122.0581 | 122.0123 | 0.13275 | 0.086975 | 121.9666 | 0.004577 | -0.05951 | 122.1634 | 122.1954 | 122.0673 | 0.22888 | 0.10071 | 0.19684 | 0.045777 | 0.19684 | 0.09613 | 0.20142 | 0.16022 | 122.1268 | 122.1268 | -0.19684 | -0.15564 | 121.9711 | 122.0627 | 121.9666 | 122.0169
2084.75 | 121.8384 | -121.5637 | 0.13275 | -0.017319 | 0.019053 | 0.012743 | 7.473e-05 | 0.019925 | -0.0012348 | -0.0040204 | 0.0018005 | 0.052011 | 0.0067504 | -0.008968 | 0.00097837 | 0.012873 | -0.0019332 | -0.054932 | 0.13275 | -0.10529 | -0.082397 | 0.041199 | -0.045776 | -0.018311 | 0.013733 | 0.16937 | -0.022888 | 0.032043 | 0.13275 | 0.022888 | 0.16479 | 121.4584 | 0 | -0.21515 | 121.6049 | 121.5454 | 121.5179 | 0.086975 | 0.05951 | 121.5408 | 0.036622 | -0.10071 | 121.6965 | 121.7285 | 121.5866 | 0.18768 | 0.045776 | 0.14649 | 0.022889 | 0.15564 | 0.054931 | 0.23804 | 0.19226 | 121.6965 | 121.7331 | -0.23804 | -0.15564 | 121.4813 | 121.5958 | 121.5088 | 121.5775
2086.5312 | 122.3099 | -121.9894 | 0.10071 | 0.0055694 | 0.01649 | 0.012102 | -0.0033433 | 0.02142 | -0.0027302 | -0.0016706 | 0.0048523 | 0.050088 | 0.005255 | 0.0017132 | 0.0039692 | 0.013941 | -0.0012924 | -0.009155 | 0.09613 | -0.059509 | 0.050354 | 0.21973 | 0.091553 | 0.082397 | 0.13275 | 0.12817 | -0.022888 | 0.11444 | 0.22888 | 0.14191 | 0.21973 | 121.9299 | -0.004578 | -0.050354 | 122.2092 | 122.0718 | 122.081 | 0.14191 | 0.15106 | 121.9666 | 0.027466 | 0.013733 | 122.2183 | 122.2092 | 122.1313 | 0.24261 | 0.16479 | 0.27924 | 0.10986 | 0.25177 | 0.13733 | 0.15564 | 0.15106 | 122.0856 | 122.1176 | -0.16022 | -0.1236 | 122.0398 | 122.1039 | 121.9803 | 122.1222
2088.2188 | 122.3099 | -122.0215 | 0.10986 | -0.0020601 | 0.015849 | 0.010179 | 7.473e-05 | 0.022061 | -0.0042254 | -0.001457 | -0.0012513 | 0.04902 | 0.006964 | 0.0051312 | 0.001192 | 0.014582 | 0.0008438 | -0.054932 | 0.082397 | -0.086975 | -0.009155 | 0.13733 | 0.032043 | 0.054932 | 0.045776 | 0.10529 | -0.059509 | 0.07782 | 0.19226 | 0.10529 | 0.19684 | 121.9345 | -0.027466 | -0.11902 | 122.1588 | 122.0764 | 122.0535 | 0.14191 | 0.11902 | 121.962 | -0.004577 | -0.032043 | 122.2137 | 122.2183 | 122.1268 | 0.25635 | 0.16479 | 0.2243 | 0.07782 | 0.25177 | 0.13733 | 0.16937 | 0.16479 | 122.1039 | 122.1268 | -0.19684 | -0.16937 | 122.0123 | 122.0993 | 121.9666 | 122.0673
2089.9688 | 122.2595 | -122.0123 | 0.10071 | 0.0055694 | 0.017131 | 0.01082 | -0.00013887 | 0.021634 | -0.0018756 | 0.00025205 | -0.0043029 | 0.048379 | 0.0061096 | -0.0040546 | 0.0022602 | 0.013727 | 0.0034072 | -0.032043 | 0.073242 | -0.054932 | -0.027466 | 0.13733 | 0.004578 | 0.036621 | 0.022888 | 0.068665 | -0.059509 | 0.027466 | 0.1236 | 0.041199 | 0.14648 | 121.9574 | -0.027466 | -0.12817 | 122.1497 | 122.0489 | 122.0169 | 0.091553 | 0.05951 | 121.9528 | -0.032043 | -0.073242 | 122.1359 | 122.1588 | 122.0535 | 0.20599 | 0.10071 | 0.19226 | 0.027466 | 0.1831 | 0.086975 | 0.12817 | 0.12817 | 122.0856 | 122.081 | -0.15564 | -0.16022 | 121.9849 | 122.0398 | 121.9803 | 122.0352
2091.6719 | 122.3236 | -122.0261 | 0.10986 | -0.0020601 | 0.019267 | 0.014452 | -0.00099327 | 0.019497 | -0.00080758 | -0.00038875 | 0.0048523 | 0.050516 | 0.0082458 | 4.214e-06 | 0.00461 | 0.016504 | -0.0006516 | 0 | 0.091553 | -0.054932 | 0.013733 | 0.18768 | 0.022888 | 0.054932 | 0.073242 | 0.082397 | -0.059509 | 0.073242 | 0.16022 | 0.050354 | 0.19226 | 121.9711 | -0.01831 | -0.09613 | 122.2137 | 122.081 | 122.0489 | 0.10986 | 0.07782 | 121.9666 | -0.027466 | -0.036621 | 122.1863 | 122.2183 | 122.0764 | 0.25177 | 0.10986 | 0.24261 | 0.068665 | 0.21973 | 0.13275 | 0.14649 | 0.14191 | 122.1176 | 122.1085 | -0.16479 | -0.16937 | 122.0398 | 122.0993 | 122.0261 | 122.0993
2093.4375 | 122.2229 | -122.0856 | 0.13275 | -0.0020601 | 0.015422 | 0.012102 | 7.473e-05 | 0.018216 | -0.0031574 | 0.001961 | 0.0018005 | 0.050088 | 0.0067504 | -0.0012774 | -0.002226 | 0.013086 | 0.0031936 | -0.027466 | 0.10529 | -0.086975 | -0.032043 | 0.10529 | 0.004578 | 0.018311 | -0.009155 | 0.16937 | -0.022888 | -0.004578 | 0.11902 | 0.009155 | 0.14191 | 121.9986 | -0.027465 | -0.16479 | 122.1909 | 122.1039 | 122.0901 | 0.10529 | 0.091553 | 122.0627 | 0.036622 | -0.13733 | 122.2046 | 122.2275 | 122.0947 | 0.16479 | 0.032043 | 0.19226 | 0.054932 | 0.14191 | 0.01831 | 0.19226 | 0.19226 | 122.1909 | 122.2549 | -0.21973 | -0.15564 | 122.0535 | 122.081 | 122.0581 | 122.0764
2095.125 | 122.2137 | -122.0947 | 0.13733 | -0.0020601 | 0.017558 | 0.009752 | 0.00028833 | 0.019497 | -0.0023028 | -0.0027386 | 0.0018005 | 0.051584 | 0.0061096 | -0.011104 | -0.0017986 | 0.012446 | -0.0006516 | -0.050354 | 0.11902 | -0.10986 | -0.073242 | 0.086975 | -0.032043 | -0.013733 | -0.013733 | 0.17395 | -0.032043 | -0.004578 | 0.10071 | 0.018311 | 0.1236 | 121.9849 | -0.01831 | -0.21057 | 122.1817 | 122.081 | 122.0627 | 0.09613 | 0.07782 | 122.0627 | 0.036621 | -0.14191 | 122.1954 | 122.2183 | 122.113 | 0.15564 | 0.050354 | 0.19684 | 0.036621 | 0.13275 | 0.027465 | 0.22888 | 0.20599 | 122.2137 | 122.2687 | -0.24719 | -0.16937 | 122.0215 | 122.0901 | 122.0444 | 122.081
2096.8281 | 122.3602 | -122.0718 | 0.10529 | 0.013199 | 0.015422 | 0.012529 | -0.0027023 | 0.019925 | -0.0029438 | -0.003166 | 0.0048523 | 0.049875 | 0.0073914 | 4.214e-06 | 0.0014056 | 0.014368 | 0.003621 | -0.022888 | 0.091553 | -0.07782 | 0.018311 | 0.19226 | 0.064087 | 0.086975 | 0.10986 | 0.10986 | -0.027466 | 0.10986 | 0.2243 | 0.14191 | 0.22888 | 121.994 | -0.013733 | -0.086975 | 122.2641 | 122.1588 | 122.1359 | 0.16479 | 0.14191 | 122.0444 | 0.004577 | 0.004577 | 122.2961 | 122.3007 | 122.2137 | 0.25635 | 0.16937 | 0.27008 | 0.096131 | 0.25177 | 0.13733 | 0.16937 | 0.13733 | 122.1634 | 122.1817 | -0.18311 | -0.13275 | 122.0901 | 122.1817 | 122.049 | 122.1817
2098.5938 | 122.2366 | -122.0535 | 0.13733 | 0.013199 | 0.017131 | 0.011888 | -0.00056607 | 0.021206 | -0.0029438 | -0.00081595 | 0.0048523 | 0.052438 | 0.006964 | -0.0059772 | 0.0054646 | 0.014582 | 0.000203 | -0.032043 | 0.1236 | -0.09613 | -0.068665 | 0.068665 | -0.054932 | -0.013733 | -0.009155 | 0.1236 | -0.059509 | -0.009155 | 0.045776 | -0.050354 | 0.11444 | 121.9574 | -0.013733 | -0.20599 | 122.1222 | 122.0398 | 121.9986 | 0.082397 | 0.041198 | 121.994 | -0.013733 | -0.14648 | 122.0993 | 122.168 | 122.0032 | 0.17395 | 0.009155 | 0.16479 | 0.027465 | 0.10528 | 0.050354 | 0.21973 | 0.1831 | 122.1771 | 122.1771 | -0.23346 | -0.19684 | 121.9849 | 122.0444 | 122.0215 | 122.0444
2100.3438 | 122.3694 | -122.0444 | 0.10071 | -0.0020601 | 0.016062 | 0.011888 | -0.0044113 | 0.022061 | -0.0025166 | 0.0023882 | 0.0018005 | 0.050943 | 0.0039734 | 0.001286 | 0.0014056 | 0.013941 | 0.0027664 | -0.009155 | 0.07782 | -0.091553 | 0.032043 | 0.21515 | 0.09613 | 0.10529 | 0.13275 | 0.10986 | -0.027466 | 0.091553 | 0.21515 | 0.14648 | 0.23346 | 121.9528 | -0.022888 | -0.068665 | 122.2595 | 122.1497 | 122.1405 | 0.19684 | 0.18768 | 122.0169 | 0.009155 | -0.009155 | 122.2595 | 122.2778 | 122.1909 | 0.26093 | 0.17395 | 0.3067 | 0.1236 | 0.24261 | 0.11902 | 0.16937 | 0.13733 | 122.1222 | 122.1542 | -0.19226 | -0.12817 | 122.0764 | 122.1359 | 122.0352 | 122.1771
2102.1094 | 122.2412 | -122.0993 | 0.13275 | 0.0055694 | 0.017344 | 0.01317 | 0.0013565 | 0.021634 | -0.00038018 | 0.00025205 | 0.0048523 | 0.052865 | 0.0071776 | -0.0046954 | 0.0033282 | 0.01565 | -0.0036422 | -0.050354 | 0.1236 | -0.10529 | -0.086975 | 0.041199 | -0.068665 | -0.068665 | -0.068665 | 0.14191 | -0.068665 | -0.036621 | 0.032043 | -0.073242 | 0.086975 | 121.994 | -0.009155 | -0.21973 | 122.1405 | 122.0306 | 122.0306 | 0.036621 | 0.036621 | 122.0306 | 0.009156 | -0.16937 | 122.1313 | 122.1863 | 122.0261 | 0.15564 | -0.004577 | 0.14649 | 0.018311 | 0.10071 | 0.032044 | 0.22888 | 0.21057 | 122.2229 | 122.2412 | -0.23804 | -0.20142 | 122.0123 | 122.0627 | 122.049 | 122.0306
2103.8594 | 122.2961 | -122.0901 | 0.1236 | -0.0020601 | 0.017771 | 0.0084702 | -0.00013887 | 0.023129 | -0.0040118 | -0.0029524 | -0.0043029 | 0.051156 | 0.0080322 | -0.010036 | 0.001833 | 0.014795 | -0.0019332 | -0.027466 | 0.10986 | -0.10071 | -0.068665 | 0.07782 | -0.022888 | 0.009155 | 0.009155 | 0.14191 | -0.050354 | 0.036621 | 0.11902 | 0.022888 | 0.17395 | 121.9894 | -0.013733 | -0.19226 | 122.168 | 122.0993 | 122.0673 | 0.10986 | 0.07782 | 122.0398 | 0.018311 | -0.086975 | 122.2092 | 122.2641 | 122.113 | 0.2243 | 0.073242 | 0.17853 | 0.032043 | 0.16937 | 0.086975 | 0.21057 | 0.19226 | 122.2 | 122.2321 | -0.2243 | -0.17395 | 122.0215 | 122.1268 | 122.0627 | 122.0993
2105.625 | 122.3419 | -122.081 | 0.11902 | -0.0020601 | 0.018412 | 0.013597 | 0.0019973 | 0.019711 | -0.0025166 | 0.00025205 | -0.0012513 | 0.050943 | 0.0082458 | -0.004909 | 0.0052508 | 0.019282 | -0.000438 | -0.068665 | 0.1236 | -0.10071 | -0.073242 | 0.082397 | -0.054932 | -0.022888 | -0.027466 | 0.10071 | -0.07782 | 0.032043 | 0.10529 | 0.013733 | 0.16479 | 121.9803 | 0.004577 | -0.19226 | 122.1634 | 122.0581 | 122.0261 | 0.07782 | 0.045776 | 122.0032 | -0.018311 | -0.086976 | 122.1863 | 122.2458 | 122.0947 | 0.24261 | 0.091553 | 0.18311 | 0.027466 | 0.18311 | 0.10986 | 0.2243 | 0.17853 | 122.2046 | 122.1817 | -0.21973 | -0.19684 | 122.0078 | 122.113 | 122.0123 | 122.0535
2107.3281 | 122.3145 | -122.1085 | 0.1236 | 0.0055694 | 0.017985 | 0.011247 | -0.0012069 | 0.01907 | -0.0014484 | 0.0032428 | 0.0048523 | 0.054147 | 0.007605 | -0.00555 | 0.0052508 | 0.016504 | 0.0034072 | -0.082397 | 0.1236 | -0.09613 | -0.10529 | 0.050354 | -0.064087 | -0.032043 | -0.054932 | 0.10071 | -0.082397 | 0.009155 | 0.064087 | -0.027466 | 0.11444 | 122.0123 | 0 | -0.22888 | 122.1588 | 122.0764 | 122.0444 | 0.064087 | 0.032043 | 122.0261 | -0.022888 | -0.11444 | 122.1725 | 122.2229 | 122.081 | 0.19684 | 0.054931 | 0.14648 | -0.009156 | 0.14648 | 0.091552 | 0.21973 | 0.18311 | 122.2321 | 122.2092 | -0.21973 | -0.20599 | 122.0032 | 122.1176 | 122.0261 | 122.0535
2109.0156 | 122.3282 | -122.1222 | 0.12817 | -0.0020601 | 0.015849 | 0.011675 | -0.0020615 | 0.019497 | -0.0035846 | -0.00081595 | -0.0012513 | 0.049447 | 0.0071776 | -0.00020939 | 0.001833 | 0.016077 | 0.0004166 | -0.050354 | 0.10071 | -0.07782 | -0.064087 | 0.10986 | -0.004578 | 0.018311 | -0.004578 | 0.09613 | -0.054932 | 0.009155 | 0.11444 | 0.032043 | 0.13733 | 122.0444 | -0.027466 | -0.19226 | 122.2321 | 122.1405 | 122.1176 | 0.096131 | 0.073242 | 122.0673 | -0.032044 | -0.11902 | 122.2366 | 122.2595 | 122.1542 | 0.19226 | 0.086975 | 0.18768 | 0.013733 | 0.16937 | 0.064087 | 0.17853 | 0.15106 | 122.2229 | 122.2183 | -0.20599 | -0.18311 | 122.0581 | 122.1313 | 122.0718 | 122.1176
2110.7656 | 122.319 | -122.1176 | 0.1236 | -0.0096891 | 0.017771 | 0.011247 | -0.00077967 | 0.024197 | -0.001662 | 3.8448e-05 | -0.0012513 | 0.052865 | 0.0084594 | -0.0036274 | 0.00012397 | 0.012659 | -0.0017196 | -0.027466 | 0.11902 | -0.09613 | -0.036621 | 0.10986 | -0.009155 | 0 | 0.018311 | 0.14191 | -0.054932 | 0.022888 | 0.11444 | 0.004578 | 0.14648 | 122.0215 | -0.004577 | -0.16022 | 122.2275 | 122.1176 | 122.1085 | 0.09613 | 0.086975 | 122.0627 | 0.018311 | -0.10071 | 122.2321 | 122.2641 | 122.1222 | 0.20142 | 0.05951 | 0.20599 | 0.059509 | 0.16937 | 0.07782 | 0.21515 | 0.19684 | 122.2366 | 122.2595 | -0.21973 | -0.17853 | 122.081 | 122.1405 | 122.0901 | 122.1359
2112.4844 | 122.3282 | -122.1451 | 0.14191 | -0.0096891 | 0.016703 | 0.01082 | -0.0014207 | 0.023129 | -0.0025166 | 3.8448e-05 | -0.0073547 | 0.050516 | 0.006964 | -0.007259 | -8.9634e-05 | 0.014368 | 0.0006302 | -0.059509 | 0.11444 | -0.10529 | -0.10529 | 0.041199 | -0.036621 | -0.022888 | -0.041199 | 0.15564 | -0.050354 | 0.009155 | 0.10986 | 0.013733 | 0.15564 | 122.0398 | -0.027466 | -0.24719 | 122.1863 | 122.1222 | 122.1085 | 0.082398 | 0.068665 | 122.0947 | 0.013733 | -0.13275 | 122.2549 | 122.3007 | 122.1588 | 0.20599 | 0.064087 | 0.14649 | 0 | 0.16022 | 0.059509 | 0.21973 | 0.20599 | 122.2595 | 122.3007 | -0.24719 | -0.19226 | 122.0398 | 122.1542 | 122.0856 | 122.1039
2114.25 | 122.2916 | -122.1588 | 0.12817 | -0.0020601 | 0.01649 | 0.010179 | -0.0022751 | 0.020566 | -0.0035846 | 0.0021746 | 0.0048523 | 0.050943 | 0.0061096 | -0.0023456 | -0.0011578 | 0.011164 | -1.0598e-05 | -0.050354 | 0.12817 | -0.10529 | -0.07782 | 0.068665 | -0.036621 | -0.022888 | -0.027466 | 0.16022 | -0.059509 | -0.018311 | 0.10071 | 0.009155 | 0.1236 | 122.0535 | 0 | -0.20599 | 122.2275 | 122.1359 | 122.1222 | 0.082398 | 0.068665 | 122.0993 | 0.032043 | -0.14649 | 122.2595 | 122.2824 | 122.168 | 0.1831 | 0.068664 | 0.17395 | 0.027466 | 0.16022 | 0.041198 | 0.23346 | 0.21973 | 122.287 | 122.319 | -0.23346 | -0.18768 | 122.081 | 122.1405 | 122.1085 | 122.1313
2116.0156 | 122.4014 | -122.1039 | 0.10071 | -0.0020601 | 0.016917 | 0.012743 | -0.00077967 | 0.024411 | -0.0040118 | -0.00017515 | -0.0043029 | 0.04902 | 0.009314 | 0.0042768 | 0.003542 | 0.01565 | -0.0010788 | -0.009155 | 0.091553 | -0.050354 | 0.004578 | 0.17395 | 0.032043 | 0.054932 | 0.064087 | 0.068665 | -0.041199 | 0.064087 | 0.15106 | 0.045776 | 0.1831 | 122.0535 | -0.009155 | -0.09613 | 122.2778 | 122.1588 | 122.1359 | 0.10529 | 0.082397 | 122.0627 | -0.032043 | -0.036621 | 122.2549 | 122.287 | 122.1497 | 0.2243 | 0.086975 | 0.2243 | 0.054932 | 0.19226 | 0.10529 | 0.14191 | 0.10986 | 122.1954 | 122.1725 | -0.15106 | -0.14191 | 122.1085 | 122.168 | 122.0947 | 122.168
2117.7188 | 122.2916 | -122.1497 | 0.13733 | 0.0055694 | 0.017131 | 0.011888 | 0.00050193 | 0.017788 | -0.0046528 | -0.00060235 | -0.0012513 | 0.050516 | 0.005255 | -0.0053364 | 0.00033757 | 0.011591 | -0.0023606 | -0.082397 | 0.14191 | -0.11902 | -0.12817 | 0.036621 | -0.050354 | -0.059509 | -0.036621 | 0.16479 | -0.013733 | -0.013733 | 0.086975 | 0.013733 | 0.12817 | 122.0306 | 0.004578 | -0.2655 | 122.1863 | 122.0901 | 122.0993 | 0.05951 | 0.068665 | 122.1359 | 0.027466 | -0.15106 | 122.2366 | 122.2778 | 122.1634 | 0.14191 | 0.027466 | 0.15564 | -0.009155 | 0.10071 | 0 | 0.26093 | 0.17853 | 122.2916 | 122.3145 | -0.25635 | -0.15106 | 122.0215 | 122.1359 | 122.0673 | 122.113
2119.4688 | 122.3373 | -122.168 | 0.11902 | 0.0055694 | 0.015849 | 0.011675 | -0.0016343 | 0.02377 | -0.0042254 | -0.0033796 | -0.0012513 | 0.050302 | 0.0073914 | -0.00063659 | -0.00051703 | 0.013514 | -0.0010788 | -0.027466 | 0.086975 | -0.091553 | -0.027466 | 0.13733 | 0.041199 | 0.050354 | 0.018311 | 0.15106 | -0.036621 | 0.018311 | 0.10529 | 0.036621 | 0.16479 | 122.0764 | -0.032044 | -0.14649 | 122.3053 | 122.2183 | 122.2092 | 0.14191 | 0.13275 | 122.1313 | 0.032043 | -0.10071 | 122.2733 | 122.3328 | 122.2046 | 0.20142 | 0.073242 | 0.22888 | 0.064087 | 0.14191 | 0.054932 | 0.17853 | 0.18768 | 122.2549 | 122.319 | -0.21057 | -0.15564 | 122.1405 | 122.1863 | 122.1405 | 122.1863
2121.2188 | 122.4289 | -122.1268 | 0.1236 | 0.013199 | 0.016276 | 0.011888 | -0.0031297 | 0.020352 | -0.0014484 | 0.00067925 | 0.0018005 | 0.050302 | 0.007605 | -0.00042299 | -0.00094423 | 0.013941 | 0.0004166 | 0.009155 | 0.10529 | -0.07782 | 0.045776 | 0.21057 | 0.07782 | 0.10529 | 0.11902 | 0.1236 | -0.036621 | 0.10986 | 0.21973 | 0.1236 | 0.23346 | 122.0489 | -0.01831 | -0.07782 | 122.3373 | 122.2321 | 122.2046 | 0.18311 | 0.15564 | 122.0901 | 0 | -0.013733 | 122.3465 | 122.3602 | 122.2504 | 0.27008 | 0.16022 | 0.28839 | 0.1236 | 0.25635 | 0.14648 | 0.18311 | 0.16022 | 122.2321 | 122.2504 | -0.20142 | -0.16022 | 122.1725 | 122.2366 | 122.1359 | 122.2458
2122.9219 | 122.4335 | -122.1405 | 0.09613 | -0.0096891 | 0.017771 | 0.012315 | -0.0016343 | 0.022275 | -0.0018756 | -0.00017515 | -0.0012513 | 0.050088 | 0.0088866 | -0.0014912 | 0.0026874 | 0.015864 | -0.0002244 | -0.013733 | 0.082397 | -0.059509 | 0.022888 | 0.1831 | 0.022888 | 0.059509 | 0.054932 | 0.068665 | -0.041199 | 0.059509 | 0.16022 | 0.059509 | 0.17395 | 122.081 | -0.013733 | -0.073242 | 122.3236 | 122.2 | 122.1634 | 0.11902 | 0.082397 | 122.0993 | -0.027465 | -0.036621 | 122.3007 | 122.3145 | 122.2 | 0.21515 | 0.10071 | 0.24261 | 0.082397 | 0.20142 | 0.10071 | 0.14191 | 0.10986 | 122.2229 | 122.2092 | -0.15564 | -0.13733 | 122.1634 | 122.2 | 122.1268 | 122.1954
2124.6875 | 122.4014 | -122.1634 | 0.1236 | -0.0096891 | 0.017131 | 0.011247 | -0.0027023 | 0.021847 | -0.003371 | 0.0011066 | -0.0043029 | 0.050302 | 0.0061096 | -0.0036274 | 0.003542 | 0.016504 | -0.0008652 | -0.059509 | 0.10529 | -0.068665 | -0.036621 | 0.11444 | -0.022888 | 0.022888 | -0.022888 | 0.10071 | -0.054932 | 0.022888 | 0.10529 | 0.027466 | 0.14648 | 122.0947 | -0.01831 | -0.16022 | 122.2778 | 122.1863 | 122.1405 | 0.091553 | 0.045777 | 122.1085 | -0.022888 | -0.10071 | 122.2687 | 122.3099 | 122.1909 | 0.20142 | 0.082398 | 0.18311 | 0.032044 | 0.16022 | 0.07782 | 0.17395 | 0.15564 | 122.2687 | 122.2641 | -0.19226 | -0.17853 | 122.1268 | 122.1863 | 122.1039 | 122.1405
2126.4375 | 122.4564 | -122.113 | 0.082397 | -0.0020601 | 0.017771 | 0.011888 | -0.0037705 | 0.027615 | -0.0014484 | -0.0010298 | 0.0018005 | 0.050516 | 0.0063232 | -0.0017048 | 0.002901 | 0.015223 | 0.000203 | -0.041199 | 0.1236 | -0.073242 | 0.013733 | 0.14648 | 0.013733 | 0.059509 | 0.041199 | 0.068665 | -0.068665 | 0.064087 | 0.14648 | 0.050354 | 0.19226 | 122.0398 | 0.041199 | -0.068664 | 122.2595 | 122.1725 | 122.1268 | 0.13275 | 0.086975 | 122.0444 | -0.013732 | -0.01831 | 122.2595 | 122.3053 | 122.1634 | 0.26093 | 0.11902 | 0.21973 | 0.086975 | 0.21515 | 0.13275 | 0.19684 | 0.13733 | 122.2366 | 122.1817 | -0.15564 | -0.15106 | 122.1268 | 122.1771 | 122.0718 | 122.1542
2128.1406 | 122.319 | -122.1909 | 0.13275 | -0.0020601 | 0.018199 | 0.011247 | -0.00099327 | 0.022702 | -0.0023028 | 0.00067925 | 0.0018005 | 0.050516 | 0.0063232 | -0.00063659 | -0.0037212 | 0.014368 | 0.0021256 | -0.064087 | 0.11444 | -0.10529 | -0.086975 | 0.07782 | -0.045776 | -0.009155 | -0.041199 | 0.15564 | -0.050354 | -0.013733 | 0.082397 | -0.004578 | 0.10529 | 122.0856 | -0.01831 | -0.21973 | 122.2687 | 122.1817 | 122.1451 | 0.096131 | 0.05951 | 122.1405 | 0.022889 | -0.14648 | 122.2733 | 122.2961 | 122.1863 | 0.15564 | 0.045776 | 0.18311 | 0.018311 | 0.13275 | 0.036621 | 0.21973 | 0.20599 | 122.3053 | 122.3465 | -0.23804 | -0.18311 | 122.1039 | 122.1771 | 122.1268 | 122.1497
2129.8906 | 122.4106 | -122.1588 | 0.11444 | 0.0055694 | 0.018412 | 0.011247 | 0.00092933 | 0.022488 | -0.0010212 | 0.00025205 | 0.0018005 | 0.050943 | 0.0080322 | 0.00085881 | 0.0048236 | 0.014795 | -0.002147 | -0.068665 | 0.1236 | -0.10529 | -0.073242 | 0.059509 | -0.050354 | -0.018311 | -0.027466 | 0.086975 | -0.07782 | 0.041199 | 0.11444 | 0.013733 | 0.15106 | 122.0535 | 0.009155 | -0.18768 | 122.2183 | 122.1405 | 122.1085 | 0.086975 | 0.054932 | 122.081 | -0.027466 | -0.073242 | 122.2733 | 122.3099 | 122.1725 | 0.22888 | 0.091553 | 0.16479 | 0.032044 | 0.19226 | 0.11902 | 0.22888 | 0.16479 | 122.2824 | 122.2458 | -0.21973 | -0.19226 | 122.0856 | 122.2 | 122.0901 | 122.1313
2131.5938 | 122.4106 | -122.168 | 0.086975 | 0.0055694 | 0.014353 | 0.011034 | -0.0018479 | 0.020352 | -0.0020892 | 0.0013202 | 0.0079041 | 0.049234 | 0.006964 | -0.0012774 | 0.0031146 | 0.014795 | 0.0016982 | -0.022888 | 0.07782 | -0.073242 | -0.009155 | 0.17395 | 0.013733 | 0.050354 | 0.036621 | 0.064087 | -0.064087 | 0.041199 | 0.12817 | 0.045776 | 0.16479 | 122.0947 | -0.009155 | -0.09613 | 122.3419 | 122.2183 | 122.1817 | 0.1236 | 0.086975 | 122.1039 | -0.022888 | -0.045776 | 122.2961 | 122.3328 | 122.2137 | 0.22888 | 0.10986 | 0.24719 | 0.064087 | 0.19226 | 0.10529 | 0.15106 | 0.12817 | 122.2458 | 122.2321 | -0.16022 | -0.15106 | 122.1588 | 122.2092 | 122.1451 | 122.2046
2133.3594 | 122.3831 | -122.1863 | 0.11902 | -0.0096891 | 0.01649 | 0.01082 | -0.0018479 | 0.023129 | -0.0046528 | -0.0018842 | 0.0018005 | 0.050302 | 0.0095276 | -0.010891 | 0.00033757 | 0.015436 | -1.0598e-05 | -0.059509 | 0.1236 | -0.10529 | -0.068665 | 0.064087 | -0.032043 | 0 | -0.009155 | 0.12817 | -0.013733 | 0.022888 | 0.11444 | 0.018311 | 0.16479 | 122.081 | 0.004577 | -0.18768 | 122.2504 | 122.1863 | 122.1542 | 0.10529 | 0.073243 | 122.1725 | 0.009155 | -0.096131 | 122.3007 | 122.3511 | 122.2046 | 0.17853 | 0.032044 | 0.16937 | 0.036621 | 0.12817 | 0.036621 | 0.22888 | 0.14191 | 122.3099 | 122.3145 | -0.22431 | -0.13275 | 122.1176 | 122.2092 | 122.1268 | 122.1771
2135.0625 | 122.4884 | -122.1634 | 0.10071 | -0.0020601 | 0.015422 | 0.011675 | -0.0035569 | 0.023984 | -0.0040118 | -0.0012434 | 0.0018005 | 0.048807 | 0.0065368 | -0.0017048 | 0.0014056 | 0.014795 | 0.001271 | 0 | 0.09613 | -0.059509 | 0.027466 | 0.2243 | 0.10071 | 0.09613 | 0.14191 | 0.11444 | -0.032043 | 0.09613 | 0.20599 | 0.12817 | 0.21973 | 122.1039 | -0.004578 | -0.073242 | 122.3877 | 122.2595 | 122.2641 | 0.15564 | 0.16022 | 122.1313 | 0.013733 | -0.004578 | 122.3694 | 122.3831 | 122.2916 | 0.25177 | 0.16022 | 0.28381 | 0.086975 | 0.23804 | 0.12817 | 0.15564 | 0.14648 | 122.2595 | 122.2778 | -0.16022 | -0.13275 | 122.1909 | 122.2595 | 122.1634 | 122.3053
2136.8281 | 122.374 | -122.1817 | 0.13733 | -0.0020601 | 0.019908 | 0.010606 | -0.00077967 | 0.019711 | -0.0027302 | 0.00089285 | -0.0012513 | 0.052011 | 0.007605 | 0.0017132 | 0.0020466 | 0.013727 | -0.0044968 | -0.032043 | 0.11902 | -0.091553 | -0.050354 | 0.09613 | -0.022888 | -0.004578 | -0.009155 | 0.13275 | -0.045776 | 0.004578 | 0.10071 | -0.027466 | 0.13275 | 122.0901 | -0.01831 | -0.18768 | 122.2778 | 122.1771 | 122.1588 | 0.086975 | 0.068665 | 122.1359 | -0.004578 | -0.13275 | 122.2824 | 122.3145 | 122.1542 | 0.17853 | 0.01831 | 0.18768 | 0.041199 | 0.14648 | 0.050354 | 0.21057 | 0.17853 | 122.3007 | 122.3145 | -0.22888 | -0.18311 | 122.1313 | 122.1863 | 122.1497 | 122.1725
2138.5938 | 122.4747 | -122.1863 | 0.10529 | -0.0020601 | 0.016703 | 0.011888 | -0.00099327 | 0.023129 | -0.00016658 | 0.0015338 | -0.0012513 | 0.051797 | 0.006964 | -0.0023456 | 0.0037556 | 0.015223 | 0.0025528 | 0.009155 | 0.091553 | -0.050354 | 0.013733 | 0.16937 | 0.018311 | 0.045776 | 0.054932 | 0.054932 | -0.050354 | 0.07782 | 0.17853 | 0.064087 | 0.1831 | 122.1359 | -0.013733 | -0.091553 | 122.3557 | 122.2321 | 122.2046 | 0.09613 | 0.068665 | 122.1359 | -0.050354 | -0.027466 | 122.3648 | 122.3694 | 122.2504 | 0.23346 | 0.11444 | 0.21973 | 0.064087 | 0.22888 | 0.12817 | 0.14191 | 0.10529 | 122.2778 | 122.2412 | -0.15564 | -0.15564 | 122.2 | 122.2641 | 122.1954 | 122.2412
2140.3594 | 122.3831 | -122.2046 | 0.13275 | -0.0096891 | 0.015849 | 0.010606 | -0.0029159 | 0.019925 | -0.0037982 | -0.0010298 | -0.0043029 | 0.052652 | 0.007605 | -0.0014912 | -0.0013714 | 0.013086 | 0.001271 | -0.10529 | 0.11902 | -0.11444 | -0.11444 | 0.013733 | -0.045776 | -0.036621 | -0.059509 | 0.14191 | -0.041199 | -0.004578 | 0.086975 | 0.004578 | 0.14648 | 122.0901 | -0.013732 | -0.24719 | 122.2183 | 122.168 | 122.1588 | 0.07782 | 0.068665 | 122.1634 | 0.009156 | -0.13733 | 122.2916 | 122.3511 | 122.2092 | 0.18768 | 0.045777 | 0.12817 | 0 | 0.12817 | 0.036621 | 0.23346 | 0.18311 | 122.3236 | 122.3465 | -0.24719 | -0.17395 | 122.0901 | 122.2 | 122.0993 | 122.1451
2142.0625 | 122.4106 | -122.2183 | 0.14648 | -0.017319 | 0.01884 | 0.011247 | -0.0024887 | 0.019497 | -0.0012348 | -0.00017515 | -0.0012513 | 0.05137 | 0.0082458 | -0.006618 | 0.00097837 | 0.013941 | 0.0025528 | -0.068665 | 0.10071 | -0.082397 | -0.091553 | 0.059509 | -0.013733 | -0.018311 | -0.045776 | 0.15106 | -0.054932 | 0.022888 | 0.11444 | 0.022888 | 0.15564 | 122.1359 | -0.045776 | -0.23804 | 122.2778 | 122.2 | 122.2046 | 0.064086 | 0.068664 | 122.1634 | 0.004578 | -0.1236 | 122.3328 | 122.374 | 122.2412 | 0.21057 | 0.07782 | 0.14191 | -0.009156 | 0.16937 | 0.07782 | 0.18311 | 0.20599 | 122.319 | 122.3694 | -0.22888 | -0.20142 | 122.1268 | 122.2412 | 122.1497 | 122.1725
2143.8125 | 122.4564 | -122.2046 | 0.11902 | -0.017319 | 0.014781 | 0.011675 | -0.0041977 | 0.022061 | -0.0014484 | 0.0015338 | 0.0018005 | 0.049447 | 0.0084594 | -0.0017048 | 0.0022602 | 0.016077 | -0.000438 | -0.073242 | 0.10071 | -0.07782 | -0.045776 | 0.14191 | 0 | 0.027466 | -0.013733 | 0.10986 | -0.050354 | 0.032043 | 0.11444 | 0.032043 | 0.16022 | 122.1268 | -0.018311 | -0.16479 | 122.3465 | 122.2321 | 122.2046 | 0.10529 | 0.07782 | 122.1542 | -0.009156 | -0.086976 | 122.319 | 122.3648 | 122.2366 | 0.21057 | 0.082397 | 0.21973 | 0.032044 | 0.16479 | 0.082397 | 0.17853 | 0.16022 | 122.3053 | 122.3145 | -0.19684 | -0.16937 | 122.1588 | 122.2366 | 122.1313 | 122.1909
2145.5 | 122.5067 | -122.1863 | 0.082397 | 0.0055694 | 0.015208 | 0.0099656 | -0.0020615 | 0.020138 | -0.0025166 | -0.00017515 | 0.0018005 | 0.05137 | 0.0046142 | 0.0023542 | 0.00012397 | 0.014155 | -0.0008652 | -0.022888 | 0.09613 | -0.082397 | 0.022888 | 0.20142 | 0.07782 | 0.09613 | 0.10529 | 0.10529 | -0.027466 | 0.10529 | 0.2243 | 0.12817 | 0.23346 | 122.1039 | 0.013733 | -0.059509 | 122.3877 | 122.2824 | 122.2641 | 0.17853 | 0.16022 | 122.1588 | 0.022889 | 0.022889 | 122.4106 | 122.4197 | 122.3145 | 0.26093 | 0.15564 | 0.28381 | 0.10528 | 0.25177 | 0.13275 | 0.17853 | 0.13275 | 122.2824 | 122.2916 | -0.16479 | -0.10986 | 122.2092 | 122.2916 | 122.1634 | 122.2916
2147.2031 | 122.3694 | -122.2549 | 0.13275 | -0.0020601 | 0.019267 | 0.010393 | -0.0029159 | 0.020566 | -0.0044392 | -0.0012434 | -0.0073547 | 0.051584 | 0.0050414 | -0.01025 | -0.0011578 | 0.0133 | 0.000203 | -0.10986 | 0.1236 | -0.11444 | -0.1236 | 0.013733 | -0.050354 | -0.045776 | -0.064087 | 0.15564 | -0.041199 | -0.022888 | 0.07782 | -0.013733 | 0.13733 | 122.1405 | -0.009155 | -0.25635 | 122.2687 | 122.2092 | 122.2046 | 0.068665 | 0.064087 | 122.2137 | 0.022889 | -0.15564 | 122.3328 | 122.3923 | 122.2412 | 0.17853 | 0.027466 | 0.12817 | -0.009155 | 0.11902 | 0.018311 | 0.23804 | 0.19684 | 122.3785 | 122.4106 | -0.24719 | -0.17395 | 122.1313 | 122.2321 | 122.1451 | 122.1909
2148.9688 | 122.4564 | -122.1954 | 0.10071 | -0.0096891 | 0.01649 | 0.011247 | -0.0027023 | 0.017788 | -0.00080758 | 0.0017474 | -0.0043029 | 0.050302 | 0.0071776 | -0.0068316 | 0.0014056 | 0.01565 | -0.0023606 | -0.050354 | 0.086975 | -0.054932 | -0.032043 | 0.14648 | -0.004578 | 0.036621 | 0.013733 | 0.082397 | -0.036621 | 0.032043 | 0.10986 | 0.041199 | 0.15106 | 122.1405 | -0.013733 | -0.13275 | 122.3419 | 122.2321 | 122.1909 | 0.091553 | 0.050354 | 122.1588 | -0.018311 | -0.068665 | 122.3053 | 122.3465 | 122.2366 | 0.18768 | 0.07782 | 0.20142 | 0.022889 | 0.14648 | 0.068664 | 0.14191 | 0.11902 | 122.2824 | 122.2778 | -0.15564 | -0.13733 | 122.1634 | 122.2275 | 122.1451 | 122.2092
2150.7188 | 122.4609 | -122.2366 | 0.10529 | 0.0055694 | 0.015208 | 0.0095382 | -0.0014207 | 0.018857 | -0.0018756 | 0.00367 | -0.0043029 | 0.050516 | 0.0048278 | -0.0029864 | 0.001192 | 0.015009 | -0.0010788 | -0.068665 | 0.086975 | -0.068665 | -0.050354 | 0.11444 | -0.022888 | 0.022888 | -0.018311 | 0.10529 | -0.041199 | 0.022888 | 0.10529 | 0.027466 | 0.16022 | 122.168 | -0.018311 | -0.15564 | 122.3511 | 122.2595 | 122.2137 | 0.091553 | 0.045777 | 122.1954 | 0 | -0.082398 | 122.3419 | 122.3969 | 122.2641 | 0.20142 | 0.068665 | 0.18311 | 0.018311 | 0.14649 | 0.064087 | 0.15564 | 0.14649 | 122.3236 | 122.3419 | -0.17395 | -0.14649 | 122.1863 | 122.2595 | 122.168 | 122.2183
2152.4219 | 122.4106 | -122.2504 | 0.11902 | 0.0055694 | 0.015849 | 0.013811 | -0.0018479 | 0.023984 | -0.0012348 | 0.0015338 | 0.0018005 | 0.052652 | 0.0065368 | 0.00085881 | 0.0031146 | 0.014155 | -0.0040696 | -0.073242 | 0.11902 | -0.091553 | -0.1236 | 0.022888 | -0.082397 | -0.045776 | -0.07782 | 0.13275 | -0.07782 | -0.036621 | 0.036621 | -0.073242 | 0.10529 | 122.1588 | 0 | -0.24261 | 122.2733 | 122.2046 | 122.168 | 0.045777 | 0.009156 | 122.1725 | 0.013732 | -0.15564 | 122.287 | 122.3557 | 122.1771 | 0.18311 | 0.004578 | 0.11444 | -0.032043 | 0.11444 | 0.041199 | 0.21057 | 0.21057 | 122.3694 | 122.3831 | -0.21057 | -0.19684 | 122.1268 | 122.2137 | 122.1771 | 122.1725
2154.1719 | 122.4747 | -122.2549 | 0.10986 | -0.0096891 | 0.019694 | 0.011461 | -0.00013887 | 0.020566 | -0.0012348 | 0.00089285 | 0.0018005 | 0.049234 | 0.0080322 | -0.0044818 | 0.001833 | 0.015864 | 0.0031936 | -0.054932 | 0.091553 | -0.082397 | -0.050354 | 0.09613 | -0.004578 | 0.032043 | -0.022888 | 0.091553 | -0.068665 | 0.036621 | 0.12817 | 0.036621 | 0.16022 | 122.1725 | -0.01831 | -0.16022 | 122.3511 | 122.287 | 122.2504 | 0.11444 | 0.077819 | 122.1863 | -0.01831 | -0.073242 | 122.3831 | 122.4152 | 122.2916 | 0.22888 | 0.10529 | 0.17853 | 0.032043 | 0.19684 | 0.10529 | 0.17395 | 0.16022 | 122.3465 | 122.3465 | -0.19226 | -0.17853 | 122.2046 | 122.2916 | 122.2 | 122.2321
2155.875 | 122.5159 | -122.2046 | 0.091553 | -0.0020601 | 0.016917 | 0.012315 | -0.0024887 | 0.024411 | -0.0012348 | -0.00038875 | 0.0079041 | 0.049447 | 0.0065368 | 0.002995 | 0.001833 | 0.013086 | 0.0010574 | 0 | 0.086975 | -0.064087 | 0.045776 | 0.21515 | 0.086975 | 0.091553 | 0.086975 | 0.11902 | -0.027466 | 0.10071 | 0.19684 | 0.1236 | 0.21057 | 122.1405 | -0.004578 | -0.045777 | 122.4197 | 122.2961 | 122.2916 | 0.15564 | 0.15106 | 122.1771 | 0.027466 | 0.009155 | 122.4014 | 122.4152 | 122.3282 | 0.23804 | 0.15106 | 0.27924 | 0.10986 | 0.2243 | 0.12817 | 0.15106 | 0.14649 | 122.2916 | 122.3236 | -0.15564 | -0.11902 | 122.2504 | 122.3053 | 122.2046 | 122.2916
2157.6406 | 122.4609 | -122.2549 | 0.13733 | -0.0020601 | 0.017558 | 0.01082 | 0.0022109 | 0.022488 | -0.001662 | 0.00089285 | 0.0048523 | 0.053934 | 0.009314 | -0.010891 | 0.00097837 | 0.015436 | 0.0040482 | -0.022888 | 0.13275 | -0.091553 | -0.027466 | 0.10071 | -0.009155 | 0.009155 | 0.018311 | 0.11902 | -0.054932 | 0.032043 | 0.10986 | 0.013733 | 0.15564 | 122.1634 | -0.004578 | -0.16479 | 122.3557 | 122.2641 | 122.2458 | 0.10071 | 0.082398 | 122.2 | -0.01831 | -0.10529 | 122.3648 | 122.4106 | 122.2687 | 0.21057 | 0.068665 | 0.19226 | 0.064087 | 0.16479 | 0.086975 | 0.2243 | 0.17395 | 122.3877 | 122.374 | -0.22888 | -0.19226 | 122.2275 | 122.287 | 122.2321 | 122.2733
2159.4062 | 122.525 | -122.2 | 0.10986 | 0.013199 | 0.017985 | 0.011888 | -0.0016343 | 0.019925 | -0.0023028 | -0.002525 | 0.0048523 | 0.048593 | 0.0063232 | -0.0076862 | -8.9634e-05 | 0.014582 | 0.0006302 | -0.004578 | 0.07782 | -0.082397 | 0.022888 | 0.20142 | 0.091553 | 0.086975 | 0.09613 | 0.10071 | -0.018311 | 0.091553 | 0.20599 | 0.11444 | 0.21515 | 122.1176 | -0.032043 | -0.086975 | 122.4014 | 122.287 | 122.2916 | 0.16937 | 0.17395 | 122.1817 | -0.009155 | -0.01831 | 122.406 | 122.4152 | 122.3145 | 0.23346 | 0.13275 | 0.28381 | 0.10528 | 0.22431 | 0.10986 | 0.16022 | 0.11902 | 122.2778 | 122.3007 | -0.19226 | -0.12817 | 122.2229 | 122.2916 | 122.1954 | 122.2961
2161.0938 | 122.4106 | -122.2641 | 0.13275 | -0.017319 | 0.014353 | 0.009111 | -0.0022751 | 0.020993 | -0.0046528 | 0.00046565 | -0.010406 | 0.052011 | 0.0073914 | -0.0078998 | 0.001192 | 0.012232 | -0.0008652 | -0.10986 | 0.11444 | -0.11444 | -0.10986 | 0.032043 | -0.059509 | -0.036621 | -0.073242 | 0.13733 | -0.064087 | -0.027466 | 0.068665 | -0.013733 | 0.1236 | 122.1497 | -0.01831 | -0.24261 | 122.2961 | 122.2275 | 122.2046 | 0.07782 | 0.054932 | 122.2 | 0.004578 | -0.16022 | 122.3328 | 122.3877 | 122.2504 | 0.18768 | 0.050354 | 0.14648 | 0.004578 | 0.13275 | 0.036621 | 0.22888 | 0.20142 | 122.3785 | 122.4014 | -0.24719 | -0.19684 | 122.1542 | 122.2366 | 122.1542 | 122.1909
2162.8438 | 122.5342 | -122.2366 | 0.10529 | 0.0055694 | 0.017131 | 0.012529 | -0.0016343 | 0.022702 | 0.00026062 | 0.0011066 | -0.0043029 | 0.051797 | 0.007605 | -0.0012774 | 0.0014056 | 0.014582 | 0.0040482 | -0.045776 | 0.1236 | -0.082397 | -0.022888 | 0.1236 | 0.022888 | 0.045776 | 0.013733 | 0.091553 | -0.050354 | 0.073242 | 0.17853 | 0.10071 | 0.19684 | 122.1542 | 0.01831 | -0.12817 | 122.3602 | 122.2824 | 122.2595 | 0.12817 | 0.10528 | 122.1863 | -0.013733 | -0.032044 | 122.4152 | 122.4335 | 122.3373 | 0.24719 | 0.15106 | 0.20599 | 0.059509 | 0.22888 | 0.1236 | 0.20599 | 0.14191 | 122.3602 | 122.3282 | -0.18768 | -0.15564 | 122.2137 | 122.3099 | 122.1909 | 122.2504
2164.6094 | 122.3923 | -122.2961 | 0.14191 | 0.0055694 | 0.017771 | 0.011675 | 0.0013565 | 0.023343 | -0.0014484 | 0.0021746 | -0.0012513 | 0.052652 | 0.0078186 | -0.0034138 | 0.0024738 | 0.012018 | -0.0006516 | -0.045776 | 0.11444 | -0.10071 | -0.09613 | 0.022888 | -0.10071 | -0.050354 | -0.091553 | 0.10986 | -0.09613 | -0.054932 | 0.018311 | -0.07782 | 0.082397 | 122.1954 | -0.027466 | -0.23804 | 122.319 | 122.2458 | 122.1954 | 0.050354 | 0 | 122.2 | -0.032044 | -0.19684 | 122.3145 | 122.3785 | 122.2183 | 0.17853 | 0.01831 | 0.1236 | 0.004578 | 0.11444 | 0.041198 | 0.21515 | 0.20599 | 122.4106 | 122.406 | -0.24262 | -0.23804 | 122.2 | 122.2412 | 122.2504 | 122.2046
2166.3594 | 122.5342 | -122.2275 | 0.091553 | -0.017319 | 0.019694 | 0.012102 | -0.0018479 | 0.021206 | -0.0048664 | -0.00081595 | -0.0012513 | 0.049234 | 0.0099548 | -0.0019184 | 0.0037556 | 0.014582 | -0.003856 | -0.018311 | 0.086975 | -0.054932 | 0.009155 | 0.1831 | 0.027466 | 0.050354 | 0.068665 | 0.082397 | -0.045776 | 0.073242 | 0.16937 | 0.054932 | 0.17853 | 122.1725 | -0.004578 | -0.082398 | 122.4106 | 122.2778 | 122.2549 | 0.10529 | 0.082398 | 122.1817 | -0.009156 | -0.018311 | 122.3969 | 122.406 | 122.2824 | 0.2243 | 0.10071 | 0.23804 | 0.064087 | 0.21515 | 0.11902 | 0.14191 | 0.12817 | 122.3145 | 122.3099 | -0.14649 | -0.13733 | 122.2366 | 122.3007 | 122.2092 | 122.2961
2168.125 | 122.5433 | -122.2458 | 0.10071 | -0.0096891 | 0.017985 | 0.012102 | -0.0016343 | 0.022702 | -0.0031574 | -0.001457 | -0.0012513 | 0.050302 | 0.0099548 | -0.010036 | -0.0013714 | 0.015223 | -0.0006516 | -0.013733 | 0.091553 | -0.059509 | 0.032043 | 0.19226 | 0.086975 | 0.091553 | 0.091553 | 0.091553 | -0.027466 | 0.09613 | 0.21057 | 0.11444 | 0.21057 | 122.1863 | -0.009155 | -0.068665 | 122.4381 | 122.3373 | 122.3328 | 0.15106 | 0.14648 | 122.2183 | -0.009155 | -0.004578 | 122.4564 | 122.4564 | 122.3602 | 0.23804 | 0.14191 | 0.25177 | 0.091552 | 0.23804 | 0.1236 | 0.15106 | 0.11902 | 122.3373 | 122.3373 | -0.16022 | -0.12817 | 122.2778 | 122.3419 | 122.2321 | 122.3373
2169.875 | 122.5204 | -122.2549 | 0.10986 | -0.0020601 | 0.017985 | 0.011034 | -0.0018479 | 0.020993 | -0.0010212 | -0.0027386 | 0.0018005 | 0.052865 | 0.0065368 | 0.0017132 | 0.00097837 | 0.011805 | 0.001271 | -0.013733 | 0.082397 | -0.059509 | 0.009155 | 0.1831 | 0.073242 | 0.082397 | 0.086975 | 0.1236 | -0.050354 | 0.086975 | 0.19684 | 0.10986 | 0.21057 | 122.1954 | -0.027466 | -0.10071 | 122.438 | 122.3373 | 122.3282 | 0.14191 | 0.13275 | 122.2046 | 0.013733 | -0.022888 | 122.4518 | 122.4655 | 122.3648 | 0.26093 | 0.16022 | 0.24261 | 0.068664 | 0.24719 | 0.13733 | 0.14191 | 0.17395 | 122.3373 | 122.3785 | -0.16937 | -0.16022 | 122.2641 | 122.3419 | 122.2412 | 122.3419
2171.5625 | 122.4243 | -122.2961 | 0.13275 | 0.013199 | 0.019908 | 0.0095382 | 0.00028833 | 0.028256 | -0.0040118 | 0.00367 | 0.0018005 | 0.050302 | 0.0080322 | -0.00020939 | 0.0031146 | 0.012446 | 0.0010574 | -0.068665 | 0.13275 | -0.10071 | -0.10529 | 0.022888 | -0.09613 | -0.064087 | -0.086975 | 0.091553 | -0.082397 | -0.036621 | 0.013733 | -0.064087 | 0.11444 | 122.1954 | 0 | -0.23804 | 122.319 | 122.2321 | 122.2 | 0.036621 | 0.004578 | 122.2137 | -0.041198 | -0.16937 | 122.3099 | 122.4106 | 122.2321 | 0.19684 | 0.01831 | 0.1236 | -0.004578 | 0.09613 | 0.045776 | 0.23346 | 0.17395 | 122.4289 | 122.3877 | -0.23346 | -0.21515 | 122.1909 | 122.2595 | 122.2275 | 122.2092
2173.3281 | 122.4518 | -122.2824 | 0.12817 | -0.0020601 | 0.018626 | 0.010606 | 0.00028833 | 0.022915 | -0.003371 | 0.0028154 | -0.0043029 | 0.053506 | 0.009314 | -0.0068316 | 0.001833 | 0.011591 | -0.0002244 | -0.036621 | 0.11444 | -0.09613 | -0.050354 | 0.09613 | -0.032043 | -0.018311 | -0.009155 | 0.10529 | -0.050354 | 0.004578 | 0.082397 | -0.027466 | 0.11902 | 122.1863 | -0.013733 | -0.17853 | 122.3785 | 122.2641 | 122.2504 | 0.077819 | 0.064087 | 122.2321 | -0.022888 | -0.1236 | 122.3648 | 122.4014 | 122.2549 | 0.16937 | 0.022888 | 0.19226 | 0.045776 | 0.13275 | 0.054932 | 0.21057 | 0.15564 | 122.3969 | 122.3877 | -0.2243 | -0.17853 | 122.2321 | 122.287 | 122.2458 | 122.2733
2175.0781 | 122.438 | -122.319 | 0.13275 | 0.0055694 | 0.016703 | 0.011247 | -0.0016343 | 0.021206 | -0.0035846 | -0.0012434 | -0.0073547 | 0.05137 | 0.0084594 | -0.0036274 | -0.00094423 | 0.013941 | 0.0008438 | -0.082397 | 0.13733 | -0.10529 | -0.10986 | 0.032043 | -0.041199 | -0.032043 | -0.07782 | 0.14191 | -0.041199 | -0.022888 | 0.082397 | -0.004578 | 0.11444 | 122.2137 | 0.004578 | -0.24261 | 122.3511 | 122.287 | 122.2778 | 0.073243 | 0.064087 | 122.2778 | 0.009156 | -0.15564 | 122.4014 | 122.4335 | 122.3145 | 0.15564 | 0.036621 | 0.13733 | -0.004577 | 0.1236 | 0.018311 | 0.24262 | 0.18311 | 122.4564 | 122.4609 | -0.23804 | -0.17395 | 122.2092 | 122.2961 | 122.2366 | 122.2412
2176.8281 | 122.5708 | -122.2641 | 0.10071 | -0.0020601 | 0.016276 | 0.012315 | -0.0022751 | 0.022061 | -0.0027302 | -0.00017515 | -0.0043029 | 0.050302 | 0.007605 | 0.0017132 | 0.00461 | 0.014155 | -0.0019332 | -0.004578 | 0.07782 | -0.050354 | 0.013733 | 0.1831 | 0.036621 | 0.059509 | 0.064087 | 0.059509 | -0.050354 | 0.068665 | 0.16022 | 0.041199 | 0.18768 | 122.2137 | -0.022888 | -0.086975 | 122.4472 | 122.3236 | 122.3007 | 0.10986 | 0.086975 | 122.2137 | -0.041199 | -0.032043 | 122.4243 | 122.4518 | 122.3053 | 0.23804 | 0.091553 | 0.23346 | 0.064087 | 0.21057 | 0.11902 | 0.12817 | 0.10986 | 122.3419 | 122.3236 | -0.15106 | -0.15106 | 122.2778 | 122.3328 | 122.2595 | 122.3282
2178.5312 | 122.5342 | -122.2366 | 0.10529 | -0.0096891 | 0.01884 | 0.010393 | 7.473e-05 | 0.018643 | -0.00059378 | -0.0010298 | 0.0018005 | 0.053506 | 0.007605 | -0.0059772 | 0.00461 | 0.015864 | 0.0042618 | -0.054932 | 0.11444 | -0.10529 | -0.054932 | 0.09613 | -0.032043 | 0.009155 | 0.009155 | 0.082397 | -0.064087 | 0.059509 | 0.12817 | 0.041199 | 0.17395 | 122.1313 | 0.009155 | -0.16022 | 122.3328 | 122.2458 | 122.2046 | 0.11444 | 0.073243 | 122.1725 | -0.022889 | -0.045777 | 122.3648 | 122.4106 | 122.2778 | 0.23804 | 0.10529 | 0.20142 | 0.050354 | 0.19226 | 0.1236 | 0.21973 | 0.14648 | 122.3511 | 122.319 | -0.21057 | -0.16937 | 122.1817 | 122.2961 | 122.1817 | 122.2458
2180.2969 | 122.5479 | -122.2687 | 0.09613 | 0.0055694 | 0.018626 | 0.014024 | 0.00028833 | 0.026333 | -0.0027302 | 0.0026018 | -0.0012513 | 0.051797 | 0.007605 | 0.002995 | 0.0043964 | 0.015436 | 0.0023392 | -0.064087 | 0.10986 | -0.11444 | -0.073242 | 0.082397 | -0.045776 | -0.018311 | -0.018311 | 0.073242 | -0.07782 | 0.041199 | 0.10986 | 0.027466 | 0.16937 | 122.1542 | 0.013733 | -0.16937 | 122.3511 | 122.2504 | 122.2229 | 0.09613 | 0.068665 | 122.1909 | -0.022888 | -0.054931 | 122.3785 | 122.438 | 122.2961 | 0.24719 | 0.10529 | 0.19684 | 0.041199 | 0.18768 | 0.11902 | 0.2243 | 0.15106 | 122.3785 | 122.3419 | -0.21057 | -0.17395 | 122.1954 | 122.3099 | 122.2046 | 122.2504
2182 | 122.4518 | -122.2961 | 0.11902 | -0.0020601 | 0.019267 | 0.01082 | 0.00028833 | 0.022275 | -0.0012348 | 0.0015338 | -0.0012513 | 0.052438 | 0.0082458 | -0.00063659 | 0.0020466 | 0.013727 | -0.001506 | -0.032043 | 0.10529 | -0.07782 | -0.073242 | 0.10529 | -0.022888 | -0.018311 | 0 | 0.10986 | -0.059509 | 0.004578 | 0.07782 | -0.027466 | 0.1236 | 122.2183 | -0.013733 | -0.19226 | 122.4014 | 122.2778 | 122.2733 | 0.059509 | 0.054932 | 122.2366 | -0.009156 | -0.11444 | 122.374 | 122.4197 | 122.2687 | 0.1831 | 0.032043 | 0.18311 | 0.004578 | 0.13733 | 0.064087 | 0.18311 | 0.16937 | 122.4014 | 122.406 | -0.19684 | -0.17853 | 122.2229 | 122.3007 | 122.2641 | 122.2961
2183.7656 | 122.4792 | -122.2961 | 0.1236 | -0.0020601 | 0.018412 | 0.011888 | 0.00028833 | 0.025906 | 0.0021832 | -0.0012434 | -0.0043029 | 0.049447 | 0.0078186 | -0.0025592 | 0.0024738 | 0.015436 | 0.0053298 | -0.086975 | 0.11444 | -0.1236 | -0.11444 | 0.032043 | -0.073242 | -0.064087 | -0.082397 | 0.10986 | -0.10986 | -0.018311 | 0.032043 | -0.041199 | 0.10071 | 122.1725 | -0.009155 | -0.23804 | 122.3282 | 122.2321 | 122.2229 | 0.059509 | 0.050354 | 122.1863 | -0.013733 | -0.14191 | 122.3282 | 122.3969 | 122.2549 | 0.21057 | 0.068664 | 0.15564 | 0.009155 | 0.14191 | 0.091552 | 0.23804 | 0.21973 | 122.4106 | 122.406 | -0.24719 | -0.23346 | 122.1817 | 122.2778 | 122.2092 | 122.2137
2185.5312 | 122.4472 | -122.3282 | 0.13733 | 0.0055694 | 0.017985 | 0.012102 | -0.00099327 | 0.026333 | -0.0010212 | 0.0011066 | -0.0012513 | 0.052865 | 0.0080322 | -0.0057636 | 0.0020466 | 0.013514 | 0.0016982 | -0.082397 | 0.12817 | -0.091553 | -0.11444 | 0.009155 | -0.10529 | -0.059509 | -0.11902 | 0.11902 | -0.09613 | -0.041199 | 0.022888 | -0.07782 | 0.091553 | 122.2366 | -0.009155 | -0.25177 | 122.3373 | 122.2687 | 122.2229 | 0.032044 | -0.013733 | 122.2321 | -0.01831 | -0.17853 | 122.3511 | 122.4197 | 122.2504 | 0.18768 | 0.01831 | 0.10071 | -0.022888 | 0.11902 | 0.054931 | 0.21973 | 0.21515 | 122.4564 | 122.4472 | -0.22888 | -0.23346 | 122.2137 | 122.287 | 122.2458 | 122.2092
2187.2812 | 122.5159 | -122.3236 | 0.11902 | 0.0055694 | 0.017985 | 0.012315 | -0.00077967 | 0.024197 | -0.003371 | 0.00025205 | 0.0018005 | 0.051156 | 0.0082458 | -0.0014912 | 0.0020466 | 0.014582 | -0.0002244 | -0.036621 | 0.11444 | -0.09613 | -0.059509 | 0.1236 | -0.022888 | 0 | 0.009155 | 0.1236 | -0.054932 | 0.022888 | 0.1236 | 0.036621 | 0.16022 | 122.2275 | -0.004578 | -0.17853 | 122.4472 | 122.3236 | 122.3007 | 0.09613 | 0.073242 | 122.2687 | 0.004577 | -0.096131 | 122.4472 | 122.4838 | 122.3602 | 0.21515 | 0.091553 | 0.21973 | 0.036621 | 0.17853 | 0.07782 | 0.21057 | 0.17853 | 122.438 | 122.4472 | -0.21515 | -0.17395 | 122.2641 | 122.3465 | 122.287 | 122.3328
2189.0469 | 122.5204 | -122.3099 | 0.10986 | 0.013199 | 0.017344 | 0.011675 | -0.0022751 | 0.022702 | -0.0029438 | -0.002525 | -0.0043029 | 0.050516 | 0.006964 | -0.0027728 | 0.001192 | 0.012018 | 0.0008438 | -0.036621 | 0.10986 | -0.10986 | -0.054932 | 0.091553 | -0.009155 | 0.004578 | 0.022888 | 0.11902 | -0.054932 | 0.027466 | 0.11902 | 0.032043 | 0.15564 | 122.2 | 0 | -0.16479 | 122.4014 | 122.3145 | 122.3007 | 0.11444 | 0.10071 | 122.2549 | 0.009156 | -0.082397 | 122.4289 | 122.4655 | 122.3419 | 0.21057 | 0.086975 | 0.20142 | 0.054931 | 0.17395 | 0.082398 | 0.21973 | 0.17395 | 122.4197 | 122.4289 | -0.21973 | -0.16479 | 122.2549 | 122.3373 | 122.2733 | 122.3328
2190.8125 | 122.4564 | -122.3145 | 0.13733 | 0.0055694 | 0.018412 | 0.010179 | -0.00056607 | 0.022061 | -0.0020892 | -0.0020978 | 0.0018005 | 0.050516 | 0.0078186 | -0.0034138 | 0.0016194 | 0.013514 | 0.0031936 | -0.091553 | 0.13275 | -0.10529 | -0.12817 | 0.004578 | -0.09613 | -0.064087 | -0.1236 | 0.10986 | -0.10529 | -0.036621 | 0.009155 | -0.07782 | 0.10529 | 122.2092 | -0.004578 | -0.2655 | 122.319 | 122.2504 | 122.2183 | 0.041199 | 0.009156 | 122.2092 | -0.027466 | -0.17395 | 122.3236 | 122.4197 | 122.2366 | 0.21057 | 0.027466 | 0.10986 | -0.022888 | 0.11444 | 0.068665 | 0.23804 | 0.21515 | 122.4472 | 122.4243 | -0.24262 | -0.24262 | 122.1863 | 122.2778 | 122.2229 | 122.1909
2192.5312 | 122.5433 | -122.3099 | 0.10529 | 0.013199 | 0.015422 | 0.011247 | -0.00099327 | 0.021634 | -0.001662 | -0.0023114 | 0.0048523 | 0.050516 | 0.009314 | -0.0074726 | 0.0024738 | 0.013514 | 0.00298 | -0.07782 | 0.13275 | -0.10071 | -0.09613 | 0.059509 | -0.064087 | -0.022888 | -0.050354 | 0.10071 | -0.068665 | 0.022888 | 0.10071 | -0.013733 | 0.14648 | 122.2092 | 0.027465 | -0.20142 | 122.3694 | 122.287 | 122.2458 | 0.07782 | 0.036621 | 122.2412 | -0.004578 | -0.082398 | 122.4106 | 122.4564 | 122.2961 | 0.21515 | 0.054932 | 0.16022 | 0.004578 | 0.16937 | 0.091553 | 0.23346 | 0.16937 | 122.4426 | 122.4106 | -0.20599 | -0.17395 | 122.2137 | 122.3328 | 122.2321 | 122.2595
2194.2969 | 122.4884 | -122.319 | 0.11444 | -0.0096891 | 0.020335 | 0.012315 | -0.00077967 | 0.022702 | -0.00059378 | -0.00038875 | -0.0012513 | 0.050302 | 0.0063232 | -0.011104 | -0.00094423 | 0.014582 | 0.0044754 | -0.036621 | 0.11444 | -0.10529 | -0.054932 | 0.11444 | -0.027466 | -0.013733 | 0.004578 | 0.11444 | -0.064087 | 0.009155 | 0.091553 | -0.022888 | 0.13275 | 122.2137 | 0 | -0.16937 | 122.4335 | 122.3053 | 122.2916 | 0.091553 | 0.07782 | 122.2549 | 0 | -0.10529 | 122.4106 | 122.4518 | 122.2961 | 0.19684 | 0.041199 | 0.21973 | 0.050354 | 0.15564 | 0.073242 | 0.21973 | 0.17853 | 122.4335 | 122.4335 | -0.21973 | -0.17853 | 122.2641 | 122.3282 | 122.2824 | 122.3236
2196.0625 | 122.5433 | -122.3328 | 0.091553 | -0.0020601 | 0.015849 | 0.011461 | -0.0016343 | 0.020993 | -0.0014484 | 0.00025205 | -0.0012513 | 0.049447 | 0.0099548 | -0.0010638 | 0.001833 | 0.015009 | 0.0021256 | -0.068665 | 0.091553 | -0.086975 | -0.059509 | 0.10071 | 0.004578 | 0.027466 | -0.027466 | 0.09613 | -0.054932 | 0.027466 | 0.11902 | 0.013733 | 0.16479 | 122.2458 | 0 | -0.15106 | 122.4335 | 122.3602 | 122.3373 | 0.11444 | 0.091553 | 122.2778 | 0.004577 | -0.064087 | 122.4518 | 122.4976 | 122.3465 | 0.21973 | 0.068665 | 0.18768 | 0.027466 | 0.17395 | 0.082398 | 0.17853 | 0.15106 | 122.4243 | 122.4289 | -0.17853 | -0.14649 | 122.2733 | 122.3602 | 122.2641 | 122.3053
2197.75 | 122.5571 | -122.3328 | 0.10071 | 0.013199 | 0.016917 | 0.010393 | -0.0027023 | 0.021634 | -0.0029438 | 0.00089285 | 0.0048523 | 0.050516 | 0.0091002 | -0.0046954 | -8.9634e-05 | 0.013727 | -0.0012924 | -0.013733 | 0.10071 | -0.073242 | 0.004578 | 0.17395 | 0.073242 | 0.082397 | 0.064087 | 0.10986 | -0.036621 | 0.07782 | 0.17853 | 0.10986 | 0.17853 | 122.2595 | 0 | -0.09613 | 122.5067 | 122.4152 | 122.406 | 0.15564 | 0.14648 | 122.2961 | 0.009155 | -0.022888 | 122.5113 | 122.5113 | 122.4426 | 0.21515 | 0.14648 | 0.24719 | 0.07782 | 0.21515 | 0.11444 | 0.17395 | 0.14648 | 122.4335 | 122.4426 | -0.17395 | -0.13733 | 122.3373 | 122.4106 | 122.319 | 122.3969
2199.5 | 122.5479 | -122.3465 | 0.1236 | 0.0055694 | 0.01884 | 0.0093246 | -0.0018479 | 0.019925 | -0.0031574 | 0.0023882 | -0.0012513 | 0.050088 | 0.0078186 | -0.0029864 | -0.0011578 | 0.012446 | -0.0017196 | -0.009155 | 0.073242 | -0.07782 | 0 | 0.16937 | 0.054932 | 0.064087 | 0.013733 | 0.13733 | -0.041199 | 0.045776 | 0.15564 | 0.068665 | 0.16937 | 122.2687 | -0.050354 | -0.1236 | 122.5159 | 122.4106 | 122.4014 | 0.14191 | 0.13275 | 122.3053 | 0.013733 | -0.07782 | 122.5021 | 122.5159 | 122.4152 | 0.21057 | 0.10986 | 0.24719 | 0.07782 | 0.19684 | 0.086975 | 0.15106 | 0.17853 | 122.4197 | 122.4838 | -0.20142 | -0.16479 | 122.3465 | 122.3923 | 122.3373 | 122.3602
2201.25 | 122.612 | -122.3053 | 0.09613 | -0.0020601 | 0.015208 | 0.012529 | -0.0020615 | 0.02142 | -0.0014484 | -0.0016706 | -0.0012513 | 0.049875 | 0.0063232 | -0.0046954 | 0.002901 | 0.015223 | 0.004689 | 0.013733 | 0.059509 | -0.027466 | 0 | 0.17853 | 0.041199 | 0.041199 | 0.050354 | 0.045776 | -0.068665 | 0.073242 | 0.16479 | 0.050354 | 0.17395 | 122.2778 | -0.036621 | -0.09613 | 122.4838 | 122.3465 | 122.3465 | 0.068665 | 0.068665 | 122.2366 | -0.050354 | -0.022888 | 122.4701 | 122.4792 | 122.3557 | 0.24261 | 0.11902 | 0.20599 | 0.027466 | 0.23346 | 0.14191 | 0.086975 | 0.11444 | 122.3648 | 122.3511 | -0.1236 | -0.16479 | 122.3053 | 122.3785 | 122.319 | 122.3557
2202.9531 | 122.493 | -122.3465 | 0.1236 | -0.0020601 | 0.018412 | 0.011034 | -0.00013887 | 0.025052 | -0.0023028 | -0.0020978 | 0.0018005 | 0.051156 | 0.0084594 | 0.0019268 | 0.00055117 | 0.016077 | 0.0010574 | -0.07782 | 0.10986 | -0.10071 | -0.1236 | 0 | -0.086975 | -0.064087 | -0.09613 | 0.11444 | -0.09613 | -0.045776 | 0.013733 | -0.07782 | 0.091553 | 122.2458 | -0.013733 | -0.24719 | 122.3465 | 122.2824 | 122.2595 | 0.036621 | 0.013733 | 122.2504 | -0.009155 | -0.16937 | 122.3602 | 122.4381 | 122.2687 | 0.18768 | 0.01831 | 0.10071 | -0.022888 | 0.10986 | 0.050354 | 0.21057 | 0.21057 | 122.4564 | 122.4609 | -0.2243 | -0.21973 | 122.2229 | 122.3007 | 122.2687 | 122.2504
2204.7031 | 122.5021 | -122.3557 | 0.12817 | -0.0020601 | 0.017985 | 0.01082 | -0.0012069 | 0.027615 | -0.001662 | 0.00046565 | -0.0012513 | 0.052438 | 0.0082458 | -0.0096088 | 0.0037556 | 0.016932 | -0.0030014 | -0.036621 | 0.10529 | -0.10071 | -0.073242 | 0.086975 | -0.041199 | -0.027466 | -0.004578 | 0.11444 | -0.07782 | -0.018311 | 0.064087 | -0.045776 | 0.10529 | 122.2549 | -0.022888 | -0.20142 | 122.4426 | 122.3282 | 122.3145 | 0.073242 | 0.059509 | 122.2778 | -0.013733 | -0.14649 | 122.4197 | 122.4609 | 122.3099 | 0.18311 | 0.032044 | 0.18768 | 0.027466 | 0.14191 | 0.059509 | 0.20599 | 0.19226 | 122.4609 | 122.4701 | -0.22888 | -0.20599 | 122.2824 | 122.3373 | 122.319 | 122.3511
2206.4531 | 122.5388 | -122.3419 | 0.10986 | 0.013199 | 0.01884 | 0.011034 | -0.0012069 | 0.02377 | -0.0014484 | -0.001457 | -0.0043029 | 0.05137 | 0.0091002 | -0.011104 | -0.002226 | 0.012873 | -0.000438 | -0.036621 | 0.10986 | -0.09613 | -0.073242 | 0.11444 | -0.013733 | 0.009155 | 0.004578 | 0.10986 | -0.050354 | 0.032043 | 0.1236 | 0.022888 | 0.15106 | 122.2458 | 0 | -0.18311 | 122.4564 | 122.3511 | 122.3282 | 0.10528 | 0.082397 | 122.2916 | 0 | -0.07782 | 122.4655 | 122.493 | 122.3648 | 0.20142 | 0.073242 | 0.21057 | 0.022888 | 0.17395 | 0.082397 | 0.20599 | 0.16022 | 122.4518 | 122.4518 | -0.20599 | -0.16022 | 122.2687 | 122.374 | 122.3053 | 122.3465
2208.2031 | 122.5525 | -122.3602 | 0.10529 | 0.0055694 | 0.017131 | 0.011247 | -0.0016343 | 0.020566 | -0.0010212 | -0.00017515 | 0.0018005 | 0.051797 | 0.008673 | -0.0068316 | 0.0014056 | 0.012446 | 0.0016982 | -0.050354 | 0.10986 | -0.07782 | -0.050354 | 0.10071 | -0.004578 | -0.004578 | -0.009155 | 0.11444 | -0.050354 | 0.036621 | 0.1236 | 0.013733 | 0.15106 | 122.2824 | 0.004577 | -0.15564 | 122.4609 | 122.3557 | 122.3557 | 0.073242 | 0.073242 | 122.3099 | 0.009155 | -0.068665 | 122.4838 | 122.5113 | 122.374 | 0.20142 | 0.064087 | 0.17853 | 0.027466 | 0.17395 | 0.086975 | 0.18768 | 0.16479 | 122.4701 | 122.4747 | -0.18311 | -0.15564 | 122.3099 | 122.3969 | 122.3099 | 122.3511
2209.9531 | 122.5479 | -122.3511 | 0.1236 | -0.0096891 | 0.017985 | 0.01082 | -0.00013887 | 0.02142 | -0.0020892 | 0.0017474 | -0.0012513 | 0.052652 | 0.0082458 | -0.0068316 | -8.9634e-05 | 0.014795 | -0.002147 | -0.041199 | 0.11444 | -0.09613 | -0.068665 | 0.10986 | -0.004578 | 0.009155 | -0.004578 | 0.1236 | -0.068665 | 0.018311 | 0.11444 | 0.018311 | 0.14648 | 122.2549 | -0.009155 | -0.19226 | 122.4609 | 122.3602 | 122.3465 | 0.10528 | 0.091552 | 122.2824 | 0 | -0.10528 | 122.4655 | 122.4976 | 122.3694 | 0.21515 | 0.086976 | 0.20599 | 0.027465 | 0.18311 | 0.086976 | 0.21057 | 0.19226 | 122.4655 | 122.4747 | -0.21973 | -0.19226 | 122.2824 | 122.3694 | 122.3099 | 122.3465
2211.6562 | 122.6257 | -122.3145 | 0.10071 | 0.0055694 | 0.016703 | 0.011247 | 7.473e-05 | 0.023556 | -0.00016658 | 0.00025205 | 0.0018005 | 0.049661 | 0.0088866 | -0.0042682 | 0.0052508 | 0.017145 | 0.0023392 | -0.054932 | 0.10529 | -0.09613 | -0.032043 | 0.13275 | 0 | 0.045776 | 0.022888 | 0.064087 | -0.068665 | 0.073242 | 0.14191 | 0.041199 | 0.18768 | 122.2183 | 0.004578 | -0.13275 | 122.4472 | 122.3602 | 122.3145 | 0.14191 | 0.09613 | 122.2458 | -0.036621 | -0.027466 | 122.4564 | 122.5021 | 122.3557 | 0.25635 | 0.10986 | 0.22888 | 0.064087 | 0.21057 | 0.14191 | 0.20142 | 0.13275 | 122.4197 | 122.3785 | -0.19684 | -0.16937 | 122.2824 | 122.3877 | 122.2595 | 122.3373
2213.4219 | 122.5891 | -122.3511 | 0.10529 | -0.017319 | 0.017131 | 0.013597 | -0.0027023 | 0.023343 | -0.0025166 | -0.0012434 | -0.0043029 | 0.048166 | 0.0071776 | 0.0010724 | 0.00033757 | 0.013941 | -0.003215 | -0.050354 | 0.09613 | -0.07782 | -0.059509 | 0.10986 | -0.004578 | 0.050354 | -0.009155 | 0.073242 | -0.064087 | 0.018311 | 0.10986 | 0.027466 | 0.14191 | 122.2733 | -0.009156 | -0.16479 | 122.4609 | 122.4014 | 122.3465 | 0.12817 | 0.073242 | 122.287 | -0.032044 | -0.086975 | 122.4609 | 122.493 | 122.3785 | 0.20599 | 0.091553 | 0.18768 | 0.018311 | 0.17395 | 0.082398 | 0.17395 | 0.13733 | 122.4472 | 122.4243 | -0.18311 | -0.16937 | 122.2916 | 122.3694 | 122.3007 | 122.3419
2215.1875 | 122.5204 | -122.374 | 0.11902 | 0.013199 | 0.01948 | 0.012743 | 0.00050193 | 0.025479 | -0.00038018 | 3.8448e-05 | -0.0012513 | 0.051156 | 0.0091002 | -0.007259 | 0.00097837 | 0.013514 | 0.0025528 | -0.041199 | 0.1236 | -0.073242 | -0.07782 | 0.09613 | -0.045776 | -0.022888 | -0.027466 | 0.1236 | -0.054932 | -0.018311 | 0.036621 | -0.059509 | 0.086975 | 122.3007 | 0.004577 | -0.19684 | 122.4701 | 122.3511 | 122.3282 | 0.050354 | 0.027466 | 122.319 | 0.004577 | -0.13733 | 122.4106 | 122.4609 | 122.3145 | 0.14191 | -0.004577 | 0.16937 | -0.004578 | 0.091553 | 0.036621 | 0.19684 | 0.17853 | 122.4976 | 122.4976 | -0.19226 | -0.17395 | 122.2961 | 122.3557 | 122.3328 | 122.3465
2216.9531 | 122.58 | -122.374 | 0.1236 | -0.0096891 | 0.017985 | 0.011247 | -0.0024887 | 0.019925 | -0.003371 | 0.0021746 | -0.0043029 | 0.050088 | 0.0073914 | -0.0057636 | -0.00094423 | 0.0133 | -0.0025742 | -0.045776 | 0.10529 | -0.10529 | -0.054932 | 0.086975 | -0.013733 | -0.004578 | -0.004578 | 0.10071 | -0.054932 | 0.022888 | 0.11902 | 0.018311 | 0.15564 | 122.2687 | -0.01831 | -0.17853 | 122.4609 | 122.3694 | 122.3602 | 0.10071 | 0.091553 | 122.319 | -0.022888 | -0.10071 | 122.493 | 122.5296 | 122.3923 | 0.21057 | 0.073243 | 0.19226 | 0.050354 | 0.17395 | 0.07782 | 0.21057 | 0.15564 | 122.4792 | 122.4747 | -0.22888 | -0.17853 | 122.319 | 122.3969 | 122.3282 | 122.3694
2218.6562 | 122.6212 | -122.3465 | 0.10986 | -0.0020601 | 0.017771 | 0.01082 | -0.0020615 | 0.020138 | -0.0023028 | 0.0021746 | -0.01651 | 0.048807 | 0.010168 | 4.214e-06 | 0.00033757 | 0.013941 | 0.001912 | -0.013733 | 0.073242 | -0.059509 | -0.009155 | 0.17853 | 0.027466 | 0.059509 | 0.054932 | 0.064087 | -0.068665 | 0.068665 | 0.16022 | 0.054932 | 0.1831 | 122.287 | -0.036621 | -0.11902 | 122.525 | 122.406 | 122.374 | 0.11902 | 0.086975 | 122.2778 | -0.045776 | -0.041198 | 122.5067 | 122.5296 | 122.4014 | 0.25177 | 0.1236 | 0.23804 | 0.050354 | 0.22888 | 0.13733 | 0.13275 | 0.13275 | 122.4197 | 122.4106 | -0.16937 | -0.17853 | 122.3373 | 122.4152 | 122.3328 | 122.4014
2220.4219 | 122.644 | -122.3831 | 0.09613 | -0.0020601 | 0.017131 | 0.011888 | -0.0033433 | 0.018002 | -0.0025166 | 0.00025205 | -0.0012513 | 0.049447 | 0.010382 | -0.00085019 | -0.00094423 | 0.014155 | 0.0004166 | -0.041199 | 0.086975 | -0.091553 | -0.036621 | 0.13275 | 0.009155 | 0.050354 | 0.013733 | 0.10071 | -0.064087 | 0.054932 | 0.15564 | 0.07782 | 0.18768 | 122.2916 | -0.009155 | -0.13275 | 122.5159 | 122.4335 | 122.3923 | 0.14191 | 0.10071 | 122.319 | 0.004578 | -0.041198 | 122.5388 | 122.5708 | 122.4609 | 0.25177 | 0.14191 | 0.2243 | 0.054932 | 0.21973 | 0.11902 | 0.17853 | 0.1648 | 122.4701 | 122.4838 | -0.18768 | -0.16022 | 122.3465 | 122.438 | 122.3419 | 122.3969
2222.1719 | 122.6761 | -122.3648 | 0.09613 | 0.013199 | 0.014994 | 0.011247 | -0.0029159 | 0.017361 | -0.00059378 | -0.001457 | -0.0043029 | 0.049875 | 0.0061096 | -0.0027728 | 0.0022602 | 0.013514 | -0.0002244 | -0.027466 | 0.082397 | -0.07782 | -0.004578 | 0.17853 | 0.059509 | 0.10071 | 0.086975 | 0.10071 | -0.068665 | 0.09613 | 0.19684 | 0.13275 | 0.22888 | 122.287 | -0.013733 | -0.10071 | 122.5433 | 122.4655 | 122.4243 | 0.17853 | 0.13733 | 122.2961 | 0.004578 | 0 | 122.5616 | 122.5937 | 122.4976 | 0.29755 | 0.20142 | 0.25635 | 0.073242 | 0.2655 | 0.16479 | 0.16022 | 0.16937 | 122.4472 | 122.4655 | -0.17395 | -0.16479 | 122.3602 | 122.4609 | 122.3373 | 122.4518
2223.9219 | 122.5067 | -122.4152 | 0.11902 | 0.0055694 | 0.017344 | 0.011034 | -0.00099327 | 0.023129 | -0.0025166 | -0.00060235 | -0.0043029 | 0.052011 | 0.0071776 | -0.0046954 | -8.9634e-05 | 0.014582 | 0.001912 | -0.073242 | 0.12817 | -0.10986 | -0.1236 | 0.013733 | -0.10071 | -0.068665 | -0.1236 | 0.11444 | -0.086975 | -0.036621 | 0.013733 | -0.073242 | 0.091553 | 122.3053 | 0.009155 | -0.24261 | 122.4289 | 122.3465 | 122.3145 | 0.041198 | 0.009155 | 122.3282 | -0.004578 | -0.15564 | 122.4289 | 122.5067 | 122.3419 | 0.17853 | 0.013733 | 0.1236 | -0.013733 | 0.10071 | 0.050354 | 0.23804 | 0.20142 | 122.5433 | 122.5296 | -0.22888 | -0.20599 | 122.2916 | 122.3785 | 122.3419 | 122.2916
2225.6875 | 122.6212 | -122.3511 | 0.1236 | 0.0055694 | 0.017771 | 0.010179 | -0.0035569 | 0.019284 | -0.006789 | 0.0013202 | -0.0043029 | 0.049661 | 0.0078186 | 0.0017132 | 0.001833 | 0.016932 | -0.0002244 | -0.059509 | 0.07782 | -0.064087 | -0.050354 | 0.10986 | -0.018311 | 0.009155 | -0.027466 | 0.091553 | -0.068665 | 0.018311 | 0.11444 | 0.022888 | 0.13733 | 122.287 | -0.045776 | -0.17395 | 122.4609 | 122.3602 | 122.3328 | 0.073242 | 0.045776 | 122.2824 | -0.032043 | -0.10528 | 122.4655 | 122.4884 | 122.374 | 0.20599 | 0.091553 | 0.17395 | 0.013733 | 0.18311 | 0.086976 | 0.14191 | 0.16022 | 122.4289 | 122.4426 | -0.18768 | -0.19226 | 122.3007 | 122.3694 | 122.2916 | 122.3236
2227.375 | 122.5342 | -122.4243 | 0.11902 | -0.0096891 | 0.017558 | 0.010179 | -0.0014207 | 0.025265 | -0.0037982 | -0.0012434 | 0.0018005 | 0.052225 | 0.0078186 | -0.0098224 | -0.0030804 | 0.012873 | -0.003215 | -0.09613 | 0.11444 | -0.1236 | -0.10529 | 0.036621 | -0.050354 | -0.027466 | -0.07782 | 0.10529 | -0.064087 | -0.027466 | 0.064087 | -0.018311 | 0.10529 | 122.3007 | -0.004578 | -0.22431 | 122.4609 | 122.3969 | 122.374 | 0.09613 | 0.073242 | 122.3602 | -0.013733 | -0.14649 | 122.4884 | 122.5296 | 122.406 | 0.16937 | 0.045776 | 0.16022 | 0.01831 | 0.12817 | 0.036621 | 0.23804 | 0.16937 | 122.5388 | 122.5296 | -0.24261 | -0.18311 | 122.319 | 122.3969 | 122.3282 | 122.3465
2229.1562 | 122.5388 | -122.4197 | 0.13275 | 0.013199 | 0.017131 | 0.010606 | -0.00056607 | 0.022915 | -0.0023028 | 0.0017474 | -0.0012513 | 0.051797 | 0.0065368 | -0.0081134 | -0.0013714 | 0.013086 | 0.0021256 | -0.07782 | 0.11444 | -0.09613 | -0.082397 | 0.068665 | -0.027466 | -0.004578 | -0.054932 | 0.14191 | -0.064087 | -0.022888 | 0.059509 | -0.009155 | 0.09613 | 122.3236 | -0.01831 | -0.21515 | 122.4884 | 122.4152 | 122.3923 | 0.091552 | 0.068664 | 122.3557 | 0.009156 | -0.15564 | 122.4792 | 122.5159 | 122.4106 | 0.16022 | 0.054932 | 0.16479 | 0.013733 | 0.1236 | 0.041199 | 0.21057 | 0.20599 | 122.5342 | 122.5616 | -0.22888 | -0.19684 | 122.3373 | 122.3969 | 122.3419 | 122.3648
2230.9219 | 122.58 | -122.406 | 0.11902 | -0.0020601 | 0.017344 | 0.011034 | -0.0035569 | 0.021634 | -0.0035846 | -0.001457 | -0.0043029 | 0.04902 | 0.0078186 | -0.0012774 | 0.00076477 | 0.013727 | -1.0598e-05 | -0.018311 | 0.082397 | -0.09613 | -0.009155 | 0.16479 | 0.045776 | 0.059509 | 0.009155 | 0.11444 | -0.027466 | 0.022888 | 0.12817 | 0.045776 | 0.14648 | 122.3099 | -0.036622 | -0.12817 | 122.5708 | 122.4655 | 122.4518 | 0.15564 | 0.14191 | 122.3785 | -0.004578 | -0.096131 | 122.5342 | 122.5525 | 122.4518 | 0.17395 | 0.073242 | 0.26092 | 0.086975 | 0.15564 | 0.050354 | 0.17853 | 0.14191 | 122.4884 | 122.5204 | -0.21515 | -0.14649 | 122.3969 | 122.4289 | 122.3877 | 122.4152
2232.625 | 122.6028 | -122.406 | 0.1236 | 0.0055694 | 0.017771 | 0.012315 | -0.0014207 | 0.017361 | -0.0023028 | 0.0021746 | 0.0018005 | 0.048807 | 0.0067504 | -0.0059772 | -0.0020122 | 0.0133 | 0.0008438 | -0.009155 | 0.073242 | -0.059509 | -0.009155 | 0.15564 | 0.050354 | 0.050354 | 0.027466 | 0.10986 | -0.050354 | 0.045776 | 0.11902 | 0.041199 | 0.14648 | 122.3465 | -0.050354 | -0.13275 | 122.5616 | 122.4564 | 122.4564 | 0.10986 | 0.10986 | 122.3557 | -0.013733 | -0.07782 | 122.525 | 122.5525 | 122.4472 | 0.19684 | 0.091553 | 0.21515 | 0.050354 | 0.16937 | 0.09613 | 0.13275 | 0.16022 | 122.4792 | 122.5159 | -0.1831 | -0.17395 | 122.3969 | 122.4518 | 122.3969 | 122.4335
2234.3906 | 122.6761 | -122.3923 | 0.09613 | 0.0055694 | 0.017558 | 0.011247 | 0.00028833 | 0.017148 | -0.0031574 | 0.0030292 | -0.0012513 | 0.050302 | 0.0078186 | -0.0068316 | 0.0061054 | 0.015436 | 0.0042618 | -0.045776 | 0.11444 | -0.09613 | -0.032043 | 0.1236 | -0.018311 | 0.022888 | 0.018311 | 0.086975 | -0.054932 | 0.068665 | 0.13275 | 0.054932 | 0.19226 | 122.2961 | 0.018311 | -0.12817 | 122.5159 | 122.4152 | 122.374 | 0.11902 | 0.077819 | 122.3373 | -0.009155 | -0.027465 | 122.525 | 122.5845 | 122.4472 | 0.24719 | 0.10986 | 0.21973 | 0.064087 | 0.18768 | 0.1236 | 0.21057 | 0.14191 | 122.5067 | 122.4792 | -0.19226 | -0.15106 | 122.3602 | 122.4609 | 122.3465 | 122.4106
2236.0938 | 122.58 | -122.4197 | 0.10986 | -0.0096891 | 0.016917 | 0.011675 | -0.00077967 | 0.021634 | -0.0012348 | 3.8448e-05 | 0.0018005 | 0.049661 | 0.0080322 | -0.010677 | -8.9634e-05 | 0.014368 | 0.001912 | -0.022888 | 0.09613 | -0.073242 | -0.018311 | 0.13733 | 0.045776 | 0.050354 | 0.022888 | 0.12817 | -0.041199 | 0 | 0.10071 | 0.032043 | 0.13275 | 122.3465 | -0.013733 | -0.12817 | 122.5571 | 122.4701 | 122.4655 | 0.1236 | 0.11902 | 122.3785 | 0.018311 | -0.10986 | 122.5204 | 122.5525 | 122.4518 | 0.17395 | 0.073242 | 0.21057 | 0.054931 | 0.14191 | 0.041199 | 0.16937 | 0.16937 | 122.5159 | 122.5479 | -0.18311 | -0.15106 | 122.4014 | 122.4197 | 122.3969 | 122.4426
2237.8438 | 122.6807 | -122.3694 | 0.10529 | -0.0096891 | 0.015422 | 0.014024 | -0.0039841 | 0.021847 | -0.0031574 | 0.0032428 | 0.0018005 | 0.049234 | 0.007605 | -0.0059772 | 0.0016194 | 0.014795 | -0.0044968 | -0.050354 | 0.082397 | -0.07782 | -0.022888 | 0.15106 | 0.032043 | 0.073242 | 0.027466 | 0.07782 | -0.064087 | 0.091553 | 0.19226 | 0.091553 | 0.21057 | 122.2916 | -0.022889 | -0.12817 | 122.5204 | 122.4426 | 122.4014 | 0.15106 | 0.10986 | 122.3053 | -0.027466 | -0.013733 | 122.5616 | 122.58 | 122.4609 | 0.27466 | 0.15564 | 0.22888 | 0.054932 | 0.25635 | 0.15564 | 0.16022 | 0.14191 | 122.4518 | 122.4472 | -0.18311 | -0.16937 | 122.3465 | 122.4609 | 122.319 | 122.3969
2239.5625 | 122.5571 | -122.4243 | 0.13275 | -0.0020601 | 0.019053 | 0.0082566 | -0.0018479 | 0.023556 | -0.00508 | 0.0023882 | 0.0018005 | 0.050088 | 0.0065368 | -0.0019184 | -0.00030343 | 0.013727 | 0.000203 | -0.032043 | 0.086975 | -0.086975 | -0.050354 | 0.10986 | -0.009155 | 0.009155 | -0.027466 | 0.14191 | -0.059509 | -0.022888 | 0.082397 | 0.004578 | 0.10529 | 122.3373 | -0.045776 | -0.18311 | 122.5342 | 122.4335 | 122.4152 | 0.09613 | 0.07782 | 122.3648 | 0.009156 | -0.15564 | 122.5067 | 122.5296 | 122.4289 | 0.16479 | 0.064087 | 0.19684 | 0.036621 | 0.14191 | 0.036621 | 0.17395 | 0.20142 | 122.5113 | 122.5662 | -0.21973 | -0.19226 | 122.374 | 122.4014 | 122.3923 | 122.3969
2241.3125 | 122.6303 | -122.3831 | 0.10529 | -0.0096891 | 0.016062 | 0.012956 | -0.00035247 | 0.024197 | -0.001662 | -0.00038875 | -0.0012513 | 0.050302 | 0.0061096 | -0.00063659 | 0.0022602 | 0.012232 | -0.000438 | -0.059509 | 0.091553 | -0.07782 | -0.045776 | 0.11444 | -0.018311 | 0.032043 | -0.036621 | 0.086975 | -0.068665 | 0.032043 | 0.11444 | 0.013733 | 0.13733 | 122.3053 | -0.013733 | -0.15106 | 122.4976 | 122.4152 | 122.3648 | 0.10986 | 0.059509 | 122.3145 | -0.018311 | -0.073243 | 122.4976 | 122.5204 | 122.3969 | 0.20599 | 0.082398 | 0.19226 | 0.032044 | 0.18311 | 0.10071 | 0.16937 | 0.15564 | 122.4747 | 122.4701 | -0.18311 | -0.17395 | 122.3373 | 122.4152 | 122.3236 | 122.3465
2243.0625 | 122.6761 | -122.3557 | 0.091553 | -0.0020601 | 0.016276 | 0.011675 | -0.00013887 | 0.020993 | -0.0010212 | 0.00025205 | -0.0043029 | 0.051156 | 0.0088866 | 0.0023542 | 0.0054646 | 0.014795 | 0.0004166 | 0 | 0.045776 | -0.059509 | 0.004578 | 0.19684 | 0.022888 | 0.073242 | 0.073242 | 0.050354 | -0.041199 | 0.068665 | 0.15106 | 0.059509 | 0.1831 | 122.2961 | -0.045777 | -0.086975 | 122.5525 | 122.4289 | 122.3785 | 0.13275 | 0.082397 | 122.3145 | -0.041199 | -0.022888 | 122.5067 | 122.5388 | 122.4152 | 0.2243 | 0.10071 | 0.25635 | 0.064087 | 0.19226 | 0.10986 | 0.10528 | 0.091553 | 122.4014 | 122.406 | -0.15106 | -0.13275 | 122.3602 | 122.4243 | 122.3557 | 122.4289
2244.8281 | 122.6807 | -122.3969 | 0.10529 | -0.0096891 | 0.018626 | 0.010606 | -0.00056607 | 0.019925 | -0.0031574 | 0.0013202 | 0.0048523 | 0.04902 | 0.006964 | -0.0014912 | 0.0014056 | 0.016291 | -0.0002244 | -0.013733 | 0.073242 | -0.073242 | 0.027466 | 0.23346 | 0.086975 | 0.10529 | 0.11902 | 0.086975 | -0.045776 | 0.091553 | 0.19226 | 0.10986 | 0.20599 | 122.3236 | -0.032044 | -0.07782 | 122.6303 | 122.5021 | 122.4838 | 0.17853 | 0.16022 | 122.3511 | -0.018311 | -0.013733 | 122.5891 | 122.6028 | 122.5067 | 0.25177 | 0.15564 | 0.3067 | 0.10071 | 0.23804 | 0.13733 | 0.14648 | 0.13275 | 122.4701 | 122.4838 | -0.17853 | -0.15106 | 122.4243 | 122.4884 | 122.3831 | 122.5159
2246.5312 | 122.5479 | -122.4289 | 0.12817 | 0.013199 | 0.018626 | 0.010606 | 0.0019973 | 0.020779 | -0.001662 | 0.0011066 | 0.0018005 | 0.053506 | 0.0063232 | -0.0032 | 0.003542 | 0.013941 | -0.0002244 | -0.064087 | 0.12817 | -0.10071 | -0.12817 | -0.013733 | -0.10071 | -0.068665 | -0.11902 | 0.11444 | -0.086975 | -0.036621 | 0.009155 | -0.068665 | 0.091553 | 122.3282 | 0 | -0.25635 | 122.4152 | 122.3602 | 122.3282 | 0.032043 | 0 | 122.3419 | -0.013733 | -0.1648 | 122.438 | 122.5204 | 122.3602 | 0.17853 | 0.01831 | 0.086975 | -0.027466 | 0.09613 | 0.050354 | 0.22888 | 0.20142 | 122.5571 | 122.5433 | -0.22888 | -0.21515 | 122.3007 | 122.3923 | 122.3648 | 122.3099
2248.2969 | 122.612 | -122.3831 | 0.11902 | -0.017319 | 0.017344 | 0.0095382 | -0.00099327 | 0.025479 | -0.0012348 | 0.00089285 | -0.0073547 | 0.051797 | 0.0071776 | -0.0074726 | 0.00033757 | 0.014155 | 0.0004166 | -0.054932 | 0.11902 | -0.10986 | -0.07782 | 0.064087 | -0.027466 | -0.013733 | -0.036621 | 0.12817 | -0.064087 | 0.013733 | 0.10986 | 0.004578 | 0.13733 | 122.2733 | 0 | -0.19684 | 122.4472 | 122.3694 | 122.3557 | 0.09613 | 0.082397 | 122.319 | 0.009155 | -0.10529 | 122.493 | 122.5204 | 122.3877 | 0.20142 | 0.068665 | 0.17395 | 0.032043 | 0.17395 | 0.07782 | 0.22888 | 0.19226 | 122.5021 | 122.5113 | -0.22888 | -0.18311 | 122.3053 | 122.3969 | 122.3282 | 122.3465
2250 | 122.5616 | -122.438 | 0.13733 | -0.0020601 | 0.016703 | 0.0095382 | -0.0027023 | 0.022061 | -0.00016658 | -0.0012434 | -0.0073547 | 0.049661 | 0.0063232 | -0.0126 | -0.001585 | 0.014795 | 0.0008438 | -0.10071 | 0.13275 | -0.10986 | -0.1236 | 0.045776 | -0.054932 | -0.032043 | -0.082397 | 0.14648 | -0.073242 | -0.036621 | 0.059509 | -0.018311 | 0.10529 | 122.3282 | -0.004578 | -0.26093 | 122.4838 | 122.406 | 122.3831 | 0.07782 | 0.054931 | 122.3648 | 0.009155 | -0.17395 | 122.4976 | 122.5433 | 122.4197 | 0.17853 | 0.054931 | 0.15564 | -0.013733 | 0.13275 | 0.036621 | 0.24261 | 0.21973 | 122.5708 | 122.5845 | -0.24719 | -0.21057 | 122.3145 | 122.4014 | 122.3373 | 122.3557
2251.7656 | 122.699 | -122.4014 | 0.10071 | -0.0096891 | 0.016703 | 0.0069748 | -0.0020615 | 0.021847 | -0.0042254 | -0.00038875 | 0.0018005 | 0.049661 | 0.008673 | -0.0029864 | 0.0014056 | 0.014582 | 0.0038346 | -0.018311 | 0.082397 | -0.064087 | 0.032043 | 0.21515 | 0.068665 | 0.09613 | 0.07782 | 0.10071 | -0.041199 | 0.091553 | 0.19684 | 0.11444 | 0.21973 | 122.3373 | -0.018311 | -0.068665 | 122.6166 | 122.4976 | 122.4701 | 0.16022 | 0.13275 | 122.3602 | 0 | -0.009155 | 122.5983 | 122.6212 | 122.5159 | 0.26093 | 0.15564 | 0.27924 | 0.09613 | 0.23804 | 0.13275 | 0.14648 | 0.14191 | 122.4838 | 122.5021 | -0.1648 | -0.14191 | 122.4335 | 122.493 | 122.3831 | 122.4792
2253.5312 | 122.6852 | -122.406 | 0.091553 | -0.0096891 | 0.01649 | 0.011675 | -0.0046249 | 0.023343 | -0.001662 | 0.0013202 | -0.0012513 | 0.05137 | 0.0073914 | -0.00085019 | 0.00055117 | 0.014582 | 0.0031936 | -0.041199 | 0.091553 | -0.082397 | -0.022888 | 0.1236 | 0.009155 | 0.036621 | 0.013733 | 0.064087 | -0.045776 | 0.050354 | 0.16022 | 0.07782 | 0.17853 | 122.3236 | 0 | -0.11444 | 122.5296 | 122.4426 | 122.4152 | 0.11902 | 0.091552 | 122.3602 | -0.027466 | -0.041199 | 122.5662 | 122.5845 | 122.4838 | 0.2243 | 0.1236 | 0.20599 | 0.059509 | 0.20599 | 0.09613 | 0.17395 | 0.10986 | 122.4976 | 122.4701 | -0.17395 | -0.13733 | 122.3831 | 122.4564 | 122.3648 | 122.4197
2255.2812 | 122.5845 | -122.287 | 0.07782 | 0.0055694 | 0.020762 | 0.012315 | -0.0027023 | 0.022488 | 0.00090142 | 0.00067925 | -0.010406 | 0.050516 | 0.006964 | -0.002132 | 0.0048236 | 0.015864 | 0.0025528 | 0.032043 | 0.082397 | -0.068665 | 0.032043 | 0.18768 | 0.041199 | 0.059509 | 0.041199 | 0.041199 | -0.068665 | 0.11444 | 0.16022 | 0.059509 | 0.1831 | 122.2183 | 0.004577 | -0.045777 | 122.4747 | 122.3465 | 122.3282 | 0.12817 | 0.10986 | 122.2183 | -0.036621 | 0.036621 | 122.4472 | 122.4701 | 122.3465 | 0.25177 | 0.12817 | 0.25635 | 0.10071 | 0.22888 | 0.18311 | 0.15106 | 0.10986 | 122.3694 | 122.3282 | -0.14649 | -0.14649 | 122.319 | 122.4014 | 122.319 | 122.3282
2257.0312 | 122.4335 | -122.0901 | 0.091553 | 0.0055694 | 0.016703 | 0.012529 | -0.0033433 | 0.022915 | -0.00080758 | 0.0028154 | -0.0043029 | 0.05137 | 0.010168 | 0.0019268 | 0.0024738 | 0.013514 | -0.0008652 | -0.018311 | 0.086975 | -0.064087 | 0.004578 | 0.16479 | 0.064087 | 0.07782 | 0.068665 | 0.086975 | -0.045776 | 0.10071 | 0.1831 | 0.11444 | 0.20142 | 122.0261 | -0.004578 | -0.086975 | 122.2549 | 122.168 | 122.1542 | 0.14191 | 0.12817 | 122.0444 | -0.004578 | 0.009155 | 122.2733 | 122.2916 | 122.2046 | 0.24719 | 0.16022 | 0.22888 | 0.068665 | 0.22888 | 0.14648 | 0.15106 | 0.13275 | 122.1771 | 122.1771 | -0.15564 | -0.13733 | 122.0947 | 122.1909 | 122.0718 | 122.1588
2258.7188 | 122.3694 | -122.2229 | 0.12817 | -0.0020601 | 0.016703 | 0.011888 | -0.0022751 | 0.020779 | -0.0042254 | 3.8448e-05 | -0.0073547 | 0.051584 | 0.0078186 | -0.0057636 | 0.00033757 | 0.013727 | 0.0014846 | -0.091553 | 0.14648 | -0.11902 | -0.10986 | 0.050354 | -0.036621 | -0.032043 | -0.086975 | 0.12817 | -0.059509 | -0.022888 | 0.059509 | -0.032043 | 0.091553 | 122.1039 | 0.01831 | -0.23804 | 122.2733 | 122.1909 | 122.1863 | 0.086976 | 0.082398 | 122.1634 | 0 | -0.15106 | 122.2824 | 122.3145 | 122.1909 | 0.15106 | 0.027466 | 0.16937 | 0.009156 | 0.11902 | 0.036621 | 0.2655 | 0.18768 | 122.3694 | 122.3511 | -0.24719 | -0.18768 | 122.113 | 122.2 | 122.1313 | 122.1359
2260.4688 | 122.4976 | -122.2 | 0.082397 | 0.0055694 | 0.017344 | 0.0099656 | -0.0022751 | 0.020138 | -0.0018756 | -0.0029524 | 0.0018005 | 0.048807 | 0.0067504 | 0.005772 | 0.0020466 | 0.016077 | 0.0016982 | -0.041199 | 0.10071 | -0.073242 | -0.032043 | 0.11902 | 0.009155 | 0.050354 | 0.004578 | 0.082397 | -0.064087 | 0.064087 | 0.15564 | 0.07782 | 0.1831 | 122.1268 | 0.018311 | -0.11444 | 122.319 | 122.2504 | 122.2092 | 0.1236 | 0.082397 | 122.1359 | 0 | -0.01831 | 122.3557 | 122.3831 | 122.2778 | 0.24719 | 0.14191 | 0.19226 | 0.041199 | 0.21973 | 0.12817 | 0.17395 | 0.14648 | 122.3007 | 122.2824 | -0.15564 | -0.14648 | 122.168 | 122.2641 | 122.1588 | 122.2046
2262.2188 | 122.5388 | -122.2137 | 0.091553 | -0.0020601 | 0.01948 | 0.012315 | -0.0012069 | 0.024197 | -0.001662 | 0.00089285 | -0.0012513 | 0.050729 | 0.007605 | -0.0040546 | 0.00012397 | 0.012446 | 0.000203 | -0.013733 | 0.09613 | -0.059509 | 0.036621 | 0.20142 | 0.059509 | 0.086975 | 0.091553 | 0.07782 | -0.045776 | 0.07782 | 0.19684 | 0.12817 | 0.20599 | 122.1542 | 0.004577 | -0.054932 | 122.4152 | 122.3007 | 122.2733 | 0.14648 | 0.11902 | 122.168 | -0.013733 | -0.013733 | 122.4106 | 122.4197 | 122.3419 | 0.25177 | 0.17395 | 0.26093 | 0.09613 | 0.24261 | 0.1236 | 0.15564 | 0.1236 | 122.3099 | 122.2916 | -0.15106 | -0.13733 | 122.2504 | 122.2916 | 122.2 | 122.3053
2263.9844 | 122.5113 | -122.2641 | 0.09613 | -0.0020601 | 0.017344 | 0.012956 | -0.00013887 | 0.02377 | -0.0010212 | 0.001961 | 0.0018005 | 0.053293 | 0.007605 | -0.0019184 | 0.0022602 | 0.016718 | -0.0030014 | -0.054932 | 0.12817 | -0.09613 | -0.054932 | 0.059509 | -0.054932 | -0.004578 | -0.022888 | 0.091553 | -0.082397 | 0.050354 | 0.10986 | 0.027466 | 0.16937 | 122.168 | 0.032044 | -0.15106 | 122.3236 | 122.2595 | 122.2092 | 0.091552 | 0.041198 | 122.1817 | -0.004577 | -0.045776 | 122.374 | 122.4335 | 122.2916 | 0.25177 | 0.10986 | 0.15564 | 0.041198 | 0.19226 | 0.13275 | 0.2243 | 0.17395 | 122.3923 | 122.3557 | -0.19226 | -0.17853 | 122.2092 | 122.3145 | 122.2092 | 122.2412
2265.6719 | 122.5113 | -122.2549 | 0.10986 | -0.0020601 | 0.016917 | 0.012743 | -0.00056607 | 0.024838 | -0.00016658 | 3.8448e-05 | -0.0012513 | 0.052865 | 0.0091002 | -0.0025592 | 0.001833 | 0.015223 | 0.001912 | -0.054932 | 0.091553 | -0.07782 | -0.032043 | 0.11444 | -0.004578 | 0.022888 | -0.036621 | 0.086975 | -0.068665 | 0.022888 | 0.11444 | 0.013733 | 0.15564 | 122.1771 | -0.01831 | -0.14191 | 122.3694 | 122.2778 | 122.2504 | 0.10071 | 0.073242 | 122.1863 | -0.022888 | -0.086975 | 122.3694 | 122.4106 | 122.2687 | 0.22431 | 0.082398 | 0.19226 | 0.045777 | 0.18311 | 0.091553 | 0.16937 | 0.15564 | 122.3465 | 122.3419 | -0.18768 | -0.17853 | 122.2229 | 122.2778 | 122.2 | 122.2183
2267.4219 | 122.5479 | -122.3007 | 0.10986 | 0.013199 | 0.017985 | 0.012529 | 0.00028833 | 0.023556 | -0.00059378 | 0.0023882 | -0.0012513 | 0.050516 | 0.007605 | -0.003841 | 0.0022602 | 0.014368 | 0.0023392 | -0.082397 | 0.12817 | -0.086975 | -0.054932 | 0.073242 | -0.045776 | -0.027466 | -0.045776 | 0.10071 | -0.091553 | 0.032043 | 0.11444 | 0.004578 | 0.15564 | 122.2137 | 0.018311 | -0.16479 | 122.374 | 122.2733 | 122.2549 | 0.059509 | 0.041199 | 122.2092 | -0.009155 | -0.07782 | 122.4152 | 122.4564 | 122.3053 | 0.24719 | 0.096131 | 0.16022 | 0.032043 | 0.20599 | 0.1236 | 0.21515 | 0.19226 | 122.4289 | 122.4014 | -0.19684 | -0.20142 | 122.2458 | 122.3328 | 122.2183 | 122.2549
2269.1875 | 122.5983 | -122.2641 | 0.10071 | 0.020828 | 0.014567 | 0.009752 | -0.0024887 | 0.023556 | -0.0027302 | 3.8448e-05 | 0.0079041 | 0.050516 | 0.0091002 | 0.0017132 | -0.0017986 | 0.01565 | 0.0025528 | -0.009155 | 0.086975 | -0.050354 | 0.054932 | 0.2243 | 0.09613 | 0.11444 | 0.09613 | 0.086975 | -0.036621 | 0.086975 | 0.20142 | 0.1236 | 0.22888 | 122.2137 | -0.013733 | -0.045776 | 122.4884 | 122.3785 | 122.3602 | 0.16479 | 0.14648 | 122.2275 | -0.013733 | -0.013733 | 122.4655 | 122.493 | 122.3877 | 0.2655 | 0.16022 | 0.27466 | 0.10529 | 0.23804 | 0.1236 | 0.13733 | 0.1236 | 122.3511 | 122.3511 | -0.15106 | -0.13733 | 122.319 | 122.3511 | 122.2549 | 122.3602
2270.9375 | 122.5388 | -122.3328 | 0.11444 | 0.0055694 | 0.016062 | 0.013811 | -0.0016343 | 0.022275 | -0.0025166 | -0.0010298 | -0.0012513 | 0.050088 | 0.0065368 | -0.0032 | -0.0020122 | 0.012018 | 0.000203 | -0.009155 | 0.10529 | -0.059509 | 0.022888 | 0.16022 | 0.050354 | 0.050354 | 0.027466 | 0.10986 | -0.032043 | 0.054932 | 0.15564 | 0.050354 | 0.16937 | 122.2733 | -0.009155 | -0.091553 | 122.493 | 122.3831 | 122.3831 | 0.10986 | 0.10986 | 122.3007 | -0.004578 | -0.059509 | 122.4884 | 122.5021 | 122.3831 | 0.20142 | 0.082397 | 0.21973 | 0.082397 | 0.18768 | 0.086975 | 0.16479 | 0.14191 | 122.4381 | 122.4426 | -0.17395 | -0.14648 | 122.3557 | 122.3877 | 122.3236 | 122.3602
2272.625 | 122.5021 | -122.3145 | 0.11444 | 0.0055694 | 0.017771 | 0.012102 | -0.00035247 | 0.020352 | -0.0031574 | -0.003166 | 0.0018005 | 0.053293 | 0.0065368 | -0.0091816 | -0.001585 | 0.014368 | -0.001506 | -0.013733 | 0.10071 | -0.068665 | -0.013733 | 0.16479 | 0.050354 | 0.050354 | 0.022888 | 0.10986 | -0.050354 | 0.009155 | 0.1236 | 0.027466 | 0.14191 | 122.2458 | -0.013733 | -0.12817 | 122.4792 | 122.3648 | 122.3648 | 0.11902 | 0.11902 | 122.2641 | -0.004578 | -0.10529 | 122.438 | 122.4564 | 122.3419 | 0.19226 | 0.07782 | 0.23346 | 0.054932 | 0.17395 | 0.059509 | 0.16937 | 0.16022 | 122.4152 | 122.4243 | -0.18311 | -0.16479 | 122.3007 | 122.3236 | 122.3007 | 122.3373
2274.375 | 122.5296 | -122.3145 | 0.12817 | -0.0096891 | 0.017558 | 0.011675 | -0.00013887 | 0.020138 | -0.0023028 | 0.00089285 | -0.0012513 | 0.052225 | 0.0080322 | -0.0053364 | 0.003542 | 0.013086 | -0.003215 | -0.022888 | 0.11902 | -0.091553 | -0.050354 | 0.10071 | -0.027466 | -0.004578 | 0.013733 | 0.11444 | -0.050354 | 0.050354 | 0.11444 | 0.009155 | 0.14648 | 122.2229 | -0.009155 | -0.17853 | 122.4152 | 122.3099 | 122.287 | 0.086975 | 0.064087 | 122.2641 | -0.013733 | -0.07782 | 122.4289 | 122.4609 | 122.3236 | 0.19684 | 0.059509 | 0.19226 | 0.041199 | 0.16479 | 0.10071 | 0.21057 | 0.16479 | 122.4335 | 122.4289 | -0.21973 | -0.17853 | 122.2641 | 122.3648 | 122.2916 | 122.3282
2276.1406 | 122.6166 | -122.3007 | 0.09613 | -0.0020601 | 0.016062 | 0.011888 | -0.0016343 | 0.025692 | -0.0023028 | 0.0013202 | -0.010406 | 0.049234 | 0.0067504 | -0.00085019 | 0.0041828 | 0.014795 | 0.001271 | 0.009155 | 0.068665 | -0.045776 | 0.009155 | 0.16022 | 0.018311 | 0.054932 | 0.036621 | 0.041199 | -0.059509 | 0.082397 | 0.16937 | 0.068665 | 0.19684 | 122.2549 | -0.027465 | -0.086975 | 122.4609 | 122.3557 | 122.319 | 0.10071 | 0.064087 | 122.2412 | -0.054931 | -0.013733 | 122.4701 | 122.4976 | 122.3694 | 0.25635 | 0.12817 | 0.20599 | 0.054931 | 0.22888 | 0.14191 | 0.11444 | 0.10071 | 122.3694 | 122.3419 | -0.14191 | -0.15564 | 122.3099 | 122.3831 | 122.3099 | 122.3373
2277.9062 | 122.493 | -122.3557 | 0.11444 | -0.0020601 | 0.018412 | 0.011461 | -0.0016343 | 0.020779 | -0.0031574 | 0.0021746 | -0.0073547 | 0.052438 | 0.0082458 | 0.00043161 | -0.003294 | 0.013086 | -0.000438 | -0.064087 | 0.10986 | -0.082397 | -0.073242 | 0.068665 | -0.027466 | -0.013733 | -0.054932 | 0.15106 | -0.068665 | -0.027466 | 0.073242 | -0.013733 | 0.10071 | 122.2733 | -0.004578 | -0.18768 | 122.4243 | 122.3419 | 122.3282 | 0.068664 | 0.054931 | 122.287 | 0.036621 | -0.14191 | 122.4289 | 122.4564 | 122.3419 | 0.16937 | 0.054932 | 0.15106 | 0.009155 | 0.14191 | 0.041199 | 0.19226 | 0.21973 | 122.4655 | 122.5067 | -0.19684 | -0.18311 | 122.2824 | 122.3282 | 122.2916 | 122.3007
2279.625 | 122.5021 | -122.3511 | 0.14191 | -0.0020601 | 0.018626 | 0.012743 | 0.0015701 | 0.025052 | -0.0020892 | 0.0015338 | 0.0018005 | 0.052438 | 0.0084594 | -0.0040546 | 0.0052508 | 0.0133 | 0.0034072 | -0.073242 | 0.10986 | -0.091553 | -0.10986 | 0.018311 | -0.091553 | -0.059509 | -0.10986 | 0.10071 | -0.091553 | -0.032043 | 0.013733 | -0.064087 | 0.086975 | 122.2595 | -0.032044 | -0.25177 | 122.3694 | 122.2916 | 122.2595 | 0.032044 | 0 | 122.2595 | -0.041199 | -0.17395 | 122.3648 | 122.438 | 122.287 | 0.17853 | 0.027466 | 0.10986 | -0.01831 | 0.10529 | 0.05951 | 0.20142 | 0.19226 | 122.4609 | 122.4518 | -0.23346 | -0.23346 | 122.2412 | 122.319 | 122.2778 | 122.2412
2281.3906 | 122.5479 | -122.3511 | 0.10529 | -0.0096891 | 0.01884 | 0.010393 | -0.00013887 | 0.024197 | -0.0046528 | -0.00081595 | 0.0018005 | 0.052225 | 0.0039734 | -0.0081134 | 0.0016194 | 0.0133 | -0.0036422 | -0.032043 | 0.1236 | -0.09613 | -0.045776 | 0.10986 | -0.013733 | 0.013733 | 0.009155 | 0.091553 | -0.059509 | 0.041199 | 0.11902 | 0.027466 | 0.16022 | 122.2549 | 0.01831 | -0.15106 | 122.4609 | 122.3648 | 122.3373 | 0.10986 | 0.082397 | 122.2916 | -0.013733 | -0.064087 | 122.4701 | 122.5113 | 122.3785 | 0.21973 | 0.086975 | 0.20599 | 0.050354 | 0.17853 | 0.10071 | 0.21973 | 0.15106 | 122.4747 | 122.4426 | -0.20142 | -0.16479 | 122.3053 | 122.3923 | 122.319 | 122.3602
2283.0938 | 122.4747 | -122.3602 | 0.14648 | 0.0055694 | 0.019694 | 0.012529 | -0.0012069 | 0.02847 | -0.00059378 | 0.00046565 | -0.0012513 | 0.051797 | 0.010168 | -0.0044818 | 0.0031146 | 0.0133 | -0.0019332 | -0.050354 | 0.11902 | -0.091553 | -0.09613 | 0.050354 | -0.059509 | -0.054932 | -0.086975 | 0.11444 | -0.086975 | -0.032043 | 0.041199 | -0.068665 | 0.07782 | 122.2687 | -0.027465 | -0.24261 | 122.4106 | 122.3053 | 122.3007 | 0.036621 | 0.032044 | 122.2733 | -0.032043 | -0.17853 | 122.4014 | 122.438 | 122.2916 | 0.16479 | 0.01831 | 0.14191 | -0.004577 | 0.12817 | 0.054932 | 0.21057 | 0.20142 | 122.4792 | 122.4747 | -0.23804 | -0.23346 | 122.2641 | 122.3282 | 122.3099 | 122.2733
2284.8594 | 122.644 | -122.3236 | 0.07782 | 0.013199 | 0.017558 | 0.013384 | -0.0012069 | 0.02377 | -0.0012348 | 0.0026018 | -0.0012513 | 0.050729 | 0.0099548 | -0.0010638 | 0.0052508 | 0.015436 | -0.0030014 | -0.036621 | 0.11902 | -0.082397 | -0.027466 | 0.14191 | 0.009155 | 0.036621 | 0.027466 | 0.073242 | -0.054932 | 0.091553 | 0.14191 | 0.059509 | 0.19684 | 122.2412 | 0.041199 | -0.10529 | 122.4655 | 122.3602 | 122.3328 | 0.11902 | 0.091552 | 122.2687 | -0.004578 | 0.013733 | 122.4655 | 122.5204 | 122.3831 | 0.25177 | 0.11444 | 0.2243 | 0.054931 | 0.19684 | 0.14649 | 0.20142 | 0.12817 | 122.4426 | 122.3968 | -0.16022 | -0.13275 | 122.2961 | 122.4152 | 122.287 | 122.3511
2286.5625 | 122.6624 | -122.3373 | 0.09613 | 0.0055694 | 0.015635 | 0.011675 | -0.0027023 | 0.02142 | -0.0018756 | -0.0012434 | 0.0048523 | 0.049234 | 0.0091002 | -0.002132 | 0.00055117 | 0.014582 | -0.0002244 | -0.022888 | 0.091553 | -0.064087 | 0.027466 | 0.21973 | 0.086975 | 0.09613 | 0.10529 | 0.068665 | -0.045776 | 0.09613 | 0.20599 | 0.11444 | 0.21057 | 122.2733 | -0.004577 | -0.068664 | 122.5571 | 122.4335 | 122.4243 | 0.16022 | 0.15106 | 122.2916 | -0.027465 | 0 | 122.5433 | 122.5479 | 122.4518 | 0.25635 | 0.16022 | 0.28381 | 0.091553 | 0.25177 | 0.14191 | 0.15564 | 0.11444 | 122.4289 | 122.406 | -0.16022 | -0.14191 | 122.3648 | 122.4335 | 122.3145 | 122.4426
2288.2656 | 122.6486 | -122.3465 | 0.10986 | 0.0055694 | 0.016703 | 0.01082 | -0.0027023 | 0.021847 | 0.0019696 | 0.0015338 | -0.0012513 | 0.049447 | 0.0097412 | -0.0061908 | 0.00012397 | 0.014155 | -0.0019332 | -0.018311 | 0.073242 | -0.068665 | 0.027466 | 0.21515 | 0.091553 | 0.10529 | 0.086975 | 0.091553 | -0.041199 | 0.09613 | 0.20599 | 0.12817 | 0.21973 | 122.2778 | -0.036621 | -0.082397 | 122.5616 | 122.4518 | 122.4381 | 0.17395 | 0.16022 | 122.3053 | -0.01831 | -0.013733 | 122.5525 | 122.5662 | 122.4747 | 0.26093 | 0.16937 | 0.28381 | 0.096131 | 0.24719 | 0.13733 | 0.14191 | 0.13275 | 122.4197 | 122.4381 | -0.17853 | -0.15106 | 122.374 | 122.4426 | 122.3282 | 122.4335
2290.0312 | 122.6349 | -122.3602 | 0.086975 | -0.017319 | 0.014781 | 0.011675 | -0.0024887 | 0.018857 | -0.0029438 | 0.0011066 | -0.0073547 | 0.049875 | 0.0048278 | -0.0014912 | 0.0026874 | 0.014795 | 0.0014846 | -0.032043 | 0.059509 | -0.032043 | 0.004578 | 0.18768 | 0.032043 | 0.064087 | 0.054932 | 0.068665 | -0.022888 | 0.073242 | 0.13733 | 0.050354 | 0.19684 | 122.3282 | -0.027466 | -0.082397 | 122.5479 | 122.4243 | 122.3923 | 0.09613 | 0.064086 | 122.3373 | -0.01831 | -0.013733 | 122.4976 | 122.5571 | 122.4106 | 0.21973 | 0.073242 | 0.21973 | 0.036621 | 0.16022 | 0.09613 | 0.091552 | 0.091553 | 122.4197 | 122.4289 | -0.11902 | -0.10986 | 122.3648 | 122.4335 | 122.3282 | 122.4152
2291.7969 | 122.6578 | -122.3282 | 0.10529 | 0.0055694 | 0.019694 | 0.012743 | -0.00077967 | 0.026333 | 4.7018e-05 | 3.8448e-05 | -0.0073547 | 0.049661 | 0.0080322 | -0.0053364 | 0.0033282 | 0.017359 | 0.0021256 | 0.004578 | 0.082397 | -0.064087 | 0.009155 | 0.18768 | 0.027466 | 0.045776 | 0.045776 | 0.050354 | -0.045776 | 0.086975 | 0.16937 | 0.07782 | 0.19684 | 122.2641 | -0.022889 | -0.096131 | 122.5159 | 122.374 | 122.3557 | 0.10986 | 0.091553 | 122.2824 | -0.054932 | -0.018311 | 122.4976 | 122.525 | 122.406 | 0.24261 | 0.1236 | 0.25177 | 0.073242 | 0.21515 | 0.13275 | 0.14648 | 0.09613 | 122.4106 | 122.3785 | -0.16937 | -0.15106 | 122.3373 | 122.4152 | 122.3328 | 122.374
2293.5469 | 122.5433 | -122.3877 | 0.13275 | -0.0020601 | 0.018626 | 0.012743 | 0.00092933 | 0.023343 | 0.00090142 | -0.00017515 | -0.0012513 | 0.052438 | 0.0091002 | -0.0081134 | 0.0037556 | 0.015009 | 0.001912 | -0.068665 | 0.14191 | -0.10071 | -0.10529 | 0.032043 | -0.091553 | -0.050354 | -0.086975 | 0.09613 | -0.082397 | -0.022888 | 0.018311 | -0.068665 | 0.09613 | 122.287 | 0.009156 | -0.23804 | 122.4197 | 122.3373 | 122.2961 | 0.050354 | 0.009155 | 122.3053 | -0.036621 | -0.15564 | 122.406 | 122.4838 | 122.319 | 0.17853 | 0.013732 | 0.13275 | -0.004578 | 0.10071 | 0.059509 | 0.24262 | 0.17853 | 122.5296 | 122.4838 | -0.23346 | -0.21515 | 122.2824 | 122.3648 | 122.319 | 122.3007
2295.25 | 122.6349 | -122.3648 | 0.10071 | -0.0020601 | 0.017558 | 0.01082 | -0.0012069 | 0.01672 | -0.001662 | -0.0027386 | 0.0018005 | 0.04902 | 0.0050414 | -0.00063659 | 0.00012397 | 0.01565 | 0.0016982 | -0.004578 | 0.091553 | -0.059509 | 0.013733 | 0.18768 | 0.073242 | 0.086975 | 0.045776 | 0.091553 | -0.045776 | 0.059509 | 0.17853 | 0.073242 | 0.19226 | 122.3053 | -0.009155 | -0.086975 | 122.5525 | 122.4518 | 122.438 | 0.14648 | 0.13275 | 122.319 | -0.009155 | -0.041199 | 122.5433 | 122.5571 | 122.438 | 0.23804 | 0.11902 | 0.24719 | 0.073242 | 0.2243 | 0.10528 | 0.15106 | 0.13733 | 122.4564 | 122.4564 | -0.16022 | -0.14648 | 122.3785 | 122.4243 | 122.3602 | 122.4106
2297.0156 | 122.5525 | -122.3923 | 0.14191 | 0.013199 | 0.015849 | 0.0099656 | -0.0018479 | 0.023343 | -0.0023028 | -0.00017515 | -0.0012513 | 0.051156 | 0.0091002 | -0.00063659 | -0.00073063 | 0.013514 | 0.0040482 | -0.050354 | 0.09613 | -0.086975 | -0.059509 | 0.091553 | 0 | -0.009155 | -0.050354 | 0.14191 | -0.068665 | -0.027466 | 0.07782 | -0.009155 | 0.11444 | 122.3053 | -0.045777 | -0.20142 | 122.4838 | 122.3831 | 122.3923 | 0.07782 | 0.086975 | 122.3236 | 0 | -0.16937 | 122.4701 | 122.5067 | 122.3831 | 0.18311 | 0.05951 | 0.17853 | 0.027466 | 0.14649 | 0.041199 | 0.1831 | 0.21057 | 122.4884 | 122.5342 | -0.22888 | -0.21057 | 122.3328 | 122.3648 | 122.3419 | 122.3419
2298.7188 | 122.5616 | -122.3923 | 0.13733 | 0.0055694 | 0.016703 | 0.011247 | -0.00013887 | 0.020779 | -0.0012348 | -0.00038875 | 0.0018005 | 0.050729 | 0.0084594 | 4.214e-06 | -0.00030343 | 0.012659 | 0.0014846 | 0 | 0.10986 | -0.07782 | -0.018311 | 0.15106 | 0.050354 | 0.036621 | 0.009155 | 0.10529 | -0.059509 | 0.004578 | 0.10986 | 0.022888 | 0.12817 | 122.3145 | -0.027466 | -0.15564 | 122.5433 | 122.4289 | 122.4426 | 0.11444 | 0.12817 | 122.3328 | -0.032043 | -0.13275 | 122.5021 | 122.5204 | 122.4152 | 0.18768 | 0.082397 | 0.22888 | 0.059509 | 0.16937 | 0.064087 | 0.18768 | 0.16479 | 122.5021 | 122.4976 | -0.21515 | -0.19684 | 122.374 | 122.3969 | 122.3923 | 122.4014
2300.4844 | 122.5937 | -122.3831 | 0.12817 | -0.017319 | 0.015849 | 0.0093246 | -0.00056607 | 0.025479 | -0.0037982 | -0.0016706 | -0.0043029 | 0.050088 | 0.005255 | -0.0019184 | 0.0033282 | 0.012659 | 0.0008438 | -0.07782 | 0.12817 | -0.10071 | -0.091553 | 0.059509 | -0.032043 | -0.018311 | -0.064087 | 0.12817 | -0.050354 | 0.004578 | 0.10071 | 0.013733 | 0.14191 | 122.2824 | 0 | -0.21973 | 122.4426 | 122.3648 | 122.3511 | 0.082397 | 0.068665 | 122.3328 | 0 | -0.1236 | 122.4838 | 122.525 | 122.3969 | 0.19226 | 0.064087 | 0.16022 | 0.009155 | 0.15106 | 0.054932 | 0.22888 | 0.17853 | 122.5113 | 122.5113 | -0.22888 | -0.17853 | 122.2916 | 122.3877 | 122.3053 | 122.319
2302.2031 | 122.6349 | -122.3831 | 0.11902 | -0.0096891 | 0.017131 | 0.010393 | -0.00077967 | 0.024838 | -0.0020892 | -0.00017515 | -0.0012513 | 0.051156 | 0.0084594 | -0.0019184 | 0.0041828 | 0.015009 | -0.0019332 | -0.064087 | 0.11444 | -0.10071 | -0.082397 | 0.073242 | -0.054932 | -0.018311 | -0.022888 | 0.09613 | -0.073242 | 0.041199 | 0.1236 | 0.022888 | 0.15106 | 122.2824 | -0.004578 | -0.20142 | 122.4564 | 122.3648 | 122.3282 | 0.082397 | 0.045776 | 122.3099 | -0.022889 | -0.07782 | 122.5067 | 122.5342 | 122.406 | 0.2243 | 0.09613 | 0.17395 | 0.018311 | 0.19684 | 0.11444 | 0.21515 | 0.16937 | 122.4976 | 122.4792 | -0.21973 | -0.19226 | 122.3007 | 122.4243 | 122.319 | 122.3602
2303.9688 | 122.5525 | -122.4243 | 0.11902 | 0.013199 | 0.020121 | 0.01082 | -0.0014207 | 0.019925 | -0.0012348 | 0.0017474 | 0.0048523 | 0.051156 | 0.010596 | -0.0046954 | 0.0016194 | 0.013727 | 0.0038346 | -0.032043 | 0.10071 | -0.091553 | -0.050354 | 0.11902 | 0.013733 | 0.009155 | -0.041199 | 0.11902 | -0.064087 | -0.018311 | 0.086975 | -0.018311 | 0.09613 | 122.3328 | -0.018311 | -0.16937 | 122.5433 | 122.4335 | 122.438 | 0.10071 | 0.10529 | 122.3602 | 0 | -0.13733 | 122.5113 | 122.5204 | 122.406 | 0.16022 | 0.045776 | 0.21057 | 0.041199 | 0.15106 | 0.045776 | 0.19226 | 0.18311 | 122.525 | 122.5433 | -0.21057 | -0.18311 | 122.374 | 122.406 | 122.3923 | 122.3831
2305.7344 | 122.6028 | -122.4106 | 0.10986 | 0.0055694 | 0.018626 | 0.011461 | -0.0020615 | 0.022488 | -0.003371 | 0.0015338 | 0.0018005 | 0.048379 | 0.0078186 | -0.0027728 | 0.00055117 | 0.012446 | 0.001912 | -0.013733 | 0.091553 | -0.082397 | -0.027466 | 0.15106 | 0.041199 | 0.041199 | 0.004578 | 0.11902 | -0.050354 | 0.009155 | 0.10529 | 0.013733 | 0.1236 | 122.3282 | -0.01831 | -0.13733 | 122.5616 | 122.4518 | 122.4518 | 0.1236 | 0.1236 | 122.3602 | 0.009156 | -0.10071 | 122.5159 | 122.5342 | 122.4243 | 0.17395 | 0.064087 | 0.23346 | 0.054931 | 0.15564 | 0.059509 | 0.17395 | 0.16937 | 122.5021 | 122.5296 | -0.19226 | -0.16022 | 122.3831 | 122.4197 | 122.3969 | 122.4152
2307.4844 | 122.6624 | -122.4152 | 0.10529 | -0.0096891 | 0.014994 | 0.011675 | -0.0016343 | 0.024197 | -0.0040118 | -0.001457 | 0.0018005 | 0.050302 | 0.0073914 | 0.00085881 | 0.0022602 | 0.016291 | 0.000203 | -0.059509 | 0.086975 | -0.068665 | -0.027466 | 0.11902 | 0.018311 | 0.041199 | 0.004578 | 0.091553 | -0.054932 | 0.041199 | 0.14191 | 0.050354 | 0.17853 | 122.3465 | -0.018311 | -0.13275 | 122.5342 | 122.4564 | 122.4335 | 0.10986 | 0.086976 | 122.3602 | -0.013733 | -0.064087 | 122.5571 | 122.5937 | 122.4655 | 0.23346 | 0.10529 | 0.18768 | 0.041199 | 0.19684 | 0.096131 | 0.15564 | 0.14649 | 122.5021 | 122.5067 | -0.17395 | -0.16022 | 122.3877 | 122.4564 | 122.3557 | 122.4197
2309.2656 | 122.6395 | -122.3831 | 0.10986 | 0.0055694 | 0.014567 | 0.011034 | -0.0016343 | 0.022061 | -0.0027302 | 0.00025205 | -0.0043029 | 0.051797 | 0.005255 | -0.00085019 | 0.0014056 | 0.012659 | 0.0004166 | -0.054932 | 0.073242 | -0.064087 | -0.036621 | 0.11444 | 0.004578 | 0.032043 | -0.022888 | 0.082397 | -0.064087 | 0.036621 | 0.13275 | 0.018311 | 0.16022 | 122.319 | -0.036621 | -0.14648 | 122.4976 | 122.4152 | 122.3877 | 0.09613 | 0.068665 | 122.319 | -0.027466 | -0.073242 | 122.5159 | 122.5433 | 122.4014 | 0.2243 | 0.082398 | 0.17853 | 0.027466 | 0.19684 | 0.10071 | 0.13733 | 0.14648 | 122.4564 | 122.4655 | -0.17395 | -0.17395 | 122.3465 | 122.4197 | 122.3282 | 122.3602
2310.9688 | 122.6624 | -122.4014 | 0.10071 | 0.0055694 | 0.018199 | 0.011461 | -0.0012069 | 0.023343 | -0.00059378 | -0.001457 | 0.0018005 | 0.052011 | 0.0099548 | -0.0081134 | 0.001833 | 0.016504 | 0.0016982 | -0.059509 | 0.11444 | -0.10071 | -0.068665 | 0.050354 | -0.054932 | -0.013733 | -0.013733 | 0.09613 | -0.068665 | 0.032043 | 0.10529 | 0.013733 | 0.15106 | 122.3007 | 0.013733 | -0.16937 | 122.4518 | 122.3877 | 122.3465 | 0.086975 | 0.045776 | 122.3328 | -0.004578 | -0.068665 | 122.5067 | 122.5525 | 122.4152 | 0.21973 | 0.082398 | 0.15106 | 0.032043 | 0.17395 | 0.10071 | 0.21515 | 0.16479 | 122.5159 | 122.4976 | -0.20142 | -0.16937 | 122.3328 | 122.4335 | 122.3419 | 122.3877
2312.7344 | 122.6486 | -122.4152 | 0.10986 | -0.0020601 | 0.013926 | 0.009111 | -0.0027023 | 0.01907 | -0.00038018 | 0.00046565 | -0.0012513 | 0.049661 | 0.006964 | 4.214e-06 | 0.0016194 | 0.015009 | -0.0023606 | -0.064087 | 0.082397 | -0.073242 | -0.036621 | 0.10071 | -0.013733 | 0.027466 | -0.009155 | 0.086975 | -0.068665 | 0.041199 | 0.15106 | 0.059509 | 0.16479 | 122.3419 | -0.027466 | -0.14648 | 122.5159 | 122.4426 | 122.4014 | 0.10071 | 0.059509 | 122.3465 | -0.022888 | -0.068664 | 122.5662 | 122.58 | 122.4747 | 0.23346 | 0.12817 | 0.17395 | 0.036621 | 0.21973 | 0.10986 | 0.15564 | 0.15564 | 122.4976 | 122.5021 | -0.18311 | -0.17853 | 122.3785 | 122.4564 | 122.3511 | 122.406
2314.4375 | 122.6212 | -122.4197 | 0.10986 | -0.017319 | 0.020548 | 0.010393 | 0.00050193 | 0.02142 | -0.0027302 | 0.00046565 | -0.0012513 | 0.051584 | 0.005896 | -0.0061908 | 0.00033757 | 0.013941 | 0.0021256 | -0.050354 | 0.1236 | -0.10529 | -0.064087 | 0.082397 | -0.027466 | -0.013733 | -0.018311 | 0.1236 | -0.059509 | 0.018311 | 0.11444 | 0.018311 | 0.14191 | 122.3145 | 0.013733 | -0.17395 | 122.5021 | 122.406 | 122.3923 | 0.091553 | 0.07782 | 122.3602 | 0.013733 | -0.091552 | 122.5342 | 122.5616 | 122.4381 | 0.20142 | 0.07782 | 0.18768 | 0.041199 | 0.17395 | 0.07782 | 0.22888 | 0.1831 | 122.5433 | 122.5433 | -0.21515 | -0.16937 | 122.3557 | 122.4381 | 122.3694 | 122.4014
2316.2031 | 122.6898 | -122.3877 | 0.073242 | -0.0096891 | 0.017558 | 0.01317 | -0.0012069 | 0.020138 | 0.00026062 | -0.0016706 | -0.0012513 | 0.050302 | 0.0067504 | 0.00085881 | 0.0041828 | 0.0133 | 0.0006302 | -0.004578 | 0.09613 | -0.073242 | 0.018311 | 0.18768 | 0.050354 | 0.054932 | 0.054932 | 0.073242 | -0.054932 | 0.091553 | 0.17395 | 0.07782 | 0.20142 | 122.3145 | 0.022888 | -0.054931 | 122.5754 | 122.4426 | 122.438 | 0.12817 | 0.1236 | 122.3328 | 0 | 0.018311 | 122.5616 | 122.5891 | 122.4655 | 0.25635 | 0.13275 | 0.26092 | 0.091553 | 0.22888 | 0.14649 | 0.16937 | 0.12817 | 122.4838 | 122.4609 | -0.14648 | -0.12817 | 122.406 | 122.4792 | 122.3831 | 122.4426
2317.8906 | 122.7127 | -122.3785 | 0.091553 | -0.0020601 | 0.01884 | 0.009111 | -0.0031297 | 0.019711 | -0.0010212 | -0.0029524 | -0.0012513 | 0.050516 | 0.010168 | -0.0036274 | 0.00012397 | 0.014795 | -0.002147 | -0.022888 | 0.091553 | -0.068665 | 0.009155 | 0.18768 | 0.073242 | 0.091553 | 0.086975 | 0.086975 | -0.054932 | 0.091553 | 0.21057 | 0.11902 | 0.23346 | 122.3099 | 0 | -0.082398 | 122.5662 | 122.4701 | 122.4518 | 0.16022 | 0.14191 | 122.3236 | -0.004578 | 0 | 122.5891 | 122.612 | 122.4976 | 0.28839 | 0.17395 | 0.25635 | 0.07782 | 0.2655 | 0.14649 | 0.16022 | 0.14191 | 122.4701 | 122.4655 | -0.16022 | -0.14649 | 122.3877 | 122.4701 | 122.3557 | 122.4655
2319.6406 | 122.7219 | -122.4197 | 0.10529 | -0.0020601 | 0.013713 | 0.011034 | -0.0016343 | 0.020566 | -0.0035846 | -0.0020978 | 0.0018005 | 0.051156 | 0.0067504 | 0.0021404 | 0.0022602 | 0.014582 | 0.0044754 | -0.018311 | 0.073242 | -0.073242 | 0.009155 | 0.19684 | 0.07782 | 0.10529 | 0.07782 | 0.082397 | -0.073242 | 0.082397 | 0.21515 | 0.1236 | 0.21515 | 122.3465 | -0.032044 | -0.096131 | 122.6166 | 122.525 | 122.4976 | 0.17853 | 0.15106 | 122.3465 | -0.022889 | -0.022889 | 122.6349 | 122.6349 | 122.5433 | 0.28839 | 0.19684 | 0.27008 | 0.082397 | 0.28839 | 0.15564 | 0.14648 | 0.15564 | 122.493 | 122.5021 | -0.17853 | -0.17853 | 122.4289 | 122.5021 | 122.4014 | 122.4976
2321.3906 | 122.7081 | -122.4197 | 0.082397 | -0.0096891 | 0.01884 | 0.014024 | -0.00035247 | 0.024411 | -0.00080758 | 0.0015338 | -0.0012513 | 0.050516 | 0.0067504 | 0.0017132 | 0.0043964 | 0.014582 | 0.0023392 | 0.013733 | 0.07782 | -0.068665 | 0.009155 | 0.17853 | 0.013733 | 0.073242 | 0.064087 | 0.059509 | -0.054932 | 0.10529 | 0.15564 | 0.073242 | 0.20599 | 122.3511 | -0.004577 | -0.073242 | 122.5983 | 122.493 | 122.4335 | 0.14191 | 0.082398 | 122.3648 | -0.022888 | 0.022889 | 122.5754 | 122.6257 | 122.493 | 0.26093 | 0.12817 | 0.24719 | 0.07782 | 0.21057 | 0.16022 | 0.14649 | 0.11444 | 122.4976 | 122.4792 | -0.15106 | -0.13733 | 122.4289 | 122.525 | 122.4335 | 122.4838
2323.0938 | 122.6349 | -122.4289 | 0.10529 | -0.0096891 | 0.017131 | 0.011461 | 0.00028833 | 0.023343 | -0.0014484 | -0.00060235 | -0.0043029 | 0.051797 | 0.011023 | -0.0070454 | -0.002226 | 0.014795 | -0.0019332 | -0.07782 | 0.11444 | -0.10986 | -0.07782 | 0.041199 | -0.032043 | -0.027466 | -0.064087 | 0.13733 | -0.064087 | 0.004578 | 0.10529 | 0.004578 | 0.13733 | 122.319 | 0.009155 | -0.18311 | 122.4701 | 122.4014 | 122.3969 | 0.082397 | 0.07782 | 122.3648 | 0.032043 | -0.10071 | 122.5342 | 122.5662 | 122.4335 | 0.20142 | 0.068665 | 0.15106 | 0.032043 | 0.16937 | 0.068665 | 0.2243 | 0.20142 | 122.5433 | 122.5662 | -0.21515 | -0.16937 | 122.3511 | 122.4335 | 122.3511 | 122.3648
2324.8594 | 122.6807 | -122.4289 | 0.10071 | -0.0096891 | 0.017985 | 0.01082 | -0.0056931 | 0.022275 | -0.0010212 | -0.00038875 | -0.0012513 | 0.049234 | 0.006964 | -0.0017048 | -0.00030343 | 0.012873 | 0.0004166 | -0.086975 | 0.10071 | -0.059509 | -0.041199 | 0.10986 | -0.009155 | 0.027466 | -0.009155 | 0.10986 | -0.068665 | 0.032043 | 0.13733 | 0.045776 | 0.16937 | 122.3694 | 0 | -0.14191 | 122.5388 | 122.4564 | 122.4197 | 0.086975 | 0.050354 | 122.3602 | 0.009155 | -0.068665 | 122.5662 | 122.5983 | 122.4747 | 0.23804 | 0.11444 | 0.16937 | 0.01831 | 0.20599 | 0.10071 | 0.16022 | 0.17853 | 122.5296 | 122.5388 | -0.16022 | -0.16937 | 122.3877 | 122.4609 | 122.3419 | 122.4197
2326.625 | 122.7356 | -122.4014 | 0.07782 | 0.0055694 | 0.015208 | 0.011675 | -0.0037705 | 0.022275 | -0.003371 | 0.00089285 | 0.0018005 | 0.050088 | 0.007605 | -0.0034138 | 0.00033757 | 0.014155 | -0.001506 | -0.009155 | 0.082397 | -0.073242 | 0.004578 | 0.20599 | 0.086975 | 0.10986 | 0.10529 | 0.073242 | -0.041199 | 0.091553 | 0.21515 | 0.13275 | 0.21515 | 122.3282 | 0.004577 | -0.073242 | 122.6074 | 122.5113 | 122.4884 | 0.18311 | 0.16022 | 122.3602 | -0.004578 | 0.013733 | 122.6166 | 122.6166 | 122.5342 | 0.25635 | 0.17395 | 0.27924 | 0.07782 | 0.25635 | 0.13275 | 0.15564 | 0.11444 | 122.4838 | 122.4747 | -0.15106 | -0.11902 | 122.406 | 122.493 | 122.3923 | 122.5067
2328.375 | 122.6669 | -122.4609 | 0.10529 | -0.024948 | 0.01649 | 0.01317 | -0.0020615 | 0.018429 | -0.0012348 | 3.8448e-05 | -0.0043029 | 0.050302 | 0.0067504 | 0.002995 | 0.0016194 | 0.014582 | 0.0023392 | -0.050354 | 0.091553 | -0.073242 | -0.045776 | 0.10071 | 0.009155 | 0.018311 | -0.022888 | 0.07782 | -0.059509 | 0.009155 | 0.10529 | 0.027466 | 0.15106 | 122.3877 | -0.013733 | -0.15106 | 122.5616 | 122.4792 | 122.4701 | 0.091553 | 0.082397 | 122.4014 | -0.027466 | -0.096131 | 122.5662 | 122.612 | 122.4884 | 0.21057 | 0.086975 | 0.17395 | 0.027466 | 0.16479 | 0.068664 | 0.16479 | 0.13733 | 122.5525 | 122.5388 | -0.17853 | -0.16479 | 122.4152 | 122.4701 | 122.4106 | 122.438
2330.0781 | 122.6303 | -122.4335 | 0.11902 | -0.0020601 | 0.017985 | 0.011888 | 0.0028519 | 0.021847 | -0.00059378 | 0.0017474 | -0.0043029 | 0.052865 | 0.0067504 | -0.0098224 | 0.0016194 | 0.012232 | 0.0038346 | -0.073242 | 0.11444 | -0.10529 | -0.091553 | 0.050354 | -0.086975 | -0.032043 | -0.064087 | 0.11444 | -0.068665 | -0.004578 | 0.07782 | -0.045776 | 0.13275 | 122.3282 | -0.004578 | -0.21057 | 122.4838 | 122.4014 | 122.3465 | 0.073243 | 0.018311 | 122.3648 | -0.004578 | -0.1236 | 122.5113 | 122.5662 | 122.3877 | 0.20142 | 0.022889 | 0.15564 | 0.013733 | 0.14649 | 0.064087 | 0.21973 | 0.18311 | 122.5479 | 122.5479 | -0.22431 | -0.18768 | 122.3419 | 122.4289 | 122.3602 | 122.3694
2331.8281 | 122.731 | -122.4197 | 0.11444 | -0.0020601 | 0.015422 | 0.011461 | -0.0029159 | 0.018429 | -0.0025166 | -0.0016706 | -0.0012513 | 0.049661 | 0.0050414 | -0.0074726 | 0.001192 | 0.012659 | 0.0023392 | -0.004578 | 0.086975 | -0.045776 | 0.018311 | 0.21515 | 0.086975 | 0.082397 | 0.10071 | 0.07782 | -0.041199 | 0.091553 | 0.20599 | 0.11444 | 0.19684 | 122.374 | -0.027466 | -0.09613 | 122.6349 | 122.5021 | 122.5067 | 0.12817 | 0.13275 | 122.3785 | -0.036621 | -0.022888 | 122.6257 | 122.6166 | 122.5342 | 0.23804 | 0.15564 | 0.26093 | 0.064087 | 0.24719 | 0.13275 | 0.13275 | 0.11902 | 122.5067 | 122.4976 | -0.16022 | -0.15564 | 122.4381 | 122.5113 | 122.4152 | 122.5204
2333.5156 | 122.6349 | -122.4747 | 0.13275 | -0.017319 | 0.018412 | 0.011034 | 7.473e-05 | 0.021847 | -0.0029438 | 0.0011066 | 0.0048523 | 0.051797 | 0.004187 | -0.0057636 | -8.9634e-05 | 0.011591 | -0.001506 | -0.068665 | 0.11902 | -0.10529 | -0.10529 | 0.032043 | -0.045776 | -0.027466 | -0.082397 | 0.11444 | -0.073242 | -0.022888 | 0.082397 | -0.009155 | 0.1236 | 122.3694 | -0.013732 | -0.23804 | 122.5067 | 122.4472 | 122.4289 | 0.07782 | 0.05951 | 122.4014 | -0.01831 | -0.15564 | 122.5571 | 122.5983 | 122.4655 | 0.19684 | 0.064087 | 0.13733 | 0 | 0.15564 | 0.050354 | 0.22431 | 0.18768 | 122.5937 | 122.5891 | -0.23804 | -0.20599 | 122.3694 | 122.4518 | 122.406 | 122.3923
2335.2812 | 122.7356 | -122.438 | 0.10071 | 0.0055694 | 0.015208 | 0.012743 | -0.0016343 | 0.016507 | -0.0044392 | 0.0013202 | 0.0018005 | 0.049234 | 0.0073914 | 4.214e-06 | 0.00033757 | 0.013514 | -0.000438 | 0.013733 | 0.082397 | -0.068665 | 0.050354 | 0.23346 | 0.10071 | 0.086975 | 0.07782 | 0.073242 | -0.032043 | 0.082397 | 0.20599 | 0.11444 | 0.20599 | 122.3694 | -0.018311 | -0.050354 | 122.6715 | 122.525 | 122.5388 | 0.15564 | 0.16937 | 122.406 | -0.027466 | -0.018311 | 122.644 | 122.644 | 122.5525 | 0.23804 | 0.14648 | 0.30212 | 0.11902 | 0.23804 | 0.11444 | 0.15106 | 0.10529 | 122.5204 | 122.5113 | -0.16937 | -0.13275 | 122.4884 | 122.5204 | 122.4518 | 122.5159
2336.9688 | 122.6028 | -122.4792 | 0.11902 | -0.0020601 | 0.017131 | 0.010606 | -0.0029159 | 0.023343 | -0.0029438 | 3.8448e-05 | -0.010406 | 0.049447 | 0.0071776 | -0.0078998 | -0.0013714 | 0.011591 | -0.0002244 | -0.086975 | 0.11444 | -0.1236 | -0.11902 | 0.045776 | -0.054932 | -0.041199 | -0.10986 | 0.11444 | -0.07782 | -0.054932 | 0.045776 | -0.045776 | 0.091553 | 122.3557 | -0.004578 | -0.23804 | 122.525 | 122.438 | 122.4243 | 0.082397 | 0.068664 | 122.4014 | -0.004578 | -0.17395 | 122.525 | 122.5708 | 122.4335 | 0.16937 | 0.032044 | 0.16937 | 0.004577 | 0.1236 | 0.022888 | 0.23804 | 0.19226 | 122.5937 | 122.5937 | -0.24261 | -0.19684 | 122.3602 | 122.4243 | 122.3923 | 122.3694
2338.7188 | 122.6578 | -122.4426 | 0.10986 | -0.0096891 | 0.018199 | 0.01317 | -0.00099327 | 0.020566 | -0.0025166 | -0.0018842 | -0.0043029 | 0.050516 | 0.0088866 | -0.0046954 | 0.0026874 | 0.0133 | 0.0006302 | -0.032043 | 0.09613 | -0.10071 | -0.050354 | 0.10986 | -0.009155 | -0.004578 | -0.004578 | 0.10071 | -0.059509 | 0.032043 | 0.11902 | 0.013733 | 0.13733 | 122.3419 | -0.013733 | -0.16022 | 122.5525 | 122.438 | 122.4335 | 0.09613 | 0.091553 | 122.3831 | -0.009155 | -0.07782 | 122.5616 | 122.58 | 122.4564 | 0.19684 | 0.073242 | 0.21057 | 0.050354 | 0.17853 | 0.091552 | 0.19684 | 0.16022 | 122.5388 | 122.5433 | -0.21057 | -0.16937 | 122.3923 | 122.4747 | 122.4106 | 122.438
2340.4844 | 122.6486 | -122.438 | 0.10529 | 0.0055694 | 0.018412 | 0.01317 | -0.00056607 | 0.025692 | -0.0018756 | -0.00038875 | 0.0048523 | 0.053506 | 0.0080322 | -0.0023456 | 0.0048236 | 0.015223 | 0.0034072 | -0.086975 | 0.11444 | -0.091553 | -0.10529 | 0.050354 | -0.082397 | -0.045776 | -0.054932 | 0.12817 | -0.082397 | 0.009155 | 0.054932 | -0.027466 | 0.1236 | 122.3465 | 0.009155 | -0.21057 | 122.4884 | 122.3923 | 122.3557 | 0.045777 | 0.009156 | 122.3557 | 0.022888 | -0.096131 | 122.493 | 122.5616 | 122.4106 | 0.20599 | 0.054931 | 0.14191 | -0.013733 | 0.13733 | 0.091552 | 0.20599 | 0.21057 | 122.5525 | 122.5662 | -0.19684 | -0.18768 | 122.3328 | 122.4472 | 122.3511 | 122.3831
2342.25 | 122.699 | -122.4472 | 0.10071 | -0.0096891 | 0.015849 | 0.012956 | -0.0035569 | 0.023129 | -0.0027302 | 0.0030292 | -0.0012513 | 0.051584 | 0.008673 | -0.00042299 | 0.001833 | 0.016932 | -0.002147 | -0.059509 | 0.07782 | -0.054932 | -0.036621 | 0.14648 | -0.009155 | 0.036621 | -0.022888 | 0.086975 | -0.059509 | 0.045776 | 0.1236 | 0.032043 | 0.15564 | 122.3923 | -0.022888 | -0.13733 | 122.5937 | 122.4838 | 122.438 | 0.091553 | 0.045777 | 122.3877 | -0.013733 | -0.054932 | 122.5708 | 122.6028 | 122.4792 | 0.21515 | 0.091552 | 0.20142 | 0.018311 | 0.1831 | 0.10528 | 0.13275 | 0.14648 | 122.525 | 122.5342 | -0.15564 | -0.16022 | 122.4106 | 122.493 | 122.3877 | 122.4243
2343.9375 | 122.7081 | -122.4655 | 0.082397 | -0.0096891 | 0.017985 | 0.010606 | -0.0022751 | 0.022275 | -0.00080758 | -0.0012434 | -0.0043029 | 0.048593 | 0.0063232 | 0.00021781 | 0.00012397 | 0.01565 | 0.0004166 | -0.064087 | 0.091553 | -0.064087 | -0.050354 | 0.10986 | -0.013733 | 0.013733 | -0.045776 | 0.082397 | -0.073242 | 0.022888 | 0.11902 | 0.022888 | 0.15106 | 122.4014 | 0.009156 | -0.13275 | 122.5754 | 122.4792 | 122.4518 | 0.07782 | 0.050354 | 122.3923 | 0 | -0.059509 | 122.5845 | 122.6166 | 122.4884 | 0.2243 | 0.09613 | 0.17395 | 0.013733 | 0.19226 | 0.09613 | 0.15564 | 0.15564 | 122.5571 | 122.5479 | -0.14648 | -0.15564 | 122.4152 | 122.4884 | 122.4014 | 122.4197
2345.7031 | 122.6028 | -122.4747 | 0.14648 | -0.0096891 | 0.017985 | 0.011675 | -0.0016343 | 0.019497 | -0.0031574 | 0.0015338 | -0.0012513 | 0.053079 | 0.0080322 | -0.0091816 | -0.002226 | 0.012873 | 0.0031936 | -0.064087 | 0.09613 | -0.09613 | -0.086975 | 0.068665 | -0.032043 | -0.013733 | -0.073242 | 0.12817 | -0.086975 | -0.036621 | 0.050354 | -0.041199 | 0.07782 | 122.3785 | -0.050354 | -0.23346 | 122.5433 | 122.4609 | 122.4426 | 0.082397 | 0.064087 | 122.3877 | -0.01831 | -0.18311 | 122.525 | 122.5525 | 122.4335 | 0.16479 | 0.045776 | 0.16479 | 0.009155 | 0.13733 | 0.050354 | 0.19226 | 0.21515 | 122.5708 | 122.6028 | -0.24261 | -0.23346 | 122.3877 | 122.438 | 122.4106 | 122.4014
2347.3906 | 122.6578 | -122.4609 | 0.14191 | -0.0020601 | 0.01884 | 0.011675 | -0.0018479 | 0.022915 | -0.00080758 | -0.00017515 | -0.0043029 | 0.051797 | 0.0095276 | -0.008968 | 0.0014056 | 0.013941 | -0.002147 | -0.041199 | 0.11902 | -0.091553 | -0.041199 | 0.09613 | -0.022888 | -0.004578 | -0.018311 | 0.10986 | -0.059509 | 0.022888 | 0.11902 | 0.004578 | 0.14648 | 122.3694 | -0.022888 | -0.18311 | 122.5571 | 122.4564 | 122.438 | 0.086975 | 0.068665 | 122.4014 | -0.032044 | -0.11902 | 122.58 | 122.6074 | 122.4655 | 0.20599 | 0.064087 | 0.18768 | 0.050354 | 0.17853 | 0.082397 | 0.21057 | 0.16937 | 122.58 | 122.5708 | -0.23346 | -0.20142 | 122.4197 | 122.4838 | 122.4197 | 122.4426
2349.0938 | 122.7356 | -122.4152 | 0.09613 | -0.0020601 | 0.016703 | 0.0093246 | -0.0012069 | 0.02377 | -0.0018756 | -0.00038875 | -0.0012513 | 0.049447 | 0.0097412 | 0.002995 | 0.0026874 | 0.014155 | 0.000203 | -0.022888 | 0.064087 | -0.054932 | 0.032043 | 0.21515 | 0.086975 | 0.09613 | 0.073242 | 0.059509 | -0.045776 | 0.068665 | 0.21057 | 0.09613 | 0.19684 | 122.3602 | -0.032043 | -0.064087 | 122.6303 | 122.5113 | 122.5021 | 0.15106 | 0.14191 | 122.3694 | -0.036621 | -0.027465 | 122.6257 | 122.612 | 122.5113 | 0.24261 | 0.14191 | 0.27008 | 0.086975 | 0.25635 | 0.11444 | 0.11902 | 0.10528 | 122.4792 | 122.4747 | -0.15106 | -0.14191 | 122.4472 | 122.4838 | 122.3923 | 122.4884
2350.8594 | 122.6349 | -122.4564 | 0.14648 | -0.0020601 | 0.017558 | 0.011034 | -0.0020615 | 0.019497 | -0.0027302 | -0.0018842 | -0.0073547 | 0.053293 | 0.0095276 | -0.006618 | 0.0033282 | 0.012659 | -0.0027878 | -0.086975 | 0.10529 | -0.11902 | -0.11902 | 0.041199 | -0.050354 | -0.032043 | -0.086975 | 0.10071 | -0.068665 | -0.036621 | 0.059509 | -0.022888 | 0.10071 | 122.3373 | -0.041198 | -0.2655 | 122.4976 | 122.4243 | 122.406 | 0.086976 | 0.068665 | 122.3877 | -0.045776 | -0.18311 | 122.5159 | 122.5571 | 122.4335 | 0.16937 | 0.045777 | 0.16022 | 0 | 0.12817 | 0.032044 | 0.22431 | 0.16937 | 122.5616 | 122.5571 | -0.2655 | -0.21515 | 122.3373 | 122.4197 | 122.3694 | 122.3694
2352.625 | 122.7356 | -122.4701 | 0.10529 | -0.017319 | 0.018412 | 0.010179 | -0.0035569 | 0.018643 | -0.00016658 | 0.0011066 | -0.0043029 | 0.048166 | 0.0063232 | -0.0014912 | 0.0033282 | 0.014155 | -0.000438 | -0.059509 | 0.086975 | -0.07782 | -0.041199 | 0.11444 | 0.004578 | 0.036621 | -0.004578 | 0.082397 | -0.050354 | 0.050354 | 0.14191 | 0.050354 | 0.16022 | 122.3923 | -0.018311 | -0.14649 | 122.5845 | 122.5067 | 122.4747 | 0.11444 | 0.082398 | 122.4197 | -0.022889 | -0.054932 | 122.612 | 122.6303 | 122.5204 | 0.21057 | 0.10071 | 0.19226 | 0.036621 | 0.19226 | 0.10071 | 0.16479 | 0.13275 | 122.5571 | 122.5525 | -0.18311 | -0.15564 | 122.4289 | 122.5204 | 122.4106 | 122.4655
2354.3281 | 122.6395 | -122.4701 | 0.10529 | 0.0055694 | 0.019053 | 0.013597 | 0.0024245 | 0.025692 | -0.0020892 | 0.0013202 | 0.0018005 | 0.05372 | 0.0082458 | -0.0070454 | 0.0024738 | 0.016077 | 0.003621 | -0.018311 | 0.11902 | -0.082397 | -0.045776 | 0.07782 | -0.050354 | -0.027466 | -0.036621 | 0.10071 | -0.07782 | -0.032043 | 0.045776 | -0.054932 | 0.091553 | 122.3877 | 0.013733 | -0.15106 | 122.5479 | 122.4426 | 122.4197 | 0.054931 | 0.032043 | 122.3923 | -0.004578 | -0.13733 | 122.5159 | 122.5616 | 122.4152 | 0.16937 | 0.022888 | 0.16022 | 0.036621 | 0.1236 | 0.045777 | 0.20142 | 0.17853 | 122.5891 | 122.5708 | -0.18768 | -0.18311 | 122.4243 | 122.4381 | 122.4518 | 122.4335
2356.0938 | 122.7219 | -122.4792 | 0.091553 | 0.0055694 | 0.016917 | 0.012956 | 0.00050193 | 0.022915 | -0.0029438 | -0.0010298 | -0.0043029 | 0.051156 | 0.0091002 | -0.00555 | 0.0026874 | 0.014368 | 0.00298 | -0.07782 | 0.10529 | -0.09613 | -0.086975 | 0.068665 | -0.054932 | -0.022888 | -0.027466 | 0.10071 | -0.07782 | 0.032043 | 0.091553 | 0.018311 | 0.15564 | 122.3831 | 0.013733 | -0.17853 | 122.5479 | 122.4564 | 122.4243 | 0.073242 | 0.041198 | 122.4014 | 0.009155 | -0.05951 | 122.5708 | 122.6349 | 122.4976 | 0.23346 | 0.096131 | 0.16479 | 0.009155 | 0.16937 | 0.10986 | 0.20142 | 0.17853 | 122.5845 | 122.58 | -0.18768 | -0.16937 | 122.3923 | 122.5113 | 122.4014 | 122.4518
2357.8438 | 122.7402 | -122.4655 | 0.10071 | -0.0020601 | 0.015635 | 0.0095382 | -0.0033433 | 0.018643 | -0.0014484 | -0.00038875 | -0.0012513 | 0.050302 | 0.0080322 | -0.00042299 | 0.001833 | 0.014582 | 0.0027664 | -0.050354 | 0.07782 | -0.086975 | -0.036621 | 0.13275 | 0.018311 | 0.045776 | -0.009155 | 0.086975 | -0.082397 | 0.036621 | 0.14648 | 0.068665 | 0.16022 | 122.3785 | -0.022888 | -0.13733 | 122.5983 | 122.5113 | 122.4838 | 0.13275 | 0.10529 | 122.3831 | -0.013733 | -0.064087 | 122.612 | 122.6257 | 122.5342 | 0.24261 | 0.15106 | 0.21973 | 0.050354 | 0.22888 | 0.11902 | 0.16479 | 0.16937 | 122.5433 | 122.5525 | -0.18768 | -0.18311 | 122.4289 | 122.5021 | 122.4152 | 122.4564
2359.5469 | 122.6532 | -122.4976 | 0.11902 | -0.0020601 | 0.017771 | 0.013384 | -0.00035247 | 0.025265 | 4.7018e-05 | 0.0017474 | -0.0043029 | 0.053934 | 0.009314 | -0.0042682 | 0.002901 | 0.014795 | -0.0030014 | -0.032043 | 0.10986 | -0.082397 | -0.068665 | 0.073242 | -0.041199 | -0.013733 | -0.045776 | 0.10529 | -0.082397 | -0.018311 | 0.045776 | -0.045776 | 0.10071 | 122.4152 | -0.009156 | -0.18768 | 122.5708 | 122.4838 | 122.4564 | 0.068664 | 0.041198 | 122.4152 | -0.013733 | -0.13733 | 122.5433 | 122.5983 | 122.4518 | 0.18311 | 0.036621 | 0.15564 | 0.013732 | 0.12817 | 0.064086 | 0.19226 | 0.18768 | 122.6074 | 122.6028 | -0.20142 | -0.20142 | 122.4289 | 122.4792 | 122.4655 | 122.4518
2361.3125 | 122.7676 | -122.4609 | 0.073242 | 0.0055694 | 0.014994 | 0.011034 | -0.0031297 | 0.022488 | -0.0042254 | 3.8448e-05 | 0.0018005 | 0.04902 | 0.006964 | -0.0012774 | 0.0014056 | 0.013514 | -0.002147 | -0.050354 | 0.07782 | -0.068665 | 0.004578 | 0.17853 | 0.054932 | 0.09613 | 0.059509 | 0.073242 | -0.064087 | 0.07782 | 0.18768 | 0.11444 | 0.17853 | 122.3923 | 0.004578 | -0.068664 | 122.6395 | 122.5571 | 122.5159 | 0.16479 | 0.1236 | 122.3969 | 0 | 0.004578 | 122.6486 | 122.6395 | 122.5754 | 0.24261 | 0.17853 | 0.24719 | 0.073243 | 0.25177 | 0.14191 | 0.14649 | 0.13733 | 122.5388 | 122.5342 | -0.14191 | -0.13733 | 122.4655 | 122.5388 | 122.4106 | 122.5204
2363.0625 | 122.7676 | -122.4792 | 0.091553 | -0.0020601 | 0.016703 | 0.011675 | -0.0018479 | 0.022061 | -0.0055072 | -0.0010298 | 0.0018005 | 0.04902 | 0.005896 | -0.008327 | 0.00097837 | 0.015009 | 0.0010574 | -0.036621 | 0.07782 | -0.068665 | -0.013733 | 0.14191 | 0.045776 | 0.068665 | 0.022888 | 0.073242 | -0.068665 | 0.064087 | 0.17395 | 0.091553 | 0.21057 | 122.4106 | -0.013733 | -0.10529 | 122.6212 | 122.5479 | 122.525 | 0.13733 | 0.11444 | 122.4106 | -0.018311 | -0.027466 | 122.6532 | 122.6898 | 122.5708 | 0.27924 | 0.16022 | 0.21057 | 0.054932 | 0.24261 | 0.13275 | 0.14649 | 0.14191 | 122.5571 | 122.5525 | -0.16022 | -0.16022 | 122.4655 | 122.5433 | 122.4426 | 122.5021
2364.8281 | 122.6532 | -122.5067 | 0.12817 | -0.017319 | 0.017344 | 0.009111 | -0.00056607 | 0.024411 | -0.0035846 | -0.001457 | -0.0012513 | 0.052438 | 0.0071776 | -0.008968 | 0.001192 | 0.012873 | 0.0021256 | -0.091553 | 0.11444 | -0.10529 | -0.10986 | 0.022888 | -0.050354 | -0.032043 | -0.11902 | 0.091553 | -0.068665 | -0.041199 | 0.045776 | -0.045776 | 0.10071 | 122.4014 | -0.013733 | -0.23804 | 122.5296 | 122.4747 | 122.4564 | 0.073243 | 0.054932 | 122.438 | -0.036621 | -0.16937 | 122.5525 | 122.6074 | 122.4609 | 0.16937 | 0.022889 | 0.12817 | -0.004577 | 0.11444 | 0.027466 | 0.21973 | 0.16022 | 122.6212 | 122.5983 | -0.23346 | -0.19684 | 122.3969 | 122.4655 | 122.4152 | 122.3877
2366.5312 | 122.644 | -122.5204 | 0.13275 | 0.0055694 | 0.020121 | 0.012315 | -0.00013887 | 0.022702 | -0.0027302 | -0.00017515 | -0.0043029 | 0.052011 | 0.0056824 | -0.0074726 | 0.0024738 | 0.015009 | 0.000203 | -0.073242 | 0.13275 | -0.082397 | -0.11902 | 0 | -0.11444 | -0.054932 | -0.10529 | 0.11444 | -0.10529 | -0.032043 | 0.018311 | -0.064087 | 0.091553 | 122.4381 | 0 | -0.25177 | 122.5204 | 122.4655 | 122.406 | 0.027465 | -0.032044 | 122.4152 | -0.01831 | -0.16479 | 122.5388 | 122.612 | 122.4564 | 0.19684 | 0.041199 | 0.082397 | -0.036622 | 0.1236 | 0.073243 | 0.21515 | 0.21973 | 122.6532 | 122.6349 | -0.21515 | -0.23804 | 122.4014 | 122.4884 | 122.4472 | 122.4152
2368.3125 | 122.644 | -122.5296 | 0.13733 | 0.0055694 | 0.017131 | 0.012743 | -0.00099327 | 0.026333 | -0.003371 | 0.0021746 | -0.0012513 | 0.050516 | 0.011023 | -0.00555 | -0.00051703 | 0.01095 | 0.001271 | -0.064087 | 0.10529 | -0.086975 | -0.082397 | 0.082397 | -0.032043 | -0.013733 | -0.07782 | 0.10529 | -0.09613 | -0.036621 | 0.050354 | -0.045776 | 0.082397 | 122.4426 | -0.032043 | -0.21973 | 122.612 | 122.5159 | 122.4976 | 0.073242 | 0.054932 | 122.4335 | -0.032043 | -0.17395 | 122.58 | 122.612 | 122.4838 | 0.17853 | 0.050354 | 0.16937 | 0.004578 | 0.14648 | 0.059509 | 0.19226 | 0.20142 | 122.6349 | 122.6349 | -0.2243 | -0.23346 | 122.4472 | 122.493 | 122.4655 | 122.4518
2370.0156 | 122.7768 | -122.5113 | 0.09613 | -0.0020601 | 0.014781 | 0.011675 | -0.0035569 | 0.023984 | -0.00059378 | 0.0011066 | 0.0018005 | 0.050516 | 0.006964 | -0.0027728 | 0.00012397 | 0.013727 | 0.0014846 | -0.036621 | 0.082397 | -0.07782 | -0.013733 | 0.16479 | 0.073242 | 0.07782 | 0.041199 | 0.064087 | -0.045776 | 0.073242 | 0.19226 | 0.10529 | 0.19226 | 122.4335 | -0.013733 | -0.10986 | 122.6761 | 122.5891 | 122.5845 | 0.15564 | 0.15106 | 122.4655 | -0.032043 | -0.022888 | 122.7036 | 122.7036 | 122.6166 | 0.23804 | 0.15106 | 0.24261 | 0.064087 | 0.23804 | 0.11902 | 0.16022 | 0.10986 | 122.5937 | 122.5754 | -0.17395 | -0.14191 | 122.4976 | 122.5845 | 122.4747 | 122.5525
2371.7656 | 122.6624 | -122.5067 | 0.13275 | -0.0096891 | 0.015635 | 0.0099656 | 7.473e-05 | 0.022915 | -0.0040118 | -0.00081595 | 0.0018005 | 0.051584 | 0.0088866 | -0.0014912 | 0.0020466 | 0.010523 | 0.0053298 | -0.045776 | 0.10529 | -0.091553 | -0.07782 | 0.09613 | -0.032043 | 0 | -0.082397 | 0.10529 | -0.068665 | -0.041199 | 0.064087 | -0.022888 | 0.07782 | 122.4152 | -0.027465 | -0.21057 | 122.6028 | 122.5067 | 122.4747 | 0.091553 | 0.05951 | 122.438 | -0.027465 | -0.17395 | 122.5708 | 122.5845 | 122.4838 | 0.14649 | 0.045777 | 0.18768 | 0.013733 | 0.13275 | 0.027466 | 0.19684 | 0.17395 | 122.612 | 122.612 | -0.2243 | -0.20142 | 122.4289 | 122.4655 | 122.4609 | 122.4243
2373.5156 | 122.6532 | -122.5067 | 0.12817 | 0.013199 | 0.015849 | 0.013384 | -0.0018479 | 0.020352 | -0.0037982 | -0.0016706 | 0.0048523 | 0.049875 | 0.0084594 | -0.010463 | -0.0024396 | 0.012232 | -0.002147 | -0.09613 | 0.10986 | -0.11444 | -0.10071 | 0.054932 | -0.041199 | -0.013733 | -0.10071 | 0.10529 | -0.10071 | -0.050354 | 0.041199 | -0.032043 | 0.086975 | 122.3923 | -0.018311 | -0.22888 | 122.5616 | 122.493 | 122.4655 | 0.10071 | 0.073242 | 122.406 | -0.022888 | -0.17853 | 122.5479 | 122.5937 | 122.4747 | 0.18768 | 0.068665 | 0.16937 | 0.013733 | 0.14191 | 0.050354 | 0.2243 | 0.20599 | 122.6166 | 122.612 | -0.24262 | -0.22888 | 122.406 | 122.4564 | 122.4106 | 122.406
2375.2188 | 122.7539 | -122.5021 | 0.11444 | 0.0055694 | 0.015849 | 0.009111 | 7.473e-05 | 0.021634 | -0.0020892 | 0.00046565 | -0.0012513 | 0.049875 | 0.006964 | 0.0034222 | 0.0037556 | 0.0133 | 0.0004166 | -0.059509 | 0.086975 | -0.07782 | -0.041199 | 0.11902 | 0.009155 | 0.045776 | -0.018311 | 0.082397 | -0.073242 | 0.036621 | 0.14191 | 0.082397 | 0.16937 | 122.4243 | -0.027466 | -0.15564 | 122.6212 | 122.5479 | 122.5113 | 0.1236 | 0.086975 | 122.4289 | -0.032044 | -0.07782 | 122.644 | 122.6715 | 122.5845 | 0.24261 | 0.15564 | 0.19684 | 0.036621 | 0.21515 | 0.10986 | 0.16479 | 0.15564 | 122.5891 | 122.5845 | -0.19226 | -0.18768 | 122.4609 | 122.5388 | 122.4426 | 122.4838
2376.9688 | 122.7859 | -122.4747 | 0.09613 | -0.0020601 | 0.016703 | 0.011034 | -0.0031297 | 0.020566 | -0.0029438 | -0.00081595 | -0.0012513 | 0.049234 | 0.0071776 | 0.00085881 | 0.0022602 | 0.012659 | 0.0004166 | -0.009155 | 0.073242 | -0.068665 | 0.022888 | 0.20142 | 0.068665 | 0.091553 | 0.07782 | 0.07782 | -0.050354 | 0.07782 | 0.19684 | 0.09613 | 0.18768 | 122.406 | -0.022888 | -0.073242 | 122.6761 | 122.5662 | 122.5433 | 0.16022 | 0.13733 | 122.4243 | -0.01831 | -0.01831 | 122.6715 | 122.6624 | 122.5708 | 0.23804 | 0.14648 | 0.27008 | 0.091553 | 0.24719 | 0.12817 | 0.14191 | 0.12817 | 122.5479 | 122.5525 | -0.16479 | -0.14648 | 122.4976 | 122.5525 | 122.4655 | 122.5525
2378.6562 | 122.6669 | -122.5525 | 0.12817 | 0.013199 | 0.020335 | 0.01082 | -0.0029159 | 0.020138 | -0.0020892 | -0.00060235 | 0.0018005 | 0.050302 | 0.008673 | -0.011745 | -0.0013714 | 0.012232 | 0.0010574 | -0.073242 | 0.11902 | -0.10071 | -0.10986 | 0.045776 | -0.045776 | -0.022888 | -0.09613 | 0.10986 | -0.082397 | -0.054932 | 0.036621 | -0.045776 | 0.082397 | 122.4518 | -0.009155 | -0.23804 | 122.5983 | 122.5296 | 122.5067 | 0.07782 | 0.054932 | 122.4701 | -0.018311 | -0.18311 | 122.5891 | 122.6349 | 122.5067 | 0.16479 | 0.036621 | 0.14648 | -0.009155 | 0.11902 | 0.027465 | 0.21973 | 0.19226 | 122.6715 | 122.6624 | -0.22888 | -0.21057 | 122.4426 | 122.4976 | 122.4792 | 122.4564
2380.4062 | 122.731 | -122.5159 | 0.10071 | -0.0020601 | 0.015422 | 0.010606 | -0.00013887 | 0.019711 | -0.0018756 | 0.0026018 | -0.0043029 | 0.053079 | 0.0082458 | -0.011531 | 0.0016194 | 0.013086 | -0.000438 | -0.018311 | 0.11902 | -0.09613 | -0.041199 | 0.10529 | -0.027466 | 0 | -0.013733 | 0.10071 | -0.068665 | 0.022888 | 0.11444 | 0.013733 | 0.13733 | 122.4197 | 0.018311 | -0.14191 | 122.6212 | 122.5159 | 122.4884 | 0.09613 | 0.068664 | 122.4472 | 0 | -0.07782 | 122.6303 | 122.6532 | 122.5296 | 0.20599 | 0.082398 | 0.20142 | 0.054931 | 0.18311 | 0.091553 | 0.21515 | 0.16937 | 122.6349 | 122.6166 | -0.19684 | -0.16937 | 122.4747 | 122.5388 | 122.4976 | 122.5021
2382.1562 | 122.6852 | -122.5067 | 0.13733 | -0.0096891 | 0.019267 | 0.012529 | -0.00077967 | 0.024411 | 0.00047422 | -0.0012434 | 0.0018005 | 0.053506 | 0.0080322 | 0.0014996 | 0.001833 | 0.013727 | 0.0031936 | -0.022888 | 0.10529 | -0.091553 | -0.07782 | 0.091553 | -0.050354 | -0.009155 | -0.041199 | 0.09613 | -0.07782 | -0.009155 | 0.054932 | -0.045776 | 0.10529 | 122.4152 | -0.032043 | -0.21515 | 122.5983 | 122.4976 | 122.4564 | 0.082398 | 0.041199 | 122.4289 | -0.041199 | -0.14648 | 122.5616 | 122.612 | 122.4609 | 0.18311 | 0.032044 | 0.18311 | 0.013733 | 0.13275 | 0.068665 | 0.19684 | 0.17395 | 122.612 | 122.6028 | -0.22888 | -0.21515 | 122.4289 | 122.4976 | 122.4838 | 122.4655
2383.9219 | 122.7768 | -122.5113 | 0.10071 | -0.0096891 | 0.016703 | 0.012102 | -0.0027023 | 0.024624 | -0.003371 | 0.0013202 | -0.0012513 | 0.049875 | 0.0080322 | -0.0036274 | 0.0020466 | 0.015009 | 0.0016982 | 0.004578 | 0.07782 | -0.036621 | 0.013733 | 0.20142 | 0.086975 | 0.091553 | 0.07782 | 0.073242 | -0.064087 | 0.073242 | 0.18768 | 0.091553 | 0.19226 | 122.4747 | -0.022888 | -0.086975 | 122.7127 | 122.6028 | 122.5983 | 0.12817 | 0.1236 | 122.4472 | -0.027466 | -0.027466 | 122.699 | 122.7036 | 122.6028 | 0.25635 | 0.15564 | 0.23804 | 0.050354 | 0.25177 | 0.13733 | 0.11444 | 0.13733 | 122.5891 | 122.5845 | -0.13733 | -0.1648 | 122.525 | 122.5845 | 122.5159 | 122.5891
2385.6094 | 122.7036 | -122.5479 | 0.13275 | -0.017319 | 0.016276 | 0.011034 | -0.0035569 | 0.022702 | -0.0046528 | 0.00025205 | -0.0043029 | 0.050729 | 0.006964 | -0.0023456 | -8.9634e-05 | 0.011805 | 0.0006302 | -0.09613 | 0.10071 | -0.09613 | -0.13275 | 0.022888 | -0.041199 | -0.045776 | -0.10529 | 0.1236 | -0.10529 | -0.045776 | 0.050354 | -0.036621 | 0.10529 | 122.4518 | -0.032043 | -0.2655 | 122.5708 | 122.5021 | 122.5067 | 0.050354 | 0.054931 | 122.4426 | -0.009155 | -0.17853 | 122.5983 | 122.6532 | 122.5113 | 0.21057 | 0.068665 | 0.11902 | -0.036621 | 0.15564 | 0.05951 | 0.19684 | 0.22888 | 122.6486 | 122.6715 | -0.22888 | -0.23804 | 122.4152 | 122.5021 | 122.4518 | 122.4426
2387.4062 | 122.7722 | -122.5067 | 0.10529 | 0.013199 | 0.01884 | 0.0088974 | -0.0012069 | 0.02142 | -0.0031574 | 0.0030292 | -0.0012513 | 0.052225 | 0.0073914 | 0.0055584 | 0.0041828 | 0.014155 | -0.0012924 | -0.064087 | 0.11444 | -0.10529 | -0.082397 | 0.082397 | -0.059509 | -0.027466 | -0.032043 | 0.10071 | -0.07782 | 0.045776 | 0.11902 | 0.018311 | 0.16479 | 122.4014 | 0.009155 | -0.18768 | 122.5891 | 122.4792 | 122.4472 | 0.07782 | 0.045777 | 122.4289 | -0.004578 | -0.05951 | 122.6257 | 122.6715 | 122.525 | 0.24261 | 0.096131 | 0.18768 | 0.022889 | 0.19684 | 0.1236 | 0.21973 | 0.17853 | 122.6212 | 122.6074 | -0.21057 | -0.18311 | 122.4243 | 122.5525 | 122.4426 | 122.4747
2389.1094 | 122.7814 | -122.5113 | 0.10071 | -0.017319 | 0.015422 | 0.010606 | -0.0029159 | 0.019497 | -0.0020892 | 0.0013202 | -0.0012513 | 0.049447 | 0.0084594 | 0.0049176 | 0.0024738 | 0.014155 | 0.0023392 | -0.073242 | 0.091553 | -0.07782 | -0.050354 | 0.1236 | 0.022888 | 0.041199 | -0.032043 | 0.086975 | -0.068665 | 0.045776 | 0.14191 | 0.068665 | 0.17395 | 122.4335 | -0.009155 | -0.15106 | 122.6349 | 122.5525 | 122.5342 | 0.11902 | 0.10071 | 122.4426 | -0.013733 | -0.054932 | 122.6532 | 122.6852 | 122.58 | 0.24261 | 0.13733 | 0.20142 | 0.027466 | 0.21057 | 0.11444 | 0.16937 | 0.15564 | 122.6028 | 122.5983 | -0.17853 | -0.16937 | 122.4609 | 122.5571 | 122.4381 | 122.4792
2390.875 | 122.7676 | -122.5296 | 0.09613 | -0.017319 | 0.017985 | 0.011675 | -0.00077967 | 0.022702 | -0.0014484 | -0.0018842 | -0.0043029 | 0.049875 | 0.006964 | -0.0042682 | 0.0014056 | 0.016077 | 0.0023392 | -0.054932 | 0.068665 | -0.054932 | -0.027466 | 0.15564 | -0.004578 | 0.041199 | -0.004578 | 0.064087 | -0.050354 | 0.036621 | 0.11444 | 0.032043 | 0.15564 | 122.4747 | -0.027465 | -0.1236 | 122.6852 | 122.5708 | 122.525 | 0.096131 | 0.050354 | 122.4792 | -0.032043 | -0.059509 | 122.644 | 122.6852 | 122.5616 | 0.20599 | 0.082397 | 0.21057 | 0.027466 | 0.16479 | 0.086975 | 0.1236 | 0.11444 | 122.5983 | 122.5937 | -0.15106 | -0.14648 | 122.5021 | 122.5662 | 122.4747 | 122.525
2392.6406 | 122.8134 | -122.5204 | 0.10071 | -0.0020601 | 0.017558 | 0.012315 | -0.0024887 | 0.021206 | -0.0020892 | -0.00060235 | -0.0012513 | 0.048807 | 0.0088866 | 4.214e-06 | 0.00012397 | 0.016504 | 0.0025528 | -0.009155 | 0.068665 | -0.050354 | 0.036621 | 0.20142 | 0.073242 | 0.082397 | 0.073242 | 0.059509 | -0.054932 | 0.068665 | 0.18768 | 0.09613 | 0.19226 | 122.4701 | -0.032043 | -0.064087 | 122.7219 | 122.6028 | 122.5937 | 0.13275 | 0.1236 | 122.4655 | -0.041199 | -0.032043 | 122.7081 | 122.7127 | 122.6166 | 0.24719 | 0.15106 | 0.25177 | 0.086975 | 0.24261 | 0.1236 | 0.11902 | 0.11444 | 122.5891 | 122.58 | -0.15106 | -0.15564 | 122.5571 | 122.5891 | 122.5113 | 122.5937
2394.4062 | 122.6578 | -122.5296 | 0.11444 | 0.0055694 | 0.018199 | 0.010393 | -0.00035247 | 0.022061 | -0.0023028 | 0.0026018 | 0.0018005 | 0.051156 | 0.0095276 | -0.0051226 | 0.0024738 | 0.012659 | -0.000438 | -0.064087 | 0.10529 | -0.086975 | -0.10986 | 0.018311 | -0.082397 | -0.064087 | -0.10529 | 0.10529 | -0.10071 | -0.054932 | 0 | -0.10071 | 0.068665 | 122.4426 | -0.009155 | -0.2243 | 122.5479 | 122.4655 | 122.4472 | 0.022888 | 0.004578 | 122.4289 | -0.009155 | -0.16937 | 122.5296 | 122.5983 | 122.4289 | 0.16937 | 0 | 0.10529 | -0.022888 | 0.10071 | 0.045776 | 0.19226 | 0.20599 | 122.6349 | 122.6349 | -0.20142 | -0.21515 | 122.4197 | 122.4747 | 122.4655 | 122.4243
2396.1094 | 122.6898 | -122.5616 | 0.11902 | 0.013199 | 0.018412 | 0.0099656 | -0.00035247 | 0.02142 | -0.0048664 | -0.001457 | -0.0043029 | 0.049875 | 0.010596 | -0.0085406 | 0.00012397 | 0.013941 | -0.002147 | -0.050354 | 0.086975 | -0.091553 | -0.054932 | 0.09613 | -0.022888 | 0.009155 | -0.059509 | 0.10529 | -0.082397 | -0.032043 | 0.050354 | -0.022888 | 0.09613 | 122.4701 | -0.032044 | -0.17395 | 122.6578 | 122.5708 | 122.5388 | 0.10071 | 0.068665 | 122.4792 | -0.013733 | -0.15106 | 122.612 | 122.6578 | 122.5388 | 0.17853 | 0.059509 | 0.18768 | 0.036621 | 0.13275 | 0.050354 | 0.17853 | 0.18768 | 122.6486 | 122.6669 | -0.21057 | -0.20142 | 122.5067 | 122.5296 | 122.5113 | 122.5021
2397.875 | 122.7859 | -122.5159 | 0.10529 | -0.0020601 | 0.017558 | 0.010606 | -0.0016343 | 0.023556 | -0.00059378 | 0.0011066 | -0.0012513 | 0.053293 | 0.010168 | -0.0051226 | 0.0065326 | 0.016504 | -0.0006516 | -0.064087 | 0.10986 | -0.10529 | -0.059509 | 0.082397 | -0.054932 | -0.009155 | -0.009155 | 0.086975 | -0.082397 | 0.045776 | 0.1236 | 0.032043 | 0.17395 | 122.4106 | 0.004577 | -0.16479 | 122.5983 | 122.5067 | 122.4609 | 0.096131 | 0.050354 | 122.4335 | -0.018311 | -0.05951 | 122.6395 | 122.6898 | 122.5479 | 0.25635 | 0.11444 | 0.18768 | 0.045777 | 0.20599 | 0.12817 | 0.21515 | 0.16937 | 122.6257 | 122.6028 | -0.21057 | -0.18768 | 122.4564 | 122.5616 | 122.4518 | 122.5067
2399.5781 | 122.7356 | -122.5388 | 0.11444 | -0.0020601 | 0.01649 | 0.010606 | 0.00050193 | 0.020352 | -0.0014484 | -0.003166 | -0.0043029 | 0.049875 | 0.0099548 | -0.007259 | 0.0014056 | 0.015009 | -1.0598e-05 | -0.036621 | 0.10529 | -0.10071 | -0.059509 | 0.10529 | -0.009155 | 0.004578 | -0.027466 | 0.10071 | -0.073242 | 0.013733 | 0.10071 | 0 | 0.13733 | 122.438 | -0.009155 | -0.17395 | 122.644 | 122.5433 | 122.5296 | 0.10529 | 0.091553 | 122.4655 | -0.013733 | -0.10071 | 122.6395 | 122.6761 | 122.5388 | 0.21057 | 0.073242 | 0.20599 | 0.041199 | 0.17395 | 0.086975 | 0.20599 | 0.17395 | 122.644 | 122.6395 | -0.21515 | -0.18768 | 122.4792 | 122.5525 | 122.5021 | 122.5113
2401.3438 | 122.8226 | -122.5067 | 0.091553 | -0.0020601 | 0.017131 | 0.012743 | -0.0022751 | 0.024197 | -0.0020892 | -0.00017515 | -0.0012513 | 0.050088 | 0.008673 | 0.002995 | 0.0054646 | 0.014155 | -1.0598e-05 | -0.004578 | 0.073242 | -0.068665 | 0 | 0.1831 | 0.041199 | 0.059509 | 0.054932 | 0.059509 | -0.045776 | 0.10071 | 0.16479 | 0.07782 | 0.20599 | 122.438 | -0.018311 | -0.091553 | 122.6898 | 122.5662 | 122.5479 | 0.12817 | 0.10986 | 122.4609 | -0.032044 | 0.009155 | 122.6715 | 122.7127 | 122.5845 | 0.25177 | 0.1236 | 0.25177 | 0.068665 | 0.21057 | 0.14648 | 0.14191 | 0.10528 | 122.58 | 122.5662 | -0.16022 | -0.13733 | 122.5067 | 122.6074 | 122.5021 | 122.5616
2403.0938 | 122.7997 | -122.5296 | 0.10071 | -0.0096891 | 0.017558 | 0.011247 | -0.0031297 | 0.020138 | -0.0052936 | 0.00046565 | -0.0012513 | 0.048807 | 0.0082458 | -0.004909 | -0.00030343 | 0.015436 | 0.00298 | -0.068665 | 0.082397 | -0.073242 | -0.041199 | 0.1236 | 0.013733 | 0.045776 | -0.013733 | 0.059509 | -0.073242 | 0.036621 | 0.14648 | 0.054932 | 0.17395 | 122.4564 | -0.018311 | -0.14191 | 122.6532 | 122.5754 | 122.5433 | 0.11902 | 0.086975 | 122.4564 | -0.041199 | -0.064087 | 122.6761 | 122.7036 | 122.5845 | 0.24719 | 0.12817 | 0.19684 | 0.032043 | 0.21973 | 0.10986 | 0.15564 | 0.13275 | 122.612 | 122.5891 | -0.17395 | -0.17395 | 122.4884 | 122.5662 | 122.4609 | 122.5159
2404.9531 | 122.7539 | -122.5616 | 0.11902 | -0.0096891 | 0.017985 | 0.01082 | 0.00050193 | 0.024838 | -0.0012348 | 0.00067925 | -0.0043029 | 0.052225 | 0.0084594 | -0.0087542 | 0.00076477 | 0.013941 | -0.0008652 | -0.045776 | 0.10071 | -0.082397 | -0.082397 | 0.086975 | -0.032043 | -0.004578 | -0.036621 | 0.09613 | -0.059509 | -0.009155 | 0.07782 | -0.018311 | 0.13733 | 122.4792 | -0.018311 | -0.20142 | 122.6486 | 122.5571 | 122.5296 | 0.077819 | 0.050354 | 122.5021 | -0.022889 | -0.12817 | 122.6395 | 122.699 | 122.5433 | 0.19684 | 0.041198 | 0.16937 | 0 | 0.13733 | 0.050354 | 0.18311 | 0.15564 | 122.6624 | 122.6578 | -0.20142 | -0.17853 | 122.4792 | 122.5525 | 122.5159 | 122.525
2407.1719 | 122.8134 | -122.525 | 0.091553 | 0.013199 | 0.016917 | 0.012956 | -0.0022751 | 0.024411 | -0.0014484 | 0.0011066 | 0.0048523 | 0.050943 | 0.007605 | -0.0023456 | 0.0039692 | 0.014795 | -0.0017196 | -0.054932 | 0.11902 | -0.07782 | -0.013733 | 0.13275 | 0.009155 | 0.027466 | 0.041199 | 0.07782 | -0.059509 | 0.07782 | 0.15106 | 0.059509 | 0.20599 | 122.4472 | 0.027466 | -0.10529 | 122.6578 | 122.5525 | 122.5342 | 0.10529 | 0.086975 | 122.4655 | -0.013733 | -0.013733 | 122.6761 | 122.731 | 122.5845 | 0.2655 | 0.11902 | 0.21057 | 0.064087 | 0.21057 | 0.13733 | 0.19684 | 0.13733 | 122.644 | 122.6028 | -0.16937 | -0.15106 | 122.5113 | 122.6028 | 122.4701 | 122.5662
2409.8125 | 122.8592 | -122.5067 | 0.11444 | -0.0020601 | 0.013926 | 0.013384 | -0.0039841 | 0.022488 | -0.0035846 | -0.00017515 | -0.0012513 | 0.047738 | 0.0067504 | -0.00555 | 0.00076477 | 0.013727 | 0.0014846 | -0.022888 | 0.091553 | -0.059509 | 0.036621 | 0.21973 | 0.091553 | 0.10986 | 0.10986 | 0.068665 | -0.054932 | 0.064087 | 0.20142 | 0.10986 | 0.18768 | 122.4472 | -0.022888 | -0.07782 | 122.7264 | 122.6166 | 122.5983 | 0.16937 | 0.15106 | 122.4518 | -0.045776 | -0.050354 | 122.7081 | 122.6944 | 122.6166 | 0.24261 | 0.16479 | 0.27924 | 0.09613 | 0.25635 | 0.11902 | 0.15106 | 0.1236 | 122.5983 | 122.5754 | -0.17395 | -0.16937 | 122.5433 | 122.5708 | 122.4838 | 122.6166
2412.8906 | 122.7585 | -122.5662 | 0.11444 | 0.0055694 | 0.017985 | 0.011034 | -0.0016343 | 0.023984 | -0.0046528 | 0.0013202 | -0.0043029 | 0.049875 | 0.0091002 | -0.0068316 | 0.00076477 | 0.014795 | 0.0004166 | -0.013733 | 0.086975 | -0.07782 | -0.027466 | 0.086975 | 0.004578 | 0.013733 | -0.004578 | 0.10071 | -0.073242 | 0.013733 | 0.09613 | 0 | 0.14648 | 122.4884 | -0.027466 | -0.14191 | 122.6532 | 122.58 | 122.5708 | 0.091553 | 0.082398 | 122.493 | -0.013733 | -0.10071 | 122.6624 | 122.7127 | 122.5662 | 0.21973 | 0.073242 | 0.16479 | 0.050354 | 0.16937 | 0.086975 | 0.16479 | 0.17395 | 122.6532 | 122.6669 | -0.19226 | -0.18768 | 122.5388 | 122.58 | 122.5525 | 122.5616
2414.6875 | 122.7173 | -122.5708 | 0.13275 | 0.0055694 | 0.016703 | 0.011675 | 0.00028833 | 0.023984 | -0.0014484 | -0.0016706 | -0.0012513 | 0.052225 | 0.01145 | -0.0093952 | 0.002901 | 0.013727 | 0.0010574 | -0.07782 | 0.11444 | -0.11444 | -0.10071 | 0.022888 | -0.086975 | -0.041199 | -0.10986 | 0.091553 | -0.10529 | -0.045776 | 0.018311 | -0.068665 | 0.091553 | 122.4564 | -0.01831 | -0.23346 | 122.5937 | 122.5296 | 122.4838 | 0.073242 | 0.027466 | 122.4655 | -0.041198 | -0.17853 | 122.5891 | 122.6624 | 122.5021 | 0.19684 | 0.036621 | 0.13733 | 0.013733 | 0.1236 | 0.05951 | 0.22888 | 0.19684 | 122.6852 | 122.6624 | -0.24719 | -0.23804 | 122.4701 | 122.525 | 122.493 | 122.4609
2416.4844 | 122.731 | -122.5708 | 0.11902 | 0.0055694 | 0.020548 | 0.011461 | -0.0016343 | 0.025906 | -0.0040118 | -0.00060235 | -0.0012513 | 0.052225 | 0.0078186 | -0.01025 | 0.0024738 | 0.012018 | 0.001271 | -0.073242 | 0.10529 | -0.091553 | -0.10529 | 0.036621 | -0.09613 | -0.032043 | -0.10071 | 0.10071 | -0.073242 | -0.022888 | 0.027466 | -0.054932 | 0.10986 | 122.4792 | -0.013733 | -0.22431 | 122.6074 | 122.5388 | 122.4747 | 0.05951 | -0.004577 | 122.4976 | -0.018311 | -0.14191 | 122.5983 | 122.6807 | 122.5159 | 0.18311 | 0.01831 | 0.12817 | -0.013733 | 0.10071 | 0.050354 | 0.19684 | 0.17395 | 122.6761 | 122.6715 | -0.21057 | -0.19226 | 122.4655 | 122.5479 | 122.4976 | 122.4701
2418.25 | 122.7676 | -122.5571 | 0.11902 | -0.017319 | 0.018199 | 0.011675 | -0.0012069 | 0.02377 | -0.0023028 | 0.00046565 | -0.0073547 | 0.052225 | 0.0084594 | -0.0036274 | 0.00076477 | 0.014795 | 0.003621 | -0.07782 | 0.091553 | -0.10071 | -0.082397 | 0.086975 | -0.018311 | -0.013733 | -0.064087 | 0.10529 | -0.07782 | 0.009155 | 0.082397 | -0.009155 | 0.12817 | 122.4564 | -0.027466 | -0.20142 | 122.644 | 122.5433 | 122.5388 | 0.086975 | 0.082397 | 122.4792 | -0.013733 | -0.10986 | 122.6395 | 122.6852 | 122.5479 | 0.20599 | 0.068665 | 0.18768 | 0.018311 | 0.16022 | 0.086975 | 0.19226 | 0.18311 | 122.6486 | 122.6624 | -0.21973 | -0.19684 | 122.4747 | 122.5662 | 122.4792 | 122.493
2420.0312 | 122.7036 | -122.5708 | 0.13275 | 0.0055694 | 0.019908 | 0.013384 | 0.00092933 | 0.024838 | -0.00080758 | 0.0030292 | 0.0048523 | 0.05137 | 0.0084594 | -0.0046954 | 0.001833 | 0.013727 | -0.003856 | -0.054932 | 0.091553 | -0.10529 | -0.09613 | 0.036621 | -0.082397 | -0.036621 | -0.086975 | 0.09613 | -0.068665 | -0.032043 | 0.027466 | -0.059509 | 0.068665 | 122.4655 | -0.041198 | -0.22888 | 122.6074 | 122.5342 | 122.4884 | 0.068665 | 0.022889 | 122.5021 | -0.036621 | -0.16479 | 122.5983 | 122.6395 | 122.5113 | 0.13733 | 0.009156 | 0.14191 | 0.009156 | 0.096131 | 0.036622 | 0.19684 | 0.16479 | 122.6624 | 122.6669 | -0.23804 | -0.20142 | 122.4747 | 122.5388 | 122.5159 | 122.4838
2421.7188 | 122.699 | -122.5845 | 0.12817 | -0.0020601 | 0.020976 | 0.012315 | -0.0014207 | 0.024197 | -0.00016658 | 0.0021746 | -0.0043029 | 0.050516 | 0.0071776 | -0.002132 | 0.00097837 | 0.017359 | 0.003621 | -0.073242 | 0.11444 | -0.10071 | -0.11902 | 0.032043 | -0.086975 | -0.050354 | -0.13733 | 0.10986 | -0.082397 | -0.045776 | 0.004578 | -0.082397 | 0.086975 | 122.4838 | -0.013733 | -0.24719 | 122.6166 | 122.5342 | 122.4976 | 0.050354 | 0.013733 | 122.5021 | -0.018311 | -0.17395 | 122.5891 | 122.6715 | 122.5021 | 0.16937 | 0 | 0.13275 | -0.018311 | 0.086975 | 0.036621 | 0.21515 | 0.19226 | 122.699 | 122.6944 | -0.22888 | -0.21057 | 122.4655 | 122.5388 | 122.5113 | 122.4472
2423.4688 | 122.731 | -122.5845 | 0.12817 | -0.0020601 | 0.017558 | 0.009752 | -0.0029159 | 0.020993 | -0.0031574 | -0.00017515 | 0.0018005 | 0.049875 | 0.0061096 | -0.0053364 | -0.00073063 | 0.013727 | -0.0002244 | -0.036621 | 0.086975 | -0.073242 | -0.041199 | 0.13275 | 0.022888 | 0.022888 | -0.041199 | 0.091553 | -0.068665 | -0.032043 | 0.068665 | -0.013733 | 0.091553 | 122.5113 | -0.041199 | -0.16937 | 122.7173 | 122.6074 | 122.6074 | 0.09613 | 0.09613 | 122.5159 | -0.036621 | -0.16022 | 122.6532 | 122.6761 | 122.5708 | 0.16022 | 0.054932 | 0.20599 | 0.032043 | 0.13733 | 0.036622 | 0.16022 | 0.16022 | 122.6715 | 122.6761 | -0.20142 | -0.19684 | 122.5433 | 122.5525 | 122.5479 | 122.5433
2425.25 | 122.8592 | -122.5433 | 0.086975 | -0.0096891 | 0.020121 | 0.011034 | -0.0044113 | 0.023129 | -0.001662 | 0.0013202 | -0.0012513 | 0.050088 | 0.0082458 | -0.0036274 | 0.0014056 | 0.013514 | 0.0027664 | -0.013733 | 0.07782 | -0.054932 | 0.018311 | 0.22888 | 0.10071 | 0.09613 | 0.086975 | 0.068665 | -0.045776 | 0.082397 | 0.19226 | 0.11444 | 0.17853 | 122.4884 | -0.009155 | -0.068664 | 122.7722 | 122.6395 | 122.644 | 0.15106 | 0.15564 | 122.4976 | -0.01831 | -0.004578 | 122.7356 | 122.7219 | 122.6578 | 0.2243 | 0.16022 | 0.28381 | 0.073243 | 0.23804 | 0.12817 | 0.13275 | 0.11444 | 122.6212 | 122.612 | -0.14191 | -0.13275 | 122.5616 | 122.6257 | 122.5296 | 122.6303
2427.0156 | 122.7951 | -122.5708 | 0.10986 | -0.0020601 | 0.014781 | 0.013597 | -0.0016343 | 0.020779 | -0.0035846 | -0.0012434 | -0.0043029 | 0.049234 | 0.008673 | 0.0021404 | 0.0022602 | 0.012659 | 0.001912 | -0.054932 | 0.073242 | -0.054932 | -0.041199 | 0.10529 | -0.004578 | 0.027466 | -0.027466 | 0.073242 | -0.082397 | 0.004578 | 0.10986 | 0.022888 | 0.15564 | 122.5159 | -0.036621 | -0.15106 | 122.6761 | 122.5983 | 122.5662 | 0.082398 | 0.050354 | 122.4884 | -0.036621 | -0.10529 | 122.6807 | 122.7264 | 122.5937 | 0.23804 | 0.10528 | 0.16022 | 0.013733 | 0.19226 | 0.086975 | 0.12817 | 0.15564 | 122.644 | 122.644 | -0.16479 | -0.19226 | 122.5296 | 122.5754 | 122.5159 | 122.5433
2428.7031 | 122.8455 | -122.58 | 0.082397 | -0.0020601 | 0.015849 | 0.010606 | -0.00056607 | 0.024197 | -0.0035846 | 0.0021746 | 0.0018005 | 0.052652 | 0.008673 | -0.0017048 | 0.0026874 | 0.012232 | 0.0014846 | -0.059509 | 0.082397 | -0.07782 | -0.036621 | 0.14191 | 0.018311 | 0.054932 | -0.004578 | 0.07782 | -0.068665 | 0.032043 | 0.15564 | 0.059509 | 0.16937 | 122.5021 | 0 | -0.11902 | 122.7219 | 122.6349 | 122.5983 | 0.13275 | 0.096131 | 122.5113 | -0.004577 | -0.050354 | 122.7356 | 122.7493 | 122.6395 | 0.23804 | 0.12817 | 0.21973 | 0.041199 | 0.22431 | 0.10071 | 0.16022 | 0.14649 | 122.6624 | 122.6578 | -0.16022 | -0.15106 | 122.5433 | 122.612 | 122.5204 | 122.5754
2430.4531 | 122.7081 | -122.5891 | 0.14191 | 0.0055694 | 0.019267 | 0.012102 | -0.00013887 | 0.023984 | -0.0018756 | 0.00025205 | -0.0012513 | 0.052225 | 0.0082458 | -0.0126 | 0.003542 | 0.014795 | 0.0014846 | -0.050354 | 0.10529 | -0.086975 | -0.086975 | 0.036621 | -0.082397 | -0.059509 | -0.09613 | 0.10529 | -0.086975 | -0.041199 | -0.009155 | -0.086975 | 0.064087 | 122.5021 | -0.036621 | -0.22888 | 122.6257 | 122.5296 | 122.5067 | 0.027466 | 0.004578 | 122.5021 | -0.036621 | -0.18311 | 122.58 | 122.6532 | 122.5021 | 0.15106 | 0 | 0.1236 | 0 | 0.07782 | 0.045776 | 0.19226 | 0.19226 | 122.6944 | 122.6944 | -0.22888 | -0.22888 | 122.5021 | 122.5479 | 122.5388 | 122.493
2432.2344 | 122.6944 | -122.6028 | 0.11444 | 0.0055694 | 0.018412 | 0.014024 | -0.00056607 | 0.028256 | -0.0018756 | -0.00081595 | -0.0073547 | 0.052865 | 0.0082458 | -0.008327 | 0.0037556 | 0.013514 | 0.0004166 | -0.073242 | 0.11444 | -0.10071 | -0.1236 | 0 | -0.09613 | -0.068665 | -0.14191 | 0.10071 | -0.10986 | -0.041199 | 0.018311 | -0.10071 | 0.091553 | 122.5021 | 0 | -0.23804 | 122.6028 | 122.5342 | 122.5067 | 0.032043 | 0.004578 | 122.493 | -0.013733 | -0.15564 | 122.6212 | 122.6944 | 122.5021 | 0.20142 | 0.009155 | 0.10071 | -0.022888 | 0.12817 | 0.068664 | 0.21515 | 0.21057 | 122.7173 | 122.7036 | -0.21515 | -0.2243 | 122.4792 | 122.5616 | 122.5296 | 122.4609
2434 | 122.7081 | -122.6028 | 0.11902 | -0.0096891 | 0.020121 | 0.013384 | -0.0012069 | 0.024838 | -0.0025166 | 0.0015338 | 0.0018005 | 0.052438 | 0.006964 | -0.0059772 | 0.0024738 | 0.016077 | 0.0004166 | -0.068665 | 0.11902 | -0.086975 | -0.11444 | 0.032043 | -0.07782 | -0.054932 | -0.12817 | 0.10071 | -0.082397 | -0.045776 | 0.009155 | -0.086975 | 0.07782 | 122.5159 | 0 | -0.23346 | 122.6349 | 122.5479 | 122.525 | 0.032043 | 0.009155 | 122.5204 | -0.018311 | -0.16479 | 122.612 | 122.6807 | 122.5159 | 0.16022 | -0.004578 | 0.11902 | -0.027466 | 0.091552 | 0.036621 | 0.20599 | 0.18311 | 122.7219 | 122.7036 | -0.20599 | -0.20142 | 122.4884 | 122.5571 | 122.5342 | 122.4747
2435.7031 | 122.7997 | -122.5983 | 0.10071 | 0.013199 | 0.017131 | 0.011675 | -0.0022751 | 0.021634 | -0.0031574 | 0.0015338 | -0.0043029 | 0.049447 | 0.0082458 | -0.0032 | -0.001585 | 0.015009 | 0.0008438 | -0.022888 | 0.07782 | -0.059509 | -0.004578 | 0.17395 | 0.059509 | 0.073242 | 0.022888 | 0.073242 | -0.073242 | 0.022888 | 0.1236 | 0.036621 | 0.13275 | 122.5388 | -0.022888 | -0.10529 | 122.7722 | 122.6715 | 122.6578 | 0.13275 | 0.11902 | 122.525 | -0.027466 | -0.07782 | 122.7219 | 122.731 | 122.6349 | 0.20599 | 0.10986 | 0.23346 | 0.054931 | 0.19684 | 0.09613 | 0.13733 | 0.14648 | 122.6761 | 122.6715 | -0.16022 | -0.17395 | 122.5937 | 122.6212 | 122.5754 | 122.6212
2437.4688 | 122.8271 | -122.5754 | 0.073242 | -0.024948 | 0.015635 | 0.011888 | -0.0022751 | 0.023984 | -0.0027302 | -0.0010298 | -0.0012513 | 0.049234 | 0.0078186 | -0.003841 | 0.00076477 | 0.014582 | 0.0023392 | -0.045776 | 0.068665 | -0.050354 | -0.027466 | 0.16022 | 0.004578 | 0.036621 | 0.013733 | 0.054932 | -0.064087 | 0.036621 | 0.11444 | 0.027466 | 0.15564 | 122.525 | -0.004577 | -0.10071 | 122.7356 | 122.612 | 122.58 | 0.086975 | 0.054932 | 122.5113 | -0.01831 | -0.036621 | 122.6898 | 122.731 | 122.6028 | 0.21973 | 0.091553 | 0.21057 | 0.022888 | 0.17853 | 0.10071 | 0.11902 | 0.11902 | 122.644 | 122.6303 | -0.1236 | -0.13733 | 122.5479 | 122.612 | 122.5296 | 122.5891
2439.2344 | 122.7585 | -122.6074 | 0.11902 | 0.0055694 | 0.01649 | 0.012102 | 0.00050193 | 0.019711 | -0.0010212 | -0.0023114 | -0.0012513 | 0.054361 | 0.0095276 | -0.0053364 | 0.0039692 | 0.012446 | 0.0010574 | -0.082397 | 0.1236 | -0.10529 | -0.11902 | 0.018311 | -0.10986 | -0.054932 | -0.10529 | 0.10529 | -0.091553 | -0.032043 | 0.022888 | -0.082397 | 0.086975 | 122.5021 | 0.004577 | -0.23804 | 122.6257 | 122.5525 | 122.4976 | 0.050354 | -0.004577 | 122.5159 | -0.013733 | -0.15106 | 122.6303 | 122.6944 | 122.525 | 0.17853 | 0.009156 | 0.1236 | -0.013733 | 0.11444 | 0.05951 | 0.22888 | 0.19684 | 122.731 | 122.7127 | -0.22431 | -0.21057 | 122.4884 | 122.5754 | 122.525 | 122.5021
2440.9219 | 122.8729 | -122.5708 | 0.091553 | -0.0020601 | 0.016062 | 0.013384 | -0.0018479 | 0.020779 | -0.0025166 | -0.00060235 | -0.0012513 | 0.049447 | 0.0084594 | 0.00043161 | 0.00055117 | 0.012446 | -0.0002244 | -0.045776 | 0.086975 | -0.068665 | -0.009155 | 0.16022 | 0.050354 | 0.082397 | 0.036621 | 0.068665 | -0.068665 | 0.068665 | 0.18768 | 0.09613 | 0.19684 | 122.5021 | -0.004578 | -0.10071 | 122.731 | 122.6532 | 122.6212 | 0.15106 | 0.11902 | 122.5021 | -0.022888 | -0.022888 | 122.7585 | 122.7676 | 122.6669 | 0.2655 | 0.16479 | 0.22888 | 0.05951 | 0.25635 | 0.13733 | 0.15564 | 0.13733 | 122.6578 | 122.6395 | -0.16022 | -0.16022 | 122.5616 | 122.6395 | 122.525 | 122.6074
2442.6719 | 122.7585 | -122.5891 | 0.1236 | -0.024948 | 0.014567 | 0.0088974 | -0.0018479 | 0.018429 | -0.0020892 | 0.00025205 | -0.0073547 | 0.050302 | 0.0088866 | -0.0076862 | 0.00012397 | 0.014795 | -0.0010788 | -0.091553 | 0.10986 | -0.10529 | -0.11902 | 0.036621 | -0.064087 | -0.032043 | -0.10986 | 0.09613 | -0.09613 | -0.068665 | 0.036621 | -0.050354 | 0.09613 | 122.4838 | -0.013733 | -0.24261 | 122.6257 | 122.5571 | 122.525 | 0.073243 | 0.041199 | 122.493 | -0.027466 | -0.19226 | 122.6257 | 122.6852 | 122.5388 | 0.19226 | 0.045776 | 0.14191 | -0.013733 | 0.13275 | 0.027465 | 0.21515 | 0.19226 | 122.699 | 122.6852 | -0.22888 | -0.21973 | 122.4701 | 122.5204 | 122.4976 | 122.4792
2444.4531 | 122.8409 | -122.5845 | 0.10071 | -0.0020601 | 0.019053 | 0.01317 | -0.0033433 | 0.020993 | -0.0018756 | -0.0020978 | 0.0018005 | 0.049875 | 0.0073914 | 0.0034222 | 0.001192 | 0.013941 | -0.002147 | -0.004578 | 0.041199 | -0.054932 | 0.022888 | 0.18768 | 0.073242 | 0.082397 | 0.045776 | 0.064087 | -0.054932 | 0.041199 | 0.16022 | 0.086975 | 0.17853 | 122.5296 | -0.059509 | -0.07782 | 122.7722 | 122.6669 | 122.6578 | 0.13733 | 0.12817 | 122.5296 | -0.036621 | -0.059509 | 122.7448 | 122.7631 | 122.6715 | 0.23346 | 0.14191 | 0.24261 | 0.07782 | 0.21515 | 0.096131 | 0.096131 | 0.11902 | 122.6257 | 122.6486 | -0.15564 | -0.15564 | 122.6074 | 122.6257 | 122.58 | 122.6303
2446.2344 | 122.8134 | -122.5937 | 0.091553 | -0.0020601 | 0.014567 | 0.010393 | -0.0041977 | 0.022488 | -0.00059378 | 0.0021746 | -0.0043029 | 0.050088 | 0.0088866 | 0.00064521 | 0.0014056 | 0.015009 | 0.0040482 | -0.054932 | 0.073242 | -0.07782 | -0.045776 | 0.10529 | -0.013733 | 0.013733 | -0.032043 | 0.064087 | -0.068665 | 0.018311 | 0.10071 | 0.018311 | 0.14648 | 122.5159 | -0.018311 | -0.13733 | 122.699 | 122.6074 | 122.58 | 0.091553 | 0.064087 | 122.525 | -0.027466 | -0.073242 | 122.6944 | 122.7402 | 122.612 | 0.21515 | 0.086976 | 0.18311 | 0.032044 | 0.16937 | 0.086976 | 0.15106 | 0.13275 | 122.6669 | 122.6578 | -0.16937 | -0.16022 | 122.5479 | 122.612 | 122.5388 | 122.5616
2447.9375 | 122.7997 | -122.5937 | 0.11444 | -0.0020601 | 0.018412 | 0.011675 | -0.00035247 | 0.024624 | -0.003371 | 0.00046565 | -0.0012513 | 0.052011 | 0.0084594 | -0.0068316 | -8.9634e-05 | 0.013727 | -0.000438 | -0.027466 | 0.10986 | -0.09613 | -0.054932 | 0.10071 | -0.009155 | 0.009155 | 0 | 0.086975 | -0.068665 | -0.004578 | 0.09613 | 0 | 0.1236 | 122.4976 | -0.004578 | -0.16937 | 122.6944 | 122.6028 | 122.5845 | 0.10528 | 0.086975 | 122.525 | -0.027466 | -0.11902 | 122.6898 | 122.7173 | 122.5937 | 0.19226 | 0.068665 | 0.19684 | 0.041198 | 0.16479 | 0.064087 | 0.20599 | 0.15564 | 122.7036 | 122.6807 | -0.21057 | -0.18311 | 122.5388 | 122.5891 | 122.5662 | 122.5937
2449.625 | 122.818 | -122.5754 | 0.10529 | 0.013199 | 0.018626 | 0.013384 | -0.00035247 | 0.023556 | -0.0010212 | -0.00017515 | 0.0018005 | 0.050302 | 0.0091002 | -0.0036274 | 0.0050372 | 0.014795 | -0.0023606 | -0.073242 | 0.10986 | -0.091553 | -0.10071 | 0.036621 | -0.07782 | -0.036621 | -0.050354 | 0.09613 | -0.07782 | 0.018311 | 0.082397 | -0.027466 | 0.13275 | 122.4838 | 0.004577 | -0.20599 | 122.612 | 122.5388 | 122.4976 | 0.054932 | 0.013733 | 122.4976 | -0.009156 | -0.086975 | 122.6578 | 122.7081 | 122.5479 | 0.21057 | 0.050354 | 0.12817 | -0.009155 | 0.16022 | 0.096131 | 0.20142 | 0.17395 | 122.6852 | 122.6715 | -0.19684 | -0.18311 | 122.4747 | 122.5937 | 122.5021 | 122.525
2451.3906 | 122.8592 | -122.5845 | 0.10986 | -0.0020601 | 0.019053 | 0.012102 | -0.0027023 | 0.02377 | -0.0023028 | 0.00046565 | 0.0018005 | 0.049447 | 0.0071776 | -0.006618 | 0.00076477 | 0.012873 | -0.000438 | -0.018311 | 0.064087 | -0.045776 | 0.018311 | 0.19226 | 0.064087 | 0.073242 | 0.059509 | 0.073242 | -0.054932 | 0.068665 | 0.16479 | 0.073242 | 0.17395 | 122.5388 | -0.045776 | -0.091552 | 122.7768 | 122.6578 | 122.6486 | 0.11902 | 0.10986 | 122.5296 | -0.036621 | -0.041198 | 122.7493 | 122.7585 | 122.6578 | 0.22888 | 0.12817 | 0.23804 | 0.064087 | 0.21973 | 0.1236 | 0.10986 | 0.12817 | 122.6486 | 122.6578 | -0.15564 | -0.16479 | 122.6028 | 122.6532 | 122.5662 | 122.644
2453.1562 | 122.8363 | -122.6074 | 0.10529 | -0.0096891 | 0.018626 | 0.0086838 | -0.0016343 | 0.026761 | -0.0012348 | 0.0013202 | -0.0012513 | 0.051797 | 0.0071776 | -0.00555 | 0.001833 | 0.015009 | 0.0034072 | -0.022888 | 0.059509 | -0.045776 | -0.027466 | 0.15106 | 0.018311 | 0.041199 | 0.018311 | 0.064087 | -0.041199 | 0.032043 | 0.10986 | 0.050354 | 0.15106 | 122.5616 | -0.045777 | -0.13275 | 122.7585 | 122.6486 | 122.6257 | 0.086975 | 0.064087 | 122.5662 | -0.041199 | -0.073243 | 122.7173 | 122.7585 | 122.6578 | 0.19226 | 0.091553 | 0.19684 | 0.01831 | 0.15106 | 0.073242 | 0.10528 | 0.10529 | 122.6669 | 122.6715 | -0.15106 | -0.14649 | 122.58 | 122.6395 | 122.5845 | 122.6257
2454.8438 | 122.8409 | -122.5754 | 0.10071 | -0.0020601 | 0.015849 | 0.0099656 | -0.0016343 | 0.023984 | -0.0029438 | -0.0029524 | -0.0012513 | 0.050302 | 0.006964 | -0.0019184 | 0.0031146 | 0.013514 | 0.001271 | -0.041199 | 0.068665 | -0.082397 | -0.041199 | 0.10529 | -0.018311 | 0.013733 | -0.036621 | 0.082397 | -0.073242 | 0.013733 | 0.10071 | 0 | 0.14648 | 122.493 | -0.032043 | -0.14191 | 122.6807 | 122.5891 | 122.5571 | 0.09613 | 0.064086 | 122.5021 | -0.018311 | -0.086975 | 122.6761 | 122.7219 | 122.5754 | 0.21973 | 0.073242 | 0.18768 | 0.041198 | 0.17395 | 0.086975 | 0.15106 | 0.15564 | 122.644 | 122.6578 | -0.18311 | -0.17395 | 122.5342 | 122.5891 | 122.5342 | 122.5388
2456.5469 | 122.8455 | -122.5845 | 0.10071 | -0.0020601 | 0.018626 | 0.010606 | -0.00099327 | 0.025265 | 0.00047422 | 0.00067925 | -0.0012513 | 0.051797 | 0.009314 | -0.0078998 | 0.0033282 | 0.014795 | -0.0006516 | -0.059509 | 0.13275 | -0.091553 | -0.073242 | 0.054932 | -0.054932 | -0.027466 | -0.009155 | 0.07782 | -0.073242 | 0.041199 | 0.09613 | 0.004578 | 0.16937 | 122.493 | 0.032043 | -0.17395 | 122.6395 | 122.5571 | 122.5296 | 0.064087 | 0.036621 | 122.5113 | -0.022888 | -0.059509 | 122.6807 | 122.7539 | 122.5891 | 0.24261 | 0.07782 | 0.14649 | 0.018311 | 0.16937 | 0.11444 | 0.2243 | 0.15106 | 122.7173 | 122.6624 | -0.19226 | -0.17395 | 122.5113 | 122.6257 | 122.525 | 122.5754
2458.3125 | 122.7676 | -122.6303 | 0.10986 | -0.0096891 | 0.014781 | 0.0095382 | -0.00056607 | 0.020779 | -0.0025166 | -0.0010298 | -0.0043029 | 0.052011 | 0.0088866 | -0.0064044 | -0.0013714 | 0.011377 | 0.001271 | -0.10529 | 0.10529 | -0.082397 | -0.12817 | 0.036621 | -0.059509 | -0.032043 | -0.10986 | 0.09613 | -0.091553 | -0.045776 | 0.036621 | -0.054932 | 0.086975 | 122.5479 | -0.004577 | -0.23804 | 122.6669 | 122.5983 | 122.5708 | 0.050354 | 0.022888 | 122.5388 | -0.013733 | -0.15564 | 122.6669 | 122.7173 | 122.5754 | 0.17853 | 0.036621 | 0.11902 | -0.045777 | 0.12817 | 0.045777 | 0.18768 | 0.18768 | 122.7356 | 122.7264 | -0.19226 | -0.20142 | 122.5021 | 122.5845 | 122.525 | 122.5204
2460 | 122.7585 | -122.612 | 0.1236 | 0.0055694 | 0.015208 | 0.0095382 | 0.00028833 | 0.020566 | 0.00090142 | 0.00067925 | 0.0018005 | 0.052011 | 0.0091002 | -0.0046954 | 0.0026874 | 0.013941 | 0.0004166 | -0.059509 | 0.09613 | -0.10071 | -0.10986 | 0.032043 | -0.10071 | -0.054932 | -0.086975 | 0.09613 | -0.07782 | -0.036621 | 0.032043 | -0.059509 | 0.09613 | 122.5113 | -0.027466 | -0.23346 | 122.644 | 122.5571 | 122.5113 | 0.045776 | 0 | 122.5342 | -0.027466 | -0.16022 | 122.644 | 122.7081 | 122.5525 | 0.17395 | 0.018311 | 0.13275 | -0.009155 | 0.10986 | 0.041199 | 0.19684 | 0.17395 | 122.7081 | 122.7081 | -0.2243 | -0.20142 | 122.5021 | 122.5754 | 122.5525 | 122.525
2461.6875 | 122.7493 | -122.612 | 0.11444 | -0.0020601 | 0.022471 | 0.011461 | -0.0020615 | 0.024411 | -0.0010212 | 0.00046565 | 0.0048523 | 0.052865 | 0.0091002 | -0.006618 | 0.0026874 | 0.012659 | -0.001506 | -0.086975 | 0.13275 | -0.086975 | -0.13275 | 0.009155 | -0.10529 | -0.059509 | -0.13275 | 0.10986 | -0.082397 | -0.032043 | 0.013733 | -0.073242 | 0.082397 | 122.525 | 0.01831 | -0.24719 | 122.6212 | 122.5525 | 122.5067 | 0.027466 | -0.018311 | 122.5296 | -0.004578 | -0.14648 | 122.6257 | 122.6944 | 122.5388 | 0.16479 | 0.009155 | 0.09613 | -0.045776 | 0.09613 | 0.050354 | 0.21973 | 0.19226 | 122.7448 | 122.7219 | -0.20142 | -0.19684 | 122.4792 | 122.58 | 122.525 | 122.4792
2463.4531 | 122.8088 | -122.6028 | 0.12817 | -0.0020601 | 0.018626 | 0.010393 | -0.0024887 | 0.02377 | -0.0014484 | -0.00038875 | -0.0043029 | 0.051584 | 0.0071776 | -0.0025592 | -0.001585 | 0.013086 | 0.0016982 | -0.059509 | 0.11902 | -0.091553 | -0.086975 | 0.050354 | -0.041199 | -0.022888 | -0.086975 | 0.10071 | -0.07782 | -0.022888 | 0.082397 | -0.004578 | 0.11444 | 122.5113 | -0.009155 | -0.21515 | 122.6532 | 122.58 | 122.5616 | 0.068665 | 0.050354 | 122.525 | -0.027466 | -0.15106 | 122.6852 | 122.7173 | 122.5983 | 0.19226 | 0.073242 | 0.14191 | 0.004578 | 0.16022 | 0.054932 | 0.21057 | 0.17853 | 122.7219 | 122.7036 | -0.21973 | -0.20599 | 122.5159 | 122.58 | 122.5433 | 122.5159
2465.1719 | 122.7814 | -122.6303 | 0.13275 | -0.017319 | 0.017344 | 0.0076156 | -0.00035247 | 0.02612 | -0.0020892 | -0.0012434 | -0.0012513 | 0.050302 | 0.0063232 | -0.0068316 | 0.0014056 | 0.014795 | -0.0006516 | -0.086975 | 0.09613 | -0.09613 | -0.11444 | 0.036621 | -0.041199 | -0.032043 | -0.10529 | 0.091553 | -0.082397 | -0.041199 | 0.050354 | -0.036621 | 0.09613 | 122.5342 | -0.036621 | -0.24719 | 122.6669 | 122.5983 | 122.5891 | 0.064087 | 0.054931 | 122.5479 | -0.041198 | -0.17395 | 122.6807 | 122.7264 | 122.5937 | 0.17853 | 0.045776 | 0.13275 | -0.018311 | 0.13275 | 0.041198 | 0.19226 | 0.17395 | 122.7264 | 122.7219 | -0.22888 | -0.21515 | 122.5159 | 122.5891 | 122.5433 | 122.525
2466.9531 | 122.7585 | -122.6532 | 0.13733 | -0.0020601 | 0.016917 | 0.010393 | -0.0014207 | 0.020779 | -0.0027302 | -0.00017515 | 0.0048523 | 0.05137 | 0.008673 | -0.0059772 | -0.0030804 | 0.012018 | 0.0010574 | -0.064087 | 0.10529 | -0.07782 | -0.09613 | 0.073242 | -0.027466 | -0.013733 | -0.086975 | 0.10986 | -0.07782 | -0.041199 | 0.054932 | -0.036621 | 0.07782 | 122.5754 | -0.032043 | -0.23346 | 122.7264 | 122.6395 | 122.6257 | 0.064087 | 0.050354 | 122.5754 | -0.027466 | -0.17853 | 122.7081 | 122.731 | 122.6166 | 0.15564 | 0.041199 | 0.15106 | -0.01831 | 0.13275 | 0.036621 | 0.18311 | 0.18768 | 122.7585 | 122.7631 | -0.21515 | -0.21515 | 122.5571 | 122.612 | 122.5891 | 122.5662
2468.7031 | 122.8088 | -122.6212 | 0.11444 | -0.0020601 | 0.015208 | 0.014452 | -0.0022751 | 0.028256 | -0.0023028 | 0.00046565 | -0.0043029 | 0.055002 | 0.0084594 | -0.0070454 | 0.00055117 | 0.012659 | 0.0025528 | -0.036621 | 0.10071 | -0.07782 | -0.059509 | 0.11902 | -0.018311 | 0.004578 | -0.009155 | 0.073242 | -0.073242 | 0.009155 | 0.082397 | -0.022888 | 0.1236 | 122.5433 | -0.013733 | -0.17395 | 122.7402 | 122.6257 | 122.6028 | 0.082398 | 0.059509 | 122.5479 | -0.041199 | -0.10529 | 122.7036 | 122.7448 | 122.5983 | 0.19684 | 0.050354 | 0.19684 | 0.018311 | 0.15564 | 0.082397 | 0.17853 | 0.14648 | 122.7219 | 122.6944 | -0.19226 | -0.18768 | 122.5616 | 122.6303 | 122.5845 | 122.612
2470.4844 | 122.8134 | -122.6212 | 0.11444 | -0.0020601 | 0.017344 | 0.01082 | 0.00071573 | 0.025479 | 0.00068782 | 0.00089285 | 0.0018005 | 0.05137 | 0.0078186 | -0.0029864 | 0.003542 | 0.015223 | 0.0034072 | -0.064087 | 0.10529 | -0.10071 | -0.11902 | 0.045776 | -0.082397 | -0.041199 | -0.064087 | 0.091553 | -0.086975 | 0.004578 | 0.059509 | -0.036621 | 0.1236 | 122.5204 | -0.009155 | -0.23346 | 122.6669 | 122.58 | 122.5388 | 0.059509 | 0.018311 | 122.5342 | -0.022888 | -0.10986 | 122.6807 | 122.7448 | 122.5845 | 0.21057 | 0.050354 | 0.14648 | -0.018311 | 0.14648 | 0.091553 | 0.20599 | 0.17853 | 122.7264 | 122.7127 | -0.21515 | -0.20142 | 122.5021 | 122.6257 | 122.5571 | 122.5571
2472.2656 | 122.818 | -122.6486 | 0.1236 | -0.0096891 | 0.018412 | 0.011034 | 0.00092933 | 0.020993 | -0.0010212 | 3.8448e-05 | -0.0012513 | 0.050729 | 0.010168 | -0.0068316 | -8.9634e-05 | 0.014368 | -0.002147 | -0.068665 | 0.091553 | -0.086975 | -0.10529 | 0.045776 | -0.032043 | -0.027466 | -0.082397 | 0.11444 | -0.082397 | -0.009155 | 0.082397 | -0.022888 | 0.11444 | 122.5616 | -0.032043 | -0.22888 | 122.6944 | 122.6212 | 122.6166 | 0.059509 | 0.054932 | 122.5662 | -0.009155 | -0.13275 | 122.731 | 122.7631 | 122.6257 | 0.19684 | 0.059509 | 0.13275 | -0.018311 | 0.16479 | 0.073242 | 0.17853 | 0.19684 | 122.7402 | 122.7631 | -0.21057 | -0.20599 | 122.5433 | 122.6395 | 122.58 | 122.5662
2473.9688 | 122.8729 | -122.5983 | 0.09613 | -0.0096891 | 0.016703 | 0.012956 | -0.0014207 | 0.021634 | -0.0025166 | -0.00017515 | -0.0012513 | 0.049875 | 0.0078186 | -0.003841 | 0.0014056 | 0.013941 | -0.001506 | -0.036621 | 0.059509 | -0.036621 | -0.027466 | 0.16937 | -0.004578 | 0.050354 | 0.036621 | 0.054932 | -0.041199 | 0.041199 | 0.1236 | 0.036621 | 0.15564 | 122.5616 | -0.036621 | -0.1236 | 122.7676 | 122.6486 | 122.5937 | 0.086975 | 0.032043 | 122.5571 | -0.041198 | -0.054931 | 122.7219 | 122.7539 | 122.6349 | 0.19684 | 0.07782 | 0.20599 | 0.009155 | 0.16479 | 0.082398 | 0.09613 | 0.096131 | 122.6578 | 122.6532 | -0.13275 | -0.13733 | 122.5708 | 122.6395 | 122.5616 | 122.6349
2475.7188 | 122.7859 | -122.6624 | 0.1236 | -0.0020601 | 0.016917 | 0.010606 | -0.0012069 | 0.024411 | -0.0044392 | 0.00067925 | -0.0043029 | 0.049875 | 0.0078186 | -0.003841 | -0.0013714 | 0.011591 | -0.0010788 | -0.09613 | 0.10529 | -0.091553 | -0.13275 | 0.036621 | -0.027466 | -0.027466 | -0.10071 | 0.11444 | -0.091553 | -0.050354 | 0.041199 | -0.045776 | 0.082397 | 122.5708 | -0.01831 | -0.25635 | 122.699 | 122.6349 | 122.6349 | 0.064087 | 0.064087 | 122.5708 | -0.009155 | -0.17395 | 122.7036 | 122.7448 | 122.6166 | 0.17395 | 0.045777 | 0.12817 | -0.041198 | 0.13275 | 0.041199 | 0.19684 | 0.20599 | 122.7676 | 122.7768 | -0.21515 | -0.21515 | 122.5296 | 122.612 | 122.5662 | 122.5616
2477.5 | 122.8134 | -122.6486 | 0.12817 | -0.0020601 | 0.017344 | 0.012315 | -0.0014207 | 0.024838 | -0.0014484 | 0.00046565 | 0.0018005 | 0.050943 | 0.005896 | -0.011745 | -0.0011578 | 0.012659 | -0.0012924 | -0.027466 | 0.068665 | -0.059509 | -0.013733 | 0.15106 | 0.054932 | 0.064087 | -0.013733 | 0.07782 | -0.068665 | 0.004578 | 0.09613 | 0.004578 | 0.11902 | 122.5891 | -0.059509 | -0.14191 | 122.7997 | 122.7127 | 122.7036 | 0.1236 | 0.11444 | 122.58 | -0.050354 | -0.1236 | 122.7448 | 122.7676 | 122.6532 | 0.18768 | 0.073243 | 0.21057 | 0.045776 | 0.16479 | 0.073243 | 0.12817 | 0.14649 | 122.7173 | 122.7264 | -0.18768 | -0.19684 | 122.6349 | 122.6532 | 122.6212 | 122.6349
2479.2031 | 122.8363 | -122.612 | 0.10529 | -0.0020601 | 0.017771 | 0.012529 | -0.00056607 | 0.025265 | -0.0025166 | -0.00081595 | 0.0018005 | 0.051584 | 0.0061096 | -0.0027728 | 0.0048236 | 0.015223 | 0.00298 | -0.073242 | 0.11444 | -0.10529 | -0.11902 | 0.050354 | -0.068665 | -0.036621 | -0.054932 | 0.10071 | -0.073242 | 0.009155 | 0.059509 | -0.027466 | 0.12817 | 122.5067 | 0.009155 | -0.22431 | 122.6624 | 122.5754 | 122.5433 | 0.068665 | 0.036621 | 122.5388 | -0.004578 | -0.096131 | 122.6715 | 122.7402 | 122.5845 | 0.20142 | 0.045776 | 0.15564 | -0.013733 | 0.13275 | 0.082397 | 0.21973 | 0.17395 | 122.7264 | 122.7127 | -0.21057 | -0.17853 | 122.493 | 122.6212 | 122.5388 | 122.5571
2480.9844 | 122.7768 | -122.6807 | 0.1236 | -0.0020601 | 0.018626 | 0.01082 | -0.0035569 | 0.019497 | -0.0035846 | -0.0010298 | -0.0043029 | 0.051584 | 0.009314 | -0.0096088 | -8.9634e-05 | 0.012018 | 0.001271 | -0.054932 | 0.07782 | -0.086975 | -0.068665 | 0.10071 | -0.009155 | -0.004578 | -0.068665 | 0.11444 | -0.086975 | -0.054932 | 0.054932 | -0.027466 | 0.07782 | 122.5937 | -0.045776 | -0.19226 | 122.7814 | 122.6761 | 122.6715 | 0.082397 | 0.07782 | 122.5937 | -0.009155 | -0.17853 | 122.7356 | 122.7585 | 122.6532 | 0.16479 | 0.059509 | 0.18768 | 0.01831 | 0.14191 | 0.032043 | 0.16479 | 0.20142 | 122.7585 | 122.7951 | -0.21057 | -0.21057 | 122.612 | 122.6257 | 122.6257 | 122.612
2482.75 | 122.8683 | -122.6166 | 0.10986 | -0.0020601 | 0.017771 | 0.010393 | -0.0037705 | 0.022702 | -0.0012348 | 0.0015338 | -0.0012513 | 0.050088 | 0.006964 | -0.0091816 | -0.00094423 | 0.013086 | 0.0016982 | 0 | 0.091553 | -0.054932 | -0.004578 | 0.1831 | 0.068665 | 0.086975 | 0.050354 | 0.068665 | -0.059509 | 0.018311 | 0.12817 | 0.054932 | 0.15564 | 122.5616 | -0.01831 | -0.11444 | 122.7997 | 122.7036 | 122.6852 | 0.14191 | 0.1236 | 122.5571 | -0.041198 | -0.091552 | 122.7448 | 122.7722 | 122.6715 | 0.21515 | 0.11444 | 0.23804 | 0.050354 | 0.18768 | 0.07782 | 0.14649 | 0.12817 | 122.7081 | 122.6852 | -0.16479 | -0.16937 | 122.612 | 122.6349 | 122.6166 | 122.6669
2484.5 | 122.9416 | -122.612 | 0.073242 | -0.0020601 | 0.017344 | 0.01317 | -0.0027023 | 0.020352 | -0.0025166 | 3.8448e-05 | 0.0018005 | 0.050729 | 0.0088866 | -0.00042299 | 0.003542 | 0.010096 | 0.000203 | -0.013733 | 0.086975 | -0.059509 | 0.004578 | 0.18768 | 0.073242 | 0.09613 | 0.082397 | 0.064087 | -0.041199 | 0.09613 | 0.19226 | 0.09613 | 0.19684 | 122.5525 | 0.013733 | -0.068664 | 122.7997 | 122.7081 | 122.6852 | 0.15564 | 0.13275 | 122.5708 | -0.009155 | 0.022888 | 122.8043 | 122.8088 | 122.7081 | 0.23804 | 0.13733 | 0.24719 | 0.064087 | 0.23346 | 0.13733 | 0.14648 | 0.10529 | 122.699 | 122.6761 | -0.13275 | -0.11444 | 122.6166 | 122.7081 | 122.5983 | 122.6944
2486.2031 | 122.7814 | -122.644 | 0.11902 | 0.0055694 | 0.018412 | 0.012315 | -0.00035247 | 0.025692 | -0.00016658 | 0.00067925 | 0.0048523 | 0.052652 | 0.0071776 | -0.0019184 | 0.0043964 | 0.013514 | 0.0006302 | -0.054932 | 0.1236 | -0.091553 | -0.11902 | 0.004578 | -0.10986 | -0.073242 | -0.11444 | 0.082397 | -0.082397 | -0.027466 | 0.004578 | -0.082397 | 0.086975 | 122.5525 | 0.004577 | -0.23804 | 122.6486 | 122.5708 | 122.5342 | 0.018311 | -0.01831 | 122.5616 | -0.036622 | -0.14649 | 122.6486 | 122.731 | 122.5616 | 0.16937 | 0 | 0.096131 | -0.027466 | 0.086975 | 0.054931 | 0.21515 | 0.16479 | 122.7676 | 122.7264 | -0.21057 | -0.20142 | 122.525 | 122.6166 | 122.5891 | 122.5296
2487.9688 | 122.905 | -122.6257 | 0.10071 | -0.0096891 | 0.016703 | 0.012529 | -0.0020615 | 0.021634 | -0.0029438 | -0.0012434 | 0.0018005 | 0.047738 | 0.006964 | -0.003841 | 0.0014056 | 0.015223 | -0.001506 | -0.059509 | 0.091553 | -0.068665 | -0.032043 | 0.11902 | 0.018311 | 0.045776 | -0.009155 | 0.064087 | -0.073242 | 0.054932 | 0.13733 | 0.064087 | 0.17853 | 122.5571 | -0.009155 | -0.13275 | 122.7448 | 122.6715 | 122.644 | 0.11444 | 0.086976 | 122.5525 | -0.036621 | -0.045776 | 122.7631 | 122.8043 | 122.6898 | 0.25177 | 0.13733 | 0.18768 | 0.036622 | 0.21057 | 0.12817 | 0.16022 | 0.13733 | 122.7173 | 122.6898 | -0.16937 | -0.17395 | 122.5937 | 122.6807 | 122.5662 | 122.6166
2489.7188 | 122.8867 | -122.644 | 0.10071 | -0.0020601 | 0.01649 | 0.01082 | -0.0037705 | 0.018216 | -0.0031574 | -0.0040204 | -0.0012513 | 0.048166 | 0.0078186 | -0.0046954 | 0.0016194 | 0.013727 | 0.0006302 | -0.064087 | 0.068665 | -0.07782 | -0.054932 | 0.11444 | 0.009155 | 0.027466 | -0.004578 | 0.07782 | -0.068665 | 0.036621 | 0.1236 | 0.050354 | 0.16022 | 122.5662 | -0.032043 | -0.15564 | 122.7585 | 122.6715 | 122.6532 | 0.10529 | 0.086975 | 122.5754 | -0.022888 | -0.064087 | 122.7676 | 122.8043 | 122.6944 | 0.22888 | 0.11902 | 0.19226 | 0.022888 | 0.19226 | 0.10529 | 0.14649 | 0.14649 | 122.7127 | 122.7219 | -0.17853 | -0.16937 | 122.5891 | 122.6807 | 122.58 | 122.6395
2491.4844 | 122.7905 | -122.6486 | 0.13275 | 0.0055694 | 0.018412 | 0.012956 | -0.0018479 | 0.025052 | -0.0014484 | -0.001457 | 0.0018005 | 0.051584 | 0.0063232 | -0.00555 | 0.003542 | 0.015223 | -0.0034286 | -0.07782 | 0.10529 | -0.10529 | -0.11902 | 0 | -0.10529 | -0.059509 | -0.11902 | 0.11444 | -0.082397 | -0.036621 | 0.022888 | -0.086975 | 0.09613 | 122.5433 | -0.027465 | -0.25177 | 122.6486 | 122.5891 | 122.5433 | 0.045777 | 0 | 122.5662 | -0.01831 | -0.16937 | 122.6715 | 122.7448 | 122.5616 | 0.17853 | -0.004578 | 0.10529 | -0.013733 | 0.10528 | 0.045776 | 0.21057 | 0.19684 | 122.7539 | 122.7631 | -0.23804 | -0.21515 | 122.5296 | 122.612 | 122.5708 | 122.5296
2493.2656 | 122.8592 | -122.6578 | 0.09613 | 0.0055694 | 0.019267 | 0.01082 | -0.0029159 | 0.02142 | -0.00038018 | 0.00046565 | -0.0073547 | 0.048807 | 0.0084594 | -0.0053364 | -0.0013714 | 0.015009 | 0.0027664 | -0.022888 | 0.073242 | -0.064087 | 0.004578 | 0.16937 | 0.054932 | 0.059509 | -0.013733 | 0.07782 | -0.059509 | 0.022888 | 0.11444 | 0.032043 | 0.13733 | 122.5937 | -0.022888 | -0.091552 | 122.8271 | 122.7173 | 122.7127 | 0.1236 | 0.11902 | 122.5983 | -0.01831 | -0.073242 | 122.7722 | 122.7951 | 122.6898 | 0.19684 | 0.091552 | 0.23346 | 0.068665 | 0.17395 | 0.082397 | 0.13733 | 0.13733 | 122.731 | 122.7356 | -0.16022 | -0.15564 | 122.6624 | 122.6807 | 122.6349 | 122.644
2494.9688 | 122.9324 | -122.5983 | 0.082397 | -0.0020601 | 0.015635 | 0.011888 | -0.00013887 | 0.026333 | -0.0012348 | -0.001457 | -0.0073547 | 0.050302 | 0.007605 | 0.0032086 | 0.0026874 | 0.014368 | -0.0019332 | -0.032043 | 0.086975 | -0.050354 | 0.009155 | 0.19226 | 0.064087 | 0.09613 | 0.073242 | 0.064087 | -0.064087 | 0.086975 | 0.19684 | 0.10071 | 0.20142 | 122.5479 | 0.004578 | -0.073242 | 122.7905 | 122.6944 | 122.6624 | 0.14648 | 0.11444 | 122.5342 | -0.01831 | 0.004578 | 122.7951 | 122.7997 | 122.699 | 0.2655 | 0.1648 | 0.24261 | 0.059509 | 0.26093 | 0.15106 | 0.13733 | 0.12817 | 122.6852 | 122.6624 | -0.13275 | -0.14648 | 122.6074 | 122.6852 | 122.5662 | 122.6715
2496.7188 | 122.8088 | -122.6761 | 0.10529 | -0.0020601 | 0.017985 | 0.013597 | -0.00077967 | 0.028256 | -0.0025166 | 0.0015338 | -0.0073547 | 0.050943 | 0.0073914 | 0.00021781 | -0.00051703 | 0.012232 | -0.0023606 | -0.07782 | 0.10071 | -0.09613 | -0.10986 | 0.050354 | -0.050354 | -0.036621 | -0.10986 | 0.09613 | -0.086975 | -0.059509 | 0.045776 | -0.054932 | 0.07782 | 122.58 | -0.004578 | -0.21515 | 122.7264 | 122.6395 | 122.6257 | 0.059509 | 0.045776 | 122.5891 | -0.009156 | -0.16479 | 122.7219 | 122.7539 | 122.6212 | 0.16479 | 0.032043 | 0.14648 | -0.013733 | 0.13275 | 0.027466 | 0.19684 | 0.1831 | 122.7768 | 122.7722 | -0.20142 | -0.19226 | 122.5662 | 122.6166 | 122.5983 | 122.5662
2498.4219 | 122.9187 | -122.6166 | 0.091553 | -0.0096891 | 0.017131 | 0.01082 | -0.0016343 | 0.023556 | -0.0027302 | -0.0018842 | -0.0073547 | 0.051797 | 0.0050414 | -0.0019184 | 0.0041828 | 0.0133 | -1.0598e-05 | -0.004578 | 0.045776 | -0.059509 | 0.032043 | 0.17395 | 0.036621 | 0.059509 | 0.054932 | 0.041199 | -0.032043 | 0.09613 | 0.16022 | 0.07782 | 0.19684 | 122.5571 | -0.045777 | -0.05951 | 122.7905 | 122.6761 | 122.6532 | 0.11902 | 0.09613 | 122.5845 | -0.050354 | 0.004577 | 122.7768 | 122.8134 | 122.6944 | 0.22888 | 0.10986 | 0.23346 | 0.091552 | 0.19226 | 0.12817 | 0.10528 | 0.073242 | 122.6624 | 122.6578 | -0.15106 | -0.1236 | 122.6486 | 122.7127 | 122.612 | 122.6715
2500.1875 | 122.7997 | -122.6578 | 0.12817 | -0.017319 | 0.015635 | 0.010606 | -0.0020615 | 0.02142 | -0.0037982 | -0.0020978 | -0.0043029 | 0.050943 | 0.0061096 | -0.0059772 | -0.0020122 | 0.0090277 | 0.0027664 | -0.086975 | 0.11444 | -0.10071 | -0.10529 | 0.027466 | -0.064087 | -0.036621 | -0.09613 | 0.10986 | -0.073242 | -0.041199 | 0.036621 | -0.032043 | 0.091553 | 122.5571 | -0.013733 | -0.23346 | 122.6852 | 122.6212 | 122.5937 | 0.064087 | 0.036621 | 122.5845 | -0.018311 | -0.16937 | 122.6944 | 122.7493 | 122.6257 | 0.16479 | 0.041199 | 0.12817 | -0.004578 | 0.10986 | 0.032043 | 0.21515 | 0.18311 | 122.7722 | 122.7676 | -0.22888 | -0.20142 | 122.5525 | 122.6166 | 122.5708 | 122.5616
2501.8906 | 122.9233 | -122.6212 | 0.068665 | -0.0020601 | 0.019267 | 0.011034 | -0.0035569 | 0.027401 | -0.00080758 | -0.00017515 | -0.0073547 | 0.049234 | 0.0088866 | -0.0044818 | 0.0054646 | 0.015009 | -0.003215 | 0.009155 | 0.059509 | -0.054932 | 0.022888 | 0.18768 | 0.032043 | 0.041199 | 0.064087 | 0.045776 | -0.045776 | 0.091553 | 0.17395 | 0.068665 | 0.19226 | 122.5662 | -0.009156 | -0.045777 | 122.8088 | 122.6624 | 122.6532 | 0.096131 | 0.086975 | 122.5754 | -0.022889 | 0.022888 | 122.7951 | 122.8134 | 122.6898 | 0.23804 | 0.11444 | 0.24261 | 0.07782 | 0.21973 | 0.13733 | 0.11444 | 0.091552 | 122.6807 | 122.6669 | -0.1236 | -0.11444 | 122.644 | 122.7127 | 122.6303 | 122.6852
2503.6562 | 122.8592 | -122.644 | 0.10986 | -0.0020601 | 0.019053 | 0.012102 | -0.0022751 | 0.023343 | -0.0012348 | -0.0020978 | -0.0073547 | 0.050729 | 0.0091002 | -0.012813 | 0.00076477 | 0.012446 | -0.0042832 | -0.036621 | 0.10071 | -0.07782 | -0.050354 | 0.10071 | -0.018311 | 0.004578 | -0.018311 | 0.086975 | -0.064087 | 0.018311 | 0.091553 | 0.004578 | 0.14648 | 122.5662 | -0.009155 | -0.16022 | 122.7448 | 122.6486 | 122.6257 | 0.082398 | 0.059509 | 122.58 | -0.022888 | -0.091552 | 122.7356 | 122.7905 | 122.6486 | 0.21057 | 0.068665 | 0.17853 | 0.027466 | 0.15564 | 0.082398 | 0.17853 | 0.15106 | 122.7448 | 122.731 | -0.18768 | -0.17395 | 122.5937 | 122.6624 | 122.6074 | 122.6257
2505.4375 | 122.905 | -122.6807 | 0.086975 | -0.0020601 | 0.01649 | 0.011461 | -0.0014207 | 0.022488 | -0.0020892 | -0.0018842 | -0.0043029 | 0.047738 | 0.0080322 | -0.0076862 | 0.0033282 | 0.014582 | -1.0598e-05 | -0.068665 | 0.073242 | -0.064087 | -0.045776 | 0.10529 | -0.009155 | 0.027466 | -0.027466 | 0.07782 | -0.054932 | 0.032043 | 0.11444 | 0.041199 | 0.15106 | 122.6166 | -0.013733 | -0.13275 | 122.7859 | 122.7081 | 122.6715 | 0.091553 | 0.054932 | 122.6257 | -0.009155 | -0.054932 | 122.7951 | 122.8317 | 122.7219 | 0.20599 | 0.096131 | 0.16937 | 0.018311 | 0.16937 | 0.086975 | 0.13733 | 0.13275 | 122.7539 | 122.7585 | -0.15106 | -0.14191 | 122.6349 | 122.7127 | 122.612 | 122.6532
2507.1406 | 122.8134 | -122.6761 | 0.11444 | 0.0055694 | 0.017558 | 0.011034 | -0.0031297 | 0.024197 | -0.0018756 | 0.0023882 | -0.0043029 | 0.053079 | 0.0080322 | -0.0081134 | -0.002226 | 0.012018 | -0.0008652 | -0.059509 | 0.10071 | -0.091553 | -0.086975 | 0.086975 | -0.018311 | 0 | -0.07782 | 0.09613 | -0.086975 | -0.050354 | 0.041199 | -0.041199 | 0.064087 | 122.5845 | -0.013733 | -0.20142 | 122.7631 | 122.6761 | 122.6578 | 0.091553 | 0.073242 | 122.5891 | -0.018311 | -0.16479 | 122.7173 | 122.7402 | 122.6349 | 0.15106 | 0.045776 | 0.17853 | 0.004578 | 0.12817 | 0.036621 | 0.19226 | 0.1831 | 122.7768 | 122.7722 | -0.20599 | -0.20142 | 122.5891 | 122.6257 | 122.6166 | 122.5983
2508.8906 | 122.9416 | -122.6257 | 0.09613 | -0.0096891 | 0.015849 | 0.013597 | -0.0033433 | 0.025692 | -0.0031574 | -0.0020978 | -0.0012513 | 0.049447 | 0.0056824 | -0.0053364 | 0.00076477 | 0.014582 | -0.003215 | -0.036621 | 0.073242 | -0.082397 | 0 | 0.17395 | 0.064087 | 0.082397 | 0.045776 | 0.07782 | -0.059509 | 0.091553 | 0.17395 | 0.09613 | 0.18768 | 122.5433 | -0.022888 | -0.09613 | 122.7997 | 122.7081 | 122.6898 | 0.16479 | 0.14648 | 122.5662 | -0.01831 | -0.004577 | 122.7997 | 122.8134 | 122.7219 | 0.24719 | 0.15564 | 0.25635 | 0.082397 | 0.23346 | 0.15106 | 0.15564 | 0.13733 | 122.699 | 122.7036 | -0.17853 | -0.15564 | 122.6257 | 122.7173 | 122.5891 | 122.6715
2510.5781 | 122.9233 | -122.644 | 0.09613 | -0.0020601 | 0.01649 | 0.011247 | -0.00056607 | 0.023556 | -0.0020892 | 0.0017474 | 0.0018005 | 0.049447 | 0.005896 | 0.00085881 | 0.0020466 | 0.0133 | 0.0027664 | -0.045776 | 0.082397 | -0.086975 | -0.027466 | 0.1236 | 0.027466 | 0.050354 | 0.004578 | 0.068665 | -0.059509 | 0.050354 | 0.16479 | 0.073242 | 0.17853 | 122.5571 | -0.013733 | -0.1236 | 122.7676 | 122.6944 | 122.6715 | 0.13733 | 0.11444 | 122.5845 | -0.027465 | -0.045776 | 122.8088 | 122.8226 | 122.7173 | 0.23804 | 0.13275 | 0.21057 | 0.059509 | 0.2243 | 0.10986 | 0.16937 | 0.12817 | 122.7264 | 122.7127 | -0.1831 | -0.15564 | 122.6166 | 122.6944 | 122.5983 | 122.6486
2512.3438 | 122.7905 | -122.6532 | 0.1236 | 0.013199 | 0.019267 | 0.011247 | 0.00050193 | 0.02142 | -0.003371 | -0.0012434 | -0.0012513 | 0.053293 | 0.0082458 | -0.0029864 | 0.0037556 | 0.012232 | 0.001271 | -0.059509 | 0.13275 | -0.091553 | -0.11902 | 0.009155 | -0.09613 | -0.059509 | -0.10986 | 0.10071 | -0.086975 | -0.022888 | 0.022888 | -0.082397 | 0.091553 | 122.5616 | 0.009155 | -0.24261 | 122.6624 | 122.5937 | 122.5571 | 0.032044 | -0.004577 | 122.5662 | -0.022888 | -0.14648 | 122.6761 | 122.7448 | 122.5708 | 0.17853 | 0.004578 | 0.10071 | -0.027466 | 0.10986 | 0.064087 | 0.2243 | 0.18768 | 122.7859 | 122.7539 | -0.21515 | -0.21057 | 122.5342 | 122.6303 | 122.5937 | 122.5433
2514.0938 | 122.7905 | -122.6807 | 0.13733 | 0.013199 | 0.019908 | 0.014879 | -0.00099327 | 0.028042 | -0.0012348 | 3.8448e-05 | 0.0048523 | 0.051797 | 0.0095276 | -0.0040546 | 0.003542 | 0.013941 | -0.0010788 | -0.064087 | 0.10529 | -0.086975 | -0.10071 | 0.045776 | -0.082397 | -0.054932 | -0.1236 | 0.10529 | -0.082397 | -0.036621 | 0.009155 | -0.082397 | 0.082397 | 122.5937 | -0.032043 | -0.23804 | 122.7264 | 122.6257 | 122.5983 | 0.032043 | 0.004578 | 122.5983 | -0.032043 | -0.17395 | 122.6898 | 122.7631 | 122.5983 | 0.16479 | 0 | 0.13275 | -0.013733 | 0.091552 | 0.045776 | 0.19226 | 0.18768 | 122.7859 | 122.7859 | -0.2243 | -0.21973 | 122.58 | 122.644 | 122.6166 | 122.5571
2515.8438 | 122.818 | -122.7081 | 0.1236 | 0.0055694 | 0.018412 | 0.010606 | -0.00077967 | 0.023129 | -0.0014484 | 0.00046565 | -0.0012513 | 0.049661 | 0.0078186 | -0.0053364 | -0.0020122 | 0.013086 | -0.0023606 | -0.050354 | 0.09613 | -0.091553 | -0.082397 | 0.10529 | -0.022888 | -0.009155 | -0.082397 | 0.10986 | -0.082397 | -0.045776 | 0.050354 | -0.041199 | 0.082397 | 122.6166 | -0.027466 | -0.20599 | 122.8134 | 122.699 | 122.6852 | 0.082398 | 0.068665 | 122.6257 | -0.013733 | -0.16937 | 122.7585 | 122.7905 | 122.6669 | 0.16479 | 0.041198 | 0.19684 | 0.009156 | 0.13275 | 0.036621 | 0.18768 | 0.19226 | 122.8043 | 122.818 | -0.21515 | -0.20599 | 122.6257 | 122.6624 | 122.6578 | 122.6257
2517.6094 | 122.8867 | -122.644 | 0.10529 | -0.0020601 | 0.017985 | 0.01082 | -0.0033433 | 0.019284 | -0.0035846 | 0.00025205 | -0.0012513 | 0.050302 | 0.0067504 | -0.0017048 | -0.00030343 | 0.012659 | 0.0040482 | -0.022888 | 0.082397 | -0.068665 | 0.018311 | 0.19684 | 0.068665 | 0.086975 | 0.032043 | 0.064087 | -0.054932 | 0.027466 | 0.13275 | 0.054932 | 0.14648 | 122.5754 | -0.022889 | -0.086975 | 122.8409 | 122.731 | 122.7127 | 0.15564 | 0.13733 | 122.5891 | -0.041199 | -0.07782 | 122.7768 | 122.7905 | 122.699 | 0.20142 | 0.10986 | 0.2655 | 0.086976 | 0.18768 | 0.082398 | 0.15106 | 0.11902 | 122.7264 | 122.7081 | -0.17395 | -0.16022 | 122.6624 | 122.6715 | 122.6212 | 122.6761
2519.375 | 122.9416 | -122.6395 | 0.09613 | 0.0055694 | 0.017558 | 0.012529 | -0.00013887 | 0.023343 | -0.0029438 | 0.0013202 | -0.0012513 | 0.050943 | 0.0082458 | -0.00063659 | 0.0056782 | 0.014368 | -0.0012924 | -0.054932 | 0.091553 | -0.086975 | -0.041199 | 0.11444 | -0.036621 | 0.018311 | 0.009155 | 0.068665 | -0.059509 | 0.082397 | 0.14648 | 0.050354 | 0.19684 | 122.5525 | -0.004577 | -0.13733 | 122.7539 | 122.6578 | 122.6028 | 0.10529 | 0.050354 | 122.58 | -0.027465 | -0.013733 | 122.7859 | 122.8363 | 122.6898 | 0.25635 | 0.10986 | 0.20142 | 0.045776 | 0.20599 | 0.14191 | 0.17853 | 0.12817 | 122.731 | 122.7081 | -0.1831 | -0.15564 | 122.5983 | 122.7219 | 122.5845 | 122.6486
2521.1406 | 122.9141 | -122.6395 | 0.07782 | -0.024948 | 0.014994 | 0.014024 | -0.0044113 | 0.023129 | -0.0012348 | 3.8448e-05 | -0.010406 | 0.050302 | 0.0078186 | -0.006618 | 0.003542 | 0.014795 | -0.000438 | -0.027466 | 0.054932 | -0.032043 | 0.004578 | 0.17853 | 0.022888 | 0.064087 | 0.045776 | 0.059509 | -0.045776 | 0.091553 | 0.14648 | 0.054932 | 0.17395 | 122.6074 | -0.022888 | -0.073242 | 122.818 | 122.7036 | 122.6624 | 0.09613 | 0.054931 | 122.5937 | -0.018311 | 0.013733 | 122.7859 | 122.8134 | 122.6944 | 0.21973 | 0.10071 | 0.21057 | 0.036621 | 0.19226 | 0.13733 | 0.086975 | 0.10528 | 122.6944 | 122.699 | -0.10986 | -0.1236 | 122.644 | 122.731 | 122.612 | 122.6852
2522.8438 | 122.8592 | -122.6807 | 0.1236 | -0.0096891 | 0.015635 | 0.013811 | 0.00050193 | 0.027401 | -0.0035846 | 3.8448e-05 | -0.0012513 | 0.050943 | 0.011023 | -0.01025 | 0.0014056 | 0.012873 | 0.0008438 | -0.045776 | 0.09613 | -0.082397 | -0.059509 | 0.091553 | -0.022888 | 0 | -0.018311 | 0.086975 | -0.07782 | 0 | 0.091553 | 0.004578 | 0.13275 | 122.5983 | -0.027466 | -0.1831 | 122.7722 | 122.6807 | 122.6578 | 0.082397 | 0.059509 | 122.6028 | -0.036621 | -0.1236 | 122.7722 | 122.8134 | 122.6852 | 0.21057 | 0.082398 | 0.17395 | 0.022888 | 0.16937 | 0.07782 | 0.17853 | 0.16479 | 122.7768 | 122.7676 | -0.20599 | -0.20142 | 122.6212 | 122.6807 | 122.6349 | 122.6624
2524.5938 | 122.8226 | -122.6852 | 0.12817 | -0.0020601 | 0.018626 | 0.009752 | -0.0024887 | 0.020779 | -0.0031574 | 0.0013202 | -0.0012513 | 0.050943 | 0.0065368 | -0.010463 | -0.0024396 | 0.011377 | -0.0017196 | -0.082397 | 0.091553 | -0.09613 | -0.10529 | 0.050354 | -0.041199 | -0.022888 | -0.10071 | 0.09613 | -0.086975 | -0.059509 | 0.050354 | -0.050354 | 0.082397 | 122.5891 | -0.036621 | -0.23346 | 122.7356 | 122.6624 | 122.644 | 0.073242 | 0.054931 | 122.5983 | -0.032044 | -0.18768 | 122.7356 | 122.7676 | 122.6349 | 0.16937 | 0.036621 | 0.14648 | -0.009156 | 0.13733 | 0.027466 | 0.18768 | 0.1831 | 122.7768 | 122.7814 | -0.2243 | -0.21515 | 122.58 | 122.6257 | 122.6028 | 122.5845
2526.3594 | 122.9462 | -122.6349 | 0.07782 | 0.0055694 | 0.018626 | 0.012529 | -0.00099327 | 0.022915 | -0.0012348 | 0.0023882 | -0.0043029 | 0.049875 | 0.0063232 | -0.0019184 | 0.0041828 | 0.015864 | 0.0031936 | -0.009155 | 0.086975 | -0.068665 | 0.009155 | 0.16022 | 0.032043 | 0.045776 | 0.073242 | 0.064087 | -0.036621 | 0.10986 | 0.16022 | 0.059509 | 0.20599 | 122.5662 | 0.009155 | -0.068665 | 122.7951 | 122.6807 | 122.6669 | 0.11444 | 0.10071 | 122.5983 | -0.013733 | 0.032043 | 122.7951 | 122.8409 | 122.6944 | 0.24262 | 0.09613 | 0.22888 | 0.07782 | 0.19684 | 0.14648 | 0.15564 | 0.10071 | 122.7219 | 122.699 | -0.14649 | -0.11444 | 122.644 | 122.7448 | 122.6257 | 122.7081
2528.0625 | 122.8455 | -122.6944 | 0.12817 | -0.0096891 | 0.019694 | 0.012743 | 0.00092933 | 0.024197 | -0.00038018 | 0.0032428 | 0.0018005 | 0.052865 | 0.0095276 | -0.0019184 | 0.00055117 | 0.0133 | -0.0025742 | -0.036621 | 0.086975 | -0.073242 | -0.054932 | 0.10529 | -0.027466 | -0.018311 | -0.009155 | 0.09613 | -0.068665 | 0.004578 | 0.073242 | -0.041199 | 0.10986 | 122.6212 | -0.041199 | -0.18311 | 122.7997 | 122.6761 | 122.6669 | 0.054931 | 0.045776 | 122.6257 | -0.032044 | -0.1236 | 122.7676 | 122.8043 | 122.6532 | 0.17853 | 0.027466 | 0.17853 | 0.01831 | 0.14191 | 0.073243 | 0.16022 | 0.16479 | 122.7814 | 122.7905 | -0.20142 | -0.19684 | 122.6395 | 122.699 | 122.6578 | 122.6852
2529.8125 | 122.8867 | -122.6944 | 0.11444 | -0.0020601 | 0.01884 | 0.011675 | -0.00035247 | 0.027829 | -0.0020892 | 0.00067925 | -0.0012513 | 0.051156 | 0.0095276 | -0.010677 | -8.9634e-05 | 0.014368 | 0.0042618 | -0.041199 | 0.09613 | -0.10529 | -0.050354 | 0.10071 | -0.013733 | 0.004578 | -0.018311 | 0.086975 | -0.068665 | 0.018311 | 0.10529 | 0.009155 | 0.13275 | 122.5891 | -0.018311 | -0.16479 | 122.7951 | 122.699 | 122.6807 | 0.10986 | 0.091553 | 122.6257 | -0.027466 | -0.09613 | 122.7997 | 122.8271 | 122.7036 | 0.20142 | 0.07782 | 0.20599 | 0.054932 | 0.17395 | 0.086976 | 0.20142 | 0.15564 | 122.7905 | 122.7814 | -0.21973 | -0.18311 | 122.644 | 122.7127 | 122.6532 | 122.6761
2531.5 | 122.9507 | -122.6715 | 0.068665 | -0.017319 | 0.018626 | 0.012956 | -0.0020615 | 0.022702 | -0.0023028 | 0.0015338 | -0.0012513 | 0.052438 | 0.007605 | 0.00085881 | 0.0020466 | 0.017359 | -1.0598e-05 | -0.022888 | 0.032043 | -0.045776 | 0.009155 | 0.18768 | 0.022888 | 0.07782 | 0.050354 | 0.068665 | -0.032043 | 0.09613 | 0.16022 | 0.059509 | 0.1831 | 122.6257 | -0.036622 | -0.05951 | 122.8592 | 122.7493 | 122.6944 | 0.1236 | 0.068664 | 122.6395 | 0 | 0.027465 | 122.8317 | 122.8546 | 122.731 | 0.21515 | 0.091552 | 0.23346 | 0.054931 | 0.19226 | 0.12817 | 0.077819 | 0.10071 | 122.7036 | 122.7402 | -0.11444 | -0.10071 | 122.6807 | 122.7676 | 122.6486 | 122.7219
2533.25 | 122.937 | -122.6669 | 0.10529 | -0.0096891 | 0.016703 | 0.013384 | -0.0035569 | 0.022488 | -0.0023028 | 0.0011066 | -0.0012513 | 0.050729 | 0.0080322 | -0.0057636 | 0.0022602 | 0.014368 | 0.0006302 | -0.059509 | 0.07782 | -0.086975 | -0.045776 | 0.13275 | 0.018311 | 0.054932 | -0.004578 | 0.07782 | -0.068665 | 0.036621 | 0.14191 | 0.082397 | 0.17853 | 122.58 | -0.027466 | -0.15106 | 122.7997 | 122.7219 | 122.6852 | 0.14191 | 0.10529 | 122.5983 | -0.027466 | -0.068665 | 122.8088 | 122.8455 | 122.7493 | 0.24719 | 0.15106 | 0.21973 | 0.041199 | 0.21057 | 0.10529 | 0.16479 | 0.14649 | 122.7448 | 122.7448 | -0.19226 | -0.17395 | 122.6212 | 122.7036 | 122.6074 | 122.6624
2535.0156 | 122.8363 | -122.7173 | 0.11902 | -0.0020601 | 0.017985 | 0.01082 | -0.0035569 | 0.024838 | -0.0010212 | 0.00067925 | 0.0018005 | 0.053293 | 0.0095276 | 0.004704 | -0.001585 | 0.011591 | 0.0004166 | -0.082397 | 0.11444 | -0.11444 | -0.09613 | 0.054932 | -0.036621 | -0.018311 | -0.10529 | 0.11444 | -0.082397 | -0.050354 | 0.050354 | -0.054932 | 0.073242 | 122.6028 | -0.004578 | -0.21515 | 122.7722 | 122.699 | 122.6807 | 0.09613 | 0.07782 | 122.6349 | -0.004578 | -0.16937 | 122.7676 | 122.7905 | 122.6624 | 0.15564 | 0.027465 | 0.16937 | 0.018311 | 0.13275 | 0.032043 | 0.22888 | 0.19684 | 122.8317 | 122.8317 | -0.23346 | -0.20142 | 122.6212 | 122.6669 | 122.6349 | 122.612
2536.7812 | 122.9599 | -122.6349 | 0.086975 | 0.0055694 | 0.017344 | 0.012315 | -0.0031297 | 0.022488 | -0.0025166 | 0.0015338 | -0.0073547 | 0.050302 | 0.0082458 | -0.002132 | 0.0041828 | 0.013941 | 0.0004166 | -0.013733 | 0.054932 | -0.041199 | 0.013733 | 0.1831 | 0.022888 | 0.050354 | 0.050354 | 0.059509 | -0.054932 | 0.091553 | 0.16479 | 0.064087 | 0.19684 | 122.5937 | -0.032043 | -0.073242 | 122.818 | 122.6852 | 122.6578 | 0.091553 | 0.064087 | 122.58 | -0.027466 | 0.004578 | 122.7997 | 122.8317 | 122.699 | 0.25177 | 0.11902 | 0.2243 | 0.054932 | 0.21973 | 0.14649 | 0.096131 | 0.11444 | 122.6898 | 122.6944 | -0.12817 | -0.14191 | 122.6486 | 122.7264 | 122.6212 | 122.6852
2538.5469 | 122.8271 | -122.6807 | 0.13275 | 0.0055694 | 0.020335 | 0.014024 | -0.0012069 | 0.022702 | -0.0025166 | 0.0030292 | -0.0012513 | 0.054147 | 0.0067504 | -0.0076862 | -0.00030343 | 0.013086 | -1.0598e-05 | -0.041199 | 0.10529 | -0.09613 | -0.064087 | 0.07782 | -0.054932 | -0.036621 | -0.050354 | 0.10986 | -0.068665 | -0.009155 | 0.032043 | -0.068665 | 0.086975 | 122.5845 | -0.027465 | -0.19684 | 122.7585 | 122.644 | 122.6257 | 0.059509 | 0.041198 | 122.612 | -0.022888 | -0.14191 | 122.7127 | 122.7676 | 122.612 | 0.15564 | 0 | 0.17395 | 0.032043 | 0.10071 | 0.05951 | 0.20142 | 0.17853 | 122.7859 | 122.7905 | -0.22888 | -0.20142 | 122.6166 | 122.6715 | 122.6395 | 122.6303
2540.2344 | 122.9599 | -122.6669 | 0.082397 | 0.0055694 | 0.017985 | 0.013384 | -0.0031297 | 0.021634 | -0.00080758 | -0.0016706 | -0.0012513 | 0.049234 | 0.007605 | -0.003841 | -0.0017986 | 0.013086 | 0.0008438 | -0.018311 | 0.082397 | -0.059509 | 0.022888 | 0.19684 | 0.073242 | 0.091553 | 0.050354 | 0.07782 | -0.068665 | 0.068665 | 0.16479 | 0.086975 | 0.17853 | 122.6074 | 0 | -0.059509 | 122.8638 | 122.7585 | 122.7402 | 0.15106 | 0.13275 | 122.5983 | -0.004577 | -0.013732 | 122.8317 | 122.8455 | 122.7539 | 0.24719 | 0.15564 | 0.25635 | 0.082397 | 0.23346 | 0.13733 | 0.14191 | 0.14649 | 122.7493 | 122.7448 | -0.14191 | -0.15106 | 122.6898 | 122.7356 | 122.6486 | 122.7173
2541.9844 | 122.9233 | -122.6669 | 0.10529 | -0.0020601 | 0.017771 | 0.011034 | -0.0012069 | 0.02377 | 0.00026062 | -0.0020978 | -0.010406 | 0.049234 | 0.0078186 | -0.006618 | 0.0043964 | 0.014368 | 0.000203 | -0.032043 | 0.064087 | -0.054932 | -0.009155 | 0.17853 | 0.009155 | 0.050354 | 0.041199 | 0.059509 | -0.045776 | 0.068665 | 0.13733 | 0.050354 | 0.16022 | 122.612 | -0.041199 | -0.11444 | 122.8455 | 122.7173 | 122.6761 | 0.10529 | 0.064087 | 122.6212 | -0.045777 | -0.036621 | 122.8043 | 122.8271 | 122.7173 | 0.20599 | 0.09613 | 0.23346 | 0.045777 | 0.18311 | 0.11444 | 0.11902 | 0.10528 | 122.731 | 122.7264 | -0.16022 | -0.15106 | 122.6578 | 122.7356 | 122.6349 | 122.7081
2543.6719 | 122.9828 | -122.6807 | 0.086975 | -0.0096891 | 0.017771 | 0.01317 | -0.0020615 | 0.020352 | -0.0020892 | 0.0017474 | -0.0012513 | 0.05137 | 0.0082458 | -0.0051226 | 0.0016194 | 0.0133 | -0.002147 | -0.045776 | 0.086975 | -0.073242 | -0.018311 | 0.15106 | 0.036621 | 0.064087 | 0.027466 | 0.054932 | -0.064087 | 0.059509 | 0.16479 | 0.10071 | 0.1831 | 122.6074 | 0 | -0.10529 | 122.8317 | 122.7448 | 122.7173 | 0.13733 | 0.10986 | 122.6166 | -0.032043 | -0.027466 | 122.8455 | 122.8638 | 122.7814 | 0.24719 | 0.1648 | 0.2243 | 0.054931 | 0.22888 | 0.1236 | 0.16022 | 0.11902 | 122.7676 | 122.7356 | -0.16022 | -0.15106 | 122.6624 | 122.7402 | 122.6349 | 122.7081
2545.4531 | 122.8363 | -122.6898 | 0.14191 | -0.0020601 | 0.01948 | 0.011461 | -0.00099327 | 0.024197 | -0.0023028 | -0.0029524 | -0.0073547 | 0.052865 | 0.0078186 | -0.0027728 | 0.00097837 | 0.01565 | -1.0598e-05 | -0.045776 | 0.10986 | -0.07782 | -0.10529 | 0.036621 | -0.07782 | -0.064087 | -0.068665 | 0.10071 | -0.054932 | -0.050354 | 0.013733 | -0.07782 | 0.10071 | 122.612 | -0.032044 | -0.24719 | 122.7264 | 122.6257 | 122.612 | 0.013733 | 0 | 122.6349 | -0.041199 | -0.19226 | 122.7036 | 122.7905 | 122.612 | 0.15564 | -0.022888 | 0.11444 | -0.027466 | 0.068665 | 0.004578 | 0.18768 | 0.15564 | 122.7997 | 122.7905 | -0.21973 | -0.19684 | 122.5845 | 122.6395 | 122.644 | 122.6212
2547.2188 | 122.9004 | -122.6807 | 0.10986 | 0.0055694 | 0.017344 | 0.013811 | -0.00077967 | 0.028256 | 4.7018e-05 | 0.0013202 | 0.0018005 | 0.051797 | 0.0088866 | -0.0029864 | 0.0043964 | 0.014368 | 0.0010574 | -0.07782 | 0.10529 | -0.082397 | -0.09613 | 0.050354 | -0.068665 | -0.036621 | -0.041199 | 0.091553 | -0.082397 | 0.013733 | 0.082397 | -0.009155 | 0.14191 | 122.5983 | -0.004577 | -0.20599 | 122.731 | 122.644 | 122.612 | 0.045776 | 0.013732 | 122.5983 | -0.01831 | -0.09613 | 122.7631 | 122.8226 | 122.6715 | 0.2243 | 0.073242 | 0.13275 | -0.013733 | 0.16479 | 0.09613 | 0.18768 | 0.17395 | 122.7859 | 122.7722 | -0.19226 | -0.19226 | 122.5845 | 122.6944 | 122.6028 | 122.6395
2548.9844 | 122.9874 | -122.6807 | 0.10071 | -0.0096891 | 0.016276 | 0.011247 | -0.0031297 | 0.020779 | -0.00016658 | -0.003166 | -0.0012513 | 0.049234 | 0.005896 | -0.0014912 | -0.0013714 | 0.014795 | -0.000438 | -0.018311 | 0.07782 | -0.050354 | 0.018311 | 0.21973 | 0.091553 | 0.082397 | 0.07782 | 0.059509 | -0.032043 | 0.07782 | 0.20599 | 0.10986 | 0.1831 | 122.6303 | -0.022888 | -0.082397 | 122.9004 | 122.7631 | 122.7722 | 0.13275 | 0.14191 | 122.6486 | -0.041199 | -0.022888 | 122.8867 | 122.8638 | 122.7905 | 0.21515 | 0.14191 | 0.27008 | 0.068665 | 0.23804 | 0.10986 | 0.12817 | 0.091552 | 122.7585 | 122.7402 | -0.15106 | -0.13275 | 122.699 | 122.7585 | 122.6624 | 122.7585
2550.6719 | 122.9599 | -122.6761 | 0.10071 | -0.0020601 | 0.017344 | 0.010606 | -0.0022751 | 0.024838 | -0.0010212 | 0.0051654 | -0.0012513 | 0.047952 | 0.0071776 | -0.0034138 | -0.0017986 | 0.013727 | -0.000438 | -0.004578 | 0.07782 | -0.045776 | 0.027466 | 0.21057 | 0.068665 | 0.086975 | 0.073242 | 0.059509 | -0.059509 | 0.064087 | 0.17395 | 0.073242 | 0.17853 | 122.6303 | -0.022888 | -0.073242 | 122.8867 | 122.7631 | 122.7448 | 0.13275 | 0.11444 | 122.6166 | -0.041199 | -0.036621 | 122.85 | 122.8546 | 122.7493 | 0.23804 | 0.13275 | 0.25635 | 0.073242 | 0.23346 | 0.1236 | 0.1236 | 0.11902 | 122.7539 | 122.7356 | -0.14648 | -0.16022 | 122.7036 | 122.7402 | 122.6715 | 122.7493
2552.4375 | 122.9187 | -122.6898 | 0.082397 | -0.017319 | 0.016276 | 0.011247 | -0.0033433 | 0.022275 | -0.0018756 | -0.00038875 | -0.0043029 | 0.051156 | 0.0063232 | -0.0057636 | 0.0039692 | 0.01565 | 0.0014846 | -0.036621 | 0.045776 | -0.018311 | -0.022888 | 0.13733 | 0.009155 | 0.050354 | 0 | 0.059509 | -0.036621 | 0.022888 | 0.10986 | 0.036621 | 0.16022 | 122.6715 | -0.036621 | -0.10528 | 122.8271 | 122.7402 | 122.699 | 0.068665 | 0.027466 | 122.6532 | -0.022888 | -0.059509 | 122.7997 | 122.85 | 122.7264 | 0.19684 | 0.073242 | 0.15564 | -0.004577 | 0.14648 | 0.059509 | 0.064087 | 0.09613 | 122.7356 | 122.7493 | -0.10071 | -0.11902 | 122.6669 | 122.7127 | 122.6532 | 122.6898
2554.2188 | 122.8775 | -122.6898 | 0.10529 | -0.017319 | 0.019908 | 0.012102 | -0.00035247 | 0.024197 | -0.0023028 | -0.00060235 | -0.0012513 | 0.052865 | 0.006964 | -0.0064044 | 0.00097837 | 0.012659 | -0.000438 | -0.027466 | 0.086975 | -0.068665 | -0.041199 | 0.10986 | -0.022888 | 0.004578 | -0.018311 | 0.11444 | -0.059509 | -0.004578 | 0.059509 | -0.041199 | 0.10529 | 122.6212 | -0.018311 | -0.14649 | 122.7997 | 122.6944 | 122.6669 | 0.073243 | 0.045777 | 122.6303 | 0.009155 | -0.10986 | 122.7493 | 122.7951 | 122.6486 | 0.16479 | 0.01831 | 0.17853 | 0.027466 | 0.11902 | 0.054931 | 0.15564 | 0.17395 | 122.7768 | 122.8043 | -0.17395 | -0.16479 | 122.6486 | 122.6852 | 122.6624 | 122.6715
2555.9844 | 122.9233 | -122.6852 | 0.09613 | -0.0096891 | 0.017771 | 0.013811 | -0.0035569 | 0.027615 | -0.0044392 | 0.0011066 | -0.0043029 | 0.050943 | 0.0071776 | -0.0014912 | 0.0031146 | 0.013514 | -1.0598e-05 | -0.050354 | 0.064087 | -0.064087 | -0.041199 | 0.14191 | 0 | 0.036621 | 0 | 0.054932 | -0.059509 | 0.022888 | 0.11902 | 0.027466 | 0.15106 | 122.6212 | -0.032043 | -0.13733 | 122.8271 | 122.7219 | 122.6852 | 0.10071 | 0.064087 | 122.6257 | -0.041198 | -0.073242 | 122.8043 | 122.8363 | 122.7127 | 0.21057 | 0.086975 | 0.20599 | 0.022888 | 0.17853 | 0.082397 | 0.12817 | 0.11444 | 122.7493 | 122.7402 | -0.16022 | -0.15564 | 122.644 | 122.7081 | 122.6349 | 122.6852
2557.6719 | 122.8592 | -122.699 | 0.1236 | -0.0020601 | 0.018412 | 0.011034 | 0.00071573 | 0.024197 | -0.0023028 | -0.0012434 | -0.0012513 | 0.051797 | 0.0088866 | -0.0068316 | 0.00055117 | 0.011805 | 0.0023392 | -0.032043 | 0.10071 | -0.091553 | -0.059509 | 0.073242 | -0.050354 | -0.027466 | -0.050354 | 0.09613 | -0.07782 | -0.018311 | 0.041199 | -0.064087 | 0.09613 | 122.6074 | -0.022888 | -0.1831 | 122.7722 | 122.6715 | 122.6486 | 0.064087 | 0.041199 | 122.6212 | -0.027466 | -0.14191 | 122.7402 | 122.7951 | 122.6349 | 0.17395 | 0.013733 | 0.16479 | 0.032044 | 0.11902 | 0.059509 | 0.19226 | 0.17395 | 122.7997 | 122.7951 | -0.21515 | -0.20142 | 122.6395 | 122.6807 | 122.6669 | 122.6486
2559.4375 | 122.8958 | -122.7127 | 0.082397 | -0.0096891 | 0.017344 | 0.011034 | -0.00099327 | 0.021847 | -0.0040118 | -0.0018842 | -0.0012513 | 0.051584 | 0.0099548 | -0.006618 | 0.0016194 | 0.013727 | -0.0008652 | -0.036621 | 0.10071 | -0.07782 | -0.045776 | 0.10529 | -0.004578 | -0.004578 | -0.009155 | 0.07782 | -0.059509 | 0.022888 | 0.10529 | -0.009155 | 0.13275 | 122.6349 | 0.018311 | -0.12817 | 122.818 | 122.7081 | 122.7081 | 0.073242 | 0.073242 | 122.6532 | -0.004577 | -0.059509 | 122.818 | 122.8455 | 122.7036 | 0.19226 | 0.050354 | 0.18311 | 0.032044 | 0.16479 | 0.082397 | 0.17853 | 0.13733 | 122.8134 | 122.7905 | -0.16022 | -0.14191 | 122.6669 | 122.7356 | 122.6761 | 122.7036
2561.1875 | 122.9416 | -122.7036 | 0.091553 | -0.0020601 | 0.019267 | 0.01082 | -0.0029159 | 0.021634 | -0.0035846 | -0.0012434 | 0.0018005 | 0.04902 | 0.0091002 | -0.0029864 | -0.00094423 | 0.011591 | 0.0027664 | -0.013733 | 0.068665 | -0.064087 | 0 | 0.1831 | 0.07782 | 0.07782 | 0.050354 | 0.073242 | -0.050354 | 0.027466 | 0.15564 | 0.059509 | 0.14648 | 122.6395 | -0.022888 | -0.091553 | 122.8867 | 122.7814 | 122.7814 | 0.14191 | 0.14191 | 122.6532 | -0.018311 | -0.064087 | 122.8592 | 122.85 | 122.7631 | 0.19684 | 0.10986 | 0.24719 | 0.064087 | 0.20599 | 0.07782 | 0.13275 | 0.1236 | 122.7722 | 122.7768 | -0.15564 | -0.14191 | 122.7036 | 122.731 | 122.6898 | 122.7539
2562.8906 | 122.9095 | -122.7173 | 0.11444 | -0.0020601 | 0.015422 | 0.010393 | -0.0044113 | 0.024624 | -0.00080758 | 0.0023882 | -0.0012513 | 0.050729 | 0.0071776 | -0.0061908 | -0.0017986 | 0.012873 | 0.0008438 | -0.004578 | 0.073242 | -0.068665 | -0.013733 | 0.15106 | 0.041199 | 0.059509 | -0.009155 | 0.068665 | -0.073242 | -0.009155 | 0.091553 | -0.009155 | 0.10986 | 122.6486 | -0.041199 | -0.12817 | 122.8683 | 122.7768 | 122.7585 | 0.12817 | 0.10986 | 122.644 | -0.045776 | -0.1236 | 122.8088 | 122.8271 | 122.7081 | 0.18311 | 0.064087 | 0.21973 | 0.054932 | 0.16479 | 0.064087 | 0.14191 | 0.14191 | 122.7905 | 122.7859 | -0.18311 | -0.18768 | 122.7036 | 122.7081 | 122.7127 | 122.7081
2564.5781 | 122.905 | -122.6807 | 0.10529 | -0.0020601 | 0.019267 | 0.011461 | -0.00077967 | 0.025479 | -0.0014484 | -0.00081595 | -0.0012513 | 0.051584 | 0.0078186 | -0.0023456 | 0.002901 | 0.0133 | 0.0027664 | -0.07782 | 0.10529 | -0.10529 | -0.10071 | 0.054932 | -0.068665 | -0.032043 | -0.050354 | 0.09613 | -0.073242 | 0.022888 | 0.07782 | -0.036621 | 0.12817 | 122.5754 | 0 | -0.20599 | 122.7356 | 122.6486 | 122.612 | 0.073243 | 0.036621 | 122.6074 | -0.009156 | -0.082398 | 122.7585 | 122.8088 | 122.644 | 0.20142 | 0.036621 | 0.16022 | 0.004578 | 0.15106 | 0.09613 | 0.21057 | 0.16937 | 122.7859 | 122.7768 | -0.21057 | -0.17853 | 122.58 | 122.7036 | 122.6028 | 122.6303
2566.3438 | 122.9462 | -122.6715 | 0.059509 | -0.0096891 | 0.016917 | 0.014879 | -0.0014207 | 0.023129 | -0.0014484 | -0.0038068 | -0.0043029 | 0.050302 | 0.0080322 | -0.0012774 | 0.0037556 | 0.013514 | -0.0017196 | -0.032043 | 0.064087 | -0.027466 | 0.013733 | 0.17395 | 0.045776 | 0.045776 | 0.041199 | 0.045776 | -0.045776 | 0.073242 | 0.14191 | 0.054932 | 0.17853 | 122.644 | 0.004578 | -0.045776 | 122.8455 | 122.7173 | 122.7173 | 0.073242 | 0.073242 | 122.6257 | -0.013733 | 0.013733 | 122.8134 | 122.85 | 122.7264 | 0.2243 | 0.10071 | 0.20142 | 0.041199 | 0.18768 | 0.11902 | 0.091553 | 0.091552 | 122.7356 | 122.7173 | -0.086975 | -0.10528 | 122.6852 | 122.7448 | 122.6395 | 122.7127
2568.125 | 122.8775 | -122.7127 | 0.1236 | -0.0096891 | 0.017771 | 0.013384 | -0.00099327 | 0.024624 | 4.7018e-05 | -0.0027386 | -0.0012513 | 0.053079 | 0.0067504 | -0.008327 | 0.002901 | 0.014155 | 0.0021256 | -0.073242 | 0.10986 | -0.09613 | -0.11444 | 0.022888 | -0.086975 | -0.045776 | -0.07782 | 0.091553 | -0.068665 | -0.009155 | 0.036621 | -0.036621 | 0.1236 | 122.6166 | -0.013733 | -0.23804 | 122.7356 | 122.6669 | 122.6257 | 0.050354 | 0.009155 | 122.644 | -0.032043 | -0.13275 | 122.7493 | 122.8363 | 122.6761 | 0.19226 | 0.032044 | 0.11902 | -0.018311 | 0.10529 | 0.05951 | 0.20599 | 0.16022 | 122.8226 | 122.8043 | -0.21973 | -0.19226 | 122.5983 | 122.7036 | 122.6395 | 122.6349
2569.8125 | 122.9507 | -122.6898 | 0.073242 | -0.0096891 | 0.017985 | 0.012102 | -0.0031297 | 0.02377 | -0.0023028 | 0.00025205 | -0.0073547 | 0.050302 | 0.0067504 | -0.010036 | 0.0014056 | 0.01565 | 0.0027664 | -0.027466 | 0.059509 | -0.036621 | 0.004578 | 0.17395 | 0.013733 | 0.054932 | 0.045776 | 0.068665 | -0.036621 | 0.073242 | 0.14191 | 0.050354 | 0.17395 | 122.6532 | -0.013733 | -0.068664 | 122.8638 | 122.7448 | 122.7036 | 0.091553 | 0.050354 | 122.6532 | -0.004577 | 0 | 122.8317 | 122.8638 | 122.7402 | 0.21057 | 0.086975 | 0.21057 | 0.041199 | 0.17853 | 0.10986 | 0.09613 | 0.10529 | 122.7493 | 122.7585 | -0.10986 | -0.10986 | 122.6944 | 122.7631 | 122.6624 | 122.7356
2571.5156 | 122.9965 | -122.6944 | 0.07782 | -0.017319 | 0.016276 | 0.0086838 | -0.0046249 | 0.022275 | -0.0035846 | 0.0011066 | -0.0012513 | 0.050943 | 0.0065368 | -0.0027728 | -0.002226 | 0.0133 | -0.0002244 | -0.032043 | 0.086975 | -0.050354 | 0.009155 | 0.1831 | 0.068665 | 0.09613 | 0.064087 | 0.050354 | -0.059509 | 0.086975 | 0.19684 | 0.10986 | 0.21057 | 122.644 | 0.009155 | -0.068665 | 122.8775 | 122.7905 | 122.7631 | 0.14648 | 0.11902 | 122.6349 | -0.027466 | 0.009155 | 122.8912 | 122.905 | 122.8043 | 0.27008 | 0.16937 | 0.23346 | 0.059509 | 0.25635 | 0.14648 | 0.13733 | 0.10986 | 122.7814 | 122.7448 | -0.12817 | -0.13733 | 122.7036 | 122.7814 | 122.6624 | 122.7585
2573.2188 | 123.0057 | -122.6807 | 0.091553 | 0.0055694 | 0.016703 | 0.011888 | -0.0035569 | 0.024411 | -0.0035846 | 0.0028154 | -0.0012513 | 0.049447 | 0.0099548 | -0.0040546 | -0.0011578 | 0.012873 | 0.0025528 | -0.018311 | 0.054932 | -0.054932 | 0.041199 | 0.23346 | 0.09613 | 0.11902 | 0.10529 | 0.059509 | -0.054932 | 0.086975 | 0.19684 | 0.10071 | 0.19684 | 122.6257 | -0.036621 | -0.050354 | 122.9141 | 122.7997 | 122.7768 | 0.17395 | 0.15106 | 122.6257 | -0.032044 | -0.004578 | 122.8775 | 122.8775 | 122.7814 | 0.25177 | 0.15564 | 0.28839 | 0.096131 | 0.25177 | 0.14191 | 0.10986 | 0.11444 | 122.7356 | 122.7402 | -0.14649 | -0.14649 | 122.7219 | 122.7676 | 122.6624 | 122.7859
2574.9844 | 122.9874 | -122.6944 | 0.10071 | -0.0096891 | 0.018412 | 0.010606 | -0.0018479 | 0.025265 | -0.0023028 | -0.0020978 | -0.0012513 | 0.050729 | 0.0080322 | -0.0034138 | 0.00097837 | 0.011164 | 0.0006302 | -0.009155 | 0.064087 | -0.064087 | 0.027466 | 0.19226 | 0.09613 | 0.09613 | 0.082397 | 0.073242 | -0.050354 | 0.068665 | 0.18768 | 0.10071 | 0.20142 | 122.6303 | -0.036621 | -0.073242 | 122.8867 | 122.7905 | 122.7905 | 0.16022 | 0.16022 | 122.644 | -0.027466 | -0.032043 | 122.8821 | 122.8958 | 122.7951 | 0.25177 | 0.15106 | 0.25635 | 0.091553 | 0.23804 | 0.11902 | 0.12817 | 0.1236 | 122.7585 | 122.7676 | -0.1648 | -0.15106 | 122.7219 | 122.7631 | 122.6852 | 122.7768
2576.6719 | 122.9919 | -122.6944 | 0.09613 | -0.0020601 | 0.019053 | 0.010393 | -0.00099327 | 0.023984 | -0.0025166 | -0.00038875 | -0.0043029 | 0.052011 | 0.0078186 | 0.0014996 | 0.0037556 | 0.014582 | -0.0006516 | -0.018311 | 0.07782 | -0.07782 | 0.013733 | 0.14648 | 0.018311 | 0.054932 | 0.064087 | 0.073242 | -0.064087 | 0.10071 | 0.16479 | 0.068665 | 0.21515 | 122.6166 | -0.01831 | -0.082397 | 122.8409 | 122.7493 | 122.7127 | 0.13275 | 0.096131 | 122.6303 | -0.022888 | 0.004578 | 122.8592 | 122.9095 | 122.7631 | 0.27924 | 0.13275 | 0.2243 | 0.091553 | 0.22888 | 0.1648 | 0.15564 | 0.13733 | 122.7722 | 122.7676 | -0.17395 | -0.16022 | 122.7081 | 122.7951 | 122.6761 | 122.7585
2578.4531 | 123.0103 | -122.6807 | 0.09613 | 0.0055694 | 0.017558 | 0.01082 | -0.0037705 | 0.021847 | -0.0012348 | 0.0023882 | -0.0043029 | 0.049661 | 0.0067504 | -0.0051226 | -0.0013714 | 0.013086 | -0.0023606 | -0.009155 | 0.064087 | -0.050354 | 0.045776 | 0.23346 | 0.10529 | 0.086975 | 0.086975 | 0.050354 | -0.027466 | 0.082397 | 0.20142 | 0.10529 | 0.19226 | 122.6303 | -0.032043 | -0.050354 | 122.9141 | 122.7676 | 122.7859 | 0.13733 | 0.15564 | 122.6532 | -0.045776 | -0.013733 | 122.8821 | 122.8729 | 122.7859 | 0.21973 | 0.13275 | 0.28381 | 0.09613 | 0.22888 | 0.10986 | 0.11444 | 0.07782 | 122.7448 | 122.731 | -0.14648 | -0.1236 | 122.7264 | 122.7631 | 122.6715 | 122.7676
2580.2188 | 122.9187 | -122.7539 | 0.10071 | -0.0096891 | 0.018412 | 0.010606 | 0.0024245 | 0.023343 | -0.0037982 | 0.0026018 | -0.0043029 | 0.052652 | 0.0078186 | -0.004909 | 0.0031146 | 0.013086 | -0.000438 | -0.045776 | 0.086975 | -0.091553 | -0.068665 | 0.073242 | -0.013733 | 0.004578 | -0.032043 | 0.10529 | -0.059509 | 0.004578 | 0.091553 | -0.004578 | 0.13275 | 122.6624 | -0.013733 | -0.16937 | 122.8271 | 122.7585 | 122.7402 | 0.096131 | 0.07782 | 122.6944 | 0.004578 | -0.09613 | 122.8455 | 122.8867 | 122.7493 | 0.19226 | 0.054931 | 0.16479 | 0.022888 | 0.15106 | 0.064087 | 0.17853 | 0.16479 | 122.8409 | 122.8592 | -0.19226 | -0.16022 | 122.6852 | 122.7585 | 122.7081 | 122.7219
2581.9062 | 122.9645 | -122.6669 | 0.091553 | -0.0020601 | 0.017558 | 0.012315 | -0.00013887 | 0.022915 | -0.001662 | 3.8448e-05 | 0.0018005 | 0.05137 | 0.0071776 | 0.00064521 | 0.0052508 | 0.0133 | -1.0598e-05 | -0.068665 | 0.10986 | -0.086975 | -0.068665 | 0.086975 | -0.054932 | 0.009155 | -0.009155 | 0.086975 | -0.07782 | 0.059509 | 0.13733 | 0.045776 | 0.17853 | 122.58 | 0.01831 | -0.16022 | 122.7539 | 122.6761 | 122.612 | 0.09613 | 0.032043 | 122.5891 | -0.004578 | -0.032044 | 122.8043 | 122.8455 | 122.7127 | 0.25635 | 0.1236 | 0.17395 | 0.01831 | 0.21515 | 0.13733 | 0.19684 | 0.16479 | 122.7768 | 122.7539 | -0.17853 | -0.16937 | 122.5983 | 122.7264 | 122.5983 | 122.6578
2583.6719 | 122.8729 | -122.7127 | 0.14191 | 0.0055694 | 0.01884 | 0.010606 | -0.0016343 | 0.022488 | -0.0018756 | 0.0011066 | -0.0012513 | 0.050943 | 0.011023 | -0.0034138 | -0.00073063 | 0.011805 | -0.0034286 | -0.032043 | 0.10529 | -0.073242 | -0.073242 | 0.064087 | -0.082397 | -0.036621 | -0.082397 | 0.10986 | -0.082397 | -0.018311 | 0.032043 | -0.07782 | 0.073242 | 122.6395 | -0.036621 | -0.21515 | 122.7768 | 122.6761 | 122.6303 | 0.036621 | -0.009155 | 122.6303 | -0.032044 | -0.16022 | 122.7448 | 122.7859 | 122.6349 | 0.15564 | 0.004577 | 0.13733 | 0 | 0.11444 | 0.064086 | 0.17853 | 0.19226 | 122.818 | 122.8226 | -0.21515 | -0.2243 | 122.6395 | 122.6944 | 122.6807 | 122.6303
2585.4531 | 122.9874 | -122.7264 | 0.07782 | -0.0020601 | 0.01948 | 0.012956 | 7.473e-05 | 0.025906 | -0.0012348 | 0.0026018 | -0.0043029 | 0.052011 | 0.008673 | -0.0051226 | 0.0058918 | 0.016291 | -0.0023606 | -0.073242 | 0.10071 | -0.086975 | -0.059509 | 0.086975 | -0.041199 | -0.004578 | -0.009155 | 0.091553 | -0.07782 | 0.068665 | 0.14191 | 0.032043 | 0.19226 | 122.6395 | 0.022888 | -0.13733 | 122.8134 | 122.7219 | 122.6852 | 0.082397 | 0.045776 | 122.6486 | 0.013733 | -0.009155 | 122.8683 | 122.9187 | 122.7585 | 0.27008 | 0.10986 | 0.17395 | 0.027466 | 0.21973 | 0.14649 | 0.18768 | 0.16937 | 122.8271 | 122.818 | -0.16479 | -0.15564 | 122.6669 | 122.7951 | 122.6532 | 122.7173
2587.2031 | 123.0194 | -122.7081 | 0.07782 | -0.0096891 | 0.016276 | 0.01317 | -0.0022751 | 0.019711 | -0.0023028 | 0.00067925 | -0.0012513 | 0.049234 | 0.0073914 | 0.0023542 | -0.0011578 | 0.015436 | 0.0016982 | -0.032043 | 0.054932 | -0.068665 | 0.013733 | 0.20599 | 0.082397 | 0.10071 | 0.064087 | 0.054932 | -0.064087 | 0.091553 | 0.1831 | 0.11444 | 0.19226 | 122.6395 | -0.022888 | -0.064087 | 122.9141 | 122.8088 | 122.7905 | 0.16937 | 0.15106 | 122.644 | -0.022888 | 0.013733 | 122.8912 | 122.9004 | 122.8226 | 0.25635 | 0.17853 | 0.27466 | 0.082398 | 0.24719 | 0.15564 | 0.1236 | 0.11902 | 122.7631 | 122.7631 | -0.14649 | -0.14191 | 122.7219 | 122.7997 | 122.6761 | 122.7722
2588.9688 | 123.0103 | -122.699 | 0.082397 | -0.0096891 | 0.016276 | 0.012743 | -0.0018479 | 0.025906 | -0.00016658 | 0.00046565 | -0.0043029 | 0.049234 | 0.007605 | -0.00085019 | 0.0020466 | 0.014795 | -0.0027878 | 0.009155 | 0.054932 | -0.068665 | 0.027466 | 0.16937 | 0.032043 | 0.064087 | 0.07782 | 0.064087 | -0.054932 | 0.10071 | 0.16937 | 0.082397 | 0.20599 | 122.6303 | -0.027465 | -0.054931 | 122.8683 | 122.7631 | 122.731 | 0.13275 | 0.10071 | 122.644 | -0.01831 | 0.018311 | 122.8683 | 122.905 | 122.7814 | 0.26093 | 0.13733 | 0.23804 | 0.096131 | 0.22431 | 0.15564 | 0.1236 | 0.11902 | 122.7539 | 122.7631 | -0.15106 | -0.13733 | 122.7264 | 122.7997 | 122.7081 | 122.7768
2590.6562 | 122.8546 | -122.7127 | 0.10986 | -0.0020601 | 0.017344 | 0.013811 | 0.00071573 | 0.025479 | -0.00080758 | -0.00017515 | -0.0012513 | 0.052011 | 0.008673 | -0.008327 | 0.00033757 | 0.012232 | 0.0031936 | -0.059509 | 0.10986 | -0.10071 | -0.1236 | 0.036621 | -0.09613 | -0.073242 | -0.1236 | 0.10071 | -0.086975 | -0.059509 | 0 | -0.091553 | 0.07782 | 122.612 | 0 | -0.23346 | 122.7493 | 122.6395 | 122.6166 | 0.027466 | 0.004578 | 122.6257 | -0.009155 | -0.16937 | 122.7127 | 122.7905 | 122.6212 | 0.16479 | -0.004578 | 0.13733 | -0.022888 | 0.086975 | 0.027466 | 0.21057 | 0.18768 | 122.8226 | 122.8134 | -0.21057 | -0.19684 | 122.5891 | 122.6532 | 122.6532 | 122.5891
2592.4375 | 122.9004 | -122.7219 | 0.10529 | 0.0055694 | 0.017344 | 0.012956 | -0.0012069 | 0.026333 | -0.00080758 | 0.0017474 | -0.0012513 | 0.052438 | 0.0097412 | -0.0051226 | -0.00030343 | 0.012018 | -0.0008652 | -0.036621 | 0.09613 | -0.07782 | -0.054932 | 0.11444 | -0.018311 | 0 | -0.018311 | 0.073242 | -0.064087 | 0.004578 | 0.09613 | 0.004578 | 0.11902 | 122.644 | -0.009156 | -0.16022 | 122.8363 | 122.7219 | 122.7036 | 0.07782 | 0.059509 | 122.6578 | -0.032044 | -0.10071 | 122.818 | 122.8409 | 122.7264 | 0.18311 | 0.068665 | 0.19226 | 0.022888 | 0.16022 | 0.068665 | 0.17395 | 0.13733 | 122.818 | 122.7951 | -0.18311 | -0.16937 | 122.6669 | 122.7264 | 122.6852 | 122.7036
2594.1562 | 122.2641 | -122.1588 | 0.11902 | -0.0096891 | 0.01884 | 0.012529 | 0.00050193 | 0.023129 | -0.0023028 | 0.0013202 | -0.0012513 | 0.052438 | 0.0097412 | -0.0061908 | 0.00055117 | 0.012232 | 0.0025528 | -0.045776 | 0.09613 | -0.086975 | -0.059509 | 0.11444 | -0.013733 | 0.004578 | -0.009155 | 0.086975 | -0.073242 | 0.027466 | 0.10986 | 0 | 0.14648 | 122.0718 | -0.022889 | -0.17853 | 122.2733 | 122.1634 | 122.1451 | 0.091553 | 0.073242 | 122.0856 | -0.032044 | -0.091553 | 122.2687 | 122.3053 | 122.1588 | 0.21973 | 0.073242 | 0.20142 | 0.027466 | 0.18311 | 0.10071 | 0.1831 | 0.16022 | 122.2549 | 122.2458 | -0.20599 | -0.19226 | 122.0993 | 122.1863 | 122.113 | 122.1497
2595.9219 | 122.3465 | -122.2275 | 0.10986 | 0.0055694 | 0.01884 | 0.011034 | -0.00035247 | 0.024624 | -0.003371 | -0.0023114 | 0.0018005 | 0.050516 | 0.010596 | -0.010891 | 0.00055117 | 0.011591 | 0.0059708 | -0.036621 | 0.10529 | -0.073242 | -0.059509 | 0.10071 | -0.036621 | 0 | -0.032043 | 0.10529 | -0.064087 | 0.004578 | 0.059509 | -0.041199 | 0.10529 | 122.1542 | -0.004577 | -0.16937 | 122.3282 | 122.2275 | 122.1909 | 0.073242 | 0.036621 | 122.1634 | -0.004577 | -0.10529 | 122.287 | 122.3328 | 122.1863 | 0.16937 | 0.022888 | 0.17395 | 0.013733 | 0.1236 | 0.068665 | 0.17853 | 0.16937 | 122.3328 | 122.3328 | -0.18311 | -0.17395 | 122.168 | 122.2321 | 122.1909 | 122.1954
2597.625 | 122.5479 | -122.3236 | 0.091553 | -0.0020601 | 0.01884 | 0.014665 | -0.0033433 | 0.022702 | 0.00047422 | 3.8448e-05 | -0.0073547 | 0.050516 | 0.0080322 | -0.0017048 | 0.0016194 | 0.014795 | 0.0016982 | -0.022888 | 0.045776 | -0.036621 | -0.009155 | 0.17853 | 0.009155 | 0.045776 | 0.064087 | 0.054932 | -0.027466 | 0.041199 | 0.13733 | 0.050354 | 0.16022 | 122.287 | -0.045777 | -0.10071 | 122.5021 | 122.3694 | 122.3328 | 0.082397 | 0.045776 | 122.2961 | -0.036621 | -0.050354 | 122.4609 | 122.4838 | 122.374 | 0.18768 | 0.07782 | 0.21515 | 0.027466 | 0.16479 | 0.068665 | 0.082397 | 0.082398 | 122.3694 | 122.3785 | -0.12817 | -0.11902 | 122.3145 | 122.3648 | 122.3007 | 122.3877
2599.4062 | 122.5571 | -122.3648 | 0.10529 | -0.0020601 | 0.017558 | 0.013811 | -0.0031297 | 0.02377 | -0.00059378 | -0.00038875 | -0.0073547 | 0.052652 | 0.009314 | -0.0051226 | -8.9634e-05 | 0.014582 | -1.0598e-05 | -0.041199 | 0.10071 | -0.086975 | -0.068665 | 0.10986 | -0.009155 | -0.009155 | 0.004578 | 0.091553 | -0.073242 | 0.004578 | 0.11444 | 0.027466 | 0.13733 | 122.2778 | -0.004578 | -0.17395 | 122.4747 | 122.3557 | 122.3557 | 0.07782 | 0.07782 | 122.2916 | -0.013733 | -0.10071 | 122.4792 | 122.5021 | 122.3923 | 0.21057 | 0.10071 | 0.19684 | 0.01831 | 0.18768 | 0.07782 | 0.18768 | 0.16479 | 122.4655 | 122.4564 | -0.19226 | -0.17853 | 122.2961 | 122.3694 | 122.3236 | 122.3694
2601.0938 | 122.5708 | -122.3831 | 0.13275 | -0.0096891 | 0.016917 | 0.011034 | -0.0016343 | 0.026761 | -0.0037982 | -0.00038875 | -0.010406 | 0.049875 | 0.0078186 | -0.008968 | 0.001192 | 0.014582 | -0.0019332 | -0.032043 | 0.10071 | -0.073242 | -0.036621 | 0.10986 | -0.027466 | 0.004578 | 0.004578 | 0.10071 | -0.059509 | 0.013733 | 0.1236 | 0.022888 | 0.15106 | 122.3099 | -0.032043 | -0.16937 | 122.493 | 122.3877 | 122.3557 | 0.07782 | 0.045776 | 122.3236 | -0.032043 | -0.11902 | 122.5067 | 122.5342 | 122.406 | 0.21057 | 0.082397 | 0.18311 | 0.036621 | 0.1831 | 0.073242 | 0.17395 | 0.16022 | 122.4838 | 122.4838 | -0.20599 | -0.19226 | 122.3465 | 122.3969 | 122.3511 | 122.3877
2602.8438 | 122.6074 | -122.4014 | 0.10986 | 0.013199 | 0.01649 | 0.012102 | 0.0013565 | 0.027188 | 0.00047422 | -0.0023114 | -0.0012513 | 0.052865 | 0.0082458 | -0.0078998 | 0.003542 | 0.014795 | -0.0006516 | -0.10071 | 0.09613 | -0.11902 | -0.11444 | 0.050354 | -0.082397 | -0.036621 | -0.068665 | 0.10071 | -0.07782 | 0.009155 | 0.086975 | -0.032043 | 0.14191 | 122.2824 | -0.013733 | -0.2243 | 122.4518 | 122.3648 | 122.319 | 0.082398 | 0.036622 | 122.3236 | -0.009155 | -0.10071 | 122.4884 | 122.5433 | 122.3694 | 0.21973 | 0.045777 | 0.16937 | 0.004578 | 0.16479 | 0.086975 | 0.21515 | 0.17853 | 122.4976 | 122.5021 | -0.22888 | -0.18768 | 122.287 | 122.4106 | 122.3007 | 122.3328
2604.5469 | 122.6624 | -122.3969 | 0.10071 | 0.0055694 | 0.014994 | 0.011888 | -0.0037705 | 0.024411 | -0.0027302 | 0.00067925 | -0.0012513 | 0.047525 | 0.0073914 | 0.0010724 | 0.00012397 | 0.012018 | -0.0008652 | -0.036621 | 0.050354 | -0.045776 | 0.022888 | 0.20142 | 0.07782 | 0.09613 | 0.050354 | 0.059509 | -0.045776 | 0.073242 | 0.17853 | 0.082397 | 0.19226 | 122.3511 | -0.050354 | -0.07782 | 122.5983 | 122.493 | 122.4747 | 0.14191 | 0.1236 | 122.3511 | -0.041199 | -0.027466 | 122.5754 | 122.5891 | 122.4792 | 0.23804 | 0.12817 | 0.24719 | 0.068664 | 0.2243 | 0.11902 | 0.09613 | 0.10528 | 122.4472 | 122.4564 | -0.14648 | -0.14648 | 122.4197 | 122.4701 | 122.3602 | 122.4472
2606.3125 | 122.5845 | -122.4243 | 0.1236 | -0.0096891 | 0.01884 | 0.011888 | -0.00099327 | 0.022702 | -0.0023028 | 0.0017474 | 0.0048523 | 0.051797 | 0.0080322 | -0.0042682 | 0.001192 | 0.012018 | -0.002147 | -0.041199 | 0.10986 | -0.073242 | -0.064087 | 0.09613 | -0.032043 | -0.009155 | -0.041199 | 0.09613 | -0.064087 | -0.009155 | 0.082397 | -0.036621 | 0.10529 | 122.3511 | -0.013733 | -0.18768 | 122.5204 | 122.4152 | 122.3923 | 0.064087 | 0.041199 | 122.3602 | -0.027466 | -0.13275 | 122.5067 | 122.5296 | 122.3877 | 0.16937 | 0.027466 | 0.16937 | 0.009155 | 0.14648 | 0.054932 | 0.18311 | 0.16022 | 122.5342 | 122.5204 | -0.19684 | -0.18768 | 122.3602 | 122.4152 | 122.3831 | 122.3831
2608.0156 | 122.7127 | -122.4152 | 0.082397 | -0.0096891 | 0.017344 | 0.010393 | -0.0046249 | 0.018857 | -0.0031574 | 0.00046565 | -0.0012513 | 0.050516 | 0.0088866 | -0.0019184 | 0.00097837 | 0.012446 | -0.0006516 | -0.045776 | 0.07782 | -0.064087 | -0.027466 | 0.15106 | 0.050354 | 0.064087 | 0.027466 | 0.050354 | -0.068665 | 0.064087 | 0.17853 | 0.10071 | 0.19226 | 122.3511 | -0.004577 | -0.10986 | 122.5662 | 122.4792 | 122.4655 | 0.12817 | 0.11444 | 122.3465 | -0.032043 | -0.01831 | 122.5937 | 122.6074 | 122.5159 | 0.26093 | 0.16937 | 0.21515 | 0.036621 | 0.24719 | 0.13275 | 0.14191 | 0.11902 | 122.493 | 122.4655 | -0.14648 | -0.15106 | 122.3877 | 122.4792 | 122.3694 | 122.4426
2609.7656 | 122.6898 | -122.4335 | 0.09613 | -0.017319 | 0.014353 | 0.012743 | -0.0024887 | 0.02142 | -0.0010212 | 0.0021746 | -0.0012513 | 0.048593 | 0.007605 | 0.00021781 | 0.0014056 | 0.013727 | -0.0006516 | -0.059509 | 0.064087 | -0.068665 | -0.050354 | 0.10529 | -0.018311 | 0.027466 | -0.027466 | 0.068665 | -0.050354 | 0.022888 | 0.11902 | 0.027466 | 0.15564 | 122.3648 | -0.032043 | -0.14648 | 122.5388 | 122.4609 | 122.4152 | 0.096131 | 0.050354 | 122.3831 | -0.027465 | -0.073242 | 122.5525 | 122.5891 | 122.4609 | 0.20599 | 0.07782 | 0.17395 | 0.018311 | 0.16937 | 0.073242 | 0.13275 | 0.11902 | 122.4976 | 122.5021 | -0.16479 | -0.14648 | 122.3831 | 122.4564 | 122.374 | 122.406
2611.5312 | 122.6257 | -122.4609 | 0.11902 | 0.0055694 | 0.017985 | 0.013384 | 0.0013565 | 0.025692 | -0.0018756 | -0.001457 | -0.0043029 | 0.053079 | 0.0088866 | -0.008327 | 0.003542 | 0.015436 | 0.0023392 | -0.064087 | 0.11444 | -0.091553 | -0.10986 | 0.032043 | -0.082397 | -0.050354 | -0.082397 | 0.1236 | -0.091553 | -0.022888 | 0.022888 | -0.059509 | 0.10986 | 122.3694 | -0.004578 | -0.22888 | 122.493 | 122.4106 | 122.3785 | 0.041199 | 0.009156 | 122.3694 | 0.004577 | -0.14191 | 122.4838 | 122.5708 | 122.4014 | 0.20142 | 0.032044 | 0.1236 | -0.01831 | 0.11444 | 0.068665 | 0.20599 | 0.21515 | 122.5754 | 122.5845 | -0.21057 | -0.21057 | 122.3511 | 122.438 | 122.3969 | 122.3785
2613.2969 | 122.6028 | -122.5204 | 0.12817 | -0.0020601 | 0.018199 | 0.012102 | 0.0015701 | 0.024411 | -0.0014484 | -0.0027386 | -0.0012513 | 0.052438 | 0.0063232 | -0.0091816 | -0.00073063 | 0.011591 | 0.0004166 | -0.082397 | 0.10529 | -0.091553 | -0.09613 | 0.059509 | -0.054932 | -0.018311 | -0.082397 | 0.10529 | -0.07782 | -0.054932 | 0.041199 | -0.054932 | 0.09613 | 122.4289 | -0.022888 | -0.2243 | 122.58 | 122.5021 | 122.4655 | 0.073242 | 0.036621 | 122.4426 | -0.022888 | -0.18311 | 122.5616 | 122.6166 | 122.4655 | 0.17395 | 0.022888 | 0.15106 | -0.004577 | 0.11902 | 0.022888 | 0.19684 | 0.18311 | 122.6257 | 122.6257 | -0.21973 | -0.20599 | 122.4243 | 122.4655 | 122.4381 | 122.4381
2615.0156 | 122.6395 | -122.4976 | 0.10071 | 0.0055694 | 0.020121 | 0.011675 | 0.0015701 | 0.022702 | -0.0029438 | 0.00089285 | 0.0018005 | 0.052225 | 0.0082458 | -0.0023456 | 0.0033282 | 0.015009 | -0.0002244 | -0.07782 | 0.10986 | -0.1236 | -0.11444 | 0.045776 | -0.086975 | -0.045776 | -0.091553 | 0.11444 | -0.07782 | -0.022888 | 0.027466 | -0.045776 | 0.10529 | 122.374 | 0.009155 | -0.21515 | 122.5433 | 122.4518 | 122.4106 | 0.07782 | 0.036621 | 122.4197 | 0.013733 | -0.1236 | 122.525 | 122.6028 | 122.4518 | 0.18311 | 0.032044 | 0.16937 | 0.009155 | 0.10529 | 0.054932 | 0.23346 | 0.19226 | 122.6074 | 122.612 | -0.2243 | -0.17853 | 122.3831 | 122.4747 | 122.4197 | 122.406
2616.7656 | 122.6303 | -122.5113 | 0.13275 | -0.0020601 | 0.017344 | 0.0095382 | -0.0020615 | 0.024197 | -0.003371 | -0.00038875 | -0.0012513 | 0.049875 | 0.007605 | -0.010036 | -0.0030804 | 0.0133 | 0.0027664 | -0.10529 | 0.10071 | -0.11444 | -0.13275 | 0.027466 | -0.054932 | -0.027466 | -0.10529 | 0.09613 | -0.07782 | -0.064087 | 0.041199 | -0.045776 | 0.07782 | 122.3969 | -0.032043 | -0.2655 | 122.5388 | 122.4838 | 122.4564 | 0.086975 | 0.059509 | 122.4335 | -0.036621 | -0.19684 | 122.5525 | 122.5891 | 122.4655 | 0.15564 | 0.032044 | 0.14191 | -0.01831 | 0.11902 | 0.013733 | 0.21515 | 0.17395 | 122.612 | 122.6074 | -0.24719 | -0.21057 | 122.3785 | 122.4472 | 122.406 | 122.406
2618.5469 | 122.7631 | -122.4518 | 0.09613 | -0.0020601 | 0.018412 | 0.010606 | -0.0029159 | 0.022061 | -0.0029438 | 0.0013202 | 0.0018005 | 0.049234 | 0.008673 | -0.0046954 | 0.00097837 | 0.012659 | -0.0027878 | 0.013733 | 0.07782 | -0.064087 | 0.022888 | 0.20599 | 0.086975 | 0.091553 | 0.064087 | 0.073242 | -0.045776 | 0.07782 | 0.21515 | 0.11444 | 0.18768 | 122.3877 | -0.01831 | -0.073242 | 122.6578 | 122.5433 | 122.5388 | 0.15564 | 0.15106 | 122.406 | -0.022888 | -0.01831 | 122.6669 | 122.6395 | 122.5662 | 0.23346 | 0.16022 | 0.27008 | 0.086975 | 0.26093 | 0.1236 | 0.14191 | 0.11902 | 122.5296 | 122.525 | -0.16022 | -0.14191 | 122.4747 | 122.5296 | 122.4655 | 122.5159
2620.2656 | 122.7814 | -122.5021 | 0.082397 | -0.0020601 | 0.016276 | 0.012102 | -0.00056607 | 0.022275 | -0.001662 | 3.8448e-05 | -0.0012513 | 0.04902 | 0.0063232 | -0.00063659 | 0.0026874 | 0.014155 | -0.0008652 | -0.036621 | 0.054932 | -0.064087 | 0.013733 | 0.19226 | 0.073242 | 0.091553 | 0.064087 | 0.07782 | -0.054932 | 0.07782 | 0.19226 | 0.10529 | 0.20142 | 122.438 | -0.027465 | -0.068664 | 122.6944 | 122.5937 | 122.5754 | 0.15564 | 0.13733 | 122.4472 | -0.004577 | -0.004577 | 122.6944 | 122.7036 | 122.6074 | 0.25635 | 0.16022 | 0.25635 | 0.07782 | 0.24719 | 0.13275 | 0.11902 | 0.13275 | 122.5571 | 122.58 | -0.14648 | -0.13733 | 122.5159 | 122.58 | 122.4655 | 122.5662
2622.0312 | 122.6532 | -122.5204 | 0.10986 | 0.0055694 | 0.017558 | 0.011461 | 0.0030655 | 0.021847 | -0.0046528 | 3.8448e-05 | -0.0012513 | 0.053293 | 0.010382 | -0.0057636 | 0.0052508 | 0.011591 | -0.003215 | -0.086975 | 0.10986 | -0.10071 | -0.10529 | 0.004578 | -0.091553 | -0.059509 | -0.10071 | 0.09613 | -0.09613 | -0.032043 | 0.013733 | -0.073242 | 0.091553 | 122.4197 | 0 | -0.21515 | 122.525 | 122.4609 | 122.4289 | 0.041199 | 0.009155 | 122.4243 | -0.013733 | -0.14191 | 122.5342 | 122.612 | 122.4472 | 0.18768 | 0.022888 | 0.10529 | -0.004578 | 0.10986 | 0.064087 | 0.21057 | 0.19226 | 122.6303 | 122.6166 | -0.21057 | -0.20599 | 122.4152 | 122.4884 | 122.4335 | 122.4197
2623.7812 | 122.7859 | -122.4838 | 0.09613 | 0.0055694 | 0.016917 | 0.011461 | 7.473e-05 | 0.020138 | -0.0029438 | -0.0012434 | -0.0012513 | 0.051584 | 0.006964 | -0.0023456 | 0.00076477 | 0.013727 | -0.0008652 | 0.009155 | 0.073242 | -0.064087 | 0.013733 | 0.21515 | 0.07782 | 0.10071 | 0.082397 | 0.068665 | -0.041199 | 0.09613 | 0.19684 | 0.11444 | 0.20142 | 122.4197 | -0.022888 | -0.082397 | 122.699 | 122.5845 | 122.5616 | 0.1648 | 0.14191 | 122.4426 | -0.027465 | 0 | 122.6807 | 122.6852 | 122.5983 | 0.24262 | 0.15564 | 0.27924 | 0.07782 | 0.23804 | 0.13733 | 0.13733 | 0.10986 | 122.5571 | 122.5525 | -0.16022 | -0.13733 | 122.4976 | 122.58 | 122.493 | 122.5662
2625.5 | 122.7905 | -122.4838 | 0.091553 | -0.0020601 | 0.01649 | 0.012315 | -0.0014207 | 0.025906 | -0.001662 | 0.0023882 | -0.0012513 | 0.050943 | 0.008673 | -0.0029864 | 0.0043964 | 0.016077 | 0.0008438 | 0 | 0.045776 | -0.036621 | 0.013733 | 0.16022 | 0.022888 | 0.036621 | 0.054932 | 0.045776 | -0.032043 | 0.091553 | 0.1831 | 0.073242 | 0.21057 | 122.4472 | -0.045777 | -0.07782 | 122.644 | 122.5204 | 122.5067 | 0.073242 | 0.059509 | 122.4518 | -0.045777 | 0 | 122.6669 | 122.6944 | 122.5571 | 0.24261 | 0.10529 | 0.19684 | 0.050354 | 0.21515 | 0.1236 | 0.082397 | 0.077819 | 122.5296 | 122.5296 | -0.12817 | -0.1236 | 122.4976 | 122.5754 | 122.4838 | 122.5388
2627.25 | 122.7356 | -122.5021 | 0.10529 | 0.0055694 | 0.019053 | 0.01082 | -0.0020615 | 0.021634 | -0.0018756 | -0.00017515 | 0.0018005 | 0.049447 | 0.0078186 | -0.00085019 | 0.002901 | 0.013727 | -0.000438 | -0.059509 | 0.07782 | -0.068665 | -0.054932 | 0.10986 | -0.009155 | 0.022888 | -0.013733 | 0.082397 | -0.068665 | 0.022888 | 0.10529 | 0.018311 | 0.13733 | 122.4335 | -0.027466 | -0.16022 | 122.612 | 122.525 | 122.493 | 0.091553 | 0.05951 | 122.4335 | -0.022889 | -0.082398 | 122.6074 | 122.6395 | 122.5204 | 0.20599 | 0.086976 | 0.17853 | 0.013733 | 0.17395 | 0.091553 | 0.14649 | 0.15106 | 122.58 | 122.5845 | -0.17395 | -0.17395 | 122.4472 | 122.525 | 122.4426 | 122.4884
2628.9531 | 122.7264 | -122.525 | 0.11902 | 0.0055694 | 0.019267 | 0.012529 | -0.00099327 | 0.023129 | -0.0012348 | -0.0016706 | -0.0043029 | 0.053293 | 0.010168 | 0.00043161 | 0.0026874 | 0.011805 | -0.0012924 | -0.050354 | 0.091553 | -0.082397 | -0.068665 | 0.068665 | -0.036621 | 0 | -0.036621 | 0.10071 | -0.07782 | 0.004578 | 0.091553 | 0.009155 | 0.14648 | 122.4426 | -0.027466 | -0.18768 | 122.5937 | 122.525 | 122.4884 | 0.082397 | 0.045776 | 122.4472 | -0.018311 | -0.11444 | 122.6166 | 122.6715 | 122.5342 | 0.2243 | 0.086975 | 0.15106 | 0.013732 | 0.16937 | 0.082398 | 0.17395 | 0.17853 | 122.6166 | 122.6257 | -0.20142 | -0.19684 | 122.4564 | 122.5296 | 122.4747 | 122.4884
2630.7188 | 122.8134 | -122.493 | 0.082397 | 0.013199 | 0.014781 | 0.012102 | -0.0031297 | 0.022915 | -0.003371 | 3.8448e-05 | -0.0012513 | 0.04902 | 0.0080322 | -0.002132 | -0.0011578 | 0.013086 | 0.001912 | -0.022888 | 0.073242 | -0.064087 | 0.013733 | 0.21057 | 0.073242 | 0.09613 | 0.073242 | 0.073242 | -0.050354 | 0.082397 | 0.19684 | 0.10071 | 0.20599 | 122.4289 | -0.009155 | -0.068664 | 122.7036 | 122.5891 | 122.5662 | 0.16022 | 0.13733 | 122.4426 | -0.009155 | 0 | 122.6898 | 122.699 | 122.5937 | 0.25635 | 0.15106 | 0.27466 | 0.07782 | 0.24719 | 0.13275 | 0.13733 | 0.1236 | 122.5662 | 122.5662 | -0.14648 | -0.13275 | 122.5067 | 122.5754 | 122.4701 | 122.5662
2632.4844 | 122.6898 | -122.5113 | 0.11902 | 0.013199 | 0.018626 | 0.013384 | 0.00050193 | 0.025479 | -0.0029438 | 0.00046565 | 0.0018005 | 0.052438 | 0.0091002 | -0.0068316 | 0.001833 | 0.015864 | 0.0008438 | -0.082397 | 0.11444 | -0.10986 | -0.1236 | 0.027466 | -0.09613 | -0.050354 | -0.09613 | 0.10986 | -0.07782 | -0.032043 | 0.022888 | -0.064087 | 0.11902 | 122.4014 | -0.004578 | -0.24261 | 122.5388 | 122.4609 | 122.4152 | 0.059509 | 0.013733 | 122.4335 | -0.009156 | -0.15106 | 122.5342 | 122.6303 | 122.4472 | 0.19684 | 0.013733 | 0.13733 | -0.013733 | 0.10071 | 0.045777 | 0.2243 | 0.18768 | 122.6257 | 122.6212 | -0.22888 | -0.19684 | 122.3877 | 122.4792 | 122.4289 | 122.4152
2634.2344 | 122.8271 | -122.5021 | 0.086975 | 0.013199 | 0.016062 | 0.014452 | -0.00056607 | 0.022915 | -0.00080758 | -0.00060235 | -0.010406 | 0.050943 | 0.006964 | -0.00085019 | 0.0041828 | 0.0133 | -0.001506 | -0.004578 | 0.036621 | -0.045776 | 0.009155 | 0.16937 | 0.018311 | 0.064087 | 0.068665 | 0.041199 | -0.041199 | 0.091553 | 0.19226 | 0.082397 | 0.20142 | 122.4564 | -0.050354 | -0.07782 | 122.6715 | 122.5662 | 122.5204 | 0.10986 | 0.064087 | 122.4609 | -0.045776 | 0.004578 | 122.6944 | 122.7036 | 122.5845 | 0.24262 | 0.1236 | 0.21515 | 0.054931 | 0.23346 | 0.13275 | 0.082397 | 0.082398 | 122.5388 | 122.5433 | -0.13275 | -0.12817 | 122.5113 | 122.5937 | 122.4976 | 122.5708
2635.9844 | 122.8043 | -122.4976 | 0.073242 | 0.013199 | 0.017131 | 0.013811 | 0.00092933 | 0.028897 | -0.00016658 | 0.0015338 | 0.0048523 | 0.05137 | 0.0095276 | -0.008327 | 0.0056782 | 0.015436 | 0.0010574 | 0.009155 | 0.073242 | -0.064087 | 0.022888 | 0.17853 | 0.045776 | 0.064087 | 0.068665 | 0.041199 | -0.013733 | 0.10986 | 0.17853 | 0.073242 | 0.21057 | 122.4335 | 0 | -0.050354 | 122.6761 | 122.5616 | 122.5433 | 0.12817 | 0.10986 | 122.4838 | -0.032043 | 0.036621 | 122.6761 | 122.7081 | 122.5708 | 0.2243 | 0.086975 | 0.24261 | 0.086975 | 0.19226 | 0.1236 | 0.13733 | 0.054932 | 122.5708 | 122.5388 | -0.13733 | -0.086975 | 122.5204 | 122.6074 | 122.5067 | 122.5662
2637.7344 | 122.8134 | -122.5113 | 0.07782 | 0.0055694 | 0.016917 | 0.016161 | -0.0016343 | 0.022915 | -0.00059378 | 3.8448e-05 | 0.0018005 | 0.052011 | 0.0073914 | 0.00043161 | 0.0041828 | 0.016077 | -0.0010788 | -0.032043 | 0.073242 | -0.068665 | 0 | 0.15564 | 0.022888 | 0.041199 | 0.059509 | 0.073242 | -0.032043 | 0.091553 | 0.15564 | 0.059509 | 0.21057 | 122.4426 | -0.004578 | -0.07782 | 122.6669 | 122.5525 | 122.5342 | 0.10986 | 0.091553 | 122.4792 | -0.004578 | 0.013733 | 122.6669 | 122.7219 | 122.5708 | 0.24261 | 0.091552 | 0.22431 | 0.068665 | 0.18768 | 0.1236 | 0.14191 | 0.10529 | 122.5845 | 122.5845 | -0.14649 | -0.10986 | 122.5113 | 122.6028 | 122.4792 | 122.5708
2639.4375 | 122.7264 | -122.5571 | 0.10986 | 0.0055694 | 0.018412 | 0.0093246 | 7.473e-05 | 0.023129 | -0.00080758 | -0.00038875 | -0.0012513 | 0.05372 | 0.009314 | -0.0093952 | 0.0033282 | 0.013514 | 0.0023392 | -0.068665 | 0.09613 | -0.10529 | -0.11444 | 0.032043 | -0.091553 | -0.059509 | -0.064087 | 0.10986 | -0.082397 | -0.032043 | 0.036621 | -0.050354 | 0.091553 | 122.4518 | -0.013733 | -0.2243 | 122.5891 | 122.4976 | 122.4655 | 0.045777 | 0.013733 | 122.4747 | 0 | -0.14191 | 122.5937 | 122.6486 | 122.5067 | 0.17395 | 0.032043 | 0.13733 | -0.009155 | 0.11902 | 0.050354 | 0.20142 | 0.19226 | 122.6532 | 122.6669 | -0.21515 | -0.19226 | 122.4426 | 122.525 | 122.4884 | 122.493
2641.1875 | 122.7356 | -122.5616 | 0.10071 | 0.0055694 | 0.017771 | 0.012315 | -0.0027023 | 0.02612 | -0.00038018 | 0.00067925 | -0.0012513 | 0.052438 | 0.010168 | -0.0098224 | 0.00033757 | 0.013727 | 0.0040482 | -0.045776 | 0.10529 | -0.082397 | -0.032043 | 0.1236 | -0.022888 | -0.013733 | -0.009155 | 0.10071 | -0.073242 | 0 | 0.073242 | -0.009155 | 0.12817 | 122.4792 | 0.004578 | -0.13275 | 122.6852 | 122.5479 | 122.5388 | 0.068664 | 0.059509 | 122.4884 | 0 | -0.10071 | 122.6349 | 122.6898 | 122.5525 | 0.20142 | 0.064087 | 0.20599 | 0.050354 | 0.14648 | 0.073242 | 0.18768 | 0.17395 | 122.6669 | 122.6624 | -0.18311 | -0.17395 | 122.5296 | 122.5616 | 122.5159 | 122.5525

## Thermal Data
Fire Time | B Position - Conduit - 3' | B Position - Conduit - Middle | B Position - Conduit - 7' | D Position - 3' | D Position - Middle | D Position - 7'
-0.8083 | 9.0418 | 9.0827 | 9.0338 | 8.9801 | 8.8903 | 8.7706
0.1917 | 9.0326 | 9.0883 | 9.0395 | 8.9824 | 8.9101 | 8.6704
1.1917 | 9.0406 | 9.0923 | 9.0391 | 8.9871 | 8.8923 | 8.7554
2.1917 | 9.038 | 9.0882 | 9.0444 | 8.9876 | 8.9006 | 8.6466
3.1917 | 9.0461 | 9.0891 | 9.0451 | 8.9842 | 8.892 | 8.7771
4.1917 | 9.0496 | 9.1008 | 9.063 | 8.9927 | 9.1181 | 8.7013
5.1917 | 9.0505 | 9.1569 | 9.061 | 8.9246 | 9.7293 | 8.6732
6.1917 | 9.0555 | 9.434 | 9.1195 | 9.3969 | 11.4504 | 10.8215
7.1917 | 9.0662 | 9.5427 | 9.2013 | 11.241 | 12.1623 | 12.5965
8.1917 | 9.1331 | 9.8888 | 9.4058 | 12.0694 | 13.7864 | 13.8884
9.1917 | 9.2338 | 9.9792 | 9.7171 | 13.169 | 15.7478 | 14.9483
10.1917 | 9.3692 | 10.234 | 9.9832 | 14.6063 | 17.4639 | 16.1391
11.2073 | 9.3484 | 10.6679 | 10.0109 | 15.8514 | 20.2518 | 17.8872
12.1917 | 9.4196 | 10.6108 | 10.279 | 16.978 | 23.137 | 19.4645
13.1917 | 9.6674 | 10.7289 | 10.3324 | 18.2246 | 26.4006 | 21.5435
14.1917 | 9.6677 | 11.0427 | 10.5955 | 20.0581 | 30.9676 | 22.9447
15.1917 | 9.6731 | 11.1147 | 11.0597 | 22.2632 | 33.6456 | 23.7639
16.1917 | 9.8808 | 11.4218 | 10.8126 | 24.0299 | 36.8677 | 24.9382
17.1917 | 9.8852 | 11.5443 | 11.0401 | 25.2638 | 39.414 | 26.5563
18.1917 | 9.838 | 11.9797 | 11.1328 | 26.6451 | 42.6523 | 27.2002
19.1917 | 9.9971 | 12.3548 | 11.2255 | 28.4203 | 45.4962 | 28.8222
20.1917 | 10.1108 | 12.36 | 11.3791 | 30.9098 | 48.2634 | 30.3932
21.1917 | 10.1617 | 12.7074 | 11.7034 | 32.653 | 51.2442 | 32.0564
22.1917 | 10.3305 | 12.6562 | 11.6796 | 34.3921 | 53.3712 | 33.8226
23.1917 | 10.3406 | 12.6792 | 12.0165 | 35.7824 | 54.9264 | 35.4952
24.1917 | 10.32 | 13.0591 | 12.0327 | 38.1943 | 57.9454 | 37.6733
25.1917 | 10.3557 | 13.496 | 12.1605 | 40.843 | 62.1353 | 40.0453
26.1917 | 10.5186 | 13.5213 | 12.498 | 42.0897 | 65.104 | 42.3061
27.1917 | 10.6361 | 13.7482 | 12.4009 | 44.9757 | 68.7381 | 44.1135
28.1917 | 10.9905 | 13.822 | 12.6198 | 47.9028 | 72.7206 | 46.6029
29.1917 | 11.0251 | 13.9978 | 12.856 | 50.1968 | 77.6192 | 50.2151
30.1917 | 11.028 | 14.4194 | 12.8262 | 52.7918 | 81.6344 | 53.7105
31.1917 | 11.2303 | 14.7831 | 12.7999 | 54.744 | 84.4922 | 56.5614
32.1917 | 11.0476 | 15.0224 | 13.015 | 56.3035 | 88.0779 | 59.1174
33.1917 | 10.9801 | 15.1415 | 13.3633 | 57.7393 | 91.6721 | 61.349
34.1917 | 11.0077 | 15.7076 | 13.3882 | 60.1591 | 94.1967 | 64.0523
35.1917 | 11.2226 | 15.7807 | 13.714 | 60.6883 | 96.5079 | 65.6132
36.1917 | 11.319 | 16.0418 | 13.864 | 61.3881 | 98.576 | 67.6505
37.1917 | 11.3604 | 16.064 | 14.2577 | 61.8915 | 100.9796 | 69.3839
38.1917 | 11.6139 | 16.4366 | 14.3964 | 62.7837 | 102.6784 | 70.7959
39.1917 | 11.7467 | 16.6459 | 14.1999 | 64.6343 | 105.0114 | 72.5878
40.1917 | 11.8427 | 16.9963 | 14.66 | 66.7528 | 107.0789 | 74.1051
41.2073 | 12.1713 | 17.2574 | 14.7086 | 67.5869 | 108.5021 | 75.7625
42.1917 | 12.2165 | 17.7439 | 14.7997 | 70.6668 | 110.0312 | 77.2893
43.1917 | 12.273 | 17.9347 | 14.8981 | 73.3156 | 111.7312 | 78.7495
44.1917 | 12.2591 | 18.2984 | 15.1261 | 74.9074 | 113.4802 | 79.9101
45.1917 | 12.0615 | 18.3115 | 15.6279 | 76.6576 | 114.1526 | 80.0324
46.1917 | 12.2085 | 18.3645 | 15.6791 | 78.9171 | 114.2108 | 81.1325
47.1917 | 12.4539 | 18.6591 | 15.9324 | 79.7837 | 116.1642 | 82.9816
48.1917 | 12.7312 | 18.8262 | 16.2217 | 80.5114 | 117.5167 | 84.9271
49.1917 | 12.7249 | 19.4263 | 16.5201 | 82.0278 | 118.8344 | 85.747
50.1917 | 12.3812 | 19.7762 | 16.3269 | 84.8124 | 119.7534 | 85.9209
51.1917 | 12.2822 | 20.3313 | 16.5221 | 86.2489 | 120.017 | 86.7725
52.1917 | 12.9151 | 20.2865 | 16.7473 | 86.8829 | 120.5555 | 87.2906
53.1917 | 12.9245 | 20.983 | 16.9824 | 88.1511 | 121.0581 | 88.1125
54.1917 | 12.7778 | 21.1605 | 17.156 | 88.7559 | 120.9315 | 88.7133
55.1917 | 12.7228 | 21.5552 | 17.5462 | 89.0926 | 121.6042 | 89.4405
56.1917 | 12.9094 | 21.9393 | 17.4486 | 89.4169 | 122.8682 | 90.1299
57.1917 | 12.7385 | 22.4759 | 17.5269 | 89.546 | 124.3169 | 91.3367
58.1917 | 12.8371 | 22.8242 | 17.814 | 89.4269 | 125.0021 | 92.7591
59.1917 | 12.9611 | 22.9461 | 18.1 | 90.3593 | 125.0599 | 93.7926
60.1917 | 13.152 | 23.1093 | 18.1187 | 91.739 | 126.1198 | 94.8902
61.1917 | 13.4314 | 23.7937 | 18.1937 | 92.5231 | 127.34 | 96.175
62.1917 | 13.4872 | 23.9996 | 18.3363 | 93.1489 | 127.9448 | 97.5855
63.1917 | 13.8012 | 24.2673 | 18.5554 | 93.3301 | 127.5882 | 98.0199
64.1917 | 13.8717 | 24.5005 | 18.6241 | 94.4183 | 128.0564 | 98.1998
65.1917 | 13.9842 | 24.8046 | 18.6303 | 94.7215 | 129.018 | 98.6864
66.1917 | 14.0219 | 25.1923 | 18.751 | 96.3295 | 131.3831 | 100.4415
67.1917 | 14.0782 | 25.2353 | 18.73 | 97.3556 | 133.0746 | 103.2104
68.1917 | 14.0923 | 25.5437 | 18.8074 | 98.7178 | 135.3162 | 105.2096
69.2073 | 14.3574 | 26.1312 | 19.0499 | 101.1404 | 138.3439 | 108.098
70.1917 | 14.2675 | 26.2916 | 19.1655 | 102.5248 | 139.8528 | 110.4844
71.1917 | 14.2831 | 26.8321 | 19.3781 | 103.8903 | 141.0168 | 111.7611
72.1917 | 14.427 | 27.2585 | 19.69 | 103.9729 | 141.636 | 112.2767
73.1917 | 14.72 | 27.5841 | 19.6776 | 104.3276 | 142.8881 | 113.6169
74.1917 | 14.5175 | 27.881 | 19.7622 | 104.7191 | 143.5312 | 114.9342
75.1917 | 14.6306 | 28.4167 | 19.981 | 106.5558 | 143.7339 | 116.1959
76.1917 | 14.5504 | 28.5788 | 20.1251 | 107.647 | 144.6525 | 116.4752
77.1917 | 14.9799 | 28.9429 | 20.4751 | 108.1556 | 146.017 | 117.4314
78.1917 | 14.7804 | 29.6045 | 20.6187 | 108.6177 | 145.6732 | 118.5716
79.1917 | 14.7441 | 29.8934 | 20.7619 | 109.424 | 145.5557 | 118.5573
80.1917 | 15.2091 | 30.5881 | 20.96 | 109.9796 | 146.8177 | 119.7383
81.1917 | 15.2016 | 31.0416 | 20.8936 | 110.3829 | 147.8442 | 120.3653
82.1917 | 15.1277 | 31.1723 | 21.1149 | 111.5384 | 148.0574 | 121.9099
83.1917 | 15.5709 | 31.9764 | 21.2893 | 111.8561 | 148.9515 | 122.727
84.1917 | 15.5555 | 32.1618 | 21.4046 | 112.4691 | 148.8453 | 123.9151
85.1917 | 15.5586 | 32.4351 | 21.5844 | 112.8825 | 148.5503 | 124.6102
86.1917 | 15.8336 | 33.2687 | 21.6021 | 113.4761 | 148.5471 | 124.6797
87.1917 | 15.9065 | 33.2097 | 21.7619 | 114.1542 | 149.3483 | 124.4343
88.1917 | 15.9212 | 33.4747 | 21.8095 | 115.3159 | 151.6069 | 126.1118
89.1917 | 15.9537 | 33.7952 | 22.3004 | 118.5063 | 153.8452 | 128.2452
90.1917 | 16.1351 | 34.2977 | 22.7003 | 119.4841 | 153.8057 | 130.4695
91.1917 | 16.1903 | 34.8391 | 22.6354 | 121.007 | 155.0319 | 130.6501
92.1917 | 16.0803 | 35.1636 | 22.9443 | 121.5069 | 155.9397 | 130.4385
93.2073 | 16.3836 | 35.5038 | 22.8247 | 123.6342 | 157.1357 | 130.2847
94.1917 | 16.4821 | 35.7173 | 23.1698 | 123.0694 | 158.2676 | 133.2321
95.1917 | 16.5002 | 36.1057 | 23.1417 | 126.015 | 159.1858 | 135.0372
96.1917 | 16.5069 | 36.3822 | 23.5061 | 127.6665 | 160.9877 | 135.053
97.2073 | 16.4741 | 36.761 | 23.3303 | 129.2766 | 161.761 | 135.7472
98.1917 | 16.5933 | 37.2115 | 23.3689 | 129.5567 | 163.3789 | 136.0904
99.2073 | 16.5743 | 37.6507 | 23.9292 | 130.3551 | 164.2892 | 136.524
100.1917 | 16.6842 | 38.0155 | 24.0709 | 129.5135 | 164.8007 | 138.1699
101.1917 | 17.1535 | 38.4094 | 24.0752 | 129.9669 | 165.5657 | 139.438
102.1917 | 17.3096 | 38.8281 | 24.0861 | 130.1374 | 165.9321 | 140.3422
103.1917 | 17.1396 | 39.1269 | 24.2571 | 131.7988 | 167.2767 | 141.828
104.1917 | 17.0204 | 39.4224 | 24.3759 | 132.153 | 167.8986 | 142.1128
105.1917 | 17.1061 | 39.8273 | 24.4652 | 132.3693 | 167.9252 | 141.6638
106.1917 | 17.3138 | 40.0548 | 24.549 | 132.5214 | 168.7778 | 141.3884
107.1917 | 17.2178 | 40.4104 | 24.7263 | 131.8503 | 169.0472 | 141.2631
108.1917 | 17.316 | 40.9035 | 24.9146 | 131.287 | 169.3749 | 141.0522
109.1917 | 17.2668 | 41.2751 | 25.2289 | 131.4642 | 169.5097 | 140.3708
110.1917 | 17.3091 | 41.688 | 25.2787 | 131.4872 | 170.4406 | 140.6141
111.1917 | 17.7232 | 42.0552 | 25.3222 | 132.9894 | 172.0741 | 141.303
112.1917 | 17.7664 | 42.5629 | 25.5336 | 132.8666 | 173.4935 | 141.6897
113.1917 | 17.9149 | 43.269 | 25.7307 | 132.7944 | 174.2153 | 142.7681
114.1917 | 18.2795 | 43.8882 | 25.7917 | 133.3202 | 173.4351 | 142.1912
115.1917 | 18.3669 | 44.1075 | 25.9805 | 133.3464 | 173.8267 | 142.2542
116.1917 | 18.2521 | 44.7186 | 26.0128 | 132.8907 | 173.5166 | 143.3984
117.1917 | 18.1485 | 45.0209 | 26.1554 | 132.461 | 173.4732 | 143.5127
118.1917 | 18.4632 | 45.5366 | 26.359 | 132.9167 | 173.8016 | 144.5129
119.1917 | 18.5009 | 46.0335 | 26.4793 | 133.7176 | 174.637 | 145.2885
120.1917 | 18.8053 | 46.3682 | 26.649 | 136.1426 | 175.4846 | 145.4718
121.1917 | 18.8311 | 46.8309 | 26.7502 | 136.9615 | 175.6234 | 145.9342
122.1917 | 18.6927 | 47.2181 | 26.95 | 136.3593 | 175.3639 | 147.273
123.1917 | 19.0576 | 47.6105 | 27.0014 | 136.0026 | 176.439 | 147.2251
124.1917 | 19.255 | 47.9937 | 27.1885 | 135.3829 | 176.2172 | 148.1452
125.1917 | 19.0798 | 48.3061 | 27.4426 | 136.1735 | 176.384 | 147.5768
126.1917 | 19.3106 | 48.7429 | 27.4879 | 135.544 | 177.0677 | 147.2867
127.1917 | 19.2723 | 49.5046 | 27.6946 | 137.2536 | 178.562 | 147.1953
128.1917 | 19.2497 | 49.868 | 27.9194 | 136.7949 | 179.255 | 148.1504
129.1917 | 19.3889 | 50.3245 | 27.8466 | 136.8775 | 180.5261 | 149.7576
130.1917 | 19.5823 | 50.7131 | 27.8806 | 136.3071 | 179.8883 | 150.8573
131.1917 | 19.6592 | 51.0596 | 28.4159 | 136.3547 | 179.3865 | 150.2804
132.1917 | 19.7237 | 51.6144 | 28.4678 | 135.8897 | 179.9644 | 151.0373
133.1917 | 19.7751 | 52.0153 | 28.5844 | 135.5336 | 180.3279 | 151.6831
134.1917 | 20.0004 | 52.6323 | 28.892 | 136.0836 | 180.2428 | 151.8632
135.1917 | 19.9664 | 53.1669 | 28.8787 | 136.3569 | 179.5521 | 152.6469
136.1917 | 20.1184 | 53.5211 | 29.0663 | 136.7322 | 179.226 | 152.6068
137.1917 | 20.3236 | 53.7859 | 29.0823 | 136.9047 | 178.8396 | 152.6575
138.1917 | 20.3336 | 54.4247 | 29.1744 | 136.6788 | 178.679 | 152.7363
139.1917 | 20.4244 | 54.7214 | 29.2675 | 135.8666 | 178.042 | 153.4455
140.1917 | 20.5574 | 55.1375 | 29.3729 | 135.9973 | 177.6437 | 154.7181
141.1917 | 20.8016 | 55.481 | 29.5953 | 136.4982 | 178.6595 | 155.6659
142.1917 | 20.8268 | 55.8124 | 29.6626 | 137.281 | 177.9907 | 155.5491
143.1917 | 20.8653 | 56.5853 | 29.7973 | 137.1731 | 177.404 | 156.0399
144.1917 | 20.7958 | 56.838 | 29.9219 | 136.6428 | 177.8808 | 157.2516
145.1917 | 20.836 | 57.2897 | 29.9243 | 136.6507 | 178.1372 | 157.5603
146.1917 | 21.142 | 57.5647 | 30.148 | 136.2933 | 178.4485 | 159.2131
147.1917 | 21.0652 | 57.9815 | 30.1827 | 135.6242 | 178.9311 | 159.5351
148.1917 | 21.1339 | 58.7323 | 30.5605 | 135.7232 | 179.5555 | 160.8352
149.1917 | 21.2013 | 59.0852 | 30.7778 | 136.8407 | 179.4444 | 163.5512
150.1917 | 21.2715 | 59.9101 | 30.9504 | 137.6166 | 180.3528 | 163.4644
151.1917 | 21.4036 | 60.1878 | 30.9826 | 137.6376 | 181.934 | 163.9199
152.1917 | 21.6674 | 60.8047 | 31.2515 | 137.969 | 182.2902 | 164.9309
153.1917 | 22.0442 | 61.1513 | 31.3296 | 138.025 | 181.9646 | 164.9173
154.1917 | 21.8425 | 61.5456 | 31.5721 | 137.7745 | 181.539 | 164.6672
155.1917 | 21.8225 | 62.3809 | 31.6448 | 137.5051 | 181.1796 | 165.0691
156.1917 | 22.0165 | 62.7478 | 31.746 | 136.7486 | 180.3966 | 164.2458
157.1917 | 22.1933 | 63.1814 | 31.9112 | 136.8654 | 179.9262 | 164.4408
158.1917 | 22.328 | 63.5788 | 31.9753 | 136.2191 | 179.271 | 164.7927
159.1917 | 22.2361 | 64.0789 | 32.0647 | 137.0179 | 179.8963 | 165.7133
160.1917 | 22.5161 | 64.8668 | 32.3504 | 137.4307 | 179.9611 | 167.0459
161.1917 | 22.6342 | 64.9751 | 32.3133 | 136.2149 | 179.2954 | 167.402
162.2073 | 22.8171 | 65.4397 | 32.5688 | 136.0029 | 180.0122 | 167.6173
163.1917 | 22.7297 | 66.0769 | 32.7412 | 136.0127 | 179.957 | 167.9109
164.1917 | 22.9513 | 66.6566 | 32.8374 | 135.2098 | 180.3719 | 167.2595
165.1917 | 22.967 | 66.8869 | 32.9046 | 135.5676 | 179.5281 | 166.8504
166.1917 | 23.3044 | 67.5208 | 32.9346 | 135.883 | 178.4347 | 166.6463
167.1917 | 23.2919 | 67.9167 | 33.2348 | 135.7784 | 177.8209 | 166.5157
168.1917 | 23.2194 | 69.0227 | 33.4501 | 135.8322 | 177.0771 | 166.4732
169.1917 | 23.5128 | 69.1512 | 33.4957 | 135.4477 | 177.0624 | 165.6227
170.1917 | 23.6623 | 69.9439 | 33.6455 | 135.9887 | 178.191 | 165.3368
171.1917 | 23.566 | 70.2666 | 33.8603 | 135.9541 | 178.7023 | 164.4515
172.1917 | 23.4249 | 70.5701 | 34.0605 | 135.4017 | 178.6998 | 164.5132
173.1917 | 23.5098 | 70.8965 | 34.4096 | 136.3256 | 178.9941 | 164.9131
174.1917 | 23.7749 | 71.3388 | 34.3754 | 137.8097 | 179.7071 | 165.5147
175.1917 | 23.7585 | 71.7494 | 34.4092 | 139.2603 | 180.3398 | 167.0367
176.1917 | 23.7955 | 72.4958 | 34.6683 | 139.1395 | 180.8971 | 167.905
177.1917 | 23.8637 | 72.7714 | 34.6846 | 139.0539 | 180.4988 | 167.847
178.1917 | 23.8365 | 73.3016 | 34.8628 | 138.7813 | 180.7397 | 168.4273
179.1917 | 23.9579 | 73.5283 | 35.0471 | 138.9876 | 180.649 | 169.7188
180.1917 | 24.1931 | 74.0294 | 35.2591 | 138.4978 | 180.7927 | 169.7474
181.1917 | 24.383 | 74.4364 | 35.2615 | 139.5685 | 180.5125 | 170.0577
182.1917 | 24.4317 | 74.9028 | 35.5581 | 138.7802 | 180.9882 | 170.7788
183.1917 | 24.5142 | 75.5244 | 35.6028 | 140.4478 | 180.8834 | 171.0593
184.1917 | 24.419 | 76.0794 | 35.5593 | 140.4653 | 181.4144 | 171.3819
185.1917 | 24.7123 | 76.9277 | 35.8328 | 139.3352 | 180.6837 | 171.5591
186.1917 | 24.8051 | 77.4104 | 36.0982 | 138.8226 | 180.9245 | 171.1247
187.1917 | 24.8272 | 77.5728 | 36.1736 | 138.6364 | 180.8991 | 170.6817
188.1917 | 25.2003 | 78.086 | 36.2133 | 138.5958 | 180.0759 | 170.8764
189.1917 | 25.4313 | 78.6243 | 36.3389 | 138.8307 | 180.656 | 169.8316
190.1917 | 25.333 | 79.1118 | 36.7342 | 138.5733 | 180.6428 | 169.5291
191.1917 | 25.2197 | 79.6624 | 36.9711 | 138.6432 | 181.143 | 169.7927
192.1917 | 25.3624 | 80.0283 | 36.9454 | 138.6279 | 181.4613 | 169.4761
193.1917 | 25.6807 | 80.6116 | 36.994 | 138.8779 | 181.1741 | 169.1771
194.1917 | 25.7909 | 81.0829 | 37.2506 | 139.179 | 180.1519 | 168.1703
195.1917 | 25.9425 | 81.6116 | 37.1869 | 138.5482 | 179.2724 | 167.9817
196.1917 | 26.0634 | 82.1568 | 37.3044 | 138.3311 | 179.1108 | 168.473
197.1917 | 26.0989 | 82.6164 | 37.5346 | 138.4349 | 178.9222 | 168.7654
198.1917 | 26.2304 | 82.9656 | 37.6587 | 138.8528 | 179.1094 | 168.4975
199.1917 | 26.26 | 83.7598 | 37.818 | 139.3572 | 179.9304 | 168.1298
200.1917 | 26.6422 | 84.0764 | 37.9669 | 140.1313 | 181.3672 | 167.7845
201.1917 | 26.6961 | 84.6286 | 38.1374 | 139.8026 | 181.363 | 168.8299
202.1917 | 26.7746 | 85.1815 | 38.229 | 139.4862 | 181.483 | 168.8851
203.1917 | 26.7939 | 85.9423 | 38.3935 | 138.6915 | 180.9757 | 168.8782
204.1917 | 27.0566 | 85.9898 | 38.4374 | 138.8383 | 180.2247 | 167.887
205.1917 | 27.127 | 86.5321 | 38.6282 | 138.5366 | 180.1747 | 168.2587
206.1917 | 27.2779 | 87.0762 | 38.7579 | 138.6587 | 179.2043 | 168.249
207.1917 | 27.2937 | 87.5826 | 38.9157 | 138.7153 | 178.7027 | 167.6261
208.1917 | 27.5752 | 87.8866 | 39.0074 | 138.1074 | 177.9282 | 166.9798
209.1917 | 27.8289 | 88.6201 | 39.2455 | 138.1333 | 177.2084 | 165.9891
210.1917 | 28.1601 | 89.0601 | 39.3297 | 137.944 | 176.8214 | 165.7884
211.1917 | 28.2434 | 89.5106 | 39.4584 | 137.3841 | 175.7491 | 165.0551
212.1917 | 28.3271 | 90.1812 | 39.8885 | 137.2997 | 176.5527 | 164.4844
213.1917 | 28.253 | 90.6469 | 40.0652 | 137.1662 | 176.7057 | 164.0796
214.1917 | 28.2342 | 91.1359 | 40.0818 | 137.5566 | 176.1574 | 163.5071
215.1917 | 28.3586 | 91.6634 | 40.3938 | 137.8435 | 175.9873 | 163.1112
216.1917 | 28.5511 | 92.3027 | 40.5521 | 137.897 | 176.458 | 162.5964
217.1917 | 28.6191 | 92.72 | 40.6089 | 138.8757 | 177.0045 | 162.4725
218.1917 | 28.8265 | 93.1516 | 40.6476 | 139.3057 | 177.1422 | 161.9999
219.1917 | 28.9349 | 93.557 | 40.9013 | 139.439 | 176.8718 | 161.5243
220.1917 | 29.2626 | 94.1816 | 41.1075 | 139.0649 | 176.8898 | 163.0828
221.1917 | 29.3593 | 94.9272 | 41.2207 | 139.4319 | 176.7128 | 162.9456
222.1917 | 29.2525 | 95.4272 | 41.4674 | 139.8681 | 177.4318 | 162.5889
223.1917 | 29.3587 | 96.0744 | 41.6052 | 139.2599 | 177.6498 | 162.7363
224.1917 | 29.2937 | 96.6308 | 42.0646 | 138.9566 | 177.3335 | 162.2976
225.1917 | 29.4769 | 97.1133 | 41.9793 | 139.8389 | 177.5042 | 162.8335
226.1917 | 29.6175 | 97.6232 | 42.0869 | 140.805 | 177.4184 | 163.5792
227.1917 | 29.6988 | 98.0619 | 42.2278 | 142.1838 | 177.7599 | 163.0968
228.1917 | 29.8534 | 98.5452 | 42.4628 | 143.0298 | 179.1312 | 163.7113
229.1917 | 30.1397 | 99.106 | 42.3702 | 142.9188 | 179.6881 | 165.3338
230.1917 | 30.1499 | 99.8857 | 42.5324 | 143.3198 | 181.1141 | 165.8347
231.1917 | 30.1975 | 100.1593 | 42.5771 | 142.9134 | 180.1412 | 165.5224
232.1917 | 30.4481 | 100.6906 | 42.792 | 143.3041 | 179.6852 | 165.1099
233.1917 | 30.3299 | 101.2643 | 42.9445 | 144.1385 | 180.6137 | 165.0854
234.1917 | 30.3634 | 101.8411 | 43.2247 | 144.2372 | 181.1175 | 165.5576
235.1917 | 30.5341 | 102.2942 | 43.2176 | 144.0415 | 181.826 | 166.5512
236.1917 | 31.0922 | 102.6821 | 43.3354 | 144.2315 | 182.274 | 167.1703
237.1917 | 31.3488 | 103.1268 | 43.4991 | 144.8953 | 183.3321 | 168.0927
238.1917 | 31.4419 | 103.6235 | 43.6546 | 144.7773 | 184.7284 | 169.6756
239.1917 | 31.4834 | 104.3332 | 43.8033 | 145.5306 | 185.9227 | 171.7332
240.1917 | 31.5618 | 104.7361 | 43.9728 | 145.0821 | 185.928 | 171.749
241.1917 | 31.5427 | 105.1893 | 44.0992 | 145.2601 | 186.1275 | 171.6797
242.1917 | 31.7509 | 105.7231 | 44.1583 | 144.7807 | 188.1434 | 173.626
243.1917 | 32.0288 | 106.2438 | 44.3283 | 146.7538 | 188.6973 | 174.3845
244.1917 | 32.2361 | 106.8125 | 44.7404 | 146.3394 | 188.7545 | 173.6532
245.1917 | 32.2719 | 107.5434 | 44.9585 | 146.4287 | 189.3905 | 173.4867
246.1917 | 32.1834 | 107.8787 | 45.0084 | 145.992 | 189.3067 | 173.0161
247.1917 | 32.5754 | 108.4685 | 45.0395 | 146.6174 | 189.4633 | 173.4262
248.1917 | 32.5322 | 108.8762 | 45.0601 | 146.244 | 189.1951 | 173.4905
249.1917 | 32.7372 | 109.2996 | 45.1866 | 146.702 | 189.2205 | 173.131
250.1917 | 32.8023 | 109.8002 | 45.3963 | 146.8654 | 188.9655 | 172.8694
251.1917 | 33.0571 | 110.5464 | 45.5302 | 146.6938 | 189.8552 | 173.1306
252.1917 | 33.0677 | 111.3476 | 45.6667 | 146.4901 | 190.3186 | 174.8548
253.1917 | 33.1089 | 111.5077 | 45.8513 | 146.4496 | 190.6726 | 176.1563
254.1917 | 33.043 | 112.1707 | 46.0484 | 146.0853 | 191.7577 | 178.5582
255.1917 | 33.3584 | 112.8612 | 46.1581 | 145.4027 | 192.1046 | 179.941
256.1917 | 33.5078 | 113.6515 | 46.2478 | 146.6537 | 191.9341 | 179.9951
257.1917 | 33.6868 | 113.9717 | 46.4261 | 146.5151 | 191.5481 | 179.6899
258.1917 | 33.7231 | 114.5321 | 46.6406 | 146.2387 | 190.5327 | 179.5627
259.1917 | 33.868 | 115.3344 | 46.6966 | 145.9587 | 190.3577 | 178.9771
260.1917 | 33.9471 | 115.7314 | 47.0024 | 146.1796 | 190.7534 | 179.6632
261.1917 | 34.3018 | 116.1553 | 47.1497 | 146.4101 | 191.3024 | 179.4916
262.1917 | 34.4533 | 116.8569 | 47.2867 | 146.3307 | 191.5223 | 179.3165
263.1917 | 34.6895 | 117.233 | 47.3455 | 147.0259 | 192.994 | 179.1318
264.1917 | 34.6414 | 118.1219 | 47.6733 | 147.3721 | 194.2068 | 180.3362
265.1917 | 34.7006 | 118.3979 | 47.6847 | 147.0341 | 194.5035 | 180.8667
266.1917 | 34.8892 | 118.775 | 47.8838 | 146.7046 | 195.0226 | 181.5969
267.1917 | 35.4742 | 119.5573 | 48.0405 | 146.9176 | 194.4228 | 181.8944
268.1917 | 35.4344 | 120.3166 | 48.1969 | 147.5323 | 194.1563 | 181.8685
269.1917 | 35.5451 | 120.71 | 48.2463 | 147.9601 | 193.2614 | 180.9205
270.1917 | 35.5906 | 121.4763 | 48.547 | 148.3861 | 193.6858 | 181.426
271.1917 | 35.6776 | 121.5818 | 48.7477 | 148.6758 | 193.804 | 181.0495
272.1917 | 35.7258 | 122.2165 | 48.7989 | 149.2653 | 193.8169 | 181.0975
273.1917 | 35.8329 | 122.8306 | 48.9636 | 150.0848 | 194.263 | 183.6737
274.1917 | 36.0552 | 123.3239 | 49.0843 | 150.4679 | 195.0272 | 183.5916
275.1917 | 36.3557 | 123.8104 | 49.148 | 150.5577 | 195.4618 | 185.0028
276.1917 | 36.24 | 124.331 | 49.2608 | 150.9061 | 194.9627 | 184.7116
277.1917 | 36.478 | 124.9442 | 49.5035 | 151.5071 | 194.6504 | 185.1281
278.1917 | 36.8397 | 125.7818 | 49.5989 | 151.2133 | 194.0344 | 184.3898
279.1917 | 37.2026 | 126.1287 | 49.7843 | 150.6958 | 193.895 | 183.2038
280.1917 | 37.079 | 126.6677 | 49.8227 | 150.7212 | 193.7501 | 182.9689
281.1917 | 37.1409 | 127.0881 | 50.2423 | 151.4426 | 193.6763 | 183.2548
282.1917 | 37.0622 | 127.8019 | 50.3285 | 151.2102 | 192.7722 | 182.2707
283.1917 | 37.1694 | 128.2444 | 50.3255 | 151.5134 | 193.3942 | 181.6642
284.1917 | 37.4991 | 128.5199 | 50.4043 | 151.5298 | 194.6645 | 182.5807
285.1917 | 37.5327 | 129.2338 | 50.7648 | 152.4126 | 195.0009 | 184.2056
286.1917 | 37.6624 | 129.7598 | 50.8103 | 151.7427 | 194.7286 | 183.7373
287.1917 | 37.9627 | 130.4061 | 50.822 | 151.6199 | 194.603 | 184.3984
288.1917 | 37.9461 | 130.9086 | 51.2681 | 152.1543 | 194.4674 | 184.5721
289.1917 | 38.0639 | 131.4412 | 51.3773 | 151.8655 | 195.0656 | 184.3629
290.1917 | 38.1966 | 132.1905 | 51.4466 | 151.6416 | 195.3947 | 184.0212
291.1917 | 38.4032 | 132.7321 | 51.679 | 151.7402 | 195.6392 | 183.4177
292.1917 | 38.4301 | 133.0348 | 51.7588 | 152.8065 | 196.1865 | 182.9204
293.1917 | 38.5259 | 133.7636 | 51.9345 | 153.3319 | 196.7405 | 182.5631
294.1917 | 38.6992 | 134.4554 | 52.1419 | 153.5714 | 196.7842 | 182.7691
295.1917 | 38.8049 | 135.0044 | 52.132 | 152.913 | 196.3105 | 183.0316
296.1917 | 38.9473 | 135.5196 | 52.3434 | 152.4971 | 195.9533 | 183.5113
297.1917 | 39.3253 | 136.0247 | 52.4066 | 152.0483 | 195.5339 | 183.8649
298.1917 | 39.4587 | 136.3135 | 52.5777 | 151.9048 | 195.7256 | 183.8075
299.1917 | 39.5917 | 136.8924 | 52.8045 | 152.6504 | 197.032 | 184.0103
300.1917 | 39.9405 | 137.6213 | 52.8862 | 152.4209 | 197.6266 | 185.1351
301.1917 | 39.9673 | 138.1494 | 53.1348 | 152.5521 | 198.1599 | 185.6543
302.1917 | 39.9138 | 138.5883 | 53.2514 | 153.7766 | 199.9931 | 185.2777
303.1917 | 40.0869 | 139.0645 | 53.5508 | 153.1576 | 198.8811 | 186.4085
304.1917 | 40.3377 | 139.5197 | 53.5548 | 154.566 | 199.7239 | 186.9508
305.2073 | 40.4627 | 140.0906 | 53.7381 | 154.96 | 199.8771 | 187.076
306.1917 | 40.3233 | 141.0321 | 53.9169 | 156.0213 | 201.5013 | 187.9384
307.1917 | 40.3547 | 141.3551 | 54.1095 | 155.9423 | 202.1007 | 188.4092
308.1917 | 40.6851 | 141.6699 | 54.2234 | 155.4392 | 202.7989 | 191.0779
309.1917 | 40.788 | 142.1171 | 54.5066 | 156.7841 | 204.9078 | 191.8582
310.1917 | 41.0531 | 142.5051 | 54.7143 | 156.5274 | 206.1253 | 194.3496
311.2073 | 40.9658 | 143.0524 | 54.7477 | 157.0488 | 206.7565 | 195.7044
312.1917 | 41.6019 | 143.8538 | 54.7635 | 157.3954 | 207.3516 | 195.5457
313.1917 | 41.6759 | 144.2559 | 55.1383 | 157.4859 | 207.1137 | 195.4197
314.1917 | 41.7585 | 144.9926 | 55.4477 | 158.409 | 208.4528 | 196.1663
315.1917 | 41.5664 | 145.3332 | 55.5051 | 159.3249 | 208.0553 | 195.9828
316.1917 | 41.5814 | 146.0059 | 55.7317 | 159.2218 | 207.5915 | 194.9319
317.1917 | 41.8953 | 146.8496 | 55.7567 | 159.9382 | 208.1813 | 194.7531
318.1917 | 42.1914 | 147.0649 | 55.8962 | 159.5535 | 207.3235 | 194.4564
319.1917 | 42.3326 | 147.523 | 56.0204 | 159.3675 | 206.9351 | 193.6999
320.1917 | 42.4854 | 148.1706 | 56.2037 | 158.9278 | 206.4642 | 193.4359
321.1917 | 42.4902 | 148.7932 | 56.2572 | 160.0776 | 206.8019 | 193.6873
322.1917 | 42.4741 | 149.1983 | 56.2655 | 159.9407 | 207.0008 | 193.9838
323.1917 | 42.7052 | 149.7278 | 56.4102 | 160.5323 | 207.5053 | 194.0898
324.1917 | 42.6924 | 149.9725 | 56.407 | 160.3586 | 207.4794 | 195.4365
325.1917 | 42.8216 | 150.3984 | 56.7524 | 160.7429 | 208.2424 | 197.1315
326.1917 | 42.9216 | 150.7654 | 56.9107 | 161.1093 | 207.8119 | 197.0483
327.1917 | 43.0239 | 151.1735 | 57.0026 | 161.0416 | 208.3623 | 196.5983
328.1917 | 42.9624 | 151.5727 | 57.0821 | 160.9545 | 207.985 | 196.6129
329.1917 | 43.0095 | 152.0851 | 57.2246 | 161.3018 | 208.1788 | 196.5099
330.1917 | 43.365 | 152.5484 | 57.5133 | 161.7557 | 209.2629 | 197.2924
331.1917 | 43.499 | 153.044 | 57.6531 | 161.658 | 209.4398 | 197.4079
332.1917 | 43.8748 | 153.7276 | 57.6665 | 163.9401 | 211.7793 | 198.0936
333.1917 | 44.1591 | 154.3863 | 58.0736 | 163.4804 | 212.8324 | 199.0558
334.1917 | 44.0963 | 154.7981 | 58.1731 | 163.6394 | 212.6234 | 199.9662
335.1917 | 44.1802 | 155.088 | 58.2586 | 163.511 | 213.074 | 201.3411
336.1917 | 44.1359 | 155.4361 | 58.4682 | 163.2786 | 213.3518 | 203.0184
337.1917 | 44.3041 | 156.0476 | 58.5457 | 164.2586 | 214.4994 | 203.5481
338.1917 | 44.7228 | 156.367 | 58.5366 | 166.5881 | 214.3514 | 204.8547
339.1917 | 44.7618 | 156.791 | 58.6679 | 167.3391 | 214.6614 | 206.4806
340.1917 | 45.051 | 157.2546 | 58.8227 | 168.3685 | 214.4949 | 207.243
341.1917 | 45.4095 | 157.812 | 58.9223 | 169.4108 | 215.0999 | 207.347
342.1917 | 45.5651 | 158.332 | 59.0403 | 169.7892 | 215.3959 | 207.6782
343.1917 | 45.5006 | 158.8027 | 59.1852 | 169.7949 | 215.2898 | 208.0707
344.1917 | 45.4937 | 159.2178 | 59.4115 | 169.6233 | 216.0841 | 208.8691
345.1917 | 45.538 | 159.9674 | 59.5957 | 168.2503 | 215.8192 | 208.0436
346.1917 | 45.5152 | 160.1883 | 59.7482 | 167.6714 | 216.3334 | 208.8991
347.1917 | 45.6674 | 160.8692 | 59.7746 | 168.6493 | 216.74 | 210.9264
348.1917 | 45.798 | 160.9902 | 59.9875 | 168.3574 | 215.9493 | 211.1856
349.1917 | 45.939 | 161.666 | 60.1323 | 168.0502 | 216.9257 | 211.7048
350.1917 | 46.0646 | 162.1966 | 60.3349 | 167.959 | 217.7467 | 210.5335
351.1917 | 46.2638 | 162.4271 | 60.3944 | 168.7909 | 217.5959 | 209.9732
352.1917 | 46.2313 | 163.1168 | 60.62 | 168.5687 | 217.9045 | 209.8069
353.1917 | 46.2743 | 163.5243 | 60.6351 | 169.5896 | 218.4733 | 209.5843
354.1917 | 46.3763 | 163.9066 | 60.9331 | 168.256 | 218.6453 | 210.3865
355.1917 | 46.441 | 164.761 | 61.2118 | 167.9769 | 218.3696 | 210.303
356.1917 | 46.6706 | 164.7964 | 61.1268 | 167.9059 | 218.6144 | 209.8388
357.1917 | 46.7636 | 165.2819 | 61.3517 | 168.3852 | 218.4533 | 209.9024
358.1917 | 46.9217 | 165.6667 | 61.5869 | 169.5103 | 218.6441 | 211.1085
359.1917 | 47.07 | 166.0952 | 61.5169 | 170.1628 | 219.2568 | 211.6586
360.1917 | 47.3618 | 166.6446 | 61.667 | 169.9575 | 219.0323 | 211.2579
361.1917 | 47.395 | 166.9834 | 61.8391 | 169.1954 | 219.1776 | 210.9289
362.1917 | 47.6785 | 167.4113 | 62.0403 | 168.8623 | 220.9596 | 211.616
363.1917 | 47.7746 | 167.9828 | 62.1052 | 168.5753 | 220.7604 | 211.5166
364.1917 | 48.0922 | 168.4611 | 62.2426 | 168.1804 | 219.3915 | 211.0324
365.1917 | 48.1373 | 168.8583 | 62.4726 | 166.721 | 218.7108 | 209.7971
366.1917 | 48.0708 | 169.3856 | 62.5454 | 166.4172 | 218.2946 | 209.5795
367.1917 | 48.4702 | 169.5665 | 62.7688 | 166.0431 | 217.2602 | 208.3398
368.1917 | 48.5264 | 170.0614 | 62.881 | 167.1627 | 216.9237 | 207.2139
369.1917 | 48.4616 | 170.4575 | 63.0269 | 167.2692 | 216.7717 | 208.7242
370.1917 | 48.6039 | 171.1566 | 63.1783 | 166.5397 | 216.7211 | 207.5673
371.1917 | 48.7942 | 171.4585 | 63.3061 | 166.7929 | 216.2051 | 207.3284
372.1917 | 48.9641 | 171.9689 | 63.538 | 166.8495 | 216.0305 | 206.8454
373.1917 | 48.9452 | 172.2999 | 63.6503 | 166.3725 | 215.9185 | 206.0144
374.1917 | 49.205 | 172.7158 | 63.7352 | 166.3125 | 217.1221 | 205.3793
375.1917 | 49.375 | 173.1916 | 63.8309 | 166.4239 | 217.6872 | 205.5291
376.1917 | 49.5529 | 173.6451 | 63.9608 | 166.7515 | 216.1544 | 205.026
377.1917 | 49.634 | 174.3 | 64.1954 | 166.1938 | 215.1602 | 205.5535
378.1917 | 49.6948 | 174.8257 | 64.2168 | 165.575 | 214.5176 | 205.0579
379.1917 | 50.0981 | 175.0214 | 64.4536 | 165.5949 | 213.7778 | 205.297
380.1917 | 50.2751 | 175.4481 | 64.5145 | 164.2624 | 215.26 | 204.5392
381.1917 | 50.2334 | 175.7377 | 64.7351 | 163.7697 | 215.2815 | 205.2299
382.1917 | 50.3772 | 175.9806 | 64.8394 | 163.2271 | 215.2502 | 205.9495
383.1917 | 50.5569 | 176.4528 | 65.0533 | 164.1828 | 216.0369 | 207.3703
384.1917 | 50.559 | 176.8368 | 65.2498 | 166.5372 | 216.8769 | 208.0629
385.1917 | 50.6271 | 177.1656 | 65.2468 | 166.3408 | 217.4991 | 208.5861
386.1917 | 51.0016 | 177.6871 | 65.2652 | 166.5875 | 218.4136 | 209.011
387.1917 | 51.0989 | 177.9777 | 65.3564 | 166.0162 | 218.5329 | 208.7659
388.1917 | 51.1675 | 178.6092 | 65.616 | 166.6568 | 219.5933 | 209.2585
389.1917 | 51.1051 | 178.9885 | 65.7977 | 167.0735 | 219.51 | 209.1538
390.1917 | 51.1767 | 179.4314 | 65.9028 | 166.8771 | 219.3666 | 208.5005
391.1917 | 51.5953 | 179.7195 | 66.0014 | 166.8387 | 219.1742 | 208.365
392.1917 | 51.7402 | 180.2305 | 66.3348 | 165.9749 | 218.7825 | 208.2032
393.1917 | 51.9024 | 180.6702 | 66.3925 | 166.2909 | 219.0327 | 206.5473
394.1917 | 52.1237 | 181.1899 | 66.6582 | 165.2879 | 218.8658 | 205.7712
395.1917 | 52.0563 | 181.7287 | 66.6618 | 164.6112 | 218.3818 | 205.6061
396.1917 | 52.1034 | 182.2649 | 66.8255 | 164.3064 | 218.2655 | 205.3146
397.1917 | 52.1329 | 182.7639 | 66.8395 | 163.6033 | 217.5275 | 205.6183
398.1917 | 52.331 | 182.9887 | 67.0889 | 163.571 | 216.4968 | 203.9403
399.1917 | 52.8609 | 182.9941 | 67.2872 | 163.593 | 214.9656 | 202.8282
400.1917 | 53.0006 | 183.3618 | 67.3404 | 164.3277 | 216.4738 | 202.7857
401.1917 | 52.9855 | 183.8934 | 67.5688 | 164.858 | 217.2605 | 203.515
402.1917 | 53.1911 | 184.2292 | 67.7489 | 164.7607 | 216.9738 | 203.5725
403.1917 | 53.0094 | 184.5995 | 67.7953 | 165.6581 | 216.553 | 205.0987
404.1917 | 53.0485 | 185.3645 | 68.0124 | 166.3398 | 216.4572 | 205.3708
405.1917 | 53.1929 | 186.0183 | 68.0739 | 165.991 | 217.0198 | 205.3217
406.1917 | 53.2776 | 186.1618 | 68.2124 | 165.8313 | 216.5786 | 205.2796
407.1917 | 53.3513 | 186.3608 | 68.3195 | 165.746 | 217.7807 | 204.5702
408.1917 | 53.7567 | 187.0183 | 68.4133 | 165.4613 | 218.6281 | 205.6857
409.1917 | 53.8354 | 187.3007 | 68.5666 | 165.3193 | 218.8438 | 205.2446
410.1917 | 53.8427 | 187.77 | 68.7521 | 165.8867 | 218.4735 | 204.3389
411.1917 | 53.9247 | 188.4984 | 68.9307 | 165.6715 | 218.0464 | 203.2157
412.1917 | 54.3148 | 188.9639 | 69.0857 | 165.9285 | 217.987 | 203.0462
413.1917 | 54.4095 | 189.4661 | 69.1779 | 165.6515 | 216.5049 | 202.5065
414.1917 | 54.5196 | 189.6874 | 69.3546 | 165.0137 | 215.9579 | 201.5619
415.1917 | 54.6116 | 190.3647 | 69.6118 | 164.4275 | 216.1182 | 200.8269
416.1917 | 54.9759 | 190.5389 | 69.7966 | 163.7015 | 215.5787 | 200.222
417.1917 | 55.2088 | 190.9775 | 69.8427 | 163.1739 | 215.0631 | 199.6403
418.1917 | 55.3979 | 191.3242 | 69.9559 | 162.8634 | 214.991 | 200.5057
419.1917 | 55.4954 | 191.8107 | 70.074 | 163.0373 | 215.0685 | 200.5567
420.1917 | 55.4968 | 192.3553 | 70.2401 | 164.5365 | 214.8016 | 200.1837
421.1917 | 55.5802 | 192.738 | 70.3898 | 165.4442 | 214.5244 | 200.079
422.1917 | 55.6173 | 192.8835 | 70.5654 | 165.6905 | 213.8969 | 199.977
423.1917 | 55.7446 | 193.3536 | 70.8379 | 165.4117 | 213.3429 | 199.0663
424.1917 | 55.8727 | 193.9234 | 70.9941 | 165.7985 | 213.3734 | 198.4323
425.2073 | 56.1164 | 194.0894 | 71.0557 | 165.3493 | 213.7134 | 198.5374
426.1917 | 55.9677 | 194.7308 | 71.5076 | 165.7161 | 214.577 | 198.7141
427.1917 | 56.2752 | 194.985 | 71.4613 | 166.7122 | 215.0017 | 198.221
428.1917 | 56.4531 | 195.5393 | 71.6499 | 167.1033 | 215.3891 | 198.229
429.1917 | 56.5019 | 195.9779 | 71.8943 | 167.1331 | 216.0411 | 198.3385
430.1917 | 56.8526 | 196.276 | 71.9268 | 167.5417 | 215.3406 | 198.0227
431.1917 | 57.0752 | 196.842 | 72.0309 | 167.8112 | 215.434 | 197.2357
432.1917 | 57.0658 | 197.0628 | 72.4107 | 167.5147 | 215.1497 | 196.1979
433.1917 | 57.3286 | 197.5574 | 72.5242 | 167.6593 | 215.0263 | 195.8868
434.1917 | 57.321 | 197.8389 | 72.6356 | 167.565 | 215.1469 | 196.374
435.1917 | 57.2822 | 198.2619 | 72.7918 | 167.0764 | 214.6624 | 196.2352
436.1917 | 57.2898 | 198.5591 | 72.9963 | 168.1473 | 214.199 | 195.3924
437.1917 | 57.4841 | 198.9738 | 73.176 | 169.057 | 213.8988 | 195.3329
438.1917 | 57.5668 | 199.656 | 73.3753 | 169.4876 | 214.2372 | 194.9594
439.1917 | 57.7674 | 199.9909 | 73.3082 | 170.6667 | 214.2981 | 194.6962
440.1917 | 57.8975 | 200.1613 | 73.4075 | 170.3535 | 214.8745 | 194.6085
441.1917 | 58.1943 | 200.5651 | 73.51 | 170.1634 | 214.6166 | 194.5914
442.1917 | 58.2523 | 201.3229 | 73.6145 | 169.8789 | 215.5634 | 195.4178
443.1917 | 58.2467 | 201.5096 | 73.7538 | 169.8736 | 216.2692 | 196.5121
444.1917 | 58.4282 | 201.5953 | 73.8763 | 169.8441 | 215.6975 | 197.9179
445.1917 | 58.5864 | 201.976 | 74.1098 | 170.2291 | 215.8058 | 198.5407
446.1917 | 58.7236 | 202.4824 | 74.2296 | 170.8559 | 216.4878 | 198.6322
447.1917 | 58.6751 | 202.9687 | 74.3495 | 170.431 | 217.2828 | 199.967
448.1917 | 58.9423 | 203.4898 | 74.6181 | 171.007 | 218.4122 | 201.5594
449.1917 | 59.1054 | 203.5853 | 74.6212 | 171.9086 | 218.4796 | 202.2819
450.1917 | 59.3794 | 203.8572 | 74.8203 | 171.8247 | 217.5268 | 202.6031
451.1917 | 59.6092 | 204.2479 | 75.0288 | 171.373 | 217.1243 | 203.0162
452.1917 | 59.6428 | 204.5728 | 75.0829 | 170.986 | 216.8948 | 202.8237
453.1917 | 59.6751 | 204.8435 | 75.2719 | 170.865 | 216.457 | 202.1832
454.1917 | 59.8579 | 205.5319 | 75.4434 | 170.2622 | 216.2049 | 201.3106
455.1917 | 59.9178 | 206.3589 | 75.5151 | 169.5312 | 216.0221 | 201.2105
456.1917 | 60.1043 | 206.3716 | 75.5575 | 168.6818 | 216.0204 | 201.138
457.1917 | 60.2651 | 206.8041 | 75.7901 | 168.1813 | 216.4034 | 202.1779
458.1917 | 60.297 | 207.7457 | 76.2192 | 167.6512 | 215.4929 | 202.7236
459.1917 | 60.3029 | 207.7439 | 76.2688 | 166.4886 | 215.7222 | 202.5891
460.1917 | 60.4638 | 208.1844 | 76.3883 | 167.1137 | 215.3602 | 202.1704
461.1917 | 60.6682 | 208.5889 | 76.3923 | 166.9664 | 216.3101 | 202.7401
462.1917 | 60.8736 | 208.7816 | 76.5124 | 166.8828 | 216.4614 | 202.8125
463.1917 | 61.4794 | 208.8716 | 76.5853 | 166.7581 | 215.8008 | 203.3568
464.1917 | 61.2624 | 209.4723 | 76.906 | 167.2124 | 216.2431 | 203.3773
465.1917 | 61.2941 | 209.9503 | 77.1041 | 166.9033 | 215.2672 | 203.5696
466.1917 | 61.4511 | 210.1758 | 77.211 | 167.2325 | 214.6131 | 203.1392
467.1917 | 61.5156 | 210.6135 | 77.3184 | 167.407 | 214.8537 | 202.5527
468.1917 | 61.5688 | 211.2525 | 77.3995 | 167.5758 | 215.3423 | 202.5888
469.1917 | 61.9489 | 211.4097 | 77.617 | 167.4674 | 214.9401 | 202.253
470.1917 | 61.9653 | 211.8283 | 77.7892 | 167.3453 | 215.9596 | 201.615
471.1917 | 62.1038 | 212.3387 | 77.9538 | 167.2593 | 216.8574 | 201.3907
472.1917 | 62.1226 | 212.784 | 78.0434 | 167.2988 | 215.2349 | 201.04
473.1917 | 62.3659 | 213.0644 | 78.076 | 166.9855 | 214.2502 | 201.1519
474.1917 | 62.5041 | 213.9309 | 78.2321 | 167.2444 | 215.0557 | 202.4483
475.1917 | 62.5763 | 214.4472 | 78.2483 | 167.1761 | 215.0705 | 202.2918
476.1917 | 62.6742 | 214.3816 | 78.3912 | 166.3229 | 215.4695 | 202.5883
477.1917 | 62.7888 | 215.0221 | 78.5351 | 166.5519 | 216.6048 | 203.8114
478.1917 | 62.8353 | 215.1962 | 78.6373 | 165.8057 | 217.026 | 204.2402
479.1917 | 62.8068 | 215.5903 | 78.916 | 167.002 | 217.831 | 204.6523
480.1917 | 62.9965 | 215.9806 | 79.0962 | 166.9239 | 218.2135 | 205.2957
481.1917 | 63.2027 | 216.2311 | 79.4274 | 167.1331 | 218.2922 | 204.7399
482.1917 | 63.5051 | 217.3072 | 79.6163 | 167.1031 | 218.2299 | 204.0981
483.1917 | 63.5971 | 217.3311 | 79.6284 | 167.8451 | 218.5519 | 203.7728
484.1917 | 63.6851 | 217.539 | 79.8732 | 169.4284 | 218.7974 | 203.0188
485.1917 | 63.9987 | 218.1276 | 80.0041 | 170.731 | 219.1211 | 204.2342
486.1917 | 63.8677 | 218.2844 | 80.0464 | 171.0458 | 219.105 | 203.8917
487.1917 | 64.1153 | 218.6642 | 80.2018 | 171.0919 | 219.0007 | 203.469
488.1917 | 64.1915 | 218.9639 | 80.4423 | 171.0508 | 219.316 | 203.4077
489.1917 | 64.2672 | 219.5674 | 80.4996 | 171.3646 | 219.8808 | 203.6977
490.1917 | 64.5019 | 220.0035 | 80.5986 | 171.087 | 219.4359 | 203.5264
491.1917 | 64.7059 | 220.2324 | 80.6596 | 170.8249 | 219.1913 | 203.6646
492.1917 | 65.0847 | 221.1416 | 80.8114 | 170.4848 | 218.7995 | 203.2611
493.1917 | 65.1424 | 221.2204 | 81.0289 | 169.5384 | 217.9513 | 202.7904
494.1917 | 65.1567 | 221.4915 | 81.1793 | 169.7104 | 217.5066 | 202.1269
495.1917 | 65.049 | 221.9166 | 81.428 | 172.1613 | 218.9498 | 201.8399
496.1917 | 65.1186 | 222.4103 | 81.5879 | 174.1996 | 220.3603 | 202.3788
497.1917 | 65.3483 | 222.5625 | 81.8579 | 174.4016 | 221.6991 | 203.4262
498.1917 | 65.4464 | 223.1084 | 82.1101 | 174.3697 | 223.6744 | 204.493
499.1917 | 65.7859 | 223.684 | 82.1327 | 174.3289 | 223.9021 | 205.1096
500.1917 | 65.7248 | 223.9192 | 82.3042 | 174.1181 | 222.9418 | 205.1922
501.1917 | 65.811 | 224.1156 | 82.481 | 174.5594 | 222.9906 | 205.6043
502.1917 | 65.8504 | 224.5566 | 82.4965 | 174.1516 | 222.9863 | 205.497
503.1917 | 66.0029 | 225.2557 | 82.7087 | 175.6385 | 224.1777 | 205.3819
504.1917 | 66.2794 | 225.9485 | 82.9774 | 176.1079 | 225.1374 | 206.224
505.1917 | 66.4521 | 226.0389 | 83.0074 | 175.8811 | 225.4215 | 206.0899
506.1917 | 66.6827 | 226.4742 | 83.2635 | 175.5726 | 225.4159 | 205.6761
507.1917 | 66.9243 | 226.7361 | 83.6758 | 174.7386 | 225.2286 | 205.5049
508.1917 | 66.938 | 227.3443 | 83.6094 | 175.6017 | 224.9865 | 205.4915
509.1917 | 67.1916 | 227.7818 | 83.8347 | 175.4822 | 224.494 | 205.2132
510.1917 | 67.3468 | 227.8119 | 83.8585 | 176.0071 | 224.248 | 204.389
511.1917 | 67.4326 | 228.1634 | 83.9966 | 175.1483 | 224.6905 | 204.9764
512.1917 | 67.5692 | 228.7478 | 84.0991 | 177.2362 | 225.2597 | 205.2301
513.1917 | 67.65 | 229.2921 | 84.2366 | 177.0299 | 226.2341 | 205.5965
514.1917 | 67.9084 | 229.9111 | 84.6269 | 177.4702 | 227.4743 | 205.716
515.1917 | 68.0118 | 230.1461 | 84.5778 | 177.6762 | 227.6836 | 206.183
516.1917 | 68.0355 | 230.3091 | 84.6699 | 178.5138 | 228.6637 | 207.1563
517.1917 | 68.2019 | 230.6679 | 84.8419 | 177.7965 | 229.5113 | 207.4641
518.1917 | 68.3799 | 231.7608 | 85.0134 | 176.3794 | 229.561 | 207.7251
519.1917 | 68.2448 | 231.9013 | 85.1928 | 176.3522 | 228.8999 | 207.638
520.1917 | 68.4154 | 232.0591 | 85.47 | 176.3514 | 229.5179 | 207.6227
521.1917 | 68.5051 | 232.4618 | 85.4702 | 176.9466 | 229.4177 | 207.5043
522.1917 | 68.7705 | 232.5349 | 85.4844 | 176.5136 | 229.1509 | 207.7974
523.1917 | 68.8612 | 233.0345 | 85.7265 | 175.8968 | 228.9906 | 208.4253
524.1917 | 68.8744 | 233.5013 | 85.8359 | 175.0259 | 228.9439 | 208.4968
525.1917 | 68.9133 | 233.7421 | 86.0415 | 174.9178 | 229.431 | 208.7219
526.1917 | 69.0482 | 234.2779 | 86.2687 | 174.422 | 228.9168 | 209.2617
527.1917 | 69.3 | 234.5909 | 86.3155 | 175.8572 | 228.5526 | 210.3303
528.1917 | 69.6298 | 235.0254 | 86.4201 | 176.1264 | 228.8224 | 209.9541
529.1917 | 69.7405 | 235.4532 | 86.6665 | 175.7735 | 227.8759 | 209.7907
530.1917 | 70.2004 | 235.5826 | 86.8397 | 175.0053 | 227.2199 | 210.3592
531.1917 | 70.1193 | 236.0714 | 87.0271 | 174.6513 | 226.455 | 209.9767
532.1917 | 70.092 | 236.5716 | 87.0323 | 174.7498 | 226.4905 | 210.2997
533.1917 | 70.0272 | 236.741 | 87.1502 | 175.288 | 226.5635 | 210.5208
534.1917 | 70.2349 | 236.8938 | 87.2461 | 175.8717 | 227.1297 | 210.5572
535.1917 | 70.4695 | 237.1793 | 87.4081 | 178.4787 | 229.0939 | 213.0506
536.1917 | 70.4982 | 237.6226 | 87.6752 | 181.1098 | 231.5105 | 214.2262
537.1917 | 70.5094 | 237.9113 | 87.8256 | 181.3345 | 232.477 | 215.5667
538.1917 | 70.6518 | 238.4763 | 88.0051 | 182.1448 | 232.4239 | 214.9753
539.1917 | 70.8025 | 239.2033 | 88.216 | 182.2728 | 233.4511 | 215.1636
540.1917 | 70.9758 | 239.4688 | 88.3336 | 181.6832 | 233.4632 | 214.4334
541.1917 | 71.3604 | 239.8579 | 88.501 | 181.5847 | 232.9584 | 213.7104
542.1917 | 71.3691 | 240.1467 | 88.6131 | 181.1238 | 233.455 | 213.0202
543.1917 | 71.4762 | 240.5038 | 88.7837 | 180.2803 | 233.7105 | 213.1575
544.1917 | 71.8247 | 240.6042 | 88.9372 | 180.1116 | 233.3071 | 213.5359
545.1917 | 71.9011 | 240.9705 | 89.16 | 179.8787 | 233.2184 | 213.6266
546.1917 | 71.811 | 241.4518 | 89.2923 | 180.4063 | 232.9389 | 213.0334
547.1917 | 71.9651 | 242.0978 | 89.6085 | 179.1728 | 232.8739 | 212.3042
548.1917 | 72.0845 | 242.4487 | 89.5297 | 179.3439 | 232.6006 | 211.3486
549.1917 | 72.2787 | 242.4257 | 89.6233 | 180.8729 | 232.6607 | 210.9874
550.1917 | 72.4816 | 242.5879 | 89.8194 | 181.3175 | 231.8026 | 210.2207
551.1917 | 72.4839 | 242.9815 | 90.0692 | 181.3251 | 231.7577 | 209.8845
552.1917 | 72.5323 | 243.5804 | 90.0305 | 182.7722 | 231.8292 | 208.6611
553.1917 | 72.7382 | 243.7347 | 90.3741 | 182.6743 | 231.6553 | 207.9754
554.1917 | 72.9795 | 244.2623 | 90.5064 | 182.3894 | 231.0247 | 207.3129
555.1917 | 73.1192 | 244.5271 | 90.451 | 183.147 | 230.5723 | 206.5749
556.1917 | 73.1264 | 244.8215 | 90.7719 | 183.2705 | 230.1015 | 206.2614
557.1917 | 73.5793 | 245.0485 | 90.9537 | 182.8317 | 229.5971 | 206.3532
558.1917 | 73.5583 | 245.1858 | 91.1158 | 183.0567 | 229.3442 | 207.4528
559.1917 | 73.6765 | 245.8038 | 91.254 | 183.1677 | 228.8667 | 207.1096
560.1917 | 73.786 | 246.2108 | 91.3953 | 183.2106 | 227.8844 | 206.4576
561.1917 | 74.2417 | 246.5119 | 91.6103 | 182.2624 | 227.2726 | 206.162
562.1917 | 74.1277 | 246.6553 | 91.7249 | 182.2704 | 227.6657 | 206.2783
563.1917 | 73.9936 | 247.2641 | 91.8995 | 182.4791 | 227.5837 | 206.5752
564.1917 | 74.278 | 247.3945 | 91.9465 | 181.4768 | 227.2959 | 205.3206
565.1917 | 74.3927 | 247.6401 | 92.2319 | 180.8447 | 227.0322 | 206.1105
566.1917 | 74.4383 | 247.9063 | 92.3624 | 181.9011 | 228.0863 | 206.6182
567.1917 | 74.3752 | 248.3916 | 92.5759 | 182.8096 | 229.2822 | 208.0297
568.1917 | 74.651 | 248.6644 | 92.7881 | 182.3621 | 228.4605 | 207.4397
569.1917 | 75.0406 | 249.0686 | 92.8053 | 182.5899 | 228.7884 | 207.7115
570.1917 | 75.1212 | 249.513 | 92.9577 | 181.4095 | 229.2876 | 208.5581
571.1917 | 75.2572 | 249.7665 | 93.0947 | 181.2908 | 229.6346 | 208.8063
572.1917 | 75.3339 | 250.1016 | 93.4338 | 180.3876 | 228.7866 | 208.5654
573.1917 | 75.3026 | 250.4705 | 93.4046 | 180.349 | 228.2645 | 207.8375
574.1917 | 75.4637 | 251.1652 | 93.4893 | 179.6057 | 227.6853 | 207.1448
575.1917 | 75.6399 | 251.1861 | 93.7993 | 179.8653 | 227.5714 | 206.6819
576.1917 | 75.8331 | 251.8339 | 93.8605 | 180.0581 | 227.6376 | 207.3394
577.1917 | 75.8569 | 251.9545 | 94.2213 | 179.803 | 227.4249 | 206.8883
578.1917 | 75.962 | 252.3708 | 94.294 | 179.1868 | 227.0806 | 206.2668
579.1917 | 76.3781 | 252.9976 | 94.3517 | 178.9833 | 226.8475 | 206.3023
580.1917 | 76.4087 | 253.1034 | 94.5007 | 179.387 | 226.7863 | 206.0014
581.1917 | 76.603 | 253.2678 | 94.5647 | 179.6327 | 227.1013 | 206.9734
582.1917 | 76.8223 | 253.9595 | 94.6644 | 180.0941 | 228.0294 | 207.5918
583.1917 | 76.9422 | 254.1812 | 94.9359 | 179.5364 | 228.0815 | 208.0008
584.1917 | 76.9618 | 254.2842 | 95.0445 | 179.4486 | 228.0696 | 207.9472
585.1917 | 77.1535 | 254.5817 | 95.1953 | 179.6428 | 228.1147 | 207.524
586.1917 | 77.1087 | 255.1625 | 95.458 | 179.4588 | 227.6918 | 207.337
587.1917 | 77.1508 | 255.3328 | 95.5231 | 178.9488 | 226.8289 | 207.242
588.1917 | 77.3338 | 256.0527 | 95.6588 | 178.5298 | 226.1037 | 206.592
589.1917 | 77.5545 | 256.3309 | 95.9304 | 177.8835 | 225.4059 | 205.6984
590.1917 | 77.6472 | 256.5425 | 95.9024 | 177.2983 | 225.3188 | 204.7974
591.1917 | 77.7483 | 256.5722 | 96.1641 | 177.1514 | 224.2316 | 204.7038
592.1917 | 77.7953 | 256.9782 | 96.3825 | 178.5129 | 224.8035 | 205.438
593.1917 | 78.0537 | 257.7682 | 96.5766 | 179.362 | 223.4323 | 205.6244
594.1917 | 78.007 | 258.1733 | 96.5543 | 179.0777 | 224.035 | 206.6201
595.1917 | 78.1775 | 258.8238 | 96.7034 | 179.275 | 225.4094 | 206.7516
596.1917 | 78.3823 | 259.1433 | 96.8433 | 179.8436 | 225.6839 | 207.081
597.1917 | 78.6428 | 259.2021 | 97.0285 | 180.2269 | 224.4058 | 206.4433
598.1917 | 78.9036 | 259.4918 | 97.1636 | 180.6753 | 224.9122 | 206.4422
599.1917 | 79.2051 | 259.6698 | 97.4612 | 182.9925 | 225.9616 | 206.6406
600.1917 | 79.1385 | 259.8944 | 97.5593 | 184.3395 | 226.6246 | 207.3563
601.1917 | 79.1379 | 260.1079 | 97.7211 | 184.253 | 227.2693 | 208.7621
602.1917 | 79.1809 | 260.4099 | 97.8612 | 184.3779 | 228.3896 | 210.3725
603.1917 | 79.0978 | 261.0333 | 98.1192 | 184.5026 | 228.5441 | 211.8001
604.1917 | 79.3001 | 261.5266 | 98.2007 | 184.7182 | 229.3455 | 212.0655
605.1917 | 79.485 | 261.7795 | 98.4455 | 185.4729 | 229.8728 | 211.5558
606.1917 | 79.6321 | 262.1098 | 98.6758 | 185.7122 | 229.5868 | 210.7662
607.1917 | 79.8497 | 262.3827 | 98.7873 | 185.3148 | 229.3728 | 210.9959
608.1917 | 79.9493 | 262.4271 | 99.1162 | 186.0507 | 229.8635 | 211.8406
609.1917 | 80.0035 | 262.7652 | 99.7029 | 186.2544 | 229.3328 | 211.3304
610.1917 | 79.9658 | 262.9913 | 99.7911 | 185.9629 | 228.2121 | 210.3313
611.1917 | 80.1226 | 263.2063 | 99.698 | 186.301 | 226.8344 | 209.4057
612.1917 | 80.2946 | 263.6441 | 99.9726 | 186.7672 | 226.6131 | 208.6593
613.1917 | 80.3443 | 264.0313 | 99.8579 | 185.9733 | 227.2311 | 208.4217
614.1917 | 80.6231 | 264.2551 | 100.0177 | 188.0025 | 228.3226 | 209.3957
615.1917 | 80.8614 | 264.9027 | 100.0792 | 188.6753 | 228.6971 | 210.4428
616.1917 | 80.7499 | 264.7691 | 100.389 | 187.9222 | 227.933 | 209.4519
617.1917 | 80.8292 | 265.2609 | 100.6495 | 187.1426 | 227.9079 | 210.0977
618.1917 | 81.0757 | 265.3441 | 100.6353 | 187.607 | 228.3603 | 210.4413
619.1917 | 81.1928 | 265.7363 | 100.7309 | 188.4472 | 228.4768 | 210.1064
620.1917 | 81.2578 | 266.0774 | 100.8639 | 187.9446 | 228.2784 | 209.4428
621.1917 | 81.3608 | 266.2743 | 101.0434 | 188.0833 | 228.6491 | 209.134
622.1917 | 81.5404 | 266.9673 | 101.4139 | 187.7994 | 227.9014 | 208.4895
623.1917 | 81.8004 | 267.4268 | 101.271 | 187.6259 | 227.8037 | 208.6159
624.1917 | 81.9001 | 267.516 | 101.5781 | 187.2879 | 227.18 | 208.4553
625.1917 | 82.0072 | 267.6832 | 101.8202 | 186.973 | 226.5883 | 207.871
626.1917 | 82.2414 | 267.9749 | 101.8346 | 186.6676 | 226.24 | 207.5292
627.1917 | 82.2742 | 267.9663 | 102.0563 | 186.567 | 225.4426 | 207.5021
628.1917 | 82.2661 | 268.12 | 102.4054 | 186.8393 | 225.2636 | 207.1567
629.1917 | 82.304 | 268.7715 | 102.545 | 187.3515 | 225.2511 | 206.8951
630.1917 | 82.4502 | 268.8005 | 102.7394 | 188.8338 | 224.6519 | 207.1917
631.1917 | 82.9331 | 269.2656 | 102.8195 | 189.2488 | 225.4165 | 206.8192
632.1917 | 82.8887 | 269.4734 | 103.0337 | 189.8568 | 225.8634 | 206.9502
633.1917 | 82.8709 | 269.6091 | 103.2159 | 188.0942 | 226.0111 | 207.1554
634.1917 | 83.1789 | 269.8975 | 103.4912 | 187.2883 | 225.8996 | 207.1671
635.1917 | 83.2925 | 270.0285 | 103.7184 | 186.6355 | 226.1986 | 206.4097
636.1917 | 83.2849 | 270.6239 | 103.8158 | 187.3981 | 226.3026 | 206.0785
637.1917 | 83.3245 | 270.9934 | 104.0059 | 187.4789 | 225.4971 | 205.9893
638.1917 | 83.6004 | 271.7875 | 104.1153 | 186.6322 | 224.8346 | 205.2541
639.1917 | 83.9085 | 271.6709 | 104.4453 | 186.1576 | 224.6341 | 205.359
640.1917 | 84.0182 | 272.6772 | 104.3791 | 184.8302 | 224.7933 | 205.6645
641.1917 | 83.9261 | 272.3417 | 104.5841 | 184.1249 | 224.7917 | 205.3792
642.1917 | 84.2808 | 272.7417 | 104.6856 | 184.3187 | 224.6565 | 205.6337
643.1917 | 84.3195 | 272.7377 | 104.8806 | 183.8408 | 224.741 | 206.0726
644.1917 | 84.3699 | 273.027 | 105.1018 | 183.803 | 224.6431 | 206.0725
645.1917 | 84.2364 | 273.1178 | 105.2048 | 184.0187 | 225.5915 | 206.3385
646.1917 | 84.5159 | 273.4777 | 105.6297 | 184.7796 | 226.2796 | 206.904
647.1917 | 84.6299 | 274.1494 | 105.5983 | 184.0934 | 226.1552 | 206.6709
648.1917 | 84.5205 | 274.9038 | 105.8781 | 183.848 | 225.8853 | 207.233
649.1917 | 84.6576 | 274.9973 | 106.1271 | 183.5359 | 225.3859 | 207.378
650.1917 | 84.9178 | 275.397 | 106.3115 | 183.4652 | 224.6102 | 206.9526
651.1917 | 85.2607 | 275.8117 | 106.3896 | 183.194 | 223.7596 | 206.5732
652.1917 | 85.3373 | 276.163 | 106.5585 | 183.2278 | 223.2633 | 206.4672
653.1917 | 85.6423 | 276.551 | 106.8184 | 182.9188 | 223.0934 | 206.8638
654.1917 | 85.7194 | 276.4253 | 106.9322 | 182.7757 | 223.0614 | 205.5781
655.1917 | 85.8905 | 276.9496 | 107.1843 | 182.6561 | 223.9334 | 205.5428
656.1917 | 85.8521 | 277.3367 | 107.2143 | 182.7648 | 223.9502 | 205.8142
657.1917 | 85.87 | 277.6097 | 107.3694 | 181.8223 | 224.9425 | 205.5336
658.1917 | 85.8213 | 277.6743 | 107.5771 | 181.5854 | 224.5533 | 205.5191
659.1917 | 86.0377 | 277.79 | 107.802 | 181.2979 | 224.8245 | 205.9594
660.1917 | 86.1653 | 278.2861 | 107.803 | 181.8379 | 226.3705 | 206.0672
661.1917 | 86.1964 | 278.5983 | 107.949 | 181.121 | 226.5548 | 206.5285
662.1917 | 86.4019 | 278.8165 | 108.1297 | 180.7927 | 226.5373 | 206.3635
663.1917 | 86.5727 | 278.7707 | 108.174 | 181.069 | 227.7434 | 207
664.1917 | 86.7108 | 278.9225 | 108.497 | 181.1986 | 227.7992 | 206.9862
665.2073 | 86.8859 | 279.4784 | 108.7424 | 181.5629 | 228.2495 | 207.9837
666.1917 | 86.8769 | 279.625 | 108.6839 | 182.1197 | 229.3002 | 208.0575
667.1917 | 87.0278 | 279.8669 | 109.2649 | 181.3675 | 230.1593 | 208.1414
668.1917 | 87.0057 | 280.2387 | 109.7185 | 182.7204 | 230.2282 | 207.4342
669.1917 | 87.0495 | 280.2529 | 110.0081 | 182.6648 | 229.2824 | 207.1385
670.1917 | 87.2785 | 280.8062 | 110.1136 | 182.9041 | 228.7698 | 207.1199
671.1917 | 87.469 | 281.3807 | 109.9937 | 184.1121 | 229.4215 | 207.1896
672.1917 | 87.5427 | 281.4476 | 110.1013 | 183.6573 | 229.3036 | 207.842
673.1917 | 87.7108 | 281.6778 | 110.4111 | 183.1003 | 229.9373 | 208.361
674.1917 | 87.7775 | 281.9156 | 110.6817 | 184.2591 | 230.7461 | 208.0415
675.1917 | 87.9939 | 282.3245 | 110.8849 | 184.4447 | 232.0514 | 208.6035
676.1917 | 87.9922 | 282.527 | 111.0087 | 184.8843 | 233.449 | 209.5158
677.1917 | 88.0005 | 282.8701 | 111.1045 | 186.0289 | 234.2901 | 210.1678
678.1917 | 88.1556 | 282.8222 | 111.1535 | 186.1761 | 234.0787 | 210.0374
679.1917 | 88.3329 | 283.4246 | 111.4754 | 187.3465 | 233.2942 | 209.6547
680.1917 | 88.6517 | 283.7036 | 111.5784 | 187.0043 | 232.331 | 208.7356
681.1917 | 88.6552 | 283.912 | 111.6116 | 187.0159 | 232.1833 | 208.673
682.1917 | 88.6762 | 284.2634 | 111.8091 | 186.6306 | 232.3447 | 209.3898
683.1917 | 88.692 | 284.4906 | 112.1115 | 187.0485 | 231.9905 | 210.2099
684.1917 | 88.7277 | 284.7913 | 112.139 | 185.6429 | 232.5574 | 209.9023
685.1917 | 88.8744 | 285.7635 | 112.3559 | 185.5459 | 232.2648 | 209.4691
686.1917 | 89.1534 | 285.854 | 112.5961 | 185.3801 | 232.2927 | 209.9616
687.2073 | 89.3632 | 286.0067 | 112.8953 | 184.594 | 233.3763 | 210.6522
688.1917 | 89.6025 | 286.3976 | 113.196 | 184.8598 | 233.3 | 210.7519
689.1917 | 89.5541 | 286.2685 | 113.3198 | 184.9715 | 231.7956 | 210.116
690.1917 | 89.5211 | 286.9186 | 113.5262 | 185.0631 | 230.9116 | 209.6365
691.2073 | 89.6722 | 287.0365 | 113.4672 | 184.7702 | 230.7776 | 209.3144
692.1917 | 89.7624 | 287.4641 | 113.7281 | 184.4794 | 229.8775 | 209.3438
693.1917 | 89.836 | 287.9217 | 113.8151 | 184.1677 | 229.8372 | 208.7163
694.1917 | 90.015 | 288.133 | 114.3144 | 184.2562 | 229.858 | 208.9353
695.1917 | 90.1862 | 288.3972 | 114.3975 | 184.6727 | 229.5475 | 209.2319
696.1917 | 90.4478 | 288.9509 | 114.5455 | 184.7969 | 228.8529 | 209.2018
697.2073 | 90.2611 | 288.8269 | 114.7877 | 183.9502 | 228.4081 | 209.0925
698.1917 | 90.6223 | 289.3412 | 115.0278 | 183.3927 | 227.912 | 209.6026
699.1917 | 90.5206 | 289.3932 | 115.0616 | 183.8676 | 227.4414 | 209.6245
700.1917 | 90.8722 | 289.3912 | 115.5221 | 183.3432 | 226.914 | 209.7398
701.1917 | 90.8265 | 290.2067 | 115.6693 | 183.7393 | 226.5288 | 209.9492
702.1917 | 90.998 | 290.378 | 115.6659 | 184.4648 | 227.543 | 210.6859
703.2073 | 91.1395 | 290.5904 | 115.9313 | 184.8767 | 229.018 | 210.6758
704.1917 | 91.0467 | 290.6191 | 116.0461 | 186.3354 | 229.7854 | 212.1073
705.1917 | 91.4859 | 291.1794 | 116.3087 | 187.2384 | 230.1804 | 212.2058
706.1917 | 91.4943 | 291.9515 | 116.5938 | 188.0422 | 229.5452 | 211.9746
707.2073 | 91.3127 | 291.5079 | 116.579 | 188.8819 | 230.2467 | 212.0442
708.1917 | 91.6285 | 291.6743 | 116.9479 | 189.17 | 230.6655 | 212.3977
709.2073 | 91.6987 | 291.7774 | 116.9966 | 190.556 | 229.8597 | 211.771
710.1917 | 91.9563 | 291.8359 | 117.1996 | 191.8817 | 232.5212 | 211.9232
711.2073 | 91.7428 | 292.4216 | 117.2805 | 194.6765 | 233.7733 | 214.5383
712.1917 | 91.7652 | 292.3182 | 117.3951 | 194.3137 | 234.3324 | 214.9031
713.1917 | 91.7426 | 292.5703 | 117.7987 | 194.1519 | 234.7623 | 214.9784
714.1917 | 91.8915 | 292.8352 | 117.753 | 194.8479 | 235.4382 | 214.0065
715.1917 | 91.834 | 292.8241 | 117.9345 | 193.8521 | 236.1902 | 213.6145
716.1917 | 91.8571 | 292.9694 | 118.3232 | 195.3204 | 237.6092 | 215.3464
717.1917 | 91.8991 | 293.4159 | 118.5278 | 198.0484 | 238.0764 | 217.2221
718.1917 | 92.1938 | 293.4832 | 118.5143 | 197.9792 | 237.9144 | 217.9183
719.1917 | 92.1549 | 293.4041 | 118.71 | 197.9482 | 239.137 | 217.8784
720.1917 | 92.2852 | 293.5475 | 118.8712 | 198.9198 | 240.7123 | 217.9576
721.1917 | 92.2561 | 293.8169 | 119.1105 | 198.2932 | 241.2723 | 216.8637
722.1917 | 92.1701 | 293.9934 | 119.3369 | 197.3145 | 241.7531 | 216.5723
723.1917 | 92.2661 | 293.9954 | 119.4145 | 200.1939 | 241.7469 | 217.3481
724.1917 | 92.2774 | 294.5645 | 119.8538 | 200.693 | 242.3844 | 217.9861
725.2073 | 92.3412 | 294.854 | 119.9296 | 199.9005 | 241.8907 | 217.439
726.1917 | 92.5558 | 294.9983 | 120.6043 | 199.3602 | 240.4069 | 216.3787
727.1917 | 92.7007 | 295.2779 | 120.403 | 198.6739 | 238.8817 | 215.2442
728.1917 | 93.0461 | 295.1159 | 120.6014 | 197.8612 | 238.2043 | 214.4154
729.1917 | 93.2991 | 295.1575 | 120.8637 | 197.2933 | 237.96 | 213.9434
730.1917 | 93.1056 | 295.6095 | 121.2381 | 196.522 | 238.2871 | 214.608
731.1917 | 93.217 | 295.7564 | 121.2852 | 196.7192 | 238.2637 | 214.0399
732.1917 | 93.2897 | 295.7488 | 121.3793 | 197.264 | 239.62 | 213.6643
733.1917 | 93.3486 | 296.4887 | 121.6252 | 199.9937 | 240.4662 | 214.0968
734.1917 | 93.5978 | 296.5459 | 121.9153 | 200.8277 | 240.2559 | 213.3376
735.1917 | 93.6855 | 296.4709 | 121.903 | 200.467 | 240.0849 | 213.5129
736.1917 | 93.7833 | 296.4183 | 122.0238 | 200.4242 | 241.3301 | 214.2767
737.1917 | 93.7091 | 296.5438 | 122.6582 | 200.0593 | 241.7166 | 213.9504
738.1917 | 93.7838 | 297.0604 | 122.7775 | 201.3781 | 241.1686 | 215.2549
739.1917 | 93.7877 | 297.1804 | 122.7463 | 201.618 | 240.3087 | 215.0993
740.1917 | 93.8884 | 297.0428 | 122.8307 | 200.8214 | 240.3118 | 214.7261
741.1917 | 93.9951 | 297.2187 | 123.0326 | 202.0119 | 241.6409 | 216.6144
742.1917 | 93.998 | 297.3232 | 123.1511 | 202.1146 | 242.55 | 216.9953
743.1917 | 93.99 | 297.5584 | 123.503 | 203.1917 | 241.7016 | 218.5455
744.1917 | 94.1915 | 297.6778 | 123.5231 | 202.6618 | 241.1018 | 218.1714
745.1917 | 94.6134 | 297.699 | 123.6821 | 203.944 | 242.063 | 218.2792
746.1917 | 94.7484 | 297.9912 | 124.1591 | 204.0472 | 242.5605 | 217.8361
747.1917 | 94.4695 | 298.0699 | 124.4374 | 203.0992 | 241.5359 | 218.1967
748.1917 | 94.4227 | 298.032 | 124.5422 | 203.8725 | 240.2526 | 218.2794
749.1917 | 94.7741 | 298.2461 | 124.5206 | 203.0352 | 239.6106 | 218.3863
750.1917 | 94.7847 | 298.6716 | 124.5442 | 202.4446 | 240.51 | 218.4704
751.1917 | 94.7186 | 298.6227 | 124.8796 | 203.1241 | 240.6647 | 217.8108
752.1917 | 94.9832 | 299.0953 | 125.1942 | 202.1436 | 240.8653 | 217.1414
753.1917 | 94.907 | 299.0996 | 125.4498 | 203.1532 | 239.9409 | 216.2931
754.1917 | 94.9948 | 299.1863 | 125.6892 | 204.5907 | 240.0365 | 216.4477
755.1917 | 95.0558 | 299.2074 | 125.8729 | 204.5678 | 239.0017 | 215.4121
756.1917 | 95.1856 | 299.2887 | 125.9993 | 206.1581 | 238.4369 | 214.5931
757.1917 | 95.1945 | 299.4843 | 126.2398 | 206.8874 | 238.0724 | 213.8309
758.1917 | 95.3313 | 299.5316 | 126.6813 | 207.6719 | 238.2855 | 213.8696
759.1917 | 95.4933 | 299.5532 | 126.6618 | 207.1558 | 237.3669 | 213.1323
760.1917 | 95.7858 | 299.6283 | 126.9788 | 207.8614 | 238.3691 | 212.7128
761.1917 | 95.8115 | 299.7518 | 126.8081 | 208.2224 | 240.0147 | 212.1452
762.1917 | 95.8261 | 300.1134 | 126.9913 | 208.7391 | 241.409 | 211.7284
763.1917 | 96.0212 | 300.5215 | 127.2952 | 208.7932 | 241.8831 | 211.8162
764.1917 | 96.3012 | 300.4537 | 127.4891 | 207.4677 | 241.6283 | 212.0995
765.1917 | 96.1621 | 300.5305 | 127.5972 | 208.0468 | 240.7598 | 212.6819
766.1917 | 96.1781 | 300.6844 | 127.7223 | 206.9257 | 240.8225 | 211.8546
767.1917 | 96.1472 | 300.5375 | 127.8728 | 209.3394 | 241.2768 | 212.534
768.1917 | 96.2251 | 300.6585 | 127.9396 | 210.4159 | 241.5154 | 214.5897
769.1917 | 96.4509 | 300.8568 | 128.1942 | 211.2273 | 243.048 | 215.3529
770.1917 | 96.4522 | 300.9535 | 128.3189 | 211.6755 | 243.2136 | 215.8142
771.1917 | 96.4581 | 301.0912 | 128.4918 | 211.4253 | 243.7996 | 215.1151
772.1917 | 96.4701 | 301.4011 | 128.6861 | 212.8252 | 244.9788 | 216.3498
773.1917 | 96.6492 | 301.3212 | 128.803 | 212.1599 | 245.0253 | 217.3306
774.1917 | 96.7866 | 301.3552 | 129.055 | 212.9125 | 245.2182 | 218.1198
775.1917 | 97.1192 | 301.7246 | 129.1936 | 214.6331 | 246.0478 | 218.8135
776.1917 | 97.1862 | 301.9391 | 129.2266 | 213.4242 | 247.142 | 218.1063
777.1917 | 97.5173 | 302.1525 | 129.4153 | 212.2704 | 246.973 | 217.6075
778.1917 | 97.2841 | 302.1102 | 129.5726 | 212.4219 | 247.2901 | 217.659
779.1917 | 97.2923 | 302.1855 | 129.6061 | 213.5209 | 248.1449 | 219.4906
780.1917 | 97.3702 | 302.5002 | 129.8243 | 214.8351 | 247.5562 | 220.0948
781.1917 | 97.4081 | 302.8112 | 129.9696 | 213.802 | 248.5927 | 220.0752
782.1917 | 97.7751 | 303.5559 | 130.3555 | 212.9057 | 249.2265 | 221.1764
783.1917 | 98.1074 | 304.139 | 130.5377 | 211.9417 | 248.2693 | 220.1995
784.1917 | 98.0829 | 304.2377 | 130.5348 | 210.2146 | 246.5996 | 218.8456
785.1917 | 98.257 | 304.5035 | 130.6245 | 208.8926 | 246.7217 | 218.3705
786.1917 | 98.2813 | 304.3688 | 130.7181 | 207.5244 | 246.0895 | 218.5615
787.1917 | 98.2304 | 304.3939 | 130.8921 | 206.2904 | 244.783 | 218.3023
788.1917 | 98.3088 | 304.3694 | 131.3428 | 205.6492 | 244.1741 | 218.8044
789.1917 | 98.3052 | 305.0996 | 131.5206 | 205.9043 | 244.0058 | 219.1296
790.1917 | 98.3673 | 305.3137 | 131.5811 | 204.6452 | 243.5603 | 219.0149
791.1917 | 98.5491 | 304.8724 | 131.8161 | 204.392 | 242.4145 | 219.1122
792.1917 | 98.6967 | 305.3585 | 131.9139 | 204.5293 | 242.1373 | 219.6225
793.1917 | 98.8251 | 305.7847 | 132.0412 | 203.1434 | 242.3032 | 221.5576
794.1917 | 98.7464 | 305.977 | 132.4206 | 202.4998 | 241.9185 | 222.0552
795.1917 | 98.8294 | 305.8239 | 132.4122 | 201.8904 | 242.0732 | 222.2063
796.1917 | 99.1254 | 305.9571 | 132.5246 | 201.5659 | 242.5151 | 222.5463
797.1917 | 99.4387 | 306.0965 | 132.6453 | 201.7103 | 242.8935 | 222.1822
798.1917 | 99.5926 | 306.9191 | 132.8978 | 201.4526 | 243.22 | 221.9454
799.1917 | 99.4103 | 307.1012 | 133.0668 | 201.0856 | 243.369 | 221.2601
800.1917 | 99.521 | 307.9955 | 133.3286 | 200.2512 | 244.3413 | 221.2048
801.1917 | 99.724 | 308.0539 | 133.5288 | 200.0598 | 244.0813 | 220.6278
802.1917 | 100.0886 | 308.1966 | 133.8052 | 199.0154 | 242.5514 | 220.1652
803.1917 | 100.1117 | 308.1813 | 134.0561 | 198.752 | 241.2351 | 219.5188
804.1917 | 100.2784 | 308.4694 | 134.1912 | 197.882 | 240.7772 | 219.5029
805.1917 | 100.228 | 308.531 | 134.3704 | 198.0824 | 240.2532 | 219.1596
806.1917 | 100.2787 | 309.119 | 134.4093 | 198.3577 | 239.2891 | 219.3869
807.1917 | 100.4385 | 309.0919 | 134.4932 | 197.7926 | 237.8451 | 218.9017
808.1917 | 100.7971 | 309.4809 | 134.6076 | 197.3774 | 237.3762 | 219.4159
809.1917 | 101.0275 | 309.7722 | 134.8656 | 197.3871 | 236.5293 | 219.4593
810.1917 | 101.0047 | 310.0146 | 135.1199 | 196.7766 | 235.3903 | 219.2952
811.1917 | 101.322 | 310.4731 | 135.0745 | 196.2874 | 234.6379 | 218.9438
812.1917 | 101.55 | 310.4435 | 135.2794 | 196.0179 | 234.4022 | 218.9599
813.1917 | 101.4709 | 310.5082 | 135.4978 | 195.8288 | 233.6928 | 218.9697
814.1917 | 101.3659 | 310.6722 | 135.6845 | 194.706 | 232.8818 | 218.6021
815.1917 | 101.6231 | 310.6119 | 136.038 | 194.7125 | 232.379 | 218.0981
816.1917 | 101.7873 | 311.1502 | 136.1379 | 193.4267 | 232.7671 | 217.7577
817.1917 | 101.78 | 311.4118 | 136.1794 | 193.138 | 232.5013 | 218.4138
818.1917 | 101.832 | 311.2877 | 136.2055 | 193.1653 | 232.1616 | 217.8382
819.1917 | 101.8924 | 311.5001 | 136.3546 | 192.5614 | 232.8941 | 217.7607
820.1917 | 101.9979 | 311.899 | 136.5385 | 192.2577 | 234.7719 | 218.1935
821.1917 | 102.028 | 312.2276 | 136.7931 | 192.8509 | 236.1399 | 217.9505
822.1917 | 102.1266 | 312.1712 | 136.8894 | 192.9089 | 236.1659 | 218.4182
823.1917 | 102.3804 | 312.7716 | 137.1151 | 194.1779 | 236.5324 | 218.0755
824.1917 | 102.4149 | 312.955 | 137.2247 | 194.0158 | 237.1855 | 217.8117
825.1917 | 102.3447 | 312.823 | 137.4657 | 193.8007 | 236.1781 | 217.5442
826.1917 | 102.5809 | 312.9163 | 137.5498 | 194.219 | 236.4879 | 217.2697
827.1917 | 102.6376 | 312.9647 | 137.6705 | 193.9145 | 236.5718 | 218.2093
828.1917 | 102.6667 | 313.2085 | 137.8766 | 193.5958 | 236.8962 | 218.522
829.1917 | 102.6493 | 313.2953 | 138.0523 | 193.5781 | 238.1721 | 218.9468
830.1917 | 102.8894 | 313.6754 | 138.1632 | 194.6287 | 238.2903 | 220.0143
831.1917 | 102.8175 | 313.6377 | 138.2835 | 194.8781 | 239.0541 | 220.4447
832.1917 | 102.9114 | 313.8363 | 138.4232 | 194.531 | 240.0483 | 220.3312
833.1917 | 103.1573 | 314.0347 | 138.4828 | 195.1904 | 240.6419 | 219.6418
834.1917 | 103.1887 | 314.3251 | 138.6435 | 195.7802 | 239.4381 | 220.5826
835.1917 | 103.2486 | 314.8454 | 138.9591 | 196.0072 | 239.9455 | 219.9619
836.1917 | 103.2416 | 314.9265 | 139.0987 | 195.986 | 239.5107 | 220.3937
837.1917 | 103.5444 | 315.1882 | 139.2374 | 196.092 | 239.7243 | 220.3146
838.1917 | 103.6673 | 315.2631 | 139.3917 | 196.914 | 239.9659 | 220.6314
839.1917 | 104.0048 | 315.5858 | 139.4732 | 197.8534 | 240.1819 | 219.7777
840.1917 | 104.13 | 315.8541 | 139.4911 | 199.0797 | 240.5312 | 219.7472
841.1917 | 104.0729 | 315.8683 | 139.6405 | 199.7668 | 240.7962 | 219.096
842.1917 | 104.4817 | 316.234 | 139.7893 | 199.9466 | 240.0131 | 218.7131
843.1917 | 104.6975 | 316.5316 | 140.034 | 199.2407 | 239.1208 | 219.5494
844.1917 | 104.4745 | 316.4214 | 140.1041 | 198.807 | 238.4499 | 219.1289
845.2073 | 104.3646 | 316.6581 | 140.3571 | 198.6598 | 238.5563 | 218.7041
846.1917 | 104.5652 | 317.2897 | 140.475 | 198.3015 | 238.4519 | 219.0533
847.1917 | 104.6435 | 317.1427 | 140.7602 | 196.8768 | 237.8324 | 219.3924
848.1917 | 104.885 | 317.4732 | 141.0255 | 196.0521 | 237.7695 | 218.9119
849.1917 | 105.1303 | 317.6222 | 141.2035 | 195.9398 | 237.1381 | 218.7353
850.1917 | 105.232 | 318.2737 | 141.36 | 196.0478 | 237.3321 | 218.859
851.1917 | 105.2257 | 318.4654 | 141.6134 | 197.0052 | 238.1268 | 218.2111
852.1917 | 105.2353 | 318.1508 | 141.8007 | 196.6486 | 238.1875 | 218.3071
853.1917 | 105.2734 | 318.7598 | 141.867 | 197.2141 | 238.1971 | 218.9826
854.1917 | 105.4406 | 318.9561 | 141.9945 | 198.1978 | 238.6424 | 220.2996
855.1917 | 105.5649 | 319.0462 | 142.1613 | 198.7068 | 239.1072 | 220.2701
856.1917 | 105.5781 | 319.135 | 142.3368 | 198.7039 | 239.2385 | 220.305
857.1917 | 105.7298 | 319.3846 | 142.4104 | 199.2829 | 240.121 | 220.0186
858.1917 | 105.9413 | 319.5463 | 142.5527 | 199.73 | 241.5016 | 220.5236
859.1917 | 106.1575 | 319.9717 | 142.8348 | 199.9327 | 241.4659 | 220.8612
860.1917 | 106.0896 | 320.148 | 142.9679 | 199.2482 | 241.308 | 221.044
861.1917 | 106.0663 | 320.3812 | 143.0185 | 199.0011 | 240.5737 | 220.4563
862.1917 | 106.3138 | 320.1835 | 143.2736 | 199.5395 | 240.2458 | 220.3374
863.1917 | 106.7516 | 320.496 | 143.5339 | 200.098 | 241.9343 | 219.9202
864.1917 | 106.7273 | 320.6866 | 143.4529 | 200.8988 | 242.2154 | 220.6612
865.1917 | 106.7657 | 321.0213 | 143.7598 | 201.2298 | 242.5288 | 221.3415
866.1917 | 106.7166 | 321.2194 | 143.9661 | 201.3783 | 242.5801 | 220.7231
867.1917 | 106.9002 | 321.372 | 144.0739 | 201.6972 | 242.6733 | 221.0915
868.1917 | 106.8517 | 321.69 | 144.135 | 201.4125 | 241.2576 | 222.1211
869.1917 | 107.1436 | 321.575 | 144.2211 | 200.5932 | 240.3334 | 221.7873
870.1917 | 107.2892 | 321.8069 | 144.6938 | 199.8079 | 239.2492 | 221.2039
871.1917 | 107.4206 | 321.931 | 144.8253 | 199.5916 | 238.7687 | 220.3253
872.1917 | 107.319 | 322.1634 | 144.9677 | 199.4319 | 238.3062 | 220.138
873.1917 | 107.3664 | 322.4668 | 145.2637 | 199.1749 | 237.9024 | 219.6783
874.1917 | 107.7362 | 322.5457 | 145.2789 | 199.5625 | 238.5158 | 220.146
875.1917 | 107.9906 | 322.8077 | 145.4562 | 199.3759 | 238.3743 | 220.4509
876.1917 | 107.8403 | 323.3173 | 145.5751 | 200.5354 | 238.8754 | 221.1522
877.1917 | 107.8522 | 323.1222 | 145.7136 | 200.3072 | 239.3211 | 220.9192
878.1917 | 108.0482 | 323.4307 | 146.1451 | 200.4865 | 237.9415 | 220.5573
879.1917 | 108.3666 | 323.605 | 146.1589 | 200.2225 | 237.2593 | 220.6065
880.1917 | 108.4539 | 323.7539 | 146.3461 | 199.8305 | 237.3776 | 220.6327
881.1917 | 108.5354 | 323.7256 | 146.5046 | 199.4703 | 236.4905 | 220.3285
882.2073 | 108.4662 | 323.9087 | 146.5275 | 199.6755 | 236.2137 | 220.8317
883.1917 | 108.6468 | 324.454 | 146.5592 | 200.667 | 236.5426 | 220.8826
884.1917 | 108.639 | 324.5083 | 146.8034 | 200.4683 | 236.7932 | 220.1821
885.1917 | 108.746 | 324.5014 | 146.9276 | 199.9167 | 236.6264 | 220.1074
886.1917 | 108.9716 | 324.6453 | 146.9872 | 200.4053 | 237.3982 | 220.0828
887.1917 | 108.9092 | 324.6679 | 147.078 | 200.5551 | 238.6831 | 220.0531
888.1917 | 108.8509 | 324.6931 | 147.1531 | 201.6419 | 240.5853 | 221.8903
889.1917 | 108.9204 | 324.9722 | 147.3176 | 204.9072 | 242.9588 | 222.5061
890.1917 | 108.9203 | 325.1106 | 147.4469 | 206.8564 | 244.2936 | 225.423
891.1917 | 108.9615 | 325.2333 | 147.5832 | 207.9435 | 244.8721 | 225.9146
892.1917 | 109.3266 | 325.3306 | 147.8168 | 207.4881 | 245.0077 | 228.3656
893.1917 | 109.6588 | 325.3781 | 147.9411 | 208.7661 | 245.0007 | 230.0291
894.1917 | 109.7959 | 325.5534 | 148.1463 | 210.995 | 245.8711 | 229.5041
895.1917 | 109.8597 | 326.0756 | 148.4726 | 214.6943 | 246.8952 | 231.9505
896.1917 | 109.804 | 325.8701 | 148.5194 | 215.4222 | 247.7516 | 232.0097
897.1917 | 109.6826 | 325.951 | 148.7236 | 215.2512 | 248.0332 | 231.8415
898.1917 | 109.7694 | 326.5418 | 148.8971 | 215.1422 | 248.7865 | 232.8079
899.1917 | 109.9856 | 326.6162 | 149.1431 | 215.256 | 248.7654 | 231.9888
900.1917 | 109.8045 | 326.5072 | 149.2004 | 214.2716 | 248.7789 | 231.6014
901.1917 | 109.8209 | 326.6949 | 149.7283 | 214.5395 | 248.9105 | 231.7488
902.1917 | 110.0319 | 327.1768 | 149.6973 | 214.8204 | 249.3398 | 230.5964
903.1917 | 110.4354 | 328.1808 | 149.7554 | 213.9644 | 250.567 | 229.9527
904.1917 | 110.7043 | 328.1413 | 149.8566 | 213.1384 | 249.2127 | 229.2392
905.1917 | 110.802 | 328.4976 | 150.0817 | 212.1388 | 248.585 | 229.1864
906.1917 | 110.8569 | 328.6067 | 150.1297 | 212.1095 | 247.8387 | 229.3604
907.1917 | 110.9115 | 328.575 | 150.2933 | 211.5684 | 248.199 | 229.4502
908.1917 | 111.1134 | 328.7979 | 150.4477 | 210.8846 | 249.0746 | 230.0713
909.1917 | 111.1661 | 329.433 | 150.625 | 210.1166 | 249.7601 | 231.3103
910.1917 | 111.3176 | 329.9417 | 150.9883 | 209.6077 | 250.7065 | 231.921
911.1917 | 111.3371 | 329.501 | 150.9853 | 209.7227 | 251.4717 | 231.4088
912.2073 | 111.3337 | 329.6203 | 151.0305 | 208.675 | 252.4002 | 231.4415
913.1917 | 111.5601 | 329.7333 | 151.3942 | 208.6875 | 252.8358 | 231.358
914.1917 | 112.1107 | 330.2006 | 151.5964 | 209.4065 | 254.3362 | 232.2105
915.1917 | 112.0146 | 330.6344 | 151.7356 | 208.6307 | 255.5423 | 233.3607
916.1917 | 112.0541 | 330.7886 | 151.9683 | 209.9256 | 256.3124 | 233.6173
917.1917 | 112.078 | 331.2483 | 152.0932 | 210.4358 | 257.2233 | 234.4758
918.1917 | 112.0869 | 331.6068 | 152.1647 | 209.7482 | 257.3553 | 235.7
919.1917 | 112.3342 | 331.8189 | 152.3016 | 208.5688 | 256.9044 | 235.4713
920.1917 | 112.6407 | 332.4325 | 152.521 | 207.6855 | 257.7698 | 235.4751
921.1917 | 112.8614 | 332.57 | 152.7406 | 207.3298 | 258.5862 | 235.3447
922.1917 | 112.9397 | 332.8396 | 152.9529 | 208.0419 | 258.9987 | 235.7718
923.1917 | 112.873 | 332.6471 | 153.0968 | 208.1257 | 258.3725 | 235.7036
924.1917 | 112.99 | 332.8893 | 153.2418 | 208.9676 | 258.5102 | 236.3486
925.1917 | 113.1718 | 333.1416 | 153.4992 | 209.3539 | 258.4016 | 235.6837
926.1917 | 113.2214 | 333.074 | 153.6685 | 209.8142 | 260.4663 | 235.5466
927.1917 | 113.4315 | 332.9591 | 153.9691 | 213.8724 | 262.901 | 238.8864
928.1917 | 113.4475 | 333.3678 | 154.4933 | 215.6737 | 263.7826 | 240.8291
929.1917 | 113.4365 | 333.2926 | 154.6347 | 215.7798 | 265.4983 | 240.7353
930.1917 | 113.429 | 333.3361 | 154.7257 | 215.6785 | 267.161 | 242.3108
931.1917 | 113.4265 | 333.5663 | 154.7318 | 217.8976 | 268.4995 | 243.6362
932.1917 | 113.705 | 333.8395 | 155.16 | 218.9973 | 269.2934 | 244.6255
933.1917 | 113.6907 | 334 | 155.2341 | 221.9602 | 270.1139 | 244.9812
934.1917 | 113.8215 | 334.314 | 155.4068 | 223.4844 | 272.462 | 245.4616
935.1917 | 114.1711 | 334.7291 | 155.7234 | 223.259 | 273.9327 | 246.5889
936.1917 | 114.3406 | 334.5981 | 155.9582 | 223.2148 | 273.7577 | 246.9894
937.1917 | 114.4067 | 334.7976 | 156.0158 | 224.4644 | 273.7374 | 246.9449
938.1917 | 114.394 | 334.9261 | 156.0358 | 228.8008 | 276.3241 | 248.1318
939.1917 | 114.5322 | 335.0775 | 156.3927 | 229.8349 | 277.5502 | 248.0204
940.1917 | 114.6298 | 335.0722 | 156.5708 | 231.0608 | 277.6198 | 247.6004
941.1917 | 114.528 | 335.0976 | 157.3344 | 233.618 | 278.5805 | 246.9362
942.1917 | 114.6377 | 335.3991 | 157.2433 | 235.1001 | 279.6406 | 247.6901
943.1917 | 114.8195 | 336.3637 | 157.6273 | 234.3596 | 280.4029 | 246.7211
944.1917 | 114.9883 | 336.0846 | 157.7392 | 233.4688 | 280.2787 | 245.3611
945.1917 | 115.137 | 336.5741 | 157.6961 | 233.0919 | 280.9687 | 246.4868
946.1917 | 115.2242 | 336.6681 | 157.7408 | 232.5736 | 281.7755 | 246.938
947.1917 | 115.4289 | 336.9323 | 157.9911 | 233.4551 | 282.8051 | 247.1581
948.1917 | 115.5338 | 337.5032 | 158.3398 | 232.6892 | 284.0919 | 248.2299
949.1917 | 115.686 | 337.6425 | 158.4404 | 231.8191 | 284.3666 | 247.4574
950.1917 | 115.8841 | 337.6429 | 158.5891 | 230.8702 | 283.597 | 248.7842
951.1917 | 116.0972 | 337.5 | 158.7642 | 230.0931 | 283.4851 | 249.4754
952.1917 | 116.0281 | 337.713 | 158.8207 | 229.2838 | 283.2761 | 250.077
953.1917 | 116.3836 | 338.2342 | 159.0848 | 229.5787 | 283.4265 | 250.4114
954.1917 | 116.6699 | 338.3134 | 159.2085 | 228.9257 | 284.5884 | 251.6118
955.1917 | 116.8278 | 339.1391 | 159.4222 | 228.5117 | 283.7648 | 252.2195
956.1917 | 116.8002 | 339.2265 | 159.3973 | 227.2648 | 282.4583 | 251.9787
957.1917 | 116.8681 | 339.7731 | 159.6673 | 225.9667 | 280.8714 | 252.0016
958.1917 | 116.8882 | 339.9485 | 159.934 | 226.9889 | 281.3859 | 251.3202
959.1917 | 116.9344 | 339.8784 | 160.2397 | 226.2463 | 280.8093 | 250.8508
960.1917 | 116.9372 | 340.0903 | 160.3398 | 226.0789 | 280.642 | 250.4459
961.1917 | 117.1724 | 339.9692 | 160.6255 | 225.8285 | 280.9143 | 250.8997
962.1917 | 117.3433 | 340.7936 | 160.9236 | 227.2286 | 281.5869 | 251.0127
963.1917 | 117.465 | 341.2227 | 161.3807 | 227.2352 | 281.1702 | 252.2409
964.1917 | 117.6334 | 340.9766 | 161.2847 | 226.1432 | 279.9471 | 251.485
965.1917 | 118.0727 | 341.2541 | 161.5586 | 225.2566 | 278.2049 | 250.8179
966.1917 | 118.172 | 341.3481 | 161.7388 | 223.9753 | 278.1339 | 250.6926
967.1917 | 118.0769 | 341.2111 | 161.7978 | 223.831 | 279.5895 | 249.9183
968.1917 | 117.9872 | 341.2413 | 162.3067 | 225.1484 | 279.6293 | 251.2275
969.1917 | 117.8609 | 341.6562 | 162.5707 | 226.4416 | 279.2322 | 250.3838
970.1917 | 118.165 | 341.9433 | 162.8979 | 227.8009 | 280.1698 | 250.4633
971.1917 | 118.2184 | 341.8515 | 162.8906 | 229.7145 | 282.2558 | 251.0151
972.2073 | 118.3036 | 341.9864 | 163.2302 | 234.247 | 283.2191 | 252.7294
973.1917 | 118.3796 | 342.0389 | 163.28 | 234.9335 | 285.1688 | 255.3762
974.1917 | 118.8531 | 342.2271 | 163.3029 | 236.5455 | 285.3011 | 256.6327
975.1917 | 118.8013 | 342.4661 | 163.4328 | 238.575 | 285.7304 | 256.736
976.1917 | 118.7584 | 342.7969 | 163.5817 | 240.1374 | 287.9127 | 256.5933
977.1917 | 118.9921 | 342.8802 | 163.7443 | 239.5318 | 288.9108 | 257.8794
978.1917 | 118.9929 | 343.0738 | 164.0599 | 240.5175 | 288.7883 | 258.792
979.1917 | 118.9408 | 343.1988 | 164.1881 | 240.3941 | 288.9074 | 257.8091
980.1917 | 119.215 | 343.725 | 164.5087 | 242.0466 | 290.5199 | 258.49
981.1917 | 119.2227 | 343.5815 | 164.638 | 242.9202 | 291.5268 | 257.9165
982.1917 | 119.4803 | 343.6487 | 164.8866 | 241.3979 | 291.979 | 259.5469
983.1917 | 119.488 | 344.0525 | 165.074 | 241.5638 | 292.4941 | 260.9796
984.1917 | 119.5632 | 343.8003 | 165.138 | 240.445 | 291.0588 | 260.5507
985.1917 | 119.7489 | 344.405 | 165.2834 | 239.8702 | 290.1895 | 260.0031
986.1917 | 119.9355 | 344.3711 | 165.4883 | 239.6661 | 290.9678 | 258.8194
987.1917 | 119.8999 | 344.5027 | 165.5587 | 240.3971 | 291.8316 | 257.8758
988.1917 | 119.9022 | 344.5878 | 165.7746 | 239.7026 | 292.02 | 258.5416
989.1917 | 119.9139 | 344.71 | 166.0605 | 239.3174 | 291.6646 | 258.1895
990.1917 | 120.1729 | 345.0951 | 166.5525 | 238.4973 | 291.4682 | 258.0125
991.1917 | 120.2313 | 345.1371 | 166.6613 | 238.4308 | 290.9322 | 257.4444
992.1917 | 120.3741 | 345.7922 | 166.9823 | 237.8422 | 290.8718 | 256.7493
993.1917 | 120.3531 | 345.5275 | 167.1202 | 237.6413 | 290.0697 | 256.6784
994.1917 | 120.3899 | 345.4386 | 167.1201 | 237.8101 | 290.307 | 256.9401
995.1917 | 120.4829 | 345.6602 | 167.1968 | 236.277 | 289.9219 | 257.3319
996.1917 | 120.8743 | 346.4588 | 167.3927 | 236.6538 | 290.5382 | 257.4575
997.1917 | 121.0722 | 346.1171 | 167.5536 | 237.0601 | 291.655 | 258.6562
998.1917 | 120.9323 | 346.3023 | 167.7917 | 237.896 | 293.1094 | 258.8738
999.1917 | 120.9929 | 346.4837 | 168.2429 | 240.7547 | 295.1368 | 260.7895
1000.1917 | 121.0851 | 346.9157 | 168.2856 | 241.6408 | 295.574 | 262.0106
1001.1917 | 121.3482 | 347.0511 | 168.392 | 241.0357 | 294.6901 | 261.4154
1002.1917 | 121.3141 | 347.422 | 168.7052 | 240.8283 | 294.614 | 260.8867
1003.1917 | 121.4492 | 347.7187 | 168.8487 | 240.2963 | 293.679 | 260.7357
1004.1917 | 121.5458 | 348.3848 | 169.0629 | 240.3439 | 294.3227 | 260.9145
1005.1917 | 121.5976 | 348.3533 | 169.2671 | 239.1628 | 293.5902 | 259.9899
1006.1917 | 121.9789 | 348.3862 | 169.4434 | 238.5076 | 293.9995 | 259.9022
1007.1917 | 122.3893 | 349.3837 | 169.5647 | 237.5278 | 292.6638 | 259.4347
1008.1917 | 122.6678 | 349.8491 | 169.6605 | 236.3321 | 291.1717 | 258.8847
1009.1917 | 122.7579 | 349.2892 | 169.9246 | 235.7465 | 291.1533 | 259.1549
1010.1917 | 122.5708 | 349.2493 | 170.1052 | 236.2427 | 292.4759 | 261.1654
1011.1917 | 122.5384 | 349.308 | 170.1732 | 237.1238 | 292.3624 | 262.1749
1012.1917 | 122.5725 | 349.4911 | 170.4307 | 237.9821 | 293.733 | 263.6662
1013.1917 | 122.6055 | 349.7822 | 170.7655 | 239.0115 | 294.455 | 263.8639
1014.1917 | 122.7757 | 349.8653 | 170.7078 | 239.3926 | 294.7413 | 264.3742
1015.1917 | 122.9621 | 349.9079 | 170.9572 | 239.4799 | 295.2001 | 266.6266
1016.1917 | 122.9287 | 350.0893 | 171.1835 | 241.4478 | 295.946 | 268.7512
1017.1917 | 123.0886 | 350.5837 | 171.4463 | 241.675 | 296.578 | 269.1061
1018.1917 | 123.0657 | 350.7409 | 171.6836 | 242.5353 | 297.1382 | 268.7196
1019.1917 | 123.2492 | 350.8362 | 171.967 | 243.4093 | 298.1015 | 269.3774
1020.1917 | 123.2682 | 350.9032 | 171.8612 | 244.4873 | 299.619 | 270.1901
1021.1917 | 123.4413 | 351.5285 | 172.357 | 244.2364 | 299.6698 | 269.4631
1022.1917 | 123.6744 | 351.5463 | 172.4284 | 243.8892 | 300.23 | 269.0634
1023.1917 | 123.8042 | 352.1729 | 172.5376 | 243.606 | 299.9573 | 269.051
1024.1917 | 124.094 | 352.6432 | 172.9178 | 242.8983 | 300.0178 | 267.986
1025.1917 | 124.2555 | 352.9899 | 173.0656 | 242.4982 | 299.9004 | 267.6201
1026.1917 | 124.1726 | 353.0398 | 173.2913 | 242.2018 | 300.1276 | 266.7511
1027.1917 | 124.2189 | 353.1866 | 173.6584 | 242.3287 | 300.0262 | 265.8813
1028.1917 | 124.2079 | 352.9247 | 173.5871 | 242.1492 | 300.8008 | 266.7642
1029.1917 | 124.1996 | 352.9864 | 173.6442 | 244.2839 | 301.1409 | 266.6681
1030.1917 | 124.3924 | 353.5795 | 174.0716 | 243.7193 | 301.2956 | 268.7666
1031.1917 | 124.473 | 353.8028 | 174.1047 | 242.9735 | 301.6373 | 268.7725
1032.2073 | 124.6188 | 354.0045 | 174.3704 | 245.0391 | 302.0128 | 269.738
1033.1917 | 124.8951 | 353.913 | 174.5433 | 244.1904 | 301.9211 | 268.5815
1034.1917 | 125.0178 | 354.1595 | 174.9369 | 244.7354 | 301.3844 | 269.6154
1035.1917 | 125.1406 | 354.735 | 175.118 | 244.0771 | 300.6654 | 268.7217
1036.1917 | 125.5033 | 355.1648 | 175.2685 | 246.9337 | 301.7926 | 268.3903
1037.1917 | 125.4485 | 355.2038 | 175.4617 | 247.9288 | 302.6654 | 267.1816
1038.1917 | 125.6272 | 355.1916 | 175.5165 | 249.8111 | 304.2676 | 269.6948
1039.1917 | 125.6106 | 355.2222 | 175.6398 | 251.9796 | 305.9108 | 272.1134
1040.1917 | 125.6526 | 355.3158 | 176.0344 | 252.2491 | 307.1307 | 272.8525
1041.1917 | 125.6823 | 355.4268 | 176.1279 | 252.228 | 309.2752 | 273.1033
1042.1917 | 125.7328 | 356.0181 | 176.4699 | 254.1574 | 310.2319 | 273.6741
1043.2073 | 125.9192 | 357.1617 | 176.8986 | 254.664 | 310.7065 | 273.3761
1044.1917 | 126.1071 | 357.5942 | 177.1735 | 253.696 | 310.2525 | 272.4835
1045.1917 | 126.1823 | 357.772 | 177.1907 | 252.8292 | 310.1002 | 271.6783
1046.1917 | 126.4239 | 357.6627 | 177.3643 | 252.6895 | 311.0168 | 271.1843
1047.1917 | 126.8031 | 358.5167 | 177.7404 | 252.0009 | 311.3421 | 271.1174
1048.1917 | 126.7142 | 358.3233 | 177.7952 | 250.3439 | 309.9746 | 270.318
1049.1917 | 126.563 | 358.0928 | 177.8859 | 248.6281 | 309.0585 | 270.3908
1050.1917 | 126.7466 | 359.0017 | 178.2807 | 248.4689 | 309.3109 | 271.9988
1051.1917 | 127.2481 | 360.3206 | 178.3981 | 250.471 | 309.8244 | 275.1332
1052.1917 | 127.68 | 361.0802 | 178.8603 | 250.4505 | 311.1783 | 274.4892
1053.2073 | 128.0074 | 360.9445 | 179.0175 | 249.2675 | 311.073 | 274.3794
1054.1917 | 127.9008 | 361.3599 | 179.228 | 248.5966 | 310.1847 | 274.7369
1055.1917 | 127.957 | 361.9254 | 179.7264 | 248.1617 | 311.3393 | 275.359
1056.1917 | 128.2558 | 362.116 | 179.7798 | 248.7532 | 311.4546 | 274.882
1057.1917 | 128.3929 | 362.4831 | 179.9475 | 248.4536 | 312.5524 | 274.6318
1058.1917 | 128.4259 | 362.8543 | 180.0869 | 248.3932 | 313.6409 | 275.2563
1059.1917 | 128.5041 | 363.2364 | 180.3979 | 247.0962 | 314.8529 | 274.829
1060.1917 | 128.5094 | 363.4435 | 180.6327 | 247.5682 | 315.7385 | 275.2144
1061.1917 | 128.606 | 363.006 | 180.7129 | 247.9989 | 315.4627 | 275.4149
1062.1917 | 129.0199 | 363.8981 | 181.6363 | 250.6155 | 315.8385 | 277.0253
1063.2073 | 128.8911 | 364.2969 | 181.7577 | 251.651 | 316.4881 | 277.7196
1064.1917 | 128.9317 | 364.557 | 182.0571 | 250.9396 | 317.5459 | 276.9624
1065.1917 | 128.894 | 364.4923 | 182.1387 | 252.8283 | 318.9989 | 280.4598
1066.1917 | 129.0015 | 365.6184 | 182.7044 | 257.6975 | 320.7513 | 281.5073
1067.1917 | 129.3515 | 366.9707 | 182.826 | 259.5752 | 323.4711 | 283.6178
1068.1917 | 129.5603 | 367.3081 | 182.8636 | 258.3082 | 325.5059 | 283.9582
1069.1917 | 129.878 | 367.9507 | 183.4843 | 256.8263 | 326.0907 | 283.9176
1070.1917 | 130.0847 | 368.1296 | 183.3188 | 255.9538 | 326.8226 | 284.3981
1071.1917 | 130.4954 | 368.1835 | 183.4906 | 254.7413 | 327.3663 | 284.6604
1072.1917 | 130.7704 | 369.0165 | 183.9034 | 254.6603 | 328.9349 | 286.5164
1073.1917 | 130.7797 | 369.2616 | 184.1562 | 254.4486 | 329.0807 | 286.4166
1074.1917 | 130.9297 | 369.1926 | 184.2856 | 253.8096 | 328.4397 | 287.0179
1075.1917 | 130.9321 | 368.9069 | 184.5164 | 255.5479 | 328.8315 | 287.1978
1076.1917 | 130.8681 | 369.5797 | 184.9927 | 257.3585 | 329.8025 | 288.3965
1077.1917 | 131.1499 | 370.2604 | 185.314 | 257.8449 | 330.9742 | 289.6876
1078.1917 | 131.1293 | 370.3678 | 185.5294 | 258.4765 | 330.6708 | 289.3278
1079.1917 | 131.2453 | 370.1901 | 185.9867 | 262.2083 | 332.2951 | 290.6515
1080.1917 | 131.3898 | 371.1235 | 186.1881 | 262.6353 | 333.5815 | 292.0674
1081.1917 | 131.42 | 371.0438 | 186.0431 | 262.7815 | 334.6148 | 291.7953
1082.1917 | 131.667 | 370.9551 | 186.1545 | 263.7006 | 337.2921 | 291.284
1083.1917 | 131.6877 | 371.0699 | 186.7494 | 266.8999 | 339.622 | 289.6394
1084.1917 | 131.6901 | 371.1612 | 186.7139 | 267.2917 | 340.8838 | 288.4909
1085.1917 | 131.7878 | 371.3723 | 187.1021 | 267.3099 | 342.7793 | 286.9272
1086.1917 | 131.8305 | 371.5525 | 187.5643 | 268.6662 | 345.5373 | 285.0071
1087.1917 | 131.9043 | 371.8462 | 187.6893 | 269.7192 | 347.762 | 283.7371
1088.1917 | 132.2263 | 372.1787 | 187.7252 | 268.5287 | 347.1273 | 282.5359
1089.1917 | 132.2559 | 372.2681 | 187.7899 | 267.6627 | 345.283 | 280.7022
1090.1917 | 132.3888 | 372.5347 | 188.1122 | 267.3376 | 344.4269 | 280.5474
1091.1917 | 132.343 | 372.5948 | 188.306 | 267.4558 | 343.5041 | 279.8579
1092.2073 | 132.4533 | 372.8252 | 188.4015 | 270.0924 | 343.2756 | 278.4814
1093.1917 | 132.3995 | 372.9078 | 188.4449 | 269.2493 | 341.3367 | 278.7004
1094.1917 | 132.6133 | 373.7003 | 189.1603 | 270.5779 | 339.7719 | 278.7865
1095.1917 | 132.8206 | 374.0148 | 189.5498 | 269.3447 | 338.4574 | 277.8661
1096.1917 | 133.0153 | 373.7925 | 189.9384 | 269.5926 | 338.1458 | 277.7117
1097.1917 | 133.0063 | 374.2188 | 189.9905 | 269.5024 | 337.8429 | 276.9951
1098.1917 | 133.2613 | 375.1784 | 190.3053 | 268.81 | 338.003 | 276.9095
1099.1917 | 133.2731 | 374.9432 | 190.9074 | 270.0143 | 336.9246 | 276.2108
1100.1917 | 133.2805 | 375.0651 | 191.2352 | 269.9219 | 337.472 | 275.7019
1101.1917 | 133.4695 | 375.1029 | 191.8023 | 269.7342 | 336.0584 | 274.9923
1102.1917 | 133.4964 | 375.0749 | 191.4007 | 271.7973 | 336.0576 | 274.318
1103.1917 | 133.7207 | 375.3358 | 191.5639 | 273.5547 | 337.2328 | 273.2524
1104.1917 | 134.117 | 375.5216 | 192.0227 | 275.4248 | 337.1416 | 273.2102
1105.1917 | 134.3053 | 375.6826 | 192.6814 | 276.2388 | 338.8854 | 273.8554
1106.1917 | 134.1736 | 376.1365 | 192.9439 | 276.4436 | 340.4152 | 274.3591
1107.1917 | 134.3757 | 376.6106 | 192.8582 | 278.399 | 340.4707 | 274.6072
1108.1917 | 134.3103 | 377.0922 | 193.0625 | 278.1851 | 340.9658 | 273.8151
1109.1917 | 134.3983 | 376.8796 | 193.2733 | 278.5958 | 341.1873 | 274.2301
1110.1917 | 134.48 | 377.0634 | 193.3016 | 278.7414 | 341.5449 | 273.7761
1111.1917 | 134.6521 | 377.2538 | 193.6254 | 278.4427 | 341.0022 | 274.5414
1112.1917 | 134.7903 | 378.0953 | 193.9125 | 277.2497 | 340.0561 | 274.4063
1113.1917 | 134.8021 | 378.1942 | 194.1162 | 277.1279 | 339.0134 | 273.8586
1114.1917 | 134.9727 | 378.4158 | 194.375 | 277.9846 | 339.7217 | 274.6934
1115.1917 | 134.9669 | 378.8576 | 194.7688 | 277.7772 | 340.6371 | 274.4288
1116.1917 | 135.1478 | 379.3609 | 194.9946 | 278.0398 | 339.0675 | 275.4048
1117.1917 | 135.4349 | 380.1296 | 195.2862 | 277.1296 | 339.8588 | 275.7425
1118.1917 | 135.6912 | 380.4905 | 195.6836 | 276.4173 | 339.1433 | 275.3375
1119.1917 | 136.0471 | 380.7857 | 195.6287 | 275.4263 | 337.3151 | 274.0127
1120.1917 | 136.2224 | 381.2467 | 195.7981 | 274.6375 | 336.5088 | 274.8681
1121.1917 | 136.2443 | 381.4177 | 196.1278 | 273.7834 | 338.1357 | 275.6639
1122.1917 | 136.1652 | 381.3941 | 196.1738 | 274.2865 | 337.4378 | 276.8996
1123.1917 | 136.1583 | 381.2669 | 196.792 | 275.1768 | 336.4462 | 277.6225
1124.1917 | 136.1558 | 381.2556 | 197.0123 | 278.5134 | 336.7462 | 279.0217
1125.1917 | 136.2815 | 381.8736 | 197.2221 | 279.0481 | 336.5428 | 279.0378
1126.1917 | 136.4172 | 382.3747 | 197.6447 | 280.884 | 338.5193 | 278.4628
1127.1917 | 136.4263 | 382.192 | 197.6453 | 280.4538 | 337.6512 | 277.019
1128.1917 | 136.6094 | 382.3816 | 197.8343 | 281.9873 | 337.8358 | 278.9134
1129.1917 | 136.6918 | 382.8678 | 198.1193 | 282.357 | 337.9442 | 279.338
1130.1917 | 136.8936 | 383.3386 | 198.2092 | 279.8799 | 337.4059 | 279.2432
1131.1917 | 137.1835 | 384.2191 | 198.5136 | 277.7856 | 338.2117 | 280.2735
1132.1917 | 137.3451 | 384.0711 | 198.6934 | 277.7369 | 339.249 | 281.053
1133.1917 | 137.4298 | 384.5206 | 198.8734 | 276.8864 | 340.2057 | 281.3463
1134.1917 | 137.5697 | 384.5757 | 199.018 | 276.2896 | 343.1431 | 282.507
1135.1917 | 137.5841 | 384.8083 | 199.2496 | 275.1924 | 341.9719 | 282.1574
1136.1917 | 137.9398 | 385.4905 | 199.6163 | 274.7039 | 342.4336 | 282.5187
1137.1917 | 138.1048 | 385.469 | 199.5856 | 274.823 | 343.8213 | 282.6356
1138.1917 | 138.1766 | 385.8753 | 199.7211 | 273.9736 | 345.5252 | 283.0289
1139.1917 | 138.1902 | 386.07 | 200.048 | 275.5057 | 346.9614 | 284.9832
1140.1917 | 138.319 | 386.6939 | 200.289 | 274.7827 | 346.3552 | 284.9055
1141.1917 | 138.5043 | 386.7357 | 200.4501 | 273.9059 | 345.5831 | 284.8903
1142.1917 | 138.4009 | 386.9322 | 200.7978 | 273.4644 | 344.8394 | 284.9553
1143.1917 | 138.3811 | 387.3705 | 200.9654 | 272.6673 | 344.3629 | 285.0292
1144.1917 | 138.7043 | 387.7324 | 200.9952 | 270.7516 | 342.9892 | 285.6448
1145.1917 | 138.7482 | 388.022 | 201.1672 | 269.3182 | 345.0609 | 286.4381
1146.1917 | 139.1284 | 389.0956 | 201.445 | 267.605 | 343.9325 | 285.7713
1147.1917 | 139.2905 | 388.7755 | 201.6014 | 265.5896 | 341.442 | 285.2674
1148.1917 | 139.4437 | 389.5749 | 201.8939 | 265.0596 | 339.4771 | 284.6353
1149.1917 | 139.2818 | 389.4158 | 202.1202 | 263.3177 | 340.5562 | 285.4112
1150.1917 | 139.3292 | 390.0022 | 202.296 | 262.7315 | 342.3294 | 285.8415
1151.1917 | 139.8746 | 390.0524 | 202.4814 | 262.1702 | 341.2576 | 284.8987
1152.1917 | 139.8713 | 390.1506 | 202.5889 | 262.8245 | 341.4154 | 285.5878
1153.1917 | 139.9841 | 390.3869 | 202.8746 | 262.473 | 339.5632 | 285.65
1154.1917 | 140.0225 | 390.4624 | 203.0016 | 262.1086 | 338.5343 | 286.3751
1155.1917 | 140.5045 | 390.7274 | 203.2884 | 262.0025 | 338.5687 | 287.9163
1156.1917 | 140.3002 | 390.8663 | 203.4194 | 265.0646 | 339.735 | 290.1484
1157.1917 | 140.3592 | 390.8419 | 203.6642 | 266.4708 | 340.17 | 290.2387
1158.1917 | 140.3699 | 391.1454 | 203.8176 | 268.2217 | 340.3705 | 291.1106
1159.1917 | 140.548 | 391.4988 | 204.0776 | 267.7096 | 341.9908 | 291.6803
1160.1917 | 140.818 | 391.8093 | 204.4326 | 268.1105 | 342.2064 | 292.897
1161.1917 | 140.8224 | 392.4368 | 204.7321 | 268.3736 | 342.3919 | 292.3685
1162.1917 | 140.9118 | 392.4802 | 204.9213 | 267.4282 | 341.4052 | 293.1388
1163.1917 | 141.0399 | 392.6399 | 205.1858 | 268.1719 | 341.8222 | 293.2451
1164.1917 | 141.0819 | 392.6943 | 205.3398 | 269.6218 | 342.4328 | 295.5002
1165.1917 | 141.1346 | 392.7604 | 205.6503 | 272.2548 | 343.0325 | 296.7145
1166.1917 | 141.1837 | 393.2983 | 205.7978 | 272.5301 | 343.413 | 297.3489
1167.1917 | 141.4932 | 393.5751 | 206.0939 | 275.235 | 345.1778 | 298.822
1168.1917 | 141.6756 | 394.0699 | 206.3088 | 274.5655 | 345.6589 | 299.082
1169.1917 | 141.5931 | 394.6019 | 206.4592 | 275.072 | 346.5015 | 299.9095
1170.1917 | 141.7011 | 394.9798 | 206.8095 | 273.998 | 347.9447 | 299.1979
1171.1917 | 141.9919 | 395.2105 | 206.9122 | 274.0187 | 347.6343 | 298.9214
1172.1917 | 142.1098 | 395.1888 | 207.1382 | 274.309 | 347.8119 | 300.4083
1173.1917 | 142.2243 | 395.3843 | 207.2784 | 274.5 | 347.7392 | 300.904
1174.1917 | 142.2774 | 395.6602 | 207.5005 | 277.2838 | 348.8453 | 301.9612
1175.1917 | 142.5619 | 395.6501 | 207.5015 | 279.1646 | 350.6452 | 302.5904
1176.1917 | 142.7055 | 396.0245 | 207.7645 | 278.428 | 350.8171 | 303.1438
1177.1917 | 142.7325 | 396.3775 | 208.0379 | 278.3025 | 352.0966 | 303.5421
1178.1917 | 142.756 | 396.654 | 208.395 | 278.136 | 353.489 | 304.0492
1179.1917 | 142.8325 | 396.5726 | 208.494 | 277.676 | 354.3988 | 303.672
1180.1917 | 142.7849 | 396.7493 | 208.6089 | 279.6531 | 355.6554 | 303.9338
1181.1917 | 143.0606 | 397.4495 | 209.0926 | 280.3056 | 355.442 | 303.8586
1182.1917 | 143.337 | 397.2493 | 209.0791 | 280.0193 | 355.4059 | 302.14
1183.1917 | 143.3063 | 397.7153 | 209.2181 | 282.2404 | 354.4049 | 302.8065
1184.1917 | 143.4957 | 398.34 | 209.5195 | 281.4998 | 354.4866 | 301.8101
1185.1917 | 143.5303 | 398.1733 | 209.7079 | 281.1097 | 355.2107 | 302.3465
1186.1917 | 143.7256 | 398.461 | 209.8881 | 281.8336 | 356.0797 | 303.8232
1187.1917 | 143.8193 | 398.8501 | 210.0582 | 282.1234 | 356.2937 | 303.7684
1188.1917 | 143.7236 | 399.186 | 210.4228 | 281.4554 | 356.7902 | 304.1049
1189.1917 | 143.852 | 399.233 | 210.4808 | 283.1492 | 356.7106 | 303.8402
1190.1917 | 144.1301 | 399.5959 | 210.6129 | 284.0917 | 356.5698 | 304.6918
1191.1917 | 144.1703 | 400.0378 | 210.8694 | 285.9896 | 356.6662 | 304.9399
1192.1917 | 144.5095 | 400.3721 | 211.4919 | 284.3074 | 357.3639 | 306.0451
1193.1917 | 144.6599 | 400.8821 | 211.5291 | 285.6715 | 357.9342 | 305.4512
1194.1917 | 144.7927 | 401.3179 | 211.8222 | 286.851 | 358.4025 | 305.8147
1195.1917 | 144.6971 | 401.5405 | 211.9454 | 286.5156 | 358.3306 | 304.8257
1196.1917 | 144.8332 | 401.9645 | 212.3806 | 284.2368 | 357.0449 | 303.6417
1197.1917 | 144.9278 | 402.2246 | 212.5813 | 284.9618 | 356.848 | 302.6849
1198.1917 | 145.1332 | 401.9649 | 212.7787 | 284.2801 | 357.1492 | 303.5724
1199.1917 | 145.1003 | 402.7787 | 212.9881 | 284.0105 | 358.0992 | 303.4335
1200.1917 | 145.2063 | 403.5057 | 213.258 | 284.0724 | 359.6867 | 302.3901
1201.1917 | 145.4936 | 403.6592 | 213.5356 | 284.7158 | 361.7845 | 304.0247
1202.1917 | 145.6971 | 403.6623 | 213.6381 | 285.0703 | 363.129 | 305.1298
1203.1917 | 145.7553 | 403.8639 | 213.7669 | 285.0001 | 362.8096 | 307.2314
1204.1917 | 145.9842 | 404.6165 | 213.9925 | 286.5246 | 362.8083 | 309.4401
1205.1917 | 146.3287 | 406.0487 | 214.4168 | 286.7257 | 364.5014 | 309.5251
1206.1917 | 146.5336 | 406.0592 | 214.9948 | 286.3223 | 364.8658 | 309.3346
1207.1917 | 146.5875 | 406.0116 | 215.0324 | 286.4849 | 365.4375 | 308.438
1208.1917 | 146.6279 | 405.8153 | 215.0624 | 285.8747 | 363.4537 | 307.6033
1209.1917 | 146.8042 | 406.1527 | 215.2862 | 285.3542 | 362.241 | 307.2995
1210.1917 | 147.0427 | 406.5865 | 215.3312 | 285.9363 | 362.172 | 307.1295
1211.1917 | 147.2714 | 406.9599 | 215.6019 | 284.9343 | 362.2501 | 308.6897
1212.1917 | 147.2929 | 407.4069 | 215.7763 | 284.836 | 362.2819 | 308.6146
1213.1917 | 147.5527 | 408.2312 | 216.1088 | 284.0562 | 362.5695 | 309.3429
1214.1917 | 147.7036 | 408.42 | 216.3144 | 284.1298 | 363.6769 | 309.1115
1215.1917 | 147.9299 | 408.7818 | 216.7223 | 282.7608 | 364.712 | 309.3686
1216.1917 | 148.0089 | 408.9362 | 216.8579 | 282.4766 | 364.4569 | 307.5407
1217.1917 | 147.9037 | 409.2727 | 217.0434 | 281.772 | 364.4657 | 307.273
1218.1917 | 147.9829 | 410.3318 | 217.2744 | 281.6504 | 364.6497 | 307.3387
1219.1917 | 148.2355 | 410.4763 | 217.6823 | 281.333 | 366.0546 | 308.0104
1220.1917 | 148.2655 | 410.6869 | 217.9109 | 281.9471 | 367.269 | 308.5353
1221.1917 | 148.6523 | 410.8667 | 218.1882 | 283.2317 | 366.4556 | 308.356
1222.1917 | 148.6838 | 411.3531 | 218.4883 | 283.8232 | 366.539 | 309.2562
1223.1917 | 148.7938 | 411.4936 | 218.7098 | 283.4585 | 366.1477 | 308.7831
1224.1917 | 148.851 | 412.3147 | 218.8807 | 285.6164 | 366.9986 | 308.1132
1225.1917 | 148.82 | 412.6534 | 218.8769 | 286.0806 | 366.7542 | 309.0115
1226.1917 | 148.8481 | 413.0443 | 219.3903 | 285.5683 | 366.278 | 308.8091
1227.1917 | 149.0764 | 413.1484 | 219.6448 | 285.6189 | 365.2413 | 307.9909
1228.1917 | 149.2999 | 413.437 | 219.9333 | 284.5616 | 362.5774 | 305.8745
1229.1917 | 149.5677 | 413.6816 | 220.0312 | 285.1153 | 361.9392 | 304.8812
1230.1917 | 149.5532 | 413.9971 | 220.4345 | 284.4145 | 362.6534 | 303.2697
1231.1917 | 149.7007 | 414.5421 | 220.4911 | 284.3796 | 363.3546 | 304.9859
1232.1917 | 149.7391 | 415.0031 | 220.8345 | 284.6884 | 364.4195 | 305.3155
1233.1917 | 149.8231 | 414.88 | 220.7934 | 285.6701 | 366.1915 | 306.0344
1234.1917 | 149.9968 | 415.1899 | 220.9363 | 285.4432 | 367.6545 | 306.6915
1235.1917 | 150.2306 | 415.6926 | 221.269 | 286.1819 | 368.0619 | 306.504
1236.1917 | 150.3206 | 415.8845 | 221.677 | 287.6798 | 368.2853 | 305.997
1237.1917 | 150.3107 | 415.7611 | 221.8439 | 287.6845 | 367.3085 | 306.0382
1238.1917 | 150.441 | 416.4587 | 221.9577 | 287.8542 | 366.5979 | 306.9948
1239.1917 | 150.6259 | 416.6314 | 222.0074 | 287.8894 | 366.3701 | 308.0101
1240.1917 | 150.7396 | 416.7648 | 222.2645 | 287.7252 | 366.8365 | 307.4946
1241.1917 | 150.7519 | 417.4375 | 222.5825 | 288.1163 | 368.4042 | 309.6366
1242.1917 | 150.9203 | 417.5837 | 222.686 | 290.0448 | 370.9213 | 310.4671
1243.1917 | 151.0004 | 417.7072 | 223.0987 | 290.6757 | 372.8436 | 312.0634
1244.1917 | 150.9669 | 417.8788 | 223.1726 | 290.4182 | 372.8892 | 311.8153
1245.1917 | 150.8953 | 418.0734 | 223.361 | 291.5696 | 373.1074 | 313.3305
1246.1917 | 151.1192 | 418.8985 | 223.5004 | 292.834 | 374.0937 | 314.3536
1247.1917 | 151.5357 | 419.2281 | 223.795 | 293.2829 | 374.6932 | 315.7405
1248.1917 | 151.6017 | 419.6178 | 224.0608 | 293.2477 | 374.2532 | 316.5004
1249.1917 | 151.7088 | 419.7705 | 224.3367 | 293.5572 | 375.1291 | 316.7013
1250.1917 | 151.7552 | 419.8522 | 225.1463 | 292.8743 | 375.4903 | 316.2684
1251.1917 | 151.9399 | 420.5067 | 225.1187 | 293.5051 | 374.8782 | 315.5581
1252.1917 | 152.2839 | 420.5901 | 225.3178 | 293.1023 | 374.1319 | 314.2604
1253.1917 | 152.2896 | 420.7878 | 225.428 | 293.5676 | 373.4531 | 314.1429
1254.1917 | 152.3164 | 421.1195 | 225.9088 | 293.4123 | 372.7002 | 313.9753
1255.1917 | 152.4588 | 421.5324 | 226.0893 | 293.4636 | 372.4755 | 313.9661
1256.1917 | 152.7848 | 421.5922 | 226.0892 | 292.7568 | 371.9736 | 312.8835
1257.1917 | 152.7526 | 421.6941 | 226.2466 | 294.0438 | 372.098 | 312.6498
1258.1917 | 152.8691 | 422.0219 | 226.4849 | 294.4454 | 372.6626 | 312.8344
1259.1917 | 152.8721 | 422.0951 | 226.7534 | 295.6752 | 373.097 | 314.2489
1260.1917 | 152.9446 | 422.2222 | 226.8859 | 297.8027 | 375.0418 | 315.4201
1261.1917 | 153.0048 | 422.6076 | 227.1473 | 298.1489 | 375.7705 | 317.5424
1262.1917 | 153.3384 | 422.99 | 227.3556 | 298.2004 | 376.4737 | 317.7147
1263.1917 | 153.3688 | 423.2892 | 227.8068 | 298.8025 | 375.9241 | 316.5132
1264.1917 | 153.6271 | 424.0689 | 228.1022 | 300.4394 | 375.4049 | 316.4802
1265.1917 | 153.5868 | 424.1419 | 228.3657 | 300.6653 | 375.5384 | 316.1122
1266.1917 | 153.8362 | 424.4901 | 228.673 | 300.1857 | 374.5973 | 314.1781
1267.1917 | 153.8588 | 424.6255 | 228.6638 | 301.7874 | 374.2754 | 313.9797
1268.1917 | 153.9657 | 424.8619 | 229.1048 | 300.6593 | 374.8534 | 315.5445
1269.1917 | 154.1665 | 425.3154 | 229.1766 | 301.8864 | 375.6724 | 315.0645
1270.1917 | 154.2919 | 425.5687 | 229.6326 | 303.2801 | 376.188 | 314.6085
1271.1917 | 154.3384 | 426.2 | 229.8517 | 304.091 | 375.4766 | 313.5303
1272.1917 | 154.3837 | 425.8672 | 229.7632 | 303.1171 | 374.9181 | 315.7596
1273.1917 | 154.5436 | 426.6299 | 229.9912 | 304.8431 | 376.4956 | 315.7916
1274.1917 | 154.7007 | 426.9038 | 230.2202 | 305.1505 | 380.5354 | 316.3069
1275.1917 | 154.9074 | 427.131 | 230.4363 | 305.9549 | 382.4407 | 318.429
1276.1917 | 154.9632 | 427.9801 | 230.7405 | 306.1387 | 384.9632 | 318.9564
1277.1917 | 155.1303 | 428.5504 | 231.0311 | 305.2569 | 387.1865 | 319.5483
1278.1917 | 155.5097 | 429.2361 | 231.1639 | 303.7687 | 388.986 | 321.1691
1279.1917 | 155.6741 | 429.1283 | 231.8416 | 305.364 | 390.4431 | 321.3878
1280.1917 | 155.7617 | 429.2738 | 232.0575 | 303.5653 | 389.4001 | 321.468
1281.1917 | 155.7386 | 429.3113 | 232.0371 | 304.5071 | 389.0404 | 321.9178
1282.1917 | 155.9948 | 430.1179 | 232.2596 | 308.062 | 390.9929 | 321.4328
1283.1917 | 156.1236 | 430.6003 | 232.4223 | 308.3226 | 391.4846 | 320.0758
1284.1917 | 156.2252 | 430.2826 | 232.4656 | 307.6844 | 390.8704 | 320.6766
1285.1917 | 156.3801 | 430.509 | 232.6181 | 306.947 | 391.1086 | 321.9129
1286.1917 | 156.6221 | 431.024 | 232.8979 | 310.2716 | 393.3872 | 322.5201
1287.1917 | 156.6421 | 430.9986 | 233.222 | 310.9745 | 393.4741 | 325.1996
1288.1917 | 156.6827 | 431.536 | 233.3952 | 312.0014 | 392.4585 | 325.4407
1289.1917 | 156.7593 | 432.0482 | 233.4235 | 311.6614 | 392.6186 | 326.0869
1290.1917 | 157.0593 | 432.4676 | 233.805 | 312.0823 | 392.9901 | 327.3963
1291.1917 | 157.0992 | 432.6931 | 234.1502 | 312.5786 | 392.6508 | 327.4586
1292.1917 | 157.4397 | 432.9619 | 234.2734 | 312.2123 | 392.9483 | 327.8441
1293.1917 | 157.8163 | 433.6911 | 234.5126 | 311.9687 | 393.1874 | 326.8539
1294.1917 | 157.7285 | 433.7588 | 234.9007 | 312.4057 | 394.3138 | 327.6328
1295.1917 | 157.784 | 433.6848 | 235.0402 | 310.9865 | 395.4629 | 327.4511
1296.1917 | 157.8491 | 434.02 | 235.1724 | 311.6528 | 394.825 | 327.7634
1297.1917 | 157.9945 | 434.7924 | 235.5007 | 312.6612 | 396.6886 | 328.364
1298.1917 | 158.3323 | 436.0297 | 235.7809 | 311.8689 | 395.3756 | 328.0446
1299.1917 | 158.7001 | 437.3484 | 236.2531 | 312.3484 | 397.1736 | 328.4423
1300.1917 | 158.8663 | 437.138 | 236.3313 | 313.6131 | 402.7335 | 328.7088
1301.1917 | 159.1449 | 437.8046 | 236.4807 | 313.5018 | 407.4217 | 331.1143
1302.1917 | 159.2812 | 438.2065 | 236.6972 | 314.5882 | 409.0453 | 331.829
1303.1917 | 159.2738 | 437.8921 | 236.8248 | 313.7241 | 408.3651 | 332.6979
1304.1917 | 159.1955 | 438.771 | 237.2613 | 312.7461 | 410.0442 | 333.9123
1305.1917 | 159.273 | 437.9801 | 237.396 | 313.9602 | 411.2832 | 332.473
1306.1917 | 159.299 | 437.909 | 237.5657 | 312.4255 | 408.5182 | 332.627
1307.1917 | 159.3981 | 438.4471 | 237.9595 | 312.0189 | 407.3593 | 331.3754
1308.1917 | 159.6367 | 438.6244 | 238.2346 | 315.9976 | 406.4293 | 330.7941
1309.1917 | 159.9455 | 438.6723 | 238.3577 | 317.9187 | 405.6108 | 331.3035
1310.1917 | 159.9467 | 439.6541 | 238.5837 | 320.0051 | 404.2721 | 331.4662
1311.1917 | 160.1614 | 439.8388 | 239.0788 | 321.0765 | 406.8393 | 335.6446
1312.1917 | 160.1343 | 439.9795 | 239.6941 | 321.8687 | 408.4221 | 337.1448
1313.1917 | 160.1357 | 440.1709 | 239.7313 | 322.3831 | 410.1929 | 336.1397
1314.1917 | 160.3758 | 440.7678 | 239.6873 | 324.6952 | 413.1571 | 335.354
1315.1917 | 160.757 | 441.9677 | 240.0238 | 323.5491 | 413.6962 | 336.0371
1316.1917 | 160.9727 | 442.6306 | 240.1737 | 323.9788 | 415.0162 | 335.9112
1317.1917 | 161.0584 | 442.891 | 240.4015 | 322.8026 | 417.7844 | 336.7506
1318.1917 | 161.2218 | 443.2725 | 240.5488 | 322.2899 | 418.7995 | 336.7231
1319.1917 | 161.4175 | 443.6363 | 240.7542 | 322.4021 | 420.8274 | 337.7042
1320.1917 | 161.5419 | 444.4607 | 241.0646 | 321.4063 | 423.0523 | 338.2855
1321.1917 | 161.6188 | 444.771 | 241.3133 | 322.4767 | 425.0794 | 338.1524
1322.1917 | 161.786 | 444.7917 | 241.4734 | 323.5361 | 425.1141 | 337.0379
1323.1917 | 162.0944 | 445.5445 | 241.7472 | 324.0402 | 426.5891 | 337.746
1324.1917 | 162.1697 | 445.8374 | 242.1449 | 325.7579 | 428.5417 | 336.4361
1325.1917 | 162.412 | 445.682 | 242.2435 | 326.7484 | 427.7925 | 336.8972
1326.1917 | 162.5401 | 445.6944 | 242.5369 | 328.3578 | 427.852 | 338.0805
1327.1917 | 162.5468 | 445.652 | 242.5181 | 327.7031 | 429.6429 | 336.5828
1328.1917 | 162.6072 | 446.3291 | 242.7052 | 327.4781 | 429.3911 | 335.544
1329.1917 | 162.7369 | 446.2485 | 243.0274 | 327.5038 | 427.0094 | 335.5849
1330.1917 | 162.7163 | 446.9137 | 243.6321 | 326.9056 | 425.8683 | 338.0224
1331.1917 | 162.7895 | 448.0737 | 243.875 | 327.7447 | 426.5702 | 340.5576
1332.1917 | 162.965 | 447.7377 | 243.9041 | 328.6193 | 426.6041 | 341.9377
1333.1917 | 163.1147 | 448.217 | 244.1834 | 328.9525 | 424.7302 | 343.2273
1334.1917 | 163.2331 | 447.8034 | 244.2719 | 329.6175 | 422.6342 | 343.4953
1335.1917 | 163.3614 | 448.0552 | 244.5929 | 331.1182 | 430.6813 | 346.0921
1336.1917 | 163.4362 | 448.3508 | 244.9096 | 331.5495 | 432.2929 | 344.2981
1337.1917 | 163.5453 | 448.6623 | 245.2242 | 331.5863 | 432.8393 | 342.9004
1338.1917 | 163.7731 | 448.5905 | 245.41 | 332.1537 | 432.9827 | 340.6763
1339.1917 | 163.7955 | 449.2855 | 245.4864 | 334.8687 | 431.5795 | 340.2177
1340.1917 | 164.1427 | 449.9353 | 245.9074 | 334.861 | 430.2022 | 340.6241
1341.1917 | 164.2835 | 450.021 | 246.3378 | 334.1013 | 430.5981 | 341.0163
1342.1917 | 164.4525 | 449.9621 | 246.7019 | 334.9373 | 431.8314 | 339.7915
1343.1917 | 164.4077 | 450.2302 | 246.9566 | 335.6162 | 432.8207 | 339.6522
1344.1917 | 164.8238 | 451.1009 | 246.9921 | 335.4594 | 433.4219 | 338.7458
1345.1917 | 164.7526 | 451.4435 | 247.1354 | 337.5032 | 436.5041 | 339.1671
1346.1917 | 164.903 | 452.4331 | 247.5384 | 337.1951 | 436.3305 | 338.4605
1347.1917 | 165.2176 | 451.9519 | 247.8053 | 338.8499 | 437.6866 | 340.4163
1348.1917 | 165.2878 | 451.9494 | 247.8434 | 338.8998 | 439.3612 | 341.0485
1349.1917 | 165.7921 | 452.6719 | 248.2491 | 340.0265 | 444.7212 | 342.9956
1350.1917 | 165.8979 | 452.6872 | 248.5253 | 339.7416 | 444.8313 | 343.4131
1351.1917 | 165.8458 | 453.1556 | 248.8148 | 342.8339 | 447.7685 | 344.86
1352.1917 | 165.9983 | 453.7958 | 249.0165 | 343.2418 | 450.9331 | 345.394
1353.1917 | 166.0084 | 453.8991 | 249.574 | 342.4779 | 449.4037 | 345.8289
1354.1917 | 165.9783 | 454.2149 | 249.6437 | 346.1638 | 450.9596 | 345.9253
1355.1917 | 166.1557 | 453.9843 | 249.7285 | 349.3567 | 451.6801 | 346.44
1356.1917 | 166.3114 | 454.1859 | 249.9274 | 347.9918 | 454.0998 | 345.5092
1357.1917 | 166.3906 | 453.9743 | 250.4607 | 346.1591 | 452.2184 | 342.9066
1358.1917 | 166.4848 | 454.0895 | 250.6784 | 344.5018 | 448.9614 | 340.4225
1359.1917 | 166.7924 | 454.8661 | 251.0411 | 346.8563 | 450.4687 | 339.4429
1360.1917 | 167.0416 | 455.3668 | 251.0398 | 345.7468 | 453.325 | 338.9693
1361.1917 | 167.1354 | 456.1356 | 251.3739 | 346.9311 | 456.4953 | 337.8248
1362.1917 | 167.3673 | 456.5991 | 251.4924 | 347.5352 | 457.7547 | 339.6985
1363.1917 | 167.3779 | 456.6241 | 251.705 | 346.6623 | 458.9408 | 340.6143
1364.1917 | 167.3797 | 457.2325 | 252.0778 | 348.4914 | 460.4094 | 342.77
1365.1917 | 167.6274 | 456.9215 | 252.397 | 350.6672 | 461.7333 | 342.4788
1366.1917 | 167.8662 | 457.2894 | 252.6205 | 352.1477 | 461.041 | 341.4582
1367.1917 | 168.0479 | 457.7216 | 253.2229 | 356.7696 | 463.0093 | 342.1319
1368.1917 | 168.014 | 458.2506 | 253.2455 | 359.7254 | 464.1233 | 344.3282
1369.1917 | 168.2578 | 458.6623 | 253.5124 | 358.6046 | 469.891 | 347.4454
1370.1917 | 168.7126 | 459.2974 | 253.8673 | 359.6896 | 471.8625 | 349.3863
1371.1917 | 168.8115 | 459.5324 | 253.9245 | 361.2706 | 474.2184 | 350.0663
1372.1917 | 169.2407 | 459.7918 | 254.2715 | 361.1247 | 476.4403 | 349.0683
1373.1917 | 169.4392 | 460.2735 | 254.5534 | 360.5641 | 477.0868 | 349.9612
1374.1917 | 169.4731 | 460.3214 | 254.763 | 361.3833 | 479.2449 | 352.2821
1375.1917 | 169.742 | 461.1278 | 255.0631 | 362.4173 | 484.3471 | 353.0622
1376.1917 | 169.9332 | 461.7055 | 255.4786 | 362.2538 | 486.1129 | 351.457
1377.1917 | 170.1295 | 461.7196 | 255.7465 | 364.7807 | 492.8324 | 352.0852
1378.1917 | 170.175 | 461.9377 | 255.6826 | 363.4733 | 496.773 | 352.7926
1379.1917 | 170.5348 | 462.9693 | 255.9627 | 364.7957 | 495.1963 | 354.2169
1380.1917 | 170.3797 | 462.5646 | 256.3441 | 366.7853 | 495.3544 | 356.2828
1381.1917 | 170.6201 | 462.2032 | 256.5511 | 368.4382 | 493.4521 | 359.1796
1382.1917 | 170.4355 | 462.4804 | 256.826 | 368.5431 | 488.5182 | 359.459
1383.1917 | 170.6119 | 463.1757 | 257.1704 | 367.3627 | 487.9369 | 357.5422
1384.1917 | 170.7894 | 463.7514 | 257.4133 | 365.6406 | 485.4197 | 357.8777
1385.1917 | 170.97 | 463.3529 | 257.7151 | 366.4411 | 482.1868 | 356.8255
1386.1917 | 171.0917 | 463.7871 | 257.7237 | 365.5289 | 480.3239 | 357.8266
1387.1917 | 171.0845 | 464.3536 | 258.2651 | 367.6834 | 484.557 | 361.5745
1388.1917 | 171.2234 | 464.4623 | 258.2857 | 370.0466 | 485.566 | 361.8831
1389.1917 | 171.7539 | 465.6882 | 258.5946 | 370.8909 | 488.0038 | 364.366
1390.1917 | 172.2238 | 465.591 | 258.9737 | 370.1666 | 486.8191 | 368.2758
1391.1917 | 172.0541 | 465.4694 | 259.3992 | 369.9481 | 485.5652 | 368.6313
1392.1917 | 172.1276 | 465.8338 | 259.7187 | 371.4768 | 487.7973 | 371.4336
1393.1917 | 172.1006 | 465.8894 | 260.0569 | 373.6199 | 486.3114 | 371.0228
1394.1917 | 172.1155 | 465.9462 | 260.3205 | 373.9742 | 483.0993 | 370.6289
1395.1917 | 172.3235 | 466.9122 | 260.489 | 374.1133 | 481.7227 | 370.0796
1396.1917 | 172.6662 | 467.7934 | 260.7883 | 376.4674 | 486.9194 | 372.1928
1397.1917 | 173.1104 | 468.7249 | 261.086 | 376.996 | 491.5318 | 371.6461
1398.1917 | 173.045 | 468.2151 | 261.1661 | 377.8453 | 499.5113 | 372.9786
1399.1917 | 173.2533 | 468.7643 | 261.5694 | 380.1777 | 503.161 | 374.956
1400.1917 | 173.5172 | 468.9252 | 262.1917 | 380.5057 | 506.4136 | 374.0335
1401.1917 | 173.8074 | 469.8554 | 262.5751 | 379.8627 | 507.4337 | 373.5986
1402.1917 | 174.0146 | 469.9564 | 262.453 | 379.4724 | 505.2122 | 372.35
1403.1917 | 174.048 | 470.3728 | 262.649 | 378.6557 | 509.227 | 373.4915
1404.1917 | 174.7026 | 470.685 | 262.9355 | 379.2796 | 512.1794 | 378.2056
1405.1917 | 174.6047 | 471.9248 | 263.2387 | 380.2865 | 514.0736 | 378.6288
1406.1917 | 174.5348 | 471.422 | 263.6034 | 380.2942 | 516.7681 | 377.4506
1407.1917 | 175.084 | 471.8935 | 264.0885 | 381.9149 | 515.7687 | 378.9055
1408.1917 | 174.9604 | 472.5191 | 264.5776 | 384.1992 | 518.7867 | 379.4452
1409.1917 | 174.8349 | 471.4686 | 264.4822 | 382.1085 | 520.244 | 378.4226
1410.1917 | 174.8669 | 471.814 | 264.7312 | 381.6242 | 519.1194 | 377.8517
1411.1917 | 174.9869 | 472.5081 | 265.1357 | 384.2717 | 519.2604 | 376.626
1412.1917 | 175.1447 | 472.9141 | 265.7166 | 387.5459 | 518.9076 | 378.1469
1413.1917 | 175.2317 | 473.3849 | 265.7853 | 387.1081 | 519.8598 | 377.8596
1414.1917 | 175.5368 | 474.4143 | 266.0717 | 389.5477 | 521.6456 | 381.9482
1415.1917 | 176.0992 | 474.1991 | 266.2966 | 390.5805 | 524.5956 | 384.0325
1416.1917 | 176.5592 | 475.1168 | 266.6803 | 390.4281 | 524.6161 | 384.0506
1417.1917 | 176.4157 | 474.6933 | 266.8549 | 390.8261 | 529.7861 | 384.3404
1418.1917 | 176.237 | 474.8322 | 267.2357 | 391.4525 | 530.8358 | 384.3577
1419.1917 | 176.5516 | 475.2899 | 267.3961 | 391.1865 | 531.0861 | 383.1972
1420.1917 | 177.0125 | 476.6656 | 267.8625 | 392.1085 | 536.7634 | 386.1882
1421.1917 | 177.1109 | 476.4151 | 268.3249 | 393.261 | 537.5656 | 385.4274
1422.1917 | 177.1975 | 475.9927 | 268.7387 | 393.9595 | 536.8094 | 383.6664
1423.1917 | 177.2091 | 477.0222 | 268.6837 | 394.2013 | 539.5684 | 384.3054
1424.1917 | 177.4748 | 477.3743 | 268.808 | 392.2466 | 538.8713 | 383.8627
1425.1917 | 177.8029 | 478.6337 | 269.3987 | 395.3363 | 541.2196 | 382.9273
1426.1917 | 177.9516 | 478.2987 | 269.5163 | 393.3181 | 541.0288 | 383.9216
1427.1917 | 178.0978 | 479.1555 | 270.2241 | 394.7029 | 538.8021 | 385.6336
1428.1917 | 178.2583 | 480.2746 | 270.3812 | 396.3814 | 542.8338 | 386.025
1429.1917 | 178.867 | 480.7847 | 270.7452 | 396.0859 | 548.6287 | 389.5901
1430.1917 | 178.792 | 480.1346 | 270.9091 | 395.5363 | 549.1568 | 388.6469
1431.1917 | 178.7696 | 480.4407 | 271.6122 | 396.57 | 552.3269 | 390.3529
1432.1917 | 178.9714 | 481.189 | 272.252 | 400.1523 | 553.9003 | 390.4536
1433.1917 | 179.0627 | 482.1192 | 272.2626 | 399.8527 | 554.2066 | 390.4381
1434.1917 | 179.4224 | 482.9299 | 272.3488 | 400.4837 | 554.1748 | 391.2203
1435.1917 | 179.936 | 483.1382 | 272.7915 | 400.8951 | 557.4748 | 394.1656
1436.1917 | 179.8457 | 482.9956 | 273.1095 | 400.0541 | 559.7583 | 393.0794
1437.1917 | 180.1704 | 484.1415 | 273.6697 | 402.0284 | 561.2745 | 392.263
1438.1917 | 180.446 | 485.2564 | 273.6376 | 402.9232 | 557.5782 | 392.4394
1439.1917 | 180.6222 | 485.213 | 274.0179 | 403.969 | 562.0255 | 393.3482
1440.1917 | 180.6743 | 484.6164 | 274.2463 | 403.0697 | 563.2908 | 395.4338
1441.1917 | 180.6377 | 485.3843 | 274.565 | 403.3159 | 563.7762 | 395.9094
1442.1917 | 180.8794 | 486.8531 | 274.9452 | 406.2919 | 565.5468 | 395.1917
1443.1917 | 181.4175 | 487.5147 | 275.2572 | 406.7818 | 565.8817 | 396.7757
1444.1917 | 181.8565 | 488.1953 | 275.7276 | 406.8076 | 575.4532 | 396.0497
1445.1917 | 182.5356 | 489.8577 | 276.2761 | 407.2954 | 579.9103 | 397.1766
1446.1917 | 182.5422 | 490.3815 | 276.5099 | 406.6794 | 578.3126 | 399.4987
1447.1917 | 182.4042 | 490.1689 | 276.732 | 406.0307 | 577.3321 | 399.0957
1448.1917 | 182.531 | 492.1547 | 277.3617 | 407.0077 | 576.3718 | 398.0542
1449.1917 | 182.6256 | 491.6247 | 277.8273 | 407.3028 | 577.0367 | 396.5803
1450.1917 | 182.838 | 491.1377 | 277.7481 | 409.4238 | 575.5531 | 396.0258
1451.1917 | 183.0252 | 491.5527 | 278.2205 | 410.7839 | 573.0376 | 399.4497
1452.1917 | 183.1961 | 492.886 | 278.2725 | 410.7434 | 576.5303 | 401.9732
1453.1917 | 183.4255 | 493.8033 | 278.4301 | 410.8679 | 579.6017 | 404.5496
1454.1917 | 183.5633 | 494.9524 | 278.7937 | 410.4844 | 578.9587 | 407.5151
1455.1917 | 183.9664 | 494.9711 | 278.9442 | 410.4256 | 579.5933 | 409.1441
1456.1917 | 184.0533 | 495.2016 | 279.1975 | 409.8483 | 578.7242 | 410.1976
1457.1917 | 184.3772 | 496.2045 | 279.6319 | 410.7978 | 578.4453 | 411.8698
1458.1917 | 184.6702 | 495.4909 | 279.8456 | 409.4322 | 576.6467 | 411.4545
1459.1917 | 184.7551 | 495.0954 | 280.2519 | 409.2214 | 575.4353 | 412.2184
1460.1917 | 184.7442 | 496.5997 | 280.8102 | 410.6096 | 577.9769 | 413.3908
1461.1917 | 184.9832 | 496.8863 | 281.2429 | 411.9533 | 578.3944 | 412.2613
1462.1917 | 185.0595 | 497.3112 | 281.7474 | 414.0597 | 575.4908 | 410.5468
1463.1917 | 185.1629 | 497.5953 | 281.7743 | 413.9876 | 577.959 | 411.3204
1464.1917 | 185.396 | 497.5781 | 282.0051 | 416.101 | 578.6331 | 412.8993
1465.1917 | 185.8285 | 498.7842 | 282.487 | 415.0132 | 583.1272 | 413.9748
1466.1917 | 186.0477 | 499.3476 | 282.8154 | 414.8719 | 584.3697 | 417.1631
1467.1917 | 186.2637 | 499.122 | 283.1563 | 415.0977 | 588.5201 | 416.8623
1468.1917 | 186.2798 | 499.3821 | 283.351 | 414.4478 | 586.6986 | 418.5021
1469.1917 | 186.43 | 499.8037 | 283.7632 | 416.3049 | 587.1736 | 419.6823
1470.1917 | 186.9079 | 499.6179 | 283.9904 | 416.3229 | 585.5082 | 418.4892
1471.1917 | 187.0784 | 500.6498 | 284.1499 | 418.1673 | 585.0376 | 418.9034
1472.1917 | 187.1085 | 501.3207 | 284.7052 | 418.252 | 586.5533 | 419.0043
1473.1917 | 187.3661 | 501.3019 | 284.9516 | 419.3258 | 589.2268 | 422.3869
1474.1917 | 187.6842 | 501.1785 | 285.1345 | 420.9936 | 588.0183 | 422.8122
1475.1917 | 187.8858 | 502.383 | 285.6808 | 422.0183 | 585.9207 | 422.6922
1476.1917 | 188.0052 | 502.267 | 285.8907 | 420.4127 | 584.0115 | 422.4105
1477.1917 | 188.2809 | 502.7865 | 286.1847 | 422.9837 | 585.244 | 421.9556
1478.1917 | 188.3675 | 502.9015 | 286.2555 | 422.0384 | 582.8886 | 422.2656
1479.1917 | 188.5856 | 503.2504 | 286.8809 | 423.0241 | 582.1625 | 420.6333
1480.1917 | 188.8193 | 503.4913 | 287.4712 | 425.8404 | 581.55 | 419.467
1481.1917 | 188.9638 | 503.4059 | 287.7409 | 428.9745 | 580.3315 | 417.6717
1482.1917 | 189.0676 | 503.2295 | 288.0439 | 428.7161 | 580.5747 | 416.7219
1483.1917 | 188.9546 | 504.4579 | 288.4921 | 429.6384 | 583.3842 | 414.5904
1484.1917 | 189.0409 | 505.3596 | 288.6259 | 431.2459 | 582.626 | 412.4587
1485.1917 | 189.4559 | 505.5982 | 288.8897 | 431.3877 | 582.2537 | 412.4816
1486.1917 | 189.6916 | 505.6064 | 289.2096 | 430.3513 | 582.6555 | 411.809
1487.1917 | 189.755 | 505.6539 | 289.6529 | 431.876 | 580.4581 | 413.7697
1488.1917 | 190.0137 | 506.334 | 289.9648 | 432.0604 | 581.8898 | 414.2889
1489.1917 | 190.1265 | 506.8171 | 290.189 | 433.1923 | 583.5074 | 412.1521
1490.1917 | 190.2081 | 506.9431 | 290.7738 | 433.34 | 583.028 | 413.7443
1491.1917 | 190.5489 | 507.4485 | 291.754 | 434.9329 | 583.645 | 414.8787
1492.1917 | 190.6676 | 508.2041 | 292.1239 | 434.3284 | 583.9595 | 414.536
1493.1917 | 190.9497 | 508.3361 | 292.0675 | 434.9865 | 586.0254 | 412.8987
1494.1917 | 191.4584 | 509.0956 | 292.2072 | 436.0279 | 591.3437 | 414.4972
1495.1917 | 191.8022 | 509.4994 | 292.404 | 434.4597 | 589.9792 | 416.0222
1496.1917 | 191.6692 | 508.9183 | 292.6405 | 434.6558 | 589.3784 | 418.5666
1497.1917 | 191.5202 | 509.3292 | 293.1594 | 434.7397 | 590.7018 | 420.8845
1498.1917 | 191.4809 | 509.599 | 293.278 | 433.7006 | 588.515 | 418.9781
1499.1917 | 191.8745 | 510.3247 | 293.8907 | 433.8117 | 590.5543 | 417.8047
1500.1917 | 192.5703 | 510.8303 | 294.261 | 434.7768 | 588.1167 | 419.3218
1501.1917 | 192.8664 | 512.3457 | 294.5601 | 436.8846 | 586.7259 | 421.2221
1502.1917 | 193.2471 | 512.3858 | 294.989 | 436.1811 | 588.4902 | 421.1115
1503.1917 | 193.5006 | 513.514 | 295.1796 | 436.6105 | 591.2085 | 420.6508
1504.1917 | 193.5005 | 513.9899 | 295.345 | 433.7784 | 587.2173 | 421.6143
1505.1917 | 193.7061 | 514.0036 | 295.6352 | 432.9312 | 588.3649 | 421.1716
1506.1917 | 193.8846 | 514.4581 | 296.2455 | 432.9153 | 591.0233 | 421.9654
1507.1917 | 194.004 | 515.3508 | 296.598 | 434.5984 | 591.2292 | 424.0382
1508.1917 | 194.1007 | 515.2357 | 296.9392 | 434.3405 | 589.8072 | 424.2082
1509.1917 | 194.1344 | 515.0052 | 297.238 | 433.6477 | 586.8205 | 425.1104
1510.1917 | 194.5286 | 516.842 | 297.6286 | 433.4636 | 586.4268 | 426.5541
1511.1917 | 194.7697 | 516.2621 | 298.0261 | 433.6836 | 586.07 | 427.1087
1512.1917 | 194.8464 | 516.6955 | 298.8248 | 434.5333 | 585.0577 | 428.6175
1513.1917 | 194.879 | 516.1059 | 299.0484 | 434.5191 | 588.0627 | 427.7207
1514.1917 | 195.0389 | 517.0072 | 299.3675 | 435.6536 | 585.933 | 427.7815
1515.1917 | 195.0888 | 516.7654 | 299.647 | 435.5869 | 586.119 | 427.138
1516.1917 | 195.3736 | 518.495 | 299.9167 | 437.8355 | 588.6338 | 426.5856
1517.1917 | 195.7513 | 518.8189 | 300.4377 | 437.8362 | 592.5489 | 428.0579
1518.1917 | 196.2992 | 519.6898 | 300.9399 | 437.6118 | 593.2726 | 429.2306
1519.1917 | 196.5021 | 521.7315 | 301.0741 | 440.2123 | 592.2275 | 430.9036
1520.1917 | 196.4975 | 519.8313 | 301.271 | 440.7314 | 589.3211 | 432.0759
1521.1917 | 196.792 | 520.432 | 301.7467 | 440.7918 | 587.9113 | 433.1376
1522.1917 | 196.9678 | 521.3436 | 302.5621 | 441.0189 | 592.2048 | 431.7606
1523.1917 | 197.3328 | 524.6457 | 303.4288 | 445.2715 | 596.6978 | 431.9977
1524.1917 | 197.4706 | 524.8454 | 303.426 | 445.0911 | 597.9656 | 431.0067
1525.1917 | 197.7174 | 526.5671 | 303.5485 | 448.1277 | 600.3895 | 431.108
1526.1917 | 197.8484 | 524.7505 | 303.6978 | 447.4958 | 595.5886 | 433.8212
1527.1917 | 198.0778 | 524.9216 | 304.054 | 446.9624 | 594.4988 | 436.4213
1528.1917 | 198.162 | 525.418 | 304.3525 | 447.1114 | 593.0313 | 441.0224
1529.1917 | 198.3029 | 525.1482 | 304.9043 | 447.6895 | 592.3879 | 443.2744
1530.1917 | 198.3931 | 525.7648 | 305.1311 | 448.2234 | 589.8317 | 445.3036
1531.1917 | 198.5021 | 525.8898 | 305.3544 | 448.0156 | 590.4502 | 446.2695
1532.1917 | 199.1096 | 525.6583 | 305.7762 | 448.1784 | 588.9626 | 444.3958
1533.1917 | 198.947 | 526.0893 | 306.3702 | 450.5719 | 592.4274 | 444.2379
1534.1917 | 199.1453 | 526.6724 | 306.7917 | 451.2703 | 593.7254 | 443.4808
1535.1917 | 199.4738 | 527.1322 | 307.1434 | 451.0278 | 593.7662 | 444.1542
1536.1917 | 199.8137 | 528.7485 | 307.6199 | 451.318 | 594.6644 | 445.07
1537.1917 | 200.088 | 528.8691 | 307.9629 | 451.6531 | 594.3401 | 444.9388
1538.1917 | 200.795 | 529.7418 | 308.283 | 451.4795 | 596.033 | 446.1035
1539.1917 | 200.8568 | 530.0207 | 308.5805 | 452.1868 | 598.4075 | 447.172
1540.1917 | 202.7604 | 530.045 | 309.1716 | 454.9521 | 596.7977 | 446.2512
1541.1917 | 201.7645 | 530.0864 | 309.5337 | 454.7481 | 598.8134 | 445.0481
1542.1917 | 201.1582 | 529.692 | 309.7133 | 454.9326 | 599.6523 | 445.2978
1543.1917 | 201.0779 | 529.2101 | 309.9055 | 455.3708 | 602.6501 | 443.7849
1544.1917 | 201.5042 | 530.8347 | 310.2812 | 456.993 | 608.3958 | 442.5836
1545.1917 | 203.4438 | 533.2392 | 310.9559 | 459.5522 | 606.9896 | 442.1808
1546.1917 | 202.269 | 531.2038 | 310.9143 | 458.2911 | 609.6519 | 443.6474
1547.1917 | 203.3772 | 533.6395 | 311.4383 | 457.2252 | 615.7584 | 440.7207
1548.1917 | 202.1247 | 531.9779 | 311.6139 | 457.5054 | 622.7731 | 441.2522
1549.1917 | 202.2343 | 532.0835 | 311.9366 | 459.5536 | 620.6293 | 439.1213
1550.1917 | 202.547 | 533.7862 | 312.6034 | 460.5644 | 620.3422 | 439.3661
1551.1917 | 202.6265 | 533.4495 | 312.9036 | 462.6341 | 620.5799 | 440.3649
1552.1917 | 202.8325 | 533.7861 | 313.3504 | 462.905 | 624.3195 | 438.9639
1553.1917 | 203.2044 | 533.8885 | 313.456 | 462.6364 | 624.045 | 437.7805
1554.1917 | 203.6443 | 534.7777 | 313.8561 | 462.5134 | 623.091 | 436.6659
1555.1917 | 203.6869 | 534.8671 | 314.4562 | 463.1688 | 622.9582 | 434.0122
1556.1917 | 203.769 | 535.4639 | 315.1198 | 466.3712 | 621.3501 | 433.6997
1557.1917 | 203.8605 | 535.0906 | 315.6303 | 467.3979 | 620.2521 | 434.2129
1558.1917 | 203.8135 | 535.7859 | 315.9171 | 469.6246 | 621.6286 | 432.9298
1559.1917 | 203.8051 | 536.1244 | 316.3316 | 473.6131 | 618.3869 | 432.8474
1560.1917 | 204.034 | 536.1277 | 316.4162 | 475.2385 | 620.0643 | 431.6168
1561.1917 | 204.5025 | 537.5852 | 316.7108 | 475.6367 | 620.9473 | 430.9764
1562.1917 | 204.7472 | 540.1118 | 317.0172 | 475.4445 | 622.1302 | 431.331
1563.1917 | 204.8833 | 539.0662 | 317.5598 | 477.2773 | 621.6588 | 433.4366
1564.1917 | 205.1341 | 538.3605 | 318.0961 | 476.5406 | 621.1479 | 434.9082
1565.2073 | 205.279 | 538.8526 | 318.5001 | 477.628 | 620.7277 | 438.3058
1566.1917 | 205.7253 | 539.5954 | 319.2553 | 479.6892 | 620.1795 | 439.1257
1567.1917 | 206.2765 | 540.1671 | 319.7749 | 479.2191 | 619.7741 | 439.64
1568.1917 | 206.4653 | 540.6529 | 319.7027 | 478.967 | 619.9181 | 440.6721
1569.1917 | 206.7511 | 542.5817 | 321.0071 | 478.4843 | 619.6561 | 442.75
1570.1917 | 207.1683 | 545.3158 | 321.5865 | 480.1649 | 619.9938 | 443.8862
1571.1917 | 207.1019 | 543.7625 | 321.5202 | 481.9821 | 620.4057 | 443.7487
1572.1917 | 207.3849 | 544.2271 | 322.371 | 481.8706 | 621.5488 | 444.7113
1573.1917 | 207.5987 | 547.7109 | 322.8148 | 484.0225 | 623.5953 | 445.7176
1574.1917 | 207.8843 | 547.5515 | 323.4202 | 486.7885 | 624.4603 | 446.6861
1575.1917 | 208.2555 | 548.7378 | 323.7803 | 488.8643 | 624.9558 | 447.0428
1576.1917 | 208.6162 | 548.1578 | 324.2055 | 489.2734 | 624.9197 | 447.6538
1577.1917 | 208.7675 | 548.2391 | 324.391 | 490.6875 | 626.6546 | 450.6306
1578.1917 | 209.1482 | 549.108 | 324.7615 | 491.8725 | 627.2973 | 452.3617
1579.1917 | 209.2196 | 549.2318 | 325.1009 | 492.6153 | 627.1356 | 452.6744
1580.1917 | 209.8755 | 548.568 | 325.7979 | 492.5066 | 625.8211 | 453.2776
1581.1917 | 210.1296 | 549.8162 | 326.3783 | 495.2225 | 624.2812 | 453.4841
1582.1917 | 210.4323 | 552.6158 | 326.5488 | 496.4245 | 623.774 | 454.311
1583.1917 | 210.524 | 552.0826 | 326.96 | 498.0994 | 623.4352 | 455.3077
1584.1917 | 210.6567 | 550.9208 | 327.2949 | 499.6896 | 624.8932 | 457.0681
1585.1917 | 211.0346 | 552.6565 | 327.671 | 499.5107 | 623.4517 | 457.9381
1586.1917 | 211.2151 | 552.5542 | 327.9458 | 499.9664 | 622.5934 | 461.1845
1587.1917 | 211.4293 | 553.4675 | 328.2476 | 500.3117 | 621.0791 | 463.8787
1588.1917 | 211.7979 | 554.8453 | 329.4277 | 497.8949 | 621.518 | 465.2091
1589.1917 | 212.3603 | 556.4932 | 329.6899 | 499.2419 | 623.6644 | 465.7099
1590.1917 | 212.8452 | 556.214 | 329.9134 | 500.4469 | 624.7943 | 465.7405
1591.1917 | 212.779 | 556.2038 | 330.4064 | 500.421 | 623.7642 | 468.2631
1592.1917 | 212.9613 | 557.6656 | 330.9989 | 501.8523 | 621.6293 | 469.4303
1593.1917 | 213.2527 | 557.1758 | 331.5187 | 501.4988 | 619.6697 | 470.4556
1594.1917 | 213.493 | 557.2419 | 331.7137 | 501.5007 | 619.5096 | 472.5589
1595.1917 | 213.9568 | 557.4277 | 332.1287 | 501.3981 | 618.4734 | 475.6145
1596.1917 | 214.3052 | 557.9827 | 332.407 | 501.4718 | 614.4899 | 477.6734
1597.1917 | 214.585 | 558.3718 | 333.0155 | 500.2494 | 616.565 | 477.9412
1598.1917 | 215.2853 | 561.1806 | 333.9033 | 501.6301 | 618.8477 | 478.0195
1599.1917 | 216.0227 | 560.9676 | 333.9548 | 503.5043 | 623.8883 | 479.8994
1600.1917 | 216.5945 | 562.3733 | 334.4828 | 501.9576 | 624.5161 | 481.7778
1601.1917 | 217.0017 | 563.3199 | 335.0385 | 502.9322 | 628.2643 | 484.8697
1602.1917 | 216.8719 | 562.3399 | 335.4449 | 504.0389 | 632.0237 | 485.6137
1603.1917 | 216.6105 | 563.8537 | 335.8485 | 506.5927 | 629.9058 | 486.7278
1604.1917 | 216.6895 | 564.285 | 336.5734 | 506.2343 | 629.6361 | 486.807
1605.1917 | 217.0512 | 563.8543 | 336.4137 | 506.8492 | 627.3573 | 488.5995
1606.1917 | 217.4264 | 564.5145 | 336.7801 | 505.3183 | 627.8736 | 492.7573
1607.1917 | 218.0091 | 564.69 | 337.3204 | 504.6419 | 625.9426 | 496.0799
1608.1917 | 218.2391 | 565.2612 | 337.3252 | 502.9699 | 626.096 | 499.4455
1609.1917 | 218.4408 | 564.523 | 337.8075 | 501.9048 | 628.4107 | 500.4581
1610.1917 | 218.5542 | 567.2386 | 338.3565 | 503.0713 | 628.4491 | 502.2419
1611.1917 | 219.0371 | 566.4267 | 338.9275 | 502.8888 | 628.084 | 504.2202
1612.1917 | 219.2662 | 566.4324 | 339.4647 | 503.8727 | 627.9014 | 505.1726
1613.1917 | 219.744 | 567.1411 | 340.1167 | 506.2203 | 625.989 | 507.5805
1614.1917 | 219.878 | 566.2665 | 340.054 | 505.3723 | 624.5051 | 508.3137
1615.1917 | 219.7476 | 566.4869 | 340.5178 | 505.8761 | 626.0145 | 507.5786
1616.1917 | 219.8672 | 567.2964 | 340.9269 | 505.842 | 628.0334 | 510.3102
1617.1917 | 220.4204 | 567.8545 | 341.3527 | 508.3186 | 628.2244 | 511.9766
1618.1917 | 220.8405 | 568.0111 | 341.9582 | 507.8237 | 628.6403 | 512.401
1619.1917 | 221.1782 | 568.0301 | 342.2036 | 508.2752 | 632.7544 | 511.3565
1620.1917 | 221.3321 | 568.4998 | 342.4849 | 510.258 | 631.972 | 513.4399
1621.1917 | 222.0559 | 569.7268 | 343.4872 | 510.1881 | 630.7801 | 515.7047
1622.1917 | 222.0882 | 571.3066 | 344.1914 | 510.3018 | 629.185 | 513.8814
1623.1917 | 221.902 | 570.7351 | 344.3891 | 511.6719 | 628.6662 | 512.2118
1624.1917 | 222.2844 | 571.6856 | 344.7678 | 512.4647 | 627.4687 | 509.8059
1625.1917 | 223.117 | 572.5449 | 344.9413 | 512.9768 | 627.6999 | 510.7833
1626.1917 | 223.1456 | 572.1889 | 345.6894 | 515.5631 | 627.9946 | 510.8101
1627.1917 | 223.4156 | 572.0038 | 345.8373 | 516.1026 | 626.9655 | 510.3065
1628.1917 | 223.2706 | 572.9083 | 346.7846 | 515.8986 | 628.348 | 509.7651
1629.1917 | 223.6001 | 573.8291 | 347.0079 | 517.3633 | 628.9528 | 511.3636
1630.1917 | 224.3289 | 574.0153 | 347.5757 | 519.1249 | 630.5334 | 512.2872
1631.1917 | 224.1906 | 573.4332 | 347.9016 | 519.3792 | 629.0329 | 512.4264
1632.1917 | 225.1063 | 575.0683 | 348.1292 | 519.0314 | 628.8235 | 515.1242
1633.1917 | 225.7797 | 574.623 | 348.8959 | 519.0728 | 628.8209 | 515.4238
1634.1917 | 225.9321 | 575.1554 | 349.4662 | 522.4613 | 626.7268 | 515.3741
1635.1917 | 226.0369 | 575.3584 | 349.7701 | 523.5219 | 626.7259 | 515.5841
1636.1917 | 226.0324 | 575.1678 | 350.1895 | 523.638 | 625.9491 | 515.6111
1637.1917 | 226.0601 | 575.0855 | 350.5702 | 523.949 | 626.7855 | 514.2706
1638.1917 | 226.9997 | 577.0914 | 351.1853 | 525.7942 | 624.8805 | 515.7228
1639.1917 | 226.8892 | 576.1734 | 351.5186 | 526.147 | 625.0349 | 516.1891
1640.1917 | 226.7293 | 575.4044 | 352.1139 | 526.9852 | 626.1392 | 515.528
1641.1917 | 227.1001 | 575.7291 | 352.5358 | 528.2864 | 632.1416 | 513.1719
1642.1917 | 227.6669 | 576.6761 | 353.5107 | 530.7614 | 632.5245 | 514.2116
1643.1917 | 228.0729 | 575.9177 | 353.6379 | 529.4972 | 629.1739 | 515.0643
1644.1917 | 228.7836 | 576.9391 | 354.1809 | 530.3436 | 626.2751 | 515.7673
1645.1917 | 229.4954 | 577.3953 | 354.6536 | 531.5117 | 629.4725 | 514.7727
1646.1917 | 230.2566 | 578.4824 | 355.4313 | 531.9626 | 628.5432 | 516.7418
1647.1917 | 230.3246 | 580.4091 | 356.0326 | 533.0789 | 628.2319 | 518.9892
1648.1917 | 230.5717 | 580.2097 | 356.2189 | 534.5475 | 628.2135 | 520.7899
1649.1917 | 230.6004 | 580.6215 | 356.8211 | 534.1352 | 626.4957 | 521.8295
1650.1917 | 230.9708 | 580.6291 | 357.4941 | 532.9399 | 626.3728 | 522.0339
1651.1917 | 231.2601 | 579.9635 | 357.735 | 534.3487 | 628.7029 | 521.556
1652.1917 | 231.7183 | 580.8994 | 358.6654 | 535.1269 | 629.9798 | 521.2714
1653.1917 | 231.6636 | 580.8482 | 359.3149 | 533.5182 | 631.5517 | 519.6864
1654.1917 | 231.4422 | 582.0983 | 359.8193 | 535.1024 | 628.5893 | 520.0973
1655.1917 | 231.6078 | 584.0064 | 360.2202 | 537.7025 | 632.7784 | 519.2957
1656.1917 | 232.1924 | 584.7356 | 360.8107 | 538.2936 | 635.2694 | 519.0211
1657.1917 | 232.6658 | 584.2127 | 361.4994 | 538.9165 | 634.1301 | 518.7003
1658.1917 | 233.6082 | 584.3615 | 361.7297 | 540.776 | 632.1936 | 520.1702
1659.1917 | 234.0463 | 584.2621 | 362.1916 | 544.2602 | 633.5662 | 522.8588
1660.1917 | 234.386 | 585.3642 | 362.6543 | 545.6251 | 633.7547 | 523.3271
1661.1917 | 234.4369 | 585.9242 | 363.0617 | 546.3188 | 631.3723 | 526.4329
1662.1917 | 234.5438 | 587.517 | 363.9028 | 547.5396 | 632.0233 | 527.6244
1663.1917 | 235.5625 | 586.6009 | 363.9316 | 549.4707 | 632.2881 | 530.2294
1664.1917 | 236.1723 | 588.7181 | 364.8496 | 549.3466 | 629.4349 | 532.6701
1665.1917 | 236.028 | 587.1532 | 365.309 | 550.653 | 630.1017 | 532.5349
1666.1917 | 236.4049 | 588.9269 | 365.8426 | 552.222 | 628.1027 | 534.0929
1667.1917 | 236.6092 | 588.7561 | 366.4138 | 553.2981 | 627.0137 | 535.1112
1668.1917 | 236.4392 | 588.6965 | 367.4122 | 554.0246 | 629.3835 | 535.8554
1669.1917 | 237.1202 | 589.1576 | 367.5571 | 554.0399 | 628.3219 | 537.1914
1670.1917 | 237.4334 | 589.6362 | 368.8135 | 555.7172 | 626.4681 | 538.8374
1671.1917 | 237.4396 | 590.0734 | 369.8642 | 557.6976 | 627.6874 | 538.4472
1672.1917 | 237.7967 | 591.524 | 371.4356 | 563.3272 | 634.6582 | 537.2374
1673.1917 | 237.649 | 592.619 | 372.1344 | 569.1293 | 639.2171 | 535.176
1674.1917 | 237.653 | 591.2754 | 371.4341 | 575.5909 | 643.4893 | 533.7378
1675.1917 | 238.5126 | 593.3957 | 372.0828 | 578.0349 | 646.0675 | 532.0074
1676.1917 | 239.8568 | 593.8676 | 372.7428 | 578.7016 | 643.3693 | 535.1417
1677.1917 | 240.783 | 594.0877 | 373.2971 | 580.8649 | 643.7074 | 539.6663
1678.1917 | 241.0885 | 593.9106 | 373.3236 | 581.6307 | 642.1404 | 541.6198
1679.1917 | 242.0982 | 593.7758 | 373.9509 | 581.875 | 643.6391 | 540.9024
1680.1917 | 243.1649 | 593.3207 | 374.2225 | 583.8789 | 646.2041 | 542.5163
1681.1917 | 243.1253 | 593.3087 | 374.5952 | 582.4808 | 645.2609 | 546.1711
1682.1917 | 244.3284 | 594.3377 | 375.8509 | 582.0448 | 643.7447 | 547.9613
1683.1917 | 245.0375 | 595.1766 | 376.3513 | 582.0394 | 641.8334 | 551.9921
1684.1917 | 244.6094 | 593.9878 | 376.2789 | 580.2567 | 639.7028 | 551.0325
1685.1917 | 243.7694 | 594.2127 | 376.8999 | 580.4122 | 637.8102 | 552.7298
1686.1917 | 245.0273 | 595.9173 | 378.3421 | 581.9927 | 638.7133 | 555.0487
1687.1917 | 245.0572 | 595.5602 | 378.4891 | 583.9778 | 638.8042 | 552.6444
1688.1917 | 245.5184 | 596.1827 | 378.5308 | 582.9601 | 638.5384 | 553.8983
1689.1917 | 245.9723 | 595.2309 | 379.0219 | 580.9197 | 635.1655 | 556.3977
1690.1917 | 246.5835 | 595.6896 | 379.7038 | 580.2162 | 634.3907 | 560.2555
1691.1917 | 246.9432 | 595.8264 | 380.3242 | 578.7806 | 636.9413 | 560.0831
1692.1917 | 247.7065 | 595.7982 | 381.1555 | 579.5862 | 635.7952 | 561.0145
1693.1917 | 246.8709 | 597.3012 | 381.5932 | 580.4619 | 633.3569 | 560.823
1694.1917 | 247.3803 | 597.5968 | 382.1146 | 581.5981 | 634.2414 | 559.9324
1695.1917 | 247.7857 | 596.8442 | 382.2791 | 583.7182 | 634.2236 | 561.3164
1696.1917 | 247.9772 | 598.1054 | 383.1516 | 582.9523 | 639.3613 | 563.0679
1697.1917 | 249.1368 | 598.0452 | 383.5685 | 584.5517 | 650.5332 | 562.0079
1698.1917 | 249.6441 | 598.0007 | 383.4218 | 586.002 | 647.7618 | 562.3314
1699.1917 | 250.5819 | 598.0301 | 384.003 | 585.1479 | 645.0491 | 567.9511
1700.1917 | 251.3066 | 597.7664 | 384.3686 | 587.4948 | 646.9854 | 571.521
1701.1917 | 250.8808 | 597.0287 | 384.9489 | 586.53 | 646.6501 | 570.8318
1702.1917 | 250.04 | 597.3426 | 385.3769 | 586.5963 | 645.6758 | 568.3492
1703.1917 | 250.8826 | 597.9906 | 386.3193 | 587.381 | 644.3028 | 565.8623
1704.1917 | 250.5113 | 598.5155 | 386.7973 | 586.303 | 641.3709 | 566.2003
1705.1917 | 251.0176 | 598.6374 | 387.2809 | 587.4992 | 643.775 | 566.3893
1706.1917 | 251.7487 | 598.4119 | 387.621 | 588.0126 | 642.7338 | 566.2759
1707.1917 | 252.0478 | 599.3572 | 387.9816 | 589.1695 | 644.5046 | 566.6233
1708.1917 | 251.9825 | 598.7105 | 389.0578 | 588.8058 | 642.7118 | 566.4108
1709.1917 | 251.9398 | 599.3503 | 389.7546 | 590.686 | 649.8855 | 566.2015
1710.1917 | 252.2235 | 600.053 | 389.5767 | 587.9574 | 646.6922 | 564.3937
1711.1917 | 252.4632 | 599.8573 | 390.7045 | 586.908 | 645.7015 | 564.5341
1712.1917 | 253.4746 | 601.4002 | 391.0282 | 587.8079 | 647.0341 | 563.4579
1713.1917 | 253.314 | 599.4751 | 390.988 | 587.8941 | 643.8741 | 563.7034
1714.1917 | 253.2049 | 599.5065 | 391.9041 | 587.8399 | 640.1438 | 561.7174
1715.1917 | 253.2785 | 600.0478 | 393.0442 | 586.7711 | 638.9717 | 560.0425
1716.1917 | 253.5162 | 602.0338 | 393.2616 | 587.5623 | 641.8048 | 559.0767
1717.1917 | 253.7053 | 602.5976 | 393.9136 | 588.7725 | 647.2149 | 557.8904
1718.1917 | 254.7578 | 602.4036 | 394.2568 | 588.532 | 645.325 | 559.5102
1719.1917 | 255.334 | 602.2091 | 394.8896 | 589.5396 | 648.0799 | 560.9944
1720.1917 | 255.4869 | 602.267 | 395.179 | 588.9616 | 647.7819 | 561.3979
1721.1917 | 256.4359 | 603.2431 | 395.5108 | 592.1441 | 646.2205 | 561.544
1722.1917 | 257.8839 | 603.2879 | 396.3071 | 590.4316 | 647.4187 | 563.5254
1723.1917 | 258.4112 | 603.2662 | 396.5385 | 593.7201 | 648.8454 | 565.137
1724.1917 | 257.7991 | 603.5751 | 396.6208 | 593.848 | 650.7 | 570.0854
1725.1917 | 257.8225 | 603.953 | 396.7709 | 592.5009 | 648.1614 | 570.727
1726.1917 | 259.6984 | 604.4991 | 397.1787 | 594.4421 | 648.673 | 570.5447
1727.1917 | 260.8338 | 604.4663 | 397.2965 | 594.0295 | 646.0983 | 572.0003
1728.1917 | 261.8886 | 604.5551 | 397.9456 | 594.2146 | 648.6061 | 575.2382
1729.1917 | 262.195 | 604.026 | 398.2238 | 597.4274 | 646.5559 | 576.6099
1730.1917 | 262.2151 | 603.8512 | 398.8943 | 594.1446 | 643.9156 | 576.3442
1731.1917 | 262.15 | 604.2614 | 399.2342 | 594.9087 | 645.1571 | 578.9031
1732.1917 | 263.0904 | 605.1374 | 399.6237 | 594.0433 | 643.3931 | 582.7186
1733.1917 | 263.5029 | 604.8729 | 400.2943 | 593.1029 | 646.9727 | 580.5474
1734.1917 | 262.6027 | 605.3534 | 400.9071 | 593.037 | 643.1064 | 577.3177
1735.1917 | 262.5608 | 605.6673 | 401.2063 | 591.6379 | 643.9813 | 576.0332
1736.1917 | 262.6238 | 605.9173 | 401.5994 | 590.8691 | 640.032 | 573.7038
1737.1917 | 264.7411 | 606.3969 | 402.1031 | 592.7531 | 642.091 | 577.7053
1738.1917 | 264.9791 | 605.5873 | 402.3843 | 592.3777 | 642.3937 | 575.345
1739.1917 | 264.8699 | 605.9371 | 402.9778 | 593.1548 | 641.1944 | 576.2779
1740.1917 | 266.063 | 606.0252 | 403.0672 | 592.8556 | 639.3571 | 580.9758
1741.1917 | 266.4051 | 606.2585 | 403.2259 | 592.2477 | 643.7529 | 584.4894
1742.1917 | 266.7804 | 606.0587 | 403.702 | 590.3833 | 642.3866 | 586.9236
1743.1917 | 268.0293 | 606.8107 | 404.1184 | 590.0689 | 642.059 | 587.5675
1744.1917 | 267.8951 | 606.4536 | 404.111 | 591.7491 | 644.5079 | 591.9781
1745.1917 | 268.6884 | 606.4191 | 404.5012 | 599.2493 | 642.8681 | 589.6368
1746.1917 | 269.419 | 606.7792 | 404.839 | 594.8351 | 642.7749 | 587.6843
1747.1917 | 269.808 | 607.0068 | 405.4807 | 595.1888 | 643.9929 | 591.1359
1748.1917 | 271.3552 | 606.6933 | 405.7443 | 597.4628 | 643.5699 | 591.755
1749.1917 | 271.8469 | 607.535 | 406.2811 | 596.6083 | 645.3689 | 592.0797
1750.1917 | 271.1296 | 607.727 | 406.6232 | 595.5055 | 646.4825 | 592.8211
1751.1917 | 270.7864 | 607.373 | 406.7637 | 594.2398 | 646.3528 | 595.3469
1752.1917 | 271.2407 | 607.2279 | 407.174 | 592.4017 | 646.6512 | 593.4163
1753.1917 | 271.5497 | 607.6657 | 407.6352 | 595.4566 | 647.6563 | 596.1076
1754.1917 | 271.3768 | 607.7423 | 408.0301 | 596.0269 | 646.3055 | 598.8332
1755.1917 | 272.3873 | 607.7601 | 409.1374 | 597.4988 | 648.9584 | 597.9658
1756.1917 | 273.1026 | 608.2379 | 409.4069 | 596.7605 | 648.0082 | 597.6333
1757.1917 | 273.03 | 608.4855 | 410.3197 | 596.3979 | 646.4793 | 596.9059
1758.1917 | 273.92 | 608.5948 | 411.104 | 597.2687 | 648.2437 | 595.8369
1759.1917 | 273.2497 | 608.1145 | 411.0099 | 596.188 | 643.5683 | 594.4173
1760.1917 | 273.5157 | 609.9581 | 411.6647 | 595.4131 | 641.1469 | 594.4965
1761.1917 | 274.0021 | 611.0029 | 412.8212 | 601.8495 | 647.6523 | 594.4758
1762.1917 | 274.1464 | 611.1835 | 412.7072 | 604.8625 | 654.8309 | 593.8795
1763.1917 | 274.2238 | 611.7794 | 413.832 | 603.4838 | 659.3732 | 595.0554
1764.1917 | 275.2018 | 610.9645 | 413.8551 | 602.6929 | 658.2959 | 594.8799
1765.1917 | 275.7826 | 610.7843 | 414.0987 | 602.7373 | 656.1198 | 593.3263
1766.1917 | 275.8452 | 611.3206 | 414.931 | 603.8605 | 653.8954 | 592.3759
1767.1917 | 275.4014 | 613.2433 | 415.034 | 604.111 | 653.6657 | 593.5659
1768.1917 | 275.2029 | 611.5228 | 415.7465 | 603.8018 | 653.2434 | 592.7061
1769.1917 | 275.126 | 612.2534 | 416.2464 | 603.8786 | 650.8588 | 592.6321
1770.1917 | 275.9871 | 612.84 | 416.6765 | 609.4347 | 653.1946 | 592.1309
1771.1917 | 277.4298 | 612.5631 | 416.8535 | 606.8511 | 651.2506 | 594.9464
1772.1917 | 279.3665 | 613.9732 | 417.0954 | 606.8463 | 653.9646 | 598.469
1773.1917 | 279.98 | 614.9831 | 417.774 | 611.8773 | 664.1342 | 604.7178
1774.1917 | 279.298 | 614.2298 | 418.5582 | 615.2088 | 663.0291 | 603.0667
1775.1917 | 279.2799 | 614.236 | 419.5083 | 616.5747 | 664.8822 | 601.5503
1776.1917 | 278.8582 | 614.5854 | 419.5272 | 618.9655 | 660.4908 | 601.4985
1777.1917 | 279.6391 | 613.7221 | 419.4352 | 619.764 | 662.4927 | 603.4093
1778.1917 | 279.5745 | 614.5564 | 420.1826 | 617.9651 | 665.2065 | 603.6502
1779.1917 | 279.6187 | 615.0251 | 420.7571 | 619.0676 | 662.655 | 602.2032
1780.1917 | 279.7917 | 615.7157 | 421.5177 | 615.8095 | 658.7148 | 601.614
1781.1917 | 280.8077 | 614.7562 | 421.987 | 616.0165 | 658.5913 | 603.2315
1782.1917 | 280.4748 | 617.33 | 422.9505 | 622.0588 | 662.4961 | 601.4558
1783.1917 | 280.6244 | 618.3064 | 423.6705 | 624.1965 | 665.8685 | 600.3962
1784.1917 | 280.5007 | 617.9156 | 423.6681 | 624.0033 | 664.2617 | 596.9441
1785.1917 | 280.8431 | 617.8072 | 423.6717 | 624.3497 | 664.8417 | 595.7108
1786.1917 | 281.3882 | 619.5105 | 424.4498 | 624.5095 | 666.7553 | 601.9706
1787.1917 | 282.6623 | 618.9788 | 425.174 | 622.2795 | 666.2239 | 601.8481
1788.1917 | 283.3495 | 618.5291 | 425.3743 | 624.6092 | 665.1303 | 599.9952
1789.1917 | 283.3367 | 621.9486 | 426.6706 | 625.2565 | 662.5364 | 600.1018
1790.1917 | 283.9186 | 621.5942 | 426.9276 | 623.941 | 663.9037 | 602.1438
1791.1917 | 285.0429 | 619.2133 | 426.8966 | 628.2747 | 667.0277 | 603.8212
1792.1917 | 284.6338 | 619.8986 | 427.3936 | 626.8548 | 665.9909 | 604.5575
1793.1917 | 284.9911 | 622.3681 | 427.7773 | 626.9209 | 664.3208 | 602.2254
1794.1917 | 285.9895 | 621.54 | 428.5844 | 625.3386 | 660.1276 | 603.0271
1795.1917 | 285.7979 | 621.9133 | 429.4755 | 624.4577 | 657.3754 | 603.2599
1796.1917 | 286.1176 | 621.8842 | 429.8306 | 630.7536 | 661.6566 | 608.5025
1797.1917 | 286.0825 | 621.4204 | 430.8139 | 635.9648 | 669.0547 | 614.7459
1798.1917 | 285.9489 | 622.8469 | 430.7285 | 637.1685 | 668.1496 | 611.1334
1799.1917 | 286.8092 | 623.1061 | 431.0589 | 635.4417 | 667.2563 | 614.8448
1800.1917 | 287.34 | 622.6349 | 431.4157 | 634.5327 | 666.3139 | 616.921
1801.1917 | 287.1938 | 622.8189 | 432.1843 | 633.9973 | 665.268 | 616.5385
1802.1917 | 287.1232 | 622.9566 | 432.7997 | 633.8223 | 664.634 | 615.2989
1803.1917 | 287.5727 | 623.8848 | 433.1796 | 635.0917 | 665.349 | 613.1514
1804.1917 | 288.6736 | 623.6198 | 433.1677 | 635.2519 | 666.3318 | 616.4369
1805.1917 | 288.7626 | 624.4172 | 433.4589 | 637.2443 | 664.4588 | 617.1146
1806.1917 | 288.5652 | 625.4319 | 434.8362 | 637.4852 | 669.213 | 617.3688
1807.1917 | 288.8937 | 624.4855 | 436.133 | 637.9728 | 673.8516 | 620.5059
1808.1917 | 288.7961 | 626.3018 | 436.3102 | 643.3162 | 680.9878 | 623.2775
1809.1917 | 289.1066 | 625.1349 | 436.9141 | 644.5041 | 679.7183 | 622.6087
1810.1917 | 290.1587 | 624.9519 | 437.6811 | 647.4946 | 680.4554 | 623.1786
1811.1917 | 290.9819 | 625.3592 | 437.8516 | 646.5767 | 676.2815 | 625.1722
1812.1917 | 292.2387 | 624.5414 | 438.3227 | 649.0041 | 676.4502 | 626.6658
1813.1917 | 292.7076 | 626.231 | 438.589 | 650.3216 | 677.7137 | 626.1811
1814.1917 | 291.5934 | 625.2455 | 439.0774 | 650.8576 | 674.5538 | 625.5875
1815.1917 | 291.1189 | 624.5174 | 439.1652 | 648.8167 | 671.2057 | 624.1146
1816.1917 | 291.5969 | 625.9451 | 439.1736 | 649.7165 | 671.4141 | 620.0657
1817.1917 | 292.2661 | 626.5478 | 439.9833 | 649.2166 | 669.1094 | 618.4644
1818.1917 | 292.212 | 625.4817 | 441.2715 | 651.806 | 669.5502 | 617.2908
1819.1917 | 292.2236 | 626.4465 | 441.5581 | 654.3275 | 670.6428 | 614.9204
1820.1917 | 292.126 | 625.701 | 441.3113 | 655.1238 | 670.4076 | 610.8939
1821.1917 | 292.0844 | 626.9036 | 442.1043 | 656.7145 | 672.112 | 611.1946
1822.1917 | 291.7842 | 626.8843 | 442.7863 | 658.298 | 673.3142 | 617.9025
1823.1917 | 291.7422 | 627.0845 | 443.2795 | 659.2752 | 669.9012 | 615.0528
1824.1917 | 292.2042 | 628.023 | 444.5487 | 659.9471 | 669.1759 | 613.5122
1825.1917 | 292.4035 | 628.911 | 445.244 | 658.9533 | 668.6786 | 612.7016
1826.1917 | 293.896 | 627.7251 | 445.3423 | 659.5 | 672.2272 | 612.0984
1827.1917 | 294.4952 | 628.2172 | 445.4709 | 657.5307 | 670.8649 | 611.6674
1828.1917 | 294.4331 | 626.9149 | 445.7617 | 663.5439 | 670.7177 | 611.6444
1829.1917 | 294.3978 | 627.0935 | 447.0343 | 665.0991 | 674.6283 | 609.7939
1830.1917 | 294.6491 | 628.0728 | 447.6709 | 669.6549 | 676.0204 | 607.3951
1831.1917 | 295.2223 | 626.5137 | 448.8848 | 667.5231 | 674.7507 | 607.0078
1832.1917 | 295.7357 | 627.0854 | 449.0294 | 669.5911 | 679.8476 | 617.2806
1833.1917 | 295.9805 | 628.2667 | 448.8961 | 665.8267 | 676.9362 | 616.009
1834.1917 | 295.6415 | 627.5209 | 450.1202 | 662.1769 | 676.7425 | 612.8072
1835.1917 | 295.5943 | 625.9863 | 450.7888 | 660.4261 | 678.4573 | 622.0344
1836.1917 | 295.7433 | 627.8524 | 451.6766 | 665.5315 | 681.085 | 618.9898
1837.1917 | 296.3287 | 627.2818 | 451.5027 | 662.4218 | 679.6454 | 620.6589
1838.1917 | 297.5739 | 627.1808 | 451.6814 | 662.2665 | 679.8191 | 619.2999
1839.1917 | 297.5315 | 626.2921 | 452.7438 | 666.5264 | 680.8262 | 615.6516
1840.1917 | 297.8667 | 626.7231 | 452.6858 | 665.2891 | 678.8499 | 611.8687
1841.1917 | 297.7462 | 626.5305 | 453.2101 | 663.9133 | 678.1728 | 608.7526
1842.1917 | 298.1326 | 626.795 | 454.337 | 659.6066 | 673.8104 | 607.0861
1843.1917 | 298.8457 | 628.666 | 454.4594 | 659.927 | 673.6118 | 608.1272
1844.1917 | 299.5417 | 627.567 | 454.5399 | 662.5384 | 670.4833 | 607.8157
1845.1917 | 300.1849 | 627.4024 | 454.8261 | 659.8212 | 667.6383 | 608.861
1846.1917 | 300.5431 | 627.1163 | 455.1393 | 661.2536 | 667.3593 | 608.54
1847.1917 | 301.5063 | 627.5358 | 455.573 | 665.2297 | 668.535 | 609.1301
1848.1917 | 302.1587 | 627.8328 | 455.2194 | 661.9154 | 672.3083 | 613.6674
1849.1917 | 301.9518 | 627.4427 | 455.1971 | 659.8246 | 671.3028 | 613.3024
1850.1917 | 301.6374 | 627.4459 | 455.7639 | 663.2454 | 670.2347 | 614.4952
1851.1917 | 301.9335 | 628.3316 | 456.5071 | 663.9828 | 667.825 | 612.5266
1852.1917 | 301.9121 | 626.4293 | 456.6752 | 664.4052 | 668.3946 | 609.4289
1853.1917 | 302.5353 | 625.9232 | 457.4245 | 662.1953 | 670.6664 | 610.7712
1854.1917 | 302.3799 | 627.282 | 457.5845 | 664.9439 | 675.1586 | 610.501
1855.1917 | 302.474 | 627.8559 | 457.7369 | 664.5039 | 673.0411 | 607.4846
1856.1917 | 302.9507 | 628.1588 | 457.9445 | 662.2773 | 671.8973 | 608.8104
1857.1917 | 303.4186 | 627.5268 | 457.7956 | 661.1939 | 671.1958 | 615.2616
1858.1917 | 304.077 | 629.8771 | 458.5364 | 661.7987 | 671.9378 | 615.2568
1859.1917 | 304.2927 | 629.3635 | 459.6226 | 661.2583 | 671.4466 | 617.2021
1860.1917 | 304.07 | 627.1206 | 459.7599 | 664.2726 | 672.538 | 613.152
1861.2073 | 304.1816 | 627.7324 | 460.2602 | 663.026 | 672.8636 | 609.4637
1862.1917 | 305.767 | 629.3077 | 460.5167 | 663.2583 | 675.0042 | 613.2127
1863.2073 | 307.3584 | 628.0716 | 460.9349 | 667.974 | 679.483 | 613.5128
1864.1917 | 306.8445 | 628.4525 | 461.2886 | 665.7118 | 679.6661 | 610.5225
1865.1917 | 306.3513 | 629.5768 | 462.8536 | 666.9695 | 678.973 | 607.1665
1866.1917 | 306.7308 | 629.87 | 463.8174 | 669.8216 | 679.5825 | 620.2845
1867.1917 | 307.3052 | 631.4767 | 464.9324 | 672.4568 | 686.4434 | 623.842
1868.1917 | 307.6516 | 631.0627 | 465.1087 | 672.5696 | 682.944 | 622.6568
1869.1917 | 309.5204 | 631.0572 | 465.5612 | 672.9119 | 679.8296 | 624.5061
1870.1917 | 309.4431 | 631.0077 | 466.4052 | 674.5803 | 691.4449 | 633.6412
1871.1917 | 309.2351 | 631.4618 | 466.8929 | 673.4098 | 692.5207 | 631.2543
1872.1917 | 309.2394 | 631.4602 | 466.9252 | 671.3104 | 688.5905 | 629.0272
1873.1917 | 309.4266 | 630.8997 | 467.0505 | 672.5983 | 686.4338 | 626.6016
1874.1917 | 309.3701 | 630.4975 | 466.8252 | 672.14 | 685.3794 | 627.7633
1875.1917 | 309.8703 | 631.36 | 468.1219 | 672.6248 | 681.5299 | 626.068
1876.1917 | 310.2485 | 633.9698 | 469.7844 | 670.9286 | 681.4867 | 625.3594
1877.1917 | 310.4619 | 634.3511 | 471.4175 | 673.0055 | 688.4851 | 629.7441
1878.1917 | 310.9051 | 634.0373 | 470.1686 | 675.0945 | 689.8333 | 636.4536
1879.1917 | 312.4486 | 634.0654 | 471.1951 | 676.041 | 692.6901 | 639.7648
1880.1917 | 313.2527 | 633.663 | 470.6086 | 677.1653 | 688.9912 | 640.1514
1881.1917 | 313.2143 | 632.7765 | 471.6119 | 674.2153 | 682.93 | 639.2601
1882.1917 | 313.5375 | 632.4209 | 470.8915 | 671.0889 | 679.8888 | 636.3086
1883.1917 | 313.7647 | 632.0643 | 471.4161 | 669.7578 | 677.4627 | 634.4464
1884.1917 | 313.7846 | 632.0645 | 471.8903 | 672.7984 | 679.4423 | 635.1046
1885.1917 | 313.9124 | 632.7181 | 471.8283 | 668.3708 | 679.9675 | 631.8616
1886.1917 | 315.0819 | 634.0545 | 472.0928 | 667.0498 | 676.5149 | 632.0752
1887.1917 | 317.2435 | 633.8664 | 472.5014 | 667.0042 | 680.823 | 637.3545
1888.1917 | 317.3797 | 634.502 | 473.0353 | 674.7706 | 690.6914 | 651.1113
1889.1917 | 317.716 | 634.0652 | 474.4246 | 673.7337 | 687.4586 | 646.8348
1890.1917 | 318.3633 | 634.1802 | 474.03 | 670.7589 | 684.9443 | 647.7012
1891.1917 | 317.7205 | 635.0274 | 474.7939 | 671.8035 | 691.162 | 647.7307
1892.1917 | 317.5022 | 636.1705 | 475.2322 | 675.4122 | 689.4925 | 642.4235
1893.1917 | 318.0182 | 633.6911 | 475.226 | 673.2003 | 682.5201 | 637.4232
1894.1917 | 318.1594 | 634.3476 | 475.5114 | 675.0395 | 681.8849 | 633.268
1895.1917 | 319.2913 | 636.0225 | 475.7908 | 672.8578 | 681.5112 | 630.7567
1896.1917 | 319.6941 | 635.052 | 475.8463 | 672.4481 | 677.3396 | 630.8897
1897.1917 | 319.4734 | 634.8851 | 476.84 | 672.846 | 681.4703 | 635.0042
1898.1917 | 319.7012 | 635.7479 | 476.7508 | 673.2033 | 678.0132 | 630.3095
1899.1917 | 319.9977 | 635.3628 | 477.9845 | 670.2464 | 680.3106 | 630.3447
1900.1917 | 320.2597 | 635.6465 | 478.2465 | 672.0582 | 684.6062 | 629.6544
1901.1917 | 320.5919 | 635.2963 | 478.1131 | 669.3285 | 680.8539 | 631.2712
1902.1917 | 321.2668 | 634.8328 | 478.0757 | 668.4538 | 679.2095 | 634.3012
1903.1917 | 321.7613 | 636.0822 | 479.1389 | 667.8619 | 677.3752 | 636.1475
1904.1917 | 321.6648 | 637.8526 | 479.5251 | 669.9879 | 682.2683 | 639.3955
1905.1917 | 322.7575 | 636.7686 | 478.9324 | 670.2552 | 682.8858 | 638.7257
1906.1917 | 324.407 | 637.477 | 480.954 | 671.8442 | 683.3379 | 644.9766
1907.1917 | 324.2013 | 638.5818 | 482.8978 | 675.0266 | 689.3128 | 649.5019
1908.1917 | 323.9926 | 637.9272 | 482.545 | 672.5156 | 692.9925 | 647.3947
1909.1917 | 324.7443 | 638.6894 | 482.308 | 678.9162 | 696.3938 | 646.6573
1910.1917 | 324.8027 | 637.4376 | 481.4272 | 678.9044 | 696.328 | 646.3943
1911.1917 | 325.0713 | 635.7661 | 482.0715 | 677.3266 | 690.9432 | 647.1635
1912.1917 | 324.1872 | 636.8779 | 481.9332 | 677.3203 | 688.1216 | 647.5504
1913.1917 | 324.179 | 638.0286 | 482.8907 | 676.0334 | 686.8154 | 642.1605
1914.1917 | 324.3279 | 636.6745 | 482.9485 | 673.2537 | 681.6976 | 654.9394
1915.1917 | 325.3185 | 637.8348 | 482.5748 | 670.2099 | 680.2098 | 654.0991
1916.1917 | 325.2581 | 636.965 | 483.1718 | 670.0188 | 678.202 | 650.983
1917.1917 | 325.302 | 637.3665 | 483.0118 | 669.3203 | 676.2635 | 650.1322
1918.1917 | 324.9677 | 638.043 | 483.8171 | 670.6013 | 674.3256 | 647.0296
1919.1917 | 325.1798 | 636.5735 | 483.8146 | 668.3553 | 670.8023 | 640.3967
1920.1917 | 325.2339 | 638.088 | 485.2643 | 666.0316 | 668.2993 | 639.1668
1921.1917 | 325.9868 | 637.0128 | 484.6704 | 669.3548 | 673.2493 | 646.9194
1922.1917 | 326.7437 | 637.1494 | 484.5289 | 665.1921 | 668.0604 | 643.4287
1923.1917 | 327.1497 | 636.2874 | 485.5931 | 674.395 | 666.9351 | 640.8211
1924.1917 | 327.2114 | 637.0083 | 486.1511 | 675.3574 | 668.7756 | 638.0448
1925.1917 | 327.6253 | 636.2028 | 486.5098 | 679.2603 | 672.8366 | 648.3398
1926.1917 | 327.3609 | 638.6574 | 487.6565 | 676.3589 | 678.4796 | 648.6144
1927.1917 | 328.3827 | 638.2947 | 488.579 | 672.9524 | 678.0536 | 650.1321
1928.1917 | 329.967 | 638.1081 | 487.566 | 678.8513 | 676.7962 | 648.8356
1929.1917 | 330.5238 | 639.6802 | 488.6351 | 677.9362 | 676.7528 | 651.2105
1930.1917 | 330.5651 | 639.8355 | 489.8066 | 684.6268 | 681.8476 | 656.6744
1931.1917 | 331.2335 | 641.1241 | 490.1903 | 686.062 | 683.1199 | 654.1025
1932.1917 | 330.8997 | 640.6871 | 490.3076 | 691.793 | 686.1483 | 652.7719
1933.1917 | 330.7166 | 639.5602 | 489.9009 | 691.4478 | 688.8111 | 656.7989
1934.1917 | 331.8288 | 638.959 | 490.7024 | 686.4073 | 686.6659 | 656.1325
1935.1917 | 332.0164 | 638.4183 | 490.491 | 686.5385 | 684.0989 | 653.8785
1936.1917 | 332.0518 | 639.0545 | 491.2307 | 683.4023 | 682.8164 | 651.0231
1937.1917 | 333.7741 | 639.4762 | 491.1702 | 683.98 | 684.6841 | 652.277
1938.1917 | 333.5268 | 638.617 | 490.7567 | 684.6346 | 685.4294 | 659.1032
1939.1917 | 333.08 | 638.735 | 492.114 | 683.8686 | 683.5947 | 660.2624
1940.1917 | 332.9274 | 639.2159 | 491.8911 | 683.8222 | 688.9958 | 659.7189
1941.1917 | 334.2842 | 640.3704 | 492.1468 | 681.3589 | 686.5896 | 658.2171
1942.1917 | 334.5916 | 640.2084 | 492.1673 | 681.8079 | 686.9757 | 661.4999
1943.1917 | 335.4398 | 639.631 | 492.1169 | 681.0306 | 682.3318 | 656.5179
1944.1917 | 335.7406 | 640.1629 | 491.9129 | 684.6213 | 680.8845 | 655.4426
1945.1917 | 336.291 | 639.8394 | 492.2499 | 685.138 | 681.9216 | 651.176
1946.1917 | 336.9164 | 640.82 | 492.4926 | 680.0488 | 676.7198 | 646.9017
1947.1917 | 337.1134 | 642.5375 | 493.1685 | 678.6778 | 675.1125 | 646.8308
1948.1917 | 337.3674 | 641.8377 | 493.8939 | 678.7739 | 677.7919 | 647.374
1949.1917 | 337.2912 | 642.6811 | 494.4745 | 679.2357 | 684.6226 | 644.6942
1950.1917 | 337.254 | 642.5766 | 493.7703 | 679.5014 | 689.754 | 643.2536
1951.1917 | 337.5908 | 643.2029 | 494.7271 | 683.6769 | 693.1905 | 645.7411
1952.1917 | 338.1425 | 643.1984 | 495.8282 | 687.6361 | 690.3071 | 648.2868
1953.1917 | 338.1758 | 643.1441 | 497.2596 | 685.9064 | 685.4929 | 648.116
1954.1917 | 338.2634 | 642.9675 | 497.8836 | 689.4516 | 684.5689 | 647.8296
1955.1917 | 338.2584 | 644.0607 | 497.8808 | 691.4849 | 681.7526 | 642.6984
1956.1917 | 338.5398 | 641.802 | 498.8332 | 694.2678 | 685.9196 | 644.8738
1957.1917 | 338.8839 | 643.9167 | 498.043 | 690.3718 | 684.8158 | 644.1328
1958.1917 | 339.3393 | 643.4819 | 499.0989 | 687.682 | 684.8488 | 645.4321
1959.1917 | 340.4081 | 642.58 | 498.6843 | 685.4077 | 684.2905 | 645.3672
1960.1917 | 340.0915 | 641.2734 | 498.2056 | 680.581 | 685.6176 | 645.4612
1961.1917 | 339.9889 | 643.0181 | 498.4922 | 680.9777 | 683.7445 | 644.4372
1962.1917 | 339.8788 | 641.6326 | 499.3731 | 679.8092 | 685.1723 | 645.5883
1963.2073 | 340.4646 | 642.2291 | 499.3664 | 680.191 | 684.8161 | 645.4761
1964.1917 | 341.8645 | 642.6626 | 499.636 | 678.7682 | 681.3906 | 643.1497
1965.1917 | 341.5787 | 642.1313 | 500.4866 | 677.6544 | 680.2685 | 643.2629
1966.1917 | 343.389 | 641.6132 | 500.5017 | 677.9251 | 680.0427 | 651.8662
1967.1917 | 343.3483 | 642.8711 | 502.0158 | 672.7612 | 681.1278 | 653.4579
1968.1917 | 343.0457 | 643.2345 | 502.5005 | 673.165 | 680.9409 | 655.9876
1969.1917 | 343.6744 | 643.9752 | 502.7747 | 678.7538 | 682.8836 | 661.5689
1970.1917 | 343.351 | 642.6557 | 503.8661 | 678.3409 | 684.1203 | 655.4207
1971.1917 | 342.9123 | 641.8592 | 503.2926 | 679.3574 | 686.3146 | 650.1424
1972.1917 | 343.7187 | 643.0381 | 503.0186 | 678.7915 | 688.6046 | 650.2874
1973.1917 | 344.1703 | 644.2475 | 504.1543 | 677.6174 | 683.8683 | 649.4913
1974.1917 | 344.2774 | 643.5651 | 503.4199 | 678.4856 | 686.4155 | 653.9261
1975.1917 | 346.1163 | 643.8016 | 504.2845 | 680.2636 | 688.59 | 651.8641
1976.1917 | 345.9159 | 642.2669 | 504.203 | 678.5806 | 685.0043 | 658.6136
1977.1917 | 346.5783 | 641.7521 | 505.6179 | 676.9924 | 682.4917 | 653.4201
1978.1917 | 346.8521 | 643.3039 | 505.0614 | 676.9429 | 683.0694 | 652.716
1979.1917 | 347.5801 | 642.1679 | 505.5244 | 681.2646 | 681.1562 | 651.6012
1980.1917 | 347.4467 | 643.7071 | 505.4397 | 684.1754 | 684.6477 | 650.947
1981.1917 | 347.6475 | 642.9422 | 505.25 | 682.7644 | 682.5386 | 648.1734
1982.1917 | 347.5149 | 642.9385 | 505.8588 | 684.3289 | 678.5416 | 646.9864
1983.1917 | 348.3668 | 643.4671 | 507.286 | 683.9674 | 681.1947 | 649.9425
1984.1917 | 348.3115 | 644.1641 | 507.962 | 686.648 | 683.1295 | 667.3511
1985.1917 | 348.2249 | 646.4091 | 508.134 | 688.8739 | 684.7867 | 665.8859
1986.1917 | 348.8073 | 645.9568 | 507.4072 | 688.0362 | 687.484 | 682.0218
1987.1917 | 349.4067 | 645.82 | 507.1849 | 688.2454 | 685.5476 | 685.9268
1988.1917 | 349.1224 | 645.7834 | 506.9886 | 692.2834 | 685.491 | 679.4281
1989.1917 | 349.1422 | 645.2569 | 507.6254 | 693.7929 | 690.8428 | 676.3151
1990.1917 | 349.4014 | 646.0772 | 508.1076 | 692.4442 | 691.1842 | 673.789
1991.1917 | 350.5756 | 645.5459 | 507.7258 | 697.3729 | 691.4207 | 672.5215
1992.1917 | 350.8997 | 644.9015 | 507.9419 | 695.6464 | 686.7028 | 672.8885
1993.2073 | 351.0342 | 646.3058 | 508.4519 | 693.1745 | 689.9301 | 668.4575
1994.1917 | 351.0458 | 645.8531 | 508.6461 | 695.5554 | 688.216 | 665.082
1995.1917 | 352.1728 | 647.8029 | 508.9895 | 693.6868 | 687.9584 | 662.9544
1996.1917 | 352.3615 | 647.6675 | 508.8647 | 693.1936 | 689.5728 | 664.9941
1997.1917 | 353.1872 | 647.0543 | 508.5146 | 693.4076 | 692.1812 | 671.2923
1998.1917 | 354.4655 | 646.7176 | 510.0959 | 692.6787 | 692.7573 | 673.6029
1999.1917 | 354.2175 | 645.9835 | 509.1688 | 688.9827 | 687.4281 | 668.8394
2000.1917 | 355.2709 | 646.7736 | 510.2884 | 686.6647 | 684.1796 | 663.7644
2001.1917 | 355.3541 | 646.8239 | 509.7651 | 685.9044 | 685.9402 | 667.8605
2002.1917 | 354.5423 | 646.4034 | 509.1553 | 681.7209 | 683.2701 | 668.015
2003.1917 | 354.2453 | 646.6265 | 509.5347 | 680.3249 | 681.6796 | 662.4708
2004.1917 | 354.4323 | 645.8692 | 510.1937 | 678.6708 | 680.5793 | 661.078
2005.1917 | 354.6038 | 646.7478 | 510.0643 | 676.465 | 679.9295 | 658.9771
2006.1917 | 354.9455 | 646.4558 | 510.8074 | 676.2536 | 679.2253 | 655.2502
2007.1917 | 355.3984 | 646.5304 | 510.7999 | 675.51 | 677.2677 | 653.1276
2008.1917 | 356.1682 | 647.3092 | 512.124 | 675.8483 | 679.029 | 651.2954
2009.1917 | 357.7843 | 645.7058 | 510.9874 | 675.1384 | 677.7635 | 651.4407
2010.1917 | 357.5808 | 646.0802 | 513.128 | 672.7102 | 676.463 | 649.7222
2011.1917 | 358.3793 | 645.3225 | 512.8693 | 668.0477 | 675.6077 | 651.1634
2012.1917 | 358.227 | 645.6919 | 511.9504 | 667.5899 | 677.8922 | 648.1898
2013.1917 | 358.1204 | 644.7259 | 513.7635 | 670.6907 | 681.9963 | 651.4182
2014.1917 | 357.611 | 645.524 | 513.7459 | 673.0438 | 682.0415 | 649.8705
2015.1917 | 358.4685 | 647.3276 | 514.627 | 675.5355 | 683.117 | 648.5531
2016.1917 | 359.1175 | 645.9241 | 515.4874 | 675.1585 | 682.4157 | 652.8972
2017.1917 | 359.6894 | 646.0596 | 514.8821 | 673.8814 | 684.8622 | 654.909
2018.1917 | 359.6593 | 646.8365 | 515.1746 | 680.1136 | 691.9244 | 659.6722
2019.1917 | 359.8018 | 645.8816 | 517.1321 | 677.7392 | 688.0506 | 667.0038
2020.1917 | 360.8227 | 646.6466 | 516.4295 | 674.568 | 683.7843 | 667.3259
2021.1917 | 361.2677 | 646.012 | 517.1875 | 679.3685 | 683.6835 | 669.0953
2022.1917 | 360.6715 | 645.4495 | 517.1337 | 678.6531 | 684.9639 | 672.4178
2023.2073 | 360.5369 | 647.4496 | 517.0889 | 679.7256 | 686.1363 | 669.3258
2024.1917 | 361.1257 | 647.6923 | 517.27 | 679.1295 | 684.5665 | 668.3868
2025.1917 | 362.7237 | 647.9911 | 517.3532 | 679.8914 | 686.3086 | 679.0942
2026.1917 | 362.5815 | 646.9532 | 519.4049 | 681.1585 | 693.4161 | 676.9214
2027.1917 | 362.7277 | 648.2775 | 519.2135 | 685.0026 | 691.6296 | 673.0021
2028.1917 | 363.9696 | 648.1549 | 520.9218 | 683.7242 | 695.5968 | 684.7798
2029.1917 | 363.6962 | 648.4472 | 521.1914 | 684.3871 | 695.7696 | 681.5545
2030.1917 | 363.352 | 648.4665 | 519.7433 | 685.6812 | 694.7235 | 678.8317
2031.1917 | 363.4905 | 646.7814 | 520.6786 | 680.1425 | 688.483 | 674.2162
2032.1917 | 363.2791 | 648.2912 | 521.786 | 678.9535 | 687.8483 | 670.012
2033.1917 | 363.3425 | 648.5397 | 521.6156 | 682.0702 | 685.6654 | 667.5717
2034.1917 | 363.7392 | 647.3164 | 519.9094 | 681.3854 | 686.9593 | 664.6436
2035.1917 | 364.2364 | 647.3955 | 519.6266 | 682.8255 | 685.111 | 661.8764
2036.1917 | 365.0386 | 647.1464 | 519.9855 | 688.8283 | 684.3135 | 660.2906
2037.1917 | 366.0502 | 647.0401 | 520.4869 | 684.8934 | 682.843 | 660.8634
2038.1917 | 368.3606 | 646.9882 | 519.5262 | 686.0012 | 679.5589 | 663.5626
2039.1917 | 371.0543 | 647.4603 | 520.0223 | 685.4604 | 679.3785 | 667.5167
2040.1917 | 372.2268 | 647.1459 | 519.8257 | 687.8911 | 681.7261 | 673.8072
2041.1917 | 372.3076 | 646.4685 | 519.5412 | 686.2987 | 679.4783 | 674.9548
2042.1917 | 371.9511 | 646.169 | 519.7862 | 685.4958 | 677.2284 | 670.6176
2043.1917 | 370.7895 | 646.2261 | 519.898 | 693.271 | 675.0002 | 671.6637
2044.1917 | 370.0823 | 646.3767 | 521.0801 | 695.9802 | 672.6494 | 669.8154
2045.1917 | 371.5865 | 646.122 | 520.2568 | 700.5035 | 670.2104 | 664.4912
2046.1917 | 373.4594 | 646.0426 | 519.4828 | 701.5365 | 670.0088 | 671.2464
2047.1917 | 373.3908 | 645.7764 | 519.7873 | 699.7536 | 671.7278 | 669.8369
2048.1917 | 373.2259 | 645.7794 | 520.009 | 705.9917 | 671.0269 | 669.8927
2049.1917 | 373.5023 | 645.5731 | 520.0182 | 704.6663 | 669.3165 | 672.6748
2050.1917 | 373.3146 | 645.2495 | 520.0034 | 711.1444 | 667.6055 | 668.5404
2051.1917 | 373.6068 | 645.886 | 520.4082 | 709.2984 | 664.357 | 665.3567
2052.1917 | 373.5606 | 645.1612 | 519.6924 | 704.5861 | 664.0765 | 662.5093
2053.1917 | 372.9569 | 645.4395 | 520.2424 | 697.7411 | 662.5835 | 658.9425
2054.1917 | 373.2766 | 645.0306 | 521.0165 | 700.9979 | 661.0871 | 657.282
2055.1917 | 373.9236 | 645.9045 | 521.0683 | 696.6163 | 670.1433 | 662.167
2056.1917 | 373.781 | 646.2983 | 521.4165 | 690.0302 | 673.1247 | 658.6741
2057.1917 | 373.7305 | 646.5354 | 522.1922 | 683.7242 | 671.5766 | 657.1401
2058.1917 | 375.2143 | 647.4997 | 523.2228 | 684.0043 | 676.7056 | 657.8764
2059.1917 | 376.3888 | 646.9358 | 522.9569 | 682.111 | 678.9828 | 660.6078
2060.1917 | 376.6851 | 646.899 | 523.2916 | 679.9029 | 676.083 | 667.8745
2061.1917 | 376.8113 | 646.0808 | 524.3534 | 680.6144 | 671.3149 | 671.9169
2062.1917 | 376.6874 | 647.2928 | 524.8052 | 690.4617 | 673.5858 | 670.9538
2063.1917 | 376.7638 | 647.8851 | 525.9838 | 693.6346 | 674.4959 | 668.573
2064.1917 | 376.2925 | 648.1918 | 526.8419 | 691.5192 | 678.5459 | 677.988
2065.1917 | 377.8559 | 648.2481 | 528.9515 | 687.4705 | 685.241 | 687.1844
2066.1917 | 378.4786 | 647.0287 | 526.5995 | 681.0863 | 681.1789 | 685.9083
2067.1917 | 379.5111 | 647.5576 | 525.5652 | 684.883 | 679.5783 | 689.4378
2068.1917 | 380.5929 | 647.4215 | 527.0699 | 686.6918 | 684.4212 | 689.6136
2069.1917 | 382.2182 | 646.9658 | 526.7546 | 683.545 | 679.4772 | 683.1961
2070.1917 | 381.9653 | 647.7593 | 527.538 | 680.6702 | 679.7681 | 682.4608
2071.1917 | 382.7668 | 647.9704 | 527.4264 | 681.3261 | 681.6849 | 684.8625
2072.1917 | 382.9476 | 648.8988 | 527.7943 | 677.6338 | 677.6497 | 689.0647
2073.1917 | 382.9347 | 647.8175 | 529.623 | 677.7816 | 679.5069 | 691.9598
2074.1917 | 384.3303 | 647.7438 | 528.294 | 676.2921 | 675.6586 | 684.4419
2075.1917 | 385.1422 | 647.6105 | 529.534 | 674.0382 | 674.5842 | 681.7964
2076.1917 | 386.4942 | 646.8215 | 527.8199 | 673.6859 | 673.3937 | 680.7493
2077.1917 | 386.8942 | 646.8423 | 527.2492 | 672.0999 | 668.4476 | 683.1806
2078.1917 | 386.9781 | 646.7268 | 527.2702 | 671.9663 | 668.0486 | 689.6389
2079.1917 | 389.7067 | 646.4013 | 528.2762 | 666.3683 | 670.5008 | 691.005
2080.1917 | 390.7571 | 646.8905 | 527.2236 | 667.5122 | 670.5649 | 698.3492
2081.1917 | 391.0943 | 647.3882 | 527.9146 | 666.9555 | 674.0038 | 696.8185
2082.2073 | 390.69 | 646.8114 | 527.3112 | 662.8511 | 670.3919 | 701.7303
2083.2073 | 389.1401 | 645.6371 | 527.4375 | 658.6848 | 666.8176 | 693.6034
2084.1917 | 389.5583 | 646.2931 | 529.1148 | 660.629 | 665.149 | 695.1616
2085.1917 | 390.1487 | 645.757 | 529.006 | 661.091 | 666.4521 | 694.2425
2086.2073 | 389.5738 | 645.6625 | 528.8752 | 662.4321 | 663.5862 | 691.5973
2087.1917 | 390.3057 | 645.5318 | 529.8989 | 665.8661 | 660.0858 | 695.0659
2088.2073 | 391.1048 | 645.6229 | 530.2648 | 670.187 | 660.5739 | 698.8325
2089.1917 | 390.8005 | 645.8075 | 528.6103 | 662.3116 | 657.2611 | 690.0983
2090.1917 | 391.5318 | 646.3881 | 528.2214 | 666.0363 | 662.5005 | 689.538
2091.1917 | 392.0709 | 645.9891 | 529.9631 | 669.9511 | 659.3622 | 682.9663
2092.1917 | 392.124 | 645.9789 | 532.9079 | 671.393 | 659.9311 | 685.4995
2093.1917 | 392.2019 | 646.3587 | 530.748 | 670.0224 | 660.9262 | 687.7313
2094.1917 | 392.2594 | 646.4098 | 531.9612 | 670.796 | 660.8399 | 685.1152
2095.1917 | 392.4057 | 647.7078 | 532.3933 | 667.5121 | 663.9997 | 687.8147
2096.1917 | 394.3771 | 646.8937 | 531.6055 | 670.8658 | 670.4797 | 696.4941
2097.1917 | 393.7764 | 646.5433 | 531.8257 | 671.3833 | 668.7272 | 694.6893
2098.1917 | 394.5959 | 647.0453 | 532.7099 | 677.9419 | 666.438 | 691.5547
2099.1917 | 394.8313 | 647.4349 | 533.3038 | 681.6438 | 671.7129 | 688.0607
2100.1917 | 395.4528 | 647.1071 | 532.4275 | 678.8169 | 670.8141 | 687.9249
2101.1917 | 396.1505 | 646.7943 | 532.3348 | 676.717 | 665.7788 | 684.6225
2102.1917 | 396.0073 | 647.1398 | 533.5972 | 673.9424 | 670.4312 | 684.3693
2103.1917 | 397.0007 | 647.7026 | 534.1342 | 675.1185 | 667.8999 | 679.116
2104.1917 | 396.6472 | 647.5157 | 535.7958 | 681.6577 | 666.9213 | 683.3356
2105.1917 | 397.2233 | 647.169 | 535.7877 | 676.4366 | 666.3642 | 686.8083
2106.1917 | 397.2911 | 647.4428 | 535.6006 | 675.3593 | 669.6666 | 687.4529
2107.1917 | 397.431 | 648.6098 | 536.6417 | 675.9023 | 675.44 | 687.0547
2108.1917 | 397.0692 | 647.3296 | 536.6982 | 672.6134 | 675.0239 | 692.5868
2109.1917 | 396.7429 | 647.58 | 536.0996 | 669.5356 | 674.9446 | 691.524
2110.1917 | 397.4986 | 647.2699 | 534.7173 | 669.2835 | 671.7208 | 684.6778
2111.1917 | 399.4238 | 646.763 | 536.7362 | 663.4922 | 664.3016 | 679.5937
2112.1917 | 401.881 | 647.1379 | 537.4313 | 666.9288 | 667.016 | 684.974
2113.2073 | 401.6266 | 647.3767 | 535.1517 | 662.7198 | 664.4971 | 688.519
2114.1917 | 401.3862 | 646.9659 | 535.1089 | 672.9431 | 664.3721 | 697.16
2115.1917 | 400.7483 | 646.782 | 535.3759 | 669.7518 | 660.3336 | 696.46
2116.1917 | 401.6644 | 646.7164 | 535.1675 | 680.5709 | 657.455 | 689.5366
2117.1917 | 401.5226 | 646.7764 | 535.7066 | 682.8407 | 656.1968 | 681.4196
2118.1917 | 401.5528 | 646.2159 | 535.5809 | 683.6662 | 653.7269 | 677.5979
2119.1917 | 402.1077 | 646.3568 | 537.618 | 682.1158 | 654.8816 | 682.0235
2120.1917 | 402.1587 | 646.7262 | 537.7973 | 685.1999 | 651.1844 | 689.1309
2121.1917 | 402.7914 | 646.1711 | 536.1467 | 685.03 | 653.0932 | 690.6163
2122.1917 | 403.2081 | 645.8567 | 535.4291 | 689.0395 | 652.0649 | 689.5385
2123.1917 | 403.1831 | 646.3929 | 535.4294 | 685.7904 | 656.571 | 686.8042
2124.1917 | 402.9099 | 646.468 | 537.3987 | 682.8264 | 654.2703 | 680.8721
2125.1917 | 402.8453 | 646.2307 | 536.0439 | 690.2177 | 653.1236 | 679.8541
2126.1917 | 403.8892 | 646.147 | 535.4363 | 692.0725 | 651.9227 | 674.1762
2127.1917 | 404.4167 | 645.8527 | 534.9522 | 688.5402 | 649.7477 | 677.5994
2128.1917 | 404.7741 | 645.8669 | 534.7991 | 689.2164 | 648.9983 | 675.9096
2129.1917 | 405.7129 | 645.6157 | 534.9605 | 691.6715 | 653.3378 | 675.42
2130.1917 | 406.5617 | 645.669 | 534.2169 | 700.2468 | 651.6991 | 674.8887
2131.1917 | 408.1863 | 645.8329 | 534.2406 | 698.2789 | 649.0112 | 673.3188
2132.1917 | 408.7351 | 645.7876 | 533.972 | 706.1709 | 652.4602 | 675.7214
2133.2073 | 408.6987 | 646.0155 | 533.555 | 704.3446 | 651.3546 | 677.1414
2134.1917 | 407.7477 | 646.5067 | 534.2683 | 702.7016 | 653.606 | 682.0436
2135.1917 | 408.3492 | 646.9167 | 536.59 | 702.574 | 657.0955 | 681.6186
2136.1917 | 409.9389 | 647.2424 | 536.5327 | 704.2508 | 659.9239 | 684.773
2137.1917 | 410.5872 | 647.2623 | 536.2399 | 702.8237 | 671.4814 | 691.4338
2138.1917 | 411.5195 | 647.1049 | 535.7785 | 705.1786 | 669.9556 | 691.7952
2139.1917 | 412.8944 | 646.8448 | 536.6381 | 704.6791 | 664.1965 | 695.2162
2140.1917 | 413.2327 | 647.0557 | 536.6471 | 703.2202 | 671.7828 | 694.4118
2141.1917 | 412.9865 | 646.3291 | 538.673 | 702.6994 | 669.7675 | 690.0826
2142.1917 | 412.7836 | 646.5397 | 536.6084 | 707.1533 | 667.6796 | 689.0865
2143.2073 | 412.8945 | 647.0986 | 536.7627 | 701.6393 | 668.1706 | 690.9276
2144.1917 | 412.3561 | 647.2619 | 538.3061 | 700.5498 | 670.8294 | 697.0085
2145.1917 | 411.1877 | 647.6505 | 537.3746 | 695.6441 | 679.7492 | 693.819
2146.1917 | 412.0129 | 647.9375 | 537.834 | 691.9573 | 677.0342 | 691.5834
2147.1917 | 412.8258 | 648.2121 | 539.7779 | 691.3778 | 678.0679 | 707.6883
2148.1917 | 412.4729 | 648.0147 | 540.2188 | 686.1357 | 676.2194 | 698.9614
2149.1917 | 411.8973 | 648.8856 | 540.215 | 683.3769 | 685.7 | 704.5786
2150.1917 | 411.7759 | 649.1048 | 541.2515 | 682.7433 | 687.4687 | 705.9433
2151.1917 | 411.4808 | 648.178 | 540.9641 | 682.0094 | 694.4295 | 703.8083
2152.1917 | 411.8746 | 648.681 | 540.7941 | 680.5873 | 686.5102 | 706.6259
2153.1917 | 413.1432 | 648.8429 | 541.2213 | 679.1572 | 684.9831 | 706.8054
2154.1917 | 415.1444 | 649.4004 | 539.4808 | 676.521 | 685.6716 | 710.9981
2155.1917 | 417.7442 | 649.0603 | 539.0532 | 677.6411 | 688.8093 | 714.1074
2156.1917 | 417.9303 | 648.9897 | 538.7397 | 673.9676 | 683.8518 | 709.1628
2157.1917 | 418.2854 | 649.2337 | 540.8855 | 675.116 | 685.3058 | 703.0896
2158.1917 | 418.3823 | 650.4382 | 541.688 | 678.3672 | 680.3254 | 696.6251
2159.1917 | 419.1534 | 649.4974 | 540.5417 | 680.1189 | 688.5374 | 696.9609
2160.1917 | 420.3659 | 649.3634 | 539.7212 | 675.8915 | 684.3944 | 704.8174
2161.1917 | 422.109 | 648.7212 | 539.5033 | 674.8651 | 687.2875 | 702.2963
2162.1917 | 421.986 | 649.1552 | 539.9585 | 672.7706 | 681.8078 | 700.6206
2163.1917 | 420.4722 | 648.283 | 540.8798 | 673.555 | 674.7633 | 693.2754
2164.1917 | 419.7903 | 648.6778 | 540.7318 | 673.3978 | 669.9992 | 685.2674
2165.1917 | 419.8491 | 648.5831 | 539.7853 | 672.1778 | 665.848 | 678.8402
2166.1917 | 422.304 | 648.3311 | 538.9408 | 673.8561 | 661.909 | 675.28
2167.1917 | 423.15 | 648.6955 | 538.7231 | 673.549 | 660.5714 | 674.1666
2168.1917 | 422.3002 | 649.1269 | 539.1316 | 676.5941 | 665.5552 | 677.2394
2169.1917 | 422.0881 | 649.3768 | 542.7599 | 682.5655 | 672.0304 | 680.4064
2170.1917 | 422.695 | 649.1444 | 539.7757 | 686.5744 | 676.4721 | 685.2527
2171.1917 | 424.25 | 648.7787 | 539.1544 | 688.9893 | 675.5391 | 691.0341
2172.1917 | 424.5976 | 649.3569 | 539.2886 | 686.6915 | 682.5969 | 698.8492
2173.1917 | 424.9735 | 648.7272 | 540.6311 | 686.1182 | 678.8147 | 703.0404
2174.1917 | 423.9844 | 648.8441 | 540.9541 | 688.5953 | 673.9373 | 709.4209
2175.1917 | 424.4104 | 648.8334 | 540.5322 | 690.0657 | 671.8221 | 707.4831
2176.1917 | 425.6703 | 649.3351 | 540.2449 | 687.865 | 668.9484 | 709.5104
2177.1917 | 426.0906 | 648.7947 | 540.4646 | 688.74 | 673.5309 | 710.4361
2178.1917 | 426.3254 | 649.5473 | 541.4858 | 688.4808 | 677.6902 | 708.5319
2179.1917 | 426.4321 | 648.7926 | 541.9962 | 685.9198 | 679.3257 | 704.3497
2180.1917 | 426.7404 | 649.0877 | 542.1891 | 688.779 | 673.403 | 706.6488
2181.1917 | 429.3289 | 649.7775 | 541.3133 | 689.5514 | 669.1458 | 708.7611
2182.1917 | 430.0485 | 649.5864 | 543.1325 | 694.0908 | 686.3613 | 720.8056
2183.1917 | 430.2011 | 649.983 | 543.2634 | 689.5536 | 686.855 | 727.9897
2184.1917 | 429.0037 | 649.881 | 542.9948 | 686.0067 | 689.9507 | 730.1491
2185.1917 | 427.8961 | 649.296 | 541.6124 | 681.9142 | 684.6254 | 724.8014
2186.1917 | 428.0085 | 650.0227 | 543.422 | 680.3142 | 687.3641 | 727.3464
2187.1917 | 429.519 | 650.0151 | 543.0772 | 679.1798 | 687.8823 | 723.636
2188.1917 | 429.5502 | 649.441 | 541.1187 | 677.7807 | 680.2788 | 715.8792
2189.1917 | 430.0531 | 648.6641 | 542.2219 | 680.4394 | 676.0402 | 718.7355
2190.1917 | 430.374 | 649.6179 | 542.6812 | 677.6587 | 670.7485 | 716.6741
2191.1917 | 429.6786 | 650.6593 | 543.8439 | 678.7659 | 684.7484 | 721.0846
2192.1917 | 428.9034 | 651.2098 | 543.4619 | 684.8953 | 689.6 | 713.7784
2193.1917 | 429.335 | 651.2505 | 543.0868 | 693.8538 | 684.4566 | 715.5914
2194.1917 | 429.6813 | 651.5772 | 544.413 | 701.4149 | 688.5979 | 712.9193
2195.1917 | 430.2361 | 650.7218 | 544.1901 | 701.8653 | 693.571 | 727.1549
2196.1917 | 429.9919 | 650.3098 | 545.2118 | 701.2553 | 697.6996 | 718.0812
2197.1917 | 429.7852 | 650.1125 | 544.9473 | 702.6893 | 693.5702 | 707.9275
2198.1917 | 429.1483 | 649.9154 | 544.6141 | 694.7013 | 684.284 | 699.9978
2199.1917 | 429.5252 | 649.913 | 546.8182 | 701.8401 | 682.59 | 693.0761
2200.1917 | 431.097 | 650.8157 | 545.5128 | 702.2394 | 679.3653 | 687.9385
2201.1917 | 431.216 | 651.0687 | 546.9377 | 701.1383 | 675.942 | 681.4852
2202.1917 | 432.8932 | 650.2996 | 545.4932 | 698.377 | 680.5896 | 680.7021
2203.1917 | 433.6795 | 650.5679 | 544.8766 | 690.8418 | 673.4288 | 676.275
2204.1917 | 433.1887 | 650.3839 | 545.9368 | 696.1065 | 669.2876 | 677.233
2205.1917 | 433.7398 | 650.8835 | 546.5399 | 689.1177 | 666.4824 | 676.2914
2206.1917 | 432.8742 | 650.383 | 545.9017 | 681.4423 | 670.5713 | 680.0405
2207.1917 | 432.7443 | 650.7654 | 546.6537 | 675.5127 | 667.661 | 676.9393
2208.1917 | 432.8246 | 650.8129 | 546.7863 | 669.2417 | 663.1104 | 672.6456
2209.1917 | 433.8251 | 650.2735 | 546.6941 | 665.0606 | 661.7822 | 675.4023
2210.1917 | 434.4795 | 650.1743 | 546.9341 | 661.4522 | 659.7952 | 669.8507
2211.1917 | 434.772 | 649.8069 | 546.0647 | 665.3743 | 659.393 | 669.5335
2212.1917 | 435.3441 | 650.4899 | 546.7683 | 676.5656 | 657.3351 | 669.5877
2213.1917 | 434.8177 | 650.2164 | 548.2801 | 685.7098 | 653.4694 | 664.6774
2214.1917 | 433.8331 | 650.233 | 547.6087 | 688.1139 | 659.1446 | 669.2692
2215.1917 | 433.7086 | 649.9727 | 547.3082 | 688.0286 | 656.9579 | 664.2822
2216.1917 | 433.1839 | 649.8935 | 548.3263 | 685.8426 | 659.4587 | 660.3321
2217.1917 | 433.4004 | 650.0406 | 548.2475 | 685.3386 | 663.1072 | 657.3868
2218.1917 | 433.4322 | 649.9076 | 547.6049 | 688.3985 | 661.5338 | 657.8023
2219.1917 | 435.2139 | 649.7487 | 547.3549 | 691.0643 | 657.5399 | 656.2135
2220.1917 | 436.5669 | 649.524 | 548.2261 | 696.0053 | 655.6765 | 653.4313
2221.1917 | 437.2853 | 649.6002 | 547.6505 | 694.5606 | 654.5966 | 650.4907
2222.1917 | 436.5437 | 649.6923 | 547.0784 | 691.3092 | 653.5145 | 652.7485
2223.1917 | 437.1491 | 649.7933 | 547.8493 | 698.3049 | 664.2388 | 651.4246
2224.1917 | 438.8392 | 649.4599 | 547.2284 | 707.0422 | 661.3256 | 649.9213
2225.1917 | 439.0972 | 649.8058 | 550.0541 | 713.233 | 660.7815 | 652.3519
2226.1917 | 438.9465 | 650.0968 | 549.0001 | 715.1206 | 660.6618 | 649.8897
2227.1917 | 438.3784 | 650.382 | 549.9288 | 716.5507 | 667.3803 | 649.6797
2228.1917 | 440.1157 | 651.0189 | 551.4582 | 710.8349 | 678.6056 | 650.5308
2229.1917 | 438.9477 | 650.664 | 551.4137 | 709.4659 | 683.475 | 653.6471
2230.1917 | 437.9005 | 650.6668 | 550.8799 | 707.3698 | 678.9562 | 653.4957
2231.1917 | 438.8697 | 650.8667 | 552.1127 | 704.0088 | 676.6089 | 662.734
2232.1917 | 438.7811 | 650.5077 | 552.0563 | 704.3404 | 675.7151 | 665.8376
2233.2073 | 439.5898 | 650.1514 | 551.5544 | 706.6835 | 672.5042 | 665.4156
2234.1917 | 440.9015 | 649.7255 | 552.5104 | 705.2707 | 671.687 | 663.223
2235.1917 | 440.151 | 649.4465 | 551.7838 | 695.9872 | 665.5205 | 659.715
2236.1917 | 440.1402 | 649.4815 | 552.5358 | 694.1026 | 662.7654 | 658.3526
2237.1917 | 440.3519 | 649.8572 | 552.4356 | 690.4561 | 661.4292 | 655.3377
2238.1917 | 440.5886 | 650.1338 | 553.2441 | 686.1164 | 659.4004 | 652.4915
2239.1917 | 440.5176 | 649.7118 | 552.9734 | 691.1909 | 657.4898 | 650.9395
2240.1917 | 441.0856 | 649.6733 | 553.9081 | 686.7465 | 654.1219 | 646.8073
2241.1917 | 443.1285 | 650.4166 | 553.8885 | 687.0269 | 653.8372 | 661.2236
2242.1917 | 442.4377 | 650.3019 | 553.5585 | 692.7535 | 654.7021 | 673.3257
2243.1917 | 443.5621 | 651.5062 | 554.5329 | 694.5515 | 656.9239 | 681.6112
2244.1917 | 444.0157 | 650.7733 | 555.564 | 691.1089 | 658.8453 | 694.8433
2245.1917 | 444.4059 | 650.8617 | 554.272 | 697.6079 | 658.8114 | 701.6074
2246.1917 | 444.035 | 650.5871 | 554.3753 | 702.9572 | 665.223 | 708.4308
2247.1917 | 444.3892 | 650.4758 | 554.5008 | 704.5764 | 664.0941 | 699.9583
2248.1917 | 446.134 | 650.2209 | 553.6829 | 701.0332 | 662.7097 | 693.6857
2249.1917 | 446.903 | 649.9445 | 553.2184 | 691.5801 | 659.4655 | 689.8204
2250.1917 | 446.5012 | 650.0219 | 554.6193 | 695.2945 | 658.3602 | 683.2406
2251.1917 | 446.8611 | 649.7201 | 554.6051 | 691.3618 | 655.2468 | 677.5274
2252.1917 | 447.4096 | 649.9331 | 556.4422 | 699.0303 | 661.3146 | 673.7887
2253.1917 | 447.3698 | 650.2248 | 556.3742 | 711.8344 | 659.0949 | 669.0175
2254.1917 | 447.2419 | 650.0239 | 556.6369 | 711.4609 | 657.0752 | 669.2646
2255.1917 | 447.9114 | 650.9448 | 556.6749 | 712.0266 | 660.2308 | 669.1887
2256.1917 | 449.4571 | 651.1507 | 555.323 | 706.136 | 658.9454 | 669.4675
2257.1917 | 449.6564 | 650.6964 | 555.281 | 702.9324 | 659.3949 | 682.9094
2258.1917 | 451.802 | 650.6234 | 555.5058 | 706.7083 | 657.3708 | 681.0273
2259.1917 | 452.9777 | 651.1821 | 557.4191 | 708.9005 | 662.0892 | 686.5086
2260.1917 | 451.5109 | 651.0525 | 555.848 | 705.8101 | 657.6973 | 697.6974
2261.1917 | 450.7377 | 651.0701 | 556.6884 | 706.3893 | 660.1203 | 704.893
2262.1917 | 452.9813 | 651.3133 | 556.748 | 706.1954 | 657.89 | 704.0331
2263.2073 | 451.9111 | 652.2896 | 556.7973 | 706.3962 | 656.0407 | 699.0717
2264.1917 | 450.5057 | 652.6047 | 557.2912 | 706.1434 | 658.5216 | 706.5029
2265.1917 | 450.5597 | 652.6295 | 558.7836 | 706.5773 | 657.7905 | 710.359
2266.1917 | 451.2539 | 652.5078 | 559.2019 | 705.0376 | 657.5527 | 712.8949
2267.1917 | 454.1197 | 652.1548 | 558.7877 | 703.4274 | 657.4472 | 706.872
2268.1917 | 454.5153 | 651.6925 | 557.5329 | 708.6379 | 663.7501 | 708.8102
2269.1917 | 454.1239 | 651.5464 | 557.3303 | 710.1474 | 662.9014 | 698.6878
2270.1917 | 455.3438 | 651.9083 | 557.5136 | 719.5764 | 660.9393 | 701.5974
2271.1917 | 455.9076 | 652.9947 | 559.1853 | 721.3503 | 660.7657 | 704.4725
2272.1917 | 455.6604 | 652.41 | 559.5413 | 724.0412 | 662.2977 | 706.9513
2273.1917 | 454.5536 | 652.1441 | 558.8635 | 722.0907 | 660.4879 | 708.5639
2274.1917 | 454.6116 | 653.0904 | 558.6018 | 715.4824 | 658.4401 | 700.4761
2275.1917 | 455.6572 | 652.8648 | 559.3908 | 714.5562 | 656 | 702.7302
2276.1917 | 454.9081 | 653.0195 | 560.8259 | 725.3317 | 655.8674 | 695.3641
2277.1917 | 454.6949 | 653.3934 | 561.4578 | 724.9158 | 654.7178 | 690.2282
2278.1917 | 455.114 | 653.8334 | 560.2406 | 725.0239 | 655.3059 | 693.2462
2279.1917 | 456.2709 | 653.6179 | 559.7686 | 728.3533 | 653.5269 | 690.9356
2280.1917 | 456.7503 | 653.2806 | 561.0512 | 730.0311 | 651.6308 | 685.528
2281.1917 | 456.7878 | 653.4194 | 561.2734 | 723.9392 | 651.9882 | 681.4559
2282.1917 | 456.7566 | 653.901 | 561.8246 | 714.2947 | 651.8681 | 681.9386
2283.1917 | 459.5288 | 653.6662 | 562.0633 | 712.9088 | 651.0457 | 681.869
2284.1917 | 460.4934 | 653.608 | 560.3805 | 712.1429 | 651.2909 | 680.4038
2285.1917 | 460.5939 | 653.8159 | 560.578 | 701.3958 | 651.4358 | 677.4956
2286.1917 | 461.6619 | 653.9992 | 561.7949 | 702.0072 | 651.8792 | 672.0969
2287.1917 | 462.1703 | 654.3688 | 561.0679 | 705.6255 | 653.0757 | 673.7105
2288.1917 | 463.1253 | 654.8934 | 560.1243 | 706.4375 | 652.5932 | 673.1359
2289.1917 | 463.3028 | 653.9047 | 560.3194 | 704.392 | 655.1039 | 679.6569
2290.1917 | 464.1735 | 653.2557 | 560.6967 | 695.3256 | 653.8004 | 677.2429
2291.1917 | 461.922 | 653.8016 | 561.4197 | 689.6125 | 653.9862 | 682.8111
2292.1917 | 461.256 | 654.1728 | 561.7055 | 683.4786 | 654.6134 | 679.9314
2293.1917 | 461.8634 | 654.1529 | 563.005 | 678.6364 | 656.0975 | 688.1323
2294.1917 | 461.2196 | 653.6221 | 562.0063 | 688.5006 | 653.8136 | 680.5906
2295.1917 | 461.0527 | 654.5041 | 564.0214 | 686.2137 | 652.4641 | 679.733
2296.1917 | 462.0453 | 654.9518 | 564.3147 | 688.0031 | 651.1988 | 685.3307
2297.1917 | 461.6833 | 655.8622 | 563.6931 | 690.3797 | 650.9409 | 688.8835
2298.1917 | 461.6298 | 656.2737 | 563.9735 | 690.8977 | 648.4095 | 694.7641
2299.1917 | 462.1923 | 655.9272 | 564.8135 | 697.7438 | 650.5364 | 693.0586
2300.1917 | 463.3562 | 656.7441 | 565.3326 | 693.7215 | 651.3501 | 702.4611
2301.1917 | 463.345 | 656.3786 | 565.8914 | 695.0918 | 650.537 | 703.3508
2302.1917 | 462.5994 | 655.6983 | 565.7949 | 693.2489 | 654.0682 | 695.59
2303.1917 | 463.7508 | 656.8112 | 565.6075 | 694.0278 | 654.6199 | 697.6888
2304.1917 | 463.7132 | 656.8172 | 566.8141 | 695.5292 | 654.9774 | 700.0885
2305.1917 | 463.0491 | 656.5868 | 566.4784 | 693.9763 | 656.0906 | 694.2828
2306.1917 | 463.4135 | 657.2778 | 566.5972 | 698.9599 | 655.2458 | 697.5503
2307.1917 | 463.3156 | 657.6957 | 566.2945 | 697.3979 | 655.8043 | 693.3594
2308.1917 | 464.7186 | 657.5643 | 567.0935 | 698.3166 | 655.8774 | 691.1969
2309.1917 | 466.1702 | 657.4601 | 566.3998 | 699.4183 | 656.4225 | 697.322
2310.1917 | 466.9047 | 657.7793 | 567.3832 | 699.4562 | 655.701 | 693.2179
2311.1917 | 466.0786 | 658.097 | 567.761 | 706.2565 | 656.9961 | 693.0968
2312.1917 | 465.2026 | 658.5714 | 568.0315 | 699.4 | 656.6922 | 685.1138
2313.2073 | 465.8623 | 657.9792 | 567.5876 | 703.7057 | 656.7996 | 681.8658
2314.1917 | 466.991 | 657.4117 | 567.7394 | 701.5699 | 656.8324 | 678.405
2315.1917 | 467.0327 | 657.1042 | 567.5113 | 698.6194 | 656.7205 | 674.4278
2316.1917 | 468.0458 | 657.2339 | 566.6189 | 689.4103 | 654.6032 | 668.6854
2317.1917 | 469.6463 | 656.8877 | 567.0989 | 693.0158 | 652.4969 | 666.0967
2318.1917 | 470.201 | 656.6101 | 566.4424 | 686.3003 | 652.1371 | 668.3354
2319.1917 | 469.7635 | 656.8173 | 567.0639 | 680.0211 | 649.8089 | 662.4806
2320.1917 | 468.6641 | 656.5189 | 566.801 | 676.2978 | 649.0978 | 663.8785
2321.1917 | 468.2319 | 657.858 | 567.7281 | 680.2471 | 652.0562 | 662.5352
2322.1917 | 468.8548 | 657.0581 | 566.3314 | 678.1541 | 653.0053 | 672.2493
2323.2073 | 469.0885 | 657.1946 | 567.0101 | 672.2818 | 651.5953 | 675.4807
2324.1917 | 470.1975 | 656.7098 | 567.8456 | 690.5736 | 649.0581 | 669.3214
2325.1917 | 469.5543 | 656.7603 | 567.7264 | 685.7186 | 646.9385 | 664.5211
2326.1917 | 469.0545 | 656.4328 | 567.362 | 683.2609 | 644.9768 | 666.4273
2327.1917 | 468.3433 | 656.5308 | 568.3637 | 678.491 | 645.025 | 662.8324
2328.1917 | 468.0344 | 656.6877 | 568.8413 | 673.855 | 643.999 | 659.179
2329.1917 | 468.4645 | 656.6488 | 568.1213 | 683.2661 | 642.5022 | 663.0899
2330.1917 | 469.5233 | 656.2894 | 567.3674 | 676.3503 | 640.9016 | 659.9369
2331.1917 | 471.6938 | 656.4822 | 567.1705 | 674.8026 | 639.9266 | 656.8009
2332.1917 | 471.4209 | 656.3158 | 567.9532 | 673.1119 | 639.4993 | 657.893
2333.1917 | 471.7593 | 656.4336 | 567.2245 | 670.2868 | 638.0706 | 655.6129
2334.1917 | 472.568 | 656.6064 | 569.7721 | 677.7008 | 637.1971 | 667.4924
2335.1917 | 472.1038 | 656.1561 | 568.6579 | 689.1777 | 637.6635 | 674.6234
2336.1917 | 472.6536 | 655.8809 | 567.8844 | 690.6498 | 641.182 | 673.8252
2337.1917 | 473.4481 | 656.0166 | 568.5993 | 683.4445 | 638.75 | 669.9526
2338.1917 | 472.949 | 656.6494 | 568.6119 | 689.7619 | 637.6418 | 666.0593
2339.1917 | 472.8255 | 657.0991 | 569.2293 | 711.7184 | 637.8759 | 662.3064
2340.1917 | 474.2675 | 656.6433 | 568.7261 | 713.3873 | 637.5124 | 673.1063
2341.1917 | 474.1546 | 656.0732 | 569.0357 | 714.581 | 638.0492 | 677.5809
2342.1917 | 474.0228 | 655.6501 | 568.2887 | 701.9539 | 638.5162 | 686.8828
2343.1917 | 473.6311 | 655.8142 | 567.8911 | 692.8527 | 637.9002 | 677.4525
2344.1917 | 473.2185 | 656.1769 | 569.6864 | 695.935 | 637.8456 | 673.1853
2345.1917 | 472.5332 | 655.4612 | 569.7177 | 700.3853 | 636.8954 | 665.6775
2346.1917 | 473.4058 | 654.9931 | 569.3668 | 689.4223 | 637.016 | 662.5301
2347.1917 | 473.9868 | 654.9939 | 568.3566 | 686.0131 | 639.8278 | 678.0216
2348.1917 | 476.0862 | 654.5667 | 568.2735 | 687.2008 | 643.0455 | 686.0014
2349.1917 | 477.0334 | 654.39 | 568.8121 | 683.5618 | 643.7733 | 698.706
2350.1917 | 475.9398 | 654.4384 | 568.5163 | 686.143 | 644.7285 | 699.4975
2351.1917 | 475.5381 | 654.1356 | 567.7915 | 683.3885 | 644.6687 | 691.6311
2352.1917 | 476.4441 | 653.9249 | 567.4866 | 678.4875 | 645.1704 | 695.9955
2353.1917 | 476.766 | 654.1031 | 568.044 | 678.0114 | 645.8613 | 697.2024
2354.1917 | 476.8147 | 654.582 | 570.0041 | 676.0923 | 643.3131 | 686.4992
2355.1917 | 478.2921 | 654.659 | 570.1453 | 683.7218 | 641.9456 | 691.3865
2356.1917 | 477.0475 | 655.1254 | 570.7219 | 690.8623 | 639.8284 | 686.9153
2357.1917 | 475.994 | 654.7211 | 570.7943 | 695.7091 | 638.1575 | 694.7199
2358.1917 | 476.0192 | 655.2821 | 571.2902 | 705.2191 | 639.1501 | 700.6193
2359.1917 | 476.2311 | 654.92 | 570.4157 | 696.6663 | 640.5324 | 691.4221
2360.1917 | 477.5456 | 654.3475 | 571.2734 | 696.1019 | 640.1421 | 693.295
2361.1917 | 477.3188 | 655.2625 | 571.8245 | 694.6649 | 638.9377 | 701.1712
2362.1917 | 476.9683 | 655.2591 | 571.2556 | 695.8207 | 637.4331 | 705.2014
2363.1917 | 478.2058 | 655.532 | 572.3779 | 712.3866 | 636.7245 | 715.0358
2364.1917 | 477.5308 | 655.0643 | 573.368 | 712.4042 | 634.7497 | 719.7608
2365.1917 | 476.3209 | 656.2387 | 573.8332 | 720.5961 | 633.7806 | 725.4379
2366.1917 | 477.2268 | 656.0393 | 572.9323 | 716.268 | 633.1228 | 728.8011
2367.1917 | 479.0204 | 655.7639 | 572.8724 | 721.733 | 632.6786 | 729.3624
2368.1917 | 479.491 | 655.6123 | 574.1935 | 720.5335 | 632.3215 | 732.2071
2369.1917 | 479.5955 | 656.4107 | 575.0955 | 729.0421 | 630.2939 | 733.401
2370.1917 | 479.1523 | 655.9788 | 573.4041 | 731.2771 | 631.8497 | 731.3072
2371.1917 | 480.183 | 655.8173 | 573.3154 | 723.0896 | 631.9922 | 718.5329
2372.1917 | 478.8294 | 655.3923 | 573.0511 | 713.4864 | 633.2513 | 708.0866
2373.1917 | 477.8644 | 655.5362 | 573.4286 | 702.8635 | 633.6724 | 712.205
2374.1917 | 479.6157 | 655.9571 | 572.4496 | 693.5494 | 635.8632 | 712.0429
2375.1917 | 480.6013 | 655.9072 | 572.243 | 684.8227 | 634.976 | 704.3336
2376.1917 | 480.8121 | 655.4362 | 571.7125 | 676.3664 | 635.1145 | 710.434
2377.1917 | 480.4085 | 655.6384 | 571.4446 | 670.9393 | 634.4086 | 700.8515
2378.1917 | 480.5929 | 655.5744 | 572.5415 | 665.6422 | 634.1191 | 691.4679
2379.1917 | 480.8059 | 656.0269 | 573.8823 | 671.8783 | 632.7488 | 693.3482
2380.1917 | 480.0158 | 655.7726 | 575.4952 | 685.4626 | 630.6609 | 701.1643
2381.1917 | 480.3692 | 656.0634 | 575.0509 | 691.7709 | 627.2111 | 704.0646
2382.1917 | 480.3882 | 656.6247 | 575.5042 | 699.3965 | 626.7868 | 715.0587
2383.1917 | 480.3301 | 656.7316 | 575.8825 | 703.6642 | 625.9043 | 722.6068
2384.1917 | 481.15 | 657.5376 | 575.3801 | 708.6205 | 624.2493 | 721.8034
2385.1917 | 481.4426 | 657.5446 | 576.5482 | 716.2791 | 623.3044 | 717.0314
2386.1917 | 482.3559 | 657.5257 | 577.742 | 713.107 | 623.535 | 717.753
2387.1917 | 482.3149 | 656.6474 | 577.0712 | 710.9572 | 621.6148 | 722.0334
2388.1917 | 481.4466 | 656.619 | 576.8723 | 705.6666 | 621.8588 | 724.1515
2389.1917 | 480.4668 | 656.0239 | 577.5403 | 700.7157 | 620.942 | 727.156
2390.1917 | 480.2522 | 656.2599 | 578.4981 | 696.5446 | 619.7395 | 729.7516
2391.1917 | 480.8084 | 656.1527 | 578.2915 | 697.1292 | 617.8359 | 728.6786
2392.1917 | 481.7448 | 656.1746 | 579.1456 | 709.0143 | 616.314 | 719.5285
2393.1917 | 482.0045 | 655.9875 | 579.7702 | 702.5831 | 615.3553 | 720.7401
2394.1917 | 481.5106 | 656.4865 | 579.7962 | 697.4849 | 616.4572 | 706.2554
2395.1917 | 482.5392 | 656.6613 | 578.9173 | 692.4466 | 616.0701 | 706.5883
2396.1917 | 482.6997 | 655.5596 | 578.5987 | 687.8807 | 616.4016 | 694.4922
2397.1917 | 482.5613 | 655.9033 | 579.0623 | 683.692 | 616.6575 | 691.5873
2398.1917 | 482.9191 | 655.5051 | 579.5864 | 688.5255 | 617.4012 | 685.0333
2399.1917 | 483.4252 | 655.283 | 579.5462 | 684.6789 | 615.9981 | 682.5476
2400.1917 | 482.7527 | 655.0591 | 580.257 | 679.5086 | 614.5355 | 682.5965
2401.1917 | 481.4462 | 654.811 | 580.863 | 680.072 | 612.3498 | 685.0028
2402.1917 | 481.2342 | 654.8343 | 580.8812 | 676.3 | 610.9495 | 690.2226
2403.1917 | 481.5961 | 655.1768 | 581.9571 | 688.0136 | 610.7091 | 690.3386
2404.1917 | 481.9088 | 655.2765 | 582.4313 | 692.6664 | 611.9939 | 696.2445
2405.1917 | 482.654 | 654.9966 | 582.6543 | 685.9419 | 612.8961 | 693.1102
2406.1917 | 483.7608 | 655.1602 | 581.8107 | 690.9352 | 612.5731 | 695.3043
2407.1917 | 483.8455 | 655.4925 | 583.3747 | 700.9018 | 612.9755 | 697.6807
2408.1917 | 484.3418 | 655.881 | 583.922 | 707.372 | 613.9377 | 703.4817
2409.1917 | 484.4288 | 655.4846 | 583.8355 | 709.6538 | 611.8772 | 707.9718
2410.1917 | 484.6223 | 655.3197 | 584.8189 | 711.885 | 610.0773 | 716.0455
2411.1917 | 485.853 | 655.597 | 583.521 | 712.8388 | 610.799 | 718.102
2412.1917 | 487.2361 | 656.1168 | 585.4982 | 703.7246 | 611.6736 | 720.276
2413.1917 | 487.4464 | 655.877 | 584.8912 | 705.6785 | 611.1661 | 719.1734
2414.1917 | 486.1781 | 655.3633 | 585.7669 | 703.8665 | 611.1811 | 713.7328
2415.1917 | 484.8697 | 655.1146 | 584.965 | 704.9348 | 610.7476 | 712.051
2416.1917 | 483.8715 | 655.064 | 584.8993 | 696.7062 | 610.5259 | 714.9012
2417.1917 | 484.5804 | 655.9799 | 585.8744 | 690.8864 | 611.3838 | 707.2589
2418.1917 | 485.5267 | 655.5905 | 586.3142 | 686.2466 | 612.2912 | 707.7553
2419.1917 | 486.0641 | 655.0604 | 586.4056 | 689.6283 | 612.1832 | 694.7801
2420.1917 | 485.7137 | 654.4837 | 586.3927 | 683.1086 | 611.0982 | 695.3975
2421.1917 | 485.1628 | 655.3248 | 587.2281 | 678.6207 | 610.6824 | 703.044
2422.1917 | 485.2147 | 655.0129 | 586.7532 | 689.7616 | 610.2521 | 706.6571
2423.1917 | 486.804 | 655.4383 | 587.6285 | 683.3566 | 609.5123 | 708.2479
2424.1917 | 487.0779 | 655.527 | 587.6372 | 680.3501 | 611.0326 | 704.1529
2425.1917 | 488.2691 | 655.2349 | 587.4164 | 681.7933 | 610.1978 | 706.8272
2426.1917 | 487.6699 | 655.5644 | 587.7473 | 678.0011 | 608.7052 | 710.77
2427.1917 | 486.7283 | 655.1619 | 588.0756 | 688.3152 | 608.4764 | 714.62
2428.1917 | 489.2307 | 654.5381 | 588.9692 | 690.8625 | 608.5322 | 716.7202
2429.1917 | 488.3958 | 654.0011 | 588.5862 | 692.3925 | 607.628 | 717.7711
2430.1917 | 487.9765 | 654.234 | 588.76 | 684.9531 | 606.336 | 714.3994
2431.1917 | 487.7135 | 654.7367 | 589.5537 | 677.6129 | 605.1188 | 709.2168
2432.1917 | 487.2946 | 654.4899 | 591.6298 | 682.63 | 603.8793 | 703.0277
2433.1917 | 487.419 | 655.0941 | 591.2085 | 695.6933 | 603.0486 | 707.5846
2434.1917 | 488.4129 | 654.9297 | 590.3364 | 695.7943 | 603.0069 | 712.4418
2435.1917 | 488.9382 | 655.465 | 591.0353 | 702.4892 | 604.357 | 712.6585
2436.1917 | 489.9907 | 655.7718 | 590.4876 | 702.0548 | 604.1407 | 714.1677
2437.1917 | 490.5293 | 655.3775 | 591.1533 | 705.3482 | 603.2604 | 717.9418
2438.1917 | 490.1482 | 655.4891 | 592.0334 | 700.0458 | 602.4693 | 720.2144
2439.1917 | 490.1779 | 655.1134 | 590.8924 | 698.7053 | 601.6778 | 723.3779
2440.1917 | 489.8621 | 654.9613 | 591.7204 | 690.7916 | 601.1342 | 722.3851
2441.1917 | 490.5253 | 655.4478 | 591.0229 | 686.9094 | 602.4939 | 714.4413
2442.1917 | 489.7782 | 655.7218 | 591.0091 | 680.1175 | 605.2101 | 713.0574
2443.1917 | 489.4351 | 655.4744 | 592.6124 | 675.3908 | 605.7384 | 711.7648
2444.1917 | 488.9872 | 655.487 | 592.674 | 675.5286 | 605.1683 | 716.5001
2445.1917 | 489.8341 | 654.8838 | 593.0628 | 677.4523 | 604.1864 | 723.04
2446.1917 | 490.2039 | 654.3707 | 592.9006 | 673.7075 | 603.9049 | 717.1996
2447.1917 | 489.8329 | 654.7832 | 594.2771 | 669.5324 | 602.781 | 716.2492
2448.1917 | 490.296 | 655.1789 | 593.2977 | 665.5976 | 601.752 | 712.1398
2449.1917 | 490.9025 | 655.1506 | 594.1078 | 665.4839 | 601.9906 | 712.6069
2450.1917 | 491.7288 | 656.3876 | 594.6732 | 676.6533 | 602.1856 | 712.3154
2451.1917 | 491.566 | 656.4345 | 594.0969 | 677.3792 | 602.56 | 718.7158
2452.1917 | 492.461 | 656.4185 | 593.28 | 677.4055 | 603.091 | 723.5168
2453.1917 | 492.2599 | 656.2067 | 594.1766 | 675.5545 | 605.6024 | 717.9682
2454.1917 | 491.1585 | 655.7255 | 595.4722 | 674.3715 | 605.1642 | 718.2926
2455.1917 | 491.3231 | 655.9052 | 595.3946 | 681.8593 | 603.658 | 718.5764
2456.1917 | 491.3135 | 656.4436 | 594.1648 | 686.9117 | 604.6186 | 717.7179
2457.1917 | 492.3352 | 656.1731 | 594.8082 | 678.9458 | 606.3456 | 712.3645
2458.1917 | 492.5382 | 655.8027 | 596.1347 | 675.1818 | 605.3912 | 709.2562
2459.1917 | 492.7022 | 656.1456 | 595.6536 | 678.9416 | 606.9599 | 709.5652
2460.1917 | 491.8929 | 656.2191 | 593.6061 | 679.4094 | 607.3245 | 698.3668
2461.1917 | 492.7382 | 656.3644 | 594.0702 | 672.1963 | 609.0384 | 695.4931
2462.1917 | 493.3204 | 656.1132 | 594.1221 | 667.8789 | 608.6319 | 687.9929
2463.1917 | 493.5839 | 656.4405 | 594.0761 | 663.5654 | 608.9532 | 687.7667
2464.1917 | 493.8788 | 656.1856 | 595.8422 | 660.6462 | 608.8725 | 689.644
2465.1917 | 493.1978 | 656.1989 | 594.189 | 664.3769 | 607.7789 | 688.1221
2466.1917 | 493.6873 | 657.0178 | 595.3049 | 657.4931 | 606.7724 | 687.8629
2467.1917 | 492.4913 | 656.8038 | 594.8779 | 653.7728 | 606.8803 | 679.8125
2468.1917 | 492.6219 | 656.5374 | 594.9582 | 654.8352 | 606.6064 | 676.6365
2469.1917 | 492.8947 | 656.5369 | 595.409 | 652.8258 | 608.9144 | 678.1836
2470.1917 | 492.2818 | 656.4757 | 595.8877 | 651.8464 | 607.9563 | 678.2475
2471.1917 | 492.9909 | 656.6443 | 595.145 | 648.5666 | 607.9288 | 674.4483
2472.1917 | 494.0788 | 656.6486 | 595.3477 | 649.3717 | 607.502 | 675.9681
2473.1917 | 494.5822 | 656.9049 | 595.1664 | 650.0516 | 609.2085 | 674.4898
2474.1917 | 495.2992 | 656.8596 | 595.2365 | 647.2566 | 608.5922 | 672.9055
2475.1917 | 495.6228 | 657.1553 | 595.9015 | 644.5942 | 608.6729 | 671.3109
2476.1917 | 494.2934 | 656.9792 | 595.7469 | 643.9852 | 607.6541 | 677.0735
2477.1917 | 493.7476 | 656.7352 | 596.8769 | 646.962 | 605.1723 | 687.0891
2478.1917 | 493.7005 | 656.3543 | 597.1536 | 646.9252 | 603.4915 | 698.5744
2479.1917 | 494.0685 | 656.3578 | 597.0348 | 651.2031 | 602.3355 | 697.5857
2480.1917 | 494.8921 | 657.3586 | 596.6803 | 652.8186 | 602.5213 | 704.2108
2481.1917 | 496.0212 | 657.6227 | 595.4905 | 655.5987 | 601.9141 | 702.7954
2482.1917 | 497.2456 | 657.3209 | 596.4655 | 651.2122 | 601.631 | 707.143
2483.1917 | 496.1891 | 657.5555 | 596.934 | 652.6097 | 601.7936 | 705.6263
2484.1917 | 495.8526 | 657.417 | 595.9489 | 650.644 | 603.728 | 699.0781
2485.1917 | 495.9538 | 657.3959 | 597.0799 | 647.8461 | 604.7091 | 692.0826
2486.1917 | 496.9492 | 657.5908 | 596.713 | 647.543 | 607.1879 | 689.0701
2487.1917 | 497.204 | 657.4542 | 598.0413 | 645.3203 | 608.1892 | 692.0477
2488.1917 | 497.1335 | 657.1856 | 597.4459 | 646.7233 | 607.249 | 683.4863
2489.1917 | 497.0032 | 656.6437 | 597.648 | 642.9161 | 605.6195 | 680.0968
2490.1917 | 496.0576 | 656.5473 | 598.0038 | 640.7787 | 604.749 | 674.8758
2491.1917 | 496.3759 | 657.0659 | 599.0704 | 641.745 | 604.0543 | 674.3343
2492.1917 | 496.007 | 656.7397 | 599.0924 | 641.736 | 602.0554 | 679.7797
2493.1917 | 495.8169 | 656.1112 | 599.1186 | 643.1775 | 600.6851 | 677.732
2494.1917 | 496.1233 | 656.0722 | 598.4626 | 646.014 | 599.7829 | 675.8679
2495.1917 | 495.8764 | 656.3919 | 599.0335 | 642.7731 | 599.4397 | 675.096
2496.1917 | 496.392 | 656.2733 | 598.5571 | 640.541 | 599.2823 | 673.0769
2497.1917 | 496.5609 | 655.8389 | 597.8961 | 639.2326 | 599.0054 | 674.2181
2498.1917 | 498.0318 | 655.9471 | 599.4563 | 636.8361 | 598.9633 | 667.9773
2499.1917 | 496.8446 | 655.8503 | 599.6609 | 638.2689 | 598.0984 | 672.1817
2500.1917 | 496.9711 | 655.6489 | 599.7339 | 637.1923 | 596.5658 | 668.2801
2501.1917 | 498.1603 | 655.8175 | 599.6723 | 635.0471 | 595.7258 | 661.4407
2502.1917 | 498.5303 | 655.8989 | 600.1708 | 634.6038 | 597.1708 | 667.4136
2503.1917 | 498.252 | 655.6091 | 599.9801 | 639.0374 | 595.6574 | 677.9501
2504.1917 | 497.7138 | 655.7521 | 599.7417 | 640.1806 | 594.8197 | 686.7183
2505.1917 | 497.6255 | 655.4321 | 599.5796 | 637.1848 | 594.4345 | 683.004
2506.1917 | 498.8836 | 655.8427 | 598.7739 | 635.5223 | 596.4155 | 672.1822
2507.1917 | 500.0034 | 655.524 | 598.9128 | 633.7361 | 598.7739 | 667.2306
2508.1917 | 499.4063 | 654.7768 | 601.0609 | 634.1324 | 597.8105 | 663.4791
2509.1917 | 498.7624 | 653.9532 | 599.6696 | 636.3394 | 597.3964 | 662.7759
2510.1917 | 498.6595 | 654.6308 | 600.1436 | 635.2249 | 597.3618 | 663.0235
2511.1917 | 498.664 | 654.7175 | 600.3203 | 633.5901 | 598.1764 | 660.4579
2512.1917 | 498.8316 | 654.4447 | 599.8847 | 632.1729 | 598.7228 | 656.1541
2513.1917 | 499.9451 | 654.9088 | 600.1483 | 631.5769 | 597.6112 | 668.1249
2514.1917 | 500.1022 | 654.971 | 600.8771 | 630.1464 | 596.7652 | 670.2061
2515.1917 | 499.7724 | 654.9539 | 600.4759 | 628.3205 | 597.3197 | 666.889
2516.1917 | 499.8513 | 654.6807 | 601.4549 | 627.3413 | 597.2087 | 667.7576
2517.1917 | 499.5379 | 654.4844 | 601.5142 | 630.3412 | 595.9143 | 672.6951
2518.1917 | 499.9921 | 654.0207 | 603.1835 | 629.7993 | 593.6537 | 680.2332
2519.1917 | 500.8334 | 653.9959 | 601.0616 | 626.8922 | 593.4048 | 678.8016
2520.1917 | 501.6467 | 653.9631 | 601.0855 | 626.5851 | 594.6433 | 670.5817
2521.1917 | 501.3411 | 653.6396 | 601.9269 | 628.2984 | 595.1827 | 662.8483
2522.1917 | 500.5789 | 653.2647 | 602.6997 | 627.4848 | 595.1573 | 662.4054
2523.1917 | 500.3993 | 652.7966 | 601.4903 | 625.7378 | 592.4872 | 671.8107
2524.1917 | 500.7649 | 652.6202 | 601.6134 | 622.7384 | 590.4817 | 672.0243
2525.1917 | 501.4399 | 652.4737 | 602.1207 | 620.7292 | 589.7775 | 665.8392
2526.1917 | 501.6864 | 652.2955 | 602.1478 | 618.0092 | 588.7968 | 667.628
2527.1917 | 501.5637 | 652.0675 | 602.1897 | 618.2356 | 588.0211 | 673.0578
2528.1917 | 502.1614 | 651.6707 | 602.2339 | 616.0793 | 586.9611 | 673.631
2529.1917 | 501.4817 | 651.5741 | 603.2371 | 617.7718 | 586.4298 | 674.1526
2530.1917 | 502.4128 | 651.1787 | 602.9706 | 618.6838 | 587.2948 | 672.868
2531.1917 | 502.4692 | 651.2023 | 601.6297 | 618.7531 | 588.3834 | 667.3579
2532.1917 | 502.0273 | 651.0824 | 601.5002 | 618.2479 | 587.8494 | 664.556
2533.1917 | 501.3835 | 651.087 | 602.56 | 617.0628 | 586.8108 | 663.7237
2534.1917 | 501.4687 | 651.3217 | 603.1356 | 615.0175 | 586.8104 | 659.9015
2535.1917 | 502.3158 | 651.0428 | 601.7935 | 614.6474 | 586.867 | 662.9607
2536.1917 | 502.5058 | 650.5616 | 602.469 | 613.199 | 586.2796 | 660.9893
2537.1917 | 502.277 | 650.742 | 602.3798 | 613.5998 | 586.9148 | 659.4274
2538.1917 | 502.709 | 650.4175 | 602.9172 | 614.7694 | 587.3254 | 660.68
2539.1917 | 503.7753 | 650.1288 | 603.0612 | 614.0605 | 586.8486 | 662.3302
2540.2073 | 503.2521 | 650.0124 | 602.8277 | 612.6864 | 584.07 | 666.6624
2541.1917 | 503.6234 | 650.1953 | 602.2025 | 611.2506 | 584.3961 | 667.3978
2542.1917 | 503.0692 | 650.2114 | 601.748 | 609.7026 | 584.596 | 667.7172
2543.1917 | 503.8039 | 649.9876 | 602.0505 | 609.2256 | 585.3471 | 661.7342
2544.2073 | 503.3748 | 649.6319 | 602.5673 | 608.9318 | 585.8102 | 663.6177
2545.1917 | 503.5567 | 649.3593 | 602.9909 | 610.1009 | 586.0909 | 665.8658
2546.1917 | 503.5495 | 649.0292 | 602.905 | 615.9376 | 584.6475 | 673.5044
2547.1917 | 503.6966 | 648.4858 | 602.4768 | 614.7779 | 584.2797 | 673.1766
2548.1917 | 504.3194 | 648.1581 | 602.8123 | 614.7205 | 583.8895 | 684.3046
2549.1917 | 504.7387 | 648.416 | 603.0239 | 614.0225 | 583.6229 | 684.7944
2550.1917 | 504.4375 | 647.9926 | 602.8652 | 611.8924 | 582.7976 | 684.6644
2551.1917 | 503.9435 | 647.503 | 603.0403 | 610.4489 | 581.2625 | 677.7126
2552.1917 | 504.0647 | 647.5253 | 602.2469 | 610.966 | 581.7695 | 679.2798
2553.1917 | 506.5015 | 647.8783 | 603.4695 | 609.1694 | 582.1434 | 679.4848
2554.1917 | 505.8407 | 647.9186 | 603.0226 | 608.389 | 583.3236 | 672.8159
2555.1917 | 505.277 | 647.6359 | 602.8591 | 608.0076 | 584.1436 | 672.9194
2556.1917 | 504.7286 | 647.3635 | 603.2727 | 606.9185 | 584.0544 | 665.6361
2557.1917 | 504.7381 | 647.1819 | 603.4501 | 606.6386 | 584.478 | 663.5845
2558.1917 | 504.9111 | 647.0102 | 603.1207 | 606.1061 | 583.5201 | 666.0335
2559.1917 | 505.3309 | 646.2585 | 602.7324 | 606.5133 | 584.0173 | 666.1653
2560.1917 | 505.6076 | 646.5775 | 603.7648 | 606.3644 | 584.8823 | 660.6244
2561.1917 | 506.1206 | 646.6932 | 603.3872 | 604.3771 | 584.7694 | 663.7219
2562.1917 | 506.3909 | 646.114 | 603.8539 | 604.2236 | 583.1526 | 660.5935
2563.1917 | 506.2776 | 645.9621 | 602.9844 | 604.3466 | 583.1378 | 664.9828
2564.1917 | 506.0382 | 645.7209 | 602.7907 | 602.6356 | 583.3291 | 665.7089
2565.1917 | 506.5654 | 645.7965 | 602.5727 | 600.7352 | 585.1111 | 656.3249
2566.1917 | 506.8205 | 645.9411 | 603.3219 | 599.92 | 586.6321 | 650.7187
2567.1917 | 506.7677 | 646.1593 | 603.0898 | 598.0494 | 586.6766 | 645.1589
2568.1917 | 507.2902 | 646.2418 | 603.184 | 596.8853 | 585.8753 | 652.9887
2569.1917 | 507.4553 | 646.7229 | 603.8098 | 595.9834 | 585.8457 | 656.0092
2570.1917 | 507.2495 | 646.4519 | 603.5146 | 594.1253 | 584.0658 | 658.0103
2571.1917 | 507.5771 | 646.2394 | 603.2128 | 592.1643 | 583.2124 | 660.9192
2572.1917 | 508.5594 | 646.5409 | 604.0327 | 590.2994 | 583.9271 | 652.0165
2573.1917 | 508.7668 | 646.4376 | 603.9382 | 589.3583 | 584.4603 | 656.5794
2574.1917 | 508.9541 | 645.9999 | 603.8709 | 588.1718 | 582.9355 | 663.8707
2575.1917 | 509.4316 | 645.7795 | 603.4484 | 586.9232 | 582.277 | 669.1959
2576.1917 | 508.7123 | 646.0761 | 603.1587 | 585.9674 | 582.9025 | 662.5634
2577.1917 | 509.1339 | 646.0229 | 602.7152 | 585.3669 | 582.9615 | 653.1396
2578.1917 | 510.6512 | 645.7832 | 603.5476 | 584.5547 | 582.467 | 646.7719
2579.1917 | 510.0077 | 645.177 | 603.2844 | 583.8747 | 582.1377 | 639.1041
2580.1917 | 510.2224 | 645.0592 | 602.8368 | 584.6755 | 583.5432 | 632.1192
2581.1917 | 509.8992 | 644.6859 | 602.0097 | 585.1783 | 584.8946 | 624.9113
2582.1917 | 509.9573 | 645.2161 | 602.7556 | 585.3906 | 587.0476 | 620.9913
2583.1917 | 509.5878 | 645.493 | 603.0902 | 586.9038 | 588.8959 | 617.5286
2584.1917 | 509.4652 | 644.831 | 604.3055 | 586.5515 | 588.696 | 623.8939
2585.1917 | 509.0551 | 644.5261 | 604.4062 | 587.0852 | 589.6801 | 620.5576
2586.1917 | 508.8397 | 644.2447 | 603.7828 | 586.7087 | 588.8037 | 620.9562
2587.1917 | 508.8957 | 644.1787 | 603.3689 | 585.6233 | 587.0616 | 621.6567
2588.1917 | 508.8632 | 643.8395 | 602.9729 | 584.6254 | 587.1253 | 622.1704
2589.1917 | 508.72 | 643.9208 | 603.2755 | 584.5382 | 587.7311 | 621.3525
2590.1917 | 508.9074 | 644.3576 | 603.8702 | 583.8133 | 588.7927 | 618.7647
2591.1917 | 509.0792 | 644.1878 | 603.91 | 583.4913 | 589.7766 | 623.2119
2592.1917 | 510.5929 | 643.6143 | 603.995 | 581.9447 | 588.3561 | 622.6105
2593.1917 | 510.0063 | 643.3083 | 603.758 | 581.1414 | 587.7373 | 622.7667
2594.1917 | 510.3718 | 642.518 | 603.248 | 580.0974 | 585.1231 | 623.0219
2595.1917 | 510.2824 | 642.3385 | 602.4762 | 578.8764 | 583.3836 | 629.0304
2596.1917 | 510.4033 | 642.9498 | 602.606 | 579.1039 | 583.4966 | 624.461
2597.1917 | 510.4676 | 643.1704 | 603.93 | 578.2358 | 582.3635 | 620.8845
2598.1917 | 509.8286 | 642.5756 | 603.9437 | 577.153 | 580.6017 | 616.6749
2599.1917 | 509.3325 | 641.9609 | 603.7264 | 576.1961 | 578.6907 | 616.941
2600.1917 | 509.6084 | 641.6013 | 603.4453 | 575.8386 | 577.1085 | 624.6903
2601.1917 | 509.6797 | 641.9439 | 603.5966 | 575.2688 | 574.8596 | 634.8558
2602.1917 | 510.3886 | 642.0617 | 604.2131 | 574.7791 | 572.8733 | 644.1819
2603.1917 | 510.8046 | 641.3043 | 603.773 | 573.3557 | 570.8733 | 638.4391
2604.1917 | 510.6852 | 641.213 | 603.4663 | 572.5036 | 571.7009 | 638.8636
2605.1917 | 511.7614 | 641.2547 | 604.3881 | 572.1442 | 571.2087 | 639.4717
2606.1917 | 511.5347 | 641.0083 | 603.3627 | 572.1994 | 571.4235 | 651.1581
2607.1917 | 511.4008 | 641.2298 | 603.0622 | 571.8857 | 571.9597 | 648.3894
2608.1917 | 511.1795 | 641.4655 | 603.0205 | 572.8317 | 573.1409 | 642.1506
2609.1917 | 510.4052 | 641.387 | 603.331 | 572.5111 | 573.9483 | 641.9065
2610.1917 | 509.8142 | 641.1592 | 602.8935 | 571.7682 | 575.0087 | 636.9566
2611.1917 | 510.1387 | 641.0036 | 603.0468 | 571.5843 | 575.5699 | 640.9936
2612.1917 | 510.7074 | 640.8156 | 603.2417 | 571.8123 | 576.2124 | 643.0061
2613.1917 | 511.1004 | 640.5226 | 603.2011 | 571.2683 | 575.1947 | 639.4963
2614.1917 | 511.3606 | 639.9076 | 604.1028 | 572.3948 | 574.5564 | 639.638
2615.1917 | 511.8359 | 640.2376 | 604.7288 | 573.072 | 573.6138 | 637.235
2616.1917 | 511.7286 | 639.8676 | 604.4622 | 573.1352 | 572.8205 | 641.1517
2617.1917 | 510.9037 | 639.2768 | 603.9599 | 571.422 | 570.3465 | 638.1963
2618.1917 | 511.0743 | 639.4935 | 603.7518 | 571.7168 | 569.381 | 637.5732
2619.1917 | 511.0722 | 639.6804 | 604.1059 | 571.6658 | 569.0595 | 642.5923
2620.1917 | 511.2486 | 639.7063 | 603.5801 | 570.9891 | 567.568 | 640.2046
2621.1917 | 512.0966 | 639.3259 | 604.5699 | 570.1786 | 567.1594 | 641.1724
2622.1917 | 511.7879 | 639.729 | 603.4396 | 569.7705 | 568.039 | 638.8607
2623.1917 | 512.5024 | 640.5341 | 602.9711 | 569.3526 | 568.9466 | 634.9852
2624.1917 | 513.956 | 640.3585 | 604.1953 | 569.3767 | 571.2893 | 628.4252
2625.1917 | 513.4501 | 639.1125 | 604.8243 | 568.6124 | 570.7815 | 629.1188
2626.1917 | 513.1048 | 638.854 | 604.7786 | 569.0899 | 570.7343 | 624.1741
2627.1917 | 513.1956 | 638.8992 | 604.1145 | 568.9006 | 571.6433 | 619.3632
2628.1917 | 513.0486 | 638.6774 | 603.3478 | 569.6459 | 572.5509 | 617.976
2629.1917 | 513.5193 | 638.9398 | 603.1515 | 570.6311 | 573.6295 | 621.7873
2630.1917 | 514.0045 | 639.0119 | 603.7865 | 570.1341 | 574.0218 | 619.0197
2631.1917 | 514.63 | 638.2447 | 603.627 | 570.0715 | 572.7999 | 615.8069
2632.1917 | 514.0002 | 638.2669 | 603.8168 | 569.7511 | 571.6274 | 614.4244
2633.1917 | 513.664 | 638.4912 | 604.7357 | 568.806 | 571.4928 | 615.4261
2634.1917 | 513.3863 | 638.8036 | 603.6854 | 569.5975 | 572.8821 | 613.9289
2635.1917 | 513.3596 | 638.7654 | 603.9079 | 569.3492 | 574.1621 | 614.947
2636.1917 | 513.8696 | 638.6089 | 604.7145 | 569.8154 | 574.7969 | 609.5397
2637.1917 | 513.7543 | 638.3502 | 605.9945 | 569.406 | 575.2778 | 610.3454
2638.1917 | 513.9632 | 637.8923 | 605.0925 | 569.5322 | 574.0822 | 607.7299
2639.1917 | 514.0596 | 637.5974 | 605.137 | 568.9261 | 572.8766 | 610.6305
2640.1917 | 514.3342 | 637.2096 | 604.9142 | 568.7107 | 570.6668 | 611.3815