## Test Conditions
DESIREE-FIRE Intermediate Scale Test 5 - Circuit Simulator Data Only
Test Date: | 2010-03-01
DCSim DAQ Start Time | 13:30
DCSim Time for Synchronization | 13:42
Heat Source Synchronization | 0:01 | hour:minutes:seconds
Heat Source DAQ Start Time | 13:41
Fire Time | 14:02
Offset | 0:32 | hour:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 1920 | seconds
Heat Source Offset | 0:21 | hour:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 1288 | seconds
Heat Source Stop Time | 14:46
Test Duration | 0:44 | hour:minutes:seconds
| 2640 | seconds
CT500 turns | 2 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 turns | 5 | 1 or 5
Pre-Test Baseline: | Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
SOV 1 | PE/PVC, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 2, 3, and 4 represents the conduit temperature 3', 5', and 7' down the conduit located in B Position. These are labeled as "B Position - Conduit - 3'", "B Position - Conduit - Middle", " B Position - Conduit - 7'", respectively.
SOV 2 | PE/PVC, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 8, 9, and 10 represents the air temperature 3', 5', and 7' down the tray located in D Position. These are labeled as "D Position - 3'", "D Position - Middle", " D Position - 7'", respectively.
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | SOV-1_CT500 | SOV-1_CT35_1_P | SOV-1_CT35_2_S1 | SOV-1_CT35_3_G | SOV-1_CT35_4_S2 | SOV-1_CT35_5_N | SOV-2_CT500 | SOV-2_CT35_1_P | SOV-2_CT35_2_S1 | SOV-2_CT35_3_G | SOV-2_CT35_4_S2 | SOV-2_CT35_5_N | SOV-1_VT7_1_R | SOV-1_VT7_2_SP | SOV-1_VT7_3_S | SOV-1_VTU_1_P | SOV-1_VTU_2_S1 | SOV-1_VTU_3_G | SOV-1_VTU_4_N | SOV-2_VT7_1_R | SOV-2_VT7_2_SP | SOV-2_VT7_3_S | SOV-2_VTU_1_P | SOV-2_VTU_2_S1 | SOV-2_VTU_3_G | SOV-2_VTU_4_N | {SOV1} V(N) - V(Batt -) | {SOV1} V(P) - V(Batt +) | {SOV1} V(R) - V(Batt -) | {SOV1} V(S) - V(Batt -) | {SOV1} V(S) - V(N) | {SOV1} V(S1) - V(Batt +) | {SOV1} V(G) - V(Batt +) | {SOV2} V(N) - V(Batt -) | {SOV2} V(P) - V(Batt +) | {SOV2} V(R) - V(Batt -) | {SOV2} V(S) - V(Batt -) | {SOV2} V(S) - V(N) | {SOV2} V(S1) - V(Batt +) | {SOV2} V(G) - V(Batt +) | {SOV1} V(P) - V(Batt -) | {SOV1} V(S1) - V(Batt -) | {SOV1} V(G) - V(Batt -) | {SOV1} V(SP) - V(Batt -) | {SOV1} V(N) - V(Batt +) | {SOV2} V(P) - V(Batt -) | {SOV2} V(S1) - V(Batt -) | {SOV1} V(G) - V(Batt -) | {SOV2} V(SP) - V(Batt -) | {SOV2} V(N) - V(Batt +)
-1.6094 | 124.0173 | -62.0407 | 61.8759 | 1.4211e-13 | -0.0015983 | 0.0018804 | 0.065682 | -0.0049655 | 0.062276 | -0.006028 | -0.0022453 | -0.0012777 | 0.070433 | 0.013049 | 0.064694 | -61.9171 | -0.016908 | -62.0578 | 61.8008 | 61.5777 | 61.7013 | -62.0571 | -61.9809 | 0.004938 | -62.0429 | 61.6515 | 61.7791 | 61.1687 | -62.2117 | -0.016407 | -0.075071 | 0.12364 | -0.017136 | -0.000729 | -0.29818 | -0.17464 | -0.17099 | -0.22438 | 0.059762 | -0.002215 | 0.16878 | -0.096862 | -0.70719 | 123.8416 | 123.6184 | 123.742 | 62.0238 | -123.933 | 123.6922 | 123.8198 | 123.2094 | 62.0456 | -124.0876
0.0625 | 123.9944 | -62.0316 | 61.908 | 1.4211e-13 | -0.0022393 | 0.0018804 | 0.065682 | -0.0047519 | 0.062276 | -0.013659 | -0.0022453 | -0.0014913 | 0.070006 | 0.013476 | 0.06448 | -61.9216 | -0.016908 | -62.0578 | 61.8008 | 61.5823 | 61.7059 | -62.0434 | -61.9809 | -0.00422 | -62.0475 | 61.647 | 61.7745 | 61.1687 | -62.2071 | -0.011825 | -0.10711 | 0.10991 | -0.026291 | -0.014466 | -0.32564 | -0.2021 | -0.17557 | -0.261 | 0.050607 | -0.015949 | 0.15962 | -0.13348 | -0.73924 | 123.8324 | 123.6139 | 123.7374 | 62.0146 | -123.9513 | 123.6785 | 123.806 | 123.2003 | 62.0273 | -124.1151
1.8125 | 124.1272 | -62.0544 | 61.8256 | 1.4211e-13 | -0.0013847 | 0.0016666 | 0.065682 | -0.0049655 | 0.06249 | 0.0016025 | -0.0022453 | -0.0010641 | 0.07022 | 0.013263 | 0.06448 | -61.9125 | -0.007751 | -62.0624 | 61.8054 | 61.5823 | 61.7059 | -62.0525 | -61.9764 | 0.004938 | -62.0429 | 61.647 | 61.7699 | 61.1641 | -62.2117 | 0.001905 | -0.020139 | 0.14195 | -0.007981 | -0.009886 | -0.24325 | -0.11971 | -0.15726 | -0.17861 | 0.078074 | 0.011518 | 0.16878 | -0.055665 | -0.66142 | 123.8599 | 123.6368 | 123.7603 | 62.0467 | -123.8781 | 123.7014 | 123.8243 | 123.2186 | 62.0594 | -124.0373
3.4844 | 123.9853 | -62.0773 | 61.8988 | 1.4211e-13 | -0.0020257 | 0.0018804 | 0.065682 | -0.0047519 | 0.062704 | -0.006028 | -0.0022453 | -0.0010641 | 0.070006 | 0.013476 | 0.064694 | -61.9125 | -0.021486 | -62.067 | 61.7963 | 61.5777 | 61.6921 | -62.0342 | -61.9855 | 0.004938 | -62.0383 | 61.6424 | 61.7745 | 61.1641 | -62.2071 | 0.04311 | -0.10254 | 0.16484 | 0.01033 | -0.03278 | -0.32107 | -0.20668 | -0.12979 | -0.25643 | 0.091806 | 0.038986 | 0.16878 | -0.12433 | -0.73466 | 123.8736 | 123.6551 | 123.7695 | 62.0558 | -123.933 | 123.7197 | 123.8518 | 123.2415 | 62.0823 | -124.1059
5.2344 | 124.0723 | -62.0499 | 61.8073 | 1.4211e-13 | -0.0020257 | 0.0016666 | 0.065896 | -0.0047519 | 0.062063 | 0.0016025 | -0.0022453 | -0.0010641 | 0.069792 | 0.013049 | 0.064267 | -61.9125 | -0.012329 | -62.067 | 61.8054 | 61.5777 | 61.7013 | -62.0525 | -61.9809 | 0.004938 | -62.0338 | 61.6424 | 61.7699 | 61.2511 | -62.2071 | -0.002672 | -0.001828 | 0.13737 | -0.017136 | -0.014464 | -0.22951 | -0.10597 | -0.15726 | -0.16488 | 0.068918 | 0.016098 | 0.17335 | -0.037354 | -0.55611 | 123.8553 | 123.6276 | 123.7511 | 62.0375 | -123.8598 | 123.6922 | 123.8198 | 123.301 | 62.0548 | -124.0144
6.9688 | 124.0082 | -62.027 | 61.9034 | 1.4211e-13 | -0.0013847 | 0.002094 | 0.065896 | -0.0051793 | 0.062704 | -0.006028 | -0.0024589 | -0.0010641 | 0.07022 | 0.012835 | 0.06448 | -61.9125 | -0.016908 | -62.0624 | 61.7963 | 61.5732 | 61.7013 | -62.0434 | -61.9855 | -0.00422 | -62.0429 | 61.6286 | 61.7745 | 61.1641 | -62.2071 | -0.016402 | -0.10712 | 0.11449 | -0.035446 | -0.019044 | -0.33022 | -0.2021 | -0.18014 | -0.27474 | 0.041452 | -0.015947 | 0.1642 | -0.12891 | -0.73924 | 123.8232 | 123.6001 | 123.7283 | 62.0101 | -123.9468 | 123.6556 | 123.8015 | 123.1911 | 62.0228 | -124.1105
8.6406 | 124.1135 | -62.059 | 61.7706 | 1.4211e-13 | -0.0018119 | 0.0018804 | 0.065682 | -0.0047519 | 0.062063 | -0.006028 | -0.0022453 | -0.0010641 | 0.07022 | 0.013263 | 0.064267 | -61.9033 | -0.016908 | -62.0533 | 61.7963 | 61.5777 | 61.7013 | -62.0434 | -61.9764 | 0.004938 | -62.0429 | 61.6424 | 61.7745 | 61.1687 | -62.2117 | 0.015641 | 0.025636 | 0.15569 | 0.005754 | -0.009887 | -0.19289 | -0.069353 | -0.15268 | -0.12825 | 0.082652 | 0.016096 | 0.16878 | 0.003846 | -0.60191 | 123.8553 | 123.6368 | 123.7603 | 62.0421 | -123.814 | 123.7014 | 123.8335 | 123.2277 | 62.064 | -123.9823
10.3906 | 123.9807 | -62.059 | 61.8668 | 1.4211e-13 | -0.0018119 | 0.0016666 | 0.065468 | -0.0049655 | 0.062276 | -0.006028 | -0.0022453 | -0.0010641 | 0.069792 | 0.013263 | 0.06448 | -61.9079 | -0.016908 | -62.0533 | 61.7917 | 61.5777 | 61.7013 | -62.048 | -61.9809 | -0.008798 | -62.0338 | 61.6332 | 61.7699 | 61.155 | -62.2071 | 0.011062 | -0.075072 | 0.15111 | 0.005754 | -0.005308 | -0.28902 | -0.16548 | -0.1481 | -0.23354 | 0.078073 | 0.025253 | 0.17335 | -0.096863 | -0.71177 | 123.8507 | 123.6368 | 123.7603 | 62.0421 | -123.9147 | 123.6922 | 123.8289 | 123.214 | 62.0502 | -124.0739
12.1406 | 123.9578 | -62.0224 | 61.8805 | 1.4211e-13 | -0.0018119 | 0.0016666 | 0.065682 | -0.0047519 | 0.06249 | -0.006028 | -0.0022453 | -0.0012777 | 0.070006 | 0.01369 | 0.064267 | -61.9079 | -0.012329 | -62.0624 | 61.7917 | 61.5823 | 61.6967 | -62.0342 | -61.9718 | 0.000359 | -62.0383 | 61.6332 | 61.7699 | 61.1504 | -62.2071 | -0.011822 | -0.088805 | 0.11449 | -0.040024 | -0.028202 | -0.29818 | -0.1838 | -0.18472 | -0.24727 | 0.05061 | -0.015946 | 0.16878 | -0.1106 | -0.73008 | 123.8141 | 123.6047 | 123.7191 | 62.0101 | -123.9147 | 123.6556 | 123.7923 | 123.1728 | 62.0228 | -124.0876
13.875 | 123.967 | -62.0361 | 61.8851 | 1.4211e-13 | -0.0018119 | 0.0018804 | 0.065896 | -0.0051793 | 0.062276 | -0.013659 | -0.0022453 | -0.0012777 | 0.070006 | 0.013476 | 0.06448 | -61.9033 | -0.012329 | -62.0533 | 61.7963 | 61.5686 | 61.6921 | -62.0388 | -61.9718 | -0.00422 | -62.0383 | 61.6378 | 61.7562 | 61.155 | -62.2071 | -0.002668 | -0.088805 | 0.1328 | -0.017134 | -0.014466 | -0.31649 | -0.19295 | -0.17099 | -0.24727 | 0.064343 | -0.002213 | 0.16878 | -0.12891 | -0.73008 | 123.8324 | 123.6047 | 123.7283 | 62.0238 | -123.9239 | 123.6739 | 123.7923 | 123.1911 | 62.0319 | -124.0922
15.5469 | 123.9899 | -62.0132 | 61.8988 | 1.4211e-13 | -0.0018119 | 0.0016666 | 0.065468 | -0.0049655 | 0.062276 | 0.0092325 | -0.0022453 | -0.0012777 | 0.07022 | 0.013476 | 0.064267 | -61.9033 | -0.016908 | -62.0578 | 61.7963 | 61.5732 | 61.6921 | -62.0388 | -61.9718 | -0.008798 | -62.0383 | 61.6332 | 61.7745 | 61.155 | -62.198 | -0.025556 | -0.10254 | 0.10991 | -0.044601 | -0.019045 | -0.32565 | -0.20668 | -0.18472 | -0.26559 | 0.041455 | -0.025101 | 0.15962 | -0.12433 | -0.74382 | 123.8095 | 123.5864 | 123.7054 | 61.9963 | -123.9376 | 123.6465 | 123.7877 | 123.1682 | 62.0044 | -124.0968
17.2969 | 123.9853 | -62.0316 | 61.9034 | 1.4211e-13 | -0.0020257 | 0.0018804 | 0.065896 | -0.0047519 | 0.062063 | -0.013659 | -0.0024589 | -0.0012777 | 0.070006 | 0.013476 | 0.064267 | -61.9033 | -0.016908 | -62.0487 | 61.7871 | 61.5777 | 61.6875 | -62.0525 | -61.9672 | -0.00422 | -62.0292 | 61.6286 | 61.7653 | 61.1504 | -62.2025 | -0.020983 | -0.11627 | 0.12822 | -0.017134 | 0.003849 | -0.32565 | -0.21584 | -0.17099 | -0.27474 | 0.064343 | 0.002366 | 0.17335 | -0.13806 | -0.75297 | 123.8187 | 123.6093 | 123.7191 | 62.0146 | -123.9559 | 123.6602 | 123.7969 | 123.182 | 62.0273 | -124.1059
18.9688 | 124.0997 | -62.0132 | 61.7981 | 1.4211e-13 | -0.0022393 | 0.0016666 | 0.065682 | -0.0051793 | 0.06249 | 0.0016025 | -0.0024589 | -0.00085026 | 0.070006 | 0.013476 | 0.06448 | -61.8988 | -0.016908 | -62.0487 | 61.7963 | 61.5777 | 61.6875 | -62.0525 | -61.9764 | -0.00422 | -62.0292 | 61.6332 | 61.7607 | 61.1458 | -62.198 | -0.039293 | -0.00183 | 0.11449 | -0.035444 | 0.003849 | -0.22036 | -0.11055 | -0.18472 | -0.16488 | 0.036876 | -0.015944 | 0.16877 | -0.037356 | -0.65227 | 123.8095 | 123.591 | 123.7008 | 61.9963 | -123.8506 | 123.6465 | 123.774 | 123.1591 | 62.009 | -123.9961
20.7188 | 123.9853 | -62.0132 | 61.8805 | 1.4211e-13 | -0.0018119 | 0.002094 | 0.065682 | -0.0049655 | 0.062276 | -0.006028 | -0.0024589 | -0.0010641 | 0.069579 | 0.01369 | 0.064267 | -61.9033 | -0.016908 | -62.0441 | 61.7917 | 61.5777 | 61.6967 | -62.0342 | -61.9672 | 0.004938 | -62.0292 | 61.6332 | 61.7653 | 61.1458 | -62.2025 | -0.020977 | -0.088805 | 0.10991 | -0.030866 | -0.009889 | -0.30276 | -0.1838 | -0.1893 | -0.24727 | 0.046033 | -0.015944 | 0.17335 | -0.11517 | -0.73466 | 123.8049 | 123.591 | 123.7099 | 61.9963 | -123.9147 | 123.6465 | 123.7786 | 123.1591 | 62.0182 | -124.083
22.4531 | 123.9761 | -62.0178 | 61.853 | 1.4211e-13 | -0.0024529 | 0.0018804 | 0.065682 | -0.0045383 | 0.062276 | -0.013659 | -0.0022453 | -0.0012777 | 0.069792 | 0.013476 | 0.06448 | -61.8988 | -0.021486 | -62.0487 | 61.7871 | 61.5686 | 61.6875 | -62.0342 | -61.9626 | 0.000359 | -62.0246 | 61.6332 | 61.7562 | 61.1504 | -62.1934 | -0.0164 | -0.065917 | 0.11907 | -0.030867 | -0.014467 | -0.28445 | -0.16549 | -0.17556 | -0.21981 | 0.055189 | -0.006788 | 0.16877 | -0.096866 | -0.70262 | 123.8049 | 123.5864 | 123.7054 | 61.9963 | -123.8872 | 123.651 | 123.774 | 123.1682 | 62.0182 | -124.0464
24.1875 | 123.9578 | -62.0361 | 61.8668 | 1.4211e-13 | -0.0020257 | 0.0018804 | 0.065468 | -0.0049655 | 0.062063 | -0.013659 | -0.0022453 | -0.0012777 | 0.069792 | 0.01369 | 0.06448 | -61.8942 | -0.007751 | -62.0487 | 61.7917 | 61.5777 | 61.6875 | -62.0434 | -61.9672 | 0.000359 | -62.0292 | 61.6286 | 61.7562 | 61.155 | -62.1934 | -0.007247 | -0.075072 | 0.14196 | -0.012556 | -0.005309 | -0.28902 | -0.17922 | -0.15725 | -0.23812 | 0.068921 | 0.006944 | 0.1642 | -0.1106 | -0.71177 | 123.8278 | 123.6139 | 123.7237 | 62.0284 | -123.9101 | 123.6648 | 123.7923 | 123.1911 | 62.0365 | -124.0601
25.9219 | 124.0265 | -62.0407 | 61.8164 | 1.4211e-13 | -0.0018119 | 0.002094 | 0.065682 | -0.0051793 | 0.06249 | -0.021289 | -0.0024589 | -0.0012777 | 0.070006 | 0.013263 | 0.064267 | -61.8988 | -0.003172 | -62.0487 | 61.7871 | 61.5686 | 61.6875 | -62.0342 | -61.9626 | -0.008798 | -62.0155 | 61.6241 | 61.7607 | 61.155 | -62.2025 | 0.006488 | -0.029296 | 0.14195 | -0.007979 | -0.014467 | -0.24783 | -0.12886 | -0.16183 | -0.19234 | 0.078077 | 0.025257 | 0.18709 | -0.055666 | -0.66142 | 123.8278 | 123.6093 | 123.7283 | 62.0375 | -123.8506 | 123.6648 | 123.8014 | 123.1957 | 62.0319 | -124.0189
27.5938 | 123.9899 | -62.0087 | 61.8988 | 1.4211e-13 | -0.0018119 | 0.0016666 | 0.066109 | -0.0049655 | 0.06249 | 0.0016025 | -0.0024589 | -0.0014913 | 0.070006 | 0.013476 | 0.064267 | -61.8896 | -0.012329 | -62.0487 | 61.778 | 61.5686 | 61.683 | -62.0251 | -61.9581 | -0.00422 | -62.0292 | 61.6241 | 61.7607 | 61.1458 | -62.198 | -0.016397 | -0.12085 | 0.11907 | -0.040022 | -0.023625 | -0.33023 | -0.21584 | -0.1893 | -0.27474 | 0.050613 | -0.020522 | 0.16877 | -0.13806 | -0.75297 | 123.7866 | 123.5772 | 123.6916 | 61.9963 | -123.9239 | 123.6327 | 123.7694 | 123.1545 | 62.0044 | -124.0968
29.3438 | 124.0402 | -62.0361 | 61.7889 | 1.4211e-13 | -0.0020257 | 0.0018804 | 0.065682 | -0.0049655 | 0.062276 | 0.0016025 | -0.0022453 | -0.0012777 | 0.070006 | 0.013476 | 0.06448 | -61.8942 | -0.012329 | -62.0395 | 61.7825 | 61.5686 | 61.6875 | -62.0296 | -61.9581 | -0.00422 | -62.0246 | 61.6286 | 61.7653 | 61.1504 | -62.198 | 0.00649 | -0.006409 | 0.14196 | -0.003399 | -0.009889 | -0.22036 | -0.1014 | -0.16183 | -0.1603 | 0.078079 | 0.011523 | 0.17335 | -0.023621 | -0.63853 | 123.8187 | 123.6047 | 123.7237 | 62.0238 | -123.8186 | 123.6648 | 123.8015 | 123.1865 | 62.0319 | -123.9869
31.0781 | 124.0219 | -62.0544 | 61.7844 | 1.4211e-13 | -0.0018119 | 0.0016666 | 0.066109 | -0.0051793 | 0.062276 | -0.013659 | -0.0022453 | -0.0012777 | 0.069579 | 0.01369 | 0.064267 | -61.8896 | -0.016908 | -62.0441 | 61.7963 | 61.564 | 61.6875 | -62.0296 | -61.9581 | 0.000359 | -62.0155 | 61.6241 | 61.7607 | 61.1413 | -62.1934 | 0.0248 | 0.011903 | 0.16484 | 0.010332 | -0.014468 | -0.22036 | -0.096822 | -0.13894 | -0.1603 | 0.096389 | 0.03899 | 0.17793 | -0.023623 | -0.64311 | 123.8507 | 123.6184 | 123.742 | 62.0375 | -123.814 | 123.6785 | 123.8152 | 123.1957 | 62.0548 | -123.9777
32.8281 | 124.0723 | -62.0041 | 61.7615 | 1.4211e-13 | -0.0020257 | 0.0016666 | 0.066109 | -0.0049655 | 0.062276 | 0.0016025 | -0.0022453 | -0.0012777 | 0.07022 | 0.013904 | 0.064267 | -61.8896 | -0.016908 | -62.0395 | 61.7871 | 61.5686 | 61.6875 | -62.0296 | -61.9581 | -0.00422 | -62.0109 | 61.6241 | 61.7562 | 61.1458 | -62.1934 | -0.025554 | 0.025635 | 0.11449 | -0.035443 | -0.009889 | -0.1929 | -0.073934 | -0.1893 | -0.13741 | 0.046035 | -0.006785 | 0.18251 | -0.005314 | -0.61565 | 123.7912 | 123.5727 | 123.6916 | 61.9872 | -123.7911 | 123.6282 | 123.7602 | 123.1499 | 61.9999 | -123.9549
34.5156 | 123.9258 | -62.0087 | 61.8439 | 1.4211e-13 | -0.0022393 | 0.0018804 | 0.065682 | -0.0051793 | 0.06249 | -0.006028 | -0.0022453 | -0.0010641 | 0.070006 | 0.01369 | 0.064267 | -61.8896 | -0.021486 | -62.035 | 61.7825 | 61.5686 | 61.6875 | -62.0251 | -61.9535 | -0.008798 | -62.02 | 61.6241 | 61.7562 | 61.1458 | -62.1934 | -0.016397 | -0.061341 | 0.11907 | -0.026287 | -0.00989 | -0.27529 | -0.15633 | -0.18472 | -0.21981 | 0.055192 | -0.011365 | 0.17335 | -0.087711 | -0.69804 | 123.7912 | 123.5772 | 123.6962 | 61.9872 | -123.8689 | 123.6327 | 123.7648 | 123.1545 | 61.9999 | -124.0373
36.2656 | 124.0036 | -62.0041 | 61.7844 | 1.4211e-13 | -0.0022393 | 0.002094 | 0.065682 | -0.0049655 | 0.06249 | -0.013659 | -0.0026725 | -0.0014913 | 0.070006 | 0.01369 | 0.06448 | -61.8988 | -0.012329 | -62.0395 | 61.7734 | 61.564 | 61.6875 | -62.0342 | -61.9581 | -0.00422 | -62.0155 | 61.6149 | 61.747 | 61.1504 | -62.1934 | -0.030133 | -0.010989 | 0.10533 | -0.035443 | -0.00531 | -0.22036 | -0.096822 | -0.1893 | -0.16946 | 0.046035 | -0.011364 | 0.17793 | -0.037359 | -0.63395 | 123.7775 | 123.5681 | 123.6916 | 61.9918 | -123.8186 | 123.619 | 123.7511 | 123.1545 | 61.9999 | -123.9777
38 | 123.9807 | -61.9858 | 61.8851 | 1.4211e-13 | -0.0018119 | 0.002094 | 0.065896 | -0.0051793 | 0.062704 | -0.013659 | -0.0024589 | -0.0012777 | 0.070006 | 0.013904 | 0.064267 | -61.885 | -0.021486 | -62.035 | 61.7734 | 61.5548 | 61.6784 | -62.0296 | -61.9581 | 0.000359 | -62.02 | 61.6149 | 61.7562 | 61.1458 | -62.1888 | -0.043864 | -0.1117 | 0.10076 | -0.049175 | -0.005311 | -0.33023 | -0.20669 | -0.20303 | -0.27017 | 0.027725 | -0.034253 | 0.16877 | -0.12891 | -0.73924 | 123.7592 | 123.5406 | 123.6642 | 61.9643 | -123.9147 | 123.6007 | 123.7419 | 123.1316 | 61.9861 | -124.0739
39.6719 | 123.9532 | -62.0087 | 61.8851 | 1.4211e-13 | -0.0018119 | 0.0016666 | 0.065896 | -0.0049655 | 0.062704 | -0.006028 | -0.0020317 | -0.0012777 | 0.070006 | 0.014117 | 0.064053 | -61.885 | -0.012329 | -62.035 | 61.778 | 61.5548 | 61.6875 | -62.0159 | -61.9581 | -0.008798 | -62.02 | 61.6103 | 61.7516 | 61.1367 | -62.1842 | -0.007239 | -0.10712 | 0.12365 | -0.026287 | -0.019048 | -0.33023 | -0.19753 | -0.17556 | -0.27475 | 0.050613 | -0.011365 | 0.1642 | -0.13349 | -0.7484 | 123.7866 | 123.5635 | 123.6962 | 61.9963 | -123.901 | 123.619 | 123.7602 | 123.1453 | 61.9999 | -124.0693
41.4062 | 123.967 | -62.0453 | 61.8393 | 1.4211e-13 | -0.0024529 | 0.001453 | 0.065682 | -0.0049655 | 0.06249 | -0.006028 | -0.0024589 | -0.0012777 | 0.070006 | 0.013476 | 0.06448 | -61.885 | -0.012329 | -62.0395 | 61.7825 | 61.5686 | 61.6875 | -62.0205 | -61.9489 | -0.008798 | -62.0109 | 61.6149 | 61.747 | 61.1413 | -62.1888 | 0.024803 | -0.056763 | 0.16027 | 0.005756 | -0.019047 | -0.27072 | -0.15175 | -0.14352 | -0.22439 | 0.096391 | 0.034414 | 0.17793 | -0.09229 | -0.69804 | 123.8278 | 123.6139 | 123.7328 | 62.033 | -123.8598 | 123.6602 | 123.7923 | 123.1865 | 62.0365 | -124.0281
43.1406 | 123.912 | -62.0087 | 61.853 | 1.4211e-13 | -0.0022393 | 0.002094 | 0.065896 | -0.0051793 | 0.06249 | -0.006028 | -0.0022453 | -0.0014913 | 0.069792 | 0.013904 | 0.06448 | -61.885 | -0.016908 | -62.0395 | 61.778 | 61.5548 | 61.6784 | -62.0296 | -61.9535 | 0.000359 | -62.0109 | 61.6195 | 61.747 | 61.1367 | -62.1888 | -0.020976 | -0.075074 | 0.12365 | -0.030865 | -0.009889 | -0.29818 | -0.17464 | -0.18014 | -0.23354 | 0.055192 | -0.002207 | 0.17793 | -0.10602 | -0.71635 | 123.7866 | 123.5635 | 123.6871 | 61.9918 | -123.8827 | 123.6282 | 123.7557 | 123.1453 | 62.009 | -124.0418
44.9062 | 123.9487 | -62.0224 | 61.8713 | 1.4211e-13 | -0.0018119 | 0.002094 | 0.065896 | -0.0049655 | 0.062704 | -0.013659 | -0.0022453 | -0.0014913 | 0.070006 | 0.013904 | 0.064267 | -61.885 | -0.007751 | -62.0304 | 61.778 | 61.5503 | 61.683 | -62.0388 | -61.9489 | 0.000359 | -62.0155 | 61.6195 | 61.7516 | 61.1779 | -62.1888 | -0.016401 | -0.093385 | 0.13738 | -0.007976 | 0.008425 | -0.32108 | -0.18838 | -0.16641 | -0.25185 | 0.073503 | 0.006947 | 0.17335 | -0.11976 | -0.69346 | 123.8004 | 123.5727 | 123.7054 | 62.0146 | -123.9101 | 123.6419 | 123.774 | 123.2003 | 62.0228 | -124.0601
46.5625 | 123.9944 | -62.0361 | 61.7615 | 1.4211e-13 | -0.0024529 | 0.0016666 | 0.065468 | -0.0049655 | 0.062704 | 0.0016025 | -0.0024589 | -0.0012777 | 0.07022 | 0.013476 | 0.064053 | -61.8759 | -0.012329 | -62.035 | 61.778 | 61.5594 | 61.683 | -62.0205 | -61.9489 | -0.00422 | -62.0063 | 61.6103 | 61.7516 | 61.1367 | -62.1842 | 0.015648 | 0.016478 | 0.16027 | 0.001179 | -0.014469 | -0.20205 | -0.078513 | -0.14809 | -0.15115 | 0.087236 | 0.029838 | 0.17793 | -0.009892 | -0.6248 | 123.8141 | 123.5956 | 123.7191 | 62.0238 | -123.782 | 123.6465 | 123.7877 | 123.1728 | 62.0319 | -123.9457
48.2969 | 124.0494 | -62.0178 | 61.7661 | 1.4211e-13 | -0.0022393 | 0.0018804 | 0.065255 | -0.0053929 | 0.062917 | -0.006028 | -0.0024589 | -0.0010641 | 0.070006 | 0.01369 | 0.06448 | -61.8804 | -0.007751 | -62.035 | 61.778 | 61.5548 | 61.683 | -62.0159 | -61.9535 | 0.000359 | -62.0063 | 61.6057 | 61.7516 | 61.1367 | -62.1888 | 0.001916 | 0.011901 | 0.13738 | -0.017132 | -0.019048 | -0.21121 | -0.08309 | -0.17098 | -0.1603 | 0.064347 | 0.011527 | 0.18251 | -0.014469 | -0.62938 | 123.7958 | 123.5727 | 123.7008 | 62.0101 | -123.782 | 123.6236 | 123.7694 | 123.1545 | 62.0182 | -123.9549
49.9688 | 124.0128 | -62.0132 | 61.7386 | 1.4211e-13 | -0.0024529 | 0.0016666 | 0.065468 | -0.0056065 | 0.062704 | -0.006028 | -0.0024589 | -0.0014913 | 0.069792 | 0.014117 | 0.064053 | -61.885 | -0.012329 | -62.0258 | 61.7734 | 61.5594 | 61.6692 | -62.0205 | -61.9489 | 0.004938 | -62.0109 | 61.6057 | 61.7424 | 61.1275 | -62.1842 | -0.00724 | 0.034788 | 0.12822 | -0.012553 | -0.005313 | -0.17916 | -0.069359 | -0.17098 | -0.13284 | 0.064348 | 0.002371 | 0.17335 | 0.00384 | -0.61107 | 123.7866 | 123.5727 | 123.6825 | 62.0009 | -123.7591 | 123.619 | 123.7557 | 123.1408 | 62.0182 | -123.9228
51.7344 | 123.9899 | -61.9949 | 61.8027 | 1.4211e-13 | -0.0022393 | 0.002094 | 0.065255 | -0.0049655 | 0.062704 | -0.006028 | -0.0022453 | -0.0012777 | 0.069579 | 0.01369 | 0.064053 | -61.885 | -0.007751 | -62.0304 | 61.7734 | 61.5548 | 61.6738 | -62.0159 | -61.9489 | 0.004938 | -62.0017 | 61.6149 | 61.747 | 61.1275 | -62.1888 | -0.020972 | -0.029299 | 0.10991 | -0.035442 | -0.01447 | -0.24783 | -0.12887 | -0.19387 | -0.18777 | 0.046037 | -0.006783 | 0.18709 | -0.055669 | -0.67516 | 123.7683 | 123.5498 | 123.6687 | 61.9872 | -123.8186 | 123.6098 | 123.7419 | 123.1225 | 61.9999 | -123.9915
53.6719 | 123.9212 | -61.9949 | 61.8576 | 1.4211e-13 | -0.0024529 | 0.0016666 | 0.065896 | -0.0053929 | 0.06249 | 0.0016025 | -0.0024589 | -0.0012777 | 0.070006 | 0.01369 | 0.064267 | -61.8667 | -0.021486 | -62.0212 | 61.7688 | 61.5548 | 61.6784 | -62.0022 | -61.9489 | 0.000359 | -62.0063 | 61.6103 | 61.7424 | 61.1275 | -62.1796 | -0.007236 | -0.088809 | 0.12823 | -0.026285 | -0.019049 | -0.30276 | -0.17922 | -0.18471 | -0.24728 | 0.046037 | -0.011361 | 0.17335 | -0.11518 | -0.73009 | 123.7637 | 123.5498 | 123.6733 | 61.9734 | -123.8598 | 123.6053 | 123.7374 | 123.1225 | 61.9953 | -124.0373
55.3594 | 124.0082 | -62.0132 | 61.7752 | 1.4211e-13 | -0.0020257 | 0.002094 | 0.065468 | -0.0047519 | 0.062917 | 0.0016025 | -0.0022453 | -0.0010641 | 0.070006 | 0.014117 | 0.064053 | -61.8713 | -0.007751 | -62.0304 | 61.7688 | 61.5548 | 61.6738 | -62.0067 | -61.9443 | -0.008798 | -61.9971 | 61.6012 | 61.747 | 61.1275 | -62.1842 | 0.006497 | -0.006412 | 0.14196 | -0.017131 | -0.023628 | -0.22037 | -0.1014 | -0.17098 | -0.17404 | 0.068927 | 0.016107 | 0.18709 | -0.028204 | -0.64769 | 123.782 | 123.5681 | 123.687 | 62.0055 | -123.782 | 123.6144 | 123.7602 | 123.1408 | 62.0044 | -123.9594
57.0312 | 123.9578 | -61.9812 | 61.853 | 1.4211e-13 | -0.0024529 | 0.0016666 | 0.065255 | -0.0049655 | 0.06249 | 0.0016025 | -0.0024589 | -0.0014913 | 0.070006 | 0.014117 | 0.064267 | -61.8759 | -0.021486 | -62.0166 | 61.7642 | 61.5503 | 61.6692 | -62.0067 | -61.9489 | 0.000359 | -62.0017 | 61.5966 | 61.7424 | 61.1275 | -62.1796 | -0.025547 | -0.088809 | 0.10534 | -0.03544 | -0.009893 | -0.30276 | -0.1838 | -0.19845 | -0.25644 | 0.032304 | -0.020516 | 0.17793 | -0.1106 | -0.72551 | 123.7454 | 123.5315 | 123.6504 | 61.9597 | -123.8598 | 123.5778 | 123.7236 | 123.1087 | 61.9816 | -124.0327
58.6875 | 123.9578 | -61.9904 | 61.853 | 1.4211e-13 | -0.0024529 | 0.002094 | 0.065682 | -0.0049655 | 0.062917 | -0.006028 | -0.0024589 | -0.0010641 | 0.069792 | 0.014331 | 0.064267 | -61.8759 | -0.003172 | -62.0304 | 61.7642 | 61.5457 | 61.6738 | -62.0067 | -61.9397 | -0.00422 | -62.0017 | 61.6057 | 61.7378 | 61.1321 | -62.1796 | -0.016392 | -0.088809 | 0.11449 | -0.04002 | -0.023628 | -0.30734 | -0.17922 | -0.18929 | -0.24728 | 0.050617 | -0.011361 | 0.17793 | -0.11518 | -0.72093 | 123.7546 | 123.536 | 123.6642 | 61.9872 | -123.8598 | 123.5961 | 123.7282 | 123.1225 | 61.9861 | -124.0327
60.3438 | 123.9716 | -62.0178 | 61.7798 | 1.4211e-13 | -0.0026667 | 0.0018804 | 0.065468 | -0.0051793 | 0.062917 | -0.013659 | -0.0024589 | -0.0012777 | 0.069792 | 0.014117 | 0.06448 | -61.8713 | -0.012329 | -62.0258 | 61.7688 | 61.5548 | 61.6784 | -62.0113 | -61.9352 | -0.00422 | -62.0063 | 61.6103 | 61.7424 | 61.1321 | -62.1796 | 0.006495 | -0.010989 | 0.14654 | -0.007976 | -0.014471 | -0.22494 | -0.1014 | -0.16183 | -0.16946 | 0.082661 | 0.011527 | 0.17335 | -0.037359 | -0.64769 | 123.7866 | 123.5727 | 123.6962 | 62.0055 | -123.7911 | 123.6281 | 123.7602 | 123.1499 | 62.0136 | -123.9594
62.0156 | 123.9487 | -61.9858 | 61.8439 | 1.4211e-13 | -0.0026667 | 0.002094 | 0.065682 | -0.0047519 | 0.062704 | -0.013659 | -0.0020317 | -0.0014913 | 0.070006 | 0.014117 | 0.064267 | -61.8667 | -0.007751 | -62.0258 | 61.7642 | 61.5411 | 61.6692 | -61.993 | -61.9397 | -0.00422 | -62.0017 | 61.6057 | 61.7378 | 61.1229 | -62.1842 | -0.007233 | -0.079654 | 0.11907 | -0.040019 | -0.032786 | -0.30277 | -0.17464 | -0.19845 | -0.23812 | 0.04604 | -0.015938 | 0.18251 | -0.10602 | -0.72093 | 123.75 | 123.5269 | 123.655 | 61.978 | -123.8369 | 123.5915 | 123.7236 | 123.1087 | 61.9816 | -124.0281
64.0469 | 124.0448 | -62.0087 | 61.7569 | 1.4211e-13 | -0.0026667 | 0.0018804 | 0.065682 | -0.0049655 | 0.062704 | 0.0016025 | -0.0022453 | -0.0012777 | 0.069792 | 0.013904 | 0.064267 | -61.8621 | -0.012329 | -62.0212 | 61.7642 | 61.5503 | 61.6692 | -61.9976 | -61.9352 | -0.008798 | -61.9971 | 61.6103 | 61.7333 | 61.1229 | -62.1751 | 0.011076 | 0.007321 | 0.14654 | -0.012552 | -0.023628 | -0.20663 | -0.08767 | -0.1664 | -0.14657 | 0.073506 | 0.011529 | 0.17793 | -0.023629 | -0.63396 | 123.7729 | 123.5589 | 123.6779 | 61.9963 | -123.7545 | 123.619 | 123.7419 | 123.1316 | 61.9999 | -123.932
65.8438 | 124.0356 | -61.9904 | 61.7523 | 1.4211e-13 | -0.0022393 | 0.002094 | 0.065255 | -0.0049655 | 0.062276 | -0.006028 | -0.0022453 | -0.0014913 | 0.07022 | 0.014331 | 0.064267 | -61.8713 | -0.012329 | -62.0258 | 61.7642 | 61.5548 | 61.6646 | -62.0067 | -61.9306 | 0.000359 | -61.988 | 61.6057 | 61.7378 | 61.1275 | -62.1751 | -0.016392 | 0.011899 | 0.11907 | -0.035442 | -0.01905 | -0.19748 | -0.087671 | -0.18471 | -0.14657 | 0.059774 | 0.002375 | 0.18709 | -0.014472 | -0.6248 | 123.7546 | 123.5452 | 123.655 | 61.978 | -123.7591 | 123.5961 | 123.7282 | 123.1179 | 61.9907 | -123.9274
67.5156 | 124.0356 | -61.9995 | 61.7615 | 1.4211e-13 | -0.0024529 | 0.0016666 | 0.065255 | -0.0049655 | 0.06249 | -0.013659 | -0.0022453 | -0.0012777 | 0.07022 | 0.014545 | 0.063839 | -61.8667 | -0.016908 | -62.0258 | 61.7551 | 61.5457 | 61.6646 | -61.9976 | -61.9306 | 0.000359 | -61.9971 | 61.6012 | 61.7333 | 61.1138 | -62.1751 | 0.001921 | -0.006414 | 0.1328 | -0.026286 | -0.028207 | -0.21579 | -0.096827 | -0.17556 | -0.16031 | 0.06893 | 0.002374 | 0.17793 | -0.028207 | -0.64769 | 123.7546 | 123.5452 | 123.6642 | 61.9826 | -123.7591 | 123.6007 | 123.7328 | 123.1133 | 61.9999 | -123.9365
69.2031 | 124.0494 | -61.9904 | 61.7386 | 1.4211e-13 | -0.0024529 | 0.0018804 | 0.065255 | -0.0051793 | 0.062704 | 0.0016025 | -0.0024589 | -0.0014913 | 0.070006 | 0.014117 | 0.064267 | -61.8667 | -0.012329 | -62.0166 | 61.7688 | 61.5457 | 61.6692 | -62.0022 | -61.9306 | -0.008798 | -61.9926 | 61.6012 | 61.7287 | 61.1184 | -62.1751 | -0.011814 | 0.03021 | 0.12365 | -0.026285 | -0.014471 | -0.1929 | -0.069359 | -0.18471 | -0.13742 | 0.059774 | -0.002203 | 0.18251 | -0.009896 | -0.62023 | 123.7592 | 123.536 | 123.6596 | 61.978 | -123.7408 | 123.5915 | 123.719 | 123.1087 | 61.9816 | -123.9137
70.8906 | 124.0219 | -61.9949 | 61.7523 | 1.4211e-13 | -0.0022393 | 0.0023076 | 0.065468 | -0.0047519 | 0.063131 | -0.006028 | -0.0022453 | -0.0012777 | 0.070006 | 0.014117 | 0.063839 | -61.8621 | -0.012329 | -62.0166 | 61.7551 | 61.5365 | 61.6601 | -62.0022 | -61.9306 | -0.008798 | -61.9971 | 61.6012 | 61.7333 | 61.1138 | -62.1751 | -0.007236 | 0.002742 | 0.1328 | -0.021707 | -0.014471 | -0.21579 | -0.09225 | -0.18014 | -0.15115 | 0.064352 | -0.002204 | 0.17793 | -0.019051 | -0.63854 | 123.75 | 123.5315 | 123.655 | 61.9826 | -123.7545 | 123.5961 | 123.7282 | 123.1087 | 61.9861 | -123.9274
72.5938 | 123.8892 | -61.9949 | 61.8347 | 1.4211e-13 | -0.0024529 | 0.002094 | 0.065468 | -0.0058203 | 0.062704 | -0.006028 | -0.0022453 | -0.0014913 | 0.069792 | 0.014331 | 0.064267 | -61.8621 | -0.012329 | -62.0212 | 61.7551 | 61.5457 | 61.6692 | -61.9884 | -61.9352 | -0.00422 | -61.988 | 61.6057 | 61.7287 | 61.1229 | -62.1705 | 0.006501 | -0.079656 | 0.1328 | -0.026285 | -0.032786 | -0.28903 | -0.16549 | -0.17556 | -0.22897 | 0.059773 | 0.006953 | 0.18251 | -0.10603 | -0.71178 | 123.75 | 123.5406 | 123.6642 | 61.9826 | -123.8231 | 123.6007 | 123.7236 | 123.1179 | 61.9907 | -124.0052
74.3125 | 124.0128 | -61.9812 | 61.7432 | 1.4211e-13 | -0.0028803 | 0.0018804 | 0.065896 | -0.0053929 | 0.062704 | -0.006028 | -0.0024589 | -0.0014913 | 0.069792 | 0.014331 | 0.064267 | -61.8576 | -0.012329 | -62.0166 | 61.7642 | 61.5457 | 61.6692 | -61.9976 | -61.926 | -0.00422 | -61.9834 | 61.6012 | 61.7241 | 61.1184 | -62.1705 | -0.01639 | 0.021054 | 0.12365 | -0.03544 | -0.01905 | -0.19748 | -0.073937 | -0.18929 | -0.142 | 0.055198 | -0.002201 | 0.18709 | -0.019053 | -0.62481 | 123.7454 | 123.5269 | 123.6504 | 61.9689 | -123.7408 | 123.5824 | 123.7053 | 123.0996 | 61.977 | -123.9137
75.9688 | 124.0173 | -61.9858 | 61.7477 | 1.4211e-13 | -0.0024529 | 0.0018804 | 0.065468 | -0.0051793 | 0.062917 | 0.0016025 | -0.0022453 | -0.0010641 | 0.070006 | 0.014117 | 0.064053 | -61.853 | -0.012329 | -62.0121 | 61.7596 | 61.5365 | 61.6646 | -61.9976 | -61.926 | -0.00422 | -61.9926 | 61.5966 | 61.7333 | 61.1138 | -62.1705 | -0.011812 | 0.011897 | 0.13281 | -0.026284 | -0.014472 | -0.21122 | -0.083094 | -0.18471 | -0.15115 | 0.059776 | -0.00678 | 0.17793 | -0.014474 | -0.63396 | 123.7454 | 123.5223 | 123.6504 | 61.9734 | -123.7453 | 123.5824 | 123.719 | 123.0996 | 61.9816 | -123.9182
77.625 | 123.999 | -61.9858 | 61.7386 | 1.4211e-13 | -0.0026667 | 0.0016666 | 0.065682 | -0.0053929 | 0.062704 | -0.013659 | -0.0022453 | -0.0012777 | 0.07022 | 0.014758 | 0.064267 | -61.8576 | -0.007751 | -62.0166 | 61.7551 | 61.5365 | 61.6738 | -61.9839 | -61.926 | -0.008798 | -61.9834 | 61.5966 | 61.7333 | 61.1138 | -62.1659 | 0.001925 | 0.016475 | 0.12823 | -0.030862 | -0.032787 | -0.20206 | -0.064781 | -0.18013 | -0.142 | 0.059776 | 0.002377 | 0.18251 | -0.005318 | -0.62481 | 123.7408 | 123.5223 | 123.6596 | 61.978 | -123.7224 | 123.5824 | 123.719 | 123.0996 | 61.977 | -123.9045
79.2812 | 124.0128 | -61.9766 | 61.7615 | 1.4211e-13 | -0.0022393 | 0.0016666 | 0.065468 | -0.0051793 | 0.062704 | -0.006028 | -0.0028861 | -0.0010641 | 0.07022 | 0.014545 | 0.063839 | -61.853 | -0.012329 | -62.0166 | 61.7551 | 61.5503 | 61.6601 | -61.9976 | -61.9168 | -0.008798 | -61.9834 | 61.592 | 61.7287 | 61.1138 | -62.1613 | -0.020967 | -0.006414 | 0.12365 | -0.040017 | -0.01905 | -0.21121 | -0.10141 | -0.18471 | -0.16946 | 0.059778 | -0.006778 | 0.17793 | -0.032785 | -0.64769 | 123.7317 | 123.5269 | 123.6367 | 61.9643 | -123.7591 | 123.5686 | 123.7053 | 123.0904 | 61.9678 | -123.9228
80.9375 | 123.999 | -61.9766 | 61.7523 | 1.4211e-13 | -0.0026667 | 0.0018804 | 0.065468 | -0.0053929 | 0.062704 | -0.013659 | -0.0022453 | -0.0014913 | 0.070006 | 0.014331 | 0.064053 | -61.853 | -0.012329 | -62.0121 | 61.7459 | 61.5274 | 61.6646 | -61.9976 | -61.9214 | -0.00422 | -61.9834 | 61.5966 | 61.7287 | 61.1138 | -62.1613 | -0.020967 | -0.006415 | 0.12365 | -0.035439 | -0.014472 | -0.22495 | -0.087671 | -0.18471 | -0.15573 | 0.0552 | -0.006778 | 0.17793 | -0.023629 | -0.63854 | 123.7225 | 123.504 | 123.6413 | 61.9643 | -123.7499 | 123.5732 | 123.7053 | 123.0904 | 61.9724 | -123.9137
82.625 | 123.9944 | -61.9858 | 61.7706 | 1.4211e-13 | -0.0024529 | 0.0018804 | 0.065468 | -0.0053929 | 0.062917 | -0.006028 | -0.0026725 | -0.0017051 | 0.069792 | 0.014758 | 0.064053 | -61.8484 | -0.007751 | -62.0121 | 61.7551 | 61.5411 | 61.6646 | -61.9839 | -61.9214 | -0.00422 | -61.9788 | 61.5966 | 61.7287 | 61.1184 | -62.1613 | 0.001925 | -0.015569 | 0.13739 | -0.026284 | -0.028209 | -0.22952 | -0.10598 | -0.17555 | -0.17404 | 0.064355 | 0.006956 | 0.18251 | -0.04194 | -0.65227 | 123.7408 | 123.5269 | 123.6504 | 61.978 | -123.7545 | 123.5824 | 123.7145 | 123.1041 | 61.9816 | -123.932
84.2812 | 123.999 | -61.9675 | 61.7477 | 1.4211e-13 | -0.0026667 | 0.0016666 | 0.065468 | -0.0053929 | 0.062704 | -0.006028 | -0.0022453 | -0.0012777 | 0.070006 | 0.014545 | 0.064053 | -61.853 | -0.007751 | -62.0075 | 61.7505 | 61.5411 | 61.6601 | -61.9976 | -61.9123 | 0.004938 | -61.9834 | 61.592 | 61.7287 | 61.1046 | -62.1659 | -0.030123 | 0.002741 | 0.1145 | -0.040016 | -0.009893 | -0.20664 | -0.087673 | -0.19844 | -0.15573 | 0.055201 | -0.015934 | 0.18251 | -0.019052 | -0.64312 | 123.718 | 123.5086 | 123.6275 | 61.9597 | -123.7453 | 123.5595 | 123.6962 | 123.0721 | 61.9724 | -123.9137
85.9375 | 124.0219 | -61.9675 | 61.7386 | 1.4211e-13 | -0.0024529 | 0.002094 | 0.065682 | -0.0051793 | 0.062917 | -0.013659 | -0.0024589 | -0.0012777 | 0.070006 | 0.014331 | 0.064053 | -61.8392 | -0.016908 | -61.9983 | 61.7505 | 61.5319 | 61.6601 | -61.9976 | -61.9168 | -0.008798 | -61.9834 | 61.5874 | 61.7241 | 61.1046 | -62.1613 | -0.030123 | 0.011897 | 0.12823 | -0.03086 | -0.000737 | -0.20664 | -0.078517 | -0.19387 | -0.15115 | 0.050622 | -0.015934 | 0.17793 | -0.014475 | -0.63396 | 123.718 | 123.4994 | 123.6275 | 61.9506 | -123.7362 | 123.5549 | 123.6916 | 123.0721 | 61.9587 | -123.8999
87.6094 | 123.8617 | -61.9766 | 61.821 | 1.4211e-13 | -0.0024529 | 0.0018804 | 0.065468 | -0.0053929 | 0.063131 | 0.0016025 | -0.0022453 | -0.0012777 | 0.070006 | 0.014545 | 0.064053 | -61.853 | -0.012329 | -61.9983 | 61.7459 | 61.5274 | 61.6555 | -61.9884 | -61.9168 | -0.00422 | -61.9788 | 61.5874 | 61.7287 | 61.1092 | -62.1659 | -0.011809 | -0.07508 | 0.12365 | -0.021704 | -0.009895 | -0.29362 | -0.16549 | -0.18929 | -0.23355 | 0.059778 | -0.002199 | 0.18709 | -0.092294 | -0.71178 | 123.7225 | 123.504 | 123.6321 | 61.9643 | -123.8094 | 123.5641 | 123.7053 | 123.0858 | 61.9724 | -123.9869
89.2656 | 123.88 | -61.9858 | 61.7889 | 1.4211e-13 | -0.0026667 | 0.001453 | 0.065468 | -0.0053929 | 0.062704 | 0.0016025 | -0.0026725 | -0.0014913 | 0.069579 | 0.014545 | 0.064053 | -61.8438 | -0.012329 | -62.0029 | 61.7459 | 61.5319 | 61.6555 | -61.9884 | -61.9168 | -0.008798 | -61.9788 | 61.5829 | 61.7195 | 61.1092 | -62.1751 | -0.002654 | -0.043036 | 0.14196 | -0.017127 | -0.014473 | -0.25699 | -0.13345 | -0.18929 | -0.20608 | 0.068933 | 0.006956 | 0.19625 | -0.069407 | -0.67974 | 123.7317 | 123.5177 | 123.6413 | 61.9734 | -123.7774 | 123.5686 | 123.7053 | 123.095 | 61.977 | -123.964
90.9375 | 123.9944 | -61.972 | 61.7615 | 1.4211e-13 | -0.0024529 | 0.0016666 | 0.065255 | -0.0053929 | 0.062917 | -0.006028 | -0.0024589 | -0.0010641 | 0.07022 | 0.014758 | 0.064053 | -61.8392 | -0.016908 | -62.0029 | 61.7459 | 61.5274 | 61.6601 | -61.9884 | -61.9123 | -0.008798 | -61.9788 | 61.5874 | 61.7287 | 61.1046 | -62.1659 | -0.016387 | -0.015571 | 0.13281 | -0.03086 | -0.014473 | -0.23411 | -0.10141 | -0.19387 | -0.17404 | 0.059779 | -0.006777 | 0.18709 | -0.032785 | -0.65685 | 123.718 | 123.4994 | 123.6321 | 61.9551 | -123.7499 | 123.5595 | 123.7007 | 123.0767 | 61.9632 | -123.9274
92.6719 | 123.8663 | -61.9629 | 61.8393 | 1.4211e-13 | -0.0024529 | 0.0018804 | 0.065468 | -0.0049655 | 0.062704 | 0.0016025 | -0.0024589 | -0.0012777 | 0.07022 | 0.014972 | 0.064267 | -61.8392 | -0.003172 | -61.9983 | 61.7413 | 61.5319 | 61.6601 | -61.9793 | -61.9168 | -0.00422 | -61.9788 | 61.5874 | 61.7195 | 61.1 | -62.1705 | -0.016384 | -0.097968 | 0.12365 | -0.035437 | -0.019053 | -0.30735 | -0.17923 | -0.2076 | -0.25186 | 0.046045 | -0.015932 | 0.19167 | -0.11976 | -0.73925 | 123.7042 | 123.4948 | 123.623 | 61.9597 | -123.8186 | 123.5503 | 123.6824 | 123.0629 | 61.9587 | -124.0098
94.3594 | 123.8846 | -61.9583 | 61.8484 | 1.4211e-13 | -0.0024529 | 0.0018804 | 0.065682 | -0.0051793 | 0.062704 | 0.0016025 | -0.0020317 | -0.0014913 | 0.070006 | 0.014758 | 0.063839 | -61.8484 | -0.012329 | -61.9983 | 61.7459 | 61.5319 | 61.6555 | -61.993 | -61.9031 | 0.000359 | -61.9788 | 61.5874 | 61.7195 | 61.1092 | -62.1568 | -0.034699 | -0.10255 | 0.10992 | -0.040015 | -0.005316 | -0.3165 | -0.19296 | -0.19844 | -0.26102 | 0.055203 | -0.02051 | 0.17793 | -0.12892 | -0.73925 | 123.7042 | 123.4903 | 123.6138 | 61.946 | -123.8415 | 123.5457 | 123.6778 | 123.0675 | 61.9587 | -124.0052
96.0312 | 123.9853 | -61.9675 | 61.7386 | 1.4211e-13 | -0.0026667 | 0.0018804 | 0.065468 | -0.0053929 | 0.06249 | -0.006028 | -0.0020317 | -0.0010641 | 0.070006 | 0.014758 | 0.064053 | -61.8438 | -0.012329 | -61.9937 | 61.7459 | 61.5365 | 61.6601 | -61.9793 | -61.9214 | 0.004938 | -61.9697 | 61.5874 | 61.7241 | 61.0955 | -62.1613 | -0.011807 | 0.007318 | 0.12365 | -0.026282 | -0.014475 | -0.20206 | -0.078517 | -0.19387 | -0.15115 | 0.046044 | -0.002198 | 0.19167 | -0.014475 | -0.64312 | 123.7134 | 123.504 | 123.6275 | 61.9551 | -123.7179 | 123.5549 | 123.6916 | 123.0629 | 61.9724 | -123.8999
97.7031 | 123.8663 | -61.9904 | 61.7844 | 1.4211e-13 | -0.0028803 | 0.002094 | 0.065896 | -0.0051793 | 0.063131 | 0.0016025 | -0.0022453 | -0.0014913 | 0.07022 | 0.014758 | 0.063839 | -61.8392 | -0.012329 | -61.9983 | 61.7459 | 61.5319 | 61.6509 | -61.9793 | -61.9031 | -0.00422 | -61.9651 | 61.5874 | 61.7241 | 61.1092 | -62.1568 | 0.011081 | -0.038459 | 0.15112 | -0.007972 | -0.019053 | -0.25242 | -0.13345 | -0.1664 | -0.19693 | 0.087246 | 0.025269 | 0.19167 | -0.060252 | -0.67516 | 123.7363 | 123.5223 | 123.6413 | 61.978 | -123.7636 | 123.5778 | 123.7145 | 123.0996 | 61.9861 | -123.9411
99.3594 | 123.912 | -61.9858 | 61.7844 | 1.4211e-13 | -0.0028803 | 0.0018804 | 0.065682 | -0.0053929 | 0.062917 | -0.013659 | -0.0024589 | -0.0010641 | 0.07022 | 0.014758 | 0.063626 | -61.8484 | -0.012329 | -61.9983 | 61.7459 | 61.5228 | 61.6509 | -61.9839 | -61.9168 | -0.008798 | -61.9788 | 61.5829 | 61.7195 | 61.1046 | -62.1613 | 0.001925 | -0.038459 | 0.13739 | -0.012549 | -0.014474 | -0.26157 | -0.13345 | -0.17555 | -0.20151 | 0.068933 | 0.006956 | 0.18251 | -0.06483 | -0.67974 | 123.7317 | 123.5086 | 123.6367 | 61.9734 | -123.7682 | 123.5686 | 123.7053 | 123.0904 | 61.977 | -123.9457
101.0312 | 123.88 | -61.9949 | 61.7706 | 1.4211e-13 | -0.0026667 | 0.002094 | 0.065896 | -0.0056065 | 0.062917 | -0.006028 | -0.0022453 | -0.0012777 | 0.070006 | 0.014331 | 0.063626 | -61.8347 | -0.007751 | -61.9983 | 61.7322 | 61.5319 | 61.6509 | -61.9793 | -61.9031 | -0.008798 | -61.9697 | 61.5829 | 61.715 | 61.1 | -62.1568 | 0.015659 | -0.038461 | 0.16027 | -0.003394 | -0.019053 | -0.23868 | -0.11972 | -0.16182 | -0.18777 | 0.091824 | 0.025268 | 0.18709 | -0.055676 | -0.67059 | 123.7271 | 123.5269 | 123.6458 | 61.9872 | -123.7499 | 123.5778 | 123.7099 | 123.095 | 61.9861 | -123.9274
102.7188 | 123.848 | -62.0041 | 61.821 | 1.4211e-13 | -0.0026667 | 0.0016666 | 0.065468 | -0.0051793 | 0.062276 | -0.013659 | -0.0024589 | -0.0012777 | 0.070006 | 0.014758 | 0.063839 | -61.8392 | -0.003172 | -61.9892 | 61.7413 | 61.5274 | 61.6509 | -61.9839 | -61.9077 | -0.00422 | -61.9697 | 61.5829 | 61.7012 | 61.1046 | -62.1522 | 0.020235 | -0.079658 | 0.16485 | 0.014918 | -0.005317 | -0.29362 | -0.17007 | -0.14809 | -0.23813 | 0.096401 | 0.034423 | 0.18251 | -0.11977 | -0.71636 | 123.7454 | 123.5315 | 123.655 | 62.0009 | -123.8048 | 123.5869 | 123.7053 | 123.1087 | 61.9999 | -123.9732
104.375 | 123.9029 | -61.972 | 61.7935 | 1.4211e-13 | -0.0026667 | 0.002094 | 0.065255 | -0.0053929 | 0.062704 | 0.0016025 | -0.0024589 | -0.0010641 | 0.070006 | 0.014545 | 0.063839 | -61.8347 | -0.016908 | -61.9892 | 61.7367 | 61.5228 | 61.6509 | -61.9839 | -61.8985 | -0.00422 | -61.9742 | 61.5829 | 61.715 | 61.0955 | -62.1522 | -0.011808 | -0.056771 | 0.13739 | -0.017125 | -0.005317 | -0.27073 | -0.14261 | -0.18013 | -0.21066 | 0.073515 | -0.002198 | 0.17793 | -0.078564 | -0.69805 | 123.7088 | 123.4948 | 123.623 | 61.9551 | -123.7774 | 123.5549 | 123.687 | 123.0675 | 61.9678 | -123.9457
106.0469 | 123.967 | -61.9629 | 61.7386 | 1.4211e-13 | -0.0024529 | 0.0018804 | 0.065468 | -0.0058203 | 0.062917 | 0.0016025 | -0.0026725 | -0.0014913 | 0.070006 | 0.014758 | 0.064053 | -61.8301 | -0.007751 | -61.9846 | 61.7367 | 61.5274 | 61.6509 | -61.9701 | -61.8985 | -0.008798 | -61.9651 | 61.5829 | 61.7104 | 61.1046 | -62.1568 | -0.007226 | -0.001839 | 0.13281 | -0.021702 | -0.014476 | -0.21122 | -0.087674 | -0.19386 | -0.15573 | 0.06436 | -0.002196 | 0.19167 | -0.028211 | -0.63396 | 123.6996 | 123.4903 | 123.6138 | 61.9551 | -123.7087 | 123.5457 | 123.6733 | 123.0675 | 61.9541 | -123.8953
107.7344 | 123.9578 | -61.9537 | 61.7386 | 1.4211e-13 | -0.0028803 | 0.0018804 | 0.065468 | -0.0051793 | 0.062704 | -0.006028 | -0.0022453 | -0.0010641 | 0.070006 | 0.015186 | 0.064053 | -61.8392 | -0.007751 | -61.9937 | 61.7322 | 61.5228 | 61.6509 | -61.9747 | -61.8985 | 0.004938 | -61.9651 | 61.5829 | 61.7058 | 61.1 | -62.143 | -0.020961 | -0.006417 | 0.1145 | -0.040015 | -0.019054 | -0.2158 | -0.087674 | -0.18928 | -0.15573 | 0.055204 | -0.011352 | 0.17793 | -0.032789 | -0.63854 | 123.6859 | 123.4765 | 123.6046 | 61.946 | -123.7133 | 123.5366 | 123.6595 | 123.0538 | 61.9587 | -123.8816
109.4219 | 123.9487 | -61.9675 | 61.7386 | 1.4211e-13 | -0.0024529 | 0.0016666 | 0.065468 | -0.0058203 | 0.062704 | -0.006028 | -0.0024589 | -0.0010641 | 0.070006 | 0.014545 | 0.064053 | -61.8347 | -0.003172 | -61.9846 | 61.7413 | 61.5274 | 61.6509 | -61.9793 | -61.9031 | -0.00422 | -61.9605 | 61.5783 | 61.7058 | 61.0955 | -62.1476 | -0.011807 | 0.00274 | 0.13281 | -0.017125 | -0.005318 | -0.21122 | -0.087674 | -0.18013 | -0.16031 | 0.064358 | 0.00696 | 0.18709 | -0.032789 | -0.64312 | 123.7088 | 123.4948 | 123.6184 | 61.9643 | -123.7179 | 123.5457 | 123.6733 | 123.0629 | 61.9632 | -123.8862
111.0781 | 123.9441 | -61.9812 | 61.7111 | 1.4211e-13 | -0.0026667 | 0.0018804 | 0.065468 | -0.0056065 | 0.06249 | 0.0092325 | -0.0024589 | -0.0010641 | 0.07022 | 0.014758 | 0.063839 | -61.8347 | -0.007751 | -61.9846 | 61.7413 | 61.5274 | 61.6463 | -61.9793 | -61.894 | 0.000359 | -61.9651 | 61.5783 | 61.7012 | 61.0955 | -62.1522 | 0.001926 | 0.030205 | 0.14654 | -0.003392 | -0.005318 | -0.18375 | -0.064787 | -0.17097 | -0.13284 | 0.087249 | 0.016114 | 0.18709 | -0.009903 | -0.61566 | 123.7225 | 123.5086 | 123.6275 | 61.9734 | -123.6904 | 123.5595 | 123.6824 | 123.0767 | 61.9816 | -123.8633
112.8125 | 123.9075 | -61.9766 | 61.7111 | 1.4211e-13 | -0.0028803 | 0.002094 | 0.065682 | -0.0053929 | 0.06249 | -0.006028 | -0.0026725 | -0.0014913 | 0.069792 | 0.014972 | 0.064267 | -61.8347 | -0.003172 | -61.9892 | 61.7322 | 61.5228 | 61.6418 | -61.9839 | -61.9077 | -0.00422 | -61.9559 | 61.5829 | 61.7058 | 61.1046 | -62.1476 | -0.00723 | 0.021048 | 0.14196 | -0.012547 | -0.005317 | -0.18833 | -0.069366 | -0.17097 | -0.12827 | 0.068936 | 0.020694 | 0.19167 | -0.005324 | -0.6065 | 123.7088 | 123.4994 | 123.6184 | 61.9735 | -123.695 | 123.5595 | 123.6824 | 123.0812 | 61.9724 | -123.8587
114.5312 | 123.912 | -61.9949 | 61.7249 | 1.4211e-13 | -0.0028803 | 0.0018804 | 0.065468 | -0.0053929 | 0.062704 | -0.013659 | -0.0024589 | -0.0012777 | 0.07022 | 0.014972 | 0.064053 | -61.8255 | -0.007751 | -61.98 | 61.7367 | 61.5228 | 61.6555 | -61.9793 | -61.9031 | 0.000359 | -61.9559 | 61.5783 | 61.7104 | 61.1 | -62.1522 | 0.015659 | 0.011893 | 0.16943 | 0.014919 | -0.00074 | -0.20206 | -0.069363 | -0.15724 | -0.14658 | 0.091824 | 0.039004 | 0.19625 | -0.014479 | -0.62481 | 123.7317 | 123.5177 | 123.6504 | 61.9872 | -123.7041 | 123.5732 | 123.7053 | 123.095 | 61.9953 | -123.877
116.1875 | 123.9304 | -61.94 | 61.7523 | 1.4211e-13 | -0.0026667 | 0.001453 | 0.065468 | -0.0053929 | 0.062917 | -0.006028 | -0.0022453 | -0.0010641 | 0.07022 | 0.014758 | 0.064053 | -61.8209 | -0.016908 | -61.98 | 61.7367 | 61.5182 | 61.6418 | -61.9747 | -61.8894 | 0.000359 | -61.9559 | 61.5783 | 61.7012 | 61.0909 | -62.1476 | -0.034694 | -0.015572 | 0.11908 | -0.040013 | -0.005319 | -0.23411 | -0.11056 | -0.20759 | -0.17404 | 0.050629 | -0.015928 | 0.19167 | -0.051101 | -0.66143 | 123.6767 | 123.4582 | 123.5818 | 61.9231 | -123.727 | 123.5183 | 123.6412 | 123.0309 | 61.9404 | -123.8999
117.8906 | 123.9624 | -61.9537 | 61.7203 | 1.4211e-13 | -0.0026667 | 0.0016666 | 0.065468 | -0.0053929 | 0.062704 | 0.0016025 | -0.0020317 | -0.0017051 | 0.069792 | 0.014758 | 0.063839 | -61.8347 | -0.007751 | -61.9846 | 61.7322 | 61.5182 | 61.6463 | -61.9655 | -61.9031 | -0.00422 | -61.9559 | 61.5783 | 61.7058 | 61.0909 | -62.143 | -0.011803 | 0.011893 | 0.11908 | -0.030858 | -0.019055 | -0.20207 | -0.073942 | -0.18928 | -0.142 | 0.050625 | -0.002195 | 0.18709 | -0.014479 | -0.62939 | 123.6859 | 123.4719 | 123.6001 | 61.946 | -123.6858 | 123.532 | 123.6595 | 123.0446 | 61.9495 | -123.8633
119.6094 | 123.8525 | -61.9354 | 61.8073 | 1.4211e-13 | -0.0028803 | 0.0018804 | 0.065682 | -0.0049655 | 0.06249 | -0.006028 | -0.0022453 | -0.0012777 | 0.070006 | 0.014972 | 0.063626 | -61.8301 | -0.007751 | -61.98 | 61.7322 | 61.5136 | 61.6463 | -61.9701 | -61.894 | -0.00422 | -61.9559 | 61.5737 | 61.7058 | 61.0955 | -62.1384 | -0.034692 | -0.075082 | 0.10534 | -0.04459 | -0.009898 | -0.29362 | -0.16092 | -0.20302 | -0.23355 | 0.041473 | -0.020505 | 0.18251 | -0.10145 | -0.71179 | 123.6676 | 123.4491 | 123.5818 | 61.9277 | -123.7774 | 123.5091 | 123.6412 | 123.0309 | 61.9312 | -123.9457
121.3125 | 123.9395 | -61.9354 | 61.7157 | 1.4211e-13 | -0.0028803 | 0.0023076 | 0.065468 | -0.0053929 | 0.06249 | -0.013659 | -0.0022453 | -0.0014913 | 0.070006 | 0.014972 | 0.064053 | -61.8255 | -0.007751 | -61.9754 | 61.7276 | 61.5228 | 61.6372 | -61.9564 | -61.9031 | -0.00422 | -61.9605 | 61.5737 | 61.7104 | 61.0863 | -62.143 | -0.020955 | 0.011893 | 0.10992 | -0.040011 | -0.019056 | -0.19291 | -0.078522 | -0.20759 | -0.142 | 0.032315 | -0.025083 | 0.18251 | -0.005323 | -0.62939 | 123.663 | 123.4582 | 123.5726 | 61.9277 | -123.6721 | 123.5091 | 123.6458 | 123.0217 | 61.9312 | -123.8587
122.9844 | 123.8663 | -61.9354 | 61.7752 | 1.4211e-13 | -0.0026667 | 0.0016666 | 0.065468 | -0.0056065 | 0.062917 | 0.0016025 | -0.0024589 | -0.0012777 | 0.070006 | 0.014972 | 0.063626 | -61.8209 | -0.012329 | -61.98 | 61.723 | 61.5136 | 61.6463 | -61.9747 | -61.8894 | 0.000359 | -61.9605 | 61.5691 | 61.6966 | 61.1092 | -62.1384 | -0.039271 | -0.052196 | 0.1145 | -0.04459 | -0.005319 | -0.26158 | -0.12887 | -0.20302 | -0.20609 | 0.046052 | -0.025083 | 0.17793 | -0.078568 | -0.66601 | 123.6584 | 123.4491 | 123.5818 | 61.9231 | -123.7499 | 123.5045 | 123.6321 | 123.0446 | 61.9358 | -123.9136
124.6562 | 123.8205 | -61.9858 | 61.7661 | 1.4211e-13 | -0.0028803 | 0.0018804 | 0.065255 | -0.0053929 | 0.06249 | -0.013659 | -0.0022453 | -0.0014913 | 0.07022 | 0.014972 | 0.063839 | -61.8209 | -0.012329 | -61.98 | 61.723 | 61.5228 | 61.6372 | -61.9655 | -61.894 | -0.00422 | -61.9514 | 61.5645 | 61.6966 | 61.0817 | -62.1384 | 0.020241 | -0.04304 | 0.16486 | 0.005764 | -0.014477 | -0.24326 | -0.12888 | -0.15266 | -0.20151 | 0.091827 | 0.034428 | 0.18709 | -0.069412 | -0.68432 | 123.7088 | 123.5086 | 123.623 | 61.9734 | -123.7316 | 123.5503 | 123.6824 | 123.0675 | 61.9816 | -123.9045
126.3281 | 123.8342 | -61.9492 | 61.7935 | 1.4211e-13 | -0.0028803 | 0.0018804 | 0.065468 | -0.0053929 | 0.06249 | 0.0016025 | -0.0026725 | -0.0012777 | 0.070006 | 0.015399 | 0.063839 | -61.8209 | -0.003172 | -61.9709 | 61.7276 | 61.5091 | 61.6418 | -61.9655 | -61.8894 | -0.008798 | -61.9559 | 61.5691 | 61.7012 | 61.0909 | -62.1384 | -0.01638 | -0.065927 | 0.12823 | -0.0217 | -0.00532 | -0.28447 | -0.15176 | -0.18928 | -0.2244 | 0.059785 | -0.006772 | 0.18251 | -0.0923 | -0.70263 | 123.6767 | 123.4582 | 123.5909 | 61.946 | -123.7591 | 123.5183 | 123.6504 | 123.04 | 61.9404 | -123.932
128 | 123.9349 | -61.9537 | 61.7065 | 1.4211e-13 | -0.0028803 | 0.0016666 | 0.065255 | -0.0053929 | 0.062704 | -0.006028 | -0.0022453 | -0.0012777 | 0.07022 | 0.014972 | 0.063626 | -61.8255 | -0.003172 | -61.9754 | 61.7322 | 61.5136 | 61.6418 | -61.9655 | -61.8894 | -0.00422 | -61.9468 | 61.5645 | 61.7058 | 61.0863 | -62.1293 | -0.011803 | 0.025626 | 0.12823 | -0.021701 | -0.009898 | -0.19291 | -0.064788 | -0.17555 | -0.142 | 0.064362 | 0.006963 | 0.18251 | -0.000746 | -0.62024 | 123.6859 | 123.4674 | 123.5955 | 61.9506 | -123.6721 | 123.5183 | 123.6595 | 123.04 | 61.9495 | -123.8358
129.6719 | 123.8709 | -61.9217 | 61.7981 | 1.4211e-13 | -0.0028803 | 0.0016666 | 0.065468 | -0.0056065 | 0.062063 | 0.0016025 | -0.0022453 | -0.0010641 | 0.070433 | 0.015186 | 0.063626 | -61.8163 | -0.003172 | -61.98 | 61.7184 | 61.5136 | 61.6372 | -61.9518 | -61.8894 | -0.013377 | -61.9559 | 61.56 | 61.7058 | 61.0863 | -62.1384 | -0.030109 | -0.079662 | 0.10535 | -0.058323 | -0.028214 | -0.28447 | -0.16092 | -0.21675 | -0.23813 | 0.032319 | -0.034238 | 0.18251 | -0.092299 | -0.71179 | 123.6401 | 123.4353 | 123.5589 | 61.9185 | -123.7499 | 123.4817 | 123.6275 | 123.008 | 61.9083 | -123.9365
131.3438 | 123.9578 | -61.972 | 61.7294 | 1.4211e-13 | -0.0028803 | 0.0018804 | 0.065682 | -0.0056065 | 0.062704 | 0.0016025 | -0.0024589 | -0.0017051 | 0.070006 | 0.015399 | 0.063626 | -61.8072 | -0.007751 | -61.9754 | 61.723 | 61.5045 | 61.6418 | -61.961 | -61.8802 | -0.00422 | -61.9468 | 61.5691 | 61.6966 | 61.0772 | -62.1384 | 0.011087 | -0.006419 | 0.16486 | -0.00339 | -0.014477 | -0.22496 | -0.087676 | -0.16639 | -0.16031 | 0.09183 | 0.025274 | 0.19167 | -0.032791 | -0.65228 | 123.6951 | 123.4765 | 123.6138 | 61.9643 | -123.6904 | 123.5412 | 123.6687 | 123.0492 | 61.9678 | -123.8679
133.0156 | 123.8068 | -61.9446 | 61.7935 | 1.4211e-13 | -0.0030939 | 0.0018804 | 0.065468 | -0.0056065 | 0.062276 | -0.006028 | -0.0022453 | -0.0012777 | 0.070006 | 0.015399 | 0.063198 | -61.8163 | -0.016908 | -61.98 | 61.7139 | 61.4999 | 61.6326 | -61.9564 | -61.8894 | -0.00422 | -61.9468 | 61.5691 | 61.6966 | 61.0817 | -62.1384 | -0.0118 | -0.079663 | 0.12824 | -0.035435 | -0.023635 | -0.29362 | -0.16092 | -0.19386 | -0.2244 | 0.055207 | -0.002192 | 0.19167 | -0.096878 | -0.71179 | 123.6584 | 123.4445 | 123.5772 | 61.9277 | -123.7499 | 123.5137 | 123.6412 | 123.0263 | 61.9404 | -123.932
134.7188 | 123.9532 | -61.94 | 61.702 | 1.4211e-13 | -0.0030939 | 0.0018804 | 0.065468 | -0.0056065 | 0.06249 | -0.006028 | -0.0022453 | -0.0012777 | 0.070006 | 0.015399 | 0.063412 | -61.8209 | -0.007751 | -61.9709 | 61.7276 | 61.5045 | 61.6326 | -61.961 | -61.8894 | 0.000359 | -61.9468 | 61.5645 | 61.7012 | 61.0772 | -62.1247 | -0.020957 | 0.025626 | 0.11908 | -0.030856 | -0.009899 | -0.19749 | -0.069367 | -0.1847 | -0.13742 | 0.050629 | -0.00677 | 0.17793 | -0.000747 | -0.62481 | 123.6676 | 123.4445 | 123.5726 | 61.9323 | -123.6629 | 123.5045 | 123.6412 | 123.0172 | 61.9404 | -123.8267
136.4219 | 123.8251 | -61.9629 | 61.7569 | 1.4211e-13 | -0.0030939 | 0.0016666 | 0.066109 | -0.0056065 | 0.06249 | -0.006028 | -0.0022453 | -0.0017051 | 0.070006 | 0.015613 | 0.063412 | -61.8163 | -0.012329 | -61.9663 | 61.723 | 61.5136 | 61.6326 | -61.9518 | -61.8848 | -0.00422 | -61.9514 | 61.56 | 61.6966 | 61.0863 | -62.1293 | 0.01109 | -0.033885 | 0.14655 | -0.003389 | -0.014479 | -0.24327 | -0.1243 | -0.16639 | -0.19693 | 0.078096 | 0.01154 | 0.17793 | -0.060257 | -0.67059 | 123.6859 | 123.4765 | 123.5955 | 61.9506 | -123.7087 | 123.5229 | 123.6595 | 123.0492 | 61.9587 | -123.8862
138.1094 | 123.8937 | -61.9675 | 61.7111 | 1.4211e-13 | -0.0026667 | 0.001453 | 0.065468 | -0.0056065 | 0.06249 | 0.0016025 | -0.0022453 | -0.0010641 | 0.069792 | 0.015186 | 0.063412 | -61.8118 | -0.003172 | -61.9709 | 61.7276 | 61.5045 | 61.6326 | -61.961 | -61.8756 | -0.008798 | -61.9468 | 61.5554 | 61.6921 | 61.0817 | -62.1247 | 0.006509 | 0.01647 | 0.1557 | -0.00339 | -0.009899 | -0.20665 | -0.078523 | -0.15724 | -0.15574 | 0.091831 | 0.020696 | 0.17793 | -0.01906 | -0.62939 | 123.6951 | 123.4719 | 123.6001 | 61.9643 | -123.6721 | 123.5229 | 123.6595 | 123.0492 | 61.9587 | -123.8358
139.8281 | 123.9304 | -61.9308 | 61.7111 | 1.4211e-13 | -0.0030939 | 0.0018804 | 0.065468 | -0.0058203 | 0.06249 | 0.0092325 | -0.0022453 | -0.0012777 | 0.07022 | 0.015186 | 0.063626 | -61.8163 | -0.003172 | -61.9754 | 61.7184 | 61.5091 | 61.6326 | -61.9472 | -61.8802 | -0.00422 | -61.9422 | 61.56 | 61.6921 | 61.0772 | -62.1247 | -0.016375 | 0.007313 | 0.1145 | -0.044589 | -0.028214 | -0.20207 | -0.078523 | -0.19386 | -0.15116 | 0.050631 | -0.011346 | 0.18251 | -0.01906 | -0.63397 | 123.6493 | 123.4399 | 123.5634 | 61.9277 | -123.6583 | 123.4908 | 123.6229 | 123.008 | 61.9266 | -123.8358
141.5 | 123.8663 | -61.9629 | 61.702 | 1.4211e-13 | -0.0030939 | 0.0016666 | 0.065255 | -0.0058203 | 0.06249 | -0.006028 | -0.0024589 | -0.0012777 | 0.07022 | 0.015186 | 0.063412 | -61.8072 | -0.012329 | -61.9617 | 61.7184 | 61.5091 | 61.6372 | -61.9472 | -61.8756 | -0.00422 | -61.9422 | 61.56 | 61.6921 | 61.0817 | -62.1293 | 0.015669 | 0.016469 | 0.1557 | 0.001189 | -0.01448 | -0.19291 | -0.064789 | -0.16639 | -0.142 | 0.087254 | 0.020698 | 0.18709 | -0.009904 | -0.62024 | 123.6813 | 123.4719 | 123.6001 | 61.9506 | -123.6492 | 123.5229 | 123.655 | 123.0446 | 61.9587 | -123.8312
143.1719 | 123.7976 | -61.9446 | 61.8164 | 1.4211e-13 | -0.0028803 | 0.0018804 | 0.065468 | -0.0056065 | 0.06249 | 0.0016025 | -0.0022453 | -0.0014913 | 0.07022 | 0.015399 | 0.063198 | -61.8163 | -0.003172 | -61.9663 | 61.7139 | 61.4999 | 61.6326 | -61.9518 | -61.8756 | -0.008798 | -61.9514 | 61.5508 | 61.6921 | 61.0817 | -62.1247 | -0.007221 | -0.10255 | 0.12824 | -0.0217 | -0.014479 | -0.31651 | -0.18381 | -0.18012 | -0.2656 | 0.068943 | -0.006771 | 0.17335 | -0.12434 | -0.73468 | 123.6584 | 123.4445 | 123.5772 | 61.9414 | -123.7682 | 123.4954 | 123.6366 | 123.0263 | 61.9358 | -123.9411
144.875 | 123.7976 | -61.9354 | 61.7935 | 1.4211e-13 | -0.0026667 | 0.0018804 | 0.065468 | -0.0058203 | 0.062276 | -0.013659 | -0.0022453 | -0.0012777 | 0.07022 | 0.015399 | 0.063412 | -61.8163 | -0.007751 | -61.9663 | 61.7184 | 61.5091 | 61.628 | -61.9472 | -61.8802 | -0.017956 | -61.9422 | 61.56 | 61.6875 | 61.0817 | -62.1339 | -0.011797 | -0.075084 | 0.11908 | -0.030855 | -0.019058 | -0.28447 | -0.1655 | -0.19844 | -0.23355 | 0.055209 | -0.006768 | 0.19167 | -0.10604 | -0.71179 | 123.6539 | 123.4445 | 123.5634 | 61.9277 | -123.7407 | 123.4954 | 123.6229 | 123.0172 | 61.9175 | -123.9274
146.5625 | 123.8297 | -61.9034 | 61.7844 | 1.4211e-13 | -0.0030939 | 0.001453 | 0.065468 | -0.0056065 | 0.062276 | -0.006028 | -0.0024589 | -0.0017051 | 0.070006 | 0.015399 | 0.063412 | -61.8026 | -0.007751 | -61.9663 | 61.7093 | 61.5045 | 61.6326 | -61.9472 | -61.8711 | -0.008798 | -61.9468 | 61.5554 | 61.6966 | 61.0772 | -62.1293 | -0.043841 | -0.075086 | 0.10077 | -0.062899 | -0.019058 | -0.27989 | -0.15176 | -0.2259 | -0.22898 | 0.032322 | -0.043391 | 0.18251 | -0.087723 | -0.70721 | 123.6127 | 123.4079 | 123.536 | 61.8956 | -123.7316 | 123.4588 | 123.6 | 122.9805 | 61.8946 | -123.9136
148.25 | 123.9258 | -61.9537 | 61.6974 | 1.4211e-13 | -0.0026667 | 0.0018804 | 0.065468 | -0.0056065 | 0.062917 | -0.006028 | -0.0024589 | -0.0017051 | 0.070006 | 0.015613 | 0.063198 | -61.8072 | -0.003172 | -61.9663 | 61.7139 | 61.4953 | 61.6326 | -61.9518 | -61.8711 | 0.000359 | -61.9468 | 61.5554 | 61.6875 | 61.0726 | -62.1293 | 0.001934 | 0.016467 | 0.14655 | -0.012545 | -0.014479 | -0.20207 | -0.06479 | -0.17555 | -0.142 | 0.082676 | 0.006963 | 0.18251 | -0.009906 | -0.62482 | 123.6676 | 123.4491 | 123.5863 | 61.9506 | -123.6492 | 123.5091 | 123.6412 | 123.0263 | 61.9541 | -123.8267
149.9375 | 123.8754 | -61.9675 | 61.6745 | 1.4211e-13 | -0.0028803 | 0.002094 | 0.065468 | -0.0056065 | 0.06249 | -0.006028 | -0.0024589 | -0.0012777 | 0.07022 | 0.015613 | 0.063198 | -61.8072 | -0.007751 | -61.9571 | 61.7184 | 61.4999 | 61.628 | -61.9518 | -61.8802 | -0.00422 | -61.9376 | 61.56 | 61.6829 | 61.0726 | -62.1201 | 0.015667 | 0.043934 | 0.16028 | 0.010345 | -0.005322 | -0.1746 | -0.046481 | -0.15266 | -0.11454 | 0.087252 | 0.029853 | 0.18251 | 0.008404 | -0.60193 | 123.6859 | 123.4674 | 123.5955 | 61.9597 | -123.6263 | 123.5274 | 123.6504 | 123.04 | 61.9632 | -123.7946
151.6562 | 123.7885 | -61.9171 | 61.7981 | 1.4211e-13 | -0.0030939 | 0.0016666 | 0.065255 | -0.0053929 | 0.06249 | -0.006028 | -0.0024589 | -0.0012777 | 0.070006 | 0.015399 | 0.063198 | -61.8072 | -0.012329 | -61.9571 | 61.7047 | 61.4999 | 61.628 | -61.9472 | -61.8665 | -0.00422 | -61.9285 | 61.5554 | 61.6783 | 61.0817 | -62.1247 | -0.030108 | -0.093397 | 0.10992 | -0.040009 | -0.009901 | -0.2982 | -0.17008 | -0.20759 | -0.24271 | 0.050634 | -0.011343 | 0.19625 | -0.11977 | -0.71637 | 123.6218 | 123.417 | 123.5451 | 61.9048 | -123.7453 | 123.4725 | 123.5954 | 122.9988 | 61.9129 | -123.9228
153.3281 | 123.8159 | -61.9217 | 61.7798 | 1.4211e-13 | -0.0028803 | 0.0018804 | 0.065682 | -0.0056065 | 0.062276 | 0.0016025 | -0.0024589 | -0.0014913 | 0.070433 | 0.015613 | 0.063412 | -61.8026 | -0.012329 | -61.9663 | 61.7184 | 61.4953 | 61.6234 | -61.9518 | -61.8711 | -0.008798 | -61.933 | 61.5462 | 61.6829 | 61.068 | -62.1293 | -0.030109 | -0.061351 | 0.11908 | -0.044588 | -0.014479 | -0.28447 | -0.15634 | -0.20759 | -0.23356 | 0.050633 | -0.011344 | 0.19625 | -0.096881 | -0.71179 | 123.6401 | 123.417 | 123.5451 | 61.9094 | -123.7316 | 123.4679 | 123.6046 | 122.9897 | 61.9129 | -123.9091
155.0156 | 123.8434 | -61.9034 | 61.7661 | 1.4211e-13 | -0.0030939 | 0.001453 | 0.065896 | -0.0053929 | 0.062704 | -0.006028 | -0.0026725 | -0.0017051 | 0.069579 | 0.015399 | 0.062985 | -61.8026 | -0.012329 | -61.9571 | 61.7093 | 61.4953 | 61.6234 | -61.9472 | -61.8665 | -0.008798 | -61.9376 | 61.5462 | 61.6829 | 61.0634 | -62.1247 | -0.043841 | -0.056775 | 0.10077 | -0.053742 | -0.009901 | -0.27074 | -0.14261 | -0.22132 | -0.21983 | 0.036901 | -0.034234 | 0.18709 | -0.083148 | -0.70264 | 123.6127 | 123.3987 | 123.5268 | 61.8911 | -123.7133 | 123.4496 | 123.5863 | 122.9668 | 61.8946 | -123.8908
156.6719 | 123.9029 | -61.9492 | 61.6882 | 1.4211e-13 | -0.0028803 | 0.0016666 | 0.065682 | -0.0056065 | 0.062276 | 0.0016025 | -0.0024589 | -0.0014913 | 0.069579 | 0.015613 | 0.063626 | -61.8026 | -0.003172 | -61.9617 | 61.7139 | 61.4953 | 61.6326 | -61.9426 | -61.8711 | -0.00422 | -61.9376 | 61.5462 | 61.6783 | 61.0588 | -62.1201 | 0.006514 | 0.025623 | 0.14655 | -0.012544 | -0.019058 | -0.19292 | -0.055634 | -0.17097 | -0.142 | 0.078099 | 0.011543 | 0.18251 | -0.009907 | -0.6294 | 123.663 | 123.4445 | 123.5818 | 61.946 | -123.6309 | 123.4954 | 123.6275 | 123.008 | 61.9449 | -123.8084
158.3281 | 123.7885 | -61.9217 | 61.7844 | 1.4211e-13 | -0.0028803 | 0.0018804 | 0.065682 | -0.0058203 | 0.06249 | 0.0092325 | -0.0024589 | -0.0010641 | 0.07022 | 0.015827 | 0.062985 | -61.7935 | -0.007751 | -61.9525 | 61.7001 | 61.4907 | 61.6234 | -61.9381 | -61.8665 | -0.00422 | -61.933 | 61.5416 | 61.6783 | 61.068 | -62.1155 | -0.016373 | -0.084243 | 0.12824 | -0.030853 | -0.01448 | -0.29363 | -0.16092 | -0.19385 | -0.24271 | 0.055212 | -0.011344 | 0.18251 | -0.10604 | -0.71637 | 123.6218 | 123.4124 | 123.5451 | 61.9139 | -123.7224 | 123.4633 | 123.6 | 122.9897 | 61.9175 | -123.8999
160 | 123.8617 | -61.9217 | 61.7294 | 1.4211e-13 | -0.0030939 | 0.0018804 | 0.065896 | -0.0056065 | 0.062704 | -0.006028 | -0.0022453 | -0.0017051 | 0.070006 | 0.015827 | 0.063198 | -61.8026 | 0.001407 | -61.9525 | 61.6955 | 61.4953 | 61.6234 | -61.9518 | -61.8665 | -0.00422 | -61.9239 | 61.5508 | 61.6783 | 61.0634 | -62.1155 | -0.030109 | -0.033889 | 0.11908 | -0.030853 | -0.000744 | -0.23411 | -0.10599 | -0.19385 | -0.17862 | 0.055212 | -0.002187 | 0.19167 | -0.051106 | -0.66602 | 123.6172 | 123.417 | 123.5451 | 61.9231 | -123.6812 | 123.4725 | 123.6 | 122.9851 | 61.9175 | -123.845
161.6875 | 123.7701 | -61.9354 | 61.7752 | 1.4211e-13 | -0.0028803 | 0.001453 | 0.065682 | -0.0056065 | 0.06249 | 0.0016025 | -0.0028861 | -0.0012777 | 0.070433 | 0.015399 | 0.062985 | -61.8026 | -0.007751 | -61.9525 | 61.7047 | 61.4953 | 61.6234 | -61.9426 | -61.8573 | -0.00422 | -61.933 | 61.5508 | 61.6829 | 61.0588 | -62.1201 | -0.007219 | -0.070509 | 0.13282 | -0.01712 | -0.009901 | -0.27989 | -0.15177 | -0.1847 | -0.2244 | 0.078102 | 0.002389 | 0.18709 | -0.092304 | -0.71637 | 123.6401 | 123.4307 | 123.5589 | 61.9277 | -123.7179 | 123.4862 | 123.6183 | 122.9943 | 61.9312 | -123.8953
163.3594 | 123.8983 | -61.9308 | 61.6837 | 1.4211e-13 | -0.0028803 | 0.0018804 | 0.066109 | -0.0051793 | 0.06249 | -0.006028 | -0.0024589 | -0.0014913 | 0.07022 | 0.015827 | 0.063198 | -61.7935 | -0.007751 | -61.948 | 61.7047 | 61.4953 | 61.6234 | -61.9472 | -61.8619 | -0.00422 | -61.9285 | 61.5416 | 61.6783 | 61.0588 | -62.1155 | -0.016375 | 0.021044 | 0.13739 | -0.01712 | -0.000745 | -0.18834 | -0.060214 | -0.1847 | -0.14201 | 0.068946 | 0.00239 | 0.18709 | -0.00533 | -0.62482 | 123.6355 | 123.4262 | 123.5543 | 61.9231 | -123.6309 | 123.4725 | 123.6092 | 122.9897 | 61.9266 | -123.7992
165.0625 | 123.848 | -61.9217 | 61.7203 | 1.4211e-13 | -0.0028803 | 0.0016666 | 0.066109 | -0.0053929 | 0.06249 | 0.0016025 | -0.0022453 | -0.0014913 | 0.070006 | 0.015613 | 0.063626 | -61.7935 | -0.012329 | -61.9434 | 61.6955 | 61.4907 | 61.6189 | -61.9426 | -61.8573 | -0.00422 | -61.9376 | 61.5371 | 61.6692 | 61.0588 | -62.1201 | -0.020952 | -0.024734 | 0.12824 | -0.021697 | -0.000745 | -0.22954 | -0.10141 | -0.19843 | -0.18321 | 0.064369 | -0.015923 | 0.18251 | -0.051108 | -0.66144 | 123.6172 | 123.4124 | 123.5406 | 61.9094 | -123.6629 | 123.4588 | 123.5909 | 122.9805 | 61.9175 | -123.8404
166.7344 | 123.7747 | -61.9263 | 61.7615 | 1.4211e-13 | -0.0030939 | 0.0016666 | 0.066109 | -0.0056065 | 0.06249 | 0.0016025 | -0.0024589 | -0.0014913 | 0.070006 | 0.015613 | 0.063198 | -61.798 | -0.007751 | -61.9434 | 61.7047 | 61.4862 | 61.6143 | -61.9381 | -61.8573 | -0.00422 | -61.9239 | 61.5371 | 61.6692 | 61.068 | -62.1201 | -0.011795 | -0.056776 | 0.12824 | -0.017119 | -0.005324 | -0.27532 | -0.14719 | -0.19385 | -0.2244 | 0.068947 | 0.002391 | 0.19624 | -0.092307 | -0.69348 | 123.631 | 123.4124 | 123.5406 | 61.9185 | -123.6995 | 123.4633 | 123.5954 | 122.9943 | 61.9221 | -123.8816
168.4062 | 123.8205 | -61.9034 | 61.7798 | 1.4211e-13 | -0.0026667 | 0.0016666 | 0.066109 | -0.0053929 | 0.062276 | -0.006028 | -0.0024589 | -0.0014913 | 0.070006 | 0.015827 | 0.062985 | -61.7889 | -0.003172 | -61.9571 | 61.7001 | 61.4862 | 61.6189 | -61.9426 | -61.8573 | -0.008798 | -61.9193 | 61.5462 | 61.6829 | 61.068 | -62.1155 | -0.039263 | -0.079665 | 0.11451 | -0.053742 | -0.014479 | -0.29363 | -0.16092 | -0.21216 | -0.23356 | 0.046058 | -0.015919 | 0.19624 | -0.096881 | -0.71179 | 123.6035 | 123.3895 | 123.5222 | 61.9002 | -123.7224 | 123.4496 | 123.5863 | 122.9714 | 61.8946 | -123.8953
170.0938 | 123.8754 | -61.908 | 61.7249 | 1.4211e-13 | -0.0033077 | 0.0016666 | 0.065896 | -0.0056065 | 0.06249 | -0.013659 | -0.0026725 | -0.0014913 | 0.07022 | 0.015613 | 0.063412 | -61.7889 | -0.003172 | -61.948 | 61.7001 | 61.4862 | 61.628 | -61.9335 | -61.8619 | 0.000359 | -61.9193 | 61.5462 | 61.6737 | 61.0543 | -62.1064 | -0.025527 | -0.024734 | 0.11908 | -0.040008 | -0.014481 | -0.2387 | -0.096835 | -0.19843 | -0.17863 | 0.046058 | -0.011341 | 0.18709 | -0.051107 | -0.6706 | 123.6081 | 123.3941 | 123.536 | 61.9048 | -123.6583 | 123.4542 | 123.5817 | 122.9622 | 61.9083 | -123.8312
171.8281 | 123.7656 | -61.94 | 61.7477 | 1.4211e-13 | -0.0028803 | 0.0016666 | 0.065896 | -0.0058203 | 0.06249 | -0.013659 | -0.0024589 | -0.0014913 | 0.069792 | 0.015613 | 0.063198 | -61.7889 | -0.012329 | -61.948 | 61.7001 | 61.4907 | 61.6189 | -61.9335 | -61.8665 | -0.00422 | -61.9239 | 61.5416 | 61.6783 | 61.0634 | -62.111 | 0.006516 | -0.047622 | 0.15113 | -0.007965 | -0.014481 | -0.257 | -0.12888 | -0.17097 | -0.20609 | 0.073522 | 0.016123 | 0.18709 | -0.069417 | -0.68433 | 123.6401 | 123.4307 | 123.5589 | 61.9277 | -123.6812 | 123.4817 | 123.6183 | 123.0034 | 61.9358 | -123.8587
173.5 | 123.8892 | -61.9125 | 61.7157 | 1.4211e-13 | -0.0028803 | 0.0018804 | 0.065896 | -0.0056065 | 0.06249 | -0.006028 | -0.0024589 | -0.0017051 | 0.07022 | 0.016254 | 0.063198 | -61.7935 | 0.001407 | -61.9525 | 61.691 | 61.4816 | 61.6234 | -61.9381 | -61.8573 | -0.008798 | -61.9193 | 61.5371 | 61.6783 | 61.0588 | -62.111 | -0.025528 | -0.024735 | 0.11908 | -0.040008 | -0.01448 | -0.23412 | -0.092257 | -0.19843 | -0.17863 | 0.055214 | -0.006763 | 0.19167 | -0.037373 | -0.65686 | 123.6035 | 123.3941 | 123.536 | 61.9139 | -123.6538 | 123.4496 | 123.5909 | 122.9714 | 61.9037 | -123.8267
175.1719 | 123.8846 | -61.8942 | 61.6699 | 1.4211e-13 | -0.0028803 | 0.0018804 | 0.065896 | -0.0058203 | 0.06249 | -0.006028 | -0.0026725 | -0.0014913 | 0.07022 | 0.016468 | 0.063198 | -61.798 | -0.007751 | -61.9388 | 61.6955 | 61.4907 | 61.6189 | -61.9335 | -61.8573 | -0.00422 | -61.9193 | 61.5371 | 61.6692 | 61.0543 | -62.111 | -0.03926 | 0.02562 | 0.096194 | -0.044584 | -0.005324 | -0.17918 | -0.05106 | -0.21674 | -0.13285 | 0.036903 | -0.025074 | 0.19167 | -0.000754 | -0.61566 | 123.5898 | 123.385 | 123.5131 | 61.8865 | -123.6034 | 123.4313 | 123.5634 | 122.9485 | 61.89 | -123.7809
176.875 | 123.7518 | -61.94 | 61.7432 | 1.4211e-13 | -0.0030939 | 0.0016666 | 0.065896 | -0.0058203 | 0.06249 | 0.0092325 | -0.0024589 | -0.0012777 | 0.070006 | 0.015827 | 0.063412 | -61.7843 | -0.003172 | -61.948 | 61.7001 | 61.477 | 61.6189 | -61.9243 | -61.8527 | 0.000359 | -61.9193 | 61.5325 | 61.6783 | 61.0634 | -62.1155 | 0.015674 | -0.043044 | 0.1557 | -0.007965 | -0.023639 | -0.26616 | -0.1243 | -0.17554 | -0.21067 | 0.087258 | 0.020702 | 0.19624 | -0.064839 | -0.67975 | 123.6401 | 123.417 | 123.5589 | 61.9368 | -123.6675 | 123.4725 | 123.6183 | 123.0034 | 61.9404 | -123.8587
178.5469 | 123.8251 | -61.9263 | 61.6928 | 1.4211e-13 | -0.0026667 | 0.0016666 | 0.065896 | -0.0060339 | 0.062276 | -0.013659 | -0.0026725 | -0.0012777 | 0.070006 | 0.015827 | 0.063412 | -61.7797 | -0.007751 | -61.9342 | 61.691 | 61.4862 | 61.6143 | -61.9243 | -61.8482 | 0.000359 | -61.9101 | 61.5371 | 61.6692 | 61.0543 | -62.111 | 0.001942 | -0.001847 | 0.14655 | -0.007962 | -0.009904 | -0.20665 | -0.078527 | -0.1847 | -0.15574 | 0.078105 | 0.016127 | 0.20082 | -0.023642 | -0.63855 | 123.6172 | 123.4124 | 123.5406 | 61.9185 | -123.6171 | 123.4633 | 123.5954 | 122.9805 | 61.9266 | -123.8038
180.2188 | 123.7289 | -61.8896 | 61.7798 | 1.4211e-13 | -0.0026667 | 0.0016666 | 0.065682 | -0.0058203 | 0.062276 | -0.006028 | -0.0024589 | -0.0014913 | 0.070006 | 0.016254 | 0.063412 | -61.7797 | 0.001407 | -61.9388 | 61.7001 | 61.4907 | 61.6143 | -61.9243 | -61.8527 | 0.000359 | -61.9193 | 61.5325 | 61.6692 | 61.0588 | -62.111 | -0.03468 | -0.079665 | 0.10993 | -0.049162 | -0.014482 | -0.28905 | -0.1655 | -0.22132 | -0.24729 | 0.036904 | -0.029652 | 0.19167 | -0.11062 | -0.72095 | 123.5898 | 123.3804 | 123.5039 | 61.8911 | -123.7041 | 123.4221 | 123.5588 | 122.9485 | 61.89 | -123.8908
181.9062 | 123.7381 | -61.9354 | 61.7706 | 1.4211e-13 | -0.0028803 | 0.002094 | 0.066109 | -0.0056065 | 0.06249 | 0.0092325 | -0.0024589 | -0.0014913 | 0.070006 | 0.015613 | 0.062985 | -61.7797 | -0.003172 | -61.9342 | 61.691 | 61.4724 | 61.6143 | -61.9335 | -61.8573 | -0.013377 | -61.9101 | 61.5371 | 61.6646 | 61.0451 | -62.1064 | 0.001939 | -0.079667 | 0.15571 | 0.001193 | -0.000746 | -0.29821 | -0.15635 | -0.17096 | -0.23356 | 0.078102 | 0.025282 | 0.19625 | -0.10604 | -0.72553 | 123.6264 | 123.4078 | 123.5497 | 61.9323 | -123.7041 | 123.4725 | 123.6 | 122.9805 | 61.922 | -123.877
183.5781 | 123.7518 | -61.9171 | 61.7752 | 1.4211e-13 | -0.0028803 | 0.0016666 | 0.065896 | -0.0058203 | 0.062276 | -0.021289 | -0.0024589 | -0.0012777 | 0.069792 | 0.015827 | 0.063412 | -61.7843 | -0.007751 | -61.9297 | 61.6955 | 61.4862 | 61.6097 | -61.9197 | -61.8527 | -0.008798 | -61.9101 | 61.5371 | 61.6646 | 61.0543 | -62.1064 | -0.002635 | -0.079666 | 0.13282 | -0.01254 | -0.009905 | -0.28905 | -0.1655 | -0.18927 | -0.23814 | 0.06437 | 0.006971 | 0.19625 | -0.11062 | -0.72095 | 123.6127 | 123.4033 | 123.5268 | 61.9094 | -123.695 | 123.4542 | 123.5817 | 122.9714 | 61.9083 | -123.8816
185.25 | 123.8434 | -61.908 | 61.7157 | 1.4211e-13 | -0.0026667 | 0.0018804 | 0.066109 | -0.0060339 | 0.062063 | -0.013659 | -0.0026725 | -0.0014913 | 0.070006 | 0.01604 | 0.062985 | -61.7797 | 0.001407 | -61.9342 | 61.691 | 61.477 | 61.6189 | -61.9289 | -61.8482 | -0.00422 | -61.9101 | 61.5325 | 61.6646 | 61.0543 | -62.1064 | -0.020948 | -0.024735 | 0.12824 | -0.026273 | -0.005325 | -0.2387 | -0.096836 | -0.19843 | -0.18321 | 0.059794 | -0.002184 | 0.19625 | -0.051109 | -0.66144 | 123.5989 | 123.385 | 123.5268 | 61.9094 | -123.6446 | 123.4405 | 123.5725 | 122.9622 | 61.9037 | -123.8221
186.9375 | 123.8159 | -61.9308 | 61.6837 | 1.4211e-13 | -0.0030939 | 0.002094 | 0.066109 | -0.0058203 | 0.062704 | 0.0016025 | -0.0028861 | -0.0012777 | 0.069792 | 0.01604 | 0.062985 | -61.7797 | -0.007751 | -61.9342 | 61.691 | 61.477 | 61.6143 | -61.9335 | -61.8527 | -0.008798 | -61.9101 | 61.5325 | 61.6554 | 61.0497 | -62.1018 | -0.002639 | 0.007308 | 0.15113 | -0.003385 | -0.000746 | -0.20666 | -0.069372 | -0.17096 | -0.15116 | 0.078103 | 0.020704 | 0.19167 | -0.028223 | -0.63398 | 123.6218 | 123.4078 | 123.5451 | 61.9231 | -123.6171 | 123.4633 | 123.5863 | 122.9805 | 61.922 | -123.7855
188.6094 | 123.7701 | -61.8851 | 61.7523 | 1.4211e-13 | -0.0028803 | 0.0016666 | 0.065682 | -0.0058203 | 0.062276 | -0.006028 | -0.0028861 | -0.0014913 | 0.07022 | 0.01604 | 0.063412 | -61.7797 | 0.001407 | -61.9297 | 61.6864 | 61.4724 | 61.6051 | -61.9152 | -61.8527 | -0.013377 | -61.9056 | 61.5325 | 61.6692 | 61.0497 | -62.1064 | -0.030099 | -0.065934 | 0.10535 | -0.044583 | -0.014484 | -0.2799 | -0.14719 | -0.22132 | -0.21983 | 0.032327 | -0.020493 | 0.20082 | -0.083151 | -0.70264 | 123.5715 | 123.3575 | 123.4902 | 61.8865 | -123.6675 | 123.4176 | 123.5542 | 122.9348 | 61.8717 | -123.8587
190.2969 | 123.8709 | -61.9263 | 61.6699 | 1.4211e-13 | -0.0030939 | 0.0016666 | 0.066109 | -0.0056065 | 0.06249 | -0.013659 | -0.0026725 | -0.0019187 | 0.070433 | 0.015613 | 0.063198 | -61.7751 | -0.007751 | -61.9297 | 61.6864 | 61.477 | 61.6005 | -61.9243 | -61.8482 | -0.00422 | -61.9056 | 61.5188 | 61.66 | 61.0497 | -62.1018 | 0.001942 | 0.016463 | 0.15113 | -0.003384 | -0.005326 | -0.19292 | -0.069374 | -0.17554 | -0.15117 | 0.078105 | 0.020706 | 0.19625 | -0.009911 | -0.62024 | 123.6127 | 123.4033 | 123.5268 | 61.9185 | -123.5943 | 123.445 | 123.5863 | 122.9759 | 61.9221 | -123.7717
191.9844 | 123.8571 | -61.9217 | 61.6699 | 1.4211e-13 | -0.0030939 | 0.0018804 | 0.066109 | -0.0058203 | 0.062276 | -0.006028 | -0.0028861 | -0.0014913 | 0.070006 | 0.01604 | 0.063412 | -61.7751 | 0.001407 | -61.9388 | 61.691 | 61.477 | 61.6005 | -61.9152 | -61.8482 | -0.00422 | -61.9056 | 61.5188 | 61.6692 | 61.0497 | -62.1018 | 0.006522 | 0.021041 | 0.14655 | -0.017118 | -0.02364 | -0.19292 | -0.069374 | -0.18012 | -0.15117 | 0.073527 | 0.016128 | 0.19625 | -0.000754 | -0.62024 | 123.6127 | 123.3987 | 123.5222 | 61.9231 | -123.5851 | 123.4404 | 123.5909 | 122.9714 | 61.9175 | -123.7717
193.7031 | 123.8754 | -61.8896 | 61.6882 | 1.4211e-13 | -0.0028803 | 0.002094 | 0.066323 | -0.0060339 | 0.062063 | -0.006028 | -0.0026725 | -0.0012777 | 0.070006 | 0.01604 | 0.063198 | -61.7751 | -0.012329 | -61.9297 | 61.6864 | 61.477 | 61.6097 | -61.9152 | -61.8482 | -0.008798 | -61.9056 | 61.5325 | 61.6646 | 61.0405 | -62.1064 | -0.025522 | -0.001847 | 0.11451 | -0.040006 | -0.014484 | -0.21123 | -0.078527 | -0.21674 | -0.15574 | 0.041483 | -0.015916 | 0.20082 | -0.023643 | -0.64771 | 123.576 | 123.3666 | 123.4994 | 61.8773 | -123.6034 | 123.4221 | 123.5542 | 122.9302 | 61.8809 | -123.7946
195.375 | 123.7335 | -61.9308 | 61.7477 | 1.4211e-13 | -0.0030939 | 0.0016666 | 0.066323 | -0.0058203 | 0.062063 | -0.013659 | -0.0026725 | -0.0014913 | 0.07022 | 0.016254 | 0.062985 | -61.7751 | -0.016908 | -61.9297 | 61.6864 | 61.477 | 61.6097 | -61.9152 | -61.8482 | -0.017956 | -61.9101 | 61.5325 | 61.66 | 61.0451 | -62.1018 | 0.015677 | -0.061357 | 0.15571 | 0.001193 | -0.014484 | -0.27074 | -0.13804 | -0.17096 | -0.21525 | 0.082682 | 0.020704 | 0.19167 | -0.087731 | -0.70264 | 123.6172 | 123.4078 | 123.5406 | 61.9139 | -123.6629 | 123.4633 | 123.5909 | 122.9759 | 61.9129 | -123.8496
197.1875 | 123.8709 | -61.9171 | 61.6608 | 1.4211e-13 | -0.0033077 | 0.0018804 | 0.065896 | -0.0058203 | 0.062276 | -0.006028 | -0.0024589 | -0.0014913 | 0.070006 | 0.016254 | 0.062985 | -61.7706 | -0.007751 | -61.9297 | 61.6818 | 61.4633 | 61.6051 | -61.9152 | -61.8436 | 0.004938 | -61.8964 | 61.5279 | 61.66 | 61.0497 | -62.1018 | 0.001944 | 0.02104 | 0.14655 | -0.01254 | -0.014484 | -0.1975 | -0.055641 | -0.1847 | -0.13285 | 0.073528 | 0.020708 | 0.2054 | -0.000756 | -0.61109 | 123.5989 | 123.3804 | 123.5222 | 61.9094 | -123.5759 | 123.445 | 123.5771 | 122.9668 | 61.9221 | -123.7626
198.9375 | 123.7656 | -61.8851 | 61.7844 | 1.4211e-13 | -0.0033077 | 0.0023076 | 0.066323 | -0.0060339 | 0.062063 | -0.013659 | -0.0024589 | -0.0010641 | 0.069792 | 0.016468 | 0.063198 | -61.7706 | -0.003172 | -61.9297 | 61.691 | 61.4633 | 61.6005 | -61.9106 | -61.8344 | -0.00422 | -61.901 | 61.5188 | 61.66 | 61.0451 | -62.111 | -0.02552 | -0.0934 | 0.11451 | -0.044583 | -0.019063 | -0.3211 | -0.18381 | -0.2259 | -0.26561 | 0.050642 | -0.015914 | 0.20998 | -0.12435 | -0.73926 | 123.576 | 123.3483 | 123.4856 | 61.8819 | -123.695 | 123.4038 | 123.5451 | 122.9302 | 61.8809 | -123.8953
200.7031 | 123.7198 | -61.908 | 61.7477 | 1.4211e-13 | -0.0033077 | 0.0018804 | 0.065896 | -0.0056065 | 0.062276 | -0.006028 | -0.0024589 | -0.0017051 | 0.070006 | 0.01604 | 0.063412 | -61.7797 | -0.003172 | -61.9297 | 61.6864 | 61.4678 | 61.6051 | -61.9152 | -61.839 | -0.00422 | -61.901 | 61.5233 | 61.66 | 61.0451 | -62.1018 | -0.007211 | -0.061357 | 0.12824 | -0.021695 | -0.014484 | -0.2799 | -0.14262 | -0.19385 | -0.22441 | 0.068951 | 0.006974 | 0.20082 | -0.087731 | -0.70264 | 123.5943 | 123.3758 | 123.5131 | 61.9048 | -123.6629 | 123.4313 | 123.568 | 122.9531 | 61.9037 | -123.8496
202.4062 | 123.7564 | -61.8896 | 61.7294 | 1.4211e-13 | -0.0033077 | 0.002094 | 0.065896 | -0.0053929 | 0.062276 | -0.006028 | -0.0026725 | -0.0014913 | 0.07022 | 0.016254 | 0.063412 | -61.766 | -0.003172 | -61.9297 | 61.6772 | 61.4633 | 61.6005 | -61.9152 | -61.839 | -0.00422 | -61.8918 | 61.5188 | 61.6646 | 61.0359 | -62.0972 | -0.025522 | -0.052203 | 0.12367 | -0.040006 | -0.014484 | -0.26617 | -0.12888 | -0.20758 | -0.21067 | 0.05064 | -0.00218 | 0.2054 | -0.064842 | -0.69349 | 123.5669 | 123.3529 | 123.4902 | 61.8865 | -123.6446 | 123.4084 | 123.5542 | 122.9256 | 61.8854 | -123.8267
204.1562 | 123.7244 | -61.9263 | 61.7523 | 1.4211e-13 | -0.0030939 | 0.0018804 | 0.065896 | -0.0056065 | 0.06249 | 0.0016025 | -0.0024589 | -0.0012777 | 0.069792 | 0.016254 | 0.063198 | -61.766 | -0.012329 | -61.9205 | 61.6772 | 61.477 | 61.5914 | -61.9197 | -61.8344 | 0.000359 | -61.901 | 61.5233 | 61.66 | 61.0451 | -62.1018 | 0.006521 | -0.075091 | 0.16029 | 0.005773 | -0.000748 | -0.27532 | -0.16093 | -0.17554 | -0.22898 | 0.091841 | 0.025285 | 0.20082 | -0.092308 | -0.70722 | 123.6035 | 123.4033 | 123.5177 | 61.9139 | -123.6721 | 123.4496 | 123.5863 | 122.9714 | 61.9266 | -123.8541
205.9062 | 123.8205 | -61.8942 | 61.702 | 1.4211e-13 | -0.0030939 | 0.0018804 | 0.065896 | -0.0060339 | 0.062276 | -0.006028 | -0.0028861 | -0.0014913 | 0.069792 | 0.016468 | 0.063198 | -61.7614 | -0.007751 | -61.9297 | 61.6726 | 61.4633 | 61.6005 | -61.906 | -61.8253 | 0.000359 | -61.8964 | 61.5279 | 61.6692 | 61.0268 | -62.1018 | -0.011786 | -0.029315 | 0.13282 | -0.035428 | -0.023642 | -0.2387 | -0.10142 | -0.20758 | -0.17405 | 0.068954 | -0.00218 | 0.2054 | -0.032797 | -0.67518 | 123.5669 | 123.3575 | 123.4948 | 61.8865 | -123.608 | 123.4221 | 123.5634 | 122.921 | 61.8946 | -123.8038
207.5938 | 123.7473 | -61.9034 | 61.7477 | 1.4211e-13 | -0.0030939 | 0.002094 | 0.066109 | -0.0060339 | 0.06249 | 0.0016025 | -0.0026725 | -0.0012777 | 0.069792 | 0.01604 | 0.063626 | -61.7706 | -0.007751 | -61.9251 | 61.6818 | 61.4678 | 61.6051 | -61.9014 | -61.839 | -0.00422 | -61.901 | 61.5188 | 61.66 | 61.0359 | -62.0972 | 0.001948 | -0.065935 | 0.13282 | -0.021694 | -0.023642 | -0.2799 | -0.14262 | -0.19385 | -0.22899 | 0.064373 | 0.002396 | 0.19625 | -0.087731 | -0.7118 | 123.5852 | 123.3712 | 123.5085 | 61.8956 | -123.6492 | 123.4221 | 123.5634 | 122.9393 | 61.8992 | -123.845
209.3281 | 123.7381 | -61.8851 | 61.7661 | 1.4211e-13 | -0.0028803 | 0.0023076 | 0.065682 | -0.0056065 | 0.06249 | -0.013659 | -0.0022453 | -0.0014913 | 0.069792 | 0.016254 | 0.063412 | -61.7614 | -0.012329 | -61.9251 | 61.6681 | 61.4541 | 61.6005 | -61.906 | -61.8253 | -0.00422 | -61.901 | 61.5188 | 61.66 | 61.0451 | -62.0972 | -0.020941 | -0.09798 | 0.12367 | -0.040004 | -0.019063 | -0.31195 | -0.1655 | -0.21216 | -0.2473 | 0.059799 | -0.015914 | 0.19625 | -0.10604 | -0.72095 | 123.5531 | 123.3392 | 123.4856 | 61.8727 | -123.6721 | 123.4038 | 123.5451 | 122.9302 | 61.8809 | -123.8633
211.0156 | 123.8434 | -61.8668 | 61.6837 | 1.4211e-13 | -0.0030939 | 0.0018804 | 0.065896 | -0.0060339 | 0.06249 | 0.0016025 | -0.0024589 | -0.0014913 | 0.070006 | 0.01604 | 0.063412 | -61.7614 | -0.007751 | -61.9205 | 61.6772 | 61.4587 | 61.6005 | -61.9106 | -61.8344 | -0.008798 | -61.8918 | 61.5142 | 61.6463 | 61.0359 | -62.0972 | -0.043831 | -0.006427 | 0.10535 | -0.053737 | -0.009906 | -0.22497 | -0.083107 | -0.23047 | -0.16948 | 0.032331 | -0.025068 | 0.2054 | -0.03738 | -0.64771 | 123.544 | 123.3254 | 123.4673 | 61.859 | -123.5942 | 123.3809 | 123.513 | 122.9027 | 61.858 | -123.7809
212.7656 | 123.7152 | -61.9217 | 61.7157 | 1.4211e-13 | -0.0030939 | 0.002094 | 0.066109 | -0.0056065 | 0.062063 | -0.006028 | -0.0026725 | -0.0014913 | 0.070006 | 0.016681 | 0.063626 | -61.7614 | -0.007751 | -61.9159 | 61.6681 | 61.4678 | 61.6005 | -61.9106 | -61.8253 | 0.000359 | -61.8964 | 61.505 | 61.66 | 61.0314 | -62.1018 | 0.011101 | -0.047626 | 0.16029 | 0.005773 | -0.005328 | -0.24786 | -0.11515 | -0.18012 | -0.21068 | 0.09642 | 0.025286 | 0.2054 | -0.055687 | -0.68433 | 123.5898 | 123.3895 | 123.5222 | 61.9139 | -123.6263 | 123.4267 | 123.5817 | 122.9531 | 61.9221 | -123.8175
214.5156 | 123.8342 | -61.908 | 61.6745 | 1.4211e-13 | -0.0030939 | 0.0016666 | 0.065682 | -0.0058203 | 0.062063 | -0.006028 | -0.0022453 | -0.0014913 | 0.070006 | 0.016468 | 0.063412 | -61.766 | -0.007751 | -61.9113 | 61.6726 | 61.4587 | 61.6005 | -61.9106 | -61.8299 | 0.000359 | -61.8872 | 61.5142 | 61.6509 | 61.0359 | -62.1018 | -0.002632 | -0.00185 | 0.14198 | -0.003382 | -0.00075 | -0.21582 | -0.073952 | -0.19385 | -0.16032 | 0.078109 | 0.02071 | 0.21456 | -0.023646 | -0.63856 | 123.5806 | 123.3666 | 123.5085 | 61.9002 | -123.5851 | 123.4221 | 123.5588 | 122.9439 | 61.9083 | -123.7763
216.25 | 123.7976 | -61.9308 | 61.6425 | 1.4211e-13 | -0.0033077 | 0.002094 | 0.065896 | -0.0060339 | 0.062063 | -0.006028 | -0.0030999 | -0.0014913 | 0.07022 | 0.016254 | 0.063412 | -61.7568 | -0.003172 | -61.9159 | 61.6772 | 61.4724 | 61.596 | -61.9106 | -61.8253 | -0.00422 | -61.8964 | 61.5142 | 61.6509 | 61.0314 | -62.0927 | 0.020256 | 0.034772 | 0.17402 | 0.014928 | -0.005328 | -0.17004 | -0.046487 | -0.1618 | -0.12828 | 0.10558 | 0.034441 | 0.19624 | 0.008398 | -0.61109 | 123.6081 | 123.4033 | 123.5268 | 61.9277 | -123.553 | 123.445 | 123.5817 | 122.9622 | 61.9266 | -123.7351
218 | 123.8251 | -61.8942 | 61.6379 | 1.4211e-13 | -0.0030939 | 0.0016666 | 0.066109 | -0.0060339 | 0.06249 | 0.0016025 | -0.0022453 | -0.0019187 | 0.07022 | 0.016254 | 0.063626 | -61.7614 | -0.007751 | -61.9113 | 61.6772 | 61.4633 | 61.596 | -61.9106 | -61.8299 | -0.008798 | -61.8918 | 61.5142 | 61.6463 | 61.0268 | -62.0927 | -0.016365 | 0.03935 | 0.13282 | -0.017115 | -0.00075 | -0.17462 | -0.041909 | -0.19842 | -0.1237 | 0.064376 | 0.002398 | 0.20082 | 0.008397 | -0.61109 | 123.5715 | 123.3575 | 123.4902 | 61.8865 | -123.5485 | 123.4084 | 123.5405 | 122.921 | 61.8854 | -123.7305
219.6875 | 123.7152 | -61.8896 | 61.734 | 1.4211e-13 | -0.0028803 | 0.002094 | 0.065896 | -0.0056065 | 0.062276 | 0.0016025 | -0.0026725 | -0.0014913 | 0.07022 | 0.016468 | 0.063626 | -61.7614 | -0.012329 | -61.9068 | 61.6635 | 61.4541 | 61.596 | -61.9014 | -61.8299 | -0.013377 | -61.8872 | 61.5142 | 61.66 | 61.0359 | -62.0972 | -0.011785 | -0.070516 | 0.12824 | -0.017114 | -0.005329 | -0.2799 | -0.13804 | -0.20758 | -0.21983 | 0.059798 | 0.002399 | 0.20998 | -0.073998 | -0.69806 | 123.5531 | 123.3438 | 123.4856 | 61.8773 | -123.6354 | 123.4038 | 123.5497 | 122.9256 | 61.8763 | -123.8312
221.4375 | 123.7015 | -61.8851 | 61.734 | 1.4211e-13 | -0.0028803 | 0.001453 | 0.066109 | -0.0058203 | 0.062276 | -0.006028 | -0.0026725 | -0.0017051 | 0.069792 | 0.016254 | 0.062985 | -61.7522 | -0.007751 | -61.9068 | 61.6726 | 61.4541 | 61.596 | -61.8969 | -61.8299 | 0.000359 | -61.8872 | 61.5096 | 61.6463 | 61.0359 | -62.0881 | -0.011783 | -0.061359 | 0.13282 | -0.021691 | -0.009908 | -0.2799 | -0.13804 | -0.203 | -0.22441 | 0.055221 | -0.002178 | 0.20082 | -0.087734 | -0.69806 | 123.5577 | 123.3392 | 123.481 | 61.8773 | -123.6309 | 123.3947 | 123.5313 | 122.921 | 61.8854 | -123.8221
223.125 | 123.7381 | -61.9125 | 61.6653 | 1.4211e-13 | -0.0033077 | 0.0018804 | 0.066109 | -0.0062475 | 0.062063 | -0.013659 | -0.0024589 | -0.0012777 | 0.07022 | 0.016254 | 0.062985 | -61.7477 | -0.003172 | -61.9159 | 61.6635 | 61.4587 | 61.5822 | -61.9014 | -61.8207 | -0.00422 | -61.8872 | 61.5142 | 61.6509 | 61.0314 | -62.0927 | 0.011104 | -0.001851 | 0.16487 | -0.003382 | -0.014486 | -0.20666 | -0.083111 | -0.18011 | -0.15117 | 0.091844 | 0.025288 | 0.2054 | -0.01449 | -0.63398 | 123.576 | 123.3712 | 123.4948 | 61.9094 | -123.5668 | 123.4267 | 123.5634 | 122.9439 | 61.9083 | -123.758
224.8906 | 123.7747 | -61.9125 | 61.6516 | 1.4211e-13 | -0.0035213 | 0.0018804 | 0.065896 | -0.0056065 | 0.062276 | -0.006028 | -0.0026725 | -0.0014913 | 0.07022 | 0.016468 | 0.062985 | -61.7568 | -0.003172 | -61.9113 | 61.6772 | 61.4633 | 61.5868 | -61.8969 | -61.8253 | -0.008798 | -61.8872 | 61.5142 | 61.6463 | 61.0268 | -62.0927 | 0.015683 | 0.025617 | 0.15571 | 0.001196 | -0.014487 | -0.18835 | -0.064799 | -0.18011 | -0.13743 | 0.087265 | 0.025288 | 0.2054 | -0.005336 | -0.62483 | 123.5898 | 123.3758 | 123.4993 | 61.9094 | -123.5485 | 123.4267 | 123.5588 | 122.9393 | 61.9037 | -123.7443
226.5625 | 123.7381 | -61.8576 | 61.734 | 1.4211e-13 | -0.0035213 | 0.002094 | 0.066109 | -0.0058203 | 0.062063 | 0.0016025 | -0.0024589 | -0.0014913 | 0.070006 | 0.016895 | 0.062985 | -61.7522 | -0.012329 | -61.9113 | 61.6726 | 61.4495 | 61.596 | -61.8969 | -61.8161 | -0.008798 | -61.8872 | 61.505 | 61.6417 | 61.0222 | -62.0927 | -0.039249 | -0.061359 | 0.10536 | -0.053736 | -0.014487 | -0.28448 | -0.13804 | -0.23505 | -0.22899 | 0.041491 | -0.029644 | 0.2054 | -0.092313 | -0.7118 | 123.5303 | 123.3071 | 123.4536 | 61.8453 | -123.6309 | 123.3626 | 123.4993 | 122.8798 | 61.8488 | -123.8267
228.2969 | 123.7473 | -61.9034 | 61.7065 | 1.4211e-13 | -0.0030939 | 0.0016666 | 0.065896 | -0.0058203 | 0.062276 | -0.006028 | -0.0024589 | -0.0017051 | 0.069792 | 0.016468 | 0.062985 | -61.7431 | -0.012329 | -61.9022 | 61.6635 | 61.4633 | 61.5868 | -61.8923 | -61.8253 | -0.00422 | -61.8781 | 61.505 | 61.6463 | 61.0314 | -62.0835 | 0.011106 | -0.04305 | 0.16029 | 0.001197 | -0.009909 | -0.24328 | -0.11973 | -0.18011 | -0.20152 | 0.078109 | 0.025289 | 0.2054 | -0.060268 | -0.67518 | 123.5669 | 123.3666 | 123.4902 | 61.8911 | -123.5988 | 123.4084 | 123.5497 | 122.9347 | 61.8992 | -123.79
230 | 123.7564 | -61.8759 | 61.7157 | 1.4211e-13 | -0.0033077 | 0.0023076 | 0.066109 | -0.0058203 | 0.061849 | 0.0016025 | -0.0024589 | -0.0010641 | 0.07022 | 0.016681 | 0.063198 | -61.7477 | -0.003172 | -61.9113 | 61.6635 | 61.4495 | 61.5914 | -61.8785 | -61.8207 | -0.008798 | -61.8827 | 61.5096 | 61.6463 | 61.0268 | -62.0927 | -0.002623 | -0.052205 | 0.12825 | -0.035425 | -0.032802 | -0.26617 | -0.12431 | -0.21673 | -0.2061 | 0.055223 | -0.006754 | 0.20998 | -0.069423 | -0.68891 | 123.5394 | 123.3254 | 123.4673 | 61.8727 | -123.5942 | 123.3855 | 123.5222 | 122.9027 | 61.8671 | -123.8083
231.75 | 123.8205 | -61.8668 | 61.6425 | 1.4211e-13 | -0.0033077 | 0.002094 | 0.065896 | -0.0060339 | 0.062063 | 0.0016025 | -0.0024589 | -0.0014913 | 0.070006 | 0.016895 | 0.062985 | -61.7431 | -0.007751 | -61.9113 | 61.6681 | 61.4541 | 61.5868 | -61.8923 | -61.8115 | -0.00422 | -61.8735 | 61.505 | 61.6371 | 61.0176 | -62.0835 | -0.025515 | 0.025616 | 0.12367 | -0.044581 | -0.019066 | -0.18835 | -0.055644 | -0.21673 | -0.13744 | 0.055225 | -0.006753 | 0.20998 | -0.005338 | -0.62483 | 123.5348 | 123.3209 | 123.4536 | 61.859 | -123.5347 | 123.3718 | 123.5039 | 122.8844 | 61.8625 | -123.726
233.4375 | 123.761 | -61.8942 | 61.6562 | 1.4211e-13 | -0.0030939 | 0.0016666 | 0.066109 | -0.0058203 | 0.061849 | -0.006028 | -0.0026725 | -0.0014913 | 0.070006 | 0.016681 | 0.062771 | -61.7522 | -0.003172 | -61.9022 | 61.6589 | 61.4541 | 61.6005 | -61.8969 | -61.8207 | -0.00422 | -61.8735 | 61.505 | 61.6371 | 61.0268 | -62.0835 | -0.002628 | 0.002726 | 0.14198 | -0.007958 | -0.00533 | -0.20208 | -0.055641 | -0.18927 | -0.15117 | 0.073533 | 0.020713 | 0.20998 | -0.019071 | -0.6294 | 123.5531 | 123.3483 | 123.4948 | 61.8911 | -123.553 | 123.3992 | 123.5313 | 122.921 | 61.89 | -123.7397
235.1094 | 123.7335 | -61.8622 | 61.7477 | 1.4211e-13 | -0.0030939 | 0.0016666 | 0.065896 | -0.0056065 | 0.061849 | -0.013659 | -0.0024589 | -0.0014913 | 0.070006 | 0.016468 | 0.062985 | -61.7477 | -0.007751 | -61.9068 | 61.6635 | 61.4495 | 61.596 | -61.8923 | -61.8115 | 0.004938 | -61.8781 | 61.5004 | 61.6371 | 61.0268 | -62.0835 | -0.030092 | -0.084249 | 0.11451 | -0.044579 | -0.014487 | -0.29822 | -0.15177 | -0.22131 | -0.2473 | 0.050648 | -0.015909 | 0.2054 | -0.11062 | -0.72096 | 123.5257 | 123.3117 | 123.4582 | 61.8544 | -123.64 | 123.3626 | 123.4993 | 122.889 | 61.8671 | -123.8312
236.8594 | 123.6923 | -61.8668 | 61.7203 | 1.4211e-13 | -0.0030939 | 0.0018804 | 0.066109 | -0.0058203 | 0.062063 | 0.0016025 | -0.0024589 | -0.0014913 | 0.07022 | 0.016895 | 0.063626 | -61.7431 | -0.007751 | -61.8976 | 61.6543 | 61.4495 | 61.5822 | -61.8831 | -61.8161 | -0.00422 | -61.8735 | 61.4959 | 61.6417 | 61.0268 | -62.0835 | -0.016358 | -0.06594 | 0.12367 | -0.030846 | -0.014488 | -0.27075 | -0.13804 | -0.21673 | -0.22441 | 0.050646 | -0.006753 | 0.20998 | -0.07858 | -0.69349 | 123.5211 | 123.3163 | 123.449 | 61.859 | -123.6034 | 123.3626 | 123.5085 | 122.8935 | 61.8625 | -123.8038
238.5625 | 123.793 | -61.8484 | 61.6241 | 1.4211e-13 | -0.0030939 | 0.0018804 | 0.065682 | -0.0060339 | 0.061849 | 0.0016025 | -0.0022453 | -0.0012777 | 0.07022 | 0.016681 | 0.062985 | -61.7385 | -0.012329 | -61.9022 | 61.6543 | 61.4541 | 61.5868 | -61.8923 | -61.8207 | -0.00422 | -61.8735 | 61.505 | 61.6463 | 61.0222 | -62.0789 | -0.043825 | 0.03019 | 0.10994 | -0.053734 | -0.009909 | -0.17004 | -0.037334 | -0.23047 | -0.11913 | 0.027757 | -0.025063 | 0.2054 | 0.022129 | -0.60194 | 123.5028 | 123.3026 | 123.4353 | 61.8361 | -123.5164 | 123.3535 | 123.4947 | 122.8707 | 61.8442 | -123.7031
240.25 | 123.8297 | -61.8851 | 61.6333 | 1.4211e-13 | -0.0030939 | 0.0016666 | 0.065682 | -0.0060339 | 0.062063 | -0.021289 | -0.0024589 | -0.0014913 | 0.070006 | 0.016468 | 0.062771 | -61.7431 | -0.012329 | -61.8976 | 61.6635 | 61.4495 | 61.5868 | -61.8831 | -61.8115 | 0.004938 | -61.8689 | 61.5004 | 61.6463 | 61.0176 | -62.0698 | 0.001953 | 0.030192 | 0.14198 | -0.012535 | -0.014488 | -0.18378 | -0.046489 | -0.18469 | -0.13286 | 0.073536 | 0.016137 | 0.20082 | 0.012974 | -0.61567 | 123.5486 | 123.3346 | 123.4719 | 61.8727 | -123.5164 | 123.3855 | 123.5313 | 122.9027 | 61.89 | -123.7031
242.0156 | 123.7427 | -61.8988 | 61.6196 | 1.4211e-13 | -0.0035213 | 0.0018804 | 0.065682 | -0.0062475 | 0.062063 | -0.013659 | -0.0026725 | -0.0014913 | 0.070006 | 0.016681 | 0.062771 | -61.7385 | -0.007751 | -61.8976 | 61.6681 | 61.4495 | 61.5914 | -61.8923 | -61.8161 | -0.00422 | -61.8781 | 61.505 | 61.6417 | 61.0176 | -62.0789 | 0.006529 | 0.048504 | 0.16029 | 0.001198 | -0.005331 | -0.17004 | -0.028178 | -0.18011 | -0.11455 | 0.08269 | 0.020712 | 0.20082 | 0.022128 | -0.60194 | 123.5669 | 123.3483 | 123.4902 | 61.8911 | -123.5118 | 123.4038 | 123.5405 | 122.9164 | 61.8946 | -123.6985
243.7656 | 123.761 | -61.8988 | 61.647 | 1.4211e-13 | -0.0033077 | 0.0016666 | 0.065896 | -0.0058203 | 0.061849 | -0.006028 | -0.0024589 | -0.0014913 | 0.07022 | 0.017109 | 0.062771 | -61.7431 | -0.007751 | -61.9022 | 61.6589 | 61.4495 | 61.5868 | -61.8877 | -61.8207 | 0.000359 | -61.8689 | 61.4959 | 61.6417 | 61.0176 | -62.0789 | 0.011108 | 0.011881 | 0.15571 | -0.00338 | -0.014488 | -0.19751 | -0.060222 | -0.18011 | -0.15117 | 0.078111 | 0.02987 | 0.20998 | -0.005338 | -0.6294 | 123.5577 | 123.3483 | 123.4856 | 61.8911 | -123.5347 | 123.3947 | 123.5405 | 122.9164 | 61.8992 | -123.7259
245.4531 | 123.6649 | -61.8851 | 61.7065 | 1.4211e-13 | -0.0033077 | 0.0016666 | 0.065896 | -0.0060339 | 0.061849 | -0.006028 | -0.0028861 | -0.0012777 | 0.070433 | 0.016681 | 0.063198 | -61.7385 | -0.007751 | -61.8976 | 61.6589 | 61.4495 | 61.5777 | -61.8831 | -61.8161 | -0.00422 | -61.8689 | 61.4959 | 61.6371 | 61.0176 | -62.0743 | 0.001953 | -0.047628 | 0.14656 | -0.012535 | -0.014488 | -0.25702 | -0.12889 | -0.18926 | -0.21068 | 0.068957 | 0.016137 | 0.2054 | -0.069425 | -0.68891 | 123.544 | 123.3346 | 123.4627 | 61.8773 | -123.5897 | 123.3809 | 123.5222 | 122.9027 | 61.8809 | -123.7809
247.1406 | 123.7473 | -61.8851 | 61.6104 | 1.4211e-13 | -0.0033077 | 0.0016666 | 0.066109 | -0.0062475 | 0.062276 | 0.0016025 | -0.0026725 | -0.0017051 | 0.070006 | 0.016895 | 0.062771 | -61.7385 | -0.007751 | -61.9022 | 61.6543 | 61.4541 | 61.5868 | -61.8877 | -61.8024 | 0.000359 | -61.8735 | 61.4959 | 61.628 | 61.0131 | -62.0789 | -0.002625 | 0.043923 | 0.14656 | -0.017113 | -0.014488 | -0.15631 | -0.023601 | -0.19384 | -0.11455 | 0.082693 | 0.011558 | 0.2054 | 0.017548 | -0.59736 | 123.5394 | 123.3392 | 123.4719 | 61.8773 | -123.4981 | 123.3809 | 123.513 | 122.8981 | 61.8854 | -123.6893
248.8906 | 123.793 | -61.8851 | 61.6333 | 1.4211e-13 | -0.0030939 | 0.0016666 | 0.065682 | -0.0062475 | 0.062276 | 0.0016025 | -0.0026725 | -0.0017051 | 0.070006 | 0.016681 | 0.062985 | -61.7385 | 0.001407 | -61.893 | 61.6498 | 61.4404 | 61.5777 | -61.8785 | -61.807 | 0.000359 | -61.8644 | 61.4959 | 61.6463 | 61.0131 | -62.0835 | 0.006532 | 0.016457 | 0.14656 | -0.007956 | -0.014488 | -0.19293 | -0.055646 | -0.19842 | -0.13744 | 0.078114 | 0.020716 | 0.21914 | 0.012974 | -0.62025 | 123.5348 | 123.3254 | 123.4627 | 61.8865 | -123.5118 | 123.3809 | 123.5313 | 122.8981 | 61.8854 | -123.7168
250.6406 | 123.642 | -61.8713 | 61.702 | 1.4211e-13 | -0.0033077 | 0.002094 | 0.065682 | -0.0058203 | 0.062063 | -0.006028 | -0.0028861 | -0.0014913 | 0.070006 | 0.017109 | 0.063198 | -61.7339 | -0.003172 | -61.9022 | 61.6589 | 61.4495 | 61.5731 | -61.8694 | -61.807 | -0.00422 | -61.8644 | 61.4913 | 61.6325 | 61.0222 | -62.0743 | 0.001957 | -0.04305 | 0.1374 | -0.030846 | -0.032803 | -0.25244 | -0.12889 | -0.203 | -0.21068 | 0.064381 | 0.006983 | 0.20998 | -0.069426 | -0.67976 | 123.5303 | 123.3209 | 123.4444 | 61.8682 | -123.5713 | 123.3626 | 123.5039 | 122.8935 | 61.8671 | -123.7763
252.3125 | 123.6969 | -61.8851 | 61.6837 | 1.4211e-13 | -0.0035213 | 0.0016666 | 0.065896 | -0.0058203 | 0.061849 | 0.016863 | -0.0026725 | -0.0017051 | 0.07022 | 0.016895 | 0.062985 | -61.7339 | -0.003172 | -61.8884 | 61.6498 | 61.4404 | 61.5822 | -61.874 | -61.807 | -0.00422 | -61.8689 | 61.4959 | 61.6371 | 61.0085 | -62.0789 | 0.011111 | -0.033897 | 0.15114 | -0.003378 | -0.014489 | -0.24329 | -0.10142 | -0.19384 | -0.18779 | 0.078114 | 0.016137 | 0.20998 | -0.046537 | -0.67518 | 123.5348 | 123.3254 | 123.4673 | 61.8819 | -123.5576 | 123.3809 | 123.5222 | 122.8935 | 61.8809 | -123.7626
254 | 123.7793 | -61.8622 | 61.6562 | 1.4211e-13 | -0.0033077 | 0.0018804 | 0.066323 | -0.0060339 | 0.062063 | -0.006028 | -0.0022453 | -0.0012777 | 0.070006 | 0.016681 | 0.062985 | -61.7248 | -0.003172 | -61.893 | 61.6543 | 61.4449 | 61.5914 | -61.8877 | -61.8024 | -0.008798 | -61.8644 | 61.4867 | 61.6325 | 61.0131 | -62.0743 | -0.025513 | -0.001853 | 0.13741 | -0.030844 | -0.005331 | -0.21124 | -0.064799 | -0.21215 | -0.16948 | 0.059805 | -0.002172 | 0.20998 | -0.02365 | -0.64314 | 123.5165 | 123.3071 | 123.4536 | 61.859 | -123.5439 | 123.3489 | 123.4947 | 122.8752 | 61.8534 | -123.7305
255.75 | 123.7061 | -61.8622 | 61.6928 | 1.4211e-13 | -0.0033077 | 0.0016666 | 0.066109 | -0.0058203 | 0.062063 | -0.006028 | -0.0024589 | -0.0017051 | 0.069792 | 0.017322 | 0.062985 | -61.7339 | -0.007751 | -61.8976 | 61.6589 | 61.4404 | 61.5685 | -61.8785 | -61.8024 | -0.008798 | -61.8644 | 61.4913 | 61.6371 | 61.0131 | -62.0789 | -0.016356 | -0.033895 | 0.12825 | -0.035423 | -0.019067 | -0.25244 | -0.12431 | -0.21673 | -0.20153 | 0.059805 | -0.002172 | 0.21456 | -0.055692 | -0.67976 | 123.5211 | 123.3026 | 123.4307 | 61.8544 | -123.5713 | 123.3535 | 123.4993 | 122.8752 | 61.8534 | -123.7717
257.4375 | 123.6511 | -61.8851 | 61.7065 | 1.4211e-13 | -0.0033077 | 0.0016666 | 0.065682 | -0.0060339 | 0.062063 | -0.006028 | -0.0026725 | -0.0010641 | 0.070006 | 0.016681 | 0.062985 | -61.7339 | -0.003172 | -61.9022 | 61.6543 | 61.4404 | 61.5777 | -61.8785 | -61.7978 | -0.00422 | -61.8598 | 61.4867 | 61.6325 | 61.0085 | -62.0698 | 0.006532 | -0.052207 | 0.15114 | -0.017113 | -0.023645 | -0.26618 | -0.12889 | -0.18469 | -0.21984 | 0.087272 | 0.025294 | 0.20998 | -0.074004 | -0.69807 | 123.5394 | 123.3254 | 123.4627 | 61.8819 | -123.5851 | 123.3718 | 123.5176 | 122.8935 | 61.8809 | -123.7763
259.1094 | 123.761 | -61.8622 | 61.6379 | 1.4211e-13 | -0.0033077 | 0.0018804 | 0.065896 | -0.0062475 | 0.062276 | 0.0016025 | -0.0028861 | -0.0017051 | 0.070433 | 0.017109 | 0.062985 | -61.7248 | -0.012329 | -61.8884 | 61.6543 | 61.4449 | 61.5731 | -61.8785 | -61.7978 | -0.013377 | -61.8598 | 61.4867 | 61.6325 | 61.0085 | -62.0652 | -0.016356 | 0.016458 | 0.13741 | -0.026266 | -0.00991 | -0.19293 | -0.064802 | -0.203 | -0.15117 | 0.064384 | 0.002406 | 0.2054 | -0.005339 | -0.62941 | 123.5165 | 123.3071 | 123.4353 | 61.8499 | -123.5164 | 123.3489 | 123.4947 | 122.8707 | 61.8488 | -123.7031
260.8438 | 123.7473 | -61.8484 | 61.6333 | 1.4211e-13 | -0.0033077 | 0.001453 | 0.065682 | -0.0058203 | 0.062063 | 0.0016025 | -0.0028861 | -0.0014913 | 0.070006 | 0.017322 | 0.062771 | -61.7294 | -0.003172 | -61.8793 | 61.6498 | 61.4449 | 61.5777 | -61.8694 | -61.8024 | 0.000359 | -61.8598 | 61.4913 | 61.6325 | 61.0131 | -62.0698 | -0.020931 | 0.016457 | 0.11909 | -0.030843 | -0.009912 | -0.18835 | -0.055646 | -0.22131 | -0.14202 | 0.046072 | -0.011327 | 0.20998 | -0.000762 | -0.62025 | 123.4982 | 123.2934 | 123.4261 | 61.8453 | -123.5027 | 123.3397 | 123.481 | 122.8615 | 61.8488 | -123.7031
262.5938 | 123.6603 | -61.8805 | 61.702 | 1.4211e-13 | -0.0037351 | 0.0018804 | 0.065896 | -0.0062475 | 0.061849 | -0.006028 | -0.0024589 | -0.0014913 | 0.070433 | 0.016895 | 0.062771 | -61.7294 | -0.003172 | -61.8884 | 61.6406 | 61.4312 | 61.5731 | -61.874 | -61.7978 | -0.00422 | -61.8598 | 61.4867 | 61.6234 | 60.9993 | -62.0698 | 0.006533 | -0.061364 | 0.15114 | -0.007956 | -0.014489 | -0.27075 | -0.12889 | -0.18926 | -0.21526 | 0.082694 | 0.020716 | 0.20998 | -0.078583 | -0.70265 | 123.5211 | 123.3117 | 123.4536 | 61.8773 | -123.5759 | 123.3672 | 123.5039 | 122.8798 | 61.8763 | -123.7717
264.2812 | 123.761 | -61.8393 | 61.6425 | 1.4211e-13 | -0.0035213 | 0.0018804 | 0.065468 | -0.0058203 | 0.061849 | 0.0016025 | -0.0026725 | -0.0012777 | 0.070006 | 0.016895 | 0.062985 | -61.7294 | -0.016908 | -61.893 | 61.6452 | 61.4404 | 61.5822 | -61.8648 | -61.8024 | -0.00422 | -61.8598 | 61.4867 | 61.6234 | 61.0039 | -62.0652 | -0.025508 | 0.002724 | 0.10994 | -0.053733 | -0.028225 | -0.20209 | -0.060223 | -0.22588 | -0.15575 | 0.036916 | -0.020483 | 0.2054 | -0.019074 | -0.63856 | 123.4845 | 123.2797 | 123.4215 | 61.8224 | -123.5073 | 123.326 | 123.4627 | 122.8432 | 61.8351 | -123.7076
265.9688 | 123.6145 | -61.8484 | 61.6928 | 1.4211e-13 | -0.0035213 | 0.0018804 | 0.065682 | -0.0058203 | 0.061635 | -0.006028 | -0.0022453 | -0.0014913 | 0.070006 | 0.017109 | 0.062985 | -61.7248 | -0.012329 | -61.8884 | 61.6452 | 61.4312 | 61.5777 | -61.8694 | -61.7978 | -0.008798 | -61.8598 | 61.4867 | 61.6234 | 60.9947 | -62.0743 | -0.020931 | -0.04763 | 0.12367 | -0.039999 | -0.019068 | -0.2616 | -0.11516 | -0.22589 | -0.2061 | 0.050651 | -0.011327 | 0.21456 | -0.069428 | -0.69807 | 123.4936 | 123.2797 | 123.4261 | 61.8361 | -123.5622 | 123.3352 | 123.4718 | 122.8432 | 61.8397 | -123.7671
267.7188 | 123.642 | -61.8576 | 61.7111 | 1.4211e-13 | -0.0035213 | 0.0018804 | 0.065468 | -0.0058203 | 0.061849 | 0.0016025 | -0.0024589 | -0.0014913 | 0.070006 | 0.017322 | 0.062985 | -61.7202 | -0.012329 | -61.8884 | 61.6452 | 61.4312 | 61.5731 | -61.8694 | -61.7932 | -0.00422 | -61.8506 | 61.4867 | 61.6234 | 61.0039 | -62.0606 | -0.011776 | -0.065941 | 0.13741 | -0.030844 | -0.019068 | -0.27991 | -0.13804 | -0.203 | -0.22441 | 0.064384 | 0.006986 | 0.20998 | -0.087739 | -0.70723 | 123.5028 | 123.2888 | 123.4307 | 61.8453 | -123.5805 | 123.3443 | 123.481 | 122.8615 | 61.8534 | -123.7717
269.4062 | 123.7427 | -61.8439 | 61.6287 | 1.4211e-13 | -0.0030939 | 0.0018804 | 0.065255 | -0.0060339 | 0.061422 | 0.0016025 | -0.0024589 | -0.0017051 | 0.070006 | 0.016895 | 0.062771 | -61.7248 | -0.012329 | -61.893 | 61.6406 | 61.4404 | 61.5685 | -61.8694 | -61.7886 | -0.008798 | -61.8506 | 61.4821 | 61.6234 | 61.0039 | -62.0698 | -0.025509 | 0.011878 | 0.11909 | -0.049155 | -0.023646 | -0.18836 | -0.060226 | -0.22589 | -0.14659 | 0.05523 | -0.006747 | 0.21914 | -0.005341 | -0.62483 | 123.4845 | 123.2842 | 123.4124 | 61.8315 | -123.4981 | 123.326 | 123.4673 | 122.8478 | 61.8351 | -123.6985
271.0938 | 123.7518 | -61.8668 | 61.6653 | 1.4211e-13 | -0.0037351 | 0.0018804 | 0.065468 | -0.0060339 | 0.061635 | -0.013659 | -0.0026725 | -0.0014913 | 0.070433 | 0.016895 | 0.062985 | -61.7202 | -0.003172 | -61.8839 | 61.6406 | 61.4266 | 61.5731 | -61.8602 | -61.7932 | 0.000359 | -61.8552 | 61.4821 | 61.6188 | 61.0039 | -62.0743 | 0.006537 | -0.024743 | 0.14656 | -0.017111 | -0.023648 | -0.23871 | -0.092268 | -0.20758 | -0.18322 | 0.073539 | 0.011562 | 0.21914 | -0.046541 | -0.66145 | 123.5074 | 123.2934 | 123.4398 | 61.8636 | -123.5256 | 123.3489 | 123.4856 | 122.8707 | 61.8671 | -123.7397
272.8594 | 123.7381 | -61.8439 | 61.6653 | 1.4211e-13 | -0.0037351 | 0.002094 | 0.065255 | -0.0062475 | 0.061208 | 0.0016025 | -0.0028861 | -0.0017051 | 0.070006 | 0.017536 | 0.062985 | -61.711 | -0.003172 | -61.8793 | 61.6406 | 61.4266 | 61.5685 | -61.8694 | -61.7932 | -0.00422 | -61.8506 | 61.4821 | 61.6142 | 60.9947 | -62.0698 | -0.025509 | -0.024743 | 0.13283 | -0.035421 | -0.009912 | -0.23871 | -0.096847 | -0.22589 | -0.18322 | 0.050651 | -0.006747 | 0.21914 | -0.051119 | -0.67061 | 123.4845 | 123.2705 | 123.4124 | 61.8407 | -123.5347 | 123.326 | 123.4581 | 122.8386 | 61.8397 | -123.7351
274.625 | 123.6877 | -61.8759 | 61.6516 | 1.4211e-13 | -0.0033077 | 0.002094 | 0.065255 | -0.0062475 | 0.061422 | -0.013659 | -0.0026725 | -0.0017051 | 0.070006 | 0.016895 | 0.063198 | -61.711 | -0.016908 | -61.8839 | 61.6406 | 61.4266 | 61.5731 | -61.8694 | -61.7886 | 0.004938 | -61.8506 | 61.4821 | 61.6234 | 61.0039 | -62.056 | 0.006535 | -0.01101 | 0.16487 | -0.007955 | -0.01449 | -0.22498 | -0.078535 | -0.18011 | -0.16948 | 0.087274 | 0.025297 | 0.2054 | -0.028229 | -0.64772 | 123.5165 | 123.3025 | 123.449 | 61.859 | -123.521 | 123.358 | 123.4993 | 122.8798 | 61.8809 | -123.7076
276.3125 | 123.6969 | -61.8759 | 61.6379 | 1.4211e-13 | -0.0037351 | 0.002094 | 0.065255 | -0.0060339 | 0.061849 | -0.006028 | -0.0028861 | -0.0017051 | 0.069792 | 0.017322 | 0.062985 | -61.7156 | -0.003172 | -61.8793 | 61.6406 | 61.4312 | 61.5685 | -61.8648 | -61.7932 | 0.000359 | -61.8506 | 61.473 | 61.6188 | 60.9993 | -62.0606 | 0.011114 | 0.002723 | 0.16029 | -0.003377 | -0.014491 | -0.20667 | -0.069381 | -0.18468 | -0.16491 | 0.082695 | 0.025297 | 0.20998 | -0.019075 | -0.63856 | 123.5165 | 123.3071 | 123.4444 | 61.8727 | -123.5027 | 123.3489 | 123.4947 | 122.8752 | 61.8763 | -123.6985
278.0781 | 123.6145 | -61.8484 | 61.702 | 1.4211e-13 | -0.0035213 | 0.0018804 | 0.065468 | -0.0060339 | 0.061422 | -0.006028 | -0.0028861 | -0.0017051 | 0.070006 | 0.017536 | 0.062985 | -61.7156 | -0.003172 | -61.8701 | 61.636 | 61.4266 | 61.5639 | -61.8648 | -61.7932 | -0.00422 | -61.8506 | 61.4776 | 61.6096 | 61.0543 | -62.0652 | -0.016352 | -0.065942 | 0.13283 | -0.021686 | -0.005334 | -0.27533 | -0.13805 | -0.21673 | -0.22442 | 0.055229 | -0.002169 | 0.21456 | -0.092319 | -0.64771 | 123.4845 | 123.2751 | 123.4124 | 61.8453 | -123.5668 | 123.326 | 123.4581 | 122.9027 | 61.8442 | -123.7671
279.8281 | 123.6923 | -61.8759 | 61.6379 | 1.4211e-13 | -0.0035213 | 0.0018804 | 0.065041 | -0.0062475 | 0.061635 | -0.006028 | -0.0026725 | -0.0014913 | 0.070006 | 0.017322 | 0.062558 | -61.711 | -0.007751 | -61.8793 | 61.636 | 61.4266 | 61.5685 | -61.8602 | -61.7841 | -0.00422 | -61.8415 | 61.4776 | 61.6142 | 60.9902 | -62.0606 | 0.015693 | -0.001855 | 0.16487 | -0.003377 | -0.01907 | -0.21125 | -0.069381 | -0.18468 | -0.16033 | 0.091853 | 0.034454 | 0.21914 | -0.023653 | -0.64772 | 123.5119 | 123.3025 | 123.4444 | 61.8682 | -123.4981 | 123.3535 | 123.4901 | 122.8661 | 61.8717 | -123.6985
281.5156 | 123.6145 | -61.8439 | 61.7249 | 1.4211e-13 | -0.0035213 | 0.0016666 | 0.065255 | -0.0062475 | 0.061849 | 0.0016025 | -0.0024589 | -0.0014913 | 0.069792 | 0.017109 | 0.062771 | -61.711 | -0.003172 | -61.8701 | 61.636 | 61.4221 | 61.5593 | -61.8511 | -61.7841 | 0.000359 | -61.8506 | 61.4776 | 61.6234 | 60.9993 | -62.0698 | -0.007193 | -0.088831 | 0.13283 | -0.026264 | -0.019071 | -0.3028 | -0.16551 | -0.22589 | -0.2473 | 0.059809 | -0.006747 | 0.21914 | -0.10147 | -0.72554 | 123.4799 | 123.2659 | 123.4032 | 61.8407 | -123.5759 | 123.3214 | 123.4673 | 122.8432 | 61.8442 | -123.7946
283.2656 | 123.7473 | -61.8347 | 61.6241 | 1.4211e-13 | -0.0035213 | 0.0016666 | 0.065468 | -0.0060339 | 0.061208 | 0.0016025 | -0.0026725 | -0.0014913 | 0.070006 | 0.017536 | 0.062771 | -61.7156 | -0.003172 | -61.8747 | 61.6314 | 61.4312 | 61.5731 | -61.8556 | -61.7841 | -0.00422 | -61.846 | 61.4776 | 61.6234 | 60.9993 | -62.056 | -0.020927 | 0.007298 | 0.1191 | -0.039997 | -0.01907 | -0.19294 | -0.05107 | -0.2213 | -0.1466 | 0.050654 | -0.011324 | 0.20998 | -0.000764 | -0.62483 | 123.4662 | 123.2659 | 123.4078 | 61.8315 | -123.4798 | 123.3123 | 123.4581 | 122.834 | 61.8305 | -123.6802
285 | 123.6374 | -61.8118 | 61.7065 | 1.4211e-13 | -0.0030939 | 0.0016666 | 0.065255 | -0.0062475 | 0.061422 | -0.006028 | -0.0028861 | -0.0014913 | 0.07022 | 0.017322 | 0.062985 | -61.711 | -0.012329 | -61.8747 | 61.6269 | 61.4221 | 61.5639 | -61.8419 | -61.7841 | 0.004938 | -61.8415 | 61.4684 | 61.6142 | 60.9947 | -62.056 | -0.030078 | -0.079677 | 0.10079 | -0.062885 | -0.032807 | -0.28449 | -0.14262 | -0.24419 | -0.23815 | 0.027766 | -0.029633 | 0.21456 | -0.092318 | -0.71181 | 123.4387 | 123.2339 | 123.3757 | 61.7995 | -123.5485 | 123.2802 | 123.4261 | 122.8066 | 61.8168 | -123.7626
286.6719 | 123.5916 | -61.853 | 61.702 | 1.4211e-13 | -0.0037351 | 0.002094 | 0.065041 | -0.0058203 | 0.061635 | -0.006028 | -0.0024589 | -0.0017051 | 0.070006 | 0.017322 | 0.062771 | -61.7156 | -0.012329 | -61.8747 | 61.6223 | 61.4266 | 61.5685 | -61.8465 | -61.7886 | 0.000359 | -61.846 | 61.4638 | 61.6096 | 60.9902 | -62.056 | 0.006541 | -0.079677 | 0.13741 | -0.021687 | -0.028228 | -0.27533 | -0.13347 | -0.20299 | -0.23815 | 0.064385 | 0.006986 | 0.20998 | -0.092319 | -0.71181 | 123.4753 | 123.2797 | 123.4215 | 61.8407 | -123.5485 | 123.3168 | 123.4627 | 122.8432 | 61.8534 | -123.758
288.4219 | 123.7106 | -61.8301 | 61.647 | 1.4211e-13 | -0.0037351 | 0.0018804 | 0.065255 | -0.0062475 | 0.060994 | 0.0016025 | -0.0026725 | -0.0012777 | 0.070006 | 0.017536 | 0.062558 | -61.711 | -0.003172 | -61.8701 | 61.6314 | 61.4266 | 61.5639 | -61.8511 | -61.7749 | -0.00422 | -61.8415 | 61.473 | 61.6142 | 60.9856 | -62.0514 | -0.020926 | -0.01559 | 0.1191 | -0.039997 | -0.019071 | -0.2204 | -0.083115 | -0.2213 | -0.17406 | 0.055233 | -0.011323 | 0.20998 | -0.032809 | -0.66145 | 123.4616 | 123.2568 | 123.3941 | 61.827 | -123.4981 | 123.3031 | 123.4444 | 122.8157 | 61.8259 | -123.6985
290.1094 | 123.6603 | -61.8713 | 61.6241 | 1.4211e-13 | -0.0035213 | 0.0016666 | 0.065468 | -0.0058203 | 0.061422 | -0.013659 | -0.0028861 | -0.0019187 | 0.07022 | 0.017322 | 0.063198 | -61.6973 | -0.016908 | -61.8701 | 61.6223 | 61.4266 | 61.5639 | -61.8465 | -61.7795 | -0.00422 | -61.8415 | 61.4684 | 61.6142 | 60.981 | -62.0469 | 0.024852 | -0.001858 | 0.17403 | 0.001202 | -0.02365 | -0.19751 | -0.060227 | -0.17553 | -0.15575 | 0.091854 | 0.029876 | 0.2054 | -0.009921 | -0.64315 | 123.4936 | 123.298 | 123.4353 | 61.8544 | -123.4706 | 123.3397 | 123.4856 | 122.8523 | 61.8671 | -123.671
291.8438 | 123.6053 | -61.8439 | 61.6791 | 1.4211e-13 | -0.0035213 | 0.0018804 | 0.065468 | -0.0062475 | 0.061422 | 0.0016025 | -0.0024589 | -0.0014913 | 0.07022 | 0.017322 | 0.063198 | -61.711 | -0.012329 | -61.8701 | 61.636 | 61.4221 | 61.5593 | -61.8511 | -61.7749 | 0.000359 | -61.846 | 61.473 | 61.6096 | 60.9947 | -62.056 | -0.007193 | -0.043054 | 0.13283 | -0.026264 | -0.019071 | -0.25702 | -0.11974 | -0.21215 | -0.20611 | 0.068966 | -0.002169 | 0.20998 | -0.069431 | -0.68434 | 123.4799 | 123.2659 | 123.4032 | 61.8315 | -123.5301 | 123.3168 | 123.4535 | 122.8386 | 61.8442 | -123.7351
293.5938 | 123.6649 | -61.821 | 61.6791 | 1.4211e-13 | -0.0030939 | 0.0018804 | 0.065255 | -0.0060339 | 0.061422 | -0.006028 | -0.0026725 | -0.0017051 | 0.07022 | 0.017536 | 0.063198 | -61.7019 | -0.007751 | -61.8701 | 61.6269 | 61.4221 | 61.5593 | -61.8511 | -61.7749 | -0.008798 | -61.846 | 61.4684 | 61.6096 | 60.9902 | -62.0514 | -0.030081 | -0.052211 | 0.1191 | -0.049152 | -0.019071 | -0.25702 | -0.11974 | -0.23046 | -0.21068 | 0.046078 | -0.025057 | 0.2054 | -0.069431 | -0.68892 | 123.4479 | 123.243 | 123.3803 | 61.8132 | -123.5301 | 123.2894 | 123.4306 | 122.8111 | 61.8122 | -123.7305
295.3281 | 123.642 | -61.8347 | 61.6699 | 1.4211e-13 | -0.0033077 | 0.002094 | 0.065255 | -0.0062475 | 0.061422 | -0.013659 | -0.0026725 | -0.0017051 | 0.070433 | 0.017322 | 0.062985 | -61.7019 | -0.003172 | -61.8656 | 61.6223 | 61.4175 | 61.5593 | -61.8511 | -61.7703 | 0.000359 | -61.8415 | 61.4638 | 61.6142 | 60.9856 | -62.0469 | -0.016348 | -0.047634 | 0.13283 | -0.030841 | -0.014493 | -0.25245 | -0.11058 | -0.21215 | -0.20611 | 0.06439 | -0.006745 | 0.2054 | -0.055697 | -0.68434 | 123.457 | 123.2522 | 123.3941 | 61.8315 | -123.521 | 123.2985 | 123.4489 | 122.8203 | 61.8351 | -123.7168
297.0938 | 123.7656 | -61.8393 | 61.6013 | 1.4211e-13 | -0.0037351 | 0.0018804 | 0.065255 | -0.0064613 | 0.061422 | 0.0016025 | -0.0028861 | -0.0014913 | 0.07022 | 0.017322 | 0.063198 | -61.7065 | 0.001407 | -61.8656 | 61.6314 | 61.4175 | 61.5685 | -61.8556 | -61.7795 | 0.000359 | -61.8323 | 61.4684 | 61.6142 | 60.9856 | -62.056 | -0.01635 | 0.030187 | 0.13283 | -0.026264 | -0.009914 | -0.18378 | -0.03276 | -0.21673 | -0.13286 | 0.05981 | 0.00699 | 0.22372 | 0.012968 | -0.61568 | 123.4707 | 123.2568 | 123.4078 | 61.8407 | -123.4569 | 123.3077 | 123.4535 | 122.8249 | 61.8397 | -123.6573
298.8438 | 123.6786 | -61.8301 | 61.6196 | 1.4211e-13 | -0.0035213 | 0.0018804 | 0.065255 | -0.0062475 | 0.061208 | 0.0016025 | -0.0028861 | -0.0014913 | 0.07022 | 0.01775 | 0.063198 | -61.6973 | -0.007751 | -61.8656 | 61.6314 | 61.4175 | 61.5685 | -61.8556 | -61.7795 | 0.000359 | -61.8369 | 61.4684 | 61.6096 | 60.981 | -62.0514 | -0.025505 | 0.011876 | 0.13283 | -0.035419 | -0.009914 | -0.20209 | -0.051071 | -0.2213 | -0.15118 | 0.050655 | -0.006744 | 0.21456 | -0.009922 | -0.63857 | 123.4616 | 123.2476 | 123.3986 | 61.8224 | -123.4752 | 123.2985 | 123.4398 | 122.8111 | 61.8305 | -123.671
300.5312 | 123.7152 | -61.8393 | 61.5921 | 1.4211e-13 | -0.0037351 | 0.0016666 | 0.064827 | -0.0062475 | 0.061208 | 0.0016025 | -0.0026725 | -0.0014913 | 0.07022 | 0.017536 | 0.062771 | -61.7019 | -0.007751 | -61.861 | 61.6269 | 61.4221 | 61.5548 | -61.8511 | -61.7703 | 0.000359 | -61.8415 | 61.4684 | 61.6142 | 60.9947 | -62.0469 | -0.011771 | 0.034764 | 0.13741 | -0.021685 | -0.009914 | -0.17005 | -0.03734 | -0.20757 | -0.12371 | 0.068967 | -0.002168 | 0.2054 | 0.022123 | -0.59737 | 123.4662 | 123.2613 | 123.3941 | 61.8315 | -123.4432 | 123.3077 | 123.4535 | 122.834 | 61.8397 | -123.639
302.2656 | 123.6603 | -61.8484 | 61.6013 | 1.4211e-13 | -0.0037351 | 0.0016666 | 0.065255 | -0.0066749 | 0.061422 | -0.013659 | -0.0028861 | -0.0012777 | 0.070006 | 0.01775 | 0.062985 | -61.7065 | -0.012329 | -61.8656 | 61.6177 | 61.4129 | 61.5593 | -61.8419 | -61.7657 | -0.00422 | -61.8415 | 61.4638 | 61.6096 | 60.981 | -62.0423 | 0.006543 | 0.016452 | 0.14199 | -0.017108 | -0.023651 | -0.18836 | -0.041917 | -0.19383 | -0.13744 | 0.082702 | 0.006988 | 0.20082 | 0.008389 | -0.62026 | 123.4662 | 123.2613 | 123.4078 | 61.8361 | -123.4432 | 123.3123 | 123.4581 | 122.8295 | 61.8442 | -123.6435
304.0156 | 123.7198 | -61.8027 | 61.6013 | 1.4211e-13 | -0.0033077 | 0.0018804 | 0.065255 | -0.0064613 | 0.061208 | -0.006028 | -0.0028861 | -0.0014913 | 0.070433 | 0.01775 | 0.062344 | -61.6973 | -0.003172 | -61.8656 | 61.6269 | 61.4129 | 61.5593 | -61.8465 | -61.7657 | 0.000359 | -61.8369 | 61.4638 | 61.6005 | 60.9856 | -62.0423 | -0.043813 | 0.025609 | 0.10537 | -0.062885 | -0.019072 | -0.18836 | -0.041917 | -0.23961 | -0.13744 | 0.036925 | -0.03421 | 0.2054 | -0.000768 | -0.61568 | 123.4295 | 123.2156 | 123.362 | 61.7995 | -123.4477 | 123.2665 | 123.4032 | 122.7883 | 61.803 | -123.6435
305.6875 | 123.6191 | -61.8256 | 61.6928 | 1.4211e-13 | -0.0035213 | 0.0018804 | 0.064827 | -0.0060339 | 0.061208 | -0.006028 | -0.0028861 | -0.0017051 | 0.07022 | 0.01775 | 0.062771 | -61.7019 | 0.001407 | -61.8564 | 61.6177 | 61.4129 | 61.5502 | -61.8373 | -61.7657 | 0.000359 | -61.8323 | 61.4638 | 61.6051 | 60.981 | -62.0377 | -0.011766 | -0.075101 | 0.12368 | -0.030839 | -0.019073 | -0.27992 | -0.14263 | -0.21214 | -0.229 | 0.059814 | -0.006742 | 0.2054 | -0.087742 | -0.71181 | 123.4433 | 123.2385 | 123.3757 | 61.827 | -123.5301 | 123.2894 | 123.4306 | 122.8066 | 61.8259 | -123.7305
307.4375 | 123.6053 | -61.8622 | 61.6791 | 1.4211e-13 | -0.0035213 | 0.0018804 | 0.065255 | -0.0064613 | 0.061422 | -0.006028 | -0.0028861 | -0.0019187 | 0.070433 | 0.017536 | 0.062985 | -61.6973 | -0.003172 | -61.8564 | 61.6314 | 61.4129 | 61.5639 | -61.8282 | -61.7703 | -0.00422 | -61.8369 | 61.4501 | 61.6096 | 60.9764 | -62.0331 | 0.034013 | -0.047633 | 0.16488 | 0.005782 | -0.028231 | -0.26618 | -0.11516 | -0.17094 | -0.229 | 0.091856 | 0.0253 | 0.19624 | -0.069431 | -0.70266 | 123.4936 | 123.2751 | 123.4261 | 61.859 | -123.5072 | 123.3123 | 123.4718 | 122.8386 | 61.858 | -123.7122
309.1875 | 123.6465 | -61.821 | 61.6745 | 1.4211e-13 | -0.0035213 | 0.0016666 | 0.065255 | -0.0058203 | 0.061208 | 0.0016025 | -0.0026725 | -0.0012777 | 0.070433 | 0.017964 | 0.062558 | -61.6973 | 0.001407 | -61.8518 | 61.6177 | 61.4129 | 61.5593 | -61.8465 | -61.7703 | 0.004938 | -61.8323 | 61.4547 | 61.6096 | 60.9856 | -62.0423 | -0.025502 | -0.056791 | 0.12368 | -0.030839 | -0.005337 | -0.26161 | -0.11516 | -0.2213 | -0.21984 | 0.050657 | -0.01132 | 0.20998 | -0.064854 | -0.68892 | 123.4387 | 123.2339 | 123.3803 | 61.8224 | -123.521 | 123.2756 | 123.4306 | 122.8066 | 61.8259 | -123.7168
310.8594 | 123.6923 | -61.8301 | 61.6196 | 1.4211e-13 | -0.0035213 | 0.002094 | 0.065255 | -0.0064613 | 0.061208 | -0.006028 | -0.0030999 | -0.0014913 | 0.07022 | 0.01775 | 0.062558 | -61.6973 | -0.003172 | -61.8564 | 61.6177 | 61.4129 | 61.5502 | -61.8327 | -61.7749 | -0.00422 | -61.8323 | 61.4592 | 61.6051 | 60.9856 | -62.0377 | -0.00261 | -0.001859 | 0.13283 | -0.026262 | -0.023652 | -0.20667 | -0.069385 | -0.20757 | -0.16033 | 0.055233 | -0.002165 | 0.2054 | -0.0145 | -0.63399 | 123.4478 | 123.243 | 123.3803 | 61.827 | -123.4523 | 123.2894 | 123.4352 | 122.8157 | 61.8259 | -123.6573
312.6094 | 123.7061 | -61.8256 | 61.6196 | 1.4211e-13 | -0.0037351 | 0.0018804 | 0.065255 | -0.0060339 | 0.061208 | -0.006028 | -0.0026725 | -0.0017051 | 0.07022 | 0.017536 | 0.062344 | -61.6973 | -0.012329 | -61.8564 | 61.6223 | 61.4129 | 61.5502 | -61.8373 | -61.7703 | 0.004938 | -61.8277 | 61.4592 | 61.6096 | 60.981 | -62.0377 | -0.011766 | 0.00272 | 0.12825 | -0.030839 | -0.019073 | -0.20667 | -0.069385 | -0.21214 | -0.16033 | 0.055235 | -0.002164 | 0.20998 | -0.009922 | -0.63857 | 123.4478 | 123.2385 | 123.3757 | 61.8132 | -123.4569 | 123.2848 | 123.4352 | 122.8066 | 61.8305 | -123.6573
314.3594 | 123.7381 | -61.8347 | 61.6333 | 1.4211e-13 | -0.0035213 | 0.002094 | 0.065041 | -0.0064613 | 0.061422 | -0.006028 | -0.0026725 | -0.0017051 | 0.070433 | 0.01775 | 0.062771 | -61.6882 | -0.007751 | -61.8564 | 61.6223 | 61.4175 | 61.5548 | -61.8419 | -61.7657 | -0.00422 | -61.8323 | 61.4592 | 61.6051 | 60.9718 | -62.0331 | -0.00719 | -0.011013 | 0.14657 | -0.021684 | -0.014494 | -0.21583 | -0.078539 | -0.19841 | -0.17407 | 0.068969 | 0.002413 | 0.20082 | -0.028233 | -0.66146 | 123.457 | 123.2522 | 123.3895 | 61.827 | -123.4752 | 123.294 | 123.4398 | 122.8066 | 61.8305 | -123.6664
316.0625 | 123.6694 | -61.8347 | 61.6241 | 1.4211e-13 | -0.0037351 | 0.0018804 | 0.064827 | -0.0062475 | 0.061422 | -0.006028 | -0.0028861 | -0.0017051 | 0.070006 | 0.01775 | 0.062771 | -61.6927 | -0.003172 | -61.8564 | 61.6177 | 61.4083 | 61.5456 | -61.8373 | -61.7657 | 0.000359 | -61.8323 | 61.4592 | 61.6051 | 60.9718 | -62.0285 | -0.002611 | -0.006437 | 0.14199 | -0.021684 | -0.019073 | -0.21583 | -0.078542 | -0.19383 | -0.16491 | 0.068969 | 0.002413 | 0.19624 | -0.019078 | -0.6523 | 123.4524 | 123.243 | 123.3803 | 61.8315 | -123.4615 | 123.294 | 123.4398 | 122.8066 | 61.8351 | -123.6527
317.8125 | 123.6603 | -61.8118 | 61.615 | 1.4211e-13 | -0.0037351 | 0.0018804 | 0.065255 | -0.0060339 | 0.060994 | 0.0016025 | -0.0028861 | -0.0019187 | 0.070006 | 0.017536 | 0.062558 | -61.6882 | 0.001407 | -61.8518 | 61.6223 | 61.4083 | 61.5548 | -61.8465 | -61.7657 | -0.00422 | -61.8231 | 61.4501 | 61.6005 | 60.9718 | -62.0331 | -0.034657 | 0.007298 | 0.12368 | -0.039994 | -0.005337 | -0.20667 | -0.060228 | -0.2213 | -0.16491 | 0.046081 | -0.011318 | 0.20998 | -0.014501 | -0.64315 | 123.4341 | 123.2201 | 123.3666 | 61.8132 | -123.4615 | 123.2619 | 123.4123 | 122.7837 | 61.8076 | -123.6481
319.5625 | 123.6923 | -61.8164 | 61.6241 | 1.4211e-13 | -0.0035213 | 0.0016666 | 0.065255 | -0.0062475 | 0.061422 | -0.006028 | -0.0026725 | -0.0019187 | 0.070433 | 0.017964 | 0.062985 | -61.6927 | 0.001407 | -61.8472 | 61.6177 | 61.4037 | 61.5456 | -61.8373 | -61.7657 | -0.008798 | -61.8277 | 61.4501 | 61.5959 | 60.9718 | -62.0331 | -0.020922 | -0.006437 | 0.12368 | -0.030839 | -0.009917 | -0.22041 | -0.078542 | -0.21672 | -0.17407 | 0.050658 | -0.01132 | 0.2054 | -0.028236 | -0.6523 | 123.4341 | 123.2201 | 123.362 | 61.8178 | -123.4615 | 123.2665 | 123.4123 | 122.7882 | 61.8076 | -123.6573
321.25 | 123.555 | -61.8256 | 61.6974 | 1.4211e-13 | -0.0035213 | 0.0018804 | 0.064827 | -0.0062475 | 0.061208 | -0.006028 | -0.0024589 | -0.0017051 | 0.070006 | 0.01775 | 0.062771 | -61.6882 | -0.003172 | -61.8518 | 61.6131 | 61.4037 | 61.5456 | -61.8236 | -61.7657 | 0.000359 | -61.8277 | 61.4455 | 61.6005 | 60.9718 | -62.0331 | 0.001971 | -0.084257 | 0.13741 | -0.026261 | -0.028232 | -0.29365 | -0.15178 | -0.20757 | -0.25189 | 0.059814 | -0.002164 | 0.2054 | -0.096899 | -0.72554 | 123.4387 | 123.2293 | 123.3712 | 61.8224 | -123.521 | 123.2711 | 123.4261 | 122.7974 | 61.8259 | -123.7305
323 | 123.6969 | -61.8073 | 61.5875 | 1.4211e-13 | -0.0035213 | 0.0016666 | 0.065255 | -0.0062475 | 0.061208 | -0.006028 | -0.0028861 | -0.0014913 | 0.070006 | 0.017964 | 0.062344 | -61.6927 | -0.003172 | -61.8472 | 61.6131 | 61.4129 | 61.541 | -61.8327 | -61.752 | 0.004938 | -61.8277 | 61.4455 | 61.5959 | 60.9581 | -62.024 | -0.025498 | 0.025607 | 0.11452 | -0.039994 | -0.014496 | -0.17463 | -0.046498 | -0.21672 | -0.14202 | 0.055239 | -0.020475 | 0.19624 | 0.008386 | -0.62942 | 123.4204 | 123.2201 | 123.3483 | 61.8041 | -123.4203 | 123.2528 | 123.4032 | 122.7654 | 61.8122 | -123.6115
324.6875 | 123.5458 | -61.8347 | 61.6745 | 1.4211e-13 | -0.0035213 | 0.0018804 | 0.065255 | -0.0060339 | 0.061422 | -0.006028 | -0.0028861 | -0.0017051 | 0.07022 | 0.017536 | 0.062344 | -61.679 | -0.003172 | -61.8564 | 61.6131 | 61.4083 | 61.5456 | -61.8282 | -61.7566 | -0.00422 | -61.8231 | 61.4592 | 61.5913 | 60.9718 | -62.0285 | 0.006547 | -0.061369 | 0.15572 | -0.021684 | -0.028231 | -0.26618 | -0.1289 | -0.19383 | -0.21526 | 0.078126 | 0.01157 | 0.2054 | -0.083168 | -0.70266 | 123.4478 | 123.243 | 123.3803 | 61.8315 | -123.5027 | 123.294 | 123.426 | 122.8066 | 61.8305 | -123.703
326.4375 | 123.6099 | -61.8027 | 61.6928 | 1.4211e-13 | -0.0033077 | 0.001453 | 0.065255 | -0.0062475 | 0.061208 | -0.006028 | -0.0030999 | -0.0014913 | 0.070433 | 0.017964 | 0.062771 | -61.6836 | -0.007751 | -61.8472 | 61.6131 | 61.4083 | 61.541 | -61.8373 | -61.7566 | 0.004938 | -61.8186 | 61.4501 | 61.5868 | 60.9673 | -62.024 | -0.034655 | -0.079679 | 0.1191 | -0.044572 | -0.009917 | -0.28449 | -0.15178 | -0.2213 | -0.24273 | 0.046082 | -0.015895 | 0.2054 | -0.10606 | -0.72555 | 123.4158 | 123.211 | 123.3437 | 61.7949 | -123.5301 | 123.2528 | 123.3894 | 122.7699 | 61.8076 | -123.7168
328.1875 | 123.6969 | -61.8073 | 61.6241 | 1.4211e-13 | -0.0037351 | 0.002094 | 0.064827 | -0.0060339 | 0.061208 | -0.006028 | -0.0024589 | -0.0014913 | 0.070433 | 0.01775 | 0.062771 | -61.6836 | -0.007751 | -61.8472 | 61.6177 | 61.4083 | 61.5456 | -61.8327 | -61.7566 | 0.004938 | -61.8186 | 61.4501 | 61.5959 | 60.9673 | -62.024 | -0.025498 | -0.006437 | 0.12368 | -0.039994 | -0.014496 | -0.21583 | -0.078542 | -0.21672 | -0.17407 | 0.05066 | -0.011317 | 0.2054 | -0.028236 | -0.65688 | 123.425 | 123.2156 | 123.3529 | 61.7995 | -123.4569 | 123.2573 | 123.4032 | 122.7745 | 61.8122 | -123.6481
329.875 | 123.6969 | -61.8118 | 61.615 | 1.4211e-13 | -0.0037351 | 0.002094 | 0.064827 | -0.0064613 | 0.061208 | -0.006028 | -0.0026725 | -0.0010641 | 0.070006 | 0.017536 | 0.062558 | -61.679 | -0.007751 | -61.8472 | 61.6086 | 61.3992 | 61.541 | -61.8282 | -61.752 | -0.00422 | -61.814 | 61.4501 | 61.5959 | 60.9718 | -62.0194 | -0.016341 | -0.006438 | 0.13284 | -0.035416 | -0.019075 | -0.21583 | -0.073964 | -0.20756 | -0.16491 | 0.059817 | -0.002161 | 0.2054 | -0.01908 | -0.64315 | 123.4204 | 123.211 | 123.3529 | 61.8041 | -123.4432 | 123.2619 | 123.4077 | 122.7837 | 61.8076 | -123.6344
331.625 | 123.6832 | -61.8027 | 61.6287 | 1.4211e-13 | -0.0035213 | 0.0018804 | 0.065041 | -0.0064613 | 0.061208 | -0.006028 | -0.0026725 | -0.0019187 | 0.070006 | 0.01775 | 0.061917 | -61.6836 | 0.001407 | -61.8335 | 61.604 | 61.3992 | 61.5364 | -61.8236 | -61.7474 | 0.000359 | -61.8231 | 61.4455 | 61.5868 | 60.9673 | -62.0285 | -0.020918 | -0.024749 | 0.1191 | -0.030837 | -0.009919 | -0.22957 | -0.092276 | -0.22588 | -0.18322 | 0.05524 | -0.020474 | 0.2054 | -0.04197 | -0.66146 | 123.4066 | 123.2018 | 123.3391 | 61.8041 | -123.4523 | 123.2482 | 123.3894 | 122.7699 | 61.803 | -123.6573
333.375 | 123.6694 | -61.8027 | 61.5875 | 1.4211e-13 | -0.0035213 | 0.0018804 | 0.064614 | -0.0066749 | 0.061208 | -0.006028 | -0.0024589 | -0.0014913 | 0.070006 | 0.017964 | 0.062344 | -61.6836 | -0.007751 | -61.8381 | 61.6086 | 61.4083 | 61.5319 | -61.8282 | -61.752 | 0.000359 | -61.814 | 61.4455 | 61.5959 | 60.9718 | -62.024 | -0.025497 | 0.021028 | 0.1191 | -0.035415 | -0.009918 | -0.17921 | -0.055655 | -0.2213 | -0.14202 | 0.050661 | -0.011317 | 0.20998 | 0.008386 | -0.61568 | 123.4112 | 123.211 | 123.3345 | 61.7949 | -123.4157 | 123.2482 | 123.3986 | 122.7745 | 61.803 | -123.6115
335.0781 | 123.5367 | -61.8393 | 61.6653 | 1.4211e-13 | -0.0037351 | 0.0016666 | 0.065041 | -0.0062475 | 0.060781 | -0.006028 | -0.0026725 | -0.0017051 | 0.07022 | 0.017964 | 0.062344 | -61.679 | 0.005985 | -61.8381 | 61.6086 | 61.4083 | 61.541 | -61.8282 | -61.7566 | 0.000359 | -61.8186 | 61.4501 | 61.5913 | 60.9581 | -62.024 | 0.011124 | -0.056792 | 0.1603 | 0.001206 | -0.009918 | -0.25703 | -0.12432 | -0.18467 | -0.21526 | 0.082703 | 0.020726 | 0.2054 | -0.074012 | -0.70724 | 123.4478 | 123.2476 | 123.3803 | 61.8453 | -123.4935 | 123.2894 | 123.4306 | 122.7974 | 61.8397 | -123.6893
336.8125 | 123.6008 | -61.7935 | 61.6974 | 1.4211e-13 | -0.0035213 | 0.0018804 | 0.064827 | -0.0066749 | 0.061208 | 0.0016025 | -0.0028861 | -0.0014913 | 0.070006 | 0.018177 | 0.06213 | -61.6744 | 0.001407 | -61.8427 | 61.6086 | 61.3946 | 61.541 | -61.819 | -61.7474 | 0.004938 | -61.8186 | 61.4409 | 61.5868 | 60.9673 | -62.0194 | -0.025495 | -0.088836 | 0.1191 | -0.049148 | -0.023653 | -0.30281 | -0.15636 | -0.22587 | -0.25647 | 0.046085 | -0.02505 | 0.20082 | -0.11063 | -0.73012 | 123.4021 | 123.1881 | 123.3345 | 61.7949 | -123.5164 | 123.2344 | 123.3803 | 122.7608 | 61.7985 | -123.7168
338.5781 | 123.6374 | -61.8027 | 61.5967 | 1.4211e-13 | -0.0039487 | 0.0018804 | 0.064827 | -0.0062475 | 0.061208 | -0.006028 | -0.0028861 | -0.0012777 | 0.070433 | 0.018177 | 0.06213 | -61.6744 | -0.003172 | -61.8427 | 61.5994 | 61.4083 | 61.5364 | -61.8282 | -61.7474 | 0.004938 | -61.8186 | 61.4409 | 61.5822 | 60.9627 | -62.0148 | -0.025497 | 0.002716 | 0.12826 | -0.039993 | -0.014496 | -0.18836 | -0.060233 | -0.21214 | -0.15576 | 0.05524 | -0.015895 | 0.19624 | -0.014505 | -0.63399 | 123.4021 | 123.211 | 123.3391 | 61.7995 | -123.4248 | 123.2436 | 123.3848 | 122.7654 | 61.8076 | -123.6115
340.2656 | 123.6649 | -61.8118 | 61.5784 | 1.4211e-13 | -0.0037351 | 0.002094 | 0.064827 | -0.0064613 | 0.061422 | -0.006028 | -0.0026725 | -0.0014913 | 0.07022 | 0.017964 | 0.062558 | -61.6744 | 0.001407 | -61.8381 | 61.604 | 61.3992 | 61.5364 | -61.8236 | -61.7566 | 0.000359 | -61.8094 | 61.4455 | 61.5776 | 60.9581 | -62.0194 | -0.011762 | 0.025605 | 0.13741 | -0.026259 | -0.014497 | -0.17921 | -0.041922 | -0.20756 | -0.13287 | 0.055238 | 0.002418 | 0.20998 | -0.000773 | -0.62026 | 123.4158 | 123.211 | 123.3483 | 61.8132 | -123.402 | 123.2573 | 123.3894 | 122.7699 | 61.8122 | -123.5978
342.0156 | 123.5779 | -61.8027 | 61.6699 | 1.4211e-13 | -0.0035213 | 0.0016666 | 0.064827 | -0.0064613 | 0.060781 | -0.006028 | -0.0028861 | -0.0014913 | 0.07022 | 0.018177 | 0.062344 | -61.6698 | 0.001407 | -61.8381 | 61.5948 | 61.39 | 61.5273 | -61.8236 | -61.752 | -0.008798 | -61.814 | 61.4409 | 61.573 | 60.9581 | -62.0194 | -0.020918 | -0.075105 | 0.13284 | -0.035415 | -0.014497 | -0.27992 | -0.14263 | -0.21672 | -0.229 | 0.050661 | -0.011317 | 0.2054 | -0.096905 | -0.71182 | 123.3975 | 123.1927 | 123.33 | 61.8041 | -123.4935 | 123.2436 | 123.3757 | 122.7608 | 61.7939 | -123.6893
343.7656 | 123.6649 | -61.8073 | 61.5875 | 1.4211e-13 | -0.0039487 | 0.0023076 | 0.064614 | -0.0062475 | 0.061208 | 0.0092325 | -0.0028861 | -0.0017051 | 0.07022 | 0.017964 | 0.06213 | -61.6744 | -0.003172 | -61.8381 | 61.5994 | 61.4037 | 61.5364 | -61.8282 | -61.7474 | 0.004938 | -61.8094 | 61.4409 | 61.5822 | 60.9627 | -62.0148 | -0.020919 | 0.011872 | 0.13284 | -0.030837 | -0.009918 | -0.18379 | -0.051077 | -0.20756 | -0.1466 | 0.059818 | -0.00216 | 0.2054 | -0.005349 | -0.62484 | 123.4066 | 123.211 | 123.3437 | 61.8041 | -123.4157 | 123.2482 | 123.3894 | 122.7699 | 61.8122 | -123.6023
345.4531 | 123.5458 | -61.8118 | 61.6791 | 1.4211e-13 | -0.0037351 | 0.001453 | 0.065041 | -0.0062475 | 0.061422 | 0.0016025 | -0.0022453 | -0.0014913 | 0.07022 | 0.018177 | 0.061917 | -61.6744 | 0.001407 | -61.8335 | 61.5994 | 61.3946 | 61.5364 | -61.8236 | -61.7474 | 0.000359 | -61.8094 | 61.4409 | 61.5776 | 60.9581 | -62.0148 | -0.011762 | -0.079681 | 0.13741 | -0.021681 | -0.009919 | -0.2845 | -0.14263 | -0.20298 | -0.23815 | 0.064396 | 0.002418 | 0.2054 | -0.10148 | -0.72097 | 123.4112 | 123.2064 | 123.3483 | 61.8132 | -123.5027 | 123.2528 | 123.3894 | 122.7699 | 61.8122 | -123.6939
347.2031 | 123.5779 | -61.7661 | 61.6562 | 1.4211e-13 | -0.0037351 | 0.002094 | 0.064827 | -0.0062475 | 0.060994 | 0.0092325 | -0.0028861 | -0.0017051 | 0.070006 | 0.018177 | 0.062558 | -61.6653 | -0.007751 | -61.8289 | 61.5948 | 61.4037 | 61.5364 | -61.8236 | -61.7474 | 0.004938 | -61.8094 | 61.4409 | 61.5776 | 60.9627 | -62.0194 | -0.057539 | -0.061372 | 0.10079 | -0.06288 | -0.005341 | -0.25245 | -0.11974 | -0.25334 | -0.21527 | 0.018619 | -0.043359 | 0.20998 | -0.078593 | -0.6935 | 123.3609 | 123.1698 | 123.3025 | 61.7583 | -123.4798 | 123.207 | 123.3436 | 122.7287 | 61.771 | -123.6756
348.9062 | 123.5092 | -61.8073 | 61.6562 | 1.4211e-13 | -0.0039487 | 0.0016666 | 0.064614 | -0.0062475 | 0.061208 | 0.0092325 | -0.0028861 | -0.0017051 | 0.069792 | 0.017964 | 0.06213 | -61.6653 | -0.007751 | -61.8289 | 61.5948 | 61.3946 | 61.5273 | -61.819 | -61.7429 | -0.00422 | -61.8094 | 61.4318 | 61.573 | 60.9581 | -62.0102 | -0.011762 | -0.061372 | 0.14199 | -0.021681 | -0.009919 | -0.26161 | -0.1289 | -0.20298 | -0.22442 | 0.064396 | -0.00216 | 0.20082 | -0.083172 | -0.69808 | 123.4021 | 123.2018 | 123.3345 | 61.7995 | -123.4752 | 123.239 | 123.3803 | 122.7654 | 61.803 | -123.6664
350.6562 | 123.5275 | -61.7889 | 61.6608 | 1.4211e-13 | -0.0041623 | 0.0023076 | 0.064614 | -0.0062475 | 0.061422 | -0.006028 | -0.0035271 | -0.0014913 | 0.070433 | 0.018177 | 0.061917 | -61.6698 | -0.007751 | -61.8244 | 61.5948 | 61.3992 | 61.5273 | -61.8236 | -61.7383 | -0.00422 | -61.8094 | 61.4318 | 61.5776 | 60.9673 | -62.0194 | -0.034651 | -0.06595 | 0.1191 | -0.035413 | -0.000762 | -0.26161 | -0.13348 | -0.23045 | -0.229 | 0.050664 | -0.020471 | 0.20998 | -0.083171 | -0.6935 | 123.3838 | 123.1881 | 123.3162 | 61.7812 | -123.4844 | 123.2207 | 123.3665 | 122.7562 | 61.7847 | -123.6802
352.4062 | 123.5184 | -61.8027 | 61.6562 | 1.4211e-13 | -0.0039487 | 0.0018804 | 0.064614 | -0.0060339 | 0.060994 | -0.013659 | -0.0028861 | -0.0017051 | 0.07022 | 0.018177 | 0.062344 | -61.6653 | -0.003172 | -61.8335 | 61.5948 | 61.3946 | 61.5273 | -61.8236 | -61.7383 | -0.00422 | -61.8048 | 61.4318 | 61.5776 | 60.9581 | -62.0148 | -0.020918 | -0.061372 | 0.13741 | -0.030837 | -0.009919 | -0.26161 | -0.1289 | -0.21214 | -0.22442 | 0.064397 | -0.002159 | 0.20998 | -0.078593 | -0.69808 | 123.3975 | 123.1973 | 123.33 | 61.7995 | -123.4798 | 123.2344 | 123.3803 | 122.7608 | 61.7985 | -123.671
354.1094 | 123.555 | -61.7844 | 61.6241 | 1.4211e-13 | -0.0033077 | 0.002094 | 0.064827 | -0.0066749 | 0.060994 | -0.006028 | -0.0030999 | -0.0014913 | 0.069792 | 0.018177 | 0.062344 | -61.6653 | -0.012329 | -61.8289 | 61.5948 | 61.3946 | 61.5319 | -61.8144 | -61.7429 | -0.00422 | -61.8003 | 61.4318 | 61.573 | 60.9581 | -62.0057 | -0.030071 | -0.029329 | 0.1191 | -0.044569 | -0.014498 | -0.22957 | -0.092277 | -0.22129 | -0.19238 | 0.041508 | -0.01589 | 0.2054 | -0.051129 | -0.66604 | 123.3792 | 123.1789 | 123.3162 | 61.772 | -123.4386 | 123.2161 | 123.3574 | 122.7425 | 61.7801 | -123.6298
355.875 | 123.6465 | -61.7752 | 61.5784 | 1.4211e-13 | -0.0037351 | 0.0016666 | 0.064614 | -0.0066749 | 0.061208 | -0.006028 | -0.0028861 | -0.0014913 | 0.07022 | 0.018177 | 0.062344 | -61.6607 | -0.003172 | -61.8289 | 61.5857 | 61.39 | 61.5319 | -61.8144 | -61.7474 | 0.000359 | -61.8048 | 61.4363 | 61.573 | 60.9535 | -62.0194 | -0.039226 | 0.007292 | 0.11453 | -0.053724 | -0.014498 | -0.18837 | -0.0465 | -0.24418 | -0.14203 | 0.027775 | -0.029624 | 0.21456 | -0.005352 | -0.62484 | 123.3609 | 123.1652 | 123.3071 | 61.772 | -123.3928 | 123.2116 | 123.3482 | 122.7287 | 61.7756 | -123.5978
357.6406 | 123.5458 | -61.7889 | 61.647 | 1.4211e-13 | -0.0037351 | 0.0018804 | 0.064614 | -0.0060339 | 0.061422 | 0.0016025 | -0.0026725 | -0.0017051 | 0.07022 | 0.018391 | 0.062558 | -61.6653 | -0.003172 | -61.8335 | 61.5902 | 61.3946 | 61.5364 | -61.8099 | -61.7383 | 0.004938 | -61.8048 | 61.4318 | 61.573 | 60.9535 | -62.0057 | -0.020915 | -0.056795 | 0.12368 | -0.04457 | -0.023655 | -0.25245 | -0.11059 | -0.21671 | -0.21527 | 0.050664 | -0.015892 | 0.20082 | -0.074017 | -0.6935 | 123.3792 | 123.1835 | 123.3254 | 61.7858 | -123.4569 | 123.2207 | 123.362 | 122.7425 | 61.7939 | -123.6527
359.3906 | 123.5962 | -61.8301 | 61.5646 | 1.4211e-13 | -0.0041623 | 0.002094 | 0.064827 | -0.0064613 | 0.061422 | 0.0092325 | -0.0028861 | -0.0014913 | 0.07022 | 0.018391 | 0.06213 | -61.6653 | -0.003172 | -61.8198 | 61.5948 | 61.3992 | 61.5273 | -61.819 | -61.7429 | 0.000359 | -61.7957 | 61.4318 | 61.573 | 60.9535 | -62.0011 | 0.011126 | 0.030181 | 0.16488 | 0.010364 | -0.000762 | -0.16548 | -0.037346 | -0.17094 | -0.13287 | 0.087284 | 0.034464 | 0.2054 | 0.008381 | -0.61111 | 123.425 | 123.2293 | 123.3574 | 61.827 | -123.3836 | 123.2619 | 123.4032 | 122.7837 | 61.8305 | -123.5657
361.0781 | 123.5184 | -61.7889 | 61.6196 | 1.4211e-13 | -0.0039487 | 0.0018804 | 0.064827 | -0.0062475 | 0.061422 | 0.0016025 | -0.0030999 | -0.0014913 | 0.070647 | 0.018177 | 0.062344 | -61.6607 | -0.007751 | -61.8289 | 61.5902 | 61.3946 | 61.5273 | -61.8099 | -61.7337 | -0.00422 | -61.8048 | 61.4363 | 61.5684 | 60.9581 | -62.0102 | -0.020915 | -0.029329 | 0.12826 | -0.039992 | -0.019077 | -0.22499 | -0.092278 | -0.22129 | -0.18322 | 0.055243 | -0.015892 | 0.2054 | -0.051129 | -0.66146 | 123.3792 | 123.1835 | 123.3162 | 61.7812 | -123.4294 | 123.2253 | 123.3574 | 122.747 | 61.7847 | -123.6298
362.8438 | 123.5321 | -61.7844 | 61.6333 | 1.4211e-13 | -0.0037351 | 0.0018804 | 0.065041 | -0.0066749 | 0.060994 | -0.013659 | -0.0030999 | -0.0017051 | 0.069792 | 0.018391 | 0.062344 | -61.6607 | -0.007751 | -61.8152 | 61.5857 | 61.3854 | 61.5273 | -61.8144 | -61.7337 | -0.00422 | -61.8003 | 61.4318 | 61.5639 | 60.9444 | -62.0057 | -0.030071 | -0.04764 | 0.12368 | -0.030834 | -0.000763 | -0.24788 | -0.10601 | -0.22129 | -0.20154 | 0.050666 | -0.01589 | 0.2054 | -0.069441 | -0.68893 | 123.37 | 123.1698 | 123.3117 | 61.7766 | -123.4477 | 123.2161 | 123.3482 | 122.7287 | 61.7801 | -123.639
364.5938 | 123.5825 | -61.7935 | 61.6425 | 1.4211e-13 | -0.0037351 | 0.0023076 | 0.064614 | -0.0064613 | 0.061635 | 0.0016025 | -0.0028861 | -0.0017051 | 0.070006 | 0.018391 | 0.06213 | -61.6607 | -0.012329 | -61.8244 | 61.5902 | 61.3854 | 61.5227 | -61.8053 | -61.7291 | -0.00422 | -61.8003 | 61.4318 | 61.5776 | 60.949 | -62.0011 | -0.011758 | -0.052217 | 0.13284 | -0.030835 | -0.019077 | -0.25704 | -0.11975 | -0.20756 | -0.21069 | 0.064399 | -0.006735 | 0.20082 | -0.06486 | -0.69351 | 123.3838 | 123.1789 | 123.3162 | 61.7812 | -123.4477 | 123.2253 | 123.3711 | 122.7425 | 61.7893 | -123.6435
366.2656 | 123.5184 | -61.8027 | 61.6425 | 1.4211e-13 | -0.0035213 | 0.002094 | 0.064827 | -0.0062475 | 0.060781 | -0.006028 | -0.0028861 | -0.0014913 | 0.07022 | 0.018177 | 0.06213 | -61.6561 | -0.003172 | -61.8244 | 61.5857 | 61.39 | 61.5227 | -61.8099 | -61.7383 | 0.000359 | -61.8048 | 61.4318 | 61.573 | 60.949 | -62.0102 | -0.007182 | -0.056795 | 0.14657 | -0.02168 | -0.014498 | -0.25246 | -0.11975 | -0.20756 | -0.21069 | 0.064397 | -0.002159 | 0.2054 | -0.069439 | -0.69351 | 123.3883 | 123.1927 | 123.3254 | 61.7995 | -123.4523 | 123.2344 | 123.3757 | 122.7516 | 61.803 | -123.6527
368.0156 | 123.5504 | -61.7706 | 61.6837 | 1.4211e-13 | -0.0039487 | 0.0023076 | 0.064827 | -0.0062475 | 0.060994 | 0.0016025 | -0.0028861 | -0.0017051 | 0.07022 | 0.018177 | 0.06213 | -61.6561 | 0.001407 | -61.8198 | 61.5857 | 61.39 | 61.5273 | -61.7961 | -61.7291 | 0.004938 | -61.7957 | 61.4272 | 61.573 | 60.949 | -62.0011 | -0.025488 | -0.097994 | 0.11453 | -0.049145 | -0.023657 | -0.29366 | -0.15637 | -0.23045 | -0.25647 | 0.041511 | -0.025045 | 0.2054 | -0.11064 | -0.7347 | 123.3563 | 123.1606 | 123.2979 | 61.772 | -123.4798 | 123.1978 | 123.3436 | 122.7196 | 61.7756 | -123.6847
369.7031 | 123.6237 | -61.7844 | 61.6058 | 1.4211e-13 | -0.0039487 | 0.002094 | 0.064186 | -0.0064613 | 0.061422 | -0.006028 | -0.0026725 | -0.0019187 | 0.070006 | 0.018177 | 0.062344 | -61.6607 | -0.007751 | -61.8198 | 61.5765 | 61.3992 | 61.5273 | -61.8053 | -61.7291 | 0.000359 | -61.8003 | 61.4226 | 61.5639 | 60.949 | -62.0011 | -0.020913 | -0.029331 | 0.12368 | -0.035412 | -0.014499 | -0.20668 | -0.078545 | -0.21671 | -0.18323 | 0.055244 | -0.01589 | 0.20082 | -0.041975 | -0.65688 | 123.3609 | 123.1835 | 123.3117 | 61.7766 | -123.4111 | 123.207 | 123.3482 | 122.7333 | 61.7847 | -123.6069
371.4531 | 123.5687 | -61.7889 | 61.6333 | 1.4211e-13 | -0.0041623 | 0.0016666 | 0.0644 | -0.0064613 | 0.060994 | -0.006028 | -0.0028861 | -0.0019187 | 0.07022 | 0.018391 | 0.062344 | -61.6561 | -0.007751 | -61.8198 | 61.5811 | 61.39 | 61.5181 | -61.7961 | -61.7245 | 0.000359 | -61.7957 | 61.4318 | 61.5776 | 60.9444 | -62.0011 | -0.007178 | -0.052219 | 0.13284 | -0.030835 | -0.023657 | -0.2433 | -0.11517 | -0.21214 | -0.20154 | 0.0644 | -0.006735 | 0.2054 | -0.055705 | -0.68893 | 123.37 | 123.1789 | 123.3071 | 61.7812 | -123.4294 | 123.2207 | 123.3665 | 122.7333 | 61.7893 | -123.6344
373.1562 | 123.5413 | -61.7569 | 61.647 | 1.4211e-13 | -0.0037351 | 0.002094 | 0.065255 | -0.0064613 | 0.061208 | -0.006028 | -0.0028861 | -0.0017051 | 0.07022 | 0.018391 | 0.062344 | -61.6515 | -0.003172 | -61.8244 | 61.5857 | 61.4037 | 61.5273 | -61.8007 | -61.7291 | 0.000359 | -61.7957 | 61.4272 | 61.5684 | 60.949 | -62.0011 | -0.0438 | -0.061373 | 0.10537 | -0.067456 | -0.023656 | -0.2433 | -0.11974 | -0.24418 | -0.21985 | 0.027778 | -0.038778 | 0.2054 | -0.078595 | -0.69808 | 123.3426 | 123.1606 | 123.2842 | 61.7537 | -123.4477 | 123.1841 | 123.3253 | 122.7058 | 61.7573 | -123.6481
374.9062 | 123.5413 | -61.7889 | 61.6333 | 1.4211e-13 | -0.0037351 | 0.002094 | 0.064827 | -0.0066749 | 0.060994 | 0.0016025 | -0.0028861 | -0.0017051 | 0.069792 | 0.018177 | 0.06213 | -61.6469 | -0.012329 | -61.8106 | 61.5857 | 61.3854 | 61.5227 | -61.8007 | -61.7245 | 0.009516 | -61.7911 | 61.418 | 61.5684 | 60.9444 | -62.0011 | -0.011757 | -0.04764 | 0.14199 | -0.021678 | -0.009921 | -0.24788 | -0.11059 | -0.21214 | -0.21527 | 0.0644 | -0.002156 | 0.20998 | -0.064862 | -0.68893 | 123.3746 | 123.1744 | 123.3117 | 61.7766 | -123.434 | 123.207 | 123.3574 | 122.7333 | 61.7985 | -123.6344
376.5938 | 123.5321 | -61.7798 | 61.6241 | 1.4211e-13 | -0.0039487 | 0.0018804 | 0.065468 | -0.0064613 | 0.061208 | -0.006028 | -0.0028861 | -0.0019187 | 0.069792 | 0.018391 | 0.061917 | -61.6515 | -0.003172 | -61.8152 | 61.5857 | 61.3854 | 61.5136 | -61.8053 | -61.7245 | 0.000359 | -61.7865 | 61.4226 | 61.5593 | 60.9444 | -62.0057 | -0.025491 | -0.038485 | 0.12826 | -0.035412 | -0.009921 | -0.23873 | -0.11059 | -0.22587 | -0.20154 | 0.055245 | -0.006732 | 0.21914 | -0.064864 | -0.67977 | 123.3654 | 123.1652 | 123.2933 | 61.7766 | -123.4294 | 123.2024 | 123.3391 | 122.7242 | 61.7801 | -123.6298
378.3438 | 123.5458 | -61.7523 | 61.6425 | 1.4211e-13 | -0.0037351 | 0.0018804 | 0.065041 | -0.0064613 | 0.060994 | 0.0016025 | -0.0028861 | -0.0017051 | 0.070006 | 0.018391 | 0.06213 | -61.6515 | -0.012329 | -61.8198 | 61.5811 | 61.3946 | 61.5227 | -61.8007 | -61.7291 | 0.000359 | -61.7911 | 61.4226 | 61.5593 | 60.949 | -61.9965 | -0.048378 | -0.061374 | 0.1008 | -0.067456 | -0.019078 | -0.24788 | -0.11975 | -0.24418 | -0.21985 | 0.0232 | -0.038777 | 0.2054 | -0.083174 | -0.69351 | 123.3334 | 123.1469 | 123.275 | 61.74 | -123.4432 | 123.1749 | 123.3116 | 122.7013 | 61.7527 | -123.639
380.0938 | 123.5229 | -61.7752 | 61.6516 | 1.4211e-13 | -0.0041623 | 0.0018804 | 0.065041 | -0.0064613 | 0.061208 | -0.006028 | -0.0028861 | -0.0017051 | 0.070006 | 0.018391 | 0.06213 | -61.6469 | -0.007751 | -61.8198 | 61.5719 | 61.3854 | 61.5181 | -61.7915 | -61.7245 | 0.009516 | -61.7865 | 61.418 | 61.5684 | 60.9444 | -61.9919 | -0.016331 | -0.079686 | 0.12826 | -0.044567 | -0.028236 | -0.26619 | -0.13348 | -0.21671 | -0.23358 | 0.050668 | -0.011309 | 0.2054 | -0.083172 | -0.70724 | 123.3471 | 123.1606 | 123.2933 | 61.7675 | -123.4432 | 123.1932 | 123.3436 | 122.7196 | 61.7847 | -123.6435
381.8438 | 123.6053 | -61.8027 | 61.5921 | 1.4211e-13 | -0.0039487 | 0.0018804 | 0.065255 | -0.0064613 | 0.060994 | 0.0016025 | -0.0026725 | -0.0017051 | 0.07022 | 0.018391 | 0.06213 | -61.6469 | -0.007751 | -61.806 | 61.5811 | 61.3808 | 61.5273 | -61.7961 | -61.7245 | -0.00422 | -61.7865 | 61.418 | 61.5684 | 60.9398 | -61.9965 | 0.006555 | -0.01102 | 0.15573 | -0.003367 | -0.009922 | -0.21126 | -0.064812 | -0.19382 | -0.17407 | 0.078133 | 0.016156 | 0.20998 | -0.023663 | -0.65231 | 123.3838 | 123.1835 | 123.33 | 61.7949 | -123.3882 | 123.2207 | 123.3711 | 122.7425 | 61.7985 | -123.5886
383.5156 | 123.4909 | -61.7615 | 61.6425 | 1.4211e-13 | -0.0041623 | 0.002094 | 0.065041 | -0.0066749 | 0.060994 | -0.006028 | -0.0026725 | -0.0017051 | 0.070433 | 0.018818 | 0.06213 | -61.6515 | -0.003172 | -61.806 | 61.5765 | 61.3854 | 61.5136 | -61.7915 | -61.7154 | -0.00422 | -61.7819 | 61.418 | 61.5593 | 60.9352 | -61.9965 | -0.030064 | -0.065952 | 0.10995 | -0.044565 | -0.014501 | -0.25704 | -0.1289 | -0.23502 | -0.22443 | 0.046092 | -0.020464 | 0.21456 | -0.083174 | -0.70724 | 123.338 | 123.1469 | 123.275 | 61.7583 | -123.434 | 123.1795 | 123.3208 | 122.6967 | 61.7573 | -123.639
385.2656 | 123.4909 | -61.7752 | 61.6653 | 1.4211e-13 | -0.0041623 | 0.0018804 | 0.065468 | -0.0066749 | 0.061422 | -0.013659 | -0.0028861 | -0.0017051 | 0.070433 | 0.018818 | 0.061917 | -61.6424 | -0.003172 | -61.8106 | 61.5765 | 61.3717 | 61.5181 | -61.7961 | -61.7154 | -0.00422 | -61.7865 | 61.418 | 61.5593 | 60.9352 | -61.9965 | -0.02091 | -0.08884 | 0.13284 | -0.03541 | -0.0145 | -0.29366 | -0.14721 | -0.22129 | -0.24731 | 0.059825 | -0.011309 | 0.20998 | -0.10606 | -0.73013 | 123.3517 | 123.1469 | 123.2933 | 61.772 | -123.4615 | 123.1932 | 123.3345 | 122.7104 | 61.771 | -123.6618
387 | 123.5046 | -61.7889 | 61.615 | 1.4211e-13 | -0.0035213 | 0.0018804 | 0.065255 | -0.0066749 | 0.060994 | -0.021289 | -0.0028861 | -0.0014913 | 0.07022 | 0.018818 | 0.062344 | -61.6515 | -0.007751 | -61.806 | 61.5719 | 61.3763 | 61.5181 | -61.7961 | -61.7154 | -0.00422 | -61.7819 | 61.418 | 61.5593 | 60.9352 | -61.9919 | -0.007178 | -0.043065 | 0.13742 | -0.0171 | -0.009922 | -0.23873 | -0.096857 | -0.20298 | -0.19696 | 0.073557 | 0.007001 | 0.20998 | -0.055708 | -0.67978 | 123.3609 | 123.1652 | 123.3071 | 61.7812 | -123.4111 | 123.207 | 123.3482 | 122.7242 | 61.7847 | -123.6069
388.6719 | 123.5458 | -61.7523 | 61.647 | 1.4211e-13 | -0.0041623 | 0.0016666 | 0.065255 | -0.0064613 | 0.060994 | 0.0016025 | -0.0028861 | -0.0019187 | 0.070006 | 0.018605 | 0.061917 | -61.6424 | -0.012329 | -61.806 | 61.5811 | 61.4083 | 61.5136 | -61.8007 | -61.72 | 0.004938 | -61.7911 | 61.4089 | 61.5639 | 60.9398 | -61.9919 | -0.048378 | -0.065952 | 0.10995 | -0.053721 | -0.005343 | -0.23872 | -0.13348 | -0.2396 | -0.23816 | 0.032358 | -0.038777 | 0.20082 | -0.083174 | -0.70724 | 123.3334 | 123.1606 | 123.2659 | 61.74 | -123.4477 | 123.1612 | 123.3162 | 122.6921 | 61.7573 | -123.639
390.4219 | 123.6191 | -61.7798 | 61.5646 | 1.4211e-13 | -0.0039487 | 0.0018804 | 0.065255 | -0.0062475 | 0.060994 | 0.0016025 | -0.0028861 | -0.0014913 | 0.069792 | 0.018605 | 0.062558 | -61.6378 | -0.003172 | -61.8106 | 61.5811 | 61.3992 | 61.5181 | -61.7915 | -61.7154 | 0.009516 | -61.7819 | 61.4043 | 61.5593 | 60.9352 | -61.9965 | -0.011754 | 0.016446 | 0.142 | -0.030833 | -0.019079 | -0.16548 | -0.046503 | -0.21671 | -0.16034 | 0.064402 | -0.002154 | 0.21456 | -0.005354 | -0.62942 | 123.3609 | 123.1789 | 123.2979 | 61.7766 | -123.3562 | 123.1841 | 123.3391 | 122.715 | 61.7893 | -123.5611
392.1094 | 123.5046 | -61.8118 | 61.5967 | 1.4211e-13 | -0.0037351 | 0.002094 | 0.065041 | -0.0062475 | 0.061208 | 0.0016025 | -0.0030999 | -0.0017051 | 0.07022 | 0.018391 | 0.062344 | -61.6378 | 0.001407 | -61.8015 | 61.5765 | 61.4083 | 61.5136 | -61.787 | -61.7108 | 0.000359 | -61.7728 | 61.4043 | 61.5593 | 60.9352 | -61.9873 | 0.024869 | -0.020176 | 0.17404 | 0.010367 | -0.014502 | -0.18836 | -0.083126 | -0.17551 | -0.19239 | 0.10102 | 0.039048 | 0.21456 | -0.037398 | -0.66147 | 123.3883 | 123.2201 | 123.3254 | 61.8132 | -123.3836 | 123.2161 | 123.3711 | 122.747 | 61.8122 | -123.584
393.8594 | 123.5916 | -61.7935 | 61.5738 | 1.4211e-13 | -0.0041623 | 0.002094 | 0.065255 | -0.0062475 | 0.061208 | 0.0016025 | -0.0030999 | -0.0021323 | 0.07022 | 0.018391 | 0.06213 | -61.6424 | 0.001407 | -61.8015 | 61.5765 | 61.3946 | 61.5136 | -61.7961 | -61.7108 | 0.004938 | -61.7819 | 61.418 | 61.5547 | 60.9398 | -61.9919 | -0.0026 | 0.002712 | 0.15115 | -0.007944 | -0.005344 | -0.17921 | -0.060238 | -0.1984 | -0.15576 | 0.082714 | 0.011579 | 0.20998 | -0.019089 | -0.634 | 123.37 | 123.1881 | 123.3071 | 61.7949 | -123.3699 | 123.2115 | 123.3482 | 122.7333 | 61.7985 | -123.5657
395.5469 | 123.4726 | -61.7661 | 61.647 | 1.4211e-13 | -0.0039487 | 0.0018804 | 0.065041 | -0.0062475 | 0.061208 | -0.006028 | -0.0030999 | -0.0017051 | 0.07022 | 0.018391 | 0.062558 | -61.6378 | -0.012329 | -61.806 | 61.5719 | 61.39 | 61.5227 | -61.787 | -61.7062 | 0.000359 | -61.7774 | 61.4135 | 61.5593 | 60.9306 | -61.9919 | -0.020908 | -0.075109 | 0.12826 | -0.039988 | -0.01908 | -0.25703 | -0.12432 | -0.22586 | -0.23358 | 0.059827 | -0.011308 | 0.21456 | -0.087752 | -0.7164 | 123.338 | 123.1561 | 123.2888 | 61.7537 | -123.434 | 123.1795 | 123.3253 | 122.6967 | 61.7664 | -123.639
397.2969 | 123.555 | -61.7798 | 61.5967 | 1.4211e-13 | -0.0037351 | 0.0023076 | 0.065041 | -0.0066749 | 0.061208 | -0.006028 | -0.0028861 | -0.0017051 | 0.07022 | 0.018818 | 0.06213 | -61.6332 | -0.012329 | -61.8015 | 61.5719 | 61.39 | 61.5181 | -61.7915 | -61.72 | -0.00422 | -61.7819 | 61.4089 | 61.5593 | 60.9352 | -61.9828 | -0.011754 | -0.024755 | 0.14657 | -0.021677 | -0.009923 | -0.20668 | -0.078547 | -0.20298 | -0.18781 | 0.059824 | -0.002154 | 0.20082 | -0.037398 | -0.66147 | 123.3517 | 123.1698 | 123.2979 | 61.7675 | -123.3882 | 123.1887 | 123.3391 | 122.715 | 61.7756 | -123.5794
399.0469 | 123.4726 | -61.7477 | 61.647 | 1.4211e-13 | -0.0043761 | 0.0018804 | 0.065255 | -0.0064613 | 0.060994 | 0.0016025 | -0.0028861 | -0.0019187 | 0.07022 | 0.018818 | 0.061917 | -61.6332 | -0.007751 | -61.7969 | 61.5719 | 61.3992 | 61.5136 | -61.7915 | -61.7154 | 0.000359 | -61.7774 | 61.4135 | 61.5593 | 60.9352 | -61.9873 | -0.043797 | -0.075109 | 0.11453 | -0.049142 | -0.005345 | -0.24788 | -0.13348 | -0.2396 | -0.23358 | 0.032359 | -0.029618 | 0.20998 | -0.087752 | -0.71182 | 123.3197 | 123.1469 | 123.2613 | 61.74 | -123.4386 | 123.1612 | 123.307 | 122.683 | 61.7481 | -123.6344
400.7969 | 123.468 | -61.7798 | 61.6013 | 1.4211e-13 | -0.0041623 | 0.0023076 | 0.065041 | -0.0064613 | 0.060567 | 0.0092325 | -0.0033135 | -0.0017051 | 0.070006 | 0.018818 | 0.062344 | -61.6241 | -0.016908 | -61.8015 | 61.5719 | 61.3808 | 61.509 | -61.7824 | -61.7062 | 0.004938 | -61.7728 | 61.4135 | 61.5547 | 60.9306 | -61.9873 | -0.002596 | -0.029332 | 0.15573 | -0.021677 | -0.019081 | -0.22041 | -0.092281 | -0.20755 | -0.18781 | 0.07356 | 0.007004 | 0.21456 | -0.046554 | -0.67062 | 123.3517 | 123.1606 | 123.2888 | 61.7629 | -123.3836 | 123.1932 | 123.3345 | 122.7104 | 61.7847 | -123.5886
402.4844 | 123.5962 | -61.7569 | 61.5875 | 1.4211e-13 | -0.0037351 | 0.0016666 | 0.065255 | -0.0066749 | 0.060781 | 0.0016025 | -0.0026725 | -0.0017051 | 0.07022 | 0.018605 | 0.06213 | -61.6378 | 0.001407 | -61.8015 | 61.5673 | 61.3946 | 61.5181 | -61.7778 | -61.7062 | 0.004938 | -61.7682 | 61.4089 | 61.5547 | 60.9306 | -61.9828 | -0.020905 | -0.020177 | 0.11911 | -0.044565 | -0.02366 | -0.19295 | -0.069391 | -0.22586 | -0.17865 | 0.050672 | -0.011306 | 0.21456 | -0.032821 | -0.65689 | 123.3242 | 123.1515 | 123.275 | 61.7583 | -123.3653 | 123.1658 | 123.3116 | 122.6875 | 61.7618 | -123.5703
404.2344 | 123.4772 | -61.7752 | 61.6241 | 1.4211e-13 | -0.0039487 | 0.0016666 | 0.064827 | -0.0066749 | 0.060994 | -0.006028 | -0.0030999 | -0.0019187 | 0.07022 | 0.018605 | 0.06213 | -61.6286 | -0.007751 | -61.7923 | 61.5628 | 61.4083 | 61.509 | -61.7732 | -61.7016 | 0.004938 | -61.7728 | 61.4043 | 61.5593 | 60.9306 | -61.9828 | 0.001985 | -0.061377 | 0.14658 | -0.017097 | -0.019082 | -0.21583 | -0.11517 | -0.20755 | -0.21985 | 0.073562 | 0.002427 | 0.20998 | -0.064864 | -0.69351 | 123.338 | 123.1835 | 123.2842 | 61.7675 | -123.3974 | 123.1795 | 123.3345 | 122.7058 | 61.7801 | -123.6069
405.9844 | 123.5596 | -61.7386 | 61.5601 | 1.4211e-13 | -0.0041623 | 0.0018804 | 0.065255 | -0.0064613 | 0.060994 | -0.006028 | -0.0033135 | -0.0014913 | 0.07022 | 0.019032 | 0.06213 | -61.6378 | -0.007751 | -61.806 | 61.5719 | 61.4175 | 61.5136 | -61.787 | -61.7062 | 0.004938 | -61.7682 | 61.4043 | 61.5547 | 60.9306 | -61.9828 | -0.048374 | 0.011866 | 0.1008 | -0.067454 | -0.01908 | -0.14259 | -0.046505 | -0.24417 | -0.15577 | 0.032361 | -0.029617 | 0.21456 | -0.005356 | -0.62942 | 123.3105 | 123.1561 | 123.2521 | 61.7308 | -123.347 | 123.1429 | 123.2933 | 122.6692 | 61.7435 | -123.5428
407.6719 | 123.5916 | -61.7615 | 61.5097 | 1.4211e-13 | -0.0039487 | 0.0016666 | 0.065041 | -0.0066749 | 0.060994 | -0.006028 | -0.0028861 | -0.0017051 | 0.070006 | 0.018818 | 0.06213 | -61.6332 | -0.003172 | -61.7877 | 61.5673 | 61.4037 | 61.509 | -61.7732 | -61.7016 | 0.004938 | -61.7636 | 61.3997 | 61.5501 | 60.9306 | -61.9782 | -0.011748 | 0.057642 | 0.12826 | -0.026252 | -0.014504 | -0.10597 | -0.000729 | -0.21671 | -0.10999 | 0.059829 | -0.002149 | 0.21456 | 0.040419 | -0.57907 | 123.3288 | 123.1652 | 123.2705 | 61.7583 | -123.2829 | 123.1612 | 123.3116 | 122.6921 | 61.7664 | -123.4879
409.4219 | 123.5916 | -61.7569 | 61.5646 | 1.4211e-13 | -0.0041623 | 0.002094 | 0.065255 | -0.0066749 | 0.060994 | -0.006028 | -0.0028861 | -0.0019187 | 0.07022 | 0.019032 | 0.062344 | -61.6332 | -0.007751 | -61.7923 | 61.5628 | 61.4083 | 61.5136 | -61.7778 | -61.7016 | 0.004938 | -61.759 | 61.4089 | 61.5547 | 60.9352 | -61.9828 | -0.020905 | -0.001867 | 0.12369 | -0.035408 | -0.014503 | -0.15632 | -0.051082 | -0.22586 | -0.15576 | 0.055251 | -0.002148 | 0.22371 | -0.009933 | -0.62942 | 123.3197 | 123.1652 | 123.2705 | 61.7491 | -123.3424 | 123.1658 | 123.3116 | 122.6921 | 61.7618 | -123.5474
411.1719 | 123.5184 | -61.734 | 61.6379 | 1.4211e-13 | -0.0037351 | 0.0023076 | 0.065255 | -0.0062475 | 0.060994 | -0.006028 | -0.0028861 | -0.0019187 | 0.07022 | 0.018818 | 0.06213 | -61.6241 | -0.003172 | -61.7877 | 61.5719 | 61.3763 | 61.5181 | -61.7732 | -61.6925 | 0.009516 | -61.7682 | 61.418 | 61.5501 | 60.9306 | -61.969 | -0.039214 | -0.065953 | 0.10996 | -0.053718 | -0.014504 | -0.26161 | -0.11975 | -0.23501 | -0.21985 | 0.04152 | -0.034194 | 0.20082 | -0.087754 | -0.70724 | 123.3059 | 123.1103 | 123.2521 | 61.7308 | -123.4111 | 123.152 | 123.2841 | 122.6646 | 61.7435 | -123.6069
412.9062 | 123.468 | -61.7798 | 61.6058 | 1.4211e-13 | -0.0041623 | 0.002094 | 0.065468 | -0.0064613 | 0.061422 | -0.006028 | -0.0028861 | -0.0014913 | 0.070006 | 0.018818 | 0.06213 | -61.6149 | -0.003172 | -61.7877 | 61.5719 | 61.3992 | 61.5227 | -61.7732 | -61.7016 | 0.004938 | -61.7636 | 61.418 | 61.5593 | 60.9306 | -61.9644 | 0.006562 | -0.03391 | 0.16489 | -0.007942 | -0.014504 | -0.20668 | -0.083124 | -0.18466 | -0.1878 | 0.078139 | 0.016161 | 0.20082 | -0.046553 | -0.6752 | 123.3517 | 123.1789 | 123.3025 | 61.7766 | -123.3791 | 123.1978 | 123.3391 | 122.7104 | 61.7847 | -123.5703
414.5781 | 123.5458 | -61.7706 | 61.5738 | 1.4211e-13 | -0.0041623 | 0.0018804 | 0.065041 | -0.0068885 | 0.061422 | 0.0016025 | -0.0028861 | -0.0021323 | 0.070006 | 0.018818 | 0.06213 | -61.6012 | -0.003172 | -61.7831 | 61.5765 | 61.39 | 61.5227 | -61.7641 | -61.6879 | 0.004938 | -61.7545 | 61.418 | 61.5639 | 60.9444 | -61.9599 | 0.006565 | 0.002712 | 0.16947 | -0.012519 | -0.019084 | -0.18379 | -0.051081 | -0.18924 | -0.15576 | 0.08272 | 0.016164 | 0.2054 | -0.009932 | -0.62942 | 123.3471 | 123.1606 | 123.2933 | 61.7675 | -123.3379 | 123.1887 | 123.3345 | 122.715 | 61.7756 | -123.5337
416.3281 | 123.5916 | -61.7432 | 61.5555 | 1.4211e-13 | -0.0041623 | 0.0023076 | 0.065041 | -0.0068885 | 0.061208 | 0.0016025 | -0.0026725 | -0.0019187 | 0.07022 | 0.018818 | 0.062558 | -61.6149 | -0.007751 | -61.7831 | 61.5811 | 61.3992 | 61.5181 | -61.7686 | -61.6833 | 0.004938 | -61.7453 | 61.4135 | 61.5684 | 60.9398 | -61.969 | -0.02548 | 0.025601 | 0.12827 | -0.039985 | -0.014505 | -0.15632 | -0.037348 | -0.22586 | -0.14203 | 0.059832 | -0.002145 | 0.22371 | 0.012958 | -0.61569 | 123.3242 | 123.1423 | 123.2613 | 61.7354 | -123.3241 | 123.1566 | 123.3116 | 122.683 | 61.7481 | -123.5245
418.0781 | 123.587 | -61.7615 | 61.5417 | 1.4211e-13 | -0.0039487 | 0.0018804 | 0.065255 | -0.0060339 | 0.061208 | -0.021289 | -0.0028861 | -0.0019187 | 0.07022 | 0.018818 | 0.06213 | -61.6149 | 0.001407 | -61.774 | 61.5628 | 61.4037 | 61.5181 | -61.7641 | -61.6925 | 0.004938 | -61.7545 | 61.4043 | 61.5501 | 60.9261 | -61.9736 | -0.00259 | 0.021021 | 0.14658 | -0.012517 | -0.009927 | -0.13801 | -0.023615 | -0.21213 | -0.13745 | 0.068986 | 0.007009 | 0.21914 | 0.008376 | -0.61569 | 123.3242 | 123.1652 | 123.2796 | 61.7629 | -123.3058 | 123.1658 | 123.3116 | 122.6875 | 61.7664 | -123.5153
419.8281 | 123.5779 | -61.7523 | 61.5326 | 1.4211e-13 | -0.0045897 | 0.0018804 | 0.064827 | -0.0064613 | 0.061208 | 0.0016025 | -0.0030999 | -0.0019187 | 0.070006 | 0.019246 | 0.06213 | -61.6195 | -0.003172 | -61.7831 | 61.5765 | 61.39 | 61.5136 | -61.7641 | -61.6925 | 0.004938 | -61.7545 | 61.4043 | 61.5547 | 60.9306 | -61.9644 | -0.011746 | 0.043911 | 0.13284 | -0.03083 | -0.019084 | -0.14259 | -0.019039 | -0.21213 | -0.1283 | 0.05983 | -0.002147 | 0.20998 | 0.02211 | -0.60196 | 123.3288 | 123.1423 | 123.2659 | 61.7491 | -123.2967 | 123.1566 | 123.307 | 122.683 | 61.7573 | -123.497
421.5 | 123.5825 | -61.7523 | 61.5555 | 1.4211e-13 | -0.0041623 | 0.002094 | 0.065468 | -0.0062475 | 0.060994 | -0.013659 | -0.0028861 | -0.0017051 | 0.070647 | 0.018605 | 0.061703 | -61.5966 | -0.012329 | -61.7694 | 61.5811 | 61.4312 | 61.5273 | -61.7458 | -61.665 | 0.004938 | -61.7362 | 61.418 | 61.573 | 60.949 | -61.9599 | 0.006569 | 0.025601 | 0.15574 | -0.017095 | -0.023664 | -0.12427 | -0.028191 | -0.20755 | -0.13745 | 0.087302 | 0.016167 | 0.22371 | 0.017536 | -0.60653 | 123.3334 | 123.1835 | 123.2796 | 61.74 | -123.3012 | 123.1703 | 123.3253 | 122.7013 | 61.7573 | -123.5153
423.25 | 123.4497 | -61.7477 | 61.6013 | 1.4211e-13 | -0.0041623 | 0.002094 | 0.065041 | -0.0064613 | 0.060781 | 0.0016025 | -0.0028861 | -0.0019187 | 0.070006 | 0.019246 | 0.061917 | -61.6241 | -0.012329 | -61.7877 | 61.5628 | 61.4129 | 61.509 | -61.7686 | -61.6925 | 0.000359 | -61.7499 | 61.3951 | 61.5455 | 60.9261 | -61.969 | -0.020902 | -0.038488 | 0.12369 | -0.039985 | -0.019083 | -0.18836 | -0.092281 | -0.22128 | -0.20612 | 0.055253 | -0.002146 | 0.21914 | -0.055711 | -0.6752 | 123.3105 | 123.1606 | 123.2567 | 61.7354 | -123.3699 | 123.1429 | 123.2933 | 122.6738 | 61.7481 | -123.5703
425.0156 | 123.436 | -61.734 | 61.6241 | 1.4211e-13 | -0.0039487 | 0.0018804 | 0.065255 | -0.0062475 | 0.060781 | -0.021289 | -0.0028861 | -0.0019187 | 0.070006 | 0.019246 | 0.061703 | -61.6149 | -0.007751 | -61.7923 | 61.5536 | 61.4129 | 61.4952 | -61.7641 | -61.6879 | 0.000359 | -61.759 | 61.4043 | 61.5501 | 60.9261 | -61.9736 | -0.030056 | -0.070534 | 0.11911 | -0.058296 | -0.02824 | -0.21125 | -0.12891 | -0.23959 | -0.21985 | 0.046099 | -0.025036 | 0.21456 | -0.074022 | -0.69809 | 123.2876 | 123.1469 | 123.2292 | 61.7263 | -123.3882 | 123.1383 | 123.2841 | 122.6601 | 61.7344 | -123.5977
426.7656 | 123.4497 | -61.7477 | 61.647 | 1.4211e-13 | -0.0043761 | 0.002094 | 0.065468 | -0.0068885 | 0.060994 | 0.0016025 | -0.0028861 | -0.0017051 | 0.070006 | 0.019032 | 0.061703 | -61.6149 | -0.007751 | -61.7877 | 61.5582 | 61.3992 | 61.4998 | -61.7595 | -61.6879 | 0.000359 | -61.7545 | 61.3951 | 61.541 | 60.9261 | -61.9736 | -0.011745 | -0.088844 | 0.13285 | -0.039985 | -0.02824 | -0.24788 | -0.14722 | -0.22586 | -0.2519 | 0.059832 | -0.006724 | 0.21914 | -0.10607 | -0.72098 | 123.3059 | 123.1469 | 123.2476 | 61.74 | -123.4065 | 123.1429 | 123.2887 | 122.6738 | 61.7481 | -123.6206
428.4531 | 123.4909 | -61.734 | 61.6241 | 1.4211e-13 | -0.0041623 | 0.0023076 | 0.065041 | -0.0064613 | 0.061208 | 0.0016025 | -0.0026725 | -0.0017051 | 0.070006 | 0.018818 | 0.061703 | -61.6103 | -0.007751 | -61.7831 | 61.5582 | 61.39 | 61.5044 | -61.7686 | -61.6879 | 0.000359 | -61.7453 | 61.386 | 61.5455 | 60.9215 | -61.969 | -0.034635 | -0.065956 | 0.12369 | -0.04914 | -0.014505 | -0.23415 | -0.11975 | -0.23501 | -0.23817 | 0.046099 | -0.0113 | 0.22371 | -0.0786 | -0.70267 | 123.2922 | 123.124 | 123.2384 | 61.7263 | -123.3928 | 123.12 | 123.2796 | 122.6555 | 61.7344 | -123.5932
430.2188 | 123.4406 | -61.7752 | 61.6196 | 1.4211e-13 | -0.0041623 | 0.002094 | 0.065468 | -0.0066749 | 0.061208 | 0.0016025 | -0.0026725 | -0.0014913 | 0.070433 | 0.018818 | 0.061703 | -61.6103 | 0.001407 | -61.7877 | 61.5536 | 61.3946 | 61.4998 | -61.7641 | -61.6879 | 0.000359 | -61.7499 | 61.3951 | 61.5547 | 60.9215 | -61.9644 | 0.011143 | -0.065956 | 0.16489 | -0.012519 | -0.023662 | -0.22499 | -0.11975 | -0.18924 | -0.22443 | 0.087298 | 0.02532 | 0.21456 | -0.064865 | -0.69809 | 123.3288 | 123.1698 | 123.275 | 61.7766 | -123.3836 | 123.1703 | 123.3299 | 122.6967 | 61.7756 | -123.584
431.9531 | 123.5184 | -61.7661 | 61.5417 | 1.4211e-13 | -0.0039487 | 0.0018804 | 0.065255 | -0.0066749 | 0.061422 | -0.013659 | -0.0030999 | -0.0017051 | 0.070006 | 0.019246 | 0.061703 | -61.6057 | 0.001407 | -61.774 | 61.5582 | 61.4221 | 61.5044 | -61.7595 | -61.6925 | 0.000359 | -61.7545 | 61.3951 | 61.5455 | 60.9261 | -61.9644 | 0.006565 | 0.016442 | 0.16031 | -0.00794 | -0.014505 | -0.1197 | -0.037351 | -0.19839 | -0.14661 | 0.073563 | 0.011586 | 0.20998 | 0.003798 | -0.61569 | 123.3242 | 123.1881 | 123.2704 | 61.7675 | -123.3012 | 123.1612 | 123.3116 | 122.6921 | 61.7664 | -123.5062
433.625 | 123.436 | -61.734 | 61.6241 | 1.4211e-13 | -0.0041623 | 0.001453 | 0.065468 | -0.0064613 | 0.061208 | 0.0016025 | -0.0028861 | -0.0014913 | 0.07022 | 0.019459 | 0.061917 | -61.6103 | -0.003172 | -61.7786 | 61.5536 | 61.4037 | 61.5044 | -61.7549 | -61.6833 | 0.004938 | -61.7545 | 61.3997 | 61.5501 | 60.9169 | -61.9644 | -0.020899 | -0.070534 | 0.12369 | -0.044561 | -0.023662 | -0.22041 | -0.11975 | -0.23043 | -0.22443 | 0.050677 | -0.020457 | 0.20998 | -0.074022 | -0.70725 | 123.2876 | 123.1377 | 123.2384 | 61.7308 | -123.3791 | 123.1337 | 123.2841 | 122.6509 | 61.7389 | -123.5886
435.3594 | 123.468 | -61.7432 | 61.6379 | 1.4211e-13 | -0.0043761 | 0.0018804 | 0.065468 | -0.0064613 | 0.060994 | -0.013659 | -0.0028861 | -0.0017051 | 0.070647 | 0.018818 | 0.061703 | -61.6057 | -0.003172 | -61.7694 | 61.5536 | 61.3854 | 61.4998 | -61.7549 | -61.6788 | 0.000359 | -61.7407 | 61.3997 | 61.5501 | 60.9215 | -61.969 | -0.011744 | -0.084266 | 0.13742 | -0.02625 | -0.014506 | -0.25246 | -0.13806 | -0.22586 | -0.23816 | 0.064411 | 0.002434 | 0.22829 | -0.087754 | -0.7164 | 123.2968 | 123.1286 | 123.243 | 61.74 | -123.3928 | 123.1429 | 123.2933 | 122.6646 | 61.7435 | -123.6069
437.0938 | 123.4955 | -61.7157 | 61.6013 | 1.4211e-13 | -0.0043761 | 0.0016666 | 0.065468 | -0.0062475 | 0.060994 | -0.013659 | -0.0030999 | -0.0017051 | 0.070433 | 0.019032 | 0.061703 | -61.6057 | -0.007751 | -61.774 | 61.5582 | 61.3763 | 61.4998 | -61.7549 | -61.6788 | 0.000359 | -61.7407 | 61.3951 | 61.541 | 60.9169 | -61.9599 | -0.03921 | -0.043067 | 0.10996 | -0.058294 | -0.019084 | -0.22499 | -0.10144 | -0.24417 | -0.20612 | 0.036945 | -0.025032 | 0.21914 | -0.06029 | -0.68436 | 123.2739 | 123.092 | 123.2155 | 61.7079 | -123.3562 | 123.1108 | 123.2567 | 122.6326 | 61.7161 | -123.5611
438.8438 | 123.4085 | -61.734 | 61.6562 | 1.4211e-13 | -0.0041623 | 0.0016666 | 0.065255 | -0.0066749 | 0.061635 | -0.006028 | -0.0030999 | -0.0019187 | 0.07022 | 0.019032 | 0.061703 | -61.5828 | -0.003172 | -61.7465 | 61.5765 | 61.4312 | 61.5227 | -61.7366 | -61.6604 | 0.004938 | -61.7224 | 61.4089 | 61.5547 | 60.9352 | -61.9461 | -0.002583 | -0.079685 | 0.15116 | -0.012513 | -0.00993 | -0.22498 | -0.13348 | -0.21212 | -0.24732 | 0.073571 | 0.011594 | 0.22371 | -0.10149 | -0.72097 | 123.3105 | 123.1652 | 123.2567 | 61.7308 | -123.3928 | 123.1429 | 123.2887 | 122.6692 | 61.7389 | -123.6023
440.5312 | 123.4131 | -61.734 | 61.6241 | 1.4211e-13 | -0.0043761 | 0.0018804 | 0.065041 | -0.0068885 | 0.061635 | 0.0092325 | -0.0028861 | -0.0017051 | 0.070006 | 0.019032 | 0.061917 | -61.5828 | -0.007751 | -61.7511 | 61.5719 | 61.4587 | 61.5181 | -61.7366 | -61.6604 | 0.004938 | -61.7316 | 61.4043 | 61.5593 | 60.9444 | -61.9461 | -0.002583 | -0.052221 | 0.15116 | -0.017092 | -0.014509 | -0.16546 | -0.10601 | -0.21212 | -0.21985 | 0.073571 | 0.002436 | 0.21456 | -0.064864 | -0.67977 | 123.3059 | 123.1927 | 123.2521 | 61.7263 | -123.3607 | 123.1383 | 123.2933 | 122.6784 | 61.7389 | -123.5703
442.2812 | 123.4131 | -61.702 | 61.6333 | 1.4211e-13 | -0.0043761 | 0.002094 | 0.065468 | -0.0064613 | 0.061422 | -0.006028 | -0.0028861 | -0.0019187 | 0.07022 | 0.019032 | 0.061703 | -61.5828 | -0.003172 | -61.7557 | 61.5719 | 61.3946 | 61.5227 | -61.7229 | -61.6559 | 0.000359 | -61.7224 | 61.4135 | 61.5547 | 60.9398 | -61.9415 | -0.02089 | -0.061376 | 0.11912 | -0.053714 | -0.032824 | -0.23872 | -0.11059 | -0.23958 | -0.21985 | 0.046106 | -0.02045 | 0.21914 | -0.078598 | -0.69351 | 123.2739 | 123.0965 | 123.2247 | 61.6988 | -123.3562 | 123.1154 | 123.2567 | 122.6418 | 61.7023 | -123.5749
444.0312 | 123.4085 | -61.7157 | 61.6425 | 1.4211e-13 | -0.0041623 | 0.001453 | 0.065255 | -0.0066749 | 0.061422 | -0.013659 | -0.0033135 | -0.0019187 | 0.070006 | 0.019032 | 0.061703 | -61.5783 | -0.003172 | -61.7419 | 61.5811 | 61.4587 | 61.5319 | -61.7274 | -61.6467 | 0.000359 | -61.7133 | 61.418 | 61.5776 | 60.9444 | -61.9324 | -0.011736 | -0.061374 | 0.13743 | -0.026246 | -0.01451 | -0.18377 | -0.11059 | -0.21669 | -0.22443 | 0.068996 | 0.00244 | 0.21913 | -0.06486 | -0.69808 | 123.2968 | 123.1744 | 123.2476 | 61.7125 | -123.3699 | 123.1337 | 123.2933 | 122.6601 | 61.7161 | -123.5748
445.7812 | 123.5504 | -61.6974 | 61.5784 | 1.4211e-13 | -0.0041623 | 0.0018804 | 0.065255 | -0.0062475 | 0.061422 | -0.013659 | -0.0030999 | -0.0019187 | 0.070433 | 0.019032 | 0.061276 | -61.5691 | 0.001407 | -61.7328 | 61.5811 | 61.4312 | 61.5227 | -61.7229 | -61.6375 | 0.000359 | -61.7087 | 61.4226 | 61.5639 | 60.9581 | -61.9324 | -0.025467 | 0.002713 | 0.12828 | -0.0354 | -0.009933 | -0.14716 | -0.055658 | -0.23501 | -0.15576 | 0.059844 | -0.011291 | 0.22371 | -0.014509 | -0.62026 | 123.2785 | 123.1286 | 123.2201 | 61.6988 | -123.3012 | 123.12 | 123.2612 | 122.6555 | 61.6977 | -123.5108
447.4531 | 123.4406 | -61.6745 | 61.6653 | 1.4211e-13 | -0.0041623 | 0.002094 | 0.065255 | -0.0066749 | 0.061422 | 0.0016025 | -0.0030999 | -0.0019187 | 0.07022 | 0.019459 | 0.061276 | -61.5508 | 0.001407 | -61.7328 | 61.5857 | 61.4678 | 61.5364 | -61.7137 | -61.6375 | -0.00422 | -61.7087 | 61.4272 | 61.5776 | 60.9535 | -61.9187 | -0.039197 | -0.079683 | 0.1237 | -0.058288 | -0.019091 | -0.1975 | -0.1289 | -0.24416 | -0.23816 | 0.036956 | -0.034179 | 0.20998 | -0.087748 | -0.71181 | 123.2602 | 123.1423 | 123.2109 | 61.6759 | -123.379 | 123.1017 | 123.2521 | 122.628 | 61.6703 | -123.584
449.125 | 123.4863 | -61.702 | 61.5784 | 1.4211e-13 | -0.0045897 | 0.0018804 | 0.065255 | -0.0066749 | 0.062063 | -0.006028 | -0.0028861 | -0.0019187 | 0.07022 | 0.019032 | 0.061917 | -61.5462 | -0.003172 | -61.7191 | 61.604 | 61.4862 | 61.5548 | -61.7045 | -61.6284 | 0.004938 | -61.6949 | 61.4318 | 61.5913 | 60.9627 | -61.9095 | -0.002574 | 0.025605 | 0.15575 | -0.017088 | -0.014514 | -0.092211 | -0.023607 | -0.20753 | -0.1466 | 0.073578 | 0.007022 | 0.21456 | 0.012963 | -0.61568 | 123.3059 | 123.1881 | 123.2567 | 61.6988 | -123.2829 | 123.1337 | 123.2933 | 122.6647 | 61.7069 | -123.4879
450.875 | 123.4222 | -61.7203 | 61.6104 | 1.4211e-13 | -0.0043761 | 0.0023076 | 0.065041 | -0.0064613 | 0.061208 | 0.0092325 | -0.0030999 | -0.0019187 | 0.070433 | 0.019459 | 0.061489 | -61.5783 | -0.003172 | -61.7511 | 61.5719 | 61.4404 | 61.5136 | -61.7366 | -61.6559 | 0.004938 | -61.7224 | 61.3997 | 61.5455 | 60.9306 | -61.9461 | -0.016316 | -0.038488 | 0.14201 | -0.030825 | -0.014509 | -0.17005 | -0.096859 | -0.22585 | -0.2107 | 0.064417 | -0.002139 | 0.22371 | -0.064867 | -0.67978 | 123.2922 | 123.1606 | 123.2338 | 61.7171 | -123.347 | 123.12 | 123.2658 | 122.6509 | 61.7252 | -123.5565
452.6094 | 123.5138 | -61.7065 | 61.5601 | 1.4211e-13 | -0.0043761 | 0.002094 | 0.065255 | -0.0068885 | 0.061422 | -0.013659 | -0.0033135 | -0.0017051 | 0.07022 | 0.019246 | 0.061489 | -61.56 | -0.003172 | -61.7236 | 61.5857 | 61.4404 | 61.5319 | -61.7229 | -61.633 | 0.000359 | -61.6949 | 61.4226 | 61.5684 | 60.9444 | -61.9187 | -0.016312 | 0.025602 | 0.14659 | -0.017088 | -0.000776 | -0.11969 | -0.02819 | -0.21211 | -0.13745 | 0.073577 | 0.0116 | 0.22371 | 0.00838 | -0.61569 | 123.2922 | 123.1469 | 123.2384 | 61.7034 | -123.2829 | 123.1292 | 123.275 | 122.6509 | 61.7069 | -123.4787
454.3438 | 123.4772 | -61.734 | 61.5738 | 1.4211e-13 | -0.0043761 | 0.0018804 | 0.065255 | -0.0066749 | 0.061422 | -0.006028 | -0.0028861 | -0.0019187 | 0.07022 | 0.019032 | 0.061703 | -61.5554 | -0.007751 | -61.7328 | 61.5902 | 61.4633 | 61.5319 | -61.7045 | -61.633 | 0.000359 | -61.6995 | 61.4226 | 61.573 | 60.9444 | -61.9141 | 0.02947 | 0.016447 | 0.17863 | 0.001221 | -0.028249 | -0.11053 | -0.041923 | -0.18007 | -0.15118 | 0.10104 | 0.034487 | 0.21455 | -0.000775 | -0.62942 | 123.3242 | 123.1973 | 123.2659 | 61.7263 | -123.2783 | 123.1566 | 123.307 | 122.6784 | 61.7344 | -123.4879
456.0938 | 123.5458 | -61.7065 | 61.5646 | 1.4211e-13 | -0.0043761 | 0.0018804 | 0.065468 | -0.0068885 | 0.061635 | -0.006028 | -0.0030999 | -0.0019187 | 0.07022 | 0.019032 | 0.061703 | -61.5554 | -0.003172 | -61.7282 | 61.5857 | 61.4633 | 61.5319 | -61.7137 | -61.6238 | 0.004938 | -61.6995 | 61.4226 | 61.5776 | 60.9535 | -61.9141 | -0.007154 | 0.021025 | 0.15117 | -0.021666 | -0.014512 | -0.10137 | -0.032767 | -0.20753 | -0.14203 | 0.082735 | 0.007021 | 0.21455 | 0.01296 | -0.61111 | 123.2922 | 123.1698 | 123.2384 | 61.7034 | -123.2783 | 123.1292 | 123.2841 | 122.6601 | 61.7115 | -123.4787
457.8438 | 123.5229 | -61.6974 | 61.5967 | 1.4211e-13 | -0.0043761 | 0.002094 | 0.065041 | -0.0068885 | 0.061635 | -0.006028 | -0.0026725 | -0.0021323 | 0.070433 | 0.019459 | 0.061489 | -61.56 | -0.007751 | -61.7374 | 61.5811 | 61.4541 | 61.5273 | -61.7137 | -61.633 | 0.004938 | -61.6995 | 61.418 | 61.5684 | 60.9352 | -61.9141 | -0.016309 | -0.015598 | 0.13743 | -0.039978 | -0.023669 | -0.14258 | -0.06939 | -0.21669 | -0.17865 | 0.064422 | -0.002134 | 0.21455 | -0.028241 | -0.66147 | 123.2785 | 123.1515 | 123.2247 | 61.6896 | -123.3104 | 123.1154 | 123.2658 | 122.6326 | 61.7023 | -123.5108
459.5312 | 123.4451 | -61.6379 | 61.6425 | 1.4211e-13 | -0.0041623 | 0.0018804 | 0.065255 | -0.0064613 | 0.060994 | -0.006028 | -0.0026725 | -0.0017051 | 0.070433 | 0.019459 | 0.061489 | -61.5416 | -0.003172 | -61.7145 | 61.5857 | 61.4541 | 61.5364 | -61.7 | -61.6238 | 0.004938 | -61.6858 | 61.4318 | 61.5868 | 60.9535 | -61.9095 | -0.062083 | -0.056795 | 0.096236 | -0.076596 | -0.014513 | -0.18835 | -0.10601 | -0.27162 | -0.21069 | 0.01407 | -0.047908 | 0.22371 | -0.055703 | -0.68893 | 123.2235 | 123.092 | 123.1743 | 61.6347 | -123.3424 | 123.0696 | 123.2246 | 122.5914 | 61.6428 | -123.552
461.2812 | 123.4177 | -61.6379 | 61.6333 | 1.4211e-13 | -0.0043761 | 0.0018804 | 0.065041 | -0.0062475 | 0.061208 | 0.0016025 | -0.0028861 | -0.0012777 | 0.070647 | 0.019459 | 0.061703 | -61.5233 | -0.007751 | -61.7007 | 61.5994 | 61.4953 | 61.5502 | -61.6816 | -61.6055 | 0.000359 | -61.6675 | 61.4455 | 61.5959 | 60.9673 | -61.8958 | -0.043767 | -0.033905 | 0.11455 | -0.062862 | -0.019095 | -0.13799 | -0.083118 | -0.25788 | -0.1878 | 0.032385 | -0.029593 | 0.22829 | -0.037391 | -0.66604 | 123.2373 | 123.1332 | 123.1881 | 61.6301 | -123.3149 | 123.0834 | 123.2338 | 122.6051 | 61.6382 | -123.5291
463.0312 | 123.5184 | -61.6974 | 61.5601 | 1.4211e-13 | -0.0043761 | 0.0018804 | 0.065041 | -0.0064613 | 0.061208 | -0.006028 | -0.0033135 | -0.0019187 | 0.070647 | 0.019246 | 0.061703 | -61.5508 | -0.003172 | -61.7282 | 61.5765 | 61.4541 | 61.5227 | -61.7137 | -61.6284 | 0.004938 | -61.6949 | 61.4135 | 61.5639 | 60.9398 | -61.9141 | -0.016309 | 0.016445 | 0.14659 | -0.030821 | -0.014512 | -0.10595 | -0.037348 | -0.21669 | -0.14661 | 0.069001 | 0.002445 | 0.21913 | 0.003801 | -0.62027 | 123.2739 | 123.1515 | 123.2201 | 61.6942 | -123.2738 | 123.1108 | 123.2612 | 122.6372 | 61.7023 | -123.4741
464.7812 | 123.4863 | -61.702 | 61.5784 | 1.4211e-13 | -0.0045897 | 0.0016666 | 0.064827 | -0.0066749 | 0.061422 | -0.006028 | -0.0028861 | -0.0017051 | 0.070433 | 0.019459 | 0.061703 | -61.56 | -0.012329 | -61.7282 | 61.5765 | 61.4404 | 61.5227 | -61.7183 | -61.6238 | 0.004938 | -61.6995 | 61.4089 | 61.5593 | 60.9352 | -61.9141 | -0.016311 | -0.001865 | 0.14201 | -0.026244 | -0.009933 | -0.138 | -0.055658 | -0.21211 | -0.1695 | 0.078157 | 0.002443 | 0.21455 | -0.019087 | -0.64316 | 123.2785 | 123.1423 | 123.2247 | 61.6896 | -123.2966 | 123.1108 | 123.2612 | 122.6372 | 61.7069 | -123.4924
466.4531 | 123.5504 | -61.6516 | 61.5692 | 1.4211e-13 | -0.0043761 | 0.001453 | 0.065255 | -0.0068885 | 0.061422 | -0.006028 | -0.0030999 | -0.0017051 | 0.07022 | 0.019246 | 0.061703 | -61.5416 | -0.012329 | -61.7191 | 61.5902 | 61.4541 | 61.5319 | -61.6862 | -61.6147 | 0.000359 | -61.6812 | 61.4318 | 61.5822 | 60.9581 | -61.9049 | -0.034613 | 0.021025 | 0.10997 | -0.067442 | -0.032829 | -0.11511 | -0.037345 | -0.25331 | -0.13745 | 0.03696 | -0.029596 | 0.22371 | 0.012961 | -0.61111 | 123.2418 | 123.1057 | 123.1835 | 61.6393 | -123.2554 | 123.0834 | 123.2338 | 122.6097 | 61.652 | -123.4741
468.1875 | 123.3856 | -61.6928 | 61.6287 | 1.4211e-13 | -0.0043761 | 0.002094 | 0.065041 | -0.0066749 | 0.061635 | 0.0016025 | -0.0033135 | -0.0019187 | 0.070006 | 0.019246 | 0.061276 | -61.5508 | -0.003172 | -61.7236 | 61.5719 | 61.4358 | 61.5227 | -61.7 | -61.6284 | 0.000359 | -61.6995 | 61.4089 | 61.5593 | 60.9261 | -61.9187 | -0.007151 | -0.056798 | 0.14201 | -0.030821 | -0.02367 | -0.19293 | -0.10601 | -0.22585 | -0.21985 | 0.064423 | -0.006712 | 0.21913 | -0.069441 | -0.70267 | 123.2647 | 123.1286 | 123.2155 | 61.6896 | -123.3287 | 123.1017 | 123.2521 | 122.6189 | 61.6932 | -123.5474
469.9375 | 123.3994 | -61.6882 | 61.6379 | 1.4211e-13 | -0.0041623 | 0.002094 | 0.065041 | -0.0066749 | 0.060994 | 0.0016025 | -0.0028861 | -0.0017051 | 0.070433 | 0.019246 | 0.061489 | -61.5233 | -0.012329 | -61.6962 | 61.5902 | 61.4724 | 61.541 | -61.6771 | -61.6055 | 0.004938 | -61.6766 | 61.4272 | 61.5822 | 60.9535 | -61.8958 | 0.011166 | -0.047639 | 0.1649 | -0.007929 | -0.019095 | -0.16546 | -0.096852 | -0.20753 | -0.21069 | 0.082739 | 0.011604 | 0.21913 | -0.055703 | -0.68435 | 123.2785 | 123.1607 | 123.2293 | 61.6759 | -123.3149 | 123.1154 | 123.2704 | 122.6418 | 61.6932 | -123.5336
471.6094 | 123.5184 | -61.6653 | 61.5738 | 1.4211e-13 | -0.0045897 | 0.002094 | 0.064827 | -0.0068885 | 0.060994 | -0.006028 | -0.0030999 | -0.0019187 | 0.07022 | 0.019246 | 0.061703 | -61.5142 | -0.007751 | -61.6916 | 61.5994 | 61.4953 | 61.5593 | -61.6679 | -61.5918 | -0.00422 | -61.6583 | 61.4455 | 61.5959 | 60.9764 | -61.8774 | -0.002564 | 0.025604 | 0.15117 | -0.026239 | -0.023675 | -0.078476 | -0.014452 | -0.2121 | -0.12829 | 0.073587 | 0.007031 | 0.21913 | 0.022118 | -0.59737 | 123.2647 | 123.1607 | 123.2247 | 61.6576 | -123.2417 | 123.1108 | 123.2613 | 122.6418 | 61.6611 | -123.4512
473.375 | 123.3948 | -61.6425 | 61.6699 | 1.4211e-13 | -0.0043761 | 0.0016666 | 0.065041 | -0.0066749 | 0.061422 | -0.006028 | -0.0030999 | -0.0017051 | 0.070433 | 0.019459 | 0.061703 | -61.505 | -0.021486 | -61.6778 | 61.6131 | 61.5274 | 61.5639 | -61.6496 | -61.5826 | 0.000359 | -61.6446 | 61.4501 | 61.6051 | 60.981 | -61.8591 | -0.007136 | -0.056791 | 0.13744 | -0.035392 | -0.028256 | -0.14255 | -0.106 | -0.21668 | -0.21984 | 0.059856 | -0.002121 | 0.21456 | -0.064854 | -0.68892 | 123.2556 | 123.1698 | 123.2064 | 61.621 | -123.3195 | 123.0925 | 123.2475 | 122.6235 | 61.6428 | -123.5291
475.0625 | 123.5001 | -61.6013 | 61.6104 | 1.4211e-13 | -0.0041623 | 0.0018804 | 0.065255 | -0.0066749 | 0.061635 | 0.0016025 | -0.0030999 | -0.0017051 | 0.070433 | 0.019673 | 0.061489 | -61.4821 | -0.007751 | -61.655 | 61.6406 | 61.5365 | 61.5914 | -61.6313 | -61.5505 | 0.004938 | -61.6125 | 61.4776 | 61.6234 | 60.9947 | -61.8362 | -0.03002 | 0.030188 | 0.11913 | -0.0537 | -0.02368 | -0.073887 | -0.019023 | -0.23498 | -0.13286 | 0.050708 | -0.011269 | 0.22371 | 0.012969 | -0.61568 | 123.2419 | 123.1378 | 123.1926 | 61.5935 | -123.2417 | 123.0788 | 123.2246 | 122.596 | 61.6062 | -123.4467
476.8125 | 123.4497 | -61.5921 | 61.7065 | 1.4211e-13 | -0.0045897 | 0.0018804 | 0.065468 | -0.0064613 | 0.061208 | 0.0016025 | -0.0033135 | -0.0017051 | 0.07022 | 0.019459 | 0.061489 | -61.4409 | -0.012329 | -61.6183 | 61.6635 | 61.5777 | 61.6143 | -61.5855 | -61.5185 | 0.004938 | -61.5851 | 61.5142 | 61.66 | 61.0359 | -61.8042 | 0.006615 | -0.04305 | 0.15118 | -0.026229 | -0.032844 | -0.12881 | -0.09226 | -0.21208 | -0.19237 | 0.073604 | 0.007048 | 0.21913 | -0.046532 | -0.6706 | 123.2556 | 123.1698 | 123.2064 | 61.5798 | -123.292 | 123.1063 | 123.2521 | 122.628 | 61.597 | -123.5107
478.5625 | 123.436 | -61.647 | 61.6562 | 1.4211e-13 | -0.0045897 | 0.0018804 | 0.065255 | -0.0064613 | 0.061422 | 0.0016025 | -0.0028861 | -0.0019187 | 0.07022 | 0.019459 | 0.061489 | -61.5142 | -0.007751 | -61.6824 | 61.604 | 61.4862 | 61.5502 | -61.6496 | -61.5872 | 0.000359 | -61.6492 | 61.4363 | 61.5868 | 60.9718 | -61.882 | -0.002558 | -0.052215 | 0.13286 | -0.035393 | -0.032835 | -0.17003 | -0.10601 | -0.23499 | -0.21984 | 0.059855 | -0.002122 | 0.23287 | -0.069436 | -0.68435 | 123.251 | 123.1332 | 123.1972 | 61.6393 | -123.3058 | 123.0834 | 123.2338 | 122.6189 | 61.6474 | -123.5382
480.2656 | 123.3765 | -61.5921 | 61.7249 | 1.4211e-13 | -0.0041623 | 0.002094 | 0.064827 | -0.0064613 | 0.060994 | 0.0016025 | -0.0033135 | -0.0019187 | 0.070006 | 0.019459 | 0.061489 | -61.4455 | -0.007751 | -61.6275 | 61.6635 | 61.5091 | 61.6143 | -61.6038 | -61.5277 | 0.009516 | -61.6034 | 61.4913 | 61.6509 | 61.0314 | -61.8133 | -0.011701 | -0.061361 | 0.14661 | -0.035385 | -0.023684 | -0.2158 | -0.11057 | -0.22124 | -0.23357 | 0.064447 | -0.011267 | 0.20997 | -0.074 | -0.69349 | 123.2556 | 123.1012 | 123.2064 | 61.5844 | -123.3287 | 123.0834 | 123.243 | 122.6235 | 61.6016 | -123.5382
482.0312 | 123.381 | -61.5738 | 61.7203 | 1.4211e-13 | -0.0043761 | 0.0016666 | 0.064827 | -0.0066749 | 0.061422 | -0.006028 | -0.0028861 | -0.0012777 | 0.070433 | 0.019887 | 0.061062 | -61.4547 | -0.007751 | -61.6321 | 61.6406 | 61.5548 | 61.6051 | -61.5992 | -61.5322 | 0.004938 | -61.6034 | 61.4913 | 61.6371 | 61.0176 | -61.8225 | -0.025432 | -0.079675 | 0.11914 | -0.058273 | -0.032841 | -0.16543 | -0.11515 | -0.24871 | -0.22899 | 0.041558 | -0.029577 | 0.21913 | -0.083158 | -0.70265 | 123.2144 | 123.1286 | 123.1789 | 61.566 | -123.3195 | 123.0651 | 123.2109 | 122.5914 | 61.5787 | -123.5428
483.7812 | 123.4451 | -61.615 | 61.6104 | 1.4211e-13 | -0.0045897 | 0.002094 | 0.065255 | -0.0068885 | 0.061635 | -0.013659 | -0.0030999 | -0.0019187 | 0.07022 | 0.019459 | 0.061276 | -61.4638 | -0.016908 | -61.6366 | 61.6452 | 61.5411 | 61.596 | -61.6084 | -61.5368 | 0.009516 | -61.6034 | 61.4867 | 61.6417 | 61.0085 | -61.8179 | 0.006608 | 0.034767 | 0.15118 | -0.021654 | -0.028262 | -0.069308 | -0.014444 | -0.20293 | -0.12371 | 0.078177 | 0.011621 | 0.21455 | 0.031283 | -0.60194 | 123.2602 | 123.1561 | 123.211 | 61.5981 | -123.2188 | 123.1017 | 123.2567 | 122.6235 | 61.6245 | -123.4283
485.4688 | 123.4222 | -61.5784 | 61.6928 | 1.4211e-13 | -0.0045897 | 0.002094 | 0.065041 | -0.0066749 | 0.061208 | 0.0016025 | -0.0028861 | -0.0017051 | 0.070647 | 0.019246 | 0.061276 | -61.473 | -0.016908 | -61.6504 | 61.6314 | 61.5274 | 61.5868 | -61.6175 | -61.5505 | -0.00422 | -61.6079 | 61.4638 | 61.6188 | 60.9947 | -61.8362 | -0.039171 | -0.061366 | 0.1054 | -0.07201 | -0.032839 | -0.16544 | -0.106 | -0.25787 | -0.229 | 0.02782 | -0.029579 | 0.22829 | -0.074007 | -0.69807 | 123.2098 | 123.1057 | 123.1652 | 61.5615 | -123.3103 | 123.0422 | 123.1972 | 122.5731 | 61.5741 | -123.529
487.2344 | 123.4222 | -61.6379 | 61.6287 | 1.4211e-13 | -0.0045897 | 0.0018804 | 0.064827 | -0.0066749 | 0.061422 | 0.0016025 | -0.0028861 | -0.0017051 | 0.070647 | 0.019673 | 0.061276 | -61.4913 | -0.007751 | -61.6687 | 61.6086 | 61.4999 | 61.5593 | -61.6633 | -61.578 | 0.000359 | -61.64 | 61.4409 | 61.5913 | 60.9764 | -61.8591 | -0.025451 | -0.020171 | 0.1466 | -0.030814 | -0.005363 | -0.12883 | -0.069383 | -0.22125 | -0.1878 | 0.059857 | -0.002121 | 0.21913 | -0.037391 | -0.6523 | 123.2464 | 123.1378 | 123.1972 | 61.6301 | -123.2921 | 123.0788 | 123.2292 | 122.6143 | 61.6382 | -123.4879
488.9219 | 123.349 | -61.6379 | 61.6333 | 1.4211e-13 | -0.0045897 | 0.0018804 | 0.065041 | -0.0066749 | 0.061208 | 0.0016025 | -0.0033135 | -0.0017051 | 0.07022 | 0.019673 | 0.061276 | -61.5004 | -0.003172 | -61.6687 | 61.5994 | 61.4862 | 61.5593 | -61.6496 | -61.578 | -0.00422 | -61.6446 | 61.4318 | 61.5913 | 60.9718 | -61.8637 | -0.011714 | -0.033905 | 0.13744 | -0.030814 | -0.0191 | -0.14714 | -0.073961 | -0.22583 | -0.20154 | 0.059857 | -0.006699 | 0.21913 | -0.041969 | -0.66146 | 123.2373 | 123.124 | 123.1972 | 61.6347 | -123.2829 | 123.0696 | 123.2292 | 122.6097 | 61.6337 | -123.497
490.6094 | 123.4222 | -61.6013 | 61.6837 | 1.4211e-13 | -0.0045897 | 0.0016666 | 0.065041 | -0.0066749 | 0.061422 | -0.006028 | -0.0028861 | -0.0019187 | 0.07022 | 0.0201 | 0.061276 | -61.4501 | -0.003172 | -61.6366 | 61.6406 | 61.5503 | 61.5914 | -61.6084 | -61.5368 | -0.00422 | -61.6034 | 61.4821 | 61.628 | 61.0085 | -61.8225 | -0.007125 | -0.043054 | 0.15118 | -0.035387 | -0.028262 | -0.13339 | -0.092265 | -0.22124 | -0.20153 | 0.064444 | -0.002112 | 0.21913 | -0.055694 | -0.67518 | 123.2419 | 123.1515 | 123.1926 | 61.5981 | -123.292 | 123.0834 | 123.2292 | 122.6097 | 61.597 | -123.5062
492.3594 | 123.4451 | -61.5875 | 61.6379 | 1.4211e-13 | -0.0043761 | 0.002094 | 0.065041 | -0.0066749 | 0.061422 | 0.0016025 | -0.0030999 | -0.0017051 | 0.070433 | 0.019673 | 0.061489 | -61.4592 | -0.007751 | -61.6366 | 61.6314 | 61.5457 | 61.596 | -61.6175 | -61.5368 | -0.00422 | -61.6034 | 61.473 | 61.6234 | 60.9993 | -61.8179 | -0.030016 | -0.006434 | 0.12829 | -0.04912 | -0.019104 | -0.092194 | -0.041909 | -0.2304 | -0.16491 | 0.050711 | -0.015845 | 0.21455 | -0.014496 | -0.63856 | 123.219 | 123.1332 | 123.1835 | 61.5798 | -123.2554 | 123.0605 | 123.2109 | 122.5868 | 61.5833 | -123.4558
494.0938 | 123.3902 | -61.5509 | 61.7661 | 1.4211e-13 | -0.0041623 | 0.0018804 | 0.065041 | -0.0071023 | 0.061422 | 0.0016025 | -0.0028861 | -0.0017051 | 0.070006 | 0.019887 | 0.061276 | -61.4272 | -0.007751 | -61.6046 | 61.6681 | 61.5869 | 61.6234 | -61.5718 | -61.5048 | 0.000359 | -61.5713 | 61.5096 | 61.6646 | 61.0405 | -61.795 | -0.020848 | -0.09798 | 0.12372 | -0.053693 | -0.032845 | -0.17916 | -0.14261 | -0.24413 | -0.25645 | 0.046141 | -0.020415 | 0.22371 | -0.10146 | -0.72553 | 123.219 | 123.1378 | 123.1743 | 61.5432 | -123.3378 | 123.0605 | 123.2155 | 122.5914 | 61.5513 | -123.5611
495.8438 | 123.4589 | -61.441 | 61.8027 | 1.4211e-13 | -0.0050171 | 0.0018804 | 0.064827 | -0.0068885 | 0.061422 | -0.006028 | -0.0028861 | -0.0021323 | 0.07022 | 0.019887 | 0.061062 | -61.3356 | -0.007751 | -61.5176 | 61.7551 | 61.6647 | 61.7059 | -61.4848 | -61.4086 | -0.00422 | -61.4843 | 61.5966 | 61.7516 | 61.1229 | -61.708 | -0.043711 | -0.047612 | 0.10543 | -0.076568 | -0.032857 | -0.13794 | -0.096818 | -0.26699 | -0.20608 | 0.032431 | -0.043282 | 0.22371 | -0.05109 | -0.67974 | 123.1961 | 123.1058 | 123.1469 | 61.4333 | -123.2874 | 123.0376 | 123.1926 | 122.564 | 61.4368 | -123.5107
497.5312 | 123.4085 | -61.4639 | 61.8118 | 1.4211e-13 | -0.0045897 | 0.002094 | 0.064827 | -0.0066749 | 0.061422 | -0.006028 | -0.0028861 | -0.0014913 | 0.070433 | 0.019887 | 0.061062 | -61.3539 | -0.012329 | -61.5268 | 61.7367 | 61.6418 | 61.6875 | -61.5031 | -61.4315 | 0.004938 | -61.5026 | 61.5737 | 61.7241 | 61.1 | -61.7263 | -0.039139 | -0.075082 | 0.11 | -0.062837 | -0.023698 | -0.16999 | -0.12429 | -0.26242 | -0.23813 | 0.032425 | -0.038709 | 0.22371 | -0.087718 | -0.71179 | 123.2007 | 123.1058 | 123.1515 | 61.4516 | -123.3149 | 123.0376 | 123.188 | 122.564 | 61.4689 | -123.5382
499.2188 | 123.4543 | -61.4914 | 61.7157 | 1.4211e-13 | -0.0045897 | 0.002094 | 0.064614 | -0.0071023 | 0.061635 | 0.0016025 | -0.0028861 | -0.0019187 | 0.070006 | 0.019673 | 0.061276 | -61.3677 | -0.016908 | -61.5451 | 61.723 | 61.6098 | 61.6784 | -61.5214 | -61.4407 | 0.018674 | -61.5072 | 61.56 | 61.7195 | 61.0863 | -61.7355 | -0.029988 | 0.007314 | 0.12373 | -0.053684 | -0.023696 | -0.10591 | -0.037314 | -0.24411 | -0.15573 | 0.050734 | -0.015822 | 0.22829 | 0.003835 | -0.62939 | 123.2144 | 123.1012 | 123.1698 | 61.4745 | -123.2371 | 123.0514 | 123.2109 | 122.5777 | 61.5101 | -123.4512
500.9844 | 123.4634 | -61.5555 | 61.6333 | 1.4211e-13 | -0.0045897 | 0.0016666 | 0.064614 | -0.0068885 | 0.061422 | 0.0016025 | -0.0026725 | -0.0019187 | 0.07022 | 0.019459 | 0.061276 | -61.4409 | -0.012329 | -61.6046 | 61.6543 | 61.5274 | 61.6051 | -61.5946 | -61.5048 | 0.004938 | -61.5759 | 61.4913 | 61.6371 | 61.0176 | -61.795 | -0.039164 | 0.021035 | 0.11456 | -0.049115 | -0.009951 | -0.10593 | -0.028175 | -0.23955 | -0.14202 | 0.050719 | -0.020416 | 0.21913 | 0.003817 | -0.61567 | 123.2098 | 123.0828 | 123.1606 | 61.5432 | -123.2279 | 123.0468 | 123.1926 | 122.5731 | 61.5604 | -123.4283
502.6562 | 123.4543 | -61.5921 | 61.6333 | 1.4211e-13 | -0.0048033 | 0.002094 | 0.065041 | -0.0066749 | 0.061208 | 0.0016025 | -0.0028861 | -0.0019187 | 0.070433 | 0.0201 | 0.061489 | -61.4409 | -0.007751 | -61.6138 | 61.6452 | 61.5548 | 61.5868 | -61.5901 | -61.5231 | 0.004938 | -61.5805 | 61.4867 | 61.6417 | 61.0085 | -61.8088 | 0.002036 | 0.011879 | 0.15118 | -0.02165 | -0.023686 | -0.078459 | -0.046489 | -0.21666 | -0.14659 | 0.069025 | 0.011627 | 0.22829 | 0.008395 | -0.62483 | 123.2373 | 123.1469 | 123.1789 | 61.5844 | -123.2234 | 123.0788 | 123.2338 | 122.6006 | 61.597 | -123.4421
504.4062 | 123.4268 | -61.6013 | 61.615 | 1.4211e-13 | -0.0045897 | 0.002094 | 0.065041 | -0.0068885 | 0.061422 | 0.0092325 | -0.0030999 | -0.0019187 | 0.070433 | 0.019673 | 0.061276 | -61.418 | -0.012329 | -61.5909 | 61.6635 | 61.5548 | 61.6234 | -61.5672 | -61.5002 | -0.00422 | -61.5622 | 61.505 | 61.6554 | 61.0268 | -61.7767 | 0.034085 | 0.048503 | 0.18323 | 0.010396 | -0.023689 | -0.060148 | 0.008451 | -0.17546 | -0.10997 | 0.10107 | 0.039096 | 0.21455 | 0.040442 | -0.5882 | 123.2647 | 123.1561 | 123.2247 | 61.5889 | -123.1822 | 123.1063 | 123.2567 | 122.628 | 61.597 | -123.3917
506.0938 | 123.4634 | -61.5097 | 61.6974 | 1.4211e-13 | -0.0043761 | 0.002094 | 0.064827 | -0.0071023 | 0.061208 | -0.013659 | -0.0028861 | -0.0017051 | 0.07022 | 0.019673 | 0.061276 | -61.3768 | -0.007751 | -61.5634 | 61.6864 | 61.5823 | 61.6463 | -61.5397 | -61.4681 | 0.004938 | -61.5301 | 61.5279 | 61.6875 | 61.0451 | -61.7584 | -0.029993 | -0.011003 | 0.13288 | -0.053686 | -0.023693 | -0.11507 | -0.051054 | -0.24869 | -0.16947 | 0.041573 | -0.020405 | 0.22829 | -0.009906 | -0.65229 | 123.1961 | 123.092 | 123.156 | 61.502 | -123.2371 | 123.0376 | 123.1972 | 122.5548 | 61.5146 | -123.4558
507.8281 | 123.4589 | -61.5005 | 61.6791 | 1.4211e-13 | -0.0052307 | 0.0018804 | 0.065041 | -0.0068885 | 0.061422 | 0.0016025 | -0.0030999 | -0.0017051 | 0.070433 | 0.019459 | 0.061489 | -61.3951 | -0.012329 | -61.568 | 61.6818 | 61.5548 | 61.6372 | -61.5443 | -61.4681 | 0.000359 | -61.5301 | 61.5325 | 61.6875 | 61.0543 | -61.7538 | -0.043728 | 0.00273 | 0.10542 | -0.067421 | -0.023693 | -0.12423 | -0.041901 | -0.25327 | -0.14659 | 0.032417 | -0.029561 | 0.22371 | 0.008405 | -0.62482 | 123.1824 | 123.0554 | 123.1377 | 61.4882 | -123.2234 | 123.033 | 123.188 | 122.5548 | 61.5009 | -123.4329
509.5625 | 123.3398 | -61.4502 | 61.8164 | 1.4211e-13 | -0.0045897 | 0.0016666 | 0.065041 | -0.0071023 | 0.061635 | -0.006028 | -0.0026725 | -0.0019187 | 0.07022 | 0.019673 | 0.061062 | -61.2898 | -0.003172 | -61.4627 | 61.7871 | 61.6785 | 61.7379 | -61.439 | -61.3674 | 0.000359 | -61.4385 | 61.6286 | 61.7836 | 61.1458 | -61.6577 | 0.011233 | -0.029296 | 0.16036 | -0.012474 | -0.023707 | -0.13793 | -0.0785 | -0.20747 | -0.18777 | 0.082794 | 0.01166 | 0.21913 | -0.032773 | -0.67058 | 123.2373 | 123.1287 | 123.1881 | 61.447 | -123.2554 | 123.0788 | 123.2338 | 122.596 | 61.4506 | -123.4741
511.3281 | 123.4131 | -61.3449 | 61.8851 | 1.4211e-13 | -0.0045897 | 0.002094 | 0.065041 | -0.0071023 | 0.060781 | -0.006028 | -0.0028861 | -0.0019187 | 0.070006 | 0.019887 | 0.061062 | -61.2303 | -0.003172 | -61.3986 | 61.8558 | 61.7655 | 61.8066 | -61.3749 | -61.2987 | 0.000359 | -61.3699 | 61.6973 | 61.8477 | 61.2191 | -61.5844 | -0.029947 | -0.029286 | 0.1146 | -0.053663 | -0.023716 | -0.1196 | -0.078486 | -0.23949 | -0.18775 | 0.04619 | -0.024945 | 0.21455 | -0.037337 | -0.66598 | 123.2007 | 123.1104 | 123.1515 | 61.3417 | -123.2599 | 123.0422 | 123.1926 | 122.564 | 61.3453 | -123.4695
513.0781 | 123.4909 | -61.2671 | 61.9171 | 1.4211e-13 | -0.0048033 | 0.0018804 | 0.064614 | -0.0071023 | 0.061208 | 0.0016025 | -0.0030999 | -0.0014913 | 0.070647 | 0.019673 | 0.061276 | -61.1433 | -0.016908 | -61.3253 | 61.9245 | 61.825 | 61.8844 | -61.2924 | -61.2209 | 0.009516 | -61.292 | 61.7706 | 61.921 | 61.3015 | -61.5066 | -0.025346 | 0.007347 | 0.12377 | -0.058231 | -0.032885 | -0.092116 | -0.032693 | -0.23947 | -0.14654 | 0.046208 | -0.024927 | 0.21455 | 0.003877 | -0.61561 | 123.1916 | 123.0921 | 123.1515 | 61.2502 | -123.2096 | 123.0377 | 123.1881 | 122.5686 | 61.2766 | -123.4237
514.8281 | 123.3856 | -61.2671 | 61.972 | 1.4211e-13 | -0.0048033 | 0.0018804 | 0.065041 | -0.0068885 | 0.061208 | 0.0016025 | -0.0030999 | -0.0014913 | 0.070006 | 0.019887 | 0.061489 | -61.1754 | -0.012329 | -61.3391 | 61.897 | 61.8021 | 61.8569 | -61.3199 | -61.2392 | 0.009516 | -61.3103 | 61.7339 | 61.8981 | 61.2695 | -61.5432 | -0.05282 | -0.075055 | 0.091719 | -0.071965 | -0.019145 | -0.16994 | -0.1151 | -0.2761 | -0.2381 | 0.027893 | -0.043242 | 0.23286 | -0.073948 | -0.70259 | 123.1641 | 123.0692 | 123.124 | 61.2548 | -123.292 | 123.001 | 123.1652 | 122.5365 | 61.2766 | -123.5152
516.5312 | 123.3627 | -61.3266 | 61.9263 | 1.4211e-13 | -0.0045897 | 0.0016666 | 0.064827 | -0.0066749 | 0.061208 | -0.006028 | -0.0030999 | -0.0017051 | 0.070433 | 0.019887 | 0.061276 | -61.1937 | -0.016908 | -61.3711 | 61.8695 | 61.7792 | 61.8295 | -61.3565 | -61.2758 | 0.000359 | -61.3378 | 61.7065 | 61.8615 | 61.2511 | -61.5752 | -0.029942 | -0.056749 | 0.13291 | -0.044504 | -0.014562 | -0.14706 | -0.096792 | -0.24865 | -0.2198 | 0.050773 | -0.011205 | 0.23744 | -0.064801 | -0.67513 | 123.1961 | 123.1058 | 123.1561 | 61.3097 | -123.2828 | 123.0331 | 123.1881 | 122.5777 | 61.327 | -123.5015
518.2812 | 123.3261 | -61.3541 | 61.8805 | 1.4211e-13 | -0.0045897 | 0.0018804 | 0.065041 | -0.0073159 | 0.061208 | -0.006028 | -0.0028861 | -0.0019187 | 0.07022 | 0.019887 | 0.060848 | -61.2212 | -0.012329 | -61.3894 | 61.8421 | 61.7517 | 61.7974 | -61.3749 | -61.2987 | 0.000359 | -61.3699 | 61.6836 | 61.8386 | 61.2054 | -61.589 | -0.020792 | -0.038443 | 0.13291 | -0.035352 | -0.01456 | -0.12876 | -0.083066 | -0.23492 | -0.19691 | 0.055345 | -0.01579 | 0.21913 | -0.041917 | -0.67514 | 123.1961 | 123.1058 | 123.1515 | 61.3417 | -123.2553 | 123.0376 | 123.1926 | 122.5594 | 61.3544 | -123.4695
520.0312 | 123.4543 | -61.3403 | 61.8393 | 1.4211e-13 | -0.0048033 | 0.002094 | 0.065041 | -0.0068885 | 0.061422 | -0.006028 | -0.0028861 | -0.0014913 | 0.07022 | 0.0201 | 0.061276 | -61.1845 | -0.003172 | -61.3619 | 61.8787 | 61.7929 | 61.8432 | -61.3382 | -61.2667 | 0.000359 | -61.3241 | 61.7202 | 61.8706 | 61.2466 | -61.5524 | 0.002107 | 0.039383 | 0.1558 | -0.021615 | -0.023722 | -0.046348 | 0.00392 | -0.21202 | -0.11908 | 0.073663 | 0.016264 | 0.22828 | 0.031333 | -0.59274 | 123.219 | 123.1333 | 123.1835 | 61.3372 | -123.1775 | 123.0605 | 123.211 | 122.5869 | 61.3407 | -123.3916
521.7188 | 123.4451 | -61.4868 | 61.6882 | 1.4211e-13 | -0.0048033 | 0.002094 | 0.065041 | -0.0071023 | 0.061208 | -0.021289 | -0.0028861 | -0.0019187 | 0.070433 | 0.019887 | 0.061703 | -61.2028 | -0.003172 | -61.3803 | 61.8604 | 61.7563 | 61.8157 | -61.3565 | -61.2758 | 0.009516 | -61.3424 | 61.6973 | 61.8569 | 61.2191 | -61.5798 | 0.13027 | 0.17213 | 0.28397 | 0.10656 | -0.023719 | 0.068082 | 0.12751 | -0.093008 | 0.009086 | 0.21099 | 0.14443 | 0.23744 | 0.16866 | -0.46914 | 123.3472 | 123.2431 | 123.3026 | 61.4836 | -123.0448 | 123.1841 | 123.3437 | 122.7059 | 61.4963 | -123.2681
523.4531 | 123.3215 | -61.2671 | 61.9812 | 1.4211e-13 | -0.0048033 | 0.001453 | 0.065041 | -0.0068885 | 0.061208 | -0.006028 | -0.0030999 | -0.0017051 | 0.070433 | 0.020314 | 0.061489 | -61.1159 | -0.012329 | -61.2795 | 61.9474 | 61.8342 | 61.9027 | -61.265 | -61.198 | 0.004938 | -61.26 | 61.7889 | 61.9439 | 61.3107 | -61.4791 | 0.002127 | -0.033848 | 0.15124 | -0.012448 | -0.014575 | -0.14704 | -0.078466 | -0.212 | -0.19231 | 0.069102 | 0.007124 | 0.21912 | -0.037317 | -0.67054 | 123.2144 | 123.1012 | 123.1698 | 61.2548 | -123.2462 | 123.056 | 123.211 | 122.5778 | 61.272 | -123.4603
525.2031 | 123.4131 | -61.1938 | 61.9675 | 1.4211e-13 | -0.0048033 | 0.0016666 | 0.064827 | -0.0071023 | 0.061208 | 0.0016025 | -0.0030999 | -0.0014913 | 0.070433 | 0.0201 | 0.061062 | -61.038 | -0.012329 | -61.2154 | 62.0298 | 61.9486 | 61.9806 | -61.1825 | -61.1156 | 0.000359 | -61.1775 | 61.8667 | 62.0217 | 61.3885 | -61.4104 | 0.011306 | 0.062296 | 0.15583 | -0.021594 | -0.0329 | -0.018839 | 0.013104 | -0.21656 | -0.10075 | 0.078276 | 0.016299 | 0.23286 | 0.054252 | -0.57897 | 123.2236 | 123.1425 | 123.1744 | 61.1815 | -123.15 | 123.0606 | 123.2156 | 122.5823 | 61.1942 | -123.3779
526.9688 | 123.3215 | -61.2991 | 61.9583 | 1.4211e-13 | -0.0048033 | 0.0018804 | 0.064827 | -0.0068885 | 0.061422 | 0.0016025 | -0.0030999 | -0.0021323 | 0.070433 | 0.019887 | 0.061489 | -61.1662 | -0.003172 | -61.3436 | 61.8924 | 61.8021 | 61.8478 | -61.3199 | -61.2392 | 0.000359 | -61.3103 | 61.7339 | 61.8889 | 61.2649 | -61.5295 | -0.020777 | -0.0659 | 0.13292 | -0.044501 | -0.023724 | -0.15621 | -0.11052 | -0.23032 | -0.22437 | 0.059936 | -0.011199 | 0.21912 | -0.069372 | -0.69344 | 123.1915 | 123.1012 | 123.1469 | 61.296 | -123.2782 | 123.0331 | 123.1881 | 122.564 | 61.2995 | -123.4878
528.6406 | 123.3307 | -61.2396 | 61.9766 | 1.4211e-13 | -0.0048033 | 0.0016666 | 0.064614 | -0.0066749 | 0.060781 | -0.006028 | -0.0030999 | -0.0017051 | 0.070433 | 0.0201 | 0.061276 | -61.1159 | -0.012329 | -61.2887 | 61.9428 | 61.8479 | 61.8936 | -61.265 | -61.1934 | 0.004938 | -61.26 | 61.7797 | 61.9393 | 61.3061 | -61.4837 | -0.025339 | -0.033849 | 0.12377 | -0.04907 | -0.023731 | -0.12873 | -0.083046 | -0.24404 | -0.19689 | 0.046214 | -0.020342 | 0.2237 | -0.037318 | -0.67054 | 123.1824 | 123.0875 | 123.1332 | 61.2273 | -123.2416 | 123.0194 | 123.1789 | 122.5457 | 61.2446 | -123.4603
530.4062 | 123.3902 | -61.3083 | 61.8759 | 1.4211e-13 | -0.0048033 | 0.0018804 | 0.065041 | -0.0073159 | 0.061208 | 0.0016025 | -0.0030999 | -0.0019187 | 0.070433 | 0.0201 | 0.061276 | -61.1616 | -0.003172 | -61.3345 | 61.9016 | 61.8204 | 61.8524 | -61.3153 | -61.23 | 0.000359 | -61.3012 | 61.7294 | 61.8844 | 61.2511 | -61.5249 | -0.007042 | 0.025653 | 0.14665 | -0.026188 | -0.019146 | -0.055497 | -0.023545 | -0.21659 | -0.14655 | 0.07825 | 0.007115 | 0.2237 | 0.008446 | -0.62478 | 123.2099 | 123.1287 | 123.1607 | 61.3051 | -123.1912 | 123.0377 | 123.1927 | 122.5594 | 61.3086 | -123.4008
532.1719 | 123.3261 | -61.2808 | 61.9812 | 1.4211e-13 | -0.0050171 | 0.002094 | 0.064827 | -0.0068885 | 0.060994 | -0.006028 | -0.0028861 | -0.0017051 | 0.070433 | 0.0201 | 0.061276 | -61.1433 | -0.012329 | -61.3162 | 61.9061 | 61.8387 | 61.8615 | -61.3016 | -61.2209 | 0.004938 | -61.2874 | 61.7523 | 61.8981 | 61.2832 | -61.5157 | -0.020771 | -0.075053 | 0.1375 | -0.035341 | -0.01457 | -0.14247 | -0.11967 | -0.2349 | -0.22894 | 0.059941 | -0.006615 | 0.22828 | -0.083103 | -0.69801 | 123.187 | 123.1196 | 123.1424 | 61.2685 | -123.2828 | 123.0331 | 123.1789 | 122.564 | 61.2858 | -123.4969
533.9062 | 123.3353 | -62.4252 | 60.7773 | 1.4211e-13 | -0.0048033 | 0.0018804 | 0.065041 | -0.0071023 | 0.060994 | 0.0016025 | -0.0033135 | -0.0019187 | 0.07022 | 0.020528 | 0.061062 | -62.2879 | -0.007751 | -62.4653 | 60.7524 | 60.6665 | 60.7123 | -62.4738 | -62.3656 | -0.00422 | -62.4321 | 60.5985 | 60.7489 | 60.1797 | -62.665 | -0.048567 | -0.024889 | 0.13731 | -0.040081 | 0.008486 | -0.11075 | -0.064984 | -0.23977 | -0.1788 | 0.059673 | -0.006883 | 0.23289 | -0.028414 | -0.59754 | 123.1776 | 123.0918 | 123.1375 | 62.4175 | -123.2511 | 123.0237 | 123.1741 | 122.605 | 62.421 | -123.4423
535.5938 | 123.3032 | -62.2971 | 60.9283 | 1.4211e-13 | -0.0048033 | 0.0018804 | 0.064827 | -0.0068885 | 0.061208 | -0.006028 | -0.0028861 | -0.0014913 | 0.070647 | 0.019887 | 0.061489 | -62.1506 | -0.016908 | -62.328 | 60.876 | 60.694 | 60.8359 | -62.2998 | -62.2236 | 0.000359 | -62.2902 | 60.7175 | 60.8862 | 60.2438 | -62.5276 | -0.002742 | -0.052335 | 0.14649 | -0.030906 | -0.028164 | -0.23434 | -0.092424 | -0.23058 | -0.21082 | 0.073439 | 0.006883 | 0.23746 | -0.042118 | -0.6845 | 123.1731 | 122.9911 | 123.133 | 62.2801 | -123.2281 | 123.0146 | 123.1833 | 122.5409 | 62.2974 | -123.456
537.3594 | 123.436 | -62.3291 | 60.7956 | 1.4211e-13 | -0.0048033 | 0.0016666 | 0.064827 | -0.0068885 | 0.060994 | -0.006028 | -0.0028861 | -0.0014913 | 0.070006 | 0.0201 | 0.061062 | -62.178 | -0.012329 | -62.36 | 60.8577 | 60.781 | 60.813 | -62.3364 | -62.2511 | 0.000359 | -62.3131 | 60.6992 | 60.8404 | 60.2164 | -62.5551 | -0.007329 | 0.062104 | 0.15106 | -0.03091 | -0.023581 | -0.01459 | 0.017435 | -0.22601 | -0.096387 | 0.07801 | 0.016033 | 0.24204 | 0.044848 | -0.57922 | 123.1868 | 123.1101 | 123.1421 | 62.3168 | -123.132 | 123.0283 | 123.1695 | 122.5455 | 62.3295 | -123.3507
539.1094 | 123.317 | -62.3749 | 60.8414 | 1.4211e-13 | -0.0048033 | 0.0018804 | 0.064614 | -0.0071023 | 0.061208 | -0.013659 | -0.0033135 | -0.0023459 | 0.070433 | 0.020314 | 0.061276 | -62.2101 | -0.012329 | -62.3921 | 60.8119 | 60.7444 | 60.7672 | -62.3639 | -62.2877 | 0.000359 | -62.3589 | 60.6488 | 60.8084 | 60.1706 | -62.5963 | 0.010973 | -0.029457 | 0.16479 | -0.017182 | -0.028155 | -0.096998 | -0.074128 | -0.22144 | -0.19253 | 0.087157 | 0.016022 | 0.23747 | -0.032979 | -0.67078 | 123.1868 | 123.1192 | 123.1421 | 62.3625 | -123.2053 | 123.0237 | 123.1833 | 122.5455 | 62.3752 | -123.4377
540.875 | 123.2895 | -62.3428 | 60.91 | 1.4211e-13 | -0.0050171 | 0.0018804 | 0.064827 | -0.0068885 | 0.061208 | 0.0016025 | -0.0030999 | -0.0019187 | 0.070647 | 0.020528 | 0.061276 | -62.1964 | -0.012329 | -62.3692 | 60.8256 | 60.7535 | 60.7856 | -62.3456 | -62.2694 | 0.000359 | -62.336 | 60.6763 | 60.8175 | 60.1843 | -62.578 | -0.002755 | -0.084386 | 0.14648 | -0.026335 | -0.02358 | -0.1565 | -0.12448 | -0.23517 | -0.23372 | 0.073428 | 0.006871 | 0.24204 | -0.092486 | -0.72571 | 123.1685 | 123.0964 | 123.1284 | 62.3305 | -123.2556 | 123.0191 | 123.1604 | 122.5272 | 62.3432 | -123.488
542.625 | 123.3627 | -62.4344 | 60.7773 | 1.4211e-13 | -0.0043761 | 0.0016666 | 0.064614 | -0.0068885 | 0.061422 | -0.013659 | -0.0028861 | -0.0017051 | 0.07022 | 0.020528 | 0.061062 | -62.2376 | -0.012329 | -62.4195 | 60.7753 | 60.7032 | 60.7443 | -62.3914 | -62.3106 | 0.004938 | -62.3817 | 60.626 | 60.7718 | 60.1477 | -62.6238 | 0.043009 | -0.001997 | 0.19683 | 0.014857 | -0.028152 | -0.074121 | -0.032934 | -0.18941 | -0.15133 | 0.12377 | 0.052637 | 0.24204 | -0.005521 | -0.62959 | 123.2097 | 123.1375 | 123.1787 | 62.4221 | -123.1687 | 123.0603 | 123.2061 | 122.5821 | 62.4393 | -123.4011
544.3125 | 123.3536 | -62.4893 | 60.6583 | 1.4211e-13 | -0.0048033 | 0.0018804 | 0.065041 | -0.0071023 | 0.061208 | 0.0016025 | -0.0033135 | -0.0014913 | 0.07022 | 0.019887 | 0.061276 | -62.3154 | -0.012329 | -62.5019 | 60.6975 | 60.6253 | 60.6619 | -62.4875 | -62.3976 | 0.004938 | -62.4642 | 60.5344 | 60.6893 | 60.166 | -62.6971 | 0.001783 | 0.039189 | 0.17393 | -0.01262 | -0.014403 | -0.032944 | 0.00367 | -0.20774 | -0.12388 | 0.091709 | 0.025153 | 0.23289 | 0.031083 | -0.49226 | 123.1868 | 123.1146 | 123.1513 | 62.477 | -123.1458 | 123.0237 | 123.1787 | 122.6553 | 62.4943 | -123.3553
546.0625 | 110.6277 | -118.5562 | 4.6051 | 1.4211e-13 | -0.0052307 | 0.0012394 | 0.0644 | -0.0073159 | 0.061635 | -0.006028 | -0.0037407 | -0.0017051 | 0.069792 | 0.020314 | 0.061703 | -91.4156 | -1.3493 | -91.3405 | 31.1165 | 30.5189 | 31.2948 | -91.843 | -91.8662 | -1.3275 | -91.8961 | 30.3987 | 30.8094 | 29.906 | -92.1572 | 26.7132 | 26.5114 | 27.1406 | 27.2157 | 0.50249 | 25.9138 | 26.6897 | 26.399 | 25.7936 | 26.69 | 26.6601 | 0.26105 | 26.2043 | 25.3009 | 149.6727 | 149.0751 | 149.851 | 117.2069 | -96.4481 | 148.9549 | 149.3656 | 148.4622 | 117.2287 | -96.7623
547.8281 | 123.3353 | -120.3918 | 2.8244 | 1.4211e-13 | -0.0054445 | 0.001453 | 0.064614 | -0.0071023 | 0.061849 | 0.0016025 | -0.0035271 | -0.0023459 | 0.069792 | 0.020314 | 0.06213 | -119.8978 | -0.17258 | -120.321 | 2.7808 | 2.7523 | 2.9029 | -120.5758 | -120.1351 | -0.16448 | -120.1605 | 2.7034 | 2.7746 | 2.787 | -120.7656 | -0.18393 | -0.043555 | 0.49407 | 0.070802 | 0.25473 | -0.072109 | 0.078461 | -0.37377 | -0.121 | 0.2567 | 0.23136 | 0.60513 | -0.049798 | -0.03744 | 123.1727 | 123.1441 | 123.2947 | 120.2193 | -123.4002 | 123.0953 | 123.1664 | 123.1788 | 120.2274 | -123.59
549.5156 | 123.3765 | -120.7581 | 2.4857 | 1.4211e-13 | -0.0056581 | 0.0016666 | 0.064186 | -0.0064613 | 0.061635 | 0.0016025 | -0.0037407 | -0.0021323 | 0.069579 | 0.020528 | 0.06213 | -119.9939 | -0.14969 | -120.4309 | 2.6298 | 2.6561 | 2.7976 | -120.6857 | -120.2359 | -0.137 | -120.2704 | 2.5935 | 2.6739 | 2.6771 | -120.8709 | 0.072391 | 0.1441 | 0.76414 | 0.32713 | 0.25474 | 0.17048 | 0.3119 | -0.11287 | 0.10787 | 0.52218 | 0.48768 | 0.60055 | 0.18822 | 0.19142 | 123.3878 | 123.4142 | 123.5556 | 120.6084 | -123.1713 | 123.3516 | 123.4319 | 123.4351 | 120.6211 | -123.3566
551.2656 | 123.317 | -121.0831 | 2.2064 | 1.4211e-13 | -0.0056581 | 0.001453 | 0.064186 | -0.0071023 | 0.061635 | 0.0016025 | -0.0037407 | -0.0021323 | 0.069792 | 0.020741 | 0.061917 | -120.8547 | -0.14969 | -121.2825 | 1.7599 | 1.7907 | 1.9322 | -121.5099 | -121.1012 | -0.13242 | -121.1358 | 1.7236 | 1.8131 | 1.8163 | -121.7409 | -0.4268 | -0.44656 | 0.22841 | -0.19941 | 0.22739 | -0.4157 | -0.27422 | -0.65783 | -0.48281 | -0.01818 | -0.052685 | 0.60515 | -0.39332 | -0.39012 | 122.8429 | 122.8738 | 123.0153 | 120.9334 | -123.7163 | 122.8067 | 122.8962 | 122.8994 | 120.9506 | -123.9473
553.0156 | 123.3627 | -122.4518 | 0.7782 | 1.4211e-13 | -0.0054445 | 0.001453 | 0.064186 | -0.0068885 | 0.062063 | 0.0016025 | -0.0035271 | -0.0023459 | 0.07022 | 0.020314 | 0.061703 | -121.7978 | -0.14053 | -122.2439 | 0.80756 | 0.67804 | 0.98901 | -122.3799 | -122.049 | -0.12784 | -122.0835 | 0.78044 | 0.85617 | 0.4473 | -122.6979 | 0.071913 | 0.029364 | 0.65398 | 0.20786 | 0.13595 | -0.10016 | 0.21081 | -0.24609 | 0.002241 | 0.40274 | 0.36823 | 0.61433 | 0.077971 | -0.3309 | 123.2593 | 123.1298 | 123.4408 | 122.3113 | -123.1581 | 123.2322 | 123.308 | 122.8991 | 122.3239 | -123.4761
554.6875 | 123.3582 | -122.4197 | 0.81482 | 1.4211e-13 | -0.0056581 | 0.0012394 | 0.064186 | -0.0071023 | 0.061849 | -0.013659 | -0.0033135 | -0.0023459 | 0.069365 | 0.020314 | 0.061917 | -121.8894 | -0.13137 | -122.3309 | 0.72973 | 0.59104 | 0.90659 | -122.444 | -122.1452 | -0.12327 | -122.1797 | 0.69345 | 0.78291 | 0.31452 | -122.794 | -0.024235 | -0.08509 | 0.53037 | 0.08883 | 0.11306 | -0.22378 | 0.091774 | -0.37429 | -0.12137 | 0.27454 | 0.24004 | 0.61433 | -0.031907 | -0.5003 | 123.1495 | 123.0108 | 123.3263 | 122.2884 | -123.2588 | 123.1132 | 123.2027 | 122.7343 | 122.2965 | -123.6089
556.4531 | 123.3078 | -122.58 | 0.68207 | 1.4211e-13 | -0.0050171 | 0.0016666 | 0.064614 | -0.0068885 | 0.061849 | 0.0016025 | -0.0035271 | -0.0027733 | 0.069792 | 0.020741 | 0.061917 | -121.9855 | -0.12679 | -122.4225 | 0.61985 | 0.49488 | 0.80129 | -122.5539 | -122.2322 | -0.11411 | -122.2713 | 0.60188 | 0.68218 | 0.15884 | -122.881 | 0.026088 | -0.06222 | 0.59444 | 0.15748 | 0.13139 | -0.18718 | 0.11922 | -0.30107 | -0.08019 | 0.34776 | 0.30868 | 0.60975 | 0.000114 | -0.52322 | 123.1998 | 123.0748 | 123.3812 | 122.4532 | -123.2359 | 123.1818 | 123.2621 | 122.7388 | 122.4658 | -123.5631
558.2031 | 123.3261 | -122.2046 | 1.062 | 1.4211e-13 | -0.0052307 | 0.001453 | 0.0644 | -0.0066749 | 0.061422 | -0.013659 | -0.0033135 | -0.0027733 | 0.07022 | 0.020741 | 0.061489 | -121.6742 | -0.12222 | -122.1066 | 0.9266 | 0.79251 | 1.1081 | -122.2425 | -121.9163 | -0.11411 | -121.9645 | 0.90406 | 0.97521 | 0.67165 | -122.5697 | -0.037911 | -0.13541 | 0.5304 | 0.098017 | 0.13593 | -0.2695 | 0.046039 | -0.36508 | -0.15795 | 0.28833 | 0.24009 | 0.60517 | -0.086799 | -0.39036 | 123.1312 | 122.9971 | 123.3126 | 122.0824 | -123.3045 | 123.1086 | 123.1798 | 122.8762 | 122.0905 | -123.6317
559.8906 | 123.4085 | -122.3053 | 0.93384 | 1.4211e-13 | -0.0056581 | 0.0012394 | 0.0644 | -0.0068885 | 0.061422 | -0.006028 | -0.0035271 | -0.0021323 | 0.069579 | 0.020741 | 0.061917 | -121.752 | -0.13137 | -122.1936 | 0.83961 | 0.70551 | 1.0302 | -122.3203 | -122.0078 | -0.11411 | -122.0469 | 0.81707 | 0.89738 | 0.58923 | -122.6521 | -0.015045 | -0.094228 | 0.55328 | 0.11174 | 0.12678 | -0.22833 | 0.096377 | -0.34679 | -0.11677 | 0.29746 | 0.25838 | 0.60517 | -0.036461 | -0.3446 | 123.1449 | 123.0108 | 123.3355 | 122.1739 | -123.2542 | 123.1224 | 123.2027 | 122.8945 | 122.1912 | -123.5859
561.6406 | 123.2758 | -122.4014 | 0.88806 | 1.4211e-13 | -0.0054445 | 0.0016666 | 0.0644 | -0.0073159 | 0.061208 | -0.013659 | -0.0035271 | -0.0023459 | 0.069792 | 0.020528 | 0.061703 | -121.7978 | -0.12222 | -122.2393 | 0.79841 | 0.65972 | 0.97527 | -122.3661 | -122.0536 | -0.10953 | -122.0835 | 0.77128 | 0.84701 | 0.34199 | -122.7025 | 0.035296 | -0.089657 | 0.60362 | 0.16208 | 0.12679 | -0.22834 | 0.08721 | -0.30103 | -0.11678 | 0.34781 | 0.31788 | 0.61891 | -0.04105 | -0.54607 | 123.1998 | 123.0612 | 123.3767 | 122.2792 | -123.2542 | 123.1727 | 123.2484 | 122.7434 | 122.2919 | -123.5905
563.3906 | 123.3673 | -122.3602 | 0.85144 | 1.4211e-13 | -0.0052307 | 0.0010256 | 0.064614 | -0.0071023 | 0.061635 | 0.0016025 | -0.0037407 | -0.0021323 | 0.069579 | 0.020314 | 0.061703 | -121.7749 | -0.13137 | -122.2165 | 0.8213 | 0.6872 | 0.99359 | -122.3432 | -122.017 | -0.11411 | -122.0652 | 0.79417 | 0.87906 | 0.3832 | -122.6704 | 0.016992 | -0.030143 | 0.58532 | 0.14378 | 0.12678 | -0.16424 | 0.14215 | -0.31017 | -0.057265 | 0.34324 | 0.295 | 0.60517 | 0.027622 | -0.46824 | 123.1815 | 123.0474 | 123.3538 | 122.2289 | -123.1947 | 123.1544 | 123.2393 | 122.7434 | 122.2461 | -123.5218
565.1406 | 123.3536 | -122.319 | 0.84686 | 1.4211e-13 | -0.0054445 | 0.0016666 | 0.064614 | -0.0071023 | 0.061635 | -0.006028 | -0.0037407 | -0.0023459 | 0.070006 | 0.020314 | 0.061917 | -121.7429 | -0.12222 | -122.1936 | 0.83961 | 0.69636 | 0.97069 | -122.3203 | -122.0033 | -0.11411 | -122.0332 | 0.81707 | 0.88822 | 0.39235 | -122.6521 | -0.001312 | -0.007253 | 0.57617 | 0.12547 | 0.12678 | -0.15051 | 0.12383 | -0.33306 | -0.029796 | 0.31578 | 0.28585 | 0.61891 | 0.041357 | -0.45451 | 123.1586 | 123.0154 | 123.2897 | 122.1968 | -123.1672 | 123.1361 | 123.2073 | 122.7114 | 122.2049 | -123.499
566.8906 | 123.3261 | -122.438 | 0.77362 | 1.4211e-13 | -0.0056581 | 0.0012394 | 0.064186 | -0.0073159 | 0.061635 | -0.013659 | -0.0035271 | -0.0021323 | 0.070006 | 0.020741 | 0.061703 | -121.8665 | -0.11306 | -122.308 | 0.72057 | 0.58646 | 0.83791 | -122.4211 | -122.1131 | -0.10495 | -122.1568 | 0.69345 | 0.77375 | 0.22295 | -122.7757 | 0.01697 | -0.053049 | 0.57157 | 0.13003 | 0.11306 | -0.18716 | 0.064293 | -0.33767 | -0.080173 | 0.32491 | 0.28124 | 0.61891 | 0.000134 | -0.55068 | 123.1586 | 123.0245 | 123.276 | 122.325 | -123.1947 | 123.1315 | 123.2118 | 122.661 | 122.3331 | -123.5493
568.5625 | 123.3627 | -122.2275 | 0.9613 | 1.4211e-13 | -0.0054445 | 0.00081202 | 0.064186 | -0.0071023 | 0.061635 | -0.013659 | -0.0037407 | -0.0021323 | 0.069579 | 0.020314 | 0.06213 | -121.6559 | -0.12222 | -122.0974 | 0.9266 | 0.80167 | 1.0577 | -122.2196 | -121.9025 | -0.11411 | -121.9416 | 0.90864 | 0.98437 | 0.4885 | -122.5605 | 0.007872 | -0.034704 | 0.5716 | 0.13006 | 0.12219 | -0.15963 | 0.096382 | -0.33303 | -0.052667 | 0.32495 | 0.28587 | 0.6189 | 0.023066 | -0.4728 | 123.1541 | 123.0291 | 123.2852 | 122.1053 | -123.1809 | 123.1361 | 123.2118 | 122.716 | 122.1134 | -123.5218
570.3125 | 123.2346 | -122.168 | 1.0712 | 1.4211e-13 | -0.0052307 | 0.0012394 | 0.064186 | -0.0071023 | 0.061849 | -0.006028 | -0.0035271 | -0.0021323 | 0.069579 | 0.020314 | 0.061703 | -121.7612 | -0.11306 | -122.2073 | 0.80756 | 0.67346 | 0.92949 | -122.3341 | -122.017 | -0.095794 | -122.0607 | 0.78502 | 0.85617 | 0.3603 | -122.6704 | -0.16611 | -0.2636 | 0.40679 | -0.039326 | 0.12678 | -0.39771 | -0.14168 | -0.50243 | -0.28615 | 0.15098 | 0.10731 | 0.60975 | -0.215 | -0.71086 | 122.9755 | 122.8414 | 123.0975 | 122.0549 | -123.4052 | 122.953 | 123.0241 | 122.5283 | 122.0722 | -123.7416
572.0625 | 123.2758 | -122.2366 | 0.99792 | 1.4211e-13 | -0.0054445 | 0.0012394 | 0.0644 | -0.0071023 | 0.061635 | 0.0016025 | -0.0037407 | -0.0023459 | 0.069792 | 0.020955 | 0.061703 | -121.6192 | -0.11306 | -122.0516 | 0.95865 | 0.81999 | 1.0852 | -122.1784 | -121.8613 | -0.10037 | -121.905 | 0.93153 | 1.0164 | 0.53887 | -122.5239 | 0.058237 | -0.039277 | 0.61738 | 0.185 | 0.12676 | -0.17794 | 0.087233 | -0.28725 | -0.066395 | 0.37532 | 0.33165 | 0.6189 | 0.018495 | -0.45906 | 123.1953 | 123.0566 | 123.3218 | 122.1236 | -123.1763 | 123.1682 | 123.2531 | 122.7755 | 122.1363 | -123.5218
573.7969 | 123.262 | -122.1909 | 1.0345 | 1.4211e-13 | -0.0056581 | 0.0012394 | 0.063759 | -0.0071023 | 0.061635 | 0.0016025 | -0.0037407 | -0.0023459 | 0.070006 | 0.020528 | 0.061703 | -121.6284 | -0.11306 | -122.0699 | 0.94034 | 0.81541 | 1.0668 | -122.1876 | -121.8796 | -0.10495 | -121.9141 | 0.92237 | 0.99811 | 0.50682 | -122.533 | 0.003303 | -0.094211 | 0.56245 | 0.12091 | 0.11761 | -0.21914 | 0.032298 | -0.34218 | -0.11217 | 0.31123 | 0.27672 | 0.6189 | -0.03644 | -0.52773 | 123.1312 | 123.0063 | 123.2577 | 122.0778 | -123.2221 | 123.1132 | 123.189 | 122.6977 | 122.0859 | -123.5676
575.4844 | 123.381 | -121.9666 | 1.1993 | 1.4211e-13 | -0.0054445 | 0.0012394 | 0.0644 | -0.0071023 | 0.061422 | 0.0016025 | -0.0035271 | -0.0023459 | 0.070006 | 0.020741 | 0.061917 | -121.2438 | -0.11764 | -121.6762 | 1.3249 | 1.1817 | 1.4514 | -121.8396 | -121.4996 | -0.10495 | -121.5295 | 1.2932 | 1.3736 | 0.92805 | -122.1393 | 0.127 | 0.12558 | 0.72273 | 0.29034 | 0.16334 | -0.017619 | 0.25211 | -0.17271 | 0.09389 | 0.46696 | 0.43703 | 0.60974 | 0.17421 | -0.27129 | 123.2915 | 123.1483 | 123.418 | 121.8489 | -123.0389 | 123.2598 | 123.3401 | 122.8946 | 121.8616 | -123.3386
577.1875 | 123.3582 | -121.6095 | 1.5427 | 1.4211e-13 | -0.0056581 | 0.0012394 | 0.064186 | -0.0068885 | 0.061635 | 0.0016025 | -0.0037407 | -0.0025597 | 0.069579 | 0.020528 | 0.061703 | -121.0836 | -0.11764 | -121.5251 | 1.4806 | 1.342 | 1.598 | -121.6656 | -121.3439 | -0.10953 | -121.3693 | 1.4535 | 1.5384 | 1.07 | -121.9927 | -0.056059 | -0.062079 | 0.52592 | 0.084366 | 0.14042 | -0.20068 | 0.055298 | -0.38324 | -0.089186 | 0.26558 | 0.24023 | 0.62347 | -0.004283 | -0.47268 | 123.0901 | 122.9515 | 123.2075 | 121.4919 | -123.2082 | 123.063 | 123.1479 | 122.6795 | 121.5 | -123.5354
578.9375 | 123.2803 | -121.3989 | 1.767 | 1.4211e-13 | -0.0056581 | 0.001453 | 0.064186 | -0.0064613 | 0.061422 | 0.0016025 | -0.0037407 | -0.0025597 | 0.069792 | 0.020955 | 0.061917 | -121.1431 | -0.11764 | -121.5938 | 1.4165 | 1.2733 | 1.5339 | -121.7526 | -121.408 | -0.10495 | -121.4288 | 1.3848 | 1.4743 | 1.0929 | -122.0568 | -0.35363 | -0.35048 | 0.25583 | -0.19488 | 0.15875 | -0.49367 | -0.23311 | -0.65792 | -0.38217 | -0.009097 | -0.029866 | 0.62805 | -0.29269 | -0.67409 | 122.8154 | 122.6722 | 122.9328 | 121.2813 | -123.5195 | 122.7837 | 122.8732 | 122.4918 | 121.294 | -123.8238
580.625 | 123.2254 | -122.0306 | 1.181 | 1.4211e-13 | -0.0056581 | 0.0010256 | 0.064186 | -0.0071023 | 0.061635 | -0.006028 | -0.0037407 | -0.0023459 | 0.070006 | 0.020741 | 0.061917 | -121.4636 | -0.11764 | -121.9097 | 1.0868 | 0.9482 | 1.2088 | -122.0364 | -121.7285 | -0.10037 | -121.7585 | 1.0597 | 1.1492 | 0.62128 | -122.3819 | -0.005809 | -0.094187 | 0.56706 | 0.12093 | 0.12674 | -0.23283 | 0.02775 | -0.3513 | -0.1213 | 0.30211 | 0.27218 | 0.62348 | -0.03183 | -0.55975 | 123.1175 | 122.9788 | 123.2394 | 121.913 | -123.2175 | 123.0904 | 123.1798 | 122.6519 | 121.9303 | -123.563
582.3906 | 123.3353 | -121.7697 | 1.4465 | 1.4211e-13 | -0.0052307 | 0.0012394 | 0.063759 | -0.0071023 | 0.061635 | -0.006028 | -0.0037407 | -0.0021323 | 0.069792 | 0.020741 | 0.061917 | -121.3629 | -0.11764 | -121.8181 | 1.1876 | 1.0581 | 1.3049 | -121.9449 | -121.6141 | -0.10495 | -121.6531 | 1.165 | 1.2499 | 0.7678 | -122.2766 | -0.17516 | -0.25897 | 0.40686 | -0.048427 | 0.12673 | -0.38844 | -0.1416 | -0.50691 | -0.2815 | 0.15565 | 0.11656 | 0.62348 | -0.1966 | -0.67873 | 122.9573 | 122.8278 | 123.0746 | 121.6521 | -123.3914 | 122.9347 | 123.0196 | 122.5375 | 121.6648 | -123.7232
584.1406 | 123.2895 | -122.1634 | 1.0162 | 1.4211e-13 | -0.0054445 | 0.0010256 | 0.064186 | -0.0068885 | 0.061208 | -0.006028 | -0.0035271 | -0.0021323 | 0.069792 | 0.020741 | 0.061917 | -121.5597 | -0.11306 | -121.9967 | 0.99985 | 0.86578 | 1.1309 | -122.1234 | -121.8109 | -0.10953 | -121.8455 | 0.98189 | 1.0576 | 0.66707 | -122.4644 | 0.039942 | -0.016381 | 0.60366 | 0.1667 | 0.12675 | -0.15046 | 0.11471 | -0.30096 | -0.034342 | 0.35244 | 0.31794 | 0.6189 | 0.041393 | -0.34917 | 123.1632 | 123.0292 | 123.2943 | 122.0503 | -123.1397 | 123.1453 | 123.221 | 122.8305 | 122.0539 | -123.4806
585.8906 | 123.2803 | -122.1634 | 1.0208 | 1.4211e-13 | -0.0054445 | 0.001453 | 0.063973 | -0.0068885 | 0.061422 | 0.0016025 | -0.0035271 | -0.0017051 | 0.070006 | 0.020741 | 0.061917 | -121.5414 | -0.11764 | -122.0059 | 1.009 | 0.87035 | 1.1309 | -122.0822 | -121.7972 | -0.10953 | -121.8363 | 0.98189 | 1.0668 | 0.58466 | -122.4552 | 0.081153 | -0.011802 | 0.62198 | 0.15754 | 0.076387 | -0.15046 | 0.11013 | -0.29181 | -0.03892 | 0.36618 | 0.32709 | 0.6189 | 0.045972 | -0.43616 | 123.1724 | 123.0337 | 123.2943 | 122.0458 | -123.1031 | 123.1453 | 123.2302 | 122.748 | 122.0539 | -123.476
587.5781 | 123.3032 | -122.287 | 0.87433 | 1.4211e-13 | -0.0054445 | 0.0012394 | 0.064186 | -0.0075295 | 0.061635 | -0.013659 | -0.0035271 | -0.0019187 | 0.069579 | 0.020955 | 0.061917 | -121.7154 | -0.11764 | -122.1707 | 0.82588 | 0.69178 | 0.95238 | -122.2746 | -121.9666 | -0.10495 | -122.0103 | 0.80333 | 0.88822 | 0.36946 | -122.6292 | 0.012434 | -0.048454 | 0.57159 | 0.11632 | 0.10388 | -0.18255 | 0.07805 | -0.34221 | -0.070997 | 0.32036 | 0.2767 | 0.6189 | 0.013891 | -0.50487 | 123.1129 | 122.9788 | 123.2394 | 122.1693 | -123.1489 | 123.0903 | 123.1752 | 122.6564 | 122.182 | -123.5035
589.3281 | 123.2391 | -122.2504 | 0.95215 | 1.4211e-13 | -0.0056581 | 0.0012394 | 0.0644 | -0.0068885 | 0.061849 | -0.006028 | -0.0033135 | -0.0021323 | 0.070006 | 0.020741 | 0.061703 | -121.6833 | -0.11306 | -122.1249 | 0.87166 | 0.73299 | 0.99816 | -122.2379 | -121.93 | -0.10953 | -121.9645 | 0.84912 | 0.91569 | 0.44272 | -122.5971 | 0.012444 | -0.080489 | 0.56702 | 0.12548 | 0.11304 | -0.21916 | 0.046017 | -0.34678 | -0.10303 | 0.32037 | 0.28587 | 0.63264 | -0.036457 | -0.50943 | 123.122 | 122.9834 | 123.2485 | 122.1373 | -123.1901 | 123.0995 | 123.1661 | 122.6931 | 122.1408 | -123.5493
591.0312 | 123.262 | -122.2641 | 0.9201 | 1.4211e-13 | -0.0056581 | 0.001453 | 0.064186 | -0.0068885 | 0.061635 | 0.0092325 | -0.0033135 | -0.0019187 | 0.069579 | 0.020528 | 0.061917 | -121.6879 | -0.11306 | -122.1524 | 0.85792 | 0.72383 | 0.97069 | -122.2562 | -121.9392 | -0.10495 | -121.9828 | 0.8308 | 0.90653 | 0.45188 | -122.6063 | 0.007861 | -0.062181 | 0.57618 | 0.11174 | 0.10388 | -0.19628 | 0.050588 | -0.3422 | -0.089302 | 0.32495 | 0.28128 | 0.62348 | -0.013571 | -0.46823 | 123.122 | 122.9879 | 123.2348 | 122.151 | -123.1763 | 123.0949 | 123.1706 | 122.716 | 122.1591 | -123.5264
592.7812 | 123.175 | -122.3145 | 0.90179 | 1.4211e-13 | -0.0056581 | 0.0012394 | 0.063759 | -0.0071023 | 0.061422 | 0.0016025 | -0.0035271 | -0.0025597 | 0.070006 | 0.020955 | 0.061703 | -121.7108 | -0.11306 | -122.1615 | 0.84419 | 0.70093 | 0.95696 | -122.2746 | -121.9575 | -0.11411 | -121.9966 | 0.81707 | 0.88822 | 0.36946 | -122.6246 | 0.0399 | -0.057605 | 0.60364 | 0.15294 | 0.11304 | -0.20086 | 0.055163 | -0.31016 | -0.084727 | 0.35698 | 0.3179 | 0.62806 | -0.013574 | -0.53233 | 123.1586 | 123.0154 | 123.2714 | 122.2014 | -123.1763 | 123.1315 | 123.2027 | 122.6839 | 122.2003 | -123.5264
594.5312 | 123.3032 | -122.2458 | 0.86975 | 1.4211e-13 | -0.0060855 | 0.00081202 | 0.063973 | -0.0071023 | 0.061635 | -0.006028 | -0.0035271 | -0.0023459 | 0.069792 | 0.020955 | 0.061703 | -121.7154 | -0.11764 | -122.1615 | 0.82588 | 0.69178 | 0.95696 | -122.2791 | -121.9712 | -0.10953 | -122.0103 | 0.80333 | 0.87906 | 0.3832 | -122.6292 | -0.033343 | -0.043876 | 0.53039 | 0.084277 | 0.11762 | -0.17797 | 0.087206 | -0.3834 | -0.066419 | 0.27459 | 0.2355 | 0.6189 | 0.009311 | -0.48656 | 123.0717 | 122.9376 | 123.2027 | 122.1282 | -123.1489 | 123.0491 | 123.1249 | 122.629 | 122.1363 | -123.4989
596.2188 | 123.2117 | -122.1863 | 1.0025 | 1.4211e-13 | -0.0056581 | 0.0012394 | 0.063973 | -0.0073159 | 0.061635 | 0.0016025 | -0.0035271 | -0.0019187 | 0.069579 | 0.021596 | 0.061917 | -121.5918 | -0.11764 | -122.0333 | 0.94491 | 0.81541 | 1.0714 | -122.1601 | -121.8476 | -0.10953 | -121.8729 | 0.92237 | 1.0073 | 0.49766 | -122.5056 | 0.026199 | -0.057589 | 0.5945 | 0.15296 | 0.12676 | -0.18709 | 0.06892 | -0.31929 | -0.080129 | 0.3387 | 0.31335 | 0.63264 | 0.004761 | -0.50484 | 123.1312 | 123.0017 | 123.2577 | 122.0686 | -123.1626 | 123.1087 | 123.1935 | 122.6839 | 122.0767 | -123.5081
597.9688 | 123.3353 | -122.2321 | 0.86975 | 1.4211e-13 | -0.0056581 | 0.0010256 | 0.064186 | -0.0071023 | 0.061635 | -0.006028 | -0.0035271 | -0.0021323 | 0.069365 | 0.021169 | 0.06213 | -121.6879 | -0.12222 | -122.1478 | 0.84419 | 0.70551 | 0.95696 | -122.27 | -121.9483 | -0.10495 | -121.9874 | 0.82165 | 0.89738 | 0.39693 | -122.6063 | -0.037918 | -0.025562 | 0.54413 | 0.084278 | 0.1222 | -0.16424 | 0.087206 | -0.37424 | -0.048105 | 0.28374 | 0.24466 | 0.6189 | 0.027626 | -0.47282 | 123.0762 | 122.9376 | 123.189 | 122.1098 | -123.1397 | 123.0537 | 123.1294 | 122.629 | 122.1271 | -123.4761
599.6562 | 123.2666 | -122.2778 | 0.86975 | 1.4211e-13 | -0.0056581 | 0.0012394 | 0.063973 | -0.0073159 | 0.061635 | -0.006028 | -0.0037407 | -0.0023459 | 0.069579 | 0.020741 | 0.061917 | -121.6833 | -0.11764 | -122.1249 | 0.85335 | 0.71925 | 0.97985 | -122.2517 | -121.9392 | -0.10953 | -121.9691 | 0.8308 | 0.90653 | 0.39693 | -122.6063 | 0.026173 | -0.016405 | 0.59449 | 0.15295 | 0.12677 | -0.1505 | 0.1101 | -0.32847 | -0.038948 | 0.33868 | 0.30875 | 0.63722 | 0.036783 | -0.47282 | 123.1312 | 122.9971 | 123.2577 | 122.1602 | -123.1214 | 123.1086 | 123.1844 | 122.6748 | 122.1683 | -123.4761
601.4219 | 123.3124 | -122.0215 | 1.0849 | 1.4211e-13 | -0.0056581 | 0.0012394 | 0.064186 | -0.0075295 | 0.061635 | -0.013659 | -0.0033135 | -0.0023459 | 0.069792 | 0.020955 | 0.061917 | -121.4041 | -0.12222 | -121.8502 | 1.1235 | 0.98483 | 1.2454 | -121.9723 | -121.6553 | -0.10495 | -121.6989 | 1.0964 | 1.1858 | 0.63502 | -122.327 | 0.04914 | 0.03857 | 0.61742 | 0.1713 | 0.12216 | -0.10007 | 0.16051 | -0.30551 | 0.011455 | 0.36621 | 0.32255 | 0.62806 | 0.10093 | -0.44988 | 123.145 | 123.0063 | 123.2669 | 121.8993 | -123.0572 | 123.1178 | 123.2073 | 122.6565 | 121.9165 | -123.4119
603.125 | 123.3307 | -122.1085 | 1.0025 | 1.4211e-13 | -0.0056581 | 0.0012394 | 0.064186 | -0.0071023 | 0.061635 | -0.006028 | -0.0033135 | -0.0023459 | 0.069365 | 0.021169 | 0.061703 | -121.5185 | -0.11306 | -121.9692 | 1.0044 | 0.86578 | 1.1309 | -122.0685 | -121.7835 | -0.10495 | -121.8134 | 0.97732 | 1.0576 | 0.53429 | -122.4506 | 0.039957 | 0.00193 | 0.58994 | 0.13923 | 0.099277 | -0.13673 | 0.12844 | -0.34216 | -0.025187 | 0.32498 | 0.29505 | 0.63722 | 0.055126 | -0.46821 | 123.1129 | 122.9742 | 123.2394 | 121.9954 | -123.071 | 123.0858 | 123.1661 | 122.6427 | 122.0035 | -123.4531
604.875 | 123.3124 | -122.3053 | 0.84686 | 1.4211e-13 | -0.0054445 | 0.0012394 | 0.063759 | -0.0073159 | 0.061635 | 0.0016025 | -0.0030999 | -0.0023459 | 0.069579 | 0.020741 | 0.061917 | -121.7108 | -0.11764 | -122.1478 | 0.83045 | 0.69178 | 0.94322 | -122.2837 | -121.962 | -0.10953 | -121.992 | 0.80333 | 0.87906 | 0.4244 | -122.62 | 0.021587 | -0.016409 | 0.59448 | 0.15752 | 0.13593 | -0.15509 | 0.096358 | -0.31474 | -0.043531 | 0.34325 | 0.31332 | 0.62806 | 0.032199 | -0.42246 | 123.1358 | 122.9971 | 123.2485 | 122.1877 | -123.1306 | 123.1086 | 123.1844 | 122.7297 | 122.1958 | -123.4669
606.5625 | 123.2254 | -122.2321 | 0.91553 | 1.4211e-13 | -0.0058717 | 0.0012394 | 0.063973 | -0.0073159 | 0.061422 | -0.006028 | -0.0035271 | -0.0021323 | 0.070006 | 0.021382 | 0.061703 | -121.665 | -0.11306 | -122.1249 | 0.85335 | 0.71009 | 0.97527 | -122.2425 | -121.9254 | -0.11411 | -121.9599 | 0.8308 | 0.90195 | 0.40609 | -122.588 | -0.010445 | -0.062181 | 0.56703 | 0.10717 | 0.11762 | -0.20544 | 0.059745 | -0.35593 | -0.084724 | 0.30664 | 0.27213 | 0.62806 | -0.013572 | -0.50944 | 123.0854 | 122.9421 | 123.2073 | 122.119 | -123.158 | 123.0629 | 123.134 | 122.6381 | 122.1179 | -123.5035
608.3125 | 123.1888 | -122.2412 | 0.9613 | 1.4211e-13 | -0.0058717 | 0.0012394 | 0.0644 | -0.0071023 | 0.061422 | -0.006028 | -0.0033135 | -0.0023459 | 0.069579 | 0.021169 | 0.061703 | -121.6376 | -0.12222 | -122.0791 | 0.88539 | 0.75588 | 1.0119 | -122.1921 | -121.8934 | -0.10495 | -121.9187 | 0.85827 | 0.94316 | 0.43356 | -122.5514 | 0.049078 | -0.07591 | 0.60365 | 0.16211 | 0.11303 | -0.20542 | 0.050596 | -0.31014 | -0.10303 | 0.34785 | 0.3225 | 0.63264 | -0.018141 | -0.52774 | 123.1266 | 122.9971 | 123.2531 | 122.119 | -123.1534 | 123.0995 | 123.1844 | 122.6748 | 122.1363 | -123.5127
610.0625 | 123.2483 | -122.1909 | 0.95215 | 1.4211e-13 | -0.0060855 | 0.0012394 | 0.063973 | -0.0068885 | 0.061422 | -0.006028 | -0.0035271 | -0.0021323 | 0.069792 | 0.021169 | 0.061917 | -121.6376 | -0.11764 | -122.0883 | 0.88997 | 0.7513 | 1.0073 | -122.2059 | -121.8934 | -0.10953 | -121.9279 | 0.85369 | 0.92485 | 0.4473 | -122.5651 | -0.015012 | -0.062175 | 0.5533 | 0.1026 | 0.11761 | -0.20084 | 0.055174 | -0.37423 | -0.098453 | 0.29749 | 0.26299 | 0.63722 | -0.0273 | -0.50485 | 123.0808 | 122.9422 | 123.1982 | 122.0732 | -123.158 | 123.0446 | 123.1157 | 122.6382 | 122.0813 | -123.5172
611.8125 | 123.1888 | -122.1359 | 1.0437 | 1.4211e-13 | -0.0056581 | 0.0012394 | 0.063759 | -0.0068885 | 0.061208 | -0.006028 | -0.0037407 | -0.0021323 | 0.070006 | 0.021169 | 0.061276 | -121.5094 | -0.11764 | -121.9509 | 1.0136 | 0.87035 | 1.1401 | -122.2196 | -121.756 | -0.10037 | -121.7859 | 0.98647 | 1.0714 | 0.53887 | -122.4323 | -0.083681 | -0.030112 | 0.62656 | 0.18501 | 0.26869 | -0.17335 | 0.0964 | -0.29638 | -0.057229 | 0.37992 | 0.34999 | 0.64637 | 0.027663 | -0.50483 | 123.1495 | 123.0063 | 123.276 | 122.0183 | -123.2633 | 123.1224 | 123.2073 | 122.6748 | 122.0356 | -123.476
613.5 | 123.2849 | -122.1817 | 0.92926 | 1.4211e-13 | -0.0058717 | 0.0012394 | 0.064186 | -0.0073159 | 0.062063 | -0.006028 | -0.0035271 | -0.0021323 | 0.069792 | 0.021169 | 0.061489 | -121.2804 | -0.13137 | -121.7266 | 1.2471 | 1.0947 | 1.3645 | -121.9128 | -121.5454 | -0.10953 | -121.5707 | 1.2062 | 1.282 | 0.90058 | -122.1942 | 0.26888 | 0.31783 | 0.90126 | 0.45513 | 0.18624 | 0.16546 | 0.43519 | -0.012504 | 0.27698 | 0.63632 | 0.61097 | 0.62347 | 0.35272 | -0.028682 | 123.4288 | 123.2764 | 123.5462 | 122.0503 | -122.8421 | 123.3879 | 123.4637 | 123.0823 | 122.0722 | -123.1235
615.25 | 123.2162 | -121.8567 | 1.2863 | 1.4211e-13 | -0.0058717 | 0.0012394 | 0.064186 | -0.0071023 | 0.061635 | 0.0016025 | -0.0033135 | -0.0025597 | 0.069792 | 0.020955 | 0.061489 | -121.3354 | -0.11306 | -121.7952 | 1.1693 | 1.0398 | 1.2958 | -121.8762 | -121.5912 | -0.10037 | -121.6303 | 1.1467 | 1.227 | 0.70828 | -122.2537 | -0.019498 | -0.11706 | 0.5213 | 0.061439 | 0.080937 | -0.24654 | 0.009458 | -0.39704 | -0.1396 | 0.26552 | 0.22643 | 0.62347 | -0.05928 | -0.57804 | 123.0259 | 122.8965 | 123.1525 | 121.7436 | -123.1625 | 123.0034 | 123.0837 | 122.565 | 121.7563 | -123.54
617.0156 | 123.3307 | -121.8521 | 1.2726 | 1.4211e-13 | -0.0058717 | 0.0016666 | 0.063973 | -0.0075295 | 0.061422 | -0.021289 | -0.0035271 | -0.0021323 | 0.069365 | 0.020741 | 0.061703 | -121.2713 | -0.12222 | -121.7312 | 1.2288 | 1.0947 | 1.3461 | -121.8853 | -121.5271 | -0.10495 | -121.5662 | 1.2062 | 1.282 | 0.84564 | -122.1988 | -0.033233 | -0.04381 | 0.58082 | 0.12096 | 0.15419 | -0.17786 | 0.073555 | -0.34667 | -0.066344 | 0.32504 | 0.28596 | 0.63263 | 0.009396 | -0.42695 | 123.0809 | 122.9468 | 123.1983 | 121.7299 | -123.1579 | 123.0584 | 123.1341 | 122.6977 | 121.7472 | -123.4714
618.6875 | 123.2895 | -121.8842 | 1.2177 | 1.4211e-13 | -0.0058717 | 0.001453 | 0.0644 | -0.0073159 | 0.061635 | 0.0016025 | -0.0037407 | -0.0021323 | 0.070006 | 0.020955 | 0.061703 | -120.8318 | -0.14511 | -121.2687 | 1.682 | 1.5343 | 1.804 | -121.4549 | -121.0875 | -0.12327 | -121.1129 | 1.6504 | 1.7215 | 1.2898 | -121.7501 | 0.42923 | 0.46438 | 1.0524 | 0.61541 | 0.18618 | 0.31665 | 0.58635 | 0.13409 | 0.4327 | 0.79664 | 0.77129 | 0.6372 | 0.50387 | 0.072108 | 123.5662 | 123.4185 | 123.6882 | 121.739 | -122.6726 | 123.5345 | 123.6057 | 123.1739 | 121.7609 | -122.9677
620.4375 | 123.1613 | -121.0281 | 2.1423 | 1.4211e-13 | -0.0058717 | 0.0012394 | 0.063759 | -0.0073159 | 0.061422 | -0.006028 | -0.0037407 | -0.0023459 | 0.069365 | 0.020955 | 0.061489 | -120.5159 | -0.11764 | -120.9574 | 1.9979 | 1.8548 | 2.1016 | -121.1939 | -120.767 | -0.10953 | -120.7924 | 1.9754 | 2.042 | 1.7064 | -121.4295 | -0.16579 | -0.14439 | 0.51228 | 0.070712 | 0.2365 | -0.28751 | -0.040726 | -0.40141 | -0.16691 | 0.26113 | 0.23579 | 0.63719 | -0.10031 | -0.43592 | 123.0261 | 122.883 | 123.1297 | 120.9105 | -123.3363 | 123.0036 | 123.0702 | 122.7345 | 120.9186 | -123.5719
622.1875 | 123.1796 | -120.5154 | 2.417 | 1.4211e-13 | -0.0058717 | 0.001453 | 0.064186 | -0.0075295 | 0.061208 | 0.0016025 | -0.0035271 | -0.0023459 | 0.069792 | 0.020955 | 0.061703 | -121.5506 | -0.11764 | -122.0059 | 0.94949 | 0.81999 | 1.0668 | -122.1418 | -121.8064 | -0.11411 | -121.8409 | 0.93153 | 1.0027 | 0.54345 | -122.4918 | -1.6263 | -1.4675 | -1.0351 | -1.4904 | 0.13591 | -1.597 | -1.3501 | -1.9764 | -1.4855 | -1.2909 | -1.3254 | 0.65095 | -1.4143 | -1.8735 | 121.4649 | 121.3354 | 121.5823 | 120.3978 | -124.5588 | 121.447 | 121.5181 | 121.0589 | 120.4013 | -124.9088
623.875 | 123.2391 | -122.287 | 0.85144 | 1.4211e-13 | -0.0060855 | 0.0010256 | 0.064186 | -0.0075295 | 0.061422 | -0.013659 | -0.0035271 | -0.0025597 | 0.069365 | 0.021382 | 0.061489 | -121.7108 | -0.10848 | -122.1615 | 0.79841 | 0.65514 | 0.91117 | -122.2746 | -121.9666 | -0.095794 | -122.0011 | 0.7667 | 0.84243 | 0.33741 | -122.6475 | 0.012434 | -0.053035 | 0.57617 | 0.12547 | 0.11304 | -0.19629 | 0.059731 | -0.36052 | -0.084736 | 0.32036 | 0.28586 | 0.64638 | -0.009006 | -0.51403 | 123.0854 | 122.9421 | 123.1982 | 122.1785 | -123.126 | 123.0537 | 123.1294 | 122.6244 | 122.1912 | -123.4989
625.6094 | 123.1567 | -121.5225 | 1.8036 | 1.4211e-13 | -0.0060855 | 0.0012394 | 0.063973 | -0.0073159 | 0.061208 | 0.0016025 | -0.0035271 | -0.0023459 | 0.069579 | 0.021169 | 0.061703 | -121.1156 | -0.11306 | -121.5663 | 1.3799 | 1.2412 | 1.4972 | -121.7846 | -121.376 | -0.10495 | -121.4105 | 1.3573 | 1.4285 | 1.0517 | -122.0523 | -0.26209 | -0.42373 | 0.4069 | -0.043814 | 0.21827 | -0.56234 | -0.30636 | -0.52974 | -0.44626 | 0.14655 | 0.11204 | 0.64178 | -0.37509 | -0.75192 | 122.9024 | 122.7638 | 123.0198 | 121.4095 | -123.5882 | 122.8799 | 122.951 | 122.5742 | 121.4176 | -123.8559
627.3594 | 123.1659 | -121.5179 | 1.6296 | 1.4211e-13 | -0.0058717 | 0.00081202 | 0.063759 | -0.0071023 | 0.060567 | 0.0016025 | -0.0033135 | -0.0023459 | 0.069792 | 0.021596 | 0.061489 | -120.8409 | -0.12679 | -121.2916 | 1.6591 | 1.5206 | 1.7765 | -121.4137 | -121.0829 | -0.10495 | -121.1266 | 1.6275 | 1.7078 | 1.3493 | -121.7684 | 0.10423 | 0.029503 | 0.67702 | 0.2263 | 0.12208 | -0.10908 | 0.14689 | -0.25043 | -0.002178 | 0.43501 | 0.39135 | 0.64178 | 0.07815 | -0.28036 | 123.1771 | 123.0385 | 123.2945 | 121.3911 | -123.0434 | 123.1454 | 123.2257 | 122.8672 | 121.413 | -123.398
629.1094 | 123.2574 | -122.2366 | 0.85602 | 1.4211e-13 | -0.0062991 | 0.00081202 | 0.063545 | -0.0073159 | 0.060994 | 0.0016025 | -0.0035271 | -0.0023459 | 0.07022 | 0.021382 | 0.061917 | -121.665 | -0.11764 | -122.1295 | 0.82588 | 0.69178 | 0.93864 | -122.2333 | -121.93 | -0.10037 | -121.9645 | 0.79417 | 0.87448 | 0.48392 | -122.6155 | 0.00329 | -0.030143 | 0.5716 | 0.10717 | 0.10388 | -0.16424 | 0.082625 | -0.37882 | -0.061843 | 0.30664 | 0.27213 | 0.65096 | 0.018466 | -0.37209 | 123.0625 | 122.9284 | 123.1753 | 122.119 | -123.0894 | 123.0308 | 123.1111 | 122.7206 | 122.1363 | -123.4715
630.8594 | 123.2025 | -122.3236 | 0.81024 | 1.4211e-13 | -0.0060855 | 0.0010256 | 0.063973 | -0.0073159 | 0.060994 | 0.0016025 | -0.0035271 | -0.0021323 | 0.069792 | 0.021382 | 0.061703 | -121.7474 | -0.11764 | -122.1981 | 0.74346 | 0.60478 | 0.86538 | -122.3249 | -121.9941 | -0.10495 | -122.0469 | 0.71634 | 0.80123 | 0.4244 | -122.6841 | -0.001313 | -0.066778 | 0.57617 | 0.12547 | 0.12678 | -0.20547 | 0.055143 | -0.36053 | -0.093902 | 0.32951 | 0.27669 | 0.63722 | -0.009016 | -0.38584 | 123.0671 | 122.9284 | 123.189 | 122.206 | -123.1352 | 123.0399 | 123.1248 | 122.748 | 122.2187 | -123.4944
632.5625 | 123.2758 | -121.9894 | 1.0529 | 1.4211e-13 | -0.0060855 | 0.0010256 | 0.063973 | -0.0073159 | 0.061208 | -0.006028 | -0.0035271 | -0.0025597 | 0.069579 | 0.021382 | 0.061703 | -121.4132 | -0.11306 | -121.8731 | 1.0823 | 0.93446 | 1.195 | -121.9861 | -121.669 | -0.10495 | -121.6944 | 1.0506 | 1.1263 | 0.80901 | -122.3453 | 0.00336 | 0.029409 | 0.57622 | 0.11636 | 0.113 | -0.1184 | 0.14219 | -0.35587 | -0.002285 | 0.32043 | 0.29508 | 0.65095 | 0.073451 | -0.24385 | 123.0717 | 122.9239 | 123.1845 | 121.8764 | -123.0389 | 123.04 | 123.1157 | 122.7984 | 121.8845 | -123.3982
634.3125 | 123.1934 | -121.0693 | 2.0737 | 1.4211e-13 | -0.0058717 | 0.0010256 | 0.063973 | -0.0075295 | 0.060994 | 0.0016025 | -0.0035271 | -0.0021323 | 0.070006 | 0.021382 | 0.061489 | -120.7677 | -0.099323 | -121.223 | 1.7141 | 1.5801 | 1.8315 | -121.3542 | -121.0143 | -0.091215 | -121.0533 | 1.7007 | 1.7582 | 1.3859 | -121.686 | -0.28485 | -0.35959 | 0.30167 | -0.15363 | 0.13122 | -0.49358 | -0.2422 | -0.61662 | -0.37295 | 0.055082 | 0.015998 | 0.63262 | -0.31552 | -0.68776 | 122.7834 | 122.6494 | 122.9008 | 120.97 | -123.4279 | 122.7701 | 122.8275 | 122.4552 | 120.9781 | -123.7596
636.0625 | 123.1522 | -121.9711 | 1.2131 | 1.4211e-13 | -0.0062991 | 0.0012394 | 0.063759 | -0.0073159 | 0.061422 | -0.013659 | -0.0033135 | -0.0023459 | 0.070006 | 0.021596 | 0.061703 | -121.3903 | -0.10848 | -121.8548 | 1.0914 | 0.96193 | 1.2088 | -121.9723 | -121.6461 | -0.10037 | -121.6898 | 1.0735 | 1.1446 | 0.77238 | -122.3316 | -0.001214 | -0.12165 | 0.5808 | 0.11636 | 0.11758 | -0.25114 | -0.004294 | -0.36044 | -0.13961 | 0.32501 | 0.28135 | 0.64179 | -0.068453 | -0.4407 | 123.0626 | 122.9331 | 123.1799 | 121.8627 | -123.1854 | 123.0446 | 123.1158 | 122.7435 | 121.8708 | -123.5446
637.8125 | 123.1934 | -121.9162 | 1.2177 | 1.4211e-13 | -0.0058717 | 0.00081202 | 0.063759 | -0.0075295 | 0.060994 | -0.006028 | -0.0033135 | -0.0023459 | 0.069792 | 0.021596 | 0.061276 | -121.3354 | -0.12222 | -121.7952 | 1.1464 | 1.0077 | 1.2591 | -121.8716 | -121.5912 | -0.10037 | -121.6257 | 1.1284 | 1.1996 | 0.80443 | -122.2766 | 0.044591 | -0.071289 | 0.58081 | 0.12095 | 0.076358 | -0.20993 | 0.041494 | -0.36043 | -0.089246 | 0.32503 | 0.29052 | 0.65095 | -0.018086 | -0.41322 | 123.0626 | 122.9239 | 123.1753 | 121.794 | -123.0893 | 123.0446 | 123.1158 | 122.7206 | 121.8158 | -123.4943
639.5 | 123.1384 | -122.1085 | 1.0391 | 1.4211e-13 | -0.0060855 | 0.00081202 | 0.063759 | -0.0073159 | 0.060994 | -0.013659 | -0.0037407 | -0.0025597 | 0.069792 | 0.021169 | 0.061703 | -121.4956 | -0.12222 | -121.9601 | 0.98612 | 0.8383 | 1.1081 | -122.0639 | -121.7468 | -0.10953 | -121.7859 | 0.959 | 1.0256 | 0.71286 | -122.4415 | 0.044536 | -0.053005 | 0.61283 | 0.14839 | 0.10385 | -0.20082 | 0.068927 | -0.333 | -0.080123 | 0.36161 | 0.32253 | 0.65553 | -0.013546 | -0.32627 | 123.0946 | 122.9468 | 123.2165 | 121.9862 | -123.103 | 123.0675 | 123.134 | 122.8213 | 121.9989 | -123.4806
641.25 | 123.2483 | -120.9595 | 2.1286 | 1.4211e-13 | -0.0060855 | 0.0010256 | 0.064186 | -0.0073159 | 0.060994 | 0.0016025 | -0.0033135 | -0.0023459 | 0.069579 | 0.021169 | 0.061703 | -120.3831 | -0.12222 | -120.8292 | 2.1032 | 1.951 | 2.2161 | -120.9558 | -120.6342 | -0.091215 | -120.6641 | 2.0716 | 2.1382 | 1.8758 | -121.3151 | 0.00365 | -0.025356 | 0.57639 | 0.13024 | 0.12659 | -0.17762 | 0.087472 | -0.3556 | -0.057026 | 0.32525 | 0.29533 | 0.65093 | 0.009577 | -0.25278 | 123.0627 | 122.9105 | 123.1755 | 120.8373 | -123.0844 | 123.031 | 123.0977 | 122.8353 | 120.8683 | -123.4437
643 | 123.1247 | -120.845 | 2.3117 | 1.4211e-13 | -0.0062991 | 0.001453 | 0.064186 | -0.0073159 | 0.060781 | 0.0016025 | -0.0033135 | -0.0021323 | 0.069579 | 0.021596 | 0.061489 | -120.351 | -0.12222 | -120.8201 | 2.117 | 1.9876 | 2.2298 | -120.9192 | -120.6022 | -0.10037 | -120.6367 | 2.0945 | 2.1702 | 1.8575 | -121.283 | -0.07416 | -0.19473 | 0.494 | 0.024956 | 0.099116 | -0.3241 | -0.081898 | -0.43799 | -0.21724 | 0.24286 | 0.20836 | 0.64635 | -0.14148 | -0.4542 | 122.962 | 122.8326 | 123.0748 | 120.7228 | -123.2309 | 122.9395 | 123.0153 | 122.7025 | 120.7447 | -123.5947
644.6719 | 123.2117 | -122.1497 | 0.96588 | 1.4211e-13 | -0.0058717 | 0.0010256 | 0.063759 | -0.0073159 | 0.060994 | -0.006028 | -0.0035271 | -0.0021323 | 0.069579 | 0.021596 | 0.061489 | -121.5506 | -0.12222 | -122.0333 | 0.90829 | 0.78336 | 1.0348 | -122.1418 | -121.8201 | -0.10953 | -121.85 | 0.89032 | 0.96606 | 0.63502 | -122.5101 | 0.007894 | -0.057595 | 0.59909 | 0.11634 | 0.10844 | -0.18253 | 0.068912 | -0.36049 | -0.075558 | 0.32955 | 0.29963 | 0.66011 | 0.000175 | -0.33086 | 123.0579 | 122.933 | 123.1845 | 122.0274 | -123.1076 | 123.04 | 123.1157 | 122.7847 | 122.0401 | -123.476
646.4219 | 123.1293 | -122.1359 | 1.0208 | 1.4211e-13 | -0.0060855 | 0.001453 | 0.064186 | -0.0071023 | 0.061208 | 0.0092325 | -0.0035271 | -0.0021323 | 0.070006 | 0.021596 | 0.061489 | -121.546 | -0.11764 | -122.0196 | 0.9266 | 0.78793 | 1.044 | -122.1189 | -121.8018 | -0.10953 | -121.8409 | 0.8949 | 0.96606 | 0.58466 | -122.4873 | 0.017055 | -0.094213 | 0.58993 | 0.11634 | 0.099284 | -0.23288 | 0.023138 | -0.35133 | -0.12591 | 0.33413 | 0.29505 | 0.64637 | -0.054757 | -0.43616 | 123.0625 | 122.9239 | 123.1799 | 122.0183 | -123.1397 | 123.0308 | 123.102 | 122.7206 | 122.0264 | -123.5081
648.1875 | 123.2483 | -121.6324 | 1.4282 | 1.4211e-13 | -0.0060855 | 0.0010256 | 0.064186 | -0.0075295 | 0.061208 | -0.006028 | -0.0033135 | -0.0021323 | 0.070006 | 0.021596 | 0.061489 | -121.1431 | -0.099323 | -121.6075 | 1.3295 | 1.1817 | 1.4423 | -121.7022 | -121.4034 | -0.10037 | -121.4288 | 1.2978 | 1.3781 | 0.92805 | -122.0843 | -0.069803 | -0.098725 | 0.48929 | 0.024844 | 0.094647 | -0.2465 | 0.014066 | -0.45193 | -0.13041 | 0.22894 | 0.20359 | 0.65552 | -0.050093 | -0.50017 | 122.9619 | 122.8141 | 123.0747 | 121.5331 | -123.1304 | 122.9302 | 123.0105 | 122.5604 | 121.532 | -123.5125
649.9375 | 123.1796 | -121.6278 | 1.4694 | 1.4211e-13 | -0.0058717 | 0.0010256 | 0.064186 | -0.0071023 | 0.061208 | 0.024493 | -0.0035271 | -0.0021323 | 0.069579 | 0.021382 | 0.061703 | -121.0973 | -0.11306 | -121.5663 | 1.3707 | 1.2367 | 1.4789 | -121.6839 | -121.3485 | -0.10037 | -121.3876 | 1.339 | 1.4102 | 1.1295 | -122.0339 | -0.056064 | -0.098718 | 0.5305 | 0.061472 | 0.11754 | -0.23275 | 0.009497 | -0.40614 | -0.13041 | 0.27931 | 0.24022 | 0.64636 | -0.059241 | -0.33991 | 122.9985 | 122.8645 | 123.1067 | 121.5147 | -123.1533 | 122.9668 | 123.038 | 122.7573 | 121.5274 | -123.5034
651.6094 | 123.175 | -121.6461 | 1.4694 | 1.4211e-13 | -0.0060855 | 0.0010256 | 0.063973 | -0.0073159 | 0.060781 | -0.006028 | -0.0037407 | -0.0021323 | 0.069792 | 0.021596 | 0.061489 | -120.731 | -0.12679 | -121.1909 | 1.7416 | 1.5847 | 1.8544 | -121.3038 | -120.9868 | -0.11869 | -121.0304 | 1.7007 | 1.7856 | 1.4866 | -121.6768 | 0.3423 | 0.27213 | 0.91508 | 0.4552 | 0.1129 | 0.11525 | 0.38494 | -0.030681 | 0.2313 | 0.65934 | 0.61567 | 0.64635 | 0.3162 | 0.017218 | 123.3877 | 123.2308 | 123.5005 | 121.5193 | -122.7732 | 123.3468 | 123.4317 | 123.1328 | 121.5274 | -123.1462
653.375 | 123.2025 | -121.6965 | 1.3641 | 1.4211e-13 | -0.0062991 | 0.00081202 | 0.064186 | -0.0077431 | 0.061208 | -0.006028 | -0.0035271 | -0.0023459 | 0.069579 | 0.021596 | 0.061703 | -121.2209 | -0.11764 | -121.6899 | 1.2379 | 1.1039 | 1.3553 | -121.7526 | -121.4813 | -0.095794 | -121.5066 | 1.2154 | 1.2957 | 0.96926 | -122.1667 | -0.056084 | -0.12621 | 0.47554 | 0.006522 | 0.062606 | -0.26026 | -0.00884 | -0.47026 | -0.14874 | 0.21519 | 0.18984 | 0.6601 | -0.068421 | -0.39488 | 122.9344 | 122.8004 | 123.0518 | 121.5788 | -123.1167 | 122.9119 | 122.9922 | 122.6657 | 121.6007 | -123.5309
655.0625 | 123.0972 | -122.5479 | 0.52643 | 1.4211e-13 | -0.0060855 | 0.00059822 | 0.063973 | -0.0075295 | 0.060781 | -0.006028 | -0.0035271 | -0.0021323 | 0.069792 | 0.021596 | 0.06213 | -121.9443 | -0.13137 | -122.4179 | 0.56033 | 0.54067 | 0.67308 | -122.6226 | -122.2093 | -0.11411 | -122.1934 | 0.47826 | 0.56314 | 0.56176 | -122.8536 | -0.074639 | 0.033901 | 0.6036 | 0.13002 | 0.20466 | 0.014244 | 0.14666 | -0.30564 | -0.048169 | 0.33862 | 0.35448 | 0.66012 | 0.036711 | 0.035334 | 123.1082 | 123.0886 | 123.221 | 122.4165 | -123.149 | 123.0262 | 123.1111 | 123.1097 | 122.4338 | -123.38
656.8125 | 123.1979 | -122.5204 | 0.56305 | 1.4211e-13 | -0.0060855 | 0.0012394 | 0.063759 | -0.0075295 | 0.061208 | 0.0016025 | -0.0037407 | -0.0021323 | 0.069792 | 0.021596 | 0.061489 | -121.9672 | -0.12222 | -122.3996 | 0.56491 | 0.54525 | 0.67308 | -122.6546 | -122.1818 | -0.10495 | -122.2301 | 0.48742 | 0.56314 | 0.56176 | -122.8856 | -0.13416 | 0.001858 | 0.55324 | 0.12086 | 0.25502 | -0.017798 | 0.11003 | -0.36516 | -0.075633 | 0.33862 | 0.29038 | 0.65554 | 9e-05 | -0.001287 | 123.0854 | 123.0657 | 123.1935 | 122.3982 | -123.2177 | 123.0079 | 123.0836 | 123.0822 | 122.4155 | -123.4487
658.5 | 123.1338 | -122.5616 | 0.54016 | 1.4211e-13 | -0.0060855 | 0.0012394 | 0.063973 | -0.0075295 | 0.060994 | -0.006028 | -0.0035271 | -0.0023459 | 0.069792 | 0.021596 | 0.061489 | -121.9947 | -0.11306 | -122.4271 | 0.55117 | 0.52236 | 0.66851 | -122.6729 | -122.2093 | -0.10495 | -122.2438 | 0.47368 | 0.55856 | 0.54803 | -122.9039 | -0.11127 | 0.011011 | 0.56697 | 0.13459 | 0.24587 | -0.017805 | 0.12834 | -0.34228 | -0.066481 | 0.35235 | 0.31784 | 0.66012 | 0.018399 | 0.007865 | 123.1128 | 123.084 | 123.2302 | 122.4486 | -123.2131 | 123.0353 | 123.1202 | 123.1097 | 122.4567 | -123.4441
660.25 | 123.0835 | -122.5662 | 0.54016 | 1.4211e-13 | -0.0058717 | 0.0012394 | 0.063759 | -0.0075295 | 0.060994 | -0.013659 | -0.0030999 | -0.0023459 | 0.069792 | 0.021596 | 0.061703 | -122.0221 | -0.12222 | -122.4545 | 0.46876 | 0.49488 | 0.63645 | -122.705 | -122.2413 | -0.10495 | -122.2667 | 0.44621 | 0.52651 | 0.52971 | -122.9406 | -0.13875 | -0.0714 | 0.54408 | 0.1117 | 0.25045 | -0.045278 | 0.096294 | -0.37433 | -0.093952 | 0.32487 | 0.29953 | 0.67386 | -0.013651 | -0.01045 | 123.035 | 123.0611 | 123.2027 | 122.444 | -123.2451 | 123.0124 | 123.0927 | 123.0959 | 122.4613 | -123.4807
662 | 123.0927 | -122.5891 | 0.53101 | 1.4211e-13 | -0.0062991 | 0.0010256 | 0.064186 | -0.0075295 | 0.060994 | 0.0016025 | -0.0035271 | -0.0023459 | 0.069579 | 0.021596 | 0.061276 | -122.0313 | -0.11764 | -122.4545 | 0.46876 | 0.49946 | 0.63645 | -122.5676 | -122.2505 | -0.10953 | -122.2804 | 0.45079 | 0.52651 | 0.52971 | -122.9406 | 0.021507 | -0.062245 | 0.55781 | 0.13459 | 0.11308 | -0.031544 | 0.10545 | -0.35144 | -0.080218 | 0.33861 | 0.30868 | 0.66012 | -0.004496 | -0.001295 | 123.0579 | 123.0886 | 123.2256 | 122.4715 | -123.0986 | 123.0399 | 123.1156 | 123.1188 | 122.4796 | -123.4716
663.6875 | 123.2712 | -122.5525 | 0.48065 | 1.4211e-13 | -0.0058717 | 0.0010256 | 0.064186 | -0.0075295 | 0.060781 | -0.013659 | -0.0037407 | -0.0023459 | 0.070006 | 0.02181 | 0.061489 | -122.0405 | -0.12222 | -122.4683 | 0.47334 | 0.49488 | 0.6273 | -122.5722 | -122.2551 | -0.10953 | -122.2804 | 0.44163 | 0.52193 | 0.14053 | -122.9543 | -0.019693 | -0.007313 | 0.51203 | 0.084233 | 0.10393 | 0.014231 | 0.14665 | -0.4018 | -0.039021 | 0.29741 | 0.27206 | 0.67386 | 0.041279 | -0.34012 | 123.0258 | 123.0474 | 123.1798 | 122.4303 | -123.0528 | 122.9941 | 123.0744 | 122.693 | 122.443 | -123.4349
665.4219 | 123.1888 | -122.5525 | 0.52643 | 1.4211e-13 | -0.0062991 | 0.00081202 | 0.0644 | -0.0077431 | 0.060781 | 0.0016025 | -0.0037407 | -0.0023459 | 0.070006 | 0.021382 | 0.061489 | -122.0267 | -0.11764 | -122.4545 | 0.48707 | 0.34836 | 0.64103 | -122.5539 | -122.2368 | -0.10495 | -122.2621 | 0.45537 | 0.53567 | 0.14511 | -122.936 | -0.001378 | -0.039353 | 0.52577 | 0.097968 | 0.099346 | -0.17807 | 0.11461 | -0.38348 | -0.071062 | 0.31572 | 0.29037 | 0.67386 | 0.009239 | -0.38132 | 123.0396 | 122.9008 | 123.1935 | 122.4349 | -123.0803 | 123.0079 | 123.0882 | 122.6976 | 122.4475 | -123.4624
667.1875 | 123.2574 | -122.5296 | 0.52185 | 1.4211e-13 | -0.0062991 | 0.0010256 | 0.063973 | -0.0075295 | 0.060781 | 0.0016025 | -0.0037407 | -0.0023459 | 0.069365 | 0.021596 | 0.061489 | -122.0176 | -0.11764 | -122.4545 | 0.47334 | 0.34836 | 0.65477 | -122.5722 | -122.2459 | -0.10037 | -122.2759 | 0.45079 | 0.53109 | 0.14969 | -122.9451 | -0.042581 | -0.048512 | 0.51203 | 0.07508 | 0.11766 | -0.17349 | 0.13292 | -0.41553 | -0.071063 | 0.28368 | 0.25375 | 0.66928 | 0.009238 | -0.37216 | 123.0029 | 122.878 | 123.1844 | 122.412 | -123.094 | 122.9804 | 123.0607 | 122.6793 | 122.4292 | -123.467
668.9219 | 123.1338 | -122.5708 | 0.5722 | 1.4211e-13 | -0.0062991 | 0.0012394 | 0.064186 | -0.0073159 | 0.060994 | 0.0016025 | -0.0030999 | -0.0019187 | 0.069792 | 0.02181 | 0.061489 | -122.0176 | -0.11764 | -122.4499 | 0.50081 | 0.35752 | 0.65935 | -122.5676 | -122.2368 | -0.10037 | -122.2667 | 0.45994 | 0.54025 | 0.22295 | -122.9406 | 0.003197 | -0.071395 | 0.55323 | 0.12086 | 0.11766 | -0.21469 | 0.087143 | -0.36975 | -0.11226 | 0.33403 | 0.30411 | 0.67386 | -0.031959 | -0.34926 | 123.0716 | 122.9283 | 123.2301 | 122.4532 | -123.1398 | 123.0307 | 123.111 | 122.7937 | 122.4704 | -123.5128
670.5938 | 123.1247 | -122.5983 | 0.54474 | 1.4211e-13 | -0.0060855 | 0.0012394 | 0.0644 | -0.0073159 | 0.061208 | 0.0092325 | -0.0037407 | -0.0023459 | 0.069792 | 0.022023 | 0.061703 | -121.9993 | -0.11306 | -122.4316 | 0.50997 | 0.37583 | 0.67308 | -122.5447 | -122.2139 | -0.11411 | -122.2438 | 0.48742 | 0.55856 | 0.10848 | -122.9222 | 0.053557 | -0.034773 | 0.59901 | 0.16664 | 0.11308 | -0.16891 | 0.12835 | -0.32397 | -0.057323 | 0.38439 | 0.35447 | 0.67844 | 0.013821 | -0.43626 | 123.1082 | 122.9741 | 123.2714 | 122.4852 | -123.0894 | 123.0857 | 123.1568 | 122.7067 | 122.4842 | -123.467
672.3594 | 123.1567 | -122.4747 | 0.63171 | 1.4211e-13 | -0.0058717 | 0.0016666 | 0.0644 | -0.0073159 | 0.060567 | 0.0016025 | -0.0035271 | -0.0025597 | 0.069579 | 0.022023 | 0.061703 | -122.0084 | -0.11764 | -122.4545 | 0.49165 | 0.34836 | 0.65019 | -122.5539 | -122.2413 | -0.10953 | -122.2759 | 0.47368 | 0.53109 | 0.13137 | -122.9406 | -0.079198 | -0.14006 | 0.46626 | 0.020148 | 0.099346 | -0.28336 | 0.018477 | -0.46588 | -0.15803 | 0.23332 | 0.19882 | 0.6647 | -0.10062 | -0.50034 | 122.9663 | 122.823 | 123.1249 | 122.357 | -123.1856 | 122.9484 | 123.0058 | 122.606 | 122.3651 | -123.5723
674.0469 | 123.2162 | -122.5937 | 0.50812 | 1.4211e-13 | -0.0060855 | 0.0012394 | 0.0644 | -0.0073159 | 0.060781 | -0.006028 | -0.0033135 | -0.0021323 | 0.069579 | 0.022023 | 0.061703 | -122.0084 | -0.12222 | -122.4454 | 0.49623 | 0.36667 | 0.66851 | -122.5722 | -122.2413 | -0.11411 | -122.2575 | 0.47368 | 0.54482 | 0.11306 | -122.9314 | 0.021506 | -0.011887 | 0.58528 | 0.14832 | 0.12682 | -0.14144 | 0.16039 | -0.33771 | -0.034438 | 0.35234 | 0.33615 | 0.67386 | 0.036706 | -0.39506 | 123.0899 | 122.9604 | 123.2622 | 122.4715 | -123.0803 | 123.0674 | 123.1385 | 122.7067 | 122.4796 | -123.4395
675.7812 | 123.1293 | -122.525 | 0.61798 | 1.4211e-13 | -0.0060855 | 0.0012394 | 0.063973 | -0.0073159 | 0.061208 | -0.013659 | -0.0037407 | -0.0023459 | 0.069579 | 0.022023 | 0.061489 | -121.9855 | -0.11764 | -122.4316 | 0.51912 | 0.38957 | 0.64561 | -122.5127 | -122.2139 | -0.10037 | -122.2392 | 0.50115 | 0.5723 | 0.18174 | -122.9039 | 0.012367 | -0.098858 | 0.53951 | 0.093393 | 0.081026 | -0.22841 | 0.027631 | -0.3789 | -0.11683 | 0.31115 | 0.2858 | 0.6647 | -0.045685 | -0.43624 | 123.0441 | 122.9146 | 123.1706 | 122.4074 | -123.1306 | 123.0262 | 123.0973 | 122.7068 | 122.4247 | -123.5219
677.5469 | 123.2712 | -122.5067 | 0.54016 | 1.4211e-13 | -0.0065127 | 0.001453 | 0.064614 | -0.0073159 | 0.061208 | 0.0016025 | -0.0035271 | -0.0021323 | 0.069579 | 0.02181 | 0.061703 | -121.9901 | -0.11764 | -122.4271 | 0.51455 | 0.37583 | 0.63645 | -122.5401 | -122.223 | -0.10495 | -122.2392 | 0.49657 | 0.56772 | 0.14053 | -122.9222 | -0.033417 | -0.025616 | 0.51662 | 0.079661 | 0.11308 | -0.16433 | 0.096294 | -0.41552 | -0.043588 | 0.28368 | 0.26749 | 0.68301 | 0.027556 | -0.39963 | 123.0213 | 122.8825 | 123.1432 | 122.3891 | -123.0803 | 123.0033 | 123.0744 | 122.6472 | 122.4018 | -123.4624
679.2969 | 123.2208 | -122.2412 | 0.87891 | 1.4211e-13 | -0.0060855 | 0.0012394 | 0.064614 | -0.0077431 | 0.061208 | -0.006028 | -0.0033135 | -0.0019187 | 0.069792 | 0.02181 | 0.061276 | -121.7429 | -0.11764 | -122.1752 | 0.77094 | 0.62767 | 0.89286 | -122.2746 | -121.962 | -0.10495 | -121.9874 | 0.75297 | 0.81954 | 0.4244 | -122.6612 | -0.033342 | -0.10797 | 0.49835 | 0.065964 | 0.099306 | -0.25123 | 0.013951 | -0.42003 | -0.12594 | 0.27916 | 0.25382 | 0.67385 | -0.059365 | -0.4545 | 123.0121 | 122.8689 | 123.1341 | 122.1236 | -123.1535 | 122.9942 | 123.0608 | 122.6656 | 122.1363 | -123.5402
681.0625 | 123.2529 | -122.2549 | 0.82855 | 1.4211e-13 | -0.0056581 | 0.0012394 | 0.0644 | -0.0075295 | 0.060994 | -0.006028 | -0.0035271 | -0.0021323 | 0.070006 | 0.021596 | 0.061489 | -121.7246 | -0.12679 | -122.1707 | 0.78009 | 0.65057 | 0.89286 | -122.2608 | -121.9575 | -0.10495 | -121.9828 | 0.74839 | 0.82412 | 0.47477 | -122.6567 | -0.005873 | -0.048461 | 0.53039 | 0.084275 | 0.090148 | -0.17799 | 0.064305 | -0.40172 | -0.080162 | 0.29748 | 0.27213 | 0.67385 | -0.004433 | -0.35378 | 123.035 | 122.9055 | 123.1478 | 122.1281 | -123.0894 | 123.0033 | 123.0791 | 122.7297 | 122.15 | -123.4852
682.8125 | 123.1064 | -122.0764 | 1.03 | 1.4211e-13 | -0.0062991 | 0.0012394 | 0.063973 | -0.0077431 | 0.060994 | 0.0016025 | -0.0035271 | -0.0023459 | 0.070006 | 0.022023 | 0.061703 | -121.4086 | -0.11306 | -121.8548 | 1.0914 | 0.96193 | 1.2088 | -122.0181 | -121.6278 | -0.10495 | -121.6623 | 1.0689 | 1.1446 | 0.84564 | -122.3361 | 0.058282 | 0.061454 | 0.66777 | 0.22165 | 0.16337 | -0.068035 | 0.17881 | -0.25973 | 0.038916 | 0.44861 | 0.41411 | 0.67384 | 0.11465 | -0.18433 | 123.1678 | 123.0383 | 123.2852 | 121.9634 | -123.0481 | 123.1453 | 123.221 | 122.9221 | 121.9715 | -123.3661
684.5 | 123.1293 | -120.8679 | 2.243 | 1.4211e-13 | -0.0060855 | 0.0012394 | 0.064186 | -0.0077431 | 0.060781 | 0.0016025 | -0.0039543 | -0.0023459 | 0.070006 | 0.021596 | 0.061703 | -120.3602 | -0.11764 | -120.7972 | 2.1399 | 1.9968 | 2.2573 | -120.9558 | -120.593 | -0.10495 | -120.6138 | 2.1128 | 2.184 | 1.8392 | -121.2876 | -0.087903 | -0.10317 | 0.50773 | 0.070735 | 0.15864 | -0.24627 | 0.014238 | -0.41968 | -0.13026 | 0.27491 | 0.25414 | 0.67382 | -0.059078 | -0.40385 | 123.0078 | 122.8647 | 123.1252 | 120.7503 | -123.1989 | 122.9807 | 123.0519 | 122.7071 | 120.763 | -123.5306
686.2344 | 123.2162 | -122.2321 | 0.86975 | 1.4211e-13 | -0.0060855 | 0.0012394 | 0.063759 | -0.0075295 | 0.060781 | -0.006028 | -0.0035271 | -0.0023459 | 0.069792 | 0.022023 | 0.061062 | -121.7062 | -0.11306 | -122.1386 | 0.80298 | 0.67346 | 0.91575 | -122.2562 | -121.9254 | -0.10495 | -121.9508 | 0.78044 | 0.86075 | 0.46561 | -122.6384 | -0.024182 | -0.066768 | 0.52582 | 0.093435 | 0.11762 | -0.19629 | 0.045999 | -0.4063 | -0.089312 | 0.30664 | 0.28129 | 0.68759 | -0.009003 | -0.40414 | 123.035 | 122.9055 | 123.1478 | 122.119 | -123.126 | 123.0125 | 123.0928 | 122.6977 | 122.1271 | -123.5081
687.9844 | 123.2254 | -122.2641 | 0.81024 | 1.4211e-13 | -0.0065127 | 0.0012394 | 0.0644 | -0.0071023 | 0.060567 | -0.006028 | -0.0035271 | -0.0023459 | 0.069579 | 0.022237 | 0.061489 | -121.7932 | -0.11764 | -122.2348 | 0.71142 | 0.58188 | 0.82876 | -122.3432 | -122.0261 | -0.10037 | -122.0423 | 0.68429 | 0.75544 | 0.4473 | -122.7299 | -0.079138 | -0.098826 | 0.47087 | 0.029334 | 0.10847 | -0.22836 | 0.018514 | -0.46583 | -0.12595 | 0.23795 | 0.22176 | 0.68759 | -0.054802 | -0.36295 | 122.9755 | 122.846 | 123.0929 | 122.1465 | -123.1535 | 122.9484 | 123.0195 | 122.7114 | 122.1637 | -123.5402
689.6562 | 123.2346 | -122.3511 | 0.74616 | 1.4211e-13 | -0.0065127 | 0.0012394 | 0.0644 | -0.0075295 | 0.060994 | 0.0016025 | -0.0033135 | -0.0023459 | 0.069579 | 0.02181 | 0.061703 | -121.8024 | -0.12222 | -122.2439 | 0.70226 | 0.55899 | 0.81502 | -122.3478 | -122.0307 | -0.10953 | -122.0607 | 0.67513 | 0.75086 | 0.37862 | -122.7391 | 0.003258 | -0.043896 | 0.54869 | 0.10715 | 0.10389 | -0.18717 | 0.068866 | -0.38801 | -0.071021 | 0.32035 | 0.29042 | 0.67843 | 0.004707 | -0.36754 | 123.0533 | 122.9101 | 123.1661 | 122.2289 | -123.094 | 123.0262 | 123.1019 | 122.7297 | 122.2415 | -123.4852
691.4062 | 123.1247 | -121.8018 | 1.3367 | 1.4211e-13 | -0.0065127 | 0.0012394 | 0.064186 | -0.0077431 | 0.060994 | -0.013659 | -0.0039543 | -0.0021323 | 0.069792 | 0.022237 | 0.061703 | -121.2392 | -0.12222 | -121.6671 | 1.27 | 1.1268 | 1.3873 | -121.7846 | -121.4584 | -0.10953 | -121.4883 | 1.2429 | 1.3232 | 0.94636 | -122.1622 | 0.01715 | -0.066691 | 0.56252 | 0.1347 | 0.11755 | -0.2099 | 0.050676 | -0.3604 | -0.093803 | 0.34337 | 0.31344 | 0.67384 | -0.013483 | -0.39031 | 123.0717 | 122.9285 | 123.1891 | 121.6795 | -123.1213 | 123.0446 | 123.1249 | 122.7481 | 121.6922 | -123.4988
693.1094 | 123.2391 | -120.4468 | 2.5864 | 1.4211e-13 | -0.0062991 | 0.0012394 | 0.064186 | -0.0073159 | 0.060567 | 0.0092325 | -0.0035271 | -0.0021323 | 0.070006 | 0.022237 | 0.061489 | -120.6074 | -0.067272 | -121.049 | 1.8697 | 1.7587 | 2.0009 | -121.1573 | -120.8219 | -0.054586 | -120.8336 | 1.8793 | 1.9413 | 1.5462 | -121.5257 | -0.71052 | -0.71662 | -0.16065 | -0.60221 | 0.10831 | -0.8277 | -0.58549 | -1.0789 | -0.70709 | -0.37517 | -0.38678 | 0.69214 | -0.64507 | -1.0402 | 122.3165 | 122.2054 | 122.4477 | 120.3795 | -123.7437 | 122.3261 | 122.3881 | 121.9929 | 120.3922 | -124.1121
694.8438 | 123.1796 | -121.7056 | 1.3962 | 1.4211e-13 | -0.0065127 | 0.001453 | 0.064186 | -0.0077431 | 0.060567 | -0.006028 | -0.0037407 | -0.0023459 | 0.070006 | 0.022237 | 0.061489 | -121.1935 | -0.11306 | -121.6304 | 1.3112 | 1.168 | 1.424 | -121.7297 | -121.408 | -0.10953 | -121.4425 | 1.2795 | 1.3598 | 0.90973 | -122.1164 | -0.024034 | -0.084995 | 0.51217 | 0.075195 | 0.099229 | -0.22819 | 0.027796 | -0.41074 | -0.11668 | 0.2976 | 0.2631 | 0.67384 | -0.036363 | -0.48644 | 123.0168 | 122.8736 | 123.1296 | 121.5926 | -123.1258 | 122.9851 | 123.0654 | 122.6154 | 121.5961 | -123.5125
696.5938 | 123.1155 | -120.9366 | 2.1835 | 1.4211e-13 | -0.0062991 | 0.001453 | 0.0644 | -0.0077431 | 0.060994 | 0.016863 | -0.0035271 | -0.0023459 | 0.069792 | 0.02181 | 0.061489 | -120.4563 | -0.11764 | -120.8933 | 2.0437 | 1.9143 | 2.1657 | -120.9925 | -120.6663 | -0.095794 | -120.7008 | 2.0212 | 2.097 | 1.8163 | -121.3792 | -0.05587 | -0.13981 | 0.48025 | 0.043255 | 0.099125 | -0.26918 | -0.017825 | -0.44259 | -0.16232 | 0.27031 | 0.23581 | 0.6784 | -0.086562 | -0.36723 | 122.9803 | 122.8509 | 123.1023 | 120.8189 | -123.176 | 122.9578 | 123.0336 | 122.7529 | 120.8408 | -123.5627
698.3594 | 123.1384 | -121.994 | 1.1398 | 1.4211e-13 | -0.0060855 | 0.0012394 | 0.0644 | -0.0073159 | 0.060994 | -0.013659 | -0.0039543 | -0.0019187 | 0.070006 | 0.022451 | 0.061489 | -121.427 | -0.12222 | -121.8685 | 1.0685 | 0.94362 | 1.195 | -121.9678 | -121.6507 | -0.10495 | -121.6715 | 1.0506 | 1.1309 | 0.79985 | -122.3545 | 0.026254 | -0.071302 | 0.56706 | 0.12552 | 0.099262 | -0.19621 | 0.055213 | -0.36044 | -0.089261 | 0.34332 | 0.32255 | 0.683 | -0.008946 | -0.33998 | 123.0625 | 122.9376 | 123.1891 | 121.8718 | -123.1076 | 123.0446 | 123.1249 | 122.7939 | 121.8891 | -123.4943
700.0625 | 123.2071 | -122.1313 | 0.90637 | 1.4211e-13 | -0.0065127 | 0.0010256 | 0.0644 | -0.0073159 | 0.060781 | 0.0016025 | -0.0033135 | -0.0021323 | 0.070006 | 0.022023 | 0.061489 | -121.6101 | -0.11764 | -122.0471 | 0.90371 | 0.76504 | 1.0211 | -122.1555 | -121.8384 | -0.10037 | -121.85 | 0.85827 | 0.95232 | 0.59839 | -122.5239 | -0.024153 | -0.002664 | 0.52126 | 0.084293 | 0.10845 | -0.14133 | 0.11469 | -0.39253 | -0.048098 | 0.29293 | 0.28132 | 0.67385 | 0.045948 | -0.30798 | 123.0351 | 122.8964 | 123.1524 | 122.0137 | -123.0619 | 122.9896 | 123.0837 | 122.7297 | 122.031 | -123.4303
701.7969 | 123.1796 | -122.1817 | 0.90637 | 1.4211e-13 | -0.0065127 | 0.001453 | 0.064186 | -0.0077431 | 0.060994 | -0.006028 | -0.0033135 | -0.0021323 | 0.070006 | 0.022023 | 0.061489 | -121.6147 | -0.11764 | -122.0562 | 0.88082 | 0.74215 | 1.0073 | -122.1189 | -121.843 | -0.10495 | -121.8638 | 0.86285 | 0.94316 | 0.56176 | -122.5422 | 0.062832 | -0.025556 | 0.56703 | 0.12549 | 0.062658 | -0.16423 | 0.10095 | -0.36049 | -0.04352 | 0.3387 | 0.31793 | 0.67843 | 0.036791 | -0.34461 | 123.0625 | 122.9238 | 123.189 | 122.0641 | -123.0252 | 123.0446 | 123.1249 | 122.7435 | 122.0768 | -123.4486
703.5469 | 123.1293 | -122.3465 | 0.80566 | 1.4211e-13 | -0.0065127 | 0.0016666 | 0.0644 | -0.0075295 | 0.060994 | -0.013659 | -0.0035271 | -0.0023459 | 0.069792 | 0.022237 | 0.061276 | -121.7749 | -0.11764 | -122.2119 | 0.72973 | 0.58188 | 0.84707 | -122.3112 | -121.9941 | -0.10953 | -122.024 | 0.70261 | 0.79207 | 0.41067 | -122.7116 | 0.035312 | -0.075935 | 0.57158 | 0.13462 | 0.099311 | -0.22378 | 0.041407 | -0.36512 | -0.10306 | 0.3524 | 0.32247 | 0.68759 | -0.013595 | -0.395 | 123.0762 | 122.9284 | 123.1936 | 122.2289 | -123.1168 | 123.0491 | 123.1386 | 122.7572 | 122.237 | -123.5173
705.2969 | 123.2712 | -122.0764 | 0.97504 | 1.4211e-13 | -0.0062991 | 0.0012394 | 0.0644 | -0.0075295 | 0.060994 | 0.0016025 | -0.0033135 | -0.0019187 | 0.069579 | 0.022451 | 0.061489 | -121.546 | -0.11764 | -121.9921 | 0.95407 | 0.81541 | 1.0714 | -122.096 | -121.7789 | -0.10037 | -121.7997 | 0.92695 | 1.0073 | 0.61213 | -122.4781 | -0.019559 | -0.020967 | 0.53042 | 0.0843 | 0.10386 | -0.15963 | 0.096385 | -0.40168 | -0.048086 | 0.29752 | 0.27675 | 0.67843 | 0.032226 | -0.36291 | 123.0305 | 122.8918 | 123.1478 | 121.9588 | -123.071 | 123.0034 | 123.0837 | 122.6885 | 121.976 | -123.4531
707.0469 | 123.2666 | -121.9025 | 1.149 | 1.4211e-13 | -0.0065127 | 0.0012394 | 0.064186 | -0.0077431 | 0.060781 | -0.006028 | -0.0037407 | -0.0025597 | 0.070006 | 0.022023 | 0.061062 | -121.3217 | -0.11306 | -121.7724 | 1.1784 | 1.0306 | 1.2912 | -121.8624 | -121.5454 | -0.10953 | -121.5799 | 1.1467 | 1.227 | 0.84106 | -122.2675 | 0.040016 | 0.029424 | 0.58081 | 0.13011 | 0.090091 | -0.11837 | 0.14221 | -0.365 | -0.002268 | 0.35708 | 0.32258 | 0.68758 | 0.078049 | -0.30793 | 123.0809 | 122.9331 | 123.1937 | 121.7894 | -123.0114 | 123.0492 | 123.1295 | 122.7435 | 121.7929 | -123.4165
708.7812 | 123.1659 | -121.7789 | 1.3092 | 1.4211e-13 | -0.0067265 | 0.0012394 | 0.064614 | -0.0075295 | 0.060781 | -0.006028 | -0.0033135 | -0.0021323 | 0.069792 | 0.022237 | 0.061703 | -121.2484 | -0.10848 | -121.6945 | 1.2425 | 1.1039 | 1.3553 | -121.8029 | -121.4813 | -0.10953 | -121.5066 | 1.2108 | 1.2957 | 0.93263 | -122.1805 | -0.024054 | -0.066695 | 0.53047 | 0.084342 | 0.1084 | -0.20532 | 0.046092 | -0.4016 | -0.098386 | 0.29759 | 0.27224 | 0.67384 | -0.013489 | -0.37658 | 123.0214 | 122.8828 | 123.1342 | 121.6704 | -123.1121 | 122.9897 | 123.0746 | 122.7115 | 121.6693 | -123.4897
710.4688 | 123.1567 | -121.2479 | 1.8723 | 1.4211e-13 | -0.0065127 | 0.0010256 | 0.0644 | -0.0079569 | 0.060994 | -0.006028 | -0.0030999 | -0.0023459 | 0.069792 | 0.022023 | 0.061276 | -120.7173 | -0.11306 | -121.1589 | 1.769 | 1.6305 | 1.8864 | -121.2718 | -120.9502 | -0.10495 | -120.9709 | 1.7465 | 1.8223 | 1.4637 | -121.6493 | -0.023905 | -0.10323 | 0.53056 | 0.088995 | 0.1129 | -0.2418 | 0.014161 | -0.40146 | -0.12575 | 0.29771 | 0.27694 | 0.67841 | -0.049999 | -0.40851 | 123.0169 | 122.8783 | 123.1343 | 121.1348 | -123.144 | 122.9944 | 123.0701 | 122.7116 | 121.1429 | -123.5216
712.2188 | 123.1842 | -121.6736 | 1.4008 | 1.4211e-13 | -0.0065127 | 0.0010256 | 0.064614 | -0.0077431 | 0.061208 | -0.006028 | -0.0035271 | -0.0023459 | 0.069792 | 0.022023 | 0.061276 | -120.9691 | -0.11306 | -121.4015 | 1.5309 | 1.3878 | 1.6483 | -121.5099 | -121.1882 | -0.10953 | -121.2136 | 1.5038 | 1.575 | 1.2394 | -121.892 | 0.16371 | 0.13019 | 0.70447 | 0.27207 | 0.10836 | -0.012984 | 0.24757 | -0.21842 | 0.10308 | 0.48534 | 0.45999 | 0.67841 | 0.17425 | -0.16136 | 123.2045 | 123.0614 | 123.3219 | 121.5605 | -122.9106 | 123.1774 | 123.2486 | 122.913 | 121.5641 | -123.2928
713.9688 | 123.1476 | -121.582 | 1.5244 | 1.4211e-13 | -0.0060855 | 0.0012394 | 0.064827 | -0.0073159 | 0.060994 | -0.006028 | -0.0033135 | -0.0019187 | 0.069792 | 0.022023 | 0.061276 | -121.0012 | -0.11764 | -121.4381 | 1.4943 | 1.3511 | 1.6071 | -121.5145 | -121.2295 | -0.10953 | -121.2548 | 1.4581 | 1.543 | 1.2165 | -121.9241 | 0.067579 | -0.030033 | 0.58087 | 0.14389 | 0.076308 | -0.17321 | 0.082766 | -0.34202 | -0.066296 | 0.35258 | 0.32723 | 0.66925 | 0.018607 | -0.30785 | 123.0764 | 122.9332 | 123.1891 | 121.4644 | -123.0388 | 123.0401 | 123.125 | 122.7985 | 121.4725 | -123.4484
715.6406 | 123.2208 | -121.8109 | 1.2177 | 1.4211e-13 | -0.0067265 | 0.001453 | 0.0644 | -0.0075295 | 0.060994 | -0.006028 | -0.0033135 | -0.0023459 | 0.069792 | 0.022023 | 0.061703 | -121.4041 | -0.11764 | -121.8502 | 1.0914 | 0.95278 | 1.2042 | -121.9494 | -121.6232 | -0.10495 | -121.6486 | 1.0597 | 1.1446 | 0.80443 | -122.3361 | -0.13854 | -0.12623 | 0.40685 | -0.039276 | 0.099261 | -0.26488 | -0.013449 | -0.52524 | -0.15792 | 0.18769 | 0.16234 | 0.68758 | -0.07303 | -0.41322 | 122.9023 | 122.7637 | 123.0151 | 121.6933 | -123.1671 | 122.8706 | 122.9555 | 122.6153 | 121.706 | -123.5538
717.3906 | 123.1338 | -121.7697 | 1.3321 | 1.4211e-13 | -0.0062991 | 0.0012394 | 0.0644 | -0.0079569 | 0.060781 | 0.0016025 | -0.0037407 | -0.0025597 | 0.069792 | 0.022237 | 0.061489 | -121.1935 | -0.10848 | -121.6442 | 1.2974 | 1.1588 | 1.4102 | -121.7342 | -121.4218 | -0.095794 | -121.4517 | 1.2703 | 1.3461 | 0.99673 | -122.1255 | 0.035474 | -0.034643 | 0.57626 | 0.12555 | 0.090073 | -0.17327 | 0.078147 | -0.35581 | -0.061754 | 0.34795 | 0.31803 | 0.67384 | 0.013988 | -0.33536 | 123.0672 | 122.9285 | 123.18 | 121.6612 | -123.0663 | 123.0401 | 123.1158 | 122.7664 | 121.6739 | -123.4576
719.0781 | 123.1979 | -121.9116 | 1.1215 | 1.4211e-13 | -0.0067265 | 0.0010256 | 0.0644 | -0.0077431 | 0.061208 | 0.0016025 | -0.0035271 | -0.0021323 | 0.069579 | 0.022451 | 0.061703 | -121.4086 | -0.10848 | -121.8502 | 1.0731 | 0.92988 | 1.1905 | -121.9494 | -121.637 | -0.10495 | -121.6669 | 1.0506 | 1.1309 | 0.66249 | -122.359 | -0.037829 | -0.048413 | 0.50298 | 0.061432 | 0.099261 | -0.19164 | 0.068945 | -0.44742 | -0.07095 | 0.27466 | 0.24474 | 0.69216 | 0.009365 | -0.45903 | 122.9847 | 122.8415 | 123.1021 | 121.8031 | -123.071 | 122.9622 | 123.0425 | 122.5741 | 121.8067 | -123.4806
720.8125 | 123.1842 | -121.9986 | 1.0483 | 1.4211e-13 | -0.0065127 | 0.0010256 | 0.064186 | -0.0077431 | 0.061208 | -0.013659 | -0.0039543 | -0.0023459 | 0.069792 | 0.022664 | 0.061489 | -121.4956 | -0.11764 | -121.9372 | 0.99528 | 0.84746 | 1.1172 | -122.041 | -121.7285 | -0.10953 | -121.7539 | 0.96816 | 1.0485 | 0.65791 | -122.4369 | -0.042432 | -0.053003 | 0.50297 | 0.061419 | 0.10385 | -0.20082 | 0.068929 | -0.43829 | -0.080121 | 0.27006 | 0.24472 | 0.683 | 0.000192 | -0.39037 | 122.9939 | 122.8461 | 123.1158 | 121.881 | -123.0893 | 122.9668 | 123.0471 | 122.6565 | 121.8891 | -123.4852
722.5 | 123.1201 | -121.9482 | 1.149 | 1.4211e-13 | -0.0065127 | 0.001453 | 0.064186 | -0.0077431 | 0.060994 | 0.0092325 | -0.0037407 | -0.0025597 | 0.07022 | 0.022664 | 0.061703 | -121.4178 | -0.11306 | -121.8639 | 1.0594 | 0.9253 | 1.1813 | -121.9632 | -121.6553 | -0.11411 | -121.6806 | 1.0368 | 1.1172 | 0.77238 | -122.3545 | -0.014944 | -0.089614 | 0.53044 | 0.084318 | 0.099262 | -0.22369 | 0.032322 | -0.40622 | -0.11215 | 0.29297 | 0.26762 | 0.67384 | -0.031837 | -0.37661 | 123.0076 | 122.8735 | 123.1296 | 121.8352 | -123.1122 | 122.9851 | 123.0654 | 122.7206 | 121.8341 | -123.5035
724.2656 | 123.1201 | -121.9025 | 1.2131 | 1.4211e-13 | -0.0067265 | 0.001453 | 0.064186 | -0.0075295 | 0.060994 | 0.0016025 | -0.0035271 | -0.0023459 | 0.069579 | 0.022237 | 0.061489 | -121.3262 | -0.11306 | -121.754 | 1.1738 | 1.0215 | 1.2775 | -121.8396 | -121.5408 | -0.10953 | -121.5753 | 1.1376 | 1.2316 | 0.93721 | -122.2629 | 0.062911 | -0.039241 | 0.57623 | 0.14842 | 0.08551 | -0.19162 | 0.064385 | -0.36042 | -0.075512 | 0.36166 | 0.32716 | 0.68758 | 0.018541 | -0.27587 | 123.0763 | 122.9239 | 123.1799 | 121.7894 | -123.0526 | 123.04 | 123.1341 | 122.8397 | 121.7929 | -123.476
725.9531 | 123.2346 | -122.3053 | 0.74616 | 1.4211e-13 | -0.0065127 | 0.0010256 | 0.0644 | -0.0077431 | 0.061208 | -0.006028 | -0.0035271 | -0.0023459 | 0.069792 | 0.022237 | 0.061703 | -121.7749 | -0.11306 | -122.221 | 0.70684 | 0.5773 | 0.83334 | -122.3341 | -121.9987 | -0.10953 | -122.0286 | 0.68429 | 0.7646 | 0.4244 | -122.7208 | -0.028781 | -0.039318 | 0.53038 | 0.084268 | 0.11305 | -0.16885 | 0.08718 | -0.41547 | -0.061864 | 0.30662 | 0.27669 | 0.69217 | 0.018442 | -0.32175 | 123.0121 | 122.8826 | 123.1386 | 122.1922 | -123.0802 | 122.9896 | 123.0699 | 122.7297 | 122.1958 | -123.4669
727.6875 | 123.2162 | -122.3373 | 0.70496 | 1.4211e-13 | -0.0062991 | 0.0010256 | 0.063973 | -0.0073159 | 0.060994 | -0.006028 | -0.0037407 | -0.0021323 | 0.069792 | 0.022023 | 0.061276 | -121.7978 | -0.12222 | -122.2393 | 0.68852 | 0.54525 | 0.80586 | -122.3478 | -122.0261 | -0.11411 | -122.0515 | 0.65682 | 0.7417 | 0.43814 | -122.7482 | -0.010475 | -0.016432 | 0.53954 | 0.097998 | 0.10847 | -0.1597 | 0.10091 | -0.4109 | -0.048136 | 0.31119 | 0.28584 | 0.69675 | 0.036748 | -0.26682 | 123.0259 | 122.8826 | 123.1432 | 122.2151 | -123.0528 | 122.9942 | 123.079 | 122.7755 | 122.2232 | -123.4532
729.4531 | 123.1796 | -122.2916 | 0.75989 | 1.4211e-13 | -0.0065127 | 0.0010256 | 0.0644 | -0.0077431 | 0.061208 | -0.013659 | -0.0035271 | -0.0023459 | 0.069792 | 0.022237 | 0.061276 | -121.6376 | -0.1039 | -122.0837 | 0.83961 | 0.70093 | 0.96154 | -122.1921 | -121.8751 | -0.10495 | -121.8912 | 0.82165 | 0.8928 | 0.59839 | -122.588 | 0.099432 | 0.079722 | 0.654 | 0.20788 | 0.10845 | -0.058954 | 0.20165 | -0.29642 | 0.061758 | 0.41651 | 0.40032 | 0.69674 | 0.13291 | -0.1615 | 123.1312 | 122.9925 | 123.2531 | 122.1877 | -122.952 | 123.1132 | 123.1844 | 122.89 | 122.1866 | -123.3479
731.1875 | 123.2254 | -122.113 | 0.89264 | 1.4211e-13 | -0.0069401 | 0.0012394 | 0.0644 | -0.0077431 | 0.060781 | 0.0016025 | -0.0039543 | -0.0021323 | 0.069579 | 0.022237 | 0.061489 | -121.6009 | -0.11306 | -122.0425 | 0.87166 | 0.74215 | 0.99816 | -122.1509 | -121.8384 | -0.10953 | -121.8546 | 0.84454 | 0.92943 | 0.71286 | -122.5514 | -0.037885 | -0.02098 | 0.5121 | 0.07056 | 0.10844 | -0.15049 | 0.10553 | -0.43832 | -0.048101 | 0.27462 | 0.25843 | 0.69674 | 0.036788 | -0.17978 | 122.9847 | 122.8552 | 123.1112 | 122 | -123.0436 | 122.9576 | 123.0425 | 122.8259 | 122.0035 | -123.444
732.875 | 123.23 | -122.0993 | 0.90637 | 1.4211e-13 | -0.0065127 | 0.0012394 | 0.0644 | -0.0079569 | 0.060994 | -0.006028 | -0.0033135 | -0.0021323 | 0.069579 | 0.022237 | 0.061917 | -121.5643 | -0.1039 | -122.015 | 0.91744 | 0.7742 | 1.0302 | -122.1234 | -121.7926 | -0.10037 | -121.8226 | 0.87659 | 0.96148 | 0.59381 | -122.5147 | -0.024145 | 0.011071 | 0.535 | 0.084297 | 0.10844 | -0.13217 | 0.12384 | -0.41542 | -0.029784 | 0.30667 | 0.27674 | 0.69216 | 0.055105 | -0.31256 | 123.0167 | 122.8735 | 123.1295 | 121.9954 | -123.0298 | 122.9759 | 123.0608 | 122.6931 | 121.9989 | -123.4211
734.625 | 123.0927 | -122.2549 | 0.84686 | 1.4211e-13 | -0.0065127 | 0.0012394 | 0.064186 | -0.0077431 | 0.060994 | 0.0016025 | -0.0030999 | -0.0021323 | 0.069792 | 0.022451 | 0.061276 | -121.6925 | -0.10848 | -122.1386 | 0.78009 | 0.65057 | 0.89743 | -122.2104 | -121.9254 | -0.10953 | -121.9508 | 0.75755 | 0.8287 | 0.40151 | -122.6429 | 0.044496 | -0.066772 | 0.56244 | 0.11632 | 0.071827 | -0.1963 | 0.050572 | -0.38799 | -0.089316 | 0.32953 | 0.30418 | 0.69217 | -0.018165 | -0.44535 | 123.035 | 122.9055 | 123.1524 | 122.1465 | -123.0573 | 123.0125 | 123.0836 | 122.6565 | 122.1454 | -123.4898
736.375 | 123.1018 | -122.2321 | 0.87433 | 1.4211e-13 | -0.0065127 | 0.0012394 | 0.0644 | -0.0075295 | 0.060994 | 0.016863 | -0.0035271 | -0.0025597 | 0.069792 | 0.022023 | 0.061489 | -121.665 | -0.10848 | -122.1066 | 0.8213 | 0.66888 | 0.92949 | -122.2059 | -121.8888 | -0.10495 | -121.9187 | 0.78502 | 0.86075 | 0.54345 | -122.6155 | 0.026187 | -0.053032 | 0.56703 | 0.12548 | 0.099296 | -0.20545 | 0.055157 | -0.3834 | -0.089311 | 0.34327 | 0.31334 | 0.69674 | -0.013581 | -0.33088 | 123.0534 | 122.9009 | 123.1615 | 122.1236 | -123.0802 | 123.0171 | 123.0928 | 122.7755 | 122.1271 | -123.4898
738.0625 | 123.0972 | -122.2229 | 0.86975 | 1.4211e-13 | -0.0062991 | 0.0010256 | 0.064614 | -0.0075295 | 0.060781 | 0.0016025 | -0.0035271 | -0.0023459 | 0.070006 | 0.022451 | 0.061703 | -121.6559 | -0.10848 | -122.0974 | 0.81214 | 0.67804 | 0.92949 | -122.1967 | -121.8934 | -0.10953 | -121.905 | 0.79417 | 0.86991 | 0.52055 | -122.6063 | 0.026188 | -0.057611 | 0.56703 | 0.12548 | 0.099295 | -0.19171 | 0.059735 | -0.3834 | -0.075576 | 0.32953 | 0.31792 | 0.70132 | 0.000154 | -0.3492 | 123.035 | 122.9009 | 123.1524 | 122.1144 | -123.0665 | 123.0171 | 123.0928 | 122.7435 | 122.1134 | -123.4761
739.8125 | 123.1155 | -122.2733 | 0.83313 | 1.4211e-13 | -0.0067265 | 0.0012394 | 0.063759 | -0.0073159 | 0.060994 | 0.0016025 | -0.0037407 | -0.0023459 | 0.069579 | 0.022451 | 0.061917 | -121.7108 | -0.1039 | -122.1478 | 0.76178 | 0.62309 | 0.88828 | -122.2517 | -121.9346 | -0.10953 | -121.9599 | 0.74381 | 0.81496 | 0.47477 | -122.6521 | 0.021595 | -0.071352 | 0.56244 | 0.12548 | 0.10388 | -0.21004 | 0.055148 | -0.37883 | -0.089319 | 0.33868 | 0.31333 | 0.69217 | -0.018168 | -0.35836 | 123.035 | 122.8963 | 123.1615 | 122.1694 | -123.0848 | 123.0171 | 123.0882 | 122.748 | 122.1637 | -123.4852
741.5156 | 123.1018 | -122.3282 | 0.79193 | 1.4211e-13 | -0.0067265 | 0.0012394 | 0.0644 | -0.0075295 | 0.061208 | 0.0016025 | -0.0037407 | -0.0023459 | 0.069792 | 0.022237 | 0.061703 | -121.752 | -0.10848 | -122.189 | 0.72057 | 0.58188 | 0.85165 | -122.3066 | -121.9758 | -0.10953 | -122.0103 | 0.69803 | 0.77375 | 0.4885 | -122.707 | 0.02158 | -0.071359 | 0.57617 | 0.1392 | 0.11762 | -0.21005 | 0.059718 | -0.37885 | -0.093905 | 0.3524 | 0.3179 | 0.69674 | -0.018176 | -0.30343 | 123.0488 | 122.9101 | 123.1798 | 122.2197 | -123.0985 | 123.0262 | 123.1019 | 122.8167 | 122.2187 | -123.499
743.2812 | 123.1796 | -122.3465 | 0.6958 | 1.4211e-13 | -0.0065127 | 0.0010256 | 0.064186 | -0.0079569 | 0.061208 | -0.006028 | -0.0033135 | -0.0023459 | 0.07022 | 0.022237 | 0.061917 | -121.7978 | -0.1039 | -122.2348 | 0.67937 | 0.53609 | 0.79671 | -122.3661 | -122.0216 | -0.11411 | -122.0515 | 0.64308 | 0.71881 | 0.40151 | -122.7437 | -0.019635 | -0.016434 | 0.54869 | 0.11173 | 0.13137 | -0.15971 | 0.10091 | -0.39717 | -0.052717 | 0.32493 | 0.295 | 0.69217 | 0.02301 | -0.29429 | 123.0259 | 122.8826 | 123.1432 | 122.2426 | -123.0619 | 122.9896 | 123.0653 | 122.748 | 122.2324 | -123.4395
745.0781 | 123.1842 | -122.3145 | 0.71869 | 1.4211e-13 | -0.0065127 | 0.0012394 | 0.063973 | -0.0077431 | 0.060781 | 0.0016025 | -0.0035271 | -0.0025597 | 0.069579 | 0.022451 | 0.061917 | -121.7749 | -0.10848 | -122.2165 | 0.69768 | 0.55441 | 0.82418 | -122.3387 | -122.0078 | -0.11411 | -122.0378 | 0.6614 | 0.75086 | 0.48392 | -122.7253 | -0.024205 | -0.021009 | 0.53954 | 0.098001 | 0.12221 | -0.16428 | 0.10549 | -0.4109 | -0.057291 | 0.30662 | 0.27669 | 0.68759 | 0.032173 | -0.23476 | 123.0121 | 122.8689 | 123.1386 | 122.206 | -123.0573 | 122.9759 | 123.0653 | 122.7984 | 122.2003 | -123.444
746.8281 | 123.1247 | -122.3145 | 0.76446 | 1.4211e-13 | -0.0062991 | 0.0012394 | 0.064186 | -0.0075295 | 0.060994 | 0.0092325 | -0.0037407 | -0.0023459 | 0.069792 | 0.022237 | 0.061489 | -121.7612 | -0.1039 | -122.2027 | 0.71599 | 0.58188 | 0.83334 | -122.302 | -121.9849 | -0.10953 | -122.0149 | 0.68887 | 0.76918 | 0.53887 | -122.707 | 0.012426 | -0.048471 | 0.55327 | 0.11174 | 0.09931 | -0.18258 | 0.06887 | -0.39258 | -0.075596 | 0.32951 | 0.29959 | 0.69217 | 0.004711 | -0.2256 | 123.0304 | 122.8963 | 123.1478 | 122.2106 | -123.0665 | 123.0033 | 123.0836 | 122.8533 | 122.2049 | -123.4715
748.5938 | 123.1384 | -122.2687 | 0.80109 | 1.4211e-13 | -0.0067265 | 0.00081202 | 0.0644 | -0.0077431 | 0.060781 | 0.0016025 | -0.0035271 | -0.0025597 | 0.069792 | 0.022451 | 0.061703 | -121.6925 | -0.10848 | -122.134 | 0.77551 | 0.63683 | 0.89286 | -122.2379 | -121.9117 | -0.11411 | -121.9462 | 0.74839 | 0.83328 | 0.51598 | -122.6429 | 0.030755 | -0.025573 | 0.57617 | 0.13463 | 0.10388 | -0.16426 | 0.091771 | -0.37425 | -0.052696 | 0.357 | 0.32249 | 0.69674 | 0.03219 | -0.28511 | 123.0442 | 122.9055 | 123.1615 | 122.1602 | -123.039 | 123.0171 | 123.102 | 122.7847 | 122.1546 | -123.444
750.2812 | 123.0835 | -122.3419 | 0.75073 | 1.4211e-13 | -0.0065127 | 0.001453 | 0.063973 | -0.0079569 | 0.061208 | -0.006028 | -0.0035271 | -0.0023459 | 0.069365 | 0.022451 | 0.061489 | -121.7566 | -0.1039 | -122.1981 | 0.71599 | 0.57273 | 0.83791 | -122.3066 | -121.9758 | -0.10495 | -122.0103 | 0.68887 | 0.7646 | 0.43356 | -122.707 | 0.035313 | -0.034738 | 0.58532 | 0.14378 | 0.10847 | -0.17801 | 0.087182 | -0.36511 | -0.061863 | 0.36614 | 0.33163 | 0.69674 | 0.013865 | -0.31717 | 123.0579 | 122.9146 | 123.1798 | 122.238 | -123.0573 | 123.0308 | 123.1065 | 122.7755 | 122.237 | -123.4578
752.0312 | 123.0698 | -122.2549 | 0.85602 | 1.4211e-13 | -0.0067265 | 0.0010256 | 0.064186 | -0.0077431 | 0.061208 | 0.0016025 | -0.0035271 | -0.0021323 | 0.069365 | 0.022237 | 0.061703 | -121.6788 | -0.11306 | -122.1203 | 0.77551 | 0.64141 | 0.90201 | -122.2196 | -121.9071 | -0.10953 | -121.9325 | 0.75755 | 0.83328 | 0.4473 | -122.6292 | 0.035338 | -0.080505 | 0.57618 | 0.13464 | 0.099298 | -0.21461 | 0.045996 | -0.37425 | -0.098471 | 0.34784 | 0.32249 | 0.69674 | -0.022742 | -0.40872 | 123.0305 | 122.8964 | 123.157 | 122.1419 | -123.0756 | 123.0125 | 123.0882 | 122.7022 | 122.1454 | -123.4852
753.7812 | 123.1064 | -121.9574 | 1.1078 | 1.4211e-13 | -0.0069401 | 0.0012394 | 0.0644 | -0.0075295 | 0.060994 | 0.0016025 | -0.0033135 | -0.0025597 | 0.069792 | 0.022878 | 0.061703 | -121.4407 | -0.11764 | -121.8822 | 1.009 | 0.87951 | 1.1401 | -121.9907 | -121.6873 | -0.10495 | -121.7035 | 0.98647 | 1.0668 | 0.67623 | -122.3957 | -0.033263 | -0.098777 | 0.51671 | 0.07516 | 0.10842 | -0.22828 | 0.032313 | -0.43828 | -0.12132 | 0.27007 | 0.25388 | 0.69216 | -0.041003 | -0.43156 | 122.9664 | 122.8369 | 123.0975 | 121.8398 | -123.0984 | 122.9439 | 123.0242 | 122.6336 | 121.8524 | -123.5035
755.4688 | 123.1201 | -122.1863 | 0.88806 | 1.4211e-13 | -0.0071537 | 0.0012394 | 0.064186 | -0.0077431 | 0.060994 | 0.0016025 | -0.0033135 | -0.0023459 | 0.069792 | 0.022664 | 0.061703 | -121.6421 | -0.1039 | -122.0791 | 0.82588 | 0.68262 | 0.94322 | -122.1876 | -121.8705 | -0.10495 | -121.8958 | 0.79875 | 0.86991 | 0.47935 | -122.5926 | -0.001275 | -0.062187 | 0.54414 | 0.10718 | 0.10845 | -0.20544 | 0.055159 | -0.40628 | -0.089309 | 0.31581 | 0.29046 | 0.69674 | -0.018157 | -0.40871 | 123.0122 | 122.8689 | 123.1295 | 122.0824 | -123.0756 | 122.985 | 123.0562 | 122.6656 | 122.0813 | -123.4806
757.1719 | 123.1201 | -122.1725 | 0.94299 | 1.4211e-13 | -0.0069401 | 0.0012394 | 0.064186 | -0.0075295 | 0.060994 | 0.0016025 | -0.0035271 | -0.0023459 | 0.069579 | 0.022664 | 0.061276 | -121.6009 | -0.11306 | -122.0379 | 0.84877 | 0.71467 | 0.97985 | -122.1555 | -121.8338 | -0.10953 | -121.8546 | 0.83538 | 0.90653 | 0.63502 | -122.5605 | 0.017045 | -0.094226 | 0.57161 | 0.13465 | 0.1176 | -0.22832 | 0.036857 | -0.38797 | -0.10761 | 0.3387 | 0.31793 | 0.7059 | -0.036459 | -0.30797 | 123.0213 | 122.8872 | 123.1524 | 122.0595 | -123.0985 | 123.0079 | 123.0791 | 122.8076 | 122.063 | -123.5035
758.9219 | 123.0743 | -122.168 | 0.93384 | 1.4211e-13 | -0.0067265 | 0.0012394 | 0.064186 | -0.0079569 | 0.060994 | 0.0092325 | -0.0035271 | -0.0023459 | 0.069792 | 0.022664 | 0.061703 | -121.6009 | -0.1039 | -122.0333 | 0.85792 | 0.71009 | 0.97985 | -122.1509 | -121.8338 | -0.10037 | -121.8592 | 0.83538 | 0.91111 | 0.60755 | -122.5559 | 0.017047 | -0.075914 | 0.56704 | 0.13465 | 0.1176 | -0.22375 | 0.046012 | -0.38796 | -0.098457 | 0.33413 | 0.30878 | 0.69674 | -0.022725 | -0.32629 | 123.0259 | 122.8781 | 123.1478 | 122.0641 | -123.0848 | 123.0033 | 123.0791 | 122.7755 | 122.0676 | -123.4898
760.6719 | 123.1522 | -122.1634 | 0.86517 | 1.4211e-13 | -0.0067265 | 0.0010256 | 0.064186 | -0.0077431 | 0.060994 | -0.013659 | -0.0035271 | -0.0019187 | 0.069792 | 0.022664 | 0.061917 | -121.633 | -0.10848 | -122.0745 | 0.8213 | 0.6872 | 0.94322 | -122.1876 | -121.8613 | -0.10953 | -121.8821 | 0.79875 | 0.87448 | 0.57092 | -122.5834 | -0.024163 | -0.043876 | 0.53041 | 0.088866 | 0.11303 | -0.17797 | 0.078048 | -0.42001 | -0.06642 | 0.30208 | 0.28131 | 0.70132 | 0.009311 | -0.29425 | 122.9847 | 122.8506 | 123.1066 | 122.0549 | -123.0527 | 122.9621 | 123.0379 | 122.7343 | 122.0539 | -123.4486
762.3594 | 123.0881 | -122.2412 | 0.83771 | 1.4211e-13 | -0.0067265 | 0.0012394 | 0.064186 | -0.0081705 | 0.060994 | 0.0016025 | -0.0037407 | -0.0021323 | 0.069365 | 0.022664 | 0.061489 | -121.6788 | -0.11306 | -122.1112 | 0.78467 | 0.64141 | 0.90201 | -122.215 | -121.9025 | -0.10953 | -121.937 | 0.75297 | 0.82412 | 0.47935 | -122.6292 | 0.026184 | -0.053038 | 0.56244 | 0.13006 | 0.10388 | -0.1963 | 0.064306 | -0.38798 | -0.08474 | 0.33869 | 0.30418 | 0.69216 | -0.013589 | -0.35836 | 123.0259 | 122.8826 | 123.1432 | 122.1282 | -123.0527 | 122.9942 | 123.0653 | 122.7206 | 122.1317 | -123.4669
764.1094 | 123.1155 | -122.2778 | 0.81482 | 1.4211e-13 | -0.0067265 | 0.0012394 | 0.064186 | -0.0077431 | 0.060994 | -0.006028 | -0.0033135 | -0.0025597 | 0.069365 | 0.022451 | 0.061703 | -121.7062 | -0.10848 | -122.134 | 0.7572 | 0.61851 | 0.87912 | -122.2517 | -121.93 | -0.11411 | -121.9599 | 0.73008 | 0.81038 | 0.46103 | -122.6521 | 0.026173 | -0.05762 | 0.5716 | 0.14379 | 0.11762 | -0.1963 | 0.064302 | -0.37426 | -0.084743 | 0.34784 | 0.31791 | 0.69217 | -0.004436 | -0.35379 | 123.035 | 122.8963 | 123.157 | 122.1694 | -123.0665 | 123.0079 | 123.0882 | 122.7389 | 122.1637 | -123.4669
765.7812 | 123.1293 | -122.2687 | 0.80109 | 1.4211e-13 | -0.0067265 | 0.0012394 | 0.0644 | -0.0077431 | 0.061208 | 0.0016025 | -0.0035271 | -0.0019187 | 0.069579 | 0.022878 | 0.061703 | -121.7291 | -0.10848 | -122.1569 | 0.72973 | 0.59104 | 0.85623 | -122.2654 | -121.9483 | -0.10953 | -121.9737 | 0.71634 | 0.78749 | 0.37404 | -122.675 | 0.003282 | -0.071357 | 0.53955 | 0.11174 | 0.10846 | -0.21005 | 0.055142 | -0.40631 | -0.084746 | 0.32037 | 0.29502 | 0.70132 | -0.013596 | -0.42705 | 122.9984 | 122.8597 | 123.1249 | 122.1602 | -123.0665 | 122.985 | 123.0562 | 122.6427 | 122.1591 | -123.4761
767.5312 | 123.2117 | -122.1451 | 0.85144 | 1.4211e-13 | -0.0069401 | 0.0010256 | 0.0644 | -0.0077431 | 0.060994 | -0.013659 | -0.0035271 | -0.0025597 | 0.070006 | 0.022451 | 0.061703 | -121.6192 | -0.10848 | -122.0562 | 0.82588 | 0.69636 | 0.95696 | -122.1601 | -121.843 | -0.10953 | -121.8683 | 0.80791 | 0.88822 | 0.57092 | -122.5742 | -0.014999 | -0.025565 | 0.52583 | 0.088869 | 0.10387 | -0.15508 | 0.10552 | -0.42917 | -0.04353 | 0.30208 | 0.27673 | 0.7059 | 0.03678 | -0.28052 | 122.971 | 122.8414 | 123.102 | 122.0366 | -123.0115 | 122.953 | 123.0333 | 122.716 | 122.0356 | -123.4257
769.2344 | 123.2254 | -122.1817 | 0.8194 | 1.4211e-13 | -0.0067265 | 0.0010256 | 0.063973 | -0.0079569 | 0.061208 | 0.0016025 | -0.0037407 | -0.0023459 | 0.070006 | 0.022878 | 0.061489 | -121.665 | -0.10848 | -122.1112 | 0.78467 | 0.64141 | 0.90659 | -122.2196 | -121.8979 | -0.10953 | -121.9187 | 0.75755 | 0.84243 | 0.46103 | -122.6155 | -0.037904 | -0.034727 | 0.51667 | 0.070551 | 0.10845 | -0.17799 | 0.087196 | -0.43376 | -0.06185 | 0.28376 | 0.26299 | 0.69674 | 0.023037 | -0.35837 | 122.9664 | 122.8231 | 123.0883 | 122.0732 | -123.039 | 122.9392 | 123.0241 | 122.6427 | 122.0722 | -123.4349
770.9844 | 123.2208 | -122.0764 | 0.89264 | 1.4211e-13 | -0.0069401 | 0.0012394 | 0.064186 | -0.0077431 | 0.060781 | 0.0016025 | -0.0033135 | -0.0023459 | 0.069579 | 0.023092 | 0.061703 | -121.5735 | -0.11306 | -121.9875 | 0.87624 | 0.73299 | 0.98901 | -122.128 | -121.7972 | -0.10953 | -121.8226 | 0.84912 | 0.92485 | 0.5755 | -122.533 | -0.051612 | -0.016401 | 0.50295 | 0.088878 | 0.14049 | -0.15965 | 0.096368 | -0.45662 | -0.043522 | 0.2792 | 0.25386 | 0.71048 | 0.032209 | -0.31714 | 122.9527 | 122.8094 | 123.0654 | 121.9634 | -123.0207 | 122.9255 | 123.0013 | 122.6519 | 121.9669 | -123.4257
772.6719 | 123.111 | -122.1725 | 0.89722 | 1.4211e-13 | -0.0067265 | 0.0010256 | 0.064186 | -0.0077431 | 0.060781 | 0.0016025 | -0.0037407 | -0.0021323 | 0.069579 | 0.022664 | 0.061489 | -121.6192 | -0.1039 | -122.0379 | 0.82588 | 0.67804 | 0.9478 | -122.1647 | -121.8476 | -0.11411 | -121.8729 | 0.80791 | 0.87906 | 0.56176 | -122.5742 | 0.007887 | -0.071342 | 0.5533 | 0.13465 | 0.12676 | -0.21918 | 0.050583 | -0.4017 | -0.089307 | 0.32497 | 0.29962 | 0.70132 | -0.018155 | -0.33546 | 122.9984 | 122.8506 | 123.1203 | 122.0686 | -123.0619 | 122.9805 | 123.0516 | 122.7343 | 122.0584 | -123.4715
774.4375 | 123.1888 | -122.0215 | 0.99792 | 1.4211e-13 | -0.0069401 | 0.00081202 | 0.0644 | -0.0075295 | 0.060994 | -0.006028 | -0.0033135 | -0.0021323 | 0.070006 | 0.022878 | 0.061917 | -121.5139 | -0.10848 | -121.928 | 0.94034 | 0.80167 | 1.0531 | -122.0685 | -121.7377 | -0.10953 | -121.763 | 0.91322 | 0.98437 | 0.62586 | -122.4644 | -0.047018 | -0.05759 | 0.50754 | 0.093464 | 0.14048 | -0.19625 | 0.055183 | -0.44287 | -0.084709 | 0.28379 | 0.25845 | 0.70132 | -0.013555 | -0.37206 | 122.9618 | 122.8232 | 123.0746 | 121.913 | -123.0664 | 122.9347 | 123.0059 | 122.6473 | 121.912 | -123.4623
776.1875 | 123.1888 | -122.081 | 0.91553 | 1.4211e-13 | -0.0071537 | 0.0012394 | 0.063973 | -0.0079569 | 0.060567 | 0.0016025 | -0.0037407 | -0.0021323 | 0.069579 | 0.022878 | 0.061703 | -121.546 | -0.11764 | -121.9738 | 0.88997 | 0.76046 | 1.0073 | -122.1143 | -121.7743 | -0.10495 | -121.818 | 0.86285 | 0.94316 | 0.56634 | -122.501 | -0.033297 | -0.025554 | 0.535 | 0.10719 | 0.14049 | -0.15507 | 0.091795 | -0.41999 | -0.052675 | 0.30667 | 0.26301 | 0.683 | 0.027636 | -0.34919 | 122.971 | 122.8415 | 123.0883 | 121.9634 | -123.0298 | 122.9438 | 123.0242 | 122.6473 | 121.976 | -123.4165
777.875 | 123.2071 | -122.1909 | 0.81024 | 1.4211e-13 | -0.0067265 | 0.0012394 | 0.0644 | -0.0079569 | 0.060781 | 0.0016025 | -0.0039543 | -0.0017051 | 0.070006 | 0.023092 | 0.061703 | -121.6559 | -0.10848 | -122.0699 | 0.78925 | 0.65057 | 0.91117 | -122.1647 | -121.8888 | -0.10495 | -121.9004 | 0.7667 | 0.84701 | 0.50224 | -122.6109 | 0.026198 | -0.020994 | 0.53498 | 0.12091 | 0.094712 | -0.15968 | 0.10093 | -0.42002 | -0.043538 | 0.30207 | 0.29046 | 0.71048 | 0.03677 | -0.308 | 122.9801 | 122.8414 | 123.102 | 122.0824 | -122.9749 | 122.9576 | 123.0379 | 122.6931 | 122.0859 | -123.4211
779.625 | 123.0698 | -122.1542 | 0.91553 | 1.4211e-13 | -0.0071537 | 0.0012394 | 0.0644 | -0.0077431 | 0.060994 | -0.006028 | -0.0033135 | -0.0023459 | 0.069792 | 0.022664 | 0.061276 | -121.5872 | -0.11764 | -121.9967 | 0.85792 | 0.71467 | 0.97527 | -122.1463 | -121.8109 | -0.10953 | -121.8409 | 0.8308 | 0.90653 | 0.53887 | -122.5422 | 0.007893 | -0.057603 | 0.56704 | 0.15754 | 0.14965 | -0.20086 | 0.059745 | -0.38796 | -0.084724 | 0.34329 | 0.31336 | 0.70132 | -0.008993 | -0.37666 | 123.0122 | 122.8689 | 123.1295 | 122.0366 | -123.0619 | 122.985 | 123.0608 | 122.6931 | 122.0447 | -123.4577
781.3906 | 123.0606 | -122.2641 | 0.79193 | 1.4211e-13 | -0.0069401 | 0.0012394 | 0.063973 | -0.0079569 | 0.060781 | 0.0016025 | -0.0035271 | -0.0021323 | 0.069792 | 0.022664 | 0.061703 | -121.6833 | -0.10848 | -122.1066 | 0.75262 | 0.61851 | 0.87912 | -122.2471 | -121.9254 | -0.11411 | -121.9416 | 0.73465 | 0.80123 | 0.45645 | -122.6338 | 0.017019 | -0.03931 | 0.58075 | 0.15753 | 0.14051 | -0.17342 | 0.08719 | -0.36967 | -0.057277 | 0.33868 | 0.32249 | 0.69216 | 0.009295 | -0.33548 | 123.0167 | 122.8826 | 123.1432 | 122.1556 | -123.039 | 122.9988 | 123.0653 | 122.7206 | 122.15 | -123.4257
783.0781 | 123.1384 | -122.2092 | 0.78278 | 1.4211e-13 | -0.0071537 | 0.0010256 | 0.063973 | -0.0077431 | 0.060994 | 0.0016025 | -0.0033135 | -0.0021323 | 0.069579 | 0.022664 | 0.061489 | -121.6696 | -0.11306 | -122.0928 | 0.76636 | 0.62767 | 0.8837 | -122.2425 | -121.9025 | -0.10953 | -121.9279 | 0.73465 | 0.81954 | 0.42898 | -122.62 | -0.033334 | -0.01642 | 0.53956 | 0.11633 | 0.14966 | -0.1551 | 0.10092 | -0.41087 | -0.048122 | 0.30664 | 0.2813 | 0.69217 | 0.036765 | -0.35379 | 122.9755 | 122.8368 | 123.0929 | 122.0961 | -123.0253 | 122.9438 | 123.0287 | 122.6381 | 122.0996 | -123.4028
784.8281 | 123.0652 | -122.3511 | 0.73242 | 1.4211e-13 | -0.0069401 | 0.0012394 | 0.063973 | -0.0079569 | 0.060994 | 0.0016025 | -0.0030999 | -0.0025597 | 0.069792 | 0.023092 | 0.061489 | -121.7566 | -0.1039 | -122.1661 | 0.67937 | 0.54067 | 0.80129 | -122.3112 | -121.9849 | -0.10953 | -122.0057 | 0.6614 | 0.73713 | 0.3603 | -122.7116 | 0.039889 | -0.053055 | 0.59448 | 0.18498 | 0.14509 | -0.19175 | 0.068863 | -0.36054 | -0.071024 | 0.36613 | 0.34537 | 0.7059 | 0.004704 | -0.37212 | 123.0304 | 122.8917 | 123.1524 | 122.2472 | -123.0436 | 123.0125 | 123.0882 | 122.7114 | 122.2415 | -123.444
786.5156 | 123.056 | -122.3831 | 0.68665 | 1.4211e-13 | -0.0069401 | 0.0010256 | 0.063973 | -0.0075295 | 0.060781 | -0.013659 | -0.0037407 | -0.0021323 | 0.070006 | 0.022664 | 0.061489 | -121.8161 | -0.11306 | -122.2302 | 0.61527 | 0.48115 | 0.74176 | -122.3844 | -122.049 | -0.11411 | -122.0698 | 0.5973 | 0.67302 | 0.36946 | -122.7757 | -0.001329 | -0.071377 | 0.567 | 0.15293 | 0.15426 | -0.2055 | 0.055117 | -0.3926 | -0.089347 | 0.33408 | 0.31331 | 0.70591 | -0.013621 | -0.31719 | 122.9984 | 122.8643 | 123.1249 | 122.2701 | -123.0711 | 122.9804 | 123.0561 | 122.7526 | 122.269 | -123.4624
788.2656 | 123.0789 | -122.3282 | 0.70953 | 1.4211e-13 | -0.0067265 | 0.0012394 | 0.064186 | -0.0079569 | 0.060567 | -0.021289 | -0.0035271 | -0.0023459 | 0.069792 | 0.022878 | 0.061489 | -121.7932 | -0.11764 | -122.1981 | 0.65648 | 0.5132 | 0.76924 | -122.357 | -122.017 | -0.11411 | -122.0423 | 0.62477 | 0.70508 | 0.39235 | -122.7437 | -0.028788 | -0.053059 | 0.53496 | 0.13005 | 0.15883 | -0.19634 | 0.059701 | -0.41548 | -0.084764 | 0.31119 | 0.28585 | 0.70132 | -0.004459 | -0.31718 | 122.9847 | 122.8414 | 123.0974 | 122.2105 | -123.0665 | 122.953 | 123.0333 | 122.7205 | 122.2141 | -123.4532
790.0312 | 123.0469 | -122.2961 | 0.7782 | 1.4211e-13 | -0.0067265 | 0.0010256 | 0.063973 | -0.0079569 | 0.060994 | -0.006028 | -0.0035271 | -0.0025597 | 0.070006 | 0.023092 | 0.061703 | -121.7383 | -0.11306 | -122.1478 | 0.6931 | 0.55441 | 0.82418 | -122.2883 | -121.9712 | -0.11411 | -121.9874 | 0.67513 | 0.75544 | 0.34199 | -122.6933 | 0.007853 | -0.085096 | 0.55786 | 0.14836 | 0.14051 | -0.22379 | 0.04598 | -0.39715 | -0.10306 | 0.32494 | 0.30875 | 0.7059 | -0.022758 | -0.43621 | 122.9892 | 122.8506 | 123.1203 | 122.1831 | -123.0665 | 122.9713 | 123.0516 | 122.6381 | 122.182 | -123.4715
791.7031 | 123.0515 | -122.3053 | 0.74616 | 1.4211e-13 | -0.0067265 | 0.00059822 | 0.0644 | -0.0079569 | 0.061208 | -0.006028 | -0.0030999 | -0.0023459 | 0.069792 | 0.022878 | 0.061703 | -121.752 | -0.10848 | -122.1661 | 0.67937 | 0.54983 | 0.80129 | -122.3112 | -121.9849 | -0.11869 | -122.0103 | 0.66598 | 0.73713 | 0.42898 | -122.7025 | -0.005887 | -0.066788 | 0.55328 | 0.13921 | 0.14509 | -0.19632 | 0.05513 | -0.39716 | -0.080178 | 0.32036 | 0.29501 | 0.69217 | -0.009029 | -0.31717 | 122.9847 | 122.8551 | 123.1066 | 122.1968 | -123.0573 | 122.9713 | 123.0424 | 122.7343 | 122.1866 | -123.4486
793.4531 | 123.0423 | -122.3923 | 0.67291 | 1.4211e-13 | -0.0071537 | 0.0012394 | 0.063973 | -0.0077431 | 0.060781 | -0.013659 | -0.0035271 | -0.0023459 | 0.069792 | 0.022664 | 0.061703 | -121.8253 | -0.11306 | -122.2393 | 0.60153 | 0.46741 | 0.73261 | -122.3753 | -122.0536 | -0.10953 | -122.0744 | 0.57441 | 0.65471 | 0.33283 | -122.7849 | 0.016983 | -0.071379 | 0.567 | 0.15293 | 0.13595 | -0.2055 | 0.059693 | -0.3926 | -0.098506 | 0.33865 | 0.31788 | 0.71048 | -0.018202 | -0.34008 | 122.9938 | 122.8597 | 123.1249 | 122.2792 | -123.0482 | 122.9667 | 123.047 | 122.7251 | 122.2827 | -123.4578
795.2188 | 123.0515 | -122.3831 | 0.67291 | 1.4211e-13 | -0.0067265 | 0.00081202 | 0.064614 | -0.0079569 | 0.060994 | -0.013659 | -0.0035271 | -0.0019187 | 0.070006 | 0.023092 | 0.061703 | -121.8436 | -0.10848 | -122.2577 | 0.59238 | 0.45367 | 0.70513 | -122.3982 | -122.0719 | -0.11411 | -122.0927 | 0.56525 | 0.65013 | 0.32367 | -122.8078 | -0.015066 | -0.080536 | 0.53953 | 0.12546 | 0.14053 | -0.21924 | 0.032221 | -0.42465 | -0.10766 | 0.31118 | 0.29041 | 0.71506 | -0.022781 | -0.34924 | 122.9755 | 122.8368 | 123.0883 | 122.2746 | -123.0711 | 122.9484 | 123.0332 | 122.7068 | 122.269 | -123.4807
796.9531 | 123.0377 | -122.3969 | 0.65918 | 1.4211e-13 | -0.0067265 | 0.0010256 | 0.063759 | -0.0079569 | 0.061208 | -0.013659 | -0.0037407 | -0.0023459 | 0.069792 | 0.022878 | 0.061703 | -121.839 | -0.11764 | -122.2439 | 0.59696 | 0.45367 | 0.71429 | -122.3799 | -122.0719 | -0.11411 | -122.0835 | 0.56983 | 0.65013 | 0.33741 | -122.7986 | 0.016982 | -0.062224 | 0.55784 | 0.15293 | 0.13595 | -0.20551 | 0.055111 | -0.40176 | -0.089351 | 0.32492 | 0.3133 | 0.71506 | -0.009048 | -0.32177 | 122.9938 | 122.8505 | 123.1111 | 122.2792 | -123.039 | 122.9667 | 123.047 | 122.7343 | 122.2827 | -123.4578
798.6406 | 123.0515 | -122.4335 | 0.64545 | 1.4211e-13 | -0.0069401 | 0.0010256 | 0.064186 | -0.0079569 | 0.060567 | -0.021289 | -0.0035271 | -0.0019187 | 0.070006 | 0.022878 | 0.061489 | -121.8527 | -0.11764 | -122.2668 | 0.57406 | 0.43078 | 0.69598 | -122.4073 | -122.0811 | -0.11411 | -122.111 | 0.55151 | 0.62724 | 0.30994 | -122.8123 | 0.02613 | -0.071383 | 0.58073 | 0.16666 | 0.14053 | -0.21467 | 0.05053 | -0.37887 | -0.093932 | 0.35238 | 0.32245 | 0.70133 | -0.018208 | -0.33551 | 123.0075 | 122.8642 | 123.1294 | 122.3158 | -123.0528 | 122.985 | 123.0607 | 122.7434 | 122.3194 | -123.4578
800.3906 | 123.0469 | -122.4106 | 0.67291 | 1.4211e-13 | -0.0069401 | 0.0012394 | 0.064186 | -0.0077431 | 0.060781 | -0.006028 | -0.0035271 | -0.0021323 | 0.069579 | 0.022664 | 0.061489 | -121.839 | -0.1039 | -122.2485 | 0.58322 | 0.45367 | 0.70513 | -122.3844 | -122.0674 | -0.11411 | -122.0881 | 0.56525 | 0.64097 | 0.41983 | -122.794 | 0.026136 | -0.089692 | 0.57157 | 0.16208 | 0.13595 | -0.21924 | 0.032221 | -0.38345 | -0.10766 | 0.34323 | 0.32246 | 0.70591 | -0.031938 | -0.25309 | 122.9938 | 122.8643 | 123.1157 | 122.3067 | -123.0574 | 122.9758 | 123.0516 | 122.8304 | 122.2965 | -123.4669
802.1406 | 123.1338 | -122.3923 | 0.6134 | 1.4211e-13 | -0.0069401 | 0.00081202 | 0.064186 | -0.0079569 | 0.060994 | 0.0016025 | -0.0035271 | -0.0023459 | 0.069792 | 0.022878 | 0.061917 | -121.8344 | -0.10848 | -122.2668 | 0.57864 | 0.44909 | 0.70971 | -122.4028 | -122.0719 | -0.10953 | -122.0973 | 0.55609 | 0.64097 | 0.31452 | -122.8032 | -0.01049 | -0.034761 | 0.55784 | 0.12546 | 0.13595 | -0.16431 | 0.09631 | -0.41092 | -0.05731 | 0.32034 | 0.29499 | 0.70591 | 0.027572 | -0.29889 | 122.9709 | 122.8414 | 123.102 | 122.2838 | -123.0162 | 122.9484 | 123.0332 | 122.7068 | 122.2827 | -123.4166
803.8906 | 123.0469 | -122.3923 | 0.6546 | 1.4211e-13 | -0.0067265 | 0.0012394 | 0.064186 | -0.0075295 | 0.061422 | 0.0092325 | -0.0035271 | -0.0021323 | 0.070006 | 0.023092 | 0.061703 | -121.8253 | -0.11764 | -122.2485 | 0.59238 | 0.46283 | 0.72345 | -122.3936 | -122.0582 | -0.12327 | -122.0835 | 0.56983 | 0.65013 | 0.33283 | -122.7849 | -0.001332 | -0.062225 | 0.567 | 0.14377 | 0.1451 | -0.19177 | 0.068847 | -0.3926 | -0.084773 | 0.33407 | 0.30873 | 0.70133 | -0.00447 | -0.32177 | 122.9847 | 122.8551 | 123.1157 | 122.2746 | -123.0482 | 122.9621 | 123.0424 | 122.7251 | 122.269 | -123.4395
805.5938 | 123.175 | -122.3282 | 0.64087 | 1.4211e-13 | -0.0069401 | 0.0012394 | 0.063973 | -0.0075295 | 0.060781 | 0.0016025 | -0.0037407 | -0.0021323 | 0.069579 | 0.023092 | 0.06213 | -121.807 | -0.11306 | -122.2165 | 0.61069 | 0.47199 | 0.73718 | -122.357 | -122.0399 | -0.10953 | -122.0607 | 0.59272 | 0.65929 | 0.35115 | -122.7711 | -0.028788 | -0.030178 | 0.52123 | 0.11173 | 0.14052 | -0.16888 | 0.096315 | -0.44295 | -0.048148 | 0.2883 | 0.26753 | 0.71048 | 0.01842 | -0.28972 | 122.9389 | 122.8002 | 123.0654 | 122.2151 | -122.9978 | 122.9209 | 122.9875 | 122.6793 | 122.2187 | -123.412
807.3438 | 123.1384 | -122.3877 | 0.62714 | 1.4211e-13 | -0.0069401 | 0.0012394 | 0.063973 | -0.0079569 | 0.060781 | -0.006028 | -0.0033135 | -0.0023459 | 0.069792 | 0.022878 | 0.061703 | -121.839 | -0.11306 | -122.2531 | 0.58322 | 0.44451 | 0.70513 | -122.3936 | -122.0674 | -0.11869 | -122.0927 | 0.55609 | 0.63182 | 0.36488 | -122.794 | -0.00591 | -0.043915 | 0.54868 | 0.13462 | 0.14053 | -0.18262 | 0.077998 | -0.40634 | -0.071043 | 0.32034 | 0.29499 | 0.70133 | 0.004682 | -0.26225 | 122.9709 | 122.8322 | 123.0928 | 122.2746 | -123.0207 | 122.9438 | 123.0195 | 122.7526 | 122.269 | -123.4212
809.0469 | 123.1888 | -122.3785 | 0.59509 | 1.4211e-13 | -0.0067265 | 0.0016666 | 0.0644 | -0.0077431 | 0.060781 | -0.006028 | -0.0030999 | -0.0023459 | 0.070006 | 0.022451 | 0.061917 | -121.8299 | -0.11764 | -122.2531 | 0.5878 | 0.43994 | 0.70513 | -122.3799 | -122.0719 | -0.11411 | -122.0973 | 0.54694 | 0.63182 | 0.168 | -122.8032 | -0.001329 | -0.007294 | 0.54869 | 0.12546 | 0.12679 | -0.15516 | 0.11004 | -0.42465 | -0.048157 | 0.3066 | 0.28126 | 0.70591 | 0.036725 | -0.42709 | 122.9663 | 122.8185 | 123.0837 | 122.2609 | -122.975 | 122.9255 | 123.0104 | 122.5465 | 122.2644 | -123.3983
810.7812 | 123.1613 | -122.4014 | 0.5722 | 1.4211e-13 | -0.0069401 | 0.00081202 | 0.064186 | -0.0077431 | 0.060567 | 0.0016025 | -0.0037407 | -0.0021323 | 0.069579 | 0.023305 | 0.061703 | -121.8573 | -0.11764 | -122.2851 | 0.55117 | 0.41704 | 0.67308 | -122.4073 | -122.0948 | -0.11869 | -122.111 | 0.52862 | 0.60893 | 0.17258 | -122.8307 | -0.005914 | -0.021033 | 0.5441 | 0.1163 | 0.12222 | -0.15516 | 0.10088 | -0.42923 | -0.043583 | 0.3066 | 0.29041 | 0.71964 | 0.03672 | -0.39962 | 122.9526 | 122.8185 | 123.0745 | 122.2838 | -122.9795 | 122.93 | 123.0104 | 122.574 | 122.2827 | -123.4029
812.5312 | 123.0698 | -122.406 | 0.63171 | 1.4211e-13 | -0.0069401 | 0.0010256 | 0.063973 | -0.0077431 | 0.060567 | -0.006028 | -0.0035271 | -0.0023459 | 0.069792 | 0.023092 | 0.061703 | -121.8573 | -0.11764 | -122.2714 | 0.56033 | 0.43078 | 0.68224 | -122.4073 | -122.0811 | -0.12327 | -122.1156 | 0.5332 | 0.6135 | 0.29162 | -122.8123 | -0.001336 | -0.071385 | 0.54868 | 0.13462 | 0.13595 | -0.20094 | 0.050527 | -0.40634 | -0.098513 | 0.32491 | 0.29041 | 0.69675 | -0.018211 | -0.34009 | 122.9663 | 122.8368 | 123.0882 | 122.2884 | -123.0391 | 122.9392 | 123.0195 | 122.6976 | 122.2827 | -123.4441
814.2812 | 123.1522 | -122.3785 | 0.59967 | 1.4211e-13 | -0.0071537 | 0.0012394 | 0.063973 | -0.0077431 | 0.060781 | -0.006028 | -0.0035271 | -0.0023459 | 0.070006 | 0.023305 | 0.061489 | -121.8436 | -0.11306 | -122.2622 | 0.56033 | 0.4262 | 0.6914 | -122.4119 | -122.0765 | -0.11411 | -122.1019 | 0.54694 | 0.62266 | 0.24126 | -122.8078 | -0.033381 | -0.039341 | 0.53495 | 0.1163 | 0.14969 | -0.17347 | 0.091728 | -0.42923 | -0.052734 | 0.30203 | 0.27668 | 0.70591 | 0.022991 | -0.35841 | 122.9389 | 122.8047 | 123.0699 | 122.2655 | -123.0116 | 122.9255 | 123.0012 | 122.6198 | 122.2644 | -123.4074
816.0312 | 123.0789 | -122.4335 | 0.60425 | 1.4211e-13 | -0.0069401 | 0.0012394 | 0.063973 | -0.0077431 | 0.060567 | 0.0016025 | -0.0035271 | -0.0025597 | 0.070006 | 0.022878 | 0.061917 | -121.8711 | -0.11306 | -122.2851 | 0.54202 | 0.4033 | 0.67308 | -122.4211 | -122.0994 | -0.11411 | -122.1248 | 0.51946 | 0.59977 | 0.25957 | -122.8261 | 0.012393 | -0.062233 | 0.56241 | 0.14835 | 0.13595 | -0.20094 | 0.068836 | -0.39261 | -0.084783 | 0.33406 | 0.30872 | 0.70133 | -0.00448 | -0.34467 | 122.9755 | 122.8368 | 123.1066 | 122.3204 | -123.0253 | 122.9529 | 123.0332 | 122.693 | 122.3194 | -123.4303
817.7188 | 123.1155 | -122.406 | 0.59052 | 1.4211e-13 | -0.0071537 | 0.0012394 | 0.064186 | -0.0075295 | 0.060781 | -0.021289 | -0.0035271 | -0.0021323 | 0.069792 | 0.023305 | 0.061489 | -121.8527 | -0.11306 | -122.2668 | 0.56033 | 0.43078 | 0.68682 | -122.4028 | -122.0857 | -0.11869 | -122.0973 | 0.54236 | 0.60435 | 0.28704 | -122.8123 | 0.003243 | -0.030186 | 0.55326 | 0.13919 | 0.13595 | -0.15974 | 0.096305 | -0.40634 | -0.048157 | 0.32033 | 0.30872 | 0.71506 | 0.013831 | -0.30347 | 122.9663 | 122.8368 | 123.0928 | 122.2929 | -122.9933 | 122.9484 | 123.0104 | 122.6931 | 122.2873 | -123.4029
819.4688 | 122.8867 | -121.6644 | 1.2314 | 1.4211e-13 | -0.0075811 | 0.0012394 | 0.0644 | -0.0079569 | 0.060567 | 0.0016025 | -0.0033135 | -0.0021323 | 0.07022 | 0.022878 | 0.061489 | -121.2576 | -0.099323 | -121.6671 | 1.0456 | 0.90241 | 1.1676 | -121.8167 | -121.4767 | -0.095794 | -121.4975 | 1.0277 | 1.1034 | 0.72201 | -122.2079 | -0.15223 | -0.18575 | 0.40687 | -0.002629 | 0.1496 | -0.32898 | -0.063811 | -0.54351 | -0.20371 | 0.18773 | 0.16696 | 0.71047 | -0.12797 | -0.50937 | 122.7101 | 122.5668 | 122.832 | 121.5651 | -123.048 | 122.6921 | 122.7678 | 122.3864 | 121.5686 | -123.4393
821.2188 | 122.7036 | -121.4172 | 1.2589 | 1.4211e-13 | -0.0069401 | 0.001453 | 0.063759 | -0.0079569 | 0.060567 | 0.0016025 | -0.0037407 | -0.0023459 | 0.070006 | 0.023305 | 0.061703 | -120.8684 | -0.10848 | -121.2733 | 1.1967 | 1.0672 | 1.3278 | -121.4091 | -121.0921 | -0.11411 | -121.1266 | 1.1788 | 1.2545 | 1.015 | -121.8233 | 0.008099 | -0.062125 | 0.54884 | 0.14391 | 0.13581 | -0.1916 | 0.068974 | -0.40609 | -0.080082 | 0.32514 | 0.29064 | 0.69673 | -0.004342 | -0.24381 | 122.614 | 122.4845 | 122.7451 | 121.3088 | -122.668 | 122.596 | 122.6717 | 122.4323 | 121.3031 | -123.0822
822.9688 | 122.5983 | -121.3623 | 1.2543 | 1.4211e-13 | -0.0069401 | 0.0010256 | 0.063973 | -0.0077431 | 0.060567 | -0.013659 | -0.0035271 | -0.0019187 | 0.070006 | 0.023092 | 0.061489 | -120.7997 | -0.11764 | -121.2092 | 1.183 | 1.0444 | 1.3004 | -121.3588 | -121.0234 | -0.11411 | -121.0533 | 1.165 | 1.2316 | 0.90973 | -121.7546 | 0.003537 | -0.071283 | 0.56259 | 0.15308 | 0.14954 | -0.20992 | 0.04608 | -0.39233 | -0.089239 | 0.33889 | 0.30897 | 0.7013 | -0.022657 | -0.34454 | 122.5453 | 122.4067 | 122.6627 | 121.2447 | -122.613 | 122.5273 | 122.5939 | 122.272 | 121.2482 | -123.0089
824.7344 | 122.5616 | -121.3074 | 1.268 | 1.4211e-13 | -0.0069401 | 0.0010256 | 0.063759 | -0.0081705 | 0.060353 | -0.013659 | -0.0037407 | -0.0025597 | 0.069792 | 0.023305 | 0.061489 | -120.7402 | -0.11306 | -121.1451 | 1.1967 | 1.0489 | 1.3095 | -121.2809 | -120.9685 | -0.10953 | -120.9892 | 1.1696 | 1.2499 | 0.95552 | -121.6951 | 0.026446 | -0.07128 | 0.56718 | 0.16224 | 0.13579 | -0.21907 | 0.041505 | -0.38774 | -0.098394 | 0.33891 | 0.31814 | 0.70588 | -0.018076 | -0.31248 | 122.5041 | 122.3563 | 122.6169 | 121.1943 | -122.5489 | 122.477 | 122.5573 | 122.2629 | 121.1978 | -122.9631
826.4219 | 122.5296 | -121.1975 | 1.3138 | 1.4211e-13 | -0.0069401 | 0.00081202 | 0.063545 | -0.0077431 | 0.060567 | 0.0016025 | -0.0035271 | -0.0023459 | 0.069792 | 0.023092 | 0.061703 | -120.6578 | -0.10848 | -121.0581 | 1.2471 | 1.113 | 1.369 | -121.1985 | -120.8723 | -0.11411 | -120.9068 | 1.2246 | 1.2957 | 1.0654 | -121.599 | -0.000996 | -0.066695 | 0.53972 | 0.13936 | 0.14036 | -0.20074 | 0.055249 | -0.40145 | -0.089229 | 0.3252 | 0.29069 | 0.69214 | -0.018067 | -0.24837 | 122.4446 | 122.3105 | 122.5665 | 121.089 | -122.5123 | 122.4221 | 122.4932 | 122.2629 | 121.0834 | -122.9127
828.1719 | 122.5983 | -121.1929 | 1.2131 | 1.4211e-13 | -0.0071537 | 0.00081202 | 0.063545 | -0.0075295 | 0.060781 | -0.006028 | -0.0033135 | -0.0021323 | 0.069365 | 0.022878 | 0.061917 | -120.6898 | -0.11306 | -121.0856 | 1.183 | 1.0581 | 1.3095 | -121.2351 | -120.9089 | -0.11411 | -120.9297 | 1.165 | 1.2408 | 0.99673 | -121.6356 | -0.042205 | -0.030085 | 0.5031 | 0.10731 | 0.14952 | -0.15498 | 0.096436 | -0.44266 | -0.048041 | 0.28399 | 0.26322 | 0.70588 | 0.027698 | -0.21635 | 122.3759 | 122.251 | 122.5024 | 121.0799 | -122.4482 | 122.358 | 122.4337 | 122.1897 | 121.0788 | -122.8487
829.9219 | 122.5113 | -121.225 | 1.2314 | 1.4211e-13 | -0.0071537 | 0.0010256 | 0.063973 | -0.0075295 | 0.060781 | 0.0016025 | -0.0037407 | -0.0025597 | 0.069365 | 0.023092 | 0.061703 | -120.6853 | -0.11764 | -121.0902 | 1.1693 | 1.0352 | 1.282 | -121.2306 | -120.8998 | -0.11411 | -120.9297 | 1.1467 | 1.2225 | 0.97841 | -121.631 | -0.005582 | -0.06213 | 0.53972 | 0.13478 | 0.14036 | -0.19619 | 0.050654 | -0.40604 | -0.084665 | 0.32519 | 0.29526 | 0.7013 | -0.008926 | -0.25297 | 122.3942 | 122.2602 | 122.507 | 121.1073 | -122.4619 | 122.3717 | 122.4474 | 122.2034 | 121.1109 | -122.8624
831.6094 | 122.4426 | -121.1929 | 1.2405 | 1.4211e-13 | -0.0069401 | 0.001453 | 0.063759 | -0.0081705 | 0.060567 | -0.006028 | -0.0037407 | -0.0023459 | 0.069792 | 0.023305 | 0.061489 | -120.6349 | -0.11306 | -121.0536 | 1.183 | 1.0489 | 1.3049 | -121.1802 | -120.8632 | -0.11869 | -120.8931 | 1.1513 | 1.2362 | 0.92347 | -121.599 | 0.012742 | -0.057551 | 0.55804 | 0.13936 | 0.12662 | -0.19161 | 0.064391 | -0.40603 | -0.089243 | 0.32978 | 0.29985 | 0.70588 | -0.004347 | -0.31707 | 122.3759 | 122.2419 | 122.4979 | 121.0799 | -122.4207 | 122.3442 | 122.4291 | 122.1164 | 121.0742 | -122.8395
833.3594 | 122.4014 | -121.17 | 1.2405 | 1.4211e-13 | -0.0071537 | 0.00081202 | 0.063759 | -0.0075295 | 0.060353 | 0.0016025 | -0.0037407 | -0.0025597 | 0.069579 | 0.023305 | 0.061276 | -120.612 | -0.1039 | -121.0261 | 1.183 | 1.0444 | 1.2958 | -121.1436 | -120.8311 | -0.11411 | -120.8473 | 1.1559 | 1.2316 | 0.86395 | -121.5577 | 0.026485 | -0.057551 | 0.55804 | 0.14395 | 0.11746 | -0.19619 | 0.055234 | -0.38771 | -0.084664 | 0.33894 | 0.32275 | 0.71045 | -0.008925 | -0.37659 | 122.353 | 122.2144 | 122.4658 | 121.0661 | -122.3841 | 122.3259 | 122.4017 | 122.034 | 121.0559 | -122.7983
835.125 | 122.438 | -121.2479 | 1.0941 | 1.4211e-13 | -0.0069401 | 0.0010256 | 0.063545 | -0.0077431 | 0.06014 | -0.021289 | -0.0037407 | -0.0019187 | 0.069579 | 0.023305 | 0.061703 | -120.6898 | -0.11306 | -121.1039 | 1.0777 | 0.93446 | 1.1905 | -121.2351 | -120.9181 | -0.11411 | -120.9434 | 1.0506 | 1.1355 | 0.86853 | -121.6493 | 0.012727 | -0.016368 | 0.55803 | 0.14393 | 0.13121 | -0.1596 | 0.096411 | -0.40146 | -0.043484 | 0.32976 | 0.30442 | 0.70588 | 0.041409 | -0.22553 | 122.3256 | 122.1823 | 122.4383 | 121.1348 | -122.3292 | 122.2984 | 122.3833 | 122.1164 | 121.1338 | -122.7434
836.875 | 122.3557 | -121.1884 | 1.1902 | 1.4211e-13 | -0.0071537 | 0.0012394 | 0.063759 | -0.0079569 | 0.060567 | 0.0016025 | -0.0037407 | -0.0023459 | 0.069579 | 0.023519 | 0.061489 | -120.612 | -0.11306 | -121.0307 | 1.1235 | 0.97567 | 1.2408 | -121.1665 | -120.8403 | -0.11411 | -120.8702 | 1.1009 | 1.1721 | 0.92805 | -121.5669 | 0.0219 | -0.066716 | 0.57635 | 0.15768 | 0.13578 | -0.21452 | 0.050645 | -0.37855 | -0.089252 | 0.34809 | 0.31817 | 0.69672 | -0.018093 | -0.26214 | 122.3118 | 122.164 | 122.4292 | 121.0753 | -122.3566 | 122.2893 | 122.3604 | 122.1164 | 121.0742 | -122.7571
838.5625 | 122.4335 | -121.1334 | 1.149 | 1.4211e-13 | -0.0069401 | 0.0012394 | 0.063759 | -0.0079569 | 0.060567 | -0.006028 | -0.0039543 | -0.0023459 | 0.069365 | 0.023305 | 0.061489 | -120.5845 | -0.11306 | -121.0078 | 1.1189 | 0.98025 | 1.2363 | -121.1436 | -120.8174 | -0.12327 | -120.8473 | 1.0918 | 1.1721 | 0.95094 | -121.5532 | -0.010136 | -0.030095 | 0.54889 | 0.12564 | 0.13577 | -0.16874 | 0.087265 | -0.41975 | -0.05721 | 0.31605 | 0.28613 | 0.70588 | 0.023106 | -0.19804 | 122.2523 | 122.1137 | 122.3697 | 121.0204 | -122.2925 | 122.2252 | 122.3055 | 122.0844 | 121.0102 | -122.7022
840.3125 | 122.3328 | -121.0831 | 1.1856 | 1.4211e-13 | -0.0069401 | 0.0010256 | 0.064186 | -0.0081705 | 0.060353 | 0.0016025 | -0.0033135 | -0.0025597 | 0.069579 | 0.023092 | 0.061917 | -120.5571 | -0.10848 | -120.962 | 1.1326 | 0.99857 | 1.2591 | -121.1069 | -120.7624 | -0.11411 | -120.8015 | 1.1101 | 1.195 | 0.92347 | -121.5165 | -0.023859 | -0.052981 | 0.52601 | 0.12107 | 0.14493 | -0.18704 | 0.073537 | -0.43347 | -0.075517 | 0.32064 | 0.28156 | 0.71503 | 0.009378 | -0.26214 | 122.2157 | 122.0816 | 122.3422 | 120.9746 | -122.2925 | 122.1932 | 122.2781 | 122.0065 | 120.969 | -122.7021
841.9844 | 122.3602 | -121.0373 | 1.1948 | 1.4211e-13 | -0.0071537 | 0.0010256 | 0.063759 | -0.0079569 | 0.060567 | 0.0016025 | -0.0039543 | -0.0025597 | 0.069579 | 0.023092 | 0.061276 | -120.525 | -0.11306 | -120.9391 | 1.1418 | 1.0077 | 1.2591 | -121.0749 | -120.7578 | -0.11869 | -120.7786 | 1.1101 | 1.1996 | 0.94636 | -121.4753 | -0.037583 | -0.052979 | 0.51228 | 0.09818 | 0.13576 | -0.18704 | 0.064382 | -0.43804 | -0.084672 | 0.27945 | 0.25868 | 0.69672 | 0.004802 | -0.2484 | 122.1791 | 122.045 | 122.2964 | 120.9242 | -122.2696 | 122.1474 | 122.2369 | 121.9837 | 120.9186 | -122.6701
843.7344 | 122.287 | -121.0876 | 1.1581 | 1.4211e-13 | -0.0069401 | 0.001453 | 0.063973 | -0.0081705 | 0.059926 | -0.013659 | -0.0037407 | -0.0021323 | 0.069151 | 0.023305 | 0.061489 | -120.5433 | -0.11306 | -120.9483 | 1.1006 | 0.96193 | 1.2271 | -121.084 | -120.7716 | -0.11411 | -120.7924 | 1.078 | 1.1629 | 0.91431 | -121.4982 | 0.003613 | -0.057563 | 0.54432 | 0.13938 | 0.13577 | -0.19621 | 0.068953 | -0.41058 | -0.080101 | 0.31606 | 0.2953 | 0.70588 | 0.004794 | -0.24383 | 122.1882 | 122.0496 | 122.3147 | 120.9746 | -122.2422 | 122.1657 | 122.2506 | 122.002 | 120.9735 | -122.6564
845.5 | 122.2275 | -121.0556 | 1.1673 | 1.4211e-13 | -0.0067265 | 0.00081202 | 0.063759 | -0.0081705 | 0.060567 | -0.006028 | -0.0035271 | -0.0021323 | 0.069365 | 0.023305 | 0.061276 | -120.5159 | -0.11764 | -120.9345 | 1.1006 | 0.95735 | 1.2225 | -121.0703 | -120.7441 | -0.11869 | -120.774 | 1.078 | 1.1629 | 0.83648 | -121.4845 | -0.014693 | -0.066718 | 0.53975 | 0.12107 | 0.13576 | -0.20994 | 0.055219 | -0.42889 | -0.089256 | 0.31149 | 0.28157 | 0.71045 | -0.004361 | -0.33082 | 122.1562 | 122.013 | 122.2781 | 120.938 | -122.2376 | 122.1336 | 122.2185 | 121.8921 | 120.9369 | -122.6518
847.25 | 122.3373 | -120.9778 | 1.1261 | 1.4211e-13 | -0.0073675 | 0.0012394 | 0.063331 | -0.0081705 | 0.060353 | 0.0016025 | -0.0037407 | -0.0023459 | 0.069365 | 0.023092 | 0.060848 | -120.4701 | -0.11764 | -120.8888 | 1.1235 | 0.98483 | 1.2408 | -121.0291 | -120.7075 | -0.11869 | -120.7282 | 1.0918 | 1.1812 | 0.9601 | -121.4295 | -0.051303 | -0.002629 | 0.50771 | 0.089033 | 0.14034 | -0.14127 | 0.11473 | -0.45176 | -0.034322 | 0.2703 | 0.24953 | 0.70129 | 0.055151 | -0.166 | 122.1013 | 121.9626 | 122.2186 | 120.8601 | -122.1552 | 122.0696 | 122.159 | 121.9379 | 120.8591 | -122.5556
848.9844 | 122.2504 | -120.9915 | 1.1673 | 1.4211e-13 | -0.0071537 | 0.0010256 | 0.063545 | -0.0079569 | 0.060353 | 0.0016025 | -0.0035271 | -0.0023459 | 0.069365 | 0.023305 | 0.061062 | -120.4563 | -0.11764 | -120.8659 | 1.1235 | 0.98025 | 1.2408 | -121.0016 | -120.6846 | -0.11411 | -120.7099 | 1.0872 | 1.1721 | 0.91889 | -121.4158 | -0.010096 | -0.043827 | 0.53518 | 0.12566 | 0.13575 | -0.18705 | 0.073534 | -0.42429 | -0.080099 | 0.30693 | 0.28158 | 0.70587 | 0.004796 | -0.2484 | 122.115 | 121.9718 | 122.2323 | 120.8739 | -122.1689 | 122.0787 | 122.1636 | 121.9104 | 120.8774 | -122.5831
850.6719 | 122.2321 | -120.9732 | 1.1307 | 1.4211e-13 | -0.0071537 | 0.0010256 | 0.063759 | -0.0079569 | 0.060353 | -0.006028 | -0.0039543 | -0.0021323 | 0.068938 | 0.023519 | 0.061489 | -120.4426 | -0.11306 | -120.8567 | 1.1052 | 0.97109 | 1.2317 | -120.9879 | -120.6754 | -0.11869 | -120.6916 | 1.0826 | 1.1629 | 0.79527 | -121.4066 | -0.014669 | -0.025519 | 0.5306 | 0.1165 | 0.13117 | -0.15958 | 0.101 | -0.43344 | -0.048056 | 0.29778 | 0.28159 | 0.71503 | 0.03226 | -0.33541 | 122.0784 | 121.9443 | 122.2049 | 120.8601 | -122.1186 | 122.0558 | 122.1361 | 121.7685 | 120.8545 | -122.5373
852.4219 | 122.1176 | -120.9549 | 1.1673 | 1.4211e-13 | -0.0073675 | 0.0010256 | 0.063331 | -0.0081705 | 0.060567 | -0.006028 | -0.0039543 | -0.0023459 | 0.069365 | 0.023092 | 0.061276 | -120.4243 | -0.11764 | -120.8292 | 1.1052 | 0.98025 | 1.2317 | -120.9696 | -120.6434 | -0.11411 | -120.6733 | 1.0826 | 1.1629 | 0.896 | -121.3838 | -0.014665 | -0.06214 | 0.53061 | 0.12566 | 0.14033 | -0.18705 | 0.064376 | -0.42886 | -0.084677 | 0.31152 | 0.28159 | 0.71045 | -0.004361 | -0.2713 | 122.0601 | 121.9351 | 122.1866 | 120.8373 | -122.1369 | 122.0375 | 122.1178 | 121.8509 | 120.8408 | -122.5511
854.1875 | 122.1313 | -121.0281 | 1.1124 | 1.4211e-13 | -0.0073675 | 0.0010256 | 0.063545 | -0.0077431 | 0.060353 | 0.0016025 | -0.0033135 | -0.0023459 | 0.069365 | 0.023305 | 0.061489 | -120.4334 | -0.10848 | -120.8475 | 1.0594 | 0.9253 | 1.1859 | -120.9879 | -120.6571 | -0.10953 | -120.6916 | 1.0414 | 1.1263 | 0.86853 | -121.3975 | 0.040262 | -0.052993 | 0.59469 | 0.18059 | 0.14033 | -0.18706 | 0.073521 | -0.36935 | -0.070952 | 0.37102 | 0.33652 | 0.70587 | 0.013941 | -0.24384 | 122.0875 | 121.9534 | 122.214 | 120.9197 | -122.1002 | 122.0696 | 122.1544 | 121.8967 | 120.9186 | -122.5099
855.9375 | 122.2458 | -120.9137 | 1.1078 | 1.4211e-13 | -0.0071537 | 0.0010256 | 0.063545 | -0.0079569 | 0.060567 | 0.0016025 | -0.0039543 | -0.0023459 | 0.069151 | 0.023305 | 0.061276 | -120.4106 | -0.11306 | -120.8201 | 1.0685 | 0.93904 | 1.1905 | -120.9604 | -120.6342 | -0.11411 | -120.655 | 1.0414 | 1.1309 | 0.87311 | -121.3654 | -0.046706 | -0.039258 | 0.50314 | 0.09362 | 0.14033 | -0.16875 | 0.082678 | -0.45174 | -0.066374 | 0.27948 | 0.25871 | 0.71045 | 0.023098 | -0.23468 | 121.9822 | 121.8527 | 122.1042 | 120.8006 | -122.0682 | 121.9551 | 122.0446 | 121.7868 | 120.7996 | -122.4732
857.6875 | 122.1313 | -120.9091 | 1.0895 | 1.4211e-13 | -0.0067265 | 0.0010256 | 0.063331 | -0.0079569 | 0.06014 | -0.013659 | -0.0037407 | -0.0021323 | 0.069365 | 0.023305 | 0.061276 | -120.3877 | -0.12679 | -120.8018 | 1.0685 | 0.92988 | 1.195 | -120.9467 | -120.6205 | -0.12327 | -120.6458 | 1.0414 | 1.1217 | 0.79527 | -121.3563 | -0.037546 | -0.020948 | 0.52146 | 0.10736 | 0.1449 | -0.1596 | 0.10557 | -0.44716 | -0.048064 | 0.28863 | 0.26329 | 0.71045 | 0.03225 | -0.29421 | 121.9776 | 121.839 | 122.1042 | 120.7823 | -122.0361 | 121.9505 | 122.0308 | 121.7044 | 120.7859 | -122.4458
859.375 | 122.0993 | -120.9229 | 1.1307 | 1.4211e-13 | -0.0069401 | 0.00081202 | 0.063118 | -0.0079569 | 0.059926 | 0.0016025 | -0.0037407 | -0.0023459 | 0.069151 | 0.023305 | 0.061276 | -120.3693 | -0.11764 | -120.7835 | 1.0685 | 0.92988 | 1.1905 | -120.9238 | -120.593 | -0.11869 | -120.6229 | 1.0368 | 1.1217 | 0.86395 | -121.3288 | -0.000919 | -0.062146 | 0.5535 | 0.1394 | 0.14032 | -0.2008 | 0.05979 | -0.40596 | -0.093841 | 0.32984 | 0.29991 | 0.70587 | -0.008948 | -0.26673 | 121.9914 | 121.8527 | 122.1133 | 120.8052 | -122.0544 | 121.9597 | 122.0446 | 121.7868 | 120.8042 | -122.4595
861.0781 | 122.0764 | -120.8679 | 1.1261 | 1.4211e-13 | -0.0069401 | 0.001453 | 0.062904 | -0.0077431 | 0.060353 | -0.013659 | -0.0035271 | -0.0025597 | 0.068938 | 0.023305 | 0.061062 | -120.3327 | -0.11306 | -120.7468 | 1.0823 | 0.93904 | 1.2134 | -120.8826 | -120.5518 | -0.11411 | -120.5817 | 1.0597 | 1.1446 | 0.91889 | -121.2968 | -0.01464 | -0.043834 | 0.5352 | 0.1211 | 0.13574 | -0.18706 | 0.08726 | -0.42884 | -0.066371 | 0.31612 | 0.28619 | 0.71503 | 0.018522 | -0.20721 | 121.9502 | 121.807 | 122.0813 | 120.7549 | -122.0087 | 121.9276 | 122.0125 | 121.7868 | 120.7538 | -122.4229
862.8125 | 122.0169 | -120.8908 | 1.1444 | 1.4211e-13 | -0.0071537 | 0.0010256 | 0.063118 | -0.0081705 | 0.06014 | 0.0016025 | -0.0037407 | -0.0023459 | 0.069151 | 0.023305 | 0.061276 | -120.3236 | -0.12222 | -120.7331 | 1.0777 | 0.93446 | 1.1996 | -120.8688 | -120.5426 | -0.11411 | -120.5726 | 1.0597 | 1.1355 | 0.87769 | -121.2739 | 0.021985 | -0.066722 | 0.56724 | 0.15772 | 0.13573 | -0.20995 | 0.055214 | -0.38306 | -0.084681 | 0.34816 | 0.31824 | 0.70129 | -0.008945 | -0.26672 | 121.9685 | 121.8253 | 122.0904 | 120.7686 | -122.0132 | 121.9505 | 122.0263 | 121.7685 | 120.7767 | -122.4183
864.5469 | 122.0078 | -120.8725 | 1.1307 | 1.4211e-13 | -0.0069401 | 0.0012394 | 0.062904 | -0.0079569 | 0.06014 | 0.0016025 | -0.0039543 | -0.0023459 | 0.069365 | 0.023092 | 0.060848 | -120.3007 | -0.11764 | -120.7148 | 1.0731 | 0.93446 | 1.195 | -120.8597 | -120.5152 | -0.11869 | -120.5497 | 1.046 | 1.14 | 0.90058 | -121.2601 | 0.012832 | -0.057568 | 0.57183 | 0.15772 | 0.14489 | -0.19622 | 0.064369 | -0.38763 | -0.084684 | 0.35732 | 0.32282 | 0.71045 | 0.009367 | -0.2301 | 121.9456 | 121.807 | 122.0675 | 120.7549 | -121.9903 | 121.9185 | 122.0125 | 121.7731 | 120.7538 | -122.3908
866.2969 | 121.9757 | -120.8633 | 1.1307 | 1.4211e-13 | -0.0069401 | 0.0010256 | 0.062904 | -0.0081705 | 0.06014 | -0.013659 | -0.0039543 | -0.0021323 | 0.069579 | 0.023519 | 0.060848 | -120.2824 | -0.11306 | -120.6965 | 1.0685 | 0.93446 | 1.1905 | -120.823 | -120.5014 | -0.12327 | -120.5405 | 1.0414 | 1.1217 | 0.85479 | -121.2372 | 0.040308 | -0.062146 | 0.58098 | 0.16688 | 0.12657 | -0.19622 | 0.05979 | -0.37389 | -0.089262 | 0.3619 | 0.32282 | 0.69671 | -0.008948 | -0.27588 | 121.9319 | 121.7978 | 122.0538 | 120.7503 | -121.9537 | 121.9048 | 121.9851 | 121.7181 | 120.7401 | -122.3679
868.0312 | 121.9757 | -120.7947 | 1.1261 | 1.4211e-13 | -0.0071537 | 0.0010256 | 0.062904 | -0.0079569 | 0.060353 | 0.0016025 | -0.0035271 | -0.0021323 | 0.069365 | 0.023305 | 0.061276 | -120.2595 | -0.10848 | -120.6736 | 1.064 | 0.93446 | 1.195 | -120.8139 | -120.4831 | -0.11869 | -120.5085 | 1.046 | 1.1217 | 0.90516 | -121.2235 | -0.019198 | -0.062148 | 0.53521 | 0.12111 | 0.1403 | -0.19164 | 0.068946 | -0.42882 | -0.080107 | 0.31155 | 0.28621 | 0.71503 | -0.004371 | -0.22094 | 121.8586 | 121.7291 | 121.9897 | 120.6862 | -121.94 | 121.8407 | 121.9164 | 121.6998 | 120.676 | -122.3496
869.7812 | 121.9162 | -120.8084 | 1.1398 | 1.4211e-13 | -0.0073675 | 0.00081202 | 0.062904 | -0.0079569 | 0.06014 | 0.0016025 | -0.0037407 | -0.0023459 | 0.069365 | 0.023092 | 0.061276 | -120.2274 | -0.12222 | -120.6461 | 1.0731 | 0.94362 | 1.1996 | -120.7864 | -120.4557 | -0.12327 | -120.4856 | 1.0597 | 1.1263 | 0.82274 | -121.2006 | 0.022008 | -0.066724 | 0.58099 | 0.16231 | 0.1403 | -0.19621 | 0.059791 | -0.39219 | -0.080104 | 0.35276 | 0.32283 | 0.71502 | -0.013525 | -0.31709 | 121.8815 | 121.752 | 122.008 | 120.6862 | -121.9262 | 121.8681 | 121.9347 | 121.6312 | 120.6851 | -122.3404
871.4688 | 121.9666 | -120.7214 | 1.1765 | 1.4211e-13 | -0.0071537 | 0.0010256 | 0.062904 | -0.0079569 | 0.06014 | -0.013659 | -0.0039543 | -0.0023459 | 0.069365 | 0.023305 | 0.061062 | -120.1679 | -0.11764 | -120.5774 | 1.1235 | 0.99399 | 1.2454 | -120.6994 | -120.387 | -0.11869 | -120.4169 | 1.1009 | 1.1858 | 0.88684 | -121.1319 | 0.022033 | -0.052983 | 0.55354 | 0.14401 | 0.12198 | -0.18247 | 0.068956 | -0.41048 | -0.075519 | 0.33446 | 0.30454 | 0.71502 | 0.009376 | -0.28961 | 121.8449 | 121.7154 | 121.9668 | 120.6038 | -121.8759 | 121.8224 | 121.9073 | 121.6083 | 120.6027 | -122.3084
873.2188 | 122.0215 | -120.6802 | 1.1124 | 1.4211e-13 | -0.0069401 | 0.0010256 | 0.063118 | -0.0077431 | 0.060567 | -0.006028 | -0.0037407 | -0.0023459 | 0.069579 | 0.023092 | 0.061062 | -120.1679 | -0.12222 | -120.5866 | 1.1006 | 0.96193 | 1.2134 | -120.7315 | -120.3915 | -0.12327 | -120.4261 | 1.0735 | 1.1584 | 0.74491 | -121.1273 | -0.051219 | -0.011787 | 0.51234 | 0.093653 | 0.14487 | -0.15043 | 0.10099 | -0.4471 | -0.038903 | 0.28869 | 0.25418 | 0.70129 | 0.045991 | -0.36746 | 121.7808 | 121.6422 | 121.8936 | 120.558 | -121.8438 | 121.7537 | 121.8386 | 121.4251 | 120.557 | -122.2397
874.9688 | 121.8704 | -120.607 | 1.2863 | 1.4211e-13 | -0.0073675 | 0.0010256 | 0.062904 | -0.0079569 | 0.06014 | 0.0016025 | -0.0039543 | -0.0019187 | 0.069365 | 0.023305 | 0.060848 | -120.0489 | -0.10848 | -120.4584 | 1.2013 | 1.0672 | 1.3232 | -120.6032 | -120.2679 | -0.11869 | -120.2979 | 1.1742 | 1.2545 | 0.87769 | -121.0129 | 0.003749 | -0.085013 | 0.55813 | 0.1486 | 0.14485 | -0.21907 | 0.036929 | -0.40588 | -0.11213 | 0.33907 | 0.30914 | 0.71502 | -0.031808 | -0.40863 | 121.8083 | 121.6742 | 121.9302 | 120.4985 | -121.8896 | 121.7812 | 121.8615 | 121.4847 | 120.4883 | -122.2992
876.6406 | 121.9391 | -120.5978 | 1.2039 | 1.4211e-13 | -0.0071537 | 0.0012394 | 0.062904 | -0.0079569 | 0.060353 | -0.006028 | -0.0039543 | -0.0019187 | 0.069579 | 0.023305 | 0.061276 | -120.0763 | -0.10848 | -120.4767 | 1.1555 | 1.0306 | 1.282 | -120.6216 | -120.2817 | -0.11411 | -120.3207 | 1.1376 | 1.2225 | 0.77696 | -121.0266 | -0.023723 | -0.048399 | 0.52151 | 0.12113 | 0.14486 | -0.1733 | 0.07812 | -0.42877 | -0.066356 | 0.31618 | 0.27709 | 0.70586 | 0.01854 | -0.42696 | 121.7534 | 121.6285 | 121.8799 | 120.4894 | -121.8255 | 121.7354 | 121.8203 | 121.3748 | 120.4837 | -122.2305
878.3906 | 121.9666 | -120.5429 | 1.181 | 1.4211e-13 | -0.0069401 | 0.0012394 | 0.062904 | -0.0081705 | 0.060353 | -0.013659 | -0.0035271 | -0.0021323 | 0.069365 | 0.023733 | 0.061276 | -120.0534 | -0.11306 | -120.4675 | 1.1555 | 1.0169 | 1.2729 | -120.6078 | -120.2771 | -0.11411 | -120.3024 | 1.133 | 1.2087 | 0.88684 | -121.0174 | -0.064917 | -0.025511 | 0.48947 | 0.075359 | 0.14028 | -0.16415 | 0.091851 | -0.47454 | -0.048047 | 0.26583 | 0.24048 | 0.71502 | 0.027692 | -0.29419 | 121.6984 | 121.5598 | 121.8158 | 120.4298 | -121.7889 | 121.6759 | 121.7516 | 121.4297 | 120.4288 | -122.1985
880.1562 | 121.875 | -120.5338 | 1.2222 | 1.4211e-13 | -0.0073675 | 0.00081202 | 0.06269 | -0.0083841 | 0.059712 | 0.0016025 | -0.0037407 | -0.0021323 | 0.069151 | 0.023305 | 0.061276 | -120.0214 | -0.10848 | -120.4355 | 1.1693 | 1.0352 | 1.2958 | -120.5804 | -120.2405 | -0.12784 | -120.2704 | 1.1421 | 1.2316 | 0.91431 | -120.99 | -0.046599 | -0.052975 | 0.51236 | 0.098251 | 0.14485 | -0.18703 | 0.073545 | -0.45622 | -0.080089 | 0.2933 | 0.26337 | 0.7196 | 0.009386 | -0.30792 | 121.703 | 121.5689 | 121.8295 | 120.4253 | -121.8026 | 121.6759 | 121.7654 | 121.4481 | 120.4059 | -122.2122
881.9062 | 121.8018 | -120.5704 | 1.1993 | 1.4211e-13 | -0.0075811 | 0.0010256 | 0.06269 | -0.0079569 | 0.059926 | 0.0016025 | -0.0035271 | -0.0025597 | 0.069151 | 0.023519 | 0.060635 | -120.0397 | -0.11764 | -120.4447 | 1.1326 | 0.99857 | 1.2591 | -120.5895 | -120.2588 | -0.11869 | -120.2979 | 1.1055 | 1.195 | 0.79985 | -121.0037 | -0.019135 | -0.066714 | 0.53067 | 0.12572 | 0.14485 | -0.20078 | 0.059804 | -0.43334 | -0.093829 | 0.31161 | 0.27252 | 0.70586 | -0.004355 | -0.39949 | 121.703 | 121.5689 | 121.8295 | 120.4527 | -121.7889 | 121.6759 | 121.7654 | 121.3702 | 120.4517 | -122.2031
883.5781 | 121.8475 | -120.575 | 1.1581 | 1.4211e-13 | -0.0071537 | 0.00081202 | 0.063118 | -0.0081705 | 0.059926 | 0.0016025 | -0.0039543 | -0.0021323 | 0.068938 | 0.023305 | 0.060848 | -120.0351 | -0.11306 | -120.4492 | 1.1097 | 0.98941 | 1.2408 | -120.5987 | -120.2633 | -0.12327 | -120.2887 | 1.0872 | 1.1812 | 0.79985 | -120.9991 | -0.023716 | -0.048407 | 0.53983 | 0.12571 | 0.14943 | -0.16873 | 0.082689 | -0.42418 | -0.070944 | 0.31161 | 0.28626 | 0.71044 | 0.023108 | -0.35829 | 121.6847 | 121.5644 | 121.8158 | 120.4619 | -121.7568 | 121.6621 | 121.7562 | 121.3748 | 120.4517 | -122.1573
885.3281 | 121.8704 | -120.575 | 1.1169 | 1.4211e-13 | -0.0069401 | 0.0012394 | 0.062904 | -0.0079569 | 0.06014 | 0.0016025 | -0.0037407 | -0.0023459 | 0.069151 | 0.023092 | 0.060635 | -120.0443 | -0.11764 | -120.4584 | 1.0823 | 0.95278 | 1.2042 | -120.6078 | -120.2633 | -0.11869 | -120.2933 | 1.0597 | 1.14 | 0.76322 | -121.0129 | -0.032874 | -0.034678 | 0.53067 | 0.11656 | 0.14943 | -0.16417 | 0.087259 | -0.43792 | -0.057215 | 0.31161 | 0.28168 | 0.7196 | 0.0231 | -0.35372 | 121.6572 | 121.5277 | 121.7792 | 120.4573 | -121.7248 | 121.6347 | 121.715 | 121.3382 | 120.4563 | -122.1298
887.0781 | 121.7697 | -120.5933 | 1.1032 | 1.4211e-13 | -0.0071537 | 0.0010256 | 0.063118 | -0.0079569 | 0.059926 | -0.013659 | -0.0037407 | -0.0023459 | 0.069365 | 0.023733 | 0.060848 | -120.0489 | -0.11764 | -120.463 | 1.064 | 0.93446 | 1.195 | -120.6078 | -120.2725 | -0.11411 | -120.2979 | 1.0414 | 1.1263 | 0.80901 | -121.0174 | -0.014563 | -0.039259 | 0.5444 | 0.13029 | 0.14486 | -0.16875 | 0.091835 | -0.42419 | -0.061796 | 0.32076 | 0.29541 | 0.7196 | 0.023097 | -0.2942 | 121.6572 | 121.5277 | 121.7883 | 120.4756 | -121.711 | 121.6347 | 121.7196 | 121.4023 | 120.4792 | -122.1207
888.8281 | 121.6965 | -120.6024 | 1.0986 | 1.4211e-13 | -0.0073675 | 0.0010256 | 0.06269 | -0.0083841 | 0.060353 | -0.006028 | -0.0037407 | -0.0025597 | 0.069365 | 0.023519 | 0.061062 | -120.0443 | -0.11306 | -120.4538 | 1.0548 | 0.91614 | 1.1767 | -120.5849 | -120.2588 | -0.11869 | -120.2887 | 1.0368 | 1.1126 | 0.76322 | -120.9991 | 0.017487 | -0.043838 | 0.55814 | 0.1486 | 0.13112 | -0.18249 | 0.078097 | -0.39672 | -0.061798 | 0.34365 | 0.31372 | 0.71044 | 0.013938 | -0.33541 | 121.6572 | 121.5186 | 121.7791 | 120.4894 | -121.6836 | 121.6393 | 121.715 | 121.3656 | 120.4837 | -122.0978
890.5469 | 121.6827 | -120.5704 | 1.1169 | 1.4211e-13 | -0.0071537 | 0.0010256 | 0.062904 | -0.0081705 | 0.06014 | -0.013659 | -0.0035271 | -0.0023459 | 0.069579 | 0.023519 | 0.060635 | -120.0168 | -0.10848 | -120.4309 | 1.0685 | 0.92072 | 1.1859 | -120.5804 | -120.2405 | -0.12327 | -120.2704 | 1.0368 | 1.1263 | 0.73575 | -120.9854 | -0.009977 | -0.048413 | 0.55356 | 0.13945 | 0.14943 | -0.19622 | 0.068944 | -0.41502 | -0.080108 | 0.32992 | 0.3 | 0.71502 | 0.009364 | -0.3812 | 121.6389 | 121.4911 | 121.7563 | 120.4619 | -121.6973 | 121.6072 | 121.6967 | 121.3061 | 120.4471 | -122.1023
892.2969 | 121.7194 | -120.5566 | 1.1078 | 1.4211e-13 | -0.0069401 | 0.0010256 | 0.062263 | -0.0081705 | 0.059926 | 0.0016025 | -0.0033135 | -0.0025597 | 0.069151 | 0.023733 | 0.060848 | -120.0122 | -0.11306 | -120.4263 | 1.0502 | 0.91156 | 1.1813 | -120.562 | -120.2359 | -0.12327 | -120.2612 | 1.0323 | 1.108 | 0.65791 | -120.9762 | -0.005395 | -0.057572 | 0.54441 | 0.1303 | 0.13569 | -0.19622 | 0.073521 | -0.4196 | -0.075531 | 0.32077 | 0.29542 | 0.71502 | 0.000205 | -0.44988 | 121.6069 | 121.4682 | 121.7379 | 120.4436 | -121.6698 | 121.5889 | 121.6646 | 121.2146 | 120.4334 | -122.084
893.9688 | 121.6507 | -120.4926 | 1.1581 | 1.4211e-13 | -0.0069401 | 0.0012394 | 0.06269 | -0.0079569 | 0.060353 | -0.013659 | -0.0039543 | -0.0023459 | 0.069151 | 0.023519 | 0.060635 | -119.9527 | -0.11306 | -120.3531 | 1.096 | 0.96651 | 1.2317 | -120.4934 | -120.1672 | -0.12784 | -120.1925 | 1.078 | 1.1675 | 0.84106 | -120.8984 | -0.000798 | -0.062142 | 0.53984 | 0.13946 | 0.14026 | -0.19163 | 0.073531 | -0.40585 | -0.080101 | 0.32536 | 0.30001 | 0.70586 | 0.009372 | -0.31709 | 121.5886 | 121.4591 | 121.7242 | 120.3795 | -121.6515 | 121.5706 | 121.6601 | 121.3336 | 120.3647 | -122.0565
895.7188 | 121.7239 | -120.4971 | 1.1032 | 1.4211e-13 | -0.0069401 | 0.0010256 | 0.06269 | -0.0079569 | 0.059926 | 0.0016025 | -0.0037407 | -0.0023459 | 0.069365 | 0.023519 | 0.060848 | -119.9619 | -0.11764 | -120.3714 | 1.0594 | 0.92072 | 1.1767 | -120.5162 | -120.1901 | -0.11869 | -120.2246 | 1.0231 | 1.1172 | 0.73575 | -120.9305 | -0.019115 | -0.043837 | 0.53526 | 0.12573 | 0.14484 | -0.18249 | 0.07352 | -0.43332 | -0.08011 | 0.30705 | 0.27254 | 0.70586 | 0.01394 | -0.36746 | 121.5565 | 121.4179 | 121.6739 | 120.3795 | -121.6195 | 121.5202 | 121.6143 | 121.2329 | 120.3784 | -122.0337
897.4688 | 121.6965 | -120.4742 | 1.1032 | 1.4211e-13 | -0.0069401 | 0.0010256 | 0.062904 | -0.0077431 | 0.06014 | -0.006028 | -0.0035271 | -0.0023459 | 0.069151 | 0.023519 | 0.060848 | -119.9527 | -0.11764 | -120.3622 | 1.0548 | 0.9253 | 1.1813 | -120.5208 | -120.1763 | -0.12327 | -120.2017 | 1.0277 | 1.1126 | 0.66249 | -120.9213 | -0.046582 | -0.048415 | 0.52153 | 0.112 | 0.15858 | -0.17791 | 0.078099 | -0.44705 | -0.075532 | 0.29789 | 0.27255 | 0.7196 | 0.009361 | -0.44072 | 121.529 | 121.3995 | 121.6556 | 120.3566 | -121.624 | 121.5019 | 121.5868 | 121.1367 | 120.351 | -122.0245
899.2188 | 121.6049 | -120.4834 | 1.1307 | 1.4211e-13 | -0.0071537 | 0.0012394 | 0.062904 | -0.0077431 | 0.059926 | -0.006028 | -0.0035271 | -0.0023459 | 0.069151 | 0.023519 | 0.060635 | -119.9207 | -0.10848 | -120.3256 | 1.0731 | 0.9253 | 1.1996 | -120.4705 | -120.1351 | -0.11869 | -120.1605 | 1.0414 | 1.1263 | 0.70828 | -120.8801 | 0.012941 | -0.057568 | 0.56273 | 0.15778 | 0.14484 | -0.20537 | 0.068947 | -0.39669 | -0.089262 | 0.34826 | 0.32291 | 0.7196 | -0.004369 | -0.4224 | 121.5565 | 121.4087 | 121.683 | 120.3749 | -121.6011 | 121.5248 | 121.6097 | 121.1917 | 120.3647 | -122.0108
900.9688 | 121.5958 | -120.433 | 1.1307 | 1.4211e-13 | -0.0069401 | 0.001453 | 0.062477 | -0.0077431 | 0.06014 | -0.013659 | -0.0037407 | -0.0023459 | 0.069365 | 0.023733 | 0.060848 | -119.8932 | -0.11306 | -120.289 | 1.0731 | 0.9482 | 1.2042 | -120.4338 | -120.1077 | -0.11869 | -120.1422 | 1.0643 | 1.14 | 0.79527 | -120.8526 | -0.000782 | -0.057568 | 0.53985 | 0.14405 | 0.14483 | -0.18248 | 0.073526 | -0.41957 | -0.06637 | 0.32537 | 0.29087 | 0.71044 | 0.009367 | -0.33541 | 121.5062 | 121.3812 | 121.6372 | 120.32 | -121.5645 | 121.4973 | 121.5731 | 121.2283 | 120.3144 | -121.9833
902.6562 | 121.637 | -120.3735 | 1.1765 | 1.4211e-13 | -0.0067265 | 0.001453 | 0.062477 | -0.0079569 | 0.059712 | -0.006028 | -0.0035271 | -0.0021323 | 0.069365 | 0.023305 | 0.060421 | -119.8428 | -0.11764 | -120.2478 | 1.1006 | 0.96193 | 1.2317 | -120.3926 | -120.071 | -0.12784 | -120.0827 | 1.0872 | 1.1721 | 0.84106 | -120.8068 | -0.01908 | -0.075874 | 0.5307 | 0.12574 | 0.14482 | -0.21452 | 0.05522 | -0.43329 | -0.089255 | 0.3025 | 0.29088 | 0.72417 | -0.00436 | -0.3354 | 121.4741 | 121.3355 | 121.6052 | 120.2559 | -121.5691 | 121.4607 | 121.5456 | 121.2146 | 120.2457 | -121.9833
904.3906 | 121.5363 | -120.4102 | 1.1169 | 1.4211e-13 | -0.0071537 | 0.001453 | 0.06269 | -0.0079569 | 0.059712 | -0.006028 | -0.0033135 | -0.0021323 | 0.068938 | 0.023733 | 0.060421 | -119.8703 | -0.10848 | -120.2661 | 1.064 | 0.93446 | 1.195 | -120.4292 | -120.0894 | -0.11869 | -120.1239 | 1.0414 | 1.1263 | 0.69912 | -120.8251 | -0.019091 | -0.052992 | 0.53985 | 0.14405 | 0.16314 | -0.18248 | 0.078102 | -0.41498 | -0.075529 | 0.3208 | 0.2863 | 0.70128 | 0.009364 | -0.41782 | 121.4741 | 121.3446 | 121.6052 | 120.3017 | -121.5462 | 121.4516 | 121.5365 | 121.1093 | 120.2915 | -121.9421
906.1406 | 121.6141 | -120.3873 | 1.0941 | 1.4211e-13 | -0.0071537 | 0.0010256 | 0.062904 | -0.0081705 | 0.059926 | -0.006028 | -0.0039543 | -0.0021323 | 0.068938 | 0.023733 | 0.060635 | -119.8611 | -0.11764 | -120.2707 | 1.0548 | 0.92072 | 1.1813 | -120.4109 | -120.0802 | -0.12327 | -120.1147 | 1.0323 | 1.108 | 0.81816 | -120.8251 | -0.023663 | -0.03926 | 0.52612 | 0.11659 | 0.14025 | -0.17333 | 0.087254 | -0.43787 | -0.061798 | 0.30707 | 0.27257 | 0.71044 | 0.013938 | -0.27589 | 121.4421 | 121.308 | 121.5686 | 120.2696 | -121.505 | 121.4195 | 121.4953 | 121.2054 | 120.264 | -121.9192
907.8906 | 121.6415 | -120.3873 | 1.0712 | 1.4211e-13 | -0.0071537 | 0.0010256 | 0.06269 | -0.0077431 | 0.06014 | -0.013659 | -0.0039543 | -0.0023459 | 0.069151 | 0.023733 | 0.060635 | -119.8474 | -0.11306 | -120.2569 | 1.0502 | 0.91614 | 1.1767 | -120.4109 | -120.071 | -0.11869 | -120.101 | 1.0323 | 1.108 | 0.68538 | -120.8068 | -0.023663 | -0.020951 | 0.53986 | 0.13032 | 0.15398 | -0.15502 | 0.10556 | -0.41956 | -0.03891 | 0.31623 | 0.2863 | 0.70586 | 0.036826 | -0.38578 | 121.4375 | 121.3034 | 121.564 | 120.2742 | -121.4821 | 121.4195 | 121.4953 | 121.0727 | 120.2686 | -121.878
909.5781 | 121.7239 | -0.25177 | 121.5591 | 1.4211e-13 | -0.0062991 | 0.0023076 | 0.063759 | -0.0081705 | 0.059071 | -0.006028 | -0.0024589 | -0.0010641 | 0.070006 | 0.023519 | 0.059139 | -0.099677 | 0.34022 | -0.18238 | 121.5305 | 121.3968 | 121.3284 | -0.30574 | -0.10426 | 0.3346 | -0.21203 | 121.1582 | 121.484 | 120.773 | -0.36562 | -0.05397 | -0.02865 | 0.15209 | 0.069386 | 0.12336 | -0.16234 | -0.23073 | -0.11385 | -0.40091 | 0.14751 | 0.039743 | 0.15359 | -0.075112 | -0.78617 | 121.7823 | 121.6486 | 121.5802 | 0.59199 | -121.8649 | 121.41 | 121.7358 | 121.0247 | 0.58637 | -121.9248
911.3281 | 121.9574 | -0.23804 | 121.6003 | 1.4211e-13 | -0.0062991 | 0.0018804 | 0.063545 | -0.0081705 | 0.058644 | 0.0016025 | -0.0026725 | -0.0014913 | 0.07022 | 0.023733 | 0.059353 | -0.09052 | 0.2807 | -0.16407 | 121.645 | 121.5021 | 121.4383 | -0.29658 | -0.095105 | 0.24303 | -0.19371 | 121.2681 | 121.6031 | 120.8829 | -0.35188 | -0.058545 | 0.04461 | 0.14752 | 0.073966 | 0.13251 | -0.09822 | -0.16204 | -0.11384 | -0.33222 | 0.14293 | 0.044325 | 0.15817 | 0.002733 | -0.71748 | 121.883 | 121.7402 | 121.6763 | 0.51874 | -121.8969 | 121.5062 | 121.8411 | 121.1209 | 0.48107 | -121.9522
913.0781 | 121.8933 | -0.25177 | 121.6827 | 1.4211e-13 | -0.0058717 | 0.0018804 | 0.063759 | -0.0085979 | 0.058644 | -0.006028 | -0.0028861 | -0.0012777 | 0.070647 | 0.023733 | 0.059566 | -0.095099 | 0.24865 | -0.16865 | 121.6999 | 121.5525 | 121.4932 | -0.29658 | -0.095105 | 0.21556 | -0.19829 | 121.3139 | 121.6534 | 120.9332 | -0.3473 | -0.044812 | 0.017154 | 0.15667 | 0.083121 | 0.12793 | -0.13025 | -0.18949 | -0.095531 | -0.36884 | 0.15666 | 0.053479 | 0.14901 | -0.029299 | -0.74952 | 121.9517 | 121.8043 | 121.745 | 0.50042 | -121.9793 | 121.5657 | 121.9052 | 121.185 | 0.46733 | -122.03
914.8281 | 121.9208 | -0.28381 | 121.7102 | 1.4211e-13 | -0.0062991 | 0.002094 | 0.063545 | -0.0081705 | 0.059071 | -0.013659 | -0.0028861 | -0.0010641 | 0.07022 | 0.023305 | 0.059566 | -0.095099 | 0.20286 | -0.15949 | 121.7274 | 121.58 | 121.5299 | -0.29658 | -0.099684 | 0.20182 | -0.20287 | 121.3551 | 121.6855 | 120.9607 | -0.34272 | -0.012769 | 0.017158 | 0.18871 | 0.12432 | 0.13709 | -0.13024 | -0.18033 | -0.05891 | -0.3551 | 0.18413 | 0.080943 | 0.13985 | -0.024715 | -0.74951 | 122.0112 | 121.8638 | 121.8137 | 0.48668 | -122.0068 | 121.6389 | 121.9693 | 121.2445 | 0.48563 | -122.0529
916.5312 | 121.8979 | -0.2655 | 121.7148 | 1.4211e-13 | -0.0067265 | 0.002094 | 0.063759 | -0.0083841 | 0.058644 | 0.0092325 | -0.0028861 | -0.0012777 | 0.070433 | 0.023305 | 0.059566 | -0.09052 | 0.19371 | -0.16407 | 121.7594 | 121.6029 | 121.5619 | -0.292 | -0.099684 | 0.18809 | -0.20745 | 121.378 | 121.7175 | 120.9882 | -0.3473 | -0.026501 | 0.044629 | 0.17498 | 0.10143 | 0.12793 | -0.11192 | -0.15286 | -0.081798 | -0.33678 | 0.16582 | 0.058054 | 0.13985 | 0.002757 | -0.72662 | 122.0249 | 121.8684 | 121.8274 | 0.45921 | -122.0068 | 121.6435 | 121.983 | 121.2537 | 0.45359 | -122.0621
918.2812 | 121.9894 | -0.25177 | 121.6965 | 1.4211e-13 | -0.0060855 | 0.002094 | 0.063545 | -0.0081705 | 0.058858 | -0.013659 | -0.0028861 | -0.0012777 | 0.070006 | 0.023519 | 0.059566 | -0.09052 | 0.17997 | -0.15949 | 121.7823 | 121.6349 | 121.5711 | -0.29658 | -0.090527 | 0.18809 | -0.20287 | 121.4009 | 121.7359 | 121.0019 | -0.3473 | -0.044812 | 0.085832 | 0.16125 | 0.092277 | 0.13709 | -0.061561 | -0.12539 | -0.095531 | -0.29558 | 0.16124 | 0.0489 | 0.14443 | 0.039382 | -0.69457 | 122.0341 | 121.8867 | 121.8229 | 0.43174 | -121.9931 | 121.6527 | 121.9876 | 121.2537 | 0.43986 | -122.0438
920.0156 | 122.049 | -0.27008 | 121.7102 | 1.4211e-13 | -0.0062991 | 0.002094 | 0.063545 | -0.0083841 | 0.058858 | 0.0016025 | -0.0026725 | -0.0012777 | 0.07022 | 0.023733 | 0.05978 | -0.09052 | 0.17081 | -0.15491 | 121.8006 | 121.6578 | 121.6031 | -0.30116 | -0.095105 | 0.17435 | -0.19371 | 121.4238 | 121.7542 | 121.0248 | -0.34272 | -0.03108 | 0.090413 | 0.17956 | 0.11517 | 0.14625 | -0.0524 | -0.10707 | -0.072642 | -0.28642 | 0.17498 | 0.076369 | 0.14901 | 0.043964 | -0.68541 | 122.0707 | 121.9279 | 121.8732 | 0.4409 | -122.0114 | 121.6939 | 122.0243 | 121.2949 | 0.44443 | -122.0529
921.7188 | 122.0306 | -0.26093 | 121.7239 | 1.4211e-13 | -0.0065127 | 0.002094 | 0.064186 | -0.0083841 | 0.058858 | -0.006028 | -0.0026725 | -0.00085026 | 0.070647 | 0.023092 | 0.059353 | -0.095099 | 0.17081 | -0.16865 | 121.8144 | 121.6624 | 121.6169 | -0.28742 | -0.090527 | 0.17435 | -0.20287 | 121.4375 | 121.7587 | 121.0385 | -0.33357 | -0.0265 | 0.090415 | 0.16583 | 0.092276 | 0.11878 | -0.061554 | -0.10707 | -0.07264 | -0.28642 | 0.1704 | 0.058055 | 0.1307 | 0.034809 | -0.68541 | 122.0753 | 121.9233 | 121.8778 | 0.43174 | -122.0114 | 121.6984 | 122.0197 | 121.2995 | 0.43528 | -122.0575
923.4531 | 122.049 | -0.25177 | 121.7651 | 1.4211e-13 | -0.0058717 | 0.0016666 | 0.063759 | -0.0083841 | 0.058858 | -0.006028 | -0.0026725 | -0.0012777 | 0.07022 | 0.023092 | 0.059353 | -0.09052 | 0.17539 | -0.16407 | 121.8235 | 121.6853 | 121.6214 | -0.292 | -0.090527 | 0.16519 | -0.19371 | 121.4467 | 121.7816 | 121.0568 | -0.33814 | -0.040234 | 0.058373 | 0.16125 | 0.087699 | 0.12793 | -0.079858 | -0.14369 | -0.086374 | -0.31846 | 0.16124 | 0.058058 | 0.14443 | 0.016503 | -0.70829 | 122.0753 | 121.937 | 121.8732 | 0.42716 | -122.0571 | 121.6984 | 122.0334 | 121.3086 | 0.41696 | -122.1033
925.2031 | 121.9803 | -0.27924 | 121.7697 | 1.4211e-13 | -0.0062991 | 0.002094 | 0.063973 | -0.0083841 | 0.059285 | 0.0016025 | -0.0026725 | -0.0014913 | 0.070647 | 0.023305 | 0.05978 | -0.085942 | 0.16166 | -0.15034 | 121.8464 | 121.6944 | 121.6489 | -0.292 | -0.085948 | 0.16519 | -0.19371 | 121.4696 | 121.8 | 121.0797 | -0.33357 | -0.012768 | 0.076688 | 0.19329 | 0.1289 | 0.14167 | -0.075277 | -0.12079 | -0.054329 | -0.30014 | 0.19329 | 0.085524 | 0.13985 | 0.030241 | -0.68998 | 122.1256 | 121.9737 | 121.9282 | 0.44089 | -122.0617 | 121.7488 | 122.0792 | 121.359 | 0.44443 | -122.1033
926.9531 | 122.1085 | -0.22888 | 121.7743 | 1.4211e-13 | -0.0060855 | 0.0018804 | 0.063973 | -0.0081705 | 0.058858 | 0.0092325 | -0.0026725 | -0.0010641 | 0.070433 | 0.023733 | 0.059566 | -0.095099 | 0.16166 | -0.14576 | 121.851 | 121.7128 | 121.6627 | -0.28742 | -0.090527 | 0.15604 | -0.19829 | 121.4833 | 121.8137 | 121.0889 | -0.33357 | -0.058543 | 0.076688 | 0.13378 | 0.083124 | 0.14167 | -0.06154 | -0.11164 | -0.10468 | -0.29098 | 0.13836 | 0.030591 | 0.13527 | 0.039399 | -0.6854 | 122.0799 | 121.9416 | 121.8915 | 0.39054 | -122.0617 | 121.7122 | 122.0426 | 121.3178 | 0.38492 | -122.1079
928.6406 | 121.9803 | -0.28381 | 121.8155 | 1.4211e-13 | -0.0060855 | 0.002094 | 0.063973 | -0.0083841 | 0.058858 | 0.0016025 | -0.0024589 | -0.0014913 | 0.070433 | 0.023946 | 0.059566 | -0.095099 | 0.16166 | -0.14576 | 121.8693 | 121.7219 | 121.6718 | -0.28742 | -0.095105 | 0.15604 | -0.18913 | 121.497 | 121.8183 | 121.1026 | -0.32899 | -0.003612 | 0.053802 | 0.18871 | 0.13805 | 0.14167 | -0.093581 | -0.14368 | -0.045173 | -0.31845 | 0.18871 | 0.094679 | 0.13985 | 0.002778 | -0.71286 | 122.1531 | 122.0057 | 121.9556 | 0.44547 | -122.1029 | 121.7809 | 122.1021 | 121.3864 | 0.43985 | -122.1445
930.3906 | 122.0169 | -0.28381 | 121.8201 | 1.4211e-13 | -0.0062991 | 0.0023076 | 0.063759 | -0.0079569 | 0.05843 | -0.006028 | -0.0024589 | -0.0014913 | 0.070861 | 0.023519 | 0.059994 | -0.095099 | 0.15708 | -0.15034 | 121.8785 | 121.7356 | 121.681 | -0.28742 | -0.090527 | 0.15604 | -0.19371 | 121.5016 | 121.8412 | 121.1072 | -0.32899 | -0.003612 | 0.058382 | 0.18871 | 0.13348 | 0.13709 | -0.084421 | -0.1391 | -0.045173 | -0.31845 | 0.19329 | 0.090101 | 0.13527 | 0.021094 | -0.71286 | 122.1623 | 122.0195 | 121.9648 | 0.44089 | -122.1075 | 121.7854 | 122.125 | 121.391 | 0.43985 | -122.1491
932.1562 | 122.0123 | -0.27466 | 121.8384 | 1.4211e-13 | -0.0062991 | 0.002094 | 0.064186 | -0.0085979 | 0.058858 | 0.0016025 | -0.0026725 | -0.0012777 | 0.070433 | 0.023946 | 0.059994 | -0.095099 | 0.1525 | -0.14576 | 121.8785 | 121.7448 | 121.6901 | -0.292 | -0.095105 | 0.15604 | -0.20287 | 121.5062 | 121.8457 | 121.1209 | -0.32441 | -0.017346 | 0.040071 | 0.17956 | 0.1289 | 0.14625 | -0.093574 | -0.14825 | -0.049749 | -0.33218 | 0.17955 | 0.071788 | 0.12154 | 0.007362 | -0.71744 | 122.1531 | 122.0195 | 121.9648 | 0.42716 | -122.1304 | 121.7809 | 122.1204 | 121.3956 | 0.43069 | -122.1628
933.8906 | 122.1268 | -0.24719 | 121.788 | 1.4211e-13 | -0.0060855 | 0.002094 | 0.063759 | -0.0083841 | 0.059071 | -0.006028 | -0.0028861 | -0.0014913 | 0.070433 | 0.023305 | 0.05978 | -0.09052 | 0.1525 | -0.15034 | 121.8922 | 121.7585 | 121.7039 | -0.292 | -0.095105 | 0.16061 | -0.19829 | 121.5108 | 121.8549 | 121.1255 | -0.33814 | -0.044812 | 0.10416 | 0.15667 | 0.096856 | 0.14167 | -0.029484 | -0.084162 | -0.090952 | -0.27725 | 0.15209 | 0.048901 | 0.13985 | 0.066873 | -0.6625 | 122.1394 | 122.0057 | 121.9511 | 0.39969 | -122.08 | 121.758 | 122.1021 | 121.3727 | 0.40781 | -122.1262
935.5938 | 122.0032 | -0.29297 | 121.843 | 1.4211e-13 | -0.0060855 | 0.0018804 | 0.063973 | -0.0085979 | 0.059071 | 0.0016025 | -0.0026725 | -0.0012777 | 0.070433 | 0.023519 | 0.059566 | -0.099677 | 0.1525 | -0.15949 | 121.9059 | 121.7585 | 121.7084 | -0.28742 | -0.099684 | 0.15146 | -0.21203 | 121.5199 | 121.8595 | 121.1301 | -0.33357 | 0.005544 | 0.062964 | 0.19329 | 0.13348 | 0.12793 | -0.084416 | -0.13452 | -0.040596 | -0.32302 | 0.19328 | 0.080942 | 0.12154 | 0.01652 | -0.71286 | 122.1989 | 122.0515 | 122.0014 | 0.44547 | -122.1304 | 121.8129 | 122.1524 | 121.4231 | 0.44442 | -122.1765
937.3438 | 122.0764 | -0.28381 | 121.8658 | 1.4211e-13 | -0.0065127 | 0.002094 | 0.063759 | -0.0081705 | 0.059071 | -0.013659 | -0.0024589 | -0.0012777 | 0.070433 | 0.023519 | 0.059566 | -0.10426 | 0.14334 | -0.15949 | 121.9151 | 121.7631 | 121.7084 | -0.28285 | -0.095105 | 0.15604 | -0.20287 | 121.5245 | 121.8595 | 121.1484 | -0.32899 | 0.000967 | 0.049232 | 0.17956 | 0.12432 | 0.12335 | -0.10272 | -0.1574 | -0.045173 | -0.34133 | 0.18871 | 0.080943 | 0.12612 | -0.006368 | -0.71743 | 122.1989 | 122.0469 | 121.9923 | 0.42716 | -122.1487 | 121.8083 | 122.1433 | 121.4322 | 0.43985 | -122.1948
939.0781 | 122.049 | -0.31128 | 121.8384 | 1.4211e-13 | -0.0062991 | 0.002094 | 0.063973 | -0.0085979 | 0.058644 | -0.013659 | -0.0024589 | -0.0014913 | 0.070433 | 0.023519 | 0.059566 | -0.10426 | 0.1525 | -0.15491 | 121.9013 | 121.7723 | 121.7313 | -0.28742 | -0.10426 | 0.15604 | -0.21661 | 121.5428 | 121.8686 | 121.1393 | -0.33814 | 0.023854 | 0.062963 | 0.20702 | 0.15636 | 0.13251 | -0.066101 | -0.10704 | -0.026865 | -0.29555 | 0.20702 | 0.094673 | 0.12154 | 0.030255 | -0.69912 | 122.2126 | 122.0836 | 122.0426 | 0.46378 | -122.1258 | 121.8541 | 122.1799 | 121.4505 | 0.46731 | -122.1765
940.8281 | 122.0306 | -0.3067 | 121.8246 | 1.4211e-13 | -0.0062991 | 0.0018804 | 0.063973 | -0.0083841 | 0.058644 | 0.0016025 | -0.0026725 | -0.0012777 | 0.070433 | 0.023305 | 0.05978 | -0.11799 | 0.14792 | -0.16865 | 121.9105 | 121.7677 | 121.7176 | -0.30574 | -0.10884 | 0.14688 | -0.22118 | 121.5245 | 121.8549 | 121.1347 | -0.35188 | 0.000962 | 0.085853 | 0.18871 | 0.13805 | 0.13709 | -0.056947 | -0.10705 | -0.045178 | -0.30013 | 0.19786 | 0.085517 | 0.1307 | 0.030252 | -0.68997 | 122.2172 | 122.0744 | 122.0243 | 0.45462 | -122.1304 | 121.8312 | 122.1616 | 121.4414 | 0.45358 | -122.1765
942.5156 | 122.049 | -0.32044 | 121.8384 | 1.4211e-13 | -0.0062991 | 0.002094 | 0.063545 | -0.0085979 | 0.058858 | -0.006028 | -0.0026725 | -0.0012777 | 0.07022 | 0.023519 | 0.059994 | -0.12257 | 0.1525 | -0.18238 | 121.9059 | 121.7723 | 121.7222 | -0.31032 | -0.12716 | 0.15146 | -0.23492 | 121.5245 | 121.8595 | 121.1301 | -0.35188 | 0.010116 | 0.067542 | 0.19787 | 0.13805 | 0.12794 | -0.066101 | -0.1162 | -0.031445 | -0.31387 | 0.19328 | 0.085514 | 0.11696 | 0.021098 | -0.70828 | 122.2264 | 122.0927 | 122.0426 | 0.47293 | -122.1487 | 121.8449 | 122.1799 | 121.4505 | 0.47189 | -122.1903
944.2656 | 122.0764 | -0.31128 | 121.8384 | 1.4211e-13 | -0.0062991 | 0.0018804 | 0.063973 | -0.0083841 | 0.058858 | -0.006028 | -0.0028861 | -0.0014913 | 0.07022 | 0.023733 | 0.059353 | -0.12715 | 0.15708 | -0.18238 | 121.9059 | 121.7677 | 121.7222 | -0.31948 | -0.12716 | 0.15146 | -0.23492 | 121.5383 | 121.8595 | 121.1255 | -0.35646 | -0.008198 | 0.067542 | 0.18413 | 0.12889 | 0.13709 | -0.07068 | -0.1162 | -0.04518 | -0.30013 | 0.18412 | 0.076358 | 0.12154 | 0.021098 | -0.71286 | 122.2172 | 122.079 | 122.0335 | 0.46836 | -122.1579 | 121.8495 | 122.1708 | 121.4368 | 0.46274 | -122.1948
946.0156 | 122.1405 | -0.28839 | 121.8063 | 1.4211e-13 | -0.0062991 | 0.002094 | 0.063973 | -0.0085979 | 0.058858 | -0.006028 | -0.0026725 | -0.0012777 | 0.070861 | 0.023519 | 0.05978 | -0.1363 | 0.1525 | -0.19612 | 121.9059 | 121.7677 | 121.7176 | -0.33321 | -0.13173 | 0.15146 | -0.25324 | 121.5291 | 121.8549 | 121.1164 | -0.3702 | -0.044823 | 0.099586 | 0.15209 | 0.092272 | 0.1371 | -0.038636 | -0.088736 | -0.081805 | -0.27724 | 0.15666 | 0.035155 | 0.11696 | 0.048563 | -0.68997 | 122.1943 | 122.0561 | 122.006 | 0.44089 | -122.1395 | 121.8175 | 122.1433 | 121.4048 | 0.43985 | -122.1765
947.7031 | 122.2183 | -0.30212 | 121.7651 | 1.4211e-13 | -0.0060855 | 0.0018804 | 0.063973 | -0.0083841 | 0.059071 | -0.006028 | -0.0022453 | -0.0012777 | 0.070647 | 0.023733 | 0.059353 | -0.15462 | 0.14792 | -0.2007 | 121.8922 | 121.7631 | 121.7176 | -0.33779 | -0.14089 | 0.15146 | -0.24866 | 121.5154 | 121.8549 | 121.1301 | -0.3702 | -0.035669 | 0.12705 | 0.14751 | 0.10143 | 0.1371 | -0.002017 | -0.047538 | -0.068072 | -0.24978 | 0.16123 | 0.053467 | 0.12154 | 0.089761 | -0.63504 | 122.1943 | 122.0652 | 122.0197 | 0.45005 | -122.1029 | 121.8175 | 122.157 | 121.4322 | 0.45358 | -122.1353
949.4531 | 122.0535 | -0.35248 | 121.8475 | 1.4211e-13 | -0.0062991 | 0.0023076 | 0.063759 | -0.0085979 | 0.058644 | 0.0016025 | -0.0024589 | -0.0014913 | 0.070647 | 0.023733 | 0.059566 | -0.15462 | 0.14792 | -0.20985 | 121.8922 | 121.7631 | 121.713 | -0.33779 | -0.14547 | 0.15146 | -0.26239 | 121.5245 | 121.8549 | 121.1255 | -0.37935 | 0.014685 | 0.044651 | 0.19786 | 0.14262 | 0.12794 | -0.084414 | -0.13451 | -0.026875 | -0.32302 | 0.20701 | 0.090085 | 0.11696 | 0.007364 | -0.72201 | 122.2447 | 122.1156 | 122.0655 | 0.5004 | -122.1853 | 121.877 | 122.2074 | 121.478 | 0.50393 | -122.2269
951.2031 | 122.168 | -0.3067 | 121.8475 | 1.4211e-13 | -0.0058717 | 0.002094 | 0.063973 | -0.0085979 | 0.058644 | -0.006028 | -0.0026725 | -0.00085026 | 0.070647 | 0.023733 | 0.059566 | -0.15462 | 0.14334 | -0.20528 | 121.9151 | 121.7677 | 121.7313 | -0.33321 | -0.15005 | 0.15146 | -0.26697 | 121.5337 | 121.8641 | 121.1347 | -0.37477 | -0.026512 | 0.067543 | 0.15208 | 0.10143 | 0.12794 | -0.079835 | -0.1162 | -0.068072 | -0.31386 | 0.15665 | 0.03973 | 0.1078 | 0.016521 | -0.71285 | 122.2218 | 122.0744 | 122.038 | 0.45004 | -122.1807 | 121.8404 | 122.1708 | 121.4414 | 0.45816 | -122.2223
952.9531 | 122.2137 | -0.31128 | 121.7972 | 1.4211e-13 | -0.0058717 | 0.0016666 | 0.063759 | -0.0083841 | 0.059285 | -0.006028 | -0.0026725 | -0.0014913 | 0.070433 | 0.023733 | 0.059353 | -0.15004 | 0.14792 | -0.2007 | 121.9151 | 121.786 | 121.7359 | -0.33321 | -0.14547 | 0.15146 | -0.26239 | 121.5474 | 121.8778 | 121.1438 | -0.3702 | -0.021935 | 0.1179 | 0.16124 | 0.11058 | 0.13252 | -0.011165 | -0.061267 | -0.058917 | -0.24977 | 0.16581 | 0.048886 | 0.1078 | 0.080611 | -0.65334 | 122.2264 | 122.0973 | 122.0472 | 0.4592 | -122.1304 | 121.8587 | 122.1891 | 121.4551 | 0.46274 | -122.1674
954.6406 | 122.1497 | -0.32501 | 121.8292 | 1.4211e-13 | -0.0065127 | 0.0023076 | 0.063973 | -0.0083841 | 0.058644 | 0.0016025 | -0.0028861 | -0.0019187 | 0.070647 | 0.02416 | 0.059353 | -0.15004 | 0.14792 | -0.20528 | 121.9105 | 121.7723 | 121.7359 | -0.33321 | -0.14547 | 0.15604 | -0.25324 | 121.5428 | 121.8824 | 121.1438 | -0.37477 | -0.008202 | 0.081275 | 0.17497 | 0.11974 | 0.12794 | -0.056946 | -0.093311 | -0.049762 | -0.2864 | 0.17954 | 0.071776 | 0.12154 | 0.053146 | -0.68539 | 122.2355 | 122.0973 | 122.0609 | 0.47293 | -122.1624 | 121.8678 | 122.2074 | 121.4688 | 0.48105 | -122.204
956.4062 | 122.1451 | -0.34332 | 121.8567 | 1.4211e-13 | -0.0062991 | 0.0018804 | 0.063973 | -0.0083841 | 0.059285 | 0.0016025 | -0.0024589 | -0.0012777 | 0.070433 | 0.023519 | 0.05978 | -0.15004 | 0.14334 | -0.20528 | 121.9242 | 121.786 | 121.7405 | -0.33779 | -0.14089 | 0.15146 | -0.25781 | 121.5383 | 121.8869 | 121.153 | -0.3702 | 0.00553 | 0.067545 | 0.19328 | 0.13805 | 0.13252 | -0.070674 | -0.1162 | -0.026873 | -0.31844 | 0.20243 | 0.085509 | 0.11238 | 0.030259 | -0.70369 | 122.2676 | 122.1293 | 122.0838 | 0.48667 | -122.1945 | 121.8816 | 122.2303 | 121.4963 | 0.49478 | -122.2269
958.1562 | 122.2275 | -0.31128 | 121.8338 | 1.4211e-13 | -0.0065127 | 0.002094 | 0.063759 | -0.0085979 | 0.058858 | -0.006028 | -0.0026725 | -0.0014913 | 0.070433 | 0.023733 | 0.059566 | -0.15004 | 0.14334 | -0.2007 | 121.9242 | 121.7906 | 121.7588 | -0.33321 | -0.15005 | 0.15146 | -0.26239 | 121.552 | 121.8869 | 121.153 | -0.37477 | -0.021935 | 0.090433 | 0.16124 | 0.11058 | 0.13252 | -0.043207 | -0.074995 | -0.063495 | -0.28182 | 0.16123 | 0.048886 | 0.11238 | 0.053147 | -0.68081 | 122.2355 | 122.1019 | 122.0701 | 0.45462 | -122.167 | 121.8633 | 122.1982 | 121.4643 | 0.46274 | -122.2086
959.8906 | 122.2229 | -0.29755 | 121.8292 | 1.4211e-13 | -0.0062991 | 0.002094 | 0.063973 | -0.0081705 | 0.059071 | -0.013659 | -0.0026725 | -0.0012777 | 0.070861 | 0.023733 | 0.059353 | -0.15004 | 0.14792 | -0.19612 | 121.938 | 121.7998 | 121.7542 | -0.33321 | -0.14547 | 0.14688 | -0.26239 | 121.5566 | 121.8915 | 121.1576 | -0.38393 | -0.035668 | 0.10874 | 0.14751 | 0.10143 | 0.1371 | -0.029472 | -0.074997 | -0.086386 | -0.27266 | 0.15207 | 0.035153 | 0.12154 | 0.062303 | -0.67165 | 122.2355 | 122.0973 | 122.0518 | 0.44547 | -122.1624 | 121.8541 | 122.1891 | 121.4551 | 0.44442 | -122.2132
961.6406 | 122.2275 | -0.3067 | 121.8613 | 1.4211e-13 | -0.0060855 | 0.0023076 | 0.063759 | -0.0083841 | 0.058644 | 0.0016025 | -0.0024589 | -0.0017051 | 0.070647 | 0.023733 | 0.059566 | -0.15004 | 0.14334 | -0.20528 | 121.938 | 121.8089 | 121.7725 | -0.32406 | -0.14089 | 0.15146 | -0.26239 | 121.5657 | 121.9098 | 121.1667 | -0.3702 | -0.017354 | 0.076702 | 0.15666 | 0.10143 | 0.11878 | -0.052357 | -0.088725 | -0.063494 | -0.29555 | 0.16581 | 0.044309 | 0.1078 | 0.048574 | -0.69454 | 122.2447 | 122.1156 | 122.0792 | 0.45004 | -122.1853 | 121.8724 | 122.2165 | 121.4734 | 0.45816 | -122.2315
963.3906 | 122.2321 | -0.30212 | 121.8384 | 1.4211e-13 | -0.0062991 | 0.0025214 | 0.063973 | -0.0083841 | 0.059071 | 0.0016025 | -0.0024589 | -0.0010641 | 0.070433 | 0.023733 | 0.059353 | -0.14546 | 0.14792 | -0.19612 | 121.9563 | 121.8181 | 121.7771 | -0.32864 | -0.14089 | 0.15604 | -0.24408 | 121.5795 | 121.9098 | 121.1942 | -0.37477 | -0.026511 | 0.1179 | 0.15666 | 0.10601 | 0.13252 | -0.020312 | -0.061259 | -0.07265 | -0.25892 | 0.16123 | 0.058046 | 0.1307 | 0.071462 | -0.64418 | 122.2584 | 122.1202 | 122.0792 | 0.45005 | -122.167 | 121.8816 | 122.212 | 121.4963 | 0.45816 | -122.2132
965.0781 | 122.1588 | -0.32044 | 121.8796 | 1.4211e-13 | -0.0067265 | 0.0016666 | 0.063973 | -0.0083841 | 0.059071 | -0.006028 | -0.0026725 | -0.0012777 | 0.070647 | 0.023733 | 0.059566 | -0.15004 | 0.1525 | -0.2007 | 121.9517 | 121.8272 | 121.7817 | -0.32406 | -0.13631 | 0.14688 | -0.24408 | 121.584 | 121.9144 | 121.185 | -0.3702 | -0.003621 | 0.072126 | 0.1704 | 0.11974 | 0.12336 | -0.052353 | -0.097879 | -0.049761 | -0.29554 | 0.18412 | 0.076357 | 0.12612 | 0.034842 | -0.69453 | 122.2721 | 122.1477 | 122.1021 | 0.47293 | -122.2036 | 121.9045 | 122.2349 | 121.5055 | 0.46731 | -122.2498
966.8594 | 122.1359 | -0.34332 | 121.8704 | 1.4211e-13 | -0.0060855 | 0.002094 | 0.064186 | -0.0090251 | 0.059071 | 0.0092325 | -0.0024589 | -0.0012777 | 0.070433 | 0.023946 | 0.059566 | -0.14546 | 0.14334 | -0.19154 | 121.9563 | 121.8226 | 121.7909 | -0.32864 | -0.14547 | 0.14688 | -0.24866 | 121.5795 | 121.919 | 121.1759 | -0.36562 | 0.014688 | 0.085861 | 0.19786 | 0.15178 | 0.13709 | -0.047776 | -0.079566 | -0.022294 | -0.29097 | 0.19785 | 0.094666 | 0.11696 | 0.048577 | -0.69453 | 122.2996 | 122.166 | 122.1342 | 0.48667 | -122.1991 | 121.9228 | 122.2623 | 121.5192 | 0.4902 | -122.236
968.5469 | 122.2595 | -0.30212 | 121.8521 | 1.4211e-13 | -0.0062991 | 0.0018804 | 0.064186 | -0.0083841 | 0.059499 | -0.006028 | -0.0024589 | -0.0014913 | 0.070647 | 0.023733 | 0.05978 | -0.1363 | 0.1525 | -0.19612 | 121.9609 | 121.8318 | 121.7954 | -0.31948 | -0.13631 | 0.15146 | -0.24408 | 121.5932 | 121.9373 | 121.1896 | -0.37477 | -0.017353 | 0.10875 | 0.16582 | 0.10601 | 0.12336 | -0.020308 | -0.056677 | -0.07265 | -0.25892 | 0.16581 | 0.058046 | 0.1307 | 0.085201 | -0.66249 | 122.263 | 122.1339 | 122.0976 | 0.45462 | -122.1716 | 121.8953 | 122.2394 | 121.4917 | 0.45358 | -122.2269
970.2969 | 122.1771 | -0.32044 | 121.9162 | 1.4211e-13 | -0.0062991 | 0.002094 | 0.0644 | -0.0085979 | 0.059071 | -0.006028 | -0.0026725 | -0.0012777 | 0.070433 | 0.023946 | 0.05978 | -0.15004 | 0.15708 | -0.19612 | 121.9654 | 121.8318 | 121.7863 | -0.32864 | -0.14547 | 0.15604 | -0.24408 | 121.584 | 121.9373 | 121.2034 | -0.3702 | -0.0082 | 0.049241 | 0.1704 | 0.12432 | 0.13252 | -0.084395 | -0.12992 | -0.049761 | -0.33216 | 0.17496 | 0.076357 | 0.12612 | 0.021114 | -0.71284 | 122.2859 | 122.1522 | 122.1067 | 0.47751 | -122.2448 | 121.9045 | 122.2577 | 121.5238 | 0.47647 | -122.2864
972.0469 | 122.1405 | -0.3479 | 121.9025 | 1.4211e-13 | -0.0067265 | 0.002094 | 0.063973 | -0.0083841 | 0.059071 | -0.006028 | -0.0026725 | -0.0012777 | 0.070433 | 0.023519 | 0.059353 | -0.14546 | 0.14334 | -0.20528 | 121.9609 | 121.8364 | 121.7909 | -0.32864 | -0.13631 | 0.15146 | -0.26239 | 121.5886 | 121.9282 | 121.2034 | -0.36562 | 0.019265 | 0.058395 | 0.20244 | 0.14262 | 0.12336 | -0.066083 | -0.11161 | -0.017717 | -0.31385 | 0.21159 | 0.085507 | 0.10322 | 0.02569 | -0.69911 | 122.3088 | 122.1843 | 122.1388 | 0.49124 | -122.2311 | 121.9365 | 122.2761 | 121.5513 | 0.49936 | -122.2681
973.8125 | 122.1954 | -0.33417 | 121.9208 | 1.4211e-13 | -0.0062991 | 0.0018804 | 0.063759 | -0.0088115 | 0.059071 | -0.006028 | -0.0026725 | -0.0012777 | 0.070647 | 0.023519 | 0.059353 | -0.14546 | 0.13876 | -0.19612 | 121.97 | 121.8364 | 121.8 | -0.31948 | -0.14547 | 0.14688 | -0.26239 | 121.5978 | 121.9373 | 121.2125 | -0.36562 | 0.01469 | 0.049242 | 0.18871 | 0.13805 | 0.12336 | -0.084393 | -0.12076 | -0.03145 | -0.32301 | 0.1887 | 0.071774 | 0.10322 | 0.016537 | -0.70826 | 122.3042 | 122.1705 | 122.1342 | 0.47293 | -122.2403 | 121.9319 | 122.2715 | 121.5467 | 0.48105 | -122.2864
975.5156 | 122.287 | -0.29297 | 121.8658 | 1.4211e-13 | -0.0062991 | 0.0023076 | 0.063973 | -0.0085979 | 0.059071 | 0.0016025 | -0.0024589 | -0.0014913 | 0.070647 | 0.023946 | 0.059566 | -0.15004 | 0.14334 | -0.2007 | 121.9792 | 121.841 | 121.8092 | -0.33321 | -0.15005 | 0.15146 | -0.25781 | 121.6023 | 121.9465 | 121.2079 | -0.3702 | -0.040245 | 0.11333 | 0.14293 | 0.092272 | 0.13252 | -0.024883 | -0.056674 | -0.077227 | -0.2635 | 0.14292 | 0.035155 | 0.11238 | 0.080625 | -0.65791 | 122.2721 | 122.1339 | 122.1021 | 0.43631 | -122.1991 | 121.8953 | 122.2394 | 121.5009 | 0.44442 | -122.236
977.2656 | 122.2641 | -0.29755 | 121.8704 | 1.4211e-13 | -0.0065127 | 0.0018804 | 0.063973 | -0.0085979 | 0.058858 | -0.006028 | -0.0028861 | -0.0014913 | 0.070861 | 0.023733 | 0.059353 | -0.15004 | 0.14792 | -0.20528 | 121.9792 | 121.8455 | 121.8046 | -0.33321 | -0.14547 | 0.15604 | -0.26239 | 121.5978 | 121.9419 | 121.2034 | -0.3702 | -0.035668 | 0.10875 | 0.14751 | 0.092271 | 0.12794 | -0.024881 | -0.06583 | -0.07265 | -0.27265 | 0.15207 | 0.035153 | 0.1078 | 0.07147 | -0.66706 | 122.2767 | 122.1431 | 122.1021 | 0.44547 | -122.2036 | 121.8953 | 122.2394 | 121.5009 | 0.45358 | -122.2406
979 | 122.168 | -0.34332 | 121.9162 | 1.4211e-13 | -0.0065127 | 0.0018804 | 0.063973 | -0.0083841 | 0.059285 | 0.0092325 | -0.0024589 | -0.0014913 | 0.070647 | 0.023733 | 0.059353 | -0.15462 | 0.1525 | -0.20528 | 121.9746 | 121.8455 | 121.8 | -0.32406 | -0.15463 | 0.15146 | -0.25781 | 121.5978 | 121.9419 | 121.1942 | -0.3702 | 0.019267 | 0.058397 | 0.1887 | 0.13805 | 0.11878 | -0.070658 | -0.11619 | -0.026873 | -0.31843 | 0.18869 | 0.085509 | 0.11238 | 0.025693 | -0.722 | 122.3179 | 122.1889 | 122.1433 | 0.49582 | -122.2403 | 121.9411 | 122.2852 | 121.5375 | 0.49478 | -122.2864
980.6875 | 122.2687 | -0.29297 | 121.875 | 1.4211e-13 | -0.0065127 | 0.0018804 | 0.063759 | -0.0083841 | 0.059071 | -0.006028 | -0.0028861 | -0.0012777 | 0.07022 | 0.02416 | 0.059353 | -0.15462 | 0.1525 | -0.2007 | 121.9883 | 121.8593 | 121.8229 | -0.33779 | -0.14547 | 0.16061 | -0.26239 | 121.6069 | 121.9465 | 121.2537 | -0.37477 | -0.044824 | 0.11333 | 0.13835 | 0.092272 | 0.1371 | -0.015722 | -0.052094 | -0.081805 | -0.26807 | 0.1475 | 0.030576 | 0.11238 | 0.07147 | -0.62128 | 122.2813 | 122.1522 | 122.1159 | 0.44547 | -122.2128 | 121.8999 | 122.2394 | 121.5467 | 0.45358 | -122.2498
982.4531 | 122.3007 | -0.31128 | 121.8796 | 1.4211e-13 | -0.0065127 | 0.002094 | 0.063759 | -0.0085979 | 0.059071 | -0.006028 | -0.0022453 | -0.0012777 | 0.070433 | 0.023733 | 0.059353 | -0.15004 | 0.14334 | -0.2007 | 121.9883 | 121.8547 | 121.8275 | -0.32406 | -0.14547 | 0.14688 | -0.25324 | 121.6252 | 121.9602 | 121.2125 | -0.3702 | -0.012777 | 0.10875 | 0.16124 | 0.11058 | 0.12336 | -0.024879 | -0.052093 | -0.058917 | -0.25434 | 0.16581 | 0.058043 | 0.11696 | 0.080628 | -0.66706 | 122.2996 | 122.166 | 122.1388 | 0.45462 | -122.2036 | 121.9365 | 122.2715 | 121.5238 | 0.45816 | -122.2498
984.1875 | 122.1451 | -0.35248 | 121.9208 | 1.4211e-13 | -0.0062991 | 0.0018804 | 0.064186 | -0.0085979 | 0.058858 | -0.006028 | -0.0024589 | -0.0012777 | 0.07022 | 0.023946 | 0.059566 | -0.14546 | 0.14792 | -0.20528 | 121.9929 | 121.873 | 121.8321 | -0.33321 | -0.15005 | 0.15146 | -0.25781 | 121.6207 | 121.9648 | 121.2217 | -0.3702 | 0.019264 | 0.072134 | 0.20702 | 0.1472 | 0.12794 | -0.047761 | -0.088712 | -0.017718 | -0.30011 | 0.20243 | 0.094664 | 0.11238 | 0.044009 | -0.6991 | 122.3454 | 122.2255 | 122.1845 | 0.5004 | -122.254 | 121.9731 | 122.3173 | 121.5742 | 0.50393 | -122.291
985.9375 | 122.2046 | -0.34332 | 121.9162 | 1.4211e-13 | -0.0065127 | 0.002094 | 0.063759 | -0.0085979 | 0.059071 | 0.0016025 | -0.0024589 | -0.0012777 | 0.070433 | 0.023946 | 0.059139 | -0.15462 | 0.14334 | -0.20528 | 121.9975 | 121.8684 | 121.8366 | -0.32406 | -0.14547 | 0.14688 | -0.25324 | 121.6298 | 121.9648 | 121.2171 | -0.36562 | 0.019267 | 0.081289 | 0.1887 | 0.13805 | 0.11878 | -0.047763 | -0.079557 | -0.022294 | -0.28638 | 0.19785 | 0.090087 | 0.11238 | 0.048586 | -0.6991 | 122.3408 | 122.2118 | 122.18 | 0.48667 | -122.2403 | 121.9731 | 122.3081 | 121.5604 | 0.4902 | -122.2818
987.6406 | 122.287 | -0.28839 | 121.8796 | 1.4211e-13 | -0.0060855 | 0.002094 | 0.063973 | -0.0085979 | 0.059071 | 0.0016025 | -0.0026725 | -0.0012777 | 0.070433 | 0.023946 | 0.059353 | -0.15462 | 0.14792 | -0.20985 | 122.0021 | 121.8639 | 121.8366 | -0.32864 | -0.15463 | 0.15604 | -0.26697 | 121.6252 | 121.9694 | 121.2171 | -0.37477 | -0.040244 | 0.12249 | 0.13377 | 0.078537 | 0.11878 | -0.015721 | -0.042936 | -0.086383 | -0.25434 | 0.13376 | 0.021419 | 0.1078 | 0.089785 | -0.66248 | 122.2905 | 122.1522 | 122.125 | 0.43631 | -122.2082 | 121.9136 | 122.2578 | 121.5055 | 0.44443 | -122.2544
989.4062 | 122.2137 | -0.33875 | 121.9116 | 1.4211e-13 | -0.0065127 | 0.002094 | 0.063759 | -0.0083841 | 0.059285 | 0.0016025 | -0.0024589 | -0.0017051 | 0.070433 | 0.023733 | 0.058925 | -0.16377 | 0.1525 | -0.20528 | 121.9975 | 121.8639 | 121.8321 | -0.32406 | -0.15005 | 0.14688 | -0.26697 | 121.6207 | 121.9556 | 121.2217 | -0.3702 | 0.014689 | 0.085867 | 0.17497 | 0.13347 | 0.11878 | -0.047764 | -0.079557 | -0.031451 | -0.29096 | 0.1887 | 0.071773 | 0.10322 | 0.044006 | -0.68995 | 122.3362 | 122.2026 | 122.1708 | 0.49125 | -122.2357 | 121.9594 | 122.2944 | 121.5604 | 0.48562 | -122.2818
991.0938 | 122.2733 | -0.33875 | 121.8796 | 1.4211e-13 | -0.0062991 | 0.002094 | 0.064186 | -0.0083841 | 0.059285 | 0.0016025 | -0.0022453 | -0.0017051 | 0.070433 | 0.023946 | 0.059566 | -0.16377 | 0.1525 | -0.21443 | 121.9929 | 121.8684 | 121.8366 | -0.33779 | -0.16379 | 0.15604 | -0.26239 | 121.6298 | 121.9602 | 121.2217 | -0.3702 | 0.000952 | 0.11333 | 0.17497 | 0.12431 | 0.12336 | -0.011142 | -0.042936 | -0.031451 | -0.24976 | 0.17496 | 0.076352 | 0.1078 | 0.080628 | -0.6579 | 122.3317 | 122.2072 | 122.1754 | 0.49125 | -122.2174 | 121.9686 | 122.299 | 121.5604 | 0.49478 | -122.2498
992.875 | 122.1542 | -0.35706 | 121.9345 | 1.4211e-13 | -0.0062991 | 0.002094 | 0.063973 | -0.0085979 | 0.059071 | 0.0016025 | -0.0024589 | -0.0012777 | 0.070647 | 0.02416 | 0.059139 | -0.15004 | 0.14334 | -0.20985 | 121.9975 | 121.8776 | 121.8412 | -0.33321 | -0.15921 | 0.16061 | -0.26697 | 121.6344 | 121.9602 | 121.2675 | -0.3702 | 0.023842 | 0.062979 | 0.20702 | 0.1472 | 0.12336 | -0.056915 | -0.093288 | -0.01314 | -0.30011 | 0.19785 | 0.090084 | 0.10322 | 0.025697 | -0.66705 | 122.3545 | 122.2347 | 122.1983 | 0.5004 | -122.2677 | 121.9915 | 122.3173 | 121.6245 | 0.51767 | -122.3047
994.5625 | 122.1909 | -0.36621 | 121.9208 | 1.4211e-13 | -0.0060855 | 0.0018804 | 0.063973 | -0.0085979 | 0.059285 | 0.0092325 | -0.0024589 | -0.0012777 | 0.070647 | 0.023733 | 0.059139 | -0.1592 | 0.14792 | -0.20985 | 121.9975 | 121.873 | 121.8458 | -0.33321 | -0.15921 | 0.15604 | -0.26239 | 121.6298 | 121.9694 | 121.2583 | -0.37935 | 0.032997 | 0.076712 | 0.20702 | 0.15636 | 0.12336 | -0.047761 | -0.074976 | -0.013142 | -0.29096 | 0.207 | 0.10382 | 0.11696 | 0.048587 | -0.66247 | 122.3637 | 122.2392 | 122.212 | 0.51413 | -122.254 | 121.996 | 122.3356 | 121.6245 | 0.52225 | -122.3001
996.3281 | 122.3145 | -0.29755 | 121.8842 | 1.4211e-13 | -0.0062991 | 0.0018804 | 0.063973 | -0.0085979 | 0.058858 | -0.006028 | -0.0020317 | -0.0012777 | 0.070647 | 0.02416 | 0.059353 | -0.14546 | 0.14334 | -0.21443 | 122.0066 | 121.8822 | 121.8458 | -0.33779 | -0.15463 | 0.15604 | -0.26697 | 121.6344 | 121.9739 | 121.2491 | -0.37935 | -0.040247 | 0.12249 | 0.15208 | 0.083114 | 0.12336 | -0.001983 | -0.038355 | -0.081807 | -0.24976 | 0.14292 | 0.030574 | 0.11238 | 0.089787 | -0.63501 | 122.3042 | 122.1797 | 122.1433 | 0.44089 | -122.2219 | 121.9319 | 122.2715 | 121.5467 | 0.45358 | -122.2635
998.0781 | 122.168 | -0.34332 | 121.9574 | 1.4211e-13 | -0.0065127 | 0.0025214 | 0.063973 | -0.0085979 | 0.059071 | -0.013659 | -0.0028861 | -0.0012777 | 0.070433 | 0.023733 | 0.059566 | -0.15462 | 0.14792 | -0.20985 | 122.0112 | 121.8822 | 121.855 | -0.34237 | -0.15005 | 0.15604 | -0.26239 | 121.6344 | 121.9739 | 121.24 | -0.37477 | 0.000951 | 0.053827 | 0.1887 | 0.13347 | 0.13252 | -0.075225 | -0.10244 | -0.031451 | -0.323 | 0.19327 | 0.08093 | 0.11238 | 0.016545 | -0.71741 | 122.3545 | 122.2255 | 122.1983 | 0.49124 | -122.2998 | 121.9777 | 122.3173 | 121.5833 | 0.49936 | -122.3322
999.8438 | 122.287 | -0.3067 | 121.8933 | 1.4211e-13 | -0.0062991 | 0.0016666 | 0.063545 | -0.0090251 | 0.059285 | -0.006028 | -0.0024589 | -0.0012777 | 0.070861 | 0.023946 | 0.059353 | -0.15462 | 0.15708 | -0.2007 | 122.0158 | 121.8959 | 121.8687 | -0.33321 | -0.14547 | 0.15604 | -0.25781 | 121.6481 | 121.9831 | 121.2537 | -0.37477 | -0.026512 | 0.12249 | 0.15208 | 0.106 | 0.13252 | 0.002598 | -0.024618 | -0.068072 | -0.24518 | 0.16123 | 0.048888 | 0.11696 | 0.089788 | -0.63959 | 122.3225 | 122.2026 | 122.1754 | 0.46378 | -122.2265 | 121.9548 | 122.2898 | 121.5604 | 0.46274 | -122.2681
1001.5469 | 122.2961 | -0.33875 | 121.8979 | 1.4211e-13 | -0.0067265 | 0.0018804 | 0.064186 | -0.0085979 | 0.059071 | -0.006028 | -0.0026725 | -0.0012777 | 0.070861 | 0.02416 | 0.059139 | -0.1592 | 0.1525 | -0.21901 | 122.0112 | 121.8913 | 121.855 | -0.33321 | -0.15463 | 0.16061 | -0.27155 | 121.6436 | 121.9877 | 121.2446 | -0.37477 | 0.005531 | 0.11334 | 0.17955 | 0.11974 | 0.1142 | -0.006558 | -0.042931 | -0.036029 | -0.25433 | 0.18412 | 0.067195 | 0.10322 | 0.08979 | -0.65332 | 122.35 | 122.2301 | 122.1937 | 0.49125 | -122.2311 | 121.9823 | 122.3264 | 121.5833 | 0.49936 | -122.2727
1003.2344 | 122.3236 | -0.30212 | 121.8933 | 1.4211e-13 | -0.0065127 | 0.0016666 | 0.063973 | -0.0081705 | 0.059071 | 0.0092325 | -0.0024589 | -0.0012777 | 0.070647 | 0.024374 | 0.059139 | -0.15462 | 0.14792 | -0.20528 | 122.0204 | 121.8959 | 121.8641 | -0.34695 | -0.15463 | 0.15604 | -0.25781 | 121.6481 | 121.9877 | 121.2491 | -0.37935 | -0.044827 | 0.12707 | 0.14751 | 0.096849 | 0.14168 | 0.002598 | -0.029197 | -0.077229 | -0.24518 | 0.1475 | 0.04431 | 0.12154 | 0.094367 | -0.64417 | 122.3225 | 122.198 | 122.1662 | 0.45005 | -122.2403 | 121.9503 | 122.2898 | 121.5513 | 0.45816 | -122.2727
1004.9844 | 122.1909 | -0.35706 | 121.9345 | 1.4211e-13 | -0.0062991 | 0.0023076 | 0.063759 | -0.0085979 | 0.058858 | -0.006028 | -0.0024589 | -0.0012777 | 0.070647 | 0.023946 | 0.059139 | -0.15462 | 0.14334 | -0.20985 | 122.0295 | 121.9051 | 121.8687 | -0.33321 | -0.15005 | 0.16061 | -0.26697 | 121.6573 | 121.9968 | 121.2812 | -0.3702 | 0.023842 | 0.095028 | 0.20244 | 0.1472 | 0.12336 | -0.029442 | -0.065816 | -0.01314 | -0.27722 | 0.20701 | 0.090084 | 0.10322 | 0.062326 | -0.65331 | 122.3866 | 122.2621 | 122.2257 | 0.5004 | -122.2677 | 122.0143 | 122.3539 | 121.6383 | 0.51767 | -122.3047
1006.6719 | 122.3373 | -0.30212 | 121.9116 | 1.4211e-13 | -0.0065127 | 0.0018804 | 0.063973 | -0.0088115 | 0.059285 | -0.013659 | -0.0026725 | -0.0017051 | 0.070433 | 0.024374 | 0.059353 | -0.1363 | 0.14792 | -0.2007 | 122.0295 | 121.9051 | 121.8778 | -0.32864 | -0.14547 | 0.16519 | -0.25781 | 121.6573 | 121.9923 | 121.2537 | -0.3702 | -0.026511 | 0.11792 | 0.16582 | 0.10143 | 0.12794 | -0.006554 | -0.033771 | -0.068072 | -0.25433 | 0.15665 | 0.04431 | 0.11238 | 0.080635 | -0.6579 | 122.3317 | 122.2072 | 122.18 | 0.45005 | -122.2403 | 121.9594 | 122.2944 | 121.5558 | 0.46732 | -122.2818
1008.4219 | 122.3099 | -0.31586 | 121.9345 | 1.4211e-13 | -0.0065127 | 0.0018804 | 0.063759 | -0.0083841 | 0.059071 | 0.0016025 | -0.0022453 | -0.0012777 | 0.070433 | 0.023946 | 0.059139 | -0.14546 | 0.14792 | -0.20528 | 122.0341 | 121.9096 | 121.8778 | -0.32864 | -0.14547 | 0.15604 | -0.25781 | 121.6619 | 122.0014 | 121.2583 | -0.37935 | -0.012778 | 0.099606 | 0.1704 | 0.11058 | 0.12336 | -0.024863 | -0.056659 | -0.063496 | -0.27264 | 0.17039 | 0.058043 | 0.12154 | 0.066904 | -0.67621 | 122.35 | 122.2255 | 122.1937 | 0.46378 | -122.2631 | 121.9777 | 122.3173 | 121.5742 | 0.47189 | -122.3139
1010.1094 | 122.3007 | -0.30212 | 121.9162 | 1.4211e-13 | -0.0062991 | 0.002094 | 0.064186 | -0.0081705 | 0.058858 | 0.0016025 | -0.0024589 | -0.0017051 | 0.070861 | 0.024374 | 0.058925 | -0.14546 | 0.14792 | -0.20528 | 122.0341 | 121.9142 | 121.8778 | -0.32406 | -0.15005 | 0.16977 | -0.26239 | 121.6573 | 122.006 | 121.2812 | -0.3702 | -0.021932 | 0.11792 | 0.15666 | 0.096849 | 0.11878 | -0.001974 | -0.038349 | -0.068072 | -0.25891 | 0.15207 | 0.039731 | 0.1078 | 0.089793 | -0.635 | 122.3362 | 122.2163 | 122.18 | 0.45005 | -122.2403 | 121.9594 | 122.3081 | 121.5833 | 0.4719 | -122.2864
1011.8594 | 122.2412 | -0.35248 | 121.9391 | 1.4211e-13 | -0.0062991 | 0.0023076 | 0.063545 | -0.0085979 | 0.058858 | 0.0016025 | -0.0024589 | -0.0014913 | 0.070861 | 0.023946 | 0.058925 | -0.15462 | 0.15708 | -0.21443 | 122.0295 | 121.9188 | 121.887 | -0.32864 | -0.15463 | 0.16519 | -0.26697 | 121.6664 | 122.006 | 121.2583 | -0.37477 | 0.023843 | 0.09045 | 0.19786 | 0.13805 | 0.1142 | -0.020283 | -0.05208 | -0.022296 | -0.27264 | 0.19785 | 0.085506 | 0.1078 | 0.066905 | -0.68078 | 122.382 | 122.2713 | 122.2395 | 0.50956 | -122.2677 | 122.0189 | 122.3585 | 121.6108 | 0.51767 | -122.3139
1013.5469 | 122.3099 | -0.33417 | 121.907 | 1.4211e-13 | -0.0062991 | 0.002094 | 0.063759 | -0.0083841 | 0.059285 | -0.006028 | -0.0024589 | -0.0012777 | 0.070647 | 0.023946 | 0.059139 | -0.15004 | 0.1525 | -0.21443 | 122.0387 | 121.9188 | 121.887 | -0.33779 | -0.15463 | 0.15604 | -0.26239 | 121.671 | 122.0014 | 121.272 | -0.3702 | -0.003626 | 0.13165 | 0.18413 | 0.11973 | 0.12336 | 0.011761 | -0.020036 | -0.036029 | -0.23602 | 0.17954 | 0.071774 | 0.1078 | 0.09437 | -0.63501 | 122.3729 | 122.253 | 122.2212 | 0.48667 | -122.2448 | 122.0052 | 122.3356 | 121.6062 | 0.4902 | -122.2772
1015.2344 | 122.3145 | -0.3067 | 121.9299 | 1.4211e-13 | -0.0062991 | 0.0018804 | 0.064186 | -0.0085979 | 0.059071 | 0.0016025 | -0.0022453 | -0.0014913 | 0.070433 | 0.02416 | 0.059139 | -0.15462 | 0.1525 | -0.21443 | 122.0433 | 121.9234 | 121.887 | -0.33321 | -0.15005 | 0.16519 | -0.26239 | 121.6664 | 122.0106 | 121.2995 | -0.3702 | -0.026512 | 0.11334 | 0.15208 | 0.09227 | 0.11878 | -0.006549 | -0.042925 | -0.063494 | -0.26348 | 0.15665 | 0.044309 | 0.1078 | 0.080639 | -0.63042 | 122.35 | 122.2301 | 122.1937 | 0.4592 | -122.2631 | 121.9732 | 122.3173 | 121.6062 | 0.47189 | -122.3001
1017 | 122.287 | -0.32501 | 121.962 | 1.4211e-13 | -0.0062991 | 0.0016666 | 0.064186 | -0.0083841 | 0.058858 | 0.0016025 | -0.0024589 | -0.0010641 | 0.070647 | 0.02416 | 0.058925 | -0.1592 | 0.14792 | -0.21443 | 122.0479 | 121.928 | 121.8916 | -0.32864 | -0.15005 | 0.16061 | -0.25781 | 121.671 | 122.0197 | 121.2949 | -0.38393 | -0.003623 | 0.085876 | 0.16582 | 0.11058 | 0.1142 | -0.034013 | -0.070389 | -0.05892 | -0.29095 | 0.17496 | 0.067198 | 0.12612 | 0.057753 | -0.66704 | 122.3729 | 122.253 | 122.2166 | 0.47293 | -122.2906 | 121.996 | 122.3447 | 121.6199 | 0.48563 | -122.3459
1018.6875 | 122.319 | -0.32044 | 121.9116 | 1.4211e-13 | -0.0060855 | 0.0016666 | 0.063973 | -0.0085979 | 0.059285 | 0.0016025 | -0.0024589 | -0.0014913 | 0.070433 | 0.024374 | 0.058925 | -0.15004 | 0.14792 | -0.20985 | 122.0433 | 121.928 | 121.887 | -0.32406 | -0.15463 | 0.15604 | -0.26239 | 121.6802 | 122.0106 | 121.2949 | -0.37477 | -0.003621 | 0.13165 | 0.1704 | 0.11058 | 0.1142 | 0.016341 | -0.024614 | -0.054339 | -0.23144 | 0.16581 | 0.058042 | 0.11238 | 0.09895 | -0.61669 | 122.3637 | 122.2484 | 122.2074 | 0.46836 | -122.2357 | 122.0006 | 122.331 | 121.6154 | 0.47647 | -122.2864
1020.4375 | 122.2412 | -0.35248 | 121.9666 | 1.4211e-13 | -0.0060855 | 0.002094 | 0.063973 | -0.0085979 | 0.059071 | -0.006028 | -0.0024589 | -0.00085026 | 0.070433 | 0.024374 | 0.058925 | -0.15462 | 0.1525 | -0.21901 | 122.0433 | 121.9234 | 121.8962 | -0.33779 | -0.15463 | 0.15604 | -0.26697 | 121.6756 | 122.0106 | 121.2858 | -0.37477 | 0.014685 | 0.076719 | 0.19786 | 0.13347 | 0.11878 | -0.04317 | -0.070389 | -0.022296 | -0.29095 | 0.19785 | 0.085506 | 0.1078 | 0.044018 | -0.68078 | 122.3958 | 122.2759 | 122.2486 | 0.50498 | -122.3043 | 122.0281 | 122.363 | 121.6383 | 0.50851 | -122.3413
1022.1875 | 122.2321 | -0.35248 | 121.9574 | 1.4211e-13 | -0.0062991 | 0.0016666 | 0.063973 | -0.0085979 | 0.058858 | 0.0016025 | -0.0022453 | -0.0010641 | 0.070433 | 0.023946 | 0.059139 | -0.15462 | 0.1525 | -0.22817 | 122.0433 | 121.928 | 121.8916 | -0.34237 | -0.15921 | 0.15604 | -0.26697 | 121.6664 | 122.0151 | 121.2812 | -0.38393 | 0.010106 | 0.085875 | 0.19786 | 0.12431 | 0.11421 | -0.029435 | -0.065811 | -0.031454 | -0.29095 | 0.19327 | 0.085506 | 0.11696 | 0.057752 | -0.6762 | 122.3958 | 122.2804 | 122.2441 | 0.50498 | -122.2998 | 122.0189 | 122.3676 | 121.6337 | 0.50851 | -122.3413
1023.9375 | 122.2183 | -0.36163 | 121.9299 | 1.4211e-13 | -0.0060855 | 0.0012394 | 0.063973 | -0.0085979 | 0.058858 | -0.006028 | -0.0026725 | -0.0017051 | 0.070433 | 0.024374 | 0.059139 | -0.16377 | 0.14334 | -0.23275 | 122.0524 | 121.928 | 121.8824 | -0.34237 | -0.15921 | 0.16061 | -0.27155 | 121.671 | 122.0151 | 121.2995 | -0.3702 | 0.019261 | 0.1225 | 0.19786 | 0.12889 | 0.10963 | -0.00197 | -0.047504 | -0.008563 | -0.25891 | 0.20243 | 0.090083 | 0.098646 | 0.085217 | -0.63042 | 122.4141 | 122.2896 | 122.2441 | 0.50498 | -122.2723 | 122.0327 | 122.3768 | 121.6611 | 0.52225 | -122.3001
1025.625 | 122.3099 | -0.32501 | 121.9482 | 1.4211e-13 | -0.0067265 | 0.0016666 | 0.063973 | -0.0083841 | 0.058858 | -0.006028 | -0.0024589 | -0.0014913 | 0.070647 | 0.023946 | 0.058925 | -0.16835 | 0.14792 | -0.23275 | 122.0433 | 121.928 | 121.8962 | -0.34237 | -0.15921 | 0.16061 | -0.27613 | 121.6756 | 122.006 | 121.2766 | -0.37935 | -0.01736 | 0.09503 | 0.15666 | 0.092267 | 0.10963 | -0.02028 | -0.052078 | -0.054341 | -0.27264 | 0.16581 | 0.048883 | 0.10322 | 0.05775 | -0.67162 | 122.3683 | 122.253 | 122.2212 | 0.47293 | -122.2906 | 122.0006 | 122.331 | 121.6016 | 0.48563 | -122.3276
1027.3906 | 122.2092 | -0.36621 | 121.962 | 1.4211e-13 | -0.0060855 | 0.0016666 | 0.063973 | -0.0085979 | 0.058644 | -0.006028 | -0.0022453 | -0.0014913 | 0.070647 | 0.02416 | 0.058712 | -0.16377 | 0.14792 | -0.23732 | 122.0479 | 121.9188 | 121.8916 | -0.34237 | -0.16379 | 0.15604 | -0.28071 | 121.671 | 122.0197 | 121.2858 | -0.38851 | 0.023839 | 0.085876 | 0.20244 | 0.12889 | 0.10505 | -0.043171 | -0.070389 | -0.0223 | -0.29095 | 0.20243 | 0.085503 | 0.1078 | 0.057753 | -0.6762 | 122.4141 | 122.285 | 122.2578 | 0.51413 | -122.3043 | 122.0372 | 122.3859 | 121.652 | 0.52225 | -122.3505
1029.1406 | 122.3236 | -0.32959 | 121.9482 | 1.4211e-13 | -0.0062991 | 0.002094 | 0.063973 | -0.0081705 | 0.058858 | -0.006028 | -0.0024589 | -0.0010641 | 0.070433 | 0.02416 | 0.059139 | -0.16377 | 0.14792 | -0.23732 | 122.0433 | 121.928 | 121.9007 | -0.33779 | -0.15921 | 0.16061 | -0.28071 | 121.6802 | 122.0197 | 121.2812 | -0.38393 | -0.008203 | 0.09503 | 0.16582 | 0.092267 | 0.10047 | -0.02028 | -0.047499 | -0.054342 | -0.26806 | 0.17038 | 0.048882 | 0.10322 | 0.071486 | -0.66705 | 122.3729 | 122.2576 | 122.2303 | 0.47751 | -122.286 | 122.0098 | 122.3493 | 121.6108 | 0.4902 | -122.3322
1030.9062 | 122.3007 | -0.35248 | 121.9482 | 1.4211e-13 | -0.0062991 | 0.002094 | 0.064186 | -0.0083841 | 0.059071 | -0.006028 | -0.0024589 | -0.0012777 | 0.070433 | 0.02416 | 0.059353 | -0.1592 | 0.1525 | -0.23275 | 122.0479 | 121.9371 | 121.9053 | -0.33779 | -0.16379 | 0.15146 | -0.28071 | 121.6848 | 122.0243 | 121.3041 | -0.37935 | 0.014685 | 0.099609 | 0.19328 | 0.11973 | 0.10505 | -0.011122 | -0.042921 | -0.026875 | -0.26348 | 0.18869 | 0.07177 | 0.098645 | 0.076064 | -0.64415 | 122.4003 | 122.2896 | 122.2578 | 0.50498 | -122.286 | 122.0372 | 122.3768 | 121.6566 | 0.50393 | -122.3276
1032.5938 | 122.2412 | -0.37537 | 121.994 | 1.4211e-13 | -0.0062991 | 0.002094 | 0.063759 | -0.0083841 | 0.058858 | 0.0016025 | -0.0024589 | -0.0014913 | 0.070433 | 0.024374 | 0.059139 | -0.16835 | 0.14792 | -0.23275 | 122.0524 | 121.9325 | 121.9053 | -0.33779 | -0.16379 | 0.16519 | -0.28529 | 121.6848 | 122.0197 | 121.3957 | -0.37935 | 0.037573 | 0.05841 | 0.20701 | 0.14262 | 0.10505 | -0.061478 | -0.088698 | -0.003987 | -0.30926 | 0.21158 | 0.090079 | 0.094066 | 0.025709 | -0.59836 | 122.4278 | 122.3079 | 122.2807 | 0.52329 | -122.3318 | 122.0601 | 122.3951 | 121.771 | 0.54056 | -122.3734
1034.3438 | 122.3007 | -0.33417 | 121.9162 | 1.4211e-13 | -0.0058717 | 0.0018804 | 0.063973 | -0.0090251 | 0.059071 | -0.013659 | -0.0022453 | -0.0014913 | 0.070861 | 0.024374 | 0.059353 | -0.16377 | 0.14334 | -0.2419 | 122.0524 | 121.9417 | 121.9145 | -0.34237 | -0.15921 | 0.16061 | -0.27155 | 121.6893 | 122.0197 | 121.2858 | -0.38851 | -0.008205 | 0.13623 | 0.17039 | 0.092265 | 0.10047 | 0.025499 | -0.00172 | -0.054344 | -0.22686 | 0.17496 | 0.062617 | 0.11696 | 0.10353 | -0.63043 | 122.3866 | 122.2759 | 122.2486 | 0.47751 | -122.2586 | 122.0235 | 122.3539 | 121.6199 | 0.49478 | -122.3047
1036.0938 | 122.2549 | -0.37537 | 121.9986 | 1.4211e-13 | -0.0060855 | 0.0018804 | 0.064186 | -0.0088115 | 0.058644 | -0.006028 | -0.0024589 | -0.0012777 | 0.070647 | 0.02416 | 0.059139 | -0.16835 | 0.14334 | -0.24648 | 122.057 | 121.9417 | 121.9053 | -0.34237 | -0.15921 | 0.16061 | -0.28071 | 121.6848 | 122.0151 | 121.2904 | -0.38393 | 0.032994 | 0.058411 | 0.20701 | 0.12889 | 0.095892 | -0.056898 | -0.093275 | -0.008566 | -0.31383 | 0.21616 | 0.094658 | 0.10322 | 0.016553 | -0.70824 | 122.4324 | 122.3171 | 122.2807 | 0.51871 | -122.341 | 122.0601 | 122.3905 | 121.6657 | 0.53598 | -122.3825
1037.875 | 122.2412 | -0.37537 | 121.9437 | 1.4211e-13 | -0.0065127 | 0.0018804 | 0.063759 | -0.0085979 | 0.058858 | 0.0016025 | -0.0026725 | -0.0014913 | 0.070861 | 0.02416 | 0.058925 | -0.17751 | 0.15708 | -0.25106 | 122.0479 | 121.9325 | 121.9007 | -0.35611 | -0.17294 | 0.16519 | -0.28986 | 121.6848 | 122.0151 | 121.272 | -0.38851 | 0.019258 | 0.10419 | 0.19786 | 0.12431 | 0.10505 | -0.011124 | -0.042922 | -0.013145 | -0.2589 | 0.20242 | 0.085501 | 0.098646 | 0.071484 | -0.67163 | 122.4232 | 122.3079 | 122.2761 | 0.53244 | -122.2998 | 122.0601 | 122.3905 | 121.6474 | 0.54056 | -122.3322
1039.5625 | 122.2504 | -0.39368 | 121.9803 | 1.4211e-13 | -0.0065127 | 0.0023076 | 0.063759 | -0.0085979 | 0.058644 | -0.006028 | -0.0024589 | -0.0012777 | 0.070433 | 0.024374 | 0.059139 | -0.17293 | 0.14792 | -0.24648 | 122.0524 | 121.9325 | 121.9007 | -0.35153 | -0.17752 | 0.16519 | -0.28071 | 121.6802 | 122.0151 | 121.2904 | -0.39309 | 0.042147 | 0.072143 | 0.22075 | 0.1472 | 0.10505 | -0.047745 | -0.079543 | 0.000587 | -0.3001 | 0.21615 | 0.11297 | 0.11238 | 0.034863 | -0.68993 | 122.4461 | 122.3262 | 122.2944 | 0.5416 | -122.3318 | 122.0739 | 122.4088 | 121.684 | 0.55887 | -122.3734
1041.3125 | 122.3831 | -0.33417 | 121.9528 | 1.4211e-13 | -0.0062991 | 0.0018804 | 0.064186 | -0.0088115 | 0.059071 | -0.013659 | -0.0028861 | -0.0012777 | 0.071074 | 0.024374 | 0.059353 | -0.16835 | 0.15708 | -0.23732 | 122.0524 | 121.9554 | 121.9191 | -0.34237 | -0.16836 | 0.16519 | -0.28529 | 121.6893 | 122.0197 | 121.2904 | -0.39309 | -0.008205 | 0.099609 | 0.16581 | 0.096844 | 0.10505 | 0.002615 | -0.033763 | -0.058923 | -0.26348 | 0.1658 | 0.04888 | 0.1078 | 0.066908 | -0.66247 | 122.3866 | 122.2896 | 122.2532 | 0.49125 | -122.2952 | 122.0235 | 122.3539 | 121.6245 | 0.49936 | -122.3459
1043.0781 | 122.3877 | -0.32501 | 121.9528 | 1.4211e-13 | -0.0060855 | 0.0025214 | 0.063973 | -0.0085979 | 0.059071 | 0.0016025 | -0.0024589 | -0.0014913 | 0.071074 | 0.02416 | 0.059139 | -0.16377 | 0.14334 | -0.24648 | 122.0616 | 121.9509 | 121.9282 | -0.34237 | -0.16379 | 0.16061 | -0.27155 | 121.6985 | 122.038 | 121.2949 | -0.38393 | -0.01736 | 0.10877 | 0.16124 | 0.078532 | 0.095892 | -0.001964 | -0.024606 | -0.05892 | -0.25432 | 0.16123 | 0.053462 | 0.11238 | 0.085222 | -0.65789 | 122.3866 | 122.2759 | 122.2532 | 0.46836 | -122.2952 | 122.0235 | 122.3631 | 121.6199 | 0.48563 | -122.3368
1044.8281 | 122.3373 | -0.32501 | 121.9528 | 1.4211e-13 | -0.0062991 | 0.002094 | 0.064186 | -0.0085979 | 0.058858 | -0.013659 | -0.0026725 | -0.0012777 | 0.070433 | 0.02416 | 0.059566 | -0.1592 | 0.14792 | -0.23275 | 122.0616 | 121.9554 | 121.9236 | -0.34695 | -0.16836 | 0.16519 | -0.27613 | 121.6939 | 122.0289 | 121.2995 | -0.38393 | -0.021939 | 0.10877 | 0.16582 | 0.092267 | 0.11421 | 0.002615 | -0.029184 | -0.05892 | -0.2589 | 0.15665 | 0.048883 | 0.1078 | 0.076065 | -0.65331 | 122.3866 | 122.2804 | 122.2486 | 0.47293 | -122.2998 | 122.0189 | 122.3539 | 121.6245 | 0.49021 | -122.3368
1046.5156 | 122.319 | -0.33417 | 121.9391 | 1.4211e-13 | -0.0065127 | 0.002094 | 0.063973 | -0.0085979 | 0.059071 | 0.0016025 | -0.0026725 | -0.0014913 | 0.070647 | 0.024587 | 0.059139 | -0.16377 | 0.14334 | -0.2419 | 122.0662 | 121.9646 | 121.9236 | -0.34695 | -0.16836 | 0.16977 | -0.28071 | 121.7077 | 122.0426 | 121.4186 | -0.37935 | -0.012784 | 0.12708 | 0.17039 | 0.092265 | 0.10505 | 0.025506 | -0.015451 | -0.045186 | -0.23143 | 0.1658 | 0.053459 | 0.098645 | 0.10353 | -0.52053 | 122.4003 | 122.2988 | 122.2578 | 0.47751 | -122.286 | 122.0418 | 122.3768 | 121.7527 | 0.50394 | -122.3184
1048.2656 | 122.3831 | -0.32044 | 121.9711 | 1.4211e-13 | -0.0060855 | 0.0018804 | 0.063759 | -0.0085979 | 0.058858 | -0.013659 | -0.0024589 | -0.0014913 | 0.070861 | 0.02416 | 0.059139 | -0.16835 | 0.14792 | -0.2419 | 122.0753 | 121.9554 | 121.9236 | -0.34237 | -0.16379 | 0.16061 | -0.27613 | 121.6939 | 122.038 | 121.3178 | -0.37935 | -0.021937 | 0.10419 | 0.15208 | 0.078533 | 0.10047 | -0.015695 | -0.047494 | -0.058918 | -0.27721 | 0.15665 | 0.044306 | 0.10322 | 0.066912 | -0.65331 | 122.3958 | 122.2759 | 122.2441 | 0.46836 | -122.3135 | 122.0144 | 122.3585 | 121.6383 | 0.48105 | -122.3505
1050.0156 | 122.2321 | -0.37994 | 121.994 | 1.4211e-13 | -0.0065127 | 0.0018804 | 0.064186 | -0.0088115 | 0.058858 | -0.013659 | -0.0026725 | -0.0010641 | 0.070647 | 0.024374 | 0.058712 | -0.16377 | 0.1525 | -0.2419 | 122.0662 | 121.9554 | 121.9282 | -0.34237 | -0.16836 | 0.16519 | -0.28071 | 121.6985 | 122.038 | 121.3407 | -0.38851 | 0.037572 | 0.072145 | 0.21617 | 0.13804 | 0.10047 | -0.038584 | -0.065805 | -0.008567 | -0.29552 | 0.21158 | 0.099236 | 0.1078 | 0.044023 | -0.6533 | 122.4461 | 122.3354 | 122.3082 | 0.53244 | -122.3364 | 122.0784 | 122.418 | 121.7207 | 0.54514 | -122.3825
1051.7031 | 122.3145 | -0.37079 | 121.962 | 1.4211e-13 | -0.0062991 | 0.0018804 | 0.063973 | -0.0088115 | 0.059071 | 0.0016025 | -0.0024589 | -0.0010641 | 0.070433 | 0.024587 | 0.059353 | -0.17293 | 0.13876 | -0.25106 | 122.0524 | 121.9417 | 121.9099 | -0.33779 | -0.17294 | 0.16519 | -0.28529 | 121.6848 | 122.0289 | 121.2766 | -0.37935 | 0.032996 | 0.090454 | 0.19786 | 0.11973 | 0.086735 | -0.020277 | -0.052075 | -0.008564 | -0.27721 | 0.19785 | 0.085502 | 0.094066 | 0.06691 | -0.68536 | 122.4232 | 122.3125 | 122.2807 | 0.50955 | -122.2998 | 122.0556 | 122.3997 | 121.6474 | 0.53598 | -122.3413
1053.4688 | 122.3831 | -0.32959 | 121.907 | 1.4211e-13 | -0.0062991 | 0.0018804 | 0.063973 | -0.0085979 | 0.059285 | -0.006028 | -0.0026725 | -0.0012777 | 0.070647 | 0.024587 | 0.059139 | -0.17293 | 0.14334 | -0.2419 | 122.0707 | 121.96 | 121.9236 | -0.35153 | -0.17294 | 0.16519 | -0.28986 | 121.7031 | 122.0426 | 121.3224 | -0.39767 | -0.02194 | 0.1637 | 0.15666 | 0.087688 | 0.10963 | 0.052971 | 0.016593 | -0.068078 | -0.20397 | 0.15665 | 0.039725 | 0.1078 | 0.13558 | -0.58464 | 122.4003 | 122.2896 | 122.2532 | 0.47293 | -122.2586 | 122.0327 | 122.3722 | 121.652 | 0.49478 | -122.3047
1055.2344 | 122.2916 | -0.37079 | 121.9757 | 1.4211e-13 | -0.0065127 | 0.002094 | 0.064186 | -0.0085979 | 0.058858 | -0.006028 | -0.0024589 | -0.0014913 | 0.070861 | 0.02416 | 0.058712 | -0.17293 | 0.14334 | -0.24648 | 122.0662 | 121.96 | 121.9328 | -0.34695 | -0.17294 | 0.16061 | -0.28986 | 121.7031 | 122.0426 | 121.3361 | -0.38851 | 0.023838 | 0.090456 | 0.19786 | 0.12431 | 0.10047 | -0.015694 | -0.042915 | -0.017722 | -0.27263 | 0.19785 | 0.080924 | 0.098646 | 0.066913 | -0.63957 | 122.437 | 122.3308 | 122.3036 | 0.51413 | -122.3227 | 122.0739 | 122.4134 | 121.7069 | 0.5314 | -122.3642
1057 | 122.3007 | -0.36163 | 121.9849 | 1.4211e-13 | -0.0062991 | 0.0018804 | 0.063973 | -0.0085979 | 0.058644 | -0.006028 | -0.0026725 | -0.0014913 | 0.070861 | 0.024587 | 0.059139 | -0.16835 | 0.14792 | -0.25106 | 122.0753 | 121.96 | 121.9328 | -0.35153 | -0.17294 | 0.16061 | -0.28986 | 121.7077 | 122.0335 | 121.3041 | -0.38393 | 0.010103 | 0.090458 | 0.19328 | 0.11057 | 0.10047 | -0.024849 | -0.05207 | -0.022299 | -0.27721 | 0.18869 | 0.071768 | 0.094067 | 0.048601 | -0.68077 | 122.437 | 122.3216 | 122.2944 | 0.50955 | -122.3364 | 122.0693 | 122.3951 | 121.6657 | 0.52225 | -122.3688
1058.6875 | 122.3969 | -0.20599 | 122.0856 | 1.4211e-13 | -0.0062991 | 0.002094 | 0.063759 | -0.0081705 | 0.059071 | 0.0016025 | -0.0024589 | -0.0014913 | 0.070861 | 0.024587 | 0.059139 | -0.14546 | 0.14334 | -0.22817 | 122.0936 | 121.9875 | 121.9603 | -0.33321 | -0.15005 | 0.16519 | -0.26697 | 121.7305 | 122.0655 | 121.3545 | -0.37477 | -0.12722 | 0.008064 | 0.060533 | -0.022173 | 0.10505 | -0.098083 | -0.12531 | -0.16878 | -0.35502 | 0.055944 | -0.060978 | 0.1078 | -0.020057 | -0.73112 | 122.2996 | 122.1935 | 122.1663 | 0.34934 | -122.4188 | 121.9365 | 122.2715 | 121.5604 | 0.37119 | -122.4603
1060.4531 | 122.2824 | -0.22888 | 122.1451 | 1.4211e-13 | -0.0060855 | 0.002094 | 0.0644 | -0.0081705 | 0.058644 | 0.0016025 | -0.0022453 | -0.0019187 | 0.071074 | 0.024587 | 0.058925 | -0.058472 | 0.14792 | -0.12745 | 122.2081 | 122.0928 | 122.0656 | -0.2279 | -0.053897 | 0.17435 | -0.16166 | 121.8313 | 122.1846 | 121.4781 | -0.26946 | 0.000983 | 0.063013 | 0.17041 | 0.10144 | 0.10045 | -0.052278 | -0.079509 | -0.04058 | -0.31381 | 0.17499 | 0.067221 | 0.1078 | 0.039476 | -0.66701 | 122.437 | 122.3217 | 122.2945 | 0.3768 | -122.373 | 122.0602 | 122.4134 | 121.707 | 0.40323 | -122.4145
1062.2031 | 122.3831 | -0.21057 | 122.0856 | 1.4211e-13 | -0.0062991 | 0.002094 | 0.063973 | -0.0085979 | 0.058858 | 0.0016025 | -0.0022453 | -0.0014913 | 0.070861 | 0.024374 | 0.058925 | -0.053893 | 0.14334 | -0.12287 | 122.2035 | 122.102 | 122.0656 | -0.21874 | -0.058476 | 0.17893 | -0.1525 | 121.8404 | 122.1846 | 121.4552 | -0.27404 | -0.00817 | 0.11794 | 0.15668 | 0.087705 | 0.095875 | 0.01639 | -0.019999 | -0.063469 | -0.24514 | 0.1521 | 0.058067 | 0.12154 | 0.098986 | -0.63039 | 122.4141 | 122.3125 | 122.2761 | 0.35391 | -122.3043 | 122.051 | 122.3951 | 121.6658 | 0.3895 | -122.3596
1063.9375 | 122.2916 | -0.2243 | 122.113 | 1.4211e-13 | -0.0060855 | 0.0018804 | 0.064186 | -0.0083841 | 0.058858 | -0.006028 | -0.0026725 | -0.0010641 | 0.071288 | 0.024374 | 0.059353 | -0.049315 | 0.14334 | -0.12287 | 122.2127 | 122.0974 | 122.0747 | -0.23248 | -0.058476 | 0.16519 | -0.15708 | 121.845 | 122.1891 | 121.4552 | -0.26946 | -0.008173 | 0.099636 | 0.17499 | 0.10144 | 0.10961 | -0.015655 | -0.038307 | -0.045158 | -0.26803 | 0.16583 | 0.067221 | 0.11238 | 0.076099 | -0.65786 | 122.437 | 122.3217 | 122.299 | 0.36765 | -122.3455 | 122.0693 | 122.4134 | 121.6795 | 0.3895 | -122.3825
1065.625 | 122.3007 | -0.25177 | 122.1268 | 1.4211e-13 | -0.0062991 | 0.0018804 | 0.064614 | -0.0085979 | 0.059071 | -0.013659 | -0.0024589 | -0.0017051 | 0.07022 | 0.024587 | 0.059139 | -0.06305 | 0.14334 | -0.12745 | 122.2173 | 122.102 | 122.0747 | -0.205 | -0.053897 | 0.16519 | -0.1525 | 121.8542 | 122.1846 | 121.4598 | -0.26488 | 0.046766 | 0.090481 | 0.18872 | 0.12432 | 0.077559 | -0.024809 | -0.05204 | -0.013113 | -0.2726 | 0.19787 | 0.099266 | 0.11238 | 0.057787 | -0.66701 | 122.469 | 122.3537 | 122.3265 | 0.39511 | -122.3318 | 122.1059 | 122.4363 | 121.7115 | 0.41696 | -122.3917
1067.375 | 122.2778 | -0.25177 | 122.1451 | 1.4211e-13 | -0.0062991 | 0.0018804 | 0.063759 | -0.0085979 | 0.058858 | 0.0016025 | -0.0026725 | -0.0014913 | 0.070647 | 0.024801 | 0.059353 | -0.053893 | 0.14334 | -0.12287 | 122.2173 | 122.1065 | 122.0702 | -0.23248 | -0.053897 | 0.16061 | -0.16166 | 121.845 | 122.1891 | 121.4552 | -0.27862 | 0.019293 | 0.07217 | 0.19788 | 0.1289 | 0.10961 | -0.038541 | -0.07493 | -0.026849 | -0.30007 | 0.19787 | 0.090109 | 0.11696 | 0.044055 | -0.6899 | 122.469 | 122.3583 | 122.3219 | 0.39511 | -122.3776 | 122.0968 | 122.4409 | 121.707 | 0.41238 | -122.4237
1069.125 | 122.3602 | -0.21515 | 122.0947 | 1.4211e-13 | -0.0060855 | 0.002094 | 0.064186 | -0.0090251 | 0.059071 | 0.0016025 | -0.0022453 | -0.0012777 | 0.070861 | 0.024587 | 0.059139 | -0.053893 | 0.14792 | -0.11829 | 122.2081 | 122.1065 | 122.0793 | -0.2279 | -0.058476 | 0.16977 | -0.1525 | 121.8404 | 122.1891 | 121.4506 | -0.26946 | -0.01275 | 0.11337 | 0.16126 | 0.096861 | 0.10961 | 0.011813 | -0.015419 | -0.054313 | -0.2543 | 0.15667 | 0.062645 | 0.11696 | 0.094409 | -0.64412 | 122.4232 | 122.3217 | 122.2945 | 0.36307 | -122.3226 | 122.0556 | 122.4043 | 121.6658 | 0.38492 | -122.3642
1070.875 | 122.3282 | -0.2243 | 122.1085 | 1.4211e-13 | -0.0062991 | 0.0018804 | 0.063973 | -0.0083841 | 0.058644 | 0.0016025 | -0.0028861 | -0.0014913 | 0.070647 | 0.02416 | 0.059139 | -0.058472 | 0.14792 | -0.12745 | 122.2127 | 122.102 | 122.0793 | -0.19585 | -0.058476 | 0.16977 | -0.15708 | 121.8587 | 122.1846 | 121.4643 | -0.27404 | 0.028458 | 0.10421 | 0.16583 | 0.096859 | 0.068401 | -0.006498 | -0.029151 | -0.049736 | -0.24971 | 0.16583 | 0.067221 | 0.11696 | 0.076098 | -0.64412 | 122.437 | 122.3263 | 122.3036 | 0.37223 | -122.3043 | 122.083 | 122.4089 | 121.6886 | 0.39408 | -122.3825
1072.6406 | 122.3969 | -0.20599 | 122.0947 | 1.4211e-13 | -0.0062991 | 0.002094 | 0.063545 | -0.0085979 | 0.059071 | 0.016863 | -0.0024589 | -0.0012777 | 0.070647 | 0.024374 | 0.059353 | -0.053893 | 0.1525 | -0.1366 | 122.2218 | 122.1203 | 122.0793 | -0.2279 | -0.063054 | 0.16977 | -0.15708 | 121.8542 | 122.1983 | 121.4643 | -0.27862 | -0.021905 | 0.1271 | 0.1521 | 0.069393 | 0.091298 | 0.02555 | -0.015419 | -0.072625 | -0.24056 | 0.14294 | 0.048911 | 0.12154 | 0.10357 | -0.63039 | 122.4278 | 122.3263 | 122.2853 | 0.35849 | -122.3226 | 122.0602 | 122.4043 | 121.6703 | 0.37577 | -122.3733
1074.3281 | 122.2824 | -0.23804 | 122.1497 | 1.4211e-13 | -0.0065127 | 0.002094 | 0.063973 | -0.0088115 | 0.059071 | 0.0092325 | -0.0022453 | -0.0014913 | 0.070861 | 0.024374 | 0.059353 | -0.053893 | 0.14792 | -0.12745 | 122.2264 | 122.1157 | 122.0839 | -0.23248 | -0.067633 | 0.17435 | -0.1525 | 121.8587 | 122.2029 | 121.4827 | -0.26946 | 0.00556 | 0.07675 | 0.18414 | 0.11059 | 0.10503 | -0.03396 | -0.065771 | -0.031425 | -0.29091 | 0.1704 | 0.085533 | 0.11696 | 0.053214 | -0.667 | 122.4644 | 122.3537 | 122.3219 | 0.38596 | -122.3821 | 122.0968 | 122.4409 | 121.7207 | 0.41239 | -122.4191
1076.0625 | 122.2733 | -0.25635 | 122.1542 | 1.4211e-13 | -0.0060855 | 0.0018804 | 0.0644 | -0.0083841 | 0.059285 | 0.0092325 | -0.0024589 | -0.0012777 | 0.070647 | 0.024587 | 0.059353 | -0.058472 | 0.1525 | -0.12287 | 122.2356 | 122.1157 | 122.0885 | -0.21416 | -0.058476 | 0.17435 | -0.1525 | 121.8587 | 122.1983 | 121.4643 | -0.26946 | 0.042186 | 0.081329 | 0.19788 | 0.13348 | 0.091296 | -0.038538 | -0.065771 | -0.013114 | -0.29549 | 0.19787 | 0.10384 | 0.11696 | 0.044057 | -0.6899 | 122.4919 | 122.372 | 122.3448 | 0.40885 | -122.3684 | 122.1151 | 122.4546 | 121.7207 | 0.4307 | -122.4237
1077.8125 | 122.2916 | -0.23804 | 122.1588 | 1.4211e-13 | -0.0065127 | 0.0018804 | 0.064186 | -0.0088115 | 0.058644 | -0.006028 | -0.0024589 | -0.0012777 | 0.070433 | 0.024587 | 0.059353 | -0.06305 | 0.14792 | -0.12287 | 122.2264 | 122.1203 | 122.0976 | -0.21416 | -0.049318 | 0.16519 | -0.1525 | 121.8679 | 122.2029 | 121.4918 | -0.26946 | 0.023875 | 0.067595 | 0.17499 | 0.11517 | 0.091296 | -0.038536 | -0.06119 | -0.031425 | -0.29091 | 0.18872 | 0.085533 | 0.11696 | 0.044059 | -0.667 | 122.4644 | 122.3583 | 122.3357 | 0.38596 | -122.373 | 122.1059 | 122.4409 | 121.7298 | 0.40323 | -122.4283
1079.5625 | 122.3694 | -0.21973 | 122.0993 | 1.4211e-13 | -0.0062991 | 0.002094 | 0.064186 | -0.0090251 | 0.059285 | -0.006028 | -0.0022453 | -0.0010641 | 0.070647 | 0.024587 | 0.059139 | -0.049315 | 0.1525 | -0.12287 | 122.231 | 122.1249 | 122.093 | -0.20958 | -0.049318 | 0.16977 | -0.1525 | 121.8587 | 122.1983 | 121.4918 | -0.26488 | 0.010144 | 0.13168 | 0.17041 | 0.096861 | 0.086717 | 0.025551 | -0.00626 | -0.045156 | -0.24056 | 0.17041 | 0.067223 | 0.11238 | 0.098989 | -0.60749 | 122.4507 | 122.3446 | 122.3128 | 0.37223 | -122.3089 | 122.0785 | 122.418 | 121.7115 | 0.3895 | -122.3642
1081.25 | 122.2687 | -0.25177 | 122.1451 | 1.4211e-13 | -0.0065127 | 0.0023076 | 0.064186 | -0.0083841 | 0.058858 | 0.0016025 | -0.0022453 | -0.0012777 | 0.070861 | 0.024587 | 0.059353 | -0.049315 | 0.15708 | -0.11829 | 122.2401 | 122.1386 | 122.1114 | -0.21416 | -0.053897 | 0.16519 | -0.1525 | 121.8679 | 122.212 | 121.4689 | -0.2603 | 0.037608 | 0.095062 | 0.20245 | 0.13348 | 0.095874 | -0.006489 | -0.033723 | -0.008534 | -0.27718 | 0.19787 | 0.099266 | 0.1078 | 0.066948 | -0.67616 | 122.4919 | 122.3904 | 122.3631 | 0.40885 | -122.3592 | 122.1197 | 122.4638 | 121.7207 | 0.41696 | -122.4054
1083.0156 | 122.3419 | -0.22888 | 122.1359 | 1.4211e-13 | -0.0060855 | 0.0023076 | 0.063759 | -0.0088115 | 0.059285 | 0.0092325 | -0.0026725 | -0.0012777 | 0.070647 | 0.024587 | 0.058925 | -0.044736 | 0.14792 | -0.11371 | 122.2447 | 122.1386 | 122.1114 | -0.21416 | -0.040161 | 0.16519 | -0.14335 | 121.8771 | 122.212 | 121.4827 | -0.2603 | 0.01472 | 0.1088 | 0.18415 | 0.11517 | 0.10045 | 0.002667 | -0.024567 | -0.031422 | -0.25887 | 0.18872 | 0.085535 | 0.11696 | 0.076104 | -0.65327 | 122.4736 | 122.3675 | 122.3402 | 0.3768 | -122.3501 | 122.1059 | 122.4409 | 121.7115 | 0.39408 | -122.3962
1084.7656 | 122.4289 | -0.19226 | 122.1222 | 1.4211e-13 | -0.0065127 | 0.0018804 | 0.063973 | -0.0088115 | 0.059071 | -0.006028 | -0.0024589 | -0.0014913 | 0.070647 | 0.024587 | 0.059353 | -0.040158 | 0.15708 | -0.10913 | 122.2401 | 122.1386 | 122.1068 | -0.19585 | -0.040161 | 0.16061 | -0.13877 | 121.8816 | 122.2212 | 121.5193 | -0.25572 | -0.003585 | 0.11795 | 0.1521 | 0.083129 | 0.086714 | 0.0164 | -0.015412 | -0.063464 | -0.24056 | 0.1521 | 0.053493 | 0.11696 | 0.098994 | -0.60291 | 122.4324 | 122.3309 | 122.299 | 0.34934 | -122.318 | 122.0739 | 122.4134 | 121.7115 | 0.35287 | -122.3779
1086.4688 | 122.4243 | -0.19684 | 122.1451 | 1.4211e-13 | -0.0067265 | 0.002094 | 0.064186 | -0.0085979 | 0.058644 | -0.006028 | -0.0026725 | -0.0014913 | 0.070433 | 0.024374 | 0.059566 | -0.044736 | 0.16624 | -0.11371 | 122.2539 | 122.1432 | 122.1159 | -0.15464 | -0.040161 | 0.17435 | -0.13877 | 121.8862 | 122.2212 | 121.501 | -0.25115 | 0.042202 | 0.1088 | 0.1521 | 0.083128 | 0.040926 | -0.00191 | -0.029144 | -0.054308 | -0.25887 | 0.15668 | 0.05807 | 0.11238 | 0.076105 | -0.64411 | 122.4507 | 122.34 | 122.3128 | 0.36307 | -122.2997 | 122.0831 | 122.418 | 121.6978 | 0.37119 | -122.3962
1088.2188 | 122.4197 | -0.19226 | 122.1313 | 1.4211e-13 | -0.0065127 | 0.0018804 | 0.063973 | -0.0085979 | 0.058858 | 0.0016025 | -0.0024589 | -0.0014913 | 0.070433 | 0.024801 | 0.059566 | -0.03558 | 0.17081 | -0.099975 | 122.2585 | 122.1569 | 122.1388 | -0.12716 | -0.035582 | 0.16977 | -0.13419 | 121.8954 | 122.2303 | 121.4918 | -0.25115 | 0.065099 | 0.12711 | 0.15668 | 0.092286 | 0.027187 | 0.02556 | 0.007482 | -0.058885 | -0.23598 | 0.15668 | 0.058072 | 0.11696 | 0.098996 | -0.63954 | 122.4507 | 122.3492 | 122.3311 | 0.36308 | -122.2585 | 122.0876 | 122.4226 | 121.6841 | 0.36203 | -122.3825
1089.9688 | 122.3465 | -0.2243 | 122.1451 | 1.4211e-13 | -0.0062991 | 0.0018804 | 0.064186 | -0.0085979 | 0.058858 | -0.006028 | -0.0024589 | -0.0012777 | 0.070647 | 0.024801 | 0.059139 | -0.03558 | 0.16166 | -0.10913 | 122.2585 | 122.1615 | 122.1297 | -0.15464 | -0.040161 | 0.16519 | -0.14335 | 121.8954 | 122.2395 | 121.5284 | -0.25115 | 0.069668 | 0.11337 | 0.18872 | 0.11517 | 0.045504 | 0.016406 | -0.015408 | -0.026842 | -0.24971 | 0.18414 | 0.080957 | 0.1078 | 0.09442 | -0.61664 | 122.4828 | 122.3858 | 122.354 | 0.38596 | -122.2997 | 122.1197 | 122.4638 | 121.7527 | 0.3895 | -122.3962
1091.6562 | 122.4472 | -0.17395 | 122.1222 | 1.4211e-13 | -0.0062991 | 0.002094 | 0.064186 | -0.0088115 | 0.058858 | 0.0016025 | -0.0024589 | -0.0012777 | 0.070433 | 0.024587 | 0.059353 | -0.03558 | 0.16624 | -0.10455 | 122.2539 | 122.1661 | 122.1343 | -0.072215 | -0.035582 | 0.16977 | -0.13419 | 121.8908 | 122.2349 | 121.533 | -0.24199 | 0.10173 | 0.13169 | 0.13837 | 0.069397 | -0.032338 | 0.043874 | 0.012059 | -0.068039 | -0.2314 | 0.13837 | 0.039761 | 0.1078 | 0.11273 | -0.58917 | 122.4278 | 122.34 | 122.3082 | 0.34019 | -122.1944 | 122.0647 | 122.4089 | 121.707 | 0.34372 | -122.3642
1093.4062 | 122.3785 | -0.19684 | 122.1497 | 1.4211e-13 | -0.0062991 | 0.002094 | 0.063973 | -0.0085979 | 0.059071 | -0.013659 | -0.0024589 | -0.0014913 | 0.070861 | 0.024374 | 0.059353 | -0.026423 | 0.17081 | -0.10455 | 122.2676 | 122.1752 | 122.1343 | -0.13174 | -0.031003 | 0.17893 | -0.12961 | 121.9091 | 122.2258 | 121.5284 | -0.24199 | 0.065097 | 0.11795 | 0.17042 | 0.092285 | 0.027188 | 0.025566 | -0.015407 | -0.045151 | -0.24055 | 0.16584 | 0.067228 | 0.11238 | 0.076107 | -0.62122 | 122.4645 | 122.3721 | 122.3311 | 0.36765 | -122.2814 | 122.1059 | 122.4226 | 121.7253 | 0.37577 | -122.3916
1095.1562 | 122.2824 | -0.23346 | 122.2137 | 1.4211e-13 | -0.0062991 | 0.0023076 | 0.063973 | -0.0083841 | 0.058858 | 0.0016025 | -0.0024589 | -0.0014913 | 0.070861 | 0.024374 | 0.059353 | -0.03558 | 0.16166 | -0.10455 | 122.2585 | 122.1569 | 122.1388 | -0.09511 | -0.026425 | 0.17435 | -0.13877 | 121.9 | 122.2395 | 121.5239 | -0.23741 | 0.13835 | 0.044711 | 0.19788 | 0.12891 | -0.009443 | -0.056837 | -0.074915 | -0.003951 | -0.31379 | 0.20703 | 0.094691 | 0.098642 | 0.025756 | -0.68988 | 122.4919 | 122.3904 | 122.3723 | 0.39512 | -122.3089 | 122.1334 | 122.473 | 121.7573 | 0.40781 | -122.4512
1096.9219 | 122.3282 | -0.23804 | 122.2 | 1.4211e-13 | -0.0062991 | 0.002094 | 0.063973 | -0.0088115 | 0.058644 | 0.0016025 | -0.0024589 | -0.0012777 | 0.070433 | 0.024374 | 0.059353 | -0.031001 | 0.16166 | -0.10455 | 122.2676 | 122.1752 | 122.1434 | -0.067636 | -0.031003 | 0.16977 | -0.13419 | 121.9045 | 122.2395 | 121.5513 | -0.25115 | 0.1704 | 0.067601 | 0.20704 | 0.13348 | -0.036917 | -0.024788 | -0.056603 | -0.013109 | -0.29548 | 0.20703 | 0.10385 | 0.11696 | 0.039489 | -0.64868 | 122.5057 | 122.4133 | 122.3814 | 0.3997 | -122.2676 | 122.1426 | 122.4775 | 121.7894 | 0.40781 | -122.4512
1098.625 | 122.3007 | -0.21515 | 122.1588 | 1.4211e-13 | -0.0062991 | 0.0025214 | 0.064614 | -0.0085979 | 0.058858 | 0.0092325 | -0.0026725 | -0.0012777 | 0.070647 | 0.025015 | 0.059139 | -0.03558 | 0.16624 | -0.099975 | 122.2676 | 122.1752 | 122.1434 | -0.14548 | -0.026425 | 0.16977 | -0.13419 | 121.9045 | 122.2487 | 121.5468 | -0.24199 | 0.069671 | 0.1088 | 0.17957 | 0.11517 | 0.045503 | 0.016411 | -0.015404 | -0.02684 | -0.25428 | 0.18872 | 0.08096 | 0.1078 | 0.089845 | -0.61206 | 122.4828 | 122.3904 | 122.3586 | 0.38138 | -122.3043 | 122.1197 | 122.4638 | 121.7619 | 0.38492 | -122.4008
1100.375 | 122.3923 | -0.16937 | 122.1542 | 1.4211e-13 | -0.0060855 | 0.002094 | 0.063973 | -0.0085979 | 0.058858 | 0.0092325 | -0.0024589 | -0.0010641 | 0.070861 | 0.024801 | 0.059566 | -0.031001 | 0.16624 | -0.099975 | 122.2768 | 122.1798 | 122.1434 | -0.12258 | -0.026425 | 0.16977 | -0.13877 | 121.9137 | 122.2349 | 121.5101 | -0.24199 | 0.04679 | 0.12253 | 0.13837 | 0.069398 | 0.022608 | 0.025567 | -0.010827 | -0.072616 | -0.24055 | 0.14295 | 0.030605 | 0.10322 | 0.080686 | -0.64411 | 122.4461 | 122.3492 | 122.3128 | 0.33561 | -122.2768 | 122.0831 | 122.4043 | 121.6795 | 0.33914 | -122.3962
1102.1094 | 122.3877 | -0.21515 | 122.1634 | 1.4211e-13 | -0.0062991 | 0.002094 | 0.0644 | -0.0088115 | 0.058858 | 0.0016025 | -0.0024589 | -0.0014913 | 0.070647 | 0.024374 | 0.059353 | -0.031001 | 0.16624 | -0.095397 | 122.2676 | 122.1706 | 122.148 | -0.13174 | -0.035582 | 0.17893 | -0.12961 | 121.9091 | 122.2487 | 121.5513 | -0.24657 | 0.083408 | 0.10422 | 0.18415 | 0.11975 | 0.036344 | 0.007254 | -0.015404 | -0.031418 | -0.25428 | 0.17957 | 0.085539 | 0.11696 | 0.085267 | -0.61206 | 122.4828 | 122.3858 | 122.3631 | 0.38138 | -122.2951 | 122.1243 | 122.4638 | 121.7665 | 0.39408 | -122.41
1103.875 | 122.4197 | -0.18768 | 122.1497 | 1.4211e-13 | -0.0062991 | 0.002094 | 0.063973 | -0.0090251 | 0.058644 | -0.006028 | -0.0024589 | -0.0014913 | 0.070647 | 0.024801 | 0.059353 | -0.040158 | 0.16624 | -0.099975 | 122.2722 | 122.1661 | 122.1388 | -0.15464 | -0.040161 | 0.17435 | -0.13877 | 121.9 | 122.2349 | 121.5239 | -0.25115 | 0.033047 | 0.12253 | 0.14752 | 0.087708 | 0.054661 | 0.016408 | -0.010828 | -0.063463 | -0.24971 | 0.14752 | 0.048915 | 0.11238 | 0.085264 | -0.6258 | 122.4599 | 122.3537 | 122.3265 | 0.35392 | -122.3043 | 122.0876 | 122.4226 | 121.7115 | 0.36203 | -122.4008
1105.5781 | 122.3511 | -0.21515 | 122.1909 | 1.4211e-13 | -0.0065127 | 0.0023076 | 0.063973 | -0.0083841 | 0.059285 | -0.013659 | -0.0022453 | -0.0010641 | 0.070861 | 0.024374 | 0.059139 | -0.040158 | 0.16166 | -0.10913 | 122.263 | 122.1752 | 122.148 | -0.15006 | -0.040161 | 0.17893 | -0.13877 | 121.9137 | 122.2349 | 121.533 | -0.25115 | 0.065092 | 0.072178 | 0.17499 | 0.10602 | 0.040925 | -0.015633 | -0.04287 | -0.035997 | -0.27717 | 0.17499 | 0.076381 | 0.11238 | 0.044065 | -0.65784 | 122.4782 | 122.3904 | 122.3631 | 0.37681 | -122.3409 | 122.1288 | 122.4501 | 121.7482 | 0.39408 | -122.442
1107.3281 | 122.4426 | -0.18768 | 122.1313 | 1.4211e-13 | -0.0060855 | 0.002094 | 0.063973 | -0.0090251 | 0.059285 | -0.013659 | -0.0024589 | -0.0012777 | 0.070647 | 0.024801 | 0.059353 | -0.03558 | 0.16166 | -0.10913 | 122.263 | 122.1752 | 122.1434 | -0.20958 | -0.040161 | 0.16519 | -0.14335 | 121.9091 | 122.2349 | 121.5193 | -0.25572 | -0.0219 | 0.13169 | 0.1521 | 0.078551 | 0.10045 | 0.043876 | 0.012061 | -0.068042 | -0.22224 | 0.14752 | 0.044336 | 0.11238 | 0.10357 | -0.61207 | 122.4507 | 122.3629 | 122.3311 | 0.34934 | -122.3409 | 122.0968 | 122.4226 | 121.707 | 0.35288 | -122.3871
1109.0625 | 122.3831 | -0.2243 | 122.1634 | 1.4211e-13 | -0.0062991 | 0.0018804 | 0.063973 | -0.0085979 | 0.059071 | -0.013659 | -0.0026725 | -0.0014913 | 0.070861 | 0.024587 | 0.059353 | -0.058472 | 0.16624 | -0.12745 | 122.2401 | 122.1523 | 122.1297 | -0.21874 | -0.058476 | 0.17893 | -0.15708 | 121.8908 | 122.2166 | 121.4872 | -0.26488 | 0.005563 | 0.076752 | 0.16583 | 0.096859 | 0.091296 | -0.011062 | -0.033718 | -0.040579 | -0.2726 | 0.16583 | 0.067221 | 0.1078 | 0.053217 | -0.67616 | 122.4644 | 122.3766 | 122.354 | 0.39054 | -122.3821 | 122.1151 | 122.4409 | 121.7115 | 0.40323 | -122.4283
1110.8125 | 122.4335 | -0.19226 | 122.1222 | 1.4211e-13 | -0.0060855 | 0.0016666 | 0.0644 | -0.0088115 | 0.059071 | 0.0016025 | -0.0026725 | -0.0010641 | 0.070433 | 0.024587 | 0.059353 | -0.053893 | 0.16166 | -0.12287 | 122.2539 | 122.1706 | 122.1297 | -0.19585 | -0.058476 | 0.17435 | -0.16166 | 121.9 | 122.2258 | 121.533 | -0.26946 | -0.003585 | 0.13169 | 0.13837 | 0.069395 | 0.07298 | 0.048453 | 0.007481 | -0.077201 | -0.22224 | 0.13378 | 0.0306 | 0.1078 | 0.10357 | -0.58917 | 122.4461 | 122.3629 | 122.3219 | 0.35392 | -122.318 | 122.0922 | 122.418 | 121.7253 | 0.36661 | -122.3917
1112.5156 | 122.3145 | -0.23346 | 122.2046 | 1.4211e-13 | -0.0062991 | 0.002094 | 0.064186 | -0.0088115 | 0.059071 | 0.0016025 | -0.0024589 | -0.0010641 | 0.070861 | 0.024801 | 0.059139 | -0.049315 | 0.17081 | -0.11829 | 122.2676 | 122.1661 | 122.1526 | -0.20042 | -0.049318 | 0.17893 | -0.14793 | 121.8954 | 122.2303 | 121.5559 | -0.2603 | 0.033034 | 0.063023 | 0.18414 | 0.11517 | 0.082137 | -0.038524 | -0.052024 | -0.026845 | -0.30922 | 0.18414 | 0.085534 | 0.11238 | 0.025754 | -0.64868 | 122.5011 | 122.3995 | 122.386 | 0.40427 | -122.405 | 122.1288 | 122.4638 | 121.7894 | 0.41239 | -122.4649
1114.2656 | 122.3465 | -0.23346 | 122.2 | 1.4211e-13 | -0.0062991 | 0.0018804 | 0.063973 | -0.0083841 | 0.058858 | 0.0016025 | -0.0024589 | -0.0012777 | 0.070861 | 0.024801 | 0.059139 | -0.040158 | 0.17081 | -0.10913 | 122.263 | 122.1798 | 122.148 | -0.20042 | -0.035582 | 0.17435 | -0.13877 | 121.9091 | 122.2441 | 121.5651 | -0.25572 | 0.033034 | 0.063023 | 0.1933 | 0.12433 | 0.091293 | -0.020209 | -0.052025 | -0.022266 | -0.2909 | 0.19788 | 0.094691 | 0.11696 | 0.044067 | -0.63494 | 122.4965 | 122.4133 | 122.3814 | 0.40427 | -122.4004 | 122.1426 | 122.4775 | 121.7985 | 0.40781 | -122.4557
1116.0156 | 122.287 | -0.23804 | 122.2 | 1.4211e-13 | -0.0060855 | 0.002094 | 0.064186 | -0.0085979 | 0.059071 | -0.006028 | -0.0022453 | -0.0017051 | 0.070433 | 0.024587 | 0.059353 | -0.053893 | 0.17539 | -0.10913 | 122.2722 | 122.1752 | 122.148 | -0.19585 | -0.040161 | 0.17435 | -0.14335 | 121.9091 | 122.2441 | 121.5651 | -0.25115 | 0.042191 | 0.07218 | 0.18414 | 0.1289 | 0.086714 | -0.024788 | -0.052025 | -0.013109 | -0.2909 | 0.19788 | 0.09469 | 0.1078 | 0.044067 | -0.63494 | 122.5102 | 122.4133 | 122.386 | 0.41343 | -122.3959 | 122.1471 | 122.4821 | 121.8031 | 0.41239 | -122.4512
1117.7031 | 122.3465 | -0.21057 | 122.1771 | 1.4211e-13 | -0.0062991 | 0.0016666 | 0.063759 | -0.0085979 | 0.058644 | 0.0016025 | -0.0026725 | -0.0014913 | 0.070647 | 0.024587 | 0.059566 | -0.049315 | 0.18455 | -0.10913 | 122.2722 | 122.1798 | 122.148 | -0.20042 | -0.044739 | 0.16977 | -0.14335 | 121.9137 | 122.2441 | 121.5376 | -0.25572 | 0.010146 | 0.095068 | 0.16126 | 0.10144 | 0.091293 | 0.002679 | -0.029137 | -0.045154 | -0.26344 | 0.16583 | 0.067224 | 0.11238 | 0.066955 | -0.63953 | 122.4828 | 122.3904 | 122.3586 | 0.39512 | -122.3775 | 122.1243 | 122.4547 | 121.7482 | 0.38034 | -122.4328
1119.4531 | 122.3465 | -0.2243 | 122.168 | 1.4211e-13 | -0.0062991 | 0.0018804 | 0.064186 | -0.0085979 | 0.059071 | 0.0016025 | -0.0024589 | -0.0014913 | 0.070861 | 0.024801 | 0.059566 | -0.040158 | 0.18913 | -0.10455 | 122.2676 | 122.189 | 122.1526 | -0.19127 | -0.040161 | 0.17435 | -0.14335 | 121.9137 | 122.2487 | 121.5193 | -0.25115 | 0.033037 | 0.099644 | 0.18415 | 0.11975 | 0.086714 | 0.020991 | -0.015403 | -0.026842 | -0.25428 | 0.18414 | 0.080957 | 0.1078 | 0.080689 | -0.64869 | 122.4919 | 122.4133 | 122.3769 | 0.41343 | -122.3592 | 122.138 | 122.473 | 121.7436 | 0.39865 | -122.4191
1121.1875 | 122.3419 | -0.24261 | 122.1863 | 1.4211e-13 | -0.0062991 | 0.0023076 | 0.063973 | -0.0085979 | 0.05843 | -0.006028 | -0.0022453 | -0.0012777 | 0.070647 | 0.025015 | 0.059139 | -0.049315 | 0.17539 | -0.10455 | 122.2813 | 122.189 | 122.1617 | -0.19127 | -0.035582 | 0.18351 | -0.14335 | 121.9183 | 122.2487 | 121.533 | -0.25572 | 0.051348 | 0.095069 | 0.1933 | 0.13806 | 0.086714 | 0.002681 | -0.024556 | -0.01311 | -0.26801 | 0.20703 | 0.099268 | 0.11238 | 0.062379 | -0.65326 | 122.524 | 122.4316 | 122.4043 | 0.41801 | -122.3775 | 122.1609 | 122.4913 | 121.7756 | 0.42612 | -122.442
1122.9531 | 122.2916 | -0.21515 | 122.1909 | 1.4211e-13 | -0.0060855 | 0.0016666 | 0.063759 | -0.0083841 | 0.058858 | -0.006028 | -0.0026725 | -0.0012777 | 0.070647 | 0.024587 | 0.059353 | -0.049315 | 0.16624 | -0.11829 | 122.2722 | 122.1798 | 122.1526 | -0.21874 | -0.058476 | 0.18351 | -0.1525 | 121.9137 | 122.2349 | 121.5101 | -0.26488 | -0.003592 | 0.081335 | 0.16583 | 0.096861 | 0.10045 | -0.011054 | -0.038291 | -0.049734 | -0.27717 | 0.15667 | 0.062645 | 0.11238 | 0.044065 | -0.68073 | 122.4873 | 122.395 | 122.3677 | 0.38138 | -122.4096 | 122.1288 | 122.4501 | 121.7253 | 0.39866 | -122.4557
1124.6406 | 122.2961 | -0.23804 | 122.2092 | 1.4211e-13 | -0.0062991 | 0.002094 | 0.063759 | -0.0090251 | 0.059071 | -0.006028 | -0.0024589 | -0.0017051 | 0.070647 | 0.024801 | 0.059566 | -0.053893 | 0.17997 | -0.11371 | 122.2768 | 122.1844 | 122.1526 | -0.19585 | -0.044739 | 0.18351 | -0.15708 | 121.9183 | 122.2395 | 121.5193 | -0.2603 | 0.042191 | 0.067603 | 0.18414 | 0.12433 | 0.082136 | -0.024786 | -0.056601 | -0.022267 | -0.2909 | 0.1933 | 0.080954 | 0.10322 | 0.030334 | -0.68988 | 122.5148 | 122.4224 | 122.3906 | 0.41801 | -122.405 | 122.1563 | 122.4775 | 121.7573 | 0.42154 | -122.4695
1126.3906 | 122.4014 | -0.20599 | 122.1863 | 1.4211e-13 | -0.0065127 | 0.0018804 | 0.063759 | -0.0088115 | 0.059071 | -0.013659 | -0.0022453 | -0.0014913 | 0.070861 | 0.025015 | 0.059566 | -0.049315 | 0.16166 | -0.10913 | 122.2722 | 122.189 | 122.1617 | -0.21874 | -0.044739 | 0.16977 | -0.1525 | 121.9137 | 122.2487 | 121.533 | -0.26488 | -0.012747 | 0.085913 | 0.15668 | 0.096862 | 0.10961 | 0.002681 | -0.024556 | -0.058889 | -0.27259 | 0.16126 | 0.05349 | 0.11238 | 0.062379 | -0.65326 | 122.4782 | 122.395 | 122.3677 | 0.36765 | -122.405 | 122.1197 | 122.4547 | 121.739 | 0.37577 | -122.4512
1128.1406 | 122.3648 | -0.23346 | 122.168 | 1.4211e-13 | -0.0062991 | 0.002094 | 0.064186 | -0.0090251 | 0.058644 | 0.0016025 | -0.0022453 | -0.0012777 | 0.070861 | 0.024801 | 0.059566 | -0.058472 | 0.17539 | -0.11371 | 122.2813 | 122.1844 | 122.1571 | -0.19127 | -0.044739 | 0.17893 | -0.14793 | 121.9091 | 122.2441 | 121.5376 | -0.26488 | 0.042192 | 0.11338 | 0.17499 | 0.11975 | 0.077557 | 0.016412 | -0.010825 | -0.031424 | -0.25886 | 0.18872 | 0.085534 | 0.11696 | 0.07611 | -0.63037 | 122.5148 | 122.4178 | 122.3906 | 0.40885 | -122.3592 | 122.1426 | 122.4775 | 121.7711 | 0.41239 | -122.4329
1129.8906 | 122.4609 | -0.1831 | 122.1634 | 1.4211e-13 | -0.0062991 | 0.002094 | 0.063973 | -0.0088115 | 0.058858 | 0.0016025 | -0.0028861 | -0.0014913 | 0.070861 | 0.024801 | 0.059566 | -0.053893 | 0.16166 | -0.11829 | 122.2768 | 122.1844 | 122.1617 | -0.20958 | -0.044739 | 0.17893 | -0.15708 | 121.9183 | 122.2487 | 121.5422 | -0.2603 | -0.026478 | 0.11338 | 0.12921 | 0.064817 | 0.091295 | 0.02099 | -0.001668 | -0.077199 | -0.24513 | 0.13837 | 0.026022 | 0.10322 | 0.085267 | -0.62122 | 122.4599 | 122.3675 | 122.3448 | 0.34476 | -122.373 | 122.1014 | 122.4318 | 121.7253 | 0.36203 | -122.4237
1131.5938 | 122.4014 | -0.21515 | 122.1725 | 1.4211e-13 | -0.0062991 | 0.002094 | 0.063973 | -0.0088115 | 0.058858 | -0.006028 | -0.0028861 | -0.0014913 | 0.070861 | 0.025015 | 0.059566 | -0.053893 | 0.16166 | -0.11371 | 122.2722 | 122.1981 | 122.1571 | -0.21874 | -0.053897 | 0.17893 | -0.14793 | 121.9274 | 122.2532 | 121.5605 | -0.26488 | -0.003592 | 0.099646 | 0.16126 | 0.10144 | 0.10503 | 0.025572 | -0.015402 | -0.049734 | -0.24512 | 0.16125 | 0.067224 | 0.11696 | 0.080691 | -0.61206 | 122.4873 | 122.4133 | 122.3723 | 0.37681 | -122.3913 | 122.1426 | 122.4684 | 121.7756 | 0.39408 | -122.4374
1133.3438 | 122.3694 | -0.24719 | 122.168 | 1.4211e-13 | -0.0060855 | 0.002094 | 0.064186 | -0.0085979 | 0.059071 | -0.006028 | -0.0024589 | -0.0017051 | 0.070861 | 0.024801 | 0.059353 | -0.053893 | 0.18913 | -0.11829 | 122.2768 | 122.1844 | 122.1663 | -0.23248 | -0.053897 | 0.17893 | -0.15708 | 121.9228 | 122.2441 | 121.5513 | -0.25572 | 0.014715 | 0.1088 | 0.1933 | 0.1289 | 0.11419 | 0.016412 | -0.001667 | -0.008533 | -0.24513 | 0.19329 | 0.090109 | 0.098642 | 0.07611 | -0.61664 | 122.524 | 122.4316 | 122.4135 | 0.43632 | -122.4004 | 122.17 | 122.4913 | 121.7985 | 0.42612 | -122.4237
1135.0938 | 122.4609 | -0.20142 | 122.1497 | 1.4211e-13 | -0.0065127 | 0.002094 | 0.064186 | -0.0085979 | 0.058858 | 0.0016025 | -0.0026725 | -0.0012777 | 0.070647 | 0.025015 | 0.059353 | -0.053893 | 0.22118 | -0.10455 | 122.2813 | 122.1844 | 122.1617 | -0.18669 | -0.049318 | 0.18351 | -0.14335 | 121.9183 | 122.2578 | 121.5468 | -0.27404 | 0.014728 | 0.13169 | 0.14752 | 0.096863 | 0.082135 | 0.034723 | 0.012065 | -0.072624 | -0.23139 | 0.1521 | 0.058069 | 0.13069 | 0.10816 | -0.6029 | 122.4828 | 122.3858 | 122.3631 | 0.42259 | -122.3363 | 122.1197 | 122.4592 | 121.7482 | 0.38492 | -122.4237
1136.8438 | 122.3694 | -0.21515 | 122.1909 | 1.4211e-13 | -0.0062991 | 0.0018804 | 0.064186 | -0.0085979 | 0.058858 | -0.006028 | -0.0022453 | -0.0014913 | 0.070861 | 0.024801 | 0.059566 | -0.053893 | 0.24865 | -0.10455 | 122.2813 | 122.1981 | 122.1663 | -0.20042 | -0.044739 | 0.17435 | -0.14335 | 121.9228 | 122.2487 | 121.5605 | -0.2603 | 0.014724 | 0.090491 | 0.16126 | 0.1106 | 0.095872 | 0.007261 | -0.024555 | -0.045155 | -0.26801 | 0.17041 | 0.071802 | 0.11696 | 0.057801 | -0.63037 | 122.4965 | 122.4133 | 122.3815 | 0.4638 | -122.3913 | 122.138 | 122.4638 | 121.7756 | 0.3895 | -122.4512
1138.5469 | 122.4152 | -0.21973 | 122.168 | 1.4211e-13 | -0.0062991 | 0.002094 | 0.063973 | -0.0085979 | 0.059071 | 0.0016025 | -0.0024589 | -0.0017051 | 0.070647 | 0.024801 | 0.059353 | -0.053893 | 0.24407 | -0.11371 | 122.2859 | 122.1935 | 122.1755 | -0.17753 | -0.044739 | 0.17893 | -0.15708 | 121.9366 | 122.267 | 121.5742 | -0.2603 | 0.042197 | 0.11796 | 0.16583 | 0.10602 | 0.06382 | 0.02557 | 0.00749 | -0.040577 | -0.23139 | 0.17499 | 0.062644 | 0.10322 | 0.099003 | -0.59374 | 122.5057 | 122.4133 | 122.3952 | 0.4638 | -122.3455 | 122.1563 | 122.4867 | 121.794 | 0.39866 | -122.4283
1140.2969 | 122.4426 | -0.18768 | 122.168 | 1.4211e-13 | -0.0058717 | 0.0016666 | 0.063973 | -0.0085979 | 0.05843 | -0.006028 | -0.0022453 | -0.0014913 | 0.070647 | 0.024587 | 0.059139 | -0.040158 | 0.27154 | -0.10455 | 122.2997 | 122.2073 | 122.18 | -0.15464 | -0.035582 | 0.17893 | -0.14793 | 121.9366 | 122.2716 | 121.5742 | -0.25115 | 0.033047 | 0.13169 | 0.14752 | 0.08313 | 0.050083 | 0.039307 | 0.012068 | -0.063463 | -0.23139 | 0.1521 | 0.039758 | 0.10322 | 0.10358 | -0.59374 | 122.4873 | 122.395 | 122.3677 | 0.45923 | -122.3226 | 122.1243 | 122.4592 | 121.7619 | 0.36661 | -122.4191
1142.0312 | 122.4197 | -0.20142 | 122.1634 | 1.4211e-13 | -0.0065127 | 0.0018804 | 0.063759 | -0.0083841 | 0.059071 | 0.0092325 | -0.0026725 | -0.0012777 | 0.070647 | 0.025015 | 0.059353 | -0.040158 | 0.27612 | -0.10455 | 122.2905 | 122.2027 | 122.18 | -0.21416 | -0.044739 | 0.17893 | -0.1525 | 121.9274 | 122.2716 | 121.6017 | -0.25115 | -0.012746 | 0.12711 | 0.16126 | 0.096863 | 0.10961 | 0.039306 | 0.016646 | -0.04973 | -0.23597 | 0.15668 | 0.048912 | 0.098642 | 0.10816 | -0.56169 | 122.4919 | 122.4041 | 122.3815 | 0.47754 | -122.3776 | 122.1288 | 122.473 | 121.8031 | 0.38035 | -122.4145
1143.7812 | 122.4106 | -0.18768 | 122.1909 | 1.4211e-13 | -0.0067265 | 0.002094 | 0.063973 | -0.0088115 | 0.058858 | -0.006028 | -0.0022453 | -0.0014913 | 0.070647 | 0.024801 | 0.059353 | -0.044736 | 0.28528 | -0.10913 | 122.2951 | 122.1981 | 122.18 | -0.205 | -0.049318 | 0.17435 | -0.14335 | 121.9366 | 122.2716 | 121.5696 | -0.2603 | -0.017321 | 0.10423 | 0.14295 | 0.078551 | 0.095872 | 0.007261 | -0.01082 | -0.072621 | -0.25428 | 0.13836 | 0.044336 | 0.11696 | 0.080694 | -0.62121 | 122.4828 | 122.3858 | 122.3677 | 0.47296 | -122.3959 | 122.1243 | 122.4592 | 121.7573 | 0.36203 | -122.4512
1145.4688 | 122.4289 | -0.22888 | 122.1588 | 1.4211e-13 | -0.0062991 | 0.002094 | 0.064186 | -0.0085979 | 0.058858 | -0.006028 | -0.0028861 | -0.0014913 | 0.070647 | 0.025015 | 0.059566 | -0.044736 | 0.30359 | -0.10913 | 122.2951 | 122.2073 | 122.1755 | -0.20042 | -0.044739 | 0.18351 | -0.14335 | 121.932 | 122.2716 | 121.5742 | -0.25572 | 0.028457 | 0.13627 | 0.18415 | 0.11975 | 0.091293 | 0.048463 | 0.016646 | -0.026843 | -0.22681 | 0.18414 | 0.085535 | 0.11238 | 0.11274 | -0.58459 | 122.524 | 122.4362 | 122.4043 | 0.53248 | -122.3592 | 122.1609 | 122.5004 | 121.8031 | 0.41239 | -122.4145
1147.2031 | 122.4701 | -0.1831 | 122.1771 | 1.4211e-13 | -0.0058717 | 0.002094 | 0.064186 | -0.0085979 | 0.059071 | -0.013659 | -0.0022453 | -0.0014913 | 0.070861 | 0.024801 | 0.058925 | -0.044736 | 0.30817 | -0.11371 | 122.2859 | 122.1935 | 122.1755 | -0.20958 | -0.044739 | 0.18351 | -0.1525 | 121.9274 | 122.2578 | 121.5513 | -0.26488 | -0.026478 | 0.1088 | 0.13837 | 0.069395 | 0.095873 | 0.016415 | -0.001665 | -0.081778 | -0.2497 | 0.13837 | 0.030601 | 0.11238 | 0.080691 | -0.62579 | 122.469 | 122.3766 | 122.3586 | 0.49128 | -122.3867 | 122.1105 | 122.4409 | 121.7344 | 0.36661 | -122.442
1148.9688 | 122.3282 | -0.23804 | 122.2321 | 1.4211e-13 | -0.0065127 | 0.002094 | 0.064614 | -0.0083841 | 0.059071 | 0.0016025 | -0.0022453 | -0.0017051 | 0.070647 | 0.025015 | 0.059353 | -0.03558 | 0.31733 | -0.10455 | 122.2951 | 122.2073 | 122.1846 | -0.15464 | -0.049318 | 0.18351 | -0.14793 | 121.932 | 122.267 | 121.5605 | -0.25572 | 0.083401 | 0.063028 | 0.20246 | 0.13348 | 0.050083 | -0.02478 | -0.04744 | -0.017688 | -0.30006 | 0.18872 | 0.090112 | 0.1078 | 0.034916 | -0.67157 | 122.5331 | 122.4453 | 122.4227 | 0.55537 | -122.3867 | 122.17 | 122.505 | 121.7985 | 0.42154 | -122.4878
1150.6562 | 122.4609 | -0.16937 | 122.1863 | 1.4211e-13 | -0.0062991 | 0.0023076 | 0.064186 | -0.0085979 | 0.05843 | -0.006028 | -0.0022453 | -0.0014913 | 0.070433 | 0.024587 | 0.059353 | -0.026423 | 0.3448 | -0.099975 | 122.2997 | 122.2256 | 122.1938 | -0.20042 | -0.044739 | 0.17893 | -0.13877 | 121.9549 | 122.267 | 121.5834 | -0.25572 | -0.031052 | 0.11338 | 0.14295 | 0.069398 | 0.10045 | 0.039313 | 0.007494 | -0.086352 | -0.23139 | 0.12463 | 0.030605 | 0.11696 | 0.080693 | -0.6029 | 122.469 | 122.395 | 122.3631 | 0.51418 | -122.3867 | 122.1243 | 122.4363 | 121.7528 | 0.3483 | -122.442
1152.4062 | 122.3694 | -0.21057 | 122.2137 | 1.4211e-13 | -0.0065127 | 0.0025214 | 0.063759 | -0.0085979 | 0.058858 | -0.006028 | -0.0024589 | -0.0014913 | 0.070861 | 0.024801 | 0.059353 | -0.03558 | 0.37227 | -0.10455 | 122.2997 | 122.2119 | 122.1938 | -0.205 | -0.035582 | 0.18809 | -0.14335 | 121.9457 | 122.2807 | 121.5834 | -0.25572 | 0.005567 | 0.085917 | 0.17499 | 0.10602 | 0.10045 | -0.00189 | -0.019972 | -0.045154 | -0.26801 | 0.17499 | 0.067224 | 0.11238 | 0.066963 | -0.63036 | 122.5102 | 122.4224 | 122.4043 | 0.58284 | -122.4187 | 122.1563 | 122.4913 | 121.794 | 0.39866 | -122.4695
1154.1562 | 122.4518 | -0.18768 | 122.1863 | 1.4211e-13 | -0.0062991 | 0.0018804 | 0.063973 | -0.0085979 | 0.058858 | -0.013659 | -0.0026725 | -0.0012777 | 0.070647 | 0.025015 | 0.059139 | -0.026423 | 0.36769 | -0.099975 | 122.2997 | 122.221 | 122.2029 | -0.17753 | -0.040161 | 0.18351 | -0.13877 | 121.9503 | 122.2807 | 121.5651 | -0.25572 | 0.010153 | 0.11338 | 0.16126 | 0.087708 | 0.077555 | 0.034734 | 0.016652 | -0.068042 | -0.23596 | 0.14752 | 0.048915 | 0.11696 | 0.094429 | -0.62121 | 122.4873 | 122.4087 | 122.3906 | 0.55538 | -122.3638 | 122.138 | 122.4684 | 121.7528 | 0.37119 | -122.442
1155.9219 | 122.3969 | -0.20599 | 122.2275 | 1.4211e-13 | -0.0060855 | 0.0023076 | 0.063759 | -0.0088115 | 0.059071 | -0.013659 | -0.0026725 | -0.0014913 | 0.070647 | 0.024801 | 0.059353 | -0.026423 | 0.30817 | -0.099975 | 122.2997 | 122.2302 | 122.1938 | -0.15006 | -0.035582 | 0.17435 | -0.13877 | 121.9457 | 122.2899 | 121.6063 | -0.24657 | 0.055937 | 0.072184 | 0.17957 | 0.10602 | 0.050082 | 0.002693 | -0.033705 | -0.040573 | -0.28174 | 0.17041 | 0.067226 | 0.1078 | 0.062387 | -0.6212 | 122.5057 | 122.4362 | 122.3998 | 0.51417 | -122.3775 | 122.1517 | 122.4959 | 121.8123 | 0.38034 | -122.474
1157.6094 | 122.3282 | -0.2243 | 122.2458 | 1.4211e-13 | -0.0062991 | 0.0018804 | 0.064186 | -0.0090251 | 0.058858 | -0.013659 | -0.0026725 | -0.0014913 | 0.070861 | 0.024587 | 0.059353 | -0.021844 | 0.32649 | -0.10455 | 122.3134 | 122.2302 | 122.2075 | -0.15921 | -0.035582 | 0.17893 | -0.13877 | 121.9595 | 122.2944 | 121.5742 | -0.24199 | 0.065089 | 0.067608 | 0.20246 | 0.11975 | 0.054662 | -0.015618 | -0.03828 | -0.017685 | -0.28632 | 0.18872 | 0.085536 | 0.10322 | 0.048655 | -0.67156 | 122.5377 | 122.4545 | 122.4318 | 0.55079 | -122.405 | 122.1838 | 122.5187 | 121.7985 | 0.40323 | -122.4878
1159.3594 | 122.3831 | -0.21515 | 122.2366 | 1.4211e-13 | -0.0058717 | 0.002094 | 0.0644 | -0.0085979 | 0.059071 | -0.013659 | -0.0026725 | -0.0017051 | 0.070861 | 0.025015 | 0.059353 | -0.021844 | 0.35396 | -0.095397 | 122.3134 | 122.2302 | 122.2029 | -0.118 | -0.031003 | 0.18351 | -0.12503 | 121.9595 | 122.2899 | 121.6109 | -0.23741 | 0.097145 | 0.076764 | 0.19331 | 0.11975 | 0.022607 | -0.006462 | -0.033702 | -0.022261 | -0.27716 | 0.18415 | 0.090117 | 0.11238 | 0.053232 | -0.62578 | 122.5285 | 122.4453 | 122.4181 | 0.56911 | -122.3546 | 122.1746 | 122.505 | 121.826 | 0.39866 | -122.474
1161.0938 | 122.3282 | -0.22888 | 122.2458 | 1.4211e-13 | -0.0062991 | 0.0023076 | 0.063973 | -0.0085979 | 0.058858 | 0.0092325 | -0.0024589 | -0.0017051 | 0.070647 | 0.025015 | 0.059353 | -0.026423 | 0.3448 | -0.10455 | 122.3226 | 122.2393 | 122.2121 | -0.10427 | -0.026425 | 0.17893 | -0.12961 | 121.9686 | 122.2899 | 121.5651 | -0.23741 | 0.12461 | 0.076765 | 0.20246 | 0.12433 | -0.000285 | -0.00646 | -0.033701 | -0.008528 | -0.27716 | 0.20246 | 0.099272 | 0.1078 | 0.044076 | -0.68072 | 122.5514 | 122.4682 | 122.441 | 0.57368 | -122.3501 | 122.1975 | 122.5187 | 121.794 | 0.40781 | -122.4832
1162.8438 | 122.3969 | -0.20142 | 122.2229 | 1.4211e-13 | -0.0065127 | 0.002094 | 0.064186 | -0.0085979 | 0.059071 | -0.006028 | -0.0024589 | -0.0012777 | 0.070433 | 0.024587 | 0.059353 | -0.017266 | 0.3448 | -0.08624 | 122.318 | 122.2393 | 122.2167 | -0.090531 | -0.031003 | 0.18809 | -0.12961 | 121.9641 | 122.2944 | 121.5742 | -0.24657 | 0.11089 | 0.095076 | 0.18415 | 0.11518 | 0.004291 | 0.016429 | -0.006234 | -0.045151 | -0.25885 | 0.17041 | 0.071806 | 0.11696 | 0.071544 | -0.64867 | 122.5194 | 122.4407 | 122.4181 | 0.54622 | -122.3134 | 122.1655 | 122.4959 | 121.7756 | 0.3895 | -122.4695
1164.5312 | 122.4701 | -0.18768 | 122.1863 | 1.4211e-13 | -0.0065127 | 0.002094 | 0.064186 | -0.0085979 | 0.058858 | 0.0092325 | -0.0024589 | -0.0012777 | 0.070647 | 0.024801 | 0.058925 | -0.017266 | 0.34938 | -0.10455 | 122.3226 | 122.2302 | 122.2075 | -0.16379 | -0.035582 | 0.17435 | -0.13877 | 121.9503 | 122.2853 | 121.6154 | -0.24199 | 0.023889 | 0.13627 | 0.17042 | 0.08313 | 0.059241 | 0.043892 | 0.02123 | -0.054306 | -0.23596 | 0.1521 | 0.048915 | 0.10322 | 0.099008 | -0.57085 | 122.5102 | 122.4179 | 122.3952 | 0.53706 | -122.3501 | 122.138 | 122.473 | 121.8031 | 0.36203 | -122.4283
1166.2656 | 122.4106 | -0.19684 | 122.1954 | 1.4211e-13 | -0.0060855 | 0.002094 | 0.064186 | -0.0085979 | 0.058858 | -0.006028 | -0.0026725 | -0.0012777 | 0.070647 | 0.024587 | 0.059139 | -0.017266 | 0.37685 | -0.10455 | 122.318 | 122.2256 | 122.2121 | -0.16837 | -0.035582 | 0.18809 | -0.13419 | 121.9549 | 122.2944 | 121.588 | -0.24199 | 0.028465 | 0.12254 | 0.17957 | 0.092285 | 0.06382 | 0.030157 | 0.016653 | -0.045151 | -0.24054 | 0.16126 | 0.062649 | 0.1078 | 0.099009 | -0.60747 | 122.5148 | 122.4224 | 122.4089 | 0.57369 | -122.3638 | 122.1517 | 122.4913 | 121.7848 | 0.38492 | -122.4374
1168.0156 | 122.4197 | -0.19226 | 122.2092 | 1.4211e-13 | -0.0062991 | 0.0023076 | 0.063973 | -0.0083841 | 0.059285 | -0.006028 | -0.0026725 | -0.0014913 | 0.070861 | 0.024801 | 0.059353 | -0.003531 | 0.41348 | -0.10455 | 122.318 | 122.2348 | 122.2167 | -0.15921 | -0.035582 | 0.17893 | -0.13877 | 121.9641 | 122.3036 | 121.5925 | -0.24199 | 0.033046 | 0.10881 | 0.18873 | 0.087708 | 0.054662 | 0.025583 | 0.007499 | -0.049728 | -0.24512 | 0.15668 | 0.053493 | 0.10322 | 0.094434 | -0.61663 | 122.5102 | 122.427 | 122.4089 | 0.60574 | -122.3684 | 122.1563 | 122.4959 | 121.7848 | 0.37119 | -122.4512
1169.7031 | 122.4655 | -0.15564 | 122.1817 | 1.4211e-13 | -0.0062991 | 0.002094 | 0.063973 | -0.0088115 | 0.05843 | -0.006028 | -0.0028861 | -0.0017051 | 0.070647 | 0.025015 | 0.059139 | -0.003531 | 0.45011 | -0.10455 | 122.3226 | 122.2348 | 122.2167 | -0.10427 | -0.031003 | 0.19724 | -0.13419 | 121.9686 | 122.299 | 121.6063 | -0.23283 | 0.051372 | 0.14085 | 0.15211 | 0.051087 | -0.000285 | 0.053048 | 0.034964 | -0.077191 | -0.21307 | 0.12464 | 0.021451 | 0.098642 | 0.11732 | -0.57543 | 122.4782 | 122.3904 | 122.3723 | 0.60575 | -122.286 | 122.1243 | 122.4547 | 121.7619 | 0.35288 | -122.4145
1171.4531 | 122.3373 | -0.22888 | 122.2458 | 1.4211e-13 | -0.0058717 | 0.0018804 | 0.0644 | -0.0088115 | 0.058858 | 0.0016025 | -0.0022453 | -0.0017051 | 0.070647 | 0.025015 | 0.059566 | 0.001048 | 0.56 | -0.10455 | 122.3271 | 122.2393 | 122.2167 | -0.085952 | -0.031003 | 0.18351 | -0.13419 | 121.9641 | 122.3036 | 121.5925 | -0.23283 | 0.14293 | 0.081343 | 0.22993 | 0.12433 | -0.018601 | -0.00646 | -0.029123 | -0.003949 | -0.28174 | 0.19788 | 0.094693 | 0.098642 | 0.057812 | -0.65325 | 122.556 | 122.4682 | 122.4455 | 0.78888 | -122.3317 | 122.1929 | 122.5325 | 121.8214 | 0.41239 | -122.4786
1173.2031 | 122.4197 | -0.17853 | 122.2183 | 1.4211e-13 | -0.0065127 | 0.0023076 | 0.063973 | -0.0085979 | 0.058858 | 0.0016025 | -0.0026725 | -0.0012777 | 0.070861 | 0.025015 | 0.059139 | 0.005626 | 0.65615 | -0.095397 | 122.3271 | 122.2485 | 122.2304 | -0.085952 | -0.012689 | 0.18351 | -0.12961 | 121.9824 | 122.3128 | 121.6017 | -0.23283 | 0.092576 | 0.10881 | 0.18415 | 0.083131 | -0.009445 | 0.030163 | 0.012079 | -0.054303 | -0.23596 | 0.16584 | 0.048918 | 0.10322 | 0.094435 | -0.61662 | 122.5057 | 122.427 | 122.4089 | 0.83468 | -122.3043 | 122.1609 | 122.4913 | 121.7802 | 0.36203 | -122.4512
1174.8906 | 122.4792 | -0.16022 | 122.2092 | 1.4211e-13 | -0.0065127 | 0.002094 | 0.064186 | -0.0090251 | 0.059071 | 0.0016025 | -0.0024589 | -0.0012777 | 0.070861 | 0.025015 | 0.059566 | 0.005626 | 0.83929 | -0.095397 | 122.3363 | 122.2485 | 122.2304 | -0.072215 | -0.017267 | 0.18351 | -0.12503 | 121.9732 | 122.3128 | 121.6109 | -0.23283 | 0.088002 | 0.12712 | 0.16584 | 0.06482 | -0.023182 | 0.039319 | 0.021235 | -0.072614 | -0.23596 | 0.14295 | 0.035185 | 0.1078 | 0.10359 | -0.59831 | 122.4965 | 122.4087 | 122.3906 | 0.99951 | -122.2814 | 122.1334 | 122.473 | 121.7711 | 0.34372 | -122.442
1176.6406 | 122.3373 | -0.2243 | 122.2549 | 1.4211e-13 | -0.0065127 | 0.0023076 | 0.064186 | -0.0083841 | 0.058858 | 0.0016025 | -0.0026725 | -0.0012777 | 0.070647 | 0.025015 | 0.059353 | 0.010204 | 0.98581 | -0.099975 | 122.3409 | 122.2393 | 122.2258 | -0.076794 | -0.026425 | 0.18809 | -0.12045 | 121.9778 | 122.3082 | 121.6154 | -0.2191 | 0.14751 | 0.085923 | 0.23451 | 0.12433 | -0.023181 | -0.015615 | -0.02912 | 0.005209 | -0.27716 | 0.19788 | 0.10385 | 0.098642 | 0.053236 | -0.63951 | 122.5652 | 122.4636 | 122.4501 | 1.2101 | -122.3317 | 122.2021 | 122.5325 | 121.8397 | 0.41239 | -122.474
1178.3906 | 122.4747 | -0.16937 | 122.2366 | 1.4211e-13 | -0.0065127 | 0.0023076 | 0.0644 | -0.0090251 | 0.058858 | 0.016863 | -0.0026725 | -0.0012777 | 0.071074 | 0.025015 | 0.059353 | 0.005626 | 1.0636 | -0.090818 | 122.3271 | 122.2439 | 122.235 | -0.053899 | -0.031003 | 0.17893 | -0.12503 | 121.9778 | 122.3219 | 121.6612 | -0.22825 | 0.11547 | 0.090499 | 0.175 | 0.078555 | -0.036919 | 0.007274 | -0.001652 | -0.058879 | -0.25885 | 0.13837 | 0.044341 | 0.10322 | 0.085283 | -0.57541 | 122.4965 | 122.4133 | 122.4044 | 1.233 | -122.2905 | 122.1472 | 122.4913 | 121.8306 | 0.3483 | -122.4649
1180.0781 | 122.374 | -0.20599 | 122.2687 | 1.4211e-13 | -0.0067265 | 0.002094 | 0.064186 | -0.0090251 | 0.05843 | 0.0016025 | -0.0022453 | -0.0017051 | 0.070861 | 0.025228 | 0.059139 | 0.005626 | 1.1644 | -0.095397 | 122.3409 | 122.2531 | 122.235 | -0.026426 | -0.021846 | 0.17893 | -0.12503 | 121.9732 | 122.3128 | 121.62 | -0.23283 | 0.17957 | 0.07219 | 0.21162 | 0.1106 | -0.068971 | -0.015612 | -0.033696 | -0.026837 | -0.29547 | 0.18415 | 0.080962 | 0.1078 | 0.044081 | -0.64866 | 122.5469 | 122.4591 | 122.441 | 1.3704 | -122.2951 | 122.1792 | 122.5188 | 121.826 | 0.38492 | -122.5015
1181.8281 | 122.4655 | -0.14648 | 122.2366 | 1.4211e-13 | -0.0062991 | 0.0018804 | 0.0644 | -0.0088115 | 0.058644 | 0.0016025 | -0.0026725 | -0.0017051 | 0.070861 | 0.025442 | 0.059139 | 0.005626 | 1.201 | -0.10455 | 122.3271 | 122.2668 | 122.2396 | -0.058478 | -0.021846 | 0.18809 | -0.13419 | 121.9824 | 122.3173 | 121.62 | -0.23283 | 0.088006 | 0.090499 | 0.15211 | 0.041931 | -0.046075 | 0.030169 | 0.002926 | -0.086347 | -0.25427 | 0.12464 | 0.012295 | 0.098642 | 0.080704 | -0.61662 | 122.4736 | 122.4133 | 122.386 | 1.3475 | -122.2951 | 122.1288 | 122.4638 | 121.7665 | 0.33457 | -122.4695
1183.5312 | 122.3877 | -0.22888 | 122.2595 | 1.4211e-13 | -0.0062991 | 0.0025214 | 0.064186 | -0.0083841 | 0.059071 | -0.006028 | -0.0024589 | -0.0017051 | 0.070861 | 0.025442 | 0.059353 | 0.010204 | 1.3796 | -0.095397 | 122.3409 | 122.2576 | 122.2396 | -0.09511 | -0.026425 | 0.19267 | -0.12503 | 121.9778 | 122.3173 | 121.6475 | -0.22825 | 0.13377 | 0.081346 | 0.23909 | 0.13349 | -0.000287 | -0.001877 | -0.019962 | 0.00063 | -0.28174 | 0.20246 | 0.10385 | 0.10322 | 0.057816 | -0.61204 | 122.5697 | 122.4865 | 122.4684 | 1.6084 | -122.3546 | 122.2067 | 122.5462 | 121.8764 | 0.42155 | -122.4878
1185.2812 | 122.4564 | -0.16937 | 122.2137 | 1.4211e-13 | -0.0065127 | 0.0025214 | 0.064186 | -0.0092389 | 0.058858 | -0.006028 | -0.0026725 | -0.0017051 | 0.070861 | 0.025228 | 0.059139 | 0.023939 | 1.5169 | -0.095397 | 122.3363 | 122.2576 | 122.2396 | -0.049321 | -0.017267 | 0.18351 | -0.12503 | 121.9778 | 122.3265 | 121.6109 | -0.22825 | 0.12005 | 0.12254 | 0.19331 | 0.073976 | -0.046076 | 0.043899 | 0.025814 | -0.058879 | -0.23596 | 0.15211 | 0.044341 | 0.10322 | 0.11275 | -0.60289 | 122.5057 | 122.427 | 122.4089 | 1.6863 | -122.2631 | 122.1472 | 122.4959 | 121.7802 | 0.35288 | -122.442
1187.0312 | 122.3282 | -0.21515 | 122.2549 | 1.4211e-13 | -0.0060855 | 0.002094 | 0.063973 | -0.0088115 | 0.058858 | -0.006028 | -0.0022453 | -0.0014913 | 0.070647 | 0.025228 | 0.058925 | 0.010204 | 1.6268 | -0.090818 | 122.3409 | 122.2576 | 122.235 | -0.040163 | -0.021846 | 0.18809 | -0.12961 | 121.9732 | 122.3219 | 121.6521 | -0.22825 | 0.17499 | 0.085923 | 0.22535 | 0.12433 | -0.050655 | 0.0027 | -0.019963 | -0.013103 | -0.28174 | 0.1933 | 0.085539 | 0.098642 | 0.066972 | -0.60288 | 122.556 | 122.4728 | 122.4501 | 1.842 | -122.2951 | 122.1884 | 122.5371 | 121.8672 | 0.40324 | -122.4832
1188.7188 | 122.4426 | -0.16479 | 122.2092 | 1.4211e-13 | -0.0060855 | 0.0023076 | 0.064186 | -0.0090251 | 0.059071 | -0.006028 | -0.0024589 | -0.0019187 | 0.071074 | 0.024801 | 0.059139 | 0.014783 | 1.7916 | -0.090818 | 122.3409 | 122.2576 | 122.2396 | -0.067636 | -0.021846 | 0.19267 | -0.12045 | 121.9824 | 122.3265 | 121.6841 | -0.22825 | 0.097159 | 0.1317 | 0.17958 | 0.073977 | -0.023182 | 0.048477 | 0.030392 | -0.063457 | -0.2268 | 0.14295 | 0.044342 | 0.1078 | 0.11733 | -0.52505 | 122.5057 | 122.4224 | 122.4044 | 1.9564 | -122.2768 | 122.1472 | 122.4913 | 121.8489 | 0.35746 | -122.4374
1190.4688 | 122.4014 | -0.19684 | 122.2504 | 1.4211e-13 | -0.0067265 | 0.002094 | 0.063759 | -0.0083841 | 0.05843 | -0.013659 | -0.0022453 | -0.0014913 | 0.070647 | 0.025228 | 0.059139 | 0.014783 | 1.9015 | -0.095397 | 122.35 | 122.2668 | 122.2487 | -0.026426 | -0.017267 | 0.18809 | -0.12503 | 121.9869 | 122.3219 | 121.6521 | -0.22367 | 0.17041 | 0.099658 | 0.21162 | 0.10144 | -0.068971 | 0.016436 | -0.001649 | -0.026835 | -0.26342 | 0.17957 | 0.071806 | 0.098641 | 0.07155 | -0.5983 | 122.5469 | 122.4636 | 122.4456 | 2.0984 | -122.2768 | 122.1838 | 122.5188 | 121.8489 | 0.38492 | -122.474
1192.2031 | 122.3877 | -0.1831 | 122.2412 | 1.4211e-13 | -0.0065127 | 0.002094 | 0.0644 | -0.0085979 | 0.058858 | 0.0016025 | -0.0022453 | -0.0012777 | 0.070433 | 0.025015 | 0.058925 | 0.023939 | 2.0435 | -0.099975 | 122.3409 | 122.2668 | 122.2441 | -0.049321 | -0.026425 | 0.18809 | -0.12045 | 121.9869 | 122.3357 | 121.6704 | -0.22825 | 0.13378 | 0.099656 | 0.20704 | 0.08313 | -0.050654 | 0.025591 | 0.002927 | -0.045147 | -0.25427 | 0.15668 | 0.062652 | 0.1078 | 0.09444 | -0.57083 | 122.524 | 122.4499 | 122.4272 | 2.2266 | -122.2905 | 122.17 | 122.5188 | 121.8535 | 0.37119 | -122.4695
1193.9688 | 122.4472 | -0.16937 | 122.2183 | 1.4211e-13 | -0.0062991 | 0.002094 | 0.063973 | -0.0088115 | 0.058644 | 0.0016025 | -0.0026725 | -0.0010641 | 0.070861 | 0.025015 | 0.059566 | 0.014783 | 2.1488 | -0.090818 | 122.3454 | 122.2576 | 122.2533 | -0.031005 | -0.021846 | 0.17893 | -0.12503 | 121.9869 | 122.3265 | 121.6704 | -0.22367 | 0.13837 | 0.12712 | 0.18416 | 0.078555 | -0.059813 | 0.039321 | 0.034972 | -0.0543 | -0.23138 | 0.14753 | 0.044341 | 0.098641 | 0.10817 | -0.54795 | 122.5148 | 122.427 | 122.4227 | 2.3181 | -122.2493 | 122.1563 | 122.4959 | 121.8397 | 0.3483 | -122.442
1195.7188 | 122.4014 | -0.19226 | 122.2504 | 1.4211e-13 | -0.0062991 | 0.0025214 | 0.064186 | -0.0085979 | 0.058644 | 0.0016025 | -0.0024589 | -0.0017051 | 0.070647 | 0.025015 | 0.058925 | 0.019361 | 2.3319 | -0.08624 | 122.35 | 122.2622 | 122.2533 | -0.031005 | -0.021846 | 0.19267 | -0.12503 | 121.9961 | 122.3357 | 121.6704 | -0.2191 | 0.16126 | 0.099658 | 0.21162 | 0.10602 | -0.055235 | 0.011857 | 0.002929 | -0.026834 | -0.25427 | 0.17041 | 0.067229 | 0.094063 | 0.085285 | -0.57999 | 122.5423 | 122.4545 | 122.4456 | 2.5242 | -122.2814 | 122.1884 | 122.5279 | 121.8626 | 0.38493 | -122.4695
1197.4062 | 122.4655 | -0.1831 | 122.2366 | 1.4211e-13 | -0.0065127 | 0.0023076 | 0.064186 | -0.0088115 | 0.059071 | 0.0016025 | -0.0024589 | -0.0014913 | 0.070861 | 0.025228 | 0.059566 | 0.023939 | 2.6066 | -0.08624 | 122.3454 | 122.2714 | 122.2579 | -0.072215 | -0.017267 | 0.19724 | -0.1113 | 121.9961 | 122.3402 | 121.6978 | -0.22825 | 0.11089 | 0.10881 | 0.20704 | 0.096865 | -0.014025 | 0.034748 | 0.021241 | -0.045147 | -0.24053 | 0.16584 | 0.071809 | 0.11696 | 0.1036 | -0.53879 | 122.5286 | 122.4545 | 122.441 | 2.7897 | -122.3088 | 122.1792 | 122.5233 | 121.881 | 0.38035 | -122.4649
1199.1562 | 122.3557 | -0.20599 | 122.2824 | 1.4211e-13 | -0.0060855 | 0.002094 | 0.064186 | -0.0090251 | 0.058644 | 0.0016025 | -0.0022453 | -0.0014913 | 0.070647 | 0.025228 | 0.059139 | 0.019361 | 2.7211 | -0.08624 | 122.35 | 122.2714 | 122.2533 | -0.035584 | -0.026425 | 0.18809 | -0.12503 | 121.9961 | 122.3357 | 121.7024 | -0.22367 | 0.17041 | 0.067614 | 0.22535 | 0.11975 | -0.050656 | -0.011029 | -0.029115 | -0.017679 | -0.28631 | 0.17957 | 0.080962 | 0.098641 | 0.053241 | -0.57998 | 122.556 | 122.4774 | 122.4593 | 2.9271 | -122.318 | 122.2021 | 122.5416 | 121.9084 | 0.39408 | -122.5061
1200.9062 | 122.406 | -0.19684 | 122.2641 | 1.4211e-13 | -0.0062991 | 0.002094 | 0.064186 | -0.0085979 | 0.059071 | -0.006028 | -0.0024589 | -0.0014913 | 0.070861 | 0.025015 | 0.059139 | 0.014783 | 2.9592 | -0.072505 | 122.35 | 122.2714 | 122.2579 | -0.031005 | -0.017267 | 0.19267 | -0.11587 | 121.9915 | 122.3357 | 121.6704 | -0.2191 | 0.16583 | 0.085925 | 0.21162 | 0.12433 | -0.0415 | 0.007282 | -0.006225 | -0.022257 | -0.27258 | 0.17957 | 0.080964 | 0.10322 | 0.071552 | -0.59372 | 122.5469 | 122.4682 | 122.4547 | 3.156 | -122.2951 | 122.1884 | 122.5325 | 121.8672 | 0.3895 | -122.4832
1202.5938 | 122.4243 | -0.18768 | 122.2366 | 1.4211e-13 | -0.0065127 | 0.002094 | 0.063973 | -0.0085979 | 0.059285 | 0.0016025 | -0.0024589 | -0.0012777 | 0.070861 | 0.025228 | 0.059566 | 0.028518 | 3.037 | -0.067927 | 122.35 | 122.2714 | 122.2579 | -0.049321 | -0.026425 | 0.19267 | -0.12503 | 121.9961 | 122.3357 | 121.6475 | -0.21452 | 0.13836 | 0.11339 | 0.2162 | 0.11976 | -0.018606 | 0.034748 | 0.021241 | -0.026833 | -0.24053 | 0.16126 | 0.062651 | 0.089484 | 0.099018 | -0.58915 | 122.5377 | 122.4591 | 122.4456 | 3.2247 | -122.286 | 122.1838 | 122.5233 | 121.8352 | 0.38035 | -122.4511
1204.3438 | 122.3648 | -0.20142 | 122.2504 | 1.4211e-13 | -0.0062991 | 0.002094 | 0.064186 | -0.0090251 | 0.058858 | 0.0016025 | -0.0024589 | -0.0017051 | 0.070647 | 0.025015 | 0.059139 | 0.028518 | 3.4262 | -0.077084 | 122.3454 | 122.276 | 122.2625 | -0.044742 | -0.017267 | 0.19267 | -0.12503 | 121.9961 | 122.3357 | 121.6429 | -0.22367 | 0.15667 | 0.09508 | 0.22993 | 0.12433 | -0.032342 | 0.025594 | 0.012086 | -0.022257 | -0.25427 | 0.18415 | 0.076384 | 0.098641 | 0.085285 | -0.60746 | 122.5469 | 122.4774 | 122.4639 | 3.6276 | -122.2951 | 122.1975 | 122.5371 | 121.8443 | 0.39408 | -122.474
1206.0938 | 122.4792 | -0.16479 | 122.2458 | 1.4211e-13 | -0.0065127 | 0.002094 | 0.0644 | -0.0092389 | 0.058858 | -0.006028 | -0.0024589 | -0.0014913 | 0.070647 | 0.025442 | 0.059353 | 0.028518 | 3.9573 | -0.063349 | 122.3638 | 122.276 | 122.267 | -0.026426 | -0.021846 | 0.20182 | -0.12045 | 121.9961 | 122.3357 | 121.6429 | -0.23283 | 0.13837 | 0.11797 | 0.19331 | 0.10145 | -0.036923 | 0.030171 | 0.021242 | -0.068036 | -0.24969 | 0.14295 | 0.044342 | 0.11238 | 0.089862 | -0.60288 | 122.5286 | 122.4408 | 122.4318 | 4.1221 | -122.2722 | 122.1609 | 122.5004 | 121.8077 | 0.36662 | -122.4786
1207.8438 | 122.4335 | -0.17853 | 122.2366 | 1.4211e-13 | -0.0065127 | 0.0023076 | 0.063973 | -0.0085979 | 0.058644 | -0.006028 | -0.0022453 | -0.0017051 | 0.070861 | 0.025015 | 0.059139 | 0.019361 | 4.3831 | -0.072505 | 122.3546 | 122.2805 | 122.2625 | -0.058478 | -0.021846 | 0.18809 | -0.11587 | 121.9961 | 122.3402 | 121.6887 | -0.22367 | 0.12005 | 0.11797 | 0.19789 | 0.10602 | -0.014027 | 0.043906 | 0.025819 | -0.045145 | -0.24053 | 0.15668 | 0.062654 | 0.1078 | 0.1036 | -0.54794 | 122.5331 | 122.4591 | 122.441 | 4.5617 | -122.2951 | 122.1746 | 122.5188 | 121.8672 | 0.36661 | -122.4603
1209.6094 | 122.3511 | -0.2243 | 122.2733 | 1.4211e-13 | -0.0065127 | 0.0023076 | 0.0644 | -0.0088115 | 0.058644 | 0.0016025 | -0.0024589 | -0.0012777 | 0.070861 | 0.025228 | 0.059353 | 0.019361 | 4.7769 | -0.072505 | 122.3546 | 122.276 | 122.2533 | -0.044742 | -0.017267 | 0.19267 | -0.12045 | 122.0007 | 122.3311 | 121.6612 | -0.21452 | 0.17956 | 0.081349 | 0.24366 | 0.1518 | -0.027763 | 0.002706 | -0.019959 | 0.009788 | -0.27258 | 0.20704 | 0.10385 | 0.094063 | 0.057819 | -0.61203 | 122.5789 | 122.5003 | 122.4776 | 5.0012 | -122.318 | 122.225 | 122.5554 | 121.8855 | 0.41697 | -122.4878
1211.2969 | 122.3602 | -0.21057 | 122.2778 | 1.4211e-13 | -0.0062991 | 0.002094 | 0.0644 | -0.0085979 | 0.059071 | -0.006028 | -0.0022453 | -0.0014913 | 0.070861 | 0.025442 | 0.059566 | 0.019361 | 5.189 | -0.077084 | 122.3546 | 122.2714 | 122.267 | -0.044742 | -0.017267 | 0.20182 | -0.12045 | 121.9961 | 122.3402 | 121.6887 | -0.2191 | 0.16583 | 0.076771 | 0.22993 | 0.13349 | -0.032342 | -0.006451 | -0.010801 | -0.008524 | -0.28173 | 0.1933 | 0.090118 | 0.098642 | 0.062398 | -0.58914 | 122.5652 | 122.482 | 122.4776 | 5.3995 | -122.3226 | 122.2067 | 122.5508 | 121.8993 | 0.41239 | -122.4969
1213 | 122.438 | -0.1831 | 122.2366 | 1.4211e-13 | -0.0062991 | 0.0023076 | 0.0644 | -0.0088115 | 0.058858 | 0.0016025 | -0.0024589 | -0.0017051 | 0.070861 | 0.025015 | 0.059139 | 0.023939 | 5.3721 | -0.081662 | 122.3454 | 122.276 | 122.2625 | -0.040163 | -0.021846 | 0.19724 | -0.12045 | 121.9915 | 122.3357 | 121.6887 | -0.22825 | 0.14294 | 0.10881 | 0.20704 | 0.10144 | -0.041499 | 0.039327 | 0.025819 | -0.045147 | -0.24511 | 0.16126 | 0.062652 | 0.1078 | 0.099018 | -0.54794 | 122.5286 | 122.4591 | 122.4456 | 5.5552 | -122.2768 | 122.1746 | 122.5188 | 121.8718 | 0.38035 | -122.4649
1214.7656 | 122.3831 | -0.19226 | 122.2504 | 1.4211e-13 | -0.0067265 | 0.0023076 | 0.0644 | -0.0085979 | 0.058644 | -0.006028 | -0.0026725 | -0.0014913 | 0.070861 | 0.025228 | 0.059139 | 0.019361 | 5.6102 | -0.067927 | 122.35 | 122.2851 | 122.267 | -0.053899 | -0.021846 | 0.19724 | -0.12503 | 122.0098 | 122.3448 | 121.6704 | -0.23283 | 0.13836 | 0.099658 | 0.21162 | 0.12433 | -0.014028 | 0.034752 | 0.016665 | -0.04057 | -0.24053 | 0.17041 | 0.067229 | 0.1078 | 0.094443 | -0.57999 | 122.5423 | 122.4774 | 122.4593 | 5.8025 | -122.3043 | 122.2021 | 122.5371 | 121.8626 | 0.3895 | -122.4832
1216.5156 | 122.3785 | -0.21515 | 122.287 | 1.4211e-13 | -0.0060855 | 0.0025214 | 0.064186 | -0.0085979 | 0.058644 | -0.013659 | -0.0022453 | -0.0017051 | 0.071074 | 0.025228 | 0.059139 | 0.019361 | 5.7979 | -0.077084 | 122.3546 | 122.276 | 122.267 | -0.031005 | -0.017267 | 0.19267 | -0.12045 | 122.0007 | 122.3448 | 121.6887 | -0.2191 | 0.18414 | 0.067616 | 0.23451 | 0.13806 | -0.046079 | -0.011027 | -0.019956 | -0.003946 | -0.28631 | 0.19788 | 0.094696 | 0.098642 | 0.057822 | -0.5983 | 122.5698 | 122.4911 | 122.4822 | 6.0131 | -122.318 | 122.2158 | 122.56 | 121.9038 | 0.40781 | -122.5061
1218.2031 | 122.4792 | -0.16022 | 122.2595 | 1.4211e-13 | -0.0062991 | 0.002094 | 0.063973 | -0.0090251 | 0.058858 | -0.006028 | -0.0026725 | -0.0019187 | 0.070861 | 0.025228 | 0.059139 | -0.003531 | 5.9582 | -0.067927 | 122.3592 | 122.2805 | 122.2716 | -0.058478 | -0.012689 | 0.20182 | -0.12503 | 122.0053 | 122.3448 | 121.6521 | -0.2191 | 0.10174 | 0.09966 | 0.15669 | 0.09229 | -0.009449 | 0.021018 | 0.012089 | -0.058878 | -0.25427 | 0.14753 | 0.035185 | 0.094063 | 0.085288 | -0.60746 | 122.5194 | 122.4408 | 122.4318 | 6.1184 | -122.318 | 122.1655 | 122.505 | 121.8123 | 0.36204 | -122.4786
1219.9688 | 122.4152 | -0.19226 | 122.2916 | 1.4211e-13 | -0.0062991 | 0.0023076 | 0.064186 | -0.0085979 | 0.058858 | 0.0092325 | -0.0024589 | -0.0017051 | 0.071074 | 0.025228 | 0.058925 | 0.010204 | 6.0726 | -0.067927 | 122.3592 | 122.2805 | 122.2716 | -0.035584 | -0.017267 | 0.20182 | -0.11587 | 122.0053 | 122.3494 | 121.6246 | -0.2191 | 0.15668 | 0.067616 | 0.20246 | 0.12433 | -0.032343 | -0.011026 | -0.019955 | -0.026834 | -0.28631 | 0.17499 | 0.076387 | 0.10322 | 0.057822 | -0.66697 | 122.5514 | 122.4728 | 122.4639 | 6.2649 | -122.3271 | 122.1975 | 122.5416 | 121.8169 | 0.39408 | -122.5107
1221.7031 | 122.3831 | -0.21057 | 122.2595 | 1.4211e-13 | -0.0062991 | 0.002094 | 0.064186 | -0.0090251 | 0.058644 | 0.0016025 | -0.0026725 | -0.0012777 | 0.071074 | 0.025228 | 0.059139 | 0.014783 | 6.3977 | -0.072505 | 122.3592 | 122.2851 | 122.2762 | -0.090531 | -0.021846 | 0.19267 | -0.12045 | 122.0098 | 122.3585 | 121.7299 | -0.22367 | 0.12004 | 0.09966 | 0.22535 | 0.13807 | 0.018026 | 0.025597 | 0.016667 | -0.013102 | -0.24969 | 0.18873 | 0.090118 | 0.10322 | 0.099023 | -0.52962 | 122.5698 | 122.4957 | 122.4868 | 6.6083 | -122.3501 | 122.2204 | 122.5691 | 121.9405 | 0.40324 | -122.4832
1223.3906 | 122.3877 | -0.19226 | 122.2961 | 1.4211e-13 | -0.0058717 | 0.0023076 | 0.064614 | -0.0085979 | 0.058858 | 0.0016025 | -0.0022453 | -0.0021323 | 0.071074 | 0.025228 | 0.059139 | 0.014783 | 6.9014 | -0.072505 | 122.3683 | 122.2851 | 122.2808 | -0.026426 | -0.017267 | 0.19724 | -0.11587 | 122.0144 | 122.354 | 121.6841 | -0.21452 | 0.16583 | 0.072195 | 0.20704 | 0.11976 | -0.046079 | -0.011025 | -0.015376 | -0.022255 | -0.28173 | 0.17499 | 0.076387 | 0.098642 | 0.057823 | -0.61203 | 122.5606 | 122.4774 | 122.473 | 7.0936 | -122.3226 | 122.2067 | 122.5462 | 121.8764 | 0.3895 | -122.5107
1225.0938 | 122.3602 | -0.21973 | 122.2687 | 1.4211e-13 | -0.0062991 | 0.0023076 | 0.0644 | -0.0083841 | 0.058644 | -0.006028 | -0.0026725 | -0.0017051 | 0.071074 | 0.025656 | 0.059353 | 0.019361 | 7.4691 | -0.05877 | 122.3638 | 122.2943 | 122.2762 | -0.058478 | -0.017267 | 0.19724 | -0.10672 | 122.0144 | 122.3585 | 121.675 | -0.20994 | 0.16125 | 0.095082 | 0.23909 | 0.16096 | -0.000292 | 0.025599 | 0.007511 | 0.00979 | -0.25426 | 0.20246 | 0.11301 | 0.10322 | 0.089867 | -0.59372 | 122.5835 | 122.514 | 122.4959 | 7.6888 | -122.3272 | 122.2341 | 122.5783 | 121.8947 | 0.41697 | -122.4786
1226.8594 | 122.438 | -0.1831 | 122.2595 | 1.4211e-13 | -0.0065127 | 0.002094 | 0.0644 | -0.0085979 | 0.058858 | 0.0016025 | -0.0026725 | -0.0017051 | 0.070861 | 0.025015 | 0.059353 | 0.014783 | 7.6935 | -0.054192 | 122.3683 | 122.2897 | 122.2808 | -0.15006 | -0.00811 | 0.2064 | -0.1113 | 122.0144 | 122.3677 | 121.7162 | -0.21452 | 0.033048 | 0.10882 | 0.19789 | 0.12891 | 0.095865 | 0.030176 | 0.021246 | -0.031411 | -0.24511 | 0.17499 | 0.071809 | 0.10322 | 0.10818 | -0.54336 | 122.5514 | 122.4728 | 122.4639 | 7.8766 | -122.4096 | 122.1975 | 122.5508 | 121.8993 | 0.38951 | -122.474
1228.6094 | 122.4838 | -0.16937 | 122.2458 | 1.4211e-13 | -0.0062991 | 0.0018804 | 0.0644 | -0.0088115 | 0.05843 | -0.006028 | -0.0026725 | -0.0014913 | 0.070647 | 0.025228 | 0.059139 | 0.019361 | 7.6339 | -0.05877 | 122.3638 | 122.2943 | 122.2762 | -0.021847 | -0.017267 | 0.20182 | -0.11587 | 122.0144 | 122.3585 | 121.7024 | -0.2191 | 0.14753 | 0.11797 | 0.18873 | 0.1106 | -0.036923 | 0.048487 | 0.030399 | -0.049722 | -0.23138 | 0.15211 | 0.053499 | 0.10322 | 0.11275 | -0.54336 | 122.5331 | 122.4636 | 122.4456 | 7.8033 | -122.2676 | 122.1838 | 122.5279 | 121.8718 | 0.37119 | -122.4649
1230.2969 | 122.4838 | -0.15564 | 122.2687 | 1.4211e-13 | -0.0062991 | 0.002094 | 0.064614 | -0.0090251 | 0.058858 | 0.0016025 | -0.0024589 | -0.0017051 | 0.070647 | 0.025228 | 0.059353 | 0.014783 | 7.7759 | -0.05877 | 122.3683 | 122.2943 | 122.2853 | -0.031005 | -0.00811 | 0.19724 | -0.1113 | 122.0144 | 122.3677 | 121.7024 | -0.21452 | 0.12463 | 0.099661 | 0.17042 | 0.09687 | -0.027765 | 0.025599 | 0.016668 | -0.058876 | -0.25426 | 0.14753 | 0.044344 | 0.10322 | 0.099025 | -0.56625 | 122.524 | 122.4499 | 122.441 | 7.9315 | -122.2997 | 122.1701 | 122.5233 | 121.8581 | 0.35288 | -122.4832
1232.0469 | 122.4335 | -0.19684 | 122.287 | 1.4211e-13 | -0.0062991 | 0.002094 | 0.0644 | -0.0085979 | 0.058644 | -0.006028 | -0.0024589 | -0.0019187 | 0.071074 | 0.025228 | 0.058925 | 0.019361 | 8.1696 | -0.067927 | 122.3683 | 122.2989 | 122.2808 | -0.017268 | -0.00811 | 0.20182 | -0.11587 | 122.019 | 122.3585 | 121.6887 | -0.20994 | 0.17957 | 0.081351 | 0.2162 | 0.12891 | -0.050659 | 0.011868 | -0.00622 | -0.013099 | -0.26799 | 0.18873 | 0.080964 | 0.094063 | 0.071557 | -0.5983 | 122.5652 | 122.4957 | 122.4776 | 8.3665 | -122.3043 | 122.2158 | 122.5554 | 121.8855 | 0.39866 | -122.4969
1233.7969 | 122.438 | -0.16479 | 122.2595 | 1.4211e-13 | -0.0067265 | 0.0023076 | 0.064614 | -0.0088115 | 0.058644 | -0.006028 | -0.0024589 | -0.0014913 | 0.071074 | 0.025656 | 0.058925 | 0.019361 | 8.4672 | -0.063349 | 122.3775 | 122.2989 | 122.2899 | -0.017268 | -0.012689 | 0.2064 | -0.1113 | 122.0236 | 122.3631 | 121.6978 | -0.20994 | 0.14753 | 0.11797 | 0.18416 | 0.10145 | -0.046081 | 0.039334 | 0.030403 | -0.045142 | -0.23595 | 0.15211 | 0.053499 | 0.098641 | 0.1036 | -0.56167 | 122.5423 | 122.4637 | 122.4547 | 8.632 | -122.2768 | 122.1884 | 122.5279 | 121.8626 | 0.3712 | -122.4695
1235.5 | 122.4106 | -0.1831 | 122.2961 | 1.4211e-13 | -0.0062991 | 0.0025214 | 0.064614 | -0.0092389 | 0.058644 | 0.0092325 | -0.0022453 | -0.0012777 | 0.071288 | 0.025228 | 0.059139 | 0.019361 | 8.4444 | -0.054192 | 122.3729 | 122.3034 | 122.2853 | -0.021847 | -0.012689 | 0.20182 | -0.10672 | 122.0144 | 122.354 | 121.6887 | -0.21452 | 0.16126 | 0.076773 | 0.20247 | 0.12891 | -0.032345 | 0.00729 | -0.010798 | -0.031411 | -0.28173 | 0.17042 | 0.076388 | 0.1078 | 0.057823 | -0.60745 | 122.556 | 122.4865 | 122.4685 | 8.6275 | -122.318 | 122.1975 | 122.5371 | 121.8718 | 0.38493 | -122.5107
1237.2344 | 122.3877 | -0.18768 | 122.3053 | 1.4211e-13 | -0.0062991 | 0.002094 | 0.0644 | -0.0088115 | 0.058858 | -0.006028 | -0.0026725 | -0.0019187 | 0.070861 | 0.025442 | 0.059139 | 0.005626 | 9.0625 | -0.05877 | 122.3775 | 122.2897 | 122.2853 | -0.021847 | -0.012689 | 0.20182 | -0.1113 | 122.0236 | 122.3585 | 121.7345 | -0.20994 | 0.16584 | 0.072197 | 0.19331 | 0.12891 | -0.036923 | -0.015601 | -0.019953 | -0.022254 | -0.28173 | 0.17499 | 0.076387 | 0.098641 | 0.053246 | -0.57082 | 122.5652 | 122.4774 | 122.473 | 9.2501 | -122.3271 | 122.2113 | 122.5462 | 121.9222 | 0.3895 | -122.5152
1238.9844 | 122.3969 | -0.20142 | 122.2961 | 1.4211e-13 | -0.0065127 | 0.0023076 | 0.064827 | -0.0083841 | 0.059071 | 0.0016025 | -0.0022453 | -0.0017051 | 0.070647 | 0.025442 | 0.059353 | 0.010204 | 9.2639 | -0.049614 | 122.3821 | 122.2989 | 122.2899 | -0.026426 | -0.00811 | 0.2064 | -0.1113 | 122.0281 | 122.3677 | 121.6933 | -0.20994 | 0.17499 | 0.08593 | 0.21162 | 0.1518 | -0.023188 | 0.002712 | -0.006219 | -0.008521 | -0.26799 | 0.19331 | 0.09012 | 0.098641 | 0.071559 | -0.60287 | 122.5835 | 122.5003 | 122.4913 | 9.4653 | -122.3226 | 122.2296 | 122.5691 | 121.8947 | 0.40782 | -122.5061
1240.6719 | 122.4289 | -0.19226 | 122.2733 | 1.4211e-13 | -0.0062991 | 0.0025214 | 0.064827 | -0.0088115 | 0.058858 | 0.0016025 | -0.0028861 | -0.0014913 | 0.070861 | 0.025442 | 0.059353 | 0.010204 | 9.6806 | -0.063349 | 122.3683 | 122.2989 | 122.2899 | -0.049321 | -0.00811 | 0.20182 | -0.1113 | 122.019 | 122.3585 | 121.7803 | -0.2191 | 0.14294 | 0.095084 | 0.20246 | 0.12891 | -0.014028 | 0.025601 | 0.01667 | -0.026834 | -0.25426 | 0.18415 | 0.080965 | 0.1078 | 0.08529 | -0.49299 | 122.5606 | 122.4911 | 122.4822 | 9.8728 | -122.3226 | 122.2113 | 122.5508 | 121.9725 | 0.39408 | -122.4923
1242.4219 | 122.4518 | -0.16022 | 122.2504 | 1.4211e-13 | -0.0062991 | 0.002735 | 0.064827 | -0.0090251 | 0.058858 | 0.0016025 | -0.0026725 | -0.0014913 | 0.071074 | 0.025228 | 0.059353 | 0.019361 | 10.1796 | -0.045036 | 122.3775 | 122.2989 | 122.2945 | -0.021847 | -0.012689 | 0.2064 | -0.1113 | 122.0327 | 122.3585 | 121.6795 | -0.21452 | 0.13837 | 0.12713 | 0.17958 | 0.11518 | -0.023189 | 0.048489 | 0.044137 | -0.054299 | -0.21764 | 0.14753 | 0.048921 | 0.10322 | 0.10818 | -0.57083 | 122.5377 | 122.4591 | 122.4547 | 10.3399 | -122.2722 | 122.1929 | 122.5188 | 121.8398 | 0.36662 | -122.4649
1244.1094 | 122.3785 | -0.2243 | 122.287 | 1.4211e-13 | -0.0062991 | 0.0023076 | 0.064614 | -0.0088115 | 0.058858 | -0.013659 | -0.0026725 | -0.0017051 | 0.070861 | 0.025228 | 0.059139 | 0.010204 | 10.5047 | -0.05877 | 122.3821 | 122.3034 | 122.2945 | -0.017268 | -0.017267 | 0.2064 | -0.1113 | 122.0236 | 122.3677 | 121.6933 | -0.20536 | 0.20704 | 0.095086 | 0.23451 | 0.16553 | -0.041502 | 0.016446 | 0.007516 | 0.018946 | -0.26342 | 0.20704 | 0.11301 | 0.094062 | 0.080715 | -0.59372 | 122.6064 | 122.5277 | 122.5188 | 10.729 | -122.3043 | 122.2479 | 122.592 | 121.9176 | 0.43071 | -122.4923
1245.8594 | 122.4518 | -0.16022 | 122.2504 | 1.4211e-13 | -0.0060855 | 0.002094 | 0.064614 | -0.0088115 | 0.058858 | 0.0092325 | -0.0024589 | -0.0014913 | 0.070861 | 0.025656 | 0.058925 | 0.010204 | 11.4204 | -0.049614 | 122.3867 | 122.3034 | 122.2991 | -0.021847 | -0.012689 | 0.21098 | -0.11587 | 122.0281 | 122.3723 | 121.7116 | -0.20078 | 0.13837 | 0.13629 | 0.17042 | 0.1106 | -0.027767 | 0.053067 | 0.048715 | -0.040562 | -0.22222 | 0.14753 | 0.044343 | 0.084905 | 0.12191 | -0.53878 | 122.5469 | 122.4637 | 122.4593 | 11.5807 | -122.2722 | 122.1884 | 122.5325 | 121.8718 | 0.3712 | -122.4511
1247.6094 | 122.5159 | -0.15564 | 122.2824 | 1.4211e-13 | -0.0062991 | 0.0025214 | 0.064827 | -0.0088115 | 0.058858 | -0.006028 | -0.0020317 | -0.0014913 | 0.070861 | 0.025442 | 0.058925 | 0.014783 | 12.3087 | -0.045036 | 122.3912 | 122.3126 | 122.3082 | -0.017268 | -0.003531 | 0.2064 | -0.10214 | 122.0419 | 122.3723 | 121.6933 | -0.20536 | 0.13837 | 0.10882 | 0.17042 | 0.1106 | -0.027768 | 0.030181 | 0.025828 | -0.049718 | -0.24053 | 0.15211 | 0.053502 | 0.10322 | 0.08987 | -0.58914 | 122.5469 | 122.4682 | 122.4639 | 12.4643 | -122.2997 | 122.1975 | 122.5279 | 121.8489 | 0.36204 | -122.4878
1249.3594 | 122.4609 | -0.16022 | 122.2916 | 1.4211e-13 | -0.0060855 | 0.0018804 | 0.064614 | -0.0085979 | 0.058858 | 0.0016025 | -0.0024589 | -0.0017051 | 0.070647 | 0.025442 | 0.058925 | 0.033096 | 12.4644 | -0.049614 | 122.3912 | 122.3126 | 122.3082 | -0.017268 | 0.001048 | 0.20182 | -0.10672 | 122.0373 | 122.3769 | 121.7024 | -0.20536 | 0.14295 | 0.099665 | 0.19331 | 0.1106 | -0.032346 | 0.021026 | 0.016673 | -0.045141 | -0.25426 | 0.16126 | 0.0535 | 0.098641 | 0.085294 | -0.58914 | 122.5514 | 122.4728 | 122.4685 | 12.6246 | -122.3088 | 122.1975 | 122.5371 | 121.8626 | 0.36204 | -122.4969
1251.1094 | 122.4106 | -0.17853 | 122.2641 | 1.4211e-13 | -0.0067265 | 0.0018804 | 0.064614 | -0.0085979 | 0.059071 | -0.013659 | -0.0022453 | -0.0017051 | 0.070647 | 0.025656 | 0.059139 | 0.019361 | 12.707 | -0.045036 | 122.3958 | 122.3172 | 122.3037 | -0.012689 | 0.001048 | 0.2064 | -0.097559 | 122.0373 | 122.3814 | 121.7391 | -0.20536 | 0.16584 | 0.13171 | 0.19789 | 0.13349 | -0.032347 | 0.053071 | 0.039561 | -0.02683 | -0.22679 | 0.17958 | 0.080969 | 0.1078 | 0.11734 | -0.52504 | 122.5743 | 122.4957 | 122.4822 | 12.8856 | -122.2768 | 122.2158 | 122.56 | 121.9176 | 0.38493 | -122.4695
1252.8906 | 122.3602 | -0.18768 | 122.3007 | 1.4211e-13 | -0.0062991 | 0.002094 | 0.064614 | -0.0085979 | 0.058644 | 0.0016025 | -0.0022453 | -0.0014913 | 0.071074 | 0.025442 | 0.059566 | 0.033096 | 13.1374 | -0.045036 | 122.3912 | 122.3126 | 122.3082 | -0.017268 | -0.003531 | 0.2064 | -0.10214 | 122.0373 | 122.3723 | 121.6933 | -0.20078 | 0.17041 | 0.09051 | 0.22078 | 0.14265 | -0.027768 | 0.011871 | 0.007518 | -0.013096 | -0.26341 | 0.18415 | 0.085545 | 0.098641 | 0.07156 | -0.60745 | 122.5789 | 122.5003 | 122.4959 | 13.3251 | -122.318 | 122.225 | 122.56 | 121.881 | 0.39408 | -122.5015
1254.6562 | 122.493 | -0.15106 | 122.2961 | 1.4211e-13 | -0.0065127 | 0.0023076 | 0.064827 | -0.0083841 | 0.058644 | -0.013659 | -0.0024589 | -0.0014913 | 0.071074 | 0.025442 | 0.059353 | 0.028518 | 12.6612 | -0.045036 | 122.3912 | 122.3172 | 122.3128 | -0.012689 | -0.00811 | 0.2064 | -0.10214 | 122.0419 | 122.3723 | 121.6841 | -0.20078 | 0.13837 | 0.095087 | 0.17958 | 0.10603 | -0.032347 | 0.021027 | 0.016674 | -0.049717 | -0.25426 | 0.14295 | 0.048924 | 0.098641 | 0.076137 | -0.61203 | 122.5423 | 122.4682 | 122.4639 | 12.8123 | -122.3088 | 122.1929 | 122.5233 | 121.8352 | 0.35746 | -122.4969
1256.4062 | 122.4426 | -0.16022 | 122.287 | 1.4211e-13 | -0.0065127 | 0.002094 | 0.064614 | -0.0085979 | 0.058644 | 0.0016025 | -0.0024589 | -0.0017051 | 0.070647 | 0.025228 | 0.059139 | 0.042253 | 12.9268 | -0.045036 | 122.3958 | 122.3263 | 122.3082 | -0.017268 | -0.003531 | 0.21556 | -0.097559 | 122.0465 | 122.3814 | 121.707 | -0.20078 | 0.14295 | 0.10882 | 0.20247 | 0.11518 | -0.027768 | 0.039341 | 0.021251 | -0.040562 | -0.24052 | 0.15669 | 0.062658 | 0.10322 | 0.09445 | -0.57998 | 122.556 | 122.4865 | 122.4685 | 13.087 | -122.3043 | 122.2067 | 122.5417 | 121.8672 | 0.37577 | -122.4878
1258.1094 | 122.374 | -0.1831 | 122.3099 | 1.4211e-13 | -0.0062991 | 0.0023076 | 0.064827 | -0.0085979 | 0.058858 | -0.013659 | -0.0024589 | -0.0017051 | 0.071288 | 0.025015 | 0.059139 | 0.037675 | 12.9497 | -0.045036 | 122.4004 | 122.3126 | 122.3174 | -0.012689 | 0.005626 | 0.2064 | -0.10214 | 122.0465 | 122.3769 | 121.7116 | -0.20078 | 0.17042 | 0.090511 | 0.22078 | 0.13807 | -0.032347 | 0.002716 | 0.007521 | -0.017674 | -0.26341 | 0.18873 | 0.080967 | 0.098641 | 0.066984 | -0.59829 | 122.5835 | 122.4957 | 122.5005 | 13.1328 | -122.3226 | 122.2296 | 122.56 | 121.8947 | 0.38951 | -122.5107
1259.8594 | 122.3877 | -0.20142 | 122.3007 | 1.4211e-13 | -0.0060855 | 0.002094 | 0.064614 | -0.0088115 | 0.058644 | -0.013659 | -0.0024589 | -0.0014913 | 0.070433 | 0.025015 | 0.058925 | 0.042253 | 12.9726 | -0.045036 | 122.3958 | 122.3263 | 122.3174 | -0.017268 | -0.003531 | 0.2064 | -0.10214 | 122.0419 | 122.3769 | 121.6978 | -0.20536 | 0.18415 | 0.095088 | 0.24367 | 0.15638 | -0.027768 | 0.025608 | 0.016676 | -0.003942 | -0.25884 | 0.19789 | 0.099278 | 0.10322 | 0.076139 | -0.60287 | 122.5972 | 122.5277 | 122.5188 | 13.174 | -122.318 | 122.2433 | 122.5783 | 121.8993 | 0.40782 | -122.5061
1261.5469 | 122.4014 | -0.18768 | 122.3099 | 1.4211e-13 | -0.0062991 | 0.002735 | 0.065041 | -0.0085979 | 0.059071 | 0.0016025 | -0.0024589 | -0.0012777 | 0.070861 | 0.025015 | 0.058712 | 0.037675 | 13.2748 | -0.040457 | 122.3958 | 122.3217 | 122.322 | -0.021847 | -0.003531 | 0.21098 | -0.097559 | 122.0419 | 122.3814 | 121.7482 | -0.19162 | 0.16584 | 0.085933 | 0.22536 | 0.14723 | -0.01861 | 0.011874 | 0.012099 | -0.003939 | -0.26799 | 0.18415 | 0.090124 | 0.094063 | 0.071562 | -0.56166 | 122.5835 | 122.5094 | 122.5097 | 13.4625 | -122.3317 | 122.2296 | 122.5691 | 121.9359 | 0.39866 | -122.5015
1263.2344 | 122.374 | -0.1831 | 122.3282 | 1.4211e-13 | -0.0062991 | 0.002735 | 0.064827 | -0.0088115 | 0.058858 | 0.0016025 | -0.0020317 | -0.0014913 | 0.070861 | 0.025442 | 0.059139 | 0.037675 | 13.4396 | -0.040457 | 122.3912 | 122.3217 | 122.3174 | -0.017268 | -0.003531 | 0.21556 | -0.10214 | 122.0465 | 122.3814 | 121.7299 | -0.20078 | 0.16584 | 0.063044 | 0.22078 | 0.14265 | -0.023189 | -0.006437 | -0.01079 | -0.017674 | -0.28172 | 0.17957 | 0.080967 | 0.098641 | 0.053251 | -0.59829 | 122.5743 | 122.5049 | 122.5005 | 13.6227 | -122.3455 | 122.2296 | 122.5645 | 121.913 | 0.39866 | -122.529
1264.9844 | 122.3785 | -0.19684 | 122.287 | 1.4211e-13 | -0.0060855 | 0.0023076 | 0.0644 | -0.0085979 | 0.058858 | -0.006028 | -0.0024589 | -0.0014913 | 0.070861 | 0.025442 | 0.059139 | 0.033096 | 13.8288 | -0.040457 | 122.3867 | 122.3172 | 122.3128 | -0.012689 | -0.00811 | 0.21556 | -0.10672 | 122.0419 | 122.3814 | 121.7436 | -0.20078 | 0.18415 | 0.099664 | 0.22993 | 0.15638 | -0.027768 | 0.030183 | 0.02583 | -0.003941 | -0.2451 | 0.18873 | 0.090121 | 0.094062 | 0.09445 | -0.54335 | 122.5835 | 122.514 | 122.5097 | 14.0256 | -122.2997 | 122.2387 | 122.5783 | 121.9405 | 0.4124 | -122.4878
1266.6562 | 122.4747 | -0.13733 | 122.2961 | 1.4211e-13 | -0.0060855 | 0.002735 | 0.064614 | -0.0092389 | 0.058858 | 0.0016025 | -0.0024589 | -0.0017051 | 0.070861 | 0.025228 | 0.059139 | 0.033096 | 14.2912 | -0.045036 | 122.3912 | 122.3309 | 122.3128 | -0.026426 | -0.003531 | 0.21098 | -0.10214 | 122.0373 | 122.386 | 121.7436 | -0.18704 | 0.1109 | 0.095087 | 0.17042 | 0.092293 | -0.01861 | 0.034764 | 0.016674 | -0.049714 | -0.25884 | 0.1338 | 0.035191 | 0.084905 | 0.089873 | -0.55251 | 122.5286 | 122.4682 | 122.4501 | 14.4286 | -122.3226 | 122.1746 | 122.5233 | 121.881 | 0.34831 | -122.4832
1268.4062 | 122.5204 | -0.14648 | 122.2549 | 1.4211e-13 | -0.0065127 | 0.0025214 | 0.064614 | -0.0092389 | 0.058644 | 0.0016025 | -0.0022453 | -0.0012777 | 0.070861 | 0.025442 | 0.058925 | 0.037675 | 14.1813 | -0.045036 | 122.3912 | 122.3172 | 122.3128 | -0.017268 | -0.003531 | 0.21556 | -0.10214 | 122.051 | 122.3814 | 121.7436 | -0.20078 | 0.12922 | 0.13629 | 0.18416 | 0.10145 | -0.027768 | 0.062226 | 0.057873 | -0.054295 | -0.2039 | 0.14295 | 0.044346 | 0.098641 | 0.12649 | -0.51131 | 122.5377 | 122.4637 | 122.4593 | 14.3278 | -122.2722 | 122.1975 | 122.5279 | 121.8901 | 0.36204 | -122.4557
1270.1094 | 122.3785 | -0.19226 | 122.2916 | 1.4211e-13 | -0.0060855 | 0.0025214 | 0.064827 | -0.0090251 | 0.058644 | -0.006028 | -0.0024589 | -0.0017051 | 0.071288 | 0.025442 | 0.059353 | 0.037675 | 14.9277 | -0.049614 | 122.4004 | 122.3172 | 122.3311 | -0.017268 | -0.003531 | 0.20182 | -0.10672 | 122.0419 | 122.3814 | 121.7391 | -0.1962 | 0.17499 | 0.10882 | 0.22994 | 0.14265 | -0.032346 | 0.025605 | 0.039566 | -0.003939 | -0.24968 | 0.18873 | 0.085544 | 0.089483 | 0.089872 | -0.55251 | 122.5926 | 122.5094 | 122.5234 | 15.1199 | -122.3088 | 122.2341 | 122.5737 | 121.9313 | 0.39408 | -122.4878
1271.8438 | 122.4609 | -0.17395 | 122.2916 | 1.4211e-13 | -0.0062991 | 0.0023076 | 0.065041 | -0.0092389 | 0.058858 | 0.0016025 | -0.0020317 | -0.0019187 | 0.070861 | 0.025228 | 0.059353 | 0.037675 | 14.8223 | -0.035879 | 122.4004 | 122.3263 | 122.3174 | -0.012689 | -0.00811 | 0.21556 | -0.097559 | 122.0465 | 122.3814 | 121.7482 | -0.20536 | 0.16126 | 0.10882 | 0.21163 | 0.13807 | -0.02319 | 0.034763 | 0.025831 | -0.031408 | -0.2451 | 0.16584 | 0.076391 | 0.1078 | 0.089872 | -0.54335 | 122.5743 | 122.5003 | 122.4913 | 14.9963 | -122.3043 | 122.2204 | 122.5554 | 121.9222 | 0.38951 | -122.4969
1273.5312 | 122.5021 | -0.14648 | 122.2733 | 1.4211e-13 | -0.0060855 | 0.0025214 | 0.064827 | -0.0090251 | 0.058858 | 0.0016025 | -0.0022453 | -0.0019187 | 0.071288 | 0.025442 | 0.059353 | 0.042253 | 15.1795 | -0.045036 | 122.3958 | 122.3217 | 122.3174 | -0.017268 | -0.003531 | 0.22014 | -0.10672 | 122.0465 | 122.3814 | 121.7436 | -0.20994 | 0.12922 | 0.12255 | 0.18874 | 0.10145 | -0.027768 | 0.048495 | 0.044142 | -0.063453 | -0.22679 | 0.14295 | 0.039767 | 0.10322 | 0.10818 | -0.52962 | 122.5423 | 122.4682 | 122.4639 | 15.326 | -122.2905 | 122.1929 | 122.5279 | 121.8901 | 0.36662 | -122.4832
1275.2188 | 122.5113 | -0.15106 | 122.2733 | 1.4211e-13 | -0.0065127 | 0.0023076 | 0.064614 | -0.0088115 | 0.058858 | -0.006028 | -0.0024589 | -0.0021323 | 0.070861 | 0.025442 | 0.059353 | 0.042253 | 15.3214 | -0.040457 | 122.405 | 122.3263 | 122.3311 | -0.017268 | -0.003531 | 0.21556 | -0.10214 | 122.051 | 122.3769 | 121.7299 | -0.20536 | 0.13379 | 0.13171 | 0.19332 | 0.11061 | -0.023189 | 0.053074 | 0.057877 | -0.054296 | -0.22221 | 0.14753 | 0.048924 | 0.10322 | 0.10361 | -0.54335 | 122.556 | 122.4774 | 122.4822 | 15.4725 | -122.2905 | 122.2021 | 122.5279 | 121.881 | 0.36662 | -122.4786
1276.9688 | 122.3785 | -0.19226 | 122.3145 | 1.4211e-13 | -0.0060855 | 0.0025214 | 0.064614 | -0.0092389 | 0.058858 | -0.006028 | -0.0026725 | -0.0014913 | 0.070861 | 0.025442 | 0.059566 | 0.05141 | 14.8132 | -0.040457 | 122.3958 | 122.3309 | 122.322 | -0.021847 | -0.003531 | 0.21098 | -0.10672 | 122.051 | 122.386 | 121.7574 | -0.1962 | 0.17041 | 0.081355 | 0.24367 | 0.1518 | -0.01861 | 0.016454 | 0.007521 | -0.003939 | -0.26341 | 0.18873 | 0.085544 | 0.089483 | 0.071563 | -0.55708 | 122.5881 | 122.5232 | 122.5142 | 15.0054 | -122.3363 | 122.2433 | 122.5783 | 121.9496 | 0.40324 | -122.5107
1278.7188 | 122.3785 | -0.19684 | 122.2961 | 1.4211e-13 | -0.0062991 | 0.002094 | 0.064827 | -0.0085979 | 0.059071 | -0.006028 | -0.0026725 | -0.0017051 | 0.070647 | 0.025656 | 0.059353 | 0.037675 | 15.0925 | -0.040457 | 122.4004 | 122.3263 | 122.3174 | -0.017268 | -0.003531 | 0.22472 | -0.10214 | 122.051 | 122.3814 | 121.7299 | -0.20078 | 0.17957 | 0.10424 | 0.23451 | 0.15638 | -0.023189 | 0.030185 | 0.021253 | -0.003941 | -0.2451 | 0.19331 | 0.0947 | 0.098641 | 0.085294 | -0.56624 | 122.5972 | 122.5232 | 122.5142 | 15.2893 | -122.3134 | 122.2479 | 122.5783 | 121.9267 | 0.42155 | -122.4969
1280.4219 | 122.3923 | -0.17853 | 122.3007 | 1.4211e-13 | -0.0065127 | 0.0025214 | 0.064827 | -0.0090251 | 0.058858 | 0.016863 | -0.0024589 | -0.0014913 | 0.070647 | 0.025869 | 0.059353 | 0.037675 | 15.0467 | -0.045036 | 122.3958 | 122.3309 | 122.3266 | -0.012689 | 0.005626 | 0.22472 | -0.10672 | 122.0556 | 122.3906 | 121.7253 | -0.1962 | 0.16584 | 0.095088 | 0.2162 | 0.13349 | -0.032347 | 0.030187 | 0.025833 | -0.017672 | -0.2451 | 0.18415 | 0.071811 | 0.089483 | 0.089875 | -0.5754 | 122.5743 | 122.5094 | 122.5051 | 15.2252 | -122.3134 | 122.2341 | 122.5691 | 121.9038 | 0.40324 | -122.4969
1282.1094 | 122.374 | -0.19226 | 122.319 | 1.4211e-13 | -0.0060855 | 0.0025214 | 0.064614 | -0.0090251 | 0.058858 | -0.006028 | -0.0028861 | -0.0017051 | 0.071074 | 0.025656 | 0.05978 | 0.037675 | 15.8388 | -0.040457 | 122.4004 | 122.3309 | 122.3311 | -0.021847 | -0.003531 | 0.22014 | -0.10214 | 122.051 | 122.386 | 121.7116 | -0.20536 | 0.17041 | 0.081355 | 0.22994 | 0.1518 | -0.01861 | 0.011876 | 0.0121 | -0.013097 | -0.26799 | 0.18873 | 0.090123 | 0.10322 | 0.066985 | -0.60745 | 122.5926 | 122.5232 | 122.5234 | 16.0311 | -122.3409 | 122.2433 | 122.5783 | 121.9038 | 0.4124 | -122.5244
1283.8594 | 122.4472 | -0.16022 | 122.3053 | 1.4211e-13 | -0.0065127 | 0.002094 | 0.064827 | -0.0090251 | 0.058858 | -0.006028 | -0.0022453 | -0.0014913 | 0.071074 | 0.025656 | 0.059353 | 0.042253 | 16.4661 | -0.035879 | 122.4095 | 122.3263 | 122.3311 | -0.017268 | -0.003531 | 0.22472 | -0.097559 | 122.0602 | 122.386 | 121.7253 | -0.21452 | 0.14295 | 0.10425 | 0.20247 | 0.12434 | -0.018611 | 0.02103 | 0.025833 | -0.054299 | -0.2451 | 0.15669 | 0.062658 | 0.11696 | 0.080718 | -0.57998 | 122.5698 | 122.4865 | 122.4913 | 16.6263 | -122.3226 | 122.2204 | 122.5462 | 121.8855 | 0.38493 | -122.5198
1285.625 | 122.4152 | -0.16479 | 122.3373 | 1.4211e-13 | -0.0062991 | 0.0023076 | 0.064614 | -0.0090251 | 0.059071 | -0.006028 | -0.0026725 | -0.0017051 | 0.071074 | 0.025656 | 0.059566 | 0.042253 | 16.6538 | -0.045036 | 122.4095 | 122.3309 | 122.3311 | -0.003531 | 0.001048 | 0.22014 | -0.10672 | 122.0602 | 122.386 | 121.7436 | -0.17788 | 0.16126 | 0.072202 | 0.20705 | 0.11976 | -0.041505 | -0.006434 | -0.00621 | -0.01309 | -0.27714 | 0.16584 | 0.058078 | 0.071168 | 0.048675 | -0.59371 | 122.5743 | 122.4957 | 122.4959 | 16.8186 | -122.3409 | 122.225 | 122.5508 | 121.9084 | 0.38493 | -122.5152
1287.3594 | 122.3877 | -0.19226 | 122.3099 | 1.4211e-13 | -0.0058717 | 0.0023076 | 0.064614 | -0.0088115 | 0.059285 | -0.006028 | -0.0026725 | -0.0017051 | 0.071074 | 0.025228 | 0.059566 | 0.046831 | 17.0521 | -0.040457 | 122.405 | 122.3263 | 122.3357 | -0.017268 | -0.003531 | 0.22472 | -0.10214 | 122.051 | 122.3906 | 121.7482 | -0.1962 | 0.17499 | 0.09509 | 0.23909 | 0.1518 | -0.023189 | 0.016453 | 0.025835 | -0.003939 | -0.25883 | 0.18873 | 0.090123 | 0.094062 | 0.08072 | -0.56166 | 122.5972 | 122.5186 | 122.528 | 17.2444 | -122.3271 | 122.2433 | 122.5829 | 121.9405 | 0.41698 | -122.5061
1289.1094 | 122.5204 | -0.13733 | 122.2916 | 1.4211e-13 | -0.0065127 | 0.002735 | 0.064827 | -0.0092389 | 0.059071 | -0.006028 | -0.0022453 | -0.0014913 | 0.071074 | 0.025656 | 0.059566 | 0.046831 | 18.0319 | -0.040457 | 122.405 | 122.3401 | 122.3357 | -0.021847 | -0.003531 | 0.22472 | -0.097559 | 122.0602 | 122.3906 | 121.7207 | -0.20536 | 0.11548 | 0.1134 | 0.18416 | 0.096872 | -0.01861 | 0.0485 | 0.044145 | -0.068029 | -0.23137 | 0.1338 | 0.03977 | 0.1078 | 0.09903 | -0.57082 | 122.5423 | 122.4774 | 122.473 | 18.1693 | -122.3134 | 122.1975 | 122.5279 | 121.8581 | 0.36205 | -122.4969
1290.875 | 122.4655 | -0.16937 | 122.2961 | 1.4211e-13 | -0.0065127 | 0.002094 | 0.064614 | -0.0090251 | 0.059071 | -0.013659 | -0.0024589 | -0.0014913 | 0.070861 | 0.025442 | 0.059566 | 0.055988 | 19.0118 | -0.040457 | 122.405 | 122.3401 | 122.3357 | -0.017268 | 0.001048 | 0.22472 | -0.097559 | 122.0602 | 122.386 | 121.8123 | -0.20536 | 0.1521 | 0.10882 | 0.22536 | 0.12892 | -0.023189 | 0.043922 | 0.039567 | -0.035985 | -0.23595 | 0.17042 | 0.071814 | 0.1078 | 0.089873 | -0.48383 | 122.5743 | 122.5094 | 122.5051 | 19.1811 | -122.3134 | 122.2296 | 122.5554 | 121.9817 | 0.39409 | -122.5015
1292.6406 | 122.493 | -0.15564 | 122.2778 | 1.4211e-13 | -0.0065127 | 0.0025214 | 0.064827 | -0.0092389 | 0.059071 | -0.006028 | -0.0024589 | -0.0017051 | 0.071074 | 0.025656 | 0.059566 | 0.060567 | 19.0255 | -0.031301 | 122.405 | 122.3355 | 122.3311 | -0.021847 | 0.001048 | 0.22014 | -0.097559 | 122.0556 | 122.3952 | 121.7619 | -0.20994 | 0.13379 | 0.12713 | 0.21621 | 0.12434 | -0.009454 | 0.057654 | 0.053299 | -0.054297 | -0.22221 | 0.15669 | 0.058081 | 0.11238 | 0.11734 | -0.51588 | 122.5606 | 122.4911 | 122.4868 | 19.1811 | -122.2997 | 122.2113 | 122.5508 | 121.9176 | 0.37578 | -122.4878
1294.3281 | 122.5113 | -0.14648 | 122.2824 | 1.4211e-13 | -0.0062991 | 0.0023076 | 0.065041 | -0.0090251 | 0.058858 | 0.0016025 | -0.0022453 | -0.0017051 | 0.070861 | 0.025442 | 0.059566 | 0.060567 | 19.172 | -0.026723 | 122.4095 | 122.3401 | 122.3311 | -0.017268 | -0.00811 | 0.22929 | -0.097559 | 122.0602 | 122.3906 | 121.675 | -0.1962 | 0.12922 | 0.12713 | 0.20705 | 0.11976 | -0.009455 | 0.057655 | 0.048721 | -0.049716 | -0.22221 | 0.13837 | 0.048925 | 0.098641 | 0.10819 | -0.60746 | 122.556 | 122.4865 | 122.4776 | 19.3185 | -122.2997 | 122.2067 | 122.5371 | 121.8214 | 0.37578 | -122.4786
1296.0938 | 122.4014 | -0.17853 | 122.3007 | 1.4211e-13 | -0.0062991 | 0.002094 | 0.065041 | -0.0085979 | 0.058858 | -0.013659 | -0.0024589 | -0.0021323 | 0.071288 | 0.025869 | 0.059139 | 0.055988 | 20.509 | -0.035879 | 122.4004 | 122.3401 | 122.3403 | -0.012689 | -0.003531 | 0.22014 | -0.097559 | 122.0602 | 122.3952 | 121.7253 | -0.20078 | 0.16584 | 0.099666 | 0.23452 | 0.14265 | -0.02319 | 0.039345 | 0.039569 | -0.022251 | -0.24052 | 0.175 | 0.080969 | 0.10322 | 0.094453 | -0.5754 | 122.5789 | 122.5186 | 122.5188 | 20.6875 | -122.3134 | 122.2387 | 122.5737 | 121.9038 | 0.39866 | -122.5015
1297.8438 | 122.4747 | -0.16937 | 122.3099 | 1.4211e-13 | -0.0062991 | 0.0018804 | 0.0644 | -0.0090251 | 0.059071 | 0.0016025 | -0.0024589 | -0.0017051 | 0.070861 | 0.025442 | 0.059353 | 0.069723 | 20.6326 | -0.026723 | 122.4141 | 122.3355 | 122.3357 | -0.049321 | -0.003531 | 0.23387 | -0.10214 | 122.0602 | 122.3952 | 121.7345 | -0.20078 | 0.12005 | 0.10425 | 0.2391 | 0.14265 | 0.022598 | 0.025611 | 0.025835 | -0.031406 | -0.24968 | 0.16584 | 0.067235 | 0.098641 | 0.085298 | -0.5754 | 122.5835 | 122.5049 | 122.5051 | 20.802 | -122.3592 | 122.2296 | 122.5645 | 121.9038 | 0.40325 | -122.5107
1299.6094 | 122.3557 | -0.1831 | 122.3419 | 1.4211e-13 | -0.0060855 | 0.002094 | 0.065041 | -0.0085979 | 0.058858 | 0.0016025 | -0.0024589 | -0.0019187 | 0.071074 | 0.025656 | 0.059566 | 0.060567 | 19.8634 | -0.026723 | 122.4095 | 122.3401 | 122.3311 | -0.017268 | -0.003531 | 0.23387 | -0.10214 | 122.0556 | 122.3952 | 121.7482 | -0.20536 | 0.16584 | 0.067624 | 0.24367 | 0.15638 | -0.009455 | -0.001854 | -0.010788 | -0.022253 | -0.2863 | 0.17957 | 0.080967 | 0.10322 | 0.053254 | -0.59371 | 122.5926 | 122.5232 | 122.5142 | 20.0465 | -122.3592 | 122.2387 | 122.5783 | 121.9313 | 0.41698 | -122.5473
1301.3594 | 122.3877 | -0.19684 | 122.3282 | 1.4211e-13 | -0.0062991 | 0.0025214 | 0.064827 | -0.0090251 | 0.058644 | -0.013659 | -0.0024589 | -0.0014913 | 0.071074 | 0.025228 | 0.058925 | 0.069723 | 18.998 | -0.026723 | 122.4095 | 122.3446 | 122.3357 | -0.00811 | -0.003531 | 0.23387 | -0.097559 | 122.0602 | 122.3952 | 121.7436 | -0.20078 | 0.18873 | 0.081357 | 0.26656 | 0.17012 | -0.018613 | 0.016458 | 0.007524 | -0.003941 | -0.26799 | 0.19331 | 0.099279 | 0.10322 | 0.066987 | -0.58455 | 122.6064 | 122.5415 | 122.5325 | 19.1949 | -122.3363 | 122.257 | 122.592 | 121.9405 | 0.43071 | -122.529
1303.0469 | 122.5021 | -0.14191 | 122.2916 | 1.4211e-13 | -0.0060855 | 0.0025214 | 0.064827 | -0.0090251 | 0.058644 | -0.006028 | -0.0026725 | -0.0019187 | 0.070861 | 0.025656 | 0.059566 | 0.069723 | 19.2865 | -0.022144 | 122.4141 | 122.3401 | 122.3357 | -0.017268 | 0.001048 | 0.22929 | -0.10672 | 122.0648 | 122.3998 | 121.7299 | -0.1962 | 0.12464 | 0.12256 | 0.21163 | 0.11976 | -0.004876 | 0.0485 | 0.044145 | -0.054293 | -0.22679 | 0.14295 | 0.03519 | 0.089483 | 0.10819 | -0.56167 | 122.556 | 122.482 | 122.4776 | 19.4284 | -122.3088 | 122.2067 | 122.5417 | 121.8718 | 0.3712 | -122.4878
1304.7969 | 122.406 | -0.19226 | 122.3099 | 1.4211e-13 | -0.0062991 | 0.0023076 | 0.064614 | -0.0092389 | 0.059071 | -0.006028 | -0.0024589 | -0.0017051 | 0.071074 | 0.026083 | 0.059139 | 0.065145 | 19.9046 | -0.017566 | 122.4141 | 122.3446 | 122.3403 | -0.003531 | 0.005626 | 0.22929 | -0.10672 | 122.0648 | 122.3998 | 121.7528 | -0.20536 | 0.18873 | 0.10425 | 0.25741 | 0.17469 | -0.014035 | 0.034769 | 0.030414 | -0.013097 | -0.2451 | 0.19789 | 0.085544 | 0.098641 | 0.089877 | -0.55708 | 122.6064 | 122.5369 | 122.5326 | 20.0969 | -122.3134 | 122.257 | 122.592 | 121.9451 | 0.42156 | -122.5152
1306.4844 | 122.4655 | -0.16479 | 122.2824 | 1.4211e-13 | -0.0060855 | 0.0023076 | 0.064827 | -0.0088115 | 0.059285 | -0.013659 | -0.0026725 | -0.0017051 | 0.071074 | 0.025228 | 0.059353 | 0.074302 | 19.9595 | -0.012988 | 122.4095 | 122.3492 | 122.3449 | -0.021847 | -0.003531 | 0.22929 | -0.097559 | 122.0648 | 122.3998 | 121.7528 | -0.20078 | 0.14295 | 0.12713 | 0.2391 | 0.15181 | 0.008859 | 0.066813 | 0.062457 | -0.035984 | -0.21763 | 0.16126 | 0.067236 | 0.10322 | 0.11734 | -0.52962 | 122.5743 | 122.514 | 122.5097 | 20.1243 | -122.3043 | 122.2296 | 122.5645 | 121.9176 | 0.39409 | -122.4832
1308.2344 | 122.4655 | -0.15564 | 122.2961 | 1.4211e-13 | -0.0060855 | 0.0023076 | 0.064614 | -0.0088115 | 0.059285 | 0.0016025 | -0.0026725 | -0.0019187 | 0.071074 | 0.025442 | 0.059353 | 0.069723 | 19.6116 | -0.008409 | 122.4187 | 122.3492 | 122.354 | -0.026426 | -0.00811 | 0.23387 | -0.097559 | 122.0648 | 122.3998 | 121.7345 | -0.20536 | 0.12921 | 0.12256 | 0.22536 | 0.14723 | 0.018017 | 0.05308 | 0.057881 | -0.049718 | -0.23137 | 0.14753 | 0.058081 | 0.1078 | 0.10361 | -0.56167 | 122.5743 | 122.5049 | 122.5097 | 19.7672 | -122.3226 | 122.2204 | 122.5554 | 121.8901 | 0.38951 | -122.5015
1310 | 122.5204 | -0.15106 | 122.2549 | 1.4211e-13 | -0.0062991 | 0.002094 | 0.065041 | -0.0090251 | 0.059071 | -0.013659 | -0.0024589 | -0.0014913 | 0.071074 | 0.025656 | 0.059353 | 0.074302 | 19.5704 | -0.008409 | 122.4187 | 122.3446 | 122.3449 | -0.017268 | 0.005626 | 0.23387 | -0.097559 | 122.0602 | 122.3998 | 121.7436 | -0.20536 | 0.13379 | 0.16376 | 0.22536 | 0.14265 | 0.008859 | 0.0897 | 0.089923 | -0.054296 | -0.19475 | 0.15669 | 0.053503 | 0.1078 | 0.14481 | -0.51131 | 122.5698 | 122.4957 | 122.4959 | 19.7214 | -122.2722 | 122.2113 | 122.5508 | 121.8947 | 0.38494 | -122.4603
1311.6875 | 122.4564 | -0.15564 | 122.287 | 1.4211e-13 | -0.0062991 | 0.002094 | 0.064614 | -0.0088115 | 0.058644 | -0.006028 | -0.0024589 | -0.0017051 | 0.070647 | 0.025656 | 0.059139 | 0.07888 | 20.5364 | 0.000747 | 122.4187 | 122.3401 | 122.3403 | -0.021847 | -0.00811 | 0.23845 | -0.097559 | 122.0648 | 122.3952 | 121.7528 | -0.20994 | 0.13379 | 0.13171 | 0.23452 | 0.15639 | 0.022594 | 0.053078 | 0.053302 | -0.054297 | -0.22221 | 0.14753 | 0.058081 | 0.11238 | 0.10819 | -0.53419 | 122.5743 | 122.4957 | 122.4959 | 20.6921 | -122.3088 | 122.2204 | 122.5508 | 121.9084 | 0.39409 | -122.4969
1313.4219 | 122.4976 | -0.13733 | 122.2733 | 1.4211e-13 | -0.0065127 | 0.0023076 | 0.064827 | -0.0090251 | 0.058858 | -0.006028 | -0.0022453 | -0.0017051 | 0.071288 | 0.025869 | 0.059139 | 0.074302 | 20.6738 | -0.003831 | 122.4187 | 122.3446 | 122.3449 | -0.021847 | 0.005626 | 0.23387 | -0.10214 | 122.0648 | 122.3906 | 121.7574 | -0.1962 | 0.11548 | 0.14545 | 0.21163 | 0.1335 | 0.018016 | 0.07139 | 0.071613 | -0.058871 | -0.20848 | 0.14295 | 0.035191 | 0.094062 | 0.11734 | -0.51588 | 122.556 | 122.482 | 122.4822 | 20.8111 | -122.2951 | 122.2021 | 122.5279 | 121.8947 | 0.3712 | -122.4695
1315.1094 | 122.3831 | -0.21057 | 122.3328 | 1.4211e-13 | -0.0062991 | 0.0023076 | 0.064827 | -0.0092389 | 0.058644 | -0.006028 | -0.0024589 | -0.0019187 | 0.070861 | 0.025869 | 0.059353 | 0.069723 | 20.2709 | -0.003831 | 122.4141 | 122.3355 | 122.3449 | -0.017268 | -0.00811 | 0.24303 | -0.097559 | 122.0602 | 122.3998 | 121.7253 | -0.20078 | 0.1933 | 0.081358 | 0.28029 | 0.20674 | 0.013437 | 0.002722 | 0.012103 | 0.009792 | -0.27257 | 0.20246 | 0.11301 | 0.10322 | 0.066988 | -0.60744 | 122.6247 | 122.5461 | 122.5554 | 20.4815 | -122.35 | 122.2708 | 122.6103 | 121.9359 | 0.4536 | -122.5335
1316.8594 | 122.5067 | -0.17395 | 122.3007 | 1.4211e-13 | -0.0062991 | 0.0023076 | 0.064827 | -0.0088115 | 0.059071 | -0.006028 | -0.0024589 | -0.0019187 | 0.070861 | 0.025442 | 0.059566 | 0.07888 | 20.8524 | 0.005325 | 122.4187 | 122.3446 | 122.3494 | -0.012689 | -0.003531 | 0.23845 | -0.10672 | 122.0602 | 122.4089 | 121.7436 | -0.20536 | 0.16126 | 0.11798 | 0.25283 | 0.17927 | 0.018014 | 0.043924 | 0.048726 | -0.031408 | -0.24052 | 0.17042 | 0.067233 | 0.098641 | 0.10819 | -0.55709 | 122.5927 | 122.5186 | 122.5234 | 21.0263 | -122.3134 | 122.2341 | 122.5829 | 121.9176 | 0.4124 | -122.5061
1318.6094 | 122.4243 | -0.17853 | 122.2916 | 1.4211e-13 | -0.0060855 | 0.0023076 | 0.064614 | -0.0090251 | 0.059285 | -0.006028 | -0.0024589 | -0.0014913 | 0.071288 | 0.025869 | 0.059566 | 0.069723 | 21.6261 | 0.000747 | 122.4187 | 122.3446 | 122.3449 | -0.017268 | -0.00811 | 0.24303 | -0.10214 | 122.0694 | 122.3998 | 121.7345 | -0.20078 | 0.16126 | 0.12713 | 0.24825 | 0.17927 | 0.018015 | 0.053079 | 0.053302 | -0.022251 | -0.22221 | 0.17042 | 0.07639 | 0.098641 | 0.10819 | -0.55709 | 122.5972 | 122.5232 | 122.5234 | 21.8047 | -122.3088 | 122.2479 | 122.5783 | 121.913 | 0.42156 | -122.4923
1320.375 | 122.5525 | -0.16022 | 122.2778 | 1.4211e-13 | -0.0062991 | 0.0025214 | 0.064827 | -0.0094525 | 0.058858 | 0.0016025 | -0.0022453 | -0.0012777 | 0.070861 | 0.025442 | 0.059353 | 0.074302 | 22.2672 | 0.005325 | 122.4095 | 122.3401 | 122.3494 | -0.012689 | 0.001048 | 0.23845 | -0.10214 | 122.0556 | 122.3998 | 121.6978 | -0.20536 | 0.14753 | 0.13171 | 0.23452 | 0.16554 | 0.018014 | 0.062233 | 0.071614 | -0.045141 | -0.22221 | 0.16126 | 0.058079 | 0.10322 | 0.12192 | -0.57998 | 122.5698 | 122.5003 | 122.5097 | 22.4274 | -122.2905 | 122.2158 | 122.56 | 121.8581 | 0.39867 | -122.4832
1322.125 | 122.438 | -0.14191 | 122.2961 | 1.4211e-13 | -0.0062991 | 0.0023076 | 0.064827 | -0.0090251 | 0.058858 | -0.006028 | -0.0024589 | -0.0017051 | 0.070861 | 0.025656 | 0.059353 | 0.07888 | 22.0657 | 0.009904 | 122.4187 | 122.3446 | 122.3494 | -0.017268 | 0.001048 | 0.24761 | -0.097559 | 122.0694 | 122.4089 | 121.7299 | -0.18246 | 0.12464 | 0.12256 | 0.22079 | 0.15181 | 0.027172 | 0.048501 | 0.053303 | -0.040557 | -0.22679 | 0.14295 | 0.044348 | 0.084905 | 0.11277 | -0.56624 | 122.5606 | 122.4866 | 122.4914 | 22.2076 | -122.3134 | 122.2113 | 122.5508 | 121.8718 | 0.38952 | -122.4786
1323.875 | 122.3923 | -0.18768 | 122.3373 | 1.4211e-13 | -0.0060855 | 0.0025214 | 0.065041 | -0.0090251 | 0.058858 | -0.006028 | -0.0022453 | -0.0014913 | 0.070861 | 0.025869 | 0.059566 | 0.07888 | 21.6536 | 0.005325 | 122.4095 | 122.3446 | 122.3494 | -0.017268 | 0.001048 | 0.25219 | -0.10214 | 122.0694 | 122.4135 | 121.6933 | -0.20536 | 0.17041 | 0.072202 | 0.26656 | 0.19301 | 0.022593 | 0.007303 | 0.012105 | -0.017675 | -0.26799 | 0.18873 | 0.085545 | 0.10322 | 0.076147 | -0.64407 | 122.5972 | 122.5323 | 122.5371 | 21.8413 | -122.3546 | 122.257 | 122.6012 | 121.881 | 0.43987 | -122.5427
1325.6406 | 122.4838 | -0.14191 | 122.3053 | 1.4211e-13 | -0.0060855 | 0.0023076 | 0.0644 | -0.0090251 | 0.058858 | 0.0092325 | -0.0022453 | -0.0019187 | 0.071074 | 0.025442 | 0.059139 | 0.092615 | 21.5025 | 0.009904 | 122.4187 | 122.3538 | 122.3494 | -0.017268 | 0.001048 | 0.25219 | -0.097559 | 122.0694 | 122.4135 | 121.7207 | -0.20536 | 0.12464 | 0.1134 | 0.23452 | 0.15181 | 0.027172 | 0.048504 | 0.044148 | -0.063451 | -0.23594 | 0.14295 | 0.044348 | 0.1078 | 0.10819 | -0.58456 | 122.5606 | 122.4957 | 122.4914 | 21.6444 | -122.3226 | 122.2113 | 122.5554 | 121.8626 | 0.3941 | -122.5107
1327.375 | 122.5159 | -0.14648 | 122.2778 | 1.4211e-13 | -0.0062991 | 0.002735 | 0.065041 | -0.0088115 | 0.058858 | -0.006028 | -0.0024589 | -0.0017051 | 0.070861 | 0.025869 | 0.059353 | 0.083459 | 20.8753 | 0.014482 | 122.4095 | 122.3492 | 122.354 | -0.012689 | 0.001048 | 0.24761 | -0.10672 | 122.0694 | 122.4043 | 121.7665 | -0.20536 | 0.13379 | 0.13171 | 0.22994 | 0.16097 | 0.027171 | 0.071391 | 0.076192 | -0.058874 | -0.20848 | 0.14753 | 0.039767 | 0.098641 | 0.1265 | -0.51131 | 122.556 | 122.4957 | 122.5005 | 21.0217 | -122.2905 | 122.2158 | 122.5508 | 121.913 | 0.39409 | -122.4832
1329.0625 | 122.5296 | -0.13733 | 122.2778 | 1.4211e-13 | -0.0062991 | 0.0023076 | 0.065041 | -0.0088115 | 0.059071 | -0.006028 | -0.0024589 | -0.0019187 | 0.070861 | 0.025442 | 0.059353 | 0.088037 | 21.1546 | 0.009904 | 122.4233 | 122.3538 | 122.3494 | -0.017268 | 0.001048 | 0.25219 | -0.10214 | 122.0739 | 122.4043 | 121.7162 | -0.20078 | 0.12006 | 0.14545 | 0.22537 | 0.14723 | 0.027172 | 0.07597 | 0.071614 | -0.06345 | -0.2039 | 0.13838 | 0.035191 | 0.098641 | 0.1265 | -0.56167 | 122.5606 | 122.4911 | 122.4868 | 21.2919 | -122.2951 | 122.2113 | 122.5417 | 121.8535 | 0.38952 | -122.4786
1330.8281 | 122.4426 | -0.15564 | 122.3282 | 1.4211e-13 | -0.0062991 | 0.0025214 | 0.065041 | -0.0092389 | 0.058858 | 0.0016025 | -0.0020317 | -0.0019187 | 0.070861 | 0.025656 | 0.059566 | 0.083459 | 21.6124 | 0.005325 | 122.4187 | 122.3538 | 122.3586 | -0.012689 | 0.001048 | 0.24761 | -0.10214 | 122.0694 | 122.4089 | 121.7528 | -0.20536 | 0.14295 | 0.090514 | 0.2391 | 0.16096 | 0.018014 | 0.025616 | 0.030417 | -0.049718 | -0.25883 | 0.15669 | 0.053502 | 0.10322 | 0.080723 | -0.57539 | 122.5743 | 122.5094 | 122.5142 | 21.7681 | -122.3409 | 122.225 | 122.5645 | 121.9084 | 0.40325 | -122.5335
1332.5156 | 122.3785 | -0.19226 | 122.3419 | 1.4211e-13 | -0.0062991 | 0.0023076 | 0.064827 | -0.0088115 | 0.059071 | 0.0016025 | -0.0024589 | -0.0019187 | 0.071074 | 0.025656 | 0.059353 | 0.097194 | 21.7635 | 0.028217 | 122.4233 | 122.3675 | 122.3586 | -0.012689 | 0.010205 | 0.25219 | -0.092981 | 122.0831 | 122.4181 | 121.7436 | -0.20078 | 0.17957 | 0.081359 | 0.28946 | 0.22048 | 0.040906 | 0.025619 | 0.016684 | -0.008518 | -0.25883 | 0.20247 | 0.09928 | 0.1078 | 0.076147 | -0.59829 | 122.6155 | 122.5598 | 122.5509 | 21.9558 | -122.3546 | 122.2754 | 122.6103 | 121.9359 | 0.44445 | -122.5427
1334.2656 | 122.3923 | -0.16937 | 122.3465 | 1.4211e-13 | -0.0062991 | 0.0025214 | 0.065041 | -0.0088115 | 0.058858 | 0.0016025 | -0.0022453 | -0.0017051 | 0.070861 | 0.025869 | 0.059353 | 0.092615 | 21.4522 | 0.041952 | 122.4324 | 122.363 | 122.3678 | -0.012689 | 0.010205 | 0.25677 | -0.092981 | 122.0831 | 122.4272 | 121.7711 | -0.19162 | 0.15668 | 0.085938 | 0.26199 | 0.21132 | 0.054641 | 0.016463 | 0.021263 | -0.022249 | -0.26341 | 0.17958 | 0.076392 | 0.098641 | 0.080726 | -0.57539 | 122.6018 | 122.5323 | 122.5371 | 21.6215 | -122.3592 | 122.2525 | 122.5966 | 121.9405 | 0.42614 | -122.5381
1336.0156 | 122.4243 | -0.19226 | 122.319 | 1.4211e-13 | -0.0060855 | 0.0023076 | 0.065041 | -0.0088115 | 0.059071 | 0.0016025 | -0.0026725 | -0.0021323 | 0.071074 | 0.025869 | 0.059139 | 0.10177 | 21.7086 | 0.041952 | 122.4279 | 122.363 | 122.3632 | -0.012689 | 0.001048 | 0.24761 | -0.097559 | 122.0785 | 122.4181 | 121.7528 | -0.18704 | 0.17957 | 0.10883 | 0.29403 | 0.23421 | 0.054641 | 0.043929 | 0.044151 | 0.005218 | -0.24052 | 0.19331 | 0.094702 | 0.089484 | 0.099035 | -0.56624 | 122.6201 | 122.5552 | 122.5554 | 21.9008 | -122.3317 | 122.2708 | 122.6103 | 121.9451 | 0.43987 | -122.5061
1337.7031 | 122.406 | -0.1831 | 122.3511 | 1.4211e-13 | -0.0065127 | 0.0025214 | 0.065041 | -0.0090251 | 0.058858 | -0.013659 | -0.0020317 | -0.0017051 | 0.071288 | 0.025228 | 0.059139 | 0.088037 | 21.356 | 0.041952 | 122.4279 | 122.3584 | 122.3632 | -0.012689 | 0.001048 | 0.24761 | -0.10672 | 122.0877 | 122.4089 | 121.7574 | -0.19162 | 0.17042 | 0.076783 | 0.27114 | 0.22506 | 0.054641 | 0.007307 | 0.012108 | -0.008517 | -0.2634 | 0.18415 | 0.076388 | 0.084905 | 0.057835 | -0.5937 | 122.611 | 122.5415 | 122.5463 | 21.5391 | -122.3638 | 122.2708 | 122.592 | 121.9405 | 0.43071 | -122.5427
1339.4375 | 117.7597 | -92.363 | 25.2365 | 1.4211e-13 | -0.0071537 | 0.0012394 | 0.060767 | -0.0083841 | 0.056721 | 0.0092325 | -0.0030999 | -0.0023459 | 0.06787 | 0.026083 | 0.058712 | -91.8277 | -10.6164 | -92.0685 | 25.3569 | 25.3447 | 25.5028 | -92.4703 | -92.1409 | -0.60403 | -92.1708 | 25.2204 | 25.3563 | 25.3137 | -92.6608 | -0.10736 | 0.12037 | 0.5353 | 0.2945 | 0.40186 | 0.10819 | 0.26633 | -0.29786 | -0.016064 | 0.22207 | 0.19214 | 0.49 | 0.11976 | 0.077176 | 117.7199 | 117.7077 | 117.8658 | 81.7466 | -117.7068 | 117.5834 | 117.7192 | 117.6767 | 91.7589 | -117.8973
1341.1875 | 117.2836 | -92.0242 | 25.0305 | 1.4211e-13 | -0.0071537 | 0.0012394 | 0.060554 | -0.0088115 | 0.056294 | -0.013659 | -0.0033135 | -0.0023459 | 0.067015 | 0.025869 | 0.058071 | -91.5163 | -10.5385 | -91.7617 | 25.1234 | 25.1203 | 25.2648 | -92.1498 | -91.8158 | -0.48498 | -91.8549 | 24.9961 | 25.1365 | 25.1031 | -92.3449 | -0.12558 | 0.092862 | 0.50788 | 0.2625 | 0.38808 | 0.089821 | 0.23424 | -0.32067 | -0.034418 | 0.20841 | 0.16933 | 0.48999 | 0.10598 | 0.072553 | 117.1476 | 117.1446 | 117.289 | 81.4857 | -117.1803 | 117.0203 | 117.1607 | 117.1273 | 91.5392 | -117.3754
1342.875 | 116.7892 | -91.7358 | 24.9481 | 1.4211e-13 | -0.0073675 | 0.001453 | 0.06034 | -0.0081705 | 0.05608 | 0.0016025 | -0.0028861 | -0.0025597 | 0.067015 | 0.025869 | 0.057857 | -91.2325 | -10.9231 | -91.4641 | 24.9448 | 25.0013 | 25.1457 | -91.8522 | -91.5319 | -0.46667 | -91.5664 | 24.8771 | 25.0037 | 24.984 | -92.0473 | -0.11634 | -0.003298 | 0.50335 | 0.2717 | 0.38804 | 0.053167 | 0.19759 | -0.31143 | -0.071061 | 0.2039 | 0.16939 | 0.48083 | 0.055599 | 0.035907 | 116.6807 | 116.7371 | 116.8816 | 80.8127 | -116.8003 | 116.6129 | 116.7396 | 116.7199 | 91.2692 | -116.9954
1344.625 | 116.5009 | -91.4886 | 24.852 | 1.4211e-13 | -0.0071537 | 0.001453 | 0.06034 | -0.0085979 | 0.055867 | -0.013659 | -0.0035271 | -0.0027733 | 0.067015 | 0.025869 | 0.057857 | -90.9761 | -10.8774 | -91.2123 | 24.8441 | 24.9006 | 25.0541 | -91.6141 | -91.2847 | -0.44836 | -91.3192 | 24.7763 | 24.903 | 24.8879 | -91.8092 | -0.12543 | -0.007892 | 0.51255 | 0.27631 | 0.40174 | 0.048561 | 0.20215 | -0.32053 | -0.075657 | 0.20396 | 0.16945 | 0.48998 | 0.051 | 0.035887 | 116.3327 | 116.3892 | 116.5428 | 80.6113 | -116.4661 | 116.265 | 116.3916 | 116.3765 | 91.0403 | -116.6612
1346.375 | 116.2949 | -91.2872 | 24.7513 | 1.4211e-13 | -0.0075811 | 0.0012394 | 0.059913 | -0.0081705 | 0.056294 | -0.006028 | -0.0030999 | -0.0025597 | 0.067015 | 0.025869 | 0.057644 | -90.7792 | -10.74 | -91.0155 | 24.7754 | 24.8273 | 24.9809 | -91.4126 | -91.0924 | -0.4392 | -91.1315 | 24.6985 | 24.8297 | 24.4575 | -91.6123 | -0.12537 | 0.02414 | 0.508 | 0.27176 | 0.39713 | 0.076006 | 0.2296 | -0.32505 | -0.052784 | 0.19485 | 0.15576 | 0.48082 | 0.07845 | -0.29379 | 116.0627 | 116.1145 | 116.2681 | 80.5472 | -116.1639 | 115.9857 | 116.117 | 115.7447 | 90.848 | -116.3636
1348.0625 | 116.0706 | -91.1179 | 24.7055 | 1.4211e-13 | -0.0071537 | 0.0012394 | 0.060126 | -0.0083841 | 0.055653 | -0.006028 | -0.0030999 | -0.0025597 | 0.066588 | 0.025869 | 0.057216 | -90.6281 | -10.5981 | -90.8644 | 24.7159 | 24.7082 | 24.9214 | -91.1562 | -90.9413 | -0.44836 | -90.9804 | 24.6481 | 24.7702 | 24.4071 | -91.4749 | -0.038323 | 0.010398 | 0.48972 | 0.25347 | 0.2918 | 0.002731 | 0.21586 | -0.35706 | -0.05737 | 0.17657 | 0.13749 | 0.49455 | 0.064705 | -0.29838 | 115.8338 | 115.8261 | 116.0392 | 80.5198 | -115.8617 | 115.766 | 115.8881 | 115.525 | 90.6695 | -116.1804
1349.7969 | 115.8875 | -91.0309 | 24.6506 | 1.4211e-13 | -0.0073675 | 0.0010256 | 0.059913 | -0.0083841 | 0.055439 | -0.006028 | -0.0030999 | -0.0027733 | 0.066588 | 0.025656 | 0.05743 | -90.4954 | -10.6393 | -90.7499 | 24.6701 | 24.6624 | 24.8664 | -91.0326 | -90.8222 | -0.43462 | -90.8613 | 24.5978 | 24.7198 | 24.4621 | -91.3513 | -0.001667 | 0.019545 | 0.53552 | 0.28095 | 0.28262 | 0.011873 | 0.21585 | -0.32041 | -0.052803 | 0.20864 | 0.16956 | 0.48997 | 0.069272 | -0.18851 | 115.701 | 115.6933 | 115.8973 | 80.3916 | -115.6831 | 115.6287 | 115.7507 | 115.493 | 90.5963 | -116.0019
1351.5469 | 115.7959 | -90.8844 | 24.5865 | 1.4211e-13 | -0.0073675 | 0.001453 | 0.059699 | -0.0088115 | 0.055439 | -0.013659 | -0.0030999 | -0.0025597 | 0.066374 | 0.025869 | 0.05743 | -90.3992 | -10.6713 | -90.6492 | 24.6198 | 24.6167 | 24.7657 | -90.9364 | -90.7307 | -0.44378 | -90.7652 | 24.5474 | 24.6786 | 24.3797 | -91.2551 | -0.051995 | 0.03327 | 0.48518 | 0.23519 | 0.28719 | 0.03017 | 0.1792 | -0.37074 | -0.039079 | 0.15373 | 0.11923 | 0.48997 | 0.092151 | -0.20684 | 115.5042 | 115.5011 | 115.6501 | 80.2131 | -115.5229 | 115.4318 | 115.563 | 115.2641 | 90.4406 | -115.8416
1353.2969 | 114.8621 | -29.4479 | 85.4691 | 1.4211e-13 | -0.0067265 | 0.0016666 | 0.059485 | -0.0088115 | 0.054157 | -0.006028 | -0.0028861 | -0.0019187 | 0.06616 | 0.025869 | 0.055507 | -34.4239 | 9.1861 | -34.5286 | 79.8488 | 79.8614 | 79.8371 | -34.5653 | -34.5499 | 0.25677 | -34.6348 | 79.7 | 79.8645 | 79.7945 | -34.6564 | -5.1173 | -5.6202 | -4.9759 | -5.0807 | 0.036609 | -5.6077 | -5.6319 | -5.2084 | -5.7691 | -5.102 | -5.1868 | 0.021611 | -5.6045 | -5.6746 | 109.2968 | 109.3093 | 109.2851 | 38.634 | -120.0343 | 109.1479 | 109.3125 | 109.2424 | 29.7047 | -120.1254
1355 | 119.0094 | -0.16937 | 118.9087 | 1.4211e-13 | -0.0065127 | 0.0023076 | 0.063118 | -0.0090251 | 0.056721 | -0.006028 | -0.0024589 | -0.0017051 | 0.069151 | 0.025442 | 0.057644 | 0.10635 | 19.6116 | 0.064843 | 118.9483 | 118.8784 | 118.8972 | -0.026426 | 0.001048 | 0.36666 | -0.097559 | 118.608 | 118.9475 | 118.2959 | -0.2603 | 0.14295 | 0.039591 | 0.27572 | 0.23422 | 0.091269 | -0.030293 | -0.011512 | -0.090931 | -0.30068 | 0.17042 | 0.071814 | 0.16274 | 0.038795 | -0.61274 | 119.1177 | 119.0478 | 119.0666 | 19.7809 | -118.9351 | 118.7774 | 119.1169 | 118.4653 | 0.53603 | -119.169
1356.75 | 115.7547 | -24.6185 | 91.301 | 1.4211e-13 | -0.0071537 | 0.0016666 | 0.061836 | -0.0090251 | 0.055653 | 0.0016025 | -0.0028861 | -0.0019187 | 0.067442 | 0.025442 | 0.056789 | -14.3522 | 12.6887 | -14.3751 | 102.5027 | 102.4217 | 102.5195 | -14.6103 | -14.5272 | -0.008798 | -14.6258 | 102.1392 | 102.4325 | 102.1838 | -14.6973 | 10.0082 | 11.2017 | 10.2663 | 10.2435 | 0.23525 | 11.1208 | 11.2186 | 9.9212 | 10.8382 | 10.0913 | 9.9927 | 0.071509 | 11.1315 | 10.8829 | 127.1212 | 127.0403 | 127.138 | 37.3072 | -105.9113 | 126.7577 | 127.051 | 126.8024 | 24.6097 | -105.9983
1358.5 | 119.101 | -0.15564 | 118.9362 | 1.4211e-13 | -0.0060855 | 0.002094 | 0.063118 | -0.0090251 | 0.057148 | -0.013659 | -0.0024589 | -0.0017051 | 0.069151 | 0.025442 | 0.057216 | 0.092615 | 16.489 | 0.064843 | 119.0353 | 118.9746 | 118.9796 | -0.053899 | -0.00811 | 0.3575 | -0.10672 | 118.7637 | 119.0299 | 118.3829 | -0.26488 | 0.10174 | 0.099114 | 0.24826 | 0.22048 | 0.11874 | 0.038398 | 0.043437 | -0.10924 | -0.17247 | 0.14753 | 0.048923 | 0.15817 | 0.093743 | -0.55322 | 119.1909 | 119.1302 | 119.1352 | 16.6446 | -118.9901 | 118.9193 | 119.1855 | 118.5386 | 0.51314 | -119.201
1360.1875 | 119.2932 | -0.14191 | 119.0735 | 1.4211e-13 | -0.0060855 | 0.002094 | 0.06269 | -0.0090251 | 0.056721 | 0.0016025 | -0.0026725 | -0.0017051 | 0.068938 | 0.025442 | 0.057644 | 0.10177 | 15.8846 | 0.060265 | 119.1452 | 119.0845 | 119.0895 | -0.21874 | -0.012689 | 0.33918 | -0.11587 | 118.8736 | 119.1444 | 118.5249 | -0.27862 | -0.076834 | 0.071667 | 0.24368 | 0.20217 | 0.27901 | 0.010964 | 0.015995 | -0.13671 | -0.19992 | 0.12922 | 0.026033 | 0.16275 | 0.070879 | -0.54861 | 119.2871 | 119.2264 | 119.2314 | 16.0265 | -119.2922 | 119.0155 | 119.2863 | 118.6668 | 0.48109 | -119.3521
1361.9375 | 119.3024 | -0.20142 | 119.1925 | 1.4211e-13 | -0.0062991 | 0.0023076 | 0.063118 | -0.0092389 | 0.057148 | 0.0016025 | -0.0022453 | -0.0017051 | 0.069151 | 0.025442 | 0.057644 | 0.11093 | 15.1291 | 0.051108 | 119.255 | 119.1898 | 119.1902 | -0.12258 | -0.00811 | 0.29797 | -0.1113 | 118.9789 | 119.2543 | 118.6485 | -0.26946 | 0.078833 | 0.062529 | 0.31234 | 0.25252 | 0.17369 | -0.00274 | -0.002295 | -0.068046 | -0.21363 | 0.19331 | 0.09012 | 0.15817 | 0.061747 | -0.54401 | 119.4564 | 119.3912 | 119.3916 | 15.3305 | -119.3151 | 119.1803 | 119.4557 | 118.8499 | 0.49939 | -119.462
1363.6875 | 116.2582 | -26.7105 | 89.209 | 1.4211e-13 | -0.0062991 | 0.002094 | 0.06269 | -0.0094525 | 0.056294 | -0.006028 | -0.0024589 | -0.0021323 | 0.068511 | 0.025442 | 0.05743 | -6.3217 | 12.7116 | -6.3173 | 112.4332 | 112.2298 | 112.4688 | -6.6476 | -6.5877 | -0.76886 | -6.7046 | 111.9417 | 112.2994 | 111.4967 | -6.8996 | 20.063 | 23.2243 | 20.3888 | 20.3932 | 0.33027 | 23.0208 | 23.2598 | 19.8109 | 22.7327 | 20.1228 | 20.0059 | 0.19495 | 23.0904 | 22.2877 | 139.1437 | 138.9403 | 139.1793 | 39.4221 | -95.8565 | 138.6522 | 139.0099 | 138.2072 | 25.9416 | -96.1086
1365.4219 | 119.3344 | -0.1831 | 119.2383 | 1.4211e-13 | -0.0067265 | 0.0023076 | 0.062904 | -0.0092389 | 0.056935 | 0.0016025 | -0.0022453 | -0.0014913 | 0.069365 | 0.025656 | 0.05743 | 0.10177 | 14.6758 | 0.051108 | 119.2825 | 119.2218 | 119.2314 | -0.10885 | -0.012689 | 0.33003 | -0.1113 | 119.0109 | 119.2863 | 118.6164 | -0.26488 | 0.074258 | 0.044223 | 0.28488 | 0.23421 | 0.15996 | -0.016464 | -0.006864 | -0.081778 | -0.22736 | 0.17042 | 0.071809 | 0.15359 | 0.048021 | -0.62183 | 119.4656 | 119.4049 | 119.4145 | 14.8589 | -119.3471 | 119.194 | 119.4694 | 118.7996 | 0.51313 | -119.5032
1367.1094 | 119.4168 | -0.19226 | 119.3024 | 1.4211e-13 | -0.0067265 | 0.002094 | 0.063331 | -0.0092389 | 0.057148 | -0.006028 | -0.0026725 | -0.0014913 | 0.069365 | 0.025442 | 0.057644 | 0.10177 | 15.1841 | 0.04653 | 119.3878 | 119.3317 | 119.3276 | -0.19127 | -0.012689 | 0.33003 | -0.11587 | 119.1116 | 119.3916 | 118.7492 | -0.26488 | 0.000994 | 0.085439 | 0.29403 | 0.23879 | 0.2378 | 0.029343 | 0.0252 | -0.072622 | -0.19072 | 0.17957 | 0.076387 | 0.14901 | 0.089242 | -0.55314 | 119.5801 | 119.524 | 119.5198 | 15.3763 | -119.4936 | 119.3039 | 119.5839 | 118.9415 | 0.52229 | -119.5673
1368.8594 | 119.4946 | -0.17853 | 119.3665 | 1.4211e-13 | -0.0062991 | 0.0023076 | 0.062904 | -0.0094525 | 0.057576 | 0.0092325 | -0.0024589 | -0.0017051 | 0.069365 | 0.026083 | 0.057857 | 0.12009 | 14.8956 | 0.041952 | 119.4611 | 119.3912 | 119.3962 | -0.058478 | -0.003531 | 0.27966 | -0.11587 | 119.1803 | 119.4557 | 118.8088 | -0.2603 | 0.12005 | 0.094606 | 0.29861 | 0.22048 | 0.10043 | 0.024782 | 0.029792 | -0.081776 | -0.18613 | 0.175 | 0.062654 | 0.14443 | 0.089255 | -0.5577 | 119.6396 | 119.5698 | 119.5748 | 15.0741 | -119.4249 | 119.3589 | 119.6342 | 118.9873 | 0.45819 | -119.6268
1370.625 | 119.6091 | -0.16937 | 119.4214 | 1.4211e-13 | -0.0065127 | 0.0023076 | 0.063545 | -0.0090251 | 0.057362 | 0.0016025 | -0.0024589 | -0.0017051 | 0.069365 | 0.025869 | 0.057857 | 0.074302 | 14.0669 | 0.041952 | 119.516 | 119.4416 | 119.4558 | -0.090531 | -0.012689 | 0.27966 | -0.12045 | 119.2398 | 119.5061 | 118.8683 | -0.27862 | 0.078842 | 0.094615 | 0.24368 | 0.21132 | 0.13248 | 0.020219 | 0.034382 | -0.10925 | -0.18154 | 0.15668 | 0.04892 | 0.15817 | 0.084688 | -0.55311 | 119.6854 | 119.611 | 119.6251 | 14.2362 | -119.5119 | 119.4092 | 119.6754 | 119.0376 | 0.44903 | -119.7
1372.3281 | 119.6869 | -0.17853 | 119.4305 | 1.4211e-13 | -0.0062991 | 0.002094 | 0.063118 | -0.0094525 | 0.057576 | -0.006028 | -0.0026725 | -0.0019187 | 0.069579 | 0.025869 | 0.057857 | 0.074302 | 13.4259 | 0.037373 | 119.5572 | 119.4828 | 119.497 | -0.15464 | -0.026425 | 0.28424 | -0.13419 | 119.2673 | 119.5519 | 118.9278 | -0.26946 | 0.023892 | 0.12667 | 0.25283 | 0.2159 | 0.19201 | 0.052274 | 0.066434 | -0.090934 | -0.16323 | 0.1521 | 0.044339 | 0.13527 | 0.12132 | -0.50275 | 119.7357 | 119.6613 | 119.6755 | 13.6044 | -119.5852 | 119.4458 | 119.7304 | 119.1063 | 0.46277 | -119.7
1374.0156 | 119.7327 | -0.13733 | 119.4717 | 1.4211e-13 | -0.0060855 | 0.0023076 | 0.063118 | -0.0092389 | 0.057789 | 0.0016025 | -0.0026725 | -0.0017051 | 0.069579 | 0.025656 | 0.057857 | 0.074302 | 12.8856 | 0.032795 | 119.603 | 119.5423 | 119.5473 | -0.14548 | -0.026425 | 0.28882 | -0.13419 | 119.3268 | 119.5976 | 118.9232 | -0.27862 | -0.008149 | 0.13125 | 0.21163 | 0.17012 | 0.17827 | 0.070601 | 0.0756 | -0.14129 | -0.1449 | 0.1109 | 0.00314 | 0.14443 | 0.12591 | -0.54853 | 119.7403 | 119.6797 | 119.6847 | 13.0229 | -119.6172 | 119.4642 | 119.735 | 119.0605 | 0.42615 | -119.7504
1375.7656 | 119.7784 | -0.17853 | 119.5358 | 1.4211e-13 | -0.0060855 | 0.002094 | 0.063331 | -0.0094525 | 0.057148 | -0.006028 | -0.0022453 | -0.0019187 | 0.069365 | 0.025869 | 0.058284 | 0.065145 | 12.6017 | 0.032795 | 119.6534 | 119.579 | 119.584 | -0.17295 | -0.035582 | 0.28424 | -0.12961 | 119.3635 | 119.6343 | 119.0331 | -0.27862 | 0.005577 | 0.11753 | 0.24367 | 0.21132 | 0.20575 | 0.043145 | 0.048142 | -0.10009 | -0.17236 | 0.14295 | 0.048918 | 0.14901 | 0.098448 | -0.50273 | 119.8319 | 119.7575 | 119.7625 | 12.7802 | -119.7088 | 119.542 | 119.8128 | 119.2116 | 0.46277 | -119.8144
1377.5312 | 119.6869 | -0.21515 | 119.5953 | 1.4211e-13 | -0.0060855 | 0.002094 | 0.063118 | -0.0090251 | 0.057148 | 0.0016025 | -0.0026725 | -0.0017051 | 0.069579 | 0.025656 | 0.058071 | 0.069723 | 12.2675 | 0.032795 | 119.6991 | 119.6293 | 119.6343 | -0.15921 | -0.031003 | 0.2934 | -0.12961 | 119.4138 | 119.6801 | 119.056 | -0.27404 | 0.055934 | 0.1038 | 0.28487 | 0.24794 | 0.19201 | 0.034005 | 0.038997 | -0.058891 | -0.18151 | 0.18415 | 0.085539 | 0.14443 | 0.084725 | -0.53934 | 119.9143 | 119.8445 | 119.8495 | 12.4826 | -119.7546 | 119.629 | 119.8952 | 119.2711 | 0.50855 | -119.8694
1379.2188 | 119.8746 | -0.17853 | 119.632 | 1.4211e-13 | -0.0062991 | 0.002094 | 0.063331 | -0.0090251 | 0.057362 | -0.006028 | -0.0024589 | -0.0019187 | 0.069579 | 0.025656 | 0.058284 | 0.069723 | 12.3819 | 0.032795 | 119.7266 | 119.6614 | 119.6755 | -0.15464 | -0.031003 | 0.27508 | -0.13419 | 119.4505 | 119.735 | 119.1155 | -0.27862 | 0.023892 | 0.09465 | 0.24825 | 0.21132 | 0.18743 | 0.029436 | 0.043584 | -0.10009 | -0.1815 | 0.14752 | 0.044339 | 0.14443 | 0.10305 | -0.51644 | 119.9051 | 119.8399 | 119.8541 | 12.5605 | -119.7866 | 119.629 | 119.9135 | 119.294 | 0.45361 | -119.9106
1380.9688 | 119.8791 | -0.1831 | 119.6777 | 1.4211e-13 | -0.0062991 | 0.0025214 | 0.063331 | -0.0092389 | 0.057362 | -0.006028 | -0.0026725 | -0.0019187 | 0.069365 | 0.025869 | 0.058071 | 0.065145 | 12.0248 | 0.032795 | 119.7815 | 119.7118 | 119.7213 | -0.12716 | -0.035582 | 0.2705 | -0.12961 | 119.4917 | 119.7716 | 119.1659 | -0.2832 | 0.055943 | 0.10381 | 0.24825 | 0.2159 | 0.15996 | 0.034028 | 0.043594 | -0.10009 | -0.18607 | 0.14752 | 0.053495 | 0.15359 | 0.0939 | -0.51185 | 119.9647 | 119.8949 | 119.9044 | 12.2079 | -119.8049 | 119.6748 | 119.9547 | 119.349 | 0.45361 | -119.9609
1382.7344 | 119.8746 | -0.17395 | 119.7189 | 1.4211e-13 | -0.0060855 | 0.0023076 | 0.063118 | -0.0090251 | 0.057362 | -0.006028 | -0.0024589 | -0.0014913 | 0.069579 | 0.025869 | 0.058071 | 0.074302 | 12.1668 | 0.028217 | 119.8182 | 119.7484 | 119.758 | -0.1409 | -0.031003 | 0.27508 | -0.13419 | 119.5329 | 119.8037 | 119.1979 | -0.27862 | 0.033051 | 0.099243 | 0.24825 | 0.20217 | 0.16912 | 0.029461 | 0.039024 | -0.10467 | -0.18606 | 0.14295 | 0.039761 | 0.14443 | 0.084751 | -0.521 | 119.9921 | 119.9223 | 119.9319 | 12.3407 | -119.8598 | 119.7068 | 119.9776 | 119.3719 | 0.44903 | -119.9976
1384.4219 | 119.8608 | -0.2243 | 119.7601 | 1.4211e-13 | -0.0062991 | 0.0023076 | 0.063545 | -0.0094525 | 0.057576 | -0.006028 | -0.0026725 | -0.0014913 | 0.069365 | 0.025869 | 0.057857 | 0.074302 | 12.5468 | 0.032795 | 119.8456 | 119.785 | 119.7946 | -0.14548 | -0.026425 | 0.26592 | -0.12961 | 119.5741 | 119.8449 | 119.1934 | -0.2832 | 0.078826 | 0.085514 | 0.29861 | 0.2571 | 0.17827 | 0.024893 | 0.034454 | -0.058894 | -0.18606 | 0.19788 | 0.094694 | 0.15359 | 0.08476 | -0.56678 | 120.07 | 120.0093 | 120.0189 | 12.7711 | -119.9056 | 119.7984 | 120.0692 | 119.4177 | 0.49023 | -120.0433
1386.125 | 119.9936 | -0.18768 | 119.783 | 1.4211e-13 | -0.0058717 | 0.0023076 | 0.063118 | -0.0092389 | 0.057362 | -0.006028 | -0.0022453 | -0.0019187 | 0.069365 | 0.025869 | 0.058284 | 0.065145 | 12.6383 | 0.023639 | 119.896 | 119.8308 | 119.8312 | -0.13632 | -0.026425 | 0.27508 | -0.12961 | 119.6061 | 119.8815 | 119.2758 | -0.27404 | 0.051363 | 0.11299 | 0.25283 | 0.21132 | 0.15996 | 0.047794 | 0.048194 | -0.086357 | -0.17689 | 0.16126 | 0.058073 | 0.14443 | 0.0985 | -0.50725 | 120.0837 | 120.0185 | 120.0189 | 12.826 | -119.9193 | 119.7938 | 120.0692 | 119.4635 | 0.46276 | -120.0571
1387.875 | 119.9249 | -0.2243 | 119.8608 | 1.4211e-13 | -0.0065127 | 0.0023076 | 0.063545 | -0.0092389 | 0.057362 | 0.0016025 | -0.0024589 | -0.0021323 | 0.069579 | 0.025656 | 0.058284 | 0.074302 | 12.5742 | 0.032795 | 119.9235 | 119.8583 | 119.8724 | -0.17295 | -0.026425 | 0.2934 | -0.13419 | 119.6428 | 119.9227 | 119.3078 | -0.27404 | 0.051353 | 0.062639 | 0.29861 | 0.2571 | 0.20575 | -0.002552 | 0.011582 | -0.049736 | -0.21809 | 0.19788 | 0.090115 | 0.13985 | 0.061888 | -0.55302 | 120.1478 | 120.0826 | 120.0967 | 12.7986 | -120.0338 | 119.8671 | 120.147 | 119.5321 | 0.5177 | -120.1349
1389.625 | 120.0806 | -0.19226 | 119.8563 | 1.4211e-13 | -0.0065127 | 0.0025214 | 0.063331 | -0.0090251 | 0.057148 | 0.0016025 | -0.0030999 | -0.0019187 | 0.069792 | 0.025656 | 0.058498 | 0.083459 | 12.5285 | 0.032795 | 119.9647 | 119.8903 | 119.8999 | -0.15921 | -0.031003 | 0.31629 | -0.12045 | 119.684 | 119.9548 | 119.3124 | -0.27404 | 0.033046 | 0.10842 | 0.27572 | 0.22506 | 0.19201 | 0.034078 | 0.043631 | -0.081779 | -0.1723 | 0.16126 | 0.071808 | 0.15359 | 0.098516 | -0.54387 | 120.1569 | 120.0826 | 120.0922 | 12.7207 | -120.0155 | 119.8762 | 120.147 | 119.5047 | 0.50855 | -120.1303
1391.3125 | 120.0577 | -0.20142 | 119.9203 | 1.4211e-13 | -0.0062991 | 0.002094 | 0.063759 | -0.0090251 | 0.057576 | 0.0016025 | -0.0024589 | -0.0014913 | 0.069792 | 0.025442 | 0.058071 | 0.074302 | 12.5788 | 0.01906 | 119.9967 | 119.927 | 119.9365 | -0.16379 | -0.031003 | 0.32087 | -0.13419 | 119.7206 | 119.996 | 119.3719 | -0.27862 | 0.037622 | 0.076384 | 0.27572 | 0.22048 | 0.18285 | 0.006623 | 0.016173 | -0.077203 | -0.19976 | 0.17041 | 0.067227 | 0.14443 | 0.075636 | -0.54843 | 120.1981 | 120.1284 | 120.1379 | 12.7802 | -120.0841 | 119.922 | 120.1974 | 119.5733 | 0.52228 | -120.199
1393 | 120.0439 | -0.23804 | 119.9478 | 1.4211e-13 | -0.0062991 | 0.0018804 | 0.063759 | -0.0092389 | 0.057362 | 0.0016025 | -0.0024589 | -0.0019187 | 0.069579 | 0.025656 | 0.058071 | 0.074302 | 12.9176 | 0.023639 | 120.0379 | 119.959 | 119.964 | -0.12258 | -0.026425 | 0.29797 | -0.12961 | 119.7481 | 120.0235 | 119.4085 | -0.26946 | 0.11545 | 0.090123 | 0.31234 | 0.26168 | 0.14622 | 0.011209 | 0.016179 | -0.031425 | -0.19976 | 0.21161 | 0.10843 | 0.13985 | 0.075642 | -0.53927 | 120.276 | 120.1971 | 120.202 | 13.1557 | -120.0704 | 119.9861 | 120.2615 | 119.6466 | 0.53601 | -120.2173
1394.75 | 120.1355 | -0.19684 | 119.9615 | 1.4211e-13 | -0.0062991 | 0.002094 | 0.063759 | -0.0098799 | 0.057789 | -0.006028 | -0.0026725 | -0.0019187 | 0.069579 | 0.025869 | 0.057644 | 0.074302 | 12.7803 | 0.028217 | 120.0654 | 119.9911 | 120.0052 | -0.18669 | -0.031003 | 0.30255 | -0.12961 | 119.7847 | 120.0601 | 119.436 | -0.27404 | 0.01015 | 0.10386 | 0.27114 | 0.22506 | 0.2149 | 0.029529 | 0.043653 | -0.077202 | -0.17686 | 0.16584 | 0.067228 | 0.14443 | 0.098538 | -0.52553 | 120.2622 | 120.1879 | 120.202 | 12.9771 | -120.1482 | 119.9815 | 120.2569 | 119.6329 | 0.49939 | -120.2356
1396.5 | 120.2316 | -0.18768 | 119.9707 | 1.4211e-13 | -0.0060855 | 0.0025214 | 0.063973 | -0.0094525 | 0.057362 | -0.006028 | -0.0024589 | -0.0019187 | 0.069792 | 0.025656 | 0.058284 | 0.069723 | 12.8215 | 0.01906 | 120.0837 | 120.0231 | 120.0281 | -0.16379 | -0.031003 | 0.31171 | -0.11587 | 119.8167 | 120.0921 | 119.4818 | -0.27404 | 0.023889 | 0.11302 | 0.25741 | 0.20674 | 0.18285 | 0.052426 | 0.057391 | -0.086357 | -0.15397 | 0.15668 | 0.071809 | 0.15817 | 0.12143 | -0.4889 | 120.2714 | 120.2108 | 120.2158 | 13.0092 | -120.1345 | 120.0044 | 120.2798 | 119.6695 | 0.49939 | -120.2447
1398.2031 | 120.2179 | -0.19226 | 120.0302 | 1.4211e-13 | -0.0060855 | 0.0025214 | 0.063545 | -0.0090251 | 0.057576 | 0.0016025 | -0.0024589 | -0.0014913 | 0.069579 | 0.025869 | 0.058071 | 0.074302 | 13.1924 | 0.01906 | 120.1341 | 120.0598 | 120.0693 | -0.16379 | -0.017267 | 0.32087 | -0.12961 | 119.835 | 120.1105 | 119.5093 | -0.27404 | 0.028467 | 0.10387 | 0.26656 | 0.21132 | 0.18285 | 0.029548 | 0.03909 | -0.081779 | -0.19516 | 0.17499 | 0.062651 | 0.14443 | 0.080239 | -0.52094 | 120.3263 | 120.252 | 120.2616 | 13.3846 | -120.194 | 120.0273 | 120.3027 | 119.7015 | 0.51313 | -120.3043
1399.9531 | 120.1447 | -0.21515 | 120.0577 | 1.4211e-13 | -0.0060855 | 0.0023076 | 0.063973 | -0.0090251 | 0.057362 | 0.0016025 | -0.0026725 | -0.0014913 | 0.069365 | 0.025656 | 0.058284 | 0.07888 | 13.1374 | 0.028217 | 120.157 | 120.0918 | 120.0968 | -0.17753 | -0.026425 | 0.31171 | -0.12503 | 119.8763 | 120.1517 | 119.5367 | -0.27862 | 0.037619 | 0.099298 | 0.29403 | 0.24337 | 0.20575 | 0.034135 | 0.039095 | -0.06347 | -0.18142 | 0.18872 | 0.090117 | 0.15359 | 0.09398 | -0.52093 | 120.3721 | 120.307 | 120.3119 | 13.3526 | -120.2352 | 120.0914 | 120.3668 | 119.7519 | 0.52686 | -120.3363
1401.6562 | 120.1904 | -0.21515 | 120.1035 | 1.4211e-13 | -0.0060855 | 0.0023076 | 0.063759 | -0.0094525 | 0.057576 | -0.013659 | -0.0024589 | -0.0021323 | 0.069365 | 0.025656 | 0.058284 | 0.07888 | 13.2153 | 0.014482 | 120.1844 | 120.1147 | 120.1288 | -0.16837 | -0.026425 | 0.32545 | -0.12961 | 119.8991 | 120.1791 | 119.5688 | -0.2832 | 0.046776 | 0.080992 | 0.29403 | 0.22963 | 0.18285 | 0.011253 | 0.025369 | -0.068049 | -0.20431 | 0.18872 | 0.085539 | 0.15359 | 0.075675 | -0.53466 | 120.3996 | 120.3299 | 120.344 | 13.4304 | -120.2718 | 120.1143 | 120.3943 | 119.7839 | 0.5406 | -120.3867
1403.4062 | 120.3598 | -0.15564 | 120.1035 | 1.4211e-13 | -0.0062991 | 0.002094 | 0.063759 | -0.0092389 | 0.057789 | -0.006028 | -0.0024589 | -0.0017051 | 0.069579 | 0.025869 | 0.058498 | 0.074302 | 13.3801 | 0.014482 | 120.2211 | 120.1513 | 120.1655 | -0.15464 | -0.031003 | 0.33003 | -0.13419 | 119.9358 | 120.2112 | 119.5825 | -0.27404 | 0.001004 | 0.11762 | 0.22994 | 0.17012 | 0.16912 | 0.047884 | 0.061997 | -0.1184 | -0.16768 | 0.12464 | 0.021451 | 0.13985 | 0.10773 | -0.52092 | 120.3767 | 120.307 | 120.3211 | 13.5357 | -120.2581 | 120.0914 | 120.3668 | 119.7382 | 0.48567 | -120.3775
1405.1094 | 120.3873 | -0.16022 | 120.1263 | 1.4211e-13 | -0.0060855 | 0.002094 | 0.063759 | -0.0092389 | 0.057789 | -0.006028 | -0.0024589 | -0.0019187 | 0.069792 | 0.025869 | 0.058712 | 0.083459 | 13.3663 | 0.014482 | 120.2485 | 120.1788 | 120.1838 | -0.15921 | -0.017267 | 0.33003 | -0.12503 | 119.9541 | 120.2341 | 119.6192 | -0.26946 | 0.001002 | 0.1222 | 0.24368 | 0.1747 | 0.1737 | 0.052469 | 0.057424 | -0.10924 | -0.17225 | 0.14295 | 0.035185 | 0.14443 | 0.10773 | -0.50718 | 120.4088 | 120.339 | 120.344 | 13.5266 | -120.2856 | 120.1143 | 120.3943 | 119.7794 | 0.49024 | -120.3958
1406.875 | 120.3049 | -0.2243 | 120.1996 | 1.4211e-13 | -0.0058717 | 0.0023076 | 0.063759 | -0.0092389 | 0.057789 | 0.0016025 | -0.0022453 | -0.0017051 | 0.069579 | 0.025869 | 0.058712 | 0.069723 | 13.5953 | 0.009904 | 120.2714 | 120.2063 | 120.2112 | -0.18669 | -0.035582 | 0.32545 | -0.12961 | 119.9953 | 120.2707 | 119.697 | -0.2832 | 0.037616 | 0.071851 | 0.29403 | 0.23421 | 0.19659 | 0.006701 | 0.011653 | -0.058894 | -0.20429 | 0.18872 | 0.094694 | 0.15359 | 0.071117 | -0.50259 | 120.4957 | 120.4306 | 120.4355 | 13.8196 | -120.3863 | 120.2196 | 120.495 | 119.9213 | 0.54975 | -120.4828
1408.625 | 120.314 | -0.23346 | 120.2225 | 1.4211e-13 | -0.0060855 | 0.0023076 | 0.063759 | -0.0092389 | 0.057789 | 0.0092325 | -0.0022453 | -0.0017051 | 0.069792 | 0.025869 | 0.058284 | 0.083459 | 14.0577 | 0.009904 | 120.3035 | 120.2338 | 120.2387 | -0.17753 | -0.021846 | 0.31629 | -0.13419 | 120.0228 | 120.2936 | 119.6787 | -0.27404 | 0.055929 | 0.081012 | 0.31692 | 0.24336 | 0.18743 | 0.011287 | 0.016237 | -0.040581 | -0.1997 | 0.21161 | 0.09927 | 0.13985 | 0.071122 | -0.54379 | 120.5369 | 120.4672 | 120.4722 | 14.2912 | -120.4 | 120.2562 | 120.5271 | 119.9121 | 0.54975 | -120.4965
1410.3125 | 120.3781 | -0.21057 | 120.2545 | 1.4211e-13 | -0.0058717 | 0.0023076 | 0.064186 | -0.0092389 | 0.057789 | -0.006028 | -0.0022453 | -0.0021323 | 0.069792 | 0.026083 | 0.058284 | 0.074302 | 13.7235 | 0.009904 | 120.3218 | 120.2567 | 120.2662 | -0.12258 | -0.031003 | 0.31629 | -0.12961 | 120.0457 | 120.3119 | 119.7062 | -0.27862 | 0.087988 | 0.067281 | 0.28487 | 0.22048 | 0.13249 | 0.002137 | 0.011665 | -0.068048 | -0.20886 | 0.17957 | 0.080961 | 0.14901 | 0.057392 | -0.54836 | 120.5324 | 120.4672 | 120.4768 | 13.934 | -120.3771 | 120.2562 | 120.5225 | 119.9167 | 0.52686 | -120.5331
1412 | 120.3644 | -0.21515 | 120.2957 | 1.4211e-13 | -0.0060855 | 0.002094 | 0.063759 | -0.0090251 | 0.057789 | 0.0092325 | -0.0024589 | -0.0021323 | 0.07022 | 0.025656 | 0.058284 | 0.083459 | 14.1218 | 0.009904 | 120.3584 | 120.2841 | 120.2937 | -0.14548 | -0.035582 | 0.32545 | -0.12961 | 120.0686 | 120.3348 | 119.7382 | -0.27404 | 0.069671 | 0.062711 | 0.29861 | 0.22505 | 0.15538 | -0.011587 | -0.002062 | -0.058891 | -0.22716 | 0.17957 | 0.085539 | 0.14443 | 0.039087 | -0.55751 | 120.5736 | 120.4993 | 120.5088 | 14.337 | -120.4412 | 120.2837 | 120.55 | 119.9534 | 0.5406 | -120.5698
1413.75 | 120.5109 | -0.16479 | 120.2545 | 1.4211e-13 | -0.0058717 | 0.0023076 | 0.063973 | -0.0092389 | 0.057789 | -0.006028 | -0.0024589 | -0.0019187 | 0.070006 | 0.026083 | 0.058071 | 0.083459 | 13.8334 | 0.005325 | 120.3813 | 120.3116 | 120.3303 | -0.17295 | -0.031003 | 0.32545 | -0.12961 | 120.1006 | 120.3623 | 119.7565 | -0.27862 | -0.008156 | 0.1268 | 0.24825 | 0.17012 | 0.17828 | 0.057084 | 0.075765 | -0.11382 | -0.15392 | 0.13379 | 0.035185 | 0.14901 | 0.10776 | -0.498 | 120.5461 | 120.4764 | 120.4951 | 13.9982 | -120.4275 | 120.2654 | 120.5271 | 119.9213 | 0.49024 | -120.5331
1415.5156 | 120.5429 | -0.19226 | 120.2728 | 1.4211e-13 | -0.0058717 | 0.002094 | 0.063973 | -0.0088115 | 0.058003 | 0.0016025 | -0.0022453 | -0.0019187 | 0.070006 | 0.025869 | 0.058284 | 0.083459 | 13.87 | 0.014482 | 120.4134 | 120.3437 | 120.3486 | -0.14548 | -0.035582 | 0.3346 | -0.13419 | 120.1281 | 120.3852 | 119.7886 | -0.27404 | 0.046783 | 0.14054 | 0.27572 | 0.20674 | 0.15996 | 0.070827 | 0.075769 | -0.081779 | -0.14475 | 0.15668 | 0.058072 | 0.13985 | 0.11234 | -0.48426 | 120.6056 | 120.5359 | 120.5409 | 14.0623 | -120.4183 | 120.3203 | 120.5774 | 119.9808 | 0.52687 | -120.5469
1417.2812 | 120.433 | -0.21057 | 120.3506 | 1.4211e-13 | -0.0060855 | 0.002094 | 0.064186 | -0.0092389 | 0.057576 | -0.006028 | -0.0024589 | -0.0019187 | 0.069579 | 0.025869 | 0.058284 | 0.074302 | 13.7876 | 0.005325 | 120.4363 | 120.3711 | 120.3761 | -0.10885 | -0.031003 | 0.33003 | -0.12961 | 120.1464 | 120.4218 | 119.8389 | -0.27404 | 0.10172 | 0.085611 | 0.28487 | 0.2159 | 0.11417 | 0.02048 | 0.025421 | -0.063469 | -0.20426 | 0.17957 | 0.080961 | 0.14443 | 0.071149 | -0.51171 | 120.6468 | 120.5817 | 120.5866 | 13.9981 | -120.4595 | 120.357 | 120.6324 | 120.0495 | 0.5406 | -120.6247
1418.9688 | 120.4605 | -0.21057 | 120.3644 | 1.4211e-13 | -0.0058717 | 0.0025214 | 0.063973 | -0.0092389 | 0.057576 | -0.006028 | -0.0028861 | -0.0019187 | 0.070006 | 0.026083 | 0.058284 | 0.07888 | 14.0348 | 0.000747 | 120.4591 | 120.3849 | 120.4035 | -0.118 | -0.026425 | 0.33003 | -0.13419 | 120.1693 | 120.4493 | 119.8389 | -0.27862 | 0.092567 | 0.09477 | 0.28945 | 0.21132 | 0.11875 | 0.020484 | 0.03916 | -0.068048 | -0.1951 | 0.18415 | 0.076382 | 0.14443 | 0.084887 | -0.52544 | 120.6697 | 120.5954 | 120.6141 | 14.2454 | -120.4824 | 120.3799 | 120.6598 | 120.0495 | 0.5406 | -120.643
1420.7031 | 120.5704 | -0.19684 | 120.3506 | 1.4211e-13 | -0.0060855 | 0.0023076 | 0.064186 | -0.0090251 | 0.057789 | -0.006028 | -0.0026725 | -0.0021323 | 0.070006 | 0.025869 | 0.058284 | 0.07888 | 13.6868 | 0.009904 | 120.482 | 120.4169 | 120.431 | -0.1409 | -0.021846 | 0.34834 | -0.12961 | 120.1922 | 120.4676 | 119.8572 | -0.27862 | 0.055939 | 0.1314 | 0.27572 | 0.20674 | 0.1508 | 0.06627 | 0.080364 | -0.081781 | -0.15847 | 0.17499 | 0.067228 | 0.14901 | 0.11693 | -0.4934 | 120.6789 | 120.6138 | 120.6278 | 13.8837 | -120.4915 | 120.389 | 120.6644 | 120.0541 | 0.54518 | -120.6293
1422.4531 | 120.5063 | -0.21515 | 120.4147 | 1.4211e-13 | -0.0058717 | 0.0023076 | 0.063973 | -0.0090251 | 0.057576 | 0.0016025 | -0.0022453 | -0.0021323 | 0.070006 | 0.025869 | 0.058284 | 0.069723 | 13.5907 | 0.000747 | 120.5004 | 120.4398 | 120.4539 | -0.1409 | -0.031003 | 0.33918 | -0.12503 | 120.2242 | 120.4905 | 119.8756 | -0.27404 | 0.07425 | 0.085622 | 0.28487 | 0.2159 | 0.14165 | 0.025077 | 0.03917 | -0.058891 | -0.19051 | 0.18415 | 0.090117 | 0.14901 | 0.075741 | -0.53917 | 120.7155 | 120.655 | 120.6691 | 13.8058 | -120.5556 | 120.4394 | 120.7056 | 120.0907 | 0.55433 | -120.6888
1424.1406 | 120.5017 | -0.21515 | 120.3278 | 1.4211e-13 | -0.0058717 | 0.0025214 | 0.063759 | -0.0092389 | 0.057576 | -0.006028 | -0.0024589 | -0.0021323 | 0.069792 | 0.025869 | 0.058284 | 0.060567 | 13.4854 | -0.003831 | 120.4363 | 120.362 | 120.3761 | -0.17295 | -0.035582 | 0.34376 | -0.12503 | 120.151 | 120.4218 | 119.8069 | -0.27862 | 0.042198 | 0.1085 | 0.27572 | 0.21132 | 0.16912 | 0.03421 | 0.048309 | -0.06347 | -0.17679 | 0.17957 | 0.090117 | 0.15359 | 0.094037 | -0.52087 | 120.6514 | 120.5771 | 120.5912 | 13.7005 | -120.5007 | 120.3661 | 120.6369 | 120.022 | 0.55891 | -120.6064
1425.8906 | 120.6573 | -0.16022 | 120.3964 | 1.4211e-13 | -0.0058717 | 0.002094 | 0.0644 | -0.0090251 | 0.057789 | -0.013659 | -0.0022453 | -0.0019187 | 0.069792 | 0.025869 | 0.058284 | 0.060567 | 13.6182 | -0.003831 | 120.5049 | 120.4398 | 120.4539 | -0.18669 | -0.040161 | 0.33918 | -0.12961 | 120.2196 | 120.4951 | 119.9397 | -0.27862 | -0.026471 | 0.10851 | 0.22078 | 0.15639 | 0.18286 | 0.043388 | 0.057481 | -0.1184 | -0.17678 | 0.12006 | 0.030607 | 0.14901 | 0.09863 | -0.45676 | 120.6652 | 120.6 | 120.6141 | 13.7784 | -120.5831 | 120.3799 | 120.6553 | 120.0999 | 0.4994 | -120.675
1427.5781 | 120.5383 | -0.21973 | 120.4285 | 1.4211e-13 | -0.0058717 | 0.002094 | 0.064186 | -0.0090251 | 0.057789 | -0.013659 | -0.0022453 | -0.0019187 | 0.070006 | 0.026083 | 0.058284 | 0.065145 | 13.7647 | -0.008409 | 120.537 | 120.4673 | 120.4768 | -0.12258 | -0.040161 | 0.33918 | -0.13877 | 120.2517 | 120.5225 | 119.9076 | -0.27862 | 0.097144 | 0.10852 | 0.28487 | 0.21132 | 0.11417 | 0.038818 | 0.04833 | -0.058892 | -0.17677 | 0.17957 | 0.080959 | 0.13985 | 0.094058 | -0.52085 | 120.7567 | 120.687 | 120.6965 | 13.9844 | -120.5511 | 120.4714 | 120.7423 | 120.1273 | 0.55891 | -120.7071
1429.2812 | 120.4376 | -0.23346 | 120.4193 | 1.4211e-13 | -0.0060855 | 0.002094 | 0.064614 | -0.0088115 | 0.057576 | 0.0092325 | -0.0022453 | -0.0019187 | 0.070006 | 0.026083 | 0.058498 | -0.21414 | 13.7052 | -0.28768 | 120.1158 | 120.0598 | 120.051 | -0.52095 | -0.30115 | 0.36208 | -0.40433 | 119.8396 | 120.0967 | 119.5322 | -0.54877 | -0.28749 | -0.30354 | 0.019322 | -0.054225 | 0.23327 | -0.35955 | -0.36832 | -0.31531 | -0.57968 | -0.067688 | -0.17087 | 0.14444 | -0.3226 | -0.88714 | 120.3492 | 120.2932 | 120.2844 | 13.9386 | -120.9403 | 120.0731 | 120.3302 | 119.7656 | 0.59554 | -120.9681
1431.0312 | 120.7077 | -0.17395 | 120.4605 | 1.4211e-13 | -0.0056581 | 0.0023076 | 0.064186 | -0.0092389 | 0.057789 | 0.0016025 | -0.0026725 | -0.0023459 | 0.07022 | 0.026083 | 0.058284 | 0.065145 | 13.6594 | 0.000747 | 120.5828 | 120.5131 | 120.5363 | -0.19127 | -0.026425 | 0.32545 | -0.12503 | 120.2975 | 120.5729 | 119.9534 | -0.26946 | -0.017317 | 0.12226 | 0.2391 | 0.1747 | 0.19201 | 0.052564 | 0.075809 | -0.095512 | -0.16303 | 0.14752 | 0.048918 | 0.14443 | 0.11238 | -0.50711 | 120.7567 | 120.687 | 120.7103 | 13.8333 | -120.6518 | 120.4714 | 120.7468 | 120.1274 | 0.4994 | -120.73
1432.7188 | 120.5063 | -0.16022 | 120.282 | 1.4211e-13 | -0.0056581 | 0.0023076 | 0.063973 | -0.0090251 | 0.057576 | -0.006028 | -0.0024589 | -0.0019187 | 0.070006 | 0.025869 | 0.058071 | -0.15004 | 13.7006 | -0.2419 | 120.0517 | 120.0002 | 119.9732 | -0.45685 | -0.2462 | 0.38497 | -0.34481 | 119.771 | 120.0189 | 119.4726 | -0.48924 | -0.29663 | -0.23031 | 0.010178 | -0.081685 | 0.21494 | -0.28175 | -0.30883 | -0.32903 | -0.51103 | -0.085986 | -0.18459 | 0.14443 | -0.2631 | -0.80933 | 120.2119 | 120.1605 | 120.1334 | 13.8608 | -120.7388 | 119.9312 | 120.1791 | 119.6329 | 0.54519 | -120.7712
1434.4688 | 120.6116 | -0.19226 | 120.5292 | 1.4211e-13 | -0.0060855 | 0.0023076 | 0.064186 | -0.0090251 | 0.057576 | -0.006028 | -0.0024589 | -0.0019187 | 0.07022 | 0.026083 | 0.058498 | 0.074302 | 13.6365 | 0.009904 | 120.5919 | 120.5177 | 120.5455 | -0.049321 | -0.003531 | 0.33918 | -0.11587 | 120.3112 | 120.5866 | 119.9809 | -0.25572 | 0.14294 | 0.062748 | 0.26656 | 0.20216 | 0.059225 | -0.011522 | 0.016301 | -0.063464 | -0.21796 | 0.18873 | 0.076387 | 0.13985 | 0.05745 | -0.5483 | 120.7842 | 120.7099 | 120.7377 | 13.8287 | -120.5785 | 120.5035 | 120.7789 | 120.1731 | 0.53144 | -120.7849
1436.2188 | 120.7352 | -0.15106 | 120.5292 | 1.4211e-13 | -0.0060855 | 0.0023076 | 0.0644 | -0.0094525 | 0.057362 | 0.0016025 | -0.0024589 | -0.0019187 | 0.070006 | 0.026083 | 0.058498 | 0.069723 | 13.7418 | 0.000747 | 120.6331 | 120.568 | 120.5775 | -0.085952 | -0.00811 | 0.33918 | -0.1113 | 120.3478 | 120.6233 | 120.0038 | -0.26488 | 0.06511 | 0.10395 | 0.22079 | 0.15181 | 0.086699 | 0.038846 | 0.048352 | -0.11382 | -0.18133 | 0.14295 | 0.039766 | 0.15359 | 0.094079 | -0.52541 | 120.7842 | 120.7191 | 120.7286 | 13.8929 | -120.6151 | 120.4989 | 120.7743 | 120.1548 | 0.49025 | -120.7941
1437.9062 | 120.6711 | -0.19226 | 120.5795 | 1.4211e-13 | -0.0060855 | 0.0023076 | 0.0644 | -0.0090251 | 0.057789 | -0.013659 | -0.0024589 | -0.0019187 | 0.070006 | 0.026297 | 0.058498 | 0.065145 | 13.7235 | -0.008409 | 120.6606 | 120.5909 | 120.6096 | -0.053899 | -0.012689 | 0.34834 | -0.10672 | 120.3753 | 120.6461 | 120.0312 | -0.2603 | 0.13836 | 0.08107 | 0.25741 | 0.18385 | 0.04549 | 0.011387 | 0.030048 | -0.068043 | -0.20422 | 0.17957 | 0.085544 | 0.15359 | 0.066618 | -0.54829 | 120.8529 | 120.7832 | 120.8018 | 13.9157 | -120.6334 | 120.5676 | 120.8384 | 120.2235 | 0.5406 | -120.8398
1439.6562 | 120.7855 | -0.14191 | 120.5521 | 1.4211e-13 | -0.0060855 | 0.0023076 | 0.0644 | -0.0092389 | 0.058003 | -0.006028 | -0.0026725 | -0.0019187 | 0.070006 | 0.025869 | 0.058498 | 0.055988 | 13.7418 | -0.012988 | 120.6835 | 120.6184 | 120.637 | -0.049321 | -0.017267 | 0.34834 | -0.11587 | 120.3982 | 120.6828 | 120.0724 | -0.25572 | 0.092586 | 0.13143 | 0.1979 | 0.12892 | 0.036333 | 0.066326 | 0.084985 | -0.11382 | -0.15386 | 0.12464 | 0.026033 | 0.13985 | 0.13071 | -0.47962 | 120.8254 | 120.7603 | 120.779 | 13.8837 | -120.6014 | 120.5401 | 120.8247 | 120.2144 | 0.49025 | -120.8078
1441.3438 | 120.7901 | -0.16022 | 120.5978 | 1.4211e-13 | -0.0060855 | 0.0018804 | 0.0644 | -0.0092389 | 0.057789 | -0.006028 | -0.0022453 | -0.0019187 | 0.069792 | 0.026083 | 0.058498 | 0.05141 | 13.4259 | -0.012988 | 120.7064 | 120.6459 | 120.6554 | -0.031005 | -0.003531 | 0.36208 | -0.1113 | 120.4211 | 120.6919 | 120.0862 | -0.25572 | 0.12921 | 0.10854 | 0.21163 | 0.14723 | 0.018017 | 0.048024 | 0.057524 | -0.095508 | -0.17674 | 0.15669 | 0.048921 | 0.14443 | 0.094094 | -0.51166 | 120.8666 | 120.8061 | 120.8156 | 13.5861 | -120.6288 | 120.5813 | 120.8522 | 120.2464 | 0.52229 | -120.8536
1443.1094 | 120.7993 | -0.17853 | 120.6116 | 1.4211e-13 | -0.0058717 | 0.002094 | 0.064614 | -0.0092389 | 0.058003 | -0.006028 | -0.0024589 | -0.0014913 | 0.070006 | 0.026297 | 0.058498 | 0.05141 | 12.8764 | -0.012988 | 120.7293 | 120.6596 | 120.6737 | -0.053899 | -0.012689 | 0.36208 | -0.1113 | 120.4531 | 120.7194 | 120.1091 | -0.25115 | 0.12463 | 0.1177 | 0.22994 | 0.16554 | 0.040911 | 0.048028 | 0.062105 | -0.072618 | -0.15843 | 0.16584 | 0.067232 | 0.13985 | 0.10783 | -0.5025 | 120.9078 | 120.8381 | 120.8522 | 13.055 | -120.6655 | 120.6317 | 120.8979 | 120.2876 | 0.54061 | -120.8627
1444.8594 | 120.7214 | -0.19226 | 120.6253 | 1.4211e-13 | -0.0058717 | 0.0023076 | 0.064827 | -0.0090251 | 0.057789 | 0.0016025 | -0.0022453 | -0.0019187 | 0.07022 | 0.025869 | 0.058712 | 0.05141 | 12.5651 | -0.003831 | 120.7522 | 120.6871 | 120.692 | -0.035584 | -0.012689 | 0.36208 | -0.1113 | 120.4577 | 120.7377 | 120.1228 | -0.2603 | 0.15668 | 0.12686 | 0.24367 | 0.18843 | 0.031753 | 0.061768 | 0.066687 | -0.068043 | -0.16758 | 0.17957 | 0.080965 | 0.14901 | 0.11241 | -0.5025 | 120.9444 | 120.8793 | 120.8843 | 12.7574 | -120.6609 | 120.65 | 120.93 | 120.3151 | 0.55434 | -120.8856
1446.5469 | 120.8862 | -0.16479 | 120.6345 | 1.4211e-13 | -0.0060855 | 0.0018804 | 0.064614 | -0.0092389 | 0.057789 | -0.006028 | -0.0022453 | -0.0019187 | 0.07022 | 0.026297 | 0.058284 | 0.055988 | 12.5971 | -0.017566 | 120.7613 | 120.7008 | 120.7195 | -0.012689 | -0.012689 | 0.36666 | -0.11587 | 120.4852 | 120.7515 | 120.1549 | -0.25115 | 0.15211 | 0.12686 | 0.22078 | 0.14723 | -0.004877 | 0.06635 | 0.085003 | -0.086351 | -0.14926 | 0.15211 | 0.048921 | 0.13527 | 0.117 | -0.4796 | 120.9261 | 120.8656 | 120.8843 | 12.7619 | -120.6471 | 120.65 | 120.9163 | 120.3197 | 0.53145 | -120.8856
1448.25 | 120.8817 | -0.15564 | 120.6757 | 1.4211e-13 | -0.0058717 | 0.0025214 | 0.0644 | -0.0092389 | 0.058003 | 0.0092325 | -0.0028861 | -0.0019187 | 0.070006 | 0.026083 | 0.058712 | 0.042253 | 13.2519 | -0.008409 | 120.7796 | 120.7191 | 120.7332 | -0.040163 | -0.012689 | 0.36666 | -0.11587 | 120.4989 | 120.7789 | 120.164 | -0.25572 | 0.11548 | 0.10398 | 0.19789 | 0.14723 | 0.031754 | 0.043467 | 0.05754 | -0.10008 | -0.17673 | 0.14295 | 0.039766 | 0.13985 | 0.10327 | -0.51164 | 120.9353 | 120.8748 | 120.8888 | 13.4075 | -120.7158 | 120.6546 | 120.9346 | 120.3197 | 0.5223 | -120.9314
1450 | 120.9274 | -0.14191 | 120.6802 | 1.4211e-13 | -0.0058717 | 0.0018804 | 0.065041 | -0.0090251 | 0.058003 | -0.006028 | -0.0026725 | -0.0014913 | 0.070006 | 0.025869 | 0.058712 | 0.042253 | 13.4945 | -0.003831 | 120.8025 | 120.742 | 120.7515 | -0.12716 | -0.012689 | 0.38039 | -0.1113 | 120.5264 | 120.7972 | 120.2464 | -0.2603 | 0.014745 | 0.12229 | 0.18416 | 0.13808 | 0.12333 | 0.061783 | 0.071277 | -0.1184 | -0.15384 | 0.12922 | 0.030611 | 0.14901 | 0.117 | -0.43381 | 120.9444 | 120.8839 | 120.8934 | 13.6365 | -120.8074 | 120.6683 | 120.9391 | 120.3883 | 0.5223 | -120.9405
1451.6875 | 120.8771 | -0.17853 | 120.6802 | 1.4211e-13 | -0.0060855 | 0.0023076 | 0.064827 | -0.0092389 | 0.057789 | 0.0016025 | -0.0026725 | -0.0021323 | 0.070006 | 0.026083 | 0.058498 | 0.042253 | 13.4991 | -0.008409 | 120.8254 | 120.7603 | 120.7698 | -0.026426 | -0.00811 | 0.38497 | -0.1113 | 120.5401 | 120.8201 | 120.1778 | -0.25572 | 0.1521 | 0.14518 | 0.22078 | 0.17012 | 0.018017 | 0.080099 | 0.089591 | -0.077197 | -0.1401 | 0.17042 | 0.067232 | 0.14443 | 0.1399 | -0.50249 | 121.0039 | 120.9389 | 120.9484 | 13.6777 | -120.7067 | 120.7187 | 120.9987 | 120.3563 | 0.5635 | -120.936
1453.4531 | 120.9549 | -0.13733 | 120.694 | 1.4211e-13 | -0.0060855 | 0.0025214 | 0.064614 | -0.0094525 | 0.058003 | -0.006028 | -0.0024589 | -0.0019187 | 0.07022 | 0.026083 | 0.058925 | 0.037675 | 13.0184 | -0.012988 | 120.8437 | 120.7832 | 120.7973 | -0.026426 | -0.021846 | 0.38497 | -0.10672 | 120.5539 | 120.8384 | 120.2052 | -0.2603 | 0.1109 | 0.14977 | 0.175 | 0.12434 | 0.013438 | 0.089261 | 0.10333 | -0.12297 | -0.1401 | 0.11548 | 0.030612 | 0.15359 | 0.14448 | -0.48875 | 120.9811 | 120.9206 | 120.9346 | 13.1557 | -120.7204 | 120.6912 | 120.9758 | 120.3426 | 0.5223 | -120.9543
1455.2188 | 120.9045 | -0.17853 | 120.726 | 1.4211e-13 | -0.0058717 | 0.0018804 | 0.064827 | -0.0094525 | 0.057789 | 0.0016025 | -0.0024589 | -0.0017051 | 0.070433 | 0.026297 | 0.058498 | 0.037675 | 13.023 | -0.008409 | 120.8666 | 120.7924 | 120.811 | -0.11342 | -0.00811 | 0.38497 | -0.11587 | 120.5768 | 120.8522 | 120.3884 | -0.25115 | 0.065103 | 0.14061 | 0.2162 | 0.17012 | 0.10502 | 0.066375 | 0.085022 | -0.072618 | -0.14925 | 0.17042 | 0.062654 | 0.13527 | 0.12617 | -0.33764 | 121.0452 | 120.9709 | 120.9896 | 13.2015 | -120.8394 | 120.7553 | 121.0307 | 120.5669 | 0.5635 | -120.9772
1456.9062 | 120.8267 | -0.19226 | 120.7764 | 1.4211e-13 | -0.0056581 | 0.002094 | 0.065041 | -0.0092389 | 0.057789 | 0.016863 | -0.0024589 | -0.0014913 | 0.070433 | 0.026083 | 0.058712 | 0.028518 | 13.2244 | -0.008409 | 120.8758 | 120.8107 | 120.8294 | -0.049321 | -0.021846 | 0.40329 | -0.10672 | 120.5905 | 120.8751 | 120.2281 | -0.25572 | 0.14294 | 0.099416 | 0.22078 | 0.18385 | 0.040912 | 0.034337 | 0.052983 | -0.063464 | -0.18587 | 0.17041 | 0.085544 | 0.14901 | 0.09871 | -0.54825 | 121.068 | 121.003 | 121.0216 | 13.4167 | -120.8257 | 120.7828 | 121.0673 | 120.4204 | 0.59555 | -121.0321
1458.6562 | 120.9045 | -0.20142 | 120.8313 | 1.4211e-13 | -0.0056581 | 0.0023076 | 0.065255 | -0.0094525 | 0.058003 | 0.0016025 | -0.0024589 | -0.0017051 | 0.070006 | 0.026297 | 0.058925 | 0.037675 | 13.3938 | -0.003831 | 120.9033 | 120.829 | 120.8431 | -0.049321 | -0.003531 | 0.40329 | -0.1113 | 120.6088 | 120.8842 | 120.2922 | -0.25115 | 0.1521 | 0.071955 | 0.23909 | 0.19759 | 0.04549 | -0.002279 | 0.011787 | -0.04973 | -0.22248 | 0.19789 | 0.09012 | 0.13985 | 0.052935 | -0.53908 | 121.1047 | 121.0304 | 121.0445 | 13.5952 | -120.8806 | 120.8102 | 121.0857 | 120.4936 | 0.6047 | -121.0824
1460.4062 | 121.0236 | -0.13275 | 120.7809 | 1.4211e-13 | -0.0056581 | 0.002094 | 0.065468 | -0.0092389 | 0.057789 | -0.006028 | -0.0026725 | -0.0014913 | 0.07022 | 0.026083 | 0.058712 | 0.033096 | 13.0687 | -0.008409 | 120.9124 | 120.8519 | 120.866 | -0.072215 | -0.012689 | 0.40329 | -0.11587 | 120.6271 | 120.9025 | 120.2876 | -0.25115 | 0.060536 | 0.13146 | 0.16585 | 0.12434 | 0.063806 | 0.070969 | 0.085034 | -0.11839 | -0.15382 | 0.12006 | 0.016877 | 0.13527 | 0.1216 | -0.49331 | 121.0452 | 120.9847 | 120.9987 | 13.2015 | -120.8532 | 120.7599 | 121.0353 | 120.4204 | 0.53604 | -121.0321
1462.1562 | 116.954 | -22.7234 | 94.1071 | 1.4211e-13 | -0.0065127 | 0.0018804 | 0.061195 | -0.0085979 | 0.055226 | -0.006028 | -0.0028861 | -0.0019187 | 0.067229 | 0.025869 | 0.056789 | -32.1118 | 4.5205 | -32.1983 | 84.0381 | 84.0465 | 84.0586 | -32.2346 | -32.201 | 0.027831 | -32.295 | 83.8389 | 84.0448 | 84.0205 | -32.2891 | -9.5112 | -10.069 | -9.3884 | -9.4749 | 0.036281 | -10.0605 | -10.0485 | -9.5657 | -10.2681 | -9.4776 | -9.5717 | -0.005917 | -10.0623 | -10.0865 | 106.7615 | 106.7699 | 106.782 | 27.2439 | -126.3416 | 106.5623 | 106.7682 | 106.7439 | 22.7512 | -126.3962
1463.9062 | 120.6848 | -0.1831 | 120.575 | 1.4211e-13 | -0.0058717 | 0.002094 | 0.064827 | -0.0092389 | 0.058003 | -0.006028 | -0.0022453 | -0.0021323 | 0.070006 | 0.025869 | 0.058712 | 0.042253 | 13.2153 | -0.008409 | 120.6606 | 120.6001 | 120.6142 | -0.12716 | -0.012689 | 0.40329 | -0.12045 | 120.3753 | 120.6507 | 120.0175 | -0.26946 | 0.055943 | 0.085648 | 0.22536 | 0.1747 | 0.11875 | 0.025123 | 0.039204 | -0.086357 | -0.19964 | 0.17042 | 0.062652 | 0.14901 | 0.075775 | -0.55745 | 120.8437 | 120.7832 | 120.7973 | 13.3984 | -120.7021 | 120.5584 | 120.8338 | 120.2006 | 0.58639 | -120.8444
1465.5938 | 120.8221 | -0.16937 | 120.6528 | 1.4211e-13 | -0.0058717 | 0.0023076 | 0.065041 | -0.0090251 | 0.058003 | 0.0092325 | -0.0024589 | -0.0019187 | 0.070006 | 0.025869 | 0.058712 | 0.033096 | 12.8902 | -0.008409 | 120.7339 | 120.6688 | 120.6874 | -0.23706 | -0.012689 | 0.39413 | -0.1113 | 120.4486 | 120.724 | 120.0908 | -0.26946 | -0.067683 | 0.081082 | 0.20247 | 0.16096 | 0.22865 | 0.015986 | 0.034642 | -0.10009 | -0.2042 | 0.15668 | 0.058077 | 0.15817 | 0.071212 | -0.56201 | 120.9032 | 120.8381 | 120.8568 | 13.0595 | -120.8898 | 120.6179 | 120.8934 | 120.2601 | 0.5635 | -120.9222
1467.3594 | 120.575 | -0.1831 | 120.4971 | 1.4211e-13 | -0.0058717 | 0.0023076 | 0.065041 | -0.0092389 | 0.057576 | -0.013659 | -0.0024589 | -0.0019187 | 0.069792 | 0.025869 | 0.058071 | -0.17751 | 11.48 | -0.23732 | 120.2669 | 120.22 | 120.2067 | -0.28285 | -0.22789 | 0.45365 | -0.33565 | 119.9953 | 120.257 | 119.6695 | -0.4343 | -0.099741 | -0.23027 | 0.005595 | -0.054218 | 0.045523 | -0.27711 | -0.29047 | -0.25119 | -0.50183 | -0.044783 | -0.15255 | 0.098647 | -0.24016 | -0.8276 | 120.45 | 120.4031 | 120.3898 | 11.6631 | -120.78 | 120.1784 | 120.4401 | 119.8526 | 0.63676 | -120.9314
1469.1094 | 120.7031 | -0.19684 | 120.639 | 1.4211e-13 | -0.0060855 | 0.002094 | 0.065468 | -0.0094525 | 0.058003 | 0.0016025 | -0.0024589 | -0.0017051 | 0.070006 | 0.026297 | 0.058498 | 0.037675 | 11.7318 | 0.000747 | 120.7201 | 120.6596 | 120.6783 | -0.072215 | -0.012689 | 0.43534 | -0.12045 | 120.4394 | 120.7102 | 120.1182 | -0.2191 | 0.12462 | 0.08108 | 0.23451 | 0.19759 | 0.072962 | 0.020562 | 0.039218 | -0.022257 | -0.19963 | 0.18415 | 0.076385 | 0.098642 | 0.071209 | -0.52081 | 120.917 | 120.8564 | 120.8751 | 11.9286 | -120.7113 | 120.6362 | 120.9071 | 120.3151 | 0.63217 | -120.8581
1470.8594 | 120.7718 | -0.21515 | 120.6757 | 1.4211e-13 | -0.0056581 | 0.002094 | 0.065255 | -0.0090251 | 0.057789 | -0.013659 | -0.0022453 | -0.0021323 | 0.070006 | 0.025869 | 0.058712 | 0.05141 | 11.805 | -0.003831 | 120.7705 | 120.7054 | 120.7195 | -0.072215 | -0.017267 | 0.44907 | -0.11587 | 120.4852 | 120.7743 | 120.164 | -0.2191 | 0.14293 | 0.094821 | 0.26656 | 0.21132 | 0.068384 | 0.02973 | 0.043804 | -0.003946 | -0.19046 | 0.19788 | 0.099275 | 0.10322 | 0.098689 | -0.51164 | 120.9856 | 120.9205 | 120.9346 | 12.0202 | -120.7479 | 120.7003 | 120.9895 | 120.3792 | 0.66422 | -120.8948
1472.5625 | 120.8359 | -0.21515 | 120.726 | 1.4211e-13 | -0.0058717 | 0.0023076 | 0.065255 | -0.0094525 | 0.057789 | -0.006028 | -0.0024589 | -0.0021323 | 0.070433 | 0.026297 | 0.058925 | 0.028518 | 12.1027 | -0.008409 | 120.8071 | 120.742 | 120.7561 | -0.085952 | -0.00811 | 0.41244 | -0.11587 | 120.5264 | 120.7972 | 120.1915 | -0.22367 | 0.1292 | 0.081095 | 0.24367 | 0.20674 | 0.077543 | 0.016007 | 0.030079 | -0.008524 | -0.19961 | 0.20704 | 0.099275 | 0.1078 | 0.071228 | -0.53452 | 121.0223 | 120.9572 | 120.9712 | 12.3178 | -120.812 | 120.7416 | 121.0124 | 120.4066 | 0.62759 | -120.9497
1474.3281 | 120.8908 | -0.15564 | 120.5978 | 1.4211e-13 | -0.0058717 | 0.0023076 | 0.065682 | -0.0092389 | 0.058003 | 0.0016025 | -0.0024589 | -0.0021323 | 0.070006 | 0.026083 | 0.058498 | 0.042253 | 11.9516 | -0.003831 | 120.7339 | 120.6733 | 120.6828 | -0.23248 | -0.012689 | 0.45365 | -0.12503 | 120.4531 | 120.7331 | 120.0999 | -0.2603 | -0.076837 | 0.13601 | 0.19789 | 0.15181 | 0.22865 | 0.075497 | 0.084995 | -0.10466 | -0.14469 | 0.14295 | 0.030608 | 0.13527 | 0.1353 | -0.49792 | 120.8895 | 120.829 | 120.8385 | 12.1072 | -120.8303 | 120.6088 | 120.8888 | 120.2556 | 0.60929 | -120.8581
1476.0781 | 120.8084 | -0.21057 | 120.7535 | 1.4211e-13 | -0.0058717 | 0.0023076 | 0.065255 | -0.0092389 | 0.058003 | -0.013659 | -0.0026725 | -0.0021323 | 0.070433 | 0.026297 | 0.058498 | 0.055988 | 11.7913 | 0.005325 | 120.8392 | 120.7649 | 120.7836 | -0.072215 | -0.00811 | 0.44907 | -0.11587 | 120.5493 | 120.8293 | 120.2968 | -0.2603 | 0.13836 | 0.085677 | 0.26656 | 0.2159 | 0.07754 | 0.011436 | 0.030085 | -0.049733 | -0.20418 | 0.20246 | 0.094697 | 0.14443 | 0.075812 | -0.45668 | 121.0497 | 120.9755 | 120.9941 | 12.0019 | -120.8257 | 120.7599 | 121.0399 | 120.5074 | 0.65964 | -121.0138
1477.8281 | 120.9732 | -0.16479 | 120.7169 | 1.4211e-13 | -0.0058717 | 0.002094 | 0.065682 | -0.0092389 | 0.058003 | -0.006028 | -0.0024589 | -0.0019187 | 0.07022 | 0.026083 | 0.058284 | 0.028518 | 11.7867 | 0.000747 | 120.8666 | 120.8015 | 120.8202 | -0.067636 | -0.003531 | 0.42618 | -0.12045 | 120.5768 | 120.8522 | 120.2419 | -0.2603 | 0.097159 | 0.14977 | 0.19331 | 0.16554 | 0.068383 | 0.084688 | 0.10334 | -0.095509 | -0.14009 | 0.16126 | 0.044342 | 0.13985 | 0.13533 | -0.475 | 121.0314 | 120.9663 | 120.985 | 11.9515 | -120.7845 | 120.7416 | 121.017 | 120.4066 | 0.59097 | -120.9772
1479.5156 | 120.9595 | -0.17395 | 120.7809 | 1.4211e-13 | -0.0062991 | 0.0025214 | 0.066109 | -0.0090251 | 0.057789 | 0.0092325 | -0.0026725 | -0.0019187 | 0.070006 | 0.026297 | 0.058712 | 0.037675 | 11.48 | -0.008409 | 120.8895 | 120.8244 | 120.8339 | -0.072215 | -0.00811 | 0.41244 | -0.1113 | 120.6042 | 120.8751 | 120.3197 | -0.25572 | 0.10173 | 0.10857 | 0.21163 | 0.16554 | 0.063806 | 0.043496 | 0.052983 | -0.081775 | -0.17671 | 0.16584 | 0.062654 | 0.14443 | 0.094132 | -0.46126 | 121.0635 | 120.9984 | 121.0079 | 11.6539 | -120.8532 | 120.7782 | 121.049 | 120.4936 | 0.58639 | -121.0367
1481.2656 | 120.9091 | -0.20599 | 120.8084 | 1.4211e-13 | -0.0058717 | 0.0025214 | 0.065896 | -0.0092389 | 0.057789 | -0.006028 | -0.0024589 | -0.0021323 | 0.070006 | 0.02651 | 0.058498 | 0.028518 | 11.3426 | -0.003831 | 120.9078 | 120.8473 | 120.8706 | -0.058478 | -0.012689 | 0.41702 | -0.11587 | 120.6226 | 120.898 | 120.2602 | -0.26488 | 0.14752 | 0.099421 | 0.23451 | 0.20216 | 0.054647 | 0.038924 | 0.062146 | -0.058889 | -0.18586 | 0.19331 | 0.09012 | 0.14901 | 0.089559 | -0.54824 | 121.1138 | 121.0533 | 121.0766 | 11.5486 | -120.8669 | 120.8285 | 121.104 | 120.4662 | 0.62302 | -121.0733
1483.0312 | 120.8633 | -0.19226 | 120.7397 | 1.4211e-13 | -0.0060855 | 0.002735 | 0.065468 | -0.0092389 | 0.057789 | 0.0016025 | -0.0024589 | -0.0019187 | 0.069792 | 0.026083 | 0.058498 | 0.055988 | 11.6356 | 0.01906 | 120.9124 | 120.8473 | 120.7973 | -0.017268 | -0.00811 | 0.4216 | -0.10672 | 120.5585 | 120.8339 | 120.4342 | -0.20536 | 0.17499 | 0.17266 | 0.24825 | 0.21132 | 0.036328 | 0.10759 | 0.057554 | -0.013097 | -0.18129 | 0.18415 | 0.085544 | 0.098641 | 0.094124 | -0.30559 | 121.1047 | 121.0396 | 120.9896 | 11.8279 | -120.757 | 120.7507 | 121.0261 | 120.6264 | 0.61386 | -120.9451
1484.7188 | 121.0144 | -0.15106 | 120.7535 | 1.4211e-13 | -0.0056581 | 0.0029488 | 0.066109 | -0.0094525 | 0.057789 | -0.013659 | -0.0024589 | -0.0019187 | 0.070006 | 0.026083 | 0.058712 | 0.055988 | 11.2922 | 0.014482 | 120.917 | 120.8565 | 120.866 | -0.035584 | -0.003531 | 0.42618 | -0.10672 | 120.6271 | 120.898 | 120.3426 | -0.2191 | 0.11548 | 0.16351 | 0.20705 | 0.16554 | 0.050066 | 0.10301 | 0.1125 | -0.068033 | -0.12635 | 0.14753 | 0.044345 | 0.11238 | 0.14449 | -0.4109 | 121.0681 | 121.0076 | 121.017 | 11.4433 | -120.7891 | 120.7782 | 121.049 | 120.4936 | 0.57724 | -120.9726
1486.4688 | 121.0419 | -0.14191 | 120.7809 | 1.4211e-13 | -0.0060855 | 0.002094 | 0.066323 | -0.0090251 | 0.057789 | 0.0016025 | -0.0026725 | -0.0019187 | 0.069792 | 0.026297 | 0.058498 | 0.037675 | 11.0954 | 0.014482 | 120.9399 | 120.8748 | 120.8935 | -0.021847 | 0.001048 | 0.42618 | -0.1113 | 120.65 | 120.9346 | 120.3288 | -0.21452 | 0.12006 | 0.15894 | 0.17958 | 0.15639 | 0.036329 | 0.093864 | 0.1125 | -0.072609 | -0.13092 | 0.14295 | 0.030611 | 0.10322 | 0.15365 | -0.4521 | 121.0818 | 121.0167 | 121.0354 | 11.2373 | -120.8028 | 120.7919 | 121.0765 | 120.4708 | 0.56809 | -120.9955
1488.2188 | 120.932 | -0.18768 | 120.8588 | 1.4211e-13 | -0.0060855 | 0.0025214 | 0.066109 | -0.0092389 | 0.057789 | 0.0016025 | -0.0026725 | -0.0019187 | 0.07022 | 0.025869 | 0.058498 | 0.042253 | 11.338 | 0.014482 | 120.9628 | 120.9023 | 120.9163 | -0.017268 | -0.003531 | 0.42618 | -0.10672 | 120.6867 | 120.9529 | 120.3288 | -0.21452 | 0.17041 | 0.10401 | 0.22994 | 0.20216 | 0.03175 | 0.043518 | 0.057578 | -0.026833 | -0.17212 | 0.18415 | 0.080966 | 0.1078 | 0.094148 | -0.52992 | 121.1505 | 121.09 | 121.104 | 11.5257 | -120.876 | 120.8743 | 121.1406 | 120.5165 | 0.61386 | -121.0733
1489.9688 | 120.9961 | -0.1831 | 120.845 | 1.4211e-13 | -0.0058717 | 0.0023076 | 0.065896 | -0.0092389 | 0.057789 | 0.0092325 | -0.0026725 | -0.0019187 | 0.07022 | 0.026297 | 0.058498 | 0.033096 | 11.1869 | 0.005325 | 120.9811 | 120.9206 | 120.9347 | -0.017268 | -0.003531 | 0.41244 | -0.10672 | 120.7004 | 120.9666 | 120.3701 | -0.20994 | 0.16584 | 0.13605 | 0.2162 | 0.18843 | 0.022593 | 0.075566 | 0.089626 | -0.026832 | -0.14465 | 0.17957 | 0.076388 | 0.10322 | 0.12162 | -0.47498 | 121.1642 | 121.1037 | 121.1178 | 11.37 | -120.8623 | 120.8835 | 121.1498 | 120.5532 | 0.59555 | -121.055
1491.6562 | 120.9686 | -0.20599 | 120.8908 | 1.4211e-13 | -0.0056581 | 0.002735 | 0.066323 | -0.0092389 | 0.057789 | 0.0016025 | -0.0022453 | -0.0019187 | 0.069792 | 0.026083 | 0.058284 | 0.037675 | 10.8664 | 0.009904 | 120.9948 | 120.9298 | 120.9576 | -0.063057 | 0.001048 | 0.41702 | -0.10672 | 120.7141 | 120.9895 | 120.3701 | -0.21452 | 0.14294 | 0.10401 | 0.24367 | 0.2159 | 0.072961 | 0.038948 | 0.066743 | -0.008522 | -0.17669 | 0.20704 | 0.099277 | 0.1078 | 0.098734 | -0.52075 | 121.2008 | 121.1358 | 121.1635 | 11.0724 | -120.9539 | 120.9201 | 121.1955 | 120.576 | 0.62302 | -121.1053
1493.4062 | 121.0968 | -0.14648 | 120.8771 | 1.4211e-13 | -0.0058717 | 0.0029488 | 0.066323 | -0.0092389 | 0.057576 | 0.0016025 | -0.0028861 | -0.0023459 | 0.070006 | 0.026297 | 0.058712 | 0.05141 | 10.8115 | 0.01906 | 121.0177 | 120.9481 | 120.9667 | -0.049321 | 0.001048 | 0.4216 | -0.10672 | 120.7324 | 121.0079 | 120.4204 | -0.20994 | 0.097163 | 0.14064 | 0.19789 | 0.16554 | 0.068381 | 0.070997 | 0.089633 | -0.063453 | -0.14464 | 0.14753 | 0.039767 | 0.10322 | 0.13078 | -0.45666 | 121.1642 | 121.0946 | 121.1132 | 10.958 | -120.9264 | 120.8789 | 121.1543 | 120.5669 | 0.56808 | -121.087
1495.1719 | 121.0648 | -0.16937 | 120.9457 | 1.4211e-13 | -0.0058717 | 0.002735 | 0.066537 | -0.0092389 | 0.058003 | -0.006028 | -0.0026725 | -0.0019187 | 0.07022 | 0.026297 | 0.058925 | 0.046831 | 10.7016 | 0.01906 | 121.036 | 120.9618 | 120.9896 | -0.021847 | 0.001048 | 0.4216 | -0.10672 | 120.7553 | 121.0307 | 120.4021 | -0.21452 | 0.14753 | 0.090287 | 0.2162 | 0.18843 | 0.040907 | 0.016069 | 0.043861 | -0.045143 | -0.19041 | 0.17042 | 0.062656 | 0.1078 | 0.08501 | -0.54364 | 121.2054 | 121.1312 | 121.159 | 10.871 | -120.9676 | 120.9247 | 121.2001 | 120.5715 | 0.59097 | -121.1603
1496.9375 | 121.0602 | -0.17395 | 120.9549 | 1.4211e-13 | -0.0058717 | 0.002735 | 0.066537 | -0.0094525 | 0.058003 | -0.006028 | -0.0026725 | -0.0017051 | 0.07022 | 0.026083 | 0.058284 | 0.046831 | 10.5505 | 0.023639 | 121.0406 | 120.9893 | 120.9988 | -0.021847 | -0.003531 | 0.43534 | -0.1113 | 120.7599 | 121.0445 | 120.4387 | -0.20994 | 0.1521 | 0.08571 | 0.22078 | 0.19759 | 0.045486 | 0.034387 | 0.043863 | -0.035987 | -0.19499 | 0.17042 | 0.062654 | 0.098641 | 0.08959 | -0.51616 | 121.2146 | 121.1632 | 121.1727 | 10.7245 | -120.9767 | 120.9339 | 121.2184 | 120.6127 | 0.60929 | -121.1648
1498.625 | 121.0556 | -0.21057 | 120.9824 | 1.4211e-13 | -0.0058717 | 0.0029488 | 0.066537 | -0.0094525 | 0.057789 | -0.006028 | -0.0024589 | -0.0021323 | 0.070433 | 0.026724 | 0.058498 | 0.05141 | 10.4956 | 0.028217 | 121.0635 | 121.003 | 121.0125 | -0.012689 | -0.003531 | 0.43534 | -0.10214 | 120.7874 | 121.0582 | 120.4525 | -0.20994 | 0.19788 | 0.081136 | 0.26198 | 0.23879 | 0.040906 | 0.020658 | 0.030133 | 0.000634 | -0.19498 | 0.20704 | 0.10843 | 0.1078 | 0.07586 | -0.52989 | 121.2741 | 121.2136 | 121.2231 | 10.7061 | -120.995 | 120.9979 | 121.2688 | 120.663 | 0.64591 | -121.1923
1500.375 | 121.1655 | -0.14648 | 120.9229 | 1.4211e-13 | -0.0056581 | 0.002735 | 0.06675 | -0.0092389 | 0.058003 | -0.013659 | -0.0028861 | -0.0019187 | 0.07022 | 0.026297 | 0.058498 | 0.046831 | 10.4131 | 0.023639 | 121.0818 | 121.0213 | 121.0354 | -0.035584 | -0.00811 | 0.5498 | -0.10672 | 120.792 | 121.0765 | 120.4479 | -0.21452 | 0.1109 | 0.15896 | 0.19332 | 0.17012 | 0.059223 | 0.098483 | 0.11253 | -0.068032 | -0.1309 | 0.13837 | 0.039767 | 0.1078 | 0.15368 | -0.47496 | 121.2283 | 121.1678 | 121.1819 | 10.5596 | -120.9584 | 120.9384 | 121.223 | 120.5944 | 0.69629 | -121.1374
1502.1406 | 121.0876 | -0.18768 | 120.9595 | 1.4211e-13 | -0.0056581 | 0.0025214 | 0.06675 | -0.0094525 | 0.057789 | -0.006028 | -0.0024589 | -0.0019187 | 0.070433 | 0.026297 | 0.058498 | 0.055988 | 10.3216 | 0.032795 | 121.0452 | 120.9801 | 120.9942 | -0.017268 | -0.003531 | 0.7009 | -0.10214 | 120.7599 | 121.0307 | 120.425 | -0.20994 | 0.17041 | 0.085711 | 0.24367 | 0.22048 | 0.050063 | 0.020651 | 0.034706 | -0.022254 | -0.19957 | 0.18415 | 0.085545 | 0.1078 | 0.071277 | -0.53448 | 121.2329 | 121.1678 | 121.1819 | 10.5093 | -120.9767 | 120.9476 | 121.2184 | 120.6127 | 0.88858 | -121.1694
1503.9062 | 121.0464 | -0.18768 | 120.9137 | 1.4211e-13 | -0.0054445 | 0.002735 | 0.06675 | -0.0090251 | 0.058003 | -0.006028 | -0.0024589 | -0.0021323 | 0.07022 | 0.026297 | 0.058284 | 0.05141 | 10.2208 | 0.028217 | 121.0498 | 120.9847 | 121.0079 | -0.026426 | -0.003531 | 0.72837 | -0.10672 | 120.7599 | 121.0399 | 120.4433 | -0.20536 | 0.16126 | 0.13607 | 0.23909 | 0.2159 | 0.054643 | 0.071007 | 0.094219 | -0.017675 | -0.15379 | 0.18415 | 0.080966 | 0.098641 | 0.12621 | -0.47039 | 121.2374 | 121.1724 | 121.1956 | 10.4085 | -120.9401 | 120.9476 | 121.2276 | 120.631 | 0.91606 | -121.1191
1505.6094 | 120.9961 | -0.14191 | 120.813 | 1.4211e-13 | -0.0056581 | 0.0025214 | 0.066964 | -0.0090251 | 0.058003 | 0.0016025 | -0.0026725 | -0.0019187 | 0.070647 | 0.026297 | 0.058284 | 0.074302 | 9.9141 | 0.055687 | 120.9216 | 120.8565 | 120.8797 | -0.017268 | 0.005626 | 0.80621 | -0.092981 | 120.6409 | 120.9163 | 120.3151 | -0.15499 | 0.12464 | 0.10858 | 0.21621 | 0.19759 | 0.072955 | 0.043505 | 0.066726 | -0.013084 | -0.17212 | 0.14753 | 0.048926 | 0.06201 | 0.1033 | -0.49788 | 121.0635 | 120.9984 | 121.0216 | 10.056 | -120.8303 | 120.7828 | 121.0582 | 120.457 | 0.94812 | -120.968
1507.375 | 121.0098 | -0.19684 | 120.8771 | 1.4211e-13 | -0.0062991 | 0.002735 | 0.066964 | -0.0094525 | 0.057576 | -0.006028 | -0.0030999 | -0.0017051 | 0.070433 | 0.026083 | 0.058284 | 0.07888 | 9.7996 | 0.060265 | 120.9857 | 120.916 | 120.9438 | -0.017268 | 0.005626 | 0.75127 | -0.10672 | 120.705 | 120.9666 | 120.3655 | -0.24199 | 0.17957 | 0.10859 | 0.27572 | 0.2571 | 0.077533 | 0.038944 | 0.06674 | -0.045151 | -0.17211 | 0.20246 | 0.090121 | 0.13527 | 0.089574 | -0.5116 | 121.1825 | 121.1129 | 121.1407 | 9.9965 | -120.8943 | 120.9018 | 121.1635 | 120.5623 | 0.9481 | -121.1191
1509.0781 | 121.1014 | -0.12817 | 120.8633 | 1.4211e-13 | -0.0058717 | 0.0029488 | 0.066964 | -0.0092389 | 0.058003 | -0.006028 | -0.0028861 | -0.0017051 | 0.07022 | 0.026297 | 0.058284 | 0.074302 | 9.5615 | 0.064843 | 121.0223 | 120.9481 | 120.9667 | -0.031005 | 0.001048 | 0.75127 | -0.097559 | 120.7324 | 120.9987 | 120.4021 | -0.24657 | 0.097169 | 0.15895 | 0.20248 | 0.19302 | 0.095848 | 0.08473 | 0.10337 | -0.11839 | -0.13091 | 0.12922 | 0.030615 | 0.14901 | 0.13536 | -0.46124 | 121.1505 | 121.0762 | 121.0949 | 9.6897 | -120.8943 | 120.8606 | 121.1269 | 120.5303 | 0.87944 | -121.1099
1510.8438 | 121.106 | -0.14191 | 120.9229 | 1.4211e-13 | -0.0054445 | 0.002735 | 0.067391 | -0.0094525 | 0.057789 | 0.0016025 | -0.0024589 | -0.0019187 | 0.070433 | 0.026297 | 0.058498 | 0.065145 | 9.2685 | 0.064843 | 121.0314 | 120.9618 | 120.9804 | -0.031005 | 0.001048 | 1.0855 | -0.10214 | 120.7462 | 121.0079 | 120.4067 | -0.24199 | 0.1109 | 0.1086 | 0.20705 | 0.20675 | 0.095848 | 0.038957 | 0.057592 | -0.10008 | -0.17668 | 0.14295 | 0.039769 | 0.13985 | 0.085005 | -0.51617 | 121.1734 | 121.1037 | 121.1224 | 9.4104 | -120.9539 | 120.8881 | 121.1498 | 120.5486 | 1.2274 | -121.1648
1512.5938 | 121.0556 | -0.18768 | 120.9366 | 1.4211e-13 | -0.0058717 | 0.002735 | 0.067819 | -0.0092389 | 0.057576 | -0.006028 | -0.0028861 | -0.0019187 | 0.07022 | 0.026297 | 0.058925 | 0.055988 | 8.9251 | 0.069421 | 121.0406 | 120.9801 | 120.9896 | -0.017268 | 0.005626 | 1.058 | -0.097559 | 120.7599 | 121.0307 | 120.4204 | -0.24657 | 0.17041 | 0.10402 | 0.24367 | 0.2571 | 0.086689 | 0.04354 | 0.053017 | -0.058884 | -0.17668 | 0.19331 | 0.090124 | 0.14901 | 0.094166 | -0.51617 | 121.2283 | 121.1678 | 121.1773 | 9.1128 | -120.9539 | 120.9476 | 121.2184 | 120.6081 | 1.2457 | -121.1832
1514.3438 | 121.1288 | -0.14191 | 120.9229 | 1.4211e-13 | -0.0058717 | 0.0031624 | 0.067605 | -0.0090251 | 0.058003 | 0.0016025 | -0.0026725 | -0.0019187 | 0.070433 | 0.02651 | 0.058284 | 0.07888 | 8.5771 | 0.087735 | 121.0635 | 120.9939 | 121.0171 | -0.012689 | 0.010205 | 1.026 | -0.10214 | 120.7645 | 121.0491 | 120.4433 | -0.24657 | 0.12922 | 0.14064 | 0.22079 | 0.22964 | 0.10042 | 0.071009 | 0.09422 | -0.10466 | -0.15837 | 0.15211 | 0.039769 | 0.14443 | 0.12621 | -0.47954 | 121.2054 | 121.1358 | 121.159 | 8.719 | -120.9355 | 120.9064 | 121.191 | 120.5852 | 1.1679 | -121.1694
1516.0938 | 121.1609 | -0.13733 | 120.9412 | 1.4211e-13 | -0.0056581 | 0.002735 | 0.068033 | -0.0094525 | 0.058003 | -0.006028 | -0.0026725 | -0.0019187 | 0.07022 | 0.02651 | 0.058284 | 0.074302 | 7.9315 | 0.083156 | 121.0681 | 121.003 | 121.0262 | -0.017268 | 0.005626 | 1.0397 | -0.097559 | 120.7782 | 121.0582 | 120.457 | -0.24657 | 0.12006 | 0.12691 | 0.21163 | 0.22048 | 0.10042 | 0.061857 | 0.085068 | -0.10924 | -0.16294 | 0.14295 | 0.03977 | 0.14901 | 0.11706 | -0.48412 | 121.2054 | 121.1403 | 121.1636 | 8.0689 | -120.9584 | 120.9155 | 121.1955 | 120.5944 | 1.1771 | -121.1877
1517.8594 | 121.1426 | -0.14648 | 120.9412 | 1.4211e-13 | -0.0056581 | 0.0031624 | 0.067819 | -0.0092389 | 0.057789 | 0.0016025 | -0.0028861 | -0.0019187 | 0.07022 | 0.026083 | 0.058498 | 0.088037 | 7.7484 | 0.078578 | 121.0772 | 121.0213 | 121.04 | -0.017268 | 0.023941 | 1.0168 | -0.092981 | 120.8011 | 121.0674 | 120.5303 | -0.24199 | 0.12922 | 0.13607 | 0.23452 | 0.22506 | 0.095846 | 0.080173 | 0.098803 | -0.095505 | -0.14005 | 0.17042 | 0.053503 | 0.14901 | 0.12622 | -0.41086 | 121.2237 | 121.1678 | 121.1864 | 7.8949 | -120.9584 | 120.9476 | 121.2139 | 120.6768 | 1.1633 | -121.1832
1519.5938 | 121.1151 | -0.17853 | 121.0236 | 1.4211e-13 | -0.0056581 | 0.0031624 | 0.067819 | -0.0094525 | 0.057789 | 0.0016025 | -0.0026725 | -0.0019187 | 0.07022 | 0.02651 | 0.058712 | 0.083459 | 8.2154 | 0.092313 | 121.0955 | 121.0305 | 121.0491 | -0.017268 | 0.010205 | 0.99394 | -0.10214 | 120.8057 | 121.072 | 120.4937 | -0.24199 | 0.16126 | 0.071986 | 0.26199 | 0.27084 | 0.10958 | 0.006932 | 0.025563 | -0.063461 | -0.21787 | 0.18873 | 0.07639 | 0.13985 | 0.048397 | -0.52988 | 121.2741 | 121.209 | 121.2277 | 8.3939 | -121.0408 | 120.9842 | 121.2505 | 120.6722 | 1.1725 | -121.2655
1521.3594 | 121.0693 | -0.19684 | 121.0098 | 1.4211e-13 | -0.0058717 | 0.0029488 | 0.068033 | -0.0092389 | 0.057789 | 0.0016025 | -0.0028861 | -0.0021323 | 0.070433 | 0.026297 | 0.058498 | 0.07888 | 8.0552 | 0.092313 | 121.1001 | 121.0442 | 121.0629 | -0.017268 | 0.010205 | 1.1542 | -0.10214 | 120.8103 | 121.0903 | 120.5349 | -0.24199 | 0.17957 | 0.090297 | 0.27572 | 0.28915 | 0.10958 | 0.034402 | 0.053031 | -0.045151 | -0.19956 | 0.20704 | 0.0947 | 0.13985 | 0.080444 | -0.47494 | 121.297 | 121.2411 | 121.2597 | 8.252 | -121.0271 | 121.0071 | 121.2871 | 120.7317 | 1.351 | -121.2518
1523.0625 | 121.1288 | -0.19684 | 121.019 | 1.4211e-13 | -0.0054445 | 0.0031624 | 0.068246 | -0.0094525 | 0.058003 | -0.006028 | -0.0028861 | -0.0019187 | 0.07022 | 0.026297 | 0.058284 | 0.07888 | 7.6248 | 0.087735 | 121.1139 | 121.0488 | 121.0629 | -0.017268 | 0.005626 | 1.1588 | -0.10672 | 120.8286 | 121.0994 | 120.5028 | -0.24657 | 0.17957 | 0.094878 | 0.27572 | 0.28457 | 0.105 | 0.029826 | 0.043876 | -0.049729 | -0.1904 | 0.20246 | 0.090121 | 0.13985 | 0.080447 | -0.51615 | 121.3107 | 121.2456 | 121.2597 | 7.8216 | -121.0362 | 121.0254 | 121.2963 | 120.6997 | 1.3556 | -121.2655
1524.7969 | 121.138 | -0.16022 | 121.019 | 1.4211e-13 | -0.0060855 | 0.0031624 | 0.068246 | -0.0092389 | 0.058003 | -0.006028 | -0.0030999 | -0.0019187 | 0.070433 | 0.02651 | 0.058498 | 0.083459 | 7.1715 | 0.096891 | 121.123 | 121.0625 | 121.0903 | -0.012689 | 0.014784 | 1.1588 | -0.10672 | 120.8377 | 121.1132 | 120.512 | -0.24657 | 0.14753 | 0.10403 | 0.24368 | 0.25711 | 0.10958 | 0.043563 | 0.071348 | -0.08635 | -0.18124 | 0.175 | 0.0535 | 0.13985 | 0.094182 | -0.50699 | 121.2832 | 121.2228 | 121.2505 | 7.3317 | -121.0317 | 120.998 | 121.2734 | 120.6722 | 1.319 | -121.2655
1526.5469 | 121.1517 | -0.18768 | 121.019 | 1.4211e-13 | -0.0058717 | 0.0031624 | 0.06846 | -0.0092389 | 0.058217 | -0.006028 | -0.0024589 | -0.0019187 | 0.070433 | 0.02651 | 0.058712 | 0.088037 | 7.3317 | 0.10605 | 121.1322 | 121.0717 | 121.0903 | -0.017268 | 0.010205 | 1.1221 | -0.10672 | 120.8469 | 121.1269 | 120.512 | -0.23283 | 0.17041 | 0.11319 | 0.27572 | 0.29373 | 0.12332 | 0.052721 | 0.071348 | -0.045148 | -0.17208 | 0.19789 | 0.080966 | 0.12611 | 0.10792 | -0.50699 | 121.3199 | 121.2594 | 121.278 | 7.5194 | -121.0362 | 121.0346 | 121.3146 | 120.6997 | 1.3098 | -121.2518
1528.2344 | 121.1975 | -0.13733 | 121.0098 | 1.4211e-13 | -0.0058717 | 0.0031624 | 0.068674 | -0.0092389 | 0.057789 | -0.006028 | -0.0030999 | -0.0019187 | 0.070006 | 0.026297 | 0.058712 | 0.097194 | 7.3546 | 0.10147 | 121.1413 | 121.0809 | 121.0995 | -0.00811 | 0.014784 | 1.0992 | -0.088402 | 120.8561 | 121.1315 | 120.5349 | -0.24199 | 0.12922 | 0.1315 | 0.23452 | 0.2388 | 0.10958 | 0.071034 | 0.08966 | -0.10466 | -0.15377 | 0.15211 | 0.048927 | 0.15359 | 0.12165 | -0.47494 | 121.2787 | 121.2182 | 121.2368 | 7.492 | -121.0179 | 120.9934 | 121.2688 | 120.6722 | 1.2366 | -121.2518
1529.9844 | 121.2296 | -0.13733 | 121.0098 | 1.4211e-13 | -0.0058717 | 0.0042308 | 0.068246 | -0.0090251 | 0.058003 | -0.006028 | -0.0026725 | -0.0019187 | 0.070006 | 0.026297 | 0.058284 | 0.097194 | 7.4416 | 0.11063 | 121.1596 | 121.09 | 121.1132 | -0.044742 | 0.014784 | 1.113 | -0.097559 | 120.8744 | 121.1498 | 120.6036 | -0.24657 | 0.092587 | 0.14982 | 0.23452 | 0.24796 | 0.15537 | 0.080191 | 0.1034 | -0.10924 | -0.13546 | 0.15211 | 0.03977 | 0.14901 | 0.13997 | -0.40627 | 121.297 | 121.2273 | 121.2506 | 7.579 | -121.0546 | 121.0117 | 121.2871 | 120.7409 | 1.2503 | -121.2564
1531.7344 | 121.2524 | -0.14648 | 121.0327 | 1.4211e-13 | -0.0058717 | 0.0050856 | 0.06846 | -0.0094525 | 0.058003 | -0.013659 | -0.0024589 | -0.0021323 | 0.070861 | 0.026083 | 0.058284 | 0.10635 | 7.2127 | 0.1152 | 121.1551 | 121.0992 | 121.1224 | -0.012689 | 0.014784 | 1.1221 | -0.097559 | 120.8789 | 121.159 | 120.6036 | -0.24657 | 0.13379 | 0.12235 | 0.25283 | 0.26169 | 0.12789 | 0.066461 | 0.089665 | -0.10008 | -0.15377 | 0.16127 | 0.048925 | 0.14901 | 0.12624 | -0.42915 | 121.3015 | 121.2457 | 121.2689 | 7.3592 | -121.0454 | 121.0254 | 121.3054 | 120.75 | 1.2686 | -121.2793
1533.4375 | 121.2982 | -0.1236 | 121.051 | 1.4211e-13 | -0.0058717 | 0.0052992 | 0.068246 | -0.0092389 | 0.058003 | -0.006028 | -0.0028861 | -0.0021323 | 0.07022 | 0.026297 | 0.058498 | 0.12466 | 7.3363 | 0.11978 | 121.1734 | 121.1083 | 121.1178 | -0.012689 | 0.014784 | 1.1405 | -0.10214 | 120.8835 | 121.1635 | 120.6127 | -0.20994 | 0.11091 | 0.12235 | 0.24826 | 0.24338 | 0.13247 | 0.057309 | 0.066777 | -0.086341 | -0.1675 | 0.13838 | 0.021458 | 0.1078 | 0.1125 | -0.4383 | 121.297 | 121.2319 | 121.2414 | 7.4599 | -121.0637 | 121.0071 | 121.2871 | 120.7363 | 1.2641 | -121.261
1535.1406 | 121.1014 | -0.14191 | 121.0831 | 1.4211e-13 | -0.0052307 | 0.010427 | 0.06846 | -0.0094525 | 0.057576 | -0.013659 | -0.0026725 | -0.0021323 | 0.070433 | 0.026083 | 0.058498 | 0.12466 | 7.3272 | 0.11978 | 121.1825 | 121.1175 | 121.1361 | -0.13632 | 0.001048 | 1.0306 | -0.10214 | 120.8973 | 121.1773 | 120.599 | 0.13347 | 0.005587 | 0.099466 | 0.26657 | 0.26169 | 0.2561 | 0.034423 | 0.053047 | 0.27538 | -0.18581 | 0.14295 | 0.039769 | -0.23561 | 0.094196 | -0.48408 | 121.3244 | 121.2594 | 121.278 | 7.4691 | -121.2194 | 121.0392 | 121.3192 | 120.7409 | 1.1725 | -120.9496
1536.8906 | 121.3028 | -0.15106 | 121.0602 | 1.4211e-13 | -0.0056581 | 0.0040172 | 0.068674 | -0.0092389 | 0.058217 | 0.0016025 | -0.0026725 | -0.0021323 | 0.070861 | 0.026297 | 0.058498 | 0.12466 | 7.318 | 0.13352 | 121.1963 | 121.1312 | 121.1453 | -0.072215 | 0.010205 | 120.4662 | -0.10214 | 120.911 | 121.191 | 120.5944 | -0.20536 | 0.078847 | 0.13609 | 0.27573 | 0.28458 | 0.20573 | 0.071048 | 0.085092 | -0.054296 | -0.14919 | 0.16127 | 0.048924 | 0.10322 | 0.13082 | -0.46578 | 121.3473 | 121.2823 | 121.2963 | 7.4691 | -121.1324 | 121.0621 | 121.3421 | 120.7455 | 120.6173 | -121.2655
1538.6406 | 121.2982 | -0.14648 | 121.0831 | 1.4211e-13 | -0.0054445 | 0.0038034 | 0.068887 | -0.0092389 | 0.05843 | -0.006028 | -0.0024589 | -0.0019187 | 0.070433 | 0.02651 | 0.058498 | 0.12924 | 6.9884 | 0.1381 | 121.2054 | 121.1404 | 121.1544 | -0.021847 | 0.010205 | 120.5898 | -0.10214 | 120.9202 | 121.2002 | 120.6219 | -0.24199 | 0.12464 | 0.12236 | 0.27573 | 0.28458 | 0.15994 | 0.057318 | 0.071362 | -0.095505 | -0.16292 | 0.15669 | 0.044346 | 0.13985 | 0.11709 | -0.46119 | 121.3519 | 121.2869 | 121.3009 | 7.1348 | -121.1049 | 121.0666 | 121.3466 | 120.7684 | 120.7363 | -121.3251
1540.3281 | 121.1655 | -0.12817 | 121.1014 | 1.4211e-13 | -0.0058717 | 0.0038034 | 0.068674 | -0.0094525 | 0.058217 | -0.006028 | -0.0024589 | -0.0021323 | 0.070647 | 0.02651 | 0.058925 | 0.12924 | 7.025 | 0.14267 | 121.2192 | 121.145 | 121.1636 | -0.031005 | 0.010205 | 120.599 | -0.097559 | 120.9293 | 121.1956 | 120.6081 | -0.24199 | 0.097169 | 0.11778 | 0.25742 | 0.27085 | 0.17368 | 0.043587 | 0.062209 | -0.11381 | -0.17207 | 0.13838 | 0.030615 | 0.14443 | 0.0942 | -0.49324 | 121.3473 | 121.2731 | 121.2918 | 7.1532 | -121.1324 | 121.0575 | 121.3238 | 120.7363 | 120.7272 | -121.3434
1542.0156 | 121.3028 | -0.16022 | 121.1014 | 1.4211e-13 | -0.0056581 | 0.0038034 | 0.068674 | -0.0096661 | 0.058003 | 0.0016025 | -0.0026725 | -0.0019187 | 0.070433 | 0.026083 | 0.058712 | 0.16587 | 6.7777 | 0.15183 | 121.2146 | 121.1541 | 121.1682 | -0.067636 | 0.010205 | 120.631 | -0.092981 | 120.9247 | 121.2093 | 120.9515 | -0.24199 | 0.092581 | 0.11321 | 0.32609 | 0.31205 | 0.21947 | 0.052744 | 0.066787 | -0.081772 | -0.17665 | 0.17042 | 0.067236 | 0.14901 | 0.10794 | -0.14984 | 121.3748 | 121.3143 | 121.3284 | 6.938 | -121.169 | 121.0849 | 121.3695 | 121.1118 | 120.7913 | -121.3434
1543.7812 | 121.2936 | -0.14191 | 121.0693 | 1.4211e-13 | -0.0058717 | 0.0040172 | 0.069101 | -0.0096661 | 0.058217 | 0.0016025 | -0.0026725 | -0.0019187 | 0.070647 | 0.025869 | 0.058498 | 0.18418 | 7.1349 | 0.16099 | 121.21 | 121.1633 | 121.1773 | -0.040163 | 0.019362 | 120.6173 | -0.088402 | 120.9293 | 121.2139 | 120.6448 | -0.24657 | 0.10174 | 0.14067 | 0.32609 | 0.30289 | 0.20115 | 0.093945 | 0.10799 | -0.10466 | -0.14003 | 0.16127 | 0.053505 | 0.15817 | 0.14456 | -0.42457 | 121.3519 | 121.3052 | 121.3192 | 7.2768 | -121.1095 | 121.0712 | 121.3558 | 120.7867 | 120.7592 | -121.3159
1545.4688 | 121.1838 | -0.20599 | 121.1288 | 1.4211e-13 | -0.0060855 | 0.0044444 | 0.069101 | -0.0092389 | 0.057789 | 0.0016025 | -0.0024589 | -0.0019187 | 0.070433 | 0.026297 | 0.058712 | 0.2025 | 7.0296 | 0.18846 | 121.2283 | 121.1541 | 121.1773 | -0.012689 | 0.014784 | 120.6402 | -0.10672 | 120.9385 | 121.2093 | 120.6402 | -0.24199 | 0.19331 | 0.099474 | 0.40849 | 0.39445 | 0.20115 | 0.025278 | 0.048479 | -0.035995 | -0.19038 | 0.22078 | 0.099277 | 0.13527 | 0.08047 | -0.48865 | 121.4343 | 121.3601 | 121.3833 | 7.2356 | -121.1415 | 121.1445 | 121.4153 | 120.8462 | 120.8462 | -121.3708
1547.2188 | 121.2936 | -0.16479 | 121.1197 | 1.4211e-13 | -0.0060855 | 0.0042308 | 0.069528 | -0.0092389 | 0.058003 | 0.016863 | -0.0028861 | -0.0023459 | 0.070647 | 0.026083 | 0.058925 | 0.21165 | 6.8922 | 0.18388 | 121.2329 | 121.1679 | 121.1911 | -0.017268 | 0.005626 | 120.6814 | -0.097559 | 120.943 | 121.2231 | 120.6173 | -0.24657 | 0.14753 | 0.11321 | 0.37645 | 0.34867 | 0.20115 | 0.04817 | 0.071369 | -0.081772 | -0.17665 | 0.17042 | 0.067236 | 0.14901 | 0.10336 | -0.50239 | 121.3977 | 121.3327 | 121.3559 | 7.057 | -121.137 | 121.1078 | 121.3878 | 120.7821 | 120.8462 | -121.3663
1548.9688 | 121.2296 | -0.1831 | 121.106 | 1.4211e-13 | -0.0058717 | 0.0040172 | 0.069528 | -0.0094525 | 0.057789 | -0.006028 | -0.0026725 | -0.0021323 | 0.07022 | 0.02651 | 0.058712 | 0.22539 | 6.4984 | 0.19304 | 121.2421 | 121.1816 | 121.1911 | -0.026426 | 0.010205 | 120.6723 | -0.10214 | 120.9522 | 121.2276 | 120.6448 | -0.24199 | 0.15668 | 0.1361 | 0.40849 | 0.37614 | 0.21946 | 0.07564 | 0.085102 | -0.058884 | -0.15376 | 0.19331 | 0.080967 | 0.13985 | 0.12167 | -0.46119 | 121.4252 | 121.3647 | 121.3742 | 6.6815 | -121.1324 | 121.1353 | 121.4107 | 120.8279 | 120.8554 | -121.3479
1550.6406 | 121.2982 | -0.16479 | 121.106 | 1.4211e-13 | -0.0058717 | 0.0044444 | 0.069742 | -0.0094525 | 0.058217 | 0.0016025 | -0.0028861 | -0.0023459 | 0.070861 | 0.026297 | 0.059139 | 0.23455 | 5.8162 | 0.19761 | 121.2558 | 121.1862 | 121.2002 | -0.049321 | 0.014784 | 120.686 | -0.10214 | 120.9614 | 121.2368 | 120.6448 | -0.24657 | 0.11547 | 0.14983 | 0.39934 | 0.36241 | 0.24693 | 0.080219 | 0.09426 | -0.081772 | -0.1446 | 0.17958 | 0.062657 | 0.14443 | 0.13083 | -0.46119 | 121.4206 | 121.351 | 121.365 | 5.981 | -121.1553 | 121.1262 | 121.4016 | 120.8096 | 120.8508 | -121.3525
1552.3906 | 121.3257 | -0.16022 | 121.1243 | 1.4211e-13 | -0.0056581 | 0.0061538 | 0.069315 | -0.0085979 | 0.058003 | -0.006028 | -0.0026725 | -0.0019187 | 0.070647 | 0.026724 | 0.058712 | 0.23455 | 5.7796 | 0.20677 | 121.2558 | 121.1999 | 121.2048 | -0.063057 | 0.014784 | 120.7043 | -0.097559 | 120.9705 | 121.2459 | 120.6448 | -0.24657 | 0.09716 | 0.13152 | 0.39476 | 0.36699 | 0.26983 | 0.075645 | 0.080527 | -0.08635 | -0.15375 | 0.175 | 0.062658 | 0.14901 | 0.12168 | -0.4795 | 121.416 | 121.3601 | 121.365 | 5.9398 | -121.1873 | 121.1307 | 121.4062 | 120.805 | 120.8645 | -121.3708
1554.1562 | 121.2204 | -0.19684 | 121.1472 | 1.4211e-13 | -0.0056581 | 0.0042308 | 0.069528 | -0.0090251 | 0.058003 | -0.013659 | -0.0026725 | -0.0021323 | 0.07022 | 0.026297 | 0.058712 | 0.25744 | 5.4683 | 0.21593 | 121.2649 | 121.2091 | 121.2185 | -0.035584 | 0.005626 | 120.7135 | -0.097559 | 120.9797 | 121.2597 | 120.6631 | -0.24657 | 0.16125 | 0.11779 | 0.45428 | 0.41276 | 0.25151 | 0.061915 | 0.071375 | -0.049729 | -0.16748 | 0.20246 | 0.099279 | 0.14901 | 0.11252 | -0.48407 | 121.4618 | 121.4059 | 121.4154 | 5.6651 | -121.1827 | 121.1765 | 121.4565 | 120.8599 | 120.9103 | -121.3937
1555.9062 | 121.2479 | -0.1831 | 121.1884 | 1.4211e-13 | -0.010573 | 0.022393 | -0.0031241 | -0.0094525 | -0.0052412 | 0.0092325 | -0.0024589 | -0.0021323 | 0.070433 | 0.02651 | 0.058498 | -0.008109 | 0.16166 | -0.05877 | 0.26273 | 0.26594 | 0.4762 | -0.076794 | 0.042256 | 120.7684 | -0.083823 | 121.0026 | 121.2734 | 120.6722 | -0.23283 | 0.10631 | -120.9256 | 0.175 | 0.12433 | 0.018024 | -120.9224 | -120.7122 | -0.049726 | -0.18579 | 0.22536 | 0.099282 | 0.14901 | 0.085062 | -0.51611 | 0.44584 | 0.44904 | 0.65931 | 0.34476 | -121.2651 | 121.1857 | 121.4565 | 120.8553 | 120.9515 | -121.4212
1557.5938 | 121.3394 | -0.14648 | 121.138 | 1.4211e-13 | -0.011 | 0.022393 | -0.0031241 | -0.0094525 | -0.0054548 | -0.006028 | -0.0024589 | -0.0019187 | 0.070647 | 0.026083 | 0.058925 | 0.005626 | 0.13876 | -0.067927 | 0.21237 | 0.21099 | 0.42584 | -0.026426 | 0.037677 | 120.7593 | -0.088402 | 121.0117 | 121.2826 | 120.6906 | -0.23283 | 0.12006 | -120.9256 | 0.15211 | 0.078557 | -0.041501 | -120.927 | -120.7122 | -0.086347 | -0.12628 | 0.18416 | 0.058082 | 0.14443 | 0.14457 | -0.44744 | 0.35886 | 0.35747 | 0.57232 | 0.28525 | -121.1644 | 121.1582 | 121.4291 | 120.837 | 120.9057 | -121.3708
1559.3594 | 121.2936 | -0.15564 | 121.1929 | 1.4211e-13 | -0.010786 | 0.02218 | -0.0031241 | -0.0094525 | -0.0050274 | -0.006028 | -0.0024589 | -0.0019187 | 0.070861 | 0.026297 | 0.058712 | -0.012688 | 0.12503 | -0.063349 | 0.19864 | 0.19725 | 0.40753 | -0.021847 | 0.042256 | 120.7776 | -0.088402 | 121.0163 | 121.2963 | 120.6997 | -0.23283 | 0.13379 | -120.9943 | 0.14295 | 0.092291 | -0.041502 | -120.9957 | -120.7854 | -0.077191 | -0.17663 | 0.1979 | 0.067238 | 0.14443 | 0.10338 | -0.49322 | 0.35428 | 0.35289 | 0.56317 | 0.28067 | -121.2148 | 121.1719 | 121.4519 | 120.8554 | 120.9332 | -121.4258
1561.0625 | 121.2845 | -0.17853 | 121.2158 | 1.4211e-13 | -0.010573 | 0.022393 | -0.0031241 | -0.0094525 | -0.0054548 | -0.006028 | -0.0024589 | -0.0019187 | 0.070647 | 0.026083 | 0.058712 | -0.017266 | 0.12503 | -0.05877 | 0.15743 | 0.19725 | 0.40295 | -0.00811 | 0.046835 | 120.773 | -0.088402 | 121.0346 | 121.31 | 120.7272 | -0.23283 | 0.17042 | -121.0584 | 0.16126 | 0.11976 | -0.05066 | -121.0186 | -120.8129 | -0.054303 | -0.1812 | 0.22536 | 0.090126 | 0.14443 | 0.094224 | -0.48863 | 0.33596 | 0.37578 | 0.58147 | 0.30356 | -121.2239 | 121.2131 | 121.4886 | 120.9057 | 120.9515 | -121.4487
1562.8125 | 121.3943 | -0.10986 | 121.1517 | 1.4211e-13 | -0.011 | 0.02218 | -0.0033377 | -0.0094525 | -0.0054548 | -0.013659 | -0.0022453 | -0.0021323 | 0.070647 | 0.026724 | 0.058712 | -0.012688 | 0.12503 | -0.05877 | 0.15285 | 0.19267 | 0.40295 | -0.012689 | 0.037677 | 120.7776 | -0.083823 | 121.03 | 121.3146 | 120.7318 | -0.23283 | 0.097174 | -120.9989 | 0.097175 | 0.051093 | -0.046081 | -120.9591 | -120.7488 | -0.12297 | -0.1217 | 0.14754 | 0.02604 | 0.14901 | 0.16289 | -0.41997 | 0.26271 | 0.30254 | 0.51281 | 0.23489 | -121.1644 | 121.1399 | 121.4245 | 120.8416 | 120.8874 | -121.3846
1564.5625 | 121.3806 | -0.15106 | 121.1838 | 1.4211e-13 | -0.010786 | 0.022607 | -0.0031241 | -0.0096661 | -0.0056684 | -0.013659 | -0.0030999 | -0.0021323 | 0.070433 | 0.02651 | 0.058712 | -0.012688 | 0.13419 | -0.054192 | 0.14369 | 0.17436 | 0.38463 | -0.017268 | 0.042256 | 120.7776 | -0.088402 | 121.0438 | 121.3238 | 120.6677 | -0.23741 | 0.13379 | -121.0401 | 0.13837 | 0.09687 | -0.036924 | -121.0094 | -120.7991 | -0.086348 | -0.14001 | 0.19332 | 0.06266 | 0.14901 | 0.14 | -0.51611 | 0.29476 | 0.32542 | 0.53569 | 0.28525 | -121.201 | 121.1948 | 121.4748 | 120.8187 | 120.9286 | -121.4212
1566.3125 | 121.3669 | -0.15564 | 121.1838 | 1.4211e-13 | -0.010786 | 0.02218 | -0.0031241 | -0.0096661 | -0.0056684 | -0.006028 | -0.0026725 | -0.0021323 | 0.070647 | 0.02651 | 0.058498 | -0.003531 | 0.12503 | -0.05877 | 0.14369 | 0.17894 | 0.38463 | -0.026426 | 0.042256 | 120.7959 | -0.092981 | 121.0529 | 121.3329 | 120.8462 | -0.23741 | 0.12921 | -121.0401 | 0.15211 | 0.09687 | -0.032344 | -121.0048 | -120.7991 | -0.08177 | -0.13085 | 0.1979 | 0.062659 | 0.14443 | 0.14916 | -0.33755 | 0.29934 | 0.33458 | 0.54027 | 0.28067 | -121.2102 | 121.2086 | 121.4886 | 121.0019 | 120.9515 | -121.4212
1568 | 121.4172 | -0.13275 | 121.1929 | 1.4211e-13 | -0.011 | 0.022393 | -0.0035515 | -0.0092389 | -0.0056684 | -0.006028 | -0.0026725 | -0.0019187 | 0.070433 | 0.026297 | 0.058712 | -0.012688 | 0.12503 | -0.049614 | 0.14369 | 0.087359 | 0.38005 | -0.026426 | 0.051413 | 120.7776 | -0.083823 | 121.0575 | 121.3238 | 120.8188 | -0.23741 | 0.10633 | -121.0492 | 0.12006 | 0.083137 | -0.023188 | -121.1056 | -120.8129 | -0.10466 | -0.13542 | 0.18416 | 0.048928 | 0.15359 | 0.13085 | -0.37417 | 0.27645 | 0.22011 | 0.5128 | 0.25778 | -121.2194 | 121.1903 | 121.4565 | 120.9515 | 120.9103 | -121.4303
1569.75 | 121.312 | -0.19226 | 121.2387 | 1.4211e-13 | -0.011 | 0.02218 | -0.0033377 | -0.0092389 | -0.0054548 | -0.013659 | -0.0026725 | -0.0019187 | 0.07022 | 0.026083 | 0.059353 | -0.008109 | 0.12503 | -0.054192 | 0.13912 | 0.08278 | 0.38005 | -0.031005 | 0.042256 | 120.7593 | -0.092981 | 121.0621 | 121.3329 | 120.8417 | -0.23283 | 0.16126 | -121.0996 | 0.18415 | 0.13807 | -0.023187 | -121.1559 | -120.8587 | -0.04057 | -0.17662 | 0.23452 | 0.09928 | 0.13985 | 0.094229 | -0.39706 | 0.33138 | 0.27504 | 0.57231 | 0.31729 | -121.2697 | 121.2543 | 121.5252 | 121.0339 | 120.9515 | -121.4715
1571.5 | 121.4355 | -0.15106 | 121.2296 | 1.4211e-13 | -0.011 | 0.02218 | -0.0031241 | -0.0094525 | -0.0056684 | -0.006028 | -0.0026725 | -0.0021323 | 0.070861 | 0.026724 | 0.058712 | -0.008109 | 0.12961 | -0.063349 | 0.13912 | 0.08278 | 0.38005 | -0.017268 | 0.046835 | 120.7684 | -0.088402 | 121.0667 | 121.3421 | 120.8462 | -0.22825 | 0.13379 | -121.0904 | 0.14295 | 0.087713 | -0.046081 | -121.1468 | -120.8495 | -0.07719 | -0.16289 | 0.1979 | 0.06266 | 0.13985 | 0.11254 | -0.38332 | 0.29018 | 0.23384 | 0.53112 | 0.28067 | -121.2468 | 121.2177 | 121.4932 | 120.9973 | 120.9195 | -121.4578
1573.1875 | 121.3348 | -0.1831 | 121.257 | 1.4211e-13 | -0.010786 | 0.022607 | -0.0033377 | -0.0096661 | -0.0054548 | 0.0016025 | -0.0028861 | -0.0019187 | 0.070861 | 0.026083 | 0.058712 | -0.008109 | 0.12503 | -0.054192 | 0.14369 | 0.073622 | 0.38463 | -0.012689 | 0.051413 | 120.8371 | -0.079245 | 121.0758 | 121.3513 | 120.7501 | -0.23283 | 0.17042 | -121.1133 | 0.175 | 0.12891 | -0.041503 | -121.1834 | -120.8724 | -0.049726 | -0.1812 | 0.23452 | 0.10386 | 0.15359 | 0.094233 | -0.50694 | 0.3268 | 0.25673 | 0.56774 | 0.30813 | -121.2697 | 121.2589 | 121.5344 | 120.9332 | 121.0202 | -121.4899
1574.9375 | 120.9 | -0.16479 | 120.8725 | 1.4211e-13 | -0.011 | 0.022393 | -0.0031241 | -0.0092389 | -0.0054548 | 0.0016025 | -0.0030999 | -0.0019187 | 0.070433 | 0.02651 | 0.058284 | -0.021844 | 0.11129 | -0.077084 | 0.12538 | 0.069043 | 0.33427 | -0.031005 | 0.019362 | 120.2739 | -0.10672 | 120.531 | 120.7972 | 120.2464 | -0.24657 | 0.13379 | -120.7471 | 0.14295 | 0.087711 | -0.046079 | -120.8035 | -120.5382 | -0.081772 | -0.34152 | 0.18416 | 0.058078 | 0.13985 | -0.075257 | -0.62607 | 0.29018 | 0.23384 | 0.49906 | 0.27609 | -120.9035 | 120.6958 | 120.962 | 120.4112 | 120.4387 | -121.1191
1576.625 | 121.2067 | -0.15106 | 121.0648 | 1.4211e-13 | -0.010573 | 0.021966 | -0.0033377 | -0.0096661 | -0.0054548 | -0.006028 | -0.0024589 | -0.0017051 | 0.070433 | 0.02651 | 0.058498 | -0.003531 | 0.12503 | -0.049614 | 0.13454 | 0.073622 | 0.32969 | -0.017268 | 0.033099 | 120.6723 | -0.083823 | 120.9064 | 121.1818 | 120.5761 | -0.22825 | 0.13379 | -120.9302 | 0.14753 | 0.10145 | -0.032346 | -120.9911 | -120.7351 | -0.07719 | -0.15834 | 0.18416 | 0.067239 | 0.14443 | 0.11709 | -0.48867 | 0.2856 | 0.22468 | 0.48075 | 0.27609 | -121.082 | 121.0575 | 121.3329 | 120.7272 | 120.8233 | -121.293
1578.3906 | 121.312 | -0.15564 | 121.106 | 1.4211e-13 | -0.010786 | 0.021539 | -0.0031241 | -0.0092389 | -0.0054548 | 0.0016025 | -0.0024589 | -0.0019187 | 0.070647 | 0.026297 | 0.058925 | -0.012688 | 0.13419 | -0.054192 | 0.12996 | 0.055306 | 0.32511 | -0.021847 | 0.037677 | 120.7043 | -0.079245 | 120.9659 | 121.2414 | 120.6493 | -0.23283 | 0.13379 | -120.976 | 0.14295 | 0.10145 | -0.032345 | -121.0507 | -120.7808 | -0.077191 | -0.14002 | 0.19332 | 0.076395 | 0.15359 | 0.13541 | -0.45661 | 0.2856 | 0.21095 | 0.48075 | 0.28983 | -121.1278 | 121.1216 | 121.397 | 120.805 | 120.8599 | -121.3388
1580.0781 | 121.3074 | -0.13733 | 121.1334 | 1.4211e-13 | -0.010786 | 0.021966 | -0.0033377 | -0.0092389 | -0.0054548 | 0.0016025 | -0.0024589 | -0.0019187 | 0.070647 | 0.026297 | 0.058712 | -0.003531 | 0.13419 | -0.054192 | 0.13912 | 0.055306 | 0.33427 | -0.00811 | 0.02852 | 120.7821 | -0.083823 | 120.998 | 121.2734 | 120.6951 | -0.23741 | 0.12922 | -120.9943 | 0.1338 | 0.083137 | -0.046082 | -121.0781 | -120.7992 | -0.10008 | -0.13544 | 0.16585 | 0.053506 | 0.15359 | 0.13999 | -0.43829 | 0.27645 | 0.19264 | 0.4716 | 0.27152 | -121.1415 | 121.1353 | 121.4107 | 120.8325 | 120.9195 | -121.3708
1581.8281 | 121.3257 | -0.14191 | 121.1929 | 1.4211e-13 | -0.010573 | 0.021539 | -0.0031241 | -0.0094525 | -0.0056684 | -0.006028 | -0.0026725 | -0.0019187 | 0.070433 | 0.026297 | 0.058712 | -0.008109 | 0.15708 | -0.05877 | 0.12996 | 0.069043 | 0.33427 | -0.017268 | 0.037677 | 120.7959 | -0.088402 | 121.0346 | 121.3055 | 120.7455 | -0.23283 | 0.12464 | -121.063 | 0.1338 | 0.083137 | -0.041502 | -121.1239 | -120.8587 | -0.090924 | -0.15832 | 0.17958 | 0.053505 | 0.14443 | 0.11253 | -0.44743 | 0.27187 | 0.21095 | 0.47617 | 0.29899 | -121.2102 | 121.1765 | 121.4474 | 120.8874 | 120.9378 | -121.4258
1583.5156 | 121.3531 | -0.15106 | 121.2021 | 1.4211e-13 | -0.010573 | 0.02218 | -0.0031241 | -0.0092389 | -0.0052412 | 0.0016025 | -0.0026725 | -0.0021323 | 0.070861 | 0.026724 | 0.058925 | -0.008109 | 0.15708 | -0.049614 | 0.12996 | 0.059885 | 0.33427 | -0.040163 | 0.033099 | 120.8234 | -0.074666 | 121.0529 | 121.3284 | 120.7089 | -0.22367 | 0.1109 | -121.0721 | 0.14295 | 0.10145 | -0.009451 | -121.1422 | -120.8678 | -0.072611 | -0.14916 | 0.18416 | 0.076396 | 0.14901 | 0.12627 | -0.49322 | 0.28102 | 0.21095 | 0.48533 | 0.30814 | -121.2423 | 121.204 | 121.4794 | 120.8599 | 120.9744 | -121.4258
1585.2656 | 121.3028 | -0.16479 | 121.2753 | 1.4211e-13 | -0.010573 | 0.021752 | -0.0029103 | -0.0092389 | -0.0054548 | 0.0016025 | -0.0028861 | -0.0019187 | 0.070861 | 0.02651 | 0.058498 | -0.008109 | 0.16166 | -0.054192 | 0.12996 | 0.055306 | 0.32511 | -0.012689 | 0.02852 | 120.8462 | -0.088402 | 121.0804 | 121.3513 | 120.7547 | -0.22367 | 0.15211 | -121.1454 | 0.15669 | 0.1106 | -0.041503 | -121.22 | -120.9502 | -0.058878 | -0.19493 | 0.19331 | 0.076393 | 0.13527 | 0.075922 | -0.52067 | 0.29475 | 0.2201 | 0.48991 | 0.32645 | -121.288 | 121.2452 | 121.516 | 120.9195 | 121.011 | -121.499
1587.0156 | 121.4401 | -0.12817 | 121.2341 | 1.4211e-13 | -0.010573 | 0.021539 | -0.0033377 | -0.0092389 | -0.0056684 | 0.016863 | -0.0024589 | -0.0019187 | 0.070861 | 0.026297 | 0.058498 | -0.008109 | 0.16166 | -0.049614 | 0.12538 | 0.050727 | 0.32969 | -0.017268 | 0.02852 | 120.8737 | -0.079245 | 121.0941 | 121.3696 | 120.7867 | -0.22367 | 0.11091 | -121.1087 | 0.12007 | 0.07856 | -0.032346 | -121.1834 | -120.9044 | -0.095499 | -0.13999 | 0.15669 | 0.048929 | 0.14443 | 0.13544 | -0.44743 | 0.25356 | 0.1789 | 0.45786 | 0.28983 | -121.2514 | 121.2223 | 121.4977 | 120.9149 | 121.0019 | -121.4578
1588.7031 | 120.5063 | -46.0876 | 74.7528 | 1.4211e-13 | -0.011214 | 0.020684 | -0.0020557 | -0.0088115 | -0.00032684 | -0.013659 | -0.0030999 | -0.0025597 | 0.069792 | 0.026724 | 0.059566 | -45.1739 | -6.0149 | -45.7592 | -8.5415 | -8.434 | -8.681 | -46.1499 | -46.0516 | 74.3861 | -46.1228 | 74.4026 | 74.59 | 74.5611 | -46.2591 | -0.062287 | -83.2943 | 0.91374 | 0.32848 | 0.39077 | -83.1868 | -83.4338 | -0.17146 | -0.35017 | 0.03603 | -0.035105 | 0.13635 | -0.16282 | -0.19167 | 37.5461 | 37.6536 | 37.4066 | 40.0728 | -120.9027 | 120.4903 | 120.6776 | 120.6488 | 120.4737 | -121.0119
1590.4688 | 121.1975 | -45.7718 | 75.4074 | 1.4211e-13 | -0.011427 | 0.020684 | -0.0016283 | -0.0083841 | -0.00032684 | -0.013659 | -0.0030999 | -0.0027733 | 0.07022 | 0.026938 | 0.059994 | -44.9404 | -5.9004 | -44.9397 | -8.569 | -8.4707 | -8.7268 | -45.8889 | -45.7952 | 75.1782 | -45.8663 | 75.2085 | 75.4096 | 75.3578 | -45.989 | -0.11714 | -83.9764 | 0.83138 | 0.83214 | 0.94928 | -83.8781 | -84.1342 | -0.21716 | -0.19895 | -0.023418 | -0.094553 | 0.12261 | 0.002144 | -0.049598 | 37.2028 | 37.3011 | 37.045 | 39.8714 | -121.2963 | 120.9802 | 121.1813 | 121.1296 | 120.95 | -121.3964
1592.1562 | 121.2433 | -45.6665 | 75.5493 | 1.4211e-13 | -0.011427 | 0.02047 | -0.0018419 | -0.0083841 | -0.0011816 | 0.0016025 | -0.0028861 | -0.0021323 | 0.07022 | 0.026724 | 0.05978 | -44.858 | -6.6055 | -44.1293 | -8.5827 | -8.4752 | -8.7314 | -45.7561 | -45.6212 | 75.3659 | -45.7244 | 75.3916 | 75.5927 | 75.138 | -45.8653 | -0.089641 | -84.132 | 0.80851 | 1.5372 | 1.6268 | -84.0245 | -84.2807 | -0.19882 | -0.15772 | 0.045287 | -0.057899 | 0.14092 | 0.043382 | -0.41128 | 37.0838 | 37.1913 | 36.9351 | 39.061 | -121.3055 | 121.0581 | 121.2592 | 120.8045 | 121.0324 | -121.4146
1593.9219 | 121.3669 | -45.4559 | 75.7233 | 1.4211e-13 | -0.011214 | 0.020898 | -0.0014147 | -0.0081705 | -0.0011816 | -0.013659 | -0.0028861 | -0.0021323 | 0.07022 | 0.02651 | 0.060421 | -44.6932 | -6.1202 | -43.6577 | -8.5781 | -8.4844 | -8.7314 | -45.4951 | -45.4381 | 75.5399 | -45.5504 | 75.6114 | 75.8079 | 75.3715 | -45.6822 | -0.039214 | -84.3014 | 0.76276 | 1.7982 | 1.8374 | -84.2077 | -84.4546 | -0.22624 | -0.1119 | 0.017864 | -0.094479 | 0.13176 | 0.084626 | -0.35172 | 36.8778 | 36.9715 | 36.7246 | 39.3357 | -121.2184 | 121.0673 | 121.2638 | 120.8275 | 120.9958 | -121.4054
1595.6094 | 121.3577 | -121.1014 | 0.20599 | 1.4211e-13 | -0.011427 | 0.018975 | 0.0011495 | -0.0045383 | 0.006083 | -0.006028 | -0.0037407 | -0.0032007 | 0.069792 | 0.026724 | 0.061062 | -117.8009 | -16.3396 | -114.4883 | -8.5781 | -8.4798 | -8.7314 | -121.1619 | -120.6434 | 0.1194 | -120.7191 | 0.22644 | 0.34794 | 0.3191 | -121.4021 | -0.060496 | -8.7841 | 3.3005 | 6.6131 | 6.6736 | -8.6858 | -8.9374 | -0.30069 | 0.020447 | 0.458 | 0.38229 | 0.68298 | 0.14195 | 0.1131 | 112.5232 | 112.6216 | 112.37 | 104.7618 | -121.3679 | 121.3278 | 121.4493 | 121.4205 | 121.2208 | -121.6081
1597.3594 | 121.4539 | -121.0648 | 0.16022 | 1.4211e-13 | -0.011214 | 0.018547 | 0.00093595 | -0.0043245 | 0.0062966 | -0.013659 | -0.0039543 | -0.0032007 | 0.069792 | 0.026938 | 0.061276 | -117.3568 | -15.4331 | -114.3143 | -8.5827 | -8.489 | -8.7359 | -121.2077 | -120.6846 | 0.064461 | -120.7649 | 0.18066 | 0.30216 | 0.27331 | -121.4479 | -0.14291 | -8.7429 | 3.708 | 6.7504 | 6.8933 | -8.6492 | -8.8962 | -0.3831 | 0.020439 | 0.38017 | 0.29988 | 0.68298 | 0.14194 | 0.11309 | 112.482 | 112.5758 | 112.3288 | 105.6317 | -121.3679 | 121.2454 | 121.3669 | 121.3381 | 121.1292 | -121.6081
1599.0625 | 121.4859 | -121.0831 | 0.17853 | 1.4211e-13 | -0.011427 | 0.018547 | 0.0011495 | -0.0036837 | 0.006724 | 0.0016025 | -0.0037407 | -0.0032007 | 0.069792 | 0.026724 | 0.061062 | -117.224 | -15.6803 | -114.2457 | -8.5781 | -8.4798 | -8.7359 | -121.2443 | -120.7121 | 0.073618 | -120.7924 | 0.18066 | 0.30216 | 0.26873 | -121.4936 | -0.16123 | -8.7567 | 3.8591 | 6.8374 | 6.9986 | -8.6583 | -8.9145 | -0.41058 | 0.002128 | 0.37101 | 0.29072 | 0.7013 | 0.12363 | 0.090203 | 112.5049 | 112.6033 | 112.3471 | 105.4028 | -121.4228 | 121.2637 | 121.3852 | 121.3518 | 121.1567 | -121.6722
1600.75 | 121.376 | -121.1334 | 0.23346 | 1.4211e-13 | -0.011641 | 0.018547 | 0.00093595 | -0.0041109 | 0.0075786 | -0.013659 | -0.0035271 | -0.0032007 | 0.069792 | 0.027151 | 0.061062 | -117.0088 | -15.195 | -114.1724 | -8.5873 | -8.4844 | -8.7405 | -121.1436 | -120.7395 | 0.06904 | -120.8152 | 0.17608 | 0.29758 | 0.26415 | -121.5074 | -0.010136 | -8.8207 | 4.1246 | 6.961 | 6.9711 | -8.7178 | -8.974 | -0.37396 | -0.057381 | 0.39389 | 0.31818 | 0.69214 | 0.064121 | 0.030693 | 112.5461 | 112.649 | 112.3929 | 105.9384 | -121.377 | 121.3095 | 121.431 | 121.3976 | 121.2025 | -121.7408
1602.5 | 121.5225 | -121.17 | 0.18768 | 1.4211e-13 | -0.011427 | 0.018334 | 0.0011495 | -0.0038973 | 0.007365 | 0.0016025 | -0.0035271 | -0.0034143 | 0.069579 | 0.027151 | 0.061062 | -117.1965 | -11.6649 | -114.0305 | -8.5964 | -8.4798 | -8.7314 | -121.1573 | -120.7533 | 0.064461 | -120.8336 | 0.1715 | 0.293 | 0.26415 | -121.5303 | 0.012748 | -8.7841 | 3.9735 | 7.1396 | 7.1268 | -8.6675 | -8.919 | -0.36023 | -0.016184 | 0.41678 | 0.33648 | 0.69672 | 0.10532 | 0.076469 | 112.5736 | 112.6902 | 112.4387 | 109.5052 | -121.345 | 121.3415 | 121.463 | 121.4342 | 121.2345 | -121.718
1604.25 | 121.4355 | -121.1746 | 0.19226 | 1.4211e-13 | -0.011 | 0.018547 | 0.0011495 | -0.0036837 | 0.0077924 | -0.006028 | -0.0037407 | -0.0032007 | 0.069792 | 0.02651 | 0.061062 | -116.8531 | -9.3756 | -113.8748 | -8.5781 | -8.489 | -8.7359 | -121.1802 | -120.7716 | 0.06904 | -120.8427 | 0.1715 | 0.293 | -0.079243 | -121.544 | -0.005568 | -8.7704 | 4.3215 | 7.2998 | 7.3054 | -8.6812 | -8.9282 | -0.36939 | -0.020762 | 0.40304 | 0.33191 | 0.7013 | 0.10074 | -0.2715 | 112.5965 | 112.6857 | 112.4387 | 111.7991 | -121.3725 | 121.3461 | 121.4676 | 121.0954 | 121.2437 | -121.7363
1606 | 121.4493 | -121.1838 | 0.20599 | 1.4211e-13 | -0.011 | 0.018334 | 0.0015769 | -0.0034699 | 0.0077924 | 0.0016025 | -0.0039543 | -0.0032007 | 0.070006 | 0.026724 | 0.060848 | -116.6425 | -8.5789 | -113.3025 | -8.5781 | -8.489 | -8.7451 | -121.1893 | -120.7807 | 0.06904 | -120.861 | 0.16692 | 0.28384 | -0.079243 | -121.5623 | -0.005571 | -8.7841 | 4.5412 | 7.8812 | 7.8868 | -8.695 | -8.9511 | -0.37855 | -0.039073 | 0.40304 | 0.32275 | 0.7013 | 0.07785 | -0.28524 | 112.6056 | 112.6948 | 112.4387 | 112.6049 | -121.3953 | 121.3507 | 121.4676 | 121.1045 | 121.2528 | -121.7683
1607.6719 | 121.5317 | -121.1792 | 0.16937 | 1.4211e-13 | -0.011641 | 0.018334 | 0.0015769 | -0.0030427 | 0.008006 | 0.0016025 | -0.0035271 | -0.0032007 | 0.069365 | 0.026938 | 0.061062 | -116.6975 | -4.8702 | -113.0965 | -8.5919 | -8.4935 | -8.7405 | -121.2077 | -120.7853 | 0.064461 | -120.8702 | 0.16234 | 0.28384 | -0.083821 | -121.5852 | -0.028465 | -8.7612 | 4.4817 | 8.0827 | 8.1111 | -8.6629 | -8.9099 | -0.40602 | -0.007031 | 0.39388 | 0.30901 | 0.71503 | 0.11447 | -0.25319 | 112.5873 | 112.6857 | 112.4387 | 116.309 | -121.377 | 121.3415 | 121.463 | 121.0954 | 121.2437 | -121.7546
1609.4375 | 121.4813 | -121.2204 | 0.21057 | 1.4211e-13 | -0.011427 | 0.018334 | 0.0013633 | -0.0026153 | 0.0084332 | -0.006028 | -0.0033135 | -0.0034143 | 0.069792 | 0.026938 | 0.061062 | -116.5143 | -3.1304 | -112.9683 | -8.5919 | -8.4935 | -8.7451 | -121.226 | -120.7899 | 0.050725 | -120.8793 | 0.1715 | 0.28384 | -0.065507 | -121.599 | -0.005582 | -8.8024 | 4.7061 | 8.2521 | 8.2577 | -8.7041 | -8.9557 | -0.37856 | -0.039072 | 0.4305 | 0.34105 | 0.71961 | 0.073273 | -0.27608 | 112.6285 | 112.7269 | 112.4753 | 118.09 | -121.4366 | 121.3919 | 121.5042 | 121.1549 | 121.2711 | -121.8095
1611.1875 | 121.5591 | -121.2341 | 0.16022 | 1.4211e-13 | -0.011427 | 0.018334 | 0.0017907 | -0.0024017 | 0.0082196 | 0.0016025 | -0.0037407 | -0.0029869 | 0.069792 | 0.026938 | 0.061276 | -116.4823 | -1.9628 | -112.7486 | -8.5827 | -8.489 | -8.7405 | -121.1985 | -120.8036 | 0.055303 | -120.8931 | 0.16692 | 0.27926 | -0.079243 | -121.6081 | 0.035625 | -8.7429 | 4.7518 | 8.4856 | 8.4499 | -8.6492 | -8.9007 | -0.37399 | 0.006704 | 0.4305 | 0.34105 | 0.71503 | 0.11905 | -0.23946 | 112.6514 | 112.7452 | 112.4936 | 119.2713 | -121.3587 | 121.4011 | 121.5134 | 121.1549 | 121.2894 | -121.7683
1612.9375 | 121.4584 | -121.2662 | 0.20599 | 1.4211e-13 | -0.011214 | 0.017693 | 0.0015769 | -0.0034699 | 0.0090742 | 0.0016025 | -0.0039543 | -0.0032007 | 0.069792 | 0.026724 | 0.061062 | -116.203 | -1.5874 | -113.6551 | -8.5964 | -8.489 | -8.7405 | -121.2489 | -120.8082 | 0.050725 | -120.9022 | 0.15776 | 0.27926 | -0.042614 | -121.6173 | 0.0173 | -8.8024 | 5.0632 | 7.6111 | 7.5938 | -8.695 | -8.9465 | -0.3511 | -0.04823 | 0.45796 | 0.36393 | 0.71504 | 0.073271 | -0.24861 | 112.6697 | 112.7772 | 112.5257 | 119.6788 | -121.4549 | 121.4239 | 121.5454 | 121.2236 | 121.3169 | -121.8233
1614.625 | 121.4584 | -121.2433 | 0.21057 | 1.4211e-13 | -0.011214 | 0.017906 | 0.0015769 | -0.0034699 | 0.0090742 | 0.0016025 | -0.0037407 | -0.0032007 | 0.070006 | 0.026724 | 0.060848 | -116.1298 | -1.3768 | -113.2384 | -8.5873 | -8.489 | -8.7451 | -121.2535 | -120.8174 | 0.050725 | -120.9114 | 0.1715 | 0.27469 | -0.0243 | -121.631 | -0.010167 | -8.7979 | 5.1135 | 8.0048 | 8.015 | -8.6995 | -8.9557 | -0.38773 | -0.039072 | 0.42592 | 0.33189 | 0.71961 | 0.064116 | -0.23487 | 112.656 | 112.7543 | 112.4982 | 119.8665 | -121.464 | 121.4148 | 121.518 | 121.219 | 121.294 | -121.8416
1616.3594 | 121.5958 | -121.2341 | 0.16022 | 1.4211e-13 | -0.011641 | 0.01812 | 0.0017907 | -0.0030427 | 0.0095016 | -0.006028 | -0.0035271 | -0.0034143 | 0.069579 | 0.02651 | 0.061276 | -116.1435 | -1.3172 | -113.0324 | -8.5919 | -8.4935 | -8.7497 | -121.2718 | -120.8311 | 0.050725 | -120.9251 | 0.15776 | 0.27011 | -0.097557 | -121.6539 | -0.037638 | -8.7521 | 5.0906 | 8.2017 | 8.2393 | -8.6538 | -8.9099 | -0.41977 | -0.002453 | 0.40303 | 0.309 | 0.72877 | 0.10989 | -0.25777 | 112.6423 | 112.7406 | 112.4845 | 119.9169 | -121.432 | 121.3919 | 121.5042 | 121.1366 | 121.2849 | -121.8141
1618.1094 | 121.5637 | -121.2524 | 0.17853 | 1.4211e-13 | -0.011427 | 0.018334 | 0.0015769 | -0.0032563 | 0.0095016 | -0.006028 | -0.0037407 | -0.0034143 | 0.069579 | 0.026724 | 0.061276 | -116.0428 | -1.1753 | -113.0645 | -8.5919 | -8.489 | -8.7451 | -121.2947 | -120.8403 | 0.059882 | -120.9297 | 0.15776 | 0.27011 | -0.079243 | -121.6585 | -0.042222 | -8.7704 | 5.2097 | 8.188 | 8.2302 | -8.6675 | -8.9236 | -0.40604 | -0.020764 | 0.41218 | 0.32273 | 0.72877 | 0.09158 | -0.25777 | 112.6606 | 112.7635 | 112.5073 | 120.0771 | -121.4732 | 121.4102 | 121.5225 | 121.1732 | 121.3123 | -121.837
1619.8594 | 121.5591 | -121.2753 | 0.19226 | 1.4211e-13 | -0.011214 | 0.017906 | 0.0017907 | -0.0026153 | 0.009929 | -0.006028 | -0.0037407 | -0.0032007 | 0.070006 | 0.026938 | 0.060207 | -116.0519 | -1.157 | -112.6158 | -8.5964 | -8.4935 | -8.7451 | -121.2992 | -120.8448 | 0.055303 | -120.9297 | 0.15776 | 0.27469 | -0.074664 | -121.6768 | -0.023912 | -8.7887 | 5.2234 | 8.6595 | 8.6834 | -8.6858 | -8.9374 | -0.40147 | -0.034497 | 0.43049 | 0.34562 | 0.74709 | 0.082426 | -0.26692 | 112.6789 | 112.7818 | 112.5302 | 120.1183 | -121.4915 | 121.4331 | 121.55 | 121.2007 | 121.3306 | -121.8691
1621.5469 | 121.5179 | -121.2936 | 0.20142 | 1.4211e-13 | -0.011214 | 0.01812 | 0.0013633 | -0.0024017 | 0.01057 | 0.0016025 | -0.0037407 | -0.0032007 | 0.070006 | 0.026938 | 0.060207 | -115.8963 | -1.2119 | -112.2266 | -8.5919 | -8.4844 | -8.7497 | -121.3084 | -120.8494 | 0.046146 | -120.9389 | 0.15318 | 0.27926 | -0.079243 | -121.6814 | -0.01476 | -8.7933 | 5.3974 | 9.067 | 9.0818 | -8.6858 | -8.9511 | -0.38774 | -0.048231 | 0.44422 | 0.35477 | 0.74251 | 0.077849 | -0.28066 | 112.7018 | 112.8093 | 112.544 | 120.0817 | -121.5098 | 121.4468 | 121.5729 | 121.2144 | 121.3398 | -121.8828
1623.3125 | 121.5683 | -121.3211 | 0.18768 | 1.4211e-13 | -0.011 | 0.017906 | 0.0015769 | -0.0017607 | 0.010356 | -0.006028 | -0.0039543 | -0.0034143 | 0.069792 | 0.026938 | 0.059994 | -116.029 | -1.2302 | -111.4666 | -8.5964 | -8.4981 | -8.7497 | -121.3176 | -120.854 | 0.050725 | -120.9572 | 0.15318 | 0.27926 | -0.05635 | -121.6997 | 0.003548 | -8.7841 | 5.2921 | 9.8545 | 9.8509 | -8.6858 | -8.9374 | -0.37859 | -0.034498 | 0.46711 | 0.36392 | 0.74251 | 0.091582 | -0.24403 | 112.7247 | 112.823 | 112.5714 | 120.0909 | -121.5052 | 121.4743 | 121.6004 | 121.2648 | 121.3718 | -121.8874
1625.0781 | 121.6553 | -121.2845 | 0.16479 | 1.4211e-13 | -0.011214 | 0.017906 | 0.0020043 | -0.0011197 | 0.011211 | -0.006028 | -0.0037407 | -0.0032007 | 0.070006 | 0.027151 | 0.059994 | -115.9466 | -1.2257 | -110.7891 | -8.6056 | -8.4981 | -8.7497 | -121.3359 | -120.8448 | 0.050725 | -120.9572 | 0.15776 | 0.27469 | -0.083821 | -121.7134 | -0.051389 | -8.7704 | 5.3379 | 10.4954 | 10.5468 | -8.6629 | -8.9145 | -0.42894 | -0.007031 | 0.43964 | 0.3273 | 0.75625 | 0.10989 | -0.24862 | 112.6789 | 112.7864 | 112.5348 | 120.0588 | -121.5007 | 121.4422 | 121.5592 | 121.2007 | 121.3352 | -121.8782
1626.8125 | 121.582 | -121.3394 | 0.20599 | 1.4211e-13 | -0.011214 | 0.017906 | 0.0015769 | -0.00090586 | 0.011425 | 0.0016025 | -0.0035271 | -0.0032007 | 0.070006 | 0.026938 | 0.060207 | -115.9237 | -1.2348 | -110.3587 | -8.5964 | -8.4935 | -8.7497 | -121.3405 | -120.8769 | 0.055303 | -120.9847 | 0.15776 | 0.27469 | -0.10214 | -121.7226 | -0.001036 | -8.8024 | 5.4157 | 10.9807 | 10.9817 | -8.6995 | -8.9557 | -0.38317 | -0.04823 | 0.46252 | 0.35476 | 0.73793 | 0.068693 | -0.30813 | 112.743 | 112.8459 | 112.5897 | 120.1046 | -121.5464 | 121.4972 | 121.6141 | 121.2373 | 121.3947 | -121.9286
1628.5 | 121.5454 | -121.3165 | 0.20142 | 1.4211e-13 | -0.011641 | 0.017906 | 0.0020043 | -5.1258e-05 | 0.012066 | -0.013659 | -0.0037407 | -0.0029869 | 0.069792 | 0.026724 | 0.060207 | -115.791 | -1.2898 | -109.2645 | -8.5919 | -8.5027 | -8.7543 | -121.345 | -120.8769 | 0.046146 | -120.9892 | 0.15776 | 0.26553 | -0.0884 | -121.7272 | -0.028504 | -8.7933 | 5.5256 | 12.052 | 12.0805 | -8.7041 | -8.9557 | -0.41064 | -0.043652 | 0.43964 | 0.32729 | 0.73793 | 0.064114 | -0.28982 | 112.7247 | 112.8138 | 112.5623 | 120.0268 | -121.5464 | 121.4743 | 121.5821 | 121.2281 | 121.3627 | -121.9286
1630.25 | 121.6187 | -121.3303 | 0.19684 | 1.4211e-13 | -0.011 | 0.017906 | 0.0015769 | 0.0012307 | 0.012493 | -0.006028 | -0.0039543 | -0.0032007 | 0.069792 | 0.026938 | 0.060421 | -115.8596 | -1.8438 | -108.1062 | -8.6056 | -8.4981 | -8.7543 | -121.3496 | -120.8769 | 0.055303 | -120.9938 | 0.15776 | 0.27926 | -0.070086 | -121.7363 | -0.01935 | -8.8024 | 5.4706 | 13.2241 | 13.2434 | -8.695 | -8.9511 | -0.40606 | -0.039074 | 0.45337 | 0.33645 | 0.74251 | 0.082427 | -0.26692 | 112.7247 | 112.8321 | 112.576 | 119.4865 | -121.5464 | 121.488 | 121.6095 | 121.2602 | 121.3856 | -121.9332
1631.9375 | 121.6187 | -121.344 | 0.18768 | 1.4211e-13 | -0.011427 | 0.017906 | 0.0015769 | 0.0018717 | 0.013775 | -0.006028 | -0.0041681 | -0.0027733 | 0.069792 | 0.027151 | 0.060207 | -115.4522 | -1.7705 | -106.9937 | -8.5964 | -8.5027 | -8.7543 | -121.3679 | -120.8952 | 0.055303 | -121.0076 | 0.15776 | 0.26553 | -0.060928 | -121.7501 | -0.023932 | -8.7841 | 5.8918 | 14.3503 | 14.3743 | -8.6904 | -8.9419 | -0.40607 | -0.029919 | 0.44879 | 0.33644 | 0.74251 | 0.077847 | -0.24861 | 112.7475 | 112.8413 | 112.5897 | 119.5735 | -121.5556 | 121.5018 | 121.6095 | 121.2831 | 121.3993 | -121.9377
1633.6719 | 121.582 | -121.3623 | 0.19684 | 1.4211e-13 | -0.011427 | 0.017906 | 0.0013633 | 0.0040083 | 0.015271 | -0.006028 | -0.0039543 | -0.0032007 | 0.070006 | 0.026724 | 0.060635 | -115.2187 | -1.7522 | -104.3154 | -8.601 | -8.5073 | -8.7451 | -121.3771 | -120.9044 | 0.050725 | -121.0076 | 0.15776 | 0.27469 | -0.083821 | -121.7592 | -0.014779 | -8.7979 | 6.1436 | 17.0469 | 17.0617 | -8.7041 | -8.9419 | -0.39691 | -0.039074 | 0.45794 | 0.35475 | 0.75167 | 0.077849 | -0.28066 | 112.7613 | 112.855 | 112.6172 | 119.6101 | -121.5739 | 121.5201 | 121.637 | 121.2785 | 121.413 | -121.9561
1635.4375 | 121.6278 | -121.3623 | 0.21515 | 1.4211e-13 | -0.011214 | 0.018547 | 0.00093595 | 0.012128 | 0.021039 | 0.0016025 | -0.0033135 | -0.0034143 | 0.070006 | 0.026938 | 0.060421 | -113.8772 | -1.3355 | -93.8586 | -8.601 | -8.5027 | -8.7588 | -121.3771 | -120.9044 | 0.059882 | -121.0121 | 0.15318 | 0.27469 | -0.033457 | -121.7638 | -0.014779 | -8.8162 | 7.4851 | 27.5037 | 27.5185 | -8.7179 | -8.974 | -0.40149 | -0.061964 | 0.45794 | 0.35018 | 0.75167 | 0.059538 | -0.24861 | 112.7613 | 112.8596 | 112.6035 | 120.0268 | -121.5922 | 121.5155 | 121.637 | 121.3288 | 121.4222 | -121.9789
1637.1875 | 121.669 | -121.3394 | 0.20599 | 1.4211e-13 | -0.011 | 0.02047 | -0.0016283 | 0.044391 | 0.044542 | 0.0016025 | -0.0037407 | -0.0029869 | 0.070006 | 0.026938 | 0.060421 | -113.0943 | -0.97841 | -48.5611 | -8.6056 | -8.5027 | -8.7543 | -121.3771 | -120.8906 | 0.06904 | -121.003 | 0.17608 | 0.27926 | 0.016908 | -121.7638 | -0.037667 | -8.8116 | 8.2451 | 72.7783 | 72.816 | -8.7087 | -8.9603 | -0.42438 | -0.029916 | 0.44879 | 0.33644 | 0.76082 | 0.073271 | -0.18909 | 112.7338 | 112.8367 | 112.5852 | 120.361 | -121.5831 | 121.5155 | 121.6187 | 121.3563 | 121.4085 | -121.9698
1638.9375 | 121.6049 | -121.3577 | 0.22888 | 1.4211e-13 | -0.010786 | 0.021111 | -0.0022693 | 0.055929 | 0.05138 | 0.0016025 | -0.0035271 | -0.0032007 | 0.070006 | 0.027151 | 0.060635 | -112.7326 | -0.92347 | -34.1899 | -8.601 | -8.5073 | -8.7543 | -121.3679 | -120.886 | 0.073618 | -121.0076 | 0.1715 | 0.28384 | -0.019721 | -121.7638 | -0.010199 | -8.8299 | 8.6251 | 87.1679 | 87.1781 | -8.7362 | -8.9831 | -0.40607 | -0.057383 | 0.47168 | 0.35018 | 0.75625 | 0.054962 | -0.2486 | 112.7567 | 112.8504 | 112.6035 | 120.4343 | -121.5968 | 121.5292 | 121.6416 | 121.338 | 121.4313 | -121.9927
1640.625 | 121.6965 | -121.3577 | 0.20599 | 1.4211e-13 | -0.011 | 0.020898 | -0.0026967 | 0.056997 | 0.051807 | 0.0016025 | -0.0037407 | -0.0036279 | 0.070006 | 0.026938 | 0.060207 | -112.4167 | -0.98299 | -32.7111 | -8.5964 | -8.5027 | -8.7588 | -121.3771 | -120.8906 | 0.073618 | -121.0121 | 0.18066 | 0.28384 | -0.0243 | -121.7775 | -0.019357 | -8.8024 | 8.941 | 88.6467 | 88.666 | -8.7087 | -8.9648 | -0.41981 | -0.025338 | 0.4671 | 0.3456 | 0.7654 | 0.07785 | -0.23029 | 112.7613 | 112.855 | 112.5989 | 120.3747 | -121.5831 | 121.5384 | 121.6416 | 121.3334 | 121.4313 | -121.9835
1642.375 | 121.6232 | -121.3669 | 0.21973 | 1.4211e-13 | -0.011 | 0.021325 | -0.0026967 | 0.055929 | 0.052021 | -0.006028 | -0.0035271 | -0.0032007 | 0.069579 | 0.026938 | 0.060635 | -111.675 | -0.96468 | -34.2677 | -8.6056 | -8.5073 | -8.7543 | -121.3908 | -120.8952 | 0.078197 | -121.0167 | 0.1715 | 0.27926 | -0.05635 | -121.7867 | -0.023939 | -8.8253 | 9.6919 | 87.0992 | 87.1231 | -8.727 | -8.974 | -0.41981 | -0.048228 | 0.47168 | 0.35017 | 0.76998 | 0.059538 | -0.27608 | 112.7613 | 112.8596 | 112.6126 | 120.4022 | -121.6105 | 121.5384 | 121.6461 | 121.3105 | 121.4451 | -122.0064
1644.125 | 121.7056 | -121.3623 | 0.21057 | 1.4211e-13 | -0.010573 | 0.021539 | -0.0029103 | 0.058065 | 0.053303 | 0.0092325 | -0.0039543 | -0.0032007 | 0.070006 | 0.026938 | 0.060635 | -111.4644 | -0.99215 | -31.4841 | -8.6056 | -8.5027 | -8.7588 | -121.4091 | -120.8998 | 0.082776 | -121.0213 | 0.18066 | 0.27926 | -0.065507 | -121.7867 | -0.046832 | -8.8162 | 9.8979 | 89.8782 | 89.925 | -8.7133 | -8.9694 | -0.42439 | -0.029915 | 0.46252 | 0.34102 | 0.7654 | 0.068694 | -0.27608 | 112.7567 | 112.8596 | 112.6035 | 120.3702 | -121.6197 | 121.543 | 121.6416 | 121.2968 | 121.4451 | -121.9973
1645.8906 | 121.6644 | -121.3943 | 0.2243 | 1.4211e-13 | -0.010359 | 0.021325 | -0.0031241 | 0.060202 | 0.055226 | -0.013659 | 0.044114 | 0.042095 | 0.070647 | 0.11967 | 0.060421 | -110.8097 | -1.0563 | -28.554 | -8.6102 | -8.4981 | -8.7588 | -121.3954 | -120.886 | 0.055303 | -0.065509 | 0.16234 | 0.27011 | -0.070086 | -121.7867 | -0.001052 | -8.8345 | 10.5847 | 92.8404 | 92.8414 | -8.7224 | -8.9831 | -0.39234 | -0.061962 | 0.5083 | 121.3288 | 121.7212 | 0.045804 | -0.29439 | 112.7842 | 112.8962 | 112.6355 | 120.3381 | -121.6197 | 121.5567 | 121.6645 | 121.3243 | 121.4497 | -122.011
1647.5625 | 121.7468 | -121.3531 | 0.16937 | 1.4211e-13 | -0.010359 | 0.021539 | -0.0031241 | 0.060415 | 0.055867 | -0.006028 | 0.042832 | 0.043163 | 0.070861 | 0.11967 | 0.060635 | -110.6128 | -1.2119 | -28 | -8.601 | -8.5073 | -8.7588 | -121.3954 | -120.8952 | 0.059882 | -0.015143 | 0.16234 | 0.27469 | -0.079243 | -121.7775 | -0.042251 | -8.7704 | 10.7403 | 93.3531 | 93.3954 | -8.6767 | -8.9282 | -0.42438 | -0.007031 | 0.45794 | 121.338 | 121.7624 | 0.10531 | -0.24862 | 112.7521 | 112.8459 | 112.5943 | 120.1412 | -121.5648 | 121.5155 | 121.6278 | 121.2739 | 121.413 | -121.9469
1649.3125 | 121.701 | -121.3943 | 0.20142 | 1.4211e-13 | -0.010573 | 0.021752 | -0.0033377 | 0.061484 | 0.056507 | -0.006028 | 0.050951 | 0.035044 | 0.070647 | 0.11946 | 0.060207 | -110.2465 | -1.4775 | -26.9241 | -8.6056 | -8.5119 | -8.7588 | -121.4137 | -120.8952 | 0.050725 | -0.015143 | 0.15318 | 0.27926 | -0.079243 | -121.7958 | -0.019367 | -8.807 | 11.1478 | 94.4702 | 94.4896 | -8.7133 | -8.9603 | -0.4015 | -0.048231 | 0.49914 | 121.3792 | 121.7807 | 0.077849 | -0.28066 | 112.7887 | 112.8825 | 112.6355 | 119.9169 | -121.6151 | 121.5475 | 121.6736 | 121.3151 | 121.4451 | -121.9973
1651 | 121.7194 | -121.463 | 0.16937 | 1.4211e-13 | -0.010573 | 0.021966 | -0.0033377 | -0.0092389 | 0.01057 | 0.0016025 | 0.0486 | 0.037181 | 0.07022 | 0.11924 | 0.060421 | -0.072207 | -0.081008 | -0.11829 | 0.14369 | 0.078201 | 0.32969 | -0.17753 | -120.9364 | 0.014095 | -0.06093 | 0.12114 | 0.24264 | -0.11587 | -121.8371 | 121.2855 | -0.025678 | 121.3908 | 121.3447 | 0.059242 | -0.091172 | 0.16032 | -0.37404 | -0.048237 | 0.5266 | 121.4021 | 121.7761 | 0.073264 | -0.28524 | 121.6067 | 121.5412 | 121.7927 | 121.382 | -0.3469 | 121.5841 | 121.7057 | 121.3471 | 121.4771 | -122.0064
1652.7344 | 121.7514 | -121.4447 | 0.16479 | 1.4211e-13 | -0.010573 | 0.02218 | -0.0031241 | -0.0090251 | 0.0095016 | -0.006028 | 0.052019 | 0.033976 | 0.07022 | 0.11924 | 0.060635 | -0.026423 | -0.090166 | -0.090818 | 0.14827 | 0.087359 | 0.32969 | -0.085952 | -120.941 | 0.023253 | -0.047194 | 0.13029 | 0.23806 | -0.10671 | -121.8554 | 121.3588 | -0.016521 | 121.4183 | 121.3539 | -0.004866 | -0.077436 | 0.16489 | -0.41067 | -0.034502 | 0.50371 | 121.3975 | 121.8082 | 0.073263 | -0.27151 | 121.593 | 121.5321 | 121.7744 | 121.3545 | -0.25075 | 121.575 | 121.6828 | 121.338 | 121.468 | -122.0202
1654.5 | 121.6965 | -121.4722 | 0.16479 | 1.4211e-13 | -0.010359 | 0.021966 | -0.0031241 | -0.0090251 | 0.009288 | 0.0092325 | 0.044328 | 0.040813 | 0.070433 | 0.11882 | 0.060635 | -0.008109 | -0.13595 | -0.08624 | 0.15285 | 0.091937 | 0.33885 | -0.053899 | -120.9502 | 0.03241 | -0.047194 | 0.12114 | 0.23806 | -0.11129 | -121.8691 | 121.4183 | -0.011943 | 121.4641 | 121.3859 | -0.032341 | -0.072858 | 0.17405 | -0.39694 | -0.043659 | 0.52202 | 121.425 | 121.8219 | 0.073263 | -0.27609 | 121.625 | 121.5641 | 121.811 | 121.3362 | -0.21869 | 121.5933 | 121.7102 | 121.3609 | 121.5046 | -122.0339
1656.2656 | 121.701 | -121.4767 | 0.19226 | 1.4211e-13 | -0.010359 | 0.021752 | -0.0033377 | -0.0094525 | 0.0095016 | -0.006028 | 0.047105 | 0.038676 | 0.072356 | 0.11903 | 0.060207 | -0.008109 | -0.15884 | -0.081662 | 0.14827 | 0.091937 | 0.33885 | -0.035584 | -120.9456 | 0.018674 | -0.051772 | 0.13029 | 0.24264 | -0.10671 | -121.8691 | 121.4412 | -0.043987 | 121.4686 | 121.3951 | -0.046078 | -0.10032 | 0.14658 | -0.39236 | -0.061968 | 0.53117 | 121.425 | 121.8173 | 0.050376 | -0.29897 | 121.625 | 121.5687 | 121.8156 | 121.3179 | -0.22784 | 121.607 | 121.7194 | 121.37 | 121.4954 | -122.0614
1658.0312 | 121.7972 | -121.4447 | 0.13733 | 1.4211e-13 | -0.010359 | 0.021752 | -0.0037651 | -0.0085979 | 0.0097152 | 0.0016025 | 0.051591 | 0.03419 | 0.071929 | 0.11903 | 0.060207 | -0.008109 | -0.17258 | -0.081662 | 0.15743 | 0.091937 | 0.33885 | -0.026426 | -120.9502 | 0.027831 | -0.1525 | 0.12571 | 0.24264 | -0.11587 | -121.8783 | 121.4183 | 0.020102 | 121.4366 | 121.363 | -0.055236 | -0.045392 | 0.20152 | -0.43356 | -0.011615 | 0.49455 | 121.2922 | 121.7258 | 0.10531 | -0.2532 | 121.6021 | 121.5366 | 121.7835 | 121.2721 | -0.16376 | 121.5704 | 121.6873 | 121.3288 | 121.4725 | -122.0156
1659.7188 | 121.7377 | -121.5134 | 0.15564 | 1.4211e-13 | -0.010359 | 0.022393 | -0.0033377 | -0.0090251 | 0.0095016 | -0.006028 | -0.0043817 | -0.0034143 | 0.074279 | 0.027151 | 0.060635 | -0.003531 | -0.1909 | -0.072505 | 0.15743 | 0.091937 | 0.348 | -0.021847 | -120.9822 | 0.041567 | -121.0076 | 0.13487 | 0.24264 | -0.10671 | -121.9057 | 121.4915 | 0.001791 | 121.5098 | 121.4409 | -0.050658 | -0.063703 | 0.19236 | -0.39237 | -0.020769 | 0.53116 | 0.50582 | 0.89819 | 0.086997 | -0.26235 | 121.6708 | 121.6053 | 121.8614 | 121.3225 | -0.17749 | 121.6482 | 121.756 | 121.4067 | 121.5549 | -122.0614
1661.4688 | 121.8109 | -121.4676 | 0.15564 | 1.4211e-13 | -0.010573 | 0.021539 | -0.0033377 | -0.0092389 | 0.010356 | -0.013659 | -0.0041681 | -0.0032007 | 0.074279 | 0.027365 | 0.05978 | -0.003531 | -0.21379 | -0.072505 | 0.16201 | 0.096516 | 0.33885 | -0.118 | -120.9776 | 0.046146 | -121.0945 | 0.13029 | 0.25637 | -0.092979 | -121.9241 | 121.3496 | 0.006369 | 121.4641 | 121.3951 | 0.045499 | -0.059124 | 0.18321 | -0.45647 | -0.025347 | 0.48997 | 0.37304 | 0.82951 | 0.10073 | -0.24862 | 121.6296 | 121.5641 | 121.8064 | 121.2538 | -0.27364 | 121.5979 | 121.724 | 121.3746 | 121.5137 | -122.0797
1663.2031 | 121.7697 | -121.4905 | 0.16937 | 1.4211e-13 | -0.010573 | 0.021752 | -0.0035515 | -0.0090251 | 0.01057 | -0.021289 | -0.0045953 | -0.0029869 | 0.074493 | 0.027365 | 0.059994 | -0.017266 | -0.21837 | -0.072505 | 0.15743 | 0.096516 | 0.33427 | -0.012689 | -120.9776 | 0.036989 | -121.0991 | 0.13487 | 0.24721 | -0.11129 | -121.9241 | 121.4778 | -0.011942 | 121.4732 | 121.418 | -0.059816 | -0.072857 | 0.16489 | -0.43358 | -0.034502 | 0.51285 | 0.39135 | 0.82493 | 0.077842 | -0.28067 | 121.6479 | 121.587 | 121.8247 | 121.2721 | -0.18206 | 121.6253 | 121.7377 | 121.3792 | 121.5275 | -122.0934
1664.9531 | 121.8292 | -121.4813 | 0.14191 | 1.4211e-13 | -0.010786 | 0.021966 | -0.0035515 | -0.0092389 | 0.010143 | -0.006028 | -0.0043817 | -0.0032007 | 0.074706 | 0.027151 | 0.059566 | -0.012688 | -0.24126 | -0.081662 | 0.14827 | 0.091937 | 0.33427 | -0.040163 | -120.9547 | 0.11025 | -120.9663 | 0.18981 | 0.31132 | 0.28247 | -121.8508 | 121.4412 | 0.006367 | 121.4686 | 121.3997 | -0.041499 | -0.04997 | 0.19236 | -0.36947 | 0.047906 | 0.52659 | 0.51498 | 0.88445 | 0.16941 | 0.14056 | 121.6296 | 121.5733 | 121.8156 | 121.2401 | -0.18207 | 121.6711 | 121.7926 | 121.7638 | 121.5916 | -121.9927
1666.625 | 121.6919 | -97.8378 | 23.8266 | 1.4211e-13 | -0.010359 | 0.021966 | -0.0037651 | -0.0090251 | 0.010143 | 0.0016025 | 0.035141 | 0.036967 | 0.07492 | 0.10557 | 0.05978 | 0.001048 | -0.19547 | -0.067927 | 0.13454 | 0.078201 | 0.32053 | -0.012689 | -97.3835 | 23.7501 | 8.0846 | 23.7462 | 23.8774 | 23.5876 | -98.1371 | 97.8251 | -23.6921 | 97.8389 | 97.7699 | -0.055238 | -23.7484 | -23.5061 | -0.29927 | -0.080428 | 0.4543 | 105.9224 | 106.2217 | 0.050784 | -0.23905 | 97.9724 | 97.916 | 98.1584 | 97.6424 | -23.8393 | 121.584 | 121.7152 | 121.4254 | 121.588 | -121.9637
1668.375 | 121.7834 | -97.7737 | 23.8083 | 1.4211e-13 | -0.010359 | 0.021752 | -0.0033377 | -0.0090251 | 0.010143 | -0.006028 | 0.041123 | 0.044232 | 0.074706 | 0.1186 | 0.059566 | 0.001048 | -0.20005 | -0.072505 | 0.13912 | 0.08278 | 0.32511 | -0.012689 | -97.3515 | 23.7455 | 23.817 | 23.7279 | 23.8591 | 23.6013 | -98.1646 | 97.7611 | -23.6692 | 97.7748 | 97.7012 | -0.059816 | -23.7255 | -23.4832 | -0.39083 | -0.080432 | 0.42226 | 121.5908 | 121.9816 | 0.050779 | -0.207 | 97.9129 | 97.8565 | 98.0989 | 97.5737 | -23.821 | 121.5016 | 121.6328 | 121.375 | 121.5193 | -121.9729
1670.125 | 121.7468 | -97.7783 | 23.8495 | 1.4211e-13 | -0.010145 | 0.021752 | -0.0031241 | -0.0092389 | 0.01057 | 0.0092325 | 0.040696 | 0.044232 | 0.075134 | 0.11839 | 0.059353 | 0.001048 | -0.19547 | -0.072505 | 0.14827 | 0.073622 | 0.32511 | -0.012689 | -97.3332 | 23.7547 | 23.8445 | 23.7553 | 23.882 | 23.6562 | -98.1508 | 97.7656 | -23.7012 | 97.7794 | 97.7058 | -0.059816 | -23.7759 | -23.5244 | -0.37252 | -0.094159 | 0.44515 | 121.6228 | 121.9954 | 0.032474 | -0.19325 | 97.9266 | 97.8519 | 98.1034 | 97.5828 | -23.8622 | 121.5336 | 121.6603 | 121.4346 | 121.533 | -122.0003
1671.875 | 121.843 | -97.7371 | 23.8495 | 1.4211e-13 | -0.010359 | 0.021966 | -0.0033377 | -0.0092389 | 0.010356 | 0.0016025 | 0.04091 | 0.044232 | 0.075134 | 0.1186 | 0.059566 | 0.001048 | -0.20921 | -0.067927 | 0.14369 | 0.059885 | 0.32969 | -0.035584 | -97.3149 | 23.7684 | 23.8674 | 23.7691 | 23.8911 | 23.6288 | -98.1371 | 97.7015 | -23.7058 | 97.7382 | 97.6692 | -0.032343 | -23.7896 | -23.5198 | -0.39998 | -0.080423 | 0.42227 | 121.6045 | 122.0045 | 0.041632 | -0.22073 | 97.8808 | 97.797 | 98.0668 | 97.5279 | -23.8851 | 121.5062 | 121.6282 | 121.3659 | 121.5056 | -121.9866
1673.5625 | 121.7468 | -97.7509 | 23.8953 | 1.4211e-13 | -0.010573 | 0.021752 | -0.0033377 | -0.0094525 | 0.01057 | 0.0016025 | 0.040482 | 0.044018 | 0.07492 | 0.11839 | 0.059994 | -0.008109 | -0.20463 | -0.067927 | 0.13912 | 0.073622 | 0.32053 | -0.00811 | -97.3057 | 23.7868 | 23.8811 | 23.7782 | 23.9094 | 23.6425 | -98.1371 | 97.7427 | -23.7561 | 97.7427 | 97.6829 | -0.059817 | -23.8216 | -23.5747 | -0.38625 | -0.11704 | 0.44516 | 121.632 | 122.0182 | 0.014169 | -0.25277 | 97.89 | 97.8245 | 98.0714 | 97.5462 | -23.9034 | 121.5291 | 121.6603 | 121.3934 | 121.5376 | -122.0324
1675.3281 | 121.8292 | -97.7142 | 23.8724 | 1.4211e-13 | -0.010145 | 0.021966 | -0.0031241 | -0.0094525 | 0.010143 | -0.013659 | 0.040696 | 0.044232 | 0.075561 | 0.11839 | 0.059566 | 0.001048 | -0.19547 | -0.067927 | 0.14369 | 0.073622 | 0.32969 | -0.012689 | -97.292 | 23.8142 | 23.904 | 23.8011 | 23.9277 | 23.6379 | -98.1188 | 97.7015 | -23.7287 | 97.7153 | 97.6463 | -0.055238 | -23.7988 | -23.5427 | -0.40455 | -0.071262 | 0.42227 | 121.6183 | 122.0228 | 0.055372 | -0.23446 | 97.8579 | 97.7879 | 98.0439 | 97.5188 | -23.8851 | 121.5153 | 121.642 | 121.3522 | 121.5285 | -121.9912
1677.0938 | 121.8201 | -97.7188 | 23.9227 | 1.4211e-13 | -0.010573 | 0.021966 | -0.0033377 | -0.0094525 | 0.010356 | 0.0092325 | 0.04091 | 0.044018 | 0.075347 | 0.11839 | 0.05978 | 0.010204 | -0.1909 | -0.072505 | 0.13912 | 0.073622 | 0.32053 | -0.00811 | -97.2691 | 23.8417 | 23.9269 | 23.8286 | 23.9644 | 23.6745 | -98.1096 | 97.7107 | -23.7836 | 97.729 | 97.6463 | -0.064395 | -23.8491 | -23.6022 | -0.39082 | -0.094145 | 0.44975 | 121.6457 | 122.0366 | 0.041647 | -0.24818 | 97.8579 | 97.7924 | 98.0393 | 97.5279 | -23.9308 | 121.5474 | 121.6832 | 121.3934 | 121.5605 | -122.0324
1678.8438 | 121.8063 | -121.5042 | 0.17395 | 1.4211e-13 | -0.010359 | 0.021966 | -0.0031241 | -0.0092389 | 0.010356 | -0.006028 | 0.040482 | 0.043804 | 0.075134 | 0.11796 | 0.060207 | 0.001048 | -0.24584 | -0.081662 | 0.16201 | 0.091937 | 0.33427 | -0.017268 | -120.9547 | 0.050725 | -0.019721 | 0.14403 | 0.25637 | 0.2321 | -121.9607 | 121.4869 | -0.011941 | 121.5053 | 121.4225 | -0.064394 | -0.082013 | 0.16032 | -0.45647 | -0.029922 | 0.54948 | 121.4845 | 121.941 | 0.082422 | 0.058152 | 121.6662 | 121.5961 | 121.8385 | 121.2584 | -0.19122 | 121.6482 | 121.7606 | 121.7363 | 121.5549 | -122.1346
1680.5469 | 121.8475 | -121.5179 | 0.16479 | 1.4211e-13 | -0.010573 | 0.021752 | -0.0031241 | -0.0092389 | 0.01057 | -0.006028 | 0.040482 | 0.043591 | 0.075347 | 0.11818 | 0.059994 | -0.008109 | -0.2321 | -0.077084 | 0.14827 | 0.091937 | 0.33427 | -0.012689 | -120.9868 | 0.036989 | -0.028879 | 0.13029 | 0.23806 | 0.21379 | -121.9836 | 121.5053 | -0.016521 | 121.5098 | 121.4409 | -0.064395 | -0.072858 | 0.16947 | -0.46564 | -0.034502 | 0.53116 | 121.4891 | 121.9547 | 0.073263 | 0.048993 | 121.6662 | 121.6099 | 121.8522 | 121.2858 | -0.17748 | 121.6482 | 121.756 | 121.7317 | 121.5549 | -122.1484
1682.2969 | 121.7834 | -121.6003 | 0.17395 | 1.4211e-13 | -0.010145 | 0.021539 | -0.0033377 | -0.0090251 | 0.010143 | 0.0016025 | 0.040055 | 0.043377 | 0.075134 | 0.11796 | 0.05978 | 0.001048 | -0.24126 | -0.077084 | 0.15285 | 0.096516 | 0.34342 | -0.012689 | -120.9868 | 0.023253 | -0.028879 | 0.13029 | 0.24721 | -0.10671 | -121.9882 | 121.5877 | -0.021098 | 121.6014 | 121.5233 | -0.064395 | -0.077434 | 0.16947 | -0.38782 | -0.043657 | 0.61356 | 121.5715 | 121.9593 | 0.073265 | -0.28066 | 121.7532 | 121.6969 | 121.9438 | 121.3591 | -0.18664 | 121.7306 | 121.8476 | 121.4936 | 121.6236 | -122.1621
1684.0625 | 121.9208 | -121.5408 | 0.13275 | 1.4211e-13 | -0.010359 | 0.021752 | -0.0033377 | -0.0092389 | 0.010143 | 0.0092325 | 0.040482 | 0.043804 | 0.07492 | 0.11796 | 0.059994 | 0.005626 | -0.24584 | -0.081662 | 0.15743 | 0.091937 | 0.32969 | -0.012689 | -120.9547 | 0.027831 | -0.033458 | 0.12571 | 0.24264 | -0.092979 | -121.9927 | 121.5281 | 0.02468 | 121.5465 | 121.4592 | -0.068973 | -0.040814 | 0.19694 | -0.4519 | -0.007037 | 0.5861 | 121.5074 | 121.9593 | 0.10989 | -0.22573 | 121.6983 | 121.6328 | 121.8705 | 121.295 | -0.14544 | 121.6665 | 121.7835 | 121.4479 | 121.5687 | -122.1255
1685.8125 | 121.8384 | -121.5912 | 0.16937 | 1.4211e-13 | -0.010786 | 0.021752 | -0.0033377 | -0.0090251 | 0.010143 | -0.006028 | 0.040055 | 0.043377 | 0.07492 | 0.11775 | 0.05978 | 0.001048 | -0.24126 | -0.081662 | 0.14827 | 0.087359 | 0.33427 | -0.012689 | -120.973 | 0.027831 | -0.028879 | 0.12571 | 0.24264 | -0.11129 | -122.0065 | 121.5785 | -0.021099 | 121.5922 | 121.5095 | -0.068973 | -0.082014 | 0.16489 | -0.41529 | -0.043659 | 0.61814 | 121.5623 | 121.9776 | 0.073264 | -0.28067 | 121.7395 | 121.6785 | 121.9255 | 121.3499 | -0.18206 | 121.7169 | 121.8338 | 121.4799 | 121.619 | -122.1758
1687.5781 | 121.8018 | -119.3665 | 2.4033 | 1.4211e-13 | -0.010573 | 0.02218 | -0.0033377 | -0.0092389 | 0.010356 | -0.006028 | 0.039841 | 0.043804 | 0.074706 | 0.11818 | 0.060207 | 0.001048 | -0.24126 | -0.072505 | 0.15285 | 0.091937 | 0.33427 | -0.012689 | -118.6791 | 2.2806 | 2.2788 | 2.4058 | 2.5228 | 2.2925 | -119.7079 | 119.3538 | -2.2504 | 119.3675 | 119.2939 | -0.059816 | -2.3113 | -2.069 | -0.34145 | 0.002546 | 0.68734 | 121.6452 | 121.9867 | 0.11952 | -0.11079 | 119.5193 | 119.4584 | 119.7007 | 119.1252 | -2.4159 | 121.7723 | 121.8892 | 121.6589 | 121.647 | -122.1112
1689.2656 | 121.8338 | -119.0918 | 2.6779 | 1.4211e-13 | -0.010359 | 0.02218 | -0.0033377 | -0.0090251 | 0.010356 | -0.006028 | 0.039841 | 0.043163 | 0.07492 | 0.11775 | 0.059994 | -0.003531 | -0.22295 | -0.072505 | 0.14827 | 0.08278 | 0.33885 | -0.044742 | -118.5143 | 2.4545 | 2.4436 | 2.5752 | 2.6876 | 2.5763 | -119.5431 | 119.0471 | -2.5296 | 119.0883 | 119.0193 | -0.027763 | -2.5951 | -2.3391 | -0.45127 | -0.10271 | 0.57752 | 121.5354 | 121.9867 | 0.009693 | -0.10157 | 119.2401 | 119.1746 | 119.4306 | 118.8689 | -2.7227 | 121.667 | 121.7794 | 121.6681 | 121.5463 | -122.221
1691.0156 | 121.7606 | -97.7463 | 24.0509 | 1.4211e-13 | -0.010573 | 0.022393 | -0.0031241 | -0.0092389 | 0.010356 | -0.006028 | 0.040482 | 0.043804 | 0.07492 | 0.11796 | 0.059994 | 0.010204 | -0.18632 | -0.05877 | 0.13912 | 0.073622 | 0.32053 | -0.00811 | -97.1454 | 23.9653 | 24.0597 | 23.9522 | 24.088 | 23.8485 | -98.0364 | 97.7382 | -23.9118 | 97.7565 | 97.6875 | -0.05066 | -23.9773 | -23.7304 | -0.29009 | -0.0987 | 0.60084 | 121.806 | 122.0961 | 0.037096 | -0.20237 | 97.8854 | 97.8199 | 98.0668 | 97.56 | -24.059 | 121.6985 | 121.8343 | 121.5948 | 121.7116 | -122.0873
1692.6875 | 121.9025 | -97.673 | 24.0005 | 1.4211e-13 | -0.010359 | 0.02218 | -0.0031241 | -0.0094525 | 0.010356 | -0.006028 | 0.040055 | 0.043591 | 0.075134 | 0.11711 | 0.059994 | 0.001048 | -0.19547 | -0.045036 | 0.13912 | 0.064464 | 0.31595 | -0.012689 | -97.15 | 23.9562 | 24.0506 | 23.943 | 24.0788 | 23.8394 | -98.0501 | 97.6603 | -23.8614 | 97.6741 | 97.628 | -0.032347 | -23.9361 | -23.6846 | -0.37707 | -0.057503 | 0.52302 | 121.7236 | 122.1007 | 0.078292 | -0.16117 | 97.8122 | 97.7375 | 97.989 | 97.4776 | -24.0132 | 121.6161 | 121.7519 | 121.5124 | 121.6292 | -122.0507
1694.4531 | 121.9437 | -121.5591 | 0.14191 | 1.4211e-13 | -0.010359 | 0.021966 | -0.0033377 | -0.0090251 | 0.01057 | -0.006028 | 0.040055 | 0.043377 | 0.07492 | 0.11732 | 0.060207 | 0.005626 | -0.23668 | -0.054192 | 0.15743 | 0.091937 | 0.33885 | 0.001048 | -120.9776 | 0.041567 | -0.028879 | 0.12571 | 0.24264 | 0.21837 | -122.0339 | 121.5602 | 0.015524 | 121.5648 | 121.505 | -0.05524 | -0.04997 | 0.19694 | -0.4748 | -0.016193 | 0.58152 | 121.5303 | 122.0051 | 0.10073 | 0.076459 | 121.7166 | 121.6511 | 121.898 | 121.3225 | -0.14086 | 121.6849 | 121.8018 | 121.7775 | 121.6007 | -122.1759
1696.1562 | 121.9162 | -121.582 | 0.15564 | 1.4211e-13 | -0.010359 | 0.02218 | -0.0035515 | -0.0094525 | 0.010356 | 0.0016025 | 0.039841 | 0.043163 | 0.074493 | 0.11754 | 0.060207 | 0.014783 | -0.22752 | -0.049614 | 0.15285 | 0.087359 | 0.34342 | -0.00811 | -120.9685 | 0.046146 | -0.0243 | 0.12571 | 0.23348 | -0.10214 | -122.0523 | 121.5739 | -0.002788 | 121.5968 | 121.5324 | -0.041504 | -0.068281 | 0.18778 | -0.47023 | -0.029926 | 0.61356 | 121.5577 | 122.028 | 0.077839 | -0.25778 | 121.7349 | 121.6694 | 121.9255 | 121.3545 | -0.16375 | 121.7077 | 121.8155 | 121.4799 | 121.6282 | -122.2079
1697.9062 | 121.9803 | -121.6232 | 0.13275 | 1.4211e-13 | -0.010145 | 0.022393 | -0.0033377 | -0.0094525 | 0.010784 | 0.0016025 | 0.039628 | 0.043377 | 0.074706 | 0.11775 | 0.05978 | 0.014783 | -0.24126 | -0.05877 | 0.15743 | 0.087359 | 0.33885 | -0.003531 | -120.9959 | 0.03241 | -0.0243 | 0.11656 | 0.23348 | -0.11129 | -122.0523 | 121.6197 | 0.02468 | 121.638 | 121.5645 | -0.055239 | -0.045392 | 0.20609 | -0.42903 | -0.016194 | 0.62729 | 121.5989 | 122.028 | 0.10073 | -0.24404 | 121.7807 | 121.7106 | 121.9621 | 121.382 | -0.13628 | 121.7398 | 121.8567 | 121.5119 | 121.6556 | -122.185
1699.5938 | 121.8567 | -121.6461 | 0.17395 | 1.4211e-13 | -0.010359 | 0.021966 | -0.0035515 | -0.0090251 | 0.010356 | -0.006028 | 0.039414 | 0.043377 | 0.075561 | 0.11754 | 0.059994 | 0.019361 | -0.23668 | -0.054192 | 0.15285 | 0.087359 | 0.33427 | -0.00811 | -120.9959 | 0.027831 | -0.038036 | 0.12571 | 0.23806 | -0.11129 | -122.066 | 121.638 | -0.021098 | 121.6655 | 121.5919 | -0.046082 | -0.086591 | 0.16032 | -0.41988 | -0.048236 | 0.65018 | 121.6081 | 122.028 | 0.064108 | -0.28524 | 121.799 | 121.7335 | 121.9804 | 121.4094 | -0.18206 | 121.7718 | 121.8842 | 121.5348 | 121.6739 | -122.2399
1701.3594 | 121.8521 | -121.6553 | 0.17853 | 1.4211e-13 | -0.010145 | 0.021966 | -0.0031241 | -0.0090251 | 0.010356 | 0.0092325 | 0.039628 | 0.043377 | 0.075134 | 0.11668 | 0.059994 | 0.010204 | -0.2321 | -0.063349 | 0.15743 | 0.087359 | 0.33427 | -0.003531 | -121.0005 | 0.023253 | -0.028879 | 0.12114 | 0.23348 | -0.11587 | -122.066 | 121.6517 | -0.021097 | 121.6655 | 121.5919 | -0.059818 | -0.091169 | 0.15574 | -0.41073 | -0.057392 | 0.65475 | 121.6264 | 122.0371 | 0.054951 | -0.2944 | 121.8127 | 121.7426 | 121.9895 | 121.4232 | -0.18206 | 121.7764 | 121.8888 | 121.5394 | 121.6785 | -122.2445
1703.125 | 121.907 | -121.669 | 0.16937 | 1.4211e-13 | -0.010145 | 0.02218 | -0.0031241 | -0.0094525 | 0.010784 | 0.0016025 | 0.040269 | 0.042522 | 0.075347 | 0.11732 | 0.059994 | 0.010204 | -0.21837 | -0.054192 | 0.15285 | 0.087359 | 0.33427 | 0.005627 | -120.9959 | 0.027831 | -0.038036 | 0.12571 | 0.23806 | -0.11587 | -122.0752 | 121.6746 | -0.016521 | 121.6792 | 121.6148 | -0.059819 | -0.082014 | 0.16489 | -0.40615 | -0.043659 | 0.67307 | 121.631 | 122.0371 | 0.068685 | -0.28524 | 121.8219 | 121.7564 | 122.0033 | 121.4506 | -0.16375 | 121.7947 | 121.9071 | 121.5531 | 121.6968 | -122.2445
1704.875 | 121.8567 | -121.6782 | 0.20599 | 1.4211e-13 | -0.010359 | 0.021966 | -0.0031241 | -0.0094525 | 0.010143 | -0.006028 | 0.039628 | 0.042736 | 0.074706 | 0.11732 | 0.059994 | 0.023939 | -0.20463 | -0.045036 | 0.15743 | 0.091937 | 0.33885 | -0.003531 | -120.9776 | 0.041567 | -0.033458 | 0.13029 | 0.24264 | -0.10671 | -122.0889 | 121.6746 | -0.048563 | 121.7021 | 121.6331 | -0.041505 | -0.11406 | 0.13285 | -0.41073 | -0.075701 | 0.70054 | 121.6447 | 122.0554 | 0.036643 | -0.31271 | 121.8356 | 121.7701 | 122.017 | 121.4735 | -0.20953 | 121.8085 | 121.9208 | 121.5714 | 121.7197 | -122.2949
1706.5781 | 121.9391 | -121.6599 | 0.15564 | 1.4211e-13 | -0.010145 | 0.021752 | -0.0033377 | -0.0092389 | 0.010143 | -0.006028 | 0.039414 | 0.04295 | 0.07492 | 0.11732 | 0.060207 | 0.019361 | -0.19547 | -0.049614 | 0.15285 | 0.091937 | 0.32969 | -0.00811 | -120.941 | 0.023253 | -0.028879 | 0.13029 | 0.24721 | -0.10214 | -122.0935 | 121.6517 | -0.002788 | 121.6792 | 121.6102 | -0.041504 | -0.063703 | 0.17405 | -0.43362 | -0.025347 | 0.71886 | 121.631 | 122.0646 | 0.091575 | -0.25778 | 121.8127 | 121.7518 | 121.9895 | 121.4644 | -0.16375 | 121.7901 | 121.9071 | 121.5577 | 121.6831 | -122.2491
1708.3281 | 121.9528 | -121.5317 | 0.25177 | 1.4211e-13 | -0.010573 | 0.021752 | -0.0033377 | -0.0092389 | 0.010356 | -0.013659 | 0.040055 | 0.042522 | 0.075134 | 0.11689 | 0.059994 | 0.023939 | -0.19547 | -0.045036 | 0.15285 | 0.08278 | 0.33427 | 0.001048 | -120.8677 | 0.064461 | 0.007751 | 0.15776 | 0.27926 | -0.042614 | -122.0523 | 121.5327 | -0.098918 | 121.5556 | 121.4866 | -0.046084 | -0.16899 | 0.082497 | -0.52058 | -0.094006 | 0.66394 | 121.5394 | 122.06 | 0.027495 | -0.29438 | 121.6845 | 121.6145 | 121.8659 | 121.3362 | -0.25072 | 121.6894 | 121.8109 | 121.4891 | 121.5961 | -122.304
1710.0156 | 121.962 | -121.582 | 0.21973 | 1.4211e-13 | -0.010145 | 0.021966 | -0.0033377 | -0.0092389 | 0.01057 | 0.0092325 | 0.0439 | 0.038676 | 0.075347 | 0.11668 | 0.060207 | 0.023939 | -0.1909 | -0.045036 | 0.15743 | 0.091937 | 0.33885 | -0.003531 | -120.8174 | 0.078197 | 0.030644 | 0.18066 | 0.28842 | -0.028878 | -122.0431 | 121.5785 | -0.062296 | 121.606 | 121.537 | -0.041505 | -0.12779 | 0.11912 | -0.46107 | -0.039071 | 0.76466 | 121.6127 | 122.0737 | 0.068696 | -0.24861 | 121.7395 | 121.674 | 121.9209 | 121.3911 | -0.22326 | 121.7627 | 121.8705 | 121.5532 | 121.6602 | -122.2628
1711.7812 | 121.9437 | -121.6644 | 0.1831 | 1.4211e-13 | -0.010359 | 0.02218 | -0.0033377 | -0.0092389 | 0.010356 | 0.0092325 | 0.040269 | 0.042095 | 0.075134 | 0.11647 | 0.059994 | 0.014783 | -0.18174 | -0.049614 | 0.15285 | 0.087359 | 0.32969 | 0.001048 | -120.8677 | 0.046146 | -0.010564 | 0.15318 | 0.26095 | -0.10214 | -122.0843 | 121.6655 | -0.030253 | 121.6792 | 121.6148 | -0.050662 | -0.095746 | 0.14658 | -0.41989 | -0.02992 | 0.79669 | 121.6539 | 122.0738 | 0.077846 | -0.28524 | 121.8173 | 121.7518 | 121.9941 | 121.4827 | -0.18206 | 121.8176 | 121.9254 | 121.5623 | 121.7106 | -122.2674
1713.5469 | 121.8979 | -121.5637 | 0.34332 | 1.4211e-13 | -0.010359 | 0.02218 | -0.0033377 | -0.0092389 | 0.010784 | 0.0092325 | 0.039841 | 0.042736 | 0.075134 | 0.11647 | 0.059994 | 0.014783 | -0.18174 | -0.045036 | 0.15743 | 0.08278 | 0.32969 | 0.005627 | -120.7121 | 0.16519 | 0.12222 | 0.27223 | 0.38457 | 0.1909 | -121.9653 | 121.5693 | -0.18589 | 121.5785 | 121.5187 | -0.050663 | -0.26054 | -0.013634 | -0.40154 | -0.071097 | 0.85166 | 121.6859 | 122.0875 | 0.04125 | -0.15243 | 121.7212 | 121.6465 | 121.8934 | 121.382 | -0.3377 | 121.8359 | 121.9483 | 121.7546 | 121.7289 | -122.3086
1715.3125 | 122.0215 | -119.3024 | 2.4582 | 1.4211e-13 | -0.0099315 | 0.021539 | -0.0035515 | -0.0096661 | 0.010356 | -0.013659 | 0.039628 | 0.042095 | 0.075347 | 0.11668 | 0.060207 | 0.023939 | -0.168 | -0.045036 | 0.14369 | 0.087359 | 0.32969 | 0.001048 | -118.4593 | 2.4545 | 2.4024 | 2.534 | 2.6464 | 2.6313 | -119.6804 | 119.3034 | -2.3145 | 119.3263 | 119.2573 | -0.046084 | -2.3708 | -2.1285 | -0.37807 | 0.075812 | 0.84303 | 121.7048 | 122.0829 | 0.18821 | 0.1731 | 119.4461 | 119.3897 | 119.6321 | 119.1344 | -2.4571 | 121.8364 | 121.9488 | 121.9337 | 121.7569 | -122.1386
1717.0625 | 121.9437 | -118.8629 | 2.9709 | 1.4211e-13 | -0.010145 | 0.021752 | -0.0035515 | -0.0092389 | 0.01057 | -0.006028 | 0.039841 | 0.042522 | 0.07492 | 0.11647 | 0.059994 | 0.055988 | -0.058115 | 0.000747 | 0.15743 | 0.1011 | 0.34342 | 0.014784 | -118.061 | 2.8163 | 2.7596 | 2.8865 | 2.999 | 2.8419 | -119.3233 | 118.8777 | -2.8135 | 118.9189 | 118.8637 | -0.014037 | -2.8698 | -2.6275 | -0.46037 | -0.084339 | 0.80193 | 121.6225 | 122.0828 | 0.028069 | -0.12898 | 119.0203 | 118.964 | 119.2063 | 118.8048 | -2.9561 | 121.7495 | 121.8619 | 121.7048 | 121.6792 | -122.2942
1718.8125 | 122.0306 | -118.6707 | 3.1265 | 1.4211e-13 | -0.010145 | 0.021966 | -0.0033377 | -0.0094525 | 0.010143 | 0.0016025 | 0.039841 | 0.042522 | 0.075134 | 0.11647 | 0.059994 | 0.055988 | -0.062694 | 0.000747 | 0.15743 | 0.08278 | 0.33427 | 0.023942 | -117.8733 | 3.0086 | 2.9931 | 3.1155 | 3.2233 | 2.9884 | -119.0943 | 118.6946 | -2.9691 | 118.7266 | 118.6714 | -0.023195 | -3.0437 | -2.7923 | -0.42369 | -0.011054 | 0.79739 | 121.6637 | 122.0874 | 0.096781 | -0.1381 | 118.8281 | 118.7534 | 119.0049 | 118.608 | -3.1026 | 121.7861 | 121.894 | 121.6591 | 121.6792 | -122.2209
1720.5156 | 121.9666 | -121.6965 | 0.17395 | 1.4211e-13 | -0.010573 | 0.021966 | -0.0035515 | -0.0090251 | 0.010356 | -0.013659 | 0.039414 | 0.042736 | 0.075347 | 0.11647 | 0.060207 | 0.046831 | -0.053537 | 0.000747 | 0.15743 | 0.091937 | 0.34342 | 0.010206 | -120.8815 | 0.03241 | -0.0243 | 0.12571 | 0.24264 | -0.11129 | -122.1255 | 121.7067 | -0.016519 | 121.7433 | 121.6972 | -0.009459 | -0.082013 | 0.16947 | -0.42905 | -0.048236 | 0.815 | 121.6722 | 122.1012 | 0.068687 | -0.28524 | 121.8539 | 121.7884 | 122.0399 | 121.6429 | -0.16374 | 121.8222 | 121.9391 | 121.5852 | 121.7289 | -122.2995
1722.2656 | 121.9482 | -121.6919 | 0.16479 | 1.4211e-13 | -0.010359 | 0.021966 | -0.0031241 | -0.0094525 | 0.01057 | -0.006028 | 0.039414 | 0.042309 | 0.075134 | 0.11625 | 0.059994 | 0.055988 | -0.021486 | 0.014482 | 0.16659 | 0.1011 | 0.348 | 0.023942 | -120.8769 | 0.018674 | -0.033458 | 0.11656 | 0.22432 | -0.11587 | -122.1301 | 121.7158 | 0.001792 | 121.7479 | 121.7064 | -0.00946 | -0.0637 | 0.18321 | -0.43821 | -0.048238 | 0.815 | 121.6584 | 122.0966 | 0.059527 | -0.28067 | 121.8585 | 121.793 | 122.0399 | 121.6704 | -0.14085 | 121.8085 | 121.9162 | 121.576 | 121.7106 | -122.2949
1724.0156 | 122.0078 | -121.7102 | 0.14648 | 1.4211e-13 | -0.010359 | 0.021966 | -0.0033377 | -0.0090251 | 0.010356 | -0.006028 | 0.040269 | 0.041454 | 0.07492 | 0.11604 | 0.060421 | 0.055988 | -0.016908 | 0.01906 | 0.16659 | 0.1011 | 0.34342 | 0.028521 | -120.8265 | 0.027831 | -0.033458 | 0.11656 | 0.2289 | -0.11587 | -122.1393 | 121.7387 | 0.020103 | 121.7662 | 121.7293 | -0.009461 | -0.045389 | 0.19694 | -0.42905 | -0.029927 | 0.88368 | 121.6767 | 122.1058 | 0.082417 | -0.26236 | 121.8768 | 121.8113 | 122.0536 | 121.6933 | -0.11796 | 121.8268 | 121.9391 | 121.5943 | 121.738 | -122.2857
1725.7031 | 122.0535 | -121.6736 | 0.13275 | 1.4211e-13 | -0.010145 | 0.021966 | -0.0033377 | -0.0090251 | 0.010143 | -0.013659 | 0.039841 | 0.041668 | 0.07492 | 0.11647 | 0.060421 | 0.055988 | -0.030644 | 0.009904 | 0.16201 | 0.1011 | 0.34342 | 0.010206 | -120.8128 | 0.03241 | -0.033458 | 0.12114 | 0.22432 | -0.11587 | -122.1438 | 121.6838 | 0.029258 | 121.7296 | 121.6835 | -0.000302 | -0.031656 | 0.21067 | -0.47025 | -0.011615 | 0.86079 | 121.6401 | 122.1104 | 0.091571 | -0.24862 | 121.8356 | 121.7747 | 122.017 | 121.6429 | -0.12255 | 121.7947 | 121.8979 | 121.5577 | 121.706 | -122.2766
1727.4688 | 122.0398 | -121.6965 | 0.14191 | 1.4211e-13 | -0.010145 | 0.021752 | -0.0033377 | -0.0090251 | 0.010143 | 0.0016025 | 0.039414 | 0.042736 | 0.07492 | 0.11604 | 0.060635 | 0.055988 | -0.026065 | 0.014482 | 0.16659 | 0.1011 | 0.348 | 0.023942 | -120.8586 | 0.023253 | -0.033458 | 0.11198 | 0.23348 | -0.11129 | -122.1393 | 121.7204 | 0.02468 | 121.7525 | 121.711 | -0.00946 | -0.040812 | 0.2061 | -0.44279 | -0.029928 | 0.83789 | 121.663 | 122.1058 | 0.091572 | -0.2532 | 121.8631 | 121.7976 | 122.0445 | 121.6704 | -0.11797 | 121.8085 | 121.93 | 121.5852 | 121.7197 | -122.2812
1729.2344 | 122.0215 | -121.6782 | 0.1236 | 1.4211e-13 | -0.010573 | 0.02218 | -0.0031241 | -0.0094525 | 0.010356 | -0.006028 | 0.043687 | 0.038249 | 0.074706 | 0.11604 | 0.060207 | 0.055988 | -0.035222 | 0.005325 | 0.16201 | 0.091937 | 0.33885 | 0.0331 | -120.9227 | 0.023253 | -0.028879 | 0.12571 | 0.23348 | -0.11587 | -122.1438 | 121.7113 | 0.038413 | 121.7341 | 121.6835 | -0.027775 | -0.031659 | 0.21525 | -0.46568 | 0.002118 | 0.75548 | 121.6493 | 122.115 | 0.10988 | -0.23947 | 121.8402 | 121.7701 | 122.017 | 121.6429 | -0.090496 | 121.8039 | 121.9116 | 121.5623 | 121.7014 | -122.2674
1731 | 122.0123 | -121.6873 | 0.16022 | 1.4211e-13 | -0.0099315 | 0.021752 | -0.0033377 | -0.0088115 | 0.01057 | 0.0016025 | 0.044114 | 0.037608 | 0.075134 | 0.11604 | 0.060421 | 0.065145 | -0.030644 | 0.009904 | 0.15743 | 0.096516 | 0.33885 | 0.023942 | -120.9135 | 0.03241 | -0.028879 | 0.11656 | 0.22432 | -0.11129 | -122.153 | 121.7113 | -0.002786 | 121.7525 | 121.6972 | -0.014038 | -0.063701 | 0.17863 | -0.46568 | -0.04366 | 0.77379 | 121.6584 | 122.1241 | 0.064105 | -0.27151 | 121.8447 | 121.7838 | 122.0262 | 121.6567 | -0.13628 | 121.8039 | 121.9116 | 121.576 | 121.7197 | -122.3132
1732.7031 | 121.9437 | -121.7285 | 0.16937 | 1.4211e-13 | -0.010359 | 0.021966 | -0.0031241 | -0.0094525 | 0.01057 | -0.013659 | 0.0439 | 0.037822 | 0.07492 | 0.11604 | 0.060207 | 0.065145 | -0.026065 | 0.009904 | 0.15285 | 0.087359 | 0.348 | 0.028521 | -120.9639 | 0.03241 | -0.033458 | 0.11656 | 0.2289 | -0.11587 | -122.1622 | 121.757 | -0.016521 | 121.7937 | 121.7384 | -0.018617 | -0.082014 | 0.17863 | -0.43364 | -0.052816 | 0.76463 | 121.6951 | 122.1287 | 0.059528 | -0.28524 | 121.8814 | 121.8159 | 122.0765 | 121.7025 | -0.14085 | 121.8451 | 121.9574 | 121.6126 | 121.7609 | -122.3315
1734.4531 | 121.8475 | -121.8063 | 0.1831 | 1.4211e-13 | -0.010145 | 0.021966 | -0.0035515 | -0.0090251 | 0.01057 | 0.0016025 | 0.044328 | 0.036967 | 0.075134 | 0.11625 | 0.059994 | 0.083459 | 0.033457 | 0.032795 | 0.17117 | 0.11025 | 0.35258 | 0.11552 | -120.9685 | 0.027831 | -0.038036 | 0.11198 | 0.2289 | -0.11129 | -122.1347 | 121.9219 | -0.011939 | 121.8898 | 121.8391 | -0.082726 | -0.072852 | 0.16948 | -0.32835 | -0.071126 | 0.83787 | 121.7683 | 122.0966 | 0.045796 | -0.2944 | 121.9775 | 121.9166 | 122.1589 | 121.8398 | -0.067584 | 121.9183 | 122.0352 | 121.695 | 121.8342 | -122.3178
1736.2188 | 121.9025 | -121.8292 | 0.16479 | 1.4211e-13 | -0.010359 | 0.02218 | -0.0035515 | -0.0088115 | 0.01057 | -0.006028 | 0.044969 | 0.036113 | 0.075134 | 0.11583 | 0.060207 | 0.07888 | 0.033457 | 0.037373 | 0.16659 | 0.1011 | 0.33885 | 0.10178 | -120.9822 | 0.023253 | -0.033458 | 0.10282 | 0.22432 | -0.10671 | -122.185 | 121.931 | 0.001792 | 121.9081 | 121.8666 | -0.064411 | -0.0637 | 0.17405 | -0.35582 | -0.061973 | 0.84702 | 121.7958 | 122.1516 | 0.059527 | -0.27151 | 121.9958 | 121.9303 | 122.1681 | 121.8627 | -0.063011 | 121.932 | 122.0535 | 121.7225 | 121.8525 | -122.3498
1737.9688 | 122.0627 | -121.7377 | 0.14191 | 1.4211e-13 | -0.010359 | 0.02218 | -0.0031241 | -0.0092389 | 0.010143 | -0.006028 | 0.043687 | 0.037822 | 0.07492 | 0.11604 | 0.060207 | 0.07888 | 0.033457 | 0.037373 | 0.16201 | 0.1011 | 0.348 | 0.10636 | -120.9593 | 0.023253 | -0.038036 | 0.11198 | 0.22432 | -0.12045 | -122.1942 | 121.844 | 0.020102 | 121.8166 | 121.775 | -0.06899 | -0.040812 | 0.2061 | -0.45653 | -0.029928 | 0.77836 | 121.6996 | 122.1562 | 0.082415 | -0.26236 | 121.8997 | 121.8388 | 122.0857 | 121.7711 | -0.035544 | 121.8497 | 121.962 | 121.6172 | 121.7609 | -122.3361
1739.6406 | 121.9482 | -121.7789 | 0.17395 | 1.4211e-13 | -0.010145 | 0.021966 | -0.0033377 | -0.0090251 | 0.010356 | -0.006028 | 0.0439 | 0.037395 | 0.075134 | 0.11561 | 0.060207 | 0.083459 | 0.028878 | 0.037373 | 0.16659 | 0.1011 | 0.348 | 0.088047 | -120.9593 | 0.023253 | -0.033458 | 0.1074 | 0.23348 | -0.12045 | -122.1942 | 121.8669 | -0.007363 | 121.8623 | 121.8162 | -0.050674 | -0.072855 | 0.17405 | -0.41534 | -0.066549 | 0.81956 | 121.7454 | 122.1607 | 0.059529 | -0.2944 | 121.9455 | 121.88 | 122.1269 | 121.8077 | -0.085903 | 121.8863 | 122.0123 | 121.6584 | 121.8021 | -122.3682
1741.4219 | 122.0627 | -121.7331 | 0.12817 | 1.4211e-13 | -0.010145 | 0.02218 | -0.0031241 | -0.0088115 | 0.010356 | -0.006028 | 0.052446 | 0.029062 | 0.075134 | 0.11583 | 0.060207 | 0.088037 | 0.028878 | 0.032795 | 0.16659 | 0.10567 | 0.34342 | 0.11552 | -120.9685 | 0.018674 | -0.028879 | 0.1074 | 0.23348 | -0.11587 | -122.2079 | 121.8486 | 0.038413 | 121.8211 | 121.7659 | -0.082726 | -0.0225 | 0.21525 | -0.47485 | -0.020773 | 0.76463 | 121.7042 | 122.1791 | 0.1053 | -0.24405 | 121.8997 | 121.8388 | 122.0765 | 121.762 | -0.012653 | 121.8405 | 121.9666 | 121.6172 | 121.7518 | -122.3361
1743.1094 | 122.081 | -121.7331 | 0.1236 | 1.4211e-13 | -0.0099315 | 0.02218 | -0.0033377 | -0.0090251 | 0.010143 | -0.006028 | 0.045182 | 0.035899 | 0.075134 | 0.1154 | 0.060207 | 0.07888 | 0.033457 | 0.041952 | 0.16201 | 0.1011 | 0.35716 | 0.11094 | -121.0417 | 0.018674 | -0.042615 | 0.11656 | 0.21974 | -0.11587 | -122.2171 | 121.844 | 0.038413 | 121.812 | 121.775 | -0.06899 | -0.022501 | 0.23356 | -0.48401 | -0.007039 | 0.69137 | 121.6905 | 122.1745 | 0.096148 | -0.23947 | 121.8951 | 121.8342 | 122.0903 | 121.7665 | -0.012654 | 121.8496 | 121.9528 | 121.6172 | 121.7518 | -122.3407
1744.8594 | 121.9666 | -121.8201 | 0.15564 | 1.4211e-13 | -0.010359 | 0.022393 | -0.0031241 | -0.0092389 | 0.010143 | -0.006028 | 0.043687 | 0.037608 | 0.075347 | 0.11561 | 0.060207 | 0.083459 | 0.038035 | 0.041952 | 0.16659 | 0.10567 | 0.34342 | 0.11552 | -120.9502 | 0.018674 | -0.038036 | 0.1074 | 0.21974 | -0.11129 | -122.2217 | 121.9356 | 0.010947 | 121.9035 | 121.862 | -0.073569 | -0.049966 | 0.18778 | -0.40161 | -0.048239 | 0.86992 | 121.782 | 122.1836 | 0.064104 | -0.26693 | 121.9867 | 121.9257 | 122.1635 | 121.8581 | -0.040119 | 121.9275 | 122.0398 | 121.7088 | 121.8387 | -122.3773
1746.5781 | 122.0993 | -121.7743 | 0.14648 | 1.4211e-13 | -0.010145 | 0.021752 | -0.0031241 | -0.0092389 | 0.010356 | -0.006028 | 0.046464 | 0.034403 | 0.07492 | 0.11561 | 0.060421 | 0.083459 | 0.038035 | 0.037373 | 0.16201 | 0.1011 | 0.348 | 0.11552 | -120.9364 | 0.027831 | -0.038036 | 0.11198 | 0.21974 | -0.11587 | -122.2308 | 121.8898 | 0.015525 | 121.8578 | 121.8117 | -0.078148 | -0.045389 | 0.20152 | -0.45654 | -0.034505 | 0.83788 | 121.7363 | 122.1928 | 0.07326 | -0.26236 | 121.9363 | 121.8754 | 122.1223 | 121.8123 | -0.030963 | 121.8863 | 121.994 | 121.6584 | 121.8021 | -122.3773
1748.2812 | 121.9986 | -121.8063 | 0.17395 | 1.4211e-13 | -0.0099315 | 0.021752 | -0.0033377 | -0.0090251 | 0.010143 | -0.006028 | 0.04796 | 0.033976 | 0.075134 | 0.11561 | 0.060207 | 0.074302 | 0.038035 | 0.037373 | 0.16659 | 0.096516 | 0.35258 | 0.07431 | -120.9593 | 0.018674 | -0.038036 | 0.11656 | 0.21516 | -0.10671 | -122.2308 | 121.8806 | -0.007363 | 121.8806 | 121.8437 | -0.036937 | -0.077434 | 0.17863 | -0.4245 | -0.057393 | 0.84703 | 121.7683 | 122.1928 | 0.041215 | -0.28066 | 121.9729 | 121.9029 | 122.1589 | 121.8444 | -0.09964 | 121.9229 | 122.0215 | 121.6996 | 121.825 | -122.4048
1750.0156 | 122.0673 | -121.7697 | 0.13733 | 1.4211e-13 | -0.010359 | 0.021966 | -0.0033377 | -0.0094525 | 0.010356 | -0.021289 | 0.055223 | 0.026071 | 0.07492 | 0.11604 | 0.060207 | 0.074302 | 0.038035 | 0.032795 | 0.16659 | 0.091937 | 0.348 | 0.10636 | -120.9639 | 0.018674 | -0.042615 | 0.11656 | 0.21516 | -0.11587 | -122.2354 | 121.8761 | 0.029258 | 121.844 | 121.8025 | -0.073568 | -0.045392 | 0.21067 | -0.4657 | -0.020772 | 0.80583 | 121.7271 | 122.1928 | 0.077836 | -0.2532 | 121.9363 | 121.8617 | 122.1177 | 121.8077 | -0.030966 | 121.8863 | 121.9849 | 121.6538 | 121.7884 | -122.3727
1751.7031 | 122.081 | -121.788 | 0.13275 | 1.4211e-13 | -0.010145 | 0.021752 | -0.0033377 | -0.0090251 | 0.010143 | 0.0016025 | 0.047105 | 0.034403 | 0.07492 | 0.11604 | 0.060421 | 0.083459 | 0.038035 | 0.032795 | 0.16659 | 0.1011 | 0.348 | 0.10636 | -121.028 | 0.023253 | -0.033458 | 0.11198 | 0.22432 | -0.12045 | -122.2446 | 121.8944 | 0.033836 | 121.8715 | 121.8208 | -0.073568 | -0.031656 | 0.21525 | -0.45655 | -0.020772 | 0.76004 | 121.7546 | 122.2111 | 0.091571 | -0.2532 | 121.9546 | 121.8891 | 122.136 | 121.8261 | -0.026388 | 121.9 | 122.0123 | 121.6676 | 121.8113 | -122.3773
1753.4531 | 121.994 | -121.8292 | 0.16479 | 1.4211e-13 | -0.010145 | 0.02218 | -0.0035515 | -0.0090251 | 0.010356 | 0.0016025 | 0.045396 | 0.035899 | 0.075134 | 0.11561 | 0.060207 | 0.07888 | 0.033457 | 0.041952 | 0.17117 | 0.1011 | 0.348 | 0.10636 | -121.0463 | 0.014095 | -0.038036 | 0.11198 | 0.21516 | -0.11587 | -122.2492 | 121.9356 | 0.006371 | 121.9081 | 121.8712 | -0.064411 | -0.0637 | 0.18321 | -0.41993 | -0.052816 | 0.78292 | 121.7912 | 122.2111 | 0.05037 | -0.28067 | 122.0004 | 121.9303 | 122.1772 | 121.8627 | -0.058432 | 121.9412 | 122.0444 | 121.7134 | 121.8433 | -122.4139
1755.1406 | 122.0718 | -121.8246 | 0.16479 | 1.4211e-13 | -0.010145 | 0.021752 | -0.0031241 | -0.0092389 | 0.010356 | 0.0016025 | 0.082996 | -0.0025597 | 0.07492 | 0.11561 | 0.059994 | 0.07888 | 0.033457 | 0.037373 | 0.16659 | 0.1011 | 0.33885 | 0.092626 | -121.0509 | 0.014095 | -0.051772 | 0.1074 | 0.22432 | -0.10671 | -122.2537 | 121.9173 | 0.001792 | 121.9035 | 121.862 | -0.055253 | -0.0637 | 0.17405 | -0.42908 | -0.057394 | 0.77376 | 121.7729 | 122.202 | 0.059527 | -0.27151 | 121.9912 | 121.9257 | 122.1635 | 121.8581 | -0.072169 | 121.932 | 122.049 | 121.7179 | 121.8387 | -122.4185
1756.8906 | 122.1542 | -121.8018 | 0.15106 | 1.4211e-13 | -0.010145 | 0.021752 | -0.0026967 | -0.0090251 | 0.01057 | -0.006028 | 0.083423 | -0.0027733 | 0.07492 | 0.1154 | 0.059994 | 0.083459 | 0.038035 | 0.041952 | 0.16659 | 0.091937 | 0.33427 | 0.10636 | -121.0646 | 0.014095 | -0.038036 | 0.10282 | 0.21059 | -0.11587 | -122.2629 | 121.9081 | 0.015525 | 121.8852 | 121.8437 | -0.064411 | -0.059125 | 0.1832 | -0.46113 | -0.04824 | 0.73714 | 121.7637 | 122.2249 | 0.059524 | -0.26693 | 121.9683 | 121.8937 | 122.136 | 121.8398 | -0.044699 | 121.9046 | 122.0123 | 121.6859 | 121.8159 | -122.4139
1758.6562 | 122.0627 | -121.8475 | 0.16937 | 1.4211e-13 | -0.010145 | 0.021966 | -0.0033377 | -0.0088115 | 0.010356 | 0.0016025 | 0.083637 | -0.0027733 | 0.075134 | 0.11518 | 0.059994 | 0.083459 | 0.042614 | 0.037373 | 0.16659 | 0.096516 | 0.34342 | 0.10636 | -121.0646 | 0.014095 | -0.047194 | 0.11198 | 0.22432 | -0.11587 | -122.2629 | 121.9539 | -0.002786 | 121.931 | 121.8849 | -0.06899 | -0.072857 | 0.17405 | -0.41535 | -0.057394 | 0.78291 | 121.8003 | 122.2157 | 0.054949 | -0.28524 | 122.0141 | 121.944 | 122.191 | 121.8901 | -0.06301 | 121.9595 | 122.0719 | 121.7317 | 121.8616 | -122.4323
1760.4219 | 121.9986 | -121.8704 | 0.15564 | 1.4211e-13 | -0.0097179 | 0.02218 | -0.0029103 | -0.0090251 | 0.010356 | -0.006028 | 0.082996 | -0.0025597 | 0.075134 | 0.11518 | 0.060207 | 0.07888 | 0.0243 | 0.028217 | 0.15743 | 0.096516 | 0.33885 | 0.083468 | -121.0829 | 0.014095 | -0.056351 | 0.098244 | 0.21059 | 0.18632 | -122.2812 | 121.9539 | 0.001791 | 121.9493 | 121.8986 | -0.055251 | -0.059124 | 0.18321 | -0.41078 | -0.057396 | 0.78749 | 121.8141 | 122.2249 | 0.054946 | 0.030676 | 122.0279 | 121.9669 | 122.2093 | 121.8947 | -0.072172 | 121.9687 | 122.081 | 122.0567 | 121.8845 | -122.4368
1762.125 | 122.0215 | -121.8384 | 0.15564 | 1.4211e-13 | -0.010145 | 0.021539 | -0.0031241 | -0.0090251 | 0.01057 | 0.0016025 | 0.048387 | 0.03248 | 0.075134 | 0.1154 | 0.060421 | 0.074302 | 0.0243 | 0.037373 | 0.16201 | 0.091937 | 0.33427 | 0.10178 | -121.0875 | 0.004938 | -0.047194 | 0.098244 | 0.21059 | -0.11587 | -122.2766 | 121.9402 | 0.006369 | 121.9127 | 121.8758 | -0.064411 | -0.063703 | 0.17863 | -0.43825 | -0.057396 | 0.75087 | 121.7912 | 122.2294 | 0.054946 | -0.27151 | 122.0004 | 121.9303 | 122.1726 | 121.8627 | -0.053856 | 121.9366 | 122.049 | 121.7225 | 121.8433 | -122.4323
1763.875 | 122.0352 | -121.843 | 0.15564 | 1.4211e-13 | -0.0099315 | 0.021752 | -0.0029103 | -0.0088115 | 0.010356 | -0.013659 | 0.04091 | 0.040172 | 0.07492 | 0.11497 | 0.059994 | 0.088037 | 0.038035 | 0.032795 | 0.16201 | 0.1011 | 0.33885 | 0.078889 | -121.0784 | 0.009516 | -0.038036 | 0.093665 | 0.21059 | -0.11129 | -122.2858 | 121.9218 | 0.006369 | 121.931 | 121.8758 | -0.046094 | -0.054545 | 0.18321 | -0.44282 | -0.061975 | 0.7646 | 121.8049 | 122.2477 | 0.054946 | -0.26693 | 122.005 | 121.9441 | 122.1818 | 121.881 | -0.076751 | 121.9366 | 122.0535 | 121.7317 | 121.8525 | -122.4414
1765.625 | 121.3715 | -121.1288 | 0.16022 | 1.4211e-13 | -0.010359 | 0.021966 | -0.0035515 | -0.0088115 | 0.010143 | -0.006028 | 0.057573 | 0.021797 | 0.074279 | 0.1139 | 0.060207 | 0.069723 | 0.033457 | 0.032795 | 0.15285 | 0.08278 | 0.32969 | -0.12258 | -114.5674 | 5.0324 | 5.1313 | 5.2399 | 5.4668 | 5.2274 | -115.5687 | 121.0063 | -0.007365 | 121.1986 | 121.1616 | 0.15538 | -0.077437 | 0.16947 | 5.5602 | 5.0797 | 6.5614 | 126.2602 | 120.7 | 5.3066 | 5.0671 | 121.2817 | 121.2116 | 121.4585 | 121.1623 | -0.2828 | 126.3687 | 126.5957 | 126.3562 | 126.1612 | -115.7289
1767.4062 | 121.9391 | -121.6965 | 0.15106 | 1.4211e-13 | -0.010145 | 0.02218 | -0.0031241 | -0.0092389 | 0.010356 | 0.0016025 | 0.082996 | -0.0025597 | 0.075134 | 0.1154 | 0.060421 | 0.074302 | 0.033457 | 0.032795 | 0.15285 | 0.087359 | 0.34342 | 0.078889 | -120.9135 | 0.009516 | -0.051772 | 0.10282 | 0.21516 | 0.18632 | -122.1393 | 121.7754 | 0.00179 | 121.7708 | 121.7293 | -0.046094 | -0.063703 | 0.19236 | -0.44279 | -0.04824 | 0.78295 | 121.6447 | 122.0875 | 0.064103 | 0.035254 | 121.8493 | 121.7838 | 122.0399 | 121.7299 | -0.072173 | 121.7993 | 121.9116 | 121.8828 | 121.706 | -122.2903
1769.1094 | 121.8933 | -121.7377 | 0.14191 | 1.4211e-13 | -0.010145 | 0.022393 | -0.0033377 | -0.0092389 | 0.010143 | -0.006028 | 0.04155 | 0.039317 | 0.07492 | 0.11518 | 0.059994 | 0.065145 | 0.028878 | 0.028217 | 0.15285 | 0.091937 | 0.33885 | 0.097205 | -120.941 | 0.014095 | -0.042615 | 0.098244 | 0.21516 | 0.18632 | -122.185 | 121.8349 | 0.010945 | 121.8028 | 121.7659 | -0.068988 | -0.04997 | 0.19694 | -0.44738 | -0.043663 | 0.79668 | 121.6951 | 122.1424 | 0.073258 | 0.044409 | 121.8905 | 121.8296 | 122.0765 | 121.7665 | -0.044702 | 121.8359 | 121.9528 | 121.924 | 121.7518 | -122.327
1770.8594 | 122.081 | -121.7606 | 0.13275 | 1.4211e-13 | -0.0099315 | 0.021966 | -0.0029103 | -0.0088115 | 0.010356 | -0.006028 | 0.03856 | 0.042309 | 0.075134 | 0.11518 | 0.059994 | 0.07888 | 0.028878 | 0.037373 | 0.15285 | 0.091937 | 0.33427 | 0.10636 | -120.9776 | 0.018674 | -0.051772 | 0.093665 | 0.21516 | -0.11587 | -122.2079 | 121.8669 | 0.020101 | 121.8394 | 121.7979 | -0.06899 | -0.040814 | 0.20152 | -0.44738 | -0.039086 | 0.78293 | 121.7088 | 122.1562 | 0.082414 | -0.24862 | 121.9134 | 121.8525 | 122.0948 | 121.7894 | -0.026388 | 121.8542 | 121.9757 | 121.6447 | 121.7792 | -122.3407
1772.625 | 121.994 | -121.7743 | 0.15106 | 1.4211e-13 | -0.0099315 | 0.021966 | -0.0031241 | -0.0092389 | 0.010356 | -0.006028 | 0.03856 | 0.041881 | 0.075134 | 0.11518 | 0.060207 | 0.074302 | 0.028878 | 0.032795 | 0.16201 | 0.087359 | 0.33427 | 0.088047 | -120.973 | 0.014095 | -0.056351 | 0.10282 | 0.20601 | -0.12045 | -122.2171 | 121.8623 | 0.010947 | 121.8486 | 121.8071 | -0.055252 | -0.063703 | 0.1832 | -0.44281 | -0.04824 | 0.80125 | 121.7179 | 122.1607 | 0.054946 | -0.27151 | 121.9363 | 121.8617 | 122.1086 | 121.8032 | -0.063015 | 121.8771 | 121.9803 | 121.6538 | 121.7884 | -122.3682
1774.3906 | 122.0901 | -121.7651 | 0.1236 | 1.4211e-13 | -0.0097179 | 0.02218 | -0.0033377 | -0.0090251 | 0.010356 | -0.013659 | 0.03856 | 0.042095 | 0.075134 | 0.11497 | 0.060207 | 0.074302 | 0.0243 | 0.032795 | 0.16659 | 0.096516 | 0.34342 | 0.07431 | -120.9593 | 0.014095 | -0.047194 | 0.098244 | 0.20143 | -0.11587 | -122.2354 | 121.8394 | 0.042991 | 121.8394 | 121.7979 | -0.041515 | -0.02708 | 0.21983 | -0.47028 | -0.025352 | 0.80583 | 121.7179 | 122.1882 | 0.077833 | -0.23947 | 121.9317 | 121.8617 | 122.1086 | 121.7894 | -0.049286 | 121.8634 | 121.9666 | 121.6493 | 121.7792 | -122.359
1776.0781 | 122.0169 | -121.8018 | 0.15564 | 1.4211e-13 | -0.0099315 | 0.02218 | -0.0031241 | -0.0092389 | 0.010784 | 0.0016025 | 0.03856 | 0.041668 | 0.075134 | 0.11518 | 0.059994 | 0.074302 | 0.028878 | 0.028217 | 0.16659 | 0.087359 | 0.33427 | 0.092626 | -120.973 | 0.014095 | -0.051772 | 0.10282 | 0.20601 | -0.11587 | -122.2446 | 121.8944 | 0.010947 | 121.8761 | 121.83 | -0.064409 | -0.068281 | 0.17863 | -0.44281 | -0.052818 | 0.82871 | 121.75 | 122.1928 | 0.050368 | -0.27151 | 121.9683 | 121.8891 | 122.136 | 121.8306 | -0.063014 | 121.9046 | 122.0078 | 121.6859 | 121.8159 | -122.4002
1777.8281 | 122.0627 | -121.8018 | 0.15106 | 1.4211e-13 | -0.0099315 | 0.02218 | -0.0031241 | -0.0092389 | 0.010356 | -0.006028 | 0.038346 | 0.041668 | 0.07492 | 0.11497 | 0.060421 | 0.074302 | 0.033457 | 0.032795 | 0.15743 | 0.091937 | 0.34342 | 0.069732 | -120.973 | 0.018674 | -0.047194 | 0.10282 | 0.20601 | -0.11587 | -122.2492 | 121.8715 | 0.006369 | 121.8761 | 121.8346 | -0.036937 | -0.059125 | 0.19236 | -0.44739 | -0.04824 | 0.82871 | 121.7546 | 122.202 | 0.054946 | -0.26693 | 121.9592 | 121.8937 | 122.1452 | 121.8352 | -0.08133 | 121.9046 | 122.0078 | 121.6859 | 121.8204 | -122.4002
1779.5938 | 122.0352 | -121.8155 | 0.14648 | 1.4211e-13 | -0.010145 | 0.021966 | -0.0033377 | -0.0094525 | 0.01057 | 0.0016025 | 0.03856 | 0.042095 | 0.075134 | 0.11476 | 0.060421 | 0.069723 | 0.0243 | 0.032795 | 0.15743 | 0.096516 | 0.33885 | 0.065153 | -120.9776 | 0.009516 | -0.042615 | 0.098244 | 0.21059 | -0.10671 | -122.2675 | 121.8806 | 0.010947 | 121.8852 | 121.8483 | -0.032358 | -0.049968 | 0.19236 | -0.45198 | -0.04824 | 0.83787 | 121.7729 | 122.2249 | 0.064102 | -0.2532 | 121.9729 | 121.912 | 122.1543 | 121.8398 | -0.081331 | 121.9137 | 122.0261 | 121.7088 | 121.825 | -122.414
1781.3594 | 122.1451 | -121.8063 | 0.11902 | 1.4211e-13 | -0.0099315 | 0.02218 | -0.0031241 | -0.0090251 | 0.01057 | -0.006028 | 0.038346 | 0.041881 | 0.07492 | 0.11518 | 0.059994 | 0.069723 | 0.0243 | 0.041952 | 0.16201 | 0.091937 | 0.32969 | 0.065153 | -120.973 | 0.014095 | -0.042615 | 0.1074 | 0.21059 | -0.11587 | -122.2629 | 121.8715 | 0.04299 | 121.8761 | 121.8483 | -0.023201 | -0.027082 | 0.21067 | -0.45655 | -0.011618 | 0.83329 | 121.7637 | 122.2203 | 0.091567 | -0.23489 | 121.9683 | 121.8983 | 122.136 | 121.8306 | -0.053866 | 121.9137 | 122.0169 | 121.6905 | 121.8204 | -122.3819
1783.0469 | 122.0078 | -121.8658 | 0.16479 | 1.4211e-13 | -0.0095041 | 0.02218 | -0.0031241 | -0.0090251 | 0.010356 | 0.0016025 | 0.038132 | 0.041881 | 0.075134 | 0.11497 | 0.060421 | 0.074302 | 0.033457 | 0.032795 | 0.17574 | 0.091937 | 0.33885 | 0.083468 | -120.973 | 0.009516 | -0.051772 | 0.1074 | 0.20601 | -0.12045 | -122.272 | 121.9493 | 0.010949 | 121.9401 | 121.8986 | -0.050673 | -0.072858 | 0.17405 | -0.4062 | -0.057394 | 0.8928 | 121.8141 | 122.2203 | 0.041213 | -0.28524 | 122.0416 | 121.9578 | 122.2047 | 121.8993 | -0.081327 | 121.9732 | 122.0719 | 121.7454 | 121.8754 | -122.4368
1784.7812 | 122.0169 | -121.8613 | 0.14191 | 1.4211e-13 | -0.010359 | 0.02218 | -0.0035515 | -0.0088115 | 0.01057 | 0.0016025 | 0.037919 | 0.041881 | 0.075347 | 0.11454 | 0.060421 | 0.07888 | 0.028878 | 0.032795 | 0.15285 | 0.096516 | 0.33885 | 0.065153 | -120.9822 | 0.018674 | -0.042615 | 0.098244 | 0.20143 | -0.12045 | -122.2858 | 121.9264 | 0.010945 | 121.9401 | 121.8941 | -0.032358 | -0.045391 | 0.19694 | -0.42451 | -0.043663 | 0.87906 | 121.8187 | 122.2432 | 0.059522 | -0.26236 | 122.0141 | 121.9578 | 122.2001 | 121.8901 | -0.076754 | 121.9595 | 122.0627 | 121.7408 | 121.8799 | -122.4277
1786.5469 | 122.1497 | -121.8292 | 0.12817 | 1.4211e-13 | -0.010359 | 0.021966 | -0.0031241 | -0.0094525 | 0.010356 | -0.006028 | 0.037919 | 0.041881 | 0.075134 | 0.11454 | 0.060207 | 0.074302 | 0.019721 | 0.032795 | 0.15743 | 0.096516 | 0.32969 | 0.092626 | -120.9959 | 0.009516 | -0.038036 | 0.093665 | 0.21059 | -0.12045 | -122.2858 | 121.9218 | 0.029257 | 121.9035 | 121.862 | -0.059831 | -0.031658 | 0.20151 | -0.45656 | -0.034509 | 0.83328 | 121.7912 | 122.2477 | 0.082412 | -0.24862 | 121.9867 | 121.9257 | 122.1589 | 121.8489 | -0.035548 | 121.9229 | 122.0398 | 121.7088 | 121.8387 | -122.414
1788.25 | 122.0993 | -121.8338 | 0.1236 | 1.4211e-13 | -0.010145 | 0.021966 | -0.0029103 | -0.0090251 | 0.01057 | 0.0016025 | 0.03856 | 0.041881 | 0.075347 | 0.11476 | 0.060421 | 0.07888 | 0.038035 | 0.037373 | 0.16659 | 0.091937 | 0.33427 | 0.078889 | -120.9776 | 0.014095 | -0.047194 | 0.098244 | 0.20601 | -0.11587 | -122.2949 | 121.9127 | 0.042991 | 121.9127 | 121.8712 | -0.041516 | -0.031659 | 0.21067 | -0.46114 | -0.025352 | 0.85618 | 121.7866 | 122.2477 | 0.082412 | -0.23947 | 122.0004 | 121.9257 | 122.1681 | 121.8718 | -0.044707 | 121.932 | 122.0398 | 121.7179 | 121.8479 | -122.4185
1789.9375 | 122.0032 | -121.8796 | 0.16479 | 1.4211e-13 | -0.010145 | 0.021752 | -0.0033377 | -0.0090251 | 0.010356 | -0.006028 | 0.038346 | 0.041881 | 0.075134 | 0.11454 | 0.060421 | 0.07888 | 0.019721 | 0.037373 | 0.16201 | 0.1011 | 0.33885 | 0.092626 | -120.9639 | 0.009516 | -0.047194 | 0.098244 | 0.20601 | -0.10671 | -122.3041 | 121.9722 | -0.002786 | 121.9585 | 121.917 | -0.055253 | -0.0637 | 0.17405 | -0.42452 | -0.066551 | 0.91569 | 121.8324 | 122.2569 | 0.041213 | -0.27151 | 122.0416 | 121.9807 | 122.2184 | 121.8993 | -0.072169 | 121.9778 | 122.0856 | 121.7729 | 121.8891 | -122.4689
1791.6875 | 122.0581 | -121.8842 | 0.13733 | 1.4211e-13 | -0.0097179 | 0.021752 | -0.0029103 | -0.0092389 | 0.010356 | -0.013659 | 0.037919 | 0.041881 | 0.07492 | 0.11476 | 0.060207 | 0.07888 | 0.028878 | 0.028217 | 0.16201 | 0.091937 | 0.33427 | 0.10636 | -120.9914 | 0.018674 | -0.042615 | 0.093665 | 0.21516 | -0.11587 | -122.3087 | 121.9905 | 0.02468 | 121.963 | 121.9124 | -0.078146 | -0.045392 | 0.19694 | -0.42452 | -0.043664 | 0.8928 | 121.8415 | 122.2661 | 0.077836 | -0.2532 | 122.0462 | 121.9761 | 122.2184 | 121.913 | -0.030966 | 121.9778 | 122.0993 | 121.7683 | 121.9028 | -122.446
1793.4375 | 122.1176 | -121.875 | 0.13275 | 1.4211e-13 | -0.010145 | 0.021966 | -0.0035515 | -0.0092389 | 0.01057 | -0.013659 | 0.038132 | 0.042309 | 0.075347 | 0.11454 | 0.060207 | 0.074302 | 0.033457 | 0.037373 | 0.15285 | 0.087359 | 0.33885 | 0.07431 | -120.9914 | 0.014095 | -0.038036 | 0.10282 | 0.21516 | -0.11587 | -122.3133 | 121.9493 | 0.020101 | 121.9493 | 121.9124 | -0.036937 | -0.045392 | 0.20609 | -0.43825 | -0.029929 | 0.88364 | 121.837 | 122.2752 | 0.082414 | -0.24862 | 122.0279 | 121.9624 | 122.2138 | 121.9085 | -0.058441 | 121.9778 | 122.0902 | 121.7591 | 121.8891 | -122.446
1795.125 | 122.1817 | -121.843 | 0.10529 | 1.4211e-13 | -0.0099315 | 0.022393 | -0.0031241 | -0.0090251 | 0.010784 | 0.0016025 | 0.038132 | 0.041881 | 0.075134 | 0.11454 | 0.059994 | 0.074302 | 0.028878 | 0.037373 | 0.16201 | 0.096516 | 0.33427 | 0.083468 | -120.9685 | 0.004938 | -0.042615 | 0.098244 | 0.21059 | -0.11129 | -122.327 | 121.9264 | 0.056723 | 121.9173 | 121.8803 | -0.046095 | -0.00877 | 0.22898 | -0.48404 | -0.007042 | 0.87449 | 121.8003 | 122.2844 | 0.1053 | -0.21658 | 122.005 | 121.9395 | 122.1772 | 121.8718 | -0.021818 | 121.9412 | 122.0535 | 121.7317 | 121.8479 | -122.4323
1796.875 | 122.168 | -121.8613 | 0.1236 | 1.4211e-13 | -0.0099315 | 0.02218 | -0.0031241 | -0.0092389 | 0.01057 | 0.0016025 | 0.038132 | 0.041668 | 0.075347 | 0.11433 | 0.060421 | 0.07888 | 0.033457 | 0.032795 | 0.16659 | 0.087359 | 0.33885 | 0.083468 | -120.9593 | 0.009516 | -0.047194 | 0.10282 | 0.21059 | -0.11587 | -122.3224 | 121.9447 | 0.042991 | 121.9401 | 121.8941 | -0.050673 | -0.036237 | 0.21525 | -0.46115 | -0.020774 | 0.90196 | 121.8141 | 122.2752 | 0.08699 | -0.23947 | 122.0279 | 121.9486 | 122.2001 | 121.8947 | -0.040128 | 121.9641 | 122.0719 | 121.7454 | 121.8708 | -122.446
1798.5625 | 122.1085 | -121.8475 | 0.15564 | 1.4211e-13 | -0.0097179 | 0.021966 | -0.0031241 | -0.0094525 | 0.01057 | -0.006028 | 0.038346 | 0.041668 | 0.075347 | 0.11454 | 0.060207 | 0.074302 | 0.0243 | 0.032795 | 0.16201 | 0.087359 | 0.33427 | 0.083468 | -120.9639 | 0.023253 | -0.038036 | 0.10282 | 0.21516 | -0.11587 | -122.327 | 121.931 | 0.006369 | 121.9218 | 121.8803 | -0.050673 | -0.068281 | 0.17863 | -0.47946 | -0.052818 | 0.88365 | 121.8095 | 122.289 | 0.059525 | -0.27151 | 122.0095 | 121.9349 | 122.1818 | 121.8718 | -0.072172 | 121.9504 | 122.0627 | 121.7317 | 121.8708 | -122.4826
1800.3125 | 122.0901 | -121.9025 | 0.15564 | 1.4211e-13 | -0.010145 | 0.021752 | -0.0031241 | -0.0096661 | 0.010356 | -0.013659 | 0.038132 | 0.041454 | 0.07492 | 0.11476 | 0.060635 | 0.074302 | 0.0243 | 0.032795 | 0.16201 | 0.087359 | 0.33427 | 0.10178 | -120.9639 | 0.014095 | -0.047194 | 0.093665 | 0.20143 | -0.11129 | -122.3316 | 122.0042 | 0.006369 | 121.9768 | 121.9353 | -0.068989 | -0.068281 | 0.17863 | -0.4291 | -0.061975 | 0.93858 | 121.8553 | 122.2844 | 0.045789 | -0.26693 | 122.0645 | 121.9898 | 122.2367 | 121.9268 | -0.053856 | 121.9961 | 122.1039 | 121.7912 | 121.9166 | -122.4872
1802 | 122.081 | -121.9162 | 0.14648 | 1.4211e-13 | -0.010145 | 0.021966 | -0.0033377 | -0.0092389 | 0.01057 | -0.021289 | 0.038132 | 0.041881 | 0.07492 | 0.11476 | 0.060421 | 0.07888 | 0.0243 | 0.032795 | 0.16201 | 0.091937 | 0.33885 | 0.078889 | -120.9639 | 0.009516 | -0.047194 | 0.089087 | 0.21059 | -0.11587 | -122.3407 | 121.9951 | 0.015525 | 121.9951 | 121.949 | -0.046094 | -0.054547 | 0.19236 | -0.42453 | -0.057397 | 0.95231 | 121.869 | 122.2935 | 0.064102 | -0.26236 | 122.0782 | 122.0081 | 122.255 | 121.9405 | -0.067595 | 122.0053 | 122.1268 | 121.8003 | 121.9257 | -122.4872
1803.75 | 122.1771 | -121.8933 | 0.1236 | 1.4211e-13 | -0.0097179 | 0.022393 | -0.0031241 | -0.0090251 | 0.01057 | -0.006028 | 0.03856 | 0.042095 | 0.075347 | 0.11476 | 0.060421 | 0.083459 | 0.033457 | 0.032795 | 0.16659 | 0.1011 | 0.33427 | 0.092626 | -120.9593 | 0.014095 | -0.047194 | 0.098244 | 0.20601 | -0.12045 | -122.3361 | 121.9859 | 0.042991 | 121.9768 | 121.9261 | -0.059831 | -0.022501 | 0.21067 | -0.44284 | -0.025352 | 0.934 | 121.8461 | 122.289 | 0.082412 | -0.24405 | 122.0599 | 121.9944 | 122.2276 | 121.9268 | -0.03097 | 121.9916 | 122.0993 | 121.7729 | 121.9074 | -122.4597
1805.4531 | 122.1817 | -121.8933 | 0.12817 | 1.4211e-13 | -0.0099315 | 0.021752 | -0.0031241 | -0.0090251 | 0.010356 | -0.006028 | 0.038132 | 0.042095 | 0.075134 | 0.11433 | 0.060207 | 0.074302 | 0.028878 | 0.037373 | 0.16201 | 0.091937 | 0.33427 | 0.065153 | -120.9502 | 0.018674 | -0.047194 | 0.098244 | 0.21516 | -0.12045 | -122.3453 | 121.9585 | 0.033835 | 121.9676 | 121.9307 | -0.02778 | -0.036237 | 0.20609 | -0.452 | -0.02993 | 0.94316 | 121.8461 | 122.2981 | 0.086991 | -0.24862 | 122.0553 | 121.9852 | 122.2276 | 121.9222 | -0.063021 | 121.9916 | 122.1085 | 121.7729 | 121.912 | -122.4735
1807.2188 | 122.1634 | -121.907 | 0.13275 | 1.4211e-13 | -0.0097179 | 0.021966 | -0.0031241 | -0.0090251 | 0.010143 | -0.006028 | 0.038346 | 0.041881 | 0.075134 | 0.1139 | 0.060635 | 0.074302 | 0.028878 | 0.041952 | 0.15743 | 0.091937 | 0.33885 | 0.10178 | -120.941 | 0.014095 | -0.042615 | 0.093665 | 0.20601 | -0.11587 | -122.3545 | 122.0088 | 0.02468 | 121.9813 | 121.949 | -0.059832 | -0.040814 | 0.20609 | -0.44742 | -0.039086 | 0.96605 | 121.8644 | 122.3118 | 0.073257 | -0.24862 | 122.0645 | 121.999 | 122.2459 | 121.9359 | -0.030967 | 122.0007 | 122.1131 | 121.7912 | 121.9211 | -122.4872
1808.9688 | 122.2046 | -121.8933 | 0.11902 | 1.4211e-13 | -0.0097179 | 0.021966 | -0.0035515 | -0.0094525 | 0.010143 | -0.006028 | 0.038132 | 0.041881 | 0.075347 | 0.11433 | 0.060635 | 0.074302 | 0.0243 | 0.037373 | 0.16201 | 0.096516 | 0.33885 | 0.10636 | -120.941 | 0.004938 | -0.042615 | 0.10282 | 0.19685 | -0.12045 | -122.3499 | 121.9997 | 0.04299 | 121.9676 | 121.9307 | -0.06899 | -0.022503 | 0.21983 | -0.45658 | -0.016197 | 0.95232 | 121.8507 | 122.3073 | 0.077832 | -0.23947 | 122.0553 | 121.9898 | 122.2322 | 121.9176 | -0.012656 | 121.9961 | 122.0902 | 121.7729 | 121.8982 | -122.4689
1810.6562 | 122.0947 | -121.9391 | 0.14191 | 1.4211e-13 | -0.0097179 | 0.021966 | -0.0035515 | -0.0092389 | 0.010356 | 0.0016025 | 0.037919 | 0.042095 | 0.075347 | 0.11433 | 0.060635 | 0.074302 | 0.033457 | 0.037373 | 0.15743 | 0.091937 | 0.33427 | 0.10636 | -120.9273 | 0.009516 | -0.047194 | 0.093665 | 0.21059 | -0.11587 | -122.3636 | 122.0455 | 0.015524 | 122.0134 | 121.9765 | -0.06899 | -0.04997 | 0.19236 | -0.42454 | -0.048242 | 1.0118 | 121.8919 | 122.3164 | 0.068679 | -0.25778 | 122.0965 | 122.031 | 122.2734 | 121.9725 | -0.035544 | 122.0328 | 122.1497 | 121.8232 | 121.9486 | -122.5055
1812.4219 | 122.1725 | -121.9025 | 0.1236 | 1.4211e-13 | -0.0099315 | 0.021966 | -0.0033377 | -0.0092389 | 0.010143 | 0.0092325 | 0.037705 | 0.042309 | 0.075134 | 0.11412 | 0.060421 | 0.074302 | 0.028878 | 0.032795 | 0.15743 | 0.1011 | 0.33427 | 0.042258 | -120.9502 | 0.018674 | -0.051772 | 0.089087 | 0.20601 | -0.11129 | -122.3636 | 121.9447 | 0.033835 | 121.9768 | 121.9353 | -0.009463 | -0.022501 | 0.21067 | -0.46116 | -0.034509 | 0.95231 | 121.8507 | 122.3119 | 0.082412 | -0.23489 | 122.0599 | 122.0036 | 122.2367 | 121.9313 | -0.081338 | 121.9916 | 122.1085 | 121.7912 | 121.9211 | -122.4872
1814.1719 | 122.2046 | -121.8933 | 0.09613 | 1.4211e-13 | -0.0097179 | 0.021966 | -0.0031241 | -0.0088115 | 0.010356 | 0.0016025 | 0.037705 | 0.042309 | 0.075134 | 0.11433 | 0.060421 | 0.07888 | 0.028878 | 0.032795 | 0.15285 | 0.096516 | 0.34342 | 0.078889 | -120.941 | 0.009516 | -0.033458 | 0.10282 | 0.20601 | -0.11129 | -122.3636 | 121.9722 | 0.056722 | 121.9722 | 121.9261 | -0.046094 | 0.000386 | 0.24729 | -0.47031 | 0.006692 | 0.95232 | 121.8599 | 122.3302 | 0.10988 | -0.20742 | 122.0462 | 121.9898 | 122.2367 | 121.9222 | -0.017241 | 121.9961 | 122.0993 | 121.782 | 121.9028 | -122.4598
1815.9219 | 122.0718 | -121.9254 | 0.15564 | 1.4211e-13 | -0.0099315 | 0.021752 | -0.0031241 | -0.0090251 | 0.01057 | 0.0016025 | 0.037705 | 0.042095 | 0.075134 | 0.11412 | 0.060421 | 0.074302 | 0.028878 | 0.032795 | 0.16201 | 0.1011 | 0.33427 | 0.078889 | -120.9318 | 0.018674 | -0.042615 | 0.089087 | 0.21059 | -0.12045 | -122.3728 | 122.0042 | 0.006369 | 121.9997 | 121.9581 | -0.046094 | -0.054545 | 0.17863 | -0.44743 | -0.066553 | 0.99352 | 121.8827 | 122.3302 | 0.054946 | -0.27609 | 122.0874 | 122.0264 | 122.2596 | 121.9542 | -0.076751 | 122.0144 | 122.1359 | 121.8049 | 121.944 | -122.5284
1817.625 | 122.0856 | -121.9482 | 0.15564 | 1.4211e-13 | -0.0097179 | 0.021966 | -0.0035515 | -0.0092389 | 0.010143 | -0.006028 | 0.037705 | 0.041668 | 0.075347 | 0.11412 | 0.060421 | 0.074302 | 0.033457 | 0.037373 | 0.15285 | 0.096516 | 0.32969 | 0.10178 | -120.941 | 0.014095 | -0.038036 | 0.1074 | 0.21059 | -0.11587 | -122.3819 | 122.05 | -0.002788 | 122.0225 | 121.9856 | -0.064411 | -0.059124 | 0.17405 | -0.4337 | -0.048239 | 1.0072 | 121.9102 | 122.3439 | 0.054946 | -0.27151 | 122.1011 | 122.0448 | 122.2779 | 121.9817 | -0.053856 | 122.0556 | 122.1588 | 121.8324 | 121.9623 | -122.5376
1819.375 | 122.2 | -121.9254 | 0.11444 | 1.4211e-13 | -0.010359 | 0.021966 | -0.0035515 | -0.0092389 | 0.01057 | 0.0016025 | 0.037491 | 0.041668 | 0.07492 | 0.11412 | 0.060635 | 0.065145 | 0.028878 | 0.032795 | 0.16201 | 0.091937 | 0.33885 | 0.088047 | -120.9502 | 0.014095 | -0.033458 | 0.093665 | 0.20601 | -0.11587 | -122.3865 | 122.0134 | 0.047568 | 121.9905 | 121.9581 | -0.055252 | -0.022504 | 0.2244 | -0.46116 | -0.020776 | 0.9752 | 121.8919 | 122.3531 | 0.091567 | -0.23031 | 122.0874 | 122.0173 | 122.2642 | 121.9542 | -0.026394 | 122.019 | 122.1314 | 121.8095 | 121.9394 | -122.501
1821.0781 | 122.2412 | -121.907 | 0.11444 | 1.4211e-13 | -0.010145 | 0.022393 | -0.0029103 | -0.0090251 | 0.01057 | -0.006028 | 0.037705 | 0.042095 | 0.075347 | 0.11412 | 0.060421 | 0.074302 | 0.0243 | 0.028217 | 0.15743 | 0.091937 | 0.33427 | 0.078889 | -120.941 | 0.014095 | -0.042615 | 0.098244 | 0.20143 | -0.12045 | -122.3957 | 121.9859 | 0.04299 | 121.9813 | 121.9353 | -0.050672 | -0.022504 | 0.21983 | -0.48863 | -0.016197 | 0.96605 | 121.8644 | 122.3531 | 0.086988 | -0.23489 | 122.0645 | 121.999 | 122.2413 | 121.9313 | -0.035552 | 122.0053 | 122.1085 | 121.7866 | 121.9211 | -122.5101
1822.8281 | 122.2549 | -121.9208 | 0.12817 | 1.4211e-13 | -0.0099315 | 0.02218 | -0.0031241 | -0.0094525 | 0.010784 | -0.006028 | 0.037705 | 0.042309 | 0.075134 | 0.11433 | 0.060207 | 0.074302 | 0.028878 | 0.032795 | 0.15743 | 0.1011 | 0.32969 | 0.092626 | -120.9318 | 0.014095 | -0.038036 | 0.093665 | 0.20143 | -0.12503 | -122.3957 | 122.0134 | 0.029257 | 121.9951 | 121.9536 | -0.059831 | -0.027079 | 0.20151 | -0.4749 | -0.034509 | 0.98894 | 121.8827 | 122.3576 | 0.073255 | -0.2532 | 122.0782 | 122.0219 | 122.2505 | 121.9497 | -0.035548 | 122.0144 | 122.1222 | 121.7957 | 121.9349 | -122.5238
1824.5938 | 122.2046 | -121.9437 | 0.11902 | 1.4211e-13 | -0.0099315 | 0.021752 | -0.0033377 | -0.0085979 | 0.010356 | 0.0016025 | 0.038132 | 0.041881 | 0.075347 | 0.1139 | 0.060421 | 0.074302 | 0.028878 | 0.037373 | 0.16201 | 0.078201 | 0.33885 | 0.092626 | -120.941 | 0.014095 | -0.047194 | 0.093665 | 0.19685 | -0.11587 | -122.4003 | 122.0363 | 0.04299 | 122.018 | 121.981 | -0.055253 | -0.040818 | 0.21983 | -0.45659 | -0.025354 | 1.0027 | 121.8965 | 122.3531 | 0.077832 | -0.23489 | 122.1057 | 122.0219 | 122.2825 | 121.9725 | -0.026393 | 122.0373 | 122.1405 | 121.8278 | 121.9578 | -122.5193
1826.2969 | 122.1497 | -121.9711 | 0.14648 | 1.4211e-13 | -0.0099315 | 0.021966 | -0.0033377 | -0.0092389 | 0.01057 | 0.0016025 | 0.037705 | 0.041881 | 0.075134 | 0.11412 | 0.060635 | 0.074302 | 0.028878 | 0.037373 | 0.15285 | 0.096516 | 0.33427 | 0.11094 | -120.9273 | 0.014095 | -0.042615 | 0.10282 | 0.20601 | -0.11587 | -122.4003 | 122.0821 | 0.006368 | 122.0454 | 122.0085 | -0.073569 | -0.049968 | 0.18778 | -0.42912 | -0.043662 | 1.0439 | 121.9285 | 122.3576 | 0.059524 | -0.26236 | 122.124 | 122.0676 | 122.3054 | 122 | -0.035542 | 122.074 | 122.1771 | 121.8553 | 121.9852 | -122.5467
1829.4688 | 122.2687 | -121.9254 | 0.12817 | 1.4211e-13 | -0.0095041 | 0.02218 | -0.0035515 | -0.0088115 | 0.010143 | -0.006028 | 0.037705 | 0.041668 | 0.075347 | 0.11433 | 0.060635 | 0.074302 | 0.019721 | 0.037373 | 0.15743 | 0.1011 | 0.33427 | 0.10178 | -120.9364 | 0.023253 | -0.042615 | 0.098244 | 0.20143 | -0.11587 | -122.4094 | 122.0271 | 0.029257 | 121.9997 | 121.9627 | -0.064411 | -0.027079 | 0.20609 | -0.48406 | -0.02993 | 0.98894 | 121.8827 | 122.3668 | 0.073255 | -0.24405 | 122.0828 | 122.0264 | 122.2596 | 121.9451 | -0.02639 | 122.0236 | 122.1268 | 121.8095 | 121.9486 | -122.5376
1833.4531 | 122.2458 | -121.962 | 0.1236 | 1.4211e-13 | -0.0097179 | 0.021966 | -0.0031241 | -0.0092389 | 0.010356 | 0.0016025 | 0.037491 | 0.042095 | 0.075347 | 0.1139 | 0.060635 | 0.07888 | 0.028878 | 0.028217 | 0.14827 | 0.096516 | 0.33885 | 0.078889 | -120.8998 | 0.018674 | -0.042615 | 0.098244 | 0.20143 | -0.11587 | -122.4277 | 122.0409 | 0.024678 | 122.0409 | 121.9902 | -0.050672 | -0.02708 | 0.21525 | -0.46575 | -0.025352 | 1.0622 | 121.9194 | 122.3851 | 0.077833 | -0.23947 | 122.1102 | 122.0585 | 122.3008 | 121.9909 | -0.044707 | 122.0602 | 122.1634 | 121.8461 | 121.9806 | -122.5513
1839.6406 | 122.1634 | -122.0032 | 0.16937 | 1.4211e-13 | -0.010145 | 0.021966 | -0.0033377 | -0.0092389 | 0.010356 | -0.006028 | 0.037705 | 0.042095 | 0.075561 | 0.11348 | 0.060421 | 0.069723 | 0.028878 | 0.032795 | 0.15285 | 0.087359 | 0.32969 | 0.088047 | -120.9181 | 0.018674 | -0.047194 | 0.093665 | 0.20601 | -0.12503 | -122.4277 | 122.0912 | -0.016521 | 122.0729 | 122.036 | -0.055252 | -0.082014 | 0.16032 | -0.42455 | -0.075708 | 1.0851 | 121.956 | 122.3805 | 0.036635 | -0.2944 | 122.156 | 122.0905 | 122.3329 | 122.0321 | -0.081326 | 122.0968 | 122.2092 | 121.8781 | 122.0218 | -122.5971
1841.4844 | 122.1588 | -121.994 | 0.1236 | 1.4211e-13 | -0.0097179 | 0.021752 | -0.0033377 | -0.0090251 | 0.010143 | 0.0016025 | 0.037491 | 0.041668 | 0.075134 | 0.11348 | 0.060421 | 0.074302 | 0.0243 | 0.032795 | 0.15285 | 0.087359 | 0.32511 | 0.078889 | -120.8952 | 0.014095 | -0.038036 | 0.089087 | 0.20601 | -0.12045 | -122.4415 | 122.0729 | 0.029256 | 122.0683 | 122.0268 | -0.046094 | -0.036237 | 0.20151 | -0.44744 | -0.034509 | 1.0988 | 121.956 | 122.4034 | 0.082412 | -0.24405 | 122.1469 | 122.0814 | 122.3191 | 122.0183 | -0.044707 | 122.0831 | 122.2 | 121.8736 | 122.0081 | -122.5651
1843.1875 | 122.1771 | -122.0169 | 0.14648 | 1.4211e-13 | -0.0097179 | 0.021966 | -0.0031241 | -0.0094525 | 0.01057 | -0.006028 | 0.037705 | 0.042095 | 0.075347 | 0.11348 | 0.060421 | 0.069723 | 0.019721 | 0.028217 | 0.16201 | 0.078201 | 0.33427 | 0.092626 | -120.8815 | 0.018674 | -0.042615 | 0.089087 | 0.19685 | -0.12045 | -122.446 | 122.1095 | 0.015525 | 122.0866 | 122.0451 | -0.064409 | -0.068283 | 0.18778 | -0.42913 | -0.057397 | 1.1354 | 121.9743 | 122.4034 | 0.050367 | -0.26693 | 122.1789 | 122.0951 | 122.3512 | 122.0366 | -0.053858 | 122.106 | 122.2138 | 121.8965 | 122.0356 | -122.5925
1844.9375 | 122.2092 | -122.0261 | 0.16022 | 1.4211e-13 | -0.0099315 | 0.021752 | -0.0031241 | -0.0090251 | 0.01057 | -0.013659 | 0.037705 | 0.041881 | 0.075347 | 0.11369 | 0.060635 | 0.07888 | 0.028878 | 0.032795 | 0.16201 | 0.087359 | 0.32969 | 0.07431 | -120.8723 | 0.018674 | -0.047194 | 0.098244 | 0.19685 | -0.12045 | -122.4506 | 122.1004 | 0.001792 | 122.1049 | 122.0589 | -0.041515 | -0.072858 | 0.16947 | -0.42456 | -0.061973 | 1.1537 | 121.9789 | 122.4034 | 0.036634 | -0.28067 | 122.1881 | 122.1134 | 122.3558 | 122.0549 | -0.085907 | 122.1243 | 122.2229 | 121.9056 | 122.0447 | -122.6108
1846.7031 | 122.2595 | -121.9894 | 0.1236 | 1.4211e-13 | -0.010145 | 0.021539 | -0.0031241 | -0.0094525 | 0.009929 | -0.006028 | 0.037491 | 0.04124 | 0.075347 | 0.1139 | 0.060421 | 0.07888 | 0.0243 | 0.032795 | 0.16201 | 0.091937 | 0.32969 | 0.065153 | -120.8677 | 0.018674 | -0.038036 | 0.093665 | 0.20601 | -0.12045 | -122.4598 | 122.0546 | 0.038413 | 122.0683 | 122.0222 | -0.032358 | -0.031659 | 0.20609 | -0.47034 | -0.029931 | 1.1217 | 121.9514 | 122.4217 | 0.082412 | -0.24405 | 122.1514 | 122.0814 | 122.3191 | 122.0137 | -0.058443 | 122.0831 | 122.1954 | 121.869 | 122.0081 | -122.5834
1848.4688 | 122.2046 | -122.0078 | 0.13733 | 1.4211e-13 | -0.010145 | 0.021966 | -0.0035515 | -0.0092389 | 0.010784 | 0.0016025 | 0.037491 | 0.041881 | 0.075561 | 0.11369 | 0.060635 | 0.069723 | 0.0243 | 0.032795 | 0.16201 | 0.08278 | 0.33427 | 0.083468 | -120.854 | 0.018674 | -0.047194 | 0.093665 | 0.20601 | -0.11587 | -122.4644 | 122.0912 | 0.02468 | 122.0775 | 122.0405 | -0.050673 | -0.054549 | 0.19694 | -0.4566 | -0.043664 | 1.1538 | 121.9606 | 122.4172 | 0.068679 | -0.2532 | 122.1698 | 122.0905 | 122.342 | 122.0321 | -0.053861 | 122.1014 | 122.2138 | 121.8919 | 122.0264 | -122.6017
1850.1562 | 122.168 | -122.0352 | 0.14191 | 1.4211e-13 | -0.0099315 | 0.021752 | -0.0033377 | -0.0092389 | 0.010143 | 0.0092325 | 0.037705 | 0.041454 | 0.075134 | 0.11369 | 0.060635 | 0.074302 | 0.028878 | 0.028217 | 0.16659 | 0.091937 | 0.32969 | 0.069732 | -120.8448 | 0.027831 | -0.042615 | 0.093665 | 0.20601 | -0.11587 | -122.4735 | 122.1049 | 0.02468 | 122.1095 | 122.0634 | -0.041515 | -0.04997 | 0.18778 | -0.4383 | -0.048242 | 1.1904 | 121.9926 | 122.4309 | 0.064101 | -0.25778 | 122.2018 | 122.1272 | 122.3649 | 122.0641 | -0.072175 | 122.1289 | 122.2412 | 121.9193 | 122.063 | -122.6154
1851.8438 | 122.2321 | -122.0398 | 0.16022 | 1.4211e-13 | -0.0097179 | 0.021966 | -0.0035515 | -0.0092389 | 0.010356 | 0.0016025 | 0.037278 | 0.041668 | 0.075347 | 0.11369 | 0.060421 | 0.074302 | 0.0243 | 0.032795 | 0.15285 | 0.091937 | 0.32969 | 0.07431 | -120.8311 | 0.014095 | -0.047194 | 0.093665 | 0.21059 | -0.11587 | -122.4689 | 122.1141 | -0.007365 | 122.1141 | 122.0726 | -0.041515 | -0.06828 | 0.16947 | -0.42914 | -0.066552 | 1.2087 | 121.9926 | 122.4217 | 0.050369 | -0.27609 | 122.1926 | 122.1317 | 122.3695 | 122.0641 | -0.085907 | 122.1335 | 122.2504 | 121.9239 | 122.0539 | -122.6292
1853.5938 | 122.2641 | -122.0078 | 0.13275 | 1.4211e-13 | -0.0097179 | 0.021752 | -0.0033377 | -0.0092389 | 0.010356 | -0.006028 | 0.037491 | 0.041668 | 0.075134 | 0.11348 | 0.060635 | 0.069723 | 0.0243 | 0.032795 | 0.14827 | 0.091937 | 0.33427 | 0.083468 | -120.8311 | 0.018674 | -0.042615 | 0.093665 | 0.21059 | -0.12503 | -122.4735 | 122.0912 | 0.015523 | 122.0775 | 122.0405 | -0.050673 | -0.040814 | 0.20152 | -0.46576 | -0.039086 | 1.1766 | 121.9651 | 122.4309 | 0.077835 | -0.25778 | 122.156 | 122.0997 | 122.342 | 122.0321 | -0.049283 | 122.1014 | 122.2183 | 121.8827 | 122.0264 | -122.6063
1855.2812 | 122.287 | -121.994 | 0.12817 | 1.4211e-13 | -0.0095041 | 0.021966 | -0.0031241 | -0.0092389 | 0.01057 | -0.006028 | 0.037491 | 0.041881 | 0.075347 | 0.11369 | 0.060635 | 0.069723 | 0.0243 | 0.028217 | 0.15743 | 0.096516 | 0.32511 | 0.088047 | -120.8082 | 0.018674 | -0.042615 | 0.098244 | 0.20143 | -0.11587 | -122.4781 | 122.0821 | 0.029257 | 122.0637 | 122.0222 | -0.05983 | -0.031658 | 0.19694 | -0.48407 | -0.02993 | 1.1858 | 121.9514 | 122.4355 | 0.073255 | -0.24405 | 122.1514 | 122.0905 | 122.3191 | 122.0183 | -0.040127 | 122.0923 | 122.1954 | 121.8781 | 122.0127 | -122.6063
1857.0312 | 122.3373 | -122.0306 | 0.11444 | 1.4211e-13 | -0.0097179 | 0.021966 | -0.0033377 | -0.0090251 | 0.010784 | 0.0016025 | 0.037278 | 0.041454 | 0.075561 | 0.11348 | 0.060635 | 0.074302 | 0.028878 | 0.037373 | 0.15743 | 0.087359 | 0.32969 | 0.065153 | -120.8219 | 0.018674 | -0.038036 | 0.093665 | 0.20601 | -0.12045 | -122.4827 | 122.0958 | 0.04299 | 122.1049 | 122.068 | -0.02778 | -0.027082 | 0.21525 | -0.45203 | -0.020776 | 1.2087 | 121.9926 | 122.4446 | 0.091567 | -0.23489 | 122.1881 | 122.118 | 122.3603 | 122.0595 | -0.049288 | 122.1243 | 122.2366 | 121.9102 | 122.0493 | -122.5971
1858.7969 | 122.3282 | -122.0718 | 0.11902 | 1.4211e-13 | -0.0097179 | 0.02218 | -0.0033377 | -0.0092389 | 0.010356 | 0.0016025 | -0.050314 | 0.030985 | 0.0082618 | 0.029075 | 0.0078625 | 0.069723 | 0.028878 | 0.01906 | 0.15743 | 0.087359 | 0.33427 | 0.060574 | -1.8625 | 0.041567 | -0.005985 | 0.1074 | 0.21974 | 0.20005 | -2.3666 | 122.1324 | 0.038412 | 122.1416 | 122.0909 | -0.041514 | -0.03166 | 0.21525 | 119.7053 | -0.011618 | 120.2094 | 122.0659 | 2.3606 | 0.10072 | 0.081033 | 122.2293 | 122.1592 | 122.4061 | 122.1007 | -0.058445 | 122.1792 | 122.2916 | 122.2719 | 122.1134 | -2.4856
1860.5625 | 122.3053 | -122.0764 | 0.1236 | 1.4211e-13 | -0.0099315 | 0.021752 | -0.0035515 | -0.0092389 | 0.010356 | -0.006028 | -0.053946 | 0.027566 | 0.0074072 | 0.027579 | 0.0044439 | 0.065145 | 0.0243 | 0.028217 | 0.15285 | 0.087359 | 0.32969 | 0.065153 | 0.046835 | 0.050725 | -0.005985 | 0.11198 | 0.21516 | -0.11587 | -0.25115 | 122.1416 | 0.029256 | 122.1416 | 122.1046 | -0.036936 | -0.036237 | 0.20609 | 121.8253 | -0.011617 | 122.1233 | 122.0704 | 0.24516 | 0.091569 | -0.23947 | 122.2293 | 122.1638 | 122.4061 | 122.1007 | -0.058443 | 122.1884 | 122.2916 | 121.9605 | 122.1271 | -0.37474
1862.2656 | 122.3099 | -122.0306 | 0.11902 | 1.4211e-13 | -0.0099315 | 0.021966 | -0.0033377 | -0.0092389 | 0.01057 | 0.0092325 | -0.054159 | 0.02778 | 0.0071936 | 0.027792 | 0.0042303 | 0.069723 | 0.028878 | 0.032795 | 0.15743 | 0.096516 | 0.32969 | 0.051416 | 0.060571 | 0.036989 | -0.010564 | 0.1074 | 0.21516 | -0.12045 | -0.24199 | 122.0821 | 0.038412 | 122.1004 | 122.0634 | -0.018621 | -0.022503 | 0.21067 | 121.7887 | -0.011618 | 122.0912 | 122.0201 | 0.23143 | 0.096146 | -0.23947 | 122.1881 | 122.1272 | 122.3603 | 122.0595 | -0.067603 | 122.138 | 122.2458 | 121.9102 | 122.0676 | -0.36101
1864.0156 | 122.3511 | -122.0306 | 0.10986 | 1.4211e-13 | -0.0099315 | 0.02218 | -0.0035515 | -0.0090251 | 0.010143 | -0.013659 | -0.053732 | 0.027566 | 0.0071936 | 0.028006 | 0.0046577 | 0.074302 | 0.019721 | 0.032795 | 0.15285 | 0.087359 | 0.32969 | 0.065153 | 0.06515 | 0.046146 | -0.005985 | 0.1074 | 0.21974 | -0.11587 | -0.22825 | 122.0958 | 0.042989 | 122.1049 | 122.0634 | -0.032358 | -0.022504 | 0.21983 | 121.8024 | -0.002462 | 122.0958 | 122.0247 | 0.22227 | 0.10988 | -0.22574 | 122.1835 | 122.118 | 122.3603 | 122.0504 | -0.04471 | 122.138 | 122.2504 | 121.9148 | 122.0768 | -0.33811
1865.7031 | 122.3007 | -122.0764 | 0.11902 | 1.4211e-13 | -0.0095041 | 0.021966 | -0.0031241 | -0.0088115 | 0.010356 | 0.0016025 | -0.053732 | 0.027566 | 0.0074072 | 0.028006 | 0.0044439 | 0.07888 | 0.028878 | 0.032795 | 0.15285 | 0.096516 | 0.33427 | 0.060574 | 0.06515 | 0.036989 | -0.001407 | 0.1074 | 0.21059 | -0.11587 | -0.19162 | 122.137 | 0.033833 | 122.1553 | 122.1092 | -0.027779 | -0.022503 | 0.21525 | 121.8848 | -0.011618 | 122.1416 | 122.075 | 0.19021 | 0.091567 | -0.23489 | 122.2293 | 122.1729 | 122.4107 | 122.1053 | -0.058445 | 122.1838 | 122.287 | 121.9605 | 122.1134 | -0.31064
1867.4688 | 122.2412 | -122.0993 | 0.15106 | 1.4211e-13 | -0.0097179 | 0.021752 | -0.0033377 | -0.0092389 | 0.010784 | 0.0016025 | -0.053732 | 0.027139 | 0.0071936 | 0.027792 | 0.0044439 | 0.069723 | 0.0243 | 0.028217 | 0.16201 | 0.087359 | 0.32969 | 0.065153 | 0.06515 | 0.036989 | -0.005985 | 0.1074 | 0.21974 | -0.11129 | -0.17788 | 122.1645 | 0.010947 | 122.169 | 122.1275 | -0.036936 | -0.063703 | 0.17863 | 121.9214 | -0.043661 | 122.1645 | 122.0933 | 0.1719 | 0.068682 | -0.26236 | 122.2613 | 122.1867 | 122.429 | 122.1236 | -0.085909 | 122.2067 | 122.319 | 121.988 | 122.1363 | -0.32895
1869.1719 | 122.3145 | -122.0352 | 0.1236 | 1.4211e-13 | -0.0097179 | 0.021966 | -0.0033377 | -0.0092389 | 0.010356 | -0.006028 | -0.053732 | 0.027566 | 0.0071936 | 0.027792 | 0.0048713 | 0.074302 | 0.028878 | 0.028217 | 0.15285 | 0.08278 | 0.32511 | 0.046837 | 0.074307 | 0.046146 | -0.010564 | 0.098244 | 0.21059 | -0.11587 | -0.17331 | 122.0821 | 0.029256 | 122.1095 | 122.0634 | -0.01862 | -0.040816 | 0.20151 | 121.8619 | -0.025352 | 122.1095 | 122.0247 | 0.16274 | 0.08699 | -0.23947 | 122.1881 | 122.118 | 122.3603 | 122.0641 | -0.076759 | 122.1335 | 122.2458 | 121.9193 | 122.0814 | -0.2969
1870.9219 | 122.2412 | -122.0764 | 0.14648 | 1.4211e-13 | -0.0099315 | 0.021752 | -0.0031241 | -0.0094525 | 0.01057 | -0.006028 | -0.053732 | 0.027566 | 0.0071936 | 0.027792 | 0.0048713 | 0.069723 | 0.0243 | 0.032795 | 0.15285 | 0.08278 | 0.33427 | 0.07431 | 0.06515 | 0.03241 | 0.003172 | 0.10282 | 0.21059 | -0.11129 | -0.17788 | 122.1507 | 0.006368 | 122.1461 | 122.1092 | -0.041515 | -0.063704 | 0.18778 | 121.8985 | -0.043662 | 122.1416 | 122.0796 | 0.18106 | 0.064102 | -0.25778 | 122.2293 | 122.1592 | 122.4107 | 122.1007 | -0.072174 | 122.1792 | 122.287 | 121.9651 | 122.1088 | -0.32437
1872.625 | 122.3694 | -122.0581 | 0.13275 | 1.4211e-13 | -0.0095041 | 0.021752 | -0.0035515 | -0.0092389 | 0.010356 | -0.006028 | -0.053732 | 0.027353 | 0.0071936 | 0.028006 | 0.0044439 | 0.074302 | 0.0243 | 0.032795 | 0.15743 | 0.096516 | 0.32969 | 0.055995 | 0.06515 | 0.036989 | -0.001407 | 0.11198 | 0.21516 | -0.11587 | -0.16415 | 122.1141 | 0.02468 | 122.1324 | 122.0909 | -0.0232 | -0.036235 | 0.19694 | 121.894 | -0.020772 | 122.1233 | 122.0567 | 0.16274 | 0.082414 | -0.24862 | 122.2155 | 122.1546 | 122.3878 | 122.0824 | -0.076756 | 122.1701 | 122.2733 | 121.9422 | 122.0951 | -0.2969
1874.3906 | 122.3557 | -122.0856 | 0.11902 | 1.4211e-13 | -0.0099315 | 0.021539 | -0.0035515 | -0.0092389 | 0.010356 | -0.013659 | -0.053732 | 0.02778 | 0.0074072 | 0.028006 | 0.0044439 | 0.07888 | 0.019721 | 0.032795 | 0.15743 | 0.096516 | 0.32511 | 0.07431 | 0.060571 | 0.041567 | -0.005985 | 0.1074 | 0.21974 | -0.11587 | -0.16873 | 122.1599 | 0.038412 | 122.1645 | 122.1184 | -0.041515 | -0.022503 | 0.20609 | 121.9168 | -0.011618 | 122.1461 | 122.0796 | 0.16274 | 0.10072 | -0.23489 | 122.243 | 122.1821 | 122.4107 | 122.1053 | -0.044709 | 122.193 | 122.3053 | 121.9697 | 122.1271 | -0.28775
1876.1562 | 122.2641 | -122.0764 | 0.16937 | 1.4211e-13 | -0.0095041 | 0.021752 | -0.0033377 | -0.0092389 | 0.010356 | 0.0092325 | -0.053519 | 0.027994 | 0.0078344 | 0.027579 | 0.0046577 | 0.069723 | 0.0243 | 0.028217 | 0.15743 | 0.091937 | 0.32969 | 0.060574 | 0.06515 | 0.036989 | -0.001407 | 0.10282 | 0.21516 | -0.11587 | -0.15957 | 122.137 | -0.011942 | 122.1461 | 122.1046 | -0.032357 | -0.077436 | 0.16032 | 121.9168 | -0.066551 | 122.1416 | 122.075 | 0.15816 | 0.045792 | -0.28524 | 122.2338 | 122.1684 | 122.4061 | 122.1007 | -0.1088 | 122.1792 | 122.2916 | 121.9605 | 122.1134 | -0.32894
1877.9219 | 122.4014 | -122.0627 | 0.11902 | 1.4211e-13 | -0.0095041 | 0.021966 | -0.0033377 | -0.0094525 | 0.010356 | 0.0016025 | -0.05245 | 0.027566 | 0.0074072 | 0.027792 | 0.0050849 | 0.065145 | 0.019721 | 0.032795 | 0.15285 | 0.087359 | 0.32969 | 0.065153 | 0.06515 | 0.041567 | -0.005985 | 0.10282 | 0.21516 | -0.10671 | -0.15957 | 122.1278 | 0.033833 | 122.1278 | 122.0955 | -0.032358 | -0.03166 | 0.21067 | 121.9031 | -0.016197 | 122.1278 | 122.0567 | 0.15358 | 0.096146 | -0.22573 | 122.2155 | 122.15 | 122.3924 | 122.0824 | -0.053866 | 122.1655 | 122.2778 | 121.956 | 122.1043 | -0.27859
1879.6875 | 122.4014 | -122.0627 | 0.10529 | 1.4211e-13 | -0.0095041 | 0.021966 | -0.0033377 | -0.0092389 | 0.01057 | -0.006028 | -0.052664 | 0.027566 | 0.0074072 | 0.027579 | 0.0044439 | 0.069723 | 0.015142 | 0.032795 | 0.15285 | 0.091937 | 0.33427 | 0.078889 | 0.069728 | 0.041567 | -0.001407 | 0.098244 | 0.21516 | -0.11587 | -0.16873 | 122.1416 | 0.047566 | 122.1324 | 122.0955 | -0.046094 | -0.013349 | 0.22898 | 121.894 | -0.007042 | 122.1324 | 122.0613 | 0.16732 | 0.10988 | -0.22116 | 122.2155 | 122.1546 | 122.397 | 122.0778 | -0.026397 | 122.1609 | 122.2778 | 121.9468 | 122.1043 | -0.27401
1881.4375 | 122.3785 | -122.0673 | 0.15106 | 1.4211e-13 | -0.0097179 | 0.02218 | -0.0029103 | -0.0090251 | 0.009929 | -0.006028 | -0.05245 | 0.027566 | 0.0076208 | 0.02822 | 0.0046577 | 0.074302 | 0.019721 | 0.032795 | 0.16201 | 0.087359 | 0.32969 | 0.037679 | 0.074307 | 0.046146 | -0.010564 | 0.1074 | 0.21516 | -0.11587 | -0.13668 | 122.1049 | 0.010947 | 122.1416 | 122.1001 | -0.004884 | -0.063703 | 0.17863 | 121.9306 | -0.043661 | 122.1416 | 122.0567 | 0.12611 | 0.064103 | -0.26693 | 122.2293 | 122.1546 | 122.397 | 122.087 | -0.11338 | 122.1747 | 122.2824 | 121.9514 | 122.1134 | -0.28774
1883.1406 | 122.4014 | -122.081 | 0.1236 | 1.4211e-13 | -0.0092905 | 0.021752 | -0.0033377 | -0.0090251 | 0.01057 | 0.0016025 | -0.052237 | 0.02778 | 0.0074072 | 0.028006 | 0.0042303 | 0.074302 | 0.0243 | 0.032795 | 0.16201 | 0.096516 | 0.33427 | 0.078889 | 0.074307 | 0.036989 | -0.001407 | 0.1074 | 0.21974 | -0.12045 | -0.16415 | 122.1599 | 0.038413 | 122.1553 | 122.1138 | -0.046094 | -0.02708 | 0.21067 | 121.9168 | -0.016195 | 122.1553 | 122.0796 | 0.16274 | 0.096148 | -0.24405 | 122.243 | 122.1775 | 122.4153 | 122.1053 | -0.044707 | 122.1884 | 122.3007 | 121.9605 | 122.118 | -0.28774
1884.8906 | 122.3785 | -122.0947 | 0.11902 | 1.4211e-13 | -0.0097179 | 0.021966 | -0.0029103 | -0.0092389 | 0.01057 | -0.013659 | -0.052878 | 0.02778 | 0.0076208 | 0.027579 | 0.0046577 | 0.069723 | 0.0243 | 0.032795 | 0.14827 | 0.08278 | 0.33427 | 0.037679 | 0.074307 | 0.041567 | -0.001407 | 0.1074 | 0.20601 | -0.11129 | -0.15957 | 122.1324 | 0.029255 | 122.1645 | 122.1275 | -0.004884 | -0.036239 | 0.21525 | 121.9352 | -0.011618 | 122.169 | 122.0933 | 0.15816 | 0.086989 | -0.23031 | 122.243 | 122.1775 | 122.429 | 122.119 | -0.08134 | 122.2021 | 122.3007 | 121.9834 | 122.1363 | -0.27859
1886.5781 | 122.4152 | -122.1222 | 0.1236 | 1.4211e-13 | -0.0097179 | 0.021752 | -0.0033377 | -0.0090251 | 0.01057 | -0.006028 | -0.052664 | 0.02778 | 0.0076208 | 0.027792 | 0.0046577 | 0.069723 | 0.0243 | 0.028217 | 0.16201 | 0.087359 | 0.32511 | 0.051416 | 0.083464 | 0.041567 | -0.001407 | 0.10282 | 0.21974 | -0.10671 | -0.14583 | 122.1736 | 0.038413 | 122.1919 | 122.1504 | -0.023199 | -0.036237 | 0.20151 | 121.9764 | -0.020774 | 122.2057 | 122.1208 | 0.14443 | 0.096148 | -0.23031 | 122.2842 | 122.2096 | 122.4473 | 122.1465 | -0.07218 | 122.225 | 122.3419 | 122.0155 | 122.1638 | -0.26943
1888.2656 | 122.3236 | -122.1222 | 0.14191 | 1.4211e-13 | -0.0090769 | 0.021966 | -0.0029103 | -0.0090251 | 0.010784 | -0.006028 | -0.052664 | 0.027353 | 0.0074072 | 0.028006 | 0.0044439 | 0.065145 | 0.019721 | 0.028217 | 0.15743 | 0.091937 | 0.32969 | 0.042258 | 0.069728 | 0.041567 | -0.001407 | 0.10282 | 0.21516 | -0.11587 | -0.16415 | 122.1645 | 0.015524 | 122.1873 | 122.1504 | -0.014041 | -0.04997 | 0.18778 | 121.958 | -0.039085 | 122.1919 | 122.1208 | 0.16274 | 0.073258 | -0.25778 | 122.2796 | 122.2141 | 122.4519 | 122.1419 | -0.099649 | 122.225 | 122.3374 | 122.0063 | 122.1638 | -0.30606
1890.0312 | 122.3465 | -122.1313 | 0.13733 | 1.4211e-13 | -0.0097179 | 0.02218 | -0.0033377 | -0.0090251 | 0.010143 | 0.0016025 | -0.052878 | 0.027353 | 0.0074072 | 0.027792 | 0.0044439 | 0.060567 | 0.0243 | 0.023639 | 0.15285 | 0.091937 | 0.32511 | 0.037679 | 0.060571 | 0.041567 | -0.001407 | 0.1074 | 0.21516 | -0.11129 | -0.15499 | 122.169 | 0.015523 | 122.1919 | 122.155 | -0.01404 | -0.045392 | 0.18778 | 121.9764 | -0.029928 | 122.1919 | 122.1299 | 0.15358 | 0.077836 | -0.24862 | 122.2842 | 122.2233 | 122.4565 | 122.1556 | -0.09965 | 122.2387 | 122.3465 | 122.0201 | 122.1729 | -0.29232
1891.7969 | 122.4655 | -122.1039 | 0.10529 | 1.4211e-13 | -0.0095041 | 0.021966 | -0.0033377 | -0.0092389 | 0.010143 | 0.0016025 | -0.052664 | 0.027353 | 0.0071936 | 0.028006 | 0.0048713 | 0.065145 | 0.028878 | 0.01906 | 0.15743 | 0.087359 | 0.33885 | 0.046837 | 0.055992 | 0.050725 | 0.003172 | 0.11198 | 0.20601 | -0.11587 | -0.15957 | 122.1507 | 0.052145 | 122.169 | 122.1229 | -0.027777 | -0.017927 | 0.23356 | 121.9443 | 0.006693 | 122.1599 | 122.1071 | 0.16274 | 0.10072 | -0.22116 | 122.2613 | 122.1912 | 122.4427 | 122.1328 | -0.058449 | 122.2159 | 122.3099 | 121.988 | 122.1546 | -0.26486
1893.5469 | 122.3785 | -122.1268 | 0.1236 | 1.4211e-13 | -0.0099315 | 0.021966 | -0.0033377 | -0.0092389 | 0.010784 | -0.013659 | -0.05245 | 0.027353 | 0.0074072 | 0.028006 | 0.0046577 | 0.074302 | 0.028878 | 0.032795 | 0.14369 | 0.096516 | 0.32511 | 0.055995 | 0.060571 | 0.041567 | -0.005985 | 0.1074 | 0.21516 | -0.11587 | -0.15957 | 122.1828 | 0.020099 | 122.2011 | 122.1596 | -0.0232 | -0.02708 | 0.20151 | 121.9672 | -0.016195 | 122.1873 | 122.1208 | 0.15358 | 0.091569 | -0.23947 | 122.2705 | 122.2233 | 122.4519 | 122.1556 | -0.067601 | 122.2342 | 122.3419 | 122.0109 | 122.1683 | -0.28317
1895.25 | 122.438 | -122.1222 | 0.10986 | 1.4211e-13 | -0.0095041 | 0.021752 | -0.0029103 | -0.0090251 | 0.01057 | -0.006028 | -0.05245 | 0.02778 | 0.0074072 | 0.028006 | 0.0044439 | 0.074302 | 0.0243 | 0.028217 | 0.15285 | 0.091937 | 0.32969 | 0.060574 | 0.060571 | 0.046146 | -0.001407 | 0.1074 | 0.21059 | -0.12503 | -0.16415 | 122.1828 | 0.042989 | 122.1965 | 122.1504 | -0.032357 | -0.017926 | 0.21983 | 121.958 | -0.002462 | 122.1828 | 122.1208 | 0.16274 | 0.10072 | -0.23489 | 122.275 | 122.2141 | 122.4519 | 122.1465 | -0.049289 | 122.2296 | 122.3328 | 121.9972 | 122.1683 | -0.27401
1897 | 122.3373 | -122.1817 | 0.15106 | 1.4211e-13 | -0.0099315 | 0.02218 | -0.0031241 | -0.0094525 | 0.01057 | -0.006028 | -0.05245 | 0.027566 | 0.0074072 | 0.028006 | 0.0046577 | 0.065145 | 0.015142 | 0.032795 | 0.15743 | 0.087359 | 0.32511 | 0.065153 | 0.060571 | 0.036989 | -0.001407 | 0.1074 | 0.21516 | -0.11587 | -0.12752 | 122.2469 | 0.006369 | 122.2468 | 122.2145 | -0.032358 | -0.063703 | 0.17405 | 122.0542 | -0.043661 | 122.2423 | 122.1803 | 0.12611 | 0.064103 | -0.26693 | 122.3391 | 122.2691 | 122.5068 | 122.1968 | -0.085909 | 122.2891 | 122.3969 | 122.0658 | 122.2187 | -0.27858
1898.6875 | 122.3785 | -122.1359 | 0.14191 | 1.4211e-13 | -0.0097179 | 0.021966 | -0.0031241 | -0.0092389 | 0.010143 | -0.006028 | -0.052237 | 0.026712 | 0.0076208 | 0.027792 | 0.0044439 | 0.074302 | 0.019721 | 0.023639 | 0.15743 | 0.091937 | 0.32969 | 0.051416 | 0.069728 | 0.041567 | -0.001407 | 0.1074 | 0.21516 | -0.12045 | -0.12294 | 122.1873 | 0.015524 | 122.2102 | 122.1596 | -0.027777 | -0.04997 | 0.18778 | 122.013 | -0.034506 | 122.2057 | 122.1345 | 0.12153 | 0.073258 | -0.26236 | 122.2934 | 122.2279 | 122.4656 | 122.1556 | -0.090491 | 122.2433 | 122.3511 | 122.0155 | 122.1775 | -0.26485
1900.4375 | 122.3648 | -122.1588 | 0.15106 | 1.4211e-13 | -0.0097179 | 0.021752 | -0.0033377 | -0.0088115 | 0.01057 | -0.006028 | -0.052237 | 0.026284 | 0.0074072 | 0.028006 | 0.0044439 | 0.074302 | 0.019721 | 0.028217 | 0.15285 | 0.087359 | 0.32969 | 0.065153 | 0.051413 | 0.036989 | -0.001407 | 0.11656 | 0.22432 | -0.11587 | -0.12752 | 122.224 | 0.00179 | 122.2331 | 122.187 | -0.036936 | -0.063703 | 0.17863 | 122.0313 | -0.034505 | 122.2102 | 122.1574 | 0.12611 | 0.07326 | -0.26693 | 122.3117 | 122.2462 | 122.4885 | 122.1785 | -0.085909 | 122.2754 | 122.3831 | 122.0429 | 122.1958 | -0.27858
1902.1562 | 122.4335 | -122.1313 | 0.11902 | 1.4211e-13 | -0.0097179 | 0.021539 | -0.0033377 | -0.0088115 | 0.010356 | -0.006028 | -0.05245 | 0.026712 | 0.0074072 | 0.028006 | 0.0042303 | 0.069723 | 0.015142 | 0.028217 | 0.14827 | 0.091937 | 0.32969 | 0.065153 | 0.060571 | 0.03241 | -0.005985 | 0.11198 | 0.21974 | -0.11587 | -0.15041 | 122.1965 | 0.029255 | 122.2011 | 122.1596 | -0.036936 | -0.027082 | 0.21067 | 121.9809 | -0.00704 | 122.1919 | 122.1254 | 0.14443 | 0.10072 | -0.23489 | 122.2796 | 122.2233 | 122.461 | 122.1465 | -0.053866 | 122.2433 | 122.3511 | 122.0155 | 122.1638 | -0.26943
1903.875 | 122.3511 | -122.168 | 0.14191 | 1.4211e-13 | -0.0097179 | 0.021752 | -0.0033377 | -0.0085979 | 0.010356 | -0.006028 | -0.052664 | 0.026712 | 0.0074072 | 0.027792 | 0.0046577 | 0.069723 | 0.019721 | 0.028217 | 0.15743 | 0.087359 | 0.32511 | 0.046837 | 0.060571 | 0.050725 | -0.001407 | 0.1074 | 0.21059 | -0.11587 | -0.13668 | 122.2148 | 0.015524 | 122.2377 | 122.1962 | -0.01862 | -0.054548 | 0.1832 | 122.0313 | -0.034506 | 122.2285 | 122.1666 | 0.13527 | 0.068679 | -0.25778 | 122.3254 | 122.2553 | 122.4931 | 122.1877 | -0.09507 | 122.2754 | 122.3786 | 122.0521 | 122.2187 | -0.27858
1905.6406 | 122.3236 | -122.168 | 0.15106 | 1.4211e-13 | -0.0099315 | 0.021752 | -0.0033377 | -0.0088115 | 0.01057 | -0.006028 | -0.05245 | 0.026284 | 0.0071936 | 0.027792 | 0.0046577 | 0.069723 | 0.0243 | 0.028217 | 0.14827 | 0.08278 | 0.32969 | 0.037679 | 0.060571 | 0.041567 | -0.005985 | 0.1074 | 0.21516 | -0.11129 | -0.13668 | 122.2056 | -0.002788 | 122.2377 | 122.1962 | -0.009462 | -0.068282 | 0.17863 | 122.0313 | -0.043661 | 122.2285 | 122.162 | 0.13069 | 0.064103 | -0.26236 | 122.3162 | 122.2507 | 122.4977 | 122.1923 | -0.11338 | 122.2754 | 122.3831 | 122.0567 | 122.2095 | -0.28774
1907.3906 | 122.3373 | -122.1771 | 0.11902 | 1.4211e-13 | -0.010145 | 0.021752 | -0.0031241 | -0.0090251 | 0.01057 | -0.006028 | -0.052664 | 0.026712 | 0.0076208 | 0.027792 | 0.0042303 | 0.069723 | 0.015142 | 0.028217 | 0.14827 | 0.096516 | 0.32511 | 0.055995 | 0.055992 | 0.041567 | -0.001407 | 0.11198 | 0.21516 | -0.11587 | -0.12752 | 122.2331 | 0.029255 | 122.2468 | 122.2053 | -0.027778 | -0.022503 | 0.20609 | 122.0496 | -0.00704 | 122.2331 | 122.1757 | 0.12611 | 0.096146 | -0.23489 | 122.3254 | 122.2736 | 122.5022 | 122.1923 | -0.063024 | 122.2891 | 122.3923 | 122.0613 | 122.2187 | -0.24654
1909.0938 | 122.3328 | -122.2183 | 0.14191 | 1.4211e-13 | -0.0097179 | 0.02218 | -0.0031241 | -0.0090251 | 0.010356 | 0.0016025 | -0.052023 | 0.026498 | 0.0071936 | 0.027792 | 0.0046577 | 0.065145 | 0.015142 | 0.032795 | 0.14827 | 0.087359 | 0.32969 | 0.065153 | 0.06515 | 0.041567 | -0.010564 | 0.10282 | 0.21974 | -0.11587 | -0.14125 | 122.2835 | 0.006367 | 122.2835 | 122.2511 | -0.032358 | -0.054548 | 0.18778 | 122.0771 | -0.039085 | 122.2835 | 122.2078 | 0.13069 | 0.077837 | -0.25778 | 122.3666 | 122.3057 | 122.548 | 122.2335 | -0.076754 | 122.3211 | 122.4381 | 122.1025 | 122.2599 | -0.28316
1910.8438 | 122.3236 | -122.1588 | 0.14191 | 1.4211e-13 | -0.0097179 | 0.021966 | -0.0031241 | -0.0092389 | 0.010356 | -0.006028 | -0.052664 | 0.026498 | 0.0076208 | 0.028006 | 0.0042303 | 0.060567 | 0.015142 | 0.037373 | 0.15285 | 0.087359 | 0.32511 | 0.055995 | 0.055992 | 0.046146 | -0.005985 | 0.10282 | 0.21974 | -0.12045 | -0.14583 | 122.2148 | 0.010945 | 122.2194 | 122.1962 | -0.018622 | -0.054548 | 0.1832 | 122.013 | -0.039085 | 122.2148 | 122.1528 | 0.13985 | 0.077837 | -0.26236 | 122.3117 | 122.2462 | 122.4839 | 122.174 | -0.085912 | 122.2616 | 122.3786 | 122.0384 | 122.205 | -0.28774
1912.6094 | 122.406 | -122.1725 | 0.13275 | 1.4211e-13 | -0.0095041 | 0.021752 | -0.0031241 | -0.0094525 | 0.010356 | 0.0016025 | -0.052878 | 0.026498 | 0.0069798 | 0.027579 | 0.0044439 | 0.060567 | 0.019721 | 0.023639 | 0.15285 | 0.087359 | 0.32053 | 0.097205 | 0.055992 | 0.041567 | -0.001407 | 0.11198 | 0.21974 | -0.11587 | -0.12294 | 122.2698 | 0.020101 | 122.2331 | 122.1962 | -0.073566 | -0.045392 | 0.18778 | 122.0496 | -0.020772 | 122.2285 | 122.1711 | 0.12153 | 0.086993 | -0.24862 | 122.3254 | 122.2599 | 122.4931 | 122.1923 | -0.035546 | 122.2845 | 122.3923 | 122.0567 | 122.2141 | -0.25569
1914.375 | 122.4426 | -122.1771 | 0.11902 | 1.4211e-13 | -0.0095041 | 0.021752 | -0.0031241 | -0.0088115 | 0.01057 | 0.0016025 | -0.05245 | 0.026284 | 0.0076208 | 0.028006 | 0.0040167 | 0.074302 | 0.015142 | 0.028217 | 0.16201 | 0.091937 | 0.33427 | 0.046837 | 0.06515 | 0.036989 | -0.001407 | 0.10282 | 0.21974 | -0.11587 | -0.14125 | 122.224 | 0.04299 | 122.2514 | 122.2053 | -0.01862 | -0.027082 | 0.21525 | 122.0359 | -0.016197 | 122.2423 | 122.1757 | 0.13985 | 0.10072 | -0.23489 | 122.3391 | 122.2691 | 122.5114 | 122.1923 | -0.072182 | 122.2799 | 122.3969 | 122.0613 | 122.2141 | -0.26027
1916.0625 | 122.4792 | -122.1405 | 0.10071 | 1.4211e-13 | -0.0099315 | 0.02218 | -0.0031241 | -0.0092389 | 0.010356 | 0.0016025 | -0.052878 | 0.026498 | 0.0071936 | 0.027792 | 0.0046577 | 0.069723 | 0.015142 | 0.028217 | 0.15743 | 0.087359 | 0.32969 | 0.037679 | 0.06515 | 0.03241 | 0.003172 | 0.1074 | 0.21974 | -0.11129 | -0.14125 | 122.1782 | 0.056723 | 122.2102 | 122.1687 | -0.009462 | -0.013349 | 0.22898 | 121.9992 | 0.006693 | 122.2057 | 122.1437 | 0.14443 | 0.11904 | -0.212 | 122.2979 | 122.2279 | 122.4702 | 122.1556 | -0.063029 | 122.2479 | 122.3602 | 122.0292 | 122.1729 | -0.24196
1917.8125 | 122.3694 | -122.2275 | 0.16022 | 1.4211e-13 | -0.0097179 | 0.021752 | -0.0035515 | -0.0090251 | 0.010143 | 0.0016025 | -0.05245 | 0.026498 | 0.0069798 | 0.027579 | 0.0046577 | 0.069723 | 0.0243 | 0.028217 | 0.15285 | 0.087359 | 0.32053 | 0.055995 | 0.055992 | 0.041567 | -0.001407 | 0.10282 | 0.21516 | -0.11129 | -0.14125 | 122.2835 | -0.007365 | 122.2972 | 122.2557 | -0.027778 | -0.072858 | 0.16031 | 122.0862 | -0.057395 | 122.2835 | 122.2261 | 0.13985 | 0.054948 | -0.27151 | 122.3803 | 122.3148 | 122.548 | 122.2518 | -0.10422 | 122.3303 | 122.4426 | 122.1162 | 122.269 | -0.30147
1919.5781 | 122.3602 | -122.2183 | 0.15564 | 1.4211e-13 | -0.0095041 | 0.021752 | -0.0033377 | -0.0090251 | 0.010143 | -0.013659 | -0.052878 | 0.026925 | 0.0076208 | 0.028006 | 0.0046577 | 0.074302 | 0.010564 | 0.032795 | 0.15743 | 0.087359 | 0.32511 | 0.0331 | 0.06515 | 0.041567 | 0.003172 | 0.10282 | 0.21059 | -0.11587 | -0.14125 | 122.2514 | 0.001791 | 122.2926 | 122.2511 | -0.000305 | -0.068281 | 0.16947 | 122.0771 | -0.052818 | 122.2835 | 122.2215 | 0.14443 | 0.054946 | -0.27151 | 122.3758 | 122.3057 | 122.5434 | 122.2289 | -0.12254 | 122.3211 | 122.4289 | 122.1025 | 122.2599 | -0.2969
1921.3438 | 122.4518 | -122.1909 | 0.11444 | 1.4211e-13 | -0.0095041 | 0.021752 | -0.0031241 | -0.0092389 | 0.01057 | 0.0092325 | -0.05245 | 0.026284 | 0.0074072 | 0.027792 | 0.0048713 | 0.07888 | 0.019721 | 0.028217 | 0.14827 | 0.087359 | 0.32511 | 0.042258 | 0.069728 | 0.050725 | -0.005985 | 0.098244 | 0.21059 | -0.11587 | -0.14583 | 122.2331 | 0.033833 | 122.2697 | 122.2191 | -0.014041 | -0.027082 | 0.21067 | 122.045 | -0.016197 | 122.2606 | 122.1849 | 0.13985 | 0.096145 | -0.23031 | 122.3391 | 122.2782 | 122.516 | 122.2106 | -0.072183 | 122.2891 | 122.4014 | 122.075 | 122.2416 | -0.26027
1923.0312 | 122.4976 | -122.1909 | 0.12817 | 1.4211e-13 | -0.0097179 | 0.021966 | -0.0035515 | -0.0092389 | 0.010784 | 0.0092325 | -0.052878 | 0.026712 | 0.0071936 | 0.028006 | 0.0044439 | 0.069723 | 0.015142 | 0.028217 | 0.15285 | 0.087359 | 0.32053 | 0.060574 | 0.06515 | 0.041567 | 0.003172 | 0.10282 | 0.21516 | -0.11129 | -0.1321 | 122.2514 | 0.024678 | 122.2606 | 122.2191 | -0.032357 | -0.040815 | 0.19236 | 122.0588 | -0.025352 | 122.256 | 122.194 | 0.13527 | 0.086991 | -0.23947 | 122.3437 | 122.2782 | 122.5114 | 122.206 | -0.0676 | 122.2937 | 122.406 | 122.0796 | 122.2324 | -0.26027
1924.7969 | 122.3785 | -122.2412 | 0.14648 | 1.4211e-13 | -0.0092905 | 0.021966 | -0.0031241 | -0.0092389 | 0.01057 | 0.0016025 | -0.052878 | 0.026712 | 0.0071936 | 0.02822 | 0.0046577 | 0.074302 | 0.010564 | 0.032795 | 0.15285 | 0.087359 | 0.32511 | 0.042258 | 0.060571 | 0.036989 | -0.005985 | 0.1074 | 0.21974 | -0.12045 | -0.10004 | 122.2835 | 0.006368 | 122.3155 | 122.274 | -0.009463 | -0.059125 | 0.17863 | 122.1412 | -0.039083 | 122.3018 | 122.2352 | 0.09406 | 0.07326 | -0.26693 | 122.3941 | 122.3286 | 122.5663 | 122.2518 | -0.10423 | 122.3486 | 122.461 | 122.1208 | 122.2782 | -0.24653
1926.5625 | 122.4426 | -122.1954 | 0.12817 | 1.4211e-13 | -0.0092905 | 0.021966 | -0.0035515 | -0.0092389 | 0.010143 | -0.013659 | -0.052664 | 0.026498 | 0.0076208 | 0.027792 | 0.0048713 | 0.065145 | 0.010564 | 0.032795 | 0.15285 | 0.091937 | 0.32511 | 0.037679 | 0.060571 | 0.041567 | 0.003172 | 0.1074 | 0.21059 | -0.11129 | -0.11836 | 122.2331 | 0.024678 | 122.2606 | 122.2282 | -0.004884 | -0.036237 | 0.19694 | 122.0771 | -0.020773 | 122.256 | 122.1986 | 0.12153 | 0.082412 | -0.23947 | 122.3483 | 122.2874 | 122.5205 | 122.206 | -0.090495 | 122.3028 | 122.406 | 122.0841 | 122.237 | -0.24654
1928.25 | 122.4106 | -122.2183 | 0.14191 | 1.4211e-13 | -0.0095041 | 0.021966 | -0.0031241 | -0.0090251 | 0.010356 | -0.006028 | -0.052878 | 0.026498 | 0.0074072 | 0.028006 | 0.0042303 | 0.074302 | 0.015142 | 0.032795 | 0.14827 | 0.087359 | 0.32053 | 0.060574 | 0.060571 | 0.036989 | -0.001407 | 0.10282 | 0.21516 | -0.10671 | -0.13668 | 122.2789 | 0.006367 | 122.2926 | 122.2511 | -0.027779 | -0.054548 | 0.17862 | 122.0816 | -0.039085 | 122.2789 | 122.2169 | 0.13527 | 0.073258 | -0.24862 | 122.3666 | 122.3057 | 122.5389 | 122.2335 | -0.081333 | 122.3211 | 122.4335 | 122.1116 | 122.2553 | -0.27858
1930 | 122.4014 | -122.2229 | 0.14191 | 1.4211e-13 | -0.0095041 | 0.021966 | -0.0035515 | -0.0090251 | 0.010356 | 0.0016025 | -0.052237 | 0.026498 | 0.0074072 | 0.028006 | 0.0042303 | 0.065145 | 0.010564 | 0.023639 | 0.14827 | 0.08278 | 0.32511 | 0.060574 | 0.055992 | 0.041567 | 0.003172 | 0.1074 | 0.22432 | -0.12045 | -0.11378 | 122.2835 | 0.006367 | 122.288 | 122.2465 | -0.036935 | -0.059127 | 0.1832 | 122.1091 | -0.034506 | 122.2789 | 122.2261 | 0.11695 | 0.082415 | -0.26236 | 122.3712 | 122.3057 | 122.548 | 122.2335 | -0.081333 | 122.3303 | 122.4472 | 122.1024 | 122.2645 | -0.25569
1931.7031 | 122.4518 | -122.2183 | 0.13275 | 1.4211e-13 | -0.0092905 | 0.021752 | -0.0033377 | -0.0092389 | 0.010784 | 0.0016025 | -0.05245 | 0.026498 | 0.0076208 | 0.027579 | 0.0044439 | 0.069723 | 0.015142 | 0.028217 | 0.14827 | 0.08278 | 0.32053 | 0.037679 | 0.060571 | 0.041567 | -0.005985 | 0.1074 | 0.21516 | -0.11129 | -0.11378 | 122.256 | 0.015523 | 122.288 | 122.2465 | -0.009462 | -0.049971 | 0.18778 | 122.1045 | -0.02535 | 122.2789 | 122.2123 | 0.1078 | 0.082414 | -0.24404 | 122.3666 | 122.3011 | 122.5389 | 122.2335 | -0.095072 | 122.3257 | 122.4335 | 122.107 | 122.2599 | -0.24653
1933.3906 | 122.406 | -122.2229 | 0.16022 | 1.4211e-13 | -0.0097179 | 0.021966 | -0.0033377 | -0.0092389 | 0.010143 | 0.0016025 | -0.05245 | 0.026284 | 0.0078344 | 0.028006 | 0.0044439 | 0.060567 | 0.019721 | 0.028217 | 0.15285 | 0.087359 | 0.32053 | 0.055995 | 0.060571 | 0.046146 | -0.001407 | 0.10282 | 0.21059 | -0.11129 | -0.14125 | 122.2789 | -0.007365 | 122.2835 | 122.2511 | -0.027778 | -0.072858 | 0.16031 | 122.0816 | -0.057395 | 122.2835 | 122.2215 | 0.13985 | 0.050369 | -0.27151 | 122.3758 | 122.3103 | 122.5434 | 122.2426 | -0.10422 | 122.3257 | 122.4335 | 122.1116 | 122.269 | -0.30147
1935.0938 | 122.5342 | -122.2046 | 0.11902 | 1.4211e-13 | -0.0092905 | 0.021752 | -0.0033377 | -0.0090251 | 0.01057 | 0.0016025 | -0.052664 | 0.026712 | 0.0074072 | 0.027792 | 0.0044439 | 0.074302 | 0.010564 | 0.032795 | 0.14369 | 0.087359 | 0.32969 | 0.065153 | 0.060571 | 0.041567 | 0.003172 | 0.1074 | 0.20601 | -0.12045 | -0.14125 | 122.2697 | 0.024676 | 122.2789 | 122.2374 | -0.032358 | -0.03166 | 0.21067 | 122.0633 | -0.011618 | 122.2652 | 122.2078 | 0.14443 | 0.086989 | -0.23947 | 122.3483 | 122.2919 | 122.5343 | 122.2152 | -0.053866 | 122.312 | 122.4106 | 122.0841 | 122.2462 | -0.26027
1936.8125 | 122.5159 | -122.2092 | 0.1236 | 1.4211e-13 | -0.0097179 | 0.022393 | -0.0035515 | -0.0090251 | 0.010784 | -0.013659 | -0.052878 | 0.026712 | 0.0076208 | 0.02822 | 0.0046577 | 0.069723 | 0.010564 | 0.037373 | 0.15285 | 0.091937 | 0.32511 | 0.055995 | 0.055992 | 0.041567 | -0.005985 | 0.1074 | 0.20601 | -0.11587 | -0.12752 | 122.2652 | 0.029256 | 122.2789 | 122.2465 | -0.018622 | -0.031659 | 0.20151 | 122.0816 | -0.016195 | 122.2652 | 122.2032 | 0.12153 | 0.082412 | -0.23947 | 122.362 | 122.3011 | 122.5343 | 122.2197 | -0.067601 | 122.3166 | 122.4152 | 122.0933 | 122.2507 | -0.25111
1938.5781 | 122.3923 | -122.2321 | 0.15106 | 1.4211e-13 | -0.0095041 | 0.021752 | -0.0033377 | -0.0092389 | 0.010143 | -0.006028 | -0.052664 | 0.026498 | 0.0074072 | 0.027792 | 0.0046577 | 0.07888 | 0.001407 | 0.028217 | 0.14827 | 0.087359 | 0.32969 | 0.083468 | 0.06515 | 0.041567 | -0.001407 | 0.1074 | 0.21516 | -0.11587 | -0.10462 | 122.3155 | -0.002788 | 122.3109 | 122.2603 | -0.055251 | -0.063703 | 0.17863 | 122.1274 | -0.043661 | 122.2972 | 122.2306 | 0.10322 | 0.064103 | -0.26693 | 122.3803 | 122.3194 | 122.5617 | 122.2335 | -0.067594 | 122.3395 | 122.4472 | 122.1162 | 122.2736 | -0.25569
1940.3438 | 122.4014 | -122.2824 | 0.14191 | 1.4211e-13 | -0.0095041 | 0.021966 | -0.0031241 | -0.0092389 | 0.010143 | -0.006028 | -0.052664 | 0.026712 | 0.0071936 | 0.028006 | 0.0048713 | 0.07888 | 0.010564 | 0.028217 | 0.14827 | 0.078201 | 0.32511 | 0.11094 | 0.06515 | 0.041567 | -0.001407 | 0.11198 | 0.21516 | -0.12503 | -0.077151 | 122.3934 | 0.006367 | 122.3613 | 122.3106 | -0.082725 | -0.063706 | 0.1832 | 122.2053 | -0.029928 | 122.3476 | 122.281 | 0.075744 | 0.073258 | -0.26694 | 122.4307 | 122.3606 | 122.6075 | 122.293 | -0.030965 | 122.3944 | 122.4976 | 122.1574 | 122.324 | -0.21906
1942.0312 | 122.4884 | -122.2366 | 0.11444 | 1.4211e-13 | -0.0099315 | 0.02218 | -0.0033377 | -0.0092389 | 0.01057 | -0.006028 | -0.052664 | 0.026284 | 0.0074072 | 0.028006 | 0.0046577 | 0.065145 | 0.019721 | 0.028217 | 0.14827 | 0.078201 | 0.33427 | 0.083468 | 0.06515 | 0.036989 | -0.001407 | 0.1074 | 0.20601 | -0.11587 | -0.13668 | 122.3201 | 0.033833 | 122.3018 | 122.2648 | -0.055251 | -0.03624 | 0.21983 | 122.1 | -0.00704 | 122.3018 | 122.2352 | 0.13527 | 0.091567 | -0.23031 | 122.3849 | 122.3148 | 122.5709 | 122.2564 | -0.030973 | 122.344 | 122.4426 | 122.1208 | 122.2736 | -0.25112
1943.7969 | 122.5388 | -122.2183 | 0.10986 | 1.4211e-13 | -0.0090769 | 0.021966 | -0.0029103 | -0.0092389 | 0.010356 | -0.006028 | -0.052664 | 0.026284 | 0.0076208 | 0.027792 | 0.0048713 | 0.069723 | 0.010564 | 0.032795 | 0.14369 | 0.087359 | 0.32511 | 0.051416 | 0.060571 | 0.036989 | -0.005985 | 0.098244 | 0.20143 | -0.11129 | -0.12294 | 122.2697 | 0.033832 | 122.288 | 122.2511 | -0.018621 | -0.022504 | 0.21525 | 122.0954 | -0.011619 | 122.2789 | 122.2123 | 0.11695 | 0.091566 | -0.22116 | 122.362 | 122.3057 | 122.5434 | 122.2289 | -0.058447 | 122.3166 | 122.4198 | 122.107 | 122.2553 | -0.2328
1945.5781 | 122.4884 | -122.2321 | 0.13275 | 1.4211e-13 | -0.0092905 | 0.021966 | -0.0031241 | -0.0094525 | 0.010356 | -0.006028 | -0.052664 | 0.026498 | 0.0074072 | 0.028006 | 0.0046577 | 0.069723 | 0.0243 | 0.032795 | 0.15285 | 0.08278 | 0.32511 | 0.065153 | 0.06515 | 0.046146 | -0.005985 | 0.10282 | 0.21059 | -0.11587 | -0.10462 | 122.2972 | 0.020101 | 122.3018 | 122.2649 | -0.032358 | -0.049971 | 0.19236 | 122.1274 | -0.029929 | 122.2972 | 122.2261 | 0.098639 | 0.077835 | -0.24862 | 122.3849 | 122.3148 | 122.5572 | 122.2564 | -0.067598 | 122.3349 | 122.4426 | 122.1162 | 122.2782 | -0.23738
1947.3438 | 122.4609 | -122.2687 | 0.14648 | 1.4211e-13 | -0.0090769 | 0.021752 | -0.0035515 | -0.0092389 | 0.010356 | -0.006028 | -0.052878 | 0.026498 | 0.0076208 | 0.027792 | 0.0046577 | 0.069723 | 0.005985 | 0.032795 | 0.15743 | 0.08278 | 0.32053 | 0.028521 | 0.06515 | 0.041567 | -0.005985 | 0.11198 | 0.21059 | -0.12045 | -0.10004 | 122.2972 | 0.010947 | 122.3384 | 122.3015 | 0.004274 | -0.063704 | 0.17405 | 122.1686 | -0.034505 | 122.3338 | 122.2627 | 0.09406 | 0.064102 | -0.26693 | 122.4261 | 122.3515 | 122.5892 | 122.2747 | -0.11796 | 122.3807 | 122.4793 | 122.1482 | 122.3102 | -0.24653
1949.0312 | 122.3969 | -122.287 | 0.14191 | 1.4211e-13 | -0.0099315 | 0.021966 | -0.0031241 | -0.0092389 | 0.01057 | -0.006028 | -0.052878 | 0.026498 | 0.0071936 | 0.027792 | 0.0040167 | 0.060567 | 0.019721 | 0.032795 | 0.15285 | 0.08278 | 0.32511 | 0.055995 | 0.06515 | 0.041567 | -0.005985 | 0.10282 | 0.20601 | -0.12045 | -0.086309 | 122.343 | 0.010945 | 122.3476 | 122.3198 | -0.0232 | -0.059127 | 0.1832 | 122.2007 | -0.039085 | 122.3521 | 122.281 | 0.080324 | 0.064101 | -0.26236 | 122.4398 | 122.3698 | 122.6121 | 122.3067 | -0.085912 | 122.3898 | 122.493 | 122.1665 | 122.3286 | -0.22822
1950.7969 | 122.4335 | -122.2778 | 0.14191 | 1.4211e-13 | -0.0097179 | 0.021966 | -0.0031241 | -0.0094525 | 0.01057 | 0.0016025 | -0.052664 | 0.026284 | 0.0074072 | 0.027792 | 0.0044439 | 0.060567 | 0.010564 | 0.037373 | 0.14369 | 0.08278 | 0.32053 | 0.07431 | 0.060571 | 0.041567 | -0.010564 | 0.10282 | 0.21059 | -0.11587 | -0.11836 | 122.3521 | 0.001788 | 122.3384 | 122.3152 | -0.036937 | -0.059127 | 0.17862 | 122.1595 | -0.039085 | 122.3384 | 122.2673 | 0.1078 | 0.068679 | -0.25778 | 122.4215 | 122.3606 | 122.5984 | 122.2884 | -0.067597 | 122.3807 | 122.4884 | 122.162 | 122.3194 | -0.26027
1952.5469 | 122.4243 | -122.2641 | 0.15106 | 1.4211e-13 | -0.0097179 | 0.02218 | -0.0035515 | -0.0088115 | 0.010356 | 0.0016025 | -0.05245 | 0.026498 | 0.0074072 | 0.027792 | 0.0046577 | 0.060567 | 0.010564 | 0.023639 | 0.14827 | 0.087359 | 0.32511 | 0.055995 | 0.069728 | 0.036989 | -0.010564 | 0.10282 | 0.21974 | -0.11129 | -0.13668 | 122.3201 | -0.002788 | 122.3247 | 122.2877 | -0.032356 | -0.063703 | 0.17405 | 122.1274 | -0.04824 | 122.3338 | 122.2535 | 0.12611 | 0.068682 | -0.26236 | 122.4124 | 122.3515 | 122.5892 | 122.2747 | -0.095067 | 122.3669 | 122.4838 | 122.1528 | 122.3011 | -0.28774
1954.25 | 122.5159 | -122.2687 | 0.10529 | 1.4211e-13 | -0.0097179 | 0.02218 | -0.0033377 | -0.0090251 | 0.01057 | -0.013659 | -0.052664 | 0.026712 | 0.0069798 | 0.028006 | 0.0044439 | 0.065145 | 0.019721 | 0.032795 | 0.14827 | 0.087359 | 0.32053 | 0.055995 | 0.06515 | 0.041567 | 0.003172 | 0.10282 | 0.20601 | -0.11587 | -0.11378 | 122.3247 | 0.042988 | 122.3338 | 122.3015 | -0.0232 | -0.017927 | 0.21525 | 122.1549 | -0.002464 | 122.3338 | 122.2718 | 0.11695 | 0.10072 | -0.22116 | 122.417 | 122.356 | 122.5892 | 122.2884 | -0.049291 | 122.3715 | 122.4747 | 122.1528 | 122.3102 | -0.21907
1956.0156 | 122.5204 | -122.2733 | 0.10529 | 1.4211e-13 | -0.0097179 | 0.02218 | -0.0035515 | -0.0094525 | 0.010356 | 0.0016025 | -0.052878 | 0.026925 | 0.0071936 | 0.02822 | 0.0044439 | 0.074302 | 0.019721 | 0.028217 | 0.14827 | 0.091937 | 0.32511 | 0.046837 | 0.055992 | 0.050725 | -0.010564 | 0.10282 | 0.21516 | -0.12045 | -0.11378 | 122.3201 | 0.042988 | 122.3476 | 122.3015 | -0.01862 | -0.013349 | 0.21982 | 122.1595 | -0.002464 | 122.3292 | 122.2627 | 0.10322 | 0.10988 | -0.22574 | 122.4215 | 122.3652 | 122.5984 | 122.293 | -0.058449 | 122.3761 | 122.4884 | 122.1528 | 122.324 | -0.21907
1957.7812 | 122.58 | -122.2549 | 0.10986 | 1.4211e-13 | -0.0095041 | 0.021966 | -0.0033377 | -0.0090251 | 0.010143 | 0.0016025 | -0.052664 | 0.026712 | 0.0069798 | 0.027792 | 0.0042303 | 0.065145 | 0.010564 | 0.023639 | 0.14827 | 0.087359 | 0.32053 | 0.051416 | 0.06515 | 0.046146 | -0.005985 | 0.1074 | 0.21059 | -0.11129 | -0.11836 | 122.3064 | 0.038411 | 122.3201 | 122.2786 | -0.027777 | -0.022504 | 0.21067 | 122.1366 | -0.002462 | 122.3201 | 122.249 | 0.11238 | 0.10072 | -0.22116 | 122.4032 | 122.3423 | 122.5755 | 122.2655 | -0.058447 | 122.3623 | 122.4655 | 122.1437 | 122.3011 | -0.22822
1959.5625 | 122.438 | -122.2824 | 0.13733 | 1.4211e-13 | -0.0092905 | 0.022393 | -0.0037651 | -0.0088115 | 0.010356 | -0.013659 | -0.05245 | 0.026498 | 0.0074072 | 0.028006 | 0.0044439 | 0.074302 | 0.005985 | 0.032795 | 0.14827 | 0.08278 | 0.32053 | 0.051416 | 0.055992 | 0.041567 | -0.005985 | 0.098244 | 0.21059 | -0.12045 | -0.10004 | 122.3338 | 0.010945 | 122.3567 | 122.3152 | -0.018621 | -0.054549 | 0.1832 | 122.1824 | -0.039085 | 122.3384 | 122.2764 | 0.09406 | 0.073257 | -0.25778 | 122.4307 | 122.3652 | 122.6029 | 122.2884 | -0.085913 | 122.3807 | 122.493 | 122.162 | 122.324 | -0.23737
1961.25 | 122.5204 | -122.2687 | 0.1236 | 1.4211e-13 | -0.0092905 | 0.02218 | -0.0033377 | -0.0094525 | 0.010356 | -0.006028 | -0.05245 | 0.026498 | 0.0071936 | 0.027792 | 0.0042303 | 0.065145 | 0.015142 | 0.028217 | 0.14369 | 0.078201 | 0.32511 | 0.046837 | 0.069728 | 0.036989 | -0.001407 | 0.1074 | 0.21059 | -0.10671 | -0.095467 | 122.3155 | 0.020099 | 122.3338 | 122.2969 | -0.01862 | -0.045395 | 0.20151 | 122.1732 | -0.016195 | 122.3384 | 122.2673 | 0.09406 | 0.08699 | -0.23031 | 122.4124 | 122.3469 | 122.5938 | 122.2838 | -0.076759 | 122.3761 | 122.4793 | 122.162 | 122.3057 | -0.21906
1963 | 122.4472 | -122.2916 | 0.13275 | 1.4211e-13 | -0.0095041 | 0.021966 | -0.0033377 | -0.0090251 | 0.010356 | -0.006028 | -0.052237 | 0.026284 | 0.0071936 | 0.028006 | 0.0044439 | 0.074302 | 0.010564 | 0.032795 | 0.14827 | 0.078201 | 0.32511 | 0.046837 | 0.055992 | 0.046146 | 0.003172 | 0.10282 | 0.21059 | -0.12045 | -0.10462 | 122.3384 | 0.015523 | 122.3659 | 122.3244 | -0.014042 | -0.05455 | 0.19236 | 122.1869 | -0.029929 | 122.3476 | 122.2947 | 0.1078 | 0.077835 | -0.2532 | 122.4398 | 122.3698 | 122.6167 | 122.3021 | -0.085914 | 122.3944 | 122.5022 | 122.1711 | 122.3377 | -0.23738
1964.7656 | 122.5113 | -122.2549 | 0.11902 | 1.4211e-13 | -0.0092905 | 0.021966 | -0.0035515 | -0.0092389 | 0.010356 | 0.0016025 | -0.052878 | 0.026498 | 0.0071936 | 0.027792 | 0.0046577 | 0.074302 | 0.010564 | 0.028217 | 0.14827 | 0.08278 | 0.32969 | 0.065153 | 0.060571 | 0.046146 | -0.005985 | 0.1074 | 0.21059 | -0.11587 | -0.1321 | 122.3201 | 0.029255 | 122.3292 | 122.2832 | -0.036936 | -0.036239 | 0.21067 | 122.1228 | -0.011618 | 122.3155 | 122.249 | 0.12611 | 0.091567 | -0.23489 | 122.4032 | 122.3377 | 122.5846 | 122.2655 | -0.053866 | 122.3623 | 122.4655 | 122.1391 | 122.3011 | -0.25112
1966.5312 | 122.5342 | -122.2961 | 0.1236 | 1.4211e-13 | -0.0092905 | 0.021752 | -0.0031241 | -0.0088115 | 0.010143 | 0.0016025 | -0.052664 | 0.026284 | 0.0074072 | 0.027792 | 0.0044439 | 0.069723 | 0.015142 | 0.023639 | 0.14369 | 0.078201 | 0.32969 | 0.042258 | 0.060571 | 0.046146 | -0.001407 | 0.098244 | 0.21059 | -0.12045 | -0.11836 | 122.3384 | 0.020099 | 122.3659 | 122.3198 | -0.018619 | -0.045395 | 0.20609 | 122.1778 | -0.025352 | 122.3567 | 122.2947 | 0.11695 | 0.08699 | -0.24405 | 122.4398 | 122.3743 | 122.6258 | 122.3113 | -0.081338 | 122.3944 | 122.5067 | 122.1757 | 122.3423 | -0.24196
1968.2969 | 122.5983 | -122.2687 | 0.10529 | 1.4211e-13 | -0.0095041 | 0.021752 | -0.0033377 | -0.0094525 | 0.010356 | -0.006028 | -0.052237 | 0.026712 | 0.0071936 | 0.02822 | 0.0044439 | 0.069723 | 0.015142 | 0.028217 | 0.15285 | 0.078201 | 0.32511 | 0.042258 | 0.06515 | 0.036989 | -0.001407 | 0.10282 | 0.20601 | -0.11129 | -0.1092 | 122.3109 | 0.047566 | 122.3384 | 122.2969 | -0.014041 | -0.027085 | 0.21982 | 122.1595 | -0.002464 | 122.3338 | 122.2673 | 0.1078 | 0.10072 | -0.21658 | 122.4215 | 122.3469 | 122.5938 | 122.2838 | -0.063028 | 122.3715 | 122.4747 | 122.1574 | 122.3057 | -0.21449
1969.9844 | 122.4564 | -122.3236 | 0.15564 | 1.4211e-13 | -0.0092905 | 0.021752 | -0.0035515 | -0.0090251 | 0.01057 | -0.006028 | -0.052237 | 0.026284 | 0.0078344 | 0.028006 | 0.0042303 | 0.065145 | 0.010564 | 0.041952 | 0.14369 | 0.08278 | 0.32969 | 0.042258 | 0.060571 | 0.046146 | -0.001407 | 0.10282 | 0.20601 | -0.12045 | -0.095467 | 122.3659 | -0.011945 | 122.3888 | 122.3656 | -0.000306 | -0.07286 | 0.17405 | 122.2281 | -0.052818 | 122.3842 | 122.3222 | 0.09406 | 0.050368 | -0.27609 | 122.4673 | 122.4064 | 122.6533 | 122.3342 | -0.11338 | 122.4264 | 122.5296 | 122.2032 | 122.3698 | -0.25111
1971.7344 | 122.5616 | -122.2824 | 0.11444 | 1.4211e-13 | -0.0095041 | 0.02218 | -0.0033377 | -0.0090251 | 0.010143 | 0.0016025 | -0.052878 | 0.026712 | 0.0071936 | 0.028006 | 0.0046577 | 0.065145 | 0.015142 | 0.028217 | 0.15285 | 0.078201 | 0.32053 | 0.028521 | 0.051413 | 0.036989 | -0.001407 | 0.1074 | 0.21516 | -0.11587 | -0.11836 | 122.3109 | 0.038411 | 122.3476 | 122.3106 | -0.000304 | -0.03624 | 0.20609 | 122.164 | -0.00704 | 122.3338 | 122.281 | 0.11695 | 0.10072 | -0.23031 | 122.4353 | 122.3606 | 122.6029 | 122.2976 | -0.08592 | 122.3898 | 122.4976 | 122.1665 | 122.3194 | -0.2328
1973.5 | 122.493 | -122.319 | 0.15106 | 1.4211e-13 | -0.0090769 | 0.021966 | -0.0033377 | -0.0090251 | 0.010356 | -0.006028 | -0.052237 | 0.026498 | 0.0076208 | 0.028006 | 0.0044439 | 0.060567 | 0.001407 | 0.032795 | 0.14827 | 0.087359 | 0.32053 | 0.060574 | 0.06515 | 0.036989 | -0.001407 | 0.10282 | 0.21974 | -0.12045 | -0.10004 | 122.3796 | -0.002788 | 122.3796 | 122.3518 | -0.027779 | -0.063703 | 0.16947 | 122.219 | -0.04824 | 122.3842 | 122.3176 | 0.098638 | 0.068682 | -0.27151 | 122.4673 | 122.4064 | 122.6396 | 122.3204 | -0.090488 | 122.4219 | 122.5388 | 122.1986 | 122.356 | -0.25111
1975.1875 | 122.5708 | -122.2824 | 0.1236 | 1.4211e-13 | -0.0095041 | 0.021966 | -0.0029103 | -0.0092389 | 0.009929 | 0.0092325 | -0.052664 | 0.026498 | 0.0071936 | 0.027792 | 0.0042303 | 0.065145 | 0.010564 | 0.028217 | 0.15285 | 0.078201 | 0.32053 | 0.028521 | 0.06515 | 0.041567 | 0.003172 | 0.1074 | 0.21516 | -0.10671 | -0.11836 | 122.3109 | 0.029256 | 122.3476 | 122.3106 | -0.000304 | -0.045395 | 0.19694 | 122.164 | -0.016195 | 122.3476 | 122.2856 | 0.12153 | 0.091569 | -0.23031 | 122.4353 | 122.3606 | 122.6029 | 122.293 | -0.095075 | 122.3898 | 122.4976 | 122.1757 | 122.324 | -0.24196
1976.9531 | 122.5113 | -122.3282 | 0.13733 | 1.4211e-13 | -0.0097179 | 0.021966 | -0.0033377 | -0.0090251 | 0.010356 | 0.0016025 | -0.05245 | 0.026071 | 0.0071936 | 0.028006 | 0.0044439 | 0.065145 | 0.015142 | 0.032795 | 0.14827 | 0.078201 | 0.32511 | 0.065153 | 0.051413 | 0.041567 | -0.005985 | 0.1074 | 0.20601 | -0.11129 | -0.10462 | 122.3933 | 0.010945 | 122.3933 | 122.361 | -0.032358 | -0.059128 | 0.18778 | 122.2236 | -0.029928 | 122.3796 | 122.3222 | 0.098639 | 0.068679 | -0.24862 | 122.4765 | 122.4064 | 122.6533 | 122.3433 | -0.072176 | 122.4356 | 122.5342 | 122.2169 | 122.3698 | -0.24195
1978.7031 | 122.4564 | -122.3145 | 0.15564 | 1.4211e-13 | -0.0095041 | 0.021966 | -0.0031241 | -0.0090251 | 0.010143 | -0.006028 | -0.052664 | 0.026712 | 0.0074072 | 0.028433 | 0.0042303 | 0.065145 | 0.015142 | 0.028217 | 0.15285 | 0.08278 | 0.32511 | 0.042258 | 0.06515 | 0.041567 | -0.005985 | 0.1074 | 0.21516 | -0.11129 | -0.090888 | 122.3567 | -0.002788 | 122.3796 | 122.3427 | -0.014041 | -0.07286 | 0.16947 | 122.2236 | -0.048239 | 122.3796 | 122.3085 | 0.084903 | 0.059525 | -0.26693 | 122.4673 | 122.3972 | 122.6396 | 122.3296 | -0.11338 | 122.4219 | 122.5296 | 122.2032 | 122.356 | -0.24653
1980.4062 | 122.6074 | -122.2778 | 0.10986 | 1.4211e-13 | -0.0092905 | 0.021752 | -0.0035515 | -0.0088115 | 0.010143 | -0.021289 | -0.052878 | 0.026498 | 0.0078344 | 0.028006 | 0.0040167 | 0.069723 | 0.010564 | 0.028217 | 0.14827 | 0.087359 | 0.32511 | 0.028521 | 0.060571 | 0.041567 | 0.003172 | 0.1074 | 0.20601 | -0.11129 | -0.12294 | 122.3064 | 0.038411 | 122.3476 | 122.306 | -0.000304 | -0.022504 | 0.21525 | 122.1549 | -0.002462 | 122.3384 | 122.281 | 0.12611 | 0.096145 | -0.22116 | 122.4261 | 122.3652 | 122.6029 | 122.2884 | -0.081342 | 122.3852 | 122.4838 | 122.1665 | 122.3194 | -0.2328
1982.1094 | 122.4655 | -122.319 | 0.13275 | 1.4211e-13 | -0.0092905 | 0.021966 | -0.0035515 | -0.0096661 | 0.010356 | -0.013659 | -0.052878 | 0.026498 | 0.0076208 | 0.027792 | 0.0042303 | 0.069723 | 0.005985 | 0.028217 | 0.14827 | 0.087359 | 0.32511 | 0.051416 | 0.06515 | 0.041567 | -0.001407 | 0.10282 | 0.21059 | -0.11129 | -0.10004 | 122.3704 | 0.015523 | 122.3888 | 122.3472 | -0.023199 | -0.045392 | 0.19236 | 122.219 | -0.029929 | 122.3842 | 122.3176 | 0.098638 | 0.077835 | -0.24404 | 122.4673 | 122.4064 | 122.6441 | 122.325 | -0.081335 | 122.4219 | 122.5296 | 122.2077 | 122.3606 | -0.2328
1983.8594 | 122.5571 | -122.2961 | 0.1236 | 1.4211e-13 | -0.0092905 | 0.021966 | -0.0033377 | -0.0098799 | 0.010143 | -0.006028 | -0.052664 | 0.026712 | 0.0069798 | 0.02822 | 0.0042303 | 0.069723 | 0.010564 | 0.028217 | 0.15285 | 0.087359 | 0.32511 | 0.042258 | 0.06515 | 0.03241 | 0.003172 | 0.10282 | 0.21974 | -0.12045 | -0.11378 | 122.3384 | 0.029256 | 122.3659 | 122.3244 | -0.014041 | -0.036237 | 0.20151 | 122.1824 | -0.020774 | 122.3613 | 122.2993 | 0.11695 | 0.096148 | -0.24405 | 122.449 | 122.3835 | 122.6213 | 122.3067 | -0.081338 | 122.399 | 122.5159 | 122.1757 | 122.3286 | -0.23738
1985.5625 | 122.4701 | -122.3236 | 0.13275 | 1.4211e-13 | -0.0092905 | 0.021966 | -0.0033377 | -0.0094525 | 0.010356 | 0.0092325 | -0.052878 | 0.026498 | 0.0074072 | 0.027792 | 0.0044439 | 0.074302 | 0.005985 | 0.032795 | 0.14369 | 0.073622 | 0.32053 | 0.046837 | 0.060571 | 0.041567 | 0.003172 | 0.10282 | 0.21059 | -0.11129 | -0.1092 | 122.3704 | 0.010944 | 122.3979 | 122.3564 | -0.014042 | -0.059129 | 0.18778 | 122.2144 | -0.029929 | 122.3842 | 122.3268 | 0.11237 | 0.077835 | -0.24404 | 122.4673 | 122.3972 | 122.6441 | 122.3296 | -0.085914 | 122.4264 | 122.5342 | 122.2123 | 122.3652 | -0.24195
1987.2656 | 122.5708 | -122.3099 | 0.10071 | 1.4211e-13 | -0.0095041 | 0.02218 | -0.0031241 | -0.0094525 | 0.010356 | -0.006028 | -0.052878 | 0.026498 | 0.0074072 | 0.028006 | 0.0044439 | 0.069723 | 0.015142 | 0.032795 | 0.14827 | 0.087359 | 0.32969 | 0.051416 | 0.060571 | 0.050725 | -0.005985 | 0.11198 | 0.21059 | -0.11129 | -0.10462 | 122.3613 | 0.047566 | 122.3796 | 122.3427 | -0.018621 | -0.013349 | 0.22898 | 122.2053 | 0.011271 | 122.3704 | 122.3039 | 0.098639 | 0.10988 | -0.212 | 122.4581 | 122.3972 | 122.6396 | 122.325 | -0.049292 | 122.4219 | 122.5205 | 122.1986 | 122.3606 | -0.20533
1988.9531 | 122.6028 | -122.3145 | 0.12817 | 1.4211e-13 | -0.0092905 | 0.021966 | -0.0035515 | -0.0090251 | 0.010143 | 0.0016025 | -0.053091 | 0.026498 | 0.0076208 | 0.027792 | 0.0042303 | 0.074302 | 0.010564 | 0.032795 | 0.14369 | 0.08278 | 0.32511 | 0.028521 | 0.069728 | 0.041567 | -0.005985 | 0.1074 | 0.21059 | -0.11587 | -0.11378 | 122.343 | 0.015521 | 122.3888 | 122.3472 | 0.004274 | -0.045394 | 0.19694 | 122.2007 | -0.020773 | 122.3842 | 122.3085 | 0.1078 | 0.082412 | -0.24405 | 122.4581 | 122.3972 | 122.6396 | 122.325 | -0.099653 | 122.4219 | 122.525 | 122.1986 | 122.356 | -0.24196
1990.7344 | 122.5433 | -122.3373 | 0.10986 | 1.4211e-13 | -0.0092905 | 0.021966 | -0.0033377 | -0.0090251 | 0.010143 | 0.0016025 | -0.052664 | 0.026498 | 0.0074072 | 0.028006 | 0.0042303 | 0.069723 | 0.010564 | 0.028217 | 0.14827 | 0.08278 | 0.32053 | 0.042258 | 0.074307 | 0.046146 | -0.001407 | 0.1074 | 0.21059 | -0.10671 | -0.10004 | 122.3796 | 0.038411 | 122.4071 | 122.3656 | -0.014041 | -0.027083 | 0.21067 | 122.2373 | -0.002462 | 122.4116 | 122.3359 | 0.098638 | 0.10072 | -0.21658 | 122.4856 | 122.4201 | 122.6579 | 122.3479 | -0.067605 | 122.4447 | 122.5479 | 122.2306 | 122.3835 | -0.20991
1992.5 | 122.5983 | -122.3236 | 0.13275 | 1.4211e-13 | -0.0092905 | 0.02218 | -0.0033377 | -0.0090251 | 0.010143 | 0.0016025 | -0.05245 | 0.026712 | 0.0074072 | 0.028006 | 0.0044439 | 0.069723 | 0.015142 | 0.028217 | 0.14827 | 0.078201 | 0.32053 | 0.023942 | 0.055992 | 0.036989 | -0.005985 | 0.10282 | 0.21516 | -0.12045 | -0.095467 | 122.3475 | 0.015523 | 122.3933 | 122.3518 | 0.004275 | -0.05455 | 0.18778 | 122.2281 | -0.029929 | 122.3796 | 122.3176 | 0.089482 | 0.082414 | -0.2532 | 122.4719 | 122.4018 | 122.6441 | 122.3387 | -0.10881 | 122.4264 | 122.5388 | 122.2032 | 122.3606 | -0.22822
1994.25 | 122.5159 | -122.3694 | 0.14648 | 1.4211e-13 | -0.0095041 | 0.021752 | -0.0033377 | -0.0092389 | 0.01057 | -0.006028 | -0.052664 | 0.026712 | 0.0076208 | 0.028006 | 0.0044439 | 0.065145 | 0.005985 | 0.023639 | 0.15285 | 0.091937 | 0.32053 | 0.069732 | 0.055992 | 0.041567 | -0.001407 | 0.1074 | 0.21516 | -0.12045 | -0.11836 | 122.4391 | 0.006368 | 122.4345 | 122.393 | -0.046093 | -0.054547 | 0.17405 | 122.251 | -0.039083 | 122.4254 | 122.368 | 0.11695 | 0.068681 | -0.26693 | 122.5222 | 122.4613 | 122.6899 | 122.3754 | -0.076752 | 122.4768 | 122.5845 | 122.2489 | 122.411 | -0.26484
1995.9531 | 122.5067 | -122.3419 | 0.14191 | 1.4211e-13 | -0.0092905 | 0.021752 | -0.0029103 | -0.0094525 | 0.01057 | -0.006028 | -0.052664 | 0.026284 | 0.0071936 | 0.028006 | 0.0044439 | 0.060567 | 0.015142 | 0.028217 | 0.14827 | 0.08278 | 0.33427 | 0.051416 | 0.055992 | 0.036989 | -0.001407 | 0.098244 | 0.21974 | -0.11587 | -0.11836 | 122.3933 | 0.006367 | 122.4025 | 122.3701 | -0.023199 | -0.059127 | 0.19236 | 122.2236 | -0.043663 | 122.3979 | 122.3405 | 0.11695 | 0.077837 | -0.25778 | 122.4902 | 122.4247 | 122.6762 | 122.3571 | -0.090491 | 122.4402 | 122.5617 | 122.226 | 122.3789 | -0.26027
1997.7031 | 122.493 | -122.3648 | 0.15106 | 1.4211e-13 | -0.0095041 | 0.021752 | -0.0033377 | -0.0090251 | 0.010356 | -0.006028 | -0.053091 | 0.026498 | 0.0069798 | 0.02822 | 0.0042303 | 0.069723 | 0.005985 | 0.028217 | 0.14369 | 0.08278 | 0.32511 | 0.037679 | 0.055992 | 0.041567 | -0.001407 | 0.1074 | 0.21059 | -0.11587 | -0.11836 | 122.4025 | -0.007367 | 122.4345 | 122.393 | -0.009462 | -0.068282 | 0.17405 | 122.2464 | -0.043661 | 122.4208 | 122.3634 | 0.11695 | 0.059524 | -0.26693 | 122.5085 | 122.4476 | 122.6899 | 122.3708 | -0.11338 | 122.4722 | 122.5754 | 122.2489 | 122.4064 | -0.26942
1999.4688 | 122.5021 | -122.374 | 0.14191 | 1.4211e-13 | -0.0090769 | 0.021966 | -0.0031241 | -0.0094525 | 0.010143 | -0.013659 | -0.052664 | 0.026925 | 0.0074072 | 0.02822 | 0.0042303 | 0.069723 | 0.015142 | 0.028217 | 0.15285 | 0.08278 | 0.32053 | 0.046837 | 0.051413 | 0.03241 | -0.005985 | 0.1074 | 0.21516 | -0.11129 | -0.1321 | 122.4208 | 0.010945 | 122.4437 | 122.4022 | -0.01862 | -0.059127 | 0.17862 | 122.2419 | -0.034506 | 122.4254 | 122.368 | 0.12611 | 0.073258 | -0.2532 | 122.5268 | 122.4567 | 122.6945 | 122.3891 | -0.09507 | 122.4814 | 122.5891 | 122.2627 | 122.4064 | -0.274
2001.2344 | 122.6532 | -122.3145 | 0.10071 | 1.4211e-13 | -0.0095041 | 0.021966 | -0.0035515 | -0.0088115 | 0.01057 | 0.0016025 | -0.052664 | 0.026498 | 0.0074072 | 0.02822 | 0.0042303 | 0.074302 | 0.005985 | 0.032795 | 0.14827 | 0.08278 | 0.32511 | 0.037679 | 0.060571 | 0.046146 | -0.010564 | 0.1074 | 0.21059 | -0.11587 | -0.11836 | 122.3521 | 0.047566 | 122.3888 | 122.3472 | -0.004884 | -0.017928 | 0.2244 | 122.1961 | 0.006693 | 122.375 | 122.3039 | 0.1078 | 0.10988 | -0.21658 | 122.4627 | 122.3972 | 122.6396 | 122.3204 | -0.063029 | 122.4219 | 122.525 | 122.1986 | 122.3606 | -0.21907
2003 | 122.5204 | -122.3923 | 0.14648 | 1.4211e-13 | -0.0092905 | 0.021752 | -0.0033377 | -0.0088115 | 0.010784 | 0.0016025 | -0.05245 | 0.026712 | 0.0076208 | 0.028006 | 0.0044439 | 0.065145 | 0.015142 | 0.023639 | 0.14827 | 0.078201 | 0.32511 | 0.046837 | 0.074307 | 0.041567 | -0.005985 | 0.10282 | 0.20601 | -0.11129 | -0.095467 | 122.4391 | 0.00179 | 122.4574 | 122.4159 | -0.023198 | -0.068283 | 0.17863 | 122.2968 | -0.043662 | 122.4666 | 122.3863 | 0.089482 | 0.059524 | -0.25778 | 122.5405 | 122.4705 | 122.7174 | 122.4074 | -0.099647 | 122.4951 | 122.5983 | 122.281 | 122.4338 | -0.24195
2004.7031 | 122.5708 | -122.3694 | 0.14648 | 1.4211e-13 | -0.0092905 | 0.021966 | -0.0033377 | -0.0092389 | 0.01057 | 0.0016025 | -0.05245 | 0.026712 | 0.0074072 | 0.028006 | 0.0044439 | 0.055988 | 0.015142 | 0.028217 | 0.14827 | 0.087359 | 0.32969 | 0.028521 | 0.069728 | 0.041567 | 0.003172 | 0.10282 | 0.20601 | -0.10671 | -0.12752 | 122.3979 | 0.00179 | 122.4254 | 122.3976 | -0.000304 | -0.059125 | 0.18321 | 122.2419 | -0.043662 | 122.4391 | 122.3726 | 0.13069 | 0.059524 | -0.2532 | 122.5177 | 122.4567 | 122.6991 | 122.3845 | -0.11796 | 122.4722 | 122.5754 | 122.2627 | 122.411 | -0.274
2006.4688 | 122.6212 | -122.3694 | 0.11902 | 1.4211e-13 | -0.0092905 | 0.021539 | -0.0035515 | -0.0090251 | 0.010143 | 0.0016025 | -0.05245 | 0.026712 | 0.0074072 | 0.02822 | 0.0046577 | 0.074302 | 0.005985 | 0.041952 | 0.13912 | 0.078201 | 0.32511 | 0.019363 | 0.078886 | 0.041567 | -0.010564 | 0.10282 | 0.20143 | -0.097557 | -0.11836 | 122.3887 | 0.020098 | 122.4437 | 122.4113 | 0.022589 | -0.040818 | 0.20609 | 122.251 | -0.016197 | 122.4483 | 122.3588 | 0.1078 | 0.08241 | -0.21658 | 122.5085 | 122.4476 | 122.6945 | 122.3754 | -0.099656 | 122.4722 | 122.5708 | 122.2718 | 122.411 | -0.23738
2008.2188 | 122.6486 | -122.3099 | 0.11444 | 1.4211e-13 | -0.0092905 | 0.02218 | -0.0035515 | -0.0090251 | 0.010143 | -0.013659 | -0.052878 | 0.026284 | 0.0071936 | 0.028006 | 0.0038031 | 0.069723 | 0.010564 | 0.023639 | 0.14369 | 0.08278 | 0.32511 | 0.051416 | 0.069728 | 0.046146 | -0.010564 | 0.098244 | 0.21059 | -0.11587 | -0.10462 | 122.3613 | 0.029254 | 122.3796 | 122.3335 | -0.027777 | -0.031661 | 0.21067 | 122.2053 | -0.016197 | 122.3796 | 122.2993 | 0.09406 | 0.096145 | -0.23031 | 122.4536 | 122.3927 | 122.635 | 122.3204 | -0.063025 | 122.4081 | 122.5205 | 122.194 | 122.356 | -0.21907
2009.9688 | 122.5113 | -122.3923 | 0.12817 | 1.4211e-13 | -0.0092905 | 0.021539 | -0.0035515 | -0.0094525 | 0.01057 | 0.0016025 | -0.052664 | 0.026498 | 0.0069798 | 0.028006 | 0.0042303 | 0.065145 | 0.010564 | 0.028217 | 0.14369 | 0.08278 | 0.32053 | 0.028521 | 0.074307 | 0.046146 | -0.001407 | 0.1074 | 0.21516 | -0.11587 | -0.10462 | 122.4208 | 0.015521 | 122.4574 | 122.4205 | -0.000304 | -0.045394 | 0.19236 | 122.2876 | -0.020773 | 122.4666 | 122.3909 | 0.10322 | 0.086991 | -0.24405 | 122.536 | 122.4751 | 122.7128 | 122.4028 | -0.099653 | 122.4997 | 122.6074 | 122.2764 | 122.4384 | -0.2328
2011.6719 | 122.6578 | -122.319 | 0.09613 | 1.4211e-13 | -0.0099315 | 0.021752 | -0.0031241 | -0.0094525 | 0.01057 | -0.006028 | -0.052664 | 0.026498 | 0.0069798 | 0.02822 | 0.0044439 | 0.060567 | 0.001407 | 0.028217 | 0.14369 | 0.087359 | 0.32511 | 0.019363 | 0.074307 | 0.050725 | 0.003172 | 0.10282 | 0.20601 | -0.11587 | -0.08173 | 122.3384 | 0.047565 | 122.3796 | 122.3472 | 0.008854 | -0.008771 | 0.22898 | 122.2373 | 0.006692 | 122.3933 | 122.3222 | 0.084902 | 0.10988 | -0.212 | 122.4627 | 122.4064 | 122.6441 | 122.3204 | -0.076767 | 122.4219 | 122.525 | 122.2032 | 122.3698 | -0.17786
2013.4219 | 122.5433 | -122.3648 | 0.14648 | 1.4211e-13 | -0.0090769 | 0.021966 | -0.0033377 | -0.0092389 | 0.010143 | -0.006028 | -0.052878 | 0.026712 | 0.0074072 | 0.028006 | 0.0052987 | 0.069723 | 0.010564 | 0.028217 | 0.14827 | 0.078201 | 0.32053 | 0.055995 | 0.06515 | 0.046146 | -0.001407 | 0.10282 | 0.20601 | -0.11587 | -0.10462 | 122.4208 | 0.00179 | 122.4345 | 122.393 | -0.027778 | -0.068283 | 0.17405 | 122.2602 | -0.043662 | 122.43 | 122.3634 | 0.10322 | 0.059524 | -0.26236 | 122.5131 | 122.443 | 122.6853 | 122.3754 | -0.090489 | 122.4676 | 122.5708 | 122.2489 | 122.411 | -0.25111
2015.1719 | 122.6669 | -122.3328 | 0.10986 | 1.4211e-13 | -0.0092905 | 0.021539 | -0.0033377 | -0.0092389 | 0.010356 | 0.0016025 | -0.052878 | 0.026712 | 0.0071936 | 0.027579 | 0.0050849 | 0.069723 | 0.015142 | 0.032795 | 0.14827 | 0.078201 | 0.32511 | 0.046837 | 0.06515 | 0.041567 | -0.001407 | 0.093665 | 0.20601 | -0.11129 | -0.095467 | 122.3796 | 0.038411 | 122.4025 | 122.3656 | -0.014042 | -0.031662 | 0.21525 | 122.2373 | -0.016198 | 122.3979 | 122.3314 | 0.09406 | 0.096145 | -0.22116 | 122.481 | 122.411 | 122.6579 | 122.3479 | -0.063026 | 122.4264 | 122.5388 | 122.2215 | 122.3743 | -0.20533
2016.9375 | 122.6807 | -122.3328 | 0.10986 | 1.4211e-13 | -0.0095041 | 0.021752 | -0.0029103 | -0.0094525 | 0.009929 | -0.013659 | -0.052664 | 0.026925 | 0.0069798 | 0.027792 | 0.0046577 | 0.069723 | 0.015142 | 0.023639 | 0.15285 | 0.087359 | 0.31595 | 0.028521 | 0.074307 | 0.050725 | -0.001407 | 0.10282 | 0.21516 | -0.12045 | -0.11378 | 122.3613 | 0.042989 | 122.4025 | 122.3564 | -0.004882 | -0.022504 | 0.20609 | 122.219 | -0.007041 | 122.4071 | 122.3314 | 0.11237 | 0.1053 | -0.23031 | 122.4856 | 122.4201 | 122.6487 | 122.3479 | -0.081342 | 122.4356 | 122.5479 | 122.2123 | 122.3835 | -0.22364
2018.625 | 122.5388 | -122.4014 | 0.11902 | 1.4211e-13 | -0.0092905 | 0.021752 | -0.0031241 | -0.0094525 | 0.010356 | -0.006028 | -0.052237 | 0.026284 | 0.0076208 | 0.028006 | 0.0050849 | 0.065145 | 0.010564 | 0.037373 | 0.14827 | 0.069043 | 0.32511 | 0.042258 | 0.074307 | 0.041567 | -0.010564 | 0.11198 | 0.21059 | -0.11587 | -0.058836 | 122.4437 | 0.029255 | 122.4666 | 122.4388 | -0.004885 | -0.049976 | 0.20609 | 122.3426 | -0.00704 | 122.4757 | 122.3909 | 0.048272 | 0.091567 | -0.23489 | 122.5497 | 122.4705 | 122.7265 | 122.412 | -0.076761 | 122.5134 | 122.612 | 122.2856 | 122.443 | -0.17785
2020.3906 | 122.525 | -122.4152 | 0.1236 | 1.4211e-13 | -0.0092905 | 0.021539 | -0.0033377 | -0.0092389 | 0.010143 | 0.0016025 | -0.05245 | 0.026071 | 0.0074072 | 0.027579 | 0.0050849 | 0.065145 | 0.005985 | 0.023639 | 0.15285 | 0.08278 | 0.32511 | 0.042258 | 0.069728 | 0.046146 | -0.005985 | 0.1074 | 0.21059 | -0.12045 | -0.11836 | 122.4574 | 0.029256 | 122.4803 | 122.4388 | -0.018619 | -0.040816 | 0.20151 | 122.2968 | -0.016195 | 122.4849 | 122.4092 | 0.11238 | 0.08699 | -0.24405 | 122.568 | 122.4979 | 122.7403 | 122.4211 | -0.081338 | 122.5226 | 122.6257 | 122.2947 | 122.4613 | -0.24196
2022.1562 | 122.5891 | -122.3969 | 0.14191 | 1.4211e-13 | -0.0092905 | 0.021966 | -0.0035515 | -0.0090251 | 0.010143 | 0.0016025 | -0.052664 | 0.026284 | 0.0071936 | 0.02822 | 0.0048713 | 0.065145 | 0.005985 | 0.032795 | 0.13912 | 0.08278 | 0.31595 | 0.037679 | 0.069728 | 0.03241 | -0.001407 | 0.1074 | 0.20143 | -0.12503 | -0.095467 | 122.4345 | -0.00279 | 122.462 | 122.4296 | -0.004884 | -0.059127 | 0.17405 | 122.3014 | -0.034506 | 122.4666 | 122.3954 | 0.09406 | 0.059522 | -0.26694 | 122.536 | 122.4796 | 122.7128 | 122.4028 | -0.10423 | 122.5043 | 122.5983 | 122.2718 | 122.4293 | -0.23737
2023.9375 | 122.493 | -122.2549 | 0.10529 | 1.4211e-13 | -0.0092905 | 0.021966 | -0.0033377 | -0.0094525 | 0.010356 | -0.006028 | -0.052664 | 0.026284 | 0.0074072 | 0.027792 | 0.0052987 | 0.060567 | 0.005985 | 0.023639 | 0.13454 | 0.087359 | 0.31137 | 0.010206 | 1.219 | 1.1771 | 1.1524 | 1.2429 | 1.3598 | 1.2531 | 0.16095 | 122.2651 | 0.029253 | 122.3155 | 122.2786 | 0.013433 | -0.017927 | 0.20609 | 122.4159 | 1.1376 | 123.4739 | 123.4074 | 0.99148 | 1.2545 | 1.1478 | 122.3895 | 122.3423 | 122.5663 | 122.2609 | -0.09508 | 123.4978 | 123.6148 | 123.5081 | 123.432 | 0.055661
2025.7031 | 122.5525 | -122.4335 | 0.13275 | 1.4211e-13 | -0.0095041 | 0.021752 | -0.0033377 | -0.0090251 | 0.010143 | 0.0016025 | -0.05245 | 0.026284 | 0.0074072 | 0.02822 | 0.0050849 | 0.065145 | 0.001407 | 0.032795 | 0.13912 | 0.08278 | 0.31595 | 0.037679 | 0.083464 | 0.050725 | -0.005985 | 0.093665 | 0.19685 | 0.18174 | -0.18704 | 122.4712 | 0.006366 | 122.4986 | 122.4663 | -0.004884 | -0.049971 | 0.1832 | 122.2464 | -0.039086 | 122.5169 | 122.4275 | 0.18106 | 0.0641 | 0.048987 | 122.5726 | 122.5163 | 122.7494 | 122.4349 | -0.095072 | 122.5271 | 122.6303 | 122.6152 | 122.4842 | -0.31979
2027.4062 | 122.612 | -122.3831 | 0.10071 | 1.4211e-13 | -0.0092905 | 0.021966 | -0.0031241 | -0.0092389 | 0.010356 | -0.013659 | -0.052664 | 0.026498 | 0.0076208 | 0.028006 | 0.0046577 | 0.065145 | 0.010564 | 0.023639 | 0.14369 | 0.078201 | 0.31137 | 0.028521 | 0.078886 | 0.050725 | -0.001407 | 0.089087 | 0.19685 | 0.18632 | -0.18704 | 122.4116 | 0.042987 | 122.4483 | 122.4068 | -0.004882 | -0.022507 | 0.21067 | 122.1961 | -0.011621 | 122.462 | 122.3817 | 0.18564 | 0.096143 | 0.085608 | 122.5268 | 122.4613 | 122.6945 | 122.3937 | -0.072187 | 122.4722 | 122.58 | 122.5694 | 122.4338 | -0.28775
2029.0938 | 122.6898 | -122.3831 | 0.10529 | 1.4211e-13 | -0.0088631 | 0.021752 | -0.0035515 | -0.0092389 | 0.010143 | 0.0092325 | -0.052664 | 0.026498 | 0.0074072 | 0.027579 | 0.0052987 | 0.065145 | 0.010564 | 0.023639 | 0.13912 | 0.073622 | 0.31137 | 0.023942 | 0.074307 | 0.036989 | -0.001407 | 0.10282 | 0.20143 | -0.12045 | -0.18246 | 122.4071 | 0.033831 | 122.4483 | 122.4068 | -0.000303 | -0.031664 | 0.20609 | 122.2007 | -0.002464 | 122.4574 | 122.3817 | 0.18106 | 0.096143 | -0.22574 | 122.5222 | 122.4567 | 122.6945 | 122.3937 | -0.081344 | 122.4859 | 122.5845 | 122.2627 | 122.4201 | -0.28775
2030.8594 | 122.58 | -122.3923 | 0.11902 | 1.4211e-13 | -0.0092905 | 0.021966 | -0.0031241 | -0.0094525 | 0.010143 | -0.013659 | -0.052878 | 0.026498 | 0.0078344 | 0.028006 | 0.0052987 | 0.065145 | 0.001407 | 0.028217 | 0.13912 | 0.069043 | 0.32053 | 0.023942 | 0.078886 | 0.027831 | -0.005985 | 0.093665 | 0.20143 | -0.11587 | -0.19162 | 122.4162 | 0.020098 | 122.4574 | 122.4205 | 0.004275 | -0.049976 | 0.20151 | 122.2007 | -0.025354 | 122.4712 | 122.3863 | 0.18564 | 0.08241 | -0.23489 | 122.5314 | 122.4613 | 122.7128 | 122.3937 | -0.095077 | 122.4859 | 122.5937 | 122.2764 | 122.4201 | -0.31064
2032.625 | 122.6807 | -122.3602 | 0.11444 | 1.4211e-13 | -0.0095041 | 0.02218 | -0.0033377 | -0.0090251 | 0.010356 | -0.006028 | -0.052664 | 0.026712 | 0.0074072 | 0.02822 | 0.0048713 | 0.065145 | 0.005985 | 0.028217 | 0.13454 | 0.078201 | 0.31595 | 0.0331 | 0.078886 | 0.041567 | -0.015143 | 0.093665 | 0.19685 | -0.12503 | -0.18704 | 122.3933 | 0.020098 | 122.4254 | 122.3884 | -0.004883 | -0.03624 | 0.20151 | 122.1732 | -0.020776 | 122.4391 | 122.3451 | 0.1719 | 0.08241 | -0.23947 | 122.4948 | 122.4384 | 122.6762 | 122.3662 | -0.081341 | 122.4539 | 122.5571 | 122.2352 | 122.4018 | -0.30148
2034.375 | 122.6349 | -122.3923 | 0.09613 | 1.4211e-13 | -0.0090769 | 0.02218 | -0.0031241 | -0.0088115 | 0.010356 | 0.0016025 | -0.052664 | 0.026712 | 0.0071936 | 0.027792 | 0.0048713 | 0.055988 | 0.005985 | 0.028217 | 0.12996 | 0.08278 | 0.32053 | 0.019363 | 0.078886 | 0.041567 | -0.019721 | 0.098244 | 0.20601 | -0.12503 | -0.18704 | 122.4116 | 0.03383 | 122.4483 | 122.4205 | 0.008854 | -0.01335 | 0.2244 | 122.2052 | 0.002114 | 122.4712 | 122.3726 | 0.16732 | 0.10988 | -0.22116 | 122.5222 | 122.4751 | 122.7128 | 122.3983 | -0.076767 | 122.4905 | 122.5983 | 122.2672 | 122.4338 | -0.28317
2036.0781 | 122.5891 | -122.4197 | 0.12817 | 1.4211e-13 | -0.0088631 | 0.021539 | -0.0035515 | -0.0096661 | 0.010356 | 0.0092325 | -0.053091 | 0.026498 | 0.0076208 | 0.028006 | 0.0048713 | 0.065145 | 0.010564 | 0.023639 | 0.13912 | 0.064464 | 0.3068 | 0.0331 | 0.074307 | 0.041567 | -0.010564 | 0.098244 | 0.19685 | -0.11129 | -0.18704 | 122.4528 | 0.010943 | 122.4849 | 122.4434 | -0.009461 | -0.06371 | 0.17862 | 122.2327 | -0.02993 | 122.494 | 122.4092 | 0.17648 | 0.068677 | -0.23947 | 122.5589 | 122.4842 | 122.7265 | 122.4303 | -0.095074 | 122.518 | 122.6166 | 122.3084 | 122.4613 | -0.31522
2037.8281 | 122.1176 | -121.9025 | 0.11902 | 1.4211e-13 | -0.0088631 | 0.021966 | -0.0033377 | -0.0092389 | 0.010356 | -0.006028 | -0.052664 | 0.026498 | 0.0071936 | 0.02822 | 0.0048713 | 0.065145 | 0.015142 | 0.028217 | 0.14827 | 0.073622 | 0.32053 | -0.058478 | 0.50928 | 0.43534 | 0.41526 | 0.50115 | 0.63182 | 0.5755 | -0.077151 | 121.844 | 0.029255 | 121.9676 | 121.9307 | 0.086695 | -0.045397 | 0.20151 | 121.8253 | 0.38213 | 122.4117 | 122.3177 | 0.49241 | 0.5128 | 0.45648 | 122.0507 | 121.9761 | 122.223 | 121.9176 | -0.1775 | 122.4036 | 122.5343 | 122.478 | 122.3378 | -0.19617
2039.5938 | 122.4609 | -122.1863 | 0.10071 | 1.4211e-13 | -0.0088631 | 0.021966 | -0.0035515 | -0.0090251 | 0.010143 | -0.006028 | -0.052664 | 0.026284 | 0.0069798 | 0.027792 | 0.0048713 | 0.065145 | 0.010564 | 0.023639 | 0.14369 | 0.073622 | 0.32053 | 0.037679 | 0.088043 | 0.055303 | -0.005985 | 0.098244 | 0.21059 | 0.1909 | -0.18246 | 122.224 | 0.042987 | 122.2514 | 122.2099 | -0.01404 | -0.027086 | 0.21982 | 122.0038 | -0.002464 | 122.2743 | 122.1803 | 0.17648 | 0.10988 | 0.090187 | 122.33 | 122.2599 | 122.5068 | 122.1968 | -0.063029 | 122.2845 | 122.3969 | 122.3772 | 122.2416 | -0.28317
2041.3594 | 122.5021 | -122.1954 | 0.11902 | 1.4211e-13 | -0.0088631 | 0.021966 | -0.0033377 | -0.0092389 | 0.010356 | 0.0092325 | -0.052878 | 0.026498 | 0.0071936 | 0.028006 | 0.0048713 | 0.069723 | 0.010564 | 0.028217 | 0.13912 | 0.08278 | 0.31595 | 0.028521 | 0.083464 | 0.050725 | -0.005985 | 0.10282 | 0.20143 | 0.18632 | -0.16873 | 122.224 | 0.020098 | 122.2652 | 122.2237 | -0.000304 | -0.036239 | 0.19693 | 122.0267 | -0.016197 | 122.2789 | 122.1895 | 0.16274 | 0.08241 | 0.067297 | 122.3346 | 122.2782 | 122.5114 | 122.206 | -0.090498 | 122.2983 | 122.3969 | 122.3818 | 122.2462 | -0.28775
2043.0312 | 122.4609 | -122.2366 | 0.1236 | 1.4211e-13 | -0.0090769 | 0.02218 | -0.0033377 | -0.0094525 | 0.01057 | -0.006028 | -0.052664 | 0.026712 | 0.0074072 | 0.027792 | 0.0048713 | 0.055988 | 0.005985 | 0.032795 | 0.15285 | 0.073622 | 0.31595 | 0.046837 | 0.092622 | 0.046146 | -0.010564 | 0.10282 | 0.20143 | -0.11587 | -0.18704 | 122.2835 | 0.029256 | 122.2926 | 122.2694 | -0.014042 | -0.049974 | 0.19236 | 122.0496 | -0.020774 | 122.3293 | 122.2261 | 0.17648 | 0.077833 | -0.23947 | 122.3895 | 122.3103 | 122.5526 | 122.2426 | -0.076759 | 122.3395 | 122.4381 | 122.1208 | 122.2828 | -0.31064
2044.7812 | 122.4243 | -122.2824 | 0.14648 | 1.4211e-13 | -0.0095041 | 0.021966 | -0.0033377 | -0.0094525 | 0.01057 | 0.0016025 | -0.05245 | 0.026498 | 0.0076208 | 0.027792 | 0.0048713 | 0.065145 | 0.005985 | 0.032795 | 0.13454 | 0.078201 | 0.32053 | 0.042258 | 0.078886 | 0.041567 | -0.015143 | 0.089087 | 0.19685 | -0.11587 | -0.18246 | 122.3247 | -0.011945 | 122.3476 | 122.3152 | -0.009463 | -0.068283 | 0.17405 | 122.0999 | -0.057397 | 122.3613 | 122.2673 | 0.16732 | 0.050367 | -0.26236 | 122.4169 | 122.3606 | 122.6029 | 122.2884 | -0.10423 | 122.3715 | 122.4793 | 122.1665 | 122.324 | -0.32895
2046.5469 | 122.5571 | -122.2458 | 0.10529 | 1.4211e-13 | -0.0092905 | 0.02218 | -0.0037651 | -0.0094525 | 0.010356 | 0.0016025 | -0.052878 | 0.026284 | 0.0071936 | 0.028006 | 0.0048713 | 0.069723 | 0.010564 | 0.032795 | 0.14369 | 0.078201 | 0.32969 | 0.042258 | 0.083464 | 0.041567 | -0.010564 | 0.098244 | 0.20143 | -0.11587 | -0.18246 | 122.288 | 0.038409 | 122.3155 | 122.2786 | -0.009463 | -0.027085 | 0.2244 | 122.0633 | -0.007042 | 122.3293 | 122.2352 | 0.1719 | 0.096143 | -0.22116 | 122.3895 | 122.324 | 122.5755 | 122.2564 | -0.063028 | 122.344 | 122.4472 | 122.1299 | 122.2874 | -0.28775
2048.2344 | 122.5754 | -122.2458 | 0.10529 | 1.4211e-13 | -0.0092905 | 0.021966 | -0.0033377 | -0.0090251 | 0.01057 | -0.006028 | -0.053091 | 0.026498 | 0.0069798 | 0.02822 | 0.0050849 | 0.065145 | 0.015142 | 0.028217 | 0.14827 | 0.073622 | 0.31595 | 0.023942 | 0.088043 | 0.041567 | -0.005985 | 0.1074 | 0.19685 | -0.11587 | -0.18246 | 122.2697 | 0.042988 | 122.3109 | 122.274 | 0.004275 | -0.031664 | 0.21067 | 122.0633 | 0.002115 | 122.3338 | 122.2398 | 0.17648 | 0.091565 | -0.22116 | 122.3941 | 122.3194 | 122.5617 | 122.2609 | -0.081344 | 122.3532 | 122.4426 | 122.1299 | 122.2874 | -0.28775
2050 | 122.5113 | -122.2916 | 0.13733 | 1.4211e-13 | -0.0090769 | 0.022393 | -0.0035515 | -0.0096661 | 0.010143 | 0.0016025 | -0.052664 | 0.026284 | 0.0076208 | 0.028006 | 0.0050849 | 0.060567 | -0.003172 | 0.032795 | 0.14369 | 0.069043 | 0.31595 | 0.069732 | 0.074307 | 0.03241 | -0.005985 | 0.10282 | 0.20143 | -0.11587 | -0.18246 | 122.3613 | 0.006366 | 122.3521 | 122.3244 | -0.036937 | -0.068286 | 0.17862 | 122.1091 | -0.034507 | 122.3659 | 122.2856 | 0.17648 | 0.0641 | -0.2532 | 122.4353 | 122.3606 | 122.6075 | 122.2884 | -0.067597 | 122.3944 | 122.493 | 122.1757 | 122.324 | -0.31979
2051.75 | 122.4747 | -122.3236 | 0.15106 | 1.4211e-13 | -0.0090769 | 0.022393 | -0.0033377 | -0.0094525 | 0.010143 | 0.0016025 | -0.052878 | 0.026925 | 0.0076208 | 0.02822 | 0.0048713 | 0.065145 | 0.005985 | 0.032795 | 0.13912 | 0.073622 | 0.32053 | 0.0331 | 0.083464 | 0.036989 | -0.005985 | 0.10282 | 0.20143 | -0.11129 | -0.17788 | 122.3567 | -0.011945 | 122.3888 | 122.3564 | -0.000305 | -0.07744 | 0.16947 | 122.1457 | -0.04824 | 122.4071 | 122.3176 | 0.1719 | 0.050367 | -0.26236 | 122.4627 | 122.3972 | 122.6441 | 122.3296 | -0.11796 | 122.4264 | 122.525 | 122.2123 | 122.3606 | -0.32895
2053.5 | 117.1783 | -78.3966 | 38.5025 | 1.4211e-13 | -0.0095041 | 0.021752 | -0.0037651 | -0.0090251 | 0.0095016 | -0.013659 | -0.052237 | 0.02778 | 0.0074072 | 0.02822 | 0.0048713 | 0.046831 | 0.001407 | 0.014482 | 0.12538 | -0.008799 | 0.29764 | 0.019363 | 27.3497 | 27.6741 | 27.3793 | 27.3998 | 27.3022 | 27.5252 | 5.5273 | 78.416 | -38.3771 | 78.4434 | 78.4111 | -0.004881 | -38.5113 | -38.2049 | 83.9239 | -11.1027 | 105.7463 | 105.7759 | 21.852 | -11.2003 | -10.9774 | 78.522 | 78.3878 | 78.6942 | 78.398 | -38.4831 | 105.7964 | 105.6988 | 105.9218 | 106.0707 | -32.9752
2055.25 | 122.3511 | -122.081 | 0.09613 | 1.4211e-13 | -0.0092905 | 0.02218 | -0.0033377 | -0.0090251 | 0.010356 | 0.0016025 | -0.052664 | 0.026712 | 0.0076208 | 0.028006 | 0.0046577 | 0.060567 | 0.001407 | 0.023639 | 0.14369 | 0.073622 | 0.32053 | 0.046837 | 0.078886 | 0.046146 | -0.010564 | 0.098244 | 0.20143 | 0.18632 | -0.18246 | 122.1278 | 0.047565 | 122.1416 | 122.1046 | -0.023198 | -0.022508 | 0.2244 | 121.8985 | 0.002114 | 122.1599 | 122.0704 | 0.1719 | 0.1053 | 0.090186 | 122.2247 | 122.1546 | 122.4015 | 122.0824 | -0.049293 | 122.1792 | 122.2824 | 122.2673 | 122.1271 | -0.27859
2056.9688 | 122.1588 | -121.7194 | 0.10071 | 1.4211e-13 | -0.0092905 | 0.021752 | -0.0031241 | -0.0092389 | 0.01057 | -0.006028 | -0.05245 | 0.026712 | 0.0074072 | 0.02822 | 0.0050849 | 0.060567 | 0.001407 | 0.023639 | 0.13454 | 0.073622 | 0.31137 | 0.014784 | 0.31698 | 0.26592 | 0.22295 | 0.32259 | 0.4441 | 0.39693 | -0.13668 | 121.7341 | 0.033831 | 121.7799 | 121.743 | 0.008855 | -0.027086 | 0.21067 | 121.5827 | 0.22188 | 122.0363 | 121.9423 | 0.35963 | 0.34339 | 0.29622 | 121.8539 | 121.793 | 122.0307 | 121.7208 | -0.085924 | 122.0419 | 122.1635 | 122.1163 | 121.9853 | -0.23738
2058.7344 | 122.0673 | -121.6644 | 0.091553 | 1.4211e-13 | -0.0088631 | 0.021966 | -0.0031241 | -0.0092389 | 0.010356 | 0.0092325 | -0.052664 | 0.026712 | 0.0074072 | 0.028006 | 0.0048713 | 0.060567 | 0.001407 | 0.028217 | 0.13454 | 0.073622 | 0.31595 | 0.046837 | 0.078886 | 0.050725 | -0.005985 | 0.098244 | 0.21059 | 0.18632 | -0.17331 | 121.7113 | 0.042986 | 121.725 | 121.6926 | -0.01862 | -0.017931 | 0.2244 | 121.4911 | 0.006691 | 121.7433 | 121.6584 | 0.16732 | 0.11903 | 0.094763 | 121.799 | 121.7381 | 121.9804 | 121.6658 | -0.044716 | 121.7627 | 121.875 | 121.8507 | 121.7152 | -0.26486
2060.4375 | 121.8201 | -121.431 | 0.10529 | 1.4211e-13 | -0.0095041 | 0.02218 | -0.0035515 | -0.0094525 | 0.01057 | 0.0016025 | -0.052237 | 0.026498 | 0.0074072 | 0.028006 | 0.0050849 | 0.060567 | 0.005985 | 0.028217 | 0.13912 | 0.064464 | 0.31137 | 0.019363 | 0.71075 | 0.64138 | 0.63045 | 0.71176 | 0.84701 | 0.77238 | -0.063415 | 121.4503 | 0.033831 | 121.4915 | 121.4592 | 0.008854 | -0.040822 | 0.20609 | 121.3676 | 0.60648 | 122.1417 | 122.0614 | 0.69387 | 0.74173 | 0.66709 | 121.5701 | 121.4954 | 121.7423 | 121.437 | -0.085923 | 122.1427 | 122.278 | 122.2033 | 122.0723 | -0.1687
2062.1875 | 121.9849 | -121.7697 | 0.14191 | 1.4211e-13 | -0.0090769 | 0.021539 | -0.0035515 | -0.0092389 | 0.010356 | -0.006028 | -0.05245 | 0.026498 | 0.0076208 | 0.028433 | 0.0048713 | 0.055988 | 0.005985 | 0.032795 | 0.13454 | 0.069043 | 0.31595 | 0.023942 | 0.078886 | 0.041567 | -0.010564 | 0.089087 | 0.21059 | 0.17716 | -0.18246 | 121.7937 | -0.007368 | 121.8257 | 121.8025 | 0.008853 | -0.072864 | 0.17405 | 121.5872 | -0.05282 | 121.8486 | 121.7591 | 0.1719 | 0.068679 | 0.035252 | 121.9043 | 121.8388 | 122.0857 | 121.7757 | -0.11797 | 121.8588 | 121.9803 | 121.9469 | 121.8113 | -0.32437
2063.9531 | 122.0352 | -121.8613 | 0.13275 | 1.4211e-13 | -0.0095041 | 0.02218 | -0.0035515 | -0.0092389 | 0.010143 | 0.0016025 | -0.05245 | 0.026498 | 0.0076208 | 0.028006 | 0.0050849 | 0.060567 | 0.001407 | 0.01906 | 0.13454 | 0.078201 | 0.31137 | 0.019363 | 0.074307 | 0.046146 | -0.005985 | 0.089087 | 0.20143 | 0.17716 | -0.18246 | 121.8806 | 0.001788 | 121.9218 | 121.8803 | -0.000303 | -0.05455 | 0.17862 | 121.6788 | -0.043664 | 121.9356 | 121.8553 | 0.17648 | 0.068678 | 0.044408 | 121.9958 | 121.9395 | 122.1726 | 121.8627 | -0.11339 | 121.9504 | 122.0627 | 122.0384 | 121.9074 | -0.31522
2065.7031 | 122.1725 | -121.8613 | 0.10986 | 1.4211e-13 | -0.0090769 | 0.02218 | -0.0035515 | -0.0092389 | 0.010356 | -0.006028 | -0.052237 | 0.026712 | 0.0071936 | 0.028006 | 0.0046577 | 0.060567 | 0.005985 | 0.01906 | 0.14369 | 0.050727 | 0.31595 | 0.019363 | 0.083464 | 0.050725 | -0.010564 | 0.089087 | 0.20601 | -0.047193 | -0.17788 | 121.8806 | 0.033832 | 121.9218 | 121.8803 | -0.000303 | -0.059136 | 0.20609 | 121.6834 | -0.020776 | 121.9447 | 121.8507 | 0.16732 | 0.096145 | -0.15706 | 122.005 | 121.912 | 122.1772 | 121.8673 | -0.0905 | 121.9504 | 122.0673 | 121.8141 | 121.912 | -0.28775
2067.4062 | 122.0673 | -121.9299 | 0.13733 | 1.4211e-13 | -0.0092905 | 0.02218 | -0.0029103 | -0.0094525 | 0.010356 | -0.006028 | -0.05245 | 0.026712 | 0.0074072 | 0.028006 | 0.0048713 | 0.060567 | 0.010564 | 0.032795 | 0.14369 | 0.055306 | 0.31137 | 0.0331 | 0.083464 | 0.036989 | -0.010564 | 0.093665 | 0.20143 | -0.12503 | -0.18246 | 121.963 | 0.006366 | 121.9905 | 121.9627 | -0.000305 | -0.082023 | 0.17404 | 121.7475 | -0.043664 | 122.0134 | 121.9194 | 0.1719 | 0.0641 | -0.26236 | 122.0736 | 121.9852 | 122.2413 | 121.9405 | -0.10423 | 122.0236 | 122.1314 | 121.8049 | 121.9669 | -0.31979
2069.0938 | 121.9574 | -121.9345 | 0.15106 | 1.4211e-13 | -0.0092905 | 0.021966 | -0.0035515 | -0.0094525 | 0.010356 | -0.006028 | -0.05245 | 0.026284 | 0.0074072 | 0.02822 | 0.0050849 | 0.060567 | 0.005985 | 0.01906 | 0.13912 | 0.064464 | 0.31595 | 0.019363 | 0.069728 | 0.036989 | -0.005985 | 0.084508 | 0.20143 | -0.11587 | -0.18246 | 121.9539 | -0.011945 | 121.9951 | 121.9536 | -0.000303 | -0.086598 | 0.16489 | 121.752 | -0.066554 | 122.0042 | 121.9285 | 0.17648 | 0.050367 | -0.26693 | 122.0736 | 121.999 | 122.2505 | 121.9405 | -0.1317 | 122.019 | 122.1359 | 121.8186 | 121.9715 | -0.33353
2070.8438 | 122.2366 | -121.9162 | 0.10529 | 1.4211e-13 | -0.0092905 | 0.021966 | -0.0035515 | -0.0094525 | 0.010143 | 0.0016025 | -0.052664 | 0.026284 | 0.0071936 | 0.028006 | 0.0052987 | 0.060567 | 0.001407 | 0.023639 | 0.13912 | 0.046148 | 0.31595 | 0.023942 | 0.083464 | 0.027831 | -0.010564 | 0.089087 | 0.20601 | -0.12503 | -0.18246 | 121.9401 | 0.033831 | 121.9768 | 121.9398 | -0.000303 | -0.059138 | 0.21067 | 121.7337 | -0.016199 | 121.9997 | 121.9056 | 0.1719 | 0.10072 | -0.23031 | 122.0553 | 121.9623 | 122.2322 | 121.9176 | -0.081344 | 122.0053 | 122.1222 | 121.7912 | 121.944 | -0.28775
2072.625 | 122.1863 | -121.9437 | 0.10986 | 1.4211e-13 | -0.0092905 | 0.021752 | -0.0033377 | -0.0096661 | 0.010356 | 0.0016025 | -0.05245 | 0.026284 | 0.0076208 | 0.02822 | 0.0048713 | 0.065145 | 0.010564 | 0.023639 | 0.14369 | 0.073622 | 0.31595 | 0.0331 | 0.074307 | 0.036989 | -0.010564 | 0.089087 | 0.20601 | -0.11587 | -0.17788 | 121.9768 | 0.033832 | 122.0088 | 121.9673 | -0.009461 | -0.036241 | 0.20609 | 121.7658 | -0.020776 | 122.018 | 121.9331 | 0.16732 | 0.096145 | -0.22574 | 122.0874 | 122.0173 | 122.2596 | 121.9542 | -0.076763 | 122.0328 | 122.1497 | 121.8278 | 121.9807 | -0.28775
2074.3906 | 122.2229 | -121.9345 | 0.12817 | 1.4211e-13 | -0.0090769 | 0.022393 | -0.0033377 | -0.0090251 | 0.010356 | -0.006028 | -0.052023 | 0.026498 | 0.0074072 | 0.02822 | 0.0048713 | 0.065145 | 0.005985 | 0.028217 | 0.14369 | 0.078201 | 0.31595 | 0.023942 | 0.074307 | 0.03241 | -0.015143 | 0.093665 | 0.20601 | -0.097557 | -0.17331 | 121.9585 | 0.015521 | 121.9997 | 121.9627 | 0.004275 | -0.049973 | 0.18778 | 121.7612 | -0.034509 | 122.0088 | 121.9194 | 0.15816 | 0.077834 | -0.22573 | 122.0782 | 122.0127 | 122.2505 | 121.9405 | -0.10423 | 122.0282 | 122.1405 | 121.837 | 121.9669 | -0.30148
2076.0938 | 121.4493 | -121.4951 | 0.14648 | 1.4211e-13 | -0.0090769 | 0.02218 | -0.0035515 | -0.0096661 | 0.010356 | 0.0016025 | -0.052878 | 0.026284 | 0.0071936 | 0.028433 | 0.0048713 | 0.060567 | 0.005985 | 0.023639 | 0.13912 | 0.055306 | 0.31137 | 0.023942 | 0.074307 | 0.027831 | -0.001407 | 0.098244 | 0.20601 | -0.11587 | -0.19162 | 121.519 | -0.007367 | 121.5556 | 121.5187 | -0.000303 | -0.091178 | 0.16489 | 121.3034 | -0.04824 | 121.5694 | 121.4936 | 0.19021 | 0.059524 | -0.26236 | 121.6342 | 121.5504 | 121.8064 | 121.501 | -0.12254 | 121.5933 | 121.7011 | 121.3792 | 121.5229 | -0.33811
2077.8438 | 121.5546 | -121.5317 | 0.12817 | 1.4211e-13 | -0.0088631 | 0.02218 | -0.0033377 | -0.0092389 | 0.010356 | -0.006028 | -0.052237 | 0.026284 | 0.0076208 | 0.02822 | 0.0046577 | 0.060567 | 0.001407 | 0.032795 | 0.14369 | 0.073622 | 0.31595 | 0.019363 | 0.069728 | 0.041567 | -0.010564 | 0.093665 | 0.20143 | -0.11587 | -0.17788 | 121.551 | 0.015521 | 121.5922 | 121.5645 | 0.013432 | -0.054552 | 0.18778 | 121.3538 | -0.034509 | 121.6014 | 121.5211 | 0.16732 | 0.073255 | -0.24405 | 121.6754 | 121.6053 | 121.8476 | 121.5331 | -0.10881 | 121.6253 | 121.7331 | 121.4158 | 121.5732 | -0.30606
2079.6094 | 122.2412 | -121.9849 | 0.11444 | 1.4211e-13 | -0.0090769 | 0.021966 | -0.0033377 | -0.0092389 | 0.010356 | 0.0016025 | -0.052878 | 0.026284 | 0.0076208 | 0.028006 | 0.0048713 | 0.069723 | 0.001407 | 0.032795 | 0.13912 | 0.078201 | 0.31595 | 0.028521 | 0.083464 | 0.036989 | -0.010564 | 0.093665 | 0.20601 | -0.12045 | -0.17788 | 122.0134 | 0.024676 | 122.0546 | 122.0177 | 0.004274 | -0.03624 | 0.20151 | 121.807 | -0.020776 | 122.0683 | 121.9743 | 0.16732 | 0.091567 | -0.23489 | 122.124 | 122.0631 | 122.3008 | 121.9863 | -0.08592 | 122.0785 | 122.1909 | 121.8644 | 122.0219 | -0.29233
2081.3125 | 122.2321 | -122.0169 | 0.12817 | 1.4211e-13 | -0.0090769 | 0.02218 | -0.0033377 | -0.0094525 | 0.010356 | -0.006028 | -0.052664 | 0.026712 | 0.0074072 | 0.028006 | 0.0048713 | 0.060567 | 0.005985 | 0.028217 | 0.13454 | 0.064464 | 0.31137 | 0.028521 | 0.078886 | 0.03241 | -0.015143 | 0.093665 | 0.20601 | -0.11587 | -0.17788 | 122.0454 | 0.006365 | 122.0775 | 122.0451 | -0.000304 | -0.06371 | 0.1832 | 121.839 | -0.034509 | 122.0958 | 122.0018 | 0.16274 | 0.077834 | -0.24405 | 122.1514 | 122.0814 | 122.3283 | 122.0229 | -0.099653 | 122.1106 | 122.2229 | 121.901 | 122.0493 | -0.30606
2083 | 122.2641 | -122.0169 | 0.10529 | 1.4211e-13 | -0.0090769 | 0.021966 | -0.0031241 | -0.0092389 | 0.010356 | -0.006028 | -0.052664 | 0.026284 | 0.0076208 | 0.028006 | 0.0050849 | 0.065145 | 0.005985 | 0.032795 | 0.13912 | 0.073622 | 0.31137 | 0.019363 | 0.074307 | 0.036989 | -0.010564 | 0.098244 | 0.19685 | -0.12045 | -0.17788 | 122.0363 | 0.033831 | 122.0821 | 122.0497 | 0.013432 | -0.031664 | 0.20609 | 121.839 | -0.007042 | 122.0912 | 122.0063 | 0.16732 | 0.091565 | -0.22574 | 122.156 | 122.0905 | 122.3283 | 122.0229 | -0.085923 | 122.1152 | 122.2138 | 121.8965 | 122.0539 | -0.28317
2084.75 | 121.8384 | -121.5637 | 0.13275 | 1.4211e-13 | -0.0088631 | 0.021966 | -0.0031241 | -0.0092389 | 0.010356 | -0.006028 | -0.052023 | 0.026712 | 0.0076208 | 0.02822 | 0.0048713 | 0.055988 | 0.001407 | 0.028217 | 0.14827 | 0.073622 | 0.31595 | 0.028521 | 0.078886 | 0.03241 | -0.005985 | 0.10282 | 0.19685 | -0.12503 | -0.18246 | 121.5922 | 0.015523 | 121.6197 | 121.5919 | -0.000304 | -0.059129 | 0.1832 | 121.3813 | -0.029929 | 121.6426 | 121.5577 | 0.17648 | 0.0641 | -0.25778 | 121.712 | 121.6373 | 121.8797 | 121.5651 | -0.10423 | 121.6665 | 121.7606 | 121.4387 | 121.5961 | -0.31522
2086.5312 | 122.3099 | -121.9894 | 0.10071 | 1.4211e-13 | -0.0090769 | 0.021966 | -0.0033377 | -0.0092389 | 0.010143 | -0.006028 | -0.05245 | 0.026284 | 0.0078344 | 0.028006 | 0.0048713 | 0.055988 | 0.010564 | 0.028217 | 0.13454 | 0.073622 | 0.31137 | 0.023942 | 0.074307 | 0.036989 | -0.010564 | 0.089087 | 0.20601 | -0.11587 | -0.18246 | 122.0134 | 0.033831 | 122.0454 | 122.0177 | 0.004275 | -0.027086 | 0.21067 | 121.807 | -0.011621 | 122.0637 | 121.9789 | 0.1719 | 0.1053 | -0.21658 | 122.124 | 122.0631 | 122.3008 | 122 | -0.076766 | 122.0785 | 122.1954 | 121.8736 | 122.0264 | -0.28317
2088.2188 | 122.3099 | -122.0215 | 0.10986 | 1.4211e-13 | -0.0088631 | 0.02218 | -0.0033377 | -0.0096661 | 0.01057 | -0.006028 | -0.052664 | 0.026284 | 0.0074072 | 0.028006 | 0.0046577 | 0.046831 | 0.010564 | 0.01906 | 0.13912 | 0.073622 | 0.3068 | 0.023942 | 0.055992 | 0.036989 | -0.005985 | 0.089087 | 0.19227 | -0.12045 | -0.17331 | 122.0454 | 0.029254 | 122.0683 | 122.0405 | -0.004882 | -0.036241 | 0.19693 | 121.8482 | -0.020776 | 122.0775 | 122.0155 | 0.16732 | 0.082409 | -0.23031 | 122.1606 | 122.0951 | 122.3283 | 122.032 | -0.085921 | 122.1106 | 122.2138 | 121.901 | 122.0585 | -0.28317
2089.9688 | 122.2595 | -122.0123 | 0.10071 | 1.4211e-13 | -0.0095041 | 0.022393 | -0.0033377 | -0.0094525 | 0.010356 | -0.013659 | -0.052878 | 0.026284 | 0.0074072 | 0.02822 | 0.0048713 | 0.060567 | 0.010564 | 0.023639 | 0.13454 | 0.078201 | 0.31595 | 0.019363 | 0.060571 | 0.03241 | -0.005985 | 0.093665 | 0.20143 | -0.11129 | -0.18704 | 122.0317 | 0.033831 | 122.0729 | 122.036 | 0.004276 | -0.022507 | 0.21524 | 121.8253 | -0.007043 | 122.0729 | 122.0063 | 0.18106 | 0.10072 | -0.212 | 122.1469 | 122.0905 | 122.3283 | 122.0229 | -0.081345 | 122.106 | 122.2138 | 121.901 | 122.0447 | -0.28775
2091.6719 | 122.3236 | -122.0261 | 0.10986 | 1.4211e-13 | -0.0090769 | 0.02218 | -0.0035515 | -0.0092389 | 0.01057 | 0.0016025 | -0.052237 | 0.026498 | 0.0078344 | 0.028006 | 0.0048713 | 0.065145 | 0.001407 | 0.032795 | 0.13912 | 0.08278 | 0.31595 | 0.014784 | 0.060571 | 0.036989 | -0.015143 | 0.084508 | 0.19227 | -0.11587 | -0.17788 | 122.0408 | 0.029254 | 122.0912 | 122.0589 | 0.018011 | -0.027083 | 0.20609 | 121.8482 | -0.025355 | 122.0866 | 122.0109 | 0.16274 | 0.082409 | -0.22574 | 122.1652 | 122.1088 | 122.342 | 122.0275 | -0.095079 | 122.1106 | 122.2183 | 121.9102 | 122.0631 | -0.28775
2093.4375 | 122.2229 | -122.0856 | 0.13275 | 1.4211e-13 | -0.0088631 | 0.021966 | -0.0037651 | -0.0090251 | 0.010356 | -0.006028 | -0.05245 | 0.026284 | 0.0076208 | 0.02822 | 0.0050849 | 0.055988 | 0.005985 | 0.028217 | 0.13454 | 0.069043 | 0.31137 | 0.028521 | 0.060571 | 0.041567 | -0.015143 | 0.084508 | 0.20601 | -0.12045 | -0.17788 | 122.1141 | 0.001788 | 122.1416 | 122.1138 | -0.000304 | -0.063708 | 0.17862 | 121.9077 | -0.048243 | 122.1461 | 122.0704 | 0.16274 | 0.073257 | -0.2532 | 122.2201 | 122.1546 | 122.3969 | 122.0916 | -0.10423 | 122.1701 | 122.2916 | 121.9651 | 122.1271 | -0.31064
2095.125 | 122.2137 | -122.0947 | 0.13733 | 1.4211e-13 | -0.0090769 | 0.021966 | -0.0031241 | -0.0092389 | 0.01057 | 0.0016025 | -0.052664 | 0.026284 | 0.0076208 | 0.028433 | 0.0048713 | 0.05141 | 0.005985 | 0.023639 | 0.13912 | 0.055306 | 0.32053 | 0.023942 | 0.06515 | 0.027831 | -0.005985 | 0.093665 | 0.19685 | -0.12045 | -0.16873 | 122.1187 | 0.001788 | 122.1461 | 122.1184 | -0.000303 | -0.082023 | 0.1832 | 121.926 | -0.043664 | 122.1599 | 122.0887 | 0.16274 | 0.059522 | -0.25778 | 122.2338 | 122.15 | 122.4153 | 122.1007 | -0.11339 | 122.1884 | 122.2916 | 121.9743 | 122.1226 | -0.30606
2096.8281 | 122.3602 | -122.0718 | 0.10529 | 1.4211e-13 | -0.0088631 | 0.021539 | -0.0037651 | -0.0090251 | 0.010143 | -0.013659 | -0.052664 | 0.026284 | 0.0074072 | 0.028006 | 0.0048713 | 0.065145 | -0.003172 | 0.028217 | 0.12996 | 0.064464 | 0.32053 | 0.019363 | 0.060571 | 0.03241 | -0.005985 | 0.093665 | 0.20143 | -0.11587 | -0.17331 | 122.0912 | 0.024674 | 122.137 | 122.1001 | 0.008854 | -0.040822 | 0.21525 | 121.8985 | -0.011621 | 122.1324 | 122.0659 | 0.16732 | 0.096143 | -0.22116 | 122.2018 | 122.1363 | 122.3924 | 122.0687 | -0.085923 | 122.1655 | 122.2733 | 121.956 | 122.1042 | -0.27859
2098.5938 | 122.2366 | -122.0535 | 0.13733 | 1.4211e-13 | -0.0092905 | 0.021966 | -0.0035515 | -0.0088115 | 0.01057 | -0.006028 | -0.052023 | 0.026498 | 0.0074072 | 0.028006 | 0.0048713 | 0.055988 | -0.003172 | 0.023639 | 0.14369 | 0.078201 | 0.31137 | 0.028521 | 0.060571 | 0.027831 | -0.010564 | 0.098244 | 0.19685 | -0.11587 | -0.18246 | 122.082 | 0.006366 | 122.1095 | 122.0772 | -0.004882 | -0.059128 | 0.17404 | 121.8711 | -0.039085 | 122.1141 | 122.043 | 0.1719 | 0.059522 | -0.2532 | 122.1972 | 122.1317 | 122.3649 | 122.0504 | -0.10881 | 122.1518 | 122.2504 | 121.9377 | 122.0814 | -0.31979
2100.3438 | 122.3694 | -122.0444 | 0.10071 | 1.4211e-13 | -0.0088631 | 0.02218 | -0.0033377 | -0.0092389 | 0.009929 | -0.013659 | -0.052237 | 0.026498 | 0.0074072 | 0.02822 | 0.0048713 | 0.060567 | 0.005985 | 0.023639 | 0.13454 | 0.073622 | 0.32053 | 0.019363 | 0.06515 | 0.027831 | -0.015143 | 0.089087 | 0.20143 | -0.11587 | -0.18246 | 122.0637 | 0.033831 | 122.1049 | 122.068 | 0.004276 | -0.027086 | 0.21982 | 121.8619 | -0.011621 | 122.1095 | 122.0292 | 0.16732 | 0.10072 | -0.21658 | 122.1789 | 122.118 | 122.3649 | 122.0504 | -0.081345 | 122.1335 | 122.2458 | 121.9285 | 122.0722 | -0.28317
2102.1094 | 122.2412 | -122.0993 | 0.13275 | 1.4211e-13 | -0.0095041 | 0.021752 | -0.0033377 | -0.0094525 | 0.01057 | -0.013659 | -0.05245 | 0.026284 | 0.0071936 | 0.028647 | 0.0046577 | 0.060567 | -0.003172 | 0.023639 | 0.12996 | 0.073622 | 0.31595 | 0.023942 | 0.06515 | 0.03241 | -0.001407 | 0.098244 | 0.20143 | -0.11587 | -0.17331 | 122.1232 | -0.002791 | 122.1599 | 122.1229 | -0.000303 | -0.059129 | 0.1832 | 121.926 | -0.034507 | 122.1645 | 122.0979 | 0.1719 | 0.068678 | -0.24862 | 122.2293 | 122.1729 | 122.4153 | 122.0961 | -0.10881 | 122.1975 | 122.3007 | 121.9834 | 122.1317 | -0.30606
2103.8594 | 122.2961 | -122.0901 | 0.1236 | 1.4211e-13 | -0.0092905 | 0.022393 | -0.0035515 | -0.0090251 | 0.010356 | 0.0016025 | -0.05245 | 0.026498 | 0.0074072 | 0.028433 | 0.0048713 | 0.065145 | 0.005985 | 0.028217 | 0.13454 | 0.073622 | 0.31137 | 0.028521 | 0.060571 | 0.027831 | -0.019721 | 0.07993 | 0.19685 | -0.11587 | -0.17788 | 122.1187 | 0.010943 | 122.1553 | 122.1184 | -0.000304 | -0.049974 | 0.18778 | 121.9123 | -0.043666 | 122.1507 | 122.0704 | 0.15816 | 0.073255 | -0.23947 | 122.2247 | 122.1638 | 122.4015 | 122.0961 | -0.095075 | 122.1701 | 122.287 | 121.9743 | 122.118 | -0.30148
2105.625 | 122.3419 | -122.081 | 0.11902 | 1.4211e-13 | -0.0088631 | 0.02218 | -0.0031241 | -0.0092389 | 0.009929 | 0.0016025 | -0.052664 | 0.026712 | 0.0071936 | 0.028006 | 0.0046577 | 0.060567 | 0.001407 | 0.028217 | 0.13912 | 0.073622 | 0.31137 | 0.028521 | 0.069728 | 0.03241 | -0.005985 | 0.093665 | 0.19685 | -0.11587 | -0.17788 | 122.1095 | 0.020098 | 122.1416 | 122.1092 | -0.000304 | -0.045397 | 0.19235 | 121.9031 | -0.025354 | 122.1507 | 122.075 | 0.1719 | 0.077832 | -0.23489 | 122.2201 | 122.1546 | 122.3924 | 122.0824 | -0.090498 | 122.1747 | 122.2778 | 121.9651 | 122.1134 | -0.2969
2107.3281 | 122.3145 | -122.1085 | 0.1236 | 1.4211e-13 | -0.0090769 | 0.022393 | -0.0031241 | -0.0092389 | 0.010356 | -0.006028 | -0.052664 | 0.026712 | 0.0074072 | 0.02822 | 0.0046577 | 0.055988 | 0.005985 | 0.023639 | 0.13912 | 0.078201 | 0.31595 | 0.019363 | 0.06515 | 0.03241 | -0.010564 | 0.098244 | 0.19685 | -0.11587 | -0.18246 | 122.1278 | 0.015521 | 122.1644 | 122.1321 | 0.004276 | -0.045395 | 0.19236 | 121.926 | -0.025352 | 122.1736 | 122.0979 | 0.1719 | 0.073255 | -0.23947 | 122.2476 | 122.1867 | 122.4244 | 122.1144 | -0.10423 | 122.2067 | 122.3053 | 121.9926 | 122.1409 | -0.30606
2109.0156 | 122.3282 | -122.1222 | 0.12817 | 1.4211e-13 | -0.0092905 | 0.021752 | -0.0033377 | -0.0094525 | 0.010143 | 0.0016025 | -0.052664 | 0.026498 | 0.0076208 | 0.02822 | 0.0044439 | 0.055988 | 0.001407 | 0.037373 | 0.13454 | 0.073622 | 0.32053 | 0.019363 | 0.069728 | 0.036989 | -0.005985 | 0.098244 | 0.20143 | -0.11587 | -0.18246 | 122.1416 | 0.006365 | 122.1782 | 122.1596 | 0.01801 | -0.054552 | 0.19236 | 121.9397 | -0.02993 | 122.1919 | 122.1162 | 0.17648 | 0.073255 | -0.24405 | 122.2567 | 122.1958 | 122.4427 | 122.1236 | -0.10881 | 122.2204 | 122.3236 | 122.0063 | 122.1592 | -0.31064
2110.7656 | 122.319 | -122.1176 | 0.1236 | 1.4211e-13 | -0.0092905 | 0.02218 | -0.0033377 | -0.0088115 | 0.010143 | -0.006028 | -0.05245 | 0.026071 | 0.0069798 | 0.027792 | 0.0046577 | 0.055988 | 0.001407 | 0.037373 | 0.13912 | 0.069043 | 0.32053 | 0.028521 | 0.060571 | 0.03241 | -0.005985 | 0.098244 | 0.20143 | -0.12045 | -0.17788 | 122.1461 | 0.015521 | 122.1736 | 122.155 | 0.008852 | -0.054553 | 0.19694 | 121.9397 | -0.025352 | 122.1782 | 122.1116 | 0.1719 | 0.077833 | -0.24405 | 122.2567 | 122.1867 | 122.4381 | 122.119 | -0.095075 | 122.2159 | 122.319 | 121.9972 | 122.15 | -0.30148
2112.4844 | 122.3282 | -122.1451 | 0.14191 | 1.4211e-13 | -0.0092905 | 0.021752 | -0.0033377 | -0.0088115 | 0.01057 | -0.006028 | -0.052237 | 0.026498 | 0.0076208 | 0.028433 | 0.0048713 | 0.055988 | 0.010564 | 0.028217 | 0.13912 | 0.069043 | 0.3068 | 0.028521 | 0.055992 | 0.023253 | -0.015143 | 0.093665 | 0.20143 | -0.11587 | -0.17788 | 122.1736 | -0.00279 | 122.2011 | 122.1733 | -0.000304 | -0.072864 | 0.16489 | 121.9672 | -0.048242 | 122.2011 | 122.1299 | 0.16274 | 0.059522 | -0.25778 | 122.2842 | 122.2141 | 122.4519 | 122.1556 | -0.11339 | 122.2387 | 122.3465 | 122.0292 | 122.1683 | -0.31979
2114.25 | 122.2916 | -122.1588 | 0.12817 | 1.4211e-13 | -0.0090769 | 0.021752 | -0.0035515 | -0.0088115 | 0.01057 | 0.0016025 | -0.052237 | 0.026498 | 0.0074072 | 0.02822 | 0.0046577 | 0.060567 | 0.010564 | 0.023639 | 0.13912 | 0.073622 | 0.3068 | 0.028521 | 0.06515 | 0.027831 | -0.005985 | 0.098244 | 0.20143 | -0.11587 | -0.18246 | 122.1873 | 0.010943 | 122.2194 | 122.1825 | -0.004882 | -0.054552 | 0.17862 | 121.9763 | -0.02993 | 122.224 | 122.1528 | 0.17648 | 0.073255 | -0.24405 | 122.2979 | 122.2324 | 122.4656 | 122.1694 | -0.099653 | 122.2571 | 122.3602 | 122.0429 | 122.1866 | -0.31064
2116.0156 | 122.4014 | -122.1039 | 0.10071 | 1.4211e-13 | -0.0092905 | 0.02218 | -0.0033377 | -0.0092389 | 0.010356 | -0.013659 | -0.052664 | 0.026712 | 0.0076208 | 0.028006 | 0.0046577 | 0.060567 | 0.005985 | 0.032795 | 0.13912 | 0.073622 | 0.31137 | 0.037679 | 0.069728 | 0.027831 | -0.015143 | 0.093665 | 0.19685 | -0.11587 | -0.17788 | 122.1416 | 0.038409 | 122.1644 | 122.1367 | -0.004884 | -0.027086 | 0.21067 | 121.926 | -0.007043 | 122.1736 | 122.0887 | 0.16274 | 0.096143 | -0.21658 | 122.243 | 122.1775 | 122.4153 | 122.1099 | -0.063029 | 122.1975 | 122.3007 | 121.988 | 122.1317 | -0.27859
2117.7188 | 122.2916 | -122.1497 | 0.13733 | 1.4211e-13 | -0.0097179 | 0.021752 | -0.0033377 | -0.0092389 | 0.009929 | -0.013659 | -0.05245 | 0.026284 | 0.0078344 | 0.028433 | 0.0050849 | 0.060567 | 0.005985 | 0.028217 | 0.14369 | 0.073622 | 0.31595 | 0.023942 | 0.06515 | 0.03241 | -0.005985 | 0.089087 | 0.19685 | -0.11587 | -0.17788 | 122.1736 | 0.006366 | 122.2102 | 122.1779 | 0.004275 | -0.063707 | 0.17862 | 121.9718 | -0.048242 | 122.2148 | 122.1437 | 0.1719 | 0.059522 | -0.2532 | 122.2934 | 122.2233 | 122.4656 | 122.1556 | -0.11339 | 122.2387 | 122.3465 | 122.0338 | 122.1821 | -0.31521
2119.4688 | 122.3373 | -122.168 | 0.11902 | 1.4211e-13 | -0.0090769 | 0.02218 | -0.0035515 | -0.0090251 | 0.010356 | 0.016863 | -0.052664 | 0.026498 | 0.0074072 | 0.02822 | 0.0048713 | 0.060567 | -0.003172 | 0.014482 | 0.13912 | 0.064464 | 0.3068 | 0.023942 | 0.055992 | 0.027831 | -0.005985 | 0.093665 | 0.19227 | -0.12503 | -0.17788 | 122.1919 | 0.020098 | 122.2285 | 122.1825 | -0.00946 | -0.054555 | 0.18778 | 121.9901 | -0.025354 | 122.224 | 122.162 | 0.1719 | 0.073253 | -0.24405 | 122.3071 | 122.2324 | 122.4748 | 122.1648 | -0.095077 | 122.2616 | 122.3602 | 122.0429 | 122.1958 | -0.2969
2121.2188 | 122.4289 | -122.1268 | 0.1236 | 1.4211e-13 | -0.0097179 | 0.02218 | -0.0033377 | -0.0092389 | 0.010356 | 0.0092325 | -0.05245 | 0.026498 | 0.0071936 | 0.027792 | 0.0052987 | 0.055988 | 0.010564 | 0.023639 | 0.13912 | 0.064464 | 0.31137 | 0.028521 | 0.069728 | 0.027831 | -0.001407 | 0.093665 | 0.19685 | -0.11587 | -0.17788 | 122.1553 | 0.015521 | 122.1828 | 122.1504 | -0.004882 | -0.059132 | 0.18778 | 121.9489 | -0.029931 | 122.1965 | 122.1254 | 0.17648 | 0.073255 | -0.23947 | 122.2659 | 122.1912 | 122.4381 | 122.1373 | -0.095075 | 122.2204 | 122.3236 | 122.0109 | 122.1546 | -0.30148
2122.9219 | 122.4335 | -122.1405 | 0.09613 | 1.4211e-13 | -0.0090769 | 0.021966 | -0.0033377 | -0.0092389 | 0.01057 | -0.006028 | -0.05245 | 0.026498 | 0.0071936 | 0.02822 | 0.0044439 | 0.060567 | 0.005985 | 0.032795 | 0.13912 | 0.059885 | 0.29764 | 0.028521 | 0.074307 | 0.03241 | -0.005985 | 0.084508 | 0.20601 | -0.12045 | -0.18704 | 122.169 | 0.042987 | 122.2011 | 122.1733 | 0.004274 | -0.036245 | 0.20151 | 121.9535 | -0.011622 | 122.2148 | 122.1345 | 0.18106 | 0.10988 | -0.21658 | 122.2796 | 122.2004 | 122.4381 | 122.1465 | -0.067609 | 122.225 | 122.3465 | 122.0201 | 122.1729 | -0.28317
2124.6875 | 122.4014 | -122.1634 | 0.1236 | 1.4211e-13 | -0.0092905 | 0.021966 | -0.0035515 | -0.0094525 | 0.010143 | 0.0016025 | -0.052237 | 0.026498 | 0.0071936 | 0.02822 | 0.0046577 | 0.055988 | 0.010564 | 0.023639 | 0.13912 | 0.069043 | 0.31595 | 0.042258 | 0.06515 | 0.036989 | -0.010564 | 0.093665 | 0.19685 | -0.11587 | -0.17788 | 122.2056 | 0.015521 | 122.2194 | 122.187 | -0.018619 | -0.054553 | 0.19236 | 121.9855 | -0.029931 | 122.2285 | 122.1528 | 0.16732 | 0.073255 | -0.23947 | 122.3025 | 122.2324 | 122.4793 | 122.174 | -0.081338 | 122.2571 | 122.3602 | 122.0475 | 122.2004 | -0.30148
2126.4375 | 122.4564 | -122.113 | 0.082397 | 1.4211e-13 | -0.0090769 | 0.021966 | -0.0033377 | -0.0094525 | 0.010143 | 0.0016025 | -0.05245 | 0.026712 | 0.0076208 | 0.028433 | 0.0046577 | 0.055988 | 0.010564 | 0.023639 | 0.12538 | 0.069043 | 0.3068 | 0.019363 | 0.060571 | 0.027831 | -0.010564 | 0.089087 | 0.19685 | -0.12045 | -0.16873 | 122.1324 | 0.042985 | 122.169 | 122.1367 | 0.004276 | -0.013354 | 0.2244 | 121.9443 | 0.00669 | 122.1736 | 122.1025 | 0.15816 | 0.11445 | -0.20285 | 122.2384 | 122.1821 | 122.4198 | 122.1236 | -0.063034 | 122.2021 | 122.3099 | 121.9926 | 122.1409 | -0.25112
2128.1406 | 122.319 | -122.1909 | 0.13275 | 1.4211e-13 | -0.0095041 | 0.02218 | -0.0031241 | -0.0092389 | 0.01057 | 0.0016025 | -0.05245 | 0.026712 | 0.0076208 | 0.02822 | 0.0044439 | 0.055988 | 0.001407 | 0.028217 | 0.13912 | 0.078201 | 0.32053 | 0.037679 | 0.06515 | 0.027831 | -0.005985 | 0.084508 | 0.19685 | -0.10671 | -0.18246 | 122.2285 | 0.006366 | 122.2468 | 122.2191 | -0.009462 | -0.05455 | 0.18778 | 122.0084 | -0.048243 | 122.256 | 122.1849 | 0.17648 | 0.0641 | -0.23947 | 122.33 | 122.2691 | 122.5114 | 122.1923 | -0.095072 | 122.2754 | 122.3877 | 122.0841 | 122.2187 | -0.31522
2129.8906 | 122.4106 | -122.1588 | 0.11444 | 1.4211e-13 | -0.0090769 | 0.02218 | -0.0031241 | -0.0090251 | 0.010143 | -0.006028 | -0.05245 | 0.026498 | 0.0074072 | 0.027579 | 0.0048713 | 0.060567 | 0.001407 | 0.028217 | 0.13912 | 0.073622 | 0.3068 | 0.023942 | 0.06515 | 0.027831 | -0.010564 | 0.098244 | 0.20601 | -0.11587 | -0.17788 | 122.1828 | 0.024676 | 122.2194 | 122.187 | 0.004275 | -0.040819 | 0.19235 | 121.9809 | -0.016197 | 122.224 | 122.1482 | 0.16732 | 0.091567 | -0.23031 | 122.2979 | 122.2324 | 122.4656 | 122.1602 | -0.090499 | 122.2571 | 122.3648 | 122.0429 | 122.1866 | -0.29233
2131.5938 | 122.4106 | -122.168 | 0.086975 | 1.4211e-13 | -0.0092905 | 0.021752 | -0.0035515 | -0.0094525 | 0.010356 | 0.0016025 | -0.052664 | 0.026284 | 0.0076208 | 0.028647 | 0.0048713 | 0.05141 | 0.001407 | 0.032795 | 0.13912 | 0.069043 | 0.31137 | 0.019363 | 0.069728 | 0.03241 | -0.005985 | 0.084508 | 0.19685 | -0.12045 | -0.17788 | 122.1873 | 0.052142 | 122.2194 | 122.2008 | 0.013432 | -0.017932 | 0.2244 | 121.9901 | -0.002467 | 122.2377 | 122.162 | 0.1719 | 0.10988 | -0.20742 | 122.3071 | 122.237 | 122.4793 | 122.1694 | -0.067612 | 122.2525 | 122.3648 | 122.0475 | 122.2004 | -0.26486
2133.3594 | 122.3831 | -122.1863 | 0.11902 | 1.4211e-13 | -0.0097179 | 0.021966 | -0.0033377 | -0.0088115 | 0.010356 | -0.006028 | -0.052237 | 0.026284 | 0.0071936 | 0.028006 | 0.0044439 | 0.060567 | 0.005985 | 0.028217 | 0.13454 | 0.078201 | 0.31137 | 0.0331 | 0.055992 | 0.027831 | -0.015143 | 0.089087 | 0.19685 | -0.12503 | -0.18246 | 122.2194 | 0.01552 | 122.2468 | 122.2145 | -0.004883 | -0.040818 | 0.19235 | 122.0038 | -0.029932 | 122.2423 | 122.1711 | 0.16732 | 0.077832 | -0.24405 | 122.3208 | 122.2645 | 122.4977 | 122.1923 | -0.085919 | 122.2754 | 122.3831 | 122.0613 | 122.2141 | -0.30148
2135.0625 | 122.4884 | -122.1634 | 0.10071 | 1.4211e-13 | -0.0090769 | 0.02218 | -0.0033377 | -0.0092389 | 0.010143 | 0.0092325 | -0.05245 | 0.026712 | 0.0076208 | 0.028433 | 0.0046577 | 0.065145 | 0.005985 | 0.028217 | 0.13912 | 0.069043 | 0.31137 | 0.019363 | 0.06515 | 0.03241 | -0.005985 | 0.089087 | 0.19227 | -0.12045 | -0.17331 | 122.1828 | 0.038409 | 122.2285 | 122.1916 | 0.008854 | -0.031665 | 0.21067 | 121.9901 | -0.011621 | 122.2285 | 122.1574 | 0.16732 | 0.091564 | -0.22116 | 122.3025 | 122.2324 | 122.4748 | 122.1694 | -0.081345 | 122.2525 | 122.3557 | 122.0429 | 122.1958 | -0.27401
2136.8281 | 122.374 | -122.1817 | 0.13733 | 1.4211e-13 | -0.0092905 | 0.021966 | -0.0031241 | -0.0092389 | 0.010356 | -0.006028 | -0.052237 | 0.026284 | 0.0078344 | 0.028006 | 0.0048713 | 0.060567 | 0.005985 | 0.028217 | 0.13454 | 0.069043 | 0.31137 | 0.028521 | 0.074307 | 0.023253 | -0.010564 | 0.093665 | 0.20601 | -0.11129 | -0.18704 | 122.2102 | -0.00279 | 122.2423 | 122.2099 | -0.000304 | -0.068286 | 0.17404 | 121.9947 | -0.043664 | 122.256 | 122.1711 | 0.17648 | 0.068679 | -0.24862 | 122.3162 | 122.2507 | 122.4931 | 122.1877 | -0.10881 | 122.2754 | 122.3877 | 122.0704 | 122.205 | -0.32437
2138.5938 | 122.4747 | -122.1863 | 0.10529 | 1.4211e-13 | -0.0090769 | 0.02218 | -0.0033377 | -0.0096661 | 0.010143 | 0.0016025 | -0.052023 | 0.026498 | 0.0076208 | 0.02822 | 0.0046577 | 0.060567 | 0.010564 | 0.032795 | 0.13454 | 0.078201 | 0.32053 | 0.019363 | 0.069728 | 0.03241 | -0.010564 | 0.093665 | 0.19685 | -0.12045 | -0.17788 | 122.2056 | 0.029253 | 122.2468 | 122.2191 | 0.013432 | -0.027085 | 0.21525 | 122.0084 | -0.011621 | 122.256 | 122.1757 | 0.16732 | 0.091565 | -0.22574 | 122.3208 | 122.2645 | 122.5068 | 122.1968 | -0.085923 | 122.2799 | 122.3831 | 122.0658 | 122.2187 | -0.28317
2140.3594 | 122.3831 | -122.2046 | 0.13275 | 1.4211e-13 | -0.0090769 | 0.02218 | -0.0035515 | -0.0094525 | 0.01057 | 0.0092325 | -0.05245 | 0.026284 | 0.0071936 | 0.028006 | 0.0042303 | 0.055988 | 0.010564 | 0.01906 | 0.13454 | 0.069043 | 0.31137 | 0.037679 | 0.06515 | 0.027831 | -0.010564 | 0.098244 | 0.20143 | -0.11587 | -0.17331 | 122.2423 | 0.001788 | 122.2606 | 122.2236 | -0.018619 | -0.063708 | 0.17862 | 122.0313 | -0.034507 | 122.2697 | 122.194 | 0.16274 | 0.068678 | -0.24862 | 122.3391 | 122.2736 | 122.516 | 122.2152 | -0.095072 | 122.3028 | 122.406 | 122.0887 | 122.2324 | -0.30606
2142.0625 | 122.4106 | -122.2183 | 0.14648 | 1.4211e-13 | -0.0088631 | 0.02218 | -0.0033377 | -0.0094525 | 0.010356 | 0.0016025 | -0.052023 | 0.026498 | 0.0076208 | 0.02822 | 0.0048713 | 0.060567 | 0.005985 | 0.023639 | 0.13912 | 0.073622 | 0.31137 | 0.0331 | 0.06515 | 0.03241 | -0.015143 | 0.089087 | 0.19685 | -0.11587 | -0.17788 | 122.2514 | -0.007367 | 122.2789 | 122.242 | -0.009461 | -0.072862 | 0.16489 | 122.0404 | -0.057397 | 122.2835 | 122.2032 | 0.16274 | 0.050367 | -0.26236 | 122.3574 | 122.2919 | 122.5297 | 122.2243 | -0.11338 | 122.3074 | 122.4152 | 122.1025 | 122.2507 | -0.32437
2143.8125 | 122.4564 | -122.2046 | 0.11902 | 1.4211e-13 | -0.0090769 | 0.02218 | -0.0033377 | -0.0092389 | 0.010143 | -0.013659 | -0.05245 | 0.026498 | 0.0076208 | 0.028433 | 0.0044439 | 0.074302 | 0.005985 | 0.01906 | 0.13912 | 0.073622 | 0.31595 | 0.023942 | 0.06515 | 0.023253 | -0.010564 | 0.098244 | 0.19685 | -0.12045 | -0.17788 | 122.2285 | 0.020098 | 122.2789 | 122.2236 | -0.004882 | -0.045397 | 0.19693 | 122.0267 | -0.020775 | 122.2697 | 122.194 | 0.16732 | 0.077832 | -0.23947 | 122.3437 | 122.2782 | 122.5205 | 122.2106 | -0.095077 | 122.3028 | 122.4014 | 122.0841 | 122.2278 | -0.2969
2145.5 | 122.5067 | -122.1863 | 0.082397 | 1.4211e-13 | -0.0088631 | 0.021966 | -0.0033377 | -0.0094525 | 0.01057 | 0.0016025 | -0.052878 | 0.026071 | 0.0074072 | 0.028433 | 0.0046577 | 0.060567 | 0.005985 | 0.032795 | 0.13912 | 0.046148 | 0.30222 | 0.023942 | 0.06515 | 0.03241 | -0.005985 | 0.084508 | 0.19227 | -0.11587 | -0.18246 | 122.2102 | 0.05672 | 122.2468 | 122.2191 | 0.008853 | -0.036249 | 0.21982 | 122.0038 | 0.002111 | 122.2514 | 122.1803 | 0.17648 | 0.10988 | -0.19827 | 122.3254 | 122.2324 | 122.4885 | 122.1923 | -0.058455 | 122.2708 | 122.3786 | 122.0704 | 122.2187 | -0.26486
2147.2031 | 122.3694 | -122.2549 | 0.13275 | 1.4211e-13 | -0.0090769 | 0.021966 | -0.0031241 | -0.0092389 | 0.010356 | 0.0016025 | -0.052878 | 0.026498 | 0.0076208 | 0.02822 | 0.0048713 | 0.065145 | 0.010564 | 0.032795 | 0.13454 | 0.073622 | 0.31137 | 0.042258 | 0.051413 | 0.03241 | -0.005985 | 0.093665 | 0.19685 | -0.12045 | -0.17788 | 122.2972 | 0.001788 | 122.3201 | 122.2877 | -0.009463 | -0.059129 | 0.17862 | 122.0771 | -0.039086 | 122.3064 | 122.249 | 0.1719 | 0.0641 | -0.2532 | 122.3895 | 122.3286 | 122.5663 | 122.2655 | -0.090493 | 122.3486 | 122.4518 | 122.1345 | 122.2874 | -0.31064
2148.9688 | 122.4564 | -122.1954 | 0.10071 | 1.4211e-13 | -0.0092905 | 0.022393 | -0.0031241 | -0.0096661 | 0.01057 | -0.013659 | -0.05245 | 0.026284 | 0.0076208 | 0.02822 | 0.0046577 | 0.060567 | 0.010564 | 0.032795 | 0.13912 | 0.064464 | 0.31137 | 0.037679 | 0.06515 | 0.03241 | -0.001407 | 0.084508 | 0.19685 | -0.11587 | -0.17788 | 122.2331 | 0.038409 | 122.256 | 122.2282 | -0.004884 | -0.036244 | 0.21067 | 122.0175 | -0.0162 | 122.2606 | 122.194 | 0.17648 | 0.096143 | -0.21658 | 122.3346 | 122.2599 | 122.5068 | 122.206 | -0.063029 | 122.2799 | 122.3923 | 122.0796 | 122.2278 | -0.27859
2150.7188 | 122.4609 | -122.2366 | 0.10529 | 1.4211e-13 | -0.0092905 | 0.021752 | -0.0031241 | -0.0094525 | 0.01057 | -0.006028 | -0.052237 | 0.026284 | 0.0071936 | 0.02822 | 0.0046577 | 0.065145 | 0.010564 | 0.023639 | 0.13912 | 0.073622 | 0.3068 | 0.037679 | 0.069728 | 0.03241 | -0.005985 | 0.093665 | 0.20143 | -0.12503 | -0.18246 | 122.2743 | 0.033831 | 122.3018 | 122.2603 | -0.01404 | -0.031664 | 0.20151 | 122.0542 | -0.011621 | 122.3064 | 122.2306 | 0.17648 | 0.096143 | -0.23031 | 122.3757 | 122.3103 | 122.5434 | 122.2472 | -0.067607 | 122.3303 | 122.4381 | 122.1116 | 122.269 | -0.28775
2152.4219 | 122.4106 | -122.2504 | 0.11902 | 1.4211e-13 | -0.0092905 | 0.02218 | -0.0029103 | -0.0092389 | 0.010356 | 0.0016025 | -0.05245 | 0.026712 | 0.0074072 | 0.028433 | 0.0044439 | 0.069723 | 0.005985 | 0.032795 | 0.12996 | 0.064464 | 0.3068 | 0.019363 | 0.06515 | 0.023253 | -0.010564 | 0.084508 | 0.20601 | -0.11129 | -0.17331 | 122.2697 | 0.010941 | 122.3201 | 122.2832 | 0.013432 | -0.054555 | 0.18778 | 122.0771 | -0.034511 | 122.3155 | 122.2398 | 0.16274 | 0.086989 | -0.23031 | 122.3803 | 122.3148 | 122.5572 | 122.2564 | -0.099656 | 122.3349 | 122.4564 | 122.1391 | 122.2736 | -0.29233
2154.1719 | 122.4747 | -122.2549 | 0.10986 | 1.4211e-13 | -0.0090769 | 0.02218 | -0.0031241 | -0.0090251 | 0.010143 | -0.006028 | -0.05245 | 0.026284 | 0.0071936 | 0.02822 | 0.0042303 | 0.065145 | -0.003172 | 0.028217 | 0.13912 | 0.050727 | 0.31595 | 0.019363 | 0.06515 | 0.027831 | -0.010564 | 0.089087 | 0.19227 | -0.11587 | -0.17788 | 122.2743 | 0.029254 | 122.3201 | 122.2832 | 0.008854 | -0.059136 | 0.20609 | 122.0771 | -0.020776 | 122.3201 | 122.2444 | 0.16732 | 0.082409 | -0.22574 | 122.3941 | 122.3057 | 122.5709 | 122.2518 | -0.0905 | 122.344 | 122.4472 | 122.1391 | 122.2828 | -0.28775
2155.875 | 122.5159 | -122.2046 | 0.091553 | 1.4211e-13 | -0.0090769 | 0.02218 | -0.0033377 | -0.0092389 | 0.010356 | -0.006028 | -0.052237 | 0.026498 | 0.0076208 | 0.02822 | 0.0046577 | 0.065145 | 0.005985 | 0.023639 | 0.13912 | 0.064464 | 0.31595 | 0.019363 | 0.06515 | 0.027831 | -0.010564 | 0.093665 | 0.20143 | -0.12503 | -0.17331 | 122.224 | 0.047564 | 122.2697 | 122.2282 | 0.004276 | -0.027089 | 0.2244 | 122.0313 | 0.002112 | 122.2697 | 122.194 | 0.16274 | 0.10988 | -0.21658 | 122.3437 | 122.2691 | 122.5205 | 122.2106 | -0.07219 | 122.2983 | 122.406 | 122.0796 | 122.2324 | -0.26486
2157.6406 | 122.4609 | -122.2549 | 0.13733 | 1.4211e-13 | -0.0092905 | 0.021966 | -0.0033377 | -0.0090251 | 0.010784 | 0.0016025 | -0.052237 | 0.026498 | 0.0074072 | 0.028006 | 0.0048713 | 0.065145 | 0.005985 | 0.023639 | 0.13912 | 0.069043 | 0.3068 | 0.028521 | 0.060571 | 0.03241 | -0.010564 | 0.093665 | 0.20143 | -0.11129 | -0.17331 | 122.2835 | 0.001788 | 122.3201 | 122.2786 | -0.004882 | -0.068286 | 0.16947 | 122.0816 | -0.043664 | 122.3155 | 122.2444 | 0.16274 | 0.0641 | -0.24862 | 122.3941 | 122.324 | 122.5617 | 122.2609 | -0.10881 | 122.3486 | 122.4564 | 122.1437 | 122.2874 | -0.31063
2159.4062 | 122.525 | -122.2 | 0.10986 | 1.4211e-13 | -0.0092905 | 0.021966 | -0.0031241 | -0.0096661 | 0.010143 | 0.0092325 | -0.05245 | 0.026498 | 0.0071936 | 0.028006 | 0.0044439 | 0.065145 | 0.005985 | 0.028217 | 0.12996 | 0.064464 | 0.31595 | 0.051416 | 0.060571 | 0.027831 | -0.015143 | 0.093665 | 0.19685 | -0.12045 | -0.17788 | 122.2514 | 0.020097 | 122.2652 | 122.2282 | -0.023199 | -0.045399 | 0.20609 | 122.0221 | -0.016198 | 122.2606 | 122.1849 | 0.16274 | 0.086988 | -0.23031 | 122.33 | 122.2645 | 122.516 | 122.206 | -0.058447 | 122.2937 | 122.3969 | 122.0796 | 122.2278 | -0.28775
2161.0938 | 122.4106 | -122.2641 | 0.13275 | 1.4211e-13 | -0.0090769 | 0.021966 | -0.0033377 | -0.0092389 | 0.01057 | 0.0092325 | -0.052664 | 0.026284 | 0.0074072 | 0.02822 | 0.0046577 | 0.060567 | 0.005985 | 0.01906 | 0.13912 | 0.073622 | 0.31137 | 0.028521 | 0.06515 | 0.023253 | -0.015143 | 0.089087 | 0.19685 | -0.11587 | -0.17788 | 122.2926 | 0.006366 | 122.3247 | 122.2832 | -0.009461 | -0.059129 | 0.17862 | 122.0862 | -0.043664 | 122.3292 | 122.249 | 0.16274 | 0.0641 | -0.24862 | 122.4032 | 122.3377 | 122.5755 | 122.2701 | -0.10423 | 122.3532 | 122.4609 | 122.1482 | 122.2874 | -0.31064
2162.8438 | 122.5342 | -122.2366 | 0.10529 | 1.4211e-13 | -0.0088631 | 0.021966 | -0.0031241 | -0.0094525 | 0.010356 | 0.0016025 | -0.05245 | 0.026284 | 0.0074072 | 0.02822 | 0.0044439 | 0.055988 | 0.010564 | 0.023639 | 0.13912 | 0.073622 | 0.31137 | 0.014784 | 0.06515 | 0.027831 | -0.005985 | 0.093665 | 0.19685 | -0.11587 | -0.17331 | 122.2514 | 0.033831 | 122.2926 | 122.2603 | 0.008855 | -0.031664 | 0.20609 | 122.0633 | -0.011621 | 122.3018 | 122.2306 | 0.16732 | 0.091565 | -0.22116 | 122.3757 | 122.3103 | 122.548 | 122.2472 | -0.090502 | 122.3303 | 122.4335 | 122.1208 | 122.2645 | -0.27859
2164.6094 | 122.3923 | -122.2961 | 0.14191 | 1.4211e-13 | -0.0086495 | 0.02218 | -0.0033377 | -0.0092389 | 0.01057 | -0.006028 | -0.05245 | 0.026498 | 0.0071936 | 0.028433 | 0.0046577 | 0.065145 | 0.001407 | 0.023639 | 0.13454 | 0.073622 | 0.31137 | 0.019363 | 0.06515 | 0.023253 | -0.019721 | 0.093665 | 0.20143 | -0.12045 | -0.17331 | 122.3155 | -0.007368 | 122.3613 | 122.3198 | 0.004276 | -0.068285 | 0.16947 | 122.1228 | -0.048242 | 122.3613 | 122.2764 | 0.15358 | 0.059522 | -0.26236 | 122.4307 | 122.3698 | 122.6075 | 122.2976 | -0.12254 | 122.3898 | 122.4976 | 122.1757 | 122.3194 | -0.31521
2166.3594 | 122.5342 | -122.2275 | 0.091553 | 1.4211e-13 | -0.0090769 | 0.022393 | -0.0031241 | -0.0092389 | 0.01057 | 0.0016025 | -0.052664 | 0.026071 | 0.0074072 | 0.02822 | 0.0046577 | 0.060567 | 0.005985 | 0.028217 | 0.13912 | 0.069043 | 0.3068 | 0.028521 | 0.069728 | 0.027831 | -0.005985 | 0.089087 | 0.20143 | -0.12045 | -0.17788 | 122.256 | 0.047564 | 122.288 | 122.2557 | -0.000304 | -0.02251 | 0.21524 | 122.0496 | -0.002466 | 122.2972 | 122.2215 | 0.1719 | 0.10988 | -0.212 | 122.3666 | 122.2965 | 122.5343 | 122.2335 | -0.063032 | 122.3166 | 122.4289 | 122.107 | 122.2553 | -0.26944
2168.125 | 122.5433 | -122.2458 | 0.10071 | 1.4211e-13 | -0.0090769 | 0.02218 | -0.0033377 | -0.0092389 | 0.010356 | 0.0016025 | -0.05245 | 0.026498 | 0.0076208 | 0.028006 | 0.0046577 | 0.065145 | -0.003172 | 0.028217 | 0.13454 | 0.069043 | 0.31137 | 0.037679 | 0.06515 | 0.023253 | -0.010564 | 0.093665 | 0.20143 | -0.12503 | -0.17788 | 122.2835 | 0.033831 | 122.3109 | 122.274 | -0.009462 | -0.031665 | 0.21067 | 122.0679 | -0.007043 | 122.3109 | 122.2352 | 0.16732 | 0.10072 | -0.22574 | 122.3803 | 122.3148 | 122.5572 | 122.2426 | -0.063029 | 122.3395 | 122.4472 | 122.1208 | 122.269 | -0.27859
2169.875 | 122.5204 | -122.2549 | 0.10986 | 1.4211e-13 | -0.0090769 | 0.021752 | -0.0035515 | -0.0096661 | 0.010356 | -0.006028 | -0.052664 | 0.026712 | 0.0076208 | 0.02822 | 0.0046577 | 0.060567 | 0.005985 | 0.01906 | 0.13454 | 0.069043 | 0.31595 | 0.0331 | 0.060571 | 0.027831 | -0.010564 | 0.089087 | 0.21059 | -0.11587 | -0.16873 | 122.288 | 0.024676 | 122.3155 | 122.274 | -0.01404 | -0.04082 | 0.20609 | 122.0862 | -0.020776 | 122.3155 | 122.2444 | 0.15816 | 0.10072 | -0.22574 | 122.3895 | 122.324 | 122.5709 | 122.2609 | -0.076763 | 122.344 | 122.4655 | 122.1391 | 122.2828 | -0.27859
2171.5625 | 122.4243 | -122.2961 | 0.13275 | 1.4211e-13 | -0.0088631 | 0.021966 | -0.0031241 | -0.0092389 | 0.01057 | 0.0016025 | -0.05245 | 0.026925 | 0.0071936 | 0.028433 | 0.0046577 | 0.055988 | 0.001407 | 0.023639 | 0.12996 | 0.078201 | 0.31595 | 0.019363 | 0.06515 | 0.027831 | -0.005985 | 0.089087 | 0.20143 | -0.11587 | -0.17788 | 122.3155 | -0.002791 | 122.3521 | 122.3198 | 0.004276 | -0.05455 | 0.1832 | 122.1183 | -0.043664 | 122.3613 | 122.2902 | 0.1719 | 0.068678 | -0.24862 | 122.4261 | 122.3743 | 122.6121 | 122.2976 | -0.11339 | 122.3852 | 122.4976 | 122.1803 | 122.324 | -0.31064
2173.3281 | 122.4518 | -122.2824 | 0.12817 | 1.4211e-13 | -0.0090769 | 0.02218 | -0.0031241 | -0.0092389 | 0.010143 | -0.006028 | -0.05245 | 0.026498 | 0.0074072 | 0.028647 | 0.0046577 | 0.069723 | 0.001407 | 0.01906 | 0.13454 | 0.073622 | 0.31595 | 0.014784 | 0.069728 | 0.023253 | -0.015143 | 0.10282 | 0.20601 | -0.11129 | -0.17788 | 122.2972 | 0.006365 | 122.3521 | 122.3015 | 0.004276 | -0.054552 | 0.18778 | 122.1045 | -0.025352 | 122.3521 | 122.2673 | 0.16274 | 0.077834 | -0.23947 | 122.4169 | 122.356 | 122.5984 | 122.2838 | -0.11339 | 122.3852 | 122.4884 | 122.1711 | 122.3057 | -0.30606
2175.0781 | 122.438 | -122.319 | 0.13275 | 1.4211e-13 | -0.0088631 | 0.021966 | -0.0033377 | -0.0092389 | 0.010356 | 0.0092325 | -0.052237 | 0.026498 | 0.0076208 | 0.02822 | 0.0050849 | 0.060567 | -0.007751 | 0.009904 | 0.13912 | 0.069043 | 0.3068 | 0.028521 | 0.069728 | 0.023253 | -0.005985 | 0.089087 | 0.20601 | -0.12503 | -0.17788 | 122.3476 | 0.006366 | 122.3796 | 122.3289 | -0.018617 | -0.063708 | 0.17405 | 122.1411 | -0.043664 | 122.3888 | 122.313 | 0.1719 | 0.073257 | -0.25778 | 122.4581 | 122.3881 | 122.6258 | 122.3113 | -0.10423 | 122.4081 | 122.525 | 122.194 | 122.3423 | -0.31064
2176.8281 | 122.5708 | -122.2641 | 0.10071 | 1.4211e-13 | -0.0090769 | 0.02218 | -0.0033377 | -0.0094525 | 0.010143 | 0.0092325 | -0.05245 | 0.026498 | 0.0078344 | 0.02822 | 0.0044439 | 0.060567 | 0.010564 | 0.023639 | 0.13912 | 0.069043 | 0.31137 | 0.023942 | 0.069728 | 0.03241 | -0.005985 | 0.084508 | 0.19685 | -0.12045 | -0.17331 | 122.288 | 0.038409 | 122.3247 | 122.2877 | -0.000303 | -0.031665 | 0.21067 | 122.0908 | -0.0162 | 122.3338 | 122.2581 | 0.16732 | 0.096143 | -0.22116 | 122.4032 | 122.3331 | 122.5755 | 122.2747 | -0.076766 | 122.3486 | 122.4609 | 122.1436 | 122.2965 | -0.27401
2178.5312 | 122.5342 | -122.2366 | 0.10529 | 1.4211e-13 | -0.0095041 | 0.021966 | -0.0031241 | -0.0094525 | 0.01057 | -0.006028 | -0.052237 | 0.026284 | 0.0074072 | 0.02822 | 0.0046577 | 0.065145 | 0.005985 | 0.01906 | 0.13912 | 0.064464 | 0.31137 | 0.028521 | 0.06515 | 0.027831 | -0.005985 | 0.098244 | 0.20143 | -0.11587 | -0.18246 | 122.2652 | 0.033831 | 122.3018 | 122.2557 | -0.009461 | -0.040822 | 0.20609 | 122.0542 | -0.007042 | 122.3018 | 122.2306 | 0.17648 | 0.096143 | -0.22116 | 122.3757 | 122.3011 | 122.548 | 122.2426 | -0.076765 | 122.3349 | 122.4381 | 122.1208 | 122.2645 | -0.28775
2180.2969 | 122.5479 | -122.2687 | 0.09613 | 1.4211e-13 | -0.0088631 | 0.02218 | -0.0031241 | -0.0094525 | 0.010356 | 0.0016025 | -0.05245 | 0.026498 | 0.0076208 | 0.028433 | 0.0046577 | 0.060567 | 0.005985 | 0.023639 | 0.13912 | 0.069043 | 0.31595 | 0.028521 | 0.069728 | 0.027831 | -0.010564 | 0.093665 | 0.20143 | -0.12503 | -0.17331 | 122.2972 | 0.042987 | 122.3292 | 122.2923 | -0.004882 | -0.027087 | 0.21982 | 122.0954 | -0.002465 | 122.3384 | 122.2581 | 0.16274 | 0.1053 | -0.22116 | 122.4078 | 122.3377 | 122.5846 | 122.2747 | -0.067609 | 122.3623 | 122.4701 | 122.1436 | 122.2965 | -0.26944
2182 | 122.4518 | -122.2961 | 0.11902 | 1.4211e-13 | -0.0088631 | 0.022393 | -0.0031241 | -0.0094525 | 0.010143 | -0.006028 | -0.05245 | 0.026498 | 0.0078344 | 0.028006 | 0.0044439 | 0.060567 | 0.010564 | 0.023639 | 0.12996 | 0.059885 | 0.31595 | 0.028521 | 0.06515 | 0.03241 | -0.010564 | 0.093665 | 0.20601 | -0.11129 | -0.17788 | 122.3247 | 0.010941 | 122.3567 | 122.3198 | -0.004882 | -0.059134 | 0.19693 | 122.1183 | -0.025354 | 122.3613 | 122.2856 | 0.16732 | 0.086989 | -0.23031 | 122.4261 | 122.356 | 122.6121 | 122.3067 | -0.090498 | 122.3898 | 122.5022 | 122.1848 | 122.3286 | -0.2969
2183.7656 | 122.4792 | -122.2961 | 0.1236 | 1.4211e-13 | -0.0092905 | 0.021966 | -0.0033377 | -0.0094525 | 0.010356 | -0.006028 | -0.052237 | 0.026712 | 0.0071936 | 0.02822 | 0.0046577 | 0.05141 | 0.005985 | 0.014482 | 0.13454 | 0.078201 | 0.32053 | 0.019363 | 0.06515 | 0.023253 | -0.005985 | 0.089087 | 0.19685 | -0.12045 | -0.17331 | 122.3155 | 0.010943 | 122.3476 | 122.3106 | -0.004881 | -0.045395 | 0.19694 | 122.1228 | -0.034509 | 122.3613 | 122.2902 | 0.16732 | 0.073255 | -0.24405 | 122.4307 | 122.3743 | 122.6167 | 122.3021 | -0.10423 | 122.3852 | 122.493 | 122.1757 | 122.3194 | -0.2969
2185.5312 | 122.4472 | -122.3282 | 0.13733 | 1.4211e-13 | -0.0090769 | 0.02218 | -0.0033377 | -0.0094525 | 0.010356 | -0.013659 | -0.052237 | 0.026071 | 0.0078344 | 0.02822 | 0.0046577 | 0.060567 | 0.001407 | 0.028217 | 0.13912 | 0.059885 | 0.31137 | 0.037679 | 0.06515 | 0.03241 | -0.010564 | 0.098244 | 0.20143 | -0.12045 | -0.17788 | 122.3659 | 0.001788 | 122.3888 | 122.3564 | -0.009462 | -0.077444 | 0.17404 | 122.1503 | -0.039085 | 122.3933 | 122.3176 | 0.16732 | 0.0641 | -0.25778 | 122.4673 | 122.3881 | 122.6396 | 122.3296 | -0.09965 | 122.4264 | 122.5296 | 122.2077 | 122.3606 | -0.31521
2187.2812 | 122.5159 | -122.3236 | 0.11902 | 1.4211e-13 | -0.0090769 | 0.02218 | -0.0033377 | -0.0092389 | 0.010356 | 0.0016025 | -0.052664 | 0.026925 | 0.0078344 | 0.02822 | 0.0048713 | 0.060567 | -0.003172 | 0.023639 | 0.12996 | 0.073622 | 0.31595 | 0.023942 | 0.055992 | 0.027831 | -0.010564 | 0.089087 | 0.20601 | -0.12045 | -0.18704 | 122.3475 | 0.010941 | 122.3842 | 122.3472 | -0.000303 | -0.045397 | 0.19693 | 122.1366 | -0.029932 | 122.3796 | 122.313 | 0.17648 | 0.086989 | -0.23947 | 122.4536 | 122.3972 | 122.6396 | 122.3204 | -0.095077 | 122.4127 | 122.5296 | 122.2032 | 122.3514 | -0.30606
2189.0469 | 122.5204 | -122.3099 | 0.10986 | 1.4211e-13 | -0.0088631 | 0.02218 | -0.0031241 | -0.0092389 | 0.010356 | -0.006028 | -0.052237 | 0.026712 | 0.0078344 | 0.028006 | 0.0044439 | 0.065145 | -0.003172 | 0.023639 | 0.12996 | 0.073622 | 0.31137 | 0.023942 | 0.060571 | 0.023253 | -0.010564 | 0.093665 | 0.20143 | -0.12045 | -0.17331 | 122.3338 | 0.020097 | 122.375 | 122.3335 | -0.000303 | -0.036241 | 0.20151 | 122.1366 | -0.016198 | 122.3704 | 122.2993 | 0.16274 | 0.091566 | -0.23031 | 122.4398 | 122.3835 | 122.6212 | 122.3067 | -0.085921 | 122.4035 | 122.5113 | 122.1894 | 122.3331 | -0.28317
2190.8125 | 122.4564 | -122.3145 | 0.13733 | 1.4211e-13 | -0.0092905 | 0.021966 | -0.0035515 | -0.0094525 | 0.010356 | -0.006028 | -0.052664 | 0.026498 | 0.0074072 | 0.028433 | 0.0046577 | 0.055988 | -0.003172 | 0.01906 | 0.12996 | 0.078201 | 0.31137 | 0.019363 | 0.060571 | 0.027831 | -0.005985 | 0.084508 | 0.19685 | -0.11587 | -0.19162 | 122.3338 | -0.007369 | 122.3704 | 122.3335 | -0.000303 | -0.059128 | 0.17404 | 122.1228 | -0.052821 | 122.375 | 122.3085 | 0.18564 | 0.059522 | -0.2532 | 122.4444 | 122.3927 | 122.6258 | 122.3113 | -0.11797 | 122.399 | 122.5113 | 122.1986 | 122.3423 | -0.32895
2192.5312 | 122.5433 | -122.3099 | 0.10529 | 1.4211e-13 | -0.0088631 | 0.02218 | -0.0037651 | -0.0094525 | 0.010356 | 0.0016025 | -0.052237 | 0.026498 | 0.0071936 | 0.028433 | 0.0048713 | 0.065145 | -0.003172 | 0.028217 | 0.12996 | 0.073622 | 0.31595 | 0.023942 | 0.074307 | 0.027831 | -0.005985 | 0.089087 | 0.20143 | -0.11587 | -0.17788 | 122.3338 | 0.024674 | 122.375 | 122.3381 | 0.004275 | -0.031664 | 0.21067 | 122.132 | -0.016199 | 122.3842 | 122.3039 | 0.1719 | 0.096143 | -0.22116 | 122.4398 | 122.3835 | 122.6258 | 122.3067 | -0.081344 | 122.399 | 122.5113 | 122.194 | 122.3377 | -0.28317
2194.2969 | 122.4884 | -122.319 | 0.11444 | 1.4211e-13 | -0.0090769 | 0.02218 | -0.0035515 | -0.0090251 | 0.010143 | -0.006028 | -0.05245 | 0.026498 | 0.0074072 | 0.028433 | 0.0046577 | 0.060567 | 0.001407 | 0.023639 | 0.13912 | 0.050727 | 0.3068 | 0.028521 | 0.060571 | 0.03241 | -0.010564 | 0.089087 | 0.20143 | -0.12045 | -0.17331 | 122.3476 | 0.024676 | 122.3796 | 122.3427 | -0.004882 | -0.063714 | 0.19235 | 122.1457 | -0.025354 | 122.3796 | 122.3085 | 0.16274 | 0.086988 | -0.23489 | 122.4581 | 122.3698 | 122.6258 | 122.3204 | -0.08592 | 122.4081 | 122.5205 | 122.1986 | 122.3514 | -0.28775
2196.0625 | 122.5433 | -122.3328 | 0.091553 | 1.4211e-13 | -0.0092905 | 0.021752 | -0.0031241 | -0.0092389 | 0.010356 | 0.0016025 | -0.052664 | 0.026498 | 0.0069798 | 0.02822 | 0.0046577 | 0.055988 | 0.005985 | 0.014482 | 0.13454 | 0.073622 | 0.3068 | 0.028521 | 0.06515 | 0.036989 | -0.015143 | 0.089087 | 0.20601 | -0.12045 | -0.17788 | 122.3613 | 0.042986 | 122.3888 | 122.3472 | -0.014039 | -0.017931 | 0.21524 | 122.1549 | -0.002466 | 122.3979 | 122.3176 | 0.16274 | 0.11446 | -0.212 | 122.4673 | 122.4064 | 122.6396 | 122.3387 | -0.063032 | 122.4219 | 122.5388 | 122.2123 | 122.3698 | -0.26944
2197.75 | 122.5571 | -122.3328 | 0.10071 | 1.4211e-13 | -0.0086495 | 0.02218 | -0.0031241 | -0.0094525 | 0.010143 | 0.0016025 | -0.05245 | 0.026284 | 0.0078344 | 0.02822 | 0.0046577 | 0.065145 | 0.001407 | 0.023639 | 0.13454 | 0.073622 | 0.31137 | 0.028521 | 0.06515 | 0.023253 | -0.015143 | 0.098244 | 0.19685 | -0.12503 | -0.18246 | 122.3613 | 0.033831 | 122.3979 | 122.3564 | -0.004882 | -0.027086 | 0.21067 | 122.1503 | -0.002464 | 122.3979 | 122.3176 | 0.16732 | 0.096143 | -0.22574 | 122.4673 | 122.4064 | 122.6441 | 122.3342 | -0.072187 | 122.431 | 122.5296 | 122.2077 | 122.356 | -0.28317
2199.5 | 122.5479 | -122.3465 | 0.1236 | 1.4211e-13 | -0.0092905 | 0.021966 | -0.0031241 | -0.0094525 | 0.010356 | 0.0016025 | -0.052237 | 0.026498 | 0.0071936 | 0.028433 | 0.0046577 | 0.055988 | 0.001407 | 0.023639 | 0.13454 | 0.073622 | 0.31137 | 0.014784 | 0.060571 | 0.027831 | -0.019721 | 0.098244 | 0.19227 | -0.12503 | -0.18246 | 122.3613 | 0.010943 | 122.4025 | 122.3701 | 0.008855 | -0.049974 | 0.18778 | 122.164 | -0.025352 | 122.4071 | 122.3268 | 0.16274 | 0.068676 | -0.24862 | 122.481 | 122.4201 | 122.6579 | 122.3479 | -0.10881 | 122.4447 | 122.5388 | 122.2215 | 122.3743 | -0.30606
2201.25 | 122.612 | -122.3053 | 0.09613 | 1.4211e-13 | -0.0092905 | 0.021966 | -0.0033377 | -0.0094525 | 0.010356 | 0.0092325 | -0.052664 | 0.026498 | 0.0074072 | 0.028433 | 0.0046577 | 0.055988 | 0.005985 | 0.01906 | 0.13454 | 0.069043 | 0.31137 | 0.019363 | 0.069728 | 0.027831 | -0.010564 | 0.098244 | 0.19685 | -0.12045 | -0.18246 | 122.3247 | 0.038409 | 122.3613 | 122.3244 | -0.000303 | -0.027087 | 0.21524 | 122.1228 | 0.002114 | 122.375 | 122.2947 | 0.1719 | 0.10072 | -0.21658 | 122.4398 | 122.3743 | 122.6167 | 122.3113 | -0.076767 | 122.4035 | 122.5021 | 122.1848 | 122.3331 | -0.27859
2202.9531 | 122.493 | -122.3465 | 0.1236 | 1.4211e-13 | -0.0092905 | 0.021966 | -0.0033377 | -0.0096661 | 0.010356 | -0.006028 | -0.05245 | 0.026498 | 0.0078344 | 0.028433 | 0.0040167 | 0.055988 | 0.001407 | 0.028217 | 0.13454 | 0.055306 | 0.31137 | 0.019363 | 0.069728 | 0.023253 | -0.010564 | 0.089087 | 0.20143 | -0.12045 | -0.17788 | 122.3659 | 0.010943 | 122.4025 | 122.3747 | 0.008854 | -0.06829 | 0.18778 | 122.1686 | -0.034509 | 122.4162 | 122.3359 | 0.16732 | 0.077833 | -0.24405 | 122.481 | 122.4018 | 122.6579 | 122.3479 | -0.10423 | 122.4356 | 122.5479 | 122.226 | 122.3697 | -0.30148
2204.7031 | 122.5021 | -122.3557 | 0.12817 | 1.4211e-13 | -0.0086495 | 0.02218 | -0.0033377 | -0.0094525 | 0.010143 | -0.006028 | -0.052664 | 0.026498 | 0.0076208 | 0.028647 | 0.0048713 | 0.060567 | 0.005985 | 0.023639 | 0.14369 | 0.073622 | 0.31595 | 0.019363 | 0.060571 | 0.027831 | -0.005985 | 0.093665 | 0.19685 | -0.12045 | -0.17788 | 122.375 | 0.015521 | 122.4162 | 122.3793 | 0.004276 | -0.054552 | 0.18778 | 122.1778 | -0.034509 | 122.4162 | 122.3497 | 0.1719 | 0.068677 | -0.24862 | 122.4993 | 122.4293 | 122.6716 | 122.3616 | -0.10881 | 122.4493 | 122.5525 | 122.2352 | 122.3835 | -0.30606
2206.4531 | 122.5388 | -122.3419 | 0.10986 | 1.4211e-13 | -0.0092905 | 0.022393 | -0.0033377 | -0.0096661 | 0.010143 | -0.006028 | -0.052237 | 0.026498 | 0.0076208 | 0.028433 | 0.0046577 | 0.055988 | 0.005985 | 0.023639 | 0.13454 | 0.069043 | 0.31595 | 0.019363 | 0.06515 | 0.027831 | -0.005985 | 0.098244 | 0.18769 | -0.12045 | -0.17331 | 122.3613 | 0.024676 | 122.3979 | 122.3656 | 0.004276 | -0.04082 | 0.20609 | 122.1686 | -0.011619 | 122.4071 | 122.3359 | 0.16732 | 0.07783 | -0.23031 | 122.4765 | 122.411 | 122.6579 | 122.3479 | -0.0905 | 122.4402 | 122.5296 | 122.2215 | 122.3698 | -0.28317
2208.2031 | 122.5525 | -122.3602 | 0.10529 | 1.4211e-13 | -0.0092905 | 0.02218 | -0.0033377 | -0.0092389 | 0.010356 | 0.0016025 | -0.052237 | 0.026712 | 0.0071936 | 0.028647 | 0.0044439 | 0.060567 | 0.005985 | 0.028217 | 0.13454 | 0.073622 | 0.31137 | 0.028521 | 0.06515 | 0.023253 | -0.010564 | 0.093665 | 0.19685 | -0.12045 | -0.17788 | 122.3888 | 0.029253 | 122.4208 | 122.3884 | -0.000304 | -0.031664 | 0.20609 | 122.1823 | -0.011621 | 122.4254 | 122.3497 | 0.16732 | 0.091565 | -0.22574 | 122.4948 | 122.4339 | 122.6716 | 122.3662 | -0.076765 | 122.4539 | 122.5571 | 122.2398 | 122.3835 | -0.28317
2209.9531 | 122.5479 | -122.3511 | 0.1236 | 1.4211e-13 | -0.0090769 | 0.022393 | -0.0031241 | -0.0094525 | 0.010784 | 0.0016025 | -0.05245 | 0.026284 | 0.0074072 | 0.02822 | 0.0048713 | 0.060567 | 0.001407 | 0.028217 | 0.13454 | 0.069043 | 0.31137 | 0.023942 | 0.06515 | 0.03241 | -0.010564 | 0.093665 | 0.19685 | -0.12503 | -0.17788 | 122.375 | 0.010943 | 122.4116 | 122.3793 | 0.004275 | -0.054553 | 0.18778 | 122.1732 | -0.029931 | 122.4162 | 122.3405 | 0.16732 | 0.073255 | -0.24862 | 122.4856 | 122.4201 | 122.6624 | 122.3525 | -0.099654 | 122.4447 | 122.5479 | 122.226 | 122.3835 | -0.30148
2211.6562 | 122.6257 | -122.3145 | 0.10071 | 1.4211e-13 | -0.0092905 | 0.021966 | -0.0035515 | -0.0090251 | 0.010356 | 0.0016025 | -0.05245 | 0.026498 | 0.0076208 | 0.028433 | 0.0046577 | 0.060567 | 0.001407 | 0.028217 | 0.13454 | 0.073622 | 0.31137 | 0.023942 | 0.069728 | 0.027831 | -0.010564 | 0.084508 | 0.19227 | -0.12503 | -0.16873 | 122.3384 | 0.033831 | 122.375 | 122.3427 | 0.004275 | -0.027086 | 0.21067 | 122.1457 | -0.0162 | 122.3842 | 122.3039 | 0.15816 | 0.091564 | -0.22574 | 122.449 | 122.3881 | 122.6258 | 122.3159 | -0.076766 | 122.399 | 122.5067 | 122.1894 | 122.3423 | -0.26944
2213.4219 | 122.5891 | -122.3511 | 0.10529 | 1.4211e-13 | -0.0092905 | 0.02218 | -0.0031241 | -0.0094525 | 0.010356 | 0.0016025 | -0.05245 | 0.026498 | 0.0069798 | 0.028647 | 0.0048713 | 0.065145 | 0.010564 | 0.028217 | 0.13454 | 0.069043 | 0.31137 | 0.023942 | 0.060571 | 0.036989 | -0.001407 | 0.093665 | 0.19685 | -0.12503 | -0.17331 | 122.375 | 0.029253 | 122.4162 | 122.3793 | 0.004275 | -0.036243 | 0.20609 | 122.1778 | -0.011621 | 122.4116 | 122.3497 | 0.1719 | 0.091565 | -0.23031 | 122.4856 | 122.4201 | 122.6624 | 122.3616 | -0.081344 | 122.4447 | 122.5479 | 122.226 | 122.3881 | -0.27859
2215.1875 | 122.5204 | -122.374 | 0.11902 | 1.4211e-13 | -0.0088631 | 0.022607 | -0.0035515 | -0.0094525 | 0.010356 | 0.0016025 | -0.05245 | 0.026498 | 0.0076208 | 0.028433 | 0.0044439 | 0.060567 | 0.001407 | 0.023639 | 0.14369 | 0.069043 | 0.31137 | 0.0331 | 0.06515 | 0.027831 | -0.005985 | 0.093665 | 0.19685 | -0.12503 | -0.17331 | 122.4071 | 0.024676 | 122.4345 | 122.3976 | -0.009461 | -0.049976 | 0.19235 | 122.2007 | -0.025354 | 122.4391 | 122.368 | 0.16732 | 0.077832 | -0.24405 | 122.5177 | 122.443 | 122.6853 | 122.3754 | -0.085919 | 122.4676 | 122.5708 | 122.2489 | 122.4018 | -0.29233
2216.9531 | 122.58 | -122.374 | 0.1236 | 1.4211e-13 | -0.0092905 | 0.021966 | -0.0037651 | -0.0092389 | 0.010784 | -0.006028 | -0.052237 | 0.026284 | 0.0074072 | 0.028433 | 0.0046577 | 0.060567 | -0.007751 | 0.014482 | 0.14369 | 0.069043 | 0.29306 | 0.023942 | 0.069728 | 0.03241 | -0.005985 | 0.093665 | 0.20601 | -0.12045 | -0.16873 | 122.3979 | 0.020099 | 122.4345 | 122.3884 | -0.00946 | -0.054553 | 0.16946 | 122.2052 | -0.029931 | 122.4437 | 122.368 | 0.16274 | 0.082412 | -0.24405 | 122.5177 | 122.443 | 122.667 | 122.3662 | -0.099654 | 122.4676 | 122.58 | 122.2535 | 122.4064 | -0.29232
2218.6562 | 122.6212 | -122.3465 | 0.10986 | 1.4211e-13 | -0.0088631 | 0.022393 | -0.0033377 | -0.0094525 | 0.010356 | 0.0016025 | -0.052878 | 0.026712 | 0.0071936 | 0.028433 | 0.0046577 | 0.065145 | 0.001407 | 0.028217 | 0.13454 | 0.073622 | 0.31595 | 0.010206 | 0.06515 | 0.027831 | -0.015143 | 0.098244 | 0.19685 | -0.11587 | -0.16873 | 122.3567 | 0.024676 | 122.4116 | 122.3747 | 0.018011 | -0.036241 | 0.20609 | 122.1778 | -0.011619 | 122.4116 | 122.3314 | 0.15358 | 0.086988 | -0.22574 | 122.481 | 122.4201 | 122.6624 | 122.3479 | -0.099657 | 122.4447 | 122.5433 | 122.2306 | 122.3743 | -0.27859
2220.4219 | 122.644 | -122.3831 | 0.09613 | 1.4211e-13 | -0.0088631 | 0.021966 | -0.0031241 | -0.0090251 | 0.010356 | 0.0016025 | -0.05245 | 0.026284 | 0.0076208 | 0.02822 | 0.0044439 | 0.060567 | 0.001407 | 0.023639 | 0.13454 | 0.078201 | 0.3068 | 0.023942 | 0.06515 | 0.036989 | -0.010564 | 0.093665 | 0.19685 | -0.10671 | -0.16873 | 122.4071 | 0.038409 | 122.4437 | 122.4068 | -0.000303 | -0.017929 | 0.21067 | 122.2144 | -0.002465 | 122.4483 | 122.3726 | 0.15816 | 0.10072 | -0.20284 | 122.5177 | 122.4613 | 122.6899 | 122.3845 | -0.072188 | 122.4768 | 122.58 | 122.2764 | 122.4201 | -0.26486
2222.1719 | 122.6761 | -122.3648 | 0.09613 | 1.4211e-13 | -0.0090769 | 0.021966 | -0.0029103 | -0.0094525 | 0.010356 | 0.0016025 | -0.052664 | 0.026284 | 0.0074072 | 0.028433 | 0.0044439 | 0.060567 | 0.010564 | 0.023639 | 0.13912 | 0.073622 | 0.3068 | 0.019363 | 0.069728 | 0.036989 | -0.010564 | 0.084508 | 0.20143 | -0.12503 | -0.17788 | 122.3842 | 0.042987 | 122.4254 | 122.3884 | 0.004276 | -0.022508 | 0.21067 | 122.1869 | -0.011622 | 122.4345 | 122.3542 | 0.16732 | 0.1053 | -0.22116 | 122.5039 | 122.4384 | 122.6716 | 122.3754 | -0.076767 | 122.4493 | 122.5662 | 122.2398 | 122.4018 | -0.27402
2223.9219 | 122.5067 | -122.4152 | 0.11902 | 1.4211e-13 | -0.0092905 | 0.022393 | -0.0031241 | -0.0092389 | 0.010143 | 0.0016025 | -0.05245 | 0.026498 | 0.0074072 | 0.028433 | 0.0044439 | 0.055988 | 0.001407 | 0.01906 | 0.12996 | 0.078201 | 0.31595 | 0.019363 | 0.069728 | 0.027831 | -0.005985 | 0.093665 | 0.20143 | -0.12045 | -0.17331 | 122.4345 | 0.010941 | 122.4711 | 122.4342 | -0.000303 | -0.040818 | 0.19693 | 122.2419 | -0.025354 | 122.4849 | 122.4092 | 0.16732 | 0.08241 | -0.23947 | 122.5451 | 122.4934 | 122.7311 | 122.4166 | -0.099656 | 122.5088 | 122.6166 | 122.2947 | 122.443 | -0.29233
2225.6875 | 122.6212 | -122.3511 | 0.1236 | 1.4211e-13 | -0.0090769 | 0.02218 | -0.0031241 | -0.0094525 | 0.010143 | 0.0016025 | -0.05245 | 0.026498 | 0.0071936 | 0.02822 | 0.0044439 | 0.055988 | 0.010564 | 0.023639 | 0.13912 | 0.073622 | 0.31595 | 0.023942 | 0.069728 | 0.027831 | -0.010564 | 0.093665 | 0.20143 | -0.11587 | -0.17331 | 122.375 | 0.015521 | 122.4071 | 122.3747 | -0.000303 | -0.049974 | 0.19236 | 122.1778 | -0.029931 | 122.4208 | 122.3405 | 0.16274 | 0.077833 | -0.23947 | 122.4902 | 122.4247 | 122.667 | 122.3616 | -0.099654 | 122.4447 | 122.5525 | 122.2352 | 122.3789 | -0.2969
2227.375 | 122.5342 | -122.4243 | 0.11902 | 1.4211e-13 | -0.0088631 | 0.022393 | -0.0033377 | -0.0094525 | 0.010356 | -0.006028 | -0.05245 | 0.026284 | 0.0074072 | 0.028433 | 0.0046577 | 0.055988 | -0.003172 | 0.023639 | 0.12538 | 0.08278 | 0.31595 | 0.019363 | 0.06515 | 0.027831 | -0.005985 | 0.098244 | 0.19685 | -0.11587 | -0.18246 | 122.4437 | 0.006363 | 122.4803 | 122.448 | 0.004276 | -0.036239 | 0.19693 | 122.2419 | -0.020775 | 122.4895 | 122.4183 | 0.17648 | 0.077832 | -0.23489 | 122.5497 | 122.5071 | 122.7403 | 122.4211 | -0.099656 | 122.5226 | 122.6212 | 122.3084 | 122.4521 | -0.30148
2229.1562 | 122.5388 | -122.4197 | 0.13275 | 1.4211e-13 | -0.0088631 | 0.021966 | -0.0033377 | -0.0094525 | 0.010356 | -0.006028 | -0.052237 | 0.026284 | 0.0076208 | 0.028433 | 0.0048713 | 0.060567 | 0.001407 | 0.028217 | 0.12996 | 0.078201 | 0.3068 | 0.019363 | 0.069728 | 0.03241 | -0.010564 | 0.093665 | 0.19685 | -0.11587 | -0.18246 | 122.4391 | -0.002791 | 122.4803 | 122.448 | 0.008854 | -0.05455 | 0.17405 | 122.2373 | -0.039086 | 122.4895 | 122.4092 | 0.1719 | 0.0641 | -0.24862 | 122.5497 | 122.4979 | 122.7265 | 122.4211 | -0.11339 | 122.5134 | 122.6166 | 122.3039 | 122.4521 | -0.31522
2230.9219 | 122.58 | -122.406 | 0.11902 | 1.4211e-13 | -0.0088631 | 0.021966 | -0.0035515 | -0.0096661 | 0.010356 | -0.021289 | -0.05245 | 0.026712 | 0.0076208 | 0.028433 | 0.0046577 | 0.060567 | 0.001407 | 0.023639 | 0.13912 | 0.059885 | 0.3068 | 0.023942 | 0.06515 | 0.03241 | -0.015143 | 0.093665 | 0.19227 | -0.12045 | -0.18246 | 122.4299 | 0.020098 | 122.4666 | 122.4296 | -0.000303 | -0.059134 | 0.18778 | 122.2235 | -0.025354 | 122.4712 | 122.3909 | 0.16732 | 0.073253 | -0.23947 | 122.5451 | 122.4659 | 122.7128 | 122.4074 | -0.095077 | 122.4997 | 122.5983 | 122.2856 | 122.4384 | -0.30148
2232.625 | 122.6028 | -122.406 | 0.1236 | 1.4211e-13 | -0.0090769 | 0.021966 | -0.0031241 | -0.0090251 | 0.010356 | -0.013659 | -0.052023 | 0.026498 | 0.0074072 | 0.028647 | 0.0044439 | 0.055988 | 0.005985 | 0.032795 | 0.12996 | 0.069043 | 0.31137 | 0.028521 | 0.06515 | 0.018674 | -0.010564 | 0.089087 | 0.19685 | -0.12045 | -0.17788 | 122.4345 | 0.006364 | 122.462 | 122.4388 | 0.004274 | -0.054553 | 0.18778 | 122.2281 | -0.034509 | 122.4712 | 122.3954 | 0.16732 | 0.073255 | -0.24405 | 122.536 | 122.475 | 122.7174 | 122.412 | -0.095075 | 122.4951 | 122.6029 | 122.2856 | 122.4247 | -0.30148
2234.3906 | 122.6761 | -122.3923 | 0.09613 | 1.4211e-13 | -0.0092905 | 0.02218 | -0.0033377 | -0.0096661 | 0.0097152 | 0.0016025 | -0.052664 | 0.026498 | 0.0074072 | 0.028433 | 0.0048713 | 0.055988 | -0.003172 | 0.032795 | 0.13454 | 0.069043 | 0.30222 | 0.0331 | 0.060571 | 0.027831 | -0.015143 | 0.093665 | 0.19685 | -0.11129 | -0.18704 | 122.4254 | 0.038409 | 122.4483 | 122.4251 | -0.000305 | -0.027087 | 0.20609 | 122.2052 | -0.002465 | 122.4528 | 122.3771 | 0.1719 | 0.10072 | -0.20742 | 122.5268 | 122.4613 | 122.6945 | 122.3891 | -0.06303 | 122.4859 | 122.5891 | 122.281 | 122.4201 | -0.28317
2236.0938 | 122.58 | -122.4197 | 0.10986 | 1.4211e-13 | -0.0088631 | 0.02218 | -0.0037651 | -0.0092389 | 0.010356 | -0.013659 | -0.05245 | 0.026284 | 0.0076208 | 0.028433 | 0.0046577 | 0.05141 | 0.005985 | 0.01906 | 0.12538 | 0.073622 | 0.3068 | 0.0331 | 0.06515 | 0.036989 | -0.005985 | 0.093665 | 0.20143 | -0.11587 | -0.17788 | 122.4528 | 0.015519 | 122.4711 | 122.4388 | -0.01404 | -0.036241 | 0.19693 | 122.2419 | -0.016198 | 122.4849 | 122.4138 | 0.1719 | 0.091566 | -0.22574 | 122.5451 | 122.4934 | 122.7265 | 122.4257 | -0.076763 | 122.5134 | 122.6212 | 122.3039 | 122.4567 | -0.28775
2237.8438 | 122.6807 | -122.3694 | 0.10529 | 1.4211e-13 | -0.0090769 | 0.022393 | -0.0035515 | -0.0094525 | 0.010356 | 0.0016025 | -0.052664 | 0.026498 | 0.0074072 | 0.028647 | 0.0046577 | 0.055988 | 0.001407 | 0.01906 | 0.13912 | 0.069043 | 0.3068 | 0.019363 | 0.06515 | 0.03241 | -0.005985 | 0.093665 | 0.20143 | -0.12045 | -0.17331 | 122.3887 | 0.033831 | 122.4254 | 122.3884 | -0.000303 | -0.036243 | 0.20151 | 122.1961 | -0.011621 | 122.4345 | 122.3634 | 0.16732 | 0.096143 | -0.22574 | 122.5085 | 122.4384 | 122.6762 | 122.3708 | -0.085923 | 122.463 | 122.5708 | 122.2489 | 122.4018 | -0.27859
2239.5625 | 122.5571 | -122.4243 | 0.13275 | 1.4211e-13 | -0.0086495 | 0.021966 | -0.0033377 | -0.0092389 | 0.01057 | -0.013659 | -0.052023 | 0.026498 | 0.0074072 | 0.028647 | 0.0044439 | 0.055988 | -0.007751 | 0.023639 | 0.12996 | 0.059885 | 0.31595 | 0.019363 | 0.060571 | 0.03241 | -0.010564 | 0.093665 | 0.19685 | -0.11587 | -0.17331 | 122.4437 | -0.002791 | 122.4803 | 122.448 | 0.004276 | -0.072866 | 0.1832 | 122.251 | -0.039086 | 122.4849 | 122.4138 | 0.16274 | 0.0641 | -0.24862 | 122.5543 | 122.4842 | 122.7403 | 122.4166 | -0.11339 | 122.518 | 122.6212 | 122.3084 | 122.4567 | -0.30606
2241.3125 | 122.6303 | -122.3831 | 0.10529 | 1.4211e-13 | -0.0088631 | 0.022393 | -0.0033377 | -0.0094525 | 0.010143 | -0.006028 | -0.052664 | 0.026284 | 0.0078344 | 0.02822 | 0.0044439 | 0.055988 | -0.003172 | 0.01906 | 0.13454 | 0.073622 | 0.31595 | 0.019363 | 0.06515 | 0.023253 | -0.010564 | 0.089087 | 0.19685 | -0.11587 | -0.17788 | 122.4025 | 0.029253 | 122.4391 | 122.4022 | -0.000303 | -0.031664 | 0.21067 | 122.2052 | -0.016199 | 122.4483 | 122.3726 | 0.16732 | 0.091565 | -0.22116 | 122.5177 | 122.4567 | 122.6991 | 122.3799 | -0.085923 | 122.4722 | 122.58 | 122.2672 | 122.4064 | -0.28317
2243.0625 | 122.6761 | -122.3557 | 0.091553 | 1.4211e-13 | -0.0090769 | 0.02218 | -0.0033377 | -0.0094525 | 0.010356 | 0.0016025 | -0.052237 | 0.026498 | 0.0076208 | 0.028647 | 0.0046577 | 0.069723 | 0.005985 | 0.023639 | 0.13454 | 0.078201 | 0.31595 | 0.023942 | 0.069728 | 0.03241 | -0.010564 | 0.098244 | 0.20601 | -0.12045 | -0.18246 | 122.3796 | 0.042986 | 122.4254 | 122.3793 | -0.000303 | -0.013352 | 0.2244 | 122.1732 | 0.006691 | 122.4254 | 122.3451 | 0.1719 | 0.11446 | -0.212 | 122.4902 | 122.4339 | 122.6716 | 122.3616 | -0.067611 | 122.4539 | 122.5617 | 122.2352 | 122.3881 | -0.27402
2244.8281 | 122.6807 | -122.3969 | 0.10529 | 1.4211e-13 | -0.0090769 | 0.02218 | -0.0033377 | -0.0096661 | 0.010356 | -0.006028 | -0.052237 | 0.026284 | 0.0076208 | 0.028861 | 0.0046577 | 0.060567 | -0.003172 | 0.023639 | 0.13454 | 0.069043 | 0.31595 | 0.023942 | 0.06515 | 0.023253 | -0.005985 | 0.089087 | 0.20143 | -0.11129 | -0.17331 | 122.4208 | 0.029253 | 122.4574 | 122.4205 | -0.000303 | -0.036243 | 0.21067 | 122.2235 | -0.016199 | 122.462 | 122.3909 | 0.16732 | 0.096143 | -0.21658 | 122.5314 | 122.4659 | 122.7128 | 122.3937 | -0.081344 | 122.4859 | 122.5983 | 122.2856 | 122.4201 | -0.27859
2246.5312 | 122.5479 | -122.4289 | 0.12817 | 1.4211e-13 | -0.0092905 | 0.02218 | -0.0031241 | -0.0090251 | 0.010356 | -0.013659 | -0.05245 | 0.026284 | 0.0069798 | 0.028647 | 0.0046577 | 0.060567 | 0.001407 | 0.023639 | 0.13454 | 0.073622 | 0.3068 | 0.028521 | 0.060571 | 0.036989 | -0.005985 | 0.089087 | 0.19227 | -0.12045 | -0.17788 | 122.4574 | 0.006365 | 122.4895 | 122.4525 | -0.004882 | -0.054552 | 0.17862 | 122.251 | -0.039087 | 122.4895 | 122.4229 | 0.1719 | 0.064098 | -0.24862 | 122.5634 | 122.5025 | 122.7357 | 122.4303 | -0.099653 | 122.518 | 122.6212 | 122.3084 | 122.4659 | -0.30606
2248.2969 | 122.612 | -122.3831 | 0.11902 | 1.4211e-13 | -0.0090769 | 0.02218 | -0.0033377 | -0.0094525 | 0.01057 | -0.006028 | -0.052664 | 0.026284 | 0.0074072 | 0.028433 | 0.0046577 | 0.055988 | -0.003172 | 0.023639 | 0.14369 | 0.069043 | 0.32053 | 0.037679 | 0.055992 | 0.036989 | -0.010564 | 0.093665 | 0.19685 | -0.12045 | -0.17331 | 122.4208 | 0.024676 | 122.4391 | 122.4068 | -0.01404 | -0.049976 | 0.20151 | 122.2098 | -0.025354 | 122.4391 | 122.3726 | 0.16274 | 0.077832 | -0.23947 | 122.5268 | 122.4522 | 122.7036 | 122.3799 | -0.08134 | 122.4768 | 122.58 | 122.2627 | 122.4201 | -0.29233
2250 | 122.5616 | -122.438 | 0.13733 | 1.4211e-13 | -0.0088631 | 0.021966 | -0.0035515 | -0.0094525 | 0.010143 | -0.006028 | -0.052237 | 0.026071 | 0.0076208 | 0.028647 | 0.0044439 | 0.060567 | 0.005985 | 0.023639 | 0.13454 | 0.069043 | 0.3068 | 0.028521 | 0.06515 | 0.03241 | -0.010564 | 0.089087 | 0.20143 | -0.11587 | -0.17788 | 122.4666 | -0.00279 | 122.4986 | 122.4617 | -0.004882 | -0.068286 | 0.16947 | 122.2602 | -0.048242 | 122.5032 | 122.4275 | 0.16732 | 0.0641 | -0.2532 | 122.5726 | 122.5071 | 122.7448 | 122.444 | -0.10881 | 122.5271 | 122.6395 | 122.3222 | 122.4705 | -0.31521
2251.7656 | 122.699 | -122.4014 | 0.10071 | 1.4211e-13 | -0.0090769 | 0.022607 | -0.0033377 | -0.0094525 | 0.01057 | -0.006028 | -0.05245 | 0.026284 | 0.0074072 | 0.028861 | 0.0044439 | 0.060567 | 0.001407 | 0.01906 | 0.12996 | 0.069043 | 0.31137 | 0.028521 | 0.060571 | 0.023253 | -0.005985 | 0.093665 | 0.19685 | -0.12045 | -0.16415 | 122.4299 | 0.029252 | 122.462 | 122.4205 | -0.009461 | -0.031665 | 0.21067 | 122.2373 | -0.007043 | 122.462 | 122.3954 | 0.15816 | 0.096143 | -0.22116 | 122.5314 | 122.4705 | 122.7128 | 122.4028 | -0.072187 | 122.4951 | 122.5983 | 122.281 | 122.4247 | -0.26486
2253.5312 | 122.6852 | -122.406 | 0.091553 | 1.4211e-13 | -0.0090769 | 0.022393 | -0.0033377 | -0.0092389 | 0.010143 | 0.0016025 | -0.05245 | 0.026071 | 0.0074072 | 0.028647 | 0.0042303 | 0.060567 | 0.010564 | 0.028217 | 0.12996 | 0.08278 | 0.31137 | 0.023942 | 0.06515 | 0.036989 | -0.015143 | 0.084508 | 0.18769 | -0.12045 | -0.17331 | 122.4299 | 0.038407 | 122.4666 | 122.4342 | 0.004275 | -0.008773 | 0.21982 | 122.2327 | -0.007045 | 122.4712 | 122.3909 | 0.15816 | 0.09614 | -0.212 | 122.536 | 122.4888 | 122.7174 | 122.4166 | -0.067611 | 122.4905 | 122.5937 | 122.2856 | 122.443 | -0.26486
2255.2812 | 122.5845 | -122.287 | 0.07782 | 1.4211e-13 | -0.0090769 | 0.021966 | -0.0033377 | -0.0096661 | 0.010143 | 0.0016025 | 0.0086503 | 0.020729 | 0.075347 | 0.028433 | 0.0046577 | 0.065145 | 0.001407 | 0.028217 | 0.13454 | 0.087359 | 0.31595 | -0.017268 | 0.060571 | 0.027831 | -0.010564 | 0.093665 | 0.19685 | 0.17716 | -0.17331 | 122.2697 | 0.056719 | 122.3521 | 122.3152 | 0.045485 | 0.009539 | 0.23813 | 122.1137 | 0.015845 | 122.3476 | 122.2764 | 0.16274 | 0.11903 | 0.099339 | 122.4215 | 122.3743 | 122.6029 | 122.2884 | -0.095088 | 122.3807 | 122.4838 | 122.4641 | 122.3148 | -0.25113
2257.0312 | 122.4335 | -122.0901 | 0.091553 | 1.4211e-13 | -0.0090769 | 0.02218 | -0.0035515 | -0.0096661 | 0.010356 | -0.006028 | 0.0084367 | 0.020302 | 0.075134 | 0.028647 | 0.0044439 | 0.065145 | 0.015142 | 0.023639 | 0.12538 | 0.069043 | 0.32053 | 0.023942 | 0.06515 | 0.027831 | -0.010564 | 0.089087 | 0.19227 | 0.18174 | -0.17788 | 122.1141 | 0.033829 | 122.1553 | 122.1138 | -0.000303 | -0.02251 | 0.22898 | 121.9123 | -0.002466 | 122.1553 | 122.0796 | 0.16732 | 0.10072 | 0.090185 | 122.2155 | 122.1592 | 122.4107 | 122.1053 | -0.067611 | 122.1792 | 122.2824 | 122.2719 | 122.118 | -0.26944
2258.7188 | 122.3694 | -122.2229 | 0.12817 | 1.4211e-13 | -0.0092905 | 0.021966 | -0.0033377 | -0.0092389 | 0.01057 | 0.0016025 | 0.0082229 | 0.020516 | 0.074706 | 0.028433 | 0.0048713 | 0.065145 | 0.010564 | 0.023639 | 0.13454 | 0.078201 | 0.31137 | 0.028521 | 0.06515 | 0.023253 | -0.010564 | 0.084508 | 0.19227 | -0.12045 | -0.18246 | 122.2514 | 0.006365 | 122.288 | 122.2465 | -0.004882 | -0.049973 | 0.1832 | 122.0404 | -0.043666 | 122.288 | 122.2123 | 0.1719 | 0.064098 | -0.24862 | 122.3574 | 122.3011 | 122.5343 | 122.2335 | -0.099653 | 122.3074 | 122.4152 | 122.1024 | 122.2462 | -0.31064
2260.4688 | 122.4976 | -122.2 | 0.082397 | 1.4211e-13 | -0.0088631 | 0.02218 | -0.0033377 | -0.0094525 | 0.01057 | -0.006028 | 0.0084367 | 0.020302 | 0.074706 | 0.02822 | 0.0044439 | 0.060567 | 0.005985 | 0.028217 | 0.13912 | 0.073622 | 0.31595 | 0.023942 | 0.06515 | 0.03241 | -0.015143 | 0.089087 | 0.19685 | -0.12045 | -0.17788 | 122.224 | 0.05672 | 122.2606 | 122.2282 | 0.004275 | -0.008775 | 0.23356 | 122.0221 | 0.00669 | 122.2652 | 122.1849 | 0.16274 | 0.11445 | -0.20285 | 122.3391 | 122.2736 | 122.516 | 122.206 | -0.058455 | 122.2891 | 122.3969 | 122.0796 | 122.2324 | -0.26028
2262.2188 | 122.5388 | -122.2137 | 0.091553 | 1.4211e-13 | -0.0092905 | 0.021966 | -0.0033377 | -0.0094525 | 0.010143 | -0.006028 | 0.0088639 | 0.020302 | 0.074493 | 0.028647 | 0.0046577 | 0.055988 | 0.005985 | 0.028217 | 0.12996 | 0.069043 | 0.31137 | 0.028521 | 0.06515 | 0.023253 | -0.001407 | 0.089087 | 0.19685 | -0.11587 | -0.17788 | 122.2423 | 0.038407 | 122.2697 | 122.242 | -0.000304 | -0.02251 | 0.21982 | 122.0359 | -0.002466 | 122.2789 | 122.2123 | 0.17648 | 0.1053 | -0.20742 | 122.3437 | 122.2828 | 122.5251 | 122.2197 | -0.063032 | 122.3028 | 122.4106 | 122.0979 | 122.237 | -0.26944
2263.9844 | 122.5113 | -122.2641 | 0.09613 | 1.4211e-13 | -0.0090769 | 0.021966 | -0.0033377 | -0.0092389 | 0.010356 | -0.006028 | 0.0086503 | 0.020729 | 0.074493 | 0.028433 | 0.0044439 | 0.065145 | 0.010564 | 0.032795 | 0.14369 | 0.078201 | 0.31137 | 0.023942 | 0.06515 | 0.027831 | -0.010564 | 0.084508 | 0.20143 | -0.11129 | -0.17788 | 122.288 | 0.047565 | 122.3292 | 122.2969 | 0.008853 | -0.017929 | 0.21524 | 122.0862 | -0.011622 | 122.3292 | 122.2535 | 0.16732 | 0.1053 | -0.20742 | 122.4078 | 122.3423 | 122.5755 | 122.2747 | -0.072188 | 122.3486 | 122.4655 | 122.1528 | 122.2919 | -0.27402
2265.6719 | 122.5113 | -122.2549 | 0.10986 | 1.4211e-13 | -0.0086495 | 0.02218 | -0.0031241 | -0.0092389 | 0.010356 | -0.013659 | 0.0084367 | 0.020302 | 0.074493 | 0.028861 | 0.0046577 | 0.065145 | 0.005985 | 0.028217 | 0.13454 | 0.059885 | 0.32053 | 0.019363 | 0.069728 | 0.027831 | -0.010564 | 0.084508 | 0.19227 | -0.12045 | -0.18246 | 122.2743 | 0.024676 | 122.3201 | 122.2832 | 0.008854 | -0.049978 | 0.21067 | 122.0725 | -0.025355 | 122.3247 | 122.2444 | 0.1719 | 0.082409 | -0.23031 | 122.3895 | 122.3148 | 122.5755 | 122.2609 | -0.0905 | 122.3395 | 122.4472 | 122.1345 | 122.2828 | -0.29233
2267.4219 | 122.5479 | -122.3007 | 0.10986 | 1.4211e-13 | -0.0095041 | 0.021966 | -0.0035515 | -0.0094525 | 0.01057 | 0.0016025 | 0.0088639 | 0.020302 | 0.074706 | 0.028647 | 0.0044439 | 0.060567 | 0.005985 | 0.028217 | 0.14369 | 0.078201 | 0.31595 | 0.019363 | 0.060571 | 0.027831 | -0.005985 | 0.089087 | 0.19227 | -0.12045 | -0.16873 | 122.3201 | 0.033832 | 122.3613 | 122.3289 | 0.008854 | -0.031662 | 0.20609 | 122.132 | -0.020776 | 122.3613 | 122.2947 | 0.16274 | 0.082409 | -0.23031 | 122.4444 | 122.3789 | 122.6167 | 122.3067 | -0.0905 | 122.3898 | 122.493 | 122.1803 | 122.3286 | -0.27859
2269.1875 | 122.5983 | -122.2641 | 0.10071 | 1.4211e-13 | -0.0090769 | 0.02218 | -0.0033377 | -0.0094525 | 0.010784 | -0.006028 | 0.0084367 | 0.020516 | 0.075775 | 0.028433 | 0.0044439 | 0.055988 | 0.001407 | 0.023639 | 0.14369 | 0.078201 | 0.31595 | 0.037679 | 0.069728 | 0.027831 | -0.001407 | 0.098244 | 0.19685 | -0.11587 | -0.18246 | 122.3018 | 0.042987 | 122.3201 | 122.2877 | -0.01404 | -0.022507 | 0.21524 | 122.0816 | -0.002464 | 122.3338 | 122.2627 | 0.18106 | 0.096143 | -0.21658 | 122.4078 | 122.3423 | 122.5801 | 122.2655 | -0.063029 | 122.3623 | 122.4609 | 122.1482 | 122.2919 | -0.28317
2270.9375 | 122.5388 | -122.3328 | 0.11444 | 1.4211e-13 | -0.0092905 | 0.022607 | -0.0031241 | -0.0094525 | 0.01057 | 0.0016025 | 0.0086503 | 0.020516 | 0.075347 | 0.028433 | 0.0046577 | 0.065145 | 0.001407 | 0.01906 | 0.13912 | 0.073622 | 0.31137 | 0.0331 | 0.060571 | 0.027831 | -0.015143 | 0.089087 | 0.19227 | -0.11129 | -0.17788 | 122.3659 | 0.024676 | 122.3979 | 122.3518 | -0.01404 | -0.040819 | 0.19693 | 122.1549 | -0.025354 | 122.3933 | 122.3176 | 0.16274 | 0.077831 | -0.22573 | 122.4719 | 122.4064 | 122.6441 | 122.3342 | -0.081341 | 122.4219 | 122.525 | 122.2215 | 122.3606 | -0.29233
2272.625 | 122.5021 | -122.3145 | 0.11444 | 1.4211e-13 | -0.0090769 | 0.02218 | -0.0035515 | -0.0094525 | 0.01057 | 0.0016025 | 0.0090775 | 0.020088 | 0.075561 | 0.028861 | 0.0046577 | 0.065145 | 0.015142 | 0.028217 | 0.13912 | 0.078201 | 0.31137 | 0.028521 | 0.060571 | 0.018674 | -0.010564 | 0.089087 | 0.20143 | -0.11587 | -0.17788 | 122.343 | 0.024676 | 122.3796 | 122.3427 | -0.000304 | -0.03624 | 0.19693 | 122.1366 | -0.025354 | 122.375 | 122.3039 | 0.16732 | 0.086988 | -0.23031 | 122.4536 | 122.3927 | 122.6258 | 122.3296 | -0.08592 | 122.4035 | 122.5159 | 122.1986 | 122.3331 | -0.29233
2274.375 | 122.5296 | -122.3145 | 0.12817 | 1.4211e-13 | -0.0088631 | 0.021966 | -0.0031241 | -0.0094525 | 0.010784 | -0.006028 | 0.0090775 | 0.020088 | 0.075561 | 0.028433 | 0.0042303 | 0.065145 | 0.015142 | 0.023639 | 0.12996 | 0.073622 | 0.31137 | 0.023942 | 0.06515 | 0.018674 | -0.010564 | 0.084508 | 0.20143 | -0.10671 | -0.17331 | 122.3384 | 0.001786 | 122.3796 | 122.3381 | -0.000303 | -0.054552 | 0.1832 | 122.1411 | -0.043666 | 122.3796 | 122.3039 | 0.16274 | 0.073255 | -0.23489 | 122.4444 | 122.3881 | 122.6258 | 122.3296 | -0.10423 | 122.399 | 122.5159 | 122.2077 | 122.3331 | -0.30148
2276.1406 | 122.6166 | -122.3007 | 0.09613 | 1.4211e-13 | -0.0088631 | 0.02218 | -0.0037651 | -0.0096661 | 0.01057 | 0.0016025 | 0.0088639 | 0.020729 | 0.075775 | 0.029075 | 0.0044439 | 0.069723 | 0.010564 | 0.032795 | 0.13912 | 0.073622 | 0.31137 | 0.019363 | 0.06515 | 0.027831 | -0.019721 | 0.089087 | 0.20143 | -0.12045 | -0.18704 | 122.3201 | 0.042987 | 122.3704 | 122.3335 | 0.013432 | -0.022508 | 0.21524 | 122.1137 | -0.007043 | 122.3659 | 122.281 | 0.16732 | 0.1053 | -0.21658 | 122.4398 | 122.3743 | 122.6121 | 122.3113 | -0.076767 | 122.3898 | 122.5021 | 122.1803 | 122.3286 | -0.28317
2277.9062 | 122.493 | -122.3557 | 0.11444 | 1.4211e-13 | -0.0090769 | 0.022393 | -0.0035515 | -0.0096661 | 0.010784 | -0.021289 | 0.0088639 | 0.020302 | 0.075561 | 0.028433 | 0.0046577 | 0.065145 | 0.005985 | 0.023639 | 0.13912 | 0.073622 | 0.31137 | 0.028521 | 0.055992 | 0.018674 | -0.015143 | 0.089087 | 0.19227 | -0.11587 | -0.17788 | 122.3842 | 0.024676 | 122.4208 | 122.3793 | -0.004882 | -0.040819 | 0.19693 | 122.1778 | -0.025354 | 122.4116 | 122.3405 | 0.16274 | 0.077831 | -0.23031 | 122.4948 | 122.4293 | 122.667 | 122.3616 | -0.08592 | 122.4447 | 122.5479 | 122.2398 | 122.3743 | -0.29233
2279.625 | 122.5021 | -122.3511 | 0.14191 | 1.4211e-13 | -0.0088631 | 0.022393 | -0.0029103 | -0.0092389 | 0.01057 | 0.0016025 | 0.0088639 | 0.020516 | 0.075775 | 0.028433 | 0.0044439 | 0.055988 | 0.001407 | 0.023639 | 0.13454 | 0.078201 | 0.31137 | 0.023942 | 0.055992 | 0.027831 | -0.010564 | 0.084508 | 0.19685 | -0.12045 | -0.17788 | 122.375 | -0.007368 | 122.4071 | 122.3747 | -0.000303 | -0.063706 | 0.16947 | 122.1732 | -0.057399 | 122.4071 | 122.3405 | 0.16732 | 0.054944 | -0.26236 | 122.4856 | 122.4293 | 122.6624 | 122.3525 | -0.11797 | 122.4356 | 122.5479 | 122.2306 | 122.3789 | -0.31979
2281.3906 | 122.5479 | -122.3511 | 0.10529 | 1.4211e-13 | -0.0088631 | 0.02218 | -0.0033377 | -0.0094525 | 0.010997 | 0.0092325 | 0.0088639 | 0.020302 | 0.075988 | 0.028433 | 0.0042303 | 0.060567 | 0.015142 | 0.028217 | 0.13912 | 0.078201 | 0.32053 | 0.023942 | 0.06515 | 0.023253 | -0.010564 | 0.084508 | 0.20143 | -0.11587 | -0.17331 | 122.375 | 0.033831 | 122.4116 | 122.3793 | 0.004275 | -0.027085 | 0.21525 | 122.1778 | -0.020778 | 122.4162 | 122.3405 | 0.16274 | 0.096143 | -0.22116 | 122.4902 | 122.4293 | 122.6716 | 122.3662 | -0.081344 | 122.4356 | 122.5525 | 122.2352 | 122.3743 | -0.27859
2283.0938 | 122.4747 | -122.3602 | 0.14648 | 1.4211e-13 | -0.0090769 | 0.02218 | -0.0031241 | -0.0094525 | 0.010784 | -0.006028 | 0.0088639 | 0.020729 | 0.075988 | 0.028433 | 0.0044439 | 0.060567 | 0.010564 | 0.023639 | 0.13454 | 0.078201 | 0.31137 | 0.019363 | 0.060571 | 0.023253 | -0.0243 | 0.089087 | 0.19685 | -0.11587 | -0.17788 | 122.3796 | -0.011945 | 122.4208 | 122.3839 | 0.004276 | -0.068283 | 0.16489 | 122.1823 | -0.057397 | 122.4208 | 122.3359 | 0.15358 | 0.050367 | -0.26236 | 122.4948 | 122.4384 | 122.6716 | 122.3708 | -0.12712 | 122.4493 | 122.5571 | 122.2444 | 122.3835 | -0.32437
2284.8594 | 122.644 | -122.3236 | 0.07782 | 1.4211e-13 | -0.0086495 | 0.022393 | -0.0035515 | -0.0096661 | 0.01057 | 0.0016025 | 0.0088639 | 0.019661 | 0.075988 | 0.028647 | 0.0048713 | 0.069723 | 0.005985 | 0.028217 | 0.13454 | 0.078201 | 0.31595 | 0.028521 | 0.06515 | 0.023253 | -0.010564 | 0.089087 | 0.19227 | -0.12045 | -0.17788 | 122.3521 | 0.056719 | 122.3933 | 122.3518 | -0.000304 | 0.000381 | 0.23813 | 122.1457 | 0.011267 | 122.3888 | 122.313 | 0.16732 | 0.11445 | -0.19827 | 122.4581 | 122.4018 | 122.6396 | 122.3296 | -0.049299 | 122.4127 | 122.5159 | 122.2032 | 122.3469 | -0.2557
2286.5625 | 122.6624 | -122.3373 | 0.09613 | 1.4211e-13 | -0.0090769 | 0.022393 | -0.0033377 | -0.0092389 | 0.01057 | -0.013659 | 0.0086503 | 0.019447 | 0.075775 | 0.028861 | 0.0048713 | 0.065145 | 0.010564 | 0.028217 | 0.12996 | 0.08278 | 0.32053 | 0.023942 | 0.06515 | 0.027831 | -0.005985 | 0.089087 | 0.19685 | -0.12961 | -0.17331 | 122.3613 | 0.03383 | 122.4025 | 122.3656 | 0.004275 | -0.01335 | 0.2244 | 122.164 | -0.007043 | 122.4025 | 122.3314 | 0.16732 | 0.10072 | -0.22574 | 122.4673 | 122.4201 | 122.6579 | 122.3479 | -0.072188 | 122.4264 | 122.5342 | 122.2077 | 122.3652 | -0.26944
2288.2656 | 122.6486 | -122.3465 | 0.10986 | 1.4211e-13 | -0.0088631 | 0.021966 | -0.0035515 | -0.0090251 | 0.01057 | 0.0016025 | 0.0088639 | 0.019234 | 0.075561 | 0.028433 | 0.0046577 | 0.060567 | 0.010564 | 0.028217 | 0.14369 | 0.078201 | 0.31137 | 0.019363 | 0.060571 | 0.027831 | -0.005985 | 0.084508 | 0.19227 | -0.11587 | -0.17331 | 122.3659 | 0.033832 | 122.4071 | 122.3747 | 0.008854 | -0.031662 | 0.20151 | 122.1732 | -0.025355 | 122.4071 | 122.3405 | 0.16732 | 0.082409 | -0.22574 | 122.4902 | 122.4247 | 122.6579 | 122.3571 | -0.0905 | 122.431 | 122.5388 | 122.2306 | 122.3743 | -0.28317
2290.0312 | 122.6349 | -122.3602 | 0.086975 | 1.4211e-13 | -0.0088631 | 0.021752 | -0.0033377 | -0.0092389 | 0.010356 | -0.013659 | 0.0088639 | 0.019447 | 0.075775 | 0.028647 | 0.0044439 | 0.055988 | 0.010564 | 0.028217 | 0.13912 | 0.073622 | 0.32053 | 0.023942 | 0.069728 | 0.023253 | -0.005985 | 0.089087 | 0.19227 | -0.11129 | -0.17788 | 122.3842 | 0.052142 | 122.4162 | 122.3884 | 0.004275 | -0.013353 | 0.23356 | 122.1823 | 0.002112 | 122.43 | 122.3542 | 0.1719 | 0.1053 | -0.19827 | 122.4993 | 122.4339 | 122.6808 | 122.3708 | -0.063033 | 122.4493 | 122.5525 | 122.2489 | 122.3835 | -0.26486
2291.7969 | 122.6578 | -122.3282 | 0.10529 | 1.4211e-13 | -0.0088631 | 0.022393 | -0.0031241 | -0.0092389 | 0.010356 | 0.0016025 | 0.0082229 | 0.019234 | 0.075561 | 0.028433 | 0.0044439 | 0.065145 | 0.015142 | 0.028217 | 0.12996 | 0.073622 | 0.31595 | 0.023942 | 0.06515 | 0.027831 | -0.005985 | 0.07993 | 0.18311 | -0.12503 | -0.17788 | 122.3521 | 0.024674 | 122.3933 | 122.3564 | 0.004275 | -0.031664 | 0.21067 | 122.1503 | -0.025356 | 122.3933 | 122.3222 | 0.1719 | 0.077829 | -0.23031 | 122.4581 | 122.4018 | 122.6441 | 122.3433 | -0.081344 | 122.4081 | 122.5113 | 122.2032 | 122.356 | -0.28317
2293.5469 | 122.5433 | -122.3877 | 0.13275 | 1.4211e-13 | -0.0090769 | 0.021966 | -0.0035515 | -0.0092389 | 0.010356 | -0.006028 | 0.0086503 | 0.019447 | 0.075347 | 0.028433 | 0.0044439 | 0.065145 | 0.010564 | 0.028217 | 0.12996 | 0.073622 | 0.31595 | 0.019363 | 0.060571 | 0.027831 | -0.005985 | 0.084508 | 0.19685 | -0.12045 | -0.17331 | 122.4071 | -0.002791 | 122.4528 | 122.4159 | 0.008854 | -0.059129 | 0.1832 | 122.2144 | -0.048243 | 122.4483 | 122.3817 | 0.16732 | 0.0641 | -0.2532 | 122.5177 | 122.4613 | 122.7036 | 122.3983 | -0.11339 | 122.4722 | 122.5845 | 122.2672 | 122.4155 | -0.30606
2295.25 | 122.6349 | -122.3648 | 0.10071 | 1.4211e-13 | -0.0088631 | 0.02218 | -0.0033377 | -0.0092389 | 0.01057 | -0.006028 | 0.0088639 | 0.019447 | 0.075775 | 0.028433 | 0.0048713 | 0.065145 | 0.005985 | 0.032795 | 0.13454 | 0.078201 | 0.3068 | 0.028521 | 0.060571 | 0.027831 | -0.010564 | 0.093665 | 0.20143 | -0.12503 | -0.16873 | 122.3933 | 0.033831 | 122.43 | 122.3976 | 0.004274 | -0.022507 | 0.20609 | 122.1961 | -0.007043 | 122.4254 | 122.3542 | 0.15816 | 0.10072 | -0.22574 | 122.4993 | 122.443 | 122.6716 | 122.3708 | -0.072187 | 122.4585 | 122.5662 | 122.2398 | 122.3926 | -0.26944
2297.0156 | 122.5525 | -122.3923 | 0.14191 | 1.4211e-13 | -0.0092905 | 0.021966 | -0.0033377 | -0.0092389 | 0.01057 | -0.006028 | 0.0088639 | 0.019234 | 0.075775 | 0.028647 | 0.0044439 | 0.065145 | 0.010564 | 0.023639 | 0.13454 | 0.073622 | 0.30222 | 0.0331 | 0.06515 | 0.018674 | -0.001407 | 0.093665 | 0.19685 | -0.11129 | -0.17331 | 122.4254 | -0.007368 | 122.4574 | 122.4159 | -0.009461 | -0.068285 | 0.16031 | 122.219 | -0.048242 | 122.4574 | 122.3909 | 0.1719 | 0.054944 | -0.2532 | 122.5268 | 122.4659 | 122.6945 | 122.4028 | -0.10881 | 122.4859 | 122.5891 | 122.281 | 122.4109 | -0.31521
2298.7188 | 122.5616 | -122.3923 | 0.13733 | 1.4211e-13 | -0.0095041 | 0.02218 | -0.0029103 | -0.0092389 | 0.010784 | -0.013659 | 0.0086503 | 0.019661 | 0.075988 | 0.028647 | 0.0046577 | 0.065145 | 0.005985 | 0.023639 | 0.13454 | 0.073622 | 0.31137 | 0.019363 | 0.06515 | 0.027831 | -0.019721 | 0.07993 | 0.18769 | -0.11587 | -0.17331 | 122.4116 | -0.00279 | 122.4574 | 122.4159 | 0.004276 | -0.063707 | 0.17404 | 122.219 | -0.057399 | 122.4574 | 122.3726 | 0.15358 | 0.050364 | -0.2532 | 122.5268 | 122.4659 | 122.7036 | 122.3983 | -0.11797 | 122.4722 | 122.58 | 122.2764 | 122.4201 | -0.31063
2300.4844 | 122.5937 | -122.3831 | 0.12817 | 1.4211e-13 | -0.0088631 | 0.02218 | -0.0035515 | -0.0094525 | 0.01057 | 0.0016025 | 0.0084367 | 0.019661 | 0.075561 | 0.029075 | 0.0048713 | 0.069723 | 0.010564 | 0.023639 | 0.12996 | 0.078201 | 0.31137 | 0.028521 | 0.06515 | 0.018674 | -0.010564 | 0.093665 | 0.18769 | -0.11587 | -0.17331 | 122.4116 | 0.001786 | 122.4528 | 122.4068 | -0.004882 | -0.049973 | 0.1832 | 122.2098 | -0.034509 | 122.4483 | 122.3726 | 0.16274 | 0.059519 | -0.24405 | 122.5131 | 122.4613 | 122.6945 | 122.3937 | -0.099653 | 122.4768 | 122.5708 | 122.2672 | 122.4018 | -0.30148
2302.2031 | 122.6349 | -122.3831 | 0.11902 | 1.4211e-13 | -0.0088631 | 0.02218 | -0.0031241 | -0.0094525 | 0.01057 | 0.0016025 | 0.0090775 | 0.019447 | 0.075561 | 0.028647 | 0.0044439 | 0.060567 | 0.005985 | 0.028217 | 0.13454 | 0.078201 | 0.31137 | 0.014784 | 0.06515 | 0.023253 | -0.005985 | 0.084508 | 0.19685 | -0.11129 | -0.18246 | 122.3979 | 0.01552 | 122.4437 | 122.4113 | 0.013433 | -0.040818 | 0.19235 | 122.2007 | -0.034511 | 122.4483 | 122.3771 | 0.17648 | 0.077832 | -0.23031 | 122.5177 | 122.4613 | 122.6945 | 122.3891 | -0.10423 | 122.4676 | 122.58 | 122.2718 | 122.4064 | -0.30148
2303.9688 | 122.5525 | -122.4243 | 0.11902 | 1.4211e-13 | -0.0088631 | 0.02218 | -0.0031241 | -0.0094525 | 0.010784 | -0.006028 | 0.0090775 | 0.019661 | 0.075561 | 0.028861 | 0.0044439 | 0.060567 | 0.015142 | 0.032795 | 0.14369 | 0.069043 | 0.31137 | 0.014784 | 0.060571 | 0.03241 | -0.001407 | 0.089087 | 0.19227 | -0.11129 | -0.16873 | 122.4391 | 0.024676 | 122.4849 | 122.4571 | 0.018011 | -0.049976 | 0.19235 | 122.2556 | -0.029932 | 122.4849 | 122.4229 | 0.16732 | 0.073253 | -0.23031 | 122.568 | 122.4934 | 122.7357 | 122.4395 | -0.10423 | 122.5134 | 122.6166 | 122.313 | 122.4567 | -0.28775
2305.7344 | 122.6028 | -122.4106 | 0.10986 | 1.4211e-13 | -0.0090769 | 0.02218 | -0.0029103 | -0.0094525 | 0.01057 | -0.006028 | 0.0088639 | 0.019234 | 0.075775 | 0.028647 | 0.0044439 | 0.065145 | 0.005985 | 0.028217 | 0.12996 | 0.073622 | 0.31137 | 0.028521 | 0.055992 | 0.03241 | -0.005985 | 0.084508 | 0.20143 | -0.11587 | -0.18246 | 122.4391 | 0.020097 | 122.4757 | 122.4388 | -0.000304 | -0.036241 | 0.20151 | 122.2281 | -0.025355 | 122.4666 | 122.4046 | 0.17648 | 0.091566 | -0.22574 | 122.5405 | 122.4842 | 122.722 | 122.4166 | -0.081342 | 122.4951 | 122.612 | 122.2947 | 122.443 | -0.29233
2307.4844 | 122.6624 | -122.4152 | 0.10529 | 1.4211e-13 | -0.0090769 | 0.02218 | -0.0033377 | -0.0096661 | 0.010143 | -0.006028 | 0.0090775 | 0.019234 | 0.075775 | 0.028433 | 0.0044439 | 0.065145 | 0.010564 | 0.028217 | 0.13454 | 0.073622 | 0.31595 | 0.023942 | 0.06515 | 0.023253 | -0.005985 | 0.084508 | 0.19227 | -0.12045 | -0.17331 | 122.4391 | 0.029253 | 122.4803 | 122.4434 | 0.004275 | -0.031664 | 0.21067 | 122.2419 | -0.020778 | 122.4803 | 122.4092 | 0.16732 | 0.086986 | -0.22574 | 122.5497 | 122.4888 | 122.7311 | 122.4257 | -0.081344 | 122.4997 | 122.6074 | 122.2947 | 122.4384 | -0.27859
2309.2656 | 122.6395 | -122.3831 | 0.10986 | 1.4211e-13 | -0.0090769 | 0.02218 | -0.0035515 | -0.0096661 | 0.010356 | 0.0016025 | 0.0086503 | 0.019234 | 0.075775 | 0.028861 | 0.0044439 | 0.065145 | 0.015142 | 0.028217 | 0.13912 | 0.08278 | 0.32053 | 0.028521 | 0.069728 | 0.023253 | -0.001407 | 0.089087 | 0.19685 | -0.11587 | -0.17331 | 122.4116 | 0.029254 | 122.4483 | 122.4113 | -0.000304 | -0.027083 | 0.21067 | 122.2098 | -0.020776 | 122.4528 | 122.3817 | 0.1719 | 0.086988 | -0.22574 | 122.5222 | 122.4659 | 122.7036 | 122.3983 | -0.081342 | 122.4722 | 122.58 | 122.2672 | 122.4064 | -0.28317
2310.9688 | 122.6624 | -122.4014 | 0.10071 | 1.4211e-13 | -0.0090769 | 0.021966 | -0.0035515 | -0.0094525 | 0.010997 | -0.013659 | 0.0086503 | 0.019661 | 0.075561 | 0.02822 | 0.0046577 | 0.065145 | 0.010564 | 0.028217 | 0.13912 | 0.08278 | 0.32053 | 0.019363 | 0.069728 | 0.027831 | -0.005985 | 0.089087 | 0.19227 | -0.11587 | -0.16873 | 122.4208 | 0.038409 | 122.4666 | 122.4296 | 0.008854 | -0.017928 | 0.21982 | 122.2327 | -0.011621 | 122.4712 | 122.3954 | 0.16274 | 0.091564 | -0.21658 | 122.5405 | 122.4842 | 122.722 | 122.412 | -0.081345 | 122.4905 | 122.5937 | 122.2856 | 122.4293 | -0.26944
2312.7344 | 122.6486 | -122.4152 | 0.10986 | 1.4211e-13 | -0.0090769 | 0.021752 | -0.0035515 | -0.0096661 | 0.010997 | -0.006028 | 0.0090775 | 0.019447 | 0.075561 | 0.028433 | 0.0046577 | 0.065145 | 0.015142 | 0.023639 | 0.13454 | 0.08278 | 0.31137 | 0.019363 | 0.06515 | 0.03241 | -0.015143 | 0.084508 | 0.19685 | -0.11587 | -0.17788 | 122.4345 | 0.024676 | 122.4803 | 122.4388 | 0.004276 | -0.027083 | 0.20151 | 122.2373 | -0.025355 | 122.4803 | 122.4 | 0.16274 | 0.086988 | -0.22574 | 122.5497 | 122.4979 | 122.7265 | 122.4303 | -0.0905 | 122.4997 | 122.612 | 122.2993 | 122.4476 | -0.28775
2314.4375 | 122.6212 | -122.4197 | 0.10986 | 1.4211e-13 | -0.0088631 | 0.021752 | -0.0033377 | -0.0090251 | 0.010356 | -0.013659 | 0.0086503 | 0.019661 | 0.075561 | 0.028861 | 0.0046577 | 0.065145 | 0.010564 | 0.028217 | 0.13454 | 0.073622 | 0.31595 | 0.023942 | 0.060571 | 0.027831 | -0.001407 | 0.084508 | 0.19685 | -0.11587 | -0.17788 | 122.4437 | 0.024676 | 122.4849 | 122.448 | 0.004275 | -0.036241 | 0.20609 | 122.2419 | -0.025355 | 122.4803 | 122.4183 | 0.17648 | 0.086988 | -0.22574 | 122.5543 | 122.4934 | 122.7357 | 122.4303 | -0.085921 | 122.5042 | 122.6166 | 122.3039 | 122.4476 | -0.28775
2316.2031 | 122.6898 | -122.3877 | 0.073242 | 1.4211e-13 | -0.0088631 | 0.021966 | -0.0033377 | -0.0094525 | 0.01057 | 0.0016025 | 0.0086503 | 0.019661 | 0.075561 | 0.028861 | 0.0046577 | 0.065145 | 0.019721 | 0.028217 | 0.14369 | 0.073622 | 0.31595 | 0.023942 | 0.060571 | 0.027831 | -0.005985 | 0.093665 | 0.19227 | -0.11587 | -0.17788 | 122.4116 | 0.070453 | 122.4528 | 122.4159 | 0.004275 | 0.00038 | 0.24271 | 122.2098 | 0.020423 | 122.4483 | 122.3817 | 0.1719 | 0.11903 | -0.18911 | 122.5314 | 122.4613 | 122.7036 | 122.4074 | -0.0493 | 122.4814 | 122.58 | 122.2718 | 122.4155 | -0.25113
2317.8906 | 122.7127 | -122.3785 | 0.091553 | 1.4211e-13 | -0.0088631 | 0.021966 | -0.0035515 | -0.0094525 | 0.010784 | -0.021289 | 0.0088639 | 0.019661 | 0.075988 | 0.028861 | 0.0046577 | 0.065145 | 0.010564 | 0.028217 | 0.13454 | 0.078201 | 0.3068 | 0.023942 | 0.06515 | 0.023253 | -0.010564 | 0.089087 | 0.18769 | -0.11587 | -0.17788 | 122.4025 | 0.042986 | 122.4437 | 122.4068 | 0.004275 | -0.013352 | 0.21524 | 122.2007 | -0.002466 | 122.4437 | 122.368 | 0.16732 | 0.09614 | -0.20742 | 122.5131 | 122.4567 | 122.6853 | 122.3891 | -0.067611 | 122.4676 | 122.5662 | 122.2627 | 122.4018 | -0.26944
2319.6406 | 122.7219 | -122.4197 | 0.10529 | 1.4211e-13 | -0.0090769 | 0.02218 | -0.0033377 | -0.0096661 | 0.010784 | 0.0016025 | 0.0084367 | 0.019234 | 0.075775 | 0.028433 | 0.0046577 | 0.069723 | 0.005985 | 0.028217 | 0.12996 | 0.073622 | 0.31595 | 0.028521 | 0.06515 | 0.03241 | -0.005985 | 0.089087 | 0.18769 | -0.11129 | -0.16873 | 122.4483 | 0.024674 | 122.4895 | 122.448 | -0.000304 | -0.031664 | 0.21067 | 122.251 | -0.016199 | 122.4849 | 122.4138 | 0.16274 | 0.082407 | -0.21658 | 122.5497 | 122.4934 | 122.7357 | 122.4257 | -0.076765 | 122.5088 | 122.6074 | 122.3084 | 122.4521 | -0.27401
2321.3906 | 122.7081 | -122.4197 | 0.082397 | 1.4211e-13 | -0.0090769 | 0.02218 | -0.0033377 | -0.0092389 | 0.010997 | 0.0016025 | 0.0090775 | 0.019234 | 0.075561 | 0.028861 | 0.0046577 | 0.065145 | 0.010564 | 0.032795 | 0.13454 | 0.064464 | 0.31595 | 0.023942 | 0.060571 | 0.027831 | -0.001407 | 0.089087 | 0.19227 | -0.12045 | -0.17331 | 122.4437 | 0.052142 | 122.4849 | 122.4525 | 0.008853 | -0.017933 | 0.23356 | 122.2464 | 0.00669 | 122.4803 | 122.4183 | 0.1719 | 0.10988 | -0.20285 | 122.5543 | 122.4842 | 122.7357 | 122.4303 | -0.058455 | 122.5088 | 122.612 | 122.2993 | 122.4476 | -0.2557
2323.0938 | 122.6349 | -122.4289 | 0.10529 | 1.4211e-13 | -0.0090769 | 0.022393 | -0.0035515 | -0.0094525 | 0.01057 | 0.0016025 | 0.0086503 | 0.019447 | 0.075775 | 0.028647 | 0.0046577 | 0.05141 | 0.015142 | 0.023639 | 0.13912 | 0.073622 | 0.31137 | 0.028521 | 0.060571 | 0.027831 | -0.001407 | 0.093665 | 0.19685 | -0.12503 | -0.17788 | 122.4574 | 0.033831 | 122.4803 | 122.4525 | -0.004882 | -0.031664 | 0.20609 | 122.251 | -0.011621 | 122.4895 | 122.4275 | 0.17648 | 0.091565 | -0.23031 | 122.568 | 122.5025 | 122.7403 | 122.444 | -0.076765 | 122.5226 | 122.6257 | 122.3039 | 122.4567 | -0.28317
2324.8594 | 122.6807 | -122.4289 | 0.10071 | 1.4211e-13 | -0.0090769 | 0.021966 | -0.0033377 | -0.0090251 | 0.01057 | 0.0016025 | 0.0088639 | 0.019447 | 0.075561 | 0.028647 | 0.0050849 | 0.065145 | 0.005985 | 0.023639 | 0.12996 | 0.078201 | 0.31595 | 0.037679 | 0.069728 | 0.018674 | -0.015143 | 0.089087 | 0.20143 | -0.11587 | -0.16873 | 122.4666 | 0.029252 | 122.494 | 122.4525 | -0.01404 | -0.022507 | 0.21524 | 122.2602 | -0.011621 | 122.4986 | 122.4138 | 0.15358 | 0.10072 | -0.21658 | 122.5589 | 122.5071 | 122.7448 | 122.4349 | -0.063029 | 122.518 | 122.6303 | 122.313 | 122.4476 | -0.26944
2326.625 | 122.7356 | -122.4014 | 0.07782 | 1.4211e-13 | -0.0090769 | 0.02218 | -0.0031241 | -0.0094525 | 0.010784 | 0.0016025 | 0.0088639 | 0.01902 | 0.075347 | 0.028861 | 0.0046577 | 0.060567 | 0.005985 | 0.028217 | 0.13912 | 0.069043 | 0.32053 | 0.037679 | 0.06515 | 0.023253 | -0.005985 | 0.089087 | 0.19685 | -0.11587 | -0.16873 | 122.4391 | 0.061297 | 122.462 | 122.4296 | -0.009462 | -0.008777 | 0.24271 | 122.2327 | 0.011267 | 122.4666 | 122.3954 | 0.16274 | 0.11903 | -0.19369 | 122.5405 | 122.4705 | 122.722 | 122.4074 | -0.040141 | 122.4905 | 122.5983 | 122.2856 | 122.4247 | -0.24655
2328.375 | 122.6669 | -122.4609 | 0.10529 | 1.4211e-13 | -0.0090769 | 0.021966 | -0.0033377 | -0.0092389 | 0.01057 | 0.0016025 | 0.0086503 | 0.01902 | 0.075134 | 0.028433 | 0.0044439 | 0.069723 | 0.005985 | 0.032795 | 0.13454 | 0.069043 | 0.31595 | 0.014784 | 0.060571 | 0.023253 | -0.001407 | 0.098244 | 0.19227 | -0.11587 | -0.17331 | 122.4757 | 0.029253 | 122.5307 | 122.4937 | 0.018011 | -0.036243 | 0.21067 | 122.2876 | -0.007042 | 122.5215 | 122.4595 | 0.1719 | 0.086986 | -0.22116 | 122.5955 | 122.53 | 122.7769 | 122.4669 | -0.090502 | 122.5592 | 122.6532 | 122.3451 | 122.4842 | -0.27859
2330.0781 | 122.6303 | -122.4335 | 0.11902 | 1.4211e-13 | -0.0088631 | 0.02218 | -0.0035515 | -0.0096661 | 0.011211 | 0.0016025 | 0.0086503 | 0.019234 | 0.075775 | 0.028647 | 0.0048713 | 0.060567 | 0.005985 | 0.032795 | 0.13454 | 0.069043 | 0.31137 | 0.023942 | 0.060571 | 0.023253 | -0.001407 | 0.089087 | 0.19227 | -0.11129 | -0.16873 | 122.4574 | 0.01552 | 122.494 | 122.4663 | 0.008853 | -0.049976 | 0.19235 | 122.2647 | -0.029932 | 122.494 | 122.4321 | 0.16732 | 0.073253 | -0.23031 | 122.568 | 122.5025 | 122.7448 | 122.4395 | -0.095077 | 122.5226 | 122.6257 | 122.3222 | 122.4567 | -0.28775
2331.8281 | 122.731 | -122.4197 | 0.11444 | 1.4211e-13 | -0.0090769 | 0.02218 | -0.0033377 | -0.0092389 | 0.010997 | -0.006028 | 0.0086503 | 0.019234 | 0.075561 | 0.028861 | 0.0044439 | 0.069723 | 0.005985 | 0.032795 | 0.13454 | 0.078201 | 0.31595 | 0.028521 | 0.060571 | 0.023253 | -0.005985 | 0.07993 | 0.19685 | -0.12503 | -0.16873 | 122.4483 | 0.020098 | 122.4895 | 122.4525 | 0.004274 | -0.03624 | 0.20151 | 122.251 | -0.034511 | 122.4803 | 122.4138 | 0.16274 | 0.08241 | -0.23947 | 122.5543 | 122.4979 | 122.7357 | 122.4257 | -0.08592 | 122.4997 | 122.6166 | 122.2947 | 122.443 | -0.28317
2333.5156 | 122.6349 | -122.4747 | 0.13275 | 1.4211e-13 | -0.0092905 | 0.02218 | -0.0033377 | -0.0094525 | 0.010784 | -0.006028 | 0.0090775 | 0.019447 | 0.075561 | 0.028647 | 0.0042303 | 0.065145 | 0.005985 | 0.01906 | 0.13454 | 0.08278 | 0.3068 | 0.028521 | 0.069728 | 0.023253 | -0.001407 | 0.084508 | 0.19227 | -0.11587 | -0.16873 | 122.5032 | 0.001788 | 122.5398 | 122.4937 | -0.009461 | -0.049971 | 0.17405 | 122.3059 | -0.048243 | 122.5444 | 122.4733 | 0.16732 | 0.059521 | -0.24862 | 122.6092 | 122.5575 | 122.7815 | 122.4807 | -0.10423 | 122.5592 | 122.6669 | 122.3588 | 122.4979 | -0.30148
2335.2812 | 122.7356 | -122.438 | 0.10071 | 1.4211e-13 | -0.0088631 | 0.02218 | -0.0035515 | -0.0094525 | 0.010784 | 0.0092325 | 0.0086503 | 0.019447 | 0.075561 | 0.028647 | 0.0044439 | 0.069723 | 0.015142 | 0.028217 | 0.14827 | 0.078201 | 0.31595 | 0.028521 | 0.06515 | 0.023253 | -0.005985 | 0.089087 | 0.19685 | -0.12045 | -0.17788 | 122.4666 | 0.047566 | 122.5078 | 122.4663 | -0.000304 | -0.022507 | 0.21524 | 122.2602 | -0.011621 | 122.5032 | 122.4321 | 0.1719 | 0.096143 | -0.22116 | 122.5863 | 122.5163 | 122.754 | 122.4532 | -0.072187 | 122.5271 | 122.6349 | 122.3176 | 122.4613 | -0.27859
2336.9688 | 122.6028 | -122.4792 | 0.11902 | 1.4211e-13 | -0.0086495 | 0.021966 | -0.0033377 | -0.0094525 | 0.010997 | -0.006028 | 0.0088639 | 0.019447 | 0.075561 | 0.028861 | 0.0046577 | 0.065145 | 0.010564 | 0.023639 | 0.13912 | 0.069043 | 0.32053 | 0.023942 | 0.069728 | 0.023253 | -0.005985 | 0.089087 | 0.20143 | -0.12045 | -0.17331 | 122.5032 | 0.020098 | 122.5444 | 122.5029 | -0.000303 | -0.049976 | 0.20151 | 122.3059 | -0.029932 | 122.549 | 122.4733 | 0.16732 | 0.08241 | -0.23947 | 122.6184 | 122.5483 | 122.7998 | 122.4898 | -0.095077 | 122.5683 | 122.6807 | 122.3588 | 122.5025 | -0.29233
2338.7188 | 122.6578 | -122.4426 | 0.10986 | 1.4211e-13 | -0.0090769 | 0.02218 | -0.0031241 | -0.0094525 | 0.010784 | 0.0016025 | 0.0088639 | 0.019447 | 0.075561 | 0.028433 | 0.0046577 | 0.065145 | 0.010564 | 0.023639 | 0.13912 | 0.078201 | 0.32511 | 0.037679 | 0.06515 | 0.023253 | 0.003172 | 0.093665 | 0.19685 | -0.11587 | -0.17331 | 122.4803 | 0.029254 | 122.5078 | 122.4663 | -0.01404 | -0.031662 | 0.21525 | 122.2693 | -0.016198 | 122.5078 | 122.4458 | 0.17648 | 0.086988 | -0.22574 | 122.5817 | 122.5208 | 122.7677 | 122.4532 | -0.072184 | 122.5363 | 122.6395 | 122.3268 | 122.4659 | -0.28317
2340.4844 | 122.6486 | -122.438 | 0.10529 | 1.4211e-13 | -0.0088631 | 0.021966 | -0.0031241 | -0.0094525 | 0.010997 | -0.006028 | 0.0086503 | 0.019447 | 0.075347 | 0.028647 | 0.0044439 | 0.065145 | 0.005985 | 0.023639 | 0.13454 | 0.078201 | 0.31595 | 0.0331 | 0.06515 | 0.027831 | -0.005985 | 0.089087 | 0.19685 | -0.11129 | -0.16873 | 122.4711 | 0.029253 | 122.5032 | 122.4617 | -0.009461 | -0.027085 | 0.21067 | 122.2693 | -0.016199 | 122.5032 | 122.4321 | 0.16274 | 0.091565 | -0.21658 | 122.5726 | 122.5163 | 122.754 | 122.444 | -0.072186 | 122.5271 | 122.6349 | 122.3268 | 122.4659 | -0.27401
2342.25 | 122.699 | -122.4472 | 0.10071 | 1.4211e-13 | -0.0088631 | 0.02218 | -0.0033377 | -0.0094525 | 0.01057 | 0.0016025 | 0.0084367 | 0.019447 | 0.075347 | 0.028861 | 0.0046577 | 0.069723 | 0.010564 | 0.023639 | 0.12996 | 0.073622 | 0.31595 | 0.014784 | 0.06515 | 0.023253 | -0.001407 | 0.089087 | 0.19685 | -0.12045 | -0.16873 | 122.462 | 0.029252 | 122.5169 | 122.4708 | 0.008855 | -0.027086 | 0.21524 | 122.2785 | -0.011621 | 122.5124 | 122.4458 | 0.16732 | 0.096143 | -0.22116 | 122.5772 | 122.5208 | 122.7632 | 122.4578 | -0.085924 | 122.5363 | 122.6441 | 122.3268 | 122.4705 | -0.26944
2343.9375 | 122.7081 | -122.4655 | 0.082397 | 1.4211e-13 | -0.0090769 | 0.022393 | -0.0031241 | -0.0096661 | 0.010784 | -0.006028 | 0.0088639 | 0.019447 | 0.075561 | 0.028647 | 0.0048713 | 0.065145 | 0.015142 | 0.028217 | 0.13912 | 0.078201 | 0.31137 | 0.023942 | 0.069728 | 0.023253 | -0.010564 | 0.089087 | 0.19685 | -0.11587 | -0.17788 | 122.4895 | 0.05672 | 122.5307 | 122.4937 | 0.004275 | -0.004196 | 0.22898 | 122.2876 | 0.00669 | 122.5352 | 122.455 | 0.16732 | 0.11445 | -0.19827 | 122.6046 | 122.5437 | 122.7769 | 122.4807 | -0.058455 | 122.5546 | 122.6624 | 122.3496 | 122.4888 | -0.26028
2345.7031 | 122.6028 | -122.4747 | 0.14648 | 1.4211e-13 | -0.0088631 | 0.02218 | -0.0035515 | -0.0094525 | 0.010784 | -0.013659 | 0.0086503 | 0.019447 | 0.075561 | 0.029075 | 0.0046577 | 0.065145 | 0.005985 | 0.032795 | 0.13912 | 0.073622 | 0.31595 | 0.023942 | 0.06515 | 0.023253 | -0.010564 | 0.089087 | 0.19685 | -0.12503 | -0.17788 | 122.4986 | -0.007367 | 122.5398 | 122.5075 | 0.008853 | -0.072862 | 0.16947 | 122.2968 | -0.057397 | 122.5398 | 122.4641 | 0.16732 | 0.050367 | -0.27151 | 122.6138 | 122.5483 | 122.7906 | 122.4807 | -0.12254 | 122.5638 | 122.6715 | 122.3496 | 122.4979 | -0.32437
2347.3906 | 122.6578 | -122.4609 | 0.14191 | 1.4211e-13 | -0.0090769 | 0.021966 | -0.0033377 | -0.0094525 | 0.010784 | 0.0016025 | 0.0084367 | 0.019447 | 0.075561 | 0.028861 | 0.0046577 | 0.069723 | 0.015142 | 0.032795 | 0.13454 | 0.073622 | 0.31137 | 0.019363 | 0.06515 | 0.023253 | -0.001407 | 0.089087 | 0.19685 | -0.11129 | -0.17788 | 122.4803 | -0.007368 | 122.5307 | 122.4937 | 0.013432 | -0.068285 | 0.16947 | 122.2831 | -0.05282 | 122.5261 | 122.4595 | 0.17648 | 0.054944 | -0.2532 | 122.5955 | 122.5346 | 122.7723 | 122.4761 | -0.12254 | 122.55 | 122.6578 | 122.3496 | 122.4842 | -0.31979
2349.0938 | 122.7356 | -122.4152 | 0.09613 | 1.4211e-13 | -0.0088631 | 0.021966 | -0.0035515 | -0.0094525 | 0.010997 | -0.006028 | 0.0086503 | 0.019447 | 0.075775 | 0.028647 | 0.0042303 | 0.055988 | 0.005985 | 0.023639 | 0.12996 | 0.073622 | 0.31595 | 0.023942 | 0.069728 | 0.03241 | 0.003172 | 0.093665 | 0.19685 | -0.12045 | -0.17331 | 122.4391 | 0.03383 | 122.4711 | 122.4388 | -0.000303 | -0.022508 | 0.21982 | 122.2419 | -0.002465 | 122.4849 | 122.4183 | 0.17648 | 0.10072 | -0.21658 | 122.5451 | 122.4888 | 122.7311 | 122.4211 | -0.072188 | 122.5088 | 122.612 | 122.2947 | 122.4476 | -0.26944
2350.8594 | 122.6349 | -122.4564 | 0.14648 | 1.4211e-13 | -0.0090769 | 0.022393 | -0.0033377 | -0.0094525 | 0.010784 | 0.0016025 | 0.0088639 | 0.019234 | 0.075561 | 0.028647 | 0.0044439 | 0.055988 | 0.010564 | 0.023639 | 0.13912 | 0.073622 | 0.31595 | 0.023942 | 0.06515 | 0.027831 | -0.001407 | 0.093665 | 0.19685 | -0.11587 | -0.16873 | 122.4803 | -0.007367 | 122.5123 | 122.48 | -0.000303 | -0.072862 | 0.16947 | 122.2876 | -0.052819 | 122.5215 | 122.455 | 0.16732 | 0.050367 | -0.26236 | 122.5955 | 122.53 | 122.7723 | 122.4669 | -0.12254 | 122.55 | 122.6532 | 122.3405 | 122.4842 | -0.31521
2352.625 | 122.7356 | -122.4701 | 0.10529 | 1.4211e-13 | -0.0090769 | 0.022393 | -0.0035515 | -0.0094525 | 0.01057 | 0.0092325 | 0.0082229 | 0.019447 | 0.075561 | 0.028647 | 0.0046577 | 0.065145 | 0.005985 | 0.023639 | 0.13454 | 0.073622 | 0.31595 | 0.014784 | 0.069728 | 0.023253 | -0.001407 | 0.089087 | 0.18769 | -0.11587 | -0.17788 | 122.4849 | 0.029253 | 122.5352 | 122.4937 | 0.008855 | -0.031664 | 0.21067 | 122.2922 | -0.016199 | 122.5398 | 122.4687 | 0.17648 | 0.082407 | -0.22116 | 122.6046 | 122.5437 | 122.786 | 122.4761 | -0.090502 | 122.5592 | 122.6578 | 122.3542 | 122.4933 | -0.28317
2354.3281 | 122.6395 | -122.4701 | 0.10529 | 1.4211e-13 | -0.0090769 | 0.021966 | -0.0031241 | -0.0090251 | 0.010784 | 0.016863 | 0.0088639 | 0.019447 | 0.075988 | 0.028647 | 0.0046577 | 0.055988 | 0.005985 | 0.01906 | 0.13454 | 0.073622 | 0.31137 | 0.019363 | 0.06515 | 0.023253 | -0.005985 | 0.089087 | 0.20143 | -0.11129 | -0.17331 | 122.4895 | 0.029253 | 122.5261 | 122.4892 | -0.000303 | -0.031664 | 0.20609 | 122.2968 | -0.016199 | 122.5352 | 122.4641 | 0.16732 | 0.096143 | -0.21658 | 122.6046 | 122.5437 | 122.7815 | 122.4761 | -0.085923 | 122.5592 | 122.6715 | 122.3588 | 122.4933 | -0.27859
2356.0938 | 122.7219 | -122.4792 | 0.091553 | 1.4211e-13 | -0.0092905 | 0.02218 | -0.0033377 | -0.0098799 | 0.010997 | 0.0016025 | 0.0086503 | 0.019234 | 0.075561 | 0.028861 | 0.0048713 | 0.060567 | 0.015142 | 0.023639 | 0.12996 | 0.069043 | 0.31137 | 0.014784 | 0.06515 | 0.023253 | -0.005985 | 0.084508 | 0.20143 | -0.12045 | -0.17331 | 122.494 | 0.038407 | 122.5398 | 122.5029 | 0.008855 | -0.02251 | 0.21982 | 122.3059 | -0.007045 | 122.5444 | 122.4733 | 0.16732 | 0.10988 | -0.212 | 122.6092 | 122.5483 | 122.7906 | 122.4944 | -0.076769 | 122.5638 | 122.6807 | 122.3588 | 122.5025 | -0.26486
2357.8438 | 122.7402 | -122.4655 | 0.10071 | 1.4211e-13 | -0.0090769 | 0.021966 | -0.0033377 | -0.0092389 | 0.01057 | -0.013659 | 0.0082229 | 0.019234 | 0.075561 | 0.028861 | 0.0042303 | 0.065145 | 0.010564 | 0.028217 | 0.13454 | 0.073622 | 0.31595 | 0.019363 | 0.055992 | 0.023253 | 0.003172 | 0.089087 | 0.20143 | -0.097557 | -0.16415 | 122.4849 | 0.033831 | 122.5307 | 122.4937 | 0.008854 | -0.027086 | 0.21524 | 122.3014 | -0.011621 | 122.5215 | 122.4687 | 0.16732 | 0.10072 | -0.19827 | 122.6001 | 122.5391 | 122.7815 | 122.4761 | -0.081345 | 122.5546 | 122.6669 | 122.368 | 122.4888 | -0.26486
2359.5469 | 122.6532 | -122.4976 | 0.11902 | 1.4211e-13 | -0.0090769 | 0.021966 | -0.0037651 | -0.0094525 | 0.010784 | -0.013659 | 0.0086503 | 0.019661 | 0.075775 | 0.029075 | 0.0046577 | 0.055988 | 0.010564 | 0.032795 | 0.13912 | 0.078201 | 0.31137 | 0.019363 | 0.06515 | 0.018674 | -0.001407 | 0.089087 | 0.20143 | -0.12045 | -0.16873 | 122.5169 | 0.020098 | 122.5535 | 122.5304 | 0.013432 | -0.040818 | 0.19235 | 122.3288 | -0.029932 | 122.5627 | 122.4962 | 0.16732 | 0.08241 | -0.23947 | 122.6367 | 122.5758 | 122.8089 | 122.5081 | -0.099656 | 122.5866 | 122.699 | 122.3771 | 122.5162 | -0.28775
2361.3125 | 122.7676 | -122.4609 | 0.073242 | 1.4211e-13 | -0.0086495 | 0.021752 | -0.0035515 | -0.0094525 | 0.010784 | 0.0016025 | 0.0088639 | 0.019661 | 0.075561 | 0.028861 | 0.0044439 | 0.060567 | 0.015142 | 0.032795 | 0.13912 | 0.073622 | 0.32053 | 0.028521 | 0.060571 | 0.023253 | -0.001407 | 0.093665 | 0.19685 | -0.11129 | -0.16873 | 122.4895 | 0.065875 | 122.5215 | 122.4937 | 0.004274 | 0.00038 | 0.24729 | 122.2922 | 0.020423 | 122.5215 | 122.4595 | 0.16732 | 0.12361 | -0.18454 | 122.6001 | 122.5346 | 122.7815 | 122.4761 | -0.044721 | 122.5546 | 122.6578 | 122.3496 | 122.4842 | -0.24197
2363.0625 | 122.7676 | -122.4792 | 0.091553 | 1.4211e-13 | -0.0086495 | 0.021966 | -0.0033377 | -0.0096661 | 0.010784 | 0.0016025 | 0.0086503 | 0.019234 | 0.075561 | 0.028861 | 0.0044439 | 0.069723 | 0.010564 | 0.023639 | 0.13454 | 0.08278 | 0.31595 | 0.023942 | 0.060571 | 0.027831 | -0.001407 | 0.089087 | 0.19685 | -0.12503 | -0.17331 | 122.5032 | 0.042986 | 122.549 | 122.5029 | -0.000303 | -0.008773 | 0.2244 | 122.3059 | -0.002466 | 122.5398 | 122.4778 | 0.1719 | 0.1053 | -0.21658 | 122.6138 | 122.562 | 122.7952 | 122.4898 | -0.067611 | 122.5683 | 122.6761 | 122.3542 | 122.5071 | -0.26486
2364.8281 | 122.6532 | -122.5067 | 0.12817 | 1.4211e-13 | -0.0088631 | 0.02218 | -0.0033377 | -0.0096661 | 0.010784 | -0.013659 | 0.0090775 | 0.019447 | 0.075561 | 0.028647 | 0.0046577 | 0.060567 | 0.010564 | 0.028217 | 0.12996 | 0.078201 | 0.31137 | 0.028521 | 0.060571 | 0.027831 | -0.005985 | 0.089087 | 0.19685 | -0.12045 | -0.18704 | 122.5352 | 0.001786 | 122.5673 | 122.5349 | -0.000304 | -0.049973 | 0.1832 | 122.3197 | -0.039087 | 122.5673 | 122.5007 | 0.18106 | 0.068677 | -0.24862 | 122.6367 | 122.5849 | 122.8181 | 122.5173 | -0.099653 | 122.5958 | 122.7036 | 122.3863 | 122.5345 | -0.31522
2366.5312 | 122.644 | -122.5204 | 0.13275 | 1.4211e-13 | -0.0086495 | 0.02218 | -0.0031241 | -0.0094525 | 0.010997 | 0.0016025 | 0.0088639 | 0.019447 | 0.075561 | 0.028861 | 0.0044439 | 0.069723 | 0.005985 | 0.01906 | 0.13454 | 0.078201 | 0.31595 | 0.019363 | 0.06515 | 0.023253 | -0.001407 | 0.084508 | 0.19227 | -0.12045 | -0.16415 | 122.5398 | 0.001788 | 122.5902 | 122.5395 | -0.000303 | -0.05455 | 0.1832 | 122.3563 | -0.048243 | 122.5856 | 122.519 | 0.16274 | 0.059521 | -0.2532 | 122.655 | 122.5986 | 122.8364 | 122.5264 | -0.11339 | 122.605 | 122.7127 | 122.4 | 122.5437 | -0.2969
2368.3125 | 122.644 | -122.5296 | 0.13733 | 1.4211e-13 | -0.0088631 | 0.02218 | -0.0033377 | -0.0094525 | 0.010784 | -0.006028 | 0.0086503 | 0.019234 | 0.075561 | 0.028861 | 0.0044439 | 0.065145 | 0.010564 | 0.032795 | 0.13454 | 0.078201 | 0.31137 | 0.028521 | 0.06515 | 0.03241 | -0.001407 | 0.089087 | 0.20143 | -0.11587 | -0.17331 | 122.5581 | -0.00279 | 122.5947 | 122.5624 | 0.004274 | -0.059128 | 0.17404 | 122.3563 | -0.048242 | 122.5948 | 122.5282 | 0.1719 | 0.0641 | -0.2532 | 122.6641 | 122.6078 | 122.841 | 122.5402 | -0.10881 | 122.6187 | 122.731 | 122.4137 | 122.562 | -0.31063
2370.0156 | 122.7768 | -122.5113 | 0.09613 | 1.4211e-13 | -0.0090769 | 0.022393 | -0.0035515 | -0.0094525 | 0.010784 | 0.0016025 | 0.0086503 | 0.019234 | 0.075347 | 0.028647 | 0.0040167 | 0.069723 | 0.010564 | 0.01906 | 0.13454 | 0.078201 | 0.32053 | 0.019363 | 0.069728 | 0.027831 | -0.001407 | 0.093665 | 0.19685 | -0.11587 | -0.17331 | 122.5307 | 0.038409 | 122.581 | 122.5304 | -0.000303 | -0.017929 | 0.2244 | 122.338 | -0.002465 | 122.581 | 122.5099 | 0.1719 | 0.10072 | -0.212 | 122.6458 | 122.5895 | 122.8318 | 122.5219 | -0.076767 | 122.605 | 122.7081 | 122.3954 | 122.5391 | -0.26944
2371.7656 | 122.6624 | -122.5067 | 0.13275 | 1.4211e-13 | -0.0086495 | 0.021752 | -0.0031241 | -0.0092389 | 0.010997 | 0.0016025 | 0.0084367 | 0.019447 | 0.075561 | 0.028647 | 0.0046577 | 0.065145 | 0.010564 | 0.023639 | 0.12538 | 0.078201 | 0.32053 | 0.023942 | 0.069728 | 0.036989 | 0.003172 | 0.093665 | 0.19685 | -0.11587 | -0.17331 | 122.5307 | -0.007369 | 122.5719 | 122.5304 | -0.000303 | -0.05455 | 0.18778 | 122.3334 | -0.039086 | 122.5764 | 122.5099 | 0.17648 | 0.0641 | -0.24862 | 122.6321 | 122.5849 | 122.8272 | 122.5173 | -0.10881 | 122.6004 | 122.7036 | 122.3908 | 122.5437 | -0.30606
2373.5156 | 122.6532 | -122.5067 | 0.12817 | 1.4211e-13 | -0.0090769 | 0.02218 | -0.0031241 | -0.0092389 | 0.011211 | -0.006028 | 0.0088639 | 0.019234 | 0.075561 | 0.028861 | 0.0046577 | 0.060567 | 0.005985 | 0.023639 | 0.14369 | 0.08278 | 0.31595 | 0.023942 | 0.060571 | 0.036989 | -0.005985 | 0.093665 | 0.19227 | -0.11587 | -0.17331 | 122.5307 | 0.015521 | 122.5673 | 122.5304 | -0.000303 | -0.045394 | 0.18778 | 122.3334 | -0.034509 | 122.5673 | 122.5007 | 0.16732 | 0.064098 | -0.24405 | 122.6504 | 122.5895 | 122.8227 | 122.5127 | -0.10423 | 122.6004 | 122.699 | 122.3908 | 122.5437 | -0.30148
2375.2188 | 122.7539 | -122.5021 | 0.11444 | 1.4211e-13 | -0.0088631 | 0.02218 | -0.0031241 | -0.0094525 | 0.01057 | -0.013659 | 0.0088639 | 0.019234 | 0.075775 | 0.028647 | 0.0046577 | 0.065145 | 0.010564 | 0.037373 | 0.13454 | 0.073622 | 0.32053 | 0.023942 | 0.06515 | 0.036989 | -0.001407 | 0.089087 | 0.19685 | -0.12045 | -0.17788 | 122.5261 | 0.020098 | 122.5673 | 122.5395 | 0.013431 | -0.040819 | 0.20609 | 122.3243 | -0.025354 | 122.5673 | 122.5007 | 0.17648 | 0.08241 | -0.23489 | 122.6367 | 122.5758 | 122.8227 | 122.5127 | -0.090499 | 122.5912 | 122.699 | 122.3817 | 122.5391 | -0.29233
2376.9688 | 122.7859 | -122.4747 | 0.09613 | 1.4211e-13 | -0.0088631 | 0.021966 | -0.0033377 | -0.0090251 | 0.010997 | -0.006028 | 0.0086503 | 0.019447 | 0.075775 | 0.028647 | 0.0046577 | 0.055988 | 0.010564 | 0.028217 | 0.13454 | 0.078201 | 0.31137 | 0.042258 | 0.055992 | 0.036989 | -0.001407 | 0.089087 | 0.19685 | -0.11129 | -0.17331 | 122.5169 | 0.038409 | 122.5307 | 122.5029 | -0.014041 | -0.017929 | 0.21524 | 122.3014 | -0.007043 | 122.5307 | 122.4733 | 0.1719 | 0.10072 | -0.20742 | 122.6092 | 122.5529 | 122.786 | 122.4852 | -0.053872 | 122.5638 | 122.6715 | 122.3634 | 122.5117 | -0.26944
2378.6562 | 122.6669 | -122.5525 | 0.12817 | 1.4211e-13 | -0.0090769 | 0.02218 | -0.0033377 | -0.0096661 | 0.011211 | 0.0016025 | 0.0088639 | 0.019447 | 0.075347 | 0.028433 | 0.0044439 | 0.060567 | 0.010564 | 0.028217 | 0.13454 | 0.078201 | 0.3068 | 0.023942 | 0.06515 | 0.027831 | -0.005985 | 0.093665 | 0.19227 | -0.11587 | -0.17788 | 122.5764 | 0.006365 | 122.6131 | 122.5807 | 0.004275 | -0.049973 | 0.17862 | 122.3746 | -0.034509 | 122.6176 | 122.5465 | 0.1719 | 0.064098 | -0.24405 | 122.687 | 122.6307 | 122.8593 | 122.5631 | -0.10423 | 122.6462 | 122.7448 | 122.4366 | 122.5803 | -0.30606
2380.4062 | 122.731 | -122.5159 | 0.10071 | 1.4211e-13 | -0.0090769 | 0.021966 | -0.0035515 | -0.0096661 | 0.010784 | 0.0092325 | 0.0090775 | 0.019234 | 0.075775 | 0.029075 | 0.0048713 | 0.060567 | 0.010564 | 0.01906 | 0.12996 | 0.069043 | 0.31137 | 0.028521 | 0.06515 | 0.036989 | 0.007751 | 0.093665 | 0.19227 | -0.12503 | -0.16873 | 122.5444 | 0.029252 | 122.5764 | 122.5349 | -0.009461 | -0.031665 | 0.21067 | 122.3471 | -0.007043 | 122.581 | 122.5236 | 0.17648 | 0.091564 | -0.22574 | 122.6458 | 122.5849 | 122.8272 | 122.5264 | -0.072187 | 122.6095 | 122.7081 | 122.3908 | 122.5529 | -0.26944
2382.1562 | 122.6852 | -122.5067 | 0.13733 | 1.4211e-13 | -0.0088631 | 0.02218 | -0.0031241 | -0.0094525 | 0.01057 | 0.0092325 | 0.0090775 | 0.019234 | 0.075988 | 0.029288 | 0.0046577 | 0.060567 | 0.005985 | 0.01906 | 0.13912 | 0.073622 | 0.31137 | 0.014784 | 0.06515 | 0.03241 | 0.003172 | 0.089087 | 0.19227 | -0.12045 | -0.17788 | 122.5215 | 0.001788 | 122.5673 | 122.5258 | 0.004276 | -0.063707 | 0.17404 | 122.3288 | -0.048242 | 122.5719 | 122.5099 | 0.18106 | 0.054943 | -0.25778 | 122.6458 | 122.5803 | 122.8181 | 122.5127 | -0.12255 | 122.5958 | 122.699 | 122.3863 | 122.5391 | -0.31521
2383.9219 | 122.7768 | -122.5113 | 0.10071 | 1.4211e-13 | -0.0090769 | 0.02218 | -0.0033377 | -0.0092389 | 0.010997 | -0.013659 | 0.0086503 | 0.019234 | 0.075561 | 0.028861 | 0.0048713 | 0.060567 | 0.005985 | 0.023639 | 0.12996 | 0.073622 | 0.31137 | 0.028521 | 0.060571 | 0.027831 | -0.010564 | 0.084508 | 0.19685 | -0.11129 | -0.17788 | 122.5398 | 0.029252 | 122.5719 | 122.5349 | -0.004882 | -0.027086 | 0.21067 | 122.3334 | -0.0162 | 122.5719 | 122.5007 | 0.16732 | 0.096143 | -0.212 | 122.6413 | 122.5849 | 122.8227 | 122.5173 | -0.072187 | 122.5958 | 122.7081 | 122.4 | 122.5391 | -0.27859
2385.6094 | 122.7036 | -122.5479 | 0.13275 | 1.4211e-13 | -0.0088631 | 0.022393 | -0.0031241 | -0.0096661 | 0.010784 | -0.006028 | 0.0084367 | 0.019447 | 0.075561 | 0.029075 | 0.0048713 | 0.065145 | 0.010564 | 0.023639 | 0.13454 | 0.078201 | 0.31595 | 0.019363 | 0.060571 | 0.036989 | -0.005985 | 0.089087 | 0.19685 | -0.11587 | -0.17788 | 122.5673 | 0.001788 | 122.6131 | 122.5716 | 0.004276 | -0.05455 | 0.1832 | 122.37 | -0.043664 | 122.6085 | 122.5419 | 0.1719 | 0.0641 | -0.24862 | 122.6825 | 122.6261 | 122.8639 | 122.5585 | -0.11339 | 122.637 | 122.7448 | 122.432 | 122.5849 | -0.31064
2387.4062 | 122.7722 | -122.5067 | 0.10529 | 1.4211e-13 | -0.0088631 | 0.022393 | -0.0033377 | -0.0092389 | 0.01057 | -0.006028 | 0.0084367 | 0.019447 | 0.075561 | 0.029075 | 0.0046577 | 0.060567 | 0.010564 | 0.023639 | 0.13454 | 0.087359 | 0.31137 | 0.014784 | 0.06515 | 0.027831 | -0.005985 | 0.093665 | 0.19227 | -0.12045 | -0.17331 | 122.5215 | 0.029253 | 122.5673 | 122.5304 | 0.008855 | -0.017927 | 0.20609 | 122.3334 | -0.011621 | 122.5719 | 122.5007 | 0.16732 | 0.086986 | -0.22574 | 122.6413 | 122.5941 | 122.8181 | 122.5173 | -0.090502 | 122.6004 | 122.699 | 122.3863 | 122.5345 | -0.27859
2389.1094 | 122.7814 | -122.5113 | 0.10071 | 1.4211e-13 | -0.0092905 | 0.021966 | -0.0031241 | -0.0094525 | 0.010997 | -0.013659 | 0.0084367 | 0.019447 | 0.075561 | 0.029075 | 0.0048713 | 0.065145 | 0.010564 | 0.032795 | 0.13454 | 0.08278 | 0.31595 | 0.028521 | 0.060571 | 0.03241 | -0.010564 | 0.089087 | 0.19685 | -0.11587 | -0.17331 | 122.5398 | 0.033831 | 122.5764 | 122.5441 | 0.004274 | -0.017928 | 0.21524 | 122.338 | -0.011621 | 122.5719 | 122.5007 | 0.16274 | 0.096143 | -0.21658 | 122.6458 | 122.5941 | 122.8272 | 122.5219 | -0.072187 | 122.6004 | 122.7081 | 122.3954 | 122.5437 | -0.27401
2390.875 | 122.7676 | -122.5296 | 0.09613 | 1.4211e-13 | -0.0088631 | 0.021966 | -0.0033377 | -0.0094525 | 0.010784 | -0.006028 | 0.0090775 | 0.019447 | 0.075134 | 0.028861 | 0.0050849 | 0.065145 | 0.005985 | 0.028217 | 0.13912 | 0.073622 | 0.32511 | 0.028521 | 0.06515 | 0.03241 | 0.007751 | 0.089087 | 0.19685 | -0.11587 | -0.17331 | 122.5581 | 0.042987 | 122.5947 | 122.5578 | -0.000304 | -0.022508 | 0.22898 | 122.3563 | -0.007043 | 122.5948 | 122.5374 | 0.18106 | 0.10072 | -0.212 | 122.6687 | 122.6032 | 122.8547 | 122.5356 | -0.067609 | 122.6187 | 122.7265 | 122.4137 | 122.562 | -0.26944
2392.6406 | 122.8134 | -122.5204 | 0.10071 | 1.4211e-13 | -0.0088631 | 0.02218 | -0.0035515 | -0.0096661 | 0.01057 | -0.006028 | 0.0086503 | 0.019234 | 0.075988 | 0.028861 | 0.0046577 | 0.065145 | 0.005985 | 0.023639 | 0.12538 | 0.08278 | 0.31137 | 0.019363 | 0.060571 | 0.027831 | -0.005985 | 0.089087 | 0.19227 | -0.11587 | -0.17331 | 122.5398 | 0.024674 | 122.5856 | 122.5441 | 0.004276 | -0.017928 | 0.21067 | 122.3471 | -0.011621 | 122.581 | 122.5145 | 0.16732 | 0.091564 | -0.21658 | 122.6458 | 122.6032 | 122.8318 | 122.5264 | -0.081345 | 122.6095 | 122.7127 | 122.4046 | 122.5483 | -0.27401
2394.4062 | 122.6578 | -122.5296 | 0.11444 | 1.4211e-13 | -0.0088631 | 0.021966 | -0.0031241 | -0.0098799 | 0.01057 | -0.006028 | 0.0084367 | 0.019661 | 0.075561 | 0.028647 | 0.0044439 | 0.060567 | 0.005985 | 0.028217 | 0.13454 | 0.08278 | 0.31137 | 0.023942 | 0.060571 | 0.027831 | -0.001407 | 0.089087 | 0.19685 | -0.11129 | -0.16873 | 122.5535 | 0.020098 | 122.5902 | 122.5578 | 0.004275 | -0.031661 | 0.19693 | 122.3609 | -0.025354 | 122.5902 | 122.5282 | 0.16732 | 0.08241 | -0.22573 | 122.6641 | 122.6124 | 122.841 | 122.5356 | -0.090499 | 122.6187 | 122.7265 | 122.4183 | 122.5574 | -0.28317
2396.1094 | 122.6898 | -122.5616 | 0.11902 | 1.4211e-13 | -0.0088631 | 0.021966 | -0.0037651 | -0.0092389 | 0.010997 | -0.006028 | 0.0088639 | 0.019875 | 0.075775 | 0.029075 | 0.0048713 | 0.065145 | 0.015142 | 0.01906 | 0.12996 | 0.069043 | 0.31595 | 0.023942 | 0.06515 | 0.027831 | -0.005985 | 0.07993 | 0.20143 | -0.11129 | -0.16873 | 122.5856 | 0.010941 | 122.6268 | 122.5807 | -0.004882 | -0.049976 | 0.19693 | 122.3929 | -0.039089 | 122.6268 | 122.5557 | 0.16274 | 0.08241 | -0.23031 | 122.6916 | 122.6307 | 122.8776 | 122.5768 | -0.095077 | 122.6416 | 122.7631 | 122.4504 | 122.5895 | -0.28775
2397.875 | 122.7859 | -122.5159 | 0.10529 | 1.4211e-13 | -0.0090769 | 0.022393 | -0.0035515 | -0.0096661 | 0.010997 | -0.006028 | 0.0090775 | 0.01902 | 0.075561 | 0.028433 | 0.0044439 | 0.065145 | 0.015142 | 0.032795 | 0.12996 | 0.078201 | 0.31137 | 0.014784 | 0.060571 | 0.027831 | -0.001407 | 0.098244 | 0.19227 | -0.12045 | -0.17331 | 122.5307 | 0.024674 | 122.581 | 122.5487 | 0.018011 | -0.027085 | 0.20609 | 122.3426 | -0.007042 | 122.5764 | 122.5145 | 0.1719 | 0.086986 | -0.22574 | 122.6458 | 122.5941 | 122.8272 | 122.531 | -0.090502 | 122.6141 | 122.7081 | 122.3954 | 122.5437 | -0.27859
2399.5781 | 122.7356 | -122.5388 | 0.11444 | 1.4211e-13 | -0.0086495 | 0.021966 | -0.0033377 | -0.0092389 | 0.010784 | -0.006028 | 0.0084367 | 0.019447 | 0.075561 | 0.029075 | 0.0046577 | 0.069723 | 0.010564 | 0.028217 | 0.12996 | 0.073622 | 0.31595 | 0.028521 | 0.069728 | 0.027831 | -0.005985 | 0.089087 | 0.19685 | -0.11587 | -0.17331 | 122.5673 | 0.015519 | 122.6085 | 122.567 | -0.000304 | -0.040819 | 0.20151 | 122.3655 | -0.025354 | 122.6085 | 122.5328 | 0.16732 | 0.08241 | -0.23031 | 122.6687 | 122.6124 | 122.8547 | 122.5493 | -0.08592 | 122.6278 | 122.7356 | 122.4229 | 122.5666 | -0.28775
2401.3438 | 122.8226 | -122.5067 | 0.091553 | 1.4211e-13 | -0.0088631 | 0.021966 | -0.0033377 | -0.0092389 | 0.010784 | 0.0092325 | 0.0088639 | 0.019447 | 0.075134 | 0.028861 | 0.0048713 | 0.065145 | 0.010564 | 0.023639 | 0.13912 | 0.078201 | 0.32511 | 0.019363 | 0.074307 | 0.027831 | -0.001407 | 0.084508 | 0.19685 | -0.11129 | -0.17331 | 122.5261 | 0.047564 | 122.5719 | 122.5304 | 0.004276 | -0.013352 | 0.23356 | 122.3334 | -0.007045 | 122.581 | 122.5053 | 0.1719 | 0.1053 | -0.20285 | 122.6458 | 122.5849 | 122.8318 | 122.5173 | -0.07219 | 122.5912 | 122.7036 | 122.3954 | 122.5345 | -0.26486
2403.0938 | 122.7997 | -122.5296 | 0.10071 | 1.4211e-13 | -0.0090769 | 0.022393 | -0.0031241 | -0.0092389 | 0.010997 | -0.013659 | 0.0084367 | 0.019661 | 0.075561 | 0.028861 | 0.0044439 | 0.065145 | 0.010564 | 0.032795 | 0.13912 | 0.078201 | 0.31595 | 0.023942 | 0.069728 | 0.036989 | -0.001407 | 0.089087 | 0.19685 | -0.11129 | -0.16873 | 122.5535 | 0.038409 | 122.5947 | 122.5624 | 0.008853 | -0.022507 | 0.21524 | 122.3609 | -0.011621 | 122.5993 | 122.5282 | 0.16732 | 0.096143 | -0.212 | 122.6687 | 122.6078 | 122.8456 | 122.5402 | -0.076766 | 122.6187 | 122.7265 | 122.4183 | 122.5666 | -0.26944
2404.9531 | 122.7539 | -122.5616 | 0.11902 | 1.4211e-13 | -0.0090769 | 0.021966 | -0.0033377 | -0.0092389 | 0.010997 | 0.0016025 | 0.0086503 | 0.019447 | 0.075347 | 0.028647 | 0.0046577 | 0.060567 | 0.005985 | 0.023639 | 0.13454 | 0.073622 | 0.31137 | 0.023942 | 0.060571 | 0.023253 | 0.003172 | 0.089087 | 0.19227 | -0.12045 | -0.17331 | 122.5856 | 0.01552 | 122.6222 | 122.5853 | -0.000303 | -0.045397 | 0.19235 | 122.3883 | -0.029932 | 122.6222 | 122.5648 | 0.17648 | 0.073253 | -0.23947 | 122.6962 | 122.6353 | 122.873 | 122.5676 | -0.095077 | 122.6507 | 122.7539 | 122.4412 | 122.5849 | -0.29233
2407.1719 | 122.8134 | -122.525 | 0.091553 | 1.4211e-13 | -0.0086495 | 0.021966 | -0.0033377 | -0.0092389 | 0.01057 | 0.0016025 | 0.0086503 | 0.019447 | 0.075988 | 0.029075 | 0.0050849 | 0.065145 | 0.015142 | 0.028217 | 0.13912 | 0.073622 | 0.31595 | 0.023942 | 0.06515 | 0.027831 | -0.001407 | 0.093665 | 0.19227 | -0.11587 | -0.16873 | 122.549 | 0.047564 | 122.5902 | 122.5532 | 0.004275 | -0.017931 | 0.2244 | 122.3563 | 0.002112 | 122.5902 | 122.5236 | 0.16732 | 0.10072 | -0.20742 | 122.6641 | 122.5986 | 122.841 | 122.5402 | -0.067611 | 122.6187 | 122.7173 | 122.4092 | 122.5529 | -0.26028
2409.8125 | 122.8592 | -122.5067 | 0.11444 | 1.4211e-13 | -0.0088631 | 0.02218 | -0.0033377 | -0.0096661 | 0.010784 | -0.006028 | 0.0084367 | 0.019875 | 0.075347 | 0.029075 | 0.0048713 | 0.069723 | 0.010564 | 0.032795 | 0.13912 | 0.073622 | 0.31595 | 0.023942 | 0.060571 | 0.03241 | 0.007751 | 0.089087 | 0.19227 | -0.11129 | -0.16415 | 122.5307 | 0.024676 | 122.5764 | 122.5395 | 0.008853 | -0.040819 | 0.20151 | 122.3426 | -0.025354 | 122.5673 | 122.5145 | 0.1719 | 0.077831 | -0.22573 | 122.6458 | 122.5803 | 122.8227 | 122.5173 | -0.090499 | 122.5958 | 122.699 | 122.3954 | 122.5391 | -0.27859
2412.8906 | 122.7585 | -122.5662 | 0.11444 | 1.4211e-13 | -0.0092905 | 0.022393 | -0.0033377 | -0.0092389 | 0.010784 | 0.0016025 | 0.0084367 | 0.019661 | 0.075561 | 0.028861 | 0.0048713 | 0.065145 | 0.010564 | 0.023639 | 0.13454 | 0.078201 | 0.31595 | 0.023942 | 0.06515 | 0.03241 | 0.003172 | 0.093665 | 0.19227 | -0.11587 | -0.16415 | 122.5902 | 0.020098 | 122.6314 | 122.5899 | -0.000303 | -0.03624 | 0.20151 | 122.4021 | -0.020776 | 122.6314 | 122.5694 | 0.16732 | 0.077831 | -0.23031 | 122.7008 | 122.6444 | 122.8822 | 122.5768 | -0.090499 | 122.6599 | 122.7585 | 122.4504 | 122.5986 | -0.27859
2414.6875 | 122.7173 | -122.5708 | 0.13275 | 1.4211e-13 | -0.0092905 | 0.02218 | -0.0033377 | -0.0096661 | 0.01057 | 0.0016025 | 0.0086503 | 0.019447 | 0.075347 | 0.028647 | 0.0048713 | 0.060567 | 0.010564 | 0.028217 | 0.13454 | 0.078201 | 0.32053 | 0.023942 | 0.069728 | 0.027831 | -0.001407 | 0.093665 | 0.19227 | -0.12045 | -0.17788 | 122.5947 | 0.001788 | 122.6314 | 122.599 | 0.004275 | -0.05455 | 0.18778 | 122.3929 | -0.039086 | 122.6405 | 122.5694 | 0.17648 | 0.059521 | -0.2532 | 122.7053 | 122.649 | 122.8913 | 122.5814 | -0.10881 | 122.6645 | 122.7631 | 122.4504 | 122.5986 | -0.31064
2416.4844 | 122.731 | -122.5708 | 0.11902 | 1.4211e-13 | -0.0088631 | 0.021966 | -0.0033377 | -0.0092389 | 0.010997 | -0.006028 | 0.0090775 | 0.019234 | 0.075134 | 0.029075 | 0.0048713 | 0.060567 | 0.010564 | 0.01906 | 0.13454 | 0.073622 | 0.32053 | 0.028521 | 0.06515 | 0.027831 | -0.005985 | 0.089087 | 0.19227 | -0.11587 | -0.17331 | 122.5993 | 0.01552 | 122.6314 | 122.5899 | -0.009461 | -0.045397 | 0.20151 | 122.3975 | -0.029932 | 122.636 | 122.5648 | 0.16732 | 0.073253 | -0.23489 | 122.7053 | 122.6444 | 122.8913 | 122.5814 | -0.090498 | 122.6599 | 122.7631 | 122.4549 | 122.5986 | -0.29233
2418.25 | 122.7676 | -122.5571 | 0.11902 | 1.4211e-13 | -0.0088631 | 0.022393 | -0.0033377 | -0.0092389 | 0.010997 | -0.006028 | 0.0086503 | 0.019447 | 0.075775 | 0.029075 | 0.0048713 | 0.055988 | 0.015142 | 0.023639 | 0.12996 | 0.069043 | 0.31595 | 0.023942 | 0.060571 | 0.027831 | -0.005985 | 0.089087 | 0.19227 | -0.11587 | -0.17788 | 122.581 | 0.010941 | 122.6131 | 122.5807 | -0.000303 | -0.049976 | 0.19693 | 122.3792 | -0.029932 | 122.6176 | 122.5511 | 0.1719 | 0.073253 | -0.23489 | 122.687 | 122.6261 | 122.873 | 122.5722 | -0.095077 | 122.6462 | 122.7493 | 122.4412 | 122.5849 | -0.2969
2420.0312 | 122.7036 | -122.5708 | 0.13275 | 1.4211e-13 | -0.0086495 | 0.022393 | -0.0033377 | -0.0094525 | 0.010784 | -0.013659 | 0.0084367 | 0.019234 | 0.075561 | 0.028647 | 0.0048713 | 0.060567 | 0.015142 | 0.028217 | 0.13454 | 0.041569 | 0.31137 | 0.019363 | 0.060571 | 0.027831 | -0.005985 | 0.084508 | 0.19685 | -0.12045 | -0.16873 | 122.5902 | 0.001788 | 122.6314 | 122.599 | 0.008854 | -0.091182 | 0.17862 | 122.4021 | -0.048243 | 122.6314 | 122.5648 | 0.16274 | 0.0641 | -0.2532 | 122.7053 | 122.6124 | 122.8822 | 122.5859 | -0.11339 | 122.6553 | 122.7677 | 122.4504 | 122.5986 | -0.30148
2421.7188 | 122.699 | -122.5845 | 0.12817 | 1.4211e-13 | -0.0088631 | 0.021752 | -0.0037651 | -0.0096661 | 0.010784 | -0.013659 | 0.0086503 | 0.019234 | 0.075775 | 0.028861 | 0.0046577 | 0.060567 | 0.015142 | 0.028217 | 0.13454 | 0.08278 | 0.31137 | 0.023942 | 0.06515 | 0.023253 | -0.001407 | 0.089087 | 0.20143 | -0.11587 | -0.16415 | 122.6085 | 0.006365 | 122.6451 | 122.6128 | 0.004275 | -0.045394 | 0.1832 | 122.4204 | -0.039087 | 122.6497 | 122.5831 | 0.16274 | 0.073255 | -0.24405 | 122.7191 | 122.6673 | 122.8959 | 122.5997 | -0.10423 | 122.6736 | 122.786 | 122.4687 | 122.6078 | -0.29232
2423.4688 | 122.731 | -122.5845 | 0.12817 | 1.4211e-13 | -0.0092905 | 0.02218 | -0.0031241 | -0.0092389 | 0.010997 | -0.013659 | 0.0088639 | 0.019661 | 0.075561 | 0.028861 | 0.0048713 | 0.065145 | 0.005985 | 0.023639 | 0.13454 | 0.073622 | 0.31595 | 0.019363 | 0.055992 | 0.018674 | -0.005985 | 0.075351 | 0.18769 | -0.12503 | -0.18246 | 122.6039 | 0.006365 | 122.6497 | 122.6082 | 0.004276 | -0.054552 | 0.18778 | 122.4021 | -0.052823 | 122.6405 | 122.5785 | 0.17648 | 0.059519 | -0.2532 | 122.7191 | 122.6582 | 122.9005 | 122.5905 | -0.10881 | 122.6599 | 122.7722 | 122.4595 | 122.6032 | -0.31064
2425.25 | 122.8592 | -122.5433 | 0.086975 | 1.4211e-13 | -0.0088631 | 0.021966 | -0.0031241 | -0.0092389 | 0.01057 | -0.006028 | 0.0086503 | 0.019447 | 0.075347 | 0.028861 | 0.0048713 | 0.065145 | 0.010564 | 0.028217 | 0.12996 | 0.078201 | 0.31137 | 0.023942 | 0.060571 | 0.018674 | -0.010564 | 0.07993 | 0.18311 | -0.11587 | -0.18246 | 122.5673 | 0.042985 | 122.6085 | 122.5716 | 0.004275 | -0.008774 | 0.2244 | 122.3609 | -0.007045 | 122.6039 | 122.5328 | 0.1719 | 0.09614 | -0.20285 | 122.6733 | 122.6215 | 122.8547 | 122.5539 | -0.063033 | 122.6233 | 122.7264 | 122.4275 | 122.562 | -0.26944
2427.0156 | 122.7951 | -122.5708 | 0.10986 | 1.4211e-13 | -0.0088631 | 0.022393 | -0.0033377 | -0.0096661 | 0.010784 | 0.0092325 | 0.0086503 | 0.019447 | 0.075347 | 0.028861 | 0.0046577 | 0.060567 | 0.005985 | 0.023639 | 0.13912 | 0.073622 | 0.31137 | 0.019363 | 0.060571 | 0.014095 | -0.005985 | 0.07993 | 0.18769 | -0.12045 | -0.18704 | 122.5902 | 0.029254 | 122.6314 | 122.5944 | 0.004276 | -0.036241 | 0.20151 | 122.3838 | -0.029933 | 122.6314 | 122.5648 | 0.18106 | 0.07783 | -0.23031 | 122.7099 | 122.6444 | 122.8822 | 122.5768 | -0.0905 | 122.6507 | 122.7585 | 122.4504 | 122.5849 | -0.29691
2428.7031 | 122.8455 | -122.58 | 0.082397 | 1.4211e-13 | -0.0090769 | 0.02218 | -0.0033377 | -0.0096661 | 0.010356 | 0.0016025 | 0.0084367 | 0.019447 | 0.075561 | 0.028861 | 0.0046577 | 0.060567 | 0.015142 | 0.028217 | 0.13912 | 0.073622 | 0.31137 | 0.019363 | 0.051413 | 0.014095 | -0.015143 | 0.089087 | 0.18769 | -0.12045 | -0.17788 | 122.5993 | 0.05672 | 122.6405 | 122.6082 | 0.008854 | -0.008775 | 0.22898 | 122.4021 | 0.00669 | 122.6314 | 122.5648 | 0.16274 | 0.1053 | -0.20285 | 122.7191 | 122.6536 | 122.8913 | 122.5951 | -0.063034 | 122.669 | 122.7676 | 122.4595 | 122.5941 | -0.26028
2430.4531 | 122.7081 | -122.5891 | 0.14191 | 1.4211e-13 | -0.0088631 | 0.022393 | -0.0031241 | -0.0094525 | 0.010784 | 0.0016025 | 0.0086503 | 0.019234 | 0.075775 | 0.028647 | 0.0046577 | 0.060567 | 0.015142 | 0.028217 | 0.13454 | 0.08278 | 0.31137 | 0.019363 | 0.046835 | 0.014095 | -0.010564 | 0.084508 | 0.18311 | -0.11587 | -0.18246 | 122.6085 | -0.007368 | 122.6497 | 122.6173 | 0.008854 | -0.059127 | 0.16947 | 122.4066 | -0.057399 | 122.6359 | 122.5785 | 0.1719 | 0.041208 | -0.25778 | 122.7237 | 122.6719 | 122.9005 | 122.6043 | -0.12254 | 122.6736 | 122.7722 | 122.4732 | 122.6032 | -0.32437
2432.2344 | 122.6944 | -122.6028 | 0.11444 | 1.4211e-13 | -0.0086495 | 0.02218 | -0.0037651 | -0.0094525 | 0.010997 | -0.013659 | 0.0086503 | 0.019447 | 0.075775 | 0.028647 | 0.0048713 | 0.065145 | 0.019721 | 0.023639 | 0.13912 | 0.064464 | 0.31595 | 0.019363 | 0.051413 | 0.018674 | -0.005985 | 0.075351 | 0.18311 | -0.11587 | -0.17788 | 122.6222 | 0.024676 | 122.668 | 122.6265 | 0.004276 | -0.049977 | 0.20151 | 122.425 | -0.03909 | 122.6543 | 122.5969 | 0.1719 | 0.068674 | -0.23031 | 122.742 | 122.6673 | 122.9188 | 122.6226 | -0.095078 | 122.6782 | 122.786 | 122.487 | 122.6215 | -0.29233
2434 | 122.7081 | -122.6028 | 0.11902 | 1.4211e-13 | -0.0088631 | 0.022393 | -0.0035515 | -0.0096661 | 0.010997 | -0.013659 | 0.0088639 | 0.019234 | 0.076202 | 0.029075 | 0.0048713 | 0.069723 | 0.010564 | 0.028217 | 0.13454 | 0.078201 | 0.31595 | 0.023942 | 0.051413 | 0.014095 | -0.015143 | 0.084508 | 0.18311 | -0.11587 | -0.17788 | 122.6268 | 0.01552 | 122.6726 | 122.6311 | 0.004275 | -0.040818 | 0.19693 | 122.425 | -0.034511 | 122.6543 | 122.5877 | 0.16274 | 0.064096 | -0.23489 | 122.7374 | 122.681 | 122.9188 | 122.6134 | -0.095077 | 122.6874 | 122.786 | 122.487 | 122.6169 | -0.2969
2435.7031 | 122.7997 | -122.5983 | 0.10071 | 1.4211e-13 | -0.0088631 | 0.021966 | -0.0035515 | -0.0092389 | 0.010997 | -0.006028 | 0.0086503 | 0.019234 | 0.075775 | 0.028861 | 0.0048713 | 0.055988 | 0.010564 | 0.023639 | 0.13454 | 0.073622 | 0.31595 | 0.028521 | 0.055992 | 0.018674 | -0.019721 | 0.084508 | 0.18311 | -0.12045 | -0.18246 | 122.6268 | 0.033831 | 122.6543 | 122.6219 | -0.004882 | -0.027086 | 0.21524 | 122.4158 | -0.0162 | 122.6543 | 122.5785 | 0.16274 | 0.082407 | -0.22116 | 122.7328 | 122.6719 | 122.9142 | 122.6088 | -0.072187 | 122.6828 | 122.7814 | 122.4778 | 122.6169 | -0.28317
2437.4688 | 122.8271 | -122.5754 | 0.073242 | 1.4211e-13 | -0.0086495 | 0.022607 | -0.0035515 | -0.0096661 | 0.01057 | -0.006028 | 0.0088639 | 0.019234 | 0.075561 | 0.028647 | 0.0044439 | 0.065145 | 0.010564 | 0.028217 | 0.12996 | 0.078201 | 0.32053 | 0.023942 | 0.051413 | 0.023253 | -0.015143 | 0.07993 | 0.17854 | -0.12045 | -0.18246 | 122.5993 | 0.056718 | 122.6405 | 122.6036 | 0.004275 | 0.004959 | 0.24729 | 122.3929 | 0.006688 | 122.6268 | 122.5602 | 0.16732 | 0.10529 | -0.19369 | 122.7053 | 122.6536 | 122.8959 | 122.5859 | -0.0493 | 122.6553 | 122.7539 | 122.4549 | 122.5986 | -0.25571
2439.2344 | 122.7585 | -122.6074 | 0.11902 | 1.4211e-13 | -0.0088631 | 0.021966 | -0.0035515 | -0.0094525 | 0.010784 | -0.006028 | 0.0084367 | 0.019447 | 0.075561 | 0.029075 | 0.0048713 | 0.065145 | 0.010564 | 0.028217 | 0.13454 | 0.073622 | 0.31595 | 0.019363 | 0.055992 | 0.004938 | -0.015143 | 0.075351 | 0.17396 | -0.12503 | -0.18246 | 122.6268 | 0.01552 | 122.6726 | 122.6356 | 0.008854 | -0.045397 | 0.19693 | 122.425 | -0.043668 | 122.6634 | 122.5923 | 0.16732 | 0.054939 | -0.24405 | 122.742 | 122.681 | 122.9234 | 122.618 | -0.099656 | 122.6828 | 122.7814 | 122.4824 | 122.6124 | -0.30148
2440.9219 | 122.8729 | -122.5708 | 0.091553 | 1.4211e-13 | -0.0086495 | 0.022393 | -0.0033377 | -0.0096661 | 0.010784 | 0.0016025 | 0.0086503 | 0.019661 | 0.075561 | 0.028647 | 0.0048713 | 0.065145 | 0.015142 | 0.037373 | 0.13454 | 0.078201 | 0.31137 | 0.019363 | 0.060571 | 0.014095 | -0.019721 | 0.07993 | 0.18311 | -0.12045 | -0.18704 | 122.5902 | 0.042986 | 122.6359 | 122.6082 | 0.01801 | -0.013352 | 0.21982 | 122.3838 | -0.011623 | 122.6314 | 122.5511 | 0.16732 | 0.091562 | -0.212 | 122.7053 | 122.649 | 122.8822 | 122.5859 | -0.07219 | 122.6507 | 122.7539 | 122.4504 | 122.5849 | -0.2786
2442.6719 | 122.7585 | -122.5891 | 0.1236 | 1.4211e-13 | -0.0088631 | 0.022607 | -0.0035515 | -0.0092389 | 0.010997 | -0.006028 | 0.0086503 | 0.019234 | 0.075988 | 0.028861 | 0.0048713 | 0.065145 | 0.005985 | 0.037373 | 0.13454 | 0.073622 | 0.31595 | 0.019363 | 0.051413 | 0.023253 | -0.019721 | 0.07993 | 0.17396 | -0.11587 | -0.17788 | 122.6085 | 0.010943 | 122.6543 | 122.6265 | 0.01801 | -0.049974 | 0.19236 | 122.4112 | -0.043666 | 122.6405 | 122.5694 | 0.15816 | 0.050362 | -0.23947 | 122.7237 | 122.6627 | 122.9051 | 122.5951 | -0.10423 | 122.669 | 122.7631 | 122.4732 | 122.6124 | -0.30148
2444.4531 | 122.8409 | -122.5845 | 0.10071 | 1.4211e-13 | -0.0088631 | 0.021966 | -0.0033377 | -0.0096661 | 0.010784 | 0.0016025 | 0.0086503 | 0.019234 | 0.075561 | 0.029075 | 0.0048713 | 0.060567 | 0.010564 | 0.028217 | 0.12996 | 0.069043 | 0.32053 | 0.014784 | 0.055992 | 0.014095 | -0.005985 | 0.07993 | 0.18311 | -0.11587 | -0.18246 | 122.5993 | 0.029252 | 122.6451 | 122.6128 | 0.013433 | -0.031665 | 0.21982 | 122.4021 | -0.020778 | 122.6405 | 122.5785 | 0.17648 | 0.082407 | -0.21658 | 122.7145 | 122.6536 | 122.9051 | 122.5951 | -0.085924 | 122.6645 | 122.7676 | 122.4687 | 122.5986 | -0.28317
2446.2344 | 122.8134 | -122.5937 | 0.091553 | 1.4211e-13 | -0.0088631 | 0.021966 | -0.0033377 | -0.0096661 | 0.010997 | 0.0016025 | 0.0082229 | 0.019447 | 0.075561 | 0.028861 | 0.0048713 | 0.074302 | 0.019721 | 0.028217 | 0.13454 | 0.069043 | 0.32511 | 0.023942 | 0.055992 | 0.014095 | -0.010564 | 0.07993 | 0.18311 | -0.12503 | -0.18246 | 122.6176 | 0.042986 | 122.668 | 122.6219 | 0.004275 | -0.02251 | 0.23356 | 122.4112 | -0.011623 | 122.6497 | 122.5831 | 0.1719 | 0.091562 | -0.21658 | 122.7282 | 122.6627 | 122.9188 | 122.6134 | -0.067611 | 122.6736 | 122.7768 | 122.4687 | 122.6078 | -0.27402
2447.9375 | 122.7997 | -122.5937 | 0.11444 | 1.4211e-13 | -0.0090769 | 0.02218 | -0.0031241 | -0.0092389 | 0.010784 | -0.013659 | 0.0086503 | 0.019661 | 0.075561 | 0.028861 | 0.0046577 | 0.065145 | 0.010564 | 0.01906 | 0.12996 | 0.073622 | 0.31595 | 0.019363 | 0.055992 | 0.004938 | -0.015143 | 0.070773 | 0.18311 | -0.12045 | -0.18246 | 122.6131 | 0.015519 | 122.6588 | 122.6127 | -0.000303 | -0.040819 | 0.20151 | 122.4112 | -0.043668 | 122.6497 | 122.5785 | 0.16732 | 0.068674 | -0.23489 | 122.7236 | 122.6673 | 122.9096 | 122.6043 | -0.095078 | 122.6645 | 122.7768 | 122.4732 | 122.5986 | -0.2969
2449.625 | 122.818 | -122.5754 | 0.10529 | 1.4211e-13 | -0.0090769 | 0.02218 | -0.0033377 | -0.0094525 | 0.010356 | 0.0016025 | 0.0088639 | 0.019234 | 0.075775 | 0.029075 | 0.0046577 | 0.065145 | 0.015142 | 0.028217 | 0.13454 | 0.08278 | 0.31137 | 0.019363 | 0.051413 | 0.014095 | -0.010564 | 0.075351 | 0.17854 | -0.12045 | -0.18704 | 122.5947 | 0.029253 | 122.6405 | 122.6036 | 0.008854 | -0.022506 | 0.20609 | 122.3883 | -0.029935 | 122.6268 | 122.5648 | 0.17648 | 0.07325 | -0.22574 | 122.7099 | 122.6582 | 122.8868 | 122.5905 | -0.085923 | 122.6507 | 122.7539 | 122.4549 | 122.5895 | -0.29233
2451.3906 | 122.8592 | -122.5845 | 0.10986 | 1.4211e-13 | -0.0088631 | 0.02218 | -0.0033377 | -0.0092389 | 0.010997 | -0.006028 | 0.0086503 | 0.019447 | 0.075561 | 0.028647 | 0.0050849 | 0.060567 | 0.010564 | 0.023639 | 0.12996 | 0.078201 | 0.3068 | 0.028521 | 0.055992 | 0.014095 | -0.015143 | 0.07993 | 0.18311 | -0.11129 | -0.18704 | 122.6131 | 0.020097 | 122.6451 | 122.6082 | -0.004882 | -0.031662 | 0.19693 | 122.3975 | -0.029933 | 122.6405 | 122.5694 | 0.1719 | 0.073252 | -0.22116 | 122.7145 | 122.6627 | 122.8913 | 122.5951 | -0.081342 | 122.6645 | 122.7676 | 122.4732 | 122.5986 | -0.29691
2453.1562 | 122.8363 | -122.6074 | 0.10529 | 1.4211e-13 | -0.0088631 | 0.02218 | -0.0035515 | -0.0094525 | 0.010356 | 0.0016025 | 0.0086503 | 0.019234 | 0.075561 | 0.028861 | 0.0046577 | 0.065145 | 0.010564 | 0.028217 | 0.13454 | 0.073622 | 0.31137 | 0.014784 | 0.051413 | 0.014095 | -0.015143 | 0.075351 | 0.17854 | -0.12045 | -0.17788 | 122.6222 | 0.029253 | 122.6726 | 122.6356 | 0.013433 | -0.031664 | 0.20609 | 122.4295 | -0.029935 | 122.6588 | 122.5923 | 0.16274 | 0.07325 | -0.22574 | 122.742 | 122.681 | 122.9188 | 122.618 | -0.090502 | 122.6828 | 122.786 | 122.487 | 122.6215 | -0.28317
2454.8438 | 122.8409 | -122.5754 | 0.10071 | 1.4211e-13 | -0.0088631 | 0.02218 | -0.0033377 | -0.0098799 | 0.010997 | 0.0016025 | 0.0086503 | 0.019234 | 0.075347 | 0.028861 | 0.0046577 | 0.069723 | 0.015142 | 0.028217 | 0.14369 | 0.078201 | 0.31595 | 0.014784 | 0.051413 | 0.014095 | -0.0243 | 0.075351 | 0.18311 | -0.12503 | -0.17788 | 122.5902 | 0.042987 | 122.6451 | 122.6036 | 0.013433 | -0.022507 | 0.21524 | 122.3975 | -0.025357 | 122.6268 | 122.5511 | 0.15358 | 0.082407 | -0.22574 | 122.7191 | 122.6536 | 122.8913 | 122.5905 | -0.085924 | 122.6507 | 122.7585 | 122.4503 | 122.5895 | -0.27859
2456.5469 | 122.8455 | -122.5845 | 0.10071 | 1.4211e-13 | -0.0086495 | 0.02218 | -0.0033377 | -0.0092389 | 0.010997 | -0.006028 | 0.0084367 | 0.019447 | 0.075775 | 0.028861 | 0.0046577 | 0.069723 | 0.010564 | 0.028217 | 0.13454 | 0.078201 | 0.31137 | 0.023942 | 0.055992 | 0.014095 | -0.015143 | 0.075351 | 0.18311 | -0.11587 | -0.18246 | 122.6085 | 0.033831 | 122.6543 | 122.6128 | 0.004275 | -0.022507 | 0.21067 | 122.4021 | -0.025357 | 122.6405 | 122.5694 | 0.16732 | 0.082407 | -0.21658 | 122.7191 | 122.6627 | 122.8959 | 122.5951 | -0.076766 | 122.6599 | 122.7676 | 122.4687 | 122.5986 | -0.28317
2458.3125 | 122.7676 | -122.6303 | 0.10986 | 1.4211e-13 | -0.0090769 | 0.02218 | -0.0035515 | -0.0094525 | 0.010784 | -0.006028 | 0.0088639 | 0.019234 | 0.075561 | 0.029288 | 0.0044439 | 0.069723 | 0.015142 | 0.01906 | 0.13454 | 0.08278 | 0.31137 | 0.023942 | 0.060571 | 0.018674 | -0.010564 | 0.084508 | 0.19227 | -0.12045 | -0.17331 | 122.6543 | 0.024676 | 122.7 | 122.6494 | -0.004882 | -0.027083 | 0.20151 | 122.457 | -0.025355 | 122.6909 | 122.6197 | 0.16274 | 0.082409 | -0.23031 | 122.7648 | 122.7131 | 122.9417 | 122.6455 | -0.085921 | 122.7148 | 122.8226 | 122.5099 | 122.649 | -0.28317
2460 | 122.7585 | -122.612 | 0.1236 | 1.4211e-13 | -0.0088631 | 0.022607 | -0.0035515 | -0.0090251 | 0.010784 | 0.0016025 | 0.0088639 | 0.019234 | 0.075775 | 0.029075 | 0.0046577 | 0.060567 | 0.015142 | 0.023639 | 0.13912 | 0.078201 | 0.31137 | 0.019363 | 0.069728 | 0.023253 | 0.003172 | 0.07993 | 0.18769 | -0.10671 | -0.16873 | 122.6314 | 0.015521 | 122.6726 | 122.6356 | 0.004276 | -0.045395 | 0.18778 | 122.4433 | -0.043666 | 122.6817 | 122.6152 | 0.1719 | 0.064097 | -0.23031 | 122.7511 | 122.6902 | 122.9234 | 122.6271 | -0.10423 | 122.6919 | 122.7997 | 122.5053 | 122.6353 | -0.29232
2461.6875 | 122.7493 | -122.612 | 0.11444 | 1.4211e-13 | -0.0086495 | 0.02218 | -0.0033377 | -0.0092389 | 0.01057 | -0.013659 | 0.0088639 | 0.019447 | 0.075561 | 0.029075 | 0.0046577 | 0.060567 | 0.005985 | 0.023639 | 0.13454 | 0.069043 | 0.31595 | 0.019363 | 0.06515 | 0.018674 | -0.010564 | 0.089087 | 0.19685 | -0.11587 | -0.17788 | 122.6314 | 0.020098 | 122.6726 | 122.6356 | 0.004276 | -0.045398 | 0.20151 | 122.4341 | -0.025354 | 122.6771 | 122.6014 | 0.16732 | 0.08241 | -0.23031 | 122.7465 | 122.681 | 122.928 | 122.618 | -0.095078 | 122.7011 | 122.8089 | 122.4961 | 122.6307 | -0.29233
2463.4531 | 122.8088 | -122.6028 | 0.12817 | 1.4211e-13 | -0.0088631 | 0.022393 | -0.0035515 | -0.0092389 | 0.01057 | -0.013659 | 0.0086503 | 0.019447 | 0.075347 | 0.028647 | 0.0044439 | 0.060567 | 0.010564 | 0.028217 | 0.13454 | 0.08278 | 0.31595 | 0.019363 | 0.06515 | 0.023253 | -0.010564 | 0.084508 | 0.19227 | -0.12503 | -0.17331 | 122.6222 | 0.006365 | 122.6634 | 122.6311 | 0.008854 | -0.045394 | 0.18778 | 122.4295 | -0.043666 | 122.668 | 122.5923 | 0.16274 | 0.064098 | -0.2532 | 122.7374 | 122.6856 | 122.9188 | 122.6134 | -0.10881 | 122.6874 | 122.7951 | 122.4778 | 122.6261 | -0.30148
2465.1719 | 122.7814 | -122.6303 | 0.13275 | 1.4211e-13 | -0.0090769 | 0.021752 | -0.0033377 | -0.0096661 | 0.010997 | 0.0092325 | 0.0088639 | 0.019234 | 0.075775 | 0.028861 | 0.0046577 | 0.046831 | 0.005985 | 0.023639 | 0.12996 | 0.078201 | 0.32053 | 0.028521 | 0.060571 | 0.027831 | -0.005985 | 0.089087 | 0.19227 | -0.10671 | -0.17331 | 122.6588 | -0.002791 | 122.6771 | 122.6539 | -0.004882 | -0.05455 | 0.18778 | 122.457 | -0.043664 | 122.6909 | 122.6243 | 0.16732 | 0.059521 | -0.23947 | 122.7603 | 122.7085 | 122.9508 | 122.6363 | -0.10423 | 122.7194 | 122.8226 | 122.5236 | 122.6581 | -0.30606
2466.9531 | 122.7585 | -122.6532 | 0.13733 | 1.4211e-13 | -0.0090769 | 0.021966 | -0.0031241 | -0.0092389 | 0.01057 | -0.006028 | 0.0086503 | 0.019447 | 0.075561 | 0.029075 | 0.0048713 | 0.065145 | 0.015142 | 0.014482 | 0.12996 | 0.073622 | 0.31595 | 0.019363 | 0.060571 | 0.023253 | -0.001407 | 0.084508 | 0.19685 | -0.12045 | -0.16873 | 122.6726 | -0.007369 | 122.7183 | 122.6677 | -0.004881 | -0.063707 | 0.17862 | 122.4845 | -0.052821 | 122.7138 | 122.6518 | 0.16732 | 0.059522 | -0.25778 | 122.7832 | 122.7268 | 122.9692 | 122.6683 | -0.11797 | 122.7377 | 122.85 | 122.5327 | 122.6765 | -0.30606
2468.7031 | 122.8088 | -122.6212 | 0.11444 | 1.4211e-13 | -0.0086495 | 0.021966 | -0.0033377 | -0.0094525 | 0.010784 | -0.006028 | 0.0086503 | 0.019234 | 0.075347 | 0.028861 | 0.0048713 | 0.060567 | 0.015142 | 0.01906 | 0.13912 | 0.08278 | 0.32053 | 0.028521 | 0.060571 | 0.023253 | -0.001407 | 0.089087 | 0.19227 | -0.11129 | -0.17788 | 122.6497 | 0.024676 | 122.6817 | 122.6402 | -0.009461 | -0.031661 | 0.20609 | 122.4433 | -0.025354 | 122.6817 | 122.6197 | 0.17648 | 0.077831 | -0.22573 | 122.7603 | 122.7039 | 122.9417 | 122.6363 | -0.08592 | 122.7102 | 122.8134 | 122.5099 | 122.6444 | -0.29233
2470.4844 | 122.8134 | -122.6212 | 0.11444 | 1.4211e-13 | -0.0088631 | 0.02218 | -0.0033377 | -0.0094525 | 0.010784 | 0.0016025 | 0.0088639 | 0.019447 | 0.075561 | 0.029288 | 0.0046577 | 0.060567 | 0.010564 | 0.023639 | 0.13912 | 0.08278 | 0.3068 | 0.019363 | 0.06515 | 0.023253 | -0.010564 | 0.089087 | 0.17854 | -0.11587 | -0.16415 | 122.6405 | 0.024676 | 122.6817 | 122.6448 | 0.004276 | -0.031661 | 0.19235 | 122.457 | -0.025354 | 122.6863 | 122.6106 | 0.15358 | 0.064095 | -0.23031 | 122.7603 | 122.7039 | 122.928 | 122.6317 | -0.095078 | 122.7102 | 122.7997 | 122.5053 | 122.6444 | -0.27859
2472.2656 | 122.818 | -122.6486 | 0.1236 | 1.4211e-13 | -0.0088631 | 0.02218 | -0.0033377 | -0.0096661 | 0.011425 | -0.006028 | 0.0086503 | 0.019447 | 0.075561 | 0.028861 | 0.0044439 | 0.055988 | 0.005985 | 0.01906 | 0.13454 | 0.078201 | 0.32511 | 0.014784 | 0.06515 | 0.023253 | 0.003172 | 0.089087 | 0.19227 | -0.11587 | -0.16873 | 122.6634 | 0.010943 | 122.7046 | 122.6677 | 0.004276 | -0.045395 | 0.20151 | 122.4799 | -0.034509 | 122.7138 | 122.6518 | 0.1719 | 0.068676 | -0.23947 | 122.7832 | 122.7268 | 122.9737 | 122.6546 | -0.10881 | 122.7377 | 122.8409 | 122.5327 | 122.6719 | -0.29232
2473.9688 | 122.8729 | -122.5983 | 0.09613 | 1.4211e-13 | -0.0088631 | 0.021966 | -0.0033377 | -0.0096661 | 0.010997 | 0.0016025 | 0.0088639 | 0.019447 | 0.075134 | 0.028861 | 0.0048713 | 0.065145 | 0.010564 | 0.023639 | 0.13454 | 0.078201 | 0.31595 | 0.028521 | 0.06515 | 0.014095 | -0.010564 | 0.084508 | 0.19685 | -0.12045 | -0.17331 | 122.6268 | 0.038409 | 122.6634 | 122.6219 | -0.004882 | -0.017929 | 0.21982 | 122.425 | -0.011622 | 122.6634 | 122.5877 | 0.16274 | 0.10072 | -0.21658 | 122.7328 | 122.6765 | 122.9142 | 122.6088 | -0.067609 | 122.6828 | 122.7951 | 122.4778 | 122.6124 | -0.26944
2475.7188 | 122.7859 | -122.6624 | 0.1236 | 1.4211e-13 | -0.0086495 | 0.02218 | -0.0031241 | -0.0092389 | 0.010997 | 0.0016025 | 0.0090775 | 0.019234 | 0.075561 | 0.029075 | 0.0044439 | 0.055988 | 0.005985 | 0.023639 | 0.12996 | 0.073622 | 0.31595 | 0.023942 | 0.06515 | 0.018674 | -0.001407 | 0.084508 | 0.19685 | -0.12045 | -0.16873 | 122.6863 | 0.006364 | 122.7183 | 122.686 | -0.000303 | -0.049974 | 0.19236 | 122.4936 | -0.039088 | 122.7275 | 122.6609 | 0.16732 | 0.073255 | -0.24405 | 122.7923 | 122.736 | 122.9783 | 122.6683 | -0.099654 | 122.7469 | 122.8592 | 122.5419 | 122.681 | -0.29232
2477.5 | 122.8134 | -122.6486 | 0.12817 | 1.4211e-13 | -0.0092905 | 0.021752 | -0.0033377 | -0.0094525 | 0.010784 | 0.0092325 | 0.0086503 | 0.019234 | 0.075561 | 0.029075 | 0.0046577 | 0.060567 | 0.010564 | 0.023639 | 0.13912 | 0.073622 | 0.31137 | 0.037679 | 0.06515 | 0.023253 | -0.001407 | 0.089087 | 0.19685 | -0.11587 | -0.16873 | 122.6863 | 0.010943 | 122.7092 | 122.6723 | -0.01404 | -0.054552 | 0.1832 | 122.4799 | -0.039087 | 122.7138 | 122.6472 | 0.16732 | 0.068677 | -0.24405 | 122.7877 | 122.7222 | 122.96 | 122.6592 | -0.090495 | 122.7377 | 122.8455 | 122.5327 | 122.6719 | -0.2969
2479.2031 | 122.8363 | -122.612 | 0.10529 | 1.4211e-13 | -0.0086495 | 0.02218 | -0.0033377 | -0.0094525 | 0.01057 | -0.006028 | 0.0086503 | 0.019234 | 0.075561 | 0.029288 | 0.0046577 | 0.060567 | 0.010564 | 0.028217 | 0.13912 | 0.073622 | 0.31137 | 0.019363 | 0.069728 | 0.018674 | -0.001407 | 0.084508 | 0.20143 | -0.12045 | -0.17331 | 122.6314 | 0.033831 | 122.6726 | 122.6402 | 0.008854 | -0.031664 | 0.20609 | 122.4387 | -0.020778 | 122.6817 | 122.6106 | 0.1719 | 0.096143 | -0.22574 | 122.7511 | 122.6856 | 122.9234 | 122.6226 | -0.085923 | 122.6965 | 122.8134 | 122.4915 | 122.6307 | -0.27859
2480.9844 | 122.7768 | -122.6807 | 0.1236 | 1.4211e-13 | -0.0088631 | 0.022393 | -0.0031241 | -0.0096661 | 0.011211 | -0.006028 | 0.0090775 | 0.019447 | 0.075347 | 0.029288 | 0.0044439 | 0.065145 | 0.015142 | 0.028217 | 0.13912 | 0.08278 | 0.31595 | 0.028521 | 0.06515 | 0.018674 | -0.001407 | 0.089087 | 0.19685 | -0.12045 | -0.16415 | 122.7092 | 0.015521 | 122.7458 | 122.7089 | -0.000304 | -0.040816 | 0.19236 | 122.5165 | -0.034509 | 122.7458 | 122.6793 | 0.16274 | 0.073255 | -0.24405 | 122.8198 | 122.7634 | 122.9966 | 122.6958 | -0.095075 | 122.7698 | 122.8775 | 122.5602 | 122.6993 | -0.28774
2482.75 | 122.8683 | -122.6166 | 0.10986 | 1.4211e-13 | -0.0088631 | 0.021966 | -0.0033377 | -0.0094525 | 0.010997 | -0.013659 | 0.0088639 | 0.019234 | 0.075775 | 0.028861 | 0.0046577 | 0.055988 | 0.019721 | 0.023639 | 0.13912 | 0.069043 | 0.31137 | 0.019363 | 0.069728 | 0.018674 | -0.001407 | 0.089087 | 0.19685 | -0.11587 | -0.16873 | 122.6359 | 0.029254 | 122.6726 | 122.6402 | 0.004276 | -0.04082 | 0.20151 | 122.4478 | -0.020776 | 122.6863 | 122.6152 | 0.16732 | 0.086988 | -0.22574 | 122.7557 | 122.6856 | 122.928 | 122.6363 | -0.0905 | 122.7057 | 122.8134 | 122.5007 | 122.6353 | -0.27859
2484.5 | 122.9416 | -122.612 | 0.073242 | 1.4211e-13 | -0.0090769 | 0.021966 | -0.0033377 | -0.0090251 | 0.010997 | -0.006028 | 0.0086503 | 0.019234 | 0.075561 | 0.028861 | 0.0046577 | 0.060567 | 0.015142 | 0.023639 | 0.12996 | 0.069043 | 0.31595 | 0.023942 | 0.06515 | 0.018674 | -0.001407 | 0.093665 | 0.19227 | -0.12045 | -0.16873 | 122.6359 | 0.056718 | 122.6726 | 122.6356 | -0.000303 | -0.004199 | 0.24271 | 122.4433 | 0.020423 | 122.6771 | 122.6106 | 0.16732 | 0.11903 | -0.19369 | 122.742 | 122.681 | 122.928 | 122.6271 | -0.0493 | 122.7057 | 122.8043 | 122.4915 | 122.6307 | -0.24197
2486.2031 | 122.7814 | -122.644 | 0.11902 | 1.4211e-13 | -0.0086495 | 0.021752 | -0.0031241 | -0.0092389 | 0.010784 | -0.021289 | 0.0086503 | 0.019234 | 0.075561 | 0.028861 | 0.0048713 | 0.055988 | 0.010564 | 0.028217 | 0.13454 | 0.08278 | 0.31595 | 0.028521 | 0.069728 | 0.018674 | 0.003172 | 0.084508 | 0.19685 | -0.12045 | -0.16873 | 122.6726 | 0.01552 | 122.7 | 122.6723 | -0.000304 | -0.036239 | 0.19693 | 122.4753 | -0.034511 | 122.7138 | 122.6472 | 0.1719 | 0.077832 | -0.23947 | 122.7786 | 122.7268 | 122.96 | 122.6546 | -0.090498 | 122.7286 | 122.8409 | 122.5236 | 122.6627 | -0.28775
2487.9688 | 122.905 | -122.6257 | 0.10071 | 1.4211e-13 | -0.0090769 | 0.02218 | -0.0035515 | -0.0092389 | 0.010784 | 0.0016025 | 0.0086503 | 0.019234 | 0.075347 | 0.029075 | 0.0048713 | 0.060567 | 0.010564 | 0.023639 | 0.14369 | 0.064464 | 0.32053 | 0.019363 | 0.060571 | 0.023253 | -0.001407 | 0.084508 | 0.19227 | -0.12503 | -0.16873 | 122.6451 | 0.042987 | 122.6863 | 122.6494 | 0.004276 | -0.036244 | 0.21982 | 122.457 | -0.0162 | 122.6863 | 122.6243 | 0.16732 | 0.091564 | -0.22574 | 122.7694 | 122.6902 | 122.9463 | 122.6363 | -0.081345 | 122.7102 | 122.818 | 122.5007 | 122.649 | -0.26944
2489.7188 | 122.8867 | -122.644 | 0.10071 | 1.4211e-13 | -0.0092905 | 0.02218 | -0.0033377 | -0.0094525 | 0.011425 | -0.006028 | 0.0086503 | 0.019234 | 0.075561 | 0.029075 | 0.0046577 | 0.065145 | 0.015142 | 0.023639 | 0.12996 | 0.073622 | 0.31137 | 0.019363 | 0.06515 | 0.03241 | -0.001407 | 0.084508 | 0.18769 | -0.11587 | -0.17331 | 122.6634 | 0.029252 | 122.7092 | 122.6677 | 0.004276 | -0.027086 | 0.21067 | 122.4707 | -0.0162 | 122.7092 | 122.6426 | 0.1719 | 0.086985 | -0.21658 | 122.774 | 122.7177 | 122.9554 | 122.6592 | -0.081345 | 122.7286 | 122.8317 | 122.5282 | 122.6765 | -0.27401
2491.4844 | 122.7905 | -122.6486 | 0.13275 | 1.4211e-13 | -0.0090769 | 0.02218 | -0.0035515 | -0.0092389 | 0.010997 | -0.021289 | 0.0084367 | 0.019234 | 0.075561 | 0.029288 | 0.0048713 | 0.060567 | 0.010564 | 0.028217 | 0.12996 | 0.069043 | 0.32053 | 0.028521 | 0.06515 | 0.027831 | 0.003172 | 0.084508 | 0.19685 | -0.11587 | -0.16873 | 122.6771 | -0.002791 | 122.7092 | 122.6768 | -0.000304 | -0.063708 | 0.18778 | 122.4799 | -0.048243 | 122.7138 | 122.6518 | 0.1719 | 0.0641 | -0.24862 | 122.7786 | 122.7177 | 122.9692 | 122.6592 | -0.10423 | 122.7331 | 122.8455 | 122.5327 | 122.6765 | -0.30148
2493.2656 | 122.8592 | -122.6578 | 0.09613 | 1.4211e-13 | -0.0086495 | 0.022393 | -0.0033377 | -0.0092389 | 0.010997 | -0.013659 | 0.0086503 | 0.019234 | 0.075561 | 0.028647 | 0.0046577 | 0.060567 | 0.001407 | 0.032795 | 0.13454 | 0.078201 | 0.31137 | 0.019363 | 0.06515 | 0.018674 | -0.005985 | 0.089087 | 0.19227 | -0.11587 | -0.16873 | 122.6771 | 0.038409 | 122.7183 | 122.6906 | 0.013432 | -0.017929 | 0.21524 | 122.489 | -0.007043 | 122.7229 | 122.6518 | 0.16274 | 0.096142 | -0.212 | 122.7923 | 122.736 | 122.9691 | 122.6592 | -0.076767 | 122.7469 | 122.85 | 122.5419 | 122.6765 | -0.26486
2494.9688 | 122.9324 | -122.5983 | 0.082397 | 1.4211e-13 | -0.0090769 | 0.02218 | -0.0035515 | -0.0092389 | 0.01057 | -0.006028 | 0.0088639 | 0.019875 | 0.075561 | 0.028647 | 0.0046577 | 0.065145 | 0.005985 | 0.023639 | 0.13454 | 0.073622 | 0.32053 | 0.019363 | 0.06515 | 0.027831 | -0.001407 | 0.089087 | 0.20143 | -0.11587 | -0.16873 | 122.6176 | 0.052142 | 122.6634 | 122.6219 | 0.004276 | -0.008775 | 0.23813 | 122.4295 | 0.00669 | 122.6634 | 122.5969 | 0.16732 | 0.11903 | -0.19827 | 122.7328 | 122.6719 | 122.9188 | 122.6043 | -0.063034 | 122.6874 | 122.7997 | 122.4824 | 122.6261 | -0.25112
2496.7188 | 122.8088 | -122.6761 | 0.10529 | 1.4211e-13 | -0.0088631 | 0.021966 | -0.0031241 | -0.0094525 | 0.01057 | -0.006028 | 0.0084367 | 0.019447 | 0.075988 | 0.028861 | 0.0046577 | 0.060567 | 0.010564 | 0.032795 | 0.13454 | 0.069043 | 0.31595 | 0.023942 | 0.069728 | 0.023253 | -0.005985 | 0.07993 | 0.19227 | -0.11587 | -0.16415 | 122.7 | 0.029253 | 122.7367 | 122.7089 | 0.008853 | -0.036243 | 0.21067 | 122.5119 | -0.025356 | 122.7458 | 122.6701 | 0.15816 | 0.086986 | -0.22116 | 122.8106 | 122.7451 | 122.992 | 122.6867 | -0.081344 | 122.756 | 122.8684 | 122.5602 | 122.6993 | -0.26943
2498.4219 | 122.9187 | -122.6166 | 0.091553 | 1.4211e-13 | -0.0090769 | 0.02218 | -0.0031241 | -0.0096661 | 0.01057 | 0.0016025 | 0.0086503 | 0.019661 | 0.075561 | 0.028647 | 0.0046577 | 0.060567 | 0.010564 | 0.028217 | 0.13912 | 0.073622 | 0.31137 | 0.019363 | 0.060571 | 0.027831 | -0.001407 | 0.093665 | 0.19227 | -0.11587 | -0.17331 | 122.6359 | 0.047564 | 122.6771 | 122.6448 | 0.008854 | -0.017931 | 0.21982 | 122.4433 | 0.002112 | 122.6771 | 122.6152 | 0.1719 | 0.10072 | -0.20742 | 122.7557 | 122.6902 | 122.928 | 122.6271 | -0.07219 | 122.7102 | 122.8088 | 122.5007 | 122.6444 | -0.26486
2500.1875 | 122.7997 | -122.6578 | 0.12817 | 1.4211e-13 | -0.0086495 | 0.02218 | -0.0033377 | -0.0094525 | 0.010784 | 0.0016025 | 0.0090775 | 0.019447 | 0.075561 | 0.028433 | 0.0048713 | 0.060567 | 0.005985 | 0.01906 | 0.12996 | 0.073622 | 0.3068 | 0.019363 | 0.069728 | 0.018674 | -0.005985 | 0.089087 | 0.19685 | -0.11587 | -0.17331 | 122.6771 | 0.001786 | 122.7183 | 122.6768 | -0.000303 | -0.054552 | 0.17862 | 122.4845 | -0.039087 | 122.7275 | 122.6518 | 0.16732 | 0.068677 | -0.24405 | 122.7877 | 122.7314 | 122.9646 | 122.6638 | -0.10881 | 122.7469 | 122.8546 | 122.5419 | 122.6765 | -0.30148
2501.8906 | 122.9233 | -122.6212 | 0.068665 | 1.4211e-13 | -0.0084359 | 0.02218 | -0.0033377 | -0.0094525 | 0.010997 | -0.006028 | 0.0086503 | 0.019447 | 0.075775 | 0.029288 | 0.0048713 | 0.060567 | 0.010564 | 0.01906 | 0.12996 | 0.069043 | 0.31137 | 0.023942 | 0.06515 | 0.027831 | -0.005985 | 0.084508 | 0.19227 | -0.11587 | -0.16873 | 122.6451 | 0.061295 | 122.6817 | 122.6402 | -0.004882 | 0.000378 | 0.24271 | 122.4524 | 0.015843 | 122.6863 | 122.6152 | 0.16274 | 0.12361 | -0.18454 | 122.7511 | 122.6902 | 122.9325 | 122.6317 | -0.044723 | 122.7057 | 122.8134 | 122.5053 | 122.649 | -0.23739
2503.6562 | 122.8592 | -122.644 | 0.10986 | 1.4211e-13 | -0.0088631 | 0.021966 | -0.0033377 | -0.0094525 | 0.010997 | -0.006028 | 0.0086503 | 0.019447 | 0.075775 | 0.029075 | 0.0048713 | 0.065145 | 0.010564 | 0.023639 | 0.13454 | 0.069043 | 0.31595 | 0.014784 | 0.069728 | 0.023253 | -0.005985 | 0.084508 | 0.19685 | -0.11587 | -0.17331 | 122.6588 | 0.024676 | 122.7092 | 122.6677 | 0.008855 | -0.04082 | 0.20609 | 122.4707 | -0.025355 | 122.7138 | 122.6381 | 0.16732 | 0.086988 | -0.22574 | 122.7786 | 122.7131 | 122.96 | 122.6546 | -0.095079 | 122.7286 | 122.8409 | 122.5282 | 122.6673 | -0.28317
2505.4375 | 122.905 | -122.6807 | 0.086975 | 1.4211e-13 | -0.0086495 | 0.02218 | -0.0035515 | -0.0094525 | 0.010784 | 0.0016025 | 0.0084367 | 0.019447 | 0.075347 | 0.028647 | 0.0050849 | 0.060567 | 0.010564 | 0.023639 | 0.13454 | 0.078201 | 0.31595 | 0.014784 | 0.06515 | 0.023253 | -0.001407 | 0.098244 | 0.18769 | -0.11587 | -0.16873 | 122.6954 | 0.047564 | 122.7412 | 122.7043 | 0.008855 | -0.008774 | 0.22898 | 122.5119 | 0.011269 | 122.7458 | 122.6793 | 0.16732 | 0.10072 | -0.20285 | 122.8152 | 122.7589 | 122.9966 | 122.6912 | -0.072191 | 122.7789 | 122.8684 | 122.5648 | 122.7039 | -0.2557
2507.1406 | 122.8134 | -122.6761 | 0.11444 | 1.4211e-13 | -0.0086495 | 0.021966 | -0.0035515 | -0.0092389 | 0.01057 | -0.006028 | 0.0090775 | 0.019447 | 0.075561 | 0.029075 | 0.0048713 | 0.055988 | 0.001407 | 0.01906 | 0.12996 | 0.073622 | 0.31595 | 0.023942 | 0.06515 | 0.023253 | 0.003172 | 0.07993 | 0.18769 | -0.12045 | -0.17331 | 122.7 | 0.015519 | 122.7321 | 122.6951 | -0.004882 | -0.040819 | 0.20151 | 122.5028 | -0.034511 | 122.7412 | 122.6793 | 0.17648 | 0.073252 | -0.23489 | 122.806 | 122.7497 | 122.992 | 122.6775 | -0.090499 | 122.756 | 122.8638 | 122.5556 | 122.6993 | -0.28775
2508.8906 | 122.9416 | -122.6257 | 0.09613 | 1.4211e-13 | -0.0090769 | 0.02218 | -0.0033377 | -0.0094525 | 0.010784 | -0.006028 | 0.0090775 | 0.019661 | 0.075561 | 0.029075 | 0.0048713 | 0.069723 | 0.005985 | 0.023639 | 0.12996 | 0.073622 | 0.31595 | 0.023942 | 0.060571 | 0.027831 | -0.005985 | 0.089087 | 0.19685 | -0.11587 | -0.16873 | 122.6497 | 0.03383 | 122.6955 | 122.6494 | -0.000303 | -0.022508 | 0.21982 | 122.457 | -0.007043 | 122.6863 | 122.6197 | 0.16274 | 0.10072 | -0.212 | 122.7557 | 122.6994 | 122.9417 | 122.6317 | -0.072188 | 122.7148 | 122.8226 | 122.5099 | 122.6536 | -0.26486
2510.5781 | 122.9233 | -122.644 | 0.09613 | 1.4211e-13 | -0.0090769 | 0.021966 | -0.0033377 | -0.0092389 | 0.010784 | 0.0016025 | 0.0090775 | 0.019447 | 0.075347 | 0.029075 | 0.0050849 | 0.065145 | 0.015142 | 0.023639 | 0.12996 | 0.073622 | 0.31137 | 0.023942 | 0.06515 | 0.023253 | -0.005985 | 0.089087 | 0.19227 | -0.11587 | -0.16873 | 122.668 | 0.03383 | 122.7092 | 122.6677 | -0.000303 | -0.022508 | 0.21524 | 122.4753 | -0.007043 | 122.7092 | 122.6381 | 0.16274 | 0.096142 | -0.212 | 122.774 | 122.7177 | 122.9554 | 122.6592 | -0.072188 | 122.7331 | 122.8363 | 122.5282 | 122.6673 | -0.26486
2512.3438 | 122.7905 | -122.6532 | 0.1236 | 1.4211e-13 | -0.0088631 | 0.021752 | -0.0035515 | -0.0094525 | 0.010997 | -0.006028 | 0.0084367 | 0.019447 | 0.075561 | 0.029075 | 0.0046577 | 0.065145 | 0.001407 | 0.028217 | 0.12538 | 0.073622 | 0.31595 | 0.019363 | 0.06515 | 0.014095 | -0.001407 | 0.089087 | 0.19227 | -0.11587 | -0.17331 | 122.6726 | 0.001786 | 122.7183 | 122.6814 | 0.008854 | -0.049974 | 0.19236 | 122.4799 | -0.034509 | 122.7183 | 122.6518 | 0.1719 | 0.068676 | -0.23947 | 122.7786 | 122.7268 | 122.9692 | 122.6546 | -0.10423 | 122.7423 | 122.8455 | 122.5373 | 122.6673 | -0.2969
2514.0938 | 122.7905 | -122.6807 | 0.13733 | 1.4211e-13 | -0.0088631 | 0.02218 | -0.0037651 | -0.0096661 | 0.010997 | -0.006028 | 0.0086503 | 0.019234 | 0.075561 | 0.029075 | 0.0046577 | 0.065145 | 0.005985 | 0.023639 | 0.13454 | 0.073622 | 0.3068 | 0.019363 | 0.069728 | 0.023253 | -0.005985 | 0.07993 | 0.19227 | -0.11587 | -0.17331 | 122.7 | -0.00279 | 122.7458 | 122.7043 | 0.004276 | -0.063707 | 0.16947 | 122.5074 | -0.057399 | 122.7504 | 122.6747 | 0.16732 | 0.054943 | -0.2532 | 122.8152 | 122.7543 | 122.9875 | 122.6866 | -0.11797 | 122.7606 | 122.8729 | 122.5648 | 122.7039 | -0.31063
2515.8438 | 122.818 | -122.7081 | 0.1236 | 1.4211e-13 | -0.0088631 | 0.022393 | -0.0033377 | -0.0094525 | 0.010784 | -0.013659 | 0.0088639 | 0.019447 | 0.075561 | 0.029075 | 0.0046577 | 0.060567 | 0.005985 | 0.023639 | 0.13454 | 0.08278 | 0.31595 | 0.028521 | 0.06515 | 0.018674 | -0.005985 | 0.089087 | 0.19685 | -0.12045 | -0.17331 | 122.7367 | 0.010943 | 122.7687 | 122.7318 | -0.004882 | -0.040816 | 0.19236 | 122.5348 | -0.034509 | 122.7733 | 122.7021 | 0.16732 | 0.073255 | -0.24405 | 122.8427 | 122.7909 | 123.0241 | 122.7141 | -0.095075 | 122.7972 | 122.905 | 122.5877 | 122.7268 | -0.2969
2517.6094 | 122.8867 | -122.644 | 0.10529 | 1.4211e-13 | -0.0088631 | 0.02218 | -0.0031241 | -0.0096661 | 0.010997 | 0.0016025 | 0.0084367 | 0.019234 | 0.075561 | 0.028861 | 0.0048713 | 0.060567 | 0.010564 | 0.023639 | 0.13454 | 0.069043 | 0.31137 | 0.019363 | 0.06515 | 0.023253 | -0.001407 | 0.084508 | 0.19227 | -0.11587 | -0.17331 | 122.6634 | 0.029253 | 122.7046 | 122.6677 | 0.004276 | -0.036243 | 0.20609 | 122.4707 | -0.020778 | 122.7092 | 122.6426 | 0.1719 | 0.086986 | -0.22116 | 122.7786 | 122.7131 | 122.9554 | 122.6546 | -0.085923 | 122.7286 | 122.8363 | 122.5282 | 122.6673 | -0.27859
2519.375 | 122.9416 | -122.6395 | 0.09613 | 1.4211e-13 | -0.0090769 | 0.021966 | -0.0035515 | -0.0096661 | 0.01057 | -0.006028 | 0.0086503 | 0.019447 | 0.075134 | 0.028861 | 0.0046577 | 0.060567 | 0.010564 | 0.023639 | 0.13454 | 0.064464 | 0.3068 | 0.019363 | 0.060571 | 0.027831 | -0.001407 | 0.093665 | 0.19227 | -0.12045 | -0.17331 | 122.6588 | 0.038409 | 122.7 | 122.6631 | 0.004276 | -0.031666 | 0.21067 | 122.4662 | -0.002465 | 122.7 | 122.6381 | 0.1719 | 0.096142 | -0.21658 | 122.774 | 122.7039 | 122.9463 | 122.65 | -0.076767 | 122.7331 | 122.8317 | 122.519 | 122.6673 | -0.26944
2521.1406 | 122.9141 | -122.6395 | 0.07782 | 1.4211e-13 | -0.0088631 | 0.02218 | -0.0035515 | -0.0094525 | 0.010784 | -0.006028 | 0.0088639 | 0.019447 | 0.075347 | 0.028647 | 0.0046577 | 0.065145 | 0.005985 | 0.023639 | 0.12996 | 0.087359 | 0.31595 | 0.014784 | 0.069728 | 0.027831 | -0.005985 | 0.089087 | 0.19227 | -0.11129 | -0.17788 | 122.6542 | 0.05214 | 122.7046 | 122.6631 | 0.008855 | 0.009539 | 0.23813 | 122.4616 | 0.011267 | 122.7092 | 122.6335 | 0.1719 | 0.11445 | -0.18911 | 122.7694 | 122.7268 | 122.9554 | 122.6454 | -0.063036 | 122.7286 | 122.8317 | 122.5282 | 122.6673 | -0.2557
2522.8438 | 122.8592 | -122.6807 | 0.1236 | 1.4211e-13 | -0.0088631 | 0.02218 | -0.0031241 | -0.0094525 | 0.010784 | -0.006028 | 0.0084367 | 0.019661 | 0.075561 | 0.029288 | 0.0044439 | 0.060567 | 0.005985 | 0.028217 | 0.12996 | 0.073622 | 0.32053 | 0.028521 | 0.06515 | 0.027831 | -0.005985 | 0.084508 | 0.19227 | -0.12503 | -0.17788 | 122.7092 | 0.006364 | 122.7412 | 122.7089 | -0.000304 | -0.049974 | 0.19694 | 122.5028 | -0.039088 | 122.7458 | 122.6747 | 0.1719 | 0.068676 | -0.24862 | 122.8106 | 122.7543 | 123.0012 | 122.6866 | -0.095075 | 122.7652 | 122.8729 | 122.5556 | 122.7085 | -0.30148
2524.5938 | 122.8226 | -122.6852 | 0.12817 | 1.4211e-13 | -0.0084359 | 0.021966 | -0.0033377 | -0.0094525 | 0.011638 | 0.0016025 | 0.0090775 | 0.019234 | 0.075775 | 0.029288 | 0.0046577 | 0.065145 | 0.015142 | 0.028217 | 0.13912 | 0.069043 | 0.31595 | 0.019363 | 0.06515 | 0.018674 | 0.003172 | 0.089087 | 0.19227 | -0.12503 | -0.17331 | 122.7046 | 0.010943 | 122.7504 | 122.7135 | 0.008854 | -0.059131 | 0.18778 | 122.5119 | -0.039087 | 122.7504 | 122.6884 | 0.17648 | 0.064098 | -0.2532 | 122.8244 | 122.7543 | 123.0012 | 122.7004 | -0.10881 | 122.7743 | 122.8775 | 122.5602 | 122.7039 | -0.30148
2526.3594 | 122.9462 | -122.6349 | 0.07782 | 1.4211e-13 | -0.0088631 | 0.022607 | -0.0029103 | -0.0090251 | 0.010784 | -0.006028 | 0.0086503 | 0.019875 | 0.075561 | 0.029288 | 0.0048713 | 0.065145 | 0.005985 | 0.023639 | 0.13454 | 0.078201 | 0.31137 | 0.028521 | 0.069728 | 0.03241 | -0.001407 | 0.089087 | 0.19685 | -0.11587 | -0.16873 | 122.6634 | 0.056719 | 122.7 | 122.6585 | -0.004882 | 0.000381 | 0.23355 | 122.4662 | 0.011267 | 122.7046 | 122.6335 | 0.16732 | 0.11903 | -0.19369 | 122.7694 | 122.7131 | 122.9463 | 122.6409 | -0.049299 | 122.724 | 122.8317 | 122.519 | 122.6673 | -0.24655
2528.0625 | 122.8455 | -122.6944 | 0.12817 | 1.4211e-13 | -0.0088631 | 0.022393 | -0.0033377 | -0.0096661 | 0.011211 | 0.0092325 | 0.0088639 | 0.019447 | 0.075561 | 0.029075 | 0.0048713 | 0.065145 | 0.015142 | 0.014482 | 0.12996 | 0.073622 | 0.32053 | 0.028521 | 0.06515 | 0.027831 | -0.005985 | 0.084508 | 0.19685 | -0.10671 | -0.17331 | 122.7229 | 0.001786 | 122.7595 | 122.7089 | -0.014039 | -0.054552 | 0.19236 | 122.5211 | -0.043666 | 122.7595 | 122.6884 | 0.16732 | 0.068677 | -0.23489 | 122.8244 | 122.768 | 123.0149 | 122.7095 | -0.099653 | 122.7789 | 122.8912 | 122.5877 | 122.7222 | -0.30148
2529.8125 | 122.8867 | -122.6944 | 0.11444 | 1.4211e-13 | -0.0088631 | 0.02218 | -0.0035515 | -0.0096661 | 0.010997 | 0.0016025 | 0.0086503 | 0.019234 | 0.075134 | 0.028861 | 0.0048713 | 0.060567 | 0.015142 | 0.023639 | 0.12538 | 0.08278 | 0.31595 | 0.028521 | 0.069728 | 0.027831 | -0.001407 | 0.084508 | 0.18769 | -0.11587 | -0.16873 | 122.7229 | 0.010941 | 122.755 | 122.718 | -0.004882 | -0.031661 | 0.20151 | 122.5257 | -0.029933 | 122.7641 | 122.693 | 0.16732 | 0.073252 | -0.23031 | 122.8198 | 122.7772 | 123.0103 | 122.7095 | -0.08592 | 122.7789 | 122.8821 | 122.5785 | 122.7222 | -0.28317
2531.5 | 122.9507 | -122.6715 | 0.068665 | 1.4211e-13 | -0.0088631 | 0.022393 | -0.0035515 | -0.0096661 | 0.010997 | 0.0016025 | 0.0086503 | 0.019661 | 0.075561 | 0.028861 | 0.0048713 | 0.065145 | 0.005985 | 0.01906 | 0.12996 | 0.073622 | 0.32053 | 0.014784 | 0.06515 | 0.023253 | -0.010564 | 0.084508 | 0.18311 | -0.11587 | -0.18246 | 122.6863 | 0.061295 | 122.7367 | 122.6906 | 0.004276 | 0.004957 | 0.25187 | 122.489 | 0.015843 | 122.7367 | 122.6609 | 0.1719 | 0.11445 | -0.18454 | 122.8015 | 122.7451 | 122.992 | 122.6775 | -0.053881 | 122.756 | 122.8546 | 122.5556 | 122.6948 | -0.25113
2533.25 | 122.937 | -122.6669 | 0.10529 | 1.4211e-13 | -0.0086495 | 0.021752 | -0.0031241 | -0.0092389 | 0.010997 | 0.0016025 | 0.0086503 | 0.019234 | 0.075561 | 0.028647 | 0.0046577 | 0.065145 | 0.015142 | 0.028217 | 0.12996 | 0.08278 | 0.32969 | 0.019363 | 0.06515 | 0.023253 | -0.010564 | 0.07993 | 0.19685 | -0.11587 | -0.16873 | 122.6863 | 0.024674 | 122.7321 | 122.6951 | 0.008854 | -0.022506 | 0.2244 | 122.4982 | -0.025356 | 122.7321 | 122.6564 | 0.15816 | 0.091565 | -0.22116 | 122.7969 | 122.7497 | 122.9966 | 122.6821 | -0.085923 | 122.7469 | 122.8638 | 122.5511 | 122.6902 | -0.27401
2535.0156 | 122.8363 | -122.7173 | 0.11902 | 1.4211e-13 | -0.0088631 | 0.022393 | -0.0035515 | -0.0094525 | 0.010784 | -0.006028 | 0.0086503 | 0.019875 | 0.075775 | 0.028861 | 0.0048713 | 0.060567 | 0.010564 | 0.023639 | 0.13912 | 0.078201 | 0.31595 | 0.028521 | 0.060571 | 0.023253 | -0.001407 | 0.093665 | 0.19685 | -0.12045 | -0.17788 | 122.7458 | 0.020098 | 122.7779 | 122.7409 | -0.004882 | -0.040818 | 0.19693 | 122.5394 | -0.025354 | 122.7779 | 122.7159 | 0.17648 | 0.077832 | -0.23947 | 122.8564 | 122.7955 | 123.0332 | 122.7278 | -0.090498 | 122.811 | 122.9141 | 122.5968 | 122.7405 | -0.2969
2536.7812 | 122.9599 | -122.6349 | 0.086975 | 1.4211e-13 | -0.0088631 | 0.021966 | -0.0031241 | -0.0098799 | 0.010997 | 0.0016025 | 0.0086503 | 0.019447 | 0.075347 | 0.029075 | 0.0048713 | 0.060567 | 0.010564 | 0.014482 | 0.12996 | 0.073622 | 0.31137 | 0.019363 | 0.06515 | 0.027831 | -0.005985 | 0.089087 | 0.19227 | -0.11129 | -0.17331 | 122.6543 | 0.042985 | 122.6955 | 122.6494 | -0.004881 | -0.013353 | 0.2244 | 122.4616 | 0.002112 | 122.7 | 122.6289 | 0.16732 | 0.1053 | -0.19827 | 122.7648 | 122.7085 | 122.9463 | 122.6455 | -0.067612 | 122.724 | 122.8272 | 122.5236 | 122.6627 | -0.26028
2538.5469 | 122.8271 | -122.6807 | 0.13275 | 1.4211e-13 | -0.0088631 | 0.021752 | -0.0033377 | -0.0094525 | 0.011211 | -0.006028 | 0.0084367 | 0.019661 | 0.075561 | 0.029075 | 0.0048713 | 0.060567 | 0.005985 | 0.01906 | 0.13912 | 0.08278 | 0.32053 | 0.019363 | 0.06515 | 0.027831 | 0.007751 | 0.089087 | 0.19227 | -0.11587 | -0.17788 | 122.7 | 0.006366 | 122.7412 | 122.6997 | -0.000303 | -0.049971 | 0.18778 | 122.5028 | -0.043664 | 122.7458 | 122.6884 | 0.18564 | 0.059521 | -0.24862 | 122.8198 | 122.7634 | 123.0012 | 122.6866 | -0.11339 | 122.7698 | 122.8729 | 122.5648 | 122.7085 | -0.31064
2540.2344 | 122.9599 | -122.6669 | 0.082397 | 1.4211e-13 | -0.0090769 | 0.022393 | -0.0033377 | -0.0096661 | 0.010784 | 0.0092325 | 0.0086503 | 0.019234 | 0.075347 | 0.029075 | 0.0046577 | 0.060567 | 0.010564 | 0.014482 | 0.12538 | 0.073622 | 0.31595 | 0.019363 | 0.069728 | 0.023253 | -0.010564 | 0.089087 | 0.19227 | -0.11587 | -0.17788 | 122.6863 | 0.042985 | 122.7275 | 122.6814 | -0.004881 | -0.008775 | 0.23356 | 122.489 | 0.00669 | 122.7367 | 122.6564 | 0.16732 | 0.10988 | -0.19827 | 122.7923 | 122.7406 | 122.9829 | 122.6775 | -0.063034 | 122.756 | 122.8592 | 122.5511 | 122.6902 | -0.26028
2541.9844 | 122.9233 | -122.6669 | 0.10529 | 1.4211e-13 | -0.0088631 | 0.021966 | -0.0037651 | -0.0096661 | 0.01057 | -0.013659 | 0.0088639 | 0.019447 | 0.075347 | 0.028861 | 0.0046577 | 0.065145 | 0.010564 | 0.009904 | 0.13454 | 0.078201 | 0.31137 | 0.014784 | 0.060571 | 0.036989 | -0.001407 | 0.084508 | 0.18769 | -0.11587 | -0.16873 | 122.6817 | 0.029253 | 122.7321 | 122.6768 | -0.00488 | -0.027085 | 0.20609 | 122.4982 | -0.020778 | 122.7275 | 122.6655 | 0.16732 | 0.082407 | -0.22116 | 122.8015 | 122.7451 | 122.9783 | 122.6775 | -0.090502 | 122.7514 | 122.8546 | 122.5511 | 122.7039 | -0.27401
2543.6719 | 122.9828 | -122.6807 | 0.086975 | 1.4211e-13 | -0.0086495 | 0.02218 | -0.0031241 | -0.0092389 | 0.010997 | -0.006028 | 0.0088639 | 0.019447 | 0.075134 | 0.029075 | 0.0046577 | 0.065145 | 0.010564 | 0.009904 | 0.12996 | 0.078201 | 0.3068 | 0.019363 | 0.060571 | 0.023253 | 0.003172 | 0.089087 | 0.19227 | -0.11587 | -0.17788 | 122.7 | 0.042985 | 122.7458 | 122.6906 | -0.009459 | -0.008774 | 0.21982 | 122.5028 | 0.002112 | 122.7412 | 122.6838 | 0.18106 | 0.1053 | -0.20285 | 122.8106 | 122.7589 | 122.9875 | 122.6912 | -0.067612 | 122.7698 | 122.8729 | 122.5648 | 122.7039 | -0.26486
2545.4531 | 122.8363 | -122.6898 | 0.14191 | 1.4211e-13 | -0.0086495 | 0.02218 | -0.0033377 | -0.0094525 | 0.010997 | 0.0092325 | 0.0086503 | 0.019234 | 0.075347 | 0.029288 | 0.0048713 | 0.060567 | 0.015142 | 0.000747 | 0.13912 | 0.073622 | 0.31595 | 0.019363 | 0.06515 | 0.023253 | -0.015143 | 0.10282 | 0.18311 | -0.11587 | -0.17331 | 122.7092 | -0.00279 | 122.7504 | 122.6906 | -0.018616 | -0.068285 | 0.17405 | 122.5165 | -0.039085 | 122.755 | 122.6747 | 0.15816 | 0.041208 | -0.25778 | 122.8289 | 122.7634 | 123.0058 | 122.705 | -0.12254 | 122.7926 | 122.8729 | 122.5739 | 122.7131 | -0.31521
2547.2188 | 122.9004 | -122.6807 | 0.10986 | 1.4211e-13 | -0.0088631 | 0.02218 | -0.0033377 | -0.0094525 | 0.010784 | -0.006028 | 0.0086503 | 0.019447 | 0.075134 | 0.029075 | 0.0044439 | 0.065145 | 0.010564 | 0.01906 | 0.12538 | 0.087359 | 0.31595 | 0.019363 | 0.069728 | 0.023253 | 0.003172 | 0.089087 | 0.18769 | -0.12045 | -0.16873 | 122.7 | 0.015519 | 122.7458 | 122.6997 | -0.000303 | -0.022504 | 0.20609 | 122.5119 | -0.020776 | 122.7504 | 122.6838 | 0.1719 | 0.07783 | -0.23031 | 122.806 | 122.768 | 122.9966 | 122.6912 | -0.0905 | 122.7698 | 122.8684 | 122.5602 | 122.7039 | -0.27859
2548.9844 | 122.9874 | -122.6807 | 0.10071 | 1.4211e-13 | -0.0090769 | 0.02218 | -0.0035515 | -0.0094525 | 0.01057 | -0.006028 | 0.0088639 | 0.019234 | 0.075561 | 0.028861 | 0.0046577 | 0.060567 | 0.019721 | 0.01906 | 0.13454 | 0.078201 | 0.31595 | 0.019363 | 0.06515 | 0.027831 | -0.001407 | 0.093665 | 0.19685 | -0.12045 | -0.16873 | 122.7 | 0.033831 | 122.7412 | 122.6997 | -0.000303 | -0.022507 | 0.21524 | 122.5119 | -0.007043 | 122.7458 | 122.6793 | 0.16732 | 0.096143 | -0.22116 | 122.8152 | 122.7589 | 122.9966 | 122.7004 | -0.081345 | 122.7743 | 122.8775 | 122.5602 | 122.7085 | -0.26944
2550.6719 | 122.9599 | -122.6761 | 0.10071 | 1.4211e-13 | -0.0090769 | 0.021966 | -0.0035515 | -0.0094525 | 0.010784 | -0.006028 | 0.0086503 | 0.019447 | 0.075561 | 0.029075 | 0.0044439 | 0.060567 | 0.015142 | 0.009904 | 0.12996 | 0.073622 | 0.31595 | 0.023942 | 0.06515 | 0.023253 | -0.005985 | 0.089087 | 0.19685 | -0.11587 | -0.17788 | 122.7 | 0.029252 | 122.7367 | 122.686 | -0.014038 | -0.027086 | 0.21524 | 122.4982 | -0.011621 | 122.7412 | 122.6701 | 0.1719 | 0.096143 | -0.21658 | 122.806 | 122.7497 | 122.992 | 122.6912 | -0.076766 | 122.7652 | 122.8729 | 122.5602 | 122.6993 | -0.27859
2552.4375 | 122.9187 | -122.6898 | 0.082397 | 1.4211e-13 | -0.0088631 | 0.02218 | -0.0031241 | -0.0096661 | 0.010997 | 0.0092325 | 0.0084367 | 0.019234 | 0.075134 | 0.028861 | 0.0048713 | 0.060567 | 0.015142 | 0.01906 | 0.13454 | 0.08278 | 0.32053 | 0.023942 | 0.06515 | 0.023253 | -0.005985 | 0.084508 | 0.19685 | -0.12045 | -0.17331 | 122.7138 | 0.052142 | 122.7504 | 122.7089 | -0.004882 | 0.000383 | 0.23813 | 122.5165 | 0.002111 | 122.755 | 122.6838 | 0.16732 | 0.11445 | -0.20285 | 122.8244 | 122.7726 | 123.0104 | 122.705 | -0.058455 | 122.7743 | 122.8867 | 122.5694 | 122.7131 | -0.2557
2554.2188 | 122.8775 | -122.6898 | 0.10529 | 1.4211e-13 | -0.0088631 | 0.02218 | -0.0031241 | -0.0096661 | 0.010784 | 0.0016025 | 0.0086503 | 0.019234 | 0.075775 | 0.028861 | 0.0046577 | 0.055988 | 0.015142 | 0.009904 | 0.12996 | 0.08278 | 0.31137 | 0.023942 | 0.06515 | 0.023253 | -0.001407 | 0.084508 | 0.19227 | -0.12045 | -0.16415 | 122.7138 | 0.024674 | 122.7458 | 122.6997 | -0.014038 | -0.022506 | 0.20609 | 122.5257 | -0.020778 | 122.755 | 122.6884 | 0.16274 | 0.086986 | -0.22574 | 122.8198 | 122.7726 | 123.0012 | 122.705 | -0.081344 | 122.7743 | 122.8821 | 122.5694 | 122.7131 | -0.26943
2555.9844 | 122.9233 | -122.6852 | 0.09613 | 1.4211e-13 | -0.0088631 | 0.021966 | -0.0035515 | -0.0096661 | 0.010784 | -0.006028 | 0.0086503 | 0.019447 | 0.075561 | 0.029075 | 0.0044439 | 0.065145 | 0.015142 | 0.005325 | 0.13454 | 0.08278 | 0.31595 | 0.019363 | 0.060571 | 0.023253 | -0.001407 | 0.089087 | 0.19227 | -0.12503 | -0.16873 | 122.7046 | 0.038409 | 122.7504 | 122.6906 | -0.014038 | -0.01335 | 0.21982 | 122.5165 | -0.007043 | 122.7458 | 122.6838 | 0.16732 | 0.096142 | -0.22116 | 122.8198 | 122.768 | 123.0012 | 122.7004 | -0.076767 | 122.7743 | 122.8775 | 122.5602 | 122.7085 | -0.26486
2557.6719 | 122.8592 | -122.699 | 0.1236 | 1.4211e-13 | -0.0086495 | 0.022393 | -0.0035515 | -0.0096661 | 0.010356 | 0.0092325 | 0.0088639 | 0.019447 | 0.075347 | 0.028861 | 0.0046577 | 0.060567 | 0.005985 | 0.009904 | 0.13454 | 0.078201 | 0.31595 | 0.019363 | 0.060571 | 0.023253 | -0.010564 | 0.075351 | 0.18311 | -0.12045 | -0.17331 | 122.7183 | 0.010943 | 122.7595 | 122.7089 | -0.009459 | -0.045395 | 0.19236 | 122.5257 | -0.048245 | 122.7595 | 122.6884 | 0.16274 | 0.059519 | -0.24405 | 122.8335 | 122.7772 | 123.0149 | 122.705 | -0.10423 | 122.7743 | 122.8821 | 122.5785 | 122.7222 | -0.2969
2559.4375 | 122.8958 | -122.7127 | 0.082397 | 1.4211e-13 | -0.0088631 | 0.021752 | -0.0035515 | -0.0094525 | 0.010997 | -0.006028 | 0.0086503 | 0.019447 | 0.075134 | 0.029075 | 0.0048713 | 0.060567 | 0.010564 | 0.009904 | 0.12996 | 0.078201 | 0.31595 | 0.023942 | 0.060571 | 0.018674 | -0.005985 | 0.07993 | 0.18769 | -0.12045 | -0.17331 | 122.7367 | 0.047563 | 122.7733 | 122.7226 | -0.014038 | -0.004196 | 0.23356 | 122.5394 | -0.002467 | 122.7733 | 122.7067 | 0.16732 | 0.1053 | -0.20285 | 122.8427 | 122.7909 | 123.0287 | 122.7233 | -0.058455 | 122.7926 | 122.9004 | 122.5923 | 122.7314 | -0.2557
2561.1875 | 122.9416 | -122.7036 | 0.091553 | 1.4211e-13 | -0.0088631 | 0.02218 | -0.0035515 | -0.0092389 | 0.010784 | -0.006028 | 0.0086503 | 0.019234 | 0.075561 | 0.029075 | 0.0048713 | 0.060567 | 0.015142 | 0.01906 | 0.12996 | 0.069043 | 0.32053 | 0.028521 | 0.060571 | 0.027831 | -0.001407 | 0.084508 | 0.19685 | -0.11129 | -0.17331 | 122.7321 | 0.038407 | 122.7641 | 122.7226 | -0.009461 | -0.02251 | 0.22898 | 122.5302 | -0.007045 | 122.7641 | 122.7021 | 0.1719 | 0.1053 | -0.20285 | 122.8335 | 122.7726 | 123.0241 | 122.7187 | -0.063032 | 122.7881 | 122.9004 | 122.5923 | 122.7314 | -0.26486
2562.8906 | 122.9095 | -122.7173 | 0.11444 | 1.4211e-13 | -0.0092905 | 0.021966 | -0.0033377 | -0.0096661 | 0.010784 | 0.0092325 | 0.0086503 | 0.019661 | 0.075347 | 0.029075 | 0.0046577 | 0.055988 | 0.005985 | 0.01906 | 0.13454 | 0.069043 | 0.32053 | 0.023942 | 0.069728 | 0.027831 | -0.005985 | 0.089087 | 0.19227 | -0.12503 | -0.17788 | 122.7412 | 0.020098 | 122.7733 | 122.7363 | -0.004882 | -0.045398 | 0.20609 | 122.5394 | -0.025354 | 122.787 | 122.7113 | 0.1719 | 0.077831 | -0.23947 | 122.8518 | 122.7863 | 123.0378 | 122.7233 | -0.090499 | 122.8064 | 122.9096 | 122.5923 | 122.7451 | -0.29233
2564.5781 | 122.905 | -122.6807 | 0.10529 | 1.4211e-13 | -0.0088631 | 0.021966 | -0.0035515 | -0.0098799 | 0.01057 | 0.0016025 | 0.0086503 | 0.019447 | 0.075134 | 0.029075 | 0.0044439 | 0.060567 | 0.001407 | 0.014482 | 0.13912 | 0.069043 | 0.31137 | 0.023942 | 0.060571 | 0.027831 | -0.001407 | 0.084508 | 0.19685 | -0.12045 | -0.16873 | 122.7046 | 0.033831 | 122.7412 | 122.6951 | -0.00946 | -0.036243 | 0.20609 | 122.5119 | -0.020778 | 122.7412 | 122.6793 | 0.16732 | 0.091565 | -0.22574 | 122.8198 | 122.7497 | 122.992 | 122.6821 | -0.081344 | 122.7652 | 122.8775 | 122.5602 | 122.7085 | -0.27401
2566.3438 | 122.9462 | -122.6715 | 0.059509 | 1.4211e-13 | -0.0092905 | 0.02218 | -0.0035515 | -0.0092389 | 0.01057 | -0.006028 | 0.0088639 | 0.019447 | 0.07492 | 0.029288 | 0.0044439 | 0.065145 | 0.019721 | 0.009904 | 0.13454 | 0.078201 | 0.31137 | 0.019363 | 0.060571 | 0.023253 | -0.001407 | 0.089087 | 0.19227 | -0.11129 | -0.17331 | 122.6909 | 0.07503 | 122.7367 | 122.6814 | -0.009459 | 0.018692 | 0.25187 | 122.4982 | 0.029578 | 122.7321 | 122.6701 | 0.1719 | 0.13276 | -0.1708 | 122.806 | 122.7497 | 122.9829 | 122.6912 | -0.040146 | 122.7606 | 122.8638 | 122.5602 | 122.6948 | -0.23281
2568.125 | 122.8775 | -122.7127 | 0.1236 | 1.4211e-13 | -0.0088631 | 0.02218 | -0.0033377 | -0.0094525 | 0.01057 | -0.006028 | 0.0088639 | 0.019234 | 0.075134 | 0.029075 | 0.0048713 | 0.065145 | 0.015142 | 0.014482 | 0.13454 | 0.078201 | 0.31595 | 0.014784 | 0.074307 | 0.023253 | -0.001407 | 0.089087 | 0.19227 | -0.11129 | -0.17331 | 122.7275 | 0.010943 | 122.7779 | 122.7272 | -0.000302 | -0.045395 | 0.19236 | 122.5394 | -0.034509 | 122.787 | 122.7113 | 0.1719 | 0.068676 | -0.23489 | 122.8472 | 122.7909 | 123.0287 | 122.7279 | -0.10881 | 122.8018 | 122.905 | 122.6014 | 122.736 | -0.2969
2569.8125 | 122.9507 | -122.6898 | 0.073242 | 1.4211e-13 | -0.0088631 | 0.022607 | -0.0033377 | -0.0096661 | 0.010784 | 0.0016025 | 0.0088639 | 0.019875 | 0.075561 | 0.028861 | 0.0048713 | 0.055988 | 0.010564 | 0.009904 | 0.13454 | 0.08278 | 0.31595 | 0.023942 | 0.060571 | 0.023253 | 0.003172 | 0.084508 | 0.18769 | -0.12045 | -0.17331 | 122.7138 | 0.061297 | 122.7458 | 122.6997 | -0.014038 | 0.009538 | 0.24271 | 122.5165 | 0.011266 | 122.7504 | 122.693 | 0.17648 | 0.11445 | -0.19369 | 122.8244 | 122.7726 | 123.0058 | 122.7004 | -0.0493 | 122.7743 | 122.8775 | 122.5694 | 122.7131 | -0.24655
2571.5156 | 122.9965 | -122.6944 | 0.07782 | 1.4211e-13 | -0.0086495 | 0.022393 | -0.0035515 | -0.0096661 | 0.011211 | -0.021289 | 0.0090775 | 0.019447 | 0.075775 | 0.029075 | 0.0044439 | 0.060567 | 0.015142 | 0.014482 | 0.13454 | 0.078201 | 0.31595 | 0.019363 | 0.069728 | 0.03241 | -0.005985 | 0.084508 | 0.19685 | -0.12045 | -0.17788 | 122.7138 | 0.056719 | 122.755 | 122.7089 | -0.004881 | 0.000381 | 0.23813 | 122.5165 | 0.006688 | 122.7641 | 122.6884 | 0.1719 | 0.11903 | -0.19827 | 122.8289 | 122.7726 | 123.0103 | 122.7095 | -0.058457 | 122.7789 | 122.8912 | 122.5739 | 122.7268 | -0.2557
2573.2188 | 123.0057 | -122.6807 | 0.091553 | 1.4211e-13 | -0.0086495 | 0.02218 | -0.0033377 | -0.0096661 | 0.010784 | -0.006028 | 0.0088639 | 0.019447 | 0.075347 | 0.028861 | 0.0046577 | 0.055988 | 0.010564 | 0.009904 | 0.13454 | 0.069043 | 0.31595 | 0.028521 | 0.069728 | 0.027831 | -0.001407 | 0.084508 | 0.19227 | -0.12503 | -0.17331 | 122.7092 | 0.042986 | 122.7367 | 122.6906 | -0.018617 | -0.02251 | 0.2244 | 122.5074 | -0.007045 | 122.7504 | 122.6793 | 0.1719 | 0.10072 | -0.21658 | 122.8152 | 122.7497 | 122.9966 | 122.6912 | -0.063032 | 122.7652 | 122.8729 | 122.5556 | 122.7085 | -0.26486
2574.9844 | 122.9874 | -122.6944 | 0.10071 | 1.4211e-13 | -0.0088631 | 0.022393 | -0.0035515 | -0.0092389 | 0.01057 | 0.0092325 | 0.0082229 | 0.019447 | 0.075134 | 0.028861 | 0.0048713 | 0.065145 | 0.015142 | -0.003831 | 0.13454 | 0.078201 | 0.31595 | 0.019363 | 0.06515 | 0.023253 | -0.005985 | 0.089087 | 0.19685 | -0.11587 | -0.17331 | 122.7138 | 0.033831 | 122.7595 | 122.6906 | -0.023194 | -0.022507 | 0.21524 | 122.5211 | -0.011621 | 122.7595 | 122.6884 | 0.16732 | 0.096143 | -0.21658 | 122.8289 | 122.7726 | 123.0103 | 122.7095 | -0.081345 | 122.7835 | 122.8912 | 122.5785 | 122.7176 | -0.27401
2576.6719 | 122.9919 | -122.6944 | 0.09613 | 1.4211e-13 | -0.0090769 | 0.02218 | -0.0035515 | -0.0094525 | 0.010997 | 0.0092325 | 0.0088639 | 0.019661 | 0.075561 | 0.029075 | 0.0048713 | 0.069723 | 0.010564 | 0.000747 | 0.13912 | 0.073622 | 0.32053 | 0.014784 | 0.069728 | 0.027831 | -0.001407 | 0.084508 | 0.18769 | -0.11129 | -0.17331 | 122.7092 | 0.042987 | 122.7641 | 122.6951 | -0.014037 | -0.022508 | 0.2244 | 122.5211 | -0.011622 | 122.7641 | 122.693 | 0.1719 | 0.091563 | -0.20742 | 122.8335 | 122.768 | 123.0149 | 122.705 | -0.081346 | 122.7789 | 122.8821 | 122.5831 | 122.7222 | -0.26944
2578.4531 | 123.0103 | -122.6807 | 0.09613 | 1.4211e-13 | -0.0090769 | 0.02218 | -0.0035515 | -0.0098799 | 0.01057 | -0.006028 | 0.0086503 | 0.019447 | 0.075561 | 0.028861 | 0.0046577 | 0.060567 | 0.010564 | -0.003831 | 0.13454 | 0.073622 | 0.31137 | 0.014784 | 0.060571 | 0.018674 | -0.005985 | 0.07993 | 0.19227 | -0.11129 | -0.17788 | 122.6954 | 0.038409 | 122.7412 | 122.6768 | -0.018615 | -0.022508 | 0.21524 | 122.5028 | -0.0162 | 122.7412 | 122.6747 | 0.1719 | 0.096142 | -0.20742 | 122.8152 | 122.7543 | 122.992 | 122.6912 | -0.081346 | 122.7606 | 122.8729 | 122.5694 | 122.6993 | -0.27402
2580.2188 | 122.9187 | -122.7539 | 0.10071 | 1.4211e-13 | -0.0088631 | 0.021752 | -0.0033377 | -0.0092389 | 0.010784 | 0.0016025 | 0.0086503 | 0.019234 | 0.075134 | 0.029502 | 0.0044439 | 0.060567 | 0.005985 | 0.000747 | 0.13912 | 0.073622 | 0.31595 | 0.0331 | 0.069728 | 0.023253 | -0.005985 | 0.07993 | 0.19227 | -0.11587 | -0.17331 | 122.787 | 0.038409 | 122.8145 | 122.7547 | -0.032353 | -0.027086 | 0.21524 | 122.5806 | -0.020778 | 122.8236 | 122.7479 | 0.16732 | 0.091564 | -0.21658 | 122.893 | 122.8275 | 123.0699 | 122.7599 | -0.067608 | 122.8338 | 122.9462 | 122.638 | 122.7772 | -0.27401
2581.9062 | 122.9645 | -122.6669 | 0.091553 | 1.4211e-13 | -0.0090769 | 0.021966 | -0.0033377 | -0.0098799 | 0.010356 | 0.0016025 | 0.0086503 | 0.019234 | 0.075347 | 0.028861 | 0.0042303 | 0.065145 | 0.019721 | 0.000747 | 0.13454 | 0.078201 | 0.32053 | 0.019363 | 0.069728 | 0.027831 | -0.010564 | 0.089087 | 0.19227 | -0.11587 | -0.16873 | 122.6863 | 0.042986 | 122.7321 | 122.6677 | -0.018616 | -0.013352 | 0.22898 | 122.4982 | -0.002466 | 122.7367 | 122.6564 | 0.15816 | 0.10072 | -0.20742 | 122.8015 | 122.7451 | 122.9875 | 122.6867 | -0.07219 | 122.756 | 122.8592 | 122.5511 | 122.6948 | -0.26028
2583.6719 | 122.8729 | -122.7127 | 0.14191 | 1.4211e-13 | -0.0088631 | 0.02218 | -0.0033377 | -0.0096661 | 0.01057 | -0.006028 | 0.0088639 | 0.019661 | 0.075347 | 0.028861 | 0.0046577 | 0.060567 | 0.005985 | 0.000747 | 0.13454 | 0.073622 | 0.31595 | 0.023942 | 0.060571 | 0.023253 | -0.005985 | 0.089087 | 0.19685 | -0.12045 | -0.16873 | 122.7367 | -0.007368 | 122.7733 | 122.7135 | -0.023195 | -0.068285 | 0.17405 | 122.544 | -0.05282 | 122.7733 | 122.7067 | 0.16274 | 0.054944 | -0.26236 | 122.8472 | 122.7863 | 123.0287 | 122.7187 | -0.11797 | 122.8018 | 122.9096 | 122.5923 | 122.736 | -0.31063
2585.4531 | 122.9874 | -122.7264 | 0.07782 | 1.4211e-13 | -0.0090769 | 0.022393 | -0.0033377 | -0.0094525 | 0.01057 | -0.006028 | 0.0084367 | 0.019661 | 0.075347 | 0.029075 | 0.0044439 | 0.065145 | 0.010564 | 0.009904 | 0.12996 | 0.073622 | 0.31595 | 0.014784 | 0.055992 | 0.023253 | -0.010564 | 0.084508 | 0.19685 | -0.11129 | -0.17788 | 122.7412 | 0.05214 | 122.7916 | 122.7363 | -0.00488 | -0.004198 | 0.23813 | 122.5486 | 0.006688 | 122.7824 | 122.7159 | 0.16732 | 0.11903 | -0.18911 | 122.8564 | 122.8001 | 123.0424 | 122.737 | -0.063036 | 122.8109 | 122.9233 | 122.6151 | 122.7497 | -0.2557
2587.2031 | 123.0194 | -122.7081 | 0.07782 | 1.4211e-13 | -0.0088631 | 0.022393 | -0.0033377 | -0.0096661 | 0.010784 | -0.006028 | 0.0086503 | 0.019661 | 0.075347 | 0.028647 | 0.0048713 | 0.055988 | 0.005985 | 0.005325 | 0.13454 | 0.073622 | 0.32053 | 0.019363 | 0.060571 | 0.027831 | -0.001407 | 0.089087 | 0.19227 | -0.11587 | -0.16415 | 122.7275 | 0.056719 | 122.7641 | 122.7135 | -0.014038 | -0.004198 | 0.24271 | 122.544 | 0.011267 | 122.7687 | 122.7067 | 0.16274 | 0.11445 | -0.19369 | 122.8427 | 122.7818 | 123.0287 | 122.7141 | -0.058457 | 122.7972 | 122.9004 | 122.5923 | 122.736 | -0.24197
2588.9688 | 123.0103 | -122.699 | 0.082397 | 1.4211e-13 | -0.0090769 | 0.02218 | -0.0033377 | -0.0094525 | 0.01057 | -0.006028 | 0.0086503 | 0.019234 | 0.075134 | 0.029288 | 0.0046577 | 0.065145 | 0.010564 | 0.005325 | 0.13454 | 0.073622 | 0.31595 | 0.019363 | 0.060571 | 0.023253 | -0.001407 | 0.089087 | 0.18769 | -0.11587 | -0.16873 | 122.7183 | 0.052142 | 122.7641 | 122.7043 | -0.014038 | -0.008775 | 0.23356 | 122.5302 | 0.00669 | 122.7595 | 122.6976 | 0.16732 | 0.1053 | -0.19827 | 122.8335 | 122.7726 | 123.0149 | 122.7095 | -0.063034 | 122.7881 | 122.8867 | 122.5831 | 122.7222 | -0.25112
2590.6562 | 122.8546 | -122.7127 | 0.10986 | 1.4211e-13 | -0.0090769 | 0.021966 | -0.0033377 | -0.0092389 | 0.01057 | 0.0092325 | 0.0086503 | 0.019661 | 0.075347 | 0.029288 | 0.0044439 | 0.055988 | 0.010564 | -0.003831 | 0.12996 | 0.073622 | 0.32053 | 0.014784 | 0.06515 | 0.023253 | -0.005985 | 0.089087 | 0.17854 | -0.11129 | -0.16415 | 122.7275 | 0.020097 | 122.7687 | 122.7089 | -0.018615 | -0.036241 | 0.21067 | 122.5486 | -0.020776 | 122.7779 | 122.7067 | 0.15816 | 0.068673 | -0.22116 | 122.8427 | 122.7863 | 123.0332 | 122.7233 | -0.095079 | 122.8018 | 122.8912 | 122.6014 | 122.736 | -0.27401
2592.4375 | 122.9004 | -122.7219 | 0.10529 | 1.4211e-13 | -0.0088631 | 0.021966 | -0.0029103 | -0.0094525 | 0.01057 | -0.006028 | 0.0086503 | 0.019447 | 0.075561 | 0.028861 | 0.0046577 | 0.060567 | 0.015142 | -0.008409 | 0.12996 | 0.073622 | 0.31137 | 0.019363 | 0.06515 | 0.027831 | -0.001407 | 0.07993 | 0.19227 | -0.12045 | -0.17331 | 122.7412 | 0.024674 | 122.7824 | 122.7135 | -0.027772 | -0.031664 | 0.20609 | 122.5486 | -0.025356 | 122.787 | 122.7205 | 0.1719 | 0.086986 | -0.22574 | 122.8518 | 122.7955 | 123.0332 | 122.737 | -0.085923 | 122.8018 | 122.9141 | 122.6014 | 122.7497 | -0.27859
2594.1562 | 122.2641 | -122.1588 | 0.11902 | 1.4211e-13 | -0.0090769 | 0.022393 | -0.0029103 | -0.0094525 | 0.010784 | 0.0016025 | 0.0086503 | 0.019234 | 0.075775 | 0.028861 | 0.0044439 | 0.065145 | 0.010564 | 0.000747 | 0.12996 | 0.073622 | 0.31595 | 0.023942 | 0.060571 | 0.023253 | -0.001407 | 0.089087 | 0.19227 | -0.11587 | -0.17331 | 122.1828 | 0.010941 | 122.224 | 122.1596 | -0.023195 | -0.045397 | 0.19693 | 121.9855 | -0.029932 | 122.2194 | 122.1574 | 0.1719 | 0.073253 | -0.23489 | 122.2888 | 122.2324 | 122.4748 | 122.1694 | -0.095077 | 122.2479 | 122.3511 | 122.0429 | 122.1821 | -0.29233
2595.9219 | 122.3465 | -122.2275 | 0.10986 | 1.4211e-13 | -0.0090769 | 0.02218 | -0.0031241 | -0.0094525 | 0.010784 | -0.006028 | 0.0086503 | 0.019234 | 0.075347 | 0.029075 | 0.0044439 | 0.065145 | 0.019721 | 0.000747 | 0.12996 | 0.078201 | 0.32053 | 0.023942 | 0.069728 | 0.023253 | -0.001407 | 0.098244 | 0.18769 | -0.11587 | -0.17331 | 122.2514 | 0.020097 | 122.2926 | 122.2282 | -0.023195 | -0.031662 | 0.21067 | 122.0542 | -0.011619 | 122.2972 | 122.2261 | 0.1719 | 0.07783 | -0.22574 | 122.3574 | 122.3057 | 122.548 | 122.2472 | -0.085921 | 122.3257 | 122.4152 | 122.1116 | 122.2507 | -0.28317
2597.625 | 122.5479 | -122.3236 | 0.091553 | 1.4211e-13 | -0.0090769 | 0.022607 | -0.0037651 | -0.0096661 | 0.01057 | 0.0016025 | 0.0084367 | 0.019447 | 0.075561 | 0.029075 | 0.0044439 | 0.055988 | 0.010564 | 0.009904 | 0.13912 | 0.08278 | 0.3068 | 0.019363 | 0.074307 | 0.027831 | -0.001407 | 0.07993 | 0.19685 | -0.11129 | -0.16873 | 122.343 | 0.047564 | 122.3796 | 122.3335 | -0.009459 | -0.008773 | 0.21524 | 122.1549 | -0.011623 | 122.3979 | 122.3222 | 0.16732 | 0.1053 | -0.20285 | 122.4627 | 122.4064 | 122.6304 | 122.3342 | -0.07219 | 122.4035 | 122.5205 | 122.2123 | 122.3514 | -0.26028
2599.4062 | 122.5571 | -122.3648 | 0.10529 | 1.4211e-13 | -0.0090769 | 0.02218 | -0.0033377 | -0.0094525 | 0.010356 | -0.006028 | 0.0086503 | 0.019234 | 0.075134 | 0.028861 | 0.0044439 | 0.055988 | 0.005985 | 0.009904 | 0.13454 | 0.078201 | 0.32053 | 0.019363 | 0.06515 | 0.023253 | -0.005985 | 0.089087 | 0.20143 | -0.11587 | -0.17331 | 122.3842 | 0.029253 | 122.4208 | 122.3747 | -0.009459 | -0.027085 | 0.21525 | 122.1915 | -0.016199 | 122.43 | 122.3588 | 0.16732 | 0.096143 | -0.22116 | 122.4993 | 122.443 | 122.6853 | 122.3708 | -0.085923 | 122.4539 | 122.5662 | 122.2489 | 122.3881 | -0.27859
2601.0938 | 122.5708 | -122.3831 | 0.13275 | 1.4211e-13 | -0.0090769 | 0.022393 | -0.0031241 | -0.0094525 | 0.010784 | -0.006028 | 0.0082229 | 0.01902 | 0.075134 | 0.028861 | 0.0046577 | 0.060567 | 0.015142 | 0.005325 | 0.13912 | 0.073622 | 0.3068 | 0.019363 | 0.060571 | 0.018674 | -0.010564 | 0.093665 | 0.19685 | -0.11587 | -0.17788 | 122.4025 | 0.006366 | 122.4437 | 122.3884 | -0.014038 | -0.059129 | 0.17405 | 122.2052 | -0.039086 | 122.4437 | 122.3726 | 0.16732 | 0.0641 | -0.24862 | 122.5222 | 122.4567 | 122.6899 | 122.3983 | -0.11339 | 122.4768 | 122.58 | 122.2672 | 122.4018 | -0.31064
2602.8438 | 122.6074 | -122.4014 | 0.10986 | 1.4211e-13 | -0.0088631 | 0.02218 | -0.0033377 | -0.0096661 | 0.01057 | 0.0016025 | 0.0092911 | 0.019234 | 0.075561 | 0.029075 | 0.0044439 | 0.069723 | 0.010564 | 0.014482 | 0.13454 | 0.078201 | 0.31137 | 0.014784 | 0.060571 | 0.027831 | -0.005985 | 0.084508 | 0.18769 | -0.11587 | -0.16415 | 122.4162 | 0.024676 | 122.4712 | 122.4159 | -0.000302 | -0.031662 | 0.20151 | 122.2373 | -0.025355 | 122.462 | 122.3954 | 0.15816 | 0.07783 | -0.22574 | 122.536 | 122.4796 | 122.7128 | 122.412 | -0.095079 | 122.4859 | 122.5891 | 122.2856 | 122.4293 | -0.27401
2604.5469 | 122.6624 | -122.3969 | 0.10071 | 1.4211e-13 | -0.0090769 | 0.022393 | -0.0037651 | -0.0092389 | 0.010784 | -0.006028 | 0.0086503 | 0.019234 | 0.075134 | 0.028861 | 0.0046577 | 0.060567 | 0.015142 | 0.009904 | 0.12538 | 0.069043 | 0.32053 | 0.014784 | 0.069728 | 0.018674 | -0.001407 | 0.089087 | 0.19227 | -0.12045 | -0.17788 | 122.4116 | 0.024674 | 122.4574 | 122.4068 | -0.00488 | -0.031665 | 0.21982 | 122.219 | -0.011621 | 122.4666 | 122.3954 | 0.17648 | 0.091564 | -0.22116 | 122.5222 | 122.4659 | 122.7174 | 122.412 | -0.085924 | 122.4859 | 122.5891 | 122.2764 | 122.4155 | -0.27859
2606.3125 | 122.5845 | -122.4243 | 0.1236 | 1.4211e-13 | -0.0086495 | 0.02218 | -0.0035515 | -0.0096661 | 0.010997 | -0.006028 | 0.0084367 | 0.019447 | 0.075347 | 0.029075 | 0.0046577 | 0.060567 | 0.005985 | 0.01906 | 0.13454 | 0.078201 | 0.32053 | 0.023942 | 0.06515 | 0.023253 | -0.001407 | 0.084508 | 0.19685 | -0.11129 | -0.16873 | 122.4483 | 0.010943 | 122.4849 | 122.4434 | -0.004882 | -0.045395 | 0.19694 | 122.2556 | -0.039088 | 122.4895 | 122.4229 | 0.16732 | 0.073255 | -0.23489 | 122.5589 | 122.5025 | 122.7448 | 122.4303 | -0.099654 | 122.5088 | 122.6212 | 122.313 | 122.4476 | -0.29232
2608.0156 | 122.7127 | -122.4152 | 0.082397 | 1.4211e-13 | -0.0086495 | 0.021966 | -0.0033377 | -0.0094525 | 0.010784 | 0.0016025 | 0.0088639 | 0.019661 | 0.075347 | 0.029075 | 0.0046577 | 0.060567 | 0.005985 | 0.009904 | 0.13454 | 0.073622 | 0.31595 | 0.0331 | 0.060571 | 0.018674 | -0.001407 | 0.07993 | 0.19685 | -0.11587 | -0.16873 | 122.4483 | 0.052142 | 122.4757 | 122.4251 | -0.023196 | -0.008775 | 0.23356 | 122.2464 | -0.002467 | 122.4757 | 122.4138 | 0.16732 | 0.11445 | -0.19827 | 122.5497 | 122.4888 | 122.7311 | 122.4211 | -0.049297 | 122.4951 | 122.612 | 122.2993 | 122.4338 | -0.25112
2609.7656 | 122.6898 | -122.4335 | 0.09613 | 1.4211e-13 | -0.0090769 | 0.02218 | -0.0033377 | -0.0094525 | 0.010784 | 0.0016025 | 0.0088639 | 0.01902 | 0.075134 | 0.029288 | 0.0048713 | 0.060567 | 0.010564 | 0.01906 | 0.13454 | 0.069043 | 0.32053 | 0.023942 | 0.060571 | 0.018674 | -0.005985 | 0.07993 | 0.19227 | -0.11587 | -0.16873 | 122.4574 | 0.038409 | 122.494 | 122.4525 | -0.004882 | -0.027087 | 0.2244 | 122.2647 | -0.0162 | 122.494 | 122.4275 | 0.16274 | 0.096142 | -0.212 | 122.568 | 122.5025 | 122.754 | 122.444 | -0.072188 | 122.5134 | 122.6257 | 122.3176 | 122.4521 | -0.26486
2611.5312 | 122.6257 | -122.4609 | 0.11902 | 1.4211e-13 | -0.0088631 | 0.02218 | -0.0033377 | -0.0092389 | 0.010784 | 0.0092325 | 0.0088639 | 0.019447 | 0.075561 | 0.029075 | 0.0044439 | 0.060567 | 0.010564 | 0.009904 | 0.13454 | 0.069043 | 0.32053 | 0.014784 | 0.06515 | 0.027831 | -0.010564 | 0.089087 | 0.19227 | -0.11587 | -0.15957 | 122.4757 | 0.01552 | 122.5215 | 122.4708 | -0.00488 | -0.049976 | 0.20151 | 122.3014 | -0.029932 | 122.5261 | 122.4504 | 0.14901 | 0.073253 | -0.23489 | 122.5955 | 122.53 | 122.7815 | 122.4715 | -0.10423 | 122.55 | 122.6532 | 122.3451 | 122.4888 | -0.27859
2613.2969 | 122.6028 | -122.5204 | 0.12817 | 1.4211e-13 | -0.0092905 | 0.021966 | -0.0033377 | -0.0094525 | 0.010784 | -0.006028 | 0.0088639 | 0.019234 | 0.075347 | 0.028861 | 0.0044439 | 0.055988 | 0.010564 | 0.009904 | 0.13912 | 0.064464 | 0.32053 | 0.023942 | 0.060571 | 0.023253 | -0.005985 | 0.07993 | 0.20143 | -0.11587 | -0.16873 | 122.5444 | 0.010943 | 122.5764 | 122.5304 | -0.014038 | -0.06371 | 0.19236 | 122.3517 | -0.048244 | 122.581 | 122.5145 | 0.16274 | 0.073255 | -0.24405 | 122.6596 | 122.5849 | 122.841 | 122.531 | -0.10423 | 122.6004 | 122.7219 | 122.4046 | 122.5437 | -0.2969
2615.0156 | 122.6395 | -122.4976 | 0.10071 | 1.4211e-13 | -0.0092905 | 0.022607 | -0.0031241 | -0.0092389 | 0.010784 | 0.0092325 | 0.0088639 | 0.019234 | 0.075347 | 0.029075 | 0.0044439 | 0.060567 | 0.010564 | 0.014482 | 0.12996 | 0.078201 | 0.31137 | 0.023942 | 0.069728 | 0.018674 | -0.001407 | 0.089087 | 0.19685 | -0.12045 | -0.16415 | 122.5215 | 0.029252 | 122.5581 | 122.512 | -0.00946 | -0.022507 | 0.21067 | 122.3334 | -0.011621 | 122.5673 | 122.4962 | 0.16274 | 0.096143 | -0.22116 | 122.6275 | 122.5758 | 122.8089 | 122.5081 | -0.076766 | 122.5866 | 122.6944 | 122.3771 | 122.5162 | -0.26486
2616.7656 | 122.6303 | -122.5113 | 0.13275 | 1.4211e-13 | -0.0088631 | 0.021966 | -0.0035515 | -0.0094525 | 0.01057 | -0.021289 | 0.0088639 | 0.019234 | 0.075561 | 0.029288 | 0.0044439 | 0.065145 | 0.010564 | 0.014482 | 0.13454 | 0.069043 | 0.31595 | 0.023942 | 0.06515 | 0.03241 | -0.005985 | 0.089087 | 0.19685 | -0.12503 | -0.16873 | 122.5352 | 0.001788 | 122.5764 | 122.5258 | -0.00946 | -0.063708 | 0.1832 | 122.3426 | -0.043664 | 122.5764 | 122.5053 | 0.16274 | 0.0641 | -0.25778 | 122.6458 | 122.5803 | 122.8272 | 122.5219 | -0.10881 | 122.6004 | 122.7081 | 122.3863 | 122.5437 | -0.30148
2618.5469 | 122.7631 | -122.4518 | 0.09613 | 1.4211e-13 | -0.0090769 | 0.02218 | -0.0033377 | -0.0092389 | 0.011211 | 0.0016025 | 0.0086503 | 0.019447 | 0.075134 | 0.029288 | 0.0046577 | 0.069723 | 0.015142 | 0.009904 | 0.13912 | 0.069043 | 0.31595 | 0.042258 | 0.06515 | 0.018674 | -0.015143 | 0.089087 | 0.19227 | -0.11587 | -0.17788 | 122.494 | 0.042987 | 122.5215 | 122.4617 | -0.032354 | -0.027087 | 0.21982 | 122.2739 | -0.007043 | 122.5169 | 122.4366 | 0.16274 | 0.096142 | -0.212 | 122.5909 | 122.5208 | 122.7677 | 122.4669 | -0.053872 | 122.5409 | 122.6441 | 122.3359 | 122.4705 | -0.27402
2620.2656 | 122.7814 | -122.5021 | 0.082397 | 1.4211e-13 | -0.0090769 | 0.02218 | -0.0033377 | -0.0094525 | 0.010784 | 0.0016025 | 0.0088639 | 0.019234 | 0.075347 | 0.028861 | 0.0046577 | 0.060567 | 0.001407 | 0.009904 | 0.14369 | 0.073622 | 0.31595 | 0.019363 | 0.06515 | 0.027831 | -0.001407 | 0.07993 | 0.19685 | -0.11587 | -0.17331 | 122.5215 | 0.061298 | 122.5627 | 122.512 | -0.009459 | -0.008775 | 0.23356 | 122.3288 | -0.002467 | 122.5673 | 122.5007 | 0.1719 | 0.11445 | -0.19827 | 122.6458 | 122.5758 | 122.8181 | 122.5035 | -0.063034 | 122.5821 | 122.699 | 122.3863 | 122.53 | -0.2557
2622.0312 | 122.6532 | -122.5204 | 0.10986 | 1.4211e-13 | -0.0086495 | 0.021752 | -0.0033377 | -0.0096661 | 0.01057 | -0.006028 | 0.0086503 | 0.019447 | 0.075561 | 0.028647 | 0.0046577 | 0.060567 | 0.005985 | 0.009904 | 0.12538 | 0.073622 | 0.32053 | 0.019363 | 0.055992 | 0.018674 | -0.005985 | 0.084508 | 0.20143 | -0.12045 | -0.16873 | 122.5398 | 0.015519 | 122.581 | 122.5304 | -0.009459 | -0.036241 | 0.21067 | 122.3517 | -0.025355 | 122.5764 | 122.5145 | 0.16274 | 0.091566 | -0.23031 | 122.6458 | 122.5941 | 122.841 | 122.5264 | -0.0905 | 122.605 | 122.7219 | 122.4 | 122.5391 | -0.27859
2623.7812 | 122.7859 | -122.4838 | 0.09613 | 1.4211e-13 | -0.0090769 | 0.021966 | -0.0035515 | -0.0094525 | 0.010784 | 0.0016025 | 0.0086503 | 0.01902 | 0.075561 | 0.029288 | 0.0044439 | 0.060567 | 0.010564 | 0.009904 | 0.13454 | 0.078201 | 0.3068 | 0.019363 | 0.060571 | 0.027831 | -0.005985 | 0.084508 | 0.19685 | -0.12045 | -0.16873 | 122.5032 | 0.038409 | 122.5444 | 122.4937 | -0.009459 | -0.017929 | 0.21067 | 122.3151 | -0.011622 | 122.5444 | 122.4778 | 0.16274 | 0.10072 | -0.21658 | 122.6184 | 122.562 | 122.7906 | 122.4944 | -0.076767 | 122.5683 | 122.6807 | 122.3634 | 122.5117 | -0.26486
2625.5 | 122.7905 | -122.4838 | 0.091553 | 1.4211e-13 | -0.0088631 | 0.021752 | -0.0035515 | -0.0094525 | 0.01057 | 0.0016025 | 0.0086503 | 0.019661 | 0.075134 | 0.029075 | 0.0046577 | 0.060567 | 0.010564 | 0.009904 | 0.13454 | 0.073622 | 0.31137 | 0.023942 | 0.060571 | 0.027831 | -0.005985 | 0.075351 | 0.19685 | -0.11587 | -0.16415 | 122.5078 | 0.042986 | 122.5444 | 122.4937 | -0.014038 | -0.017931 | 0.21982 | 122.3197 | -0.016202 | 122.5444 | 122.4778 | 0.15816 | 0.1053 | -0.20742 | 122.6184 | 122.5574 | 122.7952 | 122.4944 | -0.067611 | 122.5592 | 122.6807 | 122.368 | 122.5117 | -0.2557
2627.25 | 122.7356 | -122.5021 | 0.10529 | 1.4211e-13 | -0.0090769 | 0.022393 | -0.0033377 | -0.0096661 | 0.01057 | -0.006028 | 0.0088639 | 0.019447 | 0.075347 | 0.029075 | 0.0042303 | 0.060567 | 0.019721 | 0.005325 | 0.12996 | 0.08278 | 0.31595 | 0.023942 | 0.06515 | 0.03241 | 0.003172 | 0.07993 | 0.20143 | -0.12045 | -0.16873 | 122.5261 | 0.024674 | 122.5627 | 122.5075 | -0.018617 | -0.022506 | 0.21067 | 122.3334 | -0.025356 | 122.5673 | 122.5053 | 0.1719 | 0.096143 | -0.22574 | 122.6321 | 122.5849 | 122.8181 | 122.5219 | -0.081344 | 122.5821 | 122.7036 | 122.3817 | 122.5345 | -0.27401
2628.9531 | 122.7264 | -122.525 | 0.11902 | 1.4211e-13 | -0.0088631 | 0.02218 | -0.0031241 | -0.0098799 | 0.010997 | 0.0016025 | 0.0086503 | 0.019447 | 0.075561 | 0.029288 | 0.0046577 | 0.060567 | 0.010564 | 0.000747 | 0.13454 | 0.078201 | 0.31595 | 0.028521 | 0.06515 | 0.023253 | 0.003172 | 0.084508 | 0.19685 | -0.12045 | -0.16873 | 122.5535 | 0.01552 | 122.5856 | 122.5258 | -0.027774 | -0.040818 | 0.19693 | 122.3563 | -0.034511 | 122.5902 | 122.5282 | 0.1719 | 0.077832 | -0.23947 | 122.6596 | 122.6032 | 122.841 | 122.5356 | -0.090498 | 122.6095 | 122.7219 | 122.4046 | 122.5483 | -0.28775
2630.7188 | 122.8134 | -122.493 | 0.082397 | 1.4211e-13 | -0.0092905 | 0.021966 | -0.0033377 | -0.0092389 | 0.010997 | -0.006028 | 0.0088639 | 0.019234 | 0.075347 | 0.029502 | 0.0046577 | 0.069723 | 0.019721 | 0.005325 | 0.12996 | 0.069043 | 0.31595 | 0.023942 | 0.055992 | 0.027831 | -0.005985 | 0.089087 | 0.19685 | -0.12045 | -0.16873 | 122.5169 | 0.047563 | 122.5627 | 122.4983 | -0.018617 | -0.013354 | 0.23356 | 122.3243 | 0.00669 | 122.549 | 122.487 | 0.16274 | 0.11445 | -0.20285 | 122.6229 | 122.562 | 122.8089 | 122.5127 | -0.058455 | 122.5821 | 122.6898 | 122.3725 | 122.5208 | -0.25112
2632.4844 | 122.6898 | -122.5113 | 0.11902 | 1.4211e-13 | -0.0088631 | 0.02218 | -0.0031241 | -0.0096661 | 0.010784 | 0.0092325 | 0.0086503 | 0.019447 | 0.075347 | 0.028861 | 0.0046577 | 0.069723 | 0.005985 | 0.009904 | 0.12996 | 0.08278 | 0.32053 | 0.019363 | 0.06515 | 0.027831 | -0.001407 | 0.089087 | 0.19685 | -0.11587 | -0.16873 | 122.5307 | 0.010941 | 122.581 | 122.5212 | -0.009459 | -0.036239 | 0.20151 | 122.3426 | -0.029932 | 122.5764 | 122.5099 | 0.16732 | 0.077832 | -0.23489 | 122.6413 | 122.5941 | 122.8318 | 122.5173 | -0.099656 | 122.6004 | 122.7081 | 122.3954 | 122.5391 | -0.28775
2634.2344 | 122.8271 | -122.5021 | 0.086975 | 1.4211e-13 | -0.0092905 | 0.021966 | -0.0033377 | -0.0094525 | 0.011211 | -0.006028 | 0.0084367 | 0.019661 | 0.075775 | 0.029075 | 0.0046577 | 0.060567 | 0.005985 | 0.000747 | 0.13454 | 0.078201 | 0.31595 | 0.014784 | 0.06515 | 0.027831 | -0.010564 | 0.084508 | 0.19685 | -0.11587 | -0.16415 | 122.5169 | 0.047564 | 122.5627 | 122.5029 | -0.014037 | -0.008774 | 0.22898 | 122.338 | -0.002467 | 122.5673 | 122.4916 | 0.15358 | 0.10988 | -0.20285 | 122.6367 | 122.5803 | 122.8181 | 122.5081 | -0.072191 | 122.5866 | 122.699 | 122.3863 | 122.53 | -0.25112
2635.9844 | 122.8043 | -122.4976 | 0.073242 | 1.4211e-13 | -0.0088631 | 0.02218 | -0.0033377 | -0.0094525 | 0.010997 | -0.013659 | 0.0084367 | 0.019447 | 0.075347 | 0.029288 | 0.0046577 | 0.065145 | 0.010564 | 0.000747 | 0.13454 | 0.08278 | 0.31137 | 0.014784 | 0.06515 | 0.023253 | -0.010564 | 0.084508 | 0.19227 | -0.11587 | -0.17331 | 122.5123 | 0.061297 | 122.5627 | 122.4983 | -0.014037 | 0.009538 | 0.23813 | 122.3243 | 0.011266 | 122.5627 | 122.487 | 0.16274 | 0.11903 | -0.18911 | 122.6321 | 122.5803 | 122.8089 | 122.5081 | -0.058458 | 122.5821 | 122.6898 | 122.3817 | 122.5208 | -0.24655
2637.7344 | 122.8134 | -122.5113 | 0.07782 | 1.4211e-13 | -0.0088631 | 0.021966 | -0.0031241 | -0.0092389 | 0.01057 | -0.006028 | 0.0088639 | 0.019234 | 0.075347 | 0.029288 | 0.0048713 | 0.069723 | 0.015142 | -0.003831 | 0.13454 | 0.08278 | 0.31595 | 0.019363 | 0.06515 | 0.027831 | -0.001407 | 0.093665 | 0.19227 | -0.12045 | -0.16873 | 122.5307 | 0.056719 | 122.581 | 122.5075 | -0.023194 | 0.00496 | 0.23813 | 122.3426 | 0.015845 | 122.5764 | 122.5099 | 0.16732 | 0.11445 | -0.19827 | 122.6458 | 122.5941 | 122.8272 | 122.5264 | -0.058457 | 122.605 | 122.7036 | 122.3908 | 122.5391 | -0.24655
2639.4375 | 122.7264 | -122.5571 | 0.10986 | 1.4211e-13 | -0.0088631 | 0.021966 | -0.0035515 | -0.0094525 | 0.01057 | -0.006028 | 0.0086503 | 0.019661 | 0.075347 | 0.028861 | 0.0044439 | 0.060567 | 0.015142 | 0.009904 | 0.13912 | 0.087359 | 0.31595 | 0.019363 | 0.06515 | 0.027831 | -0.005985 | 0.084508 | 0.18769 | -0.11587 | -0.17331 | 122.5764 | 0.029254 | 122.6176 | 122.567 | -0.009459 | -0.022504 | 0.20609 | 122.3838 | -0.025355 | 122.6222 | 122.5511 | 0.16732 | 0.07783 | -0.22574 | 122.6962 | 122.6444 | 122.873 | 122.5722 | -0.0905 | 122.6416 | 122.7448 | 122.4412 | 122.5849 | -0.28317
2641.1875 | 122.7356 | -122.5616 | 0.10071 | 1.4211e-13 | -0.0088631 | 0.02218 | -0.0035515 | -0.0096661 | 0.010784 | -0.006028 | 0.0088639 | 0.019661 | 0.075134 | 0.028861 | 0.0044439 | 0.065145 | 0.010564 | 0.009904 | 0.13454 | 0.078201 | 0.31595 | 0.0331 | 0.069728 | 0.023253 | -0.001407 | 0.084508 | 0.19685 | -0.11587 | -0.16873 | 122.5947 | 0.033831 | 122.6268 | 122.5716 | -0.023196 | -0.022507 | 0.21524 | 122.3929 | -0.0162 | 122.6314 | 122.5602 | 0.16732 | 0.096143 | -0.21658 | 122.6962 | 122.6398 | 122.8776 | 122.5722 | -0.067608 | 122.6462 | 122.7585 | 122.4458 | 122.5849 | -0.26944

## Thermal Data
Fire Time | B Position - Conduit - 3' | B Position - Conduit - Middle | B Position - Conduit - 7' | D Position - 3' | D Position - Middle | D Position - 7'
-0.8083 | 9.0418 | 9.0827 | 9.0338 | 8.9801 | 8.8903 | 8.7706
0.1917 | 9.0326 | 9.0883 | 9.0395 | 8.9824 | 8.9101 | 8.6704
1.1917 | 9.0406 | 9.0923 | 9.0391 | 8.9871 | 8.8923 | 8.7554
2.1917 | 9.038 | 9.0882 | 9.0444 | 8.9876 | 8.9006 | 8.6466
3.1917 | 9.0461 | 9.0891 | 9.0451 | 8.9842 | 8.892 | 8.7771
4.1917 | 9.0496 | 9.1008 | 9.063 | 8.9927 | 9.1181 | 8.7013
5.1917 | 9.0505 | 9.1569 | 9.061 | 8.9246 | 9.7293 | 8.6732
6.1917 | 9.0555 | 9.434 | 9.1195 | 9.3969 | 11.4504 | 10.8215
7.1917 | 9.0662 | 9.5427 | 9.2013 | 11.241 | 12.1623 | 12.5965
8.1917 | 9.1331 | 9.8888 | 9.4058 | 12.0694 | 13.7864 | 13.8884
9.1917 | 9.2338 | 9.9792 | 9.7171 | 13.169 | 15.7478 | 14.9483
10.1917 | 9.3692 | 10.234 | 9.9832 | 14.6063 | 17.4639 | 16.1391
11.2073 | 9.3484 | 10.6679 | 10.0109 | 15.8514 | 20.2518 | 17.8872
12.1917 | 9.4196 | 10.6108 | 10.279 | 16.978 | 23.137 | 19.4645
13.1917 | 9.6674 | 10.7289 | 10.3324 | 18.2246 | 26.4006 | 21.5435
14.1917 | 9.6677 | 11.0427 | 10.5955 | 20.0581 | 30.9676 | 22.9447
15.1917 | 9.6731 | 11.1147 | 11.0597 | 22.2632 | 33.6456 | 23.7639
16.1917 | 9.8808 | 11.4218 | 10.8126 | 24.0299 | 36.8677 | 24.9382
17.1917 | 9.8852 | 11.5443 | 11.0401 | 25.2638 | 39.414 | 26.5563
18.1917 | 9.838 | 11.9797 | 11.1328 | 26.6451 | 42.6523 | 27.2002
19.1917 | 9.9971 | 12.3548 | 11.2255 | 28.4203 | 45.4962 | 28.8222
20.1917 | 10.1108 | 12.36 | 11.3791 | 30.9098 | 48.2634 | 30.3932
21.1917 | 10.1617 | 12.7074 | 11.7034 | 32.653 | 51.2442 | 32.0564
22.1917 | 10.3305 | 12.6562 | 11.6796 | 34.3921 | 53.3712 | 33.8226
23.1917 | 10.3406 | 12.6792 | 12.0165 | 35.7824 | 54.9264 | 35.4952
24.1917 | 10.32 | 13.0591 | 12.0327 | 38.1943 | 57.9454 | 37.6733
25.1917 | 10.3557 | 13.496 | 12.1605 | 40.843 | 62.1353 | 40.0453
26.1917 | 10.5186 | 13.5213 | 12.498 | 42.0897 | 65.104 | 42.3061
27.1917 | 10.6361 | 13.7482 | 12.4009 | 44.9757 | 68.7381 | 44.1135
28.1917 | 10.9905 | 13.822 | 12.6198 | 47.9028 | 72.7206 | 46.6029
29.1917 | 11.0251 | 13.9978 | 12.856 | 50.1968 | 77.6192 | 50.2151
30.1917 | 11.028 | 14.4194 | 12.8262 | 52.7918 | 81.6344 | 53.7105
31.1917 | 11.2303 | 14.7831 | 12.7999 | 54.744 | 84.4922 | 56.5614
32.1917 | 11.0476 | 15.0224 | 13.015 | 56.3035 | 88.0779 | 59.1174
33.1917 | 10.9801 | 15.1415 | 13.3633 | 57.7393 | 91.6721 | 61.349
34.1917 | 11.0077 | 15.7076 | 13.3882 | 60.1591 | 94.1967 | 64.0523
35.1917 | 11.2226 | 15.7807 | 13.714 | 60.6883 | 96.5079 | 65.6132
36.1917 | 11.319 | 16.0418 | 13.864 | 61.3881 | 98.576 | 67.6505
37.1917 | 11.3604 | 16.064 | 14.2577 | 61.8915 | 100.9796 | 69.3839
38.1917 | 11.6139 | 16.4366 | 14.3964 | 62.7837 | 102.6784 | 70.7959
39.1917 | 11.7467 | 16.6459 | 14.1999 | 64.6343 | 105.0114 | 72.5878
40.1917 | 11.8427 | 16.9963 | 14.66 | 66.7528 | 107.0789 | 74.1051
41.2073 | 12.1713 | 17.2574 | 14.7086 | 67.5869 | 108.5021 | 75.7625
42.1917 | 12.2165 | 17.7439 | 14.7997 | 70.6668 | 110.0312 | 77.2893
43.1917 | 12.273 | 17.9347 | 14.8981 | 73.3156 | 111.7312 | 78.7495
44.1917 | 12.2591 | 18.2984 | 15.1261 | 74.9074 | 113.4802 | 79.9101
45.1917 | 12.0615 | 18.3115 | 15.6279 | 76.6576 | 114.1526 | 80.0324
46.1917 | 12.2085 | 18.3645 | 15.6791 | 78.9171 | 114.2108 | 81.1325
47.1917 | 12.4539 | 18.6591 | 15.9324 | 79.7837 | 116.1642 | 82.9816
48.1917 | 12.7312 | 18.8262 | 16.2217 | 80.5114 | 117.5167 | 84.9271
49.1917 | 12.7249 | 19.4263 | 16.5201 | 82.0278 | 118.8344 | 85.747
50.1917 | 12.3812 | 19.7762 | 16.3269 | 84.8124 | 119.7534 | 85.9209
51.1917 | 12.2822 | 20.3313 | 16.5221 | 86.2489 | 120.017 | 86.7725
52.1917 | 12.9151 | 20.2865 | 16.7473 | 86.8829 | 120.5555 | 87.2906
53.1917 | 12.9245 | 20.983 | 16.9824 | 88.1511 | 121.0581 | 88.1125
54.1917 | 12.7778 | 21.1605 | 17.156 | 88.7559 | 120.9315 | 88.7133
55.1917 | 12.7228 | 21.5552 | 17.5462 | 89.0926 | 121.6042 | 89.4405
56.1917 | 12.9094 | 21.9393 | 17.4486 | 89.4169 | 122.8682 | 90.1299
57.1917 | 12.7385 | 22.4759 | 17.5269 | 89.546 | 124.3169 | 91.3367
58.1917 | 12.8371 | 22.8242 | 17.814 | 89.4269 | 125.0021 | 92.7591
59.1917 | 12.9611 | 22.9461 | 18.1 | 90.3593 | 125.0599 | 93.7926
60.1917 | 13.152 | 23.1093 | 18.1187 | 91.739 | 126.1198 | 94.8902
61.1917 | 13.4314 | 23.7937 | 18.1937 | 92.5231 | 127.34 | 96.175
62.1917 | 13.4872 | 23.9996 | 18.3363 | 93.1489 | 127.9448 | 97.5855
63.1917 | 13.8012 | 24.2673 | 18.5554 | 93.3301 | 127.5882 | 98.0199
64.1917 | 13.8717 | 24.5005 | 18.6241 | 94.4183 | 128.0564 | 98.1998
65.1917 | 13.9842 | 24.8046 | 18.6303 | 94.7215 | 129.018 | 98.6864
66.1917 | 14.0219 | 25.1923 | 18.751 | 96.3295 | 131.3831 | 100.4415
67.1917 | 14.0782 | 25.2353 | 18.73 | 97.3556 | 133.0746 | 103.2104
68.1917 | 14.0923 | 25.5437 | 18.8074 | 98.7178 | 135.3162 | 105.2096
69.2073 | 14.3574 | 26.1312 | 19.0499 | 101.1404 | 138.3439 | 108.098
70.1917 | 14.2675 | 26.2916 | 19.1655 | 102.5248 | 139.8528 | 110.4844
71.1917 | 14.2831 | 26.8321 | 19.3781 | 103.8903 | 141.0168 | 111.7611
72.1917 | 14.427 | 27.2585 | 19.69 | 103.9729 | 141.636 | 112.2767
73.1917 | 14.72 | 27.5841 | 19.6776 | 104.3276 | 142.8881 | 113.6169
74.1917 | 14.5175 | 27.881 | 19.7622 | 104.7191 | 143.5312 | 114.9342
75.1917 | 14.6306 | 28.4167 | 19.981 | 106.5558 | 143.7339 | 116.1959
76.1917 | 14.5504 | 28.5788 | 20.1251 | 107.647 | 144.6525 | 116.4752
77.1917 | 14.9799 | 28.9429 | 20.4751 | 108.1556 | 146.017 | 117.4314
78.1917 | 14.7804 | 29.6045 | 20.6187 | 108.6177 | 145.6732 | 118.5716
79.1917 | 14.7441 | 29.8934 | 20.7619 | 109.424 | 145.5557 | 118.5573
80.1917 | 15.2091 | 30.5881 | 20.96 | 109.9796 | 146.8177 | 119.7383
81.1917 | 15.2016 | 31.0416 | 20.8936 | 110.3829 | 147.8442 | 120.3653
82.1917 | 15.1277 | 31.1723 | 21.1149 | 111.5384 | 148.0574 | 121.9099
83.1917 | 15.5709 | 31.9764 | 21.2893 | 111.8561 | 148.9515 | 122.727
84.1917 | 15.5555 | 32.1618 | 21.4046 | 112.4691 | 148.8453 | 123.9151
85.1917 | 15.5586 | 32.4351 | 21.5844 | 112.8825 | 148.5503 | 124.6102
86.1917 | 15.8336 | 33.2687 | 21.6021 | 113.4761 | 148.5471 | 124.6797
87.1917 | 15.9065 | 33.2097 | 21.7619 | 114.1542 | 149.3483 | 124.4343
88.1917 | 15.9212 | 33.4747 | 21.8095 | 115.3159 | 151.6069 | 126.1118
89.1917 | 15.9537 | 33.7952 | 22.3004 | 118.5063 | 153.8452 | 128.2452
90.1917 | 16.1351 | 34.2977 | 22.7003 | 119.4841 | 153.8057 | 130.4695
91.1917 | 16.1903 | 34.8391 | 22.6354 | 121.007 | 155.0319 | 130.6501
92.1917 | 16.0803 | 35.1636 | 22.9443 | 121.5069 | 155.9397 | 130.4385
93.2073 | 16.3836 | 35.5038 | 22.8247 | 123.6342 | 157.1357 | 130.2847
94.1917 | 16.4821 | 35.7173 | 23.1698 | 123.0694 | 158.2676 | 133.2321
95.1917 | 16.5002 | 36.1057 | 23.1417 | 126.015 | 159.1858 | 135.0372
96.1917 | 16.5069 | 36.3822 | 23.5061 | 127.6665 | 160.9877 | 135.053
97.2073 | 16.4741 | 36.761 | 23.3303 | 129.2766 | 161.761 | 135.7472
98.1917 | 16.5933 | 37.2115 | 23.3689 | 129.5567 | 163.3789 | 136.0904
99.2073 | 16.5743 | 37.6507 | 23.9292 | 130.3551 | 164.2892 | 136.524
100.1917 | 16.6842 | 38.0155 | 24.0709 | 129.5135 | 164.8007 | 138.1699
101.1917 | 17.1535 | 38.4094 | 24.0752 | 129.9669 | 165.5657 | 139.438
102.1917 | 17.3096 | 38.8281 | 24.0861 | 130.1374 | 165.9321 | 140.3422
103.1917 | 17.1396 | 39.1269 | 24.2571 | 131.7988 | 167.2767 | 141.828
104.1917 | 17.0204 | 39.4224 | 24.3759 | 132.153 | 167.8986 | 142.1128
105.1917 | 17.1061 | 39.8273 | 24.4652 | 132.3693 | 167.9252 | 141.6638
106.1917 | 17.3138 | 40.0548 | 24.549 | 132.5214 | 168.7778 | 141.3884
107.1917 | 17.2178 | 40.4104 | 24.7263 | 131.8503 | 169.0472 | 141.2631
108.1917 | 17.316 | 40.9035 | 24.9146 | 131.287 | 169.3749 | 141.0522
109.1917 | 17.2668 | 41.2751 | 25.2289 | 131.4642 | 169.5097 | 140.3708
110.1917 | 17.3091 | 41.688 | 25.2787 | 131.4872 | 170.4406 | 140.6141
111.1917 | 17.7232 | 42.0552 | 25.3222 | 132.9894 | 172.0741 | 141.303
112.1917 | 17.7664 | 42.5629 | 25.5336 | 132.8666 | 173.4935 | 141.6897
113.1917 | 17.9149 | 43.269 | 25.7307 | 132.7944 | 174.2153 | 142.7681
114.1917 | 18.2795 | 43.8882 | 25.7917 | 133.3202 | 173.4351 | 142.1912
115.1917 | 18.3669 | 44.1075 | 25.9805 | 133.3464 | 173.8267 | 142.2542
116.1917 | 18.2521 | 44.7186 | 26.0128 | 132.8907 | 173.5166 | 143.3984
117.1917 | 18.1485 | 45.0209 | 26.1554 | 132.461 | 173.4732 | 143.5127
118.1917 | 18.4632 | 45.5366 | 26.359 | 132.9167 | 173.8016 | 144.5129
119.1917 | 18.5009 | 46.0335 | 26.4793 | 133.7176 | 174.637 | 145.2885
120.1917 | 18.8053 | 46.3682 | 26.649 | 136.1426 | 175.4846 | 145.4718
121.1917 | 18.8311 | 46.8309 | 26.7502 | 136.9615 | 175.6234 | 145.9342
122.1917 | 18.6927 | 47.2181 | 26.95 | 136.3593 | 175.3639 | 147.273
123.1917 | 19.0576 | 47.6105 | 27.0014 | 136.0026 | 176.439 | 147.2251
124.1917 | 19.255 | 47.9937 | 27.1885 | 135.3829 | 176.2172 | 148.1452
125.1917 | 19.0798 | 48.3061 | 27.4426 | 136.1735 | 176.384 | 147.5768
126.1917 | 19.3106 | 48.7429 | 27.4879 | 135.544 | 177.0677 | 147.2867
127.1917 | 19.2723 | 49.5046 | 27.6946 | 137.2536 | 178.562 | 147.1953
128.1917 | 19.2497 | 49.868 | 27.9194 | 136.7949 | 179.255 | 148.1504
129.1917 | 19.3889 | 50.3245 | 27.8466 | 136.8775 | 180.5261 | 149.7576
130.1917 | 19.5823 | 50.7131 | 27.8806 | 136.3071 | 179.8883 | 150.8573
131.1917 | 19.6592 | 51.0596 | 28.4159 | 136.3547 | 179.3865 | 150.2804
132.1917 | 19.7237 | 51.6144 | 28.4678 | 135.8897 | 179.9644 | 151.0373
133.1917 | 19.7751 | 52.0153 | 28.5844 | 135.5336 | 180.3279 | 151.6831
134.1917 | 20.0004 | 52.6323 | 28.892 | 136.0836 | 180.2428 | 151.8632
135.1917 | 19.9664 | 53.1669 | 28.8787 | 136.3569 | 179.5521 | 152.6469
136.1917 | 20.1184 | 53.5211 | 29.0663 | 136.7322 | 179.226 | 152.6068
137.1917 | 20.3236 | 53.7859 | 29.0823 | 136.9047 | 178.8396 | 152.6575
138.1917 | 20.3336 | 54.4247 | 29.1744 | 136.6788 | 178.679 | 152.7363
139.1917 | 20.4244 | 54.7214 | 29.2675 | 135.8666 | 178.042 | 153.4455
140.1917 | 20.5574 | 55.1375 | 29.3729 | 135.9973 | 177.6437 | 154.7181
141.1917 | 20.8016 | 55.481 | 29.5953 | 136.4982 | 178.6595 | 155.6659
142.1917 | 20.8268 | 55.8124 | 29.6626 | 137.281 | 177.9907 | 155.5491
143.1917 | 20.8653 | 56.5853 | 29.7973 | 137.1731 | 177.404 | 156.0399
144.1917 | 20.7958 | 56.838 | 29.9219 | 136.6428 | 177.8808 | 157.2516
145.1917 | 20.836 | 57.2897 | 29.9243 | 136.6507 | 178.1372 | 157.5603
146.1917 | 21.142 | 57.5647 | 30.148 | 136.2933 | 178.4485 | 159.2131
147.1917 | 21.0652 | 57.9815 | 30.1827 | 135.6242 | 178.9311 | 159.5351
148.1917 | 21.1339 | 58.7323 | 30.5605 | 135.7232 | 179.5555 | 160.8352
149.1917 | 21.2013 | 59.0852 | 30.7778 | 136.8407 | 179.4444 | 163.5512
150.1917 | 21.2715 | 59.9101 | 30.9504 | 137.6166 | 180.3528 | 163.4644
151.1917 | 21.4036 | 60.1878 | 30.9826 | 137.6376 | 181.934 | 163.9199
152.1917 | 21.6674 | 60.8047 | 31.2515 | 137.969 | 182.2902 | 164.9309
153.1917 | 22.0442 | 61.1513 | 31.3296 | 138.025 | 181.9646 | 164.9173
154.1917 | 21.8425 | 61.5456 | 31.5721 | 137.7745 | 181.539 | 164.6672
155.1917 | 21.8225 | 62.3809 | 31.6448 | 137.5051 | 181.1796 | 165.0691
156.1917 | 22.0165 | 62.7478 | 31.746 | 136.7486 | 180.3966 | 164.2458
157.1917 | 22.1933 | 63.1814 | 31.9112 | 136.8654 | 179.9262 | 164.4408
158.1917 | 22.328 | 63.5788 | 31.9753 | 136.2191 | 179.271 | 164.7927
159.1917 | 22.2361 | 64.0789 | 32.0647 | 137.0179 | 179.8963 | 165.7133
160.1917 | 22.5161 | 64.8668 | 32.3504 | 137.4307 | 179.9611 | 167.0459
161.1917 | 22.6342 | 64.9751 | 32.3133 | 136.2149 | 179.2954 | 167.402
162.2073 | 22.8171 | 65.4397 | 32.5688 | 136.0029 | 180.0122 | 167.6173
163.1917 | 22.7297 | 66.0769 | 32.7412 | 136.0127 | 179.957 | 167.9109
164.1917 | 22.9513 | 66.6566 | 32.8374 | 135.2098 | 180.3719 | 167.2595
165.1917 | 22.967 | 66.8869 | 32.9046 | 135.5676 | 179.5281 | 166.8504
166.1917 | 23.3044 | 67.5208 | 32.9346 | 135.883 | 178.4347 | 166.6463
167.1917 | 23.2919 | 67.9167 | 33.2348 | 135.7784 | 177.8209 | 166.5157
168.1917 | 23.2194 | 69.0227 | 33.4501 | 135.8322 | 177.0771 | 166.4732
169.1917 | 23.5128 | 69.1512 | 33.4957 | 135.4477 | 177.0624 | 165.6227
170.1917 | 23.6623 | 69.9439 | 33.6455 | 135.9887 | 178.191 | 165.3368
171.1917 | 23.566 | 70.2666 | 33.8603 | 135.9541 | 178.7023 | 164.4515
172.1917 | 23.4249 | 70.5701 | 34.0605 | 135.4017 | 178.6998 | 164.5132
173.1917 | 23.5098 | 70.8965 | 34.4096 | 136.3256 | 178.9941 | 164.9131
174.1917 | 23.7749 | 71.3388 | 34.3754 | 137.8097 | 179.7071 | 165.5147
175.1917 | 23.7585 | 71.7494 | 34.4092 | 139.2603 | 180.3398 | 167.0367
176.1917 | 23.7955 | 72.4958 | 34.6683 | 139.1395 | 180.8971 | 167.905
177.1917 | 23.8637 | 72.7714 | 34.6846 | 139.0539 | 180.4988 | 167.847
178.1917 | 23.8365 | 73.3016 | 34.8628 | 138.7813 | 180.7397 | 168.4273
179.1917 | 23.9579 | 73.5283 | 35.0471 | 138.9876 | 180.649 | 169.7188
180.1917 | 24.1931 | 74.0294 | 35.2591 | 138.4978 | 180.7927 | 169.7474
181.1917 | 24.383 | 74.4364 | 35.2615 | 139.5685 | 180.5125 | 170.0577
182.1917 | 24.4317 | 74.9028 | 35.5581 | 138.7802 | 180.9882 | 170.7788
183.1917 | 24.5142 | 75.5244 | 35.6028 | 140.4478 | 180.8834 | 171.0593
184.1917 | 24.419 | 76.0794 | 35.5593 | 140.4653 | 181.4144 | 171.3819
185.1917 | 24.7123 | 76.9277 | 35.8328 | 139.3352 | 180.6837 | 171.5591
186.1917 | 24.8051 | 77.4104 | 36.0982 | 138.8226 | 180.9245 | 171.1247
187.1917 | 24.8272 | 77.5728 | 36.1736 | 138.6364 | 180.8991 | 170.6817
188.1917 | 25.2003 | 78.086 | 36.2133 | 138.5958 | 180.0759 | 170.8764
189.1917 | 25.4313 | 78.6243 | 36.3389 | 138.8307 | 180.656 | 169.8316
190.1917 | 25.333 | 79.1118 | 36.7342 | 138.5733 | 180.6428 | 169.5291
191.1917 | 25.2197 | 79.6624 | 36.9711 | 138.6432 | 181.143 | 169.7927
192.1917 | 25.3624 | 80.0283 | 36.9454 | 138.6279 | 181.4613 | 169.4761
193.1917 | 25.6807 | 80.6116 | 36.994 | 138.8779 | 181.1741 | 169.1771
194.1917 | 25.7909 | 81.0829 | 37.2506 | 139.179 | 180.1519 | 168.1703
195.1917 | 25.9425 | 81.6116 | 37.1869 | 138.5482 | 179.2724 | 167.9817
196.1917 | 26.0634 | 82.1568 | 37.3044 | 138.3311 | 179.1108 | 168.473
197.1917 | 26.0989 | 82.6164 | 37.5346 | 138.4349 | 178.9222 | 168.7654
198.1917 | 26.2304 | 82.9656 | 37.6587 | 138.8528 | 179.1094 | 168.4975
199.1917 | 26.26 | 83.7598 | 37.818 | 139.3572 | 179.9304 | 168.1298
200.1917 | 26.6422 | 84.0764 | 37.9669 | 140.1313 | 181.3672 | 167.7845
201.1917 | 26.6961 | 84.6286 | 38.1374 | 139.8026 | 181.363 | 168.8299
202.1917 | 26.7746 | 85.1815 | 38.229 | 139.4862 | 181.483 | 168.8851
203.1917 | 26.7939 | 85.9423 | 38.3935 | 138.6915 | 180.9757 | 168.8782
204.1917 | 27.0566 | 85.9898 | 38.4374 | 138.8383 | 180.2247 | 167.887
205.1917 | 27.127 | 86.5321 | 38.6282 | 138.5366 | 180.1747 | 168.2587
206.1917 | 27.2779 | 87.0762 | 38.7579 | 138.6587 | 179.2043 | 168.249
207.1917 | 27.2937 | 87.5826 | 38.9157 | 138.7153 | 178.7027 | 167.6261
208.1917 | 27.5752 | 87.8866 | 39.0074 | 138.1074 | 177.9282 | 166.9798
209.1917 | 27.8289 | 88.6201 | 39.2455 | 138.1333 | 177.2084 | 165.9891
210.1917 | 28.1601 | 89.0601 | 39.3297 | 137.944 | 176.8214 | 165.7884
211.1917 | 28.2434 | 89.5106 | 39.4584 | 137.3841 | 175.7491 | 165.0551
212.1917 | 28.3271 | 90.1812 | 39.8885 | 137.2997 | 176.5527 | 164.4844
213.1917 | 28.253 | 90.6469 | 40.0652 | 137.1662 | 176.7057 | 164.0796
214.1917 | 28.2342 | 91.1359 | 40.0818 | 137.5566 | 176.1574 | 163.5071
215.1917 | 28.3586 | 91.6634 | 40.3938 | 137.8435 | 175.9873 | 163.1112
216.1917 | 28.5511 | 92.3027 | 40.5521 | 137.897 | 176.458 | 162.5964
217.1917 | 28.6191 | 92.72 | 40.6089 | 138.8757 | 177.0045 | 162.4725
218.1917 | 28.8265 | 93.1516 | 40.6476 | 139.3057 | 177.1422 | 161.9999
219.1917 | 28.9349 | 93.557 | 40.9013 | 139.439 | 176.8718 | 161.5243
220.1917 | 29.2626 | 94.1816 | 41.1075 | 139.0649 | 176.8898 | 163.0828
221.1917 | 29.3593 | 94.9272 | 41.2207 | 139.4319 | 176.7128 | 162.9456
222.1917 | 29.2525 | 95.4272 | 41.4674 | 139.8681 | 177.4318 | 162.5889
223.1917 | 29.3587 | 96.0744 | 41.6052 | 139.2599 | 177.6498 | 162.7363
224.1917 | 29.2937 | 96.6308 | 42.0646 | 138.9566 | 177.3335 | 162.2976
225.1917 | 29.4769 | 97.1133 | 41.9793 | 139.8389 | 177.5042 | 162.8335
226.1917 | 29.6175 | 97.6232 | 42.0869 | 140.805 | 177.4184 | 163.5792
227.1917 | 29.6988 | 98.0619 | 42.2278 | 142.1838 | 177.7599 | 163.0968
228.1917 | 29.8534 | 98.5452 | 42.4628 | 143.0298 | 179.1312 | 163.7113
229.1917 | 30.1397 | 99.106 | 42.3702 | 142.9188 | 179.6881 | 165.3338
230.1917 | 30.1499 | 99.8857 | 42.5324 | 143.3198 | 181.1141 | 165.8347
231.1917 | 30.1975 | 100.1593 | 42.5771 | 142.9134 | 180.1412 | 165.5224
232.1917 | 30.4481 | 100.6906 | 42.792 | 143.3041 | 179.6852 | 165.1099
233.1917 | 30.3299 | 101.2643 | 42.9445 | 144.1385 | 180.6137 | 165.0854
234.1917 | 30.3634 | 101.8411 | 43.2247 | 144.2372 | 181.1175 | 165.5576
235.1917 | 30.5341 | 102.2942 | 43.2176 | 144.0415 | 181.826 | 166.5512
236.1917 | 31.0922 | 102.6821 | 43.3354 | 144.2315 | 182.274 | 167.1703
237.1917 | 31.3488 | 103.1268 | 43.4991 | 144.8953 | 183.3321 | 168.0927
238.1917 | 31.4419 | 103.6235 | 43.6546 | 144.7773 | 184.7284 | 169.6756
239.1917 | 31.4834 | 104.3332 | 43.8033 | 145.5306 | 185.9227 | 171.7332
240.1917 | 31.5618 | 104.7361 | 43.9728 | 145.0821 | 185.928 | 171.749
241.1917 | 31.5427 | 105.1893 | 44.0992 | 145.2601 | 186.1275 | 171.6797
242.1917 | 31.7509 | 105.7231 | 44.1583 | 144.7807 | 188.1434 | 173.626
243.1917 | 32.0288 | 106.2438 | 44.3283 | 146.7538 | 188.6973 | 174.3845
244.1917 | 32.2361 | 106.8125 | 44.7404 | 146.3394 | 188.7545 | 173.6532
245.1917 | 32.2719 | 107.5434 | 44.9585 | 146.4287 | 189.3905 | 173.4867
246.1917 | 32.1834 | 107.8787 | 45.0084 | 145.992 | 189.3067 | 173.0161
247.1917 | 32.5754 | 108.4685 | 45.0395 | 146.6174 | 189.4633 | 173.4262
248.1917 | 32.5322 | 108.8762 | 45.0601 | 146.244 | 189.1951 | 173.4905
249.1917 | 32.7372 | 109.2996 | 45.1866 | 146.702 | 189.2205 | 173.131
250.1917 | 32.8023 | 109.8002 | 45.3963 | 146.8654 | 188.9655 | 172.8694
251.1917 | 33.0571 | 110.5464 | 45.5302 | 146.6938 | 189.8552 | 173.1306
252.1917 | 33.0677 | 111.3476 | 45.6667 | 146.4901 | 190.3186 | 174.8548
253.1917 | 33.1089 | 111.5077 | 45.8513 | 146.4496 | 190.6726 | 176.1563
254.1917 | 33.043 | 112.1707 | 46.0484 | 146.0853 | 191.7577 | 178.5582
255.1917 | 33.3584 | 112.8612 | 46.1581 | 145.4027 | 192.1046 | 179.941
256.1917 | 33.5078 | 113.6515 | 46.2478 | 146.6537 | 191.9341 | 179.9951
257.1917 | 33.6868 | 113.9717 | 46.4261 | 146.5151 | 191.5481 | 179.6899
258.1917 | 33.7231 | 114.5321 | 46.6406 | 146.2387 | 190.5327 | 179.5627
259.1917 | 33.868 | 115.3344 | 46.6966 | 145.9587 | 190.3577 | 178.9771
260.1917 | 33.9471 | 115.7314 | 47.0024 | 146.1796 | 190.7534 | 179.6632
261.1917 | 34.3018 | 116.1553 | 47.1497 | 146.4101 | 191.3024 | 179.4916
262.1917 | 34.4533 | 116.8569 | 47.2867 | 146.3307 | 191.5223 | 179.3165
263.1917 | 34.6895 | 117.233 | 47.3455 | 147.0259 | 192.994 | 179.1318
264.1917 | 34.6414 | 118.1219 | 47.6733 | 147.3721 | 194.2068 | 180.3362
265.1917 | 34.7006 | 118.3979 | 47.6847 | 147.0341 | 194.5035 | 180.8667
266.1917 | 34.8892 | 118.775 | 47.8838 | 146.7046 | 195.0226 | 181.5969
267.1917 | 35.4742 | 119.5573 | 48.0405 | 146.9176 | 194.4228 | 181.8944
268.1917 | 35.4344 | 120.3166 | 48.1969 | 147.5323 | 194.1563 | 181.8685
269.1917 | 35.5451 | 120.71 | 48.2463 | 147.9601 | 193.2614 | 180.9205
270.1917 | 35.5906 | 121.4763 | 48.547 | 148.3861 | 193.6858 | 181.426
271.1917 | 35.6776 | 121.5818 | 48.7477 | 148.6758 | 193.804 | 181.0495
272.1917 | 35.7258 | 122.2165 | 48.7989 | 149.2653 | 193.8169 | 181.0975
273.1917 | 35.8329 | 122.8306 | 48.9636 | 150.0848 | 194.263 | 183.6737
274.1917 | 36.0552 | 123.3239 | 49.0843 | 150.4679 | 195.0272 | 183.5916
275.1917 | 36.3557 | 123.8104 | 49.148 | 150.5577 | 195.4618 | 185.0028
276.1917 | 36.24 | 124.331 | 49.2608 | 150.9061 | 194.9627 | 184.7116
277.1917 | 36.478 | 124.9442 | 49.5035 | 151.5071 | 194.6504 | 185.1281
278.1917 | 36.8397 | 125.7818 | 49.5989 | 151.2133 | 194.0344 | 184.3898
279.1917 | 37.2026 | 126.1287 | 49.7843 | 150.6958 | 193.895 | 183.2038
280.1917 | 37.079 | 126.6677 | 49.8227 | 150.7212 | 193.7501 | 182.9689
281.1917 | 37.1409 | 127.0881 | 50.2423 | 151.4426 | 193.6763 | 183.2548
282.1917 | 37.0622 | 127.8019 | 50.3285 | 151.2102 | 192.7722 | 182.2707
283.1917 | 37.1694 | 128.2444 | 50.3255 | 151.5134 | 193.3942 | 181.6642
284.1917 | 37.4991 | 128.5199 | 50.4043 | 151.5298 | 194.6645 | 182.5807
285.1917 | 37.5327 | 129.2338 | 50.7648 | 152.4126 | 195.0009 | 184.2056
286.1917 | 37.6624 | 129.7598 | 50.8103 | 151.7427 | 194.7286 | 183.7373
287.1917 | 37.9627 | 130.4061 | 50.822 | 151.6199 | 194.603 | 184.3984
288.1917 | 37.9461 | 130.9086 | 51.2681 | 152.1543 | 194.4674 | 184.5721
289.1917 | 38.0639 | 131.4412 | 51.3773 | 151.8655 | 195.0656 | 184.3629
290.1917 | 38.1966 | 132.1905 | 51.4466 | 151.6416 | 195.3947 | 184.0212
291.1917 | 38.4032 | 132.7321 | 51.679 | 151.7402 | 195.6392 | 183.4177
292.1917 | 38.4301 | 133.0348 | 51.7588 | 152.8065 | 196.1865 | 182.9204
293.1917 | 38.5259 | 133.7636 | 51.9345 | 153.3319 | 196.7405 | 182.5631
294.1917 | 38.6992 | 134.4554 | 52.1419 | 153.5714 | 196.7842 | 182.7691
295.1917 | 38.8049 | 135.0044 | 52.132 | 152.913 | 196.3105 | 183.0316
296.1917 | 38.9473 | 135.5196 | 52.3434 | 152.4971 | 195.9533 | 183.5113
297.1917 | 39.3253 | 136.0247 | 52.4066 | 152.0483 | 195.5339 | 183.8649
298.1917 | 39.4587 | 136.3135 | 52.5777 | 151.9048 | 195.7256 | 183.8075
299.1917 | 39.5917 | 136.8924 | 52.8045 | 152.6504 | 197.032 | 184.0103
300.1917 | 39.9405 | 137.6213 | 52.8862 | 152.4209 | 197.6266 | 185.1351
301.1917 | 39.9673 | 138.1494 | 53.1348 | 152.5521 | 198.1599 | 185.6543
302.1917 | 39.9138 | 138.5883 | 53.2514 | 153.7766 | 199.9931 | 185.2777
303.1917 | 40.0869 | 139.0645 | 53.5508 | 153.1576 | 198.8811 | 186.4085
304.1917 | 40.3377 | 139.5197 | 53.5548 | 154.566 | 199.7239 | 186.9508
305.2073 | 40.4627 | 140.0906 | 53.7381 | 154.96 | 199.8771 | 187.076
306.1917 | 40.3233 | 141.0321 | 53.9169 | 156.0213 | 201.5013 | 187.9384
307.1917 | 40.3547 | 141.3551 | 54.1095 | 155.9423 | 202.1007 | 188.4092
308.1917 | 40.6851 | 141.6699 | 54.2234 | 155.4392 | 202.7989 | 191.0779
309.1917 | 40.788 | 142.1171 | 54.5066 | 156.7841 | 204.9078 | 191.8582
310.1917 | 41.0531 | 142.5051 | 54.7143 | 156.5274 | 206.1253 | 194.3496
311.2073 | 40.9658 | 143.0524 | 54.7477 | 157.0488 | 206.7565 | 195.7044
312.1917 | 41.6019 | 143.8538 | 54.7635 | 157.3954 | 207.3516 | 195.5457
313.1917 | 41.6759 | 144.2559 | 55.1383 | 157.4859 | 207.1137 | 195.4197
314.1917 | 41.7585 | 144.9926 | 55.4477 | 158.409 | 208.4528 | 196.1663
315.1917 | 41.5664 | 145.3332 | 55.5051 | 159.3249 | 208.0553 | 195.9828
316.1917 | 41.5814 | 146.0059 | 55.7317 | 159.2218 | 207.5915 | 194.9319
317.1917 | 41.8953 | 146.8496 | 55.7567 | 159.9382 | 208.1813 | 194.7531
318.1917 | 42.1914 | 147.0649 | 55.8962 | 159.5535 | 207.3235 | 194.4564
319.1917 | 42.3326 | 147.523 | 56.0204 | 159.3675 | 206.9351 | 193.6999
320.1917 | 42.4854 | 148.1706 | 56.2037 | 158.9278 | 206.4642 | 193.4359
321.1917 | 42.4902 | 148.7932 | 56.2572 | 160.0776 | 206.8019 | 193.6873
322.1917 | 42.4741 | 149.1983 | 56.2655 | 159.9407 | 207.0008 | 193.9838
323.1917 | 42.7052 | 149.7278 | 56.4102 | 160.5323 | 207.5053 | 194.0898
324.1917 | 42.6924 | 149.9725 | 56.407 | 160.3586 | 207.4794 | 195.4365
325.1917 | 42.8216 | 150.3984 | 56.7524 | 160.7429 | 208.2424 | 197.1315
326.1917 | 42.9216 | 150.7654 | 56.9107 | 161.1093 | 207.8119 | 197.0483
327.1917 | 43.0239 | 151.1735 | 57.0026 | 161.0416 | 208.3623 | 196.5983
328.1917 | 42.9624 | 151.5727 | 57.0821 | 160.9545 | 207.985 | 196.6129
329.1917 | 43.0095 | 152.0851 | 57.2246 | 161.3018 | 208.1788 | 196.5099
330.1917 | 43.365 | 152.5484 | 57.5133 | 161.7557 | 209.2629 | 197.2924
331.1917 | 43.499 | 153.044 | 57.6531 | 161.658 | 209.4398 | 197.4079
332.1917 | 43.8748 | 153.7276 | 57.6665 | 163.9401 | 211.7793 | 198.0936
333.1917 | 44.1591 | 154.3863 | 58.0736 | 163.4804 | 212.8324 | 199.0558
334.1917 | 44.0963 | 154.7981 | 58.1731 | 163.6394 | 212.6234 | 199.9662
335.1917 | 44.1802 | 155.088 | 58.2586 | 163.511 | 213.074 | 201.3411
336.1917 | 44.1359 | 155.4361 | 58.4682 | 163.2786 | 213.3518 | 203.0184
337.1917 | 44.3041 | 156.0476 | 58.5457 | 164.2586 | 214.4994 | 203.5481
338.1917 | 44.7228 | 156.367 | 58.5366 | 166.5881 | 214.3514 | 204.8547
339.1917 | 44.7618 | 156.791 | 58.6679 | 167.3391 | 214.6614 | 206.4806
340.1917 | 45.051 | 157.2546 | 58.8227 | 168.3685 | 214.4949 | 207.243
341.1917 | 45.4095 | 157.812 | 58.9223 | 169.4108 | 215.0999 | 207.347
342.1917 | 45.5651 | 158.332 | 59.0403 | 169.7892 | 215.3959 | 207.6782
343.1917 | 45.5006 | 158.8027 | 59.1852 | 169.7949 | 215.2898 | 208.0707
344.1917 | 45.4937 | 159.2178 | 59.4115 | 169.6233 | 216.0841 | 208.8691
345.1917 | 45.538 | 159.9674 | 59.5957 | 168.2503 | 215.8192 | 208.0436
346.1917 | 45.5152 | 160.1883 | 59.7482 | 167.6714 | 216.3334 | 208.8991
347.1917 | 45.6674 | 160.8692 | 59.7746 | 168.6493 | 216.74 | 210.9264
348.1917 | 45.798 | 160.9902 | 59.9875 | 168.3574 | 215.9493 | 211.1856
349.1917 | 45.939 | 161.666 | 60.1323 | 168.0502 | 216.9257 | 211.7048
350.1917 | 46.0646 | 162.1966 | 60.3349 | 167.959 | 217.7467 | 210.5335
351.1917 | 46.2638 | 162.4271 | 60.3944 | 168.7909 | 217.5959 | 209.9732
352.1917 | 46.2313 | 163.1168 | 60.62 | 168.5687 | 217.9045 | 209.8069
353.1917 | 46.2743 | 163.5243 | 60.6351 | 169.5896 | 218.4733 | 209.5843
354.1917 | 46.3763 | 163.9066 | 60.9331 | 168.256 | 218.6453 | 210.3865
355.1917 | 46.441 | 164.761 | 61.2118 | 167.9769 | 218.3696 | 210.303
356.1917 | 46.6706 | 164.7964 | 61.1268 | 167.9059 | 218.6144 | 209.8388
357.1917 | 46.7636 | 165.2819 | 61.3517 | 168.3852 | 218.4533 | 209.9024
358.1917 | 46.9217 | 165.6667 | 61.5869 | 169.5103 | 218.6441 | 211.1085
359.1917 | 47.07 | 166.0952 | 61.5169 | 170.1628 | 219.2568 | 211.6586
360.1917 | 47.3618 | 166.6446 | 61.667 | 169.9575 | 219.0323 | 211.2579
361.1917 | 47.395 | 166.9834 | 61.8391 | 169.1954 | 219.1776 | 210.9289
362.1917 | 47.6785 | 167.4113 | 62.0403 | 168.8623 | 220.9596 | 211.616
363.1917 | 47.7746 | 167.9828 | 62.1052 | 168.5753 | 220.7604 | 211.5166
364.1917 | 48.0922 | 168.4611 | 62.2426 | 168.1804 | 219.3915 | 211.0324
365.1917 | 48.1373 | 168.8583 | 62.4726 | 166.721 | 218.7108 | 209.7971
366.1917 | 48.0708 | 169.3856 | 62.5454 | 166.4172 | 218.2946 | 209.5795
367.1917 | 48.4702 | 169.5665 | 62.7688 | 166.0431 | 217.2602 | 208.3398
368.1917 | 48.5264 | 170.0614 | 62.881 | 167.1627 | 216.9237 | 207.2139
369.1917 | 48.4616 | 170.4575 | 63.0269 | 167.2692 | 216.7717 | 208.7242
370.1917 | 48.6039 | 171.1566 | 63.1783 | 166.5397 | 216.7211 | 207.5673
371.1917 | 48.7942 | 171.4585 | 63.3061 | 166.7929 | 216.2051 | 207.3284
372.1917 | 48.9641 | 171.9689 | 63.538 | 166.8495 | 216.0305 | 206.8454
373.1917 | 48.9452 | 172.2999 | 63.6503 | 166.3725 | 215.9185 | 206.0144
374.1917 | 49.205 | 172.7158 | 63.7352 | 166.3125 | 217.1221 | 205.3793
375.1917 | 49.375 | 173.1916 | 63.8309 | 166.4239 | 217.6872 | 205.5291
376.1917 | 49.5529 | 173.6451 | 63.9608 | 166.7515 | 216.1544 | 205.026
377.1917 | 49.634 | 174.3 | 64.1954 | 166.1938 | 215.1602 | 205.5535
378.1917 | 49.6948 | 174.8257 | 64.2168 | 165.575 | 214.5176 | 205.0579
379.1917 | 50.0981 | 175.0214 | 64.4536 | 165.5949 | 213.7778 | 205.297
380.1917 | 50.2751 | 175.4481 | 64.5145 | 164.2624 | 215.26 | 204.5392
381.1917 | 50.2334 | 175.7377 | 64.7351 | 163.7697 | 215.2815 | 205.2299
382.1917 | 50.3772 | 175.9806 | 64.8394 | 163.2271 | 215.2502 | 205.9495
383.1917 | 50.5569 | 176.4528 | 65.0533 | 164.1828 | 216.0369 | 207.3703
384.1917 | 50.559 | 176.8368 | 65.2498 | 166.5372 | 216.8769 | 208.0629
385.1917 | 50.6271 | 177.1656 | 65.2468 | 166.3408 | 217.4991 | 208.5861
386.1917 | 51.0016 | 177.6871 | 65.2652 | 166.5875 | 218.4136 | 209.011
387.1917 | 51.0989 | 177.9777 | 65.3564 | 166.0162 | 218.5329 | 208.7659
388.1917 | 51.1675 | 178.6092 | 65.616 | 166.6568 | 219.5933 | 209.2585
389.1917 | 51.1051 | 178.9885 | 65.7977 | 167.0735 | 219.51 | 209.1538
390.1917 | 51.1767 | 179.4314 | 65.9028 | 166.8771 | 219.3666 | 208.5005
391.1917 | 51.5953 | 179.7195 | 66.0014 | 166.8387 | 219.1742 | 208.365
392.1917 | 51.7402 | 180.2305 | 66.3348 | 165.9749 | 218.7825 | 208.2032
393.1917 | 51.9024 | 180.6702 | 66.3925 | 166.2909 | 219.0327 | 206.5473
394.1917 | 52.1237 | 181.1899 | 66.6582 | 165.2879 | 218.8658 | 205.7712
395.1917 | 52.0563 | 181.7287 | 66.6618 | 164.6112 | 218.3818 | 205.6061
396.1917 | 52.1034 | 182.2649 | 66.8255 | 164.3064 | 218.2655 | 205.3146
397.1917 | 52.1329 | 182.7639 | 66.8395 | 163.6033 | 217.5275 | 205.6183
398.1917 | 52.331 | 182.9887 | 67.0889 | 163.571 | 216.4968 | 203.9403
399.1917 | 52.8609 | 182.9941 | 67.2872 | 163.593 | 214.9656 | 202.8282
400.1917 | 53.0006 | 183.3618 | 67.3404 | 164.3277 | 216.4738 | 202.7857
401.1917 | 52.9855 | 183.8934 | 67.5688 | 164.858 | 217.2605 | 203.515
402.1917 | 53.1911 | 184.2292 | 67.7489 | 164.7607 | 216.9738 | 203.5725
403.1917 | 53.0094 | 184.5995 | 67.7953 | 165.6581 | 216.553 | 205.0987
404.1917 | 53.0485 | 185.3645 | 68.0124 | 166.3398 | 216.4572 | 205.3708
405.1917 | 53.1929 | 186.0183 | 68.0739 | 165.991 | 217.0198 | 205.3217
406.1917 | 53.2776 | 186.1618 | 68.2124 | 165.8313 | 216.5786 | 205.2796
407.1917 | 53.3513 | 186.3608 | 68.3195 | 165.746 | 217.7807 | 204.5702
408.1917 | 53.7567 | 187.0183 | 68.4133 | 165.4613 | 218.6281 | 205.6857
409.1917 | 53.8354 | 187.3007 | 68.5666 | 165.3193 | 218.8438 | 205.2446
410.1917 | 53.8427 | 187.77 | 68.7521 | 165.8867 | 218.4735 | 204.3389
411.1917 | 53.9247 | 188.4984 | 68.9307 | 165.6715 | 218.0464 | 203.2157
412.1917 | 54.3148 | 188.9639 | 69.0857 | 165.9285 | 217.987 | 203.0462
413.1917 | 54.4095 | 189.4661 | 69.1779 | 165.6515 | 216.5049 | 202.5065
414.1917 | 54.5196 | 189.6874 | 69.3546 | 165.0137 | 215.9579 | 201.5619
415.1917 | 54.6116 | 190.3647 | 69.6118 | 164.4275 | 216.1182 | 200.8269
416.1917 | 54.9759 | 190.5389 | 69.7966 | 163.7015 | 215.5787 | 200.222
417.1917 | 55.2088 | 190.9775 | 69.8427 | 163.1739 | 215.0631 | 199.6403
418.1917 | 55.3979 | 191.3242 | 69.9559 | 162.8634 | 214.991 | 200.5057
419.1917 | 55.4954 | 191.8107 | 70.074 | 163.0373 | 215.0685 | 200.5567
420.1917 | 55.4968 | 192.3553 | 70.2401 | 164.5365 | 214.8016 | 200.1837
421.1917 | 55.5802 | 192.738 | 70.3898 | 165.4442 | 214.5244 | 200.079
422.1917 | 55.6173 | 192.8835 | 70.5654 | 165.6905 | 213.8969 | 199.977
423.1917 | 55.7446 | 193.3536 | 70.8379 | 165.4117 | 213.3429 | 199.0663
424.1917 | 55.8727 | 193.9234 | 70.9941 | 165.7985 | 213.3734 | 198.4323
425.2073 | 56.1164 | 194.0894 | 71.0557 | 165.3493 | 213.7134 | 198.5374
426.1917 | 55.9677 | 194.7308 | 71.5076 | 165.7161 | 214.577 | 198.7141
427.1917 | 56.2752 | 194.985 | 71.4613 | 166.7122 | 215.0017 | 198.221
428.1917 | 56.4531 | 195.5393 | 71.6499 | 167.1033 | 215.3891 | 198.229
429.1917 | 56.5019 | 195.9779 | 71.8943 | 167.1331 | 216.0411 | 198.3385
430.1917 | 56.8526 | 196.276 | 71.9268 | 167.5417 | 215.3406 | 198.0227
431.1917 | 57.0752 | 196.842 | 72.0309 | 167.8112 | 215.434 | 197.2357
432.1917 | 57.0658 | 197.0628 | 72.4107 | 167.5147 | 215.1497 | 196.1979
433.1917 | 57.3286 | 197.5574 | 72.5242 | 167.6593 | 215.0263 | 195.8868
434.1917 | 57.321 | 197.8389 | 72.6356 | 167.565 | 215.1469 | 196.374
435.1917 | 57.2822 | 198.2619 | 72.7918 | 167.0764 | 214.6624 | 196.2352
436.1917 | 57.2898 | 198.5591 | 72.9963 | 168.1473 | 214.199 | 195.3924
437.1917 | 57.4841 | 198.9738 | 73.176 | 169.057 | 213.8988 | 195.3329
438.1917 | 57.5668 | 199.656 | 73.3753 | 169.4876 | 214.2372 | 194.9594
439.1917 | 57.7674 | 199.9909 | 73.3082 | 170.6667 | 214.2981 | 194.6962
440.1917 | 57.8975 | 200.1613 | 73.4075 | 170.3535 | 214.8745 | 194.6085
441.1917 | 58.1943 | 200.5651 | 73.51 | 170.1634 | 214.6166 | 194.5914
442.1917 | 58.2523 | 201.3229 | 73.6145 | 169.8789 | 215.5634 | 195.4178
443.1917 | 58.2467 | 201.5096 | 73.7538 | 169.8736 | 216.2692 | 196.5121
444.1917 | 58.4282 | 201.5953 | 73.8763 | 169.8441 | 215.6975 | 197.9179
445.1917 | 58.5864 | 201.976 | 74.1098 | 170.2291 | 215.8058 | 198.5407
446.1917 | 58.7236 | 202.4824 | 74.2296 | 170.8559 | 216.4878 | 198.6322
447.1917 | 58.6751 | 202.9687 | 74.3495 | 170.431 | 217.2828 | 199.967
448.1917 | 58.9423 | 203.4898 | 74.6181 | 171.007 | 218.4122 | 201.5594
449.1917 | 59.1054 | 203.5853 | 74.6212 | 171.9086 | 218.4796 | 202.2819
450.1917 | 59.3794 | 203.8572 | 74.8203 | 171.8247 | 217.5268 | 202.6031
451.1917 | 59.6092 | 204.2479 | 75.0288 | 171.373 | 217.1243 | 203.0162
452.1917 | 59.6428 | 204.5728 | 75.0829 | 170.986 | 216.8948 | 202.8237
453.1917 | 59.6751 | 204.8435 | 75.2719 | 170.865 | 216.457 | 202.1832
454.1917 | 59.8579 | 205.5319 | 75.4434 | 170.2622 | 216.2049 | 201.3106
455.1917 | 59.9178 | 206.3589 | 75.5151 | 169.5312 | 216.0221 | 201.2105
456.1917 | 60.1043 | 206.3716 | 75.5575 | 168.6818 | 216.0204 | 201.138
457.1917 | 60.2651 | 206.8041 | 75.7901 | 168.1813 | 216.4034 | 202.1779
458.1917 | 60.297 | 207.7457 | 76.2192 | 167.6512 | 215.4929 | 202.7236
459.1917 | 60.3029 | 207.7439 | 76.2688 | 166.4886 | 215.7222 | 202.5891
460.1917 | 60.4638 | 208.1844 | 76.3883 | 167.1137 | 215.3602 | 202.1704
461.1917 | 60.6682 | 208.5889 | 76.3923 | 166.9664 | 216.3101 | 202.7401
462.1917 | 60.8736 | 208.7816 | 76.5124 | 166.8828 | 216.4614 | 202.8125
463.1917 | 61.4794 | 208.8716 | 76.5853 | 166.7581 | 215.8008 | 203.3568
464.1917 | 61.2624 | 209.4723 | 76.906 | 167.2124 | 216.2431 | 203.3773
465.1917 | 61.2941 | 209.9503 | 77.1041 | 166.9033 | 215.2672 | 203.5696
466.1917 | 61.4511 | 210.1758 | 77.211 | 167.2325 | 214.6131 | 203.1392
467.1917 | 61.5156 | 210.6135 | 77.3184 | 167.407 | 214.8537 | 202.5527
468.1917 | 61.5688 | 211.2525 | 77.3995 | 167.5758 | 215.3423 | 202.5888
469.1917 | 61.9489 | 211.4097 | 77.617 | 167.4674 | 214.9401 | 202.253
470.1917 | 61.9653 | 211.8283 | 77.7892 | 167.3453 | 215.9596 | 201.615
471.1917 | 62.1038 | 212.3387 | 77.9538 | 167.2593 | 216.8574 | 201.3907
472.1917 | 62.1226 | 212.784 | 78.0434 | 167.2988 | 215.2349 | 201.04
473.1917 | 62.3659 | 213.0644 | 78.076 | 166.9855 | 214.2502 | 201.1519
474.1917 | 62.5041 | 213.9309 | 78.2321 | 167.2444 | 215.0557 | 202.4483
475.1917 | 62.5763 | 214.4472 | 78.2483 | 167.1761 | 215.0705 | 202.2918
476.1917 | 62.6742 | 214.3816 | 78.3912 | 166.3229 | 215.4695 | 202.5883
477.1917 | 62.7888 | 215.0221 | 78.5351 | 166.5519 | 216.6048 | 203.8114
478.1917 | 62.8353 | 215.1962 | 78.6373 | 165.8057 | 217.026 | 204.2402
479.1917 | 62.8068 | 215.5903 | 78.916 | 167.002 | 217.831 | 204.6523
480.1917 | 62.9965 | 215.9806 | 79.0962 | 166.9239 | 218.2135 | 205.2957
481.1917 | 63.2027 | 216.2311 | 79.4274 | 167.1331 | 218.2922 | 204.7399
482.1917 | 63.5051 | 217.3072 | 79.6163 | 167.1031 | 218.2299 | 204.0981
483.1917 | 63.5971 | 217.3311 | 79.6284 | 167.8451 | 218.5519 | 203.7728
484.1917 | 63.6851 | 217.539 | 79.8732 | 169.4284 | 218.7974 | 203.0188
485.1917 | 63.9987 | 218.1276 | 80.0041 | 170.731 | 219.1211 | 204.2342
486.1917 | 63.8677 | 218.2844 | 80.0464 | 171.0458 | 219.105 | 203.8917
487.1917 | 64.1153 | 218.6642 | 80.2018 | 171.0919 | 219.0007 | 203.469
488.1917 | 64.1915 | 218.9639 | 80.4423 | 171.0508 | 219.316 | 203.4077
489.1917 | 64.2672 | 219.5674 | 80.4996 | 171.3646 | 219.8808 | 203.6977
490.1917 | 64.5019 | 220.0035 | 80.5986 | 171.087 | 219.4359 | 203.5264
491.1917 | 64.7059 | 220.2324 | 80.6596 | 170.8249 | 219.1913 | 203.6646
492.1917 | 65.0847 | 221.1416 | 80.8114 | 170.4848 | 218.7995 | 203.2611
493.1917 | 65.1424 | 221.2204 | 81.0289 | 169.5384 | 217.9513 | 202.7904
494.1917 | 65.1567 | 221.4915 | 81.1793 | 169.7104 | 217.5066 | 202.1269
495.1917 | 65.049 | 221.9166 | 81.428 | 172.1613 | 218.9498 | 201.8399
496.1917 | 65.1186 | 222.4103 | 81.5879 | 174.1996 | 220.3603 | 202.3788
497.1917 | 65.3483 | 222.5625 | 81.8579 | 174.4016 | 221.6991 | 203.4262
498.1917 | 65.4464 | 223.1084 | 82.1101 | 174.3697 | 223.6744 | 204.493
499.1917 | 65.7859 | 223.684 | 82.1327 | 174.3289 | 223.9021 | 205.1096
500.1917 | 65.7248 | 223.9192 | 82.3042 | 174.1181 | 222.9418 | 205.1922
501.1917 | 65.811 | 224.1156 | 82.481 | 174.5594 | 222.9906 | 205.6043
502.1917 | 65.8504 | 224.5566 | 82.4965 | 174.1516 | 222.9863 | 205.497
503.1917 | 66.0029 | 225.2557 | 82.7087 | 175.6385 | 224.1777 | 205.3819
504.1917 | 66.2794 | 225.9485 | 82.9774 | 176.1079 | 225.1374 | 206.224
505.1917 | 66.4521 | 226.0389 | 83.0074 | 175.8811 | 225.4215 | 206.0899
506.1917 | 66.6827 | 226.4742 | 83.2635 | 175.5726 | 225.4159 | 205.6761
507.1917 | 66.9243 | 226.7361 | 83.6758 | 174.7386 | 225.2286 | 205.5049
508.1917 | 66.938 | 227.3443 | 83.6094 | 175.6017 | 224.9865 | 205.4915
509.1917 | 67.1916 | 227.7818 | 83.8347 | 175.4822 | 224.494 | 205.2132
510.1917 | 67.3468 | 227.8119 | 83.8585 | 176.0071 | 224.248 | 204.389
511.1917 | 67.4326 | 228.1634 | 83.9966 | 175.1483 | 224.6905 | 204.9764
512.1917 | 67.5692 | 228.7478 | 84.0991 | 177.2362 | 225.2597 | 205.2301
513.1917 | 67.65 | 229.2921 | 84.2366 | 177.0299 | 226.2341 | 205.5965
514.1917 | 67.9084 | 229.9111 | 84.6269 | 177.4702 | 227.4743 | 205.716
515.1917 | 68.0118 | 230.1461 | 84.5778 | 177.6762 | 227.6836 | 206.183
516.1917 | 68.0355 | 230.3091 | 84.6699 | 178.5138 | 228.6637 | 207.1563
517.1917 | 68.2019 | 230.6679 | 84.8419 | 177.7965 | 229.5113 | 207.4641
518.1917 | 68.3799 | 231.7608 | 85.0134 | 176.3794 | 229.561 | 207.7251
519.1917 | 68.2448 | 231.9013 | 85.1928 | 176.3522 | 228.8999 | 207.638
520.1917 | 68.4154 | 232.0591 | 85.47 | 176.3514 | 229.5179 | 207.6227
521.1917 | 68.5051 | 232.4618 | 85.4702 | 176.9466 | 229.4177 | 207.5043
522.1917 | 68.7705 | 232.5349 | 85.4844 | 176.5136 | 229.1509 | 207.7974
523.1917 | 68.8612 | 233.0345 | 85.7265 | 175.8968 | 228.9906 | 208.4253
524.1917 | 68.8744 | 233.5013 | 85.8359 | 175.0259 | 228.9439 | 208.4968
525.1917 | 68.9133 | 233.7421 | 86.0415 | 174.9178 | 229.431 | 208.7219
526.1917 | 69.0482 | 234.2779 | 86.2687 | 174.422 | 228.9168 | 209.2617
527.1917 | 69.3 | 234.5909 | 86.3155 | 175.8572 | 228.5526 | 210.3303
528.1917 | 69.6298 | 235.0254 | 86.4201 | 176.1264 | 228.8224 | 209.9541
529.1917 | 69.7405 | 235.4532 | 86.6665 | 175.7735 | 227.8759 | 209.7907
530.1917 | 70.2004 | 235.5826 | 86.8397 | 175.0053 | 227.2199 | 210.3592
531.1917 | 70.1193 | 236.0714 | 87.0271 | 174.6513 | 226.455 | 209.9767
532.1917 | 70.092 | 236.5716 | 87.0323 | 174.7498 | 226.4905 | 210.2997
533.1917 | 70.0272 | 236.741 | 87.1502 | 175.288 | 226.5635 | 210.5208
534.1917 | 70.2349 | 236.8938 | 87.2461 | 175.8717 | 227.1297 | 210.5572
535.1917 | 70.4695 | 237.1793 | 87.4081 | 178.4787 | 229.0939 | 213.0506
536.1917 | 70.4982 | 237.6226 | 87.6752 | 181.1098 | 231.5105 | 214.2262
537.1917 | 70.5094 | 237.9113 | 87.8256 | 181.3345 | 232.477 | 215.5667
538.1917 | 70.6518 | 238.4763 | 88.0051 | 182.1448 | 232.4239 | 214.9753
539.1917 | 70.8025 | 239.2033 | 88.216 | 182.2728 | 233.4511 | 215.1636
540.1917 | 70.9758 | 239.4688 | 88.3336 | 181.6832 | 233.4632 | 214.4334
541.1917 | 71.3604 | 239.8579 | 88.501 | 181.5847 | 232.9584 | 213.7104
542.1917 | 71.3691 | 240.1467 | 88.6131 | 181.1238 | 233.455 | 213.0202
543.1917 | 71.4762 | 240.5038 | 88.7837 | 180.2803 | 233.7105 | 213.1575
544.1917 | 71.8247 | 240.6042 | 88.9372 | 180.1116 | 233.3071 | 213.5359
545.1917 | 71.9011 | 240.9705 | 89.16 | 179.8787 | 233.2184 | 213.6266
546.1917 | 71.811 | 241.4518 | 89.2923 | 180.4063 | 232.9389 | 213.0334
547.1917 | 71.9651 | 242.0978 | 89.6085 | 179.1728 | 232.8739 | 212.3042
548.1917 | 72.0845 | 242.4487 | 89.5297 | 179.3439 | 232.6006 | 211.3486
549.1917 | 72.2787 | 242.4257 | 89.6233 | 180.8729 | 232.6607 | 210.9874
550.1917 | 72.4816 | 242.5879 | 89.8194 | 181.3175 | 231.8026 | 210.2207
551.1917 | 72.4839 | 242.9815 | 90.0692 | 181.3251 | 231.7577 | 209.8845
552.1917 | 72.5323 | 243.5804 | 90.0305 | 182.7722 | 231.8292 | 208.6611
553.1917 | 72.7382 | 243.7347 | 90.3741 | 182.6743 | 231.6553 | 207.9754
554.1917 | 72.9795 | 244.2623 | 90.5064 | 182.3894 | 231.0247 | 207.3129
555.1917 | 73.1192 | 244.5271 | 90.451 | 183.147 | 230.5723 | 206.5749
556.1917 | 73.1264 | 244.8215 | 90.7719 | 183.2705 | 230.1015 | 206.2614
557.1917 | 73.5793 | 245.0485 | 90.9537 | 182.8317 | 229.5971 | 206.3532
558.1917 | 73.5583 | 245.1858 | 91.1158 | 183.0567 | 229.3442 | 207.4528
559.1917 | 73.6765 | 245.8038 | 91.254 | 183.1677 | 228.8667 | 207.1096
560.1917 | 73.786 | 246.2108 | 91.3953 | 183.2106 | 227.8844 | 206.4576
561.1917 | 74.2417 | 246.5119 | 91.6103 | 182.2624 | 227.2726 | 206.162
562.1917 | 74.1277 | 246.6553 | 91.7249 | 182.2704 | 227.6657 | 206.2783
563.1917 | 73.9936 | 247.2641 | 91.8995 | 182.4791 | 227.5837 | 206.5752
564.1917 | 74.278 | 247.3945 | 91.9465 | 181.4768 | 227.2959 | 205.3206
565.1917 | 74.3927 | 247.6401 | 92.2319 | 180.8447 | 227.0322 | 206.1105
566.1917 | 74.4383 | 247.9063 | 92.3624 | 181.9011 | 228.0863 | 206.6182
567.1917 | 74.3752 | 248.3916 | 92.5759 | 182.8096 | 229.2822 | 208.0297
568.1917 | 74.651 | 248.6644 | 92.7881 | 182.3621 | 228.4605 | 207.4397
569.1917 | 75.0406 | 249.0686 | 92.8053 | 182.5899 | 228.7884 | 207.7115
570.1917 | 75.1212 | 249.513 | 92.9577 | 181.4095 | 229.2876 | 208.5581
571.1917 | 75.2572 | 249.7665 | 93.0947 | 181.2908 | 229.6346 | 208.8063
572.1917 | 75.3339 | 250.1016 | 93.4338 | 180.3876 | 228.7866 | 208.5654
573.1917 | 75.3026 | 250.4705 | 93.4046 | 180.349 | 228.2645 | 207.8375
574.1917 | 75.4637 | 251.1652 | 93.4893 | 179.6057 | 227.6853 | 207.1448
575.1917 | 75.6399 | 251.1861 | 93.7993 | 179.8653 | 227.5714 | 206.6819
576.1917 | 75.8331 | 251.8339 | 93.8605 | 180.0581 | 227.6376 | 207.3394
577.1917 | 75.8569 | 251.9545 | 94.2213 | 179.803 | 227.4249 | 206.8883
578.1917 | 75.962 | 252.3708 | 94.294 | 179.1868 | 227.0806 | 206.2668
579.1917 | 76.3781 | 252.9976 | 94.3517 | 178.9833 | 226.8475 | 206.3023
580.1917 | 76.4087 | 253.1034 | 94.5007 | 179.387 | 226.7863 | 206.0014
581.1917 | 76.603 | 253.2678 | 94.5647 | 179.6327 | 227.1013 | 206.9734
582.1917 | 76.8223 | 253.9595 | 94.6644 | 180.0941 | 228.0294 | 207.5918
583.1917 | 76.9422 | 254.1812 | 94.9359 | 179.5364 | 228.0815 | 208.0008
584.1917 | 76.9618 | 254.2842 | 95.0445 | 179.4486 | 228.0696 | 207.9472
585.1917 | 77.1535 | 254.5817 | 95.1953 | 179.6428 | 228.1147 | 207.524
586.1917 | 77.1087 | 255.1625 | 95.458 | 179.4588 | 227.6918 | 207.337
587.1917 | 77.1508 | 255.3328 | 95.5231 | 178.9488 | 226.8289 | 207.242
588.1917 | 77.3338 | 256.0527 | 95.6588 | 178.5298 | 226.1037 | 206.592
589.1917 | 77.5545 | 256.3309 | 95.9304 | 177.8835 | 225.4059 | 205.6984
590.1917 | 77.6472 | 256.5425 | 95.9024 | 177.2983 | 225.3188 | 204.7974
591.1917 | 77.7483 | 256.5722 | 96.1641 | 177.1514 | 224.2316 | 204.7038
592.1917 | 77.7953 | 256.9782 | 96.3825 | 178.5129 | 224.8035 | 205.438
593.1917 | 78.0537 | 257.7682 | 96.5766 | 179.362 | 223.4323 | 205.6244
594.1917 | 78.007 | 258.1733 | 96.5543 | 179.0777 | 224.035 | 206.6201
595.1917 | 78.1775 | 258.8238 | 96.7034 | 179.275 | 225.4094 | 206.7516
596.1917 | 78.3823 | 259.1433 | 96.8433 | 179.8436 | 225.6839 | 207.081
597.1917 | 78.6428 | 259.2021 | 97.0285 | 180.2269 | 224.4058 | 206.4433
598.1917 | 78.9036 | 259.4918 | 97.1636 | 180.6753 | 224.9122 | 206.4422
599.1917 | 79.2051 | 259.6698 | 97.4612 | 182.9925 | 225.9616 | 206.6406
600.1917 | 79.1385 | 259.8944 | 97.5593 | 184.3395 | 226.6246 | 207.3563
601.1917 | 79.1379 | 260.1079 | 97.7211 | 184.253 | 227.2693 | 208.7621
602.1917 | 79.1809 | 260.4099 | 97.8612 | 184.3779 | 228.3896 | 210.3725
603.1917 | 79.0978 | 261.0333 | 98.1192 | 184.5026 | 228.5441 | 211.8001
604.1917 | 79.3001 | 261.5266 | 98.2007 | 184.7182 | 229.3455 | 212.0655
605.1917 | 79.485 | 261.7795 | 98.4455 | 185.4729 | 229.8728 | 211.5558
606.1917 | 79.6321 | 262.1098 | 98.6758 | 185.7122 | 229.5868 | 210.7662
607.1917 | 79.8497 | 262.3827 | 98.7873 | 185.3148 | 229.3728 | 210.9959
608.1917 | 79.9493 | 262.4271 | 99.1162 | 186.0507 | 229.8635 | 211.8406
609.1917 | 80.0035 | 262.7652 | 99.7029 | 186.2544 | 229.3328 | 211.3304
610.1917 | 79.9658 | 262.9913 | 99.7911 | 185.9629 | 228.2121 | 210.3313
611.1917 | 80.1226 | 263.2063 | 99.698 | 186.301 | 226.8344 | 209.4057
612.1917 | 80.2946 | 263.6441 | 99.9726 | 186.7672 | 226.6131 | 208.6593
613.1917 | 80.3443 | 264.0313 | 99.8579 | 185.9733 | 227.2311 | 208.4217
614.1917 | 80.6231 | 264.2551 | 100.0177 | 188.0025 | 228.3226 | 209.3957
615.1917 | 80.8614 | 264.9027 | 100.0792 | 188.6753 | 228.6971 | 210.4428
616.1917 | 80.7499 | 264.7691 | 100.389 | 187.9222 | 227.933 | 209.4519
617.1917 | 80.8292 | 265.2609 | 100.6495 | 187.1426 | 227.9079 | 210.0977
618.1917 | 81.0757 | 265.3441 | 100.6353 | 187.607 | 228.3603 | 210.4413
619.1917 | 81.1928 | 265.7363 | 100.7309 | 188.4472 | 228.4768 | 210.1064
620.1917 | 81.2578 | 266.0774 | 100.8639 | 187.9446 | 228.2784 | 209.4428
621.1917 | 81.3608 | 266.2743 | 101.0434 | 188.0833 | 228.6491 | 209.134
622.1917 | 81.5404 | 266.9673 | 101.4139 | 187.7994 | 227.9014 | 208.4895
623.1917 | 81.8004 | 267.4268 | 101.271 | 187.6259 | 227.8037 | 208.6159
624.1917 | 81.9001 | 267.516 | 101.5781 | 187.2879 | 227.18 | 208.4553
625.1917 | 82.0072 | 267.6832 | 101.8202 | 186.973 | 226.5883 | 207.871
626.1917 | 82.2414 | 267.9749 | 101.8346 | 186.6676 | 226.24 | 207.5292
627.1917 | 82.2742 | 267.9663 | 102.0563 | 186.567 | 225.4426 | 207.5021
628.1917 | 82.2661 | 268.12 | 102.4054 | 186.8393 | 225.2636 | 207.1567
629.1917 | 82.304 | 268.7715 | 102.545 | 187.3515 | 225.2511 | 206.8951
630.1917 | 82.4502 | 268.8005 | 102.7394 | 188.8338 | 224.6519 | 207.1917
631.1917 | 82.9331 | 269.2656 | 102.8195 | 189.2488 | 225.4165 | 206.8192
632.1917 | 82.8887 | 269.4734 | 103.0337 | 189.8568 | 225.8634 | 206.9502
633.1917 | 82.8709 | 269.6091 | 103.2159 | 188.0942 | 226.0111 | 207.1554
634.1917 | 83.1789 | 269.8975 | 103.4912 | 187.2883 | 225.8996 | 207.1671
635.1917 | 83.2925 | 270.0285 | 103.7184 | 186.6355 | 226.1986 | 206.4097
636.1917 | 83.2849 | 270.6239 | 103.8158 | 187.3981 | 226.3026 | 206.0785
637.1917 | 83.3245 | 270.9934 | 104.0059 | 187.4789 | 225.4971 | 205.9893
638.1917 | 83.6004 | 271.7875 | 104.1153 | 186.6322 | 224.8346 | 205.2541
639.1917 | 83.9085 | 271.6709 | 104.4453 | 186.1576 | 224.6341 | 205.359
640.1917 | 84.0182 | 272.6772 | 104.3791 | 184.8302 | 224.7933 | 205.6645
641.1917 | 83.9261 | 272.3417 | 104.5841 | 184.1249 | 224.7917 | 205.3792
642.1917 | 84.2808 | 272.7417 | 104.6856 | 184.3187 | 224.6565 | 205.6337
643.1917 | 84.3195 | 272.7377 | 104.8806 | 183.8408 | 224.741 | 206.0726
644.1917 | 84.3699 | 273.027 | 105.1018 | 183.803 | 224.6431 | 206.0725
645.1917 | 84.2364 | 273.1178 | 105.2048 | 184.0187 | 225.5915 | 206.3385
646.1917 | 84.5159 | 273.4777 | 105.6297 | 184.7796 | 226.2796 | 206.904
647.1917 | 84.6299 | 274.1494 | 105.5983 | 184.0934 | 226.1552 | 206.6709
648.1917 | 84.5205 | 274.9038 | 105.8781 | 183.848 | 225.8853 | 207.233
649.1917 | 84.6576 | 274.9973 | 106.1271 | 183.5359 | 225.3859 | 207.378
650.1917 | 84.9178 | 275.397 | 106.3115 | 183.4652 | 224.6102 | 206.9526
651.1917 | 85.2607 | 275.8117 | 106.3896 | 183.194 | 223.7596 | 206.5732
652.1917 | 85.3373 | 276.163 | 106.5585 | 183.2278 | 223.2633 | 206.4672
653.1917 | 85.6423 | 276.551 | 106.8184 | 182.9188 | 223.0934 | 206.8638
654.1917 | 85.7194 | 276.4253 | 106.9322 | 182.7757 | 223.0614 | 205.5781
655.1917 | 85.8905 | 276.9496 | 107.1843 | 182.6561 | 223.9334 | 205.5428
656.1917 | 85.8521 | 277.3367 | 107.2143 | 182.7648 | 223.9502 | 205.8142
657.1917 | 85.87 | 277.6097 | 107.3694 | 181.8223 | 224.9425 | 205.5336
658.1917 | 85.8213 | 277.6743 | 107.5771 | 181.5854 | 224.5533 | 205.5191
659.1917 | 86.0377 | 277.79 | 107.802 | 181.2979 | 224.8245 | 205.9594
660.1917 | 86.1653 | 278.2861 | 107.803 | 181.8379 | 226.3705 | 206.0672
661.1917 | 86.1964 | 278.5983 | 107.949 | 181.121 | 226.5548 | 206.5285
662.1917 | 86.4019 | 278.8165 | 108.1297 | 180.7927 | 226.5373 | 206.3635
663.1917 | 86.5727 | 278.7707 | 108.174 | 181.069 | 227.7434 | 207
664.1917 | 86.7108 | 278.9225 | 108.497 | 181.1986 | 227.7992 | 206.9862
665.2073 | 86.8859 | 279.4784 | 108.7424 | 181.5629 | 228.2495 | 207.9837
666.1917 | 86.8769 | 279.625 | 108.6839 | 182.1197 | 229.3002 | 208.0575
667.1917 | 87.0278 | 279.8669 | 109.2649 | 181.3675 | 230.1593 | 208.1414
668.1917 | 87.0057 | 280.2387 | 109.7185 | 182.7204 | 230.2282 | 207.4342
669.1917 | 87.0495 | 280.2529 | 110.0081 | 182.6648 | 229.2824 | 207.1385
670.1917 | 87.2785 | 280.8062 | 110.1136 | 182.9041 | 228.7698 | 207.1199
671.1917 | 87.469 | 281.3807 | 109.9937 | 184.1121 | 229.4215 | 207.1896
672.1917 | 87.5427 | 281.4476 | 110.1013 | 183.6573 | 229.3036 | 207.842
673.1917 | 87.7108 | 281.6778 | 110.4111 | 183.1003 | 229.9373 | 208.361
674.1917 | 87.7775 | 281.9156 | 110.6817 | 184.2591 | 230.7461 | 208.0415
675.1917 | 87.9939 | 282.3245 | 110.8849 | 184.4447 | 232.0514 | 208.6035
676.1917 | 87.9922 | 282.527 | 111.0087 | 184.8843 | 233.449 | 209.5158
677.1917 | 88.0005 | 282.8701 | 111.1045 | 186.0289 | 234.2901 | 210.1678
678.1917 | 88.1556 | 282.8222 | 111.1535 | 186.1761 | 234.0787 | 210.0374
679.1917 | 88.3329 | 283.4246 | 111.4754 | 187.3465 | 233.2942 | 209.6547
680.1917 | 88.6517 | 283.7036 | 111.5784 | 187.0043 | 232.331 | 208.7356
681.1917 | 88.6552 | 283.912 | 111.6116 | 187.0159 | 232.1833 | 208.673
682.1917 | 88.6762 | 284.2634 | 111.8091 | 186.6306 | 232.3447 | 209.3898
683.1917 | 88.692 | 284.4906 | 112.1115 | 187.0485 | 231.9905 | 210.2099
684.1917 | 88.7277 | 284.7913 | 112.139 | 185.6429 | 232.5574 | 209.9023
685.1917 | 88.8744 | 285.7635 | 112.3559 | 185.5459 | 232.2648 | 209.4691
686.1917 | 89.1534 | 285.854 | 112.5961 | 185.3801 | 232.2927 | 209.9616
687.2073 | 89.3632 | 286.0067 | 112.8953 | 184.594 | 233.3763 | 210.6522
688.1917 | 89.6025 | 286.3976 | 113.196 | 184.8598 | 233.3 | 210.7519
689.1917 | 89.5541 | 286.2685 | 113.3198 | 184.9715 | 231.7956 | 210.116
690.1917 | 89.5211 | 286.9186 | 113.5262 | 185.0631 | 230.9116 | 209.6365
691.2073 | 89.6722 | 287.0365 | 113.4672 | 184.7702 | 230.7776 | 209.3144
692.1917 | 89.7624 | 287.4641 | 113.7281 | 184.4794 | 229.8775 | 209.3438
693.1917 | 89.836 | 287.9217 | 113.8151 | 184.1677 | 229.8372 | 208.7163
694.1917 | 90.015 | 288.133 | 114.3144 | 184.2562 | 229.858 | 208.9353
695.1917 | 90.1862 | 288.3972 | 114.3975 | 184.6727 | 229.5475 | 209.2319
696.1917 | 90.4478 | 288.9509 | 114.5455 | 184.7969 | 228.8529 | 209.2018
697.2073 | 90.2611 | 288.8269 | 114.7877 | 183.9502 | 228.4081 | 209.0925
698.1917 | 90.6223 | 289.3412 | 115.0278 | 183.3927 | 227.912 | 209.6026
699.1917 | 90.5206 | 289.3932 | 115.0616 | 183.8676 | 227.4414 | 209.6245
700.1917 | 90.8722 | 289.3912 | 115.5221 | 183.3432 | 226.914 | 209.7398
701.1917 | 90.8265 | 290.2067 | 115.6693 | 183.7393 | 226.5288 | 209.9492
702.1917 | 90.998 | 290.378 | 115.6659 | 184.4648 | 227.543 | 210.6859
703.2073 | 91.1395 | 290.5904 | 115.9313 | 184.8767 | 229.018 | 210.6758
704.1917 | 91.0467 | 290.6191 | 116.0461 | 186.3354 | 229.7854 | 212.1073
705.1917 | 91.4859 | 291.1794 | 116.3087 | 187.2384 | 230.1804 | 212.2058
706.1917 | 91.4943 | 291.9515 | 116.5938 | 188.0422 | 229.5452 | 211.9746
707.2073 | 91.3127 | 291.5079 | 116.579 | 188.8819 | 230.2467 | 212.0442
708.1917 | 91.6285 | 291.6743 | 116.9479 | 189.17 | 230.6655 | 212.3977
709.2073 | 91.6987 | 291.7774 | 116.9966 | 190.556 | 229.8597 | 211.771
710.1917 | 91.9563 | 291.8359 | 117.1996 | 191.8817 | 232.5212 | 211.9232
711.2073 | 91.7428 | 292.4216 | 117.2805 | 194.6765 | 233.7733 | 214.5383
712.1917 | 91.7652 | 292.3182 | 117.3951 | 194.3137 | 234.3324 | 214.9031
713.1917 | 91.7426 | 292.5703 | 117.7987 | 194.1519 | 234.7623 | 214.9784
714.1917 | 91.8915 | 292.8352 | 117.753 | 194.8479 | 235.4382 | 214.0065
715.1917 | 91.834 | 292.8241 | 117.9345 | 193.8521 | 236.1902 | 213.6145
716.1917 | 91.8571 | 292.9694 | 118.3232 | 195.3204 | 237.6092 | 215.3464
717.1917 | 91.8991 | 293.4159 | 118.5278 | 198.0484 | 238.0764 | 217.2221
718.1917 | 92.1938 | 293.4832 | 118.5143 | 197.9792 | 237.9144 | 217.9183
719.1917 | 92.1549 | 293.4041 | 118.71 | 197.9482 | 239.137 | 217.8784
720.1917 | 92.2852 | 293.5475 | 118.8712 | 198.9198 | 240.7123 | 217.9576
721.1917 | 92.2561 | 293.8169 | 119.1105 | 198.2932 | 241.2723 | 216.8637
722.1917 | 92.1701 | 293.9934 | 119.3369 | 197.3145 | 241.7531 | 216.5723
723.1917 | 92.2661 | 293.9954 | 119.4145 | 200.1939 | 241.7469 | 217.3481
724.1917 | 92.2774 | 294.5645 | 119.8538 | 200.693 | 242.3844 | 217.9861
725.2073 | 92.3412 | 294.854 | 119.9296 | 199.9005 | 241.8907 | 217.439
726.1917 | 92.5558 | 294.9983 | 120.6043 | 199.3602 | 240.4069 | 216.3787
727.1917 | 92.7007 | 295.2779 | 120.403 | 198.6739 | 238.8817 | 215.2442
728.1917 | 93.0461 | 295.1159 | 120.6014 | 197.8612 | 238.2043 | 214.4154
729.1917 | 93.2991 | 295.1575 | 120.8637 | 197.2933 | 237.96 | 213.9434
730.1917 | 93.1056 | 295.6095 | 121.2381 | 196.522 | 238.2871 | 214.608
731.1917 | 93.217 | 295.7564 | 121.2852 | 196.7192 | 238.2637 | 214.0399
732.1917 | 93.2897 | 295.7488 | 121.3793 | 197.264 | 239.62 | 213.6643
733.1917 | 93.3486 | 296.4887 | 121.6252 | 199.9937 | 240.4662 | 214.0968
734.1917 | 93.5978 | 296.5459 | 121.9153 | 200.8277 | 240.2559 | 213.3376
735.1917 | 93.6855 | 296.4709 | 121.903 | 200.467 | 240.0849 | 213.5129
736.1917 | 93.7833 | 296.4183 | 122.0238 | 200.4242 | 241.3301 | 214.2767
737.1917 | 93.7091 | 296.5438 | 122.6582 | 200.0593 | 241.7166 | 213.9504
738.1917 | 93.7838 | 297.0604 | 122.7775 | 201.3781 | 241.1686 | 215.2549
739.1917 | 93.7877 | 297.1804 | 122.7463 | 201.618 | 240.3087 | 215.0993
740.1917 | 93.8884 | 297.0428 | 122.8307 | 200.8214 | 240.3118 | 214.7261
741.1917 | 93.9951 | 297.2187 | 123.0326 | 202.0119 | 241.6409 | 216.6144
742.1917 | 93.998 | 297.3232 | 123.1511 | 202.1146 | 242.55 | 216.9953
743.1917 | 93.99 | 297.5584 | 123.503 | 203.1917 | 241.7016 | 218.5455
744.1917 | 94.1915 | 297.6778 | 123.5231 | 202.6618 | 241.1018 | 218.1714
745.1917 | 94.6134 | 297.699 | 123.6821 | 203.944 | 242.063 | 218.2792
746.1917 | 94.7484 | 297.9912 | 124.1591 | 204.0472 | 242.5605 | 217.8361
747.1917 | 94.4695 | 298.0699 | 124.4374 | 203.0992 | 241.5359 | 218.1967
748.1917 | 94.4227 | 298.032 | 124.5422 | 203.8725 | 240.2526 | 218.2794
749.1917 | 94.7741 | 298.2461 | 124.5206 | 203.0352 | 239.6106 | 218.3863
750.1917 | 94.7847 | 298.6716 | 124.5442 | 202.4446 | 240.51 | 218.4704
751.1917 | 94.7186 | 298.6227 | 124.8796 | 203.1241 | 240.6647 | 217.8108
752.1917 | 94.9832 | 299.0953 | 125.1942 | 202.1436 | 240.8653 | 217.1414
753.1917 | 94.907 | 299.0996 | 125.4498 | 203.1532 | 239.9409 | 216.2931
754.1917 | 94.9948 | 299.1863 | 125.6892 | 204.5907 | 240.0365 | 216.4477
755.1917 | 95.0558 | 299.2074 | 125.8729 | 204.5678 | 239.0017 | 215.4121
756.1917 | 95.1856 | 299.2887 | 125.9993 | 206.1581 | 238.4369 | 214.5931
757.1917 | 95.1945 | 299.4843 | 126.2398 | 206.8874 | 238.0724 | 213.8309
758.1917 | 95.3313 | 299.5316 | 126.6813 | 207.6719 | 238.2855 | 213.8696
759.1917 | 95.4933 | 299.5532 | 126.6618 | 207.1558 | 237.3669 | 213.1323
760.1917 | 95.7858 | 299.6283 | 126.9788 | 207.8614 | 238.3691 | 212.7128
761.1917 | 95.8115 | 299.7518 | 126.8081 | 208.2224 | 240.0147 | 212.1452
762.1917 | 95.8261 | 300.1134 | 126.9913 | 208.7391 | 241.409 | 211.7284
763.1917 | 96.0212 | 300.5215 | 127.2952 | 208.7932 | 241.8831 | 211.8162
764.1917 | 96.3012 | 300.4537 | 127.4891 | 207.4677 | 241.6283 | 212.0995
765.1917 | 96.1621 | 300.5305 | 127.5972 | 208.0468 | 240.7598 | 212.6819
766.1917 | 96.1781 | 300.6844 | 127.7223 | 206.9257 | 240.8225 | 211.8546
767.1917 | 96.1472 | 300.5375 | 127.8728 | 209.3394 | 241.2768 | 212.534
768.1917 | 96.2251 | 300.6585 | 127.9396 | 210.4159 | 241.5154 | 214.5897
769.1917 | 96.4509 | 300.8568 | 128.1942 | 211.2273 | 243.048 | 215.3529
770.1917 | 96.4522 | 300.9535 | 128.3189 | 211.6755 | 243.2136 | 215.8142
771.1917 | 96.4581 | 301.0912 | 128.4918 | 211.4253 | 243.7996 | 215.1151
772.1917 | 96.4701 | 301.4011 | 128.6861 | 212.8252 | 244.9788 | 216.3498
773.1917 | 96.6492 | 301.3212 | 128.803 | 212.1599 | 245.0253 | 217.3306
774.1917 | 96.7866 | 301.3552 | 129.055 | 212.9125 | 245.2182 | 218.1198
775.1917 | 97.1192 | 301.7246 | 129.1936 | 214.6331 | 246.0478 | 218.8135
776.1917 | 97.1862 | 301.9391 | 129.2266 | 213.4242 | 247.142 | 218.1063
777.1917 | 97.5173 | 302.1525 | 129.4153 | 212.2704 | 246.973 | 217.6075
778.1917 | 97.2841 | 302.1102 | 129.5726 | 212.4219 | 247.2901 | 217.659
779.1917 | 97.2923 | 302.1855 | 129.6061 | 213.5209 | 248.1449 | 219.4906
780.1917 | 97.3702 | 302.5002 | 129.8243 | 214.8351 | 247.5562 | 220.0948
781.1917 | 97.4081 | 302.8112 | 129.9696 | 213.802 | 248.5927 | 220.0752
782.1917 | 97.7751 | 303.5559 | 130.3555 | 212.9057 | 249.2265 | 221.1764
783.1917 | 98.1074 | 304.139 | 130.5377 | 211.9417 | 248.2693 | 220.1995
784.1917 | 98.0829 | 304.2377 | 130.5348 | 210.2146 | 246.5996 | 218.8456
785.1917 | 98.257 | 304.5035 | 130.6245 | 208.8926 | 246.7217 | 218.3705
786.1917 | 98.2813 | 304.3688 | 130.7181 | 207.5244 | 246.0895 | 218.5615
787.1917 | 98.2304 | 304.3939 | 130.8921 | 206.2904 | 244.783 | 218.3023
788.1917 | 98.3088 | 304.3694 | 131.3428 | 205.6492 | 244.1741 | 218.8044
789.1917 | 98.3052 | 305.0996 | 131.5206 | 205.9043 | 244.0058 | 219.1296
790.1917 | 98.3673 | 305.3137 | 131.5811 | 204.6452 | 243.5603 | 219.0149
791.1917 | 98.5491 | 304.8724 | 131.8161 | 204.392 | 242.4145 | 219.1122
792.1917 | 98.6967 | 305.3585 | 131.9139 | 204.5293 | 242.1373 | 219.6225
793.1917 | 98.8251 | 305.7847 | 132.0412 | 203.1434 | 242.3032 | 221.5576
794.1917 | 98.7464 | 305.977 | 132.4206 | 202.4998 | 241.9185 | 222.0552
795.1917 | 98.8294 | 305.8239 | 132.4122 | 201.8904 | 242.0732 | 222.2063
796.1917 | 99.1254 | 305.9571 | 132.5246 | 201.5659 | 242.5151 | 222.5463
797.1917 | 99.4387 | 306.0965 | 132.6453 | 201.7103 | 242.8935 | 222.1822
798.1917 | 99.5926 | 306.9191 | 132.8978 | 201.4526 | 243.22 | 221.9454
799.1917 | 99.4103 | 307.1012 | 133.0668 | 201.0856 | 243.369 | 221.2601
800.1917 | 99.521 | 307.9955 | 133.3286 | 200.2512 | 244.3413 | 221.2048
801.1917 | 99.724 | 308.0539 | 133.5288 | 200.0598 | 244.0813 | 220.6278
802.1917 | 100.0886 | 308.1966 | 133.8052 | 199.0154 | 242.5514 | 220.1652
803.1917 | 100.1117 | 308.1813 | 134.0561 | 198.752 | 241.2351 | 219.5188
804.1917 | 100.2784 | 308.4694 | 134.1912 | 197.882 | 240.7772 | 219.5029
805.1917 | 100.228 | 308.531 | 134.3704 | 198.0824 | 240.2532 | 219.1596
806.1917 | 100.2787 | 309.119 | 134.4093 | 198.3577 | 239.2891 | 219.3869
807.1917 | 100.4385 | 309.0919 | 134.4932 | 197.7926 | 237.8451 | 218.9017
808.1917 | 100.7971 | 309.4809 | 134.6076 | 197.3774 | 237.3762 | 219.4159
809.1917 | 101.0275 | 309.7722 | 134.8656 | 197.3871 | 236.5293 | 219.4593
810.1917 | 101.0047 | 310.0146 | 135.1199 | 196.7766 | 235.3903 | 219.2952
811.1917 | 101.322 | 310.4731 | 135.0745 | 196.2874 | 234.6379 | 218.9438
812.1917 | 101.55 | 310.4435 | 135.2794 | 196.0179 | 234.4022 | 218.9599
813.1917 | 101.4709 | 310.5082 | 135.4978 | 195.8288 | 233.6928 | 218.9697
814.1917 | 101.3659 | 310.6722 | 135.6845 | 194.706 | 232.8818 | 218.6021
815.1917 | 101.6231 | 310.6119 | 136.038 | 194.7125 | 232.379 | 218.0981
816.1917 | 101.7873 | 311.1502 | 136.1379 | 193.4267 | 232.7671 | 217.7577
817.1917 | 101.78 | 311.4118 | 136.1794 | 193.138 | 232.5013 | 218.4138
818.1917 | 101.832 | 311.2877 | 136.2055 | 193.1653 | 232.1616 | 217.8382
819.1917 | 101.8924 | 311.5001 | 136.3546 | 192.5614 | 232.8941 | 217.7607
820.1917 | 101.9979 | 311.899 | 136.5385 | 192.2577 | 234.7719 | 218.1935
821.1917 | 102.028 | 312.2276 | 136.7931 | 192.8509 | 236.1399 | 217.9505
822.1917 | 102.1266 | 312.1712 | 136.8894 | 192.9089 | 236.1659 | 218.4182
823.1917 | 102.3804 | 312.7716 | 137.1151 | 194.1779 | 236.5324 | 218.0755
824.1917 | 102.4149 | 312.955 | 137.2247 | 194.0158 | 237.1855 | 217.8117
825.1917 | 102.3447 | 312.823 | 137.4657 | 193.8007 | 236.1781 | 217.5442
826.1917 | 102.5809 | 312.9163 | 137.5498 | 194.219 | 236.4879 | 217.2697
827.1917 | 102.6376 | 312.9647 | 137.6705 | 193.9145 | 236.5718 | 218.2093
828.1917 | 102.6667 | 313.2085 | 137.8766 | 193.5958 | 236.8962 | 218.522
829.1917 | 102.6493 | 313.2953 | 138.0523 | 193.5781 | 238.1721 | 218.9468
830.1917 | 102.8894 | 313.6754 | 138.1632 | 194.6287 | 238.2903 | 220.0143
831.1917 | 102.8175 | 313.6377 | 138.2835 | 194.8781 | 239.0541 | 220.4447
832.1917 | 102.9114 | 313.8363 | 138.4232 | 194.531 | 240.0483 | 220.3312
833.1917 | 103.1573 | 314.0347 | 138.4828 | 195.1904 | 240.6419 | 219.6418
834.1917 | 103.1887 | 314.3251 | 138.6435 | 195.7802 | 239.4381 | 220.5826
835.1917 | 103.2486 | 314.8454 | 138.9591 | 196.0072 | 239.9455 | 219.9619
836.1917 | 103.2416 | 314.9265 | 139.0987 | 195.986 | 239.5107 | 220.3937
837.1917 | 103.5444 | 315.1882 | 139.2374 | 196.092 | 239.7243 | 220.3146
838.1917 | 103.6673 | 315.2631 | 139.3917 | 196.914 | 239.9659 | 220.6314
839.1917 | 104.0048 | 315.5858 | 139.4732 | 197.8534 | 240.1819 | 219.7777
840.1917 | 104.13 | 315.8541 | 139.4911 | 199.0797 | 240.5312 | 219.7472
841.1917 | 104.0729 | 315.8683 | 139.6405 | 199.7668 | 240.7962 | 219.096
842.1917 | 104.4817 | 316.234 | 139.7893 | 199.9466 | 240.0131 | 218.7131
843.1917 | 104.6975 | 316.5316 | 140.034 | 199.2407 | 239.1208 | 219.5494
844.1917 | 104.4745 | 316.4214 | 140.1041 | 198.807 | 238.4499 | 219.1289
845.2073 | 104.3646 | 316.6581 | 140.3571 | 198.6598 | 238.5563 | 218.7041
846.1917 | 104.5652 | 317.2897 | 140.475 | 198.3015 | 238.4519 | 219.0533
847.1917 | 104.6435 | 317.1427 | 140.7602 | 196.8768 | 237.8324 | 219.3924
848.1917 | 104.885 | 317.4732 | 141.0255 | 196.0521 | 237.7695 | 218.9119
849.1917 | 105.1303 | 317.6222 | 141.2035 | 195.9398 | 237.1381 | 218.7353
850.1917 | 105.232 | 318.2737 | 141.36 | 196.0478 | 237.3321 | 218.859
851.1917 | 105.2257 | 318.4654 | 141.6134 | 197.0052 | 238.1268 | 218.2111
852.1917 | 105.2353 | 318.1508 | 141.8007 | 196.6486 | 238.1875 | 218.3071
853.1917 | 105.2734 | 318.7598 | 141.867 | 197.2141 | 238.1971 | 218.9826
854.1917 | 105.4406 | 318.9561 | 141.9945 | 198.1978 | 238.6424 | 220.2996
855.1917 | 105.5649 | 319.0462 | 142.1613 | 198.7068 | 239.1072 | 220.2701
856.1917 | 105.5781 | 319.135 | 142.3368 | 198.7039 | 239.2385 | 220.305
857.1917 | 105.7298 | 319.3846 | 142.4104 | 199.2829 | 240.121 | 220.0186
858.1917 | 105.9413 | 319.5463 | 142.5527 | 199.73 | 241.5016 | 220.5236
859.1917 | 106.1575 | 319.9717 | 142.8348 | 199.9327 | 241.4659 | 220.8612
860.1917 | 106.0896 | 320.148 | 142.9679 | 199.2482 | 241.308 | 221.044
861.1917 | 106.0663 | 320.3812 | 143.0185 | 199.0011 | 240.5737 | 220.4563
862.1917 | 106.3138 | 320.1835 | 143.2736 | 199.5395 | 240.2458 | 220.3374
863.1917 | 106.7516 | 320.496 | 143.5339 | 200.098 | 241.9343 | 219.9202
864.1917 | 106.7273 | 320.6866 | 143.4529 | 200.8988 | 242.2154 | 220.6612
865.1917 | 106.7657 | 321.0213 | 143.7598 | 201.2298 | 242.5288 | 221.3415
866.1917 | 106.7166 | 321.2194 | 143.9661 | 201.3783 | 242.5801 | 220.7231
867.1917 | 106.9002 | 321.372 | 144.0739 | 201.6972 | 242.6733 | 221.0915
868.1917 | 106.8517 | 321.69 | 144.135 | 201.4125 | 241.2576 | 222.1211
869.1917 | 107.1436 | 321.575 | 144.2211 | 200.5932 | 240.3334 | 221.7873
870.1917 | 107.2892 | 321.8069 | 144.6938 | 199.8079 | 239.2492 | 221.2039
871.1917 | 107.4206 | 321.931 | 144.8253 | 199.5916 | 238.7687 | 220.3253
872.1917 | 107.319 | 322.1634 | 144.9677 | 199.4319 | 238.3062 | 220.138
873.1917 | 107.3664 | 322.4668 | 145.2637 | 199.1749 | 237.9024 | 219.6783
874.1917 | 107.7362 | 322.5457 | 145.2789 | 199.5625 | 238.5158 | 220.146
875.1917 | 107.9906 | 322.8077 | 145.4562 | 199.3759 | 238.3743 | 220.4509
876.1917 | 107.8403 | 323.3173 | 145.5751 | 200.5354 | 238.8754 | 221.1522
877.1917 | 107.8522 | 323.1222 | 145.7136 | 200.3072 | 239.3211 | 220.9192
878.1917 | 108.0482 | 323.4307 | 146.1451 | 200.4865 | 237.9415 | 220.5573
879.1917 | 108.3666 | 323.605 | 146.1589 | 200.2225 | 237.2593 | 220.6065
880.1917 | 108.4539 | 323.7539 | 146.3461 | 199.8305 | 237.3776 | 220.6327
881.1917 | 108.5354 | 323.7256 | 146.5046 | 199.4703 | 236.4905 | 220.3285
882.2073 | 108.4662 | 323.9087 | 146.5275 | 199.6755 | 236.2137 | 220.8317
883.1917 | 108.6468 | 324.454 | 146.5592 | 200.667 | 236.5426 | 220.8826
884.1917 | 108.639 | 324.5083 | 146.8034 | 200.4683 | 236.7932 | 220.1821
885.1917 | 108.746 | 324.5014 | 146.9276 | 199.9167 | 236.6264 | 220.1074
886.1917 | 108.9716 | 324.6453 | 146.9872 | 200.4053 | 237.3982 | 220.0828
887.1917 | 108.9092 | 324.6679 | 147.078 | 200.5551 | 238.6831 | 220.0531
888.1917 | 108.8509 | 324.6931 | 147.1531 | 201.6419 | 240.5853 | 221.8903
889.1917 | 108.9204 | 324.9722 | 147.3176 | 204.9072 | 242.9588 | 222.5061
890.1917 | 108.9203 | 325.1106 | 147.4469 | 206.8564 | 244.2936 | 225.423
891.1917 | 108.9615 | 325.2333 | 147.5832 | 207.9435 | 244.8721 | 225.9146
892.1917 | 109.3266 | 325.3306 | 147.8168 | 207.4881 | 245.0077 | 228.3656
893.1917 | 109.6588 | 325.3781 | 147.9411 | 208.7661 | 245.0007 | 230.0291
894.1917 | 109.7959 | 325.5534 | 148.1463 | 210.995 | 245.8711 | 229.5041
895.1917 | 109.8597 | 326.0756 | 148.4726 | 214.6943 | 246.8952 | 231.9505
896.1917 | 109.804 | 325.8701 | 148.5194 | 215.4222 | 247.7516 | 232.0097
897.1917 | 109.6826 | 325.951 | 148.7236 | 215.2512 | 248.0332 | 231.8415
898.1917 | 109.7694 | 326.5418 | 148.8971 | 215.1422 | 248.7865 | 232.8079
899.1917 | 109.9856 | 326.6162 | 149.1431 | 215.256 | 248.7654 | 231.9888
900.1917 | 109.8045 | 326.5072 | 149.2004 | 214.2716 | 248.7789 | 231.6014
901.1917 | 109.8209 | 326.6949 | 149.7283 | 214.5395 | 248.9105 | 231.7488
902.1917 | 110.0319 | 327.1768 | 149.6973 | 214.8204 | 249.3398 | 230.5964
903.1917 | 110.4354 | 328.1808 | 149.7554 | 213.9644 | 250.567 | 229.9527
904.1917 | 110.7043 | 328.1413 | 149.8566 | 213.1384 | 249.2127 | 229.2392
905.1917 | 110.802 | 328.4976 | 150.0817 | 212.1388 | 248.585 | 229.1864
906.1917 | 110.8569 | 328.6067 | 150.1297 | 212.1095 | 247.8387 | 229.3604
907.1917 | 110.9115 | 328.575 | 150.2933 | 211.5684 | 248.199 | 229.4502
908.1917 | 111.1134 | 328.7979 | 150.4477 | 210.8846 | 249.0746 | 230.0713
909.1917 | 111.1661 | 329.433 | 150.625 | 210.1166 | 249.7601 | 231.3103
910.1917 | 111.3176 | 329.9417 | 150.9883 | 209.6077 | 250.7065 | 231.921
911.1917 | 111.3371 | 329.501 | 150.9853 | 209.7227 | 251.4717 | 231.4088
912.2073 | 111.3337 | 329.6203 | 151.0305 | 208.675 | 252.4002 | 231.4415
913.1917 | 111.5601 | 329.7333 | 151.3942 | 208.6875 | 252.8358 | 231.358
914.1917 | 112.1107 | 330.2006 | 151.5964 | 209.4065 | 254.3362 | 232.2105
915.1917 | 112.0146 | 330.6344 | 151.7356 | 208.6307 | 255.5423 | 233.3607
916.1917 | 112.0541 | 330.7886 | 151.9683 | 209.9256 | 256.3124 | 233.6173
917.1917 | 112.078 | 331.2483 | 152.0932 | 210.4358 | 257.2233 | 234.4758
918.1917 | 112.0869 | 331.6068 | 152.1647 | 209.7482 | 257.3553 | 235.7
919.1917 | 112.3342 | 331.8189 | 152.3016 | 208.5688 | 256.9044 | 235.4713
920.1917 | 112.6407 | 332.4325 | 152.521 | 207.6855 | 257.7698 | 235.4751
921.1917 | 112.8614 | 332.57 | 152.7406 | 207.3298 | 258.5862 | 235.3447
922.1917 | 112.9397 | 332.8396 | 152.9529 | 208.0419 | 258.9987 | 235.7718
923.1917 | 112.873 | 332.6471 | 153.0968 | 208.1257 | 258.3725 | 235.7036
924.1917 | 112.99 | 332.8893 | 153.2418 | 208.9676 | 258.5102 | 236.3486
925.1917 | 113.1718 | 333.1416 | 153.4992 | 209.3539 | 258.4016 | 235.6837
926.1917 | 113.2214 | 333.074 | 153.6685 | 209.8142 | 260.4663 | 235.5466
927.1917 | 113.4315 | 332.9591 | 153.9691 | 213.8724 | 262.901 | 238.8864
928.1917 | 113.4475 | 333.3678 | 154.4933 | 215.6737 | 263.7826 | 240.8291
929.1917 | 113.4365 | 333.2926 | 154.6347 | 215.7798 | 265.4983 | 240.7353
930.1917 | 113.429 | 333.3361 | 154.7257 | 215.6785 | 267.161 | 242.3108
931.1917 | 113.4265 | 333.5663 | 154.7318 | 217.8976 | 268.4995 | 243.6362
932.1917 | 113.705 | 333.8395 | 155.16 | 218.9973 | 269.2934 | 244.6255
933.1917 | 113.6907 | 334 | 155.2341 | 221.9602 | 270.1139 | 244.9812
934.1917 | 113.8215 | 334.314 | 155.4068 | 223.4844 | 272.462 | 245.4616
935.1917 | 114.1711 | 334.7291 | 155.7234 | 223.259 | 273.9327 | 246.5889
936.1917 | 114.3406 | 334.5981 | 155.9582 | 223.2148 | 273.7577 | 246.9894
937.1917 | 114.4067 | 334.7976 | 156.0158 | 224.4644 | 273.7374 | 246.9449
938.1917 | 114.394 | 334.9261 | 156.0358 | 228.8008 | 276.3241 | 248.1318
939.1917 | 114.5322 | 335.0775 | 156.3927 | 229.8349 | 277.5502 | 248.0204
940.1917 | 114.6298 | 335.0722 | 156.5708 | 231.0608 | 277.6198 | 247.6004
941.1917 | 114.528 | 335.0976 | 157.3344 | 233.618 | 278.5805 | 246.9362
942.1917 | 114.6377 | 335.3991 | 157.2433 | 235.1001 | 279.6406 | 247.6901
943.1917 | 114.8195 | 336.3637 | 157.6273 | 234.3596 | 280.4029 | 246.7211
944.1917 | 114.9883 | 336.0846 | 157.7392 | 233.4688 | 280.2787 | 245.3611
945.1917 | 115.137 | 336.5741 | 157.6961 | 233.0919 | 280.9687 | 246.4868
946.1917 | 115.2242 | 336.6681 | 157.7408 | 232.5736 | 281.7755 | 246.938
947.1917 | 115.4289 | 336.9323 | 157.9911 | 233.4551 | 282.8051 | 247.1581
948.1917 | 115.5338 | 337.5032 | 158.3398 | 232.6892 | 284.0919 | 248.2299
949.1917 | 115.686 | 337.6425 | 158.4404 | 231.8191 | 284.3666 | 247.4574
950.1917 | 115.8841 | 337.6429 | 158.5891 | 230.8702 | 283.597 | 248.7842
951.1917 | 116.0972 | 337.5 | 158.7642 | 230.0931 | 283.4851 | 249.4754
952.1917 | 116.0281 | 337.713 | 158.8207 | 229.2838 | 283.2761 | 250.077
953.1917 | 116.3836 | 338.2342 | 159.0848 | 229.5787 | 283.4265 | 250.4114
954.1917 | 116.6699 | 338.3134 | 159.2085 | 228.9257 | 284.5884 | 251.6118
955.1917 | 116.8278 | 339.1391 | 159.4222 | 228.5117 | 283.7648 | 252.2195
956.1917 | 116.8002 | 339.2265 | 159.3973 | 227.2648 | 282.4583 | 251.9787
957.1917 | 116.8681 | 339.7731 | 159.6673 | 225.9667 | 280.8714 | 252.0016
958.1917 | 116.8882 | 339.9485 | 159.934 | 226.9889 | 281.3859 | 251.3202
959.1917 | 116.9344 | 339.8784 | 160.2397 | 226.2463 | 280.8093 | 250.8508
960.1917 | 116.9372 | 340.0903 | 160.3398 | 226.0789 | 280.642 | 250.4459
961.1917 | 117.1724 | 339.9692 | 160.6255 | 225.8285 | 280.9143 | 250.8997
962.1917 | 117.3433 | 340.7936 | 160.9236 | 227.2286 | 281.5869 | 251.0127
963.1917 | 117.465 | 341.2227 | 161.3807 | 227.2352 | 281.1702 | 252.2409
964.1917 | 117.6334 | 340.9766 | 161.2847 | 226.1432 | 279.9471 | 251.485
965.1917 | 118.0727 | 341.2541 | 161.5586 | 225.2566 | 278.2049 | 250.8179
966.1917 | 118.172 | 341.3481 | 161.7388 | 223.9753 | 278.1339 | 250.6926
967.1917 | 118.0769 | 341.2111 | 161.7978 | 223.831 | 279.5895 | 249.9183
968.1917 | 117.9872 | 341.2413 | 162.3067 | 225.1484 | 279.6293 | 251.2275
969.1917 | 117.8609 | 341.6562 | 162.5707 | 226.4416 | 279.2322 | 250.3838
970.1917 | 118.165 | 341.9433 | 162.8979 | 227.8009 | 280.1698 | 250.4633
971.1917 | 118.2184 | 341.8515 | 162.8906 | 229.7145 | 282.2558 | 251.0151
972.2073 | 118.3036 | 341.9864 | 163.2302 | 234.247 | 283.2191 | 252.7294
973.1917 | 118.3796 | 342.0389 | 163.28 | 234.9335 | 285.1688 | 255.3762
974.1917 | 118.8531 | 342.2271 | 163.3029 | 236.5455 | 285.3011 | 256.6327
975.1917 | 118.8013 | 342.4661 | 163.4328 | 238.575 | 285.7304 | 256.736
976.1917 | 118.7584 | 342.7969 | 163.5817 | 240.1374 | 287.9127 | 256.5933
977.1917 | 118.9921 | 342.8802 | 163.7443 | 239.5318 | 288.9108 | 257.8794
978.1917 | 118.9929 | 343.0738 | 164.0599 | 240.5175 | 288.7883 | 258.792
979.1917 | 118.9408 | 343.1988 | 164.1881 | 240.3941 | 288.9074 | 257.8091
980.1917 | 119.215 | 343.725 | 164.5087 | 242.0466 | 290.5199 | 258.49
981.1917 | 119.2227 | 343.5815 | 164.638 | 242.9202 | 291.5268 | 257.9165
982.1917 | 119.4803 | 343.6487 | 164.8866 | 241.3979 | 291.979 | 259.5469
983.1917 | 119.488 | 344.0525 | 165.074 | 241.5638 | 292.4941 | 260.9796
984.1917 | 119.5632 | 343.8003 | 165.138 | 240.445 | 291.0588 | 260.5507
985.1917 | 119.7489 | 344.405 | 165.2834 | 239.8702 | 290.1895 | 260.0031
986.1917 | 119.9355 | 344.3711 | 165.4883 | 239.6661 | 290.9678 | 258.8194
987.1917 | 119.8999 | 344.5027 | 165.5587 | 240.3971 | 291.8316 | 257.8758
988.1917 | 119.9022 | 344.5878 | 165.7746 | 239.7026 | 292.02 | 258.5416
989.1917 | 119.9139 | 344.71 | 166.0605 | 239.3174 | 291.6646 | 258.1895
990.1917 | 120.1729 | 345.0951 | 166.5525 | 238.4973 | 291.4682 | 258.0125
991.1917 | 120.2313 | 345.1371 | 166.6613 | 238.4308 | 290.9322 | 257.4444
992.1917 | 120.3741 | 345.7922 | 166.9823 | 237.8422 | 290.8718 | 256.7493
993.1917 | 120.3531 | 345.5275 | 167.1202 | 237.6413 | 290.0697 | 256.6784
994.1917 | 120.3899 | 345.4386 | 167.1201 | 237.8101 | 290.307 | 256.9401
995.1917 | 120.4829 | 345.6602 | 167.1968 | 236.277 | 289.9219 | 257.3319
996.1917 | 120.8743 | 346.4588 | 167.3927 | 236.6538 | 290.5382 | 257.4575
997.1917 | 121.0722 | 346.1171 | 167.5536 | 237.0601 | 291.655 | 258.6562
998.1917 | 120.9323 | 346.3023 | 167.7917 | 237.896 | 293.1094 | 258.8738
999.1917 | 120.9929 | 346.4837 | 168.2429 | 240.7547 | 295.1368 | 260.7895
1000.1917 | 121.0851 | 346.9157 | 168.2856 | 241.6408 | 295.574 | 262.0106
1001.1917 | 121.3482 | 347.0511 | 168.392 | 241.0357 | 294.6901 | 261.4154
1002.1917 | 121.3141 | 347.422 | 168.7052 | 240.8283 | 294.614 | 260.8867
1003.1917 | 121.4492 | 347.7187 | 168.8487 | 240.2963 | 293.679 | 260.7357
1004.1917 | 121.5458 | 348.3848 | 169.0629 | 240.3439 | 294.3227 | 260.9145
1005.1917 | 121.5976 | 348.3533 | 169.2671 | 239.1628 | 293.5902 | 259.9899
1006.1917 | 121.9789 | 348.3862 | 169.4434 | 238.5076 | 293.9995 | 259.9022
1007.1917 | 122.3893 | 349.3837 | 169.5647 | 237.5278 | 292.6638 | 259.4347
1008.1917 | 122.6678 | 349.8491 | 169.6605 | 236.3321 | 291.1717 | 258.8847
1009.1917 | 122.7579 | 349.2892 | 169.9246 | 235.7465 | 291.1533 | 259.1549
1010.1917 | 122.5708 | 349.2493 | 170.1052 | 236.2427 | 292.4759 | 261.1654
1011.1917 | 122.5384 | 349.308 | 170.1732 | 237.1238 | 292.3624 | 262.1749
1012.1917 | 122.5725 | 349.4911 | 170.4307 | 237.9821 | 293.733 | 263.6662
1013.1917 | 122.6055 | 349.7822 | 170.7655 | 239.0115 | 294.455 | 263.8639
1014.1917 | 122.7757 | 349.8653 | 170.7078 | 239.3926 | 294.7413 | 264.3742
1015.1917 | 122.9621 | 349.9079 | 170.9572 | 239.4799 | 295.2001 | 266.6266
1016.1917 | 122.9287 | 350.0893 | 171.1835 | 241.4478 | 295.946 | 268.7512
1017.1917 | 123.0886 | 350.5837 | 171.4463 | 241.675 | 296.578 | 269.1061
1018.1917 | 123.0657 | 350.7409 | 171.6836 | 242.5353 | 297.1382 | 268.7196
1019.1917 | 123.2492 | 350.8362 | 171.967 | 243.4093 | 298.1015 | 269.3774
1020.1917 | 123.2682 | 350.9032 | 171.8612 | 244.4873 | 299.619 | 270.1901
1021.1917 | 123.4413 | 351.5285 | 172.357 | 244.2364 | 299.6698 | 269.4631
1022.1917 | 123.6744 | 351.5463 | 172.4284 | 243.8892 | 300.23 | 269.0634
1023.1917 | 123.8042 | 352.1729 | 172.5376 | 243.606 | 299.9573 | 269.051
1024.1917 | 124.094 | 352.6432 | 172.9178 | 242.8983 | 300.0178 | 267.986
1025.1917 | 124.2555 | 352.9899 | 173.0656 | 242.4982 | 299.9004 | 267.6201
1026.1917 | 124.1726 | 353.0398 | 173.2913 | 242.2018 | 300.1276 | 266.7511
1027.1917 | 124.2189 | 353.1866 | 173.6584 | 242.3287 | 300.0262 | 265.8813
1028.1917 | 124.2079 | 352.9247 | 173.5871 | 242.1492 | 300.8008 | 266.7642
1029.1917 | 124.1996 | 352.9864 | 173.6442 | 244.2839 | 301.1409 | 266.6681
1030.1917 | 124.3924 | 353.5795 | 174.0716 | 243.7193 | 301.2956 | 268.7666
1031.1917 | 124.473 | 353.8028 | 174.1047 | 242.9735 | 301.6373 | 268.7725
1032.2073 | 124.6188 | 354.0045 | 174.3704 | 245.0391 | 302.0128 | 269.738
1033.1917 | 124.8951 | 353.913 | 174.5433 | 244.1904 | 301.9211 | 268.5815
1034.1917 | 125.0178 | 354.1595 | 174.9369 | 244.7354 | 301.3844 | 269.6154
1035.1917 | 125.1406 | 354.735 | 175.118 | 244.0771 | 300.6654 | 268.7217
1036.1917 | 125.5033 | 355.1648 | 175.2685 | 246.9337 | 301.7926 | 268.3903
1037.1917 | 125.4485 | 355.2038 | 175.4617 | 247.9288 | 302.6654 | 267.1816
1038.1917 | 125.6272 | 355.1916 | 175.5165 | 249.8111 | 304.2676 | 269.6948
1039.1917 | 125.6106 | 355.2222 | 175.6398 | 251.9796 | 305.9108 | 272.1134
1040.1917 | 125.6526 | 355.3158 | 176.0344 | 252.2491 | 307.1307 | 272.8525
1041.1917 | 125.6823 | 355.4268 | 176.1279 | 252.228 | 309.2752 | 273.1033
1042.1917 | 125.7328 | 356.0181 | 176.4699 | 254.1574 | 310.2319 | 273.6741
1043.2073 | 125.9192 | 357.1617 | 176.8986 | 254.664 | 310.7065 | 273.3761
1044.1917 | 126.1071 | 357.5942 | 177.1735 | 253.696 | 310.2525 | 272.4835
1045.1917 | 126.1823 | 357.772 | 177.1907 | 252.8292 | 310.1002 | 271.6783
1046.1917 | 126.4239 | 357.6627 | 177.3643 | 252.6895 | 311.0168 | 271.1843
1047.1917 | 126.8031 | 358.5167 | 177.7404 | 252.0009 | 311.3421 | 271.1174
1048.1917 | 126.7142 | 358.3233 | 177.7952 | 250.3439 | 309.9746 | 270.318
1049.1917 | 126.563 | 358.0928 | 177.8859 | 248.6281 | 309.0585 | 270.3908
1050.1917 | 126.7466 | 359.0017 | 178.2807 | 248.4689 | 309.3109 | 271.9988
1051.1917 | 127.2481 | 360.3206 | 178.3981 | 250.471 | 309.8244 | 275.1332
1052.1917 | 127.68 | 361.0802 | 178.8603 | 250.4505 | 311.1783 | 274.4892
1053.2073 | 128.0074 | 360.9445 | 179.0175 | 249.2675 | 311.073 | 274.3794
1054.1917 | 127.9008 | 361.3599 | 179.228 | 248.5966 | 310.1847 | 274.7369
1055.1917 | 127.957 | 361.9254 | 179.7264 | 248.1617 | 311.3393 | 275.359
1056.1917 | 128.2558 | 362.116 | 179.7798 | 248.7532 | 311.4546 | 274.882
1057.1917 | 128.3929 | 362.4831 | 179.9475 | 248.4536 | 312.5524 | 274.6318
1058.1917 | 128.4259 | 362.8543 | 180.0869 | 248.3932 | 313.6409 | 275.2563
1059.1917 | 128.5041 | 363.2364 | 180.3979 | 247.0962 | 314.8529 | 274.829
1060.1917 | 128.5094 | 363.4435 | 180.6327 | 247.5682 | 315.7385 | 275.2144
1061.1917 | 128.606 | 363.006 | 180.7129 | 247.9989 | 315.4627 | 275.4149
1062.1917 | 129.0199 | 363.8981 | 181.6363 | 250.6155 | 315.8385 | 277.0253
1063.2073 | 128.8911 | 364.2969 | 181.7577 | 251.651 | 316.4881 | 277.7196
1064.1917 | 128.9317 | 364.557 | 182.0571 | 250.9396 | 317.5459 | 276.9624
1065.1917 | 128.894 | 364.4923 | 182.1387 | 252.8283 | 318.9989 | 280.4598
1066.1917 | 129.0015 | 365.6184 | 182.7044 | 257.6975 | 320.7513 | 281.5073
1067.1917 | 129.3515 | 366.9707 | 182.826 | 259.5752 | 323.4711 | 283.6178
1068.1917 | 129.5603 | 367.3081 | 182.8636 | 258.3082 | 325.5059 | 283.9582
1069.1917 | 129.878 | 367.9507 | 183.4843 | 256.8263 | 326.0907 | 283.9176
1070.1917 | 130.0847 | 368.1296 | 183.3188 | 255.9538 | 326.8226 | 284.3981
1071.1917 | 130.4954 | 368.1835 | 183.4906 | 254.7413 | 327.3663 | 284.6604
1072.1917 | 130.7704 | 369.0165 | 183.9034 | 254.6603 | 328.9349 | 286.5164
1073.1917 | 130.7797 | 369.2616 | 184.1562 | 254.4486 | 329.0807 | 286.4166
1074.1917 | 130.9297 | 369.1926 | 184.2856 | 253.8096 | 328.4397 | 287.0179
1075.1917 | 130.9321 | 368.9069 | 184.5164 | 255.5479 | 328.8315 | 287.1978
1076.1917 | 130.8681 | 369.5797 | 184.9927 | 257.3585 | 329.8025 | 288.3965
1077.1917 | 131.1499 | 370.2604 | 185.314 | 257.8449 | 330.9742 | 289.6876
1078.1917 | 131.1293 | 370.3678 | 185.5294 | 258.4765 | 330.6708 | 289.3278
1079.1917 | 131.2453 | 370.1901 | 185.9867 | 262.2083 | 332.2951 | 290.6515
1080.1917 | 131.3898 | 371.1235 | 186.1881 | 262.6353 | 333.5815 | 292.0674
1081.1917 | 131.42 | 371.0438 | 186.0431 | 262.7815 | 334.6148 | 291.7953
1082.1917 | 131.667 | 370.9551 | 186.1545 | 263.7006 | 337.2921 | 291.284
1083.1917 | 131.6877 | 371.0699 | 186.7494 | 266.8999 | 339.622 | 289.6394
1084.1917 | 131.6901 | 371.1612 | 186.7139 | 267.2917 | 340.8838 | 288.4909
1085.1917 | 131.7878 | 371.3723 | 187.1021 | 267.3099 | 342.7793 | 286.9272
1086.1917 | 131.8305 | 371.5525 | 187.5643 | 268.6662 | 345.5373 | 285.0071
1087.1917 | 131.9043 | 371.8462 | 187.6893 | 269.7192 | 347.762 | 283.7371
1088.1917 | 132.2263 | 372.1787 | 187.7252 | 268.5287 | 347.1273 | 282.5359
1089.1917 | 132.2559 | 372.2681 | 187.7899 | 267.6627 | 345.283 | 280.7022
1090.1917 | 132.3888 | 372.5347 | 188.1122 | 267.3376 | 344.4269 | 280.5474
1091.1917 | 132.343 | 372.5948 | 188.306 | 267.4558 | 343.5041 | 279.8579
1092.2073 | 132.4533 | 372.8252 | 188.4015 | 270.0924 | 343.2756 | 278.4814
1093.1917 | 132.3995 | 372.9078 | 188.4449 | 269.2493 | 341.3367 | 278.7004
1094.1917 | 132.6133 | 373.7003 | 189.1603 | 270.5779 | 339.7719 | 278.7865
1095.1917 | 132.8206 | 374.0148 | 189.5498 | 269.3447 | 338.4574 | 277.8661
1096.1917 | 133.0153 | 373.7925 | 189.9384 | 269.5926 | 338.1458 | 277.7117
1097.1917 | 133.0063 | 374.2188 | 189.9905 | 269.5024 | 337.8429 | 276.9951
1098.1917 | 133.2613 | 375.1784 | 190.3053 | 268.81 | 338.003 | 276.9095
1099.1917 | 133.2731 | 374.9432 | 190.9074 | 270.0143 | 336.9246 | 276.2108
1100.1917 | 133.2805 | 375.0651 | 191.2352 | 269.9219 | 337.472 | 275.7019
1101.1917 | 133.4695 | 375.1029 | 191.8023 | 269.7342 | 336.0584 | 274.9923
1102.1917 | 133.4964 | 375.0749 | 191.4007 | 271.7973 | 336.0576 | 274.318
1103.1917 | 133.7207 | 375.3358 | 191.5639 | 273.5547 | 337.2328 | 273.2524
1104.1917 | 134.117 | 375.5216 | 192.0227 | 275.4248 | 337.1416 | 273.2102
1105.1917 | 134.3053 | 375.6826 | 192.6814 | 276.2388 | 338.8854 | 273.8554
1106.1917 | 134.1736 | 376.1365 | 192.9439 | 276.4436 | 340.4152 | 274.3591
1107.1917 | 134.3757 | 376.6106 | 192.8582 | 278.399 | 340.4707 | 274.6072
1108.1917 | 134.3103 | 377.0922 | 193.0625 | 278.1851 | 340.9658 | 273.8151
1109.1917 | 134.3983 | 376.8796 | 193.2733 | 278.5958 | 341.1873 | 274.2301
1110.1917 | 134.48 | 377.0634 | 193.3016 | 278.7414 | 341.5449 | 273.7761
1111.1917 | 134.6521 | 377.2538 | 193.6254 | 278.4427 | 341.0022 | 274.5414
1112.1917 | 134.7903 | 378.0953 | 193.9125 | 277.2497 | 340.0561 | 274.4063
1113.1917 | 134.8021 | 378.1942 | 194.1162 | 277.1279 | 339.0134 | 273.8586
1114.1917 | 134.9727 | 378.4158 | 194.375 | 277.9846 | 339.7217 | 274.6934
1115.1917 | 134.9669 | 378.8576 | 194.7688 | 277.7772 | 340.6371 | 274.4288
1116.1917 | 135.1478 | 379.3609 | 194.9946 | 278.0398 | 339.0675 | 275.4048
1117.1917 | 135.4349 | 380.1296 | 195.2862 | 277.1296 | 339.8588 | 275.7425
1118.1917 | 135.6912 | 380.4905 | 195.6836 | 276.4173 | 339.1433 | 275.3375
1119.1917 | 136.0471 | 380.7857 | 195.6287 | 275.4263 | 337.3151 | 274.0127
1120.1917 | 136.2224 | 381.2467 | 195.7981 | 274.6375 | 336.5088 | 274.8681
1121.1917 | 136.2443 | 381.4177 | 196.1278 | 273.7834 | 338.1357 | 275.6639
1122.1917 | 136.1652 | 381.3941 | 196.1738 | 274.2865 | 337.4378 | 276.8996
1123.1917 | 136.1583 | 381.2669 | 196.792 | 275.1768 | 336.4462 | 277.6225
1124.1917 | 136.1558 | 381.2556 | 197.0123 | 278.5134 | 336.7462 | 279.0217
1125.1917 | 136.2815 | 381.8736 | 197.2221 | 279.0481 | 336.5428 | 279.0378
1126.1917 | 136.4172 | 382.3747 | 197.6447 | 280.884 | 338.5193 | 278.4628
1127.1917 | 136.4263 | 382.192 | 197.6453 | 280.4538 | 337.6512 | 277.019
1128.1917 | 136.6094 | 382.3816 | 197.8343 | 281.9873 | 337.8358 | 278.9134
1129.1917 | 136.6918 | 382.8678 | 198.1193 | 282.357 | 337.9442 | 279.338
1130.1917 | 136.8936 | 383.3386 | 198.2092 | 279.8799 | 337.4059 | 279.2432
1131.1917 | 137.1835 | 384.2191 | 198.5136 | 277.7856 | 338.2117 | 280.2735
1132.1917 | 137.3451 | 384.0711 | 198.6934 | 277.7369 | 339.249 | 281.053
1133.1917 | 137.4298 | 384.5206 | 198.8734 | 276.8864 | 340.2057 | 281.3463
1134.1917 | 137.5697 | 384.5757 | 199.018 | 276.2896 | 343.1431 | 282.507
1135.1917 | 137.5841 | 384.8083 | 199.2496 | 275.1924 | 341.9719 | 282.1574
1136.1917 | 137.9398 | 385.4905 | 199.6163 | 274.7039 | 342.4336 | 282.5187
1137.1917 | 138.1048 | 385.469 | 199.5856 | 274.823 | 343.8213 | 282.6356
1138.1917 | 138.1766 | 385.8753 | 199.7211 | 273.9736 | 345.5252 | 283.0289
1139.1917 | 138.1902 | 386.07 | 200.048 | 275.5057 | 346.9614 | 284.9832
1140.1917 | 138.319 | 386.6939 | 200.289 | 274.7827 | 346.3552 | 284.9055
1141.1917 | 138.5043 | 386.7357 | 200.4501 | 273.9059 | 345.5831 | 284.8903
1142.1917 | 138.4009 | 386.9322 | 200.7978 | 273.4644 | 344.8394 | 284.9553
1143.1917 | 138.3811 | 387.3705 | 200.9654 | 272.6673 | 344.3629 | 285.0292
1144.1917 | 138.7043 | 387.7324 | 200.9952 | 270.7516 | 342.9892 | 285.6448
1145.1917 | 138.7482 | 388.022 | 201.1672 | 269.3182 | 345.0609 | 286.4381
1146.1917 | 139.1284 | 389.0956 | 201.445 | 267.605 | 343.9325 | 285.7713
1147.1917 | 139.2905 | 388.7755 | 201.6014 | 265.5896 | 341.442 | 285.2674
1148.1917 | 139.4437 | 389.5749 | 201.8939 | 265.0596 | 339.4771 | 284.6353
1149.1917 | 139.2818 | 389.4158 | 202.1202 | 263.3177 | 340.5562 | 285.4112
1150.1917 | 139.3292 | 390.0022 | 202.296 | 262.7315 | 342.3294 | 285.8415
1151.1917 | 139.8746 | 390.0524 | 202.4814 | 262.1702 | 341.2576 | 284.8987
1152.1917 | 139.8713 | 390.1506 | 202.5889 | 262.8245 | 341.4154 | 285.5878
1153.1917 | 139.9841 | 390.3869 | 202.8746 | 262.473 | 339.5632 | 285.65
1154.1917 | 140.0225 | 390.4624 | 203.0016 | 262.1086 | 338.5343 | 286.3751
1155.1917 | 140.5045 | 390.7274 | 203.2884 | 262.0025 | 338.5687 | 287.9163
1156.1917 | 140.3002 | 390.8663 | 203.4194 | 265.0646 | 339.735 | 290.1484
1157.1917 | 140.3592 | 390.8419 | 203.6642 | 266.4708 | 340.17 | 290.2387
1158.1917 | 140.3699 | 391.1454 | 203.8176 | 268.2217 | 340.3705 | 291.1106
1159.1917 | 140.548 | 391.4988 | 204.0776 | 267.7096 | 341.9908 | 291.6803
1160.1917 | 140.818 | 391.8093 | 204.4326 | 268.1105 | 342.2064 | 292.897
1161.1917 | 140.8224 | 392.4368 | 204.7321 | 268.3736 | 342.3919 | 292.3685
1162.1917 | 140.9118 | 392.4802 | 204.9213 | 267.4282 | 341.4052 | 293.1388
1163.1917 | 141.0399 | 392.6399 | 205.1858 | 268.1719 | 341.8222 | 293.2451
1164.1917 | 141.0819 | 392.6943 | 205.3398 | 269.6218 | 342.4328 | 295.5002
1165.1917 | 141.1346 | 392.7604 | 205.6503 | 272.2548 | 343.0325 | 296.7145
1166.1917 | 141.1837 | 393.2983 | 205.7978 | 272.5301 | 343.413 | 297.3489
1167.1917 | 141.4932 | 393.5751 | 206.0939 | 275.235 | 345.1778 | 298.822
1168.1917 | 141.6756 | 394.0699 | 206.3088 | 274.5655 | 345.6589 | 299.082
1169.1917 | 141.5931 | 394.6019 | 206.4592 | 275.072 | 346.5015 | 299.9095
1170.1917 | 141.7011 | 394.9798 | 206.8095 | 273.998 | 347.9447 | 299.1979
1171.1917 | 141.9919 | 395.2105 | 206.9122 | 274.0187 | 347.6343 | 298.9214
1172.1917 | 142.1098 | 395.1888 | 207.1382 | 274.309 | 347.8119 | 300.4083
1173.1917 | 142.2243 | 395.3843 | 207.2784 | 274.5 | 347.7392 | 300.904
1174.1917 | 142.2774 | 395.6602 | 207.5005 | 277.2838 | 348.8453 | 301.9612
1175.1917 | 142.5619 | 395.6501 | 207.5015 | 279.1646 | 350.6452 | 302.5904
1176.1917 | 142.7055 | 396.0245 | 207.7645 | 278.428 | 350.8171 | 303.1438
1177.1917 | 142.7325 | 396.3775 | 208.0379 | 278.3025 | 352.0966 | 303.5421
1178.1917 | 142.756 | 396.654 | 208.395 | 278.136 | 353.489 | 304.0492
1179.1917 | 142.8325 | 396.5726 | 208.494 | 277.676 | 354.3988 | 303.672
1180.1917 | 142.7849 | 396.7493 | 208.6089 | 279.6531 | 355.6554 | 303.9338
1181.1917 | 143.0606 | 397.4495 | 209.0926 | 280.3056 | 355.442 | 303.8586
1182.1917 | 143.337 | 397.2493 | 209.0791 | 280.0193 | 355.4059 | 302.14
1183.1917 | 143.3063 | 397.7153 | 209.2181 | 282.2404 | 354.4049 | 302.8065
1184.1917 | 143.4957 | 398.34 | 209.5195 | 281.4998 | 354.4866 | 301.8101
1185.1917 | 143.5303 | 398.1733 | 209.7079 | 281.1097 | 355.2107 | 302.3465
1186.1917 | 143.7256 | 398.461 | 209.8881 | 281.8336 | 356.0797 | 303.8232
1187.1917 | 143.8193 | 398.8501 | 210.0582 | 282.1234 | 356.2937 | 303.7684
1188.1917 | 143.7236 | 399.186 | 210.4228 | 281.4554 | 356.7902 | 304.1049
1189.1917 | 143.852 | 399.233 | 210.4808 | 283.1492 | 356.7106 | 303.8402
1190.1917 | 144.1301 | 399.5959 | 210.6129 | 284.0917 | 356.5698 | 304.6918
1191.1917 | 144.1703 | 400.0378 | 210.8694 | 285.9896 | 356.6662 | 304.9399
1192.1917 | 144.5095 | 400.3721 | 211.4919 | 284.3074 | 357.3639 | 306.0451
1193.1917 | 144.6599 | 400.8821 | 211.5291 | 285.6715 | 357.9342 | 305.4512
1194.1917 | 144.7927 | 401.3179 | 211.8222 | 286.851 | 358.4025 | 305.8147
1195.1917 | 144.6971 | 401.5405 | 211.9454 | 286.5156 | 358.3306 | 304.8257
1196.1917 | 144.8332 | 401.9645 | 212.3806 | 284.2368 | 357.0449 | 303.6417
1197.1917 | 144.9278 | 402.2246 | 212.5813 | 284.9618 | 356.848 | 302.6849
1198.1917 | 145.1332 | 401.9649 | 212.7787 | 284.2801 | 357.1492 | 303.5724
1199.1917 | 145.1003 | 402.7787 | 212.9881 | 284.0105 | 358.0992 | 303.4335
1200.1917 | 145.2063 | 403.5057 | 213.258 | 284.0724 | 359.6867 | 302.3901
1201.1917 | 145.4936 | 403.6592 | 213.5356 | 284.7158 | 361.7845 | 304.0247
1202.1917 | 145.6971 | 403.6623 | 213.6381 | 285.0703 | 363.129 | 305.1298
1203.1917 | 145.7553 | 403.8639 | 213.7669 | 285.0001 | 362.8096 | 307.2314
1204.1917 | 145.9842 | 404.6165 | 213.9925 | 286.5246 | 362.8083 | 309.4401
1205.1917 | 146.3287 | 406.0487 | 214.4168 | 286.7257 | 364.5014 | 309.5251
1206.1917 | 146.5336 | 406.0592 | 214.9948 | 286.3223 | 364.8658 | 309.3346
1207.1917 | 146.5875 | 406.0116 | 215.0324 | 286.4849 | 365.4375 | 308.438
1208.1917 | 146.6279 | 405.8153 | 215.0624 | 285.8747 | 363.4537 | 307.6033
1209.1917 | 146.8042 | 406.1527 | 215.2862 | 285.3542 | 362.241 | 307.2995
1210.1917 | 147.0427 | 406.5865 | 215.3312 | 285.9363 | 362.172 | 307.1295
1211.1917 | 147.2714 | 406.9599 | 215.6019 | 284.9343 | 362.2501 | 308.6897
1212.1917 | 147.2929 | 407.4069 | 215.7763 | 284.836 | 362.2819 | 308.6146
1213.1917 | 147.5527 | 408.2312 | 216.1088 | 284.0562 | 362.5695 | 309.3429
1214.1917 | 147.7036 | 408.42 | 216.3144 | 284.1298 | 363.6769 | 309.1115
1215.1917 | 147.9299 | 408.7818 | 216.7223 | 282.7608 | 364.712 | 309.3686
1216.1917 | 148.0089 | 408.9362 | 216.8579 | 282.4766 | 364.4569 | 307.5407
1217.1917 | 147.9037 | 409.2727 | 217.0434 | 281.772 | 364.4657 | 307.273
1218.1917 | 147.9829 | 410.3318 | 217.2744 | 281.6504 | 364.6497 | 307.3387
1219.1917 | 148.2355 | 410.4763 | 217.6823 | 281.333 | 366.0546 | 308.0104
1220.1917 | 148.2655 | 410.6869 | 217.9109 | 281.9471 | 367.269 | 308.5353
1221.1917 | 148.6523 | 410.8667 | 218.1882 | 283.2317 | 366.4556 | 308.356
1222.1917 | 148.6838 | 411.3531 | 218.4883 | 283.8232 | 366.539 | 309.2562
1223.1917 | 148.7938 | 411.4936 | 218.7098 | 283.4585 | 366.1477 | 308.7831
1224.1917 | 148.851 | 412.3147 | 218.8807 | 285.6164 | 366.9986 | 308.1132
1225.1917 | 148.82 | 412.6534 | 218.8769 | 286.0806 | 366.7542 | 309.0115
1226.1917 | 148.8481 | 413.0443 | 219.3903 | 285.5683 | 366.278 | 308.8091
1227.1917 | 149.0764 | 413.1484 | 219.6448 | 285.6189 | 365.2413 | 307.9909
1228.1917 | 149.2999 | 413.437 | 219.9333 | 284.5616 | 362.5774 | 305.8745
1229.1917 | 149.5677 | 413.6816 | 220.0312 | 285.1153 | 361.9392 | 304.8812
1230.1917 | 149.5532 | 413.9971 | 220.4345 | 284.4145 | 362.6534 | 303.2697
1231.1917 | 149.7007 | 414.5421 | 220.4911 | 284.3796 | 363.3546 | 304.9859
1232.1917 | 149.7391 | 415.0031 | 220.8345 | 284.6884 | 364.4195 | 305.3155
1233.1917 | 149.8231 | 414.88 | 220.7934 | 285.6701 | 366.1915 | 306.0344
1234.1917 | 149.9968 | 415.1899 | 220.9363 | 285.4432 | 367.6545 | 306.6915
1235.1917 | 150.2306 | 415.6926 | 221.269 | 286.1819 | 368.0619 | 306.504
1236.1917 | 150.3206 | 415.8845 | 221.677 | 287.6798 | 368.2853 | 305.997
1237.1917 | 150.3107 | 415.7611 | 221.8439 | 287.6845 | 367.3085 | 306.0382
1238.1917 | 150.441 | 416.4587 | 221.9577 | 287.8542 | 366.5979 | 306.9948
1239.1917 | 150.6259 | 416.6314 | 222.0074 | 287.8894 | 366.3701 | 308.0101
1240.1917 | 150.7396 | 416.7648 | 222.2645 | 287.7252 | 366.8365 | 307.4946
1241.1917 | 150.7519 | 417.4375 | 222.5825 | 288.1163 | 368.4042 | 309.6366
1242.1917 | 150.9203 | 417.5837 | 222.686 | 290.0448 | 370.9213 | 310.4671
1243.1917 | 151.0004 | 417.7072 | 223.0987 | 290.6757 | 372.8436 | 312.0634
1244.1917 | 150.9669 | 417.8788 | 223.1726 | 290.4182 | 372.8892 | 311.8153
1245.1917 | 150.8953 | 418.0734 | 223.361 | 291.5696 | 373.1074 | 313.3305
1246.1917 | 151.1192 | 418.8985 | 223.5004 | 292.834 | 374.0937 | 314.3536
1247.1917 | 151.5357 | 419.2281 | 223.795 | 293.2829 | 374.6932 | 315.7405
1248.1917 | 151.6017 | 419.6178 | 224.0608 | 293.2477 | 374.2532 | 316.5004
1249.1917 | 151.7088 | 419.7705 | 224.3367 | 293.5572 | 375.1291 | 316.7013
1250.1917 | 151.7552 | 419.8522 | 225.1463 | 292.8743 | 375.4903 | 316.2684
1251.1917 | 151.9399 | 420.5067 | 225.1187 | 293.5051 | 374.8782 | 315.5581
1252.1917 | 152.2839 | 420.5901 | 225.3178 | 293.1023 | 374.1319 | 314.2604
1253.1917 | 152.2896 | 420.7878 | 225.428 | 293.5676 | 373.4531 | 314.1429
1254.1917 | 152.3164 | 421.1195 | 225.9088 | 293.4123 | 372.7002 | 313.9753
1255.1917 | 152.4588 | 421.5324 | 226.0893 | 293.4636 | 372.4755 | 313.9661
1256.1917 | 152.7848 | 421.5922 | 226.0892 | 292.7568 | 371.9736 | 312.8835
1257.1917 | 152.7526 | 421.6941 | 226.2466 | 294.0438 | 372.098 | 312.6498
1258.1917 | 152.8691 | 422.0219 | 226.4849 | 294.4454 | 372.6626 | 312.8344
1259.1917 | 152.8721 | 422.0951 | 226.7534 | 295.6752 | 373.097 | 314.2489
1260.1917 | 152.9446 | 422.2222 | 226.8859 | 297.8027 | 375.0418 | 315.4201
1261.1917 | 153.0048 | 422.6076 | 227.1473 | 298.1489 | 375.7705 | 317.5424
1262.1917 | 153.3384 | 422.99 | 227.3556 | 298.2004 | 376.4737 | 317.7147
1263.1917 | 153.3688 | 423.2892 | 227.8068 | 298.8025 | 375.9241 | 316.5132
1264.1917 | 153.6271 | 424.0689 | 228.1022 | 300.4394 | 375.4049 | 316.4802
1265.1917 | 153.5868 | 424.1419 | 228.3657 | 300.6653 | 375.5384 | 316.1122
1266.1917 | 153.8362 | 424.4901 | 228.673 | 300.1857 | 374.5973 | 314.1781
1267.1917 | 153.8588 | 424.6255 | 228.6638 | 301.7874 | 374.2754 | 313.9797
1268.1917 | 153.9657 | 424.8619 | 229.1048 | 300.6593 | 374.8534 | 315.5445
1269.1917 | 154.1665 | 425.3154 | 229.1766 | 301.8864 | 375.6724 | 315.0645
1270.1917 | 154.2919 | 425.5687 | 229.6326 | 303.2801 | 376.188 | 314.6085
1271.1917 | 154.3384 | 426.2 | 229.8517 | 304.091 | 375.4766 | 313.5303
1272.1917 | 154.3837 | 425.8672 | 229.7632 | 303.1171 | 374.9181 | 315.7596
1273.1917 | 154.5436 | 426.6299 | 229.9912 | 304.8431 | 376.4956 | 315.7916
1274.1917 | 154.7007 | 426.9038 | 230.2202 | 305.1505 | 380.5354 | 316.3069
1275.1917 | 154.9074 | 427.131 | 230.4363 | 305.9549 | 382.4407 | 318.429
1276.1917 | 154.9632 | 427.9801 | 230.7405 | 306.1387 | 384.9632 | 318.9564
1277.1917 | 155.1303 | 428.5504 | 231.0311 | 305.2569 | 387.1865 | 319.5483
1278.1917 | 155.5097 | 429.2361 | 231.1639 | 303.7687 | 388.986 | 321.1691
1279.1917 | 155.6741 | 429.1283 | 231.8416 | 305.364 | 390.4431 | 321.3878
1280.1917 | 155.7617 | 429.2738 | 232.0575 | 303.5653 | 389.4001 | 321.468
1281.1917 | 155.7386 | 429.3113 | 232.0371 | 304.5071 | 389.0404 | 321.9178
1282.1917 | 155.9948 | 430.1179 | 232.2596 | 308.062 | 390.9929 | 321.4328
1283.1917 | 156.1236 | 430.6003 | 232.4223 | 308.3226 | 391.4846 | 320.0758
1284.1917 | 156.2252 | 430.2826 | 232.4656 | 307.6844 | 390.8704 | 320.6766
1285.1917 | 156.3801 | 430.509 | 232.6181 | 306.947 | 391.1086 | 321.9129
1286.1917 | 156.6221 | 431.024 | 232.8979 | 310.2716 | 393.3872 | 322.5201
1287.1917 | 156.6421 | 430.9986 | 233.222 | 310.9745 | 393.4741 | 325.1996
1288.1917 | 156.6827 | 431.536 | 233.3952 | 312.0014 | 392.4585 | 325.4407
1289.1917 | 156.7593 | 432.0482 | 233.4235 | 311.6614 | 392.6186 | 326.0869
1290.1917 | 157.0593 | 432.4676 | 233.805 | 312.0823 | 392.9901 | 327.3963
1291.1917 | 157.0992 | 432.6931 | 234.1502 | 312.5786 | 392.6508 | 327.4586
1292.1917 | 157.4397 | 432.9619 | 234.2734 | 312.2123 | 392.9483 | 327.8441
1293.1917 | 157.8163 | 433.6911 | 234.5126 | 311.9687 | 393.1874 | 326.8539
1294.1917 | 157.7285 | 433.7588 | 234.9007 | 312.4057 | 394.3138 | 327.6328
1295.1917 | 157.784 | 433.6848 | 235.0402 | 310.9865 | 395.4629 | 327.4511
1296.1917 | 157.8491 | 434.02 | 235.1724 | 311.6528 | 394.825 | 327.7634
1297.1917 | 157.9945 | 434.7924 | 235.5007 | 312.6612 | 396.6886 | 328.364
1298.1917 | 158.3323 | 436.0297 | 235.7809 | 311.8689 | 395.3756 | 328.0446
1299.1917 | 158.7001 | 437.3484 | 236.2531 | 312.3484 | 397.1736 | 328.4423
1300.1917 | 158.8663 | 437.138 | 236.3313 | 313.6131 | 402.7335 | 328.7088
1301.1917 | 159.1449 | 437.8046 | 236.4807 | 313.5018 | 407.4217 | 331.1143
1302.1917 | 159.2812 | 438.2065 | 236.6972 | 314.5882 | 409.0453 | 331.829
1303.1917 | 159.2738 | 437.8921 | 236.8248 | 313.7241 | 408.3651 | 332.6979
1304.1917 | 159.1955 | 438.771 | 237.2613 | 312.7461 | 410.0442 | 333.9123
1305.1917 | 159.273 | 437.9801 | 237.396 | 313.9602 | 411.2832 | 332.473
1306.1917 | 159.299 | 437.909 | 237.5657 | 312.4255 | 408.5182 | 332.627
1307.1917 | 159.3981 | 438.4471 | 237.9595 | 312.0189 | 407.3593 | 331.3754
1308.1917 | 159.6367 | 438.6244 | 238.2346 | 315.9976 | 406.4293 | 330.7941
1309.1917 | 159.9455 | 438.6723 | 238.3577 | 317.9187 | 405.6108 | 331.3035
1310.1917 | 159.9467 | 439.6541 | 238.5837 | 320.0051 | 404.2721 | 331.4662
1311.1917 | 160.1614 | 439.8388 | 239.0788 | 321.0765 | 406.8393 | 335.6446
1312.1917 | 160.1343 | 439.9795 | 239.6941 | 321.8687 | 408.4221 | 337.1448
1313.1917 | 160.1357 | 440.1709 | 239.7313 | 322.3831 | 410.1929 | 336.1397
1314.1917 | 160.3758 | 440.7678 | 239.6873 | 324.6952 | 413.1571 | 335.354
1315.1917 | 160.757 | 441.9677 | 240.0238 | 323.5491 | 413.6962 | 336.0371
1316.1917 | 160.9727 | 442.6306 | 240.1737 | 323.9788 | 415.0162 | 335.9112
1317.1917 | 161.0584 | 442.891 | 240.4015 | 322.8026 | 417.7844 | 336.7506
1318.1917 | 161.2218 | 443.2725 | 240.5488 | 322.2899 | 418.7995 | 336.7231
1319.1917 | 161.4175 | 443.6363 | 240.7542 | 322.4021 | 420.8274 | 337.7042
1320.1917 | 161.5419 | 444.4607 | 241.0646 | 321.4063 | 423.0523 | 338.2855
1321.1917 | 161.6188 | 444.771 | 241.3133 | 322.4767 | 425.0794 | 338.1524
1322.1917 | 161.786 | 444.7917 | 241.4734 | 323.5361 | 425.1141 | 337.0379
1323.1917 | 162.0944 | 445.5445 | 241.7472 | 324.0402 | 426.5891 | 337.746
1324.1917 | 162.1697 | 445.8374 | 242.1449 | 325.7579 | 428.5417 | 336.4361
1325.1917 | 162.412 | 445.682 | 242.2435 | 326.7484 | 427.7925 | 336.8972
1326.1917 | 162.5401 | 445.6944 | 242.5369 | 328.3578 | 427.852 | 338.0805
1327.1917 | 162.5468 | 445.652 | 242.5181 | 327.7031 | 429.6429 | 336.5828
1328.1917 | 162.6072 | 446.3291 | 242.7052 | 327.4781 | 429.3911 | 335.544
1329.1917 | 162.7369 | 446.2485 | 243.0274 | 327.5038 | 427.0094 | 335.5849
1330.1917 | 162.7163 | 446.9137 | 243.6321 | 326.9056 | 425.8683 | 338.0224
1331.1917 | 162.7895 | 448.0737 | 243.875 | 327.7447 | 426.5702 | 340.5576
1332.1917 | 162.965 | 447.7377 | 243.9041 | 328.6193 | 426.6041 | 341.9377
1333.1917 | 163.1147 | 448.217 | 244.1834 | 328.9525 | 424.7302 | 343.2273
1334.1917 | 163.2331 | 447.8034 | 244.2719 | 329.6175 | 422.6342 | 343.4953
1335.1917 | 163.3614 | 448.0552 | 244.5929 | 331.1182 | 430.6813 | 346.0921
1336.1917 | 163.4362 | 448.3508 | 244.9096 | 331.5495 | 432.2929 | 344.2981
1337.1917 | 163.5453 | 448.6623 | 245.2242 | 331.5863 | 432.8393 | 342.9004
1338.1917 | 163.7731 | 448.5905 | 245.41 | 332.1537 | 432.9827 | 340.6763
1339.1917 | 163.7955 | 449.2855 | 245.4864 | 334.8687 | 431.5795 | 340.2177
1340.1917 | 164.1427 | 449.9353 | 245.9074 | 334.861 | 430.2022 | 340.6241
1341.1917 | 164.2835 | 450.021 | 246.3378 | 334.1013 | 430.5981 | 341.0163
1342.1917 | 164.4525 | 449.9621 | 246.7019 | 334.9373 | 431.8314 | 339.7915
1343.1917 | 164.4077 | 450.2302 | 246.9566 | 335.6162 | 432.8207 | 339.6522
1344.1917 | 164.8238 | 451.1009 | 246.9921 | 335.4594 | 433.4219 | 338.7458
1345.1917 | 164.7526 | 451.4435 | 247.1354 | 337.5032 | 436.5041 | 339.1671
1346.1917 | 164.903 | 452.4331 | 247.5384 | 337.1951 | 436.3305 | 338.4605
1347.1917 | 165.2176 | 451.9519 | 247.8053 | 338.8499 | 437.6866 | 340.4163
1348.1917 | 165.2878 | 451.9494 | 247.8434 | 338.8998 | 439.3612 | 341.0485
1349.1917 | 165.7921 | 452.6719 | 248.2491 | 340.0265 | 444.7212 | 342.9956
1350.1917 | 165.8979 | 452.6872 | 248.5253 | 339.7416 | 444.8313 | 343.4131
1351.1917 | 165.8458 | 453.1556 | 248.8148 | 342.8339 | 447.7685 | 344.86
1352.1917 | 165.9983 | 453.7958 | 249.0165 | 343.2418 | 450.9331 | 345.394
1353.1917 | 166.0084 | 453.8991 | 249.574 | 342.4779 | 449.4037 | 345.8289
1354.1917 | 165.9783 | 454.2149 | 249.6437 | 346.1638 | 450.9596 | 345.9253
1355.1917 | 166.1557 | 453.9843 | 249.7285 | 349.3567 | 451.6801 | 346.44
1356.1917 | 166.3114 | 454.1859 | 249.9274 | 347.9918 | 454.0998 | 345.5092
1357.1917 | 166.3906 | 453.9743 | 250.4607 | 346.1591 | 452.2184 | 342.9066
1358.1917 | 166.4848 | 454.0895 | 250.6784 | 344.5018 | 448.9614 | 340.4225
1359.1917 | 166.7924 | 454.8661 | 251.0411 | 346.8563 | 450.4687 | 339.4429
1360.1917 | 167.0416 | 455.3668 | 251.0398 | 345.7468 | 453.325 | 338.9693
1361.1917 | 167.1354 | 456.1356 | 251.3739 | 346.9311 | 456.4953 | 337.8248
1362.1917 | 167.3673 | 456.5991 | 251.4924 | 347.5352 | 457.7547 | 339.6985
1363.1917 | 167.3779 | 456.6241 | 251.705 | 346.6623 | 458.9408 | 340.6143
1364.1917 | 167.3797 | 457.2325 | 252.0778 | 348.4914 | 460.4094 | 342.77
1365.1917 | 167.6274 | 456.9215 | 252.397 | 350.6672 | 461.7333 | 342.4788
1366.1917 | 167.8662 | 457.2894 | 252.6205 | 352.1477 | 461.041 | 341.4582
1367.1917 | 168.0479 | 457.7216 | 253.2229 | 356.7696 | 463.0093 | 342.1319
1368.1917 | 168.014 | 458.2506 | 253.2455 | 359.7254 | 464.1233 | 344.3282
1369.1917 | 168.2578 | 458.6623 | 253.5124 | 358.6046 | 469.891 | 347.4454
1370.1917 | 168.7126 | 459.2974 | 253.8673 | 359.6896 | 471.8625 | 349.3863
1371.1917 | 168.8115 | 459.5324 | 253.9245 | 361.2706 | 474.2184 | 350.0663
1372.1917 | 169.2407 | 459.7918 | 254.2715 | 361.1247 | 476.4403 | 349.0683
1373.1917 | 169.4392 | 460.2735 | 254.5534 | 360.5641 | 477.0868 | 349.9612
1374.1917 | 169.4731 | 460.3214 | 254.763 | 361.3833 | 479.2449 | 352.2821
1375.1917 | 169.742 | 461.1278 | 255.0631 | 362.4173 | 484.3471 | 353.0622
1376.1917 | 169.9332 | 461.7055 | 255.4786 | 362.2538 | 486.1129 | 351.457
1377.1917 | 170.1295 | 461.7196 | 255.7465 | 364.7807 | 492.8324 | 352.0852
1378.1917 | 170.175 | 461.9377 | 255.6826 | 363.4733 | 496.773 | 352.7926
1379.1917 | 170.5348 | 462.9693 | 255.9627 | 364.7957 | 495.1963 | 354.2169
1380.1917 | 170.3797 | 462.5646 | 256.3441 | 366.7853 | 495.3544 | 356.2828
1381.1917 | 170.6201 | 462.2032 | 256.5511 | 368.4382 | 493.4521 | 359.1796
1382.1917 | 170.4355 | 462.4804 | 256.826 | 368.5431 | 488.5182 | 359.459
1383.1917 | 170.6119 | 463.1757 | 257.1704 | 367.3627 | 487.9369 | 357.5422
1384.1917 | 170.7894 | 463.7514 | 257.4133 | 365.6406 | 485.4197 | 357.8777
1385.1917 | 170.97 | 463.3529 | 257.7151 | 366.4411 | 482.1868 | 356.8255
1386.1917 | 171.0917 | 463.7871 | 257.7237 | 365.5289 | 480.3239 | 357.8266
1387.1917 | 171.0845 | 464.3536 | 258.2651 | 367.6834 | 484.557 | 361.5745
1388.1917 | 171.2234 | 464.4623 | 258.2857 | 370.0466 | 485.566 | 361.8831
1389.1917 | 171.7539 | 465.6882 | 258.5946 | 370.8909 | 488.0038 | 364.366
1390.1917 | 172.2238 | 465.591 | 258.9737 | 370.1666 | 486.8191 | 368.2758
1391.1917 | 172.0541 | 465.4694 | 259.3992 | 369.9481 | 485.5652 | 368.6313
1392.1917 | 172.1276 | 465.8338 | 259.7187 | 371.4768 | 487.7973 | 371.4336
1393.1917 | 172.1006 | 465.8894 | 260.0569 | 373.6199 | 486.3114 | 371.0228
1394.1917 | 172.1155 | 465.9462 | 260.3205 | 373.9742 | 483.0993 | 370.6289
1395.1917 | 172.3235 | 466.9122 | 260.489 | 374.1133 | 481.7227 | 370.0796
1396.1917 | 172.6662 | 467.7934 | 260.7883 | 376.4674 | 486.9194 | 372.1928
1397.1917 | 173.1104 | 468.7249 | 261.086 | 376.996 | 491.5318 | 371.6461
1398.1917 | 173.045 | 468.2151 | 261.1661 | 377.8453 | 499.5113 | 372.9786
1399.1917 | 173.2533 | 468.7643 | 261.5694 | 380.1777 | 503.161 | 374.956
1400.1917 | 173.5172 | 468.9252 | 262.1917 | 380.5057 | 506.4136 | 374.0335
1401.1917 | 173.8074 | 469.8554 | 262.5751 | 379.8627 | 507.4337 | 373.5986
1402.1917 | 174.0146 | 469.9564 | 262.453 | 379.4724 | 505.2122 | 372.35
1403.1917 | 174.048 | 470.3728 | 262.649 | 378.6557 | 509.227 | 373.4915
1404.1917 | 174.7026 | 470.685 | 262.9355 | 379.2796 | 512.1794 | 378.2056
1405.1917 | 174.6047 | 471.9248 | 263.2387 | 380.2865 | 514.0736 | 378.6288
1406.1917 | 174.5348 | 471.422 | 263.6034 | 380.2942 | 516.7681 | 377.4506
1407.1917 | 175.084 | 471.8935 | 264.0885 | 381.9149 | 515.7687 | 378.9055
1408.1917 | 174.9604 | 472.5191 | 264.5776 | 384.1992 | 518.7867 | 379.4452
1409.1917 | 174.8349 | 471.4686 | 264.4822 | 382.1085 | 520.244 | 378.4226
1410.1917 | 174.8669 | 471.814 | 264.7312 | 381.6242 | 519.1194 | 377.8517
1411.1917 | 174.9869 | 472.5081 | 265.1357 | 384.2717 | 519.2604 | 376.626
1412.1917 | 175.1447 | 472.9141 | 265.7166 | 387.5459 | 518.9076 | 378.1469
1413.1917 | 175.2317 | 473.3849 | 265.7853 | 387.1081 | 519.8598 | 377.8596
1414.1917 | 175.5368 | 474.4143 | 266.0717 | 389.5477 | 521.6456 | 381.9482
1415.1917 | 176.0992 | 474.1991 | 266.2966 | 390.5805 | 524.5956 | 384.0325
1416.1917 | 176.5592 | 475.1168 | 266.6803 | 390.4281 | 524.6161 | 384.0506
1417.1917 | 176.4157 | 474.6933 | 266.8549 | 390.8261 | 529.7861 | 384.3404
1418.1917 | 176.237 | 474.8322 | 267.2357 | 391.4525 | 530.8358 | 384.3577
1419.1917 | 176.5516 | 475.2899 | 267.3961 | 391.1865 | 531.0861 | 383.1972
1420.1917 | 177.0125 | 476.6656 | 267.8625 | 392.1085 | 536.7634 | 386.1882
1421.1917 | 177.1109 | 476.4151 | 268.3249 | 393.261 | 537.5656 | 385.4274
1422.1917 | 177.1975 | 475.9927 | 268.7387 | 393.9595 | 536.8094 | 383.6664
1423.1917 | 177.2091 | 477.0222 | 268.6837 | 394.2013 | 539.5684 | 384.3054
1424.1917 | 177.4748 | 477.3743 | 268.808 | 392.2466 | 538.8713 | 383.8627
1425.1917 | 177.8029 | 478.6337 | 269.3987 | 395.3363 | 541.2196 | 382.9273
1426.1917 | 177.9516 | 478.2987 | 269.5163 | 393.3181 | 541.0288 | 383.9216
1427.1917 | 178.0978 | 479.1555 | 270.2241 | 394.7029 | 538.8021 | 385.6336
1428.1917 | 178.2583 | 480.2746 | 270.3812 | 396.3814 | 542.8338 | 386.025
1429.1917 | 178.867 | 480.7847 | 270.7452 | 396.0859 | 548.6287 | 389.5901
1430.1917 | 178.792 | 480.1346 | 270.9091 | 395.5363 | 549.1568 | 388.6469
1431.1917 | 178.7696 | 480.4407 | 271.6122 | 396.57 | 552.3269 | 390.3529
1432.1917 | 178.9714 | 481.189 | 272.252 | 400.1523 | 553.9003 | 390.4536
1433.1917 | 179.0627 | 482.1192 | 272.2626 | 399.8527 | 554.2066 | 390.4381
1434.1917 | 179.4224 | 482.9299 | 272.3488 | 400.4837 | 554.1748 | 391.2203
1435.1917 | 179.936 | 483.1382 | 272.7915 | 400.8951 | 557.4748 | 394.1656
1436.1917 | 179.8457 | 482.9956 | 273.1095 | 400.0541 | 559.7583 | 393.0794
1437.1917 | 180.1704 | 484.1415 | 273.6697 | 402.0284 | 561.2745 | 392.263
1438.1917 | 180.446 | 485.2564 | 273.6376 | 402.9232 | 557.5782 | 392.4394
1439.1917 | 180.6222 | 485.213 | 274.0179 | 403.969 | 562.0255 | 393.3482
1440.1917 | 180.6743 | 484.6164 | 274.2463 | 403.0697 | 563.2908 | 395.4338
1441.1917 | 180.6377 | 485.3843 | 274.565 | 403.3159 | 563.7762 | 395.9094
1442.1917 | 180.8794 | 486.8531 | 274.9452 | 406.2919 | 565.5468 | 395.1917
1443.1917 | 181.4175 | 487.5147 | 275.2572 | 406.7818 | 565.8817 | 396.7757
1444.1917 | 181.8565 | 488.1953 | 275.7276 | 406.8076 | 575.4532 | 396.0497
1445.1917 | 182.5356 | 489.8577 | 276.2761 | 407.2954 | 579.9103 | 397.1766
1446.1917 | 182.5422 | 490.3815 | 276.5099 | 406.6794 | 578.3126 | 399.4987
1447.1917 | 182.4042 | 490.1689 | 276.732 | 406.0307 | 577.3321 | 399.0957
1448.1917 | 182.531 | 492.1547 | 277.3617 | 407.0077 | 576.3718 | 398.0542
1449.1917 | 182.6256 | 491.6247 | 277.8273 | 407.3028 | 577.0367 | 396.5803
1450.1917 | 182.838 | 491.1377 | 277.7481 | 409.4238 | 575.5531 | 396.0258
1451.1917 | 183.0252 | 491.5527 | 278.2205 | 410.7839 | 573.0376 | 399.4497
1452.1917 | 183.1961 | 492.886 | 278.2725 | 410.7434 | 576.5303 | 401.9732
1453.1917 | 183.4255 | 493.8033 | 278.4301 | 410.8679 | 579.6017 | 404.5496
1454.1917 | 183.5633 | 494.9524 | 278.7937 | 410.4844 | 578.9587 | 407.5151
1455.1917 | 183.9664 | 494.9711 | 278.9442 | 410.4256 | 579.5933 | 409.1441
1456.1917 | 184.0533 | 495.2016 | 279.1975 | 409.8483 | 578.7242 | 410.1976
1457.1917 | 184.3772 | 496.2045 | 279.6319 | 410.7978 | 578.4453 | 411.8698
1458.1917 | 184.6702 | 495.4909 | 279.8456 | 409.4322 | 576.6467 | 411.4545
1459.1917 | 184.7551 | 495.0954 | 280.2519 | 409.2214 | 575.4353 | 412.2184
1460.1917 | 184.7442 | 496.5997 | 280.8102 | 410.6096 | 577.9769 | 413.3908
1461.1917 | 184.9832 | 496.8863 | 281.2429 | 411.9533 | 578.3944 | 412.2613
1462.1917 | 185.0595 | 497.3112 | 281.7474 | 414.0597 | 575.4908 | 410.5468
1463.1917 | 185.1629 | 497.5953 | 281.7743 | 413.9876 | 577.959 | 411.3204
1464.1917 | 185.396 | 497.5781 | 282.0051 | 416.101 | 578.6331 | 412.8993
1465.1917 | 185.8285 | 498.7842 | 282.487 | 415.0132 | 583.1272 | 413.9748
1466.1917 | 186.0477 | 499.3476 | 282.8154 | 414.8719 | 584.3697 | 417.1631
1467.1917 | 186.2637 | 499.122 | 283.1563 | 415.0977 | 588.5201 | 416.8623
1468.1917 | 186.2798 | 499.3821 | 283.351 | 414.4478 | 586.6986 | 418.5021
1469.1917 | 186.43 | 499.8037 | 283.7632 | 416.3049 | 587.1736 | 419.6823
1470.1917 | 186.9079 | 499.6179 | 283.9904 | 416.3229 | 585.5082 | 418.4892
1471.1917 | 187.0784 | 500.6498 | 284.1499 | 418.1673 | 585.0376 | 418.9034
1472.1917 | 187.1085 | 501.3207 | 284.7052 | 418.252 | 586.5533 | 419.0043
1473.1917 | 187.3661 | 501.3019 | 284.9516 | 419.3258 | 589.2268 | 422.3869
1474.1917 | 187.6842 | 501.1785 | 285.1345 | 420.9936 | 588.0183 | 422.8122
1475.1917 | 187.8858 | 502.383 | 285.6808 | 422.0183 | 585.9207 | 422.6922
1476.1917 | 188.0052 | 502.267 | 285.8907 | 420.4127 | 584.0115 | 422.4105
1477.1917 | 188.2809 | 502.7865 | 286.1847 | 422.9837 | 585.244 | 421.9556
1478.1917 | 188.3675 | 502.9015 | 286.2555 | 422.0384 | 582.8886 | 422.2656
1479.1917 | 188.5856 | 503.2504 | 286.8809 | 423.0241 | 582.1625 | 420.6333
1480.1917 | 188.8193 | 503.4913 | 287.4712 | 425.8404 | 581.55 | 419.467
1481.1917 | 188.9638 | 503.4059 | 287.7409 | 428.9745 | 580.3315 | 417.6717
1482.1917 | 189.0676 | 503.2295 | 288.0439 | 428.7161 | 580.5747 | 416.7219
1483.1917 | 188.9546 | 504.4579 | 288.4921 | 429.6384 | 583.3842 | 414.5904
1484.1917 | 189.0409 | 505.3596 | 288.6259 | 431.2459 | 582.626 | 412.4587
1485.1917 | 189.4559 | 505.5982 | 288.8897 | 431.3877 | 582.2537 | 412.4816
1486.1917 | 189.6916 | 505.6064 | 289.2096 | 430.3513 | 582.6555 | 411.809
1487.1917 | 189.755 | 505.6539 | 289.6529 | 431.876 | 580.4581 | 413.7697
1488.1917 | 190.0137 | 506.334 | 289.9648 | 432.0604 | 581.8898 | 414.2889
1489.1917 | 190.1265 | 506.8171 | 290.189 | 433.1923 | 583.5074 | 412.1521
1490.1917 | 190.2081 | 506.9431 | 290.7738 | 433.34 | 583.028 | 413.7443
1491.1917 | 190.5489 | 507.4485 | 291.754 | 434.9329 | 583.645 | 414.8787
1492.1917 | 190.6676 | 508.2041 | 292.1239 | 434.3284 | 583.9595 | 414.536
1493.1917 | 190.9497 | 508.3361 | 292.0675 | 434.9865 | 586.0254 | 412.8987
1494.1917 | 191.4584 | 509.0956 | 292.2072 | 436.0279 | 591.3437 | 414.4972
1495.1917 | 191.8022 | 509.4994 | 292.404 | 434.4597 | 589.9792 | 416.0222
1496.1917 | 191.6692 | 508.9183 | 292.6405 | 434.6558 | 589.3784 | 418.5666
1497.1917 | 191.5202 | 509.3292 | 293.1594 | 434.7397 | 590.7018 | 420.8845
1498.1917 | 191.4809 | 509.599 | 293.278 | 433.7006 | 588.515 | 418.9781
1499.1917 | 191.8745 | 510.3247 | 293.8907 | 433.8117 | 590.5543 | 417.8047
1500.1917 | 192.5703 | 510.8303 | 294.261 | 434.7768 | 588.1167 | 419.3218
1501.1917 | 192.8664 | 512.3457 | 294.5601 | 436.8846 | 586.7259 | 421.2221
1502.1917 | 193.2471 | 512.3858 | 294.989 | 436.1811 | 588.4902 | 421.1115
1503.1917 | 193.5006 | 513.514 | 295.1796 | 436.6105 | 591.2085 | 420.6508
1504.1917 | 193.5005 | 513.9899 | 295.345 | 433.7784 | 587.2173 | 421.6143
1505.1917 | 193.7061 | 514.0036 | 295.6352 | 432.9312 | 588.3649 | 421.1716
1506.1917 | 193.8846 | 514.4581 | 296.2455 | 432.9153 | 591.0233 | 421.9654
1507.1917 | 194.004 | 515.3508 | 296.598 | 434.5984 | 591.2292 | 424.0382
1508.1917 | 194.1007 | 515.2357 | 296.9392 | 434.3405 | 589.8072 | 424.2082
1509.1917 | 194.1344 | 515.0052 | 297.238 | 433.6477 | 586.8205 | 425.1104
1510.1917 | 194.5286 | 516.842 | 297.6286 | 433.4636 | 586.4268 | 426.5541
1511.1917 | 194.7697 | 516.2621 | 298.0261 | 433.6836 | 586.07 | 427.1087
1512.1917 | 194.8464 | 516.6955 | 298.8248 | 434.5333 | 585.0577 | 428.6175
1513.1917 | 194.879 | 516.1059 | 299.0484 | 434.5191 | 588.0627 | 427.7207
1514.1917 | 195.0389 | 517.0072 | 299.3675 | 435.6536 | 585.933 | 427.7815
1515.1917 | 195.0888 | 516.7654 | 299.647 | 435.5869 | 586.119 | 427.138
1516.1917 | 195.3736 | 518.495 | 299.9167 | 437.8355 | 588.6338 | 426.5856
1517.1917 | 195.7513 | 518.8189 | 300.4377 | 437.8362 | 592.5489 | 428.0579
1518.1917 | 196.2992 | 519.6898 | 300.9399 | 437.6118 | 593.2726 | 429.2306
1519.1917 | 196.5021 | 521.7315 | 301.0741 | 440.2123 | 592.2275 | 430.9036
1520.1917 | 196.4975 | 519.8313 | 301.271 | 440.7314 | 589.3211 | 432.0759
1521.1917 | 196.792 | 520.432 | 301.7467 | 440.7918 | 587.9113 | 433.1376
1522.1917 | 196.9678 | 521.3436 | 302.5621 | 441.0189 | 592.2048 | 431.7606
1523.1917 | 197.3328 | 524.6457 | 303.4288 | 445.2715 | 596.6978 | 431.9977
1524.1917 | 197.4706 | 524.8454 | 303.426 | 445.0911 | 597.9656 | 431.0067
1525.1917 | 197.7174 | 526.5671 | 303.5485 | 448.1277 | 600.3895 | 431.108
1526.1917 | 197.8484 | 524.7505 | 303.6978 | 447.4958 | 595.5886 | 433.8212
1527.1917 | 198.0778 | 524.9216 | 304.054 | 446.9624 | 594.4988 | 436.4213
1528.1917 | 198.162 | 525.418 | 304.3525 | 447.1114 | 593.0313 | 441.0224
1529.1917 | 198.3029 | 525.1482 | 304.9043 | 447.6895 | 592.3879 | 443.2744
1530.1917 | 198.3931 | 525.7648 | 305.1311 | 448.2234 | 589.8317 | 445.3036
1531.1917 | 198.5021 | 525.8898 | 305.3544 | 448.0156 | 590.4502 | 446.2695
1532.1917 | 199.1096 | 525.6583 | 305.7762 | 448.1784 | 588.9626 | 444.3958
1533.1917 | 198.947 | 526.0893 | 306.3702 | 450.5719 | 592.4274 | 444.2379
1534.1917 | 199.1453 | 526.6724 | 306.7917 | 451.2703 | 593.7254 | 443.4808
1535.1917 | 199.4738 | 527.1322 | 307.1434 | 451.0278 | 593.7662 | 444.1542
1536.1917 | 199.8137 | 528.7485 | 307.6199 | 451.318 | 594.6644 | 445.07
1537.1917 | 200.088 | 528.8691 | 307.9629 | 451.6531 | 594.3401 | 444.9388
1538.1917 | 200.795 | 529.7418 | 308.283 | 451.4795 | 596.033 | 446.1035
1539.1917 | 200.8568 | 530.0207 | 308.5805 | 452.1868 | 598.4075 | 447.172
1540.1917 | 202.7604 | 530.045 | 309.1716 | 454.9521 | 596.7977 | 446.2512
1541.1917 | 201.7645 | 530.0864 | 309.5337 | 454.7481 | 598.8134 | 445.0481
1542.1917 | 201.1582 | 529.692 | 309.7133 | 454.9326 | 599.6523 | 445.2978
1543.1917 | 201.0779 | 529.2101 | 309.9055 | 455.3708 | 602.6501 | 443.7849
1544.1917 | 201.5042 | 530.8347 | 310.2812 | 456.993 | 608.3958 | 442.5836
1545.1917 | 203.4438 | 533.2392 | 310.9559 | 459.5522 | 606.9896 | 442.1808
1546.1917 | 202.269 | 531.2038 | 310.9143 | 458.2911 | 609.6519 | 443.6474
1547.1917 | 203.3772 | 533.6395 | 311.4383 | 457.2252 | 615.7584 | 440.7207
1548.1917 | 202.1247 | 531.9779 | 311.6139 | 457.5054 | 622.7731 | 441.2522
1549.1917 | 202.2343 | 532.0835 | 311.9366 | 459.5536 | 620.6293 | 439.1213
1550.1917 | 202.547 | 533.7862 | 312.6034 | 460.5644 | 620.3422 | 439.3661
1551.1917 | 202.6265 | 533.4495 | 312.9036 | 462.6341 | 620.5799 | 440.3649
1552.1917 | 202.8325 | 533.7861 | 313.3504 | 462.905 | 624.3195 | 438.9639
1553.1917 | 203.2044 | 533.8885 | 313.456 | 462.6364 | 624.045 | 437.7805
1554.1917 | 203.6443 | 534.7777 | 313.8561 | 462.5134 | 623.091 | 436.6659
1555.1917 | 203.6869 | 534.8671 | 314.4562 | 463.1688 | 622.9582 | 434.0122
1556.1917 | 203.769 | 535.4639 | 315.1198 | 466.3712 | 621.3501 | 433.6997
1557.1917 | 203.8605 | 535.0906 | 315.6303 | 467.3979 | 620.2521 | 434.2129
1558.1917 | 203.8135 | 535.7859 | 315.9171 | 469.6246 | 621.6286 | 432.9298
1559.1917 | 203.8051 | 536.1244 | 316.3316 | 473.6131 | 618.3869 | 432.8474
1560.1917 | 204.034 | 536.1277 | 316.4162 | 475.2385 | 620.0643 | 431.6168
1561.1917 | 204.5025 | 537.5852 | 316.7108 | 475.6367 | 620.9473 | 430.9764
1562.1917 | 204.7472 | 540.1118 | 317.0172 | 475.4445 | 622.1302 | 431.331
1563.1917 | 204.8833 | 539.0662 | 317.5598 | 477.2773 | 621.6588 | 433.4366
1564.1917 | 205.1341 | 538.3605 | 318.0961 | 476.5406 | 621.1479 | 434.9082
1565.2073 | 205.279 | 538.8526 | 318.5001 | 477.628 | 620.7277 | 438.3058
1566.1917 | 205.7253 | 539.5954 | 319.2553 | 479.6892 | 620.1795 | 439.1257
1567.1917 | 206.2765 | 540.1671 | 319.7749 | 479.2191 | 619.7741 | 439.64
1568.1917 | 206.4653 | 540.6529 | 319.7027 | 478.967 | 619.9181 | 440.6721
1569.1917 | 206.7511 | 542.5817 | 321.0071 | 478.4843 | 619.6561 | 442.75
1570.1917 | 207.1683 | 545.3158 | 321.5865 | 480.1649 | 619.9938 | 443.8862
1571.1917 | 207.1019 | 543.7625 | 321.5202 | 481.9821 | 620.4057 | 443.7487
1572.1917 | 207.3849 | 544.2271 | 322.371 | 481.8706 | 621.5488 | 444.7113
1573.1917 | 207.5987 | 547.7109 | 322.8148 | 484.0225 | 623.5953 | 445.7176
1574.1917 | 207.8843 | 547.5515 | 323.4202 | 486.7885 | 624.4603 | 446.6861
1575.1917 | 208.2555 | 548.7378 | 323.7803 | 488.8643 | 624.9558 | 447.0428
1576.1917 | 208.6162 | 548.1578 | 324.2055 | 489.2734 | 624.9197 | 447.6538
1577.1917 | 208.7675 | 548.2391 | 324.391 | 490.6875 | 626.6546 | 450.6306
1578.1917 | 209.1482 | 549.108 | 324.7615 | 491.8725 | 627.2973 | 452.3617
1579.1917 | 209.2196 | 549.2318 | 325.1009 | 492.6153 | 627.1356 | 452.6744
1580.1917 | 209.8755 | 548.568 | 325.7979 | 492.5066 | 625.8211 | 453.2776
1581.1917 | 210.1296 | 549.8162 | 326.3783 | 495.2225 | 624.2812 | 453.4841
1582.1917 | 210.4323 | 552.6158 | 326.5488 | 496.4245 | 623.774 | 454.311
1583.1917 | 210.524 | 552.0826 | 326.96 | 498.0994 | 623.4352 | 455.3077
1584.1917 | 210.6567 | 550.9208 | 327.2949 | 499.6896 | 624.8932 | 457.0681
1585.1917 | 211.0346 | 552.6565 | 327.671 | 499.5107 | 623.4517 | 457.9381
1586.1917 | 211.2151 | 552.5542 | 327.9458 | 499.9664 | 622.5934 | 461.1845
1587.1917 | 211.4293 | 553.4675 | 328.2476 | 500.3117 | 621.0791 | 463.8787
1588.1917 | 211.7979 | 554.8453 | 329.4277 | 497.8949 | 621.518 | 465.2091
1589.1917 | 212.3603 | 556.4932 | 329.6899 | 499.2419 | 623.6644 | 465.7099
1590.1917 | 212.8452 | 556.214 | 329.9134 | 500.4469 | 624.7943 | 465.7405
1591.1917 | 212.779 | 556.2038 | 330.4064 | 500.421 | 623.7642 | 468.2631
1592.1917 | 212.9613 | 557.6656 | 330.9989 | 501.8523 | 621.6293 | 469.4303
1593.1917 | 213.2527 | 557.1758 | 331.5187 | 501.4988 | 619.6697 | 470.4556
1594.1917 | 213.493 | 557.2419 | 331.7137 | 501.5007 | 619.5096 | 472.5589
1595.1917 | 213.9568 | 557.4277 | 332.1287 | 501.3981 | 618.4734 | 475.6145
1596.1917 | 214.3052 | 557.9827 | 332.407 | 501.4718 | 614.4899 | 477.6734
1597.1917 | 214.585 | 558.3718 | 333.0155 | 500.2494 | 616.565 | 477.9412
1598.1917 | 215.2853 | 561.1806 | 333.9033 | 501.6301 | 618.8477 | 478.0195
1599.1917 | 216.0227 | 560.9676 | 333.9548 | 503.5043 | 623.8883 | 479.8994
1600.1917 | 216.5945 | 562.3733 | 334.4828 | 501.9576 | 624.5161 | 481.7778
1601.1917 | 217.0017 | 563.3199 | 335.0385 | 502.9322 | 628.2643 | 484.8697
1602.1917 | 216.8719 | 562.3399 | 335.4449 | 504.0389 | 632.0237 | 485.6137
1603.1917 | 216.6105 | 563.8537 | 335.8485 | 506.5927 | 629.9058 | 486.7278
1604.1917 | 216.6895 | 564.285 | 336.5734 | 506.2343 | 629.6361 | 486.807
1605.1917 | 217.0512 | 563.8543 | 336.4137 | 506.8492 | 627.3573 | 488.5995
1606.1917 | 217.4264 | 564.5145 | 336.7801 | 505.3183 | 627.8736 | 492.7573
1607.1917 | 218.0091 | 564.69 | 337.3204 | 504.6419 | 625.9426 | 496.0799
1608.1917 | 218.2391 | 565.2612 | 337.3252 | 502.9699 | 626.096 | 499.4455
1609.1917 | 218.4408 | 564.523 | 337.8075 | 501.9048 | 628.4107 | 500.4581
1610.1917 | 218.5542 | 567.2386 | 338.3565 | 503.0713 | 628.4491 | 502.2419
1611.1917 | 219.0371 | 566.4267 | 338.9275 | 502.8888 | 628.084 | 504.2202
1612.1917 | 219.2662 | 566.4324 | 339.4647 | 503.8727 | 627.9014 | 505.1726
1613.1917 | 219.744 | 567.1411 | 340.1167 | 506.2203 | 625.989 | 507.5805
1614.1917 | 219.878 | 566.2665 | 340.054 | 505.3723 | 624.5051 | 508.3137
1615.1917 | 219.7476 | 566.4869 | 340.5178 | 505.8761 | 626.0145 | 507.5786
1616.1917 | 219.8672 | 567.2964 | 340.9269 | 505.842 | 628.0334 | 510.3102
1617.1917 | 220.4204 | 567.8545 | 341.3527 | 508.3186 | 628.2244 | 511.9766
1618.1917 | 220.8405 | 568.0111 | 341.9582 | 507.8237 | 628.6403 | 512.401
1619.1917 | 221.1782 | 568.0301 | 342.2036 | 508.2752 | 632.7544 | 511.3565
1620.1917 | 221.3321 | 568.4998 | 342.4849 | 510.258 | 631.972 | 513.4399
1621.1917 | 222.0559 | 569.7268 | 343.4872 | 510.1881 | 630.7801 | 515.7047
1622.1917 | 222.0882 | 571.3066 | 344.1914 | 510.3018 | 629.185 | 513.8814
1623.1917 | 221.902 | 570.7351 | 344.3891 | 511.6719 | 628.6662 | 512.2118
1624.1917 | 222.2844 | 571.6856 | 344.7678 | 512.4647 | 627.4687 | 509.8059
1625.1917 | 223.117 | 572.5449 | 344.9413 | 512.9768 | 627.6999 | 510.7833
1626.1917 | 223.1456 | 572.1889 | 345.6894 | 515.5631 | 627.9946 | 510.8101
1627.1917 | 223.4156 | 572.0038 | 345.8373 | 516.1026 | 626.9655 | 510.3065
1628.1917 | 223.2706 | 572.9083 | 346.7846 | 515.8986 | 628.348 | 509.7651
1629.1917 | 223.6001 | 573.8291 | 347.0079 | 517.3633 | 628.9528 | 511.3636
1630.1917 | 224.3289 | 574.0153 | 347.5757 | 519.1249 | 630.5334 | 512.2872
1631.1917 | 224.1906 | 573.4332 | 347.9016 | 519.3792 | 629.0329 | 512.4264
1632.1917 | 225.1063 | 575.0683 | 348.1292 | 519.0314 | 628.8235 | 515.1242
1633.1917 | 225.7797 | 574.623 | 348.8959 | 519.0728 | 628.8209 | 515.4238
1634.1917 | 225.9321 | 575.1554 | 349.4662 | 522.4613 | 626.7268 | 515.3741
1635.1917 | 226.0369 | 575.3584 | 349.7701 | 523.5219 | 626.7259 | 515.5841
1636.1917 | 226.0324 | 575.1678 | 350.1895 | 523.638 | 625.9491 | 515.6111
1637.1917 | 226.0601 | 575.0855 | 350.5702 | 523.949 | 626.7855 | 514.2706
1638.1917 | 226.9997 | 577.0914 | 351.1853 | 525.7942 | 624.8805 | 515.7228
1639.1917 | 226.8892 | 576.1734 | 351.5186 | 526.147 | 625.0349 | 516.1891
1640.1917 | 226.7293 | 575.4044 | 352.1139 | 526.9852 | 626.1392 | 515.528
1641.1917 | 227.1001 | 575.7291 | 352.5358 | 528.2864 | 632.1416 | 513.1719
1642.1917 | 227.6669 | 576.6761 | 353.5107 | 530.7614 | 632.5245 | 514.2116
1643.1917 | 228.0729 | 575.9177 | 353.6379 | 529.4972 | 629.1739 | 515.0643
1644.1917 | 228.7836 | 576.9391 | 354.1809 | 530.3436 | 626.2751 | 515.7673
1645.1917 | 229.4954 | 577.3953 | 354.6536 | 531.5117 | 629.4725 | 514.7727
1646.1917 | 230.2566 | 578.4824 | 355.4313 | 531.9626 | 628.5432 | 516.7418
1647.1917 | 230.3246 | 580.4091 | 356.0326 | 533.0789 | 628.2319 | 518.9892
1648.1917 | 230.5717 | 580.2097 | 356.2189 | 534.5475 | 628.2135 | 520.7899
1649.1917 | 230.6004 | 580.6215 | 356.8211 | 534.1352 | 626.4957 | 521.8295
1650.1917 | 230.9708 | 580.6291 | 357.4941 | 532.9399 | 626.3728 | 522.0339
1651.1917 | 231.2601 | 579.9635 | 357.735 | 534.3487 | 628.7029 | 521.556
1652.1917 | 231.7183 | 580.8994 | 358.6654 | 535.1269 | 629.9798 | 521.2714
1653.1917 | 231.6636 | 580.8482 | 359.3149 | 533.5182 | 631.5517 | 519.6864
1654.1917 | 231.4422 | 582.0983 | 359.8193 | 535.1024 | 628.5893 | 520.0973
1655.1917 | 231.6078 | 584.0064 | 360.2202 | 537.7025 | 632.7784 | 519.2957
1656.1917 | 232.1924 | 584.7356 | 360.8107 | 538.2936 | 635.2694 | 519.0211
1657.1917 | 232.6658 | 584.2127 | 361.4994 | 538.9165 | 634.1301 | 518.7003
1658.1917 | 233.6082 | 584.3615 | 361.7297 | 540.776 | 632.1936 | 520.1702
1659.1917 | 234.0463 | 584.2621 | 362.1916 | 544.2602 | 633.5662 | 522.8588
1660.1917 | 234.386 | 585.3642 | 362.6543 | 545.6251 | 633.7547 | 523.3271
1661.1917 | 234.4369 | 585.9242 | 363.0617 | 546.3188 | 631.3723 | 526.4329
1662.1917 | 234.5438 | 587.517 | 363.9028 | 547.5396 | 632.0233 | 527.6244
1663.1917 | 235.5625 | 586.6009 | 363.9316 | 549.4707 | 632.2881 | 530.2294
1664.1917 | 236.1723 | 588.7181 | 364.8496 | 549.3466 | 629.4349 | 532.6701
1665.1917 | 236.028 | 587.1532 | 365.309 | 550.653 | 630.1017 | 532.5349
1666.1917 | 236.4049 | 588.9269 | 365.8426 | 552.222 | 628.1027 | 534.0929
1667.1917 | 236.6092 | 588.7561 | 366.4138 | 553.2981 | 627.0137 | 535.1112
1668.1917 | 236.4392 | 588.6965 | 367.4122 | 554.0246 | 629.3835 | 535.8554
1669.1917 | 237.1202 | 589.1576 | 367.5571 | 554.0399 | 628.3219 | 537.1914
1670.1917 | 237.4334 | 589.6362 | 368.8135 | 555.7172 | 626.4681 | 538.8374
1671.1917 | 237.4396 | 590.0734 | 369.8642 | 557.6976 | 627.6874 | 538.4472
1672.1917 | 237.7967 | 591.524 | 371.4356 | 563.3272 | 634.6582 | 537.2374
1673.1917 | 237.649 | 592.619 | 372.1344 | 569.1293 | 639.2171 | 535.176
1674.1917 | 237.653 | 591.2754 | 371.4341 | 575.5909 | 643.4893 | 533.7378
1675.1917 | 238.5126 | 593.3957 | 372.0828 | 578.0349 | 646.0675 | 532.0074
1676.1917 | 239.8568 | 593.8676 | 372.7428 | 578.7016 | 643.3693 | 535.1417
1677.1917 | 240.783 | 594.0877 | 373.2971 | 580.8649 | 643.7074 | 539.6663
1678.1917 | 241.0885 | 593.9106 | 373.3236 | 581.6307 | 642.1404 | 541.6198
1679.1917 | 242.0982 | 593.7758 | 373.9509 | 581.875 | 643.6391 | 540.9024
1680.1917 | 243.1649 | 593.3207 | 374.2225 | 583.8789 | 646.2041 | 542.5163
1681.1917 | 243.1253 | 593.3087 | 374.5952 | 582.4808 | 645.2609 | 546.1711
1682.1917 | 244.3284 | 594.3377 | 375.8509 | 582.0448 | 643.7447 | 547.9613
1683.1917 | 245.0375 | 595.1766 | 376.3513 | 582.0394 | 641.8334 | 551.9921
1684.1917 | 244.6094 | 593.9878 | 376.2789 | 580.2567 | 639.7028 | 551.0325
1685.1917 | 243.7694 | 594.2127 | 376.8999 | 580.4122 | 637.8102 | 552.7298
1686.1917 | 245.0273 | 595.9173 | 378.3421 | 581.9927 | 638.7133 | 555.0487
1687.1917 | 245.0572 | 595.5602 | 378.4891 | 583.9778 | 638.8042 | 552.6444
1688.1917 | 245.5184 | 596.1827 | 378.5308 | 582.9601 | 638.5384 | 553.8983
1689.1917 | 245.9723 | 595.2309 | 379.0219 | 580.9197 | 635.1655 | 556.3977
1690.1917 | 246.5835 | 595.6896 | 379.7038 | 580.2162 | 634.3907 | 560.2555
1691.1917 | 246.9432 | 595.8264 | 380.3242 | 578.7806 | 636.9413 | 560.0831
1692.1917 | 247.7065 | 595.7982 | 381.1555 | 579.5862 | 635.7952 | 561.0145
1693.1917 | 246.8709 | 597.3012 | 381.5932 | 580.4619 | 633.3569 | 560.823
1694.1917 | 247.3803 | 597.5968 | 382.1146 | 581.5981 | 634.2414 | 559.9324
1695.1917 | 247.7857 | 596.8442 | 382.2791 | 583.7182 | 634.2236 | 561.3164
1696.1917 | 247.9772 | 598.1054 | 383.1516 | 582.9523 | 639.3613 | 563.0679
1697.1917 | 249.1368 | 598.0452 | 383.5685 | 584.5517 | 650.5332 | 562.0079
1698.1917 | 249.6441 | 598.0007 | 383.4218 | 586.002 | 647.7618 | 562.3314
1699.1917 | 250.5819 | 598.0301 | 384.003 | 585.1479 | 645.0491 | 567.9511
1700.1917 | 251.3066 | 597.7664 | 384.3686 | 587.4948 | 646.9854 | 571.521
1701.1917 | 250.8808 | 597.0287 | 384.9489 | 586.53 | 646.6501 | 570.8318
1702.1917 | 250.04 | 597.3426 | 385.3769 | 586.5963 | 645.6758 | 568.3492
1703.1917 | 250.8826 | 597.9906 | 386.3193 | 587.381 | 644.3028 | 565.8623
1704.1917 | 250.5113 | 598.5155 | 386.7973 | 586.303 | 641.3709 | 566.2003
1705.1917 | 251.0176 | 598.6374 | 387.2809 | 587.4992 | 643.775 | 566.3893
1706.1917 | 251.7487 | 598.4119 | 387.621 | 588.0126 | 642.7338 | 566.2759
1707.1917 | 252.0478 | 599.3572 | 387.9816 | 589.1695 | 644.5046 | 566.6233
1708.1917 | 251.9825 | 598.7105 | 389.0578 | 588.8058 | 642.7118 | 566.4108
1709.1917 | 251.9398 | 599.3503 | 389.7546 | 590.686 | 649.8855 | 566.2015
1710.1917 | 252.2235 | 600.053 | 389.5767 | 587.9574 | 646.6922 | 564.3937
1711.1917 | 252.4632 | 599.8573 | 390.7045 | 586.908 | 645.7015 | 564.5341
1712.1917 | 253.4746 | 601.4002 | 391.0282 | 587.8079 | 647.0341 | 563.4579
1713.1917 | 253.314 | 599.4751 | 390.988 | 587.8941 | 643.8741 | 563.7034
1714.1917 | 253.2049 | 599.5065 | 391.9041 | 587.8399 | 640.1438 | 561.7174
1715.1917 | 253.2785 | 600.0478 | 393.0442 | 586.7711 | 638.9717 | 560.0425
1716.1917 | 253.5162 | 602.0338 | 393.2616 | 587.5623 | 641.8048 | 559.0767
1717.1917 | 253.7053 | 602.5976 | 393.9136 | 588.7725 | 647.2149 | 557.8904
1718.1917 | 254.7578 | 602.4036 | 394.2568 | 588.532 | 645.325 | 559.5102
1719.1917 | 255.334 | 602.2091 | 394.8896 | 589.5396 | 648.0799 | 560.9944
1720.1917 | 255.4869 | 602.267 | 395.179 | 588.9616 | 647.7819 | 561.3979
1721.1917 | 256.4359 | 603.2431 | 395.5108 | 592.1441 | 646.2205 | 561.544
1722.1917 | 257.8839 | 603.2879 | 396.3071 | 590.4316 | 647.4187 | 563.5254
1723.1917 | 258.4112 | 603.2662 | 396.5385 | 593.7201 | 648.8454 | 565.137
1724.1917 | 257.7991 | 603.5751 | 396.6208 | 593.848 | 650.7 | 570.0854
1725.1917 | 257.8225 | 603.953 | 396.7709 | 592.5009 | 648.1614 | 570.727
1726.1917 | 259.6984 | 604.4991 | 397.1787 | 594.4421 | 648.673 | 570.5447
1727.1917 | 260.8338 | 604.4663 | 397.2965 | 594.0295 | 646.0983 | 572.0003
1728.1917 | 261.8886 | 604.5551 | 397.9456 | 594.2146 | 648.6061 | 575.2382
1729.1917 | 262.195 | 604.026 | 398.2238 | 597.4274 | 646.5559 | 576.6099
1730.1917 | 262.2151 | 603.8512 | 398.8943 | 594.1446 | 643.9156 | 576.3442
1731.1917 | 262.15 | 604.2614 | 399.2342 | 594.9087 | 645.1571 | 578.9031
1732.1917 | 263.0904 | 605.1374 | 399.6237 | 594.0433 | 643.3931 | 582.7186
1733.1917 | 263.5029 | 604.8729 | 400.2943 | 593.1029 | 646.9727 | 580.5474
1734.1917 | 262.6027 | 605.3534 | 400.9071 | 593.037 | 643.1064 | 577.3177
1735.1917 | 262.5608 | 605.6673 | 401.2063 | 591.6379 | 643.9813 | 576.0332
1736.1917 | 262.6238 | 605.9173 | 401.5994 | 590.8691 | 640.032 | 573.7038
1737.1917 | 264.7411 | 606.3969 | 402.1031 | 592.7531 | 642.091 | 577.7053
1738.1917 | 264.9791 | 605.5873 | 402.3843 | 592.3777 | 642.3937 | 575.345
1739.1917 | 264.8699 | 605.9371 | 402.9778 | 593.1548 | 641.1944 | 576.2779
1740.1917 | 266.063 | 606.0252 | 403.0672 | 592.8556 | 639.3571 | 580.9758
1741.1917 | 266.4051 | 606.2585 | 403.2259 | 592.2477 | 643.7529 | 584.4894
1742.1917 | 266.7804 | 606.0587 | 403.702 | 590.3833 | 642.3866 | 586.9236
1743.1917 | 268.0293 | 606.8107 | 404.1184 | 590.0689 | 642.059 | 587.5675
1744.1917 | 267.8951 | 606.4536 | 404.111 | 591.7491 | 644.5079 | 591.9781
1745.1917 | 268.6884 | 606.4191 | 404.5012 | 599.2493 | 642.8681 | 589.6368
1746.1917 | 269.419 | 606.7792 | 404.839 | 594.8351 | 642.7749 | 587.6843
1747.1917 | 269.808 | 607.0068 | 405.4807 | 595.1888 | 643.9929 | 591.1359
1748.1917 | 271.3552 | 606.6933 | 405.7443 | 597.4628 | 643.5699 | 591.755
1749.1917 | 271.8469 | 607.535 | 406.2811 | 596.6083 | 645.3689 | 592.0797
1750.1917 | 271.1296 | 607.727 | 406.6232 | 595.5055 | 646.4825 | 592.8211
1751.1917 | 270.7864 | 607.373 | 406.7637 | 594.2398 | 646.3528 | 595.3469
1752.1917 | 271.2407 | 607.2279 | 407.174 | 592.4017 | 646.6512 | 593.4163
1753.1917 | 271.5497 | 607.6657 | 407.6352 | 595.4566 | 647.6563 | 596.1076
1754.1917 | 271.3768 | 607.7423 | 408.0301 | 596.0269 | 646.3055 | 598.8332
1755.1917 | 272.3873 | 607.7601 | 409.1374 | 597.4988 | 648.9584 | 597.9658
1756.1917 | 273.1026 | 608.2379 | 409.4069 | 596.7605 | 648.0082 | 597.6333
1757.1917 | 273.03 | 608.4855 | 410.3197 | 596.3979 | 646.4793 | 596.9059
1758.1917 | 273.92 | 608.5948 | 411.104 | 597.2687 | 648.2437 | 595.8369
1759.1917 | 273.2497 | 608.1145 | 411.0099 | 596.188 | 643.5683 | 594.4173
1760.1917 | 273.5157 | 609.9581 | 411.6647 | 595.4131 | 641.1469 | 594.4965
1761.1917 | 274.0021 | 611.0029 | 412.8212 | 601.8495 | 647.6523 | 594.4758
1762.1917 | 274.1464 | 611.1835 | 412.7072 | 604.8625 | 654.8309 | 593.8795
1763.1917 | 274.2238 | 611.7794 | 413.832 | 603.4838 | 659.3732 | 595.0554
1764.1917 | 275.2018 | 610.9645 | 413.8551 | 602.6929 | 658.2959 | 594.8799
1765.1917 | 275.7826 | 610.7843 | 414.0987 | 602.7373 | 656.1198 | 593.3263
1766.1917 | 275.8452 | 611.3206 | 414.931 | 603.8605 | 653.8954 | 592.3759
1767.1917 | 275.4014 | 613.2433 | 415.034 | 604.111 | 653.6657 | 593.5659
1768.1917 | 275.2029 | 611.5228 | 415.7465 | 603.8018 | 653.2434 | 592.7061
1769.1917 | 275.126 | 612.2534 | 416.2464 | 603.8786 | 650.8588 | 592.6321
1770.1917 | 275.9871 | 612.84 | 416.6765 | 609.4347 | 653.1946 | 592.1309
1771.1917 | 277.4298 | 612.5631 | 416.8535 | 606.8511 | 651.2506 | 594.9464
1772.1917 | 279.3665 | 613.9732 | 417.0954 | 606.8463 | 653.9646 | 598.469
1773.1917 | 279.98 | 614.9831 | 417.774 | 611.8773 | 664.1342 | 604.7178
1774.1917 | 279.298 | 614.2298 | 418.5582 | 615.2088 | 663.0291 | 603.0667
1775.1917 | 279.2799 | 614.236 | 419.5083 | 616.5747 | 664.8822 | 601.5503
1776.1917 | 278.8582 | 614.5854 | 419.5272 | 618.9655 | 660.4908 | 601.4985
1777.1917 | 279.6391 | 613.7221 | 419.4352 | 619.764 | 662.4927 | 603.4093
1778.1917 | 279.5745 | 614.5564 | 420.1826 | 617.9651 | 665.2065 | 603.6502
1779.1917 | 279.6187 | 615.0251 | 420.7571 | 619.0676 | 662.655 | 602.2032
1780.1917 | 279.7917 | 615.7157 | 421.5177 | 615.8095 | 658.7148 | 601.614
1781.1917 | 280.8077 | 614.7562 | 421.987 | 616.0165 | 658.5913 | 603.2315
1782.1917 | 280.4748 | 617.33 | 422.9505 | 622.0588 | 662.4961 | 601.4558
1783.1917 | 280.6244 | 618.3064 | 423.6705 | 624.1965 | 665.8685 | 600.3962
1784.1917 | 280.5007 | 617.9156 | 423.6681 | 624.0033 | 664.2617 | 596.9441
1785.1917 | 280.8431 | 617.8072 | 423.6717 | 624.3497 | 664.8417 | 595.7108
1786.1917 | 281.3882 | 619.5105 | 424.4498 | 624.5095 | 666.7553 | 601.9706
1787.1917 | 282.6623 | 618.9788 | 425.174 | 622.2795 | 666.2239 | 601.8481
1788.1917 | 283.3495 | 618.5291 | 425.3743 | 624.6092 | 665.1303 | 599.9952
1789.1917 | 283.3367 | 621.9486 | 426.6706 | 625.2565 | 662.5364 | 600.1018
1790.1917 | 283.9186 | 621.5942 | 426.9276 | 623.941 | 663.9037 | 602.1438
1791.1917 | 285.0429 | 619.2133 | 426.8966 | 628.2747 | 667.0277 | 603.8212
1792.1917 | 284.6338 | 619.8986 | 427.3936 | 626.8548 | 665.9909 | 604.5575
1793.1917 | 284.9911 | 622.3681 | 427.7773 | 626.9209 | 664.3208 | 602.2254
1794.1917 | 285.9895 | 621.54 | 428.5844 | 625.3386 | 660.1276 | 603.0271
1795.1917 | 285.7979 | 621.9133 | 429.4755 | 624.4577 | 657.3754 | 603.2599
1796.1917 | 286.1176 | 621.8842 | 429.8306 | 630.7536 | 661.6566 | 608.5025
1797.1917 | 286.0825 | 621.4204 | 430.8139 | 635.9648 | 669.0547 | 614.7459
1798.1917 | 285.9489 | 622.8469 | 430.7285 | 637.1685 | 668.1496 | 611.1334
1799.1917 | 286.8092 | 623.1061 | 431.0589 | 635.4417 | 667.2563 | 614.8448
1800.1917 | 287.34 | 622.6349 | 431.4157 | 634.5327 | 666.3139 | 616.921
1801.1917 | 287.1938 | 622.8189 | 432.1843 | 633.9973 | 665.268 | 616.5385
1802.1917 | 287.1232 | 622.9566 | 432.7997 | 633.8223 | 664.634 | 615.2989
1803.1917 | 287.5727 | 623.8848 | 433.1796 | 635.0917 | 665.349 | 613.1514
1804.1917 | 288.6736 | 623.6198 | 433.1677 | 635.2519 | 666.3318 | 616.4369
1805.1917 | 288.7626 | 624.4172 | 433.4589 | 637.2443 | 664.4588 | 617.1146
1806.1917 | 288.5652 | 625.4319 | 434.8362 | 637.4852 | 669.213 | 617.3688
1807.1917 | 288.8937 | 624.4855 | 436.133 | 637.9728 | 673.8516 | 620.5059
1808.1917 | 288.7961 | 626.3018 | 436.3102 | 643.3162 | 680.9878 | 623.2775
1809.1917 | 289.1066 | 625.1349 | 436.9141 | 644.5041 | 679.7183 | 622.6087
1810.1917 | 290.1587 | 624.9519 | 437.6811 | 647.4946 | 680.4554 | 623.1786
1811.1917 | 290.9819 | 625.3592 | 437.8516 | 646.5767 | 676.2815 | 625.1722
1812.1917 | 292.2387 | 624.5414 | 438.3227 | 649.0041 | 676.4502 | 626.6658
1813.1917 | 292.7076 | 626.231 | 438.589 | 650.3216 | 677.7137 | 626.1811
1814.1917 | 291.5934 | 625.2455 | 439.0774 | 650.8576 | 674.5538 | 625.5875
1815.1917 | 291.1189 | 624.5174 | 439.1652 | 648.8167 | 671.2057 | 624.1146
1816.1917 | 291.5969 | 625.9451 | 439.1736 | 649.7165 | 671.4141 | 620.0657
1817.1917 | 292.2661 | 626.5478 | 439.9833 | 649.2166 | 669.1094 | 618.4644
1818.1917 | 292.212 | 625.4817 | 441.2715 | 651.806 | 669.5502 | 617.2908
1819.1917 | 292.2236 | 626.4465 | 441.5581 | 654.3275 | 670.6428 | 614.9204
1820.1917 | 292.126 | 625.701 | 441.3113 | 655.1238 | 670.4076 | 610.8939
1821.1917 | 292.0844 | 626.9036 | 442.1043 | 656.7145 | 672.112 | 611.1946
1822.1917 | 291.7842 | 626.8843 | 442.7863 | 658.298 | 673.3142 | 617.9025
1823.1917 | 291.7422 | 627.0845 | 443.2795 | 659.2752 | 669.9012 | 615.0528
1824.1917 | 292.2042 | 628.023 | 444.5487 | 659.9471 | 669.1759 | 613.5122
1825.1917 | 292.4035 | 628.911 | 445.244 | 658.9533 | 668.6786 | 612.7016
1826.1917 | 293.896 | 627.7251 | 445.3423 | 659.5 | 672.2272 | 612.0984
1827.1917 | 294.4952 | 628.2172 | 445.4709 | 657.5307 | 670.8649 | 611.6674
1828.1917 | 294.4331 | 626.9149 | 445.7617 | 663.5439 | 670.7177 | 611.6444
1829.1917 | 294.3978 | 627.0935 | 447.0343 | 665.0991 | 674.6283 | 609.7939
1830.1917 | 294.6491 | 628.0728 | 447.6709 | 669.6549 | 676.0204 | 607.3951
1831.1917 | 295.2223 | 626.5137 | 448.8848 | 667.5231 | 674.7507 | 607.0078
1832.1917 | 295.7357 | 627.0854 | 449.0294 | 669.5911 | 679.8476 | 617.2806
1833.1917 | 295.9805 | 628.2667 | 448.8961 | 665.8267 | 676.9362 | 616.009
1834.1917 | 295.6415 | 627.5209 | 450.1202 | 662.1769 | 676.7425 | 612.8072
1835.1917 | 295.5943 | 625.9863 | 450.7888 | 660.4261 | 678.4573 | 622.0344
1836.1917 | 295.7433 | 627.8524 | 451.6766 | 665.5315 | 681.085 | 618.9898
1837.1917 | 296.3287 | 627.2818 | 451.5027 | 662.4218 | 679.6454 | 620.6589
1838.1917 | 297.5739 | 627.1808 | 451.6814 | 662.2665 | 679.8191 | 619.2999
1839.1917 | 297.5315 | 626.2921 | 452.7438 | 666.5264 | 680.8262 | 615.6516
1840.1917 | 297.8667 | 626.7231 | 452.6858 | 665.2891 | 678.8499 | 611.8687
1841.1917 | 297.7462 | 626.5305 | 453.2101 | 663.9133 | 678.1728 | 608.7526
1842.1917 | 298.1326 | 626.795 | 454.337 | 659.6066 | 673.8104 | 607.0861
1843.1917 | 298.8457 | 628.666 | 454.4594 | 659.927 | 673.6118 | 608.1272
1844.1917 | 299.5417 | 627.567 | 454.5399 | 662.5384 | 670.4833 | 607.8157
1845.1917 | 300.1849 | 627.4024 | 454.8261 | 659.8212 | 667.6383 | 608.861
1846.1917 | 300.5431 | 627.1163 | 455.1393 | 661.2536 | 667.3593 | 608.54
1847.1917 | 301.5063 | 627.5358 | 455.573 | 665.2297 | 668.535 | 609.1301
1848.1917 | 302.1587 | 627.8328 | 455.2194 | 661.9154 | 672.3083 | 613.6674
1849.1917 | 301.9518 | 627.4427 | 455.1971 | 659.8246 | 671.3028 | 613.3024
1850.1917 | 301.6374 | 627.4459 | 455.7639 | 663.2454 | 670.2347 | 614.4952
1851.1917 | 301.9335 | 628.3316 | 456.5071 | 663.9828 | 667.825 | 612.5266
1852.1917 | 301.9121 | 626.4293 | 456.6752 | 664.4052 | 668.3946 | 609.4289
1853.1917 | 302.5353 | 625.9232 | 457.4245 | 662.1953 | 670.6664 | 610.7712
1854.1917 | 302.3799 | 627.282 | 457.5845 | 664.9439 | 675.1586 | 610.501
1855.1917 | 302.474 | 627.8559 | 457.7369 | 664.5039 | 673.0411 | 607.4846
1856.1917 | 302.9507 | 628.1588 | 457.9445 | 662.2773 | 671.8973 | 608.8104
1857.1917 | 303.4186 | 627.5268 | 457.7956 | 661.1939 | 671.1958 | 615.2616
1858.1917 | 304.077 | 629.8771 | 458.5364 | 661.7987 | 671.9378 | 615.2568
1859.1917 | 304.2927 | 629.3635 | 459.6226 | 661.2583 | 671.4466 | 617.2021
1860.1917 | 304.07 | 627.1206 | 459.7599 | 664.2726 | 672.538 | 613.152
1861.2073 | 304.1816 | 627.7324 | 460.2602 | 663.026 | 672.8636 | 609.4637
1862.1917 | 305.767 | 629.3077 | 460.5167 | 663.2583 | 675.0042 | 613.2127
1863.2073 | 307.3584 | 628.0716 | 460.9349 | 667.974 | 679.483 | 613.5128
1864.1917 | 306.8445 | 628.4525 | 461.2886 | 665.7118 | 679.6661 | 610.5225
1865.1917 | 306.3513 | 629.5768 | 462.8536 | 666.9695 | 678.973 | 607.1665
1866.1917 | 306.7308 | 629.87 | 463.8174 | 669.8216 | 679.5825 | 620.2845
1867.1917 | 307.3052 | 631.4767 | 464.9324 | 672.4568 | 686.4434 | 623.842
1868.1917 | 307.6516 | 631.0627 | 465.1087 | 672.5696 | 682.944 | 622.6568
1869.1917 | 309.5204 | 631.0572 | 465.5612 | 672.9119 | 679.8296 | 624.5061
1870.1917 | 309.4431 | 631.0077 | 466.4052 | 674.5803 | 691.4449 | 633.6412
1871.1917 | 309.2351 | 631.4618 | 466.8929 | 673.4098 | 692.5207 | 631.2543
1872.1917 | 309.2394 | 631.4602 | 466.9252 | 671.3104 | 688.5905 | 629.0272
1873.1917 | 309.4266 | 630.8997 | 467.0505 | 672.5983 | 686.4338 | 626.6016
1874.1917 | 309.3701 | 630.4975 | 466.8252 | 672.14 | 685.3794 | 627.7633
1875.1917 | 309.8703 | 631.36 | 468.1219 | 672.6248 | 681.5299 | 626.068
1876.1917 | 310.2485 | 633.9698 | 469.7844 | 670.9286 | 681.4867 | 625.3594
1877.1917 | 310.4619 | 634.3511 | 471.4175 | 673.0055 | 688.4851 | 629.7441
1878.1917 | 310.9051 | 634.0373 | 470.1686 | 675.0945 | 689.8333 | 636.4536
1879.1917 | 312.4486 | 634.0654 | 471.1951 | 676.041 | 692.6901 | 639.7648
1880.1917 | 313.2527 | 633.663 | 470.6086 | 677.1653 | 688.9912 | 640.1514
1881.1917 | 313.2143 | 632.7765 | 471.6119 | 674.2153 | 682.93 | 639.2601
1882.1917 | 313.5375 | 632.4209 | 470.8915 | 671.0889 | 679.8888 | 636.3086
1883.1917 | 313.7647 | 632.0643 | 471.4161 | 669.7578 | 677.4627 | 634.4464
1884.1917 | 313.7846 | 632.0645 | 471.8903 | 672.7984 | 679.4423 | 635.1046
1885.1917 | 313.9124 | 632.7181 | 471.8283 | 668.3708 | 679.9675 | 631.8616
1886.1917 | 315.0819 | 634.0545 | 472.0928 | 667.0498 | 676.5149 | 632.0752
1887.1917 | 317.2435 | 633.8664 | 472.5014 | 667.0042 | 680.823 | 637.3545
1888.1917 | 317.3797 | 634.502 | 473.0353 | 674.7706 | 690.6914 | 651.1113
1889.1917 | 317.716 | 634.0652 | 474.4246 | 673.7337 | 687.4586 | 646.8348
1890.1917 | 318.3633 | 634.1802 | 474.03 | 670.7589 | 684.9443 | 647.7012
1891.1917 | 317.7205 | 635.0274 | 474.7939 | 671.8035 | 691.162 | 647.7307
1892.1917 | 317.5022 | 636.1705 | 475.2322 | 675.4122 | 689.4925 | 642.4235
1893.1917 | 318.0182 | 633.6911 | 475.226 | 673.2003 | 682.5201 | 637.4232
1894.1917 | 318.1594 | 634.3476 | 475.5114 | 675.0395 | 681.8849 | 633.268
1895.1917 | 319.2913 | 636.0225 | 475.7908 | 672.8578 | 681.5112 | 630.7567
1896.1917 | 319.6941 | 635.052 | 475.8463 | 672.4481 | 677.3396 | 630.8897
1897.1917 | 319.4734 | 634.8851 | 476.84 | 672.846 | 681.4703 | 635.0042
1898.1917 | 319.7012 | 635.7479 | 476.7508 | 673.2033 | 678.0132 | 630.3095
1899.1917 | 319.9977 | 635.3628 | 477.9845 | 670.2464 | 680.3106 | 630.3447
1900.1917 | 320.2597 | 635.6465 | 478.2465 | 672.0582 | 684.6062 | 629.6544
1901.1917 | 320.5919 | 635.2963 | 478.1131 | 669.3285 | 680.8539 | 631.2712
1902.1917 | 321.2668 | 634.8328 | 478.0757 | 668.4538 | 679.2095 | 634.3012
1903.1917 | 321.7613 | 636.0822 | 479.1389 | 667.8619 | 677.3752 | 636.1475
1904.1917 | 321.6648 | 637.8526 | 479.5251 | 669.9879 | 682.2683 | 639.3955
1905.1917 | 322.7575 | 636.7686 | 478.9324 | 670.2552 | 682.8858 | 638.7257
1906.1917 | 324.407 | 637.477 | 480.954 | 671.8442 | 683.3379 | 644.9766
1907.1917 | 324.2013 | 638.5818 | 482.8978 | 675.0266 | 689.3128 | 649.5019
1908.1917 | 323.9926 | 637.9272 | 482.545 | 672.5156 | 692.9925 | 647.3947
1909.1917 | 324.7443 | 638.6894 | 482.308 | 678.9162 | 696.3938 | 646.6573
1910.1917 | 324.8027 | 637.4376 | 481.4272 | 678.9044 | 696.328 | 646.3943
1911.1917 | 325.0713 | 635.7661 | 482.0715 | 677.3266 | 690.9432 | 647.1635
1912.1917 | 324.1872 | 636.8779 | 481.9332 | 677.3203 | 688.1216 | 647.5504
1913.1917 | 324.179 | 638.0286 | 482.8907 | 676.0334 | 686.8154 | 642.1605
1914.1917 | 324.3279 | 636.6745 | 482.9485 | 673.2537 | 681.6976 | 654.9394
1915.1917 | 325.3185 | 637.8348 | 482.5748 | 670.2099 | 680.2098 | 654.0991
1916.1917 | 325.2581 | 636.965 | 483.1718 | 670.0188 | 678.202 | 650.983
1917.1917 | 325.302 | 637.3665 | 483.0118 | 669.3203 | 676.2635 | 650.1322
1918.1917 | 324.9677 | 638.043 | 483.8171 | 670.6013 | 674.3256 | 647.0296
1919.1917 | 325.1798 | 636.5735 | 483.8146 | 668.3553 | 670.8023 | 640.3967
1920.1917 | 325.2339 | 638.088 | 485.2643 | 666.0316 | 668.2993 | 639.1668
1921.1917 | 325.9868 | 637.0128 | 484.6704 | 669.3548 | 673.2493 | 646.9194
1922.1917 | 326.7437 | 637.1494 | 484.5289 | 665.1921 | 668.0604 | 643.4287
1923.1917 | 327.1497 | 636.2874 | 485.5931 | 674.395 | 666.9351 | 640.8211
1924.1917 | 327.2114 | 637.0083 | 486.1511 | 675.3574 | 668.7756 | 638.0448
1925.1917 | 327.6253 | 636.2028 | 486.5098 | 679.2603 | 672.8366 | 648.3398
1926.1917 | 327.3609 | 638.6574 | 487.6565 | 676.3589 | 678.4796 | 648.6144
1927.1917 | 328.3827 | 638.2947 | 488.579 | 672.9524 | 678.0536 | 650.1321
1928.1917 | 329.967 | 638.1081 | 487.566 | 678.8513 | 676.7962 | 648.8356
1929.1917 | 330.5238 | 639.6802 | 488.6351 | 677.9362 | 676.7528 | 651.2105
1930.1917 | 330.5651 | 639.8355 | 489.8066 | 684.6268 | 681.8476 | 656.6744
1931.1917 | 331.2335 | 641.1241 | 490.1903 | 686.062 | 683.1199 | 654.1025
1932.1917 | 330.8997 | 640.6871 | 490.3076 | 691.793 | 686.1483 | 652.7719
1933.1917 | 330.7166 | 639.5602 | 489.9009 | 691.4478 | 688.8111 | 656.7989
1934.1917 | 331.8288 | 638.959 | 490.7024 | 686.4073 | 686.6659 | 656.1325
1935.1917 | 332.0164 | 638.4183 | 490.491 | 686.5385 | 684.0989 | 653.8785
1936.1917 | 332.0518 | 639.0545 | 491.2307 | 683.4023 | 682.8164 | 651.0231
1937.1917 | 333.7741 | 639.4762 | 491.1702 | 683.98 | 684.6841 | 652.277
1938.1917 | 333.5268 | 638.617 | 490.7567 | 684.6346 | 685.4294 | 659.1032
1939.1917 | 333.08 | 638.735 | 492.114 | 683.8686 | 683.5947 | 660.2624
1940.1917 | 332.9274 | 639.2159 | 491.8911 | 683.8222 | 688.9958 | 659.7189
1941.1917 | 334.2842 | 640.3704 | 492.1468 | 681.3589 | 686.5896 | 658.2171
1942.1917 | 334.5916 | 640.2084 | 492.1673 | 681.8079 | 686.9757 | 661.4999
1943.1917 | 335.4398 | 639.631 | 492.1169 | 681.0306 | 682.3318 | 656.5179
1944.1917 | 335.7406 | 640.1629 | 491.9129 | 684.6213 | 680.8845 | 655.4426
1945.1917 | 336.291 | 639.8394 | 492.2499 | 685.138 | 681.9216 | 651.176
1946.1917 | 336.9164 | 640.82 | 492.4926 | 680.0488 | 676.7198 | 646.9017
1947.1917 | 337.1134 | 642.5375 | 493.1685 | 678.6778 | 675.1125 | 646.8308
1948.1917 | 337.3674 | 641.8377 | 493.8939 | 678.7739 | 677.7919 | 647.374
1949.1917 | 337.2912 | 642.6811 | 494.4745 | 679.2357 | 684.6226 | 644.6942
1950.1917 | 337.254 | 642.5766 | 493.7703 | 679.5014 | 689.754 | 643.2536
1951.1917 | 337.5908 | 643.2029 | 494.7271 | 683.6769 | 693.1905 | 645.7411
1952.1917 | 338.1425 | 643.1984 | 495.8282 | 687.6361 | 690.3071 | 648.2868
1953.1917 | 338.1758 | 643.1441 | 497.2596 | 685.9064 | 685.4929 | 648.116
1954.1917 | 338.2634 | 642.9675 | 497.8836 | 689.4516 | 684.5689 | 647.8296
1955.1917 | 338.2584 | 644.0607 | 497.8808 | 691.4849 | 681.7526 | 642.6984
1956.1917 | 338.5398 | 641.802 | 498.8332 | 694.2678 | 685.9196 | 644.8738
1957.1917 | 338.8839 | 643.9167 | 498.043 | 690.3718 | 684.8158 | 644.1328
1958.1917 | 339.3393 | 643.4819 | 499.0989 | 687.682 | 684.8488 | 645.4321
1959.1917 | 340.4081 | 642.58 | 498.6843 | 685.4077 | 684.2905 | 645.3672
1960.1917 | 340.0915 | 641.2734 | 498.2056 | 680.581 | 685.6176 | 645.4612
1961.1917 | 339.9889 | 643.0181 | 498.4922 | 680.9777 | 683.7445 | 644.4372
1962.1917 | 339.8788 | 641.6326 | 499.3731 | 679.8092 | 685.1723 | 645.5883
1963.2073 | 340.4646 | 642.2291 | 499.3664 | 680.191 | 684.8161 | 645.4761
1964.1917 | 341.8645 | 642.6626 | 499.636 | 678.7682 | 681.3906 | 643.1497
1965.1917 | 341.5787 | 642.1313 | 500.4866 | 677.6544 | 680.2685 | 643.2629
1966.1917 | 343.389 | 641.6132 | 500.5017 | 677.9251 | 680.0427 | 651.8662
1967.1917 | 343.3483 | 642.8711 | 502.0158 | 672.7612 | 681.1278 | 653.4579
1968.1917 | 343.0457 | 643.2345 | 502.5005 | 673.165 | 680.9409 | 655.9876
1969.1917 | 343.6744 | 643.9752 | 502.7747 | 678.7538 | 682.8836 | 661.5689
1970.1917 | 343.351 | 642.6557 | 503.8661 | 678.3409 | 684.1203 | 655.4207
1971.1917 | 342.9123 | 641.8592 | 503.2926 | 679.3574 | 686.3146 | 650.1424
1972.1917 | 343.7187 | 643.0381 | 503.0186 | 678.7915 | 688.6046 | 650.2874
1973.1917 | 344.1703 | 644.2475 | 504.1543 | 677.6174 | 683.8683 | 649.4913
1974.1917 | 344.2774 | 643.5651 | 503.4199 | 678.4856 | 686.4155 | 653.9261
1975.1917 | 346.1163 | 643.8016 | 504.2845 | 680.2636 | 688.59 | 651.8641
1976.1917 | 345.9159 | 642.2669 | 504.203 | 678.5806 | 685.0043 | 658.6136
1977.1917 | 346.5783 | 641.7521 | 505.6179 | 676.9924 | 682.4917 | 653.4201
1978.1917 | 346.8521 | 643.3039 | 505.0614 | 676.9429 | 683.0694 | 652.716
1979.1917 | 347.5801 | 642.1679 | 505.5244 | 681.2646 | 681.1562 | 651.6012
1980.1917 | 347.4467 | 643.7071 | 505.4397 | 684.1754 | 684.6477 | 650.947
1981.1917 | 347.6475 | 642.9422 | 505.25 | 682.7644 | 682.5386 | 648.1734
1982.1917 | 347.5149 | 642.9385 | 505.8588 | 684.3289 | 678.5416 | 646.9864
1983.1917 | 348.3668 | 643.4671 | 507.286 | 683.9674 | 681.1947 | 649.9425
1984.1917 | 348.3115 | 644.1641 | 507.962 | 686.648 | 683.1295 | 667.3511
1985.1917 | 348.2249 | 646.4091 | 508.134 | 688.8739 | 684.7867 | 665.8859
1986.1917 | 348.8073 | 645.9568 | 507.4072 | 688.0362 | 687.484 | 682.0218
1987.1917 | 349.4067 | 645.82 | 507.1849 | 688.2454 | 685.5476 | 685.9268
1988.1917 | 349.1224 | 645.7834 | 506.9886 | 692.2834 | 685.491 | 679.4281
1989.1917 | 349.1422 | 645.2569 | 507.6254 | 693.7929 | 690.8428 | 676.3151
1990.1917 | 349.4014 | 646.0772 | 508.1076 | 692.4442 | 691.1842 | 673.789
1991.1917 | 350.5756 | 645.5459 | 507.7258 | 697.3729 | 691.4207 | 672.5215
1992.1917 | 350.8997 | 644.9015 | 507.9419 | 695.6464 | 686.7028 | 672.8885
1993.2073 | 351.0342 | 646.3058 | 508.4519 | 693.1745 | 689.9301 | 668.4575
1994.1917 | 351.0458 | 645.8531 | 508.6461 | 695.5554 | 688.216 | 665.082
1995.1917 | 352.1728 | 647.8029 | 508.9895 | 693.6868 | 687.9584 | 662.9544
1996.1917 | 352.3615 | 647.6675 | 508.8647 | 693.1936 | 689.5728 | 664.9941
1997.1917 | 353.1872 | 647.0543 | 508.5146 | 693.4076 | 692.1812 | 671.2923
1998.1917 | 354.4655 | 646.7176 | 510.0959 | 692.6787 | 692.7573 | 673.6029
1999.1917 | 354.2175 | 645.9835 | 509.1688 | 688.9827 | 687.4281 | 668.8394
2000.1917 | 355.2709 | 646.7736 | 510.2884 | 686.6647 | 684.1796 | 663.7644
2001.1917 | 355.3541 | 646.8239 | 509.7651 | 685.9044 | 685.9402 | 667.8605
2002.1917 | 354.5423 | 646.4034 | 509.1553 | 681.7209 | 683.2701 | 668.015
2003.1917 | 354.2453 | 646.6265 | 509.5347 | 680.3249 | 681.6796 | 662.4708
2004.1917 | 354.4323 | 645.8692 | 510.1937 | 678.6708 | 680.5793 | 661.078
2005.1917 | 354.6038 | 646.7478 | 510.0643 | 676.465 | 679.9295 | 658.9771
2006.1917 | 354.9455 | 646.4558 | 510.8074 | 676.2536 | 679.2253 | 655.2502
2007.1917 | 355.3984 | 646.5304 | 510.7999 | 675.51 | 677.2677 | 653.1276
2008.1917 | 356.1682 | 647.3092 | 512.124 | 675.8483 | 679.029 | 651.2954
2009.1917 | 357.7843 | 645.7058 | 510.9874 | 675.1384 | 677.7635 | 651.4407
2010.1917 | 357.5808 | 646.0802 | 513.128 | 672.7102 | 676.463 | 649.7222
2011.1917 | 358.3793 | 645.3225 | 512.8693 | 668.0477 | 675.6077 | 651.1634
2012.1917 | 358.227 | 645.6919 | 511.9504 | 667.5899 | 677.8922 | 648.1898
2013.1917 | 358.1204 | 644.7259 | 513.7635 | 670.6907 | 681.9963 | 651.4182
2014.1917 | 357.611 | 645.524 | 513.7459 | 673.0438 | 682.0415 | 649.8705
2015.1917 | 358.4685 | 647.3276 | 514.627 | 675.5355 | 683.117 | 648.5531
2016.1917 | 359.1175 | 645.9241 | 515.4874 | 675.1585 | 682.4157 | 652.8972
2017.1917 | 359.6894 | 646.0596 | 514.8821 | 673.8814 | 684.8622 | 654.909
2018.1917 | 359.6593 | 646.8365 | 515.1746 | 680.1136 | 691.9244 | 659.6722
2019.1917 | 359.8018 | 645.8816 | 517.1321 | 677.7392 | 688.0506 | 667.0038
2020.1917 | 360.8227 | 646.6466 | 516.4295 | 674.568 | 683.7843 | 667.3259
2021.1917 | 361.2677 | 646.012 | 517.1875 | 679.3685 | 683.6835 | 669.0953
2022.1917 | 360.6715 | 645.4495 | 517.1337 | 678.6531 | 684.9639 | 672.4178
2023.2073 | 360.5369 | 647.4496 | 517.0889 | 679.7256 | 686.1363 | 669.3258
2024.1917 | 361.1257 | 647.6923 | 517.27 | 679.1295 | 684.5665 | 668.3868
2025.1917 | 362.7237 | 647.9911 | 517.3532 | 679.8914 | 686.3086 | 679.0942
2026.1917 | 362.5815 | 646.9532 | 519.4049 | 681.1585 | 693.4161 | 676.9214
2027.1917 | 362.7277 | 648.2775 | 519.2135 | 685.0026 | 691.6296 | 673.0021
2028.1917 | 363.9696 | 648.1549 | 520.9218 | 683.7242 | 695.5968 | 684.7798
2029.1917 | 363.6962 | 648.4472 | 521.1914 | 684.3871 | 695.7696 | 681.5545
2030.1917 | 363.352 | 648.4665 | 519.7433 | 685.6812 | 694.7235 | 678.8317
2031.1917 | 363.4905 | 646.7814 | 520.6786 | 680.1425 | 688.483 | 674.2162
2032.1917 | 363.2791 | 648.2912 | 521.786 | 678.9535 | 687.8483 | 670.012
2033.1917 | 363.3425 | 648.5397 | 521.6156 | 682.0702 | 685.6654 | 667.5717
2034.1917 | 363.7392 | 647.3164 | 519.9094 | 681.3854 | 686.9593 | 664.6436
2035.1917 | 364.2364 | 647.3955 | 519.6266 | 682.8255 | 685.111 | 661.8764
2036.1917 | 365.0386 | 647.1464 | 519.9855 | 688.8283 | 684.3135 | 660.2906
2037.1917 | 366.0502 | 647.0401 | 520.4869 | 684.8934 | 682.843 | 660.8634
2038.1917 | 368.3606 | 646.9882 | 519.5262 | 686.0012 | 679.5589 | 663.5626
2039.1917 | 371.0543 | 647.4603 | 520.0223 | 685.4604 | 679.3785 | 667.5167
2040.1917 | 372.2268 | 647.1459 | 519.8257 | 687.8911 | 681.7261 | 673.8072
2041.1917 | 372.3076 | 646.4685 | 519.5412 | 686.2987 | 679.4783 | 674.9548
2042.1917 | 371.9511 | 646.169 | 519.7862 | 685.4958 | 677.2284 | 670.6176
2043.1917 | 370.7895 | 646.2261 | 519.898 | 693.271 | 675.0002 | 671.6637
2044.1917 | 370.0823 | 646.3767 | 521.0801 | 695.9802 | 672.6494 | 669.8154
2045.1917 | 371.5865 | 646.122 | 520.2568 | 700.5035 | 670.2104 | 664.4912
2046.1917 | 373.4594 | 646.0426 | 519.4828 | 701.5365 | 670.0088 | 671.2464
2047.1917 | 373.3908 | 645.7764 | 519.7873 | 699.7536 | 671.7278 | 669.8369
2048.1917 | 373.2259 | 645.7794 | 520.009 | 705.9917 | 671.0269 | 669.8927
2049.1917 | 373.5023 | 645.5731 | 520.0182 | 704.6663 | 669.3165 | 672.6748
2050.1917 | 373.3146 | 645.2495 | 520.0034 | 711.1444 | 667.6055 | 668.5404
2051.1917 | 373.6068 | 645.886 | 520.4082 | 709.2984 | 664.357 | 665.3567
2052.1917 | 373.5606 | 645.1612 | 519.6924 | 704.5861 | 664.0765 | 662.5093
2053.1917 | 372.9569 | 645.4395 | 520.2424 | 697.7411 | 662.5835 | 658.9425
2054.1917 | 373.2766 | 645.0306 | 521.0165 | 700.9979 | 661.0871 | 657.282
2055.1917 | 373.9236 | 645.9045 | 521.0683 | 696.6163 | 670.1433 | 662.167
2056.1917 | 373.781 | 646.2983 | 521.4165 | 690.0302 | 673.1247 | 658.6741
2057.1917 | 373.7305 | 646.5354 | 522.1922 | 683.7242 | 671.5766 | 657.1401
2058.1917 | 375.2143 | 647.4997 | 523.2228 | 684.0043 | 676.7056 | 657.8764
2059.1917 | 376.3888 | 646.9358 | 522.9569 | 682.111 | 678.9828 | 660.6078
2060.1917 | 376.6851 | 646.899 | 523.2916 | 679.9029 | 676.083 | 667.8745
2061.1917 | 376.8113 | 646.0808 | 524.3534 | 680.6144 | 671.3149 | 671.9169
2062.1917 | 376.6874 | 647.2928 | 524.8052 | 690.4617 | 673.5858 | 670.9538
2063.1917 | 376.7638 | 647.8851 | 525.9838 | 693.6346 | 674.4959 | 668.573
2064.1917 | 376.2925 | 648.1918 | 526.8419 | 691.5192 | 678.5459 | 677.988
2065.1917 | 377.8559 | 648.2481 | 528.9515 | 687.4705 | 685.241 | 687.1844
2066.1917 | 378.4786 | 647.0287 | 526.5995 | 681.0863 | 681.1789 | 685.9083
2067.1917 | 379.5111 | 647.5576 | 525.5652 | 684.883 | 679.5783 | 689.4378
2068.1917 | 380.5929 | 647.4215 | 527.0699 | 686.6918 | 684.4212 | 689.6136
2069.1917 | 382.2182 | 646.9658 | 526.7546 | 683.545 | 679.4772 | 683.1961
2070.1917 | 381.9653 | 647.7593 | 527.538 | 680.6702 | 679.7681 | 682.4608
2071.1917 | 382.7668 | 647.9704 | 527.4264 | 681.3261 | 681.6849 | 684.8625
2072.1917 | 382.9476 | 648.8988 | 527.7943 | 677.6338 | 677.6497 | 689.0647
2073.1917 | 382.9347 | 647.8175 | 529.623 | 677.7816 | 679.5069 | 691.9598
2074.1917 | 384.3303 | 647.7438 | 528.294 | 676.2921 | 675.6586 | 684.4419
2075.1917 | 385.1422 | 647.6105 | 529.534 | 674.0382 | 674.5842 | 681.7964
2076.1917 | 386.4942 | 646.8215 | 527.8199 | 673.6859 | 673.3937 | 680.7493
2077.1917 | 386.8942 | 646.8423 | 527.2492 | 672.0999 | 668.4476 | 683.1806
2078.1917 | 386.9781 | 646.7268 | 527.2702 | 671.9663 | 668.0486 | 689.6389
2079.1917 | 389.7067 | 646.4013 | 528.2762 | 666.3683 | 670.5008 | 691.005
2080.1917 | 390.7571 | 646.8905 | 527.2236 | 667.5122 | 670.5649 | 698.3492
2081.1917 | 391.0943 | 647.3882 | 527.9146 | 666.9555 | 674.0038 | 696.8185
2082.2073 | 390.69 | 646.8114 | 527.3112 | 662.8511 | 670.3919 | 701.7303
2083.2073 | 389.1401 | 645.6371 | 527.4375 | 658.6848 | 666.8176 | 693.6034
2084.1917 | 389.5583 | 646.2931 | 529.1148 | 660.629 | 665.149 | 695.1616
2085.1917 | 390.1487 | 645.757 | 529.006 | 661.091 | 666.4521 | 694.2425
2086.2073 | 389.5738 | 645.6625 | 528.8752 | 662.4321 | 663.5862 | 691.5973
2087.1917 | 390.3057 | 645.5318 | 529.8989 | 665.8661 | 660.0858 | 695.0659
2088.2073 | 391.1048 | 645.6229 | 530.2648 | 670.187 | 660.5739 | 698.8325
2089.1917 | 390.8005 | 645.8075 | 528.6103 | 662.3116 | 657.2611 | 690.0983
2090.1917 | 391.5318 | 646.3881 | 528.2214 | 666.0363 | 662.5005 | 689.538
2091.1917 | 392.0709 | 645.9891 | 529.9631 | 669.9511 | 659.3622 | 682.9663
2092.1917 | 392.124 | 645.9789 | 532.9079 | 671.393 | 659.9311 | 685.4995
2093.1917 | 392.2019 | 646.3587 | 530.748 | 670.0224 | 660.9262 | 687.7313
2094.1917 | 392.2594 | 646.4098 | 531.9612 | 670.796 | 660.8399 | 685.1152
2095.1917 | 392.4057 | 647.7078 | 532.3933 | 667.5121 | 663.9997 | 687.8147
2096.1917 | 394.3771 | 646.8937 | 531.6055 | 670.8658 | 670.4797 | 696.4941
2097.1917 | 393.7764 | 646.5433 | 531.8257 | 671.3833 | 668.7272 | 694.6893
2098.1917 | 394.5959 | 647.0453 | 532.7099 | 677.9419 | 666.438 | 691.5547
2099.1917 | 394.8313 | 647.4349 | 533.3038 | 681.6438 | 671.7129 | 688.0607
2100.1917 | 395.4528 | 647.1071 | 532.4275 | 678.8169 | 670.8141 | 687.9249
2101.1917 | 396.1505 | 646.7943 | 532.3348 | 676.717 | 665.7788 | 684.6225
2102.1917 | 396.0073 | 647.1398 | 533.5972 | 673.9424 | 670.4312 | 684.3693
2103.1917 | 397.0007 | 647.7026 | 534.1342 | 675.1185 | 667.8999 | 679.116
2104.1917 | 396.6472 | 647.5157 | 535.7958 | 681.6577 | 666.9213 | 683.3356
2105.1917 | 397.2233 | 647.169 | 535.7877 | 676.4366 | 666.3642 | 686.8083
2106.1917 | 397.2911 | 647.4428 | 535.6006 | 675.3593 | 669.6666 | 687.4529
2107.1917 | 397.431 | 648.6098 | 536.6417 | 675.9023 | 675.44 | 687.0547
2108.1917 | 397.0692 | 647.3296 | 536.6982 | 672.6134 | 675.0239 | 692.5868
2109.1917 | 396.7429 | 647.58 | 536.0996 | 669.5356 | 674.9446 | 691.524
2110.1917 | 397.4986 | 647.2699 | 534.7173 | 669.2835 | 671.7208 | 684.6778
2111.1917 | 399.4238 | 646.763 | 536.7362 | 663.4922 | 664.3016 | 679.5937
2112.1917 | 401.881 | 647.1379 | 537.4313 | 666.9288 | 667.016 | 684.974
2113.2073 | 401.6266 | 647.3767 | 535.1517 | 662.7198 | 664.4971 | 688.519
2114.1917 | 401.3862 | 646.9659 | 535.1089 | 672.9431 | 664.3721 | 697.16
2115.1917 | 400.7483 | 646.782 | 535.3759 | 669.7518 | 660.3336 | 696.46
2116.1917 | 401.6644 | 646.7164 | 535.1675 | 680.5709 | 657.455 | 689.5366
2117.1917 | 401.5226 | 646.7764 | 535.7066 | 682.8407 | 656.1968 | 681.4196
2118.1917 | 401.5528 | 646.2159 | 535.5809 | 683.6662 | 653.7269 | 677.5979
2119.1917 | 402.1077 | 646.3568 | 537.618 | 682.1158 | 654.8816 | 682.0235
2120.1917 | 402.1587 | 646.7262 | 537.7973 | 685.1999 | 651.1844 | 689.1309
2121.1917 | 402.7914 | 646.1711 | 536.1467 | 685.03 | 653.0932 | 690.6163
2122.1917 | 403.2081 | 645.8567 | 535.4291 | 689.0395 | 652.0649 | 689.5385
2123.1917 | 403.1831 | 646.3929 | 535.4294 | 685.7904 | 656.571 | 686.8042
2124.1917 | 402.9099 | 646.468 | 537.3987 | 682.8264 | 654.2703 | 680.8721
2125.1917 | 402.8453 | 646.2307 | 536.0439 | 690.2177 | 653.1236 | 679.8541
2126.1917 | 403.8892 | 646.147 | 535.4363 | 692.0725 | 651.9227 | 674.1762
2127.1917 | 404.4167 | 645.8527 | 534.9522 | 688.5402 | 649.7477 | 677.5994
2128.1917 | 404.7741 | 645.8669 | 534.7991 | 689.2164 | 648.9983 | 675.9096
2129.1917 | 405.7129 | 645.6157 | 534.9605 | 691.6715 | 653.3378 | 675.42
2130.1917 | 406.5617 | 645.669 | 534.2169 | 700.2468 | 651.6991 | 674.8887
2131.1917 | 408.1863 | 645.8329 | 534.2406 | 698.2789 | 649.0112 | 673.3188
2132.1917 | 408.7351 | 645.7876 | 533.972 | 706.1709 | 652.4602 | 675.7214
2133.2073 | 408.6987 | 646.0155 | 533.555 | 704.3446 | 651.3546 | 677.1414
2134.1917 | 407.7477 | 646.5067 | 534.2683 | 702.7016 | 653.606 | 682.0436
2135.1917 | 408.3492 | 646.9167 | 536.59 | 702.574 | 657.0955 | 681.6186
2136.1917 | 409.9389 | 647.2424 | 536.5327 | 704.2508 | 659.9239 | 684.773
2137.1917 | 410.5872 | 647.2623 | 536.2399 | 702.8237 | 671.4814 | 691.4338
2138.1917 | 411.5195 | 647.1049 | 535.7785 | 705.1786 | 669.9556 | 691.7952
2139.1917 | 412.8944 | 646.8448 | 536.6381 | 704.6791 | 664.1965 | 695.2162
2140.1917 | 413.2327 | 647.0557 | 536.6471 | 703.2202 | 671.7828 | 694.4118
2141.1917 | 412.9865 | 646.3291 | 538.673 | 702.6994 | 669.7675 | 690.0826
2142.1917 | 412.7836 | 646.5397 | 536.6084 | 707.1533 | 667.6796 | 689.0865
2143.2073 | 412.8945 | 647.0986 | 536.7627 | 701.6393 | 668.1706 | 690.9276
2144.1917 | 412.3561 | 647.2619 | 538.3061 | 700.5498 | 670.8294 | 697.0085
2145.1917 | 411.1877 | 647.6505 | 537.3746 | 695.6441 | 679.7492 | 693.819
2146.1917 | 412.0129 | 647.9375 | 537.834 | 691.9573 | 677.0342 | 691.5834
2147.1917 | 412.8258 | 648.2121 | 539.7779 | 691.3778 | 678.0679 | 707.6883
2148.1917 | 412.4729 | 648.0147 | 540.2188 | 686.1357 | 676.2194 | 698.9614
2149.1917 | 411.8973 | 648.8856 | 540.215 | 683.3769 | 685.7 | 704.5786
2150.1917 | 411.7759 | 649.1048 | 541.2515 | 682.7433 | 687.4687 | 705.9433
2151.1917 | 411.4808 | 648.178 | 540.9641 | 682.0094 | 694.4295 | 703.8083
2152.1917 | 411.8746 | 648.681 | 540.7941 | 680.5873 | 686.5102 | 706.6259
2153.1917 | 413.1432 | 648.8429 | 541.2213 | 679.1572 | 684.9831 | 706.8054
2154.1917 | 415.1444 | 649.4004 | 539.4808 | 676.521 | 685.6716 | 710.9981
2155.1917 | 417.7442 | 649.0603 | 539.0532 | 677.6411 | 688.8093 | 714.1074
2156.1917 | 417.9303 | 648.9897 | 538.7397 | 673.9676 | 683.8518 | 709.1628
2157.1917 | 418.2854 | 649.2337 | 540.8855 | 675.116 | 685.3058 | 703.0896
2158.1917 | 418.3823 | 650.4382 | 541.688 | 678.3672 | 680.3254 | 696.6251
2159.1917 | 419.1534 | 649.4974 | 540.5417 | 680.1189 | 688.5374 | 696.9609
2160.1917 | 420.3659 | 649.3634 | 539.7212 | 675.8915 | 684.3944 | 704.8174
2161.1917 | 422.109 | 648.7212 | 539.5033 | 674.8651 | 687.2875 | 702.2963
2162.1917 | 421.986 | 649.1552 | 539.9585 | 672.7706 | 681.8078 | 700.6206
2163.1917 | 420.4722 | 648.283 | 540.8798 | 673.555 | 674.7633 | 693.2754
2164.1917 | 419.7903 | 648.6778 | 540.7318 | 673.3978 | 669.9992 | 685.2674
2165.1917 | 419.8491 | 648.5831 | 539.7853 | 672.1778 | 665.848 | 678.8402
2166.1917 | 422.304 | 648.3311 | 538.9408 | 673.8561 | 661.909 | 675.28
2167.1917 | 423.15 | 648.6955 | 538.7231 | 673.549 | 660.5714 | 674.1666
2168.1917 | 422.3002 | 649.1269 | 539.1316 | 676.5941 | 665.5552 | 677.2394
2169.1917 | 422.0881 | 649.3768 | 542.7599 | 682.5655 | 672.0304 | 680.4064
2170.1917 | 422.695 | 649.1444 | 539.7757 | 686.5744 | 676.4721 | 685.2527
2171.1917 | 424.25 | 648.7787 | 539.1544 | 688.9893 | 675.5391 | 691.0341
2172.1917 | 424.5976 | 649.3569 | 539.2886 | 686.6915 | 682.5969 | 698.8492
2173.1917 | 424.9735 | 648.7272 | 540.6311 | 686.1182 | 678.8147 | 703.0404
2174.1917 | 423.9844 | 648.8441 | 540.9541 | 688.5953 | 673.9373 | 709.4209
2175.1917 | 424.4104 | 648.8334 | 540.5322 | 690.0657 | 671.8221 | 707.4831
2176.1917 | 425.6703 | 649.3351 | 540.2449 | 687.865 | 668.9484 | 709.5104
2177.1917 | 426.0906 | 648.7947 | 540.4646 | 688.74 | 673.5309 | 710.4361
2178.1917 | 426.3254 | 649.5473 | 541.4858 | 688.4808 | 677.6902 | 708.5319
2179.1917 | 426.4321 | 648.7926 | 541.9962 | 685.9198 | 679.3257 | 704.3497
2180.1917 | 426.7404 | 649.0877 | 542.1891 | 688.779 | 673.403 | 706.6488
2181.1917 | 429.3289 | 649.7775 | 541.3133 | 689.5514 | 669.1458 | 708.7611
2182.1917 | 430.0485 | 649.5864 | 543.1325 | 694.0908 | 686.3613 | 720.8056
2183.1917 | 430.2011 | 649.983 | 543.2634 | 689.5536 | 686.855 | 727.9897
2184.1917 | 429.0037 | 649.881 | 542.9948 | 686.0067 | 689.9507 | 730.1491
2185.1917 | 427.8961 | 649.296 | 541.6124 | 681.9142 | 684.6254 | 724.8014
2186.1917 | 428.0085 | 650.0227 | 543.422 | 680.3142 | 687.3641 | 727.3464
2187.1917 | 429.519 | 650.0151 | 543.0772 | 679.1798 | 687.8823 | 723.636
2188.1917 | 429.5502 | 649.441 | 541.1187 | 677.7807 | 680.2788 | 715.8792
2189.1917 | 430.0531 | 648.6641 | 542.2219 | 680.4394 | 676.0402 | 718.7355
2190.1917 | 430.374 | 649.6179 | 542.6812 | 677.6587 | 670.7485 | 716.6741
2191.1917 | 429.6786 | 650.6593 | 543.8439 | 678.7659 | 684.7484 | 721.0846
2192.1917 | 428.9034 | 651.2098 | 543.4619 | 684.8953 | 689.6 | 713.7784
2193.1917 | 429.335 | 651.2505 | 543.0868 | 693.8538 | 684.4566 | 715.5914
2194.1917 | 429.6813 | 651.5772 | 544.413 | 701.4149 | 688.5979 | 712.9193
2195.1917 | 430.2361 | 650.7218 | 544.1901 | 701.8653 | 693.571 | 727.1549
2196.1917 | 429.9919 | 650.3098 | 545.2118 | 701.2553 | 697.6996 | 718.0812
2197.1917 | 429.7852 | 650.1125 | 544.9473 | 702.6893 | 693.5702 | 707.9275
2198.1917 | 429.1483 | 649.9154 | 544.6141 | 694.7013 | 684.284 | 699.9978
2199.1917 | 429.5252 | 649.913 | 546.8182 | 701.8401 | 682.59 | 693.0761
2200.1917 | 431.097 | 650.8157 | 545.5128 | 702.2394 | 679.3653 | 687.9385
2201.1917 | 431.216 | 651.0687 | 546.9377 | 701.1383 | 675.942 | 681.4852
2202.1917 | 432.8932 | 650.2996 | 545.4932 | 698.377 | 680.5896 | 680.7021
2203.1917 | 433.6795 | 650.5679 | 544.8766 | 690.8418 | 673.4288 | 676.275
2204.1917 | 433.1887 | 650.3839 | 545.9368 | 696.1065 | 669.2876 | 677.233
2205.1917 | 433.7398 | 650.8835 | 546.5399 | 689.1177 | 666.4824 | 676.2914
2206.1917 | 432.8742 | 650.383 | 545.9017 | 681.4423 | 670.5713 | 680.0405
2207.1917 | 432.7443 | 650.7654 | 546.6537 | 675.5127 | 667.661 | 676.9393
2208.1917 | 432.8246 | 650.8129 | 546.7863 | 669.2417 | 663.1104 | 672.6456
2209.1917 | 433.8251 | 650.2735 | 546.6941 | 665.0606 | 661.7822 | 675.4023
2210.1917 | 434.4795 | 650.1743 | 546.9341 | 661.4522 | 659.7952 | 669.8507
2211.1917 | 434.772 | 649.8069 | 546.0647 | 665.3743 | 659.393 | 669.5335
2212.1917 | 435.3441 | 650.4899 | 546.7683 | 676.5656 | 657.3351 | 669.5877
2213.1917 | 434.8177 | 650.2164 | 548.2801 | 685.7098 | 653.4694 | 664.6774
2214.1917 | 433.8331 | 650.233 | 547.6087 | 688.1139 | 659.1446 | 669.2692
2215.1917 | 433.7086 | 649.9727 | 547.3082 | 688.0286 | 656.9579 | 664.2822
2216.1917 | 433.1839 | 649.8935 | 548.3263 | 685.8426 | 659.4587 | 660.3321
2217.1917 | 433.4004 | 650.0406 | 548.2475 | 685.3386 | 663.1072 | 657.3868
2218.1917 | 433.4322 | 649.9076 | 547.6049 | 688.3985 | 661.5338 | 657.8023
2219.1917 | 435.2139 | 649.7487 | 547.3549 | 691.0643 | 657.5399 | 656.2135
2220.1917 | 436.5669 | 649.524 | 548.2261 | 696.0053 | 655.6765 | 653.4313
2221.1917 | 437.2853 | 649.6002 | 547.6505 | 694.5606 | 654.5966 | 650.4907
2222.1917 | 436.5437 | 649.6923 | 547.0784 | 691.3092 | 653.5145 | 652.7485
2223.1917 | 437.1491 | 649.7933 | 547.8493 | 698.3049 | 664.2388 | 651.4246
2224.1917 | 438.8392 | 649.4599 | 547.2284 | 707.0422 | 661.3256 | 649.9213
2225.1917 | 439.0972 | 649.8058 | 550.0541 | 713.233 | 660.7815 | 652.3519
2226.1917 | 438.9465 | 650.0968 | 549.0001 | 715.1206 | 660.6618 | 649.8897
2227.1917 | 438.3784 | 650.382 | 549.9288 | 716.5507 | 667.3803 | 649.6797
2228.1917 | 440.1157 | 651.0189 | 551.4582 | 710.8349 | 678.6056 | 650.5308
2229.1917 | 438.9477 | 650.664 | 551.4137 | 709.4659 | 683.475 | 653.6471
2230.1917 | 437.9005 | 650.6668 | 550.8799 | 707.3698 | 678.9562 | 653.4957
2231.1917 | 438.8697 | 650.8667 | 552.1127 | 704.0088 | 676.6089 | 662.734
2232.1917 | 438.7811 | 650.5077 | 552.0563 | 704.3404 | 675.7151 | 665.8376
2233.2073 | 439.5898 | 650.1514 | 551.5544 | 706.6835 | 672.5042 | 665.4156
2234.1917 | 440.9015 | 649.7255 | 552.5104 | 705.2707 | 671.687 | 663.223
2235.1917 | 440.151 | 649.4465 | 551.7838 | 695.9872 | 665.5205 | 659.715
2236.1917 | 440.1402 | 649.4815 | 552.5358 | 694.1026 | 662.7654 | 658.3526
2237.1917 | 440.3519 | 649.8572 | 552.4356 | 690.4561 | 661.4292 | 655.3377
2238.1917 | 440.5886 | 650.1338 | 553.2441 | 686.1164 | 659.4004 | 652.4915
2239.1917 | 440.5176 | 649.7118 | 552.9734 | 691.1909 | 657.4898 | 650.9395
2240.1917 | 441.0856 | 649.6733 | 553.9081 | 686.7465 | 654.1219 | 646.8073
2241.1917 | 443.1285 | 650.4166 | 553.8885 | 687.0269 | 653.8372 | 661.2236
2242.1917 | 442.4377 | 650.3019 | 553.5585 | 692.7535 | 654.7021 | 673.3257
2243.1917 | 443.5621 | 651.5062 | 554.5329 | 694.5515 | 656.9239 | 681.6112
2244.1917 | 444.0157 | 650.7733 | 555.564 | 691.1089 | 658.8453 | 694.8433
2245.1917 | 444.4059 | 650.8617 | 554.272 | 697.6079 | 658.8114 | 701.6074
2246.1917 | 444.035 | 650.5871 | 554.3753 | 702.9572 | 665.223 | 708.4308
2247.1917 | 444.3892 | 650.4758 | 554.5008 | 704.5764 | 664.0941 | 699.9583
2248.1917 | 446.134 | 650.2209 | 553.6829 | 701.0332 | 662.7097 | 693.6857
2249.1917 | 446.903 | 649.9445 | 553.2184 | 691.5801 | 659.4655 | 689.8204
2250.1917 | 446.5012 | 650.0219 | 554.6193 | 695.2945 | 658.3602 | 683.2406
2251.1917 | 446.8611 | 649.7201 | 554.6051 | 691.3618 | 655.2468 | 677.5274
2252.1917 | 447.4096 | 649.9331 | 556.4422 | 699.0303 | 661.3146 | 673.7887
2253.1917 | 447.3698 | 650.2248 | 556.3742 | 711.8344 | 659.0949 | 669.0175
2254.1917 | 447.2419 | 650.0239 | 556.6369 | 711.4609 | 657.0752 | 669.2646
2255.1917 | 447.9114 | 650.9448 | 556.6749 | 712.0266 | 660.2308 | 669.1887
2256.1917 | 449.4571 | 651.1507 | 555.323 | 706.136 | 658.9454 | 669.4675
2257.1917 | 449.6564 | 650.6964 | 555.281 | 702.9324 | 659.3949 | 682.9094
2258.1917 | 451.802 | 650.6234 | 555.5058 | 706.7083 | 657.3708 | 681.0273
2259.1917 | 452.9777 | 651.1821 | 557.4191 | 708.9005 | 662.0892 | 686.5086
2260.1917 | 451.5109 | 651.0525 | 555.848 | 705.8101 | 657.6973 | 697.6974
2261.1917 | 450.7377 | 651.0701 | 556.6884 | 706.3893 | 660.1203 | 704.893
2262.1917 | 452.9813 | 651.3133 | 556.748 | 706.1954 | 657.89 | 704.0331
2263.2073 | 451.9111 | 652.2896 | 556.7973 | 706.3962 | 656.0407 | 699.0717
2264.1917 | 450.5057 | 652.6047 | 557.2912 | 706.1434 | 658.5216 | 706.5029
2265.1917 | 450.5597 | 652.6295 | 558.7836 | 706.5773 | 657.7905 | 710.359
2266.1917 | 451.2539 | 652.5078 | 559.2019 | 705.0376 | 657.5527 | 712.8949
2267.1917 | 454.1197 | 652.1548 | 558.7877 | 703.4274 | 657.4472 | 706.872
2268.1917 | 454.5153 | 651.6925 | 557.5329 | 708.6379 | 663.7501 | 708.8102
2269.1917 | 454.1239 | 651.5464 | 557.3303 | 710.1474 | 662.9014 | 698.6878
2270.1917 | 455.3438 | 651.9083 | 557.5136 | 719.5764 | 660.9393 | 701.5974
2271.1917 | 455.9076 | 652.9947 | 559.1853 | 721.3503 | 660.7657 | 704.4725
2272.1917 | 455.6604 | 652.41 | 559.5413 | 724.0412 | 662.2977 | 706.9513
2273.1917 | 454.5536 | 652.1441 | 558.8635 | 722.0907 | 660.4879 | 708.5639
2274.1917 | 454.6116 | 653.0904 | 558.6018 | 715.4824 | 658.4401 | 700.4761
2275.1917 | 455.6572 | 652.8648 | 559.3908 | 714.5562 | 656 | 702.7302
2276.1917 | 454.9081 | 653.0195 | 560.8259 | 725.3317 | 655.8674 | 695.3641
2277.1917 | 454.6949 | 653.3934 | 561.4578 | 724.9158 | 654.7178 | 690.2282
2278.1917 | 455.114 | 653.8334 | 560.2406 | 725.0239 | 655.3059 | 693.2462
2279.1917 | 456.2709 | 653.6179 | 559.7686 | 728.3533 | 653.5269 | 690.9356
2280.1917 | 456.7503 | 653.2806 | 561.0512 | 730.0311 | 651.6308 | 685.528
2281.1917 | 456.7878 | 653.4194 | 561.2734 | 723.9392 | 651.9882 | 681.4559
2282.1917 | 456.7566 | 653.901 | 561.8246 | 714.2947 | 651.8681 | 681.9386
2283.1917 | 459.5288 | 653.6662 | 562.0633 | 712.9088 | 651.0457 | 681.869
2284.1917 | 460.4934 | 653.608 | 560.3805 | 712.1429 | 651.2909 | 680.4038
2285.1917 | 460.5939 | 653.8159 | 560.578 | 701.3958 | 651.4358 | 677.4956
2286.1917 | 461.6619 | 653.9992 | 561.7949 | 702.0072 | 651.8792 | 672.0969
2287.1917 | 462.1703 | 654.3688 | 561.0679 | 705.6255 | 653.0757 | 673.7105
2288.1917 | 463.1253 | 654.8934 | 560.1243 | 706.4375 | 652.5932 | 673.1359
2289.1917 | 463.3028 | 653.9047 | 560.3194 | 704.392 | 655.1039 | 679.6569
2290.1917 | 464.1735 | 653.2557 | 560.6967 | 695.3256 | 653.8004 | 677.2429
2291.1917 | 461.922 | 653.8016 | 561.4197 | 689.6125 | 653.9862 | 682.8111
2292.1917 | 461.256 | 654.1728 | 561.7055 | 683.4786 | 654.6134 | 679.9314
2293.1917 | 461.8634 | 654.1529 | 563.005 | 678.6364 | 656.0975 | 688.1323
2294.1917 | 461.2196 | 653.6221 | 562.0063 | 688.5006 | 653.8136 | 680.5906
2295.1917 | 461.0527 | 654.5041 | 564.0214 | 686.2137 | 652.4641 | 679.733
2296.1917 | 462.0453 | 654.9518 | 564.3147 | 688.0031 | 651.1988 | 685.3307
2297.1917 | 461.6833 | 655.8622 | 563.6931 | 690.3797 | 650.9409 | 688.8835
2298.1917 | 461.6298 | 656.2737 | 563.9735 | 690.8977 | 648.4095 | 694.7641
2299.1917 | 462.1923 | 655.9272 | 564.8135 | 697.7438 | 650.5364 | 693.0586
2300.1917 | 463.3562 | 656.7441 | 565.3326 | 693.7215 | 651.3501 | 702.4611
2301.1917 | 463.345 | 656.3786 | 565.8914 | 695.0918 | 650.537 | 703.3508
2302.1917 | 462.5994 | 655.6983 | 565.7949 | 693.2489 | 654.0682 | 695.59
2303.1917 | 463.7508 | 656.8112 | 565.6075 | 694.0278 | 654.6199 | 697.6888
2304.1917 | 463.7132 | 656.8172 | 566.8141 | 695.5292 | 654.9774 | 700.0885
2305.1917 | 463.0491 | 656.5868 | 566.4784 | 693.9763 | 656.0906 | 694.2828
2306.1917 | 463.4135 | 657.2778 | 566.5972 | 698.9599 | 655.2458 | 697.5503
2307.1917 | 463.3156 | 657.6957 | 566.2945 | 697.3979 | 655.8043 | 693.3594
2308.1917 | 464.7186 | 657.5643 | 567.0935 | 698.3166 | 655.8774 | 691.1969
2309.1917 | 466.1702 | 657.4601 | 566.3998 | 699.4183 | 656.4225 | 697.322
2310.1917 | 466.9047 | 657.7793 | 567.3832 | 699.4562 | 655.701 | 693.2179
2311.1917 | 466.0786 | 658.097 | 567.761 | 706.2565 | 656.9961 | 693.0968
2312.1917 | 465.2026 | 658.5714 | 568.0315 | 699.4 | 656.6922 | 685.1138
2313.2073 | 465.8623 | 657.9792 | 567.5876 | 703.7057 | 656.7996 | 681.8658
2314.1917 | 466.991 | 657.4117 | 567.7394 | 701.5699 | 656.8324 | 678.405
2315.1917 | 467.0327 | 657.1042 | 567.5113 | 698.6194 | 656.7205 | 674.4278
2316.1917 | 468.0458 | 657.2339 | 566.6189 | 689.4103 | 654.6032 | 668.6854
2317.1917 | 469.6463 | 656.8877 | 567.0989 | 693.0158 | 652.4969 | 666.0967
2318.1917 | 470.201 | 656.6101 | 566.4424 | 686.3003 | 652.1371 | 668.3354
2319.1917 | 469.7635 | 656.8173 | 567.0639 | 680.0211 | 649.8089 | 662.4806
2320.1917 | 468.6641 | 656.5189 | 566.801 | 676.2978 | 649.0978 | 663.8785
2321.1917 | 468.2319 | 657.858 | 567.7281 | 680.2471 | 652.0562 | 662.5352
2322.1917 | 468.8548 | 657.0581 | 566.3314 | 678.1541 | 653.0053 | 672.2493
2323.2073 | 469.0885 | 657.1946 | 567.0101 | 672.2818 | 651.5953 | 675.4807
2324.1917 | 470.1975 | 656.7098 | 567.8456 | 690.5736 | 649.0581 | 669.3214
2325.1917 | 469.5543 | 656.7603 | 567.7264 | 685.7186 | 646.9385 | 664.5211
2326.1917 | 469.0545 | 656.4328 | 567.362 | 683.2609 | 644.9768 | 666.4273
2327.1917 | 468.3433 | 656.5308 | 568.3637 | 678.491 | 645.025 | 662.8324
2328.1917 | 468.0344 | 656.6877 | 568.8413 | 673.855 | 643.999 | 659.179
2329.1917 | 468.4645 | 656.6488 | 568.1213 | 683.2661 | 642.5022 | 663.0899
2330.1917 | 469.5233 | 656.2894 | 567.3674 | 676.3503 | 640.9016 | 659.9369
2331.1917 | 471.6938 | 656.4822 | 567.1705 | 674.8026 | 639.9266 | 656.8009
2332.1917 | 471.4209 | 656.3158 | 567.9532 | 673.1119 | 639.4993 | 657.893
2333.1917 | 471.7593 | 656.4336 | 567.2245 | 670.2868 | 638.0706 | 655.6129
2334.1917 | 472.568 | 656.6064 | 569.7721 | 677.7008 | 637.1971 | 667.4924
2335.1917 | 472.1038 | 656.1561 | 568.6579 | 689.1777 | 637.6635 | 674.6234
2336.1917 | 472.6536 | 655.8809 | 567.8844 | 690.6498 | 641.182 | 673.8252
2337.1917 | 473.4481 | 656.0166 | 568.5993 | 683.4445 | 638.75 | 669.9526
2338.1917 | 472.949 | 656.6494 | 568.6119 | 689.7619 | 637.6418 | 666.0593
2339.1917 | 472.8255 | 657.0991 | 569.2293 | 711.7184 | 637.8759 | 662.3064
2340.1917 | 474.2675 | 656.6433 | 568.7261 | 713.3873 | 637.5124 | 673.1063
2341.1917 | 474.1546 | 656.0732 | 569.0357 | 714.581 | 638.0492 | 677.5809
2342.1917 | 474.0228 | 655.6501 | 568.2887 | 701.9539 | 638.5162 | 686.8828
2343.1917 | 473.6311 | 655.8142 | 567.8911 | 692.8527 | 637.9002 | 677.4525
2344.1917 | 473.2185 | 656.1769 | 569.6864 | 695.935 | 637.8456 | 673.1853
2345.1917 | 472.5332 | 655.4612 | 569.7177 | 700.3853 | 636.8954 | 665.6775
2346.1917 | 473.4058 | 654.9931 | 569.3668 | 689.4223 | 637.016 | 662.5301
2347.1917 | 473.9868 | 654.9939 | 568.3566 | 686.0131 | 639.8278 | 678.0216
2348.1917 | 476.0862 | 654.5667 | 568.2735 | 687.2008 | 643.0455 | 686.0014
2349.1917 | 477.0334 | 654.39 | 568.8121 | 683.5618 | 643.7733 | 698.706
2350.1917 | 475.9398 | 654.4384 | 568.5163 | 686.143 | 644.7285 | 699.4975
2351.1917 | 475.5381 | 654.1356 | 567.7915 | 683.3885 | 644.6687 | 691.6311
2352.1917 | 476.4441 | 653.9249 | 567.4866 | 678.4875 | 645.1704 | 695.9955
2353.1917 | 476.766 | 654.1031 | 568.044 | 678.0114 | 645.8613 | 697.2024
2354.1917 | 476.8147 | 654.582 | 570.0041 | 676.0923 | 643.3131 | 686.4992
2355.1917 | 478.2921 | 654.659 | 570.1453 | 683.7218 | 641.9456 | 691.3865
2356.1917 | 477.0475 | 655.1254 | 570.7219 | 690.8623 | 639.8284 | 686.9153
2357.1917 | 475.994 | 654.7211 | 570.7943 | 695.7091 | 638.1575 | 694.7199
2358.1917 | 476.0192 | 655.2821 | 571.2902 | 705.2191 | 639.1501 | 700.6193
2359.1917 | 476.2311 | 654.92 | 570.4157 | 696.6663 | 640.5324 | 691.4221
2360.1917 | 477.5456 | 654.3475 | 571.2734 | 696.1019 | 640.1421 | 693.295
2361.1917 | 477.3188 | 655.2625 | 571.8245 | 694.6649 | 638.9377 | 701.1712
2362.1917 | 476.9683 | 655.2591 | 571.2556 | 695.8207 | 637.4331 | 705.2014
2363.1917 | 478.2058 | 655.532 | 572.3779 | 712.3866 | 636.7245 | 715.0358
2364.1917 | 477.5308 | 655.0643 | 573.368 | 712.4042 | 634.7497 | 719.7608
2365.1917 | 476.3209 | 656.2387 | 573.8332 | 720.5961 | 633.7806 | 725.4379
2366.1917 | 477.2268 | 656.0393 | 572.9323 | 716.268 | 633.1228 | 728.8011
2367.1917 | 479.0204 | 655.7639 | 572.8724 | 721.733 | 632.6786 | 729.3624
2368.1917 | 479.491 | 655.6123 | 574.1935 | 720.5335 | 632.3215 | 732.2071
2369.1917 | 479.5955 | 656.4107 | 575.0955 | 729.0421 | 630.2939 | 733.401
2370.1917 | 479.1523 | 655.9788 | 573.4041 | 731.2771 | 631.8497 | 731.3072
2371.1917 | 480.183 | 655.8173 | 573.3154 | 723.0896 | 631.9922 | 718.5329
2372.1917 | 478.8294 | 655.3923 | 573.0511 | 713.4864 | 633.2513 | 708.0866
2373.1917 | 477.8644 | 655.5362 | 573.4286 | 702.8635 | 633.6724 | 712.205
2374.1917 | 479.6157 | 655.9571 | 572.4496 | 693.5494 | 635.8632 | 712.0429
2375.1917 | 480.6013 | 655.9072 | 572.243 | 684.8227 | 634.976 | 704.3336
2376.1917 | 480.8121 | 655.4362 | 571.7125 | 676.3664 | 635.1145 | 710.434
2377.1917 | 480.4085 | 655.6384 | 571.4446 | 670.9393 | 634.4086 | 700.8515
2378.1917 | 480.5929 | 655.5744 | 572.5415 | 665.6422 | 634.1191 | 691.4679
2379.1917 | 480.8059 | 656.0269 | 573.8823 | 671.8783 | 632.7488 | 693.3482
2380.1917 | 480.0158 | 655.7726 | 575.4952 | 685.4626 | 630.6609 | 701.1643
2381.1917 | 480.3692 | 656.0634 | 575.0509 | 691.7709 | 627.2111 | 704.0646
2382.1917 | 480.3882 | 656.6247 | 575.5042 | 699.3965 | 626.7868 | 715.0587
2383.1917 | 480.3301 | 656.7316 | 575.8825 | 703.6642 | 625.9043 | 722.6068
2384.1917 | 481.15 | 657.5376 | 575.3801 | 708.6205 | 624.2493 | 721.8034
2385.1917 | 481.4426 | 657.5446 | 576.5482 | 716.2791 | 623.3044 | 717.0314
2386.1917 | 482.3559 | 657.5257 | 577.742 | 713.107 | 623.535 | 717.753
2387.1917 | 482.3149 | 656.6474 | 577.0712 | 710.9572 | 621.6148 | 722.0334
2388.1917 | 481.4466 | 656.619 | 576.8723 | 705.6666 | 621.8588 | 724.1515
2389.1917 | 480.4668 | 656.0239 | 577.5403 | 700.7157 | 620.942 | 727.156
2390.1917 | 480.2522 | 656.2599 | 578.4981 | 696.5446 | 619.7395 | 729.7516
2391.1917 | 480.8084 | 656.1527 | 578.2915 | 697.1292 | 617.8359 | 728.6786
2392.1917 | 481.7448 | 656.1746 | 579.1456 | 709.0143 | 616.314 | 719.5285
2393.1917 | 482.0045 | 655.9875 | 579.7702 | 702.5831 | 615.3553 | 720.7401
2394.1917 | 481.5106 | 656.4865 | 579.7962 | 697.4849 | 616.4572 | 706.2554
2395.1917 | 482.5392 | 656.6613 | 578.9173 | 692.4466 | 616.0701 | 706.5883
2396.1917 | 482.6997 | 655.5596 | 578.5987 | 687.8807 | 616.4016 | 694.4922
2397.1917 | 482.5613 | 655.9033 | 579.0623 | 683.692 | 616.6575 | 691.5873
2398.1917 | 482.9191 | 655.5051 | 579.5864 | 688.5255 | 617.4012 | 685.0333
2399.1917 | 483.4252 | 655.283 | 579.5462 | 684.6789 | 615.9981 | 682.5476
2400.1917 | 482.7527 | 655.0591 | 580.257 | 679.5086 | 614.5355 | 682.5965
2401.1917 | 481.4462 | 654.811 | 580.863 | 680.072 | 612.3498 | 685.0028
2402.1917 | 481.2342 | 654.8343 | 580.8812 | 676.3 | 610.9495 | 690.2226
2403.1917 | 481.5961 | 655.1768 | 581.9571 | 688.0136 | 610.7091 | 690.3386
2404.1917 | 481.9088 | 655.2765 | 582.4313 | 692.6664 | 611.9939 | 696.2445
2405.1917 | 482.654 | 654.9966 | 582.6543 | 685.9419 | 612.8961 | 693.1102
2406.1917 | 483.7608 | 655.1602 | 581.8107 | 690.9352 | 612.5731 | 695.3043
2407.1917 | 483.8455 | 655.4925 | 583.3747 | 700.9018 | 612.9755 | 697.6807
2408.1917 | 484.3418 | 655.881 | 583.922 | 707.372 | 613.9377 | 703.4817
2409.1917 | 484.4288 | 655.4846 | 583.8355 | 709.6538 | 611.8772 | 707.9718
2410.1917 | 484.6223 | 655.3197 | 584.8189 | 711.885 | 610.0773 | 716.0455
2411.1917 | 485.853 | 655.597 | 583.521 | 712.8388 | 610.799 | 718.102
2412.1917 | 487.2361 | 656.1168 | 585.4982 | 703.7246 | 611.6736 | 720.276
2413.1917 | 487.4464 | 655.877 | 584.8912 | 705.6785 | 611.1661 | 719.1734
2414.1917 | 486.1781 | 655.3633 | 585.7669 | 703.8665 | 611.1811 | 713.7328
2415.1917 | 484.8697 | 655.1146 | 584.965 | 704.9348 | 610.7476 | 712.051
2416.1917 | 483.8715 | 655.064 | 584.8993 | 696.7062 | 610.5259 | 714.9012
2417.1917 | 484.5804 | 655.9799 | 585.8744 | 690.8864 | 611.3838 | 707.2589
2418.1917 | 485.5267 | 655.5905 | 586.3142 | 686.2466 | 612.2912 | 707.7553
2419.1917 | 486.0641 | 655.0604 | 586.4056 | 689.6283 | 612.1832 | 694.7801
2420.1917 | 485.7137 | 654.4837 | 586.3927 | 683.1086 | 611.0982 | 695.3975
2421.1917 | 485.1628 | 655.3248 | 587.2281 | 678.6207 | 610.6824 | 703.044
2422.1917 | 485.2147 | 655.0129 | 586.7532 | 689.7616 | 610.2521 | 706.6571
2423.1917 | 486.804 | 655.4383 | 587.6285 | 683.3566 | 609.5123 | 708.2479
2424.1917 | 487.0779 | 655.527 | 587.6372 | 680.3501 | 611.0326 | 704.1529
2425.1917 | 488.2691 | 655.2349 | 587.4164 | 681.7933 | 610.1978 | 706.8272
2426.1917 | 487.6699 | 655.5644 | 587.7473 | 678.0011 | 608.7052 | 710.77
2427.1917 | 486.7283 | 655.1619 | 588.0756 | 688.3152 | 608.4764 | 714.62
2428.1917 | 489.2307 | 654.5381 | 588.9692 | 690.8625 | 608.5322 | 716.7202
2429.1917 | 488.3958 | 654.0011 | 588.5862 | 692.3925 | 607.628 | 717.7711
2430.1917 | 487.9765 | 654.234 | 588.76 | 684.9531 | 606.336 | 714.3994
2431.1917 | 487.7135 | 654.7367 | 589.5537 | 677.6129 | 605.1188 | 709.2168
2432.1917 | 487.2946 | 654.4899 | 591.6298 | 682.63 | 603.8793 | 703.0277
2433.1917 | 487.419 | 655.0941 | 591.2085 | 695.6933 | 603.0486 | 707.5846
2434.1917 | 488.4129 | 654.9297 | 590.3364 | 695.7943 | 603.0069 | 712.4418
2435.1917 | 488.9382 | 655.465 | 591.0353 | 702.4892 | 604.357 | 712.6585
2436.1917 | 489.9907 | 655.7718 | 590.4876 | 702.0548 | 604.1407 | 714.1677
2437.1917 | 490.5293 | 655.3775 | 591.1533 | 705.3482 | 603.2604 | 717.9418
2438.1917 | 490.1482 | 655.4891 | 592.0334 | 700.0458 | 602.4693 | 720.2144
2439.1917 | 490.1779 | 655.1134 | 590.8924 | 698.7053 | 601.6778 | 723.3779
2440.1917 | 489.8621 | 654.9613 | 591.7204 | 690.7916 | 601.1342 | 722.3851
2441.1917 | 490.5253 | 655.4478 | 591.0229 | 686.9094 | 602.4939 | 714.4413
2442.1917 | 489.7782 | 655.7218 | 591.0091 | 680.1175 | 605.2101 | 713.0574
2443.1917 | 489.4351 | 655.4744 | 592.6124 | 675.3908 | 605.7384 | 711.7648
2444.1917 | 488.9872 | 655.487 | 592.674 | 675.5286 | 605.1683 | 716.5001
2445.1917 | 489.8341 | 654.8838 | 593.0628 | 677.4523 | 604.1864 | 723.04
2446.1917 | 490.2039 | 654.3707 | 592.9006 | 673.7075 | 603.9049 | 717.1996
2447.1917 | 489.8329 | 654.7832 | 594.2771 | 669.5324 | 602.781 | 716.2492
2448.1917 | 490.296 | 655.1789 | 593.2977 | 665.5976 | 601.752 | 712.1398
2449.1917 | 490.9025 | 655.1506 | 594.1078 | 665.4839 | 601.9906 | 712.6069
2450.1917 | 491.7288 | 656.3876 | 594.6732 | 676.6533 | 602.1856 | 712.3154
2451.1917 | 491.566 | 656.4345 | 594.0969 | 677.3792 | 602.56 | 718.7158
2452.1917 | 492.461 | 656.4185 | 593.28 | 677.4055 | 603.091 | 723.5168
2453.1917 | 492.2599 | 656.2067 | 594.1766 | 675.5545 | 605.6024 | 717.9682
2454.1917 | 491.1585 | 655.7255 | 595.4722 | 674.3715 | 605.1642 | 718.2926
2455.1917 | 491.3231 | 655.9052 | 595.3946 | 681.8593 | 603.658 | 718.5764
2456.1917 | 491.3135 | 656.4436 | 594.1648 | 686.9117 | 604.6186 | 717.7179
2457.1917 | 492.3352 | 656.1731 | 594.8082 | 678.9458 | 606.3456 | 712.3645
2458.1917 | 492.5382 | 655.8027 | 596.1347 | 675.1818 | 605.3912 | 709.2562
2459.1917 | 492.7022 | 656.1456 | 595.6536 | 678.9416 | 606.9599 | 709.5652
2460.1917 | 491.8929 | 656.2191 | 593.6061 | 679.4094 | 607.3245 | 698.3668
2461.1917 | 492.7382 | 656.3644 | 594.0702 | 672.1963 | 609.0384 | 695.4931
2462.1917 | 493.3204 | 656.1132 | 594.1221 | 667.8789 | 608.6319 | 687.9929
2463.1917 | 493.5839 | 656.4405 | 594.0761 | 663.5654 | 608.9532 | 687.7667
2464.1917 | 493.8788 | 656.1856 | 595.8422 | 660.6462 | 608.8725 | 689.644
2465.1917 | 493.1978 | 656.1989 | 594.189 | 664.3769 | 607.7789 | 688.1221
2466.1917 | 493.6873 | 657.0178 | 595.3049 | 657.4931 | 606.7724 | 687.8629
2467.1917 | 492.4913 | 656.8038 | 594.8779 | 653.7728 | 606.8803 | 679.8125
2468.1917 | 492.6219 | 656.5374 | 594.9582 | 654.8352 | 606.6064 | 676.6365
2469.1917 | 492.8947 | 656.5369 | 595.409 | 652.8258 | 608.9144 | 678.1836
2470.1917 | 492.2818 | 656.4757 | 595.8877 | 651.8464 | 607.9563 | 678.2475
2471.1917 | 492.9909 | 656.6443 | 595.145 | 648.5666 | 607.9288 | 674.4483
2472.1917 | 494.0788 | 656.6486 | 595.3477 | 649.3717 | 607.502 | 675.9681
2473.1917 | 494.5822 | 656.9049 | 595.1664 | 650.0516 | 609.2085 | 674.4898
2474.1917 | 495.2992 | 656.8596 | 595.2365 | 647.2566 | 608.5922 | 672.9055
2475.1917 | 495.6228 | 657.1553 | 595.9015 | 644.5942 | 608.6729 | 671.3109
2476.1917 | 494.2934 | 656.9792 | 595.7469 | 643.9852 | 607.6541 | 677.0735
2477.1917 | 493.7476 | 656.7352 | 596.8769 | 646.962 | 605.1723 | 687.0891
2478.1917 | 493.7005 | 656.3543 | 597.1536 | 646.9252 | 603.4915 | 698.5744
2479.1917 | 494.0685 | 656.3578 | 597.0348 | 651.2031 | 602.3355 | 697.5857
2480.1917 | 494.8921 | 657.3586 | 596.6803 | 652.8186 | 602.5213 | 704.2108
2481.1917 | 496.0212 | 657.6227 | 595.4905 | 655.5987 | 601.9141 | 702.7954
2482.1917 | 497.2456 | 657.3209 | 596.4655 | 651.2122 | 601.631 | 707.143
2483.1917 | 496.1891 | 657.5555 | 596.934 | 652.6097 | 601.7936 | 705.6263
2484.1917 | 495.8526 | 657.417 | 595.9489 | 650.644 | 603.728 | 699.0781
2485.1917 | 495.9538 | 657.3959 | 597.0799 | 647.8461 | 604.7091 | 692.0826
2486.1917 | 496.9492 | 657.5908 | 596.713 | 647.543 | 607.1879 | 689.0701
2487.1917 | 497.204 | 657.4542 | 598.0413 | 645.3203 | 608.1892 | 692.0477
2488.1917 | 497.1335 | 657.1856 | 597.4459 | 646.7233 | 607.249 | 683.4863
2489.1917 | 497.0032 | 656.6437 | 597.648 | 642.9161 | 605.6195 | 680.0968
2490.1917 | 496.0576 | 656.5473 | 598.0038 | 640.7787 | 604.749 | 674.8758
2491.1917 | 496.3759 | 657.0659 | 599.0704 | 641.745 | 604.0543 | 674.3343
2492.1917 | 496.007 | 656.7397 | 599.0924 | 641.736 | 602.0554 | 679.7797
2493.1917 | 495.8169 | 656.1112 | 599.1186 | 643.1775 | 600.6851 | 677.732
2494.1917 | 496.1233 | 656.0722 | 598.4626 | 646.014 | 599.7829 | 675.8679
2495.1917 | 495.8764 | 656.3919 | 599.0335 | 642.7731 | 599.4397 | 675.096
2496.1917 | 496.392 | 656.2733 | 598.5571 | 640.541 | 599.2823 | 673.0769
2497.1917 | 496.5609 | 655.8389 | 597.8961 | 639.2326 | 599.0054 | 674.2181
2498.1917 | 498.0318 | 655.9471 | 599.4563 | 636.8361 | 598.9633 | 667.9773
2499.1917 | 496.8446 | 655.8503 | 599.6609 | 638.2689 | 598.0984 | 672.1817
2500.1917 | 496.9711 | 655.6489 | 599.7339 | 637.1923 | 596.5658 | 668.2801
2501.1917 | 498.1603 | 655.8175 | 599.6723 | 635.0471 | 595.7258 | 661.4407
2502.1917 | 498.5303 | 655.8989 | 600.1708 | 634.6038 | 597.1708 | 667.4136
2503.1917 | 498.252 | 655.6091 | 599.9801 | 639.0374 | 595.6574 | 677.9501
2504.1917 | 497.7138 | 655.7521 | 599.7417 | 640.1806 | 594.8197 | 686.7183
2505.1917 | 497.6255 | 655.4321 | 599.5796 | 637.1848 | 594.4345 | 683.004
2506.1917 | 498.8836 | 655.8427 | 598.7739 | 635.5223 | 596.4155 | 672.1822
2507.1917 | 500.0034 | 655.524 | 598.9128 | 633.7361 | 598.7739 | 667.2306
2508.1917 | 499.4063 | 654.7768 | 601.0609 | 634.1324 | 597.8105 | 663.4791
2509.1917 | 498.7624 | 653.9532 | 599.6696 | 636.3394 | 597.3964 | 662.7759
2510.1917 | 498.6595 | 654.6308 | 600.1436 | 635.2249 | 597.3618 | 663.0235
2511.1917 | 498.664 | 654.7175 | 600.3203 | 633.5901 | 598.1764 | 660.4579
2512.1917 | 498.8316 | 654.4447 | 599.8847 | 632.1729 | 598.7228 | 656.1541
2513.1917 | 499.9451 | 654.9088 | 600.1483 | 631.5769 | 597.6112 | 668.1249
2514.1917 | 500.1022 | 654.971 | 600.8771 | 630.1464 | 596.7652 | 670.2061
2515.1917 | 499.7724 | 654.9539 | 600.4759 | 628.3205 | 597.3197 | 666.889
2516.1917 | 499.8513 | 654.6807 | 601.4549 | 627.3413 | 597.2087 | 667.7576
2517.1917 | 499.5379 | 654.4844 | 601.5142 | 630.3412 | 595.9143 | 672.6951
2518.1917 | 499.9921 | 654.0207 | 603.1835 | 629.7993 | 593.6537 | 680.2332
2519.1917 | 500.8334 | 653.9959 | 601.0616 | 626.8922 | 593.4048 | 678.8016
2520.1917 | 501.6467 | 653.9631 | 601.0855 | 626.5851 | 594.6433 | 670.5817
2521.1917 | 501.3411 | 653.6396 | 601.9269 | 628.2984 | 595.1827 | 662.8483
2522.1917 | 500.5789 | 653.2647 | 602.6997 | 627.4848 | 595.1573 | 662.4054
2523.1917 | 500.3993 | 652.7966 | 601.4903 | 625.7378 | 592.4872 | 671.8107
2524.1917 | 500.7649 | 652.6202 | 601.6134 | 622.7384 | 590.4817 | 672.0243
2525.1917 | 501.4399 | 652.4737 | 602.1207 | 620.7292 | 589.7775 | 665.8392
2526.1917 | 501.6864 | 652.2955 | 602.1478 | 618.0092 | 588.7968 | 667.628
2527.1917 | 501.5637 | 652.0675 | 602.1897 | 618.2356 | 588.0211 | 673.0578
2528.1917 | 502.1614 | 651.6707 | 602.2339 | 616.0793 | 586.9611 | 673.631
2529.1917 | 501.4817 | 651.5741 | 603.2371 | 617.7718 | 586.4298 | 674.1526
2530.1917 | 502.4128 | 651.1787 | 602.9706 | 618.6838 | 587.2948 | 672.868
2531.1917 | 502.4692 | 651.2023 | 601.6297 | 618.7531 | 588.3834 | 667.3579
2532.1917 | 502.0273 | 651.0824 | 601.5002 | 618.2479 | 587.8494 | 664.556
2533.1917 | 501.3835 | 651.087 | 602.56 | 617.0628 | 586.8108 | 663.7237
2534.1917 | 501.4687 | 651.3217 | 603.1356 | 615.0175 | 586.8104 | 659.9015
2535.1917 | 502.3158 | 651.0428 | 601.7935 | 614.6474 | 586.867 | 662.9607
2536.1917 | 502.5058 | 650.5616 | 602.469 | 613.199 | 586.2796 | 660.9893
2537.1917 | 502.277 | 650.742 | 602.3798 | 613.5998 | 586.9148 | 659.4274
2538.1917 | 502.709 | 650.4175 | 602.9172 | 614.7694 | 587.3254 | 660.68
2539.1917 | 503.7753 | 650.1288 | 603.0612 | 614.0605 | 586.8486 | 662.3302
2540.2073 | 503.2521 | 650.0124 | 602.8277 | 612.6864 | 584.07 | 666.6624
2541.1917 | 503.6234 | 650.1953 | 602.2025 | 611.2506 | 584.3961 | 667.3978
2542.1917 | 503.0692 | 650.2114 | 601.748 | 609.7026 | 584.596 | 667.7172
2543.1917 | 503.8039 | 649.9876 | 602.0505 | 609.2256 | 585.3471 | 661.7342
2544.2073 | 503.3748 | 649.6319 | 602.5673 | 608.9318 | 585.8102 | 663.6177
2545.1917 | 503.5567 | 649.3593 | 602.9909 | 610.1009 | 586.0909 | 665.8658
2546.1917 | 503.5495 | 649.0292 | 602.905 | 615.9376 | 584.6475 | 673.5044
2547.1917 | 503.6966 | 648.4858 | 602.4768 | 614.7779 | 584.2797 | 673.1766
2548.1917 | 504.3194 | 648.1581 | 602.8123 | 614.7205 | 583.8895 | 684.3046
2549.1917 | 504.7387 | 648.416 | 603.0239 | 614.0225 | 583.6229 | 684.7944
2550.1917 | 504.4375 | 647.9926 | 602.8652 | 611.8924 | 582.7976 | 684.6644
2551.1917 | 503.9435 | 647.503 | 603.0403 | 610.4489 | 581.2625 | 677.7126
2552.1917 | 504.0647 | 647.5253 | 602.2469 | 610.966 | 581.7695 | 679.2798
2553.1917 | 506.5015 | 647.8783 | 603.4695 | 609.1694 | 582.1434 | 679.4848
2554.1917 | 505.8407 | 647.9186 | 603.0226 | 608.389 | 583.3236 | 672.8159
2555.1917 | 505.277 | 647.6359 | 602.8591 | 608.0076 | 584.1436 | 672.9194
2556.1917 | 504.7286 | 647.3635 | 603.2727 | 606.9185 | 584.0544 | 665.6361
2557.1917 | 504.7381 | 647.1819 | 603.4501 | 606.6386 | 584.478 | 663.5845
2558.1917 | 504.9111 | 647.0102 | 603.1207 | 606.1061 | 583.5201 | 666.0335
2559.1917 | 505.3309 | 646.2585 | 602.7324 | 606.5133 | 584.0173 | 666.1653
2560.1917 | 505.6076 | 646.5775 | 603.7648 | 606.3644 | 584.8823 | 660.6244
2561.1917 | 506.1206 | 646.6932 | 603.3872 | 604.3771 | 584.7694 | 663.7219
2562.1917 | 506.3909 | 646.114 | 603.8539 | 604.2236 | 583.1526 | 660.5935
2563.1917 | 506.2776 | 645.9621 | 602.9844 | 604.3466 | 583.1378 | 664.9828
2564.1917 | 506.0382 | 645.7209 | 602.7907 | 602.6356 | 583.3291 | 665.7089
2565.1917 | 506.5654 | 645.7965 | 602.5727 | 600.7352 | 585.1111 | 656.3249
2566.1917 | 506.8205 | 645.9411 | 603.3219 | 599.92 | 586.6321 | 650.7187
2567.1917 | 506.7677 | 646.1593 | 603.0898 | 598.0494 | 586.6766 | 645.1589
2568.1917 | 507.2902 | 646.2418 | 603.184 | 596.8853 | 585.8753 | 652.9887
2569.1917 | 507.4553 | 646.7229 | 603.8098 | 595.9834 | 585.8457 | 656.0092
2570.1917 | 507.2495 | 646.4519 | 603.5146 | 594.1253 | 584.0658 | 658.0103
2571.1917 | 507.5771 | 646.2394 | 603.2128 | 592.1643 | 583.2124 | 660.9192
2572.1917 | 508.5594 | 646.5409 | 604.0327 | 590.2994 | 583.9271 | 652.0165
2573.1917 | 508.7668 | 646.4376 | 603.9382 | 589.3583 | 584.4603 | 656.5794
2574.1917 | 508.9541 | 645.9999 | 603.8709 | 588.1718 | 582.9355 | 663.8707
2575.1917 | 509.4316 | 645.7795 | 603.4484 | 586.9232 | 582.277 | 669.1959
2576.1917 | 508.7123 | 646.0761 | 603.1587 | 585.9674 | 582.9025 | 662.5634
2577.1917 | 509.1339 | 646.0229 | 602.7152 | 585.3669 | 582.9615 | 653.1396
2578.1917 | 510.6512 | 645.7832 | 603.5476 | 584.5547 | 582.467 | 646.7719
2579.1917 | 510.0077 | 645.177 | 603.2844 | 583.8747 | 582.1377 | 639.1041
2580.1917 | 510.2224 | 645.0592 | 602.8368 | 584.6755 | 583.5432 | 632.1192
2581.1917 | 509.8992 | 644.6859 | 602.0097 | 585.1783 | 584.8946 | 624.9113
2582.1917 | 509.9573 | 645.2161 | 602.7556 | 585.3906 | 587.0476 | 620.9913
2583.1917 | 509.5878 | 645.493 | 603.0902 | 586.9038 | 588.8959 | 617.5286
2584.1917 | 509.4652 | 644.831 | 604.3055 | 586.5515 | 588.696 | 623.8939
2585.1917 | 509.0551 | 644.5261 | 604.4062 | 587.0852 | 589.6801 | 620.5576
2586.1917 | 508.8397 | 644.2447 | 603.7828 | 586.7087 | 588.8037 | 620.9562
2587.1917 | 508.8957 | 644.1787 | 603.3689 | 585.6233 | 587.0616 | 621.6567
2588.1917 | 508.8632 | 643.8395 | 602.9729 | 584.6254 | 587.1253 | 622.1704
2589.1917 | 508.72 | 643.9208 | 603.2755 | 584.5382 | 587.7311 | 621.3525
2590.1917 | 508.9074 | 644.3576 | 603.8702 | 583.8133 | 588.7927 | 618.7647
2591.1917 | 509.0792 | 644.1878 | 603.91 | 583.4913 | 589.7766 | 623.2119
2592.1917 | 510.5929 | 643.6143 | 603.995 | 581.9447 | 588.3561 | 622.6105
2593.1917 | 510.0063 | 643.3083 | 603.758 | 581.1414 | 587.7373 | 622.7667
2594.1917 | 510.3718 | 642.518 | 603.248 | 580.0974 | 585.1231 | 623.0219
2595.1917 | 510.2824 | 642.3385 | 602.4762 | 578.8764 | 583.3836 | 629.0304
2596.1917 | 510.4033 | 642.9498 | 602.606 | 579.1039 | 583.4966 | 624.461
2597.1917 | 510.4676 | 643.1704 | 603.93 | 578.2358 | 582.3635 | 620.8845
2598.1917 | 509.8286 | 642.5756 | 603.9437 | 577.153 | 580.6017 | 616.6749
2599.1917 | 509.3325 | 641.9609 | 603.7264 | 576.1961 | 578.6907 | 616.941
2600.1917 | 509.6084 | 641.6013 | 603.4453 | 575.8386 | 577.1085 | 624.6903
2601.1917 | 509.6797 | 641.9439 | 603.5966 | 575.2688 | 574.8596 | 634.8558
2602.1917 | 510.3886 | 642.0617 | 604.2131 | 574.7791 | 572.8733 | 644.1819
2603.1917 | 510.8046 | 641.3043 | 603.773 | 573.3557 | 570.8733 | 638.4391
2604.1917 | 510.6852 | 641.213 | 603.4663 | 572.5036 | 571.7009 | 638.8636
2605.1917 | 511.7614 | 641.2547 | 604.3881 | 572.1442 | 571.2087 | 639.4717
2606.1917 | 511.5347 | 641.0083 | 603.3627 | 572.1994 | 571.4235 | 651.1581
2607.1917 | 511.4008 | 641.2298 | 603.0622 | 571.8857 | 571.9597 | 648.3894
2608.1917 | 511.1795 | 641.4655 | 603.0205 | 572.8317 | 573.1409 | 642.1506
2609.1917 | 510.4052 | 641.387 | 603.331 | 572.5111 | 573.9483 | 641.9065
2610.1917 | 509.8142 | 641.1592 | 602.8935 | 571.7682 | 575.0087 | 636.9566
2611.1917 | 510.1387 | 641.0036 | 603.0468 | 571.5843 | 575.5699 | 640.9936
2612.1917 | 510.7074 | 640.8156 | 603.2417 | 571.8123 | 576.2124 | 643.0061
2613.1917 | 511.1004 | 640.5226 | 603.2011 | 571.2683 | 575.1947 | 639.4963
2614.1917 | 511.3606 | 639.9076 | 604.1028 | 572.3948 | 574.5564 | 639.638
2615.1917 | 511.8359 | 640.2376 | 604.7288 | 573.072 | 573.6138 | 637.235
2616.1917 | 511.7286 | 639.8676 | 604.4622 | 573.1352 | 572.8205 | 641.1517
2617.1917 | 510.9037 | 639.2768 | 603.9599 | 571.422 | 570.3465 | 638.1963
2618.1917 | 511.0743 | 639.4935 | 603.7518 | 571.7168 | 569.381 | 637.5732
2619.1917 | 511.0722 | 639.6804 | 604.1059 | 571.6658 | 569.0595 | 642.5923
2620.1917 | 511.2486 | 639.7063 | 603.5801 | 570.9891 | 567.568 | 640.2046
2621.1917 | 512.0966 | 639.3259 | 604.5699 | 570.1786 | 567.1594 | 641.1724
2622.1917 | 511.7879 | 639.729 | 603.4396 | 569.7705 | 568.039 | 638.8607
2623.1917 | 512.5024 | 640.5341 | 602.9711 | 569.3526 | 568.9466 | 634.9852
2624.1917 | 513.956 | 640.3585 | 604.1953 | 569.3767 | 571.2893 | 628.4252
2625.1917 | 513.4501 | 639.1125 | 604.8243 | 568.6124 | 570.7815 | 629.1188
2626.1917 | 513.1048 | 638.854 | 604.7786 | 569.0899 | 570.7343 | 624.1741
2627.1917 | 513.1956 | 638.8992 | 604.1145 | 568.9006 | 571.6433 | 619.3632
2628.1917 | 513.0486 | 638.6774 | 603.3478 | 569.6459 | 572.5509 | 617.976
2629.1917 | 513.5193 | 638.9398 | 603.1515 | 570.6311 | 573.6295 | 621.7873
2630.1917 | 514.0045 | 639.0119 | 603.7865 | 570.1341 | 574.0218 | 619.0197
2631.1917 | 514.63 | 638.2447 | 603.627 | 570.0715 | 572.7999 | 615.8069
2632.1917 | 514.0002 | 638.2669 | 603.8168 | 569.7511 | 571.6274 | 614.4244
2633.1917 | 513.664 | 638.4912 | 604.7357 | 568.806 | 571.4928 | 615.4261
2634.1917 | 513.3863 | 638.8036 | 603.6854 | 569.5975 | 572.8821 | 613.9289
2635.1917 | 513.3596 | 638.7654 | 603.9079 | 569.3492 | 574.1621 | 614.947
2636.1917 | 513.8696 | 638.6089 | 604.7145 | 569.8154 | 574.7969 | 609.5397
2637.1917 | 513.7543 | 638.3502 | 605.9945 | 569.406 | 575.2778 | 610.3454
2638.1917 | 513.9632 | 637.8923 | 605.0925 | 569.5322 | 574.0822 | 607.7299
2639.1917 | 514.0596 | 637.5974 | 605.137 | 568.9261 | 572.8766 | 610.6305
2640.1917 | 514.3342 | 637.2096 | 604.9142 | 568.7107 | 570.6668 | 611.3815