## Test Conditions
DESIREE-FIRE Intermediate Scale Test 6 - Circuit Simulator Data Only
Test Date: | 2010-03-03
DCSim DAQ Start Time | 13:38
DCSim Time for Synchronization | 14:06
Heat Source Synchronization | 0:00 | hours:minutes:seconds
Heat Source DAQ Start Time | 14:05
Fire Time | 14:34
Offset | 0:56 | hours:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 3360 | seconds
Heat Source Offset | 0:29 | hours:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 1740 | seconds
Heat Source Stop Time | 15:15
Test Duration | 0:41 | hours:minutes:seconds
| 2460 | seconds
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
Intercable Configuration | PE/PVC, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 8, 9, and 10 represents the air temperature 3', 5', and 7' down the tray located in D Position. These are labeled as "D Position - 3'", "D Position - Middle", "D Position - 7'", respectively.
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds.
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | Int-Cab_VT7-T1 | Int-Cab_VT7-T2 | Int-Cab_VT7-T3 | Int-Cab_VT7-T4 | Int-Cab_VT7-T5 | Int-Cab_VT7-T6 | Int-Cab_VT7-T7 | Int-Cab_VTU-S1+a | Int-Cab_VTU-S1+b | Int-Cab_VTU-S2+a | Int-Cab_VTU-S2+b | Int-Cab_VTU-S1-a | Int-Cab_VTU-S1-b | Int-Cab_VTU-S2-a | Int-Cab_VTU-S2-b | T1-V(Batt -) | T2 -V(Batt -) | T3 - V(Batt -) | T4 - V(Batt -) | T5 - V(Batt -) | T6 - V(Batt -) | T7 - V(Batt -) | {S1+a} - V(Batt - ) | {S1+b} - V(Batt - ) | {S2+a} - V(Batt - ) | {S2+b} - V(Batt - ) | {S1-a} - V(Batt -) | {S1-b} - V(Batt - ) | {S2-a} - V(Batt - ) | {S2-b} - V(Batt - ) | {S1+a} - {S1-a} | {S1+a} - {S2-a} | {S2+a} - {S1-a} | {S2+a} - {S2-a}
-0.96875 | 123.587 | -61.6653 | 61.6882 | 0.053175 | -0.0451 | 0.015472 | -0.043331 | 0.06831 | 0.039799 | -0.067295 | 61.5371 | 61.4583 | 61.3402 | 61.0191 | 61.6704 | 61.818 | 61.349 | 61.5046 | 61.7185 | 61.6202 | 61.6808 | 61.622 | 61.7337 | 61.7051 | 61.598 | 61.5371 | 61.4583 | 61.3402 | 61.0191 | 61.6704 | 61.818 | 61.349 | 61.5046 | -0.13335 | 0.18814 | -0.33029 | -0.0088
0.70312 | 123.5001 | -61.7157 | 61.6608 | 0.062332 | -0.049678 | 0.006315 | -0.034174 | 0.06831 | 0.035221 | -0.058139 | 61.5371 | 61.4674 | 61.331 | 61.01 | 61.675 | 61.818 | 61.349 | 61.5046 | 61.778 | 61.666 | 61.722 | 61.6815 | 61.784 | 61.7509 | 61.6576 | 61.5371 | 61.4674 | 61.331 | 61.01 | 61.675 | 61.818 | 61.349 | 61.5046 | -0.13792 | 0.18814 | -0.34402 | -0.017957
2.4375 | 123.4543 | -61.7157 | 61.7157 | 0.057754 | -0.040521 | 0.010893 | -0.029595 | 0.063733 | 0.035221 | -0.062717 | 61.5463 | 61.4583 | 61.3722 | 61.0191 | 61.6796 | 61.8088 | 61.3444 | 61.5092 | 61.7735 | 61.6752 | 61.7266 | 61.6861 | 61.7794 | 61.7509 | 61.653 | 61.5463 | 61.4583 | 61.3722 | 61.0191 | 61.6796 | 61.8088 | 61.3444 | 61.5092 | -0.13335 | 0.20187 | -0.30739 | 0.027827
4.1562 | 123.5184 | -61.6974 | 61.6882 | 0.062332 | -0.054257 | 0.010893 | -0.029595 | 0.06831 | 0.035221 | -0.067295 | 61.473 | 61.4537 | 61.3218 | 61.0146 | 61.6796 | 61.8042 | 61.3535 | 61.5092 | 61.7597 | 61.6431 | 61.7083 | 61.6678 | 61.7657 | 61.7326 | 61.6301 | 61.473 | 61.4537 | 61.3218 | 61.0146 | 61.6796 | 61.8042 | 61.3535 | 61.5092 | -0.2066 | 0.11946 | -0.35776 | -0.031692
5.8906 | 123.5779 | -61.6653 | 61.6608 | 0.057754 | -0.054257 | 0.006315 | -0.029595 | 0.06831 | 0.044377 | -0.076452 | 61.5463 | 61.4491 | 61.2944 | 61.0146 | 61.6613 | 61.8134 | 61.3444 | 61.5 | 61.7231 | 61.6111 | 61.6717 | 61.6357 | 61.7337 | 61.7097 | 61.5889 | 61.5463 | 61.4491 | 61.2944 | 61.0146 | 61.6613 | 61.8134 | 61.3444 | 61.5 | -0.11503 | 0.20187 | -0.36691 | -0.050004
7.5781 | 123.5321 | -61.647 | 61.6516 | 0.048597 | -0.054257 | 0.006315 | -0.038752 | 0.063733 | 0.035221 | -0.062717 | 61.4959 | 61.4491 | 61.2944 | 61.0146 | 61.6704 | 61.8088 | 61.3352 | 61.4954 | 61.6956 | 61.5928 | 61.6533 | 61.6083 | 61.7108 | 61.6823 | 61.5843 | 61.4959 | 61.4491 | 61.2944 | 61.0146 | 61.6704 | 61.8088 | 61.3352 | 61.4954 | -0.17455 | 0.16067 | -0.37607 | -0.040847
9.3125 | 123.5229 | -61.6562 | 61.6745 | 0.053175 | -0.0451 | 0.006315 | -0.034174 | 0.06831 | 0.030642 | -0.067295 | 61.5325 | 61.4491 | 61.3218 | 61.0146 | 61.6613 | 61.8042 | 61.3398 | 61.5 | 61.7094 | 61.6111 | 61.6625 | 61.622 | 61.7245 | 61.6868 | 61.5889 | 61.5325 | 61.4491 | 61.3218 | 61.0146 | 61.6613 | 61.8042 | 61.3398 | 61.5 | -0.12877 | 0.19272 | -0.33944 | -0.017957
11.0469 | 123.4543 | -61.7249 | 61.6745 | 0.071489 | -0.058836 | 0.010893 | -0.034174 | 0.06831 | 0.035221 | -0.076452 | 61.56 | 61.4445 | 61.331 | 61.01 | 61.6704 | 61.8088 | 61.3398 | 61.5046 | 61.7963 | 61.666 | 61.7357 | 61.6907 | 61.7932 | 61.7601 | 61.6484 | 61.56 | 61.4445 | 61.331 | 61.01 | 61.6704 | 61.8088 | 61.3398 | 61.5046 | -0.11046 | 0.22019 | -0.33944 | -0.0088
12.7188 | 123.4818 | -61.702 | 61.6882 | 0.062332 | -0.0451 | 0.010893 | -0.038752 | 0.06831 | 0.035221 | -0.067295 | 61.5096 | 61.4491 | 61.3081 | 61.01 | 61.6659 | 61.8088 | 61.3398 | 61.4909 | 61.7643 | 61.6569 | 61.7129 | 61.6632 | 61.7703 | 61.7372 | 61.6347 | 61.5096 | 61.4491 | 61.3081 | 61.01 | 61.6659 | 61.8088 | 61.3398 | 61.4909 | -0.15624 | 0.16982 | -0.35775 | -0.031691
14.4531 | 123.4131 | -61.7203 | 61.6791 | 0.057754 | -0.058836 | 0.001736 | -0.034174 | 0.063733 | 0.044377 | -0.076452 | 61.5188 | 61.4491 | 61.2944 | 61.01 | 61.6659 | 61.7951 | 61.3444 | 61.4954 | 61.778 | 61.6614 | 61.722 | 61.6861 | 61.784 | 61.7647 | 61.6438 | 61.5188 | 61.4491 | 61.2944 | 61.01 | 61.6659 | 61.7951 | 61.3444 | 61.4954 | -0.14708 | 0.1744 | -0.37149 | -0.050004
16.1875 | 123.4634 | -61.7157 | 61.6425 | 0.057754 | -0.049678 | 0.006315 | -0.047909 | 0.063733 | 0.035221 | -0.067295 | 61.505 | 61.4537 | 61.3539 | 61.0054 | 61.6659 | 61.8088 | 61.3398 | 61.4909 | 61.7735 | 61.666 | 61.722 | 61.6678 | 61.7794 | 61.7509 | 61.6484 | 61.505 | 61.4537 | 61.3539 | 61.0054 | 61.6659 | 61.8088 | 61.3398 | 61.4909 | -0.16082 | 0.16524 | -0.31197 | 0.014091
17.9375 | 123.4314 | -61.6837 | 61.7157 | 0.053175 | -0.054257 | 0.010893 | -0.038752 | 0.063733 | 0.035221 | -0.067295 | 61.505 | 61.4399 | 61.299 | 61.01 | 61.6704 | 61.8042 | 61.3398 | 61.4909 | 61.7368 | 61.6294 | 61.6945 | 61.6449 | 61.7474 | 61.7189 | 61.6164 | 61.505 | 61.4399 | 61.299 | 61.01 | 61.6704 | 61.8042 | 61.3398 | 61.4909 | -0.1654 | 0.16524 | -0.37149 | -0.040848
19.6094 | 123.5596 | -61.6562 | 61.6333 | 0.057754 | -0.054257 | 0.010893 | -0.038752 | 0.06831 | 0.035221 | -0.062717 | 61.5142 | 61.4399 | 61.3081 | 61.0008 | 61.6613 | 61.8042 | 61.3352 | 61.4954 | 61.7139 | 61.6019 | 61.6671 | 61.6174 | 61.7245 | 61.6914 | 61.5935 | 61.5142 | 61.4399 | 61.3081 | 61.0008 | 61.6613 | 61.8042 | 61.3352 | 61.4954 | -0.14708 | 0.17898 | -0.35318 | -0.027112
21.3438 | 123.468 | -61.6837 | 61.6745 | 0.062332 | -0.049678 | 0.006315 | -0.043331 | 0.063733 | 0.035221 | -0.062717 | 61.4959 | 61.4491 | 61.3905 | 61.0054 | 61.6659 | 61.8042 | 61.3352 | 61.5 | 61.746 | 61.634 | 61.69 | 61.6403 | 61.7474 | 61.7189 | 61.6209 | 61.4959 | 61.4491 | 61.3905 | 61.0054 | 61.6659 | 61.8042 | 61.3352 | 61.5 | -0.16998 | 0.16067 | -0.27535 | 0.055297
23.0156 | 123.4497 | -61.7111 | 61.6562 | 0.062332 | -0.058836 | 0.001736 | -0.043331 | 0.072888 | 0.030642 | -0.062717 | 61.4913 | 61.4399 | 61.3951 | 61.0054 | 61.6613 | 61.7996 | 61.3306 | 61.4909 | 61.7735 | 61.6523 | 61.7129 | 61.6678 | 61.784 | 61.7418 | 61.6484 | 61.4913 | 61.4399 | 61.3951 | 61.0054 | 61.6613 | 61.7996 | 61.3306 | 61.4909 | -0.16998 | 0.16067 | -0.26619 | 0.064453
24.7344 | 123.436 | -61.6928 | 61.6379 | 0.057754 | -0.049678 | 0.015472 | -0.038752 | 0.063733 | 0.039799 | -0.067295 | 61.5691 | 61.4445 | 61.3768 | 61.0008 | 61.6659 | 61.7951 | 61.3352 | 61.4863 | 61.7506 | 61.6431 | 61.7083 | 61.6541 | 61.7565 | 61.7326 | 61.6255 | 61.5691 | 61.4445 | 61.3768 | 61.0008 | 61.6659 | 61.7951 | 61.3352 | 61.4863 | -0.09672 | 0.23392 | -0.28908 | 0.041562
26.4688 | 123.5733 | -61.6287 | 61.6653 | 0.053175 | -0.058836 | 0.001736 | -0.043331 | 0.06831 | 0.030642 | -0.067295 | 61.4822 | 61.4445 | 61.3585 | 61.0008 | 61.6704 | 61.7996 | 61.3398 | 61.5 | 61.6819 | 61.5699 | 61.6305 | 61.5854 | 61.697 | 61.6594 | 61.5614 | 61.4822 | 61.4445 | 61.3585 | 61.0008 | 61.6704 | 61.7996 | 61.3398 | 61.5 | -0.18829 | 0.14235 | -0.31197 | 0.01867
28.2031 | 123.4772 | -61.6974 | 61.6425 | 0.062332 | -0.054257 | 0.015472 | -0.034174 | 0.072888 | 0.044377 | -0.071874 | 61.5463 | 61.4399 | 61.3631 | 61.0054 | 61.6659 | 61.8042 | 61.3352 | 61.4863 | 61.7597 | 61.6431 | 61.7129 | 61.6632 | 61.7703 | 61.7418 | 61.6255 | 61.5463 | 61.4399 | 61.3631 | 61.0054 | 61.6659 | 61.8042 | 61.3352 | 61.4863 | -0.11961 | 0.21103 | -0.30282 | 0.027827
29.9375 | 123.468 | -61.6882 | 61.6608 | 0.057754 | -0.054257 | 0.010893 | -0.038752 | 0.06831 | 0.035221 | -0.062717 | 61.5005 | 61.4445 | 61.3539 | 61.0008 | 61.6613 | 61.8042 | 61.3352 | 61.5 | 61.746 | 61.634 | 61.6991 | 61.6495 | 61.7565 | 61.7235 | 61.6255 | 61.5005 | 61.4445 | 61.3539 | 61.0008 | 61.6613 | 61.8042 | 61.3352 | 61.5 | -0.16082 | 0.16525 | -0.30739 | 0.01867
31.6094 | 123.5367 | -61.6608 | 61.6379 | 0.057754 | -0.049678 | 0.010893 | -0.038752 | 0.06831 | 0.026064 | -0.067295 | 61.5096 | 61.4399 | 61.3722 | 61.01 | 61.6567 | 61.7996 | 61.3215 | 61.4863 | 61.7185 | 61.6111 | 61.6717 | 61.622 | 61.7291 | 61.6868 | 61.5935 | 61.5096 | 61.4399 | 61.3722 | 61.01 | 61.6567 | 61.7996 | 61.3215 | 61.4863 | -0.14708 | 0.18814 | -0.2845 | 0.050719
33.3438 | 123.4818 | -61.647 | 61.7111 | 0.062332 | -0.049678 | 0.010893 | -0.038752 | 0.063733 | 0.026064 | -0.071874 | 61.5279 | 61.4445 | 61.3631 | 60.9917 | 61.6613 | 61.7951 | 61.3352 | 61.4909 | 61.7094 | 61.5974 | 61.6579 | 61.6083 | 61.7108 | 61.6731 | 61.5752 | 61.5279 | 61.4445 | 61.3631 | 60.9917 | 61.6613 | 61.7951 | 61.3352 | 61.4909 | -0.13335 | 0.19272 | -0.29824 | 0.027827
35.0156 | 123.5275 | -61.6287 | 61.647 | 0.057754 | -0.049678 | 0.006315 | -0.038752 | 0.06831 | 0.030642 | -0.071874 | 61.5142 | 61.4354 | 61.331 | 61.0008 | 61.6567 | 61.7951 | 61.3306 | 61.4909 | 61.6865 | 61.579 | 61.635 | 61.59 | 61.697 | 61.6594 | 61.5568 | 61.5142 | 61.4354 | 61.331 | 61.0008 | 61.6567 | 61.7951 | 61.3306 | 61.4909 | -0.14251 | 0.18356 | -0.32571 | 0.000357
36.75 | 123.4497 | -61.6882 | 61.647 | 0.057754 | -0.054257 | 0.006315 | -0.047909 | 0.063733 | 0.030642 | -0.062717 | 61.505 | 61.4399 | 61.3859 | 60.9962 | 61.6567 | 61.7951 | 61.3261 | 61.4817 | 61.746 | 61.634 | 61.6945 | 61.6403 | 61.752 | 61.7189 | 61.6255 | 61.505 | 61.4399 | 61.3859 | 60.9962 | 61.6567 | 61.7951 | 61.3261 | 61.4817 | -0.15166 | 0.17898 | -0.27077 | 0.059874
38.4219 | 123.5046 | -61.6196 | 61.6791 | 0.057754 | -0.058836 | 0.006315 | -0.043331 | 0.06831 | 0.039799 | -0.076452 | 61.5234 | 61.4354 | 61.3859 | 60.9962 | 61.6613 | 61.7996 | 61.3398 | 61.4863 | 61.6773 | 61.5607 | 61.6259 | 61.5762 | 61.6879 | 61.6594 | 61.5431 | 61.5234 | 61.4354 | 61.3859 | 60.9962 | 61.6613 | 61.7996 | 61.3398 | 61.4863 | -0.13793 | 0.18356 | -0.27535 | 0.046139
40.0781 | 123.4909 | -61.6562 | 61.6745 | 0.057754 | -0.054257 | 0.006315 | -0.034174 | 0.063733 | 0.026064 | -0.067295 | 61.5417 | 61.4354 | 61.3539 | 61.0008 | 61.6567 | 61.7951 | 61.3215 | 61.4909 | 61.7139 | 61.6019 | 61.6625 | 61.622 | 61.7199 | 61.6823 | 61.5889 | 61.5417 | 61.4354 | 61.3539 | 61.0008 | 61.6567 | 61.7951 | 61.3215 | 61.4909 | -0.11504 | 0.22019 | -0.30282 | 0.032405
41.8125 | 123.5321 | -61.6653 | 61.6241 | 0.057754 | -0.054257 | 0.010893 | -0.038752 | 0.063733 | 0.030642 | -0.067295 | 61.5508 | 61.4308 | 61.3081 | 60.9962 | 61.6476 | 61.7951 | 61.3306 | 61.4909 | 61.7231 | 61.6111 | 61.6762 | 61.6266 | 61.7291 | 61.696 | 61.598 | 61.5508 | 61.4308 | 61.3081 | 60.9962 | 61.6476 | 61.7951 | 61.3306 | 61.4909 | -0.096721 | 0.22019 | -0.33944 | -0.022534
43.5469 | 123.4772 | -61.6196 | 61.6974 | 0.057754 | -0.049678 | 0.001736 | -0.043331 | 0.063733 | 0.039799 | -0.062717 | 61.5508 | 61.4445 | 61.3631 | 60.9917 | 61.6613 | 61.7859 | 61.3306 | 61.4817 | 61.6773 | 61.5699 | 61.6213 | 61.5762 | 61.6833 | 61.6594 | 61.5569 | 61.5508 | 61.4445 | 61.3631 | 60.9917 | 61.6613 | 61.7859 | 61.3306 | 61.4817 | -0.11046 | 0.22019 | -0.29824 | 0.032405
45.2188 | 123.4497 | -61.6425 | 61.6928 | 0.057754 | -0.063415 | 0.006315 | -0.038752 | 0.059155 | 0.035221 | -0.071874 | 61.5279 | 61.4354 | 61.3585 | 60.9871 | 61.6521 | 61.7905 | 61.3261 | 61.4909 | 61.7002 | 61.579 | 61.6488 | 61.6037 | 61.7016 | 61.6777 | 61.5706 | 61.5279 | 61.4354 | 61.3585 | 60.9871 | 61.6521 | 61.7905 | 61.3261 | 61.4909 | -0.12419 | 0.20187 | -0.29366 | 0.032405
46.9375 | 123.5275 | -61.6333 | 61.6241 | 0.057754 | -0.049678 | 0.006315 | -0.038752 | 0.072888 | 0.039799 | -0.062717 | 61.5142 | 61.4308 | 61.3402 | 60.9917 | 61.6476 | 61.7951 | 61.3261 | 61.4725 | 61.6911 | 61.5836 | 61.6396 | 61.5945 | 61.7062 | 61.6731 | 61.5706 | 61.5142 | 61.4308 | 61.3402 | 60.9917 | 61.6476 | 61.7951 | 61.3261 | 61.4725 | -0.13335 | 0.18814 | -0.30739 | 0.014092
48.6719 | 123.4177 | -61.702 | 61.6333 | 0.06691 | -0.049678 | 0.015472 | -0.038752 | 0.06831 | 0.030642 | -0.067295 | 61.5463 | 61.4308 | 61.3173 | 60.9917 | 61.6521 | 61.7905 | 61.3215 | 61.4725 | 61.7689 | 61.6523 | 61.7174 | 61.6632 | 61.7703 | 61.7326 | 61.6347 | 61.5463 | 61.4308 | 61.3173 | 60.9917 | 61.6521 | 61.7905 | 61.3215 | 61.4725 | -0.10588 | 0.22477 | -0.33487 | -0.004221
50.4219 | 123.5413 | -61.6425 | 61.6287 | 0.057754 | -0.054257 | -0.002842 | -0.043331 | 0.06831 | 0.030642 | -0.067295 | 61.56 | 61.4262 | 61.3173 | 60.9871 | 61.6521 | 61.7813 | 61.3169 | 61.4725 | 61.7002 | 61.5882 | 61.6396 | 61.5991 | 61.7108 | 61.6731 | 61.5752 | 61.56 | 61.4262 | 61.3173 | 60.9871 | 61.6521 | 61.7813 | 61.3169 | 61.4725 | -0.092143 | 0.24308 | -0.33487 | 0.000357
52.0938 | 123.4772 | -61.6241 | 61.6699 | 0.057754 | -0.054257 | 0.006315 | -0.043331 | 0.054577 | 0.021485 | -0.076452 | 61.5737 | 61.4171 | 61.3081 | 60.9871 | 61.6476 | 61.7905 | 61.3169 | 61.4771 | 61.6819 | 61.5699 | 61.6305 | 61.5808 | 61.6787 | 61.6456 | 61.5477 | 61.5737 | 61.4171 | 61.3081 | 60.9871 | 61.6476 | 61.7905 | 61.3169 | 61.4771 | -0.073828 | 0.25682 | -0.33944 | -0.008799
53.8125 | 123.5367 | -61.6104 | 61.6562 | 0.053175 | -0.058836 | 0.001736 | -0.043331 | 0.063733 | 0.026064 | -0.071874 | 61.5646 | 61.4216 | 61.3356 | 60.9825 | 61.6476 | 61.7813 | 61.3169 | 61.4725 | 61.6636 | 61.5516 | 61.6121 | 61.5671 | 61.6741 | 61.6365 | 61.5385 | 61.5646 | 61.4216 | 61.3356 | 60.9825 | 61.6476 | 61.7813 | 61.3169 | 61.4725 | -0.082985 | 0.24766 | -0.31197 | 0.01867
55.5469 | 123.3902 | -61.6699 | 61.6379 | 0.062332 | -0.058836 | 0.010893 | -0.038752 | 0.063733 | 0.035221 | -0.071874 | 61.5417 | 61.4171 | 61.299 | 60.9825 | 61.6476 | 61.7859 | 61.3169 | 61.4725 | 61.7323 | 61.6111 | 61.6808 | 61.6312 | 61.7337 | 61.7051 | 61.598 | 61.5417 | 61.4171 | 61.299 | 60.9825 | 61.6476 | 61.7859 | 61.3169 | 61.4725 | -0.10588 | 0.22476 | -0.3486 | -0.017956
57.2969 | 123.4589 | -61.6791 | 61.6425 | 0.057754 | -0.058836 | 0.001736 | -0.029595 | 0.06831 | 0.039799 | -0.067295 | 61.5371 | 61.4216 | 61.3081 | 60.9779 | 61.6384 | 61.7813 | 61.3078 | 61.468 | 61.7368 | 61.6202 | 61.6808 | 61.6495 | 61.7474 | 61.7189 | 61.6118 | 61.5371 | 61.4216 | 61.3081 | 60.9779 | 61.6384 | 61.7813 | 61.3078 | 61.468 | -0.1013 | 0.22934 | -0.33029 | 0.000358
58.9688 | 123.436 | -61.647 | 61.647 | 0.057754 | -0.054257 | 0.010893 | -0.038752 | 0.059155 | 0.035221 | -0.062717 | 61.5463 | 61.4262 | 61.2898 | 60.9733 | 61.6476 | 61.7722 | 61.3078 | 61.4725 | 61.7048 | 61.5928 | 61.6579 | 61.6083 | 61.7062 | 61.6823 | 61.5843 | 61.5463 | 61.4262 | 61.2898 | 60.9733 | 61.6476 | 61.7722 | 61.3078 | 61.4725 | -0.1013 | 0.2385 | -0.35776 | -0.017955
60.6875 | 123.5046 | -61.5829 | 61.6562 | 0.057754 | -0.063415 | 0.010893 | -0.038752 | 0.063733 | 0.030642 | -0.076452 | 61.5417 | 61.4216 | 61.3035 | 60.9825 | 61.643 | 61.7813 | 61.3123 | 61.4725 | 61.6407 | 61.5195 | 61.5938 | 61.5442 | 61.6467 | 61.6136 | 61.5065 | 61.5417 | 61.4216 | 61.3035 | 60.9825 | 61.643 | 61.7813 | 61.3123 | 61.4725 | -0.1013 | 0.22934 | -0.33944 | -0.008799
62.4375 | 123.4497 | -61.6241 | 61.6425 | 0.062332 | -0.058836 | 0.015472 | -0.034174 | 0.063733 | 0.044377 | -0.062717 | 61.4822 | 61.4171 | 61.3035 | 60.9779 | 61.6338 | 61.7768 | 61.3123 | 61.4588 | 61.6865 | 61.5653 | 61.6396 | 61.59 | 61.6879 | 61.6685 | 61.5614 | 61.4822 | 61.4171 | 61.3035 | 60.9779 | 61.6338 | 61.7768 | 61.3123 | 61.4588 | -0.15166 | 0.16982 | -0.33029 | -0.008799
64.1719 | 123.4177 | -61.6699 | 61.647 | 0.062332 | -0.058836 | 0.006315 | -0.038752 | 0.072888 | 0.039799 | -0.067295 | 61.5554 | 61.4216 | 61.331 | 60.9733 | 61.6384 | 61.7768 | 61.3169 | 61.4634 | 61.7323 | 61.6111 | 61.6762 | 61.6312 | 61.7428 | 61.7097 | 61.6026 | 61.5554 | 61.4216 | 61.331 | 60.9733 | 61.6384 | 61.7768 | 61.3169 | 61.4634 | -0.082986 | 0.2385 | -0.30739 | 0.014092
65.8281 | 123.3673 | -61.6562 | 61.702 | 0.048597 | -0.063415 | 0.015472 | -0.038752 | 0.059155 | 0.035221 | -0.067295 | 61.5417 | 61.4262 | 61.3447 | 60.9733 | 61.6384 | 61.7676 | 61.3078 | 61.468 | 61.7048 | 61.5928 | 61.6717 | 61.6174 | 61.7153 | 61.6914 | 61.5889 | 61.5417 | 61.4262 | 61.3447 | 60.9733 | 61.6384 | 61.7676 | 61.3078 | 61.468 | -0.096722 | 0.23392 | -0.29366 | 0.036984
67.5625 | 123.436 | -61.6516 | 61.6699 | 0.062332 | -0.054257 | 0.001736 | -0.034174 | 0.063733 | 0.035221 | -0.071874 | 61.5142 | 61.4171 | 61.3127 | 60.9688 | 61.6338 | 61.7768 | 61.3032 | 61.4725 | 61.7139 | 61.5974 | 61.6533 | 61.6174 | 61.7153 | 61.6868 | 61.5797 | 61.5142 | 61.4171 | 61.3127 | 60.9688 | 61.6338 | 61.7768 | 61.3032 | 61.4725 | -0.11962 | 0.21103 | -0.32113 | 0.009514
69.2344 | 123.4589 | -61.6058 | 61.6287 | 0.062332 | -0.054257 | 0.006315 | -0.038752 | 0.072888 | 0.030642 | -0.071874 | 61.5279 | 61.4079 | 61.2761 | 60.9642 | 61.6338 | 61.7722 | 61.294 | 61.4542 | 61.6682 | 61.5516 | 61.6121 | 61.5671 | 61.6787 | 61.6365 | 61.534 | 61.5279 | 61.4079 | 61.2761 | 60.9642 | 61.6338 | 61.7722 | 61.294 | 61.4542 | -0.10588 | 0.23392 | -0.35776 | -0.017955
70.9688 | 123.4543 | -61.5921 | 61.6333 | 0.057754 | -0.054257 | 0.015472 | -0.043331 | 0.059155 | 0.044377 | -0.071874 | 61.505 | 61.4079 | 61.3264 | 60.9688 | 61.6338 | 61.763 | 61.3032 | 61.4634 | 61.6499 | 61.5378 | 61.6076 | 61.5488 | 61.6513 | 61.6365 | 61.5202 | 61.505 | 61.4079 | 61.3264 | 60.9688 | 61.6338 | 61.763 | 61.3032 | 61.4634 | -0.12877 | 0.20187 | -0.30739 | 0.023249
72.7188 | 123.5046 | -61.5601 | 61.6562 | 0.057754 | -0.054257 | 0.001736 | -0.043331 | 0.072888 | 0.039799 | -0.076452 | 61.5325 | 61.4125 | 61.3402 | 60.9642 | 61.6338 | 61.7722 | 61.3032 | 61.4634 | 61.6178 | 61.5058 | 61.5618 | 61.5167 | 61.6329 | 61.5999 | 61.4836 | 61.5325 | 61.4125 | 61.3402 | 60.9642 | 61.6338 | 61.7722 | 61.3032 | 61.4634 | -0.1013 | 0.22934 | -0.29366 | 0.036984
74.3906 | 123.3444 | -61.6745 | 61.6241 | 0.062332 | -0.054257 | 0.001736 | -0.038752 | 0.06831 | 0.039799 | -0.067295 | 61.5279 | 61.4079 | 61.2898 | 60.9596 | 61.6292 | 61.7676 | 61.294 | 61.4496 | 61.7368 | 61.6202 | 61.6762 | 61.6357 | 61.7428 | 61.7143 | 61.6072 | 61.5279 | 61.4079 | 61.2898 | 60.9596 | 61.6292 | 61.7676 | 61.294 | 61.4496 | -0.1013 | 0.23392 | -0.33944 | -0.00422
76.125 | 123.4497 | -61.6196 | 61.6287 | 0.057754 | -0.054257 | 0.015472 | -0.038752 | 0.063733 | 0.030642 | -0.076452 | 61.5325 | 61.4079 | 61.2944 | 60.9688 | 61.6201 | 61.7676 | 61.3032 | 61.4588 | 61.6773 | 61.5653 | 61.635 | 61.5808 | 61.6833 | 61.6502 | 61.5431 | 61.5325 | 61.4079 | 61.2944 | 60.9688 | 61.6201 | 61.7676 | 61.3032 | 61.4588 | -0.087566 | 0.22934 | -0.32571 | -0.008799
77.7969 | 123.4039 | -61.6379 | 61.6333 | 0.057754 | -0.058836 | 0.006315 | -0.034174 | 0.072888 | 0.035221 | -0.067295 | 61.5234 | 61.4079 | 61.3539 | 60.9642 | 61.6338 | 61.763 | 61.2986 | 61.4588 | 61.6956 | 61.579 | 61.6442 | 61.6037 | 61.7108 | 61.6731 | 61.5706 | 61.5234 | 61.4079 | 61.3539 | 60.9642 | 61.6338 | 61.763 | 61.2986 | 61.4588 | -0.11046 | 0.22476 | -0.27993 | 0.055297
79.5312 | 123.436 | -61.5921 | 61.647 | 0.053175 | -0.058836 | 0.010893 | -0.038752 | 0.063733 | 0.026064 | -0.071874 | 61.5096 | 61.4033 | 61.3768 | 60.955 | 61.6201 | 61.7584 | 61.2894 | 61.4496 | 61.6453 | 61.5333 | 61.603 | 61.5533 | 61.6558 | 61.6182 | 61.5202 | 61.5096 | 61.4033 | 61.3768 | 60.955 | 61.6201 | 61.7584 | 61.2894 | 61.4496 | -0.11046 | 0.22019 | -0.2433 | 0.087345
81.2031 | 123.349 | -61.6882 | 61.6196 | 0.053175 | -0.054257 | 0.006315 | -0.029595 | 0.063733 | 0.039799 | -0.062717 | 61.5142 | 61.4033 | 61.2806 | 60.9642 | 61.6201 | 61.7584 | 61.2894 | 61.4451 | 61.7414 | 61.634 | 61.6945 | 61.6586 | 61.752 | 61.728 | 61.6255 | 61.5142 | 61.4033 | 61.2806 | 60.9642 | 61.6201 | 61.7584 | 61.2894 | 61.4451 | -0.10588 | 0.22476 | -0.33944 | -0.008799
83 | 123.349 | -61.6837 | 61.5875 | 0.057754 | -0.049678 | 0.010893 | -0.038752 | 0.06831 | 0.039799 | -0.062717 | 61.5234 | 61.3987 | 61.331 | 60.9596 | 61.6201 | 61.763 | 61.294 | 61.4496 | 61.7414 | 61.634 | 61.6945 | 61.6449 | 61.752 | 61.7235 | 61.6209 | 61.5234 | 61.3987 | 61.331 | 60.9596 | 61.6201 | 61.763 | 61.294 | 61.4496 | -0.096723 | 0.22934 | -0.28908 | 0.036984
84.6875 | 123.3856 | -61.6425 | 61.6333 | 0.057754 | -0.054257 | 0.010893 | -0.038752 | 0.06831 | 0.035221 | -0.067295 | 61.4959 | 61.4033 | 61.3264 | 60.9596 | 61.6247 | 61.7584 | 61.2986 | 61.4496 | 61.7002 | 61.5882 | 61.6533 | 61.6037 | 61.7108 | 61.6777 | 61.5752 | 61.4959 | 61.4033 | 61.3264 | 60.9596 | 61.6247 | 61.7584 | 61.2986 | 61.4496 | -0.12877 | 0.19729 | -0.29824 | 0.027828
86.4844 | 123.4039 | -61.6425 | 61.5967 | 0.057754 | -0.063415 | 0.010893 | -0.038752 | 0.063733 | 0.039799 | -0.067295 | 61.5234 | 61.3987 | 61.2852 | 60.9642 | 61.6201 | 61.7584 | 61.2894 | 61.4451 | 61.7002 | 61.579 | 61.6533 | 61.6037 | 61.7062 | 61.6823 | 61.5752 | 61.5234 | 61.3987 | 61.2852 | 60.9642 | 61.6201 | 61.7584 | 61.2894 | 61.4451 | -0.096723 | 0.23392 | -0.33487 | -0.004221
88.2188 | 123.3261 | -61.6425 | 61.6653 | 0.062332 | -0.054257 | 0.001736 | -0.038752 | 0.063733 | 0.039799 | -0.071874 | 61.5096 | 61.4033 | 61.331 | 60.955 | 61.6201 | 61.7539 | 61.2894 | 61.4451 | 61.7048 | 61.5882 | 61.6442 | 61.6037 | 61.7062 | 61.6823 | 61.5706 | 61.5096 | 61.4033 | 61.331 | 60.955 | 61.6201 | 61.7539 | 61.2894 | 61.4451 | -0.11046 | 0.22019 | -0.28908 | 0.041562
90 | 123.4726 | -61.5738 | 61.6379 | 0.062332 | -0.058836 | 0.010893 | -0.043331 | 0.063733 | 0.030642 | -0.076452 | 61.5096 | 61.3987 | 61.3356 | 60.9504 | 61.6201 | 61.7539 | 61.2849 | 61.4496 | 61.6361 | 61.515 | 61.5847 | 61.5305 | 61.6375 | 61.6044 | 61.4973 | 61.5096 | 61.3987 | 61.3356 | 60.9504 | 61.6201 | 61.7539 | 61.2849 | 61.4496 | -0.11046 | 0.22476 | -0.2845 | 0.050719
91.7969 | 123.4314 | -61.5921 | 61.6013 | 0.048597 | -0.054257 | 0.006315 | -0.047909 | 0.06831 | 0.030642 | -0.071874 | 61.4822 | 61.3942 | 61.3356 | 60.955 | 61.6155 | 61.7584 | 61.2803 | 61.4496 | 61.6407 | 61.5378 | 61.5984 | 61.5442 | 61.6604 | 61.6227 | 61.5202 | 61.4822 | 61.3942 | 61.3356 | 60.955 | 61.6155 | 61.7584 | 61.2803 | 61.4496 | -0.13335 | 0.20187 | -0.27993 | 0.055297
93.5938 | 123.3856 | -61.6333 | 61.6013 | 0.053175 | -0.054257 | 0.010893 | -0.034174 | 0.063733 | 0.030642 | -0.062717 | 61.5279 | 61.3942 | 61.3218 | 60.9504 | 61.6155 | 61.7493 | 61.2849 | 61.4451 | 61.6865 | 61.579 | 61.6442 | 61.5991 | 61.697 | 61.6639 | 61.5706 | 61.5279 | 61.3942 | 61.3218 | 60.9504 | 61.6155 | 61.7493 | 61.2849 | 61.4451 | -0.087566 | 0.24308 | -0.29366 | 0.036984
95.2656 | 123.4543 | -61.5692 | 61.6333 | 0.053175 | -0.058836 | 0.006315 | -0.047909 | 0.06831 | 0.035221 | -0.067295 | 61.5188 | 61.385 | 61.2898 | 60.9504 | 61.6109 | 61.7539 | 61.2849 | 61.4451 | 61.6224 | 61.5104 | 61.5755 | 61.5213 | 61.6375 | 61.6044 | 61.5019 | 61.5188 | 61.385 | 61.2898 | 60.9504 | 61.6109 | 61.7539 | 61.2849 | 61.4451 | -0.092145 | 0.23392 | -0.32113 | 0.004937
97 | 123.4314 | -61.5875 | 61.6104 | 0.057754 | -0.058836 | 0.006315 | -0.043331 | 0.063733 | 0.035221 | -0.067295 | 61.5234 | 61.3896 | 61.3447 | 60.9596 | 61.6018 | 61.7493 | 61.2803 | 61.4451 | 61.6453 | 61.5287 | 61.5938 | 61.5442 | 61.6513 | 61.6227 | 61.5202 | 61.5234 | 61.3896 | 61.3447 | 60.9596 | 61.6018 | 61.7493 | 61.2803 | 61.4451 | -0.078411 | 0.24308 | -0.25704 | 0.064454
98.6719 | 123.4772 | -61.5372 | 61.6516 | 0.062332 | -0.058836 | 0.010893 | -0.038752 | 0.063733 | 0.030642 | -0.071874 | 61.5234 | 61.3942 | 61.2944 | 60.955 | 61.6064 | 61.7493 | 61.2711 | 61.4405 | 61.5995 | 61.4783 | 61.5481 | 61.4984 | 61.6009 | 61.5678 | 61.4653 | 61.5234 | 61.3942 | 61.2944 | 60.955 | 61.6064 | 61.7493 | 61.2711 | 61.4405 | -0.082989 | 0.25223 | -0.31197 | 0.02325
100.3906 | 123.3627 | -61.6379 | 61.6241 | 0.062332 | -0.058836 | 0.006315 | -0.034174 | 0.063733 | 0.035221 | -0.062717 | 61.505 | 61.4033 | 61.3676 | 60.9504 | 61.6064 | 61.7447 | 61.2849 | 61.4405 | 61.7002 | 61.579 | 61.6442 | 61.6037 | 61.7016 | 61.6731 | 61.5752 | 61.505 | 61.4033 | 61.3676 | 60.9504 | 61.6064 | 61.7447 | 61.2849 | 61.4405 | -0.1013 | 0.22019 | -0.23872 | 0.082767
102.1875 | 123.3582 | -61.6196 | 61.6013 | 0.062332 | -0.063415 | 0.015472 | -0.038752 | 0.063733 | 0.030642 | -0.058139 | 61.5325 | 61.3942 | 61.3356 | 60.9596 | 61.6064 | 61.7401 | 61.2666 | 61.4268 | 61.6819 | 61.5562 | 61.635 | 61.5808 | 61.6833 | 61.6502 | 61.5614 | 61.5325 | 61.3942 | 61.3356 | 60.9596 | 61.6064 | 61.7401 | 61.2666 | 61.4268 | -0.073832 | 0.26597 | -0.27077 | 0.069032
103.8438 | 123.3215 | -61.6058 | 61.6745 | 0.057754 | -0.058836 | 0.006315 | -0.038752 | 0.063733 | 0.035221 | -0.067295 | 61.5325 | 61.3987 | 61.3722 | 60.955 | 61.6064 | 61.7401 | 61.2711 | 61.4359 | 61.6636 | 61.547 | 61.6121 | 61.5671 | 61.6696 | 61.6411 | 61.5385 | 61.5325 | 61.3987 | 61.3722 | 60.955 | 61.6064 | 61.7401 | 61.2711 | 61.4359 | -0.073832 | 0.26139 | -0.23414 | 0.10108
105.5156 | 123.381 | -61.6104 | 61.6241 | 0.06691 | -0.058836 | 0.006315 | -0.038752 | 0.063733 | 0.035221 | -0.062717 | 61.5279 | 61.4033 | 61.2852 | 60.9504 | 61.6018 | 61.7264 | 61.2711 | 61.4268 | 61.6773 | 61.5516 | 61.6167 | 61.5717 | 61.6741 | 61.6456 | 61.5477 | 61.5279 | 61.4033 | 61.2852 | 60.9504 | 61.6018 | 61.7264 | 61.2711 | 61.4268 | -0.073832 | 0.25681 | -0.31655 | 0.014093
107.1875 | 123.3536 | -61.6241 | 61.6196 | 0.062332 | -0.054257 | 0.010893 | -0.038752 | 0.063733 | 0.035221 | -0.058139 | 61.5417 | 61.4033 | 61.3814 | 60.955 | 61.5972 | 61.7355 | 61.2666 | 61.4268 | 61.6865 | 61.5699 | 61.635 | 61.5854 | 61.6879 | 61.6594 | 61.566 | 61.5417 | 61.4033 | 61.3814 | 60.955 | 61.5972 | 61.7355 | 61.2666 | 61.4268 | -0.055518 | 0.27513 | -0.21583 | 0.11482
108.8438 | 123.4268 | -61.5829 | 61.5829 | 0.057754 | -0.054257 | 0.015472 | -0.034174 | 0.063733 | 0.030642 | -0.062717 | 61.4913 | 61.3942 | 61.3631 | 60.9596 | 61.5972 | 61.731 | 61.2574 | 61.4222 | 61.6407 | 61.5287 | 61.5984 | 61.5488 | 61.6467 | 61.6136 | 61.5202 | 61.4913 | 61.3942 | 61.3631 | 60.9596 | 61.5972 | 61.731 | 61.2574 | 61.4222 | -0.10588 | 0.23392 | -0.23414 | 0.10566
110.5156 | 123.317 | -61.647 | 61.5967 | 0.062332 | -0.063415 | 0.015472 | -0.034174 | 0.063733 | 0.030642 | -0.071874 | 61.5325 | 61.4079 | 61.3173 | 60.9596 | 61.588 | 61.7264 | 61.2666 | 61.4176 | 61.7094 | 61.5836 | 61.6625 | 61.6129 | 61.7108 | 61.6777 | 61.5752 | 61.5325 | 61.4079 | 61.3173 | 60.9596 | 61.588 | 61.7264 | 61.2666 | 61.4176 | -0.055519 | 0.26597 | -0.27077 | 0.050719
112.1875 | 123.4497 | -61.5555 | 61.6425 | 0.057754 | -0.063415 | 0.006315 | -0.043331 | 0.054577 | 0.035221 | -0.067295 | 61.5417 | 61.4033 | 61.331 | 60.955 | 61.588 | 61.731 | 61.2574 | 61.4313 | 61.6132 | 61.4921 | 61.5618 | 61.5121 | 61.6101 | 61.5907 | 61.4882 | 61.5417 | 61.4033 | 61.331 | 60.955 | 61.588 | 61.731 | 61.2574 | 61.4313 | -0.046362 | 0.28428 | -0.25704 | 0.073611
113.8594 | 123.3719 | -61.6013 | 61.6104 | 0.06691 | -0.054257 | 0.010893 | -0.038752 | 0.054577 | 0.039799 | -0.067295 | 61.5188 | 61.3987 | 61.3402 | 60.9504 | 61.5926 | 61.7264 | 61.2666 | 61.4176 | 61.6682 | 61.547 | 61.6121 | 61.5625 | 61.6558 | 61.6411 | 61.534 | 61.5188 | 61.3987 | 61.3402 | 60.9504 | 61.5926 | 61.7264 | 61.2666 | 61.4176 | -0.073832 | 0.25223 | -0.25246 | 0.073611
115.5781 | 123.3536 | -61.6287 | 61.6333 | 0.062332 | -0.054257 | 0.006315 | -0.029595 | 0.063733 | 0.035221 | -0.062717 | 61.5234 | 61.4079 | 61.3768 | 60.9504 | 61.588 | 61.7172 | 61.2574 | 61.4176 | 61.6911 | 61.5745 | 61.635 | 61.5991 | 61.6925 | 61.6639 | 61.566 | 61.5234 | 61.4079 | 61.3768 | 60.9504 | 61.588 | 61.7172 | 61.2574 | 61.4176 | -0.064676 | 0.26597 | -0.21125 | 0.11939
117.25 | 123.381 | -61.5692 | 61.615 | 0.062332 | -0.058836 | 0.001736 | -0.038752 | 0.063733 | 0.044377 | -0.067295 | 61.5554 | 61.3987 | 61.3402 | 60.955 | 61.5789 | 61.7218 | 61.2528 | 61.413 | 61.6315 | 61.5104 | 61.571 | 61.5305 | 61.6329 | 61.6136 | 61.5019 | 61.5554 | 61.3987 | 61.3402 | 60.955 | 61.5789 | 61.7218 | 61.2528 | 61.413 | -0.02347 | 0.3026 | -0.23872 | 0.087347
118.9375 | 123.4314 | -61.5417 | 61.6241 | 0.053175 | -0.063415 | 0.001736 | -0.038752 | 0.059155 | 0.035221 | -0.067295 | 61.5325 | 61.4125 | 61.3356 | 60.955 | 61.5789 | 61.7172 | 61.2528 | 61.413 | 61.5949 | 61.4783 | 61.5435 | 61.503 | 61.6009 | 61.577 | 61.4745 | 61.5325 | 61.4125 | 61.3356 | 60.955 | 61.5789 | 61.7172 | 61.2528 | 61.413 | -0.046363 | 0.27971 | -0.2433 | 0.082768
120.6094 | 123.381 | -61.5601 | 61.6333 | 0.057754 | -0.058836 | 0.010893 | -0.047909 | 0.059155 | 0.035221 | -0.071874 | 61.5234 | 61.4033 | 61.3951 | 60.9504 | 61.5697 | 61.7127 | 61.2482 | 61.4039 | 61.6178 | 61.5012 | 61.571 | 61.5122 | 61.6192 | 61.5953 | 61.4882 | 61.5234 | 61.4033 | 61.3951 | 60.9504 | 61.5697 | 61.7127 | 61.2482 | 61.4039 | -0.046363 | 0.27513 | -0.17463 | 0.14686
122.3125 | 123.4497 | -61.5417 | 61.6196 | 0.062332 | -0.067994 | 0.006315 | -0.043331 | 0.059155 | 0.026064 | -0.067295 | 61.5188 | 61.4079 | 61.3585 | 60.955 | 61.5697 | 61.7081 | 61.2437 | 61.3993 | 61.6041 | 61.4738 | 61.5481 | 61.4984 | 61.6009 | 61.5678 | 61.4745 | 61.5188 | 61.4079 | 61.3585 | 60.955 | 61.5697 | 61.7081 | 61.2437 | 61.3993 | -0.050941 | 0.27513 | -0.21125 | 0.11482
123.9844 | 123.2986 | -61.615 | 61.6196 | 0.057754 | -0.054257 | 0.006315 | -0.038752 | 0.06831 | 0.039799 | -0.058139 | 61.5417 | 61.4033 | 61.3722 | 60.9596 | 61.5651 | 61.7081 | 61.2345 | 61.3993 | 61.6727 | 61.5607 | 61.6213 | 61.5762 | 61.6833 | 61.6548 | 61.5569 | 61.5417 | 61.4033 | 61.3722 | 60.9596 | 61.5651 | 61.7081 | 61.2345 | 61.3993 | -0.023471 | 0.30718 | -0.19294 | 0.13771
125.6875 | 123.4314 | -61.5692 | 61.5784 | 0.062332 | -0.054257 | 0.010893 | -0.043331 | 0.063733 | 0.035221 | -0.067295 | 61.5234 | 61.4079 | 61.3859 | 60.9642 | 61.5651 | 61.7035 | 61.2391 | 61.3947 | 61.6315 | 61.515 | 61.5801 | 61.5259 | 61.6329 | 61.6044 | 61.5019 | 61.5234 | 61.4079 | 61.3859 | 60.9642 | 61.5651 | 61.7035 | 61.2391 | 61.3947 | -0.041785 | 0.28428 | -0.1792 | 0.14686
127.3594 | 123.2986 | -61.5555 | 61.6653 | 0.06691 | -0.058836 | 0.006315 | -0.047909 | 0.059155 | 0.035221 | -0.062717 | 61.5371 | 61.4216 | 61.3722 | 60.9688 | 61.5697 | 61.6989 | 61.2391 | 61.3947 | 61.6224 | 61.4966 | 61.5618 | 61.5076 | 61.6146 | 61.5907 | 61.4928 | 61.5371 | 61.4216 | 61.3722 | 60.9688 | 61.5697 | 61.6989 | 61.2391 | 61.3947 | -0.032627 | 0.29802 | -0.19752 | 0.13313
129.0312 | 123.3261 | -61.5967 | 61.6379 | 0.057754 | -0.054257 | 0.010893 | -0.047909 | 0.063733 | 0.026064 | -0.062717 | 61.5142 | 61.4216 | 61.3905 | 60.9688 | 61.556 | 61.6943 | 61.2299 | 61.3901 | 61.6544 | 61.5424 | 61.6076 | 61.5488 | 61.6604 | 61.6227 | 61.534 | 61.5142 | 61.4216 | 61.3905 | 60.9688 | 61.556 | 61.6943 | 61.2299 | 61.3901 | -0.041786 | 0.28428 | -0.16547 | 0.1606
130.75 | 123.3856 | -61.528 | 61.647 | 0.057754 | -0.063415 | 0.006315 | -0.043331 | 0.06831 | 0.030642 | -0.071874 | 61.5371 | 61.4171 | 61.3585 | 60.9733 | 61.5377 | 61.6943 | 61.2253 | 61.3764 | 61.5858 | 61.4646 | 61.5343 | 61.4847 | 61.5963 | 61.5587 | 61.4561 | 61.5371 | 61.4171 | 61.3585 | 60.9733 | 61.5377 | 61.6943 | 61.2253 | 61.3764 | -0.00058 | 0.31176 | -0.17921 | 0.13313
132.4219 | 123.3307 | -61.5921 | 61.6791 | 0.062332 | -0.058836 | 0.010893 | -0.038752 | 0.063733 | 0.035221 | -0.067295 | 61.5691 | 61.4262 | 61.3997 | 60.9733 | 61.5423 | 61.676 | 61.2208 | 61.3856 | 61.6544 | 61.5333 | 61.603 | 61.5533 | 61.6558 | 61.6273 | 61.5248 | 61.5691 | 61.4262 | 61.3997 | 60.9733 | 61.5423 | 61.676 | 61.2208 | 61.3856 | 0.026891 | 0.34838 | -0.14258 | 0.17891
134.125 | 123.2849 | -61.5372 | 61.6974 | 0.048597 | -0.063415 | 0.006315 | -0.043331 | 0.063733 | 0.035221 | -0.062717 | 61.5737 | 61.4308 | 61.4409 | 60.9779 | 61.5377 | 61.6669 | 61.207 | 61.3672 | 61.5858 | 61.4738 | 61.5435 | 61.4938 | 61.6009 | 61.5724 | 61.4745 | 61.5737 | 61.4308 | 61.4409 | 60.9779 | 61.5377 | 61.6669 | 61.207 | 61.3672 | 0.036048 | 0.3667 | -0.096796 | 0.23385
135.8438 | 123.2849 | -61.5509 | 61.7065 | 0.057754 | -0.063415 | 0.006315 | -0.034174 | 0.059155 | 0.035221 | -0.062717 | 61.592 | 61.4399 | 61.3493 | 60.9917 | 61.5285 | 61.6623 | 61.1979 | 61.3581 | 61.6087 | 61.4875 | 61.5572 | 61.5167 | 61.6101 | 61.5861 | 61.4882 | 61.592 | 61.4399 | 61.3493 | 60.9917 | 61.5285 | 61.6623 | 61.1979 | 61.3581 | 0.063518 | 0.39417 | -0.17921 | 0.15144
137.5312 | 123.2574 | -61.5829 | 61.6699 | 0.057754 | -0.063415 | 0.006315 | -0.034174 | 0.06831 | 0.039799 | -0.062717 | 61.592 | 61.4491 | 61.4043 | 61.0008 | 61.5056 | 61.6486 | 61.1887 | 61.3443 | 61.6407 | 61.5195 | 61.5893 | 61.5488 | 61.6513 | 61.6227 | 61.5202 | 61.592 | 61.4491 | 61.4043 | 61.0008 | 61.5056 | 61.6486 | 61.1887 | 61.3443 | 0.086409 | 0.40332 | -0.10138 | 0.21554
139.2031 | 123.3582 | -61.4914 | 61.6882 | 0.048597 | -0.063415 | 0.010893 | -0.038752 | 0.063733 | 0.030642 | -0.062717 | 61.5966 | 61.4583 | 61.4134 | 61.0054 | 61.5056 | 61.6394 | 61.1704 | 61.3352 | 61.54 | 61.428 | 61.5023 | 61.4526 | 61.5551 | 61.522 | 61.4287 | 61.5966 | 61.4583 | 61.4134 | 61.0054 | 61.5056 | 61.6394 | 61.1704 | 61.3352 | 0.090987 | 0.42622 | -0.092219 | 0.24301
140.875 | 123.2712 | -61.4822 | 61.7523 | 0.057754 | -0.058836 | 0.010893 | -0.038752 | 0.059155 | 0.039799 | -0.067295 | 61.592 | 61.4766 | 61.4409 | 61.0237 | 61.4965 | 61.6257 | 61.1567 | 61.3215 | 61.54 | 61.4234 | 61.4931 | 61.4435 | 61.5414 | 61.522 | 61.4149 | 61.592 | 61.4766 | 61.4409 | 61.0237 | 61.4965 | 61.6257 | 61.1567 | 61.3215 | 0.095565 | 0.43537 | -0.055593 | 0.28421
142.5469 | 123.3582 | -61.4548 | 61.7157 | 0.057754 | -0.063415 | 0.001736 | -0.043331 | 0.063733 | 0.026064 | -0.071874 | 61.6195 | 61.4812 | 61.4226 | 61.0374 | 61.4782 | 61.6074 | 61.1429 | 61.3031 | 61.5125 | 61.3914 | 61.4565 | 61.4114 | 61.5185 | 61.4808 | 61.3829 | 61.6195 | 61.4812 | 61.4226 | 61.0374 | 61.4782 | 61.6074 | 61.1429 | 61.3031 | 0.14135 | 0.47658 | -0.055593 | 0.27964
144.2031 | 123.2666 | -61.496 | 61.7249 | 0.062332 | -0.058836 | 0.001736 | -0.043331 | 0.059155 | 0.030642 | -0.058139 | 61.6195 | 61.4949 | 61.418 | 61.0466 | 61.4599 | 61.5936 | 61.1292 | 61.2894 | 61.5583 | 61.4371 | 61.4977 | 61.4526 | 61.5551 | 61.5266 | 61.4378 | 61.6195 | 61.4949 | 61.418 | 61.0466 | 61.4599 | 61.5936 | 61.1292 | 61.2894 | 0.15966 | 0.49031 | -0.041859 | 0.28879
145.875 | 123.3765 | -61.4273 | 61.7157 | 0.048597 | -0.063415 | 0.006315 | -0.038752 | 0.063733 | 0.030642 | -0.062717 | 61.6424 | 61.504 | 61.3951 | 61.0649 | 61.4553 | 61.5845 | 61.1246 | 61.2757 | 61.4759 | 61.3639 | 61.4336 | 61.3886 | 61.491 | 61.4579 | 61.3646 | 61.6424 | 61.504 | 61.3951 | 61.0649 | 61.4553 | 61.5845 | 61.1246 | 61.2757 | 0.18713 | 0.51778 | -0.060172 | 0.27048
147.5469 | 123.317 | -61.4365 | 61.7477 | 0.053175 | -0.063415 | 0.010893 | -0.034174 | 0.059155 | 0.035221 | -0.062717 | 61.6241 | 61.5269 | 61.4134 | 61.0649 | 61.437 | 61.5707 | 61.1109 | 61.2619 | 61.4896 | 61.373 | 61.4474 | 61.4023 | 61.4956 | 61.4717 | 61.3737 | 61.6241 | 61.5269 | 61.4134 | 61.0649 | 61.437 | 61.5707 | 61.1109 | 61.2619 | 0.18713 | 0.51321 | -0.023546 | 0.30253
149.25 | 123.262 | -61.4639 | 61.7569 | 0.06691 | -0.054257 | 0.010893 | -0.043331 | 0.063733 | 0.044377 | -0.062717 | 61.6378 | 61.5315 | 61.5233 | 61.0787 | 61.4232 | 61.5616 | 61.0971 | 61.2482 | 61.5308 | 61.4097 | 61.4748 | 61.4206 | 61.5277 | 61.5083 | 61.4012 | 61.6378 | 61.5315 | 61.5233 | 61.0787 | 61.4232 | 61.5616 | 61.0971 | 61.2482 | 0.2146 | 0.54068 | 0.10007 | 0.42614
150.9844 | 123.2803 | -61.409 | 61.8301 | 0.057754 | -0.054257 | 0.006315 | -0.034174 | 0.063733 | 0.035221 | -0.058139 | 61.6699 | 61.5498 | 61.505 | 61.0878 | 61.4095 | 61.5478 | 61.0743 | 61.2391 | 61.4668 | 61.3547 | 61.4153 | 61.3748 | 61.4727 | 61.4442 | 61.3509 | 61.6699 | 61.5498 | 61.505 | 61.0878 | 61.4095 | 61.5478 | 61.0743 | 61.2391 | 0.26038 | 0.59562 | 0.095489 | 0.43072
152.6875 | 123.3307 | -61.3586 | 61.7798 | 0.062332 | -0.054257 | 0.010893 | -0.052488 | 0.063733 | 0.035221 | -0.067295 | 61.6836 | 61.5453 | 61.5279 | 61.097 | 61.3958 | 61.5387 | 61.0743 | 61.2299 | 61.421 | 61.3044 | 61.3695 | 61.3062 | 61.4224 | 61.3939 | 61.2913 | 61.6836 | 61.5453 | 61.5279 | 61.097 | 61.3958 | 61.5387 | 61.0743 | 61.2299 | 0.28785 | 0.60935 | 0.13211 | 0.45361
154.3594 | 123.3398 | -61.4319 | 61.7065 | 0.057754 | -0.0451 | 0.006315 | -0.043331 | 0.054577 | 0.030642 | -0.071874 | 61.6424 | 61.5315 | 61.4546 | 61.1244 | 61.4186 | 61.5478 | 61.0834 | 61.2436 | 61.4896 | 61.3868 | 61.4382 | 61.3886 | 61.4865 | 61.4625 | 61.36 | 61.6424 | 61.5315 | 61.4546 | 61.1244 | 61.4186 | 61.5478 | 61.0834 | 61.2436 | 0.22376 | 0.55899 | 0.035971 | 0.3712
156.0625 | 123.1293 | -69.4244 | 54.538 | 0.071489 | -0.067994 | 0.001736 | -0.043331 | 0.072888 | 0.035221 | -0.076452 | 55.9834 | 55.8217 | 55.9195 | 55.7075 | 67.352 | 67.2933 | 66.9621 | 67.0945 | 69.4959 | 69.3564 | 69.4262 | 69.3811 | 69.4973 | 69.4597 | 69.348 | 55.9834 | 55.8217 | 55.9195 | 55.7075 | 67.352 | 67.2933 | 66.9621 | 67.0945 | -11.3686 | -10.9787 | -11.4325 | -11.0426
157.7656 | 123.381 | -119.0414 | 4.1428 | 0.057754 | -0.067994 | 0.001736 | -0.038752 | 0.059155 | 0.035221 | -0.067295 | 4.457 | 4.4703 | 4.4184 | 4.3582 | 118.8381 | 118.8378 | 118.5697 | 118.6493 | 119.0992 | 118.9734 | 119.0432 | 119.0027 | 119.1006 | 119.0767 | 118.9741 | 4.457 | 4.4703 | 4.4184 | 4.3582 | 118.8381 | 118.8378 | 118.5697 | 118.6493 | -114.3811 | -114.1127 | -114.4197 | -114.1513
159.4531 | 123.3124 | -119.3069 | 3.9185 | 0.053175 | -0.049678 | 0.006315 | -0.038752 | 0.054577 | 0.030642 | -0.067295 | 3.8481 | 3.898 | 3.6996 | 3.7812 | 119.5523 | 119.5199 | 119.2427 | 119.3819 | 119.3601 | 119.2573 | 119.3133 | 119.2682 | 119.3615 | 119.3376 | 119.2397 | 3.8481 | 3.898 | 3.6996 | 3.7812 | 119.5523 | 119.5199 | 119.2427 | 119.3819 | -115.7042 | -115.3946 | -115.8527 | -115.5431
161.125 | 123.3078 | -120.195 | 3.0899 | 0.048597 | -0.054257 | 0.006315 | -0.043331 | 0.063733 | 0.035221 | -0.067295 | 3.262 | 3.3119 | 3.0541 | 2.6502 | 120.1383 | 120.1059 | 119.6364 | 119.9633 | 120.2436 | 120.1407 | 120.2013 | 120.1517 | 120.2587 | 120.2302 | 120.1277 | 3.262 | 3.3119 | 3.0541 | 2.6502 | 120.1383 | 120.1059 | 119.6364 | 119.9633 | -116.8763 | -116.3744 | -117.0842 | -116.5823
162.7969 | 123.2758 | -119.4122 | 3.8544 | 0.053175 | -0.063415 | 0.015472 | -0.043331 | 0.059155 | 0.035221 | -0.058139 | 3.8297 | 3.6827 | 3.6492 | 3.218 | 119.36 | 119.5382 | 119.0641 | 119.4047 | 119.4654 | 119.3488 | 119.4277 | 119.3689 | 119.4714 | 119.4475 | 119.3541 | 3.8297 | 3.6827 | 3.6492 | 3.218 | 119.36 | 119.5382 | 119.0641 | 119.4047 | -115.5303 | -115.2344 | -115.7108 | -115.4149
164.5312 | 123.3078 | -118.9636 | 4.2892 | 0.053175 | -0.063415 | 0.010893 | -0.038752 | 0.059155 | 0.035221 | -0.067295 | 4.718 | 4.5665 | 4.5283 | 4.0926 | 118.4673 | 118.6455 | 118.1713 | 118.5028 | 119.0168 | 118.9002 | 118.9745 | 118.9249 | 119.0228 | 118.9988 | 118.8963 | 4.718 | 4.5665 | 4.5283 | 4.0926 | 118.4673 | 118.6455 | 118.1713 | 118.5028 | -113.7493 | -113.4534 | -113.939 | -113.6431
166.2031 | 123.4497 | -119.7784 | 3.3783 | 0.057754 | -0.058836 | 0.006315 | -0.034174 | 0.059155 | 0.039799 | -0.067295 | 3.8847 | 3.9163 | 3.8461 | 3.8087 | 119.5019 | 119.4741 | 119.1969 | 119.3269 | 119.8362 | 119.7196 | 119.7848 | 119.7443 | 119.8376 | 119.8182 | 119.7111 | 3.8847 | 3.9163 | 3.8461 | 3.8087 | 119.5019 | 119.4741 | 119.1969 | 119.3269 | -115.6172 | -115.3122 | -115.6558 | -115.3508
167.8906 | 123.2254 | -57.3853 | 65.5838 | 0.080646 | -0.049678 | 0.015472 | -0.029595 | 0.082044 | 0.053534 | -0.067295 | 66.3583 | 66.3622 | 66.3213 | 66.253 | 56.9732 | 56.9011 | 56.6241 | 56.7845 | 57.4659 | 57.3356 | 57.4007 | 57.3557 | 57.4673 | 57.4388 | 57.318 | 66.3583 | 66.3622 | 66.3213 | 66.253 | 56.9732 | 56.9011 | 56.6241 | 56.7845 | 9.385 | 9.7342 | 9.3481 | 9.6973
169.5625 | 123.4589 | -118.7485 | 4.3579 | 0.080646 | -0.067994 | 0.015472 | -0.034174 | 0.063733 | 0.026064 | -0.062717 | 4.3929 | 4.4291 | 4.3589 | 4.3216 | 118.98 | 118.9568 | 118.6933 | 118.8142 | 118.8291 | 118.6805 | 118.7639 | 118.7143 | 118.8122 | 118.7745 | 118.6858 | 4.3929 | 4.4291 | 4.3589 | 4.3216 | 118.98 | 118.9568 | 118.6933 | 118.8142 | -114.5871 | -114.3004 | -114.6211 | -114.3344
171.25 | 123.3032 | -118.6661 | 4.5044 | 0.048597 | -0.067994 | 0.006315 | -0.038752 | 0.072888 | 0.030642 | -0.062717 | 4.5898 | 4.626 | 4.5557 | 4.5139 | 118.7923 | 118.7508 | 118.4918 | 118.6219 | 118.7147 | 118.5981 | 118.6724 | 118.6273 | 118.739 | 118.6967 | 118.6034 | 4.5898 | 4.626 | 4.5557 | 4.5139 | 118.7923 | 118.7508 | 118.4918 | 118.6219 | -114.2025 | -113.902 | -114.2366 | -113.9361
173 | 123.3078 | -118.8354 | 4.3762 | 0.053175 | -0.0451 | 0.006315 | -0.038752 | 0.06831 | 0.035221 | -0.067295 | 4.3883 | 4.4428 | 4.2124 | 3.7675 | 118.9754 | 118.9431 | 118.4598 | 118.8096 | 118.8886 | 118.7903 | 118.8418 | 118.7967 | 118.9038 | 118.8707 | 118.7682 | 4.3883 | 4.4428 | 4.2124 | 3.7675 | 118.9754 | 118.9431 | 118.4598 | 118.8096 | -114.5871 | -114.0714 | -114.7631 | -114.2474
174.6719 | 123.2803 | -118.9911 | 4.2709 | 0.062332 | -0.054257 | 0.006315 | -0.038752 | 0.059155 | 0.030642 | -0.067295 | 4.2647 | 4.3192 | 4.0842 | 3.6484 | 119.1036 | 119.0712 | 118.5925 | 118.9332 | 119.0534 | 118.9368 | 118.9974 | 118.9523 | 119.0502 | 119.0217 | 118.9238 | 4.2647 | 4.3192 | 4.0842 | 3.6484 | 119.1036 | 119.0712 | 118.5925 | 118.9332 | -114.8389 | -114.3278 | -115.0194 | -114.5084
176.3438 | 123.2986 | -118.8675 | 4.3716 | 0.057754 | -0.058836 | 0.010893 | -0.038752 | 0.06831 | 0.035221 | -0.062717 | 4.5394 | 4.4062 | 4.3635 | 3.9323 | 118.6138 | 118.7782 | 118.3224 | 118.6493 | 118.9252 | 118.8087 | 118.8784 | 118.8287 | 118.9358 | 118.9027 | 118.8048 | 4.5394 | 4.4062 | 4.3635 | 3.9323 | 118.6138 | 118.7782 | 118.3224 | 118.6493 | -114.0744 | -113.783 | -114.2503 | -113.959
178.0469 | 123.3078 | -119.1055 | 4.129 | 0.062332 | -0.058836 | 0.010893 | -0.043331 | 0.06831 | 0.030642 | -0.062717 | 4.2372 | 4.0811 | 4.0567 | 3.6255 | 118.9159 | 119.0896 | 118.62 | 118.9607 | 119.1679 | 119.0467 | 119.1164 | 119.0622 | 119.1738 | 119.1362 | 119.0428 | 4.2372 | 4.0811 | 4.0567 | 3.6255 | 118.9159 | 119.0896 | 118.62 | 118.9607 | -114.6787 | -114.3828 | -114.8592 | -114.5633
179.7188 | 123.4131 | -118.7576 | 4.4128 | 0.057754 | -0.049678 | 0.006315 | -0.043331 | 0.063733 | 0.026064 | -0.076452 | 4.5028 | 4.3467 | 4.2902 | 3.8866 | 118.6412 | 118.824 | 118.3453 | 118.6905 | 118.8154 | 118.708 | 118.7639 | 118.7143 | 118.8214 | 118.7837 | 118.6812 | 4.5028 | 4.3467 | 4.2902 | 3.8866 | 118.6412 | 118.824 | 118.3453 | 118.6905 | -114.1384 | -113.8425 | -114.351 | -114.0551
181.3906 | 123.3124 | -119.3802 | 3.7903 | 0.053175 | -0.058836 | 0.001736 | -0.047909 | 0.06831 | 0.026064 | -0.071874 | 3.9351 | 3.7835 | 3.75 | 3.3233 | 119.2089 | 119.3871 | 118.9085 | 119.2491 | 119.4334 | 119.3214 | 119.3819 | 119.3323 | 119.4485 | 119.4063 | 119.3083 | 3.9351 | 3.7835 | 3.75 | 3.3233 | 119.2089 | 119.3871 | 118.9085 | 119.2491 | -115.2739 | -114.9734 | -115.459 | -115.1585
183.0781 | 123.349 | -119.0735 | 4.1199 | 0.048597 | -0.054257 | 0.001736 | -0.043331 | 0.063733 | 0.039799 | -0.062717 | 4.0953 | 3.9483 | 3.9056 | 3.4836 | 119.0395 | 119.2132 | 118.7345 | 118.8737 | 119.1221 | 119.0192 | 119.0752 | 119.0302 | 119.1372 | 119.1133 | 119.0108 | 4.0953 | 3.9483 | 3.9056 | 3.4836 | 119.0395 | 119.2132 | 118.7345 | 118.8737 | -114.9442 | -114.6392 | -115.1339 | -114.8288
184.75 | 123.2712 | -119.2154 | 4.01 | 0.057754 | -0.054257 | 0.010893 | -0.034174 | 0.063733 | 0.035221 | -0.062717 | 3.6512 | 3.5179 | 3.4661 | 3.0486 | 119.4836 | 119.6572 | 119.1877 | 119.3132 | 119.2731 | 119.1611 | 119.2263 | 119.1812 | 119.2791 | 119.2506 | 119.1527 | 3.6512 | 3.5179 | 3.4661 | 3.0486 | 119.4836 | 119.6572 | 119.1877 | 119.3132 | -115.8324 | -115.5366 | -116.0175 | -115.7216
186.4219 | 123.2712 | -119.2657 | 3.9276 | 0.057754 | -0.054257 | 0.006315 | -0.034174 | 0.059155 | 0.026064 | -0.062717 | 4.0678 | 3.9208 | 3.8827 | 3.4424 | 119.0807 | 119.2452 | 118.7848 | 118.9057 | 119.3235 | 119.2115 | 119.2721 | 119.2316 | 119.3249 | 119.2918 | 119.203 | 4.0678 | 3.9208 | 3.8827 | 3.4424 | 119.0807 | 119.2452 | 118.7848 | 118.9057 | -115.0129 | -114.717 | -115.198 | -114.9021
188.0938 | 123.2346 | -119.2657 | 3.9459 | 0.057754 | -0.058836 | 0.010893 | -0.038752 | 0.063733 | 0.035221 | -0.067295 | 3.9213 | 3.7789 | 3.75 | 3.3188 | 119.2181 | 119.3871 | 118.913 | 119.0431 | 119.3235 | 119.2069 | 119.2766 | 119.227 | 119.3295 | 119.301 | 119.1985 | 3.9213 | 3.7789 | 3.75 | 3.3188 | 119.2181 | 119.3871 | 118.913 | 119.0431 | -115.2968 | -114.9917 | -115.4681 | -115.1631
189.7656 | 123.2986 | -119.1513 | 4.0146 | 0.057754 | -0.067994 | 0.006315 | -0.047909 | 0.063733 | 0.026064 | -0.071874 | 4.0404 | 3.898 | 3.8644 | 3.4286 | 119.0807 | 119.2635 | 118.794 | 118.9378 | 119.2091 | 119.0833 | 119.1576 | 119.1034 | 119.215 | 119.1774 | 119.0794 | 4.0404 | 3.898 | 3.8644 | 3.4286 | 119.0807 | 119.2635 | 118.794 | 118.9378 | -115.0404 | -114.7536 | -115.2163 | -114.9296
191.4375 | 123.4039 | -122.2916 | 0.79193 | 0.057754 | -0.054257 | 0.010893 | -0.043331 | 0.063733 | 0.030642 | -0.062717 | 0.80794 | 0.86677 | 0.77409 | 0.74076 | 122.551 | 122.5231 | 122.2598 | 122.3943 | 122.3493 | 122.2373 | 122.3025 | 122.2482 | 122.3553 | 122.3222 | 122.2288 | 0.80794 | 0.86677 | 0.77409 | 0.74076 | 122.551 | 122.5231 | 122.2598 | 122.3943 | -121.7431 | -121.4519 | -121.7769 | -121.4857
193.1562 | 123.262 | -122.3099 | 0.92468 | 0.062332 | -0.054257 | 0.006315 | -0.043331 | 0.06831 | 0.030642 | -0.062717 | 0.89035 | 0.94919 | 0.55891 | 0.30117 | 122.4686 | 122.4407 | 121.9577 | 122.2981 | 122.3722 | 122.2556 | 122.3162 | 122.2665 | 122.3782 | 122.3405 | 122.2472 | 0.89035 | 0.94919 | 0.55891 | 0.30117 | 122.4686 | 122.4407 | 121.9577 | 122.2981 | -121.5782 | -121.0673 | -121.9097 | -121.3988
194.9688 | 123.3994 | -122.2092 | 0.95673 | 0.06691 | -0.058836 | 0.010893 | -0.047909 | 0.063733 | 0.039799 | -0.062717 | 0.94072 | 0.99498 | 0.65048 | 0.31949 | 122.2031 | 122.4087 | 121.921 | 122.2707 | 122.2761 | 122.1503 | 122.2201 | 122.1613 | 122.2729 | 122.249 | 122.1464 | 0.94072 | 0.99498 | 0.65048 | 0.31949 | 122.2031 | 122.4087 | 121.921 | 122.2707 | -121.2623 | -120.9803 | -121.5526 | -121.2706
196.7031 | 123.3765 | -122.1451 | 1.0254 | 0.053175 | -0.058836 | 0.001736 | -0.038752 | 0.072888 | 0.026064 | -0.062717 | 1.0369 | 0.88509 | 0.74662 | 0.40649 | 122.1252 | 122.3125 | 121.8386 | 122.1791 | 122.1983 | 122.0862 | 122.1468 | 122.1063 | 122.218 | 122.1711 | 122.0824 | 1.0369 | 0.88509 | 0.74662 | 0.40649 | 122.1252 | 122.3125 | 121.8386 | 122.1791 | -121.0884 | -120.8018 | -121.3786 | -121.092
198.3906 | 123.2666 | -122.3328 | 0.92926 | 0.06691 | -0.054257 | 0.010893 | -0.034174 | 0.06831 | 0.035221 | -0.067295 | 0.89493 | 0.74772 | 0.56807 | 0.26911 | 122.2717 | 122.4544 | 121.976 | 122.1059 | 122.3997 | 122.2785 | 122.3437 | 122.2986 | 122.4011 | 122.368 | 122.2655 | 0.89493 | 0.74772 | 0.56807 | 0.26911 | 122.2717 | 122.4544 | 121.976 | 122.1059 | -121.3768 | -121.081 | -121.7037 | -121.4079
200.125 | 123.2758 | -122.2549 | 0.99335 | 0.057754 | -0.058836 | 0.006315 | -0.038752 | 0.063733 | 0.035221 | -0.062717 | 0.99566 | 0.84388 | 0.66879 | 0.37443 | 122.1756 | 122.3491 | 121.889 | 122.0143 | 122.3127 | 122.1961 | 122.2613 | 122.2162 | 122.3187 | 122.2902 | 122.1922 | 0.99566 | 0.84388 | 0.66879 | 0.37443 | 122.1756 | 122.3491 | 121.889 | 122.0143 | -121.1799 | -120.8933 | -121.5068 | -121.2202
201.8438 | 123.381 | -122.374 | 0.82855 | 0.053175 | -0.049678 | 0.006315 | -0.038752 | 0.06831 | 0.039799 | -0.067295 | 0.83999 | 0.6882 | 0.5406 | 0.20959 | 122.3267 | 122.5185 | 122.0355 | 122.1654 | 122.4271 | 122.3243 | 122.3803 | 122.3352 | 122.4423 | 122.4138 | 122.3067 | 0.83999 | 0.6882 | 0.5406 | 0.20959 | 122.3267 | 122.5185 | 122.0355 | 122.1654 | -121.4867 | -121.1955 | -121.7861 | -121.4949
203.5781 | 123.2529 | -122.3602 | 0.94757 | 0.053175 | -0.054257 | 0.006315 | -0.043331 | 0.063733 | 0.039799 | -0.062717 | 0.84457 | 0.71109 | 0.53602 | 0.23248 | 122.3175 | 122.5002 | 122.0263 | 122.1516 | 122.4134 | 122.306 | 122.3665 | 122.3169 | 122.424 | 122.4 | 122.2975 | 0.84457 | 0.71109 | 0.53602 | 0.23248 | 122.3175 | 122.5002 | 122.0263 | 122.1516 | -121.4729 | -121.1818 | -121.7815 | -121.4903
205.25 | 123.3582 | -122.3328 | 0.86975 | 0.062332 | -0.058836 | 0.006315 | -0.038752 | 0.063733 | 0.030642 | -0.067295 | 0.89951 | 0.76604 | 0.62758 | 0.28285 | 122.2809 | 122.4453 | 121.9806 | 122.1104 | 122.3951 | 122.2739 | 122.3391 | 122.294 | 122.3965 | 122.3634 | 122.2655 | 0.89951 | 0.76604 | 0.62758 | 0.28285 | 122.2809 | 122.4453 | 121.9806 | 122.1104 | -121.3814 | -121.081 | -121.6533 | -121.353
206.9844 | 123.2895 | -122.3831 | 0.89264 | 0.053175 | -0.058836 | 0.010893 | -0.034174 | 0.072888 | 0.030642 | -0.062717 | 0.86288 | 0.72941 | 0.55433 | 0.24622 | 122.3129 | 122.4865 | 122.0126 | 122.1425 | 122.4363 | 122.3243 | 122.394 | 122.3489 | 122.456 | 122.4138 | 122.3204 | 0.86288 | 0.72941 | 0.55433 | 0.24622 | 122.3129 | 122.4865 | 122.0126 | 122.1425 | -121.45 | -121.1497 | -121.7586 | -121.4583
208.7188 | 123.317 | -122.3053 | 0.91553 | 0.057754 | -0.058836 | 0.010893 | -0.038752 | 0.063733 | 0.026064 | -0.071874 | 0.93156 | 0.77978 | 0.5818 | 0.30575 | 122.2443 | 122.4178 | 121.9577 | 122.0738 | 122.3631 | 122.2465 | 122.3162 | 122.2665 | 122.369 | 122.3314 | 122.2334 | 0.93156 | 0.77978 | 0.5818 | 0.30575 | 122.2443 | 122.4178 | 121.9577 | 122.0738 | -121.3127 | -121.0261 | -121.6625 | -121.3759
210.4531 | 123.3536 | -122.2321 | 0.97046 | 0.06691 | -0.054257 | 0.006315 | -0.038752 | 0.063733 | 0.035221 | -0.062717 | 0.96819 | 0.81641 | 0.71915 | 0.34696 | 122.2122 | 122.3858 | 121.9119 | 122.0326 | 122.299 | 122.1778 | 122.2384 | 122.1933 | 122.2958 | 122.2673 | 122.1693 | 0.96819 | 0.81641 | 0.71915 | 0.34696 | 122.2122 | 122.3858 | 121.9119 | 122.0326 | -121.244 | -120.9437 | -121.4931 | -121.1927
212.1094 | 123.2437 | -122.2412 | 1.03 | 0.062332 | -0.054257 | 0.010893 | -0.043331 | 0.063733 | 0.026064 | -0.067295 | 1.0002 | 0.85762 | 0.73746 | 0.38359 | 122.1664 | 122.3446 | 121.8707 | 122.0051 | 122.3035 | 122.187 | 122.2521 | 122.1979 | 122.3049 | 122.2673 | 122.1739 | 1.0002 | 0.85762 | 0.73746 | 0.38359 | 122.1664 | 122.3446 | 121.8707 | 122.0051 | -121.1662 | -120.8704 | -121.429 | -121.1332
213.7812 | 123.2941 | -121.6782 | 1.5976 | 0.062332 | -0.049678 | 0.010893 | -0.043331 | 0.063733 | 0.030642 | -0.058139 | 1.4947 | 1.3567 | 1.2182 | 0.8827 | 121.6857 | 121.8547 | 121.3899 | 121.5199 | 121.7405 | 121.6285 | 121.6891 | 121.6348 | 121.7419 | 121.7088 | 121.62 | 1.4947 | 1.3567 | 1.2182 | 0.8827 | 121.6857 | 121.8547 | 121.3899 | 121.5199 | -120.191 | -119.8952 | -120.4675 | -120.1718
215.4688 | 123.3994 | -121.6141 | 1.5564 | 0.053175 | -0.063415 | 0.001736 | -0.034174 | 0.059155 | 0.030642 | -0.067295 | 1.5863 | 1.4345 | 1.3876 | 0.95597 | 121.6079 | 121.7631 | 121.3075 | 121.4146 | 121.6672 | 121.5507 | 121.6158 | 121.5799 | 121.6732 | 121.6447 | 121.5468 | 1.5863 | 1.4345 | 1.3876 | 0.95597 | 121.6079 | 121.7631 | 121.3075 | 121.4146 | -120.0216 | -119.7212 | -120.2203 | -119.92
217.1406 | 123.3948 | -120.3369 | 2.7374 | 0.06691 | -0.054257 | 0.001736 | -0.038752 | 0.063733 | 0.030642 | -0.071874 | 2.7675 | 2.6159 | 2.5505 | 2.1511 | 120.3672 | 120.5362 | 120.0714 | 120.1968 | 120.4038 | 120.2827 | 120.3386 | 120.2982 | 120.4006 | 120.3676 | 120.265 | 2.7675 | 2.6159 | 2.5505 | 2.1511 | 120.3672 | 120.5362 | 120.0714 | 120.1968 | -117.5997 | -117.3038 | -117.8167 | -117.5209
218.8125 | 123.3261 | -120.6802 | 2.4216 | 0.06691 | -0.058836 | -0.002842 | -0.043331 | 0.06831 | 0.030642 | -0.062717 | 2.5203 | 2.3686 | 2.3215 | 1.9038 | 120.6373 | 120.7606 | 120.314 | 120.4303 | 120.7471 | 120.6214 | 120.6774 | 120.6369 | 120.7485 | 120.7109 | 120.6175 | 2.5203 | 2.3686 | 2.3215 | 1.9038 | 120.6373 | 120.7606 | 120.314 | 120.4303 | -118.117 | -117.7937 | -118.3158 | -117.9925
220.5625 | 123.1979 | -120.8771 | 2.2797 | 0.053175 | -0.063415 | 0.010893 | -0.034174 | 0.063733 | 0.044377 | -0.058139 | 2.3005 | 2.1488 | 2.1201 | 1.6795 | 120.7976 | 120.9528 | 120.5017 | 120.6271 | 120.9303 | 120.8137 | 120.888 | 120.8429 | 120.9408 | 120.9215 | 120.8189 | 2.3005 | 2.1488 | 2.1201 | 1.6795 | 120.7976 | 120.9528 | 120.5017 | 120.6271 | -118.497 | -118.2012 | -118.6775 | -118.3816
222.2188 | 123.1796 | -120.5109 | 2.6688 | 0.062332 | -0.058836 | 0.006315 | -0.034174 | 0.06831 | 0.035221 | -0.058139 | 2.5844 | 2.4465 | 2.3948 | 1.9863 | 120.4817 | 120.6553 | 120.195 | 120.3204 | 120.5732 | 120.452 | 120.5172 | 120.4767 | 120.5792 | 120.5461 | 120.4527 | 2.5844 | 2.4465 | 2.3948 | 1.9863 | 120.4817 | 120.6553 | 120.195 | 120.3204 | -117.8973 | -117.6106 | -118.0869 | -117.8002
223.9531 | 123.2803 | -120.7352 | 2.3071 | 0.057754 | -0.058836 | 0.001736 | -0.038752 | 0.06831 | 0.030642 | -0.062717 | 2.3417 | 2.1946 | 2.1476 | 1.7298 | 120.7197 | 120.8933 | 120.4193 | 120.5447 | 120.7929 | 120.6763 | 120.7369 | 120.6964 | 120.8035 | 120.7658 | 120.6725 | 2.3417 | 2.1946 | 2.1476 | 1.7298 | 120.7197 | 120.8933 | 120.4193 | 120.5447 | -118.378 | -118.0776 | -118.5722 | -118.2717
225.625 | 123.2483 | -120.7535 | 2.3529 | 0.062332 | -0.058836 | 0.001736 | -0.034174 | 0.06831 | 0.039799 | -0.062717 | 2.4058 | 2.245 | 2.2117 | 1.8031 | 120.6419 | 120.8109 | 120.3552 | 120.476 | 120.8158 | 120.6946 | 120.7552 | 120.7193 | 120.8218 | 120.7933 | 120.6908 | 2.4058 | 2.245 | 2.2117 | 1.8031 | 120.6419 | 120.8109 | 120.3552 | 120.476 | -118.2361 | -117.9494 | -118.4302 | -118.1436
227.3594 | 123.1659 | -120.5429 | 2.5726 | 0.057754 | -0.058836 | 0.010893 | -0.029595 | 0.06831 | 0.039799 | -0.058139 | 2.4928 | 2.3503 | 2.3078 | 1.8764 | 120.5503 | 120.7102 | 120.2499 | 120.3662 | 120.6007 | 120.4841 | 120.5538 | 120.5133 | 120.6112 | 120.5827 | 120.4848 | 2.4928 | 2.3503 | 2.3078 | 1.8764 | 120.5503 | 120.7102 | 120.2499 | 120.3662 | -118.0575 | -117.7571 | -118.2425 | -117.9421
229.0781 | 123.1018 | -120.9 | 2.2385 | 0.062332 | -0.058836 | 0.010893 | -0.043331 | 0.06831 | 0.035221 | -0.071874 | 2.0716 | 2.0618 | 1.9644 | 1.597 | 120.8296 | 120.994 | 120.5338 | 120.6592 | 120.9623 | 120.8411 | 120.9109 | 120.8566 | 120.9683 | 120.9352 | 120.8281 | 2.0716 | 2.0618 | 1.9644 | 1.597 | 120.8296 | 120.994 | 120.5338 | 120.6592 | -118.758 | -118.4622 | -118.8652 | -118.5693
230.75 | 123.1476 | -119.2978 | 3.598 | 0.085224 | -0.058836 | 0.010893 | -0.047909 | 0.077466 | 0.048956 | -0.076452 | 10.029 | 9.9191 | 9.9581 | 9.7843 | 113.2024 | 113.2205 | 112.9428 | 113.0136 | 119.383 | 119.239 | 119.3087 | 119.2499 | 119.3753 | 119.3467 | 119.2213 | 10.029 | 9.9191 | 9.9581 | 9.7843 | 113.2024 | 113.2205 | 112.9428 | 113.0136 | -103.1733 | -102.9138 | -103.2442 | -102.9847
232.4844 | 123.3032 | -118.515 | 4.4998 | 0.053175 | -0.058836 | 0.001736 | -0.038752 | 0.063733 | 0.030642 | -0.067295 | 4.457 | 4.5069 | 4.4367 | 4.4086 | 118.7832 | 118.7416 | 118.4827 | 118.6173 | 118.5682 | 118.4562 | 118.5168 | 118.4763 | 118.5787 | 118.5457 | 118.4477 | 4.457 | 4.5069 | 4.4367 | 4.4086 | 118.7832 | 118.7416 | 118.4827 | 118.6173 | -114.3262 | -114.0257 | -114.3464 | -114.046
234.2188 | 123.2025 | -118.1992 | 4.9164 | 0.062332 | -0.054257 | 0.015472 | -0.038752 | 0.06831 | 0.044377 | -0.062717 | 4.924 | 4.9831 | 4.8945 | 4.8619 | 118.3345 | 118.2976 | 118.0386 | 118.1641 | 118.2615 | 118.1449 | 118.2146 | 118.1604 | 118.2675 | 118.2435 | 118.1364 | 4.924 | 4.9831 | 4.8945 | 4.8619 | 118.3345 | 118.2976 | 118.0386 | 118.1641 | -113.4105 | -113.1146 | -113.44 | -113.144
235.9531 | 123.2025 | -118.2724 | 4.9026 | 0.057754 | -0.058836 | 0.006315 | -0.038752 | 0.063733 | 0.030642 | -0.062717 | 4.8736 | 4.9236 | 4.8488 | 4.8161 | 118.394 | 118.3571 | 118.1118 | 118.2327 | 118.3302 | 118.2136 | 118.2787 | 118.2336 | 118.3361 | 118.303 | 118.2097 | 4.8736 | 4.9236 | 4.8488 | 4.8161 | 118.394 | 118.3571 | 118.1118 | 118.2327 | -113.5204 | -113.2382 | -113.5453 | -113.2631
237.6875 | 123.2758 | -118.5745 | 4.5547 | 0.053175 | -0.058836 | 0.006315 | -0.038752 | 0.063733 | 0.035221 | -0.067295 | 4.5944 | 4.6443 | 4.423 | 4.5459 | 118.6824 | 118.6455 | 118.1805 | 118.5166 | 118.6277 | 118.5157 | 118.5808 | 118.5358 | 118.6383 | 118.6097 | 118.5072 | 4.5944 | 4.6443 | 4.423 | 4.5459 | 118.6824 | 118.6455 | 118.1805 | 118.5166 | -114.0881 | -113.5861 | -114.2595 | -113.7575
239.3594 | 123.2346 | -118.1763 | 5.0079 | 0.062332 | -0.054257 | 0.006315 | -0.038752 | 0.06831 | 0.039799 | -0.058139 | 4.5669 | 4.6214 | 4.3955 | 3.969 | 118.5085 | 118.6821 | 118.2171 | 118.5532 | 118.2386 | 118.122 | 118.1826 | 118.1375 | 118.2446 | 118.2161 | 118.1181 | 4.5669 | 4.6214 | 4.3955 | 3.969 | 118.5085 | 118.6821 | 118.2171 | 118.5532 | -113.9416 | -113.6502 | -114.113 | -113.8216
241.0938 | 123.2437 | -115.1825 | 7.9742 | 0.057754 | -0.058836 | 0.001736 | -0.043331 | 0.072888 | 0.030642 | -0.062717 | 7.9412 | 7.9868 | 7.756 | 7.3162 | 115.1298 | 115.3172 | 114.8337 | 115.1837 | 115.2402 | 115.1237 | 115.1842 | 115.1392 | 115.2554 | 115.2131 | 115.1198 | 7.9412 | 7.9868 | 7.756 | 7.3162 | 115.1298 | 115.3172 | 114.8337 | 115.1837 | -107.1885 | -106.8925 | -107.3738 | -107.0777
242.8438 | 123.2895 | -115.8142 | 7.2968 | 0.057754 | -0.058836 | 0.001736 | -0.038752 | 0.063733 | 0.030642 | -0.071874 | 7.3781 | 7.2268 | 7.2066 | 6.7713 | 115.7112 | 115.8803 | 115.406 | 115.7559 | 115.872 | 115.7554 | 115.8159 | 115.7755 | 115.8779 | 115.8449 | 115.7423 | 7.3781 | 7.2268 | 7.2066 | 6.7713 | 115.7112 | 115.8803 | 115.406 | 115.7559 | -108.3331 | -108.0279 | -108.5046 | -108.1994
244.5312 | 123.0469 | -94.7067 | 28.3997 | 0.057754 | -0.058836 | 0.006315 | -0.043331 | 0.063733 | 0.030642 | -0.067295 | 28.3522 | 28.1565 | 28.1385 | 27.6884 | 94.7249 | 94.8853 | 94.4095 | 94.7604 | 94.7645 | 94.6479 | 94.713 | 94.6634 | 94.7705 | 94.7374 | 94.6394 | 28.3522 | 28.1565 | 28.1385 | 27.6884 | 94.7249 | 94.8853 | 94.4095 | 94.7604 | -66.3727 | -66.0573 | -66.5864 | -66.271
246.2656 | 123.0331 | -94.6426 | 28.4454 | 0.057754 | -0.054257 | 0.010893 | -0.038752 | 0.072888 | 0.039799 | -0.062717 | 28.4483 | 28.2573 | 28.2392 | 27.7937 | 94.6241 | 94.7892 | 94.3225 | 94.6735 | 94.7004 | 94.5884 | 94.6535 | 94.6039 | 94.7155 | 94.6824 | 94.5799 | 28.4483 | 28.2573 | 28.2392 | 27.7937 | 94.6241 | 94.7892 | 94.3225 | 94.6735 | -66.1758 | -65.8742 | -66.3849 | -66.0833
248.0156 | 123.2986 | -94.5786 | 28.4821 | 0.06691 | -0.049678 | 0.001736 | -0.038752 | 0.06831 | 0.039799 | -0.062717 | 28.3247 | 28.1474 | 28.1339 | 27.8303 | 94.7752 | 94.9219 | 94.4644 | 94.6002 | 94.6455 | 94.5289 | 94.5803 | 94.5398 | 94.6469 | 94.6184 | 94.5158 | 28.3247 | 28.1474 | 28.1339 | 27.8303 | 94.7752 | 94.9219 | 94.4644 | 94.6002 | -66.4505 | -66.1397 | -66.6413 | -66.3305
249.6875 | 123.2986 | -94.4962 | 28.5828 | 0.053175 | -0.058836 | 0.006315 | -0.038752 | 0.063733 | 0.035221 | -0.062717 | 28.5811 | 28.3855 | 28.3903 | 27.9173 | 94.5097 | 94.6702 | 94.1897 | 94.3301 | 94.5493 | 94.4373 | 94.5025 | 94.4574 | 94.5599 | 94.5314 | 94.4334 | 28.5811 | 28.3855 | 28.3903 | 27.9173 | 94.5097 | 94.6702 | 94.1897 | 94.3301 | -65.9286 | -65.6086 | -66.1194 | -65.7995
251.4219 | 123.3215 | -117.0364 | 6.0471 | 0.057754 | -0.063415 | 0.010893 | -0.038752 | 0.072888 | 0.030642 | -0.067295 | 6.0778 | 6.1233 | 5.9018 | 5.4617 | 117.1213 | 117.2126 | 116.7429 | 117.0882 | 117.0942 | 116.973 | 117.0473 | 116.9977 | 117.1093 | 117.0671 | 116.9691 | 6.0778 | 6.1233 | 5.9018 | 5.4617 | 117.1213 | 117.2126 | 116.7429 | 117.0882 | -111.0435 | -110.6651 | -111.2195 | -110.8411
253.1719 | 123.2391 | -117.3935 | 5.7999 | 0.06691 | -0.054257 | 0.010893 | -0.038752 | 0.072888 | 0.021485 | -0.067295 | 5.7802 | 5.6425 | 5.6133 | 5.1687 | 117.3365 | 117.5147 | 117.0405 | 117.2118 | 117.4604 | 117.3392 | 117.4044 | 117.3547 | 117.4664 | 117.415 | 117.3262 | 5.7802 | 5.6425 | 5.6133 | 5.1687 | 117.3365 | 117.5147 | 117.0405 | 117.2118 | -111.5563 | -111.2603 | -111.7231 | -111.4271
254.9062 | 123.23 | -117.3065 | 5.8685 | 0.057754 | -0.054257 | 0.001736 | -0.034174 | 0.077466 | 0.039799 | -0.062717 | 5.8626 | 5.7066 | 5.6774 | 5.2419 | 117.2586 | 117.4415 | 116.9672 | 117.0882 | 117.3643 | 117.2523 | 117.3083 | 117.2723 | 117.384 | 117.3463 | 117.2438 | 5.8626 | 5.7066 | 5.6774 | 5.2419 | 117.2586 | 117.4415 | 116.9672 | 117.0882 | -111.396 | -111.1046 | -111.5812 | -111.2898
256.6094 | 123.2391 | -117.0914 | 6.102 | 0.062332 | -0.058836 | 0.010893 | -0.038752 | 0.06831 | 0.035221 | -0.058139 | 6.0824 | 5.9401 | 5.9109 | 5.4846 | 117.0206 | 117.2034 | 116.7383 | 116.8639 | 117.1537 | 117.0325 | 117.1023 | 117.0526 | 117.1597 | 117.1266 | 117.0332 | 6.0824 | 5.9401 | 5.9109 | 5.4846 | 117.0206 | 117.2034 | 116.7383 | 116.8639 | -110.9382 | -110.6559 | -111.1096 | -110.8274
258.2812 | 123.2483 | -117.1005 | 6.1295 | 0.06691 | -0.054257 | 0.001736 | -0.043331 | 0.06831 | 0.035221 | -0.067295 | 6.1648 | 6.0134 | 5.9933 | 5.5579 | 116.9519 | 117.1256 | 116.6696 | 116.7906 | 117.1674 | 117.0463 | 117.1023 | 117.0572 | 117.1688 | 117.1357 | 117.0332 | 6.1648 | 6.0134 | 5.9933 | 5.5579 | 116.9519 | 117.1256 | 116.6696 | 116.7906 | -110.7871 | -110.5048 | -110.9586 | -110.6763
260.0312 | 123.3444 | -117.0959 | 6.0516 | 0.057754 | -0.054257 | 0.006315 | -0.043331 | 0.06831 | 0.035221 | -0.067295 | 6.3891 | 6.2194 | 6.2131 | 5.7685 | 116.7367 | 116.9058 | 116.4407 | 116.5525 | 117.1537 | 117.0417 | 117.1023 | 117.0526 | 117.1643 | 117.1312 | 117.0287 | 6.3891 | 6.2194 | 6.2131 | 5.7685 | 116.7367 | 116.9058 | 116.4407 | 116.5525 | -110.3476 | -110.0516 | -110.5236 | -110.2276
261.7344 | 123.3032 | -116.1713 | 6.9901 | 0.057754 | -0.054257 | 0.001736 | -0.043331 | 0.06831 | 0.030642 | -0.071874 | 6.9569 | 6.7872 | 6.7808 | 6.3501 | 116.1599 | 116.3381 | 115.8684 | 116.0032 | 116.229 | 116.117 | 116.173 | 116.1279 | 116.2396 | 116.2019 | 116.0994 | 6.9569 | 6.7872 | 6.7808 | 6.3501 | 116.1599 | 116.3381 | 115.8684 | 116.0032 | -109.203 | -108.9115 | -109.3791 | -109.0876
263.4062 | 123.2529 | -116.8716 | 6.2942 | 0.062332 | -0.063415 | 0.006315 | -0.034174 | 0.072888 | 0.044377 | -0.067295 | 6.3021 | 6.137 | 6.1307 | 5.6861 | 116.8237 | 116.9882 | 116.5277 | 116.6487 | 116.934 | 116.8082 | 116.878 | 116.8375 | 116.9445 | 116.916 | 116.8043 | 6.3021 | 6.137 | 6.1307 | 5.6861 | 116.8237 | 116.9882 | 116.5277 | 116.6487 | -110.5216 | -110.2256 | -110.693 | -110.397
265.125 | 123.3582 | -116.1987 | 6.9397 | 0.057754 | -0.058836 | 0.010893 | -0.034174 | 0.06831 | 0.030642 | -0.067295 | 6.9019 | 6.7551 | 6.7213 | 6.2814 | 116.224 | 116.4022 | 115.9371 | 116.0627 | 116.2565 | 116.1399 | 116.2096 | 116.1646 | 116.267 | 116.2294 | 116.1314 | 6.9019 | 6.7551 | 6.7213 | 6.2814 | 116.224 | 116.4022 | 115.9371 | 116.0627 | -109.322 | -109.0352 | -109.5027 | -109.2158
266.8594 | 123.2529 | -116.098 | 7.1091 | 0.057754 | -0.058836 | 0.010893 | -0.043331 | 0.06831 | 0.039799 | -0.067295 | 7.0576 | 6.9062 | 6.8815 | 6.4325 | 116.082 | 116.2466 | 115.7723 | 115.9116 | 116.1558 | 116.0392 | 116.1089 | 116.0547 | 116.1663 | 116.1378 | 116.0307 | 7.0576 | 6.9062 | 6.8815 | 6.4325 | 116.082 | 116.2466 | 115.7723 | 115.9116 | -109.0245 | -108.7147 | -109.2005 | -108.8907
268.5469 | 123.2529 | -117.4438 | 5.7541 | 0.057754 | -0.049678 | 0.006315 | -0.038752 | 0.077466 | 0.035221 | -0.062717 | 5.7756 | 5.6242 | 5.5996 | 5.1641 | 117.3548 | 117.5284 | 117.0634 | 117.1935 | 117.5016 | 117.3942 | 117.4502 | 117.4051 | 117.5213 | 117.4791 | 117.3811 | 5.7756 | 5.6242 | 5.5996 | 5.1641 | 117.3548 | 117.5284 | 117.0634 | 117.1935 | -111.5792 | -111.2878 | -111.7552 | -111.4638
270.2344 | 123.2803 | -117.2928 | 5.8456 | 0.062332 | -0.054257 | 0.010893 | -0.034174 | 0.077466 | 0.039799 | -0.071874 | 5.8397 | 5.6837 | 5.6591 | 5.2328 | 117.2861 | 117.4598 | 116.9901 | 117.1248 | 117.3551 | 117.2385 | 117.3037 | 117.2586 | 117.3703 | 117.3326 | 117.2209 | 5.8397 | 5.6837 | 5.6591 | 5.2328 | 117.2861 | 117.4598 | 116.9901 | 117.1248 | -111.4464 | -111.1504 | -111.627 | -111.331
272.0156 | 123.3124 | -117.2928 | 5.8868 | 0.053175 | -0.054257 | 0.006315 | -0.047909 | 0.077466 | 0.035221 | -0.062717 | 5.8489 | 5.7066 | 5.6728 | 5.2465 | 117.2769 | 117.4506 | 116.981 | 117.1065 | 117.346 | 117.2385 | 117.2991 | 117.2449 | 117.3703 | 117.328 | 117.2301 | 5.8489 | 5.7066 | 5.6728 | 5.2465 | 117.2769 | 117.4506 | 116.981 | 117.1065 | -111.4281 | -111.1321 | -111.6041 | -111.3081
273.7188 | 123.2071 | -116.4322 | 6.7657 | 0.071489 | -0.049678 | 0.010893 | -0.043331 | 0.072888 | 0.035221 | -0.062717 | 6.6318 | 6.4804 | 6.4557 | 6.0295 | 116.4986 | 116.6632 | 116.198 | 116.3328 | 116.5037 | 116.3825 | 116.4431 | 116.3889 | 116.5051 | 116.4674 | 116.3695 | 6.6318 | 6.4804 | 6.4557 | 6.0295 | 116.4986 | 116.6632 | 116.198 | 116.3328 | -109.8669 | -109.5663 | -110.0429 | -109.7423
275.4062 | 123.2895 | -116.6382 | 6.5369 | 0.06691 | -0.058836 | 0.006315 | -0.038752 | 0.072888 | 0.039799 | -0.062717 | 6.4761 | 6.3201 | 6.2909 | 5.8555 | 116.6589 | 116.8326 | 116.3629 | 116.493 | 116.7051 | 116.5793 | 116.6445 | 116.5994 | 116.7111 | 116.678 | 116.5755 | 6.4761 | 6.3201 | 6.2909 | 5.8555 | 116.6589 | 116.8326 | 116.3629 | 116.493 | -110.1828 | -109.8868 | -110.368 | -110.072
277.0781 | 123.3353 | -116.2857 | 6.8527 | 0.062332 | -0.054257 | 0.006315 | -0.043331 | 0.063733 | 0.039799 | -0.062717 | 6.8103 | 6.6544 | 6.6343 | 6.199 | 116.3293 | 116.4938 | 116.0241 | 116.1497 | 116.348 | 116.2314 | 116.292 | 116.2424 | 116.3494 | 116.3255 | 116.223 | 6.8103 | 6.6544 | 6.6343 | 6.199 | 116.3293 | 116.4938 | 116.0241 | 116.1497 | -109.5189 | -109.2137 | -109.695 | -109.3898
278.7656 | 123.0057 | -94.5969 | 28.5278 | 0.062332 | -0.049678 | 0.020051 | -0.034174 | 0.082044 | 0.048956 | -0.053561 | 23.1418 | 23.2206 | 23.02 | 22.6606 | 99.9028 | 99.9853 | 99.5556 | 99.8147 | 94.6592 | 94.5472 | 94.6169 | 94.5627 | 94.6789 | 94.6458 | 94.5433 | 23.1418 | 23.2206 | 23.02 | 22.6606 | 99.9028 | 99.9853 | 99.5556 | 99.8147 | -76.7609 | -76.4138 | -76.8828 | -76.5357
280.4375 | 123.2941 | -94.6198 | 28.537 | 0.06691 | -0.054257 | 0.006315 | -0.038752 | 0.06831 | 0.030642 | -0.058139 | 28.5216 | 28.3214 | 28.3399 | 27.8715 | 94.5967 | 94.748 | 94.2721 | 94.4171 | 94.6867 | 94.5655 | 94.6261 | 94.581 | 94.6881 | 94.6504 | 94.5616 | 28.5216 | 28.3214 | 28.3399 | 27.8715 | 94.5967 | 94.748 | 94.2721 | 94.4171 | -66.0751 | -65.7506 | -66.2568 | -65.9322
282.1406 | 123.2803 | -94.5694 | 28.5233 | 0.062332 | -0.063415 | 0.006315 | -0.043331 | 0.06831 | 0.039799 | -0.062717 | 28.517 | 28.3168 | 28.3353 | 27.8578 | 94.5967 | 94.7571 | 94.2767 | 94.4262 | 94.6317 | 94.506 | 94.5757 | 94.5261 | 94.6377 | 94.6092 | 94.5067 | 28.517 | 28.3168 | 28.3353 | 27.8578 | 94.5967 | 94.7571 | 94.2767 | 94.4262 | -66.0797 | -65.7597 | -66.2613 | -65.9414
283.8125 | 123.1934 | -95.6131 | 27.5894 | 0.057754 | -0.058836 | 0.001736 | -0.038752 | 0.06831 | 0.039799 | -0.062717 | 28.1507 | 27.9779 | 27.9553 | 27.5647 | 94.9767 | 95.1142 | 94.6522 | 94.7971 | 95.6709 | 95.5543 | 95.6148 | 95.5743 | 95.6814 | 95.6529 | 95.5504 | 28.1507 | 27.9779 | 27.9553 | 27.5647 | 94.9767 | 95.1142 | 94.6522 | 94.7971 | -66.8259 | -66.5014 | -67.0213 | -66.6968
285.4844 | 123.2986 | -115.9012 | 7.1869 | 0.053175 | -0.054257 | 0.006315 | -0.043331 | 0.06831 | 0.044377 | -0.053561 | 7.2361 | 7.2817 | 7.0646 | 6.7072 | 116.1049 | 116.0635 | 115.5937 | 115.9436 | 115.9544 | 115.8469 | 115.9075 | 115.8579 | 115.9695 | 115.9456 | 115.8476 | 7.2361 | 7.2817 | 7.0646 | 6.7072 | 116.1049 | 116.0635 | 115.5937 | 115.9436 | -108.8688 | -108.3576 | -109.0403 | -108.5291
287.1719 | 123.2712 | -94.5969 | 28.5049 | 0.06691 | -0.058836 | 0.006315 | -0.034174 | 0.06831 | 0.030642 | -0.058139 | 28.4529 | 28.3168 | 28.3124 | 27.8715 | 94.5967 | 94.7571 | 94.2813 | 94.4262 | 94.6638 | 94.538 | 94.6032 | 94.5627 | 94.6652 | 94.6275 | 94.5387 | 28.4529 | 28.3168 | 28.3124 | 27.8715 | 94.5967 | 94.7571 | 94.2813 | 94.4262 | -66.1438 | -65.8284 | -66.2842 | -65.9689
288.875 | 123.317 | -94.5648 | 28.5141 | 0.053175 | -0.054257 | 0.006315 | -0.043331 | 0.072888 | 0.030642 | -0.062717 | 28.4666 | 28.3443 | 28.3628 | 27.8853 | 94.5738 | 94.7388 | 94.2538 | 94.4125 | 94.618 | 94.5106 | 94.5711 | 94.5215 | 94.6377 | 94.5955 | 94.5021 | 28.4666 | 28.3443 | 28.3628 | 27.8853 | 94.5738 | 94.7388 | 94.2538 | 94.4125 | -66.1071 | -65.7872 | -66.211 | -65.891
290.5469 | 123.2849 | -94.5602 | 28.5324 | 0.053175 | -0.058836 | 0.010893 | -0.038752 | 0.072888 | 0.039799 | -0.058139 | 28.4621 | 28.3534 | 28.3582 | 27.8807 | 94.5784 | 94.7342 | 94.2584 | 94.3988 | 94.6134 | 94.5014 | 94.5711 | 94.5215 | 94.6331 | 94.6 | 94.5021 | 28.4621 | 28.3534 | 28.3582 | 27.8807 | 94.5784 | 94.7342 | 94.2584 | 94.3988 | -66.1163 | -65.7964 | -66.2201 | -65.9002
292.2188 | 123.317 | -94.6014 | 28.5278 | 0.062332 | -0.054257 | 0.001736 | -0.038752 | 0.063733 | 0.039799 | -0.062717 | 28.4666 | 28.3443 | 28.3124 | 27.8807 | 94.5829 | 94.7342 | 94.263 | 94.4079 | 94.6638 | 94.5472 | 94.6032 | 94.5627 | 94.6652 | 94.6412 | 94.5387 | 28.4666 | 28.3443 | 28.3124 | 27.8807 | 94.5829 | 94.7342 | 94.263 | 94.4079 | -66.1163 | -65.7964 | -66.2705 | -65.9505
293.9219 | 123.2803 | -94.5602 | 28.537 | 0.062332 | -0.054257 | 0.010893 | -0.038752 | 0.072888 | 0.035221 | -0.062717 | 28.4529 | 28.3397 | 28.3216 | 27.8807 | 94.5784 | 94.7342 | 94.2538 | 94.3942 | 94.6226 | 94.506 | 94.5711 | 94.5215 | 94.6331 | 94.5955 | 94.4975 | 28.4529 | 28.3397 | 28.3216 | 27.8807 | 94.5784 | 94.7342 | 94.2538 | 94.3942 | -66.1255 | -65.8009 | -66.2568 | -65.9322
295.625 | 123.2346 | -94.6243 | 28.537 | 0.06691 | -0.063415 | 0.006315 | -0.043331 | 0.06831 | 0.030642 | -0.062717 | 28.4666 | 28.3443 | 28.3491 | 27.8715 | 94.5875 | 94.7388 | 94.2676 | 94.4079 | 94.6912 | 94.5609 | 94.6306 | 94.581 | 94.6926 | 94.655 | 94.5616 | 28.4666 | 28.3443 | 28.3491 | 27.8715 | 94.5875 | 94.7388 | 94.2676 | 94.4079 | -66.1209 | -65.8009 | -66.2384 | -65.9185
297.3438 | 123.2986 | -94.5648 | 28.5416 | 0.048597 | -0.058836 | 0.010893 | -0.038752 | 0.072888 | 0.044377 | -0.062717 | 28.4621 | 28.3488 | 28.3582 | 27.8761 | 94.5875 | 94.7388 | 94.263 | 94.4125 | 94.6134 | 94.506 | 94.5757 | 94.5261 | 94.6377 | 94.6092 | 94.5021 | 28.4621 | 28.3488 | 28.3582 | 27.8761 | 94.5875 | 94.7388 | 94.263 | 94.4125 | -66.1255 | -65.8009 | -66.2293 | -65.9048
299.0469 | 123.1934 | -94.6289 | 28.5461 | 0.057754 | -0.058836 | 0.010893 | -0.043331 | 0.06831 | 0.035221 | -0.062717 | 28.4666 | 28.3534 | 28.3582 | 27.8807 | 94.5784 | 94.7342 | 94.2676 | 94.4033 | 94.6867 | 94.5701 | 94.6398 | 94.5856 | 94.6972 | 94.6641 | 94.5662 | 28.4666 | 28.3534 | 28.3582 | 27.8807 | 94.5784 | 94.7342 | 94.2676 | 94.4033 | -66.1117 | -65.8009 | -66.2201 | -65.9093
300.7344 | 123.3124 | -94.574 | 28.4866 | 0.062332 | -0.054257 | 0.015472 | -0.043331 | 0.072888 | 0.039799 | -0.062717 | 28.4621 | 28.3397 | 28.3491 | 27.8761 | 94.5784 | 94.7434 | 94.263 | 94.4125 | 94.6363 | 94.5197 | 94.5894 | 94.5306 | 94.6469 | 94.6138 | 94.5113 | 28.4621 | 28.3397 | 28.3491 | 27.8761 | 94.5784 | 94.7434 | 94.263 | 94.4125 | -66.1163 | -65.8009 | -66.2293 | -65.9139
302.4062 | 123.2986 | -94.5877 | 28.5187 | 0.057754 | -0.054257 | 0.010893 | -0.034174 | 0.072888 | 0.030642 | -0.067295 | 28.4392 | 28.3259 | 28.3399 | 27.8624 | 94.5829 | 94.748 | 94.2676 | 94.4171 | 94.6455 | 94.5335 | 94.5986 | 94.5535 | 94.6606 | 94.6184 | 94.5204 | 28.4392 | 28.3259 | 28.3399 | 27.8624 | 94.5829 | 94.748 | 94.2676 | 94.4171 | -66.1438 | -65.8284 | -66.243 | -65.9277
304.1094 | 123.1979 | -94.6106 | 28.5324 | 0.053175 | -0.063415 | 0.010893 | -0.034174 | 0.077466 | 0.030642 | -0.058139 | 28.4483 | 28.3305 | 28.3399 | 27.8669 | 94.5738 | 94.748 | 94.2721 | 94.4125 | 94.6638 | 94.5472 | 94.6215 | 94.5764 | 94.6881 | 94.6412 | 94.5525 | 28.4483 | 28.3305 | 28.3399 | 27.8669 | 94.5738 | 94.748 | 94.2721 | 94.4125 | -66.1255 | -65.8238 | -66.2339 | -65.9322
305.7969 | 123.3444 | -94.5602 | 28.5095 | 0.062332 | -0.058836 | 0.006315 | -0.038752 | 0.06831 | 0.030642 | -0.062717 | 28.4483 | 28.3305 | 28.3353 | 27.8624 | 94.5875 | 94.7434 | 94.263 | 94.4125 | 94.6226 | 94.5014 | 94.5666 | 94.5215 | 94.6286 | 94.5909 | 94.4975 | 28.4483 | 28.3305 | 28.3353 | 27.8624 | 94.5875 | 94.7434 | 94.263 | 94.4125 | -66.1392 | -65.8147 | -66.2522 | -65.9277
307.5156 | 123.2208 | -94.6198 | 28.5233 | 0.06691 | -0.063415 | 0.015472 | -0.043331 | 0.072888 | 0.035221 | -0.062717 | 28.4346 | 28.3214 | 28.3353 | 27.8669 | 94.5784 | 94.7388 | 94.2584 | 94.4217 | 94.6867 | 94.5563 | 94.6352 | 94.5764 | 94.6926 | 94.655 | 94.557 | 28.4346 | 28.3214 | 28.3353 | 27.8669 | 94.5784 | 94.7388 | 94.2584 | 94.4217 | -66.1438 | -65.8238 | -66.243 | -65.9231
309.1875 | 123.262 | -94.5786 | 28.5233 | 0.057754 | -0.063415 | 0.010893 | -0.043331 | 0.06831 | 0.039799 | -0.062717 | 28.4392 | 28.3214 | 28.3445 | 27.8532 | 94.5829 | 94.7434 | 94.263 | 94.4217 | 94.6363 | 94.5151 | 94.5894 | 94.5352 | 94.6469 | 94.6184 | 94.5158 | 28.4392 | 28.3214 | 28.3445 | 27.8532 | 94.5829 | 94.7434 | 94.263 | 94.4217 | -66.1438 | -65.8238 | -66.2384 | -65.9185
310.875 | 123.2758 | -94.574 | 28.5233 | 0.057754 | -0.058836 | 0.015472 | -0.038752 | 0.072888 | 0.030642 | -0.062717 | 28.4437 | 28.3259 | 28.3308 | 27.8532 | 94.5967 | 94.7434 | 94.2676 | 94.4171 | 94.6317 | 94.5151 | 94.5894 | 94.5352 | 94.6469 | 94.6046 | 94.5113 | 28.4437 | 28.3259 | 28.3308 | 27.8532 | 94.5967 | 94.7434 | 94.2676 | 94.4171 | -66.1529 | -65.8238 | -66.2659 | -65.9368
312.5781 | 123.2391 | -94.606 | 28.5187 | 0.057754 | -0.063415 | 0.001736 | -0.038752 | 0.072888 | 0.044377 | -0.067295 | 28.4392 | 28.3168 | 28.3308 | 27.8532 | 94.5967 | 94.7434 | 94.2767 | 94.4217 | 94.6638 | 94.5426 | 94.6078 | 94.5673 | 94.6789 | 94.6504 | 94.5387 | 28.4392 | 28.3168 | 28.3308 | 27.8532 | 94.5967 | 94.7434 | 94.2767 | 94.4217 | -66.1575 | -65.8376 | -66.2659 | -65.946
314.25 | 123.2849 | -94.5877 | 28.4775 | 0.062332 | -0.067994 | 0.015472 | -0.034174 | 0.072888 | 0.039799 | -0.071874 | 28.4208 | 28.3076 | 28.3216 | 27.8486 | 94.5921 | 94.748 | 94.2767 | 94.4171 | 94.65 | 94.5197 | 94.6032 | 94.5535 | 94.6606 | 94.6275 | 94.5158 | 28.4208 | 28.3076 | 28.3216 | 27.8486 | 94.5921 | 94.748 | 94.2767 | 94.4171 | -66.1712 | -65.8559 | -66.2705 | -65.9551
315.9844 | 123.2346 | -94.6152 | 28.4637 | 0.062332 | -0.063415 | 0.010893 | -0.052488 | 0.06831 | 0.030642 | -0.062717 | 28.4346 | 28.3122 | 28.3262 | 27.844 | 94.5967 | 94.748 | 94.2767 | 94.4217 | 94.6775 | 94.5518 | 94.6261 | 94.5627 | 94.6835 | 94.6458 | 94.5525 | 28.4346 | 28.3122 | 28.3262 | 27.844 | 94.5967 | 94.748 | 94.2767 | 94.4217 | -66.1621 | -65.8421 | -66.2705 | -65.9505
317.6562 | 123.3353 | -94.6106 | 28.4729 | 0.062332 | -0.058836 | 0.010893 | -0.047909 | 0.06831 | 0.035221 | -0.058139 | 28.4208 | 28.303 | 28.3124 | 27.8349 | 94.5921 | 94.7617 | 94.2721 | 94.4217 | 94.6729 | 94.5518 | 94.6215 | 94.5627 | 94.6789 | 94.6458 | 94.5525 | 28.4208 | 28.303 | 28.3124 | 27.8349 | 94.5921 | 94.7617 | 94.2721 | 94.4217 | -66.1712 | -65.8513 | -66.2796 | -65.9597
319.375 | 123.1888 | -94.6518 | 28.5416 | 0.053175 | -0.058836 | 0.001736 | -0.043331 | 0.077466 | 0.026064 | -0.058139 | 28.4117 | 28.2985 | 28.3124 | 27.8303 | 94.6058 | 94.7617 | 94.2859 | 94.44 | 94.705 | 94.593 | 94.6535 | 94.6085 | 94.7293 | 94.6779 | 94.5937 | 28.4117 | 28.2985 | 28.3124 | 27.8303 | 94.6058 | 94.7617 | 94.2859 | 94.44 | -66.1941 | -65.8742 | -66.2934 | -65.9734
321.0625 | 123.2986 | -94.5877 | 28.4729 | 0.057754 | -0.058836 | 0.006315 | -0.034174 | 0.072888 | 0.039799 | -0.062717 | 28.4071 | 28.2985 | 28.3079 | 27.8257 | 94.615 | 94.7617 | 94.295 | 94.44 | 94.6455 | 94.5289 | 94.594 | 94.5535 | 94.6606 | 94.6275 | 94.525 | 28.4071 | 28.2985 | 28.3079 | 27.8257 | 94.615 | 94.7617 | 94.295 | 94.44 | -66.2079 | -65.8879 | -66.3071 | -65.9872
322.7188 | 123.1613 | -94.6472 | 28.5049 | 0.06691 | -0.054257 | 0.010893 | -0.034174 | 0.077466 | 0.035221 | -0.062717 | 28.4071 | 28.2847 | 28.2896 | 27.8303 | 94.6104 | 94.7617 | 94.2859 | 94.44 | 94.7141 | 94.593 | 94.6581 | 94.613 | 94.7247 | 94.6824 | 94.5845 | 28.4071 | 28.2847 | 28.2896 | 27.8303 | 94.6104 | 94.7617 | 94.2859 | 94.44 | -66.2033 | -65.8788 | -66.3209 | -65.9963
324.4688 | 123.3032 | -94.5923 | 28.4683 | 0.053175 | -0.054257 | 0.001736 | -0.043331 | 0.072888 | 0.035221 | -0.058139 | 28.4025 | 28.271 | 28.2941 | 27.812 | 94.6196 | 94.78 | 94.3042 | 94.4491 | 94.6455 | 94.538 | 94.594 | 94.549 | 94.6652 | 94.6275 | 94.5341 | 28.4025 | 28.271 | 28.2941 | 27.812 | 94.6196 | 94.78 | 94.3042 | 94.4491 | -66.217 | -65.9017 | -66.3254 | -66.0101
326.1562 | 123.1659 | -94.6564 | 28.4592 | 0.057754 | -0.058836 | 0.001736 | -0.038752 | 0.06831 | 0.030642 | -0.058139 | 28.398 | 28.2756 | 28.285 | 27.812 | 94.6196 | 94.7846 | 94.3042 | 94.4491 | 94.7141 | 94.5975 | 94.6581 | 94.6176 | 94.7247 | 94.687 | 94.5982 | 28.398 | 28.2756 | 28.285 | 27.812 | 94.6196 | 94.7846 | 94.3042 | 94.4491 | -66.2216 | -65.9062 | -66.3346 | -66.0192
327.8281 | 123.2986 | -94.6335 | 28.4363 | 0.06691 | -0.067994 | 0.010893 | -0.043331 | 0.072888 | 0.026064 | -0.062717 | 28.3751 | 28.2618 | 28.2758 | 27.8028 | 94.615 | 94.7846 | 94.3088 | 94.4583 | 94.7004 | 94.5655 | 94.6444 | 94.5902 | 94.7064 | 94.6595 | 94.5708 | 28.3751 | 28.2618 | 28.2758 | 27.8028 | 94.615 | 94.7846 | 94.3088 | 94.4583 | -66.2399 | -65.9337 | -66.3392 | -66.033
329.5469 | 123.1979 | -94.6472 | 28.4775 | 0.062332 | -0.054257 | 0.006315 | -0.038752 | 0.063733 | 0.035221 | -0.067295 | 28.3796 | 28.271 | 28.2804 | 27.8028 | 94.6379 | 94.7846 | 94.3134 | 94.4629 | 94.7095 | 94.593 | 94.6535 | 94.6085 | 94.7109 | 94.6824 | 94.5799 | 28.3796 | 28.271 | 28.2804 | 27.8028 | 94.6379 | 94.7846 | 94.3134 | 94.4629 | -66.2582 | -65.9337 | -66.3575 | -66.033
331.2188 | 123.1934 | -94.6564 | 28.4592 | 0.062332 | -0.063415 | 0.010893 | -0.047909 | 0.082044 | 0.030642 | -0.062717 | 28.3842 | 28.2618 | 28.2712 | 27.7937 | 94.647 | 94.7983 | 94.3225 | 94.4629 | 94.7187 | 94.593 | 94.6673 | 94.6085 | 94.7384 | 94.687 | 94.5937 | 28.3842 | 28.2618 | 28.2712 | 27.7937 | 94.647 | 94.7983 | 94.3225 | 94.4629 | -66.2628 | -65.9383 | -66.3758 | -66.0513
332.8906 | 123.3582 | -94.6152 | 28.4363 | 0.06691 | -0.063415 | 0.006315 | -0.034174 | 0.072888 | 0.035221 | -0.062717 | 28.3751 | 28.2527 | 28.2712 | 27.7937 | 94.6425 | 94.7938 | 94.3225 | 94.472 | 94.6821 | 94.5518 | 94.6215 | 94.581 | 94.6881 | 94.6504 | 94.5525 | 28.3751 | 28.2527 | 28.2712 | 27.7937 | 94.6425 | 94.7938 | 94.3225 | 94.472 | -66.2674 | -65.9475 | -66.3712 | -66.0513
334.5781 | 123.2025 | -94.6655 | 28.45 | 0.053175 | -0.063415 | 0.006315 | -0.038752 | 0.072888 | 0.026064 | -0.062717 | 28.3659 | 28.2573 | 28.2667 | 27.7937 | 94.6425 | 94.8029 | 94.3271 | 94.4766 | 94.7187 | 94.6021 | 94.6718 | 94.6268 | 94.7384 | 94.6916 | 94.6028 | 28.3659 | 28.2573 | 28.2667 | 27.7937 | 94.6425 | 94.8029 | 94.3271 | 94.4766 | -66.2765 | -65.9612 | -66.3758 | -66.0604
336.2656 | 123.2346 | -122.8775 | 0.3067 | 0.057754 | -0.067994 | 0.006315 | -0.043331 | 0.072888 | 0.035221 | -0.058139 | 0.29515 | 0.35852 | 0.041563 | -0.13842 | 123.0454 | 123.013 | 122.5529 | 122.8979 | 122.9353 | 122.8095 | 122.8838 | 122.8342 | 122.9504 | 122.9127 | 122.8194 | 0.29515 | 0.35852 | 0.041563 | -0.13842 | 123.0454 | 123.013 | 122.5529 | 122.8979 | -122.7503 | -122.2577 | -123.0039 | -122.5113
338.125 | 123.317 | -122.8683 | 0.26093 | 0.062332 | -0.067994 | 0.010893 | -0.047909 | 0.06831 | 0.035221 | -0.062717 | 0.29515 | 0.17079 | -0.022532 | -0.13842 | 122.8577 | 123.0175 | 122.5574 | 122.9025 | 122.9307 | 122.8004 | 122.8792 | 122.8204 | 122.9367 | 122.9036 | 122.8056 | 0.29515 | 0.17079 | -0.022532 | -0.13842 | 122.8577 | 123.0175 | 122.5574 | 122.9025 | -122.5626 | -122.2623 | -122.8803 | -122.58
339.8906 | 123.2803 | -122.8912 | 0.27466 | 0.053175 | -0.058836 | 0.006315 | -0.043331 | 0.06831 | 0.030642 | -0.062717 | 0.28599 | 0.16164 | -0.004219 | -0.143 | 122.8715 | 123.0267 | 122.562 | 122.6964 | 122.9444 | 122.8324 | 122.8975 | 122.8479 | 122.9595 | 122.9219 | 122.8285 | 0.28599 | 0.16164 | -0.004219 | -0.143 | 122.8715 | 123.0267 | 122.562 | 122.6964 | -122.5855 | -122.276 | -122.8757 | -122.5662
341.5781 | 123.3078 | -122.8867 | 0.27466 | 0.057754 | -0.067994 | 0.006315 | -0.043331 | 0.06831 | 0.039799 | -0.058139 | 0.29973 | 0.17537 | -0.017954 | -0.14758 | 123.0546 | 123.013 | 122.7726 | 122.8933 | 122.9444 | 122.8187 | 122.893 | 122.8433 | 122.955 | 122.9265 | 122.8285 | 0.29973 | 0.17537 | -0.017954 | -0.14758 | 123.0546 | 123.013 | 122.7726 | 122.8933 | -122.7549 | -122.4729 | -123.0725 | -122.7906
343.3281 | 123.2071 | -122.9004 | 0.32501 | 0.062332 | -0.072572 | 0.015472 | -0.043331 | 0.06831 | 0.039799 | -0.058139 | 0.29973 | 0.17079 | 0.009515 | -0.15216 | 122.8532 | 123.0038 | 122.5391 | 122.6873 | 122.9627 | 122.8278 | 122.9159 | 122.8571 | 122.9687 | 122.9402 | 122.8423 | 0.29973 | 0.17079 | 0.009515 | -0.15216 | 122.8532 | 123.0038 | 122.5391 | 122.6873 | -122.5534 | -122.2394 | -122.8436 | -122.5296
345.0781 | 123.3078 | -122.8546 | 0.29755 | 0.057754 | -0.063415 | 0.006315 | -0.043331 | 0.072888 | 0.030642 | -0.062717 | 0.3272 | 0.17995 | 0.036985 | -0.143 | 122.8257 | 122.9763 | 122.5162 | 122.6507 | 122.9124 | 122.7912 | 122.8609 | 122.8113 | 122.9275 | 122.8853 | 122.7919 | 0.3272 | 0.17995 | 0.036985 | -0.143 | 122.8257 | 122.9763 | 122.5162 | 122.6507 | -122.4985 | -122.189 | -122.7887 | -122.4792
346.75 | 123.1842 | -122.9004 | 0.34332 | 0.057754 | -0.063415 | 0.015472 | -0.038752 | 0.072888 | 0.035221 | -0.067295 | 0.3272 | 0.19827 | 0.055298 | -0.14758 | 122.8303 | 122.9855 | 122.5162 | 122.6461 | 122.9581 | 122.837 | 122.9159 | 122.8616 | 122.9733 | 122.9356 | 122.8331 | 0.3272 | 0.19827 | 0.055298 | -0.14758 | 122.8303 | 122.9855 | 122.5162 | 122.6461 | -122.5031 | -122.189 | -122.775 | -122.4609
348.5 | 123.175 | -122.8867 | 0.33875 | 0.06691 | -0.077151 | 0.006315 | -0.043331 | 0.077466 | 0.035221 | -0.062717 | 0.32262 | 0.18911 | 0.004937 | -0.15674 | 122.8257 | 122.9809 | 122.5162 | 122.6369 | 122.9536 | 122.8095 | 122.893 | 122.8433 | 122.9641 | 122.9219 | 122.8239 | 0.32262 | 0.18911 | 0.004937 | -0.15674 | 122.8257 | 122.9809 | 122.5162 | 122.6369 | -122.5031 | -122.1936 | -122.8207 | -122.5113
350.1875 | 123.2803 | -122.8271 | 0.3479 | 0.053175 | -0.072572 | 0.001736 | -0.038752 | 0.072888 | 0.035221 | -0.067295 | 0.33178 | 0.20284 | 0.014094 | -0.15216 | 122.812 | 122.9672 | 122.5025 | 122.6324 | 122.8803 | 122.7546 | 122.8289 | 122.7884 | 122.9 | 122.8624 | 122.7599 | 0.33178 | 0.20284 | 0.014094 | -0.15216 | 122.812 | 122.9672 | 122.5025 | 122.6324 | -122.4802 | -122.1707 | -122.7979 | -122.4884
351.9219 | 123.1934 | -122.8958 | 0.34332 | 0.062332 | -0.063415 | 0.006315 | -0.043331 | 0.072888 | 0.044377 | -0.062717 | -0.029925 | 0.19827 | 0.009515 | -0.14758 | 122.8257 | 122.9901 | 122.5162 | 122.6461 | 122.9581 | 122.8324 | 122.9021 | 122.8525 | 122.9687 | 122.9402 | 122.8331 | -0.029925 | 0.19827 | 0.009515 | -0.14758 | 122.8257 | 122.9901 | 122.5162 | 122.6461 | -122.8556 | -122.5461 | -122.8162 | -122.5067
353.6094 | 123.2712 | -122.8409 | 0.28381 | 0.062332 | -0.063415 | 0.010893 | -0.047909 | 0.072888 | 0.035221 | -0.067295 | -0.029925 | 0.17995 | 0.02325 | -0.15216 | 122.8257 | 122.9901 | 122.5254 | 122.6507 | 122.9032 | 122.7775 | 122.8518 | 122.793 | 122.9138 | 122.8761 | 122.7736 | -0.029925 | 0.17995 | 0.02325 | -0.15216 | 122.8257 | 122.9901 | 122.5254 | 122.6507 | -122.8556 | -122.5553 | -122.8024 | -122.5021
355.3594 | 123.1522 | -122.8821 | 0.32959 | 0.06691 | -0.072572 | 0.010893 | -0.038752 | 0.072888 | 0.044377 | -0.058139 | -0.011611 | 0.18453 | 0.041563 | -0.14758 | 122.844 | 122.9946 | 122.53 | 122.6598 | 122.949 | 122.8095 | 122.893 | 122.8433 | 122.955 | 122.9265 | 122.8239 | -0.011611 | 0.18453 | 0.041563 | -0.14758 | 122.844 | 122.9946 | 122.53 | 122.6598 | -122.8556 | -122.5416 | -122.8024 | -122.4884
357.1094 | 123.2529 | -122.8592 | 0.28839 | 0.057754 | -0.063415 | 0.010893 | -0.043331 | 0.072888 | 0.030642 | -0.058139 | -0.029925 | 0.1479 | -0.017954 | -0.14758 | 122.876 | 122.9992 | 122.5345 | 122.6644 | 122.9169 | 122.7958 | 122.8701 | 122.8159 | 122.9321 | 122.8898 | 122.8011 | -0.029925 | 0.1479 | -0.017954 | -0.14758 | 122.876 | 122.9992 | 122.5345 | 122.6644 | -122.906 | -122.5645 | -122.894 | -122.5525
358.7969 | 123.317 | -122.8546 | 0.30212 | 0.053175 | -0.063415 | 0.015472 | -0.043331 | 0.072888 | 0.035221 | -0.067295 | -0.052818 | 0.17995 | -0.017954 | -0.14758 | 122.8669 | 122.9901 | 122.5345 | 122.6736 | 122.9078 | 122.7912 | 122.8701 | 122.8113 | 122.9275 | 122.8898 | 122.7873 | -0.052818 | 0.17995 | -0.017954 | -0.14758 | 122.8669 | 122.9901 | 122.5345 | 122.6736 | -122.9197 | -122.5874 | -122.8848 | -122.5525
360.5625 | 123.2941 | -122.8592 | 0.31586 | 0.057754 | -0.072572 | 0.006315 | -0.038752 | 0.072888 | 0.035221 | -0.067295 | -0.020768 | 0.17079 | 0.009515 | -0.13842 | 122.844 | 122.9901 | 122.53 | 122.6598 | 122.9169 | 122.7866 | 122.8655 | 122.8204 | 122.9321 | 122.8944 | 122.7919 | -0.020768 | 0.17079 | 0.009515 | -0.13842 | 122.844 | 122.9901 | 122.53 | 122.6598 | -122.8648 | -122.5507 | -122.8345 | -122.5204
362.25 | 123.2803 | -122.818 | 0.33417 | 0.062332 | -0.072572 | 0.001736 | -0.034174 | 0.072888 | 0.039799 | -0.053561 | 0.047909 | 0.19827 | 0.069033 | -0.15216 | 122.7936 | 122.9672 | 122.4933 | 122.6324 | 122.8803 | 122.7454 | 122.8197 | 122.7838 | 122.8909 | 122.8578 | 122.7644 | 0.047909 | 0.19827 | 0.069033 | -0.15216 | 122.7936 | 122.9672 | 122.4933 | 122.6324 | -122.7457 | -122.4454 | -122.7246 | -122.4243
363.9844 | 123.1567 | -122.8363 | 0.36163 | 0.062332 | -0.072572 | 0.015472 | -0.034174 | 0.06831 | 0.030642 | -0.058139 | -0.034504 | 0.20284 | 0.009515 | -0.15216 | 122.7936 | 122.9489 | 122.4842 | 122.6186 | 122.8986 | 122.7637 | 122.8518 | 122.8021 | 122.9046 | 122.8669 | 122.7782 | -0.034504 | 0.20284 | 0.009515 | -0.15216 | 122.7936 | 122.9489 | 122.4842 | 122.6186 | -122.8281 | -122.5187 | -122.7841 | -122.4747
365.6875 | 123.2483 | -122.7997 | 0.33875 | 0.062332 | -0.067994 | -0.002842 | -0.043331 | 0.077466 | 0.030642 | -0.067295 | 0.002124 | 0.20742 | 0.027829 | -0.14758 | 122.8074 | 122.9443 | 122.4842 | 122.6232 | 122.862 | 122.7317 | 122.7968 | 122.7564 | 122.8771 | 122.8303 | 122.7324 | 0.002124 | 0.20742 | 0.027829 | -0.14758 | 122.8074 | 122.9443 | 122.4842 | 122.6232 | -122.8052 | -122.4821 | -122.7795 | -122.4563
367.4219 | 123.2437 | -122.7859 | 0.37537 | 0.062332 | -0.067994 | 0.010893 | -0.034174 | 0.072888 | 0.026064 | -0.062717 | 0.002124 | 0.2349 | 0.041563 | -0.143 | 122.7845 | 122.9122 | 122.4475 | 122.5774 | 122.8483 | 122.718 | 122.7968 | 122.7518 | 122.8588 | 122.812 | 122.7232 | 0.002124 | 0.2349 | 0.041563 | -0.143 | 122.7845 | 122.9122 | 122.4475 | 122.5774 | -122.7824 | -122.4454 | -122.7429 | -122.406
369.0938 | 123.1705 | -122.7951 | 0.40283 | 0.06691 | -0.067994 | 0.010893 | -0.038752 | 0.082044 | 0.035221 | -0.062717 | 0.020438 | 0.23948 | 0.05072 | -0.15216 | 122.7799 | 122.9077 | 122.4521 | 122.5774 | 122.862 | 122.7271 | 122.806 | 122.7564 | 122.8771 | 122.8303 | 122.7324 | 0.020438 | 0.23948 | 0.05072 | -0.15216 | 122.7799 | 122.9077 | 122.4521 | 122.5774 | -122.7595 | -122.4317 | -122.7292 | -122.4014
370.8281 | 123.1888 | -122.9004 | 0.31128 | 0.071489 | -0.067994 | 0.010893 | -0.043331 | 0.077466 | 0.039799 | -0.058139 | -0.052818 | 0.17537 | -0.031689 | -0.15216 | 122.8715 | 123.0084 | 122.5437 | 122.6781 | 122.9719 | 122.8324 | 122.9113 | 122.8571 | 122.9779 | 122.9402 | 122.8423 | -0.052818 | 0.17537 | -0.031689 | -0.15216 | 122.8715 | 123.0084 | 122.5437 | 122.6781 | -122.9243 | -122.5965 | -122.9032 | -122.5754
372.5 | 123.2803 | -122.8363 | 0.28381 | 0.057754 | -0.063415 | 0.006315 | -0.043331 | 0.082044 | 0.035221 | -0.053561 | 0.01586 | 0.18453 | 0.02325 | -0.14758 | 122.8211 | 122.9809 | 122.4979 | 122.6369 | 122.8941 | 122.7729 | 122.8426 | 122.793 | 122.9183 | 122.8715 | 122.7827 | 0.01586 | 0.18453 | 0.02325 | -0.14758 | 122.8211 | 122.9809 | 122.4979 | 122.6369 | -122.8052 | -122.4821 | -122.7979 | -122.4747
374.2344 | 123.1842 | -122.7951 | 0.39368 | 0.057754 | -0.058836 | 0.006315 | -0.038752 | 0.06831 | 0.030642 | -0.058139 | -0.011611 | 0.23032 | 0.027829 | -0.14758 | 122.7845 | 122.9214 | 122.4475 | 122.582 | 122.8529 | 122.7363 | 122.8014 | 122.7564 | 122.8634 | 122.8257 | 122.737 | -0.011611 | 0.23032 | 0.027829 | -0.14758 | 122.7845 | 122.9214 | 122.4475 | 122.582 | -122.7961 | -122.4592 | -122.7567 | -122.4197
375.9219 | 123.143 | -122.8546 | 0.33875 | 0.062332 | -0.072572 | 0.001736 | -0.043331 | 0.072888 | 0.035221 | -0.058139 | 0.006703 | 0.21658 | 0.055298 | -0.13842 | 122.8257 | 122.958 | 122.4796 | 122.6278 | 122.9169 | 122.782 | 122.8563 | 122.8113 | 122.9275 | 122.8898 | 122.7965 | 0.006703 | 0.21658 | 0.055298 | -0.13842 | 122.8257 | 122.958 | 122.4796 | 122.6278 | -122.819 | -122.4729 | -122.7704 | -122.4243
377.6719 | 123.1979 | -122.85 | 0.33875 | 0.057754 | -0.063415 | 0.010893 | -0.038752 | 0.082044 | 0.039799 | -0.062717 | -0.01619 | 0.18911 | 0.009515 | -0.15216 | 122.8394 | 122.9672 | 122.4888 | 122.6369 | 122.9078 | 122.7866 | 122.8609 | 122.8113 | 122.9321 | 122.8898 | 122.7873 | -0.01619 | 0.18911 | 0.009515 | -0.15216 | 122.8394 | 122.9672 | 122.4888 | 122.6369 | -122.8556 | -122.5049 | -122.8299 | -122.4792
379.3594 | 123.1384 | -122.8592 | 0.34332 | 0.071489 | -0.063415 | 0.006315 | -0.043331 | 0.072888 | 0.035221 | -0.058139 | 0.01586 | 0.18911 | 0.032407 | -0.14758 | 122.844 | 122.9672 | 122.4979 | 122.6232 | 122.9307 | 122.7958 | 122.8655 | 122.8159 | 122.9321 | 122.8944 | 122.8011 | 0.01586 | 0.18911 | 0.032407 | -0.14758 | 122.844 | 122.9672 | 122.4979 | 122.6232 | -122.8281 | -122.4821 | -122.8116 | -122.4655
381.1094 | 123.2758 | -122.8043 | 0.32501 | 0.057754 | -0.077151 | 0.010893 | -0.043331 | 0.077466 | 0.030642 | -0.067295 | 0.052488 | 0.18911 | 0.036985 | -0.143 | 122.8303 | 122.958 | 122.4888 | 122.6278 | 122.862 | 122.7271 | 122.8152 | 122.7609 | 122.8817 | 122.8349 | 122.737 | 0.052488 | 0.18911 | 0.036985 | -0.143 | 122.8303 | 122.958 | 122.4888 | 122.6278 | -122.7778 | -122.4363 | -122.7933 | -122.4518
382.7812 | 123.175 | -122.8821 | 0.33417 | 0.053175 | -0.063415 | 0.006315 | -0.034174 | 0.077466 | 0.035221 | -0.058139 | 0.034174 | 0.18453 | 0.055298 | -0.14758 | 122.8486 | 122.9626 | 122.4933 | 122.6369 | 122.9353 | 122.8187 | 122.8884 | 122.8479 | 122.9595 | 122.9173 | 122.8239 | 0.034174 | 0.18453 | 0.055298 | -0.14758 | 122.8486 | 122.9626 | 122.4933 | 122.6369 | -122.8144 | -122.4592 | -122.7933 | -122.438
384.5312 | 123.2025 | -122.8271 | 0.30212 | 0.057754 | -0.067994 | 0.006315 | -0.052488 | 0.072888 | 0.026064 | -0.062717 | -0.029925 | 0.18453 | 0.036985 | -0.15674 | 122.8532 | 122.958 | 122.4979 | 122.6278 | 122.8849 | 122.7592 | 122.8335 | 122.7747 | 122.9 | 122.8532 | 122.7644 | -0.029925 | 0.18453 | 0.036985 | -0.15674 | 122.8532 | 122.958 | 122.4979 | 122.6278 | -122.8831 | -122.5278 | -122.8162 | -122.4609
386.2344 | 123.2666 | -122.8592 | 0.31128 | 0.057754 | -0.072572 | 0.006315 | -0.038752 | 0.072888 | 0.026064 | -0.071874 | -0.002454 | 0.15706 | 0.014094 | -0.14758 | 122.8806 | 122.9855 | 122.5162 | 122.6598 | 122.9169 | 122.7866 | 122.8655 | 122.8204 | 122.9321 | 122.8853 | 122.7873 | -0.002454 | 0.15706 | 0.014094 | -0.14758 | 122.8806 | 122.9855 | 122.5162 | 122.6598 | -122.8831 | -122.5187 | -122.8665 | -122.5021
387.9844 | 123.2254 | -122.8455 | 0.28381 | 0.062332 | -0.072572 | 0.015472 | -0.034174 | 0.06831 | 0.035221 | -0.062717 | -0.002454 | 0.16622 | 0.036985 | -0.143 | 122.8989 | 122.9946 | 122.53 | 122.6736 | 122.9078 | 122.7729 | 122.8609 | 122.8113 | 122.9138 | 122.8807 | 122.7827 | -0.002454 | 0.16622 | 0.036985 | -0.143 | 122.8989 | 122.9946 | 122.53 | 122.6736 | -122.9014 | -122.5324 | -122.862 | -122.493
389.7188 | 123.1384 | -122.8683 | 0.30212 | 0.057754 | -0.067994 | 0.010893 | -0.034174 | 0.06831 | 0.030642 | -0.062717 | -0.043661 | 0.15706 | 0.014094 | -0.14758 | 122.8715 | 122.9992 | 122.5254 | 122.669 | 122.9261 | 122.8004 | 122.8792 | 122.8342 | 122.9367 | 122.899 | 122.8056 | -0.043661 | 0.15706 | 0.014094 | -0.14758 | 122.8715 | 122.9992 | 122.5254 | 122.669 | -122.9151 | -122.569 | -122.8574 | -122.5113
391.4688 | 123.2254 | -122.8455 | 0.27924 | 0.057754 | -0.067994 | 0.010893 | -0.038752 | 0.072888 | 0.048956 | -0.053561 | -0.025347 | 0.16622 | 0.014094 | -0.15216 | 122.876 | 122.9946 | 122.5208 | 122.669 | 122.9032 | 122.7775 | 122.8564 | 122.8067 | 122.9183 | 122.8944 | 122.7919 | -0.025347 | 0.16622 | 0.014094 | -0.15216 | 122.876 | 122.9946 | 122.5208 | 122.669 | -122.9014 | -122.5461 | -122.862 | -122.5067
393.2188 | 123.143 | -122.8867 | 0.29755 | 0.057754 | -0.067994 | 0.006315 | -0.034174 | 0.06831 | 0.030642 | -0.053561 | -0.07571 | 0.16164 | -0.022532 | -0.15216 | 122.8898 | 122.9992 | 122.5345 | 122.6736 | 122.9444 | 122.8187 | 122.893 | 122.8525 | 122.955 | 122.9173 | 122.8331 | -0.07571 | 0.16164 | -0.022532 | -0.15216 | 122.8898 | 122.9992 | 122.5345 | 122.6736 | -122.9655 | -122.6102 | -122.9123 | -122.5571
394.8906 | 123.2758 | -122.8455 | 0.25177 | 0.057754 | -0.067994 | 0.010893 | -0.038752 | 0.072888 | 0.030642 | -0.058139 | -0.025347 | 0.16622 | 0.004937 | -0.143 | 122.9127 | 122.9992 | 122.5391 | 122.6736 | 122.9032 | 122.7775 | 122.8564 | 122.8067 | 122.9183 | 122.8761 | 122.7873 | -0.025347 | 0.16622 | 0.004937 | -0.143 | 122.9127 | 122.9992 | 122.5391 | 122.6736 | -122.938 | -122.5645 | -122.9077 | -122.5342
396.6406 | 123.1705 | -122.8867 | 0.28381 | 0.053175 | -0.067994 | 0.010893 | -0.043331 | 0.06831 | 0.030642 | -0.062717 | -0.002454 | 0.17079 | 0.009515 | -0.15674 | 122.8806 | 122.9992 | 122.5437 | 122.6827 | 122.9398 | 122.8187 | 122.8976 | 122.8433 | 122.955 | 122.9173 | 122.8239 | -0.002454 | 0.17079 | 0.009515 | -0.15674 | 122.8806 | 122.9992 | 122.5437 | 122.6827 | -122.8831 | -122.5461 | -122.8711 | -122.5342
398.3906 | 123.2391 | -122.8317 | 0.27466 | 0.062332 | -0.072572 | 0.006315 | -0.038752 | 0.077466 | 0.039799 | -0.067295 | 0.011281 | 0.17537 | 0.036985 | -0.14758 | 122.8944 | 122.9946 | 122.5254 | 122.6644 | 122.8941 | 122.7592 | 122.838 | 122.793 | 122.9092 | 122.8715 | 122.7644 | 0.011281 | 0.17537 | 0.036985 | -0.14758 | 122.8944 | 122.9946 | 122.5254 | 122.6644 | -122.8831 | -122.5141 | -122.8574 | -122.4884
400.1406 | 123.2529 | -122.8226 | 0.28839 | 0.057754 | -0.063415 | 0.006315 | -0.043331 | 0.06831 | 0.039799 | -0.058139 | -0.025347 | 0.17995 | -0.004219 | -0.14758 | 122.8852 | 122.9855 | 122.5162 | 122.6552 | 122.8803 | 122.7592 | 122.8289 | 122.7792 | 122.8909 | 122.8624 | 122.7644 | -0.025347 | 0.17995 | -0.004219 | -0.14758 | 122.8852 | 122.9855 | 122.5162 | 122.6552 | -122.9105 | -122.5416 | -122.8894 | -122.5204
401.8281 | 123.1201 | -122.8729 | 0.32959 | 0.062332 | -0.067994 | 0.006315 | -0.038752 | 0.077466 | 0.039799 | -0.053561 | 0.01586 | 0.17537 | 0.069033 | -0.14758 | 122.8806 | 122.9809 | 122.5116 | 122.6507 | 122.9353 | 122.8049 | 122.8792 | 122.8342 | 122.9504 | 122.9127 | 122.8194 | 0.01586 | 0.17537 | 0.069033 | -0.14758 | 122.8806 | 122.9809 | 122.5116 | 122.6507 | -122.8648 | -122.4958 | -122.8116 | -122.4426
403.5781 | 123.1338 | -122.8683 | 0.29755 | 0.062332 | -0.063415 | 0.010893 | -0.047909 | 0.072888 | 0.039799 | -0.058139 | -0.029925 | 0.17537 | 0.009515 | -0.15216 | 122.9127 | 122.9901 | 122.5208 | 122.669 | 122.9307 | 122.8049 | 122.8792 | 122.8204 | 122.9412 | 122.9081 | 122.8102 | -0.029925 | 0.17537 | 0.009515 | -0.15216 | 122.9127 | 122.9901 | 122.5208 | 122.669 | -122.9426 | -122.5507 | -122.9032 | -122.5113
405.2656 | 123.1659 | -122.8821 | 0.28839 | 0.06691 | -0.067994 | 0.006315 | -0.034174 | 0.06831 | 0.044377 | -0.053561 | 0.025017 | 0.17079 | 0.064455 | -0.15216 | 122.8669 | 122.9946 | 122.5162 | 122.669 | 122.949 | 122.8141 | 122.8884 | 122.8479 | 122.9504 | 122.9265 | 122.8285 | 0.025017 | 0.17079 | 0.064455 | -0.15216 | 122.8669 | 122.9946 | 122.5162 | 122.669 | -122.8419 | -122.4912 | -122.8024 | -122.4518
407.0156 | 123.2391 | -122.8409 | 0.25177 | 0.057754 | -0.072572 | 0.006315 | -0.034174 | 0.06831 | 0.035221 | -0.062717 | 0.025017 | 0.16622 | 0.082768 | -0.15216 | 122.8989 | 122.9992 | 122.5345 | 122.6827 | 122.8986 | 122.7683 | 122.8472 | 122.8067 | 122.9092 | 122.8761 | 122.7782 | 0.025017 | 0.16622 | 0.082768 | -0.15216 | 122.8989 | 122.9992 | 122.5345 | 122.6827 | -122.8739 | -122.5095 | -122.8162 | -122.4518
408.7031 | 123.2574 | -122.8683 | 0.26093 | 0.057754 | -0.063415 | 0.010893 | -0.043331 | 0.072888 | 0.035221 | -0.067295 | -0.029925 | 0.15248 | 0.02325 | -0.14758 | 122.9127 | 123.013 | 122.5391 | 122.6919 | 122.9261 | 122.8049 | 122.8792 | 122.825 | 122.9412 | 122.9036 | 122.8011 | -0.029925 | 0.15248 | 0.02325 | -0.14758 | 122.9127 | 123.013 | 122.5391 | 122.6919 | -122.9426 | -122.569 | -122.8894 | -122.5159
410.4531 | 123.1567 | -122.905 | 0.27924 | 0.06691 | -0.072572 | 0.006315 | -0.043331 | 0.06831 | 0.030642 | -0.062717 | -0.002454 | 0.1479 | 0.02325 | -0.15216 | 122.9218 | 123.0084 | 122.5391 | 122.6873 | 122.9719 | 122.8324 | 122.9113 | 122.8616 | 122.9733 | 122.9356 | 122.8423 | -0.002454 | 0.1479 | 0.02325 | -0.15216 | 122.9218 | 123.0084 | 122.5391 | 122.6873 | -122.9243 | -122.5416 | -122.8986 | -122.5159
412.2031 | 123.2391 | -122.85 | 0.25635 | 0.053175 | -0.072572 | 0.006315 | -0.038752 | 0.077466 | 0.035221 | -0.058139 | -0.057396 | 0.15706 | 0.000359 | -0.15674 | 122.8898 | 122.9992 | 122.53 | 122.6736 | 122.9032 | 122.7775 | 122.8564 | 122.8113 | 122.9275 | 122.8853 | 122.7919 | -0.057396 | 0.15706 | 0.000359 | -0.15674 | 122.8898 | 122.9992 | 122.53 | 122.6736 | -122.9472 | -122.5874 | -122.8894 | -122.5296
413.9531 | 123.1522 | -122.8729 | 0.27466 | 0.062332 | -0.058836 | 0.006315 | -0.038752 | 0.077466 | 0.039799 | -0.058139 | 0.029595 | 0.16164 | 0.059877 | -0.15674 | 122.9127 | 123.0038 | 122.5391 | 122.6736 | 122.9353 | 122.8141 | 122.8792 | 122.8342 | 122.9504 | 122.9127 | 122.8148 | 0.029595 | 0.16164 | 0.059877 | -0.15674 | 122.9127 | 123.0038 | 122.5391 | 122.6736 | -122.8831 | -122.5095 | -122.8528 | -122.4792
415.6875 | 123.1155 | -122.8912 | 0.31128 | 0.057754 | -0.063415 | 0.010893 | -0.038752 | 0.072888 | 0.035221 | -0.058139 | -0.002454 | 0.16164 | 0.032407 | -0.15216 | 122.8989 | 122.9855 | 122.5254 | 122.669 | 122.949 | 122.8278 | 122.9021 | 122.8525 | 122.9641 | 122.9265 | 122.8331 | -0.002454 | 0.16164 | 0.032407 | -0.15216 | 122.8989 | 122.9855 | 122.5254 | 122.669 | -122.9014 | -122.5278 | -122.8665 | -122.493
417.375 | 123.2162 | -122.8775 | 0.23804 | 0.053175 | -0.067994 | 0.006315 | -0.038752 | 0.072888 | 0.035221 | -0.062717 | -0.07571 | 0.13874 | 0.018672 | -0.143 | 122.9264 | 123.013 | 122.5483 | 122.6827 | 122.9307 | 122.8095 | 122.8838 | 122.8388 | 122.9504 | 122.9127 | 122.8148 | -0.07571 | 0.13874 | 0.018672 | -0.143 | 122.9264 | 123.013 | 122.5483 | 122.6827 | -123.0021 | -122.624 | -122.9077 | -122.5296
419.1094 | 123.2346 | -122.8821 | 0.23804 | 0.06691 | -0.063415 | 0.006315 | -0.034174 | 0.06831 | 0.035221 | -0.062717 | -0.025347 | 0.14332 | 0.014094 | -0.15674 | 122.9401 | 123.0175 | 122.5483 | 122.6919 | 122.949 | 122.8187 | 122.8884 | 122.8479 | 122.9504 | 122.9173 | 122.8194 | -0.025347 | 0.14332 | 0.014094 | -0.15674 | 122.9401 | 123.0175 | 122.5483 | 122.6919 | -122.9655 | -122.5736 | -122.926 | -122.5342
420.7812 | 123.2025 | -122.8821 | 0.2243 | 0.057754 | -0.063415 | 0.006315 | -0.043331 | 0.06831 | 0.030642 | -0.062717 | -0.061975 | 0.13874 | -0.031689 | -0.15216 | 122.9447 | 123.0221 | 122.5483 | 122.6919 | 122.9398 | 122.8187 | 122.8884 | 122.8387 | 122.9504 | 122.9127 | 122.8194 | -0.061975 | 0.13874 | -0.031689 | -0.15216 | 122.9447 | 123.0221 | 122.5483 | 122.6919 | -123.0067 | -122.6102 | -122.9764 | -122.58
422.5156 | 123.1247 | -122.9233 | 0.26093 | 0.062332 | -0.063415 | 0.010893 | -0.043331 | 0.072888 | 0.030642 | -0.062717 | -0.071132 | 0.1479 | -0.050002 | -0.14758 | 122.9401 | 123.0267 | 122.5574 | 122.7056 | 122.9856 | 122.8599 | 122.9342 | 122.8799 | 122.9962 | 122.9539 | 122.8606 | -0.071132 | 0.1479 | -0.050002 | -0.14758 | 122.9401 | 123.0267 | 122.5574 | 122.7056 | -123.0113 | -122.6286 | -122.9901 | -122.6074
424.25 | 123.1934 | -122.9095 | 0.23346 | 0.062332 | -0.067994 | 0.006315 | -0.038752 | 0.082044 | 0.030642 | -0.053561 | -0.084867 | 0.12501 | -0.072894 | -0.15216 | 122.963 | 123.045 | 122.5803 | 122.7148 | 122.9719 | 122.8416 | 122.9159 | 122.8708 | 122.9916 | 122.9402 | 122.856 | -0.084867 | 0.12501 | -0.072894 | -0.15216 | 122.963 | 123.045 | 122.5803 | 122.7148 | -123.0479 | -122.6652 | -123.0359 | -122.6532
425.9844 | 123.1705 | -122.9233 | 0.24261 | 0.06691 | -0.063415 | 0.001736 | -0.034174 | 0.06831 | 0.039799 | -0.053561 | -0.089445 | 0.12501 | -0.045424 | -0.16131 | 122.9585 | 123.0359 | 122.5666 | 122.7148 | 122.9902 | 122.8599 | 122.925 | 122.8891 | 122.9916 | 122.9631 | 122.8697 | -0.089445 | 0.12501 | -0.045424 | -0.16131 | 122.9585 | 123.0359 | 122.5666 | 122.7148 | -123.0479 | -122.656 | -123.0039 | -122.612
427.6719 | 123.1567 | -122.9416 | 0.24261 | 0.062332 | -0.067994 | 0.010893 | -0.038752 | 0.072888 | 0.035221 | -0.053561 | -0.066553 | 0.12958 | -0.050002 | -0.15216 | 122.963 | 123.0359 | 122.5757 | 122.7193 | 123.0039 | 122.8736 | 122.9525 | 122.9028 | 123.0145 | 122.9768 | 122.888 | -0.066553 | 0.12958 | -0.050002 | -0.15216 | 122.963 | 123.0359 | 122.5757 | 122.7193 | -123.0296 | -122.6423 | -123.013 | -122.6257
429.4062 | 123.2025 | -122.8958 | 0.23804 | 0.071489 | -0.072572 | 0.006315 | -0.043331 | 0.072888 | 0.026064 | -0.058139 | -0.061975 | 0.13416 | -0.036267 | -0.15674 | 122.9401 | 123.0313 | 122.562 | 122.7056 | 122.9673 | 122.8232 | 122.9021 | 122.8525 | 122.9687 | 122.9219 | 122.8377 | -0.061975 | 0.13416 | -0.036267 | -0.15674 | 122.9401 | 123.0313 | 122.562 | 122.7056 | -123.0021 | -122.624 | -122.9764 | -122.5983
431.1562 | 123.262 | -122.8775 | 0.2243 | 0.057754 | -0.072572 | 0.006315 | -0.043331 | 0.082044 | 0.030642 | -0.062717 | -0.071132 | 0.13874 | -0.031689 | -0.15674 | 122.9401 | 123.0267 | 122.5529 | 122.7102 | 122.9353 | 122.8049 | 122.8838 | 122.8342 | 122.9595 | 122.9081 | 122.8148 | -0.071132 | 0.13874 | -0.031689 | -0.15674 | 122.9401 | 123.0267 | 122.5529 | 122.7102 | -123.0113 | -122.624 | -122.9718 | -122.5845
432.8438 | 123.2758 | -122.8729 | 0.21973 | 0.057754 | -0.058836 | 0.006315 | -0.043331 | 0.077466 | 0.030642 | -0.058139 | -0.071132 | 0.13874 | -0.027111 | -0.14758 | 122.931 | 123.0267 | 122.5529 | 122.6964 | 122.9307 | 122.8141 | 122.8792 | 122.8296 | 122.9504 | 122.9036 | 122.8148 | -0.071132 | 0.13874 | -0.027111 | -0.14758 | 122.931 | 123.0267 | 122.5529 | 122.6964 | -123.0021 | -122.624 | -122.9581 | -122.58
434.5781 | 123.2437 | -122.8546 | 0.22888 | 0.057754 | -0.058836 | 0.001736 | -0.043331 | 0.072888 | 0.030642 | -0.062717 | -0.052818 | 0.13416 | -0.022532 | -0.15674 | 122.9401 | 123.0221 | 122.5529 | 122.701 | 122.9124 | 122.7958 | 122.8563 | 122.8113 | 122.9275 | 122.8853 | 122.7919 | -0.052818 | 0.13416 | -0.022532 | -0.15674 | 122.9401 | 123.0221 | 122.5529 | 122.701 | -122.993 | -122.6057 | -122.9627 | -122.5754
436.3125 | 123.2483 | -122.85 | 0.21973 | 0.06691 | -0.063415 | 0.006315 | -0.034174 | 0.06831 | 0.021485 | -0.062717 | -0.089445 | 0.12958 | -0.059159 | -0.15216 | 122.9356 | 123.013 | 122.5483 | 122.6919 | 122.9169 | 122.7866 | 122.8564 | 122.8159 | 122.9183 | 122.8715 | 122.7873 | -0.089445 | 0.12958 | -0.059159 | -0.15216 | 122.9356 | 123.013 | 122.5483 | 122.6919 | -123.025 | -122.6377 | -122.9947 | -122.6074
438.0625 | 123.1567 | -122.8867 | 0.24261 | 0.06691 | -0.063415 | 0.006315 | -0.038752 | 0.072888 | 0.039799 | -0.044405 | -0.048239 | 0.13416 | -0.031689 | -0.15674 | 122.9356 | 123.013 | 122.5437 | 122.6964 | 122.9536 | 122.8232 | 122.893 | 122.8479 | 122.9595 | 122.9265 | 122.8423 | -0.048239 | 0.13416 | -0.031689 | -0.15674 | 122.9356 | 123.013 | 122.5437 | 122.6964 | -122.9838 | -122.5919 | -122.9673 | -122.5754
439.75 | 123.1018 | -122.905 | 0.2655 | 0.06691 | -0.063415 | 0.015472 | -0.034174 | 0.072888 | 0.035221 | -0.053561 | -0.061975 | 0.13874 | -0.022532 | -0.14758 | 122.9264 | 123.0267 | 122.5529 | 122.6919 | 122.9719 | 122.8416 | 122.9204 | 122.8708 | 122.9779 | 122.9402 | 122.8514 | -0.061975 | 0.13874 | -0.022532 | -0.14758 | 122.9264 | 123.0267 | 122.5529 | 122.6919 | -122.9884 | -122.6148 | -122.9489 | -122.5754
441.4844 | 123.1567 | -122.905 | 0.25635 | 0.062332 | -0.058836 | 0.010893 | -0.043331 | 0.072888 | 0.030642 | -0.062717 | -0.080288 | 0.13416 | -0.027111 | -0.15216 | 122.9401 | 123.0175 | 122.5529 | 122.6919 | 122.9673 | 122.8461 | 122.9159 | 122.8616 | 122.9779 | 122.9356 | 122.8423 | -0.080288 | 0.13416 | -0.027111 | -0.15216 | 122.9401 | 123.0175 | 122.5529 | 122.6919 | -123.0204 | -122.6331 | -122.9673 | -122.58
443.2344 | 123.1338 | -122.8958 | 0.24719 | 0.06691 | -0.049678 | 0.001736 | -0.038752 | 0.072888 | 0.030642 | -0.058139 | -0.007033 | 0.1479 | 0.059877 | -0.15216 | 122.9264 | 123.0084 | 122.5437 | 122.6919 | 122.9627 | 122.8461 | 122.8975 | 122.8571 | 122.9687 | 122.9265 | 122.8377 | -0.007033 | 0.1479 | 0.059877 | -0.15216 | 122.9264 | 123.0084 | 122.5437 | 122.6919 | -122.9334 | -122.5507 | -122.8665 | -122.4838
444.9844 | 123.143 | -122.9095 | 0.26093 | 0.057754 | -0.058836 | 0.006315 | -0.038752 | 0.077466 | 0.030642 | -0.062717 | -0.057396 | 0.14332 | -0.022532 | -0.14758 | 122.9264 | 123.0038 | 122.5483 | 122.6873 | 122.9673 | 122.8507 | 122.9159 | 122.8708 | 122.987 | 122.9402 | 122.8468 | -0.057396 | 0.14332 | -0.022532 | -0.14758 | 122.9264 | 123.0038 | 122.5483 | 122.6873 | -122.9838 | -122.6057 | -122.9489 | -122.5708
446.6719 | 123.1796 | -122.8729 | 0.20599 | 0.057754 | -0.063415 | 0.001736 | -0.043331 | 0.06831 | 0.039799 | -0.053561 | -0.089445 | 0.13874 | -0.027111 | -0.15674 | 122.9264 | 123.0084 | 122.5345 | 122.6827 | 122.9307 | 122.8095 | 122.8747 | 122.8296 | 122.9412 | 122.9127 | 122.8194 | -0.089445 | 0.13874 | -0.027111 | -0.15674 | 122.9264 | 123.0084 | 122.5345 | 122.6827 | -123.0159 | -122.624 | -122.9535 | -122.5616
448.4062 | 123.2208 | -122.8683 | 0.21973 | 0.057754 | -0.054257 | 0.001736 | -0.038752 | 0.072888 | 0.026064 | -0.062717 | -0.084867 | 0.12501 | -0.063737 | -0.15674 | 122.931 | 123.013 | 122.5437 | 122.6873 | 122.9261 | 122.8141 | 122.8701 | 122.8296 | 122.9412 | 122.8944 | 122.8056 | -0.084867 | 0.12501 | -0.063737 | -0.15674 | 122.931 | 123.013 | 122.5437 | 122.6873 | -123.0159 | -122.6286 | -122.9947 | -122.6074
450.1562 | 123.2391 | -122.8592 | 0.25177 | 0.062332 | -0.054257 | 0.010893 | -0.043331 | 0.077466 | 0.030642 | -0.053561 | -0.061975 | 0.12501 | -0.027111 | -0.14758 | 122.931 | 123.0038 | 122.5391 | 122.6736 | 122.9215 | 122.8049 | 122.8701 | 122.8159 | 122.9367 | 122.8898 | 122.8056 | -0.061975 | 0.12501 | -0.027111 | -0.14758 | 122.931 | 123.0038 | 122.5391 | 122.6736 | -122.993 | -122.6011 | -122.9581 | -122.5662
451.8438 | 123.2346 | -122.8592 | 0.24261 | 0.057754 | -0.067994 | 0.006315 | -0.038752 | 0.072888 | 0.035221 | -0.062717 | -0.080288 | 0.13874 | -0.031689 | -0.15216 | 122.9218 | 122.9946 | 122.5391 | 122.6781 | 122.9169 | 122.7912 | 122.8655 | 122.8204 | 122.9321 | 122.8944 | 122.7965 | -0.080288 | 0.13874 | -0.031689 | -0.15216 | 122.9218 | 122.9946 | 122.5391 | 122.6781 | -123.0021 | -122.6194 | -122.9535 | -122.5708
453.5781 | 123.0972 | -122.9141 | 0.25635 | 0.053175 | -0.067994 | 0.010893 | -0.038752 | 0.072888 | 0.030642 | -0.058139 | -0.084867 | 0.14332 | -0.008798 | -0.15216 | 122.9264 | 123.0084 | 122.5345 | 122.6736 | 122.9673 | 122.8461 | 122.925 | 122.8754 | 122.987 | 122.9448 | 122.856 | -0.084867 | 0.14332 | -0.008798 | -0.15216 | 122.9264 | 123.0084 | 122.5345 | 122.6736 | -123.0113 | -122.6194 | -122.9352 | -122.5433
455.3281 | 123.2071 | -122.8363 | 0.23804 | 0.06691 | -0.063415 | 0.010893 | -0.043331 | 0.063733 | 0.030642 | -0.053561 | -0.089445 | 0.14332 | -0.063737 | -0.15674 | 122.9172 | 122.9992 | 122.5345 | 122.6781 | 122.9032 | 122.7729 | 122.8472 | 122.793 | 122.9 | 122.8669 | 122.7827 | -0.089445 | 0.14332 | -0.063737 | -0.15674 | 122.9172 | 122.9992 | 122.5345 | 122.6781 | -123.0067 | -122.624 | -122.981 | -122.5983
457.0625 | 123.2391 | -122.8409 | 0.23346 | 0.053175 | -0.058836 | 0.010893 | -0.047909 | 0.077466 | 0.030642 | -0.058139 | -0.089445 | 0.13874 | -0.050002 | -0.15216 | 122.9218 | 122.9992 | 122.53 | 122.6781 | 122.8941 | 122.782 | 122.8518 | 122.793 | 122.9183 | 122.8715 | 122.7827 | -0.089445 | 0.13874 | -0.050002 | -0.15216 | 122.9218 | 122.9992 | 122.53 | 122.6781 | -123.0113 | -122.6194 | -122.9718 | -122.58
458.7344 | 123.1476 | -122.8821 | 0.27008 | 0.062332 | -0.058836 | 0.010893 | -0.034174 | 0.06831 | 0.035221 | -0.053561 | -0.084867 | 0.12958 | -0.063737 | -0.15216 | 122.9264 | 122.9946 | 122.5391 | 122.6781 | 122.9444 | 122.8232 | 122.893 | 122.8479 | 122.9504 | 122.9173 | 122.8285 | -0.084867 | 0.12958 | -0.063737 | -0.15216 | 122.9264 | 122.9946 | 122.5391 | 122.6781 | -123.0113 | -122.624 | -122.9901 | -122.6029
460.5 | 123.2025 | -122.8455 | 0.25635 | 0.062332 | -0.063415 | 0.015472 | -0.043331 | 0.072888 | 0.021485 | -0.058139 | -0.094024 | 0.13416 | -0.050002 | -0.15216 | 122.9035 | 122.9992 | 122.5208 | 122.6598 | 122.9078 | 122.782 | 122.8609 | 122.8021 | 122.9183 | 122.8669 | 122.7873 | -0.094024 | 0.13416 | -0.050002 | -0.15216 | 122.9035 | 122.9992 | 122.5208 | 122.6598 | -122.9975 | -122.6148 | -122.9535 | -122.5708
462.1719 | 123.1155 | -122.8775 | 0.26093 | 0.062332 | -0.058836 | 0.001736 | -0.043331 | 0.06831 | 0.039799 | -0.058139 | -0.084867 | 0.13416 | -0.040846 | -0.15216 | 122.9127 | 122.9946 | 122.5208 | 122.6507 | 122.9398 | 122.8187 | 122.8792 | 122.8342 | 122.9458 | 122.9173 | 122.8194 | -0.084867 | 0.13416 | -0.040846 | -0.15216 | 122.9127 | 122.9946 | 122.5208 | 122.6507 | -122.9975 | -122.6057 | -122.9535 | -122.5616
463.9062 | 123.2162 | -122.8363 | 0.2243 | 0.057754 | -0.067994 | 0.015472 | -0.043331 | 0.077466 | 0.030642 | -0.053561 | -0.048239 | 0.13416 | -0.017954 | -0.15674 | 122.9081 | 122.9992 | 122.5162 | 122.6598 | 122.8941 | 122.7683 | 122.8518 | 122.793 | 122.9138 | 122.8669 | 122.7827 | -0.048239 | 0.13416 | -0.017954 | -0.15674 | 122.9081 | 122.9992 | 122.5162 | 122.6598 | -122.9563 | -122.5645 | -122.926 | -122.5342
465.6562 | 123.1979 | -122.8409 | 0.23346 | 0.062332 | -0.063415 | 0.006315 | -0.038752 | 0.077466 | 0.026064 | -0.053561 | -0.057396 | 0.13874 | 0.009515 | -0.14758 | 122.9127 | 122.9901 | 122.5208 | 122.6644 | 122.9032 | 122.7775 | 122.8472 | 122.8021 | 122.9183 | 122.8669 | 122.7873 | -0.057396 | 0.13874 | 0.009515 | -0.14758 | 122.9127 | 122.9901 | 122.5208 | 122.6644 | -122.9701 | -122.5782 | -122.9032 | -122.5113
467.3906 | 123.1979 | -122.8683 | 0.24261 | 0.06691 | -0.058836 | 0.015472 | -0.034174 | 0.06831 | 0.030642 | -0.058139 | -0.089445 | 0.12958 | -0.045424 | -0.15674 | 122.9081 | 122.9901 | 122.5116 | 122.6552 | 122.9353 | 122.8095 | 122.8838 | 122.8342 | 122.9367 | 122.899 | 122.8102 | -0.089445 | 0.12958 | -0.045424 | -0.15674 | 122.9081 | 122.9901 | 122.5116 | 122.6552 | -122.9975 | -122.6011 | -122.9535 | -122.5571
469.125 | 123.2117 | -122.8226 | 0.24261 | 0.062332 | -0.058836 | 0.010893 | -0.043331 | 0.072888 | 0.039799 | -0.053561 | -0.061975 | 0.15248 | -0.027111 | -0.15216 | 122.9035 | 122.9946 | 122.5254 | 122.6507 | 122.8849 | 122.7637 | 122.8335 | 122.7792 | 122.8955 | 122.8624 | 122.769 | -0.061975 | 0.15248 | -0.027111 | -0.15216 | 122.9035 | 122.9946 | 122.5254 | 122.6507 | -122.9655 | -122.5874 | -122.9306 | -122.5525
470.7969 | 123.1155 | -122.8546 | 0.26093 | 0.06691 | -0.058836 | 0.006315 | -0.043331 | 0.06831 | 0.035221 | -0.058139 | -0.071132 | 0.1479 | -0.027111 | -0.15216 | 122.8989 | 122.9855 | 122.5162 | 122.6552 | 122.9215 | 122.7958 | 122.8609 | 122.8113 | 122.9229 | 122.8898 | 122.7965 | -0.071132 | 0.1479 | -0.027111 | -0.15216 | 122.8989 | 122.9855 | 122.5162 | 122.6552 | -122.9701 | -122.5874 | -122.926 | -122.5433
472.5469 | 123.1064 | -122.8317 | 0.27924 | 0.06691 | -0.054257 | 0.015472 | -0.043331 | 0.072888 | 0.035221 | -0.062717 | -0.066553 | 0.16164 | 0.014094 | -0.15216 | 122.8852 | 122.9626 | 122.4933 | 122.6415 | 122.8986 | 122.7775 | 122.8472 | 122.7884 | 122.9046 | 122.8669 | 122.769 | -0.066553 | 0.16164 | 0.014094 | -0.15216 | 122.8852 | 122.9626 | 122.4933 | 122.6415 | -122.9518 | -122.5599 | -122.8711 | -122.4792
474.2188 | 123.0881 | -122.8226 | 0.29755 | 0.06691 | -0.067994 | 0.010893 | -0.038752 | 0.077466 | 0.026064 | -0.044405 | -0.07571 | 0.15706 | -0.050002 | -0.15216 | 122.8806 | 122.9626 | 122.4933 | 122.6324 | 122.8895 | 122.7546 | 122.8335 | 122.7838 | 122.9 | 122.8486 | 122.7782 | -0.07571 | 0.15706 | -0.050002 | -0.15216 | 122.8806 | 122.9626 | 122.4933 | 122.6324 | -122.9563 | -122.569 | -122.9306 | -122.5433
475.9688 | 123.1659 | -122.7859 | 0.28381 | 0.062332 | -0.054257 | 0.010893 | -0.038752 | 0.072888 | 0.035221 | -0.053561 | 0.006703 | 0.16622 | 0.018672 | -0.15674 | 122.876 | 122.9534 | 122.4888 | 122.6324 | 122.8483 | 122.7317 | 122.7968 | 122.7472 | 122.8588 | 122.8212 | 122.7324 | 0.006703 | 0.16622 | 0.018672 | -0.15674 | 122.876 | 122.9534 | 122.4888 | 122.6324 | -122.8693 | -122.4821 | -122.8574 | -122.4701
477.6562 | 123.111 | -122.8455 | 0.31128 | 0.062332 | -0.063415 | 0.010893 | -0.034174 | 0.06831 | 0.035221 | -0.058139 | -0.057396 | 0.16622 | 0.009515 | -0.15216 | 122.876 | 122.958 | 122.4933 | 122.6324 | 122.9078 | 122.782 | 122.8564 | 122.8113 | 122.9138 | 122.8807 | 122.7873 | -0.057396 | 0.16622 | 0.009515 | -0.15216 | 122.876 | 122.958 | 122.4933 | 122.6324 | -122.9334 | -122.5507 | -122.8665 | -122.4838
479.4062 | 123.1705 | -122.8088 | 0.27466 | 0.06691 | -0.063415 | 0.006315 | -0.047909 | 0.06831 | 0.026064 | -0.062717 | -0.034504 | 0.17079 | 0.036985 | -0.15216 | 122.8577 | 122.9397 | 122.4842 | 122.6186 | 122.8757 | 122.7454 | 122.8152 | 122.7609 | 122.8771 | 122.8349 | 122.7461 | -0.034504 | 0.17079 | 0.036985 | -0.15216 | 122.8577 | 122.9397 | 122.4842 | 122.6186 | -122.8922 | -122.5187 | -122.8207 | -122.4472
481.1562 | 123.1934 | -122.8043 | 0.2655 | 0.057754 | -0.067994 | 0.001736 | -0.043331 | 0.072888 | 0.030642 | -0.058139 | -0.061975 | 0.17537 | -0.004219 | -0.143 | 122.8623 | 122.9443 | 122.4842 | 122.6095 | 122.862 | 122.7363 | 122.806 | 122.7609 | 122.8771 | 122.8349 | 122.7461 | -0.061975 | 0.17537 | -0.004219 | -0.143 | 122.8623 | 122.9443 | 122.4842 | 122.6095 | -122.9243 | -122.5461 | -122.8665 | -122.4884
482.9062 | 123.1338 | -122.7859 | 0.27924 | 0.062332 | -0.058836 | 0.015472 | -0.038752 | 0.06831 | 0.039799 | -0.062717 | -0.01619 | 0.16622 | -0.013376 | -0.15216 | 122.8669 | 122.9489 | 122.475 | 122.614 | 122.8483 | 122.7271 | 122.8014 | 122.7472 | 122.8543 | 122.8257 | 122.7232 | -0.01619 | 0.16622 | -0.013376 | -0.15216 | 122.8669 | 122.9489 | 122.475 | 122.614 | -122.8831 | -122.4912 | -122.8803 | -122.4884
484.5781 | 123.1934 | -122.7814 | 0.27924 | 0.053175 | -0.054257 | 0.006315 | -0.043331 | 0.077466 | 0.026064 | -0.062717 | -0.039082 | 0.17079 | -0.013376 | -0.16131 | 122.8577 | 122.9443 | 122.475 | 122.6095 | 122.8345 | 122.7271 | 122.7877 | 122.738 | 122.8588 | 122.8074 | 122.7187 | -0.039082 | 0.17079 | -0.013376 | -0.16131 | 122.8577 | 122.9443 | 122.475 | 122.6095 | -122.8968 | -122.5141 | -122.8711 | -122.4884
486.3125 | 123.0743 | -122.8226 | 0.27924 | 0.062332 | -0.058836 | 0.006315 | -0.038752 | 0.072888 | 0.035221 | -0.058139 | -0.011611 | 0.17537 | 0.009515 | -0.14758 | 122.8669 | 122.9443 | 122.475 | 122.614 | 122.8849 | 122.7637 | 122.8289 | 122.7838 | 122.8955 | 122.8578 | 122.7644 | -0.011611 | 0.17537 | 0.009515 | -0.14758 | 122.8669 | 122.9443 | 122.475 | 122.614 | -122.8785 | -122.4866 | -122.8574 | -122.4655
488.0625 | 123.1659 | -122.7722 | 0.28381 | 0.057754 | -0.054257 | 0.010893 | -0.047909 | 0.077466 | 0.035221 | -0.058139 | -0.057396 | 0.16164 | 0.009515 | -0.15216 | 122.8623 | 122.9534 | 122.4842 | 122.614 | 122.83 | 122.718 | 122.7831 | 122.7243 | 122.8497 | 122.8074 | 122.7141 | -0.057396 | 0.16164 | 0.009515 | -0.15216 | 122.8623 | 122.9534 | 122.4842 | 122.614 | -122.9197 | -122.5416 | -122.8528 | -122.4747
489.7344 | 123.2162 | -122.8226 | 0.27008 | 0.06691 | -0.058836 | 0.006315 | -0.043331 | 0.077466 | 0.035221 | -0.053561 | -0.071132 | 0.15706 | -0.036267 | -0.15674 | 122.876 | 122.9443 | 122.4888 | 122.614 | 122.8895 | 122.7637 | 122.8289 | 122.7792 | 122.9 | 122.8578 | 122.769 | -0.071132 | 0.15706 | -0.036267 | -0.15674 | 122.876 | 122.9443 | 122.4888 | 122.614 | -122.9472 | -122.5599 | -122.9123 | -122.525
491.4688 | 123.1979 | -122.7997 | 0.24261 | 0.06691 | -0.054257 | 0.006315 | -0.043331 | 0.072888 | 0.030642 | -0.053561 | -0.07571 | 0.16164 | -0.031689 | -0.15216 | 122.8715 | 122.958 | 122.4888 | 122.614 | 122.8666 | 122.7454 | 122.806 | 122.7564 | 122.8726 | 122.8303 | 122.7461 | -0.07571 | 0.16164 | -0.031689 | -0.15216 | 122.8715 | 122.958 | 122.4888 | 122.614 | -122.9472 | -122.5645 | -122.9032 | -122.5204
493.2344 | 123.0606 | -122.85 | 0.31128 | 0.06691 | -0.058836 | 0.010893 | -0.047909 | 0.072888 | 0.035221 | -0.058139 | -0.039082 | 0.15248 | -0.008798 | -0.15216 | 122.8852 | 122.9534 | 122.4933 | 122.6186 | 122.9169 | 122.7912 | 122.8609 | 122.8021 | 122.9229 | 122.8853 | 122.7919 | -0.039082 | 0.15248 | -0.008798 | -0.15216 | 122.8852 | 122.9534 | 122.4933 | 122.6186 | -122.9243 | -122.5324 | -122.894 | -122.5021
494.9844 | 123.0698 | -122.8317 | 0.27466 | 0.057754 | -0.058836 | 0.015472 | -0.043331 | 0.077466 | 0.039799 | -0.048983 | -0.007033 | 0.15706 | 0.064455 | -0.14758 | 122.8944 | 122.9672 | 122.4979 | 122.6324 | 122.8895 | 122.7729 | 122.8472 | 122.7884 | 122.9092 | 122.8715 | 122.7827 | -0.007033 | 0.15706 | 0.064455 | -0.14758 | 122.8944 | 122.9672 | 122.4979 | 122.6324 | -122.9014 | -122.5049 | -122.8299 | -122.4335
496.6562 | 123.0606 | -122.8638 | 0.27924 | 0.057754 | -0.058836 | 0.015472 | -0.034174 | 0.072888 | 0.035221 | -0.058139 | -0.034504 | 0.1479 | 0.018672 | -0.15216 | 122.8898 | 122.9718 | 122.4979 | 122.6324 | 122.9215 | 122.8049 | 122.8792 | 122.8296 | 122.9367 | 122.899 | 122.8056 | -0.034504 | 0.1479 | 0.018672 | -0.15216 | 122.8898 | 122.9718 | 122.4979 | 122.6324 | -122.9243 | -122.5324 | -122.8711 | -122.4792
498.4062 | 123.1979 | -122.8271 | 0.24719 | 0.053175 | -0.067994 | 0.010893 | -0.043331 | 0.072888 | 0.035221 | -0.062717 | -0.080288 | 0.14332 | -0.050002 | -0.15216 | 122.8898 | 122.9763 | 122.5071 | 122.6369 | 122.8803 | 122.7592 | 122.838 | 122.7838 | 122.9 | 122.8624 | 122.7644 | -0.080288 | 0.14332 | -0.050002 | -0.15216 | 122.8898 | 122.9763 | 122.5071 | 122.6369 | -122.9701 | -122.5874 | -122.9398 | -122.5571
500.1562 | 123.0743 | -122.8546 | 0.27924 | 0.057754 | -0.058836 | 0.010893 | -0.043331 | 0.072888 | 0.035221 | -0.058139 | -0.025347 | 0.15706 | 0.055298 | -0.14758 | 122.8944 | 122.9809 | 122.5071 | 122.6507 | 122.9124 | 122.7958 | 122.8655 | 122.8113 | 122.9275 | 122.8898 | 122.7965 | -0.025347 | 0.15706 | 0.055298 | -0.14758 | 122.8944 | 122.9809 | 122.5071 | 122.6507 | -122.9197 | -122.5324 | -122.8391 | -122.4518
501.8281 | 123.1201 | -122.8363 | 0.27924 | 0.062332 | -0.058836 | 0.006315 | -0.047909 | 0.072888 | 0.039799 | -0.058139 | -0.020768 | 0.16622 | 0.027829 | -0.15216 | 122.8806 | 122.958 | 122.4979 | 122.6278 | 122.8986 | 122.7775 | 122.8426 | 122.7884 | 122.9092 | 122.8761 | 122.7782 | -0.020768 | 0.16622 | 0.027829 | -0.15216 | 122.8806 | 122.958 | 122.4979 | 122.6278 | -122.9014 | -122.5187 | -122.8528 | -122.4701
503.5781 | 123.1155 | -122.8317 | 0.28381 | 0.06691 | -0.058836 | 0.010893 | -0.043331 | 0.072888 | 0.039799 | -0.053561 | -0.061975 | 0.1479 | -0.022532 | -0.15216 | 122.8852 | 122.9626 | 122.5025 | 122.6324 | 122.8986 | 122.7729 | 122.8426 | 122.7884 | 122.9046 | 122.8715 | 122.7782 | -0.061975 | 0.1479 | -0.022532 | -0.15216 | 122.8852 | 122.9626 | 122.5025 | 122.6324 | -122.9472 | -122.5645 | -122.9077 | -122.525
505.3281 | 123.0743 | -122.8592 | 0.28381 | 0.062332 | -0.058836 | 0.015472 | -0.038752 | 0.077466 | 0.044377 | -0.048983 | -0.084867 | 0.14332 | 0.009515 | -0.15216 | 122.8852 | 122.9672 | 122.5025 | 122.6324 | 122.9215 | 122.8004 | 122.8747 | 122.8204 | 122.9367 | 122.9036 | 122.8102 | -0.084867 | 0.14332 | 0.009515 | -0.15216 | 122.8852 | 122.9672 | 122.5025 | 122.6324 | -122.9701 | -122.5874 | -122.8757 | -122.493
507.0625 | 123.1567 | -122.818 | 0.2243 | 0.062332 | -0.063415 | 0.010893 | -0.043331 | 0.072888 | 0.039799 | -0.053561 | -0.07571 | 0.14332 | -0.008798 | -0.15216 | 122.8852 | 122.9626 | 122.5025 | 122.6324 | 122.8803 | 122.7546 | 122.8289 | 122.7747 | 122.8909 | 122.8578 | 122.7644 | -0.07571 | 0.14332 | -0.008798 | -0.15216 | 122.8852 | 122.9626 | 122.5025 | 122.6324 | -122.9609 | -122.5782 | -122.894 | -122.5113
508.75 | 123.1201 | -122.8363 | 0.25635 | 0.053175 | -0.054257 | 0.010893 | -0.043331 | 0.082044 | 0.039799 | -0.053561 | -0.080288 | 0.14332 | -0.045424 | -0.15216 | 122.9035 | 122.9718 | 122.5116 | 122.6415 | 122.8895 | 122.782 | 122.8472 | 122.793 | 122.9183 | 122.8761 | 122.7827 | -0.080288 | 0.14332 | -0.045424 | -0.15216 | 122.9035 | 122.9718 | 122.5116 | 122.6415 | -122.9838 | -122.5919 | -122.9489 | -122.5571
510.5 | 123.143 | -122.8592 | 0.24261 | 0.057754 | -0.058836 | 0.006315 | -0.047909 | 0.072888 | 0.035221 | -0.058139 | -0.048239 | 0.13874 | 0.004937 | -0.15674 | 122.8898 | 122.9718 | 122.5116 | 122.6369 | 122.9169 | 122.8004 | 122.8655 | 122.8113 | 122.9321 | 122.8944 | 122.8011 | -0.048239 | 0.13874 | 0.004937 | -0.15674 | 122.8898 | 122.9718 | 122.5116 | 122.6369 | -122.938 | -122.5599 | -122.8848 | -122.5067
512.2344 | 123.1796 | -122.8226 | 0.21057 | 0.053175 | -0.058836 | 0.001736 | -0.047909 | 0.072888 | 0.039799 | -0.053561 | -0.01619 | 0.1479 | 0.009515 | -0.15216 | 122.8898 | 122.9763 | 122.5071 | 122.6415 | 122.8757 | 122.7637 | 122.8243 | 122.7747 | 122.8955 | 122.8624 | 122.769 | -0.01619 | 0.1479 | 0.009515 | -0.15216 | 122.8898 | 122.9763 | 122.5071 | 122.6415 | -122.906 | -122.5233 | -122.8803 | -122.4976
513.9844 | 123.0515 | -122.85 | 0.2655 | 0.062332 | -0.054257 | 0.015472 | -0.043331 | 0.072888 | 0.030642 | -0.053561 | -0.089445 | 0.12958 | -0.045424 | -0.15216 | 122.8806 | 122.9763 | 122.5025 | 122.6369 | 122.9124 | 122.7958 | 122.8655 | 122.8067 | 122.9229 | 122.8807 | 122.7965 | -0.089445 | 0.12958 | -0.045424 | -0.15216 | 122.8806 | 122.9763 | 122.5025 | 122.6369 | -122.9701 | -122.5919 | -122.926 | -122.5479
515.6719 | 123.1064 | -122.8226 | 0.25177 | 0.057754 | -0.054257 | 0.006315 | -0.043331 | 0.072888 | 0.030642 | -0.058139 | -0.066553 | 0.13874 | -0.027111 | -0.15674 | 122.8806 | 122.9672 | 122.4933 | 122.6278 | 122.8803 | 122.7683 | 122.8289 | 122.7792 | 122.8955 | 122.8532 | 122.7644 | -0.066553 | 0.13874 | -0.027111 | -0.15674 | 122.8806 | 122.9672 | 122.4933 | 122.6278 | -122.9472 | -122.5599 | -122.9077 | -122.5204
517.4062 | 123.0515 | -122.85 | 0.25177 | 0.062332 | -0.054257 | 0.020051 | -0.043331 | 0.072888 | 0.039799 | -0.053561 | -0.080288 | 0.13874 | -0.050002 | -0.15216 | 122.8898 | 122.9718 | 122.5025 | 122.6278 | 122.9124 | 122.7958 | 122.8701 | 122.8067 | 122.9229 | 122.8898 | 122.7965 | -0.080288 | 0.13874 | -0.050002 | -0.15216 | 122.8898 | 122.9718 | 122.5025 | 122.6278 | -122.9701 | -122.5828 | -122.9398 | -122.5525
519.1406 | 123.0743 | -122.8409 | 0.25177 | 0.071489 | -0.054257 | 0.010893 | -0.038752 | 0.077466 | 0.035221 | -0.048983 | -0.057396 | 0.14332 | -0.017954 | -0.15674 | 122.8898 | 122.9718 | 122.5071 | 122.6324 | 122.9124 | 122.7866 | 122.8518 | 122.8021 | 122.9183 | 122.8761 | 122.7919 | -0.057396 | 0.14332 | -0.017954 | -0.15674 | 122.8898 | 122.9718 | 122.5071 | 122.6324 | -122.9472 | -122.5645 | -122.9077 | -122.525
520.8125 | 123.0469 | -122.8409 | 0.25177 | 0.057754 | -0.049678 | 0.006315 | -0.043331 | 0.082044 | 0.039799 | -0.058139 | -0.061975 | 0.14332 | -0.004219 | -0.15216 | 122.8898 | 122.9672 | 122.5025 | 122.6324 | 122.8986 | 122.7912 | 122.8472 | 122.7976 | 122.9229 | 122.8807 | 122.7827 | -0.061975 | 0.14332 | -0.004219 | -0.15216 | 122.8898 | 122.9672 | 122.5025 | 122.6324 | -122.9518 | -122.5645 | -122.894 | -122.5067
522.5625 | 123.1705 | -122.8271 | 0.21057 | 0.057754 | -0.049678 | 0.010893 | -0.043331 | 0.082044 | 0.039799 | -0.058139 | -0.061975 | 0.13416 | -0.031689 | -0.15216 | 122.8852 | 122.9672 | 122.5025 | 122.6415 | 122.8849 | 122.7775 | 122.838 | 122.7838 | 122.9092 | 122.8669 | 122.769 | -0.061975 | 0.13416 | -0.031689 | -0.15216 | 122.8852 | 122.9672 | 122.5025 | 122.6415 | -122.9472 | -122.5645 | -122.9169 | -122.5342
524.3125 | 123.0652 | -122.8638 | 0.25635 | 0.062332 | -0.054257 | 0.015472 | -0.043331 | 0.077466 | 0.044377 | -0.053561 | -0.057396 | 0.13874 | -0.036267 | -0.15216 | 122.8898 | 122.9718 | 122.5071 | 122.6461 | 122.9261 | 122.8095 | 122.8792 | 122.8204 | 122.9412 | 122.9081 | 122.8102 | -0.057396 | 0.13874 | -0.036267 | -0.15216 | 122.8898 | 122.9718 | 122.5071 | 122.6461 | -122.9472 | -122.5645 | -122.926 | -122.5433
526 | 123.0652 | -122.8592 | 0.24719 | 0.062332 | -0.058836 | 0.015472 | -0.047909 | 0.086622 | 0.044377 | -0.053561 | -0.080288 | 0.12958 | 0.004937 | -0.14758 | 122.8944 | 122.9763 | 122.5116 | 122.6461 | 122.9215 | 122.8004 | 122.8747 | 122.8113 | 122.9458 | 122.9036 | 122.8056 | -0.080288 | 0.12958 | 0.004937 | -0.14758 | 122.8944 | 122.9763 | 122.5116 | 122.6461 | -122.9746 | -122.5919 | -122.8894 | -122.5067
527.75 | 123.1934 | -122.8134 | 0.2243 | 0.062332 | -0.058836 | 0.015472 | -0.052488 | 0.077466 | 0.044377 | -0.062717 | -0.043661 | 0.13416 | -0.017954 | -0.15216 | 122.8898 | 122.9763 | 122.5116 | 122.6415 | 122.8757 | 122.7546 | 122.8289 | 122.7609 | 122.8909 | 122.8578 | 122.7507 | -0.043661 | 0.13416 | -0.017954 | -0.15216 | 122.8898 | 122.9763 | 122.5116 | 122.6415 | -122.9334 | -122.5553 | -122.9077 | -122.5296
529.4844 | 123.1842 | -122.8088 | 0.2243 | 0.062332 | -0.058836 | 0.006315 | -0.038752 | 0.077466 | 0.030642 | -0.058139 | -0.043661 | 0.1479 | -0.022532 | -0.16131 | 122.8944 | 122.9763 | 122.5116 | 122.6507 | 122.8712 | 122.75 | 122.8152 | 122.7701 | 122.8863 | 122.8395 | 122.7507 | -0.043661 | 0.1479 | -0.022532 | -0.16131 | 122.8944 | 122.9763 | 122.5116 | 122.6507 | -122.938 | -122.5553 | -122.9169 | -122.5342
531.2188 | 123.1659 | -122.8134 | 0.22888 | 0.053175 | -0.063415 | 0.010893 | -0.043331 | 0.06831 | 0.044377 | -0.053561 | 0.006703 | 0.14332 | 0.004937 | -0.15674 | 122.8989 | 122.9809 | 122.5116 | 122.6461 | 122.8666 | 122.75 | 122.8243 | 122.7701 | 122.8817 | 122.8578 | 122.7599 | 0.006703 | 0.14332 | 0.004937 | -0.15674 | 122.8989 | 122.9809 | 122.5116 | 122.6461 | -122.8922 | -122.5049 | -122.894 | -122.5067
532.9844 | 123.1476 | -122.8134 | 0.22888 | 0.057754 | -0.054257 | 0.015472 | -0.034174 | 0.077466 | 0.035221 | -0.058139 | -0.061975 | 0.14332 | -0.036267 | -0.16131 | 122.8944 | 122.9763 | 122.5116 | 122.6461 | 122.8712 | 122.7592 | 122.8289 | 122.7792 | 122.8909 | 122.8486 | 122.7553 | -0.061975 | 0.14332 | -0.036267 | -0.16131 | 122.8944 | 122.9763 | 122.5116 | 122.6461 | -122.9563 | -122.5736 | -122.9306 | -122.5479
534.7188 | 123.2208 | -122.8134 | 0.2243 | 0.057754 | -0.058836 | 0.010893 | -0.047909 | 0.072888 | 0.044377 | -0.058139 | -0.071132 | 0.12958 | -0.031689 | -0.15216 | 122.8944 | 122.9809 | 122.5116 | 122.6415 | 122.8712 | 122.7546 | 122.8243 | 122.7655 | 122.8863 | 122.8578 | 122.7553 | -0.071132 | 0.12958 | -0.031689 | -0.15216 | 122.8944 | 122.9809 | 122.5116 | 122.6415 | -122.9655 | -122.5828 | -122.926 | -122.5433
536.3906 | 123.0331 | -122.8592 | 0.2243 | 0.06691 | -0.054257 | 0.015472 | -0.034174 | 0.072888 | 0.048956 | -0.048983 | -0.071132 | 0.12043 | -0.05458 | -0.15674 | 122.9035 | 122.9855 | 122.5208 | 122.6507 | 122.9261 | 122.8049 | 122.8747 | 122.825 | 122.9321 | 122.9081 | 122.8102 | -0.071132 | 0.12043 | -0.05458 | -0.15674 | 122.9035 | 122.9855 | 122.5208 | 122.6507 | -122.9746 | -122.5919 | -122.9581 | -122.5754
538.1406 | 123.0515 | -122.8775 | 0.24261 | 0.06691 | -0.054257 | 0.015472 | -0.043331 | 0.06831 | 0.039799 | -0.058139 | -0.034504 | 0.13416 | -0.013376 | -0.15216 | 122.9035 | 122.9809 | 122.5116 | 122.6552 | 122.9444 | 122.8232 | 122.893 | 122.8342 | 122.9458 | 122.9173 | 122.8194 | -0.034504 | 0.13416 | -0.013376 | -0.15216 | 122.9035 | 122.9809 | 122.5116 | 122.6552 | -122.938 | -122.5461 | -122.9169 | -122.525
539.8125 | 123.0469 | -122.8546 | 0.2243 | 0.071489 | -0.054257 | 0.015472 | -0.043331 | 0.077466 | 0.039799 | -0.048983 | -0.057396 | 0.12958 | -0.036267 | -0.15216 | 122.9035 | 122.9763 | 122.5162 | 122.6461 | 122.9261 | 122.8004 | 122.8701 | 122.8113 | 122.9321 | 122.8944 | 122.8056 | -0.057396 | 0.12958 | -0.036267 | -0.15216 | 122.9035 | 122.9763 | 122.5162 | 122.6461 | -122.9609 | -122.5736 | -122.9398 | -122.5525
541.5469 | 123.0743 | -122.8546 | 0.2243 | 0.062332 | -0.049678 | 0.015472 | -0.038752 | 0.077466 | 0.044377 | -0.044405 | -0.029925 | 0.14332 | -0.008798 | -0.14758 | 122.8944 | 122.9718 | 122.5162 | 122.6461 | 122.9169 | 122.8049 | 122.8701 | 122.8159 | 122.9321 | 122.899 | 122.8102 | -0.029925 | 0.14332 | -0.008798 | -0.14758 | 122.8944 | 122.9718 | 122.5162 | 122.6461 | -122.9243 | -122.5461 | -122.9032 | -122.525
543.3281 | 123.0972 | -122.8546 | 0.21973 | 0.06691 | -0.054257 | 0.010893 | -0.043331 | 0.072888 | 0.044377 | -0.058139 | -0.07571 | 0.12958 | -0.022532 | -0.15674 | 122.9035 | 122.9809 | 122.5071 | 122.6461 | 122.9215 | 122.8004 | 122.8655 | 122.8113 | 122.9275 | 122.899 | 122.7965 | -0.07571 | 0.12958 | -0.022532 | -0.15674 | 122.9035 | 122.9809 | 122.5071 | 122.6461 | -122.9792 | -122.5828 | -122.926 | -122.5296
545.0625 | 123.0881 | -122.8363 | 0.22888 | 0.062332 | -0.054257 | 0.010893 | -0.038752 | 0.082044 | 0.039799 | -0.053561 | -0.089445 | 0.13416 | -0.036267 | -0.15674 | 122.8898 | 122.9763 | 122.4979 | 122.6278 | 122.8986 | 122.782 | 122.8472 | 122.7976 | 122.9183 | 122.8761 | 122.7827 | -0.089445 | 0.13416 | -0.036267 | -0.15674 | 122.8898 | 122.9763 | 122.4979 | 122.6278 | -122.9792 | -122.5874 | -122.926 | -122.5342
546.7969 | 123.1064 | -122.8363 | 0.25177 | 0.06691 | -0.058836 | 0.006315 | -0.043331 | 0.077466 | 0.039799 | -0.058139 | -0.029925 | 0.13416 | 0.014094 | -0.14758 | 122.8852 | 122.9718 | 122.4979 | 122.6415 | 122.9032 | 122.7775 | 122.8426 | 122.793 | 122.9138 | 122.8761 | 122.7782 | -0.029925 | 0.13416 | 0.014094 | -0.14758 | 122.8852 | 122.9718 | 122.4979 | 122.6415 | -122.9151 | -122.5278 | -122.8711 | -122.4838
548.4844 | 123.1888 | -122.7859 | 0.23346 | 0.071489 | -0.058836 | 0.006315 | -0.043331 | 0.077466 | 0.035221 | -0.062717 | -0.01619 | 0.13416 | 0.036985 | -0.15674 | 122.8944 | 122.9626 | 122.5025 | 122.6369 | 122.8574 | 122.7271 | 122.7923 | 122.7426 | 122.8634 | 122.8212 | 122.7232 | -0.01619 | 0.13416 | 0.036985 | -0.15674 | 122.8944 | 122.9626 | 122.5025 | 122.6369 | -122.9105 | -122.5187 | -122.8574 | -122.4655
550.1562 | 123.056 | -122.8546 | 0.24261 | 0.06691 | -0.054257 | 0.015472 | -0.047909 | 0.082044 | 0.044377 | -0.048983 | 0.01586 | 0.13416 | 0.046142 | -0.14758 | 122.8989 | 122.9763 | 122.5116 | 122.6415 | 122.9215 | 122.8004 | 122.8701 | 122.8067 | 122.9367 | 122.899 | 122.8056 | 0.01586 | 0.13416 | 0.046142 | -0.14758 | 122.8989 | 122.9763 | 122.5116 | 122.6415 | -122.8831 | -122.4958 | -122.8528 | -122.4655
551.8906 | 123.1476 | -122.8043 | 0.21057 | 0.062332 | -0.058836 | 0.010893 | -0.047909 | 0.06831 | 0.035221 | -0.058139 | -0.071132 | 0.13416 | 0.004937 | -0.15216 | 122.8852 | 122.9672 | 122.4979 | 122.6278 | 122.8666 | 122.7454 | 122.8152 | 122.7564 | 122.8726 | 122.8395 | 122.7461 | -0.071132 | 0.13416 | 0.004937 | -0.15216 | 122.8852 | 122.9672 | 122.4979 | 122.6278 | -122.9563 | -122.569 | -122.8803 | -122.493
553.5781 | 123.0331 | -122.8546 | 0.24261 | 0.071489 | -0.058836 | 0.010893 | -0.047909 | 0.077466 | 0.044377 | -0.053561 | -0.007033 | 0.13416 | 0.018672 | -0.14758 | 122.8898 | 122.9626 | 122.4979 | 122.6369 | 122.9261 | 122.7958 | 122.8655 | 122.8067 | 122.9321 | 122.899 | 122.8011 | -0.007033 | 0.13416 | 0.018672 | -0.14758 | 122.8898 | 122.9626 | 122.4979 | 122.6369 | -122.8968 | -122.5049 | -122.8711 | -122.4792
555.3281 | 123.1888 | -122.7859 | 0.22888 | 0.06691 | -0.049678 | 0.006315 | -0.047909 | 0.06831 | 0.044377 | -0.058139 | -0.025347 | 0.13874 | -0.008798 | -0.16131 | 122.876 | 122.958 | 122.4888 | 122.6278 | 122.8529 | 122.7363 | 122.7923 | 122.738 | 122.8543 | 122.8303 | 122.7278 | -0.025347 | 0.13874 | -0.008798 | -0.16131 | 122.876 | 122.958 | 122.4888 | 122.6278 | -122.9014 | -122.5141 | -122.8848 | -122.4976
557.0781 | 123.143 | -122.8226 | 0.23804 | 0.06691 | -0.054257 | 0.006315 | -0.043331 | 0.082044 | 0.035221 | -0.062717 | -0.01619 | 0.13874 | 0.027829 | -0.15674 | 122.8806 | 122.958 | 122.4979 | 122.6278 | 122.8895 | 122.7683 | 122.8289 | 122.7792 | 122.9046 | 122.8578 | 122.7599 | -0.01619 | 0.13874 | 0.027829 | -0.15674 | 122.8806 | 122.958 | 122.4979 | 122.6278 | -122.8968 | -122.5141 | -122.8528 | -122.4701
558.7656 | 123.0835 | -122.8088 | 0.25177 | 0.057754 | -0.054257 | 0.010893 | -0.038752 | 0.072888 | 0.039799 | -0.058139 | -0.01619 | 0.14332 | 0.02325 | -0.15674 | 122.8852 | 122.958 | 122.4979 | 122.6324 | 122.8666 | 122.7546 | 122.8197 | 122.7701 | 122.8817 | 122.8486 | 122.7507 | -0.01619 | 0.14332 | 0.02325 | -0.15674 | 122.8852 | 122.958 | 122.4979 | 122.6324 | -122.9014 | -122.5141 | -122.862 | -122.4747
560.5156 | 123.1659 | -122.8043 | 0.21515 | 0.057754 | -0.049678 | 0.010893 | -0.043331 | 0.082044 | 0.039799 | -0.053561 | 0.002124 | 0.14332 | 0.032407 | -0.15216 | 122.8852 | 122.9718 | 122.4979 | 122.6324 | 122.862 | 122.7546 | 122.8152 | 122.7609 | 122.8863 | 122.8441 | 122.7507 | 0.002124 | 0.14332 | 0.032407 | -0.15216 | 122.8852 | 122.9718 | 122.4979 | 122.6324 | -122.8831 | -122.4958 | -122.8528 | -122.4655
562.1875 | 123.0469 | -122.8592 | 0.25177 | 0.053175 | -0.049678 | 0.015472 | -0.047909 | 0.077466 | 0.039799 | -0.058139 | -0.066553 | 0.13416 | -0.027111 | -0.15216 | 122.8806 | 122.9718 | 122.5025 | 122.6369 | 122.9124 | 122.8095 | 122.8747 | 122.8113 | 122.9367 | 122.899 | 122.8011 | -0.066553 | 0.13416 | -0.027111 | -0.15216 | 122.8806 | 122.9718 | 122.5025 | 122.6369 | -122.9472 | -122.569 | -122.9077 | -122.5296
563.9375 | 123.0194 | -122.8409 | 0.22888 | 0.06691 | -0.0451 | 0.006315 | -0.043331 | 0.082044 | 0.035221 | -0.058139 | -0.061975 | 0.12501 | 0.018672 | -0.14758 | 122.8852 | 122.9672 | 122.5025 | 122.6369 | 122.9078 | 122.7958 | 122.8472 | 122.7976 | 122.9229 | 122.8761 | 122.7827 | -0.061975 | 0.12501 | 0.018672 | -0.14758 | 122.8852 | 122.9672 | 122.5025 | 122.6369 | -122.9472 | -122.5645 | -122.8665 | -122.4838
565.625 | 123.0927 | -122.8226 | 0.22888 | 0.06691 | -0.058836 | 0.015472 | -0.034174 | 0.077466 | 0.044377 | -0.058139 | -0.01619 | 0.13416 | -0.022532 | -0.15216 | 122.9035 | 122.9809 | 122.5116 | 122.6461 | 122.8895 | 122.7637 | 122.838 | 122.7884 | 122.9 | 122.8669 | 122.7644 | -0.01619 | 0.13416 | -0.022532 | -0.15216 | 122.9035 | 122.9809 | 122.5116 | 122.6461 | -122.9197 | -122.5278 | -122.926 | -122.5342
567.3594 | 123.024 | -122.85 | 0.23804 | 0.062332 | -0.040521 | 0.015472 | -0.038752 | 0.077466 | 0.039799 | -0.053561 | -0.080288 | 0.12501 | -0.045424 | -0.15674 | 122.8898 | 122.9718 | 122.5071 | 122.6369 | 122.9124 | 122.8095 | 122.8655 | 122.8113 | 122.9275 | 122.8898 | 122.7965 | -0.080288 | 0.12501 | -0.045424 | -0.15674 | 122.8898 | 122.9718 | 122.5071 | 122.6369 | -122.9701 | -122.5874 | -122.9352 | -122.5525
569.1094 | 123.1659 | -122.7997 | 0.20599 | 0.06691 | -0.058836 | 0.015472 | -0.043331 | 0.077466 | 0.035221 | -0.044405 | -0.084867 | 0.12501 | -0.050002 | -0.14758 | 122.8898 | 122.9718 | 122.5025 | 122.6324 | 122.8666 | 122.7408 | 122.8152 | 122.7564 | 122.8771 | 122.8349 | 122.7553 | -0.084867 | 0.12501 | -0.050002 | -0.14758 | 122.8898 | 122.9718 | 122.5025 | 122.6324 | -122.9746 | -122.5874 | -122.9398 | -122.5525
570.8438 | 123.0423 | -122.8455 | 0.21973 | 0.057754 | -0.049678 | 0.015472 | -0.043331 | 0.077466 | 0.035221 | -0.058139 | -0.048239 | 0.12501 | -0.036267 | -0.15674 | 122.8944 | 122.9763 | 122.5071 | 122.6324 | 122.9032 | 122.7958 | 122.8609 | 122.8021 | 122.9229 | 122.8807 | 122.7873 | -0.048239 | 0.12501 | -0.036267 | -0.15674 | 122.8944 | 122.9763 | 122.5071 | 122.6324 | -122.9426 | -122.5553 | -122.9306 | -122.5433
572.5156 | 123.1705 | -122.8043 | 0.20599 | 0.06691 | -0.054257 | 0.010893 | -0.043331 | 0.072888 | 0.035221 | -0.058139 | -0.043661 | 0.12043 | -0.068315 | -0.15216 | 122.8989 | 122.9718 | 122.5116 | 122.6369 | 122.8712 | 122.75 | 122.8152 | 122.7609 | 122.8771 | 122.8395 | 122.7461 | -0.043661 | 0.12043 | -0.068315 | -0.15216 | 122.8989 | 122.9718 | 122.5116 | 122.6369 | -122.9426 | -122.5553 | -122.9673 | -122.58
574.2656 | 123.0423 | -122.8363 | 0.23804 | 0.06691 | -0.054257 | 0.006315 | -0.047909 | 0.072888 | 0.039799 | -0.062717 | -0.01619 | 0.12043 | -0.027111 | -0.15216 | 122.8806 | 122.958 | 122.4796 | 122.6278 | 122.9032 | 122.782 | 122.8426 | 122.7884 | 122.9092 | 122.8761 | 122.7736 | -0.01619 | 0.12043 | -0.027111 | -0.15216 | 122.8806 | 122.958 | 122.4796 | 122.6278 | -122.8968 | -122.4958 | -122.9077 | -122.5067
576 | 123.1247 | -122.7905 | 0.2243 | 0.06691 | -0.0451 | 0.006315 | -0.043331 | 0.072888 | 0.039799 | -0.062717 | -0.025347 | 0.12501 | -0.017954 | -0.15216 | 122.8806 | 122.9626 | 122.4979 | 122.6278 | 122.8574 | 122.7454 | 122.7968 | 122.7472 | 122.8634 | 122.8303 | 122.7278 | -0.025347 | 0.12501 | -0.017954 | -0.15216 | 122.8806 | 122.9626 | 122.4979 | 122.6278 | -122.906 | -122.5233 | -122.8986 | -122.5159
577.75 | 123.1064 | -122.8088 | 0.2243 | 0.06691 | -0.049678 | 0.015472 | -0.038752 | 0.077466 | 0.035221 | -0.067295 | -0.052818 | 0.12501 | -0.013376 | -0.14758 | 122.8944 | 122.9718 | 122.5071 | 122.6369 | 122.8757 | 122.7592 | 122.8243 | 122.7701 | 122.8863 | 122.8441 | 122.7415 | -0.052818 | 0.12501 | -0.013376 | -0.14758 | 122.8944 | 122.9718 | 122.5071 | 122.6369 | -122.9472 | -122.5599 | -122.9077 | -122.5204
579.5 | 123.0469 | -122.8317 | 0.21515 | 0.06691 | -0.0451 | 0.010893 | -0.052488 | 0.072888 | 0.035221 | -0.058139 | -0.043661 | 0.11585 | -0.036267 | -0.16131 | 122.8898 | 122.9672 | 122.4979 | 122.6324 | 122.8986 | 122.7866 | 122.8426 | 122.7792 | 122.9046 | 122.8669 | 122.7736 | -0.043661 | 0.11585 | -0.036267 | -0.16131 | 122.8898 | 122.9672 | 122.4979 | 122.6324 | -122.9334 | -122.5416 | -122.926 | -122.5342
581.1719 | 123.143 | -122.8134 | 0.20599 | 0.062332 | -0.054257 | 0.010893 | -0.052488 | 0.072888 | 0.035221 | -0.067295 | -0.066553 | 0.12501 | -0.05458 | -0.15674 | 122.8806 | 122.9626 | 122.4888 | 122.6324 | 122.8757 | 122.7592 | 122.8243 | 122.7609 | 122.8863 | 122.8486 | 122.7461 | -0.066553 | 0.12501 | -0.05458 | -0.15674 | 122.8806 | 122.9626 | 122.4888 | 122.6324 | -122.9472 | -122.5553 | -122.9352 | -122.5433
582.9062 | 123.0835 | -122.8409 | 0.2243 | 0.062332 | -0.054257 | 0.010893 | -0.047909 | 0.077466 | 0.035221 | -0.058139 | -0.011611 | 0.11127 | 0.004937 | -0.15216 | 122.8898 | 122.9718 | 122.4979 | 122.6369 | 122.9032 | 122.7866 | 122.8518 | 122.793 | 122.9183 | 122.8761 | 122.7827 | -0.011611 | 0.11127 | 0.004937 | -0.15216 | 122.8898 | 122.9718 | 122.4979 | 122.6369 | -122.9014 | -122.5095 | -122.8848 | -122.493
584.5938 | 123.0377 | -122.8455 | 0.23804 | 0.06691 | -0.058836 | 0.006315 | -0.052488 | 0.072888 | 0.035221 | -0.058139 | -0.034504 | 0.12043 | -0.045424 | -0.15216 | 122.8852 | 122.9718 | 122.4979 | 122.6369 | 122.9124 | 122.7866 | 122.8518 | 122.793 | 122.9183 | 122.8807 | 122.7873 | -0.034504 | 0.12043 | -0.045424 | -0.15216 | 122.8852 | 122.9718 | 122.4979 | 122.6369 | -122.9197 | -122.5324 | -122.9306 | -122.5433
586.3438 | 123.0286 | -122.8409 | 0.21973 | 0.071489 | -0.058836 | 0.010893 | -0.043331 | 0.072888 | 0.039799 | -0.053561 | -0.057396 | 0.11585 | -0.068315 | -0.15216 | 122.8898 | 122.9718 | 122.5071 | 122.6324 | 122.9124 | 122.782 | 122.8518 | 122.7976 | 122.9138 | 122.8807 | 122.7873 | -0.057396 | 0.11585 | -0.068315 | -0.15216 | 122.8898 | 122.9718 | 122.5071 | 122.6324 | -122.9472 | -122.5645 | -122.9581 | -122.5754
588.0938 | 122.9919 | -122.8546 | 0.23804 | 0.071489 | -0.054257 | 0.006315 | -0.047909 | 0.072888 | 0.035221 | -0.053561 | -0.084867 | 0.12043 | -0.050002 | -0.15216 | 122.8898 | 122.958 | 122.5025 | 122.6369 | 122.9261 | 122.8004 | 122.8609 | 122.8067 | 122.9275 | 122.8898 | 122.8011 | -0.084867 | 0.12043 | -0.050002 | -0.15216 | 122.8898 | 122.958 | 122.5025 | 122.6369 | -122.9746 | -122.5874 | -122.9398 | -122.5525
589.7812 | 123.0331 | -122.85 | 0.23346 | 0.06691 | -0.054257 | 0.006315 | -0.047909 | 0.06831 | 0.035221 | -0.058139 | -0.080288 | 0.12501 | -0.063737 | -0.15216 | 122.8898 | 122.9672 | 122.5071 | 122.6415 | 122.9169 | 122.7958 | 122.8564 | 122.8021 | 122.9183 | 122.8853 | 122.7919 | -0.080288 | 0.12501 | -0.063737 | -0.15216 | 122.8898 | 122.9672 | 122.5071 | 122.6415 | -122.9701 | -122.5874 | -122.9535 | -122.5708
591.5156 | 122.9919 | -122.8363 | 0.23804 | 0.06691 | -0.054257 | 0.006315 | -0.047909 | 0.06831 | 0.030642 | -0.058139 | -0.080288 | 0.11585 | -0.059159 | -0.14758 | 122.8852 | 122.9626 | 122.4979 | 122.6369 | 122.9032 | 122.782 | 122.8426 | 122.7884 | 122.9046 | 122.8669 | 122.7782 | -0.080288 | 0.11585 | -0.059159 | -0.14758 | 122.8852 | 122.9626 | 122.4979 | 122.6369 | -122.9655 | -122.5782 | -122.9444 | -122.5571
593.2031 | 123.1659 | -122.8088 | 0.20599 | 0.06691 | -0.0451 | 0.010893 | -0.047909 | 0.06831 | 0.030642 | -0.067295 | -0.084867 | 0.12043 | -0.072894 | -0.15216 | 122.8806 | 122.9626 | 122.5071 | 122.6324 | 122.8757 | 122.7637 | 122.8197 | 122.7609 | 122.8771 | 122.8395 | 122.7415 | -0.084867 | 0.12043 | -0.072894 | -0.15216 | 122.8806 | 122.9626 | 122.5071 | 122.6324 | -122.9655 | -122.5919 | -122.9535 | -122.58
594.9531 | 123.0286 | -122.8363 | 0.21515 | 0.06691 | -0.049678 | 0.015472 | -0.047909 | 0.06831 | 0.030642 | -0.058139 | -0.052818 | 0.11585 | -0.045424 | -0.15674 | 122.8898 | 122.9718 | 122.4979 | 122.6324 | 122.9032 | 122.7866 | 122.8518 | 122.7884 | 122.9046 | 122.8669 | 122.7782 | -0.052818 | 0.11585 | -0.045424 | -0.15674 | 122.8898 | 122.9718 | 122.4979 | 122.6324 | -122.9426 | -122.5507 | -122.9352 | -122.5433
596.6875 | 123.143 | -122.7951 | 0.1831 | 0.06691 | -0.054257 | 0.001736 | -0.057066 | 0.063733 | 0.030642 | -0.067295 | -0.057396 | 0.11585 | -0.063737 | -0.15674 | 122.8852 | 122.9763 | 122.5025 | 122.6278 | 122.862 | 122.7408 | 122.7968 | 122.738 | 122.8588 | 122.8257 | 122.7278 | -0.057396 | 0.11585 | -0.063737 | -0.15674 | 122.8852 | 122.9763 | 122.5025 | 122.6278 | -122.9426 | -122.5599 | -122.9489 | -122.5662
598.4375 | 123.0331 | -122.8409 | 0.24719 | 0.062332 | -0.063415 | 0.010893 | -0.057066 | 0.063733 | 0.030642 | -0.058139 | -0.043661 | 0.12501 | -0.045424 | -0.143 | 122.8944 | 122.9672 | 122.4979 | 122.6324 | 122.9032 | 122.7775 | 122.8518 | 122.7838 | 122.9046 | 122.8715 | 122.7827 | -0.043661 | 0.12501 | -0.045424 | -0.143 | 122.8944 | 122.9672 | 122.4979 | 122.6324 | -122.938 | -122.5416 | -122.9398 | -122.5433
600.125 | 123.0103 | -122.8546 | 0.2243 | 0.062332 | -0.063415 | 0.001736 | -0.057066 | 0.063733 | 0.021485 | -0.058139 | -0.048239 | 0.12043 | -0.031689 | -0.143 | 122.8944 | 122.9626 | 122.5025 | 122.6369 | 122.9169 | 122.7912 | 122.8563 | 122.7975 | 122.9183 | 122.8761 | 122.7965 | -0.048239 | 0.12043 | -0.031689 | -0.143 | 122.8944 | 122.9626 | 122.5025 | 122.6369 | -122.9426 | -122.5507 | -122.926 | -122.5342
601.8594 | 123.1018 | -122.818 | 0.20599 | 0.057754 | -0.063415 | -0.002842 | -0.057066 | 0.06831 | 0.021485 | -0.067295 | -0.066553 | 0.11585 | -0.068315 | -0.15216 | 122.8944 | 122.9718 | 122.5025 | 122.6369 | 122.8757 | 122.7546 | 122.8152 | 122.7609 | 122.8863 | 122.8395 | 122.7507 | -0.066553 | 0.11585 | -0.068315 | -0.15216 | 122.8944 | 122.9718 | 122.5025 | 122.6369 | -122.9609 | -122.569 | -122.9627 | -122.5708
603.5938 | 123.0835 | -122.818 | 0.20142 | 0.06691 | -0.067994 | 0.001736 | -0.057066 | 0.06831 | 0.026064 | -0.071874 | -0.052818 | 0.10211 | -0.077472 | -0.14758 | 122.8989 | 122.9672 | 122.5025 | 122.6461 | 122.8849 | 122.75 | 122.8197 | 122.7609 | 122.8863 | 122.8441 | 122.7461 | -0.052818 | 0.10211 | -0.077472 | -0.14758 | 122.8989 | 122.9672 | 122.5025 | 122.6461 | -122.9518 | -122.5553 | -122.9764 | -122.58
605.2812 | 123.0881 | -122.8317 | 0.1831 | 0.062332 | -0.054257 | 0.006315 | -0.057066 | 0.059155 | 0.021485 | -0.071874 | -0.066553 | 0.10211 | -0.08205 | -0.14758 | 122.8989 | 122.9809 | 122.5116 | 122.6369 | 122.8941 | 122.7775 | 122.838 | 122.7747 | 122.8909 | 122.8532 | 122.7599 | -0.066553 | 0.10211 | -0.08205 | -0.14758 | 122.8989 | 122.9809 | 122.5116 | 122.6369 | -122.9655 | -122.5782 | -122.981 | -122.5937
607.0312 | 123.0606 | -122.8409 | 0.19684 | 0.06691 | -0.049678 | 0.001736 | -0.061645 | 0.063733 | 0.035221 | -0.062717 | -0.094024 | 0.10669 | -0.068315 | -0.14758 | 122.9081 | 122.9763 | 122.5162 | 122.6552 | 122.9078 | 122.7912 | 122.8426 | 122.7792 | 122.9046 | 122.8761 | 122.7782 | -0.094024 | 0.10669 | -0.068315 | -0.14758 | 122.9081 | 122.9763 | 122.5162 | 122.6552 | -123.0021 | -122.6102 | -122.9764 | -122.5845
608.7812 | 122.9919 | -122.8683 | 0.21515 | 0.062332 | -0.049678 | 0.001736 | -0.052488 | 0.063733 | 0.030642 | -0.058139 | -0.10318 | 0.097532 | -0.08205 | -0.143 | 122.9081 | 122.9901 | 122.5208 | 122.6552 | 122.9307 | 122.8187 | 122.8701 | 122.8159 | 122.9321 | 122.899 | 122.8102 | -0.10318 | 0.097532 | -0.08205 | -0.143 | 122.9081 | 122.9901 | 122.5208 | 122.6552 | -123.0113 | -122.624 | -122.9901 | -122.6029
610.4688 | 123.0881 | -122.85 | 0.16937 | 0.057754 | -0.063415 | -0.007421 | -0.057066 | 0.063733 | 0.030642 | -0.067295 | -0.057396 | 0.10669 | -0.086628 | -0.14758 | 122.9081 | 122.9901 | 122.5208 | 122.6552 | 122.9078 | 122.7866 | 122.8426 | 122.793 | 122.9138 | 122.8807 | 122.7827 | -0.057396 | 0.10669 | -0.086628 | -0.14758 | 122.9081 | 122.9901 | 122.5208 | 122.6552 | -122.9655 | -122.5782 | -122.9947 | -122.6074
612.2188 | 123.0194 | -122.8775 | 0.18768 | 0.062332 | -0.063415 | 0.001736 | -0.057066 | 0.063733 | 0.026064 | -0.062717 | -0.098602 | 0.088375 | -0.091207 | -0.14758 | 122.9081 | 122.9901 | 122.5208 | 122.6644 | 122.9398 | 122.8141 | 122.8792 | 122.8204 | 122.9412 | 122.9036 | 122.8148 | -0.098602 | 0.088375 | -0.091207 | -0.14758 | 122.9081 | 122.9901 | 122.5208 | 122.6644 | -123.0067 | -122.6194 | -122.9993 | -122.612
613.9062 | 123.1247 | -122.8043 | 0.17395 | 0.062332 | -0.058836 | -0.007421 | -0.052488 | 0.054577 | 0.026064 | -0.058139 | -0.098602 | 0.097532 | -0.091207 | -0.14758 | 122.9081 | 122.9901 | 122.5254 | 122.6598 | 122.8666 | 122.7454 | 122.7968 | 122.7518 | 122.8588 | 122.8303 | 122.7461 | -0.098602 | 0.097532 | -0.091207 | -0.14758 | 122.9081 | 122.9901 | 122.5254 | 122.6598 | -123.0067 | -122.624 | -122.9993 | -122.6166
615.6406 | 123.1247 | -122.8409 | 0.16022 | 0.057754 | -0.067994 | 0.001736 | -0.057066 | 0.059155 | 0.030642 | -0.062717 | -0.10776 | 0.097532 | -0.08205 | -0.143 | 122.9035 | 122.9901 | 122.5208 | 122.6552 | 122.8986 | 122.7729 | 122.8426 | 122.7838 | 122.9 | 122.8715 | 122.7782 | -0.10776 | 0.097532 | -0.08205 | -0.143 | 122.9035 | 122.9901 | 122.5208 | 122.6552 | -123.0113 | -122.6286 | -122.9856 | -122.6029
617.3906 | 123.0606 | -122.8363 | 0.19684 | 0.06691 | -0.067994 | -0.002842 | -0.061645 | 0.059155 | 0.026064 | -0.062717 | -0.10318 | 0.088375 | -0.091207 | -0.14758 | 122.9035 | 122.9946 | 122.5254 | 122.6598 | 122.9032 | 122.7683 | 122.8335 | 122.7747 | 122.8955 | 122.8624 | 122.7736 | -0.10318 | 0.088375 | -0.091207 | -0.14758 | 122.9035 | 122.9946 | 122.5254 | 122.6598 | -123.0067 | -122.6286 | -122.9947 | -122.6166
619.0781 | 123.0194 | -122.8729 | 0.19226 | 0.062332 | -0.058836 | -0.002842 | -0.052488 | 0.059155 | 0.026064 | -0.067295 | -0.10318 | 0.10211 | -0.10036 | -0.15216 | 122.9127 | 122.9855 | 122.5254 | 122.6552 | 122.9353 | 122.8141 | 122.8701 | 122.8204 | 122.9321 | 122.899 | 122.8056 | -0.10318 | 0.10211 | -0.10036 | -0.15216 | 122.9127 | 122.9855 | 122.5254 | 122.6552 | -123.0159 | -122.6286 | -123.013 | -122.6257
620.8125 | 123.0148 | -122.85 | 0.20599 | 0.062332 | -0.063415 | -0.002842 | -0.061645 | 0.054577 | 0.035221 | -0.062717 | -0.089445 | 0.097532 | -0.08205 | -0.143 | 122.9081 | 122.9855 | 122.5116 | 122.6507 | 122.9124 | 122.7866 | 122.8472 | 122.7884 | 122.9046 | 122.8853 | 122.7873 | -0.089445 | 0.097532 | -0.08205 | -0.143 | 122.9081 | 122.9855 | 122.5116 | 122.6507 | -122.9975 | -122.6011 | -122.9901 | -122.5937
622.5625 | 123.1338 | -122.8271 | 0.15564 | 0.071489 | -0.058836 | -0.002842 | -0.061645 | 0.06831 | 0.026064 | -0.076452 | -0.10318 | 0.092954 | -0.08205 | -0.143 | 122.8944 | 122.9855 | 122.5071 | 122.6461 | 122.8986 | 122.7683 | 122.8243 | 122.7655 | 122.8955 | 122.8532 | 122.7507 | -0.10318 | 0.092954 | -0.08205 | -0.143 | 122.8944 | 122.9855 | 122.5071 | 122.6461 | -122.9975 | -122.6102 | -122.9764 | -122.5891
624.25 | 123.1293 | -122.7951 | 0.16937 | 0.076067 | -0.063415 | 0.006315 | -0.061645 | 0.06831 | 0.026064 | -0.076452 | -0.10318 | 0.092954 | -0.095785 | -0.143 | 122.8989 | 122.9901 | 122.5025 | 122.6415 | 122.8712 | 122.7317 | 122.8014 | 122.7335 | 122.8634 | 122.8212 | 122.7187 | -0.10318 | 0.092954 | -0.095785 | -0.143 | 122.8989 | 122.9901 | 122.5025 | 122.6415 | -123.0021 | -122.6057 | -122.9947 | -122.5983
626 | 123.0515 | -122.8546 | 0.17395 | 0.062332 | -0.054257 | 0.006315 | -0.061645 | 0.063733 | 0.021485 | -0.067295 | -0.080288 | 0.092954 | -0.086628 | -0.14758 | 122.9035 | 122.9809 | 122.5162 | 122.6507 | 122.9169 | 122.8004 | 122.8609 | 122.793 | 122.9183 | 122.8761 | 122.7873 | -0.080288 | 0.092954 | -0.086628 | -0.14758 | 122.9035 | 122.9809 | 122.5162 | 122.6507 | -122.9838 | -122.5965 | -122.9901 | -122.6029
627.75 | 123.1064 | -122.8363 | 0.16479 | 0.057754 | -0.058836 | -0.002842 | -0.052488 | 0.059155 | 0.026064 | -0.071874 | -0.10318 | 0.10211 | -0.08205 | -0.15674 | 122.8898 | 122.9809 | 122.5071 | 122.6461 | 122.8941 | 122.7775 | 122.8335 | 122.7838 | 122.8955 | 122.8624 | 122.7644 | -0.10318 | 0.10211 | -0.08205 | -0.15674 | 122.8898 | 122.9809 | 122.5071 | 122.6461 | -122.993 | -122.6102 | -122.9718 | -122.5891
629.4375 | 123.0011 | -122.818 | 0.18768 | 0.062332 | -0.063415 | -0.002842 | -0.052488 | 0.063733 | 0.030642 | -0.067295 | -0.07571 | 0.10211 | -0.086628 | -0.143 | 122.8944 | 122.9855 | 122.5116 | 122.6461 | 122.8803 | 122.7546 | 122.8152 | 122.7655 | 122.8817 | 122.8486 | 122.7507 | -0.07571 | 0.10211 | -0.086628 | -0.143 | 122.8944 | 122.9855 | 122.5116 | 122.6461 | -122.9701 | -122.5874 | -122.981 | -122.5983
631.1875 | 123.1155 | -122.8226 | 0.17395 | 0.06691 | -0.063415 | -0.002842 | -0.061645 | 0.054577 | 0.012329 | -0.071874 | -0.10776 | 0.097532 | -0.086628 | -0.15674 | 122.8898 | 122.9763 | 122.5116 | 122.6415 | 122.8895 | 122.7592 | 122.8197 | 122.7609 | 122.8771 | 122.8349 | 122.7507 | -0.10776 | 0.097532 | -0.086628 | -0.15674 | 122.8898 | 122.9763 | 122.5116 | 122.6415 | -122.9975 | -122.6194 | -122.9764 | -122.5983
632.9219 | 123.1155 | -122.8317 | 0.16479 | 0.062332 | -0.063415 | -0.002842 | -0.066223 | 0.054577 | 0.016907 | -0.062717 | -0.080288 | 0.097532 | -0.086628 | -0.14758 | 122.8944 | 122.9718 | 122.5071 | 122.6369 | 122.8941 | 122.7683 | 122.8289 | 122.7655 | 122.8863 | 122.8486 | 122.769 | -0.080288 | 0.097532 | -0.086628 | -0.14758 | 122.8944 | 122.9718 | 122.5071 | 122.6369 | -122.9746 | -122.5874 | -122.981 | -122.5937
634.6094 | 123.0011 | -122.85 | 0.21057 | 0.062332 | -0.063415 | -0.002842 | -0.061645 | 0.054577 | 0.021485 | -0.062717 | -0.089445 | 0.088375 | -0.077472 | -0.14758 | 122.8944 | 122.9809 | 122.5025 | 122.6415 | 122.9124 | 122.7866 | 122.8472 | 122.7884 | 122.9046 | 122.8715 | 122.7873 | -0.089445 | 0.088375 | -0.077472 | -0.14758 | 122.8944 | 122.9809 | 122.5025 | 122.6415 | -122.9838 | -122.5919 | -122.9718 | -122.58
636.3438 | 123.0423 | -122.818 | 0.20142 | 0.057754 | -0.054257 | 0.001736 | -0.057066 | 0.049999 | 0.021485 | -0.067295 | -0.071132 | 0.10211 | -0.086628 | -0.14758 | 122.9035 | 122.9672 | 122.5116 | 122.6369 | 122.8757 | 122.7637 | 122.8197 | 122.7609 | 122.868 | 122.8395 | 122.7507 | -0.071132 | 0.10211 | -0.086628 | -0.14758 | 122.9035 | 122.9672 | 122.5116 | 122.6369 | -122.9746 | -122.5828 | -122.9901 | -122.5983
638.0312 | 123.0057 | -122.818 | 0.22888 | 0.062332 | -0.067994 | -0.007421 | -0.070802 | 0.059155 | 0.021485 | -0.08103 | -0.061975 | 0.10669 | -0.072894 | -0.14758 | 122.876 | 122.9534 | 122.4842 | 122.6186 | 122.8803 | 122.75 | 122.8106 | 122.7472 | 122.8771 | 122.8395 | 122.737 | -0.061975 | 0.10669 | -0.072894 | -0.14758 | 122.876 | 122.9534 | 122.4842 | 122.6186 | -122.938 | -122.5461 | -122.9489 | -122.5571
639.7812 | 123.1201 | -122.7951 | 0.18768 | 0.062332 | -0.072572 | -0.012 | -0.070802 | 0.045421 | 0.021485 | -0.076452 | -0.039082 | 0.10669 | -0.040846 | -0.14758 | 122.8715 | 122.9534 | 122.4933 | 122.6186 | 122.8574 | 122.7225 | 122.7831 | 122.7243 | 122.8405 | 122.8166 | 122.7187 | -0.039082 | 0.10669 | -0.040846 | -0.14758 | 122.8715 | 122.9534 | 122.4933 | 122.6186 | -122.9105 | -122.5324 | -122.9123 | -122.5342
641.4531 | 123.0423 | -122.8088 | 0.21973 | 0.057754 | -0.067994 | -0.007421 | -0.066223 | 0.049999 | 0.021485 | -0.067295 | -0.080288 | 0.12043 | -0.059159 | -0.15216 | 122.876 | 122.9534 | 122.4888 | 122.6278 | 122.8666 | 122.7408 | 122.8014 | 122.7426 | 122.8588 | 122.8303 | 122.7415 | -0.080288 | 0.12043 | -0.059159 | -0.15216 | 122.876 | 122.9534 | 122.4888 | 122.6278 | -122.9563 | -122.569 | -122.9352 | -122.5479
643.1406 | 123.1338 | -122.7814 | 0.18768 | 0.062332 | -0.072572 | -0.007421 | -0.066223 | 0.059155 | 0.021485 | -0.071874 | -0.098602 | 0.11127 | -0.068315 | -0.15216 | 122.8715 | 122.9534 | 122.4842 | 122.6186 | 122.8437 | 122.7088 | 122.774 | 122.7151 | 122.8405 | 122.8029 | 122.7095 | -0.098602 | 0.11127 | -0.068315 | -0.15216 | 122.8715 | 122.9534 | 122.4842 | 122.6186 | -122.9701 | -122.5828 | -122.9398 | -122.5525
644.8906 | 122.9919 | -122.8363 | 0.21973 | 0.062332 | -0.077151 | -0.012 | -0.061645 | 0.049999 | 0.016907 | -0.067295 | -0.071132 | 0.11585 | -0.059159 | -0.15216 | 122.8715 | 122.9534 | 122.4933 | 122.6232 | 122.8986 | 122.7592 | 122.8243 | 122.7747 | 122.8863 | 122.8532 | 122.769 | -0.071132 | 0.11585 | -0.059159 | -0.15216 | 122.8715 | 122.9534 | 122.4933 | 122.6232 | -122.9426 | -122.5645 | -122.9306 | -122.5525
646.5781 | 123.1064 | -122.7676 | 0.1831 | 0.057754 | -0.072572 | -0.012 | -0.070802 | 0.049999 | 0.016907 | -0.071874 | -0.07571 | 0.11127 | -0.063737 | -0.15674 | 122.8623 | 122.958 | 122.4842 | 122.614 | 122.8254 | 122.6951 | 122.7556 | 122.6968 | 122.8176 | 122.7845 | 122.6958 | -0.07571 | 0.11127 | -0.063737 | -0.15674 | 122.8623 | 122.958 | 122.4842 | 122.614 | -122.938 | -122.5599 | -122.926 | -122.5479
648.2656 | 122.9691 | -122.8226 | 0.23346 | 0.062332 | -0.072572 | -0.007421 | -0.066223 | 0.054577 | 0.021485 | -0.071874 | -0.048239 | 0.11127 | -0.068315 | -0.15216 | 122.876 | 122.9534 | 122.4888 | 122.614 | 122.8849 | 122.75 | 122.8152 | 122.7563 | 122.8771 | 122.8441 | 122.7507 | -0.048239 | 0.11127 | -0.068315 | -0.15216 | 122.876 | 122.9534 | 122.4888 | 122.614 | -122.9243 | -122.537 | -122.9444 | -122.5571
650.0156 | 123.0927 | -122.7859 | 0.18768 | 0.062332 | -0.08173 | -0.012 | -0.066223 | 0.049999 | 0.021485 | -0.08103 | -0.094024 | 0.11127 | -0.077472 | -0.16131 | 122.8715 | 122.9443 | 122.4888 | 122.6232 | 122.8483 | 122.7042 | 122.7739 | 122.7197 | 122.8359 | 122.8074 | 122.7049 | -0.094024 | 0.11127 | -0.077472 | -0.16131 | 122.8715 | 122.9443 | 122.4888 | 122.6232 | -122.9655 | -122.5828 | -122.9489 | -122.5662
651.75 | 123.0057 | -122.818 | 0.21515 | 0.071489 | -0.072572 | -0.012 | -0.07538 | 0.049999 | 0.016907 | -0.071874 | -0.039082 | 0.11585 | -0.050002 | -0.15216 | 122.876 | 122.9489 | 122.4888 | 122.614 | 122.8895 | 122.7454 | 122.806 | 122.7426 | 122.868 | 122.8349 | 122.7461 | -0.039082 | 0.11585 | -0.050002 | -0.15216 | 122.876 | 122.9489 | 122.4888 | 122.614 | -122.9151 | -122.5278 | -122.926 | -122.5388
653.5 | 123.1064 | -122.7631 | 0.17395 | 0.057754 | -0.072572 | -0.007421 | -0.070802 | 0.049999 | 0.00775 | -0.076452 | -0.084867 | 0.097532 | -0.063737 | -0.14758 | 122.8669 | 122.9489 | 122.4796 | 122.6095 | 122.8208 | 122.6905 | 122.7556 | 122.6923 | 122.8131 | 122.7708 | 122.6866 | -0.084867 | 0.097532 | -0.063737 | -0.14758 | 122.8669 | 122.9489 | 122.4796 | 122.6095 | -122.9518 | -122.5645 | -122.9306 | -122.5433
655.2031 | 123.0652 | -122.7859 | 0.19226 | 0.06691 | -0.077151 | -0.007421 | -0.061645 | 0.045421 | 0.012329 | -0.076452 | -0.039082 | 0.11127 | -0.027111 | -0.15674 | 122.8715 | 122.9534 | 122.4704 | 122.6186 | 122.8529 | 122.7088 | 122.7785 | 122.7243 | 122.8314 | 122.7983 | 122.7095 | -0.039082 | 0.11127 | -0.027111 | -0.15674 | 122.8715 | 122.9534 | 122.4704 | 122.6186 | -122.9105 | -122.5095 | -122.8986 | -122.4976
656.9375 | 123.0011 | -122.8226 | 0.20599 | 0.06691 | -0.072572 | -0.002842 | -0.07538 | 0.045421 | 0.016907 | -0.076452 | -0.048239 | 0.11585 | -0.05458 | -0.14758 | 122.8715 | 122.9443 | 122.4796 | 122.6095 | 122.8895 | 122.75 | 122.8197 | 122.7472 | 122.868 | 122.8395 | 122.7461 | -0.048239 | 0.11585 | -0.05458 | -0.14758 | 122.8715 | 122.9443 | 122.4796 | 122.6095 | -122.9197 | -122.5278 | -122.926 | -122.5342
658.6719 | 123.0331 | -122.8088 | 0.21973 | 0.071489 | -0.067994 | -0.002842 | -0.07538 | 0.040843 | 0.021485 | -0.071874 | -0.066553 | 0.12043 | -0.059159 | -0.15674 | 122.8715 | 122.9489 | 122.4842 | 122.6186 | 122.8803 | 122.7408 | 122.806 | 122.7335 | 122.8497 | 122.8303 | 122.737 | -0.066553 | 0.12043 | -0.059159 | -0.15674 | 122.8715 | 122.9489 | 122.4842 | 122.6186 | -122.938 | -122.5507 | -122.9306 | -122.5433
660.3594 | 122.9874 | -122.7859 | 0.21515 | 0.06691 | -0.077151 | -0.002842 | -0.066223 | 0.045421 | 0.021485 | -0.071874 | -0.043661 | 0.11127 | -0.063737 | -0.15674 | 122.8715 | 122.9443 | 122.4796 | 122.6095 | 122.8529 | 122.7088 | 122.7831 | 122.7197 | 122.8314 | 122.8074 | 122.7141 | -0.043661 | 0.11127 | -0.063737 | -0.15674 | 122.8715 | 122.9443 | 122.4796 | 122.6095 | -122.9151 | -122.5233 | -122.9352 | -122.5433
662.0938 | 123.0881 | -122.7768 | 0.19684 | 0.06691 | -0.072572 | -0.002842 | -0.070802 | 0.045421 | 0.012329 | -0.071874 | -0.071132 | 0.12501 | -0.059159 | -0.15216 | 122.8669 | 122.9443 | 122.4704 | 122.6095 | 122.8437 | 122.7042 | 122.774 | 122.706 | 122.8222 | 122.7891 | 122.7049 | -0.071132 | 0.12501 | -0.059159 | -0.15216 | 122.8669 | 122.9443 | 122.4704 | 122.6095 | -122.938 | -122.5416 | -122.926 | -122.5296
663.7812 | 122.9874 | -122.8409 | 0.21515 | 0.062332 | -0.077151 | -0.012 | -0.070802 | 0.049999 | 0.012329 | -0.076452 | -0.052818 | 0.12043 | -0.068315 | -0.15216 | 122.8623 | 122.9489 | 122.4796 | 122.6232 | 122.9032 | 122.7637 | 122.8289 | 122.7701 | 122.8909 | 122.8532 | 122.7644 | -0.052818 | 0.12043 | -0.068315 | -0.15216 | 122.8623 | 122.9489 | 122.4796 | 122.6232 | -122.9151 | -122.5324 | -122.9306 | -122.5479
665.5312 | 123.111 | -122.7676 | 0.17853 | 0.053175 | -0.08173 | -0.012 | -0.066223 | 0.045421 | 0.021485 | -0.08103 | -0.084867 | 0.12043 | -0.068315 | -0.14758 | 122.8623 | 122.9397 | 122.4704 | 122.6095 | 122.8208 | 122.6859 | 122.7556 | 122.7014 | 122.8131 | 122.7891 | 122.6866 | -0.084867 | 0.12043 | -0.068315 | -0.14758 | 122.8623 | 122.9397 | 122.4704 | 122.6095 | -122.9472 | -122.5553 | -122.9306 | -122.5388
667.2656 | 123.0148 | -122.8134 | 0.21973 | 0.062332 | -0.067994 | -0.012 | -0.07538 | 0.049999 | 0.012329 | -0.076452 | -0.029925 | 0.12501 | -0.068315 | -0.14758 | 122.8623 | 122.9443 | 122.4704 | 122.614 | 122.8757 | 122.7454 | 122.8014 | 122.738 | 122.8634 | 122.8257 | 122.737 | -0.029925 | 0.12501 | -0.068315 | -0.14758 | 122.8623 | 122.9443 | 122.4704 | 122.614 | -122.8922 | -122.5004 | -122.9306 | -122.5388
669.0156 | 123.0652 | -122.7768 | 0.19684 | 0.062332 | -0.077151 | -0.007421 | -0.061645 | 0.049999 | 0.012329 | -0.085608 | -0.043661 | 0.11127 | -0.045424 | -0.14758 | 122.8532 | 122.9306 | 122.4704 | 122.6003 | 122.8391 | 122.6996 | 122.7694 | 122.7151 | 122.8268 | 122.7891 | 122.6912 | -0.043661 | 0.11127 | -0.045424 | -0.14758 | 122.8532 | 122.9306 | 122.4704 | 122.6003 | -122.8968 | -122.5141 | -122.8986 | -122.5159
670.7031 | 122.9599 | -122.8043 | 0.20599 | 0.06691 | -0.072572 | -0.007421 | -0.070802 | 0.040843 | 0.016907 | -0.076452 | -0.066553 | 0.097532 | -0.077472 | -0.15216 | 122.8669 | 122.9397 | 122.4659 | 122.6095 | 122.8712 | 122.7317 | 122.7968 | 122.7335 | 122.8451 | 122.8212 | 122.7278 | -0.066553 | 0.097532 | -0.077472 | -0.15216 | 122.8669 | 122.9397 | 122.4659 | 122.6095 | -122.9334 | -122.5324 | -122.9444 | -122.5433
672.4531 | 123.0057 | -122.7905 | 0.21973 | 0.06691 | -0.077151 | -0.007421 | -0.066223 | 0.049999 | 0.012329 | -0.071874 | -0.07571 | 0.12501 | -0.068315 | -0.15216 | 122.8623 | 122.9351 | 122.475 | 122.614 | 122.8574 | 122.7134 | 122.7831 | 122.7243 | 122.8405 | 122.8029 | 122.7187 | -0.07571 | 0.12501 | -0.068315 | -0.15216 | 122.8623 | 122.9351 | 122.475 | 122.614 | -122.938 | -122.5507 | -122.9306 | -122.5433
674.1406 | 123.056 | -122.7676 | 0.19684 | 0.06691 | -0.067994 | -0.012 | -0.070802 | 0.045421 | 0.012329 | -0.076452 | -0.089445 | 0.12043 | -0.077472 | -0.15216 | 122.8532 | 122.9397 | 122.4659 | 122.5957 | 122.8345 | 122.6996 | 122.7556 | 122.6968 | 122.8131 | 122.78 | 122.6912 | -0.089445 | 0.12043 | -0.077472 | -0.15216 | 122.8532 | 122.9397 | 122.4659 | 122.5957 | -122.9426 | -122.5553 | -122.9306 | -122.5433
675.8906 | 123.0606 | -122.7402 | 0.18768 | 0.06691 | -0.072572 | -0.007421 | -0.070802 | 0.054577 | 0.016907 | -0.08103 | -0.052818 | 0.11127 | -0.077472 | -0.15216 | 122.8623 | 122.926 | 122.4613 | 122.5957 | 122.8071 | 122.6676 | 122.7328 | 122.6694 | 122.7947 | 122.7571 | 122.6591 | -0.052818 | 0.11127 | -0.077472 | -0.15216 | 122.8623 | 122.926 | 122.4613 | 122.5957 | -122.9151 | -122.5141 | -122.9398 | -122.5388
677.625 | 122.9736 | -122.7951 | 0.20142 | 0.06691 | -0.072572 | -0.002842 | -0.079959 | 0.045421 | 0.012329 | -0.08103 | -0.071132 | 0.11585 | -0.063737 | -0.15674 | 122.8532 | 122.9351 | 122.4659 | 122.6003 | 122.862 | 122.7225 | 122.7923 | 122.7151 | 122.8405 | 122.8074 | 122.7141 | -0.071132 | 0.11585 | -0.063737 | -0.15674 | 122.8532 | 122.9351 | 122.4659 | 122.6003 | -122.9243 | -122.537 | -122.9169 | -122.5296
679.3594 | 122.9645 | -122.7997 | 0.23804 | 0.062332 | -0.077151 | -0.002842 | -0.070802 | 0.049999 | 0.016907 | -0.076452 | -0.048239 | 0.11585 | -0.027111 | -0.14758 | 122.8577 | 122.9351 | 122.4659 | 122.5957 | 122.862 | 122.7225 | 122.7968 | 122.7289 | 122.8497 | 122.8166 | 122.7232 | -0.048239 | 0.11585 | -0.027111 | -0.14758 | 122.8577 | 122.9351 | 122.4659 | 122.5957 | -122.906 | -122.5141 | -122.8848 | -122.493
681.1094 | 123.111 | -122.7585 | 0.16937 | 0.062332 | -0.077151 | -0.016578 | -0.066223 | 0.049999 | 0.012329 | -0.076452 | -0.039082 | 0.11585 | -0.050002 | -0.15216 | 122.8486 | 122.926 | 122.4613 | 122.5957 | 122.8208 | 122.6813 | 122.7419 | 122.6923 | 122.8085 | 122.7708 | 122.682 | -0.039082 | 0.11585 | -0.050002 | -0.15216 | 122.8486 | 122.926 | 122.4613 | 122.5957 | -122.8877 | -122.5004 | -122.8986 | -122.5113
682.8594 | 123.0698 | -122.7676 | 0.20142 | 0.062332 | -0.077151 | -0.012 | -0.070802 | 0.054577 | 0.012329 | -0.085608 | -0.084867 | 0.11585 | -0.072894 | -0.15216 | 122.8577 | 122.9351 | 122.4613 | 122.6095 | 122.83 | 122.6905 | 122.7556 | 122.6968 | 122.8222 | 122.78 | 122.682 | -0.084867 | 0.11585 | -0.072894 | -0.15216 | 122.8577 | 122.9351 | 122.4613 | 122.6095 | -122.9426 | -122.5461 | -122.9306 | -122.5342
684.5469 | 123.0835 | -122.7539 | 0.20142 | 0.057754 | -0.08173 | -0.012 | -0.07538 | 0.045421 | 0.012329 | -0.085608 | -0.039082 | 0.12043 | -0.050002 | -0.15216 | 122.8577 | 122.9306 | 122.4613 | 122.6003 | 122.8117 | 122.6722 | 122.7419 | 122.6785 | 122.7993 | 122.7662 | 122.6683 | -0.039082 | 0.12043 | -0.050002 | -0.15216 | 122.8577 | 122.9306 | 122.4613 | 122.6003 | -122.8968 | -122.5004 | -122.9077 | -122.5113
686.2969 | 122.9599 | -122.7814 | 0.21973 | 0.06691 | -0.077151 | -0.007421 | -0.066223 | 0.049999 | 0.00775 | -0.071874 | -0.048239 | 0.10669 | -0.045424 | -0.15674 | 122.8394 | 122.9306 | 122.4659 | 122.5957 | 122.8483 | 122.7042 | 122.774 | 122.7151 | 122.8314 | 122.7891 | 122.7095 | -0.048239 | 0.10669 | -0.045424 | -0.15674 | 122.8394 | 122.9306 | 122.4659 | 122.5957 | -122.8877 | -122.5141 | -122.8848 | -122.5113
688.0469 | 123.0835 | -122.7631 | 0.17395 | 0.062332 | -0.077151 | -0.012 | -0.07538 | 0.040843 | 0.003172 | -0.08103 | -0.080288 | 0.12043 | -0.077472 | -0.15216 | 122.8486 | 122.9351 | 122.4613 | 122.6003 | 122.8254 | 122.6859 | 122.7511 | 122.6877 | 122.8039 | 122.7662 | 122.682 | -0.080288 | 0.12043 | -0.077472 | -0.15216 | 122.8486 | 122.9351 | 122.4613 | 122.6003 | -122.9289 | -122.5416 | -122.926 | -122.5388
689.75 | 122.9599 | -122.8043 | 0.21515 | 0.062332 | -0.08173 | -0.007421 | -0.070802 | 0.036265 | 0.012329 | -0.08103 | -0.048239 | 0.12043 | -0.072894 | -0.15674 | 122.8486 | 122.9351 | 122.4613 | 122.6003 | 122.8666 | 122.7225 | 122.7968 | 122.7335 | 122.8405 | 122.8166 | 122.7232 | -0.048239 | 0.12043 | -0.072894 | -0.15674 | 122.8486 | 122.9351 | 122.4613 | 122.6003 | -122.8968 | -122.5095 | -122.9215 | -122.5342
691.4844 | 122.937 | -122.7859 | 0.19684 | 0.06691 | -0.086309 | -0.021157 | -0.07538 | 0.040843 | 0.00775 | -0.085608 | -0.089445 | 0.10211 | -0.068315 | -0.15216 | 122.8532 | 122.9351 | 122.4659 | 122.6003 | 122.8529 | 122.6996 | 122.7648 | 122.7106 | 122.8268 | 122.7937 | 122.7003 | -0.089445 | 0.10211 | -0.068315 | -0.15216 | 122.8532 | 122.9351 | 122.4659 | 122.6003 | -122.9426 | -122.5553 | -122.9215 | -122.5342
693.2188 | 123.0286 | -122.7814 | 0.20599 | 0.06691 | -0.086309 | -0.016578 | -0.07538 | 0.031687 | 0.003172 | -0.090186 | -0.071132 | 0.10211 | -0.068315 | -0.15674 | 122.8486 | 122.9306 | 122.4659 | 122.5957 | 122.8483 | 122.6951 | 122.7648 | 122.706 | 122.8131 | 122.7845 | 122.6912 | -0.071132 | 0.10211 | -0.068315 | -0.15674 | 122.8486 | 122.9306 | 122.4659 | 122.5957 | -122.9197 | -122.537 | -122.9169 | -122.5342
694.9688 | 122.937 | -122.7768 | 0.21057 | 0.062332 | -0.077151 | -0.021157 | -0.079959 | 0.040843 | 0.016907 | -0.076452 | -0.057396 | 0.12043 | -0.063737 | -0.14758 | 122.8532 | 122.9351 | 122.4567 | 122.6049 | 122.8391 | 122.6996 | 122.7556 | 122.6968 | 122.8176 | 122.7937 | 122.7003 | -0.057396 | 0.12043 | -0.063737 | -0.14758 | 122.8532 | 122.9351 | 122.4567 | 122.6049 | -122.9106 | -122.5141 | -122.9169 | -122.5204
696.7031 | 122.9507 | -122.7997 | 0.21057 | 0.06691 | -0.086309 | -0.016578 | -0.07538 | 0.036265 | 0.00775 | -0.090186 | -0.057396 | 0.12501 | -0.072894 | -0.15674 | 122.8486 | 122.9306 | 122.4659 | 122.6049 | 122.8666 | 122.7134 | 122.7831 | 122.7243 | 122.8359 | 122.8074 | 122.7095 | -0.057396 | 0.12501 | -0.072894 | -0.15674 | 122.8486 | 122.9306 | 122.4659 | 122.6049 | -122.906 | -122.5233 | -122.9215 | -122.5388
698.4062 | 123.0011 | -122.7814 | 0.21973 | 0.06691 | -0.08173 | -0.016578 | -0.084537 | 0.036265 | -0.001406 | -0.08103 | -0.052818 | 0.11585 | -0.031689 | -0.14758 | 122.8486 | 122.9214 | 122.4659 | 122.5957 | 122.8483 | 122.6996 | 122.7648 | 122.6968 | 122.8176 | 122.78 | 122.7003 | -0.052818 | 0.11585 | -0.031689 | -0.14758 | 122.8486 | 122.9214 | 122.4659 | 122.5957 | -122.9014 | -122.5187 | -122.8803 | -122.4976
700.1562 | 123.0652 | -122.7722 | 0.17395 | 0.062332 | -0.086309 | -0.016578 | -0.079959 | 0.022531 | 0.00775 | -0.085608 | -0.057396 | 0.11127 | -0.068315 | -0.14758 | 122.8486 | 122.926 | 122.4567 | 122.5957 | 122.8345 | 122.6859 | 122.7556 | 122.6923 | 122.7947 | 122.78 | 122.6866 | -0.057396 | 0.11127 | -0.068315 | -0.14758 | 122.8486 | 122.926 | 122.4567 | 122.5957 | -122.906 | -122.5141 | -122.9169 | -122.525
701.8281 | 123.0789 | -122.7905 | 0.16479 | 0.062332 | -0.090888 | -0.016578 | -0.079959 | 0.031687 | 0.003172 | -0.090186 | -0.080288 | 0.11585 | -0.059159 | -0.15216 | 122.844 | 122.926 | 122.4567 | 122.6003 | 122.8529 | 122.6996 | 122.7739 | 122.7106 | 122.8222 | 122.7937 | 122.7003 | -0.080288 | 0.11585 | -0.059159 | -0.15216 | 122.844 | 122.926 | 122.4567 | 122.6003 | -122.9243 | -122.537 | -122.9032 | -122.5159
703.5625 | 122.9507 | -122.8317 | 0.23346 | 0.062332 | -0.086309 | -0.025735 | -0.07538 | 0.036265 | 0.003172 | -0.08103 | -0.025347 | 0.12043 | -0.05458 | -0.15216 | 122.8577 | 122.9351 | 122.4567 | 122.6003 | 122.8941 | 122.7454 | 122.806 | 122.7563 | 122.868 | 122.8349 | 122.7507 | -0.025347 | 0.12043 | -0.05458 | -0.15216 | 122.8577 | 122.9351 | 122.4567 | 122.6003 | -122.8831 | -122.4821 | -122.9123 | -122.5113
705.25 | 123.056 | -122.7539 | 0.1831 | 0.057754 | -0.095467 | -0.021157 | -0.079959 | 0.036265 | -0.001406 | -0.085608 | -0.057396 | 0.11585 | -0.077472 | -0.14758 | 122.8486 | 122.926 | 122.4659 | 122.6095 | 122.8117 | 122.6584 | 122.7327 | 122.6739 | 122.7902 | 122.7525 | 122.6683 | -0.057396 | 0.11585 | -0.077472 | -0.14758 | 122.8486 | 122.926 | 122.4659 | 122.6095 | -122.906 | -122.5233 | -122.926 | -122.5433
707 | 123.0881 | -122.7356 | 0.1831 | 0.057754 | -0.086309 | -0.025735 | -0.07538 | 0.036265 | 0.003172 | -0.085608 | -0.089445 | 0.10669 | -0.063737 | -0.143 | 122.8532 | 122.9306 | 122.4567 | 122.5957 | 122.7934 | 122.6493 | 122.7099 | 122.6602 | 122.7719 | 122.7388 | 122.65 | -0.089445 | 0.10669 | -0.063737 | -0.143 | 122.8532 | 122.9306 | 122.4567 | 122.5957 | -122.9426 | -122.5461 | -122.9169 | -122.5204
708.7344 | 123.0789 | -122.7448 | 0.1831 | 0.062332 | -0.095467 | -0.021157 | -0.084537 | 0.031687 | -0.001406 | -0.090186 | -0.025347 | 0.11585 | -0.068315 | -0.14758 | 122.844 | 122.9306 | 122.4567 | 122.5912 | 122.8071 | 122.6493 | 122.7236 | 122.6602 | 122.7764 | 122.7433 | 122.6546 | -0.025347 | 0.11585 | -0.068315 | -0.14758 | 122.844 | 122.9306 | 122.4567 | 122.5912 | -122.8693 | -122.4821 | -122.9123 | -122.525
710.4844 | 123.0881 | -122.731 | 0.19226 | 0.06691 | -0.08173 | -0.021157 | -0.079959 | 0.031687 | 0.003172 | -0.085608 | -0.01619 | 0.12043 | -0.031689 | -0.15674 | 122.8532 | 122.9351 | 122.4521 | 122.5912 | 122.7979 | 122.6493 | 122.7099 | 122.6511 | 122.7627 | 122.7342 | 122.6454 | -0.01619 | 0.12043 | -0.031689 | -0.15674 | 122.8532 | 122.9351 | 122.4521 | 122.5912 | -122.8693 | -122.4683 | -122.8848 | -122.4838
712.1719 | 123.0835 | -122.7448 | 0.19684 | 0.06691 | -0.08173 | -0.021157 | -0.089116 | 0.031687 | 0.003172 | -0.085608 | -0.057396 | 0.12043 | -0.050002 | -0.14758 | 122.8532 | 122.9214 | 122.4613 | 122.6003 | 122.8117 | 122.663 | 122.7236 | 122.6556 | 122.7764 | 122.7479 | 122.6591 | -0.057396 | 0.12043 | -0.050002 | -0.14758 | 122.8532 | 122.9214 | 122.4613 | 122.6003 | -122.9106 | -122.5187 | -122.9032 | -122.5113
713.9219 | 123.1064 | -122.7402 | 0.17853 | 0.062332 | -0.086309 | -0.021157 | -0.084537 | 0.027109 | 0.003172 | -0.094765 | -0.066553 | 0.11585 | -0.072894 | -0.14758 | 122.8394 | 122.926 | 122.4613 | 122.5957 | 122.8025 | 122.6539 | 122.719 | 122.6556 | 122.7673 | 122.7433 | 122.6454 | -0.066553 | 0.11585 | -0.072894 | -0.14758 | 122.8394 | 122.926 | 122.4613 | 122.5957 | -122.906 | -122.5278 | -122.9123 | -122.5342
715.6719 | 123.0606 | -122.7585 | 0.19226 | 0.057754 | -0.08173 | -0.025735 | -0.089116 | 0.036265 | -0.001406 | -0.099343 | -0.034504 | 0.12043 | -0.063737 | -0.15216 | 122.844 | 122.926 | 122.4521 | 122.5957 | 122.8162 | 122.6768 | 122.7327 | 122.6694 | 122.7947 | 122.7571 | 122.6591 | -0.034504 | 0.12043 | -0.063737 | -0.15216 | 122.844 | 122.926 | 122.4521 | 122.5957 | -122.8785 | -122.4866 | -122.9077 | -122.5159
717.3438 | 123.0423 | -122.7539 | 0.17853 | 0.062332 | -0.090888 | -0.021157 | -0.084537 | 0.031687 | -0.005985 | -0.090186 | -0.043661 | 0.11585 | -0.063737 | -0.14758 | 122.844 | 122.9214 | 122.4567 | 122.5912 | 122.8162 | 122.663 | 122.7327 | 122.6694 | 122.7856 | 122.7479 | 122.6637 | -0.043661 | 0.11585 | -0.063737 | -0.14758 | 122.844 | 122.9214 | 122.4567 | 122.5912 | -122.8877 | -122.5004 | -122.9077 | -122.5204
719.0781 | 122.9507 | -122.7997 | 0.2243 | 0.062332 | -0.08173 | -0.025735 | -0.089116 | 0.031687 | -0.001406 | -0.090186 | -0.043661 | 0.11585 | -0.068315 | -0.15216 | 122.8486 | 122.9168 | 122.4521 | 122.5912 | 122.862 | 122.718 | 122.7739 | 122.7106 | 122.8314 | 122.7983 | 122.7095 | -0.043661 | 0.11585 | -0.068315 | -0.15216 | 122.8486 | 122.9168 | 122.4521 | 122.5912 | -122.8922 | -122.4958 | -122.9169 | -122.5204
720.8281 | 123.0469 | -122.7356 | 0.17853 | 0.057754 | -0.095467 | -0.025735 | -0.089116 | 0.027109 | -0.005985 | -0.090186 | -0.039082 | 0.10211 | -0.059159 | -0.14758 | 122.8394 | 122.9168 | 122.4475 | 122.5866 | 122.7934 | 122.6401 | 122.7099 | 122.6465 | 122.7627 | 122.7296 | 122.6454 | -0.039082 | 0.10211 | -0.059159 | -0.14758 | 122.8394 | 122.9168 | 122.4475 | 122.5866 | -122.8785 | -122.4866 | -122.8986 | -122.5067
722.5781 | 122.9782 | -122.731 | 0.21057 | 0.062332 | -0.090888 | -0.025735 | -0.079959 | 0.027109 | -0.005985 | -0.090186 | -0.029925 | 0.11585 | -0.040846 | -0.15216 | 122.8394 | 122.9214 | 122.443 | 122.5912 | 122.7934 | 122.6401 | 122.7053 | 122.6511 | 122.7581 | 122.725 | 122.6408 | -0.029925 | 0.11585 | -0.040846 | -0.15216 | 122.8394 | 122.9214 | 122.443 | 122.5912 | -122.8693 | -122.4729 | -122.8803 | -122.4838
724.2656 | 122.9645 | -122.7814 | 0.21515 | 0.062332 | -0.08173 | -0.021157 | -0.084537 | 0.036265 | -0.001406 | -0.090186 | -0.01619 | 0.12501 | -0.072894 | -0.15674 | 122.8348 | 122.926 | 122.4521 | 122.5957 | 122.8437 | 122.6996 | 122.7602 | 122.6968 | 122.8176 | 122.78 | 122.6912 | -0.01619 | 0.12501 | -0.072894 | -0.15674 | 122.8348 | 122.926 | 122.4521 | 122.5957 | -122.851 | -122.4683 | -122.9077 | -122.525
726.0156 | 122.9828 | -122.7859 | 0.20142 | 0.071489 | -0.090888 | -0.021157 | -0.089116 | 0.031687 | -0.005985 | -0.090186 | -0.048239 | 0.12043 | -0.027111 | -0.143 | 122.8348 | 122.9214 | 122.4567 | 122.6003 | 122.8574 | 122.6951 | 122.7648 | 122.6968 | 122.8176 | 122.78 | 122.6958 | -0.048239 | 0.12043 | -0.027111 | -0.143 | 122.8348 | 122.9214 | 122.4567 | 122.6003 | -122.8831 | -122.5049 | -122.862 | -122.4838
727.6875 | 123.0469 | -122.7448 | 0.17853 | 0.057754 | -0.086309 | -0.030314 | -0.079959 | 0.027109 | -0.001406 | -0.094765 | -0.048239 | 0.11585 | -0.05458 | -0.14758 | 122.8394 | 122.9168 | 122.443 | 122.5866 | 122.8025 | 122.6584 | 122.7144 | 122.6648 | 122.7719 | 122.7433 | 122.65 | -0.048239 | 0.11585 | -0.05458 | -0.14758 | 122.8394 | 122.9168 | 122.443 | 122.5866 | -122.8877 | -122.4912 | -122.894 | -122.4975
729.4219 | 123.0743 | -122.7356 | 0.1831 | 0.06691 | -0.08173 | -0.025735 | -0.07538 | 0.031687 | 0.003172 | -0.090186 | -0.07571 | 0.11127 | -0.068315 | -0.14758 | 122.8348 | 122.9214 | 122.4475 | 122.5912 | 122.8025 | 122.6539 | 122.7099 | 122.6602 | 122.7673 | 122.7388 | 122.6454 | -0.07571 | 0.11127 | -0.068315 | -0.14758 | 122.8348 | 122.9214 | 122.4475 | 122.5912 | -122.9106 | -122.5233 | -122.9032 | -122.5159
731.1094 | 122.9599 | -122.7768 | 0.21515 | 0.062332 | -0.095467 | -0.012 | -0.089116 | 0.022531 | -0.005985 | -0.090186 | -0.071132 | 0.11127 | -0.063737 | -0.15216 | 122.8394 | 122.9214 | 122.4521 | 122.6003 | 122.8391 | 122.6813 | 122.7648 | 122.6877 | 122.7993 | 122.7708 | 122.6866 | -0.071132 | 0.11127 | -0.063737 | -0.15216 | 122.8394 | 122.9214 | 122.4521 | 122.6003 | -122.9106 | -122.5233 | -122.9032 | -122.5159
732.8438 | 123.056 | -122.7768 | 0.19226 | 0.062332 | -0.095467 | -0.025735 | -0.084537 | 0.031687 | -0.005985 | -0.090186 | -0.048239 | 0.11585 | -0.040846 | -0.14758 | 122.844 | 122.926 | 122.4475 | 122.6003 | 122.8391 | 122.6813 | 122.7511 | 122.6923 | 122.8085 | 122.7708 | 122.6866 | -0.048239 | 0.11585 | -0.040846 | -0.14758 | 122.844 | 122.926 | 122.4475 | 122.6003 | -122.8922 | -122.4958 | -122.8848 | -122.4884
734.5938 | 122.9416 | -122.7676 | 0.21057 | 0.062332 | -0.095467 | -0.030314 | -0.089116 | 0.036265 | 0.003172 | -0.090186 | -0.043661 | 0.11585 | -0.072894 | -0.15216 | 122.8394 | 122.9122 | 122.4521 | 122.5957 | 122.83 | 122.6722 | 122.7373 | 122.6785 | 122.8039 | 122.7708 | 122.6775 | -0.043661 | 0.11585 | -0.072894 | -0.15216 | 122.8394 | 122.9122 | 122.4521 | 122.5957 | -122.8831 | -122.4958 | -122.9123 | -122.525
736.2812 | 123.0515 | -122.7219 | 0.18768 | 0.062332 | -0.090888 | -0.030314 | -0.079959 | 0.031687 | -0.001406 | -0.094765 | -0.043661 | 0.12043 | -0.072894 | -0.15674 | 122.8348 | 122.9168 | 122.4521 | 122.5957 | 122.7842 | 122.631 | 122.6915 | 122.6419 | 122.7536 | 122.7205 | 122.6271 | -0.043661 | 0.12043 | -0.072894 | -0.15674 | 122.8348 | 122.9168 | 122.4521 | 122.5957 | -122.8785 | -122.4958 | -122.9077 | -122.525
738.0312 | 123.0606 | -122.7127 | 0.17853 | 0.062332 | -0.095467 | -0.021157 | -0.089116 | 0.027109 | -0.005985 | -0.090186 | -0.089445 | 0.11127 | -0.077472 | -0.143 | 122.8303 | 122.9122 | 122.443 | 122.5957 | 122.775 | 122.6172 | 122.6916 | 122.6236 | 122.7398 | 122.7067 | 122.6225 | -0.089445 | 0.11127 | -0.077472 | -0.143 | 122.8303 | 122.9122 | 122.443 | 122.5957 | -122.9197 | -122.5324 | -122.9077 | -122.5204
739.7031 | 122.9645 | -122.7676 | 0.19684 | 0.06691 | -0.090888 | -0.034893 | -0.079959 | 0.027109 | -0.001406 | -0.090186 | -0.052818 | 0.11585 | -0.068315 | -0.15216 | 122.8348 | 122.9122 | 122.4475 | 122.5957 | 122.8345 | 122.6768 | 122.7327 | 122.6877 | 122.7947 | 122.7662 | 122.6775 | -0.052818 | 0.11585 | -0.068315 | -0.15216 | 122.8348 | 122.9122 | 122.4475 | 122.5957 | -122.8877 | -122.5004 | -122.9032 | -122.5159
741.4531 | 122.9507 | -122.7585 | 0.2243 | 0.06691 | -0.10004 | -0.025735 | -0.079959 | 0.027109 | -0.005985 | -0.094765 | -0.039082 | 0.10669 | -0.031689 | -0.15216 | 122.8348 | 122.9122 | 122.4338 | 122.582 | 122.8254 | 122.6584 | 122.7327 | 122.6785 | 122.7856 | 122.7525 | 122.6637 | -0.039082 | 0.10669 | -0.031689 | -0.15216 | 122.8348 | 122.9122 | 122.4338 | 122.582 | -122.8739 | -122.4729 | -122.8665 | -122.4655
743.1406 | 122.9828 | -122.7722 | 0.20599 | 0.06691 | -0.086309 | -0.030314 | -0.084537 | 0.017953 | -0.001406 | -0.094765 | -0.061975 | 0.10669 | -0.05458 | -0.15216 | 122.8348 | 122.9122 | 122.4475 | 122.5866 | 122.8391 | 122.6859 | 122.7419 | 122.6877 | 122.7902 | 122.7708 | 122.6775 | -0.061975 | 0.10669 | -0.05458 | -0.15216 | 122.8348 | 122.9122 | 122.4475 | 122.5866 | -122.8968 | -122.5095 | -122.8894 | -122.5021
744.8906 | 122.9462 | -122.7539 | 0.21515 | 0.062332 | -0.090888 | -0.034893 | -0.098273 | 0.022531 | 0.003172 | -0.094765 | -0.034504 | 0.12043 | -0.08205 | -0.14758 | 122.8257 | 122.9168 | 122.4475 | 122.5866 | 122.8162 | 122.663 | 122.719 | 122.6556 | 122.7764 | 122.7571 | 122.6591 | -0.034504 | 0.12043 | -0.08205 | -0.14758 | 122.8257 | 122.9168 | 122.4475 | 122.5866 | -122.8602 | -122.4821 | -122.9077 | -122.5296
746.5938 | 122.9736 | -122.7768 | 0.19226 | 0.06691 | -0.095467 | -0.030314 | -0.084537 | 0.031687 | -0.010563 | -0.099343 | -0.057396 | 0.11585 | -0.072894 | -0.14758 | 122.8257 | 122.9031 | 122.443 | 122.5774 | 122.8437 | 122.6813 | 122.7465 | 122.6923 | 122.8085 | 122.7662 | 122.6775 | -0.057396 | 0.11585 | -0.072894 | -0.14758 | 122.8257 | 122.9031 | 122.443 | 122.5774 | -122.8831 | -122.5004 | -122.8986 | -122.5159
748.3438 | 122.9645 | -122.7676 | 0.1831 | 0.06691 | -0.095467 | -0.021157 | -0.084537 | 0.031687 | -0.005985 | -0.094765 | -0.039082 | 0.11585 | -0.045424 | -0.15216 | 122.8348 | 122.9077 | 122.443 | 122.582 | 122.8345 | 122.6722 | 122.7465 | 122.6831 | 122.7993 | 122.7617 | 122.6729 | -0.039082 | 0.11585 | -0.045424 | -0.15216 | 122.8348 | 122.9077 | 122.443 | 122.582 | -122.8739 | -122.4821 | -122.8803 | -122.4884
750.0938 | 123.0606 | -122.7036 | 0.1831 | 0.062332 | -0.095467 | -0.025735 | -0.084537 | 0.031687 | -0.005985 | -0.099343 | -0.020768 | 0.11127 | -0.072894 | -0.14758 | 122.8257 | 122.9122 | 122.4384 | 122.582 | 122.7659 | 122.6081 | 122.6778 | 122.619 | 122.7352 | 122.6976 | 122.6042 | -0.020768 | 0.11127 | -0.072894 | -0.14758 | 122.8257 | 122.9122 | 122.4384 | 122.582 | -122.8465 | -122.4592 | -122.8986 | -122.5113
751.7656 | 123.0194 | -122.7539 | 0.19684 | 0.062332 | -0.095467 | -0.034893 | -0.084537 | 0.027109 | -0.005985 | -0.090186 | -0.043661 | 0.10669 | -0.027111 | -0.15674 | 122.8211 | 122.9168 | 122.443 | 122.5866 | 122.8162 | 122.6584 | 122.719 | 122.6694 | 122.781 | 122.7479 | 122.6637 | -0.043661 | 0.10669 | -0.027111 | -0.15674 | 122.8211 | 122.9168 | 122.443 | 122.5866 | -122.8648 | -122.4866 | -122.8482 | -122.4701
753.5156 | 123.056 | -122.7219 | 0.17853 | 0.062332 | -0.090888 | -0.030314 | -0.079959 | 0.027109 | -0.005985 | -0.090186 | -0.043661 | 0.11127 | -0.08205 | -0.143 | 122.8303 | 122.9168 | 122.4384 | 122.5774 | 122.7842 | 122.631 | 122.6915 | 122.6419 | 122.749 | 122.7159 | 122.6317 | -0.043661 | 0.11127 | -0.08205 | -0.143 | 122.8303 | 122.9168 | 122.4384 | 122.5774 | -122.8739 | -122.4821 | -122.9123 | -122.5204
755.2656 | 123.0423 | -122.7173 | 0.1831 | 0.062332 | -0.10004 | -0.021157 | -0.089116 | 0.031687 | -0.001406 | -0.10392 | -0.039082 | 0.11585 | -0.050002 | -0.15674 | 122.8257 | 122.9077 | 122.443 | 122.5774 | 122.7796 | 122.6172 | 122.6961 | 122.6282 | 122.749 | 122.7159 | 122.6134 | -0.039082 | 0.11585 | -0.050002 | -0.15674 | 122.8257 | 122.9077 | 122.443 | 122.5774 | -122.8648 | -122.4821 | -122.8757 | -122.493
757.0312 | 122.9736 | -122.7448 | 0.21057 | 0.062332 | -0.095467 | -0.030314 | -0.093694 | 0.022531 | 0.003172 | -0.094765 | -0.043661 | 0.12501 | -0.05458 | -0.15674 | 122.8211 | 122.9122 | 122.4384 | 122.582 | 122.8071 | 122.6493 | 122.7144 | 122.6511 | 122.7673 | 122.7479 | 122.65 | -0.043661 | 0.12501 | -0.05458 | -0.15674 | 122.8211 | 122.9122 | 122.4384 | 122.582 | -122.8648 | -122.4821 | -122.8757 | -122.493
758.7656 | 122.9691 | -122.7676 | 0.19684 | 0.06691 | -0.095467 | -0.030314 | -0.084537 | 0.022531 | -0.001406 | -0.099343 | 0.002124 | 0.12043 | -0.031689 | -0.15216 | 122.8257 | 122.8985 | 122.4475 | 122.582 | 122.8345 | 122.6722 | 122.7373 | 122.6831 | 122.7902 | 122.7662 | 122.6683 | 0.002124 | 0.12043 | -0.031689 | -0.15216 | 122.8257 | 122.8985 | 122.4475 | 122.582 | -122.8236 | -122.4454 | -122.8574 | -122.4792
760.4531 | 122.937 | -122.7722 | 0.20599 | 0.06691 | -0.10462 | -0.025735 | -0.093694 | 0.031687 | 0.00775 | -0.094765 | -0.052818 | 0.12043 | -0.063737 | -0.14758 | 122.8257 | 122.8985 | 122.4292 | 122.5728 | 122.8391 | 122.6676 | 122.7465 | 122.6785 | 122.8039 | 122.78 | 122.6775 | -0.052818 | 0.12043 | -0.063737 | -0.14758 | 122.8257 | 122.8985 | 122.4292 | 122.5728 | -122.8785 | -122.4821 | -122.8894 | -122.493
762.2031 | 123.0789 | -122.7081 | 0.16937 | 0.053175 | -0.095467 | -0.030314 | -0.084537 | 0.022531 | -0.010563 | -0.094765 | -0.080288 | 0.097532 | -0.068315 | -0.15216 | 122.8211 | 122.9031 | 122.4292 | 122.5774 | 122.7613 | 122.6127 | 122.6778 | 122.6236 | 122.7307 | 122.6976 | 122.6134 | -0.080288 | 0.097532 | -0.068315 | -0.15216 | 122.8211 | 122.9031 | 122.4292 | 122.5774 | -122.9014 | -122.5095 | -122.8894 | -122.4975
763.9531 | 122.9187 | -122.7676 | 0.21973 | 0.057754 | -0.090888 | -0.030314 | -0.089116 | 0.027109 | -0.005985 | -0.094765 | -0.07571 | 0.097532 | -0.068315 | -0.15216 | 122.8165 | 122.9031 | 122.4247 | 122.582 | 122.8254 | 122.6768 | 122.7373 | 122.6785 | 122.7947 | 122.7617 | 122.6729 | -0.07571 | 0.097532 | -0.068315 | -0.15216 | 122.8165 | 122.9031 | 122.4247 | 122.582 | -122.8922 | -122.5004 | -122.8848 | -122.493
765.625 | 123.024 | -122.7264 | 0.17853 | 0.06691 | -0.095467 | -0.030314 | -0.079959 | 0.022531 | -0.015142 | -0.099343 | -0.034504 | 0.11585 | -0.040846 | -0.15216 | 122.8303 | 122.8985 | 122.4338 | 122.5728 | 122.7933 | 122.631 | 122.6961 | 122.6465 | 122.749 | 122.7113 | 122.6271 | -0.034504 | 0.11585 | -0.040846 | -0.15216 | 122.8303 | 122.8985 | 122.4338 | 122.5728 | -122.8648 | -122.4683 | -122.8711 | -122.4747
767.375 | 122.9187 | -122.7859 | 0.20599 | 0.062332 | -0.10462 | -0.030314 | -0.093694 | 0.027109 | -0.001406 | -0.094765 | -0.020768 | 0.12501 | -0.050002 | -0.15216 | 122.8303 | 122.9031 | 122.4338 | 122.5866 | 122.8483 | 122.6813 | 122.7556 | 122.6923 | 122.8131 | 122.7845 | 122.6912 | -0.020768 | 0.12501 | -0.050002 | -0.15216 | 122.8303 | 122.9031 | 122.4338 | 122.5866 | -122.851 | -122.4546 | -122.8803 | -122.4838
769.125 | 123.0469 | -122.7264 | 0.18768 | 0.053175 | -0.10462 | -0.039471 | -0.089116 | 0.017953 | -0.010563 | -0.099343 | -0.098602 | 0.12501 | -0.063737 | -0.15216 | 122.8165 | 122.8985 | 122.4292 | 122.582 | 122.7796 | 122.6218 | 122.687 | 122.6373 | 122.7444 | 122.7159 | 122.6271 | -0.098602 | 0.12501 | -0.063737 | -0.15216 | 122.8165 | 122.8985 | 122.4292 | 122.582 | -122.9151 | -122.5278 | -122.8803 | -122.493
770.8125 | 122.9507 | -122.7493 | 0.17395 | 0.071489 | -0.1092 | -0.030314 | -0.079959 | 0.022531 | -0.005985 | -0.094765 | -0.061975 | 0.12043 | -0.072894 | -0.15216 | 122.8257 | 122.9077 | 122.4338 | 122.5728 | 122.8208 | 122.6401 | 122.719 | 122.6694 | 122.7719 | 122.7433 | 122.6546 | -0.061975 | 0.12043 | -0.072894 | -0.15216 | 122.8257 | 122.9077 | 122.4338 | 122.5728 | -122.8877 | -122.4958 | -122.8986 | -122.5067
772.5625 | 122.9507 | -122.7493 | 0.2243 | 0.062332 | -0.10004 | -0.030314 | -0.084537 | 0.022531 | -0.001406 | -0.090186 | -0.084867 | 0.12043 | -0.068315 | -0.14758 | 122.8257 | 122.8985 | 122.4292 | 122.582 | 122.8117 | 122.6493 | 122.719 | 122.6648 | 122.7719 | 122.7479 | 122.6591 | -0.084867 | 0.12043 | -0.068315 | -0.14758 | 122.8257 | 122.8985 | 122.4292 | 122.582 | -122.9106 | -122.5141 | -122.894 | -122.4975
774.3125 | 123.024 | -122.7356 | 0.19226 | 0.053175 | -0.10462 | -0.034893 | -0.093694 | 0.017953 | 0.003172 | -0.094765 | -0.048239 | 0.11585 | -0.031689 | -0.15216 | 122.8074 | 122.9031 | 122.4292 | 122.5728 | 122.7888 | 122.631 | 122.7007 | 122.6419 | 122.7535 | 122.7388 | 122.6408 | -0.048239 | 0.11585 | -0.031689 | -0.15216 | 122.8074 | 122.9031 | 122.4292 | 122.5728 | -122.8556 | -122.4775 | -122.8391 | -122.4609
776 | 122.9874 | -122.7356 | 0.20142 | 0.062332 | -0.10004 | -0.030314 | -0.098273 | 0.022531 | -0.010563 | -0.10392 | -0.057396 | 0.12043 | -0.036267 | -0.14758 | 122.8165 | 122.9031 | 122.4338 | 122.5728 | 122.7979 | 122.6356 | 122.7053 | 122.6373 | 122.7581 | 122.725 | 122.6317 | -0.057396 | 0.12043 | -0.036267 | -0.14758 | 122.8165 | 122.9031 | 122.4338 | 122.5728 | -122.8739 | -122.4912 | -122.8528 | -122.4701
777.7344 | 123.0377 | -122.7585 | 0.19226 | 0.062332 | -0.1092 | -0.034893 | -0.084537 | 0.022531 | -0.005985 | -0.094765 | -0.052818 | 0.11585 | -0.068315 | -0.15216 | 122.812 | 122.8939 | 122.4292 | 122.5728 | 122.8208 | 122.6493 | 122.7236 | 122.6739 | 122.781 | 122.7525 | 122.6637 | -0.052818 | 0.11585 | -0.068315 | -0.15216 | 122.812 | 122.8939 | 122.4292 | 122.5728 | -122.8648 | -122.4821 | -122.8803 | -122.4975
779.4688 | 122.9233 | -122.7676 | 0.21515 | 0.062332 | -0.1092 | -0.034893 | -0.089116 | 0.013375 | -0.015142 | -0.090186 | -0.01619 | 0.12501 | -0.022532 | -0.15674 | 122.8165 | 122.8939 | 122.4292 | 122.5728 | 122.83 | 122.6584 | 122.7327 | 122.6785 | 122.781 | 122.7525 | 122.6775 | -0.01619 | 0.12501 | -0.022532 | -0.15674 | 122.8165 | 122.8939 | 122.4292 | 122.5728 | -122.8327 | -122.4454 | -122.8391 | -122.4518
781.2188 | 122.9416 | -122.7631 | 0.23346 | 0.057754 | -0.10004 | -0.034893 | -0.089116 | 0.017953 | -0.001406 | -0.10392 | -0.043661 | 0.11127 | -0.045424 | -0.143 | 122.8257 | 122.8939 | 122.4338 | 122.5728 | 122.8208 | 122.663 | 122.7282 | 122.6739 | 122.781 | 122.7617 | 122.6591 | -0.043661 | 0.11127 | -0.045424 | -0.143 | 122.8257 | 122.8939 | 122.4338 | 122.5728 | -122.8693 | -122.4775 | -122.8711 | -122.4792
782.9688 | 122.9919 | -122.7264 | 0.17853 | 0.06691 | -0.10462 | -0.030314 | -0.089116 | 0.022531 | -0.010563 | -0.099343 | -0.089445 | 0.11127 | -0.077472 | -0.15216 | 122.8211 | 122.8985 | 122.4247 | 122.5728 | 122.7933 | 122.6218 | 122.6961 | 122.6373 | 122.749 | 122.7159 | 122.6271 | -0.089445 | 0.11127 | -0.077472 | -0.15216 | 122.8211 | 122.8985 | 122.4247 | 122.5728 | -122.9106 | -122.5141 | -122.8986 | -122.5021
784.6406 | 122.9507 | -122.7448 | 0.21057 | 0.062332 | -0.10462 | -0.034893 | -0.093694 | 0.013375 | -0.001406 | -0.094765 | -0.057396 | 0.12501 | -0.05458 | -0.14758 | 122.8165 | 122.8894 | 122.4201 | 122.5637 | 122.8071 | 122.6401 | 122.7099 | 122.6511 | 122.7581 | 122.7433 | 122.65 | -0.057396 | 0.12501 | -0.05458 | -0.14758 | 122.8165 | 122.8894 | 122.4201 | 122.5637 | -122.8739 | -122.4775 | -122.8711 | -122.4747
786.4062 | 122.9553 | -122.7219 | 0.21057 | 0.062332 | -0.10462 | -0.034893 | -0.084537 | 0.022531 | -0.010563 | -0.10392 | -0.07571 | 0.12043 | -0.050002 | -0.15216 | 122.8165 | 122.8894 | 122.4155 | 122.5683 | 122.7842 | 122.6172 | 122.687 | 122.6373 | 122.7444 | 122.7113 | 122.6179 | -0.07571 | 0.12043 | -0.050002 | -0.15216 | 122.8165 | 122.8894 | 122.4155 | 122.5683 | -122.8922 | -122.4912 | -122.8665 | -122.4655
788.0938 | 122.9965 | -122.7173 | 0.19226 | 0.053175 | -0.10004 | -0.039471 | -0.089116 | 0.022531 | -0.005985 | -0.10392 | -0.029925 | 0.12043 | -0.036267 | -0.15216 | 122.8074 | 122.8848 | 122.4201 | 122.5591 | 122.7705 | 122.6172 | 122.6778 | 122.6282 | 122.7398 | 122.7113 | 122.6134 | -0.029925 | 0.12043 | -0.036267 | -0.15216 | 122.8074 | 122.8848 | 122.4201 | 122.5591 | -122.8373 | -122.45 | -122.8436 | -122.4563
789.8438 | 122.9736 | -122.731 | 0.18768 | 0.06691 | -0.095467 | -0.030314 | -0.089116 | 0.017953 | -0.010563 | -0.094765 | -0.066553 | 0.12043 | -0.059159 | -0.15216 | 122.8074 | 122.8894 | 122.4155 | 122.5637 | 122.7979 | 122.6356 | 122.7007 | 122.6419 | 122.749 | 122.7205 | 122.6363 | -0.066553 | 0.12043 | -0.059159 | -0.15216 | 122.8074 | 122.8894 | 122.4155 | 122.5637 | -122.8739 | -122.4821 | -122.8665 | -122.4747
791.5781 | 122.9187 | -122.7539 | 0.20142 | 0.057754 | -0.10004 | -0.034893 | -0.089116 | 0.017953 | -0.005985 | -0.10392 | -0.039082 | 0.12958 | -0.072894 | -0.15216 | 122.8028 | 122.8894 | 122.4292 | 122.5591 | 122.8117 | 122.6539 | 122.719 | 122.6648 | 122.7719 | 122.7479 | 122.65 | -0.039082 | 0.12958 | -0.072894 | -0.15216 | 122.8028 | 122.8894 | 122.4292 | 122.5591 | -122.8419 | -122.4683 | -122.8757 | -122.5021
793.2812 | 123.056 | -122.7173 | 0.18768 | 0.057754 | -0.10004 | -0.039471 | -0.098273 | 0.017953 | -0.010563 | -0.090186 | -0.043661 | 0.12043 | -0.068315 | -0.15216 | 122.812 | 122.8848 | 122.4201 | 122.5591 | 122.775 | 122.6172 | 122.6778 | 122.619 | 122.7352 | 122.7067 | 122.6271 | -0.043661 | 0.12043 | -0.068315 | -0.15216 | 122.812 | 122.8848 | 122.4201 | 122.5591 | -122.8556 | -122.4637 | -122.8803 | -122.4884
795.0156 | 122.9187 | -122.7493 | 0.19684 | 0.057754 | -0.10462 | -0.039471 | -0.089116 | 0.022531 | -0.010563 | -0.10392 | -0.080288 | 0.11585 | -0.072894 | -0.14758 | 122.8028 | 122.8894 | 122.4109 | 122.5545 | 122.8071 | 122.6447 | 122.7099 | 122.6602 | 122.7719 | 122.7388 | 122.6454 | -0.080288 | 0.11585 | -0.072894 | -0.14758 | 122.8028 | 122.8894 | 122.4109 | 122.5545 | -122.8831 | -122.4912 | -122.8757 | -122.4838
796.7656 | 122.9874 | -122.7219 | 0.19226 | 0.062332 | -0.1092 | -0.034893 | -0.093694 | 0.017953 | -0.010563 | -0.10392 | -0.039082 | 0.11585 | -0.013376 | -0.15216 | 122.8028 | 122.8894 | 122.4155 | 122.5545 | 122.7842 | 122.6127 | 122.687 | 122.6282 | 122.7398 | 122.7113 | 122.6179 | -0.039082 | 0.11585 | -0.013376 | -0.15216 | 122.8028 | 122.8894 | 122.4155 | 122.5545 | -122.8419 | -122.4546 | -122.8162 | -122.4289
798.5312 | 122.9645 | -122.7127 | 0.19226 | 0.057754 | -0.095467 | -0.039471 | -0.098273 | 0.022531 | -0.010563 | -0.099343 | -0.01619 | 0.12958 | -0.027111 | -0.15216 | 122.812 | 122.8802 | 122.4109 | 122.5683 | 122.7705 | 122.6172 | 122.6732 | 122.6144 | 122.7352 | 122.7021 | 122.6134 | -0.01619 | 0.12958 | -0.027111 | -0.15216 | 122.812 | 122.8802 | 122.4109 | 122.5683 | -122.8281 | -122.4271 | -122.8391 | -122.438
800.2188 | 122.9507 | -122.7264 | 0.20599 | 0.06691 | -0.10004 | -0.034893 | -0.089116 | 0.017953 | -0.010563 | -0.099343 | -0.048239 | 0.12043 | -0.045424 | -0.143 | 122.8074 | 122.8802 | 122.4155 | 122.5683 | 122.7933 | 122.6264 | 122.6915 | 122.6373 | 122.7444 | 122.7159 | 122.6271 | -0.048239 | 0.12043 | -0.045424 | -0.143 | 122.8074 | 122.8802 | 122.4155 | 122.5683 | -122.8556 | -122.4637 | -122.8528 | -122.4609
801.9531 | 122.9828 | -122.6944 | 0.19684 | 0.062332 | -0.1092 | -0.034893 | -0.093694 | 0.013375 | -0.010563 | -0.1085 | -0.07571 | 0.11585 | -0.072894 | -0.14758 | 122.8074 | 122.8802 | 122.4155 | 122.5545 | 122.7567 | 122.5852 | 122.6595 | 122.6007 | 122.7078 | 122.6838 | 122.5859 | -0.07571 | 0.11585 | -0.072894 | -0.14758 | 122.8074 | 122.8802 | 122.4155 | 122.5545 | -122.8831 | -122.4912 | -122.8803 | -122.4884
803.6406 | 122.8958 | -122.7539 | 0.21515 | 0.06691 | -0.1092 | -0.039471 | -0.093694 | 0.013375 | -0.005985 | -0.094765 | -0.039082 | 0.12501 | -0.063737 | -0.15216 | 122.8074 | 122.8848 | 122.4155 | 122.5683 | 122.8208 | 122.6447 | 122.7144 | 122.6602 | 122.7673 | 122.7479 | 122.6591 | -0.039082 | 0.12501 | -0.063737 | -0.15216 | 122.8074 | 122.8848 | 122.4155 | 122.5683 | -122.8465 | -122.4546 | -122.8711 | -122.4792
805.3906 | 122.9095 | -122.7127 | 0.21057 | 0.06691 | -0.11378 | -0.04405 | -0.10285 | 0.013375 | -0.005985 | -0.10392 | -0.084867 | 0.12958 | -0.063737 | -0.14758 | 122.8074 | 122.8802 | 122.4155 | 122.5637 | 122.7796 | 122.5989 | 122.6687 | 122.6099 | 122.7261 | 122.7067 | 122.6088 | -0.084867 | 0.12958 | -0.063737 | -0.14758 | 122.8074 | 122.8802 | 122.4155 | 122.5637 | -122.8922 | -122.5004 | -122.8711 | -122.4792
807.1562 | 123.0103 | -122.7081 | 0.17853 | 0.062332 | -0.11378 | -0.039471 | -0.089116 | 0.017953 | -0.015142 | -0.1085 | -0.089445 | 0.11585 | -0.068315 | -0.15216 | 122.8028 | 122.8802 | 122.4109 | 122.5637 | 122.7705 | 122.5943 | 122.6687 | 122.619 | 122.7261 | 122.693 | 122.5996 | -0.089445 | 0.11585 | -0.068315 | -0.15216 | 122.8028 | 122.8802 | 122.4109 | 122.5637 | -122.8922 | -122.5004 | -122.8711 | -122.4792
808.8281 | 122.9416 | -122.7539 | 0.21057 | 0.06691 | -0.10462 | -0.04405 | -0.093694 | 0.008797 | -0.015142 | -0.099343 | -0.034504 | 0.12043 | -0.027111 | -0.15216 | 122.8074 | 122.8848 | 122.4201 | 122.5683 | 122.8208 | 122.6493 | 122.7099 | 122.6602 | 122.7627 | 122.7388 | 122.6546 | -0.034504 | 0.12043 | -0.027111 | -0.15216 | 122.8074 | 122.8848 | 122.4201 | 122.5683 | -122.8419 | -122.4546 | -122.8345 | -122.4472
810.5625 | 122.9279 | -122.7402 | 0.21515 | 0.062332 | -0.1092 | -0.04405 | -0.098273 | 0.013375 | -0.01972 | -0.099343 | -0.080288 | 0.11585 | -0.077472 | -0.15674 | 122.8074 | 122.8894 | 122.4155 | 122.5728 | 122.8025 | 122.631 | 122.6961 | 122.6419 | 122.7535 | 122.7205 | 122.6408 | -0.080288 | 0.11585 | -0.077472 | -0.15674 | 122.8074 | 122.8894 | 122.4155 | 122.5728 | -122.8877 | -122.4958 | -122.8848 | -122.493
812.3125 | 122.905 | -122.7585 | 0.1831 | 0.06691 | -0.1092 | -0.039471 | -0.093694 | 0.008797 | -0.015142 | -0.10392 | -0.066553 | 0.12043 | -0.072894 | -0.15216 | 122.812 | 122.8848 | 122.4109 | 122.5637 | 122.8254 | 122.6493 | 122.719 | 122.6648 | 122.7673 | 122.7433 | 122.6546 | -0.066553 | 0.12043 | -0.072894 | -0.15216 | 122.812 | 122.8848 | 122.4109 | 122.5637 | -122.8785 | -122.4775 | -122.8848 | -122.4838
814.0625 | 123.0148 | -122.7219 | 0.17395 | 0.062332 | -0.1092 | -0.039471 | -0.093694 | 0.008797 | -0.015142 | -0.10392 | -0.057396 | 0.11585 | -0.059159 | -0.15216 | 122.7982 | 122.8848 | 122.4063 | 122.5591 | 122.7842 | 122.6127 | 122.6824 | 122.6282 | 122.7307 | 122.7067 | 122.6179 | -0.057396 | 0.11585 | -0.059159 | -0.15216 | 122.7982 | 122.8848 | 122.4063 | 122.5591 | -122.8556 | -122.4637 | -122.8574 | -122.4655
815.75 | 123.0286 | -122.7036 | 0.17853 | 0.06691 | -0.11378 | -0.048628 | -0.093694 | 0.004219 | -0.024298 | -0.10392 | -0.07571 | 0.10669 | -0.077472 | -0.14758 | 122.812 | 122.8802 | 122.4109 | 122.5683 | 122.7705 | 122.5898 | 122.6549 | 122.6099 | 122.7078 | 122.6793 | 122.5996 | -0.07571 | 0.10669 | -0.077472 | -0.14758 | 122.812 | 122.8802 | 122.4109 | 122.5683 | -122.8877 | -122.4866 | -122.8894 | -122.4884
817.5 | 122.9279 | -122.7402 | 0.21973 | 0.057754 | -0.11378 | -0.053207 | -0.093694 | 0.008797 | -0.010563 | -0.10392 | -0.057396 | 0.11585 | -0.063737 | -0.14758 | 122.812 | 122.8894 | 122.4155 | 122.5637 | 122.7979 | 122.6264 | 122.687 | 122.6465 | 122.749 | 122.7296 | 122.6363 | -0.057396 | 0.11585 | -0.063737 | -0.14758 | 122.812 | 122.8894 | 122.4155 | 122.5637 | -122.8693 | -122.4729 | -122.8757 | -122.4792
819.25 | 122.9828 | -122.7219 | 0.20142 | 0.048597 | -0.1092 | -0.048628 | -0.093694 | 0.013375 | -0.010563 | -0.1085 | -0.089445 | 0.11127 | -0.068315 | -0.14758 | 122.8074 | 122.8802 | 122.4109 | 122.5545 | 122.7705 | 122.6127 | 122.6732 | 122.6282 | 122.7352 | 122.7113 | 122.6134 | -0.089445 | 0.11127 | -0.068315 | -0.14758 | 122.8074 | 122.8802 | 122.4109 | 122.5545 | -122.8968 | -122.5004 | -122.8757 | -122.4792
820.9375 | 122.9095 | -122.7585 | 0.22888 | 0.053175 | -0.11378 | -0.048628 | -0.098273 | 0.008797 | -0.01972 | -0.1085 | -0.071132 | 0.11127 | -0.045424 | -0.14758 | 122.7982 | 122.8802 | 122.4109 | 122.5637 | 122.8117 | 122.6447 | 122.7099 | 122.6602 | 122.7673 | 122.7388 | 122.65 | -0.071132 | 0.11127 | -0.045424 | -0.14758 | 122.7982 | 122.8802 | 122.4109 | 122.5637 | -122.8693 | -122.4821 | -122.8436 | -122.4563
822.6875 | 123.0057 | -122.6944 | 0.17395 | 0.062332 | -0.11378 | -0.048628 | -0.098273 | 0.008797 | -0.015142 | -0.1085 | -0.048239 | 0.11127 | -0.050002 | -0.14758 | 122.8074 | 122.8848 | 122.4247 | 122.5591 | 122.7567 | 122.5806 | 122.6458 | 122.5961 | 122.7032 | 122.6793 | 122.5859 | -0.048239 | 0.11127 | -0.050002 | -0.14758 | 122.8074 | 122.8848 | 122.4247 | 122.5591 | -122.8556 | -122.4729 | -122.8574 | -122.4747
824.4375 | 123.0377 | -122.6852 | 0.16937 | 0.06691 | -0.11836 | -0.053207 | -0.098273 | 0.004219 | -0.028877 | -0.1085 | -0.052818 | 0.11127 | -0.045424 | -0.143 | 122.8028 | 122.8848 | 122.4155 | 122.5637 | 122.7522 | 122.5669 | 122.632 | 122.587 | 122.6895 | 122.6564 | 122.5767 | -0.052818 | 0.11127 | -0.045424 | -0.143 | 122.8028 | 122.8848 | 122.4155 | 122.5637 | -122.8556 | -122.4683 | -122.8482 | -122.4609
826.125 | 122.9553 | -122.7127 | 0.20142 | 0.057754 | -0.11378 | -0.04405 | -0.10285 | 0.008797 | -0.024298 | -0.11308 | -0.048239 | 0.11585 | -0.036267 | -0.14758 | 122.7982 | 122.8756 | 122.4109 | 122.5591 | 122.7705 | 122.5989 | 122.6687 | 122.6099 | 122.7215 | 122.6884 | 122.5996 | -0.048239 | 0.11585 | -0.036267 | -0.14758 | 122.7982 | 122.8756 | 122.4109 | 122.5591 | -122.8465 | -122.4592 | -122.8345 | -122.4472
827.8906 | 122.8363 | -122.7768 | 0.21973 | 0.057754 | -0.11378 | -0.04405 | -0.10285 | 0.008797 | -0.01972 | -0.10392 | 0.199 | 0.27153 | 0.17891 | 0.13174 | 0.68002 | 0.71451 | 122.5712 | 122.7193 | 122.8345 | 122.663 | 122.7327 | 122.6739 | 122.7856 | 122.7571 | 122.6729 | 0.199 | 0.27153 | 0.17891 | 0.13174 | 0.68002 | 0.71451 | 122.5712 | 122.7193 | -0.48102 | -122.3722 | -0.50111 | -122.3923
829.5781 | 122.8317 | -122.7448 | 0.21057 | 0.06691 | -0.11836 | -0.053207 | -0.10743 | 0.008797 | -0.01972 | -0.10392 | 0.18984 | 0.26237 | 0.17891 | 0.13632 | 0.080283 | 0.13309 | 122.3834 | 122.7605 | 122.8117 | 122.6264 | 122.6915 | 122.6373 | 122.7535 | 122.725 | 122.6408 | 0.18984 | 0.26237 | 0.17891 | 0.13632 | 0.080283 | 0.13309 | 122.3834 | 122.7605 | 0.10956 | -122.1936 | 0.098629 | -122.2045
831.3281 | 122.9645 | -122.6944 | 0.16022 | 0.062332 | -0.11836 | -0.053207 | -0.10285 | 0.004219 | -0.024298 | -0.11308 | 0.18984 | 0.26237 | -0.05458 | -0.14758 | 0.075705 | 0.1102 | 122.3972 | 122.756 | 122.7567 | 122.576 | 122.6412 | 122.5915 | 122.6986 | 122.6701 | 122.5813 | 0.18984 | 0.26237 | -0.05458 | -0.14758 | 0.075705 | 0.1102 | 122.3972 | 122.756 | 0.11414 | -122.2073 | -0.13028 | -122.4518
833.0625 | 122.85 | -122.7173 | 0.23346 | 0.062332 | -0.11836 | -0.048628 | -0.098273 | 0.008797 | -0.015142 | -0.11765 | 0.18984 | 0.12501 | -0.063737 | -0.143 | 0.066548 | 0.11936 | 122.4018 | 122.5362 | 122.7796 | 122.5989 | 122.6687 | 122.619 | 122.7261 | 122.7021 | 122.5996 | 0.18984 | 0.12501 | -0.063737 | -0.143 | 0.066548 | 0.11936 | 122.4018 | 122.5362 | 0.1233 | -122.2119 | -0.13028 | -122.4655
834.7344 | 122.85 | -122.7264 | 0.21515 | 0.06691 | -0.11378 | -0.053207 | -0.093694 | 0.004219 | -0.015142 | -0.11765 | 0.18984 | 0.11585 | -0.050002 | -0.15674 | 0.066548 | 0.10562 | 122.3926 | 122.5408 | 122.7933 | 122.6127 | 122.6732 | 122.6327 | 122.7307 | 122.7113 | 122.6088 | 0.18984 | 0.11585 | -0.050002 | -0.15674 | 0.066548 | 0.10562 | 122.3926 | 122.5408 | 0.1233 | -122.2028 | -0.11655 | -122.4426
836.4844 | 122.9279 | -122.6898 | 0.20599 | 0.062332 | -0.11378 | -0.04405 | -0.10743 | 0.008797 | -0.024298 | -0.12223 | 0.18984 | 0.12501 | -0.040846 | -0.15674 | 0.06197 | 0.10562 | 122.4018 | 122.5454 | 122.7522 | 122.576 | 122.6458 | 122.5824 | 122.6986 | 122.6655 | 122.5676 | 0.18984 | 0.12501 | -0.040846 | -0.15674 | 0.06197 | 0.10562 | 122.4018 | 122.5454 | 0.12787 | -122.2119 | -0.10282 | -122.4426
838.25 | 123.0148 | -122.6578 | 0.17853 | 0.062332 | -0.11836 | -0.053207 | -0.098273 | 0.008797 | -0.024298 | -0.1085 | 0.19442 | 0.11127 | -0.072894 | -0.143 | 0.057392 | 0.1102 | 122.3926 | 122.5408 | 122.7201 | 122.5394 | 122.6046 | 122.5595 | 122.6666 | 122.6335 | 122.5493 | 0.19442 | 0.11127 | -0.072894 | -0.143 | 0.057392 | 0.1102 | 122.3926 | 122.5408 | 0.13703 | -122.1982 | -0.13029 | -122.4655
839.9375 | 122.8775 | -122.6807 | 0.20599 | 0.057754 | -0.12294 | -0.04405 | -0.10743 | 0.008797 | -0.015142 | -0.1085 | 0.18526 | 0.11585 | -0.077472 | -0.143 | 0.057392 | 0.10562 | 122.3926 | 122.5408 | 122.7384 | 122.5577 | 122.6366 | 122.5732 | 122.6895 | 122.6655 | 122.5722 | 0.18526 | 0.11585 | -0.077472 | -0.143 | 0.057392 | 0.10562 | 122.3926 | 122.5408 | 0.12787 | -122.2073 | -0.13486 | -122.4701
841.6719 | 122.9874 | -122.6898 | 0.15564 | 0.057754 | -0.1092 | -0.053207 | -0.098273 | -0.000359 | -0.024298 | -0.11308 | 0.19442 | 0.10669 | -0.077472 | -0.15674 | 0.066548 | 0.10562 | 122.3972 | 122.5408 | 122.7476 | 122.5806 | 122.6366 | 122.5915 | 122.6895 | 122.6655 | 122.5767 | 0.19442 | 0.10669 | -0.077472 | -0.15674 | 0.066548 | 0.10562 | 122.3972 | 122.5408 | 0.12787 | -122.2028 | -0.14402 | -122.4747
843.4219 | 122.9233 | -122.699 | 0.21057 | 0.057754 | -0.11378 | -0.04405 | -0.10285 | 0.004219 | -0.01972 | -0.11765 | 0.18984 | 0.11585 | -0.08205 | -0.143 | 0.057392 | 0.10105 | 122.3972 | 122.5454 | 122.7567 | 122.5852 | 122.6549 | 122.5961 | 122.7032 | 122.6793 | 122.5813 | 0.18984 | 0.11585 | -0.08205 | -0.143 | 0.057392 | 0.10105 | 122.3972 | 122.5454 | 0.13245 | -122.2073 | -0.13944 | -122.4792
845.1094 | 122.9462 | -122.6761 | 0.19226 | 0.06691 | -0.11378 | -0.048628 | -0.10743 | 0.004219 | -0.01972 | -0.1085 | 0.18984 | 0.12043 | -0.072894 | -0.15674 | 0.057392 | 0.10105 | 122.3926 | 122.5408 | 122.743 | 122.5623 | 122.6275 | 122.5687 | 122.6803 | 122.6564 | 122.5676 | 0.18984 | 0.12043 | -0.072894 | -0.15674 | 0.057392 | 0.10105 | 122.3926 | 122.5408 | 0.13245 | -122.2028 | -0.13029 | -122.4655
846.8438 | 123.0057 | -122.6898 | 0.17395 | 0.053175 | -0.12294 | -0.053207 | -0.10743 | 0.004219 | -0.024298 | -0.11765 | 0.18069 | 0.11585 | -0.072894 | -0.14758 | 0.057392 | 0.10562 | 122.3972 | 122.5454 | 122.743 | 122.5669 | 122.6366 | 122.5824 | 122.694 | 122.6655 | 122.5722 | 0.18069 | 0.11585 | -0.072894 | -0.14758 | 0.057392 | 0.10562 | 122.3972 | 122.5454 | 0.12329 | -122.2165 | -0.13029 | -122.4701
848.5312 | 122.8683 | -122.731 | 0.18768 | 0.057754 | -0.11836 | -0.057786 | -0.10743 | -0.004937 | -0.028877 | -0.11308 | 0.18526 | 0.10669 | -0.077472 | -0.15674 | 0.057392 | 0.10562 | 122.3926 | 122.5454 | 122.7888 | 122.6127 | 122.6732 | 122.6236 | 122.7261 | 122.7021 | 122.6179 | 0.18526 | 0.10669 | -0.077472 | -0.15674 | 0.057392 | 0.10562 | 122.3926 | 122.5454 | 0.12787 | -122.2073 | -0.13486 | -122.4701
850.2656 | 122.8546 | -122.6944 | 0.20142 | 0.062332 | -0.11836 | -0.057786 | -0.10743 | -0.004937 | -0.028877 | -0.11765 | 0.17611 | 0.10669 | -0.050002 | -0.15674 | 0.052814 | 0.1102 | 122.3514 | 122.5087 | 122.7567 | 122.576 | 122.6366 | 122.587 | 122.6895 | 122.6655 | 122.5767 | 0.17611 | 0.10669 | -0.050002 | -0.15674 | 0.052814 | 0.1102 | 122.3514 | 122.5087 | 0.12329 | -122.1753 | -0.10282 | -122.4014
851.9531 | 123.0331 | -122.6532 | 0.1831 | 0.057754 | -0.12294 | -0.048628 | -0.11201 | -0.004937 | -0.024298 | -0.11308 | 0.18984 | 0.10211 | -0.072894 | -0.16131 | 0.057392 | 0.10562 | 122.3972 | 122.5408 | 122.711 | 122.5303 | 122.6046 | 122.5412 | 122.6483 | 122.6289 | 122.5401 | 0.18984 | 0.10211 | -0.072894 | -0.16131 | 0.057392 | 0.10562 | 122.3972 | 122.5408 | 0.13245 | -122.2073 | -0.13029 | -122.4701
853.7031 | 122.9599 | -122.6852 | 0.1831 | 0.062332 | -0.1321 | -0.057786 | -0.11659 | 0.004219 | -0.024298 | -0.11765 | 0.18984 | 0.10669 | -0.077472 | -0.14758 | 0.06197 | 0.10562 | 122.3926 | 122.5408 | 122.7476 | 122.5531 | 122.6275 | 122.5687 | 122.6895 | 122.6609 | 122.5676 | 0.18984 | 0.10669 | -0.077472 | -0.14758 | 0.06197 | 0.10562 | 122.3926 | 122.5408 | 0.12787 | -122.2028 | -0.13944 | -122.4701
855.4531 | 122.9599 | -122.7036 | 0.15106 | 0.071489 | -0.1321 | -0.048628 | -0.11201 | -0.000359 | -0.028877 | -0.11765 | 0.18984 | 0.11585 | -0.068315 | -0.14758 | 0.057392 | 0.096469 | 122.388 | 122.5408 | 122.775 | 122.5715 | 122.6549 | 122.5915 | 122.7032 | 122.6747 | 122.5859 | 0.18984 | 0.11585 | -0.068315 | -0.14758 | 0.057392 | 0.096469 | 122.388 | 122.5408 | 0.13245 | -122.1982 | -0.12571 | -122.4563
857.2031 | 122.8729 | -122.699 | 0.21057 | 0.062332 | -0.11836 | -0.053207 | -0.11201 | 0.004219 | -0.024298 | -0.12223 | 0.19442 | 0.12043 | -0.072894 | -0.15216 | 0.048236 | 0.10562 | 122.3926 | 122.5499 | 122.7613 | 122.5806 | 122.6458 | 122.587 | 122.7032 | 122.6747 | 122.5767 | 0.19442 | 0.12043 | -0.072894 | -0.15216 | 0.048236 | 0.10562 | 122.3926 | 122.5499 | 0.14619 | -122.1982 | -0.12113 | -122.4655
858.875 | 122.9553 | -122.6898 | 0.17395 | 0.057754 | -0.12294 | -0.053207 | -0.11201 | -0.009515 | -0.028877 | -0.12223 | 0.18526 | 0.10211 | -0.072894 | -0.15216 | 0.057392 | 0.10105 | 122.3926 | 122.5362 | 122.7476 | 122.5669 | 122.6366 | 122.5778 | 122.6803 | 122.6609 | 122.5676 | 0.18526 | 0.10211 | -0.072894 | -0.15216 | 0.057392 | 0.10105 | 122.3926 | 122.5362 | 0.12787 | -122.2073 | -0.13029 | -122.4655
860.6094 | 122.9507 | -122.6669 | 0.17853 | 0.053175 | -0.12294 | -0.053207 | -0.10743 | -0.004937 | -0.028877 | -0.12223 | 0.18984 | 0.11127 | -0.072894 | -0.143 | 0.052814 | 0.10105 | 122.3834 | 122.5408 | 122.7201 | 122.544 | 122.6137 | 122.5595 | 122.662 | 122.6381 | 122.5447 | 0.18984 | 0.11127 | -0.072894 | -0.143 | 0.052814 | 0.10105 | 122.3834 | 122.5408 | 0.13703 | -122.1936 | -0.12571 | -122.4563
862.2969 | 122.8226 | -122.7127 | 0.21973 | 0.071489 | -0.12294 | -0.053207 | -0.10285 | -0.004937 | -0.024298 | -0.12681 | 0.19442 | 0.10211 | -0.086628 | -0.14758 | 0.057392 | 0.091891 | 122.388 | 122.5408 | 122.7842 | 122.5898 | 122.6595 | 122.6099 | 122.7078 | 122.6884 | 122.5859 | 0.19442 | 0.10211 | -0.086628 | -0.14758 | 0.057392 | 0.091891 | 122.388 | 122.5408 | 0.13703 | -122.1936 | -0.14402 | -122.4747
864.0469 | 123.0331 | -122.6761 | 0.17395 | 0.06691 | -0.12294 | -0.057786 | -0.11201 | 0.004219 | -0.028877 | -0.12223 | 0.18984 | 0.10211 | -0.086628 | -0.15216 | 0.075705 | 0.13309 | 122.3972 | 122.5499 | 122.743 | 122.5531 | 122.6183 | 122.5641 | 122.6803 | 122.6472 | 122.5539 | 0.18984 | 0.10211 | -0.086628 | -0.15216 | 0.075705 | 0.13309 | 122.3972 | 122.5499 | 0.11414 | -122.2073 | -0.16233 | -122.4838
865.7188 | 122.8683 | -122.699 | 0.20599 | 0.057754 | -0.12294 | -0.057786 | -0.11659 | -0.004937 | -0.028877 | -0.11765 | 0.18526 | 0.11127 | -0.077472 | -0.14758 | 0.071126 | 0.13309 | 122.388 | 122.5408 | 122.7567 | 122.576 | 122.6412 | 122.5824 | 122.694 | 122.6701 | 122.5813 | 0.18526 | 0.11127 | -0.077472 | -0.14758 | 0.071126 | 0.13309 | 122.388 | 122.5408 | 0.11414 | -122.2028 | -0.1486 | -122.4655
867.4688 | 122.8867 | -122.7173 | 0.21057 | 0.062332 | -0.12294 | -0.053207 | -0.11659 | -0.000359 | -0.024298 | -0.13139 | 0.18984 | 0.10669 | -0.05458 | -0.14758 | 0.071126 | 0.12851 | 122.3926 | 122.5408 | 122.7796 | 122.5943 | 122.6641 | 122.6007 | 122.7169 | 122.693 | 122.5859 | 0.18984 | 0.10669 | -0.05458 | -0.14758 | 0.071126 | 0.12851 | 122.3926 | 122.5408 | 0.11872 | -122.2028 | -0.12571 | -122.4472
869.1562 | 122.9965 | -122.6852 | 0.17853 | 0.062332 | -0.12752 | -0.053207 | -0.11659 | -0.004937 | -0.038034 | -0.11765 | 0.18526 | 0.11127 | -0.059159 | -0.14758 | 0.071126 | 0.12394 | 122.3926 | 122.5408 | 122.7476 | 122.5577 | 122.632 | 122.5687 | 122.6803 | 122.6472 | 122.5676 | 0.18526 | 0.11127 | -0.059159 | -0.14758 | 0.071126 | 0.12394 | 122.3926 | 122.5408 | 0.11414 | -122.2073 | -0.13028 | -122.4518
870.8906 | 122.9691 | -122.6761 | 0.20599 | 0.053175 | -0.12294 | -0.057786 | -0.12116 | -0.000359 | -0.033455 | -0.11765 | 0.18526 | 0.10669 | -0.077472 | -0.14758 | 0.075705 | 0.12394 | 122.388 | 122.5454 | 122.7293 | 122.5531 | 122.6183 | 122.5549 | 122.6757 | 122.6426 | 122.5584 | 0.18526 | 0.10669 | -0.077472 | -0.14758 | 0.075705 | 0.12394 | 122.388 | 122.5454 | 0.10956 | -122.2028 | -0.15318 | -122.4655
872.6406 | 122.8592 | -122.7264 | 0.18768 | 0.062332 | -0.12752 | -0.057786 | -0.10743 | -0.000359 | -0.024298 | -0.11308 | 0.18526 | 0.10669 | -0.072894 | -0.15674 | 0.048236 | 0.096469 | 122.3926 | 122.5316 | 122.7888 | 122.5989 | 122.6687 | 122.619 | 122.7261 | 122.7021 | 122.6134 | 0.18526 | 0.10669 | -0.072894 | -0.15674 | 0.048236 | 0.096469 | 122.3926 | 122.5316 | 0.13703 | -122.2073 | -0.12113 | -122.4655
874.3125 | 122.8867 | -122.7173 | 0.21973 | 0.062332 | -0.1321 | -0.053207 | -0.11201 | -0.004937 | -0.033455 | -0.12681 | 0.18526 | 0.10211 | -0.077472 | -0.14758 | 0.052814 | 0.10105 | 122.3926 | 122.5408 | 122.7796 | 122.5852 | 122.6641 | 122.6053 | 122.7123 | 122.6838 | 122.5905 | 0.18526 | 0.10211 | -0.077472 | -0.14758 | 0.052814 | 0.10105 | 122.3926 | 122.5408 | 0.13245 | -122.2073 | -0.13029 | -122.4701
876.0625 | 122.8821 | -122.7081 | 0.19226 | 0.06691 | -0.1321 | -0.057786 | -0.11659 | -0.000359 | -0.028877 | -0.12681 | 0.18526 | 0.11127 | -0.077472 | -0.143 | 0.057392 | 0.096469 | 122.3972 | 122.5408 | 122.775 | 122.576 | 122.6503 | 122.5915 | 122.7078 | 122.6793 | 122.5813 | 0.18526 | 0.11127 | -0.077472 | -0.143 | 0.057392 | 0.096469 | 122.3972 | 122.5408 | 0.12787 | -122.2119 | -0.13486 | -122.4747
877.75 | 122.8683 | -122.7127 | 0.21057 | 0.06691 | -0.1321 | -0.057786 | -0.11201 | -0.004937 | -0.033455 | -0.12223 | 0.18526 | 0.11585 | -0.068315 | -0.14758 | 0.052814 | 0.091891 | 122.4018 | 122.5408 | 122.7796 | 122.5806 | 122.6549 | 122.6007 | 122.7078 | 122.6793 | 122.5905 | 0.18526 | 0.11585 | -0.068315 | -0.14758 | 0.052814 | 0.091891 | 122.4018 | 122.5408 | 0.13245 | -122.2165 | -0.12113 | -122.4701
879.5 | 122.9828 | -122.6486 | 0.16937 | 0.057754 | -0.13668 | -0.066943 | -0.12116 | -0.004937 | -0.028877 | -0.13139 | 0.18984 | 0.11127 | -0.08205 | -0.15216 | 0.057392 | 0.087313 | 122.3789 | 122.5362 | 122.7064 | 122.5119 | 122.5817 | 122.5275 | 122.6437 | 122.6197 | 122.5172 | 0.18984 | 0.11127 | -0.08205 | -0.15216 | 0.057392 | 0.087313 | 122.3789 | 122.5362 | 0.13245 | -122.189 | -0.13944 | -122.4609
881.25 | 122.937 | -122.6807 | 0.16479 | 0.062332 | -0.12752 | -0.057786 | -0.11659 | -0.004937 | -0.028877 | -0.12681 | 0.18526 | 0.10669 | -0.068315 | -0.14758 | 0.052814 | 0.10105 | 122.388 | 122.5362 | 122.743 | 122.5531 | 122.6229 | 122.5641 | 122.6757 | 122.6518 | 122.5539 | 0.18526 | 0.10669 | -0.068315 | -0.14758 | 0.052814 | 0.10105 | 122.388 | 122.5362 | 0.13245 | -122.2028 | -0.12113 | -122.4563
883 | 122.8867 | -122.7127 | 0.20599 | 0.062332 | -0.12752 | -0.053207 | -0.11659 | -0.004937 | -0.033455 | -0.12223 | 0.18984 | 0.11127 | -0.072894 | -0.15216 | 0.098596 | 0.14225 | 122.4018 | 122.5362 | 122.775 | 122.5852 | 122.6595 | 122.5961 | 122.7078 | 122.6793 | 122.5905 | 0.18984 | 0.11127 | -0.072894 | -0.15216 | 0.098596 | 0.14225 | 122.4018 | 122.5362 | 0.091247 | -122.2119 | -0.17149 | -122.4747
884.6719 | 122.85 | -122.7264 | 0.20599 | 0.06691 | -0.12294 | -0.062364 | -0.11201 | -0.009515 | -0.033455 | -0.12223 | -0.043661 | 0.11127 | -0.072894 | -0.14758 | 0.10775 | 0.15598 | 122.388 | 122.5408 | 122.7933 | 122.6035 | 122.6641 | 122.6144 | 122.7169 | 122.693 | 122.6042 | -0.043661 | 0.11127 | -0.072894 | -0.14758 | 0.10775 | 0.15598 | 122.388 | 122.5408 | -0.15141 | -122.4317 | -0.18065 | -122.4609
886.4219 | 122.9599 | -122.6715 | 0.17395 | 0.062332 | -0.12752 | -0.057786 | -0.10743 | -0.004937 | -0.028877 | -0.12223 | -0.029925 | 0.10669 | -0.050002 | -0.143 | 0.10775 | 0.1743 | 122.3926 | 122.5316 | 122.7338 | 122.544 | 122.6137 | 122.5641 | 122.6666 | 122.6426 | 122.5493 | -0.029925 | 0.10669 | -0.050002 | -0.143 | 0.10775 | 0.1743 | 122.3926 | 122.5316 | -0.13768 | -122.4225 | -0.15775 | -122.4426
888.1719 | 122.905 | -122.7081 | 0.18768 | 0.062332 | -0.12752 | -0.057786 | -0.11659 | -0.009515 | -0.033455 | -0.12223 | -0.048239 | 0.11585 | -0.077472 | -0.14758 | 0.11233 | 0.16514 | 122.3926 | 122.5408 | 122.7705 | 122.5806 | 122.6503 | 122.5915 | 122.6986 | 122.6747 | 122.5859 | -0.048239 | 0.11585 | -0.077472 | -0.14758 | 0.11233 | 0.16514 | 122.3926 | 122.5408 | -0.16057 | -122.4408 | -0.1898 | -122.4701
889.9062 | 123.0011 | -122.6532 | 0.17395 | 0.062332 | -0.12294 | -0.057786 | -0.10285 | -0.004937 | -0.028877 | -0.12223 | -0.098602 | 0.092954 | -0.068315 | -0.14758 | 0.11691 | 0.16056 | 122.3834 | 122.5362 | 122.7155 | 122.5303 | 122.5954 | 122.5503 | 122.6483 | 122.6243 | 122.531 | -0.098602 | 0.092954 | -0.068315 | -0.14758 | 0.11691 | 0.16056 | 122.3834 | 122.5362 | -0.21551 | -122.4821 | -0.18522 | -122.4518
891.5938 | 122.9095 | -122.7081 | 0.20142 | 0.062332 | -0.12752 | -0.066943 | -0.11201 | -0.004937 | -0.024298 | -0.12681 | -0.071132 | 0.11127 | -0.072894 | -0.143 | 0.11691 | 0.16056 | 122.3972 | 122.5454 | 122.7705 | 122.5806 | 122.6412 | 122.5961 | 122.7032 | 122.6838 | 122.5813 | -0.071132 | 0.11127 | -0.072894 | -0.143 | 0.11691 | 0.16056 | 122.3972 | 122.5454 | -0.18804 | -122.4683 | -0.1898 | -122.4701
893.3594 | 122.9462 | -122.6852 | 0.16479 | 0.057754 | -0.12294 | -0.062364 | -0.11201 | -0.004937 | -0.033455 | -0.11765 | -0.094024 | 0.12043 | -0.086628 | -0.143 | 0.11691 | 0.16972 | 122.3972 | 122.5408 | 122.743 | 122.5623 | 122.6229 | 122.5732 | 122.6803 | 122.6518 | 122.5676 | -0.094024 | 0.12043 | -0.086628 | -0.143 | 0.11691 | 0.16972 | 122.3972 | 122.5408 | -0.21093 | -122.4912 | -0.20354 | -122.4838
895.0312 | 122.8958 | -122.7127 | 0.19226 | 0.057754 | -0.12752 | -0.057786 | -0.11659 | -0.004937 | -0.024298 | -0.12223 | -0.07571 | 0.10669 | -0.077472 | -0.15216 | 0.12149 | 0.16514 | 122.3926 | 122.5408 | 122.7705 | 122.5852 | 122.6549 | 122.5961 | 122.7078 | 122.6884 | 122.5905 | -0.07571 | 0.10669 | -0.077472 | -0.15216 | 0.12149 | 0.16514 | 122.3926 | 122.5408 | -0.1972 | -122.4683 | -0.19896 | -122.4701
896.7656 | 122.9004 | -122.699 | 0.20142 | 0.062332 | -0.12294 | -0.053207 | -0.11201 | -0.004937 | -0.024298 | -0.11765 | -0.071132 | 0.10669 | -0.077472 | -0.14758 | 0.11691 | 0.16972 | 122.3972 | 122.5316 | 122.7613 | 122.576 | 122.6458 | 122.587 | 122.694 | 122.6747 | 122.5813 | -0.071132 | 0.10669 | -0.077472 | -0.14758 | 0.11691 | 0.16972 | 122.3972 | 122.5316 | -0.18804 | -122.4683 | -0.19438 | -122.4747
898.5156 | 122.9416 | -122.6761 | 0.17395 | 0.057754 | -0.12752 | -0.053207 | -0.11201 | -0.009515 | -0.033455 | -0.12223 | -0.066553 | 0.10669 | -0.08205 | -0.14758 | 0.12149 | 0.16056 | 122.3834 | 122.5408 | 122.7338 | 122.5486 | 122.6229 | 122.5641 | 122.6666 | 122.6426 | 122.5539 | -0.066553 | 0.10669 | -0.08205 | -0.14758 | 0.12149 | 0.16056 | 122.3834 | 122.5408 | -0.18804 | -122.45 | -0.20354 | -122.4655
900.2656 | 122.9599 | -122.6761 | 0.16937 | 0.062332 | -0.1321 | -0.053207 | -0.11659 | -0.004937 | -0.028877 | -0.13139 | -0.10318 | 0.10211 | -0.08205 | -0.16131 | 0.10775 | 0.16056 | 122.3834 | 122.5271 | 122.7384 | 122.544 | 122.6229 | 122.5595 | 122.6711 | 122.6472 | 122.5447 | -0.10318 | 0.10211 | -0.08205 | -0.16131 | 0.10775 | 0.16056 | 122.3834 | 122.5271 | -0.21093 | -122.4866 | -0.1898 | -122.4655
902.0156 | 122.8683 | -122.7356 | 0.2243 | -0.006344 | -0.11836 | -0.04405 | -0.10285 | -0.000359 | -0.024298 | -0.11765 | -0.080288 | 0.11127 | -0.077472 | -0.15674 | 0.12149 | 0.16514 | 122.3972 | 122.5408 | 122.7293 | 122.6172 | 122.6915 | 122.6327 | 122.7352 | 122.7113 | 122.6179 | -0.080288 | 0.11127 | -0.077472 | -0.15674 | 0.12149 | 0.16514 | 122.3972 | 122.5408 | -0.20177 | -122.4775 | -0.19896 | -122.4747
903.7656 | 123.0148 | -122.6624 | 0.16937 | -0.006344 | -0.12752 | -0.039471 | -0.098273 | 0.004219 | -0.015142 | -0.11765 | -0.094024 | 0.092954 | -0.077472 | -0.14758 | 0.10775 | 0.16514 | 122.3789 | 122.5316 | 122.656 | 122.5348 | 122.6229 | 122.5641 | 122.6666 | 122.6472 | 122.5447 | -0.094024 | 0.092954 | -0.077472 | -0.14758 | 0.10775 | 0.16514 | 122.3789 | 122.5316 | -0.20178 | -122.4729 | -0.18522 | -122.4563
905.4531 | 122.8592 | -122.731 | 0.21973 | -0.010922 | -0.11836 | -0.053207 | -0.11201 | -0.000359 | -0.01972 | -0.11765 | -0.084867 | 0.11127 | -0.077472 | -0.15216 | 0.11233 | 0.16972 | 122.3926 | 122.5362 | 122.7201 | 122.6127 | 122.6778 | 122.619 | 122.7307 | 122.7113 | 122.6134 | -0.084867 | 0.11127 | -0.077472 | -0.15216 | 0.11233 | 0.16972 | 122.3926 | 122.5362 | -0.1972 | -122.4775 | -0.1898 | -122.4701
907.2031 | 122.8592 | -122.7264 | 0.20599 | -0.006344 | -0.11836 | -0.053207 | -0.10743 | 0.008797 | -0.028877 | -0.11308 | -0.094024 | 0.10669 | -0.077472 | -0.15216 | 0.12149 | 0.16514 | 122.3972 | 122.5362 | 122.7201 | 122.6081 | 122.6732 | 122.619 | 122.7352 | 122.6976 | 122.6134 | -0.094024 | 0.10669 | -0.077472 | -0.15216 | 0.12149 | 0.16514 | 122.3972 | 122.5362 | -0.21551 | -122.4912 | -0.19896 | -122.4747
908.9531 | 122.9736 | -122.6852 | 0.1831 | -0.010922 | -0.1321 | -0.048628 | -0.10743 | 0.013375 | -0.01972 | -0.12223 | -0.084867 | 0.10669 | -0.068315 | -0.143 | 0.11691 | 0.16514 | 122.3926 | 122.5408 | 122.6743 | 122.5531 | 122.6366 | 122.5778 | 122.6986 | 122.6655 | 122.563 | -0.084867 | 0.10669 | -0.068315 | -0.143 | 0.11691 | 0.16514 | 122.3926 | 122.5408 | -0.20177 | -122.4775 | -0.18522 | -122.4609
910.625 | 122.9874 | -122.6807 | 0.18768 | -0.001765 | -0.11836 | -0.04405 | -0.098273 | 0.004219 | -0.024298 | -0.11765 | -0.084867 | 0.10669 | -0.077472 | -0.14758 | 0.11691 | 0.16972 | 122.388 | 122.5362 | 122.6789 | 122.5623 | 122.6366 | 122.5824 | 122.6849 | 122.6564 | 122.563 | -0.084867 | 0.10669 | -0.077472 | -0.14758 | 0.11691 | 0.16972 | 122.388 | 122.5362 | -0.20177 | -122.4729 | -0.19438 | -122.4655
912.3594 | 122.8638 | -122.7219 | 0.17853 | -0.006344 | -0.11836 | -0.048628 | -0.11201 | 0.013375 | -0.01972 | -0.1085 | -0.094024 | 0.10211 | -0.072894 | -0.14758 | 0.11691 | 0.16056 | 122.3834 | 122.5362 | 122.7155 | 122.6035 | 122.6732 | 122.6099 | 122.7352 | 122.7021 | 122.6134 | -0.094024 | 0.10211 | -0.072894 | -0.14758 | 0.11691 | 0.16056 | 122.3834 | 122.5362 | -0.21093 | -122.4775 | -0.1898 | -122.4563
914.0938 | 122.85 | -122.7081 | 0.20599 | -0.010922 | -0.12294 | -0.048628 | -0.10285 | 0.008797 | -0.024298 | -0.11765 | -0.07571 | 0.11127 | -0.077472 | -0.15216 | 0.11691 | 0.16972 | 122.3789 | 122.5362 | 122.6972 | 122.5852 | 122.6595 | 122.6053 | 122.7169 | 122.6838 | 122.5905 | -0.07571 | 0.11127 | -0.077472 | -0.15216 | 0.11691 | 0.16972 | 122.3789 | 122.5362 | -0.19262 | -122.4546 | -0.19438 | -122.4563
915.7656 | 122.85 | -122.7173 | 0.19684 | 0.002813 | -0.12294 | -0.053207 | -0.10743 | -0.000359 | -0.028877 | -0.12223 | -0.061975 | 0.10669 | -0.059159 | -0.14758 | 0.11233 | 0.16514 | 122.3789 | 122.5316 | 122.7201 | 122.5943 | 122.6641 | 122.6099 | 122.7169 | 122.6884 | 122.5951 | -0.061975 | 0.10669 | -0.059159 | -0.14758 | 0.11233 | 0.16514 | 122.3789 | 122.5316 | -0.1743 | -122.4408 | -0.17149 | -122.438
917.5 | 122.8455 | -122.6944 | 0.20142 | -0.006344 | -0.11836 | -0.048628 | -0.11201 | -0.000359 | -0.010563 | -0.11765 | -0.057396 | 0.10669 | -0.068315 | -0.143 | 0.11233 | 0.16514 | 122.3834 | 122.5362 | 122.6881 | 122.576 | 122.6458 | 122.5824 | 122.694 | 122.6838 | 122.5767 | -0.057396 | 0.10669 | -0.068315 | -0.143 | 0.11233 | 0.16514 | 122.3834 | 122.5362 | -0.16973 | -122.4408 | -0.18065 | -122.4518
919.25 | 122.9645 | -122.6715 | 0.17853 | -0.010922 | -0.11836 | -0.048628 | -0.10743 | 0.004219 | -0.028877 | -0.11308 | -0.061975 | 0.10669 | -0.086628 | -0.143 | 0.11691 | 0.16514 | 122.3834 | 122.5362 | 122.6606 | 122.5531 | 122.6229 | 122.5641 | 122.6757 | 122.6426 | 122.5584 | -0.061975 | 0.10669 | -0.086628 | -0.143 | 0.11691 | 0.16514 | 122.3834 | 122.5362 | -0.17888 | -122.4454 | -0.20354 | -122.4701
921 | 122.8546 | -122.7036 | 0.17853 | -0.010922 | -0.12752 | -0.053207 | -0.11201 | 0.004219 | -0.024298 | -0.11308 | -0.071132 | 0.10669 | -0.086628 | -0.15216 | 0.11233 | 0.16514 | 122.3789 | 122.5271 | 122.6926 | 122.576 | 122.6503 | 122.5915 | 122.7078 | 122.6793 | 122.5905 | -0.071132 | 0.10669 | -0.086628 | -0.15216 | 0.11233 | 0.16514 | 122.3789 | 122.5271 | -0.18346 | -122.45 | -0.19896 | -122.4655
922.6719 | 122.8317 | -122.6669 | 0.19226 | -0.015501 | -0.12752 | -0.048628 | -0.10285 | 0.008797 | -0.01972 | -0.11308 | -0.094024 | 0.10211 | -0.08205 | -0.15216 | 0.10775 | 0.16056 | 122.3834 | 122.5316 | 122.6514 | 122.5394 | 122.6183 | 122.5641 | 122.6757 | 122.6472 | 122.5539 | -0.094024 | 0.10211 | -0.08205 | -0.15216 | 0.10775 | 0.16056 | 122.3834 | 122.5316 | -0.20178 | -122.4775 | -0.1898 | -122.4655
924.4375 | 122.9279 | -122.6807 | 0.15564 | -0.001765 | -0.12752 | -0.04405 | -0.11201 | -0.000359 | -0.024298 | -0.12223 | -0.07571 | 0.097532 | -0.077472 | -0.14758 | 0.10775 | 0.15598 | 122.3834 | 122.5225 | 122.6789 | 122.5531 | 122.6366 | 122.5687 | 122.6803 | 122.6564 | 122.5584 | -0.07571 | 0.097532 | -0.077472 | -0.14758 | 0.10775 | 0.15598 | 122.3834 | 122.5225 | -0.18346 | -122.4592 | -0.18522 | -122.4609
926.125 | 122.937 | -122.6944 | 0.17395 | -0.006344 | -0.12752 | -0.039471 | -0.11201 | -0.000359 | -0.01972 | -0.11308 | -0.098602 | 0.097532 | -0.086628 | -0.143 | 0.12149 | 0.16972 | 122.3743 | 122.5362 | 122.6881 | 122.5669 | 122.6549 | 122.5824 | 122.694 | 122.6747 | 122.5813 | -0.098602 | 0.097532 | -0.086628 | -0.143 | 0.12149 | 0.16972 | 122.3743 | 122.5362 | -0.22009 | -122.4729 | -0.20811 | -122.4609
927.8594 | 122.8546 | -122.7081 | 0.21057 | -0.006344 | -0.12752 | -0.048628 | -0.11201 | 0.004219 | -0.01972 | -0.11308 | -0.084867 | 0.11585 | -0.08205 | -0.14758 | 0.11691 | 0.16514 | 122.388 | 122.5316 | 122.7018 | 122.5806 | 122.6595 | 122.5961 | 122.7123 | 122.6884 | 122.5951 | -0.084867 | 0.11585 | -0.08205 | -0.14758 | 0.11691 | 0.16514 | 122.388 | 122.5316 | -0.20177 | -122.4729 | -0.19896 | -122.4701
929.6094 | 122.9553 | -122.612 | 0.17395 | -0.001765 | -0.12294 | -0.04405 | -0.10743 | 0.004219 | -0.024298 | -0.11765 | -0.10318 | 0.10669 | -0.08205 | -0.14758 | 0.11233 | 0.16514 | 122.3789 | 122.5271 | 122.6102 | 122.4891 | 122.5679 | 122.5046 | 122.6162 | 122.5877 | 122.4943 | -0.10318 | 0.10669 | -0.08205 | -0.14758 | 0.11233 | 0.16514 | 122.3789 | 122.5271 | -0.21551 | -122.4821 | -0.19438 | -122.4609
931.3594 | 122.8546 | -122.7081 | 0.20142 | -0.010922 | -0.12294 | -0.053207 | -0.10743 | -0.000359 | -0.028877 | -0.11308 | -0.061975 | 0.11585 | -0.068315 | -0.14758 | 0.12149 | 0.16972 | 122.3789 | 122.5316 | 122.6972 | 122.5852 | 122.6549 | 122.6007 | 122.7078 | 122.6793 | 122.5951 | -0.061975 | 0.11585 | -0.068315 | -0.14758 | 0.12149 | 0.16972 | 122.3789 | 122.5316 | -0.18346 | -122.4408 | -0.1898 | -122.4472
933.1094 | 122.8729 | -122.6898 | 0.21515 | -0.010922 | -0.12752 | -0.053207 | -0.11201 | 0.004219 | -0.028877 | -0.1085 | -0.098602 | 0.11127 | -0.08205 | -0.143 | 0.12149 | 0.16972 | 122.388 | 122.5271 | 122.6789 | 122.5623 | 122.6366 | 122.5778 | 122.694 | 122.6609 | 122.5813 | -0.098602 | 0.11127 | -0.08205 | -0.143 | 0.12149 | 0.16972 | 122.388 | 122.5271 | -0.22009 | -122.4866 | -0.20354 | -122.4701
934.8438 | 122.8775 | -122.6944 | 0.19226 | -0.015501 | -0.1321 | -0.04405 | -0.11201 | -0.000359 | -0.01972 | -0.11308 | -0.084867 | 0.10669 | -0.077472 | -0.143 | 0.12149 | 0.16514 | 122.3789 | 122.5271 | 122.6789 | 122.5623 | 122.6503 | 122.5824 | 122.694 | 122.6747 | 122.5813 | -0.084867 | 0.10669 | -0.077472 | -0.143 | 0.12149 | 0.16514 | 122.3789 | 122.5271 | -0.20635 | -122.4637 | -0.19896 | -122.4563
936.5938 | 122.9736 | -122.644 | 0.15564 | -0.015501 | -0.1321 | -0.048628 | -0.11201 | -0.000359 | -0.024298 | -0.11308 | -0.048239 | 0.097532 | -0.072894 | -0.15216 | 0.11233 | 0.16514 | 122.3789 | 122.5225 | 122.6285 | 122.5119 | 122.5954 | 122.532 | 122.6437 | 122.6197 | 122.531 | -0.048239 | 0.097532 | -0.072894 | -0.15216 | 0.11233 | 0.16514 | 122.3789 | 122.5225 | -0.16057 | -122.4271 | -0.18522 | -122.4518
938.2812 | 122.9507 | -122.6486 | 0.17853 | -0.001765 | -0.12752 | -0.053207 | -0.10743 | 0.004219 | -0.024298 | -0.11308 | -0.098602 | 0.097532 | -0.08205 | -0.15674 | 0.11691 | 0.16514 | 122.3697 | 122.5271 | 122.6469 | 122.5211 | 122.5954 | 122.5412 | 122.6528 | 122.6243 | 122.5355 | -0.098602 | 0.097532 | -0.08205 | -0.15674 | 0.11691 | 0.16514 | 122.3697 | 122.5271 | -0.21551 | -122.4683 | -0.19896 | -122.4518
940.0312 | 122.8363 | -122.7219 | 0.20599 | -0.006344 | -0.1321 | -0.048628 | -0.10743 | -0.000359 | -0.024298 | -0.11308 | -0.10318 | 0.10669 | -0.08205 | -0.143 | 0.11691 | 0.16972 | 122.3789 | 122.5316 | 122.7155 | 122.5898 | 122.6732 | 122.6144 | 122.7215 | 122.6976 | 122.6088 | -0.10318 | 0.10669 | -0.08205 | -0.143 | 0.11691 | 0.16972 | 122.3789 | 122.5316 | -0.22009 | -122.4821 | -0.19896 | -122.4609
941.7188 | 122.8775 | -122.6715 | 0.16937 | -0.015501 | -0.1321 | -0.053207 | -0.10743 | -0.004937 | -0.01972 | -0.11308 | -0.10318 | 0.10669 | -0.08205 | -0.143 | 0.10775 | 0.16514 | 122.3743 | 122.5271 | 122.656 | 122.5394 | 122.6183 | 122.5641 | 122.6666 | 122.6518 | 122.5584 | -0.10318 | 0.10669 | -0.08205 | -0.143 | 0.10775 | 0.16514 | 122.3743 | 122.5271 | -0.21093 | -122.4775 | -0.1898 | -122.4563
943.4688 | 122.8455 | -122.699 | 0.20599 | -0.010922 | -0.1321 | -0.053207 | -0.10743 | 0.004219 | -0.024298 | -0.11308 | -0.094024 | 0.10211 | -0.08205 | -0.13842 | 0.12607 | 0.16972 | 122.3834 | 122.5316 | 122.6881 | 122.5669 | 122.6458 | 122.5915 | 122.7032 | 122.6747 | 122.5859 | -0.094024 | 0.10211 | -0.08205 | -0.13842 | 0.12607 | 0.16972 | 122.3834 | 122.5316 | -0.22009 | -122.4775 | -0.20811 | -122.4655
945.2031 | 122.8363 | -122.6852 | 0.18768 | -0.001765 | -0.13668 | -0.048628 | -0.11201 | -0.000359 | -0.01972 | -0.11308 | -0.061975 | 0.10669 | -0.072894 | -0.143 | 0.12149 | 0.16514 | 122.3834 | 122.5225 | 122.6835 | 122.5486 | 122.6366 | 122.5732 | 122.6849 | 122.6655 | 122.5722 | -0.061975 | 0.10669 | -0.072894 | -0.143 | 0.12149 | 0.16514 | 122.3834 | 122.5225 | -0.18346 | -122.4454 | -0.19438 | -122.4563
946.9375 | 122.9324 | -122.6578 | 0.16937 | -0.010922 | -0.13668 | -0.057786 | -0.11201 | -0.004937 | -0.01972 | -0.11765 | -0.089445 | 0.097532 | -0.08205 | -0.15216 | 0.11233 | 0.16514 | 122.3697 | 122.5179 | 122.6469 | 122.5211 | 122.6 | 122.5458 | 122.6528 | 122.6381 | 122.5401 | -0.089445 | 0.097532 | -0.08205 | -0.15216 | 0.11233 | 0.16514 | 122.3697 | 122.5179 | -0.20177 | -122.4592 | -0.19438 | -122.4518
948.625 | 122.9691 | -122.6669 | 0.14648 | -0.015501 | -0.14125 | -0.053207 | -0.11201 | -0.004937 | -0.033455 | -0.11308 | -0.10318 | 0.10211 | -0.08205 | -0.15216 | 0.11691 | 0.16972 | 122.3743 | 122.5225 | 122.6514 | 122.5257 | 122.6137 | 122.5549 | 122.662 | 122.6335 | 122.5539 | -0.10318 | 0.10211 | -0.08205 | -0.15216 | 0.11691 | 0.16972 | 122.3743 | 122.5225 | -0.22009 | -122.4775 | -0.19896 | -122.4563
950.3125 | 122.8912 | -122.6669 | 0.17853 | -0.010922 | -0.1321 | -0.04405 | -0.11201 | 0.004219 | -0.015142 | -0.11308 | -0.094024 | 0.10211 | -0.086628 | -0.143 | 0.11233 | 0.16972 | 122.3743 | 122.5271 | 122.656 | 122.5348 | 122.6229 | 122.5549 | 122.6712 | 122.6518 | 122.5539 | -0.094024 | 0.10211 | -0.086628 | -0.143 | 0.11233 | 0.16972 | 122.3743 | 122.5271 | -0.20635 | -122.4683 | -0.19896 | -122.4609
952.0625 | 122.8592 | -122.6852 | 0.16937 | -0.001765 | -0.1321 | -0.048628 | -0.12116 | 0.004219 | -0.01972 | -0.11765 | -0.10318 | 0.097532 | -0.077472 | -0.14758 | 0.11691 | 0.16972 | 122.3697 | 122.5179 | 122.6835 | 122.5531 | 122.6366 | 122.5641 | 122.6895 | 122.6655 | 122.5676 | -0.10318 | 0.097532 | -0.077472 | -0.14758 | 0.11691 | 0.16972 | 122.3697 | 122.5179 | -0.22009 | -122.4729 | -0.19438 | -122.4472
953.75 | 122.905 | -122.6715 | 0.1831 | -0.006344 | -0.13668 | -0.048628 | -0.10285 | 0.013375 | -0.024298 | -0.11308 | -0.089445 | 0.10211 | -0.08205 | -0.143 | 0.11691 | 0.1743 | 122.3743 | 122.5179 | 122.6652 | 122.5348 | 122.6229 | 122.5687 | 122.6849 | 122.6472 | 122.5584 | -0.089445 | 0.10211 | -0.08205 | -0.143 | 0.11691 | 0.1743 | 122.3743 | 122.5179 | -0.20635 | -122.4637 | -0.19896 | -122.4563
955.5 | 122.85 | -122.6532 | 0.19226 | -0.001765 | -0.13668 | -0.04405 | -0.10743 | 0.004219 | -0.024298 | -0.11308 | -0.098602 | 0.092954 | -0.072894 | -0.15216 | 0.12149 | 0.16514 | 122.3697 | 122.5133 | 122.6514 | 122.5165 | 122.6091 | 122.5458 | 122.6574 | 122.6289 | 122.5401 | -0.098602 | 0.092954 | -0.072894 | -0.15216 | 0.12149 | 0.16514 | 122.3697 | 122.5133 | -0.22009 | -122.4683 | -0.19438 | -122.4426
957.1875 | 122.9553 | -122.6669 | 0.17395 | -0.010922 | -0.14125 | -0.057786 | -0.10285 | -0.004937 | -0.010563 | -0.11765 | -0.061975 | 0.10669 | -0.077472 | -0.14758 | 0.11233 | 0.16972 | 122.3697 | 122.5133 | 122.656 | 122.5257 | 122.6091 | 122.5641 | 122.662 | 122.6564 | 122.5493 | -0.061975 | 0.10669 | -0.077472 | -0.14758 | 0.11233 | 0.16972 | 122.3697 | 122.5133 | -0.1743 | -122.4317 | -0.1898 | -122.4472
958.9375 | 122.905 | -122.6807 | 0.1831 | -0.001765 | -0.1321 | -0.048628 | -0.10285 | 0.004219 | -0.015142 | -0.1085 | -0.10318 | 0.10211 | -0.077472 | -0.143 | 0.11233 | 0.16972 | 122.3697 | 122.5133 | 122.6789 | 122.5486 | 122.632 | 122.5778 | 122.6849 | 122.6655 | 122.5722 | -0.10318 | 0.10211 | -0.077472 | -0.143 | 0.11233 | 0.16972 | 122.3697 | 122.5133 | -0.21551 | -122.4729 | -0.1898 | -122.4472
960.6719 | 122.8317 | -122.7127 | 0.20599 | -0.006344 | -0.13668 | -0.048628 | -0.11201 | -0.000359 | -0.015142 | -0.11308 | -0.057396 | 0.10211 | -0.072894 | -0.15216 | 0.12149 | 0.1743 | 122.3743 | 122.5179 | 122.7064 | 122.576 | 122.6641 | 122.6007 | 122.7123 | 122.6976 | 122.5996 | -0.057396 | 0.10211 | -0.072894 | -0.15216 | 0.12149 | 0.1743 | 122.3743 | 122.5179 | -0.17888 | -122.4317 | -0.19438 | -122.4472
962.4062 | 122.8867 | -122.6624 | 0.19226 | -0.015501 | -0.1321 | -0.048628 | -0.10285 | 0.004219 | -0.01972 | -0.11308 | -0.080288 | 0.10211 | -0.072894 | -0.14758 | 0.11691 | 0.16514 | 122.3651 | 122.5133 | 122.6469 | 122.5303 | 122.6137 | 122.5595 | 122.6666 | 122.6426 | 122.5493 | -0.080288 | 0.10211 | -0.072894 | -0.14758 | 0.11691 | 0.16514 | 122.3651 | 122.5133 | -0.1972 | -122.4454 | -0.1898 | -122.438
964.0938 | 122.8317 | -122.731 | 0.20599 | -0.010922 | -0.1321 | -0.048628 | -0.10743 | 0.004219 | -0.01972 | -0.10392 | -0.07571 | 0.097532 | -0.077472 | -0.15216 | 0.12607 | 0.16514 | 122.3651 | 122.5133 | 122.7201 | 122.5989 | 122.6824 | 122.6236 | 122.7352 | 122.7113 | 122.6271 | -0.07571 | 0.097532 | -0.077472 | -0.15216 | 0.12607 | 0.16514 | 122.3651 | 122.5133 | -0.20178 | -122.4408 | -0.20354 | -122.4426
965.8281 | 122.8867 | -122.6761 | 0.19684 | -0.010922 | -0.1321 | -0.04405 | -0.10743 | 0.008797 | -0.01972 | -0.11308 | -0.089445 | 0.092954 | -0.077472 | -0.15674 | 0.11691 | 0.16972 | 122.3697 | 122.5179 | 122.6652 | 122.544 | 122.632 | 122.5687 | 122.6849 | 122.6564 | 122.563 | -0.089445 | 0.092954 | -0.077472 | -0.15674 | 0.11691 | 0.16972 | 122.3697 | 122.5179 | -0.20635 | -122.4592 | -0.19438 | -122.4472
967.5781 | 122.9507 | -122.644 | 0.16022 | -0.010922 | -0.13668 | -0.048628 | -0.10285 | 0.008797 | -0.024298 | -0.11308 | -0.07571 | 0.10211 | -0.072894 | -0.15216 | 0.11233 | 0.1743 | 122.3606 | 122.5042 | 122.6331 | 122.5074 | 122.5954 | 122.5412 | 122.6528 | 122.6197 | 122.531 | -0.07571 | 0.10211 | -0.072894 | -0.15216 | 0.11233 | 0.1743 | 122.3606 | 122.5042 | -0.18804 | -122.4363 | -0.18522 | -122.4335
969.2656 | 122.9965 | -122.644 | 0.15564 | -0.015501 | -0.1321 | -0.053207 | -0.11201 | 0.004219 | -0.028877 | -0.12681 | -0.094024 | 0.10211 | -0.08205 | -0.143 | 0.11233 | 0.16972 | 122.3651 | 122.5087 | 122.6285 | 122.5119 | 122.5908 | 122.532 | 122.6483 | 122.6152 | 122.5172 | -0.094024 | 0.10211 | -0.08205 | -0.143 | 0.11233 | 0.16972 | 122.3651 | 122.5087 | -0.20635 | -122.4592 | -0.19438 | -122.4472
971 | 122.8867 | -122.6852 | 0.19226 | -0.006344 | -0.1321 | -0.04405 | -0.10285 | 0.004219 | -0.024298 | -0.11308 | -0.094024 | 0.092954 | -0.072894 | -0.15674 | 0.11233 | 0.16972 | 122.3743 | 122.5133 | 122.6789 | 122.5531 | 122.6412 | 122.5824 | 122.6895 | 122.6609 | 122.5722 | -0.094024 | 0.092954 | -0.072894 | -0.15674 | 0.11233 | 0.16972 | 122.3743 | 122.5133 | -0.20635 | -122.4683 | -0.18522 | -122.4472
972.75 | 122.8638 | -122.699 | 0.20142 | -0.010922 | -0.1321 | -0.04405 | -0.10743 | 0.004219 | -0.024298 | -0.1085 | -0.080288 | 0.10669 | -0.077472 | -0.15216 | 0.12149 | 0.16972 | 122.3743 | 122.5179 | 122.6881 | 122.5669 | 122.6549 | 122.5915 | 122.7032 | 122.6747 | 122.5905 | -0.080288 | 0.10669 | -0.077472 | -0.15216 | 0.12149 | 0.16972 | 122.3743 | 122.5179 | -0.20177 | -122.4546 | -0.19896 | -122.4518
974.5156 | 122.937 | -122.6486 | 0.1831 | -0.010922 | -0.14125 | -0.053207 | -0.11659 | 0.004219 | -0.028877 | -0.11765 | -0.07571 | 0.10669 | -0.08205 | -0.14758 | 0.11691 | 0.1743 | 122.356 | 122.5133 | 122.6377 | 122.5074 | 122.5954 | 122.532 | 122.6528 | 122.6197 | 122.531 | -0.07571 | 0.10669 | -0.08205 | -0.14758 | 0.11691 | 0.1743 | 122.356 | 122.5133 | -0.19262 | -122.4317 | -0.19896 | -122.438
976.2031 | 122.937 | -122.6624 | 0.14191 | -0.010922 | -0.13668 | -0.048628 | -0.11201 | 0.004219 | -0.01972 | -0.1085 | -0.071132 | 0.092954 | -0.05458 | -0.14758 | 0.12149 | 0.16514 | 122.3606 | 122.5087 | 122.6514 | 122.5257 | 122.6137 | 122.5503 | 122.6666 | 122.6426 | 122.5539 | -0.071132 | 0.092954 | -0.05458 | -0.14758 | 0.12149 | 0.16514 | 122.3606 | 122.5087 | -0.19262 | -122.4317 | -0.17607 | -122.4151
977.9531 | 122.9416 | -122.6074 | 0.16479 | -0.006344 | -0.14125 | -0.053207 | -0.10743 | 0.008797 | -0.015142 | -0.12223 | -0.061975 | 0.097532 | -0.08205 | -0.14758 | 0.10317 | 0.16972 | 122.3606 | 122.5133 | 122.6011 | 122.4662 | 122.5542 | 122.5 | 122.6162 | 122.5923 | 122.4852 | -0.061975 | 0.097532 | -0.08205 | -0.14758 | 0.10317 | 0.16972 | 122.3606 | 122.5133 | -0.16515 | -122.4225 | -0.18522 | -122.4426
979.7188 | 122.9187 | -122.6578 | 0.16937 | -0.015501 | -0.14583 | -0.048628 | -0.11201 | 0.004219 | -0.028877 | -0.11765 | -0.071132 | 0.10211 | -0.077472 | -0.14758 | 0.10775 | 0.16972 | 122.3651 | 122.5133 | 122.6423 | 122.5119 | 122.6091 | 122.5458 | 122.662 | 122.6289 | 122.5401 | -0.071132 | 0.10211 | -0.077472 | -0.14758 | 0.10775 | 0.16972 | 122.3651 | 122.5133 | -0.17888 | -122.4363 | -0.18522 | -122.4426
981.4062 | 122.8592 | -122.6715 | 0.21057 | -0.001765 | -0.1321 | -0.04405 | -0.10743 | 0.013375 | -0.01972 | -0.1085 | -0.080288 | 0.10669 | -0.08205 | -0.14758 | 0.12149 | 0.1743 | 122.3651 | 122.5133 | 122.6697 | 122.5394 | 122.6275 | 122.5641 | 122.6849 | 122.6518 | 122.563 | -0.080288 | 0.10669 | -0.08205 | -0.14758 | 0.12149 | 0.1743 | 122.3651 | 122.5133 | -0.20177 | -122.4454 | -0.20354 | -122.4472
983.0781 | 122.9553 | -122.6257 | 0.14648 | -0.010922 | -0.14125 | -0.048628 | -0.11201 | -0.000359 | -0.024298 | -0.11308 | -0.07571 | 0.10211 | -0.077472 | -0.15674 | 0.11233 | 0.1743 | 122.3606 | 122.5042 | 122.6148 | 122.4845 | 122.5771 | 122.5137 | 122.6254 | 122.6014 | 122.5127 | -0.07571 | 0.10211 | -0.077472 | -0.15674 | 0.11233 | 0.1743 | 122.3606 | 122.5042 | -0.18804 | -122.4363 | -0.1898 | -122.438
984.8281 | 122.9004 | -122.6578 | 0.17853 | -0.015501 | -0.13668 | -0.053207 | -0.11201 | -0.004937 | -0.024298 | -0.11765 | -0.10318 | 0.097532 | -0.08205 | -0.14758 | 0.11233 | 0.16972 | 122.356 | 122.5042 | 122.6423 | 122.5211 | 122.6046 | 122.5458 | 122.6528 | 122.6335 | 122.5401 | -0.10318 | 0.097532 | -0.08205 | -0.14758 | 0.11233 | 0.16972 | 122.356 | 122.5042 | -0.21551 | -122.4592 | -0.19438 | -122.438
986.5781 | 122.9462 | -122.6578 | 0.15564 | -0.010922 | -0.13668 | -0.053207 | -0.10285 | 0.004219 | -0.01972 | -0.11765 | -0.10318 | 0.10211 | -0.077472 | -0.143 | 0.10775 | 0.16972 | 122.3606 | 122.5087 | 122.6469 | 122.5211 | 122.6046 | 122.5549 | 122.662 | 122.6381 | 122.5401 | -0.10318 | 0.10211 | -0.077472 | -0.143 | 0.10775 | 0.16972 | 122.3606 | 122.5087 | -0.21093 | -122.4637 | -0.18522 | -122.438
988.2969 | 122.8226 | -122.6898 | 0.18768 | -0.006344 | -0.14583 | -0.053207 | -0.10743 | -0.000359 | -0.028877 | -0.11308 | -0.066553 | 0.11127 | -0.077472 | -0.14758 | 0.12607 | 0.16972 | 122.3651 | 122.5087 | 122.6835 | 122.544 | 122.6366 | 122.5824 | 122.6895 | 122.6609 | 122.5767 | -0.066553 | 0.11127 | -0.077472 | -0.14758 | 0.12607 | 0.16972 | 122.3651 | 122.5087 | -0.19262 | -122.4317 | -0.20354 | -122.4426
990.0156 | 122.8592 | -122.6624 | 0.17853 | -0.010922 | -0.14125 | -0.057786 | -0.10285 | 0.004219 | -0.024298 | -0.11308 | -0.057396 | 0.10669 | -0.072894 | -0.143 | 0.11691 | 0.16972 | 122.3651 | 122.5087 | 122.6514 | 122.5211 | 122.6046 | 122.5595 | 122.6666 | 122.6381 | 122.5493 | -0.057396 | 0.10669 | -0.072894 | -0.143 | 0.11691 | 0.16972 | 122.3651 | 122.5087 | -0.1743 | -122.4225 | -0.1898 | -122.438
991.7812 | 122.9645 | -122.6486 | 0.16022 | -0.015501 | -0.14125 | -0.053207 | -0.10743 | -0.004937 | -0.028877 | -0.11765 | -0.098602 | 0.079217 | -0.086628 | -0.14758 | 0.12149 | 0.1743 | 122.3651 | 122.5042 | 122.6331 | 122.5074 | 122.5954 | 122.5412 | 122.6437 | 122.6197 | 122.531 | -0.098602 | 0.079217 | -0.086628 | -0.14758 | 0.12149 | 0.1743 | 122.3651 | 122.5042 | -0.22009 | -122.4637 | -0.20811 | -122.4518
993.4688 | 122.8638 | -122.6761 | 0.18768 | -0.010922 | -0.14125 | -0.053207 | -0.11201 | 0.004219 | -0.024298 | -0.11765 | -0.089445 | 0.10211 | -0.077472 | -0.14758 | 0.11691 | 0.1743 | 122.3606 | 122.5042 | 122.6652 | 122.5348 | 122.6229 | 122.5641 | 122.6803 | 122.6518 | 122.5584 | -0.089445 | 0.10211 | -0.077472 | -0.14758 | 0.11691 | 0.1743 | 122.3606 | 122.5042 | -0.20635 | -122.45 | -0.19438 | -122.438
995.2188 | 122.9324 | -122.6715 | 0.16937 | -0.020079 | -0.14125 | -0.057786 | -0.11201 | 0.004219 | -0.033455 | -0.12223 | -0.098602 | 0.10211 | -0.077472 | -0.13842 | 0.11691 | 0.1743 | 122.356 | 122.5087 | 122.6514 | 122.5303 | 122.6137 | 122.5595 | 122.6757 | 122.6381 | 122.5493 | -0.098602 | 0.10211 | -0.077472 | -0.13842 | 0.11691 | 0.1743 | 122.356 | 122.5087 | -0.21551 | -122.4546 | -0.19438 | -122.4335
996.9688 | 122.9782 | -122.6395 | 0.17395 | -0.020079 | -0.14583 | -0.048628 | -0.11659 | 0.004219 | -0.033455 | -0.11765 | -0.071132 | 0.11127 | -0.08205 | -0.15674 | 0.11233 | 0.16972 | 122.3606 | 122.5042 | 122.6194 | 122.4936 | 122.5908 | 122.5229 | 122.6437 | 122.606 | 122.5218 | -0.071132 | 0.11127 | -0.08205 | -0.15674 | 0.11233 | 0.16972 | 122.3606 | 122.5042 | -0.18346 | -122.4317 | -0.19438 | -122.4426
998.6562 | 122.9324 | -122.6349 | 0.15106 | -0.020079 | -0.14125 | -0.057786 | -0.11201 | -0.009515 | -0.028877 | -0.12223 | -0.10318 | 0.10669 | -0.08205 | -0.14758 | 0.11233 | 0.16972 | 122.3606 | 122.4996 | 122.6148 | 122.4936 | 122.5771 | 122.5229 | 122.6254 | 122.606 | 122.5127 | -0.10318 | 0.10669 | -0.08205 | -0.14758 | 0.11233 | 0.16972 | 122.3606 | 122.4996 | -0.21551 | -122.4637 | -0.19438 | -122.4426
1000.4062 | 122.8088 | -122.6807 | 0.20142 | -0.020079 | -0.14125 | -0.048628 | -0.11659 | -0.004937 | -0.01972 | -0.11765 | -0.061975 | 0.10211 | -0.08205 | -0.14758 | 0.12149 | 0.17887 | 122.3514 | 122.5042 | 122.6606 | 122.5394 | 122.632 | 122.5641 | 122.6757 | 122.6609 | 122.563 | -0.061975 | 0.10211 | -0.08205 | -0.14758 | 0.12149 | 0.17887 | 122.3514 | 122.5042 | -0.18346 | -122.4134 | -0.20354 | -122.4335
1002.1562 | 122.9462 | -122.6257 | 0.15564 | -0.010922 | -0.14583 | -0.053207 | -0.11659 | -0.004937 | -0.028877 | -0.11765 | -0.025347 | 0.097532 | -0.077472 | -0.15216 | 0.11233 | 0.1743 | 122.3514 | 122.4996 | 122.6148 | 122.4799 | 122.5725 | 122.5091 | 122.6208 | 122.5969 | 122.5081 | -0.025347 | 0.097532 | -0.077472 | -0.15216 | 0.11233 | 0.1743 | 122.3514 | 122.4996 | -0.13768 | -122.3767 | -0.1898 | -122.4289
1003.8438 | 122.8867 | -122.6578 | 0.16937 | -0.024657 | -0.13668 | -0.062364 | -0.11201 | -0.000359 | -0.024298 | -0.11765 | -0.057396 | 0.10669 | -0.08205 | -0.15216 | 0.10775 | 0.16972 | 122.356 | 122.5042 | 122.6331 | 122.5211 | 122.5954 | 122.5458 | 122.6574 | 122.6335 | 122.5401 | -0.057396 | 0.10669 | -0.08205 | -0.15216 | 0.10775 | 0.16972 | 122.356 | 122.5042 | -0.16515 | -122.4134 | -0.1898 | -122.438
1005.5781 | 122.9141 | -122.644 | 0.15564 | -0.020079 | -0.14583 | -0.053207 | -0.11659 | -0.000359 | -0.028877 | -0.12223 | -0.071132 | 0.092954 | -0.077472 | -0.143 | 0.11233 | 0.15598 | 122.3514 | 122.5042 | 122.624 | 122.4982 | 122.5908 | 122.5275 | 122.6437 | 122.6152 | 122.5218 | -0.071132 | 0.092954 | -0.077472 | -0.143 | 0.11233 | 0.15598 | 122.3514 | 122.5042 | -0.18346 | -122.4225 | -0.1898 | -122.4289
1007.2656 | 122.9507 | -122.6303 | 0.16022 | -0.015501 | -0.15041 | -0.057786 | -0.11201 | -0.000359 | -0.024298 | -0.12223 | -0.094024 | 0.11127 | -0.077472 | -0.14758 | 0.11691 | 0.17887 | 122.356 | 122.5087 | 122.6148 | 122.4799 | 122.5725 | 122.5183 | 122.63 | 122.606 | 122.5081 | -0.094024 | 0.11127 | -0.077472 | -0.14758 | 0.11691 | 0.17887 | 122.356 | 122.5087 | -0.21093 | -122.45 | -0.19438 | -122.4335
1009.0156 | 122.9416 | -122.6257 | 0.16022 | -0.020079 | -0.14583 | -0.057786 | -0.12574 | -0.009515 | -0.024298 | -0.12223 | -0.080288 | 0.11585 | -0.072894 | -0.15674 | 0.11233 | 0.16972 | 122.356 | 122.5042 | 122.6057 | 122.4799 | 122.5679 | 122.5 | 122.6162 | 122.6014 | 122.5035 | -0.080288 | 0.11585 | -0.072894 | -0.15674 | 0.11233 | 0.16972 | 122.356 | 122.5042 | -0.19262 | -122.4363 | -0.18522 | -122.4289
1010.6875 | 122.8363 | -122.6761 | 0.19684 | -0.015501 | -0.14583 | -0.057786 | -0.11659 | 0.004219 | -0.024298 | -0.12223 | -0.080288 | 0.10669 | -0.08205 | -0.13842 | 0.12149 | 0.1743 | 122.3606 | 122.4996 | 122.6606 | 122.5303 | 122.6183 | 122.5595 | 122.6803 | 122.6518 | 122.5539 | -0.080288 | 0.10669 | -0.08205 | -0.13842 | 0.12149 | 0.1743 | 122.3606 | 122.4996 | -0.20177 | -122.4408 | -0.20354 | -122.4426
1012.4375 | 122.8363 | -122.6486 | 0.19684 | -0.020079 | -0.14583 | -0.057786 | -0.12116 | -0.004937 | -0.028877 | -0.12223 | -0.039082 | 0.11127 | -0.072894 | -0.15216 | 0.12149 | 0.16972 | 122.356 | 122.5042 | 122.6285 | 122.5028 | 122.5908 | 122.5275 | 122.6437 | 122.6197 | 122.5264 | -0.039082 | 0.11127 | -0.072894 | -0.15216 | 0.12149 | 0.16972 | 122.356 | 122.5042 | -0.16057 | -122.3951 | -0.19438 | -122.4289
1014.2031 | 122.8271 | -122.6715 | 0.19684 | -0.020079 | -0.14583 | -0.053207 | -0.11659 | -0.004937 | -0.042612 | -0.12681 | -0.061975 | 0.11127 | -0.072894 | -0.14758 | 0.13064 | 0.16972 | 122.3514 | 122.5087 | 122.6514 | 122.5257 | 122.6183 | 122.5549 | 122.6666 | 122.6289 | 122.5447 | -0.061975 | 0.11127 | -0.072894 | -0.14758 | 0.13064 | 0.16972 | 122.3514 | 122.5087 | -0.19262 | -122.4134 | -0.20354 | -122.4243
1015.9531 | 122.9095 | -122.6532 | 0.17853 | -0.020079 | -0.14583 | -0.057786 | -0.11659 | -0.009515 | -0.033455 | -0.12681 | -0.07571 | 0.10211 | -0.072894 | -0.14758 | 0.10775 | 0.17887 | 122.3514 | 122.495 | 122.6331 | 122.5074 | 122.5954 | 122.5366 | 122.6437 | 122.6197 | 122.5264 | -0.07571 | 0.10211 | -0.072894 | -0.14758 | 0.10775 | 0.17887 | 122.3514 | 122.495 | -0.18346 | -122.4271 | -0.18065 | -122.4243
1017.625 | 122.85 | -122.6624 | 0.17395 | -0.020079 | -0.14583 | -0.062364 | -0.11659 | -0.000359 | -0.028877 | -0.12223 | -0.10318 | 0.10669 | -0.077472 | -0.15674 | 0.11691 | 0.17887 | 122.356 | 122.4996 | 122.6423 | 122.5165 | 122.6 | 122.5458 | 122.662 | 122.6335 | 122.5401 | -0.10318 | 0.10669 | -0.077472 | -0.15674 | 0.11691 | 0.17887 | 122.356 | 122.4996 | -0.22009 | -122.4592 | -0.19438 | -122.4335
1019.3906 | 122.9095 | -122.612 | 0.16937 | -0.024657 | -0.14583 | -0.057786 | -0.11659 | -0.000359 | -0.033455 | -0.12223 | -0.098602 | 0.10669 | -0.072894 | -0.15216 | 0.11233 | 0.1743 | 122.3514 | 122.495 | 122.5873 | 122.4662 | 122.5542 | 122.4954 | 122.6116 | 122.5785 | 122.4898 | -0.098602 | 0.10669 | -0.072894 | -0.15216 | 0.11233 | 0.1743 | 122.3514 | 122.495 | -0.21093 | -122.45 | -0.18522 | -122.4243
1021.0781 | 122.8683 | -122.6715 | 0.19684 | -0.020079 | -0.15041 | -0.066943 | -0.11659 | -0.004937 | -0.033455 | -0.13139 | -0.039082 | 0.11585 | -0.072894 | -0.143 | 0.12149 | 0.1743 | 122.356 | 122.4996 | 122.6514 | 122.5211 | 122.6046 | 122.5549 | 122.6666 | 122.6381 | 122.5401 | -0.039082 | 0.11585 | -0.072894 | -0.143 | 0.12149 | 0.1743 | 122.356 | 122.4996 | -0.16057 | -122.3951 | -0.19438 | -122.4289
1022.8125 | 122.8867 | -122.644 | 0.17395 | -0.015501 | -0.14583 | -0.062364 | -0.12116 | -0.009515 | -0.033455 | -0.13139 | -0.084867 | 0.10211 | -0.086628 | -0.14758 | 0.11691 | 0.17887 | 122.3514 | 122.495 | 122.6285 | 122.4982 | 122.5817 | 122.5229 | 122.6345 | 122.6106 | 122.5127 | -0.084867 | 0.10211 | -0.086628 | -0.14758 | 0.11691 | 0.17887 | 122.3514 | 122.495 | -0.20177 | -122.4363 | -0.20354 | -122.438
1024.5625 | 122.8043 | -122.6761 | 0.1831 | -0.020079 | -0.15499 | -0.053207 | -0.11201 | -0.000359 | -0.033455 | -0.12223 | -0.071132 | 0.088375 | -0.072894 | -0.14758 | 0.11691 | 0.17887 | 122.3377 | 122.4904 | 122.656 | 122.5211 | 122.6229 | 122.5641 | 122.6757 | 122.6426 | 122.5539 | -0.071132 | 0.088375 | -0.072894 | -0.14758 | 0.11691 | 0.17887 | 122.3377 | 122.4904 | -0.18804 | -122.4088 | -0.1898 | -122.4106
1026.3125 | 122.9462 | -122.6028 | 0.17395 | -0.024657 | -0.15041 | -0.062364 | -0.11201 | -0.000359 | -0.024298 | -0.11765 | -0.094024 | 0.11127 | -0.077472 | -0.14758 | 0.12149 | 0.18345 | 122.3422 | 122.495 | 122.5782 | 122.4524 | 122.5405 | 122.4908 | 122.6025 | 122.5785 | 122.4852 | -0.094024 | 0.11127 | -0.077472 | -0.14758 | 0.12149 | 0.18345 | 122.3422 | 122.495 | -0.21551 | -122.4363 | -0.19896 | -122.4197
1028.0625 | 122.8088 | -122.6624 | 0.20142 | -0.020079 | -0.15499 | -0.053207 | -0.10743 | -0.000359 | -0.028877 | -0.12223 | -0.071132 | 0.11127 | -0.08205 | -0.14758 | 0.11691 | 0.18803 | 122.3606 | 122.495 | 122.6423 | 122.5074 | 122.6091 | 122.5549 | 122.662 | 122.6335 | 122.5401 | -0.071132 | 0.11127 | -0.08205 | -0.14758 | 0.11691 | 0.18803 | 122.3606 | 122.495 | -0.18804 | -122.4317 | -0.19896 | -122.4426
1029.75 | 122.9233 | -122.612 | 0.16937 | -0.020079 | -0.15041 | -0.062364 | -0.11201 | -0.009515 | -0.038034 | -0.11765 | -0.043661 | 0.10669 | -0.077472 | -0.14758 | 0.12607 | 0.18345 | 122.3514 | 122.4996 | 122.5919 | 122.4616 | 122.5496 | 122.5 | 122.6025 | 122.574 | 122.4943 | -0.043661 | 0.10669 | -0.077472 | -0.14758 | 0.12607 | 0.18345 | 122.3514 | 122.4996 | -0.16973 | -122.3951 | -0.20354 | -122.4289
1031.5 | 122.9553 | -122.612 | 0.16479 | -0.015501 | -0.15499 | -0.066943 | -0.11659 | -0.000359 | -0.038034 | -0.12681 | -0.071132 | 0.10211 | -0.077472 | -0.15216 | 0.12149 | 0.17887 | 122.3468 | 122.4904 | 122.5965 | 122.457 | 122.5451 | 122.4954 | 122.6116 | 122.574 | 122.4852 | -0.071132 | 0.10211 | -0.077472 | -0.15216 | 0.12149 | 0.17887 | 122.3468 | 122.4904 | -0.19262 | -122.418 | -0.19896 | -122.4243
1033.1875 | 122.8455 | -122.6578 | 0.16022 | -0.020079 | -0.14583 | -0.048628 | -0.11201 | -0.004937 | -0.024298 | -0.11765 | -0.094024 | 0.11127 | -0.068315 | -0.15216 | 0.11691 | 0.18345 | 122.3468 | 122.4904 | 122.6377 | 122.5119 | 122.6091 | 122.5458 | 122.6528 | 122.6335 | 122.5401 | -0.094024 | 0.11127 | -0.068315 | -0.15216 | 0.11691 | 0.18345 | 122.3468 | 122.4904 | -0.21093 | -122.4408 | -0.18522 | -122.4151
1034.9375 | 122.9141 | -122.6303 | 0.14191 | -0.024657 | -0.15499 | -0.066943 | -0.10743 | -0.004937 | -0.033455 | -0.12681 | -0.066553 | 0.10211 | -0.072894 | -0.15216 | 0.12149 | 0.17887 | 122.356 | 122.495 | 122.6057 | 122.4753 | 122.5634 | 122.5229 | 122.6254 | 122.5969 | 122.5035 | -0.066553 | 0.10211 | -0.072894 | -0.15216 | 0.12149 | 0.17887 | 122.356 | 122.495 | -0.18804 | -122.4225 | -0.19438 | -122.4289
1036.6875 | 122.7997 | -122.6624 | 0.19226 | -0.024657 | -0.15041 | -0.053207 | -0.11201 | -0.009515 | -0.038034 | -0.13139 | -0.057396 | 0.10211 | -0.072894 | -0.143 | 0.12149 | 0.1743 | 122.3377 | 122.4904 | 122.6377 | 122.5119 | 122.6091 | 122.5503 | 122.6528 | 122.6243 | 122.531 | -0.057396 | 0.10211 | -0.072894 | -0.143 | 0.12149 | 0.1743 | 122.3377 | 122.4904 | -0.17888 | -122.3951 | -0.19438 | -122.4106
1038.4375 | 122.8455 | -122.6486 | 0.16022 | -0.020079 | -0.15499 | -0.066943 | -0.10743 | -0.009515 | -0.038034 | -0.13139 | -0.089445 | 0.10669 | -0.077472 | -0.15674 | 0.052814 | 0.096469 | 122.3514 | 122.4904 | 122.6285 | 122.4936 | 122.5817 | 122.5412 | 122.6391 | 122.6106 | 122.5172 | -0.089445 | 0.10669 | -0.077472 | -0.15674 | 0.052814 | 0.096469 | 122.3514 | 122.4904 | -0.14226 | -122.4408 | -0.13029 | -122.4289
1040.1875 | 122.937 | -122.6074 | 0.17395 | -0.024657 | -0.15957 | -0.066943 | -0.11659 | -0.014093 | -0.04719 | -0.12681 | -0.043661 | 0.10669 | -0.050002 | -0.14758 | 0.043657 | 0.087313 | 122.3422 | 122.4904 | 122.5828 | 122.4479 | 122.5405 | 122.4908 | 122.5933 | 122.5602 | 122.4806 | -0.043661 | 0.10669 | -0.050002 | -0.14758 | 0.043657 | 0.087313 | 122.3422 | 122.4904 | -0.087318 | -122.3859 | -0.093659 | -122.3922
1041.9219 | 122.8409 | -122.644 | 0.18768 | -0.029236 | -0.15957 | -0.062364 | -0.12574 | -0.018671 | -0.033455 | -0.12681 | -0.025347 | 0.11127 | -0.059159 | -0.14758 | 0.048236 | 0.082735 | 122.3514 | 122.4859 | 122.6148 | 122.4845 | 122.5817 | 122.5183 | 122.6254 | 122.6106 | 122.5172 | -0.025347 | 0.11127 | -0.059159 | -0.14758 | 0.048236 | 0.082735 | 122.3514 | 122.4859 | -0.073583 | -122.3767 | -0.1074 | -122.4106
1043.6562 | 122.9279 | -122.6395 | 0.15564 | -0.029236 | -0.15957 | -0.066943 | -0.12574 | -0.009515 | -0.038034 | -0.13597 | -0.039082 | 0.097532 | -0.045424 | -0.15674 | 0.048236 | 0.087313 | 122.3377 | 122.4813 | 122.6102 | 122.4799 | 122.5725 | 122.5137 | 122.63 | 122.6014 | 122.5035 | -0.039082 | 0.097532 | -0.045424 | -0.15674 | 0.048236 | 0.087313 | 122.3377 | 122.4813 | -0.087318 | -122.3767 | -0.09366 | -122.3831
1045.3438 | 122.8683 | -122.6212 | 0.17853 | -0.029236 | -0.15957 | -0.062364 | -0.11659 | -0.014093 | -0.04719 | -0.12681 | -0.061975 | 0.10669 | -0.045424 | -0.14758 | 0.039079 | 0.087313 | 122.3468 | 122.4859 | 122.5919 | 122.4616 | 122.5588 | 122.5046 | 122.6071 | 122.574 | 122.4943 | -0.061975 | 0.10669 | -0.045424 | -0.14758 | 0.039079 | 0.087313 | 122.3468 | 122.4859 | -0.10105 | -122.4088 | -0.084503 | -122.3922
1047.0938 | 122.818 | -122.6715 | 0.1831 | -0.024657 | -0.15499 | -0.062364 | -0.11659 | -0.018671 | -0.042612 | -0.13597 | -0.025347 | 0.10669 | -0.072894 | -0.15216 | 0.043657 | 0.091891 | 122.3468 | 122.4904 | 122.6469 | 122.5165 | 122.6091 | 122.5549 | 122.6528 | 122.6289 | 122.5355 | -0.025347 | 0.10669 | -0.072894 | -0.15216 | 0.043657 | 0.091891 | 122.3468 | 122.4904 | -0.069004 | -122.3722 | -0.11655 | -122.4197
1048.7656 | 122.8088 | -122.6532 | 0.19684 | -0.024657 | -0.15499 | -0.062364 | -0.12574 | -0.018671 | -0.042612 | -0.13597 | -0.039082 | 0.11585 | -0.05458 | -0.143 | 0.043657 | 0.087313 | 122.3468 | 122.495 | 122.6285 | 122.4982 | 122.5908 | 122.5275 | 122.6345 | 122.6106 | 122.5172 | -0.039082 | 0.11585 | -0.05458 | -0.143 | 0.043657 | 0.087313 | 122.3468 | 122.495 | -0.082739 | -122.3859 | -0.098237 | -122.4014
1050.5156 | 122.8729 | -122.6395 | 0.17395 | -0.038393 | -0.15957 | -0.066943 | -0.13032 | -0.023249 | -0.04719 | -0.13597 | -0.057396 | 0.11127 | -0.059159 | -0.15216 | 0.039079 | 0.087313 | 122.3377 | 122.4767 | 122.6011 | 122.4799 | 122.5725 | 122.5091 | 122.6162 | 122.5923 | 122.5035 | -0.057396 | 0.11127 | -0.059159 | -0.15216 | 0.039079 | 0.087313 | 122.3377 | 122.4767 | -0.096475 | -122.3951 | -0.098238 | -122.3968
1052.2656 | 122.8043 | -122.6669 | 0.19226 | -0.024657 | -0.15957 | -0.066943 | -0.12116 | -0.009515 | -0.033455 | -0.13139 | -0.052818 | 0.10669 | -0.072894 | -0.143 | 0.048236 | 0.087313 | 122.3422 | 122.4813 | 122.6423 | 122.5074 | 122.6 | 122.5458 | 122.6574 | 122.6335 | 122.5355 | -0.052818 | 0.10669 | -0.072894 | -0.143 | 0.048236 | 0.087313 | 122.3422 | 122.4813 | -0.10105 | -122.3951 | -0.12113 | -122.4151
1054.0156 | 122.8958 | -122.6028 | 0.16479 | -0.029236 | -0.15499 | -0.066943 | -0.11659 | -0.014093 | -0.042612 | -0.12681 | -0.029925 | 0.10669 | -0.059159 | -0.15674 | 0.039079 | 0.082735 | 122.3377 | 122.4767 | 122.5736 | 122.4479 | 122.5359 | 122.4863 | 122.5888 | 122.5602 | 122.476 | -0.029925 | 0.10669 | -0.059159 | -0.15674 | 0.039079 | 0.082735 | 122.3377 | 122.4767 | -0.069004 | -122.3676 | -0.098238 | -122.3968
1055.7188 | 122.8821 | -122.6212 | 0.16479 | -0.029236 | -0.15957 | -0.071521 | -0.12116 | -0.018671 | -0.038034 | -0.13597 | -0.039082 | 0.10211 | -0.063737 | -0.15216 | 0.039079 | 0.087313 | 122.3331 | 122.4859 | 122.5919 | 122.4616 | 122.5496 | 122.5 | 122.6025 | 122.5831 | 122.4852 | -0.039082 | 0.10211 | -0.063737 | -0.15216 | 0.039079 | 0.087313 | 122.3331 | 122.4859 | -0.078161 | -122.3722 | -0.10282 | -122.3968
1057.4531 | 122.8546 | -122.6395 | 0.15564 | -0.029236 | -0.15957 | -0.0761 | -0.11659 | -0.014093 | -0.04719 | -0.14055 | 0.002124 | 0.10669 | -0.068315 | -0.14758 | 0.039079 | 0.082735 | 122.3377 | 122.4813 | 122.6102 | 122.4799 | 122.5634 | 122.5229 | 122.6254 | 122.5923 | 122.4989 | 0.002124 | 0.10669 | -0.068315 | -0.14758 | 0.039079 | 0.082735 | 122.3377 | 122.4813 | -0.036955 | -122.3355 | -0.10739 | -122.406
1059.2031 | 122.8455 | -122.612 | 0.17395 | -0.033814 | -0.16415 | -0.066943 | -0.11201 | -0.018671 | -0.038034 | -0.13139 | -0.011611 | 0.097532 | -0.072894 | -0.143 | 0.029923 | 0.082735 | 122.3285 | 122.4813 | 122.5782 | 122.4479 | 122.5451 | 122.5 | 122.5933 | 122.574 | 122.4806 | -0.011611 | 0.097532 | -0.072894 | -0.143 | 0.029923 | 0.082735 | 122.3285 | 122.4813 | -0.041534 | -122.3401 | -0.10282 | -122.4014
1060.9531 | 122.7951 | -122.6624 | 0.19684 | -0.038393 | -0.16415 | -0.0761 | -0.11659 | -0.018671 | -0.042612 | -0.13597 | -0.057396 | 0.11585 | -0.077472 | -0.15216 | 0.039079 | 0.082735 | 122.3468 | 122.4904 | 122.624 | 122.4982 | 122.5863 | 122.5458 | 122.6437 | 122.6197 | 122.5264 | -0.057396 | 0.11585 | -0.077472 | -0.15216 | 0.039079 | 0.082735 | 122.3468 | 122.4904 | -0.096475 | -122.4042 | -0.11655 | -122.4243
1062.7031 | 122.818 | -122.6807 | 0.19226 | -0.038393 | -0.16873 | -0.066943 | -0.11659 | -0.014093 | -0.04719 | -0.14055 | -0.034504 | 0.11127 | -0.059159 | -0.14758 | 0.043657 | 0.087313 | 122.3377 | 122.4767 | 122.6423 | 122.5119 | 122.6137 | 122.5641 | 122.6666 | 122.6335 | 122.5401 | -0.034504 | 0.11127 | -0.059159 | -0.14758 | 0.043657 | 0.087313 | 122.3377 | 122.4767 | -0.078161 | -122.3722 | -0.10282 | -122.3968
1064.3906 | 122.7905 | -122.6715 | 0.20142 | -0.024657 | -0.15957 | -0.066943 | -0.12574 | -0.014093 | -0.033455 | -0.13139 | -0.034504 | 0.11127 | -0.077472 | -0.15216 | 0.039079 | 0.096469 | 122.3422 | 122.4859 | 122.6469 | 122.5119 | 122.6046 | 122.5458 | 122.6574 | 122.6381 | 122.5401 | -0.034504 | 0.11127 | -0.077472 | -0.15216 | 0.039079 | 0.096469 | 122.3422 | 122.4859 | -0.073583 | -122.3767 | -0.11655 | -122.4197
1066.1406 | 122.9187 | -122.6074 | 0.16937 | -0.042971 | -0.15957 | -0.080679 | -0.12574 | -0.023249 | -0.04719 | -0.13139 | -0.043661 | 0.10211 | -0.059159 | -0.14758 | 0.043657 | 0.082735 | 122.3331 | 122.4767 | 122.5645 | 122.4479 | 122.5267 | 122.4817 | 122.5842 | 122.5602 | 122.476 | -0.043661 | 0.10211 | -0.059159 | -0.14758 | 0.043657 | 0.082735 | 122.3331 | 122.4767 | -0.087318 | -122.3767 | -0.10282 | -122.3922
1067.8906 | 122.9141 | -122.5983 | 0.15564 | -0.024657 | -0.16873 | -0.071521 | -0.12116 | -0.014093 | -0.04719 | -0.14055 | -0.039082 | 0.10211 | -0.068315 | -0.15216 | 0.043657 | 0.096469 | 122.3377 | 122.4767 | 122.5736 | 122.4295 | 122.5267 | 122.4771 | 122.5842 | 122.5511 | 122.4577 | -0.039082 | 0.10211 | -0.068315 | -0.15216 | 0.043657 | 0.096469 | 122.3377 | 122.4767 | -0.082739 | -122.3767 | -0.11197 | -122.406
1069.5781 | 122.9141 | -122.612 | 0.17395 | -0.029236 | -0.16415 | -0.071521 | -0.12574 | -0.023249 | -0.051769 | -0.14055 | 0.020438 | 0.11127 | -0.017954 | -0.14758 | 0.039079 | 0.082735 | 122.3422 | 122.4813 | 122.5828 | 122.4479 | 122.5405 | 122.4863 | 122.5888 | 122.5602 | 122.4715 | 0.020438 | 0.11127 | -0.017954 | -0.14758 | 0.039079 | 0.082735 | 122.3422 | 122.4813 | -0.018641 | -122.3218 | -0.057033 | -122.3602
1071.3438 | 122.818 | -122.6532 | 0.19684 | -0.033814 | -0.16873 | -0.0761 | -0.11659 | -0.014093 | -0.038034 | -0.13597 | -0.057396 | 0.10211 | -0.077472 | -0.14758 | 0.039079 | 0.082735 | 122.3377 | 122.4813 | 122.6194 | 122.4845 | 122.5771 | 122.5366 | 122.6391 | 122.6152 | 122.5172 | -0.057396 | 0.10211 | -0.077472 | -0.14758 | 0.039079 | 0.082735 | 122.3377 | 122.4813 | -0.096475 | -122.3951 | -0.11655 | -122.4151
1073.0781 | 122.818 | -122.644 | 0.19684 | -0.024657 | -0.15957 | -0.071521 | -0.12574 | -0.018671 | -0.038034 | -0.14055 | -0.052818 | 0.10669 | -0.072894 | -0.14758 | 0.039079 | 0.087313 | 122.3331 | 122.4767 | 122.6194 | 122.4845 | 122.5725 | 122.5183 | 122.6254 | 122.606 | 122.5035 | -0.052818 | 0.10669 | -0.072894 | -0.14758 | 0.039079 | 0.087313 | 122.3331 | 122.4767 | -0.091897 | -122.3859 | -0.11197 | -122.406
1074.8281 | 122.8363 | -122.6532 | 0.17395 | -0.038393 | -0.16415 | -0.066943 | -0.11659 | -0.014093 | -0.04719 | -0.13139 | -0.007033 | 0.11127 | -0.050002 | -0.14758 | 0.043657 | 0.078157 | 122.3331 | 122.4767 | 122.6148 | 122.489 | 122.5863 | 122.5366 | 122.6391 | 122.606 | 122.5218 | -0.007033 | 0.11127 | -0.050002 | -0.14758 | 0.043657 | 0.078157 | 122.3331 | 122.4767 | -0.05069 | -122.3401 | -0.093659 | -122.3831
1076.5156 | 122.9233 | -122.5983 | 0.16479 | -0.029236 | -0.16873 | -0.071521 | -0.12116 | -0.027827 | -0.04719 | -0.14055 | -0.061975 | 0.10211 | -0.059159 | -0.13842 | 0.039079 | 0.082735 | 122.3377 | 122.4767 | 122.569 | 122.4295 | 122.5267 | 122.4771 | 122.5704 | 122.5511 | 122.4577 | -0.061975 | 0.10211 | -0.059159 | -0.13842 | 0.039079 | 0.082735 | 122.3377 | 122.4767 | -0.10105 | -122.3996 | -0.098238 | -122.3968
1078.2656 | 122.7859 | -122.6349 | 0.18768 | -0.033814 | -0.16415 | -0.080679 | -0.11659 | -0.018671 | -0.042612 | -0.13597 | -0.07571 | 0.11585 | -0.068315 | -0.14758 | 0.039079 | 0.082735 | 122.3331 | 122.4767 | 122.6011 | 122.4707 | 122.5542 | 122.5183 | 122.6162 | 122.5923 | 122.4989 | -0.07571 | 0.11585 | -0.068315 | -0.14758 | 0.039079 | 0.082735 | 122.3331 | 122.4767 | -0.11479 | -122.4088 | -0.10739 | -122.4014
1080.0156 | 122.9233 | -122.6028 | 0.16022 | -0.042971 | -0.15957 | -0.071521 | -0.12574 | -0.018671 | -0.038034 | -0.13597 | -0.029925 | 0.10669 | -0.063737 | -0.14758 | 0.034501 | 0.087313 | 122.3377 | 122.4675 | 122.5599 | 122.4433 | 122.5313 | 122.4771 | 122.5842 | 122.5648 | 122.4669 | -0.029925 | 0.10669 | -0.063737 | -0.14758 | 0.034501 | 0.087313 | 122.3377 | 122.4675 | -0.064426 | -122.3676 | -0.098238 | -122.4014
1081.7656 | 122.9095 | -122.5983 | 0.15106 | -0.033814 | -0.16873 | -0.0761 | -0.11659 | -0.014093 | -0.04719 | -0.13597 | -0.011611 | 0.11585 | -0.031689 | -0.14758 | 0.039079 | 0.082735 | 122.3285 | 122.4721 | 122.5645 | 122.4295 | 122.5222 | 122.4817 | 122.5842 | 122.5511 | 122.4623 | -0.011611 | 0.11585 | -0.031689 | -0.14758 | 0.039079 | 0.082735 | 122.3285 | 122.4721 | -0.05069 | -122.3401 | -0.070768 | -122.3602
1083.4375 | 122.9279 | -122.612 | 0.16022 | -0.033814 | -0.16415 | -0.0761 | -0.11659 | -0.018671 | -0.042612 | -0.13139 | -0.01619 | 0.11585 | -0.05458 | -0.15674 | 0.052814 | 0.096469 | 122.3239 | 122.4721 | 122.5782 | 122.4479 | 122.5359 | 122.4954 | 122.5933 | 122.5694 | 122.4806 | -0.01619 | 0.11585 | -0.05458 | -0.15674 | 0.052814 | 0.096469 | 122.3239 | 122.4721 | -0.069004 | -122.3401 | -0.10739 | -122.3785
1085.1875 | 122.8317 | -122.6532 | 0.19684 | -0.029236 | -0.15957 | -0.066943 | -0.12116 | -0.004937 | -0.04719 | -0.13139 | -0.057396 | 0.10669 | -0.068315 | -0.14758 | 0.039079 | 0.087313 | 122.3331 | 122.4721 | 122.624 | 122.4936 | 122.5863 | 122.532 | 122.6483 | 122.606 | 122.5218 | -0.057396 | 0.10669 | -0.068315 | -0.14758 | 0.039079 | 0.087313 | 122.3331 | 122.4721 | -0.096475 | -122.3905 | -0.10739 | -122.4014
1086.9219 | 122.7768 | -122.6578 | 0.19226 | -0.029236 | -0.16415 | -0.066943 | -0.12574 | -0.014093 | -0.042612 | -0.14055 | -0.025347 | 0.10669 | -0.072894 | -0.143 | 0.052814 | 0.087313 | 122.3239 | 122.4813 | 122.6285 | 122.4936 | 122.5908 | 122.532 | 122.6437 | 122.6152 | 122.5172 | -0.025347 | 0.10669 | -0.072894 | -0.143 | 0.052814 | 0.087313 | 122.3239 | 122.4813 | -0.078161 | -122.3493 | -0.12571 | -122.3968
1088.5938 | 122.7905 | -122.6624 | 0.16937 | -0.024657 | -0.16415 | -0.0761 | -0.12116 | -0.014093 | -0.042612 | -0.13597 | -0.01619 | 0.10211 | -0.072894 | -0.15216 | 0.043657 | 0.078157 | 122.3285 | 122.4721 | 122.6377 | 122.4982 | 122.5863 | 122.5412 | 122.6483 | 122.6197 | 122.5264 | -0.01619 | 0.10211 | -0.072894 | -0.15216 | 0.043657 | 0.078157 | 122.3285 | 122.4721 | -0.059847 | -122.3447 | -0.11655 | -122.4014
1090.3438 | 122.7905 | -122.6532 | 0.20599 | -0.029236 | -0.16415 | -0.066943 | -0.11659 | -0.023249 | -0.033455 | -0.12681 | -0.057396 | 0.10669 | -0.072894 | -0.143 | 0.039079 | 0.087313 | 122.3239 | 122.4675 | 122.624 | 122.489 | 122.5863 | 122.5366 | 122.6299 | 122.6197 | 122.5264 | -0.057396 | 0.10669 | -0.072894 | -0.143 | 0.039079 | 0.087313 | 122.3239 | 122.4675 | -0.096475 | -122.3813 | -0.11197 | -122.3968
1092.0938 | 122.9095 | -122.6166 | 0.16937 | -0.033814 | -0.15957 | -0.066943 | -0.11659 | -0.023249 | -0.038034 | -0.13597 | -0.066553 | 0.11127 | -0.068315 | -0.15216 | 0.034501 | 0.087313 | 122.3194 | 122.4721 | 122.5828 | 122.457 | 122.5496 | 122.5 | 122.5933 | 122.5785 | 122.4806 | -0.066553 | 0.11127 | -0.068315 | -0.15216 | 0.034501 | 0.087313 | 122.3194 | 122.4721 | -0.10105 | -122.3859 | -0.10282 | -122.3877
1093.7812 | 122.8363 | -122.644 | 0.1831 | -0.033814 | -0.16415 | -0.0761 | -0.12116 | -0.018671 | -0.042612 | -0.13597 | -0.066553 | 0.097532 | -0.063737 | -0.14758 | 0.057392 | 0.096469 | 122.3331 | 122.4767 | 122.6102 | 122.4799 | 122.5679 | 122.5229 | 122.6254 | 122.6014 | 122.5081 | -0.066553 | 0.097532 | -0.063737 | -0.14758 | 0.057392 | 0.096469 | 122.3331 | 122.4767 | -0.12394 | -122.3996 | -0.12113 | -122.3968
1095.5312 | 122.9187 | -122.6212 | 0.16022 | -0.038393 | -0.16415 | -0.071521 | -0.11201 | -0.018671 | -0.038034 | -0.13597 | -0.020768 | 0.11127 | -0.063737 | -0.14758 | 0.029923 | 0.087313 | 122.3239 | 122.463 | 122.5828 | 122.457 | 122.5496 | 122.5091 | 122.6025 | 122.5831 | 122.4852 | -0.020768 | 0.11127 | -0.063737 | -0.14758 | 0.029923 | 0.087313 | 122.3239 | 122.463 | -0.050691 | -122.3447 | -0.09366 | -122.3877
1097.2188 | 122.7951 | -122.6349 | 0.1831 | -0.024657 | -0.16415 | -0.066943 | -0.11659 | -0.014093 | -0.038034 | -0.12681 | -0.071132 | 0.11585 | -0.08205 | -0.14758 | 0.039079 | 0.082735 | 122.3377 | 122.4675 | 122.6102 | 122.4707 | 122.5679 | 122.5183 | 122.6208 | 122.5969 | 122.5081 | -0.071132 | 0.11585 | -0.08205 | -0.14758 | 0.039079 | 0.082735 | 122.3377 | 122.4675 | -0.11021 | -122.4088 | -0.12113 | -122.4197
1098.9531 | 122.9004 | -122.5891 | 0.16022 | -0.029236 | -0.16415 | -0.071521 | -0.11659 | -0.023249 | -0.038034 | -0.12681 | -0.080288 | 0.10211 | -0.077472 | -0.15216 | 0.034501 | 0.087313 | 122.3285 | 122.4675 | 122.5599 | 122.425 | 122.5176 | 122.4725 | 122.5659 | 122.5511 | 122.4623 | -0.080288 | 0.10211 | -0.077472 | -0.15216 | 0.034501 | 0.087313 | 122.3285 | 122.4675 | -0.11479 | -122.4088 | -0.11197 | -122.406
1100.7031 | 122.9095 | -122.612 | 0.17395 | -0.033814 | -0.15957 | -0.071521 | -0.11659 | -0.014093 | -0.042612 | -0.12681 | -0.052818 | 0.11585 | -0.072894 | -0.15216 | 0.039079 | 0.091891 | 122.3148 | 122.4675 | 122.5782 | 122.4524 | 122.5405 | 122.4954 | 122.5979 | 122.5694 | 122.4852 | -0.052818 | 0.11585 | -0.072894 | -0.15216 | 0.039079 | 0.091891 | 122.3148 | 122.4675 | -0.091897 | -122.3676 | -0.11197 | -122.3877
1102.375 | 122.818 | -122.6212 | 0.19226 | -0.024657 | -0.15957 | -0.066943 | -0.11659 | -0.009515 | -0.038034 | -0.13597 | -0.039082 | 0.10669 | -0.068315 | -0.143 | 0.048236 | 0.082735 | 122.3194 | 122.4721 | 122.5965 | 122.4616 | 122.5542 | 122.5046 | 122.6116 | 122.5831 | 122.4852 | -0.039082 | 0.10669 | -0.068315 | -0.143 | 0.048236 | 0.082735 | 122.3194 | 122.4721 | -0.087318 | -122.3584 | -0.11655 | -122.3877
1104.125 | 122.7859 | -122.6166 | 0.19684 | -0.029236 | -0.16415 | -0.071521 | -0.11659 | -0.014093 | -0.042612 | -0.12223 | -0.011611 | 0.10211 | -0.050002 | -0.15216 | 0.029923 | 0.082735 | 122.3148 | 122.4675 | 122.5873 | 122.4524 | 122.5451 | 122.5 | 122.6025 | 122.574 | 122.4943 | -0.011611 | 0.10211 | -0.050002 | -0.15216 | 0.029923 | 0.082735 | 122.3148 | 122.4675 | -0.041534 | -122.3264 | -0.079925 | -122.3648
1105.8906 | 122.8867 | -122.612 | 0.16937 | -0.033814 | -0.16873 | -0.071521 | -0.11659 | -0.018671 | -0.038034 | -0.13139 | -0.034504 | 0.083796 | -0.068315 | -0.14758 | 0.048236 | 0.10105 | 122.3194 | 122.4538 | 122.5782 | 122.4433 | 122.5405 | 122.4954 | 122.5933 | 122.574 | 122.4806 | -0.034504 | 0.083796 | -0.068315 | -0.14758 | 0.048236 | 0.10105 | 122.3194 | 122.4538 | -0.08274 | -122.3539 | -0.11655 | -122.3877
1107.6406 | 122.8592 | -122.5937 | 0.17853 | -0.033814 | -0.16873 | -0.066943 | -0.11201 | -0.018671 | -0.038034 | -0.14055 | -0.071132 | 0.10669 | -0.072894 | -0.14758 | 0.048236 | 0.096469 | 122.3194 | 122.4675 | 122.5599 | 122.425 | 122.5267 | 122.4817 | 122.575 | 122.5557 | 122.4531 | -0.071132 | 0.10669 | -0.072894 | -0.14758 | 0.048236 | 0.096469 | 122.3194 | 122.4675 | -0.11937 | -122.3905 | -0.12113 | -122.3922
1109.3125 | 122.7814 | -122.6578 | 0.18768 | -0.033814 | -0.15499 | -0.071521 | -0.11201 | -0.014093 | -0.033455 | -0.13139 | -0.07571 | 0.10669 | -0.063737 | -0.14758 | 0.057392 | 0.10562 | 122.3239 | 122.4675 | 122.624 | 122.5028 | 122.5863 | 122.5458 | 122.6437 | 122.6243 | 122.5264 | -0.07571 | 0.10669 | -0.063737 | -0.14758 | 0.057392 | 0.10562 | 122.3239 | 122.4675 | -0.1331 | -122.3996 | -0.12113 | -122.3877
1111.0625 | 122.8821 | -122.612 | 0.17395 | -0.029236 | -0.16415 | -0.071521 | -0.11659 | -0.009515 | -0.033455 | -0.14512 | -0.048239 | 0.11585 | -0.077472 | -0.14758 | 0.12149 | 0.18803 | 122.3102 | 122.463 | 122.5828 | 122.4479 | 122.5405 | 122.4954 | 122.6025 | 122.5785 | 122.4669 | -0.048239 | 0.11585 | -0.077472 | -0.14758 | 0.12149 | 0.18803 | 122.3102 | 122.463 | -0.16972 | -122.3584 | -0.19896 | -122.3877
1112.75 | 122.8363 | -122.6257 | 0.19684 | -0.029236 | -0.16415 | -0.071521 | -0.12116 | -0.018671 | -0.042612 | -0.13597 | -0.025347 | 0.11585 | -0.040846 | -0.14758 | 0.12149 | 0.18803 | 122.3239 | 122.4675 | 122.5965 | 122.4616 | 122.5542 | 122.5046 | 122.6071 | 122.5831 | 122.4898 | -0.025347 | 0.11585 | -0.040846 | -0.14758 | 0.12149 | 0.18803 | 122.3239 | 122.4675 | -0.14683 | -122.3493 | -0.16233 | -122.3648
1114.5312 | 122.8592 | -122.6166 | 0.16022 | -0.024657 | -0.15957 | -0.071521 | -0.11201 | -0.014093 | -0.033455 | -0.13597 | -0.020768 | 0.11585 | -0.050002 | -0.143 | 0.11691 | 0.17887 | 122.3194 | 122.4675 | 122.5919 | 122.457 | 122.5451 | 122.5046 | 122.6025 | 122.5831 | 122.4806 | -0.020768 | 0.11585 | -0.050002 | -0.143 | 0.11691 | 0.17887 | 122.3194 | 122.4675 | -0.13768 | -122.3401 | -0.16691 | -122.3694
1116.2188 | 122.8867 | -122.6028 | 0.16479 | -0.033814 | -0.15499 | -0.071521 | -0.12116 | -0.009515 | -0.042612 | -0.12681 | -0.029925 | 0.11585 | -0.08205 | -0.14758 | 0.048236 | 0.091891 | 122.3194 | 122.4538 | 122.569 | 122.4479 | 122.5313 | 122.4817 | 122.5933 | 122.5602 | 122.476 | -0.029925 | 0.11585 | -0.08205 | -0.14758 | 0.048236 | 0.091891 | 122.3194 | 122.4538 | -0.078161 | -122.3493 | -0.13029 | -122.4014
1117.9531 | 122.8638 | -122.5983 | 0.17395 | -0.038393 | -0.15957 | -0.066943 | -0.11659 | -0.014093 | -0.038034 | -0.13139 | -0.052818 | 0.10211 | -0.077472 | -0.15216 | 0.06197 | 0.11478 | 122.3148 | 122.463 | 122.5599 | 122.4387 | 122.5313 | 122.4817 | 122.5842 | 122.5602 | 122.4669 | -0.052818 | 0.10211 | -0.077472 | -0.15216 | 0.06197 | 0.11478 | 122.3148 | 122.463 | -0.11479 | -122.3676 | -0.13944 | -122.3922
1119.6875 | 122.9233 | -122.6028 | 0.17853 | -0.029236 | -0.16873 | -0.066943 | -0.11659 | -0.009515 | -0.033455 | -0.13139 | -0.034504 | 0.10211 | -0.05458 | -0.14758 | 0.12149 | 0.18345 | 122.3239 | 122.4721 | 122.5736 | 122.4341 | 122.5359 | 122.4863 | 122.5933 | 122.5694 | 122.4715 | -0.034504 | 0.10211 | -0.05458 | -0.14758 | 0.12149 | 0.18345 | 122.3239 | 122.4721 | -0.15599 | -122.3584 | -0.17607 | -122.3785
1121.4375 | 122.7905 | -122.6257 | 0.17853 | -0.024657 | -0.15957 | -0.066943 | -0.11201 | -0.018671 | -0.038034 | -0.12681 | -0.011611 | 0.11585 | -0.040846 | -0.143 | 0.11233 | 0.1743 | 122.3194 | 122.463 | 122.6011 | 122.4662 | 122.5588 | 122.5137 | 122.6071 | 122.5877 | 122.4989 | -0.011611 | 0.11585 | -0.040846 | -0.143 | 0.11233 | 0.1743 | 122.3194 | 122.463 | -0.12394 | -122.331 | -0.15318 | -122.3602
1123.1875 | 122.7905 | -122.6212 | 0.19226 | -0.024657 | -0.15499 | -0.071521 | -0.11201 | -0.018671 | -0.038034 | -0.14055 | -0.089445 | 0.10669 | -0.068315 | -0.15216 | 0.12149 | 0.18345 | 122.3148 | 122.4584 | 122.5965 | 122.4662 | 122.5496 | 122.5091 | 122.6025 | 122.5831 | 122.4806 | -0.089445 | 0.10669 | -0.068315 | -0.15216 | 0.12149 | 0.18345 | 122.3148 | 122.4584 | -0.21093 | -122.4042 | -0.1898 | -122.3831
1124.8594 | 122.8226 | -122.6028 | 0.19684 | -0.020079 | -0.15499 | -0.066943 | -0.11659 | -0.014093 | -0.042612 | -0.13139 | -0.07571 | 0.11127 | -0.072894 | -0.143 | 0.12149 | 0.18803 | 122.3194 | 122.463 | 122.5828 | 122.4479 | 122.5359 | 122.4863 | 122.5888 | 122.5602 | 122.4715 | -0.07571 | 0.11127 | -0.072894 | -0.143 | 0.12149 | 0.18803 | 122.3194 | 122.463 | -0.1972 | -122.3951 | -0.19438 | -122.3922
1126.6094 | 122.8546 | -122.5983 | 0.1831 | -0.029236 | -0.15499 | -0.066943 | -0.11201 | -0.014093 | -0.033455 | -0.13139 | -0.052818 | 0.10669 | -0.045424 | -0.15674 | 0.12149 | 0.18345 | 122.3148 | 122.4538 | 122.569 | 122.4433 | 122.5313 | 122.4863 | 122.5842 | 122.5648 | 122.4669 | -0.052818 | 0.10669 | -0.045424 | -0.15674 | 0.12149 | 0.18345 | 122.3148 | 122.4538 | -0.1743 | -122.3676 | -0.16691 | -122.3602
1128.3594 | 122.7768 | -122.644 | 0.19684 | -0.024657 | -0.15957 | -0.057786 | -0.10743 | -0.014093 | -0.028877 | -0.12681 | -0.066553 | 0.11127 | -0.068315 | -0.14758 | 0.12149 | 0.18803 | 122.3102 | 122.463 | 122.6194 | 122.4845 | 122.5863 | 122.5366 | 122.6299 | 122.6152 | 122.5172 | -0.066553 | 0.11127 | -0.068315 | -0.14758 | 0.12149 | 0.18803 | 122.3102 | 122.463 | -0.18804 | -122.3767 | -0.1898 | -122.3785
1130.0469 | 122.8867 | -122.6028 | 0.16479 | -0.015501 | -0.16415 | -0.066943 | -0.11201 | -0.004937 | -0.028877 | -0.12681 | -0.034504 | 0.11585 | -0.063737 | -0.143 | 0.12149 | 0.18345 | 122.3148 | 122.4492 | 122.5873 | 122.4387 | 122.5359 | 122.4908 | 122.5979 | 122.574 | 122.476 | -0.034504 | 0.11585 | -0.063737 | -0.143 | 0.12149 | 0.18345 | 122.3148 | 122.4492 | -0.15599 | -122.3493 | -0.18522 | -122.3785
1131.7969 | 122.9095 | -122.5754 | 0.15564 | -0.015501 | -0.15041 | -0.062364 | -0.11201 | -0.009515 | -0.033455 | -0.13139 | -0.066553 | 0.10669 | -0.08205 | -0.13842 | 0.11691 | 0.1743 | 122.3056 | 122.4538 | 122.5599 | 122.425 | 122.513 | 122.4634 | 122.5659 | 122.5419 | 122.444 | -0.066553 | 0.10669 | -0.08205 | -0.13842 | 0.11691 | 0.1743 | 122.3056 | 122.4538 | -0.18346 | -122.3722 | -0.19896 | -122.3877
1133.5469 | 122.8867 | -122.5845 | 0.17395 | -0.020079 | -0.15957 | -0.071521 | -0.10743 | -0.009515 | -0.033455 | -0.11765 | -0.066553 | 0.10211 | -0.077472 | -0.143 | 0.12149 | 0.19719 | 122.3102 | 122.4584 | 122.5645 | 122.425 | 122.513 | 122.4771 | 122.575 | 122.5511 | 122.4669 | -0.066553 | 0.10211 | -0.077472 | -0.143 | 0.12149 | 0.19719 | 122.3102 | 122.4584 | -0.18804 | -122.3767 | -0.19896 | -122.3877
1135.2344 | 122.8226 | -122.6212 | 0.1831 | -0.020079 | -0.14583 | -0.062364 | -0.11201 | -0.004937 | -0.033455 | -0.12223 | -0.039082 | 0.11127 | -0.077472 | -0.15216 | 0.12149 | 0.18345 | 122.3148 | 122.463 | 122.6011 | 122.4753 | 122.5588 | 122.5091 | 122.6162 | 122.5877 | 122.4989 | -0.039082 | 0.11127 | -0.077472 | -0.15216 | 0.12149 | 0.18345 | 122.3148 | 122.463 | -0.16057 | -122.3539 | -0.19896 | -122.3922
1136.9844 | 122.8455 | -122.5891 | 0.16937 | -0.015501 | -0.15041 | -0.053207 | -0.10743 | -0.004937 | -0.033455 | -0.11765 | -0.034504 | 0.092954 | -0.036267 | -0.13842 | 0.11233 | 0.19261 | 122.301 | 122.4446 | 122.5736 | 122.4387 | 122.5359 | 122.4817 | 122.5842 | 122.5557 | 122.4715 | -0.034504 | 0.092954 | -0.036267 | -0.13842 | 0.11233 | 0.19261 | 122.301 | 122.4446 | -0.14683 | -122.3355 | -0.1486 | -122.3373
1138.7188 | 122.8775 | -122.5754 | 0.15564 | 0.01197 | -0.12752 | -0.04405 | -0.089116 | 0.008797 | -0.005985 | -0.099343 | -0.084867 | 0.097532 | -0.08205 | -0.14758 | 0.11691 | 0.18345 | 122.3056 | 122.4538 | 122.5873 | 122.4479 | 122.5313 | 122.4863 | 122.5842 | 122.5694 | 122.476 | -0.084867 | 0.097532 | -0.08205 | -0.14758 | 0.11691 | 0.18345 | 122.3056 | 122.4538 | -0.20177 | -122.3905 | -0.19896 | -122.3877
1140.4688 | 122.8546 | -122.5662 | 0.16937 | -0.015501 | -0.14583 | -0.053207 | -0.10285 | -0.000359 | -0.01972 | -0.12223 | -0.020768 | 0.12043 | -0.045424 | -0.14758 | 0.12149 | 0.18803 | 122.3102 | 122.4584 | 122.5507 | 122.4204 | 122.513 | 122.4634 | 122.5659 | 122.5465 | 122.444 | -0.020768 | 0.12043 | -0.045424 | -0.14758 | 0.12149 | 0.18803 | 122.3102 | 122.4584 | -0.14225 | -122.331 | -0.16691 | -122.3556
1142.2188 | 122.8821 | -122.5754 | 0.15106 | -0.006344 | -0.12752 | -0.048628 | -0.093694 | 0.008797 | -0.015142 | -0.11308 | -0.061975 | 0.12043 | -0.063737 | -0.143 | 0.12149 | 0.18803 | 122.3056 | 122.4492 | 122.569 | 122.4479 | 122.5268 | 122.4817 | 122.5842 | 122.5602 | 122.4623 | -0.061975 | 0.12043 | -0.063737 | -0.143 | 0.12149 | 0.18803 | 122.3056 | 122.4492 | -0.18346 | -122.3676 | -0.18522 | -122.3694
1143.9062 | 122.7631 | -122.6303 | 0.19684 | -0.015501 | -0.14583 | -0.053207 | -0.10285 | -0.000359 | -0.024298 | -0.11765 | -0.029925 | 0.10669 | -0.068315 | -0.14758 | 0.12149 | 0.18803 | 122.3056 | 122.4538 | 122.6148 | 122.4845 | 122.5771 | 122.5275 | 122.63 | 122.606 | 122.5127 | -0.029925 | 0.10669 | -0.068315 | -0.14758 | 0.12149 | 0.18803 | 122.3056 | 122.4538 | -0.15141 | -122.3355 | -0.1898 | -122.3739
1145.6562 | 122.7997 | -122.612 | 0.17853 | -0.001765 | -0.13668 | -0.04405 | -0.10285 | 0.008797 | -0.015142 | -0.10392 | -0.07571 | 0.11127 | -0.063737 | -0.15216 | 0.11691 | 0.18803 | 122.3056 | 122.4538 | 122.6102 | 122.4753 | 122.5679 | 122.5091 | 122.6208 | 122.5969 | 122.5081 | -0.07571 | 0.11127 | -0.063737 | -0.15216 | 0.11691 | 0.18803 | 122.3056 | 122.4538 | -0.19262 | -122.3813 | -0.18065 | -122.3694
1147.3438 | 122.818 | -122.6212 | 0.1831 | -0.001765 | -0.1321 | -0.048628 | -0.089116 | 0.008797 | -0.010563 | -0.1085 | -0.048239 | 0.10669 | -0.045424 | -0.14758 | 0.12149 | 0.18345 | 122.3102 | 122.4584 | 122.6194 | 122.4891 | 122.5725 | 122.532 | 122.63 | 122.6106 | 122.5127 | -0.048239 | 0.10669 | -0.045424 | -0.14758 | 0.12149 | 0.18345 | 122.3102 | 122.4584 | -0.16972 | -122.3584 | -0.16691 | -122.3556
1149.0781 | 122.8683 | -122.5845 | 0.16479 | -0.006344 | -0.12752 | -0.039471 | -0.093694 | 0.017953 | -0.015142 | -0.10392 | -0.084867 | 0.097532 | -0.072894 | -0.15216 | 0.12149 | 0.18803 | 122.301 | 122.4446 | 122.5782 | 122.457 | 122.5451 | 122.4908 | 122.6025 | 122.5694 | 122.4806 | -0.084867 | 0.097532 | -0.072894 | -0.15216 | 0.12149 | 0.18803 | 122.301 | 122.4446 | -0.20635 | -122.3859 | -0.19438 | -122.3739
1150.75 | 122.7676 | -122.612 | 0.19226 | -0.001765 | -0.13668 | -0.04405 | -0.089116 | 0.004219 | -0.015142 | -0.11308 | -0.052818 | 0.11127 | -0.040846 | -0.143 | 0.11691 | 0.18345 | 122.3148 | 122.4584 | 122.6102 | 122.4753 | 122.5679 | 122.5229 | 122.6162 | 122.5969 | 122.4989 | -0.052818 | 0.11127 | -0.040846 | -0.143 | 0.11691 | 0.18345 | 122.3148 | 122.4584 | -0.16973 | -122.3676 | -0.15775 | -122.3556
1152.5 | 122.7859 | -122.612 | 0.21515 | -0.020079 | -0.15041 | -0.053207 | -0.10743 | -0.000359 | -0.024298 | -0.12223 | -0.011611 | 0.12043 | -0.05458 | -0.15216 | 0.12607 | 0.19261 | 122.3194 | 122.4584 | 122.5919 | 122.4616 | 122.5588 | 122.5046 | 122.6116 | 122.5877 | 122.4898 | -0.011611 | 0.12043 | -0.05458 | -0.15216 | 0.12607 | 0.19261 | 122.3194 | 122.4584 | -0.13768 | -122.331 | -0.18065 | -122.3739
1154.25 | 122.7631 | -122.4792 | 0.29755 | -0.010922 | -0.14583 | -0.053207 | -0.10285 | 0.008797 | -0.015142 | -0.11308 | 0.14864 | 0.20284 | 0.16518 | -0.14758 | 0.11691 | 0.17887 | 122.1545 | 122.3027 | 122.4683 | 122.3334 | 122.426 | 122.3764 | 122.488 | 122.4641 | 122.3662 | 0.14864 | 0.20284 | 0.16518 | -0.14758 | 0.11691 | 0.17887 | 122.1545 | 122.3027 | 0.031728 | -122.0059 | 0.048269 | -121.9894
1156 | 122.8088 | -122.5891 | 0.17853 | -0.020079 | -0.15041 | -0.062364 | -0.10285 | -0.000359 | -0.028877 | -0.12223 | -0.01619 | 0.12043 | -0.072894 | -0.143 | 0.12607 | 0.18803 | 122.2873 | 122.4355 | 122.569 | 122.4387 | 122.5267 | 122.4863 | 122.5888 | 122.5602 | 122.4669 | -0.01619 | 0.12043 | -0.072894 | -0.143 | 0.12607 | 0.18803 | 122.2873 | 122.4355 | -0.14226 | -122.3035 | -0.19896 | -122.3602
1157.6875 | 122.8821 | -122.5708 | 0.16937 | -0.010922 | -0.14583 | -0.053207 | -0.098273 | 0.004219 | -0.028877 | -0.11765 | -0.039082 | 0.11585 | -0.040846 | -0.14758 | 0.12607 | 0.18345 | 122.2827 | 122.4309 | 122.5599 | 122.425 | 122.5176 | 122.4725 | 122.575 | 122.5419 | 122.4531 | -0.039082 | 0.11585 | -0.040846 | -0.14758 | 0.12607 | 0.18345 | 122.2827 | 122.4309 | -0.16515 | -122.3218 | -0.16691 | -122.3236
1159.4219 | 122.7356 | -122.6303 | 0.19226 | -0.010922 | -0.15041 | -0.053207 | -0.10743 | -0.000359 | -0.028877 | -0.11765 | -0.043661 | 0.11127 | -0.068315 | -0.15216 | 0.11691 | 0.18803 | 122.2919 | 122.4355 | 122.6194 | 122.4799 | 122.5771 | 122.5229 | 122.63 | 122.6014 | 122.5127 | -0.043661 | 0.11127 | -0.068315 | -0.15216 | 0.11691 | 0.18803 | 122.2919 | 122.4355 | -0.16057 | -122.3355 | -0.18522 | -122.3602
1161.1719 | 122.8226 | -122.3373 | 0.36163 | 0.016548 | -0.12294 | -0.025735 | -0.07538 | 0.027109 | -0.001406 | -0.085608 | 0.21731 | 0.25779 | 0.20638 | -0.14758 | 0.12607 | 0.19261 | 122.1637 | 122.2661 | 122.3539 | 122.2144 | 122.3116 | 122.262 | 122.3644 | 122.3359 | 122.2517 | 0.21731 | 0.25779 | 0.20638 | -0.14758 | 0.12607 | 0.19261 | 122.1637 | 122.2661 | 0.091249 | -121.9464 | 0.080317 | -121.9573
1162.8594 | 122.6898 | -122.3511 | 0.36621 | -0.006344 | -0.14583 | -0.04405 | -0.093694 | 0.004219 | -0.024298 | -0.1085 | 0.17611 | 0.23032 | 0.18807 | -0.13842 | 0.181 | 0.18803 | 122.2736 | 122.4172 | 122.3447 | 122.2052 | 122.307 | 122.2574 | 122.3553 | 122.3268 | 122.2426 | 0.17611 | 0.23032 | 0.18807 | -0.13842 | 0.181 | 0.18803 | 122.2736 | 122.4172 | -0.004896 | -122.0975 | 0.007065 | -122.0855
1164.5938 | 122.6212 | -122.2366 | 0.42114 | -0.006344 | -0.14125 | -0.048628 | -0.098273 | 0.022531 | -0.01972 | -0.1085 | 0.23105 | 0.28069 | 0.2247 | -0.143 | 0.181 | 0.17887 | 122.1683 | 122.3165 | 122.2303 | 122.0954 | 122.188 | 122.1384 | 122.2592 | 122.2169 | 122.1281 | 0.23105 | 0.28069 | 0.2247 | -0.143 | 0.181 | 0.17887 | 122.1683 | 122.3165 | 0.050046 | -121.9372 | 0.043692 | -121.9436
1166.3438 | 122.6303 | -121.5454 | 0.92468 | 0.016548 | -0.1092 | -0.016578 | -0.066223 | 0.040843 | 0.003172 | -0.076452 | 0.74842 | 0.76146 | 0.69626 | 0.2508 | 0.19931 | 0.17887 | 121.5593 | 121.6938 | 121.562 | 121.4362 | 121.5288 | 121.4792 | 121.5863 | 121.5486 | 121.469 | 0.74842 | 0.76146 | 0.69626 | 0.2508 | 0.19931 | 0.17887 | 121.5593 | 121.6938 | 0.5491 | -120.8109 | 0.49694 | -120.8631
1168.0312 | 122.612 | -44.1788 | 78.154 | -0.015501 | -0.15041 | -0.053207 | -0.10743 | -0.004937 | -0.015142 | -0.12681 | 0.12574 | 0.20284 | 0.11482 | 0.063059 | 0.12607 | 0.18345 | 43.8366 | 43.9748 | 44.1633 | 44.0284 | 44.1256 | 44.0713 | 44.1738 | 44.1636 | 44.052 | 0.12574 | 0.20284 | 0.11482 | 0.063059 | 0.12607 | 0.18345 | 43.8366 | 43.9748 | -0.000321 | -43.7109 | -0.011249 | -43.7218
1169.7812 | 122.6532 | -3.9139 | 118.689 | -0.029236 | -0.15957 | -0.062364 | -0.11201 | -0.009515 | -0.028877 | -0.12681 | 0.10285 | 0.17079 | -0.1141 | -0.11552 | 0.13064 | 0.19719 | 3.556 | 3.5953 | 3.8846 | 3.7543 | 3.8515 | 3.8019 | 3.9044 | 3.885 | 3.7871 | 0.10285 | 0.17079 | -0.1141 | -0.11552 | 0.13064 | 0.19719 | 3.556 | 3.5953 | -0.027792 | -3.4531 | -0.24474 | -3.6701
1171.5312 | 122.6761 | -10.0204 | 112.5137 | -0.024657 | -0.16415 | -0.071521 | -0.11201 | -0.009515 | -0.038034 | -0.13139 | 0.098273 | 0.042587 | -0.10952 | -0.12468 | 0.11691 | 0.19261 | 9.778 | 9.8491 | 9.9958 | 9.8563 | 9.9489 | 9.9084 | 10.0109 | 9.9824 | 9.8891 | 0.098273 | 0.042587 | -0.10952 | -0.12468 | 0.11691 | 0.19261 | 9.778 | 9.8491 | -0.018635 | -9.6797 | -0.22643 | -9.8875
1173.2656 | 122.7036 | -9.7549 | 112.793 | -0.033814 | -0.15957 | -0.071521 | -0.12116 | -0.009515 | -0.038034 | -0.13139 | 0.10285 | 0.047165 | -0.11868 | -0.13384 | 0.12607 | 0.18345 | 9.5216 | 9.5973 | 9.7211 | 9.5954 | 9.6834 | 9.6338 | 9.7454 | 9.7169 | 9.6236 | 0.10285 | 0.047165 | -0.11868 | -0.13384 | 0.12607 | 0.18345 | 9.5216 | 9.5973 | -0.023214 | -9.4188 | -0.24474 | -9.6403
1175.0156 | 122.731 | -10.144 | 112.4268 | -0.029236 | -0.15957 | -0.066943 | -0.12116 | -0.004937 | -0.028877 | -0.12681 | 0.098273 | 0.047165 | -0.11868 | -0.12926 | 0.12149 | 0.18345 | 9.8467 | 9.9269 | 10.1148 | 9.9845 | 10.0771 | 10.0229 | 10.1391 | 10.1152 | 10.0172 | 0.098273 | 0.047165 | -0.11868 | -0.12926 | 0.12149 | 0.18345 | 9.8467 | 9.9269 | -0.023213 | -9.7484 | -0.24016 | -9.9654
1176.7656 | 122.6074 | -13.1882 | 109.4696 | -0.038393 | -0.16415 | -0.080679 | -0.11659 | -0.014093 | -0.038034 | -0.13139 | 0.10285 | 0.047165 | -0.10494 | -0.12926 | 0.12149 | 0.18803 | 12.9646 | 13.0492 | 13.1498 | 13.024 | 13.1075 | 13.0716 | 13.1741 | 13.1501 | 13.0568 | 0.10285 | 0.047165 | -0.10494 | -0.12926 | 0.12149 | 0.18803 | 12.9646 | 13.0492 | -0.018635 | -12.8617 | -0.22643 | -13.0695
1178.4375 | 122.7127 | -13.4537 | 109.1537 | -0.029236 | -0.15957 | -0.0761 | -0.12116 | -0.018671 | -0.038034 | -0.13139 | 0.10285 | 0.042587 | -0.10952 | -0.12926 | 0.11691 | 0.19261 | 13.253 | 13.3514 | 13.4244 | 13.2941 | 13.3776 | 13.3325 | 13.435 | 13.4156 | 13.3223 | 0.10285 | 0.042587 | -0.10952 | -0.12926 | 0.11691 | 0.19261 | 13.253 | 13.3514 | -0.014057 | -13.1501 | -0.22643 | -13.3625
1180.1719 | 122.699 | -11.3342 | 111.2869 | -0.029236 | -0.15957 | -0.066943 | -0.12574 | -0.014093 | -0.04719 | -0.13139 | 0.10743 | 0.042587 | -0.10952 | -0.13384 | 0.11691 | 0.18345 | 11.1469 | 11.2408 | 11.305 | 11.1747 | 11.2673 | 11.2085 | 11.3201 | 11.287 | 11.2028 | 0.10743 | 0.042587 | -0.10952 | -0.13384 | 0.11691 | 0.18345 | 11.1469 | 11.2408 | -0.009478 | -11.0395 | -0.22643 | -11.2565
1181.9219 | 122.6395 | -11.1053 | 111.5799 | -0.033814 | -0.16873 | -0.0761 | -0.12574 | -0.009515 | -0.04719 | -0.13597 | 0.10285 | 0.047165 | -0.10952 | -0.1201 | 0.12149 | 0.18345 | 10.6342 | 10.7098 | 11.0715 | 10.9366 | 11.0292 | 10.9796 | 11.0958 | 11.0582 | 10.9694 | 0.10285 | 0.047165 | -0.10952 | -0.1201 | 0.12149 | 0.18345 | 10.6342 | 10.7098 | -0.018635 | -10.5313 | -0.23101 | -10.7437
1183.6719 | 122.6852 | -11.4304 | 111.2228 | -0.029236 | -0.16873 | -0.066943 | -0.12116 | -0.023249 | -0.038034 | -0.13139 | 0.10743 | 0.024271 | -0.10494 | -0.11552 | 0.11691 | 0.1743 | 11.124 | 11.2134 | 11.4011 | 11.2616 | 11.3634 | 11.3092 | 11.4071 | 11.3923 | 11.299 | 0.10743 | 0.024271 | -0.10494 | -0.11552 | 0.11691 | 0.1743 | 11.124 | 11.2134 | -0.009478 | -11.0166 | -0.22185 | -11.229
1185.3594 | 122.7676 | -11.3983 | 111.1862 | -0.033814 | -0.16415 | -0.062364 | -0.12574 | -0.018671 | -0.038034 | -0.12681 | 0.10285 | 0.042587 | -0.1141 | -0.12468 | 0.11691 | 0.17887 | 11.1607 | 11.2317 | 11.3645 | 11.2342 | 11.336 | 11.2726 | 11.3796 | 11.3603 | 11.2715 | 0.10285 | 0.042587 | -0.1141 | -0.12468 | 0.11691 | 0.17887 | 11.1607 | 11.2317 | -0.014057 | -11.0578 | -0.23101 | -11.2748
1187.1094 | 122.7036 | -11.0916 | 111.5616 | -0.024657 | -0.16873 | -0.0761 | -0.12116 | -0.009515 | -0.038034 | -0.13597 | 0.11201 | 0.047165 | -0.11868 | -0.12926 | 0.11691 | 0.17887 | 10.8173 | 10.902 | 11.067 | 10.9229 | 11.0155 | 10.9704 | 11.0821 | 11.0536 | 10.9556 | 0.11201 | 0.047165 | -0.11868 | -0.12926 | 0.11691 | 0.17887 | 10.8173 | 10.902 | -0.0049 | -10.7053 | -0.23558 | -10.936
1188.8594 | 122.7219 | -8.1894 | 114.4638 | -0.029236 | -0.16415 | -0.0761 | -0.12574 | -0.009515 | -0.04719 | -0.13597 | 0.098273 | 0.038008 | -0.1141 | -0.12468 | 0.10775 | 0.18345 | 8.0703 | 8.1368 | 8.1602 | 8.0252 | 8.1133 | 8.0636 | 8.1799 | 8.1422 | 8.0534 | 0.098273 | 0.038008 | -0.1141 | -0.12468 | 0.10775 | 0.18345 | 8.0703 | 8.1368 | -0.009479 | -7.972 | -0.22185 | -8.1844
1190.6094 | 122.6715 | -7.8094 | 114.8804 | -0.033814 | -0.17331 | -0.071521 | -0.12574 | -0.023249 | -0.042612 | -0.13597 | 0.10285 | 0.038008 | -0.10952 | -0.12468 | 0.11691 | 0.17887 | 7.498 | 7.5691 | 7.7756 | 7.6361 | 7.7379 | 7.6837 | 7.7862 | 7.7668 | 7.6735 | 0.10285 | 0.038008 | -0.10952 | -0.12468 | 0.11691 | 0.17887 | 7.498 | 7.5691 | -0.014057 | -7.3951 | -0.22643 | -7.6075
1192.3594 | 122.6944 | -8.2718 | 114.4363 | -0.033814 | -0.16873 | -0.066943 | -0.11659 | -0.009515 | -0.033455 | -0.12681 | 0.10743 | 0.047165 | -0.11868 | -0.12468 | 0.11233 | 0.17887 | 7.9375 | 7.9995 | 8.238 | 8.1031 | 8.2048 | 8.1552 | 8.2623 | 8.2383 | 8.145 | 0.10743 | 0.047165 | -0.11868 | -0.12468 | 0.11233 | 0.17887 | 7.9375 | 7.9995 | -0.0049 | -7.8301 | -0.23101 | -8.0562
1194.0469 | 122.7631 | -8.1161 | 114.537 | -0.029236 | -0.17331 | -0.0761 | -0.12574 | -0.018671 | -0.042612 | -0.14512 | 0.10743 | 0.047165 | -0.10494 | -0.12468 | 0.11233 | 0.16972 | 7.8322 | 7.9033 | 8.0869 | 7.9428 | 8.04 | 7.9904 | 8.0975 | 8.0735 | 7.971 | 0.10743 | 0.047165 | -0.10494 | -0.12468 | 0.11233 | 0.16972 | 7.8322 | 7.9033 | -0.0049 | -7.7248 | -0.21727 | -7.9371
1195.7969 | 122.7264 | -8.3176 | 114.3631 | -0.033814 | -0.17331 | -0.0761 | -0.12116 | -0.018671 | -0.042612 | -0.14055 | 0.10285 | 0.060902 | -0.11868 | -0.12468 | 0.11691 | 0.16972 | 7.9924 | 8.059 | 8.2838 | 8.1443 | 8.2415 | 8.1964 | 8.2989 | 8.275 | 8.177 | 0.10285 | 0.060902 | -0.11868 | -0.12468 | 0.11691 | 0.16972 | 7.9924 | 8.059 | -0.014057 | -7.8896 | -0.23558 | -8.1111
1197.5 | 122.7859 | -8.2901 | 114.3539 | -0.042971 | -0.17331 | -0.080679 | -0.13032 | -0.018671 | -0.042612 | -0.13597 | 0.098273 | 0.042587 | -0.12326 | -0.12926 | 0.11233 | 0.1743 | 8.4228 | 8.5031 | 8.2471 | 8.1168 | 8.2094 | 8.1598 | 8.2714 | 8.2475 | 8.1541 | 0.098273 | 0.042587 | -0.12326 | -0.12926 | 0.11233 | 0.1743 | 8.4228 | 8.5031 | -0.014057 | -8.3245 | -0.23558 | -8.5461
1199.2656 | 122.7951 | -8.5327 | 114.1251 | -0.038393 | -0.17788 | -0.0761 | -0.13032 | -0.018671 | -0.042612 | -0.14512 | -0.13065 | 0.047165 | -0.1141 | -0.11552 | 0.10317 | 0.1743 | 8.2992 | 8.384 | 8.4943 | 8.3548 | 8.4566 | 8.4024 | 8.514 | 8.4901 | 8.3876 | -0.13065 | 0.047165 | -0.1141 | -0.11552 | 0.10317 | 0.1743 | 8.2992 | 8.384 | -0.23383 | -8.4298 | -0.21727 | -8.4133
1201.0156 | 122.7768 | -8.3496 | 114.2761 | -0.033814 | -0.17331 | -0.0761 | -0.12574 | -0.023249 | -0.042612 | -0.13597 | -0.12607 | 0.051744 | -0.10952 | -0.12468 | 0.10775 | 0.17887 | 8.0977 | 8.1689 | 8.3158 | 8.1763 | 8.2735 | 8.2239 | 8.3264 | 8.307 | 8.2136 | -0.12607 | 0.051744 | -0.10952 | -0.12468 | 0.10775 | 0.17887 | 8.0977 | 8.1689 | -0.23383 | -8.2238 | -0.21727 | -8.2073
1202.7031 | 122.7036 | -8.1207 | 114.5828 | -0.033814 | -0.16415 | -0.071521 | -0.12116 | -0.014093 | -0.038034 | -0.14512 | -0.13981 | 0.047165 | -0.1141 | -0.1201 | 0.11233 | 0.16972 | 7.8139 | 7.8759 | 8.0869 | 7.9566 | 8.0492 | 7.9996 | 8.1066 | 8.0827 | 7.9756 | -0.13981 | 0.047165 | -0.1141 | -0.1201 | 0.11233 | 0.16972 | 7.8139 | 7.8759 | -0.25214 | -7.9537 | -0.22643 | -7.928
1204.4531 | 122.7859 | -8.02 | 114.6332 | -0.042971 | -0.16873 | -0.0761 | -0.1349 | -0.014093 | -0.042612 | -0.14055 | -0.13065 | 0.042587 | -0.10952 | -0.12468 | 0.10775 | 0.16514 | 7.7589 | 7.8301 | 7.977 | 7.8513 | 7.9439 | 7.8851 | 8.0059 | 7.9774 | 7.8795 | -0.13065 | 0.042587 | -0.10952 | -0.12468 | 0.10775 | 0.16514 | 7.7589 | 7.8301 | -0.2384 | -7.8896 | -0.21727 | -7.8685
1206.1875 | 122.8134 | -8.0978 | 114.537 | -0.033814 | -0.16873 | -0.071521 | -0.13948 | -0.027827 | -0.042612 | -0.13597 | -0.13065 | 0.047165 | -0.1141 | -0.12468 | 0.11233 | 0.16972 | 7.8413 | 7.8988 | 8.064 | 7.9291 | 8.0263 | 7.9584 | 8.07 | 8.0552 | 7.9619 | -0.13065 | 0.047165 | -0.1141 | -0.12468 | 0.11233 | 0.16972 | 7.8413 | 7.8988 | -0.24298 | -7.972 | -0.22643 | -7.9554
1207.875 | 122.7219 | -9.3155 | 113.3652 | -0.038393 | -0.16873 | -0.0761 | -0.13032 | -0.023249 | -0.04719 | -0.13139 | -0.12607 | 0.047165 | -0.1141 | -0.12468 | 0.10775 | 0.16514 | 8.8165 | 8.8876 | 9.2771 | 9.1468 | 9.2394 | 9.1852 | 9.2922 | 9.2683 | 9.1841 | -0.12607 | 0.047165 | -0.1141 | -0.12468 | 0.10775 | 0.16514 | 8.8165 | 8.8876 | -0.23383 | -8.9426 | -0.22185 | -8.9306
1209.625 | 122.7356 | -8.1207 | 114.5187 | -0.038393 | -0.16415 | -0.080679 | -0.12574 | -0.027827 | -0.051769 | -0.13597 | -0.13065 | 0.042587 | -0.1141 | -0.12468 | 0.10317 | 0.1743 | 7.7956 | 7.8667 | 8.0823 | 7.9566 | 8.04 | 7.995 | 8.0929 | 8.069 | 7.9848 | -0.13065 | 0.042587 | -0.1141 | -0.12468 | 0.10317 | 0.1743 | 7.7956 | 7.8667 | -0.23383 | -7.9262 | -0.21727 | -7.9097
1211.3125 | 122.7081 | -8.4641 | 114.267 | -0.033814 | -0.17331 | -0.0761 | -0.12574 | -0.018671 | -0.051769 | -0.14055 | -0.13065 | 0.051744 | -0.10952 | -0.12468 | 0.11233 | 0.16514 | 8.0794 | 8.146 | 8.4302 | 8.2907 | 8.388 | 8.3383 | 8.4454 | 8.4123 | 8.3235 | -0.13065 | 0.051744 | -0.10952 | -0.12468 | 0.11233 | 0.16514 | 8.0794 | 8.146 | -0.24298 | -8.2101 | -0.22185 | -8.1889
1213.0625 | 122.7493 | -8.5236 | 114.1571 | -0.042971 | -0.16415 | -0.085257 | -0.12574 | -0.027827 | -0.051769 | -0.14055 | -0.13065 | 0.042587 | -0.11868 | -0.12926 | 0.11233 | 0.16514 | 8.1664 | 8.2192 | 8.4806 | 8.3594 | 8.4383 | 8.3978 | 8.4957 | 8.4718 | 8.383 | -0.13065 | 0.042587 | -0.11868 | -0.12926 | 0.11233 | 0.16514 | 8.1664 | 8.2192 | -0.24298 | -8.2971 | -0.23101 | -8.2851
1214.7969 | 122.7539 | -9.407 | 113.2736 | -0.042971 | -0.17331 | -0.0761 | -0.12574 | -0.018671 | -0.04719 | -0.14512 | -0.13065 | 0.042587 | -0.11868 | -0.1201 | 0.098596 | 0.16514 | 9.192 | 9.2676 | 9.3641 | 9.2337 | 9.3309 | 9.2813 | 9.3884 | 9.3599 | 9.2619 | -0.13065 | 0.042587 | -0.11868 | -0.1201 | 0.098596 | 0.16514 | 9.192 | 9.2676 | -0.22925 | -9.3226 | -0.21727 | -9.3106
1216.5 | 122.6852 | -8.7662 | 113.9557 | -0.038393 | -0.16873 | -0.0761 | -0.12574 | -0.018671 | -0.038034 | -0.14055 | -0.12607 | 0.051744 | -0.10494 | -0.12468 | 0.11233 | 0.16514 | 8.6655 | 8.7457 | 8.7278 | 8.5974 | 8.6901 | 8.6404 | 8.7475 | 8.7281 | 8.6256 | -0.12607 | 0.051744 | -0.10494 | -0.12468 | 0.11233 | 0.16514 | 8.6655 | 8.7457 | -0.2384 | -8.7915 | -0.21727 | -8.7704
1218.25 | 122.6669 | -8.6609 | 114.0747 | -0.042971 | -0.16873 | -0.071521 | -0.13032 | -0.018671 | -0.042612 | -0.13139 | -0.13523 | 0.047165 | -0.10952 | -0.12468 | 0.10775 | 0.16514 | 8.3679 | 8.4436 | 8.6179 | 8.4922 | 8.5894 | 8.5306 | 8.6422 | 8.6183 | 8.5295 | -0.13523 | 0.047165 | -0.10952 | -0.12468 | 0.10775 | 0.16514 | 8.3679 | 8.4436 | -0.24298 | -8.5031 | -0.21727 | -8.4774
1220 | 122.7631 | -8.5419 | 114.1571 | -0.038393 | -0.17331 | -0.0761 | -0.13032 | -0.032405 | -0.04719 | -0.14055 | -0.13065 | 0.042587 | -0.11868 | -0.12468 | 0.10317 | 0.15598 | 8.258 | 8.3245 | 8.5035 | 8.3686 | 8.4658 | 8.4115 | 8.5095 | 8.4947 | 8.4013 | -0.13065 | 0.042587 | -0.11868 | -0.12468 | 0.10317 | 0.15598 | 8.258 | 8.3245 | -0.23383 | -8.3886 | -0.22185 | -8.3767
1221.7656 | 122.6395 | -8.5098 | 114.2624 | -0.038393 | -0.17788 | -0.0761 | -0.12574 | -0.023249 | -0.04719 | -0.1497 | -0.13523 | 0.047165 | -0.11868 | -0.12468 | 0.10775 | 0.16972 | 8.1618 | 8.2375 | 8.4714 | 8.3319 | 8.4337 | 8.3841 | 8.4866 | 8.4626 | 8.3601 | -0.13523 | 0.047165 | -0.11868 | -0.12468 | 0.10775 | 0.16972 | 8.1618 | 8.2375 | -0.24298 | -8.2971 | -0.22643 | -8.2805
1223.4531 | 122.7036 | -8.6334 | 114.0747 | -0.038393 | -0.17331 | -0.0761 | -0.12574 | -0.027827 | -0.042612 | -0.1497 | -0.13065 | 0.042587 | -0.10952 | -0.12468 | 0.10317 | 0.16056 | 8.4136 | 8.4848 | 8.595 | 8.4601 | 8.5573 | 8.5077 | 8.6056 | 8.5908 | 8.4837 | -0.13065 | 0.042587 | -0.10952 | -0.12468 | 0.10317 | 0.16056 | 8.4136 | 8.4848 | -0.23383 | -8.5443 | -0.21269 | -8.5232
1225.2031 | 122.7905 | -8.6105 | 114.0472 | -0.042971 | -0.16873 | -0.085257 | -0.13032 | -0.027827 | -0.04719 | -0.14055 | -0.12607 | 0.047165 | -0.1141 | -0.12468 | 0.10317 | 0.16056 | 8.3587 | 8.439 | 8.5676 | 8.4418 | 8.5253 | 8.4802 | 8.5827 | 8.5633 | 8.47 | -0.12607 | 0.047165 | -0.1141 | -0.12468 | 0.10317 | 0.16056 | 8.3587 | 8.439 | -0.22925 | -8.4848 | -0.21727 | -8.4728
1226.9062 | 122.644 | -8.7341 | 114.0152 | -0.042971 | -0.16873 | -0.080679 | -0.13032 | -0.027827 | -0.042612 | -0.14512 | -0.13523 | 0.042587 | -0.12326 | -0.12468 | 0.10775 | 0.15598 | 8.4548 | 8.5214 | 8.6912 | 8.5654 | 8.6535 | 8.6038 | 8.7063 | 8.6915 | 8.589 | -0.13523 | 0.042587 | -0.12326 | -0.12468 | 0.10775 | 0.15598 | 8.4548 | 8.5214 | -0.24298 | -8.5901 | -0.23101 | -8.5781
1228.6406 | 122.699 | -8.6334 | 114.0839 | -0.038393 | -0.16873 | -0.080679 | -0.12116 | -0.023249 | -0.04719 | -0.14055 | -0.13065 | 0.042587 | -0.1141 | -0.13384 | 0.10775 | 0.16056 | 8.432 | 8.4985 | 8.595 | 8.4647 | 8.5527 | 8.5123 | 8.6102 | 8.5862 | 8.4929 | -0.13065 | 0.042587 | -0.1141 | -0.13384 | 0.10775 | 0.16056 | 8.432 | 8.4985 | -0.2384 | -8.5626 | -0.22185 | -8.5461
1230.3906 | 122.7448 | -8.7708 | 113.9008 | -0.047549 | -0.16873 | -0.085257 | -0.13032 | -0.027827 | -0.042612 | -0.14512 | -0.13065 | 0.02885 | -0.10494 | -0.12468 | 0.11233 | 0.16972 | 8.5189 | 8.5901 | 8.7232 | 8.602 | 8.6855 | 8.6404 | 8.7429 | 8.7281 | 8.6256 | -0.13065 | 0.02885 | -0.10494 | -0.12468 | 0.11233 | 0.16972 | 8.5189 | 8.5901 | -0.24298 | -8.6496 | -0.21727 | -8.6239
1232.0938 | 122.7585 | -8.5922 | 114.0701 | -0.042971 | -0.16873 | -0.080679 | -0.1349 | -0.027827 | -0.04719 | -0.14512 | -0.13065 | 0.038008 | -0.10952 | -0.13384 | 0.094017 | 0.16514 | 8.3083 | 8.3749 | 8.5493 | 8.4235 | 8.5115 | 8.4573 | 8.5644 | 8.545 | 8.4471 | -0.13065 | 0.038008 | -0.10952 | -0.13384 | 0.094017 | 0.16514 | 8.3083 | 8.3749 | -0.22467 | -8.439 | -0.20354 | -8.4179
1233.8438 | 122.6761 | -8.9584 | 113.7863 | -0.038393 | -0.17331 | -0.085257 | -0.1349 | -0.032405 | -0.04719 | -0.14055 | -0.13065 | 0.047165 | -0.10952 | -0.12468 | 0.11233 | 0.16972 | 8.6014 | 8.6725 | 8.92 | 8.7851 | 8.8732 | 8.8235 | 8.926 | 8.9112 | 8.8179 | -0.13065 | 0.047165 | -0.10952 | -0.12468 | 0.11233 | 0.16972 | 8.6014 | 8.6725 | -0.24298 | -8.732 | -0.22185 | -8.7109
1235.5156 | 122.7493 | -8.757 | 113.9099 | -0.052128 | -0.17331 | -0.080679 | -0.13948 | -0.032405 | -0.056347 | -0.14055 | -0.12607 | 0.047165 | -0.10952 | -0.12468 | 0.10317 | 0.16056 | 8.5602 | 8.6267 | 8.7049 | 8.5837 | 8.6763 | 8.6175 | 8.7246 | 8.7007 | 8.6165 | -0.12607 | 0.047165 | -0.10952 | -0.12468 | 0.10317 | 0.16056 | 8.5602 | 8.6267 | -0.22925 | -8.6862 | -0.21269 | -8.6697
1237.2656 | 122.7997 | -8.8348 | 113.8092 | -0.038393 | -0.16873 | -0.085257 | -0.13948 | -0.032405 | -0.04719 | -0.14055 | -0.13065 | 0.038008 | -0.1141 | -0.12468 | 0.10317 | 0.15598 | 8.638 | 8.7091 | 8.7964 | 8.6661 | 8.7496 | 8.6954 | 8.8024 | 8.7876 | 8.6943 | -0.13065 | 0.038008 | -0.1141 | -0.12468 | 0.10317 | 0.15598 | 8.638 | 8.7091 | -0.23383 | -8.7686 | -0.21727 | -8.7521
1239.0156 | 122.7585 | -9.3475 | 113.3286 | -0.042971 | -0.16873 | -0.085257 | -0.13948 | -0.032405 | -0.04719 | -0.14055 | -0.13065 | 0.047165 | -0.10952 | -0.12926 | 0.10775 | 0.1743 | 9.0775 | 9.1532 | 9.3046 | 9.1788 | 9.2623 | 9.2081 | 9.3151 | 9.3003 | 9.207 | -0.13065 | 0.047165 | -0.10952 | -0.12926 | 0.10775 | 0.1743 | 9.0775 | 9.1532 | -0.2384 | -9.2082 | -0.21727 | -9.187
1240.6875 | 122.7448 | -9.2331 | 113.4613 | -0.038393 | -0.17331 | -0.080679 | -0.14406 | -0.027827 | -0.042612 | -0.14055 | -0.13523 | 0.047165 | -0.10952 | -0.12468 | 0.10775 | 0.16056 | 8.9722 | 9.0296 | 9.1947 | 9.0598 | 9.1524 | 9.089 | 9.2053 | 9.1905 | 9.0925 | -0.13523 | 0.047165 | -0.10952 | -0.12468 | 0.10775 | 0.16056 | 8.9722 | 9.0296 | -0.24298 | -9.1074 | -0.21727 | -9.0817
1242.4375 | 122.7768 | -8.8577 | 113.8138 | -0.047549 | -0.16415 | -0.080679 | -0.1349 | -0.027827 | -0.042612 | -0.14512 | -0.13523 | 0.042587 | -0.10952 | -0.12468 | 0.10317 | 0.16056 | 8.5922 | 8.677 | 8.8102 | 8.6936 | 8.777 | 8.7228 | 8.8299 | 8.8151 | 8.7126 | -0.13523 | 0.042587 | -0.10952 | -0.12468 | 0.10317 | 0.16056 | 8.5922 | 8.677 | -0.2384 | -8.7274 | -0.21269 | -8.7017
1244.125 | 122.7814 | -9.0225 | 113.5803 | -0.047549 | -0.16415 | -0.085257 | -0.13948 | -0.032405 | -0.04719 | -0.14512 | -0.13523 | 0.042587 | -0.11868 | -0.1201 | 0.10775 | 0.15598 | 8.7295 | 8.8098 | 8.975 | 8.8584 | 8.9373 | 8.883 | 8.9901 | 8.9753 | 8.8774 | -0.13523 | 0.042587 | -0.11868 | -0.1201 | 0.10775 | 0.15598 | 8.7295 | 8.8098 | -0.24298 | -8.8648 | -0.22643 | -8.8482
1245.875 | 122.7951 | -8.9218 | 113.7039 | -0.038393 | -0.15957 | -0.085257 | -0.13948 | -0.027827 | -0.042612 | -0.14512 | -0.13065 | 0.038008 | -0.11868 | -0.12468 | 0.10775 | 0.16514 | 8.6838 | 8.7595 | 8.8834 | 8.7622 | 8.8366 | 8.7823 | 8.894 | 8.8792 | 8.7767 | -0.13065 | 0.038008 | -0.11868 | -0.12468 | 0.10775 | 0.16514 | 8.6838 | 8.7595 | -0.2384 | -8.8144 | -0.22643 | -8.8024
1247.6406 | 122.7859 | -8.9722 | 113.6765 | -0.038393 | -0.16415 | -0.0761 | -0.1349 | -0.027827 | -0.038034 | -0.14055 | -0.13065 | 0.042587 | -0.1141 | -0.1201 | 0.10317 | 0.16972 | 8.6655 | 8.7457 | 8.9338 | 8.808 | 8.8961 | 8.8373 | 8.9443 | 8.9341 | 8.8316 | -0.13065 | 0.042587 | -0.1141 | -0.1201 | 0.10317 | 0.16972 | 8.6655 | 8.7457 | -0.23383 | -8.7961 | -0.21727 | -8.7796
1249.4062 | 122.7631 | -8.9172 | 113.7451 | -0.029236 | -0.15957 | -0.080679 | -0.13032 | -0.027827 | -0.042612 | -0.13597 | -0.13065 | 0.042587 | -0.10494 | -0.12926 | 0.10317 | 0.16056 | 8.6471 | 8.7182 | 8.888 | 8.7577 | 8.8366 | 8.7869 | 8.8894 | 8.8746 | 8.7813 | -0.13065 | 0.042587 | -0.10494 | -0.12926 | 0.10317 | 0.16056 | 8.6471 | 8.7182 | -0.23383 | -8.7778 | -0.20812 | -8.7521
1251.1562 | 122.7905 | -8.8394 | 113.8046 | -0.047549 | -0.16873 | -0.080679 | -0.1349 | -0.027827 | -0.04719 | -0.14055 | -0.13523 | 0.047165 | -0.10494 | -0.1201 | 0.10775 | 0.16514 | 8.6197 | 8.6954 | 8.7919 | 8.6707 | 8.7587 | 8.7045 | 8.8116 | 8.7922 | 8.6989 | -0.13523 | 0.047165 | -0.10494 | -0.1201 | 0.10775 | 0.16514 | 8.6197 | 8.6954 | -0.24298 | -8.7549 | -0.21269 | -8.7246
1252.9062 | 122.7127 | -8.8303 | 113.9145 | -0.042971 | -0.16415 | -0.085257 | -0.12574 | -0.018671 | -0.051769 | -0.14512 | -0.13523 | 0.056323 | -0.10952 | -0.12468 | 0.10775 | 0.16972 | 8.5006 | 8.5672 | 8.7873 | 8.6661 | 8.745 | 8.7045 | 8.8116 | 8.7785 | 8.6851 | -0.13523 | 0.056323 | -0.10952 | -0.12468 | 0.10775 | 0.16972 | 8.5006 | 8.5672 | -0.24298 | -8.6359 | -0.21727 | -8.6101
1254.6562 | 122.7997 | -8.8577 | 113.7588 | -0.038393 | -0.16873 | -0.085257 | -0.1349 | -0.023249 | -0.051769 | -0.14512 | -0.13065 | 0.042587 | -0.1141 | -0.12468 | 0.10317 | 0.16514 | 8.6426 | 8.7137 | 8.8193 | 8.689 | 8.7725 | 8.7228 | 8.8345 | 8.806 | 8.7126 | -0.13065 | 0.042587 | -0.1141 | -0.12468 | 0.10317 | 0.16514 | 8.6426 | 8.7137 | -0.23383 | -8.7732 | -0.21727 | -8.7567
1256.3438 | 122.7127 | -8.7753 | 113.942 | -0.047549 | -0.16873 | -0.085257 | -0.13032 | -0.027827 | -0.042612 | -0.14055 | -0.13065 | 0.047165 | -0.10494 | -0.12468 | 0.10775 | 0.16514 | 8.4869 | 8.5534 | 8.7278 | 8.6066 | 8.6901 | 8.645 | 8.7475 | 8.7327 | 8.6348 | -0.13065 | 0.047165 | -0.10494 | -0.12468 | 0.10775 | 0.16514 | 8.4869 | 8.5534 | -0.2384 | -8.6175 | -0.21269 | -8.5918
1258.0781 | 122.6624 | -8.8486 | 113.8824 | -0.042971 | -0.16415 | -0.085257 | -0.13032 | -0.018671 | -0.042612 | -0.1497 | -0.12607 | 0.042587 | -0.10952 | -0.12468 | 0.10775 | 0.16514 | 8.5098 | 8.5901 | 8.8056 | 8.6844 | 8.7633 | 8.7183 | 8.8299 | 8.806 | 8.6989 | -0.12607 | 0.042587 | -0.10952 | -0.12468 | 0.10775 | 0.16514 | 8.5098 | 8.5901 | -0.23383 | -8.6359 | -0.21727 | -8.6193
1259.7656 | 122.7676 | -9.2834 | 113.4064 | -0.052128 | -0.15957 | -0.085257 | -0.13032 | -0.027827 | -0.042612 | -0.13597 | -0.13065 | 0.047165 | -0.10952 | -0.1201 | 0.11233 | 0.16972 | 8.931 | 9.0113 | 9.2313 | 9.1239 | 9.1982 | 9.1531 | 9.2556 | 9.2408 | 9.1475 | -0.13065 | 0.047165 | -0.10952 | -0.1201 | 0.11233 | 0.16972 | 8.931 | 9.0113 | -0.24298 | -9.0617 | -0.22185 | -9.0405
1261.5312 | 122.7539 | -9.3933 | 113.2645 | -0.047549 | -0.16415 | -0.089836 | -0.1349 | -0.027827 | -0.051769 | -0.14512 | -0.12607 | 0.038008 | -0.10494 | -0.12926 | 0.10317 | 0.16972 | 9.105 | 9.1761 | 9.3458 | 9.2292 | 9.3035 | 9.2584 | 9.3655 | 9.3415 | 9.2482 | -0.12607 | 0.038008 | -0.10494 | -0.12926 | 0.10317 | 0.16972 | 9.105 | 9.1761 | -0.22925 | -9.2311 | -0.20812 | -9.2099
1263.2188 | 122.7768 | -9.4162 | 113.1958 | -0.042971 | -0.15499 | -0.089836 | -0.13032 | -0.018671 | -0.051769 | -0.14055 | -0.13523 | 0.047165 | -0.1141 | -0.13384 | 0.094017 | 0.16972 | 9.1599 | 9.2447 | 9.3732 | 9.2612 | 9.3264 | 9.2859 | 9.3975 | 9.3644 | 9.2757 | -0.13523 | 0.047165 | -0.1141 | -0.13384 | 0.094017 | 0.16972 | 9.1599 | 9.2447 | -0.22925 | -9.2951 | -0.20811 | -9.274
1264.9688 | 122.7081 | -9.4849 | 113.2004 | -0.042971 | -0.16873 | -0.085257 | -0.13032 | -0.027827 | -0.038034 | -0.14512 | -0.12607 | 0.047165 | -0.10952 | -0.1201 | 0.11233 | 0.16514 | 9.1828 | 9.2585 | 9.4419 | 9.3161 | 9.3996 | 9.3545 | 9.457 | 9.4468 | 9.3397 | -0.12607 | 0.047165 | -0.10952 | -0.1201 | 0.11233 | 0.16514 | 9.1828 | 9.2585 | -0.2384 | -9.3089 | -0.22185 | -9.2923
1266.7344 | 122.8088 | -9.2789 | 113.3606 | -0.042971 | -0.16873 | -0.080679 | -0.1349 | -0.027827 | -0.04719 | -0.13597 | -0.12607 | 0.047165 | -0.10952 | -0.1201 | 0.11233 | 0.17887 | 9.0317 | 9.112 | 9.2359 | 9.1101 | 9.1982 | 9.144 | 9.251 | 9.2317 | 9.1429 | -0.12607 | 0.047165 | -0.10952 | -0.1201 | 0.11233 | 0.17887 | 9.0317 | 9.112 | -0.2384 | -9.1578 | -0.22185 | -9.1412
1268.4219 | 122.8043 | -9.2468 | 113.3835 | -0.038393 | -0.15957 | -0.071521 | -0.12574 | -0.027827 | -0.038034 | -0.14055 | -0.13065 | 0.051744 | -0.10494 | -0.1201 | 0.10317 | 0.16972 | 8.9859 | 9.0616 | 9.2084 | 9.0873 | 9.1753 | 9.1211 | 9.219 | 9.2088 | 9.1063 | -0.13065 | 0.051744 | -0.10494 | -0.1201 | 0.10317 | 0.16972 | 8.9859 | 9.0616 | -0.23383 | -9.1166 | -0.20812 | -9.0909
1270.1719 | 122.7356 | -9.343 | 113.3102 | -0.033814 | -0.17331 | -0.094414 | -0.13032 | -0.023249 | -0.042612 | -0.14055 | -0.12607 | 0.042587 | -0.10952 | -0.12468 | 0.10775 | 0.16972 | 9.0775 | 9.1578 | 9.3091 | 9.1697 | 9.2485 | 9.2126 | 9.3197 | 9.3003 | 9.2024 | -0.12607 | 0.042587 | -0.10952 | -0.12468 | 0.10775 | 0.16972 | 9.0775 | 9.1578 | -0.23383 | -9.2036 | -0.21727 | -9.187
1271.9219 | 122.7539 | -9.2834 | 113.3835 | -0.047549 | -0.17788 | -0.085257 | -0.1349 | -0.027827 | -0.038034 | -0.14055 | -0.12607 | 0.047165 | -0.10952 | -0.12468 | 0.10317 | 0.1743 | 8.9814 | 9.057 | 9.2359 | 9.1056 | 9.1982 | 9.1485 | 9.2556 | 9.2454 | 9.1429 | -0.12607 | 0.047165 | -0.10952 | -0.12468 | 0.10317 | 0.1743 | 8.9814 | 9.057 | -0.22925 | -9.1074 | -0.21269 | -9.0909
1273.6719 | 122.8043 | -9.1415 | 113.4567 | -0.042971 | -0.16415 | -0.085257 | -0.12574 | -0.027827 | -0.042612 | -0.14512 | -0.13065 | 0.051744 | -0.1141 | -0.12468 | 0.10775 | 0.16972 | 8.8898 | 8.9609 | 9.0986 | 8.9774 | 9.0563 | 9.0158 | 9.1137 | 9.0989 | 8.9964 | -0.13065 | 0.051744 | -0.1141 | -0.12468 | 0.10775 | 0.16972 | 8.8898 | 8.9609 | -0.2384 | -9.0204 | -0.22185 | -9.0039
1275.3594 | 122.644 | -8.8074 | 113.8916 | -0.038393 | -0.15957 | -0.080679 | -0.1349 | -0.023249 | -0.04719 | -0.13597 | -0.13065 | 0.051744 | -0.1141 | -0.12468 | 0.10775 | 0.16514 | 8.4732 | 8.5534 | 8.769 | 8.6478 | 8.7267 | 8.6725 | 8.7841 | 8.7602 | 8.6714 | -0.13065 | 0.051744 | -0.1141 | -0.12468 | 0.10775 | 0.16514 | 8.4732 | 8.5534 | -0.2384 | -8.6038 | -0.22185 | -8.5873
1277.0469 | 122.6669 | -9.256 | 113.4705 | -0.038393 | -0.15957 | -0.080679 | -0.13032 | -0.023249 | -0.042612 | -0.14055 | -0.13065 | 0.042587 | -0.1141 | -0.12468 | 0.10775 | 0.16514 | 8.8944 | 8.9655 | 9.2176 | 9.0964 | 9.1753 | 9.1257 | 9.2327 | 9.2134 | 9.1154 | -0.13065 | 0.042587 | -0.1141 | -0.12468 | 0.10775 | 0.16514 | 8.8944 | 8.9655 | -0.2384 | -9.025 | -0.22185 | -9.0085
1278.7344 | 122.7905 | -8.931 | 113.7131 | -0.038393 | -0.16415 | -0.0761 | -0.12116 | -0.023249 | -0.042612 | -0.14512 | -0.13065 | 0.047165 | -0.11868 | -0.12468 | 0.098596 | 0.16514 | 8.6563 | 8.7228 | 8.8926 | 8.7668 | 8.8549 | 8.8098 | 8.9077 | 8.8884 | 8.7858 | -0.13065 | 0.047165 | -0.11868 | -0.12468 | 0.098596 | 0.16514 | 8.6563 | 8.7228 | -0.22925 | -8.7869 | -0.21727 | -8.775
1280.4219 | 122.7173 | -9.2011 | 113.5071 | -0.042971 | -0.15957 | -0.080679 | -0.1349 | -0.023249 | -0.042612 | -0.14055 | -0.1215 | 0.042587 | -0.10952 | -0.12468 | 0.10317 | 0.16514 | 8.9218 | 8.9792 | 9.1581 | 9.0415 | 9.1204 | 9.0661 | 9.1778 | 9.1584 | 9.0605 | -0.1215 | 0.042587 | -0.10952 | -0.12468 | 0.10317 | 0.16514 | 8.9218 | 8.9792 | -0.22467 | -9.0433 | -0.21269 | -9.0314
1282.1094 | 122.8043 | -9.2468 | 113.3835 | -0.042971 | -0.16415 | -0.071521 | -0.1349 | -0.018671 | -0.042612 | -0.13597 | -0.12607 | 0.042587 | -0.10952 | -0.12468 | 0.10775 | 0.16514 | 8.9676 | 9.0296 | 9.2039 | 9.0827 | 9.1753 | 9.1119 | 9.2282 | 9.2042 | 9.1109 | -0.12607 | 0.042587 | -0.10952 | -0.12468 | 0.10775 | 0.16514 | 8.9676 | 9.0296 | -0.23383 | -9.0937 | -0.21727 | -9.0771
1283.8594 | 122.7814 | -9.2743 | 113.3698 | -0.038393 | -0.16873 | -0.0761 | -0.12574 | -0.018671 | -0.038034 | -0.14055 | -0.13065 | 0.051744 | -0.1141 | -0.12926 | 0.11233 | 0.16972 | 9.0088 | 9.0937 | 9.2359 | 9.1056 | 9.1982 | 9.1485 | 9.2556 | 9.2363 | 9.1337 | -0.13065 | 0.051744 | -0.1141 | -0.12926 | 0.11233 | 0.16972 | 9.0088 | 9.0937 | -0.24298 | -9.1395 | -0.22643 | -9.1229
1285.5312 | 122.7951 | -9.3338 | 113.2736 | -0.033814 | -0.15957 | -0.080679 | -0.12574 | -0.023249 | -0.042612 | -0.13139 | -0.13065 | 0.051744 | -0.10952 | -0.1201 | 0.10317 | 0.16514 | 9.0546 | 9.1303 | 9.3 | 9.1742 | 9.2531 | 9.2081 | 9.3106 | 9.2912 | 9.2024 | -0.13065 | 0.051744 | -0.10952 | -0.1201 | 0.10317 | 0.16514 | 9.0546 | 9.1303 | -0.23383 | -9.1853 | -0.21269 | -9.1641
1287.2969 | 122.7676 | -9.288 | 113.3331 | -0.029236 | -0.15499 | -0.071521 | -0.12574 | -0.014093 | -0.028877 | -0.12681 | -0.13065 | 0.038008 | -0.11868 | -0.12468 | 0.098596 | 0.16056 | 9.0088 | 9.0891 | 9.2588 | 9.133 | 9.2165 | 9.1623 | 9.2739 | 9.2591 | 9.1612 | -0.13065 | 0.038008 | -0.11868 | -0.12468 | 0.098596 | 0.16056 | 9.0088 | 9.0891 | -0.22925 | -9.1395 | -0.21727 | -9.1275
1288.9844 | 122.7036 | -9.3796 | 113.2645 | -0.029236 | -0.15499 | -0.066943 | -0.13032 | -0.014093 | -0.028877 | -0.12681 | -0.12607 | 0.042587 | -0.1141 | -0.12468 | 0.10775 | 0.16514 | 9.0409 | 9.1211 | 9.3503 | 9.2246 | 9.3126 | 9.2493 | 9.3655 | 9.3507 | 9.2528 | -0.12607 | 0.042587 | -0.1141 | -0.12468 | 0.10775 | 0.16514 | 9.0409 | 9.1211 | -0.23383 | -9.167 | -0.22185 | -9.155
1290.7188 | 122.7631 | -9.2834 | 113.3652 | -0.033814 | -0.15499 | -0.071521 | -0.12116 | -0.014093 | -0.038034 | -0.13597 | -0.13065 | 0.042587 | -0.10952 | -0.1201 | 0.098596 | 0.16972 | 9.0043 | 9.0891 | 9.2496 | 9.1285 | 9.2119 | 9.1623 | 9.2694 | 9.2454 | 9.1475 | -0.13065 | 0.042587 | -0.10952 | -0.1201 | 0.098596 | 0.16972 | 9.0043 | 9.0891 | -0.22925 | -9.1349 | -0.20812 | -9.1138
1292.4688 | 122.7036 | -14.4974 | 108.1467 | -0.024657 | -0.15041 | -0.071521 | -0.11659 | -0.000359 | -0.033455 | -0.12681 | -0.13065 | 0.047165 | -0.10952 | -0.12468 | 0.10775 | 0.15598 | 14.3152 | 14.5783 | 14.4727 | 14.347 | 14.4259 | 14.3808 | 14.497 | 14.4639 | 14.3706 | -0.13065 | 0.047165 | -0.10952 | -0.12468 | 0.10775 | 0.15598 | 14.3152 | 14.5783 | -0.2384 | -14.4458 | -0.21727 | -14.4247
1294.1562 | 122.7448 | -13.5544 | 109.0805 | -0.033814 | -0.15041 | -0.0761 | -0.12574 | -0.018671 | -0.038034 | -0.12681 | -0.12607 | 0.047165 | -0.1141 | -0.12468 | 0.10317 | 0.16972 | 13.2759 | 13.3651 | 13.5206 | 13.404 | 13.4783 | 13.4286 | 13.5357 | 13.5163 | 13.4276 | -0.12607 | 0.047165 | -0.1141 | -0.12468 | 0.10317 | 0.16972 | 13.2759 | 13.3651 | -0.22925 | -13.402 | -0.21727 | -13.39
1295.8906 | 122.6669 | -12.8723 | 109.8404 | -0.033814 | -0.15041 | -0.062364 | -0.11201 | -0.014093 | -0.033455 | -0.12223 | -0.13065 | 0.051744 | -0.10494 | -0.12926 | 0.10775 | 0.16514 | 12.5205 | 12.6051 | 12.8385 | 12.7219 | 12.8099 | 12.7603 | 12.8582 | 12.8389 | 12.7501 | -0.13065 | 0.051744 | -0.10494 | -0.12926 | 0.10775 | 0.16514 | 12.5205 | 12.6051 | -0.2384 | -12.6511 | -0.21269 | -12.6254
1297.5781 | 122.7585 | -12.7213 | 109.9091 | -0.024657 | -0.15041 | -0.071521 | -0.11659 | -0.009515 | -0.033455 | -0.12681 | -0.13523 | 0.051744 | -0.11868 | -0.12468 | 0.10317 | 0.16056 | 12.4106 | 12.4952 | 12.6966 | 12.5708 | 12.6497 | 12.6047 | 12.7117 | 12.6878 | 12.5944 | -0.13523 | 0.051744 | -0.11868 | -0.12468 | 0.10317 | 0.16056 | 12.4106 | 12.4952 | -0.2384 | -12.5458 | -0.22185 | -12.5293
1299.3438 | 122.7905 | -12.7579 | 109.8267 | -0.024657 | -0.15041 | -0.071521 | -0.11659 | -0.014093 | -0.033455 | -0.12681 | -0.13065 | 0.051744 | -0.10952 | -0.1201 | 0.098596 | 0.16514 | 12.4609 | 12.5639 | 12.7332 | 12.6075 | 12.6864 | 12.6413 | 12.7438 | 12.7244 | 12.6311 | -0.13065 | 0.051744 | -0.10952 | -0.1201 | 0.098596 | 0.16514 | 12.4609 | 12.5639 | -0.22925 | -12.5916 | -0.20812 | -12.5705
1301.0938 | 122.6761 | -12.4832 | 110.2203 | -0.024657 | -0.15041 | -0.0761 | -0.12116 | -0.009515 | -0.024298 | -0.12681 | -0.12607 | 0.042587 | -0.10952 | -0.12926 | 0.10317 | 0.15598 | 12.1633 | 12.248 | 12.4586 | 12.3328 | 12.4071 | 12.362 | 12.4737 | 12.4589 | 12.3564 | -0.12607 | 0.042587 | -0.10952 | -0.12926 | 0.10317 | 0.15598 | 12.1633 | 12.248 | -0.22925 | -12.2894 | -0.21269 | -12.2729
1302.7812 | 122.6761 | -12.5702 | 110.1151 | -0.024657 | -0.15041 | -0.066943 | -0.11659 | -0.004937 | -0.028877 | -0.12223 | -0.13065 | 0.047165 | -0.1141 | -0.12926 | 0.11233 | 0.16514 | 12.2686 | 12.3579 | 12.5455 | 12.4198 | 12.5032 | 12.4536 | 12.5653 | 12.5413 | 12.448 | -0.13065 | 0.047165 | -0.1141 | -0.12926 | 0.11233 | 0.16514 | 12.2686 | 12.3579 | -0.24298 | -12.3993 | -0.22643 | -12.3827
1304.5469 | 122.7219 | -8.9401 | 113.6902 | -0.020079 | -0.14583 | -0.066943 | -0.12116 | -0.004937 | -0.033455 | -0.13139 | -0.12607 | 0.042587 | -0.1141 | -0.12468 | 0.094017 | 0.16056 | 8.6746 | 8.7595 | 8.92 | 8.7943 | 8.8732 | 8.819 | 8.9352 | 8.9067 | 8.8087 | -0.12607 | 0.042587 | -0.1141 | -0.12468 | 0.094017 | 0.16056 | 8.6746 | 8.7595 | -0.22009 | -8.8007 | -0.20811 | -8.7887
1306.2344 | 122.6486 | -9.137 | 113.5986 | -0.020079 | -0.14125 | -0.062364 | -0.11659 | -0.000359 | -0.028877 | -0.12223 | -0.12607 | 0.051744 | -0.1141 | -0.12468 | 0.10775 | 0.15598 | 8.7891 | 8.8693 | 9.1169 | 8.9957 | 9.0746 | 9.0204 | 9.1366 | 9.1081 | 9.0147 | -0.12607 | 0.051744 | -0.1141 | -0.12468 | 0.10775 | 0.15598 | 8.7891 | 8.8693 | -0.23383 | -8.9151 | -0.22185 | -8.9032
1307.9844 | 122.6944 | -9.1003 | 113.5849 | -0.024657 | -0.14583 | -0.062364 | -0.11659 | -0.004937 | -0.028877 | -0.12223 | -0.12607 | 0.042587 | -0.10952 | -0.11552 | 0.10317 | 0.16972 | 8.7708 | 8.8464 | 9.0757 | 8.9545 | 9.038 | 8.9838 | 9.0954 | 9.0715 | 8.9781 | -0.12607 | 0.042587 | -0.10952 | -0.11552 | 0.10317 | 0.16972 | 8.7708 | 8.8464 | -0.22925 | -8.8968 | -0.21269 | -8.8803
1309.7344 | 122.644 | -9.2514 | 113.443 | -0.024657 | -0.1321 | -0.062364 | -0.12116 | -0.000359 | -0.028877 | -0.11765 | -0.12607 | 0.038008 | -0.10494 | -0.12926 | 0.098596 | 0.16056 | 8.9356 | 9.0204 | 9.2267 | 9.1193 | 9.189 | 9.1302 | 9.251 | 9.2225 | 9.1337 | -0.12607 | 0.038008 | -0.10494 | -0.12926 | 0.098596 | 0.16056 | 8.9356 | 9.0204 | -0.22467 | -9.0617 | -0.20354 | -9.0405
1311.5 | 122.6852 | -9.2194 | 113.4888 | -0.010922 | -0.14583 | -0.062364 | -0.11659 | -0.000359 | -0.024298 | -0.11765 | -0.13523 | 0.038008 | -0.1141 | -0.12926 | 0.10775 | 0.16056 | 8.9081 | 8.9838 | 9.2084 | 9.0735 | 9.157 | 9.1028 | 9.219 | 9.1951 | 9.1017 | -0.13523 | 0.038008 | -0.1141 | -0.12926 | 0.10775 | 0.16056 | 8.9081 | 8.9838 | -0.24298 | -9.0433 | -0.22185 | -9.0222
1313.2344 | 122.731 | -9.2102 | 113.4567 | -0.020079 | -0.13668 | -0.057786 | -0.10743 | 0.008797 | -0.024298 | -0.11308 | -0.13065 | 0.042587 | -0.1141 | -0.1201 | 0.094017 | 0.16056 | 8.9035 | 8.9746 | 9.1901 | 9.0735 | 9.1524 | 9.1028 | 9.219 | 9.1859 | 9.0971 | -0.13065 | 0.042587 | -0.1141 | -0.1201 | 0.094017 | 0.16056 | 8.9035 | 8.9746 | -0.22467 | -9.0342 | -0.20811 | -9.0176
1314.9062 | 122.7448 | -9.2056 | 113.4659 | -0.020079 | -0.13668 | -0.053207 | -0.11201 | 0.008797 | -0.024298 | -0.12223 | -0.13065 | 0.051744 | -0.10952 | -0.1201 | 0.11233 | 0.16514 | 8.9173 | 9.0021 | 9.1855 | 9.069 | 9.1524 | 9.0936 | 9.2144 | 9.1813 | 9.0834 | -0.13065 | 0.051744 | -0.10952 | -0.1201 | 0.11233 | 0.16514 | 8.9173 | 9.0021 | -0.24298 | -9.0479 | -0.22185 | -9.0268
1316.6562 | 122.6349 | -9.1736 | 113.4888 | -0.006344 | -0.1321 | -0.053207 | -0.10743 | 0.004219 | -0.010563 | -0.11308 | -0.13065 | 0.047165 | -0.1141 | -0.12926 | 0.10317 | 0.16056 | 8.8761 | 8.9517 | 9.1672 | 9.0415 | 9.1204 | 9.0662 | 9.1778 | 9.163 | 9.0605 | -0.13065 | 0.047165 | -0.1141 | -0.12926 | 0.10317 | 0.16056 | 8.8761 | 8.9517 | -0.23383 | -9.0067 | -0.21727 | -8.9902
1318.4219 | 122.7631 | -9.3933 | 113.2416 | -0.006344 | -0.12752 | -0.053207 | -0.10285 | 0.013375 | -0.015142 | -0.11308 | -0.13065 | 0.056323 | -0.11868 | -0.12468 | 0.10317 | 0.16514 | 9.105 | 9.1852 | 9.387 | 9.2658 | 9.3401 | 9.2905 | 9.4067 | 9.3782 | 9.2802 | -0.13065 | 0.056323 | -0.11868 | -0.12468 | 0.10317 | 0.16514 | 9.105 | 9.1852 | -0.23383 | -9.2356 | -0.22185 | -9.2237
1320.1094 | 122.6624 | -9.4574 | 113.2233 | -0.006344 | -0.12752 | -0.048628 | -0.10743 | 0.008797 | -0.010563 | -0.1085 | -0.11692 | 0.051744 | -0.1141 | -0.11552 | 0.10317 | 0.16056 | 9.1187 | 9.1898 | 9.4511 | 9.3299 | 9.4088 | 9.35 | 9.4662 | 9.4468 | 9.3489 | -0.11692 | 0.051744 | -0.1141 | -0.11552 | 0.10317 | 0.16056 | 9.1187 | 9.1898 | -0.22009 | -9.2356 | -0.21727 | -9.2328
1321.8594 | 122.7127 | -9.4482 | 113.1775 | -0.010922 | -0.1321 | -0.057786 | -0.098273 | 0.013375 | -0.01972 | -0.11308 | -0.13065 | 0.047165 | -0.1141 | -0.12468 | 0.10317 | 0.16056 | 9.1645 | 9.2356 | 9.4373 | 9.3161 | 9.3905 | 9.35 | 9.4616 | 9.4285 | 9.3352 | -0.13065 | 0.047165 | -0.1141 | -0.12468 | 0.10317 | 0.16056 | 9.1645 | 9.2356 | -0.23383 | -9.2951 | -0.21727 | -9.2786
1323.625 | 122.699 | -9.5581 | 113.1226 | 0.002813 | -0.12752 | -0.048628 | -0.10285 | 0.008797 | -0.01972 | -0.099343 | -0.12607 | 0.042587 | -0.11868 | -0.1201 | 0.10775 | 0.16514 | 9.2835 | 9.3546 | 9.5609 | 9.4306 | 9.5095 | 9.4553 | 9.5669 | 9.5384 | 9.4588 | -0.12607 | 0.042587 | -0.11868 | -0.1201 | 0.10775 | 0.16514 | 9.2835 | 9.3546 | -0.23383 | -9.4096 | -0.22643 | -9.4022
1325.375 | 122.7676 | -12.4603 | 110.1196 | -0.010922 | -0.1321 | -0.053207 | -0.098273 | 0.013375 | -0.010563 | -0.1085 | -0.13065 | 0.047165 | -0.1141 | -0.12468 | 0.098596 | 0.16972 | 12.2274 | 12.3121 | 12.4494 | 12.3282 | 12.4071 | 12.3621 | 12.4737 | 12.4498 | 12.3518 | -0.13065 | 0.047165 | -0.1141 | -0.12468 | 0.098596 | 0.16972 | 12.2274 | 12.3121 | -0.22925 | -12.3581 | -0.21269 | -12.3415
1327.125 | 122.7722 | -12.2269 | 110.4034 | -0.006344 | -0.1321 | -0.048628 | -0.10285 | 0.008797 | -0.015142 | -0.11308 | -0.13065 | 0.047165 | -0.1141 | -0.12926 | 0.10775 | 0.16514 | 11.9161 | 11.9916 | 12.2205 | 12.0948 | 12.1782 | 12.124 | 12.2357 | 12.2117 | 12.1138 | -0.13065 | 0.047165 | -0.1141 | -0.12926 | 0.10775 | 0.16514 | 11.9161 | 11.9916 | -0.2384 | -12.0468 | -0.22185 | -12.0302
1328.7969 | 122.6395 | -12.1811 | 110.5179 | -0.006344 | -0.1321 | -0.048628 | -0.098273 | 0.017953 | -0.010563 | -0.10392 | -0.13523 | 0.042587 | -0.11868 | -0.12468 | 0.098596 | 0.16056 | 11.8612 | 11.9504 | 12.1747 | 12.049 | 12.1325 | 12.0828 | 12.199 | 12.1705 | 12.0772 | -0.13523 | 0.042587 | -0.11868 | -0.12468 | 0.098596 | 0.16056 | 11.8612 | 11.9504 | -0.23383 | -11.9964 | -0.21727 | -11.9798
1330.5469 | 122.7814 | -11.9385 | 110.6461 | -0.001765 | -0.12294 | -0.057786 | -0.10285 | 0.008797 | -0.010563 | -0.10392 | -0.13065 | 0.038008 | -0.10494 | -0.12468 | 0.10317 | 0.16514 | 11.6735 | 11.7627 | 11.9367 | 11.8155 | 11.8807 | 11.8356 | 11.9473 | 11.9279 | 11.8346 | -0.13065 | 0.038008 | -0.10494 | -0.12468 | 0.10317 | 0.16514 | 11.6735 | 11.7627 | -0.23383 | -11.8041 | -0.20812 | -11.7784
1332.2344 | 122.7722 | -12.5656 | 110.0693 | -0.001765 | -0.12752 | -0.039471 | -0.093694 | 0.013375 | -0.010563 | -0.10392 | -0.12607 | 0.051744 | -0.11868 | -0.1201 | 0.11233 | 0.16056 | 12.3053 | 12.3899 | 12.5638 | 12.4381 | 12.5261 | 12.4719 | 12.579 | 12.5551 | 12.4617 | -0.12607 | 0.051744 | -0.11868 | -0.1201 | 0.11233 | 0.16056 | 12.3053 | 12.3899 | -0.2384 | -12.4313 | -0.23101 | -12.4239
1333.9844 | 122.7768 | -13.0783 | 109.52 | 0.002813 | -0.11836 | -0.053207 | -0.10285 | 0.008797 | -0.005985 | -0.10392 | -0.13065 | 0.056323 | -0.10952 | -0.12468 | 0.098596 | 0.16514 | 12.7402 | 12.8249 | 13.0811 | 12.9599 | 13.0251 | 12.9755 | 13.0871 | 13.0723 | 12.9744 | -0.13065 | 0.056323 | -0.10952 | -0.12468 | 0.098596 | 0.16514 | 12.7402 | 12.8249 | -0.22925 | -12.8709 | -0.20812 | -12.8497
1335.7188 | 122.7264 | -12.7075 | 109.9548 | 0.002813 | -0.11836 | -0.04405 | -0.098273 | 0.017953 | -0.010563 | -0.099343 | -0.13523 | 0.047165 | -0.1141 | -0.12926 | 0.10317 | 0.16056 | 12.4426 | 12.5319 | 12.7103 | 12.5892 | 12.6635 | 12.6092 | 12.7255 | 12.697 | 12.6082 | -0.13523 | 0.047165 | -0.1141 | -0.12926 | 0.10317 | 0.16056 | 12.4426 | 12.5319 | -0.2384 | -12.5779 | -0.21727 | -12.5567
1337.4688 | 122.7951 | -12.4603 | 110.1471 | -0.010922 | -0.12752 | -0.053207 | -0.093694 | 0.017953 | -0.01972 | -0.10392 | -0.12607 | 0.047165 | -0.1141 | -0.12926 | 0.10317 | 0.16056 | 12.2274 | 12.3121 | 12.4494 | 12.3328 | 12.4071 | 12.3666 | 12.4783 | 12.4406 | 12.3564 | -0.12607 | 0.047165 | -0.1141 | -0.12926 | 0.10317 | 0.16056 | 12.2274 | 12.3121 | -0.22925 | -12.3535 | -0.21727 | -12.3415
1339.1562 | 122.699 | -12.3642 | 110.3302 | -0.006344 | -0.1321 | -0.048628 | -0.098273 | 0.022531 | -0.015142 | -0.099343 | -0.1215 | 0.047165 | -0.10952 | -0.12468 | 0.10775 | 0.16514 | 12.0626 | 12.1519 | 12.3579 | 12.2321 | 12.3156 | 12.2659 | 12.3867 | 12.3491 | 12.2649 | -0.1215 | 0.047165 | -0.10952 | -0.12468 | 0.10775 | 0.16514 | 12.0626 | 12.1519 | -0.22925 | -12.1841 | -0.21727 | -12.1721
1340.8906 | 122.6898 | -12.4786 | 110.2249 | -0.001765 | -0.12294 | -0.04405 | -0.093694 | 0.017953 | -0.010563 | -0.10392 | -0.12607 | 0.051744 | -0.10494 | -0.12468 | 0.10775 | 0.16514 | 12.1908 | 12.2755 | 12.4769 | 12.3557 | 12.4346 | 12.3849 | 12.4966 | 12.4681 | 12.3747 | -0.12607 | 0.051744 | -0.10494 | -0.12468 | 0.10775 | 0.16514 | 12.1908 | 12.2755 | -0.23383 | -12.3169 | -0.21269 | -12.2958
1342.625 | 122.7127 | -12.9547 | 109.7076 | 0.002813 | -0.11836 | -0.04405 | -0.098273 | 0.013375 | -0.010563 | -0.099343 | -0.12607 | 0.056323 | -0.10952 | -0.12468 | 0.10317 | 0.15598 | 12.6349 | 12.7333 | 12.9575 | 12.8364 | 12.9107 | 12.8564 | 12.9681 | 12.9441 | 12.8554 | -0.12607 | 0.056323 | -0.10952 | -0.12468 | 0.10317 | 0.15598 | 12.6349 | 12.7333 | -0.22925 | -12.761 | -0.21269 | -12.7444
1344.3125 | 122.699 | -12.8311 | 109.8679 | -0.001765 | -0.12294 | -0.048628 | -0.093694 | 0.022531 | -0.001406 | -0.094765 | -0.12607 | 0.051744 | -0.10036 | -0.1201 | 0.10775 | 0.16514 | 12.5021 | 12.5914 | 12.8294 | 12.7082 | 12.7825 | 12.7374 | 12.8536 | 12.8297 | 12.7364 | -0.12607 | 0.051744 | -0.10036 | -0.1201 | 0.10775 | 0.16514 | 12.5021 | 12.5914 | -0.23383 | -12.6282 | -0.20811 | -12.6025
1346.0625 | 122.7356 | -12.6251 | 109.9915 | -0.001765 | -0.12294 | -0.048628 | -0.093694 | 0.017953 | -0.001406 | -0.094765 | -0.12607 | 0.047165 | -0.10952 | -0.1201 | 0.098596 | 0.16056 | 12.3282 | 12.4128 | 12.6234 | 12.5022 | 12.5765 | 12.5314 | 12.6431 | 12.6237 | 12.5304 | -0.12607 | 0.047165 | -0.10952 | -0.1201 | 0.098596 | 0.16056 | 12.3282 | 12.4128 | -0.22467 | -12.4542 | -0.20812 | -12.4377
1347.8125 | 122.7859 | -12.6389 | 109.9915 | 0.002813 | -0.12294 | -0.04405 | -0.089116 | 0.022531 | -0.005985 | -0.094765 | -0.13065 | 0.042587 | -0.10952 | -0.12926 | 0.094017 | 0.15598 | 12.2778 | 12.3671 | 12.6417 | 12.5159 | 12.5948 | 12.5497 | 12.6614 | 12.6329 | 12.5441 | -0.13065 | 0.042587 | -0.10952 | -0.12926 | 0.094017 | 0.15598 | 12.2778 | 12.3671 | -0.22467 | -12.4085 | -0.20354 | -12.3873
1349.5156 | 122.6852 | -12.5107 | 110.2112 | 0.002813 | -0.11836 | -0.039471 | -0.089116 | 0.027109 | -0.005985 | -0.090186 | -0.12607 | 0.047165 | -0.10952 | -0.1201 | 0.098596 | 0.15141 | 12.1359 | 12.2206 | 12.5135 | 12.3923 | 12.4712 | 12.4216 | 12.5378 | 12.5047 | 12.4205 | -0.12607 | 0.047165 | -0.10952 | -0.1201 | 0.098596 | 0.15141 | 12.1359 | 12.2206 | -0.22467 | -12.2619 | -0.20812 | -12.2454
1351.2656 | 122.7676 | -12.2864 | 110.3302 | 0.002813 | -0.12294 | -0.04405 | -0.093694 | 0.022531 | -0.001406 | -0.094765 | -0.12607 | 0.042587 | -0.10952 | -0.12926 | 0.098596 | 0.16056 | 12.0123 | 12.0969 | 12.2892 | 12.1634 | 12.2423 | 12.1927 | 12.3089 | 12.285 | 12.1916 | -0.12607 | 0.042587 | -0.10952 | -0.12926 | 0.098596 | 0.16056 | 12.0123 | 12.0969 | -0.22467 | -12.1383 | -0.20812 | -12.1218
1352.9375 | 122.6624 | -12.1445 | 110.582 | -0.001765 | -0.1092 | -0.04405 | -0.079959 | 0.013375 | -0.010563 | -0.099343 | -0.13065 | 0.047165 | -0.1141 | -0.1201 | 0.11233 | 0.16514 | 11.7421 | 11.8314 | 12.1427 | 12.0353 | 12.1004 | 12.0645 | 12.1578 | 12.1339 | 12.0451 | -0.13065 | 0.047165 | -0.1141 | -0.1201 | 0.11233 | 0.16514 | 11.7421 | 11.8314 | -0.24298 | -11.8728 | -0.22643 | -11.8562
1354.7031 | 122.6715 | -12.0163 | 110.733 | 0.002813 | -0.11836 | -0.04405 | -0.084537 | 0.022531 | -0.001406 | -0.090186 | -0.1215 | 0.047165 | -0.10952 | -0.12468 | 0.10317 | 0.16056 | 11.6506 | 11.7444 | 12.0191 | 11.8979 | 11.9722 | 11.9318 | 12.0388 | 12.0149 | 11.9261 | -0.1215 | 0.047165 | -0.10952 | -0.12468 | 0.10317 | 0.16056 | 11.6506 | 11.7444 | -0.22467 | -11.7721 | -0.21269 | -11.7601
1356.375 | 122.6578 | -11.7188 | 110.9802 | -0.001765 | -0.11378 | -0.039471 | -0.093694 | 0.027109 | -0.005985 | -0.085608 | -0.12607 | 0.056323 | -0.10952 | -0.1201 | 0.094017 | 0.16514 | 11.4628 | 11.5476 | 11.717 | 11.605 | 11.6793 | 11.6251 | 11.7459 | 11.7128 | 11.6331 | -0.12607 | 0.056323 | -0.10952 | -0.1201 | 0.094017 | 0.16514 | 11.4628 | 11.5476 | -0.22009 | -11.5889 | -0.20354 | -11.5724
1358.125 | 122.7722 | -11.6272 | 111.026 | -0.001765 | -0.1092 | -0.039471 | -0.093694 | 0.022531 | -0.001406 | -0.090186 | -0.12607 | 0.042587 | -0.10952 | -0.12468 | 0.10317 | 0.16056 | 11.4308 | 11.5155 | 11.6254 | 11.518 | 11.5877 | 11.5335 | 11.6497 | 11.6258 | 11.537 | -0.12607 | 0.042587 | -0.10952 | -0.12468 | 0.10317 | 0.16056 | 11.4308 | 11.5155 | -0.22925 | -11.5569 | -0.21269 | -11.5403
1359.8125 | 122.7997 | -11.6455 | 110.9848 | -0.001765 | -0.11836 | -0.039471 | -0.093694 | 0.022531 | -0.001406 | -0.090186 | -0.1215 | 0.033429 | -0.10952 | -0.12926 | 0.094017 | 0.16056 | 11.3347 | 11.4194 | 11.6437 | 11.5271 | 11.606 | 11.5518 | 11.668 | 11.6441 | 11.5553 | -0.1215 | 0.033429 | -0.10952 | -0.12926 | 0.094017 | 0.16056 | 11.3347 | 11.4194 | -0.21551 | -11.4561 | -0.20354 | -11.4442
1361.5625 | 122.7173 | -11.6501 | 111.0443 | 0.007391 | -0.11836 | -0.04405 | -0.089116 | 0.022531 | -0.001406 | -0.090186 | -0.13065 | 0.051744 | -0.10952 | -0.1201 | 0.098596 | 0.16514 | 11.3347 | 11.4194 | 11.6575 | 11.5317 | 11.606 | 11.561 | 11.6726 | 11.6487 | 11.5599 | -0.13065 | 0.051744 | -0.10952 | -0.1201 | 0.098596 | 0.16514 | 11.3347 | 11.4194 | -0.22925 | -11.4653 | -0.20812 | -11.4442
1363.2344 | 122.6715 | -11.5723 | 111.1038 | 0.007391 | -0.11836 | -0.039471 | -0.089116 | 0.027109 | -0.001406 | -0.090186 | -0.1215 | 0.042587 | -0.1141 | -0.12468 | 0.10775 | 0.15598 | 11.3072 | 11.4056 | 11.5797 | 11.4539 | 11.5328 | 11.4832 | 11.5994 | 11.5709 | 11.4821 | -0.1215 | 0.042587 | -0.1141 | -0.12468 | 0.10775 | 0.15598 | 11.3072 | 11.4056 | -0.22925 | -11.4287 | -0.22185 | -11.4213
1365 | 122.7905 | -11.5723 | 111.0718 | 0.002813 | -0.1092 | -0.030314 | -0.089116 | 0.022531 | -0.005985 | -0.099343 | -0.12607 | 0.051744 | -0.10952 | -0.12926 | 0.10775 | 0.16056 | 11.2568 | 11.3415 | 11.5751 | 11.4631 | 11.542 | 11.4832 | 11.5948 | 11.5663 | 11.4729 | -0.12607 | 0.051744 | -0.10952 | -0.12926 | 0.10775 | 0.16056 | 11.2568 | 11.3415 | -0.23383 | -11.3829 | -0.21727 | -11.3663
1366.6875 | 122.7905 | -11.5128 | 111.1313 | 0.007391 | -0.1092 | -0.04405 | -0.084537 | 0.027109 | -0.001406 | -0.094765 | -0.11692 | 0.047165 | -0.10952 | -0.1201 | 0.10317 | 0.15141 | 11.2294 | 11.3095 | 11.5201 | 11.4036 | 11.4687 | 11.4282 | 11.5399 | 11.5114 | 11.418 | -0.11692 | 0.047165 | -0.10952 | -0.1201 | 0.10317 | 0.15141 | 11.2294 | 11.3095 | -0.22009 | -11.3463 | -0.21269 | -11.3389
1368.4375 | 122.7814 | -11.4944 | 111.145 | 0.007391 | -0.1092 | -0.034893 | -0.089116 | 0.027109 | -0.005985 | -0.085608 | -0.12607 | 0.042587 | -0.10952 | -0.1201 | 0.098596 | 0.15141 | 11.2065 | 11.2912 | 11.5018 | 11.3852 | 11.4596 | 11.4053 | 11.5216 | 11.4885 | 11.4088 | -0.12607 | 0.042587 | -0.10952 | -0.1201 | 0.098596 | 0.15141 | 11.2065 | 11.2912 | -0.22467 | -11.3325 | -0.20812 | -11.316
1370.125 | 122.6486 | -11.4487 | 111.2549 | 0.007391 | -0.10462 | -0.034893 | -0.084537 | 0.027109 | 0.003172 | -0.090186 | -0.12607 | 0.042587 | -0.10952 | -0.1201 | 0.098596 | 0.15598 | 11.1744 | 11.2591 | 11.4561 | 11.344 | 11.4138 | 11.3641 | 11.4758 | 11.4518 | 11.3585 | -0.12607 | 0.042587 | -0.10952 | -0.1201 | 0.098596 | 0.15598 | 11.1744 | 11.2591 | -0.22467 | -11.3005 | -0.20812 | -11.2839
1371.875 | 122.7219 | -11.7004 | 110.9619 | 0.002813 | -0.1092 | -0.034893 | -0.084537 | 0.027109 | 0.003172 | -0.090186 | -0.1215 | 0.056323 | -0.10494 | -0.11552 | 0.10317 | 0.16514 | 11.4033 | 11.4926 | 11.7033 | 11.5912 | 11.6655 | 11.6159 | 11.7275 | 11.7036 | 11.6103 | -0.1215 | 0.056323 | -0.10494 | -0.11552 | 0.10317 | 0.16514 | 11.4033 | 11.4926 | -0.22467 | -11.5248 | -0.20812 | -11.5083
1373.5469 | 122.7264 | -11.6043 | 111.0397 | 0.002813 | -0.11378 | -0.034893 | -0.079959 | 0.022531 | 0.003172 | -0.094765 | -0.13065 | 0.047165 | -0.11868 | -0.12468 | 0.098596 | 0.16056 | 11.3072 | 11.4056 | 11.6071 | 11.4905 | 11.5694 | 11.5244 | 11.6268 | 11.6075 | 11.5095 | -0.13065 | 0.047165 | -0.11868 | -0.12468 | 0.098596 | 0.16056 | 11.3072 | 11.4056 | -0.22925 | -11.4378 | -0.21727 | -11.4259
1375.2812 | 122.8043 | -11.5219 | 111.1313 | 0.016548 | -0.1092 | -0.034893 | -0.084537 | 0.031687 | -0.005985 | -0.090186 | -0.12607 | 0.038008 | -0.11868 | -0.12468 | 0.098596 | 0.15598 | 11.2522 | 11.337 | 11.5385 | 11.4127 | 11.487 | 11.4374 | 11.5536 | 11.5159 | 11.4317 | -0.12607 | 0.038008 | -0.11868 | -0.12468 | 0.098596 | 0.15598 | 11.2522 | 11.337 | -0.22467 | -11.3783 | -0.21727 | -11.3709
1377.0469 | 122.6715 | -11.5631 | 111.1313 | 0.016548 | -0.1092 | -0.030314 | -0.079959 | 0.027109 | -0.001406 | -0.085608 | -0.12607 | 0.051744 | -0.1141 | -0.1201 | 0.10317 | 0.16056 | 11.2614 | 11.3415 | 11.5797 | 11.4539 | 11.5328 | 11.4832 | 11.5902 | 11.5617 | 11.4775 | -0.12607 | 0.051744 | -0.1141 | -0.1201 | 0.10317 | 0.16056 | 11.2614 | 11.3415 | -0.22925 | -11.3875 | -0.21727 | -11.3755
1378.7969 | 122.7356 | -11.467 | 111.1954 | 0.01197 | -0.10004 | -0.025735 | -0.084537 | 0.031687 | -0.001406 | -0.094765 | -0.13065 | 0.042587 | -0.1141 | -0.12468 | 0.098596 | 0.15598 | 11.1881 | 11.2774 | 11.4789 | 11.3669 | 11.4412 | 11.3824 | 11.4987 | 11.4656 | 11.3722 | -0.13065 | 0.042587 | -0.1141 | -0.12468 | 0.098596 | 0.15598 | 11.1881 | 11.2774 | -0.22925 | -11.3188 | -0.21269 | -11.3022
1380.4844 | 122.699 | -11.5036 | 111.2091 | 0.01197 | -0.095467 | -0.025735 | -0.07538 | 0.036265 | 0.003172 | -0.08103 | -0.1215 | 0.047165 | -0.10952 | -0.12468 | 0.10317 | 0.16056 | 11.1653 | 11.2454 | 11.5156 | 11.4081 | 11.4779 | 11.4282 | 11.5399 | 11.5068 | 11.4226 | -0.1215 | 0.047165 | -0.10952 | -0.12468 | 0.10317 | 0.16056 | 11.1653 | 11.2454 | -0.22467 | -11.2867 | -0.21269 | -11.2748
1382.2344 | 122.7448 | -11.7554 | 110.8841 | 0.01197 | -0.1092 | -0.030314 | -0.079959 | 0.036265 | 0.00775 | -0.090186 | -0.12607 | 0.047165 | -0.10952 | -0.12926 | 0.10317 | 0.16056 | 11.4354 | 11.5292 | 11.7673 | 11.6462 | 11.7251 | 11.6754 | 11.7916 | 11.7631 | 11.6652 | -0.12607 | 0.047165 | -0.10952 | -0.12926 | 0.10317 | 0.16056 | 11.4354 | 11.5292 | -0.22925 | -11.5615 | -0.21269 | -11.5449
1383.9844 | 122.7722 | -11.586 | 111.0535 | 0.01197 | -0.095467 | -0.034893 | -0.084537 | 0.027109 | 0.003172 | -0.085608 | -0.12607 | 0.047165 | -0.1141 | -0.12468 | 0.098596 | 0.15598 | 11.3667 | 11.4468 | 11.598 | 11.4905 | 11.5511 | 11.5015 | 11.6131 | 11.5892 | 11.5004 | -0.12607 | 0.047165 | -0.1141 | -0.12468 | 0.098596 | 0.15598 | 11.3667 | 11.4468 | -0.22467 | -11.4928 | -0.21269 | -11.4808
1385.7188 | 122.699 | -11.7096 | 110.9619 | 0.021127 | -0.090888 | -0.025735 | -0.07538 | 0.036265 | 0.021485 | -0.090186 | -0.12607 | 0.051744 | -0.10952 | -0.12468 | 0.098596 | 0.15598 | 11.4171 | 11.5018 | 11.7307 | 11.6187 | 11.6839 | 11.6342 | 11.7459 | 11.7311 | 11.6194 | -0.12607 | 0.051744 | -0.10952 | -0.12468 | 0.098596 | 0.15598 | 11.4171 | 11.5018 | -0.22467 | -11.5431 | -0.20812 | -11.5266
1387.4062 | 122.7905 | -11.4761 | 111.1404 | 0.01197 | -0.10004 | -0.025735 | -0.089116 | 0.027109 | 0.003172 | -0.085608 | -0.13065 | 0.042587 | -0.10952 | -0.1201 | 0.098596 | 0.15141 | 11.2706 | 11.369 | 11.4881 | 11.3761 | 11.4504 | 11.387 | 11.5032 | 11.4793 | 11.3905 | -0.13065 | 0.042587 | -0.10952 | -0.1201 | 0.098596 | 0.15141 | 11.2706 | 11.369 | -0.22925 | -11.4012 | -0.20812 | -11.3801
1389.1719 | 122.6578 | -11.6547 | 111.0764 | 0.01197 | -0.1092 | -0.025735 | -0.07538 | 0.031687 | 0.003172 | -0.085608 | -0.12607 | 0.038008 | -0.1141 | -0.1201 | 0.089439 | 0.15598 | 11.3667 | 11.4468 | 11.6666 | 11.5455 | 11.6289 | 11.5793 | 11.6863 | 11.6578 | 11.5691 | -0.12607 | 0.038008 | -0.1141 | -0.1201 | 0.089439 | 0.15598 | 11.3667 | 11.4468 | -0.21551 | -11.4928 | -0.20354 | -11.4808
1390.8594 | 122.7264 | -11.3525 | 111.2915 | 0.016548 | -0.10004 | -0.030314 | -0.07538 | 0.036265 | 0.003172 | -0.08103 | -0.13065 | 0.042587 | -0.11868 | -0.12926 | 0.089439 | 0.15598 | 11.2156 | 11.2958 | 11.3691 | 11.2525 | 11.3222 | 11.2772 | 11.3888 | 11.3557 | 11.2715 | -0.13065 | 0.042587 | -0.11868 | -0.12926 | 0.089439 | 0.15598 | 11.2156 | 11.2958 | -0.22009 | -11.3463 | -0.20811 | -11.3343
1392.5938 | 122.7264 | -11.5585 | 111.0901 | 0.016548 | -0.10462 | -0.030314 | -0.084537 | 0.031687 | 0.003172 | -0.076452 | -0.13523 | 0.042587 | -0.10952 | -0.12926 | 0.084861 | 0.15141 | 11.2294 | 11.3049 | 11.5751 | 11.4539 | 11.5282 | 11.474 | 11.5902 | 11.5617 | 11.4821 | -0.13523 | 0.042587 | -0.10952 | -0.12926 | 0.084861 | 0.15141 | 11.2294 | 11.3049 | -0.22009 | -11.3646 | -0.19438 | -11.3389
1394.3438 | 122.7951 | -11.4304 | 111.1954 | 0.016548 | -0.10462 | -0.025735 | -0.07538 | 0.031687 | 0.003172 | -0.076452 | -0.13065 | 0.047165 | -0.1141 | -0.12926 | 0.094017 | 0.14683 | 11.1653 | 11.2546 | 11.4469 | 11.3257 | 11.4046 | 11.355 | 11.462 | 11.4335 | 11.3539 | -0.13065 | 0.047165 | -0.1141 | -0.12926 | 0.094017 | 0.14683 | 11.1653 | 11.2546 | -0.22467 | -11.2959 | -0.20811 | -11.2794
1396.0938 | 122.7905 | -11.4349 | 111.1954 | 0.021127 | -0.095467 | -0.021157 | -0.070802 | 0.036265 | 0.016907 | -0.08103 | -0.13523 | 0.047165 | -0.10952 | -0.1201 | 0.10317 | 0.15598 | 11.1149 | 11.195 | 11.4561 | 11.3395 | 11.4138 | 11.3641 | 11.4712 | 11.4518 | 11.3539 | -0.13523 | 0.047165 | -0.10952 | -0.1201 | 0.10317 | 0.15598 | 11.1149 | 11.195 | -0.2384 | -11.2501 | -0.21269 | -11.2244
1397.7812 | 122.7127 | -11.4532 | 111.232 | 0.01197 | -0.090888 | -0.025735 | -0.079959 | 0.045421 | 0.012329 | -0.076452 | -0.1215 | 0.047165 | -0.10494 | -0.12468 | 0.089439 | 0.16056 | 11.0554 | 11.1493 | 11.4652 | 11.3624 | 11.4275 | 11.3733 | 11.4987 | 11.4656 | 11.3768 | -0.1215 | 0.047165 | -0.10494 | -0.12468 | 0.089439 | 0.16056 | 11.0554 | 11.1493 | -0.21093 | -11.1769 | -0.19438 | -11.1603
1399.5469 | 122.6852 | -11.4532 | 111.2228 | 0.021127 | -0.10462 | -0.030314 | -0.070802 | 0.036265 | -0.005985 | -0.076452 | -0.13065 | 0.051744 | -0.1141 | -0.12926 | 0.10317 | 0.15598 | 11.1881 | 11.282 | 11.4744 | 11.3486 | 11.4229 | 11.3824 | 11.4895 | 11.4473 | 11.3768 | -0.13065 | 0.051744 | -0.1141 | -0.12926 | 0.10317 | 0.15598 | 11.1881 | 11.282 | -0.23383 | -11.3188 | -0.21727 | -11.3022
1401.2969 | 122.7859 | -11.3159 | 111.3007 | 0.025705 | -0.10004 | -0.030314 | -0.070802 | 0.036265 | 0.012329 | -0.08103 | -0.13981 | 0.042587 | -0.10952 | -0.12926 | 0.094017 | 0.16056 | 11.1424 | 11.2271 | 11.3416 | 11.2159 | 11.2856 | 11.2451 | 11.3522 | 11.3282 | 11.2349 | -0.13981 | 0.042587 | -0.10952 | -0.12926 | 0.094017 | 0.16056 | 11.1424 | 11.2271 | -0.23383 | -11.2822 | -0.20354 | -11.2519
1402.9688 | 122.7264 | -11.348 | 111.3281 | 0.021127 | -0.095467 | -0.025735 | -0.079959 | 0.040843 | 0.012329 | -0.076452 | -0.1215 | 0.051744 | -0.10952 | -0.12926 | 0.098596 | 0.16514 | 11.0783 | 11.163 | 11.3691 | 11.2525 | 11.3222 | 11.268 | 11.3888 | 11.3603 | 11.2715 | -0.1215 | 0.051744 | -0.10952 | -0.12926 | 0.098596 | 0.16514 | 11.0783 | 11.163 | -0.22009 | -11.1998 | -0.20812 | -11.1878
1404.7188 | 122.7905 | -11.4304 | 111.2045 | 0.021127 | -0.095467 | -0.021157 | -0.084537 | 0.045421 | 0.012329 | -0.08103 | -0.13065 | 0.042587 | -0.1141 | -0.12468 | 0.089439 | 0.15598 | 11.1378 | 11.2317 | 11.4515 | 11.3349 | 11.4092 | 11.3458 | 11.4758 | 11.4427 | 11.3493 | -0.13065 | 0.042587 | -0.1141 | -0.12468 | 0.089439 | 0.15598 | 11.1378 | 11.2317 | -0.22009 | -11.2684 | -0.20354 | -11.2519
1406.4688 | 122.6944 | -11.348 | 111.3419 | 0.021127 | -0.090888 | -0.021157 | -0.07538 | 0.040843 | 0.00775 | -0.08103 | -0.13065 | 0.047165 | -0.11868 | -0.12468 | 0.094017 | 0.15598 | 11.0966 | 11.1859 | 11.3691 | 11.2571 | 11.3268 | 11.2726 | 11.3888 | 11.3557 | 11.2669 | -0.13065 | 0.047165 | -0.11868 | -0.12468 | 0.094017 | 0.15598 | 11.0966 | 11.1859 | -0.22467 | -11.2272 | -0.21269 | -11.2153
1408.2188 | 122.7356 | -11.2839 | 111.4197 | 0.016548 | -0.086309 | -0.025735 | -0.079959 | 0.040843 | 0.016907 | -0.085608 | -0.13065 | 0.042587 | -0.10952 | -0.12468 | 0.089439 | 0.15141 | 11.0096 | 11.1035 | 11.3004 | 11.1976 | 11.2581 | 11.2039 | 11.3247 | 11.3008 | 11.1983 | -0.13065 | 0.042587 | -0.10952 | -0.12468 | 0.089439 | 0.15141 | 11.0096 | 11.1035 | -0.22009 | -11.1402 | -0.19896 | -11.1191
1409.9844 | 122.6486 | -11.348 | 111.3739 | 0.025705 | -0.095467 | -0.025735 | -0.070802 | 0.040843 | 0.00775 | -0.071874 | -0.13065 | 0.051744 | -0.10494 | -0.1201 | 0.094017 | 0.16056 | 11.0325 | 11.1172 | 11.3737 | 11.2525 | 11.3222 | 11.2772 | 11.3888 | 11.3557 | 11.2761 | -0.13065 | 0.051744 | -0.10494 | -0.1201 | 0.094017 | 0.16056 | 11.0325 | 11.1172 | -0.22467 | -11.1631 | -0.19896 | -11.1374
1411.7344 | 122.6761 | -11.4487 | 111.3007 | 0.025705 | -0.095467 | -0.021157 | -0.07538 | 0.040843 | 0.016907 | -0.085608 | -0.12607 | 0.042587 | -0.1141 | -0.12468 | 0.098596 | 0.15598 | 11.0691 | 11.1447 | 11.4744 | 11.3532 | 11.4275 | 11.3733 | 11.4895 | 11.4656 | 11.3631 | -0.12607 | 0.042587 | -0.1141 | -0.12468 | 0.098596 | 0.15598 | 11.0691 | 11.1447 | -0.22467 | -11.1952 | -0.21269 | -11.1832
1413.4219 | 122.6578 | -11.2885 | 111.438 | 0.030283 | -0.086309 | -0.021157 | -0.079959 | 0.040843 | 0.016907 | -0.085608 | -0.13065 | 0.047165 | -0.1141 | -0.12926 | 0.094017 | 0.15141 | 10.9684 | 11.0577 | 11.3187 | 11.2021 | 11.2673 | 11.2085 | 11.3293 | 11.3054 | 11.2028 | -0.13065 | 0.047165 | -0.1141 | -0.12926 | 0.094017 | 0.15141 | 10.9684 | 11.0577 | -0.22467 | -11.099 | -0.20811 | -11.0825
1415.1719 | 122.6898 | -11.3617 | 111.3876 | 0.030283 | -0.095467 | -0.016578 | -0.070802 | 0.040843 | 0.00775 | -0.076452 | -0.13065 | 0.047165 | -0.10952 | -0.12926 | 0.098596 | 0.16056 | 10.9546 | 11.0394 | 11.392 | 11.2662 | 11.3451 | 11.2909 | 11.4025 | 11.3694 | 11.2852 | -0.13065 | 0.047165 | -0.10952 | -0.12926 | 0.098596 | 0.16056 | 10.9546 | 11.0394 | -0.22925 | -11.0853 | -0.20812 | -11.0642
1416.8594 | 122.8134 | -11.2793 | 111.3464 | 0.025705 | -0.095467 | -0.021157 | -0.07538 | 0.045421 | 0.016907 | -0.08103 | -0.13065 | 0.033429 | -0.10952 | -0.12468 | 0.089439 | 0.15598 | 10.9959 | 11.076 | 11.305 | 11.1838 | 11.2581 | 11.2039 | 11.3247 | 11.2962 | 11.1983 | -0.13065 | 0.033429 | -0.10952 | -0.12468 | 0.089439 | 0.15598 | 10.9959 | 11.076 | -0.22009 | -11.1265 | -0.19896 | -11.1054
1418.6094 | 122.7585 | -11.2793 | 111.3968 | 0.01197 | -0.090888 | -0.021157 | -0.07538 | 0.036265 | 0.012329 | -0.071874 | -0.13523 | 0.042587 | -0.10952 | -0.1201 | 0.094017 | 0.15598 | 10.9821 | 11.076 | 11.2913 | 11.1884 | 11.2581 | 11.2039 | 11.3156 | 11.2916 | 11.2074 | -0.13523 | 0.042587 | -0.10952 | -0.1201 | 0.094017 | 0.15598 | 10.9821 | 11.076 | -0.22925 | -11.1173 | -0.20354 | -11.0916
1420.2969 | 122.7631 | -11.5036 | 111.1725 | 0.021127 | -0.095467 | -0.025735 | -0.079959 | 0.045421 | 0.012329 | -0.076452 | -0.13065 | 0.051744 | -0.1141 | -0.11552 | 0.094017 | 0.15598 | 11.211 | 11.3095 | 11.5247 | 11.4081 | 11.4779 | 11.4236 | 11.549 | 11.5159 | 11.4271 | -0.13065 | 0.051744 | -0.1141 | -0.11552 | 0.094017 | 0.15598 | 11.211 | 11.3095 | -0.22467 | -11.3417 | -0.20811 | -11.3251
1422.0469 | 122.7127 | -11.3709 | 111.3281 | 0.01197 | -0.10004 | -0.025735 | -0.07538 | 0.040843 | 0.012329 | -0.071874 | -0.13065 | 0.042587 | -0.1141 | -0.12468 | 0.089439 | 0.15598 | 11.0966 | 11.1996 | 11.3828 | 11.2708 | 11.3451 | 11.2955 | 11.4117 | 11.3832 | 11.299 | -0.13065 | 0.042587 | -0.1141 | -0.12468 | 0.089439 | 0.15598 | 11.0966 | 11.1996 | -0.22009 | -11.2272 | -0.20354 | -11.2107
1423.7344 | 122.7859 | -11.4075 | 111.2503 | 0.021127 | -0.095467 | -0.016578 | -0.079959 | 0.045421 | 0.012329 | -0.076452 | -0.13065 | 0.042587 | -0.11868 | -0.1201 | 0.084861 | 0.15141 | 11.0325 | 11.1172 | 11.4286 | 11.312 | 11.3909 | 11.3275 | 11.4529 | 11.4198 | 11.331 | -0.13065 | 0.042587 | -0.11868 | -0.1201 | 0.084861 | 0.15141 | 11.0325 | 11.1172 | -0.21551 | -11.1631 | -0.20354 | -11.1512
1425.4844 | 122.6715 | -11.3297 | 111.3556 | 0.025705 | -0.095467 | -0.016578 | -0.07538 | 0.045421 | 0.012329 | -0.071874 | -0.13065 | 0.051744 | -0.10036 | -0.1201 | 0.080283 | 0.15141 | 11.0279 | 11.1126 | 11.3554 | 11.2342 | 11.3131 | 11.2543 | 11.3751 | 11.342 | 11.2578 | -0.13065 | 0.051744 | -0.10036 | -0.1201 | 0.080283 | 0.15141 | 11.0279 | 11.1126 | -0.21093 | -11.1586 | -0.18065 | -11.1283
1427.1719 | 122.7173 | -11.261 | 111.4014 | 0.025705 | -0.095467 | -0.016578 | -0.070802 | 0.040843 | 0.012329 | -0.076452 | -0.13065 | 0.042587 | -0.10494 | -0.12926 | 0.080283 | 0.15141 | 10.9501 | 11.0394 | 11.2867 | 11.1655 | 11.2444 | 11.1902 | 11.3018 | 11.2733 | 11.1845 | -0.13065 | 0.042587 | -0.10494 | -0.12926 | 0.080283 | 0.15141 | 10.9501 | 11.0394 | -0.21093 | -11.0807 | -0.18522 | -11.055
1428.9062 | 122.7127 | -11.2061 | 111.5158 | 0.030283 | -0.095467 | -0.016578 | -0.079959 | 0.049999 | 0.016907 | -0.076452 | -0.12607 | 0.047165 | -0.10952 | -0.12926 | 0.084861 | 0.15598 | 10.9089 | 10.9936 | 11.2363 | 11.1106 | 11.1895 | 11.1261 | 11.2561 | 11.223 | 11.1296 | -0.12607 | 0.047165 | -0.10952 | -0.12926 | 0.084861 | 0.15598 | 10.9089 | 10.9936 | -0.21093 | -11.0349 | -0.19438 | -11.0184
1430.6562 | 122.7997 | -11.087 | 111.5707 | 0.025705 | -0.090888 | -0.016578 | -0.079959 | 0.045421 | 0.016907 | -0.071874 | -0.13523 | 0.047165 | -0.10952 | -0.1201 | 0.071126 | 0.14683 | 10.744 | 10.8334 | 11.1127 | 10.9961 | 11.0705 | 11.0071 | 11.1325 | 11.1039 | 11.0152 | -0.13523 | 0.047165 | -0.10952 | -0.1201 | 0.071126 | 0.14683 | 10.744 | 10.8334 | -0.20636 | -10.8793 | -0.18065 | -10.8536
1432.3438 | 122.6852 | -11.2061 | 111.5112 | 0.025705 | -0.090888 | -0.016578 | -0.07538 | 0.049999 | 0.016907 | -0.067295 | -0.12607 | 0.047165 | -0.10952 | -0.12468 | 0.084861 | 0.14683 | 10.831 | 10.9203 | 11.2318 | 11.1152 | 11.1895 | 11.1307 | 11.2561 | 11.223 | 11.1388 | -0.12607 | 0.047165 | -0.10952 | -0.12468 | 0.084861 | 0.14683 | 10.831 | 10.9203 | -0.21093 | -10.9571 | -0.19438 | -10.9405
1434.0781 | 122.7493 | -11.3617 | 111.2915 | 0.030283 | -0.090888 | -0.025735 | -0.070802 | 0.045421 | 0.00775 | -0.067295 | -0.13065 | 0.038008 | -0.10494 | -0.1201 | 0.080283 | 0.14225 | 10.9913 | 11.0852 | 11.392 | 11.2708 | 11.336 | 11.2909 | 11.4071 | 11.3694 | 11.2944 | -0.13065 | 0.038008 | -0.10494 | -0.1201 | 0.080283 | 0.14225 | 10.9913 | 11.0852 | -0.21093 | -11.1219 | -0.18522 | -11.0962
1435.7656 | 122.8043 | -11.0779 | 111.5341 | 0.025705 | -0.086309 | -0.021157 | -0.079959 | 0.045421 | 0.016907 | -0.076452 | -0.12607 | 0.038008 | -0.10952 | -0.12468 | 0.080283 | 0.15141 | 10.8173 | 10.9066 | 11.1036 | 10.9916 | 11.0567 | 10.9979 | 11.1233 | 11.0948 | 11.0014 | -0.12607 | 0.038008 | -0.10952 | -0.12468 | 0.080283 | 0.15141 | 10.8173 | 10.9066 | -0.20636 | -10.9434 | -0.1898 | -10.9268
1437.5 | 122.6761 | -10.9772 | 111.7584 | 0.030283 | -0.090888 | -0.016578 | -0.079959 | 0.049999 | 0.012329 | -0.067295 | -0.13065 | 0.047165 | -0.10952 | -0.1201 | 0.084861 | 0.14683 | 10.8356 | 10.9249 | 11.0075 | 10.8863 | 10.9606 | 10.8972 | 11.0272 | 10.9895 | 10.9099 | -0.13065 | 0.047165 | -0.10952 | -0.1201 | 0.084861 | 0.14683 | 10.8356 | 10.9249 | -0.21551 | -10.9663 | -0.19438 | -10.9451
1439.25 | 122.6852 | -11.1374 | 111.5753 | 0.030283 | -0.086309 | -0.016578 | -0.079959 | 0.049999 | 0.021485 | -0.067295 | -0.12607 | 0.051744 | -0.10952 | -0.1201 | 0.084861 | 0.15141 | 10.744 | 10.8288 | 11.1677 | 11.0511 | 11.1208 | 11.0574 | 11.1874 | 11.1589 | 11.0701 | -0.12607 | 0.051744 | -0.10952 | -0.1201 | 0.084861 | 0.15141 | 10.744 | 10.8288 | -0.21093 | -10.8701 | -0.19438 | -10.8536
1441.0156 | 122.8271 | -11.0046 | 111.6486 | 0.025705 | -0.095467 | -0.021157 | -0.084537 | 0.040843 | 0.012329 | -0.067295 | -0.12607 | 0.051744 | -0.10952 | -0.12468 | 0.075705 | 0.15141 | 10.7257 | 10.8059 | 11.0303 | 10.9092 | 10.9835 | 10.9201 | 11.0455 | 11.017 | 10.9373 | -0.12607 | 0.051744 | -0.10952 | -0.12468 | 0.075705 | 0.15141 | 10.7257 | 10.8059 | -0.20178 | -10.8518 | -0.18523 | -10.8352
1442.7031 | 122.8271 | -10.817 | 111.8591 | 0.030283 | -0.090888 | -0.016578 | -0.07538 | 0.045421 | 0.021485 | -0.071874 | -0.13065 | 0.042587 | -0.10952 | -0.12468 | 0.089439 | 0.14683 | 10.5701 | 10.6502 | 10.8472 | 10.7261 | 10.8004 | 10.7416 | 10.8624 | 10.8384 | 10.7451 | -0.13065 | 0.042587 | -0.10952 | -0.12468 | 0.089439 | 0.14683 | 10.5701 | 10.6502 | -0.22009 | -10.7007 | -0.19896 | -10.6796
1444.4531 | 122.6807 | -10.7895 | 111.9781 | 0.025705 | -0.095467 | -0.016578 | -0.084537 | 0.049999 | 0.016907 | -0.067295 | -0.1215 | 0.042587 | -0.11868 | -0.1201 | 0.080283 | 0.15598 | 10.5426 | 10.6273 | 10.8152 | 10.694 | 10.7729 | 10.705 | 10.8395 | 10.8064 | 10.7222 | -0.1215 | 0.042587 | -0.11868 | -0.1201 | 0.080283 | 0.15598 | 10.5426 | 10.6273 | -0.20178 | -10.6641 | -0.19896 | -10.6613
1446.2031 | 122.7676 | -10.675 | 111.9827 | 0.030283 | -0.090888 | -0.012 | -0.079959 | 0.045421 | 0.016907 | -0.076452 | -0.13065 | 0.042587 | -0.1141 | -0.12926 | 0.075705 | 0.15141 | 10.3778 | 10.4671 | 10.7053 | 10.5842 | 10.663 | 10.5951 | 10.7205 | 10.692 | 10.5986 | -0.13065 | 0.042587 | -0.1141 | -0.12926 | 0.075705 | 0.15141 | 10.3778 | 10.4671 | -0.20636 | -10.5084 | -0.1898 | -10.4919
1447.8906 | 122.6761 | -10.9726 | 111.7859 | 0.030283 | -0.086309 | -0.016578 | -0.07538 | 0.040843 | 0.012329 | -0.076452 | -0.1215 | 0.047165 | -0.10036 | -0.12468 | 0.084861 | 0.15141 | 10.5289 | 10.609 | 11.0029 | 10.8863 | 10.956 | 10.8972 | 11.0134 | 10.9849 | 10.8961 | -0.1215 | 0.047165 | -0.10036 | -0.12468 | 0.084861 | 0.15141 | 10.5289 | 10.609 | -0.20636 | -10.6504 | -0.18522 | -10.6292
1449.6406 | 122.818 | -10.7758 | 111.8317 | 0.021127 | -0.08173 | -0.012 | -0.07538 | 0.054577 | 0.012329 | -0.071874 | -0.13523 | 0.042587 | -0.10952 | -0.12468 | 0.080283 | 0.15141 | 10.5792 | 10.6685 | 10.7969 | 10.694 | 10.7638 | 10.7004 | 10.8303 | 10.7881 | 10.7039 | -0.13523 | 0.042587 | -0.10952 | -0.12468 | 0.080283 | 0.15141 | 10.5792 | 10.6685 | -0.21551 | -10.7144 | -0.1898 | -10.6887
1451.375 | 122.6852 | -10.611 | 112.0743 | 0.025705 | -0.10004 | -0.012 | -0.07538 | 0.040843 | 0.016907 | -0.076452 | -0.12607 | 0.051744 | -0.10952 | -0.12468 | 0.084861 | 0.15141 | 10.3183 | 10.4076 | 10.6367 | 10.5109 | 10.599 | 10.5356 | 10.6518 | 10.6279 | 10.5345 | -0.12607 | 0.051744 | -0.10952 | -0.12468 | 0.084861 | 0.15141 | 10.3183 | 10.4076 | -0.21093 | -10.4443 | -0.19438 | -10.4278
1453.1094 | 122.6761 | -10.5377 | 112.2162 | 0.030283 | -0.086309 | -0.016578 | -0.07538 | 0.054577 | 0.016907 | -0.08103 | -0.12607 | 0.047165 | -0.10952 | -0.12926 | 0.075705 | 0.15598 | 10.1809 | 10.2565 | 10.568 | 10.4514 | 10.5211 | 10.4623 | 10.5923 | 10.5546 | 10.4567 | -0.12607 | 0.047165 | -0.10952 | -0.12926 | 0.075705 | 0.15598 | 10.1809 | 10.2565 | -0.20178 | -10.307 | -0.18523 | -10.2904
1454.8594 | 122.7081 | -10.5103 | 112.2299 | 0.025705 | -0.086309 | -0.021157 | -0.079959 | 0.040843 | 0.016907 | -0.071874 | -0.13065 | 0.056323 | -0.10036 | -0.1201 | 0.084861 | 0.15141 | 10.1672 | 10.2565 | 10.536 | 10.4239 | 10.4891 | 10.4303 | 10.5511 | 10.5272 | 10.4384 | -0.13065 | 0.056323 | -0.10036 | -0.1201 | 0.084861 | 0.15141 | 10.1672 | 10.2565 | -0.21551 | -10.2978 | -0.18522 | -10.2675
1456.5312 | 122.8043 | -10.6293 | 112.0468 | 0.025705 | -0.095467 | -0.012 | -0.07538 | 0.040843 | 0.016907 | -0.076452 | -0.12607 | 0.056323 | -0.10952 | -0.12926 | 0.084861 | 0.14683 | 10.2725 | 10.3527 | 10.655 | 10.5338 | 10.6173 | 10.5539 | 10.6701 | 10.6462 | 10.5528 | -0.12607 | 0.056323 | -0.10952 | -0.12926 | 0.084861 | 0.14683 | 10.2725 | 10.3527 | -0.21093 | -10.3985 | -0.19438 | -10.382
1458.2812 | 122.6532 | -10.8536 | 111.882 | 0.025705 | -0.086309 | -0.016578 | -0.079959 | 0.036265 | 0.021485 | -0.076452 | -0.1215 | 0.047165 | -0.11868 | -0.12468 | 0.075705 | 0.15141 | 10.4236 | 10.5083 | 10.8793 | 10.7673 | 10.837 | 10.7736 | 10.8898 | 10.8751 | 10.7771 | -0.1215 | 0.047165 | -0.11868 | -0.12468 | 0.075705 | 0.15141 | 10.4236 | 10.5083 | -0.1972 | -10.545 | -0.19438 | -10.5422
1459.9531 | 122.6807 | -10.7712 | 111.9553 | 0.021127 | -0.095467 | -0.012 | -0.084537 | 0.049999 | 0.012329 | -0.076452 | -0.1215 | 0.047165 | -0.10952 | -0.1201 | 0.080283 | 0.15141 | 10.4144 | 10.49 | 10.7923 | 10.6757 | 10.7592 | 10.6866 | 10.8212 | 10.7835 | 10.6947 | -0.1215 | 0.047165 | -0.10952 | -0.1201 | 0.080283 | 0.15141 | 10.4144 | 10.49 | -0.20178 | -10.5359 | -0.1898 | -10.5239
1461.7031 | 122.8043 | -10.8398 | 111.8042 | 0.025705 | -0.090888 | -0.025735 | -0.079959 | 0.045421 | 0.012329 | -0.071874 | -0.13065 | 0.047165 | -0.10952 | -0.13384 | 0.080283 | 0.15598 | 10.4785 | 10.5587 | 10.8655 | 10.749 | 10.8141 | 10.7599 | 10.8853 | 10.8522 | 10.768 | -0.13065 | 0.047165 | -0.10952 | -0.13384 | 0.080283 | 0.15598 | 10.4785 | 10.5587 | -0.21093 | -10.6091 | -0.1898 | -10.588
1463.375 | 122.7127 | -10.6247 | 112.1155 | 0.025705 | -0.090888 | -0.016578 | -0.084537 | 0.049999 | 0.016907 | -0.067295 | -0.12607 | 0.047165 | -0.10494 | -0.12468 | 0.080283 | 0.15598 | 10.3595 | 10.4351 | 10.6504 | 10.5338 | 10.6081 | 10.5402 | 10.6747 | 10.6416 | 10.5574 | -0.12607 | 0.047165 | -0.10494 | -0.12468 | 0.080283 | 0.15598 | 10.3595 | 10.4351 | -0.20636 | -10.4855 | -0.18522 | -10.4644
1465.125 | 122.7814 | -10.8124 | 111.8774 | 0.025705 | -0.090888 | -0.016578 | -0.07538 | 0.040843 | 0.012329 | -0.085608 | -0.12607 | 0.047165 | -0.10952 | -0.12468 | 0.080283 | 0.15598 | 10.4007 | 10.4763 | 10.8381 | 10.7215 | 10.7958 | 10.737 | 10.8532 | 10.8247 | 10.7268 | -0.12607 | 0.047165 | -0.10952 | -0.12468 | 0.080283 | 0.15598 | 10.4007 | 10.4763 | -0.20636 | -10.5267 | -0.1898 | -10.5102
1466.875 | 122.6761 | -10.7254 | 112.0377 | 0.025705 | -0.090888 | -0.021157 | -0.07538 | 0.040843 | 0.026064 | -0.076452 | -0.12607 | 0.042587 | -0.10952 | -0.12468 | 0.075705 | 0.15141 | 10.4419 | 10.5266 | 10.7511 | 10.6345 | 10.7042 | 10.65 | 10.7662 | 10.7515 | 10.649 | -0.12607 | 0.042587 | -0.10952 | -0.12468 | 0.075705 | 0.15141 | 10.4419 | 10.5266 | -0.20178 | -10.5679 | -0.18523 | -10.5514
1468.5625 | 122.8134 | -10.3409 | 112.3306 | 0.025705 | -0.086309 | -0.025735 | -0.07538 | 0.045421 | 0.016907 | -0.076452 | -0.1215 | 0.038008 | -0.1141 | -0.12468 | 0.080283 | 0.15141 | 10.0802 | 10.1695 | 10.3666 | 10.2546 | 10.3151 | 10.2655 | 10.3863 | 10.3578 | 10.2644 | -0.1215 | 0.038008 | -0.1141 | -0.12468 | 0.080283 | 0.15141 | 10.0802 | 10.1695 | -0.20178 | -10.2017 | -0.19438 | -10.1943
1470.3125 | 122.8271 | -10.4416 | 112.2116 | 0.030283 | -0.095467 | -0.021157 | -0.079959 | 0.045421 | 0.016907 | -0.071874 | -0.13523 | 0.042587 | -0.11868 | -0.1201 | 0.084861 | 0.15141 | 10.0848 | 10.1695 | 10.4719 | 10.3461 | 10.4204 | 10.3616 | 10.487 | 10.4585 | 10.3697 | -0.13523 | 0.042587 | -0.11868 | -0.1201 | 0.084861 | 0.15141 | 10.0848 | 10.1695 | -0.22009 | -10.22 | -0.20354 | -10.2034
1472.0625 | 122.8134 | -10.3134 | 112.3489 | 0.025705 | -0.095467 | -0.016578 | -0.079959 | 0.040843 | 0.00775 | -0.071874 | -0.13065 | 0.047165 | -0.1141 | -0.1201 | 0.11691 | 0.17887 | 10.0344 | 10.1146 | 10.3391 | 10.2179 | 10.2968 | 10.2335 | 10.3543 | 10.3212 | 10.2415 | -0.13065 | 0.047165 | -0.1141 | -0.1201 | 0.11691 | 0.17887 | 10.0344 | 10.1146 | -0.24756 | -10.165 | -0.23101 | -10.1485
1473.75 | 122.7173 | -10.2859 | 112.4634 | 0.021127 | -0.090888 | -0.016578 | -0.079959 | 0.049999 | 0.021485 | -0.071874 | -0.1215 | 0.047165 | -0.10952 | -0.1201 | 0.10775 | 0.18345 | 9.9749 | 10.0642 | 10.3071 | 10.1951 | 10.2694 | 10.206 | 10.3359 | 10.3074 | 10.2141 | -0.1215 | 0.047165 | -0.10952 | -0.1201 | 0.10775 | 0.18345 | 9.9749 | 10.0642 | -0.22925 | -10.0964 | -0.21727 | -10.0844
1475.5156 | 122.6852 | -10.1257 | 112.6282 | 0.025705 | -0.090888 | -0.016578 | -0.07538 | 0.040843 | 0.021485 | -0.076452 | -0.13065 | 0.047165 | -0.11868 | -0.12926 | 0.089439 | 0.15598 | 9.8146 | 9.8903 | 10.1514 | 10.0348 | 10.1092 | 10.0504 | 10.1666 | 10.1472 | 10.0493 | -0.13065 | 0.047165 | -0.11868 | -0.12926 | 0.089439 | 0.15598 | 9.8146 | 9.8903 | -0.22009 | -9.9453 | -0.20811 | -9.9333
1477.2188 | 122.7356 | -10.0754 | 112.6328 | 0.021127 | -0.090888 | -0.016578 | -0.079959 | 0.045421 | 0.016907 | -0.071874 | -0.1215 | 0.042587 | -0.10952 | -0.12926 | 0.11233 | 0.1743 | 9.7414 | 9.8216 | 10.0965 | 9.9845 | 10.0588 | 9.9954 | 10.1208 | 10.0923 | 10.0035 | -0.1215 | 0.042587 | -0.10952 | -0.12926 | 0.11233 | 0.1743 | 9.7414 | 9.8216 | -0.23383 | -9.8629 | -0.22185 | -9.8509
1478.9844 | 122.6669 | -10.0983 | 112.6556 | 0.025705 | -0.090888 | -0.021157 | -0.079959 | 0.045421 | 0.016907 | -0.071874 | -0.1215 | 0.051744 | -0.10494 | -0.1201 | 0.089439 | 0.16056 | 9.6681 | 9.7575 | 10.124 | 10.0074 | 10.0771 | 10.0183 | 10.1437 | 10.1152 | 10.0264 | -0.1215 | 0.051744 | -0.10494 | -0.1201 | 0.089439 | 0.16056 | 9.6681 | 9.7575 | -0.21093 | -9.7896 | -0.19438 | -9.7731
1480.6562 | 122.699 | -10.1486 | 112.5778 | 0.030283 | -0.095467 | -0.016578 | -0.079959 | 0.045421 | 0.012329 | -0.071874 | -0.12607 | 0.047165 | -0.10952 | -0.1201 | 0.11233 | 0.16972 | 9.8925 | 9.9727 | 10.1789 | 10.0532 | 10.132 | 10.0687 | 10.194 | 10.1609 | 10.0767 | -0.12607 | 0.047165 | -0.10952 | -0.1201 | 0.11233 | 0.16972 | 9.8925 | 9.9727 | -0.2384 | -10.0185 | -0.22185 | -10.002
1482.4062 | 122.7036 | -10.0891 | 112.619 | 0.025705 | -0.090888 | -0.016578 | -0.093694 | 0.049999 | 0.021485 | -0.071874 | -0.13065 | 0.047165 | -0.10952 | -0.1201 | 0.11233 | 0.18803 | 9.8146 | 9.8903 | 10.1148 | 9.9982 | 10.0725 | 9.9954 | 10.1391 | 10.1106 | 10.0172 | -0.13065 | 0.047165 | -0.10952 | -0.1201 | 0.11233 | 0.18803 | 9.8146 | 9.8903 | -0.24298 | -9.9453 | -0.22185 | -9.9241
1484.0938 | 122.7081 | -10.2722 | 112.4313 | 0.025705 | -0.086309 | -0.016578 | -0.079959 | 0.036265 | 0.021485 | -0.071874 | -0.12607 | 0.051744 | -0.10494 | -0.1201 | 0.10775 | 0.17887 | 9.9108 | 9.991 | 10.2979 | 10.1859 | 10.2556 | 10.1923 | 10.3085 | 10.2937 | 10.2003 | -0.12607 | 0.051744 | -0.10494 | -0.1201 | 0.10775 | 0.17887 | 9.9108 | 9.991 | -0.23383 | -10.0368 | -0.21269 | -10.0157
1485.8281 | 122.6944 | -10.1578 | 112.5458 | 0.025705 | -0.10004 | -0.016578 | -0.07538 | 0.045421 | 0.012329 | -0.071874 | -0.13065 | 0.042587 | -0.1141 | -0.12468 | 0.11233 | 0.17887 | 9.8787 | 9.9544 | 10.1835 | 10.0577 | 10.1412 | 10.0824 | 10.2032 | 10.1701 | 10.0859 | -0.13065 | 0.042587 | -0.1141 | -0.12468 | 0.11233 | 0.17887 | 9.8787 | 9.9544 | -0.24298 | -10.0094 | -0.22643 | -9.9928
1487.5625 | 122.699 | -10.0708 | 112.5961 | 0.025705 | -0.086309 | -0.025735 | -0.089116 | 0.045421 | 0.012329 | -0.071874 | -0.13523 | 0.047165 | -0.10952 | -0.12926 | 0.10775 | 0.17887 | 9.778 | 9.8582 | 10.0965 | 9.9845 | 10.0451 | 9.9817 | 10.1162 | 10.0831 | 9.9989 | -0.13523 | 0.047165 | -0.10952 | -0.12926 | 0.10775 | 0.17887 | 9.778 | 9.8582 | -0.24298 | -9.9132 | -0.21727 | -9.8875
1489.2969 | 122.7905 | -10.0662 | 112.5641 | 0.021127 | -0.086309 | -0.021157 | -0.07538 | 0.045421 | 0.012329 | -0.076452 | -0.13065 | 0.042587 | -0.1141 | -0.12926 | 0.10775 | 0.17887 | 9.8055 | 9.8903 | 10.0874 | 9.9799 | 10.0451 | 9.9908 | 10.1116 | 10.0786 | 9.9898 | -0.13065 | 0.042587 | -0.1141 | -0.12926 | 0.10775 | 0.17887 | 9.8055 | 9.8903 | -0.2384 | -9.9361 | -0.22185 | -9.9196
1491.0469 | 122.6532 | -10.1578 | 112.5732 | 0.030283 | -0.090888 | -0.016578 | -0.084537 | 0.045421 | 0.021485 | -0.062717 | -0.12607 | 0.047165 | -0.10494 | -0.12468 | 0.10317 | 0.18345 | 9.8513 | 9.9406 | 10.1881 | 10.0669 | 10.1412 | 10.0732 | 10.2032 | 10.1793 | 10.0951 | -0.12607 | 0.047165 | -0.10494 | -0.12468 | 0.10317 | 0.18345 | 9.8513 | 9.9406 | -0.22925 | -9.9773 | -0.20812 | -9.9562
1492.7188 | 122.7356 | -10.2264 | 112.4176 | 0.025705 | -0.090888 | -0.012 | -0.07538 | 0.045421 | 0.012329 | -0.071874 | -0.13523 | 0.047165 | -0.11868 | -0.12926 | 0.10775 | 0.18345 | 9.9154 | 9.9818 | 10.2521 | 10.1356 | 10.2144 | 10.1511 | 10.2719 | 10.2388 | 10.1546 | -0.13523 | 0.047165 | -0.11868 | -0.12926 | 0.10775 | 0.18345 | 9.9154 | 9.9818 | -0.24298 | -10.0506 | -0.22643 | -10.034
1494.4688 | 122.7814 | -10.1074 | 112.5641 | 0.034862 | -0.095467 | -0.030314 | -0.070802 | 0.049999 | 0.016907 | -0.067295 | -0.1215 | 0.042587 | -0.1141 | -0.12468 | 0.10775 | 0.18803 | 9.7917 | 9.8719 | 10.1423 | 10.012 | 10.0771 | 10.0366 | 10.1574 | 10.1243 | 10.0401 | -0.1215 | 0.042587 | -0.1141 | -0.12468 | 0.10775 | 0.18803 | 9.7917 | 9.8719 | -0.22925 | -9.9132 | -0.22185 | -9.9058
1496.2188 | 122.731 | -10.1532 | 112.4817 | 0.021127 | -0.086309 | -0.021157 | -0.084537 | 0.049999 | 0.012329 | -0.071874 | -0.13065 | 0.042587 | -0.11868 | -0.1201 | 0.10775 | 0.18345 | 9.7414 | 9.8216 | 10.1743 | 10.0669 | 10.132 | 10.0687 | 10.2032 | 10.1655 | 10.0813 | -0.13065 | 0.042587 | -0.11868 | -0.1201 | 0.10775 | 0.18345 | 9.7414 | 9.8216 | -0.2384 | -9.872 | -0.22643 | -9.8601
1497.9062 | 122.6944 | -10.0937 | 112.5824 | 0.034862 | -0.090888 | -0.016578 | -0.079959 | 0.040843 | 0.016907 | -0.071874 | -0.1215 | 0.042587 | -0.1141 | -0.1201 | 0.11233 | 0.1743 | 9.7231 | 9.7987 | 10.1286 | 10.0028 | 10.0771 | 10.0137 | 10.1345 | 10.1106 | 10.0218 | -0.1215 | 0.042587 | -0.1141 | -0.1201 | 0.11233 | 0.1743 | 9.7231 | 9.7987 | -0.23383 | -9.8446 | -0.22643 | -9.8372
1499.6562 | 122.6624 | -10.1486 | 112.5504 | 0.021127 | -0.090888 | -0.012 | -0.07538 | 0.045421 | 0.016907 | -0.076452 | -0.13065 | 0.042587 | -0.095785 | -0.12468 | 0.10775 | 0.1743 | 9.7963 | 9.8765 | 10.1697 | 10.0577 | 10.1366 | 10.0732 | 10.194 | 10.1655 | 10.0722 | -0.13065 | 0.042587 | -0.095785 | -0.12468 | 0.10775 | 0.1743 | 9.7963 | 9.8765 | -0.2384 | -9.927 | -0.20354 | -9.8921
1501.4219 | 122.7081 | -13.4354 | 109.2316 | 0.025705 | -0.090888 | -0.021157 | -0.079959 | 0.045421 | 0.012329 | -0.067295 | -0.1215 | 0.047165 | -0.11868 | -0.12468 | 0.10775 | 0.1743 | 13.2164 | 13.3056 | 13.4611 | 13.3445 | 13.4142 | 13.3554 | 13.4808 | 13.4477 | 13.3681 | -0.1215 | 0.047165 | -0.11868 | -0.12468 | 0.10775 | 0.1743 | 13.2164 | 13.3056 | -0.22925 | -13.3379 | -0.22643 | -13.335
1503.1719 | 122.6944 | -12.3642 | 110.3119 | 0.025705 | -0.095467 | -0.021157 | -0.079959 | 0.049999 | 0.016907 | -0.071874 | -0.12607 | 0.051744 | -0.1141 | -0.13384 | 0.10775 | 0.1743 | 12.0443 | 12.1198 | 12.3899 | 12.2687 | 12.343 | 12.2842 | 12.4142 | 12.3811 | 12.2923 | -0.12607 | 0.051744 | -0.1141 | -0.13384 | 0.10775 | 0.1743 | 12.0443 | 12.1198 | -0.23383 | -12.1704 | -0.22185 | -12.1584
1504.9219 | 122.6761 | -8.9264 | 113.7588 | 0.030283 | -0.086309 | -0.016578 | -0.079959 | 0.054577 | 0.016907 | -0.076452 | -0.12607 | 0.051744 | -0.1141 | -0.12468 | 0.11233 | 0.1743 | 8.6151 | 8.6954 | 8.9567 | 8.8401 | 8.9098 | 8.8464 | 8.981 | 8.9433 | 8.8499 | -0.12607 | 0.051744 | -0.1141 | -0.12468 | 0.11233 | 0.1743 | 8.6151 | 8.6954 | -0.2384 | -8.7412 | -0.22643 | -8.7292
1506.6094 | 122.6257 | -8.9905 | 113.7085 | 0.030283 | -0.095467 | -0.016578 | -0.079959 | 0.045421 | 0.021485 | -0.067295 | -0.12607 | 0.051744 | -0.1141 | -0.1201 | 0.11233 | 0.17887 | 8.67 | 8.7503 | 9.0208 | 8.895 | 8.9739 | 8.9105 | 9.0359 | 9.012 | 8.9232 | -0.12607 | 0.051744 | -0.1141 | -0.1201 | 0.11233 | 0.17887 | 8.67 | 8.7503 | -0.2384 | -8.7961 | -0.22643 | -8.7841
1508.3438 | 122.6578 | -9.0866 | 113.5941 | 0.030283 | -0.090888 | -0.012 | -0.07538 | 0.049999 | 0.016907 | -0.071874 | -0.13065 | 0.056323 | -0.10952 | -0.1201 | 0.11233 | 0.17887 | 8.7616 | 8.8602 | 9.1169 | 8.9957 | 9.0746 | 9.0112 | 9.1366 | 9.1035 | 9.0147 | -0.13065 | 0.056323 | -0.10952 | -0.1201 | 0.11233 | 0.17887 | 8.7616 | 8.8602 | -0.24298 | -8.8923 | -0.22185 | -8.8711
1510.0781 | 122.644 | -9.1049 | 113.5986 | 0.025705 | -0.08173 | -0.016578 | -0.079959 | 0.045421 | 0.016907 | -0.067295 | -0.13065 | 0.051744 | -0.10494 | -0.12926 | 0.11233 | 0.18345 | 8.8349 | 8.9105 | 9.1306 | 9.0232 | 9.0883 | 9.025 | 9.1503 | 9.1218 | 9.0376 | -0.13065 | 0.051744 | -0.10494 | -0.12926 | 0.11233 | 0.18345 | 8.8349 | 8.9105 | -0.24298 | -8.9655 | -0.21727 | -8.9398
1511.8281 | 122.7173 | -8.9951 | 113.6719 | 0.030283 | -0.095467 | -0.016578 | -0.079959 | 0.045421 | 0.021485 | -0.076452 | -0.1215 | 0.051744 | -0.10952 | -0.12926 | 0.11233 | 0.17887 | 8.7341 | 8.7961 | 9.0253 | 8.8996 | 8.9785 | 8.9151 | 9.0405 | 9.0165 | 8.9186 | -0.1215 | 0.051744 | -0.10952 | -0.12926 | 0.11233 | 0.17887 | 8.7341 | 8.7961 | -0.23383 | -8.8556 | -0.22185 | -8.8436
1513.5156 | 122.6898 | -9.5489 | 113.1638 | 0.021127 | -0.095467 | -0.016578 | -0.084537 | 0.049999 | 0.016907 | -0.071874 | -0.12607 | 0.047165 | -0.10952 | -0.12468 | 0.10775 | 0.17887 | 9.1324 | 9.2081 | 9.5701 | 9.4535 | 9.5324 | 9.4644 | 9.5989 | 9.5659 | 9.4771 | -0.12607 | 0.047165 | -0.10952 | -0.12468 | 0.10775 | 0.17887 | 9.1324 | 9.2081 | -0.23383 | -9.2585 | -0.21727 | -9.242
1515.25 | 122.6898 | -12.2726 | 110.408 | 0.016548 | -0.086309 | -0.016578 | -0.079959 | 0.045421 | 0.021485 | -0.071874 | -0.12607 | 0.042587 | -0.10036 | -0.1201 | 0.11233 | 0.18345 | 12.0855 | 12.1793 | 12.2892 | 12.1863 | 12.2561 | 12.1927 | 12.3181 | 12.2941 | 12.2008 | -0.12607 | 0.042587 | -0.10036 | -0.1201 | 0.11233 | 0.18345 | 12.0855 | 12.1793 | -0.2384 | -12.2116 | -0.21269 | -12.1859
1517 | 122.6715 | -10.8353 | 111.8408 | 0.025705 | -0.090888 | -0.021157 | -0.084537 | 0.045421 | 0.016907 | -0.076452 | -0.13065 | 0.047165 | -0.10494 | -0.12468 | 0.10775 | 0.18345 | 10.5334 | 10.6228 | 10.861 | 10.7444 | 10.8141 | 10.7507 | 10.8807 | 10.8522 | 10.7588 | -0.13065 | 0.047165 | -0.10494 | -0.12468 | 0.10775 | 0.18345 | 10.5334 | 10.6228 | -0.2384 | -10.6641 | -0.21269 | -10.6384
1518.7344 | 122.7219 | -7.6538 | 115.0635 | 0.016548 | -0.086309 | -0.016578 | -0.079959 | 0.045421 | 0.012329 | -0.071874 | -0.12607 | 0.042587 | -0.11868 | -0.1201 | 0.11233 | 0.1743 | 7.324 | 7.3997 | 7.6704 | 7.5675 | 7.6372 | 7.5739 | 7.6992 | 7.6661 | 7.5819 | -0.12607 | 0.042587 | -0.11868 | -0.1201 | 0.11233 | 0.1743 | 7.324 | 7.3997 | -0.2384 | -7.4501 | -0.23101 | -7.4427
1520.4844 | 122.7173 | -7.5439 | 115.1184 | 0.025705 | -0.095467 | -0.012 | -0.084537 | 0.045421 | 0.012329 | -0.076452 | -0.12607 | 0.051744 | -0.10952 | -0.12468 | 0.098596 | 0.17887 | 7.3148 | 7.386 | 7.5697 | 7.4485 | 7.5319 | 7.4594 | 7.5894 | 7.5563 | 7.4675 | -0.12607 | 0.051744 | -0.10952 | -0.12468 | 0.098596 | 0.17887 | 7.3148 | 7.386 | -0.22467 | -7.4409 | -0.20812 | -7.4243
1522.1719 | 122.7219 | -9.1507 | 113.5071 | 0.021127 | -0.095467 | -0.021157 | -0.07538 | 0.040843 | 0.00775 | -0.067295 | -0.13523 | 0.042587 | -0.10952 | -0.1201 | 0.10775 | 0.18345 | 8.9264 | 9.0067 | 9.1718 | 9.0552 | 9.1295 | 9.0753 | 9.1915 | 9.1584 | 9.0834 | -0.13523 | 0.042587 | -0.10952 | -0.1201 | 0.10775 | 0.18345 | 8.9264 | 9.0067 | -0.24298 | -9.0617 | -0.21727 | -9.0359
1523.9062 | 122.7493 | -8.519 | 114.1479 | 0.025705 | -0.090888 | -0.021157 | -0.07538 | 0.031687 | 0.016907 | -0.071874 | -0.13065 | 0.051744 | -0.1141 | -0.12926 | 0.11233 | 0.18803 | 8.2626 | 8.352 | 8.5447 | 8.4281 | 8.4978 | 8.4436 | 8.5507 | 8.5359 | 8.4471 | -0.13065 | 0.051744 | -0.1141 | -0.12926 | 0.11233 | 0.18803 | 8.2626 | 8.352 | -0.24298 | -8.3932 | -0.22643 | -8.3767
1525.6562 | 122.6578 | -7.9514 | 114.8117 | 0.030283 | -0.095467 | -0.012 | -0.079959 | 0.045421 | 0.012329 | -0.067295 | -0.1215 | 0.051744 | -0.11868 | -0.12926 | 0.10317 | 0.18345 | 7.6307 | 7.7019 | 7.9816 | 7.8559 | 7.9394 | 7.8714 | 7.9968 | 7.9637 | 7.8841 | -0.1215 | 0.051744 | -0.11868 | -0.12926 | 0.10317 | 0.18345 | 7.6307 | 7.7019 | -0.22467 | -7.7522 | -0.22185 | -7.7494
1527.3438 | 122.6898 | -7.8369 | 114.8987 | 0.025705 | -0.086309 | -0.012 | -0.079959 | 0.040843 | 0.012329 | -0.076452 | -0.13065 | 0.056323 | -0.10952 | -0.12926 | 0.11691 | 0.18803 | 7.5025 | 7.5783 | 7.8626 | 7.7506 | 7.8249 | 7.757 | 7.8778 | 7.8492 | 7.7605 | -0.13065 | 0.056323 | -0.10952 | -0.12926 | 0.11691 | 0.18803 | 7.5025 | 7.5783 | -0.24756 | -7.6332 | -0.22643 | -7.6121
1529.0938 | 122.7676 | -7.6447 | 115.004 | 0.021127 | -0.095467 | -0.021157 | -0.079959 | 0.045421 | 0.021485 | -0.076452 | -0.13523 | 0.047165 | -0.1141 | -0.12468 | 0.11233 | 0.18345 | 7.4201 | 7.4867 | 7.6658 | 7.5492 | 7.6235 | 7.5647 | 7.6901 | 7.6661 | 7.5682 | -0.13523 | 0.047165 | -0.1141 | -0.12468 | 0.11233 | 0.18345 | 7.4201 | 7.4867 | -0.24756 | -7.5554 | -0.22643 | -7.5342
1530.7812 | 122.699 | -7.5943 | 115.1093 | 0.021127 | -0.095467 | -0.016578 | -0.07538 | 0.049999 | 0.012329 | -0.076452 | -0.13523 | 0.047165 | -0.10494 | -0.11552 | 0.10317 | 0.18345 | 7.269 | 7.354 | 7.6154 | 7.4988 | 7.5777 | 7.5189 | 7.6443 | 7.6066 | 7.5178 | -0.13523 | 0.047165 | -0.10494 | -0.11552 | 0.10317 | 0.18345 | 7.269 | 7.354 | -0.2384 | -7.4043 | -0.20812 | -7.374
1532.5312 | 122.7997 | -7.4844 | 115.1459 | 0.025705 | -0.090888 | -0.021157 | -0.084537 | 0.040843 | 0.012329 | -0.071874 | -0.12607 | 0.047165 | -0.10036 | -0.1201 | 0.11691 | 0.18345 | 7.2507 | 7.3219 | 7.5101 | 7.3935 | 7.4633 | 7.3999 | 7.5253 | 7.4968 | 7.4126 | -0.12607 | 0.047165 | -0.10036 | -0.1201 | 0.11691 | 0.18345 | 7.2507 | 7.3219 | -0.24298 | -7.3768 | -0.21727 | -7.3511
1534.2812 | 122.7814 | -7.5119 | 115.1001 | 0.016548 | -0.090888 | -0.025735 | -0.079959 | 0.045421 | 0.012329 | -0.071874 | -0.13065 | 0.051744 | -0.10952 | -0.12468 | 0.10775 | 0.18345 | 7.2324 | 7.3082 | 7.5285 | 7.421 | 7.4862 | 7.4319 | 7.5573 | 7.5242 | 7.44 | -0.13065 | 0.051744 | -0.10952 | -0.12468 | 0.10775 | 0.18345 | 7.2324 | 7.3082 | -0.2384 | -7.3631 | -0.21727 | -7.3419
1536.0469 | 122.7585 | -7.402 | 115.2649 | 0.030283 | -0.086309 | -0.012 | -0.079959 | 0.040843 | 0.016907 | -0.076452 | -0.1215 | 0.042587 | -0.11868 | -0.12468 | 0.10775 | 0.1743 | 7.15 | 7.2303 | 7.4323 | 7.3157 | 7.39 | 7.3221 | 7.4429 | 7.4189 | 7.3256 | -0.1215 | 0.042587 | -0.11868 | -0.12468 | 0.10775 | 0.1743 | 7.15 | 7.2303 | -0.22925 | -7.2715 | -0.22643 | -7.2687
1537.7344 | 122.6669 | -105.098 | 17.3904 | 0.053175 | -0.077151 | 0.001736 | -0.057066 | 0.06831 | 0.044377 | -0.058139 | -0.10318 | 0.097532 | -0.08205 | -0.143 | 0.3504 | 0.35284 | 105.5899 | 105.803 | 105.1511 | 105.0208 | 105.0997 | 105.0409 | 105.1663 | 105.1423 | 105.0398 | -0.10318 | 0.097532 | -0.08205 | -0.143 | 0.3504 | 0.35284 | 105.5899 | 105.803 | -0.45358 | -105.6931 | -0.43245 | -105.672
1539.4844 | 122.6898 | -122.1405 | 0.55847 | 0.048597 | -0.08173 | -0.007421 | -0.066223 | 0.063733 | 0.044377 | -0.058139 | -0.089445 | 0.10211 | -0.072894 | -0.15216 | 0.3275 | 0.38947 | 121.8569 | 121.9731 | 122.1891 | 122.0588 | 122.1331 | 122.0743 | 122.2042 | 122.1849 | 122.0824 | -0.089445 | 0.10211 | -0.072894 | -0.15216 | 0.3275 | 0.38947 | 121.8569 | 121.9731 | -0.41695 | -121.9464 | -0.4004 | -121.9298
1541.25 | 122.7768 | -122.1176 | 0.51727 | 0.044018 | -0.077151 | 0.001736 | -0.061645 | 0.06831 | 0.030642 | -0.053561 | -0.089445 | 0.11127 | -0.072894 | -0.143 | 0.31377 | 0.39862 | 121.9989 | 122.115 | 122.1616 | 122.0405 | 122.1194 | 122.056 | 122.1859 | 122.1483 | 122.0641 | -0.089445 | 0.11127 | -0.072894 | -0.143 | 0.31377 | 0.39862 | 121.9989 | 122.115 | -0.40321 | -122.0883 | -0.38666 | -122.0718
1543 | 122.5616 | -119.0964 | 3.5477 | 0.03944 | -0.072572 | -0.007421 | -0.061645 | 0.063733 | 0.035221 | -0.058139 | -0.057396 | 0.10669 | -0.08205 | -0.14758 | 0.25883 | 0.38489 | 119.142 | 119.272 | 119.1358 | 119.0238 | 119.089 | 119.0347 | 119.1601 | 119.1316 | 119.0382 | -0.057396 | 0.10669 | -0.08205 | -0.14758 | 0.25883 | 0.38489 | 119.142 | 119.272 | -0.31623 | -119.1993 | -0.34088 | -119.224
1544.6719 | 122.525 | -118.0161 | 4.3854 | 0.053175 | -0.067994 | 0.006315 | -0.052488 | 0.072888 | 0.044377 | -0.053561 | -0.094024 | 0.11585 | -0.068315 | -0.143 | 0.2451 | 0.36657 | 117.9745 | 118.2236 | 118.0692 | 117.9481 | 118.0224 | 117.9636 | 118.0889 | 118.0604 | 117.9625 | -0.094024 | 0.11585 | -0.068315 | -0.143 | 0.2451 | 0.36657 | 117.9745 | 118.2236 | -0.33912 | -118.0685 | -0.31341 | -118.0428
1546.4219 | 122.3282 | -118.0573 | 4.1519 | 0.048597 | -0.063415 | 0.006315 | -0.052488 | 0.072888 | 0.048956 | -0.053561 | -0.039082 | 0.12501 | -0.05458 | -0.14758 | 0.22678 | 0.35742 | 117.7593 | 118.0633 | 118.1058 | 117.9938 | 118.0636 | 118.0048 | 118.1301 | 118.1062 | 118.0037 | -0.039082 | 0.12501 | -0.05458 | -0.14758 | 0.22678 | 0.35742 | 117.7593 | 118.0633 | -0.26587 | -117.7984 | -0.28136 | -117.8139
1548.1562 | 122.1268 | -118.3411 | 3.7811 | 0.071489 | -0.063415 | 0.015472 | -0.038752 | 0.082044 | 0.058113 | -0.044405 | -0.084867 | 0.11585 | -0.059159 | -0.14758 | 0.25883 | 0.35284 | 118.2446 | 118.3975 | 118.4126 | 118.2776 | 118.3565 | 118.3023 | 118.4231 | 118.3992 | 118.2967 | -0.084867 | 0.11585 | -0.059159 | -0.14758 | 0.25883 | 0.35284 | 118.2446 | 118.3975 | -0.3437 | -118.3295 | -0.31799 | -118.3037
1549.8438 | 122.1634 | -118.4967 | 3.479 | 0.053175 | -0.058836 | 0.015472 | -0.047909 | 0.082044 | 0.053534 | -0.044405 | -0.061975 | 0.12501 | -0.05458 | -0.14758 | 0.24052 | 0.37573 | 118.2446 | 118.5532 | 118.5499 | 118.4379 | 118.5122 | 118.4488 | 118.5787 | 118.5502 | 118.4523 | -0.061975 | 0.12501 | -0.05458 | -0.14758 | 0.24052 | 0.37573 | 118.2446 | 118.5532 | -0.30249 | -118.3066 | -0.2951 | -118.2992
1551.5938 | 121.9757 | -118.6386 | 3.4287 | 0.06691 | -0.054257 | 0.015472 | -0.043331 | 0.077466 | 0.058113 | -0.039826 | 0.038752 | 0.17079 | 0.000359 | -0.14758 | 0.23594 | 0.362 | 118.3819 | 118.631 | 118.7055 | 118.5844 | 118.6541 | 118.5953 | 118.7161 | 118.6967 | 118.5988 | 0.038752 | 0.17079 | 0.000359 | -0.14758 | 0.23594 | 0.362 | 118.3819 | 118.631 | -0.19719 | -118.3432 | -0.23558 | -118.3816
1553.3594 | 122.0078 | -118.515 | 3.4882 | 0.048597 | -0.063415 | 0.010893 | -0.047909 | 0.077466 | 0.048956 | -0.048983 | -0.025347 | 0.12958 | -0.013376 | -0.143 | 0.22221 | 0.35284 | 118.2858 | 118.5944 | 118.5636 | 118.4516 | 118.5259 | 118.4671 | 118.5925 | 118.564 | 118.466 | -0.025347 | 0.12958 | -0.013376 | -0.143 | 0.22221 | 0.35284 | 118.2858 | 118.5944 | -0.24755 | -118.3111 | -0.23558 | -118.2992
1555.1094 | 122.081 | -118.5837 | 3.3371 | 0.053175 | -0.058836 | 0.015472 | -0.047909 | 0.082044 | 0.048956 | -0.044405 | 0.029595 | 0.1479 | -0.045424 | -0.14758 | 0.22678 | 0.34369 | 118.359 | 118.6265 | 118.6369 | 118.5248 | 118.5992 | 118.5358 | 118.6657 | 118.6326 | 118.5393 | 0.029595 | 0.1479 | -0.045424 | -0.14758 | 0.22678 | 0.34369 | 118.359 | 118.6265 | -0.19719 | -118.3295 | -0.27221 | -118.4045
1556.8125 | 122.0261 | -117.2745 | 4.5868 | 0.057754 | -0.063415 | 0.006315 | -0.052488 | 0.082044 | 0.053534 | -0.044405 | -0.084867 | 0.12958 | -0.059159 | -0.143 | 0.27714 | 0.34826 | 116.5048 | 116.6395 | 117.3322 | 117.2111 | 117.2808 | 117.222 | 117.3565 | 117.328 | 117.2301 | -0.084867 | 0.12958 | -0.059159 | -0.143 | 0.27714 | 0.34826 | 116.5048 | 116.6395 | -0.36201 | -116.5897 | -0.3363 | -116.564
1558.5625 | 122.0078 | -118.1717 | 3.6896 | 0.057754 | -0.063415 | 0.010893 | -0.043331 | 0.082044 | 0.048956 | -0.048983 | -0.071132 | 0.13416 | -0.050002 | -0.143 | 0.23136 | 0.35284 | 117.9149 | 118.2144 | 118.2294 | 118.1083 | 118.1826 | 118.1284 | 118.2537 | 118.2206 | 118.1227 | -0.071132 | 0.13416 | -0.050002 | -0.143 | 0.23136 | 0.35284 | 117.9149 | 118.2144 | -0.3025 | -117.9861 | -0.28137 | -117.9649
1560.3125 | 122.0123 | -118.0573 | 3.7399 | 0.057754 | -0.072572 | 0.010893 | -0.057066 | 0.06831 | 0.044377 | -0.044405 | 0.002124 | 0.13874 | -0.040846 | -0.15216 | 0.24052 | 0.36657 | 117.7867 | 118.1183 | 118.115 | 117.9847 | 118.0681 | 118.0002 | 118.1256 | 118.1016 | 118.0128 | 0.002124 | 0.13874 | -0.040846 | -0.15216 | 0.24052 | 0.36657 | 117.7867 | 118.1183 | -0.2384 | -117.7846 | -0.28137 | -117.8276
1562.0156 | 121.875 | -118.0573 | 3.804 | 0.044018 | -0.067994 | 0.006315 | -0.052488 | 0.06831 | 0.048956 | -0.053561 | -0.057396 | 0.12501 | -0.059159 | -0.13842 | 0.26341 | 0.37573 | 117.8646 | 118.0725 | 118.1013 | 117.9893 | 118.0636 | 118.0048 | 118.1256 | 118.1062 | 118.0037 | -0.057396 | 0.12501 | -0.059159 | -0.13842 | 0.26341 | 0.37573 | 117.8646 | 118.0725 | -0.32081 | -117.922 | -0.32257 | -117.9237
1563.7656 | 121.9162 | -118.2266 | 3.6072 | 0.044018 | -0.077151 | 0.001736 | -0.061645 | 0.063733 | 0.039799 | -0.048983 | -0.061975 | 0.11585 | -0.063737 | -0.15216 | 0.30919 | 0.38489 | 118.1255 | 118.2648 | 118.2706 | 118.1495 | 118.2284 | 118.165 | 118.2904 | 118.2664 | 118.1776 | -0.061975 | 0.11585 | -0.063737 | -0.15216 | 0.30919 | 0.38489 | 118.1255 | 118.2648 | -0.37117 | -118.1875 | -0.37293 | -118.1893
1565.5312 | 121.9894 | -2.0096 | 119.989 | 0.034862 | -0.10004 | -0.012 | -0.079959 | 0.045421 | 0.016907 | -0.067295 | -0.11692 | 0.060902 | -0.10036 | -0.13384 | 0.21305 | 0.16514 | 15.7207 | 16.0983 | 2.0444 | 1.9095 | 1.9976 | 1.9296 | 2.055 | 2.0265 | 1.9423 | -0.11692 | 0.060902 | -0.10036 | -0.13384 | 0.21305 | 0.16514 | 15.7207 | 16.0983 | -0.32997 | -15.8377 | -0.31341 | -15.8211
1567.2344 | 122.0535 | -2.3392 | 119.8151 | 0.016548 | -0.095467 | -0.021157 | -0.093694 | 0.045421 | 0.00775 | -0.076452 | -0.12607 | 0.056323 | -0.10494 | -0.1201 | 0.098596 | 0.15598 | 2.0634 | 2.1074 | 2.3557 | 2.2437 | 2.318 | 2.2455 | 2.3846 | 2.3469 | 2.2627 | -0.12607 | 0.056323 | -0.10494 | -0.1201 | 0.098596 | 0.15598 | 2.0634 | 2.1074 | -0.22467 | -2.1895 | -0.20354 | -2.1684
1569 | 122.1863 | -2.4719 | 119.6594 | 0.021127 | -0.10004 | -0.012 | -0.07538 | 0.045421 | 0.021485 | -0.071874 | -0.13981 | 0.042587 | -0.11868 | -0.1201 | 0.094017 | 0.16056 | 2.2008 | 2.2539 | 2.4931 | 2.3719 | 2.4599 | 2.3965 | 2.5173 | 2.4934 | 2.4001 | -0.13981 | 0.042587 | -0.11868 | -0.1201 | 0.094017 | 0.16056 | 2.2008 | 2.2539 | -0.23383 | -2.3406 | -0.21269 | -2.3194
1570.6719 | 122.2092 | -2.4948 | 119.6594 | 0.021127 | -0.10004 | -0.021157 | -0.07538 | 0.040843 | 0.016907 | -0.071874 | -0.12607 | 0.047165 | -0.1141 | -0.12468 | 0.098596 | 0.16514 | 2.2237 | 2.2813 | 2.5159 | 2.3948 | 2.4737 | 2.4194 | 2.5357 | 2.5117 | 2.4229 | -0.12607 | 0.047165 | -0.1141 | -0.12468 | 0.098596 | 0.16514 | 2.2237 | 2.2813 | -0.22467 | -2.3497 | -0.21269 | -2.3378
1572.4219 | 122.1954 | -2.5223 | 119.6274 | 0.021127 | -0.10004 | -0.030314 | -0.084537 | 0.040843 | 0.012329 | -0.071874 | -0.13523 | 0.033429 | -0.1141 | -0.12468 | 0.098596 | 0.16056 | 2.2328 | 2.2951 | 2.5434 | 2.4222 | 2.492 | 2.4377 | 2.5631 | 2.5346 | 2.4504 | -0.13523 | 0.033429 | -0.1141 | -0.12468 | 0.098596 | 0.16056 | 2.2328 | 2.2951 | -0.23383 | -2.368 | -0.21269 | -2.3469
1574.1562 | 122.2229 | -2.5177 | 119.6503 | 0.025705 | -0.095467 | -0.025735 | -0.07538 | 0.036265 | 0.00775 | -0.076452 | -0.12607 | 0.047165 | -0.10952 | -0.1201 | 0.098596 | 0.16514 | 2.2374 | 2.2951 | 2.5434 | 2.4222 | 2.492 | 2.4423 | 2.554 | 2.5255 | 2.4412 | -0.12607 | 0.047165 | -0.10952 | -0.1201 | 0.098596 | 0.16514 | 2.2374 | 2.2951 | -0.22467 | -2.3635 | -0.20812 | -2.3469
1575.8438 | 122.1863 | -2.449 | 119.7052 | 0.021127 | -0.10462 | -0.021157 | -0.089116 | 0.045421 | 0.012329 | -0.08103 | -0.13523 | 0.051744 | -0.1141 | -0.12468 | 0.094017 | 0.16514 | 2.1825 | 2.231 | 2.4702 | 2.3444 | 2.4279 | 2.3599 | 2.4945 | 2.4614 | 2.368 | -0.13523 | 0.051744 | -0.1141 | -0.12468 | 0.094017 | 0.16514 | 2.1825 | 2.231 | -0.22925 | -2.3177 | -0.20811 | -2.2966
1577.6094 | 122.168 | -2.4536 | 119.7601 | 0.021127 | -0.10004 | -0.021157 | -0.07538 | 0.045421 | 0.00775 | -0.076452 | -0.12607 | 0.051744 | -0.10036 | -0.12468 | 0.098596 | 0.16056 | 2.1779 | 2.2401 | 2.4747 | 2.3536 | 2.4325 | 2.3782 | 2.499 | 2.4614 | 2.3772 | -0.12607 | 0.051744 | -0.10036 | -0.12468 | 0.098596 | 0.16056 | 2.1779 | 2.2401 | -0.22467 | -2.3039 | -0.19896 | -2.2782
1579.2969 | 122.1725 | -2.4536 | 119.7693 | 0.021127 | -0.090888 | -0.021157 | -0.079959 | 0.040843 | 0.012329 | -0.071874 | -0.13065 | 0.047165 | -0.10494 | -0.1201 | 0.094017 | 0.15598 | 2.1412 | 2.2035 | 2.4747 | 2.3627 | 2.4325 | 2.3737 | 2.4945 | 2.4659 | 2.3817 | -0.13065 | 0.047165 | -0.10494 | -0.1201 | 0.094017 | 0.15598 | 2.1412 | 2.2035 | -0.22467 | -2.2719 | -0.19896 | -2.2462
1581.0312 | 122.2 | -2.4124 | 119.7739 | 0.021127 | -0.10462 | -0.025735 | -0.089116 | 0.040843 | 0.012329 | -0.076452 | -0.13065 | 0.042587 | -0.10952 | -0.12926 | 0.094017 | 0.16056 | 2.1184 | 2.176 | 2.4335 | 2.3078 | 2.3867 | 2.3233 | 2.4533 | 2.4247 | 2.336 | -0.13065 | 0.042587 | -0.10952 | -0.12926 | 0.094017 | 0.16056 | 2.1184 | 2.176 | -0.22467 | -2.249 | -0.20354 | -2.2279
1582.7812 | 122.2504 | -2.3712 | 119.7739 | 0.030283 | -0.10462 | -0.021157 | -0.089116 | 0.040843 | 0.012329 | -0.076452 | -0.1215 | 0.051744 | -0.1141 | -0.11552 | 0.089439 | 0.16056 | 2.1046 | 2.1531 | 2.4015 | 2.2666 | 2.3501 | 2.2821 | 2.4121 | 2.3835 | 2.2948 | -0.1215 | 0.051744 | -0.1141 | -0.11552 | 0.089439 | 0.16056 | 2.1046 | 2.1531 | -0.21093 | -2.2261 | -0.20354 | -2.2187
1584.4844 | 122.2092 | -2.3712 | 119.8013 | 0.021127 | -0.10462 | -0.016578 | -0.079959 | 0.040843 | 0.00775 | -0.076452 | -0.13523 | 0.042587 | -0.10952 | -0.1201 | 0.098596 | 0.16514 | 2.0817 | 2.1303 | 2.3923 | 2.2666 | 2.3546 | 2.2913 | 2.4121 | 2.379 | 2.2948 | -0.13523 | 0.042587 | -0.10952 | -0.1201 | 0.098596 | 0.16514 | 2.0817 | 2.1303 | -0.23383 | -2.217 | -0.20812 | -2.1913
1586.25 | 122.2046 | -2.3987 | 119.7693 | 0.021127 | -0.10004 | -0.030314 | -0.084537 | 0.040843 | 0.00775 | -0.071874 | -0.13981 | 0.042587 | -0.10494 | -0.12468 | 0.084861 | 0.16056 | 2.1046 | 2.1577 | 2.4198 | 2.2986 | 2.3684 | 2.3141 | 2.4395 | 2.4064 | 2.3268 | -0.13981 | 0.042587 | -0.10494 | -0.12468 | 0.084861 | 0.16056 | 2.1046 | 2.1577 | -0.22467 | -2.2444 | -0.1898 | -2.2096
1588 | 122.1268 | -2.4307 | 119.7922 | 0.021127 | -0.095467 | -0.016578 | -0.079959 | 0.040843 | 0.012329 | -0.067295 | -0.1215 | 0.056323 | -0.1141 | -0.1201 | 0.089439 | 0.15598 | 2.1092 | 2.1531 | 2.4519 | 2.3353 | 2.4141 | 2.3508 | 2.4716 | 2.4431 | 2.3634 | -0.1215 | 0.056323 | -0.1141 | -0.1201 | 0.089439 | 0.15598 | 2.1092 | 2.1531 | -0.21093 | -2.2307 | -0.20354 | -2.2233
1589.6875 | 122.2641 | -2.3712 | 119.7968 | 0.016548 | -0.095467 | -0.021157 | -0.079959 | 0.036265 | 0.003172 | -0.076452 | -0.1215 | 0.047165 | -0.10494 | -0.12468 | 0.089439 | 0.16056 | 2.1046 | 2.1669 | 2.3878 | 2.2757 | 2.3501 | 2.2913 | 2.4075 | 2.3744 | 2.2948 | -0.1215 | 0.047165 | -0.10494 | -0.12468 | 0.089439 | 0.16056 | 2.1046 | 2.1669 | -0.21093 | -2.2261 | -0.19438 | -2.2096
1591.4375 | 122.1725 | -2.4765 | 119.7601 | 0.021127 | -0.10462 | -0.025735 | -0.084537 | 0.040843 | 0.016907 | -0.08103 | -0.12607 | 0.047165 | -0.10952 | -0.12468 | 0.084861 | 0.15598 | 2.155 | 2.2081 | 2.4976 | 2.3719 | 2.4508 | 2.392 | 2.5173 | 2.4934 | 2.3955 | -0.12607 | 0.047165 | -0.10952 | -0.12468 | 0.084861 | 0.15598 | 2.155 | 2.2081 | -0.21093 | -2.2811 | -0.19438 | -2.2645
1593.1875 | 122.2366 | -2.4353 | 119.7372 | 0.021127 | -0.10004 | -0.021157 | -0.07538 | 0.036265 | 0.016907 | -0.076452 | -0.1215 | 0.042587 | -0.1141 | -0.1201 | 0.084861 | 0.15598 | 2.155 | 2.2035 | 2.4564 | 2.3353 | 2.4141 | 2.3599 | 2.4716 | 2.4522 | 2.3589 | -0.1215 | 0.042587 | -0.1141 | -0.1201 | 0.084861 | 0.15598 | 2.155 | 2.2035 | -0.20636 | -2.2765 | -0.19896 | -2.2691
1594.9219 | 122.1909 | -2.4445 | 119.7922 | 0.021127 | -0.095467 | -0.016578 | -0.089116 | 0.045421 | 0.012329 | -0.071874 | -0.13065 | 0.042587 | -0.10494 | -0.12926 | 0.094017 | 0.15141 | 2.1275 | 2.1852 | 2.4656 | 2.349 | 2.4279 | 2.3553 | 2.4899 | 2.4568 | 2.3726 | -0.13065 | 0.042587 | -0.10494 | -0.12926 | 0.094017 | 0.15141 | 2.1275 | 2.1852 | -0.22467 | -2.2582 | -0.19896 | -2.2325
1596.6875 | 122.1771 | -2.4628 | 119.7601 | 0.021127 | -0.10004 | -0.025735 | -0.084537 | 0.045421 | 0.012329 | -0.076452 | -0.1215 | 0.047165 | -0.1141 | -0.1201 | 0.080283 | 0.15598 | 2.1641 | 2.2218 | 2.4839 | 2.3627 | 2.437 | 2.3782 | 2.5082 | 2.4751 | 2.3863 | -0.1215 | 0.047165 | -0.1141 | -0.1201 | 0.080283 | 0.15598 | 2.1641 | 2.2218 | -0.20178 | -2.2856 | -0.19438 | -2.2782
1598.375 | 122.2458 | -2.4078 | 119.8105 | 0.025705 | -0.10004 | -0.021157 | -0.089116 | 0.036265 | 0.012329 | -0.076452 | -0.12607 | 0.051744 | -0.1141 | -0.1201 | 0.089439 | 0.15598 | 2.1275 | 2.1852 | 2.4335 | 2.3078 | 2.3867 | 2.3187 | 2.4441 | 2.4202 | 2.3314 | -0.12607 | 0.051744 | -0.1141 | -0.1201 | 0.089439 | 0.15598 | 2.1275 | 2.1852 | -0.21551 | -2.2536 | -0.20354 | -2.2416
1600.1094 | 122.1863 | -2.4399 | 119.8288 | 0.01197 | -0.095467 | -0.021157 | -0.079959 | 0.049999 | 0.012329 | -0.076452 | -0.12607 | 0.047165 | -0.1141 | -0.1201 | 0.094017 | 0.16514 | 2.1275 | 2.1806 | 2.4518 | 2.3444 | 2.4187 | 2.3599 | 2.4899 | 2.4522 | 2.3634 | -0.12607 | 0.047165 | -0.1141 | -0.1201 | 0.094017 | 0.16514 | 2.1275 | 2.1806 | -0.22009 | -2.2536 | -0.20811 | -2.2416
1601.875 | 122.1405 | -2.4445 | 119.8151 | 0.025705 | -0.1092 | -0.025735 | -0.089116 | 0.049999 | 0.021485 | -0.076452 | -0.13523 | 0.047165 | -0.10494 | -0.1201 | 0.089439 | 0.15598 | 2.1184 | 2.1715 | 2.4702 | 2.3353 | 2.4187 | 2.3553 | 2.4945 | 2.4659 | 2.368 | -0.13523 | 0.047165 | -0.10494 | -0.1201 | 0.089439 | 0.15598 | 2.1184 | 2.1715 | -0.22467 | -2.2536 | -0.19438 | -2.2233
1603.5625 | 122.0856 | -68.4998 | 53.7598 | 0.021127 | -0.10004 | -0.016578 | -0.079959 | 0.054577 | 0.012329 | -0.067295 | -0.11234 | 0.074638 | -0.10036 | -0.12926 | 0.2451 | 0.27959 | 48.8591 | 48.9329 | 68.5209 | 68.3997 | 68.4832 | 68.4198 | 68.5543 | 68.5121 | 68.4325 | -0.11234 | 0.074638 | -0.10036 | -0.12926 | 0.2451 | 0.27959 | 48.8591 | 48.9329 | -0.35744 | -48.9715 | -0.34546 | -48.9595
1605.3125 | 121.9986 | -111.2823 | 10.4416 | 0.025705 | -0.090888 | -0.012 | -0.079959 | 0.063733 | 0.030642 | -0.071874 | -0.10776 | 0.092954 | -0.095785 | -0.13842 | 0.37329 | 0.34826 | 80.0013 | 79.9455 | 111.3081 | 111.1915 | 111.2703 | 111.2024 | 111.3461 | 111.313 | 111.2105 | -0.10776 | 0.092954 | -0.095785 | -0.13842 | 0.37329 | 0.34826 | 80.0013 | 79.9455 | -0.48105 | -80.1091 | -0.46907 | -80.0971
1607.0781 | 122.1039 | -0.74158 | 120.6894 | 0.021127 | -0.10004 | -0.012 | -0.07538 | 0.045421 | 0.016907 | -0.076452 | -0.13523 | 0.047165 | -0.10494 | -0.12468 | 0.19931 | 0.15141 | 0.66243 | 0.70187 | 0.7627 | 0.64153 | 0.72958 | 0.6662 | 0.787 | 0.75848 | 0.66513 | -0.13523 | 0.047165 | -0.10494 | -0.12468 | 0.19931 | 0.15141 | 0.66243 | 0.70187 | -0.33454 | -0.79766 | -0.30426 | -0.76737
1608.8281 | 122.1588 | -0.79651 | 121.2936 | 0.025705 | -0.095467 | -0.016578 | -0.079959 | 0.045421 | 0.016907 | -0.076452 | -0.12607 | 0.047165 | -0.10952 | -0.12926 | 0.080283 | 0.14683 | 0.52508 | 0.76138 | 0.82221 | 0.70104 | 0.77993 | 0.71655 | 0.84193 | 0.81342 | 0.72006 | -0.12607 | 0.047165 | -0.10952 | -0.12926 | 0.080283 | 0.14683 | 0.52508 | 0.76138 | -0.20636 | -0.65115 | -0.1898 | -0.6346
1610.5156 | 122.0261 | -0.88806 | 121.3074 | 0.030283 | -0.095467 | -0.012 | -0.07538 | 0.049999 | 0.016907 | -0.062717 | -0.12607 | 0.051744 | -0.10952 | -0.12926 | 0.089439 | 0.15598 | 0.54339 | 0.58741 | 0.91834 | 0.7926 | 0.87606 | 0.81268 | 0.93806 | 0.90497 | 0.82534 | -0.12607 | 0.051744 | -0.10952 | -0.12926 | 0.089439 | 0.15598 | 0.54339 | 0.58741 | -0.21551 | -0.66946 | -0.19896 | -0.65291
1612.2812 | 122.1268 | -0.83313 | 121.2845 | 0.034862 | -0.095467 | -0.016578 | -0.07538 | 0.045421 | 0.021485 | -0.067295 | -0.12607 | 0.047165 | -0.1141 | -0.12468 | 0.084861 | 0.14225 | 0.54339 | 0.59657 | 0.86799 | 0.73766 | 0.81655 | 0.75775 | 0.87855 | 0.85462 | 0.76584 | -0.12607 | 0.047165 | -0.1141 | -0.12468 | 0.084861 | 0.14225 | 0.54339 | 0.59657 | -0.21093 | -0.66946 | -0.19896 | -0.65749
1614.0312 | 122.1359 | -0.87891 | 121.2799 | 0.025705 | -0.10462 | -0.012 | -0.079959 | 0.045421 | 0.012329 | -0.071874 | -0.13981 | 0.047165 | -0.1141 | -0.13384 | 0.089439 | 0.15141 | 0.56628 | 0.61488 | 0.90461 | 0.77428 | 0.86691 | 0.79895 | 0.92433 | 0.89123 | 0.80703 | -0.13981 | 0.047165 | -0.1141 | -0.13384 | 0.089439 | 0.15141 | 0.56628 | 0.61488 | -0.22925 | -0.70609 | -0.20354 | -0.68038
1615.7188 | 122.113 | -0.86517 | 121.3074 | 0.030283 | -0.10004 | -0.012 | -0.070802 | 0.049999 | 0.021485 | -0.071874 | -0.12607 | 0.047165 | -0.10494 | -0.12926 | 0.075705 | 0.15141 | 0.56171 | 0.60572 | 0.89546 | 0.76513 | 0.85317 | 0.79437 | 0.91517 | 0.88666 | 0.7933 | -0.12607 | 0.047165 | -0.10494 | -0.12926 | 0.075705 | 0.15141 | 0.56171 | 0.60572 | -0.20178 | -0.68778 | -0.18065 | -0.66665
1617.5 | 122.0947 | -0.85144 | 121.3486 | 0.021127 | -0.10004 | -0.007421 | -0.07538 | 0.049999 | 0.026064 | -0.067295 | -0.12607 | 0.056323 | -0.1141 | -0.1201 | 0.084861 | 0.15598 | 0.53424 | 0.58283 | 0.87257 | 0.7514 | 0.84402 | 0.77606 | 0.90144 | 0.8775 | 0.78414 | -0.12607 | 0.056323 | -0.1141 | -0.1201 | 0.084861 | 0.15598 | 0.53424 | 0.58283 | -0.21093 | -0.66031 | -0.19896 | -0.64833
1619.2031 | 122.0947 | -0.85144 | 121.3394 | 0.034862 | -0.095467 | -0.012 | -0.066223 | 0.049999 | 0.016907 | -0.071874 | -0.1215 | 0.047165 | -0.10494 | -0.13384 | 0.080283 | 0.15141 | 0.54339 | 0.58283 | 0.8863 | 0.75597 | 0.83944 | 0.78522 | 0.90144 | 0.86835 | 0.77957 | -0.1215 | 0.047165 | -0.10494 | -0.13384 | 0.080283 | 0.15141 | 0.54339 | 0.58283 | -0.20178 | -0.66489 | -0.18522 | -0.64833
1620.9375 | 122.1954 | -0.82855 | 121.2891 | 0.021127 | -0.10004 | -0.016578 | -0.070802 | 0.045421 | 0.00775 | -0.067295 | -0.13065 | 0.051744 | -0.1141 | -0.12468 | 0.071126 | 0.15141 | 0.54339 | 0.58741 | 0.84968 | 0.72851 | 0.81197 | 0.75775 | 0.87397 | 0.8363 | 0.76126 | -0.13065 | 0.051744 | -0.1141 | -0.12468 | 0.071126 | 0.15141 | 0.54339 | 0.58741 | -0.20178 | -0.67404 | -0.18522 | -0.65749
1622.625 | 122.1497 | -0.84228 | 121.2936 | 0.030283 | -0.10004 | -0.016578 | -0.066223 | 0.049999 | 0.016907 | -0.067295 | -0.13065 | 0.047165 | -0.10494 | -0.12468 | 0.084861 | 0.16056 | 0.55255 | 0.59657 | 0.87257 | 0.74224 | 0.82571 | 0.77606 | 0.89228 | 0.85919 | 0.77499 | -0.13065 | 0.047165 | -0.10494 | -0.12468 | 0.084861 | 0.16056 | 0.55255 | 0.59657 | -0.21551 | -0.6832 | -0.1898 | -0.65749
1624.3906 | 122.081 | -0.87891 | 121.3303 | 0.030283 | -0.10004 | -0.021157 | -0.079959 | 0.045421 | 0.016907 | -0.076452 | -0.12607 | 0.047165 | -0.10952 | -0.1201 | 0.075705 | 0.15141 | 0.55255 | 0.59199 | 0.90919 | 0.77886 | 0.85775 | 0.79895 | 0.92433 | 0.89581 | 0.80245 | -0.12607 | 0.047165 | -0.10952 | -0.1201 | 0.075705 | 0.15141 | 0.55255 | 0.59199 | -0.20178 | -0.67862 | -0.18523 | -0.66207
1626.125 | 122.1405 | -0.82855 | 121.3028 | 0.025705 | -0.10004 | -0.012 | -0.070802 | 0.045421 | 0.016907 | -0.067295 | -0.11692 | 0.042587 | -0.10952 | -0.1201 | 0.075705 | 0.14683 | 0.55255 | 0.60115 | 0.85426 | 0.72851 | 0.81655 | 0.75775 | 0.87397 | 0.84546 | 0.76126 | -0.11692 | 0.042587 | -0.10952 | -0.1201 | 0.075705 | 0.14683 | 0.55255 | 0.60115 | -0.19262 | -0.66946 | -0.18523 | -0.66207
1627.875 | 122.1405 | -0.83771 | 121.2799 | 0.021127 | -0.095467 | -0.016578 | -0.079959 | 0.054577 | 0.00775 | -0.071874 | -0.13065 | 0.042587 | -0.1141 | -0.12468 | 0.071126 | 0.15141 | 0.56171 | 0.60572 | 0.85884 | 0.74224 | 0.82113 | 0.75775 | 0.89228 | 0.84546 | 0.76583 | -0.13065 | 0.042587 | -0.1141 | -0.12468 | 0.071126 | 0.15141 | 0.56171 | 0.60572 | -0.20178 | -0.69236 | -0.18522 | -0.6758
1629.625 | 122.1405 | -0.88806 | 121.2662 | 0.016548 | -0.10004 | -0.016578 | -0.07538 | 0.045421 | 0.016907 | -0.076452 | -0.13065 | 0.047165 | -0.1141 | -0.12468 | 0.075705 | 0.15141 | 0.58918 | 0.63319 | 0.90461 | 0.78802 | 0.87148 | 0.81268 | 0.93348 | 0.90497 | 0.81161 | -0.13065 | 0.047165 | -0.1141 | -0.12468 | 0.075705 | 0.15141 | 0.58918 | 0.63319 | -0.20636 | -0.71983 | -0.1898 | -0.70327
1631.3125 | 122.113 | -0.89722 | 121.2845 | 0.025705 | -0.10004 | -0.016578 | -0.070802 | 0.049999 | 0.021485 | -0.067295 | -0.13065 | 0.051744 | -0.095785 | -0.12926 | 0.075705 | 0.15141 | 0.5846 | 0.62862 | 0.92292 | 0.79717 | 0.88064 | 0.82642 | 0.94722 | 0.9187 | 0.82992 | -0.13065 | 0.051744 | -0.095785 | -0.12926 | 0.075705 | 0.15141 | 0.5846 | 0.62862 | -0.20636 | -0.71525 | -0.17149 | -0.68038
1633.0781 | 122.1405 | -0.88348 | 121.2753 | 0.030283 | -0.095467 | -0.025735 | -0.070802 | 0.049999 | 0.012329 | -0.076452 | -0.12607 | 0.051744 | -0.10952 | -0.12468 | 0.075705 | 0.15141 | 0.57544 | 0.62862 | 0.91377 | 0.78802 | 0.85775 | 0.81268 | 0.93348 | 0.89581 | 0.80703 | -0.12607 | 0.051744 | -0.10952 | -0.12468 | 0.075705 | 0.15141 | 0.57544 | 0.62862 | -0.20178 | -0.70151 | -0.18523 | -0.68496
1634.7656 | 122.0673 | -0.92468 | 121.2708 | 0.021127 | -0.1092 | -0.016578 | -0.07538 | 0.049999 | 0.016907 | -0.071874 | -0.1215 | 0.056323 | -0.11868 | -0.12926 | 0.075705 | 0.14683 | 0.59833 | 0.64693 | 0.94581 | 0.81548 | 0.90811 | 0.8493 | 0.97468 | 0.94159 | 0.85281 | -0.1215 | 0.056323 | -0.11868 | -0.12926 | 0.075705 | 0.14683 | 0.59833 | 0.64693 | -0.1972 | -0.71983 | -0.19438 | -0.71701
1636.5156 | 122.1405 | -0.88348 | 121.2341 | 0.016548 | -0.10462 | -0.016578 | -0.07538 | 0.045421 | 0.012329 | -0.067295 | -0.12607 | 0.051744 | -0.1141 | -0.13384 | 0.080283 | 0.14225 | 0.60749 | 0.66066 | 0.90003 | 0.77886 | 0.86691 | 0.8081 | 0.92891 | 0.89581 | 0.81619 | -0.12607 | 0.051744 | -0.1141 | -0.13384 | 0.080283 | 0.14225 | 0.60749 | 0.66066 | -0.20636 | -0.73356 | -0.19438 | -0.72159
1638.2031 | 122.2183 | -0.89264 | 121.2387 | 0.021127 | -0.10004 | -0.016578 | -0.066223 | 0.049999 | 0.016907 | -0.062717 | -0.13523 | 0.051744 | -0.10494 | -0.12468 | 0.071126 | 0.14683 | 0.61207 | 0.66524 | 0.91377 | 0.79259 | 0.87606 | 0.82642 | 0.94264 | 0.90955 | 0.82992 | -0.13523 | 0.051744 | -0.10494 | -0.12468 | 0.071126 | 0.14683 | 0.61207 | 0.66524 | -0.20636 | -0.7473 | -0.17607 | -0.71701
1639.9531 | 122.1771 | -1.0483 | 121.1975 | 0.025705 | -0.095467 | -0.016578 | -0.07538 | 0.045421 | 0.021485 | -0.071874 | -0.12607 | 0.060902 | -0.10494 | -0.11552 | 0.075705 | 0.14683 | 0.71279 | 0.76596 | 1.074 | 0.95281 | 1.0317 | 0.9729 | 1.0937 | 1.0698 | 0.9764 | -0.12607 | 0.060902 | -0.10494 | -0.11552 | 0.075705 | 0.14683 | 0.71279 | 0.76596 | -0.20178 | -0.83887 | -0.18065 | -0.81773
1641.7031 | 122.168 | -0.93384 | 121.3211 | 0.030283 | -0.090888 | -0.012 | -0.07538 | 0.049999 | 0.021485 | -0.067295 | -0.1215 | 0.051744 | -0.10952 | -0.1201 | 0.075705 | 0.15141 | 0.61207 | 0.66066 | 0.96412 | 0.84295 | 0.92184 | 0.85846 | 0.98384 | 0.95532 | 0.86654 | -0.1215 | 0.051744 | -0.10952 | -0.1201 | 0.075705 | 0.15141 | 0.61207 | 0.66066 | -0.1972 | -0.73356 | -0.18523 | -0.72159
1643.3906 | 122.1863 | -1.236 | 121.0373 | 0.025705 | -0.095467 | -0.021157 | -0.07538 | 0.049999 | 0.016907 | -0.067295 | -0.11234 | 0.065481 | -0.10952 | -0.12926 | 0.089439 | 0.15141 | 0.90966 | 0.95825 | 1.2617 | 1.1405 | 1.2148 | 1.1606 | 1.286 | 1.2529 | 1.1687 | -0.11234 | 0.065481 | -0.10952 | -0.12926 | 0.089439 | 0.15141 | 0.90966 | 0.95825 | -0.20178 | -1.022 | -0.19896 | -1.0192
1645.1406 | 122.1909 | -0.94299 | 121.3623 | 0.021127 | -0.095467 | -0.016578 | -0.079959 | 0.045421 | 0.012329 | -0.071874 | -0.13523 | 0.051744 | -0.10494 | -0.13384 | 0.071126 | 0.14225 | 0.60291 | 0.65151 | 0.96412 | 0.84753 | 0.92641 | 0.86303 | 0.98841 | 0.95532 | 0.87112 | -0.13523 | 0.051744 | -0.10494 | -0.13384 | 0.071126 | 0.14225 | 0.60291 | 0.65151 | -0.20636 | -0.73814 | -0.17607 | -0.70785
1646.8906 | 122.1634 | -1.2222 | 121.0876 | 0.025705 | -0.090888 | -0.007421 | -0.07538 | 0.049999 | 0.016907 | -0.067295 | -0.12607 | 0.047165 | -0.10036 | -0.12468 | 0.080283 | 0.13767 | 0.94171 | 0.98571 | 1.2479 | 1.1313 | 1.2148 | 1.1468 | 1.2722 | 1.2391 | 1.1549 | -0.12607 | 0.047165 | -0.10036 | -0.12468 | 0.080283 | 0.13767 | 0.94171 | 0.98571 | -0.20636 | -1.0678 | -0.18065 | -1.0421
1648.5781 | 122.2046 | -0.95215 | 121.3898 | 0.021127 | -0.095467 | -0.012 | -0.07538 | 0.054577 | 0.012329 | -0.071874 | -0.13065 | 0.056323 | -0.10952 | -0.12926 | 0.075705 | 0.14225 | 1.1294 | 1.1826 | 0.97328 | 0.85668 | 0.94015 | 0.87677 | 1.0067 | 0.96448 | 0.88027 | -0.13065 | 0.056323 | -0.10952 | -0.12926 | 0.075705 | 0.14225 | 1.1294 | 1.1826 | -0.20636 | -1.2601 | -0.18523 | -1.2389
1650.3125 | 122.3373 | -0.97046 | 121.2433 | 0.021127 | -0.095467 | -0.012 | -0.07538 | 0.045421 | 0.016907 | -0.071874 | -0.12607 | 0.051744 | -0.10494 | -0.12468 | 0.080283 | 0.14225 | 1.4453 | 1.4939 | 0.99159 | 0.87499 | 0.95846 | 0.89508 | 1.0159 | 0.98737 | 0.89858 | -0.12607 | 0.051744 | -0.10494 | -0.12468 | 0.080283 | 0.14225 | 1.4453 | 1.4939 | -0.20636 | -1.5714 | -0.18522 | -1.5503
1652 | 122.3373 | -1.2863 | 121.0007 | 0.025705 | -0.095467 | -0.021157 | -0.079959 | 0.049999 | 0.016907 | -0.067295 | -0.12607 | 0.047165 | -0.10952 | -0.12926 | 0.080283 | 0.15141 | 0.91882 | 0.99945 | 1.312 | 1.1908 | 1.2652 | 1.2064 | 1.3363 | 1.3032 | 1.219 | -0.12607 | 0.047165 | -0.10952 | -0.12926 | 0.080283 | 0.15141 | 0.91882 | 0.99945 | -0.20636 | -1.0449 | -0.1898 | -1.0283
1653.75 | 122.2229 | -2.1927 | 120.1263 | 0.021127 | -0.095467 | -0.012 | -0.07538 | 0.054577 | 0.021485 | -0.067295 | -0.13065 | 0.056323 | -0.10494 | -0.12926 | 0.075705 | 0.15141 | 1.8253 | 1.8876 | 2.2138 | 2.0972 | 2.1807 | 2.1173 | 2.2473 | 2.2142 | 2.1254 | -0.13065 | 0.056323 | -0.10494 | -0.12926 | 0.075705 | 0.15141 | 1.8253 | 1.8876 | -0.20636 | -1.956 | -0.18065 | -1.9303
1655.5 | 122.3099 | -1.1948 | 121.0419 | 0.030283 | -0.10004 | -0.012 | -0.079959 | 0.049999 | 0.003172 | -0.067295 | -0.13065 | 0.051744 | -0.10036 | -0.12468 | 0.071126 | 0.14225 | 1.0241 | 1.0773 | 1.225 | 1.0947 | 1.1828 | 1.1148 | 1.2448 | 1.1979 | 1.1275 | -0.13065 | 0.051744 | -0.10036 | -0.12468 | 0.071126 | 0.14225 | 1.0241 | 1.0773 | -0.20178 | -1.1548 | -0.17149 | -1.1245
1657.2031 | 122.2641 | -1.4603 | 120.8679 | 0.025705 | -0.095467 | -0.016578 | -0.066223 | 0.045421 | 0.021485 | -0.062717 | -0.12607 | 0.056323 | -0.10494 | -0.1201 | 0.075705 | 0.14225 | 1.1248 | 1.178 | 1.486 | 1.3648 | 1.4437 | 1.394 | 1.5057 | 1.4818 | 1.3975 | -0.12607 | 0.056323 | -0.10494 | -0.1201 | 0.075705 | 0.14225 | 1.1248 | 1.178 | -0.20178 | -1.2509 | -0.18065 | -1.2298
1658.9688 | 122.2412 | -2.0142 | 120.2591 | 0.021127 | -0.095467 | -0.016578 | -0.07538 | 0.059155 | 0.021485 | -0.058139 | -0.12607 | 0.065481 | -0.10952 | -0.12926 | 0.080283 | 0.14683 | 1.9032 | 1.9654 | 2.0353 | 1.9187 | 1.9976 | 1.9388 | 2.0733 | 2.0356 | 1.956 | -0.12607 | 0.065481 | -0.10952 | -0.12926 | 0.080283 | 0.14683 | 1.9032 | 1.9654 | -0.20636 | -2.0292 | -0.1898 | -2.0127
1660.6562 | 122.3328 | -2.0462 | 120.2042 | 0.021127 | -0.10004 | -0.012 | -0.066223 | 0.049999 | 0.026064 | -0.067295 | -0.12607 | 0.042587 | -0.10952 | -0.1201 | 0.071126 | 0.14683 | 1.9444 | 1.9975 | 2.0673 | 1.9462 | 2.0342 | 1.98 | 2.0962 | 2.0723 | 1.9789 | -0.12607 | 0.042587 | -0.10952 | -0.1201 | 0.071126 | 0.14683 | 1.9444 | 1.9975 | -0.1972 | -2.0705 | -0.18065 | -2.0539
1662.4219 | 122.3145 | -3.6392 | 118.5974 | 0.021127 | -0.10004 | -0.016578 | -0.07538 | 0.049999 | 0.016907 | -0.067295 | -0.12607 | 0.051744 | -0.095785 | -0.12926 | 0.071126 | 0.15141 | 2.8417 | 2.904 | 3.6603 | 3.5392 | 3.6226 | 3.5638 | 3.6892 | 3.6561 | 3.5719 | -0.12607 | 0.051744 | -0.095785 | -0.12926 | 0.071126 | 0.15141 | 2.8417 | 2.904 | -0.1972 | -2.9678 | -0.16691 | -2.9375
1664.1719 | 122.2778 | -1.355 | 121.0327 | 0.030283 | -0.095467 | -0.012 | -0.070802 | 0.049999 | 0.021485 | -0.062717 | -0.13065 | 0.047165 | -0.10494 | -0.13384 | 0.080283 | 0.13767 | 0.97834 | 1.0361 | 1.3853 | 1.2595 | 1.343 | 1.2842 | 1.405 | 1.3765 | 1.2923 | -0.13065 | 0.047165 | -0.10494 | -0.13384 | 0.080283 | 0.13767 | 0.97834 | 1.0361 | -0.21093 | -1.109 | -0.18522 | -1.0833
1665.9219 | 122.3557 | -0.86517 | 121.3852 | 0.021127 | -0.10462 | -0.007421 | -0.070802 | 0.049999 | 0.016907 | -0.058139 | -0.12607 | 0.056323 | -0.10036 | -0.12926 | 0.066548 | 0.15141 | 0.63038 | 0.68813 | 0.8863 | 0.76055 | 0.85775 | 0.79437 | 0.91517 | 0.88208 | 0.80703 | -0.12607 | 0.056323 | -0.10036 | -0.12926 | 0.066548 | 0.15141 | 0.63038 | 0.68813 | -0.19262 | -0.75645 | -0.16691 | -0.73074
1667.6094 | 122.3282 | -0.94299 | 121.3669 | 0.025705 | -0.10004 | -0.012 | -0.079959 | 0.049999 | 0.012329 | -0.062717 | -0.1215 | 0.056323 | -0.10494 | -0.13842 | 0.075705 | 0.14683 | 0.63954 | 0.68813 | 0.9687 | 0.84295 | 0.93099 | 0.86303 | 0.99299 | 0.95532 | 0.88028 | -0.1215 | 0.056323 | -0.10494 | -0.13842 | 0.075705 | 0.14683 | 0.63954 | 0.68813 | -0.1972 | -0.76103 | -0.18065 | -0.74448
1669.3594 | 122.2733 | -0.98877 | 121.4035 | 0.021127 | -0.10004 | -0.012 | -0.070802 | 0.054577 | 0.026064 | -0.062717 | -0.12607 | 0.060902 | -0.1141 | -0.12468 | 0.080283 | 0.14683 | 0.64412 | 0.69271 | 1.0099 | 0.88872 | 0.97677 | 0.91797 | 1.0433 | 1.0148 | 0.92605 | -0.12607 | 0.060902 | -0.1141 | -0.12468 | 0.080283 | 0.14683 | 0.64412 | 0.69271 | -0.20636 | -0.77019 | -0.19438 | -0.75822
1671.0938 | 122.3831 | -0.86517 | 121.431 | 0.021127 | -0.10462 | -0.016578 | -0.07538 | 0.045421 | 0.016907 | -0.067295 | -0.12607 | 0.047165 | -0.1141 | -0.12468 | 0.075705 | 0.15141 | 0.8181 | 0.87126 | 0.8863 | 0.76055 | 0.84859 | 0.78979 | 0.91059 | 0.88208 | 0.79788 | -0.12607 | 0.047165 | -0.1141 | -0.12468 | 0.075705 | 0.15141 | 0.8181 | 0.87126 | -0.20178 | -0.94417 | -0.1898 | -0.93219
1672.7812 | 122.374 | -0.87433 | 121.4264 | 0.016548 | -0.10004 | -0.012 | -0.061645 | 0.045421 | 0.016907 | -0.058139 | -0.13065 | 0.042587 | -0.10494 | -0.12468 | 0.066548 | 0.14683 | 0.58918 | 0.63319 | 0.89088 | 0.77428 | 0.86233 | 0.81268 | 0.91975 | 0.89124 | 0.81619 | -0.13065 | 0.042587 | -0.10494 | -0.12468 | 0.066548 | 0.14683 | 0.58918 | 0.63319 | -0.1972 | -0.71983 | -0.17149 | -0.69412
1674.5469 | 122.4014 | -0.86517 | 121.4539 | 0.03944 | -0.095467 | -0.021157 | -0.07538 | 0.045421 | 0.016907 | -0.067295 | -0.13065 | 0.051744 | -0.10494 | -0.12926 | 0.075705 | 0.14683 | 0.58918 | 0.63777 | 0.90461 | 0.76971 | 0.84402 | 0.78979 | 0.91059 | 0.88208 | 0.79788 | -0.13065 | 0.051744 | -0.10494 | -0.12926 | 0.075705 | 0.14683 | 0.58918 | 0.63777 | -0.20636 | -0.71983 | -0.18065 | -0.69412
1676.2969 | 122.2687 | -0.92926 | 121.5134 | 0.030283 | -0.095467 | -0.012 | -0.066223 | 0.049999 | 0.016907 | -0.062717 | -0.1215 | 0.060902 | -0.11868 | -0.12468 | 0.071126 | 0.14683 | 0.60749 | 0.65151 | 0.95954 | 0.83379 | 0.91726 | 0.86304 | 0.97926 | 0.94617 | 0.86654 | -0.1215 | 0.060902 | -0.11868 | -0.12468 | 0.071126 | 0.14683 | 0.60749 | 0.65151 | -0.19262 | -0.72898 | -0.1898 | -0.72617
1678.0625 | 122.319 | -0.91095 | 121.5134 | 0.021127 | -0.095467 | -0.012 | -0.079959 | 0.049999 | 0.016907 | -0.071874 | -0.13065 | 0.060902 | -0.10494 | -0.1201 | 0.075705 | 0.14225 | 0.67159 | 0.72018 | 0.93208 | 0.81548 | 0.89895 | 0.83099 | 0.96095 | 0.92786 | 0.83908 | -0.13065 | 0.060902 | -0.10494 | -0.1201 | 0.075705 | 0.14225 | 0.67159 | 0.72018 | -0.20636 | -0.80224 | -0.18065 | -0.77653
1679.75 | 122.406 | -0.89264 | 121.4493 | 0.025705 | -0.10462 | -0.012 | -0.070802 | 0.054577 | 0.016907 | -0.062717 | -0.12607 | 0.047165 | -0.10494 | -0.12468 | 0.075705 | 0.14683 | 0.60749 | 0.65609 | 0.91834 | 0.78801 | 0.88064 | 0.82184 | 0.94722 | 0.90955 | 0.82992 | -0.12607 | 0.047165 | -0.10494 | -0.12468 | 0.075705 | 0.14683 | 0.60749 | 0.65609 | -0.20178 | -0.73356 | -0.18065 | -0.71243
1681.5 | 122.3007 | -0.91095 | 121.4905 | 0.021127 | -0.10462 | -0.007421 | -0.066223 | 0.059155 | 0.016907 | -0.062717 | -0.1215 | 0.047165 | -0.10494 | -0.12468 | 0.080283 | 0.14225 | 0.59833 | 0.64693 | 0.93208 | 0.80633 | 0.90353 | 0.84473 | 0.9701 | 0.92786 | 0.84823 | -0.1215 | 0.047165 | -0.10494 | -0.12468 | 0.080283 | 0.14225 | 0.59833 | 0.64693 | -0.20178 | -0.71983 | -0.18522 | -0.70327
1683.2031 | 122.3145 | -0.89264 | 121.5088 | 0.021127 | -0.10004 | -0.012 | -0.07538 | 0.049999 | 0.021485 | -0.071874 | -0.12607 | 0.051744 | -0.10036 | -0.12468 | 0.071126 | 0.15141 | 0.56628 | 0.62404 | 0.91377 | 0.79259 | 0.88064 | 0.81726 | 0.94264 | 0.91412 | 0.82076 | -0.12607 | 0.051744 | -0.10036 | -0.12468 | 0.071126 | 0.15141 | 0.56628 | 0.62404 | -0.1972 | -0.69236 | -0.17149 | -0.66665
1684.9531 | 122.3969 | -0.83313 | 121.4905 | 0.025705 | -0.10004 | -0.012 | -0.070802 | 0.054577 | 0.012329 | -0.067295 | -0.12607 | 0.060902 | -0.1141 | -0.1201 | 0.080283 | 0.14683 | 0.67159 | 0.72934 | 0.85884 | 0.73308 | 0.82113 | 0.76233 | 0.88771 | 0.84546 | 0.76584 | -0.12607 | 0.060902 | -0.1141 | -0.1201 | 0.080283 | 0.14683 | 0.67159 | 0.72934 | -0.20636 | -0.79766 | -0.19438 | -0.78569
1686.7031 | 122.4243 | -0.82855 | 121.4951 | 0.025705 | -0.090888 | -0.016578 | -0.070802 | 0.049999 | 0.026064 | -0.071874 | -0.13065 | 0.051744 | -0.10952 | -0.12468 | 0.071126 | 0.14225 | 0.56628 | 0.61488 | 0.85426 | 0.73766 | 0.81197 | 0.75775 | 0.87855 | 0.85462 | 0.75668 | -0.13065 | 0.051744 | -0.10952 | -0.12468 | 0.071126 | 0.14225 | 0.56628 | 0.61488 | -0.20178 | -0.69694 | -0.18065 | -0.6758
1688.4531 | 122.3511 | -0.87891 | 121.5271 | 0.021127 | -0.095467 | -0.012 | -0.066223 | 0.054577 | 0.016907 | -0.062717 | -0.11692 | 0.060902 | -0.10952 | -0.12926 | 0.080283 | 0.15141 | 0.58002 | 0.62862 | 0.90003 | 0.78344 | 0.86691 | 0.81268 | 0.93348 | 0.89581 | 0.81619 | -0.11692 | 0.060902 | -0.10952 | -0.12926 | 0.080283 | 0.15141 | 0.58002 | 0.62862 | -0.1972 | -0.69693 | -0.1898 | -0.68954
1690.2031 | 122.4335 | -0.85602 | 121.4951 | 0.021127 | -0.10004 | -0.016578 | -0.070802 | 0.054577 | 0.021485 | -0.062717 | -0.12607 | 0.056323 | -0.10952 | -0.12468 | 0.084861 | 0.15141 | 0.58002 | 0.63319 | 0.87714 | 0.75597 | 0.83944 | 0.78522 | 0.91059 | 0.8775 | 0.7933 | -0.12607 | 0.056323 | -0.10952 | -0.12468 | 0.084861 | 0.15141 | 0.58002 | 0.63319 | -0.21093 | -0.70609 | -0.19438 | -0.68954
1691.9531 | 122.3373 | -2.5452 | 119.8425 | 0.030283 | -0.095467 | -0.012 | -0.066223 | 0.045421 | 0.021485 | -0.058139 | -0.12607 | 0.060902 | -0.10952 | -0.1201 | 0.075705 | 0.14225 | 1.6056 | 1.6541 | 2.5754 | 2.4497 | 2.5332 | 2.4789 | 2.5906 | 2.5667 | 2.487 | -0.12607 | 0.060902 | -0.10952 | -0.1201 | 0.075705 | 0.14225 | 1.6056 | 1.6541 | -0.20178 | -1.7317 | -0.18523 | -1.7151
1693.6406 | 122.3007 | -0.94299 | 121.4355 | 0.025705 | -0.10004 | -0.007421 | -0.070802 | 0.054577 | 0.016907 | -0.067295 | -0.13065 | 0.060902 | -0.10494 | -0.12468 | 0.075705 | 0.14683 | 1.0104 | 1.0635 | 0.9687 | 0.84295 | 0.93557 | 0.87219 | 0.99757 | 0.9599 | 0.8757 | -0.13065 | 0.060902 | -0.10494 | -0.12468 | 0.075705 | 0.14683 | 1.0104 | 1.0635 | -0.20636 | -1.141 | -0.18065 | -1.1153
1695.3906 | 122.3145 | -1.1215 | 121.2524 | 0.021127 | -0.10462 | -0.012 | -0.070802 | 0.049999 | 0.026064 | -0.067295 | -0.12607 | 0.047165 | -0.10494 | -0.13384 | 0.080283 | 0.15141 | 0.84099 | 0.89415 | 1.1426 | 1.0169 | 1.1095 | 1.0507 | 1.1715 | 1.1476 | 1.0542 | -0.12607 | 0.047165 | -0.10494 | -0.13384 | 0.080283 | 0.15141 | 0.84099 | 0.89415 | -0.20636 | -0.96706 | -0.18522 | -0.94593
1697.1406 | 122.2824 | -0.91095 | 121.5317 | 0.034862 | -0.10462 | -0.012 | -0.07538 | 0.054577 | 0.021485 | -0.053561 | -0.13065 | 0.051744 | -0.10494 | -0.12468 | 0.071126 | 0.14225 | 0.66243 | 0.71102 | 0.94581 | 0.80633 | 0.89895 | 0.83557 | 0.96553 | 0.93244 | 0.85739 | -0.13065 | 0.051744 | -0.10494 | -0.12468 | 0.071126 | 0.14225 | 0.66243 | 0.71102 | -0.20178 | -0.79308 | -0.17607 | -0.76737
1698.8281 | 122.4243 | -0.88348 | 121.5088 | 0.016548 | -0.10004 | -0.012 | -0.079959 | 0.049999 | 0.026064 | -0.062717 | -0.13065 | 0.051744 | -0.10952 | -0.1201 | 0.075705 | 0.15141 | 0.68074 | 0.72476 | 0.90003 | 0.78344 | 0.87148 | 0.80353 | 0.93348 | 0.90955 | 0.82077 | -0.13065 | 0.051744 | -0.10952 | -0.1201 | 0.075705 | 0.15141 | 0.68074 | 0.72476 | -0.20636 | -0.8114 | -0.18523 | -0.79026
1700.5781 | 122.2595 | -16.0584 | 106.1691 | 0.021127 | -0.10462 | -0.021157 | -0.07538 | 0.045421 | 0.016907 | -0.071874 | -0.12607 | 0.060902 | -0.10494 | -0.12468 | 0.071126 | 0.14225 | 15.3819 | 15.4573 | 16.0795 | 15.9537 | 16.0372 | 15.983 | 16.1038 | 16.0753 | 15.9865 | -0.12607 | 0.060902 | -0.10494 | -0.12468 | 0.071126 | 0.14225 | 15.3819 | 15.4573 | -0.1972 | -15.508 | -0.17607 | -15.4869
1702.3281 | 122.3419 | -2.2476 | 120.1721 | 0.025705 | -0.10004 | -0.012 | -0.066223 | 0.059155 | 0.021485 | -0.062717 | -0.1215 | 0.056323 | -0.1141 | -0.12926 | 0.075705 | 0.14683 | 1.6834 | 1.7365 | 2.2733 | 2.1476 | 2.2356 | 2.1814 | 2.3068 | 2.2691 | 2.1849 | -0.1215 | 0.056323 | -0.1141 | -0.12926 | 0.075705 | 0.14683 | 1.6834 | 1.7365 | -0.1972 | -1.8049 | -0.1898 | -1.7975
1704.0781 | 122.406 | -2.3621 | 119.8929 | 0.030283 | -0.10462 | -0.016578 | -0.070802 | 0.045421 | 0.026064 | -0.062717 | -0.13065 | 0.047165 | -0.1141 | -0.12926 | 0.066548 | 0.14225 | 2.0359 | 2.0936 | 2.3923 | 2.2574 | 2.3455 | 2.2913 | 2.4075 | 2.3881 | 2.2993 | -0.13065 | 0.047165 | -0.1141 | -0.12926 | 0.066548 | 0.14225 | 2.0359 | 2.0936 | -0.1972 | -2.1666 | -0.18065 | -2.15
1705.7656 | 122.4518 | -2.0691 | 120.3552 | 0.025705 | -0.10004 | -0.016578 | -0.070802 | 0.045421 | 0.021485 | -0.067295 | -0.1215 | 0.056323 | -0.10494 | -0.12468 | 0.075705 | 0.14683 | 1.6514 | 1.7228 | 2.0948 | 1.969 | 2.0525 | 1.9983 | 2.1145 | 2.0906 | 2.0018 | -0.1215 | 0.056323 | -0.10494 | -0.12468 | 0.075705 | 0.14683 | 1.6514 | 1.7228 | -0.1972 | -1.7729 | -0.18065 | -1.7563
1707.5469 | 122.3419 | -1.9547 | 120.5383 | 0.025705 | -0.095467 | -0.007421 | -0.070802 | 0.063733 | 0.021485 | -0.067295 | -0.12607 | 0.056323 | -0.10494 | -0.13384 | 0.071126 | 0.14225 | 1.5781 | 1.6267 | 1.9804 | 1.8592 | 1.9472 | 1.8838 | 2.0184 | 1.9761 | 1.8874 | -0.12607 | 0.056323 | -0.10494 | -0.13384 | 0.071126 | 0.14225 | 1.5781 | 1.6267 | -0.1972 | -1.7042 | -0.17607 | -1.6831
1709.25 | 122.4243 | -1.5747 | 120.7672 | 0.025705 | -0.095467 | -0.016578 | -0.07538 | 0.054577 | 0.021485 | -0.058139 | -0.1215 | 0.056323 | -0.10494 | -0.13384 | 0.080283 | 0.15141 | 1.6376 | 1.7045 | 1.6004 | 1.4792 | 1.5581 | 1.4993 | 1.6293 | 1.5962 | 1.5166 | -0.1215 | 0.056323 | -0.10494 | -0.13384 | 0.080283 | 0.15141 | 1.6376 | 1.7045 | -0.20178 | -1.7591 | -0.18522 | -1.7426
1711 | 122.3969 | -1.7075 | 120.4742 | 0.030283 | -0.10462 | -0.007421 | -0.07538 | 0.049999 | 0.021485 | -0.058139 | -0.1215 | 0.056323 | -0.10952 | -0.12926 | 0.075705 | 0.15598 | 2.0405 | 2.0982 | 1.7377 | 1.6028 | 1.7 | 1.6321 | 1.7575 | 1.7289 | 1.6493 | -0.1215 | 0.056323 | -0.10952 | -0.12926 | 0.075705 | 0.15598 | 2.0405 | 2.0982 | -0.1972 | -2.162 | -0.18523 | -2.15
1712.6875 | 122.4655 | -1.9775 | 120.5658 | 0.025705 | -0.10462 | -0.016578 | -0.066223 | 0.059155 | 0.021485 | -0.062717 | -0.12607 | 0.056323 | -0.10494 | -0.12468 | 0.075705 | 0.15598 | 1.5873 | 1.6541 | 2.0032 | 1.8729 | 1.961 | 1.9113 | 2.0367 | 1.999 | 1.9148 | -0.12607 | 0.056323 | -0.10494 | -0.12468 | 0.075705 | 0.15598 | 1.5873 | 1.6541 | -0.20178 | -1.7133 | -0.18065 | -1.6922
1714.4375 | 122.3373 | -2.298 | 120.1859 | 0.025705 | -0.10004 | -0.016578 | -0.070802 | 0.049999 | 0.021485 | -0.062717 | -0.13065 | 0.056323 | -0.10494 | -0.12468 | 0.080283 | 0.14683 | 2.2694 | 2.3271 | 2.3237 | 2.1979 | 2.2814 | 2.2272 | 2.348 | 2.3195 | 2.2353 | -0.13065 | 0.056323 | -0.10494 | -0.12468 | 0.080283 | 0.14683 | 2.2694 | 2.3271 | -0.21093 | -2.4001 | -0.18522 | -2.3744
1716.125 | 122.5113 | -1.9089 | 120.5429 | 0.025705 | -0.095467 | -0.012 | -0.079959 | 0.049999 | 0.021485 | -0.067295 | -0.12607 | 0.060902 | -0.10952 | -0.12468 | 0.071126 | 0.15141 | 2.5625 | 2.611 | 1.9346 | 1.8134 | 1.8969 | 1.8289 | 1.9589 | 1.9304 | 1.8416 | -0.12607 | 0.060902 | -0.10952 | -0.12468 | 0.071126 | 0.15141 | 2.5625 | 2.611 | -0.1972 | -2.6885 | -0.18065 | -2.672
1717.875 | 122.3236 | -3.7537 | 118.6478 | 0.025705 | -0.095467 | -0.012 | -0.070802 | 0.049999 | 0.026064 | -0.062717 | -0.1215 | 0.047165 | -0.10494 | -0.12926 | 0.080283 | 0.14225 | 3.0111 | 3.0734 | 3.7794 | 3.6582 | 3.7417 | 3.6829 | 3.8037 | 3.7797 | 3.6909 | -0.1215 | 0.047165 | -0.10494 | -0.12926 | 0.080283 | 0.14225 | 3.0111 | 3.0734 | -0.20178 | -3.1326 | -0.18522 | -3.1161
1719.6094 | 122.3465 | -3.6026 | 118.7805 | 0.021127 | -0.10004 | -0.007421 | -0.070802 | 0.059155 | 0.026064 | -0.062717 | -0.1215 | 0.060902 | -0.10494 | -0.12468 | 0.080283 | 0.14225 | 2.7548 | 2.817 | 3.6237 | 3.5026 | 3.5952 | 3.5318 | 3.6618 | 3.6287 | 3.5399 | -0.1215 | 0.060902 | -0.10494 | -0.12468 | 0.080283 | 0.14225 | 2.7548 | 2.817 | -0.20178 | -2.8762 | -0.18522 | -2.8597
1721.3594 | 118.2999 | -26.1795 | 91.8503 | 0.025705 | -0.1092 | -0.012 | -0.079959 | 0.045421 | 0.021485 | -0.071874 | -0.12607 | 0.074638 | -0.10494 | -0.12926 | 0.071126 | 0.13309 | 26.0725 | 26.2023 | 26.2052 | 26.0703 | 26.1675 | 26.0995 | 26.2249 | 26.201 | 26.1076 | -0.12607 | 0.074638 | -0.10494 | -0.12926 | 0.071126 | 0.13309 | 26.0725 | 26.2023 | -0.1972 | -26.1986 | -0.17607 | -26.1774
1723.1094 | 117.659 | -26.7838 | 90.8203 | 0.025705 | -0.10462 | -0.016578 | -0.079959 | 0.049999 | 0.016907 | -0.071874 | -0.11234 | 0.07006 | -0.10494 | -0.12468 | 0.071126 | 0.13767 | 26.5761 | 26.8432 | 26.8095 | 26.6791 | 26.7672 | 26.7038 | 26.8338 | 26.8007 | 26.7119 | -0.11234 | 0.07006 | -0.10494 | -0.12468 | 0.071126 | 0.13767 | 26.5761 | 26.8432 | -0.18346 | -26.6884 | -0.17607 | -26.681
1724.8438 | 117.3157 | -29.6585 | 87.3825 | 0.016548 | -0.11378 | -0.021157 | -0.07538 | 0.045421 | 0.016907 | -0.067295 | -0.11692 | 0.074638 | -0.095785 | -0.12926 | 0.071126 | 0.13767 | 29.1308 | 29.3612 | 29.6751 | 29.5447 | 29.6374 | 29.5831 | 29.7039 | 29.6754 | 29.5912 | -0.11692 | 0.074638 | -0.095785 | -0.12926 | 0.071126 | 0.13767 | 29.1308 | 29.3612 | -0.18804 | -29.2478 | -0.16691 | -29.2266
1726.5156 | 115.535 | -77.0828 | 38.3881 | 0.007391 | -0.12294 | -0.030314 | -0.084537 | 0.031687 | -0.005985 | -0.08103 | -0.10776 | 0.097532 | -0.063737 | -0.13384 | 0.052814 | 0.1102 | 75.8853 | 76.0632 | 77.0902 | 76.9599 | 77.0525 | 76.9983 | 77.1145 | 77.0768 | 77.0018 | -0.10776 | 0.097532 | -0.063737 | -0.13384 | 0.052814 | 0.1102 | 75.8853 | 76.0632 | -0.16057 | -75.9931 | -0.11655 | -75.9491
1728.2812 | 119.6594 | -119.1696 | 0.27466 | -0.006344 | -0.1321 | -0.04405 | -0.10743 | 0.013375 | -0.015142 | -0.094765 | -0.061975 | 0.11127 | -0.050002 | -0.14758 | 0.039079 | 0.10105 | 118.8215 | 118.9103 | 119.1633 | 119.0375 | 119.1256 | 119.0622 | 119.183 | 119.1545 | 119.0749 | -0.061975 | 0.11127 | -0.050002 | -0.14758 | 0.039079 | 0.10105 | 118.8215 | 118.9103 | -0.10105 | -118.8834 | -0.089081 | -118.8715
1729.9531 | 120.0485 | -119.6045 | 0.21515 | -0.001765 | -0.12752 | -0.039471 | -0.093694 | 0.031687 | -0.010563 | -0.094765 | -0.084867 | 0.10211 | -0.072894 | -0.14758 | 0.043657 | 0.096469 | 119.4991 | 119.6337 | 119.6027 | 119.477 | 119.565 | 119.5108 | 119.6362 | 119.5939 | 119.5097 | -0.084867 | 0.10211 | -0.072894 | -0.14758 | 0.043657 | 0.096469 | 119.4991 | 119.6337 | -0.12852 | -119.5839 | -0.11655 | -119.572
1731.7031 | 120.1172 | -119.8059 | 0.25635 | -0.001765 | -0.12294 | -0.034893 | -0.093694 | 0.031687 | -0.001406 | -0.085608 | -0.071132 | 0.10669 | -0.072894 | -0.143 | 0.039079 | 0.091891 | 119.6776 | 119.8076 | 119.8041 | 119.683 | 119.771 | 119.7122 | 119.8376 | 119.8045 | 119.7203 | -0.071132 | 0.10669 | -0.072894 | -0.143 | 0.039079 | 0.091891 | 119.6776 | 119.8076 | -0.11021 | -119.7488 | -0.11197 | -119.7505
1733.3906 | 120.2545 | -119.8883 | 0.21973 | -0.001765 | -0.12294 | -0.04405 | -0.10285 | 0.022531 | -0.010563 | -0.099343 | -0.066553 | 0.10669 | -0.05458 | -0.143 | 0.039079 | 0.10105 | 119.5494 | 119.9038 | 119.8865 | 119.7654 | 119.8443 | 119.7855 | 119.9108 | 119.8777 | 119.789 | -0.066553 | 0.10669 | -0.05458 | -0.143 | 0.039079 | 0.10105 | 119.5494 | 119.9038 | -0.10563 | -119.616 | -0.093659 | -119.604
1735.1406 | 120.2271 | -119.9982 | 0.22888 | 0.002813 | -0.12752 | -0.039471 | -0.10743 | 0.027109 | -0.005985 | -0.085608 | -0.057396 | 0.10669 | -0.063737 | -0.13842 | 0.039079 | 0.096469 | 119.6364 | 119.9953 | 120.001 | 119.8707 | 119.9587 | 119.8907 | 120.0253 | 119.9922 | 119.9126 | -0.057396 | 0.10669 | -0.063737 | -0.13842 | 0.039079 | 0.096469 | 119.6364 | 119.9953 | -0.096475 | -119.6938 | -0.10282 | -119.7002
1736.8125 | 120.3873 | -120.0485 | 0.21515 | -0.006344 | -0.1321 | -0.04405 | -0.10285 | 0.022531 | -0.005985 | -0.099343 | -0.025347 | 0.11127 | -0.072894 | -0.143 | 0.043657 | 0.10105 | 119.7051 | 120.0548 | 120.0422 | 119.9164 | 120.0045 | 119.9457 | 120.0711 | 120.0425 | 119.9492 | -0.025347 | 0.11127 | -0.072894 | -0.143 | 0.043657 | 0.10105 | 119.7051 | 120.0548 | -0.069004 | -119.7304 | -0.11655 | -119.778
1738.5625 | 120.4102 | -120.1035 | 0.24261 | -0.001765 | -0.12294 | -0.039471 | -0.11201 | 0.027109 | -0.010563 | -0.094765 | -0.098602 | 0.11127 | -0.063737 | -0.14758 | 0.039079 | 0.10562 | 119.7417 | 120.1098 | 120.1017 | 119.9805 | 120.064 | 119.9914 | 120.1306 | 120.0929 | 120.0087 | -0.098602 | 0.11127 | -0.063737 | -0.14758 | 0.039079 | 0.10562 | 119.7417 | 120.1098 | -0.13768 | -119.8403 | -0.10282 | -119.8055
1740.3281 | 120.4422 | -120.1813 | 0.23804 | -0.001765 | -0.11836 | -0.030314 | -0.093694 | 0.031687 | -0.005985 | -0.085608 | -0.07571 | 0.10669 | -0.072894 | -0.14758 | 0.043657 | 0.091891 | 119.8104 | 120.1556 | 120.1795 | 120.0629 | 120.151 | 120.0876 | 120.213 | 120.1753 | 120.0957 | -0.07571 | 0.10669 | -0.072894 | -0.14758 | 0.043657 | 0.091891 | 119.8104 | 120.1556 | -0.11937 | -119.8861 | -0.11655 | -119.8833
1742.0156 | 120.5383 | -120.195 | 0.22888 | 0.007391 | -0.10462 | -0.030314 | -0.079959 | 0.045421 | 0.003172 | -0.076452 | -0.034504 | 0.11127 | -0.045424 | -0.143 | 0.039079 | 0.096469 | 119.8379 | 120.1968 | 120.2024 | 120.0904 | 120.1647 | 120.115 | 120.2404 | 120.1982 | 120.1186 | -0.034504 | 0.11127 | -0.045424 | -0.143 | 0.039079 | 0.096469 | 119.8379 | 120.1968 | -0.073583 | -119.8724 | -0.084503 | -119.8833
1743.7656 | 120.5795 | -120.2087 | 0.21515 | 0.021127 | -0.1092 | -0.016578 | -0.079959 | 0.045421 | 0.00775 | -0.067295 | -0.025347 | 0.12043 | -0.045424 | -0.143 | 0.043657 | 0.096469 | 119.8837 | 120.2471 | 120.2299 | 120.0995 | 120.1922 | 120.1288 | 120.2542 | 120.2165 | 120.1414 | -0.025347 | 0.12043 | -0.045424 | -0.143 | 0.043657 | 0.096469 | 119.8837 | 120.2471 | -0.069004 | -119.909 | -0.089081 | -119.9291
1745.5312 | 120.6162 | -120.2454 | 0.22888 | 0.01197 | -0.10462 | -0.025735 | -0.084537 | 0.040843 | 0.012329 | -0.076452 | -0.052818 | 0.092954 | -0.068315 | -0.143 | 0.039079 | 0.10105 | 119.9203 | 120.2792 | 120.2573 | 120.1407 | 120.2196 | 120.1608 | 120.2862 | 120.2577 | 120.1689 | -0.052818 | 0.092954 | -0.068315 | -0.143 | 0.039079 | 0.10105 | 119.9203 | 120.2792 | -0.091897 | -119.9731 | -0.10739 | -119.9886
1747.2031 | 120.5887 | -120.3278 | 0.24261 | 0.021127 | -0.10462 | -0.016578 | -0.084537 | 0.040843 | 0.003172 | -0.076452 | -0.066553 | 0.11127 | -0.068315 | -0.143 | 0.043657 | 0.10562 | 119.9615 | 120.3066 | 120.3489 | 120.2231 | 120.3112 | 120.2432 | 120.3686 | 120.3309 | 120.2513 | -0.066553 | 0.11127 | -0.068315 | -0.143 | 0.043657 | 0.10562 | 119.9615 | 120.3066 | -0.11021 | -120.028 | -0.11197 | -120.0298
1748.9531 | 120.7031 | -120.3003 | 0.22888 | 0.016548 | -0.10462 | -0.021157 | -0.089116 | 0.045421 | 0.016907 | -0.076452 | -0.039082 | 0.11585 | -0.063737 | -0.13842 | 0.039079 | 0.096469 | 119.989 | 120.3478 | 120.3168 | 120.1957 | 120.2791 | 120.2112 | 120.3457 | 120.3172 | 120.2238 | -0.039082 | 0.11585 | -0.063737 | -0.13842 | 0.039079 | 0.096469 | 119.989 | 120.3478 | -0.078161 | -120.028 | -0.10282 | -120.0527
1750.6875 | 120.6802 | -120.3415 | 0.25635 | 0.021127 | -0.10462 | -0.016578 | -0.084537 | 0.045421 | 0.012329 | -0.071874 | -0.084867 | 0.10669 | -0.077472 | -0.13842 | 0.039079 | 0.10105 | 120.0118 | 120.3845 | 120.3626 | 120.2369 | 120.3249 | 120.257 | 120.3869 | 120.3538 | 120.2696 | -0.084867 | 0.10669 | -0.077472 | -0.13842 | 0.039079 | 0.10105 | 120.0118 | 120.3845 | -0.12395 | -120.0967 | -0.11655 | -120.0893
1752.4375 | 120.6482 | -120.401 | 0.27466 | 0.016548 | -0.10462 | -0.016578 | -0.079959 | 0.054577 | 0.016907 | -0.071874 | -0.011611 | 0.10669 | -0.063737 | -0.14758 | 0.043657 | 0.091891 | 120.0439 | 120.3982 | 120.4175 | 120.2964 | 120.3844 | 120.321 | 120.4556 | 120.4179 | 120.3291 | -0.011611 | 0.10669 | -0.063737 | -0.14758 | 0.043657 | 0.091891 | 120.0439 | 120.3982 | -0.055268 | -120.0555 | -0.10739 | -120.1076
1754.1875 | 120.7809 | -120.3552 | 0.2655 | 0.025705 | -0.090888 | -0.021157 | -0.07538 | 0.054577 | 0.021485 | -0.071874 | -0.039082 | 0.10669 | -0.072894 | -0.14758 | 0.043657 | 0.10105 | 120.0531 | 120.4165 | 120.3809 | 120.2643 | 120.3341 | 120.2798 | 120.4098 | 120.3767 | 120.2834 | -0.039082 | 0.10669 | -0.072894 | -0.14758 | 0.043657 | 0.10105 | 120.0531 | 120.4165 | -0.082739 | -120.0921 | -0.11655 | -120.1259
1755.9375 | 120.7489 | -120.4239 | 0.29297 | 0.016548 | -0.10462 | -0.021157 | -0.070802 | 0.049999 | 0.021485 | -0.067295 | -0.011611 | 0.11127 | -0.077472 | -0.13842 | 0.039079 | 0.10105 | 120.0851 | 120.4531 | 120.4404 | 120.3193 | 120.4027 | 120.3531 | 120.4739 | 120.4454 | 120.3566 | -0.011611 | 0.11127 | -0.077472 | -0.13842 | 0.039079 | 0.10105 | 120.0851 | 120.4531 | -0.05069 | -120.0967 | -0.11655 | -120.1626
1757.625 | 120.8084 | -120.4239 | 0.27924 | 0.025705 | -0.10462 | -0.021157 | -0.084537 | 0.049999 | 0.021485 | -0.067295 | -0.048239 | 0.11127 | -0.08205 | -0.143 | 0.039079 | 0.096469 | 120.1126 | 120.2471 | 120.4496 | 120.3193 | 120.4027 | 120.3394 | 120.4739 | 120.4454 | 120.3566 | -0.048239 | 0.11127 | -0.08205 | -0.143 | 0.039079 | 0.096469 | 120.1126 | 120.2471 | -0.087318 | -120.1608 | -0.12113 | -120.1946
1759.3906 | 120.8588 | -120.4514 | 0.28381 | 0.021127 | -0.095467 | -0.016578 | -0.070802 | 0.045421 | 0.016907 | -0.071874 | -0.071132 | 0.10669 | -0.063737 | -0.13384 | 0.039079 | 0.10105 | 120.14 | 120.27 | 120.4725 | 120.3559 | 120.4348 | 120.3806 | 120.4968 | 120.4683 | 120.3795 | -0.071132 | 0.10669 | -0.063737 | -0.13384 | 0.039079 | 0.10105 | 120.14 | 120.27 | -0.11021 | -120.2112 | -0.10282 | -120.2038
1761.0781 | 120.7993 | -120.4926 | 0.29297 | 0.030283 | -0.095467 | -0.016578 | -0.079959 | 0.049999 | 0.016907 | -0.067295 | -0.061975 | 0.10669 | -0.077472 | -0.143 | 0.039079 | 0.10105 | 120.1767 | 120.2975 | 120.5228 | 120.3971 | 120.476 | 120.4126 | 120.5426 | 120.5095 | 120.4253 | -0.061975 | 0.10669 | -0.077472 | -0.143 | 0.039079 | 0.10105 | 120.1767 | 120.2975 | -0.10105 | -120.2386 | -0.11655 | -120.2541
1762.8281 | 120.813 | -120.5246 | 0.31586 | 0.025705 | -0.10004 | -0.012 | -0.07538 | 0.049999 | 0.026064 | -0.067295 | -0.066553 | 0.11127 | -0.072894 | -0.143 | 0.043657 | 0.10562 | 120.1858 | 120.3295 | 120.5503 | 120.4246 | 120.5126 | 120.4492 | 120.5746 | 120.5507 | 120.4573 | -0.066553 | 0.11127 | -0.072894 | -0.143 | 0.043657 | 0.10562 | 120.1858 | 120.3295 | -0.11021 | -120.2524 | -0.11655 | -120.2587
1764.5781 | 120.932 | -120.5154 | 0.28381 | 0.025705 | -0.090888 | -0.012 | -0.070802 | 0.054577 | 0.030642 | -0.067295 | -0.066553 | 0.10211 | -0.068315 | -0.143 | 0.048236 | 0.096469 | 120.2133 | 120.3433 | 120.5411 | 120.4246 | 120.5034 | 120.4446 | 120.57 | 120.5461 | 120.4481 | -0.066553 | 0.10211 | -0.068315 | -0.143 | 0.048236 | 0.096469 | 120.2133 | 120.3433 | -0.11479 | -120.2798 | -0.11655 | -120.2816
1766.3281 | 120.9778 | -120.5383 | 0.30212 | 0.025705 | -0.10004 | -0.016578 | -0.070802 | 0.054577 | 0.021485 | -0.053561 | -0.080288 | 0.11585 | -0.063737 | -0.143 | 0.048236 | 0.10105 | 120.2362 | 120.3707 | 120.564 | 120.4383 | 120.5218 | 120.4675 | 120.5929 | 120.5598 | 120.4848 | -0.080288 | 0.11585 | -0.063737 | -0.143 | 0.048236 | 0.10105 | 120.2362 | 120.3707 | -0.12852 | -120.3165 | -0.11197 | -120.2999
1768.0781 | 120.9869 | -120.5612 | 0.28839 | 0.016548 | -0.10004 | -0.012 | -0.07538 | 0.054577 | 0.030642 | -0.062717 | -0.043661 | 0.10211 | -0.031689 | -0.143 | 0.034501 | 0.10562 | 120.2545 | 120.389 | 120.5778 | 120.4612 | 120.5492 | 120.4858 | 120.6158 | 120.5919 | 120.4985 | -0.043661 | 0.10211 | -0.031689 | -0.143 | 0.034501 | 0.10562 | 120.2545 | 120.389 | -0.078162 | -120.2982 | -0.06619 | -120.2862
1769.7656 | 120.9595 | -120.6207 | 0.31128 | 0.025705 | -0.086309 | -0.012 | -0.066223 | 0.059155 | 0.026064 | -0.062717 | -0.057396 | 0.10669 | -0.072894 | -0.13384 | 0.048236 | 0.10105 | 120.2774 | 120.4028 | 120.6464 | 120.5344 | 120.6087 | 120.5545 | 120.6799 | 120.6468 | 120.558 | -0.057396 | 0.10669 | -0.072894 | -0.13384 | 0.048236 | 0.10105 | 120.2774 | 120.4028 | -0.10563 | -120.3348 | -0.12113 | -120.3503
1771.5312 | 121.0052 | -120.6024 | 0.3067 | 0.030283 | -0.090888 | -0.007421 | -0.070802 | 0.054577 | 0.026064 | -0.062717 | -0.043661 | 0.11127 | -0.068315 | -0.14758 | 0.039079 | 0.10105 | 120.2911 | 120.4348 | 120.6327 | 120.5115 | 120.595 | 120.5316 | 120.657 | 120.6285 | 120.5397 | -0.043661 | 0.11127 | -0.068315 | -0.14758 | 0.039079 | 0.10105 | 120.2911 | 120.4348 | -0.08274 | -120.3348 | -0.10739 | -120.3594
1773.2812 | 120.9961 | -120.6528 | 0.32959 | 0.030283 | -0.090888 | -0.012 | -0.066223 | 0.063733 | 0.030642 | -0.058139 | -0.048239 | 0.10669 | -0.050002 | -0.143 | 0.043657 | 0.096469 | 120.3232 | 120.4486 | 120.6831 | 120.5619 | 120.6408 | 120.5865 | 120.7165 | 120.6834 | 120.5946 | -0.048239 | 0.10669 | -0.050002 | -0.143 | 0.043657 | 0.096469 | 120.3232 | 120.4486 | -0.091896 | -120.3714 | -0.093659 | -120.3732
1774.9688 | 120.9915 | -120.6848 | 0.33875 | 0.030283 | -0.090888 | -0.007421 | -0.070802 | 0.063733 | 0.026064 | -0.062717 | -0.061975 | 0.11127 | -0.077472 | -0.13842 | 0.039079 | 0.10562 | 120.3461 | 120.476 | 120.7151 | 120.5939 | 120.6774 | 120.614 | 120.7485 | 120.7109 | 120.6221 | -0.061975 | 0.11127 | -0.077472 | -0.13842 | 0.039079 | 0.10562 | 120.3461 | 120.476 | -0.10105 | -120.408 | -0.11655 | -120.4235
1776.7031 | 121.0236 | -120.6757 | 0.32044 | 0.025705 | -0.095467 | -0.007421 | -0.070802 | 0.054577 | 0.026064 | -0.062717 | -0.07571 | 0.10669 | -0.072894 | -0.143 | 0.048236 | 0.096469 | 120.3644 | 120.4989 | 120.7014 | 120.5802 | 120.6682 | 120.6049 | 120.7302 | 120.7017 | 120.6129 | -0.07571 | 0.10669 | -0.072894 | -0.143 | 0.048236 | 0.096469 | 120.3644 | 120.4989 | -0.12395 | -120.4401 | -0.12113 | -120.4373
1778.4531 | 121.0922 | -120.694 | 0.31128 | 0.021127 | -0.095467 | -0.007421 | -0.070802 | 0.054577 | 0.030642 | -0.062717 | -0.084867 | 0.10669 | -0.05458 | -0.13842 | 0.039079 | 0.096469 | 120.3781 | 120.5127 | 120.7151 | 120.5985 | 120.6865 | 120.6232 | 120.7485 | 120.7246 | 120.6313 | -0.084867 | 0.10669 | -0.05458 | -0.13842 | 0.039079 | 0.096469 | 120.3781 | 120.5127 | -0.12395 | -120.463 | -0.093659 | -120.4327
1780.2188 | 121.1243 | -120.7031 | 0.3067 | 0.03944 | -0.10462 | -0.007421 | -0.070802 | 0.059155 | 0.021485 | -0.062717 | -0.071132 | 0.11585 | -0.059159 | -0.13842 | 0.039079 | 0.10562 | 120.3964 | 120.5401 | 120.7426 | 120.5985 | 120.6957 | 120.6323 | 120.7623 | 120.7246 | 120.6404 | -0.071132 | 0.11585 | -0.059159 | -0.13842 | 0.039079 | 0.10562 | 120.3964 | 120.5401 | -0.11021 | -120.4676 | -0.098238 | -120.4556
1781.9688 | 121.0373 | -120.7718 | 0.33417 | 0.025705 | -0.095467 | -0.007421 | -0.066223 | 0.045421 | 0.026064 | -0.067295 | -0.057396 | 0.10211 | -0.050002 | -0.143 | 0.039079 | 0.091891 | 120.4056 | 120.5447 | 120.7975 | 120.6763 | 120.7644 | 120.7056 | 120.8172 | 120.7979 | 120.7045 | -0.057396 | 0.10211 | -0.050002 | -0.143 | 0.039079 | 0.091891 | 120.4056 | 120.5447 | -0.096475 | -120.463 | -0.089081 | -120.4556
1783.6562 | 121.2021 | -120.7443 | 0.3067 | 0.03944 | -0.086309 | -0.016578 | -0.07538 | 0.049999 | 0.021485 | -0.058139 | -0.043661 | 0.11585 | -0.072894 | -0.143 | 0.039079 | 0.10105 | 120.4239 | 120.563 | 120.7838 | 120.658 | 120.7277 | 120.6689 | 120.7943 | 120.7658 | 120.6862 | -0.043661 | 0.11585 | -0.072894 | -0.143 | 0.039079 | 0.10105 | 120.4239 | 120.563 | -0.08274 | -120.4676 | -0.11197 | -120.4968
1785.4062 | 121.2341 | -120.7672 | 0.31128 | 0.016548 | -0.08173 | -0.012 | -0.070802 | 0.054577 | 0.016907 | -0.058139 | -0.039082 | 0.11127 | -0.068315 | -0.13842 | 0.034501 | 0.096469 | 120.4605 | 120.5859 | 120.7838 | 120.6855 | 120.7552 | 120.6964 | 120.8218 | 120.7841 | 120.7091 | -0.039082 | 0.11127 | -0.068315 | -0.13842 | 0.034501 | 0.096469 | 120.4605 | 120.5859 | -0.073583 | -120.4996 | -0.10282 | -120.5288
1787.0938 | 121.1151 | -120.7947 | 0.3479 | 0.016548 | -0.10462 | -0.021157 | -0.07538 | 0.049999 | 0.012329 | -0.067295 | -0.025347 | 0.11127 | -0.031689 | -0.143 | 0.034501 | 0.091891 | 120.4697 | 120.6088 | 120.8112 | 120.6901 | 120.7735 | 120.7193 | 120.8447 | 120.807 | 120.7274 | -0.025347 | 0.11127 | -0.031689 | -0.143 | 0.034501 | 0.091891 | 120.4697 | 120.6088 | -0.059848 | -120.495 | -0.06619 | -120.5014
1788.8438 | 121.2021 | -120.813 | 0.32501 | 0.021127 | -0.10462 | -0.025735 | -0.07538 | 0.049999 | 0.016907 | -0.076452 | -0.057396 | 0.10669 | -0.072894 | -0.14758 | 0.039079 | 0.096469 | 120.4743 | 120.6088 | 120.8341 | 120.7084 | 120.7873 | 120.7376 | 120.863 | 120.8299 | 120.7365 | -0.057396 | 0.10669 | -0.072894 | -0.14758 | 0.039079 | 0.096469 | 120.4743 | 120.6088 | -0.096475 | -120.5317 | -0.11197 | -120.5472
1790.5938 | 121.1334 | -120.8313 | 0.35248 | 0.021127 | -0.10462 | -0.021157 | -0.084537 | 0.049999 | 0.021485 | -0.067295 | -0.057396 | 0.10211 | -0.031689 | -0.143 | 0.039079 | 0.096469 | 120.4972 | 120.6317 | 120.8524 | 120.7267 | 120.8101 | 120.7468 | 120.8813 | 120.8528 | 120.764 | -0.057396 | 0.10211 | -0.031689 | -0.143 | 0.039079 | 0.096469 | 120.4972 | 120.6317 | -0.096475 | -120.5545 | -0.070768 | -120.5288
1792.2812 | 121.2891 | -120.8359 | 0.32959 | 0.021127 | -0.10462 | -0.016578 | -0.079959 | 0.049999 | 0.021485 | -0.062717 | -0.057396 | 0.11127 | -0.05458 | -0.14758 | 0.048236 | 0.10105 | 120.5017 | 120.6408 | 120.857 | 120.7313 | 120.8193 | 120.7559 | 120.8859 | 120.8574 | 120.7732 | -0.057396 | 0.11127 | -0.05458 | -0.14758 | 0.048236 | 0.10105 | 120.5017 | 120.6408 | -0.10563 | -120.5591 | -0.10282 | -120.5563
1794.0469 | 121.2799 | -120.8313 | 0.33875 | 0.021127 | -0.095467 | -0.021157 | -0.079959 | 0.045421 | 0.012329 | -0.067295 | -0.084867 | 0.097532 | -0.072894 | -0.143 | 0.043657 | 0.096469 | 120.5246 | 120.6637 | 120.8524 | 120.7358 | 120.8101 | 120.7513 | 120.8767 | 120.8436 | 120.764 | -0.084867 | 0.097532 | -0.072894 | -0.143 | 0.043657 | 0.096469 | 120.5246 | 120.6637 | -0.12852 | -120.6095 | -0.11655 | -120.5975
1795.8125 | 121.2158 | -120.8954 | 0.37079 | 0.030283 | -0.10004 | -0.002842 | -0.066223 | 0.054577 | 0.021485 | -0.062717 | -0.071132 | 0.10669 | -0.072894 | -0.143 | 0.043657 | 0.10105 | 120.5384 | 120.6729 | 120.9257 | 120.7953 | 120.8925 | 120.8292 | 120.95 | 120.9169 | 120.8327 | -0.071132 | 0.10669 | -0.072894 | -0.143 | 0.043657 | 0.10105 | 120.5384 | 120.6729 | -0.11479 | -120.6095 | -0.11655 | -120.6113
1797.5625 | 121.2845 | -120.8633 | 0.33875 | 0.025705 | -0.095467 | -0.007421 | -0.07538 | 0.049999 | 0.016907 | -0.076452 | -0.020768 | 0.11585 | -0.050002 | -0.143 | 0.043657 | 0.1102 | 120.5521 | 120.6912 | 120.889 | 120.7679 | 120.8559 | 120.788 | 120.9133 | 120.8802 | 120.7869 | -0.020768 | 0.11585 | -0.050002 | -0.143 | 0.043657 | 0.1102 | 120.5521 | 120.6912 | -0.064425 | -120.5729 | -0.093659 | -120.6021
1799.2656 | 121.3257 | -120.8679 | 0.37079 | 0.030283 | -0.095467 | -0.007421 | -0.070802 | 0.054577 | 0.026064 | -0.058139 | -0.057396 | 0.11127 | -0.036267 | -0.15216 | 0.039079 | 0.096469 | 120.5613 | 120.7049 | 120.8982 | 120.7725 | 120.8605 | 120.7971 | 120.9225 | 120.894 | 120.8098 | -0.057396 | 0.11127 | -0.036267 | -0.15216 | 0.039079 | 0.096469 | 120.5613 | 120.7049 | -0.096475 | -120.6186 | -0.075346 | -120.5975
1801.0312 | 121.376 | -120.8633 | 0.32044 | 0.034862 | -0.095467 | -0.002842 | -0.070802 | 0.054577 | 0.030642 | -0.062717 | 0.006703 | 0.10669 | -0.040846 | -0.14758 | 0.043657 | 0.091891 | 120.575 | 120.7095 | 120.8982 | 120.7679 | 120.8605 | 120.7925 | 120.9179 | 120.894 | 120.8006 | 0.006703 | 0.10669 | -0.040846 | -0.14758 | 0.043657 | 0.091891 | 120.575 | 120.7095 | -0.036954 | -120.5683 | -0.084503 | -120.6158
1802.7656 | 121.376 | -120.8817 | 0.32959 | 0.016548 | -0.095467 | -0.016578 | -0.07538 | 0.049999 | 0.026064 | -0.062717 | -0.039082 | 0.10211 | -0.045424 | -0.13384 | 0.034501 | 0.091891 | 120.5933 | 120.7324 | 120.8982 | 120.7862 | 120.8651 | 120.8063 | 120.9317 | 120.9077 | 120.8189 | -0.039082 | 0.10211 | -0.045424 | -0.13384 | 0.034501 | 0.091891 | 120.5933 | 120.7324 | -0.073583 | -120.6324 | -0.079925 | -120.6387
1804.4531 | 121.3211 | -120.9366 | 0.36621 | 0.030283 | -0.086309 | -0.002842 | -0.07538 | 0.063733 | 0.026064 | -0.067295 | -0.020768 | 0.12501 | -0.031689 | -0.13842 | 0.039079 | 0.10105 | 120.607 | 120.7507 | 120.9669 | 120.8503 | 120.9337 | 120.8612 | 121.0003 | 120.9626 | 120.8693 | -0.020768 | 0.12501 | -0.031689 | -0.13842 | 0.039079 | 0.10105 | 120.607 | 120.7507 | -0.059847 | -120.6278 | -0.070768 | -120.6387
1806.2031 | 121.3303 | -120.932 | 0.36163 | 0.030283 | -0.090888 | -0.002842 | -0.07538 | 0.054577 | 0.030642 | -0.058139 | -0.029925 | 0.11585 | -0.050002 | -0.143 | 0.048236 | 0.096469 | 120.6253 | 120.7645 | 120.9623 | 120.8411 | 120.9292 | 120.8566 | 120.9866 | 120.9626 | 120.8739 | -0.029925 | 0.11585 | -0.050002 | -0.143 | 0.048236 | 0.096469 | 120.6253 | 120.7645 | -0.078161 | -120.6553 | -0.098238 | -120.6754
1807.9688 | 121.431 | -120.9503 | 0.35706 | 0.025705 | -0.090888 | -0.016578 | -0.079959 | 0.054577 | 0.016907 | -0.067295 | -0.029925 | 0.11585 | -0.050002 | -0.13842 | 0.048236 | 0.10105 | 120.6437 | 120.7828 | 120.976 | 120.8594 | 120.9337 | 120.8704 | 121.0049 | 120.9672 | 120.883 | -0.029925 | 0.11585 | -0.050002 | -0.13842 | 0.048236 | 0.10105 | 120.6437 | 120.7828 | -0.078161 | -120.6736 | -0.098238 | -120.6937
1809.7188 | 121.4035 | -120.9595 | 0.35706 | 0.01197 | -0.10004 | -0.021157 | -0.079959 | 0.045421 | 0.016907 | -0.067295 | -0.011611 | 0.12043 | -0.036267 | -0.14758 | 0.039079 | 0.096469 | 120.6437 | 120.7828 | 120.9714 | 120.8594 | 120.9383 | 120.8795 | 121.0049 | 120.9764 | 120.8922 | -0.011611 | 0.12043 | -0.036267 | -0.14758 | 0.039079 | 0.096469 | 120.6437 | 120.7828 | -0.05069 | -120.6553 | -0.075346 | -120.6799
1811.4688 | 121.4539 | -120.9778 | 0.35706 | 0.025705 | -0.10462 | -0.021157 | -0.084537 | 0.045421 | 0.012329 | -0.076452 | -0.020768 | 0.12958 | -0.031689 | -0.143 | 0.043657 | 0.10562 | 120.6666 | 120.8057 | 121.0035 | 120.8732 | 120.9566 | 120.8932 | 121.0232 | 120.9901 | 120.9013 | -0.020768 | 0.12958 | -0.031689 | -0.143 | 0.043657 | 0.10562 | 120.6666 | 120.8057 | -0.064425 | -120.6873 | -0.075346 | -120.6982
1813.1562 | 121.3715 | -121.0144 | 0.39825 | 0.016548 | -0.10004 | -0.016578 | -0.089116 | 0.040843 | 0.012329 | -0.071874 | -0.011611 | 0.12958 | -0.036267 | -0.14758 | 0.043657 | 0.096469 | 120.694 | 120.824 | 121.031 | 120.9144 | 120.9978 | 120.9253 | 121.0552 | 121.0267 | 120.9425 | -0.011611 | 0.12958 | -0.036267 | -0.14758 | 0.043657 | 0.096469 | 120.694 | 120.824 | -0.055268 | -120.7056 | -0.079924 | -120.7303
1814.9062 | 121.4813 | -121.019 | 0.32959 | 0.01197 | -0.10462 | -0.021157 | -0.084537 | 0.036265 | 0.003172 | -0.071874 | 0.002124 | 0.11585 | -0.027111 | -0.13842 | 0.048236 | 0.096469 | 120.694 | 120.8286 | 121.031 | 120.9144 | 120.9978 | 120.9344 | 121.0552 | 121.0222 | 120.9471 | 0.002124 | 0.11585 | -0.027111 | -0.13842 | 0.048236 | 0.096469 | 120.694 | 120.8286 | -0.046112 | -120.6919 | -0.075347 | -120.7211
1816.6406 | 121.3898 | -121.051 | 0.37537 | 0.016548 | -0.10462 | -0.021157 | -0.079959 | 0.045421 | 0.016907 | -0.071874 | -0.029925 | 0.11585 | -0.008798 | -0.143 | 0.039079 | 0.10105 | 120.7169 | 120.8514 | 121.0676 | 120.9464 | 121.0299 | 120.9711 | 121.0964 | 121.0679 | 120.9792 | -0.029925 | 0.11585 | -0.008798 | -0.143 | 0.039079 | 0.10105 | 120.7169 | 120.8514 | -0.069004 | -120.7468 | -0.047877 | -120.7257
1818.3906 | 121.4722 | -121.0464 | 0.34332 | 0.021127 | -0.095467 | -0.007421 | -0.070802 | 0.049999 | 0.016907 | -0.067295 | -0.007033 | 0.11127 | -0.059159 | -0.14758 | 0.039079 | 0.10562 | 120.7215 | 120.8606 | 121.0676 | 120.951 | 121.039 | 120.9756 | 121.0964 | 121.0634 | 120.9792 | -0.007033 | 0.11127 | -0.059159 | -0.14758 | 0.039079 | 0.10562 | 120.7215 | 120.8606 | -0.046112 | -120.7285 | -0.098238 | -120.7807
1820.1406 | 121.4264 | -121.0693 | 0.39368 | 0.021127 | -0.10004 | -0.012 | -0.079959 | 0.045421 | 0.016907 | -0.067295 | 0.011281 | 0.11585 | -0.031689 | -0.14758 | 0.039079 | 0.10562 | 120.7352 | 120.8698 | 121.0905 | 120.9693 | 121.0573 | 120.9894 | 121.1148 | 121.0862 | 121.002 | 0.011281 | 0.11585 | -0.031689 | -0.14758 | 0.039079 | 0.10562 | 120.7352 | 120.8698 | -0.027798 | -120.7239 | -0.070768 | -120.7669
1821.8906 | 121.5134 | -121.0419 | 0.37994 | 0.01197 | -0.086309 | -0.021157 | -0.079959 | 0.059155 | 0.021485 | -0.062717 | 0.011281 | 0.12501 | -0.036267 | -0.14758 | 0.039079 | 0.10105 | 120.7444 | 120.8835 | 121.0538 | 120.9556 | 121.0207 | 120.9619 | 121.101 | 121.0634 | 120.9792 | 0.011281 | 0.12501 | -0.036267 | -0.14758 | 0.039079 | 0.10105 | 120.7444 | 120.8835 | -0.027798 | -120.7331 | -0.075346 | -120.7807
1823.5625 | 121.4813 | -121.0693 | 0.38452 | 0.025705 | -0.095467 | -0.016578 | -0.079959 | 0.054577 | 0.012329 | -0.071874 | -0.011611 | 0.12043 | -0.059159 | -0.14758 | 0.048236 | 0.091891 | 120.7627 | 120.8926 | 121.095 | 120.9739 | 121.0528 | 120.9894 | 121.1239 | 121.0817 | 120.9975 | -0.011611 | 0.12043 | -0.059159 | -0.14758 | 0.048236 | 0.091891 | 120.7627 | 120.8926 | -0.059847 | -120.7743 | -0.1074 | -120.8219
1825.3281 | 121.582 | -121.0373 | 0.3479 | 0.021127 | -0.095467 | -0.021157 | -0.079959 | 0.059155 | 0.012329 | -0.062717 | -0.025347 | 0.11585 | -0.05458 | -0.143 | 0.043657 | 0.10105 | 120.7764 | 120.9155 | 121.0584 | 120.9418 | 121.0161 | 120.9573 | 121.0964 | 121.0496 | 120.9746 | -0.025347 | 0.11585 | -0.05458 | -0.143 | 0.043657 | 0.10105 | 120.7764 | 120.9155 | -0.069004 | -120.8018 | -0.098237 | -120.831
1827.0781 | 121.5866 | -121.0968 | 0.36163 | 0.030283 | -0.095467 | -0.016578 | -0.079959 | 0.054577 | 0.012329 | -0.071874 | 0.025017 | 0.12501 | -0.036267 | -0.143 | 0.043657 | 0.10105 | 120.7902 | 120.9339 | 121.1271 | 121.0013 | 121.0802 | 121.0168 | 121.1514 | 121.1091 | 121.0249 | 0.025017 | 0.12501 | -0.036267 | -0.143 | 0.043657 | 0.10105 | 120.7902 | 120.9339 | -0.01864 | -120.7652 | -0.079924 | -120.8264
1828.75 | 121.5271 | -121.1334 | 0.37994 | 0.025705 | -0.095467 | -0.007421 | -0.07538 | 0.054577 | 0.026064 | -0.062717 | 0.057066 | 0.12958 | 0.014094 | -0.14758 | 0.043657 | 0.10562 | 120.8085 | 120.9476 | 121.1591 | 121.038 | 121.126 | 121.058 | 121.188 | 121.1595 | 121.0707 | 0.057066 | 0.12958 | 0.014094 | -0.14758 | 0.043657 | 0.10562 | 120.8085 | 120.9476 | 0.013409 | -120.7514 | -0.029563 | -120.7944
1830.5156 | 121.6507 | -121.1197 | 0.33417 | 0.025705 | -0.095467 | -0.007421 | -0.07538 | 0.049999 | 0.026064 | -0.062717 | 0.020438 | 0.12501 | -0.013376 | -0.13842 | 0.043657 | 0.1102 | 120.8222 | 120.9613 | 121.1454 | 121.0242 | 121.1123 | 121.0443 | 121.1697 | 121.1458 | 121.057 | 0.020438 | 0.12501 | -0.013376 | -0.13842 | 0.043657 | 0.1102 | 120.8222 | 120.9613 | -0.023219 | -120.8018 | -0.057033 | -120.8356
1832.2031 | 121.4996 | -121.17 | 0.36163 | 0.021127 | -0.090888 | -0.016578 | -0.070802 | 0.054577 | 0.026064 | -0.053561 | 0.011281 | 0.12043 | 0.000359 | -0.143 | 0.039079 | 0.096469 | 120.8314 | 120.9659 | 121.1912 | 121.0792 | 121.1535 | 121.0992 | 121.2246 | 121.1961 | 121.1165 | 0.011281 | 0.12043 | 0.000359 | -0.143 | 0.039079 | 0.096469 | 120.8314 | 120.9659 | -0.027798 | -120.8201 | -0.03872 | -120.831
1833.9531 | 121.6278 | -121.138 | 0.35706 | 0.025705 | -0.095467 | -0.016578 | -0.066223 | 0.054577 | 0.021485 | -0.058139 | -0.025347 | 0.11585 | -0.05458 | -0.14758 | 0.039079 | 0.091891 | 120.8451 | 120.9796 | 121.1637 | 121.0425 | 121.1214 | 121.0718 | 121.1926 | 121.1595 | 121.0799 | -0.025347 | 0.11585 | -0.05458 | -0.14758 | 0.039079 | 0.091891 | 120.8451 | 120.9796 | -0.064426 | -120.8705 | -0.093659 | -120.8997
1835.7031 | 121.5866 | -121.1655 | 0.37994 | 0.025705 | -0.086309 | -0.012 | -0.070802 | 0.054577 | 0.016907 | -0.062717 | 0.01586 | 0.12501 | -0.027111 | -0.143 | 0.048236 | 0.096469 | 120.8588 | 120.9888 | 121.1912 | 121.0792 | 121.1535 | 121.0947 | 121.22 | 121.1824 | 121.1027 | 0.01586 | 0.12501 | -0.027111 | -0.143 | 0.048236 | 0.096469 | 120.8588 | 120.9888 | -0.032376 | -120.843 | -0.075347 | -120.886
1837.4375 | 121.6736 | -121.1609 | 0.3479 | 0.030283 | -0.10462 | 0.001736 | -0.07538 | 0.045421 | 0.021485 | -0.062717 | -0.048239 | 0.12043 | -0.050002 | -0.13842 | 0.034501 | 0.10105 | 120.8634 | 120.9979 | 121.1912 | 121.0563 | 121.1626 | 121.0855 | 121.2063 | 121.1824 | 121.0982 | -0.048239 | 0.12043 | -0.050002 | -0.13842 | 0.034501 | 0.10105 | 120.8634 | 120.9979 | -0.08274 | -120.9117 | -0.084503 | -120.9134
1839.125 | 121.6187 | -121.1929 | 0.37994 | 0.016548 | -0.095467 | -0.007421 | -0.084537 | 0.045421 | 0.012329 | -0.067295 | -0.020768 | 0.12501 | -0.022532 | -0.14758 | 0.043657 | 0.10105 | 120.8863 | 121.0208 | 121.2095 | 121.0975 | 121.1855 | 121.1084 | 121.2384 | 121.2053 | 121.1256 | -0.020768 | 0.12501 | -0.022532 | -0.14758 | 0.043657 | 0.10105 | 120.8863 | 121.0208 | -0.064425 | -120.9071 | -0.066189 | -120.9088
1840.8906 | 121.6415 | -121.2112 | 0.37079 | 0.016548 | -0.095467 | -0.016578 | -0.079959 | 0.049999 | 0.026064 | -0.071874 | -0.052818 | 0.13416 | -0.013376 | -0.14758 | 0.048236 | 0.096469 | 120.8863 | 121.0346 | 121.2278 | 121.1158 | 121.1947 | 121.1313 | 121.2612 | 121.2373 | 121.1394 | -0.052818 | 0.13416 | -0.013376 | -0.14758 | 0.048236 | 0.096469 | 120.8863 | 121.0346 | -0.10105 | -120.9391 | -0.061612 | -120.8997
1842.6406 | 121.582 | -121.2341 | 0.37537 | 0.025705 | -0.10462 | -0.012 | -0.070802 | 0.054577 | 0.021485 | -0.062717 | -0.011611 | 0.12043 | -0.022532 | -0.143 | 0.039079 | 0.10105 | 120.9092 | 121.0437 | 121.2598 | 121.1295 | 121.2221 | 121.1633 | 121.2887 | 121.2556 | 121.1714 | -0.011611 | 0.12043 | -0.022532 | -0.143 | 0.039079 | 0.10105 | 120.9092 | 121.0437 | -0.05069 | -120.9208 | -0.061611 | -120.9317
1844.3281 | 121.6644 | -121.2158 | 0.3479 | 0.016548 | -0.10004 | -0.016578 | -0.070802 | 0.049999 | 0.016907 | -0.067295 | -0.034504 | 0.11585 | -0.063737 | -0.143 | 0.043657 | 0.10105 | 120.9229 | 121.0483 | 121.2324 | 121.1158 | 121.1992 | 121.145 | 121.2658 | 121.2327 | 121.1485 | -0.034504 | 0.11585 | -0.063737 | -0.143 | 0.043657 | 0.10105 | 120.9229 | 121.0483 | -0.078161 | -120.9574 | -0.10739 | -120.9867
1846.0781 | 121.6324 | -121.2616 | 0.37537 | 0.016548 | -0.10004 | -0.007421 | -0.070802 | 0.049999 | 0.026064 | -0.067295 | 0.038752 | 0.13416 | -0.013376 | -0.13842 | 0.043657 | 0.10105 | 120.9367 | 121.0712 | 121.2781 | 121.1616 | 121.2542 | 121.1908 | 121.3116 | 121.2877 | 121.1943 | 0.038752 | 0.13416 | -0.013376 | -0.13842 | 0.043657 | 0.10105 | 120.9367 | 121.0712 | -0.004905 | -120.8979 | -0.057033 | -120.9501
1847.8281 | 121.6827 | -121.2708 | 0.35706 | 0.021127 | -0.10462 | -0.021157 | -0.07538 | 0.045421 | 0.021485 | -0.067295 | -0.043661 | 0.11585 | -0.063737 | -0.14758 | 0.048236 | 0.096469 | 120.9504 | 121.0941 | 121.2919 | 121.1661 | 121.2496 | 121.1954 | 121.3162 | 121.2922 | 121.2035 | -0.043661 | 0.11585 | -0.063737 | -0.14758 | 0.048236 | 0.096469 | 120.9504 | 121.0941 | -0.091897 | -120.9941 | -0.11197 | -121.0142
1849.5156 | 121.7422 | -121.2616 | 0.31586 | 0.021127 | -0.10462 | -0.016578 | -0.070802 | 0.054577 | 0.026064 | -0.062717 | -0.020768 | 0.12043 | -0.05458 | -0.143 | 0.048236 | 0.10105 | 120.9642 | 121.0987 | 121.2827 | 121.157 | 121.245 | 121.1908 | 121.3162 | 121.2877 | 121.1989 | -0.020768 | 0.12043 | -0.05458 | -0.143 | 0.048236 | 0.10105 | 120.9642 | 121.0987 | -0.069004 | -120.9849 | -0.10282 | -121.0187
1851.2031 | 121.6324 | -121.312 | 0.34332 | 0.021127 | -0.10004 | -0.007421 | -0.07538 | 0.045421 | 0.021485 | -0.062717 | -0.057396 | 0.12043 | -0.045424 | -0.13842 | 0.039079 | 0.10105 | 120.9825 | 121.1124 | 121.3331 | 121.2119 | 121.3045 | 121.2366 | 121.3574 | 121.3334 | 121.2492 | -0.057396 | 0.12043 | -0.045424 | -0.13842 | 0.039079 | 0.10105 | 120.9825 | 121.1124 | -0.096475 | -121.0399 | -0.084503 | -121.0279
1852.9531 | 121.7422 | -121.3211 | 0.33417 | 0.01197 | -0.10004 | -0.016578 | -0.07538 | 0.045421 | 0.012329 | -0.071874 | -0.007033 | 0.11585 | -0.036267 | -0.13842 | 0.039079 | 0.10562 | 120.9962 | 121.1353 | 121.3331 | 121.2211 | 121.3045 | 121.2457 | 121.3665 | 121.3334 | 121.2492 | -0.007033 | 0.11585 | -0.036267 | -0.13842 | 0.039079 | 0.10562 | 120.9962 | 121.1353 | -0.046112 | -121.0032 | -0.075346 | -121.0325
1854.7031 | 121.6461 | -121.3577 | 0.36163 | 0.016548 | -0.10004 | -0.016578 | -0.084537 | 0.045421 | 0.021485 | -0.071874 | -0.034504 | 0.11585 | -0.027111 | -0.14758 | 0.043657 | 0.096469 | 121.0099 | 121.149 | 121.3743 | 121.2577 | 121.3411 | 121.2732 | 121.4031 | 121.3792 | 121.2859 | -0.034504 | 0.11585 | -0.027111 | -0.14758 | 0.043657 | 0.096469 | 121.0099 | 121.149 | -0.078161 | -121.0444 | -0.070768 | -121.037
1856.4531 | 121.7239 | -121.3531 | 0.32501 | 0.01197 | -0.10462 | -0.021157 | -0.084537 | 0.045421 | 0.00775 | -0.067295 | 0.006703 | 0.12043 | -0.027111 | -0.143 | 0.048236 | 0.096469 | 121.0328 | 121.1673 | 121.3651 | 121.2485 | 121.332 | 121.2686 | 121.3986 | 121.3609 | 121.2859 | 0.006703 | 0.12043 | -0.027111 | -0.143 | 0.048236 | 0.096469 | 121.0328 | 121.1673 | -0.041533 | -121.0261 | -0.075347 | -121.0599
1858.1406 | 121.756 | -121.3348 | 0.32044 | 0.021127 | -0.10462 | -0.016578 | -0.079959 | 0.049999 | 0.021485 | -0.067295 | -0.011611 | 0.11585 | -0.050002 | -0.143 | 0.039079 | 0.10562 | 121.0328 | 121.1765 | 121.356 | 121.2302 | 121.3183 | 121.2549 | 121.3848 | 121.3563 | 121.2675 | -0.011611 | 0.11585 | -0.050002 | -0.143 | 0.039079 | 0.10562 | 121.0328 | 121.1765 | -0.05069 | -121.0444 | -0.089081 | -121.0828
1859.8906 | 121.7331 | -121.3852 | 0.35706 | 0.016548 | -0.10462 | -0.016578 | -0.07538 | 0.049999 | 0.021485 | -0.071874 | -0.043661 | 0.12043 | -0.031689 | -0.143 | 0.043657 | 0.10105 | 121.0511 | 121.1902 | 121.4017 | 121.2806 | 121.3686 | 121.3098 | 121.4352 | 121.4067 | 121.3133 | -0.043661 | 0.12043 | -0.031689 | -0.143 | 0.043657 | 0.10105 | 121.0511 | 121.1902 | -0.087318 | -121.0948 | -0.075346 | -121.0828
1861.6406 | 121.8018 | -121.3531 | 0.29297 | 0.021127 | -0.095467 | -0.016578 | -0.070802 | 0.054577 | 0.016907 | -0.062717 | -0.020768 | 0.10669 | -0.068315 | -0.143 | 0.043657 | 0.10562 | 121.0557 | 121.204 | 121.3743 | 121.2577 | 121.3366 | 121.2823 | 121.4077 | 121.3701 | 121.2904 | -0.020768 | 0.10669 | -0.068315 | -0.143 | 0.043657 | 0.10562 | 121.0557 | 121.204 | -0.064425 | -121.0765 | -0.11197 | -121.124
1863.4062 | 121.7834 | -121.4035 | 0.32501 | 0.016548 | -0.10004 | -0.007421 | -0.070802 | 0.045421 | 0.021485 | -0.076452 | -0.057396 | 0.12043 | -0.036267 | -0.13842 | 0.048236 | 0.10105 | 121.0832 | 121.2177 | 121.4201 | 121.3035 | 121.3961 | 121.3327 | 121.4489 | 121.425 | 121.3271 | -0.057396 | 0.12043 | -0.036267 | -0.13842 | 0.048236 | 0.10105 | 121.0832 | 121.2177 | -0.10563 | -121.1406 | -0.084503 | -121.1195
1865.1094 | 121.7377 | -121.4447 | 0.33875 | 0.025705 | -0.10462 | -0.012 | -0.070802 | 0.049999 | 0.021485 | -0.062717 | -0.025347 | 0.12043 | -0.045424 | -0.143 | 0.052814 | 0.1102 | 121.0878 | 121.2314 | 121.4704 | 121.3401 | 121.4327 | 121.3739 | 121.4947 | 121.4662 | 121.382 | -0.025347 | 0.12043 | -0.045424 | -0.143 | 0.052814 | 0.1102 | 121.0878 | 121.2314 | -0.078161 | -121.1131 | -0.098238 | -121.1332
1866.8594 | 121.7102 | -121.4447 | 0.3479 | 0.016548 | -0.1092 | -0.007421 | -0.084537 | 0.054577 | 0.012329 | -0.058139 | 0.020438 | 0.12501 | -0.063737 | -0.143 | 0.048236 | 0.10105 | 121.1061 | 121.236 | 121.4613 | 121.3355 | 121.4373 | 121.3602 | 121.4993 | 121.457 | 121.3866 | 0.020438 | 0.12501 | -0.063737 | -0.143 | 0.048236 | 0.10105 | 121.1061 | 121.236 | -0.027798 | -121.0856 | -0.11197 | -121.1698
1868.5469 | 121.8475 | -121.3898 | 0.3067 | 0.021127 | -0.1092 | -0.016578 | -0.070802 | 0.045421 | 0.016907 | -0.067295 | -0.034504 | 0.10669 | -0.031689 | -0.13842 | 0.052814 | 0.10105 | 121.1107 | 121.2452 | 121.4109 | 121.2806 | 121.3732 | 121.319 | 121.4352 | 121.4067 | 121.3225 | -0.034504 | 0.10669 | -0.031689 | -0.13842 | 0.052814 | 0.10105 | 121.1107 | 121.2452 | -0.087318 | -121.1452 | -0.084503 | -121.1423
1870.3125 | 121.7239 | -121.4722 | 0.32959 | 0.016548 | -0.10004 | -0.016578 | -0.079959 | 0.049999 | 0.016907 | -0.076452 | -0.052818 | 0.11127 | -0.050002 | -0.14758 | 0.043657 | 0.10562 | 121.1244 | 121.2497 | 121.4887 | 121.3721 | 121.4556 | 121.3922 | 121.5222 | 121.4891 | 121.3957 | -0.052818 | 0.11127 | -0.050002 | -0.14758 | 0.043657 | 0.10562 | 121.1244 | 121.2497 | -0.096475 | -121.1772 | -0.093659 | -121.1744
1872 | 121.8109 | -121.4539 | 0.31128 | 0.021127 | -0.11378 | -0.021157 | -0.079959 | 0.040843 | 0.012329 | -0.076452 | -0.052818 | 0.12043 | -0.077472 | -0.13384 | 0.048236 | 0.10105 | 121.1381 | 121.2726 | 121.475 | 121.3401 | 121.4327 | 121.3739 | 121.4947 | 121.4662 | 121.3774 | -0.052818 | 0.12043 | -0.077472 | -0.13384 | 0.048236 | 0.10105 | 121.1381 | 121.2726 | -0.10105 | -121.1909 | -0.12571 | -121.2156
1873.7344 | 121.7514 | -121.4813 | 0.31586 | 0.016548 | -0.11378 | -0.021157 | -0.084537 | 0.045421 | 0.00775 | -0.071874 | -0.020768 | 0.12043 | -0.063737 | -0.14758 | 0.048236 | 0.1102 | 121.1381 | 121.2818 | 121.4979 | 121.3675 | 121.4602 | 121.3968 | 121.5267 | 121.4891 | 121.4094 | -0.020768 | 0.12043 | -0.063737 | -0.14758 | 0.048236 | 0.1102 | 121.1381 | 121.2818 | -0.069004 | -121.1589 | -0.11197 | -121.2019
1875.5 | 121.7697 | -121.4859 | 0.32501 | 0.01197 | -0.10462 | -0.021157 | -0.084537 | 0.045421 | 0.00775 | -0.076452 | -0.061975 | 0.12501 | -0.040846 | -0.14758 | 0.048236 | 0.10562 | 121.161 | 121.2955 | 121.4979 | 121.3813 | 121.4647 | 121.4014 | 121.5313 | 121.4937 | 121.4094 | -0.061975 | 0.12501 | -0.040846 | -0.14758 | 0.048236 | 0.10562 | 121.161 | 121.2955 | -0.11021 | -121.223 | -0.089082 | -121.2019
1877.1875 | 121.8475 | -121.4584 | 0.31128 | 0.007391 | -0.11378 | -0.021157 | -0.079959 | 0.036265 | 0.012329 | -0.076452 | -0.066553 | 0.11127 | -0.068315 | -0.14758 | 0.052814 | 0.10105 | 121.1564 | 121.3001 | 121.4658 | 121.3447 | 121.4373 | 121.3785 | 121.4947 | 121.4708 | 121.382 | -0.066553 | 0.11127 | -0.068315 | -0.14758 | 0.052814 | 0.10105 | 121.1564 | 121.3001 | -0.11937 | -121.223 | -0.12113 | -121.2248
1878.9219 | 121.9254 | -121.4767 | 0.30212 | 0.01197 | -0.11378 | -0.025735 | -0.089116 | 0.036265 | 0.003172 | -0.076452 | -0.011611 | 0.12958 | -0.022532 | -0.143 | 0.048236 | 0.10562 | 121.1793 | 121.3138 | 121.4887 | 121.363 | 121.451 | 121.3876 | 121.513 | 121.4799 | 121.4003 | -0.011611 | 0.12958 | -0.022532 | -0.143 | 0.048236 | 0.10562 | 121.1793 | 121.3138 | -0.059847 | -121.1909 | -0.070768 | -121.2019
1880.6719 | 121.8018 | -121.5225 | 0.32044 | 0.021127 | -0.1092 | -0.021157 | -0.084537 | 0.036265 | 0.012329 | -0.08103 | -0.029925 | 0.12043 | -0.068315 | -0.143 | 0.052814 | 0.10562 | 121.1793 | 121.3138 | 121.5436 | 121.4133 | 121.5014 | 121.438 | 121.5588 | 121.5349 | 121.4415 | -0.029925 | 0.12043 | -0.068315 | -0.143 | 0.052814 | 0.10562 | 121.1793 | 121.3138 | -0.082739 | -121.2093 | -0.12113 | -121.2476
1882.3594 | 121.8155 | -121.5408 | 0.33875 | 0.01197 | -0.10462 | -0.016578 | -0.089116 | 0.036265 | 0.00775 | -0.076452 | -0.011611 | 0.11585 | -0.040846 | -0.143 | 0.048236 | 0.10562 | 121.1976 | 121.3322 | 121.5528 | 121.4362 | 121.5243 | 121.4517 | 121.5771 | 121.5486 | 121.4644 | -0.011611 | 0.11585 | -0.040846 | -0.143 | 0.048236 | 0.10562 | 121.1976 | 121.3322 | -0.059847 | -121.2093 | -0.089082 | -121.2385
1884.1094 | 121.8109 | -121.5134 | 0.33875 | -0.001765 | -0.1092 | -0.025735 | -0.10285 | 0.036265 | 0.00775 | -0.08103 | -0.020768 | 0.11585 | -0.008798 | -0.14758 | 0.052814 | 0.10562 | 121.1931 | 121.3367 | 121.5116 | 121.4042 | 121.4876 | 121.4105 | 121.5496 | 121.5211 | 121.4323 | -0.020768 | 0.11585 | -0.008798 | -0.14758 | 0.052814 | 0.10562 | 121.1931 | 121.3367 | -0.073582 | -121.2138 | -0.061612 | -121.2019
1885.875 | 121.9528 | -121.4813 | 0.29297 | -0.001765 | -0.12294 | -0.025735 | -0.093694 | 0.027109 | -0.001406 | -0.08103 | -0.020768 | 0.12958 | -0.050002 | -0.13842 | 0.043657 | 0.096469 | 121.2068 | 121.3459 | 121.4796 | 121.3584 | 121.4556 | 121.3876 | 121.5084 | 121.4799 | 121.4003 | -0.020768 | 0.12958 | -0.050002 | -0.13842 | 0.043657 | 0.096469 | 121.2068 | 121.3459 | -0.064425 | -121.2276 | -0.093659 | -121.2568
1888.9531 | 121.843 | -121.5729 | 0.33875 | 0.002813 | -0.12294 | -0.030314 | -0.098273 | 0.031687 | 0.003172 | -0.08103 | -0.034504 | 0.12501 | -0.05458 | -0.143 | 0.057392 | 0.10562 | 121.2251 | 121.3642 | 121.5757 | 121.4499 | 121.5426 | 121.4746 | 121.6046 | 121.576 | 121.4918 | -0.034504 | 0.12501 | -0.05458 | -0.143 | 0.057392 | 0.10562 | 121.2251 | 121.3642 | -0.091896 | -121.2596 | -0.11197 | -121.2797
1892.9375 | 121.9803 | -121.55 | 0.3067 | -0.006344 | -0.12294 | -0.034893 | -0.093694 | 0.031687 | -0.005985 | -0.08103 | 0.020438 | 0.1479 | -0.05458 | -0.143 | 0.048236 | 0.10562 | 121.2434 | 121.3825 | 121.5436 | 121.427 | 121.5151 | 121.4563 | 121.5817 | 121.544 | 121.469 | 0.020438 | 0.1479 | -0.05458 | -0.143 | 0.048236 | 0.10562 | 121.2434 | 121.3825 | -0.027798 | -121.223 | -0.10282 | -121.298
1899.2812 | 121.8933 | -121.5866 | 0.31586 | 0.002813 | -0.11836 | -0.034893 | -0.098273 | 0.031687 | 0.003172 | -0.08103 | -0.071132 | 0.12501 | -0.045424 | -0.14758 | 0.048236 | 0.1102 | 121.2755 | 121.41 | 121.5894 | 121.4682 | 121.5517 | 121.4883 | 121.6183 | 121.5898 | 121.5056 | -0.071132 | 0.12501 | -0.045424 | -0.14758 | 0.048236 | 0.1102 | 121.2755 | 121.41 | -0.11937 | -121.3466 | -0.09366 | -121.3209
1900.9844 | 121.9345 | -121.6049 | 0.32959 | -0.006344 | -0.12294 | -0.034893 | -0.089116 | 0.036265 | -0.001406 | -0.085608 | -0.07571 | 0.12043 | -0.05458 | -0.143 | 0.048236 | 0.10562 | 121.2846 | 121.4146 | 121.5986 | 121.482 | 121.57 | 121.5158 | 121.6412 | 121.6035 | 121.5193 | -0.07571 | 0.12043 | -0.05458 | -0.143 | 0.048236 | 0.10562 | 121.2846 | 121.4146 | -0.12395 | -121.3603 | -0.10282 | -121.3392
1902.75 | 122.0169 | -121.582 | 0.29297 | 0.007391 | -0.12752 | -0.039471 | -0.098273 | 0.022531 | -0.001406 | -0.085608 | -0.029925 | 0.12043 | -0.027111 | -0.143 | 0.048236 | 0.10562 | 121.2846 | 121.4146 | 121.5894 | 121.4545 | 121.5426 | 121.4838 | 121.6046 | 121.5806 | 121.4964 | -0.029925 | 0.12043 | -0.027111 | -0.143 | 0.048236 | 0.10562 | 121.2846 | 121.4146 | -0.078161 | -121.3146 | -0.075347 | -121.3117
1904.4375 | 121.9208 | -121.6232 | 0.32044 | 0.002813 | -0.1321 | -0.034893 | -0.089116 | 0.027109 | -0.001406 | -0.08103 | -0.043661 | 0.11127 | -0.036267 | -0.14758 | 0.052814 | 0.1102 | 121.303 | 121.442 | 121.626 | 121.4911 | 121.5883 | 121.5341 | 121.6503 | 121.6218 | 121.5422 | -0.043661 | 0.11127 | -0.036267 | -0.14758 | 0.052814 | 0.1102 | 121.303 | 121.442 | -0.096475 | -121.3466 | -0.089081 | -121.3392
1906.125 | 121.9162 | -121.637 | 0.33417 | -0.001765 | -0.13668 | -0.034893 | -0.098273 | 0.031687 | -0.005985 | -0.094765 | -0.061975 | 0.12501 | -0.063737 | -0.14758 | 0.052814 | 0.1102 | 121.3075 | 121.4466 | 121.6352 | 121.5003 | 121.6021 | 121.5387 | 121.6686 | 121.631 | 121.5422 | -0.061975 | 0.12501 | -0.063737 | -0.14758 | 0.052814 | 0.1102 | 121.3075 | 121.4466 | -0.11479 | -121.3695 | -0.11655 | -121.3713
1907.8906 | 122.049 | -121.5958 | 0.29297 | -0.001765 | -0.13668 | -0.034893 | -0.089116 | 0.031687 | -0.001406 | -0.08103 | -0.048239 | 0.12043 | -0.05458 | -0.143 | 0.057392 | 0.1102 | 121.3213 | 121.4558 | 121.594 | 121.4591 | 121.5609 | 121.5066 | 121.6275 | 121.5944 | 121.5147 | -0.048239 | 0.12043 | -0.05458 | -0.143 | 0.057392 | 0.1102 | 121.3213 | 121.4558 | -0.10563 | -121.3695 | -0.11197 | -121.3758
1909.6406 | 121.9299 | -121.6507 | 0.32959 | 0.002813 | -0.1321 | -0.04405 | -0.098273 | 0.031687 | -0.005985 | -0.094765 | -0.043661 | 0.11585 | -0.045424 | -0.143 | 0.057392 | 0.11936 | 121.3213 | 121.4649 | 121.6535 | 121.5186 | 121.6066 | 121.5524 | 121.6824 | 121.6447 | 121.5559 | -0.043661 | 0.11585 | -0.045424 | -0.143 | 0.057392 | 0.11936 | 121.3213 | 121.4649 | -0.10105 | -121.3649 | -0.10282 | -121.3667
1911.3906 | 122.0764 | -121.6095 | 0.28381 | 0.002813 | -0.1321 | -0.039471 | -0.093694 | 0.031687 | -0.001406 | -0.085608 | 0.002124 | 0.1479 | -0.008798 | -0.143 | 0.057392 | 0.11936 | 121.3258 | 121.4649 | 121.6123 | 121.4774 | 121.57 | 121.5158 | 121.6412 | 121.6081 | 121.5239 | 0.002124 | 0.1479 | -0.008798 | -0.143 | 0.057392 | 0.11936 | 121.3258 | 121.4649 | -0.055268 | -121.3237 | -0.06619 | -121.3346
1913.0781 | 122.0947 | -121.582 | 0.28839 | -0.006344 | -0.13668 | -0.039471 | -0.10285 | 0.022531 | -0.001406 | -0.08103 | -0.066553 | 0.12958 | -0.059159 | -0.143 | 0.057392 | 0.11936 | 121.3396 | 121.4741 | 121.5757 | 121.4454 | 121.5426 | 121.4792 | 121.6046 | 121.5806 | 121.501 | -0.066553 | 0.12958 | -0.059159 | -0.143 | 0.057392 | 0.11936 | 121.3396 | 121.4741 | -0.12394 | -121.4061 | -0.11655 | -121.3987
1914.8125 | 122.0901 | -121.6141 | 0.27924 | -0.001765 | -0.12752 | -0.039471 | -0.093694 | 0.027109 | -0.005985 | -0.085608 | -0.071132 | 0.13416 | -0.05458 | -0.143 | 0.057392 | 0.1102 | 121.3442 | 121.4787 | 121.6123 | 121.4866 | 121.5746 | 121.5204 | 121.6412 | 121.6081 | 121.5285 | -0.071132 | 0.13416 | -0.05458 | -0.143 | 0.057392 | 0.1102 | 121.3442 | 121.4787 | -0.12852 | -121.4153 | -0.11197 | -121.3987
1916.5781 | 122.0718 | -121.6278 | 0.32044 | -0.006344 | -0.13668 | -0.039471 | -0.10743 | 0.031687 | -0.005985 | -0.085608 | -0.061975 | 0.11585 | -0.05458 | -0.14758 | 0.048236 | 0.11478 | 121.3487 | 121.4878 | 121.6215 | 121.4911 | 121.5883 | 121.5204 | 121.6595 | 121.6218 | 121.5422 | -0.061975 | 0.11585 | -0.05458 | -0.14758 | 0.048236 | 0.11478 | 121.3487 | 121.4878 | -0.11021 | -121.4107 | -0.10282 | -121.4033
1918.2656 | 121.9482 | -121.6827 | 0.34332 | -0.006344 | -0.12752 | -0.048628 | -0.093694 | 0.027109 | -0.005985 | -0.085608 | 0.011281 | 0.13874 | 0.000359 | -0.14758 | 0.048236 | 0.11478 | 121.3579 | 121.4924 | 121.6764 | 121.5552 | 121.6341 | 121.589 | 121.7098 | 121.6768 | 121.5971 | 0.011281 | 0.13874 | 0.000359 | -0.14758 | 0.048236 | 0.11478 | 121.3579 | 121.4924 | -0.036955 | -121.3466 | -0.047877 | -121.3575
1920.0156 | 122.0627 | -121.6827 | 0.31128 | -0.006344 | -0.12752 | -0.034893 | -0.098273 | 0.022531 | -0.005985 | -0.085608 | -0.029925 | 0.12501 | -0.068315 | -0.143 | 0.071126 | 0.12851 | 121.3625 | 121.5061 | 121.6764 | 121.5552 | 121.6478 | 121.5845 | 121.7053 | 121.6768 | 121.5971 | -0.029925 | 0.12501 | -0.068315 | -0.143 | 0.071126 | 0.12851 | 121.3625 | 121.5061 | -0.10105 | -121.3924 | -0.13944 | -121.4308
1921.7656 | 122.1222 | -121.6553 | 0.29755 | -0.006344 | -0.1321 | -0.030314 | -0.098273 | 0.027109 | -0.005985 | -0.08103 | 0.029595 | 0.13416 | -0.017954 | -0.14758 | 0.06197 | 0.12851 | 121.3716 | 121.5061 | 121.6489 | 121.5232 | 121.625 | 121.557 | 121.6824 | 121.6493 | 121.5742 | 0.029595 | 0.13416 | -0.017954 | -0.14758 | 0.06197 | 0.12851 | 121.3716 | 121.5061 | -0.032375 | -121.342 | -0.079924 | -121.3896
1923.5156 | 122.1176 | -121.6415 | 0.27466 | 0.002813 | -0.12752 | -0.034893 | -0.093694 | 0.027109 | -0.005985 | -0.08103 | 0.006703 | 0.12501 | -0.022532 | -0.13842 | 0.048236 | 0.10562 | 121.3762 | 121.5199 | 121.6444 | 121.514 | 121.6066 | 121.5478 | 121.6686 | 121.6356 | 121.5605 | 0.006703 | 0.12501 | -0.022532 | -0.13842 | 0.048236 | 0.10562 | 121.3762 | 121.5199 | -0.041533 | -121.3695 | -0.070768 | -121.3987
1925.2031 | 121.9894 | -121.7331 | 0.3479 | 0.016548 | -0.1092 | -0.016578 | -0.089116 | 0.045421 | 0.003172 | -0.071874 | 0.006703 | 0.12958 | -0.027111 | -0.14758 | 0.066548 | 0.11936 | 121.3899 | 121.529 | 121.7496 | 121.6239 | 121.7165 | 121.644 | 121.7785 | 121.7363 | 121.6612 | 0.006703 | 0.12958 | -0.027111 | -0.14758 | 0.066548 | 0.11936 | 121.3899 | 121.529 | -0.059845 | -121.3832 | -0.093659 | -121.4171
1926.9375 | 122.0947 | -121.6873 | 0.28839 | 0.002813 | -0.1321 | -0.039471 | -0.093694 | 0.027109 | -0.005985 | -0.085608 | -0.025347 | 0.13416 | -0.040846 | -0.143 | 0.057392 | 0.12851 | 121.3945 | 121.5336 | 121.6901 | 121.5552 | 121.6478 | 121.5936 | 121.7144 | 121.6813 | 121.6017 | -0.025347 | 0.13416 | -0.040846 | -0.143 | 0.057392 | 0.12851 | 121.3945 | 121.5336 | -0.082739 | -121.4199 | -0.098238 | -121.4354
1928.6875 | 122.1222 | -121.669 | 0.3067 | -0.001765 | -0.11836 | -0.034893 | -0.098273 | 0.031687 | 0.003172 | -0.08103 | -0.01619 | 0.12958 | -0.036267 | -0.13842 | 0.052814 | 0.12394 | 121.3945 | 121.5427 | 121.6672 | 121.5506 | 121.6341 | 121.5707 | 121.7007 | 121.6722 | 121.588 | -0.01619 | 0.12958 | -0.036267 | -0.13842 | 0.052814 | 0.12394 | 121.3945 | 121.5427 | -0.069004 | -121.4107 | -0.089081 | -121.4308
1930.4375 | 122.168 | -121.6736 | 0.30212 | 0.002813 | -0.11836 | -0.030314 | -0.093694 | 0.027109 | -0.001406 | -0.08103 | 0.020438 | 0.15706 | -0.008798 | -0.14758 | 0.052814 | 0.12394 | 121.4083 | 121.5519 | 121.6764 | 121.5552 | 121.6433 | 121.5799 | 121.7007 | 121.6722 | 121.5926 | 0.020438 | 0.15706 | -0.008798 | -0.14758 | 0.052814 | 0.12394 | 121.4083 | 121.5519 | -0.032376 | -121.3878 | -0.061612 | -121.4171
1932.1406 | 122.168 | -121.7056 | 0.27924 | 0.007391 | -0.12294 | -0.030314 | -0.093694 | 0.040843 | 0.012329 | -0.085608 | 0.006703 | 0.12501 | -0.031689 | -0.14758 | 0.048236 | 0.10562 | 121.4128 | 121.5519 | 121.713 | 121.5827 | 121.6753 | 121.6119 | 121.7465 | 121.718 | 121.62 | 0.006703 | 0.12501 | -0.031689 | -0.14758 | 0.048236 | 0.10562 | 121.4128 | 121.5519 | -0.041533 | -121.4061 | -0.079925 | -121.4445
1933.8906 | 122.0627 | -121.7331 | 0.31128 | 0.016548 | -0.10462 | -0.016578 | -0.084537 | 0.049999 | 0.016907 | -0.067295 | 0.006703 | 0.1479 | -0.027111 | -0.13842 | 0.052814 | 0.10105 | 121.4174 | 121.5611 | 121.7496 | 121.6285 | 121.7165 | 121.6486 | 121.7831 | 121.75 | 121.6658 | 0.006703 | 0.1479 | -0.027111 | -0.13842 | 0.052814 | 0.10105 | 121.4174 | 121.5611 | -0.046111 | -121.4107 | -0.079925 | -121.4445
1935.625 | 122.1313 | -121.7056 | 0.28839 | 0.01197 | -0.12294 | -0.030314 | -0.084537 | 0.036265 | 0.003172 | -0.08103 | -0.011611 | 0.11585 | -0.027111 | -0.143 | 0.043657 | 0.1102 | 121.422 | 121.5656 | 121.7176 | 121.5827 | 121.6753 | 121.6211 | 121.7419 | 121.7088 | 121.6246 | -0.011611 | 0.11585 | -0.027111 | -0.143 | 0.043657 | 0.1102 | 121.422 | 121.5656 | -0.055268 | -121.4336 | -0.070768 | -121.4491
1937.375 | 122.1451 | -121.7056 | 0.28381 | 0.007391 | -0.12294 | -0.021157 | -0.093694 | 0.031687 | 0.00775 | -0.076452 | -0.011611 | 0.13416 | -0.050002 | -0.13842 | 0.048236 | 0.1102 | 121.4311 | 121.5702 | 121.713 | 121.5827 | 121.6845 | 121.6119 | 121.7373 | 121.7134 | 121.6292 | -0.011611 | 0.13416 | -0.050002 | -0.13842 | 0.048236 | 0.1102 | 121.4311 | 121.5702 | -0.059847 | -121.4428 | -0.098238 | -121.4811
1939.0625 | 122.0673 | -121.7422 | 0.33417 | 0.01197 | -0.1321 | -0.030314 | -0.084537 | 0.040843 | 0.00775 | -0.071874 | 0.01586 | 0.15248 | -0.027111 | -0.13842 | 0.048236 | 0.1102 | 121.4403 | 121.5748 | 121.7542 | 121.6102 | 121.7119 | 121.6577 | 121.7831 | 121.75 | 121.6704 | 0.01586 | 0.15248 | -0.027111 | -0.13842 | 0.048236 | 0.1102 | 121.4403 | 121.5748 | -0.032376 | -121.4244 | -0.075347 | -121.4674
1940.8125 | 122.1176 | -121.7377 | 0.32044 | 0.01197 | -0.11836 | -0.030314 | -0.084537 | 0.040843 | 0.00775 | -0.076452 | -0.007033 | 0.12958 | -0.022532 | -0.15216 | 0.048236 | 0.1102 | 121.4495 | 121.5931 | 121.7496 | 121.6193 | 121.7074 | 121.6531 | 121.7785 | 121.7454 | 121.6612 | -0.007033 | 0.12958 | -0.022532 | -0.15216 | 0.048236 | 0.1102 | 121.4495 | 121.5931 | -0.055269 | -121.4565 | -0.070768 | -121.472
1942.5625 | 122.1909 | -121.7331 | 0.28839 | 0.021127 | -0.11836 | -0.021157 | -0.07538 | 0.049999 | 0.021485 | -0.067295 | -0.002454 | 0.14332 | -0.022532 | -0.13842 | 0.039079 | 0.1102 | 121.4586 | 121.5977 | 121.7542 | 121.6147 | 121.7119 | 121.6577 | 121.7831 | 121.7546 | 121.6658 | -0.002454 | 0.14332 | -0.022532 | -0.13842 | 0.039079 | 0.1102 | 121.4586 | 121.5977 | -0.041533 | -121.4611 | -0.061611 | -121.4811
1944.25 | 122.1909 | -121.7102 | 0.29297 | 0.021127 | -0.11836 | -0.021157 | -0.07538 | 0.040843 | 0.00775 | -0.067295 | -0.007033 | 0.12958 | -0.027111 | -0.13842 | 0.057392 | 0.10105 | 121.4632 | 121.5977 | 121.7313 | 121.5918 | 121.689 | 121.6348 | 121.751 | 121.718 | 121.6429 | -0.007033 | 0.12958 | -0.027111 | -0.13842 | 0.057392 | 0.10105 | 121.4632 | 121.5977 | -0.064425 | -121.4702 | -0.084503 | -121.4903
1946.0156 | 122.1588 | -121.7422 | 0.29755 | 0.002813 | -0.11836 | -0.034893 | -0.089116 | 0.031687 | 0.003172 | -0.085608 | 0.002124 | 0.13874 | -0.004219 | -0.14758 | 0.043657 | 0.10562 | 121.4632 | 121.6068 | 121.7451 | 121.6239 | 121.7074 | 121.6531 | 121.7739 | 121.7454 | 121.6566 | 0.002124 | 0.13874 | -0.004219 | -0.14758 | 0.043657 | 0.10562 | 121.4632 | 121.6068 | -0.041533 | -121.4611 | -0.047876 | -121.4674
1947.7188 | 122.113 | -121.7743 | 0.32501 | 0.016548 | -0.11836 | -0.025735 | -0.089116 | 0.045421 | 0.012329 | -0.076452 | 0.002124 | 0.13874 | -0.036267 | -0.14758 | 0.052814 | 0.1102 | 121.4815 | 121.6114 | 121.7908 | 121.6559 | 121.7486 | 121.6852 | 121.8197 | 121.7866 | 121.6978 | 0.002124 | 0.13874 | -0.036267 | -0.14758 | 0.052814 | 0.1102 | 121.4815 | 121.6114 | -0.05069 | -121.4794 | -0.089081 | -121.5178
1949.4531 | 122.1863 | -121.7651 | 0.28839 | 0.007391 | -0.12752 | -0.030314 | -0.098273 | 0.036265 | -0.001406 | -0.085608 | -0.043661 | 0.13874 | -0.059159 | -0.14758 | 0.048236 | 0.10562 | 121.4769 | 121.6114 | 121.7725 | 121.6376 | 121.7348 | 121.6669 | 121.8014 | 121.7637 | 121.6795 | -0.043661 | 0.13874 | -0.059159 | -0.14758 | 0.048236 | 0.10562 | 121.4769 | 121.6114 | -0.091897 | -121.5206 | -0.1074 | -121.5361
1951.2031 | 122.0764 | -121.8338 | 0.32044 | 0.007391 | -0.11836 | -0.025735 | -0.079959 | 0.049999 | 0.016907 | -0.076452 | 0.002124 | 0.1479 | -0.045424 | -0.14758 | 0.048236 | 0.11478 | 121.4907 | 121.6206 | 121.8412 | 121.7154 | 121.8081 | 121.7538 | 121.8838 | 121.8507 | 121.7573 | 0.002124 | 0.1479 | -0.045424 | -0.14758 | 0.048236 | 0.11478 | 121.4907 | 121.6206 | -0.046112 | -121.4885 | -0.09366 | -121.5361
1952.9531 | 122.2046 | -121.788 | 0.28839 | 0.01197 | -0.12752 | -0.030314 | -0.084537 | 0.036265 | 0.012329 | -0.071874 | -0.034504 | 0.12958 | -0.036267 | -0.143 | 0.052814 | 0.11478 | 121.4907 | 121.6297 | 121.8 | 121.6605 | 121.7577 | 121.7035 | 121.8243 | 121.8004 | 121.7162 | -0.034504 | 0.12958 | -0.036267 | -0.143 | 0.052814 | 0.11478 | 121.4907 | 121.6297 | -0.087318 | -121.5252 | -0.089081 | -121.5269
1954.6406 | 122.168 | -121.8018 | 0.32044 | 0.002813 | -0.1321 | -0.030314 | -0.089116 | 0.031687 | -0.001406 | -0.085608 | -0.034504 | 0.12958 | -0.040846 | -0.143 | 0.052814 | 0.11936 | 121.5044 | 121.6297 | 121.8046 | 121.6697 | 121.7714 | 121.7126 | 121.8334 | 121.8004 | 121.7162 | -0.034504 | 0.12958 | -0.040846 | -0.143 | 0.052814 | 0.11936 | 121.5044 | 121.6297 | -0.087318 | -121.5389 | -0.09366 | -121.5452
1956.4062 | 122.2321 | -121.7651 | 0.29755 | -0.001765 | -0.12752 | -0.025735 | -0.089116 | 0.036265 | 0.003172 | -0.08103 | 0.020438 | 0.13416 | -0.040846 | -0.143 | 0.057392 | 0.1102 | 121.5136 | 121.6435 | 121.7634 | 121.6376 | 121.7394 | 121.676 | 121.8014 | 121.7683 | 121.6841 | 0.020438 | 0.13416 | -0.040846 | -0.143 | 0.057392 | 0.1102 | 121.5136 | 121.6435 | -0.036954 | -121.4931 | -0.098238 | -121.5544
1958.0938 | 122.1725 | -121.8292 | 0.31586 | -0.001765 | -0.13668 | -0.034893 | -0.098273 | 0.031687 | -0.001406 | -0.085608 | 0.057066 | 0.15248 | -0.008798 | -0.14758 | 0.052814 | 0.11478 | 121.5181 | 121.6526 | 121.8275 | 121.6925 | 121.7943 | 121.731 | 121.8609 | 121.8278 | 121.7436 | 0.057066 | 0.15248 | -0.008798 | -0.14758 | 0.052814 | 0.11478 | 121.5181 | 121.6526 | 0.004252 | -121.4611 | -0.061612 | -121.5269
1959.8438 | 122.1497 | -121.8201 | 0.31128 | 0.007391 | -0.11378 | -0.025735 | -0.084537 | 0.045421 | 0.00775 | -0.071874 | -0.020768 | 0.12501 | -0.05458 | -0.13842 | 0.06197 | 0.12851 | 121.5181 | 121.6526 | 121.8275 | 121.7063 | 121.7943 | 121.7355 | 121.8655 | 121.8278 | 121.7482 | -0.020768 | 0.12501 | -0.05458 | -0.13842 | 0.06197 | 0.12851 | 121.5181 | 121.6526 | -0.082738 | -121.5389 | -0.11655 | -121.5727
1961.6094 | 122.2504 | -121.8475 | 0.3067 | 0.002813 | -0.13668 | -0.039471 | -0.089116 | 0.017953 | -0.001406 | -0.090186 | 0.002124 | 0.13416 | -0.040846 | -0.143 | 0.080283 | 0.16972 | 121.5227 | 121.6618 | 121.8503 | 121.7109 | 121.8081 | 121.7584 | 121.8655 | 121.8461 | 121.7573 | 0.002124 | 0.13416 | -0.040846 | -0.143 | 0.080283 | 0.16972 | 121.5227 | 121.6618 | -0.078159 | -121.5206 | -0.12113 | -121.5636
1963.3594 | 122.1268 | -121.8567 | 0.32501 | -0.001765 | -0.13668 | -0.034893 | -0.10285 | 0.027109 | -0.001406 | -0.090186 | 0.034174 | 0.15248 | 0.004937 | -0.14758 | 0.075705 | 0.14683 | 121.5273 | 121.6755 | 121.8549 | 121.72 | 121.8218 | 121.7538 | 121.8838 | 121.8553 | 121.7665 | 0.034174 | 0.15248 | 0.004937 | -0.14758 | 0.075705 | 0.14683 | 121.5273 | 121.6755 | -0.041531 | -121.4931 | -0.070768 | -121.5224
1965.0469 | 122.2137 | -121.8521 | 0.30212 | 0.002813 | -0.1321 | -0.021157 | -0.084537 | 0.027109 | -0.001406 | -0.08103 | -0.066553 | 0.11585 | -0.05458 | -0.143 | 0.084861 | 0.15598 | 121.5364 | 121.6709 | 121.8549 | 121.72 | 121.831 | 121.7676 | 121.8792 | 121.8507 | 121.7711 | -0.066553 | 0.11585 | -0.05458 | -0.143 | 0.084861 | 0.15598 | 121.5364 | 121.6709 | -0.15141 | -121.603 | -0.13944 | -121.591
1966.7969 | 122.1405 | -121.8658 | 0.34332 | 0.002813 | -0.12752 | -0.034893 | -0.098273 | 0.031687 | 0.003172 | -0.085608 | -0.039082 | 0.11585 | -0.031689 | -0.13842 | 0.089439 | 0.1743 | 121.5456 | 121.6847 | 121.8687 | 121.7383 | 121.831 | 121.7676 | 121.8975 | 121.869 | 121.7802 | -0.039082 | 0.11585 | -0.031689 | -0.13842 | 0.089439 | 0.1743 | 121.5456 | 121.6847 | -0.12852 | -121.5847 | -0.12113 | -121.5773
1968.5469 | 122.1451 | -121.8979 | 0.33875 | 0.007391 | -0.12752 | -0.030314 | -0.098273 | 0.031687 | -0.001406 | -0.085608 | -0.01619 | 0.15706 | -0.059159 | -0.143 | 0.084861 | 0.14225 | 121.5502 | 121.6984 | 121.9053 | 121.7704 | 121.8676 | 121.7996 | 121.9296 | 121.8965 | 121.8123 | -0.01619 | 0.15706 | -0.059159 | -0.143 | 0.084861 | 0.14225 | 121.5502 | 121.6984 | -0.10105 | -121.5664 | -0.14402 | -121.6093
1970.2188 | 122.2458 | -121.8384 | 0.3067 | 0.01197 | -0.12752 | -0.021157 | -0.089116 | 0.040843 | 0.012329 | -0.076452 | -0.029925 | 0.14332 | -0.040846 | -0.143 | 0.066548 | 0.13767 | 121.5548 | 121.6938 | 121.8503 | 121.7109 | 121.8172 | 121.7493 | 121.8792 | 121.8507 | 121.7619 | -0.029925 | 0.14332 | -0.040846 | -0.143 | 0.066548 | 0.13767 | 121.5548 | 121.6938 | -0.096473 | -121.5847 | -0.10739 | -121.5956
1971.9688 | 122.2 | -121.875 | 0.32044 | 0.01197 | -0.1321 | -0.030314 | -0.084537 | 0.031687 | 0.012329 | -0.08103 | -0.029925 | 0.12501 | -0.036267 | -0.13842 | 0.075705 | 0.15598 | 121.5593 | 121.6938 | 121.887 | 121.7429 | 121.8447 | 121.7905 | 121.9067 | 121.8873 | 121.794 | -0.029925 | 0.12501 | -0.036267 | -0.13842 | 0.075705 | 0.15598 | 121.5593 | 121.6938 | -0.10563 | -121.5893 | -0.11197 | -121.5956
1973.6719 | 122.2046 | -121.8796 | 0.32501 | 0.007391 | -0.12752 | -0.025735 | -0.089116 | 0.045421 | 0.00775 | -0.076452 | -0.052818 | 0.13874 | -0.045424 | -0.143 | 0.080283 | 0.15141 | 121.5639 | 121.703 | 121.887 | 121.7521 | 121.8538 | 121.7905 | 121.925 | 121.8873 | 121.8031 | -0.052818 | 0.13874 | -0.045424 | -0.143 | 0.080283 | 0.15141 | 121.5639 | 121.703 | -0.1331 | -121.6167 | -0.12571 | -121.6093
1975.4375 | 122.2229 | -121.875 | 0.33417 | 0.002813 | -0.11836 | -0.021157 | -0.089116 | 0.031687 | 0.00775 | -0.076452 | -0.025347 | 0.12501 | -0.059159 | -0.143 | 0.10317 | 0.17887 | 121.5731 | 121.7167 | 121.8778 | 121.7566 | 121.8538 | 121.7859 | 121.9067 | 121.8828 | 121.7985 | -0.025347 | 0.12501 | -0.059159 | -0.143 | 0.10317 | 0.17887 | 121.5731 | 121.7167 | -0.12852 | -121.5984 | -0.16233 | -121.6322
1977.125 | 122.3145 | -121.8521 | 0.3067 | 0.002813 | -0.12294 | -0.030314 | -0.084537 | 0.036265 | 0.003172 | -0.08103 | 0.029595 | 0.14332 | 0.009515 | -0.14758 | 0.094017 | 0.18345 | 121.5731 | 121.7076 | 121.8549 | 121.7292 | 121.8218 | 121.7676 | 121.8884 | 121.8553 | 121.7711 | 0.029595 | 0.14332 | 0.009515 | -0.14758 | 0.094017 | 0.18345 | 121.5731 | 121.7076 | -0.064422 | -121.5435 | -0.084502 | -121.5636
1978.875 | 122.2275 | -121.875 | 0.32501 | 0.002813 | -0.12294 | -0.025735 | -0.084537 | 0.045421 | 0.016907 | -0.062717 | -0.043661 | 0.12958 | -0.050002 | -0.14758 | 0.10317 | 0.18803 | 121.5868 | 121.7213 | 121.8778 | 121.7521 | 121.8493 | 121.7905 | 121.9204 | 121.8919 | 121.8123 | -0.043661 | 0.12958 | -0.050002 | -0.14758 | 0.10317 | 0.18803 | 121.5868 | 121.7213 | -0.14683 | -121.6305 | -0.15318 | -121.6368
1980.625 | 122.1909 | -121.907 | 0.32044 | 0.007391 | -0.11378 | -0.025735 | -0.079959 | 0.045421 | 0.016907 | -0.071874 | -0.011611 | 0.13874 | -0.036267 | -0.13842 | 0.098596 | 0.18345 | 121.5777 | 121.7167 | 121.9144 | 121.7933 | 121.8813 | 121.8271 | 121.9525 | 121.924 | 121.8352 | -0.011611 | 0.13874 | -0.036267 | -0.13842 | 0.098596 | 0.18345 | 121.5777 | 121.7167 | -0.11021 | -121.5893 | -0.13486 | -121.6139
1982.3281 | 122.1817 | -121.907 | 0.33417 | -0.001765 | -0.12294 | -0.021157 | -0.084537 | 0.040843 | 0.003172 | -0.076452 | -0.011611 | 0.12043 | -0.017954 | -0.14758 | 0.10775 | 0.17887 | 121.5868 | 121.7213 | 121.9053 | 121.7841 | 121.8859 | 121.8225 | 121.9479 | 121.9102 | 121.8306 | -0.011611 | 0.12043 | -0.017954 | -0.14758 | 0.10775 | 0.17887 | 121.5868 | 121.7213 | -0.11936 | -121.5984 | -0.12571 | -121.6048
1984.0781 | 122.3419 | -121.8796 | 0.30212 | 0.016548 | -0.12752 | -0.025735 | -0.084537 | 0.036265 | 0.003172 | -0.076452 | 0.025017 | 0.15248 | -0.040846 | -0.14758 | 0.098596 | 0.18345 | 121.5914 | 121.7259 | 121.8961 | 121.7521 | 121.8538 | 121.795 | 121.9158 | 121.8828 | 121.8031 | 0.025017 | 0.15248 | -0.040846 | -0.14758 | 0.098596 | 0.18345 | 121.5914 | 121.7259 | -0.073579 | -121.5664 | -0.13944 | -121.6322
1985.8125 | 122.2092 | -121.8887 | 0.33417 | 0.01197 | -0.12752 | -0.030314 | -0.079959 | 0.036265 | 0.00775 | -0.071874 | -0.002454 | 0.13416 | -0.008798 | -0.14758 | 0.11691 | 0.21092 | 121.5914 | 121.7396 | 121.9007 | 121.7612 | 121.8584 | 121.8088 | 121.925 | 121.8965 | 121.8169 | -0.002454 | 0.13416 | -0.008798 | -0.14758 | 0.11691 | 0.21092 | 121.5914 | 121.7396 | -0.11936 | -121.5938 | -0.12571 | -121.6002
1987.5 | 122.2504 | -121.9299 | 0.32501 | 0.007391 | -0.11836 | -0.021157 | -0.084537 | 0.045421 | 0.012329 | -0.076452 | -0.034504 | 0.12958 | -0.036267 | -0.13842 | 0.10317 | 0.19261 | 121.5914 | 121.735 | 121.9373 | 121.8116 | 121.9088 | 121.8454 | 121.9754 | 121.9423 | 121.8535 | -0.034504 | 0.12958 | -0.036267 | -0.13842 | 0.10317 | 0.19261 | 121.5914 | 121.735 | -0.13768 | -121.6259 | -0.13944 | -121.6277
1989.25 | 122.2366 | -121.8979 | 0.32044 | 0.01197 | -0.12294 | -0.021157 | -0.089116 | 0.040843 | 0.016907 | -0.071874 | -0.048239 | 0.12958 | -0.050002 | -0.143 | 0.11691 | 0.2155 | 121.596 | 121.735 | 121.9099 | 121.7749 | 121.8767 | 121.8088 | 121.9387 | 121.9148 | 121.826 | -0.048239 | 0.12958 | -0.050002 | -0.143 | 0.11691 | 0.2155 | 121.596 | 121.735 | -0.16515 | -121.6442 | -0.16691 | -121.646
1990.9375 | 122.2687 | -121.9162 | 0.32501 | 0.01197 | -0.11836 | -0.021157 | -0.084537 | 0.045421 | 0.012329 | -0.062717 | 0.025017 | 0.13416 | -0.040846 | -0.14758 | 0.11691 | 0.20634 | 121.6143 | 121.7533 | 121.9282 | 121.7978 | 121.895 | 121.8317 | 121.9616 | 121.9285 | 121.8535 | 0.025017 | 0.13416 | -0.040846 | -0.14758 | 0.11691 | 0.20634 | 121.6143 | 121.7533 | -0.091891 | -121.5893 | -0.15775 | -121.6551
1992.6875 | 122.3145 | -121.9254 | 0.30212 | 0.01197 | -0.11836 | -0.025735 | -0.089116 | 0.045421 | 0.012329 | -0.071874 | -0.007033 | 0.14332 | -0.036267 | -0.14758 | 0.052814 | 0.1102 | 121.6097 | 121.7488 | 121.9373 | 121.807 | 121.8996 | 121.8362 | 121.9708 | 121.9377 | 121.8535 | -0.007033 | 0.14332 | -0.036267 | -0.14758 | 0.052814 | 0.1102 | 121.6097 | 121.7488 | -0.059847 | -121.6167 | -0.089081 | -121.646
1994.4375 | 122.2412 | -121.9391 | 0.35248 | 0.021127 | -0.11378 | -0.021157 | -0.070802 | 0.054577 | 0.026064 | -0.058139 | 0.011281 | 0.1479 | -0.045424 | -0.13842 | 0.066548 | 0.11936 | 121.6189 | 121.7625 | 121.9602 | 121.8253 | 121.9179 | 121.8683 | 121.9937 | 121.9652 | 121.8809 | 0.011281 | 0.1479 | -0.045424 | -0.13842 | 0.066548 | 0.11936 | 121.6189 | 121.7625 | -0.055267 | -121.6076 | -0.11197 | -121.6643
1996.1406 | 122.2412 | -121.9666 | 0.34332 | 0.002813 | -0.11836 | -0.021157 | -0.07538 | 0.036265 | 0.016907 | -0.076452 | 0.025017 | 0.15248 | -0.008798 | -0.13842 | 0.13064 | 0.22008 | 121.6326 | 121.7671 | 121.9694 | 121.8482 | 121.9454 | 121.8912 | 122.0028 | 121.9835 | 121.8901 | 0.025017 | 0.15248 | -0.008798 | -0.13842 | 0.13064 | 0.22008 | 121.6326 | 121.7671 | -0.10563 | -121.6076 | -0.13944 | -121.6414
1997.8906 | 122.3648 | -121.875 | 0.28381 | 0.01197 | -0.11836 | -0.021157 | -0.084537 | 0.049999 | 0.016907 | -0.071874 | -0.011611 | 0.11585 | -0.017954 | -0.143 | 0.12149 | 0.20176 | 121.6326 | 121.7671 | 121.887 | 121.7566 | 121.8538 | 121.7905 | 121.925 | 121.8919 | 121.8031 | -0.011611 | 0.11585 | -0.017954 | -0.143 | 0.12149 | 0.20176 | 121.6326 | 121.7671 | -0.1331 | -121.6442 | -0.13944 | -121.6505
1999.6406 | 122.2824 | -121.9482 | 0.33875 | 0.030283 | -0.11378 | -0.012 | -0.066223 | 0.054577 | 0.026064 | -0.062717 | -0.020768 | 0.14332 | -0.031689 | -0.143 | 0.10775 | 0.19719 | 121.6372 | 121.7854 | 121.9785 | 121.8345 | 121.9362 | 121.882 | 122.0028 | 121.9743 | 121.8855 | -0.020768 | 0.14332 | -0.031689 | -0.143 | 0.10775 | 0.19719 | 121.6372 | 121.7854 | -0.12852 | -121.6579 | -0.13944 | -121.6689
2001.3906 | 122.3328 | -121.9299 | 0.31128 | 0.021127 | -0.1092 | -0.012 | -0.079959 | 0.045421 | 0.016907 | -0.08103 | 0.01586 | 0.14332 | -0.022532 | -0.14758 | 0.10317 | 0.18803 | 121.6555 | 121.7991 | 121.9511 | 121.8207 | 121.9179 | 121.85 | 121.9754 | 121.9468 | 121.8489 | 0.01586 | 0.14332 | -0.022532 | -0.14758 | 0.10317 | 0.18803 | 121.6555 | 121.7991 | -0.087314 | -121.6396 | -0.12571 | -121.678
2003.0781 | 122.3053 | -121.962 | 0.33875 | 0.021127 | -0.11378 | -0.012 | -0.079959 | 0.049999 | 0.021485 | -0.062717 | -0.007033 | 0.1479 | -0.013376 | -0.143 | 0.10775 | 0.17887 | 121.6509 | 121.7945 | 121.9831 | 121.8482 | 121.95 | 121.882 | 122.012 | 121.9835 | 121.8993 | -0.007033 | 0.1479 | -0.013376 | -0.143 | 0.10775 | 0.17887 | 121.6509 | 121.7945 | -0.11478 | -121.6579 | -0.12113 | -121.6643
2004.8281 | 122.2916 | -121.9757 | 0.33417 | 0.01197 | -0.11378 | -0.016578 | -0.07538 | 0.049999 | 0.012329 | -0.076452 | -0.020768 | 0.1479 | -0.050002 | -0.143 | 0.10775 | 0.19261 | 121.6601 | 121.7991 | 121.9877 | 121.8619 | 121.9591 | 121.9003 | 122.0257 | 121.988 | 121.8993 | -0.020768 | 0.1479 | -0.050002 | -0.143 | 0.10775 | 0.19261 | 121.6601 | 121.7991 | -0.12852 | -121.6808 | -0.15775 | -121.7101
2006.5312 | 122.2687 | -121.9711 | 0.33417 | 0.007391 | -0.11378 | -0.021157 | -0.07538 | 0.049999 | 0.016907 | -0.067295 | -0.011611 | 0.15706 | -0.040846 | -0.14758 | 0.10317 | 0.19261 | 121.6601 | 121.8037 | 121.9785 | 121.8573 | 121.95 | 121.8958 | 122.0211 | 121.988 | 121.9038 | -0.011611 | 0.15706 | -0.040846 | -0.14758 | 0.10317 | 0.19261 | 121.6601 | 121.8037 | -0.11478 | -121.6717 | -0.14402 | -121.7009
2008.2969 | 122.3145 | -121.9711 | 0.31128 | 0.025705 | -0.11378 | -0.012 | -0.07538 | 0.049999 | 0.026064 | -0.067295 | 0.011281 | 0.13416 | -0.013376 | -0.143 | 0.10775 | 0.18803 | 121.6692 | 121.8083 | 121.9968 | 121.8573 | 121.9591 | 121.8958 | 122.0211 | 121.9972 | 121.9038 | 0.011281 | 0.13416 | -0.013376 | -0.143 | 0.10775 | 0.18803 | 121.6692 | 121.8083 | -0.096471 | -121.6579 | -0.12113 | -121.6826
2010.0469 | 122.3099 | -121.9849 | 0.32044 | 0.016548 | -0.11378 | -0.016578 | -0.084537 | 0.049999 | 0.016907 | -0.062717 | -0.007033 | 0.13874 | -0.031689 | -0.143 | 0.098596 | 0.18803 | 121.6784 | 121.8129 | 122.0014 | 121.8711 | 121.9683 | 121.9003 | 122.0349 | 122.0018 | 121.9221 | -0.007033 | 0.13874 | -0.031689 | -0.143 | 0.098596 | 0.18803 | 121.6784 | 121.8129 | -0.10563 | -121.6854 | -0.13029 | -121.7101
2011.7969 | 122.287 | -122.0215 | 0.33875 | 0.025705 | -0.1092 | -0.012 | -0.07538 | 0.054577 | 0.030642 | -0.067295 | -0.034504 | 0.12501 | -0.059159 | -0.13842 | 0.10775 | 0.18803 | 121.6875 | 121.8312 | 122.0472 | 121.9123 | 122.0095 | 121.9461 | 122.0761 | 122.0521 | 121.9542 | -0.034504 | 0.12501 | -0.059159 | -0.13842 | 0.10775 | 0.18803 | 121.6875 | 121.8312 | -0.14226 | -121.722 | -0.16691 | -121.7467
2013.4844 | 122.3557 | -121.9711 | 0.29755 | 0.030283 | -0.11378 | -0.012 | -0.079959 | 0.054577 | 0.026064 | -0.067295 | 0.066223 | 0.17079 | 0.004937 | -0.14758 | 0.094017 | 0.18345 | 121.683 | 121.8174 | 122.0014 | 121.8573 | 121.9591 | 121.8912 | 122.0257 | 121.9972 | 121.9038 | 0.066223 | 0.17079 | 0.004937 | -0.14758 | 0.094017 | 0.18345 | 121.683 | 121.8174 | -0.027794 | -121.6167 | -0.08908 | -121.678
2015.2344 | 122.4197 | -121.9666 | 0.29297 | 0.021127 | -0.11378 | -0.007421 | -0.07538 | 0.049999 | 0.021485 | -0.062717 | 0.066223 | 0.1479 | 0.009515 | -0.14758 | 0.10775 | 0.19261 | 121.6921 | 121.8266 | 121.9877 | 121.8528 | 121.9591 | 121.8912 | 122.0166 | 121.988 | 121.9038 | 0.066223 | 0.1479 | 0.009515 | -0.14758 | 0.10775 | 0.19261 | 121.6921 | 121.8266 | -0.041529 | -121.6259 | -0.098237 | -121.6826
2017 | 122.4152 | -121.9803 | 0.28839 | 0.025705 | -0.11378 | -0.007421 | -0.07538 | 0.054577 | 0.021485 | -0.071874 | 0.061645 | 0.1479 | 0.032407 | -0.13842 | 0.10317 | 0.20176 | 121.6921 | 121.8312 | 122.006 | 121.8665 | 121.9729 | 121.9049 | 122.0349 | 122.0018 | 121.9084 | 0.061645 | 0.1479 | 0.032407 | -0.13842 | 0.10317 | 0.20176 | 121.6921 | 121.8312 | -0.041529 | -121.6305 | -0.070767 | -121.6597
2018.7031 | 122.4197 | -121.9849 | 0.31128 | 0.021127 | -0.11378 | -0.007421 | -0.07538 | 0.054577 | 0.026064 | -0.071874 | 0.10285 | 0.16622 | 0.041563 | -0.14758 | 0.10775 | 0.19261 | 121.7013 | 121.8358 | 122.006 | 121.8711 | 121.9774 | 121.9095 | 122.0394 | 122.0109 | 121.913 | 0.10285 | 0.16622 | 0.041563 | -0.14758 | 0.10775 | 0.19261 | 121.7013 | 121.8358 | -0.004901 | -121.5984 | -0.066189 | -121.6597
2020.4531 | 122.1817 | -122.113 | 0.25177 | 0.076067 | -0.063415 | 0.038365 | -0.020438 | 0.10493 | 0.067269 | -0.012357 | -0.011611 | 0.13416 | -0.027111 | -0.143 | 0.043657 | 0.10105 | 0.062662 | 0.12044 | 122.1891 | 122.0496 | 122.1514 | 122.0926 | 122.218 | 122.1803 | 122.1007 | -0.011611 | 0.13416 | -0.027111 | -0.143 | 0.043657 | 0.10105 | 0.062662 | 0.12044 | -0.055268 | -0.074273 | -0.070768 | -0.089773
2022.1406 | 122.2916 | -122.0947 | 0.22888 | 0.076067 | -0.058836 | 0.033786 | -0.025017 | 0.11409 | 0.076426 | -0.026092 | 0.034174 | 0.15706 | 0.000359 | -0.143 | 0.039079 | 0.10562 | -0.015171 | 0.028875 | 122.1708 | 122.0359 | 122.1285 | 122.0697 | 122.2088 | 122.1712 | 122.0686 | 0.034174 | 0.15706 | 0.000359 | -0.143 | 0.039079 | 0.10562 | -0.015171 | 0.028875 | -0.004905 | 0.049345 | -0.03872 | 0.01553
2023.9062 | 122.4106 | -122.0581 | 0.19684 | 0.080646 | -0.072572 | 0.033786 | -0.029595 | 0.10036 | 0.067269 | -0.026092 | 0.057066 | 0.14332 | 0.027829 | -0.13842 | 0.048236 | 0.096469 | -0.024328 | 0.024297 | 122.1388 | 121.9855 | 122.0919 | 122.0285 | 122.1585 | 122.1254 | 122.032 | 0.057066 | 0.14332 | 0.027829 | -0.13842 | 0.048236 | 0.096469 | -0.024328 | 0.024297 | 0.00883 | 0.081394 | -0.020407 | 0.052157
2025.6562 | 122.4106 | -122.0856 | 0.20599 | 0.071489 | -0.077151 | 0.029208 | -0.025017 | 0.10493 | 0.071848 | -0.026092 | 0.084537 | 0.17079 | 0.032407 | -0.143 | 0.043657 | 0.10105 | -0.024328 | 0.019719 | 122.1571 | 122.0084 | 122.1148 | 122.0606 | 122.1905 | 122.1574 | 122.0595 | 0.084537 | 0.17079 | 0.032407 | -0.143 | 0.043657 | 0.10105 | -0.024328 | 0.019719 | 0.04088 | 0.10887 | -0.01125 | 0.056735
2027.3438 | 122.4472 | -122.0535 | 0.21973 | 0.071489 | -0.067994 | 0.033786 | -0.025017 | 0.095778 | 0.081005 | -0.026092 | 0.098273 | 0.17537 | 0.046142 | -0.13842 | 0.034501 | 0.096469 | -0.038063 | 0.010563 | 122.125 | 121.9855 | 122.0873 | 122.0285 | 122.1493 | 122.1345 | 122.0274 | 0.098273 | 0.17537 | 0.046142 | -0.13842 | 0.034501 | 0.096469 | -0.038063 | 0.010563 | 0.063772 | 0.13634 | 0.011641 | 0.084205
2029.0781 | 122.3145 | -122.1542 | 0.22888 | 0.076067 | -0.063415 | 0.033786 | -0.025017 | 0.10493 | 0.090161 | -0.021514 | 0.034174 | 0.16164 | 0.004937 | -0.143 | 0.039079 | 0.091891 | -0.033484 | 0.010563 | 122.2303 | 122.0908 | 122.188 | 122.1292 | 122.2592 | 122.2444 | 122.1327 | 0.034174 | 0.16164 | 0.004937 | -0.143 | 0.039079 | 0.091891 | -0.033484 | 0.010563 | -0.004905 | 0.067658 | -0.034142 | 0.038421
2030.8281 | 122.3236 | -122.1222 | 0.22888 | 0.076067 | -0.063415 | 0.038365 | -0.025017 | 0.10036 | 0.076426 | -0.021514 | 0.038752 | 0.15706 | -0.008798 | -0.143 | 0.039079 | 0.091891 | -0.033484 | 0.005985 | 122.1983 | 122.0588 | 122.1606 | 122.0972 | 122.2225 | 122.1986 | 122.1007 | 0.038752 | 0.15706 | -0.008798 | -0.143 | 0.039079 | 0.091891 | -0.033484 | 0.005985 | -0.000327 | 0.072236 | -0.047877 | 0.024686
2032.5781 | 122.319 | -122.1405 | 0.23804 | 0.076067 | -0.058836 | 0.029208 | -0.029595 | 0.10493 | 0.076426 | -0.026092 | 0.057066 | 0.17537 | 0.055298 | -0.13842 | 0.034501 | 0.10105 | -0.028906 | 0.010563 | 122.2166 | 122.0817 | 122.1697 | 122.1109 | 122.2454 | 122.2169 | 122.1144 | 0.057066 | 0.17537 | 0.055298 | -0.13842 | 0.034501 | 0.10105 | -0.028906 | 0.010563 | 0.022565 | 0.085972 | 0.020797 | 0.084204
2034.3281 | 122.4518 | -122.1039 | 0.19684 | 0.071489 | -0.058836 | 0.029208 | -0.020438 | 0.10951 | 0.067269 | -0.021514 | 0.070802 | 0.17995 | 0.041563 | -0.14758 | 0.043657 | 0.091891 | -0.038063 | 0.005985 | 122.1754 | 122.045 | 122.1331 | 122.0834 | 122.2134 | 122.1712 | 122.0824 | 0.070802 | 0.17995 | 0.041563 | -0.14758 | 0.043657 | 0.091891 | -0.038063 | 0.005985 | 0.027145 | 0.10887 | -0.002094 | 0.079626
2036.0156 | 122.374 | -122.1359 | 0.21057 | 0.076067 | -0.067994 | 0.033786 | -0.020438 | 0.10036 | 0.071848 | -0.035248 | 0.066223 | 0.15706 | 0.014094 | -0.14758 | 0.043657 | 0.096469 | -0.033484 | 0.010563 | 122.212 | 122.0679 | 122.1697 | 122.1155 | 122.2363 | 122.2078 | 122.1007 | 0.066223 | 0.15706 | 0.014094 | -0.14758 | 0.043657 | 0.096469 | -0.033484 | 0.010563 | 0.022566 | 0.099707 | -0.029563 | 0.047578
2037.7656 | 122.4472 | -122.1268 | 0.21973 | 0.071489 | -0.058836 | 0.033786 | -0.034174 | 0.10951 | 0.076426 | -0.026092 | 0.052488 | 0.17079 | -0.008798 | -0.143 | 0.043657 | 0.096469 | -0.033484 | 0.010563 | 122.1983 | 122.0679 | 122.1606 | 122.0926 | 122.2363 | 122.2032 | 122.1007 | 0.052488 | 0.17079 | -0.008798 | -0.143 | 0.043657 | 0.096469 | -0.033484 | 0.010563 | 0.008831 | 0.085972 | -0.052455 | 0.024686
2039.4531 | 122.374 | -122.1222 | 0.2243 | 0.06691 | -0.063415 | 0.033786 | -0.020438 | 0.10036 | 0.071848 | -0.026092 | 0.07538 | 0.16164 | -0.008798 | -0.143 | 0.039079 | 0.096469 | -0.033484 | 0.001406 | 122.1891 | 122.0588 | 122.156 | 122.1018 | 122.2225 | 122.194 | 122.0961 | 0.07538 | 0.16164 | -0.008798 | -0.143 | 0.039079 | 0.096469 | -0.033484 | 0.001406 | 0.036301 | 0.10886 | -0.047877 | 0.024686
2041.2031 | 122.3785 | -122.1542 | 0.22888 | 0.06691 | -0.072572 | 0.033786 | -0.020438 | 0.10951 | 0.071848 | -0.026092 | 0.066223 | 0.15706 | 0.046142 | -0.143 | 0.043657 | 0.10105 | -0.033484 | 0.001406 | 122.2211 | 122.0817 | 122.188 | 122.1338 | 122.2637 | 122.2261 | 122.1281 | 0.066223 | 0.15706 | 0.046142 | -0.143 | 0.043657 | 0.10105 | -0.033484 | 0.001406 | 0.022566 | 0.099707 | 0.002485 | 0.079626
2042.9531 | 122.3831 | -122.1725 | 0.2243 | 0.06691 | -0.058836 | 0.033786 | -0.020438 | 0.10493 | 0.071848 | -0.021514 | 0.034174 | 0.15706 | -0.017954 | -0.14758 | 0.043657 | 0.096469 | -0.038063 | 0.010563 | 122.2395 | 122.1137 | 122.2063 | 122.1521 | 122.2775 | 122.2444 | 122.151 | 0.034174 | 0.15706 | -0.017954 | -0.14758 | 0.043657 | 0.096469 | -0.038063 | 0.010563 | -0.009483 | 0.072237 | -0.061611 | 0.020109
2044.7031 | 122.3557 | -122.1863 | 0.24261 | 0.06691 | -0.063415 | 0.029208 | -0.029595 | 0.10036 | 0.076426 | -0.016936 | 0.061645 | 0.17079 | 0.014094 | -0.143 | 0.039079 | 0.096469 | -0.038063 | 0.005985 | 122.2532 | 122.1229 | 122.2155 | 122.1567 | 122.2866 | 122.2627 | 122.1693 | 0.061645 | 0.17079 | 0.014094 | -0.143 | 0.039079 | 0.096469 | -0.038063 | 0.005985 | 0.022566 | 0.099708 | -0.024985 | 0.052157
2046.3906 | 122.3557 | -122.1909 | 0.21515 | 0.071489 | -0.063415 | 0.038365 | -0.025017 | 0.10493 | 0.071848 | -0.021514 | 0.029595 | 0.17079 | 0.009515 | -0.143 | 0.043657 | 0.091891 | -0.038063 | 0.001406 | 122.2623 | 122.1274 | 122.2292 | 122.1658 | 122.2958 | 122.2627 | 122.1693 | 0.029595 | 0.17079 | 0.009515 | -0.143 | 0.043657 | 0.091891 | -0.038063 | 0.001406 | -0.014062 | 0.067658 | -0.034142 | 0.047578
2048.1406 | 122.5067 | -122.1405 | 0.20142 | 0.06691 | -0.077151 | 0.029208 | -0.025017 | 0.10493 | 0.081005 | -0.016936 | 0.070802 | 0.16622 | 0.041563 | -0.13842 | 0.039079 | 0.10105 | -0.038063 | 0.005985 | 122.2074 | 122.0634 | 122.1697 | 122.1155 | 122.2454 | 122.2215 | 122.1236 | 0.070802 | 0.16622 | 0.041563 | -0.13842 | 0.039079 | 0.10105 | -0.038063 | 0.005985 | 0.031723 | 0.10887 | 0.002484 | 0.079626
2049.8281 | 122.3694 | -122.1909 | 0.22888 | 0.080646 | -0.067994 | 0.038365 | -0.025017 | 0.095778 | 0.076426 | -0.021514 | 0.034174 | 0.17079 | -0.022532 | -0.14758 | 0.043657 | 0.091891 | -0.051798 | 0.005985 | 122.2715 | 122.1229 | 122.2292 | 122.1658 | 122.2866 | 122.2673 | 122.1693 | 0.034174 | 0.17079 | -0.022532 | -0.14758 | 0.043657 | 0.091891 | -0.051798 | 0.005985 | -0.009483 | 0.085972 | -0.066189 | 0.029266
2051.5781 | 122.4472 | -122.1451 | 0.21057 | 0.071489 | -0.067994 | 0.020051 | -0.025017 | 0.10493 | 0.071848 | -0.021514 | 0.043331 | 0.1479 | 0.009515 | -0.13842 | 0.043657 | 0.091891 | -0.038063 | 0.005985 | 122.2166 | 122.0771 | 122.1651 | 122.1201 | 122.25 | 122.2169 | 122.1236 | 0.043331 | 0.1479 | 0.009515 | -0.13842 | 0.043657 | 0.091891 | -0.038063 | 0.005985 | -0.000326 | 0.081394 | -0.034142 | 0.047578
2053.3281 | 122.4838 | -122.1771 | 0.20599 | 0.06691 | -0.063415 | 0.042944 | -0.029595 | 0.10036 | 0.071848 | -0.016936 | 0.079959 | 0.15706 | 0.018672 | -0.14758 | 0.043657 | 0.096469 | -0.04722 | -0.003172 | 122.244 | 122.1137 | 122.2201 | 122.1475 | 122.2775 | 122.249 | 122.1602 | 0.079959 | 0.15706 | 0.018672 | -0.14758 | 0.043657 | 0.096469 | -0.04722 | -0.003172 | 0.036302 | 0.12718 | -0.024985 | 0.065892
2055.0781 | 122.3877 | -122.1863 | 0.2243 | 0.06691 | -0.067994 | 0.033786 | -0.025017 | 0.10036 | 0.071848 | -0.021514 | 0.034174 | 0.15706 | -0.004219 | -0.13842 | 0.043657 | 0.087313 | -0.038063 | -0.003172 | 122.2532 | 122.1183 | 122.2201 | 122.1613 | 122.2866 | 122.2581 | 122.1648 | 0.034174 | 0.15706 | -0.004219 | -0.13842 | 0.043657 | 0.087313 | -0.038063 | -0.003172 | -0.009483 | 0.072237 | -0.047876 | 0.033844
2056.7656 | 122.3923 | -122.2366 | 0.23346 | 0.076067 | -0.063415 | 0.024629 | -0.025017 | 0.10493 | 0.076426 | -0.016936 | 0.038752 | 0.16622 | 0.004937 | -0.15216 | 0.039079 | 0.096469 | -0.038063 | 0.005985 | 122.3127 | 122.1732 | 122.2613 | 122.2116 | 122.3416 | 122.3131 | 122.2197 | 0.038752 | 0.16622 | 0.004937 | -0.15216 | 0.039079 | 0.096469 | -0.038063 | 0.005985 | -0.000327 | 0.076815 | -0.034142 | 0.043
2058.5156 | 122.5113 | -122.1725 | 0.21515 | 0.071489 | -0.067994 | 0.024629 | -0.025017 | 0.10493 | 0.067269 | -0.021514 | 0.052488 | 0.17079 | -0.004219 | -0.14758 | 0.048236 | 0.096469 | -0.038063 | 0.005985 | 122.244 | 122.1046 | 122.1972 | 122.1475 | 122.2775 | 122.2398 | 122.151 | 0.052488 | 0.17079 | -0.004219 | -0.14758 | 0.048236 | 0.096469 | -0.038063 | 0.005985 | 0.004252 | 0.090551 | -0.052455 | 0.033844
2060.25 | 122.3923 | -122.1954 | 0.22888 | 0.076067 | -0.072572 | 0.033786 | -0.025017 | 0.095778 | 0.071848 | -0.021514 | -0.002454 | 0.15706 | 0.009515 | -0.143 | 0.034501 | 0.096469 | -0.042641 | 0.010563 | 122.2715 | 122.1229 | 122.2292 | 122.1704 | 122.2912 | 122.2673 | 122.1739 | -0.002454 | 0.15706 | 0.009515 | -0.143 | 0.034501 | 0.096469 | -0.042641 | 0.010563 | -0.036955 | 0.040187 | -0.024986 | 0.052156
2062 | 122.3969 | -122.2137 | 0.21973 | 0.071489 | -0.067994 | 0.042944 | -0.025017 | 0.10493 | 0.071848 | -0.026092 | 0.057066 | 0.15706 | 0.009515 | -0.13842 | 0.048236 | 0.091891 | -0.042641 | 0.001406 | 122.2852 | 122.1458 | 122.2567 | 122.1887 | 122.3187 | 122.2856 | 122.1877 | 0.057066 | 0.15706 | 0.009515 | -0.13842 | 0.048236 | 0.091891 | -0.042641 | 0.001406 | 0.00883 | 0.099707 | -0.038721 | 0.052156
2063.6875 | 122.4884 | -122.2092 | 0.20142 | 0.076067 | -0.063415 | 0.038365 | -0.020438 | 0.10493 | 0.067269 | -0.021514 | 0.047909 | 0.15248 | -0.008798 | -0.13842 | 0.039079 | 0.096469 | -0.033484 | 0.010563 | 122.2852 | 122.1458 | 122.2475 | 122.1887 | 122.3141 | 122.2764 | 122.1877 | 0.047909 | 0.15248 | -0.008798 | -0.13842 | 0.039079 | 0.096469 | -0.033484 | 0.010563 | 0.00883 | 0.081393 | -0.047877 | 0.024686
2065.4375 | 122.5388 | -122.1725 | 0.19684 | 0.071489 | -0.067994 | 0.038365 | -0.025017 | 0.10036 | 0.076426 | -0.021514 | 0.057066 | 0.17995 | 0.027829 | -0.14758 | 0.029923 | 0.087313 | -0.042641 | 0.001406 | 122.244 | 122.1046 | 122.2109 | 122.1475 | 122.2729 | 122.249 | 122.151 | 0.057066 | 0.17995 | 0.027829 | -0.14758 | 0.029923 | 0.087313 | -0.042641 | 0.001406 | 0.027143 | 0.099707 | -0.002094 | 0.07047
2067.2031 | 122.5433 | -122.1954 | 0.20599 | 0.076067 | -0.063415 | 0.033786 | -0.029595 | 0.10036 | 0.071848 | -0.026092 | 0.07538 | 0.15706 | -0.022532 | -0.14758 | 0.039079 | 0.096469 | -0.042641 | -0.003172 | 122.2715 | 122.132 | 122.2292 | 122.1658 | 122.2958 | 122.2673 | 122.1693 | 0.07538 | 0.15706 | -0.022532 | -0.14758 | 0.039079 | 0.096469 | -0.042641 | -0.003172 | 0.036301 | 0.11802 | -0.061611 | 0.020109
2068.8906 | 122.5708 | -122.1909 | 0.19226 | 0.076067 | -0.067994 | 0.038365 | -0.025017 | 0.10036 | 0.076426 | -0.016936 | 0.089116 | 0.16164 | 0.059877 | -0.13842 | 0.039079 | 0.10105 | -0.038063 | 0.001406 | 122.2669 | 122.1229 | 122.2292 | 122.1658 | 122.2912 | 122.2673 | 122.1739 | 0.089116 | 0.16164 | 0.059877 | -0.13842 | 0.039079 | 0.10105 | -0.038063 | 0.001406 | 0.050037 | 0.12718 | 0.020798 | 0.09794
2070.6406 | 122.4564 | -122.2412 | 0.22888 | 0.071489 | -0.058836 | 0.038365 | -0.020438 | 0.10036 | 0.076426 | -0.016936 | 0.025017 | 0.15706 | -0.027111 | -0.15216 | 0.043657 | 0.091891 | -0.038063 | 0.005985 | 122.3127 | 122.1824 | 122.2796 | 122.2208 | 122.3416 | 122.3176 | 122.2243 | 0.025017 | 0.15706 | -0.027111 | -0.15216 | 0.043657 | 0.091891 | -0.038063 | 0.005985 | -0.01864 | 0.06308 | -0.070768 | 0.010952
2072.3906 | 122.5113 | -122.1817 | 0.2243 | 0.071489 | -0.067994 | 0.024629 | -0.025017 | 0.10036 | 0.067269 | -0.012357 | 0.093694 | 0.16164 | 0.032407 | -0.15216 | 0.048236 | 0.091891 | -0.042641 | 0.001406 | 122.2532 | 122.1137 | 122.2063 | 122.1567 | 122.2821 | 122.249 | 122.1693 | 0.093694 | 0.16164 | 0.032407 | -0.15216 | 0.048236 | 0.091891 | -0.042641 | 0.001406 | 0.045458 | 0.13633 | -0.015829 | 0.075048
2074.0781 | 122.5204 | -122.2137 | 0.19226 | 0.071489 | -0.058836 | 0.033786 | -0.01586 | 0.10036 | 0.071848 | -0.021514 | 0.10285 | 0.17537 | 0.05072 | -0.143 | 0.039079 | 0.091891 | -0.042641 | 0.001406 | 122.2852 | 122.1549 | 122.2475 | 122.1979 | 122.3141 | 122.2856 | 122.1922 | 0.10285 | 0.17537 | 0.05072 | -0.143 | 0.039079 | 0.091891 | -0.042641 | 0.001406 | 0.063772 | 0.14549 | 0.011641 | 0.093361
2075.8281 | 122.438 | -122.2412 | 0.23346 | 0.080646 | -0.063415 | 0.033786 | -0.025017 | 0.10036 | 0.081005 | -0.026092 | 0.01586 | 0.15248 | 0.014094 | -0.143 | 0.048236 | 0.096469 | -0.019749 | 0.019719 | 122.3219 | 122.1778 | 122.275 | 122.2162 | 122.3416 | 122.3222 | 122.2151 | 0.01586 | 0.15248 | 0.014094 | -0.143 | 0.048236 | 0.096469 | -0.019749 | 0.019719 | -0.032376 | 0.035609 | -0.034142 | 0.033843
2077.5781 | 122.438 | -122.2366 | 0.2243 | 0.071489 | -0.067994 | 0.029208 | -0.025017 | 0.10951 | 0.076426 | -0.021514 | 0.079959 | 0.17537 | 0.02325 | -0.14758 | 0.043657 | 0.091891 | -0.006014 | 0.038032 | 122.3081 | 122.1686 | 122.2658 | 122.2116 | 122.3461 | 122.3131 | 122.2151 | 0.079959 | 0.17537 | 0.02325 | -0.14758 | 0.043657 | 0.091891 | -0.006014 | 0.038032 | 0.036302 | 0.085973 | -0.020407 | 0.029264
2079.2656 | 122.4884 | -122.2321 | 0.21515 | 0.076067 | -0.067994 | 0.033786 | -0.029595 | 0.10951 | 0.081005 | -0.026092 | 0.047909 | 0.1479 | 0.009515 | -0.143 | 0.043657 | 0.096469 | 0.003143 | 0.04261 | 122.3081 | 122.1641 | 122.2658 | 122.2025 | 122.3416 | 122.3131 | 122.206 | 0.047909 | 0.1479 | 0.009515 | -0.143 | 0.043657 | 0.096469 | 0.003143 | 0.04261 | 0.004252 | 0.044766 | -0.034142 | 0.006372
2081.0312 | 122.4426 | -122.2641 | 0.21973 | 0.076067 | -0.063415 | 0.029208 | -0.020438 | 0.10036 | 0.076426 | -0.026092 | 0.089116 | 0.16164 | 0.018672 | -0.143 | 0.039079 | 0.091891 | 0.003143 | 0.060923 | 122.3402 | 122.2007 | 122.2933 | 122.2437 | 122.3645 | 122.3405 | 122.238 | 0.089116 | 0.16164 | 0.018672 | -0.143 | 0.039079 | 0.091891 | 0.003143 | 0.060923 | 0.050037 | 0.085973 | -0.020407 | 0.015529
2082.7656 | 122.4472 | -122.2687 | 0.23346 | 0.076067 | -0.058836 | 0.038365 | -0.029595 | 0.10036 | 0.071848 | -0.012357 | 0.07538 | 0.17079 | 0.041563 | -0.14758 | 0.039079 | 0.10105 | 0.007721 | 0.060923 | 122.3447 | 122.2098 | 122.307 | 122.2391 | 122.369 | 122.3405 | 122.2563 | 0.07538 | 0.17079 | 0.041563 | -0.14758 | 0.039079 | 0.10105 | 0.007721 | 0.060923 | 0.036301 | 0.067659 | 0.002484 | 0.033842
2084.5156 | 122.4472 | -122.2687 | 0.22888 | 0.076067 | -0.063415 | 0.038365 | -0.029595 | 0.10036 | 0.081005 | -0.03067 | 0.07538 | 0.17079 | 0.055298 | -0.143 | 0.048236 | 0.087313 | 0.003143 | 0.051766 | 122.3447 | 122.2053 | 122.307 | 122.2391 | 122.369 | 122.3497 | 122.238 | 0.07538 | 0.17079 | 0.055298 | -0.143 | 0.048236 | 0.087313 | 0.003143 | 0.051766 | 0.027144 | 0.072237 | 0.007062 | 0.052155
2086.2031 | 122.493 | -122.2549 | 0.21973 | 0.076067 | -0.058836 | 0.029208 | -0.01586 | 0.10036 | 0.076426 | -0.016936 | 0.066223 | 0.17995 | 0.05072 | -0.143 | 0.043657 | 0.096469 | 0.012299 | 0.056344 | 122.331 | 122.1961 | 122.2842 | 122.2391 | 122.3553 | 122.3314 | 122.238 | 0.066223 | 0.17995 | 0.05072 | -0.143 | 0.043657 | 0.096469 | 0.012299 | 0.056344 | 0.022566 | 0.053924 | 0.007063 | 0.038421
2087.9531 | 122.5891 | -122.2092 | 0.1831 | 0.071489 | -0.058836 | 0.029208 | -0.025017 | 0.10951 | 0.076426 | -0.03067 | 0.07538 | 0.18453 | 0.059877 | -0.13842 | 0.034501 | 0.096469 | 0.007721 | 0.051766 | 122.2807 | 122.1503 | 122.2384 | 122.1841 | 122.3187 | 122.2856 | 122.1785 | 0.07538 | 0.18453 | 0.059877 | -0.13842 | 0.034501 | 0.096469 | 0.007721 | 0.051766 | 0.040879 | 0.067659 | 0.025376 | 0.052156
2089.7188 | 122.5891 | -122.2183 | 0.19684 | 0.071489 | -0.058836 | 0.029208 | -0.034174 | 0.10493 | 0.081005 | -0.026092 | 0.089116 | 0.17079 | 0.041563 | -0.14758 | 0.043657 | 0.10105 | 0.003143 | 0.051766 | 122.2898 | 122.1595 | 122.2475 | 122.1841 | 122.3233 | 122.2993 | 122.1922 | 0.089116 | 0.17079 | 0.041563 | -0.14758 | 0.043657 | 0.10105 | 0.003143 | 0.051766 | 0.045459 | 0.085973 | -0.002094 | 0.03842
2091.4062 | 122.5616 | -122.2366 | 0.18768 | 0.076067 | -0.058836 | 0.033786 | -0.025017 | 0.10493 | 0.071848 | -0.03067 | 0.057066 | 0.18911 | 0.05072 | -0.15216 | 0.048236 | 0.096469 | -0.001436 | 0.056344 | 122.3127 | 122.1778 | 122.2704 | 122.2116 | 122.3416 | 122.3085 | 122.206 | 0.057066 | 0.18911 | 0.05072 | -0.15216 | 0.048236 | 0.096469 | -0.001436 | 0.056344 | 0.00883 | 0.058502 | 0.002484 | 0.052156
2093.1562 | 122.5388 | -122.287 | 0.19684 | 0.06691 | -0.054257 | 0.033786 | -0.020438 | 0.10951 | 0.071848 | -0.026092 | 0.057066 | 0.17079 | 0.036985 | -0.143 | 0.043657 | 0.10105 | -0.042641 | 0.010563 | 122.3539 | 122.2327 | 122.3208 | 122.2665 | 122.3965 | 122.3588 | 122.2609 | 0.057066 | 0.17079 | 0.036985 | -0.143 | 0.043657 | 0.10105 | -0.042641 | 0.010563 | 0.013409 | 0.099707 | -0.006672 | 0.079626
2094.9062 | 122.4609 | -122.2824 | 0.2243 | 0.076067 | -0.058836 | 0.038365 | -0.025017 | 0.10036 | 0.081005 | -0.021514 | 0.093694 | 0.18453 | 0.036985 | -0.14758 | 0.039079 | 0.087313 | -0.019749 | 0.028875 | 122.3585 | 122.2236 | 122.3208 | 122.2574 | 122.3828 | 122.3634 | 122.2609 | 0.093694 | 0.18453 | 0.036985 | -0.14758 | 0.039079 | 0.087313 | -0.019749 | 0.028875 | 0.054615 | 0.11344 | -0.002094 | 0.056734
2096.5938 | 122.4701 | -122.2778 | 0.21515 | 0.080646 | -0.058836 | 0.038365 | -0.020438 | 0.10493 | 0.076426 | -0.021514 | 0.052488 | 0.15706 | -0.008798 | -0.143 | 0.048236 | 0.091891 | -0.038063 | -0.003172 | 122.3585 | 122.219 | 122.3162 | 122.2574 | 122.3828 | 122.3543 | 122.2563 | 0.052488 | 0.15706 | -0.008798 | -0.143 | 0.048236 | 0.091891 | -0.038063 | -0.003172 | 0.004252 | 0.090551 | -0.057034 | 0.029265
2098.2812 | 122.5021 | -122.2961 | 0.22888 | 0.076067 | -0.054257 | 0.038365 | -0.025017 | 0.10493 | 0.076426 | -0.026092 | 0.057066 | 0.17995 | 0.004937 | -0.143 | 0.039079 | 0.096469 | -0.024328 | 0.015141 | 122.3722 | 122.2419 | 122.3345 | 122.2711 | 122.4011 | 122.3726 | 122.2701 | 0.057066 | 0.17995 | 0.004937 | -0.143 | 0.039079 | 0.096469 | -0.024328 | 0.015141 | 0.017987 | 0.081394 | -0.034142 | 0.029265
2100.0469 | 122.5296 | -122.2916 | 0.23804 | 0.071489 | -0.058836 | 0.038365 | -0.025017 | 0.10493 | 0.081005 | -0.016936 | 0.084537 | 0.1479 | 0.018672 | -0.143 | 0.043657 | 0.10105 | -0.042641 | 0.005985 | 122.3631 | 122.2327 | 122.3299 | 122.2665 | 122.3965 | 122.3726 | 122.2746 | 0.084537 | 0.1479 | 0.018672 | -0.143 | 0.043657 | 0.10105 | -0.042641 | 0.005985 | 0.04088 | 0.12718 | -0.024985 | 0.061313
2101.7969 | 122.4884 | -122.3099 | 0.22888 | 0.06691 | -0.058836 | 0.029208 | -0.025017 | 0.10036 | 0.076426 | -0.016936 | -0.020768 | 0.1479 | -0.017954 | -0.143 | 0.043657 | 0.091891 | -0.042641 | 0.001406 | 122.3768 | 122.251 | 122.3391 | 122.2849 | 122.4102 | 122.3863 | 122.2929 | -0.020768 | 0.1479 | -0.017954 | -0.143 | 0.043657 | 0.091891 | -0.042641 | 0.001406 | -0.064425 | 0.021873 | -0.061611 | 0.024687
2103.5469 | 122.4884 | -122.319 | 0.22888 | 0.080646 | -0.054257 | 0.038365 | -0.025017 | 0.11409 | 0.076426 | -0.016936 | 0.12116 | 0.18453 | 0.073611 | -0.13384 | 0.039079 | 0.091891 | -0.042641 | 0.010563 | 122.3997 | 122.2648 | 122.3574 | 122.294 | 122.4331 | 122.3955 | 122.3021 | 0.12116 | 0.18453 | 0.073611 | -0.13384 | 0.039079 | 0.091891 | -0.042641 | 0.010563 | 0.082086 | 0.16381 | 0.034532 | 0.11625
2105.2344 | 122.493 | -122.3328 | 0.2655 | 0.071489 | -0.063415 | 0.038365 | -0.029595 | 0.10493 | 0.081005 | -0.016936 | 0.066223 | 0.16164 | -0.008798 | -0.13384 | 0.043657 | 0.096469 | -0.024328 | 0.005985 | 122.4043 | 122.2693 | 122.3711 | 122.3032 | 122.4377 | 122.4138 | 122.3158 | 0.066223 | 0.16164 | -0.008798 | -0.13384 | 0.043657 | 0.096469 | -0.024328 | 0.005985 | 0.022566 | 0.090551 | -0.052455 | 0.01553
2106.9844 | 122.5754 | -122.2916 | 0.19684 | 0.071489 | -0.063415 | 0.029208 | -0.020438 | 0.10493 | 0.076426 | -0.035248 | 0.047909 | 0.16622 | 0.027829 | -0.13842 | 0.043657 | 0.091891 | -0.042641 | -0.003172 | 122.3631 | 122.2281 | 122.3208 | 122.2711 | 122.3965 | 122.368 | 122.2563 | 0.047909 | 0.16622 | 0.027829 | -0.13842 | 0.043657 | 0.091891 | -0.042641 | -0.003172 | 0.004252 | 0.09055 | -0.015828 | 0.07047
2108.7344 | 122.58 | -122.2824 | 0.21515 | 0.071489 | -0.058836 | 0.033786 | -0.029595 | 0.10036 | 0.067269 | -0.026092 | 0.061645 | 0.16164 | -0.004219 | -0.14758 | 0.048236 | 0.091891 | -0.033484 | 0.005985 | 122.3539 | 122.2236 | 122.3162 | 122.2528 | 122.3828 | 122.3497 | 122.2563 | 0.061645 | 0.16164 | -0.004219 | -0.14758 | 0.048236 | 0.091891 | -0.033484 | 0.005985 | 0.013409 | 0.095129 | -0.052455 | 0.029265
2110.4375 | 122.5983 | -122.2916 | 0.20599 | 0.062332 | -0.063415 | 0.033786 | -0.029595 | 0.0912 | 0.067269 | -0.03067 | 0.052488 | 0.1479 | -0.008798 | -0.15216 | 0.034501 | 0.096469 | -0.033484 | 0.024297 | 122.3539 | 122.2281 | 122.3254 | 122.262 | 122.3828 | 122.3588 | 122.2609 | 0.052488 | 0.1479 | -0.008798 | -0.15216 | 0.034501 | 0.096469 | -0.033484 | 0.024297 | 0.017987 | 0.085972 | -0.043299 | 0.024686
2112.1875 | 122.5342 | -122.3007 | 0.20599 | 0.076067 | -0.067994 | 0.024629 | -0.029595 | 0.10036 | 0.067269 | -0.026092 | 0.11659 | 0.18453 | 0.069033 | -0.14758 | 0.039079 | 0.096469 | -0.019749 | 0.019719 | 122.3768 | 122.2327 | 122.3253 | 122.2711 | 122.4011 | 122.368 | 122.2746 | 0.11659 | 0.18453 | 0.069033 | -0.14758 | 0.039079 | 0.096469 | -0.019749 | 0.019719 | 0.077508 | 0.13634 | 0.029954 | 0.088782
2113.9531 | 122.5388 | -122.3511 | 0.21515 | 0.062332 | -0.067994 | 0.033786 | -0.034174 | 0.0912 | 0.071848 | -0.021514 | 0.079959 | 0.18911 | 0.018672 | -0.13842 | 0.043657 | 0.091891 | -0.019749 | 0.028875 | 122.4134 | 122.2831 | 122.3849 | 122.3169 | 122.4423 | 122.4229 | 122.3296 | 0.079959 | 0.18911 | 0.018672 | -0.13842 | 0.043657 | 0.091891 | -0.019749 | 0.028875 | 0.036302 | 0.099708 | -0.024985 | 0.038421
2115.7031 | 122.6395 | -122.3099 | 0.1831 | 0.062332 | -0.063415 | 0.024629 | -0.029595 | 0.095778 | 0.067269 | -0.026092 | 0.066223 | 0.17537 | -0.008798 | -0.143 | 0.034501 | 0.096469 | -0.024328 | 0.024297 | 122.3722 | 122.2465 | 122.3345 | 122.2803 | 122.4057 | 122.3771 | 122.2838 | 0.066223 | 0.17537 | -0.008798 | -0.143 | 0.034501 | 0.096469 | -0.024328 | 0.024297 | 0.031722 | 0.090551 | -0.043299 | 0.01553
2117.3906 | 122.5296 | -122.3328 | 0.20599 | 0.062332 | -0.067994 | 0.020051 | -0.029595 | 0.0912 | 0.067269 | -0.021514 | 0.11201 | 0.18911 | 0.073611 | -0.13842 | 0.039079 | 0.091891 | -0.024328 | 0.015141 | 122.3951 | 122.2648 | 122.3528 | 122.3032 | 122.424 | 122.4 | 122.3113 | 0.11201 | 0.18911 | 0.073611 | -0.13842 | 0.039079 | 0.091891 | -0.024328 | 0.015141 | 0.072929 | 0.13634 | 0.034532 | 0.097939
2119.1406 | 122.6212 | -122.2916 | 0.20142 | 0.062332 | -0.063415 | 0.029208 | -0.034174 | 0.10036 | 0.071848 | -0.026092 | 0.020438 | 0.16622 | -0.004219 | -0.143 | 0.039079 | 0.091891 | -0.028906 | 0.019719 | 122.3539 | 122.2281 | 122.3208 | 122.2574 | 122.3919 | 122.3634 | 122.2655 | 0.020438 | 0.16622 | -0.004219 | -0.143 | 0.039079 | 0.091891 | -0.028906 | 0.019719 | -0.018641 | 0.049344 | -0.043298 | 0.024687
2120.8906 | 122.6578 | -122.3007 | 0.20599 | 0.062332 | -0.067994 | 0.024629 | -0.038752 | 0.095778 | 0.067269 | -0.026092 | 0.10285 | 0.18911 | 0.041563 | -0.14758 | 0.034501 | 0.091891 | -0.028906 | 0.024297 | 122.3631 | 122.2327 | 122.3253 | 122.262 | 122.3965 | 122.368 | 122.2746 | 0.10285 | 0.18911 | 0.041563 | -0.14758 | 0.034501 | 0.091891 | -0.028906 | 0.024297 | 0.06835 | 0.13176 | 0.007062 | 0.070469
2122.5781 | 122.6074 | -122.319 | 0.21057 | 0.06691 | -0.063415 | 0.024629 | -0.034174 | 0.095778 | 0.062691 | -0.035248 | 0.10285 | 0.17995 | 0.055298 | -0.14758 | 0.048236 | 0.087313 | -0.015171 | 0.028875 | 122.3859 | 122.2556 | 122.3437 | 122.2849 | 122.4148 | 122.3817 | 122.2838 | 0.10285 | 0.17995 | 0.055298 | -0.14758 | 0.048236 | 0.087313 | -0.015171 | 0.028875 | 0.054615 | 0.11802 | 0.007062 | 0.070469
2124.3438 | 122.6624 | -122.3236 | 0.19684 | 0.057754 | -0.072572 | 0.020051 | -0.034174 | 0.10036 | 0.071848 | -0.035248 | 0.084537 | 0.17537 | 0.036985 | -0.14758 | 0.039079 | 0.096469 | -0.015171 | 0.024297 | 122.3814 | 122.251 | 122.3437 | 122.2894 | 122.424 | 122.3955 | 122.2884 | 0.084537 | 0.17537 | 0.036985 | -0.14758 | 0.039079 | 0.096469 | -0.015171 | 0.024297 | 0.045458 | 0.099708 | -0.002094 | 0.052156
2126.0938 | 122.6395 | -122.3145 | 0.19226 | 0.062332 | -0.067994 | 0.029208 | -0.034174 | 0.095778 | 0.062691 | -0.03067 | 0.034174 | 0.16164 | 0.018672 | -0.143 | 0.043657 | 0.091891 | -0.019749 | 0.028875 | 122.3768 | 122.2465 | 122.3437 | 122.2803 | 122.4102 | 122.3771 | 122.2838 | 0.034174 | 0.16164 | 0.018672 | -0.143 | 0.043657 | 0.091891 | -0.019749 | 0.028875 | -0.009483 | 0.053923 | -0.024985 | 0.038421
2127.8438 | 122.5708 | -122.3419 | 0.20142 | 0.076067 | -0.063415 | 0.015472 | -0.034174 | 0.0912 | 0.071848 | -0.026092 | 0.01586 | 0.16622 | -0.022532 | -0.13842 | 0.043657 | 0.096469 | -0.024328 | 0.019719 | 122.418 | 122.2785 | 122.3574 | 122.3077 | 122.4331 | 122.4138 | 122.3158 | 0.01586 | 0.16622 | -0.022532 | -0.13842 | 0.043657 | 0.096469 | -0.024328 | 0.019719 | -0.027797 | 0.040188 | -0.066189 | 0.001796
2129.5469 | 122.5845 | -122.3419 | 0.22888 | 0.062332 | -0.067994 | 0.024629 | -0.029595 | 0.0912 | 0.058113 | -0.03067 | 0.089116 | 0.18911 | 0.055298 | -0.14758 | 0.029923 | 0.087313 | -0.038063 | -0.003172 | 122.4043 | 122.2739 | 122.3665 | 122.3123 | 122.4331 | 122.4 | 122.3112 | 0.089116 | 0.18911 | 0.055298 | -0.14758 | 0.029923 | 0.087313 | -0.038063 | -0.003172 | 0.059193 | 0.12718 | 0.025375 | 0.093361
2131.2969 | 122.644 | -122.3145 | 0.20142 | 0.057754 | -0.077151 | 0.015472 | -0.038752 | 0.095778 | 0.062691 | -0.03067 | 0.07538 | 0.17537 | 0.009515 | -0.143 | 0.043657 | 0.096469 | -0.042641 | 0.001406 | 122.3722 | 122.2373 | 122.3299 | 122.2757 | 122.4102 | 122.3771 | 122.2838 | 0.07538 | 0.17537 | 0.009515 | -0.143 | 0.043657 | 0.096469 | -0.042641 | 0.001406 | 0.031723 | 0.11802 | -0.034142 | 0.052156
2133.0469 | 122.5296 | -122.3511 | 0.22888 | 0.071489 | -0.063415 | 0.024629 | -0.038752 | 0.0912 | 0.067269 | -0.026092 | 0.029595 | 0.15706 | 0.018672 | -0.143 | 0.048236 | 0.10105 | -0.038063 | 0.010563 | 122.4226 | 122.2877 | 122.3757 | 122.3123 | 122.4423 | 122.4183 | 122.325 | 0.029595 | 0.15706 | 0.018672 | -0.143 | 0.048236 | 0.10105 | -0.038063 | 0.010563 | -0.018641 | 0.067658 | -0.029564 | 0.056735
2134.8125 | 122.5388 | -122.3831 | 0.23346 | 0.071489 | -0.072572 | 0.024629 | -0.029595 | 0.095778 | 0.062691 | -0.026092 | 0.07538 | 0.17995 | 0.05072 | -0.143 | 0.048236 | 0.091891 | -0.033484 | 0.015141 | 122.4546 | 122.3105 | 122.4077 | 122.3535 | 122.4789 | 122.4458 | 122.357 | 0.07538 | 0.17995 | 0.05072 | -0.143 | 0.048236 | 0.091891 | -0.033484 | 0.015141 | 0.027144 | 0.10886 | 0.002484 | 0.084204
2136.5156 | 122.5479 | -122.374 | 0.20599 | 0.06691 | -0.072572 | 0.020051 | -0.038752 | 0.095778 | 0.058113 | -0.03067 | 0.061645 | 0.17537 | 0.02325 | -0.143 | 0.034501 | 0.087313 | -0.042641 | 0.001406 | 122.4409 | 122.3014 | 122.394 | 122.3352 | 122.4697 | 122.4321 | 122.3433 | 0.061645 | 0.17537 | 0.02325 | -0.143 | 0.034501 | 0.087313 | -0.042641 | 0.001406 | 0.027144 | 0.10429 | -0.011251 | 0.065891
2138.2656 | 122.5525 | -122.3831 | 0.22888 | 0.057754 | -0.077151 | 0.015472 | -0.029595 | 0.095778 | 0.076426 | -0.026092 | 0.093694 | 0.16622 | 0.004937 | -0.13842 | 0.043657 | 0.087313 | -0.028906 | 0.015141 | 122.4409 | 122.306 | 122.3986 | 122.3535 | 122.4789 | 122.4595 | 122.357 | 0.093694 | 0.16622 | 0.004937 | -0.13842 | 0.043657 | 0.087313 | -0.028906 | 0.015141 | 0.050037 | 0.1226 | -0.03872 | 0.033843
2140.0312 | 122.5983 | -122.3511 | 0.21057 | 0.062332 | -0.063415 | 0.020051 | -0.029595 | 0.10493 | 0.058113 | -0.035248 | 0.057066 | 0.16622 | 0.027829 | -0.14758 | 0.039079 | 0.096469 | -0.028906 | 0.015141 | 122.4134 | 122.2877 | 122.3711 | 122.3215 | 122.456 | 122.4092 | 122.3158 | 0.057066 | 0.16622 | 0.027829 | -0.14758 | 0.039079 | 0.096469 | -0.028906 | 0.015141 | 0.017987 | 0.085972 | -0.01125 | 0.056735
2141.7188 | 122.6028 | -122.3694 | 0.20599 | 0.06691 | -0.063415 | 0.024629 | -0.025017 | 0.10036 | 0.071848 | -0.035248 | 0.066223 | 0.15706 | 0.041563 | -0.13842 | 0.048236 | 0.10105 | -0.028906 | 0.019719 | 122.4363 | 122.306 | 122.394 | 122.3444 | 122.4697 | 122.4412 | 122.3341 | 0.066223 | 0.15706 | 0.041563 | -0.13842 | 0.048236 | 0.10105 | -0.028906 | 0.019719 | 0.017987 | 0.095129 | -0.006673 | 0.070469
2143.4844 | 122.6715 | -122.3145 | 0.18768 | 0.06691 | -0.067994 | 0.024629 | -0.029595 | 0.095778 | 0.067269 | -0.03067 | 0.070802 | 0.17537 | 0.046142 | -0.143 | 0.043657 | 0.096469 | -0.038063 | 0.015141 | 122.3814 | 122.2465 | 122.3391 | 122.2849 | 122.4102 | 122.3817 | 122.2838 | 0.070802 | 0.17537 | 0.046142 | -0.143 | 0.043657 | 0.096469 | -0.038063 | 0.015141 | 0.027145 | 0.10887 | 0.002485 | 0.084205
2145.1719 | 122.5754 | -122.3831 | 0.21515 | 0.071489 | -0.072572 | 0.020051 | -0.025017 | 0.095778 | 0.076426 | -0.021514 | 0.10285 | 0.18453 | 0.041563 | -0.13842 | 0.039079 | 0.091891 | -0.033484 | 0.010563 | 122.4546 | 122.3105 | 122.4032 | 122.3581 | 122.4789 | 122.4595 | 122.3616 | 0.10285 | 0.18453 | 0.041563 | -0.13842 | 0.039079 | 0.091891 | -0.033484 | 0.010563 | 0.063772 | 0.13633 | 0.002484 | 0.075047
2146.9062 | 122.5891 | -122.3831 | 0.2243 | 0.076067 | -0.058836 | 0.029208 | -0.034174 | 0.10493 | 0.071848 | -0.026092 | 0.089116 | 0.17995 | 0.055298 | -0.14758 | 0.034501 | 0.096469 | -0.042641 | 0.015141 | 122.4592 | 122.3243 | 122.4123 | 122.3489 | 122.4881 | 122.455 | 122.357 | 0.089116 | 0.17995 | 0.055298 | -0.14758 | 0.034501 | 0.096469 | -0.042641 | 0.015141 | 0.054615 | 0.13176 | 0.020797 | 0.097939
2148.6562 | 122.7081 | -122.3511 | 0.18768 | 0.071489 | -0.063415 | 0.015472 | -0.029595 | 0.10036 | 0.067269 | -0.021514 | 0.029595 | 0.16622 | -0.008798 | -0.13842 | 0.034501 | 0.096469 | -0.024328 | 0.015141 | 122.4226 | 122.2877 | 122.3665 | 122.3215 | 122.4514 | 122.4183 | 122.3296 | 0.029595 | 0.16622 | -0.008798 | -0.13842 | 0.034501 | 0.096469 | -0.024328 | 0.015141 | -0.004906 | 0.053923 | -0.043299 | 0.01553
2150.4219 | 122.6624 | -122.3511 | 0.20599 | 0.071489 | -0.063415 | 0.029208 | -0.038752 | 0.095778 | 0.062691 | -0.03067 | 0.079959 | 0.16164 | 0.02325 | -0.14758 | 0.039079 | 0.10105 | -0.028906 | 0.015141 | 122.4226 | 122.2877 | 122.3803 | 122.3123 | 122.4469 | 122.4138 | 122.3204 | 0.079959 | 0.16164 | 0.02325 | -0.14758 | 0.039079 | 0.10105 | -0.028906 | 0.015141 | 0.04088 | 0.10887 | -0.015829 | 0.052156
2152.1094 | 122.5525 | -122.4152 | 0.2243 | 0.071489 | -0.054257 | 0.020051 | -0.034174 | 0.095778 | 0.062691 | -0.035248 | 0.084537 | 0.17079 | -0.008798 | -0.143 | 0.043657 | 0.091891 | -0.038063 | 0.010563 | 122.4866 | 122.3609 | 122.4352 | 122.381 | 122.5109 | 122.4779 | 122.3799 | 0.084537 | 0.17079 | -0.008798 | -0.143 | 0.043657 | 0.091891 | -0.038063 | 0.010563 | 0.04088 | 0.1226 | -0.052455 | 0.029265
2153.8594 | 122.5937 | -122.374 | 0.22888 | 0.062332 | -0.067994 | 0.015472 | -0.038752 | 0.095778 | 0.062691 | -0.03067 | 0.01586 | 0.16622 | -0.017954 | -0.143 | 0.043657 | 0.091891 | -0.038063 | 0.005985 | 122.4363 | 122.306 | 122.3894 | 122.3352 | 122.4697 | 122.4367 | 122.3433 | 0.01586 | 0.16622 | -0.017954 | -0.143 | 0.043657 | 0.091891 | -0.038063 | 0.005985 | -0.027797 | 0.053923 | -0.061611 | 0.020109
2155.6094 | 122.6486 | -122.3831 | 0.21973 | 0.062332 | -0.067994 | 0.020051 | -0.029595 | 0.10493 | 0.062691 | -0.026092 | -0.029925 | 0.12501 | -0.040846 | -0.143 | 0.029923 | 0.096469 | -0.04722 | -0.003172 | 122.4454 | 122.3151 | 122.4032 | 122.3535 | 122.4881 | 122.4458 | 122.357 | -0.029925 | 0.12501 | -0.040846 | -0.143 | 0.029923 | 0.096469 | -0.04722 | -0.003172 | -0.059848 | 0.017295 | -0.070769 | 0.006374
2157.3594 | 122.5845 | -122.4014 | 0.23804 | 0.06691 | -0.063415 | 0.024629 | -0.034174 | 0.0912 | 0.067269 | -0.026092 | 0.089116 | 0.17537 | 0.059877 | -0.143 | 0.039079 | 0.087313 | -0.033484 | -0.003172 | 122.4683 | 122.338 | 122.4261 | 122.3673 | 122.4926 | 122.4687 | 122.3753 | 0.089116 | 0.17537 | 0.059877 | -0.143 | 0.039079 | 0.087313 | -0.033484 | -0.003172 | 0.050037 | 0.1226 | 0.020798 | 0.093361
2159.0469 | 122.699 | -122.3785 | 0.21515 | 0.062332 | -0.067994 | 0.015472 | -0.029595 | 0.0912 | 0.067269 | -0.035248 | -0.002454 | 0.13416 | -0.022532 | -0.143 | 0.048236 | 0.10105 | -0.033484 | 0.010563 | 122.4409 | 122.3105 | 122.394 | 122.3489 | 122.4697 | 122.4458 | 122.3433 | -0.002454 | 0.13416 | -0.022532 | -0.143 | 0.048236 | 0.10105 | -0.033484 | 0.010563 | -0.05069 | 0.03103 | -0.070768 | 0.010952
2160.7969 | 122.6761 | -122.3831 | 0.21515 | 0.062332 | -0.067994 | 0.020051 | -0.034174 | 0.095778 | 0.062691 | -0.03067 | 0.006703 | 0.1479 | -0.050002 | -0.14758 | 0.048236 | 0.091891 | -0.038063 | 0.005985 | 122.4454 | 122.3151 | 122.4032 | 122.3489 | 122.4789 | 122.4458 | 122.3524 | 0.006703 | 0.1479 | -0.050002 | -0.14758 | 0.048236 | 0.091891 | -0.038063 | 0.005985 | -0.041533 | 0.044766 | -0.098238 | -0.011939
2162.5312 | 122.6898 | -122.3969 | 0.21515 | 0.071489 | -0.072572 | 0.024629 | -0.029595 | 0.095778 | 0.067269 | -0.021514 | 0.066223 | 0.16622 | 0.014094 | -0.143 | 0.043657 | 0.091891 | -0.028906 | 0.010563 | 122.4683 | 122.3243 | 122.4215 | 122.3673 | 122.4926 | 122.4641 | 122.3753 | 0.066223 | 0.16622 | 0.014094 | -0.143 | 0.043657 | 0.091891 | -0.028906 | 0.010563 | 0.022566 | 0.095129 | -0.029563 | 0.043
2164.2812 | 122.5983 | -122.3923 | 0.21057 | 0.062332 | -0.067994 | 0.024629 | -0.029595 | 0.095778 | 0.067269 | -0.03067 | -0.002454 | 0.16622 | -0.063737 | -0.14758 | 0.043657 | 0.091891 | -0.038063 | 0.010563 | 122.4546 | 122.3243 | 122.4169 | 122.3627 | 122.4881 | 122.4595 | 122.3616 | -0.002454 | 0.16622 | -0.063737 | -0.14758 | 0.043657 | 0.091891 | -0.038063 | 0.010563 | -0.046111 | 0.035609 | -0.10739 | -0.025674
2166.0469 | 122.6166 | -122.4152 | 0.21973 | 0.071489 | -0.063415 | 0.024629 | -0.034174 | 0.095778 | 0.067269 | -0.026092 | 0.025017 | 0.1479 | 0.000359 | -0.13842 | 0.039079 | 0.096469 | -0.04722 | 0.005985 | 122.4866 | 122.3517 | 122.4398 | 122.381 | 122.5109 | 122.4824 | 122.3891 | 0.025017 | 0.1479 | 0.000359 | -0.13842 | 0.039079 | 0.096469 | -0.04722 | 0.005985 | -0.014062 | 0.072237 | -0.03872 | 0.047579
2167.75 | 122.612 | -122.4243 | 0.25177 | 0.071489 | -0.067994 | 0.029208 | -0.029595 | 0.10036 | 0.067269 | -0.021514 | -0.01619 | 0.12958 | -0.040846 | -0.13842 | 0.039079 | 0.096469 | -0.038063 | -0.003172 | 122.4958 | 122.3563 | 122.4535 | 122.3947 | 122.5247 | 122.4916 | 122.4028 | -0.01619 | 0.12958 | -0.040846 | -0.13842 | 0.039079 | 0.096469 | -0.038063 | -0.003172 | -0.055269 | 0.021873 | -0.079925 | -0.002783
2169.5156 | 122.6624 | -122.4289 | 0.21515 | 0.06691 | -0.063415 | 0.024629 | -0.038752 | 0.10493 | 0.071848 | -0.021514 | 0.089116 | 0.16622 | 0.036985 | -0.143 | 0.043657 | 0.096469 | -0.028906 | 0.005985 | 122.4958 | 122.3655 | 122.4535 | 122.3901 | 122.5338 | 122.5007 | 122.4074 | 0.089116 | 0.16622 | 0.036985 | -0.143 | 0.043657 | 0.096469 | -0.028906 | 0.005985 | 0.045459 | 0.11802 | -0.006672 | 0.065891
2171.2031 | 122.7722 | -122.3785 | 0.20599 | 0.062332 | -0.077151 | 0.029208 | -0.034174 | 0.095778 | 0.067269 | -0.03067 | -0.002454 | 0.13416 | -0.013376 | -0.143 | 0.039079 | 0.096469 | -0.033484 | 0.010563 | 122.4409 | 122.3014 | 122.4077 | 122.3444 | 122.4743 | 122.4458 | 122.3479 | -0.002454 | 0.13416 | -0.013376 | -0.143 | 0.039079 | 0.096469 | -0.033484 | 0.010563 | -0.041533 | 0.03103 | -0.052455 | 0.020108
2172.9531 | 122.6349 | -122.4243 | 0.2243 | 0.062332 | -0.058836 | 0.024629 | -0.025017 | 0.095778 | 0.067269 | -0.026092 | 0.070802 | 0.16622 | 0.004937 | -0.14758 | 0.043657 | 0.091891 | -0.038063 | 0.005985 | 122.4866 | 122.3655 | 122.4489 | 122.3993 | 122.5201 | 122.4916 | 122.3982 | 0.070802 | 0.16622 | 0.004937 | -0.14758 | 0.043657 | 0.091891 | -0.038063 | 0.005985 | 0.027145 | 0.10887 | -0.03872 | 0.043
2174.6406 | 122.6074 | -122.4518 | 0.21973 | 0.06691 | -0.058836 | 0.024629 | -0.029595 | 0.10036 | 0.071848 | -0.021514 | 0.066223 | 0.15706 | 0.000359 | -0.14758 | 0.039079 | 0.087313 | -0.038063 | 0.010563 | 122.5187 | 122.3929 | 122.4764 | 122.4222 | 122.5521 | 122.5236 | 122.4303 | 0.066223 | 0.15706 | 0.000359 | -0.14758 | 0.039079 | 0.087313 | -0.038063 | 0.010563 | 0.027144 | 0.10429 | -0.03872 | 0.038422
2176.4062 | 122.6257 | -122.438 | 0.22888 | 0.071489 | -0.063415 | 0.029208 | -0.025017 | 0.10036 | 0.071848 | -0.026092 | 0.002124 | 0.13874 | -0.040846 | -0.14758 | 0.039079 | 0.096469 | -0.038063 | 0.005985 | 122.5095 | 122.3746 | 122.4673 | 122.413 | 122.5384 | 122.5099 | 122.412 | 0.002124 | 0.13874 | -0.040846 | -0.14758 | 0.039079 | 0.096469 | -0.038063 | 0.005985 | -0.036955 | 0.040187 | -0.079925 | -0.002783
2178.1562 | 122.7448 | -122.3877 | 0.20599 | 0.062332 | -0.063415 | 0.029208 | -0.034174 | 0.10036 | 0.076426 | -0.03067 | 0.047909 | 0.15248 | 0.004937 | -0.13842 | 0.039079 | 0.096469 | -0.033484 | 0.001406 | 122.45 | 122.3243 | 122.4169 | 122.3535 | 122.4881 | 122.4641 | 122.357 | 0.047909 | 0.15248 | 0.004937 | -0.13842 | 0.039079 | 0.096469 | -0.033484 | 0.001406 | 0.00883 | 0.081393 | -0.034142 | 0.038421
2179.9219 | 122.7631 | -122.3969 | 0.1831 | 0.06691 | -0.063415 | 0.033786 | -0.034174 | 0.10493 | 0.071848 | -0.026092 | 0.043331 | 0.17079 | 0.018672 | -0.14758 | 0.048236 | 0.096469 | -0.038063 | 0.005985 | 122.4638 | 122.3334 | 122.4306 | 122.3627 | 122.5018 | 122.4687 | 122.3708 | 0.043331 | 0.17079 | 0.018672 | -0.14758 | 0.048236 | 0.096469 | -0.038063 | 0.005985 | -0.004905 | 0.081394 | -0.029564 | 0.056735
2181.6094 | 122.7493 | -122.3831 | 0.20599 | 0.071489 | -0.067994 | 0.024629 | -0.034174 | 0.10951 | 0.067269 | -0.016936 | 0.002124 | 0.16622 | -0.027111 | -0.14758 | 0.039079 | 0.096469 | -0.042641 | 0.015141 | 122.4546 | 122.3151 | 122.4077 | 122.3489 | 122.4926 | 122.4504 | 122.3662 | 0.002124 | 0.16622 | -0.027111 | -0.14758 | 0.039079 | 0.096469 | -0.042641 | 0.015141 | -0.036955 | 0.044765 | -0.06619 | 0.01553
2183.3594 | 122.7081 | -122.406 | 0.20599 | 0.071489 | -0.049678 | 0.024629 | -0.029595 | 0.10036 | 0.076426 | -0.021514 | 0.011281 | 0.15248 | -0.040846 | -0.143 | 0.043657 | 0.096469 | -0.04722 | 0.010563 | 122.4775 | 122.3563 | 122.4306 | 122.3764 | 122.5064 | 122.4824 | 122.3845 | 0.011281 | 0.15248 | -0.040846 | -0.143 | 0.043657 | 0.096469 | -0.04722 | 0.010563 | -0.032376 | 0.058501 | -0.084503 | 0.006374
2185.125 | 122.6532 | -122.4564 | 0.23346 | 0.071489 | -0.058836 | 0.024629 | -0.025017 | 0.10951 | 0.081005 | -0.016936 | 0.047909 | 0.15706 | 0.032407 | -0.13842 | 0.039079 | 0.096469 | -0.033484 | 0.001406 | 122.5278 | 122.3975 | 122.481 | 122.4313 | 122.5659 | 122.5374 | 122.4394 | 0.047909 | 0.15706 | 0.032407 | -0.13842 | 0.039079 | 0.096469 | -0.033484 | 0.001406 | 0.00883 | 0.081393 | -0.006672 | 0.065891
2186.8125 | 122.7814 | -122.4152 | 0.19226 | 0.071489 | -0.063415 | 0.038365 | -0.029595 | 0.10493 | 0.071848 | -0.026092 | 0.057066 | 0.17537 | 0.018672 | -0.143 | 0.048236 | 0.091891 | -0.038063 | -0.003172 | 122.4866 | 122.3517 | 122.4535 | 122.3856 | 122.5201 | 122.487 | 122.3891 | 0.057066 | 0.17537 | 0.018672 | -0.143 | 0.048236 | 0.091891 | -0.038063 | -0.003172 | 0.00883 | 0.095129 | -0.029564 | 0.056735
2188.5781 | 122.731 | -122.3969 | 0.19684 | 0.06691 | -0.063415 | 0.033786 | -0.029595 | 0.10036 | 0.067269 | -0.026092 | -0.034504 | 0.13416 | -0.036267 | -0.15216 | 0.034501 | 0.091891 | -0.038063 | 0.010563 | 122.4638 | 122.3334 | 122.4306 | 122.3673 | 122.4972 | 122.4641 | 122.3708 | -0.034504 | 0.13416 | -0.036267 | -0.15216 | 0.034501 | 0.091891 | -0.038063 | 0.010563 | -0.069005 | 0.003559 | -0.070768 | 0.001796
2190.3438 | 122.7448 | -122.4197 | 0.19226 | 0.06691 | -0.063415 | 0.033786 | -0.029595 | 0.10493 | 0.071848 | -0.026092 | 0.029595 | 0.1479 | 0.009515 | -0.13842 | 0.039079 | 0.091891 | -0.038063 | 0.010563 | 122.4866 | 122.3563 | 122.4535 | 122.3901 | 122.5247 | 122.4916 | 122.3936 | 0.029595 | 0.1479 | 0.009515 | -0.13842 | 0.039079 | 0.091891 | -0.038063 | 0.010563 | -0.009484 | 0.067658 | -0.029564 | 0.047578
2192.0938 | 122.7997 | -122.4197 | 0.18768 | 0.071489 | -0.063415 | 0.029208 | -0.029595 | 0.095778 | 0.081005 | -0.021514 | 0.047909 | 0.12958 | 0.009515 | -0.143 | 0.039079 | 0.091891 | -0.038063 | 0.005985 | 122.4912 | 122.3563 | 122.4489 | 122.3901 | 122.5155 | 122.5007 | 122.3982 | 0.047909 | 0.12958 | 0.009515 | -0.143 | 0.039079 | 0.091891 | -0.038063 | 0.005985 | 0.00883 | 0.085972 | -0.029564 | 0.047578
2193.7969 | 122.7722 | -122.406 | 0.20142 | 0.076067 | -0.072572 | 0.033786 | -0.025017 | 0.10493 | 0.076426 | -0.016936 | 0.093694 | 0.17537 | 0.059877 | -0.14758 | 0.043657 | 0.096469 | -0.04722 | 0.010563 | 122.4821 | 122.3334 | 122.4398 | 122.381 | 122.5109 | 122.4824 | 122.3891 | 0.093694 | 0.17537 | 0.059877 | -0.14758 | 0.043657 | 0.096469 | -0.04722 | 0.010563 | 0.050037 | 0.14091 | 0.01622 | 0.1071
2195.5469 | 122.7448 | -122.4152 | 0.20142 | 0.080646 | -0.063415 | 0.033786 | -0.01586 | 0.10493 | 0.076426 | -0.021514 | 0.098273 | 0.17537 | 0.064455 | -0.13842 | 0.039079 | 0.096469 | -0.038063 | 0.015141 | 122.4958 | 122.3517 | 122.4489 | 122.3993 | 122.5201 | 122.4916 | 122.3936 | 0.098273 | 0.17537 | 0.064455 | -0.13842 | 0.039079 | 0.096469 | -0.038063 | 0.015141 | 0.059194 | 0.13634 | 0.025376 | 0.10252
2197.2969 | 122.7676 | -122.4289 | 0.19684 | 0.080646 | -0.063415 | 0.029208 | -0.029595 | 0.10951 | 0.076426 | -0.012357 | 0.084537 | 0.16164 | 0.02325 | -0.143 | 0.034501 | 0.091891 | -0.033484 | 0.005985 | 122.5095 | 122.3655 | 122.4581 | 122.3993 | 122.5384 | 122.5053 | 122.4165 | 0.084537 | 0.16164 | 0.02325 | -0.143 | 0.034501 | 0.091891 | -0.033484 | 0.005985 | 0.050036 | 0.11802 | -0.011251 | 0.056734
2199.0625 | 122.644 | -122.4884 | 0.24719 | 0.076067 | -0.058836 | 0.029208 | -0.020438 | 0.10951 | 0.071848 | -0.026092 | 0.034174 | 0.15248 | 0.018672 | -0.13842 | 0.043657 | 0.087313 | -0.033484 | 0.010563 | 122.5645 | 122.4296 | 122.5176 | 122.468 | 122.5979 | 122.5603 | 122.4623 | 0.034174 | 0.15248 | 0.018672 | -0.13842 | 0.043657 | 0.087313 | -0.033484 | 0.010563 | -0.009483 | 0.067658 | -0.024985 | 0.052156
2200.75 | 122.7768 | -122.438 | 0.20142 | 0.071489 | -0.058836 | 0.029208 | -0.020438 | 0.10036 | 0.076426 | -0.021514 | -0.01619 | 0.13874 | -0.022532 | -0.143 | 0.034501 | 0.096469 | -0.033484 | 0.005985 | 122.5095 | 122.3792 | 122.4673 | 122.4176 | 122.5384 | 122.5145 | 122.4165 | -0.01619 | 0.13874 | -0.022532 | -0.143 | 0.034501 | 0.096469 | -0.033484 | 0.005985 | -0.050691 | 0.017294 | -0.057033 | 0.010952
2202.5 | 122.6303 | -122.4701 | 0.23346 | 0.076067 | -0.054257 | 0.033786 | -0.034174 | 0.10951 | 0.076426 | -0.016936 | -0.01619 | 0.13874 | -0.022532 | -0.143 | 0.043657 | 0.096469 | -0.042641 | 0.005985 | 122.5462 | 122.4158 | 122.5039 | 122.4359 | 122.5796 | 122.5465 | 122.4532 | -0.01619 | 0.13874 | -0.022532 | -0.143 | 0.043657 | 0.096469 | -0.042641 | 0.005985 | -0.059847 | 0.026451 | -0.066189 | 0.020109
2204.25 | 122.8043 | -122.4335 | 0.19684 | 0.06691 | -0.063415 | 0.029208 | -0.025017 | 0.10036 | 0.076426 | -0.021514 | -0.007033 | 0.15706 | -0.040846 | -0.14758 | 0.039079 | 0.091891 | -0.038063 | 0.010563 | 122.5004 | 122.3701 | 122.4627 | 122.4085 | 122.5338 | 122.5099 | 122.412 | -0.007033 | 0.15706 | -0.040846 | -0.14758 | 0.039079 | 0.091891 | -0.038063 | 0.010563 | -0.046112 | 0.03103 | -0.079925 | -0.002783
2205.9531 | 122.7127 | -122.4518 | 0.20142 | 0.076067 | -0.049678 | 0.033786 | -0.025017 | 0.10036 | 0.076426 | -0.016936 | 0.043331 | 0.16164 | -0.045424 | -0.14758 | 0.043657 | 0.091891 | -0.038063 | 0.010563 | 122.5278 | 122.4021 | 122.4856 | 122.4268 | 122.5521 | 122.5282 | 122.4348 | 0.043331 | 0.16164 | -0.045424 | -0.14758 | 0.043657 | 0.091891 | -0.038063 | 0.010563 | -0.000326 | 0.081394 | -0.089081 | -0.007361
2207.7031 | 122.6303 | -122.5021 | 0.22888 | 0.071489 | -0.054257 | 0.038365 | -0.020438 | 0.10493 | 0.076426 | -0.016936 | 0.029595 | 0.13416 | -0.040846 | -0.143 | 0.034501 | 0.10105 | -0.038063 | 0.005985 | 122.5736 | 122.4479 | 122.5405 | 122.4817 | 122.6071 | 122.5786 | 122.4852 | 0.029595 | 0.13416 | -0.040846 | -0.143 | 0.034501 | 0.10105 | -0.038063 | 0.005985 | -0.004906 | 0.067658 | -0.075347 | -0.002783
2209.3906 | 122.6624 | -122.5021 | 0.23346 | 0.076067 | -0.049678 | 0.033786 | -0.020438 | 0.10036 | 0.071848 | -0.016936 | 0.01586 | 0.15706 | -0.022532 | -0.14758 | 0.043657 | 0.087313 | -0.038063 | 0.010563 | 122.5782 | 122.4525 | 122.5359 | 122.4817 | 122.6025 | 122.574 | 122.4852 | 0.01586 | 0.15706 | -0.022532 | -0.14758 | 0.043657 | 0.087313 | -0.038063 | 0.010563 | -0.027797 | 0.053923 | -0.066189 | 0.015531
2211.1406 | 122.6669 | -122.5159 | 0.21973 | 0.080646 | -0.049678 | 0.029208 | -0.020438 | 0.10493 | 0.071848 | -0.016936 | -0.039082 | 0.17079 | 0.000359 | -0.13842 | 0.043657 | 0.091891 | -0.033484 | 0.010563 | 122.5965 | 122.4662 | 122.5451 | 122.4954 | 122.6208 | 122.5877 | 122.4989 | -0.039082 | 0.17079 | 0.000359 | -0.13842 | 0.043657 | 0.091891 | -0.033484 | 0.010563 | -0.082739 | -0.005598 | -0.043298 | 0.033843
2212.8125 | 122.8134 | -122.4609 | 0.20142 | 0.076067 | -0.063415 | 0.038365 | -0.025017 | 0.10493 | 0.071848 | -0.026092 | 0.066223 | 0.17537 | 0.027829 | -0.13842 | 0.034501 | 0.091891 | -0.038063 | 0.005985 | 122.537 | 122.3975 | 122.4993 | 122.4359 | 122.5659 | 122.5328 | 122.4348 | 0.066223 | 0.17537 | 0.027829 | -0.13842 | 0.034501 | 0.091891 | -0.038063 | 0.005985 | 0.031722 | 0.10429 | -0.006672 | 0.065892
2214.5625 | 122.7448 | -122.4792 | 0.21515 | 0.080646 | -0.058836 | 0.024629 | -0.020438 | 0.10036 | 0.067269 | -0.021514 | 0.070802 | 0.16622 | 0.000359 | -0.143 | 0.034501 | 0.096469 | -0.033484 | 0.001406 | 122.5599 | 122.4204 | 122.5039 | 122.4588 | 122.5796 | 122.5465 | 122.4577 | 0.070802 | 0.16622 | 0.000359 | -0.143 | 0.034501 | 0.096469 | -0.033484 | 0.001406 | 0.036301 | 0.10429 | -0.034142 | 0.033843
2216.3281 | 122.8226 | -122.4564 | 0.20142 | 0.076067 | -0.058836 | 0.029208 | -0.025017 | 0.10036 | 0.076426 | -0.021514 | 0.034174 | 0.17995 | 0.018672 | -0.143 | 0.039079 | 0.096469 | -0.033484 | 0.005985 | 122.5324 | 122.3975 | 122.4856 | 122.4313 | 122.5567 | 122.5328 | 122.4348 | 0.034174 | 0.17995 | 0.018672 | -0.143 | 0.039079 | 0.096469 | -0.033484 | 0.005985 | -0.004905 | 0.067658 | -0.020407 | 0.052156
2218.0781 | 122.7905 | -122.4472 | 0.18768 | 0.076067 | -0.054257 | 0.029208 | -0.01586 | 0.10036 | 0.071848 | -0.021514 | -0.025347 | 0.17079 | -0.031689 | -0.14758 | 0.039079 | 0.091891 | -0.038063 | 0.015141 | 122.5233 | 122.3929 | 122.4764 | 122.4313 | 122.5476 | 122.5191 | 122.4257 | -0.025347 | 0.17079 | -0.031689 | -0.14758 | 0.039079 | 0.091891 | -0.038063 | 0.015141 | -0.064426 | 0.012716 | -0.070768 | 0.006374
2219.7656 | 122.7356 | -122.4838 | 0.22888 | 0.071489 | -0.054257 | 0.033786 | -0.025017 | 0.10036 | 0.076426 | -0.026092 | -0.052818 | 0.1479 | -0.013376 | -0.13384 | 0.043657 | 0.096469 | -0.033484 | 0.005985 | 122.5553 | 122.4296 | 122.5176 | 122.4588 | 122.5842 | 122.5603 | 122.4577 | -0.052818 | 0.1479 | -0.013376 | -0.13384 | 0.043657 | 0.096469 | -0.033484 | 0.005985 | -0.096475 | -0.019334 | -0.057033 | 0.020108
2221.5469 | 122.7036 | -122.4747 | 0.21973 | 0.076067 | -0.054257 | 0.042944 | -0.025017 | 0.10951 | 0.076426 | -0.016936 | -0.020768 | 0.15706 | -0.022532 | -0.15216 | 0.034501 | 0.091891 | -0.042641 | 0.010563 | 122.5507 | 122.4204 | 122.5176 | 122.4497 | 122.5842 | 122.5511 | 122.4577 | -0.020768 | 0.15706 | -0.022532 | -0.15216 | 0.034501 | 0.091891 | -0.042641 | 0.010563 | -0.055269 | 0.021873 | -0.057033 | 0.020109
2223.2969 | 122.8317 | -122.4564 | 0.21057 | 0.080646 | -0.049678 | 0.033786 | -0.025017 | 0.10493 | 0.067269 | -0.021514 | 0.029595 | 0.17079 | -0.031689 | -0.143 | 0.039079 | 0.091891 | -0.033484 | 0.010563 | 122.537 | 122.4067 | 122.4901 | 122.4313 | 122.5613 | 122.5236 | 122.4348 | 0.029595 | 0.17079 | -0.031689 | -0.143 | 0.039079 | 0.091891 | -0.033484 | 0.010563 | -0.009484 | 0.063079 | -0.070768 | 0.001795
2225.0469 | 122.7768 | -122.4655 | 0.21057 | 0.071489 | -0.058836 | 0.033786 | -0.025017 | 0.10036 | 0.071848 | -0.026092 | 0.011281 | 0.17537 | 0.027829 | -0.14758 | 0.034501 | 0.096469 | -0.038063 | 0.010563 | 122.537 | 122.4067 | 122.4993 | 122.4405 | 122.5659 | 122.5374 | 122.4394 | 0.011281 | 0.17537 | 0.027829 | -0.14758 | 0.034501 | 0.096469 | -0.038063 | 0.010563 | -0.02322 | 0.049344 | -0.006672 | 0.065892
2226.7344 | 122.7539 | -122.4747 | 0.2243 | 0.071489 | -0.054257 | 0.033786 | -0.020438 | 0.10493 | 0.081005 | -0.016936 | 0.020438 | 0.17079 | -0.045424 | -0.14758 | 0.043657 | 0.096469 | -0.033484 | 0.005985 | 122.5462 | 122.4204 | 122.5085 | 122.4542 | 122.5796 | 122.5557 | 122.4577 | 0.020438 | 0.17079 | -0.045424 | -0.14758 | 0.043657 | 0.096469 | -0.033484 | 0.005985 | -0.023219 | 0.053922 | -0.089081 | -0.01194
2228.4844 | 122.8226 | -122.493 | 0.19684 | 0.076067 | -0.054257 | 0.033786 | -0.020438 | 0.10493 | 0.071848 | -0.016936 | -0.002454 | 0.15248 | -0.013376 | -0.13384 | 0.043657 | 0.096469 | -0.033484 | 0.005985 | 122.569 | 122.4387 | 122.5268 | 122.4725 | 122.5979 | 122.5648 | 122.476 | -0.002454 | 0.15248 | -0.013376 | -0.13384 | 0.043657 | 0.096469 | -0.033484 | 0.005985 | -0.046111 | 0.03103 | -0.057033 | 0.020108
2230.2344 | 122.699 | -122.5067 | 0.23346 | 0.076067 | -0.049678 | 0.029208 | -0.020438 | 0.10493 | 0.076426 | -0.016936 | -0.039082 | 0.15248 | -0.040846 | -0.14758 | 0.039079 | 0.096469 | -0.038063 | 0.015141 | 122.5828 | 122.457 | 122.5359 | 122.4863 | 122.6116 | 122.5831 | 122.4898 | -0.039082 | 0.15248 | -0.040846 | -0.14758 | 0.039079 | 0.096469 | -0.038063 | 0.015141 | -0.078161 | -0.001019 | -0.079925 | -0.002783
2232 | 122.6944 | -122.5342 | 0.24261 | 0.076067 | -0.054257 | 0.038365 | -0.020438 | 0.095778 | 0.071848 | -0.016936 | 0.011281 | 0.16164 | -0.004219 | -0.14758 | 0.039079 | 0.091891 | -0.038063 | 0.005985 | 122.6102 | 122.4799 | 122.5725 | 122.5137 | 122.63 | 122.606 | 122.5172 | 0.011281 | 0.16164 | -0.004219 | -0.14758 | 0.039079 | 0.091891 | -0.038063 | 0.005985 | -0.027798 | 0.049344 | -0.043298 | 0.033844
2233.6875 | 122.8226 | -122.4609 | 0.19684 | 0.071489 | -0.049678 | 0.033786 | -0.01586 | 0.10493 | 0.071848 | -0.016936 | 0.038752 | 0.17995 | 0.032407 | -0.14758 | 0.039079 | 0.096469 | -0.038063 | 0.005985 | 122.5324 | 122.4113 | 122.4947 | 122.4451 | 122.5659 | 122.5328 | 122.444 | 0.038752 | 0.17995 | 0.032407 | -0.14758 | 0.039079 | 0.096469 | -0.038063 | 0.005985 | -0.000327 | 0.076815 | -0.006672 | 0.07047
2235.4375 | 122.731 | -122.5021 | 0.2243 | 0.085224 | -0.058836 | 0.038365 | -0.025017 | 0.10951 | 0.071848 | -0.016936 | 0.079959 | 0.16622 | 0.027829 | -0.15216 | 0.048236 | 0.096469 | -0.038063 | 0.010563 | 122.5874 | 122.4433 | 122.5405 | 122.4771 | 122.6116 | 122.574 | 122.4852 | 0.079959 | 0.16622 | 0.027829 | -0.15216 | 0.048236 | 0.096469 | -0.038063 | 0.010563 | 0.031723 | 0.11802 | -0.020407 | 0.065892
2237.1875 | 122.7676 | -122.5067 | 0.22888 | 0.080646 | -0.049678 | 0.029208 | -0.020438 | 0.10493 | 0.076426 | -0.021514 | 0.034174 | 0.15706 | 0.018672 | -0.143 | 0.043657 | 0.096469 | -0.028906 | 0.015141 | 122.5874 | 122.457 | 122.5359 | 122.4863 | 122.6116 | 122.5831 | 122.4852 | 0.034174 | 0.15706 | 0.018672 | -0.143 | 0.043657 | 0.096469 | -0.028906 | 0.015141 | -0.009483 | 0.06308 | -0.024985 | 0.047578
2238.9531 | 122.7676 | -122.4976 | 0.2243 | 0.080646 | -0.054257 | 0.033786 | -0.020438 | 0.10036 | 0.071848 | -0.021514 | 0.025017 | 0.16622 | -0.013376 | -0.143 | 0.034501 | 0.091891 | -0.033484 | 0.019719 | 122.5782 | 122.4433 | 122.5313 | 122.4771 | 122.5979 | 122.5694 | 122.476 | 0.025017 | 0.16622 | -0.013376 | -0.143 | 0.034501 | 0.091891 | -0.033484 | 0.019719 | -0.009484 | 0.058501 | -0.047877 | 0.020108
2240.6406 | 122.8088 | -122.493 | 0.21515 | 0.085224 | -0.049678 | 0.029208 | -0.029595 | 0.10493 | 0.081005 | -0.021514 | 0.038752 | 0.16164 | 0.018672 | -0.13842 | 0.034501 | 0.10105 | -0.033484 | 0.015141 | 122.5782 | 122.4433 | 122.5222 | 122.4634 | 122.5979 | 122.574 | 122.4715 | 0.038752 | 0.16164 | 0.018672 | -0.13842 | 0.034501 | 0.10105 | -0.033484 | 0.015141 | 0.004251 | 0.072236 | -0.015829 | 0.052156
2242.3906 | 122.7539 | -122.5388 | 0.21057 | 0.071489 | -0.054257 | 0.033786 | -0.020438 | 0.10036 | 0.071848 | -0.021514 | -0.025347 | 0.13874 | -0.017954 | -0.143 | 0.039079 | 0.091891 | -0.028906 | 0.019719 | 122.6102 | 122.4845 | 122.5725 | 122.5183 | 122.6391 | 122.6106 | 122.5172 | -0.025347 | 0.13874 | -0.017954 | -0.143 | 0.039079 | 0.091891 | -0.028906 | 0.019719 | -0.064426 | 0.003559 | -0.057033 | 0.010952
2244.1406 | 122.699 | -122.5433 | 0.24719 | 0.076067 | -0.049678 | 0.038365 | -0.01586 | 0.10493 | 0.076426 | -0.021514 | -0.01619 | 0.15706 | 0.004937 | -0.15216 | 0.048236 | 0.096469 | -0.028906 | 0.019719 | 122.6194 | 122.4937 | 122.5817 | 122.5275 | 122.6483 | 122.6198 | 122.5218 | -0.01619 | 0.15706 | 0.004937 | -0.15216 | 0.048236 | 0.096469 | -0.028906 | 0.019719 | -0.064426 | 0.012716 | -0.043299 | 0.033843
2245.8281 | 122.7539 | -122.4976 | 0.23804 | 0.076067 | -0.054257 | 0.033786 | -0.011281 | 0.10951 | 0.067269 | -0.016936 | 0.020438 | 0.15706 | -0.013376 | -0.143 | 0.039079 | 0.091891 | -0.028906 | 0.019719 | 122.5736 | 122.4433 | 122.5313 | 122.4863 | 122.6071 | 122.5648 | 122.4806 | 0.020438 | 0.15706 | -0.013376 | -0.143 | 0.039079 | 0.091891 | -0.028906 | 0.019719 | -0.018641 | 0.049344 | -0.052455 | 0.01553
2247.5781 | 122.7081 | -122.5433 | 0.2243 | 0.080646 | -0.049678 | 0.033786 | -0.020438 | 0.10951 | 0.076426 | -0.021514 | -0.029925 | 0.13874 | -0.040846 | -0.13384 | 0.039079 | 0.091891 | -0.019749 | 0.024297 | 122.624 | 122.4937 | 122.5771 | 122.5229 | 122.6528 | 122.6198 | 122.5218 | -0.029925 | 0.13874 | -0.040846 | -0.13384 | 0.039079 | 0.091891 | -0.019749 | 0.024297 | -0.069004 | -0.010176 | -0.079925 | -0.021097
2249.3281 | 122.7905 | -122.525 | 0.21973 | 0.080646 | -0.054257 | 0.033786 | -0.020438 | 0.11409 | 0.081005 | -0.012357 | -0.034504 | 0.14332 | -0.031689 | -0.13842 | 0.043657 | 0.096469 | -0.033484 | 0.015141 | 122.6057 | 122.4708 | 122.5588 | 122.5046 | 122.6391 | 122.606 | 122.5127 | -0.034504 | 0.14332 | -0.031689 | -0.13842 | 0.043657 | 0.096469 | -0.033484 | 0.015141 | -0.078161 | -0.00102 | -0.075346 | 0.001795
2251.0781 | 122.7585 | -122.5525 | 0.24261 | 0.071489 | -0.054257 | 0.029208 | -0.01586 | 0.10951 | 0.085583 | -0.016936 | -0.052818 | 0.12501 | -0.040846 | -0.14758 | 0.043657 | 0.091891 | -0.028906 | 0.019719 | 122.624 | 122.4982 | 122.5817 | 122.5366 | 122.662 | 122.6381 | 122.5356 | -0.052818 | 0.12501 | -0.040846 | -0.14758 | 0.043657 | 0.091891 | -0.028906 | 0.019719 | -0.096475 | -0.023912 | -0.084503 | -0.01194
2252.75 | 122.7814 | -122.5296 | 0.20142 | 0.080646 | -0.054257 | 0.033786 | -0.025017 | 0.10493 | 0.071848 | -0.021514 | -0.043661 | 0.12043 | -0.059159 | -0.143 | 0.034501 | 0.10562 | -0.028906 | 0.024297 | 122.6102 | 122.4753 | 122.5634 | 122.5046 | 122.6345 | 122.6014 | 122.5081 | -0.043661 | 0.12043 | -0.059159 | -0.143 | 0.034501 | 0.10562 | -0.028906 | 0.024297 | -0.078162 | -0.014755 | -0.09366 | -0.030253
2254.5 | 122.8638 | -122.4976 | 0.19226 | 0.080646 | -0.058836 | 0.033786 | -0.025017 | 0.10951 | 0.071848 | -0.016936 | 0.043331 | 0.16164 | -0.004219 | -0.13842 | 0.029923 | 0.091891 | -0.028906 | 0.019719 | 122.5782 | 122.4387 | 122.5313 | 122.4725 | 122.6071 | 122.5694 | 122.4806 | 0.043331 | 0.16164 | -0.004219 | -0.13842 | 0.029923 | 0.091891 | -0.028906 | 0.019719 | 0.013408 | 0.072237 | -0.034142 | 0.024687
2256.25 | 122.7585 | -122.5479 | 0.20599 | 0.080646 | -0.063415 | 0.033786 | -0.020438 | 0.10493 | 0.076426 | -0.016936 | 0.047909 | 0.16164 | 0.009515 | -0.143 | 0.039079 | 0.10105 | -0.028906 | 0.024297 | 122.6286 | 122.4845 | 122.5817 | 122.5275 | 122.6528 | 122.6243 | 122.531 | 0.047909 | 0.16164 | 0.009515 | -0.143 | 0.039079 | 0.10105 | -0.028906 | 0.024297 | 0.00883 | 0.076815 | -0.029564 | 0.038421
2258 | 122.7768 | -122.5433 | 0.24261 | 0.076067 | -0.0451 | 0.042944 | -0.020438 | 0.10951 | 0.085583 | -0.021514 | 0.070802 | 0.16622 | 0.014094 | -0.143 | 0.043657 | 0.091891 | -0.028906 | 0.019719 | 122.6194 | 122.4982 | 122.5863 | 122.5229 | 122.6528 | 122.6289 | 122.5218 | 0.070802 | 0.16622 | 0.014094 | -0.143 | 0.043657 | 0.091891 | -0.028906 | 0.019719 | 0.027145 | 0.099708 | -0.029563 | 0.043
2259.7031 | 122.8134 | -122.5159 | 0.23346 | 0.076067 | -0.058836 | 0.033786 | -0.020438 | 0.10493 | 0.076426 | -0.016936 | 0.020438 | 0.16164 | -0.027111 | -0.143 | 0.043657 | 0.10105 | -0.028906 | 0.019719 | 122.5919 | 122.457 | 122.5497 | 122.4954 | 122.6208 | 122.5923 | 122.4989 | 0.020438 | 0.16164 | -0.027111 | -0.143 | 0.043657 | 0.10105 | -0.028906 | 0.019719 | -0.023219 | 0.049344 | -0.070768 | 0.001795
2261.4688 | 122.8592 | -122.5021 | 0.19226 | 0.076067 | -0.054257 | 0.029208 | -0.020438 | 0.10493 | 0.076426 | -0.026092 | 0.002124 | 0.15706 | -0.045424 | -0.143 | 0.039079 | 0.096469 | -0.024328 | 0.010563 | 122.5782 | 122.4479 | 122.5313 | 122.4817 | 122.6071 | 122.5786 | 122.476 | 0.002124 | 0.15706 | -0.045424 | -0.143 | 0.039079 | 0.096469 | -0.024328 | 0.010563 | -0.036955 | 0.026452 | -0.084503 | -0.021096
2263.2031 | 122.8867 | -122.5113 | 0.19684 | 0.076067 | -0.0451 | 0.038365 | -0.020438 | 0.10036 | 0.081005 | -0.016936 | -0.043661 | 0.14332 | -0.036267 | -0.143 | 0.043657 | 0.096469 | -0.028906 | 0.015141 | 122.5874 | 122.4662 | 122.5497 | 122.4909 | 122.6116 | 122.5923 | 122.4944 | -0.043661 | 0.14332 | -0.036267 | -0.143 | 0.043657 | 0.096469 | -0.028906 | 0.015141 | -0.087318 | -0.014755 | -0.079924 | -0.007361
2264.9688 | 122.8821 | -122.5296 | 0.20142 | 0.076067 | -0.049678 | 0.038365 | -0.01586 | 0.10951 | 0.076426 | -0.016936 | -0.034504 | 0.16164 | -0.036267 | -0.143 | 0.043657 | 0.091891 | -0.033484 | 0.015141 | 122.6057 | 122.4799 | 122.568 | 122.5137 | 122.6391 | 122.606 | 122.5127 | -0.034504 | 0.16164 | -0.036267 | -0.143 | 0.043657 | 0.091891 | -0.033484 | 0.015141 | -0.078161 | -0.00102 | -0.079924 | -0.002783
2266.6562 | 122.8592 | -122.5388 | 0.21515 | 0.076067 | -0.054257 | 0.038365 | -0.01586 | 0.10493 | 0.071848 | -0.016936 | -0.048239 | 0.14332 | -0.059159 | -0.14758 | 0.043657 | 0.096469 | -0.033484 | 0.015141 | 122.6148 | 122.4845 | 122.5771 | 122.5229 | 122.6437 | 122.6106 | 122.5218 | -0.048239 | 0.14332 | -0.059159 | -0.14758 | 0.043657 | 0.096469 | -0.033484 | 0.015141 | -0.091896 | -0.014755 | -0.10282 | -0.025675
2268.4062 | 122.7905 | -122.58 | 0.2243 | 0.076067 | -0.049678 | 0.042944 | -0.006703 | 0.10036 | 0.076426 | -0.012357 | 0.006703 | 0.1479 | -0.017954 | -0.14758 | 0.039079 | 0.091891 | -0.051798 | 0.005985 | 122.656 | 122.5303 | 122.6229 | 122.5733 | 122.6803 | 122.6564 | 122.5676 | 0.006703 | 0.1479 | -0.017954 | -0.14758 | 0.039079 | 0.091891 | -0.051798 | 0.005985 | -0.032376 | 0.058501 | -0.057033 | 0.033844
2270.1562 | 122.8317 | -122.5479 | 0.19226 | 0.076067 | -0.054257 | 0.033786 | -0.01586 | 0.10036 | 0.076426 | -0.026092 | 0.038752 | 0.17079 | -0.008798 | -0.13842 | 0.039079 | 0.091891 | -0.056376 | -0.00775 | 122.624 | 122.4937 | 122.5817 | 122.5321 | 122.6483 | 122.6243 | 122.5218 | 0.038752 | 0.17079 | -0.008798 | -0.13842 | 0.039079 | 0.091891 | -0.056376 | -0.00775 | -0.000327 | 0.095128 | -0.047877 | 0.047578
2271.8438 | 122.905 | -122.5342 | 0.18768 | 0.080646 | -0.0451 | 0.038365 | -0.01586 | 0.10493 | 0.071848 | -0.021514 | -0.025347 | 0.12958 | -0.050002 | -0.143 | 0.043657 | 0.096469 | -0.051798 | -0.003172 | 122.6148 | 122.4891 | 122.5725 | 122.5183 | 122.6391 | 122.606 | 122.5127 | -0.025347 | 0.12958 | -0.050002 | -0.143 | 0.043657 | 0.096469 | -0.051798 | -0.003172 | -0.069004 | 0.026451 | -0.093659 | 0.001796
2273.5781 | 122.731 | -122.5616 | 0.24261 | 0.085224 | -0.058836 | 0.033786 | -0.020438 | 0.10951 | 0.076426 | -0.026092 | -0.011611 | 0.14332 | -0.063737 | -0.143 | 0.039079 | 0.096469 | -0.060955 | -0.003172 | 122.6469 | 122.5028 | 122.5954 | 122.5412 | 122.6712 | 122.6381 | 122.5356 | -0.011611 | 0.14332 | -0.063737 | -0.143 | 0.039079 | 0.096469 | -0.060955 | -0.003172 | -0.05069 | 0.049344 | -0.10282 | -0.002782
2275.3281 | 122.8409 | -122.5571 | 0.21057 | 0.071489 | -0.054257 | 0.029208 | -0.01586 | 0.10951 | 0.076426 | -0.012357 | -0.048239 | 0.12958 | -0.040846 | -0.143 | 0.029923 | 0.096469 | -0.051798 | 0.001406 | 122.6286 | 122.5028 | 122.5863 | 122.5412 | 122.6666 | 122.6335 | 122.5447 | -0.048239 | 0.12958 | -0.040846 | -0.143 | 0.029923 | 0.096469 | -0.051798 | 0.001406 | -0.078162 | 0.003559 | -0.070769 | 0.010952
2277.0938 | 122.905 | -122.525 | 0.20599 | 0.076067 | -0.049678 | 0.033786 | -0.01586 | 0.10951 | 0.081005 | -0.016936 | -0.043661 | 0.13874 | -0.059159 | -0.14758 | 0.034501 | 0.091891 | -0.051798 | -0.00775 | 122.6011 | 122.4753 | 122.5588 | 122.5092 | 122.6345 | 122.606 | 122.5081 | -0.043661 | 0.13874 | -0.059159 | -0.14758 | 0.034501 | 0.091891 | -0.051798 | -0.00775 | -0.078162 | 0.008137 | -0.09366 | -0.007361
2278.8438 | 122.8683 | -122.5296 | 0.1831 | 0.080646 | -0.0451 | 0.038365 | -0.020438 | 0.10493 | 0.071848 | -0.012357 | 0.029595 | 0.15706 | 0.009515 | -0.13842 | 0.039079 | 0.096469 | -0.051798 | -0.00775 | 122.6102 | 122.4845 | 122.568 | 122.5092 | 122.6345 | 122.6014 | 122.5172 | 0.029595 | 0.15706 | 0.009515 | -0.13842 | 0.039079 | 0.096469 | -0.051798 | -0.00775 | -0.009484 | 0.081393 | -0.029564 | 0.061313
2280.5312 | 122.8134 | -122.5616 | 0.21515 | 0.076067 | -0.054257 | 0.042944 | -0.020438 | 0.10493 | 0.085583 | -0.021514 | -0.007033 | 0.15248 | -0.05458 | -0.14758 | 0.034501 | 0.091891 | -0.042641 | 0.010563 | 122.6377 | 122.5074 | 122.6046 | 122.5412 | 122.6666 | 122.6472 | 122.5401 | -0.007033 | 0.15248 | -0.05458 | -0.14758 | 0.034501 | 0.091891 | -0.042641 | 0.010563 | -0.041534 | 0.035608 | -0.089081 | -0.011939
2282.2812 | 122.8958 | -122.5616 | 0.23346 | 0.076067 | -0.0451 | 0.033786 | -0.025017 | 0.11867 | 0.076426 | -0.021514 | 0.038752 | 0.17995 | -0.022532 | -0.13842 | 0.043657 | 0.087313 | -0.042641 | 0.010563 | 122.6377 | 122.5165 | 122.5954 | 122.5366 | 122.6803 | 122.6381 | 122.5401 | 0.038752 | 0.17995 | -0.022532 | -0.13842 | 0.043657 | 0.087313 | -0.042641 | 0.010563 | -0.004905 | 0.081393 | -0.066189 | 0.020109
2284.0469 | 122.8546 | -122.5525 | 0.20599 | 0.071489 | -0.0451 | 0.042944 | -0.01586 | 0.10493 | 0.071848 | -0.016936 | -0.039082 | 0.15706 | -0.031689 | -0.143 | 0.039079 | 0.096469 | -0.033484 | 0.010563 | 122.624 | 122.5074 | 122.5954 | 122.5366 | 122.6574 | 122.6243 | 122.5356 | -0.039082 | 0.15706 | -0.031689 | -0.143 | 0.039079 | 0.096469 | -0.033484 | 0.010563 | -0.078161 | -0.005598 | -0.070768 | 0.001795
2285.7344 | 122.7814 | -122.5571 | 0.22888 | 0.071489 | -0.054257 | 0.038365 | -0.011281 | 0.11409 | 0.071848 | -0.016936 | 0.061645 | 0.17079 | -0.017954 | -0.143 | 0.043657 | 0.096469 | -0.038063 | 0.015141 | 122.6286 | 122.5028 | 122.5954 | 122.5458 | 122.6712 | 122.6289 | 122.5401 | 0.061645 | 0.17079 | -0.017954 | -0.143 | 0.043657 | 0.096469 | -0.038063 | 0.015141 | 0.017988 | 0.099708 | -0.061611 | 0.020109
2287.4844 | 122.8912 | -122.5113 | 0.18768 | 0.080646 | -0.058836 | 0.038365 | -0.020438 | 0.11409 | 0.076426 | -0.021514 | 0.066223 | 0.17995 | 0.004937 | -0.14758 | 0.034501 | 0.096469 | -0.042641 | 0.015141 | 122.5919 | 122.4525 | 122.5497 | 122.4909 | 122.6254 | 122.5877 | 122.4898 | 0.066223 | 0.17995 | 0.004937 | -0.14758 | 0.034501 | 0.096469 | -0.042641 | 0.015141 | 0.031722 | 0.10886 | -0.029564 | 0.047578
2289.2344 | 122.7722 | -122.5983 | 0.24719 | 0.085224 | -0.054257 | 0.033786 | -0.020438 | 0.10493 | 0.081005 | -0.016936 | 0.025017 | 0.16622 | 0.004937 | -0.13842 | 0.048236 | 0.096469 | -0.033484 | 0.010563 | 122.6835 | 122.544 | 122.6321 | 122.5778 | 122.7032 | 122.6793 | 122.5813 | 0.025017 | 0.16622 | 0.004937 | -0.13842 | 0.048236 | 0.096469 | -0.033484 | 0.010563 | -0.023219 | 0.058501 | -0.043299 | 0.038421
2290.9844 | 122.7722 | -122.5937 | 0.21515 | 0.076067 | -0.040521 | 0.038365 | -0.01586 | 0.10951 | 0.076426 | -0.007779 | 0.043331 | 0.14332 | -0.013376 | -0.15216 | 0.029923 | 0.091891 | -0.04722 | 0.001406 | 122.6698 | 122.5532 | 122.6321 | 122.5778 | 122.7032 | 122.6701 | 122.5859 | 0.043331 | 0.14332 | -0.013376 | -0.15216 | 0.029923 | 0.091891 | -0.04722 | 0.001406 | 0.013408 | 0.090551 | -0.043299 | 0.033844
2292.6719 | 122.8134 | -122.5616 | 0.20599 | 0.080646 | -0.049678 | 0.038365 | -0.01586 | 0.10493 | 0.076426 | -0.007779 | -0.007033 | 0.16164 | -0.031689 | -0.143 | 0.043657 | 0.091891 | -0.042641 | 0.001406 | 122.6423 | 122.512 | 122.6 | 122.5458 | 122.6666 | 122.6381 | 122.5539 | -0.007033 | 0.16164 | -0.031689 | -0.143 | 0.043657 | 0.091891 | -0.042641 | 0.001406 | -0.05069 | 0.035608 | -0.075346 | 0.010952
2294.4375 | 122.8088 | -122.6212 | 0.24261 | 0.080646 | -0.054257 | 0.038365 | -0.01586 | 0.10951 | 0.076426 | -0.016936 | 0.034174 | 0.17079 | -0.040846 | -0.143 | 0.043657 | 0.091891 | -0.038063 | 0.005985 | 122.7018 | 122.5669 | 122.6595 | 122.6053 | 122.7307 | 122.6976 | 122.6042 | 0.034174 | 0.17079 | -0.040846 | -0.143 | 0.043657 | 0.091891 | -0.038063 | 0.005985 | -0.009483 | 0.072237 | -0.084503 | -0.002783
2296.125 | 122.8043 | -122.6028 | 0.23804 | 0.080646 | -0.058836 | 0.038365 | -0.01586 | 0.10951 | 0.071848 | -0.016936 | -0.029925 | 0.14332 | -0.017954 | -0.14758 | 0.043657 | 0.091891 | -0.042641 | 0.001406 | 122.6835 | 122.544 | 122.6412 | 122.587 | 122.7124 | 122.6747 | 122.5859 | -0.029925 | 0.14332 | -0.017954 | -0.14758 | 0.043657 | 0.091891 | -0.042641 | 0.001406 | -0.073582 | 0.012716 | -0.061611 | 0.024687
2297.875 | 122.8455 | -122.6028 | 0.21515 | 0.076067 | -0.049678 | 0.033786 | -0.01586 | 0.10493 | 0.076426 | -0.016936 | -0.029925 | 0.13874 | -0.05458 | -0.143 | 0.034501 | 0.096469 | -0.042641 | -0.003172 | 122.6789 | 122.5532 | 122.6366 | 122.587 | 122.7078 | 122.6793 | 122.5859 | -0.029925 | 0.13874 | -0.05458 | -0.143 | 0.034501 | 0.096469 | -0.042641 | -0.003172 | -0.064426 | 0.012716 | -0.089081 | -0.011939
2299.625 | 122.8363 | -122.6028 | 0.2243 | 0.071489 | -0.049678 | 0.033786 | -0.020438 | 0.10951 | 0.076426 | -0.016936 | 0.052488 | 0.16622 | -0.008798 | -0.143 | 0.048236 | 0.10105 | -0.051798 | -0.003172 | 122.6743 | 122.5532 | 122.6366 | 122.5824 | 122.7124 | 122.6793 | 122.5859 | 0.052488 | 0.16622 | -0.008798 | -0.143 | 0.048236 | 0.10105 | -0.051798 | -0.003172 | 0.004252 | 0.10429 | -0.057034 | 0.043
2301.375 | 122.8775 | -122.5479 | 0.19226 | 0.076067 | -0.054257 | 0.038365 | -0.020438 | 0.11409 | 0.081005 | -0.021514 | 0.047909 | 0.15706 | 0.009515 | -0.14758 | 0.034501 | 0.096469 | -0.038063 | 0.005985 | 122.624 | 122.4937 | 122.5863 | 122.5275 | 122.662 | 122.6289 | 122.5264 | 0.047909 | 0.15706 | 0.009515 | -0.14758 | 0.034501 | 0.096469 | -0.038063 | 0.005985 | 0.013408 | 0.085972 | -0.024986 | 0.047578
2303.1406 | 122.8775 | -122.5525 | 0.21515 | 0.080646 | -0.054257 | 0.033786 | -0.025017 | 0.11409 | 0.076426 | -0.021514 | 0.084537 | 0.18453 | 0.02325 | -0.143 | 0.034501 | 0.096469 | -0.04722 | 0.001406 | 122.6331 | 122.4982 | 122.5863 | 122.5275 | 122.6666 | 122.6289 | 122.531 | 0.084537 | 0.18453 | 0.02325 | -0.143 | 0.034501 | 0.096469 | -0.04722 | 0.001406 | 0.050036 | 0.13176 | -0.011251 | 0.07047
2304.8438 | 122.818 | -122.58 | 0.2243 | 0.080646 | -0.049678 | 0.038365 | -0.025017 | 0.10951 | 0.071848 | -0.021514 | 0.020438 | 0.17995 | -0.022532 | -0.13842 | 0.039079 | 0.091891 | -0.038063 | 0.010563 | 122.6606 | 122.5303 | 122.6183 | 122.5549 | 122.6895 | 122.6518 | 122.5584 | 0.020438 | 0.17995 | -0.022532 | -0.13842 | 0.039079 | 0.091891 | -0.038063 | 0.010563 | -0.018641 | 0.058501 | -0.061611 | 0.015531
2306.5938 | 122.7814 | -122.6074 | 0.23804 | 0.071489 | -0.049678 | 0.038365 | -0.01586 | 0.10951 | 0.085583 | -0.012357 | 0.043331 | 0.17995 | -0.022532 | -0.143 | 0.043657 | 0.091891 | -0.038063 | 0.010563 | 122.6789 | 122.5577 | 122.6458 | 122.5916 | 122.7169 | 122.693 | 122.5951 | 0.043331 | 0.17995 | -0.022532 | -0.143 | 0.043657 | 0.091891 | -0.038063 | 0.010563 | -0.000326 | 0.081394 | -0.066189 | 0.015531
2308.3438 | 122.9462 | -122.5571 | 0.20142 | 0.076067 | -0.049678 | 0.033786 | -0.01586 | 0.11409 | 0.085583 | -0.016936 | -0.071132 | 0.13416 | -0.05458 | -0.13842 | 0.048236 | 0.087313 | -0.033484 | 0.010563 | 122.6331 | 122.5074 | 122.5909 | 122.5412 | 122.6712 | 122.6427 | 122.5401 | -0.071132 | 0.13416 | -0.05458 | -0.13842 | 0.048236 | 0.087313 | -0.033484 | 0.010563 | -0.11937 | -0.037648 | -0.10282 | -0.021096
2310.0938 | 122.8088 | -122.6212 | 0.23346 | 0.076067 | -0.0451 | 0.033786 | -0.011281 | 0.10951 | 0.076426 | -0.016936 | -0.020768 | 0.14332 | -0.045424 | -0.143 | 0.043657 | 0.096469 | -0.038063 | 0.005985 | 122.6972 | 122.5761 | 122.6549 | 122.6099 | 122.7307 | 122.6976 | 122.6042 | -0.020768 | 0.14332 | -0.045424 | -0.143 | 0.043657 | 0.096469 | -0.038063 | 0.005985 | -0.064425 | 0.017295 | -0.089081 | -0.007361
2311.8438 | 122.8546 | -122.5845 | 0.20599 | 0.076067 | -0.049678 | 0.029208 | -0.01586 | 0.10951 | 0.076426 | -0.016936 | -0.034504 | 0.15248 | -0.063737 | -0.14758 | 0.039079 | 0.091891 | -0.033484 | 0.010563 | 122.6606 | 122.5349 | 122.6137 | 122.5687 | 122.694 | 122.661 | 122.5676 | -0.034504 | 0.15248 | -0.063737 | -0.14758 | 0.039079 | 0.091891 | -0.033484 | 0.010563 | -0.073583 | -0.00102 | -0.10282 | -0.030253
2313.5312 | 122.9141 | -122.6028 | 0.20599 | 0.076067 | -0.054257 | 0.029208 | -0.020438 | 0.10951 | 0.081005 | -0.021514 | 0.002124 | 0.1479 | -0.027111 | -0.15216 | 0.034501 | 0.096469 | -0.051798 | 0.005985 | 122.6789 | 122.5486 | 122.6321 | 122.5824 | 122.7124 | 122.6838 | 122.5813 | 0.002124 | 0.1479 | -0.027111 | -0.15216 | 0.034501 | 0.096469 | -0.051798 | 0.005985 | -0.032377 | 0.053922 | -0.061612 | 0.024687
2315.2656 | 122.9279 | -122.5845 | 0.20599 | 0.080646 | -0.054257 | 0.038365 | -0.01586 | 0.10951 | 0.081005 | -0.016936 | -0.011611 | 0.1479 | -0.031689 | -0.13842 | 0.039079 | 0.096469 | -0.038063 | 0.005985 | 122.6652 | 122.5303 | 122.6229 | 122.5687 | 122.694 | 122.6655 | 122.5676 | -0.011611 | 0.1479 | -0.031689 | -0.13842 | 0.039079 | 0.096469 | -0.038063 | 0.005985 | -0.05069 | 0.026452 | -0.070768 | 0.006374
2317.0312 | 122.85 | -122.6257 | 0.23804 | 0.071489 | -0.049678 | 0.024629 | -0.011281 | 0.10036 | 0.081005 | -0.012357 | -0.011611 | 0.17079 | -0.027111 | -0.14758 | 0.043657 | 0.096469 | -0.038063 | 0.005985 | 122.6972 | 122.5761 | 122.6504 | 122.6145 | 122.7261 | 122.7067 | 122.6134 | -0.011611 | 0.17079 | -0.027111 | -0.14758 | 0.043657 | 0.096469 | -0.038063 | 0.005985 | -0.055268 | 0.026452 | -0.070768 | 0.010952
2318.7188 | 122.8134 | -122.6349 | 0.22888 | 0.076067 | -0.054257 | 0.020051 | -0.011281 | 0.10493 | 0.081005 | -0.016936 | 0.043331 | 0.16164 | 0.018672 | -0.14758 | 0.048236 | 0.091891 | -0.042641 | 0.005985 | 122.711 | 122.5806 | 122.6549 | 122.6236 | 122.7398 | 122.7159 | 122.618 | 0.043331 | 0.16164 | 0.018672 | -0.14758 | 0.048236 | 0.091891 | -0.042641 | 0.005985 | -0.004905 | 0.085972 | -0.029564 | 0.061313
2320.4688 | 122.8363 | -122.6028 | 0.2243 | 0.071489 | -0.0451 | 0.033786 | -0.020438 | 0.10951 | 0.076426 | -0.016936 | -0.034504 | 0.15248 | -0.050002 | -0.143 | 0.048236 | 0.091891 | -0.038063 | 0.005985 | 122.6743 | 122.5577 | 122.6366 | 122.5824 | 122.7124 | 122.6793 | 122.5859 | -0.034504 | 0.15248 | -0.050002 | -0.143 | 0.048236 | 0.091891 | -0.038063 | 0.005985 | -0.08274 | 0.003559 | -0.098238 | -0.011939
2322.2344 | 122.9462 | -122.5845 | 0.18768 | 0.076067 | -0.058836 | 0.038365 | -0.01586 | 0.10951 | 0.067269 | -0.021514 | -0.061975 | 0.13416 | -0.072894 | -0.13842 | 0.039079 | 0.091891 | -0.038063 | 0.010563 | 122.6606 | 122.5257 | 122.6229 | 122.5687 | 122.694 | 122.6518 | 122.563 | -0.061975 | 0.13416 | -0.072894 | -0.13842 | 0.039079 | 0.091891 | -0.038063 | 0.010563 | -0.10105 | -0.023912 | -0.11197 | -0.034831
2323.9219 | 122.9599 | -122.6074 | 0.18768 | 0.071489 | -0.054257 | 0.033786 | -0.01586 | 0.10951 | 0.081005 | -0.021514 | -0.025347 | 0.12958 | -0.05458 | -0.143 | 0.039079 | 0.091891 | -0.04722 | 0.005985 | 122.6789 | 122.5532 | 122.6412 | 122.5916 | 122.7169 | 122.6884 | 122.5859 | -0.025347 | 0.12958 | -0.05458 | -0.143 | 0.039079 | 0.091891 | -0.04722 | 0.005985 | -0.064426 | 0.021873 | -0.093659 | -0.00736
2325.6719 | 122.8775 | -122.6074 | 0.19684 | 0.071489 | -0.049678 | 0.038365 | -0.020438 | 0.11409 | 0.071848 | -0.026092 | -0.043661 | 0.12958 | -0.068315 | -0.13842 | 0.039079 | 0.096469 | -0.038063 | 0.010563 | 122.6789 | 122.5577 | 122.6458 | 122.587 | 122.7215 | 122.6793 | 122.5813 | -0.043661 | 0.12958 | -0.068315 | -0.13842 | 0.039079 | 0.096469 | -0.038063 | 0.010563 | -0.08274 | -0.005598 | -0.10739 | -0.030252
2327.4219 | 122.8088 | -122.6486 | 0.22888 | 0.071489 | -0.058836 | 0.024629 | -0.020438 | 0.10951 | 0.081005 | -0.016936 | -0.034504 | 0.13874 | -0.068315 | -0.13842 | 0.039079 | 0.087313 | -0.033484 | 0.001406 | 122.7201 | 122.5898 | 122.6733 | 122.6282 | 122.7581 | 122.7296 | 122.6317 | -0.034504 | 0.13874 | -0.068315 | -0.13842 | 0.039079 | 0.087313 | -0.033484 | 0.001406 | -0.073583 | -0.00102 | -0.10739 | -0.034831
2329.125 | 122.85 | -122.6257 | 0.20599 | 0.076067 | -0.054257 | 0.033786 | -0.01586 | 0.10036 | 0.071848 | -0.016936 | -0.01619 | 0.15248 | -0.036267 | -0.143 | 0.043657 | 0.10105 | -0.042641 | 0.005985 | 122.7018 | 122.5715 | 122.6595 | 122.6099 | 122.7261 | 122.6976 | 122.6088 | -0.01619 | 0.15248 | -0.036267 | -0.143 | 0.043657 | 0.10105 | -0.042641 | 0.005985 | -0.059847 | 0.026451 | -0.079924 | 0.006374
2330.875 | 122.905 | -122.612 | 0.17853 | 0.06691 | -0.058836 | 0.033786 | -0.01586 | 0.10036 | 0.076426 | -0.021514 | -0.043661 | 0.14332 | -0.068315 | -0.13384 | 0.039079 | 0.096469 | -0.033484 | 0.001406 | 122.6789 | 122.5532 | 122.6458 | 122.5961 | 122.7124 | 122.6884 | 122.5905 | -0.043661 | 0.14332 | -0.068315 | -0.13384 | 0.039079 | 0.096469 | -0.033484 | 0.001406 | -0.08274 | -0.010177 | -0.10739 | -0.034831
2332.625 | 122.8592 | -122.6257 | 0.22888 | 0.076067 | -0.063415 | 0.033786 | -0.020438 | 0.10951 | 0.076426 | -0.021514 | -0.052818 | 0.12958 | -0.059159 | -0.14758 | 0.043657 | 0.091891 | -0.04722 | 0.010563 | 122.7018 | 122.5623 | 122.6595 | 122.6053 | 122.7352 | 122.7022 | 122.6042 | -0.052818 | 0.12958 | -0.059159 | -0.14758 | 0.043657 | 0.091891 | -0.04722 | 0.010563 | -0.096475 | -0.005598 | -0.10282 | -0.011939
2334.375 | 122.9691 | -122.6074 | 0.1831 | 0.076067 | -0.054257 | 0.033786 | -0.020438 | 0.10951 | 0.071848 | -0.016936 | -0.007033 | 0.15248 | -0.008798 | -0.143 | 0.039079 | 0.10105 | -0.042641 | -0.003172 | 122.6835 | 122.5532 | 122.6412 | 122.587 | 122.7169 | 122.6793 | 122.5905 | -0.007033 | 0.15248 | -0.008798 | -0.143 | 0.039079 | 0.10105 | -0.042641 | -0.003172 | -0.046112 | 0.035608 | -0.047877 | 0.033843
2336.125 | 122.818 | -122.6532 | 0.2243 | 0.06691 | -0.058836 | 0.038365 | -0.025017 | 0.10951 | 0.076426 | -0.016936 | -0.025347 | 0.16164 | -0.027111 | -0.14758 | 0.043657 | 0.091891 | -0.042641 | 0.001406 | 122.7201 | 122.5944 | 122.6916 | 122.6282 | 122.7627 | 122.7296 | 122.6363 | -0.025347 | 0.16164 | -0.027111 | -0.14758 | 0.043657 | 0.091891 | -0.042641 | 0.001406 | -0.069004 | 0.017294 | -0.070768 | 0.01553
2337.8281 | 122.8271 | -122.6395 | 0.2243 | 0.076067 | -0.049678 | 0.033786 | -0.01586 | 0.10951 | 0.081005 | -0.016936 | 0.057066 | 0.16622 | 0.018672 | -0.13384 | 0.039079 | 0.10105 | -0.04722 | 0.001406 | 122.7155 | 122.5898 | 122.6733 | 122.6236 | 122.749 | 122.7205 | 122.6225 | 0.057066 | 0.16622 | 0.018672 | -0.13384 | 0.039079 | 0.10105 | -0.04722 | 0.001406 | 0.017987 | 0.10429 | -0.020407 | 0.065892
2339.5625 | 122.9416 | -122.6074 | 0.20142 | 0.076067 | -0.058836 | 0.029208 | -0.025017 | 0.11409 | 0.076426 | -0.016936 | -0.048239 | 0.13874 | -0.068315 | -0.143 | 0.029923 | 0.091891 | -0.038063 | 0.005985 | 122.6835 | 122.5486 | 122.6366 | 122.5824 | 122.7215 | 122.6838 | 122.5905 | -0.048239 | 0.13874 | -0.068315 | -0.143 | 0.029923 | 0.091891 | -0.038063 | 0.005985 | -0.078162 | -0.010176 | -0.098238 | -0.030252
2341.25 | 122.8867 | -122.644 | 0.20142 | 0.071489 | -0.058836 | 0.029208 | -0.020438 | 0.10951 | 0.076426 | -0.021514 | -0.020768 | 0.17537 | -0.013376 | -0.143 | 0.034501 | 0.096469 | -0.042641 | 0.005985 | 122.7155 | 122.5852 | 122.6733 | 122.6236 | 122.7536 | 122.7205 | 122.6225 | -0.020768 | 0.17537 | -0.013376 | -0.143 | 0.034501 | 0.096469 | -0.042641 | 0.005985 | -0.055269 | 0.021873 | -0.047877 | 0.029265
2343.0156 | 122.9507 | -122.6303 | 0.19226 | 0.076067 | -0.049678 | 0.029208 | -0.020438 | 0.095778 | 0.081005 | -0.012357 | 0.038752 | 0.15248 | -0.017954 | -0.143 | 0.043657 | 0.091891 | -0.04722 | 0.010563 | 122.7064 | 122.5806 | 122.6595 | 122.6099 | 122.7261 | 122.7113 | 122.618 | 0.038752 | 0.15248 | -0.017954 | -0.143 | 0.043657 | 0.091891 | -0.04722 | 0.010563 | -0.004905 | 0.085972 | -0.061611 | 0.029266
2344.7656 | 122.9736 | -122.6212 | 0.21057 | 0.071489 | -0.049678 | 0.033786 | -0.01586 | 0.10951 | 0.076426 | -0.026092 | -0.052818 | 0.13874 | -0.063737 | -0.13842 | 0.043657 | 0.10105 | -0.038063 | 0.005985 | 122.6926 | 122.5715 | 122.6549 | 122.6053 | 122.7307 | 122.6976 | 122.5951 | -0.052818 | 0.13874 | -0.063737 | -0.13842 | 0.043657 | 0.10105 | -0.038063 | 0.005985 | -0.096475 | -0.014755 | -0.10739 | -0.025674
2346.5312 | 122.9462 | -122.644 | 0.19226 | 0.071489 | -0.054257 | 0.024629 | -0.020438 | 0.10951 | 0.076426 | -0.016936 | -0.098602 | 0.12043 | -0.063737 | -0.143 | 0.043657 | 0.096469 | -0.04722 | 0.005985 | 122.7155 | 122.5898 | 122.6687 | 122.6236 | 122.7536 | 122.7205 | 122.6271 | -0.098602 | 0.12043 | -0.063737 | -0.143 | 0.043657 | 0.096469 | -0.04722 | 0.005985 | -0.14226 | -0.051382 | -0.10739 | -0.016517
2348.2344 | 122.8592 | -122.6624 | 0.21973 | 0.080646 | -0.049678 | 0.038365 | -0.01586 | 0.10951 | 0.071848 | -0.021514 | -0.094024 | 0.10669 | -0.068315 | -0.14758 | 0.039079 | 0.096469 | -0.042641 | 0.010563 | 122.743 | 122.6127 | 122.7007 | 122.6465 | 122.7719 | 122.7342 | 122.6408 | -0.094024 | 0.10669 | -0.068315 | -0.14758 | 0.039079 | 0.096469 | -0.042641 | 0.010563 | -0.1331 | -0.051383 | -0.10739 | -0.025674
2349.9844 | 122.9279 | -122.6166 | 0.20599 | 0.076067 | -0.049678 | 0.033786 | -0.01586 | 0.10951 | 0.081005 | -0.021514 | -0.061975 | 0.13416 | -0.063737 | -0.14758 | 0.039079 | 0.096469 | -0.042641 | -0.00775 | 122.6926 | 122.5669 | 122.6504 | 122.6007 | 122.7261 | 122.6976 | 122.5951 | -0.061975 | 0.13416 | -0.063737 | -0.14758 | 0.039079 | 0.096469 | -0.042641 | -0.00775 | -0.10105 | -0.019334 | -0.10282 | -0.021096
2351.7344 | 122.9095 | -122.6578 | 0.21057 | 0.080646 | -0.049678 | 0.029208 | -0.01586 | 0.10036 | 0.085583 | -0.021514 | -0.098602 | 0.10669 | -0.068315 | -0.13842 | 0.029923 | 0.10105 | -0.042641 | 0.001406 | 122.7384 | 122.6081 | 122.687 | 122.6419 | 122.7581 | 122.7434 | 122.6363 | -0.098602 | 0.10669 | -0.068315 | -0.13842 | 0.029923 | 0.10105 | -0.042641 | 0.001406 | -0.12853 | -0.055961 | -0.098238 | -0.025674
2353.4219 | 122.9645 | -122.6349 | 0.18768 | 0.076067 | -0.054257 | 0.033786 | -0.01586 | 0.10493 | 0.081005 | -0.021514 | -0.043661 | 0.11127 | -0.072894 | -0.143 | 0.034501 | 0.091891 | -0.038063 | 0.010563 | 122.711 | 122.5806 | 122.6687 | 122.619 | 122.7398 | 122.7159 | 122.6134 | -0.043661 | 0.11127 | -0.072894 | -0.143 | 0.034501 | 0.091891 | -0.038063 | 0.010563 | -0.078162 | -0.005598 | -0.10739 | -0.034831
2355.1562 | 122.9736 | -122.612 | 0.21515 | 0.076067 | -0.049678 | 0.038365 | -0.01586 | 0.10036 | 0.071848 | -0.021514 | -0.057396 | 0.12501 | -0.045424 | -0.143 | 0.034501 | 0.091891 | -0.038063 | 0.001406 | 122.6881 | 122.5623 | 122.6504 | 122.5961 | 122.7124 | 122.6838 | 122.5905 | -0.057396 | 0.12501 | -0.045424 | -0.143 | 0.034501 | 0.091891 | -0.038063 | 0.001406 | -0.091897 | -0.019333 | -0.079925 | -0.007361
2356.9062 | 122.9233 | -122.6303 | 0.1831 | 0.071489 | -0.0451 | 0.033786 | -0.020438 | 0.10036 | 0.076426 | -0.016936 | -0.061975 | 0.13416 | -0.072894 | -0.14758 | 0.039079 | 0.091891 | -0.038063 | 0.005985 | 122.7018 | 122.5852 | 122.6641 | 122.6099 | 122.7307 | 122.7067 | 122.6134 | -0.061975 | 0.13416 | -0.072894 | -0.14758 | 0.039079 | 0.091891 | -0.038063 | 0.005985 | -0.10105 | -0.023912 | -0.11197 | -0.034831
2358.6719 | 122.9004 | -122.6669 | 0.23346 | 0.080646 | -0.049678 | 0.038365 | -0.020438 | 0.10493 | 0.076426 | -0.021514 | -0.066553 | 0.15706 | -0.068315 | -0.14758 | 0.043657 | 0.096469 | -0.038063 | 0.001406 | 122.7476 | 122.6173 | 122.7053 | 122.6465 | 122.7719 | 122.7434 | 122.6454 | -0.066553 | 0.15706 | -0.068315 | -0.14758 | 0.043657 | 0.096469 | -0.038063 | 0.001406 | -0.11021 | -0.02849 | -0.11197 | -0.030252
2360.3594 | 122.8546 | -122.6807 | 0.21973 | 0.076067 | -0.054257 | 0.029208 | -0.006703 | 0.10493 | 0.076426 | -0.016936 | -0.080288 | 0.12501 | -0.063737 | -0.13842 | 0.043657 | 0.096469 | -0.033484 | 0.005985 | 122.7567 | 122.6264 | 122.7099 | 122.674 | 122.7856 | 122.7571 | 122.6637 | -0.080288 | 0.12501 | -0.063737 | -0.13842 | 0.043657 | 0.096469 | -0.033484 | 0.005985 | -0.12394 | -0.046804 | -0.10739 | -0.030253
2362.1094 | 122.9782 | -122.612 | 0.18768 | 0.080646 | -0.054257 | 0.024629 | -0.025017 | 0.10493 | 0.076426 | -0.026092 | -0.057396 | 0.13416 | -0.063737 | -0.143 | 0.043657 | 0.10105 | -0.033484 | 0.010563 | 122.6926 | 122.5577 | 122.6366 | 122.587 | 122.7169 | 122.6884 | 122.5859 | -0.057396 | 0.13416 | -0.063737 | -0.143 | 0.043657 | 0.10105 | -0.033484 | 0.010563 | -0.10105 | -0.023912 | -0.10739 | -0.030253
2363.8125 | 122.937 | -122.6303 | 0.21515 | 0.076067 | -0.054257 | 0.024629 | -0.020438 | 0.10493 | 0.081005 | -0.016936 | -0.01619 | 0.1479 | -0.040846 | -0.143 | 0.039079 | 0.096469 | -0.038063 | 0.005985 | 122.7064 | 122.5761 | 122.6549 | 122.6099 | 122.7352 | 122.7113 | 122.6134 | -0.01619 | 0.1479 | -0.040846 | -0.143 | 0.039079 | 0.096469 | -0.038063 | 0.005985 | -0.055269 | 0.021873 | -0.079925 | -0.002783
2365.5625 | 122.9782 | -122.644 | 0.20599 | 0.076067 | -0.0451 | 0.029208 | -0.01586 | 0.10951 | 0.076426 | -0.021514 | -0.057396 | 0.1479 | -0.05458 | -0.13842 | 0.039079 | 0.096469 | -0.038063 | 0.005985 | 122.7201 | 122.5989 | 122.6733 | 122.6282 | 122.7536 | 122.7205 | 122.6225 | -0.057396 | 0.1479 | -0.05458 | -0.13842 | 0.039079 | 0.096469 | -0.038063 | 0.005985 | -0.096475 | -0.019333 | -0.093659 | -0.016517
2367.3281 | 122.9553 | -122.6486 | 0.20599 | 0.062332 | -0.058836 | 0.038365 | -0.011281 | 0.10951 | 0.076426 | -0.021514 | -0.007033 | 0.12958 | -0.059159 | -0.143 | 0.043657 | 0.091891 | -0.033484 | 0.005985 | 122.711 | 122.5898 | 122.687 | 122.6373 | 122.7581 | 122.725 | 122.6271 | -0.007033 | 0.12958 | -0.059159 | -0.143 | 0.043657 | 0.091891 | -0.033484 | 0.005985 | -0.05069 | 0.026451 | -0.10282 | -0.025675
2369.0312 | 122.8363 | -122.6852 | 0.2243 | 0.076067 | -0.054257 | 0.024629 | -0.020438 | 0.11409 | 0.071848 | -0.012357 | -0.07571 | 0.12501 | -0.050002 | -0.14758 | 0.039079 | 0.096469 | -0.038063 | 0.001406 | 122.7613 | 122.631 | 122.7099 | 122.6648 | 122.7993 | 122.7571 | 122.6729 | -0.07571 | 0.12501 | -0.050002 | -0.14758 | 0.039079 | 0.096469 | -0.038063 | 0.001406 | -0.11479 | -0.037647 | -0.089081 | -0.011939
2370.7656 | 122.8775 | -122.6624 | 0.21973 | 0.080646 | -0.054257 | 0.033786 | -0.020438 | 0.10036 | 0.076426 | -0.016936 | -0.007033 | 0.16622 | -0.027111 | -0.13842 | 0.048236 | 0.091891 | -0.042641 | 0.001406 | 122.743 | 122.6081 | 122.6961 | 122.6419 | 122.7627 | 122.7388 | 122.6454 | -0.007033 | 0.16622 | -0.027111 | -0.13842 | 0.048236 | 0.091891 | -0.042641 | 0.001406 | -0.055269 | 0.035608 | -0.075347 | 0.01553
2372.4531 | 122.9279 | -122.6578 | 0.21057 | 0.076067 | -0.049678 | 0.038365 | -0.025017 | 0.10951 | 0.067269 | -0.026092 | -0.084867 | 0.1479 | -0.063737 | -0.14758 | 0.043657 | 0.10562 | -0.038063 | 0.005985 | 122.7338 | 122.6081 | 122.6961 | 122.6328 | 122.7673 | 122.725 | 122.6317 | -0.084867 | 0.1479 | -0.063737 | -0.14758 | 0.043657 | 0.10562 | -0.038063 | 0.005985 | -0.12852 | -0.046804 | -0.10739 | -0.025674
2374.2031 | 122.905 | -122.6898 | 0.2243 | 0.071489 | -0.054257 | 0.029208 | -0.01586 | 0.10036 | 0.076426 | -0.016936 | 0.07538 | 0.17537 | 0.046142 | -0.143 | 0.039079 | 0.091891 | -0.038063 | 0.005985 | 122.7613 | 122.6356 | 122.719 | 122.674 | 122.7902 | 122.7662 | 122.6729 | 0.07538 | 0.17537 | 0.046142 | -0.143 | 0.039079 | 0.091891 | -0.038063 | 0.005985 | 0.036301 | 0.11344 | 0.007063 | 0.084205
2375.9531 | 122.9919 | -122.6349 | 0.21057 | 0.076067 | -0.054257 | 0.024629 | -0.020438 | 0.10951 | 0.071848 | -0.026092 | -0.011611 | 0.17079 | -0.036267 | -0.13842 | 0.039079 | 0.096469 | -0.042641 | 0.005985 | 122.711 | 122.5806 | 122.6595 | 122.6145 | 122.7444 | 122.7067 | 122.6088 | -0.011611 | 0.17079 | -0.036267 | -0.13842 | 0.039079 | 0.096469 | -0.042641 | 0.005985 | -0.05069 | 0.03103 | -0.075346 | 0.006374
2377.6406 | 122.905 | -122.6715 | 0.25177 | 0.071489 | -0.054257 | 0.029208 | -0.020438 | 0.11409 | 0.076426 | -0.021514 | 0.043331 | 0.17995 | 0.014094 | -0.14758 | 0.048236 | 0.096469 | -0.042641 | 0.005985 | 122.743 | 122.6173 | 122.7007 | 122.6511 | 122.7856 | 122.7479 | 122.65 | 0.043331 | 0.17995 | 0.014094 | -0.14758 | 0.048236 | 0.096469 | -0.042641 | 0.005985 | -0.004905 | 0.085972 | -0.034142 | 0.056735
2379.3906 | 123.0057 | -122.6578 | 0.19226 | 0.06691 | -0.054257 | 0.029208 | -0.01586 | 0.10036 | 0.071848 | -0.026092 | -0.048239 | 0.15706 | -0.059159 | -0.143 | 0.039079 | 0.096469 | -0.04722 | 0.005985 | 122.7247 | 122.6035 | 122.687 | 122.6419 | 122.7581 | 122.7296 | 122.6317 | -0.048239 | 0.15706 | -0.059159 | -0.143 | 0.039079 | 0.096469 | -0.04722 | 0.005985 | -0.087318 | -0.001019 | -0.098238 | -0.011939
2381.1406 | 122.9141 | -122.6624 | 0.23346 | 0.071489 | -0.054257 | 0.033786 | -0.025017 | 0.10036 | 0.076426 | -0.026092 | 0.020438 | 0.1479 | -0.027111 | -0.13842 | 0.034501 | 0.10105 | -0.038063 | 0.005985 | 122.7338 | 122.6081 | 122.6961 | 122.6373 | 122.7627 | 122.7388 | 122.6363 | 0.020438 | 0.1479 | -0.027111 | -0.13842 | 0.034501 | 0.10105 | -0.038063 | 0.005985 | -0.014063 | 0.058501 | -0.061612 | 0.010952
2382.8281 | 122.9233 | -122.6807 | 0.22888 | 0.071489 | -0.063415 | 0.038365 | -0.020438 | 0.10036 | 0.071848 | -0.016936 | -0.071132 | 0.13416 | -0.059159 | -0.15216 | 0.039079 | 0.10105 | -0.038063 | 0.005985 | 122.7522 | 122.6172 | 122.719 | 122.6602 | 122.781 | 122.7525 | 122.6637 | -0.071132 | 0.13416 | -0.059159 | -0.15216 | 0.039079 | 0.10105 | -0.038063 | 0.005985 | -0.11021 | -0.033069 | -0.098238 | -0.021096
2384.5781 | 122.9507 | -122.6669 | 0.20142 | 0.071489 | -0.063415 | 0.029208 | -0.020438 | 0.10493 | 0.067269 | -0.021514 | -0.043661 | 0.1479 | -0.036267 | -0.13842 | 0.034501 | 0.10105 | -0.042641 | 0.010563 | 122.7384 | 122.6035 | 122.6961 | 122.6465 | 122.7719 | 122.7342 | 122.6454 | -0.043661 | 0.1479 | -0.036267 | -0.13842 | 0.034501 | 0.10105 | -0.042641 | 0.010563 | -0.078162 | -0.00102 | -0.070768 | 0.006374
2386.3438 | 122.8683 | -122.7081 | 0.2243 | 0.071489 | -0.058836 | 0.024629 | -0.029595 | 0.10951 | 0.076426 | -0.026092 | -0.07571 | 0.13416 | -0.05458 | -0.143 | 0.039079 | 0.091891 | -0.042641 | 0.005985 | 122.7796 | 122.6493 | 122.7328 | 122.6785 | 122.8176 | 122.7846 | 122.682 | -0.07571 | 0.13416 | -0.05458 | -0.143 | 0.039079 | 0.091891 | -0.042641 | 0.005985 | -0.11479 | -0.033069 | -0.093659 | -0.011939
2388.0312 | 122.9187 | -122.6852 | 0.21515 | 0.071489 | -0.058836 | 0.029208 | -0.025017 | 0.10493 | 0.076426 | -0.021514 | 0.01586 | 0.16622 | -0.008798 | -0.14758 | 0.048236 | 0.096469 | -0.042641 | 0.005985 | 122.7567 | 122.6264 | 122.7144 | 122.6602 | 122.7902 | 122.7617 | 122.6637 | 0.01586 | 0.16622 | -0.008798 | -0.14758 | 0.048236 | 0.096469 | -0.042641 | 0.005985 | -0.032376 | 0.058501 | -0.057034 | 0.033843
2389.7812 | 123.0331 | -122.6761 | 0.18768 | 0.080646 | -0.054257 | 0.024629 | -0.01586 | 0.10951 | 0.067269 | -0.026092 | -0.061975 | 0.14332 | -0.05458 | -0.13842 | 0.043657 | 0.096469 | -0.042641 | 0.015141 | 122.7567 | 122.6218 | 122.7007 | 122.6602 | 122.7856 | 122.7434 | 122.65 | -0.061975 | 0.14332 | -0.05458 | -0.13842 | 0.043657 | 0.096469 | -0.042641 | 0.015141 | -0.10563 | -0.019334 | -0.098237 | -0.011939
2391.5312 | 122.9691 | -122.6715 | 0.21057 | 0.076067 | -0.054257 | 0.024629 | -0.029595 | 0.10951 | 0.067269 | -0.021514 | -0.043661 | 0.15248 | -0.027111 | -0.143 | 0.043657 | 0.096469 | -0.04722 | 0.001406 | 122.7476 | 122.6173 | 122.6961 | 122.6419 | 122.781 | 122.7388 | 122.65 | -0.043661 | 0.15248 | -0.027111 | -0.143 | 0.043657 | 0.096469 | -0.04722 | 0.001406 | -0.087318 | 0.003559 | -0.070768 | 0.020109
2393.2812 | 122.9324 | -122.6852 | 0.23804 | 0.071489 | -0.067994 | 0.024629 | -0.01586 | 0.10493 | 0.067269 | -0.021514 | -0.025347 | 0.13416 | -0.036267 | -0.143 | 0.034501 | 0.091891 | -0.04722 | 0.005985 | 122.7567 | 122.6172 | 122.7099 | 122.6694 | 122.7902 | 122.7525 | 122.6637 | -0.025347 | 0.13416 | -0.036267 | -0.143 | 0.034501 | 0.091891 | -0.04722 | 0.005985 | -0.059848 | 0.021873 | -0.070768 | 0.010953
2395.0312 | 122.9645 | -122.7081 | 0.21057 | 0.071489 | -0.054257 | 0.029208 | -0.025017 | 0.10036 | 0.067269 | -0.03067 | 0.029595 | 0.17537 | -0.027111 | -0.14758 | 0.039079 | 0.096469 | -0.042641 | 0.005985 | 122.7796 | 122.6539 | 122.7373 | 122.6831 | 122.8085 | 122.7754 | 122.6775 | 0.029595 | 0.17537 | -0.027111 | -0.14758 | 0.039079 | 0.096469 | -0.042641 | 0.005985 | -0.009484 | 0.072236 | -0.06619 | 0.01553
2396.7188 | 122.8958 | -122.731 | 0.23804 | 0.080646 | -0.054257 | 0.024629 | -0.020438 | 0.10493 | 0.067269 | -0.021514 | -0.007033 | 0.15248 | -0.045424 | -0.143 | 0.043657 | 0.10105 | -0.042641 | 0.005985 | 122.8117 | 122.6768 | 122.7556 | 122.7106 | 122.836 | 122.7983 | 122.7095 | -0.007033 | 0.15248 | -0.045424 | -0.143 | 0.043657 | 0.10105 | -0.042641 | 0.005985 | -0.05069 | 0.035608 | -0.089081 | -0.002783
2398.4844 | 122.9645 | -122.6578 | 0.22888 | 0.080646 | -0.054257 | 0.029208 | -0.020438 | 0.10951 | 0.071848 | -0.016936 | 0.070802 | 0.18453 | -0.008798 | -0.14758 | 0.043657 | 0.096469 | -0.042641 | 0.001406 | 122.7384 | 122.6035 | 122.687 | 122.6373 | 122.7673 | 122.7296 | 122.6408 | 0.070802 | 0.18453 | -0.008798 | -0.14758 | 0.043657 | 0.096469 | -0.042641 | 0.001406 | 0.027145 | 0.11344 | -0.052455 | 0.033843
2400.2344 | 123.0103 | -122.6486 | 0.19684 | 0.076067 | -0.063415 | 0.024629 | -0.020438 | 0.095778 | 0.071848 | -0.03067 | 0.020438 | 0.17537 | 0.004937 | -0.13842 | 0.043657 | 0.091891 | -0.042641 | -0.003172 | 122.7247 | 122.5852 | 122.6733 | 122.6282 | 122.7444 | 122.7205 | 122.618 | 0.020438 | 0.17537 | 0.004937 | -0.13842 | 0.043657 | 0.091891 | -0.042641 | -0.003172 | -0.023219 | 0.063079 | -0.03872 | 0.047578
2401.9844 | 122.9553 | -122.7036 | 0.2243 | 0.076067 | -0.058836 | 0.033786 | -0.020438 | 0.10493 | 0.081005 | -0.021514 | 0.020438 | 0.17995 | -0.036267 | -0.14758 | 0.043657 | 0.091891 | -0.042641 | 0.015141 | 122.7796 | 122.6447 | 122.7373 | 122.6831 | 122.8085 | 122.7846 | 122.682 | 0.020438 | 0.17995 | -0.036267 | -0.14758 | 0.043657 | 0.091891 | -0.042641 | 0.015141 | -0.023219 | 0.063079 | -0.079924 | 0.006374
2403.6875 | 122.9279 | -122.7264 | 0.21973 | 0.071489 | -0.054257 | 0.029208 | -0.01586 | 0.10493 | 0.081005 | -0.026092 | 0.025017 | 0.16164 | -0.059159 | -0.143 | 0.034501 | 0.10105 | -0.042641 | 0.005985 | 122.7979 | 122.6722 | 122.7556 | 122.7106 | 122.8314 | 122.8074 | 122.7003 | 0.025017 | 0.16164 | -0.059159 | -0.143 | 0.034501 | 0.10105 | -0.042641 | 0.005985 | -0.009484 | 0.067658 | -0.09366 | -0.016518
2405.4375 | 123.0057 | -122.6852 | 0.19226 | 0.071489 | -0.054257 | 0.029208 | -0.029595 | 0.10493 | 0.076426 | -0.026092 | -0.011611 | 0.15706 | -0.008798 | -0.14758 | 0.043657 | 0.091891 | -0.033484 | 0.001406 | 122.7567 | 122.631 | 122.7144 | 122.6556 | 122.7902 | 122.7617 | 122.6591 | -0.011611 | 0.15706 | -0.008798 | -0.14758 | 0.043657 | 0.091891 | -0.033484 | 0.001406 | -0.055268 | 0.021873 | -0.052455 | 0.024686
2407.125 | 123.0286 | -122.6944 | 0.19226 | 0.076067 | -0.049678 | 0.024629 | -0.025017 | 0.10036 | 0.067269 | -0.021514 | -0.061975 | 0.1479 | -0.05458 | -0.14758 | 0.039079 | 0.096469 | -0.038063 | 0.001406 | 122.7705 | 122.6447 | 122.719 | 122.6694 | 122.7948 | 122.7617 | 122.6729 | -0.061975 | 0.1479 | -0.05458 | -0.14758 | 0.039079 | 0.096469 | -0.038063 | 0.001406 | -0.10105 | -0.023912 | -0.093659 | -0.016517
2408.875 | 122.9416 | -122.7081 | 0.23346 | 0.076067 | -0.058836 | 0.029208 | -0.020438 | 0.11409 | 0.071848 | -0.021514 | -0.011611 | 0.18911 | -0.013376 | -0.13842 | 0.039079 | 0.10105 | -0.042641 | 0.005985 | 122.7842 | 122.6493 | 122.7373 | 122.6877 | 122.8222 | 122.78 | 122.6866 | -0.011611 | 0.18911 | -0.013376 | -0.13842 | 0.039079 | 0.10105 | -0.042641 | 0.005985 | -0.05069 | 0.03103 | -0.052455 | 0.029265
2410.5625 | 122.9187 | -122.731 | 0.23346 | 0.076067 | -0.054257 | 0.029208 | -0.020438 | 0.10036 | 0.076426 | -0.021514 | 0.002124 | 0.16622 | -0.027111 | -0.143 | 0.039079 | 0.091891 | -0.042641 | 0.015141 | 122.8071 | 122.6768 | 122.7602 | 122.7106 | 122.8314 | 122.8074 | 122.7095 | 0.002124 | 0.16622 | -0.027111 | -0.143 | 0.039079 | 0.091891 | -0.042641 | 0.015141 | -0.036955 | 0.044765 | -0.06619 | 0.01553
2412.2969 | 122.8867 | -122.7173 | 0.21515 | 0.076067 | -0.058836 | 0.024629 | -0.025017 | 0.10951 | 0.071848 | -0.016936 | 0.052488 | 0.17995 | -0.013376 | -0.143 | 0.043657 | 0.096469 | -0.056376 | -0.003172 | 122.7934 | 122.6584 | 122.7419 | 122.6923 | 122.8268 | 122.7891 | 122.7003 | 0.052488 | 0.17995 | -0.013376 | -0.143 | 0.043657 | 0.096469 | -0.056376 | -0.003172 | 0.008831 | 0.10886 | -0.057033 | 0.043
2414.0469 | 122.9416 | -122.7173 | 0.22888 | 0.06691 | -0.049678 | 0.029208 | -0.029595 | 0.10951 | 0.071848 | -0.021514 | -0.025347 | 0.14332 | -0.017954 | -0.14758 | 0.043657 | 0.096469 | -0.033484 | 0.010563 | 122.7842 | 122.6676 | 122.7465 | 122.6877 | 122.8268 | 122.7891 | 122.6958 | -0.025347 | 0.14332 | -0.017954 | -0.14758 | 0.043657 | 0.096469 | -0.033484 | 0.010563 | -0.069004 | 0.008137 | -0.061611 | 0.01553
2415.7344 | 122.9279 | -122.7127 | 0.21973 | 0.071489 | -0.054257 | 0.029208 | -0.020438 | 0.0912 | 0.076426 | -0.026092 | -0.039082 | 0.15248 | -0.027111 | -0.143 | 0.034501 | 0.096469 | -0.042641 | 0.005985 | 122.7842 | 122.6585 | 122.7419 | 122.6923 | 122.8039 | 122.7891 | 122.6866 | -0.039082 | 0.15248 | -0.027111 | -0.143 | 0.034501 | 0.096469 | -0.042641 | 0.005985 | -0.073583 | 0.003559 | -0.061612 | 0.01553
2417.4844 | 123.0057 | -122.7036 | 0.21057 | 0.076067 | -0.058836 | 0.024629 | -0.025017 | 0.10951 | 0.071848 | -0.016936 | -0.007033 | 0.15706 | -0.050002 | -0.143 | 0.043657 | 0.091891 | -0.042641 | 0.005985 | 122.7796 | 122.6447 | 122.7282 | 122.6785 | 122.8131 | 122.7754 | 122.6866 | -0.007033 | 0.15706 | -0.050002 | -0.143 | 0.043657 | 0.091891 | -0.042641 | 0.005985 | -0.05069 | 0.035608 | -0.093659 | -0.007361
2419.2656 | 123.0103 | -122.7036 | 0.20599 | 0.062332 | -0.063415 | 0.024629 | -0.020438 | 0.10036 | 0.081005 | -0.021514 | -0.01619 | 0.15248 | -0.017954 | -0.143 | 0.039079 | 0.096469 | -0.042641 | 0.010563 | 122.7659 | 122.6401 | 122.7282 | 122.6831 | 122.8039 | 122.7846 | 122.682 | -0.01619 | 0.15248 | -0.017954 | -0.143 | 0.039079 | 0.096469 | -0.042641 | 0.010563 | -0.055269 | 0.026451 | -0.057033 | 0.024687
2420.9531 | 123.0469 | -122.6944 | 0.19226 | 0.080646 | -0.058836 | 0.033786 | -0.025017 | 0.10493 | 0.081005 | -0.026092 | -0.020768 | 0.16622 | -0.040846 | -0.143 | 0.034501 | 0.10105 | -0.042641 | 0.001406 | 122.775 | 122.6356 | 122.7282 | 122.6694 | 122.7993 | 122.7754 | 122.6683 | -0.020768 | 0.16622 | -0.040846 | -0.143 | 0.034501 | 0.10105 | -0.042641 | 0.001406 | -0.055269 | 0.021873 | -0.075347 | 0.001795
2422.7031 | 123.0377 | -122.7036 | 0.21515 | 0.06691 | -0.054257 | 0.033786 | -0.029595 | 0.10493 | 0.071848 | -0.021514 | 0.020438 | 0.17079 | -0.022532 | -0.143 | 0.043657 | 0.087313 | -0.04722 | -0.003172 | 122.7705 | 122.6493 | 122.7373 | 122.674 | 122.8085 | 122.7754 | 122.682 | 0.020438 | 0.17079 | -0.022532 | -0.143 | 0.043657 | 0.087313 | -0.04722 | -0.003172 | -0.023219 | 0.067658 | -0.066189 | 0.024688
2424.4062 | 122.9599 | -122.7173 | 0.21057 | 0.071489 | -0.054257 | 0.024629 | -0.025017 | 0.10493 | 0.076426 | -0.021514 | 0.034174 | 0.17995 | 0.02325 | -0.143 | 0.043657 | 0.10105 | -0.038063 | -0.00775 | 122.7888 | 122.663 | 122.7419 | 122.6923 | 122.8222 | 122.7937 | 122.6958 | 0.034174 | 0.17995 | 0.02325 | -0.143 | 0.043657 | 0.10105 | -0.038063 | -0.00775 | -0.009483 | 0.072237 | -0.020407 | 0.061313
2426.1719 | 122.937 | -122.7493 | 0.2243 | 0.076067 | -0.0451 | 0.024629 | -0.020438 | 0.10951 | 0.081005 | -0.03067 | 0.025017 | 0.16164 | 0.014094 | -0.143 | 0.043657 | 0.10105 | -0.038063 | 0.001406 | 122.8254 | 122.7042 | 122.774 | 122.7289 | 122.8588 | 122.8303 | 122.7187 | 0.025017 | 0.16164 | 0.014094 | -0.143 | 0.043657 | 0.10105 | -0.038063 | 0.001406 | -0.01864 | 0.06308 | -0.029563 | 0.052157
2427.875 | 122.9645 | -122.7448 | 0.2243 | 0.06691 | -0.054257 | 0.033786 | -0.025017 | 0.10951 | 0.071848 | -0.016936 | 0.006703 | 0.17079 | -0.027111 | -0.143 | 0.039079 | 0.10105 | -0.04722 | 0.001406 | 122.8117 | 122.6905 | 122.7785 | 122.7197 | 122.8543 | 122.8166 | 122.7278 | 0.006703 | 0.17079 | -0.027111 | -0.143 | 0.039079 | 0.10105 | -0.04722 | 0.001406 | -0.032376 | 0.053923 | -0.06619 | 0.020109
2429.6406 | 122.9782 | -122.7264 | 0.23346 | 0.076067 | -0.049678 | 0.033786 | -0.020438 | 0.10951 | 0.076426 | -0.021514 | -0.029925 | 0.14332 | -0.063737 | -0.14758 | 0.043657 | 0.091891 | -0.038063 | 0.001406 | 122.8025 | 122.6768 | 122.7602 | 122.706 | 122.836 | 122.8029 | 122.7049 | -0.029925 | 0.14332 | -0.063737 | -0.14758 | 0.043657 | 0.091891 | -0.038063 | 0.001406 | -0.073582 | 0.008138 | -0.10739 | -0.025674
2431.4062 | 123.0057 | -122.7173 | 0.20142 | 0.062332 | -0.058836 | 0.033786 | -0.020438 | 0.095778 | 0.071848 | -0.021514 | 0.006703 | 0.15706 | -0.050002 | -0.13842 | 0.043657 | 0.096469 | -0.042641 | -0.003172 | 122.7796 | 122.6584 | 122.7511 | 122.6968 | 122.8131 | 122.7891 | 122.6958 | 0.006703 | 0.15706 | -0.050002 | -0.13842 | 0.043657 | 0.096469 | -0.042641 | -0.003172 | -0.036954 | 0.049344 | -0.093659 | -0.007361
2433.1562 | 122.9874 | -122.7264 | 0.20599 | 0.071489 | -0.054257 | 0.033786 | -0.01586 | 0.10036 | 0.081005 | -0.021514 | -0.052818 | 0.18453 | -0.050002 | -0.143 | 0.039079 | 0.091891 | -0.038063 | 0.010563 | 122.7979 | 122.6722 | 122.7602 | 122.7106 | 122.8268 | 122.8074 | 122.7049 | -0.052818 | 0.18453 | -0.050002 | -0.143 | 0.039079 | 0.091891 | -0.038063 | 0.010563 | -0.091897 | -0.014755 | -0.089081 | -0.011939
2434.8594 | 122.9691 | -122.7402 | 0.2243 | 0.06691 | -0.054257 | 0.038365 | -0.025017 | 0.10493 | 0.081005 | -0.021514 | -0.043661 | 0.17079 | -0.050002 | -0.143 | 0.034501 | 0.096469 | -0.051798 | -0.003172 | 122.8071 | 122.6859 | 122.7785 | 122.7152 | 122.8451 | 122.8212 | 122.7187 | -0.043661 | 0.17079 | -0.050002 | -0.143 | 0.034501 | 0.096469 | -0.051798 | -0.003172 | -0.078162 | 0.008137 | -0.084503 | 0.001796
2436.625 | 122.9324 | -122.7493 | 0.22888 | 0.076067 | -0.054257 | 0.029208 | -0.025017 | 0.10493 | 0.076426 | -0.021514 | -0.029925 | 0.14332 | -0.045424 | -0.13842 | 0.043657 | 0.10105 | -0.04722 | 0.010563 | 122.8254 | 122.6951 | 122.7785 | 122.7243 | 122.8543 | 122.8258 | 122.7278 | -0.029925 | 0.14332 | -0.045424 | -0.13842 | 0.043657 | 0.10105 | -0.04722 | 0.010563 | -0.073582 | 0.017295 | -0.089081 | 0.001796
2438.3125 | 122.9736 | -122.7631 | 0.23804 | 0.071489 | -0.063415 | 0.029208 | -0.020438 | 0.10493 | 0.071848 | -0.016936 | -0.011611 | 0.16164 | -0.027111 | -0.14758 | 0.043657 | 0.091891 | -0.04722 | 0.005985 | 122.8346 | 122.6996 | 122.7923 | 122.7426 | 122.868 | 122.8349 | 122.7461 | -0.011611 | 0.16164 | -0.027111 | -0.14758 | 0.043657 | 0.091891 | -0.04722 | 0.005985 | -0.055268 | 0.035609 | -0.070768 | 0.020109
2440.0625 | 122.937 | -122.7493 | 0.23804 | 0.06691 | -0.054257 | 0.033786 | -0.025017 | 0.10951 | 0.071848 | -0.03067 | -0.020768 | 0.18453 | -0.013376 | -0.143 | 0.043657 | 0.096469 | -0.042641 | 0.010563 | 122.8162 | 122.6951 | 122.7831 | 122.7243 | 122.8588 | 122.8212 | 122.7187 | -0.020768 | 0.18453 | -0.013376 | -0.143 | 0.043657 | 0.096469 | -0.042641 | 0.010563 | -0.064425 | 0.021873 | -0.057033 | 0.029265
2441.8125 | 123.0194 | -122.7036 | 0.21057 | 0.062332 | -0.058836 | 0.029208 | -0.020438 | 0.10036 | 0.076426 | -0.03067 | 0.011281 | 0.18453 | -0.017954 | -0.143 | 0.043657 | 0.10105 | -0.04722 | 0.001406 | 122.7659 | 122.6447 | 122.7328 | 122.6831 | 122.8039 | 122.78 | 122.6729 | 0.011281 | 0.18453 | -0.017954 | -0.143 | 0.043657 | 0.10105 | -0.04722 | 0.001406 | -0.032376 | 0.058501 | -0.061611 | 0.029266
2443.5156 | 123.0011 | -122.731 | 0.20599 | 0.071489 | -0.058836 | 0.033786 | -0.025017 | 0.10493 | 0.076426 | -0.021514 | 0.057066 | 0.18911 | 0.032407 | -0.13384 | 0.039079 | 0.10105 | -0.042641 | 0.005985 | 122.8025 | 122.6722 | 122.7648 | 122.706 | 122.836 | 122.8074 | 122.7095 | 0.057066 | 0.18911 | 0.032407 | -0.13384 | 0.039079 | 0.10105 | -0.042641 | 0.005985 | 0.017987 | 0.099707 | -0.006672 | 0.075048
2445.2812 | 123.0743 | -122.7081 | 0.18768 | 0.071489 | -0.058836 | 0.033786 | -0.025017 | 0.10493 | 0.071848 | -0.026092 | 0.057066 | 0.18453 | 0.032407 | -0.13842 | 0.039079 | 0.096469 | -0.038063 | 0.005985 | 122.7796 | 122.6493 | 122.7419 | 122.6831 | 122.8131 | 122.78 | 122.682 | 0.057066 | 0.18453 | 0.032407 | -0.13842 | 0.039079 | 0.096469 | -0.038063 | 0.005985 | 0.017987 | 0.095129 | -0.006672 | 0.07047
2447.0469 | 123.024 | -122.7264 | 0.20599 | 0.076067 | -0.054257 | 0.029208 | -0.025017 | 0.10036 | 0.067269 | -0.026092 | -0.002454 | 0.16622 | -0.045424 | -0.14758 | 0.034501 | 0.091891 | -0.042641 | -0.003172 | 122.8025 | 122.6722 | 122.7556 | 122.7014 | 122.8268 | 122.7937 | 122.7003 | -0.002454 | 0.16622 | -0.045424 | -0.14758 | 0.034501 | 0.091891 | -0.042641 | -0.003172 | -0.036955 | 0.040187 | -0.079925 | -0.002783
2448.75 | 123.0469 | -122.7219 | 0.19226 | 0.06691 | -0.063415 | 0.024629 | -0.025017 | 0.10951 | 0.071848 | -0.021514 | -0.011611 | 0.16164 | -0.063737 | -0.143 | 0.039079 | 0.096469 | -0.038063 | 0.005985 | 122.7888 | 122.6584 | 122.7465 | 122.6968 | 122.8314 | 122.7937 | 122.7003 | -0.011611 | 0.16164 | -0.063737 | -0.143 | 0.039079 | 0.096469 | -0.038063 | 0.005985 | -0.05069 | 0.026452 | -0.10282 | -0.025674
2450.5 | 122.9462 | -122.7539 | 0.2243 | 0.06691 | -0.054257 | 0.024629 | -0.025017 | 0.10036 | 0.076426 | -0.026092 | -0.089445 | 0.1479 | -0.063737 | -0.143 | 0.043657 | 0.10562 | -0.04722 | -0.003172 | 122.8208 | 122.6996 | 122.7785 | 122.7289 | 122.8543 | 122.8303 | 122.7278 | -0.089445 | 0.1479 | -0.063737 | -0.143 | 0.043657 | 0.10562 | -0.04722 | -0.003172 | -0.1331 | -0.042225 | -0.10739 | -0.016517
2452.25 | 122.9599 | -122.7631 | 0.21515 | 0.071489 | -0.058836 | 0.024629 | -0.020438 | 0.10036 | 0.081005 | -0.026092 | 0.002124 | 0.17537 | 0.004937 | -0.13842 | 0.039079 | 0.096469 | -0.038063 | 0.001406 | 122.8346 | 122.7042 | 122.7877 | 122.7426 | 122.8634 | 122.8441 | 122.737 | 0.002124 | 0.17537 | 0.004937 | -0.13842 | 0.039079 | 0.096469 | -0.038063 | 0.001406 | -0.036955 | 0.040187 | -0.034142 | 0.043
2454.0156 | 123.0148 | -122.7219 | 0.20142 | 0.076067 | -0.058836 | 0.024629 | -0.01586 | 0.10951 | 0.067269 | -0.021514 | -0.011611 | 0.19827 | -0.050002 | -0.13842 | 0.048236 | 0.091891 | -0.042641 | 0.010563 | 122.7979 | 122.663 | 122.7465 | 122.706 | 122.8314 | 122.7891 | 122.7003 | -0.011611 | 0.19827 | -0.050002 | -0.13842 | 0.048236 | 0.091891 | -0.042641 | 0.010563 | -0.059847 | 0.03103 | -0.098238 | -0.007361
2455.7031 | 123.0148 | -122.731 | 0.19684 | 0.076067 | -0.054257 | 0.029208 | -0.025017 | 0.10036 | 0.067269 | -0.026092 | -0.020768 | 0.14332 | -0.027111 | -0.143 | 0.039079 | 0.096469 | -0.038063 | 0.010563 | 122.8071 | 122.6768 | 122.7602 | 122.706 | 122.8314 | 122.7983 | 122.7049 | -0.020768 | 0.14332 | -0.027111 | -0.143 | 0.039079 | 0.096469 | -0.038063 | 0.010563 | -0.059847 | 0.017295 | -0.06619 | 0.010952
2457.4531 | 122.9462 | -122.7768 | 0.21973 | 0.06691 | -0.058836 | 0.029208 | -0.029595 | 0.095778 | 0.076426 | -0.016936 | 0.020438 | 0.18453 | -0.031689 | -0.13842 | 0.043657 | 0.091891 | -0.038063 | 0.001406 | 122.8437 | 122.718 | 122.806 | 122.7472 | 122.8726 | 122.8532 | 122.7599 | 0.020438 | 0.18453 | -0.031689 | -0.13842 | 0.043657 | 0.091891 | -0.038063 | 0.001406 | -0.023219 | 0.058501 | -0.075346 | 0.006374
2459.2344 | 122.9782 | -122.7676 | 0.22888 | 0.06691 | -0.058836 | 0.033786 | -0.020438 | 0.10493 | 0.071848 | -0.016936 | 0.043331 | 0.16622 | 0.000359 | -0.143 | 0.043657 | 0.096469 | -0.042641 | 0.010563 | 122.8345 | 122.7088 | 122.8014 | 122.7472 | 122.8726 | 122.8395 | 122.7507 | 0.043331 | 0.16622 | 0.000359 | -0.143 | 0.043657 | 0.096469 | -0.042641 | 0.010563 | -0.000326 | 0.085972 | -0.043298 | 0.043
2460.9219 | 123.0377 | -122.7493 | 0.20599 | 0.071489 | -0.054257 | 0.029208 | -0.020438 | 0.11409 | 0.071848 | -0.016936 | 0.07538 | 0.17995 | 0.004937 | -0.14758 | 0.034501 | 0.096469 | -0.042641 | 0.001406 | 122.8208 | 122.6951 | 122.7785 | 122.7289 | 122.8634 | 122.8212 | 122.7324 | 0.07538 | 0.17995 | 0.004937 | -0.14758 | 0.034501 | 0.096469 | -0.042641 | 0.001406 | 0.040879 | 0.11802 | -0.029564 | 0.047578

## Thermal Data
Fire Time | D Position - 3' | D Position - Middle | D Position - 7'
-0.5271 | 12.2143 | 19.2004 | 12.1365
0.4729 | 12.214 | 19.1949 | 12.1359
1.4729 | 12.2146 | 19.252 | 12.1428
2.4729 | 12.2117 | 19.2798 | 12.1494
3.4729 | 12.2062 | 19.194 | 12.1584
4.4729 | 12.1978 | 19.2109 | 12.1462
5.4729 | 12.1969 | 19.0793 | 12.1539
6.4729 | 12.1981 | 18.4197 | 12.1563
7.4729 | 12.1965 | 18.6002 | 12.1533
8.4729 | 12.2026 | 18.717 | 12.1782
9.4729 | 12.3381 | 19.0679 | 12.2021
10.4729 | 12.9017 | 19.4919 | 12.2501
11.4729 | 14.4795 | 20.1481 | 13.2389
12.4729 | 15.8102 | 26.6282 | 14.6141
13.4729 | 17.8764 | 26.636 | 15.5939
14.4729 | 19.1435 | 26.6311 | 17.1506
15.4729 | 21.312 | 26.6396 | 19.0908
16.4729 | 23.7804 | 26.6295 | 21.0628
17.4729 | 26.6407 | 26.6306 | 23.7529
18.4729 | 29.9269 | 26.6406 | 26.031
19.4729 | 32.6571 | 26.6396 | 28.5816
20.4885 | 36.2346 | 26.6286 | 31.1881
21.4885 | 39.8603 | 26.6252 | 33.5573
22.4729 | 43.2094 | 26.6213 | 34.8484
23.4729 | 46.9073 | 26.6327 | 37.312
24.4729 | 51.6102 | 26.6371 | 39.1942
25.4729 | 53.9723 | 26.6382 | 41.2622
26.4729 | 56.5424 | 26.626 | 43.3183
27.4729 | 60.0341 | 26.6318 | 48.6254
28.4729 | 63.6365 | 26.6248 | 52.9108
29.4729 | 67.8648 | 26.6246 | 54.8723
30.4729 | 71.5059 | 26.6227 | 57.6919
31.4729 | 72.921 | 26.6251 | 60.3741
32.4729 | 76.1789 | 26.6263 | 63.2747
33.4729 | 79.5284 | 26.6147 | 64.9028
34.4729 | 82.0347 | 26.6224 | 67.1626
35.4729 | 83.0935 | 26.613 | 71.3917
36.4729 | 85.5026 | 26.6189 | 74.3925
37.4729 | 89.5076 | 26.6122 | 76.839
38.4729 | 92.0365 | 26.6105 | 79.8075
39.4729 | 94.2974 | 26.6125 | 82.0067
40.4729 | 96.1381 | 26.5997 | 82.8611
41.4729 | 98.0343 | 26.6097 | 84.9393
42.4729 | 100.3269 | 26.6031 | 86.1662
43.4729 | 101.5692 | 26.6015 | 86.9473
44.4729 | 103.7087 | 26.6101 | 88.0805
45.4729 | 104.8172 | 26.6012 | 89.9352
46.4729 | 106.0986 | 26.6076 | 91.6337
47.4729 | 108.2411 | 26.6045 | 93.6968
48.4729 | 109.684 | 26.6007 | 94.7687
49.4729 | 109.6045 | 26.6057 | 95.35
50.4729 | 109.5786 | 26.6102 | 96.1565
51.4729 | 109.2767 | 26.6057 | 96.7397
52.4729 | 109.5933 | 26.597 | 97.391
53.4729 | 111.2125 | 26.5967 | 98.0841
54.4729 | 112.2374 | 26.5937 | 98.7337
55.4729 | 114.0459 | 26.5964 | 99.0513
56.4729 | 114.9986 | 26.5935 | 99.8204
57.4729 | 116.427 | 26.5949 | 101.1676
58.4729 | 117.6603 | 26.5834 | 102.3406
59.4729 | 119.0235 | 26.5868 | 104.0032
60.4729 | 120.4574 | 26.5912 | 105.8146
61.4729 | 122.5428 | 26.5921 | 107.5429
62.4729 | 124.1986 | 26.5914 | 109.311
63.4729 | 125.1111 | 26.583 | 110.1317
64.4729 | 125.884 | 26.5844 | 110.9589
65.4729 | 126.8163 | 26.5879 | 111.6843
66.4729 | 127.4571 | 26.5811 | 112.0601
67.4729 | 127.6747 | 26.5802 | 112.4996
68.4729 | 127.7608 | 26.5759 | 112.7835
69.4729 | 128.4394 | 26.5684 | 113.1549
70.4729 | 129.9965 | 26.579 | 113.896
71.4729 | 131.4492 | 26.575 | 114.532
72.4729 | 133.4236 | 26.5763 | 115.2722
73.4729 | 135.0761 | 26.5757 | 116.1114
74.4729 | 136.7037 | 26.5743 | 117.6642
75.4729 | 137.6071 | 26.5701 | 119.2099
76.4729 | 137.1905 | 26.576 | 119.4736
77.4729 | 136.5149 | 26.571 | 119.3654
78.4729 | 136.5158 | 26.5638 | 119.5714
79.4729 | 138.7719 | 26.5641 | 119.9279
80.4729 | 140.0204 | 26.5686 | 121.2974
81.4729 | 141.2641 | 26.567 | 122.4791
82.4729 | 143.1136 | 26.5639 | 125.0462
83.4729 | 143.5943 | 26.5716 | 126.5817
84.4729 | 143.8615 | 26.5686 | 126.6618
85.4729 | 144.5333 | 26.5649 | 127.0493
86.4729 | 145.0399 | 26.5593 | 127.011
87.4729 | 144.656 | 26.558 | 126.8158
88.4729 | 144.4948 | 26.5573 | 126.6251
89.4729 | 144.3163 | 26.5534 | 126.3567
90.4729 | 143.8293 | 26.5548 | 125.8225
91.4729 | 144.1945 | 26.5644 | 125.7376
92.4729 | 144.0315 | 26.5533 | 125.9941
93.4729 | 144.9639 | 26.5485 | 126.1213
94.4729 | 144.7606 | 26.5477 | 126.4352
95.4729 | 144.9728 | 26.5449 | 127.0233
96.4729 | 145.6781 | 26.5646 | 127.5374
97.4729 | 146.1054 | 26.5519 | 127.5045
98.4729 | 146.7459 | 26.5605 | 127.7435
99.4729 | 146.9644 | 26.5507 | 127.7028
100.4729 | 146.6557 | 26.5434 | 128.0191
101.4729 | 147.2056 | 26.5411 | 128.2939
102.4729 | 147.935 | 26.5477 | 129.3756
103.4729 | 149.3021 | 26.5385 | 130.2208
104.4729 | 150.3956 | 26.5406 | 130.5668
105.4729 | 150.8749 | 26.5476 | 130.8005
106.4729 | 153.0081 | 26.5433 | 131.3882
107.4729 | 154.7291 | 26.5345 | 132.4044
108.4729 | 155.2468 | 26.5295 | 132.4522
109.4729 | 155.0914 | 26.5376 | 132.5787
110.4885 | 155.6314 | 26.529 | 133.5937
111.4729 | 155.5889 | 26.5361 | 133.527
112.4729 | 155.6653 | 26.5377 | 132.9647
113.4729 | 155.552 | 26.5463 | 133.2031
114.4729 | 155.0749 | 26.5406 | 133.043
115.4729 | 155.5942 | 26.5492 | 133.7945
116.4729 | 156.2879 | 26.5465 | 134.6731
117.4729 | 155.6868 | 26.5409 | 134.7231
118.4729 | 157.1595 | 26.5613 | 135.86
119.4729 | 158.6414 | 26.5695 | 135.1114
120.4729 | 158.052 | 26.5735 | 135.2287
121.4729 | 158.3111 | 26.602 | 134.8331
122.4729 | 158.4896 | 26.617 | 134.4629
123.4729 | 158.1366 | 26.6176 | 134.1826
124.4729 | 157.8809 | 26.6203 | 133.8811
125.4729 | 157.7562 | 26.6411 | 134.0236
126.4729 | 157.7376 | 26.6774 | 134.3244
127.4729 | 158.1093 | 26.637 | 134.8153
128.4729 | 158.3174 | 26.6922 | 135.3198
129.4729 | 158.4169 | 26.715 | 135.4625
130.4729 | 158.3582 | 26.7268 | 135.8434
131.4729 | 158.0257 | 26.6868 | 135.6665
132.4729 | 157.8555 | 26.7891 | 135.5784
133.4729 | 159.2987 | 26.7829 | 135.6683
134.4729 | 158.9747 | 26.9633 | 135.3261
135.4729 | 160.0973 | 26.9591 | 135.4513
136.4729 | 160.4533 | 27 | 135.8429
137.4729 | 159.7053 | 27.1229 | 135.3103
138.4729 | 160.4362 | 27.1163 | 135.1937
139.4729 | 161.4454 | 27.4395 | 136.8028
140.4729 | 162.5078 | 27.3085 | 137.6246
141.4729 | 162.9215 | 27.4606 | 138.2059
142.4729 | 162.5408 | 27.4586 | 138.3896
143.4729 | 163.4533 | 27.7251 | 138.7786
144.4729 | 163.1653 | 27.7817 | 138.9512
145.4729 | 163.3727 | 27.9258 | 139.2547
146.4729 | 163.8525 | 28.0851 | 140.1616
147.4729 | 163.8082 | 28.058 | 139.6511
148.4729 | 163.7857 | 28.4294 | 140.0633
149.4729 | 163.3299 | 28.774 | 140.1079
150.4729 | 164.322 | 28.7209 | 140.5825
151.4729 | 164.614 | 29.109 | 141.8446
152.4729 | 163.6268 | 29.0466 | 141.8273
153.4729 | 164.483 | 29.3101 | 142.2091
154.4729 | 165.7841 | 34.9924 | 142.7126
155.4729 | 165.9646 | 35.6275 | 142.6761
156.4729 | 165.4221 | 36.2657 | 143.0255
157.4729 | 166.4177 | 36.7586 | 143.2185
158.4729 | 167.5335 | 37.8418 | 143.3577
159.4729 | 168.1624 | 43.2148 | 143.4002
160.4729 | 168.3163 | 44.0481 | 143.9368
161.4729 | 169.3761 | 47.3061 | 145.1978
162.4729 | 171.2733 | 37.7475 | 145.4642
163.4729 | 171.5337 | 43.5095 | 145.8083
164.4729 | 172.9616 | 44.2366 | 146.0306
165.4729 | 173.5183 | 50.388 | 146.0124
166.4729 | 174.7554 | 103.2963 | 146.5779
167.4729 | 174.9278 | 185.9068 | 146.4468
168.4729 | 174.0239 | 185.8452 | 146.7574
169.4729 | 174.98 | 186.4158 | 147.5132
170.4885 | 27.4075 | 27.6673 | 28.0413
171.4729 | 25.796 | 26.4604 | 25.7779
172.4729 | 28.971 | 29.0939 | 26.8343
173.4729 | 178.8251 | 188.87 | 149.0893
174.4729 | 180.3336 | 190.0959 | 149.5832
175.4729 | 181.4227 | 190.6774 | 149.8101
176.4729 | 181.1908 | 190.8913 | 149.7154
177.4729 | 182.4434 | 192.6082 | 150.6381
178.4729 | 183.5152 | 193.6392 | 151.1791
179.4729 | 183.9141 | 194.4535 | 150.8705
180.4729 | 184.429 | 195.3565 | 151.0114
181.4729 | 185.1044 | 194.9725 | 151.1192
182.4729 | 186.0618 | 195.5193 | 151.4049
183.4729 | 186.4624 | 195.7751 | 152.2632
184.4729 | 186.9328 | 196.7071 | 152.609
185.4729 | 187.5102 | 198.1064 | 153.2212
186.4729 | 187.7352 | 197.7023 | 154.3851
187.4729 | 188.7017 | 198.8547 | 154.8705
188.4729 | 189.4928 | 199.6675 | 154.8049
189.4729 | 189.0467 | 200.4322 | 154.9913
190.4729 | 190.3379 | 202.9407 | 157.0585
191.4729 | 192.4482 | 204.359 | 156.9574
192.4729 | 194.3976 | 204.7986 | 157.8758
193.4729 | 195.5014 | 205.5931 | 157.896
194.4729 | 195.6128 | 205.515 | 158.3707
195.4729 | 195.2617 | 205.3312 | 158.0758
196.4729 | 194.789 | 204.1807 | 157.9407
197.4729 | 194.5743 | 204.3317 | 158.984
198.4729 | 195.629 | 203.9047 | 159.3279
199.4729 | 196.5429 | 203.4836 | 159.3508
200.4729 | 196.6445 | 203.1122 | 159.9187
201.4729 | 197.5279 | 203.9117 | 160.8659
202.4729 | 196.6349 | 204.2951 | 160.9469
203.4729 | 196.3547 | 203.3867 | 161.1635
204.4729 | 196.5727 | 203.8318 | 161.4192
205.4729 | 197.2405 | 204.5205 | 161.6629
206.4729 | 197.731 | 205.2743 | 162.0878
207.4729 | 198.5508 | 205.2784 | 163.4247
208.4729 | 197.8461 | 205.4491 | 163.8048
209.4729 | 197.5134 | 205.0359 | 164.2529
210.4729 | 197.3617 | 205.0773 | 164.6075
211.4729 | 197.6558 | 205.5647 | 164.2789
212.4729 | 197.3319 | 205.8636 | 164.2438
213.4729 | 199.3773 | 206.1705 | 164.9415
214.4729 | 199.5075 | 205.6131 | 164.9563
215.4729 | 198.9527 | 205.5522 | 165.159
216.4729 | 199.9211 | 206.3646 | 165.3325
217.4729 | 201.4386 | 207.9589 | 165.9675
218.4729 | 203.4464 | 208.3771 | 166.5838
219.4729 | 204.8013 | 209.3484 | 166.8316
220.4729 | 205.9574 | 210.2497 | 167.2889
221.4729 | 206.0906 | 211.0982 | 167.1418
222.4729 | 206.8034 | 211.6562 | 167.3216
223.4729 | 207.9954 | 212.5794 | 167.4834
224.4729 | 209.6848 | 213.5445 | 166.9793
225.4729 | 209.5267 | 214.0549 | 166.4519
226.4729 | 209.804 | 215.7351 | 166.6428
227.4729 | 210.2454 | 216.947 | 167.6692
228.4729 | 210.2036 | 216.6586 | 168.5493
229.4729 | 209.7466 | 216.1159 | 168.3864
230.4729 | 209.5233 | 217.2056 | 168.6799
231.4729 | 209.5734 | 218.7437 | 168.4133
232.4729 | 210.4978 | 220.1385 | 168.5672
233.4729 | 212.993 | 221.1573 | 169.8214
234.4729 | 212.2175 | 221.0498 | 170.2994
235.4729 | 211.2625 | 221.1828 | 170.7505
236.4729 | 210.6682 | 220.1495 | 170.7303
237.4729 | 209.3774 | 219.4895 | 170.1663
238.4729 | 210.0175 | 219.8901 | 169.533
239.4729 | 210.5637 | 219.9945 | 170.0269
240.4729 | 209.5741 | 219.4707 | 170.1405
241.4729 | 209.1573 | 219.0189 | 170.4139
242.4729 | 208.4388 | 219.1171 | 170.7386
243.4729 | 208.0947 | 218.5359 | 171.9157
244.4729 | 208.1341 | 218.508 | 172.0291
245.4729 | 207.7808 | 217.9987 | 172.0809
246.4729 | 207.9206 | 217.2618 | 172.312
247.4729 | 206.8914 | 216.4248 | 172.6565
248.4729 | 206.5632 | 217.0449 | 172.9349
249.4729 | 207.5764 | 218.6611 | 173.3234
250.4729 | 207.5289 | 219.3839 | 173.1213
251.4729 | 208.5628 | 219.4913 | 173.4265
252.4729 | 208.9666 | 219.3947 | 173.5549
253.4729 | 209.3708 | 219.1297 | 173.2988
254.4729 | 210.1585 | 219.8661 | 173.0357
255.4729 | 210.9345 | 220.6021 | 173.3301
256.4729 | 211.6888 | 221.0603 | 173.2047
257.4729 | 213.2969 | 222.1956 | 174.3396
258.4729 | 213.8661 | 223.2559 | 174.6148
259.4729 | 215.1071 | 224.7864 | 174.5184
260.4729 | 215.1081 | 225.1052 | 174.8731
261.4729 | 215.4235 | 225.4849 | 175.3071
262.4729 | 215.0944 | 226.6197 | 175.6588
263.4729 | 217.4704 | 226.902 | 176.5748
264.4729 | 216.8629 | 226.7813 | 176.6688
265.4729 | 217.6795 | 227.547 | 176.7085
266.4729 | 219.9086 | 228.6069 | 177.3757
267.4729 | 220.3291 | 229.4008 | 177.995
268.4729 | 221.0792 | 229.6416 | 178.9254
269.4729 | 221.3428 | 230.9119 | 179.3064
270.4729 | 221.1515 | 230.3037 | 179.5181
271.4729 | 222.1317 | 230.5147 | 179.6663
272.4729 | 223.6887 | 231.9165 | 179.6663
273.4729 | 225.6949 | 233.6546 | 180.272
274.4729 | 226.5995 | 234.0682 | 181.2402
275.4729 | 226.7981 | 234.3949 | 181.4765
276.4729 | 226.5637 | 234.7101 | 181.2058
277.4729 | 227.6803 | 235.0924 | 181.3847
278.4729 | 228.6956 | 235.5993 | 181.5176
279.4729 | 229.2482 | 235.163 | 181.2922
280.4729 | 230.2724 | 234.8573 | 181.0465
281.4729 | 229.8886 | 233.9246 | 181.1168
282.4729 | 231.8024 | 234.6084 | 180.7952
283.4729 | 232.3118 | 234.9624 | 180.3863
284.4729 | 232.7337 | 235.1614 | 180.2624
285.4729 | 234.0237 | 236.0593 | 180.5108
286.4729 | 234.3478 | 236.6691 | 180.7254
287.4729 | 234.3045 | 237.1567 | 181.1306
288.4729 | 234.1906 | 237.0246 | 181.2957
289.4729 | 233.3069 | 236.2795 | 180.9643
290.4885 | 232.7601 | 236.7758 | 180.8911
291.4729 | 232.088 | 237.0287 | 181.508
292.4729 | 231.9838 | 236.8299 | 181.244
293.4729 | 232.4411 | 236.6407 | 180.9959
294.4729 | 232.1412 | 236.3189 | 180.9523
295.4729 | 230.9807 | 236.5487 | 181.1771
296.4729 | 231.3898 | 237.1093 | 181.7224
297.4729 | 230.7089 | 237.1908 | 181.5173
298.4729 | 231.1296 | 237.781 | 181.8813
299.4729 | 232.2828 | 238.7938 | 182.316
300.4729 | 232.9015 | 240.6495 | 183.8541
301.4729 | 232.94 | 241.5362 | 184.8501
302.4729 | 235.0479 | 243.9261 | 185.8042
303.4729 | 235.1775 | 244.569 | 186.0112
304.4729 | 235.8005 | 244.6458 | 186.0842
305.4729 | 235.9046 | 243.5665 | 186.2098
306.4729 | 236.1086 | 243.1479 | 185.7785
307.4729 | 237.7843 | 243.3312 | 185.7233
308.4729 | 238.2682 | 243.7263 | 185.8411
309.4729 | 238.2871 | 245.0399 | 185.7113
310.4729 | 239.5427 | 244.9873 | 186.3505
311.4729 | 239.381 | 245.0299 | 186.6246
312.4729 | 238.544 | 244.7138 | 187.5217
313.4729 | 238.3754 | 244.8287 | 187.6237
314.4729 | 238.0962 | 245.2698 | 188.0296
315.4729 | 237.5601 | 244.525 | 188.6138
316.4729 | 237.6389 | 244.9859 | 188.5981
317.4729 | 238.4631 | 245.3074 | 188.6399
318.4729 | 239.0183 | 245.1785 | 188.6501
319.4729 | 238.8665 | 245.2873 | 188.5482
320.4729 | 238.7392 | 245.2166 | 188.628
321.4729 | 240.2506 | 245.3682 | 188.4804
322.4729 | 239.2111 | 245.224 | 188.34
323.4729 | 238.51 | 244.5868 | 187.9596
324.4729 | 238.165 | 243.7595 | 188.5748
325.4729 | 236.6333 | 243.8183 | 188.4316
326.4729 | 235.9809 | 243.4551 | 188.3171
327.4729 | 237.299 | 243.5362 | 189.2017
328.4729 | 236.934 | 244.4603 | 190.1352
329.4729 | 236.9702 | 244.4416 | 190.2045
330.4729 | 236.7172 | 243.7724 | 190.1775
331.4729 | 236.6557 | 244.4733 | 190.2322
332.4729 | 236.7057 | 244.3292 | 191.223
333.4729 | 238.0107 | 243.9452 | 191.5448
334.4729 | 238.3019 | 243.8329 | 191.3478
335.4729 | 237.1109 | 243.54 | 190.8156
336.4729 | 237.5029 | 243.8277 | 190.8939
337.4729 | 238.6968 | 246.0814 | 191.5282
338.4729 | 240.7425 | 247.2212 | 191.9408
339.4729 | 242.557 | 249.048 | 192.1953
340.4729 | 241.292 | 248.4361 | 192.6261
341.4729 | 241.5285 | 249.0332 | 192.8448
342.4729 | 240.9164 | 248.977 | 192.466
343.4729 | 240.5834 | 249.3622 | 192.5978
344.4729 | 240.474 | 248.5339 | 192.2457
345.4729 | 240.5385 | 248.3531 | 191.9149
346.4729 | 241.1454 | 247.8347 | 191.8807
347.4729 | 241.0227 | 247.6404 | 191.7725
348.4729 | 240.4406 | 247.3254 | 191.6078
349.4729 | 241.7533 | 248.8346 | 191.9948
350.4885 | 242.697 | 249.3001 | 193.2746
351.4729 | 243.0617 | 250.1413 | 193.5007
352.4729 | 244.797 | 250.2331 | 194.4976
353.4729 | 246.607 | 252.8167 | 195.4744
354.4729 | 246.9304 | 253.3383 | 195.7743
355.4729 | 247.4522 | 253.2755 | 196.1491
356.4729 | 247.9958 | 254.0188 | 196.7146
357.4729 | 249.2158 | 255.5869 | 197.3407
358.4729 | 249.7452 | 255.9533 | 198.3034
359.4729 | 249.9009 | 255.7728 | 198.4553
360.4729 | 250.2966 | 255.9492 | 199.0623
361.4729 | 249.6009 | 255.8487 | 199.0791
362.4729 | 249.4786 | 255.5406 | 199.9133
363.4729 | 249.7792 | 255.6003 | 200.1152
364.4729 | 251.0298 | 255.6948 | 200.0916
365.4729 | 251.1084 | 255.6605 | 199.7035
366.4729 | 251.0571 | 255.5076 | 199.2977
367.4729 | 251.2761 | 254.9834 | 199.1744
368.4729 | 251.1001 | 255.7852 | 198.6977
369.4729 | 250.6494 | 257.0042 | 198.4516
370.4729 | 250.7824 | 257.1341 | 199.3242
371.4729 | 251.0186 | 258.1684 | 199.652
372.4729 | 251.1959 | 258.3866 | 200.2264
373.4729 | 251.9858 | 259.3746 | 200.5161
374.4729 | 251.8969 | 259.3826 | 201.1419
375.4729 | 251.801 | 259.2447 | 201.3786
376.4729 | 251.3954 | 258.443 | 201.2375
377.4729 | 251.4646 | 257.827 | 201.8958
378.4729 | 251.1808 | 257.4841 | 202.4399
379.4729 | 251.1697 | 257.3204 | 202.9353
380.4729 | 250.7214 | 257.6299 | 203.0479
381.4729 | 250.5892 | 258.2978 | 204.0833
382.4729 | 250.5185 | 259.2394 | 204.4718
383.4729 | 249.2765 | 258.684 | 204.1758
384.4729 | 248.7715 | 259.7422 | 204.4691
385.4729 | 248.8597 | 260.7831 | 205.4843
386.4729 | 249.7135 | 261.5977 | 206.2081
387.4729 | 248.8699 | 261.3442 | 207.382
388.4729 | 249.0755 | 261.7065 | 207.4415
389.4729 | 249.9802 | 261.5773 | 207.0623
390.4729 | 252.1714 | 262.3745 | 207.4884
391.4729 | 253.7142 | 263.614 | 207.7794
392.4729 | 253.7372 | 264.3672 | 208.7048
393.4729 | 254.812 | 264.4759 | 208.8336
394.4729 | 255.5756 | 264.842 | 209.4055
395.4729 | 256.6362 | 265.6371 | 209.7923
396.4729 | 256.483 | 265.6197 | 210.5697
397.4729 | 257.9317 | 266.4528 | 210.0991
398.4729 | 259.4439 | 267.2845 | 210.4552
399.4729 | 260.4255 | 268.2777 | 211.7299
400.4729 | 260.851 | 268.6141 | 211.5075
401.4729 | 261.026 | 269.7687 | 211.7665
402.4729 | 260.9404 | 270.0898 | 211.5261
403.4729 | 261.3623 | 270.5794 | 211.7271
404.4729 | 261.3499 | 270.8384 | 212.0835
405.4729 | 260.7072 | 270.9196 | 211.8347
406.4729 | 260.74 | 271.7994 | 213.1141
407.4729 | 261.5075 | 272.901 | 213.4011
408.4729 | 260.6094 | 272.5327 | 213.682
409.4729 | 260.2838 | 273.5287 | 215.0964
410.4885 | 260.3512 | 274.6694 | 215.784
411.4729 | 259.6935 | 273.945 | 215.4322
412.4729 | 259.26 | 273.6507 | 215.8178
413.4729 | 259.3652 | 273.1997 | 216.0614
414.4729 | 259.2778 | 273.3369 | 217.6025
415.4729 | 260.3523 | 274.3322 | 218.3447
416.4729 | 261.1939 | 274.8983 | 218.5634
417.4729 | 262.3224 | 275.673 | 220.2052
418.4729 | 263.7354 | 276.4152 | 220.6775
419.4729 | 264.1219 | 276.7561 | 222.247
420.4729 | 264.4224 | 277.4857 | 222.6979
421.4729 | 265.0006 | 280.3603 | 222.945
422.4729 | 268.1239 | 283.4903 | 224.5436
423.4729 | 269.0693 | 284.1812 | 226.1027
424.4729 | 270.7441 | 286.1419 | 226.9218
425.4729 | 270.9836 | 288.1895 | 227.9527
426.4729 | 272.6641 | 288.0943 | 228.2018
427.4729 | 274.8153 | 290.2664 | 230.9923
428.4729 | 278.1661 | 291.4614 | 231.562
429.4729 | 281.6793 | 292.4887 | 231.4314
430.4729 | 282.6756 | 293.3799 | 232.377
431.4729 | 284.1408 | 293.8134 | 233.0137
432.4729 | 285.0326 | 294.7472 | 233.3958
433.4729 | 284.4551 | 294.6422 | 233.4299
434.4729 | 284.7613 | 295.6746 | 234.7673
435.4729 | 284.2288 | 295.4157 | 235.5805
436.4729 | 284.9145 | 295.0627 | 234.7151
437.4729 | 286.271 | 295.295 | 234.39
438.4729 | 286.4026 | 295.3827 | 234.0679
439.4729 | 287.7507 | 295.6428 | 233.5602
440.4729 | 288.1201 | 296.1692 | 233.5656
441.4729 | 286.9589 | 296.4063 | 233.4402
442.4729 | 286.8913 | 296.8407 | 233.9743
443.4729 | 287.2883 | 298.1738 | 234.3653
444.4729 | 286.5874 | 297.031 | 234.9269
445.4729 | 287.3281 | 296.8105 | 234.2809
446.4729 | 287.5248 | 297.5255 | 235.3734
447.4729 | 288.0998 | 300.377 | 236.1434
448.4729 | 289.2115 | 301.6827 | 236.497
449.4729 | 291.1234 | 301.4484 | 236.6588
450.4729 | 292.3388 | 303.0068 | 237.2843
451.4729 | 295.2427 | 304.4289 | 237.8156
452.4729 | 298.4881 | 306.2421 | 237.8499
453.4729 | 302.0234 | 313.1129 | 239.2419
454.4729 | 300.1997 | 313.2701 | 240.0775
455.4729 | 300.9042 | 313.6598 | 241.019
456.4729 | 301.5201 | 313.7869 | 241.7228
457.4729 | 302.6471 | 313.9022 | 242.4058
458.4729 | 302.7571 | 314.015 | 242.8367
459.4729 | 303.0957 | 313.7087 | 244.3698
460.4729 | 303.2916 | 314.2603 | 245.3033
461.4729 | 304.9265 | 314.7172 | 247.0932
462.4729 | 307.6026 | 316.0293 | 249.5137
463.4729 | 306.9706 | 315.8961 | 249.7176
464.4729 | 306.8775 | 316.3562 | 249.6943
465.4729 | 307.3463 | 316.6206 | 250.2158
466.4729 | 311.1959 | 318.8423 | 250.5038
467.4729 | 314.4048 | 319.5906 | 250.824
468.4729 | 321.2169 | 324.5198 | 253.2013
469.4729 | 328.9271 | 328.0485 | 252.8992
470.4729 | 327.1976 | 329.0953 | 253.251
471.4729 | 329.3461 | 332.3102 | 255.0346
472.4729 | 328.3545 | 332.1705 | 254.6041
473.4729 | 327.1636 | 332.7557 | 254.3622
474.4729 | 326.1403 | 333.9848 | 255.4913
475.4729 | 325.3758 | 333.002 | 256.0842
476.4729 | 324.913 | 334.4948 | 257.6982
477.4729 | 323.5366 | 334.2763 | 257.7105
478.4729 | 323.2134 | 340.2863 | 257.0232
479.4729 | 321.6759 | 338.8413 | 257.2856
480.4729 | 320.8027 | 339.1235 | 257.0691
481.4729 | 320.8127 | 344.7034 | 256.9317
482.4729 | 320.7895 | 353.0023 | 257.0436
483.4729 | 318.5649 | 357.1791 | 257.3154
484.4729 | 317.0425 | 360.5272 | 257.1523
485.4729 | 314.5063 | 359.5653 | 257.3131
486.4729 | 313.4024 | 358.1496 | 257.3138
487.4729 | 314.0721 | 357.7116 | 256.6619
488.4729 | 311.6449 | 354.7122 | 256.3519
489.4729 | 309.8739 | 355.5899 | 255.9909
490.4729 | 308.8968 | 360.3786 | 256.4264
491.4729 | 308.5293 | 359.6976 | 256.0425
492.4729 | 309.0426 | 356.7441 | 255.6607
493.4729 | 308.3513 | 354.3949 | 256.2898
494.4729 | 306.7898 | 351.5158 | 256.8056
495.4729 | 307.3234 | 350.6478 | 256.7825
496.4729 | 309.9731 | 351.0868 | 258.6719
497.4729 | 313.0095 | 351.6675 | 260.8026
498.4729 | 316.7344 | 351.175 | 260.9462
499.4729 | 317.0184 | 350.3908 | 260.5043
500.4729 | 315.5203 | 350.1227 | 260.9267
501.4729 | 322.3089 | 352.5043 | 261.6038
502.4729 | 328.6044 | 352.1977 | 261.8157
503.4729 | 337.7937 | 353.8086 | 263.1147
504.4729 | 345.9978 | 354.3976 | 262.9422
505.4729 | 344.3973 | 352.8775 | 262.9249
506.4729 | 346.6259 | 358.2212 | 264.0754
507.4885 | 354.9357 | 367.6973 | 265.0467
508.4729 | 360.7282 | 383.363 | 266.684
509.4729 | 368.4071 | 382.9441 | 266.9948
510.4729 | 369.5245 | 384.9952 | 267.2763
511.4729 | 368.2967 | 385.4753 | 267.8403
512.4729 | 370.9493 | 390.2406 | 267.7011
513.4729 | 379.1481 | 392.4227 | 267.9682
514.4729 | 377.4135 | 390.0292 | 269.0789
515.4729 | 376.498 | 388.5986 | 269.8094
516.4729 | 372.5244 | 384.5335 | 270.0611
517.4729 | 370.8541 | 382.2982 | 272.0915
518.4729 | 367.61 | 379.6917 | 271.6416
519.4729 | 364.8825 | 377.9554 | 270.2887
520.4729 | 364.8125 | 376.8494 | 273.2741
521.4729 | 366.8143 | 379.6877 | 274.3919
522.4729 | 368.4908 | 379.7961 | 275.2799
523.4729 | 366.1746 | 379.0532 | 274.9415
524.4729 | 368.6121 | 382.5774 | 275.5311
525.4729 | 364.8071 | 392.1169 | 276.8443
526.4729 | 365.0071 | 399.7498 | 277.8943
527.4729 | 365.9894 | 404.4099 | 278.7963
528.4729 | 363.2918 | 403.6369 | 279.6963
529.4729 | 361.4191 | 400.0129 | 278.9641
530.4885 | 366.2551 | 396.2251 | 279.9257
531.4729 | 363.3684 | 394.8973 | 280.7882
532.4729 | 362.2007 | 395.4446 | 280.8368
533.4729 | 361.2326 | 393.2773 | 280.4877
534.4729 | 358.9021 | 389.532 | 280.4951
535.4729 | 356.8522 | 384.9543 | 280.2588
536.4729 | 354.7971 | 381.2686 | 280.5976
537.4729 | 352.3494 | 378.4041 | 280.6487
538.4729 | 350.283 | 376.1495 | 281.8586
539.4729 | 348.9076 | 374.0635 | 281.9957
540.4729 | 348.2179 | 371.5754 | 281.0898
541.4729 | 347.3947 | 369.8991 | 280.1075
542.4729 | 346.14 | 367.5748 | 279.1631
543.4729 | 344.5645 | 364.7755 | 278.7934
544.4729 | 342.9458 | 363.6072 | 278.2128
545.4729 | 343.5375 | 362.2166 | 277.8902
546.4729 | 342.9657 | 361.1974 | 278.2591
547.4729 | 341.8526 | 360.3504 | 278.1654
548.4729 | 340.339 | 359.1188 | 277.2863
549.4729 | 341.3945 | 360.3642 | 278.7935
550.4729 | 340.367 | 359.4267 | 279.1135
551.4729 | 337.6335 | 357.8184 | 279.2498
552.4729 | 336.4163 | 356.5565 | 278.7462
553.4729 | 335.7864 | 355.9611 | 280.0808
554.4729 | 335.2409 | 357.2308 | 279.701
555.4729 | 334.6915 | 358.2594 | 280.5626
556.4729 | 332.9526 | 357.0309 | 280.7881
557.4729 | 332.7639 | 356.1835 | 282.9671
558.4729 | 334.4574 | 356.6421 | 283.2772
559.4729 | 334.4374 | 357.8014 | 282.0775
560.4729 | 337.701 | 357.2791 | 280.6691
561.4729 | 336.7435 | 357.1812 | 279.8764
562.4729 | 337.6983 | 357.5719 | 279.524
563.4729 | 341.7786 | 359.7312 | 280.8424
564.4729 | 344.5008 | 364.6042 | 280.2088
565.4729 | 345.9289 | 364.1146 | 280.5028
566.4729 | 344.5361 | 363.3588 | 280.5253
567.4729 | 344.0609 | 362.0224 | 280.3439
568.4729 | 342.9003 | 360.4655 | 279.1933
569.4729 | 342.1097 | 359.0949 | 278.9247
570.4729 | 340.3351 | 357.5596 | 279.8267
571.4729 | 338.9096 | 358.2296 | 279.9771
572.4729 | 337.7097 | 358.2392 | 279.8266
573.4729 | 337.0658 | 357.5623 | 279.7403
574.4729 | 335.1484 | 356.096 | 280.0337
575.4729 | 334.0097 | 355.9604 | 279.3513
576.4729 | 334.6826 | 356.2959 | 279.9565
577.4729 | 334.3037 | 356.0746 | 279.5915
578.4729 | 332.6366 | 355.0753 | 279.7726
579.4729 | 331.7787 | 354.0743 | 279.1292
580.4729 | 331.1247 | 353.3819 | 279.5109
581.4729 | 330.4736 | 352.3575 | 279.9793
582.4729 | 328.4821 | 351.6506 | 280.2536
583.4729 | 327.9246 | 351.7962 | 280.4879
584.4729 | 328.485 | 352.6276 | 280.5956
585.4729 | 328.3968 | 353.4615 | 280.4177
586.4729 | 329.2605 | 353.1174 | 281.4684
587.4729 | 329.0183 | 352.3895 | 281.3136
588.4729 | 328.5073 | 352.3527 | 281.152
589.4729 | 329.1625 | 351.0791 | 281.0054
590.4729 | 327.9634 | 350.7585 | 281.8031
591.4729 | 326.8703 | 351.1014 | 282.1551
592.4729 | 326.9982 | 350.0851 | 282.8856
593.4729 | 326.3859 | 351.1984 | 282.5021
594.4729 | 325.4484 | 352.6602 | 283.148
595.4729 | 325.962 | 354.3625 | 283.373
596.4729 | 325.0459 | 354.4202 | 283.9697
597.4729 | 324.326 | 355.1773 | 284.1738
598.4729 | 324.0691 | 354.6008 | 283.9991
599.4729 | 324.9214 | 353.083 | 284.8063
600.4729 | 325.6584 | 352.6523 | 285.3753
601.4729 | 325.5763 | 352.1195 | 285.872
602.4729 | 326.1105 | 352.0602 | 287.5916
603.4729 | 326.0397 | 350.8664 | 288.5172
604.4729 | 325.9409 | 349.4819 | 289.4746
605.4729 | 325.6566 | 348.2091 | 289.4982
606.4729 | 325.15 | 346.7776 | 290.1575
607.4729 | 325.0601 | 345.7271 | 290.0148
608.4729 | 325.2096 | 347.1683 | 290.4078
609.4729 | 324.5956 | 348.279 | 290.3929
610.4729 | 324.1509 | 349.4621 | 290.1658
611.4729 | 324.6814 | 349.6109 | 290.5152
612.4729 | 325.7303 | 351.6316 | 291.1021
613.4729 | 328.3544 | 352.5541 | 292.01
614.4885 | 328.0108 | 353.5665 | 292.8917
615.4729 | 329.1618 | 355.1923 | 293.3422
616.4729 | 330.2106 | 356.5224 | 292.8985
617.4729 | 329.7071 | 357.4835 | 292.5809
618.4729 | 329.1504 | 357.1927 | 291.8738
619.4729 | 329.5887 | 358.2438 | 291.0013
620.4729 | 328.7118 | 357.6855 | 290.7612
621.4729 | 329.8599 | 359.2526 | 291.1095
622.4729 | 331.7961 | 359.9873 | 292.0303
623.4729 | 331.9564 | 360.5812 | 291.2659
624.4729 | 331.6157 | 360.0781 | 290.6767
625.4729 | 331.6227 | 359.6419 | 292.1616
626.4729 | 330.8623 | 358.9111 | 292.9672
627.4729 | 329.8964 | 357.5758 | 292.9923
628.4729 | 331.1896 | 356.2842 | 295.0131
629.4729 | 331.8954 | 354.7699 | 294.6789
630.4729 | 331.8761 | 354.4179 | 295.0635
631.4729 | 332.6038 | 354.5858 | 294.9245
632.4729 | 331.6883 | 354.8629 | 294.876
633.4729 | 331.092 | 354.2567 | 295.2198
634.4729 | 329.3527 | 352.9151 | 295.7318
635.4729 | 328.346 | 352.6092 | 295.8548
636.4729 | 326.0923 | 352.2505 | 297.3375
637.4729 | 324.6409 | 353.3237 | 297.5196
638.4729 | 324.5066 | 352.2672 | 298.0773
639.4729 | 321.9665 | 352.5543 | 297.3546
640.4729 | 320.5755 | 352.0229 | 295.9853
641.4729 | 319.6575 | 353.8696 | 296.0639
642.4729 | 319.729 | 355.254 | 295.7648
643.4729 | 320.2312 | 357.2554 | 294.7752
644.5042 | 321.8598 | 358.5499 | 294.7575
645.4729 | 321.6227 | 356.9379 | 294.688
646.4729 | 321.2286 | 356.9736 | 294.4704
647.4729 | 320.4411 | 355.9174 | 295.6007
648.4729 | 320.5067 | 355.5705 | 297.164
649.4729 | 319.6946 | 356.6231 | 299.1549
650.4729 | 320.8278 | 356.1206 | 299.335
651.4729 | 320.7986 | 357.2287 | 300.3572
652.4729 | 320.666 | 357.4424 | 301.201
653.4729 | 321.0661 | 356.7268 | 301.7581
654.4729 | 321.4994 | 356.8744 | 301.7253
655.4729 | 322.1265 | 356.8242 | 301.4133
656.4729 | 322.6912 | 358.2592 | 302.5146
657.4729 | 324.1031 | 359.1597 | 304.0166
658.4729 | 325.2764 | 359.4424 | 305.3238
659.4729 | 323.3647 | 359.7511 | 304.9923
660.4729 | 322.8187 | 361.3342 | 306.1684
661.4729 | 325.3999 | 364.4682 | 307.2184
662.4729 | 325.0536 | 363.7434 | 306.3376
663.4729 | 326.0654 | 363.9607 | 306.4853
664.4729 | 327.2268 | 365.9073 | 306.9362
665.4729 | 327.6918 | 366.8206 | 307.5549
666.4729 | 330.068 | 370.8041 | 307.7623
667.4729 | 332.674 | 372.1218 | 309.5086
668.4729 | 331.504 | 373.9843 | 309.0434
669.4729 | 331.7743 | 374.1426 | 308.7643
670.4729 | 330.84 | 374.5418 | 310.6115
671.4729 | 331.3651 | 379.9867 | 312.8384
672.4729 | 331.3115 | 379.6607 | 312.8504
673.4729 | 332.9932 | 380.2898 | 312.1356
674.4729 | 331.7599 | 378.4064 | 311.0356
675.4729 | 330.5752 | 376.5569 | 310.7413
676.4729 | 328.9328 | 373.7143 | 309.6225
677.4729 | 327.077 | 373.6973 | 309.3479
678.4729 | 325.1245 | 374.4502 | 310.0413
679.4729 | 324.0133 | 374.02 | 309.7956
680.4729 | 325.1035 | 374.1365 | 309.8262
681.4729 | 325.7415 | 372.7936 | 309.8822
682.4729 | 326.5748 | 372.6661 | 310.3456
683.4729 | 327.6654 | 372.9988 | 312.5864
684.4729 | 328.8453 | 373.6885 | 314.7312
685.4729 | 327.2404 | 376.0804 | 317.9586
686.4729 | 327.21 | 374.7459 | 316.6788
687.4729 | 325.1961 | 376.3764 | 317.176
688.4729 | 326.0524 | 376.7967 | 318.5864
689.4729 | 326.0267 | 376.4339 | 319.3461
690.4729 | 326.8943 | 375.9653 | 319.368
691.4729 | 328.1006 | 376.1533 | 319.6585
692.4729 | 327.6523 | 375.2456 | 319.8666
693.4729 | 326.7757 | 375.0662 | 321.3903
694.4729 | 326.927 | 374.3869 | 323.5082
695.4729 | 328.1372 | 375.5367 | 324.8555
696.4729 | 330.4993 | 375.42 | 324.3485
697.4729 | 328.4745 | 374.1726 | 323.5369
698.4729 | 327.4316 | 372.7578 | 322.7722
699.4729 | 328.1934 | 371.8906 | 322.3723
700.4729 | 328.3398 | 372.0914 | 321.8805
701.4729 | 327.8732 | 371.5792 | 321.2103
702.4729 | 328.0815 | 370.9256 | 320.149
703.4729 | 327.4001 | 370.2911 | 319.2887
704.4885 | 326.669 | 370.5375 | 318.547
705.4729 | 325.682 | 370.7854 | 317.1812
706.4729 | 324.614 | 368.9925 | 316.5147
707.4729 | 324.2291 | 369.3985 | 316.8181
708.4729 | 323.9127 | 367.9696 | 316.6909
709.4729 | 324.6082 | 369.6062 | 316.9962
710.4729 | 323.6468 | 370.278 | 316.7401
711.4729 | 322.7166 | 370.5666 | 317.3431
712.4729 | 323.4975 | 371.2377 | 317.121
713.4729 | 323.1651 | 370.122 | 316.4735
714.4729 | 321.8528 | 370.6161 | 316.4735
715.4729 | 320.5859 | 369.6681 | 316.1742
716.4729 | 320.0313 | 370.096 | 316.5087
717.4729 | 320.5257 | 370.983 | 315.172
718.4729 | 320.669 | 370.1105 | 315.1095
719.4729 | 321.052 | 368.7927 | 315.2341
720.4729 | 321.0622 | 368.6532 | 315.5689
721.4729 | 322.4156 | 370.397 | 315.9711
722.4729 | 321.6871 | 370.4365 | 315.8387
723.4729 | 321.0929 | 369.6429 | 315.9218
724.4729 | 321.1888 | 369.1741 | 317.1843
725.4729 | 321.4358 | 368.6231 | 317.37
726.4729 | 322.2622 | 369.2982 | 320.537
727.4729 | 323.5371 | 368.8551 | 321.9415
728.4729 | 324.2094 | 369.024 | 323.195
729.4729 | 325.0079 | 371.3913 | 322.7924
730.4729 | 325.3473 | 370.077 | 323.1576
731.4729 | 324.9356 | 369.028 | 324.8954
732.4729 | 326.1305 | 371.0276 | 325.103
733.4729 | 327.7443 | 371.2907 | 323.7376
734.4885 | 327.2957 | 370.2597 | 324.3479
735.4729 | 327.2503 | 369.5337 | 325.5021
736.4729 | 326.7815 | 369.7114 | 327.2142
737.4729 | 326.4899 | 369.0345 | 327.4142
738.4729 | 326.2207 | 369.7929 | 327.594
739.4729 | 326.0796 | 370.1286 | 326.3205
740.4729 | 325.1282 | 371.4904 | 326.915
741.4729 | 322.7912 | 371.7049 | 325.9809
742.4729 | 322.1758 | 372.8707 | 327.1343
743.4729 | 322.5983 | 373.3833 | 329.0448
744.4729 | 323.2885 | 374.3431 | 329.6939
745.4729 | 324.2979 | 374.4782 | 330.5843
746.4729 | 325.4647 | 374.3697 | 330.2662
747.4885 | 325.4626 | 373.3847 | 329.8615
748.4885 | 326.6796 | 373.7875 | 328.7502
749.4729 | 327.5352 | 373.4988 | 329.7996
750.4729 | 327.3071 | 372.8037 | 328.6452
751.4729 | 327.408 | 371.475 | 326.8488
752.4729 | 327.4421 | 370.3383 | 327.378
753.4729 | 327.7235 | 369.9576 | 326.04
754.4729 | 327.6356 | 370.0377 | 325.3835
755.4729 | 327.2682 | 369.8473 | 325.8825
756.4729 | 328.2036 | 369.8059 | 326.1013
757.4729 | 327.7943 | 370.4448 | 324.7284
758.4729 | 329.0786 | 371.2528 | 323.9285
759.4729 | 329.2907 | 372.4846 | 323.9605
760.4729 | 328.4502 | 373.907 | 325.0582
761.4729 | 328.842 | 373.977 | 325.8834
762.4729 | 328.9208 | 372.6451 | 325.3597
763.4729 | 327.4803 | 373.467 | 324.4464
764.4885 | 326.2288 | 373.4454 | 324.3657
765.4729 | 326.1126 | 372.7387 | 323.5002
766.4729 | 326.8033 | 371.7598 | 322.5783
767.4729 | 326.8901 | 370.4203 | 322.5955
768.4729 | 327.8496 | 370.0243 | 322.4983
769.4729 | 328.7101 | 371.17 | 321.9655
770.4729 | 328.6679 | 370.224 | 321.9069
771.4729 | 327.9052 | 369.8237 | 321.9271
772.4729 | 328.0587 | 369.658 | 322.1472
773.4729 | 327.7726 | 368.6375 | 320.9919
774.4729 | 327.6921 | 368.418 | 320.332
775.4729 | 326.6811 | 368.8031 | 318.9507
776.4729 | 325.8116 | 367.6473 | 318.4751
777.4729 | 326.0985 | 366.6585 | 318.8228
778.4729 | 326.4781 | 366.3935 | 318.367
779.4729 | 325.8226 | 365.3628 | 318.2925
780.4729 | 323.9493 | 365.2045 | 318.6224
781.4729 | 323.3222 | 364.8809 | 318.4344
782.4729 | 322.0554 | 364.662 | 317.2767
783.4729 | 322.0356 | 363.5199 | 317.5607
784.4729 | 322.2589 | 363.2596 | 317.0949
785.4729 | 324.0744 | 364.434 | 316.5339
786.4729 | 323.5439 | 364.2714 | 317.4299
787.4729 | 323.8272 | 364.0265 | 318.2981
788.4729 | 324.8957 | 363.7511 | 319.9395
789.4729 | 324.9409 | 364.1583 | 321.2837
790.4729 | 324.5099 | 364.726 | 323.6538
791.4729 | 323.8584 | 365.34 | 323.9271
792.4729 | 325.8024 | 368.161 | 324.7281
793.4729 | 326.5944 | 367.8597 | 324.7811
794.4729 | 327.8252 | 369.5439 | 326.1454
795.4729 | 327.5531 | 368.9962 | 326.0326
796.4729 | 329.9255 | 370.2739 | 326.748
797.4729 | 328.9516 | 371.3761 | 327.0778
798.4729 | 328.376 | 371.5342 | 326.7944
799.4729 | 327.8311 | 372.3537 | 326.4411
800.4729 | 327.7871 | 373.3715 | 327.0152
801.4729 | 328.7421 | 373.9715 | 328.3826
802.4729 | 329.3905 | 373.6632 | 328.0812
803.4729 | 330.5759 | 373.4343 | 328.0158
804.4729 | 330.3758 | 372.4605 | 329.0236
805.4729 | 331.7072 | 373.1487 | 329.48
806.4729 | 332.8474 | 373.7392 | 328.7098
807.4729 | 332.744 | 372.8288 | 328.3457
808.4729 | 332.6366 | 370.9638 | 328.239
809.4729 | 331.9871 | 369.7554 | 328.6568
810.4729 | 331.7049 | 369.7032 | 329.3509
811.4729 | 331.3246 | 369.2962 | 328.5668
812.4729 | 329.667 | 370.156 | 327.4866
813.4729 | 329.0415 | 369.9856 | 326.5916
814.4729 | 327.941 | 368.36 | 326.1832
815.4729 | 327.224 | 367.9545 | 325.9582
816.4729 | 327.6782 | 367.5404 | 325.8793
817.4729 | 328.5001 | 366.6349 | 325.9524
818.4729 | 329.8063 | 368.3507 | 327.3683
819.4729 | 330.247 | 368.6045 | 327.6223
820.4729 | 330.3843 | 367.6034 | 327.4279
821.4729 | 330.1733 | 366.0682 | 327.3376
822.4729 | 330.7306 | 366.4506 | 328.1151
823.4729 | 329.9468 | 366.8319 | 327.6526
824.4729 | 329.0644 | 367.1141 | 328.6356
825.4729 | 329.4271 | 367.7273 | 329.6977
826.4729 | 328.8781 | 367.3189 | 330.0376
827.4729 | 329.196 | 367.4964 | 330.3254
828.4729 | 327.4952 | 368.0509 | 331.6765
829.4729 | 326.4508 | 367.8229 | 331.14
830.4729 | 325.6321 | 368.2216 | 330.1503
831.4729 | 326.4791 | 368.3861 | 329.844
832.4729 | 326.9639 | 368.911 | 329.9094
833.4729 | 327.3552 | 368.8461 | 329.23
834.4729 | 328.3226 | 367.8973 | 328.9778
835.4729 | 328.2105 | 367.8377 | 329.6217
836.4729 | 328.6079 | 366.9686 | 329.3271
837.4729 | 328.8695 | 366.6062 | 329.5081
838.4729 | 328.5111 | 367.1023 | 329.3155
839.4729 | 328.8894 | 366.8484 | 329.9242
840.4729 | 328.1511 | 365.969 | 331.2056
841.4729 | 328.7367 | 365.5994 | 331.4958
842.4729 | 327.6358 | 365.6622 | 330.8427
843.4729 | 327.7382 | 366.3206 | 329.7689
844.4729 | 328.4776 | 366.4208 | 329.0522
845.4729 | 329.0162 | 366.5893 | 329.5361
846.4729 | 328.1052 | 365.5855 | 329.4748
847.4729 | 328.6613 | 363.9349 | 329.8402
848.4729 | 328.7261 | 364.9193 | 330.3152
849.4729 | 330.1132 | 364.8171 | 329.4127
850.4729 | 330.5181 | 364.4457 | 329.5718
851.4729 | 329.9866 | 363.0013 | 329.1557
852.4729 | 330.1505 | 362.993 | 329.3323
853.4729 | 331.3433 | 362.5146 | 328.3836
854.4885 | 332.367 | 362.3619 | 327.895
855.4729 | 332.6185 | 362.5099 | 328.0887
856.4729 | 332.7443 | 362.5713 | 327.9638
857.4729 | 332.2424 | 362.5341 | 328.1016
858.4729 | 332.0786 | 362.9533 | 327.9446
859.4729 | 331.6685 | 363.6806 | 330.3711
860.4729 | 332.2979 | 365.3631 | 330.2909
861.4729 | 332.1763 | 366.2056 | 329.833
862.4729 | 332.4322 | 366.5012 | 330.0523
863.4729 | 331.5534 | 365.388 | 330.68
864.4729 | 332.4594 | 365.3087 | 330.9647
865.4729 | 332.3695 | 364.5737 | 331.4599
866.4729 | 331.9413 | 363.9418 | 332.629
867.4729 | 331.3244 | 363.167 | 332.1475
868.4729 | 330.4538 | 362.2184 | 331.2915
869.4729 | 330.4576 | 362.5479 | 330.5057
870.4729 | 330.4557 | 363.8391 | 330.1127
871.4729 | 330.0059 | 363.9245 | 330.6595
872.4729 | 329.1191 | 362.6765 | 330.9113
873.4729 | 329.1247 | 362.4783 | 330.9924
874.4729 | 329.4727 | 362.8019 | 331.8021
875.4729 | 328.8552 | 363.3652 | 331.7707
876.4729 | 328.3574 | 362.8584 | 331.5926
877.4729 | 327.3526 | 362.8179 | 331.5027
878.4729 | 327.5974 | 361.7716 | 330.7274
879.4729 | 328.5587 | 361.3172 | 330.7126
880.4729 | 329.5698 | 361.2081 | 330.0363
881.4729 | 330.2644 | 362.051 | 329.2732
882.4729 | 329.1696 | 361.7065 | 330.2222
883.4729 | 327.8238 | 361.0662 | 330.3794
884.4729 | 326.6632 | 360.7766 | 329.9602
885.4729 | 327.3181 | 361.1724 | 331.3261
886.4729 | 326.7682 | 360.4338 | 331.4576
887.4729 | 325.1655 | 359.7321 | 332.3712
888.4729 | 325.8195 | 360.9102 | 332.5397
889.4729 | 326.5314 | 361.8591 | 333.6628
890.4729 | 327.0217 | 361.2953 | 334.2297
891.4729 | 327.5366 | 361.8179 | 334.7531
892.4729 | 326.9962 | 362.2903 | 334.5736
893.4729 | 326.9787 | 362.0097 | 336.3839
894.4729 | 327.2746 | 361.9782 | 336.7704
895.4729 | 326.5448 | 362.509 | 337.1023
896.4729 | 326.9127 | 362.7203 | 337.8597
897.4729 | 327.2563 | 363.9128 | 338.3913
898.4729 | 327.0803 | 363.8773 | 338.2836
899.4729 | 326.7717 | 363.0175 | 338.6106
900.4729 | 325.7831 | 362.6145 | 338.3706
901.4729 | 324.0457 | 362.3808 | 338.3836
902.4729 | 323.5641 | 362.0573 | 339.1702
903.4729 | 322.9942 | 362.6703 | 339.047
904.4729 | 323.3782 | 362.3779 | 339.9851
905.4729 | 322.7105 | 362.2975 | 341.0594
906.4729 | 322.8398 | 362.2702 | 341.785
907.4729 | 323.3349 | 362.1835 | 341.3699
908.4729 | 323.4918 | 362.4671 | 341.1718
909.4729 | 322.8863 | 362.2926 | 340.7874
910.4729 | 322.0541 | 361.9757 | 340.3725
911.4729 | 322.1278 | 361.397 | 340.5451
912.4729 | 322.27 | 361.191 | 340.6859
913.4729 | 322.514 | 361.6043 | 340.4416
914.4729 | 323.3124 | 361.5405 | 341.3368
915.4729 | 322.9688 | 361.3593 | 342.6252
916.4729 | 323.6888 | 361.8397 | 342.3149
917.4729 | 324.0649 | 361.6229 | 342.2552
918.4729 | 323.7146 | 360.8425 | 341.64
919.4729 | 322.6182 | 359.4685 | 341.6824
920.4729 | 323.1532 | 360.4522 | 341.6966
921.4729 | 323.3958 | 361.1807 | 342.3965
922.4729 | 322.9911 | 363.1105 | 342.7544
923.4729 | 323.2219 | 364.4747 | 342.7333
924.4729 | 323.446 | 366.6545 | 342.8712
925.4729 | 323.8991 | 367.5894 | 343.53
926.4729 | 323.7363 | 366.7361 | 343.9118
927.4729 | 323.9461 | 366.4451 | 344.581
928.4729 | 324.2583 | 366.0825 | 344.8081
929.4729 | 323.509 | 365.12 | 344.7839
930.4729 | 324.5425 | 365.9608 | 343.9212
931.4729 | 325.1136 | 366.0208 | 343.2217
932.4729 | 325.032 | 365.489 | 342.9295
933.4729 | 326.2802 | 364.2303 | 341.6946
934.4729 | 327.167 | 363.802 | 341.7675
935.4729 | 328.884 | 363.4846 | 341.0987
936.4729 | 328.4852 | 362.9726 | 341.0918
937.4729 | 328.577 | 362.4541 | 340.8764
938.4729 | 328.9835 | 362.2776 | 342.86
939.4729 | 329.1991 | 363.275 | 343.737
940.4729 | 329.3543 | 363.2588 | 343.4262
941.4729 | 329.0293 | 362.8057 | 342.655
942.4729 | 329.0946 | 364.3557 | 342.5905
943.4729 | 328.7752 | 365.4248 | 342.6753
944.4729 | 328.4834 | 365.7314 | 341.7785
945.4729 | 329.0188 | 365.9019 | 341.4345
946.4729 | 329.5471 | 366.4935 | 342.117
947.4729 | 329.5291 | 367.4972 | 341.2543
948.4729 | 328.8804 | 367.9939 | 341.027
949.4729 | 328.7611 | 367.5665 | 340.2562
950.4729 | 329.033 | 366.5467 | 339.3926
951.4729 | 329.4826 | 366.3344 | 338.5297
952.4729 | 329.5887 | 366.1137 | 338.5458
953.4729 | 329.2268 | 365.6379 | 338.1482
954.4729 | 328.6921 | 365.3158 | 337.187
955.4729 | 328.2897 | 364.9588 | 336.1946
956.4729 | 327.4744 | 364.852 | 336.3347
957.4729 | 327.8291 | 365.6736 | 337.0992
958.4729 | 327.4325 | 364.9449 | 337.8387
959.4729 | 326.6241 | 364.9542 | 338.1887
960.4729 | 328.5614 | 365.8521 | 339.4076
961.4729 | 329.0881 | 365.287 | 339.1964
962.4729 | 328.1802 | 364.442 | 339.4942
963.4729 | 327.5836 | 364.0133 | 341.2862
964.4729 | 326.929 | 363.7483 | 341.5234
965.4729 | 326.4863 | 362.8752 | 342.515
966.4729 | 326.6444 | 362.451 | 344.2778
967.4729 | 326.079 | 362.76 | 345.6593
968.4729 | 325.0811 | 363.5651 | 346.4278
969.4729 | 326.2372 | 364.6639 | 346.464
970.4729 | 326.8105 | 365.0914 | 345.9845
971.4729 | 325.9102 | 364.808 | 346.2086
972.4729 | 327.3682 | 366.1405 | 345.8038
973.4729 | 328.0432 | 367.5394 | 345.7871
974.4729 | 327.7663 | 368.4457 | 345.3274
975.4729 | 327.9109 | 369.522 | 345.6866
976.4729 | 327.8101 | 369.4771 | 346.0226
977.4729 | 327.5534 | 368.7268 | 345.3378
978.4729 | 328.2686 | 369.2538 | 344.2261
979.4729 | 328.2054 | 367.9639 | 343.358
980.4729 | 328.8025 | 368.3938 | 342.5875
981.4729 | 329.5266 | 368.3871 | 342.7016
982.4729 | 328.4223 | 367.7685 | 342.7853
983.4729 | 329.2579 | 368.2638 | 343.2104
984.4729 | 329.4642 | 368.0408 | 342.8794
985.4729 | 329.3982 | 368.5746 | 344.0871
986.4729 | 328.3449 | 367.66 | 343.8678
987.4729 | 328.4231 | 368.5061 | 345.2292
988.4729 | 328.1601 | 367.4355 | 345.0331
989.4729 | 327.5613 | 365.8174 | 344.9947
990.4729 | 328.0712 | 366.0697 | 346.0268
991.4729 | 329.4104 | 367.4634 | 345.9453
992.4729 | 329.487 | 367.6669 | 345.2504
993.4729 | 330.1654 | 367.7393 | 345.0921
994.4729 | 329.6307 | 367.5232 | 345.1724
995.4729 | 330.3947 | 366.8574 | 344.797
996.4729 | 330.0769 | 365.9875 | 344.5746
997.4729 | 330.4713 | 365.5065 | 345.0559
998.4729 | 330.291 | 366.0257 | 345.6818
999.4729 | 330.8903 | 366.4507 | 346.4063
1000.4729 | 330.3052 | 366.0273 | 346.928
1001.4729 | 330.9131 | 367.0811 | 346.8141
1002.4729 | 331.0733 | 368.0985 | 346.6167
1003.4729 | 329.9476 | 370.3171 | 347.1444
1004.4729 | 330.7921 | 371.9339 | 346.9633
1005.4729 | 331.5361 | 373.1271 | 347.0584
1006.4729 | 331.2854 | 372.7856 | 346.9579
1007.4729 | 331.4392 | 372.0515 | 347.0585
1008.4729 | 332.2607 | 372.1665 | 346.748
1009.4729 | 332.895 | 372.0813 | 347.0698
1010.4729 | 332.2381 | 372.3034 | 347.5596
1011.4729 | 332.9082 | 371.6251 | 346.779
1012.4729 | 332.652 | 372.1732 | 346.5403
1013.4729 | 332.9406 | 371.5104 | 346.0837
1014.4729 | 333.1409 | 371.277 | 346.5435
1015.4729 | 333.1842 | 371.3137 | 348.4146
1016.4729 | 333.513 | 372.1071 | 348.4462
1017.4729 | 333.9524 | 372.3997 | 348.7793
1018.4729 | 334.2402 | 371.8596 | 348.1379
1019.4729 | 334.4671 | 371.5401 | 348.2564
1020.4729 | 333.2347 | 370.5934 | 347.5492
1021.4729 | 332.4356 | 369.6183 | 347.064
1022.4729 | 330.6008 | 369.6923 | 347.5143
1023.4729 | 330.0175 | 369.553 | 349.374
1024.4729 | 330.0699 | 369.2396 | 349.5123
1025.4729 | 329.9755 | 368.5788 | 349.42
1026.4729 | 329.6495 | 367.4886 | 349.4325
1027.4729 | 328.7505 | 366.9159 | 349.6139
1028.4729 | 328.358 | 366.8663 | 349.6187
1029.4729 | 328.8848 | 366.8112 | 349.2293
1030.4729 | 328.0742 | 365.8951 | 348.1626
1031.4729 | 327.1851 | 364.8494 | 348.5716
1032.4729 | 327.5595 | 364.7545 | 348.7281
1033.4729 | 328.4878 | 363.7004 | 348.9099
1034.4729 | 329.4783 | 363.7404 | 348.7105
1035.4729 | 329.8575 | 363.7477 | 348.2845
1036.4729 | 328.7079 | 363.8668 | 347.7472
1037.4729 | 328.8587 | 365.8183 | 346.64
1038.4729 | 328.6864 | 367.2226 | 346.7498
1039.4729 | 330.3115 | 368.5663 | 348.1975
1040.4729 | 329.6521 | 368.0354 | 347.972
1041.4729 | 329.9105 | 367.729 | 348.2104
1042.4729 | 331.2336 | 367.8726 | 347.9256
1043.4729 | 331.7691 | 367.9226 | 347.2678
1044.4729 | 331.7999 | 370.1596 | 347.5541
1045.4729 | 331.2572 | 369.672 | 347.8637
1046.4729 | 330.7784 | 368.9947 | 348.0045
1047.4729 | 331.7372 | 370.4904 | 353.1447
1048.4729 | 331.5245 | 372.5624 | 354.1561
1049.4729 | 330.74 | 372.2385 | 353.824
1050.4729 | 330.8911 | 372.4938 | 354.5155
1051.4729 | 331.672 | 373.4613 | 355.8857
1052.4729 | 331.7408 | 373.1428 | 354.5403
1053.4729 | 331.5531 | 371.593 | 353.929
1054.4729 | 330.4822 | 371.1873 | 353.234
1055.4729 | 330.4553 | 372.0586 | 353.1086
1056.4729 | 330.4838 | 371.9862 | 353.2164
1057.4729 | 328.7162 | 371.9206 | 353.0399
1058.4729 | 327.7472 | 372.3398 | 353.0637
1059.4729 | 327.5857 | 373.284 | 353.0159
1060.4729 | 328.3522 | 373.7328 | 352.6914
1061.4729 | 327.8678 | 374.1305 | 352.5202
1062.4729 | 328.312 | 373.7166 | 352.0219
1063.4729 | 328.4261 | 373.7331 | 352.4136
1064.4729 | 328.6781 | 373.7959 | 352.7319
1065.4729 | 327.9356 | 373.7338 | 353.6689
1066.4729 | 328.1717 | 373.1519 | 353.7439
1067.4729 | 329.2852 | 375.0301 | 353.4878
1068.4729 | 330.6194 | 378.2045 | 355.0998
1069.4729 | 330.7733 | 378.6116 | 354.4681
1070.4729 | 331.1289 | 379.7336 | 357.265
1071.4729 | 330.0181 | 378.6723 | 357.6924
1072.4729 | 329.7003 | 379.4071 | 356.0718
1073.4729 | 332.0676 | 403.2866 | 357.3555
1074.4729 | 332.0693 | 418.3107 | 358.5861
1075.4729 | 332.2783 | 427.399 | 358.1363
1076.4729 | 331.6102 | 434.5444 | 358.5727
1077.4729 | 330.5405 | 429.8863 | 357.9558
1078.4729 | 330.8296 | 432.2014 | 356.8063
1079.4729 | 333.3197 | 442.0498 | 358.945
1080.4729 | 333.4544 | 441.9121 | 357.4707
1081.4729 | 334.1928 | 440.297 | 358.0677
1082.4729 | 337.6691 | 447.1386 | 363.9378
1083.4885 | 342.5293 | 450.0235 | 364.6206
1084.4729 | 342.9251 | 448.7536 | 363.3206
1085.4729 | 343.6024 | 445.7796 | 362.5759
1086.4729 | 343.8328 | 440.9132 | 361.1843
1087.4729 | 342.9141 | 435.6733 | 360.5209
1088.4729 | 342.8778 | 431.616 | 360.3544
1089.4729 | 342.529 | 431.8901 | 362.612
1090.4729 | 343.0104 | 430.7019 | 362.1379
1091.4729 | 341.4493 | 429.5237 | 363.031
1092.4729 | 342.0521 | 428.0378 | 361.4276
1093.4729 | 341.9907 | 428.366 | 361.308
1094.4729 | 343.1061 | 428.1486 | 361.2867
1095.4729 | 345.1485 | 426.7268 | 360.5511
1096.4729 | 346.45 | 426.7525 | 361.4695
1097.4729 | 347.3839 | 424.6668 | 361.8209
1098.4729 | 347.5765 | 422.5325 | 362.914
1099.4729 | 349.0528 | 421.1603 | 363.8567
1100.4729 | 349.9617 | 420.5036 | 363.7546
1101.4729 | 350.7383 | 418.2471 | 364.6024
1102.4729 | 351.3151 | 417.1631 | 364.7355
1103.4729 | 351.5749 | 416.7568 | 366.941
1104.4729 | 352.1966 | 417.0311 | 368.9112
1105.4729 | 353.8815 | 418.5785 | 369.0015
1106.4729 | 354.9006 | 420.8631 | 369.4244
1107.4729 | 355.0183 | 419.0582 | 368.5251
1108.4729 | 354.6665 | 418.0085 | 369.4883
1109.4729 | 354.4023 | 417.9751 | 371.6784
1110.4729 | 353.7192 | 419.0286 | 373.8523
1111.4729 | 354.3388 | 422.1139 | 376.9221
1112.4729 | 354.671 | 425.3668 | 377.2963
1113.4729 | 356.644 | 433.0479 | 379.6613
1114.4729 | 359.8502 | 440.6172 | 381.173
1115.4729 | 360.8414 | 441.3879 | 381.8505
1116.4729 | 363.176 | 444.3799 | 382.2403
1117.4729 | 362.7824 | 443.824 | 384.0317
1118.4729 | 363.4179 | 442.5074 | 384.8147
1119.4729 | 363.387 | 442.2266 | 386.5319
1120.4729 | 364.1443 | 439.9374 | 386.5499
1121.4729 | 364.285 | 437.5089 | 386.9273
1122.4729 | 362.6554 | 436.2799 | 389.3335
1123.4729 | 364.846 | 442.3175 | 390.5063
1124.4729 | 366.7473 | 445.3803 | 391.0311
1125.4729 | 364.1217 | 444.1457 | 391.8088
1126.4729 | 364.3994 | 443.8001 | 391.5817
1127.4729 | 367.1034 | 457.1011 | 393.4698
1128.4729 | 366.1358 | 473.7567 | 396.7119
1129.4729 | 364.5247 | 476.5133 | 397.3554
1130.4729 | 364.8022 | 475.0376 | 396.2444
1131.4729 | 364.999 | 470.7523 | 395.4023
1132.4729 | 365.508 | 467.9155 | 394.3044
1133.4729 | 365.2062 | 466.4844 | 394.7582
1134.4729 | 365.1181 | 461.5458 | 393.8886
1135.4729 | 365.0158 | 458.5798 | 394.5324
1136.4729 | 365.9365 | 455.5445 | 394.6624
1137.4729 | 367.4504 | 455.7511 | 393.3121
1138.4729 | 366.9367 | 454.8606 | 392.1266
1139.4729 | 367.3134 | 452.1089 | 391.3722
1140.4729 | 366.8057 | 449.14 | 391.7054
1141.4729 | 366.1844 | 446.4782 | 390.773
1142.4729 | 365.9954 | 445.6942 | 392.2973
1143.4729 | 365.1271 | 444.7577 | 392.4668
1144.4729 | 365.1313 | 443.7576 | 391.7224
1145.4729 | 365.338 | 443.5401 | 393.4006
1146.4729 | 366.0569 | 442.4382 | 394.0854
1147.4729 | 365.6836 | 442.4258 | 394.4644
1148.4729 | 365.9274 | 441.1403 | 397.863
1149.4729 | 366.2481 | 443.9879 | 398.5757
1150.4729 | 364.6817 | 441.4324 | 398.7455
1151.4729 | 364.4869 | 442.313 | 403.0852
1152.4729 | 363.2129 | 444.1679 | 403.8704
1153.4729 | 365.2662 | 458.9296 | 411.7501
1154.4729 | 370.1827 | 473.7582 | 415.7538
1155.4729 | 372.9672 | 488.5281 | 419.1918
1156.4729 | 375.7868 | 500.9715 | 419.9117
1157.4729 | 376.7929 | 500.613 | 418.6771
1158.4729 | 376.3486 | 501.4287 | 416.9957
1159.4729 | 377.1726 | 517.7755 | 417.155
1160.4729 | 381.2501 | 529.2411 | 417.7011
1161.4729 | 379.814 | 545.911 | 419.7339
1162.4729 | 380.4674 | 562.2741 | 425.2577
1163.4729 | 382.8337 | 574.1164 | 428.3044
1164.4729 | 381.9812 | 591.2753 | 432.1984
1165.4729 | 382.632 | 601.6695 | 432.271
1166.4729 | 382.558 | 607.9311 | 432.6759
1167.4729 | 381.5148 | 606.424 | 433.6679
1168.4729 | 383.8853 | 616.437 | 435.7482
1169.4729 | 382.892 | 622.589 | 442.9504
1170.4729 | 383.6505 | 615.9275 | 440.5774
1171.4729 | 384.22 | 628.1975 | 443.8711
1172.4729 | 384.7596 | 633.9537 | 445.3993
1173.4729 | 385.4259 | 637.0609 | 446.6856
1174.4729 | 386.1547 | 623.397 | 446.2215
1175.4729 | 387.3622 | 625.4716 | 445.9564
1176.4729 | 392.0623 | 632.8526 | 445.5219
1177.4729 | 392.4223 | 639.6114 | 443.7675
1178.4729 | 395.028 | 642.5655 | 444.6573
1179.4729 | 395.1354 | 646.3223 | 445.5376
1180.4729 | 395.0714 | 652.7718 | 444.3986
1181.4729 | 395.4289 | 664.3584 | 446.3785
1182.4729 | 395.2526 | 654.4649 | 445.382
1183.4729 | 395.9349 | 647.862 | 446.799
1184.4729 | 396.7649 | 640.7908 | 451.843
1185.4729 | 395.9352 | 630.1492 | 454.3596
1186.4729 | 395.2858 | 619.0666 | 453.9963
1187.4729 | 393.724 | 609.0956 | 454.8481
1188.4729 | 392.4242 | 603.7113 | 459.1841
1189.4729 | 391.8705 | 611.4562 | 460.7325
1190.4729 | 392.6793 | 620.889 | 460.7115
1191.4729 | 399.6638 | 630.5796 | 462.7477
1192.4729 | 397.6195 | 636.224 | 467.0573
1193.4729 | 396.2743 | 633.0812 | 466.9333
1194.4729 | 396.5857 | 640.8211 | 467.578
1195.4729 | 394.8558 | 638.1241 | 467.6071
1196.4729 | 393.9859 | 639.2889 | 469.5065
1197.4729 | 395.8157 | 637.9182 | 470.2953
1198.4729 | 396.9967 | 637.2442 | 471.5444
1199.4729 | 397.2453 | 640.1573 | 471.761
1200.4729 | 396.2813 | 638.8345 | 470.1344
1201.4729 | 398.084 | 650.5611 | 470.2763
1202.4729 | 399.4277 | 647.4224 | 471.1588
1203.4729 | 398.1808 | 642.8046 | 470.7206
1204.4729 | 397.2599 | 633.238 | 470.7124
1205.4729 | 397.1622 | 626.8398 | 468.2994
1206.4729 | 397.5343 | 629.3219 | 470.8867
1207.4729 | 396.5714 | 634.5007 | 471.8136
1208.4729 | 397.4501 | 643.002 | 472.1209
1209.4729 | 398.1396 | 642.4717 | 471.1549
1210.4729 | 398.9313 | 647.6791 | 474.5296
1211.4729 | 402.1999 | 644.1117 | 474.0877
1212.4729 | 403.9169 | 640.5819 | 475.7051
1213.4729 | 403.3534 | 648.7725 | 476.4917
1214.4729 | 403.7008 | 651.3953 | 477.6071
1215.4729 | 402.4169 | 648.2177 | 477.4504
1216.4729 | 401.3312 | 638.334 | 476.1946
1217.4729 | 402.2312 | 644.6455 | 473.627
1218.4729 | 404.9479 | 643.2534 | 471.0629
1219.4729 | 405.5509 | 646.4481 | 469.5552
1220.4729 | 405.4795 | 646.1745 | 469.2856
1221.4729 | 409.6385 | 647.4016 | 466.4881
1222.4729 | 407.951 | 639.7876 | 465.4418
1223.4729 | 410.7911 | 640.202 | 473.736
1224.4729 | 410.5369 | 644.1849 | 480.3729
1225.4729 | 410.7839 | 645.3652 | 480.5723
1226.4729 | 413.3942 | 642.7944 | 484.2622
1227.4729 | 415.414 | 656.2421 | 491.0487
1228.4885 | 415.9385 | 654.9104 | 489.0348
1229.4729 | 415.4792 | 650.5884 | 488.6247
1230.4885 | 414.3985 | 659.5035 | 488.7548
1231.4885 | 413.9282 | 660.6821 | 488.3685
1232.4729 | 412.9536 | 667.4461 | 487.3079
1233.4729 | 415.0561 | 669.2203 | 484.9709
1234.4729 | 415.4669 | 666.6627 | 483.4784
1235.4729 | 417.5838 | 668.1791 | 484.8499
1236.4729 | 417.341 | 672.3285 | 485.856
1237.4729 | 417.8638 | 677.3935 | 488.1307
1238.4729 | 418.0899 | 670.2941 | 486.6481
1239.4729 | 419.1775 | 662.0337 | 485.5379
1240.4729 | 422.1292 | 665.2419 | 489.7983
1241.4729 | 424.5579 | 669.7248 | 492.9862
1242.4729 | 427.7795 | 668.901 | 495.8903
1243.4729 | 427.5628 | 658.6762 | 494.4648
1244.4729 | 426.3623 | 658.9817 | 492.501
1245.4729 | 425.7338 | 666.0498 | 496.8143
1246.4729 | 427.6062 | 670.3481 | 498.599
1247.4729 | 433.9243 | 671.9944 | 499.4396
1248.4729 | 433.1464 | 675.9789 | 500.4247
1249.4729 | 432.5342 | 683.0126 | 501.9928
1250.4729 | 432.7443 | 680.5685 | 499.9038
1251.4729 | 437.0012 | 684.8328 | 499.7235
1252.4729 | 434.4497 | 681.0631 | 502.768
1253.4729 | 433.2736 | 666.6827 | 501.77
1254.4729 | 431.4246 | 670.33 | 503.696
1255.4729 | 430.2173 | 662.9422 | 505.9523
1256.4729 | 429.425 | 660.8212 | 509.5567
1257.4729 | 429.2151 | 660.9489 | 515.3191
1258.4729 | 429.4867 | 677.8446 | 514.9939
1259.4729 | 429.2157 | 674.1282 | 514.7316
1260.4729 | 429.3337 | 665.1169 | 514.1222
1261.4729 | 431.0391 | 674.4517 | 520.3499
1262.4729 | 433.9448 | 677.6545 | 522.6919
1263.4885 | 434.6424 | 676.3522 | 522.6452
1264.4729 | 436.3492 | 677.0652 | 521.8936
1265.4729 | 437.3776 | 679.7173 | 524.8278
1266.4729 | 437.1148 | 690.3871 | 528.9006
1267.4729 | 436.8369 | 694.2781 | 529.8736
1268.4729 | 437.1788 | 692.8728 | 529.4291
1269.4729 | 438.7401 | 709.7067 | 536.6156
1270.4729 | 441.1793 | 703.1459 | 538.7618
1271.4729 | 441.0872 | 706.852 | 538.8095
1272.4729 | 441.3111 | 713.1763 | 546.3159
1273.4729 | 445.0893 | 712.356 | 547.7375
1274.4729 | 443.5976 | 714.0489 | 549.1441
1275.4729 | 444.7403 | 710.6591 | 548.0994
1276.4729 | 444.2241 | 703.5028 | 546.4378
1277.4729 | 443.0336 | 702.4746 | 543.8131
1278.4729 | 444.2019 | 709.8649 | 547.224
1279.4729 | 445.0635 | 708.7517 | 548.6275
1280.4729 | 443.6246 | 700.8129 | 548.3299
1281.4729 | 443.7065 | 705.8275 | 550.9723
1282.4729 | 445.0682 | 710.8371 | 548.7593
1283.4729 | 444.5021 | 714.6924 | 547.2422
1284.4729 | 443.67 | 723.7109 | 547.3058
1285.4729 | 445.9264 | 727.6566 | 549.9692
1286.4729 | 445.0886 | 724.1631 | 551.7069
1287.4729 | 445.1691 | 726.5214 | 549.0484
1288.4729 | 447.0278 | 718.5815 | 546.8349
1289.4729 | 446.063 | 713.9277 | 546.5351
1290.4729 | 446.5248 | 710.5669 | 547.6756
1291.4729 | 446.6632 | 696.4446 | 548.803
1292.4729 | 445.1964 | 698.435 | 545.2078
1293.4729 | 445.9941 | 701.7693 | 541.65
1294.4729 | 445.6928 | 706.8233 | 540.2673
1295.4729 | 443.4395 | 705.1122 | 543.0094
1296.4729 | 442.7065 | 699.5072 | 538.5332
1297.4729 | 442.7563 | 696.4601 | 538.5286
1298.4729 | 441.4023 | 700.0932 | 541.3205
1299.4729 | 441.8417 | 695.6547 | 539.2251
1300.4729 | 444.8854 | 701.3763 | 540.7542
1301.4729 | 446.371 | 701.0456 | 540.9116
1302.4729 | 449.4813 | 700.2774 | 540.9884
1303.4729 | 452.2557 | 698.4869 | 540.4452
1304.4729 | 452.153 | 697.6252 | 537.5276
1305.4729 | 455.4808 | 694.3098 | 534.7703
1306.4729 | 457.7784 | 699.6859 | 532.6593
1307.4729 | 457.4988 | 690.9978 | 535.9101
1308.4729 | 459.1431 | 698.5295 | 532.144
1309.4729 | 456.4124 | 705.0148 | 533.9379
1310.4729 | 455.0366 | 707.8119 | 533.8976
1311.4729 | 454.1713 | 698.675 | 531.4306
1312.4729 | 454.7274 | 694.6165 | 545.8128
1313.4729 | 452.0832 | 702.4113 | 543.8541
1314.4729 | 451.1177 | 688.2705 | 539.075
1315.4729 | 457.0112 | 684.8135 | 542.678
1316.4729 | 458.28 | 687.3314 | 545.5672
1317.4729 | 456.9843 | 694.1826 | 545.0091
1318.4729 | 456.389 | 697.975 | 542.652
1319.4729 | 455.9762 | 706.8409 | 547.0183
1320.4729 | 455.6898 | 712.3561 | 546.6017
1321.4729 | 454.773 | 709.4753 | 543.0686
1322.4729 | 454.6555 | 720.4699 | 541.9385
1323.4729 | 453.0446 | 712.7691 | 540.7488
1324.4729 | 452.4788 | 704.3666 | 539.1561
1325.4729 | 451.8223 | 705.1237 | 537.4799
1326.4729 | 450.5324 | 705.189 | 537.0925
1327.4729 | 451.7357 | 707.4445 | 540.3952
1328.4729 | 452.3454 | 701.0565 | 541.3776
1329.4729 | 451.1751 | 694.3389 | 543.1132
1330.4729 | 451.2249 | 699.2123 | 542.5174
1331.4729 | 450.1584 | 700.8844 | 543.8488
1332.4729 | 452.7175 | 715.8884 | 545.3965
1333.4729 | 451.2755 | 709.7301 | 548.2667
1334.4729 | 452.3845 | 712.422 | 545.0064
1335.4729 | 455.3971 | 704.6536 | 542.2826
1336.4729 | 453.6956 | 697.3561 | 543.5751
1337.4729 | 451.5526 | 690.1858 | 543.4615
1338.4729 | 449.931 | 695.3392 | 548.2552
1339.4729 | 448.3815 | 688.6496 | 550.64
1340.4729 | 446.8207 | 679.3311 | 556.5455
1341.4729 | 447.8989 | 681.1225 | 556.9346
1342.4729 | 447.8997 | 703.8733 | 558.6536
1343.4729 | 445.596 | 699.0582 | 561.0964
1344.4729 | 444.7518 | 700.5596 | 561.1762
1345.4729 | 444.7708 | 703.9074 | 560.6581
1346.4729 | 443.6378 | 698.7057 | 556.746
1347.4729 | 443.4686 | 702.8125 | 556.8757
1348.4729 | 442.574 | 707.8334 | 556.4671
1349.4729 | 442.7185 | 706.3048 | 555.9117
1350.4729 | 442.2209 | 714.4456 | 556.0438
1351.4729 | 442.852 | 715.1978 | 552.2656
1352.4729 | 442.86 | 721.1983 | 549.4079
1353.4729 | 444.8371 | 728.4082 | 549.5597
1354.4729 | 443.0073 | 718.0188 | 551.1012
1355.4729 | 442.2519 | 704.2045 | 548.6281
1356.4885 | 439.984 | 697.1363 | 544.7085
1357.4885 | 440.5059 | 684.504 | 542.3645
1358.4729 | 440.6474 | 674.7001 | 546.8611
1359.4729 | 439.3339 | 693.8664 | 557.1003
1360.4729 | 439.5373 | 692.3353 | 562.2633
1361.4885 | 438.4473 | 695.312 | 565.6833
1362.4729 | 438.2683 | 692.0736 | 569.7441
1363.4729 | 437.9505 | 688.214 | 561.7727
1364.4729 | 438.049 | 693.4517 | 557.6376
1365.4729 | 438.2035 | 681.7598 | 555.3255
1366.4729 | 439.0352 | 674.7692 | 550.3321
1367.4729 | 438.6641 | 664.5828 | 545.5984
1368.4729 | 437.6246 | 651.9971 | 542.5939
1369.4729 | 435.626 | 649.7976 | 539.2732
1370.4729 | 440.1398 | 654.3998 | 542.9474
1371.4729 | 440.3577 | 659.187 | 542.0871
1372.4729 | 441.5529 | 673.5951 | 545.3459
1373.4729 | 442.2362 | 669.4305 | 548.0835
1374.4729 | 440.0892 | 660.5541 | 546.4935
1375.4729 | 440.3902 | 667.5873 | 552.9604
1376.4729 | 439.4274 | 657.8345 | 547.3942
1377.4729 | 436.5795 | 650.832 | 543.4711
1378.4729 | 434.5671 | 650.0494 | 549.2808
1379.4729 | 432.7909 | 638.5993 | 548.6574
1380.4729 | 431.3156 | 627.1846 | 544.0408
1381.4729 | 431.543 | 645.7494 | 559.4786
1382.4729 | 431.7853 | 643.3055 | 560.0062
1383.4729 | 430.0814 | 639.8544 | 557.8645
1384.4729 | 430.2661 | 652.9323 | 555.9589
1385.4729 | 430.6152 | 652.1866 | 548.9308
1386.4729 | 431.2063 | 650.9701 | 554.1306
1387.4729 | 430.2198 | 646.2466 | 549.9641
1388.4729 | 430.1567 | 650.4023 | 547.1053
1389.4729 | 430.8602 | 648.8271 | 544.3202
1390.4729 | 430.7898 | 649.528 | 550.4132
1391.4729 | 431.6044 | 648.6118 | 551.3839
1392.4729 | 431.0835 | 640.7536 | 561.9147
1393.4729 | 431.1149 | 656.4526 | 560.998
1394.4729 | 431.707 | 667.5124 | 567.9355
1395.4729 | 432.7421 | 662.1847 | 570.9823
1396.4729 | 431.4336 | 681.5984 | 573.5648
1397.4729 | 431.3091 | 666.0382 | 568.9423
1398.4729 | 431.1647 | 645.6725 | 560.4517
1399.4729 | 431.9223 | 649.7973 | 559.1318
1400.4729 | 433.4979 | 653.9891 | 569.7985
1401.4729 | 433.5773 | 660.6684 | 569.0003
1402.4729 | 432.8809 | 649.4918 | 562.2923
1403.4729 | 432.2391 | 638.1298 | 555.153
1404.4729 | 429.9671 | 629.0047 | 547.6692
1405.4729 | 430.2265 | 634.3271 | 554.4165
1406.4729 | 433.6471 | 641.0438 | 559.4402
1407.4729 | 431.6573 | 629.3055 | 551.1
1408.4729 | 430.2423 | 616.9957 | 545.1117
1409.4729 | 428.9682 | 609.58 | 538.8007
1410.4729 | 428.2051 | 610.7682 | 532.6125
1411.4729 | 426.5665 | 602.0808 | 528.1186
1412.4729 | 427.0996 | 599.1068 | 524.5901
1413.4729 | 425.3208 | 590.5926 | 520.1551
1414.4729 | 424.1663 | 579.9325 | 516.8142
1415.4729 | 422.8103 | 571.1103 | 512.3729
1416.4729 | 421.4213 | 564.5942 | 509.6617
1417.4729 | 420.3198 | 557.4524 | 505.2534
1418.4729 | 419.1734 | 550.3212 | 502.9811
1419.4729 | 423.3197 | 561.1442 | 510.5494
1420.4729 | 424.5273 | 574.5484 | 509.2756
1421.4729 | 422.1816 | 570.7584 | 509.5114
1422.4729 | 422.1135 | 567.0059 | 506.3716
1423.4729 | 421.8627 | 566.2402 | 503.4115
1424.4729 | 423.801 | 575.4002 | 503.2963
1425.4729 | 424.3837 | 572.7497 | 500.1201
1426.4729 | 425.7448 | 578.0611 | 512.2091
1427.4729 | 425.5665 | 572.521 | 507.7121
1428.4729 | 424.652 | 566.6838 | 504.655
1429.4729 | 423.1169 | 579.9159 | 503.1848
1430.4729 | 422.2575 | 576.5737 | 501.348
1431.4729 | 420.8217 | 570.6315 | 499.0879
1432.4729 | 419.2821 | 565.2255 | 495.7903
1433.4729 | 417.8137 | 560.229 | 494.3436
1434.4729 | 416.9386 | 558.4029 | 491.9511
1435.4729 | 415.6895 | 555.2197 | 490.4006
1436.4729 | 415.9099 | 551.2077 | 488.3751
1437.4729 | 414.5404 | 543.3927 | 485.2966
1438.4729 | 415.2041 | 538.1554 | 485.5591
1439.4729 | 413.6574 | 538.2187 | 483.124
1440.4729 | 414.4229 | 535.7502 | 481.4755
1441.4729 | 414.3215 | 532.4987 | 480.2072
1442.4729 | 413.6428 | 529.0072 | 479.8186
1443.4729 | 413.7977 | 523.2501 | 478.6148
1444.4729 | 414.871 | 520.5852 | 476.7788
1445.4729 | 413.9631 | 516.3156 | 474.3779
1446.4729 | 414.742 | 517.5255 | 473.2541
1447.4729 | 414.6814 | 520.1441 | 474.3672
1448.4729 | 414.7844 | 518.4465 | 475.3293
1449.4729 | 413.9305 | 515.52 | 475.3822
1450.4729 | 412.4353 | 512.3286 | 474.8787
1451.4729 | 412.1508 | 507.8692 | 473.3658
1452.4729 | 412.6834 | 503.196 | 471.8523
1453.4729 | 412.6983 | 501.0111 | 469.8267
1454.4729 | 411.0482 | 501.1692 | 469.4758
1455.4729 | 411.6299 | 506.259 | 478.7608
1456.4729 | 411.2643 | 505.8244 | 477.4894
1457.4729 | 410.5673 | 505.835 | 479.1197
1458.4729 | 410.9291 | 508.9323 | 477.1737
1459.4729 | 409.9689 | 505.7476 | 475.8049
1460.4729 | 409.5715 | 502.3722 | 473.8029
1461.4729 | 408.4171 | 499.9622 | 472.6242
1462.4729 | 408.1381 | 502.1277 | 475.0738
1463.4729 | 410.4185 | 507.8517 | 474.8064
1464.4729 | 411.9517 | 519.4773 | 474.9775
1465.4729 | 411.0578 | 523.0666 | 475.4669
1466.4729 | 413.7063 | 529.1299 | 473.519
1467.4729 | 412.5474 | 525.8765 | 472.419
1468.4729 | 412.2325 | 523.2412 | 472.3865
1469.4729 | 410.8836 | 517.096 | 471.6462
1470.4729 | 409.9812 | 527.2891 | 472.6301
1471.4729 | 409.2079 | 522.5806 | 471.4423
1472.4729 | 410.5627 | 518.4687 | 470.0509
1473.4729 | 409.4777 | 512.5951 | 468.5062
1474.4729 | 408.6928 | 508.8822 | 468.9475
1475.4729 | 409.0322 | 512.2992 | 470.1493
1476.4729 | 410.0661 | 520.733 | 470.306
1477.4729 | 408.7863 | 516.4671 | 470.2514
1478.4729 | 409.6822 | 543.0773 | 471.0795
1479.4729 | 408.7485 | 558.3813 | 470.8183
1480.4729 | 408.8254 | 581.4136 | 473.9796
1481.4729 | 408.8853 | 573.4896 | 472.1063
1482.4729 | 409.8392 | 569.4593 | 470.445
1483.4729 | 409.8032 | 562.0807 | 470.2008
1484.4729 | 408.9761 | 552.568 | 467.677
1485.4729 | 407.9478 | 547.9638 | 465.3369
1486.4729 | 407.4998 | 544.0062 | 464.5218
1487.4729 | 409.1041 | 547.1125 | 476.0556
1488.4729 | 409.9236 | 544.2401 | 480.1758
1489.4729 | 409.7776 | 538.8762 | 481.2118
1490.4729 | 412.0147 | 550.7359 | 485.6379
1491.4729 | 413.5177 | 543.5933 | 481.525
1492.4729 | 412.393 | 537.6164 | 478.4321
1493.4729 | 412.9482 | 535.4623 | 476.085
1494.4729 | 413.1368 | 538.4276 | 475.1453
1495.4729 | 413.9286 | 537.6428 | 473.7212
1496.4729 | 414.4903 | 539.0443 | 471.9203
1497.4729 | 413.237 | 535.776 | 471.1377
1498.4729 | 412.5263 | 537.8786 | 469.6419
1499.4729 | 412.412 | 536.0445 | 467.6912
1500.4729 | 413.328 | 550.0216 | 466.3573
1501.4729 | 413.302 | 555.0095 | 471.2432
1502.4729 | 412.8033 | 549.7943 | 469.0672
1503.4729 | 411.992 | 552.1358 | 468.726
1504.4729 | 414.9345 | 556.0903 | 468.6456
1505.4729 | 417.1764 | 548.6541 | 465.6438
1506.4729 | 410.6204 | 548.2782 | 466.7416
1507.4729 | 409.2962 | 544.2844 | 465.474
1508.4729 | 408.8054 | 538.7282 | 464.7308
1509.4729 | 408.8602 | 538.6402 | 463.7745
1510.4729 | 414.564 | 543.7285 | 462.3308
1511.4729 | 412.8882 | 539.7054 | 462.8682
1512.4729 | 412.094 | 536.4188 | 462.1952
1513.4729 | 411.2074 | 529.8213 | 461.4395
1514.4729 | 412.1913 | 523.2924 | 459.8504
1515.4729 | 412.047 | 516.6871 | 458.3683
1516.4729 | 410.5568 | 510.5932 | 456.7574
1517.4729 | 411.3137 | 516.4295 | 458.1813
1518.4729 | 410.6907 | 517.3588 | 462.7543
1519.4729 | 410.6542 | 551.7143 | 462.3165
1520.4729 | 409.4695 | 577.673 | 466.156
1521.4729 | 408.9672 | 590.3149 | 473.9146
1522.4729 | 410.8048 | 615.341 | 478.8248
1523.4729 | 410.3705 | 625.002 | 482.6996
1524.4729 | 410.8855 | 644.5463 | 481.6193
1525.4729 | 411.2539 | 663.2312 | 479.7268
1526.4729 | 412.9133 | 681.6112 | 479.334
1527.4729 | 413.4788 | 697.7927 | 478.6859
1528.4729 | 413.8416 | 703.4459 | 479.9313
1529.4729 | 413.6757 | 698.6139 | 478.4742
1530.4729 | 413.5952 | 706.5028 | 479.2043
1531.4729 | 414.1679 | 707.1072 | 480.2533
1532.4729 | 414.6789 | 713.5176 | 484.8989
1533.4729 | 414.1958 | 712.1664 | 490.4455
1534.4729 | 413.5605 | 719.6077 | 489.6881
1535.4729 | 413.7248 | 715.7593 | 488.9778
1536.4729 | 414.8122 | 693.9445 | 486.241
1537.4729 | 416.6357 | 705.24 | 485.1575
1538.4729 | 417.548 | 709.1047 | 486.9131
1539.4729 | 418.4714 | 719.6512 | 486.7556
1540.4729 | 419.5453 | 723.6917 | 490.6884
1541.4729 | 423.8625 | 707.6103 | 497.1642
1542.4729 | 423.6453 | 689.7499 | 497.8223
1543.4729 | 423.4556 | 703.1031 | 498.4321
1544.4729 | 422.0857 | 715.6892 | 498.0697
1545.4729 | 423.4315 | 717.8768 | 496.3476
1546.4729 | 424.2955 | 712.608 | 495.896
1547.4729 | 427.6592 | 708.9043 | 493.7714
1548.4729 | 428.7907 | 714.4168 | 493.4334
1549.4729 | 428.8322 | 714.0416 | 492.4604
1550.4729 | 429.2948 | 716.4548 | 492.6736
1551.4729 | 432.7136 | 718.8475 | 491.551
1552.4729 | 431.2824 | 721.0169 | 490.6701
1553.4729 | 429.8713 | 733.8109 | 489.7982
1554.4729 | 428.5067 | 744.8621 | 490.381
1555.4729 | 428.0994 | 754.8575 | 490.1017
1556.4729 | 430.2778 | 759.7537 | 491.4443
1557.4729 | 430.7759 | 765.5319 | 494.4769
1558.4729 | 433.2415 | 766.9724 | 491.8915
1559.4729 | 436.8462 | 776.9468 | 494.3051
1560.4729 | 437.2341 | 765.6304 | 494.187
1561.4729 | 441.6291 | 756.3878 | 493.3467
1562.4729 | 444.4956 | 737.9323 | 496.9127
1563.4729 | 446.5516 | 742.2618 | 501.033
1564.4729 | 452.2339 | 747.7647 | 502.9461
1565.4729 | 451.6697 | 751.8313 | 503.9262
1566.4729 | 449.4416 | 761.676 | 504.5708
1567.4729 | 447.9883 | 768.147 | 503.652
1568.4729 | 449.2618 | 774.4062 | 501.5015
1569.4729 | 451.5297 | 776.8843 | 500.7544
1570.4729 | 452.9667 | 771.4411 | 500.6298
1571.4729 | 452.1011 | 760.8853 | 505.7624
1572.4729 | 451.1626 | 769.4941 | 507.7699
1573.4729 | 450.8067 | 774.6469 | 509.0804
1574.4729 | 449.6585 | 773.2682 | 511.6147
1575.4729 | 448.9288 | 775.5801 | 524.3569
1576.4729 | 448.0059 | 762.3143 | 528.792
1577.4729 | 451.4387 | 761.9624 | 524.5929
1578.4729 | 453.0761 | 762.6843 | 529.1214
1579.4729 | 452.6536 | 766.5335 | 524.5706
1580.4729 | 452.8379 | 759.4784 | 520.3597
1581.4729 | 460.4826 | 735.3156 | 516.0195
1582.4729 | 467.6388 | 745.1216 | 518.0597
1583.4729 | 472.995 | 743.7724 | 540.7504
1584.4729 | 469.4628 | 737.8528 | 536.3564
1585.4729 | 466.826 | 740.3891 | 531.4958
1586.4729 | 463.7585 | 741.0879 | 536.6827
1587.4729 | 465.146 | 745.4912 | 531.2881
1588.4729 | 467.8847 | 743.316 | 526.6534
1589.4729 | 476.4219 | 751.8319 | 526.3901
1590.4729 | 477.9161 | 748.9145 | 521.8179
1591.4729 | 476.5592 | 745.1571 | 520.7404
1592.4729 | 474.51 | 753.6013 | 529.2555
1593.4729 | 474.2783 | 758.3611 | 523.6638
1594.4729 | 470.4582 | 757.1638 | 521.0362
1595.4729 | 469.8755 | 763.1892 | 538.0627
1596.4729 | 469.0447 | 768.6029 | 536.2829
1597.4729 | 478.916 | 763.2399 | 531.3526
1598.4729 | 480.2682 | 762.3198 | 546.2025
1599.4729 | 479.8546 | 763.255 | 546.04
1600.4729 | 478.7447 | 761.5654 | 543.4066
1601.4885 | 484.6231 | 759.7601 | 546.5404
1602.4729 | 483.5403 | 752.2249 | 547.3287
1603.4729 | 480.4491 | 756.5066 | 570.6976
1604.4729 | 476.0425 | 738.5285 | 581.2766
1605.4729 | 472.4186 | 718.3163 | 588.5221
1606.4729 | 468.3112 | 699.0076 | 579.4641
1607.4729 | 466.5523 | 678.8813 | 572.105
1608.4729 | 463.2657 | 670.2782 | 583.3062
1609.4729 | 466.0504 | 676.858 | 574.6834
1610.4729 | 465.1634 | 683.1106 | 570.3034
1611.4729 | 462.2759 | 690.6938 | 574.2935
1612.4729 | 479.7288 | 696.8087 | 579.574
1613.4729 | 475.4301 | 711.8836 | 570.091
1614.4729 | 476.2664 | 697.9315 | 562.5029
1615.4729 | 474.5295 | 699.401 | 593.2254
1616.4729 | 476.2664 | 712.1904 | 600.8889
1617.4729 | 473.1807 | 719.122 | 597.2322
1618.4729 | 473.5576 | 720.9319 | 617.4208
1619.4729 | 476.9222 | 719.2206 | 613.5691
1620.4729 | 476.4816 | 702.6632 | 605.0646
1621.4729 | 472.1362 | 683.748 | 594.743
1622.4729 | 469.8494 | 665.0833 | 586.1685
1623.4729 | 466.71 | 646.1627 | 575.0416
1624.4729 | 463.4305 | 631.025 | 565.6323
1625.4729 | 459.7187 | 621.6851 | 560.7001
1626.4729 | 457.1343 | 614.4568 | 552.4709
1627.4729 | 453.7213 | 601.4873 | 544.1099
1628.4729 | 451.0521 | 590.3111 | 538.1467
1629.4729 | 448.4351 | 581.4736 | 532.1196
1630.4729 | 446.9418 | 572.8441 | 526.7719
1631.4729 | 444.923 | 567.1558 | 524.255
1632.4729 | 442.3031 | 560.0164 | 521.2204
1633.4729 | 440.5176 | 556.9421 | 517.002
1634.4729 | 438.4752 | 552.5852 | 514.0081
1635.4729 | 436.6818 | 550.1181 | 509.6311
1636.4729 | 436.4823 | 544.2661 | 505.7229
1637.4729 | 437.6684 | 540.0461 | 508.2412
1638.4729 | 435.1686 | 536.4211 | 518.9387
1639.4729 | 437.1286 | 565.2602 | 517.9138
1640.4729 | 442.6411 | 566.1494 | 515.4724
1641.4729 | 447.5523 | 572.9775 | 515.8862
1642.4729 | 446.4083 | 574.0944 | 515.6915
1643.4729 | 447.6679 | 584.0539 | 511.6838
1644.4729 | 454.1803 | 594.1137 | 508.0997
1645.4729 | 466.134 | 604.1051 | 506.8767
1646.4729 | 477.4293 | 620.9596 | 507.1001
1647.4729 | 474.3531 | 613.7811 | 504.4439
1648.4729 | 473.9082 | 619.2071 | 501.7462
1649.4729 | 477.6298 | 648.6524 | 500.2091
1650.4729 | 492.2929 | 665.2665 | 498.9017
1651.4729 | 503.0659 | 680.4941 | 499.7725
1652.4729 | 503.6144 | 687.9046 | 500.8763
1653.4729 | 498.7837 | 683.2716 | 498.9642
1654.4729 | 497.4151 | 694.5348 | 508.3626
1655.4729 | 495.9224 | 682.4635 | 507.1108
1656.4729 | 498.0594 | 674.3283 | 503.888
1657.4729 | 497.8173 | 688.9537 | 500.5673
1658.4729 | 496.0504 | 689.8443 | 497.7745
1659.4729 | 495.0774 | 689.4383 | 494.986
1660.4729 | 489.8056 | 697.3815 | 494.194
1661.4729 | 487.3913 | 711.5405 | 493.6322
1662.4729 | 485.6555 | 709.5169 | 492.8026
1663.4729 | 485.8868 | 721.5475 | 490.1449
1664.4729 | 482.8043 | 739.0217 | 489.0778
1665.4885 | 490.8393 | 726.9324 | 488.8567
1666.4729 | 498.5483 | 730.6945 | 491.4179
1667.4729 | 506.9078 | 709.5234 | 490.3989
1668.4729 | 525.6848 | 713.182 | 492.0454
1669.4729 | 521.429 | 726.3254 | 490.2419
1670.4729 | 529.5745 | 742.2963 | 502.8546
1671.4729 | 525.4413 | 734.5073 | 499.7001
1672.4729 | 522.3895 | 736.3849 | 496.8159
1673.4729 | 522.744 | 736.2413 | 523.5097
1674.4729 | 528.6271 | 732.1406 | 541.8469
1675.4729 | 535.3609 | 729.0462 | 563.718
1676.4729 | 533.9347 | 731.5302 | 554.4077
1677.4729 | 536.8232 | 728.2724 | 573.7016
1678.4729 | 537.809 | 739.7036 | 562.4543
1679.4729 | 533.6256 | 737.4094 | 559.2072
1680.4729 | 531.3532 | 734.8991 | 561.0599
1681.4729 | 539.0947 | 735.3997 | 559.6627
1682.4729 | 546.2381 | 734.2122 | 551.799
1683.4729 | 540.5237 | 739.2611 | 564.6663
1684.4729 | 530.8955 | 714.4445 | 568.0626
1685.4729 | 531.0824 | 709.1042 | 574.8439
1686.4729 | 528.7357 | 706.5725 | 578.9248
1687.4729 | 529.5251 | 704.4053 | 577.8571
1688.4729 | 532.2556 | 708.5717 | 589.7938
1689.4729 | 526.9253 | 701.0813 | 599.6848
1690.4729 | 536.0826 | 694.1892 | 593.5049
1691.4729 | 544.2136 | 700.3963 | 601.7526
1692.4729 | 551.0202 | 710.863 | 598.4068
1693.4729 | 551.8289 | 721.7305 | 590.9896
1694.4729 | 541.5318 | 734.784 | 583.6973
1695.4885 | 533.9598 | 744.233 | 576.4079
1696.4729 | 530.5199 | 748.6187 | 571.2212
1697.4729 | 555.1275 | 751.0497 | 566.9079
1698.4729 | 555.7474 | 756.0634 | 564.6411
1699.4729 | 562.1168 | 753.2172 | 560.4465
1700.4729 | 574.2514 | 754.646 | 560.2089
1701.4729 | 572.9084 | 754.4636 | 562.047
1702.4729 | 567.8139 | 759.0583 | 561.6343
1703.4729 | 567.7957 | 759.0317 | 557.8563
1704.4729 | 557.5583 | 766.6204 | 554.3775
1705.4729 | 551.7474 | 763.5262 | 552.0765
1706.4729 | 544.8672 | 758.9082 | 557.3691
1707.4729 | 567.8865 | 760.738 | 552.112
1708.4729 | 557.221 | 755.4956 | 547.3182
1709.4729 | 548.9251 | 757.3505 | 543.7473
1710.4729 | 542.9437 | 758.7818 | 543.5702
1711.4729 | 538.1297 | 751.1088 | 554.816
1712.4729 | 536.9751 | 755.9647 | 555.4617
1713.4729 | 543.2384 | 761.6616 | 553.0603
1714.4729 | 540.21 | 766.762 | 552.6202
1715.4729 | 534.024 | 765.9898 | 548.899
1716.4729 | 530.5598 | 773.856 | 542.7485
1717.4729 | 528.0397 | 758.1676 | 538.5596
1718.4729 | 531.3493 | 735.7681 | 535.1896
1719.4729 | 544.7369 | 726.4611 | 535.3432
1720.4729 | 538.499 | 730.9231 | 531.4869
1721.4729 | 552.3897 | 748.507 | 527.8454
1722.4729 | 569.8136 | 756.7473 | 527.3072
1723.4729 | 572.9389 | 756.8591 | 527.6553
1724.4729 | 567.9597 | 760.3174 | 525.6142
1725.4729 | 562.3314 | 764.6089 | 523.6279
1726.4729 | 566.8389 | 753.2085 | 524.5325
1727.4729 | 561.4015 | 750.5775 | 523.5669
1728.4729 | 562.5849 | 749.2564 | 526.1272
1729.4729 | 571.8543 | 748.3394 | 529.7728
1730.4729 | 584.4045 | 752.6601 | 535.6956
1731.4729 | 597.884 | 760.3986 | 541.6251
1732.4729 | 594.9835 | 761.9354 | 543.3959
1733.4729 | 593.7753 | 765.8821 | 538.8895
1734.4729 | 602.8555 | 759.7541 | 552.8977
1735.4729 | 599.3097 | 752.1774 | 553.0537
1736.4729 | 611.1159 | 760.2513 | 558.1642
1737.4729 | 606.0086 | 765.8394 | 556.6903
1738.4729 | 613.155 | 769.3185 | 552.2067
1739.4729 | 625.8438 | 766.406 | 550.7875
1740.4729 | 646.8657 | 770.7888 | 572.723
1741.4729 | 654.9237 | 766.9975 | 587.4729
1742.4729 | 658.1765 | 764.6817 | 600.8547
1743.4729 | 652.7802 | 766.1662 | 599.4037
1744.4729 | 649.0961 | 761.7518 | 591.7314
1745.4729 | 651.4538 | 752.5993 | 604.4456
1746.4729 | 641.1623 | 754.3942 | 611.4023
1747.4729 | 642.3801 | 755.2569 | 614.347
1748.4729 | 651.3188 | 759.9462 | 615.7082
1749.4729 | 649.6475 | 756.1031 | 614.868
1750.4729 | 657.6607 | 759.1022 | 613.5317
1751.4729 | 653.1593 | 755.8423 | 625.9765
1752.4729 | 638.3583 | 757.3967 | 632.2839
1753.4729 | 633.2501 | 759.032 | 639.9941
1754.4729 | 639.6407 | 754.5914 | 643.7676
1755.4885 | 644.7844 | 750.183 | 643.9077
1756.4729 | 633.8202 | 753.0975 | 639.1022
1757.4729 | 645.739 | 751.2216 | 636.6846
1758.4729 | 652.2032 | 750.8881 | 639.7744
1759.4729 | 637.0869 | 756.6501 | 635.6559
1760.4729 | 641.71 | 747.1812 | 647.3657
1761.4729 | 655.0011 | 755.5945 | 655.3776
1762.4729 | 652.1781 | 752.9699 | 656.0632
1763.4729 | 648.4981 | 750.9413 | 645.6814
1764.4729 | 647.6348 | 748.831 | 650.1836
1765.4729 | 643.9133 | 754.9421 | 637.8096
1766.4729 | 644.8722 | 766.1036 | 658.1799
1767.4729 | 657.249 | 759.6211 | 662.019
1768.4729 | 661.2452 | 739.0734 | 659.3407
1769.4729 | 660.1392 | 738.2841 | 654.3592
1770.4729 | 674.0123 | 734.9953 | 660.7006
1771.4729 | 670.0316 | 738.9889 | 659.5445
1772.4729 | 665.8863 | 736.8599 | 668.8034
1773.4729 | 673.7011 | 741.7127 | 664.1431
1774.4729 | 672.947 | 743.9209 | 684.5185
1775.4729 | 670.3856 | 747.1639 | 684.936
1776.4729 | 673.343 | 750.1643 | 691.3024
1777.4729 | 670.8619 | 743.2939 | 700.6836
1778.4729 | 659.1293 | 748.4543 | 705.1875
1779.4729 | 654.0571 | 745.7994 | 696.2581
1780.4729 | 653.1977 | 740.0815 | 690.1851
1781.4729 | 658.8051 | 737.5835 | 703.8036
1782.4729 | 662.1654 | 747.8887 | 696.8136
1783.4729 | 664.8599 | 758.5627 | 682.6954
1784.4729 | 663.9986 | 757.7115 | 687.9331
1785.4729 | 666.2268 | 744.1026 | 689.853
1786.4729 | 668.527 | 742.7906 | 686.4433
1787.4729 | 680.575 | 738.4856 | 678.9424
1788.4729 | 670.4989 | 751.3095 | 662.4169
1789.4729 | 653.6513 | 753.7802 | 664.0369
1790.4729 | 639.6447 | 757.4891 | 662.3783
1791.4729 | 635.7386 | 766.4503 | 648.7247
1792.4729 | 657.9714 | 774.4451 | 644.2852
1793.4729 | 651.2967 | 766.9121 | 649.9653
1794.4729 | 649.1849 | 766.7418 | 659.1615
1795.4729 | 659.9325 | 769.0278 | 665.0767
1796.4729 | 643.4187 | 774.461 | 661.656
1797.4729 | 629.8415 | 777.503 | 649.6224
1798.4729 | 635.6769 | 768.2512 | 648.7799
1799.4729 | 647.9025 | 764.5381 | 644.144
1800.4729 | 655.126 | 766.0596 | 643.6554
1801.4729 | 664.8184 | 774.7412 | 646.2815
1802.4729 | 671.3338 | 767.8659 | 639.0424
1803.4729 | 674.9262 | 765.0952 | 638.6363
1804.4729 | 676.8389 | 769.4833 | 658.629
1805.4729 | 670.4943 | 759.4071 | 652.7761
1806.4729 | 677.2837 | 759.9906 | 653.2308
1807.4729 | 675.1389 | 750.8158 | 653.3676
1808.4729 | 688.2943 | 748.1043 | 654.7873
1809.4729 | 670.1606 | 743.974 | 646.9953
1810.4729 | 665.6979 | 756.1908 | 637.4069
1811.4729 | 668.4598 | 760.2086 | 631.4599
1812.4729 | 673.2032 | 756.1955 | 642.0462
1813.4729 | 673.6379 | 745.6228 | 633.3035
1814.4729 | 677.0492 | 733.3635 | 621.6556
1815.4729 | 683.0766 | 741.9934 | 615.9904
1816.4729 | 682.0594 | 737.2654 | 618.0575
1817.4729 | 685.6176 | 724.8988 | 625.986
1818.4729 | 689.6068 | 731.0987 | 632.6709
1819.4729 | 690.3395 | 738.3721 | 642.6471
1820.4729 | 679.688 | 749.6425 | 643.8137
1821.4729 | 681.4993 | 744.5878 | 645.9498
1822.4729 | 685.637 | 740.2759 | 641.6106
1823.4729 | 693.8815 | 745.721 | 656.5523
1824.4729 | 696.4517 | 754.7286 | 648.9187
1825.4729 | 701.4662 | 764.9432 | 638.5554
1826.4729 | 698.9403 | 766.871 | 643.2927
1827.4729 | 698.8983 | 765.508 | 631.3187
1828.4729 | 705.9608 | 759.7364 | 625.4231
1829.4729 | 702.905 | 746.2622 | 621.2964
1830.4729 | 706.8566 | 744.9162 | 620.296
1831.4729 | 714.8216 | 741.6671 | 620.3754
1832.4729 | 694.6491 | 737.0262 | 624.0313
1833.4729 | 686.4288 | 739.4099 | 621.6613
1834.4729 | 685.5719 | 746.5603 | 619.3968
1835.4729 | 687.8408 | 736.7464 | 616.5198
1836.4729 | 693.4396 | 727.1065 | 636.1436
1837.4729 | 696.971 | 733.6332 | 634.7609
1838.4729 | 688.9303 | 739.1488 | 650.5291
1839.4729 | 691.1932 | 731.6502 | 647.1403
1840.4729 | 697.3739 | 731.9835 | 660.5829
1841.4729 | 688.8876 | 723.3949 | 643.8825
1842.4729 | 685.5445 | 719.4442 | 650.0209
1843.4729 | 680.8484 | 721.1347 | 656.8664
1844.4729 | 690.2745 | 728.819 | 660.9219
1845.4729 | 693.4832 | 727.4175 | 680.2081
1846.4729 | 691.0461 | 731.1384 | 682.5273
1847.4729 | 704.6706 | 732.6243 | 688.2602
1848.4729 | 696.3642 | 736.6183 | 678.6836
1849.4729 | 681.9404 | 738.1365 | 668.2317
1850.4729 | 685.8839 | 748.1333 | 666.7444
1851.4729 | 700.0194 | 750.9454 | 671.795
1852.4729 | 715.2687 | 750.7534 | 667.555
1853.4729 | 717.5137 | 757.4997 | 677.408
1854.4729 | 714.6002 | 756.7701 | 668.9664
1855.4729 | 718.2972 | 743.2121 | 667.7418
1856.4729 | 702.1605 | 735.9123 | 667.1436
1857.4729 | 682.333 | 728.639 | 664.4535
1858.4729 | 679.8758 | 733.3117 | 662.0575
1859.4729 | 684.4183 | 735.1048 | 655.8425
1860.4729 | 686.3699 | 737.1787 | 667.2692
1861.4729 | 678.5593 | 732.5782 | 672.3091
1862.4885 | 685.1053 | 729.918 | 683.2114
1863.4729 | 689.4539 | 728.3841 | 676.5679
1864.4729 | 690.4642 | 729.6837 | 681.6621
1865.4729 | 692.3635 | 735.0008 | 690.2314
1866.4729 | 681.6863 | 738.3543 | 688.8354
1867.4729 | 690.2078 | 739.1053 | 685.2154
1868.4729 | 700.3864 | 723.8942 | 678.9485
1869.4729 | 702.1862 | 726.9538 | 681.9846
1870.4729 | 709.9573 | 730.1804 | 677.0609
1871.4729 | 710.1888 | 723.1934 | 675.6053
1872.4729 | 718.0201 | 705.1924 | 678.0028
1873.4729 | 721.7549 | 701.6649 | 667.3814
1874.4729 | 724.7066 | 708.9491 | 658.5794
1875.4729 | 724.1704 | 708.9822 | 648.6183
1876.4729 | 721.6449 | 709.8204 | 641.3055
1877.4729 | 718.6448 | 712.4346 | 641.8672
1878.4729 | 710.9284 | 701.1839 | 651.438
1879.4729 | 721.4086 | 696.6998 | 657.0939
1880.4729 | 721.4131 | 686.5352 | 658.4979
1881.4729 | 704.664 | 672.822 | 661.1246
1882.4729 | 682.5026 | 673.1725 | 668.726
1883.4729 | 681.1242 | 670.4885 | 673.3657
1884.4729 | 687.9935 | 675.158 | 676.4311
1885.4729 | 671.1773 | 660.0627 | 680.9332
1886.4729 | 657.6191 | 651.7444 | 679.9387
1887.4729 | 643.1301 | 664.1032 | 684.1947
1888.4729 | 629.7371 | 649.6764 | 687.6758
1889.4729 | 616.5448 | 637.6414 | 677.0445
1890.4729 | 605.3674 | 627.2744 | 669.326
1891.4729 | 626.0998 | 630.0016 | 654.0819
1892.4729 | 634.6154 | 632.8923 | 651.3014
1893.4729 | 620.202 | 629.4052 | 649.031
1894.4729 | 627.3459 | 630.658 | 641.1294
1895.4729 | 636.497 | 626.4892 | 637.645
1896.4729 | 639.1081 | 636.6386 | 650.1949
1897.4729 | 634.7954 | 630.4475 | 647.2255
1898.4729 | 620.5915 | 639.6269 | 653.1477
1899.4729 | 626.6706 | 638.1828 | 650.1718
1900.4729 | 650.7679 | 629.0482 | 659.6342
1901.4729 | 664.4373 | 631.8222 | 663.8321
1902.4729 | 663.7897 | 624.7794 | 668.2465
1903.4729 | 678.3273 | 623.5015 | 663.0972
1904.4729 | 677.2931 | 617.9508 | 673.8711
1905.4885 | 688.9891 | 636.3642 | 668.0146
1906.4729 | 696.6974 | 646.9915 | 662.7602
1907.4729 | 695.1101 | 646.4855 | 656.8875
1908.4729 | 705.794 | 644.6548 | 666.8098
1909.4729 | 716.8619 | 637.5575 | 666.8936
1910.4729 | 712.797 | 639.8467 | 670.8913
1911.4729 | 694.0388 | 652.5717 | 675.3904
1912.4729 | 692.9951 | 649.2088 | 691.075
1913.4729 | 682.5896 | 648.4801 | 689.1751
1914.4729 | 685.1683 | 644.7844 | 694.6557
1915.4729 | 692.6349 | 649.5326 | 702.7399
1916.4729 | 700.3271 | 646.4445 | 703.2329
1917.4729 | 715.7978 | 658.6475 | 696.2617
1918.4729 | 716.7267 | 659.0758 | 691.3102
1919.4729 | 719.8309 | 663.9286 | 688.8004
1920.4729 | 704.8952 | 654.8586 | 684.1239
1921.4729 | 711.0376 | 657.436 | 691.438
1922.4729 | 719.4372 | 651.1164 | 689.1629
1923.4729 | 717.5276 | 648.228 | 694.065
1924.4729 | 705.7262 | 650.0305 | 695.3061
1925.4729 | 708.99 | 646.3271 | 693.6652
1926.4729 | 713.5056 | 640.5383 | 693.4335
1927.4729 | 720.9812 | 646.5834 | 684.0933
1928.4729 | 722.4122 | 657.7525 | 678.3799
1929.4729 | 719.1034 | 656.8024 | 678.2145
1930.4729 | 704.451 | 666.2365 | 687.7491
1931.4729 | 690.7106 | 661.0133 | 684.1231
1932.4729 | 706.5039 | 666.3758 | 692.9228
1933.4729 | 701.3806 | 658.1483 | 696.2225
1934.4729 | 713.5431 | 655.92 | 694.8478
1935.4885 | 723.2615 | 654.5683 | 694.4372
1936.4729 | 733.8354 | 656.9077 | 693.0221
1937.4729 | 728.2012 | 676.4911 | 685.8422
1938.4729 | 725.1877 | 688.1626 | 690.1464
1939.4729 | 728.922 | 677.9644 | 693.0888
1940.4885 | 709.7388 | 663.4035 | 680.1421
1941.4885 | 688.5548 | 649.6953 | 668.7315
1942.4729 | 669.8665 | 638.7848 | 663.1829
1943.4729 | 654.1124 | 627.7962 | 659.0972
1944.4729 | 636.9655 | 616.541 | 649.4913
1945.4729 | 634.901 | 609.8344 | 644.065
1946.4729 | 640.2046 | 618.7625 | 645.956
1947.4885 | 659.0038 | 612.5344 | 642.1258
1948.4729 | 669.9562 | 627.9452 | 640.0172
1949.4729 | 679.435 | 640.0006 | 636.0418
1950.4729 | 681.8068 | 648.0099 | 641.1424
1951.4729 | 675.8757 | 658.7129 | 661.5897
1952.4729 | 683.8157 | 666.4434 | 665.9957
1953.4729 | 686.2207 | 673.9438 | 662.0826
1954.4729 | 684.6998 | 680.5662 | 652.7766
1955.4729 | 681.3231 | 690.8559 | 651.5222
1956.4729 | 676.7181 | 702.1899 | 647.2492
1957.4729 | 670.2186 | 705.0956 | 648.3377
1958.4729 | 674.8558 | 694.5292 | 643.5681
1959.4729 | 669.8485 | 701.6415 | 642.1383
1960.4729 | 684.5726 | 701.6332 | 643.6499
1961.4729 | 676.969 | 689.6466 | 659.6536
1962.4729 | 658.858 | 692.9647 | 672.1648
1963.4729 | 669.2191 | 691.3228 | 678.4942
1964.4729 | 674.5532 | 699.2042 | 678.5891
1965.4885 | 671.5237 | 703.8295 | 674.2262
1966.4729 | 682.747 | 709.9537 | 670.2989
1967.4729 | 683.3064 | 705.4776 | 665.6512
1968.4729 | 682.6043 | 707.6228 | 663.1262
1969.4729 | 685.8113 | 700.3053 | 670.9841
1970.4729 | 672.9854 | 687.2201 | 676.4594
1971.4729 | 658.1677 | 671.2976 | 675.3267
1972.4729 | 643.1568 | 663.7438 | 677.5392
1973.4729 | 650.6809 | 678.76 | 683.0019
1974.4729 | 653.1486 | 690.5679 | 685.5679
1975.4729 | 654.4419 | 698.148 | 692.0575
1976.4729 | 661.1653 | 696.9148 | 688.8755
1977.4729 | 646.7416 | 682.6256 | 698.6575
1978.4729 | 659.1244 | 686.7145 | 700.9699
1979.4729 | 668.5019 | 693.3201 | 703.2972
1980.4729 | 664.9691 | 694.6896 | 707.5084
1981.4729 | 670.1321 | 700.3164 | 713.536
1982.4729 | 682.8802 | 698.426 | 703.1246
1983.4885 | 679.0839 | 703.3412 | 695.4745
1984.4729 | 686.2855 | 704.6356 | 690.8522
1985.4729 | 685.13 | 709.0835 | 689.1983
1986.4729 | 696.0579 | 705.556 | 700.0352
1987.4729 | 711.0063 | 699.0377 | 696.7467
1988.4729 | 693.4209 | 699.153 | 694.6046
1989.4729 | 701.9203 | 711.5991 | 687.4456
1990.4729 | 710.6161 | 710.5983 | 693.538
1991.4729 | 704.5248 | 712.0531 | 690.2153
1992.4729 | 708.8165 | 706.9726 | 687.1487
1993.4729 | 717.1252 | 712.0976 | 688.1305
1994.4729 | 714.7392 | 716.7198 | 688.5286
1995.4885 | 707.4671 | 719.2832 | 682.2202
1996.4729 | 708.0539 | 723.946 | 675.9371
1997.4729 | 713.5729 | 725.1182 | 674.8228
1998.4729 | 711.8459 | 715.8774 | 671.93
1999.4729 | 721.5402 | 702.3535 | 665.8405
2000.4729 | 718.2001 | 689.2891 | 670.5077
2001.4729 | 711.2105 | 679.592 | 673.659
2002.4729 | 704.5588 | 671.4876 | 678.1152
2003.4729 | 705.1549 | 678.7521 | 681.865
2004.4729 | 713.6691 | 685.1919 | 683.6398
2005.4729 | 712.6172 | 681.3075 | 685.7067
2006.4729 | 699.887 | 671.9877 | 686.257
2007.4729 | 681.4957 | 658.9875 | 681.0704
2008.4729 | 667.1603 | 647.1429 | 678.1752
2009.4729 | 674.794 | 637.2623 | 678.9625
2010.4729 | 694.4485 | 646.1714 | 701.3827
2011.4729 | 687.0198 | 659.4721 | 700.6619
2012.4729 | 681.0314 | 656.3328 | 706.1894
2013.4729 | 681.8608 | 660.6589 | 702.3747
2014.4729 | 682.1134 | 648.4287 | 697.4187
2015.4729 | 695.2929 | 661.5885 | 699.0149
2016.4729 | 701.2225 | 654.1542 | 701.3205
2017.4729 | 715.5504 | 643.2944 | 700.7179
2018.4729 | 712.2867 | 634.6293 | 701.0349
2019.4729 | 718.9769 | 655.6868 | 703.311
2020.4729 | 721.8535 | 662.4099 | 705.8557
2021.4729 | 727.6636 | 658.2023 | 707.141
2022.4729 | 729.5066 | 652.7828 | 711.6497
2023.4729 | 734.7354 | 662.6177 | 711.5318
2024.4729 | 737.658 | 657.862 | 720.2984
2025.4885 | 744.4941 | 656.4382 | 720.0594
2026.4729 | 727.0956 | 651.0036 | 719.667
2027.4729 | 739.5993 | 669.0347 | 723.8961
2028.4729 | 728.5562 | 671.1241 | 717.7567
2029.4729 | 740.9236 | 687.9365 | 715.532
2030.4729 | 729.4528 | 697.1121 | 709.4996
2031.4729 | 714.0662 | 697.8284 | 714.802
2032.4729 | 716.3338 | 702.281 | 707.4638
2033.4729 | 722.9873 | 712.2455 | 723.5457
2034.4729 | 723.7084 | 717.0042 | 714.4556
2035.4729 | 714.8199 | 719.0275 | 719.5438
2036.4729 | 698.6989 | 720.2804 | 718.9923
2037.4729 | 701.983 | 725.4805 | 711.7774
2038.4729 | 705.4986 | 720.5175 | 717.743
2039.4729 | 708.6578 | 717.854 | 710.1924
2040.4729 | 725.2635 | 697.7552 | 713.4191
2041.4729 | 737.9451 | 702.4185 | 717.4554
2042.4729 | 719.8942 | 689.0606 | 715.3814
2043.4729 | 713.9144 | 671.6828 | 719.5597
2044.4729 | 722.9561 | 677.3595 | 711.6658
2045.4729 | 723.0628 | 677.9051 | 711.4608
2046.4729 | 721.666 | 676.3167 | 707.1335
2047.4729 | 722.6668 | 662.7579 | 704.1488
2048.4729 | 721.7429 | 656.0405 | 701.6214
2049.4729 | 725.6817 | 648.1852 | 710.2728
2050.4729 | 731.9148 | 640.763 | 708.7732
2051.4729 | 734.8838 | 636.3362 | 712.5878
2052.4729 | 740.1353 | 646.5902 | 714.3303
2053.4729 | 731.0058 | 660.6856 | 723.35
2054.4729 | 724.9089 | 660.2904 | 724.549
2055.4729 | 710.1052 | 655.7125 | 729.8415
2056.4729 | 703.5127 | 654.8512 | 734.813
2057.4729 | 711.2672 | 654.7848 | 738.9972
2058.4729 | 722.177 | 664.9935 | 727.1178
2059.4729 | 722.6827 | 674.9548 | 723.4723
2060.4729 | 729.0064 | 676.9184 | 719.507
2061.4729 | 715.1169 | 667.9841 | 718.5865
2062.4729 | 699.242 | 658.8729 | 710.9952
2063.4729 | 708.0426 | 660.6375 | 710.1687
2064.4729 | 708.9818 | 671.1713 | 714.4712
2065.4729 | 707.0382 | 678.8364 | 713.2748
2066.4729 | 707.3812 | 687.6098 | 718.1823
2067.4729 | 713.5304 | 676.5652 | 724.6576
2068.4729 | 717.43 | 672.5148 | 725.8717
2069.4729 | 700.4198 | 659.6926 | 728.918
2070.4729 | 695.0528 | 660.9343 | 735.9761
2071.4729 | 697.893 | 655.7851 | 728.0684
2072.4729 | 700.4587 | 649.8726 | 730.2349
2073.4729 | 702.8188 | 649.8986 | 731.3062
2074.4729 | 709.3102 | 650.2214 | 722.7507
2075.4729 | 716.6947 | 648.081 | 713.0113
2076.4729 | 724.5863 | 645.381 | 715.4789
2077.4729 | 729.6274 | 636.481 | 722.0964
2078.4729 | 727.1312 | 643.9327 | 725.2305
2079.4729 | 713.8136 | 637.1905 | 727.2936
2080.4729 | 695.1137 | 635.2681 | 735.3743
2081.4729 | 706.3758 | 631.7375 | 726.1818
2082.4729 | 693.3867 | 624.6999 | 731.0663
2083.4729 | 675.3285 | 621.4373 | 736.6588
2084.4729 | 680.2751 | 616.2504 | 734.088
2085.4729 | 684.2125 | 616.3184 | 738.7751
2086.4729 | 686.6334 | 613.623 | 746.108
2087.4729 | 688.8336 | 630.9813 | 749.959
2088.4729 | 691.7488 | 632.6024 | 742.8369
2089.4729 | 684.3163 | 627.9585 | 741.662
2090.4729 | 699.1127 | 641.6658 | 735.8182
2091.4729 | 696.9523 | 636.0273 | 734.5568
2092.4729 | 704.3783 | 645.528 | 738.9158
2093.4729 | 714.8572 | 648.2016 | 738.2087
2094.4729 | 704.8671 | 643.0764 | 731.6423
2095.4729 | 686.3076 | 632.4944 | 726.7359
2096.4729 | 670.1289 | 630.332 | 732.4476
2097.4729 | 677.297 | 628.4923 | 736.4241
2098.4729 | 670.6758 | 625.3932 | 734.4629
2099.4729 | 655.9952 | 620.4642 | 720.9111
2100.4729 | 655.219 | 615.4773 | 716.5393
2101.4729 | 649.4063 | 613.2223 | 721.8863
2102.4729 | 640.0335 | 608.6389 | 731.7877
2103.4729 | 630.4369 | 604.2124 | 734.0575
2104.4729 | 626.8397 | 598.2403 | 728.4432
2105.4729 | 622.8634 | 595.0261 | 715.669
2106.4729 | 628.0133 | 594.7366 | 718.0388
2107.4729 | 640.5934 | 596.7859 | 727.5592
2108.4729 | 650.0594 | 595.6929 | 735.1221
2109.4729 | 640.7119 | 595.1556 | 739.3188
2110.4729 | 629.5631 | 592.0856 | 737.6157
2111.4729 | 618.7352 | 589.2715 | 731.6375
2112.4729 | 609.8281 | 604.9663 | 723.4272
2113.4729 | 636.535 | 612.9754 | 711.4643
2114.4729 | 647.0849 | 607.3043 | 703.2928
2115.4729 | 652.3899 | 603.8592 | 710.1193
2116.4729 | 658.6429 | 604.1335 | 706.4559
2117.4729 | 679.0651 | 606.5398 | 705.96
2118.4729 | 689.4768 | 602.4768 | 703.4685
2119.4729 | 681.1983 | 598.3036 | 720.0578
2120.4729 | 670.1767 | 594.274 | 732.9257
2121.4729 | 664.4201 | 592.9469 | 745.1525
2122.4729 | 660.3607 | 591.3016 | 732.7692
2123.4729 | 651.8994 | 588.7845 | 739.1322
2124.4729 | 651.3972 | 585.917 | 739.8188
2125.4729 | 638.7582 | 581.1861 | 736.8042
2126.4729 | 630.2771 | 578.1221 | 741.7384
2127.4729 | 625.1367 | 573.3254 | 728.1896
2128.4729 | 623.8625 | 570.8736 | 715.6672
2129.4729 | 621.8518 | 569.9287 | 717.2423
2130.4729 | 630.5529 | 570.5307 | 718.8199
2131.4729 | 634.2453 | 574.457 | 728.2028
2132.4729 | 650.4342 | 577.8643 | 732.1191
2133.4729 | 661.4916 | 578.3309 | 717.017
2134.4729 | 673.5126 | 576.6618 | 719.424
2135.4729 | 682.2119 | 577.0286 | 726.052
2136.4729 | 683.6097 | 576.0877 | 731.2911
2137.4729 | 677.3414 | 575.9795 | 738.1079
2138.4729 | 697.5905 | 574.5616 | 737.7321
2139.4729 | 696.4311 | 575.0318 | 738.0246
2140.4729 | 683.1575 | 575.0293 | 741.6459
2141.4729 | 669.543 | 574.1841 | 723.6002
2142.4729 | 678.8052 | 573.2949 | 740.8374
2143.4729 | 663.0901 | 571.9528 | 743.9622
2144.4729 | 657.4291 | 571.8557 | 734.8951
2145.4729 | 650.6698 | 568.8677 | 731.9741
2146.4729 | 642.893 | 565.738 | 714.3412
2147.4729 | 636.6704 | 565.4972 | 703.713
2148.4729 | 626.4763 | 563.8292 | 708.8075
2149.4729 | 616.7268 | 563.5318 | 713.9327
2150.4729 | 616.4421 | 562.9286 | 700.2232
2151.4729 | 618.8363 | 564.2989 | 707.5529
2152.4729 | 609.8683 | 563.173 | 709.8581
2153.4729 | 606.6667 | 561.8611 | 709.9208
2154.4729 | 624.1125 | 562.2697 | 705.7592
2155.4729 | 637.4675 | 560.0919 | 698.2324
2156.4729 | 641.6875 | 557.8825 | 686.2147
2157.4729 | 643.689 | 555.8881 | 679.1776
2158.4729 | 641.4537 | 555.0363 | 666.3149
2159.4729 | 638.8919 | 556.9263 | 673.2092
2160.4729 | 656.173 | 562.9608 | 678.4811
2161.4729 | 645.1457 | 563.837 | 668.4463
2162.4729 | 636.1532 | 563.5392 | 681.8148
2163.4729 | 636.4077 | 562.778 | 690.0235
2164.4729 | 628.3738 | 561.1492 | 682.2615
2165.4729 | 618.6187 | 557.7707 | 667.8586
2166.4729 | 608.6591 | 555.034 | 654.6829
2167.4729 | 599.7889 | 553.0085 | 666.0949
2168.4729 | 591.2752 | 551.4648 | 673.1126
2169.4729 | 587.3377 | 551.0268 | 665.4676
2170.4729 | 584.1532 | 549.3237 | 679.76
2171.4729 | 578.734 | 548.1761 | 684.5707
2172.4729 | 576.3834 | 548.3564 | 684.8603
2173.4729 | 594.0902 | 550.1308 | 685.4545
2174.4729 | 614.2733 | 550.1064 | 688.8256
2175.4729 | 628.5026 | 549.3699 | 698.3973
2176.4729 | 642.6722 | 550.348 | 711.303
2177.4729 | 641.4307 | 551.0276 | 718.9605
2178.4729 | 650.4857 | 552.6937 | 715.156
2179.4729 | 653.9636 | 552.6238 | 718.672
2180.4729 | 674.4889 | 551.8231 | 716.0521
2181.4729 | 686.5238 | 550.6601 | 708.1258
2182.4729 | 681.4902 | 550.1122 | 706.8374
2183.4729 | 686.1886 | 549.4649 | 695.4345
2184.4729 | 673.3297 | 548.5943 | 680.4014
2185.4729 | 662.9892 | 546.9137 | 668.0262
2186.4729 | 650.8151 | 546.6836 | 660.8294
2187.4729 | 650.7111 | 547.1552 | 653.2197
2188.4729 | 658.536 | 547.162 | 645.2587
2189.4729 | 662.7491 | 547.1363 | 638.7294
2190.4729 | 654.6057 | 546.4474 | 634.7179
2191.4729 | 649.5533 | 546.908 | 632.1546
2192.4729 | 648.535 | 546.602 | 648.8588
2193.4729 | 653.899 | 548.9147 | 644.6514
2194.4729 | 656.996 | 550.7161 | 652.8208
2195.4729 | 651.566 | 548.8389 | 666.9391
2196.4729 | 642.217 | 548.2771 | 663.8988
2197.4729 | 642.7064 | 547.9205 | 656.7148
2198.4729 | 637.6728 | 547.2572 | 652.5174
2199.4729 | 656.1747 | 548.507 | 658.1124
2200.4729 | 653.3399 | 550.3674 | 647.3774
2201.4729 | 643.703 | 549.5719 | 654.4544
2202.4729 | 645.9734 | 550.4517 | 660.0784
2203.4729 | 641.311 | 551.7776 | 668.9467
2204.4729 | 630.205 | 549.6204 | 664.8323
2205.4729 | 621.0918 | 547.5115 | 656.012
2206.4729 | 612.1969 | 546.5945 | 661.2684
2207.4729 | 605.1618 | 546.6931 | 662.9355
2208.4729 | 598.4824 | 548.4585 | 653.375
2209.4729 | 590.3403 | 547.102 | 652.7228
2210.4729 | 589.4842 | 547.5287 | 673.4503
2211.4729 | 599.2764 | 548.2383 | 675.5845
2212.4729 | 603.4207 | 548.2261 | 668.3202
2213.4729 | 610.6889 | 546.9092 | 681.1484
2214.4729 | 618.7502 | 545.1743 | 687.3411
2215.4729 | 625.7869 | 543.4905 | 694.8727
2216.4729 | 622.905 | 542.2319 | 695.0335
2217.4729 | 625.1441 | 541.8693 | 679.5995
2218.4729 | 638.6278 | 540.8849 | 684.412
2219.4729 | 629.5124 | 541.3671 | 682.0936
2220.4729 | 636.3791 | 541.8741 | 677.2018
2221.4729 | 638.7235 | 545.4618 | 666.2185
2222.4729 | 628.078 | 544.6294 | 663.1981
2223.4729 | 618.384 | 542.6734 | 665.8665
2224.4729 | 611.1636 | 542.3927 | 669.1548
2225.4729 | 617.5113 | 544.7599 | 659.7623
2226.4729 | 620.7697 | 547.5938 | 655.3125
2227.4729 | 630.8579 | 551.2856 | 653.5023
2228.4729 | 637.981 | 551.8528 | 643.202
2229.4729 | 626.1813 | 550.7791 | 634.3209
2230.4729 | 642.0191 | 550.6909 | 644.1528
2231.4729 | 647.4766 | 551.3029 | 645.7193
2232.4729 | 638.3395 | 551.2383 | 649.5165
2233.4729 | 635.6781 | 550.3378 | 647.2172
2234.4729 | 630.8497 | 550.1562 | 637.664
2235.4729 | 630.4898 | 549.1652 | 628.6167
2236.4729 | 619.5257 | 547.4316 | 620.4844
2237.4729 | 617.3627 | 549.06 | 615.1449
2238.4729 | 629.6218 | 547.2772 | 611.1352
2239.4729 | 625.0744 | 545.8409 | 616.2345
2240.4729 | 617.9635 | 542.2141 | 608.4696
2241.4729 | 625.7623 | 540.4039 | 600.9811
2242.4729 | 631.15 | 540.3894 | 595.0063
2243.4729 | 633.0939 | 540.681 | 590.6559
2244.4729 | 644.3673 | 539.3508 | 586.3809
2245.4729 | 636.7245 | 539.1752 | 581.9672
2246.4729 | 642.1918 | 538.7405 | 577.5572
2247.4729 | 649.3681 | 537.7091 | 573.46
2248.4729 | 655.2852 | 539.5196 | 584.3353
2249.4729 | 659.7076 | 542.2809 | 591.8589
2250.4729 | 656.3826 | 542.9197 | 595.9794
2251.4729 | 661.0951 | 543.3104 | 593.0545
2252.4729 | 665.6424 | 545.1453 | 588.7266
2253.4729 | 658.4237 | 546.5977 | 592.7206
2254.4729 | 646.9487 | 546.095 | 588.6316
2255.4729 | 635.5887 | 547.4298 | 585.2268
2256.4729 | 638.3104 | 547.3772 | 582.6939
2257.4729 | 628.512 | 545.9567 | 596.7603
2258.4729 | 623.3333 | 545.5229 | 598.7875
2259.4729 | 631.0974 | 545.9708 | 601.9849
2260.4729 | 635.3656 | 547.5003 | 605.0798
2261.4729 | 642.5566 | 546.6607 | 600.6673
2262.4729 | 634.4264 | 546.5114 | 599.1659
2263.4729 | 638.1034 | 547.0983 | 604.5139
2264.4729 | 647.4807 | 546.1051 | 606.5369
2265.4729 | 634.8904 | 543.812 | 607.4937
2266.4729 | 634.2306 | 542.3355 | 612.8195
2267.4729 | 645.3442 | 542.9161 | 613.9155
2268.4729 | 647.545 | 544.0721 | 630.6781
2269.4729 | 639.6918 | 543.0106 | 635.0943
2270.4729 | 634.8667 | 543.1969 | 631.9413
2271.4729 | 630.4285 | 544.7451 | 630.3316
2272.4729 | 628.4985 | 544.7424 | 624.8101
2273.4729 | 624.5409 | 545.0514 | 618.9383
2274.4729 | 620.3705 | 547.6765 | 612.7484
2275.4729 | 624.5253 | 550.4424 | 613.7735
2276.4729 | 620.8578 | 550.8615 | 609.6619
2277.4729 | 616.1115 | 549.2873 | 616.2497
2278.4729 | 630.4242 | 547.5585 | 608.305
2279.4729 | 627.5509 | 544.7602 | 601.0123
2280.4729 | 627.5785 | 542.1781 | 594.2122
2281.4729 | 622.837 | 541.1685 | 588.4994
2282.4729 | 619.9814 | 540.2079 | 583.6811
2283.4729 | 613.9625 | 539.7445 | 580.0164
2284.4729 | 611.3362 | 540.336 | 581.0006
2285.4729 | 616.2217 | 540.1782 | 597.9462
2286.4729 | 622.7607 | 540.0496 | 594.2299
2287.4729 | 632.2388 | 538.2134 | 589.2868
2288.4729 | 623.1791 | 537.1897 | 584.3669
2289.4729 | 620.7597 | 537.97 | 583.5747
2290.4729 | 620.3533 | 537.9027 | 581.0499
2291.4729 | 621.6807 | 537.1594 | 592.1517
2292.4729 | 618.0668 | 536.232 | 605.3756
2293.4729 | 612.7034 | 536.0799 | 599.2341
2294.4729 | 610.997 | 535.1388 | 599.4136
2295.4729 | 607.2769 | 534.5414 | 594.2283
2296.4729 | 617.678 | 537.5652 | 615.1446
2297.4729 | 616.7761 | 537.3675 | 608.6626
2298.4729 | 623.8977 | 536.566 | 602.5155
2299.4729 | 629.2158 | 536.009 | 597.1448
2300.4729 | 632.5934 | 535.7686 | 591.1839
2301.4729 | 630.381 | 534.9803 | 584.9306
2302.4729 | 629.5302 | 536.2751 | 580.2037
2303.4729 | 618.9707 | 534.1848 | 576.4897
2304.4729 | 610.3137 | 532.5458 | 572.0799
2305.4729 | 611.4248 | 533.0166 | 570.2224
2306.4729 | 618.0778 | 532.8729 | 571.5
2307.4729 | 614.7794 | 533.1022 | 574.589
2308.4729 | 640.7433 | 532.1216 | 583.3949
2309.4729 | 642.4404 | 532.9531 | 589.0932
2310.4729 | 630.7942 | 534.3247 | 587.2573
2311.4729 | 641.6923 | 533.2246 | 588.1997
2312.4729 | 642.291 | 531.9773 | 596.5436
2313.4729 | 638.9499 | 531.2382 | 596.9255
2314.4729 | 626.7036 | 530.2074 | 598.0094
2315.4729 | 616.3061 | 529.3494 | 591.8199
2316.4729 | 613.555 | 529.0759 | 589.7228
2317.4729 | 617.594 | 529.3047 | 600.4814
2318.4729 | 630.2729 | 530.0539 | 600.1341
2319.4729 | 620.9495 | 529.9302 | 594.5388
2320.4729 | 618.2297 | 530.234 | 589.7712
2321.4729 | 610.877 | 529.958 | 583.6516
2322.4729 | 606.2149 | 530.0599 | 577.1734
2323.4729 | 605.5748 | 529.2482 | 572.0339
2324.4729 | 622.3607 | 529.9238 | 593.7601
2325.4729 | 628.3981 | 529.3017 | 594.6625
2326.4729 | 630.7283 | 528.228 | 589.5639
2327.4729 | 634.4494 | 529.0088 | 584.3424
2328.4729 | 628.985 | 530.2041 | 580.3063
2329.4729 | 632.0618 | 530.6446 | 586.6818
2330.4729 | 646.0992 | 531.4529 | 591.0549
2331.4729 | 649.9326 | 531.414 | 583.9648
2332.4729 | 642.8731 | 531.7496 | 578.3318
2333.4729 | 638.7334 | 532.6287 | 573.1933
2334.4729 | 631.9031 | 532.328 | 568.7416
2335.4729 | 625.6692 | 532.1317 | 563.8597
2336.4729 | 621.247 | 532.2093 | 560.5397
2337.4729 | 632.7793 | 534.3751 | 562.4065
2338.4729 | 625.9708 | 535.0827 | 568.3407
2339.4729 | 634.2715 | 535.8819 | 572.071
2340.4729 | 642.5119 | 536.2841 | 570.0703
2341.4729 | 640.9413 | 536.9355 | 567.6555
2342.4729 | 634.6362 | 540.0503 | 565.1265
2343.4729 | 626.2342 | 537.8512 | 565.7764
2344.4729 | 623.3381 | 535.5109 | 568.1456
2345.4729 | 633.7399 | 535.4787 | 572.631
2346.4729 | 631.6007 | 535.016 | 580.585
2347.4729 | 629.9648 | 533.793 | 576.3577
2348.4729 | 627.5226 | 532.5239 | 574.8835
2349.4729 | 624.5479 | 533.9831 | 576.0546
2350.4729 | 644.981 | 536.187 | 581.1469
2351.4729 | 632.8995 | 535.7693 | 595.2058
2352.4729 | 626.6886 | 533.8396 | 594.0749
2353.4729 | 632.5154 | 533.5992 | 595.5204
2354.4729 | 636.2347 | 533.6077 | 591.7151
2355.4729 | 636.1369 | 536.5542 | 599.4679
2356.4729 | 627.968 | 534.375 | 602.7639
2357.4729 | 619.1868 | 531.9427 | 594.6184
2358.4729 | 620.116 | 529.5581 | 592.3556
2359.4729 | 637.8041 | 528.8777 | 590.032
2360.4729 | 633.8777 | 527.5528 | 585.3562
2361.4729 | 624.0034 | 525.8356 | 578.9002
2362.4729 | 629.7336 | 527.4643 | 572.5218
2363.4729 | 634.576 | 529.2141 | 568.1451
2364.4729 | 626.0039 | 530.3995 | 564.9012
2365.4729 | 627.4141 | 528.3659 | 561.5907
2366.4729 | 619.4484 | 527.1203 | 558.2932
2367.4729 | 608.3831 | 527.0582 | 554.8961
2368.4729 | 612.7468 | 526.6181 | 553.4254
2369.4729 | 616.1954 | 527.2502 | 551.2547
2370.4729 | 615.4925 | 527.9772 | 549.2168
2371.4729 | 624.3777 | 529.0531 | 548.0332
2372.4729 | 626.0279 | 530.9051 | 547.2382
2373.4729 | 624.1279 | 529.5013 | 545.3909
2374.4729 | 625.2937 | 528.5289 | 543.9906
2375.4729 | 619.297 | 528.2692 | 542.5923
2376.4729 | 617.394 | 527.3927 | 540.5162
2377.4729 | 628.599 | 527.2193 | 538.2873
2378.4729 | 625.4991 | 529.396 | 536.8238
2379.4729 | 621.9844 | 529.2609 | 535.1759
2380.4729 | 620.5148 | 528.8955 | 534.3296
2381.4729 | 613.7257 | 529.4797 | 533.775
2382.4729 | 624.4793 | 528.3066 | 532.7941
2383.4729 | 620.3959 | 527.3261 | 531.2702
2384.4729 | 614.8383 | 527.7803 | 535.3406
2385.4729 | 614.1643 | 529.4475 | 541.9996
2386.4729 | 615.9308 | 528.5993 | 538.7464
2387.4729 | 613.52 | 528.2099 | 546.8377
2388.4729 | 623.7156 | 529.1029 | 548.1812
2389.4729 | 614.8742 | 528.5158 | 549.6223
2390.4729 | 606.8134 | 527.5117 | 546.757
2391.4729 | 605.3818 | 529.551 | 544.0496
2392.4729 | 604.3224 | 529.5649 | 545.5757
2393.4729 | 599.9317 | 529.6813 | 548.0635
2394.4729 | 603.4394 | 528.5331 | 545.7607
2395.4729 | 606.6652 | 527.9115 | 544.6245
2396.4729 | 611.2152 | 526.5978 | 543.1699
2397.4729 | 607.2322 | 525.8227 | 541.0855
2398.4729 | 603.8809 | 525.5171 | 539.1503
2399.4729 | 615.9613 | 524.8822 | 537.1902
2400.4729 | 605.527 | 524.44 | 534.9747
2401.4885 | 599.3372 | 525.9879 | 534.5067
2402.4729 | 602.299 | 525.77 | 534.9557
2403.4729 | 603.5058 | 526.5702 | 533.9212
2404.4729 | 600.8182 | 527.2581 | 532.215
2405.4729 | 595.8133 | 528.4011 | 531.2685
2406.4729 | 590.3132 | 527.853 | 530.5219
2407.4729 | 595.8028 | 527.4449 | 532.9322
2408.4729 | 589.191 | 525.556 | 531.3968
2409.4729 | 588.4477 | 524.9205 | 530.3447
2410.4729 | 595.15 | 524.9147 | 528.829
2411.4729 | 610.7309 | 527.2561 | 527.5378
2412.4729 | 611.4646 | 528.6503 | 528.6529
2413.4729 | 607.9999 | 530.9806 | 529.2884
2414.4729 | 619.0215 | 528.8118 | 530.7729
2415.4729 | 621.7132 | 527.9408 | 531.0279
2416.4729 | 628.5063 | 528.4551 | 531.814
2417.4729 | 625.9686 | 527.7266 | 534.6583
2418.4729 | 618.8306 | 528.4135 | 533.6684
2419.4729 | 612.9258 | 529.4869 | 531.6359
2420.4729 | 618.7936 | 528.9342 | 535.3463
2421.4729 | 623.943 | 527.4732 | 533.3414
2422.4729 | 616.1168 | 527.3967 | 531.8746
2423.4729 | 615.6867 | 529.0686 | 530.5216
2424.4729 | 615.6185 | 527.9192 | 528.4635
2425.4729 | 605.7659 | 526.3659 | 526.8788
2426.4729 | 603.9044 | 525.7354 | 526.1685
2427.4729 | 599.1246 | 524.9363 | 525.1164
2428.4729 | 592.179 | 526.6044 | 524.25
2429.4729 | 597.2383 | 527.6649 | 523.1773
2430.4729 | 591.3233 | 529.3646 | 521.7112
2431.4729 | 603.3017 | 528.3213 | 520.8877
2432.4729 | 612.1374 | 527.9187 | 520.5369
2433.4729 | 613.8987 | 526.1815 | 520.1948
2434.4729 | 603.0413 | 524.4875 | 519.4307
2435.4729 | 599.0211 | 525.4303 | 519.8311
2436.4729 | 608.1127 | 527.9238 | 520.1896
2437.4729 | 600.034 | 528.1553 | 520.1479
2438.4729 | 597.6307 | 531.5782 | 520.6636
2439.4729 | 597.5707 | 534.3572 | 521.8292
2440.4729 | 596.8885 | 534.7558 | 522.3397
2441.4729 | 597.0891 | 534.7123 | 523.6776
2442.4729 | 597.3112 | 536.6422 | 533.0504
2443.4729 | 608.045 | 537.0924 | 530.7906
2444.4729 | 606.5804 | 537.5948 | 533.4638
2445.4729 | 603.4652 | 538.6503 | 539.3746
2446.4729 | 604.6582 | 537.9779 | 536.2829
2447.4729 | 598.6709 | 535.3067 | 533.655
2448.4729 | 613.6856 | 533.7011 | 534.9659
2449.4729 | 604.6581 | 532.7679 | 535.8738
2450.4729 | 597.8495 | 531.2837 | 534.543
2451.4729 | 598.3672 | 531.5242 | 532.5203
2452.4729 | 608.6974 | 532.048 | 536.4735
2453.4729 | 612.5427 | 532.0132 | 544.9157
2454.4729 | 608.0522 | 530.6474 | 541.7564
2455.4729 | 600.3791 | 528.5465 | 538.684
2456.4729 | 596.555 | 527.7862 | 537.5634
2457.4729 | 599.6134 | 526.5353 | 537.8145
2458.4729 | 592.3379 | 525.5864 | 536.7139
2459.4729 | 593.1481 | 524.8698 | 534.9843
2460.4729 | 587.5086 | 524.6255 | 533.2583