## Test Conditions
DESIREE-FIRE Intermediate Scale Test Number 6 - Circuit Simulator Data Only
Test Date: | 2010-03-03
DCSim DAQ Start Time | 13:38
DCSim Time for Synchronization | 14:06
Heat Source Synchronization | 0:00 | hour:minutes:seconds
Heat Source DAQ Start Time | 14:05
Heat Source Start Time | 14:34
DCSim Offset | 0:56 | hour:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 3360 | seconds
Heat Source Offset | 0:29 | hour:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 1740 | seconds
Heat Source Stop Time | 15:15
Test Duration | 0:41 | hour:minutes:seconds
| 2460 | seconds
CT500 Turns | 2 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 Turns | 5 | 1 or 5
Pre-Test Baseline: | Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
SWGR Close | PE/PVC, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 2, 3, and 4 represents the conduit temperature 3', 5', and 7' down the conduit located in B Position. These are labeled as "B Position - Conduit - 3'", "B Position - Conduit - Middle", " B Position - Conduit - 7'", respectively.
SWGR Trip | PE/PVC, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 2, 3, and 4 represents the conduit temperature 3', 5', and 7' down the conduit located in B Position. These are labeled as "B Position - Conduit - 3'", "B Position - Conduit - Middle", " B Position - Conduit - 7'", respectively.
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | SWGR_CT500 | SWGR-a_CT35_1_PC | SWGR-a_CT35_2_N1 | SWGR-b_CT35_1_PT | SWGR-b_CT35_2_G | SWGR-b_CT35_3_R | SWGR-b_CT35_4_N2 | SWGR-a_VT7_1_C1 | SWGR-a_VTU_1_PC | SWGR-a_VTU_2_N1 | SWGR-b_VT7_1_G | SWGR-b_VT7_2_R | SWGR-b_VT7_3_T | SWGR-b_VT7_4_SP | SWGR-b_VT7_5_SP | SWGR-b_VTU_1_PT | SWGR-b_VTU_2_N2 | {SWGR-C} V(N1) - V(Batt -) | {SWGR-C} V(PC) - V(Batt +) | {SWGR-C} V(C1) - V(Batt +) | {SWGR-T} V(G) - V(Batt -) | {SWGR-T} V(R) - V(Batt +) | {SWGR-T} V(N2) - V(Batt -) | {SWGR-T} V(PT) - V(Batt +) | {SWGR-C} V(C1) - V(N1) | {SWGR-T} V(SP1) - V(Batt -) | {SWGR-T} V(SP2) - V(Batt -) | {SWGR-T} V(R) - V(Batt -) | {SWGR-T} V(PC) - V(Batt -) | {SWGR-T} V(C1) - V(Batt -) | {SWGR-T} V(PT) - V(Batt -) | {SWGR-T} V(T) - V(Batt -) | {SWGR-T} V(N2) - V(Batt -) | {SWGR-C} V(PC) - V(Batt -) | {SWGR-C} V(C1) - V(Batt -) | {SWGR-T} V(T) - V(Batt -) | {SWGR-T} V(R) - V(Batt -) | {SWGR-T} V(PT) - V(Batt -) | {SWGR-C} V(N1) - V(Batt +) | {SWGR-T} V(N2) - V(Batt +)
-0.96875 | 123.587 | -61.6653 | 61.6882 | -0.010757 | 0.019869 | 0.010158 | -0.0077225 | -0.0058961 | 0.06257 | 0.072412 | 0.43945 | 61.8301 | -61.9675 | 61.6699 | -61.6882 | -61.9263 | 0.11902 | 0.20142 | 61.8256 | -61.8896 | -0.30212 | 0.14191 | 62.1048 | 123.3353 | -123.3765 | -0.2243 | 0.13733 | 62.4069 | 61.7844 | 61.8668 | -0.022888 | 123.4955 | 62.1048 | 123.4909 | -0.26093 | -0.2243 | 123.4955 | 62.1048 | -0.26093 | -0.022888 | 123.4909 | -123.6557 | -123.5779
0.70312 | 123.5001 | -61.7157 | 61.6608 | 0.012131 | 0.019015 | 0.015712 | -0.0075089 | -0.0050415 | 0.063638 | 0.072412 | 0.45319 | 61.8347 | -61.9904 | 61.6379 | -61.7203 | -61.9629 | 0.068665 | 0.13275 | 61.8439 | -61.8988 | -0.27466 | 0.17395 | 62.1689 | 123.3536 | -123.381 | -0.18311 | 0.1831 | 62.4435 | 61.7844 | 61.8484 | -0.004578 | 123.5504 | 62.1689 | 123.5596 | -0.24719 | -0.18311 | 123.5504 | 62.1689 | -0.24719 | -0.004578 | 123.5596 | -123.6511 | -123.5596
2.4375 | 123.4543 | -61.7157 | 61.7157 | 0.012131 | 0.018587 | 0.014857 | -0.0062271 | -0.0050415 | 0.06257 | 0.070916 | 0.52643 | 61.8027 | -61.9904 | 61.6928 | -61.6287 | -61.8851 | 0.059509 | 0.24719 | 61.7935 | -61.8942 | -0.27466 | 0.086975 | 62.2421 | 123.4085 | -123.3444 | -0.17853 | 0.07782 | 62.5168 | 61.7752 | 61.9629 | 0.086975 | 123.5184 | 62.2421 | 123.5092 | -0.16937 | -0.17853 | 123.5184 | 62.2421 | -0.16937 | 0.086975 | 123.5092 | -123.7061 | -123.6099
4.1562 | 123.5184 | -61.6974 | 61.6882 | -0.0031279 | 0.019015 | 0.011653 | -0.0070815 | -0.0044007 | 0.064066 | 0.071344 | 0.46692 | 61.821 | -61.9949 | 61.6333 | -61.6928 | -61.9354 | 0.086975 | 0.15106 | 61.821 | -61.8713 | -0.29755 | 0.13275 | 62.1643 | 123.3307 | -123.381 | -0.17395 | 0.13275 | 62.4619 | 61.7844 | 61.8484 | 0.004578 | 123.5184 | 62.1643 | 123.5184 | -0.23804 | -0.17395 | 123.5184 | 62.1643 | -0.23804 | 0.004578 | 123.5184 | -123.6832 | -123.5596
5.8906 | 123.5779 | -61.6653 | 61.6608 | -0.0031279 | 0.016878 | 0.014217 | -0.013063 | -0.0093139 | 0.067056 | 0.070916 | 0.42572 | 61.7523 | -61.9583 | 61.6837 | -61.6333 | -61.8759 | -0.1236 | 0.23346 | 61.7249 | -61.9125 | -0.29297 | 0.091552 | 62.0911 | 123.349 | -123.2941 | -0.24719 | 0.064087 | 62.384 | 61.5417 | 61.8988 | 0.032043 | 123.4177 | 62.0911 | 123.3902 | -0.21057 | -0.24719 | 123.4177 | 62.0911 | -0.21057 | 0.032043 | 123.3902 | -123.6191 | -123.5733
7.5781 | 123.5321 | -61.647 | 61.6516 | 0.012131 | 0.017733 | 0.013148 | -0.013063 | -0.0063233 | 0.067483 | 0.070062 | 0.48065 | 61.7523 | -61.9492 | 61.7157 | -61.6104 | -61.8393 | -0.13733 | 0.27924 | 61.7477 | -61.9217 | -0.30212 | 0.10071 | 62.1277 | 123.3627 | -123.262 | -0.27466 | 0.096131 | 62.4298 | 61.5097 | 61.9263 | 0.036621 | 123.3994 | 62.1277 | 123.3948 | -0.19226 | -0.27466 | 123.3994 | 62.1277 | -0.19226 | 0.036621 | 123.3948 | -123.6008 | -123.5733
9.3125 | 123.5229 | -61.6562 | 61.6745 | -0.0031279 | 0.017947 | 0.011439 | -0.0094315 | -0.0076049 | 0.066843 | 0.068139 | 0.49896 | 61.7432 | -61.9675 | 61.7432 | -61.5875 | -61.8256 | -0.11444 | 0.31586 | 61.7432 | -61.9034 | -0.31128 | 0.068664 | 62.1552 | 123.3994 | -123.262 | -0.24719 | 0.068664 | 62.4664 | 61.5417 | 61.972 | 0.068665 | 123.3994 | 62.1552 | 123.3994 | -0.16937 | -0.24719 | 123.3994 | 62.1552 | -0.16937 | 0.068665 | 123.3994 | -123.642 | -123.5779
11.0469 | 123.4543 | -61.7249 | 61.6745 | 0.012131 | 0.020937 | 0.011867 | -0.0049453 | -0.0067505 | 0.06492 | 0.070062 | 0.45776 | 61.7889 | -62.0087 | 61.647 | -61.6791 | -61.908 | -0.064087 | 0.16937 | 61.7844 | -61.8851 | -0.28381 | 0.11444 | 62.1826 | 123.3719 | -123.3536 | -0.16022 | 0.10986 | 62.4664 | 61.6608 | 61.8942 | 0.045777 | 123.5138 | 62.1826 | 123.5092 | -0.1831 | -0.16022 | 123.5138 | 62.1826 | -0.1831 | 0.045777 | 123.5092 | -123.6832 | -123.5596
12.7188 | 123.4818 | -61.702 | 61.6882 | 0.0045011 | 0.018801 | 0.0084489 | -0.0053727 | -0.0058961 | 0.064279 | 0.07113 | 0.43945 | 61.8347 | -61.9766 | 61.6333 | -61.7157 | -61.9354 | 0 | 0.14648 | 61.7981 | -61.8988 | -0.27466 | 0.14648 | 62.1414 | 123.3353 | -123.4039 | -0.19684 | 0.10986 | 62.4161 | 61.702 | 61.8484 | -0.013733 | 123.5367 | 62.1414 | 123.5001 | -0.23346 | -0.19684 | 123.5367 | 62.1414 | -0.23346 | -0.013733 | 123.5001 | -123.6649 | -123.587
14.4531 | 123.4131 | -61.7203 | 61.6791 | 0.012131 | 0.019442 | 0.015498 | -0.0077225 | -0.0033325 | 0.067483 | 0.070062 | 0.52643 | 61.7752 | -61.9629 | 61.7157 | -61.615 | -61.8164 | -0.16022 | 0.2243 | 61.7432 | -61.9034 | -0.24262 | 0.096131 | 62.2467 | 123.436 | -123.2941 | -0.18311 | 0.064087 | 62.4893 | 61.5601 | 61.9446 | 0.10529 | 123.4955 | 62.2467 | 123.4634 | -0.09613 | -0.18311 | 123.4955 | 62.2467 | -0.09613 | 0.10529 | 123.4634 | -123.642 | -123.5825
16.1875 | 123.4634 | -61.7157 | 61.6425 | 0.012131 | 0.019442 | 0.013789 | -0.0087905 | -0.0048279 | 0.063852 | 0.069848 | 0.47607 | 61.7477 | -61.9812 | 61.7065 | -61.6241 | -61.8484 | -0.17853 | 0.21515 | 61.7157 | -61.9308 | -0.2655 | 0.10529 | 62.1918 | 123.4222 | -123.2666 | -0.21515 | 0.073242 | 62.4573 | 61.5372 | 61.9308 | 0.091552 | 123.4634 | 62.1918 | 123.4314 | -0.13275 | -0.21515 | 123.4634 | 62.1918 | -0.13275 | 0.091552 | 123.4314 | -123.6237 | -123.5733
17.9375 | 123.4314 | -61.6837 | 61.7157 | -0.0031279 | 0.020724 | 0.014857 | -0.0049453 | -0.0044007 | 0.057443 | 0.071985 | 0.51727 | 61.7981 | -61.9629 | 61.7249 | -61.615 | -61.8759 | 0.032043 | 0.25177 | 61.8256 | -61.8713 | -0.27924 | 0.082398 | 62.2009 | 123.4085 | -123.3307 | -0.18768 | 0.10986 | 62.4802 | 61.7157 | 61.9354 | 0.068665 | 123.4818 | 62.2009 | 123.5092 | -0.19226 | -0.18768 | 123.4818 | 62.2009 | -0.19226 | 0.068665 | 123.5092 | -123.6786 | -123.587
19.6094 | 123.5596 | -61.6562 | 61.6333 | 0.0045011 | 0.021151 | 0.012508 | -0.013063 | -0.0054687 | 0.065134 | 0.068567 | 0.42114 | 61.7661 | -61.9629 | 61.6425 | -61.6653 | -61.8988 | -0.10529 | 0.18768 | 61.7294 | -61.9263 | -0.3067 | 0.13275 | 62.0773 | 123.2986 | -123.2986 | -0.27008 | 0.09613 | 62.384 | 61.5509 | 61.8439 | -0.009155 | 123.4222 | 62.0773 | 123.3856 | -0.24262 | -0.27008 | 123.4222 | 62.0773 | -0.24262 | -0.009155 | 123.3856 | -123.5962 | -123.5596
21.3438 | 123.468 | -61.6837 | 61.6745 | -0.0031279 | 0.019442 | 0.0099441 | -0.0062271 | -0.0056823 | 0.061502 | 0.069635 | 0.45319 | 61.8118 | -61.9858 | 61.6379 | -61.7065 | -61.94 | 0.082397 | 0.14191 | 61.8027 | -61.908 | -0.30212 | 0.13733 | 62.1368 | 123.3215 | -123.381 | -0.2243 | 0.12817 | 62.439 | 61.7661 | 61.8256 | -0.022888 | 123.4955 | 62.1368 | 123.4863 | -0.25635 | -0.2243 | 123.4955 | 62.1368 | -0.25635 | -0.022888 | 123.4863 | -123.6603 | -123.5825
23.0156 | 123.4497 | -61.7111 | 61.6562 | -0.0031279 | 0.019442 | 0.013148 | -0.01349 | -0.0052551 | 0.06492 | 0.069207 | 0.50354 | 61.7477 | -61.9354 | 61.7203 | -61.615 | -61.8347 | -0.18768 | 0.24261 | 61.7157 | -61.8896 | -0.2243 | 0.091553 | 62.2147 | 123.4314 | -123.2712 | -0.17853 | 0.059509 | 62.439 | 61.5234 | 61.9537 | 0.096131 | 123.4589 | 62.2147 | 123.4268 | -0.1236 | -0.17853 | 123.4589 | 62.2147 | -0.1236 | 0.096131 | 123.4268 | -123.5916 | -123.5458
24.7344 | 123.436 | -61.6928 | 61.6379 | 0.0045011 | 0.020724 | 0.013576 | -0.0077225 | -0.0035461 | 0.06492 | 0.070276 | 0.48523 | 61.7889 | -61.9675 | 61.7111 | -61.6287 | -61.853 | -0.15106 | 0.21973 | 61.7523 | -61.8805 | -0.27466 | 0.15106 | 62.178 | 123.4039 | -123.2666 | -0.18768 | 0.11444 | 62.4527 | 61.5417 | 61.9125 | 0.064087 | 123.4818 | 62.178 | 123.4451 | -0.16022 | -0.18768 | 123.4818 | 62.178 | -0.16022 | 0.064087 | 123.4451 | -123.6053 | -123.5184
26.4688 | 123.5733 | -61.6287 | 61.6653 | 0.0045011 | 0.01816 | 0.011012 | -0.0092179 | -0.0069641 | 0.066843 | 0.071557 | 0.41199 | 61.821 | -61.9583 | 61.6562 | -61.6653 | -61.94 | 0.14648 | 0.2243 | 61.8073 | -61.908 | -0.32959 | 0.15564 | 62.0407 | 123.2849 | -123.3307 | -0.27924 | 0.14191 | 62.3703 | 61.7752 | 61.853 | -0.036621 | 123.4497 | 62.0407 | 123.436 | -0.31128 | -0.27924 | 123.4497 | 62.0407 | -0.31128 | -0.036621 | 123.436 | -123.6237 | -123.5733
28.2031 | 123.4772 | -61.6974 | 61.6425 | -0.0031279 | 0.020937 | 0.0099441 | -0.0072953 | -0.0041871 | 0.065134 | 0.069848 | 0.45776 | 61.8164 | -61.9904 | 61.615 | -61.6928 | -61.9492 | 0.041199 | 0.12817 | 61.8256 | -61.8896 | -0.29297 | 0.17395 | 62.1552 | 123.3124 | -123.3353 | -0.19226 | 0.18311 | 62.4481 | 61.7386 | 61.8256 | 0.004578 | 123.5138 | 62.1552 | 123.5229 | -0.25177 | -0.19226 | 123.5138 | 62.1552 | -0.25177 | 0.004578 | 123.5229 | -123.6328 | -123.5321
29.9375 | 123.468 | -61.6882 | 61.6608 | 0.0045011 | 0.018587 | 0.011867 | -0.0072953 | -0.0058961 | 0.062997 | 0.072625 | 0.44861 | 61.8256 | -61.9446 | 61.6241 | -61.6837 | -61.9263 | 0.004578 | 0.15564 | 61.7752 | -61.908 | -0.25635 | 0.16479 | 62.1368 | 123.3124 | -123.3444 | -0.21973 | 0.11444 | 62.3932 | 61.6928 | 61.8439 | 0.004577 | 123.5138 | 62.1368 | 123.4634 | -0.23804 | -0.21973 | 123.5138 | 62.1368 | -0.23804 | 0.004577 | 123.4634 | -123.6053 | -123.5687
31.6094 | 123.5367 | -61.6608 | 61.6379 | -0.0031279 | 0.016878 | 0.0086625 | -0.018404 | -0.0041871 | 0.066415 | 0.070916 | 0.4303 | 61.7294 | -61.94 | 61.6333 | -61.6745 | -61.8851 | -0.13275 | 0.16937 | 61.7477 | -61.9263 | -0.27923 | 0.091553 | 62.0911 | 123.2941 | -123.3124 | -0.2655 | 0.10986 | 62.3703 | 61.528 | 61.8301 | -0.013733 | 123.3902 | 62.0911 | 123.4085 | -0.2243 | -0.2655 | 123.3902 | 62.0911 | -0.2243 | -0.013733 | 123.4085 | -123.5779 | -123.5641
33.3438 | 123.4818 | -61.647 | 61.7111 | -0.0031279 | 0.021151 | 0.013789 | -0.01285 | -0.0046143 | 0.062143 | 0.073053 | 0.48065 | 61.821 | -61.9446 | 61.6882 | -61.6196 | -61.8713 | 0.07782 | 0.2655 | 61.7935 | -61.8851 | -0.29755 | 0.10986 | 62.1277 | 123.3353 | -123.3307 | -0.23804 | 0.082397 | 62.4252 | 61.7249 | 61.9125 | 0.027466 | 123.468 | 62.1277 | 123.4406 | -0.2243 | -0.23804 | 123.468 | 62.1277 | -0.2243 | 0.027466 | 123.4406 | -123.6557 | -123.5962
35.0156 | 123.5275 | -61.6287 | 61.647 | -0.0031279 | 0.019869 | 0.010158 | -0.019045 | -0.0056823 | 0.064493 | 0.070276 | 0.48065 | 61.7477 | -61.9537 | 61.7065 | -61.6058 | -61.8301 | -0.14191 | 0.27008 | 61.7294 | -61.8942 | -0.32501 | 0.10071 | 62.1094 | 123.3353 | -123.2529 | -0.2655 | 0.082397 | 62.4344 | 61.4868 | 61.8988 | 0.022888 | 123.3765 | 62.1094 | 123.3582 | -0.20142 | -0.2655 | 123.3765 | 62.1094 | -0.20142 | 0.022888 | 123.3582 | -123.6008 | -123.5413
36.75 | 123.4497 | -61.6882 | 61.647 | 0.012131 | 0.022433 | 0.013576 | -0.01285 | -0.0082459 | 0.065347 | 0.069207 | 0.47607 | 61.8073 | -61.9537 | 61.6196 | -61.6974 | -61.9354 | 0.041199 | 0.13733 | 61.8073 | -61.9034 | -0.2655 | 0.16022 | 62.1643 | 123.3078 | -123.3444 | -0.21515 | 0.16022 | 62.4298 | 61.7294 | 61.8256 | -0.009156 | 123.4955 | 62.1643 | 123.4955 | -0.24719 | -0.21515 | 123.4955 | 62.1643 | -0.24719 | -0.009156 | 123.4955 | -123.6008 | -123.5504
38.4219 | 123.5046 | -61.6196 | 61.6791 | -0.0031279 | 0.020937 | 0.01443 | -0.01285 | -0.0056823 | 0.065775 | 0.070276 | 0.47607 | 61.8256 | -61.9492 | 61.6928 | -61.6196 | -61.8851 | 0.10986 | 0.25177 | 61.7981 | -61.8805 | -0.32959 | 0.14648 | 62.0956 | 123.3124 | -123.2986 | -0.26093 | 0.11902 | 62.4252 | 61.7294 | 61.8713 | 0 | 123.4451 | 62.0956 | 123.4177 | -0.2655 | -0.26093 | 123.4451 | 62.0956 | -0.2655 | 0 | 123.4177 | -123.6282 | -123.5596
40.0781 | 123.4909 | -61.6562 | 61.6745 | -0.0031279 | 0.01816 | 0.014644 | -0.018617 | -0.0058961 | 0.065988 | 0.070916 | 0.49439 | 61.7569 | -61.9492 | 61.7432 | -61.5692 | -61.8118 | -0.11902 | 0.31128 | 61.734 | -61.8942 | -0.29297 | 0.082397 | 62.1506 | 123.3994 | -123.2437 | -0.23804 | 0.059509 | 62.4435 | 61.5372 | 61.9675 | 0.086975 | 123.4131 | 62.1506 | 123.3902 | -0.15564 | -0.23804 | 123.4131 | 62.1506 | -0.15564 | 0.086975 | 123.3902 | -123.6237 | -123.5687
41.8125 | 123.5321 | -61.6653 | 61.6241 | 0.0045011 | 0.017519 | 0.010371 | -0.02054 | -0.0061097 | 0.067056 | 0.069635 | 0.44403 | 61.7569 | -61.9537 | 61.647 | -61.6425 | -61.8713 | -0.11444 | 0.18768 | 61.7111 | -61.9308 | -0.28839 | 0.13275 | 62.1094 | 123.3124 | -123.2666 | -0.2655 | 0.086975 | 62.3978 | 61.5509 | 61.853 | 0.022888 | 123.4222 | 62.1094 | 123.3765 | -0.20599 | -0.2655 | 123.4222 | 62.1094 | -0.20599 | 0.022888 | 123.3765 | -123.5779 | -123.555
43.5469 | 123.4772 | -61.6196 | 61.6974 | 0.0045011 | 0.018587 | 0.012721 | -0.012209 | -0.0073913 | 0.063425 | 0.071557 | 0.50354 | 61.8027 | -61.9537 | 61.702 | -61.6058 | -61.8805 | 0.064087 | 0.27924 | 61.8256 | -61.8713 | -0.33417 | 0.10529 | 62.1231 | 123.3215 | -123.3032 | -0.25177 | 0.12817 | 62.4573 | 61.6837 | 61.8988 | 0.013733 | 123.4222 | 62.1231 | 123.4451 | -0.26093 | -0.25177 | 123.4222 | 62.1231 | -0.26093 | 0.013733 | 123.4451 | -123.6511 | -123.5687
45.2188 | 123.4497 | -61.6425 | 61.6928 | 0.0045011 | 0.019228 | 0.012935 | -0.010072 | -0.0044007 | 0.062357 | 0.071771 | 0.50354 | 61.7935 | -61.9812 | 61.7203 | -61.6058 | -61.8759 | 0.050354 | 0.26093 | 61.8118 | -61.8668 | -0.33874 | 0.10071 | 62.146 | 123.3627 | -123.2986 | -0.2243 | 0.11902 | 62.4847 | 61.6928 | 61.9034 | 0.036621 | 123.436 | 62.146 | 123.4543 | -0.23346 | -0.2243 | 123.436 | 62.146 | -0.23346 | 0.036621 | 123.4543 | -123.674 | -123.5596
46.9375 | 123.5275 | -61.6333 | 61.6241 | 0.0045011 | 0.016451 | 0.013362 | -0.019899 | -0.0091003 | 0.06492 | 0.069848 | 0.40741 | 61.7065 | -61.9949 | 61.6196 | -61.6516 | -61.8851 | -0.1236 | 0.16937 | 61.7065 | -61.8988 | -0.36163 | 0.082397 | 62.0407 | 123.2529 | -123.2758 | -0.2655 | 0.082397 | 62.4023 | 61.5097 | 61.8027 | -0.01831 | 123.3398 | 62.0407 | 123.3398 | -0.25177 | -0.2655 | 123.3398 | 62.0407 | -0.25177 | -0.01831 | 123.3398 | -123.6191 | -123.523
48.6719 | 123.4177 | -61.702 | 61.6333 | -0.0031279 | 0.020937 | 0.014857 | -0.01584 | -0.0073913 | 0.066415 | 0.069421 | 0.48981 | 61.7294 | -61.9171 | 61.6699 | -61.6333 | -61.8622 | -0.20599 | 0.21515 | 61.6974 | -61.9217 | -0.21515 | 0.09613 | 62.1918 | 123.3719 | -123.2666 | -0.21973 | 0.064087 | 62.4069 | 61.496 | 61.9171 | 0.068664 | 123.4314 | 62.1918 | 123.3994 | -0.16022 | -0.21973 | 123.4314 | 62.1918 | -0.16022 | 0.068664 | 123.3994 | -123.5504 | -123.555
50.4219 | 123.5413 | -61.6425 | 61.6287 | 0.012131 | 0.020296 | 0.0090897 | -0.017549 | -0.0071777 | 0.064706 | 0.069421 | 0.41199 | 61.7386 | -61.9446 | 61.6379 | -61.6425 | -61.8805 | -0.10071 | 0.20599 | 61.6974 | -61.908 | -0.30212 | 0.10986 | 62.0544 | 123.2803 | -123.2712 | -0.2655 | 0.068665 | 62.3566 | 61.5417 | 61.8484 | 0 | 123.381 | 62.0544 | 123.3398 | -0.23804 | -0.2655 | 123.381 | 62.0544 | -0.23804 | 0 | 123.3398 | -123.5733 | -123.5367
52.0938 | 123.4772 | -61.6241 | 61.6699 | -0.0031279 | 0.019015 | 0.0088761 | -0.017763 | -0.0080323 | 0.063852 | 0.069421 | 0.49439 | 61.7065 | -61.9492 | 61.7386 | -61.5692 | -61.8164 | -0.10986 | 0.32501 | 61.7294 | -61.9171 | -0.32501 | 0.036621 | 62.1185 | 123.3627 | -123.2391 | -0.29297 | 0.059509 | 62.4435 | 61.5143 | 61.9492 | 0.054932 | 123.3307 | 62.1185 | 123.3536 | -0.19226 | -0.29297 | 123.3307 | 62.1185 | -0.19226 | 0.054932 | 123.3536 | -123.6191 | -123.587
53.8125 | 123.5367 | -61.6104 | 61.6562 | -0.0031279 | 0.020083 | 0.014644 | -0.013063 | -0.0069641 | 0.064279 | 0.069635 | 0.43488 | 61.7981 | -61.9446 | 61.6425 | -61.6608 | -61.9263 | 0.13733 | 0.21057 | 61.8073 | -61.9034 | -0.33417 | 0.14191 | 62.0453 | 123.2529 | -123.317 | -0.29297 | 0.15106 | 62.3795 | 61.7477 | 61.821 | -0.050354 | 123.4085 | 62.0453 | 123.4177 | -0.31586 | -0.29297 | 123.4085 | 62.0453 | -0.31586 | -0.050354 | 123.4177 | -123.6008 | -123.5596
55.5469 | 123.3902 | -61.6699 | 61.6379 | 0.0045011 | 0.02051 | 0.0088761 | -0.01285 | -0.0039735 | 0.063425 | 0.070276 | 0.52643 | 61.7432 | -61.9583 | 61.7065 | -61.5646 | -61.8027 | -0.16479 | 0.23804 | 61.6974 | -61.8851 | -0.28839 | 0.10529 | 62.1964 | 123.3765 | -123.2025 | -0.21515 | 0.05951 | 62.4847 | 61.5051 | 61.908 | 0.10529 | 123.4131 | 62.1964 | 123.3673 | -0.13275 | -0.21515 | 123.4131 | 62.1964 | -0.13275 | 0.10529 | 123.3673 | -123.5962 | -123.5229
57.2969 | 123.4589 | -61.6791 | 61.6425 | 0.0045011 | 0.019015 | 0.015071 | -0.015627 | -0.0076049 | 0.066415 | 0.068139 | 0.44403 | 61.7065 | -61.9492 | 61.6516 | -61.6287 | -61.8576 | -0.14648 | 0.19226 | 61.7203 | -61.9217 | -0.27008 | 0.064087 | 62.1231 | 123.3307 | -123.2712 | -0.24262 | 0.07782 | 62.3932 | 61.5326 | 61.8713 | 0.050354 | 123.3856 | 62.1231 | 123.3994 | -0.17853 | -0.24262 | 123.3856 | 62.1231 | -0.17853 | 0.050354 | 123.3994 | -123.5916 | -123.5641
58.9688 | 123.436 | -61.647 | 61.647 | 0.0045011 | 0.021151 | 0.015285 | -0.0098587 | -0.0063233 | 0.065347 | 0.070062 | 0.48523 | 61.7889 | -61.9446 | 61.6333 | -61.6516 | -61.9125 | 0.064087 | 0.16937 | 61.7706 | -61.8851 | -0.29755 | 0.14191 | 62.1323 | 123.2803 | -123.2986 | -0.23804 | 0.1236 | 62.4298 | 61.7111 | 61.8164 | -0.004577 | 123.436 | 62.1323 | 123.4177 | -0.2655 | -0.23804 | 123.436 | 62.1323 | -0.2655 | -0.004577 | 123.4177 | -123.5916 | -123.5321
60.6875 | 123.5046 | -61.5829 | 61.6562 | 0.0045011 | 0.018374 | 0.012508 | -0.014986 | -0.0095277 | 0.065561 | 0.072625 | 0.40283 | 61.7798 | -61.9812 | 61.6196 | -61.6379 | -61.9171 | 0.13275 | 0.19226 | 61.7844 | -61.9125 | -0.39825 | 0.1236 | 61.9858 | 123.2025 | -123.2941 | -0.32959 | 0.12817 | 62.384 | 61.7157 | 61.7752 | -0.054931 | 123.3627 | 61.9858 | 123.3673 | -0.33417 | -0.32959 | 123.3627 | 61.9858 | -0.33417 | -0.054931 | 123.3673 | -123.6374 | -123.5687
62.4375 | 123.4497 | -61.6241 | 61.6425 | 0.0045011 | 0.019015 | 0.012935 | -0.017763 | -0.0048279 | 0.066202 | 0.070489 | 0.48981 | 61.7157 | -61.9583 | 61.702 | -61.5601 | -61.8027 | -0.13733 | 0.28839 | 61.6699 | -61.8805 | -0.33417 | 0.073242 | 62.114 | 123.3261 | -123.2025 | -0.25635 | 0.027466 | 62.4481 | 61.4868 | 61.9125 | 0.064087 | 123.3398 | 62.114 | 123.2941 | -0.17853 | -0.25635 | 123.3398 | 62.114 | -0.17853 | 0.064087 | 123.2941 | -123.6008 | -123.5229
64.1719 | 123.4177 | -61.6699 | 61.647 | -0.0031279 | 0.019869 | 0.017635 | -0.011781 | -0.0041871 | 0.065347 | 0.07113 | 0.4303 | 61.7477 | -61.9492 | 61.6333 | -61.6562 | -61.8713 | -0.036621 | 0.14191 | 61.7752 | -61.8759 | -0.27924 | 0.10071 | 62.1002 | 123.3032 | -123.3032 | -0.20599 | 0.12817 | 62.3795 | 61.6333 | 61.8118 | 0.013733 | 123.4177 | 62.1002 | 123.4451 | -0.20142 | -0.20599 | 123.4177 | 62.1002 | -0.20142 | 0.013733 | 123.4451 | -123.5962 | -123.5229
65.8281 | 123.3673 | -61.6562 | 61.702 | -0.0031279 | 0.020937 | 0.013148 | -0.01349 | -0.0067505 | 0.062997 | 0.069421 | 0.5127 | 61.8073 | -61.9125 | 61.702 | -61.5829 | -61.8393 | 0.022888 | 0.25177 | 61.7477 | -61.8484 | -0.25635 | 0.10529 | 62.1689 | 123.3582 | -123.2849 | -0.19226 | 0.045777 | 62.4252 | 61.6791 | 61.908 | 0.073242 | 123.4634 | 62.1689 | 123.4039 | -0.18311 | -0.19226 | 123.4634 | 62.1689 | -0.18311 | 0.073242 | 123.4039 | -123.6145 | -123.5504
67.5625 | 123.436 | -61.6516 | 61.6699 | -0.0031279 | 0.02051 | 0.012508 | -0.012209 | -0.0048279 | 0.063638 | 0.069421 | 0.49439 | 61.8164 | -61.9446 | 61.6974 | -61.5829 | -61.8484 | 0.082397 | 0.26093 | 61.7889 | -61.8713 | -0.29297 | 0.14648 | 62.146 | 123.349 | -123.2529 | -0.21973 | 0.11902 | 62.439 | 61.734 | 61.9125 | 0.068664 | 123.468 | 62.146 | 123.4406 | -0.19684 | -0.21973 | 123.468 | 62.146 | -0.19684 | 0.068664 | 123.4406 | -123.6145 | -123.5413
69.2344 | 123.4589 | -61.6058 | 61.6287 | -0.0031279 | 0.021578 | 0.0075943 | -0.021394 | -0.0048279 | 0.064706 | 0.06878 | 0.47607 | 61.7203 | -61.9125 | 61.7111 | -61.5372 | -61.7706 | -0.14191 | 0.32044 | 61.7065 | -61.8759 | -0.3067 | 0.091553 | 62.0819 | 123.317 | -123.1659 | -0.27008 | 0.07782 | 62.3886 | 61.4639 | 61.9263 | 0.068665 | 123.3261 | 62.0819 | 123.3124 | -0.16479 | -0.27008 | 123.3261 | 62.0819 | -0.16479 | 0.068665 | 123.3124 | -123.5413 | -123.5046
70.9688 | 123.4543 | -61.5921 | 61.6333 | 0.012131 | 0.018374 | 0.012935 | -0.016054 | -0.0056823 | 0.06492 | 0.071557 | 0.48981 | 61.7203 | -61.9263 | 61.6928 | -61.5509 | -61.8027 | -0.036621 | 0.3067 | 61.7249 | -61.8622 | -0.33417 | 0.086975 | 62.0819 | 123.2849 | -123.1842 | -0.27008 | 0.091553 | 62.4161 | 61.5555 | 61.8988 | 0.041199 | 123.3124 | 62.0819 | 123.317 | -0.21057 | -0.27008 | 123.3124 | 62.0819 | -0.21057 | 0.041199 | 123.317 | -123.5596 | -123.4955
72.7188 | 123.5046 | -61.5601 | 61.6562 | 0.0045011 | 0.019869 | 0.013362 | -0.015199 | -0.0095277 | 0.06492 | 0.071985 | 0.40283 | 61.7752 | -61.9583 | 61.6058 | -61.647 | -61.908 | 0.12817 | 0.20142 | 61.7569 | -61.8851 | -0.39825 | 0.11902 | 61.9629 | 123.1659 | -123.3032 | -0.32501 | 0.10071 | 62.3611 | 61.6882 | 61.7615 | -0.086975 | 123.3353 | 61.9629 | 123.317 | -0.3479 | -0.32501 | 123.3353 | 61.9629 | -0.3479 | -0.086975 | 123.317 | -123.6145 | -123.5413
74.3906 | 123.3444 | -61.6745 | 61.6241 | 0.0045011 | 0.019869 | 0.013789 | -0.014558 | -0.0061097 | 0.062997 | 0.069848 | 0.49896 | 61.7157 | -61.9217 | 61.6837 | -61.5646 | -61.7889 | -0.16937 | 0.21973 | 61.7249 | -61.8622 | -0.24719 | 0.091552 | 62.1735 | 123.3582 | -123.1888 | -0.18768 | 0.10071 | 62.4207 | 61.5051 | 61.8942 | 0.10986 | 123.3902 | 62.1735 | 123.3994 | -0.11444 | -0.18768 | 123.3902 | 62.1735 | -0.11444 | 0.10986 | 123.3994 | -123.5458 | -123.4863
76.125 | 123.4497 | -61.6196 | 61.6287 | -0.0031279 | 0.018587 | 0.012721 | -0.014131 | -0.0069641 | 0.063638 | 0.068994 | 0.48065 | 61.7203 | -61.8988 | 61.6882 | -61.5463 | -61.821 | -0.018311 | 0.29297 | 61.7203 | -61.8759 | -0.27924 | 0.091553 | 62.1002 | 123.3078 | -123.175 | -0.25635 | 0.091553 | 62.3795 | 61.6013 | 61.9125 | 0.073242 | 123.3398 | 62.1002 | 123.3398 | -0.20142 | -0.25635 | 123.3398 | 62.1002 | -0.20142 | 0.073242 | 123.3398 | -123.5275 | -123.5046
77.7969 | 123.4039 | -61.6379 | 61.6333 | -0.010757 | 0.019228 | 0.013576 | -0.01349 | -0.0056823 | 0.063852 | 0.070916 | 0.44403 | 61.7798 | -61.9492 | 61.5967 | -61.6516 | -61.8988 | 0.09613 | 0.15564 | 61.7752 | -61.8668 | -0.31128 | 0.14648 | 62.0819 | 123.2346 | -123.2849 | -0.22888 | 0.14191 | 62.3932 | 61.734 | 61.7935 | -0.013733 | 123.4177 | 62.0819 | 123.4131 | -0.26093 | -0.22888 | 123.4177 | 62.0819 | -0.26093 | -0.013733 | 123.4131 | -123.5825 | -123.5001
79.5312 | 123.436 | -61.5921 | 61.647 | -0.010757 | 0.017306 | 0.0084489 | -0.018404 | -0.0058961 | 0.065988 | 0.070703 | 0.48981 | 61.6928 | -61.9217 | 61.7065 | -61.5372 | -61.7569 | -0.13733 | 0.3067 | 61.6882 | -61.8713 | -0.32959 | 0.045776 | 62.0819 | 123.2986 | -123.1842 | -0.27924 | 0.041198 | 62.4115 | 61.4548 | 61.8988 | 0.054932 | 123.2849 | 62.0819 | 123.2803 | -0.1648 | -0.27924 | 123.2849 | 62.0819 | -0.1648 | 0.054932 | 123.2803 | -123.5687 | -123.5184
81.2031 | 123.349 | -61.6882 | 61.6196 | -0.0031279 | 0.01816 | 0.018703 | -0.016267 | -0.0063233 | 0.064706 | 0.070703 | 0.49896 | 61.6837 | -61.9446 | 61.6837 | -61.5555 | -61.7798 | -0.17853 | 0.25177 | 61.7157 | -61.8805 | -0.25635 | 0.064087 | 62.1872 | 123.3719 | -123.175 | -0.19226 | 0.09613 | 62.4435 | 61.5097 | 61.94 | 0.13275 | 123.3719 | 62.1872 | 123.4039 | -0.091553 | -0.19226 | 123.3719 | 62.1872 | -0.091553 | 0.13275 | 123.4039 | -123.5641 | -123.5001
83 | 123.349 | -61.6837 | 61.5875 | 0.0045011 | 0.019015 | 0.014644 | -0.016695 | -0.0058961 | 0.065134 | 0.06878 | 0.49896 | 61.6608 | -61.9308 | 61.6837 | -61.5509 | -61.7889 | -0.19684 | 0.25177 | 61.6882 | -61.853 | -0.24719 | 0.073243 | 62.1826 | 123.3673 | -123.1384 | -0.16937 | 0.10071 | 62.4298 | 61.4868 | 61.9354 | 0.13275 | 123.3444 | 62.1826 | 123.3719 | -0.10528 | -0.16937 | 123.3444 | 62.1826 | -0.10528 | 0.13275 | 123.3719 | -123.5184 | -123.4406
84.6875 | 123.3856 | -61.6425 | 61.6333 | 0.0045011 | 0.020083 | 0.010799 | -0.0092179 | -0.0048279 | 0.064706 | 0.069848 | 0.44861 | 61.7661 | -61.9492 | 61.6196 | -61.6425 | -61.8896 | 0.068665 | 0.17395 | 61.7706 | -61.8301 | -0.3067 | 0.13275 | 62.0911 | 123.262 | -123.2758 | -0.18768 | 0.13733 | 62.3978 | 61.7111 | 61.8164 | 0 | 123.4085 | 62.0911 | 123.4131 | -0.24719 | -0.18768 | 123.4085 | 62.0911 | -0.24719 | 0 | 123.4131 | -123.5825 | -123.4634
86.4844 | 123.4039 | -61.6425 | 61.5967 | 0.0045011 | 0.015383 | 0.011226 | -0.016695 | -0.0071777 | 0.065561 | 0.070703 | 0.4303 | 61.647 | -61.9492 | 61.615 | -61.6013 | -61.8439 | -0.14648 | 0.20599 | 61.6974 | -61.8896 | -0.3067 | 0.050354 | 62.0728 | 123.2574 | -123.1979 | -0.24719 | 0.10071 | 62.3795 | 61.496 | 61.8484 | 0.041199 | 123.2895 | 62.0728 | 123.3398 | -0.20142 | -0.24719 | 123.2895 | 62.0728 | -0.20142 | 0.041199 | 123.3398 | -123.5458 | -123.4863
88.2188 | 123.3261 | -61.6425 | 61.6653 | -0.010757 | 0.021578 | 0.015712 | -0.012422 | -0.0046143 | 0.064706 | 0.071344 | 0.52185 | 61.7981 | -61.8805 | 61.6928 | -61.5738 | -61.8164 | 0.027466 | 0.28839 | 61.7615 | -61.8393 | -0.23804 | 0.13275 | 62.1643 | 123.3353 | -123.2391 | -0.19684 | 0.096131 | 62.4023 | 61.6699 | 61.9308 | 0.068664 | 123.4406 | 62.1643 | 123.4039 | -0.17395 | -0.19684 | 123.4406 | 62.1643 | -0.17395 | 0.068664 | 123.4039 | -123.5458 | -123.5046
90 | 123.4726 | -61.5738 | 61.6379 | -0.0031279 | 0.019656 | 0.01443 | -0.01349 | -0.0065369 | 0.064066 | 0.070916 | 0.42572 | 61.7477 | -61.9492 | 61.6287 | -61.6013 | -61.8484 | 0.12817 | 0.24261 | 61.7752 | -61.8393 | -0.37537 | 0.10986 | 61.9995 | 123.2025 | -123.2391 | -0.2655 | 0.13733 | 62.3749 | 61.702 | 61.8164 | -0.027465 | 123.3215 | 61.9995 | 123.349 | -0.27466 | -0.2655 | 123.3215 | 61.9995 | -0.27466 | -0.027465 | 123.349 | -123.587 | -123.4772
91.7969 | 123.4314 | -61.5921 | 61.6013 | -0.010757 | 0.019442 | 0.010371 | -0.018404 | -0.0069641 | 0.065134 | 0.069848 | 0.44403 | 61.6837 | -61.8988 | 61.6562 | -61.5463 | -61.7844 | -0.1236 | 0.28381 | 61.6791 | -61.8668 | -0.3067 | 0.082398 | 62.0361 | 123.2483 | -123.1476 | -0.27466 | 0.07782 | 62.3428 | 61.4685 | 61.8759 | 0.045776 | 123.2758 | 62.0361 | 123.2712 | -0.19226 | -0.27466 | 123.2758 | 62.0361 | -0.19226 | 0.045776 | 123.2712 | -123.5001 | -123.468
93.5938 | 123.3856 | -61.6333 | 61.6013 | -0.0031279 | 0.019228 | 0.014644 | -0.012209 | -0.0054687 | 0.06257 | 0.070276 | 0.43945 | 61.7615 | -61.9354 | 61.5875 | -61.6425 | -61.8805 | 0.059509 | 0.13275 | 61.7935 | -61.821 | -0.30212 | 0.16022 | 62.0728 | 123.2208 | -123.2437 | -0.18768 | 0.19226 | 62.3749 | 61.6928 | 61.7661 | -0.009155 | 123.3948 | 62.0728 | 123.4268 | -0.24719 | -0.18768 | 123.3948 | 62.0728 | -0.24719 | -0.009155 | 123.4268 | -123.5367 | -123.4222
95.2656 | 123.4543 | -61.5692 | 61.6333 | -0.0031279 | 0.017733 | 0.014003 | -0.014986 | -0.0069641 | 0.063638 | 0.071985 | 0.45776 | 61.7294 | -61.9034 | 61.6333 | -61.6013 | -61.8576 | 0.064087 | 0.23346 | 61.734 | -61.8484 | -0.33417 | 0.09613 | 62.027 | 123.2025 | -123.2346 | -0.27924 | 0.10071 | 62.3611 | 61.6333 | 61.8027 | -0.032043 | 123.2986 | 62.027 | 123.3032 | -0.28839 | -0.27924 | 123.2986 | 62.027 | -0.28839 | -0.032043 | 123.3032 | -123.5367 | -123.4818
97 | 123.4314 | -61.5875 | 61.6104 | -0.010757 | 0.017519 | 0.01208 | -0.01819 | -0.0078187 | 0.065561 | 0.071771 | 0.45776 | 61.6791 | -61.8896 | 61.6608 | -61.5463 | -61.7706 | -0.13275 | 0.28381 | 61.6882 | -61.8301 | -0.30212 | 0.068664 | 62.0453 | 123.2483 | -123.1567 | -0.24262 | 0.077819 | 62.3474 | 61.4548 | 61.8713 | 0.041198 | 123.2666 | 62.0453 | 123.2758 | -0.18311 | -0.24262 | 123.2666 | 62.0453 | -0.18311 | 0.041198 | 123.2758 | -123.5001 | -123.4406
98.6719 | 123.4772 | -61.5372 | 61.6516 | -0.0031279 | 0.017733 | 0.011653 | -0.014986 | -0.0078187 | 0.064706 | 0.070062 | 0.44403 | 61.7111 | -61.9263 | 61.6425 | -61.5921 | -61.8256 | 0.064087 | 0.24719 | 61.7386 | -61.8301 | -0.3891 | 0.05951 | 61.9812 | 123.1796 | -123.2437 | -0.29297 | 0.086975 | 62.3703 | 61.6013 | 61.7844 | -0.054932 | 123.2483 | 61.9812 | 123.2758 | -0.28839 | -0.29297 | 123.2483 | 61.9812 | -0.28839 | -0.054932 | 123.2758 | -123.5779 | -123.4818
100.3906 | 123.3627 | -61.6379 | 61.6241 | -0.0031279 | 0.02051 | 0.013789 | -0.011354 | -0.0073913 | 0.064706 | 0.069207 | 0.44861 | 61.7935 | -61.9446 | 61.5967 | -61.6196 | -61.8805 | 0.041199 | 0.14191 | 61.7569 | -61.8484 | -0.3067 | 0.16937 | 62.0865 | 123.2346 | -123.2437 | -0.21057 | 0.13275 | 62.3932 | 61.6791 | 61.7798 | 0.01831 | 123.4314 | 62.0865 | 123.3948 | -0.24262 | -0.21057 | 123.4314 | 62.0865 | -0.24262 | 0.01831 | 123.3948 | -123.5687 | -123.4726
102.1875 | 123.3582 | -61.6196 | 61.6013 | -0.010757 | 0.019015 | 0.0099441 | -0.017763 | -0.0063233 | 0.063638 | 0.071557 | 0.45319 | 61.6608 | -61.8988 | 61.6333 | -61.5829 | -61.8164 | -0.14648 | 0.21515 | 61.647 | -61.8576 | -0.27924 | 0.05951 | 62.0728 | 123.2529 | -123.1842 | -0.23804 | 0.045777 | 62.352 | 61.4731 | 61.8347 | 0.036621 | 123.2803 | 62.0728 | 123.2666 | -0.19684 | -0.23804 | 123.2803 | 62.0728 | -0.19684 | 0.036621 | 123.2666 | -123.5001 | -123.4589
103.8438 | 123.3215 | -61.6058 | 61.6745 | 0.0045011 | 0.01816 | 0.0097305 | -0.013063 | -0.0039735 | 0.062997 | 0.072198 | 0.51727 | 61.7615 | -61.9171 | 61.6791 | -61.5463 | -61.821 | 0.054932 | 0.27924 | 61.7523 | -61.821 | -0.31128 | 0.086975 | 62.1231 | 123.2849 | -123.2208 | -0.21515 | 0.077819 | 62.4344 | 61.6608 | 61.8851 | 0.059509 | 123.3673 | 62.1231 | 123.3582 | -0.21515 | -0.21515 | 123.3673 | 62.1231 | -0.21515 | 0.059509 | 123.3582 | -123.5916 | -123.4955
105.5156 | 123.381 | -61.6104 | 61.6241 | 0.0045011 | 0.020937 | 0.013148 | -0.014558 | -0.0039735 | 0.065347 | 0.070916 | 0.41657 | 61.7706 | -61.9263 | 61.5875 | -61.6241 | -61.8576 | 0 | 0.15106 | 61.7523 | -61.8484 | -0.31586 | 0.14648 | 62.027 | 123.1979 | -123.2483 | -0.23804 | 0.12817 | 62.3428 | 61.6104 | 61.7615 | -0.013733 | 123.381 | 62.027 | 123.3627 | -0.24719 | -0.23804 | 123.381 | 62.027 | -0.24719 | -0.013733 | 123.3627 | -123.5504 | -123.4726
107.1875 | 123.3536 | -61.6241 | 61.6196 | 0.0045011 | 0.019015 | 0.012935 | -0.01584 | -0.0052551 | 0.065134 | 0.070916 | 0.42114 | 61.7569 | -61.9171 | 61.5601 | -61.6333 | -61.8622 | 0.027466 | 0.13733 | 61.7569 | -61.8439 | -0.29297 | 0.13733 | 62.0453 | 123.1842 | -123.2529 | -0.21973 | 0.13733 | 62.3383 | 61.6516 | 61.7615 | -0.009155 | 123.381 | 62.0453 | 123.381 | -0.23804 | -0.21973 | 123.381 | 62.0453 | -0.23804 | -0.009155 | 123.381 | -123.5367 | -123.4634
108.8438 | 123.4268 | -61.5829 | 61.5829 | 0.0045011 | 0.017947 | 0.013148 | -0.021394 | -0.0058961 | 0.065988 | 0.071344 | 0.38452 | 61.702 | -61.8988 | 61.6196 | -61.5692 | -61.7981 | -0.10071 | 0.21515 | 61.7111 | -61.8622 | -0.31586 | 0.11902 | 61.9675 | 123.2025 | -123.1522 | -0.27924 | 0.12817 | 62.2833 | 61.4822 | 61.7981 | 0.013733 | 123.2849 | 61.9675 | 123.2941 | -0.21515 | -0.27924 | 123.2849 | 61.9675 | -0.21515 | 0.013733 | 123.2941 | -123.4818 | -123.4451
110.5156 | 123.317 | -61.647 | 61.5967 | -0.0031279 | 0.018374 | 0.018275 | -0.011781 | -0.0052551 | 0.064066 | 0.070916 | 0.50354 | 61.734 | -61.9034 | 61.6837 | -61.5326 | -61.7569 | -0.19226 | 0.24261 | 61.702 | -61.8118 | -0.25635 | 0.13733 | 62.1506 | 123.3307 | -123.1293 | -0.1648 | 0.10529 | 62.4069 | 61.4548 | 61.8896 | 0.11444 | 123.381 | 62.1506 | 123.349 | -0.10986 | -0.1648 | 123.381 | 62.1506 | -0.10986 | 0.11444 | 123.349 | -123.5001 | -123.4085
112.1875 | 123.4497 | -61.5555 | 61.6425 | 0.0045011 | 0.017306 | 0.014644 | -0.016481 | -0.0065369 | 0.064066 | 0.070703 | 0.43488 | 61.7386 | -61.8988 | 61.6333 | -61.5738 | -61.821 | 0.073242 | 0.23346 | 61.7294 | -61.853 | -0.34332 | 0.09613 | 61.9904 | 123.1888 | -123.2162 | -0.29755 | 0.086975 | 62.3337 | 61.6287 | 61.7889 | -0.018311 | 123.2941 | 61.9904 | 123.2849 | -0.2655 | -0.29755 | 123.2941 | 61.9904 | -0.2655 | -0.018311 | 123.2849 | -123.5413 | -123.4955
113.8594 | 123.3719 | -61.6013 | 61.6104 | 0.0045011 | 0.020296 | 0.015498 | -0.011141 | -0.0054687 | 0.063638 | 0.07113 | 0.43488 | 61.7706 | -61.8988 | 61.6013 | -61.615 | -61.8622 | 0.059509 | 0.13275 | 61.7706 | -61.821 | -0.29755 | 0.16022 | 62.0361 | 123.2025 | -123.2254 | -0.21973 | 0.16022 | 62.3337 | 61.6608 | 61.734 | -0.013733 | 123.3719 | 62.0361 | 123.3719 | -0.26093 | -0.21973 | 123.3719 | 62.0361 | -0.26093 | -0.013733 | 123.3719 | -123.5092 | -123.4314
115.5781 | 123.3536 | -61.6287 | 61.6333 | 0.012131 | 0.018587 | 0.015285 | -0.013277 | -0.0050415 | 0.06492 | 0.072198 | 0.44403 | 61.8027 | -61.8988 | 61.5829 | -61.6104 | -61.8622 | 0.059509 | 0.15106 | 61.8301 | -61.821 | -0.27008 | 0.16937 | 62.0728 | 123.2117 | -123.2437 | -0.19226 | 0.19684 | 62.3428 | 61.6882 | 61.7798 | 0.01831 | 123.4314 | 62.0728 | 123.4589 | -0.23346 | -0.19226 | 123.4314 | 62.0728 | -0.23346 | 0.01831 | 123.4589 | -123.5321 | -123.4543
117.25 | 123.381 | -61.5692 | 61.615 | 0.012131 | 0.018587 | 0.0093033 | -0.020754 | -0.0052551 | 0.068338 | 0.070489 | 0.48065 | 61.7157 | -61.8576 | 61.7065 | -61.4639 | -61.7249 | -0.12817 | 0.32501 | 61.6974 | -61.8439 | -0.28839 | 0.10071 | 62.0499 | 123.2758 | -123.0789 | -0.27466 | 0.082398 | 62.3383 | 61.441 | 61.8942 | 0.10529 | 123.2849 | 62.0499 | 123.2666 | -0.15564 | -0.27466 | 123.2849 | 62.0499 | -0.15564 | 0.10529 | 123.2666 | -123.4726 | -123.4589
118.9375 | 123.4314 | -61.5417 | 61.6241 | -0.0031279 | 0.023714 | 0.011653 | -0.011781 | -0.0078187 | 0.064279 | 0.068567 | 0.43945 | 61.8073 | -61.9034 | 61.6287 | -61.5555 | -61.8347 | 0.1236 | 0.2655 | 61.7935 | -61.8439 | -0.36163 | 0.1831 | 61.9812 | 123.1705 | -123.1796 | -0.30212 | 0.16937 | 62.3428 | 61.6653 | 61.8073 | -0.013733 | 123.349 | 61.9812 | 123.3353 | -0.29297 | -0.30212 | 123.349 | 61.9812 | -0.29297 | -0.013733 | 123.3353 | -123.5275 | -123.468
120.6094 | 123.381 | -61.5601 | 61.6333 | -0.0031279 | 0.018374 | 0.0090897 | -0.019258 | -0.0054687 | 0.064706 | 0.068994 | 0.48981 | 61.7111 | -61.8759 | 61.6928 | -61.5005 | -61.7386 | -0.12817 | 0.31128 | 61.6837 | -61.8484 | -0.31586 | 0.07782 | 62.0499 | 123.2529 | -123.1338 | -0.28839 | 0.050354 | 62.3657 | 61.4319 | 61.8713 | 0.05951 | 123.2712 | 62.0499 | 123.2437 | -0.17853 | -0.28839 | 123.2712 | 62.0499 | -0.17853 | 0.05951 | 123.2437 | -123.5092 | -123.4818
122.3125 | 123.4497 | -61.5417 | 61.6196 | -0.0031279 | 0.01816 | 0.013148 | -0.016054 | -0.0078187 | 0.06492 | 0.070703 | 0.41657 | 61.7889 | -61.8851 | 61.6104 | -61.5829 | -61.853 | 0.10986 | 0.2243 | 61.7935 | -61.8027 | -0.34332 | 0.16937 | 61.9583 | 123.1522 | -123.2025 | -0.26093 | 0.17395 | 62.3016 | 61.6516 | 61.7661 | -0.041199 | 123.3307 | 61.9583 | 123.3353 | -0.31128 | -0.26093 | 123.3307 | 61.9583 | -0.31128 | -0.041199 | 123.3353 | -123.5046 | -123.4222
123.9844 | 123.2986 | -61.615 | 61.6196 | 0.0045011 | 0.019869 | 0.011867 | -0.014558 | -0.0022645 | 0.06257 | 0.069635 | 0.48981 | 61.7203 | -61.8988 | 61.6653 | -61.5143 | -61.7432 | -0.17395 | 0.23346 | 61.7203 | -61.7889 | -0.28381 | 0.10071 | 62.1048 | 123.2803 | -123.1338 | -0.17395 | 0.10071 | 62.3886 | 61.441 | 61.8484 | 0.10071 | 123.3353 | 62.1048 | 123.3353 | -0.12817 | -0.17395 | 123.3353 | 62.1048 | -0.12817 | 0.10071 | 123.3353 | -123.5184 | -123.4085
125.6875 | 123.4314 | -61.5692 | 61.5784 | 0.012131 | 0.020083 | 0.013789 | -0.019685 | -0.0076049 | 0.064706 | 0.070703 | 0.39825 | 61.7386 | -61.8805 | 61.615 | -61.5601 | -61.7935 | -0.091553 | 0.19684 | 61.6837 | -61.8347 | -0.31128 | 0.16022 | 61.9675 | 123.1842 | -123.1384 | -0.2655 | 0.10529 | 62.2787 | 61.4777 | 61.7661 | 0.009155 | 123.3078 | 61.9675 | 123.2529 | -0.2243 | -0.2655 | 123.3078 | 61.9675 | -0.2243 | 0.009155 | 123.2529 | -123.4589 | -123.4131
127.3594 | 123.2986 | -61.5555 | 61.6653 | -0.0031279 | 0.019656 | 0.011226 | -0.011568 | -0.0065369 | 0.061502 | 0.072198 | 0.48981 | 61.7523 | -61.8713 | 61.6882 | -61.5143 | -61.7615 | 0.032043 | 0.27924 | 61.7752 | -61.7752 | -0.31586 | 0.086975 | 62.0453 | 123.2437 | -123.1796 | -0.21973 | 0.10986 | 62.3611 | 61.5875 | 61.8347 | 0.041199 | 123.3078 | 62.0453 | 123.3307 | -0.20599 | -0.21973 | 123.3078 | 62.0453 | -0.20599 | 0.041199 | 123.3307 | -123.5367 | -123.4406
129.0312 | 123.3261 | -61.5967 | 61.6379 | -0.0031279 | 0.018587 | 0.010799 | -0.017122 | -0.0080323 | 0.065134 | 0.070489 | 0.44403 | 61.6974 | -61.8713 | 61.6287 | -61.5463 | -61.7661 | -0.16937 | 0.21515 | 61.7203 | -61.8301 | -0.27466 | 0.05951 | 62.0407 | 123.2254 | -123.1842 | -0.23346 | 0.082398 | 62.3154 | 61.4273 | 61.8118 | 0.050354 | 123.2941 | 62.0407 | 123.317 | -0.16937 | -0.23346 | 123.2941 | 62.0407 | -0.16937 | 0.050354 | 123.317 | -123.5092 | -123.468
130.75 | 123.3856 | -61.528 | 61.647 | -0.0031279 | 0.019015 | 0.011653 | -0.017336 | -0.0091003 | 0.062143 | 0.069421 | 0.45776 | 61.7157 | -61.853 | 61.6928 | -61.4822 | -61.7157 | -0.14191 | 0.28839 | 61.7111 | -61.8256 | -0.32501 | 0.068664 | 61.9858 | 123.2208 | -123.1293 | -0.29755 | 0.064087 | 62.3108 | 61.3861 | 61.8164 | 0.045776 | 123.2437 | 61.9858 | 123.2391 | -0.18768 | -0.29755 | 123.2437 | 61.9858 | -0.18768 | 0.045776 | 123.2391 | -123.5001 | -123.4726
132.4219 | 123.3307 | -61.5921 | 61.6791 | 0.0045011 | 0.021578 | 0.010585 | -0.011568 | -0.0035461 | 0.062997 | 0.071344 | 0.4303 | 61.7889 | -61.8713 | 61.6333 | -61.5829 | -61.8164 | 0.032043 | 0.12817 | 61.8164 | -61.7844 | -0.27924 | 0.10986 | 62.0224 | 123.2254 | -123.262 | -0.19226 | 0.13733 | 62.3016 | 61.6241 | 61.7203 | 0.009155 | 123.381 | 62.0224 | 123.4085 | -0.2243 | -0.19226 | 123.381 | 62.0224 | -0.2243 | 0.009155 | 123.4085 | -123.5504 | -123.4634
134.125 | 123.2849 | -61.5372 | 61.6974 | -0.0031279 | 0.019656 | 0.013362 | -0.011781 | -0.0044007 | 0.061929 | 0.071771 | 0.48981 | 61.7889 | -61.8484 | 61.7065 | -61.4822 | -61.734 | 0.045776 | 0.27008 | 61.7981 | -61.7661 | -0.31128 | 0.091552 | 62.027 | 123.2437 | -123.1796 | -0.22888 | 0.10071 | 62.3383 | 61.5829 | 61.8073 | 0.054931 | 123.3261 | 62.027 | 123.3353 | -0.19684 | -0.22888 | 123.3261 | 62.027 | -0.19684 | 0.054931 | 123.3353 | -123.5458 | -123.4634
135.8438 | 123.2849 | -61.5509 | 61.7065 | -0.0031279 | 0.019656 | 0.015285 | -0.013063 | -0.0054687 | 0.063638 | 0.070276 | 0.50354 | 61.7889 | -61.8027 | 61.702 | -61.496 | -61.7386 | 0.036621 | 0.23346 | 61.821 | -61.7386 | -0.25177 | 0.082397 | 62.0544 | 123.2529 | -123.2025 | -0.18768 | 0.11444 | 62.3062 | 61.5875 | 61.7844 | 0.054931 | 123.3398 | 62.0544 | 123.3719 | -0.18768 | -0.18768 | 123.3398 | 62.0544 | -0.18768 | 0.054931 | 123.3719 | -123.5092 | -123.4451
137.5312 | 123.2574 | -61.5829 | 61.6699 | -0.0031279 | 0.022433 | 0.013576 | -0.014986 | -0.0035461 | 0.064066 | 0.069848 | 0.51727 | 61.7706 | -61.8118 | 61.734 | -61.4502 | -61.6837 | -0.19684 | 0.24719 | 61.7432 | -61.7706 | -0.22888 | 0.10071 | 62.1002 | 123.317 | -123.1201 | -0.18768 | 0.073242 | 62.3291 | 61.3861 | 61.8301 | 0.13275 | 123.3536 | 62.1002 | 123.3261 | -0.10071 | -0.18768 | 123.3536 | 62.1002 | -0.10071 | 0.13275 | 123.3261 | -123.4818 | -123.4406
139.2031 | 123.3582 | -61.4914 | 61.6882 | -0.0031279 | 0.016024 | 0.01208 | -0.019685 | -0.0063233 | 0.061502 | 0.070703 | 0.45319 | 61.7661 | -61.7981 | 61.7477 | -61.4044 | -61.6562 | -0.10986 | 0.32959 | 61.7569 | -61.7569 | -0.3067 | 0.07782 | 61.9446 | 123.2391 | -123.0927 | -0.2655 | 0.068665 | 62.2513 | 61.3815 | 61.821 | 0.086975 | 123.2574 | 61.9446 | 123.2483 | -0.16479 | -0.2655 | 123.2574 | 61.9446 | -0.16479 | 0.086975 | 123.2483 | -123.4863 | -123.4451
140.875 | 123.2712 | -61.4822 | 61.7523 | 0.012131 | 0.020083 | 0.0099441 | -0.011995 | -0.0063233 | 0.062143 | 0.070062 | 0.49439 | 61.8256 | -61.7981 | 61.7477 | -61.4136 | -61.6974 | 0.041199 | 0.27924 | 61.8484 | -61.7065 | -0.31586 | 0.073243 | 61.9766 | 123.23 | -123.1659 | -0.2243 | 0.096131 | 62.2925 | 61.5234 | 61.7615 | 0.068665 | 123.3078 | 61.9766 | 123.3307 | -0.21515 | -0.2243 | 123.3078 | 61.9766 | -0.21515 | 0.068665 | 123.3307 | -123.5504 | -123.4589
142.5469 | 123.3582 | -61.4548 | 61.7157 | 0.012131 | 0.019869 | 0.01208 | -0.018617 | -0.0069641 | 0.065561 | 0.06878 | 0.4715 | 61.8027 | -61.7706 | 61.7615 | -61.3907 | -61.6333 | -0.086975 | 0.32044 | 61.7615 | -61.734 | -0.31586 | 0.086975 | 61.9263 | 123.2162 | -123.1064 | -0.27924 | 0.045777 | 62.2421 | 61.3678 | 61.7752 | 0.064087 | 123.2574 | 61.9263 | 123.2162 | -0.17853 | -0.27924 | 123.2574 | 61.9263 | -0.17853 | 0.064087 | 123.2162 | -123.4863 | -123.4497
144.2031 | 123.2666 | -61.496 | 61.7249 | -0.0031279 | 0.017306 | 0.012721 | -0.013277 | -0.0046143 | 0.061288 | 0.06878 | 0.48065 | 61.8164 | -61.7889 | 61.7615 | -61.4182 | -61.6241 | -0.16937 | 0.21973 | 61.7935 | -61.6837 | -0.29297 | 0.091552 | 61.9766 | 123.2574 | -123.143 | -0.18768 | 0.068664 | 62.2696 | 61.3266 | 61.7157 | 0.07782 | 123.3124 | 61.9766 | 123.2895 | -0.12817 | -0.18768 | 123.3124 | 61.9766 | -0.12817 | 0.07782 | 123.2895 | -123.5138 | -123.4085
145.875 | 123.3765 | -61.4273 | 61.7157 | -0.0031279 | 0.019015 | 0.0084489 | -0.019899 | -0.0080323 | 0.062784 | 0.06878 | 0.46692 | 61.8027 | -61.7249 | 61.8118 | -61.3586 | -61.6013 | -0.07782 | 0.31586 | 61.821 | -61.6745 | -0.29755 | 0.086975 | 61.8942 | 123.2391 | -123.0743 | -0.24719 | 0.10529 | 62.1918 | 61.3495 | 61.7432 | 0.068664 | 123.23 | 61.8942 | 123.2483 | -0.17395 | -0.24719 | 123.23 | 61.8942 | -0.17395 | 0.068664 | 123.2483 | -123.4406 | -123.3902
147.5469 | 123.317 | -61.4365 | 61.7477 | -0.0031279 | 0.020083 | 0.01443 | -0.011568 | -0.0046143 | 0.063638 | 0.070276 | 0.43945 | 61.8896 | -61.7615 | 61.6974 | -61.4639 | -61.7294 | 0.073242 | 0.15564 | 61.9171 | -61.6745 | -0.32501 | 0.14191 | 61.8759 | 123.1338 | -123.2117 | -0.23804 | 0.16937 | 62.2009 | 61.5097 | 61.5921 | -0.027466 | 123.3261 | 61.8759 | 123.3536 | -0.29297 | -0.23804 | 123.3261 | 61.8759 | -0.29297 | -0.027466 | 123.3536 | -123.5092 | -123.4222
149.25 | 123.262 | -61.4639 | 61.7569 | 0.012131 | 0.018801 | 0.015498 | -0.016267 | -0.0065369 | 0.063852 | 0.069848 | 0.48523 | 61.8393 | -61.7249 | 61.8118 | -61.3678 | -61.5967 | -0.16022 | 0.24261 | 61.8118 | -61.6425 | -0.26093 | 0.082397 | 61.9492 | 123.2758 | -123.1247 | -0.17853 | 0.054932 | 62.2101 | 61.3037 | 61.7065 | 0.09613 | 123.3032 | 61.9492 | 123.2758 | -0.13275 | -0.17853 | 123.3032 | 61.9492 | -0.13275 | 0.09613 | 123.2758 | -123.4818 | -123.3994
150.9844 | 123.2803 | -61.409 | 61.8301 | -0.010757 | 0.019015 | 0.017848 | -0.010072 | -0.0069641 | 0.063425 | 0.070489 | 0.49896 | 61.8759 | -61.7294 | 61.821 | -61.3586 | -61.6104 | 0.045776 | 0.29297 | 61.9034 | -61.6196 | -0.32043 | 0.045777 | 61.908 | 123.23 | -123.1888 | -0.21057 | 0.073242 | 62.2284 | 61.4548 | 61.702 | 0.050354 | 123.2849 | 61.908 | 123.3124 | -0.20142 | -0.21057 | 123.2849 | 61.908 | -0.20142 | 0.050354 | 123.3124 | -123.5596 | -123.4497
152.6875 | 123.3307 | -61.3586 | 61.7798 | 0.0045011 | 0.019869 | 0.014003 | -0.017763 | -0.0071777 | 0.065347 | 0.068994 | 0.48065 | 61.8439 | -61.6928 | 61.8393 | -61.3174 | -61.5738 | -0.091553 | 0.32501 | 61.8668 | -61.6562 | -0.33417 | 0.064087 | 61.8393 | 123.1979 | -123.0972 | -0.29755 | 0.086975 | 62.1735 | 61.2671 | 61.6837 | 0.041199 | 123.2025 | 61.8393 | 123.2254 | -0.21515 | -0.29755 | 123.2025 | 61.8393 | -0.21515 | 0.041199 | 123.2254 | -123.4726 | -123.436
154.3594 | 123.3398 | -61.4319 | 61.7065 | -0.0031279 | 0.016878 | 0.013789 | -0.017549 | -0.0086731 | 0.064066 | 0.068994 | 0.44861 | 61.8256 | -61.7386 | 61.8118 | -61.3312 | -61.5784 | -0.11444 | 0.29297 | 61.8484 | -61.647 | -0.3067 | 0.11902 | 61.8805 | 123.2437 | -123.0377 | -0.21515 | 0.14191 | 62.1872 | 61.3174 | 61.7249 | 0.10071 | 123.2574 | 61.8805 | 123.2803 | -0.14648 | -0.21515 | 123.2574 | 61.8805 | -0.14648 | 0.10071 | 123.2803 | -123.4451 | -123.3536
156.0625 | 123.1293 | -69.4244 | 54.538 | 0.0045011 | 0.02051 | 0.0084489 | -0.0098587 | -0.0054687 | 0.060434 | 0.067926 | -0.64087 | 46.6507 | -74.4781 | 53.0685 | -80.2917 | -84.7504 | -3.6209 | 1.6708 | 46.5546 | -74.7757 | -5.0537 | -7.8873 | 68.7836 | 122.493 | -134.8297 | -5.3513 | -7.9834 | 73.8373 | 65.8035 | 71.0953 | -10.8673 | 116.0751 | 68.7836 | 115.979 | -15.3259 | -5.3513 | 116.0751 | 68.7836 | -15.3259 | -10.8673 | 115.979 | -129.0161 | -129.3137
157.7656 | 123.381 | -119.0414 | 4.1428 | -0.0031279 | 0.019015 | 0.012294 | -0.011568 | -0.0048279 | 0.062997 | 0.072839 | -4.8386 | 4.2252 | -119.4992 | 4.1336 | -118.9178 | -119.339 | -0.24719 | 0.032043 | 4.1977 | -119.3802 | -0.45776 | 0.082398 | 114.2029 | 123.175 | -123.0606 | -0.33875 | 0.054932 | 114.6606 | 118.7943 | 119.0735 | 0.1236 | 123.2666 | 114.2029 | 123.2391 | -0.29755 | -0.33875 | 123.2666 | 114.2029 | -0.29755 | 0.1236 | 123.2391 | -123.642 | -123.5229
159.4531 | 123.3124 | -119.3069 | 3.9185 | 0.0045011 | 0.019656 | 0.012935 | -0.014986 | -0.0058961 | 0.063638 | 0.07113 | -4.6371 | 4.0329 | -119.577 | 3.9825 | -119.0552 | -119.4626 | -0.39368 | 0.073242 | 4.0054 | -119.5175 | -0.27008 | 0.11444 | 114.6698 | 123.2895 | -122.9736 | -0.21057 | 0.086975 | 114.9399 | 118.9133 | 119.3802 | 0.25177 | 123.3398 | 114.6698 | 123.3124 | -0.15564 | -0.21057 | 123.3398 | 114.6698 | -0.15564 | 0.25177 | 123.3124 | -123.4955 | -123.436
161.125 | 123.3078 | -120.195 | 3.0899 | 0.012131 | 0.019015 | 0.013576 | -0.010286 | -0.0071777 | 0.064066 | 0.072412 | -4.8614 | 3.1769 | -120.488 | 3.0533 | -119.9982 | -120.4102 | -0.19226 | 0.045776 | 3.1631 | -120.4193 | -0.29297 | 0.086975 | 115.3336 | 123.2483 | -123.0881 | -0.22431 | 0.073242 | 115.6265 | 120.0027 | 120.2408 | 0.19684 | 123.3719 | 115.3336 | 123.3582 | -0.21515 | -0.22431 | 123.3719 | 115.3336 | -0.21515 | 0.19684 | 123.3582 | -123.5779 | -123.5092
162.7969 | 123.2758 | -119.4122 | 3.8544 | 0.0045011 | 0.019228 | 0.014217 | -0.015199 | -0.0048279 | 0.063211 | 0.072839 | -4.7195 | 3.9413 | -119.7052 | 3.8589 | -119.1788 | -119.5953 | -0.16479 | 0.10071 | 3.9322 | -119.632 | -0.29297 | 0.086975 | 114.6927 | 123.2712 | -123.0331 | -0.21973 | 0.07782 | 114.9857 | 119.2474 | 119.5129 | 0.23346 | 123.3536 | 114.6927 | 123.3444 | -0.18311 | -0.21973 | 123.3536 | 114.6927 | -0.18311 | 0.23346 | 123.3444 | -123.5596 | -123.4863
164.5312 | 123.3078 | -118.9636 | 4.2892 | 0.0045011 | 0.017092 | 0.0093033 | -0.013918 | -0.0041871 | 0.064279 | 0.071985 | -4.7974 | 4.3808 | -119.2703 | 4.2709 | -118.7347 | -119.1788 | -0.19684 | 0.07782 | 4.3808 | -119.1605 | -0.3067 | 0.091552 | 114.1663 | 123.2346 | -123.024 | -0.19684 | 0.091552 | 114.473 | 118.7668 | 119.0414 | 0.22888 | 123.3444 | 114.1663 | 123.3444 | -0.21515 | -0.19684 | 123.3444 | 114.1663 | -0.21515 | 0.22888 | 123.3444 | -123.5596 | -123.4497
166.2031 | 123.4497 | -119.7784 | 3.3783 | 0.012131 | 0.020083 | 0.0093033 | -0.021608 | -0.0091003 | 0.065134 | 0.070489 | -5.2505 | 3.3051 | -120.2682 | 3.3691 | -120.1309 | -119.9295 | -0.14191 | -0.064087 | 3.3508 | -120.0119 | -0.48981 | -0.073242 | 114.5279 | 123.1476 | -123.5092 | -0.23346 | -0.027466 | 115.0177 | 119.6365 | 119.7144 | -0.35248 | 123.0835 | 114.5279 | 123.1293 | -0.15106 | -0.23346 | 123.0835 | 114.5279 | -0.15106 | -0.35248 | 123.1293 | -123.6465 | -123.3902
167.8906 | 123.2254 | -57.3853 | 65.5838 | 0.012131 | 0.013888 | 0.013148 | -0.012422 | -0.0069641 | 0.063425 | 0.070276 | -6.3538 | 62.0224 | -60.791 | 66.188 | -54.5197 | -62.7686 | -8.3176 | -2.5909 | 62.7869 | -59.6054 | -3.4058 | -3.5614 | 51.0315 | 123.5733 | -120.1035 | -2.2202 | -2.7969 | 54.4373 | 49.0677 | 54.7943 | 2.8656 | 119.4077 | 51.0315 | 120.1721 | -5.3833 | -2.2202 | 119.4077 | 51.0315 | -5.3833 | 2.8656 | 120.1721 | -126.3748 | -125.1892
169.5625 | 123.4589 | -118.7485 | 4.3579 | 0.012131 | 0.020296 | 0.015071 | -0.016054 | -0.0078187 | 0.064279 | 0.07113 | -4.8111 | 4.4632 | -119.22 | 4.3167 | -118.689 | -119.0918 | -0.16022 | 0.032043 | 4.4495 | -119.133 | -0.4715 | 0.10529 | 113.9374 | 123.0652 | -123.0469 | -0.38452 | 0.091553 | 114.4089 | 118.5883 | 118.7805 | 0.059509 | 123.2117 | 113.9374 | 123.1979 | -0.34332 | -0.38452 | 123.2117 | 113.9374 | -0.34332 | 0.059509 | 123.1979 | -123.5779 | -123.4909
171.25 | 123.3032 | -118.6661 | 4.5044 | -0.0031279 | 0.018587 | 0.013362 | -0.016054 | -0.0067505 | 0.067483 | 0.072198 | -4.6371 | 4.5731 | -118.9865 | 4.5547 | -118.4555 | -118.8446 | -0.37079 | 0.11444 | 4.5639 | -118.9407 | -0.32043 | 0.068664 | 114.0289 | 123.2208 | -122.9599 | -0.27466 | 0.059509 | 114.3494 | 118.2953 | 118.7805 | 0.21057 | 123.2391 | 114.0289 | 123.23 | -0.17853 | -0.27466 | 123.2391 | 114.0289 | -0.17853 | 0.21057 | 123.23 | -123.4909 | -123.4451
173 | 123.3078 | -118.8354 | 4.3762 | 0.012131 | 0.017306 | 0.01443 | -0.016054 | -0.0056823 | 0.065561 | 0.073053 | -4.66 | 4.4174 | -119.133 | 4.4174 | -118.5608 | -118.9819 | -0.33417 | 0.1236 | 4.422 | -119.0414 | -0.29755 | 0.041198 | 114.1754 | 123.2529 | -122.937 | -0.20599 | 0.045776 | 114.473 | 118.5013 | 118.959 | 0.27466 | 123.2529 | 114.1754 | 123.2574 | -0.14648 | -0.20599 | 123.2529 | 114.1754 | -0.14648 | 0.27466 | 123.2574 | -123.5092 | -123.4177
174.6719 | 123.2803 | -118.9911 | 4.2709 | 0.0045011 | 0.019869 | 0.013148 | -0.018831 | -0.0063233 | 0.064706 | 0.071771 | -4.66 | 4.2984 | -119.2474 | 4.2984 | -118.7073 | -119.101 | -0.35706 | 0.10986 | 4.2984 | -119.1834 | -0.25635 | 0.027466 | 114.3311 | 123.2895 | -122.9782 | -0.19226 | 0.027466 | 114.5874 | 118.634 | 119.101 | 0.28381 | 123.2895 | 114.3311 | 123.2895 | -0.10986 | -0.19226 | 123.2895 | 114.3311 | -0.10986 | 0.28381 | 123.2895 | -123.5184 | -123.4543
176.3438 | 123.2986 | -118.8675 | 4.3716 | -0.0031279 | 0.019869 | 0.015498 | -0.010072 | -0.0063233 | 0.063211 | 0.069848 | -4.6967 | 4.5136 | -119.1238 | 4.3854 | -118.6249 | -119.0506 | -0.12817 | 0.032043 | 4.5227 | -119.0414 | -0.25635 | 0.14191 | 114.1708 | 123.2529 | -122.9965 | -0.17395 | 0.15106 | 114.4272 | 118.7393 | 118.8995 | 0.24262 | 123.381 | 114.1708 | 123.3902 | -0.1831 | -0.17395 | 123.381 | 114.1708 | -0.1831 | 0.24262 | 123.3902 | -123.4955 | -123.4131
178.0469 | 123.3078 | -119.1055 | 4.129 | -0.0031279 | 0.016238 | 0.01443 | -0.014772 | -0.0050415 | 0.062784 | 0.069421 | -4.8019 | 4.2023 | -119.4351 | 4.0009 | -118.9911 | -119.371 | -0.16937 | 0 | 4.184 | -119.3619 | -0.32959 | 0.073243 | 114.3036 | 123.1064 | -123.1201 | -0.25635 | 0.054932 | 114.6332 | 118.9362 | 119.1055 | 0.11444 | 123.3078 | 114.3036 | 123.2895 | -0.2655 | -0.25635 | 123.3078 | 114.3036 | -0.2655 | 0.11444 | 123.2895 | -123.5641 | -123.4909
179.7188 | 123.4131 | -118.7576 | 4.4128 | -0.0031279 | 0.019869 | 0.01443 | -0.017763 | -0.0063233 | 0.06492 | 0.070703 | -4.7745 | 4.5227 | -119.1193 | 4.335 | -118.6295 | -119.0643 | -0.073242 | 0.059509 | 4.5273 | -119.0781 | -0.36163 | 0.10986 | 113.9832 | 123.0927 | -123.0423 | -0.32044 | 0.11444 | 114.3448 | 118.6844 | 118.8171 | 0.12817 | 123.2803 | 113.9832 | 123.2849 | -0.3067 | -0.32044 | 123.2803 | 113.9832 | -0.3067 | 0.12817 | 123.2849 | -123.5321 | -123.4909
181.3906 | 123.3124 | -119.3802 | 3.7903 | 0.0045011 | 0.01816 | 0.011653 | -0.018831 | -0.0071777 | 0.067911 | 0.070489 | -4.7653 | 3.8773 | -119.6732 | 3.8544 | -119.1147 | -119.5038 | -0.33875 | 0.13733 | 3.8635 | -119.632 | -0.29297 | 0.086975 | 114.6149 | 123.2346 | -122.905 | -0.25177 | 0.073242 | 114.9078 | 119.0414 | 119.5175 | 0.2655 | 123.2574 | 114.6149 | 123.2437 | -0.1236 | -0.25177 | 123.2574 | 114.6149 | -0.1236 | 0.2655 | 123.2437 | -123.4634 | -123.4222
183.0781 | 123.349 | -119.0735 | 4.1199 | -0.0031279 | 0.017947 | 0.010158 | -0.014131 | -0.0063233 | 0.064066 | 0.073907 | -4.7104 | 4.2068 | -119.3573 | 4.1336 | -118.8583 | -119.2566 | -0.2243 | 0.11444 | 4.1977 | -119.3069 | -0.28381 | 0.086975 | 114.3631 | 123.2071 | -122.9782 | -0.23346 | 0.07782 | 114.6469 | 118.8492 | 119.1879 | 0.21515 | 123.2803 | 114.3631 | 123.2712 | -0.18311 | -0.23346 | 123.2803 | 114.3631 | -0.18311 | 0.21515 | 123.2712 | -123.4772 | -123.4268
184.75 | 123.2712 | -119.2154 | 4.01 | 0.0045011 | 0.019656 | 0.014644 | -0.010286 | -0.0058961 | 0.062357 | 0.072412 | -4.6326 | 4.129 | -119.4946 | 3.9322 | -119.0414 | -119.4534 | -0.11902 | 0.004578 | 4.129 | -119.4214 | -0.27924 | 0.11902 | 114.5828 | 123.1476 | -123.0515 | -0.20599 | 0.11902 | 114.8621 | 119.0964 | 119.22 | 0.17395 | 123.3444 | 114.5828 | 123.3444 | -0.23804 | -0.20599 | 123.3444 | 114.5828 | -0.23804 | 0.17395 | 123.3444 | -123.5046 | -123.4314
186.4219 | 123.2712 | -119.2657 | 3.9276 | -0.010757 | 0.020296 | 0.0082351 | -0.015413 | -0.0067505 | 0.063638 | 0.071771 | -4.7882 | 4.0421 | -119.5724 | 3.9139 | -119.0643 | -119.4809 | -0.12817 | 0.082397 | 4.0146 | -119.5358 | -0.3067 | 0.11444 | 114.4775 | 123.1796 | -122.9919 | -0.27008 | 0.086975 | 114.7842 | 119.1376 | 119.3481 | 0.20142 | 123.3078 | 114.4775 | 123.2803 | -0.21515 | -0.27008 | 123.3078 | 114.4775 | -0.21515 | 0.20142 | 123.2803 | -123.5001 | -123.4634
188.0938 | 123.2346 | -119.2657 | 3.9459 | 0.0045011 | 0.018587 | 0.015285 | -0.013277 | -0.0076049 | 0.064279 | 0.069848 | -4.7287 | 4.0741 | -119.5679 | 3.9459 | -119.0323 | -119.4626 | -0.15106 | 0.1236 | 4.0329 | -119.4855 | -0.30212 | 0.12817 | 114.537 | 123.2117 | -122.9782 | -0.21973 | 0.086975 | 114.8392 | 119.1147 | 119.3893 | 0.23346 | 123.3398 | 114.537 | 123.2986 | -0.19684 | -0.21973 | 123.3398 | 114.537 | -0.19684 | 0.23346 | 123.2986 | -123.5138 | -123.4314
189.7656 | 123.2986 | -119.1513 | 4.0146 | 0.0045011 | 0.016451 | 0.016994 | -0.019045 | -0.0076049 | 0.062143 | 0.07113 | -4.7104 | 4.097 | -119.4168 | 4.0649 | -118.895 | -119.3298 | -0.2655 | 0.16022 | 4.097 | -119.3893 | -0.2655 | 0.082398 | 114.4409 | 123.2162 | -122.9095 | -0.23804 | 0.082398 | 114.7064 | 118.8858 | 119.3115 | 0.25635 | 123.2483 | 114.4409 | 123.2483 | -0.17853 | -0.23804 | 123.2483 | 114.4409 | -0.17853 | 0.25635 | 123.2483 | -123.4314 | -123.4039
191.4375 | 123.4039 | -122.2916 | 0.79193 | 0.0045011 | 0.016238 | 0.014644 | -0.019258 | -0.0067505 | 0.065988 | 0.073907 | -5.2551 | 0.86975 | -122.699 | 0.737 | -122.2 | -122.6303 | -0.3067 | 0.045776 | 0.84686 | -122.6624 | -0.40741 | 0.07782 | 117.0364 | 123.0286 | -122.9919 | -0.37079 | 0.054932 | 117.4438 | 121.9849 | 122.3373 | 0.091553 | 123.1613 | 117.0364 | 123.1384 | -0.33874 | -0.37079 | 123.1613 | 117.0364 | -0.33874 | 0.091553 | 123.1384 | -123.4909 | -123.4543
193.1562 | 123.262 | -122.3099 | 0.92468 | 0.0045011 | 0.017519 | 0.011226 | -0.014986 | -0.0058961 | 0.064066 | 0.070062 | -5.1682 | 0.92926 | -122.6303 | 0.92468 | -122.0718 | -122.4747 | -0.3891 | 0.1236 | 0.93842 | -122.5571 | -0.32043 | 0.004577 | 117.1417 | 123.2346 | -122.9965 | -0.24719 | 0.013733 | 117.4622 | 121.9208 | 122.4335 | 0.23804 | 123.2391 | 117.1417 | 123.2483 | -0.16479 | -0.24719 | 123.2391 | 117.1417 | -0.16479 | 0.23804 | 123.2483 | -123.555 | -123.4818
194.9688 | 123.3994 | -122.2092 | 0.95673 | -0.0031279 | 0.015597 | 0.011012 | -0.017763 | -0.0065369 | 0.064493 | 0.068567 | -5.2689 | 1.0117 | -122.5571 | 0.91095 | -122.0627 | -122.4747 | -0.29755 | 0.050354 | 1.0025 | -122.4884 | -0.3479 | 0.054932 | 116.9403 | 123.1201 | -123.0194 | -0.27924 | 0.045776 | 117.2882 | 121.9116 | 122.2595 | 0.14648 | 123.2208 | 116.9403 | 123.2117 | -0.2655 | -0.27924 | 123.2208 | 116.9403 | -0.2655 | 0.14648 | 123.2117 | -123.5138 | -123.4451
196.7031 | 123.3765 | -122.1451 | 1.0254 | -0.0031279 | 0.019015 | 0.015071 | -0.016054 | -0.0078187 | 0.065561 | 0.070489 | -5.2414 | 1.1169 | -122.4472 | 1.0208 | -121.962 | -122.3648 | -0.3067 | 0.082397 | 1.0986 | -122.4792 | -0.30212 | 0.091552 | 116.9037 | 123.1659 | -122.9874 | -0.33417 | 0.073242 | 117.2058 | 121.8384 | 122.2275 | 0.18311 | 123.262 | 116.9037 | 123.2437 | -0.21973 | -0.33417 | 123.262 | 116.9037 | -0.21973 | 0.18311 | 123.2437 | -123.4726 | -123.5046
198.3906 | 123.2666 | -122.3328 | 0.92926 | -0.0031279 | 0.019656 | 0.014644 | -0.012422 | -0.0069641 | 0.064706 | 0.071344 | -5.246 | 0.98419 | -122.6669 | 0.87433 | -122.1405 | -122.5433 | -0.28839 | 0.07782 | 0.9613 | -122.5754 | -0.33417 | 0.054932 | 117.0868 | 123.2071 | -123.0698 | -0.24261 | 0.032044 | 117.421 | 122.0444 | 122.4106 | 0.19226 | 123.317 | 117.0868 | 123.2941 | -0.21057 | -0.24261 | 123.317 | 117.0868 | -0.21057 | 0.19226 | 123.2941 | -123.5962 | -123.5046
200.125 | 123.2758 | -122.2549 | 0.99335 | -0.0031279 | 0.018801 | 0.014857 | -0.01285 | -0.0058961 | 0.062784 | 0.06878 | -5.2597 | 1.0757 | -122.6028 | 0.91095 | -122.0993 | -122.5204 | -0.1831 | 0.022888 | 1.0574 | -122.5342 | -0.3479 | 0.082398 | 116.9952 | 123.1659 | -123.0927 | -0.27924 | 0.064087 | 117.3431 | 122.0718 | 122.2778 | 0.15564 | 123.3307 | 116.9952 | 123.3124 | -0.2655 | -0.27924 | 123.3307 | 116.9952 | -0.2655 | 0.15564 | 123.3124 | -123.5962 | -123.5275
201.8438 | 123.381 | -122.374 | 0.82855 | -0.0031279 | 0.018801 | 0.0095169 | -0.018831 | -0.0076049 | 0.066415 | 0.070489 | -5.2917 | 0.9201 | -122.6944 | 0.8194 | -122.1771 | -122.6074 | -0.29755 | 0.054932 | 0.89722 | -122.6669 | -0.32043 | 0.091553 | 117.0822 | 123.1934 | -123.0057 | -0.29297 | 0.068665 | 117.4026 | 122.0764 | 122.4289 | 0.19684 | 123.2941 | 117.0822 | 123.2712 | -0.23346 | -0.29297 | 123.2941 | 117.0822 | -0.23346 | 0.19684 | 123.2712 | -123.5229 | -123.4955
203.5781 | 123.2529 | -122.3602 | 0.94757 | -0.010757 | 0.017306 | 0.013576 | -0.013277 | -0.0061097 | 0.063211 | 0.07113 | -5.1819 | 0.94299 | -122.6715 | 0.92926 | -122.0856 | -122.4976 | -0.34332 | 0.11902 | 0.94299 | -122.5433 | -0.31128 | -0.004578 | 117.1783 | 123.2895 | -123.0331 | -0.18311 | -0.004578 | 117.4896 | 122.0169 | 122.4792 | 0.27466 | 123.3032 | 117.1783 | 123.3032 | -0.13733 | -0.18311 | 123.3032 | 117.1783 | -0.13733 | 0.27466 | 123.3032 | -123.6191 | -123.4909
205.25 | 123.3582 | -122.3328 | 0.86975 | 0.0045011 | 0.017947 | 0.011439 | -0.013277 | -0.0078187 | 0.064279 | 0.069421 | -5.2734 | 0.96588 | -122.7173 | 0.82398 | -122.1954 | -122.6395 | -0.10529 | 0.082397 | 0.9613 | -122.6349 | -0.38452 | 0.09613 | 117.0593 | 123.1567 | -123.0652 | -0.30212 | 0.091553 | 117.4438 | 122.2275 | 122.4152 | 0.13733 | 123.2986 | 117.0593 | 123.2941 | -0.3067 | -0.30212 | 123.2986 | 117.0593 | -0.3067 | 0.13733 | 123.2941 | -123.587 | -123.5046
206.9844 | 123.2895 | -122.3831 | 0.89264 | 0.012131 | 0.020724 | 0.01443 | -0.012636 | -0.0067505 | 0.065561 | 0.071557 | -5.278 | 0.95673 | -122.7173 | 0.76904 | -122.2366 | -122.6715 | -0.19226 | -0.004578 | 0.94757 | -122.6486 | -0.33417 | 0.064087 | 117.1051 | 123.1522 | -123.1293 | -0.2655 | 0.054932 | 117.4393 | 122.1909 | 122.3785 | 0.14648 | 123.3398 | 117.1051 | 123.3307 | -0.28839 | -0.2655 | 123.3398 | 117.1051 | -0.28839 | 0.14648 | 123.3307 | -123.6099 | -123.5413
208.7188 | 123.317 | -122.3053 | 0.91553 | -0.010757 | 0.01816 | 0.012508 | -0.019472 | -0.0086731 | 0.065775 | 0.069421 | -5.2185 | 0.96588 | -122.5891 | 0.97046 | -122.0261 | -122.4564 | -0.31586 | 0.17395 | 0.95673 | -122.5616 | -0.28381 | 0.050354 | 117.0868 | 123.2758 | -122.9416 | -0.25635 | 0.041199 | 117.3706 | 121.9894 | 122.4792 | 0.27924 | 123.2712 | 117.0868 | 123.262 | -0.15106 | -0.25635 | 123.2712 | 117.0868 | -0.15106 | 0.27924 | 123.262 | -123.5046 | -123.4772
210.4531 | 123.3536 | -122.2321 | 0.97046 | -0.0031279 | 0.017947 | 0.0088761 | -0.016267 | -0.0084595 | 0.06492 | 0.069635 | -5.2231 | 1.0483 | -122.5754 | 0.97504 | -122.0306 | -122.4747 | -0.19684 | 0.1236 | 1.0437 | -122.5662 | -0.34332 | 0.07782 | 117.009 | 123.2071 | -123.0011 | -0.33417 | 0.073242 | 117.3523 | 122.0352 | 122.3557 | 0.20142 | 123.2803 | 117.009 | 123.2758 | -0.24261 | -0.33417 | 123.2803 | 117.009 | -0.24261 | 0.20142 | 123.2758 | -123.5458 | -123.5367
212.1094 | 123.2437 | -122.2412 | 1.03 | 0.0045011 | 0.017519 | 0.014857 | -0.015199 | -0.0071777 | 0.062784 | 0.069848 | -5.1956 | 1.062 | -122.5204 | 1.0162 | -121.9894 | -122.3877 | -0.36621 | 0.10986 | 1.0391 | -122.4609 | -0.27924 | 0.032044 | 117.0456 | 123.2574 | -123.0194 | -0.21973 | 0.009156 | 117.3248 | 121.875 | 122.3511 | 0.25177 | 123.3032 | 117.0456 | 123.2803 | -0.14648 | -0.21973 | 123.3032 | 117.0456 | -0.14648 | 0.25177 | 123.2803 | -123.5504 | -123.4909
213.7812 | 123.2941 | -121.6782 | 1.5976 | 0.012131 | 0.018374 | 0.011439 | -0.01285 | -0.0044007 | 0.063638 | 0.071771 | -5.1498 | 1.6617 | -122.0215 | 1.4786 | -121.5454 | -121.9711 | -0.11444 | 0.036621 | 1.6479 | -121.9482 | -0.34332 | 0.064087 | 116.5283 | 123.1567 | -123.143 | -0.27008 | 0.050354 | 116.8716 | 121.5637 | 121.7148 | 0.13275 | 123.3398 | 116.5283 | 123.3261 | -0.29297 | -0.27008 | 123.3398 | 116.5283 | -0.29297 | 0.13275 | 123.3261 | -123.6191 | -123.5458
215.4688 | 123.3994 | -121.6141 | 1.5564 | 0.0045011 | 0.019015 | 0.010371 | -0.017763 | -0.0069641 | 0.065775 | 0.070062 | -5.1361 | 1.6434 | -121.9986 | 1.5427 | -121.4584 | -121.8933 | -0.15564 | 0.10986 | 1.6159 | -121.962 | -0.38452 | 0.086976 | 116.478 | 123.1567 | -123.0148 | -0.3479 | 0.05951 | 116.8625 | 121.4584 | 121.7239 | 0.15564 | 123.2574 | 116.478 | 123.23 | -0.27924 | -0.3479 | 123.2574 | 116.478 | -0.27924 | 0.15564 | 123.23 | -123.555 | -123.5184
217.1406 | 123.3948 | -120.3369 | 2.7374 | -0.0031279 | 0.017092 | 0.0088761 | -0.017122 | -0.0048279 | 0.064279 | 0.070916 | -4.9347 | 2.8381 | -120.7031 | 2.8152 | -120.1263 | -120.5612 | -0.33417 | 0.15106 | 2.8244 | -120.6528 | -0.36621 | 0.10071 | 115.4022 | 123.1522 | -122.8638 | -0.31586 | 0.086975 | 115.7684 | 120.0027 | 120.488 | 0.21057 | 123.175 | 115.4022 | 123.1613 | -0.2243 | -0.31586 | 123.175 | 115.4022 | -0.2243 | 0.21057 | 123.1613 | -123.4406 | -123.3902
218.8125 | 123.3261 | -120.6802 | 2.4216 | 0.012131 | 0.019015 | 0.013362 | -0.01584 | -0.0088867 | 0.065988 | 0.070062 | -5.0491 | 2.4902 | -121.0327 | 2.417 | -120.5338 | -120.9274 | -0.30212 | 0.064087 | 2.4857 | -120.9686 | -0.35248 | 0.068664 | 115.6311 | 123.0972 | -122.9553 | -0.28839 | 0.064087 | 115.9836 | 120.3781 | 120.7443 | 0.14648 | 123.1705 | 115.6311 | 123.1659 | -0.24719 | -0.28839 | 123.1705 | 115.6311 | -0.24719 | 0.14648 | 123.1659 | -123.4543 | -123.3902
220.5625 | 123.1979 | -120.8771 | 2.2797 | -0.010757 | 0.015169 | 0.0097305 | -0.01285 | -0.0073913 | 0.064066 | 0.070916 | -5.04 | 2.33 | -121.2296 | 2.2476 | -120.6711 | -121.0831 | -0.3067 | 0.10986 | 2.3026 | -121.1426 | -0.35248 | 0.050354 | 115.8371 | 123.1247 | -122.9507 | -0.2655 | 0.022888 | 116.1896 | 120.5704 | 120.9869 | 0.20599 | 123.2071 | 115.8371 | 123.1796 | -0.20599 | -0.2655 | 123.2071 | 115.8371 | -0.20599 | 0.20599 | 123.1796 | -123.5092 | -123.4222
222.2188 | 123.1796 | -120.5109 | 2.6688 | 0.0045011 | 0.017733 | 0.01208 | -0.012209 | -0.0069641 | 0.062784 | 0.068994 | -4.8706 | 2.7695 | -120.7901 | 2.623 | -120.3003 | -120.7169 | -0.16479 | 0.10071 | 2.7054 | -120.7535 | -0.27924 | 0.10071 | 115.6403 | 123.1338 | -122.9691 | -0.24262 | 0.036621 | 115.9195 | 120.3461 | 120.6116 | 0.21057 | 123.2803 | 115.6403 | 123.2162 | -0.20599 | -0.24262 | 123.2803 | 115.6403 | -0.20599 | 0.21057 | 123.2162 | -123.4589 | -123.4222
223.9531 | 123.2803 | -120.7352 | 2.3071 | -0.0031279 | 0.019442 | 0.010371 | -0.017122 | -0.0080323 | 0.064066 | 0.070489 | -5.0995 | 2.4353 | -121.1243 | 2.2568 | -120.6482 | -121.0739 | -0.1236 | 0.064087 | 2.4124 | -121.0876 | -0.3891 | 0.12817 | 115.6357 | 122.9919 | -122.9553 | -0.35248 | 0.10529 | 116.0248 | 120.6116 | 120.7993 | 0.086975 | 123.1705 | 115.6357 | 123.1476 | -0.33875 | -0.35248 | 123.1705 | 115.6357 | -0.33875 | 0.086975 | 123.1476 | -123.4314 | -123.3948
225.625 | 123.2483 | -120.7535 | 2.3529 | 0.0045011 | 0.019442 | 0.015498 | -0.014558 | -0.0065369 | 0.064493 | 0.070276 | -5.0079 | 2.4124 | -121.0693 | 2.3666 | -120.5063 | -120.9137 | -0.31586 | 0.12817 | 2.4033 | -120.9778 | -0.31586 | 0.05951 | 115.7455 | 123.1201 | -122.8592 | -0.2243 | 0.050354 | 116.0614 | 120.4376 | 120.8817 | 0.24719 | 123.1659 | 115.7455 | 123.1567 | -0.16022 | -0.2243 | 123.1659 | 115.7455 | -0.16022 | 0.24719 | 123.1567 | -123.4222 | -123.3307
227.3594 | 123.1659 | -120.5429 | 2.5726 | 0.0045011 | 0.019228 | 0.012508 | -0.013704 | -0.0067505 | 0.063211 | 0.069848 | -5.0079 | 2.6367 | -120.8862 | 2.5131 | -120.3827 | -120.8267 | -0.26093 | -0.004578 | 2.6367 | -120.7901 | -0.34332 | 0.064087 | 115.535 | 123.056 | -122.9553 | -0.24719 | 0.064087 | 115.8783 | 120.282 | 120.5383 | 0.16022 | 123.1796 | 115.535 | 123.1796 | -0.28381 | -0.24719 | 123.1796 | 115.535 | -0.28381 | 0.16022 | 123.1796 | -123.4589 | -123.3627
229.0781 | 123.1018 | -120.9 | 2.2385 | 0.0045011 | 0.022005 | 0.015926 | -0.013704 | -0.0052551 | 0.063852 | 0.068139 | -4.9759 | 2.298 | -121.1655 | 2.2018 | -120.6848 | -121.1151 | -0.12817 | 0.17395 | 2.2797 | -121.138 | -0.2655 | 0.05951 | 115.9241 | 123.1018 | -122.9233 | -0.23804 | 0.041199 | 116.1896 | 120.7718 | 121.0739 | 0.21515 | 123.1979 | 115.9241 | 123.1796 | -0.21515 | -0.23804 | 123.1979 | 115.9241 | -0.21515 | 0.21515 | 123.1796 | -123.4039 | -123.3765
230.75 | 123.1476 | -119.2978 | 3.598 | 0.0045011 | 0.020083 | 0.0075943 | -0.017976 | -0.0076049 | 0.062997 | 0.070489 | -5.1956 | 3.6346 | -119.7601 | 3.6301 | -119.0781 | -119.4763 | -0.2655 | 0.2243 | 3.6301 | -119.6182 | -0.46234 | 0.036622 | 114.1022 | 122.9279 | -122.6761 | -0.32043 | 0.032044 | 114.5645 | 119.0323 | 119.5221 | 0.21973 | 122.9324 | 114.1022 | 122.9279 | -0.17853 | -0.32043 | 122.9324 | 114.1022 | -0.17853 | 0.21973 | 122.9279 | -123.3582 | -123.2162
232.4844 | 123.3032 | -118.515 | 4.4998 | 0.0045011 | 0.014956 | 0.011653 | -0.016695 | -0.0076049 | 0.068338 | 0.072412 | -4.6371 | 4.6005 | -118.8812 | 4.5136 | -118.3548 | -118.7576 | -0.20599 | 0.13275 | 4.5685 | -118.8217 | -0.36621 | 0.10071 | 113.8779 | 123.0286 | -122.8546 | -0.3067 | 0.068664 | 114.2441 | 118.309 | 118.6478 | 0.16022 | 123.1155 | 113.8779 | 123.0835 | -0.24261 | -0.3067 | 123.1155 | 113.8779 | -0.24261 | 0.16022 | 123.0835 | -123.381 | -123.3215
234.2188 | 123.2025 | -118.1992 | 4.9164 | 0.0045011 | 0.020083 | 0.0097305 | -0.013063 | -0.0050415 | 0.064279 | 0.071344 | -4.6234 | 5.0171 | -118.5516 | 4.8935 | -118.0344 | -118.4372 | -0.19684 | 0.041199 | 5.0034 | -118.428 | -0.35248 | 0.10071 | 113.5757 | 123.0927 | -122.9507 | -0.22888 | 0.086975 | 113.9282 | 118.0023 | 118.2404 | 0.16479 | 123.2162 | 113.5757 | 123.2025 | -0.23804 | -0.22888 | 123.2162 | 113.5757 | -0.23804 | 0.16479 | 123.2025 | -123.468 | -123.3444
235.9531 | 123.2025 | -118.2724 | 4.9026 | 0.012131 | 0.01816 | 0.014003 | -0.012209 | -0.0071777 | 0.063852 | 0.070916 | -4.5593 | 4.9347 | -118.6111 | 4.8569 | -118.071 | -118.4875 | -0.14191 | 0.15106 | 4.953 | -118.5013 | -0.33874 | 0.032043 | 113.7131 | 123.1293 | -122.9736 | -0.22888 | 0.050354 | 114.0518 | 118.1305 | 118.4235 | 0.20142 | 123.2071 | 113.7131 | 123.2254 | -0.21515 | -0.22888 | 123.2071 | 113.7131 | -0.21515 | 0.20142 | 123.2254 | -123.5138 | -123.4039
237.6875 | 123.2758 | -118.5745 | 4.5547 | 0.012131 | 0.016665 | 0.0095169 | -0.013918 | -0.0048279 | 0.063211 | 0.070916 | -4.6921 | 4.6829 | -118.9224 | 4.5547 | -118.3456 | -118.7897 | -0.10071 | 0.10529 | 4.6692 | -118.8309 | -0.3479 | 0.12817 | 113.8824 | 123.1293 | -122.9004 | -0.25635 | 0.11444 | 114.2303 | 118.4738 | 118.6798 | 0.22888 | 123.2574 | 113.8824 | 123.2437 | -0.21515 | -0.25635 | 123.2574 | 113.8824 | -0.21515 | 0.22888 | 123.2437 | -123.4772 | -123.3856
239.3594 | 123.2346 | -118.1763 | 5.0079 | 0.012131 | 0.019442 | 0.01443 | -0.01285 | -0.0048279 | 0.06257 | 0.069848 | -4.5639 | 5.0491 | -118.5196 | 4.8889 | -118.0435 | -118.4326 | -0.10529 | 0.036621 | 5.0491 | -118.4189 | -0.34332 | 0.041198 | 113.6124 | 123.0652 | -123.0515 | -0.24261 | 0.041198 | 113.9557 | 118.071 | 118.2129 | 0.13275 | 123.2254 | 113.6124 | 123.2254 | -0.25635 | -0.24261 | 123.2254 | 113.6124 | -0.25635 | 0.13275 | 123.2254 | -123.5275 | -123.4268
241.0938 | 123.2437 | -115.1825 | 7.9742 | -0.0031279 | 0.017519 | 0.014857 | -0.019472 | -0.0054687 | 0.066843 | 0.071344 | -4.1794 | 8.0292 | -115.4617 | 7.9651 | -114.9765 | -115.3748 | -0.31586 | 0.086975 | 8.0063 | -115.4114 | -0.27924 | 0.054932 | 111.0031 | 123.1476 | -122.9507 | -0.22888 | 0.032044 | 111.2823 | 114.8666 | 115.2695 | 0.20599 | 123.2117 | 111.0031 | 123.1888 | -0.19226 | -0.22888 | 123.2117 | 111.0031 | -0.19226 | 0.20599 | 123.1888 | -123.436 | -123.3856
242.8438 | 123.2895 | -115.8142 | 7.2968 | -0.0031279 | 0.017947 | 0.013148 | -0.017976 | -0.0080323 | 0.063638 | 0.069207 | -4.2526 | 7.3425 | -116.1118 | 7.4066 | -115.5533 | -115.9561 | -0.30212 | 0.17853 | 7.3471 | -116.0889 | -0.29755 | 0.045776 | 111.5616 | 123.2208 | -122.85 | -0.27466 | 0.050354 | 111.8591 | 115.5121 | 115.9927 | 0.26093 | 123.1567 | 111.5616 | 123.1613 | -0.14191 | -0.27466 | 123.1567 | 111.5616 | -0.14191 | 0.26093 | 123.1613 | -123.4085 | -123.3856
244.5312 | 123.0469 | -94.7067 | 28.3997 | -0.0031279 | 0.017519 | 0.0088761 | -0.01285 | -0.0061097 | 0.063852 | 0.068994 | -1.6342 | 28.4592 | -95.0638 | 28.4225 | -94.6106 | -94.9768 | 0.027466 | 0.17395 | 28.5049 | -94.9402 | -0.35706 | 0.059509 | 93.0725 | 123.1293 | -123.0103 | -0.23346 | 0.10529 | 93.4296 | 94.7342 | 94.8807 | 0.09613 | 123.1659 | 93.0725 | 123.2117 | -0.27008 | -0.23346 | 123.1659 | 93.0725 | -0.27008 | 0.09613 | 123.2117 | -123.4634 | -123.3398
246.2656 | 123.0331 | -94.6426 | 28.4454 | 0.0045011 | 0.016878 | 0.0088761 | -0.017763 | -0.0050415 | 0.065347 | 0.069207 | -1.6434 | 28.5004 | -94.9677 | 28.5095 | -94.5282 | -94.8578 | -0.17853 | 0.14191 | 28.5141 | -94.9265 | -0.32501 | 0.054931 | 92.9993 | 123.1522 | -122.9736 | -0.28381 | 0.068664 | 93.3243 | 94.4641 | 94.7845 | 0.11444 | 123.143 | 92.9993 | 123.1567 | -0.21515 | -0.28381 | 123.143 | 92.9993 | -0.21515 | 0.11444 | 123.1567 | -123.4131 | -123.3719
248.0156 | 123.2986 | -94.5786 | 28.4821 | 0.0045011 | 0.017306 | 0.0090897 | -0.018404 | -0.0069641 | 0.06492 | 0.069635 | -1.561 | 28.5141 | -94.9631 | 28.5828 | -94.4595 | -94.8395 | -0.07782 | 0.28381 | 28.5187 | -94.9356 | -0.38452 | 0.032043 | 93.0176 | 123.1613 | -122.9416 | -0.35706 | 0.036621 | 93.4021 | 94.5007 | 94.8624 | 0.11902 | 123.0927 | 93.0176 | 123.0972 | -0.26093 | -0.35706 | 123.0927 | 93.0176 | -0.26093 | 0.11902 | 123.0972 | -123.4451 | -123.4177
249.6875 | 123.2986 | -94.4962 | 28.5828 | 0.0045011 | 0.016238 | 0.014644 | -0.015199 | -0.0086731 | 0.065775 | 0.070489 | -1.5793 | 28.6423 | -94.8441 | 28.7109 | -94.3588 | -94.7159 | -0.10986 | 0.24261 | 28.6423 | -94.7891 | -0.3479 | 0.059509 | 92.9169 | 123.2071 | -122.9416 | -0.29297 | 0.059509 | 93.2648 | 94.3863 | 94.7388 | 0.13733 | 123.1384 | 92.9169 | 123.1384 | -0.21973 | -0.29297 | 123.1384 | 92.9169 | -0.21973 | 0.13733 | 123.1384 | -123.4268 | -123.3719
251.4219 | 123.3215 | -117.0364 | 6.0471 | -0.010757 | 0.016024 | 0.010585 | -0.0096451 | -0.0058961 | 0.06257 | 0.072198 | -4.454 | 6.1111 | -117.5034 | 6.0425 | -116.9403 | -117.3752 | -0.12817 | 0.10529 | 6.1066 | -117.3798 | -0.46692 | 0.064087 | 112.5824 | 123.0789 | -122.9874 | -0.34332 | 0.059509 | 113.0493 | 116.9083 | 117.1417 | 0.09613 | 123.1476 | 112.5824 | 123.143 | -0.33875 | -0.34332 | 123.1476 | 112.5824 | -0.33875 | 0.09613 | 123.143 | -123.5504 | -123.4268
253.1719 | 123.2391 | -117.3935 | 5.7999 | -0.0031279 | 0.017947 | 0.012721 | -0.011995 | -0.0048279 | 0.062997 | 0.070703 | -4.4678 | 5.8411 | -117.7643 | 5.777 | -117.1921 | -117.6453 | -0.14191 | 0.13275 | 5.8548 | -117.6361 | -0.37079 | 0.041198 | 112.9257 | 123.1705 | -122.9919 | -0.24261 | 0.054931 | 113.2965 | 117.2516 | 117.5262 | 0.20142 | 123.2346 | 112.9257 | 123.2483 | -0.25177 | -0.24261 | 123.2346 | 112.9257 | -0.25177 | 0.20142 | 123.2483 | -123.5641 | -123.436
254.9062 | 123.23 | -117.3065 | 5.8685 | 0.0045011 | 0.019015 | 0.0090897 | -0.013918 | -0.0054687 | 0.065988 | 0.072198 | -4.454 | 5.9052 | -117.6361 | 5.896 | -117.0822 | -117.485 | -0.33417 | 0.11444 | 5.8823 | -117.5446 | -0.32959 | 0.036621 | 112.8525 | 123.2025 | -122.9507 | -0.23804 | 0.013733 | 113.1821 | 116.9724 | 117.421 | 0.22431 | 123.2117 | 112.8525 | 123.1888 | -0.17853 | -0.23804 | 123.2117 | 112.8525 | -0.17853 | 0.22431 | 123.1888 | -123.5046 | -123.4131
256.6094 | 123.2391 | -117.0914 | 6.102 | 0.0045011 | 0.01816 | 0.011012 | -0.01285 | -0.0067505 | 0.065775 | 0.07113 | -4.4815 | 6.1615 | -117.4301 | 6.0745 | -116.9083 | -117.3065 | -0.26093 | 0.07782 | 6.134 | -117.3248 | -0.33875 | 0.059509 | 112.6099 | 123.1659 | -123.0103 | -0.23346 | 0.032043 | 112.9486 | 116.8304 | 117.1692 | 0.18311 | 123.2529 | 112.6099 | 123.2254 | -0.21515 | -0.23346 | 123.2529 | 112.6099 | -0.21515 | 0.18311 | 123.2254 | -123.5321 | -123.4268
258.2812 | 123.2483 | -117.1005 | 6.1295 | 0.0045011 | 0.016451 | 0.011653 | -0.01285 | -0.0065369 | 0.06257 | 0.071557 | -4.4586 | 6.1707 | -117.4347 | 6.0791 | -116.9266 | -117.3477 | -0.13275 | 0.050354 | 6.1661 | -117.3294 | -0.33417 | 0.041198 | 112.6419 | 123.1796 | -123.056 | -0.22888 | 0.036621 | 112.9761 | 116.9678 | 117.1509 | 0.17395 | 123.2712 | 112.6419 | 123.2666 | -0.24719 | -0.22888 | 123.2712 | 112.6419 | -0.24719 | 0.17395 | 123.2666 | -123.5641 | -123.4589
260.0312 | 123.3444 | -117.0959 | 6.0516 | -0.010757 | 0.017947 | 0.011226 | -0.021181 | -0.0069641 | 0.065561 | 0.069635 | -4.5593 | 6.1249 | -117.4164 | 6.0562 | -116.9174 | -117.3386 | -0.29755 | 0.064087 | 6.0883 | -117.3935 | -0.32044 | 0.073242 | 112.5366 | 123.1522 | -122.9691 | -0.29755 | 0.036621 | 112.8571 | 116.7984 | 117.16 | 0.17853 | 123.2208 | 112.5366 | 123.1842 | -0.24262 | -0.29755 | 123.2208 | 112.5366 | -0.24262 | 0.17853 | 123.1842 | -123.468 | -123.4451
261.7344 | 123.3032 | -116.1713 | 6.9901 | -0.0031279 | 0.01581 | 0.0099441 | -0.018831 | -0.0071777 | 0.066415 | 0.070062 | -4.303 | 7.0358 | -116.4963 | 7.077 | -115.9287 | -116.3269 | -0.31586 | 0.19684 | 7.0221 | -116.4459 | -0.32501 | 0.045777 | 111.8683 | 123.2483 | -122.9187 | -0.27466 | 0.032044 | 112.1933 | 115.8554 | 116.3681 | 0.24262 | 123.2071 | 111.8683 | 123.1934 | -0.15564 | -0.27466 | 123.2071 | 111.8683 | -0.15564 | 0.24262 | 123.1934 | -123.4863 | -123.436
263.4062 | 123.2529 | -116.8716 | 6.2942 | 0.012131 | 0.020083 | 0.012294 | -0.013063 | -0.0065369 | 0.065347 | 0.07113 | -4.4861 | 6.3492 | -117.2745 | 6.2439 | -116.7389 | -117.1417 | -0.14191 | 0.032043 | 6.3766 | -117.1646 | -0.40283 | 0.054932 | 112.3856 | 123.1155 | -123.0331 | -0.29297 | 0.082398 | 112.7884 | 116.7297 | 116.9037 | 0.13275 | 123.2208 | 112.3856 | 123.2483 | -0.27008 | -0.29297 | 123.2208 | 112.3856 | -0.27008 | 0.13275 | 123.2483 | -123.5687 | -123.4589
265.125 | 123.3582 | -116.1987 | 6.9397 | 0.012131 | 0.019228 | 0.0067399 | -0.015199 | -0.0095277 | 0.064706 | 0.070062 | -4.3808 | 7.0404 | -116.5878 | 6.9168 | -116.0934 | -116.5421 | -0.068665 | 0.073242 | 7.0312 | -116.5192 | -0.3891 | 0.10071 | 111.8179 | 123.1155 | -123.0331 | -0.32044 | 0.091553 | 112.207 | 116.1301 | 116.272 | 0.10528 | 123.2391 | 111.8179 | 123.23 | -0.34332 | -0.32044 | 123.2391 | 111.8179 | -0.34332 | 0.10528 | 123.23 | -123.5275 | -123.4589
266.8594 | 123.2529 | -116.098 | 7.1091 | -0.0031279 | 0.019228 | 0.01208 | -0.011995 | -0.0056823 | 0.061716 | 0.070916 | -4.3259 | 7.1594 | -116.4505 | 7.045 | -115.9607 | -116.3818 | -0.11902 | 0.045776 | 7.1594 | -116.3589 | -0.35248 | 0.050354 | 111.7722 | 123.143 | -123.0698 | -0.26093 | 0.050354 | 112.1246 | 115.979 | 116.1438 | 0.13733 | 123.2574 | 111.7722 | 123.2574 | -0.28381 | -0.26093 | 123.2574 | 111.7722 | -0.28381 | 0.13733 | 123.2574 | -123.5596 | -123.468
268.5469 | 123.2529 | -117.4438 | 5.7541 | -0.010757 | 0.017306 | 0.015071 | -0.014772 | -0.0071777 | 0.064493 | 0.070703 | -4.5639 | 5.8228 | -117.7917 | 5.6808 | -117.2791 | -117.691 | -0.21057 | 0.041199 | 5.8228 | -117.7048 | -0.3479 | 0.068665 | 112.8799 | 123.1247 | -123.0331 | -0.26093 | 0.068665 | 113.2278 | 117.2333 | 117.485 | 0.16479 | 123.2666 | 112.8799 | 123.2666 | -0.24719 | -0.26093 | 123.2666 | 112.8799 | -0.24719 | 0.16479 | 123.2666 | -123.5458 | -123.4589
270.2344 | 123.2803 | -117.2928 | 5.8456 | 0.0045011 | 0.016665 | 0.0067399 | -0.020326 | -0.0069641 | 0.065561 | 0.070916 | -4.4952 | 5.9097 | -117.5858 | 5.9372 | -117.0273 | -117.4622 | -0.32501 | 0.18768 | 5.9097 | -117.572 | -0.29297 | 0.064087 | 112.7975 | 123.23 | -122.8729 | -0.27923 | 0.064087 | 113.0905 | 116.9678 | 117.4805 | 0.2655 | 123.2025 | 112.7975 | 123.2025 | -0.16937 | -0.27923 | 123.2025 | 112.7975 | -0.16937 | 0.2655 | 123.2025 | -123.4314 | -123.4177
272.0156 | 123.3124 | -117.2928 | 5.8868 | -0.0031279 | 0.01346 | 0.0067399 | -0.016908 | -0.0076049 | 0.063638 | 0.069421 | -4.4724 | 5.9326 | -117.5995 | 5.9326 | -117.0639 | -117.4896 | -0.1831 | 0.16022 | 5.9555 | -117.5217 | -0.3067 | 0.045776 | 112.8204 | 123.2254 | -122.9507 | -0.22888 | 0.068664 | 113.1271 | 117.1097 | 117.453 | 0.22888 | 123.2254 | 112.8204 | 123.2483 | -0.19684 | -0.22888 | 123.2254 | 112.8204 | -0.19684 | 0.22888 | 123.2483 | -123.4863 | -123.4085
273.7188 | 123.2071 | -116.4322 | 6.7657 | 0.012131 | 0.017306 | 0.0073807 | -0.016054 | -0.0063233 | 0.065347 | 0.06878 | -4.2206 | 6.8207 | -116.7114 | 6.752 | -116.2216 | -116.597 | -0.32044 | 0.19226 | 6.7566 | -116.6794 | -0.27924 | 0.054932 | 112.2116 | 123.1842 | -122.9874 | -0.24719 | -0.009155 | 112.4908 | 116.1118 | 116.6245 | 0.21057 | 123.2529 | 112.2116 | 123.1888 | -0.16479 | -0.24719 | 123.2529 | 112.2116 | -0.16479 | 0.21057 | 123.1888 | -123.4772 | -123.4451
275.4062 | 123.2895 | -116.6382 | 6.5369 | -0.0031279 | 0.01581 | 0.011226 | -0.019045 | -0.0069641 | 0.065988 | 0.069848 | -4.4174 | 6.5643 | -116.954 | 6.5552 | -116.4505 | -116.8625 | -0.29297 | 0.11444 | 6.5689 | -116.9174 | -0.31586 | 0.027466 | 112.2208 | 123.1934 | -122.9874 | -0.27923 | 0.032044 | 112.5366 | 116.3452 | 116.7526 | 0.18768 | 123.2025 | 112.2208 | 123.2071 | -0.2243 | -0.27923 | 123.2025 | 112.2208 | -0.2243 | 0.18768 | 123.2071 | -123.4909 | -123.4543
277.0781 | 123.3353 | -116.2857 | 6.8527 | 0.0045011 | 0.017519 | 0.011439 | -0.017976 | -0.0080323 | 0.06492 | 0.069421 | -4.3854 | 6.9077 | -116.6519 | 6.8436 | -116.1484 | -116.5604 | -0.25635 | 0.09613 | 6.9031 | -116.6016 | -0.36621 | 0.054932 | 111.9003 | 123.1293 | -123.0011 | -0.31586 | 0.050354 | 112.2665 | 116.0294 | 116.3818 | 0.13733 | 123.1934 | 111.9003 | 123.1888 | -0.27466 | -0.31586 | 123.1934 | 111.9003 | -0.27466 | 0.13733 | 123.1888 | -123.5046 | -123.4543
278.7656 | 123.0057 | -94.5969 | 28.5278 | 0.0045011 | 0.017947 | 0.014644 | -0.017976 | -0.0065369 | 0.064493 | 0.070703 | -0.89264 | 28.5873 | -94.8944 | 28.6148 | -94.4595 | -94.8212 | -0.13275 | 0.19226 | 28.5965 | -94.8624 | -0.29755 | 0.059509 | 93.7042 | 123.2117 | -122.9874 | -0.2655 | 0.068665 | 94.0018 | 94.4641 | 94.7891 | 0.13733 | 123.1842 | 93.7042 | 123.1934 | -0.2243 | -0.2655 | 123.1842 | 93.7042 | -0.2243 | 0.13733 | 123.1934 | -123.4222 | -123.3902
280.4375 | 123.2941 | -94.6198 | 28.537 | -0.010757 | 0.017947 | 0.016353 | -0.016908 | -0.0080323 | 0.062357 | 0.070062 | -1.593 | 28.5873 | -94.8807 | 28.6697 | -94.4229 | -94.7983 | -0.086975 | 0.26093 | 28.569 | -94.8624 | -0.26093 | 0.050354 | 93.0267 | 123.2895 | -122.9599 | -0.24262 | 0.032044 | 93.2877 | 94.5328 | 94.8807 | 0.19684 | 123.2071 | 93.0267 | 123.1888 | -0.17853 | -0.24262 | 123.2071 | 93.0267 | -0.17853 | 0.19684 | 123.1888 | -123.4177 | -123.3994
282.1406 | 123.2803 | -94.5694 | 28.5233 | 0.012131 | 0.015383 | 0.0065263 | -0.014558 | -0.0084595 | 0.063425 | 0.069635 | -1.6525 | 28.5187 | -94.9677 | 28.5095 | -94.5831 | -95.018 | -0.4715 | -0.15564 | 28.2761 | -95.2194 | -0.39825 | -0.004577 | 92.9169 | 123.0789 | -123.1064 | -0.65002 | -0.24719 | 93.3151 | 94.0979 | 94.4138 | -0.013733 | 123.0881 | 92.9169 | 122.8455 | -0.44861 | -0.65002 | 123.0881 | 92.9169 | -0.44861 | -0.013733 | 122.8455 | -123.4909 | -123.7427
283.8125 | 123.1934 | -95.6131 | 27.5894 | -0.0031279 | 0.016665 | 0.01208 | -0.0094315 | -0.0048279 | 0.058939 | 0.069635 | -1.7624 | 27.6535 | -95.874 | 27.5986 | -95.43 | -95.787 | -0.29755 | -0.20599 | 27.626 | -95.8374 | -0.26093 | 0.064086 | 93.8507 | 123.2117 | -123.0194 | -0.2243 | 0.036621 | 94.1116 | 95.3156 | 95.4071 | 0.1831 | 123.2666 | 93.8507 | 123.2391 | -0.17395 | -0.2243 | 123.2666 | 93.8507 | -0.17395 | 0.1831 | 123.2391 | -123.4634 | -123.4268
285.4844 | 123.2986 | -115.9012 | 7.1869 | 0.0045011 | 0.016451 | 0.011653 | -0.013063 | -0.0054687 | 0.06257 | 0.069207 | -4.3625 | 7.283 | -116.3452 | 7.1732 | -115.8234 | -116.2399 | -0.18768 | 0 | 7.3013 | -116.2216 | -0.44403 | 0.09613 | 111.5387 | 123.0743 | -123.0103 | -0.32044 | 0.11444 | 111.9827 | 115.7135 | 115.9012 | 0.07782 | 123.1842 | 111.5387 | 123.2025 | -0.33875 | -0.32044 | 123.1842 | 111.5387 | -0.33875 | 0.07782 | 123.2025 | -123.5321 | -123.4085
287.1719 | 123.2712 | -94.5969 | 28.5049 | -0.0031279 | 0.017519 | 0.0080215 | -0.020967 | -0.0065369 | 0.063852 | 0.069848 | -1.6296 | 28.5736 | -94.9036 | 28.6926 | -94.3863 | -94.7479 | -0.24261 | 0.23346 | 28.5828 | -94.8486 | -0.3067 | 0.068664 | 92.9672 | 123.2895 | -122.8912 | -0.25177 | 0.07782 | 93.2739 | 94.3542 | 94.8303 | 0.21057 | 123.1705 | 92.9672 | 123.1796 | -0.15106 | -0.25177 | 123.1705 | 92.9672 | -0.15106 | 0.21057 | 123.1796 | -123.4085 | -123.3536
288.875 | 123.317 | -94.5648 | 28.5141 | 0.0045011 | 0.018374 | 0.0093033 | -0.015199 | -0.0073913 | 0.06257 | 0.069421 | -1.7075 | 28.6469 | -94.931 | 28.5965 | -94.4824 | -94.8807 | 0.032043 | 0.14191 | 28.6469 | -94.8624 | -0.36621 | 0.13275 | 92.8574 | 123.1613 | -122.9965 | -0.29755 | 0.13275 | 93.2236 | 94.5969 | 94.7067 | 0.082397 | 123.2117 | 92.8574 | 123.2117 | -0.31586 | -0.29755 | 123.2117 | 92.8574 | -0.31586 | 0.082397 | 123.2117 | -123.4451 | -123.3765
290.5469 | 123.2849 | -94.5602 | 28.5324 | 0.0045011 | 0.020083 | 0.0090897 | -0.012209 | -0.0065369 | 0.06257 | 0.068353 | -1.6754 | 28.6423 | -94.9219 | 28.624 | -94.455 | -94.8257 | 0 | 0.17395 | 28.6743 | -94.8395 | -0.36163 | 0.10986 | 92.8848 | 123.1842 | -122.9874 | -0.27924 | 0.14191 | 93.2465 | 94.5602 | 94.7342 | 0.10529 | 123.2025 | 92.8848 | 123.2346 | -0.2655 | -0.27924 | 123.2025 | 92.8848 | -0.2655 | 0.10529 | 123.2346 | -123.4543 | -123.3719
292.2188 | 123.317 | -94.6014 | 28.5278 | 0.0045011 | 0.018587 | 0.010585 | -0.016267 | -0.0069641 | 0.063425 | 0.071985 | -1.7075 | 28.624 | -94.9631 | 28.5782 | -94.4778 | -94.8624 | 0.013733 | 0.15106 | 28.6514 | -94.8395 | -0.36163 | 0.09613 | 92.894 | 123.1796 | -123.0057 | -0.23804 | 0.1236 | 93.2556 | 94.6152 | 94.7525 | 0.1236 | 123.2254 | 92.894 | 123.2529 | -0.26093 | -0.23804 | 123.2254 | 92.894 | -0.26093 | 0.1236 | 123.2529 | -123.4909 | -123.3673
293.9219 | 123.2803 | -94.5602 | 28.537 | -0.0031279 | 0.017306 | 0.0071671 | -0.019258 | -0.0063233 | 0.065775 | 0.068567 | -1.6525 | 28.6057 | -94.9081 | 28.688 | -94.368 | -94.7571 | -0.22888 | 0.24719 | 28.5645 | -94.8715 | -0.3479 | 0.068665 | 92.9077 | 123.2483 | -122.905 | -0.31128 | 0.027466 | 93.2556 | 94.3314 | 94.8074 | 0.19226 | 123.1659 | 92.9077 | 123.1247 | -0.19684 | -0.31128 | 123.1659 | 92.9077 | -0.19684 | 0.19226 | 123.1247 | -123.4451 | -123.4085
295.625 | 123.2346 | -94.6243 | 28.537 | 0.0045011 | 0.019015 | 0.0086625 | -0.012209 | -0.0037597 | 0.062997 | 0.069848 | -1.7029 | 28.6285 | -94.9539 | 28.5461 | -94.5374 | -94.9127 | -0.036621 | 0.09613 | 28.6469 | -94.8578 | -0.32959 | 0.091553 | 92.9214 | 123.1705 | -123.0743 | -0.23346 | 0.10986 | 93.251 | 94.5877 | 94.7205 | 0.086975 | 123.2529 | 92.9214 | 123.2712 | -0.28839 | -0.23346 | 123.2529 | 92.9214 | -0.28839 | 0.086975 | 123.2712 | -123.4909 | -123.3948
297.3438 | 123.2986 | -94.5648 | 28.5416 | 0.0045011 | 0.019656 | 0.0067399 | -0.016054 | -0.0048279 | 0.060648 | 0.070703 | -1.7075 | 28.6285 | -94.9677 | 28.6011 | -94.4595 | -94.8349 | 0.013733 | 0.16479 | 28.6606 | -94.8578 | -0.40283 | 0.086975 | 92.8574 | 123.1659 | -123.0011 | -0.29297 | 0.11902 | 93.2602 | 94.5786 | 94.7296 | 0.10528 | 123.1934 | 92.8574 | 123.2254 | -0.27008 | -0.29297 | 123.1934 | 92.8574 | -0.27008 | 0.10528 | 123.2254 | -123.5092 | -123.3994
299.0469 | 123.1934 | -94.6289 | 28.5461 | -0.0031279 | 0.019869 | 0.0097305 | -0.015627 | -0.0054687 | 0.063425 | 0.071344 | -1.6296 | 28.5461 | -94.931 | 28.6514 | -94.3954 | -94.7525 | -0.26093 | 0.19226 | 28.5599 | -94.8761 | -0.30212 | 0 | 92.9993 | 123.2803 | -122.9416 | -0.24719 | 0.013732 | 93.3014 | 94.368 | 94.8212 | 0.23346 | 123.175 | 92.9993 | 123.1888 | -0.1236 | -0.24719 | 123.175 | 92.9993 | -0.1236 | 0.23346 | 123.1888 | -123.4772 | -123.4222
300.7344 | 123.3124 | -94.574 | 28.4866 | -0.0031279 | 0.017733 | 0.012508 | -0.018831 | -0.0069641 | 0.065347 | 0.070276 | -1.7166 | 28.5736 | -94.9265 | 28.6331 | -94.4183 | -94.7708 | -0.21515 | 0.17853 | 28.5919 | -94.8578 | -0.35248 | 0.086975 | 92.8574 | 123.2071 | -122.905 | -0.28381 | 0.10529 | 93.2098 | 94.3588 | 94.7525 | 0.15564 | 123.1476 | 92.8574 | 123.1659 | -0.19684 | -0.28381 | 123.1476 | 92.8574 | -0.19684 | 0.15564 | 123.1659 | -123.4131 | -123.3444
302.4062 | 123.2986 | -94.5877 | 28.5187 | 0.0045011 | 0.013888 | 0.0095169 | -0.018404 | -0.0082459 | 0.063852 | 0.069848 | -1.6479 | 28.5599 | -94.9265 | 28.688 | -94.3771 | -94.7479 | -0.23346 | 0.26093 | 28.5645 | -94.8441 | -0.33874 | 0.041198 | 92.9398 | 123.2758 | -122.8958 | -0.25635 | 0.045776 | 93.2785 | 94.3542 | 94.8486 | 0.21057 | 123.1476 | 92.9398 | 123.1522 | -0.16022 | -0.25635 | 123.1476 | 92.9398 | -0.16022 | 0.21057 | 123.1522 | -123.4451 | -123.3627
304.1094 | 123.1979 | -94.6106 | 28.5324 | 0.012131 | 0.017947 | 0.012935 | -0.014345 | -0.0054687 | 0.063211 | 0.071771 | -1.6937 | 28.5736 | -94.9722 | 28.6377 | -94.4412 | -94.7845 | -0.22888 | 0.16479 | 28.5599 | -94.8532 | -0.36163 | 0.041198 | 92.9169 | 123.2483 | -122.9736 | -0.24261 | 0.027465 | 93.2785 | 94.3817 | 94.7754 | 0.16937 | 123.1842 | 92.9169 | 123.1705 | -0.17395 | -0.24261 | 123.1842 | 92.9169 | -0.17395 | 0.16937 | 123.1705 | -123.5046 | -123.3856
305.7969 | 123.3444 | -94.5602 | 28.5095 | -0.018387 | 0.020296 | 0.01208 | -0.014131 | -0.0069641 | 0.064493 | 0.070489 | -1.7395 | 28.6148 | -94.9677 | 28.569 | -94.487 | -94.8898 | 0.022888 | 0.14648 | 28.6102 | -94.9036 | -0.40741 | 0.10529 | 92.8207 | 123.1293 | -122.9965 | -0.34332 | 0.10071 | 93.2281 | 94.5831 | 94.7067 | 0.073242 | 123.175 | 92.8207 | 123.1705 | -0.32959 | -0.34332 | 123.175 | 92.8207 | -0.32959 | 0.073242 | 123.1705 | -123.4772 | -123.4131
307.5156 | 123.2208 | -94.6198 | 28.5233 | 0.0045011 | 0.016238 | 0.013148 | -0.018617 | -0.0067505 | 0.06257 | 0.070276 | -1.6891 | 28.5507 | -94.9356 | 28.6148 | -94.455 | -94.7891 | -0.26093 | 0.16479 | 28.5507 | -94.8532 | -0.31586 | 0.027466 | 92.9306 | 123.2346 | -122.9782 | -0.23346 | 0.027466 | 93.2465 | 94.3588 | 94.7845 | 0.16479 | 123.1705 | 92.9306 | 123.1705 | -0.16937 | -0.23346 | 123.1705 | 92.9306 | -0.16937 | 0.16479 | 123.1705 | -123.4589 | -123.3765
309.1875 | 123.262 | -94.5786 | 28.5233 | 0.0045011 | 0.016665 | 0.015071 | -0.016695 | -0.0061097 | 0.062143 | 0.067498 | -1.6754 | 28.5782 | -94.9219 | 28.656 | -94.4046 | -94.7662 | -0.20599 | 0.25177 | 28.5416 | -94.8715 | -0.34332 | 0.054932 | 92.9031 | 123.2346 | -122.9279 | -0.29297 | 0.018311 | 93.2465 | 94.3726 | 94.8303 | 0.17395 | 123.1567 | 92.9031 | 123.1201 | -0.18768 | -0.29297 | 123.1567 | 92.9031 | -0.18768 | 0.17395 | 123.1201 | -123.4451 | -123.3948
310.875 | 123.2758 | -94.574 | 28.5233 | -0.0031279 | 0.019656 | 0.0075943 | -0.017122 | -0.0071777 | 0.063852 | 0.069848 | -1.68 | 28.5461 | -94.9265 | 28.6835 | -94.3771 | -94.7433 | -0.21057 | 0.24261 | 28.5416 | -94.8441 | -0.35248 | 0.022889 | 92.894 | 123.2574 | -122.9004 | -0.27008 | 0.018311 | 93.2465 | 94.3634 | 94.8166 | 0.19684 | 123.1201 | 92.894 | 123.1155 | -0.16937 | -0.27008 | 123.1201 | 92.894 | -0.16937 | 0.19684 | 123.1155 | -123.4497 | -123.3673
312.5781 | 123.2391 | -94.606 | 28.5187 | -0.0031279 | 0.017733 | 0.01208 | -0.011781 | -0.0058961 | 0.062997 | 0.070489 | -1.7395 | 28.624 | -94.9814 | 28.5507 | -94.5465 | -94.9173 | -0.036621 | 0.086975 | 28.6148 | -94.8853 | -0.37537 | 0.10528 | 92.8665 | 123.1567 | -123.0652 | -0.27924 | 0.09613 | 93.2419 | 94.5694 | 94.693 | 0.059509 | 123.23 | 92.8665 | 123.2208 | -0.31128 | -0.27924 | 123.23 | 92.8665 | -0.31128 | 0.059509 | 123.2208 | -123.5001 | -123.4039
314.25 | 123.2849 | -94.5877 | 28.4775 | 0.0045011 | 0.015383 | 0.0084489 | -0.017549 | -0.0076049 | 0.062997 | 0.071557 | -1.7029 | 28.5507 | -94.9539 | 28.6285 | -94.4138 | -94.812 | -0.13733 | 0.22888 | 28.5599 | -94.8944 | -0.36621 | 0.073242 | 92.8848 | 123.2162 | -122.8912 | -0.3067 | 0.082397 | 93.251 | 94.4504 | 94.8166 | 0.17395 | 123.1384 | 92.8848 | 123.1476 | -0.2243 | -0.3067 | 123.1384 | 92.8848 | -0.2243 | 0.17395 | 123.1476 | -123.4314 | -123.3719
315.9844 | 123.2346 | -94.6152 | 28.4637 | 0.0045011 | 0.016878 | 0.0035355 | -0.018404 | -0.0067505 | 0.064706 | 0.067926 | -1.7258 | 28.5461 | -94.9265 | 28.5782 | -94.4641 | -94.8257 | -0.22888 | 0.15106 | 28.5233 | -94.8944 | -0.31128 | 0.082398 | 92.8894 | 123.1934 | -122.9279 | -0.27924 | 0.059509 | 93.2007 | 94.3863 | 94.7662 | 0.15106 | 123.1613 | 92.8894 | 123.1384 | -0.21057 | -0.27924 | 123.1613 | 92.8894 | -0.21057 | 0.15106 | 123.1384 | -123.3902 | -123.3582
317.6562 | 123.3353 | -94.6106 | 28.4729 | -0.0031279 | 0.017519 | 0.015285 | -0.017976 | -0.0067505 | 0.063852 | 0.068139 | -1.7487 | 28.5233 | -94.9173 | 28.5873 | -94.4687 | -94.8303 | -0.20142 | 0.15106 | 28.5599 | -94.8761 | -0.3067 | 0.050354 | 92.8619 | 123.1979 | -122.9416 | -0.2655 | 0.086975 | 93.1686 | 94.4092 | 94.7617 | 0.14191 | 123.1338 | 92.8619 | 123.1705 | -0.21973 | -0.2655 | 123.1338 | 92.8619 | -0.21973 | 0.14191 | 123.1705 | -123.3902 | -123.349
319.375 | 123.1888 | -94.6518 | 28.5416 | -0.010757 | 0.020937 | 0.0097305 | -0.010072 | -0.0054687 | 0.064493 | 0.070703 | -1.6434 | 28.6011 | -94.9356 | 28.6057 | -94.455 | -94.8486 | -0.068665 | 0.20599 | 28.6011 | -94.8715 | -0.28381 | 0.059509 | 93.0084 | 123.2574 | -122.9965 | -0.21973 | 0.059509 | 93.2922 | 94.5831 | 94.8578 | 0.19684 | 123.2529 | 93.0084 | 123.2529 | -0.19684 | -0.21973 | 123.2529 | 93.0084 | -0.19684 | 0.19684 | 123.2529 | -123.4772 | -123.4131
321.0625 | 123.2986 | -94.5877 | 28.4729 | 0.0045011 | 0.017519 | 0.010371 | -0.016481 | -0.0091003 | 0.064279 | 0.068994 | -1.7029 | 28.5507 | -94.9585 | 28.5965 | -94.4687 | -94.8395 | -0.082397 | 0.19684 | 28.5553 | -94.9173 | -0.37079 | 0.07782 | 92.8848 | 123.1842 | -122.9416 | -0.32959 | 0.082398 | 93.2556 | 94.5053 | 94.7845 | 0.11902 | 123.1384 | 92.8848 | 123.143 | -0.25177 | -0.32959 | 123.1384 | 92.8848 | -0.25177 | 0.11902 | 123.143 | -123.4314 | -123.3902
322.7188 | 123.1613 | -94.6472 | 28.5049 | -0.010757 | 0.018801 | 0.014003 | -0.014345 | -0.0037597 | 0.06492 | 0.070703 | -1.6846 | 28.5049 | -94.9539 | 28.6148 | -94.4366 | -94.7937 | -0.27466 | 0.18768 | 28.5233 | -94.8807 | -0.3067 | 0 | 92.9626 | 123.262 | -122.9416 | -0.23346 | 0.01831 | 93.2693 | 94.3726 | 94.8349 | 0.21057 | 123.1522 | 92.9626 | 123.1705 | -0.14648 | -0.23346 | 123.1522 | 92.9626 | -0.14648 | 0.21057 | 123.1705 | -123.4589 | -123.3856
324.4688 | 123.3032 | -94.5923 | 28.4683 | 0.012131 | 0.015383 | 0.0086625 | -0.01584 | -0.0078187 | 0.064066 | 0.069848 | -1.712 | 28.5141 | -94.9905 | 28.5919 | -94.455 | -94.8624 | -0.07782 | 0.21973 | 28.5461 | -94.9036 | -0.39825 | 0.045776 | 92.8802 | 123.1842 | -122.9233 | -0.31128 | 0.07782 | 93.2785 | 94.5145 | 94.812 | 0.13733 | 123.1064 | 92.8802 | 123.1384 | -0.27008 | -0.31128 | 123.1064 | 92.8802 | -0.27008 | 0.13733 | 123.1384 | -123.4589 | -123.3719
326.1562 | 123.1659 | -94.6564 | 28.4592 | -0.0031279 | 0.01816 | 0.013362 | -0.014772 | -0.0065369 | 0.064706 | 0.069848 | -1.6846 | 28.4866 | -94.9585 | 28.6057 | -94.4366 | -94.8074 | -0.28839 | 0.1831 | 28.4821 | -94.899 | -0.30212 | 0.027466 | 92.9718 | 123.262 | -122.8958 | -0.24262 | 0.022889 | 93.2739 | 94.368 | 94.8395 | 0.21973 | 123.143 | 92.9718 | 123.1384 | -0.15106 | -0.24262 | 123.143 | 92.9718 | -0.15106 | 0.21973 | 123.1384 | -123.4177 | -123.3582
327.8281 | 123.2986 | -94.6335 | 28.4363 | 0.012131 | 0.016238 | 0.011226 | -0.016908 | -0.0067505 | 0.066415 | 0.072412 | -1.767 | 28.5187 | -94.9814 | 28.5278 | -94.5145 | -94.8715 | -0.19226 | 0.1236 | 28.4821 | -94.9402 | -0.3479 | 0.082398 | 92.8665 | 123.1613 | -122.9507 | -0.3067 | 0.045777 | 93.2144 | 94.4412 | 94.7571 | 0.11902 | 123.1522 | 92.8665 | 123.1155 | -0.23804 | -0.3067 | 123.1522 | 92.8665 | -0.23804 | 0.11902 | 123.1155 | -123.4177 | -123.3765
329.5469 | 123.1979 | -94.6472 | 28.4775 | 0.012131 | 0.017733 | 0.010371 | -0.011781 | -0.0076049 | 0.06257 | 0.068994 | -1.7029 | 28.5599 | -95.0088 | 28.5782 | -94.4824 | -94.8853 | -0.041199 | 0.20599 | 28.537 | -94.9127 | -0.36163 | 0.082397 | 92.9443 | 123.2254 | -122.9599 | -0.2655 | 0.059509 | 93.306 | 94.606 | 94.8532 | 0.16479 | 123.2071 | 92.9443 | 123.1842 | -0.23804 | -0.2655 | 123.2071 | 92.9443 | -0.23804 | 0.16479 | 123.1842 | -123.4863 | -123.3902
331.2188 | 123.1934 | -94.6564 | 28.4592 | -0.0031279 | 0.019015 | 0.0058853 | -0.01285 | -0.0041871 | 0.062357 | 0.070916 | -1.7075 | 28.5324 | -95.0043 | 28.5324 | -94.5282 | -94.9127 | -0.050354 | 0.15564 | 28.5599 | -94.9036 | -0.3479 | 0.073243 | 92.9489 | 123.1888 | -122.9874 | -0.24719 | 0.10071 | 93.2968 | 94.606 | 94.812 | 0.12817 | 123.1888 | 92.9489 | 123.2162 | -0.25635 | -0.24719 | 123.1888 | 92.9489 | -0.25635 | 0.12817 | 123.2162 | -123.4634 | -123.3627
332.8906 | 123.3582 | -94.6152 | 28.4363 | 0.0045011 | 0.015597 | 0.0078079 | -0.016908 | -0.0065369 | 0.063638 | 0.067926 | -1.799 | 28.5278 | -95.0043 | 28.4866 | -94.5465 | -94.9356 | 0.032043 | 0.13733 | 28.5553 | -94.8807 | -0.3891 | 0.091553 | 92.8162 | 123.1018 | -122.9828 | -0.2655 | 0.11902 | 93.2053 | 94.6472 | 94.7525 | 0.068664 | 123.143 | 92.8162 | 123.1705 | -0.32044 | -0.2655 | 123.143 | 92.8162 | -0.32044 | 0.068664 | 123.1705 | -123.4406 | -123.317
334.5781 | 123.2025 | -94.6655 | 28.45 | 0.0045011 | 0.017947 | 0.012721 | -0.014986 | -0.0052551 | 0.061929 | 0.071557 | -1.7029 | 28.5233 | -95.0134 | 28.5416 | -94.4962 | -94.8807 | -0.050354 | 0.20599 | 28.5416 | -94.9127 | -0.3479 | 0.073242 | 92.9626 | 123.2071 | -122.9462 | -0.24719 | 0.091553 | 93.3105 | 94.6152 | 94.8715 | 0.16937 | 123.1888 | 92.9626 | 123.2071 | -0.21515 | -0.24719 | 123.1888 | 92.9626 | -0.21515 | 0.16937 | 123.2071 | -123.4634 | -123.3627
336.2656 | 123.2346 | -122.8775 | 0.3067 | -0.0031279 | 0.017519 | 0.01208 | -0.015627 | -0.0048279 | 0.06257 | 0.069421 | -5.5893 | 0.3891 | -123.2529 | 0.25635 | -122.6807 | -123.1064 | -0.32501 | 0.045776 | 0.35706 | -123.143 | -0.37537 | 0.082397 | 117.2882 | 123.1339 | -122.9874 | -0.2655 | 0.050354 | 117.6636 | 122.5525 | 122.9233 | 0.19684 | 123.2666 | 117.2882 | 123.2346 | -0.22888 | -0.2655 | 123.2666 | 117.2882 | -0.22888 | 0.19684 | 123.2346 | -123.5596 | -123.4497
338.125 | 123.317 | -122.8683 | 0.26093 | 0.012131 | 0.01816 | 0.011226 | -0.013063 | -0.0063233 | 0.063425 | 0.069207 | -5.6213 | 0.39825 | -123.2758 | 0.2243 | -122.7127 | -123.1796 | -0.1236 | 0.045776 | 0.36621 | -123.1705 | -0.40741 | 0.13733 | 117.247 | 123.0927 | -122.9736 | -0.30212 | 0.10529 | 117.6544 | 122.7448 | 122.9141 | 0.15564 | 123.2666 | 117.247 | 123.2346 | -0.31128 | -0.30212 | 123.2666 | 117.247 | -0.31128 | 0.15564 | 123.2346 | -123.5367 | -123.4314
339.8906 | 123.2803 | -122.8912 | 0.27466 | -0.0031279 | 0.016451 | 0.010371 | -0.017976 | -0.0076049 | 0.065134 | 0.071344 | -5.5573 | 0.33417 | -123.23 | 0.31586 | -122.612 | -123.0789 | -0.31128 | 0.15106 | 0.33417 | -123.1888 | -0.33875 | 0.059509 | 117.334 | 123.2071 | -122.8867 | -0.29755 | 0.059509 | 117.6727 | 122.58 | 123.0423 | 0.27923 | 123.2254 | 117.334 | 123.2254 | -0.18768 | -0.29755 | 123.2254 | 117.334 | -0.18768 | 0.27923 | 123.2254 | -123.5046 | -123.4634
341.5781 | 123.3078 | -122.8867 | 0.27466 | -0.010757 | 0.019228 | 0.01208 | -0.015627 | -0.0065369 | 0.063425 | 0.069848 | -5.6259 | 0.37994 | -123.2758 | 0.21057 | -122.7219 | -123.1842 | -0.11902 | 0.059509 | 0.38452 | -123.1567 | -0.3891 | 0.10529 | 117.2607 | 123.0972 | -122.9965 | -0.27008 | 0.10986 | 117.6498 | 122.7676 | 122.9462 | 0.16479 | 123.2666 | 117.2607 | 123.2712 | -0.29755 | -0.27008 | 123.2666 | 117.2607 | -0.29755 | 0.16479 | 123.2712 | -123.5504 | -123.4314
343.3281 | 123.2071 | -122.9004 | 0.32501 | 0.012131 | 0.021792 | 0.0093033 | -0.012422 | -0.0050415 | 0.061716 | 0.069207 | -5.5481 | 0.39825 | -123.2483 | 0.27924 | -122.6624 | -123.1338 | -0.16937 | 0.11902 | 0.39368 | -123.1247 | -0.3479 | 0.073242 | 117.3523 | 123.1796 | -122.9874 | -0.2243 | 0.068665 | 117.7002 | 122.731 | 123.0194 | 0.23804 | 123.2986 | 117.3523 | 123.2941 | -0.23346 | -0.2243 | 123.2986 | 117.3523 | -0.23346 | 0.23804 | 123.2941 | -123.5733 | -123.4497
345.0781 | 123.3078 | -122.8546 | 0.29755 | 0.0045011 | 0.01816 | 0.010585 | -0.022249 | -0.0050415 | 0.066629 | 0.070916 | -5.6213 | 0.3891 | -123.1659 | 0.28381 | -122.6349 | -123.0743 | -0.31586 | 0.068665 | 0.3891 | -123.1293 | -0.31128 | 0.091553 | 117.2333 | 123.1384 | -122.9324 | -0.27466 | 0.091553 | 117.5446 | 122.5388 | 122.9233 | 0.21973 | 123.2437 | 117.2333 | 123.2437 | -0.21973 | -0.27466 | 123.2437 | 117.2333 | -0.21973 | 0.21973 | 123.2437 | -123.4634 | -123.4268
346.75 | 123.1842 | -122.9004 | 0.34332 | 0.0045011 | 0.019015 | 0.012294 | -0.0096451 | -0.0048279 | 0.063638 | 0.070489 | -5.5481 | 0.41199 | -123.2254 | 0.31128 | -122.6395 | -123.0927 | -0.17853 | 0.11902 | 0.39825 | -123.1567 | -0.32501 | 0.068664 | 117.3523 | 123.2117 | -122.9828 | -0.25635 | 0.054931 | 117.6773 | 122.7219 | 123.0194 | 0.26093 | 123.3124 | 117.3523 | 123.2986 | -0.19226 | -0.25635 | 123.3124 | 117.3523 | -0.19226 | 0.26093 | 123.2986 | -123.5687 | -123.5001
348.5 | 123.175 | -122.8867 | 0.33875 | 0.012131 | 0.018587 | 0.0093033 | -0.013277 | -0.0046143 | 0.062784 | 0.071985 | -5.571 | 0.39368 | -123.1934 | 0.27466 | -122.6578 | -123.0881 | -0.30212 | 0.050354 | 0.39825 | -123.143 | -0.3067 | 0.054932 | 117.3157 | 123.1613 | -122.9965 | -0.25635 | 0.059509 | 117.6224 | 122.5845 | 122.937 | 0.22888 | 123.2803 | 117.3157 | 123.2849 | -0.20142 | -0.25635 | 123.2803 | 117.3157 | -0.20142 | 0.22888 | 123.2849 | -123.5321 | -123.4818
350.1875 | 123.2803 | -122.8271 | 0.3479 | 0.0045011 | 0.01816 | 0.010371 | -0.016267 | -0.0065369 | 0.064066 | 0.069207 | -5.5984 | 0.43945 | -123.2071 | 0.27924 | -122.6395 | -123.1155 | -0.11902 | 0.091553 | 0.4303 | -123.1613 | -0.37994 | 0.091553 | 117.2287 | 123.1064 | -122.9874 | -0.33417 | 0.082398 | 117.6086 | 122.7081 | 122.9187 | 0.18768 | 123.2666 | 117.2287 | 123.2574 | -0.28839 | -0.33417 | 123.2666 | 117.2287 | -0.28839 | 0.18768 | 123.2574 | -123.555 | -123.5092
351.9219 | 123.1934 | -122.8958 | 0.34332 | -0.0031279 | 0.016238 | 0.0075943 | -0.015199 | -0.0058961 | 0.062143 | 0.072625 | -5.5664 | 0.41657 | -123.2437 | 0.24719 | -122.7036 | -123.1567 | -0.14648 | 0.054932 | 0.40741 | -123.1338 | -0.3479 | 0.073242 | 117.3294 | 123.143 | -123.0469 | -0.23804 | 0.064087 | 117.6773 | 122.7493 | 122.9507 | 0.19226 | 123.3124 | 117.3294 | 123.3032 | -0.26093 | -0.23804 | 123.3124 | 117.3294 | -0.26093 | 0.19226 | 123.3032 | -123.587 | -123.4772
353.6094 | 123.2712 | -122.8409 | 0.28381 | 0.0045011 | 0.017947 | 0.0063125 | -0.021822 | -0.0073913 | 0.066843 | 0.069635 | -5.5847 | 0.37537 | -123.1613 | 0.28381 | -122.6395 | -123.0881 | -0.30212 | 0.068665 | 0.37994 | -123.1201 | -0.32044 | 0.091553 | 117.2562 | 123.1247 | -122.9233 | -0.27924 | 0.096131 | 117.5766 | 122.5388 | 122.9095 | 0.20142 | 123.2162 | 117.2562 | 123.2208 | -0.24719 | -0.27924 | 123.2162 | 117.2562 | -0.24719 | 0.20142 | 123.2208 | -123.4451 | -123.4039
355.3594 | 123.1522 | -122.8821 | 0.32959 | -0.0031279 | 0.017519 | 0.012935 | -0.015199 | -0.0088867 | 0.063425 | 0.071344 | -5.5298 | 0.35248 | -123.2117 | 0.32959 | -122.6028 | -123.0331 | -0.37537 | 0.11444 | 0.34332 | -123.1338 | -0.32959 | 0.022888 | 117.3523 | 123.2117 | -122.9324 | -0.25177 | 0.013733 | 117.6819 | 122.5067 | 122.9965 | 0.27924 | 123.2346 | 117.3523 | 123.2254 | -0.15106 | -0.25177 | 123.2346 | 117.3523 | -0.15106 | 0.27924 | 123.2254 | -123.5413 | -123.4634
357.1094 | 123.2529 | -122.8592 | 0.28839 | -0.0031279 | 0.017306 | 0.013576 | -0.020754 | -0.0093139 | 0.067483 | 0.07113 | -5.571 | 0.35248 | -123.2025 | 0.32501 | -122.6028 | -123.0469 | -0.33875 | 0.13733 | 0.33875 | -123.1842 | -0.34332 | 0.064087 | 117.2882 | 123.1842 | -122.8912 | -0.32501 | 0.050354 | 117.6315 | 122.5204 | 122.9965 | 0.25635 | 123.2117 | 117.2882 | 123.1979 | -0.18768 | -0.32501 | 123.2117 | 117.2882 | -0.18768 | 0.25635 | 123.1979 | -123.4909 | -123.4726
358.7969 | 123.317 | -122.8546 | 0.30212 | -0.0031279 | 0.018374 | 0.0078079 | -0.015413 | -0.0093139 | 0.064279 | 0.069848 | -5.6168 | 0.37994 | -123.2208 | 0.23346 | -122.6898 | -123.1659 | -0.13275 | 0.086975 | 0.37994 | -123.175 | -0.36621 | 0.07782 | 117.2379 | 123.0881 | -122.9919 | -0.32044 | 0.07782 | 117.6041 | 122.7219 | 122.9416 | 0.16479 | 123.2346 | 117.2379 | 123.2346 | -0.31128 | -0.32044 | 123.2346 | 117.2379 | -0.31128 | 0.16479 | 123.2346 | -123.5229 | -123.4772
360.5625 | 123.2941 | -122.8592 | 0.31586 | -0.010757 | 0.019015 | 0.0082351 | -0.014558 | -0.0056823 | 0.062143 | 0.070916 | -5.6351 | 0.41199 | -123.2483 | 0.22888 | -122.7264 | -123.1842 | -0.09613 | 0.064087 | 0.3891 | -123.1293 | -0.3891 | 0.09613 | 117.2241 | 123.0881 | -123.0423 | -0.27008 | 0.073242 | 117.6132 | 122.7631 | 122.9233 | 0.13275 | 123.2712 | 117.2241 | 123.2483 | -0.32501 | -0.27008 | 123.2712 | 117.2241 | -0.32501 | 0.13275 | 123.2483 | -123.5641 | -123.4451
362.25 | 123.2803 | -122.818 | 0.33417 | 0.012131 | 0.016665 | 0.0097305 | -0.018404 | -0.0091003 | 0.066629 | 0.068139 | -5.5939 | 0.41657 | -123.1934 | 0.32501 | -122.6028 | -123.0377 | -0.31586 | 0.091553 | 0.3891 | -123.1293 | -0.37537 | 0.082398 | 117.2241 | 123.143 | -122.937 | -0.31128 | 0.054932 | 117.5995 | 122.5021 | 122.9095 | 0.21515 | 123.2346 | 117.2241 | 123.2071 | -0.21973 | -0.31128 | 123.2346 | 117.2241 | -0.21973 | 0.21515 | 123.2071 | -123.5275 | -123.4634
363.9844 | 123.1567 | -122.8363 | 0.36163 | 0.0045011 | 0.017947 | 0.0093033 | -0.01349 | -0.0080323 | 0.065347 | 0.070489 | -5.5573 | 0.41657 | -123.2162 | 0.34332 | -122.6074 | -123.0423 | -0.3067 | 0.09613 | 0.39825 | -123.1201 | -0.37994 | 0.054932 | 117.2791 | 123.1796 | -122.9691 | -0.28381 | 0.036621 | 117.659 | 122.5296 | 122.9324 | 0.22888 | 123.2529 | 117.2791 | 123.2346 | -0.20599 | -0.28381 | 123.2529 | 117.2791 | -0.20599 | 0.22888 | 123.2346 | -123.5779 | -123.4817
365.6875 | 123.2483 | -122.7997 | 0.33875 | -0.0031279 | 0.016024 | 0.011439 | -0.018404 | -0.0080323 | 0.065988 | 0.068353 | -5.5069 | 0.39825 | -123.1293 | 0.41199 | -122.5388 | -122.9691 | -0.35248 | 0.1831 | 0.39825 | -123.0881 | -0.32959 | 0.059509 | 117.2928 | 123.2117 | -122.8775 | -0.28839 | 0.059509 | 117.6224 | 122.4472 | 122.9828 | 0.26093 | 123.1979 | 117.2928 | 123.1979 | -0.16937 | -0.28839 | 123.1979 | 117.2928 | -0.16937 | 0.26093 | 123.1979 | -123.468 | -123.4268
367.4219 | 123.2437 | -122.7859 | 0.37537 | 0.012131 | 0.018801 | 0.014217 | -0.017336 | -0.0086731 | 0.064066 | 0.06878 | -5.5161 | 0.4303 | -123.1018 | 0.4303 | -122.4976 | -122.9462 | -0.36621 | 0.18768 | 0.42572 | -123.0743 | -0.31586 | 0.054932 | 117.2699 | 123.2162 | -122.8729 | -0.28839 | 0.050354 | 117.5858 | 122.4197 | 122.9736 | 0.28839 | 123.2162 | 117.2699 | 123.2117 | -0.16022 | -0.28839 | 123.2162 | 117.2699 | -0.16022 | 0.28839 | 123.2117 | -123.4772 | -123.4497
369.0938 | 123.1705 | -122.7951 | 0.40283 | 0.012131 | 0.018374 | 0.015712 | -0.0094315 | -0.0071777 | 0.063425 | 0.070062 | -5.5344 | 0.48065 | -123.1796 | 0.36163 | -122.58 | -123.0423 | -0.1831 | 0.12817 | 0.45319 | -123.056 | -0.38452 | 0.07782 | 117.2607 | 123.1567 | -122.9828 | -0.26093 | 0.050354 | 117.6453 | 122.612 | 122.9233 | 0.21515 | 123.2758 | 117.2607 | 123.2483 | -0.24719 | -0.26093 | 123.2758 | 117.2607 | -0.24719 | 0.21515 | 123.2483 | -123.5825 | -123.4589
370.8281 | 123.1888 | -122.9004 | 0.31128 | -0.0031279 | 0.019442 | 0.012508 | -0.011781 | -0.0050415 | 0.062143 | 0.07113 | -5.5573 | 0.36163 | -123.2346 | 0.22888 | -122.7173 | -123.1842 | -0.14648 | 0.059509 | 0.37994 | -123.1384 | -0.33417 | 0.050354 | 117.3431 | 123.1293 | -123.0286 | -0.23804 | 0.068665 | 117.6773 | 122.7539 | 122.9599 | 0.18311 | 123.262 | 117.3431 | 123.2803 | -0.28381 | -0.23804 | 123.262 | 117.3431 | -0.28381 | 0.18311 | 123.2803 | -123.5458 | -123.4497
372.5 | 123.2803 | -122.8363 | 0.28381 | 0.0045011 | 0.016238 | 0.015071 | -0.019685 | -0.0084595 | 0.064493 | 0.073053 | -5.5984 | 0.3891 | -123.1705 | 0.30212 | -122.612 | -123.0515 | -0.31128 | 0.086975 | 0.36621 | -123.1201 | -0.33417 | 0.10529 | 117.2379 | 123.1384 | -122.8958 | -0.28381 | 0.082398 | 117.572 | 122.525 | 122.9233 | 0.2243 | 123.2254 | 117.2379 | 123.2025 | -0.21515 | -0.28381 | 123.2254 | 117.2379 | -0.21515 | 0.2243 | 123.2025 | -123.4543 | -123.4039
374.2344 | 123.1842 | -122.7951 | 0.39368 | 0.012131 | 0.01581 | 0.0099441 | -0.01584 | -0.0084595 | 0.062997 | 0.070916 | -5.5389 | 0.42572 | -123.0972 | 0.41199 | -122.5433 | -122.9828 | -0.37537 | 0.10071 | 0.43488 | -123.0377 | -0.30212 | 0.032043 | 117.2562 | 123.2071 | -122.937 | -0.24261 | 0.041198 | 117.5583 | 122.4197 | 122.8958 | 0.25177 | 123.2208 | 117.2562 | 123.23 | -0.18768 | -0.24261 | 123.2208 | 117.2562 | -0.18768 | 0.25177 | 123.23 | -123.4909 | -123.4314
375.9219 | 123.143 | -122.8546 | 0.33875 | 0.0045011 | 0.016665 | 0.011867 | -0.01349 | -0.0061097 | 0.06492 | 0.069848 | -5.5252 | 0.41199 | -123.1842 | 0.32959 | -122.5983 | -123.0698 | -0.17395 | 0.12817 | 0.40283 | -123.0927 | -0.32959 | 0.073242 | 117.3294 | 123.1842 | -122.937 | -0.23804 | 0.064087 | 117.659 | 122.6807 | 122.9828 | 0.25635 | 123.2666 | 117.3294 | 123.2574 | -0.21515 | -0.23804 | 123.2666 | 117.3294 | -0.21515 | 0.25635 | 123.2574 | -123.5229 | -123.4314
377.6719 | 123.1979 | -122.85 | 0.33875 | 0.0045011 | 0.020083 | 0.0095169 | -0.013063 | -0.0058961 | 0.064066 | 0.071557 | -5.571 | 0.42572 | -123.1934 | 0.23346 | -122.6852 | -123.1522 | -0.16022 | 0.009155 | 0.41199 | -123.1018 | -0.34332 | 0.086975 | 117.2791 | 123.0835 | -123.024 | -0.25177 | 0.073242 | 117.6224 | 122.6898 | 122.8592 | 0.16479 | 123.2758 | 117.2791 | 123.262 | -0.30212 | -0.25177 | 123.2758 | 117.2791 | -0.30212 | 0.16479 | 123.262 | -123.5321 | -123.4406
379.3594 | 123.1384 | -122.8592 | 0.34332 | -0.0031279 | 0.01816 | 0.0075943 | -0.017336 | -0.0058961 | 0.066202 | 0.070916 | -5.5252 | 0.37537 | -123.1293 | 0.34332 | -122.5845 | -123.0331 | -0.37079 | 0.10529 | 0.37994 | -123.1155 | -0.27008 | 0.032043 | 117.334 | 123.2025 | -122.9279 | -0.25635 | 0.036621 | 117.6041 | 122.4884 | 122.9645 | 0.27466 | 123.2346 | 117.334 | 123.2391 | -0.17395 | -0.25635 | 123.2346 | 117.334 | -0.17395 | 0.27466 | 123.2391 | -123.4726 | -123.4589
381.1094 | 123.2758 | -122.8043 | 0.32501 | -0.0031279 | 0.017306 | 0.0075943 | -0.018831 | -0.0046143 | 0.064279 | 0.068567 | -5.5206 | 0.37994 | -123.1384 | 0.33875 | -122.5937 | -123.0469 | -0.2243 | 0.14648 | 0.37994 | -123.1201 | -0.33417 | 0.054932 | 117.2836 | 123.143 | -122.9187 | -0.31586 | 0.054932 | 117.6178 | 122.58 | 122.9507 | 0.21057 | 123.1842 | 117.2836 | 123.1842 | -0.24262 | -0.31586 | 123.1842 | 117.2836 | -0.24262 | 0.21057 | 123.1842 | -123.4634 | -123.4451
382.7812 | 123.175 | -122.8821 | 0.33417 | 0.0045011 | 0.019228 | 0.014003 | -0.01285 | -0.0071777 | 0.061075 | 0.069848 | -5.5481 | 0.39368 | -123.2391 | 0.28381 | -122.6669 | -123.1293 | -0.15106 | 0.050354 | 0.41199 | -123.0881 | -0.35706 | 0.05951 | 117.334 | 123.1659 | -123.0011 | -0.20599 | 0.07782 | 117.691 | 122.731 | 122.9324 | 0.21515 | 123.2758 | 117.334 | 123.2941 | -0.24719 | -0.20599 | 123.2758 | 117.334 | -0.24719 | 0.21515 | 123.2941 | -123.5733 | -123.4222
384.5312 | 123.2025 | -122.8271 | 0.30212 | -0.010757 | 0.017733 | 0.011012 | -0.017976 | -0.0091003 | 0.06492 | 0.070062 | -5.5252 | 0.37079 | -123.1522 | 0.37537 | -122.5433 | -123.0011 | -0.31128 | 0.17853 | 0.36163 | -123.1018 | -0.32501 | 0.068665 | 117.3019 | 123.2025 | -122.8455 | -0.27466 | 0.059509 | 117.627 | 122.5159 | 123.0057 | 0.28381 | 123.1979 | 117.3019 | 123.1888 | -0.17395 | -0.27466 | 123.1979 | 117.3019 | -0.17395 | 0.28381 | 123.1888 | -123.4543 | -123.4039
386.2344 | 123.2666 | -122.8592 | 0.31128 | 0.0045011 | 0.017947 | 0.0065263 | -0.016054 | -0.0086731 | 0.063852 | 0.068994 | -5.5573 | 0.35706 | -123.2254 | 0.26093 | -122.6395 | -123.0881 | -0.1831 | 0.10986 | 0.36621 | -123.1705 | -0.36621 | 0.045777 | 117.3019 | 123.1201 | -122.9507 | -0.31128 | 0.054932 | 117.6682 | 122.6761 | 122.9691 | 0.21973 | 123.2162 | 117.3019 | 123.2254 | -0.22888 | -0.31128 | 123.2162 | 117.3019 | -0.22888 | 0.21973 | 123.2254 | -123.5367 | -123.4818
387.9844 | 123.2254 | -122.8455 | 0.28381 | 0.012131 | 0.014529 | 0.0071671 | -0.017122 | -0.0073913 | 0.063211 | 0.068353 | -5.5435 | 0.33417 | -123.1796 | 0.31128 | -122.5937 | -123.0606 | -0.28839 | 0.17395 | 0.33875 | -123.1338 | -0.33417 | 0.050354 | 117.3019 | 123.1567 | -122.8775 | -0.28839 | 0.054932 | 117.6361 | 122.5571 | 123.0194 | 0.25177 | 123.1796 | 117.3019 | 123.1842 | -0.21515 | -0.28839 | 123.1796 | 117.3019 | -0.21515 | 0.25177 | 123.1842 | -123.4634 | -123.4177
389.7188 | 123.1384 | -122.8683 | 0.30212 | -0.010757 | 0.016878 | 0.012294 | -0.01285 | -0.0086731 | 0.065134 | 0.071771 | -5.5161 | 0.32501 | -123.2025 | 0.31128 | -122.5983 | -123.0423 | -0.35706 | 0.10986 | 0.31586 | -123.1522 | -0.33417 | 0.022888 | 117.3523 | 123.1796 | -122.9004 | -0.28381 | 0.013733 | 117.6865 | 122.5113 | 122.9782 | 0.27008 | 123.1934 | 117.3523 | 123.1842 | -0.17395 | -0.28381 | 123.1934 | 117.3523 | -0.17395 | 0.27008 | 123.1842 | -123.5046 | -123.4543
391.4688 | 123.2254 | -122.8455 | 0.27924 | 0.012131 | 0.016238 | 0.0095169 | -0.018831 | -0.0080323 | 0.064493 | 0.06878 | -5.5389 | 0.3479 | -123.1705 | 0.32501 | -122.58 | -123.0286 | -0.33875 | 0.16022 | 0.34332 | -123.143 | -0.32501 | 0.068664 | 117.3065 | 123.1705 | -122.8592 | -0.29755 | 0.064087 | 117.6315 | 122.5067 | 123.0057 | 0.2655 | 123.1934 | 117.3065 | 123.1888 | -0.1831 | -0.29755 | 123.1934 | 117.3065 | -0.1831 | 0.2655 | 123.1888 | -123.4497 | -123.4222
393.2188 | 123.143 | -122.8867 | 0.29755 | 0.0045011 | 0.019656 | 0.0086625 | -0.011568 | -0.0065369 | 0.060434 | 0.069207 | -5.5573 | 0.36163 | -123.2346 | 0.2655 | -122.6532 | -123.1476 | -0.19226 | 0.13733 | 0.37079 | -123.1338 | -0.3479 | 0.064087 | 117.3294 | 123.1522 | -122.9507 | -0.24719 | 0.073243 | 117.6773 | 122.6944 | 123.024 | 0.23346 | 123.2483 | 117.3294 | 123.2574 | -0.26093 | -0.24719 | 123.2483 | 117.3294 | -0.26093 | 0.23346 | 123.2574 | -123.5321 | -123.4314
394.8906 | 123.2758 | -122.8455 | 0.25177 | -0.010757 | 0.016878 | 0.0097305 | -0.016695 | -0.0084595 | 0.06257 | 0.070916 | -5.6396 | 0.38452 | -123.2483 | 0.20599 | -122.7081 | -123.1567 | -0.1236 | 0.059509 | 0.37537 | -123.143 | -0.40283 | 0.13275 | 117.2058 | 123.0515 | -122.9599 | -0.29755 | 0.1236 | 117.6086 | 122.7219 | 122.905 | 0.13733 | 123.23 | 117.2058 | 123.2208 | -0.31128 | -0.29755 | 123.23 | 117.2058 | -0.31128 | 0.13733 | 123.2208 | -123.5001 | -123.3948
396.6406 | 123.1705 | -122.8867 | 0.28381 | 0.0045011 | 0.020937 | 0.010799 | -0.011781 | -0.0046143 | 0.061929 | 0.069635 | -5.5756 | 0.3479 | -123.2437 | 0.25177 | -122.6486 | -123.111 | -0.15106 | 0.1236 | 0.36621 | -123.1293 | -0.35706 | 0.064087 | 117.3111 | 123.1384 | -122.9324 | -0.24261 | 0.082398 | 117.6682 | 122.7356 | 123.0103 | 0.23804 | 123.2346 | 117.3111 | 123.2529 | -0.2243 | -0.24261 | 123.2346 | 117.3111 | -0.2243 | 0.23804 | 123.2529 | -123.5275 | -123.4131
398.3906 | 123.2391 | -122.8317 | 0.27466 | 0.0045011 | 0.016451 | 0.0099441 | -0.017763 | -0.0071777 | 0.06022 | 0.069421 | -5.5801 | 0.32501 | -123.2162 | 0.29755 | -122.5983 | -123.0789 | -0.21515 | 0.13733 | 0.35706 | -123.1201 | -0.38452 | 0.050354 | 117.2516 | 123.1293 | -122.8729 | -0.28839 | 0.082398 | 117.6361 | 122.6166 | 122.9691 | 0.23346 | 123.1567 | 117.2516 | 123.1888 | -0.24719 | -0.28839 | 123.1567 | 117.2516 | -0.24719 | 0.23346 | 123.1888 | -123.4909 | -123.3948
400.1406 | 123.2529 | -122.8226 | 0.28839 | 0.0045011 | 0.015597 | 0.01443 | -0.014345 | -0.0067505 | 0.063852 | 0.067498 | -5.6259 | 0.39368 | -123.2437 | 0.23804 | -122.6624 | -123.1476 | -0.11444 | 0.086975 | 0.40283 | -123.1064 | -0.42114 | 0.10529 | 117.1967 | 123.0606 | -122.9507 | -0.28381 | 0.11444 | 117.6178 | 122.7081 | 122.9095 | 0.16022 | 123.2162 | 117.1967 | 123.2254 | -0.32501 | -0.28381 | 123.2162 | 117.1967 | -0.32501 | 0.16022 | 123.2254 | -123.5321 | -123.3948
401.8281 | 123.1201 | -122.8729 | 0.32959 | -0.0031279 | 0.018801 | 0.011012 | -0.015627 | -0.0054687 | 0.062143 | 0.069635 | -5.5527 | 0.36163 | -123.175 | 0.31586 | -122.5937 | -123.0423 | -0.33417 | 0.1236 | 0.34332 | -123.1201 | -0.30212 | 0.032043 | 117.3203 | 123.1888 | -122.9233 | -0.24719 | 0.013733 | 117.6224 | 122.5388 | 122.9965 | 0.27924 | 123.2346 | 117.3203 | 123.2162 | -0.16937 | -0.24719 | 123.2346 | 117.3203 | -0.16937 | 0.27924 | 123.2162 | -123.5046 | -123.4497
403.5781 | 123.1338 | -122.8683 | 0.29755 | -0.0031279 | 0.018374 | 0.016139 | -0.012422 | -0.0071777 | 0.06257 | 0.070489 | -5.5481 | 0.35706 | -123.2254 | 0.27008 | -122.6349 | -123.1155 | -0.16479 | 0.11444 | 0.36163 | -123.1384 | -0.35706 | 0.05951 | 117.3203 | 123.1384 | -122.9324 | -0.27008 | 0.064087 | 117.6773 | 122.7036 | 122.9828 | 0.23346 | 123.2254 | 117.3203 | 123.23 | -0.24719 | -0.27008 | 123.2254 | 117.3203 | -0.24719 | 0.23346 | 123.23 | -123.5229 | -123.436
405.2656 | 123.1659 | -122.8821 | 0.28839 | 0.0045011 | 0.019442 | 0.01208 | -0.013704 | -0.0041871 | 0.063638 | 0.070062 | -5.6259 | 0.36621 | -123.2483 | 0.19226 | -122.699 | -123.1476 | -0.21973 | 0.032043 | 0.35706 | -123.1247 | -0.36621 | 0.07782 | 117.2562 | 123.0743 | -122.9874 | -0.24262 | 0.068665 | 117.6224 | 122.6624 | 122.9141 | 0.1831 | 123.2483 | 117.2562 | 123.2391 | -0.2655 | -0.24262 | 123.2483 | 117.2562 | -0.2655 | 0.1831 | 123.2391 | -123.5367 | -123.4131
407.0156 | 123.2391 | -122.8409 | 0.25177 | -0.0031279 | 0.018587 | 0.010158 | -0.022249 | -0.0058961 | 0.066415 | 0.070703 | -5.6396 | 0.33417 | -123.1979 | 0.23346 | -122.6349 | -123.0927 | -0.29297 | 0.050354 | 0.32501 | -123.1613 | -0.35706 | 0.082397 | 117.2012 | 123.0743 | -122.8867 | -0.32044 | 0.073242 | 117.5583 | 122.5479 | 122.8912 | 0.20599 | 123.175 | 117.2012 | 123.1659 | -0.25177 | -0.32044 | 123.175 | 117.2012 | -0.25177 | 0.20599 | 123.1659 | -123.4497 | -123.4131
408.7031 | 123.2574 | -122.8683 | 0.26093 | -0.010757 | 0.015383 | 0.011439 | -0.015413 | -0.0093139 | 0.063638 | 0.071985 | -5.6305 | 0.32501 | -123.2162 | 0.21973 | -122.6715 | -123.1338 | -0.16022 | 0.086975 | 0.37079 | -123.1567 | -0.3479 | 0.064087 | 117.2379 | 123.0881 | -122.9324 | -0.28839 | 0.10986 | 117.5858 | 122.7081 | 122.9553 | 0.19684 | 123.1934 | 117.2379 | 123.2391 | -0.2655 | -0.28839 | 123.1934 | 117.2379 | -0.2655 | 0.19684 | 123.2391 | -123.4772 | -123.4177
410.4531 | 123.1567 | -122.905 | 0.27924 | -0.0031279 | 0.016238 | 0.010371 | -0.011354 | -0.0069641 | 0.06257 | 0.070062 | -5.6396 | 0.35248 | -123.2529 | 0.20599 | -122.7264 | -123.1934 | -0.14648 | 0.045776 | 0.34332 | -123.1888 | -0.3479 | 0.073242 | 117.2653 | 123.111 | -123.0057 | -0.28381 | 0.064087 | 117.6132 | 122.7585 | 122.9507 | 0.17853 | 123.2574 | 117.2653 | 123.2483 | -0.28839 | -0.28381 | 123.2574 | 117.2653 | -0.28839 | 0.17853 | 123.2483 | -123.5321 | -123.468
412.2031 | 123.2391 | -122.85 | 0.25635 | -0.0031279 | 0.016878 | 0.0093033 | -0.019899 | -0.0084595 | 0.064493 | 0.069207 | -5.6488 | 0.32959 | -123.2025 | 0.2655 | -122.6028 | -123.0652 | -0.32501 | 0.11444 | 0.30212 | -123.143 | -0.35248 | 0.073242 | 117.2012 | 123.1155 | -122.8592 | -0.29297 | 0.045776 | 117.5537 | 122.525 | 122.9645 | 0.24719 | 123.1796 | 117.2012 | 123.1522 | -0.21515 | -0.29297 | 123.1796 | 117.2012 | -0.21515 | 0.24719 | 123.1522 | -123.4589 | -123.3994
413.9531 | 123.1522 | -122.8729 | 0.27466 | 0.0045011 | 0.019228 | 0.013576 | -0.014558 | -0.0067505 | 0.06492 | 0.070276 | -5.6396 | 0.3479 | -123.2529 | 0.23346 | -122.6715 | -123.111 | -0.28381 | 0.086975 | 0.33417 | -123.1476 | -0.37994 | 0.073242 | 117.2333 | 123.1064 | -122.9462 | -0.27466 | 0.059509 | 117.6132 | 122.5891 | 122.9599 | 0.20142 | 123.2208 | 117.2333 | 123.2071 | -0.23804 | -0.27466 | 123.2208 | 117.2333 | -0.23804 | 0.20142 | 123.2071 | -123.5275 | -123.4222
415.6875 | 123.1155 | -122.8912 | 0.31128 | 0.012131 | 0.016238 | 0.011439 | -0.012636 | -0.0039735 | 0.062997 | 0.070916 | -5.5893 | 0.32959 | -123.2025 | 0.27924 | -122.6074 | -123.0469 | -0.33875 | 0.11902 | 0.32501 | -123.1018 | -0.31128 | 0.018311 | 117.3019 | 123.1705 | -122.9187 | -0.21057 | 0.013733 | 117.6132 | 122.5525 | 123.0103 | 0.28381 | 123.2208 | 117.3019 | 123.2162 | -0.15564 | -0.21057 | 123.2208 | 117.3019 | -0.15564 | 0.28381 | 123.2162 | -123.5138 | -123.4131
417.375 | 123.2162 | -122.8775 | 0.23804 | 0.0045011 | 0.016451 | 0.0082351 | -0.018404 | -0.0073913 | 0.06257 | 0.069207 | -5.5984 | 0.29755 | -123.2071 | 0.29297 | -122.6166 | -123.0743 | -0.25635 | 0.17395 | 0.30212 | -123.143 | -0.32959 | 0.059509 | 117.2791 | 123.1705 | -122.8546 | -0.2655 | 0.064087 | 117.6086 | 122.6212 | 123.0515 | 0.26093 | 123.175 | 117.2791 | 123.1796 | -0.19684 | -0.2655 | 123.175 | 117.2791 | -0.19684 | 0.26093 | 123.1796 | -123.4451 | -123.381
419.1094 | 123.2346 | -122.8821 | 0.23804 | 0.0045011 | 0.016451 | 0.0084489 | -0.020967 | -0.0091003 | 0.065775 | 0.068567 | -5.6351 | 0.3067 | -123.2208 | 0.2655 | -122.6212 | -123.0698 | -0.32501 | 0.13733 | 0.30212 | -123.1796 | -0.33875 | 0.068665 | 117.247 | 123.1476 | -122.8592 | -0.29755 | 0.064087 | 117.5858 | 122.5571 | 123.0194 | 0.26093 | 123.1888 | 117.247 | 123.1842 | -0.18768 | -0.29755 | 123.1888 | 117.247 | -0.18768 | 0.26093 | 123.1842 | -123.4589 | -123.4177
420.7812 | 123.2025 | -122.8821 | 0.2243 | -0.0031279 | 0.016238 | 0.0099441 | -0.017336 | -0.0073913 | 0.063638 | 0.070276 | -5.603 | 0.30212 | -123.2025 | 0.32501 | -122.5891 | -123.0377 | -0.33417 | 0.17395 | 0.29297 | -123.1659 | -0.32044 | 0.07782 | 117.2791 | 123.2071 | -122.8134 | -0.28381 | 0.068665 | 117.5995 | 122.5479 | 123.056 | 0.29297 | 123.1842 | 117.2791 | 123.175 | -0.15564 | -0.28381 | 123.1842 | 117.2791 | -0.15564 | 0.29297 | 123.175 | -123.4268 | -123.3902
422.5156 | 123.1247 | -122.9233 | 0.26093 | -0.010757 | 0.019015 | 0.011867 | -0.010927 | -0.0061097 | 0.064066 | 0.071557 | -5.6168 | 0.32501 | -123.2849 | 0.23346 | -122.699 | -123.1613 | -0.16022 | 0.11902 | 0.32959 | -123.1247 | -0.36163 | 0.064087 | 117.3065 | 123.1567 | -122.9599 | -0.20142 | 0.068665 | 117.6682 | 122.7631 | 123.0423 | 0.2243 | 123.2483 | 117.3065 | 123.2529 | -0.23804 | -0.20142 | 123.2483 | 117.3065 | -0.23804 | 0.2243 | 123.2529 | -123.5458 | -123.3856
424.25 | 123.1934 | -122.9095 | 0.23346 | -0.0031279 | 0.016665 | 0.014217 | -0.015199 | -0.0050415 | 0.064279 | 0.069848 | -5.6305 | 0.3067 | -123.2895 | 0.19226 | -122.699 | -123.1705 | -0.16022 | 0.11444 | 0.31586 | -123.1705 | -0.37994 | 0.073243 | 117.2791 | 123.1018 | -122.9324 | -0.26093 | 0.082398 | 117.659 | 122.7493 | 123.024 | 0.21057 | 123.2162 | 117.2791 | 123.2254 | -0.26093 | -0.26093 | 123.2162 | 117.2791 | -0.26093 | 0.21057 | 123.2254 | -123.5229 | -123.4039
425.9844 | 123.1705 | -122.9233 | 0.24261 | 0.012131 | 0.017306 | 0.0086625 | -0.014345 | -0.0056823 | 0.063852 | 0.07113 | -5.69 | 0.31128 | -123.2529 | 0.13733 | -122.7631 | -123.2117 | -0.1831 | 0.032043 | 0.31128 | -123.1934 | -0.32959 | 0.068664 | 117.2333 | 123.0606 | -123.0057 | -0.27008 | 0.068664 | 117.5629 | 122.7402 | 122.9553 | 0.16022 | 123.2346 | 117.2333 | 123.2346 | -0.28839 | -0.27008 | 123.2346 | 117.2333 | -0.28839 | 0.16022 | 123.2346 | -123.4955 | -123.436
427.6719 | 123.1567 | -122.9416 | 0.24261 | 0.0045011 | 0.018587 | 0.010158 | -0.014558 | -0.0063233 | 0.06257 | 0.072198 | -5.6808 | 0.32044 | -123.3032 | 0.14648 | -122.7676 | -123.23 | -0.14191 | 0.018311 | 0.31586 | -123.1979 | -0.36163 | 0.07782 | 117.2607 | 123.0881 | -123.0103 | -0.25635 | 0.073242 | 117.6224 | 122.7997 | 122.9599 | 0.17395 | 123.262 | 117.2607 | 123.2574 | -0.28839 | -0.25635 | 123.262 | 117.2607 | -0.28839 | 0.17395 | 123.2574 | -123.5458 | -123.4406
429.4062 | 123.2025 | -122.8958 | 0.23804 | 0.0045011 | 0.01816 | 0.0097305 | -0.014345 | -0.0044007 | 0.062143 | 0.071344 | -5.6671 | 0.32044 | -123.2574 | 0.17853 | -122.6944 | -123.1659 | -0.13733 | 0.1236 | 0.32501 | -123.1567 | -0.36163 | 0.082398 | 117.2287 | 123.0743 | -122.9324 | -0.26093 | 0.086975 | 117.5903 | 122.7585 | 123.0194 | 0.20142 | 123.2162 | 117.2287 | 123.2208 | -0.27008 | -0.26093 | 123.2162 | 117.2287 | -0.27008 | 0.20142 | 123.2208 | -123.4955 | -123.3948
431.1562 | 123.262 | -122.8775 | 0.2243 | 0.012131 | 0.017947 | 0.011867 | -0.017549 | -0.0088867 | 0.064279 | 0.07113 | -5.722 | 0.33417 | -123.262 | 0.14191 | -122.731 | -123.1934 | -0.09613 | 0.050354 | 0.32959 | -123.1796 | -0.38452 | 0.10986 | 117.1555 | 123.0194 | -122.9553 | -0.30212 | 0.10529 | 117.54 | 122.7814 | 122.9279 | 0.14648 | 123.2117 | 117.1555 | 123.2071 | -0.31586 | -0.30212 | 123.2117 | 117.1555 | -0.31586 | 0.14648 | 123.2071 | -123.4863 | -123.4039
432.8438 | 123.2758 | -122.8729 | 0.21973 | -0.010757 | 0.021151 | 0.012294 | -0.021181 | -0.0088867 | 0.064706 | 0.069635 | -5.6992 | 0.32959 | -123.2666 | 0.16022 | -122.6898 | -123.1888 | -0.11444 | 0.064087 | 0.33417 | -123.2162 | -0.39368 | 0.10986 | 117.1738 | 123.0331 | -122.9095 | -0.34332 | 0.11444 | 117.5674 | 122.7585 | 122.937 | 0.18311 | 123.2025 | 117.1738 | 123.2071 | -0.31586 | -0.34332 | 123.2025 | 117.1738 | -0.31586 | 0.18311 | 123.2071 | -123.4863 | -123.436
434.5781 | 123.2437 | -122.8546 | 0.22888 | 0.0045011 | 0.018374 | 0.013362 | -0.018404 | -0.0067505 | 0.065988 | 0.071344 | -5.6625 | 0.31586 | -123.2162 | 0.1831 | -122.6852 | -123.1659 | -0.16022 | 0.09613 | 0.32501 | -123.1705 | -0.36163 | 0.086975 | 117.1921 | 123.0377 | -122.9141 | -0.31586 | 0.09613 | 117.5537 | 122.6944 | 122.9507 | 0.16937 | 123.1705 | 117.1921 | 123.1796 | -0.31128 | -0.31586 | 123.1705 | 117.1921 | -0.31128 | 0.16937 | 123.1796 | -123.4451 | -123.3994
436.3125 | 123.2483 | -122.85 | 0.21973 | 0.01976 | 0.016451 | 0.013362 | -0.021181 | -0.0078187 | 0.065561 | 0.069635 | -5.6992 | 0.29755 | -123.1842 | 0.21973 | -122.6532 | -123.0972 | -0.31586 | 0.086975 | 0.3067 | -123.1705 | -0.33417 | 0.077819 | 117.1509 | 123.0698 | -122.8729 | -0.32043 | 0.086975 | 117.485 | 122.5342 | 122.937 | 0.19684 | 123.1476 | 117.1509 | 123.1567 | -0.24719 | -0.32043 | 123.1476 | 117.1509 | -0.24719 | 0.19684 | 123.1567 | -123.4039 | -123.3902
438.0625 | 123.1567 | -122.8867 | 0.24261 | 0.012131 | 0.018374 | 0.013576 | -0.012636 | -0.0052551 | 0.062997 | 0.070489 | -5.6763 | 0.33417 | -123.262 | 0.16479 | -122.7493 | -123.2117 | -0.12817 | 0.004578 | 0.33417 | -123.2025 | -0.37537 | 0.091552 | 117.2104 | 123.0515 | -122.9919 | -0.31586 | 0.091552 | 117.5858 | 122.7585 | 122.8912 | 0.13733 | 123.2208 | 117.2104 | 123.2208 | -0.32501 | -0.31586 | 123.2208 | 117.2104 | -0.32501 | 0.13733 | 123.2208 | -123.5046 | -123.4451
439.75 | 123.1018 | -122.905 | 0.2655 | 0.012131 | 0.01816 | 0.013148 | -0.017549 | -0.0041871 | 0.065347 | 0.070489 | -5.5939 | 0.28381 | -123.1842 | 0.2655 | -122.6303 | -123.0423 | -0.39825 | 0.11902 | 0.27924 | -123.1659 | -0.27924 | 0.01831 | 117.3111 | 123.1705 | -122.8958 | -0.26093 | 0.013733 | 117.5903 | 122.5067 | 123.024 | 0.27466 | 123.1888 | 117.3111 | 123.1842 | -0.13733 | -0.26093 | 123.1888 | 117.3111 | -0.13733 | 0.27466 | 123.1842 | -123.4497 | -123.4314
441.4844 | 123.1567 | -122.905 | 0.25635 | 0.0045011 | 0.017947 | 0.012721 | -0.013277 | -0.0048279 | 0.061288 | 0.070062 | -5.6946 | 0.33417 | -123.2986 | 0.15564 | -122.7402 | -123.2117 | -0.13275 | 0.018311 | 0.33417 | -123.175 | -0.39368 | 0.077819 | 117.2104 | 123.0606 | -122.9965 | -0.27008 | 0.077819 | 117.6041 | 122.7722 | 122.9233 | 0.16479 | 123.2391 | 117.2104 | 123.2391 | -0.3067 | -0.27008 | 123.2391 | 117.2104 | -0.3067 | 0.16479 | 123.2391 | -123.555 | -123.4314
443.2344 | 123.1338 | -122.8958 | 0.24719 | 0.0045011 | 0.016451 | 0.013148 | -0.017549 | -0.0063233 | 0.065775 | 0.070916 | -5.6213 | 0.30212 | -123.1613 | 0.24261 | -122.6303 | -123.0881 | -0.38452 | 0.09613 | 0.30212 | -123.1659 | -0.2655 | 0.054932 | 117.2745 | 123.1384 | -122.8775 | -0.27008 | 0.054932 | 117.54 | 122.5113 | 122.9919 | 0.2655 | 123.1979 | 117.2745 | 123.1979 | -0.19226 | -0.27008 | 123.1979 | 117.2745 | -0.19226 | 0.2655 | 123.1979 | -123.4085 | -123.4131
444.9844 | 123.143 | -122.9095 | 0.26093 | 0.0045011 | 0.019228 | 0.010585 | -0.011781 | -0.0061097 | 0.062357 | 0.070916 | -5.6488 | 0.33875 | -123.2574 | 0.18768 | -122.7173 | -123.175 | -0.14191 | 0.050354 | 0.32501 | -123.1705 | -0.3479 | 0.07782 | 117.2607 | 123.0972 | -122.9782 | -0.26093 | 0.064087 | 117.6086 | 122.7676 | 122.9599 | 0.19226 | 123.2483 | 117.2607 | 123.2346 | -0.2655 | -0.26093 | 123.2483 | 117.2607 | -0.2655 | 0.19226 | 123.2346 | -123.5184 | -123.4314
446.6719 | 123.1796 | -122.8729 | 0.20599 | 0.0045011 | 0.01581 | 0.0075943 | -0.021608 | -0.0080323 | 0.065134 | 0.069848 | -5.6717 | 0.3067 | -123.23 | 0.26093 | -122.6028 | -123.0515 | -0.33417 | 0.13733 | 0.30212 | -123.1384 | -0.35706 | 0.10071 | 117.2012 | 123.1338 | -122.8088 | -0.2655 | 0.09613 | 117.5583 | 122.5388 | 123.0103 | 0.27008 | 123.1796 | 117.2012 | 123.175 | -0.17853 | -0.2655 | 123.1796 | 117.2012 | -0.17853 | 0.27008 | 123.175 | -123.436 | -123.3444
448.4062 | 123.2208 | -122.8683 | 0.21973 | -0.010757 | 0.01581 | 0.011653 | -0.019685 | -0.0082459 | 0.066629 | 0.069848 | -5.6946 | 0.29755 | -123.1979 | 0.24261 | -122.6349 | -123.0743 | -0.32501 | 0.10071 | 0.29297 | -123.1613 | -0.32959 | 0.077819 | 117.1738 | 123.111 | -122.8546 | -0.29297 | 0.073242 | 117.5034 | 122.5433 | 122.9691 | 0.23346 | 123.1659 | 117.1738 | 123.1613 | -0.20599 | -0.29297 | 123.1659 | 117.1738 | -0.20599 | 0.23346 | 123.1613 | -123.4177 | -123.381
450.1562 | 123.2391 | -122.8592 | 0.25177 | 0.0045011 | 0.014956 | 0.0097305 | -0.016695 | -0.0091003 | 0.065347 | 0.070062 | -5.6671 | 0.31586 | -123.2346 | 0.20599 | -122.6669 | -123.1338 | -0.16479 | 0.09613 | 0.33417 | -123.175 | -0.37537 | 0.064087 | 117.1921 | 123.0652 | -122.9187 | -0.31586 | 0.082397 | 117.5674 | 122.6944 | 122.9553 | 0.19226 | 123.175 | 117.1921 | 123.1934 | -0.27466 | -0.31586 | 123.175 | 117.1921 | -0.27466 | 0.19226 | 123.1934 | -123.4863 | -123.4268
451.8438 | 123.2346 | -122.8592 | 0.24261 | -0.0031279 | 0.01581 | 0.0069535 | -0.017336 | -0.010596 | 0.065988 | 0.069635 | -5.69 | 0.3067 | -123.1979 | 0.24261 | -122.6303 | -123.0881 | -0.32044 | 0.09613 | 0.31586 | -123.1659 | -0.33875 | 0.064087 | 117.1692 | 123.1018 | -122.8729 | -0.3067 | 0.073242 | 117.5079 | 122.5388 | 122.9553 | 0.22888 | 123.1659 | 117.1692 | 123.175 | -0.22888 | -0.3067 | 123.1659 | 117.1692 | -0.22888 | 0.22888 | 123.175 | -123.4406 | -123.4085
453.5781 | 123.0972 | -122.9141 | 0.25635 | -0.0031279 | 0.017733 | 0.011012 | -0.013063 | -0.0054687 | 0.06257 | 0.069207 | -5.6213 | 0.32501 | -123.2437 | 0.22888 | -122.6761 | -123.1384 | -0.16937 | 0.10986 | 0.31586 | -123.1567 | -0.32959 | 0.068664 | 117.2928 | 123.143 | -122.9324 | -0.24261 | 0.059509 | 117.6224 | 122.7448 | 123.024 | 0.23804 | 123.2391 | 117.2928 | 123.23 | -0.2243 | -0.24261 | 123.2391 | 117.2928 | -0.2243 | 0.23804 | 123.23 | -123.5001 | -123.4131
455.3281 | 123.2071 | -122.8363 | 0.23804 | 0.0045011 | 0.017519 | 0.014217 | -0.013704 | -0.0058961 | 0.06257 | 0.071344 | -5.7266 | 0.33875 | -123.2712 | 0.19226 | -122.6807 | -123.1613 | -0.13275 | 0.091553 | 0.3479 | -123.1567 | -0.43488 | 0.10071 | 117.1097 | 123.0286 | -122.9187 | -0.32043 | 0.10986 | 117.5446 | 122.7036 | 122.9279 | 0.15564 | 123.175 | 117.1097 | 123.1842 | -0.32501 | -0.32043 | 123.175 | 117.1097 | -0.32501 | 0.15564 | 123.1842 | -123.5092 | -123.3948
457.0625 | 123.2391 | -122.8409 | 0.23346 | -0.0031279 | 0.01816 | 0.0095169 | -0.016267 | -0.0082459 | 0.06492 | 0.070703 | -5.7449 | 0.34332 | -123.2437 | 0.17853 | -122.6944 | -123.175 | -0.09613 | 0.054932 | 0.3479 | -123.1979 | -0.40283 | 0.10986 | 117.0959 | 123.0194 | -122.9279 | -0.35706 | 0.11444 | 117.4988 | 122.7448 | 122.8958 | 0.14648 | 123.1842 | 117.0959 | 123.1888 | -0.33417 | -0.35706 | 123.1842 | 117.0959 | -0.33417 | 0.14648 | 123.1888 | -123.4772 | -123.4314
458.7344 | 123.1476 | -122.8821 | 0.27008 | 0.0045011 | 0.018374 | 0.012721 | -0.014558 | -0.0052551 | 0.062357 | 0.070276 | -5.6808 | 0.33875 | -123.262 | 0.1831 | -122.6944 | -123.1659 | -0.14648 | 0.036621 | 0.32501 | -123.1338 | -0.37994 | 0.068664 | 117.2012 | 123.0652 | -122.9645 | -0.25177 | 0.054931 | 117.5812 | 122.7356 | 122.9187 | 0.18768 | 123.2208 | 117.2012 | 123.2071 | -0.28381 | -0.25177 | 123.2208 | 117.2012 | -0.28381 | 0.18768 | 123.2071 | -123.5321 | -123.4039
460.5 | 123.2025 | -122.8455 | 0.25635 | -0.0031279 | 0.019656 | 0.010585 | -0.021181 | -0.0076049 | 0.06492 | 0.070276 | -5.6625 | 0.32501 | -123.2025 | 0.25635 | -122.5891 | -123.0743 | -0.2243 | 0.14648 | 0.32501 | -123.1613 | -0.35706 | 0.068664 | 117.1829 | 123.1018 | -122.8455 | -0.31586 | 0.068664 | 117.54 | 122.6212 | 122.9919 | 0.25635 | 123.1705 | 117.1829 | 123.1705 | -0.22888 | -0.31586 | 123.1705 | 117.1829 | -0.22888 | 0.25635 | 123.1705 | -123.4589 | -123.4177
462.1719 | 123.1155 | -122.8775 | 0.26093 | 0.0045011 | 0.017092 | 0.010799 | -0.017976 | -0.0067505 | 0.063852 | 0.072198 | -5.6625 | 0.3067 | -123.1979 | 0.27008 | -122.6166 | -123.0515 | -0.36621 | 0.091553 | 0.29297 | -123.1201 | -0.32043 | 0.045777 | 117.215 | 123.1476 | -122.8775 | -0.24261 | 0.032044 | 117.5354 | 122.5113 | 122.9691 | 0.26093 | 123.1842 | 117.215 | 123.1705 | -0.17395 | -0.24261 | 123.1842 | 117.215 | -0.17395 | 0.26093 | 123.1705 | -123.4589 | -123.381
463.9062 | 123.2162 | -122.8363 | 0.2243 | 0.012131 | 0.017519 | 0.0090897 | -0.019472 | -0.0088867 | 0.062784 | 0.069635 | -5.7266 | 0.31128 | -123.1659 | 0.21515 | -122.6303 | -123.0835 | -0.31128 | 0.054932 | 0.29755 | -123.1567 | -0.32959 | 0.086975 | 117.1097 | 123.0515 | -122.8546 | -0.32043 | 0.073242 | 117.4393 | 122.525 | 122.8912 | 0.20599 | 123.1476 | 117.1097 | 123.1338 | -0.24719 | -0.32043 | 123.1476 | 117.1097 | -0.24719 | 0.20599 | 123.1338 | -123.3902 | -123.381
465.6562 | 123.1979 | -122.8409 | 0.23346 | -0.0031279 | 0.016878 | 0.0078079 | -0.018617 | -0.0078187 | 0.063852 | 0.068139 | -5.722 | 0.32501 | -123.1705 | 0.23804 | -122.612 | -123.0743 | -0.31586 | 0.091553 | 0.3067 | -123.1888 | -0.32959 | 0.091553 | 117.1188 | 123.0789 | -122.8455 | -0.3479 | 0.073243 | 117.4484 | 122.525 | 122.9324 | 0.22888 | 123.1659 | 117.1188 | 123.1476 | -0.23346 | -0.3479 | 123.1659 | 117.1188 | -0.23346 | 0.22888 | 123.1476 | -123.4039 | -123.4222
467.3906 | 123.1979 | -122.8683 | 0.24261 | 0.012131 | 0.018801 | 0.0090897 | -0.017976 | -0.0078187 | 0.064066 | 0.06878 | -5.6992 | 0.32501 | -123.1934 | 0.27466 | -122.5891 | -123.056 | -0.32044 | 0.1236 | 0.30212 | -123.1476 | -0.32501 | 0.082397 | 117.1692 | 123.143 | -122.8317 | -0.27924 | 0.059509 | 117.4942 | 122.5479 | 122.9919 | 0.27924 | 123.1934 | 117.1692 | 123.1705 | -0.18768 | -0.27924 | 123.1934 | 117.1692 | -0.18768 | 0.27924 | 123.1705 | -123.436 | -123.3902
469.125 | 123.2117 | -122.8226 | 0.24261 | -0.0031279 | 0.015597 | 0.011653 | -0.016267 | -0.0078187 | 0.062784 | 0.07113 | -5.7083 | 0.3067 | -123.2071 | 0.24719 | -122.6395 | -123.0743 | -0.32959 | 0.059509 | 0.32044 | -123.1384 | -0.38452 | 0.064087 | 117.1143 | 123.0698 | -122.8821 | -0.31586 | 0.07782 | 117.4988 | 122.493 | 122.8821 | 0.18311 | 123.1293 | 117.1143 | 123.143 | -0.25177 | -0.31586 | 123.1293 | 117.1143 | -0.25177 | 0.18311 | 123.143 | -123.4497 | -123.381
470.7969 | 123.1155 | -122.8546 | 0.26093 | 0.0045011 | 0.017947 | 0.012935 | -0.015413 | -0.0063233 | 0.064706 | 0.069848 | -5.6351 | 0.32044 | -123.1705 | 0.29297 | -122.5845 | -123.0377 | -0.38452 | 0.10986 | 0.29755 | -123.1064 | -0.31586 | 0.05951 | 117.2195 | 123.1476 | -122.8455 | -0.25177 | 0.036621 | 117.5354 | 122.4701 | 122.9645 | 0.27008 | 123.175 | 117.2195 | 123.1522 | -0.18311 | -0.25177 | 123.175 | 117.2195 | -0.18311 | 0.27008 | 123.1522 | -123.4314 | -123.3673
472.5469 | 123.1064 | -122.8317 | 0.27924 | -0.0031279 | 0.01816 | 0.0080215 | -0.0090041 | -0.0078187 | 0.061288 | 0.068994 | -5.6625 | 0.36621 | -123.2162 | 0.27924 | -122.6349 | -123.0881 | -0.19226 | 0.11902 | 0.35248 | -123.1064 | -0.38452 | 0.086975 | 117.1692 | 123.111 | -122.9141 | -0.27466 | 0.073242 | 117.5537 | 122.6395 | 122.9507 | 0.19684 | 123.1979 | 117.1692 | 123.1842 | -0.25635 | -0.27466 | 123.1979 | 117.1692 | -0.25635 | 0.19684 | 123.1842 | -123.4955 | -123.3856
474.2188 | 123.0881 | -122.8226 | 0.29755 | -0.010757 | 0.016451 | 0.0069535 | -0.014558 | -0.0061097 | 0.062143 | 0.072198 | -5.6808 | 0.3479 | -123.1934 | 0.28381 | -122.5845 | -123.0377 | -0.33417 | 0.1236 | 0.32959 | -123.0927 | -0.37079 | 0.050354 | 117.1417 | 123.1064 | -122.8821 | -0.27008 | 0.032044 | 117.5125 | 122.4884 | 122.9462 | 0.23804 | 123.1705 | 117.1417 | 123.1522 | -0.21515 | -0.27008 | 123.1705 | 117.1417 | -0.21515 | 0.23804 | 123.1522 | -123.4909 | -123.3902
475.9688 | 123.1659 | -122.7859 | 0.28381 | 0.0045011 | 0.017519 | 0.012721 | -0.018617 | -0.0078187 | 0.066415 | 0.070703 | -5.7266 | 0.34332 | -123.1522 | 0.27924 | -122.5845 | -123.0377 | -0.32044 | 0.07782 | 0.32044 | -123.111 | -0.36621 | 0.05951 | 117.0593 | 123.0652 | -122.8683 | -0.32501 | 0.036622 | 117.4255 | 122.4655 | 122.8638 | 0.20142 | 123.1293 | 117.0593 | 123.1064 | -0.25177 | -0.32501 | 123.1293 | 117.0593 | -0.25177 | 0.20142 | 123.1064 | -123.436 | -123.3948
477.6562 | 123.111 | -122.8455 | 0.31128 | -0.0031279 | 0.017306 | 0.0075943 | -0.012636 | -0.0061097 | 0.063425 | 0.069848 | -5.6717 | 0.37537 | -123.2162 | 0.27466 | -122.6028 | -123.0698 | -0.1831 | 0.12817 | 0.35706 | -123.1155 | -0.37079 | 0.064087 | 117.1738 | 123.1201 | -122.9141 | -0.27008 | 0.045777 | 117.5446 | 122.6624 | 122.9736 | 0.24262 | 123.2208 | 117.1738 | 123.2025 | -0.2243 | -0.27008 | 123.2208 | 117.1738 | -0.2243 | 0.24262 | 123.2025 | -123.5275 | -123.4268
479.4062 | 123.1705 | -122.8088 | 0.27466 | -0.0031279 | 0.015383 | 0.0039627 | -0.018617 | -0.0069641 | 0.065347 | 0.06878 | -5.6763 | 0.34332 | -123.143 | 0.34332 | -122.525 | -122.9874 | -0.30212 | 0.17395 | 0.33875 | -123.1064 | -0.33417 | 0.068665 | 117.1326 | 123.1522 | -122.7997 | -0.29755 | 0.064087 | 117.4667 | 122.5067 | 122.9828 | 0.28381 | 123.1522 | 117.1326 | 123.1476 | -0.17853 | -0.29755 | 123.1522 | 117.1326 | -0.17853 | 0.28381 | 123.1476 | -123.4177 | -123.381
481.1562 | 123.1934 | -122.8043 | 0.2655 | 0.0045011 | 0.017306 | 0.010158 | -0.020113 | -0.0078187 | 0.064279 | 0.070489 | -5.6671 | 0.34332 | -123.1705 | 0.30212 | -122.5571 | -123.0423 | -0.21515 | 0.13275 | 0.35706 | -123.1018 | -0.36621 | 0.07782 | 117.1371 | 123.1064 | -122.8226 | -0.29755 | 0.091553 | 117.5034 | 122.5891 | 122.937 | 0.24719 | 123.1476 | 117.1371 | 123.1613 | -0.23804 | -0.29755 | 123.1476 | 117.1371 | -0.23804 | 0.24719 | 123.1613 | -123.436 | -123.3673
482.9062 | 123.1338 | -122.7859 | 0.27924 | 0.012131 | 0.017519 | 0.0097305 | -0.019899 | -0.0082459 | 0.065347 | 0.068994 | -5.69 | 0.35706 | -123.1613 | 0.28381 | -122.5845 | -123.0286 | -0.33875 | 0.07782 | 0.31586 | -123.1064 | -0.37537 | 0.07782 | 117.0959 | 123.0698 | -122.8638 | -0.32043 | 0.036621 | 117.4713 | 122.4472 | 122.8638 | 0.20142 | 123.143 | 117.0959 | 123.1018 | -0.24261 | -0.32043 | 123.143 | 117.0959 | -0.24261 | 0.20142 | 123.1018 | -123.4406 | -123.3856
484.5781 | 123.1934 | -122.7814 | 0.27924 | 0.0045011 | 0.017519 | 0.0082351 | -0.01819 | -0.0099549 | 0.064066 | 0.071557 | -5.6854 | 0.33417 | -123.1293 | 0.37079 | -122.5204 | -122.9828 | -0.33875 | 0.18768 | 0.33875 | -123.0698 | -0.3479 | 0.054931 | 117.0959 | 123.1522 | -122.7997 | -0.28839 | 0.059509 | 117.4438 | 122.4426 | 122.9691 | 0.26093 | 123.1155 | 117.0959 | 123.1201 | -0.20142 | -0.28839 | 123.1155 | 117.0959 | -0.20142 | 0.26093 | 123.1201 | -123.4085 | -123.349
486.3125 | 123.0743 | -122.8226 | 0.27924 | -0.0031279 | 0.016878 | 0.0099441 | -0.014558 | -0.0095277 | 0.067483 | 0.070489 | -5.6717 | 0.33417 | -123.143 | 0.32959 | -122.5433 | -122.9736 | -0.39368 | 0.1236 | 0.31586 | -123.0881 | -0.32043 | 0.054931 | 117.1509 | 123.1522 | -122.8226 | -0.2655 | 0.036621 | 117.4713 | 122.4289 | 122.9462 | 0.27924 | 123.1567 | 117.1509 | 123.1384 | -0.15106 | -0.2655 | 123.1567 | 117.1509 | -0.15106 | 0.27924 | 123.1384 | -123.4222 | -123.3673
488.0625 | 123.1659 | -122.7722 | 0.28381 | -0.0031279 | 0.016665 | 0.010799 | -0.018831 | -0.0080323 | 0.064706 | 0.070062 | -5.6992 | 0.35248 | -123.143 | 0.3479 | -122.525 | -122.9828 | -0.35248 | 0.15106 | 0.32959 | -123.0927 | -0.37079 | 0.068665 | 117.0731 | 123.1201 | -122.8088 | -0.32043 | 0.045777 | 117.4438 | 122.4197 | 122.9233 | 0.24719 | 123.1247 | 117.0731 | 123.1018 | -0.21057 | -0.32043 | 123.1247 | 117.0731 | -0.21057 | 0.24719 | 123.1018 | -123.4268 | -123.3765
489.7344 | 123.2162 | -122.8226 | 0.27008 | -0.0031279 | 0.019228 | 0.0093033 | -0.012636 | -0.010382 | 0.06257 | 0.068994 | -5.7587 | 0.37994 | -123.1979 | 0.2243 | -122.612 | -123.0972 | -0.11444 | 0.10071 | 0.37079 | -123.1018 | -0.37537 | 0.10986 | 117.0639 | 123.0469 | -122.8821 | -0.27924 | 0.10071 | 117.4393 | 122.7081 | 122.9233 | 0.21057 | 123.2025 | 117.0639 | 123.1934 | -0.27466 | -0.27924 | 123.2025 | 117.0639 | -0.27466 | 0.21057 | 123.1934 | -123.468 | -123.3719
491.4688 | 123.1979 | -122.7997 | 0.24261 | -0.0031279 | 0.016665 | 0.0065263 | -0.019258 | -0.0082459 | 0.064706 | 0.071985 | -5.7587 | 0.33417 | -123.1842 | 0.25177 | -122.5891 | -123.0423 | -0.30212 | 0.073242 | 0.33417 | -123.1018 | -0.38452 | 0.091552 | 117.041 | 123.0515 | -122.8317 | -0.30212 | 0.091552 | 117.4255 | 122.4976 | 122.8729 | 0.21057 | 123.1338 | 117.041 | 123.1338 | -0.24261 | -0.30212 | 123.1338 | 117.041 | -0.24261 | 0.21057 | 123.1338 | -123.4268 | -123.3444
493.2344 | 123.0606 | -122.85 | 0.31128 | 0.012131 | 0.016451 | 0.01443 | -0.013277 | -0.0058961 | 0.063852 | 0.070489 | -5.6671 | 0.32044 | -123.143 | 0.31128 | -122.5388 | -123.0011 | -0.40283 | 0.1236 | 0.3067 | -123.111 | -0.29297 | 0.009156 | 117.1829 | 123.1613 | -122.85 | -0.26093 | -0.004577 | 117.4759 | 122.4472 | 122.9736 | 0.31128 | 123.1705 | 117.1829 | 123.1567 | -0.15106 | -0.26093 | 123.1705 | 117.1829 | -0.15106 | 0.31128 | 123.1567 | -123.4543 | -123.4222
494.9844 | 123.0698 | -122.8317 | 0.27466 | -0.0031279 | 0.015383 | 0.0099441 | -0.016267 | -0.0067505 | 0.063638 | 0.065789 | -5.7037 | 0.31128 | -123.1476 | 0.3067 | -122.5616 | -123.0103 | -0.3891 | 0.1236 | 0.29297 | -123.111 | -0.31586 | 0.036621 | 117.128 | 123.1384 | -122.8363 | -0.27924 | 0.018311 | 117.4438 | 122.4426 | 122.9553 | 0.27008 | 123.143 | 117.128 | 123.1247 | -0.17853 | -0.27924 | 123.143 | 117.128 | -0.17853 | 0.27008 | 123.1247 | -123.4222 | -123.3856
496.6562 | 123.0606 | -122.8638 | 0.27924 | -0.0031279 | 0.016665 | 0.0071671 | -0.013918 | -0.0080323 | 0.063425 | 0.071344 | -5.69 | 0.28839 | -123.1659 | 0.30212 | -122.5616 | -123.0194 | -0.38452 | 0.1236 | 0.3067 | -123.0972 | -0.30212 | 0.009155 | 117.1738 | 123.1659 | -122.8409 | -0.23346 | 0.027466 | 117.4759 | 122.4792 | 122.9874 | 0.30212 | 123.1522 | 117.1738 | 123.1705 | -0.15564 | -0.23346 | 123.1522 | 117.1738 | -0.15564 | 0.30212 | 123.1705 | -123.4451 | -123.3765
498.4062 | 123.1979 | -122.8271 | 0.24719 | 0.0045011 | 0.017519 | 0.0078079 | -0.014558 | -0.0080323 | 0.062784 | 0.070489 | -5.7953 | 0.35706 | -123.262 | 0.17853 | -122.6761 | -123.143 | -0.11902 | 0.073242 | 0.35248 | -123.1247 | -0.43488 | 0.10986 | 117.0319 | 123.0057 | -122.9233 | -0.29755 | 0.10529 | 117.4667 | 122.7081 | 122.9004 | 0.15106 | 123.1842 | 117.0319 | 123.1796 | -0.31586 | -0.29755 | 123.1842 | 117.0319 | -0.31586 | 0.15106 | 123.1796 | -123.5092 | -123.3719
500.1562 | 123.0743 | -122.8546 | 0.27924 | 0.012131 | 0.019442 | 0.010585 | -0.012422 | -0.0071777 | 0.061288 | 0.068567 | -5.7404 | 0.34332 | -123.2071 | 0.21515 | -122.644 | -123.1384 | -0.16022 | 0.064087 | 0.33417 | -123.1018 | -0.35248 | 0.064087 | 117.1143 | 123.0698 | -122.9233 | -0.24719 | 0.054931 | 117.4667 | 122.6944 | 122.9187 | 0.21057 | 123.1979 | 117.1143 | 123.1888 | -0.28381 | -0.24719 | 123.1979 | 117.1143 | -0.28381 | 0.21057 | 123.1888 | -123.4863 | -123.381
501.8281 | 123.1201 | -122.8363 | 0.27924 | 0.0045011 | 0.02051 | 0.010585 | -0.015413 | -0.0044007 | 0.063852 | 0.069421 | -5.7907 | 0.36163 | -123.2117 | 0.17853 | -122.6761 | -123.1567 | -0.14648 | 0.013733 | 0.32959 | -123.1247 | -0.37537 | 0.082397 | 117.0456 | 123.0148 | -122.9553 | -0.28839 | 0.050354 | 117.421 | 122.6898 | 122.85 | 0.16022 | 123.1979 | 117.0456 | 123.1659 | -0.32043 | -0.28839 | 123.1979 | 117.0456 | -0.32043 | 0.16022 | 123.1659 | -123.4909 | -123.4039
503.5781 | 123.1155 | -122.8317 | 0.28381 | -0.0031279 | 0.018801 | 0.010371 | -0.013704 | -0.0050415 | 0.062357 | 0.069421 | -5.7587 | 0.34332 | -123.2162 | 0.1831 | -122.6578 | -123.1476 | -0.13733 | 0.027466 | 0.34332 | -123.1338 | -0.38452 | 0.05951 | 117.0731 | 123.0148 | -122.9416 | -0.30212 | 0.05951 | 117.4576 | 122.6944 | 122.8592 | 0.17395 | 123.175 | 117.0731 | 123.175 | -0.31586 | -0.30212 | 123.175 | 117.0731 | -0.31586 | 0.17395 | 123.175 | -123.5001 | -123.4177
505.3281 | 123.0743 | -122.8592 | 0.28381 | -0.0031279 | 0.016451 | 0.012935 | -0.016908 | -0.0037597 | 0.063425 | 0.070276 | -5.7083 | 0.32044 | -123.1705 | 0.2655 | -122.5708 | -122.9965 | -0.36621 | 0.1236 | 0.3067 | -123.0789 | -0.31128 | 0.036622 | 117.1509 | 123.1247 | -122.8546 | -0.21973 | 0.022889 | 117.4622 | 122.493 | 122.9828 | 0.28839 | 123.1796 | 117.1509 | 123.1659 | -0.13733 | -0.21973 | 123.1796 | 117.1509 | -0.13733 | 0.28839 | 123.1659 | -123.4543 | -123.3627
507.0625 | 123.1567 | -122.818 | 0.2243 | 0.0045011 | 0.017306 | 0.0099441 | -0.020113 | -0.0076049 | 0.066202 | 0.070916 | -5.7404 | 0.29297 | -123.1476 | 0.28839 | -122.5479 | -122.9919 | -0.34332 | 0.16479 | 0.30212 | -123.1293 | -0.32959 | 0.068665 | 117.0776 | 123.1064 | -122.7722 | -0.31128 | 0.07782 | 117.4072 | 122.4747 | 122.9828 | 0.27008 | 123.111 | 117.0776 | 123.1201 | -0.17395 | -0.31128 | 123.111 | 117.0776 | -0.17395 | 0.27008 | 123.1201 | -123.3719 | -123.3536
508.75 | 123.1201 | -122.8363 | 0.25635 | 0.0045011 | 0.020724 | 0.010585 | -0.013704 | -0.0056823 | 0.062997 | 0.071557 | -5.7907 | 0.32959 | -123.2162 | 0.14648 | -122.6852 | -123.1522 | -0.15106 | 0.004578 | 0.33875 | -123.1201 | -0.37994 | 0.073242 | 117.0456 | 122.9828 | -122.9416 | -0.28381 | 0.082397 | 117.4255 | 122.6852 | 122.8409 | 0.15106 | 123.1659 | 117.0456 | 123.175 | -0.31586 | -0.28381 | 123.1659 | 117.0456 | -0.31586 | 0.15106 | 123.175 | -123.4726 | -123.3765
510.5 | 123.143 | -122.8592 | 0.24261 | 0.0045011 | 0.016238 | 0.0065263 | -0.01819 | -0.0069641 | 0.063852 | 0.069207 | -5.7358 | 0.28381 | -123.1567 | 0.28839 | -122.5571 | -123.024 | -0.3067 | 0.17395 | 0.30212 | -123.1018 | -0.29755 | 0.041198 | 117.1234 | 123.1476 | -122.7997 | -0.24262 | 0.059509 | 117.421 | 122.5525 | 123.0331 | 0.30212 | 123.143 | 117.1234 | 123.1613 | -0.1648 | -0.24262 | 123.143 | 117.1234 | -0.1648 | 0.30212 | 123.1613 | -123.3994 | -123.3444
512.2344 | 123.1796 | -122.8226 | 0.21057 | -0.0031279 | 0.017733 | 0.0099441 | -0.019045 | -0.0080323 | 0.061929 | 0.068994 | -5.7724 | 0.33875 | -123.175 | 0.21057 | -122.6349 | -123.111 | -0.16022 | 0.09613 | 0.32959 | -123.1476 | -0.35248 | 0.12817 | 117.0502 | 123.0331 | -122.8455 | -0.32501 | 0.11902 | 117.4026 | 122.6624 | 122.9187 | 0.18768 | 123.1613 | 117.0502 | 123.1522 | -0.28839 | -0.32501 | 123.1613 | 117.0502 | -0.28839 | 0.18768 | 123.1522 | -123.3856 | -123.3582
513.9844 | 123.0515 | -122.85 | 0.2655 | -0.0031279 | 0.01816 | 0.0099441 | -0.015627 | -0.0058961 | 0.062997 | 0.07113 | -5.7037 | 0.31586 | -123.1705 | 0.29297 | -122.5662 | -123.0011 | -0.3891 | 0.13275 | 0.29755 | -123.1201 | -0.32043 | 0.050354 | 117.1463 | 123.143 | -122.8317 | -0.27008 | 0.032043 | 117.4667 | 122.4609 | 122.9828 | 0.28381 | 123.1659 | 117.1463 | 123.1476 | -0.15106 | -0.27008 | 123.1659 | 117.1463 | -0.15106 | 0.28381 | 123.1476 | -123.436 | -123.3856
515.6719 | 123.1064 | -122.8226 | 0.25177 | -0.010757 | 0.018374 | 0.012935 | -0.016481 | -0.0067505 | 0.064706 | 0.071985 | -5.7632 | 0.28839 | -123.1613 | 0.2655 | -122.6166 | -123.0469 | -0.37079 | 0.086975 | 0.30212 | -123.1155 | -0.33875 | 0.036621 | 117.0593 | 123.0881 | -122.8683 | -0.29297 | 0.050354 | 117.3981 | 122.4518 | 122.9095 | 0.20599 | 123.111 | 117.0593 | 123.1247 | -0.2243 | -0.29297 | 123.111 | 117.0593 | -0.2243 | 0.20599 | 123.1247 | -123.4131 | -123.3673
517.4062 | 123.0515 | -122.85 | 0.25177 | 0.0045011 | 0.016451 | 0.0086625 | -0.014986 | -0.0050415 | 0.065347 | 0.070703 | -5.7404 | 0.31128 | -123.1934 | 0.27008 | -122.5525 | -123.0148 | -0.37537 | 0.13733 | 0.29297 | -123.0652 | -0.34332 | 0.059509 | 117.1097 | 123.1201 | -122.8043 | -0.21515 | 0.041199 | 117.453 | 122.4747 | 122.9874 | 0.29755 | 123.1613 | 117.1097 | 123.143 | -0.16479 | -0.21515 | 123.1613 | 117.1097 | -0.16479 | 0.29755 | 123.143 | -123.4451 | -123.317
519.1406 | 123.0743 | -122.8409 | 0.25177 | -0.0031279 | 0.013888 | 0.010585 | -0.017549 | -0.0084595 | 0.064066 | 0.072198 | -5.7541 | 0.29297 | -123.1613 | 0.27008 | -122.5754 | -123.0148 | -0.37994 | 0.12817 | 0.29755 | -123.0789 | -0.32044 | 0.041199 | 117.0868 | 123.111 | -122.8271 | -0.23804 | 0.045776 | 117.4072 | 122.4609 | 122.9691 | 0.2655 | 123.1338 | 117.0868 | 123.1384 | -0.17395 | -0.23804 | 123.1338 | 117.0868 | -0.17395 | 0.2655 | 123.1384 | -123.4131 | -123.3307
520.8125 | 123.0469 | -122.8409 | 0.25177 | 0.012131 | 0.015597 | 0.013789 | -0.016695 | -0.0067505 | 0.063638 | 0.07113 | -5.7358 | 0.28839 | -123.1613 | 0.28381 | -122.5479 | -123.0057 | -0.37994 | 0.11902 | 0.29297 | -123.0789 | -0.32044 | 0.036621 | 117.1051 | 123.1247 | -122.7997 | -0.23804 | 0.041199 | 117.4255 | 122.4609 | 122.9599 | 0.29297 | 123.1293 | 117.1051 | 123.1338 | -0.16479 | -0.23804 | 123.1293 | 117.1051 | -0.16479 | 0.29297 | 123.1338 | -123.4131 | -123.3307
522.5625 | 123.1705 | -122.8271 | 0.21057 | -0.0031279 | 0.020296 | 0.010371 | -0.01349 | -0.0065369 | 0.066202 | 0.071771 | -5.8411 | 0.3479 | -123.2208 | 0.18768 | -122.644 | -123.143 | -0.11902 | 0.07782 | 0.35248 | -123.143 | -0.39368 | 0.13733 | 116.9861 | 123.0148 | -122.8546 | -0.31586 | 0.14191 | 117.3798 | 122.7081 | 122.905 | 0.1831 | 123.175 | 116.9861 | 123.1796 | -0.31586 | -0.31586 | 123.175 | 116.9861 | -0.31586 | 0.1831 | 123.1796 | -123.4314 | -123.3536
524.3125 | 123.0652 | -122.8638 | 0.25635 | 0.012131 | 0.01816 | 0.0065263 | -0.013918 | -0.0073913 | 0.062997 | 0.070062 | -5.7724 | 0.32044 | -123.2162 | 0.23346 | -122.6074 | -123.0927 | -0.1831 | 0.13733 | 0.31128 | -123.111 | -0.35248 | 0.064087 | 117.0914 | 123.0972 | -122.8638 | -0.24719 | 0.054931 | 117.4438 | 122.6807 | 123.0011 | 0.25635 | 123.1842 | 117.0914 | 123.175 | -0.22888 | -0.24719 | 123.1842 | 117.0914 | -0.22888 | 0.25635 | 123.175 | -123.4726 | -123.3673
526 | 123.0652 | -122.8592 | 0.24719 | 0.0045011 | 0.01816 | 0.0090897 | -0.015413 | -0.0052551 | 0.063852 | 0.072839 | -5.8319 | 0.34332 | -123.2162 | 0.1831 | -122.644 | -123.0972 | -0.27924 | 0.054932 | 0.3067 | -123.1247 | -0.35706 | 0.096131 | 117.0273 | 123.0423 | -122.8912 | -0.2655 | 0.05951 | 117.3843 | 122.58 | 122.9141 | 0.21515 | 123.2025 | 117.0273 | 123.1659 | -0.23804 | -0.2655 | 123.2025 | 117.0273 | -0.23804 | 0.21515 | 123.1659 | -123.4634 | -123.3719
527.75 | 123.1934 | -122.8134 | 0.2243 | -0.010757 | 0.02051 | 0.0084489 | -0.016908 | -0.0073913 | 0.064279 | 0.071985 | -5.8594 | 0.33417 | -123.1934 | 0.16479 | -122.6715 | -123.1522 | -0.10071 | 0.068665 | 0.33417 | -123.1476 | -0.37994 | 0.10986 | 116.954 | 122.9782 | -122.8958 | -0.33417 | 0.10986 | 117.334 | 122.7127 | 122.8821 | 0.14191 | 123.1476 | 116.954 | 123.1476 | -0.33875 | -0.33417 | 123.1476 | 116.954 | -0.33875 | 0.14191 | 123.1476 | -123.4177 | -123.3719
529.4844 | 123.1842 | -122.8088 | 0.2243 | 0.0045011 | 0.016238 | 0.0071671 | -0.017976 | -0.0067505 | 0.066843 | 0.069421 | -5.8273 | 0.30212 | -123.1705 | 0.20599 | -122.612 | -123.1064 | -0.16937 | 0.09613 | 0.32501 | -123.1613 | -0.36163 | 0.07782 | 116.9815 | 123.0148 | -122.8363 | -0.35248 | 0.10071 | 117.3431 | 122.6395 | 122.905 | 0.19684 | 123.111 | 116.9815 | 123.1338 | -0.29755 | -0.35248 | 123.111 | 116.9815 | -0.29755 | 0.19684 | 123.1338 | -123.3948 | -123.3856
531.2188 | 123.1659 | -122.8134 | 0.22888 | -0.0031279 | 0.02051 | 0.014217 | -0.016481 | -0.0080323 | 0.064066 | 0.069635 | -5.8594 | 0.33417 | -123.2529 | 0.17853 | -122.6395 | -123.1155 | -0.1236 | 0.1236 | 0.31586 | -123.1567 | -0.43945 | 0.10528 | 116.954 | 122.9919 | -122.8683 | -0.34332 | 0.086975 | 117.3935 | 122.6898 | 122.937 | 0.17395 | 123.1476 | 116.954 | 123.1293 | -0.30212 | -0.34332 | 123.1476 | 116.954 | -0.30212 | 0.17395 | 123.1293 | -123.4818 | -123.3856
532.9844 | 123.1476 | -122.8134 | 0.22888 | -0.0031279 | 0.018801 | 0.010799 | -0.015627 | -0.0073913 | 0.064279 | 0.070703 | -5.8456 | 0.33875 | -123.23 | 0.20599 | -122.6212 | -123.1064 | -0.12817 | 0.1236 | 0.31586 | -123.1247 | -0.41656 | 0.10986 | 116.9678 | 123.0194 | -122.85 | -0.31128 | 0.086975 | 117.3843 | 122.6852 | 122.937 | 0.19226 | 123.1522 | 116.9678 | 123.1293 | -0.29297 | -0.31128 | 123.1522 | 116.9678 | -0.29297 | 0.19226 | 123.1293 | -123.4589 | -123.3536
534.7188 | 123.2208 | -122.8134 | 0.2243 | 0.0045011 | 0.016665 | 0.011012 | -0.016267 | -0.0054687 | 0.06257 | 0.07113 | -5.8868 | 0.33875 | -123.2346 | 0.14648 | -122.6578 | -123.1522 | -0.11444 | 0.073242 | 0.33875 | -123.1384 | -0.42114 | 0.11444 | 116.9266 | 122.9599 | -122.8821 | -0.32501 | 0.11444 | 117.3477 | 122.699 | 122.8867 | 0.15564 | 123.1522 | 116.9266 | 123.1522 | -0.33875 | -0.32501 | 123.1522 | 116.9266 | -0.33875 | 0.15564 | 123.1522 | -123.4589 | -123.3627
536.3906 | 123.0331 | -122.8592 | 0.2243 | 0.0045011 | 0.017947 | 0.0088761 | -0.018831 | -0.0058961 | 0.06257 | 0.070489 | -5.7816 | 0.27008 | -123.23 | 0.24719 | -122.5937 | -123.0331 | -0.38452 | 0.1236 | 0.26093 | -123.1155 | -0.37079 | 0.045777 | 117.0776 | 123.1064 | -122.818 | -0.25635 | 0.036621 | 117.4484 | 122.4747 | 122.9828 | 0.2655 | 123.1293 | 117.0776 | 123.1201 | -0.17395 | -0.25635 | 123.1293 | 117.0776 | -0.17395 | 0.2655 | 123.1201 | -123.4543 | -123.3398
538.1406 | 123.0515 | -122.8775 | 0.24261 | 0.0045011 | 0.018801 | 0.011226 | -0.011995 | -0.0069641 | 0.061929 | 0.07113 | -5.8136 | 0.29297 | -123.2208 | 0.20142 | -122.6074 | -123.0881 | -0.1831 | 0.13733 | 0.31586 | -123.1384 | -0.34332 | 0.050354 | 117.0639 | 123.0789 | -122.85 | -0.26093 | 0.073242 | 117.4072 | 122.6944 | 123.0148 | 0.27008 | 123.1705 | 117.0639 | 123.1934 | -0.21057 | -0.26093 | 123.1705 | 117.0639 | -0.21057 | 0.27008 | 123.1934 | -123.4634 | -123.381
539.8125 | 123.0469 | -122.8546 | 0.2243 | -0.010757 | 0.017519 | 0.014644 | -0.016481 | -0.0054687 | 0.067911 | 0.069635 | -5.8365 | 0.27924 | -123.2025 | 0.21057 | -122.612 | -123.0606 | -0.32044 | 0.10529 | 0.28381 | -123.1064 | -0.3479 | 0.054932 | 117.0181 | 123.0652 | -122.8363 | -0.25177 | 0.059509 | 117.366 | 122.5342 | 122.9599 | 0.24261 | 123.1338 | 117.0181 | 123.1384 | -0.20599 | -0.25177 | 123.1338 | 117.0181 | -0.20599 | 0.24261 | 123.1384 | -123.4268 | -123.3307
541.5469 | 123.0743 | -122.8546 | 0.2243 | 0.012131 | 0.01581 | 0.010158 | -0.015413 | -0.0039735 | 0.061929 | 0.070703 | -5.8182 | 0.31586 | -123.23 | 0.15106 | -122.6807 | -123.1567 | -0.13733 | 0.050354 | 0.31586 | -123.1384 | -0.37537 | 0.091553 | 117.0364 | 123.0057 | -122.905 | -0.28381 | 0.091553 | 117.4118 | 122.7173 | 122.905 | 0.17395 | 123.1705 | 117.0364 | 123.1705 | -0.30212 | -0.28381 | 123.1705 | 117.0364 | -0.30212 | 0.17395 | 123.1705 | -123.4543 | -123.3627
543.3281 | 123.0972 | -122.8546 | 0.21973 | 0.0045011 | 0.017306 | 0.014217 | -0.018831 | -0.0054687 | 0.064493 | 0.070916 | -5.8823 | 0.32044 | -123.2346 | 0.13275 | -122.6761 | -123.1476 | -0.21515 | 0.022888 | 0.31586 | -123.1018 | -0.37994 | 0.10071 | 116.9724 | 122.9874 | -122.8958 | -0.24719 | 0.09613 | 117.3523 | 122.6395 | 122.8775 | 0.17853 | 123.175 | 116.9724 | 123.1705 | -0.29297 | -0.24719 | 123.175 | 116.9724 | -0.29297 | 0.17853 | 123.1705 | -123.4543 | -123.3215
545.0625 | 123.0881 | -122.8363 | 0.22888 | -0.018387 | 0.017947 | 0.0043899 | -0.021394 | -0.0078187 | 0.066843 | 0.069421 | -5.864 | 0.29755 | -123.1613 | 0.21515 | -122.5983 | -123.0469 | -0.34332 | 0.086975 | 0.28381 | -123.1018 | -0.32501 | 0.068664 | 116.9724 | 123.0515 | -122.8271 | -0.2655 | 0.054931 | 117.2974 | 122.493 | 122.9233 | 0.23804 | 123.1338 | 116.9724 | 123.1201 | -0.21057 | -0.2655 | 123.1338 | 116.9724 | -0.21057 | 0.23804 | 123.1201 | -123.3902 | -123.3307
546.7969 | 123.1064 | -122.8363 | 0.25177 | 0.0045011 | 0.017947 | 0.0097305 | -0.013918 | -0.0067505 | 0.062997 | 0.071557 | -5.8914 | 0.31586 | -123.2254 | 0.14648 | -122.6807 | -123.1293 | -0.16022 | 0.004578 | 0.32501 | -123.1293 | -0.3891 | 0.064087 | 116.9449 | 122.9828 | -122.9324 | -0.29297 | 0.073242 | 117.334 | 122.6761 | 122.8409 | 0.15564 | 123.1522 | 116.9449 | 123.1613 | -0.29297 | -0.29297 | 123.1522 | 116.9449 | -0.29297 | 0.15564 | 123.1613 | -123.4772 | -123.381
548.4844 | 123.1888 | -122.7859 | 0.23346 | 0.0045011 | 0.018374 | 0.0088761 | -0.01584 | -0.0073913 | 0.06257 | 0.070276 | -5.9143 | 0.33875 | -123.2025 | 0.14191 | -122.644 | -123.1613 | -0.091553 | 0.059509 | 0.33417 | -123.1522 | -0.41657 | 0.10529 | 116.8716 | 122.9279 | -122.8775 | -0.36621 | 0.10071 | 117.2882 | 122.6944 | 122.8455 | 0.14191 | 123.1247 | 116.8716 | 123.1201 | -0.37537 | -0.36621 | 123.1247 | 116.8716 | -0.37537 | 0.14191 | 123.1201 | -123.436 | -123.3856
550.1562 | 123.056 | -122.8546 | 0.24261 | 0.0045011 | 0.02051 | 0.012294 | -0.013063 | -0.0065369 | 0.060861 | 0.071985 | -5.8456 | 0.3067 | -123.23 | 0.15106 | -122.6852 | -123.1384 | -0.16937 | 0.050354 | 0.31586 | -123.1522 | -0.37537 | 0.064087 | 117.009 | 123.0057 | -122.9279 | -0.29755 | 0.073242 | 117.3843 | 122.6852 | 122.905 | 0.16937 | 123.1613 | 117.009 | 123.1705 | -0.28381 | -0.29755 | 123.1613 | 117.009 | -0.28381 | 0.16937 | 123.1705 | -123.4726 | -123.3948
551.8906 | 123.1476 | -122.8043 | 0.21057 | -0.0031279 | 0.014742 | 0.010371 | -0.021181 | -0.0058961 | 0.065347 | 0.069848 | -5.8823 | 0.28381 | -123.1659 | 0.24261 | -122.5616 | -123.0148 | -0.33875 | 0.14191 | 0.29297 | -123.0881 | -0.36163 | 0.073242 | 116.922 | 123.0469 | -122.7722 | -0.28381 | 0.082398 | 117.2836 | 122.4655 | 122.9462 | 0.24261 | 123.0881 | 116.922 | 123.0972 | -0.21057 | -0.28381 | 123.0881 | 116.922 | -0.21057 | 0.24261 | 123.0972 | -123.3765 | -123.2986
553.5781 | 123.0331 | -122.8546 | 0.24261 | -0.0031279 | 0.01581 | 0.012294 | -0.016695 | -0.0071777 | 0.064279 | 0.071344 | -5.8411 | 0.27008 | -123.1659 | 0.25177 | -122.5571 | -123.0148 | -0.38452 | 0.13733 | 0.2655 | -123.0698 | -0.31128 | 0.027466 | 117.0135 | 123.1064 | -122.7997 | -0.21515 | 0.022888 | 117.3248 | 122.4701 | 122.9919 | 0.29755 | 123.1247 | 117.0135 | 123.1201 | -0.16022 | -0.21515 | 123.1247 | 117.0135 | -0.16022 | 0.29755 | 123.1201 | -123.4085 | -123.3124
555.3281 | 123.1888 | -122.7859 | 0.22888 | -0.0031279 | 0.016878 | 0.010799 | -0.015627 | -0.0093139 | 0.064279 | 0.070062 | -5.9418 | 0.33417 | -123.2117 | 0.14648 | -122.6532 | -123.1476 | -0.10071 | 0.059509 | 0.33417 | -123.1613 | -0.42572 | 0.10528 | 116.8442 | 122.9324 | -122.8821 | -0.37537 | 0.10528 | 117.2699 | 122.6852 | 122.8455 | 0.13275 | 123.1201 | 116.8442 | 123.1201 | -0.36163 | -0.37537 | 123.1201 | 116.8442 | -0.36163 | 0.13275 | 123.1201 | -123.4406 | -123.3902
557.0781 | 123.143 | -122.8226 | 0.23804 | 0.0045011 | 0.016451 | 0.0099441 | -0.01584 | -0.0076049 | 0.063425 | 0.070489 | -5.9189 | 0.32044 | -123.2117 | 0.17395 | -122.612 | -123.1064 | -0.10986 | 0.091553 | 0.31586 | -123.1247 | -0.3891 | 0.082398 | 116.9037 | 122.9965 | -122.85 | -0.30212 | 0.07782 | 117.2928 | 122.7127 | 122.9141 | 0.21057 | 123.143 | 116.9037 | 123.1384 | -0.28381 | -0.30212 | 123.143 | 116.9037 | -0.28381 | 0.21057 | 123.1384 | -123.4497 | -123.3627
558.7656 | 123.0835 | -122.8088 | 0.25177 | 0.0045011 | 0.018801 | 0.0084489 | -0.014131 | -0.0061097 | 0.06257 | 0.070916 | -5.9143 | 0.32044 | -123.1934 | 0.14191 | -122.6807 | -123.1522 | -0.15564 | 0.022888 | 0.32044 | -123.1018 | -0.38452 | 0.068665 | 116.8945 | 122.9507 | -122.9324 | -0.29297 | 0.068665 | 117.2791 | 122.6532 | 122.8317 | 0.12817 | 123.1293 | 116.8945 | 123.1293 | -0.34332 | -0.29297 | 123.1293 | 116.8945 | -0.34332 | 0.12817 | 123.1293 | -123.4451 | -123.3536
560.5156 | 123.1659 | -122.8043 | 0.21515 | 0.0045011 | 0.017947 | 0.0093033 | -0.019045 | -0.0071777 | 0.063638 | 0.071557 | -5.9143 | 0.29755 | -123.1842 | 0.17853 | -122.6166 | -123.111 | -0.16022 | 0.09613 | 0.29755 | -123.1567 | -0.37994 | 0.082397 | 116.89 | 122.9828 | -122.8317 | -0.35248 | 0.082397 | 117.2699 | 122.644 | 122.9004 | 0.18768 | 123.1018 | 116.89 | 123.1018 | -0.3067 | -0.35248 | 123.1018 | 116.89 | -0.3067 | 0.18768 | 123.1018 | -123.3994 | -123.3719
562.1875 | 123.0469 | -122.8592 | 0.25177 | 0.012131 | 0.019869 | 0.012508 | -0.013063 | -0.0065369 | 0.062784 | 0.06878 | -5.8502 | 0.3067 | -123.2025 | 0.21515 | -122.6028 | -123.0881 | -0.18768 | 0.12817 | 0.31586 | -123.1018 | -0.34332 | 0.054932 | 117.009 | 123.0743 | -122.8546 | -0.24262 | 0.064087 | 117.3523 | 122.6715 | 122.9874 | 0.25635 | 123.1659 | 117.009 | 123.175 | -0.22888 | -0.24262 | 123.1659 | 117.009 | -0.22888 | 0.25635 | 123.175 | -123.4543 | -123.3536
563.9375 | 123.0194 | -122.8409 | 0.22888 | 0.0045011 | 0.017733 | 0.0078079 | -0.017976 | -0.0048279 | 0.062143 | 0.068994 | -5.9097 | 0.29297 | -123.1842 | 0.23346 | -122.5845 | -123.0331 | -0.32501 | 0.10986 | 0.29297 | -123.1247 | -0.34332 | 0.064087 | 116.9312 | 123.0743 | -122.8134 | -0.28381 | 0.064087 | 117.2745 | 122.5159 | 122.9507 | 0.25635 | 123.1338 | 116.9312 | 123.1338 | -0.19226 | -0.28381 | 123.1338 | 116.9312 | -0.19226 | 0.25635 | 123.1338 | -123.4131 | -123.3536
565.625 | 123.0927 | -122.8226 | 0.22888 | 0.012131 | 0.01816 | 0.0069535 | -0.015199 | -0.0054687 | 0.065347 | 0.07113 | -5.9509 | 0.31128 | -123.2254 | 0.1236 | -122.6898 | -123.1522 | -0.16479 | 0.013733 | 0.31128 | -123.1293 | -0.40283 | 0.082397 | 116.8716 | 122.9462 | -122.9187 | -0.3067 | 0.082397 | 117.2745 | 122.6578 | 122.8363 | 0.13275 | 123.1338 | 116.8716 | 123.1338 | -0.32959 | -0.3067 | 123.1338 | 116.8716 | -0.32959 | 0.13275 | 123.1338 | -123.4543 | -123.3582
567.3594 | 123.024 | -122.85 | 0.23804 | -0.0031279 | 0.016024 | 0.011867 | -0.017549 | -0.0056823 | 0.064706 | 0.070276 | -5.8914 | 0.27924 | -123.1934 | 0.21973 | -122.5754 | -123.0194 | -0.34332 | 0.10986 | 0.27466 | -123.1201 | -0.34332 | 0.041199 | 116.9586 | 123.0698 | -122.8134 | -0.27008 | 0.036621 | 117.3019 | 122.5067 | 122.9599 | 0.27466 | 123.1293 | 116.9586 | 123.1247 | -0.16937 | -0.27008 | 123.1293 | 116.9586 | -0.16937 | 0.27466 | 123.1247 | -123.4314 | -123.3582
569.1094 | 123.1659 | -122.7997 | 0.20599 | -0.010757 | 0.019228 | 0.0080215 | -0.020967 | -0.0095277 | 0.064493 | 0.069421 | -5.9509 | 0.29297 | -123.175 | 0.17395 | -122.6166 | -123.0698 | -0.33417 | 0.068665 | 0.27924 | -123.1476 | -0.37537 | 0.086975 | 116.8488 | 122.9736 | -122.8226 | -0.3479 | 0.073242 | 117.2241 | 122.4655 | 122.8683 | 0.18311 | 123.0927 | 116.8488 | 123.0789 | -0.27008 | -0.3479 | 123.0927 | 116.8488 | -0.27008 | 0.18311 | 123.0789 | -123.381 | -123.3536
570.8438 | 123.0423 | -122.8455 | 0.21973 | -0.010757 | 0.017733 | 0.012508 | -0.016908 | -0.0076049 | 0.064493 | 0.071344 | -5.896 | 0.27008 | -123.1659 | 0.24261 | -122.5708 | -123.0194 | -0.3891 | 0.1236 | 0.25635 | -123.0835 | -0.32043 | 0.050354 | 116.9495 | 123.0881 | -122.7905 | -0.23804 | 0.036621 | 117.2699 | 122.4564 | 122.9691 | 0.27466 | 123.1155 | 116.9495 | 123.1018 | -0.17395 | -0.23804 | 123.1155 | 116.9495 | -0.17395 | 0.27466 | 123.1018 | -123.3856 | -123.3032
572.5156 | 123.1705 | -122.8043 | 0.20599 | -0.0031279 | 0.015383 | 0.0082351 | -0.019045 | -0.0088867 | 0.066415 | 0.069207 | -5.9601 | 0.28381 | -123.1934 | 0.19684 | -122.5937 | -123.0698 | -0.30212 | 0.091553 | 0.27466 | -123.111 | -0.3891 | 0.077819 | 116.8442 | 123.0011 | -122.7997 | -0.3067 | 0.068664 | 117.2333 | 122.5021 | 122.8958 | 0.21057 | 123.0881 | 116.8442 | 123.0789 | -0.2655 | -0.3067 | 123.0881 | 116.8442 | -0.2655 | 0.21057 | 123.0789 | -123.3994 | -123.317
574.2656 | 123.0423 | -122.8363 | 0.23804 | -0.010757 | 0.016665 | 0.0095169 | -0.016267 | -0.0078187 | 0.064279 | 0.071771 | -5.8914 | 0.25635 | -123.1796 | 0.25635 | -122.5571 | -123.0103 | -0.37079 | 0.11902 | 0.27466 | -123.0927 | -0.34332 | 0.018311 | 116.9449 | 123.0927 | -122.7951 | -0.25635 | 0.036621 | 117.2882 | 122.4655 | 122.9553 | 0.27924 | 123.0927 | 116.9449 | 123.111 | -0.17395 | -0.25635 | 123.0927 | 116.9449 | -0.17395 | 0.27924 | 123.111 | -123.4177 | -123.3307
576 | 123.1247 | -122.7905 | 0.2243 | 0.0045011 | 0.016878 | 0.0088761 | -0.01819 | -0.0088867 | 0.06257 | 0.070489 | -5.9143 | 0.28381 | -123.1705 | 0.25635 | -122.5708 | -123.0377 | -0.25635 | 0.16022 | 0.28839 | -123.1155 | -0.37994 | 0.059509 | 116.8762 | 123.0469 | -122.7951 | -0.32501 | 0.064087 | 117.2562 | 122.5342 | 122.9507 | 0.21973 | 123.0743 | 116.8762 | 123.0789 | -0.24719 | -0.32501 | 123.0743 | 116.8762 | -0.24719 | 0.21973 | 123.0789 | -123.3948 | -123.3398
577.75 | 123.1064 | -122.8088 | 0.2243 | 0.0045011 | 0.017733 | 0.0088761 | -0.010713 | -0.0065369 | 0.059152 | 0.068353 | -5.9372 | 0.28839 | -123.23 | 0.19684 | -122.6395 | -123.1018 | -0.16479 | 0.11444 | 0.3067 | -123.1201 | -0.42114 | 0.064087 | 116.8716 | 123.0057 | -122.8638 | -0.31128 | 0.082398 | 117.2928 | 122.644 | 122.9233 | 0.16937 | 123.0972 | 116.8716 | 123.1155 | -0.29297 | -0.31128 | 123.0972 | 116.8716 | -0.29297 | 0.16937 | 123.1155 | -123.4543 | -123.3444
579.5 | 123.0469 | -122.8317 | 0.21515 | 0.0045011 | 0.017519 | 0.0086625 | -0.019258 | -0.0080323 | 0.064493 | 0.072412 | -5.9189 | 0.2655 | -123.1842 | 0.23346 | -122.5891 | -123.0377 | -0.37994 | 0.082397 | 0.27466 | -123.1064 | -0.35248 | 0.050354 | 116.9128 | 123.0652 | -122.8043 | -0.27466 | 0.059509 | 117.2653 | 122.4518 | 122.9141 | 0.24262 | 123.0972 | 116.9128 | 123.1064 | -0.20599 | -0.27466 | 123.0972 | 116.9128 | -0.20599 | 0.24262 | 123.1064 | -123.3994 | -123.3215
581.1719 | 123.143 | -122.8134 | 0.20599 | -0.010757 | 0.017519 | 0.0078079 | -0.017122 | -0.0078187 | 0.065347 | 0.071557 | -5.9189 | 0.27466 | -123.175 | 0.21057 | -122.5937 | -123.0652 | -0.20599 | 0.11902 | 0.30212 | -123.1338 | -0.36163 | 0.068664 | 116.8945 | 123.024 | -122.7997 | -0.32043 | 0.09613 | 117.2562 | 122.6074 | 122.9324 | 0.21973 | 123.0881 | 116.8945 | 123.1155 | -0.25177 | -0.32043 | 123.0881 | 116.8945 | -0.25177 | 0.21973 | 123.1155 | -123.381 | -123.3398
582.9062 | 123.0835 | -122.8409 | 0.2243 | 0.012131 | 0.019015 | 0.011653 | -0.013063 | -0.0061097 | 0.060861 | 0.069421 | -5.9326 | 0.27924 | -123.2391 | 0.1831 | -122.6074 | -123.1064 | -0.16022 | 0.10529 | 0.30212 | -123.1293 | -0.39826 | 0.054932 | 116.9083 | 123.024 | -122.8317 | -0.28839 | 0.07782 | 117.3065 | 122.6807 | 122.9462 | 0.23346 | 123.1201 | 116.9083 | 123.143 | -0.2655 | -0.28839 | 123.1201 | 116.9083 | -0.2655 | 0.23346 | 123.143 | -123.4634 | -123.3536
584.5938 | 123.0377 | -122.8455 | 0.23804 | 0.0045011 | 0.01816 | 0.011653 | -0.016267 | -0.0063233 | 0.063425 | 0.068139 | -5.9967 | 0.29755 | -123.2254 | 0.16937 | -122.6395 | -123.0881 | -0.27924 | 0.041199 | 0.28839 | -123.1064 | -0.37994 | 0.059509 | 116.8488 | 123.0148 | -122.8775 | -0.26093 | 0.050354 | 117.2287 | 122.5662 | 122.8867 | 0.20599 | 123.143 | 116.8488 | 123.1339 | -0.24262 | -0.26093 | 123.143 | 116.8488 | -0.24262 | 0.20599 | 123.1339 | -123.4634 | -123.3444
586.3438 | 123.0286 | -122.8409 | 0.21973 | -0.010757 | 0.016665 | 0.0080215 | -0.02054 | -0.0095277 | 0.065988 | 0.069207 | -5.9235 | 0.27466 | -123.1659 | 0.23346 | -122.5662 | -123.0194 | -0.38452 | 0.10071 | 0.26093 | -123.1155 | -0.32501 | 0.054931 | 116.9174 | 123.0743 | -122.7859 | -0.27466 | 0.041198 | 117.2424 | 122.4564 | 122.9416 | 0.27466 | 123.1155 | 116.9174 | 123.1018 | -0.17853 | -0.27466 | 123.1155 | 116.9174 | -0.17853 | 0.27466 | 123.1018 | -123.3856 | -123.3353
588.0938 | 122.9919 | -122.8546 | 0.23804 | 0.0045011 | 0.019228 | 0.014644 | -0.015199 | -0.0067505 | 0.062997 | 0.071771 | -5.896 | 0.27466 | -123.1842 | 0.25177 | -122.5616 | -123.0057 | -0.37079 | 0.11444 | 0.27008 | -123.1018 | -0.32959 | 0.036621 | 116.9586 | 123.1064 | -122.7997 | -0.24719 | 0.032044 | 117.2882 | 122.4838 | 122.9691 | 0.29297 | 123.1293 | 116.9586 | 123.1247 | -0.15106 | -0.24719 | 123.1293 | 116.9586 | -0.15106 | 0.29297 | 123.1247 | -123.4222 | -123.3398
589.7812 | 123.0331 | -122.85 | 0.23346 | -0.0031279 | 0.018801 | 0.0097305 | -0.01285 | -0.0061097 | 0.060861 | 0.071344 | -5.9418 | 0.28381 | -123.2208 | 0.17395 | -122.6486 | -123.1293 | -0.15564 | 0.054932 | 0.31128 | -123.1201 | -0.37079 | 0.050354 | 116.9083 | 123.024 | -122.8821 | -0.27008 | 0.07782 | 117.2791 | 122.6944 | 122.905 | 0.20142 | 123.1338 | 116.9083 | 123.1613 | -0.27923 | -0.27008 | 123.1338 | 116.9083 | -0.27923 | 0.20142 | 123.1613 | -123.4543 | -123.3536
591.5156 | 122.9919 | -122.8363 | 0.23804 | 0.0045011 | 0.017519 | 0.0058853 | -0.017549 | -0.0050415 | 0.064706 | 0.070703 | -5.9189 | 0.25177 | -123.1796 | 0.24719 | -122.5479 | -122.9919 | -0.40283 | 0.1236 | 0.2655 | -123.0789 | -0.34332 | 0.013733 | 116.9174 | 123.0835 | -122.7859 | -0.24261 | 0.027466 | 117.2607 | 122.4335 | 122.9599 | 0.28839 | 123.0881 | 116.9174 | 123.1018 | -0.15564 | -0.24261 | 123.0881 | 116.9174 | -0.15564 | 0.28839 | 123.1018 | -123.4177 | -123.317
593.2031 | 123.1659 | -122.8088 | 0.20599 | -0.0031279 | 0.017947 | 0.010585 | -0.017763 | -0.0086731 | 0.062997 | 0.070916 | -6.0333 | 0.32044 | -123.2162 | 0.15106 | -122.6486 | -123.1384 | -0.11444 | 0.064087 | 0.30212 | -123.1384 | -0.40741 | 0.11444 | 116.7755 | 122.9599 | -122.8546 | -0.32959 | 0.09613 | 117.1829 | 122.6944 | 122.8729 | 0.16022 | 123.1293 | 116.7755 | 123.111 | -0.32959 | -0.32959 | 123.1293 | 116.7755 | -0.32959 | 0.16022 | 123.111 | -123.4222 | -123.3444
594.9531 | 123.0286 | -122.8363 | 0.21515 | 0.0045011 | 0.01816 | 0.0093033 | -0.014131 | -0.0063233 | 0.062143 | 0.071557 | -6.0104 | 0.29755 | -123.2071 | 0.17853 | -122.612 | -123.0743 | -0.28839 | 0.054932 | 0.28839 | -123.0881 | -0.37079 | 0.082397 | 116.8259 | 123.0148 | -122.8271 | -0.25177 | 0.073242 | 117.1967 | 122.5479 | 122.8912 | 0.2243 | 123.1338 | 116.8259 | 123.1247 | -0.23804 | -0.25177 | 123.1338 | 116.8259 | -0.23804 | 0.2243 | 123.1247 | -123.4222 | -123.3032
596.6875 | 123.143 | -122.7951 | 0.1831 | 0.0045011 | 0.017733 | 0.0071671 | -0.018831 | -0.0073913 | 0.062784 | 0.069635 | -6.0471 | 0.28381 | -123.2117 | 0.14648 | -122.6349 | -123.1201 | -0.11902 | 0.064087 | 0.31586 | -123.1384 | -0.41656 | 0.10071 | 116.748 | 122.9416 | -122.818 | -0.34332 | 0.13275 | 117.1646 | 122.6761 | 122.8592 | 0.16022 | 123.0789 | 116.748 | 123.111 | -0.32501 | -0.34332 | 123.0789 | 116.748 | -0.32501 | 0.16022 | 123.111 | -123.3948 | -123.3215
598.4375 | 123.0331 | -122.8409 | 0.24719 | 0.0045011 | 0.017306 | 0.016353 | -0.01349 | -0.0063233 | 0.061075 | 0.072412 | -5.983 | 0.30212 | -123.1888 | 0.16022 | -122.6532 | -123.1155 | -0.15564 | 0.050354 | 0.29755 | -123.111 | -0.3479 | 0.054932 | 116.8579 | 123.0011 | -122.9004 | -0.27008 | 0.050354 | 117.2058 | 122.6852 | 122.8912 | 0.18768 | 123.143 | 116.8579 | 123.1384 | -0.27466 | -0.27008 | 123.143 | 116.8579 | -0.27466 | 0.18768 | 123.1384 | -123.436 | -123.3582
600.125 | 123.0103 | -122.8546 | 0.2243 | 0.0045011 | 0.01816 | 0.0099441 | -0.016695 | -0.0061097 | 0.062997 | 0.069848 | -5.9784 | 0.3067 | -123.2117 | 0.19226 | -122.6074 | -123.0835 | -0.16937 | 0.12817 | 0.28839 | -123.1155 | -0.35706 | 0.082398 | 116.8762 | 123.0469 | -122.8317 | -0.26093 | 0.064087 | 117.2333 | 122.6852 | 122.9828 | 0.24719 | 123.1613 | 116.8762 | 123.143 | -0.22888 | -0.26093 | 123.1613 | 116.8762 | -0.22888 | 0.24719 | 123.143 | -123.436 | -123.3398
601.8594 | 123.1018 | -122.818 | 0.20599 | 0.0045011 | 0.015383 | 0.0084489 | -0.020967 | -0.0073913 | 0.064706 | 0.069207 | -5.9875 | 0.27008 | -123.175 | 0.23346 | -122.5662 | -123.0469 | -0.23804 | 0.15106 | 0.27008 | -123.111 | -0.35706 | 0.064087 | 116.8304 | 123.0515 | -122.7722 | -0.29297 | 0.064087 | 117.1875 | 122.58 | 122.9691 | 0.25177 | 123.0881 | 116.8304 | 123.0881 | -0.22888 | -0.29297 | 123.0881 | 116.8304 | -0.22888 | 0.25177 | 123.0881 | -123.381 | -123.317
603.5938 | 123.0835 | -122.818 | 0.20142 | -0.0031279 | 0.017733 | 0.010371 | -0.019685 | -0.0091003 | 0.065347 | 0.068139 | -5.9875 | 0.24719 | -123.1522 | 0.24719 | -122.5388 | -122.9919 | -0.36163 | 0.1831 | 0.2655 | -123.111 | -0.33417 | 0.045776 | 116.8304 | 123.0652 | -122.7402 | -0.29297 | 0.064087 | 117.1646 | 122.4564 | 123.0011 | 0.27924 | 123.0652 | 116.8304 | 123.0835 | -0.17395 | -0.29297 | 123.0652 | 116.8304 | -0.17395 | 0.27924 | 123.0835 | -123.3536 | -123.3124
605.2812 | 123.0881 | -122.8317 | 0.1831 | -0.010757 | 0.01581 | 0.0099441 | -0.019045 | -0.0071777 | 0.064279 | 0.071771 | -5.9921 | 0.24261 | -123.1705 | 0.24719 | -122.5525 | -123.0194 | -0.33875 | 0.17853 | 0.23804 | -123.1064 | -0.33875 | 0.05951 | 116.8396 | 123.0789 | -122.7356 | -0.27466 | 0.054932 | 117.1783 | 122.493 | 123.0103 | 0.27924 | 123.0743 | 116.8396 | 123.0698 | -0.18768 | -0.27466 | 123.0743 | 116.8396 | -0.18768 | 0.27924 | 123.0698 | -123.3536 | -123.2895
607.0312 | 123.0606 | -122.8409 | 0.19684 | 0.0045011 | 0.016665 | 0.010371 | -0.013277 | -0.0054687 | 0.061502 | 0.069207 | -6.0654 | 0.27466 | -123.2758 | 0.10071 | -122.699 | -123.1659 | -0.17853 | 0.009155 | 0.28839 | -123.1247 | -0.43488 | 0.07782 | 116.7755 | 122.9416 | -122.8958 | -0.28381 | 0.091553 | 117.2104 | 122.6624 | 122.85 | 0.14191 | 123.1155 | 116.7755 | 123.1293 | -0.32501 | -0.28381 | 123.1155 | 116.7755 | -0.32501 | 0.14191 | 123.1293 | -123.4726 | -123.3215
608.7812 | 122.9919 | -122.8683 | 0.21515 | 0.0045011 | 0.018374 | 0.0086625 | -0.017122 | -0.0082459 | 0.063852 | 0.069848 | -5.9601 | 0.22888 | -123.1888 | 0.21057 | -122.5708 | -123.0331 | -0.39825 | 0.11444 | 0.21973 | -123.1338 | -0.32044 | 0.013733 | 116.9083 | 123.0789 | -122.7859 | -0.2655 | 0.004578 | 117.2287 | 122.4701 | 122.9828 | 0.29755 | 123.0972 | 116.9083 | 123.0881 | -0.16479 | -0.2655 | 123.0972 | 116.9083 | -0.16479 | 0.29755 | 123.0881 | -123.4039 | -123.349
610.4688 | 123.0881 | -122.85 | 0.16937 | -0.0031279 | 0.016878 | 0.0084489 | -0.015413 | -0.0069641 | 0.062357 | 0.071771 | -6.0516 | 0.27924 | -123.2483 | 0.15106 | -122.644 | -123.111 | -0.15564 | 0.11444 | 0.26093 | -123.1522 | -0.39825 | 0.10986 | 116.7984 | 123.0011 | -122.8134 | -0.30212 | 0.091552 | 117.1967 | 122.6944 | 122.9645 | 0.20599 | 123.1293 | 116.7984 | 123.111 | -0.26093 | -0.30212 | 123.1293 | 116.7984 | -0.26093 | 0.20599 | 123.111 | -123.4177 | -123.3215
612.2188 | 123.0194 | -122.8775 | 0.18768 | 0.01976 | 0.017733 | 0.016353 | -0.014131 | -0.0044007 | 0.061929 | 0.071557 | -6.0059 | 0.26093 | -123.2712 | 0.10986 | -122.6669 | -123.1384 | -0.16937 | 0.082397 | 0.27924 | -123.143 | -0.39368 | 0.073242 | 116.8716 | 122.9874 | -122.8546 | -0.2655 | 0.091553 | 117.2653 | 122.7081 | 122.9599 | 0.21057 | 123.1384 | 116.8716 | 123.1567 | -0.26093 | -0.2655 | 123.1384 | 116.8716 | -0.26093 | 0.21057 | 123.1567 | -123.4589 | -123.3307
613.9062 | 123.1247 | -122.8043 | 0.17395 | 0.012131 | 0.019015 | 0.011439 | -0.019685 | -0.0069641 | 0.064706 | 0.070062 | -6.0928 | 0.2655 | -123.23 | 0.10529 | -122.6486 | -123.1476 | -0.1236 | 0.045776 | 0.28381 | -123.1705 | -0.42572 | 0.091553 | 116.7114 | 122.9095 | -122.8226 | -0.36621 | 0.10986 | 117.1371 | 122.6807 | 122.85 | 0.15564 | 123.0698 | 116.7114 | 123.0881 | -0.34332 | -0.36621 | 123.0698 | 116.7114 | -0.34332 | 0.15564 | 123.0881 | -123.4039 | -123.3444
615.6406 | 123.1247 | -122.8409 | 0.16022 | 0.0045011 | 0.017306 | 0.0095169 | -0.020754 | -0.0073913 | 0.062357 | 0.069421 | -6.0104 | 0.22888 | -123.1888 | 0.19684 | -122.5845 | -123.0698 | -0.21973 | 0.13275 | 0.22888 | -123.1659 | -0.3479 | 0.068665 | 116.8304 | 123.0377 | -122.7448 | -0.32501 | 0.068665 | 117.1783 | 122.6212 | 122.9736 | 0.25635 | 123.0698 | 116.8304 | 123.0698 | -0.22888 | -0.32501 | 123.0698 | 116.8304 | -0.22888 | 0.25635 | 123.0698 | -123.349 | -123.3261
617.3906 | 123.0606 | -122.8363 | 0.19684 | 0.012131 | 0.019015 | 0.011226 | -0.013277 | -0.0076049 | 0.063852 | 0.071344 | -6.0883 | 0.2655 | -123.2483 | 0.073242 | -122.7036 | -123.175 | -0.13275 | 0 | 0.26093 | -123.1522 | -0.41199 | 0.068665 | 116.748 | 122.9095 | -122.9004 | -0.31586 | 0.064087 | 117.16 | 122.7036 | 122.8363 | 0.13275 | 123.1018 | 116.748 | 123.0972 | -0.33875 | -0.31586 | 123.1018 | 116.748 | -0.33875 | 0.13275 | 123.0972 | -123.4451 | -123.349
619.0781 | 123.0194 | -122.8729 | 0.19226 | -0.0031279 | 0.019228 | 0.0090897 | -0.015199 | -0.0065369 | 0.063638 | 0.069421 | -6.0333 | 0.2655 | -123.2437 | 0.16937 | -122.6303 | -123.1155 | -0.16937 | 0.11902 | 0.27466 | -123.1522 | -0.37079 | 0.073242 | 116.8396 | 123.0423 | -122.8226 | -0.27924 | 0.082397 | 117.2104 | 122.7036 | 122.9919 | 0.24262 | 123.1384 | 116.8396 | 123.1476 | -0.24262 | -0.27924 | 123.1384 | 116.8396 | -0.24262 | 0.24262 | 123.1476 | -123.436 | -123.3444
620.8125 | 123.0148 | -122.85 | 0.20599 | 0.0045011 | 0.016024 | 0.010371 | -0.019472 | -0.0076049 | 0.06492 | 0.070489 | -6.015 | 0.22888 | -123.1613 | 0.1831 | -122.58 | -123.0377 | -0.37994 | 0.10071 | 0.22888 | -123.143 | -0.31128 | 0.022888 | 116.835 | 123.0331 | -122.7859 | -0.29297 | 0.022888 | 117.1463 | 122.4701 | 122.9507 | 0.27008 | 123.0789 | 116.835 | 123.0789 | -0.18768 | -0.29297 | 123.0789 | 116.835 | -0.18768 | 0.27008 | 123.0789 | -123.3673 | -123.349
622.5625 | 123.1338 | -122.8271 | 0.15564 | 0.01976 | 0.017306 | 0.0054581 | -0.019258 | -0.0093139 | 0.063211 | 0.06878 | -6.0745 | 0.27466 | -123.1979 | 0.16022 | -122.6303 | -123.0927 | -0.20142 | 0.09613 | 0.25177 | -123.1705 | -0.37079 | 0.11902 | 116.7526 | 122.9874 | -122.7859 | -0.34332 | 0.09613 | 117.1234 | 122.6257 | 122.9233 | 0.19684 | 123.1018 | 116.7526 | 123.0789 | -0.2655 | -0.34332 | 123.1018 | 116.7526 | -0.2655 | 0.19684 | 123.0789 | -123.3536 | -123.3261
624.25 | 123.1293 | -122.7951 | 0.16937 | -0.0031279 | 0.019656 | 0.0080215 | -0.019899 | -0.0086731 | 0.062997 | 0.06878 | -6.0974 | 0.24719 | -123.1522 | 0.14648 | -122.6166 | -123.0835 | -0.32044 | 0.054932 | 0.24261 | -123.1155 | -0.35706 | 0.077819 | 116.6977 | 122.9416 | -122.7859 | -0.32043 | 0.073242 | 117.0547 | 122.4747 | 122.85 | 0.17853 | 123.0423 | 116.6977 | 123.0377 | -0.28839 | -0.32043 | 123.0423 | 116.6977 | -0.28839 | 0.17853 | 123.0377 | -123.3215 | -123.2849
626 | 123.0515 | -122.8546 | 0.17395 | -0.0031279 | 0.014742 | 0.010799 | -0.011995 | -0.0054687 | 0.062143 | 0.070062 | -6.1249 | 0.26093 | -123.262 | 0.086975 | -122.7036 | -123.1705 | -0.16022 | -0.013733 | 0.27008 | -123.1293 | -0.40741 | 0.086975 | 116.7297 | 122.9416 | -122.8775 | -0.27466 | 0.096131 | 117.1371 | 122.6944 | 122.8409 | 0.15106 | 123.1155 | 116.7297 | 123.1247 | -0.31586 | -0.27466 | 123.1155 | 116.7297 | -0.31586 | 0.15106 | 123.1247 | -123.436 | -123.3032
627.75 | 123.1064 | -122.8363 | 0.16479 | 0.0045011 | 0.018801 | 0.010585 | -0.019899 | -0.0078187 | 0.066843 | 0.071557 | -6.0928 | 0.22888 | -123.1705 | 0.15564 | -122.6166 | -123.0743 | -0.32959 | 0.07782 | 0.23804 | -123.1384 | -0.33417 | 0.064087 | 116.7435 | 122.9919 | -122.7814 | -0.30212 | 0.073242 | 117.0776 | 122.5067 | 122.9141 | 0.21973 | 123.0652 | 116.7435 | 123.0743 | -0.23804 | -0.30212 | 123.0652 | 116.7435 | -0.23804 | 0.21973 | 123.0743 | -123.3353 | -123.3032
629.4375 | 123.0011 | -122.818 | 0.18768 | 0.012131 | 0.018587 | 0.0071671 | -0.013918 | -0.0063233 | 0.063638 | 0.070703 | -6.0516 | 0.25177 | -123.2025 | 0.21057 | -122.5845 | -123.0469 | -0.3479 | 0.1236 | 0.22888 | -123.1064 | -0.38452 | 0.064087 | 116.7664 | 123.0286 | -122.7722 | -0.28839 | 0.041199 | 117.1509 | 122.4701 | 122.9416 | 0.23346 | 123.0698 | 116.7664 | 123.0469 | -0.22888 | -0.28839 | 123.0698 | 116.7664 | -0.22888 | 0.23346 | 123.0469 | -123.3902 | -123.2941
631.1875 | 123.1155 | -122.8226 | 0.17395 | -0.0031279 | 0.016665 | 0.011012 | -0.01819 | -0.0093139 | 0.065561 | 0.068353 | -6.0654 | 0.22888 | -123.1888 | 0.20142 | -122.5754 | -123.0606 | -0.23346 | 0.14191 | 0.26093 | -123.1522 | -0.36621 | 0.054932 | 116.7572 | 123.024 | -122.7493 | -0.32959 | 0.086975 | 117.1234 | 122.5891 | 122.9645 | 0.24719 | 123.0515 | 116.7572 | 123.0835 | -0.23804 | -0.32959 | 123.0515 | 116.7572 | -0.23804 | 0.24719 | 123.0835 | -123.3627 | -123.3261
632.9219 | 123.1155 | -122.8317 | 0.16479 | 0.0045011 | 0.018374 | 0.0082351 | -0.016695 | -0.0088867 | 0.064706 | 0.067498 | -6.0791 | 0.25177 | -123.1979 | 0.16479 | -122.5983 | -123.0927 | -0.1831 | 0.10529 | 0.2655 | -123.1338 | -0.36621 | 0.086975 | 116.7526 | 122.9965 | -122.7631 | -0.30212 | 0.10071 | 117.1188 | 122.6486 | 122.937 | 0.23346 | 123.0835 | 116.7526 | 123.0972 | -0.26093 | -0.30212 | 123.0835 | 116.7526 | -0.26093 | 0.23346 | 123.0972 | -123.3627 | -123.2986
634.6094 | 123.0011 | -122.85 | 0.21057 | -0.0031279 | 0.016238 | 0.010585 | -0.01819 | -0.0073913 | 0.063211 | 0.070916 | -6.0196 | 0.21515 | -123.1705 | 0.22888 | -122.5571 | -123.0194 | -0.38452 | 0.10986 | 0.24261 | -123.0972 | -0.32043 | 0.004578 | 116.8304 | 123.0789 | -122.7676 | -0.24719 | 0.032044 | 117.1509 | 122.4655 | 122.9599 | 0.29297 | 123.0652 | 116.8304 | 123.0927 | -0.16937 | -0.24719 | 123.0652 | 116.8304 | -0.16937 | 0.29297 | 123.0927 | -123.381 | -123.3078
636.3438 | 123.0423 | -122.818 | 0.20142 | 0.012131 | 0.017519 | 0.010799 | -0.014131 | -0.0050415 | 0.063852 | 0.070062 | -6.0974 | 0.2655 | -123.2071 | 0.11902 | -122.6761 | -123.143 | -0.15106 | 0.009155 | 0.27466 | -123.1338 | -0.3891 | 0.064087 | 116.7206 | 122.937 | -122.8775 | -0.31586 | 0.073242 | 117.1097 | 122.6669 | 122.8271 | 0.14191 | 123.0835 | 116.7206 | 123.0927 | -0.32501 | -0.31586 | 123.0835 | 116.7206 | -0.32501 | 0.14191 | 123.0927 | -123.4085 | -123.3353
638.0312 | 123.0057 | -122.818 | 0.22888 | -0.0031279 | 0.019015 | 0.011012 | -0.016267 | -0.0067505 | 0.06492 | 0.070489 | -6.0196 | 0.26093 | -123.1476 | 0.23804 | -122.5342 | -123.0057 | -0.37079 | 0.1236 | 0.24261 | -123.1293 | -0.32959 | 0.032043 | 116.7984 | 123.056 | -122.7631 | -0.31128 | 0.013733 | 117.128 | 122.4472 | 122.9416 | 0.28381 | 123.0789 | 116.7984 | 123.0606 | -0.18768 | -0.31128 | 123.0789 | 116.7984 | -0.18768 | 0.28381 | 123.0606 | -123.3765 | -123.3582
639.7812 | 123.1201 | -122.7951 | 0.18768 | -0.010757 | 0.018587 | 0.0067399 | -0.016054 | -0.0076049 | 0.063425 | 0.069848 | -6.0883 | 0.26093 | -123.175 | 0.18768 | -122.58 | -123.0515 | -0.20599 | 0.11444 | 0.28381 | -123.111 | -0.37994 | 0.073242 | 116.7068 | 122.9828 | -122.7676 | -0.31586 | 0.09613 | 117.0868 | 122.5891 | 122.9095 | 0.21515 | 123.056 | 116.7068 | 123.0789 | -0.25635 | -0.31586 | 123.056 | 116.7068 | -0.25635 | 0.21515 | 123.0789 | -123.3627 | -123.2986
641.4531 | 123.0423 | -122.8088 | 0.21973 | 0.012131 | 0.019015 | 0.0075943 | -0.012636 | -0.0048279 | 0.061716 | 0.069421 | -6.1386 | 0.30212 | -123.2117 | 0.12817 | -122.6669 | -123.143 | -0.13733 | 0.018311 | 0.29297 | -123.0927 | -0.40283 | 0.082397 | 116.6702 | 122.937 | -122.8867 | -0.28381 | 0.073242 | 117.0731 | 122.6715 | 122.8271 | 0.14191 | 123.111 | 116.6702 | 123.1018 | -0.33417 | -0.28381 | 123.111 | 116.6702 | -0.33417 | 0.14191 | 123.1018 | -123.4314 | -123.3124
643.1406 | 123.1338 | -122.7814 | 0.18768 | 0.0045011 | 0.017733 | 0.0082351 | -0.017763 | -0.0086731 | 0.063425 | 0.070916 | -6.1615 | 0.27924 | -123.2162 | 0.13733 | -122.6303 | -123.1155 | -0.11444 | 0.059509 | 0.29297 | -123.1018 | -0.43488 | 0.091553 | 116.6199 | 122.9187 | -122.818 | -0.32043 | 0.10529 | 117.0547 | 122.6669 | 122.8409 | 0.15106 | 123.0606 | 116.6199 | 123.0743 | -0.33417 | -0.32043 | 123.0606 | 116.6199 | -0.33417 | 0.15106 | 123.0743 | -123.4039 | -123.2895
644.8906 | 122.9919 | -122.8363 | 0.21973 | 0.012131 | 0.019656 | 0.011012 | -0.014345 | -0.0063233 | 0.061929 | 0.07113 | -6.0928 | 0.28839 | -123.2071 | 0.14191 | -122.6395 | -123.1155 | -0.15564 | 0.045776 | 0.28381 | -123.1064 | -0.37079 | 0.068664 | 116.7435 | 122.9782 | -122.8592 | -0.27008 | 0.064086 | 117.1143 | 122.6807 | 122.8821 | 0.19684 | 123.1247 | 116.7435 | 123.1201 | -0.27924 | -0.27008 | 123.1247 | 116.7435 | -0.27924 | 0.19684 | 123.1201 | -123.4268 | -123.3261
646.5781 | 123.1064 | -122.7676 | 0.1831 | -0.0031279 | 0.016238 | 0.0031083 | -0.022249 | -0.0076049 | 0.066202 | 0.069635 | -6.1295 | 0.27008 | -123.1522 | 0.18768 | -122.5616 | -123.024 | -0.32959 | 0.09613 | 0.26093 | -123.111 | -0.38452 | 0.086976 | 116.6382 | 122.9553 | -122.7448 | -0.34332 | 0.07782 | 117.0227 | 122.438 | 122.8638 | 0.20599 | 123.0377 | 116.6382 | 123.0286 | -0.25635 | -0.34332 | 123.0377 | 116.6382 | -0.25635 | 0.20599 | 123.0286 | -123.3353 | -123.2941
648.2656 | 122.9691 | -122.8226 | 0.23346 | 0.0045011 | 0.017306 | 0.011653 | -0.01584 | -0.0063233 | 0.063852 | 0.067071 | -6.0516 | 0.25177 | -123.143 | 0.25177 | -122.5296 | -122.9919 | -0.39825 | 0.12817 | 0.25177 | -123.0927 | -0.32043 | 0.018311 | 116.7709 | 123.0743 | -122.7631 | -0.27008 | 0.018311 | 117.0914 | 122.4243 | 122.9507 | 0.29297 | 123.0743 | 116.7709 | 123.0743 | -0.16937 | -0.27008 | 123.0743 | 116.7709 | -0.16937 | 0.29297 | 123.0743 | -123.3765 | -123.3261
650.0156 | 123.0927 | -122.7859 | 0.18768 | -0.0031279 | 0.018374 | 0.0084489 | -0.014558 | -0.0082459 | 0.063425 | 0.070276 | -6.1707 | 0.3067 | -123.1796 | 0.16479 | -122.5983 | -123.1018 | -0.11902 | 0.086975 | 0.30212 | -123.111 | -0.39368 | 0.11902 | 116.6153 | 122.9507 | -122.786 | -0.32501 | 0.11444 | 117.009 | 122.6669 | 122.8729 | 0.18768 | 123.0927 | 116.6153 | 123.0881 | -0.31586 | -0.32501 | 123.0927 | 116.6153 | -0.31586 | 0.18768 | 123.0881 | -123.3673 | -123.2986
651.75 | 123.0057 | -122.818 | 0.21515 | -0.010757 | 0.01816 | 0.012508 | -0.014131 | -0.0069641 | 0.062143 | 0.070916 | -6.1066 | 0.27924 | -123.1934 | 0.1831 | -122.5891 | -123.0652 | -0.16937 | 0.11444 | 0.27466 | -123.1064 | -0.37537 | 0.064087 | 116.7114 | 123.0011 | -122.8043 | -0.28839 | 0.059509 | 117.0868 | 122.6486 | 122.9324 | 0.22888 | 123.0972 | 116.7114 | 123.0927 | -0.24719 | -0.28839 | 123.0972 | 116.7114 | -0.24719 | 0.22888 | 123.0927 | -123.4085 | -123.3215
653.5 | 123.1064 | -122.7631 | 0.17395 | -0.018387 | 0.018801 | 0.0060989 | -0.021394 | -0.0071777 | 0.064066 | 0.069635 | -6.1569 | 0.26093 | -123.1476 | 0.16479 | -122.58 | -123.0469 | -0.31128 | 0.054932 | 0.26093 | -123.0972 | -0.38452 | 0.086975 | 116.6061 | 122.9279 | -122.7539 | -0.33417 | 0.086975 | 116.9907 | 122.4518 | 122.818 | 0.18311 | 123.024 | 116.6061 | 123.024 | -0.28381 | -0.33417 | 123.024 | 116.6061 | -0.28381 | 0.18311 | 123.024 | -123.3215 | -123.2712
655.2031 | 123.0652 | -122.7859 | 0.19226 | -0.0031279 | 0.017519 | 0.011226 | -0.018831 | -0.0058961 | 0.06257 | 0.072412 | -6.134 | 0.27008 | -123.1567 | 0.16937 | -122.5891 | -123.0469 | -0.34332 | 0.068665 | 0.27466 | -123.0881 | -0.37079 | 0.07782 | 116.6519 | 122.9553 | -122.7814 | -0.30212 | 0.082397 | 117.0227 | 122.4426 | 122.8546 | 0.19684 | 123.056 | 116.6519 | 123.0606 | -0.26093 | -0.30212 | 123.056 | 116.6519 | -0.26093 | 0.19684 | 123.0606 | -123.349 | -123.2803
656.9375 | 123.0011 | -122.8226 | 0.20599 | 0.0045011 | 0.013674 | 0.010158 | -0.016054 | -0.0067505 | 0.063638 | 0.070489 | -6.1066 | 0.25177 | -123.1705 | 0.22888 | -122.5525 | -123.0011 | -0.38452 | 0.10071 | 0.27008 | -123.0835 | -0.3479 | 0.045776 | 116.716 | 123.0515 | -122.7585 | -0.26093 | 0.064087 | 117.0639 | 122.438 | 122.9233 | 0.27008 | 123.0743 | 116.716 | 123.0927 | -0.17853 | -0.26093 | 123.0743 | 116.716 | -0.17853 | 0.27008 | 123.0927 | -123.3765 | -123.2895
658.6719 | 123.0331 | -122.8088 | 0.21973 | 0.0045011 | 0.016451 | 0.01208 | -0.015199 | -0.0061097 | 0.062997 | 0.070703 | -6.1661 | 0.27008 | -123.1934 | 0.13275 | -122.6578 | -123.1064 | -0.2243 | 0.013733 | 0.27924 | -123.0972 | -0.38452 | 0.050354 | 116.6428 | 122.9416 | -122.8775 | -0.28839 | 0.059509 | 117.0273 | 122.5845 | 122.8226 | 0.15106 | 123.0789 | 116.6428 | 123.0881 | -0.29755 | -0.28839 | 123.0789 | 116.6428 | -0.29755 | 0.15106 | 123.0881 | -123.4131 | -123.317
660.3594 | 122.9874 | -122.7859 | 0.21515 | 0.012131 | 0.017519 | 0.0054581 | -0.014986 | -0.0063233 | 0.063425 | 0.070062 | -6.0974 | 0.27008 | -123.175 | 0.22888 | -122.5388 | -123.0011 | -0.35248 | 0.10071 | 0.26093 | -123.0606 | -0.3891 | 0.054932 | 116.6885 | 123.0148 | -122.7539 | -0.27466 | 0.045776 | 117.0776 | 122.4335 | 122.8867 | 0.24719 | 123.056 | 116.6885 | 123.0469 | -0.21515 | -0.27466 | 123.056 | 116.6885 | -0.21515 | 0.24719 | 123.0469 | -123.3902 | -123.2758
662.0938 | 123.0881 | -122.7768 | 0.19684 | -0.0031279 | 0.015383 | 0.0078079 | -0.020326 | -0.0093139 | 0.064279 | 0.069635 | -6.1478 | 0.25177 | -123.1293 | 0.25177 | -122.5113 | -122.9919 | -0.3479 | 0.15564 | 0.2655 | -123.1247 | -0.35248 | 0.054932 | 116.629 | 123.0286 | -122.7081 | -0.3479 | 0.068665 | 116.9815 | 122.4289 | 122.9324 | 0.2655 | 123.0286 | 116.629 | 123.0423 | -0.21515 | -0.3479 | 123.0286 | 116.629 | -0.21515 | 0.2655 | 123.0423 | -123.3261 | -123.3215
663.7812 | 122.9874 | -122.8409 | 0.21515 | -0.0031279 | 0.016665 | 0.0069535 | -0.012209 | -0.0058961 | 0.061075 | 0.070703 | -6.134 | 0.27924 | -123.2071 | 0.19226 | -122.58 | -123.0743 | -0.19226 | 0.11902 | 0.28381 | -123.0927 | -0.36621 | 0.064087 | 116.7068 | 123.0331 | -122.7951 | -0.25177 | 0.068664 | 117.0731 | 122.6486 | 122.9599 | 0.26093 | 123.1201 | 116.7068 | 123.1247 | -0.23346 | -0.25177 | 123.1201 | 116.7068 | -0.23346 | 0.26093 | 123.1247 | -123.4222 | -123.3078
665.5312 | 123.111 | -122.7676 | 0.17853 | 0.0045011 | 0.01581 | 0.010158 | -0.01584 | -0.0052551 | 0.062997 | 0.068353 | -6.2302 | 0.29755 | -123.1796 | 0.12817 | -122.6303 | -123.1155 | -0.11444 | 0.059509 | 0.31586 | -123.1247 | -0.41199 | 0.11902 | 116.5375 | 122.8958 | -122.8088 | -0.35706 | 0.13733 | 116.9495 | 122.6532 | 122.8271 | 0.13733 | 123.0652 | 116.5375 | 123.0835 | -0.3479 | -0.35706 | 123.0652 | 116.5375 | -0.3479 | 0.13733 | 123.0835 | -123.3582 | -123.3032
667.2656 | 123.0148 | -122.8134 | 0.21973 | 0.012131 | 0.019015 | 0.0078079 | -0.013277 | -0.0067505 | 0.062143 | 0.071771 | -6.1478 | 0.29297 | -123.1796 | 0.17853 | -122.5708 | -123.0652 | -0.17395 | 0.10986 | 0.28839 | -123.0972 | -0.36621 | 0.073242 | 116.6656 | 122.9919 | -122.7905 | -0.28381 | 0.068664 | 117.0319 | 122.6395 | 122.9233 | 0.24262 | 123.1064 | 116.6656 | 123.1018 | -0.25177 | -0.28381 | 123.1064 | 116.6656 | -0.25177 | 0.24262 | 123.1018 | -123.3994 | -123.317
669.0156 | 123.0652 | -122.7768 | 0.19684 | -0.0031279 | 0.016024 | 0.0063125 | -0.019899 | -0.0093139 | 0.062997 | 0.069635 | -6.1386 | 0.2655 | -123.1018 | 0.24719 | -122.4884 | -122.9736 | -0.36621 | 0.16479 | 0.2655 | -123.1064 | -0.32501 | 0.068665 | 116.6382 | 123.024 | -122.6852 | -0.32959 | 0.068665 | 116.9632 | 122.4106 | 122.9416 | 0.28839 | 123.0423 | 116.6382 | 123.0423 | -0.19684 | -0.32959 | 123.0423 | 116.6382 | -0.19684 | 0.28839 | 123.0423 | -123.2986 | -123.3032
670.7031 | 122.9599 | -122.8043 | 0.20599 | 0.0045011 | 0.016238 | 0.010371 | -0.016267 | -0.0069641 | 0.062997 | 0.069421 | -6.1295 | 0.24261 | -123.1659 | 0.23804 | -122.5204 | -122.9782 | -0.40741 | 0.13275 | 0.26093 | -123.056 | -0.36163 | 0.036621 | 116.6748 | 123.0423 | -122.7264 | -0.25177 | 0.054931 | 117.0364 | 122.3969 | 122.937 | 0.28381 | 123.0469 | 116.6748 | 123.0652 | -0.17395 | -0.25177 | 123.0469 | 116.6748 | -0.17395 | 0.28381 | 123.0652 | -123.3719 | -123.262
672.4531 | 123.0057 | -122.7905 | 0.21973 | -0.0031279 | 0.017306 | 0.010371 | -0.010713 | -0.0061097 | 0.061929 | 0.072198 | -6.1798 | 0.27924 | -123.2025 | 0.16937 | -122.6166 | -123.0881 | -0.16937 | 0.041199 | 0.30212 | -123.0789 | -0.41199 | 0.059509 | 116.6107 | 122.9599 | -122.8363 | -0.28839 | 0.082397 | 117.0227 | 122.6212 | 122.8317 | 0.17395 | 123.0698 | 116.6107 | 123.0927 | -0.29755 | -0.28839 | 123.0698 | 116.6107 | -0.29755 | 0.17395 | 123.0927 | -123.4222 | -123.2986
674.1406 | 123.056 | -122.7676 | 0.19684 | -0.010757 | 0.017947 | 0.013576 | -0.021181 | -0.0091003 | 0.066843 | 0.071344 | -6.1844 | 0.2655 | -123.1384 | 0.19226 | -122.5525 | -123.024 | -0.34332 | 0.050354 | 0.2655 | -123.0835 | -0.37079 | 0.068665 | 116.5833 | 122.9599 | -122.7493 | -0.31586 | 0.068665 | 116.954 | 122.4243 | 122.818 | 0.21515 | 123.0331 | 116.5833 | 123.0331 | -0.25635 | -0.31586 | 123.0331 | 116.5833 | -0.25635 | 0.21515 | 123.0331 | -123.3353 | -123.2803
675.8906 | 123.0606 | -122.7402 | 0.18768 | -0.0031279 | 0.015383 | 0.0078079 | -0.020113 | -0.0093139 | 0.065988 | 0.070916 | -6.189 | 0.27008 | -123.1201 | 0.23804 | -122.5067 | -122.9599 | -0.3479 | 0.14191 | 0.2655 | -123.0927 | -0.37994 | 0.082398 | 116.5512 | 122.9782 | -122.6944 | -0.35248 | 0.07782 | 116.9312 | 122.3923 | 122.8821 | 0.23346 | 123.0103 | 116.5512 | 123.0057 | -0.21973 | -0.35248 | 123.0103 | 116.5512 | -0.21973 | 0.23346 | 123.0057 | -123.3078 | -123.2803
677.625 | 122.9736 | -122.7951 | 0.20142 | -0.0031279 | 0.014956 | 0.0095169 | -0.01584 | -0.0078187 | 0.065347 | 0.069848 | -6.1615 | 0.24719 | -123.1293 | 0.23346 | -122.5296 | -122.9782 | -0.3891 | 0.1236 | 0.24719 | -123.056 | -0.33417 | 0.045776 | 116.6336 | 123.0286 | -122.731 | -0.26093 | 0.045776 | 116.9678 | 122.406 | 122.9187 | 0.2655 | 123.0423 | 116.6336 | 123.0423 | -0.1831 | -0.26093 | 123.0423 | 116.6336 | -0.1831 | 0.2655 | 123.0423 | -123.3307 | -123.2574
679.3594 | 122.9645 | -122.7997 | 0.23804 | -0.0031279 | 0.016665 | 0.010371 | -0.018404 | -0.0082459 | 0.063211 | 0.069635 | -6.134 | 0.24719 | -123.143 | 0.25177 | -122.5204 | -122.9645 | -0.38452 | 0.11902 | 0.25177 | -123.0423 | -0.34332 | 0.009155 | 116.6656 | 123.0515 | -122.7585 | -0.24261 | 0.013733 | 117.009 | 122.4152 | 122.9187 | 0.27924 | 123.0469 | 116.6656 | 123.0515 | -0.16479 | -0.24261 | 123.0469 | 116.6656 | -0.16479 | 0.27924 | 123.0515 | -123.381 | -123.2803
681.1094 | 123.111 | -122.7585 | 0.16937 | -0.0031279 | 0.019015 | 0.0065263 | -0.01819 | -0.0097413 | 0.063852 | 0.070916 | -6.2485 | 0.25635 | -123.1293 | 0.17853 | -122.5571 | -123.0377 | -0.31128 | 0.059509 | 0.27466 | -123.1247 | -0.37079 | 0.086975 | 116.51 | 122.937 | -122.7264 | -0.36621 | 0.10529 | 116.8808 | 122.4472 | 122.818 | 0.20142 | 123.0148 | 116.51 | 123.0331 | -0.27924 | -0.36621 | 123.0148 | 116.51 | -0.27924 | 0.20142 | 123.0331 | -123.2986 | -123.2941
682.8594 | 123.0698 | -122.7676 | 0.20142 | -0.0031279 | 0.016238 | 0.010585 | -0.018617 | -0.0086731 | 0.06492 | 0.070276 | -6.1935 | 0.26093 | -123.1384 | 0.25177 | -122.493 | -122.9828 | -0.33417 | 0.14648 | 0.25177 | -123.0972 | -0.37079 | 0.059509 | 116.5741 | 123.0194 | -122.6944 | -0.32959 | 0.050354 | 116.9449 | 122.4335 | 122.9141 | 0.27466 | 123.0286 | 116.5741 | 123.0194 | -0.21515 | -0.32959 | 123.0286 | 116.5741 | -0.21515 | 0.27466 | 123.0194 | -123.3398 | -123.2986
684.5469 | 123.0835 | -122.7539 | 0.20142 | 0.0045011 | 0.01816 | 0.0073807 | -0.013918 | -0.010168 | 0.060434 | 0.067712 | -6.2576 | 0.29297 | -123.2208 | 0.17395 | -122.5845 | -123.0789 | -0.13275 | 0.091553 | 0.31586 | -123.0743 | -0.46692 | 0.091553 | 116.4963 | 122.9279 | -122.7859 | -0.32044 | 0.11444 | 116.9632 | 122.6212 | 122.8455 | 0.16937 | 123.0469 | 116.4963 | 123.0698 | -0.32501 | -0.32044 | 123.0469 | 116.4963 | -0.32501 | 0.16937 | 123.0698 | -123.4222 | -123.2758
686.2969 | 122.9599 | -122.7814 | 0.21973 | 0.0045011 | 0.01581 | 0.0088761 | -0.013704 | -0.0037597 | 0.066629 | 0.07113 | -6.1478 | 0.2655 | -123.1476 | 0.25177 | -122.525 | -122.9874 | -0.39825 | 0.11444 | 0.25635 | -123.0469 | -0.36621 | 0.045776 | 116.6336 | 123.0331 | -122.7448 | -0.2655 | 0.036621 | 116.9998 | 122.3831 | 122.8958 | 0.25635 | 123.0469 | 116.6336 | 123.0377 | -0.20599 | -0.2655 | 123.0469 | 116.6336 | -0.20599 | 0.25635 | 123.0377 | -123.3673 | -123.2666
688.0469 | 123.0835 | -122.7631 | 0.17395 | 0.0045011 | 0.016665 | 0.0099441 | -0.02054 | -0.0099549 | 0.062143 | 0.071771 | -6.2073 | 0.25635 | -123.1476 | 0.20599 | -122.5159 | -123.0377 | -0.22888 | 0.11902 | 0.28381 | -123.0743 | -0.38452 | 0.082398 | 116.5558 | 122.9691 | -122.6898 | -0.31128 | 0.10986 | 116.9403 | 122.5342 | 122.8821 | 0.24719 | 123.0194 | 116.5558 | 123.0469 | -0.27466 | -0.31128 | 123.0194 | 116.5558 | -0.27466 | 0.24719 | 123.0469 | -123.3215 | -123.2483
689.75 | 122.9599 | -122.8043 | 0.21515 | -0.0031279 | 0.013033 | 0.010799 | -0.016695 | -0.0058961 | 0.057657 | 0.071771 | -6.1844 | 0.23804 | -123.1384 | 0.24261 | -122.5067 | -122.9691 | -0.40741 | 0.13275 | 0.25177 | -123.0057 | -0.33417 | 0.022888 | 116.6199 | 123.0469 | -122.7219 | -0.20142 | 0.036621 | 116.954 | 122.3969 | 122.937 | 0.29755 | 123.0423 | 116.6199 | 123.056 | -0.16479 | -0.20142 | 123.0423 | 116.6199 | -0.16479 | 0.29755 | 123.056 | -123.3536 | -123.2208
691.4844 | 122.937 | -122.7859 | 0.19684 | 0.0045011 | 0.014956 | 0.0095169 | -0.01349 | -0.0052551 | 0.064066 | 0.069635 | -6.1661 | 0.25177 | -123.1018 | 0.23804 | -122.5021 | -122.9828 | -0.39368 | 0.11444 | 0.27466 | -123.0423 | -0.31586 | 0.054932 | 116.6199 | 123.024 | -122.699 | -0.25635 | 0.07782 | 116.9357 | 122.3923 | 122.9004 | 0.28381 | 123.0377 | 116.6199 | 123.0606 | -0.19684 | -0.25635 | 123.0377 | 116.6199 | -0.19684 | 0.28381 | 123.0606 | -123.2986 | -123.2391
693.2188 | 123.0286 | -122.7814 | 0.20599 | -0.0031279 | 0.014529 | 0.0069535 | -0.019899 | -0.010168 | 0.064493 | 0.068994 | -6.1935 | 0.26093 | -123.1247 | 0.27466 | -122.4838 | -122.9828 | -0.35248 | 0.17853 | 0.27008 | -123.0469 | -0.34332 | 0.054931 | 116.5878 | 123.056 | -122.6898 | -0.2655 | 0.064087 | 116.9312 | 122.4289 | 122.9599 | 0.29755 | 123.0423 | 116.5878 | 123.0515 | -0.20142 | -0.2655 | 123.0423 | 116.5878 | -0.20142 | 0.29755 | 123.0515 | -123.3307 | -123.2529
694.9688 | 122.937 | -122.7768 | 0.21057 | 0.0045011 | 0.013888 | 0.011226 | -0.015199 | -0.0052551 | 0.062997 | 0.073266 | -6.2073 | 0.25177 | -123.1705 | 0.24719 | -122.525 | -122.9691 | -0.39368 | 0.12817 | 0.26093 | -123.0286 | -0.39368 | 0.041199 | 116.5695 | 123.024 | -122.7356 | -0.25177 | 0.050354 | 116.9632 | 122.3831 | 122.905 | 0.25177 | 123.0286 | 116.5695 | 123.0377 | -0.19226 | -0.25177 | 123.0286 | 116.5695 | -0.19226 | 0.25177 | 123.0377 | -123.381 | -123.2391
696.7031 | 122.9507 | -122.7997 | 0.21057 | -0.0031279 | 0.016024 | 0.011012 | -0.011995 | -0.0067505 | 0.062143 | 0.070489 | -6.2119 | 0.28839 | -123.1842 | 0.19226 | -122.5616 | -123.0606 | -0.17395 | 0.09613 | 0.28381 | -123.0789 | -0.38452 | 0.07782 | 116.5878 | 122.9919 | -122.7722 | -0.27923 | 0.073242 | 116.9724 | 122.6257 | 122.8958 | 0.23804 | 123.0881 | 116.5878 | 123.0835 | -0.26093 | -0.27923 | 123.0881 | 116.5878 | -0.26093 | 0.23804 | 123.0835 | -123.3948 | -123.2895
698.4062 | 123.0011 | -122.7814 | 0.21973 | -0.010757 | 0.018587 | 0.011867 | -0.011141 | -0.0061097 | 0.061502 | 0.070489 | -6.2485 | 0.28381 | -123.1934 | 0.12817 | -122.6257 | -123.1247 | -0.15106 | 0.022888 | 0.3067 | -123.1064 | -0.41199 | 0.064086 | 116.5329 | 122.9095 | -122.8455 | -0.32501 | 0.086975 | 116.9449 | 122.6303 | 122.8043 | 0.15564 | 123.0652 | 116.5329 | 123.0881 | -0.34332 | -0.32501 | 123.0652 | 116.5329 | -0.34332 | 0.15564 | 123.0881 | -123.4131 | -123.3261
700.1562 | 123.0652 | -122.7722 | 0.17395 | -0.0031279 | 0.017092 | 0.010158 | -0.022249 | -0.0076049 | 0.063425 | 0.070276 | -6.2531 | 0.27466 | -123.1476 | 0.21057 | -122.4884 | -122.9691 | -0.34332 | 0.12817 | 0.24719 | -123.0515 | -0.37537 | 0.10071 | 116.5192 | 122.9828 | -122.6624 | -0.27924 | 0.073242 | 116.8945 | 122.4289 | 122.9004 | 0.28381 | 123.0469 | 116.5192 | 123.0194 | -0.19684 | -0.27924 | 123.0469 | 116.5192 | -0.19684 | 0.28381 | 123.0194 | -123.3215 | -123.2254
701.8281 | 123.0789 | -122.7905 | 0.16479 | -0.0031279 | 0.018587 | 0.0095169 | -0.019258 | -0.0084595 | 0.061929 | 0.069207 | -6.2531 | 0.25177 | -123.1201 | 0.21515 | -122.5067 | -123.0148 | -0.23804 | 0.1236 | 0.27466 | -123.0835 | -0.32959 | 0.086975 | 116.5375 | 123.0057 | -122.6715 | -0.29297 | 0.10986 | 116.8671 | 122.5525 | 122.9141 | 0.28381 | 123.0423 | 116.5375 | 123.0652 | -0.22431 | -0.29297 | 123.0423 | 116.5375 | -0.22431 | 0.28381 | 123.0652 | -123.2849 | -123.2483
703.5625 | 122.9507 | -122.8317 | 0.23346 | 0.0045011 | 0.018374 | 0.011012 | -0.010286 | -0.0061097 | 0.061075 | 0.068353 | -6.2256 | 0.27466 | -123.1796 | 0.19684 | -122.5433 | -123.0423 | -0.1831 | 0.1236 | 0.28839 | -123.0515 | -0.3479 | 0.041199 | 116.6061 | 123.0286 | -122.7768 | -0.21973 | 0.054932 | 116.954 | 122.6486 | 122.9553 | 0.28839 | 123.1064 | 116.6061 | 123.1201 | -0.21057 | -0.21973 | 123.1064 | 116.6061 | -0.21057 | 0.28839 | 123.1201 | -123.4131 | -123.2849
705.25 | 123.056 | -122.7539 | 0.1831 | 0.0045011 | 0.016238 | 0.0069535 | -0.013704 | -0.0065369 | 0.059793 | 0.072412 | -6.3034 | 0.28381 | -123.2025 | 0.14648 | -122.5708 | -123.0698 | -0.12817 | 0.07782 | 0.29755 | -123.0789 | -0.44861 | 0.10071 | 116.4505 | 122.9004 | -122.7539 | -0.32501 | 0.11444 | 116.8991 | 122.6257 | 122.8317 | 0.1831 | 123.0377 | 116.4505 | 123.0515 | -0.31586 | -0.32501 | 123.0377 | 116.4505 | -0.31586 | 0.1831 | 123.0515 | -123.3856 | -123.262
707 | 123.0881 | -122.7356 | 0.1831 | -0.0031279 | 0.017519 | 0.0071671 | -0.021394 | -0.0058961 | 0.063638 | 0.070703 | -6.2942 | 0.24261 | -123.1384 | 0.16479 | -122.5204 | -123.0331 | -0.31586 | 0.050354 | 0.2655 | -123.0652 | -0.40283 | 0.05951 | 116.4413 | 122.9004 | -122.7036 | -0.32959 | 0.082398 | 116.8442 | 122.4197 | 122.7859 | 0.21515 | 122.9782 | 116.4413 | 123.0011 | -0.29755 | -0.32959 | 122.9782 | 116.4413 | -0.29755 | 0.21515 | 123.0011 | -123.3215 | -123.2483
708.7344 | 123.0789 | -122.7448 | 0.1831 | -0.010757 | 0.017306 | 0.01208 | -0.022035 | -0.0080323 | 0.063211 | 0.06878 | -6.308 | 0.25635 | -123.1476 | 0.18768 | -122.5159 | -123.0148 | -0.32044 | 0.064087 | 0.28839 | -123.0881 | -0.40283 | 0.073243 | 116.4368 | 122.9324 | -122.699 | -0.34332 | 0.10529 | 116.8396 | 122.4243 | 122.8088 | 0.22888 | 123.0011 | 116.4368 | 123.0331 | -0.27008 | -0.34332 | 123.0011 | 116.4368 | -0.27008 | 0.22888 | 123.0331 | -123.3307 | -123.2712
710.4844 | 123.0881 | -122.731 | 0.19226 | 0.012131 | 0.017092 | 0.011439 | -0.018404 | -0.0073913 | 0.062784 | 0.070489 | -6.3034 | 0.25635 | -123.143 | 0.18768 | -122.5571 | -123.0377 | -0.32501 | 0.068665 | 0.27008 | -123.0881 | -0.41199 | 0.064087 | 116.4276 | 122.9187 | -122.7493 | -0.35706 | 0.07782 | 116.8396 | 122.406 | 122.7997 | 0.17395 | 122.9874 | 116.4276 | 123.0011 | -0.3067 | -0.35706 | 122.9874 | 116.4276 | -0.3067 | 0.17395 | 123.0011 | -123.3353 | -123.2803
712.1719 | 123.0835 | -122.7448 | 0.19684 | 0.0045011 | 0.017947 | 0.010799 | -0.014131 | -0.0076049 | 0.060434 | 0.070489 | -6.3263 | 0.29297 | -123.1888 | 0.16937 | -122.5616 | -123.0698 | -0.12817 | 0.068665 | 0.30212 | -123.0881 | -0.44403 | 0.096131 | 116.4185 | 122.9141 | -122.7585 | -0.34332 | 0.10529 | 116.8625 | 122.6166 | 122.8134 | 0.1831 | 123.0377 | 116.4185 | 123.0469 | -0.32501 | -0.34332 | 123.0377 | 116.4185 | -0.32501 | 0.1831 | 123.0469 | -123.3856 | -123.2849
713.9219 | 123.1064 | -122.7402 | 0.17853 | 0.0045011 | 0.017947 | 0.0090897 | -0.017122 | -0.0080323 | 0.062357 | 0.06878 | -6.3538 | 0.28839 | -123.2025 | 0.13275 | -122.5937 | -123.1064 | -0.10529 | 0.054932 | 0.31128 | -123.111 | -0.46234 | 0.10986 | 116.3864 | 122.8729 | -122.7722 | -0.37079 | 0.13275 | 116.8488 | 122.6349 | 122.7951 | 0.14648 | 123.0286 | 116.3864 | 123.0515 | -0.36621 | -0.37079 | 123.0286 | 116.3864 | -0.36621 | 0.14648 | 123.0515 | -123.381 | -123.2895
715.6719 | 123.0606 | -122.7585 | 0.19226 | -0.0031279 | 0.016024 | 0.0069535 | -0.017976 | -0.0086731 | 0.065347 | 0.070276 | -6.2668 | 0.25635 | -123.1293 | 0.22888 | -122.4976 | -123.0011 | -0.25635 | 0.15106 | 0.27924 | -123.1018 | -0.37079 | 0.064087 | 116.4917 | 122.9874 | -122.6898 | -0.34332 | 0.086975 | 116.8625 | 122.5021 | 122.9095 | 0.26093 | 123.0148 | 116.4917 | 123.0377 | -0.24262 | -0.34332 | 123.0148 | 116.4917 | -0.24262 | 0.26093 | 123.0377 | -123.3215 | -123.2941
717.3438 | 123.0423 | -122.7539 | 0.17853 | 0.012131 | 0.017947 | 0.010371 | -0.013918 | -0.0095277 | 0.062784 | 0.069635 | -6.3263 | 0.28839 | -123.1888 | 0.16937 | -122.5571 | -123.056 | -0.13733 | 0.10071 | 0.29297 | -123.0743 | -0.43488 | 0.10986 | 116.4276 | 122.9233 | -122.7356 | -0.32044 | 0.11444 | 116.8625 | 122.6166 | 122.8546 | 0.19684 | 123.0423 | 116.4276 | 123.0469 | -0.30212 | -0.32044 | 123.0423 | 116.4276 | -0.30212 | 0.19684 | 123.0469 | -123.3673 | -123.2529
719.0781 | 122.9507 | -122.7997 | 0.2243 | -0.0031279 | 0.019015 | 0.01208 | -0.013704 | -0.0048279 | 0.060648 | 0.07113 | -6.2805 | 0.27924 | -123.1934 | 0.17853 | -122.5342 | -123.0469 | -0.1831 | 0.12817 | 0.27466 | -123.0698 | -0.39368 | 0.054932 | 116.5192 | 122.9782 | -122.7585 | -0.27008 | 0.050354 | 116.9128 | 122.6166 | 122.9279 | 0.2655 | 123.0789 | 116.5192 | 123.0743 | -0.24719 | -0.27008 | 123.0789 | 116.5192 | -0.24719 | 0.2655 | 123.0743 | -123.4177 | -123.2941
720.8281 | 123.0469 | -122.7356 | 0.17853 | 0.012131 | 0.019015 | 0.0090897 | -0.021822 | -0.0082459 | 0.061502 | 0.070916 | -6.3171 | 0.25635 | -123.1064 | 0.1831 | -122.525 | -123.0011 | -0.32501 | 0.050354 | 0.28839 | -123.0606 | -0.37079 | 0.07782 | 116.4185 | 122.9187 | -122.7036 | -0.32501 | 0.10986 | 116.7892 | 122.4106 | 122.7859 | 0.21057 | 122.9919 | 116.4185 | 123.024 | -0.2655 | -0.32501 | 122.9919 | 116.4185 | -0.2655 | 0.21057 | 123.024 | -123.2849 | -123.2391
722.5781 | 122.9782 | -122.731 | 0.21057 | 0.0045011 | 0.016451 | 0.012508 | -0.019258 | -0.0073913 | 0.063425 | 0.069421 | -6.2805 | 0.24719 | -123.1064 | 0.19226 | -122.5113 | -122.9828 | -0.36621 | 0.068665 | 0.2655 | -123.0698 | -0.37537 | 0.036621 | 116.4505 | 122.9233 | -122.7219 | -0.33874 | 0.054932 | 116.8259 | 122.3648 | 122.7997 | 0.21973 | 122.9782 | 116.4505 | 122.9965 | -0.25177 | -0.33874 | 122.9782 | 116.4505 | -0.25177 | 0.21973 | 122.9965 | -123.317 | -123.2803
724.2656 | 122.9645 | -122.7814 | 0.21515 | -0.0031279 | 0.018374 | 0.014003 | -0.014131 | -0.0048279 | 0.060648 | 0.068994 | -6.2988 | 0.28839 | -123.1888 | 0.15106 | -122.5708 | -123.0698 | -0.16937 | 0.054932 | 0.28381 | -123.0469 | -0.40741 | 0.073242 | 116.4825 | 122.9324 | -122.7859 | -0.2655 | 0.068664 | 116.89 | 122.612 | 122.8363 | 0.21057 | 123.0698 | 116.4825 | 123.0652 | -0.28839 | -0.2655 | 123.0698 | 116.4825 | -0.28839 | 0.21057 | 123.0652 | -123.4039 | -123.262
726.0156 | 122.9828 | -122.7859 | 0.20142 | 0.012131 | 0.01816 | 0.0065263 | -0.013277 | -0.0050415 | 0.061288 | 0.072198 | -6.3354 | 0.3067 | -123.1888 | 0.13275 | -122.5937 | -123.0972 | -0.15106 | 0.027466 | 0.29755 | -123.0789 | -0.40283 | 0.10529 | 116.4505 | 122.9187 | -122.7951 | -0.29297 | 0.09613 | 116.8533 | 122.6349 | 122.8134 | 0.19226 | 123.0927 | 116.4505 | 123.0835 | -0.31128 | -0.29297 | 123.0927 | 116.4505 | -0.31128 | 0.19226 | 123.0835 | -123.3902 | -123.2803
727.6875 | 123.0469 | -122.7448 | 0.17853 | -0.0031279 | 0.016024 | 0.0050309 | -0.021394 | -0.0054687 | 0.065775 | 0.068567 | -6.3446 | 0.26093 | -123.1018 | 0.19684 | -122.4701 | -122.9782 | -0.32501 | 0.10986 | 0.27008 | -123.0835 | -0.35706 | 0.082397 | 116.4001 | 122.9416 | -122.6486 | -0.33875 | 0.091553 | 116.7572 | 122.4197 | 122.8546 | 0.27466 | 123.0057 | 116.4001 | 123.0148 | -0.23346 | -0.33875 | 123.0057 | 116.4001 | -0.23346 | 0.27466 | 123.0148 | -123.2803 | -123.262
729.4219 | 123.0743 | -122.7356 | 0.1831 | 0.0045011 | 0.016238 | 0.0099441 | -0.021394 | -0.0088867 | 0.06492 | 0.067926 | -6.3629 | 0.25177 | -123.1247 | 0.1831 | -122.5113 | -123.0194 | -0.3067 | 0.059509 | 0.27924 | -123.0927 | -0.3891 | 0.068665 | 116.3727 | 122.9187 | -122.6944 | -0.35706 | 0.096131 | 116.7618 | 122.4289 | 122.7951 | 0.2243 | 122.9874 | 116.3727 | 123.0148 | -0.28381 | -0.35706 | 122.9874 | 116.3727 | -0.28381 | 0.2243 | 123.0148 | -123.3078 | -123.2758
731.1094 | 122.9599 | -122.7768 | 0.21515 | 0.0045011 | 0.020937 | 0.011867 | -0.010072 | -0.0054687 | 0.060434 | 0.07113 | -6.3171 | 0.30212 | -123.175 | 0.15106 | -122.5891 | -123.0789 | -0.18768 | 0.059509 | 0.30212 | -123.0743 | -0.39826 | 0.086975 | 116.4597 | 122.9279 | -122.8043 | -0.29755 | 0.086975 | 116.8579 | 122.5891 | 122.8363 | 0.18768 | 123.0789 | 116.4597 | 123.0789 | -0.30212 | -0.29755 | 123.0789 | 116.4597 | -0.30212 | 0.18768 | 123.0789 | -123.3902 | -123.2895
732.8438 | 123.056 | -122.7768 | 0.19226 | 0.0045011 | 0.019015 | 0.0060989 | -0.013704 | -0.0063233 | 0.062357 | 0.07113 | -6.3766 | 0.29297 | -123.1705 | 0.14648 | -122.5433 | -123.0606 | -0.1236 | 0.086975 | 0.31586 | -123.056 | -0.39368 | 0.10071 | 116.4001 | 122.9233 | -122.7356 | -0.27924 | 0.1236 | 116.7938 | 122.6532 | 122.8638 | 0.23346 | 123.0698 | 116.4001 | 123.0927 | -0.28381 | -0.27924 | 123.0698 | 116.4001 | -0.28381 | 0.23346 | 123.0927 | -123.3627 | -123.2483
734.5938 | 122.9416 | -122.7676 | 0.21057 | -0.0031279 | 0.017306 | 0.015071 | -0.012636 | -0.0054687 | 0.061502 | 0.071344 | -6.3263 | 0.26093 | -123.1888 | 0.15564 | -122.5525 | -123.056 | -0.1831 | 0.082397 | 0.3067 | -123.056 | -0.42114 | 0.050354 | 116.4413 | 122.9233 | -122.7631 | -0.28839 | 0.096131 | 116.8625 | 122.5845 | 122.85 | 0.21515 | 123.0286 | 116.4413 | 123.0743 | -0.28839 | -0.28839 | 123.0286 | 116.4413 | -0.28839 | 0.21515 | 123.0743 | -123.3994 | -123.2666
736.2812 | 123.0515 | -122.7219 | 0.18768 | 0.012131 | 0.016878 | 0.0048173 | -0.018617 | -0.0073913 | 0.062143 | 0.067926 | -6.3858 | 0.28381 | -123.1567 | 0.13733 | -122.5571 | -123.0743 | -0.12817 | 0.073242 | 0.29755 | -123.0881 | -0.43488 | 0.09613 | 116.3361 | 122.8592 | -122.7448 | -0.36621 | 0.10986 | 116.7709 | 122.5937 | 122.7951 | 0.16479 | 123.0057 | 116.3361 | 123.0194 | -0.35248 | -0.36621 | 123.0057 | 116.3361 | -0.35248 | 0.16479 | 123.0194 | -123.3444 | -123.2758
738.0312 | 123.0606 | -122.7127 | 0.17853 | -0.010757 | 0.018801 | 0.0071671 | -0.017763 | -0.0058961 | 0.063425 | 0.069421 | -6.4041 | 0.3067 | -123.1476 | 0.12817 | -122.5662 | -123.0927 | -0.10986 | 0.068665 | 0.30212 | -123.0881 | -0.43487 | 0.12817 | 116.3086 | 122.8409 | -122.7448 | -0.37537 | 0.1236 | 116.7435 | 122.6028 | 122.7814 | 0.14649 | 123.0194 | 116.3086 | 123.0148 | -0.37994 | -0.37537 | 123.0194 | 116.3086 | -0.37994 | 0.14649 | 123.0148 | -123.3261 | -123.2666
739.7031 | 122.9645 | -122.7676 | 0.19684 | 0.0045011 | 0.019442 | 0.014644 | -0.015199 | -0.0065369 | 0.062784 | 0.071344 | -6.3812 | 0.28381 | -123.1567 | 0.086975 | -122.5983 | -123.0835 | -0.15106 | 0.013733 | 0.29297 | -123.0835 | -0.3891 | 0.086975 | 116.3864 | 122.8546 | -122.7951 | -0.31586 | 0.096131 | 116.7755 | 122.6166 | 122.7814 | 0.16937 | 123.0515 | 116.3864 | 123.0606 | -0.31586 | -0.31586 | 123.0515 | 116.3864 | -0.31586 | 0.16937 | 123.0606 | -123.3536 | -123.2803
741.4531 | 122.9507 | -122.7585 | 0.2243 | 0.0045011 | 0.017306 | 0.0039627 | -0.020967 | -0.0058961 | 0.064279 | 0.070062 | -6.3309 | 0.2655 | -123.111 | 0.19226 | -122.4976 | -122.9919 | -0.37994 | 0.086975 | 0.24719 | -123.0606 | -0.35248 | 0.041199 | 116.4276 | 122.9507 | -122.7219 | -0.30212 | 0.022888 | 116.7801 | 122.3785 | 122.8455 | 0.26093 | 123.024 | 116.4276 | 123.0057 | -0.23346 | -0.30212 | 123.024 | 116.4276 | -0.23346 | 0.26093 | 123.0057 | -123.3353 | -123.2849
743.1406 | 122.9828 | -122.7722 | 0.20599 | -0.0031279 | 0.018587 | 0.011653 | -0.01349 | -0.0082459 | 0.063425 | 0.070062 | -6.4041 | 0.28381 | -123.1705 | 0.10529 | -122.6212 | -123.1155 | -0.16937 | 0.004578 | 0.29755 | -123.0789 | -0.39825 | 0.077819 | 116.3681 | 122.8775 | -122.8271 | -0.3067 | 0.091552 | 116.7664 | 122.6028 | 122.7768 | 0.15106 | 123.056 | 116.3681 | 123.0698 | -0.34332 | -0.3067 | 123.056 | 116.3681 | -0.34332 | 0.15106 | 123.0698 | -123.3765 | -123.2849
744.8906 | 122.9462 | -122.7539 | 0.21515 | 0.012131 | 0.017733 | 0.010585 | -0.014558 | -0.0073913 | 0.062997 | 0.072839 | -6.34 | 0.27466 | -123.1613 | 0.12817 | -122.5708 | -123.0743 | -0.1831 | 0.054932 | 0.31128 | -123.0743 | -0.40741 | 0.059509 | 116.4139 | 122.8821 | -122.7859 | -0.32044 | 0.09613 | 116.8213 | 122.5708 | 122.8088 | 0.1831 | 123.0286 | 116.4139 | 123.0652 | -0.32044 | -0.32044 | 123.0286 | 116.4139 | -0.32044 | 0.1831 | 123.0652 | -123.3765 | -123.2895
746.5938 | 122.9736 | -122.7768 | 0.19226 | 0.012131 | 0.020296 | 0.0058853 | -0.01584 | -0.0071777 | 0.063638 | 0.071557 | -6.3904 | 0.29297 | -123.1659 | 0.086975 | -122.6074 | -123.0972 | -0.1831 | -0.004578 | 0.31128 | -123.1064 | -0.3891 | 0.10071 | 116.3864 | 122.8638 | -122.7997 | -0.32959 | 0.11902 | 116.7755 | 122.5937 | 122.7722 | 0.16937 | 123.0698 | 116.3864 | 123.0881 | -0.32044 | -0.32959 | 123.0698 | 116.3864 | -0.32044 | 0.16937 | 123.0881 | -123.3582 | -123.2986
748.3438 | 122.9645 | -122.7676 | 0.1831 | 0.0045011 | 0.019015 | 0.0088761 | -0.016908 | -0.0073913 | 0.063425 | 0.069421 | -6.4041 | 0.29297 | -123.1522 | 0.10529 | -122.58 | -123.0698 | -0.20599 | -0.004578 | 0.28839 | -123.0698 | -0.38452 | 0.10986 | 116.3635 | 122.8729 | -122.7631 | -0.30212 | 0.10529 | 116.748 | 122.5616 | 122.7631 | 0.18768 | 123.0606 | 116.3635 | 123.056 | -0.30212 | -0.30212 | 123.0606 | 116.3635 | -0.30212 | 0.18768 | 123.056 | -123.3353 | -123.2529
750.0938 | 123.0606 | -122.7036 | 0.1831 | -0.0031279 | 0.018374 | 0.010371 | -0.022249 | -0.0076049 | 0.06492 | 0.07113 | -6.4407 | 0.2655 | -123.1018 | 0.16937 | -122.5067 | -122.9874 | -0.33875 | 0.073242 | 0.2655 | -123.0881 | -0.39825 | 0.082398 | 116.2628 | 122.8729 | -122.6898 | -0.38452 | 0.082398 | 116.6611 | 122.3648 | 122.7768 | 0.19684 | 122.9691 | 116.2628 | 122.9691 | -0.28381 | -0.38452 | 122.9691 | 116.2628 | -0.28381 | 0.19684 | 122.9691 | -123.2849 | -123.2712
751.7656 | 123.0194 | -122.7539 | 0.19684 | 0.0045011 | 0.014956 | 0.011226 | -0.014131 | -0.0046143 | 0.060648 | 0.072625 | -6.3995 | 0.27924 | -123.1613 | 0.15564 | -122.5433 | -123.0286 | -0.29297 | 0.059509 | 0.28839 | -123.0331 | -0.40741 | 0.082398 | 116.3544 | 122.9095 | -122.7402 | -0.27924 | 0.091553 | 116.7618 | 122.4609 | 122.8134 | 0.21057 | 123.0331 | 116.3544 | 123.0423 | -0.27466 | -0.27924 | 123.0331 | 116.3544 | -0.27466 | 0.21057 | 123.0423 | -123.3582 | -123.23
753.5156 | 123.056 | -122.7219 | 0.17853 | 0.0045011 | 0.01581 | 0.0090897 | -0.022463 | -0.0071777 | 0.064066 | 0.070703 | -6.4087 | 0.26093 | -123.1018 | 0.16937 | -122.525 | -123.0011 | -0.33875 | 0.041199 | 0.26093 | -123.0743 | -0.37994 | 0.082397 | 116.3132 | 122.8912 | -122.7036 | -0.35248 | 0.082397 | 116.6931 | 122.3831 | 122.7631 | 0.19684 | 122.9828 | 116.3132 | 122.9828 | -0.27924 | -0.35248 | 122.9828 | 116.3132 | -0.27924 | 0.19684 | 122.9828 | -123.2803 | -123.2529
755.2656 | 123.0423 | -122.7173 | 0.1831 | 0.0045011 | 0.018587 | 0.010158 | -0.018404 | -0.0080323 | 0.064493 | 0.066217 | -6.3904 | 0.25635 | -123.1155 | 0.16937 | -122.525 | -122.9965 | -0.35248 | 0.041199 | 0.25635 | -123.0606 | -0.39825 | 0.073243 | 116.3269 | 122.8867 | -122.7081 | -0.34332 | 0.073243 | 116.7252 | 122.3648 | 122.7585 | 0.19226 | 122.9736 | 116.3269 | 122.9736 | -0.27924 | -0.34332 | 122.9736 | 116.3269 | -0.27924 | 0.19226 | 122.9736 | -123.2986 | -123.2437
757.0312 | 122.9736 | -122.7448 | 0.21057 | 0.0045011 | 0.020937 | 0.0086625 | -0.012636 | -0.0048279 | 0.062143 | 0.069421 | -6.4041 | 0.28839 | -123.1705 | 0.11902 | -122.5845 | -123.1018 | -0.19684 | -0.022888 | 0.28839 | -123.0743 | -0.42572 | 0.07782 | 116.3406 | 122.8638 | -122.7951 | -0.32959 | 0.07782 | 116.7664 | 122.5479 | 122.7219 | 0.16022 | 123.0331 | 116.3406 | 123.0331 | -0.35706 | -0.32959 | 123.0331 | 116.3406 | -0.35706 | 0.16022 | 123.0331 | -123.381 | -123.2849
758.7656 | 122.9691 | -122.7676 | 0.19684 | -0.0031279 | 0.019442 | 0.011439 | -0.01349 | -0.0052551 | 0.061716 | 0.071771 | -6.4316 | 0.27924 | -123.1796 | 0.13275 | -122.5983 | -123.0972 | -0.16022 | -0.018311 | 0.29755 | -123.0881 | -0.41199 | 0.082398 | 116.3361 | 122.9004 | -122.7951 | -0.32044 | 0.10071 | 116.748 | 122.6074 | 122.7493 | 0.16937 | 123.0469 | 116.3361 | 123.0652 | -0.32959 | -0.32044 | 123.0469 | 116.3361 | -0.32959 | 0.16937 | 123.0652 | -123.3765 | -123.2849
760.4531 | 122.937 | -122.7722 | 0.20599 | 0.0045011 | 0.018374 | 0.010158 | -0.017549 | -0.0061097 | 0.063425 | 0.069635 | -6.4178 | 0.2655 | -123.143 | 0.16937 | -122.5296 | -123.0057 | -0.35706 | 0.073242 | 0.2655 | -123.0606 | -0.37079 | 0.059509 | 116.3544 | 122.9416 | -122.7356 | -0.28839 | 0.059509 | 116.7252 | 122.4152 | 122.8455 | 0.24262 | 123.0377 | 116.3544 | 123.0377 | -0.23346 | -0.28839 | 123.0377 | 116.3544 | -0.23346 | 0.24262 | 123.0377 | -123.349 | -123.2666
762.2031 | 123.0789 | -122.7081 | 0.16937 | 0.0045011 | 0.017306 | 0.010158 | -0.018404 | -0.0088867 | 0.062357 | 0.069848 | -6.5002 | 0.28381 | -123.1522 | 0.10529 | -122.5616 | -123.0835 | -0.14191 | 0.045776 | 0.31128 | -123.0835 | -0.44403 | 0.11444 | 116.2079 | 122.8134 | -122.731 | -0.37537 | 0.14191 | 116.6519 | 122.5662 | 122.7539 | 0.14648 | 122.9919 | 116.2079 | 123.0194 | -0.37537 | -0.37537 | 122.9919 | 116.2079 | -0.37537 | 0.14648 | 123.0194 | -123.3215 | -123.2529
763.9531 | 122.9187 | -122.7676 | 0.21973 | 0.0045011 | 0.019869 | 0.0099441 | -0.017976 | -0.0082459 | 0.065134 | 0.070703 | -6.3538 | 0.25177 | -123.111 | 0.22888 | -122.4609 | -122.9462 | -0.42114 | 0.11902 | 0.26093 | -123.0286 | -0.34332 | 0.032043 | 116.4139 | 122.9965 | -122.6807 | -0.26093 | 0.041198 | 116.7572 | 122.3465 | 122.8867 | 0.3067 | 123.0194 | 116.4139 | 123.0286 | -0.17853 | -0.26093 | 123.0194 | 116.4139 | -0.17853 | 0.3067 | 123.0286 | -123.3307 | -123.2483
765.625 | 123.024 | -122.7264 | 0.17853 | -0.0031279 | 0.017519 | 0.0084489 | -0.020754 | -0.0099549 | 0.065134 | 0.069635 | -6.4224 | 0.25177 | -123.0927 | 0.21973 | -122.4472 | -122.9645 | -0.37994 | 0.1236 | 0.25635 | -123.0652 | -0.36621 | 0.073242 | 116.304 | 122.9462 | -122.6257 | -0.33875 | 0.07782 | 116.6702 | 122.3465 | 122.85 | 0.27923 | 122.9782 | 116.304 | 122.9828 | -0.23804 | -0.33875 | 122.9782 | 116.304 | -0.23804 | 0.27923 | 122.9828 | -123.2712 | -123.2437
767.375 | 122.9187 | -122.7859 | 0.20599 | -0.0031279 | 0.019015 | 0.01443 | -0.014345 | -0.0065369 | 0.061288 | 0.070276 | -6.3858 | 0.2655 | -123.1476 | 0.16937 | -122.5204 | -123.0286 | -0.24719 | 0.11902 | 0.29297 | -123.0286 | -0.36163 | 0.059509 | 116.4001 | 122.9553 | -122.7264 | -0.24261 | 0.086975 | 116.7618 | 122.5388 | 122.905 | 0.2655 | 123.0515 | 116.4001 | 123.0789 | -0.24261 | -0.24261 | 123.0515 | 116.4001 | -0.24261 | 0.2655 | 123.0789 | -123.3536 | -123.2346
769.125 | 123.0469 | -122.7264 | 0.18768 | -0.0031279 | 0.015597 | 0.010158 | -0.018617 | -0.0071777 | 0.064066 | 0.068353 | -6.4362 | 0.22888 | -123.1338 | 0.19684 | -122.493 | -123.0011 | -0.2655 | 0.11444 | 0.27924 | -123.0789 | -0.40741 | 0.041199 | 116.2903 | 122.9233 | -122.6807 | -0.35248 | 0.091553 | 116.6977 | 122.4609 | 122.8409 | 0.23346 | 122.9553 | 116.2903 | 123.0057 | -0.27466 | -0.35248 | 122.9553 | 116.2903 | -0.27466 | 0.23346 | 123.0057 | -123.3215 | -123.2666
770.8125 | 122.9507 | -122.7493 | 0.17395 | 0.0045011 | 0.019442 | 0.0084489 | -0.013704 | -0.0067505 | 0.062784 | 0.070489 | -6.4682 | 0.29297 | -123.1476 | 0.11444 | -122.5662 | -123.0652 | -0.27466 | -0.013733 | 0.29297 | -123.0652 | -0.39825 | 0.11902 | 116.2811 | 122.8638 | -122.7402 | -0.31586 | 0.11902 | 116.6794 | 122.4747 | 122.7356 | 0.18311 | 123.0423 | 116.2811 | 123.0423 | -0.31586 | -0.31586 | 123.0423 | 116.2811 | -0.31586 | 0.18311 | 123.0423 | -123.3215 | -123.2391
772.5625 | 122.9507 | -122.7493 | 0.2243 | -0.0031279 | 0.019442 | 0.0093033 | -0.01285 | -0.0052551 | 0.063211 | 0.067498 | -6.427 | 0.27924 | -123.1338 | 0.13275 | -122.5708 | -123.0881 | -0.2243 | 0.018311 | 0.29755 | -123.0606 | -0.38452 | 0.054932 | 116.3223 | 122.8821 | -122.7951 | -0.31128 | 0.073242 | 116.7068 | 122.525 | 122.7676 | 0.17853 | 123.0286 | 116.3223 | 123.0469 | -0.33875 | -0.31128 | 123.0286 | 116.3223 | -0.33875 | 0.17853 | 123.0469 | -123.3582 | -123.2849
774.3125 | 123.024 | -122.7356 | 0.19226 | 0.0045011 | 0.017733 | 0.0093033 | -0.020967 | -0.010382 | 0.062143 | 0.069635 | -6.395 | 0.23346 | -123.0881 | 0.21515 | -122.4518 | -122.9691 | -0.32501 | 0.10529 | 0.2655 | -123.0377 | -0.35248 | 0.041198 | 116.3406 | 122.9507 | -122.644 | -0.30212 | 0.073242 | 116.6931 | 122.4106 | 122.8409 | 0.28381 | 122.9691 | 116.3406 | 123.0011 | -0.23346 | -0.30212 | 122.9691 | 116.3406 | -0.23346 | 0.28381 | 123.0011 | -123.2803 | -123.23
776 | 122.9874 | -122.7356 | 0.20142 | -0.0031279 | 0.016451 | 0.010371 | -0.021822 | -0.0078187 | 0.062997 | 0.069848 | -6.3766 | 0.23804 | -123.0698 | 0.23804 | -122.4197 | -122.9095 | -0.43945 | 0.10529 | 0.25177 | -123.0286 | -0.33417 | 0.036621 | 116.3589 | 122.9736 | -122.6212 | -0.29297 | 0.050354 | 116.6931 | 122.2961 | 122.8409 | 0.31586 | 122.9736 | 116.3589 | 122.9874 | -0.17395 | -0.29297 | 122.9736 | 116.3589 | -0.17395 | 0.31586 | 122.9874 | -123.2712 | -123.23
777.7344 | 123.0377 | -122.7585 | 0.19226 | -0.0031279 | 0.016024 | 0.0060989 | -0.020967 | -0.0073913 | 0.062997 | 0.067498 | -6.427 | 0.2655 | -123.1293 | 0.20599 | -122.493 | -122.9965 | -0.30212 | 0.041199 | 0.28381 | -123.0377 | -0.37079 | 0.073242 | 116.3315 | 122.9645 | -122.6852 | -0.27924 | 0.091552 | 116.7023 | 122.4564 | 122.7997 | 0.2655 | 123.024 | 116.3315 | 123.0423 | -0.23804 | -0.27924 | 123.024 | 116.3315 | -0.23804 | 0.2655 | 123.0423 | -123.3215 | -123.23
779.4688 | 122.9233 | -122.7676 | 0.21515 | 0.0045011 | 0.020296 | 0.011653 | -0.013277 | -0.0082459 | 0.063425 | 0.069207 | -6.4133 | 0.28381 | -123.1567 | 0.19684 | -122.5113 | -123.0331 | -0.27466 | 0.059509 | 0.27008 | -123.0743 | -0.3891 | 0.068664 | 116.3544 | 122.9645 | -122.7264 | -0.3067 | 0.054932 | 116.7435 | 122.493 | 122.8271 | 0.25635 | 123.0515 | 116.3544 | 123.0377 | -0.2655 | -0.3067 | 123.0515 | 116.3544 | -0.2655 | 0.25635 | 123.0377 | -123.3719 | -123.2895
781.2188 | 122.9416 | -122.7631 | 0.23346 | 0.0045011 | 0.017947 | 0.011012 | -0.013918 | -0.0058961 | 0.061716 | 0.070276 | -6.4545 | 0.27466 | -123.1476 | 0.11902 | -122.5616 | -123.0789 | -0.28381 | -0.009155 | 0.28839 | -123.0698 | -0.38452 | 0.041199 | 116.3086 | 122.8821 | -122.7951 | -0.3067 | 0.054932 | 116.6931 | 122.4792 | 122.7539 | 0.20142 | 123.0377 | 116.3086 | 123.0515 | -0.31586 | -0.3067 | 123.0377 | 116.3086 | -0.31586 | 0.20142 | 123.0515 | -123.381 | -123.3032
782.9688 | 122.9919 | -122.7264 | 0.17853 | -0.0031279 | 0.016451 | 0.0088761 | -0.021822 | -0.0078187 | 0.06492 | 0.07113 | -6.4407 | 0.24261 | -123.1018 | 0.22888 | -122.4197 | -122.937 | -0.48065 | 0.10986 | 0.27008 | -123.0515 | -0.37537 | 0.064087 | 116.2857 | 122.9553 | -122.5983 | -0.32501 | 0.091553 | 116.6611 | 122.2458 | 122.8363 | 0.3067 | 122.9691 | 116.2857 | 122.9965 | -0.21057 | -0.32501 | 122.9691 | 116.2857 | -0.21057 | 0.3067 | 122.9965 | -123.2803 | -123.23
784.6406 | 122.9507 | -122.7448 | 0.21057 | -0.0031279 | 0.016878 | 0.0093033 | -0.015199 | -0.0080323 | 0.062997 | 0.070489 | -6.4362 | 0.2655 | -123.0743 | 0.20599 | -122.493 | -122.9736 | -0.47607 | 0.032043 | 0.24719 | -123.0515 | -0.32959 | 0.054932 | 116.3086 | 122.9507 | -122.7036 | -0.3067 | 0.036621 | 116.6382 | 122.2687 | 122.7768 | 0.25177 | 123.0103 | 116.3086 | 122.9919 | -0.22888 | -0.3067 | 123.0103 | 116.3086 | -0.22888 | 0.25177 | 122.9919 | -123.2849 | -123.262
786.4062 | 122.9553 | -122.7219 | 0.21057 | 0.0045011 | 0.019228 | 0.012721 | -0.012636 | -0.0067505 | 0.062357 | 0.070489 | -6.4957 | 0.27008 | -123.1659 | 0.086975 | -122.5845 | -123.1064 | -0.27924 | -0.041199 | 0.31128 | -123.0743 | -0.44403 | 0.05951 | 116.2262 | 122.8088 | -122.7951 | -0.35248 | 0.10071 | 116.6702 | 122.4426 | 122.6807 | 0.13733 | 122.9919 | 116.2262 | 123.0331 | -0.38452 | -0.35248 | 122.9919 | 116.2262 | -0.38452 | 0.13733 | 123.0331 | -123.3765 | -123.2849
788.0938 | 122.9965 | -122.7173 | 0.19226 | 0.012131 | 0.01581 | 0.0075943 | -0.020113 | -0.0086731 | 0.065347 | 0.070916 | -6.4407 | 0.24719 | -123.0927 | 0.26093 | -122.4335 | -122.9279 | -0.48523 | 0.068665 | 0.25635 | -123.0423 | -0.37537 | 0.054931 | 116.2766 | 122.9782 | -122.6257 | -0.32501 | 0.064087 | 116.6519 | 122.2321 | 122.7859 | 0.28381 | 122.9645 | 116.2766 | 122.9736 | -0.21057 | -0.32501 | 122.9645 | 116.2766 | -0.21057 | 0.28381 | 122.9736 | -123.2849 | -123.2346
789.8438 | 122.9736 | -122.731 | 0.18768 | 0.0045011 | 0.01816 | 0.0090897 | -0.020326 | -0.0095277 | 0.063425 | 0.068567 | -6.4545 | 0.24719 | -123.1018 | 0.25177 | -122.438 | -122.9462 | -0.43488 | 0.041199 | 0.27008 | -123.056 | -0.37079 | 0.059509 | 116.2766 | 122.9828 | -122.6257 | -0.32501 | 0.082398 | 116.6473 | 122.2961 | 122.7722 | 0.29297 | 122.9782 | 116.2766 | 123.0011 | -0.21515 | -0.32501 | 122.9782 | 116.2766 | -0.21515 | 0.29297 | 123.0011 | -123.2895 | -123.2437
791.5781 | 122.9187 | -122.7539 | 0.20142 | 0.012131 | 0.015597 | 0.010585 | -0.012422 | -0.0067505 | 0.060434 | 0.068353 | -6.4545 | 0.27466 | -123.1384 | 0.18768 | -122.5021 | -123.024 | -0.32959 | 0.036621 | 0.28381 | -123.0194 | -0.38452 | 0.073242 | 116.2994 | 122.9416 | -122.7036 | -0.2655 | 0.082397 | 116.684 | 122.4243 | 122.7905 | 0.25177 | 123.0286 | 116.2994 | 123.0377 | -0.27008 | -0.2655 | 123.0286 | 116.2994 | -0.27008 | 0.25177 | 123.0377 | -123.3398 | -123.2208
793.2812 | 123.056 | -122.7173 | 0.18768 | -0.018387 | 0.019656 | 0.0097305 | -0.019899 | -0.0039735 | 0.060861 | 0.068353 | -6.4865 | 0.28839 | -123.0972 | 0.14648 | -122.5113 | -123.0423 | -0.28839 | -0.018311 | 0.30212 | -123.0606 | -0.37994 | 0.10071 | 116.2308 | 122.8638 | -122.699 | -0.34332 | 0.11444 | 116.6107 | 122.4289 | 122.699 | 0.20599 | 123.0057 | 116.2308 | 123.0194 | -0.32501 | -0.34332 | 123.0057 | 116.2308 | -0.32501 | 0.20599 | 123.0194 | -123.2849 | -123.2483
795.0156 | 122.9187 | -122.7493 | 0.19684 | 0.0045011 | 0.018374 | 0.0097305 | -0.018831 | -0.0073913 | 0.064279 | 0.070062 | -6.4453 | 0.26093 | -123.0835 | 0.21057 | -122.4747 | -122.9645 | -0.54016 | -0.013733 | 0.2655 | -123.056 | -0.33417 | 0.064087 | 116.304 | 122.9599 | -122.6715 | -0.3067 | 0.068665 | 116.6382 | 122.2092 | 122.7356 | 0.27466 | 123.0103 | 116.304 | 123.0148 | -0.21515 | -0.3067 | 123.0103 | 116.304 | -0.21515 | 0.27466 | 123.0148 | -123.2803 | -123.2529
796.7656 | 122.9874 | -122.7219 | 0.19226 | -0.0031279 | 0.01581 | 0.0050309 | -0.019258 | -0.0071777 | 0.064706 | 0.071344 | -6.4728 | 0.25177 | -123.0881 | 0.25177 | -122.4197 | -122.9279 | -0.52185 | 0.064087 | 0.26093 | -123.0057 | -0.36621 | 0.059509 | 116.2491 | 122.9736 | -122.612 | -0.28381 | 0.068664 | 116.6153 | 122.2 | 122.7859 | 0.30212 | 122.9736 | 116.2491 | 122.9828 | -0.20599 | -0.28381 | 122.9736 | 116.2491 | -0.20599 | 0.30212 | 122.9828 | -123.2803 | -123.1979
798.5312 | 122.9645 | -122.7127 | 0.19226 | 0.0045011 | 0.016665 | 0.010799 | -0.013277 | -0.0058961 | 0.063852 | 0.070703 | -6.514 | 0.27466 | -123.1567 | 0.1236 | -122.5571 | -123.0606 | -0.35248 | -0.10071 | 0.30212 | -123.0469 | -0.44403 | 0.082397 | 116.1987 | 122.8363 | -122.7493 | -0.33417 | 0.10986 | 116.6428 | 122.3602 | 122.612 | 0.15564 | 122.9874 | 116.1987 | 123.0148 | -0.3479 | -0.33417 | 122.9874 | 116.1987 | -0.3479 | 0.15564 | 123.0148 | -123.349 | -123.2391
800.2188 | 122.9507 | -122.7264 | 0.20599 | 0.0045011 | 0.020296 | 0.011226 | -0.015199 | -0.0056823 | 0.061075 | 0.071985 | -6.5414 | 0.28839 | -123.1567 | 0.10986 | -122.5845 | -123.0927 | -0.32044 | -0.11444 | 0.3067 | -123.0423 | -0.4303 | 0.082397 | 116.185 | 122.8363 | -122.7905 | -0.31586 | 0.10071 | 116.6153 | 122.406 | 122.612 | 0.14191 | 123.0148 | 116.185 | 123.0331 | -0.36621 | -0.31586 | 123.0148 | 116.185 | -0.36621 | 0.14191 | 123.0331 | -123.3627 | -123.2483
801.9531 | 122.9828 | -122.6944 | 0.19684 | 0.0045011 | 0.018801 | 0.0090897 | -0.01819 | -0.0073913 | 0.064493 | 0.069421 | -6.4545 | 0.2655 | -123.0698 | 0.24261 | -122.3923 | -122.9095 | -0.52185 | 0.068665 | 0.24261 | -123.0148 | -0.37537 | 0.068665 | 116.2399 | 122.937 | -122.5891 | -0.32044 | 0.045777 | 116.6153 | 122.1725 | 122.7631 | 0.30212 | 122.9599 | 116.2399 | 122.937 | -0.21515 | -0.32044 | 122.9599 | 116.2399 | -0.21515 | 0.30212 | 122.937 | -123.2666 | -123.2117
803.6406 | 122.8958 | -122.7539 | 0.21515 | 0.012131 | 0.017733 | 0.011439 | -0.011781 | -0.0056823 | 0.061929 | 0.07113 | -6.459 | 0.2655 | -123.1567 | 0.17853 | -122.5067 | -123.024 | -0.37079 | -0.022888 | 0.28381 | -123.0469 | -0.40283 | 0.050354 | 116.2949 | 122.9324 | -122.7219 | -0.29297 | 0.068664 | 116.6977 | 122.3831 | 122.731 | 0.24719 | 123.0194 | 116.2949 | 123.0377 | -0.27008 | -0.29297 | 123.0194 | 116.2949 | -0.27008 | 0.24719 | 123.0377 | -123.3719 | -123.262
805.3906 | 122.9095 | -122.7127 | 0.21057 | -0.010757 | 0.021365 | 0.010585 | -0.016054 | -0.0026917 | 0.065134 | 0.068139 | -6.4819 | 0.28381 | -123.1018 | 0.18768 | -122.4747 | -122.9645 | -0.50812 | -0.050354 | 0.27924 | -123.0011 | -0.3891 | 0.073242 | 116.2308 | 122.9004 | -122.6852 | -0.28839 | 0.068665 | 116.6199 | 122.2046 | 122.6624 | 0.23804 | 122.9965 | 116.2308 | 122.9919 | -0.25177 | -0.28839 | 122.9965 | 116.2308 | -0.25177 | 0.23804 | 122.9919 | -123.3124 | -123.2117
807.1562 | 123.0103 | -122.7081 | 0.17853 | 0.012131 | 0.018374 | 0.0056717 | -0.017336 | -0.0073913 | 0.064066 | 0.070703 | -6.5369 | 0.3067 | -123.143 | 0.1236 | -122.5296 | -123.0652 | -0.29297 | -0.10071 | 0.31128 | -123.0743 | -0.43488 | 0.12817 | 116.1713 | 122.8317 | -122.7081 | -0.36621 | 0.13275 | 116.6061 | 122.4152 | 122.6074 | 0.17853 | 123.0148 | 116.1713 | 123.0194 | -0.35706 | -0.36621 | 123.0148 | 116.1713 | -0.35706 | 0.17853 | 123.0194 | -123.3215 | -123.2529
808.8281 | 122.9416 | -122.7539 | 0.21057 | 0.0045011 | 0.018587 | 0.0099441 | -0.013277 | -0.0063233 | 0.06257 | 0.071557 | -6.5231 | 0.26093 | -123.1705 | 0.1236 | -122.5388 | -123.0743 | -0.32044 | -0.14648 | 0.28839 | -123.0331 | -0.41657 | 0.050354 | 116.2308 | 122.8775 | -122.7493 | -0.27924 | 0.07782 | 116.6473 | 122.4335 | 122.6074 | 0.21515 | 123.0148 | 116.2308 | 123.0423 | -0.32044 | -0.27924 | 123.0148 | 116.2308 | -0.32044 | 0.21515 | 123.0423 | -123.381 | -123.2437
810.5625 | 122.9279 | -122.7402 | 0.21515 | -0.010757 | 0.01816 | 0.01678 | -0.016695 | -0.0056823 | 0.062997 | 0.069848 | -6.5002 | 0.27466 | -123.1293 | 0.16937 | -122.5021 | -123.0194 | -0.33417 | -0.064087 | 0.29755 | -123.056 | -0.3891 | 0.059509 | 116.2399 | 122.9095 | -122.7173 | -0.31586 | 0.082397 | 116.629 | 122.406 | 122.6761 | 0.23804 | 123.0148 | 116.2399 | 123.0377 | -0.27924 | -0.31586 | 123.0148 | 116.2399 | -0.27924 | 0.23804 | 123.0377 | -123.3444 | -123.2712
812.3125 | 122.905 | -122.7585 | 0.1831 | 0.012131 | 0.016878 | 0.011226 | -0.018404 | -0.0056823 | 0.064493 | 0.072198 | -6.459 | 0.22888 | -123.0698 | 0.23346 | -122.4335 | -122.9187 | -0.58594 | -0.091553 | 0.23346 | -123.0377 | -0.31128 | 0.045777 | 116.2994 | 122.9919 | -122.6166 | -0.27924 | 0.050354 | 116.6107 | 122.1725 | 122.6669 | 0.32501 | 122.9874 | 116.2994 | 122.9919 | -0.16022 | -0.27924 | 122.9874 | 116.2994 | -0.16022 | 0.32501 | 122.9919 | -123.2529 | -123.2208
814.0625 | 123.0148 | -122.7219 | 0.17395 | 0.012131 | 0.017092 | 0.0067399 | -0.019258 | -0.0080323 | 0.065347 | 0.070916 | -6.5598 | 0.25177 | -123.0743 | 0.16022 | -122.4747 | -122.9645 | -0.5127 | -0.1831 | 0.25177 | -123.0515 | -0.35248 | 0.07782 | 116.1621 | 122.8821 | -122.6486 | -0.32959 | 0.07782 | 116.5146 | 122.2092 | 122.5388 | 0.24719 | 122.9736 | 116.1621 | 122.9736 | -0.24262 | -0.32959 | 122.9736 | 116.1621 | -0.24262 | 0.24719 | 122.9736 | -123.2483 | -123.2254
815.75 | 123.0286 | -122.7036 | 0.17853 | -0.0031279 | 0.016665 | 0.0093033 | -0.015413 | -0.0071777 | 0.063852 | 0.070062 | -6.5964 | 0.27466 | -123.1522 | 0.11902 | -122.5388 | -123.0743 | -0.27924 | -0.24719 | 0.30212 | -123.0606 | -0.44861 | 0.09613 | 116.1072 | 122.8226 | -122.7173 | -0.35706 | 0.1236 | 116.5558 | 122.4243 | 122.4564 | 0.16479 | 122.9782 | 116.1072 | 123.0057 | -0.37079 | -0.35706 | 122.9782 | 116.1072 | -0.37079 | 0.16479 | 123.0057 | -123.3307 | -123.2391
817.5 | 122.9279 | -122.7402 | 0.21973 | -0.010757 | 0.020937 | 0.0086625 | -0.014986 | -0.0037597 | 0.062997 | 0.071985 | -6.5598 | 0.27466 | -123.1476 | 0.10529 | -122.5388 | -123.024 | -0.41199 | -0.32959 | 0.27466 | -123.024 | -0.40741 | 0.054931 | 116.1804 | 122.8455 | -122.7585 | -0.28381 | 0.054931 | 116.5878 | 122.3282 | 122.4106 | 0.20142 | 123.0148 | 116.1804 | 123.0148 | -0.28381 | -0.28381 | 123.0148 | 116.1804 | -0.28381 | 0.20142 | 123.0148 | -123.3673 | -123.2437
819.25 | 122.9828 | -122.7219 | 0.20142 | 0.0045011 | 0.016878 | 0.0093033 | -0.02054 | -0.0069641 | 0.06492 | 0.070489 | -6.4774 | 0.23804 | -123.0743 | 0.23804 | -122.4243 | -122.905 | -0.56305 | -0.22888 | 0.22888 | -123.0286 | -0.35248 | 0.036621 | 116.2445 | 122.9599 | -122.6257 | -0.3067 | 0.027466 | 116.597 | 122.1588 | 122.493 | 0.29755 | 122.9599 | 116.2445 | 122.9507 | -0.1831 | -0.3067 | 122.9599 | 116.2445 | -0.1831 | 0.29755 | 122.9507 | -123.2758 | -123.23
820.9375 | 122.9095 | -122.7585 | 0.22888 | 0.0045011 | 0.018801 | 0.0099441 | -0.012209 | -0.0073913 | 0.06257 | 0.068139 | -6.5186 | 0.2655 | -123.1796 | 0.14191 | -122.5433 | -123.0469 | -0.36163 | -0.39825 | 0.27924 | -123.056 | -0.42114 | 0.036621 | 116.2399 | 122.9004 | -122.7722 | -0.29755 | 0.050354 | 116.6611 | 122.3969 | 122.3602 | 0.21515 | 123.024 | 116.2399 | 123.0377 | -0.28839 | -0.29755 | 123.024 | 116.2399 | -0.28839 | 0.21515 | 123.0377 | -123.4085 | -123.2849
822.6875 | 123.0057 | -122.6944 | 0.17395 | 0.0045011 | 0.017092 | 0.012935 | -0.019472 | -0.0063233 | 0.063425 | 0.069635 | -6.5323 | 0.25177 | -123.1293 | 0.16022 | -122.4655 | -122.9828 | -0.42114 | -0.3891 | 0.28839 | -123.0927 | -0.43488 | 0.07782 | 116.1621 | 122.8546 | -122.6395 | -0.39825 | 0.11444 | 116.597 | 122.2733 | 122.3053 | 0.22888 | 122.9462 | 116.1621 | 122.9828 | -0.28839 | -0.39825 | 122.9462 | 116.1621 | -0.28839 | 0.22888 | 122.9828 | -123.3032 | -123.2666
824.4375 | 123.0377 | -122.6852 | 0.16937 | -0.0031279 | 0.01581 | 0.0065263 | -0.018831 | -0.0076049 | 0.064279 | 0.069848 | -6.6147 | 0.26093 | -123.143 | 0.11444 | -122.5342 | -123.0515 | -0.33875 | -0.4715 | 0.3067 | -123.0515 | -0.45776 | 0.091552 | 116.0706 | 122.7997 | -122.7036 | -0.36621 | 0.13733 | 116.5283 | 122.3465 | 122.2137 | 0.15106 | 122.9462 | 116.0706 | 122.9919 | -0.36621 | -0.36621 | 122.9462 | 116.0706 | -0.36621 | 0.15106 | 122.9919 | -123.3124 | -123.2208
826.125 | 122.9553 | -122.7127 | 0.20142 | -0.0031279 | 0.017733 | 0.011653 | -0.014986 | -0.0073913 | 0.061075 | 0.067498 | -6.6193 | 0.27924 | -123.143 | 0.09613 | -122.5616 | -123.0652 | -0.3479 | -0.59509 | 0.28839 | -123.0652 | -0.4303 | 0.07782 | 116.0934 | 122.8088 | -122.7631 | -0.35248 | 0.086975 | 116.5237 | 122.3648 | 122.1176 | 0.15106 | 122.9919 | 116.0934 | 123.0011 | -0.35248 | -0.35248 | 122.9919 | 116.0934 | -0.35248 | 0.15106 | 123.0011 | -123.3444 | -123.2666
827.8906 | 122.8363 | -122.7768 | 0.21973 | 0.0045011 | 0.019656 | 0.011653 | -0.016054 | -0.0048279 | 0.061716 | 0.071557 | -6.6101 | 0.27924 | -123.0881 | 0.091553 | -122.5204 | -123.0148 | -0.32959 | -0.50354 | 0.29297 | -123.0011 | -0.31128 | 0.059509 | 116.1667 | 122.8683 | -122.7402 | -0.22431 | 0.073242 | 116.478 | 122.4472 | 122.2733 | 0.25635 | 123.056 | 116.1667 | 123.0698 | -0.23804 | -0.22431 | 123.056 | 116.1667 | -0.23804 | 0.25635 | 123.0698 | -123.3078 | -123.2208
829.5781 | 122.8317 | -122.7448 | 0.21057 | 0.0045011 | 0.016665 | 0.010371 | -0.020754 | -0.0067505 | 0.063852 | 0.071344 | -6.5231 | 0.2243 | -123.0286 | 0.19684 | -122.4152 | -122.9141 | -0.55389 | -0.27924 | 0.25177 | -123.0286 | -0.28381 | 0.013733 | 116.2216 | 122.9416 | -122.6257 | -0.28381 | 0.041199 | 116.5054 | 122.1909 | 122.4655 | 0.32959 | 122.9691 | 116.2216 | 122.9965 | -0.16937 | -0.28381 | 122.9691 | 116.2216 | -0.16937 | 0.32959 | 122.9965 | -123.2391 | -123.2391
831.3281 | 122.9645 | -122.6944 | 0.16022 | 0.0045011 | 0.016665 | 0.010371 | -0.017763 | -0.0065369 | 0.061716 | 0.069207 | -6.5826 | 0.27008 | -123.0743 | 0.13275 | -122.4792 | -123.024 | -0.35706 | -0.31128 | 0.28839 | -123.0469 | -0.37994 | 0.10986 | 116.1118 | 122.8271 | -122.6395 | -0.35248 | 0.12817 | 116.4917 | 122.3373 | 122.3831 | 0.21515 | 122.9645 | 116.1118 | 122.9828 | -0.32959 | -0.35248 | 122.9645 | 116.1118 | -0.32959 | 0.21515 | 122.9828 | -123.2346 | -123.2071
833.0625 | 122.85 | -122.7173 | 0.23346 | 0.012131 | 0.017306 | 0.0090897 | -0.013063 | -0.0061097 | 0.062997 | 0.07113 | -6.5826 | 0.27466 | -123.111 | 0.15106 | -122.4838 | -123.024 | -0.3891 | -0.27466 | 0.27466 | -123.024 | -0.39368 | 0.041199 | 116.1346 | 122.8683 | -122.7173 | -0.3067 | 0.041199 | 116.5283 | 122.3282 | 122.4426 | 0.23346 | 122.9919 | 116.1346 | 122.9919 | -0.3067 | -0.3067 | 122.9919 | 116.1346 | -0.3067 | 0.23346 | 122.9919 | -123.3444 | -123.2574
834.7344 | 122.85 | -122.7264 | 0.21515 | -0.0031279 | 0.015383 | 0.0084489 | -0.016908 | -0.0067505 | 0.060434 | 0.070276 | -6.5689 | 0.21973 | -123.0606 | 0.21515 | -122.4335 | -122.9004 | -0.6546 | -0.23346 | 0.23804 | -122.9828 | -0.33417 | 0.004578 | 116.1575 | 122.9416 | -122.6486 | -0.25635 | 0.022888 | 116.4917 | 122.0718 | 122.493 | 0.29297 | 122.9462 | 116.1575 | 122.9645 | -0.17395 | -0.25635 | 122.9462 | 116.1575 | -0.17395 | 0.29297 | 122.9645 | -123.2758 | -123.1979
836.4844 | 122.9279 | -122.6898 | 0.20599 | -0.0031279 | 0.018801 | 0.011653 | -0.013277 | -0.0084595 | 0.061502 | 0.068567 | -6.6879 | 0.28381 | -123.1201 | 0.16479 | -122.493 | -123.0011 | -0.44861 | -0.29755 | 0.27466 | -123.0286 | -0.4303 | 0.077819 | 116.0019 | 122.8546 | -122.699 | -0.33875 | 0.068664 | 116.4322 | 122.2412 | 122.3923 | 0.19684 | 122.9736 | 116.0019 | 122.9645 | -0.31128 | -0.33875 | 122.9736 | 116.0019 | -0.31128 | 0.19684 | 122.9645 | -123.3261 | -123.2346
838.25 | 123.0148 | -122.6578 | 0.17853 | 0.0045011 | 0.01581 | 0.010585 | -0.019685 | -0.0082459 | 0.062357 | 0.06878 | -6.7612 | 0.27466 | -123.1155 | 0.11444 | -122.5204 | -123.0423 | -0.44861 | -0.33875 | 0.27924 | -123.0423 | -0.45776 | 0.09613 | 115.8966 | 122.7722 | -122.699 | -0.38452 | 0.10071 | 116.3544 | 122.2092 | 122.319 | 0.13733 | 122.9324 | 115.8966 | 122.937 | -0.38452 | -0.38452 | 122.9324 | 115.8966 | -0.38452 | 0.13733 | 122.937 | -123.2941 | -123.2208
839.9375 | 122.8775 | -122.6807 | 0.20599 | 0.0045011 | 0.018374 | 0.0086625 | -0.019258 | -0.0065369 | 0.062784 | 0.070062 | -6.7062 | 0.23346 | -123.0835 | 0.21973 | -122.4106 | -122.9141 | -0.75989 | -0.31128 | 0.24719 | -123.0194 | -0.40283 | 0.027465 | 115.9744 | 122.9004 | -122.6166 | -0.33875 | 0.041198 | 116.3773 | 121.9208 | 122.3694 | 0.27008 | 122.9141 | 115.9744 | 122.9279 | -0.23346 | -0.33875 | 122.9141 | 115.9744 | -0.23346 | 0.27008 | 122.9279 | -123.2895 | -123.2254
841.6719 | 122.9874 | -122.6898 | 0.15564 | 0.012131 | 0.016024 | 0.0078079 | -0.018404 | -0.0099549 | 0.065775 | 0.067712 | -6.8527 | 0.24261 | -123.0606 | 0.17853 | -122.4609 | -122.9416 | -0.66376 | -0.37537 | 0.25635 | -123.024 | -0.37079 | 0.086975 | 115.8371 | 122.8683 | -122.6166 | -0.33417 | 0.10071 | 116.2079 | 122.0261 | 122.3145 | 0.22888 | 122.9324 | 115.8371 | 122.9462 | -0.25177 | -0.33417 | 122.9324 | 115.8371 | -0.25177 | 0.22888 | 122.9462 | -123.2162 | -123.1796
843.4219 | 122.9233 | -122.699 | 0.21057 | 0.012131 | 0.01816 | 0.013362 | -0.011781 | -0.0088867 | 0.064066 | 0.069421 | -6.8115 | 0.28381 | -123.1384 | 0.082397 | -122.5662 | -123.0652 | -0.53101 | -0.48981 | 0.29297 | -123.0423 | -0.43945 | 0.073242 | 115.8875 | 122.7814 | -122.7768 | -0.34332 | 0.082398 | 116.3269 | 122.168 | 122.2092 | 0.13275 | 122.9828 | 115.8875 | 122.9919 | -0.36621 | -0.34332 | 122.9828 | 115.8875 | -0.36621 | 0.13275 | 122.9919 | -123.349 | -123.2529
845.1094 | 122.9462 | -122.6761 | 0.19226 | -0.010757 | 0.017519 | 0.0088761 | -0.020754 | -0.0067505 | 0.064706 | 0.069635 | -6.7291 | 0.25635 | -123.0743 | 0.23804 | -122.4106 | -122.9004 | -0.737 | -0.32501 | 0.25635 | -123.0377 | -0.39826 | 0.064087 | 115.947 | 122.9141 | -122.6028 | -0.36163 | 0.064087 | 116.3452 | 121.9391 | 122.3511 | 0.2655 | 122.9324 | 115.947 | 122.9324 | -0.22431 | -0.36163 | 122.9324 | 115.947 | -0.22431 | 0.2655 | 122.9324 | -123.2666 | -123.23
846.8438 | 123.0057 | -122.6898 | 0.17395 | 0.0045011 | 0.02051 | 0.0095169 | -0.014345 | -0.0082459 | 0.064493 | 0.06878 | -6.8893 | 0.28381 | -123.1201 | 0.10986 | -122.5159 | -123.0515 | -0.58594 | -0.46234 | 0.28839 | -123.0606 | -0.4303 | 0.10986 | 115.8005 | 122.7997 | -122.6898 | -0.37079 | 0.11444 | 116.2308 | 122.1039 | 122.2275 | 0.17395 | 122.9736 | 115.8005 | 122.9782 | -0.36163 | -0.37079 | 122.9736 | 115.8005 | -0.36163 | 0.17395 | 122.9782 | -123.2941 | -123.2346
848.5312 | 122.8683 | -122.731 | 0.18768 | 0.012131 | 0.014956 | 0.012721 | -0.01584 | -0.0035461 | 0.063211 | 0.070703 | -6.839 | 0.25177 | -123.0835 | 0.20599 | -122.4197 | -122.9233 | -0.86975 | -0.4303 | 0.24719 | -123.024 | -0.35248 | 0.064087 | 115.892 | 122.937 | -122.6074 | -0.29297 | 0.059509 | 116.2445 | 121.8613 | 122.3007 | 0.31128 | 122.9828 | 115.892 | 122.9782 | -0.19226 | -0.29297 | 122.9828 | 115.892 | -0.19226 | 0.31128 | 122.9782 | -123.2712 | -123.2117
850.2656 | 122.8546 | -122.6944 | 0.20142 | 0.0045011 | 0.015169 | 0.0080215 | -0.0072953 | 0.059473 | -0.0040802 | 0.079889 | -122.5662 | 0.21515 | -123.0286 | -122.4792 | 0.073242 | 0.20599 | -2.5726 | -0.70496 | 0.23804 | -122.9736 | -0.33417 | 0.013733 | 0.12817 | 0.21515 | -0.12817 | -0.27924 | 0.036621 | 0.46234 | 120.1218 | 121.9894 | 122.7676 | 122.9095 | 0.12817 | 122.9324 | 122.9004 | -0.27924 | 122.9095 | 0.12817 | 122.9004 | 122.7676 | 122.9324 | -123.23 | -123.175
851.9531 | 123.0331 | -122.6532 | 0.1831 | -0.0031279 | 0.016451 | 0.0082351 | -0.0060135 | 0.059259 | -0.005362 | 0.079675 | -122.6944 | 0.25177 | -123.1155 | -122.6074 | -0.009155 | 0.064087 | -2.2522 | -0.76904 | 0.29755 | -123.0423 | -0.46234 | 0.068665 | -0.041199 | 0.045776 | -0.19226 | -0.3891 | 0.11444 | 0.42114 | 120.401 | 121.8842 | 122.644 | 122.905 | -0.041199 | 122.9507 | 122.7173 | -0.3891 | 122.905 | -0.041199 | 122.7173 | 122.644 | 122.9507 | -123.2986 | -123.2254
853.7031 | 122.9599 | -122.6852 | 0.1831 | -0.010757 | 0.016451 | 0.010158 | -0.0083633 | 0.057764 | -0.0057892 | 0.079675 | -122.5891 | 0.21973 | -123.0606 | -122.4792 | 0.11444 | 0.19684 | -2.5681 | -0.75073 | 0.27008 | -123.024 | -0.37537 | 0.036622 | 0.096131 | 0.20599 | -0.068664 | -0.33875 | 0.086976 | 0.4715 | 120.1172 | 121.9345 | 122.7997 | 122.905 | 0.096131 | 122.9553 | 122.8821 | -0.33875 | 122.905 | 0.096131 | 122.8821 | 122.7997 | 122.9553 | -123.2437 | -123.2071
855.4531 | 122.9599 | -122.7036 | 0.15106 | 0.0045011 | 0.015169 | 0.0086625 | -0.0085769 | 0.058405 | -0.003653 | 0.079675 | -122.6074 | 0.21057 | -123.0606 | -122.493 | 0.10529 | 0.19226 | -2.5131 | -0.62714 | 0.25177 | -123.0194 | -0.35706 | 0.059509 | 0.09613 | 0.21057 | -0.045776 | -0.31586 | 0.10071 | 0.45319 | 120.1904 | 122.0764 | 122.8088 | 122.9141 | 0.09613 | 122.9553 | 122.8958 | -0.31586 | 122.9141 | 0.09613 | 122.8958 | 122.8088 | 122.9553 | -123.2117 | -123.1705
857.2031 | 122.8729 | -122.699 | 0.21057 | 0.0045011 | 0.015597 | 0.0060989 | -0.0025955 | 0.061182 | -0.0066438 | 0.080743 | -122.6212 | 0.20142 | -123.0927 | -122.5296 | 0.068665 | 0.15564 | -2.742 | -0.60883 | 0.25177 | -122.9828 | -0.39368 | -0.009155 | 0.07782 | 0.16937 | -0.14191 | -0.28381 | 0.041199 | 0.4715 | 119.957 | 122.0901 | 122.7676 | 122.9004 | 0.07782 | 122.9507 | 122.8546 | -0.28381 | 122.9004 | 0.07782 | 122.8546 | 122.7676 | 122.9507 | -123.3032 | -123.1934
858.875 | 122.9553 | -122.6898 | 0.17395 | 0.012131 | 0.017733 | 0.010158 | -0.0081497 | 0.058405 | -0.0042938 | 0.076043 | -122.58 | 0.19226 | -123.0469 | -122.4838 | 0.11444 | 0.19684 | -2.6459 | -0.38452 | 0.23346 | -123.024 | -0.35706 | 0.018311 | 0.10986 | 0.20599 | -0.059509 | -0.33417 | 0.059509 | 0.46692 | 120.0439 | 122.3053 | 122.8043 | 122.8821 | 0.10986 | 122.9233 | 122.8867 | -0.33417 | 122.8821 | 0.10986 | 122.8867 | 122.8043 | 122.9233 | -123.2208 | -123.1979
860.6094 | 122.9507 | -122.6669 | 0.17853 | 0.0045011 | 0.016451 | 0.0052445 | -0.0075089 | 0.058618 | -0.003653 | 0.080102 | -122.5708 | 0.20142 | -123.0743 | -122.4609 | 0.11902 | 0.21515 | -2.4857 | -0.50812 | 0.24719 | -123.0148 | -0.40741 | 0.022888 | 0.09613 | 0.20599 | -0.059509 | -0.3479 | 0.068664 | 0.50354 | 120.1813 | 122.1588 | 122.7859 | 122.8683 | 0.09613 | 122.9141 | 122.8821 | -0.3479 | 122.8683 | 0.09613 | 122.8821 | 122.7859 | 122.9141 | -123.2529 | -123.1934
862.2969 | 122.8226 | -122.7127 | 0.21973 | -0.0031279 | 0.018374 | 0.015071 | -0.0034499 | 0.060541 | -0.0049348 | 0.082452 | -122.58 | 0.18768 | -123.0835 | -122.5021 | 0.10071 | 0.21057 | -2.417 | -0.85144 | 0.26093 | -122.9919 | -0.37079 | -0.032044 | 0.13275 | 0.21057 | -0.11902 | -0.27923 | 0.041198 | 0.50354 | 120.2957 | 121.8613 | 122.8134 | 122.9004 | 0.13275 | 122.9736 | 122.9233 | -0.27923 | 122.9004 | 0.13275 | 122.9233 | 122.8134 | 122.9736 | -123.3032 | -123.2117
864.0469 | 123.0331 | -122.6761 | 0.17395 | 0.0045011 | 0.019015 | 0.0078079 | -0.0040909 | 0.061395 | -0.0072846 | 0.080743 | -122.6944 | 0.24719 | -123.1155 | -122.6212 | 0.004578 | 0.059509 | -2.417 | -0.98877 | 0.3067 | -123.056 | -0.43945 | 0.073242 | -0.018311 | 0.054931 | -0.16937 | -0.37994 | 0.13275 | 0.42114 | 120.2591 | 121.6873 | 122.6807 | 122.9233 | -0.018311 | 122.9828 | 122.7356 | -0.37994 | 122.9233 | -0.018311 | 122.7356 | 122.6807 | 122.9828 | -123.2895 | -123.23
865.7188 | 122.8683 | -122.699 | 0.20599 | 0.0045011 | 0.016665 | 0.0097305 | -0.0075089 | 0.06225 | -0.0072846 | 0.080316 | -122.5845 | 0.19226 | -123.0881 | -122.5159 | 0.11902 | 0.19684 | -2.9251 | -0.89264 | 0.23804 | -122.9965 | -0.3891 | -0.013733 | 0.11444 | 0.18311 | -0.086975 | -0.29755 | 0.032043 | 0.50354 | 119.7739 | 121.8063 | 122.818 | 122.8912 | 0.11444 | 122.937 | 122.8958 | -0.29755 | 122.8912 | 0.11444 | 122.8958 | 122.818 | 122.937 | -123.2941 | -123.2025
867.4688 | 122.8867 | -122.7173 | 0.21057 | 0.0045011 | 0.01346 | 0.0097305 | -0.0072953 | 0.060541 | -0.0062164 | 0.082025 | -122.612 | 0.19684 | -123.0698 | -122.5479 | 0.10071 | 0.19226 | -3.1769 | -1.0666 | 0.24261 | -122.9965 | -0.35248 | -0.013733 | 0.10529 | 0.16937 | -0.10986 | -0.27924 | 0.032044 | 0.45776 | 119.5404 | 121.6507 | 122.818 | 122.9141 | 0.10529 | 122.9599 | 122.9095 | -0.27924 | 122.9141 | 0.10529 | 122.9095 | 122.818 | 122.9599 | -123.2803 | -123.2071
869.1562 | 122.9965 | -122.6852 | 0.17853 | -0.0031279 | 0.015383 | 0.011867 | -0.0036637 | 0.057764 | -0.0062164 | 0.079889 | -122.699 | 0.23804 | -123.1659 | -122.5891 | 0.013733 | 0.073242 | -2.9938 | -1.3229 | 0.29755 | -123.0423 | -0.48065 | 0.059509 | -0.013733 | 0.096131 | -0.16479 | -0.35706 | 0.11902 | 0.46692 | 119.6915 | 121.3623 | 122.699 | 122.9233 | -0.013733 | 122.9828 | 122.7585 | -0.35706 | 122.9233 | -0.013733 | 122.7585 | 122.699 | 122.9828 | -123.3444 | -123.2208
870.8906 | 122.9691 | -122.6761 | 0.20599 | -0.010757 | 0.014101 | 0.0052445 | -0.0081497 | 0.05755 | -0.0068574 | 0.081384 | -122.6028 | 0.20599 | -123.0789 | -122.5204 | 0.10071 | -0.9201 | -3.2135 | -1.3916 | 0.23804 | -123.0148 | -0.40283 | 0 | 0.073242 | 0.15564 | -0.10529 | -0.33875 | 0.032043 | 0.47607 | 119.4626 | 121.2845 | 122.7768 | 122.8821 | 0.073242 | 122.9141 | 121.756 | -0.33875 | 122.8821 | 0.073242 | 121.756 | 122.7768 | 122.9141 | -123.2849 | -123.2208
872.6406 | 122.8592 | -122.7264 | 0.18768 | 0.0045011 | 0.016878 | 0.0088761 | -0.0062271 | 0.059473 | -0.0057892 | 0.080102 | -122.58 | 0.20142 | -123.0789 | -122.5159 | 0.10071 | 0.20599 | -3.4515 | -1.5976 | 0.24719 | -122.9828 | -0.35248 | 0.013733 | 0.14648 | 0.21057 | -0.086975 | -0.25635 | 0.059509 | 0.49896 | 119.2749 | 121.1288 | 122.8271 | 122.9279 | 0.14648 | 122.9736 | 122.9324 | -0.25635 | 122.9279 | 0.14648 | 122.9324 | 122.8271 | 122.9736 | -123.2666 | -123.1705
874.3125 | 122.8867 | -122.7173 | 0.21973 | 0.012131 | 0.016451 | 0.0078079 | -0.0032363 | 0.060114 | -0.0045074 | 0.080316 | -122.6349 | 0.2243 | -123.1338 | -122.5571 | 0.045776 | -8.5602 | -3.4149 | -1.6388 | 0.27008 | -123.0148 | -0.41656 | 0.004577 | 0.082397 | 0.16022 | -0.17395 | -0.29755 | 0.050354 | 0.49896 | 119.3024 | 121.0785 | 122.7631 | 122.9416 | 0.082397 | 122.9874 | 114.1571 | -0.29755 | 122.9416 | 0.082397 | 114.1571 | 122.7631 | 122.9874 | -123.3536 | -123.2346
876.0625 | 122.8821 | -122.7081 | 0.19226 | -0.010757 | 0.017733 | 0.011653 | -0.0055863 | 0.060114 | -0.0077118 | 0.079889 | -122.6395 | 0.2243 | -123.0743 | -122.5571 | 0.082397 | 0.17853 | -3.7033 | -1.4786 | 0.27008 | -123.0331 | -0.36621 | 0.032043 | 0.068665 | 0.15106 | -0.10986 | -0.32501 | 0.07782 | 0.43488 | 119.0048 | 121.2296 | 122.7905 | 122.9324 | 0.068665 | 122.9782 | 122.8867 | -0.32501 | 122.9324 | 0.068665 | 122.8867 | 122.7905 | 122.9782 | -123.2666 | -123.2254
877.75 | 122.8683 | -122.7127 | 0.21057 | -0.0031279 | 0.01816 | 0.012721 | -0.0030227 | 0.061182 | -0.005362 | 0.080743 | -122.6624 | 0.25177 | -123.1476 | -122.5662 | 0.032043 | 0.09613 | -3.772 | -1.5564 | 0.28381 | -123.0011 | -0.43487 | 0.041199 | 0.050354 | 0.14649 | -0.17853 | -0.28839 | 0.073242 | 0.48523 | 118.9407 | 121.1563 | 122.7448 | 122.9645 | 0.050354 | 122.9965 | 122.8088 | -0.28839 | 122.9645 | 0.050354 | 122.8088 | 122.7448 | 122.9965 | -123.3582 | -123.2117
879.5 | 122.9828 | -122.6486 | 0.16937 | 0.012131 | 0.01581 | 0.0078079 | -0.012422 | 0.0599 | -0.0040802 | 0.078607 | -122.644 | 0.21973 | -123.0789 | -122.5571 | 0.10071 | 0.17853 | -3.891 | -1.5289 | 0.24719 | -123.0377 | -0.4303 | 0.050354 | 0.004578 | 0.091553 | -0.068665 | -0.3891 | 0.077819 | 0.43488 | 118.7576 | 121.1197 | 122.7493 | 122.8683 | 0.004578 | 122.8958 | 122.8271 | -0.3891 | 122.8683 | 0.004578 | 122.8271 | 122.7493 | 122.8958 | -123.2483 | -123.2071
881.25 | 122.937 | -122.6807 | 0.16479 | 0.0045011 | 0.013674 | 0.0080215 | -0.0079361 | 0.058618 | -0.0049348 | 0.080957 | -122.6028 | 0.20599 | -123.0789 | -122.5159 | 0.14191 | 0.21515 | -3.8681 | -1.3962 | 0.25177 | -122.9919 | -0.39825 | 0.041199 | 0.07782 | 0.16479 | -0.022888 | -0.31128 | 0.086975 | 0.47607 | 118.8126 | 121.2845 | 122.8226 | 122.8867 | 0.07782 | 122.9324 | 122.8958 | -0.31128 | 122.8867 | 0.07782 | 122.8958 | 122.8226 | 122.9324 | -123.2437 | -123.1567
883 | 122.8867 | -122.7127 | 0.20599 | 0.012131 | 0.017092 | 0.010371 | -0.00067292 | 0.061609 | -0.0066438 | 0.081598 | -122.7036 | 0.23804 | -123.143 | -122.6257 | -0.018311 | 0.059509 | -3.7354 | -1.6342 | 0.29297 | -123.0011 | -0.4303 | 0.032043 | 0.009156 | 0.086976 | -0.22431 | -0.28839 | 0.086975 | 0.43945 | 118.9774 | 121.0785 | 122.6944 | 122.9507 | 0.009156 | 123.0057 | 122.7722 | -0.28839 | 122.9507 | 0.009156 | 122.7722 | 122.6944 | 123.0057 | -123.349 | -123.2071
884.6719 | 122.85 | -122.7264 | 0.20599 | 0.0045011 | 0.018587 | 0.013789 | -0.0038773 | 0.061609 | -0.0066438 | 0.082452 | -122.612 | 0.19226 | -123.0652 | -122.5204 | 0.10986 | 0.19226 | -3.9825 | -1.4877 | 0.24719 | -123.0011 | -0.33875 | -0.013733 | 0.11444 | 0.20599 | -0.096131 | -0.27466 | 0.041198 | 0.45319 | 118.7439 | 121.2387 | 122.8363 | 122.9187 | 0.11444 | 122.9736 | 122.9187 | -0.27466 | 122.9187 | 0.11444 | 122.9187 | 122.8363 | 122.9736 | -123.2712 | -123.2071
886.4219 | 122.9599 | -122.6715 | 0.17395 | 0.0045011 | 0.017947 | 0.0031083 | -0.010072 | 0.058832 | -0.005362 | 0.077111 | -122.5891 | 0.16937 | -123.0698 | -122.4884 | 0.1236 | 0.20142 | -4.454 | -1.4145 | 0.24261 | -123.0057 | -0.39825 | -0.004577 | 0.082398 | 0.18311 | -0.050354 | -0.33417 | 0.068665 | 0.48065 | 118.2175 | 121.257 | 122.7951 | 122.8409 | 0.082398 | 122.9141 | 122.8729 | -0.33417 | 122.8409 | 0.082398 | 122.8729 | 122.7951 | 122.9141 | -123.2437 | -123.1796
888.1719 | 122.905 | -122.7081 | 0.18768 | -0.0031279 | 0.02051 | 0.010158 | -0.0021683 | 0.061395 | -0.0089936 | 0.079034 | -122.6807 | 0.22888 | -123.1064 | -122.612 | -0.018311 | 0.07782 | -5.0354 | -2.8702 | 0.28381 | -123.0103 | -0.39825 | 0.041199 | 0.027466 | 0.09613 | -0.20599 | -0.30212 | 0.09613 | 0.42572 | 117.6727 | 119.838 | 122.6898 | 122.937 | 0.027466 | 122.9919 | 122.7859 | -0.30212 | 122.937 | 0.027466 | 122.7859 | 122.6898 | 122.9919 | -123.2941 | -123.1979
889.9062 | 123.0011 | -122.6532 | 0.17395 | 0.012131 | 0.015597 | 0.0060989 | -0.011354 | 0.059473 | -0.0040802 | 0.080529 | -122.6624 | 0.20599 | -123.0698 | -122.5708 | 0.054932 | 0.15564 | -5.365 | -2.948 | 0.26093 | -123.0103 | -0.41656 | 0.032044 | -0.009156 | 0.082397 | -0.11902 | -0.35706 | 0.086975 | 0.40741 | 117.2882 | 119.7052 | 122.7081 | 122.8592 | -0.009156 | 122.9141 | 122.8088 | -0.35706 | 122.8592 | -0.009156 | 122.8088 | 122.7081 | 122.9141 | -123.2437 | -123.1842
891.5938 | 122.9095 | -122.7081 | 0.20142 | -0.0031279 | 0.019015 | 0.013789 | -0.0023819 | 0.061182 | -0.005362 | 0.079034 | -122.6898 | 0.24261 | -123.111 | -122.6257 | -0.032043 | 0.068665 | -5.2963 | -3.1494 | 0.29297 | -123.0606 | -0.40283 | 0.041199 | 0.018311 | 0.082398 | -0.23346 | -0.35248 | 0.091553 | 0.42114 | 117.4118 | 119.5587 | 122.6761 | 122.9507 | 0.018311 | 123.0011 | 122.7768 | -0.35248 | 122.9507 | 0.018311 | 122.7768 | 122.6761 | 123.0011 | -123.3124 | -123.262
893.3594 | 122.9462 | -122.6852 | 0.16479 | -0.010757 | 0.015169 | 0.011226 | -0.0047317 | 0.061823 | -0.0072846 | 0.080957 | -122.6852 | 0.2243 | -123.143 | -122.5662 | 0.022888 | 0.091553 | -5.246 | -3.2135 | 0.27924 | -123.0148 | -0.45776 | 0.059509 | 0 | 0.11902 | -0.14191 | -0.32959 | 0.11444 | 0.45776 | 117.4393 | 119.4717 | 122.7081 | 122.9095 | 0 | 122.9645 | 122.7768 | -0.32959 | 122.9095 | 0 | 122.7768 | 122.7081 | 122.9645 | -123.3078 | -123.1796
895.0312 | 122.8958 | -122.7127 | 0.19226 | 0.012131 | 0.01816 | 0.0097305 | -0.0034499 | 0.060754 | -0.0092072 | 0.079248 | -122.699 | 0.21515 | -123.1018 | -122.6303 | -0.018311 | 0.054932 | -4.5914 | -3.3875 | 0.27924 | -123.0286 | -0.3891 | 0.022888 | 0.013733 | 0.082398 | -0.21057 | -0.31586 | 0.086975 | 0.40283 | 118.1213 | 119.3253 | 122.6944 | 122.9279 | 0.013733 | 122.9919 | 122.7676 | -0.31586 | 122.9279 | 0.013733 | 122.7676 | 122.6944 | 122.9919 | -123.2941 | -123.2208
896.7656 | 122.9004 | -122.699 | 0.20142 | 0.0045011 | 0.017947 | 0.010371 | -0.0057999 | 0.062036 | -0.0038666 | 0.080529 | -122.6944 | 0.23804 | -123.111 | -122.6303 | -0.004578 | 0.07782 | -4.9576 | -3.3142 | 0.27466 | -123.0194 | -0.41199 | 0.036621 | 0.004578 | 0.068665 | -0.20599 | -0.32043 | 0.073242 | 0.41657 | 117.7414 | 119.3848 | 122.6944 | 122.937 | 0.004578 | 122.9736 | 122.7768 | -0.32043 | 122.937 | 0.004578 | 122.7768 | 122.6944 | 122.9736 | -123.3124 | -123.2208
898.5156 | 122.9416 | -122.6761 | 0.17395 | -0.0031279 | 0.01346 | 0.011653 | -0.010927 | 0.06225 | -0.005362 | 0.079675 | -122.6028 | 0.19684 | -123.056 | -122.5204 | 0.13275 | 0.20599 | -5.7358 | -3.5568 | 0.23804 | -123.0011 | -0.37994 | 0.022888 | 0.073242 | 0.15564 | -0.041199 | -0.32501 | 0.064087 | 0.45319 | 116.9403 | 119.1193 | 122.8088 | 122.8729 | 0.073242 | 122.9141 | 122.8821 | -0.32501 | 122.8729 | 0.073242 | 122.8821 | 122.8088 | 122.9141 | -123.23 | -123.175
900.2656 | 122.9599 | -122.6761 | 0.16937 | -0.0031279 | 0.017092 | 0.0067399 | -0.010072 | 0.057337 | -0.0025848 | 0.080743 | -122.6212 | 0.20142 | -123.056 | -122.5113 | 0.11902 | 0.21057 | -6.1478 | -3.479 | 0.22888 | -122.9919 | -0.37994 | 0.032043 | 0.054931 | 0.16479 | -0.050354 | -0.31586 | 0.059509 | 0.43488 | 116.5283 | 119.1971 | 122.7951 | 122.8775 | 0.054931 | 122.905 | 122.8867 | -0.31586 | 122.8775 | 0.054931 | 122.8867 | 122.7951 | 122.905 | -123.2254 | -123.1613
902.0156 | 122.8683 | -122.7356 | 0.2243 | 0.0045011 | 0.017947 | 0.012294 | -0.0032363 | 0.062036 | -0.00878 | 0.079461 | -122.6303 | 0.20599 | -123.1064 | -122.5525 | 0.050354 | 0.1236 | -6.0516 | -3.2822 | 0.28381 | -122.9919 | -0.37079 | -0.01831 | 0.10529 | 0.18311 | -0.17395 | -0.25635 | 0.059509 | 0.47607 | 116.684 | 119.4534 | 122.7859 | 122.9416 | 0.10529 | 123.0194 | 122.8592 | -0.25635 | 122.9416 | 0.10529 | 122.8592 | 122.7859 | 123.0194 | -123.3307 | -123.2162
903.7656 | 123.0148 | -122.6624 | 0.16937 | 0.0045011 | 0.016024 | 0.0056717 | -0.010713 | 0.060327 | -0.00643 | 0.077539 | -122.6532 | 0.21515 | -123.0789 | -122.5571 | 0.082397 | 0.17853 | -6.0425 | -2.8976 | 0.2655 | -123.0331 | -0.41656 | 0.045776 | 0.009156 | 0.10529 | -0.086976 | -0.37079 | 0.09613 | 0.42572 | 116.6199 | 119.7647 | 122.7448 | 122.8775 | 0.009156 | 122.9279 | 122.8409 | -0.37079 | 122.8775 | 0.009156 | 122.8409 | 122.7448 | 122.9279 | -123.2483 | -123.2025
905.4531 | 122.8592 | -122.731 | 0.21973 | -0.0031279 | 0.017519 | 0.0088761 | -0.0011001 | 0.060327 | -0.0057892 | 0.08117 | -122.6395 | 0.20599 | -123.1247 | -122.5525 | 0.022888 | 0.11444 | -4.6875 | -2.948 | 0.26093 | -122.9874 | -0.39368 | -0.013733 | 0.091553 | 0.17853 | -0.19684 | -0.25635 | 0.041198 | 0.48523 | 118.0435 | 119.783 | 122.7539 | 122.937 | 0.091553 | 122.9919 | 122.8455 | -0.25635 | 122.937 | 0.091553 | 122.8455 | 122.7539 | 122.9919 | -123.3444 | -123.2071
907.2031 | 122.8592 | -122.7264 | 0.20599 | 0.0045011 | 0.016451 | 0.0086625 | -0.0030227 | 0.062036 | -0.0072846 | 0.082666 | -122.6166 | 0.21057 | -123.1018 | -122.5754 | 0.032043 | 0.1236 | -4.5868 | -2.9892 | 0.28381 | -123.0194 | -0.37537 | 0.004577 | 0.10986 | 0.15106 | -0.17395 | -0.29297 | 0.077819 | 0.48523 | 118.1396 | 119.7372 | 122.7585 | 122.937 | 0.10986 | 123.0103 | 122.85 | -0.29297 | 122.937 | 0.10986 | 122.85 | 122.7585 | 123.0103 | -123.3078 | -123.2254
908.9531 | 122.9736 | -122.6852 | 0.1831 | 0.0045011 | 0.015597 | 0.011653 | -0.010072 | 0.057337 | -0.0060028 | 0.079034 | -122.6074 | 0.19226 | -123.056 | -122.5204 | 0.086975 | 0.16479 | -4.9622 | -3.0441 | 0.24719 | -123.0194 | -0.37079 | 0.009156 | 0.07782 | 0.16479 | -0.09613 | -0.33417 | 0.064087 | 0.44861 | 117.7231 | 119.6411 | 122.7722 | 122.8775 | 0.07782 | 122.9324 | 122.85 | -0.33417 | 122.8775 | 0.07782 | 122.85 | 122.7722 | 122.9324 | -123.2391 | -123.2025
910.625 | 122.9874 | -122.6807 | 0.18768 | 0.0045011 | 0.019869 | 0.0050309 | -0.0053727 | 0.060754 | -0.0055756 | 0.080102 | -122.6852 | 0.23346 | -123.1201 | -122.6074 | -0.013733 | 0.068665 | -4.8203 | -2.4765 | 0.28839 | -123.0194 | -0.43945 | 0.045776 | -0.004578 | 0.073242 | -0.20142 | -0.33875 | 0.10071 | 0.43487 | 117.8604 | 120.2042 | 122.6669 | 122.9141 | -0.004578 | 122.9691 | 122.7493 | -0.33875 | 122.9141 | -0.004578 | 122.7493 | 122.6669 | 122.9691 | -123.3078 | -123.2071
912.3594 | 122.8638 | -122.7219 | 0.17853 | -0.010757 | 0.018587 | 0.0075943 | -0.0034499 | 0.063318 | -0.008139 | 0.080529 | -122.6212 | 0.19684 | -123.1293 | -122.5571 | 0.022888 | 0.11902 | -4.9713 | -2.6001 | 0.27466 | -123.0011 | -0.40741 | 0.01831 | 0.10071 | 0.16479 | -0.15564 | -0.27924 | 0.09613 | 0.50812 | 117.7506 | 120.1218 | 122.7448 | 122.9187 | 0.10071 | 122.9965 | 122.8409 | -0.27924 | 122.9187 | 0.10071 | 122.8409 | 122.7448 | 122.9965 | -123.3078 | -123.1796
914.0938 | 122.85 | -122.7081 | 0.20599 | -0.0031279 | 0.015597 | 0.012935 | -0.0038773 | 0.062891 | -0.0051484 | 0.079248 | -122.6166 | 0.21515 | -123.1155 | -122.5616 | 0.041199 | 0.1236 | -5.864 | -2.4811 | 0.27008 | -122.9919 | -0.40741 | 0.009155 | 0.091553 | 0.14648 | -0.1648 | -0.28381 | 0.064087 | 0.49896 | 116.8442 | 120.2271 | 122.7493 | 122.9233 | 0.091553 | 122.9782 | 122.8317 | -0.28381 | 122.9233 | 0.091553 | 122.8317 | 122.7493 | 122.9782 | -123.3215 | -123.1979
915.7656 | 122.85 | -122.7173 | 0.19684 | 0.012131 | 0.015597 | 0.010158 | -0.0077225 | 0.061182 | -0.0051484 | 0.080743 | -122.5937 | 0.16937 | -123.0515 | -122.5204 | 0.09613 | 0.21515 | -6.2302 | -2.6367 | 0.23346 | -122.9919 | -0.33417 | -0.027465 | 0.1236 | 0.19684 | -0.10071 | -0.27466 | 0.036621 | 0.45776 | 116.4871 | 120.0806 | 122.8134 | 122.8867 | 0.1236 | 122.9507 | 122.9324 | -0.27466 | 122.8867 | 0.1236 | 122.9324 | 122.8134 | 122.9507 | -123.2483 | -123.1888
917.5 | 122.8455 | -122.6944 | 0.20142 | -0.0031279 | 0.016238 | 0.010371 | -0.0077225 | 0.061395 | -0.0055756 | 0.080529 | -122.5937 | 0.19226 | -123.0377 | -122.5204 | 0.086975 | 0.19684 | -6.459 | -2.9434 | 0.22888 | -123.0057 | -0.34332 | -0.009155 | 0.10071 | 0.17395 | -0.11444 | -0.31128 | 0.027466 | 0.44403 | 116.2354 | 119.751 | 122.7814 | 122.8867 | 0.10071 | 122.9233 | 122.8912 | -0.31128 | 122.8867 | 0.10071 | 122.8912 | 122.7814 | 122.9233 | -123.2391 | -123.2071
919.25 | 122.9645 | -122.6715 | 0.17853 | -0.0031279 | 0.014529 | 0.011867 | -0.0072953 | 0.060114 | -0.008139 | 0.08117 | -122.7081 | 0.24719 | -123.1247 | -122.6166 | -0.013733 | 0.07782 | -6.4407 | -2.8061 | 0.28839 | -123.0286 | -0.45319 | 0.068664 | -0.036621 | 0.054932 | -0.19226 | -0.35706 | 0.10986 | 0.41657 | 116.2308 | 119.8654 | 122.6578 | 122.9187 | -0.036621 | 122.9599 | 122.7493 | -0.35706 | 122.9187 | -0.036621 | 122.7493 | 122.6578 | 122.9599 | -123.3032 | -123.2071
921 | 122.8546 | -122.7036 | 0.17853 | -0.0031279 | 0.015169 | 0.0060989 | -0.0092179 | 0.062891 | -0.0077118 | 0.080957 | -122.58 | 0.17853 | -123.0515 | -122.5113 | 0.086975 | -11.2839 | -7.7316 | -2.98 | 0.23804 | -122.9599 | -0.3479 | 0 | 0.1236 | 0.19226 | -0.091553 | -0.25635 | 0.059509 | 0.4715 | 114.9719 | 119.7235 | 122.7905 | 122.8821 | 0.1236 | 122.9416 | 111.4197 | -0.25635 | 122.8821 | 0.1236 | 111.4197 | 122.7905 | 122.9416 | -123.23 | -123.1384
922.6719 | 122.8317 | -122.6669 | 0.19226 | 0.012131 | 0.017306 | 0.0099441 | -0.0062271 | 0.0599 | -0.00643 | 0.079461 | -122.5891 | 0.20142 | -123.0423 | -122.525 | 0.07782 | -11.8652 | -8.2031 | -3.3096 | 0.24719 | -123.0057 | -0.37537 | 0.009155 | 0.07782 | 0.14191 | -0.11444 | -0.33874 | 0.054931 | 0.45319 | 114.4638 | 119.3573 | 122.7448 | 122.8683 | 0.07782 | 122.9141 | 110.8017 | -0.33874 | 122.8683 | 0.07782 | 110.8017 | 122.7448 | 122.9141 | -123.2346 | -123.1979
924.4375 | 122.9279 | -122.6807 | 0.15564 | 0.0045011 | 0.017947 | 0.0095169 | -0.010072 | 0.062463 | -0.0051484 | 0.080957 | -122.5891 | 0.20142 | -123.056 | -122.5113 | 0.10071 | -11.2976 | -1.3092 | -3.1723 | 0.24261 | -122.9782 | -0.37537 | 0.045776 | 0.091553 | 0.16937 | -0.054932 | -0.29755 | 0.086975 | 0.46692 | 121.3715 | 119.5084 | 122.7814 | 122.8821 | 0.091553 | 122.9233 | 111.3831 | -0.29755 | 122.8821 | 0.091553 | 111.3831 | 122.7814 | 122.9233 | -123.2117 | -123.1339
926.125 | 122.937 | -122.6944 | 0.17395 | -0.0031279 | 0.017092 | 0.0086625 | -0.0083633 | 0.060754 | -0.0062164 | 0.079034 | -122.5754 | 0.19684 | -123.024 | -122.493 | 0.086975 | -10.7346 | -1.2634 | -3.2135 | 0.25177 | -123.0011 | -0.32959 | 0.022888 | 0.11902 | 0.20142 | -0.086975 | -0.3067 | 0.07782 | 0.44861 | 121.431 | 119.4809 | 122.7814 | 122.8912 | 0.11902 | 122.9462 | 111.9598 | -0.3067 | 122.8912 | 0.11902 | 111.9598 | 122.7814 | 122.9462 | -123.1979 | -123.175
927.8594 | 122.8546 | -122.7081 | 0.21057 | 0.012131 | 0.021365 | 0.011653 | -0.0015273 | 0.060327 | -0.0068574 | 0.079248 | -122.6395 | 0.21515 | -123.0835 | -122.5845 | -0.013733 | -10.9131 | -1.0574 | -3.511 | 0.27008 | -123.0331 | -0.37537 | 0.004578 | 0.068665 | 0.1236 | -0.2243 | -0.32501 | 0.05951 | 0.44403 | 121.6507 | 119.1971 | 122.6944 | 122.9233 | 0.068665 | 122.9782 | 111.795 | -0.32501 | 122.9233 | 0.068665 | 111.795 | 122.6944 | 122.9782 | -123.2941 | -123.2437
929.6094 | 122.9553 | -122.612 | 0.17395 | -0.0031279 | 0.017092 | 0.0046037 | -0.0094315 | 0.063959 | -0.0055756 | 0.079461 | -122.6486 | 0.21057 | -123.0423 | -122.5708 | 0.041199 | -10.7529 | -1.1536 | -3.5934 | 0.24261 | -123.0057 | -0.4303 | 0.036621 | -0.036621 | 0.041199 | -0.13275 | -0.39368 | 0.068665 | 0.39368 | 121.4584 | 119.0186 | 122.6532 | 122.8226 | -0.036621 | 122.8546 | 111.8591 | -0.39368 | 122.8226 | -0.036621 | 111.8591 | 122.6532 | 122.8546 | -123.2162 | -123.1796
931.3594 | 122.8546 | -122.7081 | 0.20142 | 0.0045011 | 0.015383 | 0.0067399 | -0.00045932 | 0.060754 | -0.0060028 | 0.082666 | -122.6486 | 0.22888 | -123.1293 | -122.5571 | -0.013733 | -11.6455 | -1.062 | -3.3783 | 0.27466 | -123.0057 | -0.42114 | 0.027466 | 0.059509 | 0.15106 | -0.21515 | -0.29755 | 0.073242 | 0.48065 | 121.6461 | 119.3298 | 122.6944 | 122.937 | 0.059509 | 122.9828 | 111.0626 | -0.29755 | 122.937 | 0.059509 | 111.0626 | 122.6944 | 122.9828 | -123.3307 | -123.2071
933.1094 | 122.8729 | -122.6898 | 0.21515 | 0.012131 | 0.014956 | 0.011439 | -0.0032363 | 0.062036 | -0.0060028 | 0.080102 | -122.6624 | 0.22888 | -123.1201 | -122.612 | -0.027466 | -11.9476 | -1.1078 | -3.9597 | 0.28381 | -122.9874 | -0.4303 | 0.013733 | 0.027465 | 0.077819 | -0.24261 | -0.29755 | 0.068664 | 0.45776 | 121.582 | 118.7302 | 122.6624 | 122.9187 | 0.027465 | 122.9736 | 110.7422 | -0.29755 | 122.9187 | 0.027465 | 110.7422 | 122.6624 | 122.9736 | -123.3353 | -123.2025
934.8438 | 122.8775 | -122.6944 | 0.19226 | -0.0031279 | 0.018587 | 0.0080215 | -0.0032363 | 0.063959 | -0.0072846 | 0.082025 | -122.6624 | 0.22888 | -123.1018 | -122.6074 | -0.027466 | -12.7258 | -1.1444 | -3.7491 | 0.27466 | -122.9919 | -0.40741 | 0.036621 | 0.032043 | 0.086975 | -0.21973 | -0.29755 | 0.082397 | 0.43945 | 121.55 | 118.9453 | 122.6669 | 122.9233 | 0.032043 | 122.9691 | 109.9686 | -0.29755 | 122.9233 | 0.032043 | 109.9686 | 122.6669 | 122.9691 | -123.2941 | -123.1842
936.5938 | 122.9736 | -122.644 | 0.15564 | 0.0045011 | 0.014529 | 0.0063125 | -0.0081497 | 0.060541 | -0.0062164 | 0.080102 | -122.6669 | 0.24261 | -123.0835 | -122.6028 | -0.013733 | -12.6114 | -1.0666 | -3.8681 | 0.29297 | -123.0377 | -0.43945 | 0.086975 | -0.022888 | 0.041199 | -0.16937 | -0.39368 | 0.13733 | 0.41656 | 121.5775 | 118.7759 | 122.6303 | 122.8867 | -0.022888 | 122.937 | 110.0327 | -0.39368 | 122.8867 | -0.022888 | 110.0327 | 122.6303 | 122.937 | -123.2391 | -123.1934
938.2812 | 122.9507 | -122.6486 | 0.17853 | 0.0045011 | 0.016878 | 0.0095169 | -0.0096451 | 0.059045 | -0.0051484 | 0.080743 | -122.6486 | 0.19684 | -123.0652 | -122.5754 | 0.041199 | -12.5198 | -1.2222 | -4.129 | 0.23804 | -123.024 | -0.41656 | 0.01831 | 0 | 0.073243 | -0.13733 | -0.37537 | 0.059509 | 0.41656 | 121.4264 | 118.5196 | 122.6898 | 122.8455 | 0 | 122.8867 | 110.1288 | -0.37537 | 122.8455 | 0 | 110.1288 | 122.6898 | 122.8867 | -123.2437 | -123.2025
940.0312 | 122.8363 | -122.7219 | 0.20599 | -0.010757 | 0.019869 | 0.0067399 | -0.0028091 | 0.062463 | -0.0077118 | 0.080529 | -122.612 | 0.21057 | -123.111 | -122.5433 | 0.018311 | -12.9227 | -1.2634 | -4.1336 | 0.27466 | -122.9736 | -0.3891 | 0.004577 | 0.10986 | 0.17853 | -0.18768 | -0.25177 | 0.068664 | 0.49896 | 121.4584 | 118.5883 | 122.7402 | 122.9324 | 0.10986 | 122.9965 | 109.7992 | -0.25177 | 122.9324 | 0.10986 | 109.7992 | 122.7402 | 122.9965 | -123.317 | -123.1796
941.7188 | 122.8775 | -122.6715 | 0.16937 | -0.0031279 | 0.017519 | 0.0071671 | -0.011781 | 0.060541 | -0.0038666 | 0.079461 | -122.6257 | 0.21057 | -123.0469 | -122.5616 | 0.032043 | -12.6343 | -1.2222 | -4.7241 | 0.24719 | -123.0103 | -0.37537 | 0.041198 | 0.045777 | 0.10986 | -0.13733 | -0.33875 | 0.077819 | 0.42114 | 121.4493 | 117.9474 | 122.7036 | 122.8821 | 0.045777 | 122.9187 | 110.0372 | -0.33875 | 122.8821 | 0.045777 | 110.0372 | 122.7036 | 122.9187 | -123.2162 | -123.1796
943.4688 | 122.8455 | -122.699 | 0.20599 | 0.0045011 | 0.017306 | 0.0088761 | -0.0017411 | 0.061823 | -0.007071 | 0.080102 | -122.6212 | 0.21973 | -123.1064 | -122.5662 | -0.004578 | -13.2797 | -1.1536 | -3.7811 | 0.27008 | -122.9874 | -0.40741 | 0.013733 | 0.07782 | 0.13275 | -0.21057 | -0.28839 | 0.064087 | 0.48523 | 121.5454 | 118.9178 | 122.6944 | 122.9187 | 0.07782 | 122.9691 | 109.4193 | -0.28839 | 122.9187 | 0.07782 | 109.4193 | 122.6944 | 122.9691 | -123.3124 | -123.1934
945.2031 | 122.8363 | -122.6852 | 0.18768 | 0.0045011 | 0.017092 | 0.011012 | -0.0045181 | 0.060541 | -0.005362 | 0.079461 | -122.6395 | 0.23346 | -123.1338 | -122.5662 | -0.013733 | -13.1516 | -1.1078 | -4.0192 | 0.27466 | -123.0103 | -0.44861 | 0.045776 | 0.045777 | 0.11902 | -0.20142 | -0.32501 | 0.086975 | 0.49438 | 121.5775 | 118.6661 | 122.6715 | 122.9187 | 0.045777 | 122.9599 | 109.5337 | -0.32501 | 122.9187 | 0.045777 | 109.5337 | 122.6715 | 122.9599 | -123.3215 | -123.1979
946.9375 | 122.9324 | -122.6578 | 0.16937 | 0.0045011 | 0.015169 | 0.0078079 | -0.01285 | 0.059045 | -0.0045074 | 0.080957 | -122.612 | 0.1831 | -123.0606 | -122.5113 | 0.064087 | -12.4649 | -1.181 | -4.4083 | 0.24719 | -122.9782 | -0.40283 | 0.013732 | 0.045776 | 0.14648 | -0.10529 | -0.32043 | 0.077819 | 0.44861 | 121.4767 | 118.2495 | 122.7219 | 122.8409 | 0.045776 | 122.905 | 110.1929 | -0.32043 | 122.8409 | 0.045776 | 110.1929 | 122.7219 | 122.905 | -123.23 | -123.1476
948.625 | 122.9691 | -122.6669 | 0.14648 | 0.0045011 | 0.016878 | 0.0075943 | -0.0062271 | 0.058618 | -0.00643 | 0.07882 | -122.6349 | 0.2243 | -123.0515 | -122.58 | -0.013733 | -12.9181 | -1.0757 | -5.1636 | 0.28839 | -123.0423 | -0.38452 | 0.07782 | 0.032043 | 0.086975 | -0.16022 | -0.37537 | 0.14191 | 0.41656 | 121.5912 | 117.5034 | 122.6532 | 122.8912 | 0.032043 | 122.9553 | 109.7488 | -0.37537 | 122.8912 | 0.032043 | 109.7488 | 122.6532 | 122.9553 | -123.1979 | -123.1888
950.3125 | 122.8912 | -122.6669 | 0.17853 | 0.0045011 | 0.020724 | 0.0073807 | -0.0038773 | 0.061182 | -0.0074982 | 0.082666 | -122.6624 | 0.23804 | -123.0881 | -122.6257 | -0.050354 | -13.2294 | -1.1581 | -5.7632 | 0.28839 | -122.9919 | -0.42114 | 0.059509 | 0.004577 | 0.041199 | -0.22888 | -0.32501 | 0.10986 | 0.42572 | 121.5088 | 116.9037 | 122.6166 | 122.905 | 0.004577 | 122.9553 | 109.4376 | -0.32501 | 122.905 | 0.004577 | 109.4376 | 122.6166 | 122.9553 | -123.2666 | -123.1705
952.0625 | 122.8592 | -122.6852 | 0.16937 | -0.010757 | 0.017092 | 0.0063125 | -0.010286 | 0.057977 | -0.0025848 | 0.07882 | -122.5983 | 0.19684 | -123.0469 | -122.5433 | 0.059509 | -12.6068 | -1.4374 | -6.1981 | 0.25177 | -122.9874 | -0.36163 | 0.027465 | 0.086975 | 0.14191 | -0.10986 | -0.30212 | 0.082397 | 0.44861 | 121.2479 | 116.4871 | 122.7448 | 122.8821 | 0.086975 | 122.937 | 110.0784 | -0.30212 | 122.8821 | 0.086975 | 110.0784 | 122.7448 | 122.937 | -123.2162 | -123.1567
953.75 | 122.905 | -122.6715 | 0.1831 | 0.01976 | 0.016024 | 0.0093033 | -0.0032363 | 0.060114 | -0.003653 | 0.080316 | -122.6944 | 0.21057 | -123.1293 | -122.6212 | -0.082397 | -12.8265 | -1.1627 | -6.6971 | 0.29755 | -122.9965 | -0.45776 | 0.027466 | -0.022888 | 0.050354 | -0.2655 | -0.32501 | 0.11444 | 0.43488 | 121.5088 | 115.9744 | 122.5891 | 122.8821 | -0.022888 | 122.9691 | 109.845 | -0.32501 | 122.8821 | -0.022888 | 109.845 | 122.5891 | 122.9691 | -123.3124 | -123.1796
955.5 | 122.85 | -122.6532 | 0.19226 | -0.0031279 | 0.014101 | 0.0082351 | -0.0079361 | 0.063745 | -0.0060028 | 0.078607 | -122.5708 | 0.17853 | -123.0606 | -122.5342 | 0.032043 | -12.3779 | -1.2634 | -7.8415 | 0.23804 | -123.0057 | -0.40741 | -0.013733 | 0.082397 | 0.11902 | -0.16022 | -0.35248 | 0.045776 | 0.48981 | 121.3898 | 114.8117 | 122.6852 | 122.8317 | 0.082397 | 122.8912 | 110.2753 | -0.35248 | 122.8317 | 0.082397 | 110.2753 | 122.6852 | 122.8912 | -123.2529 | -123.1979
957.1875 | 122.9553 | -122.6669 | 0.17395 | 0.0045011 | 0.014956 | 0.013789 | -0.0068679 | 0.058832 | -0.0045074 | 0.079034 | -122.6166 | 0.20142 | -123.0698 | -122.5433 | 0.009155 | -12.9318 | -1.1444 | -8.3908 | 0.2655 | -123.0103 | -0.40283 | 0.027466 | 0.050354 | 0.1236 | -0.16479 | -0.34332 | 0.091553 | 0.45319 | 121.5225 | 114.2761 | 122.6761 | 122.8683 | 0.050354 | 122.9324 | 109.7351 | -0.34332 | 122.8683 | 0.050354 | 109.7351 | 122.6761 | 122.9324 | -123.2437 | -123.1842
958.9375 | 122.905 | -122.6807 | 0.1831 | -0.0031279 | 0.017733 | 0.0075943 | -0.0034499 | 0.061395 | -0.007071 | 0.080316 | -122.6761 | 0.2243 | -123.1201 | -122.6074 | -0.082397 | -12.9639 | -1.1124 | -8.931 | 0.28839 | -123.0148 | -0.43945 | 0.041199 | 0.004578 | 0.073242 | -0.2655 | -0.33417 | 0.10529 | 0.44403 | 121.5683 | 113.7497 | 122.5983 | 122.905 | 0.004578 | 122.9691 | 109.7168 | -0.33417 | 122.905 | 0.004578 | 109.7168 | 122.5983 | 122.9691 | -123.3032 | -123.1979
960.6719 | 122.8317 | -122.7127 | 0.20599 | 0.012131 | 0.014742 | 0.011439 | -0.0062271 | 0.06225 | -0.0072846 | 0.081384 | -122.6074 | 0.21515 | -123.0881 | -122.5388 | 0.004578 | -12.4695 | -1.3916 | -9.8511 | 0.27008 | -122.9782 | -0.37537 | 0.009155 | 0.10529 | 0.17395 | -0.20142 | -0.2655 | 0.064087 | 0.48065 | 121.3211 | 112.8616 | 122.7173 | 122.9279 | 0.10529 | 122.9828 | 110.2432 | -0.2655 | 122.9279 | 0.10529 | 110.2432 | 122.7173 | 122.9828 | -123.2941 | -123.1842
962.4062 | 122.8867 | -122.6624 | 0.19226 | 0.012131 | 0.015597 | 0.0088761 | -0.011354 | 0.060968 | -0.004721 | 0.079034 | -122.6303 | 0.19684 | -123.0606 | -122.5662 | 0 | -12.3322 | -1.3962 | -9.8373 | 0.22888 | -122.9965 | -0.39825 | 0.004577 | 0.032044 | 0.096131 | -0.19226 | -0.33417 | 0.036621 | 0.4303 | 121.2662 | 112.825 | 122.6624 | 122.8592 | 0.032044 | 122.8912 | 110.3302 | -0.33417 | 122.8592 | 0.032044 | 110.3302 | 122.6624 | 122.8912 | -123.2529 | -123.1888
964.0938 | 122.8317 | -122.731 | 0.20599 | 0.01976 | 0.018587 | 0.012935 | -0.0062271 | 0.060754 | -0.0060028 | 0.081811 | -122.5662 | 0.1831 | -123.0286 | -122.5021 | 0.027466 | -12.3322 | -1.3733 | -10.4004 | 0.23346 | -122.9645 | -0.29755 | -0.022889 | 0.1648 | 0.22888 | -0.17853 | -0.23346 | 0.027465 | 0.46234 | 121.3577 | 112.3306 | 122.7585 | 122.9141 | 0.1648 | 122.9645 | 110.3989 | -0.23346 | 122.9141 | 0.1648 | 110.3989 | 122.7585 | 122.9645 | -123.2346 | -123.1705
965.8281 | 122.8867 | -122.6761 | 0.19684 | 0.012131 | 0.017733 | 0.0097305 | -0.0034499 | 0.063318 | -0.0092072 | 0.081598 | -122.6807 | 0.2243 | -123.111 | -122.6395 | -0.10071 | -12.9684 | -1.2726 | -10.1486 | 0.28381 | -122.9919 | -0.43488 | 0.027466 | -0.004578 | 0.036621 | -0.29755 | -0.31586 | 0.086975 | 0.4303 | 121.4035 | 112.5275 | 122.5754 | 122.9004 | -0.004578 | 122.9599 | 109.7076 | -0.31586 | 122.9004 | -0.004578 | 109.7076 | 122.5754 | 122.9599 | -123.3078 | -123.1888
967.5781 | 122.9507 | -122.644 | 0.16022 | 0.0045011 | 0.016665 | 0.0080215 | -0.0094315 | 0.061609 | -0.0038666 | 0.079248 | -122.6349 | 0.21057 | -123.0286 | -122.5525 | -0.018311 | -9.5306 | -1.3367 | -10.3638 | 0.24261 | -123.0011 | -0.38452 | 0.050354 | 0.009155 | 0.091553 | -0.17853 | -0.35706 | 0.082398 | 0.39368 | 121.3074 | 112.2803 | 122.6257 | 122.8546 | 0.009155 | 122.8867 | 113.1134 | -0.35706 | 122.8546 | 0.009155 | 113.1134 | 122.6257 | 122.8867 | -123.1888 | -123.1613
969.2656 | 122.9965 | -122.644 | 0.15564 | 0.0045011 | 0.01816 | 0.011867 | -0.0064407 | 0.059473 | -0.0079254 | 0.080529 | -122.6669 | 0.24261 | -123.0789 | -122.6028 | -0.073242 | -0.9201 | -1.4053 | -10.2585 | 0.28381 | -123.0194 | -0.43488 | 0.086975 | -0.022888 | 0.041199 | -0.22888 | -0.37537 | 0.12817 | 0.41199 | 121.2387 | 112.3856 | 122.5708 | 122.8867 | -0.022888 | 122.9279 | 121.7239 | -0.37537 | 122.8867 | -0.022888 | 121.7239 | 122.5708 | 122.9279 | -123.2346 | -123.175
971 | 122.8867 | -122.6852 | 0.19226 | 0.0045011 | 0.018374 | 0.012294 | -0.0045181 | 0.060754 | -0.0068574 | 0.07818 | -122.6715 | 0.21515 | -123.1018 | -122.6166 | -0.086975 | -0.004578 | -1.1993 | -11.1328 | 0.28381 | -123.0148 | -0.41656 | 0.022888 | 0.013733 | 0.068665 | -0.27924 | -0.32959 | 0.091552 | 0.4303 | 121.4859 | 111.5524 | 122.5983 | 122.9004 | 0.013733 | 122.9691 | 122.6807 | -0.32959 | 122.9004 | 0.013733 | 122.6807 | 122.5983 | 122.9691 | -123.2941 | -123.2071
972.75 | 122.8638 | -122.699 | 0.20142 | 0.01976 | 0.016024 | 0.014217 | -0.0045181 | 0.062463 | -0.0066438 | 0.080743 | -122.6715 | 0.22888 | -123.1247 | -122.6166 | -0.091553 | -0.013733 | -1.1307 | -12.6114 | 0.28381 | -123.0057 | -0.42572 | 0.027466 | 0.027466 | 0.082398 | -0.29297 | -0.3067 | 0.082397 | 0.45319 | 121.5683 | 110.0876 | 122.6074 | 122.9279 | 0.027466 | 122.9828 | 122.6852 | -0.3067 | 122.9279 | 0.027466 | 122.6852 | 122.6074 | 122.9828 | -123.3261 | -123.2071
974.5156 | 122.937 | -122.6486 | 0.1831 | 0.0045011 | 0.017519 | 0.012294 | -0.0092179 | 0.060968 | -0.0057892 | 0.078393 | -122.5616 | 0.18768 | -123.0377 | -122.5113 | 0.022888 | 0.16022 | -1.2909 | -12.6022 | 0.25177 | -123.024 | -0.3891 | 0.004578 | 0.086975 | 0.13733 | -0.16022 | -0.37537 | 0.068665 | 0.47607 | 121.3577 | 110.0464 | 122.6715 | 122.8363 | 0.086975 | 122.9004 | 122.8088 | -0.37537 | 122.8363 | 0.086975 | 122.8088 | 122.6715 | 122.9004 | -123.2208 | -123.2071
976.2031 | 122.937 | -122.6624 | 0.14191 | 0.0045011 | 0.017519 | 0.0078079 | -0.0094315 | 0.060327 | -0.0051484 | 0.079461 | -122.6028 | 0.18768 | -123.0377 | -122.525 | 0.022888 | 0.13275 | -1.2451 | -12.4786 | 0.24719 | -122.9736 | -0.37537 | 0.045776 | 0.05951 | 0.13733 | -0.11902 | -0.31128 | 0.10528 | 0.43488 | 121.4172 | 110.1837 | 122.6852 | 122.85 | 0.05951 | 122.9095 | 122.7951 | -0.31128 | 122.85 | 0.05951 | 122.7951 | 122.6852 | 122.9095 | -123.1796 | -123.1155
977.9531 | 122.9416 | -122.6074 | 0.16479 | 0.0045011 | 0.017947 | 0.0043899 | -0.010286 | 0.0599 | -0.00643 | 0.080957 | -122.6395 | 0.20599 | -123.0652 | -122.5571 | -0.018311 | 0.14648 | -1.181 | -13.7375 | 0.23804 | -122.9919 | -0.45776 | 0.041199 | -0.032043 | 0.050354 | -0.18311 | -0.38452 | 0.073242 | 0.42572 | 121.4264 | 108.8699 | 122.5891 | 122.8134 | -0.032043 | 122.8455 | 122.7539 | -0.38452 | 122.8134 | -0.032043 | 122.7539 | 122.5891 | 122.8455 | -123.23 | -123.1567
979.7188 | 122.9187 | -122.6578 | 0.16937 | -0.018387 | 0.016451 | 0.012294 | -0.0083633 | 0.057977 | -0.0049348 | 0.080316 | -122.6257 | 0.19684 | -123.0469 | -122.5479 | -0.036621 | -0.045776 | -1.2039 | -14.3097 | 0.23804 | -123.0057 | -0.3891 | 0.027465 | 0.032044 | 0.10986 | -0.20599 | -0.3479 | 0.068664 | 0.42114 | 121.4539 | 108.3481 | 122.6212 | 122.8546 | 0.032044 | 122.8958 | 122.612 | -0.3479 | 122.8546 | 0.032044 | 122.612 | 122.6212 | 122.8958 | -123.2162 | -123.175
981.4062 | 122.8592 | -122.6715 | 0.21057 | 0.0045011 | 0.017947 | 0.011226 | 0.00018148 | 0.062036 | -0.0077118 | 0.081811 | -122.6532 | 0.2243 | -123.111 | -122.5891 | -0.10529 | 0.041199 | -1.149 | -13.884 | 0.27466 | -123.0011 | -0.43945 | 0.013733 | 0.018311 | 0.082398 | -0.31586 | -0.32959 | 0.064087 | 0.45776 | 121.5225 | 108.7875 | 122.5662 | 122.8958 | 0.018311 | 122.9462 | 122.7127 | -0.32959 | 122.8958 | 0.018311 | 122.7127 | 122.5662 | 122.9462 | -123.3215 | -123.2117
983.0781 | 122.9553 | -122.6257 | 0.14648 | 0.012131 | 0.017733 | 0.0093033 | -0.0079361 | 0.061609 | -0.0038666 | 0.079248 | -122.6074 | 0.20142 | -123.024 | -122.525 | -0.004578 | 0.16479 | -1.3412 | -13.4628 | 0.23346 | -122.9965 | -0.39826 | 0.054932 | 0.01831 | 0.10071 | -0.15106 | -0.37079 | 0.086975 | 0.41657 | 121.2845 | 109.1629 | 122.6212 | 122.8271 | 0.01831 | 122.8592 | 122.7905 | -0.37079 | 122.8271 | 0.01831 | 122.7905 | 122.6212 | 122.8592 | -123.1705 | -123.143
984.8281 | 122.9004 | -122.6578 | 0.17853 | 0.0045011 | 0.015169 | 0.01208 | -0.0066543 | 0.056268 | -0.0038666 | 0.080957 | -122.5754 | 0.19226 | -123.0423 | -122.4747 | 0.032043 | 0.17853 | -1.4694 | -13.8931 | 0.21973 | -122.9828 | -0.38452 | 0.013733 | 0.082398 | 0.18311 | -0.14648 | -0.32501 | 0.041199 | 0.46692 | 121.1884 | 108.7646 | 122.6898 | 122.85 | 0.082398 | 122.8775 | 122.8363 | -0.32501 | 122.85 | 0.082398 | 122.8363 | 122.6898 | 122.8775 | -123.2208 | -123.1613
986.5781 | 122.9462 | -122.6578 | 0.15564 | 0.0045011 | 0.016878 | 0.0058853 | -0.0079361 | 0.057977 | -0.0066438 | 0.079461 | -122.6166 | 0.20142 | -123.0515 | -122.5525 | -0.032043 | 0.15106 | -1.4328 | -13.5544 | 0.24261 | -122.9828 | -0.39368 | 0.045776 | 0.041199 | 0.10529 | -0.18768 | -0.32501 | 0.086975 | 0.43488 | 121.225 | 109.1034 | 122.6257 | 122.8592 | 0.041199 | 122.9004 | 122.8088 | -0.32501 | 122.8592 | 0.041199 | 122.8088 | 122.6257 | 122.9004 | -123.2071 | -123.1384
988.2969 | 122.8226 | -122.6898 | 0.18768 | 0.012131 | 0.017733 | 0.010585 | -0.0019547 | 0.062036 | -0.0062164 | 0.082238 | -122.6212 | 0.21515 | -123.1064 | -122.5433 | -0.064087 | 0.091553 | -1.2497 | -13.7238 | 0.28839 | -122.9645 | -0.41657 | 0.027466 | 0.068664 | 0.14648 | -0.25177 | -0.27466 | 0.10071 | 0.48523 | 121.4401 | 108.9661 | 122.6257 | 122.905 | 0.068664 | 122.9782 | 122.7814 | -0.27466 | 122.905 | 0.068664 | 122.7814 | 122.6257 | 122.9782 | -123.2941 | -123.1522
990.0156 | 122.8592 | -122.6624 | 0.17853 | 0.0045011 | 0.016024 | 0.010158 | -0.0038773 | 0.061609 | -0.007071 | 0.081598 | -122.6669 | 0.22888 | -123.1293 | -122.6212 | -0.13733 | 0.041199 | -1.1169 | -14.2044 | 0.27466 | -122.9874 | -0.46692 | 0.050354 | -0.004577 | 0.041199 | -0.31586 | -0.32501 | 0.09613 | 0.46234 | 121.5454 | 108.4579 | 122.525 | 122.8912 | -0.004577 | 122.937 | 122.7036 | -0.32501 | 122.8912 | -0.004577 | 122.7036 | 122.525 | 122.937 | -123.3078 | -123.1659
991.7812 | 122.9645 | -122.6486 | 0.16022 | -0.0031279 | 0.017306 | 0.0073807 | -0.0060135 | 0.058405 | -0.0062164 | 0.082666 | -122.6761 | 0.24261 | -123.0927 | -122.6074 | -0.086975 | 0.054932 | -1.0345 | -13.7009 | 0.27466 | -123.0057 | -0.44403 | 0.082398 | -0.027465 | 0.041199 | -0.24719 | -0.35705 | 0.11444 | 0.41657 | 121.6141 | 108.9478 | 122.5616 | 122.8912 | -0.027465 | 122.9233 | 122.7036 | -0.35705 | 122.8912 | -0.027465 | 122.7036 | 122.5616 | 122.9233 | -123.2529 | -123.1659
993.4688 | 122.8638 | -122.6761 | 0.18768 | 0.0045011 | 0.018587 | 0.013789 | -0.0049453 | 0.060968 | -0.0040802 | 0.08117 | -122.6624 | 0.2243 | -123.0835 | -122.6074 | -0.10071 | 0.059509 | -1.0391 | -13.6597 | 0.27924 | -122.9828 | -0.40741 | 0.036621 | 0.013732 | 0.068664 | -0.28839 | -0.3067 | 0.091553 | 0.42114 | 121.637 | 109.0164 | 122.5754 | 122.9004 | 0.013732 | 122.9553 | 122.7356 | -0.3067 | 122.9004 | 0.013732 | 122.7356 | 122.5754 | 122.9553 | -123.2712 | -123.1705
995.2188 | 122.9324 | -122.6715 | 0.16937 | 0.0045011 | 0.015597 | 0.0088761 | -0.0072953 | 0.0599 | -0.0034394 | 0.08117 | -122.5845 | 0.18768 | -123.0515 | -122.5113 | -0.018311 | 0.15564 | -1.2131 | -13.3759 | 0.26093 | -122.9965 | -0.37994 | 0.01831 | 0.086975 | 0.16022 | -0.18768 | -0.32501 | 0.091552 | 0.46692 | 121.4584 | 109.2957 | 122.6532 | 122.8592 | 0.086975 | 122.9324 | 122.8271 | -0.32501 | 122.8592 | 0.086975 | 122.8271 | 122.6532 | 122.9324 | -123.2208 | -123.1659
996.9688 | 122.9782 | -122.6395 | 0.17395 | -0.0031279 | 0.019442 | 0.0097305 | -0.0066543 | 0.061182 | -0.0042938 | 0.080316 | -122.6852 | 0.24261 | -123.0881 | -122.6028 | -0.10529 | 0.064087 | -1.0254 | -13.591 | 0.27466 | -123.0286 | -0.44861 | 0.068665 | -0.045777 | 0.036621 | -0.27924 | -0.3891 | 0.10071 | 0.40283 | 121.6141 | 109.0485 | 122.5342 | 122.8821 | -0.045777 | 122.9141 | 122.7036 | -0.3891 | 122.8821 | -0.045777 | 122.7036 | 122.5342 | 122.9141 | -123.262 | -123.2025
998.6562 | 122.9324 | -122.6349 | 0.15106 | 0.0045011 | 0.015597 | 0.0078079 | -0.011354 | 0.058405 | -0.0077118 | 0.082452 | -122.6303 | 0.19226 | -123.0423 | -122.5204 | -0.004578 | 0.17395 | -1.3779 | -12.3962 | 0.24261 | -122.9645 | -0.40741 | 0.041199 | 0.004578 | 0.11444 | -0.15564 | -0.32959 | 0.091553 | 0.41199 | 121.257 | 110.2386 | 122.6303 | 122.8271 | 0.004578 | 122.8775 | 122.8088 | -0.32959 | 122.8271 | 0.004578 | 122.8088 | 122.6303 | 122.8775 | -123.1934 | -123.1155
1000.4062 | 122.8088 | -122.6807 | 0.20142 | -0.010757 | 0.016238 | 0.0097305 | -0.0053727 | 0.061609 | -0.004721 | 0.080102 | -122.5433 | 0.19226 | -123.0377 | -122.4792 | -0.004578 | 0.20599 | -1.3046 | -12.8128 | 0.21973 | -122.9828 | -0.35706 | -0.009155 | 0.13733 | 0.20142 | -0.20599 | -0.30212 | 0.018311 | 0.49438 | 121.376 | 109.8679 | 122.6761 | 122.8729 | 0.13733 | 122.9004 | 122.8867 | -0.30212 | 122.8729 | 0.13733 | 122.8867 | 122.6761 | 122.9004 | -123.2391 | -123.1842
1002.1562 | 122.9462 | -122.6257 | 0.15564 | -0.010757 | 0.016024 | 0.0086625 | -0.0087905 | 0.058191 | -0.0049348 | 0.079889 | -122.6303 | 0.20599 | -123.0423 | -122.5479 | -0.064087 | 0.15106 | -1.236 | -12.6526 | 0.25177 | -122.9874 | -0.41657 | 0.050354 | -0.004578 | 0.077819 | -0.21973 | -0.36163 | 0.09613 | 0.41199 | 121.3898 | 109.9731 | 122.5616 | 122.8317 | -0.004578 | 122.8775 | 122.7768 | -0.36163 | 122.8317 | -0.004578 | 122.7768 | 122.5616 | 122.8775 | -123.1979 | -123.143
1003.8438 | 122.8867 | -122.6578 | 0.16937 | -0.0031279 | 0.012179 | 0.011653 | -0.0072953 | 0.060541 | -0.0051484 | 0.082666 | -122.5937 | 0.17395 | -123.0652 | -122.5296 | -0.045776 | 0.16479 | -1.3962 | -12.5336 | 0.2243 | -122.9507 | -0.40741 | 0.004577 | 0.064087 | 0.12817 | -0.21515 | -0.29297 | 0.054931 | 0.4715 | 121.2616 | 110.1242 | 122.612 | 122.8317 | 0.064087 | 122.8821 | 122.8226 | -0.29297 | 122.8317 | 0.064087 | 122.8226 | 122.612 | 122.8821 | -123.2346 | -123.1201
1005.5781 | 122.9141 | -122.644 | 0.15564 | -0.0031279 | 0.016451 | 0.010799 | -0.010286 | 0.059259 | -0.00643 | 0.082238 | -122.6074 | 0.17395 | -123.0148 | -122.5342 | -0.050354 | 0.16022 | -1.3504 | -12.5702 | 0.24719 | -122.9874 | -0.37079 | 0.01831 | 0.036621 | 0.10986 | -0.20599 | -0.34332 | 0.091552 | 0.40741 | 121.2936 | 110.0739 | 122.5937 | 122.818 | 0.036621 | 122.8912 | 122.8043 | -0.34332 | 122.818 | 0.036621 | 122.8043 | 122.5937 | 122.8912 | -123.1705 | -123.143
1007.2656 | 122.9507 | -122.6303 | 0.16022 | 0.01976 | 0.017092 | 0.0080215 | -0.0023819 | 0.060541 | -0.0083526 | 0.078607 | -122.6761 | 0.22888 | -123.111 | -122.5754 | -0.11444 | 0.059509 | -1.2177 | -12.2635 | 0.27466 | -122.9828 | -0.48065 | 0.068665 | -0.045776 | 0.054932 | -0.27466 | -0.35248 | 0.11444 | 0.43488 | 121.4127 | 110.3668 | 122.5159 | 122.8592 | -0.045776 | 122.905 | 122.6898 | -0.35248 | 122.8592 | -0.045776 | 122.6898 | 122.5159 | 122.905 | -123.2712 | -123.143
1009.0156 | 122.9416 | -122.6257 | 0.16022 | -0.0031279 | 0.019228 | 0.011012 | -0.0049453 | 0.0599 | -0.0066438 | 0.079889 | -122.6532 | 0.25177 | -123.0698 | -122.5662 | -0.11902 | 0.073242 | -1.2955 | -12.3367 | 0.27924 | -123.0057 | -0.44403 | 0.091553 | -0.027466 | 0.059509 | -0.27924 | -0.37994 | 0.11902 | 0.41656 | 121.3303 | 110.289 | 122.5067 | 122.8775 | -0.027466 | 122.905 | 122.699 | -0.37994 | 122.8775 | -0.027466 | 122.699 | 122.5067 | 122.905 | -123.23 | -123.1659
1010.6875 | 122.8363 | -122.6761 | 0.19684 | -0.010757 | 0.015383 | 0.012508 | -0.0032363 | 0.061609 | -0.0077118 | 0.079461 | -122.6257 | 0.21973 | -123.0881 | -122.5708 | -0.09613 | 0.086975 | -1.3596 | -12.41 | 0.26093 | -122.9645 | -0.41199 | 0.022889 | 0.050354 | 0.10528 | -0.29297 | -0.28839 | 0.064087 | 0.46234 | 121.3165 | 110.2661 | 122.58 | 122.8958 | 0.050354 | 122.937 | 122.7631 | -0.28839 | 122.8958 | 0.050354 | 122.7631 | 122.58 | 122.937 | -123.2849 | -123.1613
1012.4375 | 122.8363 | -122.6486 | 0.19684 | 0.0045011 | 0.016878 | 0.0073807 | -0.0049453 | 0.063959 | -0.0057892 | 0.079675 | -122.644 | 0.24719 | -123.0789 | -122.5937 | -0.07782 | 0.10071 | -1.3641 | -12.6938 | 0.27008 | -122.9874 | -0.4303 | 0.050354 | 0.004578 | 0.054932 | -0.27466 | -0.33874 | 0.073243 | 0.43488 | 121.2845 | 109.9548 | 122.5708 | 122.8958 | 0.004578 | 122.9187 | 122.7493 | -0.33874 | 122.8958 | 0.004578 | 122.7493 | 122.5708 | 122.9187 | -123.2758 | -123.1842
1014.2031 | 122.8271 | -122.6715 | 0.19684 | 0.012131 | 0.016451 | 0.010585 | -0.0051589 | 0.061823 | -0.0074982 | 0.080316 | -122.6257 | 0.23346 | -123.0972 | -122.5388 | -0.073242 | 0.11444 | -1.3229 | -12.735 | 0.27924 | -122.9507 | -0.42572 | 0.036621 | 0.045777 | 0.13275 | -0.27008 | -0.27924 | 0.082398 | 0.4715 | 121.3486 | 109.9365 | 122.5983 | 122.905 | 0.045777 | 122.9507 | 122.7859 | -0.27924 | 122.905 | 0.045777 | 122.7859 | 122.5983 | 122.9507 | -123.2941 | -123.1476
1015.9531 | 122.9095 | -122.6532 | 0.17853 | -0.0031279 | 0.015597 | 0.0060989 | -0.012422 | 0.061609 | -0.0023712 | 0.080316 | -122.5891 | 0.19226 | -123.024 | -122.5021 | 0.013733 | 0.21973 | -1.3275 | -12.3001 | 0.24261 | -123.0194 | -0.37079 | 0.013733 | 0.064087 | 0.15106 | -0.16479 | -0.36621 | 0.064087 | 0.43488 | 121.3257 | 110.3531 | 122.6669 | 122.8455 | 0.064087 | 122.8958 | 122.8729 | -0.36621 | 122.8455 | 0.064087 | 122.8729 | 122.6669 | 122.8958 | -123.2025 | -123.1979
1017.625 | 122.85 | -122.6624 | 0.17395 | 0.012131 | 0.017092 | 0.011012 | -0.0043045 | 0.060754 | -0.0079254 | 0.080316 | -122.6852 | 0.2243 | -123.0927 | -122.6212 | -0.13275 | 0.050354 | -1.2177 | -12.5656 | 0.28381 | -122.9645 | -0.4303 | 0.050354 | -0.022888 | 0.041199 | -0.3067 | -0.30212 | 0.10986 | 0.40741 | 121.4447 | 110.0967 | 122.5296 | 122.8867 | -0.022888 | 122.9462 | 122.7127 | -0.30212 | 122.8867 | -0.022888 | 122.7127 | 122.5296 | 122.9462 | -123.2666 | -123.1384
1019.3906 | 122.9095 | -122.612 | 0.16937 | 0.012131 | 0.014315 | 0.0097305 | -0.011568 | 0.059473 | -0.0032258 | 0.080957 | -122.6303 | 0.21515 | -123.024 | -122.5433 | -0.059509 | 0.16022 | -1.3138 | -12.2772 | 0.24261 | -122.9919 | -0.41199 | 0.045776 | -0.01831 | 0.068665 | -0.22888 | -0.37994 | 0.073242 | 0.39368 | 121.2982 | 110.3348 | 122.5525 | 122.8271 | -0.01831 | 122.8546 | 122.7722 | -0.37994 | 122.8271 | -0.01831 | 122.7722 | 122.5525 | 122.8546 | -123.1934 | -123.1613
1021.0781 | 122.8683 | -122.6715 | 0.19684 | 0.012131 | 0.014742 | 0.0075943 | -0.0036637 | 0.060754 | -0.0055756 | 0.082879 | -122.6669 | 0.23346 | -123.1155 | -122.6074 | -0.13733 | 0.041199 | -1.2268 | -12.5015 | 0.2655 | -123.024 | -0.44403 | 0.036621 | 0.004578 | 0.064087 | -0.33417 | -0.35248 | 0.068665 | 0.44861 | 121.4447 | 110.17 | 122.5342 | 122.905 | 0.004578 | 122.937 | 122.7127 | -0.35248 | 122.905 | 0.004578 | 122.7127 | 122.5342 | 122.937 | -123.3124 | -123.2208
1022.8125 | 122.8867 | -122.644 | 0.17395 | 0.0045011 | 0.014742 | 0.0071671 | -0.0098587 | 0.059259 | -0.00643 | 0.07818 | -122.5754 | 0.19226 | -123.0331 | -122.4976 | 0.009155 | 0.20142 | -1.3962 | -11.7599 | 0.24261 | -122.9736 | -0.3891 | 0.018311 | 0.068665 | 0.14648 | -0.16479 | -0.32959 | 0.068665 | 0.45776 | 121.2479 | 110.8841 | 122.6532 | 122.8363 | 0.068665 | 122.8867 | 122.8455 | -0.32959 | 122.8363 | 0.068665 | 122.8455 | 122.6532 | 122.8867 | -123.2071 | -123.1476
1024.5625 | 122.8043 | -122.6761 | 0.1831 | 0.012131 | 0.016024 | 0.0067399 | -0.0070815 | 0.062891 | -0.007071 | 0.082238 | -122.5525 | 0.19226 | -123.0423 | -122.4976 | -0.018311 | 0.20142 | -1.4694 | -12.9364 | 0.22888 | -122.9645 | -0.36621 | 0.009156 | 0.1236 | 0.17853 | -0.20142 | -0.28839 | 0.045777 | 0.48981 | 121.2067 | 109.7397 | 122.6578 | 122.8683 | 0.1236 | 122.905 | 122.8775 | -0.28839 | 122.8683 | 0.1236 | 122.8775 | 122.6578 | 122.905 | -123.2254 | -123.1476
1026.3125 | 122.9462 | -122.6028 | 0.17395 | 0.012131 | 0.015169 | 0.0054581 | -0.0049453 | 0.059045 | -0.0060028 | 0.079248 | -122.6578 | 0.21973 | -123.0927 | -122.5891 | -0.11444 | 0.050354 | -1.1261 | -12.886 | 0.29755 | -123.0011 | -0.48981 | 0.045777 | -0.054932 | 0.013733 | -0.28839 | -0.39825 | 0.1236 | 0.43488 | 121.4767 | 109.7168 | 122.4884 | 122.8226 | -0.054932 | 122.9004 | 122.6532 | -0.39825 | 122.8226 | -0.054932 | 122.6532 | 122.4884 | 122.9004 | -123.2666 | -123.175
1028.0625 | 122.8088 | -122.6624 | 0.20142 | 0.0045011 | 0.016024 | 0.0075943 | -0.0030227 | 0.063104 | -0.0079254 | 0.081598 | -122.6074 | 0.23804 | -123.0743 | -122.525 | -0.073242 | 0.09613 | -1.7166 | -12.2177 | 0.27008 | -122.9553 | -0.41199 | 0.036621 | 0.054932 | 0.13733 | -0.27466 | -0.29297 | 0.068665 | 0.46692 | 120.9457 | 110.4446 | 122.5891 | 122.9004 | 0.054932 | 122.9324 | 122.7585 | -0.29297 | 122.9004 | 0.054932 | 122.7585 | 122.5891 | 122.9324 | -123.2758 | -123.1567
1029.75 | 122.9233 | -122.612 | 0.16937 | 0.0045011 | 0.017733 | 0.0071671 | -0.0077225 | 0.060541 | -0.004721 | 0.080529 | -122.6532 | 0.25177 | -123.056 | -122.5754 | -0.10071 | 0.059509 | -1.442 | -12.2269 | 0.27924 | -122.9965 | -0.44403 | 0.082397 | -0.041198 | 0.036622 | -0.27008 | -0.38452 | 0.10986 | 0.40283 | 121.17 | 110.3851 | 122.5113 | 122.8638 | -0.041198 | 122.8912 | 122.6715 | -0.38452 | 122.8638 | -0.041198 | 122.6715 | 122.5113 | 122.8912 | -123.2254 | -123.1659
1031.5 | 122.9553 | -122.612 | 0.16479 | -0.0031279 | 0.018801 | 0.0082351 | -0.0068679 | 0.0599 | -0.0057892 | 0.080316 | -122.6624 | 0.2243 | -123.0927 | -122.5937 | -0.10071 | 0.064087 | -1.4008 | -12.1765 | 0.28839 | -122.9965 | -0.48065 | 0.059509 | -0.050354 | 0.018311 | -0.2655 | -0.38452 | 0.1236 | 0.4303 | 121.2112 | 110.4355 | 122.5113 | 122.8363 | -0.050354 | 122.9004 | 122.6761 | -0.38452 | 122.8363 | -0.050354 | 122.6761 | 122.5113 | 122.9004 | -123.2574 | -123.1613
1033.1875 | 122.8455 | -122.6578 | 0.16022 | -0.0031279 | 0.019442 | 0.011012 | -0.0043045 | 0.060114 | -0.0072846 | 0.080743 | -122.6624 | 0.23346 | -123.0835 | -122.6166 | -0.13275 | 0.068665 | -1.1398 | -12.1811 | 0.27008 | -122.9828 | -0.42572 | 0.073242 | -0.004578 | 0.041199 | -0.29297 | -0.32501 | 0.10986 | 0.42114 | 121.5179 | 110.4767 | 122.525 | 122.8912 | -0.004578 | 122.9279 | 122.7264 | -0.32501 | 122.8912 | -0.004578 | 122.7264 | 122.525 | 122.9279 | -123.2437 | -123.143
1034.9375 | 122.9141 | -122.6303 | 0.14191 | -0.0031279 | 0.019015 | 0.0078079 | -0.0070815 | 0.059473 | -0.0038666 | 0.079889 | -122.5983 | 0.20599 | -123.0286 | -122.5433 | -0.059509 | 0.10071 | -1.1673 | -12.2635 | 0.25635 | -123.0057 | -0.39825 | 0.064087 | 0.032043 | 0.086975 | -0.20142 | -0.37537 | 0.11444 | 0.4303 | 121.463 | 110.3668 | 122.5708 | 122.8363 | 0.032043 | 122.8867 | 122.731 | -0.37537 | 122.8363 | 0.032043 | 122.731 | 122.5708 | 122.8867 | -123.1705 | -123.1476
1036.6875 | 122.7997 | -122.6624 | 0.19226 | 0.0045011 | 0.017092 | 0.010158 | -0.0081497 | 0.060754 | -0.0027984 | 0.079034 | -122.5388 | 0.17853 | -123.0423 | -122.4976 | 0.009155 | 0.21057 | -1.2909 | -11.9293 | 0.2243 | -122.9599 | -0.37994 | -0.013733 | 0.1236 | 0.16479 | -0.18311 | -0.29755 | 0.032043 | 0.50354 | 121.3715 | 110.733 | 122.6715 | 122.8409 | 0.1236 | 122.8867 | 122.8729 | -0.29755 | 122.8409 | 0.1236 | 122.8729 | 122.6715 | 122.8867 | -123.2346 | -123.1522
1038.4375 | 122.8455 | -122.6486 | 0.16022 | 0.012131 | 0.017733 | 0.011226 | -0.0049453 | 0.059686 | -0.0040802 | 0.081598 | -122.6578 | 0.24261 | -123.0698 | -122.6028 | -0.12817 | 0.082397 | -2.1332 | -12.7533 | 0.27466 | -123.0194 | -0.42114 | 0.082398 | -0.009155 | 0.045777 | -0.28839 | -0.37079 | 0.11444 | 0.41199 | 120.5154 | 109.8953 | 122.5204 | 122.8912 | -0.009155 | 122.9233 | 122.731 | -0.37079 | 122.8912 | -0.009155 | 122.731 | 122.5204 | 122.9233 | -123.23 | -123.1796
1040.1875 | 122.937 | -122.6074 | 0.17395 | 0.0045011 | 0.017733 | 0.010799 | -0.0072953 | 0.060754 | -0.0049348 | 0.079889 | -122.6074 | 0.20599 | -123.0469 | -122.5571 | -0.068665 | 0.10071 | -1.973 | -12.3322 | 0.26093 | -122.9965 | -0.43945 | 0.032044 | 0 | 0.050354 | -0.24261 | -0.3891 | 0.086975 | 0.43945 | 120.6345 | 110.2753 | 122.5388 | 122.8134 | 0 | 122.8683 | 122.7081 | -0.3891 | 122.8134 | 0 | 122.7081 | 122.5388 | 122.8683 | -123.2208 | -123.1705
1041.9219 | 122.8409 | -122.644 | 0.18768 | -0.0031279 | 0.019228 | 0.0095169 | -0.0040909 | 0.063104 | -0.0085664 | 0.080316 | -122.644 | 0.21057 | -123.0743 | -122.5845 | -0.10986 | 0.073242 | -1.8311 | -12.2543 | 0.2655 | -122.9416 | -0.4303 | 0.022888 | 0 | 0.059509 | -0.29755 | -0.29755 | 0.07782 | 0.4303 | 120.813 | 110.3897 | 122.5342 | 122.8546 | 0 | 122.9095 | 122.7173 | -0.29755 | 122.8546 | 0 | 122.7173 | 122.5342 | 122.9095 | -123.262 | -123.1293
1043.6562 | 122.9279 | -122.6395 | 0.15564 | -0.0031279 | 0.017947 | 0.010371 | -0.0068679 | 0.062036 | -0.0060028 | 0.080957 | -122.6578 | 0.22888 | -123.0652 | -122.5845 | -0.10071 | 0.064087 | -1.7075 | -11.998 | 0.29297 | -122.9965 | -0.42572 | 0.073242 | -0.018311 | 0.054931 | -0.25635 | -0.35706 | 0.13733 | 0.40741 | 120.932 | 110.6415 | 122.5388 | 122.8683 | -0.018311 | 122.9324 | 122.7036 | -0.35706 | 122.8683 | -0.018311 | 122.7036 | 122.5388 | 122.9324 | -123.2208 | -123.1522
1045.3438 | 122.8683 | -122.6212 | 0.17853 | 0.0045011 | 0.018801 | 0.0054581 | -0.012209 | 0.060754 | -0.0042938 | 0.080957 | -122.58 | 0.19226 | -123.0194 | -122.525 | -0.045776 | 0.14648 | -16.2369 | -12.9547 | 0.24261 | -122.9874 | -0.39825 | 0.013733 | 0.041199 | 0.096131 | -0.2243 | -0.36621 | 0.064087 | 0.43945 | 106.3843 | 109.6664 | 122.5754 | 122.8134 | 0.041199 | 122.8638 | 122.7676 | -0.36621 | 122.8134 | 0.041199 | 122.7676 | 122.5754 | 122.8638 | -123.1979 | -123.1659
1047.0938 | 122.818 | -122.6715 | 0.1831 | 0.012131 | 0.017519 | 0.0082351 | -0.0019547 | 0.061609 | -0.0057892 | 0.080529 | -122.6257 | 0.22888 | -123.056 | -122.5433 | -0.091553 | 0.086975 | -15.683 | -12.8357 | 0.2655 | -122.9782 | -0.38452 | 0.045777 | 0.045777 | 0.12817 | -0.27466 | -0.3067 | 0.082398 | 0.4303 | 106.9885 | 109.8358 | 122.58 | 122.9004 | 0.045777 | 122.937 | 122.7585 | -0.3067 | 122.9004 | 0.045777 | 122.7585 | 122.58 | 122.937 | -123.2391 | -123.1613
1048.7656 | 122.8088 | -122.6532 | 0.19684 | 0.0045011 | 0.017519 | 0.010371 | -0.0051589 | 0.061823 | -0.0074982 | 0.080743 | -122.58 | 0.2243 | -123.056 | -122.5296 | -0.073242 | 0.11444 | -16.1316 | -12.9776 | 0.2655 | -122.9599 | -0.40283 | 0.027466 | 0.073242 | 0.1236 | -0.27008 | -0.3067 | 0.068665 | 0.47607 | 106.5216 | 109.6756 | 122.58 | 122.8775 | 0.073242 | 122.9187 | 122.7676 | -0.3067 | 122.8775 | 0.073242 | 122.7676 | 122.58 | 122.9187 | -123.2529 | -123.1567
1050.5156 | 122.8729 | -122.6395 | 0.17395 | 0.0045011 | 0.016451 | 0.0093033 | -0.012209 | 0.0599 | -0.0025848 | 0.079889 | -122.5571 | 0.21515 | -123.0103 | -122.4564 | 0.018311 | 0.21057 | -16.2094 | -12.5656 | 0.2243 | -122.9645 | -0.37079 | 0.041199 | 0.082397 | 0.1831 | -0.15564 | -0.32501 | 0.050354 | 0.45319 | 106.4301 | 110.0739 | 122.6578 | 122.8546 | 0.082397 | 122.8638 | 122.85 | -0.32501 | 122.8546 | 0.082397 | 122.85 | 122.6578 | 122.8638 | -123.1842 | -123.1384
1052.2656 | 122.8043 | -122.6669 | 0.19226 | 0.012131 | 0.018801 | 0.011226 | -0.0047317 | 0.059473 | -0.007071 | 0.081811 | -122.6028 | 0.21515 | -123.0972 | -122.5296 | -0.064087 | 0.10529 | -1.8631 | -11.8698 | 0.27008 | -122.9553 | -0.4303 | 0.022888 | 0.064087 | 0.13733 | -0.25635 | -0.28839 | 0.07782 | 0.49438 | 120.8038 | 110.7971 | 122.6028 | 122.8821 | 0.064087 | 122.937 | 122.7722 | -0.28839 | 122.8821 | 0.064087 | 122.7722 | 122.6028 | 122.937 | -123.2895 | -123.1476
1054.0156 | 122.8958 | -122.6028 | 0.16479 | -0.0031279 | 0.016451 | 0.0078079 | -0.011995 | 0.058405 | -0.0055756 | 0.079675 | -122.5845 | 0.19226 | -123.0148 | -122.5525 | -0.013733 | 0.14191 | -1.9318 | -12.0026 | 0.24719 | -122.9691 | -0.41199 | 0.027466 | 0.01831 | 0.050354 | -0.17853 | -0.36621 | 0.082397 | 0.4303 | 120.6711 | 110.6003 | 122.5891 | 122.7951 | 0.01831 | 122.85 | 122.7448 | -0.36621 | 122.7951 | 0.01831 | 122.7448 | 122.5891 | 122.85 | -123.1796 | -123.1338
1055.7188 | 122.8821 | -122.6212 | 0.16479 | 0.012131 | 0.014315 | 0.011439 | -0.010072 | 0.059045 | -0.00643 | 0.079034 | -122.5571 | 0.17853 | -123.0194 | -122.4609 | 0.022888 | 0.20599 | -1.7761 | -10.4782 | 0.23346 | -122.9553 | -0.39825 | 0.013733 | 0.064087 | 0.16022 | -0.14191 | -0.33417 | 0.068664 | 0.46234 | 120.845 | 112.1429 | 122.644 | 122.7997 | 0.064087 | 122.8546 | 122.8271 | -0.33417 | 122.7997 | 0.064087 | 122.8271 | 122.644 | 122.8546 | -123.1842 | -123.1201
1057.4531 | 122.8546 | -122.6395 | 0.15564 | -0.0031279 | 0.017306 | 0.011012 | -0.0066543 | 0.061182 | -0.0049348 | 0.082238 | -122.5845 | 0.19226 | -122.9965 | -122.5296 | -0.022888 | 0.15106 | -1.4877 | -10.7162 | 0.25177 | -122.9599 | -0.35706 | 0.036621 | 0.054931 | 0.10986 | -0.17853 | -0.32044 | 0.09613 | 0.41199 | 121.1517 | 111.9232 | 122.6166 | 122.8317 | 0.054931 | 122.8912 | 122.7905 | -0.32044 | 122.8317 | 0.054931 | 122.7905 | 122.6166 | 122.8912 | -123.1522 | -123.1155
1059.2031 | 122.8455 | -122.612 | 0.17395 | 0.0045011 | 0.016451 | 0.011012 | -0.0066543 | 0.060754 | -0.0062164 | 0.079034 | -122.5662 | 0.20599 | -123.0103 | -122.5159 | -0.027466 | 0.15564 | -1.5335 | -6.0242 | 0.25177 | -122.9507 | -0.39825 | 0.032044 | 0.045777 | 0.096131 | -0.20142 | -0.33875 | 0.07782 | 0.44403 | 121.0785 | 116.5878 | 122.5845 | 122.818 | 0.045777 | 122.8638 | 122.7676 | -0.33875 | 122.818 | 0.045777 | 122.7676 | 122.5845 | 122.8638 | -123.1842 | -123.1247
1060.9531 | 122.7951 | -122.6624 | 0.19684 | -0.010757 | 0.020296 | 0.0084489 | -0.0017411 | 0.063959 | -0.00643 | 0.079034 | -122.5754 | 0.22888 | -123.056 | -122.5159 | -0.041199 | 0.10071 | -1.4694 | -5.658 | 0.27924 | -122.9782 | -0.39368 | 0.032044 | 0.086976 | 0.14648 | -0.23804 | -0.31586 | 0.082398 | 0.48065 | 121.1929 | 117.0044 | 122.6212 | 122.8912 | 0.086976 | 122.9416 | 122.7631 | -0.31586 | 122.8912 | 0.086976 | 122.7631 | 122.6212 | 122.9416 | -123.2529 | -123.175
1062.7031 | 122.818 | -122.6807 | 0.19226 | -0.0031279 | 0.019442 | 0.0073807 | -0.0038773 | 0.060968 | -0.0062164 | 0.082025 | -122.6532 | 0.2243 | -123.0698 | -122.5891 | -0.091553 | 0.073242 | -1.3962 | -5.5893 | 0.28839 | -122.9645 | -0.3891 | 0.032043 | 0.027466 | 0.091553 | -0.28381 | -0.28381 | 0.09613 | 0.41656 | 121.2845 | 117.0914 | 122.5891 | 122.905 | 0.027466 | 122.9691 | 122.7539 | -0.28381 | 122.905 | 0.027466 | 122.7539 | 122.5891 | 122.9691 | -123.262 | -123.1567
1064.3906 | 122.7905 | -122.6715 | 0.20142 | 0.0045011 | 0.016238 | 0.0073807 | -0.0045181 | 0.062463 | -0.0066438 | 0.082025 | -122.6074 | 0.23346 | -123.0789 | -122.5479 | -0.073242 | 0.07782 | -1.3138 | -5.191 | 0.27924 | -122.9553 | -0.40741 | 0.032043 | 0.064087 | 0.1236 | -0.27466 | -0.28381 | 0.07782 | 0.4715 | 121.3577 | 117.4805 | 122.5983 | 122.905 | 0.064087 | 122.9507 | 122.7493 | -0.28381 | 122.905 | 0.064087 | 122.7493 | 122.5983 | 122.9507 | -123.2803 | -123.1567
1066.1406 | 122.9187 | -122.6074 | 0.16937 | 0.0045011 | 0.015597 | 0.0058853 | -0.011995 | 0.059686 | -0.005362 | 0.078607 | -122.6166 | 0.21515 | -123.0194 | -122.5204 | -0.022888 | 0.14191 | -1.5701 | -6.8024 | 0.25177 | -122.9828 | -0.41199 | 0.045776 | -0.009155 | 0.086975 | -0.19226 | -0.37537 | 0.082397 | 0.40283 | 121.0373 | 115.8051 | 122.5845 | 122.8226 | -0.009155 | 122.8592 | 122.7493 | -0.37537 | 122.8226 | -0.009155 | 122.7493 | 122.5845 | 122.8592 | -123.1888 | -123.1522
1067.8906 | 122.9141 | -122.5983 | 0.15564 | 0.0045011 | 0.017519 | 0.0078079 | -0.010286 | 0.058832 | -0.0045074 | 0.079889 | -122.6074 | 0.21057 | -123.0194 | -122.5296 | -0.018311 | 0.14191 | -1.4236 | -4.9667 | 0.22888 | -122.9736 | -0.42114 | 0.054931 | -0.009155 | 0.068665 | -0.17395 | -0.37537 | 0.073242 | 0.41199 | 121.1746 | 117.6315 | 122.58 | 122.8088 | -0.009155 | 122.8271 | 122.7402 | -0.37537 | 122.8088 | -0.009155 | 122.7402 | 122.58 | 122.8271 | -123.175 | -123.1293
1069.5781 | 122.9141 | -122.612 | 0.17395 | 0.012131 | 0.01816 | 0.01208 | -0.0043045 | 0.059473 | -0.00643 | 0.080102 | -122.644 | 0.23804 | -123.111 | -122.5525 | -0.07782 | 0.059509 | -1.4282 | -4.3442 | 0.27924 | -122.9782 | -0.49896 | 0.064087 | -0.032043 | 0.05951 | -0.25177 | -0.36621 | 0.10529 | 0.46692 | 121.1838 | 118.2678 | 122.5342 | 122.85 | -0.032043 | 122.8912 | 122.6715 | -0.36621 | 122.85 | -0.032043 | 122.6715 | 122.5342 | 122.8912 | -123.2849 | -123.1522
1071.3438 | 122.818 | -122.6532 | 0.19684 | 0.0045011 | 0.016238 | 0.0058853 | -0.0028091 | 0.061182 | -0.0057892 | 0.082025 | -122.6395 | 0.21515 | -123.0743 | -122.5754 | -0.082397 | 0.050354 | -1.4786 | -4.4495 | 0.2655 | -122.9599 | -0.42114 | 0.018311 | 0.013733 | 0.07782 | -0.27924 | -0.3067 | 0.068665 | 0.43488 | 121.1746 | 118.2037 | 122.5708 | 122.8683 | 0.013733 | 122.9187 | 122.7036 | -0.3067 | 122.8683 | 0.013733 | 122.7036 | 122.5708 | 122.9187 | -123.2712 | -123.1567
1073.0781 | 122.818 | -122.644 | 0.19684 | 0.0045011 | 0.016451 | 0.010158 | -0.0055863 | 0.062036 | -0.0040802 | 0.080743 | -122.6486 | 0.23346 | -123.0606 | -122.5571 | -0.07782 | 0.09613 | -1.5015 | -4.1748 | 0.2655 | -122.9416 | -0.41657 | 0.036621 | -0.004578 | 0.086975 | -0.27466 | -0.29755 | 0.068665 | 0.41199 | 121.1426 | 118.4692 | 122.5662 | 122.8775 | -0.004578 | 122.9095 | 122.7402 | -0.29755 | 122.8775 | -0.004578 | 122.7402 | 122.5662 | 122.9095 | -123.2574 | -123.1384
1074.8281 | 122.8363 | -122.6532 | 0.17395 | 0.0045011 | 0.016665 | 0.0073807 | -0.0043045 | 0.061823 | -0.0068574 | 0.079461 | -122.644 | 0.21973 | -123.056 | -122.5845 | -0.07782 | 0.068665 | -1.4969 | -3.0579 | 0.2655 | -122.9691 | -0.40283 | 0.045777 | 0.009155 | 0.068664 | -0.25177 | -0.31586 | 0.091553 | 0.41199 | 121.1563 | 119.5953 | 122.5754 | 122.8729 | 0.009155 | 122.9187 | 122.7219 | -0.31586 | 122.8729 | 0.009155 | 122.7219 | 122.5754 | 122.9187 | -123.23 | -123.143
1076.5156 | 122.9233 | -122.5983 | 0.16479 | 0.012131 | 0.01581 | 0.0033219 | -0.0072953 | 0.058832 | -0.0074982 | 0.080743 | -122.6807 | 0.22888 | -123.0652 | -122.5754 | -0.064087 | 0.064087 | -1.4282 | -2.3941 | 0.29755 | -123.0057 | -0.46692 | 0.064087 | -0.082397 | 0.022889 | -0.22888 | -0.40741 | 0.13275 | 0.38452 | 121.17 | 120.2042 | 122.5342 | 122.8271 | -0.082397 | 122.8958 | 122.6624 | -0.40741 | 122.8271 | -0.082397 | 122.6624 | 122.5342 | 122.8958 | -123.23 | -123.1705
1078.2656 | 122.7859 | -122.6349 | 0.18768 | 0.0045011 | 0.016878 | 0.012294 | -0.0032363 | 0.061823 | -0.005362 | 0.082238 | -122.5983 | 0.2243 | -123.0652 | -122.5388 | -0.027466 | -0.28839 | -1.4191 | -2.0599 | 0.27466 | -122.9416 | -0.4303 | 0.036621 | 0.036621 | 0.096131 | -0.21515 | -0.3067 | 0.086975 | 0.46692 | 121.2158 | 120.575 | 122.6074 | 122.8592 | 0.036621 | 122.9095 | 122.3465 | -0.3067 | 122.8592 | 0.036621 | 122.3465 | 122.6074 | 122.9095 | -123.2529 | -123.1293
1080.0156 | 122.9233 | -122.6028 | 0.16022 | -0.010757 | 0.017519 | 0.0088761 | -0.0085769 | 0.060968 | -0.0060028 | 0.079675 | -122.6166 | 0.22888 | -123.0377 | -122.5708 | -0.050354 | -0.28839 | -1.3184 | -2.005 | 0.27924 | -122.9965 | -0.43488 | 0.068665 | -0.013733 | 0.032043 | -0.21057 | -0.39368 | 0.11902 | 0.42114 | 121.2845 | 120.5978 | 122.5525 | 122.8317 | -0.013733 | 122.8821 | 122.3145 | -0.39368 | 122.8317 | -0.013733 | 122.3145 | 122.5525 | 122.8821 | -123.1979 | -123.1567
1081.7656 | 122.9095 | -122.5983 | 0.15106 | 0.0045011 | 0.015169 | 0.0084489 | -0.010286 | 0.060541 | -0.003653 | 0.07818 | -122.6074 | 0.20599 | -123.0148 | -122.525 | -0.004578 | 0.14191 | -1.4832 | -2.1332 | 0.25177 | -122.9553 | -0.41656 | 0.054932 | -0.009155 | 0.073243 | -0.15564 | -0.35705 | 0.10071 | 0.40741 | 121.1151 | 120.4651 | 122.5937 | 122.8043 | -0.009155 | 122.85 | 122.7402 | -0.35705 | 122.8043 | -0.009155 | 122.7402 | 122.5937 | 122.85 | -123.1659 | -123.1064
1083.4375 | 122.9279 | -122.612 | 0.16022 | -0.0031279 | 0.014742 | 0.0069535 | -0.0075089 | 0.057977 | -0.0057892 | 0.07882 | -122.6395 | 0.22888 | -123.0743 | -122.5708 | -0.050354 | -0.34332 | -1.4511 | -2.1469 | 0.27466 | -123.0057 | -0.46234 | 0.068665 | -0.027465 | 0.041199 | -0.21057 | -0.39368 | 0.11444 | 0.43488 | 121.1609 | 120.4651 | 122.5616 | 122.8409 | -0.027465 | 122.8867 | 122.2687 | -0.39368 | 122.8409 | -0.027465 | 122.2687 | 122.5616 | 122.8867 | -123.2346 | -123.1659
1085.1875 | 122.8317 | -122.6532 | 0.19684 | -0.0031279 | 0.015597 | 0.0099441 | -0.0017411 | 0.062677 | -0.007071 | 0.080743 | -122.6715 | 0.22888 | -123.0698 | -122.5983 | -0.11902 | -0.37537 | -1.5839 | -2.1332 | 0.25635 | -122.9599 | -0.41656 | 0.032044 | -0.018311 | 0.054931 | -0.31586 | -0.3067 | 0.05951 | 0.39825 | 121.0693 | 120.52 | 122.5342 | 122.8821 | -0.018311 | 122.9095 | 122.2778 | -0.3067 | 122.8821 | -0.018311 | 122.2778 | 122.5342 | 122.9095 | -123.2666 | -123.1567
1086.9219 | 122.7768 | -122.6578 | 0.19226 | 0.0045011 | 0.019656 | 0.012935 | -0.0036637 | 0.060754 | -0.0062164 | 0.079461 | -122.5525 | 0.22888 | -123.0331 | -122.5204 | -0.036621 | -0.27924 | -1.4923 | -2.092 | 0.27466 | -122.9645 | -0.37537 | 0.036621 | 0.10529 | 0.13733 | -0.22888 | -0.3067 | 0.082397 | 0.48065 | 121.1655 | 120.5658 | 122.6212 | 122.8867 | 0.10529 | 122.9324 | 122.3785 | -0.3067 | 122.8867 | 0.10529 | 122.3785 | 122.6212 | 122.9324 | -123.2254 | -123.1567
1088.5938 | 122.7905 | -122.6624 | 0.16937 | 0.0045011 | 0.016238 | 0.0088761 | -0.0077225 | 0.060968 | -0.0072846 | 0.08117 | -122.5479 | 0.17853 | -122.9965 | -122.4838 | 0.041199 | -0.16937 | -1.593 | -2.0645 | 0.22888 | -122.9324 | -0.33417 | 0.009155 | 0.11444 | 0.17853 | -0.12817 | -0.27008 | 0.059509 | 0.44861 | 121.0693 | 120.5978 | 122.7036 | 122.8409 | 0.11444 | 122.8912 | 122.493 | -0.27008 | 122.8409 | 0.11444 | 122.493 | 122.7036 | 122.8912 | -123.1659 | -123.1018
1090.3438 | 122.7905 | -122.6532 | 0.20599 | 0.0045011 | 0.016238 | 0.0069535 | -0.0094315 | 0.061182 | -0.0055756 | 0.080529 | -122.5342 | 0.1831 | -123.0103 | -122.4655 | 0.027466 | -0.16479 | -1.4557 | -2.0096 | 0.22888 | -122.937 | -0.35706 | -0.022889 | 0.11902 | 0.18768 | -0.17853 | -0.28381 | 0.022888 | 0.47607 | 121.1975 | 120.6436 | 122.6807 | 122.8363 | 0.11902 | 122.8821 | 122.4884 | -0.28381 | 122.8363 | 0.11902 | 122.4884 | 122.6807 | 122.8821 | -123.2162 | -123.143
1092.0938 | 122.9095 | -122.6166 | 0.16937 | -0.0031279 | 0.017733 | 0.0097305 | -0.0094315 | 0.059259 | -0.0032258 | 0.07882 | -122.5937 | 0.20599 | -123.0057 | -122.5021 | 0.009155 | -0.1831 | -1.4282 | -1.9455 | 0.25635 | -122.9462 | -0.3891 | 0.036621 | 0.022888 | 0.11444 | -0.16022 | -0.32959 | 0.086975 | 0.41199 | 121.1884 | 120.6711 | 122.6257 | 122.8226 | 0.022888 | 122.8729 | 122.4335 | -0.32959 | 122.8226 | 0.022888 | 122.4335 | 122.6257 | 122.8729 | -123.175 | -123.1155
1093.7812 | 122.8363 | -122.644 | 0.1831 | 0.0045011 | 0.01816 | 0.013148 | -0.0028091 | 0.060968 | -0.0068574 | 0.081598 | -122.6486 | 0.2243 | -123.0835 | -122.6028 | -0.09613 | -0.30212 | -1.3275 | -2.1469 | 0.27924 | -122.9553 | -0.43945 | 0.041199 | -0.004578 | 0.041199 | -0.27924 | -0.31128 | 0.096131 | 0.43487 | 121.3165 | 120.4971 | 122.5479 | 122.8683 | -0.004578 | 122.9233 | 122.3419 | -0.31128 | 122.8683 | -0.004578 | 122.3419 | 122.5479 | 122.9233 | -123.2666 | -123.1384
1095.5312 | 122.9187 | -122.6212 | 0.16022 | 0.0045011 | 0.015383 | 0.0056717 | -0.0094315 | 0.059473 | -0.0060028 | 0.077966 | -122.6166 | 0.21515 | -123.0515 | -122.5342 | -0.041199 | -0.33417 | -1.1993 | -2.092 | 0.28381 | -122.9874 | -0.4303 | 0.054932 | 0.004578 | 0.086975 | -0.20142 | -0.36621 | 0.1236 | 0.43488 | 121.4218 | 120.5292 | 122.58 | 122.8363 | 0.004578 | 122.905 | 122.287 | -0.36621 | 122.8363 | 0.004578 | 122.287 | 122.58 | 122.905 | -123.2117 | -123.1476
1097.2188 | 122.7951 | -122.6349 | 0.1831 | 0.0045011 | 0.015169 | 0.0088761 | -0.0021683 | 0.060541 | -0.00878 | 0.080957 | -122.5754 | 0.20599 | -123.0469 | -122.5067 | -0.022888 | -0.26093 | -1.1581 | -2.0187 | 0.2655 | -122.9462 | -0.41199 | 0.022889 | 0.05951 | 0.12817 | -0.20599 | -0.31128 | 0.082398 | 0.4715 | 121.4767 | 120.6162 | 122.612 | 122.8409 | 0.05951 | 122.9004 | 122.374 | -0.31128 | 122.8409 | 0.05951 | 122.374 | 122.612 | 122.9004 | -123.23 | -123.1293
1098.9531 | 122.9004 | -122.5891 | 0.16022 | 0.0045011 | 0.019869 | 0.0033219 | -0.0096451 | 0.062036 | -0.0060028 | 0.079675 | -122.6212 | 0.26093 | -123.0331 | -122.5708 | -0.064087 | -0.30212 | -1.1032 | -2.0416 | 0.3067 | -123.0103 | -0.44403 | 0.10071 | -0.032044 | 0.01831 | -0.2243 | -0.42114 | 0.14648 | 0.41199 | 121.4859 | 120.5475 | 122.525 | 122.85 | -0.032044 | 122.8958 | 122.287 | -0.42114 | 122.85 | -0.032044 | 122.287 | 122.525 | 122.8958 | -123.1934 | -123.1705
1100.7031 | 122.9095 | -122.612 | 0.17395 | 0.0045011 | 0.016024 | 0.0069535 | -0.0098587 | 0.0599 | -0.005362 | 0.07882 | -122.5891 | 0.20599 | -122.9736 | -122.493 | 0.018311 | -0.18768 | -1.3504 | -2.1927 | 0.2655 | -122.9324 | -0.36163 | 0.032044 | 0.022889 | 0.11902 | -0.15564 | -0.32043 | 0.091553 | 0.38452 | 121.2616 | 120.4193 | 122.6303 | 122.818 | 0.022889 | 122.8775 | 122.4243 | -0.32043 | 122.818 | 0.022889 | 122.4243 | 122.6303 | 122.8775 | -123.1476 | -123.1064
1102.375 | 122.818 | -122.6212 | 0.19226 | 0.0045011 | 0.017306 | 0.0073807 | -0.0023819 | 0.060541 | -0.0092072 | 0.080316 | -122.6257 | 0.2243 | -123.0469 | -122.5616 | -0.091553 | -0.31586 | -1.1856 | -2.1835 | 0.28839 | -122.937 | -0.42572 | 0.032043 | -0.004577 | 0.059509 | -0.28381 | -0.31586 | 0.09613 | 0.42114 | 121.4355 | 120.4376 | 122.5296 | 122.8455 | -0.004577 | 122.9095 | 122.3053 | -0.31586 | 122.8455 | -0.004577 | 122.3053 | 122.5296 | 122.9095 | -123.2391 | -123.1293
1104.125 | 122.7859 | -122.6166 | 0.19684 | -0.0031279 | 0.017519 | 0.012294 | -0.0096451 | 0.061823 | -0.007071 | 0.079889 | -122.5204 | 0.1831 | -123.0194 | -122.4884 | 0.018311 | -0.16479 | -1.3504 | -2.0782 | 0.24719 | -122.9553 | -0.40283 | -0.013733 | 0.09613 | 0.12817 | -0.17853 | -0.33874 | 0.050354 | 0.49896 | 121.2662 | 120.5383 | 122.6349 | 122.7997 | 0.09613 | 122.8638 | 122.4518 | -0.33874 | 122.7997 | 0.09613 | 122.4518 | 122.6349 | 122.8638 | -123.2162 | -123.1522
1105.8906 | 122.8867 | -122.612 | 0.16937 | 0.0045011 | 0.016878 | 0.0082351 | -0.0096451 | 0.061182 | -0.0066438 | 0.082025 | -122.5754 | 0.19226 | -122.9965 | -122.5113 | -0.009155 | -0.21057 | -1.2268 | -2.0782 | 0.26093 | -122.9233 | -0.38452 | 0.022888 | 0.036622 | 0.10071 | -0.17853 | -0.31128 | 0.091552 | 0.42114 | 121.3852 | 120.5338 | 122.6028 | 122.8043 | 0.036622 | 122.8729 | 122.4014 | -0.31128 | 122.8043 | 0.036622 | 122.4014 | 122.6028 | 122.8729 | -123.1659 | -123.0927
1107.6406 | 122.8592 | -122.5937 | 0.17853 | -0.010757 | 0.015169 | 0.012294 | -0.0081497 | 0.060541 | -0.00643 | 0.080743 | -122.5021 | 0.18768 | -122.9919 | -122.4472 | 0.059509 | -0.13733 | -1.2131 | -1.9135 | 0.24719 | -122.9553 | -0.39825 | 0.009155 | 0.091553 | 0.14648 | -0.11902 | -0.36163 | 0.068664 | 0.48981 | 121.3806 | 120.6802 | 122.6532 | 122.7814 | 0.091553 | 122.8409 | 122.4564 | -0.36163 | 122.7814 | 0.091553 | 122.4564 | 122.6532 | 122.8409 | -123.1705 | -123.1338
1109.3125 | 122.7814 | -122.6578 | 0.18768 | -0.0031279 | 0.016238 | 0.0067399 | -0.0021683 | 0.061823 | -0.008139 | 0.080529 | -122.5708 | 0.21057 | -123.0789 | -122.5021 | -0.036621 | -0.21973 | -1.0849 | -2.0691 | 0.27924 | -122.9645 | -0.42114 | 0.022888 | 0.086975 | 0.15564 | -0.2243 | -0.3067 | 0.091553 | 0.50812 | 121.5729 | 120.5887 | 122.6212 | 122.8683 | 0.086975 | 122.937 | 122.438 | -0.3067 | 122.8683 | 0.086975 | 122.438 | 122.6212 | 122.937 | -123.2666 | -123.1522
1111.0625 | 122.8821 | -122.612 | 0.17395 | -0.0031279 | 0.015383 | 0.0075943 | -0.0064407 | 0.059473 | -0.0068574 | 0.081384 | -122.5525 | 0.19684 | -122.9919 | -122.4701 | 0.027466 | -0.16479 | -1.1032 | -3.9276 | 0.25635 | -122.9553 | -0.37994 | 0.022888 | 0.05951 | 0.14191 | -0.14648 | -0.34332 | 0.082398 | 0.43945 | 121.5088 | 118.6844 | 122.6395 | 122.8088 | 0.05951 | 122.8683 | 122.4472 | -0.34332 | 122.8088 | 0.05951 | 122.4472 | 122.6395 | 122.8683 | -123.1659 | -123.1293
1112.75 | 122.8363 | -122.6257 | 0.19684 | 0.01976 | 0.016238 | 0.0086625 | -0.0049453 | 0.061395 | -0.005362 | 0.081384 | -122.5891 | 0.21057 | -123.0515 | -122.5113 | -0.032043 | -0.21973 | -1.1215 | -3.9871 | 0.28839 | -122.9324 | -0.42572 | 0.013733 | 0.036621 | 0.11444 | -0.22888 | -0.3067 | 0.091553 | 0.46234 | 121.5042 | 118.6386 | 122.5937 | 122.8363 | 0.036621 | 122.9141 | 122.406 | -0.3067 | 122.8363 | 0.036621 | 122.406 | 122.5937 | 122.9141 | -123.2483 | -123.1293
1114.5312 | 122.8592 | -122.6166 | 0.16022 | -0.0031279 | 0.015169 | 0.0069535 | -0.011995 | 0.060114 | -0.0057892 | 0.080102 | -122.5479 | 0.20142 | -122.9874 | -122.4518 | 0.054932 | -0.10529 | -1.2589 | -3.9185 | 0.25635 | -122.9141 | -0.37079 | 0.041199 | 0.068664 | 0.1648 | -0.10528 | -0.29755 | 0.096131 | 0.43945 | 121.3577 | 118.6981 | 122.6715 | 122.818 | 0.068664 | 122.8729 | 122.5113 | -0.29755 | 122.818 | 0.068664 | 122.5113 | 122.6715 | 122.8729 | -123.1476 | -123.0743
1116.2188 | 122.8867 | -122.6028 | 0.16479 | -0.010757 | 0.01581 | 0.0037491 | -0.0087905 | 0.058832 | -0.0094208 | 0.080529 | -122.5433 | 0.20599 | -123.0148 | -122.493 | 0.004578 | -0.17395 | -1.1078 | -3.9825 | 0.27008 | -122.9691 | -0.41199 | 0.041199 | 0.059509 | 0.10986 | -0.16022 | -0.36621 | 0.10529 | 0.4715 | 121.4951 | 118.6203 | 122.6074 | 122.8088 | 0.059509 | 122.8729 | 122.4289 | -0.36621 | 122.8088 | 0.059509 | 122.4289 | 122.6074 | 122.8729 | -123.1796 | -123.1338
1117.9531 | 122.8638 | -122.5983 | 0.17395 | 0.0045011 | 0.016238 | 0.0052445 | -0.0077225 | 0.060114 | -0.0057892 | 0.080957 | -122.5479 | 0.19684 | -122.9828 | -122.4609 | 0.041199 | -0.10071 | -1.1993 | -4.985 | 0.23804 | -122.9782 | -0.38452 | 0.022888 | 0.050354 | 0.13733 | -0.13275 | -0.37994 | 0.064087 | 0.43488 | 121.3989 | 117.6132 | 122.6395 | 122.7951 | 0.050354 | 122.8363 | 122.4976 | -0.37994 | 122.7951 | 0.050354 | 122.4976 | 122.6395 | 122.8363 | -123.1567 | -123.1522
1119.6875 | 122.9233 | -122.6028 | 0.17853 | 0.012131 | 0.014529 | 0.0078079 | -0.0034499 | 0.057977 | -0.0072846 | 0.079675 | -122.6395 | 0.22888 | -123.056 | -122.5479 | -0.091553 | -0.25635 | -0.99335 | -5.0858 | 0.29297 | -122.9874 | -0.45319 | 0.050354 | -0.036621 | 0.054931 | -0.27008 | -0.38452 | 0.11444 | 0.41657 | 121.6095 | 117.5171 | 122.5113 | 122.8317 | -0.036621 | 122.8958 | 122.3465 | -0.38452 | 122.8317 | -0.036621 | 122.3465 | 122.5113 | 122.8958 | -123.2346 | -123.1659
1121.4375 | 122.7905 | -122.6257 | 0.17853 | 0.012131 | 0.017306 | 0.012721 | -0.0062271 | 0.059473 | -0.0066438 | 0.08117 | -122.58 | 0.22888 | -123.0515 | -122.4884 | -0.027466 | -0.20142 | -1.0483 | -4.5502 | 0.28381 | -122.9416 | -0.42572 | 0.050354 | 0.045776 | 0.13733 | -0.20599 | -0.31586 | 0.10528 | 0.4715 | 121.5775 | 118.0756 | 122.5983 | 122.8546 | 0.045776 | 122.9095 | 122.4243 | -0.31586 | 122.8546 | 0.045776 | 122.4243 | 122.5983 | 122.9095 | -123.23 | -123.1201
1123.1875 | 122.7905 | -122.6212 | 0.19226 | 0.0045011 | 0.017733 | 0.011653 | -0.0040909 | 0.061609 | -0.0079254 | 0.082879 | -122.5983 | 0.2243 | -123.0469 | -122.5388 | -0.082397 | -0.23346 | -0.97961 | -4.2297 | 0.27008 | -122.9599 | -0.42572 | 0.032043 | 0.022888 | 0.082398 | -0.27466 | -0.33875 | 0.07782 | 0.44861 | 121.6415 | 118.3914 | 122.5388 | 122.8455 | 0.022888 | 122.8912 | 122.3877 | -0.33875 | 122.8455 | 0.022888 | 122.3877 | 122.5388 | 122.8912 | -123.2391 | -123.1522
1124.8594 | 122.8226 | -122.6028 | 0.19684 | 0.0045011 | 0.016238 | 0.010799 | -0.0036637 | 0.064172 | -0.007071 | 0.086511 | -122.6395 | 0.22888 | -123.0423 | -122.58 | -0.11444 | -0.24261 | -0.97046 | -4.1519 | 0.27466 | -122.9324 | -0.43945 | 0.032044 | -0.036621 | 0.022888 | -0.31128 | -0.32959 | 0.07782 | 0.40283 | 121.6324 | 118.4509 | 122.4884 | 122.8317 | -0.036621 | 122.8775 | 122.3602 | -0.32959 | 122.8317 | -0.036621 | 122.3602 | 122.4884 | 122.8775 | -123.2391 | -123.1293
1126.6094 | 122.8546 | -122.5983 | 0.1831 | -0.0031279 | 0.016451 | 0.010371 | -0.013063 | 0.061182 | -0.0068574 | 0.085443 | -122.5021 | 0.19226 | -122.9599 | -122.4426 | 0.054932 | -0.082397 | -1.1719 | -4.0421 | 0.25177 | -122.9416 | -0.36163 | 0.009156 | 0.096131 | 0.15564 | -0.12817 | -0.34332 | 0.068665 | 0.45776 | 121.4264 | 118.5562 | 122.6532 | 122.7905 | 0.096131 | 122.85 | 122.5159 | -0.34332 | 122.7905 | 0.096131 | 122.5159 | 122.6532 | 122.85 | -123.143 | -123.1247
1128.3594 | 122.7768 | -122.644 | 0.19684 | -0.0031279 | 0.017733 | 0.0099441 | -0.0047317 | 0.061182 | -0.0072846 | 0.082452 | -122.6212 | 0.23804 | -123.0331 | -122.5479 | -0.068665 | -0.15106 | -1.1902 | -4.4449 | 0.27466 | -122.9324 | -0.3891 | 0.041199 | 0.022888 | 0.09613 | -0.2655 | -0.28839 | 0.07782 | 0.41199 | 121.4539 | 118.1992 | 122.5754 | 122.8821 | 0.022888 | 122.9187 | 122.493 | -0.28839 | 122.8821 | 0.022888 | 122.493 | 122.5754 | 122.9187 | -123.23 | -123.1293
1130.0469 | 122.8867 | -122.6028 | 0.16479 | 0.012131 | 0.015597 | 0.0075943 | -0.010072 | 0.058618 | -0.0038666 | 0.081811 | -122.5754 | 0.20599 | -123.0057 | -122.5204 | -0.054932 | -0.14191 | -1.0757 | -4.7562 | 0.25177 | -122.9736 | -0.40283 | 0.041199 | 0.027466 | 0.082397 | -0.21973 | -0.37079 | 0.086975 | 0.4303 | 121.5271 | 117.8467 | 122.5479 | 122.8088 | 0.027466 | 122.8546 | 122.4609 | -0.37079 | 122.8088 | 0.027466 | 122.4609 | 122.5479 | 122.8546 | -123.1705 | -123.1384
1131.7969 | 122.9095 | -122.5754 | 0.15564 | -0.0031279 | 0.017519 | 0.0031083 | -0.0092179 | 0.059686 | -0.0060028 | 0.081384 | -122.5937 | 0.21515 | -122.9919 | -122.5204 | -0.018311 | -0.09613 | -1.1353 | -2.1927 | 0.25177 | -122.9691 | -0.41657 | 0.059509 | -0.018311 | 0.054931 | -0.17395 | -0.39368 | 0.09613 | 0.39825 | 121.4401 | 120.3827 | 122.5571 | 122.7905 | -0.018311 | 122.8271 | 122.4792 | -0.39368 | 122.7905 | -0.018311 | 122.4792 | 122.5571 | 122.8271 | -123.1476 | -123.1247
1133.5469 | 122.8867 | -122.5845 | 0.17395 | -0.0031279 | 0.016451 | 0.0080215 | -0.0064407 | 0.060541 | -0.0062164 | 0.079248 | -122.5571 | 0.20599 | -123.0103 | -122.493 | -0.036621 | -0.12817 | -1.149 | -1.6525 | 0.27924 | -122.9691 | -0.42572 | 0.032044 | 0.027466 | 0.091553 | -0.21057 | -0.38452 | 0.10529 | 0.45319 | 121.4355 | 120.932 | 122.5479 | 122.7905 | 0.027466 | 122.8638 | 122.4564 | -0.38452 | 122.7905 | 0.027466 | 122.4564 | 122.5479 | 122.8638 | -123.1842 | -123.143
1135.2344 | 122.8226 | -122.6212 | 0.1831 | -0.0031279 | 0.016665 | 0.014217 | -0.0021683 | 0.061609 | -0.0051484 | 0.080102 | -122.6074 | 0.21973 | -123.0606 | -122.5571 | -0.11444 | -0.20599 | -1.2589 | -2.0966 | 0.27008 | -122.9691 | -0.43945 | 0.036622 | 0.013733 | 0.064087 | -0.29755 | -0.3479 | 0.086976 | 0.45319 | 121.3623 | 120.5246 | 122.5067 | 122.8409 | 0.013733 | 122.8912 | 122.4152 | -0.3479 | 122.8409 | 0.013733 | 122.4152 | 122.5067 | 122.8912 | -123.2437 | -123.1522
1136.9844 | 122.8455 | -122.5891 | 0.16937 | -0.0031279 | 0.016024 | 0.0058853 | -0.010286 | 0.059686 | -0.0032258 | 0.080102 | -122.5021 | 0.20142 | -122.9828 | -122.4426 | 0.027466 | -0.050354 | -1.2817 | -2.1378 | 0.23346 | -122.9599 | -0.39368 | 0.032043 | 0.086975 | 0.14648 | -0.14191 | -0.37079 | 0.064086 | 0.48065 | 121.3074 | 120.4514 | 122.6166 | 122.7905 | 0.086975 | 122.8226 | 122.5388 | -0.37079 | 122.7905 | 0.086975 | 122.5388 | 122.6166 | 122.8226 | -123.1522 | -123.1293
1138.7188 | 122.8775 | -122.5754 | 0.15564 | -0.0031279 | 0.015169 | 0.0086625 | -0.010713 | 0.058191 | -0.0032258 | 0.080316 | -122.5616 | 0.20599 | -123.0103 | -122.4747 | 0.004578 | -0.15106 | -1.1948 | -2.2797 | 0.24719 | -122.9324 | -0.43488 | 0.050354 | 0.013732 | 0.10071 | -0.15106 | -0.35706 | 0.091552 | 0.44861 | 121.3806 | 120.2957 | 122.58 | 122.7814 | 0.013732 | 122.8226 | 122.4243 | -0.35706 | 122.7814 | 0.013732 | 122.4243 | 122.58 | 122.8226 | -123.1659 | -123.0881
1140.4688 | 122.8546 | -122.5662 | 0.16937 | 0.0045011 | 0.01816 | 0.0088761 | -0.0019547 | 0.059473 | -0.0068574 | 0.080957 | -122.5891 | 0.2243 | -123.0606 | -122.493 | -0.059509 | -0.23804 | -1.0529 | -2.5589 | 0.28839 | -122.9599 | -0.49439 | 0.054931 | -0.022888 | 0.073242 | -0.22888 | -0.39368 | 0.11902 | 0.4715 | 121.5134 | 120.0073 | 122.5067 | 122.7905 | -0.022888 | 122.8546 | 122.3282 | -0.39368 | 122.7905 | -0.022888 | 122.3282 | 122.5067 | 122.8546 | -123.23 | -123.1293
1142.2188 | 122.8821 | -122.5754 | 0.15106 | -0.018387 | 0.016665 | 0.0078079 | -0.0066543 | 0.059473 | -0.0049348 | 0.081598 | -122.6074 | 0.21973 | -123.056 | -122.5204 | -0.07782 | -0.27924 | -0.99792 | -2.0966 | 0.28381 | -122.9645 | -0.48065 | 0.068665 | -0.032044 | 0.054931 | -0.22888 | -0.3891 | 0.13275 | 0.44861 | 121.5775 | 120.4788 | 122.4976 | 122.7951 | -0.032044 | 122.8592 | 122.2961 | -0.3891 | 122.7951 | -0.032044 | 122.2961 | 122.4976 | 122.8592 | -123.2071 | -123.1155
1143.9062 | 122.7631 | -122.6303 | 0.19684 | 0.0045011 | 0.016024 | 0.013148 | -0.0057999 | 0.063318 | -0.0038666 | 0.081384 | -122.5204 | 0.19684 | -123.0194 | -122.4518 | 0 | -0.10529 | -1.1169 | -1.8082 | 0.23346 | -122.9004 | -0.3891 | 0 | 0.10986 | 0.17853 | -0.19684 | -0.27008 | 0.036621 | 0.49896 | 121.5134 | 120.8221 | 122.6303 | 122.8271 | 0.10986 | 122.8638 | 122.525 | -0.27008 | 122.8271 | 0.10986 | 122.525 | 122.6303 | 122.8638 | -123.2162 | -123.0972
1145.6562 | 122.7997 | -122.612 | 0.17853 | 0.012131 | 0.016878 | 0.010585 | -0.0053727 | 0.062463 | -0.0066438 | 0.08117 | -122.6257 | 0.21057 | -123.0286 | -122.5433 | -0.086975 | -0.2243 | -0.9613 | -1.8494 | 0.28381 | -122.9599 | -0.41656 | 0.032043 | -0.013732 | 0.068665 | -0.2655 | -0.3479 | 0.10528 | 0.40283 | 121.6507 | 120.7626 | 122.525 | 122.8226 | -0.013732 | 122.8958 | 122.3877 | -0.3479 | 122.8226 | -0.013732 | 122.3877 | 122.525 | 122.8958 | -123.2071 | -123.1384
1147.3438 | 122.818 | -122.6212 | 0.1831 | 0.0045011 | 0.015169 | 0.0099441 | -0.0045181 | 0.061182 | -0.007071 | 0.08352 | -122.6395 | 0.23346 | -123.0469 | -122.5616 | -0.1236 | -0.2243 | -0.81482 | -1.8997 | 0.27008 | -122.9141 | -0.42572 | 0.050354 | -0.01831 | 0.059509 | -0.3067 | -0.29297 | 0.086976 | 0.40741 | 121.8063 | 120.7214 | 122.4976 | 122.8546 | -0.01831 | 122.8912 | 122.3969 | -0.29297 | 122.8546 | -0.01831 | 122.3969 | 122.4976 | 122.8912 | -123.23 | -123.0972
1149.0781 | 122.8683 | -122.5845 | 0.16479 | 0.0045011 | 0.014956 | 0.0052445 | -0.0105 | 0.058832 | -0.0042938 | 0.080957 | -122.5708 | 0.19226 | -123.0057 | -122.4976 | -0.045776 | -0.091553 | -0.93384 | -1.6571 | 0.24261 | -122.9279 | -0.42114 | 0.027466 | 0.013733 | 0.086975 | -0.21057 | -0.34332 | 0.07782 | 0.43487 | 121.6507 | 120.9274 | 122.5388 | 122.7768 | 0.013733 | 122.8271 | 122.493 | -0.34332 | 122.7768 | 0.013733 | 122.493 | 122.5388 | 122.8271 | -123.1705 | -123.0927
1150.75 | 122.7676 | -122.612 | 0.19226 | -0.0031279 | 0.022219 | 0.0084489 | -0.0021683 | 0.058618 | -0.0060028 | 0.082238 | -122.5479 | 0.25177 | -123.0331 | -122.4884 | -0.045776 | -0.12817 | -1.0437 | -1.6525 | 0.2655 | -122.9645 | -0.42114 | 0.059509 | 0.064087 | 0.1236 | -0.23804 | -0.35248 | 0.073242 | 0.48523 | 121.5683 | 120.9595 | 122.5662 | 122.8638 | 0.064087 | 122.8775 | 122.4838 | -0.35248 | 122.8638 | 0.064087 | 122.4838 | 122.5662 | 122.8775 | -123.2254 | -123.1567
1152.5 | 122.7859 | -122.612 | 0.21515 | 0.0045011 | 0.018587 | 0.01208 | -0.0028091 | 0.063318 | -0.0077118 | 0.081598 | -122.612 | 0.21973 | -123.0148 | -122.5571 | -0.1236 | -0.18768 | -1.2772 | -1.6388 | 0.27924 | -122.9187 | -0.40283 | 0.004578 | 0 | 0.054932 | -0.33875 | -0.3067 | 0.064087 | 0.40283 | 121.3348 | 120.9732 | 122.4884 | 122.8317 | 0 | 122.8912 | 122.4243 | -0.3067 | 122.8317 | 0 | 122.4243 | 122.4884 | 122.8912 | -123.23 | -123.1338
1154.25 | 122.7631 | -122.4792 | 0.29755 | -0.0031279 | 0.015169 | 0.0093033 | -0.0105 | 0.06225 | -0.0057892 | 0.46847 | -122.4106 | 0.29297 | -122.85 | -122.2229 | 0.086975 | -0.10529 | -1.5793 | -1.5106 | 0.35248 | -122.7219 | -0.37079 | -0.004577 | 0.068665 | 0.25635 | -0.21057 | -0.24262 | 0.054932 | 0.43945 | 120.9 | 120.9686 | 122.5662 | 122.7722 | 0.068665 | 122.8317 | 122.374 | -0.24262 | 122.7722 | 0.068665 | 122.374 | 122.5662 | 122.8317 | -123.1476 | -123.0194
1156 | 122.8088 | -122.5891 | 0.17853 | 0.0045011 | 0.01346 | 0.010158 | -0.0062271 | 0.063318 | -0.009848 | 0.08117 | -122.5845 | 0.23346 | -123.0331 | -122.4747 | -0.064087 | -0.13733 | -1.3504 | -1.2817 | 0.27924 | -122.9095 | -0.44403 | 0.054931 | 0.004577 | 0.11444 | -0.24261 | -0.32044 | 0.10071 | 0.44861 | 121.2387 | 121.3074 | 122.525 | 122.8226 | 0.004577 | 122.8683 | 122.4518 | -0.32044 | 122.8226 | 0.004577 | 122.4518 | 122.525 | 122.8683 | -123.2117 | -123.0881
1157.6875 | 122.8821 | -122.5708 | 0.16937 | -0.0031279 | 0.017092 | 0.0078079 | -0.0092179 | 0.060327 | -0.0055756 | 0.080102 | -122.5479 | 0.21515 | -122.9736 | -122.4838 | -0.054932 | -0.13733 | -1.2497 | -1.2177 | 0.27008 | -122.9507 | -0.40283 | 0.045776 | 0.022888 | 0.086975 | -0.22431 | -0.37994 | 0.10071 | 0.42572 | 121.3211 | 121.3531 | 122.5159 | 122.7859 | 0.022888 | 122.8409 | 122.4335 | -0.37994 | 122.7859 | 0.022888 | 122.4335 | 122.5159 | 122.8409 | -123.143 | -123.1201
1159.4219 | 122.7356 | -122.6303 | 0.19226 | 0.0045011 | 0.01816 | 0.010371 | -0.0038773 | 0.060754 | -0.007071 | 0.081384 | -122.5525 | 0.21057 | -123.0194 | -122.4838 | -0.073242 | -0.1236 | -1.2085 | -1.2634 | 0.27924 | -122.9324 | -0.3891 | 0.01831 | 0.07782 | 0.14648 | -0.2655 | -0.30212 | 0.086975 | 0.46692 | 121.4218 | 121.3669 | 122.5571 | 122.8409 | 0.07782 | 122.9095 | 122.5067 | -0.30212 | 122.8409 | 0.07782 | 122.5067 | 122.5571 | 122.9095 | -123.2117 | -123.1247
1161.1719 | 122.8226 | -122.3373 | 0.36163 | 0.012131 | 0.017733 | 0.013148 | -0.011141 | 0.060541 | -0.0051484 | 0.78079 | -122.3099 | 0.38452 | -122.6669 | -122.1313 | 0.09613 | -0.13275 | -1.0345 | -1.2177 | 0.46692 | -122.6715 | -0.32959 | 0.022888 | 0.027466 | 0.20599 | -0.2655 | -0.33417 | 0.10529 | 0.35706 | 121.3028 | 121.1197 | 122.4335 | 122.7219 | 0.027466 | 122.8043 | 122.2046 | -0.33417 | 122.7219 | 0.027466 | 122.2046 | 122.4335 | 122.8043 | -123.0286 | -123.0331
1162.8594 | 122.6898 | -122.3511 | 0.36621 | -0.0031279 | 0.018587 | 0.011012 | -0.0072953 | 0.063318 | -0.003653 | 0.665 | -122.2046 | 0.35706 | -122.7219 | -121.9803 | 0.082397 | -0.013733 | -1.1856 | -1.268 | 0.41199 | -122.58 | -0.37079 | -0.009155 | 0.14648 | 0.37079 | -0.28381 | -0.22888 | 0.045776 | 0.51727 | 121.1655 | 121.0831 | 122.4335 | 122.7081 | 0.14648 | 122.7631 | 122.3373 | -0.22888 | 122.7081 | 0.14648 | 122.3373 | 122.4335 | 122.7631 | -123.0881 | -122.9462
1164.5938 | 122.6212 | -122.2366 | 0.42114 | 0.012131 | 0.015169 | 0.011653 | -0.0036637 | 0.062036 | -0.0079254 | 1.0042 | -122.2961 | 0.49896 | -122.6852 | -121.9757 | 0.041199 | -0.20599 | -0.95673 | -1.5198 | 0.5127 | -122.5388 | -0.44861 | 0.077819 | -0.05951 | 0.26093 | -0.37994 | -0.30212 | 0.091552 | 0.3891 | 121.2799 | 120.7169 | 122.2778 | 122.7356 | -0.05951 | 122.7493 | 122.0306 | -0.30212 | 122.7356 | -0.05951 | 122.0306 | 122.2778 | 122.7493 | -123.1064 | -122.9599
1166.3438 | 122.6303 | -121.5454 | 0.92468 | -0.0031279 | 0.014742 | 0.011439 | -0.0085769 | 0.060114 | -0.0030122 | 2.7269 | -121.3074 | 0.97961 | -121.9162 | -120.639 | 0.59967 | -0.16022 | -0.96588 | -1.2817 | 0.94299 | -121.701 | -0.37079 | 0.054931 | 0.23804 | 0.90637 | -0.32501 | -0.15564 | 0.01831 | 0.60883 | 120.5795 | 120.2637 | 122.1451 | 122.525 | 0.23804 | 122.4884 | 121.3852 | -0.15564 | 122.525 | 0.23804 | 121.3852 | 122.1451 | 122.4884 | -122.8409 | -122.6257
1168.0312 | 122.612 | -44.1788 | 78.154 | -0.0031279 | 0.017092 | 0.0086625 | -0.01285 | 0.057764 | -0.0045074 | 0.08587 | -44.4397 | 78.154 | -44.6594 | -44.3024 | 76.1398 | 0.21057 | -0.15106 | 0.37994 | 78.2364 | -44.6136 | -0.48065 | 0 | -0.26093 | -0.1236 | -2.0142 | -0.43487 | 0.082397 | 0.21973 | 44.0277 | 44.5587 | 120.3186 | 122.3328 | -0.26093 | 122.4152 | 44.3893 | -0.43487 | 122.3328 | -0.26093 | 44.3893 | 120.3186 | 122.4152 | -122.8134 | -122.7676
1169.7812 | 122.6532 | -3.9139 | 118.689 | 0.0045011 | 0.01816 | 0.0063125 | -0.0092179 | 0.059259 | -0.0049348 | 0.10296 | -3.9642 | 118.7897 | -4.3625 | -3.7125 | 112.5595 | 0.21515 | 0.5127 | 0.97961 | 118.9362 | -4.2618 | -0.44861 | 0.10071 | -0.050354 | 0.20142 | -6.1295 | -0.3479 | 0.24719 | 0.39825 | 4.4266 | 4.8935 | 116.4734 | 122.7036 | -0.050354 | 122.85 | 4.129 | -0.3479 | 122.7036 | -0.050354 | 4.129 | 116.4734 | 122.85 | -123.0515 | -122.9507
1171.5312 | 122.6761 | -10.0204 | 112.5137 | 0.0045011 | 0.01581 | 0.0054581 | -0.011568 | 0.0599 | -0.0021576 | 0.10211 | -10.1212 | 112.6648 | -10.437 | -9.874 | 106.2973 | 0.28381 | 0.22888 | 1.1124 | 112.7518 | -10.3409 | -0.41656 | 0.15106 | -0.10071 | 0.14649 | -6.2164 | -0.32043 | 0.23804 | 0.31586 | 10.2493 | 11.1328 | 116.3177 | 122.6852 | -0.10071 | 122.7722 | 10.3043 | -0.32043 | 122.6852 | -0.10071 | 10.3043 | 116.3177 | 122.7722 | -122.9507 | -122.8546
1173.2656 | 122.7036 | -9.7549 | 112.793 | 0.0045011 | 0.017519 | 0.0067399 | -0.010927 | 0.058618 | -0.0030122 | 0.10125 | -9.8328 | 112.9074 | -10.1852 | -9.5856 | 106.0455 | 0.29297 | 0.16022 | 1.2039 | 113.0447 | -10.0983 | -0.4303 | 0.11444 | -0.07782 | 0.16937 | -6.7474 | -0.34332 | 0.25177 | 0.35248 | 9.9152 | 10.9589 | 115.8005 | 122.6624 | -0.07782 | 122.7997 | 10.0479 | -0.34332 | 122.6624 | -0.07782 | 10.0479 | 115.8005 | 122.7997 | -122.9782 | -122.8912
1175.0156 | 122.731 | -10.144 | 112.4268 | 0.012131 | 0.01816 | 0.0088761 | -0.0047317 | 0.059473 | -0.00044857 | 0.10232 | -10.3226 | 112.5687 | -10.6384 | -10.0616 | 102.5711 | 0.16479 | 0.32501 | 1.1032 | 112.6831 | -10.524 | -0.49438 | 0.14191 | -0.17853 | 0.082397 | -9.8557 | -0.37994 | 0.25635 | 0.31586 | 10.4691 | 11.2473 | 112.7151 | 122.7127 | -0.17853 | 122.8271 | 10.3088 | -0.37994 | 122.7127 | -0.17853 | 10.3088 | 112.7151 | 122.8271 | -123.0652 | -122.9507
1176.7656 | 122.6074 | -13.1882 | 109.4696 | -0.0031279 | 0.016878 | 0.0082351 | -0.0053727 | 0.060754 | 0.014719 | 0.11984 | -13.1973 | 109.5612 | -13.5361 | -12.9684 | 71.5759 | 0.27924 | -0.004578 | 0.97961 | 109.6664 | -13.4262 | -0.3479 | 0.091553 | -0.009156 | 0.21973 | -37.8937 | -0.23804 | 0.19684 | 0.33875 | 13.1836 | 14.1678 | 84.7641 | 122.7493 | -0.009156 | 122.8546 | 13.4674 | -0.23804 | 122.7493 | -0.009156 | 13.4674 | 84.7641 | 122.8546 | -123.0057 | -122.8958
1178.4375 | 122.7127 | -13.4537 | 109.1537 | 0.012131 | 0.016665 | 0.0084489 | -0.0062271 | 0.058191 | 0.024759 | 0.12411 | -13.5223 | 109.2911 | -13.8245 | -13.2614 | 58.5709 | 0.23346 | 0.054932 | 0.84686 | 109.3597 | -13.7375 | -0.37079 | 0.13733 | -0.068665 | 0.19226 | -50.5829 | -0.28381 | 0.20599 | 0.30212 | 13.5086 | 14.3005 | 72.0245 | 122.7448 | -0.068665 | 122.8134 | 13.6871 | -0.28381 | 122.7448 | -0.068665 | 13.6871 | 72.0245 | 122.8134 | -122.9782 | -122.8912
1180.1719 | 122.699 | -11.3342 | 111.2869 | -0.010757 | 0.019656 | 0.010799 | -0.0070815 | 0.056055 | 0.027536 | 0.13159 | -11.348 | 111.4197 | -11.7096 | -11.1053 | 52.4551 | 0.23804 | 0.004578 | 0.80566 | 111.5204 | -11.6364 | -0.37537 | 0.13275 | -0.013732 | 0.22888 | -58.8318 | -0.30212 | 0.23346 | 0.36163 | 11.3388 | 12.1399 | 63.7894 | 122.7539 | -0.013732 | 122.8546 | 11.5723 | -0.30212 | 122.7539 | -0.013732 | 11.5723 | 63.7894 | 122.8546 | -122.9965 | -122.9233
1181.9219 | 122.6395 | -11.1053 | 111.5799 | -0.0031279 | 0.019228 | 0.0031083 | -0.0021683 | 0.060327 | 0.029245 | 0.13308 | -11.1237 | 111.7264 | -11.4761 | -10.8765 | 47.1176 | 0.15564 | 0.11444 | 0.70953 | 111.8362 | -11.348 | -0.37079 | 0.14648 | -0.01831 | 0.22888 | -64.4623 | -0.24261 | 0.25635 | 0.35248 | 11.2198 | 11.8149 | 58.223 | 122.8317 | -0.01831 | 122.9416 | 11.261 | -0.24261 | 122.8317 | -0.01831 | 11.261 | 58.223 | 122.9416 | -123.056 | -122.9279
1183.6719 | 122.6852 | -11.4304 | 111.2228 | 0.012131 | 0.017947 | 0.0078079 | -0.0021683 | 0.061823 | 0.031808 | 0.13842 | -11.5265 | 111.4105 | -11.8149 | -11.3159 | 38.7772 | 0.091553 | 0.10529 | 0.59509 | 111.5295 | -11.6959 | -0.38452 | 0.18768 | -0.09613 | 0.11444 | -72.4457 | -0.2655 | 0.3067 | 0.28839 | 11.5356 | 12.0255 | 50.2075 | 122.8409 | -0.09613 | 122.9599 | 11.5219 | -0.2655 | 122.8409 | -0.09613 | 11.5219 | 50.2075 | 122.9599 | -123.0377 | -122.9187
1185.3594 | 122.7676 | -11.3983 | 111.1862 | 0.0045011 | 0.018587 | 0.0099441 | -0.010286 | 0.060968 | 0.03544 | 0.13778 | -11.5311 | 111.351 | -11.8103 | -11.2793 | 37.6007 | 0.18768 | 0.022888 | 0.67749 | 111.4517 | -11.7325 | -0.41199 | 0.16479 | -0.13275 | 0.11902 | -73.5855 | -0.33417 | 0.2655 | 0.27924 | 11.4212 | 12.0758 | 48.999 | 122.7493 | -0.13275 | 122.85 | 11.586 | -0.33417 | 122.7493 | -0.13275 | 11.586 | 48.999 | 122.85 | -122.9965 | -122.9187
1187.1094 | 122.7036 | -11.0916 | 111.5616 | 0.012131 | 0.015169 | 0.0080215 | -0.0021683 | 0.061395 | 0.032022 | 0.14056 | -11.2289 | 111.7081 | -11.5173 | -10.9726 | 36.9324 | 0.091553 | 0.091553 | 0.5127 | 111.8271 | -11.3937 | -0.42572 | 0.14648 | -0.13733 | 0.11902 | -74.6292 | -0.30212 | 0.2655 | 0.28839 | 11.1832 | 11.6043 | 48.024 | 122.7997 | -0.13733 | 122.9187 | 11.1832 | -0.30212 | 122.7997 | -0.13733 | 11.1832 | 48.024 | 122.9187 | -123.0789 | -122.9553
1188.8594 | 122.7219 | -8.1894 | 114.4638 | 0.0045011 | 0.014315 | 0.0088761 | -0.010072 | 0.058832 | 0.036295 | 0.14355 | -8.1894 | 114.6057 | -8.5373 | -7.9376 | 36.6806 | 0.21057 | 0.013733 | 0.65918 | 114.7247 | -8.4595 | -0.3479 | 0.14191 | 0 | 0.25177 | -77.7832 | -0.27008 | 0.26093 | 0.3479 | 8.2031 | 8.8486 | 44.87 | 122.7951 | 0 | 122.9141 | 8.4 | -0.27008 | 122.7951 | 0 | 8.4 | 44.87 | 122.9141 | -123.0011 | -122.9233
1190.6094 | 122.6715 | -7.8094 | 114.8804 | 0.0045011 | 0.018587 | 0.0093033 | -0.0028091 | 0.062463 | 0.036081 | 0.14462 | -7.814 | 115.0314 | -8.1528 | -7.5485 | 35.1608 | 0.15564 | 0.041199 | 0.63171 | 115.1779 | -8.0429 | -0.34332 | 0.15106 | -0.004578 | 0.26092 | -79.7195 | -0.23346 | 0.29755 | 0.33874 | 7.8506 | 8.4412 | 42.9703 | 122.8409 | -0.004578 | 122.9874 | 7.9651 | -0.23346 | 122.8409 | -0.004578 | 7.9651 | 42.9703 | 122.9874 | -123.0331 | -122.9233
1192.3594 | 122.6944 | -8.2718 | 114.4363 | -0.0031279 | 0.020937 | 0.0097305 | -0.0013137 | 0.062677 | 0.038644 | 0.1444 | -8.2535 | 114.6606 | -8.6014 | -8.0383 | 34.671 | 0.086975 | 0.12817 | 0.56305 | 114.7522 | -8.5281 | -0.32959 | 0.22431 | 0.018311 | 0.23346 | -79.7653 | -0.25635 | 0.31586 | 0.3479 | 8.4 | 8.8348 | 42.9428 | 122.9324 | 0.018311 | 123.024 | 8.3588 | -0.25635 | 122.9324 | 0.018311 | 8.3588 | 42.9428 | 123.024 | -123.0377 | -122.9645
1194.0469 | 122.7631 | -8.1161 | 114.537 | -0.0031279 | 0.016878 | 0.0035355 | -0.0090041 | 0.060968 | 0.038431 | 0.14248 | -8.1299 | 114.6927 | -8.4824 | -7.8506 | 34.9274 | 0.19226 | 0.10071 | 0.67749 | 114.8026 | -8.4137 | -0.36621 | 0.15564 | -0.013733 | 0.2655 | -79.6097 | -0.29755 | 0.2655 | 0.35248 | 8.2169 | 8.7936 | 43.0435 | 122.8088 | -0.013733 | 122.9187 | 8.3084 | -0.29755 | 122.8088 | -0.013733 | 8.3084 | 43.0435 | 122.9187 | -123.0194 | -122.9507
1195.7969 | 122.7264 | -8.3176 | 114.3631 | 0.012131 | 0.016024 | 0.010799 | -0.00088652 | 0.062036 | 0.037149 | 0.14184 | -8.3496 | 114.5233 | -8.7112 | -8.0704 | 35.7422 | 0.14648 | 0.14191 | 0.60425 | 114.6698 | -8.6014 | -0.39368 | 0.16022 | -0.032043 | 0.24719 | -78.6209 | -0.28381 | 0.3067 | 0.36163 | 8.4595 | 8.9218 | 44.0598 | 122.8409 | -0.032043 | 122.9874 | 8.464 | -0.28381 | 122.8409 | -0.032043 | 8.464 | 44.0598 | 122.9874 | -123.0743 | -122.9645
1197.5 | 122.7859 | -8.2901 | 114.3539 | 0.012131 | 0.017947 | 0.0046037 | -0.0072953 | 0.0599 | 0.03544 | 0.14291 | -8.4 | 114.5233 | -8.757 | -8.1482 | 35.2341 | 0.10529 | 0.16479 | 0.53101 | 114.5874 | -8.6288 | -0.46692 | 0.16937 | -0.10986 | 0.14191 | -79.1199 | -0.33874 | 0.23346 | 0.35706 | 8.4549 | 8.8211 | 43.5242 | 122.8134 | -0.10986 | 122.8775 | 8.3954 | -0.33874 | 122.8134 | -0.10986 | 8.3954 | 43.5242 | 122.8775 | -123.111 | -122.9828
1199.2656 | 122.7951 | -8.5327 | 114.1251 | 0.0045011 | 0.016238 | 0.0086625 | -0.0068679 | 0.060327 | 0.038431 | 0.14141 | -8.551 | 114.299 | -8.9081 | -8.3221 | 34.7534 | 0.13733 | 0.13275 | 0.58136 | 114.3997 | -8.8348 | -0.37537 | 0.17395 | -0.01831 | 0.21057 | -79.3716 | -0.30212 | 0.27466 | 0.35706 | 8.6655 | 9.1141 | 43.2861 | 122.8317 | -0.01831 | 122.9324 | 8.67 | -0.30212 | 122.8317 | -0.01831 | 8.67 | 43.2861 | 122.9324 | -123.0331 | -122.9599
1201.0156 | 122.7768 | -8.3496 | 114.2761 | -0.010757 | 0.016878 | 0.0095169 | -0.0072953 | 0.059045 | 0.039499 | 0.1444 | -8.3588 | 114.4684 | -8.7112 | -8.1207 | 34.053 | 0.18768 | 0.009155 | 0.58594 | 114.6194 | -8.6014 | -0.36163 | 0.19226 | -0.009156 | 0.22888 | -80.2231 | -0.25177 | 0.34332 | 0.35248 | 8.3588 | 8.9355 | 42.4026 | 122.818 | -0.009156 | 122.9691 | 8.5373 | -0.25177 | 122.818 | -0.009156 | 8.5373 | 42.4026 | 122.9691 | -122.9874 | -122.8775
1202.7031 | 122.7036 | -8.1207 | 114.5828 | 0.0045011 | 0.020296 | 0.0082351 | -0.0028091 | 0.063532 | 0.035226 | 0.14291 | -8.1528 | 114.7522 | -8.5007 | -7.9239 | 34.9594 | 0.10071 | 0.12817 | 0.50354 | 114.8895 | -8.3725 | -0.37994 | 0.16937 | -0.032043 | 0.19684 | -79.6234 | -0.25177 | 0.3067 | 0.3479 | 8.2489 | 8.6243 | 43.0801 | 122.8729 | -0.032043 | 123.0103 | 8.2214 | -0.25177 | 122.8729 | -0.032043 | 8.2214 | 43.0801 | 123.0103 | -123.0835 | -122.9553
1204.4531 | 122.7859 | -8.02 | 114.6332 | -0.010757 | 0.018587 | 0.0039627 | -0.0068679 | 0.058191 | 0.038431 | 0.14398 | -8.0109 | 114.8346 | -8.3954 | -7.7683 | 34.552 | 0.19684 | 0.10071 | 0.72327 | 114.9353 | -8.313 | -0.37537 | 0.20142 | 0.009156 | 0.25177 | -80.0812 | -0.29297 | 0.30212 | 0.38452 | 8.1207 | 8.7433 | 42.572 | 122.8546 | 0.009156 | 122.9553 | 8.2169 | -0.29297 | 122.8546 | 0.009156 | 8.2169 | 42.572 | 122.9553 | -123.0286 | -122.9462
1206.1875 | 122.8134 | -8.0978 | 114.537 | -0.0031279 | 0.018801 | 0.0078079 | -0.0049453 | 0.061395 | 0.038858 | 0.14483 | -8.1894 | 114.7568 | -8.5052 | -7.933 | 33.6823 | 0.09613 | 0.19684 | 0.67749 | 114.8712 | -8.4137 | -0.40741 | 0.21973 | -0.091553 | 0.1648 | -80.8548 | -0.31586 | 0.33417 | 0.31586 | 8.2947 | 8.7753 | 41.7801 | 122.8546 | -0.091553 | 122.9691 | 8.194 | -0.31586 | 122.8546 | -0.091553 | 8.194 | 41.7801 | 122.9691 | -123.0423 | -122.9507
1207.875 | 122.7219 | -9.3155 | 113.3652 | 0.01976 | 0.017733 | 0.010158 | -0.0043045 | 0.0599 | 0.036722 | 0.14333 | -9.3155 | 113.6078 | -9.6451 | -9.0408 | 33.2016 | 0.15106 | 0.13275 | 0.67749 | 113.6993 | -9.5398 | -0.32959 | 0.24262 | 0 | 0.27466 | -80.1636 | -0.2243 | 0.33417 | 0.32959 | 9.4482 | 9.993 | 42.5171 | 122.9233 | 0 | 123.0148 | 9.4666 | -0.2243 | 122.9233 | 0 | 9.4666 | 42.5171 | 123.0148 | -123.0103 | -122.905
1209.625 | 122.7356 | -8.1207 | 114.5187 | 0.0045011 | 0.01346 | 0.0082351 | -0.010713 | 0.060754 | 0.03779 | 0.14526 | -8.107 | 114.6927 | -8.4915 | -7.8369 | 33.3893 | 0.22888 | 0.004578 | 0.79193 | 114.798 | -8.4137 | -0.37079 | 0.17395 | 0.013733 | 0.28381 | -81.1295 | -0.29297 | 0.27924 | 0.38452 | 8.1253 | 8.9127 | 41.51 | 122.8134 | 0.013733 | 122.9187 | 8.3496 | -0.29297 | 122.8134 | 0.013733 | 8.3496 | 41.51 | 122.9187 | -123.0103 | -122.9324
1211.3125 | 122.7081 | -8.4641 | 114.267 | 0.0045011 | 0.019015 | 0.0058853 | -0.0032363 | 0.060968 | 0.037576 | 0.14504 | -8.6014 | 114.3723 | -8.8486 | -8.3405 | 32.1304 | 0.11902 | 0.091553 | 0.5722 | 114.4913 | -8.7662 | -0.38452 | 0.10528 | -0.13733 | 0.1236 | -82.1365 | -0.30212 | 0.2243 | 0.24719 | 8.5556 | 9.0363 | 40.5945 | 122.8363 | -0.13733 | 122.9553 | 8.5831 | -0.30212 | 122.8363 | -0.13733 | 8.5831 | 40.5945 | 122.9553 | -123.1155 | -123.0331
1213.0625 | 122.7493 | -8.5236 | 114.1571 | 0.0045011 | 0.016878 | 0.0075943 | -0.0098587 | 0.059259 | 0.039712 | 0.14398 | -8.5052 | 114.2715 | -8.8898 | -8.2397 | 31.8283 | 0.23346 | -0.004578 | 0.75989 | 114.3951 | -8.8211 | -0.36621 | 0.11444 | 0.018311 | 0.28381 | -82.3288 | -0.29755 | 0.23804 | 0.38452 | 8.519 | 9.2834 | 40.3519 | 122.7951 | 0.018311 | 122.9187 | 8.757 | -0.29755 | 122.7951 | 0.018311 | 8.757 | 40.3519 | 122.9187 | -123.0469 | -122.9782
1214.7969 | 122.7539 | -9.407 | 113.2736 | -0.0031279 | 0.018801 | 0.0046037 | -0.0094315 | 0.06225 | 0.039712 | 0.14291 | -9.4299 | 113.3514 | -9.8236 | -9.1782 | 31.0135 | 0.24261 | -0.009155 | 0.75531 | 113.4705 | -9.6954 | -0.41657 | 0.077819 | -0.022889 | 0.22888 | -82.2601 | -0.28839 | 0.19684 | 0.39368 | 9.3979 | 10.1624 | 40.4205 | 122.7585 | -0.022889 | 122.8775 | 9.6497 | -0.28839 | 122.7585 | -0.022889 | 9.6497 | 40.4205 | 122.8775 | -123.0972 | -122.9691
1216.5 | 122.6852 | -8.7662 | 113.9557 | 0.0045011 | 0.023928 | 0.0095169 | -0.0013137 | 0.062677 | 0.040781 | 0.14611 | -8.7296 | 114.1663 | -9.1095 | -8.519 | 30.5145 | 0.14191 | 0.11444 | 0.55847 | 114.2487 | -9.0225 | -0.34332 | 0.21057 | 0.036621 | 0.24719 | -83.4412 | -0.25635 | 0.29297 | 0.37994 | 8.8806 | 9.3246 | 39.2807 | 122.9324 | 0.036621 | 123.0148 | 8.9081 | -0.25635 | 122.9324 | 0.036621 | 8.9081 | 39.2807 | 123.0148 | -123.0652 | -122.9782
1218.25 | 122.6669 | -8.6609 | 114.0747 | 0.0045011 | 0.018374 | 0.0052445 | -0.0040909 | 0.061823 | 0.039499 | 0.14868 | -8.7296 | 114.2075 | -9.05 | -8.4961 | 29.5761 | 0.086975 | 0.11444 | 0.4303 | 114.3219 | -8.9264 | -0.3891 | 0.13275 | -0.068664 | 0.16479 | -84.4986 | -0.2655 | 0.24719 | 0.32044 | 8.7753 | 9.0912 | 38.237 | 122.8683 | -0.068664 | 122.9828 | 8.7479 | -0.2655 | 122.8683 | -0.068664 | 8.7479 | 38.237 | 122.9828 | -123.1247 | -123.0011
1220 | 122.7631 | -8.5419 | 114.1571 | -0.0031279 | 0.015169 | 0.0099441 | -0.0092179 | 0.059473 | 0.041635 | 0.14739 | -8.5281 | 114.3219 | -8.876 | -8.2855 | 29.393 | 0.20599 | 0.045776 | 0.59967 | 114.3494 | -8.8257 | -0.33417 | 0.16479 | 0.013733 | 0.25635 | -84.7641 | -0.28381 | 0.19226 | 0.3479 | 8.5876 | 9.1415 | 37.9349 | 122.8638 | 0.013733 | 122.8912 | 8.7479 | -0.28381 | 122.8638 | 0.013733 | 8.7479 | 37.9349 | 122.8912 | -123.0331 | -122.9828
1221.7656 | 122.6395 | -8.5098 | 114.2624 | -0.0031279 | 0.017306 | 0.0058853 | -0.0047317 | 0.061182 | 0.039712 | 0.14611 | -8.4732 | 114.3951 | -8.8577 | -8.2397 | 29.512 | 0.12817 | 0.07782 | 0.52643 | 114.5187 | -8.757 | -0.3479 | 0.13275 | 0.036621 | 0.27008 | -84.7504 | -0.24719 | 0.25635 | 0.38452 | 8.5876 | 9.0363 | 38.0219 | 122.905 | 0.036621 | 123.0286 | 8.638 | -0.24719 | 122.905 | 0.036621 | 8.638 | 38.0219 | 123.0286 | -123.1201 | -123.0194
1223.4531 | 122.7036 | -8.6334 | 114.0747 | 0.0045011 | 0.019869 | 0.0099441 | -0.0053727 | 0.060541 | 0.039712 | 0.14761 | -8.6975 | 114.2578 | -9.0134 | -8.4503 | 29.2282 | 0.09613 | 0.086975 | 0.38452 | 114.3768 | -8.9081 | -0.37994 | 0.1831 | -0.064087 | 0.18311 | -84.8465 | -0.27466 | 0.30212 | 0.31586 | 8.7204 | 9.0179 | 37.8616 | 122.8912 | -0.064087 | 123.0103 | 8.7296 | -0.27466 | 122.8912 | -0.064087 | 8.7296 | 37.8616 | 123.0103 | -123.0881 | -122.9828
1225.2031 | 122.7905 | -8.6105 | 114.0472 | 0.0045011 | 0.017306 | 0.0050309 | -0.0070815 | 0.061609 | 0.040781 | 0.14633 | -8.6975 | 114.2761 | -9.0088 | -8.4595 | 29.1504 | 0.091553 | 0.16022 | 0.43488 | 114.3494 | -8.9127 | -0.39825 | 0.22888 | -0.086975 | 0.15106 | -84.8969 | -0.30212 | 0.30212 | 0.31128 | 8.7708 | 9.0454 | 37.7609 | 122.8867 | -0.086975 | 122.9599 | 8.7021 | -0.30212 | 122.8867 | -0.086975 | 8.7021 | 37.7609 | 122.9599 | -123.056 | -122.9599
1226.9062 | 122.644 | -8.7341 | 114.0152 | 0.012131 | 0.019228 | 0.0088761 | -0.0049453 | 0.060968 | 0.040781 | 0.14846 | -8.6563 | 114.1388 | -9.05 | -8.4183 | 28.9764 | 0.21515 | -0.091553 | 0.54932 | 114.2487 | -8.9493 | -0.31586 | 0.1236 | 0.07782 | 0.31586 | -85.0388 | -0.21515 | 0.23346 | 0.39368 | 8.6426 | 9.2834 | 37.7106 | 122.8729 | 0.07782 | 122.9828 | 8.9493 | -0.21515 | 122.8729 | 0.07782 | 8.9493 | 37.7106 | 122.9828 | -123.0652 | -122.9645
1228.6406 | 122.699 | -8.6334 | 114.0839 | 0.012131 | 0.018374 | 0.0095169 | -0.0045181 | 0.059686 | 0.038644 | 0.14803 | -8.6838 | 114.2578 | -8.9996 | -8.4595 | 28.6652 | 0.082397 | 0.09613 | 0.40741 | 114.4043 | -8.8715 | -0.36621 | 0.17395 | -0.050354 | 0.17395 | -85.4187 | -0.23804 | 0.32044 | 0.31586 | 8.7296 | 9.0408 | 37.2986 | 122.8912 | -0.050354 | 123.0377 | 8.7158 | -0.23804 | 122.8912 | -0.050354 | 8.7158 | 37.2986 | 123.0377 | -123.0835 | -122.9553
1230.3906 | 122.7448 | -8.7708 | 113.9008 | -0.010757 | 0.019228 | 0.0035355 | -0.0096451 | 0.0599 | 0.04249 | 0.14825 | -8.7845 | 114.0793 | -9.1278 | -8.5556 | 28.6057 | 0.17853 | -0.032043 | 0.48065 | 114.1846 | -9.05 | -0.35706 | 0.17853 | -0.013733 | 0.21515 | -85.2951 | -0.27924 | 0.28381 | 0.34332 | 8.7387 | 9.2514 | 37.3764 | 122.85 | -0.013733 | 122.9553 | 8.9493 | -0.27924 | 122.85 | -0.013733 | 8.9493 | 37.3764 | 122.9553 | -123.0286 | -122.9507
1232.0938 | 122.7585 | -8.5922 | 114.0701 | 0.0045011 | 0.02051 | 0.0082351 | -0.012422 | 0.058618 | 0.038644 | 0.1459 | -8.5419 | 114.2624 | -8.9172 | -8.2901 | 29.2145 | 0.21973 | -0.050354 | 0.54932 | 114.3631 | -8.8348 | -0.32501 | 0.19226 | 0.050354 | 0.30212 | -84.8557 | -0.24262 | 0.29297 | 0.37537 | 8.5419 | 9.1415 | 37.8067 | 122.8546 | 0.050354 | 122.9553 | 8.812 | -0.24262 | 122.8546 | 0.050354 | 8.812 | 37.8067 | 122.9553 | -122.9874 | -122.905
1233.8438 | 122.6761 | -8.9584 | 113.7863 | 0.0045011 | 0.019442 | 0.0071671 | -0.0036637 | 0.063318 | 0.040567 | 0.14782 | -8.9676 | 113.9557 | -9.2972 | -8.725 | 28.569 | 0.11444 | 0.041199 | 0.41657 | 114.0472 | -9.2194 | -0.33875 | 0.16937 | -0.009155 | 0.23346 | -85.2173 | -0.26093 | 0.26093 | 0.32959 | 8.9996 | 9.375 | 37.5275 | 122.9141 | -0.009155 | 123.0057 | 9.0729 | -0.26093 | 122.9141 | -0.009155 | 9.0729 | 37.5275 | 123.0057 | -123.0835 | -123.0057
1235.5156 | 122.7493 | -8.757 | 113.9099 | -0.010757 | 0.016878 | 0.0069535 | -0.0087905 | 0.059045 | 0.040781 | 0.14526 | -8.7158 | 114.093 | -9.0866 | -8.4915 | 28.3997 | 0.19226 | 0 | 0.49896 | 114.1617 | -9.0408 | -0.32959 | 0.18311 | 0.041199 | 0.2655 | -85.5103 | -0.28381 | 0.25177 | 0.37079 | 8.757 | 9.256 | 37.1567 | 122.85 | 0.041199 | 122.9187 | 8.9493 | -0.28381 | 122.85 | 0.041199 | 8.9493 | 37.1567 | 122.9187 | -122.9965 | -122.9507
1237.2656 | 122.7997 | -8.8348 | 113.8092 | -0.0031279 | 0.017519 | 0.0084489 | -0.0087905 | 0.062677 | 0.04249 | 0.14761 | -8.9127 | 114.0015 | -9.2056 | -8.6288 | 28.2715 | 0.15564 | -0.032043 | 0.43945 | 114.0839 | -9.1232 | -0.37079 | 0.19226 | -0.07782 | 0.20599 | -85.5377 | -0.28839 | 0.27466 | 0.29297 | 8.8028 | 9.2743 | 37.1063 | 122.8363 | -0.07782 | 122.9187 | 8.9905 | -0.28839 | 122.8363 | -0.07782 | 8.9905 | 37.1063 | 122.9187 | -123.0148 | -122.9324
1239.0156 | 122.7585 | -9.3475 | 113.3286 | -0.010757 | 0.021151 | 0.010158 | -0.0068679 | 0.060541 | 0.043558 | 0.14739 | -9.3475 | 113.4521 | -9.7092 | -9.0729 | 27.9602 | 0.21973 | -0.086975 | 0.5127 | 113.5666 | -9.6359 | -0.36163 | 0.1236 | 0 | 0.27466 | -85.3683 | -0.28839 | 0.23804 | 0.36163 | 9.2606 | 9.8602 | 37.3077 | 122.7997 | 0 | 122.9141 | 9.5673 | -0.28839 | 122.7997 | 0 | 9.5673 | 37.3077 | 122.9141 | -123.0377 | -122.9645
1240.6875 | 122.7448 | -9.2331 | 113.4613 | 0.0045011 | 0.016238 | 0.0088761 | -0.00067292 | 0.059686 | 0.040567 | 0.14547 | -9.2468 | 113.6627 | -9.581 | -8.9859 | 29.0543 | 0.10071 | 0.059509 | 0.40283 | 113.7863 | -9.4894 | -0.3479 | 0.20142 | -0.013733 | 0.24719 | -84.407 | -0.25635 | 0.32501 | 0.33417 | 9.2926 | 9.6359 | 38.2874 | 122.8958 | -0.013733 | 123.0194 | 9.3338 | -0.25635 | 122.8958 | -0.013733 | 9.3338 | 38.2874 | 123.0194 | -123.0423 | -122.9507
1242.4375 | 122.7768 | -8.8577 | 113.8138 | -0.0031279 | 0.016451 | 0.0086625 | -0.0032363 | 0.060541 | 0.040567 | 0.14675 | -8.9127 | 114.0335 | -9.2514 | -8.6517 | 28.45 | 0.086975 | 0.086975 | 0.38452 | 114.1251 | -9.1415 | -0.39368 | 0.21973 | -0.054932 | 0.20599 | -85.3638 | -0.28381 | 0.31128 | 0.33875 | 8.9447 | 9.2422 | 37.3077 | 122.8912 | -0.054932 | 122.9828 | 8.9447 | -0.28381 | 122.8912 | -0.054932 | 8.9447 | 37.3077 | 122.9828 | -123.0652 | -122.9553
1244.125 | 122.7814 | -9.0225 | 113.5803 | 0.0045011 | 0.017733 | 0.0084489 | -0.010927 | 0.059259 | 0.042062 | 0.14697 | -9.1141 | 113.7863 | -9.3979 | -8.8669 | 28.2028 | 0.15106 | -0.041199 | 0.43945 | 113.8916 | -9.3246 | -0.37537 | 0.20599 | -0.091553 | 0.15564 | -85.3775 | -0.30212 | 0.31128 | 0.28381 | 8.9813 | 9.462 | 37.2253 | 122.8088 | -0.091553 | 122.9141 | 9.1736 | -0.30212 | 122.8088 | -0.091553 | 9.1736 | 37.2253 | 122.9141 | -122.9782 | -122.905
1245.875 | 122.7951 | -8.9218 | 113.7039 | 0.0045011 | 0.014742 | 0.0086625 | -0.0090041 | 0.061395 | 0.041421 | 0.14825 | -9.0042 | 113.9328 | -9.2926 | -8.7387 | 28.0106 | 0.14191 | -0.018311 | 0.44403 | 113.9832 | -9.2331 | -0.37079 | 0.22888 | -0.082397 | 0.18311 | -85.6934 | -0.31128 | 0.27924 | 0.28839 | 8.9035 | 9.3658 | 36.9324 | 122.8546 | -0.082397 | 122.905 | 9.0637 | -0.31128 | 122.8546 | -0.082397 | 9.0637 | 36.9324 | 122.905 | -122.9965 | -122.937
1247.6406 | 122.7859 | -8.9722 | 113.6765 | 0.0045011 | 0.015597 | 0.0095169 | -0.0070815 | 0.062677 | 0.041849 | 0.14654 | -9.0271 | 113.8596 | -9.3292 | -8.7616 | 27.7176 | 0.14648 | -0.032043 | 0.44403 | 113.9648 | -9.2606 | -0.35706 | 0.18311 | -0.054932 | 0.21057 | -85.9589 | -0.28839 | 0.28839 | 0.30212 | 8.9401 | 9.4162 | 36.6898 | 122.8317 | -0.054932 | 122.937 | 9.1187 | -0.28839 | 122.8317 | -0.054932 | 9.1187 | 36.6898 | 122.937 | -123.0057 | -122.937
1249.4062 | 122.7631 | -8.9172 | 113.7451 | 0.012131 | 0.017733 | 0.0078079 | -0.0072953 | 0.060114 | 0.04249 | 0.14782 | -8.9355 | 113.9328 | -9.2468 | -8.6838 | 28.0289 | 0.14191 | -0.059509 | 0.4303 | 114.0152 | -9.169 | -0.32959 | 0.18768 | -0.018311 | 0.23346 | -85.7162 | -0.25177 | 0.27008 | 0.31128 | 8.8577 | 9.3475 | 36.9461 | 122.85 | -0.018311 | 122.9324 | 9.0591 | -0.25177 | 122.85 | -0.018311 | 9.0591 | 36.9461 | 122.9324 | -122.9919 | -122.9141
1251.1562 | 122.7905 | -8.8394 | 113.8046 | 0.01976 | 0.017947 | 0.0054581 | -0.0038773 | 0.058832 | 0.041208 | 0.14782 | -8.9539 | 114.0015 | -9.2743 | -8.6517 | 27.9007 | 0.068665 | 0.091553 | 0.36621 | 114.1296 | -9.137 | -0.43488 | 0.19684 | -0.11444 | 0.18768 | -85.9039 | -0.29755 | 0.32501 | 0.32044 | 8.931 | 9.2056 | 36.7401 | 122.8409 | -0.11444 | 122.9691 | 8.9081 | -0.29755 | 122.8409 | -0.11444 | 8.9081 | 36.7401 | 122.9691 | -123.0789 | -122.9416
1252.9062 | 122.7127 | -8.8303 | 113.9145 | 0.0045011 | 0.017306 | 0.0086625 | -0.0017411 | 0.060327 | 0.041421 | 0.14803 | -8.8669 | 114.0701 | -9.1873 | -8.6243 | 27.2415 | 0.045776 | 0.064087 | 0.31128 | 114.1846 | -9.0912 | -0.35706 | 0.15564 | -0.036621 | 0.20599 | -86.673 | -0.26093 | 0.27008 | 0.32043 | 8.8943 | 9.1415 | 36.0718 | 122.9004 | -0.036621 | 123.0148 | 8.876 | -0.26093 | 122.9004 | -0.036621 | 8.876 | 36.0718 | 123.0148 | -123.1018 | -123.0057
1254.6562 | 122.7997 | -8.8577 | 113.7588 | 0.0045011 | 0.015383 | 0.0060989 | -0.010072 | 0.060754 | 0.043771 | 0.14782 | -8.9539 | 113.942 | -9.2377 | -8.6929 | 27.1454 | 0.12817 | -0.050354 | 0.3891 | 114.0472 | -9.1599 | -0.37994 | 0.18311 | -0.09613 | 0.16479 | -86.6135 | -0.30212 | 0.28839 | 0.28381 | 8.8074 | 9.2468 | 36.0031 | 122.7997 | -0.09613 | 122.905 | 8.9859 | -0.30212 | 122.7997 | -0.09613 | 8.9859 | 36.0031 | 122.905 | -122.9965 | -122.9187
1256.3438 | 122.7127 | -8.7753 | 113.942 | 0.01976 | 0.01816 | 0.0082351 | -0.0025955 | 0.06225 | 0.042703 | 0.14825 | -8.8486 | 114.1022 | -9.1507 | -8.6014 | 26.9943 | 0.050354 | 0.054932 | 0.30212 | 114.2349 | -9.0179 | -0.37537 | 0.16022 | -0.073242 | 0.17395 | -86.9476 | -0.24261 | 0.29297 | 0.30212 | 8.8303 | 9.0775 | 35.7697 | 122.8775 | -0.073242 | 123.0103 | 8.8257 | -0.24261 | 122.8775 | -0.073242 | 8.8257 | 35.7697 | 123.0103 | -123.0927 | -122.9599
1258.0781 | 122.6624 | -8.8486 | 113.8824 | 0.01976 | 0.017519 | 0.0056717 | -0.0045181 | 0.062891 | 0.040994 | 0.14782 | -8.7982 | 114.0381 | -9.1415 | -8.551 | 27.1362 | 0.17853 | -0.10986 | 0.43945 | 114.1296 | -9.0591 | -0.29297 | 0.15564 | 0.050354 | 0.29755 | -86.7462 | -0.21057 | 0.24719 | 0.34332 | 8.7387 | 9.288 | 35.9848 | 122.8867 | 0.050354 | 122.9782 | 9.0271 | -0.21057 | 122.8867 | 0.050354 | 9.0271 | 35.9848 | 122.9782 | -123.024 | -122.9416
1259.7656 | 122.7676 | -9.2834 | 113.4064 | 0.0045011 | 0.016665 | 0.0093033 | -0.0053727 | 0.060968 | 0.04014 | 0.14547 | -9.3246 | 113.6124 | -9.6313 | -9.0363 | 27.0309 | 0.082397 | 0.082397 | 0.3891 | 113.7405 | -9.4986 | -0.3479 | 0.20599 | -0.041199 | 0.24719 | -86.3754 | -0.21515 | 0.33417 | 0.3067 | 9.3658 | 9.6725 | 36.3144 | 122.8958 | -0.041199 | 123.024 | 9.3658 | -0.21515 | 122.8958 | -0.041199 | 9.3658 | 36.3144 | 123.024 | -123.0377 | -122.905
1261.5312 | 122.7539 | -9.3933 | 113.2645 | -0.0031279 | 0.017092 | 0.012721 | -0.0098587 | 0.060541 | 0.041635 | 0.14697 | -9.3842 | 113.4567 | -9.7046 | -9.1324 | 27.0538 | 0.15564 | -0.009155 | 0.45776 | 113.562 | -9.6634 | -0.31128 | 0.19226 | 0.009156 | 0.26093 | -86.2106 | -0.27008 | 0.29755 | 0.32043 | 9.3842 | 9.8511 | 36.4471 | 122.85 | 0.009156 | 122.9553 | 9.549 | -0.27008 | 122.85 | 0.009156 | 9.549 | 36.4471 | 122.9553 | -122.9691 | -122.9279
1263.2188 | 122.7768 | -9.4162 | 113.1958 | 0.0045011 | 0.017733 | 0.0060989 | -0.0105 | 0.060541 | 0.04313 | 0.14697 | -9.4437 | 113.4521 | -9.7641 | -9.1965 | 26.8616 | 0.15106 | -0.050354 | 0.48065 | 113.53 | -9.7 | -0.3479 | 0.25635 | -0.027466 | 0.21973 | -86.3342 | -0.28381 | 0.33417 | 0.32043 | 9.3658 | 9.8969 | 36.2778 | 122.8683 | -0.027466 | 122.9462 | 9.5673 | -0.28381 | 122.8683 | -0.027466 | 9.5673 | 36.2778 | 122.9462 | -122.9599 | -122.8958
1264.9688 | 122.7081 | -9.4849 | 113.2004 | -0.0031279 | 0.019015 | 0.010585 | -0.0015273 | 0.060327 | 0.040567 | 0.14633 | -9.5123 | 113.4109 | -9.8511 | -9.256 | 26.9806 | 0.07782 | 0.045776 | 0.45319 | 113.5025 | -9.7458 | -0.36621 | 0.21057 | -0.027466 | 0.22888 | -86.2198 | -0.26093 | 0.30212 | 0.33875 | 9.5306 | 9.938 | 36.4655 | 122.8958 | -0.027466 | 122.9874 | 9.5627 | -0.26093 | 122.8958 | -0.027466 | 9.5627 | 36.4655 | 122.9874 | -123.0515 | -122.9462
1266.7344 | 122.8088 | -9.2789 | 113.3606 | 0.012131 | 0.016451 | 0.0086625 | -0.0070815 | 0.060541 | 0.041208 | 0.14568 | -9.4025 | 113.5757 | -9.6909 | -9.1461 | 26.6785 | 0.041199 | 0.09613 | 0.46692 | 113.6993 | -9.6085 | -0.41199 | 0.21515 | -0.1236 | 0.13275 | -86.6821 | -0.32959 | 0.33875 | 0.28839 | 9.375 | 9.7458 | 35.9573 | 122.8546 | -0.1236 | 122.9782 | 9.3201 | -0.32959 | 122.8546 | -0.1236 | 9.3201 | 35.9573 | 122.9782 | -123.0515 | -122.9691
1268.4219 | 122.8043 | -9.2468 | 113.3835 | 0.0045011 | 0.019869 | 0.0078079 | -0.0060135 | 0.058405 | 0.041635 | 0.14718 | -9.3567 | 113.649 | -9.6588 | -9.1095 | 27.2552 | 0.036621 | 0.10529 | 0.45776 | 113.736 | -9.5215 | -0.41199 | 0.2655 | -0.10986 | 0.13733 | -86.1282 | -0.27466 | 0.35248 | 0.30212 | 9.3521 | 9.7046 | 36.5021 | 122.8958 | -0.10986 | 122.9828 | 9.2834 | -0.27466 | 122.8958 | -0.10986 | 9.2834 | 36.5021 | 122.9828 | -123.0423 | -122.905
1270.1719 | 122.7356 | -9.343 | 113.3102 | -0.0031279 | 0.016878 | 0.0052445 | -0.0079361 | 0.059259 | 0.041635 | 0.14803 | -9.3292 | 113.5025 | -9.6771 | -9.0775 | 27.2552 | 0.18768 | -0.10071 | 0.60425 | 113.5849 | -9.6176 | -0.33417 | 0.19226 | 0.013733 | 0.2655 | -86.055 | -0.27466 | 0.27466 | 0.3479 | 9.2422 | 9.9472 | 36.5982 | 122.8455 | 0.013733 | 122.9279 | 9.5306 | -0.27466 | 122.8455 | 0.013733 | 9.5306 | 36.5982 | 122.9279 | -122.9874 | -122.9279
1271.9219 | 122.7539 | -9.2834 | 113.3835 | 0.012131 | 0.01816 | 0.0048173 | -0.0060135 | 0.059473 | 0.040781 | 0.14611 | -9.2331 | 113.5712 | -9.5947 | -9.0042 | 28.3218 | 0.17853 | -0.086975 | 0.62714 | 113.6856 | -9.5306 | -0.31128 | 0.18768 | 0.050354 | 0.27924 | -85.0616 | -0.24719 | 0.30212 | 0.36163 | 9.1965 | 9.9106 | 37.6053 | 122.8546 | 0.050354 | 122.9691 | 9.462 | -0.24719 | 122.8546 | 0.050354 | 9.462 | 37.6053 | 122.9691 | -122.9782 | -122.9141
1273.6719 | 122.8043 | -9.1415 | 113.4567 | 0.0045011 | 0.018587 | 0.0060989 | -0.0043045 | 0.0599 | 0.041635 | 0.14654 | -9.2331 | 113.7588 | -9.5169 | -8.9859 | 27.594 | 0.032043 | 0.10529 | 0.4715 | 113.8596 | -9.4299 | -0.37537 | 0.30212 | -0.091552 | 0.15564 | -85.8627 | -0.28839 | 0.40283 | 0.28381 | 9.2468 | 9.613 | 36.7355 | 122.9004 | -0.091552 | 123.0011 | 9.1736 | -0.28839 | 122.9004 | -0.091552 | 9.1736 | 36.7355 | 123.0011 | -122.9736 | -122.8867
1275.3594 | 122.644 | -8.8074 | 113.8916 | -0.0031279 | 0.019228 | 0.0082351 | -0.0032363 | 0.062036 | 0.038858 | 0.14355 | -8.7433 | 114.0656 | -9.1141 | -8.4869 | 33.9066 | 0.16022 | -0.11444 | 0.56763 | 114.1937 | -9.0179 | -0.3067 | 0.17395 | 0.064087 | 0.32043 | -79.985 | -0.21057 | 0.30212 | 0.37079 | 8.6929 | 9.375 | 42.7139 | 122.8729 | 0.064087 | 123.0011 | 8.9676 | -0.21057 | 122.8729 | 0.064087 | 8.9676 | 42.7139 | 123.0011 | -123.0057 | -122.9095
1277.0469 | 122.6669 | -9.256 | 113.4705 | 0.01976 | 0.018801 | 0.011867 | -0.0017411 | 0.061182 | 0.041849 | 0.14868 | -9.2102 | 113.681 | -9.5444 | -8.9401 | 27.1042 | 0.12817 | -0.11444 | 0.49439 | 113.7817 | -9.4254 | -0.28839 | 0.21057 | 0.045776 | 0.31586 | -86.3663 | -0.16937 | 0.31128 | 0.33417 | 9.1415 | 9.7504 | 36.3602 | 122.937 | 0.045776 | 123.0377 | 9.3842 | -0.16937 | 122.937 | 0.045776 | 9.3842 | 36.3602 | 123.0377 | -123.0148 | -122.8958
1278.7344 | 122.7905 | -8.931 | 113.7131 | 0.0045011 | 0.017092 | 0.0035355 | -0.0079361 | 0.059045 | 0.039712 | 0.14462 | -8.9996 | 113.9328 | -9.3018 | -8.7479 | 32.8674 | 0.064087 | 0.068665 | 0.47607 | 114.0289 | -9.2194 | -0.37079 | 0.21973 | -0.068665 | 0.1831 | -80.8456 | -0.28839 | 0.31586 | 0.30212 | 8.9996 | 9.407 | 41.7984 | 122.8638 | -0.068665 | 122.9599 | 8.9951 | -0.28839 | 122.8638 | -0.068665 | 8.9951 | 41.7984 | 122.9599 | -123.0148 | -122.9324
1280.4219 | 122.7173 | -9.2011 | 113.5071 | 0.0045011 | 0.019869 | 0.010799 | -0.0028091 | 0.062891 | 0.038858 | 0.14889 | -9.2606 | 113.7039 | -9.5627 | -9.0317 | 27.2873 | 0.022888 | 0.041199 | 0.35248 | 113.8138 | -9.4757 | -0.36163 | 0.19684 | -0.059509 | 0.16937 | -86.2198 | -0.27466 | 0.3067 | 0.30212 | 9.2422 | 9.5535 | 36.4883 | 122.905 | -0.059509 | 123.0148 | 9.2239 | -0.27466 | 122.905 | -0.059509 | 9.2239 | 36.4883 | 123.0148 | -123.0698 | -122.9828
1282.1094 | 122.8043 | -9.2468 | 113.3835 | 0.012131 | 0.01816 | 0.0063125 | -0.0070815 | 0.0599 | 0.042917 | 0.14782 | -9.3521 | 113.6032 | -9.6497 | -9.1003 | 27.4979 | 0.032043 | 0.1236 | 0.42572 | 113.7222 | -9.5444 | -0.40283 | 0.21973 | -0.10529 | 0.14648 | -85.8856 | -0.29755 | 0.33875 | 0.29755 | 9.3704 | 9.6725 | 36.7447 | 122.85 | -0.10529 | 122.9691 | 9.2789 | -0.29755 | 122.85 | -0.10529 | 9.2789 | 36.7447 | 122.9691 | -123.0331 | -122.9279
1283.8594 | 122.7814 | -9.2743 | 113.3698 | 0.012131 | 0.01816 | 0.0086625 | -0.0053727 | 0.059045 | 0.041421 | 0.14761 | -9.375 | 113.5895 | -9.6451 | -9.1141 | 27.5574 | 0.027466 | 0.13275 | 0.40741 | 113.6948 | -9.5993 | -0.37079 | 0.21973 | -0.10071 | 0.16022 | -85.8124 | -0.32501 | 0.32501 | 0.27008 | 9.407 | 9.6817 | 36.8317 | 122.8638 | -0.10071 | 122.9691 | 9.3018 | -0.32501 | 122.8638 | -0.10071 | 9.3018 | 36.8317 | 122.9691 | -123.0148 | -122.9691
1285.5312 | 122.7951 | -9.3338 | 113.2736 | 0.012131 | 0.017092 | 0.0084489 | -0.0105 | 0.060114 | 0.042276 | 0.14633 | -9.4116 | 113.5208 | -9.668 | -9.1507 | 27.5299 | 0.12817 | -0.041199 | 0.45319 | 113.6032 | -9.6085 | -0.33417 | 0.24719 | -0.07782 | 0.1831 | -85.7437 | -0.27466 | 0.32959 | 0.25635 | 9.2926 | 9.787 | 36.8637 | 122.8546 | -0.07782 | 122.937 | 9.462 | -0.27466 | 122.8546 | -0.07782 | 9.462 | 36.8637 | 122.937 | -122.9416 | -122.8821
1287.2969 | 122.7676 | -9.288 | 113.3331 | 0.012131 | 0.014101 | 0.0054581 | -0.010072 | 0.059473 | 0.04313 | 0.14739 | -9.3521 | 113.5025 | -9.6451 | -9.0958 | 27.2415 | 0.11444 | -0.041199 | 0.42114 | 113.6673 | -9.5764 | -0.35706 | 0.16937 | -0.064087 | 0.19226 | -86.0916 | -0.28839 | 0.33417 | 0.29297 | 9.2468 | 9.7092 | 36.5295 | 122.7905 | -0.064087 | 122.9553 | 9.4025 | -0.28839 | 122.7905 | -0.064087 | 9.4025 | 36.5295 | 122.9553 | -122.9782 | -122.9095
1288.9844 | 122.7036 | -9.3796 | 113.2645 | -0.0031279 | 0.01816 | 0.0095169 | -0.0072953 | 0.060754 | 0.042276 | 0.14761 | -9.4116 | 113.4384 | -9.7275 | -9.1599 | 26.9531 | 0.11902 | -0.068665 | 0.43488 | 113.5529 | -9.6313 | -0.3479 | 0.17395 | -0.032043 | 0.21973 | -86.3113 | -0.25177 | 0.28839 | 0.31586 | 9.3109 | 9.8145 | 36.3327 | 122.818 | -0.032043 | 122.9324 | 9.4986 | -0.25177 | 122.818 | -0.032043 | 9.4986 | 36.3327 | 122.9324 | -122.9919 | -122.8958
1290.7188 | 122.7631 | -9.2834 | 113.3652 | 0.012131 | 0.015597 | 0.0065263 | -0.0087905 | 0.0599 | 0.040567 | 0.14782 | -9.3292 | 113.5574 | -9.613 | -9.0591 | 26.8295 | 0.12817 | -0.059509 | 0.41199 | 113.6627 | -9.5352 | -0.32959 | 0.19226 | -0.045777 | 0.2243 | -86.5356 | -0.25177 | 0.29755 | 0.28381 | 9.2239 | 9.6954 | 36.113 | 122.8409 | -0.045777 | 122.9462 | 9.4116 | -0.25177 | 122.8409 | -0.045777 | 9.4116 | 36.113 | 122.9462 | -122.9782 | -122.9004
1292.4688 | 122.7036 | -14.4974 | 108.1467 | -0.0031279 | 0.017306 | 0.0099441 | -0.0019547 | 0.060754 | 0.037576 | 0.14355 | -14.6759 | 108.3344 | -14.9002 | -14.4516 | 25.9048 | 0.004578 | 0 | 0.14191 | 108.4534 | -14.8087 | -0.40283 | 0.18768 | -0.17853 | 0.045776 | -82.2418 | -0.31128 | 0.3067 | 0.2243 | 14.4974 | 14.6393 | 40.4022 | 122.8317 | -0.17853 | 122.9507 | 14.502 | -0.31128 | 122.8317 | -0.17853 | 14.502 | 40.4022 | 122.9507 | -123.0469 | -122.9553
1294.1562 | 122.7448 | -13.5544 | 109.0805 | -0.0031279 | 0.017092 | 0.0090897 | -0.0064407 | 0.060114 | 0.041635 | 0.14269 | -13.6414 | 109.2453 | -13.9206 | -13.3987 | 26.3535 | 0.14648 | -0.10071 | 0.31586 | 109.3002 | -13.8474 | -0.36621 | 0.16479 | -0.086975 | 0.15564 | -82.7271 | -0.29297 | 0.21973 | 0.27924 | 13.4537 | 13.8702 | 39.9078 | 122.7997 | -0.086975 | 122.8546 | 13.7009 | -0.29297 | 122.7997 | -0.086975 | 13.7009 | 39.9078 | 122.8546 | -123.0011 | -122.9279
1295.8906 | 122.6669 | -12.8723 | 109.8404 | -0.0031279 | 0.017733 | 0.0093033 | -0.0049453 | 0.058618 | 0.039712 | 0.14333 | -12.9135 | 110.0235 | -13.1973 | -12.6617 | 26.7059 | 0.064087 | -0.022888 | 0.33417 | 110.1334 | -13.1012 | -0.32501 | 0.18311 | -0.041199 | 0.21057 | -83.1345 | -0.22888 | 0.29297 | 0.28381 | 12.8494 | 13.2065 | 39.5782 | 122.8958 | -0.041199 | 123.0057 | 12.9364 | -0.22888 | 122.8958 | -0.041199 | 12.9364 | 39.5782 | 123.0057 | -123.0377 | -122.9416
1297.5781 | 122.7585 | -12.7213 | 109.9091 | 0.012131 | 0.016665 | 0.0090897 | -0.0081497 | 0.060327 | 0.04014 | 0.14462 | -12.7808 | 110.0922 | -13.0371 | -12.529 | 26.6235 | 0.12817 | -0.059509 | 0.3479 | 110.2066 | -12.9822 | -0.31586 | 0.1831 | -0.05951 | 0.19226 | -83.2855 | -0.26093 | 0.29755 | 0.25635 | 12.6617 | 13.0692 | 39.3448 | 122.8134 | -0.05951 | 122.9279 | 12.8494 | -0.26093 | 122.8134 | -0.05951 | 12.8494 | 39.3448 | 122.9279 | -122.9462 | -122.8912
1299.3438 | 122.7905 | -12.7579 | 109.8267 | -0.0031279 | 0.017092 | 0.011653 | -0.0098587 | 0.059045 | 0.042917 | 0.1444 | -12.8677 | 110.051 | -13.1058 | -12.6068 | 26.8066 | 0.11902 | -0.10071 | 0.39368 | 110.1746 | -13.0371 | -0.3479 | 0.2243 | -0.10986 | 0.15106 | -83.02 | -0.27923 | 0.3479 | 0.23804 | 12.6572 | 13.1516 | 39.5645 | 122.8088 | -0.10986 | 122.9324 | 12.8769 | -0.27923 | 122.8088 | -0.10986 | 12.8769 | 39.5645 | 122.9324 | -122.9324 | -122.8638
1301.0938 | 122.6761 | -12.4832 | 110.2203 | -0.0031279 | 0.016451 | 0.0071671 | -0.0060135 | 0.058832 | 0.039926 | 0.14355 | -12.4878 | 110.3897 | -12.7808 | -12.2681 | 28.3813 | 0.13733 | -0.1236 | 0.31128 | 110.4813 | -12.7167 | -0.29755 | 0.16937 | -0.004578 | 0.21515 | -81.839 | -0.23346 | 0.26093 | 0.29297 | 12.3596 | 12.7945 | 40.8646 | 122.8729 | -0.004578 | 122.9645 | 12.6205 | -0.23346 | 122.8729 | -0.004578 | 12.6205 | 40.8646 | 122.9645 | -123.0011 | -122.937
1302.7812 | 122.6761 | -12.5702 | 110.1151 | -0.0031279 | 0.016878 | 0.0082351 | -0.0023819 | 0.059686 | 0.039072 | 0.14462 | -12.6801 | 110.289 | -12.9364 | -12.4649 | 28.3585 | 0.013733 | 0.027466 | 0.27466 | 110.3897 | -12.8448 | -0.36621 | 0.17395 | -0.10986 | 0.10529 | -81.7566 | -0.27466 | 0.27466 | 0.25635 | 12.5977 | 12.8448 | 40.9286 | 122.8592 | -0.10986 | 122.9599 | 12.5839 | -0.27466 | 122.8592 | -0.10986 | 12.5839 | 40.9286 | 122.9599 | -123.0515 | -122.9599
1304.5469 | 122.7219 | -8.9401 | 113.6902 | 0.01976 | 0.016238 | 0.0016129 | -0.010927 | 0.059045 | 0.041208 | 0.14718 | -8.9493 | 113.8824 | -9.2834 | -8.6563 | 30.0751 | 0.16479 | -0.086975 | 0.50354 | 113.942 | -9.2239 | -0.34332 | 0.19226 | -0.009155 | 0.28381 | -83.6151 | -0.28381 | 0.25177 | 0.33417 | 8.8531 | 9.4437 | 39.0152 | 122.8226 | -0.009155 | 122.8821 | 9.1049 | -0.28381 | 122.8226 | -0.009155 | 9.1049 | 39.0152 | 122.8821 | -122.9736 | -122.9141
1306.2344 | 122.6486 | -9.137 | 113.5986 | 0.0045011 | 0.018374 | 0.011012 | -0.0021683 | 0.0599 | 0.039712 | 0.14611 | -9.1003 | 113.7909 | -9.4528 | -8.8486 | 29.2191 | 0.073242 | 0.027466 | 0.38452 | 113.9465 | -9.3384 | -0.31586 | 0.19226 | 0.036621 | 0.28839 | -84.3796 | -0.20142 | 0.3479 | 0.35248 | 9.1644 | 9.5215 | 38.356 | 122.9279 | 0.036621 | 123.0835 | 9.2102 | -0.20142 | 122.9279 | 0.036621 | 9.2102 | 38.356 | 123.0835 | -123.0515 | -122.937
1307.9844 | 122.6944 | -9.1003 | 113.5849 | 0.0045011 | 0.018801 | 0.0097305 | -0.0030227 | 0.063745 | 0.038431 | 0.14504 | -9.1599 | 113.8092 | -9.4482 | -8.9172 | 28.537 | 0.009155 | 0.11902 | 0.3067 | 113.942 | -9.3384 | -0.3479 | 0.2243 | -0.059509 | 0.18311 | -85.0479 | -0.23804 | 0.35706 | 0.28839 | 9.2194 | 9.407 | 37.6373 | 122.9095 | -0.059509 | 123.0423 | 9.1095 | -0.23804 | 122.9095 | -0.059509 | 9.1095 | 37.6373 | 123.0423 | -123.0331 | -122.9233
1309.7344 | 122.644 | -9.2514 | 113.443 | 0.0045011 | 0.018801 | 0.0097305 | -0.0043045 | 0.062036 | 0.038644 | 0.14803 | -9.2743 | 113.6169 | -9.581 | -9.0088 | 28.7384 | 0.10986 | 0.032043 | 0.41657 | 113.7405 | -9.4803 | -0.32959 | 0.17395 | -0.022888 | 0.24262 | -84.7046 | -0.22888 | 0.29755 | 0.3067 | 9.2834 | 9.668 | 37.9898 | 122.8683 | -0.022888 | 122.9919 | 9.3613 | -0.22888 | 122.8683 | -0.022888 | 9.3613 | 37.9898 | 122.9919 | -123.024 | -122.9233
1311.5 | 122.6852 | -9.2194 | 113.4888 | 0.01976 | 0.016024 | 0.0058853 | -0.0045181 | 0.062036 | 0.039499 | 0.14782 | -9.3018 | 113.6444 | -9.5718 | -9.0637 | 28.1937 | 0.032043 | 0.16479 | 0.33417 | 113.7634 | -9.4711 | -0.35248 | 0.15564 | -0.082398 | 0.15564 | -85.2951 | -0.25177 | 0.27466 | 0.27008 | 9.3842 | 9.5535 | 37.413 | 122.8638 | -0.082398 | 122.9828 | 9.2514 | -0.25177 | 122.8638 | -0.082398 | 9.2514 | 37.413 | 122.9828 | -123.0606 | -122.9599
1313.2344 | 122.731 | -9.2102 | 113.4567 | 0.0045011 | 0.019869 | 0.0046037 | -0.0105 | 0.060541 | 0.042062 | 0.14675 | -9.1782 | 113.6536 | -9.5078 | -8.9264 | 28.6743 | 0.16479 | 0.15564 | 0.53101 | 113.736 | -9.4437 | -0.29755 | 0.19684 | 0.032043 | 0.28381 | -84.7824 | -0.23346 | 0.27924 | 0.32959 | 9.3658 | 9.7412 | 37.8845 | 122.8638 | 0.032043 | 122.9462 | 9.375 | -0.23346 | 122.8638 | 0.032043 | 9.375 | 37.8845 | 122.9462 | -122.9645 | -122.9004
1314.9062 | 122.7448 | -9.2056 | 113.4659 | -0.0031279 | 0.017733 | 0.0084489 | -0.0032363 | 0.059686 | 0.039285 | 0.14761 | -9.2743 | 113.6673 | -9.5856 | -9.0088 | 28.9993 | 0.050354 | 0.29755 | 0.39825 | 113.8 | -9.462 | -0.37994 | 0.20142 | -0.068665 | 0.19684 | -84.4666 | -0.25635 | 0.33417 | 0.31128 | 9.5032 | 9.6039 | 38.205 | 122.8729 | -0.068665 | 123.0057 | 9.256 | -0.25635 | 122.8729 | -0.068665 | 9.256 | 38.205 | 123.0057 | -123.0515 | -122.9279
1316.6562 | 122.6349 | -9.1736 | 113.4888 | 0.01976 | 0.015597 | 0.0080215 | -0.0075089 | 0.061609 | 0.04014 | 0.14932 | -9.1278 | 113.6627 | -9.4711 | -8.8943 | 31.1371 | 0.14191 | 0.11444 | 0.48065 | 113.7863 | -9.3887 | -0.29755 | 0.17395 | 0.045776 | 0.27924 | -82.3517 | -0.21515 | 0.29755 | 0.34332 | 9.288 | 9.6542 | 40.3107 | 122.8363 | 0.045776 | 122.9599 | 9.3155 | -0.21515 | 122.8363 | 0.045776 | 9.3155 | 40.3107 | 122.9599 | -122.9599 | -122.8775
1318.4219 | 122.7631 | -9.3933 | 113.2416 | 0.012131 | 0.017519 | 0.010158 | -0.0053727 | 0.058405 | 0.042062 | 0.14782 | -9.4986 | 113.4888 | -9.7549 | -9.2514 | 29.2603 | 0.004578 | 0.35706 | 0.33417 | 113.5803 | -9.7046 | -0.36163 | 0.24719 | -0.10528 | 0.14191 | -83.9813 | -0.31128 | 0.33874 | 0.25635 | 9.7504 | 9.7275 | 38.6536 | 122.8821 | -0.10528 | 122.9736 | 9.3979 | -0.31128 | 122.8821 | -0.10528 | 9.3979 | 38.6536 | 122.9736 | -122.9965 | -122.9462
1320.1094 | 122.6624 | -9.4574 | 113.2233 | -0.010757 | 0.019869 | 0.0088761 | -0.0023819 | 0.062463 | 0.041421 | 0.1491 | -9.4849 | 113.4567 | -9.7733 | -9.2331 | 28.7201 | 0.068665 | 0.16937 | 0.6546 | 113.5529 | -9.6817 | -0.31586 | 0.23346 | -0.027466 | 0.2243 | -84.5032 | -0.2243 | 0.32959 | 0.28839 | 9.6268 | 10.112 | 38.1775 | 122.9141 | -0.027466 | 123.0103 | 9.5261 | -0.2243 | 122.9141 | -0.027466 | 9.5261 | 38.1775 | 123.0103 | -122.9965 | -122.905
1321.8594 | 122.7127 | -9.4482 | 113.1775 | -0.0031279 | 0.017092 | 0.0067399 | -0.0087905 | 0.061609 | 0.039926 | 0.14889 | -9.4254 | 113.4018 | -9.7549 | -9.169 | 28.569 | 0.15106 | 0.16479 | 0.70953 | 113.4842 | -9.7 | -0.3067 | 0.2243 | 0.022888 | 0.27924 | -84.6085 | -0.25177 | 0.3067 | 0.32959 | 9.613 | 10.1578 | 38.0173 | 122.85 | 0.022888 | 122.9324 | 9.5993 | -0.25177 | 122.85 | 0.022888 | 9.5993 | 38.0173 | 122.9324 | -122.9324 | -122.8775
1323.625 | 122.699 | -9.5581 | 113.1226 | -0.0031279 | 0.020083 | 0.01208 | -0.0064407 | 0.063318 | 0.039285 | 0.1491 | -9.6451 | 113.2919 | -9.9152 | -9.4162 | 27.7451 | 0 | 0.26093 | 0.46234 | 113.4476 | -9.8419 | -0.35706 | 0.16937 | -0.086976 | 0.14191 | -85.3775 | -0.28381 | 0.32501 | 0.27008 | 9.819 | 10.0204 | 37.3032 | 122.85 | -0.086976 | 123.0057 | 9.5581 | -0.28381 | 122.85 | -0.086976 | 9.5581 | 37.3032 | 123.0057 | -123.0377 | -122.9645
1325.375 | 122.7676 | -12.4603 | 110.1196 | -0.0031279 | 0.017306 | 0.0069535 | -0.010927 | 0.058832 | 0.036508 | 0.14184 | -12.5977 | 110.3622 | -12.8265 | -12.3413 | 34.4833 | 0.10071 | 0.13275 | 0.21515 | 110.4309 | -12.7579 | -0.36621 | 0.24262 | -0.13733 | 0.11902 | -75.6363 | -0.29755 | 0.31128 | 0.22888 | 12.5931 | 12.6755 | 46.9437 | 122.8226 | -0.13733 | 122.8912 | 12.561 | -0.29755 | 122.8226 | -0.13733 | 12.561 | 46.9437 | 122.8912 | -122.9462 | -122.8775
1327.125 | 122.7722 | -12.2269 | 110.4034 | 0.012131 | 0.019442 | 0.0065263 | -0.0085769 | 0.058191 | 0.037576 | 0.1444 | -12.3047 | 110.614 | -12.561 | -12.0529 | 33.0002 | 0.082397 | 0.19226 | -0.18768 | 110.6873 | -12.5244 | -0.33417 | 0.21057 | -0.077819 | 0.17395 | -77.4033 | -0.29755 | 0.28381 | 0.25635 | 12.4191 | 12.0392 | 45.2271 | 122.8409 | -0.077819 | 122.9141 | 12.3093 | -0.29755 | 122.8409 | -0.077819 | 12.3093 | 45.2271 | 122.9141 | -122.9645 | -122.9279
1328.7969 | 122.6395 | -12.1811 | 110.5179 | 0.0045011 | 0.016451 | 0.0086625 | -0.0060135 | 0.063318 | 0.037363 | 0.1444 | -12.1811 | 110.6461 | -12.4741 | -11.9385 | 32.4463 | 0.14191 | 0.018311 | -0.2243 | 110.7697 | -12.3779 | -0.29297 | 0.12817 | 0 | 0.24261 | -78.0716 | -0.19684 | 0.25177 | 0.29297 | 12.1994 | 11.9568 | 44.6274 | 122.8271 | 0 | 122.9507 | 12.323 | -0.19684 | 122.8271 | 0 | 12.323 | 44.6274 | 122.9507 | -122.9919 | -122.8958
1330.5469 | 122.7814 | -11.9385 | 110.6461 | -0.0031279 | 0.019015 | 0.0031083 | -0.011354 | 0.059259 | 0.039712 | 0.1444 | -12.0621 | 110.907 | -12.2955 | -11.7966 | 31.9016 | 0.086975 | 0.10071 | 0.32959 | 110.9711 | -12.2269 | -0.35705 | 0.26093 | -0.1236 | 0.14191 | -78.7445 | -0.28839 | 0.32501 | 0.23346 | 12.0392 | 12.2681 | 43.84 | 122.8455 | -0.1236 | 122.9095 | 12.0255 | -0.28839 | 122.8455 | -0.1236 | 12.0255 | 43.84 | 122.9095 | -122.9416 | -122.8729
1332.2344 | 122.7722 | -12.5656 | 110.0693 | 0.012131 | 0.018374 | 0.0082351 | -0.0040909 | 0.061182 | 0.035867 | 0.1459 | -12.6984 | 110.2661 | -12.9364 | -12.4466 | 32.3456 | 0.032043 | 0.23804 | 0.27466 | 110.4218 | -12.8311 | -0.37079 | 0.19684 | -0.13275 | 0.11902 | -77.7237 | -0.2655 | 0.35248 | 0.23804 | 12.8037 | 12.8403 | 44.9112 | 122.8317 | -0.13275 | 122.9874 | 12.5977 | -0.2655 | 122.8317 | -0.13275 | 12.5977 | 44.9112 | 122.9874 | -123.0057 | -122.9004
1333.9844 | 122.7768 | -13.0783 | 109.52 | -0.0031279 | 0.020083 | 0.0086625 | -0.0098587 | 0.060541 | 0.039926 | 0.1444 | -13.1607 | 109.7946 | -13.385 | -12.9089 | 28.537 | 0.086975 | 0.054932 | 0.26093 | 109.8953 | -13.3255 | -0.3067 | 0.27466 | -0.082398 | 0.16937 | -80.983 | -0.24719 | 0.37537 | 0.2243 | 13.1332 | 13.3392 | 41.6153 | 122.8729 | -0.082398 | 122.9736 | 13.1653 | -0.24719 | 122.8729 | -0.082398 | 13.1653 | 41.6153 | 122.9736 | -122.905 | -122.8455
1335.7188 | 122.7264 | -12.7075 | 109.9548 | -0.0031279 | 0.018374 | 0.0058853 | -0.0070815 | 0.058832 | 0.039712 | 0.1459 | -12.7441 | 110.1288 | -13.0188 | -12.5061 | 29.5624 | 0.14648 | 0.050354 | 0.36163 | 110.1929 | -12.9684 | -0.31128 | 0.17395 | -0.036621 | 0.20142 | -80.3925 | -0.26092 | 0.23804 | 0.27466 | 12.7579 | 13.0692 | 42.2699 | 122.8363 | -0.036621 | 122.9004 | 12.854 | -0.26092 | 122.8363 | -0.036621 | 12.854 | 42.2699 | 122.9004 | -122.9736 | -122.9233
1337.4688 | 122.7951 | -12.4603 | 110.1471 | 0.012131 | 0.015597 | 0.0046037 | -0.0066543 | 0.059045 | 0.036295 | 0.1459 | -12.6343 | 110.3485 | -12.8815 | -12.3734 | 31.6132 | 0.018311 | 0.23804 | 0.20142 | 110.4538 | -12.7853 | -0.42114 | 0.20142 | -0.17395 | 0.086975 | -78.5339 | -0.32501 | 0.3067 | 0.24719 | 12.6984 | 12.6617 | 44.0735 | 122.8088 | -0.17395 | 122.9141 | 12.4786 | -0.32501 | 122.8088 | -0.17395 | 12.4786 | 44.0735 | 122.9141 | -123.0286 | -122.9324
1339.1562 | 122.699 | -12.3642 | 110.3302 | 0.0045011 | 0.016451 | 0.0086625 | -0.0032363 | 0.061182 | 0.03544 | 0.14312 | -12.5107 | 110.4858 | -12.7533 | -12.2818 | 31.5811 | -0.018311 | 0.21515 | -0.41199 | 110.5865 | -12.6389 | -0.3891 | 0.15564 | -0.14648 | 0.082398 | -78.7491 | -0.27466 | 0.25635 | 0.24262 | 12.5793 | 11.9522 | 43.9453 | 122.85 | -0.14648 | 122.9507 | 12.3459 | -0.27466 | 122.85 | -0.14648 | 12.3459 | 43.9453 | 122.9507 | -123.0835 | -122.9691
1340.8906 | 122.6898 | -12.4786 | 110.2249 | 0.012131 | 0.016451 | 0.0086625 | -0.0043045 | 0.061823 | 0.036935 | 0.1444 | -12.5931 | 110.4034 | -12.8357 | -12.3917 | 31.4896 | 0 | 0.20599 | 0.28381 | 110.4767 | -12.7579 | -0.35705 | 0.17853 | -0.11444 | 0.086975 | -78.7354 | -0.27924 | 0.25177 | 0.24261 | 12.6846 | 12.7625 | 43.9682 | 122.8821 | -0.11444 | 122.9553 | 12.4786 | -0.27924 | 122.8821 | -0.11444 | 12.4786 | 43.9682 | 122.9553 | -123.0606 | -122.9828
1342.625 | 122.7127 | -12.9547 | 109.7076 | 0.01976 | 0.017733 | 0.0056717 | -0.0053727 | 0.063532 | 0.038004 | 0.14846 | -13.0875 | 109.9411 | -13.3026 | -12.8906 | 24.4446 | -0.009155 | 0.16479 | 0.17853 | 110.0372 | -13.1927 | -0.3479 | 0.23346 | -0.13275 | 0.064087 | -85.2631 | -0.23804 | 0.32959 | 0.21515 | 13.1195 | 13.1332 | 37.3993 | 122.8958 | -0.13275 | 122.9919 | 12.9456 | -0.23804 | 122.8958 | -0.13275 | 12.9456 | 37.3993 | 122.9919 | -123.0103 | -122.9004
1344.3125 | 122.699 | -12.8311 | 109.8679 | 0.0045011 | 0.016451 | 0.0093033 | -0.0034499 | 0.062036 | 0.038858 | 0.14825 | -12.9044 | 110.083 | -13.1607 | -12.7029 | 23.2956 | 0.013733 | 0.16022 | 0.2243 | 110.1974 | -13.0508 | -0.32959 | 0.21515 | -0.073242 | 0.12817 | -86.5723 | -0.21973 | 0.32959 | 0.25635 | 12.9913 | 13.0554 | 36.1267 | 122.9141 | -0.073242 | 123.0286 | 12.8448 | -0.21973 | 122.9141 | -0.073242 | 12.8448 | 36.1267 | 123.0286 | -123.0286 | -122.9187
1346.0625 | 122.7356 | -12.6251 | 109.9915 | -0.0031279 | 0.017306 | 0.0054581 | -0.012636 | 0.060754 | 0.042917 | 0.15103 | -12.5565 | 110.3439 | -12.8311 | -12.2864 | 23.0301 | 0.16022 | 0.004578 | 0.33875 | 110.4538 | -12.735 | -0.20599 | 0.35248 | 0.068664 | 0.33874 | -86.9614 | -0.10986 | 0.46234 | 0.27466 | 12.6297 | 12.9639 | 35.6552 | 122.9691 | 0.068664 | 123.0789 | 12.7853 | -0.10986 | 122.9691 | 0.068664 | 12.7853 | 35.6552 | 123.0789 | -122.8226 | -122.7264
1347.8125 | 122.7859 | -12.6389 | 109.9915 | 0.0045011 | 0.01282 | 0.0056717 | -0.0087905 | 0.060541 | 0.042917 | 0.14932 | -12.6663 | 110.3119 | -12.8998 | -12.4283 | 21.6339 | 0.022888 | 0.17853 | 0.21973 | 110.463 | -12.8265 | -0.26093 | 0.32044 | -0.027466 | 0.21057 | -88.3575 | -0.18768 | 0.4715 | 0.23346 | 12.8174 | 12.8586 | 34.2728 | 122.9507 | -0.027466 | 123.1018 | 12.6617 | -0.18768 | 122.9507 | -0.027466 | 12.6617 | 34.2728 | 123.1018 | -122.8912 | -122.818
1349.5156 | 122.6852 | -12.5107 | 110.2112 | 0.012131 | 0.018801 | 0.0082351 | -0.0013137 | 0.060754 | 0.039285 | 0.14974 | -12.5793 | 110.3851 | -12.8311 | -12.3596 | 22.5677 | 0.009155 | 0.1236 | 0.19684 | 110.5041 | -12.7533 | -0.32043 | 0.17395 | -0.068665 | 0.15106 | -87.6434 | -0.24262 | 0.29297 | 0.25177 | 12.6343 | 12.7075 | 35.0784 | 122.8958 | -0.068665 | 123.0148 | 12.5198 | -0.24262 | 122.8958 | -0.068665 | 12.5198 | 35.0784 | 123.0148 | -123.0423 | -122.9645
1351.2656 | 122.7676 | -12.2864 | 110.3302 | 0.0045011 | 0.017306 | 0.0058853 | -0.011354 | 0.058618 | 0.045267 | 0.14932 | -12.3734 | 110.5728 | -12.5839 | -12.149 | 21.524 | 0.091553 | 0.036621 | 0.29755 | 110.6644 | -12.529 | -0.29755 | 0.24262 | -0.086975 | 0.13733 | -88.8062 | -0.24262 | 0.33417 | 0.21057 | 12.323 | 12.5839 | 33.8104 | 122.8592 | -0.086975 | 122.9507 | 12.3779 | -0.24262 | 122.8592 | -0.086975 | 12.3779 | 33.8104 | 122.9507 | -122.9141 | -122.8592
1352.9375 | 122.6624 | -12.1445 | 110.582 | 0.0045011 | 0.020937 | 0.0084489 | -0.0028091 | 0.06225 | 0.044199 | 0.15038 | -12.1445 | 110.8017 | -12.4374 | -11.8881 | 21.2585 | 0.059509 | 0.13733 | 0.27466 | 110.8932 | -12.323 | -0.29297 | 0.21973 | 0 | 0.25635 | -89.3234 | -0.17853 | 0.31128 | 0.29297 | 12.2818 | 12.4191 | 33.403 | 122.9462 | 0 | 123.0377 | 12.204 | -0.17853 | 122.9462 | 0 | 12.204 | 33.403 | 123.0377 | -123.0194 | -122.905
1354.7031 | 122.6715 | -12.0163 | 110.733 | 0.0045011 | 0.017733 | 0.010371 | -0.0049453 | 0.060114 | 0.042276 | 0.14953 | -12.0666 | 110.8795 | -12.3276 | -11.8149 | 20.842 | 0.045776 | 0.10071 | -0.49896 | 110.9848 | -12.2406 | -0.31128 | 0.14649 | -0.050354 | 0.20142 | -89.8911 | -0.2243 | 0.25177 | 0.26093 | 12.117 | 11.5173 | 32.8583 | 122.8958 | -0.050354 | 123.0011 | 12.0621 | -0.2243 | 122.8958 | -0.050354 | 12.0621 | 32.8583 | 123.0011 | -123.0606 | -122.9736
1356.375 | 122.6578 | -11.7188 | 110.9802 | 0.012131 | 0.018587 | 0.0048173 | -0.0066543 | 0.063104 | 0.046121 | 0.15316 | -11.8057 | 111.0992 | -12.0895 | -11.5723 | 20.5353 | 0.12817 | -0.041199 | -0.28381 | 111.1725 | -11.9843 | -0.37079 | 0.11902 | -0.086975 | 0.14648 | -90.4449 | -0.2655 | 0.19226 | 0.28381 | 11.6776 | 11.4349 | 32.254 | 122.818 | -0.086975 | 122.8912 | 11.8469 | -0.2655 | 122.818 | -0.086975 | 11.8469 | 32.254 | 122.8912 | -123.0698 | -122.9645
1358.125 | 122.7722 | -11.6272 | 111.026 | 0.0045011 | 0.016024 | 0.0035355 | -0.0057999 | 0.058618 | 0.044412 | 0.15359 | -11.8057 | 111.2183 | -12.03 | -11.5677 | 18.956 | -0.004578 | 0.15106 | -0.59509 | 111.319 | -11.9522 | -0.40283 | 0.19226 | -0.17853 | 0.059509 | -92.07 | -0.32501 | 0.29297 | 0.2243 | 11.7783 | 11.0321 | 30.5832 | 122.8455 | -0.17853 | 122.9462 | 11.6226 | -0.32501 | 122.8455 | -0.17853 | 11.6226 | 30.5832 | 122.9462 | -123.056 | -122.9782
1359.8125 | 122.7997 | -11.6455 | 110.9848 | -0.010757 | 0.015383 | 0.0046037 | -0.0105 | 0.057977 | 0.048257 | 0.15252 | -11.7096 | 111.2549 | -11.9385 | -11.467 | 18.1641 | 0.086975 | -0.013733 | -0.013733 | 111.2961 | -11.8561 | -0.29297 | 0.27008 | -0.064087 | 0.17853 | -92.8207 | -0.21057 | 0.31128 | 0.22888 | 11.6318 | 11.6318 | 29.8096 | 122.9004 | -0.064087 | 122.9416 | 11.7325 | -0.21057 | 122.9004 | -0.064087 | 11.7325 | 29.8096 | 122.9416 | -122.9233 | -122.8409
1361.5625 | 122.7173 | -11.6501 | 111.0443 | 0.012131 | 0.01816 | 0.0067399 | -0.0015273 | 0.061823 | 0.04548 | 0.15338 | -11.7828 | 111.2503 | -12.0071 | -11.554 | 17.4271 | -0.018311 | 0.11902 | -0.44403 | 111.3327 | -11.8973 | -0.35706 | 0.20599 | -0.13275 | 0.09613 | -93.6172 | -0.24719 | 0.28839 | 0.2243 | 11.7691 | 11.2061 | 29.0771 | 122.9004 | -0.13275 | 122.9828 | 11.6318 | -0.24719 | 122.9004 | -0.13275 | 11.6318 | 29.0771 | 122.9828 | -123.0515 | -122.9416
1363.2344 | 122.6715 | -11.5723 | 111.1038 | -0.010757 | 0.019442 | 0.0052445 | -0.0047317 | 0.061823 | 0.048685 | 0.1538 | -11.7188 | 111.319 | -11.9431 | -11.4899 | 16.9327 | 0.027466 | 0.045776 | -0.51727 | 111.3739 | -11.8561 | -0.37079 | 0.21515 | -0.14648 | 0.082398 | -94.1711 | -0.28381 | 0.27008 | 0.2243 | 11.618 | 11.055 | 28.5049 | 122.8912 | -0.14648 | 122.9462 | 11.5997 | -0.28381 | 122.8912 | -0.14648 | 11.5997 | 28.5049 | 122.9462 | -123.0469 | -122.9599
1365 | 122.7905 | -11.5723 | 111.0718 | 0.0045011 | 0.020296 | 0.0028947 | -0.0057999 | 0.059259 | 0.045908 | 0.15273 | -11.7188 | 111.2961 | -11.9659 | -11.4716 | 16.0812 | 0.009155 | 0.16022 | -0.27924 | 111.3739 | -11.879 | -0.39368 | 0.22431 | -0.14648 | 0.10071 | -94.9905 | -0.3067 | 0.30212 | 0.24719 | 11.7325 | 11.293 | 27.6535 | 122.8683 | -0.14648 | 122.9462 | 11.5814 | -0.3067 | 122.8683 | -0.14648 | 11.5814 | 27.6535 | 122.9462 | -123.0377 | -122.9507
1366.6875 | 122.7905 | -11.5128 | 111.1313 | 0.0045011 | 0.019228 | 0.0073807 | -0.0068679 | 0.060327 | 0.047617 | 0.15487 | -11.6272 | 111.4517 | -11.8469 | -11.293 | 15.596 | -0.004578 | 0.17395 | -0.51727 | 111.5707 | -11.7096 | -0.33417 | 0.32043 | -0.11444 | 0.21973 | -95.5353 | -0.19684 | 0.43945 | 0.21973 | 11.6867 | 10.9955 | 27.1088 | 122.9645 | -0.11444 | 123.0835 | 11.5082 | -0.19684 | 122.9645 | -0.11444 | 11.5082 | 27.1088 | 123.0835 | -122.9782 | -122.8409
1368.4375 | 122.7814 | -11.4944 | 111.145 | 0.012131 | 0.021578 | 0.0088761 | -0.0045181 | 0.058832 | 0.048471 | 0.15466 | -11.6409 | 111.4059 | -11.879 | -11.4029 | 15.2664 | 0.022888 | 0.13275 | -0.51727 | 111.438 | -11.8057 | -0.38452 | 0.26093 | -0.14648 | 0.091553 | -95.8786 | -0.31128 | 0.29297 | 0.23804 | 11.6272 | 10.9772 | 26.7609 | 122.9004 | -0.14648 | 122.9324 | 11.5173 | -0.31128 | 122.9004 | -0.14648 | 11.5173 | 26.7609 | 122.9324 | -123.024 | -122.9507
1370.125 | 122.6486 | -11.4487 | 111.2549 | 0.0045011 | 0.017519 | 0.0060989 | -0.0053727 | 0.061395 | 0.049539 | 0.15466 | -11.5036 | 111.3968 | -11.8149 | -11.2793 | 14.9918 | 0.12817 | -0.091553 | -0.4303 | 111.4517 | -11.7371 | -0.36621 | 0.14191 | -0.054932 | 0.16937 | -96.2631 | -0.28839 | 0.19684 | 0.31128 | 11.3571 | 11.0184 | 26.4404 | 122.8455 | -0.054932 | 122.9004 | 11.5768 | -0.28839 | 122.8455 | -0.054932 | 11.5768 | 26.4404 | 122.9004 | -123.0698 | -122.9919
1371.875 | 122.7219 | -11.7004 | 110.9619 | 0.012131 | 0.016238 | 0.010585 | -0.0036637 | 0.060541 | 0.04548 | 0.15423 | -11.8378 | 111.1313 | -12.0941 | -11.5906 | 14.6713 | 0.045776 | 0.073242 | -0.60883 | 111.2091 | -12.0163 | -0.39368 | 0.16937 | -0.13733 | 0.10986 | -96.2906 | -0.31586 | 0.24719 | 0.25635 | 11.7737 | 11.0916 | 26.3718 | 122.8317 | -0.13733 | 122.9095 | 11.7462 | -0.31586 | 122.8317 | -0.13733 | 11.7462 | 26.3718 | 122.9095 | -123.056 | -122.9782
1373.5469 | 122.7264 | -11.6043 | 111.0397 | -0.0031279 | 0.01816 | 0.0054581 | -0.012422 | 0.060541 | 0.045908 | 0.15423 | -11.6455 | 111.2732 | -11.9293 | -11.3892 | 14.6301 | 0.14648 | -0.032043 | -0.5127 | 111.3098 | -11.8698 | -0.32501 | 0.23346 | -0.041199 | 0.21515 | -96.4096 | -0.2655 | 0.27008 | 0.28381 | 11.5723 | 11.0916 | 26.2344 | 122.8775 | -0.041199 | 122.9141 | 11.7508 | -0.2655 | 122.8775 | -0.041199 | 11.7508 | 26.2344 | 122.9141 | -122.9691 | -122.9095
1375.2812 | 122.8043 | -11.5219 | 111.1313 | -0.0031279 | 0.019015 | 0.0052445 | -0.0079361 | 0.0599 | 0.048257 | 0.15551 | -11.6547 | 111.3235 | -11.9019 | -11.4304 | 14.3372 | 0.036621 | 0.11444 | -0.6546 | 111.3876 | -11.8378 | -0.37994 | 0.19226 | -0.13275 | 0.091553 | -96.7941 | -0.31586 | 0.25635 | 0.24719 | 11.6364 | 10.8673 | 25.8591 | 122.8455 | -0.13275 | 122.9095 | 11.5585 | -0.31586 | 122.8455 | -0.13275 | 11.5585 | 25.8591 | 122.9095 | -123.0331 | -122.9691
1377.0469 | 122.6715 | -11.5631 | 111.1313 | 0.0045011 | 0.017092 | 0.0086625 | -0.0049453 | 0.060754 | 0.045053 | 0.15316 | -11.6135 | 111.3739 | -11.879 | -11.3434 | 14.2456 | 0.045776 | 0.07782 | -0.56305 | 111.4792 | -11.7554 | -0.31586 | 0.24261 | -0.050354 | 0.21973 | -96.8857 | -0.19226 | 0.3479 | 0.2655 | 11.6409 | 11.0001 | 25.8087 | 122.937 | -0.050354 | 123.0423 | 11.6089 | -0.19226 | 122.937 | -0.050354 | 11.6089 | 25.8087 | 123.0423 | -123.0103 | -122.8867
1378.7969 | 122.7356 | -11.467 | 111.1954 | 0.01976 | 0.017092 | 0.0063125 | -0.0094315 | 0.059473 | 0.047617 | 0.15295 | -11.4441 | 111.4288 | -11.7462 | -11.2335 | 14.1861 | 0.14191 | -0.018311 | -0.51727 | 111.4334 | -11.7233 | -0.27924 | 0.23346 | 0.022888 | 0.23346 | -97.0093 | -0.25635 | 0.23804 | 0.30212 | 11.4487 | 10.9497 | 25.6531 | 122.8958 | 0.022888 | 122.9004 | 11.6089 | -0.25635 | 122.8958 | 0.022888 | 11.6089 | 25.6531 | 122.9004 | -122.9416 | -122.9187
1380.4844 | 122.699 | -11.5036 | 111.2091 | 0.0045011 | 0.016878 | 0.0093033 | -0.0032363 | 0.061823 | 0.046976 | 0.1553 | -11.6043 | 111.4243 | -11.8286 | -11.3571 | 13.9481 | -0.009155 | 0.059509 | -0.79193 | 111.5341 | -11.7233 | -0.32501 | 0.21515 | -0.10071 | 0.14648 | -97.261 | -0.21973 | 0.32501 | 0.2243 | 11.5631 | 10.7117 | 25.4517 | 122.9279 | -0.10071 | 123.0377 | 11.4944 | -0.21973 | 122.9279 | -0.10071 | 11.4944 | 25.4517 | 123.0377 | -123.0377 | -122.9324
1382.2344 | 122.7448 | -11.7554 | 110.8841 | -0.010757 | 0.015169 | 0.0080215 | -0.011354 | 0.059045 | 0.049753 | 0.15508 | -11.7416 | 111.1633 | -12.0209 | -11.4716 | 13.916 | 0.15564 | -0.082397 | -0.52185 | 111.2274 | -11.9431 | -0.2655 | 0.27924 | 0.013733 | 0.28381 | -96.9681 | -0.18768 | 0.34332 | 0.27924 | 11.673 | 11.2335 | 25.6714 | 122.9187 | 0.013733 | 122.9828 | 11.911 | -0.18768 | 122.9187 | 0.013733 | 11.911 | 25.6714 | 122.9828 | -122.905 | -122.8271
1383.9844 | 122.7722 | -11.586 | 111.0535 | 0.0045011 | 0.017519 | 0.0035355 | -0.0092179 | 0.060114 | 0.047403 | 0.15423 | -11.6135 | 111.264 | -11.9339 | -11.348 | 13.9069 | 0.10529 | 0.027466 | -0.63629 | 111.3922 | -11.824 | -0.3479 | 0.21057 | -0.027465 | 0.23804 | -97.1466 | -0.23804 | 0.33875 | 0.32043 | 11.6135 | 10.9497 | 25.4929 | 122.85 | -0.027465 | 122.9782 | 11.6913 | -0.23804 | 122.85 | -0.027465 | 11.6913 | 25.4929 | 122.9782 | -122.9874 | -122.8775
1385.7188 | 122.699 | -11.7096 | 110.9619 | -0.0031279 | 0.017092 | 0.0058853 | -0.0021683 | 0.062891 | 0.045694 | 0.15679 | -11.9064 | 111.1221 | -12.1216 | -11.6364 | 13.6642 | -0.018311 | 0.041199 | -0.6546 | 111.2457 | -12.0255 | -0.41199 | 0.16022 | -0.19684 | 0.073242 | -97.2977 | -0.31586 | 0.28381 | 0.21515 | 11.7508 | 11.055 | 25.3738 | 122.8317 | -0.19684 | 122.9553 | 11.6913 | -0.31586 | 122.8317 | -0.19684 | 11.6913 | 25.3738 | 122.9553 | -123.0835 | -122.9874
1387.4062 | 122.7905 | -11.4761 | 111.1404 | 0.012131 | 0.017306 | 0.0065263 | -0.0081497 | 0.062463 | 0.049326 | 0.15466 | -11.6867 | 111.3327 | -11.9431 | -11.4441 | 13.6139 | 0.009155 | 0.10071 | -0.24719 | 111.3968 | -11.8607 | -0.46692 | 0.19226 | -0.21057 | 0.032043 | -97.5265 | -0.38452 | 0.25635 | 0.25635 | 11.5768 | 11.2289 | 25.09 | 122.8088 | -0.21057 | 122.8729 | 11.4853 | -0.38452 | 122.8088 | -0.21057 | 11.4853 | 25.09 | 122.8729 | -123.0835 | -123.0011
1389.1719 | 122.6578 | -11.6547 | 111.0764 | 0.012131 | 0.01581 | 0.010371 | -0.010072 | 0.058618 | 0.051035 | 0.15551 | -11.7233 | 111.2045 | -11.9797 | -11.4853 | 13.6002 | 0.12817 | -0.091553 | -0.29755 | 111.3144 | -11.8744 | -0.32501 | 0.12817 | -0.068665 | 0.16937 | -97.4762 | -0.21973 | 0.23804 | 0.25635 | 11.5631 | 11.3571 | 25.2548 | 122.8592 | -0.068665 | 122.9691 | 11.7828 | -0.21973 | 122.8592 | -0.068665 | 11.7828 | 25.2548 | 122.9691 | -123.056 | -122.9507
1390.8594 | 122.7264 | -11.3525 | 111.2915 | 0.012131 | 0.016451 | 0.0058853 | -0.0081497 | 0.059686 | 0.050607 | 0.15701 | -11.5082 | 111.3968 | -11.8103 | -11.2473 | 13.6002 | 0.15564 | -0.09613 | -0.52643 | 111.4426 | -11.7325 | -0.45776 | 0.10529 | -0.15564 | 0.10529 | -97.6913 | -0.37994 | 0.15106 | 0.30212 | 11.2564 | 10.8261 | 24.9527 | 122.7493 | -0.15564 | 122.7951 | 11.5082 | -0.37994 | 122.7493 | -0.15564 | 11.5082 | 24.9527 | 122.7951 | -123.1018 | -123.024
1392.5938 | 122.7264 | -11.5585 | 111.0901 | -0.0031279 | 0.017306 | 0.0046037 | -0.0070815 | 0.059045 | 0.049112 | 0.15743 | -11.5265 | 111.3602 | -11.824 | -11.3205 | 13.4903 | 0.13733 | -0.073242 | -0.45319 | 111.3464 | -11.8011 | -0.2655 | 0.27008 | 0.032044 | 0.23804 | -97.5998 | -0.24261 | 0.25635 | 0.29755 | 11.4853 | 11.1053 | 25.0488 | 122.9187 | 0.032044 | 122.905 | 11.6959 | -0.24261 | 122.9187 | 0.032044 | 11.6959 | 25.0488 | 122.905 | -122.9141 | -122.8912
1394.3438 | 122.7951 | -11.4304 | 111.1954 | -0.0031279 | 0.017092 | 0.0060989 | -0.0083633 | 0.056482 | 0.049966 | 0.15594 | -11.5448 | 111.3785 | -11.8011 | -11.3159 | 13.3484 | 0.082397 | -0.050354 | -0.55847 | 111.4883 | -11.7279 | -0.37079 | 0.1831 | -0.11444 | 0.11444 | -97.847 | -0.29755 | 0.29297 | 0.25635 | 11.38 | 10.8719 | 24.7787 | 122.8088 | -0.11444 | 122.9187 | 11.5128 | -0.29755 | 122.8088 | -0.11444 | 11.5128 | 24.7787 | 122.9187 | -122.9965 | -122.9233
1396.0938 | 122.7905 | -11.4349 | 111.1954 | 0.0045011 | 0.017519 | 0.0063125 | -0.0053727 | 0.059686 | 0.046976 | 0.15466 | -11.4487 | 111.5616 | -11.7096 | -11.2381 | 13.2339 | -0.004578 | 0.10986 | -0.63171 | 111.6074 | -11.6409 | -0.27466 | 0.36621 | -0.013732 | 0.19684 | -97.9614 | -0.20599 | 0.41199 | 0.26093 | 11.5448 | 10.8032 | 24.6689 | 122.9965 | -0.013732 | 123.0423 | 11.4304 | -0.20599 | 122.9965 | -0.013732 | 11.4304 | 24.6689 | 123.0423 | -122.905 | -122.8363
1397.7812 | 122.7127 | -11.4532 | 111.232 | -0.0031279 | 0.016451 | 0.0082351 | -0.0028091 | 0.060754 | 0.048898 | 0.15423 | -11.4624 | 111.5982 | -11.673 | -11.2289 | 13.1516 | 0.004578 | 0.022888 | -0.74158 | 111.6348 | -11.6364 | -0.21973 | 0.36621 | -0.009155 | 0.2243 | -98.0804 | -0.18311 | 0.40283 | 0.21057 | 11.4761 | 10.7117 | 24.6048 | 123.0515 | -0.009155 | 123.0881 | 11.4578 | -0.18311 | 123.0515 | -0.009155 | 11.4578 | 24.6048 | 123.0881 | -122.905 | -122.8683
1399.5469 | 122.6852 | -11.4532 | 111.2228 | 0.012131 | 0.016451 | 0.0069535 | -0.0043045 | 0.061182 | 0.046335 | 0.15786 | -11.554 | 111.4197 | -11.8469 | -11.2381 | 13.1424 | 0.045776 | -0.013733 | -0.84228 | 111.5158 | -11.6913 | -0.39368 | 0.19684 | -0.10071 | 0.21515 | -98.0804 | -0.23804 | 0.29297 | 0.29297 | 11.4395 | 10.611 | 24.5956 | 122.8729 | -0.10071 | 122.9691 | 11.499 | -0.23804 | 122.8729 | -0.10071 | 11.499 | 24.5956 | 122.9691 | -123.0698 | -122.9141
1401.2969 | 122.7859 | -11.3159 | 111.3007 | -0.0031279 | 0.017733 | 0.0067399 | -0.010713 | 0.0599 | 0.048257 | 0.15743 | -11.3663 | 111.5753 | -11.5997 | -11.1649 | 13.2019 | 0.082397 | -0.059509 | -0.68665 | 111.644 | -11.5814 | -0.28381 | 0.27466 | -0.050354 | 0.15106 | -98.0988 | -0.2655 | 0.34332 | 0.23346 | 11.2564 | 10.6293 | 24.5178 | 122.8912 | -0.050354 | 122.9599 | 11.3983 | -0.2655 | 122.8912 | -0.050354 | 11.3983 | 24.5178 | 122.9599 | -122.9004 | -122.8821
1402.9688 | 122.7264 | -11.348 | 111.3281 | -0.0031279 | 0.018374 | 0.010799 | -0.0045181 | 0.060754 | 0.048685 | 0.15936 | -11.4853 | 111.525 | -11.7279 | -11.2198 | 13.0234 | -0.013733 | 0.009155 | -0.85144 | 111.6943 | -11.5952 | -0.37994 | 0.19684 | -0.13733 | 0.12817 | -98.3047 | -0.24719 | 0.36621 | 0.24261 | 11.3571 | 10.4965 | 24.3713 | 122.8729 | -0.13733 | 123.0423 | 11.3342 | -0.24719 | 122.8729 | -0.13733 | 11.3342 | 24.3713 | 123.0423 | -123.056 | -122.9233
1404.7188 | 122.7905 | -11.4304 | 111.2045 | 0.0045011 | 0.015383 | 0.0082351 | -0.011354 | 0.0599 | 0.048044 | 0.15829 | -11.5082 | 111.438 | -11.7691 | -11.2564 | 13.0692 | 0.11444 | -0.11902 | -0.67291 | 111.5158 | -11.7096 | -0.33875 | 0.23346 | -0.07782 | 0.17395 | -98.1354 | -0.27924 | 0.31128 | 0.26093 | 11.3113 | 10.7574 | 24.4995 | 122.8683 | -0.07782 | 122.9462 | 11.5448 | -0.27924 | 122.8683 | -0.07782 | 11.5448 | 24.4995 | 122.9462 | -122.9736 | -122.9141
1406.4688 | 122.6944 | -11.348 | 111.3419 | 0.0045011 | 0.013674 | 0.011012 | -0.0094315 | 0.057764 | 0.049326 | 0.15936 | -11.3846 | 111.5158 | -11.6501 | -11.1557 | 13.0096 | 0.11902 | -0.16937 | -0.50812 | 111.5982 | -11.5814 | -0.30212 | 0.17395 | -0.036622 | 0.19226 | -98.3322 | -0.23346 | 0.25635 | 0.2655 | 11.1786 | 10.8398 | 24.3576 | 122.8638 | -0.036622 | 122.9462 | 11.467 | -0.23346 | 122.8638 | -0.036622 | 11.467 | 24.3576 | 122.9462 | -122.9919 | -122.9233
1408.2188 | 122.7356 | -11.2839 | 111.4197 | 0.012131 | 0.01816 | 0.0084489 | -0.0083633 | 0.056482 | 0.049966 | 0.15807 | -11.2518 | 111.6898 | -11.5173 | -11.0138 | 12.9227 | 0.10071 | -0.11444 | -0.5722 | 111.7538 | -11.4578 | -0.23346 | 0.27008 | 0.032044 | 0.27008 | -98.497 | -0.17395 | 0.33417 | 0.2655 | 11.1694 | 10.7117 | 24.2065 | 122.9736 | 0.032044 | 123.0377 | 11.3846 | -0.17395 | 122.9736 | 0.032044 | 11.3846 | 24.2065 | 123.0377 | -122.937 | -122.8775
1409.9844 | 122.6486 | -11.348 | 111.3739 | 0.0045011 | 0.017092 | 0.014003 | -0.0025955 | 0.060541 | 0.048685 | 0.15807 | -11.4029 | 111.525 | -11.6638 | -11.1237 | 12.8265 | 0.13275 | -0.20142 | -0.64545 | 111.5616 | -11.6135 | -0.31586 | 0.15106 | -0.054932 | 0.2243 | -98.5474 | -0.2655 | 0.18768 | 0.26092 | 11.1465 | 10.7025 | 24.1745 | 122.8729 | -0.054932 | 122.9095 | 11.4807 | -0.2655 | 122.8729 | -0.054932 | 11.4807 | 24.1745 | 122.9095 | -123.0377 | -122.9874
1411.7344 | 122.6761 | -11.4487 | 111.3007 | -0.0031279 | 0.017519 | 0.0069535 | -0.0028091 | 0.057977 | 0.047403 | 0.15872 | -11.412 | 111.5707 | -11.6913 | -11.1557 | 12.7258 | 0.054932 | -0.004578 | -0.70953 | 111.6577 | -11.6089 | -0.24261 | 0.27008 | 0.036621 | 0.29297 | -98.5748 | -0.16022 | 0.35706 | 0.27924 | 11.4441 | 10.7391 | 24.1745 | 123.0194 | 0.036621 | 123.1064 | 11.5036 | -0.16022 | 123.0194 | 0.036621 | 11.5036 | 24.1745 | 123.1064 | -122.9919 | -122.9095
1413.4219 | 122.6578 | -11.2885 | 111.438 | -0.0031279 | 0.018587 | 0.0078079 | -0.0057999 | 0.061395 | 0.048257 | 0.15786 | -11.1832 | 111.7264 | -11.5082 | -10.936 | 12.7853 | 0.13275 | -0.18768 | -0.62256 | 111.7538 | -11.4487 | -0.21973 | 0.28839 | 0.10529 | 0.35248 | -98.6526 | -0.16022 | 0.31586 | 0.32501 | 11.1008 | 10.6659 | 24.0738 | 123.0148 | 0.10529 | 123.0423 | 11.4212 | -0.16022 | 123.0148 | 0.10529 | 11.4212 | 24.0738 | 123.0423 | -122.9462 | -122.8867
1415.1719 | 122.6898 | -11.3617 | 111.3876 | 0.012131 | 0.017306 | 0.0084489 | -0.0021683 | 0.062036 | 0.048257 | 0.15978 | -11.3297 | 111.6486 | -11.5906 | -11.1191 | 12.6068 | 0 | -0.013733 | -0.86975 | 111.731 | -11.5402 | -0.22888 | 0.26093 | 0.032043 | 0.24261 | -98.7808 | -0.17853 | 0.34332 | 0.26093 | 11.348 | 10.4919 | 23.9685 | 123.0103 | 0.032043 | 123.0927 | 11.3617 | -0.17853 | 123.0103 | 0.032043 | 11.3617 | 23.9685 | 123.0927 | -122.9782 | -122.9279
1416.8594 | 122.8134 | -11.2793 | 111.3464 | 0.012131 | 0.017947 | 0.0090897 | -0.0105 | 0.061609 | 0.050394 | 0.15786 | -11.3663 | 111.6119 | -11.586 | -11.1237 | 12.6343 | 0.082397 | -0.091553 | -0.93384 | 111.6165 | -11.5906 | -0.3067 | 0.2655 | -0.086975 | 0.15564 | -98.7122 | -0.31128 | 0.27008 | 0.21973 | 11.1877 | 10.3455 | 23.9136 | 122.8912 | -0.086975 | 122.8958 | 11.3617 | -0.31128 | 122.8912 | -0.086975 | 11.3617 | 23.9136 | 122.8958 | -122.9324 | -122.937
1418.6094 | 122.7585 | -11.2793 | 111.3968 | 0.0045011 | 0.017519 | 0.0075943 | -0.010286 | 0.059259 | 0.050821 | 0.15572 | -11.4304 | 111.4929 | -11.705 | -11.1557 | 12.6526 | 0.14191 | -0.12817 | -0.87891 | 111.5616 | -11.6409 | -0.42572 | 0.09613 | -0.15106 | 0.1236 | -98.7442 | -0.36163 | 0.16479 | 0.27466 | 11.1511 | 10.4004 | 23.9319 | 122.7722 | -0.15106 | 122.8409 | 11.4212 | -0.36163 | 122.7722 | -0.15106 | 11.4212 | 23.9319 | 122.8409 | -123.1018 | -123.0377
1420.2969 | 122.7631 | -11.5036 | 111.1725 | 0.012131 | 0.016878 | 0.0056717 | -0.0085769 | 0.059686 | 0.048898 | 0.15637 | -11.5311 | 111.3785 | -11.8195 | -11.2564 | 12.6022 | 0.15106 | -0.14191 | -0.88806 | 111.4334 | -11.7645 | -0.31586 | 0.20599 | -0.027466 | 0.24719 | -98.5703 | -0.26093 | 0.26093 | 0.28839 | 11.3617 | 10.6155 | 24.1058 | 122.8821 | -0.027466 | 122.937 | 11.6547 | -0.26093 | 122.8821 | -0.027466 | 11.6547 | 24.1058 | 122.937 | -122.9919 | -122.937
1422.0469 | 122.7127 | -11.3709 | 111.3281 | 0.0045011 | 0.019228 | 0.0080215 | -0.0021683 | 0.061609 | 0.044839 | 0.15765 | -11.5585 | 111.47 | -11.8011 | -11.261 | 12.4008 | -0.018311 | 0.018311 | -0.90179 | 111.644 | -11.6501 | -0.4303 | 0.14191 | -0.18768 | 0.10986 | -98.9273 | -0.27923 | 0.31586 | 0.24261 | 11.3892 | 10.4691 | 23.7717 | 122.8409 | -0.18768 | 123.0148 | 11.3525 | -0.27923 | 122.8409 | -0.18768 | 11.3525 | 23.7717 | 123.0148 | -123.1293 | -122.9782
1423.7344 | 122.7859 | -11.4075 | 111.2503 | -0.0031279 | 0.017306 | 0.0063125 | -0.0057999 | 0.058191 | 0.048257 | 0.15914 | -11.4624 | 111.4746 | -11.7325 | -11.2244 | 12.4283 | 0.064087 | 0 | -0.95673 | 111.5662 | -11.6867 | -0.32501 | 0.2243 | -0.054931 | 0.18311 | -98.822 | -0.27924 | 0.31586 | 0.27008 | 11.4075 | 10.4507 | 23.8358 | 122.8821 | -0.054931 | 122.9736 | 11.4716 | -0.27924 | 122.8821 | -0.054931 | 11.4716 | 23.8358 | 122.9736 | -122.9828 | -122.937
1425.4844 | 122.6715 | -11.3297 | 111.3556 | 0.012131 | 0.021365 | 0.0065263 | -0.0034499 | 0.062677 | 0.048257 | 0.15743 | -11.5356 | 111.4746 | -11.8195 | -11.2793 | 12.3734 | 0.050354 | -0.004578 | -1.0574 | 111.5433 | -11.7416 | -0.48981 | 0.11902 | -0.20599 | 0.050354 | -98.9822 | -0.41199 | 0.18768 | 0.28381 | 11.3251 | 10.2722 | 23.703 | 122.8043 | -0.20599 | 122.8729 | 11.38 | -0.41199 | 122.8043 | -0.20599 | 11.38 | 23.703 | 122.8729 | -123.175 | -123.0972
1427.1719 | 122.7173 | -11.261 | 111.4014 | 0.0045011 | 0.017519 | 0.0080215 | -0.0036637 | 0.060541 | 0.046335 | 0.15914 | -11.2976 | 111.7218 | -11.5356 | -11.0596 | 12.3093 | -0.018311 | 0.013733 | -1.474 | 111.85 | -11.4441 | -0.27466 | 0.32044 | -0.036621 | 0.20142 | -99.0921 | -0.18311 | 0.44861 | 0.23804 | 11.2747 | 9.787 | 23.5703 | 122.9828 | -0.036621 | 123.111 | 11.2427 | -0.18311 | 122.9828 | -0.036621 | 11.2427 | 23.5703 | 123.111 | -122.937 | -122.8455
1428.9062 | 122.7127 | -11.2061 | 111.5158 | -0.0031279 | 0.019228 | 0.0073807 | -0.0047317 | 0.0646 | 0.046548 | 0.15872 | -11.3754 | 111.676 | -11.6043 | -11.0687 | 12.2452 | -0.027466 | 0.013733 | -1.4511 | 111.8408 | -11.4532 | -0.39825 | 0.16022 | -0.16937 | 0.13733 | -99.2706 | -0.24719 | 0.32501 | 0.22888 | 11.2198 | 9.7549 | 23.4512 | 122.8821 | -0.16937 | 123.0469 | 11.1786 | -0.24719 | 122.8821 | -0.16937 | 11.1786 | 23.4512 | 123.0469 | -123.1201 | -122.9691
1430.6562 | 122.7997 | -11.087 | 111.5707 | 0.0045011 | 0.015169 | 0.0037491 | -0.013277 | 0.058832 | 0.052316 | 0.15701 | -11.261 | 111.7584 | -11.4624 | -10.968 | 12.2589 | 0.086975 | -0.10529 | -0.27466 | 111.7996 | -11.412 | -0.37537 | 0.18768 | -0.17395 | 0.11902 | -99.3118 | -0.32501 | 0.22888 | 0.20142 | 10.9817 | 10.8124 | 23.3459 | 122.8455 | -0.17395 | 122.8867 | 11.174 | -0.32501 | 122.8455 | -0.17395 | 11.174 | 23.3459 | 122.8867 | -123.0331 | -122.9828
1432.3438 | 122.6852 | -11.2061 | 111.5112 | 0.012131 | 0.01816 | 0.0086625 | -0.0053727 | 0.060968 | 0.05018 | 0.15936 | -11.2198 | 111.7676 | -11.5219 | -11.0825 | 12.1216 | 0.036621 | -0.09613 | -0.63171 | 111.7905 | -11.4624 | -0.31586 | 0.25635 | -0.013733 | 0.1236 | -99.3896 | -0.25635 | 0.27924 | 0.30212 | 11.1099 | 10.5743 | 23.3276 | 122.9736 | -0.013733 | 122.9965 | 11.2427 | -0.25635 | 122.9736 | -0.013733 | 11.2427 | 23.3276 | 122.9965 | -123.0331 | -122.9736
1434.0781 | 122.7493 | -11.3617 | 111.2915 | 0.012131 | 0.019015 | 0.0069535 | -0.010072 | 0.060114 | 0.048685 | 0.15978 | -11.2473 | 111.676 | -11.5448 | -11.0596 | 12.1582 | 0.13733 | -0.13733 | -0.48065 | 111.7172 | -11.5128 | -0.18311 | 0.38452 | 0.11444 | 0.30212 | -99.1333 | -0.15106 | 0.42572 | 0.29755 | 11.2244 | 10.881 | 23.5199 | 123.0377 | 0.11444 | 123.0789 | 11.499 | -0.15106 | 123.0377 | 0.11444 | 11.499 | 23.5199 | 123.0789 | -122.8363 | -122.8043
1435.7656 | 122.8043 | -11.0779 | 111.5341 | 0.0045011 | 0.016665 | 0.0050309 | -0.0090041 | 0.058405 | 0.047189 | 0.15679 | -11.2015 | 111.795 | -11.4578 | -10.8902 | 12.0621 | 0.073242 | -0.1236 | -0.33417 | 111.8774 | -11.3617 | -0.37994 | 0.26093 | -0.1236 | 0.18768 | -99.472 | -0.28381 | 0.34332 | 0.25635 | 10.9543 | 10.7437 | 23.14 | 122.8729 | -0.1236 | 122.9553 | 11.1511 | -0.28381 | 122.8729 | -0.1236 | 11.1511 | 23.14 | 122.9553 | -122.9919 | -122.8958
1437.5 | 122.6761 | -10.9772 | 111.7584 | -0.0031279 | 0.017733 | 0.0037491 | -0.00067292 | 0.060541 | 0.046762 | 0.16 | -11.0504 | 111.9186 | -11.3388 | -10.7986 | 11.998 | 0.059509 | -0.036621 | -0.13275 | 112.0193 | -11.2518 | -0.36163 | 0.16022 | -0.073242 | 0.17853 | -99.7604 | -0.27466 | 0.26093 | 0.28839 | 10.9406 | 10.8444 | 22.9752 | 122.8958 | -0.073242 | 122.9965 | 11.0367 | -0.27466 | 122.8958 | -0.073242 | 11.0367 | 22.9752 | 122.9965 | -123.0972 | -123.0103
1439.25 | 122.6852 | -11.1374 | 111.5753 | 0.0045011 | 0.017947 | 0.0086625 | -0.0040909 | 0.060541 | 0.050607 | 0.15722 | -11.2106 | 111.7538 | -11.467 | -10.9268 | 11.9385 | 0.10071 | -0.13275 | -0.54016 | 111.8683 | -11.3251 | -0.32959 | 0.17853 | -0.073242 | 0.21057 | -99.6368 | -0.18768 | 0.29297 | 0.25635 | 11.0046 | 10.5972 | 23.0759 | 122.8912 | -0.073242 | 123.0057 | 11.2381 | -0.18768 | 122.8912 | -0.073242 | 11.2381 | 23.0759 | 123.0057 | -123.0423 | -122.9004
1441.0156 | 122.8271 | -11.0046 | 111.6486 | 0.0045011 | 0.016878 | 0.0060989 | -0.0081497 | 0.057977 | 0.048685 | 0.15914 | -11.2564 | 111.8225 | -11.5036 | -10.9955 | 11.7874 | 0 | 0.050354 | 0.20142 | 111.8958 | -11.4075 | -0.49896 | 0.17395 | -0.25177 | 0.009156 | -99.8611 | -0.40283 | 0.24719 | 0.24719 | 11.055 | 11.2061 | 22.7921 | 122.8271 | -0.25177 | 122.9004 | 11.0046 | -0.40283 | 122.8271 | -0.25177 | 11.0046 | 22.7921 | 122.9004 | -123.1522 | -123.056
1442.7031 | 122.8271 | -10.817 | 111.8591 | 0.0045011 | 0.016665 | 0.0071671 | -0.0085769 | 0.060327 | 0.04783 | 0.15786 | -11.1557 | 111.9049 | -11.3983 | -10.8078 | 11.7691 | 0.004578 | 0.054932 | -0.51727 | 112.088 | -11.1969 | -0.58136 | 0.045776 | -0.33875 | 0.009156 | -100.09 | -0.37994 | 0.22888 | 0.24261 | 10.8719 | 10.2997 | 22.5861 | 122.7219 | -0.33875 | 122.905 | 10.8215 | -0.37994 | 122.7219 | -0.33875 | 10.8215 | 22.5861 | 122.905 | -123.2574 | -123.056
1444.4531 | 122.6807 | -10.7895 | 111.9781 | 0.0045011 | 0.019015 | 0.0075943 | -0.0028091 | 0.060754 | 0.05018 | 0.15936 | -10.7803 | 112.1658 | -11.0825 | -10.5743 | 11.7371 | 0.050354 | -0.041199 | -0.43488 | 112.2574 | -11.0001 | -0.29297 | 0.18768 | 0.009156 | 0.21515 | -100.2411 | -0.21057 | 0.27924 | 0.30212 | 10.7483 | 10.3546 | 22.5266 | 122.9553 | 0.009156 | 123.0469 | 10.8398 | -0.21057 | 122.9553 | 0.009156 | 10.8398 | 22.5266 | 123.0469 | -123.0606 | -122.9782
1446.2031 | 122.7676 | -10.675 | 111.9827 | -0.0031279 | 0.018587 | 0.0058853 | -0.010713 | 0.060541 | 0.051248 | 0.15893 | -10.8078 | 112.1155 | -11.1099 | -10.5377 | 11.8011 | 0.16022 | -0.14191 | -0.27924 | 112.1658 | -11.0229 | -0.43487 | 0.13275 | -0.13275 | 0.13733 | -100.1816 | -0.3479 | 0.18311 | 0.30212 | 10.5331 | 10.3958 | 22.4762 | 122.7905 | -0.13275 | 122.8409 | 10.8353 | -0.3479 | 122.7905 | -0.13275 | 10.8353 | 22.4762 | 122.8409 | -123.0927 | -123.0057
1447.8906 | 122.6761 | -10.9726 | 111.7859 | 0.0045011 | 0.01816 | 0.0067399 | -0.0051589 | 0.061182 | 0.049753 | 0.15914 | -10.8627 | 112.0148 | -11.2015 | -10.675 | 11.7279 | 0.15106 | -0.18768 | 0.027466 | 112.0422 | -11.142 | -0.22888 | 0.22888 | 0.10986 | 0.29755 | -100.058 | -0.16937 | 0.25635 | 0.33875 | 10.7849 | 11.0001 | 22.7005 | 122.9874 | 0.10986 | 123.0148 | 11.1237 | -0.16937 | 122.9874 | 0.10986 | 11.1237 | 22.7005 | 123.0148 | -122.9874 | -122.9279
1449.6406 | 122.818 | -10.7758 | 111.8317 | -0.010757 | 0.017092 | 0.0088761 | -0.0064407 | 0.059473 | 0.048471 | 0.15807 | -10.936 | 112.1429 | -11.1649 | -10.6934 | 11.5036 | 0 | 0.064087 | -0.44403 | 112.2299 | -11.0825 | -0.3891 | 0.31128 | -0.16022 | 0.082398 | -100.3281 | -0.3067 | 0.39825 | 0.22888 | 10.8398 | 10.3317 | 22.2794 | 122.9187 | -0.16022 | 123.0057 | 10.7758 | -0.3067 | 122.9187 | -0.16022 | 10.7758 | 22.2794 | 123.0057 | -122.9965 | -122.9141
1451.375 | 122.6852 | -10.611 | 112.0743 | -0.0031279 | 0.016878 | 0.0054581 | -0.0034499 | 0.059473 | 0.050607 | 0.1585 | -10.6888 | 112.2757 | -10.9863 | -10.4599 | 11.467 | 0.050354 | -0.027466 | -0.16937 | 112.3627 | -10.8994 | -0.37537 | 0.20142 | -0.07782 | 0.15106 | -100.6073 | -0.28839 | 0.28839 | 0.29755 | 10.5835 | 10.4416 | 22.0779 | 122.8867 | -0.07782 | 122.9736 | 10.6613 | -0.28839 | 122.8867 | -0.07782 | 10.6613 | 22.0779 | 122.9736 | -123.0606 | -122.9736
1453.1094 | 122.6761 | -10.5377 | 112.2162 | 0.0045011 | 0.016878 | 0.0067399 | -0.0060135 | 0.060754 | 0.051248 | 0.1585 | -10.5057 | 112.3718 | -10.8078 | -10.2859 | 11.5082 | 0.13275 | -0.20142 | -0.17395 | 112.4405 | -10.7574 | -0.27008 | 0.15564 | 0.032044 | 0.25177 | -100.708 | -0.21973 | 0.2243 | 0.30212 | 10.3363 | 10.3638 | 22.0459 | 122.9095 | 0.032044 | 122.9782 | 10.6705 | -0.21973 | 122.9095 | 0.032044 | 10.6705 | 22.0459 | 122.9782 | -123.024 | -122.9736
1454.8594 | 122.7081 | -10.5103 | 112.2299 | 0.02739 | 0.014742 | 0.0095169 | -0.0032363 | 0.0599 | 0.049753 | 0.16021 | -10.5743 | 112.4542 | -10.8536 | -10.3638 | 11.3525 | 0.004578 | 0 | -0.027466 | 112.5183 | -10.7895 | -0.34332 | 0.22431 | -0.064087 | 0.14648 | -100.8774 | -0.27924 | 0.28839 | 0.27924 | 10.5103 | 10.4828 | 21.8628 | 122.9645 | -0.064087 | 123.0286 | 10.5148 | -0.27924 | 122.9645 | -0.064087 | 10.5148 | 21.8628 | 123.0286 | -123.0835 | -123.0194
1456.5312 | 122.8043 | -10.6293 | 112.0468 | 0.012131 | 0.018587 | 0.0071671 | -0.0081497 | 0.058618 | 0.053171 | 0.15658 | -10.6384 | 112.3489 | -10.9085 | -10.3867 | 11.3663 | 0.064087 | -0.009155 | -0.15106 | 112.381 | -10.8673 | -0.27924 | 0.30212 | -0.009156 | 0.24261 | -100.6805 | -0.23804 | 0.33417 | 0.27008 | 10.6201 | 10.4782 | 21.9955 | 122.9782 | -0.009156 | 123.0103 | 10.6934 | -0.23804 | 122.9782 | -0.009156 | 10.6934 | 21.9955 | 123.0103 | -122.9553 | -122.9141
1458.2812 | 122.6532 | -10.8536 | 111.882 | 0.0045011 | 0.018587 | 0.010799 | -0.0081497 | 0.059686 | 0.049539 | 0.15893 | -10.7712 | 112.1338 | -11.0687 | -10.5423 | 11.3754 | 0.13733 | -0.19226 | 0 | 112.2025 | -10.9863 | -0.21515 | 0.25177 | 0.082398 | 0.31128 | -100.5066 | -0.13275 | 0.32044 | 0.29755 | 10.6613 | 10.8536 | 22.229 | 122.9874 | 0.082398 | 123.056 | 10.9909 | -0.13275 | 122.9874 | 0.082398 | 10.9909 | 22.229 | 123.056 | -122.9507 | -122.8683
1459.9531 | 122.6807 | -10.7712 | 111.9553 | 0.012131 | 0.020083 | 0.010799 | -0.0040909 | 0.059686 | 0.048257 | 0.15914 | -10.7803 | 112.1979 | -11.055 | -10.524 | 11.3068 | 0.050354 | -0.045776 | 0.24719 | 112.2711 | -10.9726 | -0.28381 | 0.24262 | -0.009155 | 0.24719 | -100.6485 | -0.20142 | 0.31586 | 0.27466 | 10.7254 | 11.0184 | 22.0779 | 122.9691 | -0.009155 | 123.0423 | 10.8215 | -0.20142 | 122.9691 | -0.009155 | 10.8215 | 22.0779 | 123.0423 | -123.0103 | -122.9279
1461.7031 | 122.8043 | -10.8398 | 111.8042 | -0.0031279 | 0.018374 | 0.0084489 | -0.011781 | 0.059473 | 0.05018 | 0.16042 | -10.8902 | 112.0697 | -11.1191 | -10.6339 | 11.3022 | 0.11902 | -0.10986 | 0.29755 | 112.1613 | -11.0825 | -0.27924 | 0.2655 | -0.050354 | 0.20599 | -100.502 | -0.24261 | 0.35706 | 0.22888 | 10.73 | 11.1374 | 22.142 | 122.9095 | -0.050354 | 123.0011 | 10.9589 | -0.24261 | 122.9095 | -0.050354 | 10.9589 | 22.142 | 123.0011 | -122.9233 | -122.8867
1463.375 | 122.7127 | -10.6247 | 112.1155 | 0.0045011 | 0.017519 | 0.0080215 | -0.0015273 | 0.062463 | 0.048257 | 0.15957 | -10.73 | 112.2894 | -10.9817 | -10.5148 | 11.2015 | 0.004578 | -0.004578 | 0.16022 | 112.3672 | -10.9131 | -0.35706 | 0.17395 | -0.10529 | 0.10986 | -100.914 | -0.28839 | 0.25177 | 0.25177 | 10.6201 | 10.7849 | 21.8262 | 122.9141 | -0.10529 | 122.9919 | 10.6293 | -0.28839 | 122.9141 | -0.10529 | 10.6293 | 21.8262 | 122.9919 | -123.0972 | -123.0286
1465.125 | 122.7814 | -10.8124 | 111.8774 | 0.0045011 | 0.017519 | 0.0056717 | -0.011141 | 0.059686 | 0.049753 | 0.15978 | -10.881 | 112.0331 | -11.1603 | -10.6155 | 11.3022 | 0.14191 | -0.15106 | 0.3479 | 112.1292 | -11.0916 | -0.3479 | 0.15564 | -0.068664 | 0.19684 | -100.5753 | -0.27924 | 0.25177 | 0.27924 | 10.6613 | 11.1603 | 22.1146 | 122.8455 | -0.068664 | 122.9416 | 10.9543 | -0.27924 | 122.8455 | -0.068664 | 10.9543 | 22.1146 | 122.9416 | -123.0377 | -122.9691
1466.875 | 122.6761 | -10.7254 | 112.0377 | 0.0045011 | 0.017519 | 0.010158 | -0.0068679 | 0.063104 | 0.049966 | 0.15957 | -10.7208 | 112.1979 | -11.0184 | -10.4828 | 11.2839 | 0.12817 | -0.17395 | 0.29297 | 112.2482 | -10.9406 | -0.29297 | 0.16022 | 0.004578 | 0.24262 | -100.7538 | -0.21515 | 0.21057 | 0.29755 | 10.5515 | 11.0184 | 22.0093 | 122.9233 | 0.004578 | 122.9736 | 10.8536 | -0.21515 | 122.9233 | 0.004578 | 10.8536 | 22.0093 | 122.9736 | -123.056 | -122.9782
1468.5625 | 122.8134 | -10.3409 | 112.3306 | -0.0031279 | 0.01816 | 0.0050309 | -0.0049453 | 0.058832 | 0.048471 | 0.15978 | -10.5331 | 112.5366 | -10.7803 | -10.2448 | 11.1694 | -0.013733 | 0.050354 | 0.20599 | 112.587 | -10.6888 | -0.43945 | 0.20599 | -0.19226 | 0.09613 | -101.1612 | -0.3479 | 0.25635 | 0.24719 | 10.3912 | 10.5469 | 21.5103 | 122.8775 | -0.19226 | 122.9279 | 10.3271 | -0.3479 | 122.8775 | -0.19226 | 10.3271 | 21.5103 | 122.9279 | -123.111 | -123.0194
1470.3125 | 122.8271 | -10.4416 | 112.2116 | 0.0045011 | 0.016878 | 0.0082351 | -0.0105 | 0.060114 | 0.051035 | 0.16085 | -10.4141 | 112.5595 | -10.6522 | -10.1852 | 11.2473 | 0.09613 | -0.10071 | 0.2655 | 112.6282 | -10.643 | -0.21057 | 0.3479 | 0.027465 | 0.25635 | -100.9644 | -0.20142 | 0.41657 | 0.23804 | 10.3409 | 10.7071 | 21.6888 | 123.0011 | 0.027465 | 123.0698 | 10.5377 | -0.20142 | 123.0011 | 0.027465 | 10.5377 | 21.6888 | 123.0698 | -122.8638 | -122.8546
1472.0625 | 122.8134 | -10.3134 | 112.3489 | 0.0045011 | 0.017519 | 0.0026809 | -0.0049453 | 0.058832 | 0.050394 | 0.16042 | -10.4095 | 112.6144 | -10.6384 | -10.1669 | 11.2289 | 0.013733 | 0.045776 | 0.19684 | 112.7014 | -10.5972 | -0.32501 | 0.2655 | -0.09613 | 0.14649 | -101.12 | -0.28381 | 0.35248 | 0.22888 | 10.3592 | 10.5103 | 21.5424 | 122.9279 | -0.09613 | 123.0148 | 10.3271 | -0.28381 | 122.9279 | -0.09613 | 10.3271 | 21.5424 | 123.0148 | -122.9874 | -122.9462
1473.75 | 122.7173 | -10.2859 | 112.4634 | 0.01976 | 0.019442 | 0.0067399 | -0.0043045 | 0.062891 | 0.051035 | 0.15914 | -10.4004 | 112.6373 | -10.6522 | -10.1761 | 11.1465 | -0.013733 | 0.018311 | 0.16937 | 112.7197 | -10.5972 | -0.36621 | 0.17395 | -0.11444 | 0.10986 | -101.3168 | -0.31128 | 0.25635 | 0.25177 | 10.3043 | 10.4553 | 21.4325 | 122.9233 | -0.11444 | 123.0057 | 10.2722 | -0.31128 | 122.9233 | -0.11444 | 10.2722 | 21.4325 | 123.0057 | -123.1155 | -123.0606
1475.5156 | 122.6852 | -10.1257 | 112.6282 | 0.012131 | 0.018801 | 0.0037491 | -0.0040909 | 0.060327 | 0.047617 | 0.16171 | -10.2356 | 112.7289 | -10.5286 | -10.0021 | 11.2473 | 0.064087 | -0.027466 | 0.24261 | 112.7792 | -10.4736 | -0.40283 | 0.10071 | -0.10986 | 0.1236 | -101.3809 | -0.3479 | 0.15106 | 0.29297 | 10.0983 | 10.3683 | 21.373 | 122.8546 | -0.10986 | 122.905 | 10.1898 | -0.3479 | 122.8546 | -0.10986 | 10.1898 | 21.373 | 122.905 | -123.1567 | -123.1018
1477.2188 | 122.7356 | -10.0754 | 112.6328 | -0.010757 | 0.019442 | 0.012294 | -0.0038773 | 0.062036 | 0.050394 | 0.16171 | -10.1669 | 112.9349 | -10.3958 | -9.9472 | 11.1374 | 0.004578 | 0.018311 | 0.16022 | 112.9578 | -10.318 | -0.32043 | 0.30212 | -0.091553 | 0.12817 | -101.4954 | -0.24261 | 0.32501 | 0.22888 | 10.0937 | 10.2356 | 21.2128 | 123.0103 | -0.091553 | 123.0331 | 10.08 | -0.24261 | 123.0103 | -0.091553 | 10.08 | 21.2128 | 123.0331 | -123.0286 | -122.9507
1478.9844 | 122.6669 | -10.0983 | 112.6556 | -0.018387 | 0.015597 | 0.010158 | -0.0083633 | 0.060541 | 0.050607 | 0.16042 | -9.9884 | 112.9349 | -10.2814 | -9.7229 | 11.2381 | 0.14191 | -0.16479 | 0.28839 | 112.9807 | -10.2127 | -0.1831 | 0.27923 | 0.10986 | 0.37537 | -101.4175 | -0.11444 | 0.32501 | 0.29297 | 9.9335 | 10.3867 | 21.3364 | 123.0331 | 0.10986 | 123.0789 | 10.2402 | -0.11444 | 123.0331 | 0.10986 | 10.2402 | 21.3364 | 123.0789 | -122.937 | -122.8683
1480.6562 | 122.699 | -10.1486 | 112.5778 | 0.0045011 | 0.015383 | 0.0088761 | -0.0036637 | 0.061182 | 0.050394 | 0.16192 | -10.1944 | 112.7884 | -10.4599 | -9.9426 | 11.2518 | 0.059509 | 0 | 0.2243 | 112.8479 | -10.3912 | -0.31128 | 0.21057 | -0.045776 | 0.20599 | -101.326 | -0.24261 | 0.27008 | 0.2655 | 10.1486 | 10.3729 | 21.4005 | 122.937 | -0.045776 | 122.9965 | 10.2081 | -0.24261 | 122.937 | -0.045776 | 10.2081 | 21.4005 | 122.9965 | -123.0377 | -122.9691
1482.4062 | 122.7036 | -10.0891 | 112.619 | -0.0031279 | 0.019656 | 0.0086625 | -0.0051589 | 0.060754 | 0.051462 | 0.16384 | -10.1669 | 112.8479 | -10.4187 | -9.9426 | 11.1649 | 0.018311 | -0.073242 | 0.18768 | 112.8708 | -10.35 | -0.32959 | 0.22888 | -0.07782 | 0.14648 | -101.4542 | -0.26093 | 0.25177 | 0.25177 | 10.0159 | 10.2768 | 21.254 | 122.937 | -0.07782 | 122.9599 | 10.1074 | -0.26093 | 122.937 | -0.07782 | 10.1074 | 21.254 | 122.9599 | -123.0377 | -122.9691
1484.0938 | 122.7081 | -10.2722 | 112.4313 | 0.0045011 | 0.02051 | 0.0095169 | -0.0040909 | 0.0599 | 0.05018 | 0.16149 | -10.3455 | 112.6511 | -10.6155 | -10.0983 | 11.1374 | 0.059509 | 0 | 0.23346 | 112.6968 | -10.524 | -0.34332 | 0.21973 | -0.073242 | 0.17395 | -101.2939 | -0.25177 | 0.2655 | 0.27008 | 10.2722 | 10.5057 | 21.4096 | 122.9233 | -0.073242 | 122.9691 | 10.3317 | -0.25177 | 122.9233 | -0.073242 | 10.3317 | 21.4096 | 122.9691 | -123.0469 | -122.9553
1485.8281 | 122.6944 | -10.1578 | 112.5458 | 0.0045011 | 0.018587 | 0.0052445 | -0.0068679 | 0.062036 | 0.048898 | 0.16107 | -10.2173 | 112.738 | -10.5103 | -9.9655 | 11.1099 | 0.073242 | -0.10986 | 0.23346 | 112.8387 | -10.3867 | -0.35248 | 0.19226 | -0.059509 | 0.19226 | -101.4359 | -0.22888 | 0.29297 | 0.29297 | 10.0479 | 10.3912 | 21.2677 | 122.8958 | -0.059509 | 122.9965 | 10.231 | -0.22888 | 122.8958 | -0.059509 | 10.231 | 21.2677 | 122.9965 | -123.056 | -122.9324
1487.5625 | 122.699 | -10.0708 | 112.5961 | 0.012131 | 0.019015 | 0.0052445 | -0.0053727 | 0.060114 | 0.050821 | 0.16192 | -10.2036 | 112.7792 | -10.4462 | -9.9792 | 10.9726 | 0.022888 | -0.004578 | 0.17395 | 112.9211 | -10.3729 | -0.37537 | 0.18311 | -0.13275 | 0.091553 | -101.6235 | -0.30212 | 0.32501 | 0.24262 | 10.0662 | 10.2448 | 21.0434 | 122.85 | -0.13275 | 122.9919 | 10.0937 | -0.30212 | 122.85 | -0.13275 | 10.0937 | 21.0434 | 122.9919 | -123.0423 | -122.9691
1489.2969 | 122.7905 | -10.0662 | 112.5641 | 0.0045011 | 0.017092 | 0.0058853 | -0.010927 | 0.059259 | 0.05253 | 0.16085 | -10.2219 | 112.7472 | -10.4782 | -9.9655 | 10.9863 | 0.09613 | -0.086975 | 0.25635 | 112.7975 | -10.437 | -0.41199 | 0.1831 | -0.15564 | 0.10071 | -101.5778 | -0.37079 | 0.23346 | 0.25635 | 9.9792 | 10.3226 | 21.0526 | 122.8134 | -0.15564 | 122.8638 | 10.1624 | -0.37079 | 122.8134 | -0.15564 | 10.1624 | 21.0526 | 122.8638 | -123.0423 | -123.0011
1491.0469 | 122.6532 | -10.1578 | 112.5732 | 0.0045011 | 0.016451 | 0.0073807 | -0.0034499 | 0.062677 | 0.050821 | 0.16149 | -10.1761 | 112.7655 | -10.4919 | -9.9197 | 10.9634 | 0.054932 | -0.032043 | 0.21057 | 112.8571 | -10.3912 | -0.33417 | 0.19226 | -0.01831 | 0.23804 | -101.6098 | -0.23346 | 0.28381 | 0.31586 | 10.1257 | 10.3683 | 21.1212 | 122.9233 | -0.01831 | 123.0148 | 10.2127 | -0.23346 | 122.9233 | -0.01831 | 10.2127 | 21.1212 | 123.0148 | -123.0652 | -122.9645
1492.7188 | 122.7356 | -10.2264 | 112.4176 | 0.0045011 | 0.016878 | 0.00054467 | -0.012422 | 0.060114 | 0.052316 | 0.16256 | -10.199 | 112.674 | -10.5194 | -9.9518 | 11.0825 | 0.14648 | -0.12817 | 0.33875 | 112.7289 | -10.437 | -0.29297 | 0.25635 | 0.027465 | 0.27466 | -101.3351 | -0.21057 | 0.31128 | 0.32043 | 10.0983 | 10.5652 | 21.3089 | 122.9004 | 0.027465 | 122.9553 | 10.3729 | -0.21057 | 122.9004 | 0.027465 | 10.3729 | 21.3089 | 122.9553 | -122.937 | -122.8546
1494.4688 | 122.7814 | -10.1074 | 112.5641 | 0.012131 | 0.017519 | 0.0073807 | -0.0068679 | 0.062036 | 0.050607 | 0.1632 | -10.2036 | 112.8113 | -10.4507 | -9.9335 | 11.0092 | 0.009155 | 0.050354 | 0.21515 | 112.8845 | -10.3683 | -0.34332 | 0.24719 | -0.09613 | 0.17395 | -101.5549 | -0.26093 | 0.32043 | 0.24719 | 10.1578 | 10.3226 | 21.1166 | 122.9187 | -0.09613 | 122.9919 | 10.1166 | -0.26093 | 122.9187 | -0.09613 | 10.1166 | 21.1166 | 122.9919 | -123.0148 | -122.9324
1496.2188 | 122.731 | -10.1532 | 112.4817 | 0.0045011 | 0.017519 | 0.0088761 | -0.011568 | 0.059259 | 0.052744 | 0.16213 | -10.0388 | 112.8525 | -10.3729 | -9.8007 | 11.0779 | 0.13275 | -0.091553 | 0.32501 | 112.8662 | -10.3134 | -0.21973 | 0.37079 | 0.11444 | 0.35248 | -101.4038 | -0.16022 | 0.38452 | 0.33417 | 10.0616 | 10.4782 | 21.2311 | 123.0057 | 0.11444 | 123.0194 | 10.2859 | -0.16022 | 123.0057 | 0.11444 | 10.2859 | 21.2311 | 123.0194 | -122.8546 | -122.7951
1497.9062 | 122.6944 | -10.0937 | 112.5824 | -0.0031279 | 0.019442 | 0.0065263 | -0.0030227 | 0.061182 | 0.050607 | 0.16064 | -10.1395 | 112.8983 | -10.3912 | -9.906 | 10.9406 | 0.027466 | -0.004578 | 0.16937 | 112.9303 | -10.3226 | -0.29755 | 0.31586 | -0.045776 | 0.18768 | -101.6418 | -0.22888 | 0.3479 | 0.25177 | 10.0891 | 10.2631 | 21.0342 | 122.9919 | -0.045776 | 123.024 | 10.1212 | -0.22888 | 122.9919 | -0.045776 | 10.1212 | 21.0342 | 123.024 | -122.9736 | -122.905
1499.6562 | 122.6624 | -10.1486 | 112.5504 | 0.0045011 | 0.018587 | 0.0039627 | -0.0068679 | 0.061395 | 0.051248 | 0.16192 | -10.0937 | 112.7747 | -10.3958 | -9.874 | 11.0001 | 0.14191 | -0.14648 | 0.25177 | 112.8113 | -10.35 | -0.24719 | 0.2243 | 0.054932 | 0.27466 | -101.5503 | -0.20142 | 0.26093 | 0.30212 | 10.0021 | 10.4004 | 21.1487 | 122.9233 | 0.054932 | 122.9599 | 10.2905 | -0.20142 | 122.9233 | 0.054932 | 10.2905 | 21.1487 | 122.9599 | -122.9462 | -122.9004
1501.4219 | 122.7081 | -13.4354 | 109.2316 | 0.0045011 | 0.017092 | 0.0086625 | -0.0019547 | 0.061182 | 0.048685 | 0.2384 | -13.4262 | 109.5795 | -13.6459 | -13.1607 | 10.6979 | 0.054932 | -0.022888 | 0.17853 | 109.6344 | -13.5452 | -0.21057 | 0.3479 | 0.009156 | 0.27466 | -98.5336 | -0.10986 | 0.40283 | 0.21973 | 13.4125 | 13.6139 | 24.1333 | 123.0148 | 0.009156 | 123.0698 | 13.4903 | -0.10986 | 123.0148 | 0.009156 | 13.4903 | 24.1333 | 123.0698 | -122.8775 | -122.7768
1503.1719 | 122.6944 | -12.3642 | 110.3119 | 0.0045011 | 0.019869 | 0.0078079 | -0.0043045 | 0.06225 | 0.048257 | 0.24011 | -12.4969 | 110.5362 | -12.7121 | -12.2406 | 10.7117 | 0.013733 | 0.004578 | 0.054932 | 110.6003 | -12.6297 | -0.3479 | 0.2243 | -0.13275 | 0.1236 | -99.6002 | -0.2655 | 0.28839 | 0.21515 | 12.3688 | 12.4191 | 23.0759 | 122.9004 | -0.13275 | 122.9645 | 12.3779 | -0.2655 | 122.9004 | -0.13275 | 12.3779 | 23.0759 | 122.9645 | -123.024 | -122.9416
1504.9219 | 122.6761 | -8.9264 | 113.7588 | 0.0045011 | 0.018374 | 0.070399 | -0.0066543 | 0.061182 | 0.057657 | 0.18606 | -7.4387 | 114.0564 | -9.2102 | -8.7524 | -0.5722 | -0.022888 | 0.027466 | 0.091553 | 114.0839 | -9.1782 | -0.28381 | 0.29755 | 1.4877 | 0.17395 | -114.3311 | -0.25177 | 0.32501 | 1.7715 | 8.9539 | 9.0179 | 8.3542 | 122.9828 | 1.4877 | 123.0103 | 8.9035 | -0.25177 | 122.9828 | 1.4877 | 8.9035 | 8.3542 | 123.0103 | -122.9691 | -122.937
1506.6094 | 122.6257 | -8.9905 | 113.7085 | 0.0045011 | 0.020083 | 0.07574 | -0.0023819 | 0.061182 | 0.056802 | 0.18542 | -7.3746 | 113.9786 | -9.2514 | -8.7204 | -1.0208 | 0.036621 | 0.009155 | 0.14191 | 114.0289 | -9.1965 | -0.26093 | 0.27008 | 1.6159 | 0.27008 | -114.7293 | -0.20599 | 0.32044 | 1.8768 | 8.9996 | 9.1324 | 7.9697 | 122.9691 | 1.6159 | 123.0194 | 9.0271 | -0.20599 | 122.9691 | 1.6159 | 9.0271 | 7.9697 | 123.0194 | -122.9599 | -122.905
1508.3438 | 122.6578 | -9.0866 | 113.5941 | 0.012131 | 0.019228 | 0.076594 | -0.0051589 | 0.060968 | 0.056161 | 0.1835 | -7.5485 | 113.8824 | -9.3842 | -8.8898 | -0.91095 | 0.004578 | 0.032043 | 0.14191 | 113.9374 | -9.3155 | -0.29755 | 0.28839 | 1.5381 | 0.19684 | -114.505 | -0.22888 | 0.34332 | 1.8356 | 9.1187 | 9.2285 | 8.1757 | 122.9691 | 1.5381 | 123.024 | 9.0912 | -0.22888 | 122.9691 | 1.5381 | 9.0912 | 8.1757 | 123.024 | -122.9782 | -122.9095
1510.0781 | 122.644 | -9.1049 | 113.5986 | 0.012131 | 0.020083 | 0.077022 | -0.0055863 | 0.063104 | 0.057016 | 0.18221 | -7.4936 | 113.8412 | -9.3933 | -8.8531 | -1.2589 | 0.064087 | 0 | 0.19684 | 113.9145 | -9.343 | -0.28839 | 0.24261 | 1.6113 | 0.25177 | -114.8575 | -0.23804 | 0.31586 | 1.8997 | 9.1049 | 9.3018 | 7.8461 | 122.9462 | 1.6113 | 123.0194 | 9.169 | -0.23804 | 122.9462 | 1.6113 | 9.169 | 7.8461 | 123.0194 | -122.9919 | -122.9416
1511.8281 | 122.7173 | -8.9951 | 113.6719 | 0.012131 | 0.016024 | 0.075099 | -0.012422 | 0.060114 | 0.058084 | 0.17986 | -7.3746 | 113.8916 | -9.3109 | -8.7204 | -1.2543 | 0.13733 | -0.10071 | 0.29297 | 113.9282 | -9.2239 | -0.31586 | 0.21973 | 1.6205 | 0.27466 | -114.9261 | -0.22888 | 0.25635 | 1.9363 | 8.8943 | 9.288 | 7.7408 | 122.8867 | 1.6205 | 122.9233 | 9.1324 | -0.22888 | 122.8867 | 1.6205 | 9.1324 | 7.7408 | 122.9233 | -122.9828 | -122.8958
1513.5156 | 122.6898 | -9.5489 | 113.1638 | -0.0031279 | 0.018587 | 0.078303 | -0.0049453 | 0.059473 | 0.058511 | 0.1788 | -7.9605 | 113.443 | -9.8099 | -9.3109 | -1.6617 | -0.022888 | 0.032043 | 0.09613 | 113.4888 | -9.7549 | -0.26093 | 0.27924 | 1.5884 | 0.23804 | -114.8254 | -0.20599 | 0.32501 | 1.8494 | 9.581 | 9.6451 | 7.8873 | 122.9919 | 1.5884 | 123.0377 | 9.5261 | -0.20599 | 122.9919 | 1.5884 | 9.5261 | 7.8873 | 123.0377 | -122.9736 | -122.9187
1515.25 | 122.6898 | -12.2726 | 110.408 | 0.0045011 | 0.014101 | 0.0020401 | -0.010286 | 0.060327 | 0.051248 | 0.23904 | -12.3184 | 110.5637 | -12.561 | -12.0758 | 12.4374 | 0.13275 | -0.1236 | 0.15106 | 110.6689 | -12.4878 | -0.28839 | 0.15564 | -0.045776 | 0.19684 | -97.9706 | -0.21515 | 0.26093 | 0.24262 | 12.149 | 12.4237 | 24.7101 | 122.8363 | -0.045776 | 122.9416 | 12.4054 | -0.21515 | 122.8363 | -0.045776 | 12.4054 | 24.7101 | 122.9416 | -122.9691 | -122.8958
1517 | 122.6715 | -10.8353 | 111.8408 | 0.0045011 | 0.018374 | 0.0099441 | -0.010286 | 0.058191 | 0.050394 | 0.23968 | -10.8627 | 112.0239 | -11.142 | -10.6201 | 11.4395 | 0.13733 | -0.12817 | 0.21973 | 112.1063 | -11.0596 | -0.3067 | 0.18311 | -0.027466 | 0.21515 | -100.4013 | -0.2243 | 0.2655 | 0.27924 | 10.7071 | 11.055 | 22.2748 | 122.8592 | -0.027466 | 122.9416 | 10.9726 | -0.2243 | 122.8592 | -0.027466 | 10.9726 | 22.2748 | 122.9416 | -122.9828 | -122.9004
1518.7344 | 122.7219 | -7.6538 | 115.0635 | 0.0045011 | 0.016024 | 0.074458 | -0.0075089 | 0.057977 | 0.061288 | 0.18649 | -6.1249 | 115.2466 | -7.9376 | -7.3975 | -0.32044 | 0.10071 | -0.082397 | 0.2243 | 115.3061 | -7.8873 | -0.28381 | 0.1831 | 1.5289 | 0.25635 | -115.3839 | -0.23346 | 0.24261 | 1.8127 | 7.5714 | 7.8781 | 7.3334 | 122.9004 | 1.5289 | 122.9599 | 7.7545 | -0.23346 | 122.9004 | 1.5289 | 7.7545 | 7.3334 | 122.9599 | -123.0011 | -122.9507
1520.4844 | 122.7173 | -7.5439 | 115.1184 | 0.0045011 | 0.016451 | 0.071254 | -0.0090041 | 0.057764 | 0.057657 | 0.18499 | -5.9509 | 115.3839 | -7.8094 | -7.1823 | -0.073242 | 0.16479 | -0.09613 | 0.32501 | 115.4388 | -7.7591 | -0.2655 | 0.2655 | 1.593 | 0.36163 | -115.1916 | -0.21515 | 0.32044 | 1.8585 | 7.4478 | 7.869 | 7.4707 | 122.9279 | 1.593 | 122.9828 | 7.7087 | -0.21515 | 122.9279 | 1.593 | 7.7087 | 7.4707 | 122.9828 | -122.9279 | -122.8775
1522.1719 | 122.7219 | -9.1507 | 113.5071 | 0.0045011 | 0.017519 | 0.0039627 | -0.0096451 | 0.061395 | 0.050394 | 0.24203 | -9.1324 | 113.7497 | -9.4574 | -8.8348 | 12.0071 | 0.15564 | -0.086975 | 0.31128 | 113.7955 | -9.3979 | -0.3067 | 0.24262 | 0.018311 | 0.31586 | -101.4999 | -0.24719 | 0.28839 | 0.32501 | 9.0637 | 9.462 | 21.1578 | 122.9004 | 0.018311 | 122.9462 | 9.3063 | -0.24719 | 122.9004 | 0.018311 | 9.3063 | 21.1578 | 122.9462 | -122.9645 | -122.905
1523.9062 | 122.7493 | -8.519 | 114.1479 | 0.0045011 | 0.016451 | 0.0031083 | -0.0060135 | 0.059259 | 0.050821 | 0.24246 | -8.5236 | 114.3723 | -8.8669 | -8.2214 | 11.3663 | 0.14648 | -0.054932 | 0.29297 | 114.3951 | -8.8028 | -0.3479 | 0.2243 | -0.004578 | 0.29755 | -102.7817 | -0.28381 | 0.24719 | 0.34332 | 8.464 | 8.812 | 19.8853 | 122.8912 | -0.004578 | 122.9141 | 8.6655 | -0.28381 | 122.8912 | -0.004578 | 8.6655 | 19.8853 | 122.9141 | -123.0148 | -122.9507
1525.6562 | 122.6578 | -7.9514 | 114.8117 | 0.0045011 | 0.018587 | 0.0067399 | -0.0036637 | 0.060327 | 0.050821 | 0.24331 | -7.8644 | 115.0131 | -8.2169 | -7.5806 | 11.1969 | 0.13733 | -0.14191 | 0.25177 | 115.0497 | -8.1161 | -0.2655 | 0.20142 | 0.086975 | 0.37079 | -103.6148 | -0.16479 | 0.23804 | 0.35248 | 7.8094 | 8.2031 | 19.1483 | 122.9645 | 0.086975 | 123.0011 | 8.0887 | -0.16479 | 122.9645 | 0.086975 | 8.0887 | 19.1483 | 123.0011 | -123.0286 | -122.9279
1527.3438 | 122.6898 | -7.8369 | 114.8987 | 0.0045011 | 0.018587 | 0.011653 | -0.0049453 | 0.0599 | 0.052957 | 0.24374 | -7.8644 | 115.1321 | -8.1665 | -7.5897 | 10.9817 | 0.027466 | 0.009155 | 0.14191 | 115.1779 | -8.0704 | -0.32959 | 0.23346 | -0.027466 | 0.24719 | -103.9169 | -0.23346 | 0.27923 | 0.30212 | 7.8461 | 7.9788 | 18.8187 | 122.9691 | -0.027466 | 123.0148 | 7.8644 | -0.23346 | 122.9691 | -0.027466 | 7.8644 | 18.8187 | 123.0148 | -123.0652 | -122.9691
1529.0938 | 122.7676 | -7.6447 | 115.004 | 0.01976 | 0.016238 | 0.0093033 | -0.0087905 | 0.060968 | 0.050821 | 0.24416 | -7.6218 | 115.242 | -7.9788 | -7.3563 | 10.9589 | 0.10071 | 0.018311 | 0.21973 | 115.361 | -7.9056 | -0.33417 | 0.23804 | 0.022888 | 0.28839 | -104.0451 | -0.26093 | 0.35706 | 0.35706 | 7.663 | 7.8644 | 18.6035 | 122.8867 | 0.022888 | 123.0057 | 7.7454 | -0.26093 | 122.8867 | 0.022888 | 7.7454 | 18.6035 | 123.0057 | -122.9828 | -122.9095
1530.7812 | 122.699 | -7.5943 | 115.1093 | 0.0045011 | 0.01581 | 0.0020401 | -0.0055863 | 0.060327 | 0.051248 | 0.24566 | -7.5577 | 115.2969 | -7.869 | -7.2922 | 12.2726 | 0.11444 | -0.086975 | 0.23804 | 115.4068 | -7.8094 | -0.27466 | 0.18768 | 0.036621 | 0.30212 | -102.8366 | -0.21515 | 0.29755 | 0.31128 | 7.5073 | 7.8323 | 19.8669 | 122.8912 | 0.036621 | 123.0011 | 7.7087 | -0.21515 | 122.8912 | 0.036621 | 7.7087 | 19.8669 | 123.0011 | -122.9782 | -122.9187
1532.5312 | 122.7997 | -7.4844 | 115.1459 | 0.01976 | 0.016878 | 0.0037491 | -0.0055863 | 0.058618 | 0.051035 | 0.24246 | -7.6309 | 115.3885 | -7.9056 | -7.3196 | 12.0483 | 0.009155 | 0.10986 | 0.16479 | 115.4709 | -7.814 | -0.42114 | 0.24262 | -0.14648 | 0.16479 | -103.0975 | -0.32959 | 0.32501 | 0.27466 | 7.5943 | 7.6492 | 19.5328 | 122.8729 | -0.14648 | 122.9553 | 7.4936 | -0.32959 | 122.8729 | -0.14648 | 7.4936 | 19.5328 | 122.9553 | -123.0515 | -122.9599
1534.2812 | 122.7814 | -7.5119 | 115.1001 | 0.0045011 | 0.018587 | 0.0058853 | -0.010713 | 0.058832 | 0.053384 | 0.24545 | -7.5302 | 115.3931 | -7.8415 | -7.2189 | 12.0026 | 0.12817 | -0.068665 | 0.23804 | 115.448 | -7.7728 | -0.32959 | 0.29297 | -0.01831 | 0.29297 | -103.0975 | -0.26093 | 0.3479 | 0.31128 | 7.4432 | 7.7499 | 19.5145 | 122.905 | -0.01831 | 122.9599 | 7.6401 | -0.26093 | 122.905 | -0.01831 | 7.6401 | 19.5145 | 122.9599 | -122.9416 | -122.8729
1536.0469 | 122.7585 | -7.402 | 115.2649 | 0.0045011 | 0.016024 | 0.0075943 | -0.0083633 | 0.057977 | 0.051462 | 0.24203 | -7.37 | 115.4984 | -7.7087 | -7.0908 | 11.998 | 0.10071 | 0 | 0.29297 | 115.5853 | -7.6584 | -0.3067 | 0.23346 | 0.032044 | 0.31128 | -103.2669 | -0.25635 | 0.32043 | 0.33874 | 7.402 | 7.695 | 19.4 | 122.9004 | 0.032044 | 122.9874 | 7.5027 | -0.25635 | 122.9004 | 0.032044 | 7.5027 | 19.4 | 122.9874 | -122.9736 | -122.9233
1537.7344 | 122.6669 | -105.098 | 17.3904 | 0.0045011 | 0.012392 | 0.0082351 | -0.0066543 | 0.060327 | 0.00040583 | 2.8284 | -105.8212 | 16.6122 | -106.311 | -105.2628 | 3.3463 | 0.041199 | -0.97046 | -0.1831 | 16.5344 | -106.2607 | -1.2131 | -0.7782 | -0.72327 | -0.16479 | -14.0442 | -1.1627 | -0.85602 | 0.48981 | 104.1275 | 104.9149 | 108.4442 | 121.7102 | -0.72327 | 121.6324 | 105.1392 | -1.1627 | 121.7102 | -0.72327 | 105.1392 | 108.4442 | 121.6324 | -123.7015 | -123.6511
1539.4844 | 122.6898 | -122.1405 | 0.55847 | -0.0031279 | 0.017947 | 0.012935 | -0.00045932 | 0.062463 | -0.0085664 | 0.095697 | -121.0876 | 0.62714 | -122.525 | -122.081 | -7.0908 | -0.018311 | -1.062 | -0.52185 | 0.71411 | -122.2733 | -0.38452 | 0.068664 | 1.0529 | 0.059509 | -7.6492 | -0.13275 | 0.15564 | 1.4374 | 121.0785 | 121.6187 | 115.0497 | 122.7676 | 1.0529 | 122.8546 | 122.1222 | -0.13275 | 122.7676 | 1.0529 | 122.1222 | 115.0497 | 122.8546 | -123.0835 | -122.8317
1541.25 | 122.7768 | -122.1176 | 0.51727 | 0.0045011 | 0.014742 | 0.12701 | -0.0068679 | 0.062036 | 0.048898 | 0.10296 | -124.5575 | 0.66376 | -122.5204 | -122.0398 | -93.9789 | -0.1831 | -1.0071 | -0.54932 | 0.71869 | -122.438 | -0.40283 | 0.14648 | -2.4399 | 0.07782 | -94.4962 | -0.32043 | 0.20142 | -2.037 | 121.1105 | 121.5683 | 28.1387 | 122.7814 | -2.4399 | 122.8363 | 121.9345 | -0.32043 | 122.7814 | -2.4399 | 121.9345 | 28.1387 | 122.8363 | -123.0377 | -122.9553
1543 | 122.5616 | -119.0964 | 3.5477 | -0.0031279 | 0.015597 | 1.205 | -0.013918 | 0.06225 | 0.032236 | 0.1004 | -91.626 | 3.5934 | -119.3069 | -118.927 | -60.6995 | 0.041199 | -1.0895 | -0.37537 | 3.6667 | -119.3344 | -0.21057 | 0.045777 | 27.4704 | 0.16937 | -64.2471 | -0.23804 | 0.11902 | 27.681 | 118.0069 | 118.721 | 58.3969 | 122.6898 | 27.4704 | 122.7631 | 119.1376 | -0.23804 | 122.6898 | 27.4704 | 119.1376 | 58.3969 | 122.7631 | -122.8546 | -122.8821
1544.6719 | 122.525 | -118.0161 | 4.3854 | -0.0031279 | 0.016024 | 3.2243 | -0.0077225 | 0.061395 | 0.0072418 | 0.44326 | -42.5491 | 4.4724 | -118.1854 | -117.6727 | -15.1245 | -0.064087 | -0.85144 | -0.44403 | 4.5685 | -118.2953 | -0.16937 | 0.086975 | 75.4669 | 0.34332 | -19.5099 | -0.27924 | 0.18311 | 75.6363 | 117.1646 | 117.572 | 102.8915 | 122.4884 | 75.4669 | 122.5845 | 117.952 | -0.27924 | 122.4884 | 75.4669 | 117.952 | 102.8915 | 122.5845 | -122.5708 | -122.6807
1546.4219 | 122.3282 | -118.0573 | 4.1519 | 0.012131 | 0.01581 | 4.4166 | -0.0085769 | 0.060541 | -0.00023497 | 0.095269 | -14.653 | 4.2572 | -118.0023 | -117.9245 | -8.6517 | 0.045776 | -0.99335 | -0.31128 | 4.2755 | -118.3685 | 0.054932 | 0.10529 | 103.4042 | 0.13275 | -12.8037 | -0.31128 | 0.1236 | 103.3493 | 117.0639 | 117.746 | 109.4055 | 122.3145 | 103.4042 | 122.3328 | 118.103 | -0.31128 | 122.3145 | 103.4042 | 118.103 | 109.4055 | 122.3328 | -122.1542 | -122.5204
1548.1562 | 122.1268 | -118.3411 | 3.7811 | -0.0031279 | 0.01581 | 4.3538 | -0.0043045 | 0.059045 | -0.00087577 | 0.15807 | -13.0875 | 3.8132 | -118.4509 | -117.8467 | -7.3654 | -0.022888 | -0.85144 | -0.52185 | 3.8452 | -118.7256 | -0.10986 | 0.032043 | 105.2536 | 0.49438 | -11.1465 | -0.38452 | 0.064087 | 105.3635 | 117.4896 | 117.8192 | 110.9756 | 122.1542 | 105.2536 | 122.1863 | 118.3182 | -0.38452 | 122.1542 | 105.2536 | 118.3182 | 110.9756 | 122.1863 | -122.2321 | -122.5067
1549.8438 | 122.1634 | -118.4967 | 3.479 | -0.010757 | 0.014315 | 4.2704 | -0.010713 | 0.058832 | -0.00023497 | 0.099115 | -12.2589 | 3.6118 | -118.5974 | -118.5104 | -6.7154 | -0.059509 | -0.82855 | -0.41199 | 3.653 | -118.895 | -0.10071 | 0.13275 | 106.2378 | -0.013733 | -10.1944 | -0.39825 | 0.17395 | 106.3385 | 117.6682 | 118.0847 | 111.7813 | 122.1085 | 106.2378 | 122.1497 | 118.4372 | -0.39825 | 122.1085 | 106.2378 | 118.4372 | 111.7813 | 122.1497 | -122.0764 | -122.374
1551.5938 | 121.9757 | -118.6386 | 3.4287 | 0.012131 | 0.016024 | 4.1722 | -0.0049453 | 0.059686 | -2.1368e-05 | 0.099115 | -11.554 | 3.4836 | -118.6752 | -118.515 | -6.2485 | -0.009155 | -0.89722 | -0.3891 | 3.5431 | -118.9636 | -0.036621 | 0.054932 | 107.0847 | 0.1236 | -9.6771 | -0.32501 | 0.11444 | 107.1213 | 117.7414 | 118.2495 | 112.3901 | 122.1222 | 107.0847 | 122.1817 | 118.6295 | -0.32501 | 122.1222 | 107.0847 | 118.6295 | 112.3901 | 122.1817 | -122.1039 | -122.3923
1553.3594 | 122.0078 | -118.515 | 3.4882 | -0.0031279 | 0.01581 | 4.0739 | -0.0090041 | 0.058832 | 0.001474 | 0.15551 | -11.1099 | 3.5385 | -118.5059 | -118.4006 | -5.8273 | 0.059509 | -1.0391 | -0.38452 | 3.5706 | -118.84 | 0.009156 | 0.050354 | 107.4051 | 0.11444 | -9.3155 | -0.32501 | 0.082398 | 107.3959 | 117.4759 | 118.1305 | 112.6877 | 122.0535 | 107.4051 | 122.0856 | 118.5745 | -0.32501 | 122.0535 | 107.4051 | 118.5745 | 112.6877 | 122.0856 | -121.994 | -122.3282
1555.1094 | 122.081 | -118.5837 | 3.3371 | 0.01976 | 0.013888 | 3.9791 | -0.0098587 | 0.058618 | 0.0012604 | 0.10104 | -10.881 | 3.4058 | -118.689 | -118.5287 | -5.6305 | 0.032043 | -0.88806 | -0.36163 | 3.4744 | -118.9453 | -0.10529 | 0.068665 | 107.7026 | 0.054931 | -8.9676 | -0.36163 | 0.13733 | 107.8079 | 117.6956 | 118.222 | 112.9532 | 121.9894 | 107.7026 | 122.0581 | 118.6157 | -0.36163 | 121.9894 | 107.7026 | 118.6157 | 112.9532 | 122.0581 | -122.0261 | -122.2824
1556.8125 | 122.0261 | -117.2745 | 4.5868 | 0.0045011 | 0.022219 | 3.8656 | -0.0094315 | 0.058618 | -0.0030122 | 0.16342 | -10.2173 | 4.66 | -117.366 | -117.16 | -5.2872 | 0.064087 | -1.2634 | -0.38452 | 4.6875 | -117.6453 | -0.091553 | 0.073242 | 107.0572 | 0.11444 | -9.874 | -0.37079 | 0.10071 | 107.1487 | 116.011 | 116.89 | 111.9873 | 121.9345 | 107.0572 | 121.962 | 117.3386 | -0.37079 | 121.9345 | 107.0572 | 117.3386 | 111.9873 | 121.962 | -121.9528 | -122.2321
1558.5625 | 122.0078 | -118.1717 | 3.6896 | -0.0031279 | 0.016238 | 3.8086 | -0.011141 | 0.059473 | -0.00023497 | 0.1004 | -10.2264 | 3.7674 | -118.2404 | -118.071 | -5.0858 | 0.073242 | -1.3 | -0.40741 | 3.804 | -118.5196 | -0.068664 | 0.07782 | 107.9453 | 0.10071 | -8.7753 | -0.3479 | 0.11444 | 108.0139 | 116.8716 | 117.7643 | 113.0859 | 121.9391 | 107.9453 | 121.9757 | 118.2449 | -0.3479 | 121.9391 | 107.9453 | 118.2449 | 113.0859 | 121.9757 | -121.9299 | -122.2092
1560.3125 | 122.0123 | -118.0573 | 3.7399 | 0.0045011 | 0.017733 | 3.7366 | -0.0055863 | 0.060114 | -0.0013032 | 0.099542 | -10.0433 | 3.8864 | -118.2266 | -118.0618 | -4.9896 | -0.050354 | -1.1078 | -0.54474 | 3.923 | -118.4509 | -0.16937 | 0.14648 | 108.0139 | -0.004578 | -8.7296 | -0.39368 | 0.18311 | 108.1833 | 116.9495 | 117.5125 | 113.0676 | 121.9437 | 108.0139 | 121.9803 | 118.0069 | -0.39368 | 121.9437 | 108.0139 | 118.0069 | 113.0676 | 121.9803 | -121.9666 | -122.1909
1562.0156 | 121.875 | -118.0573 | 3.804 | -0.0031279 | 0.014956 | 3.674 | -0.0040909 | 0.061182 | -0.0038666 | 0.11086 | -9.7366 | 3.8773 | -118.19 | -117.9794 | -4.8935 | -0.013733 | -1.2955 | -0.59967 | 3.9093 | -118.3914 | -0.13275 | 0.073242 | 108.3206 | 0.07782 | -8.6975 | -0.33417 | 0.10529 | 108.4534 | 116.7618 | 117.4576 | 113.1638 | 121.9345 | 108.3206 | 121.9666 | 118.0435 | -0.33417 | 121.9345 | 108.3206 | 118.0435 | 113.1638 | 121.9666 | -121.994 | -122.1954
1563.7656 | 121.9162 | -118.2266 | 3.6072 | 0.0045011 | 0.016238 | 3.6161 | -0.0064407 | 0.059686 | -0.0017304 | 0.10061 | -9.613 | 3.7079 | -118.3594 | -118.1442 | -4.8614 | -0.018311 | -1.2817 | -0.59052 | 3.7537 | -118.5333 | -0.13275 | 0.10071 | 108.6136 | 0.082398 | -8.4686 | -0.3067 | 0.14648 | 108.7463 | 116.9449 | 117.6361 | 113.3652 | 121.9345 | 108.6136 | 121.9803 | 118.2083 | -0.3067 | 121.9345 | 108.6136 | 118.2083 | 113.3652 | 121.9803 | -121.9666 | -122.1405
1565.5312 | 121.9894 | -2.0096 | 119.989 | 0.012131 | 0.014956 | 0.066127 | -0.015199 | 0.059045 | 0.061502 | 0.10424 | -0.16937 | 120.163 | -2.3529 | -1.6663 | -0.027466 | 0.17395 | 0.036621 | 0.35706 | 120.2271 | -2.298 | -0.34332 | 0.17395 | 1.8402 | 0.34332 | -120.0165 | -0.28839 | 0.23804 | 2.1835 | 2.0462 | 2.3666 | 1.9821 | 122.1725 | 1.8402 | 122.2366 | 2.1835 | -0.28839 | 122.1725 | 1.8402 | 2.1835 | 1.9821 | 122.2366 | -122.3419 | -122.287
1567.2344 | 122.0535 | -2.3392 | 119.8151 | 0.0045011 | 0.017733 | 0.076381 | -0.0034499 | 0.062036 | 0.060861 | 0.096124 | -0.31586 | 120.0119 | -2.6871 | -2.092 | -0.18768 | 0.036621 | 0.15564 | 0.1831 | 120.1172 | -2.6001 | -0.3479 | 0.19684 | 2.0233 | 0.24719 | -120.0027 | -0.26093 | 0.30212 | 2.3712 | 2.4948 | 2.5223 | 2.1515 | 122.3511 | 2.0233 | 122.4564 | 2.3758 | -0.26093 | 122.3511 | 2.0233 | 2.3758 | 2.1515 | 122.4564 | -122.5021 | -122.4152
1569 | 122.1863 | -2.4719 | 119.6594 | -0.0031279 | 0.015597 | 0.075099 | -0.011995 | 0.05755 | 0.061288 | 0.090997 | -0.34332 | 119.87 | -2.8061 | -2.1881 | -0.10986 | 0.11902 | 0.050354 | 0.2655 | 119.9112 | -2.7695 | -0.33417 | 0.21057 | 2.1286 | 0.28381 | -119.7693 | -0.29755 | 0.25177 | 2.4628 | 2.5223 | 2.7374 | 2.3621 | 122.3419 | 2.1286 | 122.3831 | 2.5909 | -0.29755 | 122.3419 | 2.1286 | 2.5909 | 2.3621 | 122.3831 | -122.4655 | -122.4289
1570.6719 | 122.2092 | -2.4948 | 119.6594 | 0.012131 | 0.016238 | 0.075526 | -0.0072953 | 0.057123 | 0.061929 | 0.089502 | -0.3891 | 119.9066 | -2.8564 | -2.2614 | -0.20142 | 0.032043 | 0.21973 | 0.21515 | 119.9707 | -2.7969 | -0.36163 | 0.24719 | 2.1057 | 0.23346 | -119.8608 | -0.30212 | 0.31128 | 2.4673 | 2.7145 | 2.71 | 2.2934 | 122.4014 | 2.1057 | 122.4655 | 2.5269 | -0.30212 | 122.4014 | 2.1057 | 2.5269 | 2.2934 | 122.4655 | -122.5159 | -122.4564
1572.4219 | 122.1954 | -2.5223 | 119.6274 | -0.0031279 | 0.016024 | 0.07809 | -0.0105 | 0.057123 | 0.063425 | 0.090783 | -0.33875 | 119.8975 | -2.8702 | -2.1881 | -0.091553 | 0.16479 | 0.032043 | 0.32501 | 119.9158 | -2.7969 | -0.3479 | 0.27008 | 2.1835 | 0.33417 | -119.7189 | -0.27466 | 0.28839 | 2.5314 | 2.5543 | 2.8473 | 2.4307 | 122.4197 | 2.1835 | 122.438 | 2.6871 | -0.27466 | 122.4197 | 2.1835 | 2.6871 | 2.4307 | 122.438 | -122.4976 | -122.4243
1574.1562 | 122.2229 | -2.5177 | 119.6503 | 0.012131 | 0.018801 | 0.078731 | -0.0053727 | 0.058191 | 0.06022 | 0.092492 | -0.3891 | 119.9387 | -2.8656 | -2.2568 | -0.19226 | 0.027466 | 0.19684 | 0.21057 | 119.9478 | -2.8152 | -0.3479 | 0.28839 | 2.1286 | 0.26092 | -119.8425 | -0.29755 | 0.29755 | 2.4765 | 2.7145 | 2.7283 | 2.3254 | 122.4564 | 2.1286 | 122.4655 | 2.5452 | -0.29755 | 122.4564 | 2.1286 | 2.5452 | 2.3254 | 122.4655 | -122.5159 | -122.4655
1575.8438 | 122.1863 | -2.449 | 119.7052 | 0.012131 | 0.015169 | 0.074885 | -0.0090041 | 0.058405 | 0.058939 | 0.091211 | -0.29755 | 119.957 | -2.7557 | -2.0874 | -0.059509 | 0.16937 | 0.009155 | 0.36163 | 120.0027 | -2.7145 | -0.3067 | 0.25177 | 2.1515 | 0.36163 | -119.7647 | -0.2655 | 0.29755 | 2.4582 | 2.4582 | 2.8107 | 2.3895 | 122.406 | 2.1515 | 122.4518 | 2.6184 | -0.2655 | 122.406 | 2.1515 | 2.6184 | 2.3895 | 122.4518 | -122.4609 | -122.4197
1577.6094 | 122.168 | -2.4536 | 119.7601 | 0.0045011 | 0.020724 | 0.081294 | -0.00024572 | 0.0599 | 0.060861 | 0.091211 | -0.36621 | 119.989 | -2.829 | -2.2247 | -0.20142 | 0.018311 | 0.1236 | 0.17395 | 120.076 | -2.7557 | -0.37537 | 0.22888 | 2.0874 | 0.22888 | -119.9615 | -0.30212 | 0.31586 | 2.4628 | 2.5772 | 2.6276 | 2.2522 | 122.4426 | 2.0874 | 122.5296 | 2.4719 | -0.30212 | 122.4426 | 2.0874 | 2.4719 | 2.2522 | 122.5296 | -122.5891 | -122.5159
1579.2969 | 122.1725 | -2.4536 | 119.7693 | 0.012131 | 0.017306 | 0.079372 | -0.0017411 | 0.060541 | 0.05787 | 0.09356 | -0.37079 | 120.0073 | -2.7603 | -2.1927 | -0.20142 | 0.013733 | 0.16479 | 0.16022 | 120.108 | -2.7054 | -0.3067 | 0.23804 | 2.0828 | 0.26092 | -119.9707 | -0.25177 | 0.33874 | 2.3895 | 2.6184 | 2.6138 | 2.2522 | 122.4609 | 2.0828 | 122.5616 | 2.4673 | -0.25177 | 122.4609 | 2.0828 | 2.4673 | 2.2522 | 122.5616 | -122.5296 | -122.4747
1581.0312 | 122.2 | -2.4124 | 119.7739 | -0.0031279 | 0.018374 | 0.077449 | -0.0094315 | 0.0599 | 0.061929 | 0.095697 | -0.28381 | 120.0485 | -2.7283 | -2.1011 | -0.082397 | 0.13275 | 0.027466 | 0.27008 | 120.0989 | -2.655 | -0.31586 | 0.27466 | 2.1286 | 0.31128 | -119.8563 | -0.24261 | 0.32501 | 2.4445 | 2.4399 | 2.6825 | 2.33 | 122.4609 | 2.1286 | 122.5113 | 2.5452 | -0.24261 | 122.4609 | 2.1286 | 2.5452 | 2.33 | 122.5113 | -122.5021 | -122.4289
1582.7812 | 122.2504 | -2.3712 | 119.7739 | 0.0045011 | 0.016665 | 0.077022 | -0.0043045 | 0.060541 | 0.059579 | 0.094842 | -0.36163 | 120.0668 | -2.7512 | -2.1378 | -0.15106 | 0.036621 | 0.21973 | 0.21515 | 120.1492 | -2.6596 | -0.37994 | 0.29297 | 2.0096 | 0.23346 | -119.9249 | -0.28839 | 0.37537 | 2.3895 | 2.5909 | 2.5864 | 2.2202 | 122.438 | 2.0096 | 122.5204 | 2.4078 | -0.28839 | 122.438 | 2.0096 | 2.4078 | 2.2202 | 122.5204 | -122.525 | -122.4335
1584.4844 | 122.2092 | -2.3712 | 119.8013 | 0.0045011 | 0.013674 | 0.074245 | -0.0079361 | 0.059259 | 0.058511 | 0.093133 | -0.21057 | 120.0577 | -2.6688 | -1.9867 | -0.013733 | 0.17853 | 0 | 0.35706 | 120.1309 | -2.6321 | -0.29755 | 0.25635 | 2.1606 | 0.38452 | -119.8151 | -0.26092 | 0.32959 | 2.4582 | 2.3712 | 2.7283 | 2.3575 | 122.4289 | 2.1606 | 122.5021 | 2.5497 | -0.26092 | 122.4289 | 2.1606 | 2.5497 | 2.3575 | 122.5021 | -122.4701 | -122.4335
1586.25 | 122.2046 | -2.3987 | 119.7693 | -0.0031279 | 0.015383 | 0.070827 | -0.0072953 | 0.060968 | 0.061502 | 0.091638 | -0.2243 | 120.0439 | -2.7054 | -2.0096 | -0.018311 | 0.18768 | 0.018311 | 0.37994 | 120.0943 | -2.6276 | -0.3067 | 0.27466 | 2.1744 | 0.3891 | -119.7876 | -0.22888 | 0.32501 | 2.4811 | 2.417 | 2.7786 | 2.3804 | 122.4426 | 2.1744 | 122.493 | 2.5864 | -0.22888 | 122.4426 | 2.1744 | 2.5864 | 2.3804 | 122.493 | -122.4747 | -122.3969
1588 | 122.1268 | -2.4307 | 119.7922 | -0.0031279 | 0.014956 | 0.079799 | -0.0038773 | 0.063532 | 0.058725 | 0.092706 | -0.22888 | 120.0531 | -2.7054 | -2.037 | -0.054932 | 0.16022 | -0.036621 | 0.29297 | 120.108 | -2.623 | -0.27466 | 0.26093 | 2.2018 | 0.39368 | -119.8471 | -0.19226 | 0.31586 | 2.4765 | 2.3941 | 2.7237 | 2.3758 | 122.4838 | 2.2018 | 122.5388 | 2.5909 | -0.19226 | 122.4838 | 2.2018 | 2.5909 | 2.3758 | 122.5388 | -122.4976 | -122.4152
1589.6875 | 122.2641 | -2.3712 | 119.7968 | 0.0045011 | 0.017947 | 0.076594 | -0.0060135 | 0.058618 | 0.058939 | 0.091424 | -0.33875 | 120.0485 | -2.7557 | -2.1286 | -0.14648 | 0.036621 | 0.20142 | 0.21057 | 120.1355 | -2.7008 | -0.38452 | 0.25177 | 2.0325 | 0.24261 | -119.9432 | -0.32959 | 0.33875 | 2.417 | 2.5726 | 2.5818 | 2.2247 | 122.4197 | 2.0325 | 122.5067 | 2.4078 | -0.32959 | 122.4197 | 2.0325 | 2.4078 | 2.2247 | 122.5067 | -122.5525 | -122.4976
1591.4375 | 122.1725 | -2.4765 | 119.7601 | -0.0031279 | 0.017733 | 0.083003 | -0.0023819 | 0.060541 | 0.059366 | 0.091211 | -0.34332 | 120.0211 | -2.7786 | -2.1973 | -0.18768 | 0.022888 | 0.15564 | 0.1831 | 120.1035 | -2.7145 | -0.30212 | 0.26093 | 2.1332 | 0.27923 | -119.9478 | -0.23804 | 0.34332 | 2.4353 | 2.6321 | 2.6596 | 2.2888 | 122.4976 | 2.1332 | 122.58 | 2.4994 | -0.23804 | 122.4976 | 2.1332 | 2.4994 | 2.2888 | 122.58 | -122.5388 | -122.4747
1593.1875 | 122.2366 | -2.4353 | 119.7372 | -0.0031279 | 0.015169 | 0.078303 | -0.0072953 | 0.059473 | 0.061716 | 0.091424 | -0.22888 | 120.0165 | -2.7145 | -2.0645 | -0.036621 | 0.18768 | 0.022888 | 0.38452 | 120.0485 | -2.6825 | -0.27924 | 0.27923 | 2.2064 | 0.37079 | -119.7739 | -0.24719 | 0.31128 | 2.4857 | 2.4582 | 2.8198 | 2.3987 | 122.4518 | 2.2064 | 122.4838 | 2.623 | -0.24719 | 122.4518 | 2.2064 | 2.623 | 2.3987 | 122.4838 | -122.4518 | -122.4197
1594.9219 | 122.1909 | -2.4445 | 119.7922 | 0.0045011 | 0.017519 | 0.083217 | -0.0036637 | 0.060541 | 0.059152 | 0.09057 | -0.33875 | 120.0668 | -2.7786 | -2.179 | -0.17395 | 0.041199 | 0.16022 | 0.1831 | 120.1172 | -2.6962 | -0.33417 | 0.27466 | 2.1057 | 0.2655 | -119.9661 | -0.25177 | 0.32501 | 2.4399 | 2.6047 | 2.6276 | 2.2705 | 122.5113 | 2.1057 | 122.5616 | 2.4857 | -0.25177 | 122.5113 | 2.1057 | 2.4857 | 2.2705 | 122.5616 | -122.5708 | -122.4884
1596.6875 | 122.1771 | -2.4628 | 119.7601 | 0.0045011 | 0.01816 | 0.076808 | -0.0066543 | 0.061182 | 0.059579 | 0.091638 | -0.37994 | 120.0119 | -2.8107 | -2.1973 | -0.15106 | 0.059509 | 0.10529 | 0.20599 | 120.0623 | -2.7374 | -0.3479 | 0.25177 | 2.0828 | 0.2655 | -119.9112 | -0.27466 | 0.30212 | 2.4307 | 2.5681 | 2.6688 | 2.3117 | 122.4747 | 2.0828 | 122.525 | 2.5223 | -0.27466 | 122.4747 | 2.0828 | 2.5223 | 2.3117 | 122.525 | -122.5708 | -122.4976
1598.375 | 122.2458 | -2.4078 | 119.8105 | -0.010757 | 0.016878 | 0.079585 | -0.0032363 | 0.05755 | 0.060648 | 0.091851 | -0.33875 | 120.076 | -2.7649 | -2.1378 | -0.14191 | 0.059509 | 0.18768 | 0.26093 | 120.0897 | -2.6871 | -0.35706 | 0.2655 | 2.0691 | 0.27008 | -119.9524 | -0.27924 | 0.27924 | 2.4261 | 2.5955 | 2.6688 | 2.2659 | 122.4838 | 2.0691 | 122.4976 | 2.4673 | -0.27924 | 122.4838 | 2.0691 | 2.4673 | 2.2659 | 122.4976 | -122.5754 | -122.4976
1600.1094 | 122.1863 | -2.4399 | 119.8288 | 0.0045011 | 0.017733 | 0.077235 | -0.0030227 | 0.060754 | 0.059579 | 0.093347 | -0.3479 | 120.0165 | -2.774 | -2.1835 | -0.17853 | 0.027466 | 0.15564 | 0.1831 | 120.1309 | -2.7054 | -0.33417 | 0.18768 | 2.092 | 0.25635 | -120.0073 | -0.2655 | 0.30212 | 2.4261 | 2.5955 | 2.623 | 2.2614 | 122.4564 | 2.092 | 122.5708 | 2.4673 | -0.2655 | 122.4564 | 2.092 | 2.4673 | 2.2614 | 122.5708 | -122.6028 | -122.5342
1601.875 | 122.1405 | -2.4445 | 119.8151 | 0.0045011 | 0.016451 | 0.080226 | -0.0062271 | 0.060541 | 0.063211 | 0.093347 | -0.30212 | 120.0577 | -2.742 | -2.1103 | -0.082397 | 0.1236 | 0.018311 | 0.29297 | 120.0623 | -2.6688 | -0.29755 | 0.24262 | 2.1423 | 0.33417 | -119.8975 | -0.2243 | 0.24719 | 2.4399 | 2.4628 | 2.7374 | 2.3621 | 122.5021 | 2.1423 | 122.5067 | 2.5681 | -0.2243 | 122.5021 | 2.1423 | 2.5681 | 2.3621 | 122.5067 | -122.5571 | -122.4838
1603.5625 | 122.0856 | -68.4998 | 53.7598 | 0.0045011 | 1.6906 | 0.0013993 | -0.014345 | 0.058832 | 0.025186 | 1.7716 | 8.8898 | 56.4056 | 8.5144 | -61.6837 | 6.4957 | 0.10986 | -0.53101 | 0.29755 | 59.8389 | -62.439 | 77.0142 | 2.6459 | 77.3895 | 6.8161 | -47.2641 | 6.0608 | 6.0791 | 0.37537 | 67.9688 | 68.7973 | 74.9954 | 124.9054 | 77.3895 | 128.3386 | 68.6096 | 6.0608 | 124.9054 | 77.3895 | 68.6096 | 74.9954 | 128.3386 | -45.2454 | -116.1987
1605.3125 | 121.9986 | -111.2823 | 10.4416 | -0.0031279 | 0.70859 | 0.0067399 | -0.0068679 | 0.060541 | 0.0051056 | 0.76071 | 3.566 | 20.3293 | 8.1253 | -100.2365 | 2.5864 | -1.1536 | -1.4603 | 0.21057 | 21.0526 | -101.6281 | 119.4077 | 9.8877 | 114.8483 | 11.0458 | -7.8552 | 9.6542 | 10.611 | -4.5593 | 109.8221 | 111.4929 | 113.8687 | 131.6116 | 114.8483 | 132.3349 | 110.1288 | 9.6542 | 131.6116 | 114.8483 | 110.1288 | 113.8687 | 132.3349 | -2.3163 | -112.0697
1607.0781 | 122.1039 | -0.74158 | 120.6894 | 0.0045011 | 0.088869 | 0.0041763 | -0.01349 | 0.04281 | 0.062143 | 0.22814 | -0.27008 | 121.5912 | 8.4961 | 25.3693 | -0.31586 | -0.32501 | 0.44403 | 0.47607 | 121.669 | -0.98419 | 9.2377 | 0.9018 | 0.4715 | 26.1108 | -121.0052 | -0.24261 | 0.97961 | -8.7662 | 1.1856 | 1.2177 | 0.42572 | 122.3328 | 0.4715 | 122.4106 | 0.41657 | -0.24261 | 122.3328 | 0.4715 | 0.41657 | 0.42572 | 122.4106 | -112.1933 | -121.6736
1608.8281 | 122.1588 | -0.79651 | 121.2936 | 0.012131 | 0.088229 | 0.00075827 | -0.0094315 | 0.050287 | 0.059579 | 0.23391 | -0.3891 | 121.5454 | 8.5007 | 13.9618 | -0.44403 | -0.44403 | 0.31586 | 0.42572 | 121.6003 | -1.0757 | 9.2972 | 0.25177 | 0.40741 | 14.7583 | -121.7377 | -0.27924 | 0.3067 | -8.8898 | 1.1124 | 1.2222 | 0.35248 | 122.3419 | 0.40741 | 122.3969 | 0.35248 | -0.27924 | 122.3419 | 0.40741 | 0.35248 | 0.35248 | 122.3969 | -112.793 | -122.3694
1610.5156 | 122.0261 | -0.88806 | 121.3074 | 0.01976 | 0.093355 | 0.0041763 | -0.0028091 | 0.051782 | 0.058725 | 0.23242 | -0.33875 | 121.55 | 8.5007 | 13.385 | -0.50812 | -0.48523 | 0.38452 | 0.3891 | 121.6553 | -1.0803 | 9.3887 | 0.24262 | 0.54932 | 14.2731 | -121.8155 | -0.19226 | 0.3479 | -8.8394 | 1.2726 | 1.2772 | 0.37994 | 122.4381 | 0.54932 | 122.5433 | 0.40283 | -0.19226 | 122.4381 | 0.54932 | 0.40283 | 0.37994 | 122.5433 | -112.8067 | -122.3877
1612.2812 | 122.1268 | -0.83313 | 121.2845 | -0.0031279 | 0.08716 | -9.6132e-05 | -0.0077225 | 0.048792 | 0.061075 | 0.2322 | -0.31586 | 121.5408 | 8.5052 | 12.8357 | -0.40741 | -0.40283 | 0.25177 | 0.49896 | 121.5775 | -1.0483 | 9.3384 | 0.25635 | 0.51727 | 13.6688 | -121.6919 | -0.21515 | 0.29297 | -8.8211 | 1.0849 | 1.3321 | 0.42572 | 122.374 | 0.51727 | 122.4106 | 0.4303 | -0.21515 | 122.374 | 0.51727 | 0.4303 | 0.42572 | 122.4106 | -112.7792 | -122.3328
1614.0312 | 122.1359 | -0.87891 | 121.2799 | 0.012131 | 0.089724 | 0.0024673 | -0.010072 | 0.05285 | 0.062357 | 0.23434 | -0.33875 | 121.4951 | 8.5098 | 8.9722 | -0.43488 | -0.42572 | 0.21973 | 0.47607 | 121.5637 | -1.1032 | 9.3887 | 0.21515 | 0.54016 | 9.8511 | -121.7148 | -0.2243 | 0.28381 | -8.8486 | 1.0986 | 1.355 | 0.44403 | 122.374 | 0.54016 | 122.4426 | 0.45319 | -0.2243 | 122.374 | 0.54016 | 0.45319 | 0.44403 | 122.4426 | -112.7701 | -122.3831
1615.7188 | 122.113 | -0.86517 | 121.3074 | 0.0045011 | 0.089083 | 0.0043899 | -0.0028091 | 0.055414 | 0.062143 | 0.23519 | -0.4303 | 121.582 | 8.5052 | 8.2901 | -0.57678 | -0.5722 | 0.32959 | 0.28381 | 121.6599 | -1.1078 | 9.3704 | 0.27466 | 0.43487 | 9.1553 | -121.8842 | -0.24262 | 0.35248 | -8.9355 | 1.1948 | 1.149 | 0.28839 | 122.4472 | 0.43487 | 122.525 | 0.29297 | -0.24262 | 122.4472 | 0.43487 | 0.29297 | 0.28839 | 122.525 | -112.8021 | -122.4152
1617.5 | 122.0947 | -0.85144 | 121.3486 | 0.0045011 | 0.087374 | 0.0063125 | -0.00067292 | 0.05755 | 0.059152 | 0.23455 | -0.40741 | 121.5729 | 8.5007 | 7.5851 | -0.52643 | -0.53101 | 0.28839 | 0.28839 | 121.6553 | -1.0757 | 9.3521 | 0.2243 | 0.44403 | 8.4366 | -121.875 | -0.2243 | 0.3067 | -8.9081 | 1.1398 | 1.1398 | 0.32501 | 122.4243 | 0.44403 | 122.5067 | 0.32043 | -0.2243 | 122.4243 | 0.44403 | 0.32043 | 0.32501 | 122.5067 | -112.8479 | -122.4243
1619.2031 | 122.0947 | -0.85144 | 121.3394 | -0.0031279 | 0.088015 | -0.00095053 | -0.0043045 | 0.054559 | 0.059793 | 0.23391 | -0.40283 | 121.5958 | 8.5052 | 7.3746 | -0.53558 | -0.51727 | 0.25177 | 0.31586 | 121.6507 | -1.0757 | 9.3567 | 0.25635 | 0.44861 | 8.226 | -121.875 | -0.2243 | 0.31128 | -8.9081 | 1.1032 | 1.1673 | 0.31586 | 122.4472 | 0.44861 | 122.5021 | 0.33417 | -0.2243 | 122.4472 | 0.44861 | 0.33417 | 0.31586 | 122.5021 | -112.8342 | -122.4152
1620.9375 | 122.1954 | -0.82855 | 121.2891 | -0.0031279 | 0.083102 | 0.0037491 | -0.011141 | 0.055414 | 0.06022 | 0.2337 | -0.40741 | 121.5317 | 8.5052 | 7.3425 | -0.47607 | -0.46692 | 0.21515 | 0.39368 | 121.6095 | -1.0849 | 9.3338 | 0.24262 | 0.42114 | 8.1711 | -121.7651 | -0.25635 | 0.32044 | -8.9127 | 1.0437 | 1.2222 | 0.35248 | 122.3602 | 0.42114 | 122.438 | 0.36163 | -0.25635 | 122.3602 | 0.42114 | 0.36163 | 0.35248 | 122.438 | -112.7838 | -122.374
1622.625 | 122.1497 | -0.84228 | 121.2936 | 0.012131 | 0.084383 | 0.0063125 | -0.0051589 | 0.054773 | 0.058725 | 0.23306 | -0.40741 | 121.5591 | 8.5052 | 7.2784 | -0.51727 | -0.53101 | 0.32044 | 0.36621 | 121.6415 | -1.0986 | 9.3475 | 0.2655 | 0.43487 | 8.1207 | -121.8109 | -0.25635 | 0.3479 | -8.9127 | 1.1627 | 1.2085 | 0.32501 | 122.4014 | 0.43487 | 122.4838 | 0.31128 | -0.25635 | 122.4014 | 0.43487 | 0.31128 | 0.32501 | 122.4838 | -112.7884 | -122.3923
1624.3906 | 122.081 | -0.87891 | 121.3303 | -0.0031279 | 0.084811 | 0.0048173 | -0.0077225 | 0.054987 | 0.06022 | 0.23412 | -0.33417 | 121.5408 | 8.5098 | 7.1228 | -0.43945 | -0.43945 | 0.15106 | 0.42114 | 121.582 | -1.0849 | 9.3887 | 0.21057 | 0.54474 | 8.0017 | -121.7697 | -0.20599 | 0.25177 | -8.844 | 1.03 | 1.3 | 0.43945 | 122.4197 | 0.54474 | 122.4609 | 0.43945 | -0.20599 | 122.4197 | 0.54474 | 0.43945 | 0.43945 | 122.4609 | -112.8204 | -122.4152
1626.125 | 122.1405 | -0.82855 | 121.3028 | -0.010757 | 0.088656 | 0.0050309 | -0.0070815 | 0.057123 | 0.063852 | 0.23562 | -0.36621 | 121.5546 | 8.5144 | 7.0404 | -0.49896 | -0.47607 | 0.19684 | 0.39368 | 121.5958 | -1.0757 | 9.343 | 0.25177 | 0.46234 | 7.869 | -121.8018 | -0.24719 | 0.29297 | -8.8806 | 1.0254 | 1.2222 | 0.32959 | 122.3831 | 0.46234 | 122.4243 | 0.35248 | -0.24719 | 122.3831 | 0.46234 | 0.35248 | 0.32959 | 122.4243 | -112.7884 | -122.3785
1627.875 | 122.1405 | -0.83771 | 121.2799 | -0.010757 | 0.082888 | 0.0016129 | -0.0079361 | 0.0552 | 0.063211 | 0.23092 | -0.33417 | 121.5363 | 8.5144 | 7.0129 | -0.4303 | -0.43488 | 0.15564 | 0.48065 | 121.5591 | -1.0941 | 9.3521 | 0.25635 | 0.50354 | 7.8506 | -121.7102 | -0.25635 | 0.27924 | -8.8486 | 0.99335 | 1.3184 | 0.40741 | 122.374 | 0.50354 | 122.3969 | 0.40283 | -0.25635 | 122.374 | 0.50354 | 0.40283 | 0.40741 | 122.3969 | -112.7655 | -122.374
1629.625 | 122.1405 | -0.88806 | 121.2662 | -0.0031279 | 0.085238 | 0.0078079 | -0.0051589 | 0.054346 | 0.063211 | 0.23412 | -0.35706 | 121.4951 | 8.5098 | 6.9397 | -0.46234 | -0.48065 | 0.23804 | 0.44861 | 121.5546 | -1.1078 | 9.3979 | 0.22888 | 0.53101 | 7.8278 | -121.7285 | -0.21973 | 0.28839 | -8.8669 | 1.1261 | 1.3367 | 0.42572 | 122.3831 | 0.53101 | 122.4426 | 0.40741 | -0.21973 | 122.3831 | 0.53101 | 0.40741 | 0.42572 | 122.4426 | -112.7563 | -122.374
1631.3125 | 122.113 | -0.89722 | 121.2845 | -0.010757 | 0.088656 | 0.0054581 | -0.0021683 | 0.055414 | 0.062784 | 0.23348 | -0.43945 | 121.5179 | 8.5007 | 6.6742 | -0.56763 | -0.5722 | 0.26093 | 0.31128 | 121.6095 | -1.1444 | 9.3979 | 0.23346 | 0.45776 | 7.5714 | -121.8521 | -0.24719 | 0.32501 | -8.9401 | 1.1581 | 1.2085 | 0.32959 | 122.4152 | 0.45776 | 122.5067 | 0.32501 | -0.24719 | 122.4152 | 0.45776 | 0.32501 | 0.32959 | 122.5067 | -112.7838 | -122.4289
1633.0781 | 122.1405 | -0.88348 | 121.2753 | 0.012131 | 0.086092 | 0.0069535 | -0.0038773 | 0.056696 | 0.059793 | 0.23348 | -0.4303 | 121.5179 | 8.5007 | 6.8207 | -0.53101 | -0.53558 | 0.34332 | 0.36621 | 121.5912 | -1.1215 | 9.3842 | 0.24261 | 0.45319 | 7.7042 | -121.8063 | -0.23804 | 0.31586 | -8.931 | 1.2268 | 1.2497 | 0.35248 | 122.4014 | 0.45319 | 122.4747 | 0.3479 | -0.23804 | 122.4014 | 0.45319 | 0.3479 | 0.35248 | 122.4747 | -112.7747 | -122.3969
1634.7656 | 122.0673 | -0.92468 | 121.2708 | -0.0031279 | 0.091647 | 0.0080215 | -0.0036637 | 0.056909 | 0.062357 | 0.24075 | -0.43488 | 121.5225 | 8.5007 | 6.8207 | -0.56763 | -0.57678 | 0.24719 | 0.32959 | 121.55 | -1.149 | 9.4254 | 0.25177 | 0.48981 | 7.7454 | -121.8384 | -0.2243 | 0.27924 | -8.9355 | 1.1719 | 1.2543 | 0.35706 | 122.4472 | 0.48981 | 122.4747 | 0.3479 | -0.2243 | 122.4472 | 0.48981 | 0.3479 | 0.35706 | 122.4747 | -112.7701 | -122.4197
1636.5156 | 122.1405 | -0.88348 | 121.2341 | -0.010757 | 0.091433 | 0.0056717 | -0.0090041 | 0.054346 | 0.063638 | 0.23712 | -0.40741 | 121.4996 | 8.5098 | 6.9534 | -0.46692 | -0.48523 | 0.20142 | 0.48981 | 121.4996 | -1.1444 | 9.3933 | 0.2655 | 0.47607 | 7.8369 | -121.7011 | -0.26092 | 0.2655 | -8.9172 | 1.0849 | 1.3733 | 0.41657 | 122.3831 | 0.47607 | 122.3831 | 0.39826 | -0.26092 | 122.3831 | 0.47607 | 0.39826 | 0.41657 | 122.3831 | -112.7243 | -122.3785
1638.2031 | 122.2183 | -0.89264 | 121.2387 | 0.0045011 | 0.093142 | 0.0052445 | -0.0079361 | 0.052423 | 0.061929 | 0.23797 | -0.41657 | 121.5271 | 8.5144 | 6.7886 | -0.48981 | -0.48981 | 0.24261 | 0.45776 | 121.5683 | -1.1627 | 9.407 | 0.28839 | 0.47607 | 7.6813 | -121.7285 | -0.27008 | 0.32959 | -8.931 | 1.1353 | 1.3504 | 0.40283 | 122.4197 | 0.47607 | 122.4609 | 0.40283 | -0.27008 | 122.4197 | 0.47607 | 0.40283 | 0.40283 | 122.4609 | -112.7243 | -122.4014
1639.9531 | 122.1771 | -1.0483 | 121.1975 | 0.0045011 | 0.10297 | 0.0075943 | -0.0011001 | 0.053491 | 0.058298 | 0.24694 | -0.54016 | 121.4539 | 8.5098 | 7.1686 | -0.66834 | -0.68665 | 0.35706 | 0.37537 | 121.5408 | -1.268 | 9.5581 | 0.25635 | 0.50812 | 8.2169 | -121.8658 | -0.21973 | 0.34332 | -9.05 | 1.4053 | 1.4236 | 0.37994 | 122.5021 | 0.50812 | 122.5891 | 0.36163 | -0.21973 | 122.5021 | 0.50812 | 0.36163 | 0.37994 | 122.5891 | -112.6877 | -122.4655
1641.7031 | 122.168 | -0.93384 | 121.3211 | 0.0045011 | 0.07947 | 0.0071671 | -0.0096451 | 0.057123 | 0.059793 | 0.22729 | -0.40741 | 121.5546 | 8.5144 | 7.338 | -0.52185 | -0.49439 | 0.19684 | 0.42114 | 121.637 | -1.1215 | 9.4482 | 0.23346 | 0.52643 | 8.2718 | -121.843 | -0.18768 | 0.31586 | -8.9218 | 1.1307 | 1.355 | 0.41199 | 122.4884 | 0.52643 | 122.5708 | 0.43945 | -0.18768 | 122.4884 | 0.52643 | 0.43945 | 0.41199 | 122.5708 | -112.8067 | -122.4426
1643.3906 | 122.1863 | -1.236 | 121.0373 | 0.0045011 | 0.12519 | 0.0054581 | -0.0060135 | 0.057123 | 0.060434 | 0.27065 | -0.64545 | 121.2524 | 8.519 | 7.3059 | -0.79193 | -0.7782 | 0.20599 | 0.40283 | 121.3303 | -1.442 | 9.7549 | 0.21515 | 0.59052 | 8.5419 | -121.8292 | -0.20599 | 0.29297 | -9.1644 | 1.442 | 1.6388 | 0.44403 | 122.4884 | 0.59052 | 122.5662 | 0.45776 | -0.20599 | 122.4884 | 0.59052 | 0.45776 | 0.44403 | 122.5662 | -112.5183 | -122.4792
1645.1406 | 122.1909 | -0.94299 | 121.3623 | -0.0031279 | 0.082674 | 0.0028947 | -0.0038773 | 0.05755 | 0.062997 | 0.22579 | -0.35706 | 121.6278 | 8.519 | 7.5348 | -0.49896 | -0.48065 | 0.20599 | 0.40741 | 121.6644 | -1.1169 | 9.462 | 0.2655 | 0.58594 | 8.4778 | -121.8613 | -0.17395 | 0.30212 | -8.876 | 1.149 | 1.3504 | 0.44403 | 122.5708 | 0.58594 | 122.6074 | 0.46234 | -0.17395 | 122.5708 | 0.58594 | 0.46234 | 0.44403 | 122.6074 | -112.8433 | -122.4792
1646.8906 | 122.1634 | -1.2222 | 121.0876 | 0.012131 | 0.1207 | 0.010585 | -0.0057999 | 0.055414 | 0.062143 | 0.26553 | -0.63171 | 121.3074 | 8.5052 | 7.9697 | -0.72784 | -0.73242 | 0.20142 | 0.39368 | 121.3715 | -1.3916 | 9.7275 | 0.21973 | 0.59052 | 9.1919 | -121.8155 | -0.16937 | 0.28381 | -9.137 | 1.4236 | 1.6159 | 0.49438 | 122.5296 | 0.59052 | 122.5937 | 0.48981 | -0.16937 | 122.5296 | 0.59052 | 0.48981 | 0.49438 | 122.5937 | -112.5824 | -122.4792
1648.5781 | 122.2046 | -0.95215 | 121.3898 | 0.0045011 | 0.080752 | 0.0052445 | -0.0062271 | 0.052423 | 0.06257 | 0.22302 | -0.40283 | 121.5866 | 8.5144 | 8.1299 | -0.52643 | -0.52185 | 0.23804 | 0.36621 | 121.6415 | -1.1398 | 9.4666 | 0.19684 | 0.54932 | 9.082 | -121.9162 | -0.18768 | 0.25177 | -8.9172 | 1.1902 | 1.3184 | 0.42572 | 122.5388 | 0.54932 | 122.5937 | 0.4303 | -0.18768 | 122.5388 | 0.54932 | 0.4303 | 0.42572 | 122.5937 | -112.8754 | -122.5296
1650.3125 | 122.3373 | -0.97046 | 121.2433 | 0.012131 | 0.22067 | -0.00095053 | -0.0092179 | 0.052637 | 0.062357 | 0.3655 | -1.3458 | 120.5887 | 8.519 | 8.0246 | -1.4236 | -1.442 | 0.3479 | 0.37537 | 120.6162 | -2.1469 | 9.4894 | -0.6546 | -0.37537 | 8.9951 | -122.6669 | -1.1765 | -0.62714 | -9.8648 | 1.3184 | 1.3458 | -0.45319 | 121.5591 | -0.37537 | 121.5866 | -0.4715 | -1.1765 | 121.5591 | -0.37537 | -0.4715 | -0.45319 | 121.5866 | -112.7243 | -123.3902
1652 | 122.3373 | -1.2863 | 121.0007 | 0.0045011 | 0.085665 | 0.0071671 | -0.0034499 | 0.053919 | 0.062143 | 0.2275 | -0.48065 | 121.6553 | 8.5144 | 7.9971 | -0.63629 | -0.65918 | 0.52643 | 0.30212 | 121.7239 | -1.1353 | 9.8007 | 0.6546 | 0.80566 | 9.2834 | -121.637 | 0.15106 | 0.72327 | -8.9951 | 1.8127 | 1.5884 | 0.65002 | 122.9416 | 0.80566 | 123.0103 | 0.62714 | 0.15106 | 122.9416 | 0.80566 | 0.62714 | 0.65002 | 123.0103 | -112.4863 | -122.1359
1653.75 | 122.2229 | -2.1927 | 120.1263 | -0.0031279 | 0.26041 | 0.0067399 | -0.0011001 | 0.055414 | 0.060861 | 0.40481 | -1.5335 | 120.3461 | 8.5098 | 7.9056 | -1.6983 | -1.7303 | 0.42114 | 0.28381 | 120.4285 | -2.3987 | 10.7025 | 0.21973 | 0.65918 | 10.0983 | -121.8246 | -0.20599 | 0.30212 | -10.0433 | 2.6138 | 2.4765 | 0.49439 | 122.5388 | 0.65918 | 122.6212 | 0.46234 | -0.20599 | 122.5388 | 0.65918 | 0.46234 | 0.49439 | 122.6212 | -111.6165 | -122.525
1655.5 | 122.3099 | -1.1948 | 121.0419 | 0.0045011 | 0.12219 | 0.0069535 | -0.0092179 | 0.054773 | 0.061075 | 0.26702 | -0.67291 | 121.2799 | 8.519 | 7.9193 | -0.77362 | -0.8194 | 0.43488 | 0.39368 | 121.4081 | -1.4374 | 9.7137 | 0.23804 | 0.52185 | 9.1141 | -121.8155 | -0.24262 | 0.36621 | -9.1919 | 1.6296 | 1.5884 | 0.42114 | 122.4747 | 0.52185 | 122.6028 | 0.37537 | -0.24262 | 122.4747 | 0.52185 | 0.37537 | 0.42114 | 122.6028 | -112.5229 | -122.4792
1657.2031 | 122.2641 | -1.4603 | 120.8679 | 0.0045011 | 0.14847 | 0.0028947 | -0.0043045 | 0.056696 | 0.062143 | 0.29586 | -0.93842 | 121.1472 | 8.5144 | 7.7591 | -1.0712 | -1.0803 | 0.4715 | 0.27466 | 121.2616 | -1.6525 | 9.9747 | 0.27924 | 0.52185 | 9.2194 | -121.9391 | -0.19226 | 0.39368 | -9.4528 | 1.9318 | 1.7349 | 0.3891 | 122.6074 | 0.52185 | 122.7219 | 0.37994 | -0.19226 | 122.6074 | 0.52185 | 0.37994 | 0.3891 | 122.7219 | -112.3535 | -122.5204
1658.9688 | 122.2412 | -2.0142 | 120.2591 | 0.012131 | 0.19248 | 0.0054581 | -0.0040909 | 0.056696 | 0.062784 | 0.33837 | -1.2314 | 120.7809 | 8.5052 | 7.7774 | -1.3641 | -1.3916 | 0.4715 | 0.27466 | 120.8176 | -2.0004 | 10.5194 | 0.52185 | 0.78278 | 9.7916 | -121.6232 | 0.013733 | 0.55847 | -9.7366 | 2.4857 | 2.2888 | 0.65002 | 122.7951 | 0.78278 | 122.8317 | 0.62256 | 0.013733 | 122.7951 | 0.78278 | 0.62256 | 0.65002 | 122.8317 | -111.7538 | -122.2595
1660.6562 | 122.3328 | -2.0462 | 120.2042 | 0.0045011 | 0.23477 | 0.0078079 | -0.0105 | 0.055414 | 0.063425 | 0.40161 | -1.5244 | 120.4147 | 8.519 | 7.7866 | -1.5427 | -1.6571 | 0.37079 | 0.39368 | 120.4926 | -2.3483 | 10.5652 | 0.21057 | 0.52185 | 9.8328 | -121.7468 | -0.30212 | 0.28839 | -10.0433 | 2.417 | 2.4399 | 0.50354 | 122.4609 | 0.52185 | 122.5388 | 0.3891 | -0.30212 | 122.4609 | 0.52185 | 0.3891 | 0.50354 | 122.5388 | -111.6852 | -122.5525
1662.4219 | 122.3145 | -3.6392 | 118.5974 | 0.012131 | 0.4704 | 0.0035355 | -0.0028091 | 0.053278 | 0.060861 | 0.61352 | -2.8427 | 118.8766 | 8.519 | 7.5531 | -2.9663 | -3.0075 | 0.46234 | 0.34332 | 118.9636 | -3.8589 | 12.1582 | 0.27924 | 0.79651 | 11.1923 | -121.5637 | -0.21973 | 0.36621 | -11.3617 | 4.1016 | 3.9825 | 0.67291 | 122.5159 | 0.79651 | 122.6028 | 0.63171 | -0.21973 | 122.5159 | 0.79651 | 0.63171 | 0.67291 | 122.6028 | -110.0784 | -122.4564
1664.1719 | 122.2778 | -1.355 | 121.0327 | 0.0045011 | 0.1348 | 0.0071671 | -0.0038773 | 0.058832 | 0.061502 | 0.2322 | -0.74158 | 121.3989 | 8.5098 | 7.608 | -0.64087 | -0.68207 | 0.48065 | 0.27924 | 121.7651 | -1.1444 | 9.8648 | 0.36621 | 0.6134 | 8.963 | -121.6736 | 0.21057 | 0.73242 | -9.2514 | 1.8356 | 1.6342 | 0.71411 | 122.7539 | 0.6134 | 123.1201 | 0.67291 | 0.21057 | 122.7539 | 0.6134 | 0.67291 | 0.71411 | 123.1201 | -112.5229 | -122.1771
1665.9219 | 122.3557 | -0.86517 | 121.3852 | 0.0045011 | 0.083529 | 0.0026809 | -0.010286 | 0.053919 | 0.06492 | 0.22921 | -0.44861 | 121.7056 | 8.5236 | 7.7774 | -0.54016 | -0.53101 | 0.37994 | 0.41199 | 121.6873 | -1.1627 | 9.3887 | 0.32043 | 0.41656 | 8.6426 | -121.9254 | -0.29755 | 0.30212 | -8.9722 | 1.2451 | 1.2772 | 0.32501 | 122.5708 | 0.41656 | 122.5525 | 0.33417 | -0.29755 | 122.5708 | 0.41656 | 0.33417 | 0.32501 | 122.5525 | -112.8616 | -122.5479
1667.6094 | 122.3282 | -0.94299 | 121.3669 | 0.0045011 | 0.083742 | 0.0050309 | -0.0081497 | 0.053064 | 0.061716 | 0.22964 | -0.46234 | 121.637 | 8.519 | 7.608 | -0.57678 | -0.55847 | 0.34332 | 0.40283 | 121.6782 | -1.1673 | 9.462 | 0.27008 | 0.48065 | 8.551 | -121.9437 | -0.2243 | 0.31128 | -8.9813 | 1.2863 | 1.3458 | 0.36621 | 122.58 | 0.48065 | 122.6212 | 0.38452 | -0.2243 | 122.58 | 0.48065 | 0.38452 | 0.36621 | 122.6212 | -112.8479 | -122.5342
1669.3594 | 122.2733 | -0.98877 | 121.4035 | 0.012131 | 0.08417 | 0.0060989 | -0.0032363 | 0.058405 | 0.058511 | 0.23562 | -0.48065 | 121.6644 | 8.5098 | 7.576 | -0.65002 | -0.64087 | 0.45319 | 0.32959 | 121.7468 | -1.2039 | 9.4986 | 0.26093 | 0.50812 | 8.5648 | -122.0535 | -0.21515 | 0.34332 | -8.9905 | 1.442 | 1.3184 | 0.33875 | 122.6532 | 0.50812 | 122.7356 | 0.3479 | -0.21515 | 122.6532 | 0.50812 | 0.3479 | 0.33875 | 122.7356 | -112.8937 | -122.6074
1671.0938 | 122.3831 | -0.86517 | 121.431 | 0.0045011 | 0.077975 | 0.00011747 | -0.0085769 | 0.054559 | 0.062357 | 0.22344 | -0.44403 | 121.7285 | 8.519 | 7.6492 | -0.54016 | -0.54474 | 0.3479 | 0.41199 | 121.7331 | -1.1353 | 9.3842 | 0.29755 | 0.42114 | 8.5144 | -121.9711 | -0.27008 | 0.30212 | -8.963 | 1.2131 | 1.2772 | 0.32501 | 122.5937 | 0.42114 | 122.5983 | 0.32043 | -0.27008 | 122.5937 | 0.42114 | 0.32043 | 0.32501 | 122.5983 | -112.912 | -122.5662
1672.7812 | 122.374 | -0.87433 | 121.4264 | 0.0045011 | 0.073702 | 0.0028947 | -0.0077225 | 0.053491 | 0.06257 | 0.22366 | -0.42572 | 121.7102 | 8.5144 | 7.6904 | -0.49896 | -0.49896 | 0.34332 | 0.44403 | 121.7743 | -1.1215 | 9.3887 | 0.28381 | 0.44861 | 8.5648 | -121.9254 | -0.24719 | 0.3479 | -8.9401 | 1.2177 | 1.3184 | 0.37537 | 122.5845 | 0.44861 | 122.6486 | 0.37537 | -0.24719 | 122.5845 | 0.44861 | 0.37537 | 0.37537 | 122.6486 | -112.912 | -122.5479
1674.5469 | 122.4014 | -0.86517 | 121.4539 | 0.0045011 | 0.075838 | 0.00054467 | -0.0025955 | 0.051141 | 0.061288 | 0.22387 | -0.48981 | 121.756 | 8.519 | 7.5989 | -0.60425 | -0.62714 | 0.54932 | 0.3479 | 121.8155 | -1.1581 | 9.3842 | 0.30212 | 0.37537 | 8.4641 | -122.0581 | -0.29297 | 0.36163 | -9.0088 | 1.4145 | 1.2131 | 0.26092 | 122.6212 | 0.37537 | 122.6807 | 0.23804 | -0.29297 | 122.6212 | 0.37537 | 0.23804 | 0.26092 | 122.6807 | -112.9349 | -122.612
1676.2969 | 122.2687 | -0.92926 | 121.5134 | -0.0031279 | 0.078829 | 0.0065263 | -0.0034499 | 0.0552 | 0.061288 | 0.22173 | -0.41199 | 121.7377 | 8.5144 | 7.6401 | -0.55389 | -0.56763 | 0.44861 | 0.37537 | 121.7972 | -1.1261 | 9.4437 | 0.2243 | 0.51727 | 8.5693 | -122.0673 | -0.19684 | 0.28381 | -8.9264 | 1.3779 | 1.3046 | 0.37537 | 122.6669 | 0.51727 | 122.7264 | 0.36163 | -0.19684 | 122.6669 | 0.51727 | 0.36163 | 0.37537 | 122.7264 | -112.999 | -122.6395
1678.0625 | 122.319 | -0.91095 | 121.5134 | 0.0045011 | 0.079043 | 0.0035355 | -0.0023819 | 0.057337 | 0.061288 | 0.22408 | -0.45776 | 121.7331 | 8.5098 | 7.5027 | -0.6134 | -0.61798 | 0.50354 | 0.30212 | 121.8155 | -1.1215 | 9.4208 | 0.21973 | 0.45319 | 8.4137 | -122.1268 | -0.21057 | 0.30212 | -8.9676 | 1.4145 | 1.2131 | 0.29755 | 122.644 | 0.45319 | 122.7264 | 0.29297 | -0.21057 | 122.644 | 0.45319 | 0.29297 | 0.29755 | 122.7264 | -113.0035 | -122.6349
1679.75 | 122.406 | -0.89264 | 121.4493 | -0.0031279 | 0.077975 | 0.0067399 | -0.0087905 | 0.05285 | 0.063638 | 0.22579 | -0.49439 | 121.7834 | 8.5144 | 7.8232 | -0.60425 | -0.6134 | 0.54932 | 0.37537 | 121.7697 | -1.1581 | 9.407 | 0.33417 | 0.39825 | 8.7158 | -122.0535 | -0.2655 | 0.32043 | -9.0088 | 1.442 | 1.268 | 0.28839 | 122.6761 | 0.39825 | 122.6624 | 0.27924 | -0.2655 | 122.6761 | 0.39825 | 0.27924 | 0.28839 | 122.6624 | -112.9349 | -122.6074
1681.5 | 122.3007 | -0.91095 | 121.4905 | 0.012131 | 0.074343 | 0.0052445 | -0.0070815 | 0.057123 | 0.064279 | 0.22366 | -0.37994 | 121.756 | 8.519 | 7.8781 | -0.51727 | -0.49439 | 0.3067 | 0.44403 | 121.7743 | -1.1169 | 9.4299 | 0.2655 | 0.53101 | 8.7891 | -122.0078 | -0.20599 | 0.28381 | -8.8989 | 1.2177 | 1.355 | 0.39368 | 122.6669 | 0.53101 | 122.6852 | 0.41657 | -0.20599 | 122.6669 | 0.53101 | 0.41657 | 0.39368 | 122.6852 | -112.9715 | -122.6074
1683.2031 | 122.3145 | -0.89264 | 121.5088 | 0.0045011 | 0.079043 | 0.0086625 | -0.0038773 | 0.054559 | 0.061716 | 0.22558 | -0.42572 | 121.8018 | 8.519 | 7.8415 | -0.59052 | -0.56305 | 0.41657 | 0.33875 | 121.8613 | -1.1078 | 9.4116 | 0.29297 | 0.46692 | 8.7341 | -122.0993 | -0.21515 | 0.35248 | -8.9447 | 1.3092 | 1.2314 | 0.30212 | 122.6944 | 0.46692 | 122.7539 | 0.32959 | -0.21515 | 122.6944 | 0.46692 | 0.32959 | 0.30212 | 122.7539 | -112.9898 | -122.6166
1684.9531 | 122.3969 | -0.83313 | 121.4905 | -0.0031279 | 0.07477 | -0.0013779 | -0.0096451 | 0.054987 | 0.064066 | 0.22473 | -0.48065 | 121.7743 | 8.519 | 7.8781 | -0.50812 | -0.48523 | 0.38452 | 0.4303 | 121.8567 | -1.0941 | 9.3521 | 0.28381 | 0.35248 | 8.7112 | -121.9986 | -0.26092 | 0.36621 | -8.9996 | 1.2177 | 1.2634 | 0.32501 | 122.6074 | 0.35248 | 122.6898 | 0.3479 | -0.26092 | 122.6074 | 0.35248 | 0.3479 | 0.32501 | 122.6898 | -112.9715 | -122.5845
1686.7031 | 122.4243 | -0.82855 | 121.4951 | 0.012131 | 0.075198 | 0.0022537 | -0.0081497 | 0.053491 | 0.061929 | 0.22216 | -0.39825 | 121.7834 | 8.5236 | 7.9742 | -0.51727 | -0.52643 | 0.38452 | 0.40741 | 121.8338 | -1.1078 | 9.3521 | 0.28839 | 0.4303 | 8.8028 | -122.0123 | -0.27924 | 0.33874 | -8.9218 | 1.2131 | 1.236 | 0.31128 | 122.612 | 0.4303 | 122.6624 | 0.30212 | -0.27924 | 122.612 | 0.4303 | 0.30212 | 0.31128 | 122.6624 | -112.9715 | -122.6028
1688.4531 | 122.3511 | -0.87891 | 121.5271 | 0.0045011 | 0.076266 | 0.011226 | 0.00018148 | 0.055414 | 0.061288 | 0.22088 | -0.46692 | 121.7606 | 8.5236 | 7.9376 | -0.6134 | -0.60425 | 0.49439 | 0.32501 | 121.8887 | -1.1215 | 9.4025 | 0.23346 | 0.41199 | 8.8165 | -122.1405 | -0.24262 | 0.36163 | -8.9905 | 1.3733 | 1.2039 | 0.2655 | 122.6395 | 0.41199 | 122.7676 | 0.27466 | -0.24262 | 122.6395 | 0.41199 | 0.27466 | 0.2655 | 122.7676 | -113.0035 | -122.6486
1690.2031 | 122.4335 | -0.85602 | 121.4951 | 0.0045011 | 0.076693 | -0.0022323 | -0.010927 | 0.054132 | 0.063425 | 0.22537 | -0.41657 | 121.7789 | 8.5281 | 7.8964 | -0.54016 | -0.52643 | 0.44403 | 0.44861 | 121.8018 | -1.1032 | 9.3842 | 0.28381 | 0.43945 | 8.7524 | -122.0352 | -0.24719 | 0.3067 | -8.9447 | 1.3 | 1.3046 | 0.31586 | 122.6349 | 0.43945 | 122.6578 | 0.32959 | -0.24719 | 122.6349 | 0.43945 | 0.32959 | 0.31586 | 122.6578 | -112.9669 | -122.5983
1691.9531 | 122.3373 | -2.5452 | 119.8425 | 0.0045011 | 0.34607 | 0.0052445 | -0.0025955 | 0.055414 | 0.061929 | 0.49859 | -1.9455 | 120.0348 | 8.5236 | 7.7911 | -2.092 | -2.124 | 0.46692 | 0.3479 | 120.1126 | -2.8198 | 11.0687 | 0.19226 | 0.59967 | 10.3363 | -121.9345 | -0.27466 | 0.27008 | -10.4691 | 3.0121 | 2.8931 | 0.45319 | 122.58 | 0.59967 | 122.6578 | 0.42114 | -0.27466 | 122.58 | 0.59967 | 0.42114 | 0.45319 | 122.6578 | -111.319 | -122.6624
1693.6406 | 122.3007 | -0.94299 | 121.4355 | -0.0031279 | 0.12262 | 0.0065263 | -0.0043045 | 0.058191 | 0.059793 | 0.23712 | -0.59052 | 121.5775 | 8.5098 | 7.8644 | -0.60883 | -0.62714 | 0.41657 | 0.36621 | 121.7148 | -1.2451 | 9.4528 | 0.14191 | 0.35248 | 8.8074 | -122.0444 | -0.30212 | 0.27924 | -9.1003 | 1.3596 | 1.3092 | 0.33417 | 122.5204 | 0.35248 | 122.6578 | 0.31586 | -0.30212 | 122.5204 | 0.35248 | 0.31586 | 0.33417 | 122.6578 | -112.9257 | -122.6807
1695.3906 | 122.3145 | -1.1215 | 121.2524 | 0.012131 | 0.11749 | 0.0060989 | -0.0034499 | 0.056482 | 0.058725 | 0.26724 | -0.63629 | 121.5729 | 8.5281 | 7.869 | -0.82855 | -0.77362 | 0.50812 | 0.40741 | 121.5408 | -1.3962 | 9.6497 | 0.32043 | 0.48523 | 8.9905 | -122.081 | -0.27466 | 0.28839 | -9.1644 | 1.6296 | 1.5289 | 0.29297 | 122.6944 | 0.48523 | 122.6624 | 0.3479 | -0.27466 | 122.6944 | 0.48523 | 0.3479 | 0.29297 | 122.6624 | -112.7243 | -122.6486
1697.1406 | 122.2824 | -0.91095 | 121.5317 | 0.0045011 | 0.078188 | 0.0048173 | -0.0057999 | 0.056268 | 0.063211 | 0.2275 | -0.33875 | 121.7285 | 8.5236 | 7.933 | -0.49896 | -0.46234 | 0.37079 | 0.47607 | 121.8063 | -1.0941 | 9.4345 | 0.19684 | 0.57221 | 8.844 | -122.0306 | -0.1831 | 0.27466 | -8.8623 | 1.2817 | 1.387 | 0.41199 | 122.6395 | 0.57221 | 122.7173 | 0.44861 | -0.1831 | 122.6395 | 0.57221 | 0.44861 | 0.41199 | 122.7173 | -113.0081 | -122.6257
1698.8281 | 122.4243 | -0.88348 | 121.5088 | -0.0031279 | 0.082033 | 0.0020401 | -0.0053727 | 0.054773 | 0.061075 | 0.22836 | -0.44403 | 121.7743 | 8.5236 | 7.9102 | -0.59509 | -0.60883 | 0.59509 | 0.38452 | 121.9025 | -1.1536 | 9.407 | 0.2655 | 0.43945 | 8.7936 | -122.1039 | -0.27008 | 0.39368 | -8.9676 | 1.4786 | 1.268 | 0.28839 | 122.6578 | 0.43945 | 122.7859 | 0.27466 | -0.27008 | 122.6578 | 0.43945 | 0.27466 | 0.28839 | 122.7859 | -112.9852 | -122.6624
1700.5781 | 122.2595 | -16.0584 | 106.1691 | -0.0031279 | 0.074343 | 0.0054581 | 2.2704 | 0.060114 | 0.051462 | 2.5925 | 0.66376 | 103.7064 | 8.5144 | -18.5898 | 0.50354 | 83.432 | -0.23346 | 0.3067 | 102.4155 | -19.931 | 24.5728 | -2.4628 | 16.7221 | -2.5314 | -105.6656 | -3.8727 | -3.7537 | -7.8506 | 15.8249 | 16.3651 | 16.5619 | 119.7647 | 16.7221 | 118.4738 | 99.4904 | -3.8727 | 119.7647 | 16.7221 | 99.4904 | 16.5619 | 118.4738 | -97.6547 | -126.1002
1702.3281 | 122.3419 | -2.2476 | 120.1721 | 0.0045011 | 0.17539 | 0.0069535 | 0.00082248 | 0.061823 | 0.059579 | 0.33795 | 0.75989 | 120.4468 | 8.5144 | -1.886 | 0.55389 | 0.027466 | 0.35706 | 0.31586 | 120.5429 | -2.4445 | 10.762 | 0.27466 | 3.0075 | 0.36163 | -119.6182 | -0.19684 | 0.37079 | -7.7545 | 2.6047 | 2.5635 | 2.8015 | 122.6944 | 3.0075 | 122.7905 | 2.2751 | -0.19684 | 122.6944 | 3.0075 | 2.2751 | 2.8015 | 122.7905 | -111.6577 | -122.6166
1704.0781 | 122.406 | -2.3621 | 119.8929 | 0.0045011 | 0.25421 | 0.0088761 | -0.0015273 | 0.059473 | 0.062357 | 0.3435 | 0.90179 | 120.2774 | 8.5144 | -1.7441 | 0.6958 | 0.18768 | 0.21973 | 0.5127 | 120.3552 | -2.4811 | 10.8765 | 0.38452 | 3.2639 | 0.61798 | -119.1971 | -0.11902 | 0.46234 | -7.6126 | 2.5818 | 2.8748 | 3.0579 | 122.6395 | 3.2639 | 122.7173 | 2.5497 | -0.11902 | 122.6395 | 3.2639 | 2.5497 | 3.0579 | 122.7173 | -111.3785 | -122.374
1705.7656 | 122.4518 | -2.0691 | 120.3552 | -0.0031279 | 0.13629 | -0.0024459 | -0.0021683 | 0.059259 | 0.061929 | 0.31402 | 0.8606 | 120.8084 | 8.5144 | -1.5564 | 0.6546 | 0.086975 | 0.26093 | 0.44403 | 120.8725 | -2.0645 | 10.5835 | 0.45319 | 2.9297 | 0.5127 | -119.7006 | 0.004578 | 0.51727 | -7.6538 | 2.33 | 2.5131 | 2.7237 | 122.8775 | 2.9297 | 122.9416 | 2.1561 | 0.004578 | 122.8775 | 2.9297 | 2.1561 | 2.7237 | 122.9416 | -111.8408 | -122.4197
1707.5469 | 122.3419 | -1.9547 | 120.5383 | 0.012131 | 0.081393 | 0.0086625 | 0.0027451 | 0.060327 | 0.061716 | 0.25228 | 1.0025 | 121.0876 | 8.5236 | -1.0071 | 0.69122 | 0.16937 | 0.21515 | 0.46234 | 121.1563 | -1.7853 | 10.4782 | 0.54932 | 2.9572 | 0.94757 | -119.8471 | 0.16937 | 0.61798 | -7.5211 | 2.1698 | 2.417 | 2.6459 | 123.0423 | 2.9572 | 123.111 | 2.124 | 0.16937 | 123.0423 | 2.9572 | 2.124 | 2.6459 | 123.111 | -112.0148 | -122.3236
1709.25 | 122.4243 | -1.5747 | 120.7672 | -0.0031279 | 0.1788 | 0.0026809 | -0.0025955 | 0.059686 | 0.061716 | 0.2572 | 0.94757 | 120.5338 | 8.5098 | -1.4099 | 0.6958 | 0.10986 | 0.32044 | 0.43488 | 121.0922 | -1.9226 | 10.0845 | -0.23346 | 2.5223 | 0.1648 | -120.0714 | -0.3479 | 0.32501 | -7.5623 | 1.8951 | 2.0096 | 2.2705 | 122.1085 | 2.5223 | 122.6669 | 1.6846 | -0.3479 | 122.1085 | 2.5223 | 1.6846 | 2.2705 | 122.6669 | -112.2574 | -122.6898
1711 | 122.3969 | -1.7075 | 120.4742 | 0.0045011 | 0.1489 | 0.0035355 | 0.0053085 | 0.059473 | 0.05787 | 0.32064 | 0.9201 | 120.7443 | 8.4961 | -1.4648 | 0.63629 | 0.036621 | 0.41657 | 0.34332 | 121.0739 | -1.8814 | 10.2036 | 0.27008 | 2.6276 | 0.24261 | -119.838 | -0.17395 | 0.59967 | -7.576 | 2.124 | 2.0508 | 2.3438 | 122.4518 | 2.6276 | 122.7814 | 1.7441 | -0.17395 | 122.4518 | 2.6276 | 1.7441 | 2.3438 | 122.7814 | -111.9781 | -122.3557
1712.6875 | 122.4655 | -1.9775 | 120.5658 | 0.0045011 | 0.12113 | 0.00011747 | -0.0011001 | 0.0599 | 0.060007 | 0.2839 | 0.99792 | 120.9824 | 8.5281 | -1.3229 | 0.70038 | 0.10071 | 0.29755 | 0.42114 | 121.0373 | -1.9409 | 10.5057 | 0.41656 | 2.9755 | 0.6546 | -119.8654 | 0.036621 | 0.4715 | -7.5302 | 2.2751 | 2.3987 | 2.6779 | 122.9599 | 2.9755 | 123.0148 | 2.0782 | 0.036621 | 122.9599 | 2.9755 | 2.0782 | 2.6779 | 123.0148 | -112.0377 | -122.5067
1714.4375 | 122.3373 | -2.298 | 120.1859 | -0.0031279 | 0.17453 | 0.0073807 | 0.0063767 | 0.062036 | 0.060434 | 0.34051 | 1.1124 | 120.5566 | 8.5098 | -1.9547 | 0.75073 | 0.054932 | 0.35248 | 0.37079 | 120.369 | -2.5497 | 10.8078 | 0.37079 | 3.4103 | 0.34332 | -119.4351 | -0.25177 | 0.18311 | -7.3975 | 2.6505 | 2.6688 | 3.0487 | 122.8546 | 3.4103 | 122.6669 | 2.3529 | -0.25177 | 122.8546 | 3.4103 | 2.3529 | 3.0487 | 122.6669 | -111.676 | -122.7356
1716.125 | 122.5113 | -1.9089 | 120.5429 | 0.0045011 | 0.18265 | -0.0022323 | -0.0015273 | 0.059045 | 0.060861 | 0.36636 | 1.0666 | 120.314 | 8.519 | -2.2842 | 0.75531 | 0.032043 | 0.48065 | 0.39368 | 120.433 | -2.6184 | 10.4279 | -0.22888 | 2.9755 | -0.37537 | -119.7876 | -0.70953 | -0.10986 | -7.4524 | 2.3895 | 2.3026 | 2.6642 | 122.2229 | 2.9755 | 122.3419 | 1.9409 | -0.70953 | 122.2229 | 2.9755 | 1.9409 | 2.6642 | 122.3419 | -112.0239 | -123.1613
1717.875 | 122.3236 | -3.7537 | 118.6478 | -0.0031279 | 0.38751 | 0.0084489 | 0.0050949 | 0.060541 | 0.06022 | 0.50564 | 1.1765 | 118.9682 | 8.5236 | -2.8976 | 0.79193 | 0.11902 | 0.14648 | 0.41199 | 119.1605 | -3.6346 | 12.2772 | 0.32043 | 4.9301 | 0.85602 | -117.8558 | 0.11902 | 0.51269 | -7.3471 | 3.9001 | 4.1656 | 4.5456 | 122.7219 | 4.9301 | 122.9141 | 3.8727 | 0.11902 | 122.7219 | 4.9301 | 3.8727 | 4.5456 | 122.9141 | -110.1242 | -122.2824
1719.6094 | 122.3465 | -3.6026 | 118.7805 | -0.0031279 | 0.3324 | 0.010371 | 0.0044541 | 0.062463 | 0.062357 | 0.50607 | 1.0849 | 119.3115 | 8.5236 | -2.9388 | 0.70038 | -0.004578 | 0.37537 | 0.28381 | 119.4031 | -3.5614 | 12.1262 | 0.531 | 4.6875 | 0.66376 | -118.0801 | 0.041199 | 0.62256 | -7.4387 | 3.978 | 3.8864 | 4.303 | 122.9141 | 4.6875 | 123.0057 | 3.598 | 0.041199 | 122.9141 | 4.6875 | 3.598 | 4.303 | 123.0057 | -110.257 | -122.3419
1721.3594 | 118.2999 | -26.1795 | 91.8503 | 0.042648 | 0.30249 | 0.0078079 | 6.9397 | 0.00029913 | 0.042062 | 7.0222 | 0.33417 | 92.276 | 8.4961 | 67.6483 | 0.041199 | 0.086975 | 1.062 | 0.40741 | 84.7183 | -18.6813 | 34.6756 | 0.42572 | 26.5137 | 93.8278 | -91.8091 | 7.4982 | -7.132 | -8.1619 | 27.2415 | 26.5869 | 26.2207 | 118.4555 | 26.5137 | 110.8978 | 26.2665 | 7.4982 | 118.4555 | 26.5137 | 26.2665 | 26.2207 | 110.8978 | -83.3542 | -110.5316
1723.1094 | 117.659 | -26.7838 | 90.8203 | 0.0045011 | 0.28113 | 0.0041763 | 6.9397 | 0.0039307 | 0.039499 | 7.0222 | 0.60883 | 90.9988 | 8.5373 | 66.7603 | 0.27924 | 0.15106 | 1.2817 | 0.43945 | 83.6288 | -19.2764 | 35.321 | 0.17853 | 27.3926 | 93.544 | -90.5411 | 7.5073 | -7.1915 | -7.9285 | 28.0655 | 27.2232 | 27.063 | 117.7826 | 27.3926 | 110.4126 | 26.9348 | 7.5073 | 117.7826 | 27.3926 | 26.9348 | 27.063 | 110.4126 | -82.283 | -110.0967
1724.8438 | 117.3157 | -29.6585 | 87.3825 | -0.0031279 | 0.26682 | 0.0065263 | 6.9397 | -0.00055547 | 0.037363 | 7.0222 | -0.022888 | 87.3138 | 8.5419 | 63.1531 | -0.33417 | 0.091553 | 3.1128 | 0.43488 | 79.9759 | -22.554 | 38.2004 | -0.068664 | 29.6356 | 92.8116 | -87.7167 | 7.1045 | -7.4066 | -8.5648 | 32.7713 | 30.0934 | 29.3243 | 116.9724 | 29.6356 | 109.6344 | 29.7501 | 7.1045 | 116.9724 | 29.6356 | 29.7501 | 29.3243 | 109.6344 | -78.8406 | -109.9365
1726.5156 | 115.535 | -77.0828 | 38.3881 | 0.012131 | 4.3434 | 0.0050309 | 6.9397 | 0.011194 | 0.023477 | 7.0222 | 2.6459 | 46.4401 | 8.5373 | 2.8381 | -23.8449 | 2.5635 | 4.985 | 5.8044 | 33.2291 | -54.4922 | 85.6201 | 8.0521 | 79.7287 | 79.921 | -62.233 | 22.5906 | -5.159 | -5.8914 | 82.0679 | 82.8873 | 53.2379 | 123.523 | 79.7287 | 110.3119 | 79.6463 | 22.5906 | 123.523 | 79.7287 | 79.6463 | 53.2379 | 110.3119 | -29.8508 | -92.8802
1728.2812 | 119.6594 | -119.1696 | 0.27466 | 0.0045011 | 0.023074 | 0.0033219 | 0.01364 | -0.0046143 | -0.0038666 | 0.018792 | 0.11444 | 0.36621 | -0.26093 | 0.20142 | 0.12817 | 0.18768 | -0.11902 | 0.40283 | 0.40741 | -0.27924 | 118.9087 | 0.091553 | 119.2841 | 119.371 | -0.14648 | 118.8904 | 0.13275 | 0.37537 | 119.0506 | 119.5724 | 119.2978 | 119.5358 | 119.2841 | 119.577 | 119.3573 | 118.8904 | 119.5358 | 119.2841 | 119.3573 | 119.2978 | 119.577 | -0.53558 | -0.55389
1729.9531 | 120.0485 | -119.6045 | 0.21515 | 0.012131 | 0.019228 | 0.0052445 | 0.015135 | -0.0044007 | -0.0032258 | 0.021356 | 0.036621 | 0.35248 | -0.31586 | 0.15564 | 0.054932 | 0.14191 | -0.10529 | 0.32044 | 0.39825 | -0.28381 | 119.2886 | 0.13733 | 119.6411 | 119.7601 | -0.16022 | 119.3207 | 0.1831 | 0.35248 | 119.4992 | 119.9249 | 119.6594 | 119.957 | 119.6411 | 120.0027 | 119.7464 | 119.3207 | 119.957 | 119.6411 | 119.7464 | 119.6594 | 120.0027 | -0.53101 | -0.49896
1731.7031 | 120.1172 | -119.8059 | 0.25635 | 0.0045011 | 0.023928 | 0.0067399 | 0.021117 | -0.0078187 | -0.004721 | 0.018579 | -0.013733 | 0.36163 | -0.32501 | 0.10071 | -0.022888 | 0.054932 | 0.018311 | 0.22888 | 0.41199 | -0.28839 | 119.4809 | 0.10528 | 119.7922 | 119.9066 | -0.27924 | 119.5175 | 0.15564 | 0.31128 | 119.8242 | 120.0348 | 119.783 | 120.1675 | 119.7922 | 120.2179 | 119.8608 | 119.5175 | 120.1675 | 119.7922 | 119.8608 | 119.783 | 120.2179 | -0.58136 | -0.54474
1733.3906 | 120.2545 | -119.8883 | 0.21973 | 0.0045011 | 0.016665 | 0.00097207 | 0.012785 | -0.0086731 | -0.004721 | 0.01687 | 0.09613 | 0.33417 | -0.27466 | 0.21973 | 0.11444 | 0.18768 | -0.086975 | 0.38452 | 0.37994 | -0.26093 | 119.6136 | 0.11444 | 119.9844 | 120.108 | -0.10529 | 119.6274 | 0.16022 | 0.37079 | 119.8013 | 120.2728 | 120.0027 | 120.2225 | 119.9844 | 120.2682 | 120.076 | 119.6274 | 120.2225 | 119.9844 | 120.076 | 120.0027 | 120.2682 | -0.49439 | -0.48065
1735.1406 | 120.2271 | -119.9982 | 0.22888 | 0.0045011 | 0.019656 | 0.0060989 | 0.019835 | -0.0050415 | -0.0055756 | 0.018579 | 0.036621 | 0.34332 | -0.33875 | 0.19684 | 0.091553 | 0.17395 | -0.16937 | 0.32501 | 0.34332 | -0.24719 | 119.6594 | 0.11444 | 120.0348 | 120.195 | -0.13733 | 119.751 | 0.11444 | 0.37537 | 119.8288 | 120.3232 | 120.0897 | 120.3415 | 120.0348 | 120.3415 | 120.1721 | 119.751 | 120.3415 | 120.0348 | 120.1721 | 120.0897 | 120.3415 | -0.56763 | -0.47607
1736.8125 | 120.3873 | -120.0485 | 0.21515 | 0.0045011 | 0.021792 | 0.0078079 | 0.020903 | -0.0080323 | -0.0066438 | 0.016443 | -0.013733 | 0.35706 | -0.35706 | 0.16479 | 0.032043 | 0.10071 | 0.004578 | 0.27924 | 0.39368 | -0.29297 | 119.6915 | 0.14191 | 120.0348 | 120.2133 | -0.18311 | 119.7556 | 0.17853 | 0.34332 | 120.0531 | 120.3278 | 120.0806 | 120.4056 | 120.0348 | 120.4422 | 120.1492 | 119.7556 | 120.4056 | 120.0348 | 120.1492 | 120.0806 | 120.4422 | -0.5722 | -0.50812
1738.5625 | 120.4102 | -120.1035 | 0.24261 | 0.0045011 | 0.020083 | 0.0022537 | 0.012999 | -0.0065369 | -0.0045074 | 0.01452 | 0.11444 | 0.30212 | -0.27924 | 0.22888 | 0.12817 | 0.19226 | -0.13733 | 0.40741 | 0.35248 | -0.24719 | 119.8242 | 0.059509 | 120.2179 | 120.3323 | -0.11444 | 119.8563 | 0.10986 | 0.39368 | 119.9661 | 120.5109 | 120.2316 | 120.4056 | 120.2179 | 120.4559 | 120.2957 | 119.8563 | 120.4056 | 120.2179 | 120.2957 | 120.2316 | 120.4559 | -0.52185 | -0.48981
1740.3281 | 120.4422 | -120.1813 | 0.23804 | 0.0045011 | 0.020296 | 0.0013993 | 0.021544 | -0.0054687 | -0.0068574 | 0.017724 | 0.018311 | 0.36621 | -0.33875 | 0.16022 | 0.032043 | 0.10529 | 0.004578 | 0.30212 | 0.40741 | -0.27466 | 119.8425 | 0.12817 | 120.1996 | 120.3415 | -0.20599 | 119.9066 | 0.16937 | 0.35706 | 120.1859 | 120.4834 | 120.2133 | 120.5475 | 120.1996 | 120.5887 | 120.2866 | 119.9066 | 120.5475 | 120.1996 | 120.2866 | 120.2133 | 120.5887 | -0.57678 | -0.5127
1742.0156 | 120.5383 | -120.195 | 0.22888 | -0.0031279 | 0.023714 | 0.0043899 | 0.017699 | -0.0054687 | -0.0060028 | 0.017938 | -0.009155 | 0.35248 | -0.3479 | 0.12817 | 0.027466 | 0.073242 | 0.050354 | 0.27008 | 0.40741 | -0.27466 | 119.8471 | 0.1236 | 120.1859 | 120.3232 | -0.20142 | 119.9203 | 0.17853 | 0.33874 | 120.2454 | 120.4651 | 120.2225 | 120.5475 | 120.1859 | 120.6024 | 120.2682 | 119.9203 | 120.5475 | 120.1859 | 120.2682 | 120.2225 | 120.6024 | -0.57678 | -0.50354
1743.7656 | 120.5795 | -120.2087 | 0.21515 | -0.0031279 | 0.019869 | 0.0037491 | 0.01663 | -0.0056823 | -0.0051484 | 0.016229 | 0.013733 | 0.37537 | -0.33417 | 0.13733 | 0.022888 | 0.082397 | 0.050354 | 0.27466 | 0.41199 | -0.27924 | 119.8746 | 0.16022 | 120.2225 | 120.3461 | -0.19226 | 119.9295 | 0.19684 | 0.3479 | 120.2591 | 120.4834 | 120.2316 | 120.5841 | 120.2225 | 120.6207 | 120.2911 | 119.9295 | 120.5841 | 120.2225 | 120.2911 | 120.2316 | 120.6207 | -0.54932 | -0.49438
1745.5312 | 120.6162 | -120.2454 | 0.22888 | 0.0045011 | 0.017947 | 0.0026809 | 0.011931 | -0.0076049 | -0.003653 | 0.01687 | 0.064087 | 0.35248 | -0.28839 | 0.2243 | 0.12817 | 0.19684 | -0.10529 | 0.3891 | 0.38452 | -0.24261 | 119.957 | 0.1236 | 120.3094 | 120.4697 | -0.10071 | 120.0027 | 0.15564 | 0.35248 | 120.1401 | 120.6345 | 120.3735 | 120.5978 | 120.3094 | 120.6299 | 120.4422 | 120.0027 | 120.5978 | 120.3094 | 120.4422 | 120.3735 | 120.6299 | -0.51727 | -0.4715
1747.2031 | 120.5887 | -120.3278 | 0.24261 | 0.012131 | 0.021151 | 0.0097305 | 0.017912 | -0.0069641 | -0.00643 | 0.015588 | -0.009155 | 0.3891 | -0.3067 | 0.12817 | 0.004578 | 0.064087 | -0.004578 | 0.2243 | 0.40283 | -0.27466 | 120.0211 | 0.14648 | 120.3186 | 120.4559 | -0.23804 | 120.0531 | 0.16022 | 0.29755 | 120.3232 | 120.5521 | 120.3323 | 120.7169 | 120.3186 | 120.7306 | 120.3918 | 120.0531 | 120.7169 | 120.3186 | 120.3918 | 120.3323 | 120.7306 | -0.54932 | -0.51727
1748.9531 | 120.7031 | -120.3003 | 0.22888 | 0.012131 | 0.022005 | 0.0028947 | 0.016203 | -0.0071777 | -0.0060028 | 0.01452 | 0.009155 | 0.37079 | -0.34332 | 0.1236 | 0.013733 | 0.073242 | 0.082397 | 0.27466 | 0.42572 | -0.27924 | 119.957 | 0.14191 | 120.3094 | 120.4239 | -0.21515 | 120.0211 | 0.19684 | 0.35248 | 120.3827 | 120.575 | 120.314 | 120.6711 | 120.3094 | 120.726 | 120.3735 | 120.0211 | 120.6711 | 120.3094 | 120.3735 | 120.314 | 120.726 | -0.5722 | -0.50812
1750.6875 | 120.6802 | -120.3415 | 0.25635 | 0.012131 | 0.017733 | 0.00097207 | 0.012785 | -0.0082459 | -0.0066438 | 0.016443 | 0.11444 | 0.33417 | -0.27466 | 0.25635 | 0.16479 | 0.22888 | -0.086975 | 0.44861 | 0.37994 | -0.2243 | 120.0668 | 0.077819 | 120.4559 | 120.5978 | -0.091553 | 120.1172 | 0.1236 | 0.3891 | 120.2545 | 120.7901 | 120.5063 | 120.6757 | 120.4559 | 120.7214 | 120.5704 | 120.1172 | 120.6757 | 120.4559 | 120.5704 | 120.5063 | 120.7214 | -0.53101 | -0.48065
1752.4375 | 120.6482 | -120.401 | 0.27466 | -0.0031279 | 0.02286 | 0.0058853 | 0.017912 | -0.0078187 | -0.0068574 | 0.014947 | 0.07782 | 0.3891 | -0.29755 | 0.21057 | 0.07782 | 0.14648 | 0.022888 | 0.32959 | 0.43945 | -0.23346 | 120.1035 | 0.11444 | 120.4788 | 120.6116 | -0.19684 | 120.1675 | 0.16479 | 0.37537 | 120.4239 | 120.7306 | 120.4788 | 120.7901 | 120.4788 | 120.8405 | 120.5475 | 120.1675 | 120.7901 | 120.4788 | 120.5475 | 120.4788 | 120.8405 | -0.5722 | -0.50812
1754.1875 | 120.7809 | -120.3552 | 0.2655 | -0.0031279 | 0.019015 | 0.0052445 | 0.011931 | -0.0086731 | -0.0032258 | 0.016015 | 0.086975 | 0.37537 | -0.25177 | 0.20599 | 0.10529 | 0.19226 | -0.068665 | 0.36621 | 0.3891 | -0.21515 | 120.1035 | 0.10986 | 120.4422 | 120.5612 | -0.16022 | 120.1401 | 0.1236 | 0.33874 | 120.2866 | 120.7214 | 120.4605 | 120.7306 | 120.4422 | 120.7443 | 120.5475 | 120.1401 | 120.7306 | 120.4422 | 120.5475 | 120.4605 | 120.7443 | -0.51727 | -0.48065
1755.9375 | 120.7489 | -120.4239 | 0.29297 | 0.012131 | 0.021578 | 0.0082351 | 0.020048 | -0.0056823 | -0.0092072 | 0.016229 | 0.041199 | 0.3891 | -0.28381 | 0.16479 | 0.022888 | 0.11444 | 0.050354 | 0.26093 | 0.46692 | -0.23804 | 120.1401 | 0.09613 | 120.4651 | 120.5887 | -0.27008 | 120.1859 | 0.17395 | 0.32501 | 120.4742 | 120.6848 | 120.4468 | 120.813 | 120.4651 | 120.8908 | 120.5383 | 120.1859 | 120.813 | 120.4651 | 120.5383 | 120.4468 | 120.8908 | -0.57678 | -0.53101
1757.625 | 120.8084 | -120.4239 | 0.27924 | -0.0031279 | 0.019015 | -0.00073693 | 0.010008 | -0.0058961 | -0.0074982 | 0.012811 | 0.14648 | 0.38452 | -0.23804 | 0.28381 | 0.17395 | 0.25635 | -0.07782 | 0.45776 | 0.42114 | -0.19226 | 120.1859 | 0.10529 | 120.5704 | 120.7077 | -0.10529 | 120.2316 | 0.14191 | 0.38452 | 120.3461 | 120.8817 | 120.5978 | 120.8084 | 120.5704 | 120.845 | 120.6802 | 120.2316 | 120.8084 | 120.5704 | 120.6802 | 120.5978 | 120.845 | -0.51727 | -0.4715
1759.3906 | 120.8588 | -120.4514 | 0.28381 | 0.012131 | 0.022433 | 0.011226 | 0.016203 | -0.0069641 | -0.007071 | 0.014093 | 0.050354 | 0.39825 | -0.29297 | 0.19684 | 0.068665 | 0.14191 | 0.10529 | 0.33417 | 0.45776 | -0.21973 | 120.1584 | 0.11444 | 120.5017 | 120.6482 | -0.21515 | 120.2316 | 0.17395 | 0.34332 | 120.5566 | 120.7855 | 120.52 | 120.8496 | 120.5017 | 120.9091 | 120.5933 | 120.2316 | 120.8496 | 120.5017 | 120.5933 | 120.52 | 120.9091 | -0.57678 | -0.50354
1761.0781 | 120.7993 | -120.4926 | 0.29297 | -0.0031279 | 0.02286 | 0.0063125 | 0.018339 | -0.0046143 | -0.0092072 | 0.016229 | 0.073242 | 0.39825 | -0.27924 | 0.16937 | 0.059509 | 0.12817 | 0.064087 | 0.28381 | 0.45776 | -0.21515 | 120.2133 | 0.10529 | 120.5658 | 120.6619 | -0.23346 | 120.2774 | 0.1648 | 0.35248 | 120.5566 | 120.7764 | 120.5521 | 120.8908 | 120.5658 | 120.9503 | 120.6207 | 120.2774 | 120.8908 | 120.5658 | 120.6207 | 120.5521 | 120.9503 | -0.5722 | -0.50812
1762.8281 | 120.813 | -120.5246 | 0.31586 | -0.0031279 | 0.018587 | 0.0035355 | 0.01663 | -0.0061097 | -0.00878 | 0.016229 | 0.11902 | 0.40741 | -0.27008 | 0.24261 | 0.13275 | 0.19226 | 0.041199 | 0.38452 | 0.45319 | -0.20599 | 120.2545 | 0.091553 | 120.6436 | 120.7672 | -0.18311 | 120.3186 | 0.13733 | 0.3891 | 120.5658 | 120.9091 | 120.6573 | 120.932 | 120.6436 | 120.9778 | 120.7169 | 120.3186 | 120.932 | 120.6436 | 120.7169 | 120.6573 | 120.9778 | -0.58594 | -0.52185
1764.5781 | 120.932 | -120.5154 | 0.28381 | 0.012131 | 0.019869 | 0.0018265 | 0.013213 | -0.0065369 | -0.0025848 | 0.016229 | 0.11444 | 0.39825 | -0.21973 | 0.23346 | 0.13275 | 0.22888 | -0.027466 | 0.3891 | 0.43488 | -0.17395 | 120.2957 | 0.11444 | 120.6299 | 120.7489 | -0.15106 | 120.3415 | 0.15106 | 0.33417 | 120.488 | 120.9045 | 120.6482 | 120.9137 | 120.6299 | 120.9503 | 120.7443 | 120.3415 | 120.9137 | 120.6299 | 120.7443 | 120.6482 | 120.9503 | -0.50354 | -0.45776
1766.3281 | 120.9778 | -120.5383 | 0.30212 | 0.0045011 | 0.017519 | 0.0028947 | 0.017912 | -0.010382 | -0.0051484 | 0.016229 | 0.036621 | 0.42114 | -0.24719 | 0.19226 | 0.086975 | 0.13733 | 0.13733 | 0.34332 | 0.48981 | -0.21515 | 120.2911 | 0.11902 | 120.575 | 120.7306 | -0.21515 | 120.3232 | 0.18768 | 0.28381 | 120.6757 | 120.8817 | 120.6253 | 120.9595 | 120.575 | 121.0281 | 120.6757 | 120.3232 | 120.9595 | 120.575 | 120.6757 | 120.6253 | 121.0281 | -0.54932 | -0.51727
1768.0781 | 120.9869 | -120.5612 | 0.28839 | -0.0031279 | 0.019015 | 0.0031083 | 0.014708 | -0.0076049 | -0.00643 | 0.012811 | 0.14648 | 0.38452 | -0.2243 | 0.25177 | 0.15106 | 0.21515 | -0.013733 | 0.40283 | 0.45319 | -0.17395 | 120.3369 | 0.09613 | 120.7077 | 120.813 | -0.13733 | 120.3873 | 0.16479 | 0.37079 | 120.5475 | 120.9641 | 120.7123 | 120.9457 | 120.7077 | 121.0144 | 120.7764 | 120.3873 | 120.9457 | 120.7077 | 120.7764 | 120.7123 | 121.0144 | -0.5127 | -0.46234
1769.7656 | 120.9595 | -120.6207 | 0.31128 | 0.0045011 | 0.018587 | 0.0048173 | 0.012358 | -0.0088867 | -0.0057892 | 0.013025 | 0.16022 | 0.39825 | -0.21515 | 0.27466 | 0.17395 | 0.25177 | -0.045776 | 0.43488 | 0.43945 | -0.16937 | 120.4056 | 0.086975 | 120.7809 | 120.8954 | -0.13733 | 120.4514 | 0.12817 | 0.37537 | 120.575 | 121.0556 | 120.7947 | 121.019 | 120.7809 | 121.0602 | 120.8725 | 120.4514 | 121.019 | 120.7809 | 120.8725 | 120.7947 | 121.0602 | -0.52643 | -0.48065
1771.5312 | 121.0052 | -120.6024 | 0.3067 | -0.010757 | 0.020296 | 0.0052445 | 0.017058 | -0.0088867 | -0.0077118 | 0.014306 | 0.19684 | 0.38452 | -0.23346 | 0.33417 | 0.2243 | 0.29755 | -0.032043 | 0.51727 | 0.44403 | -0.15564 | 120.369 | 0.077819 | 120.7993 | 120.9366 | -0.082398 | 120.4468 | 0.13733 | 0.4303 | 120.5704 | 121.1197 | 120.8267 | 120.9869 | 120.7993 | 121.0464 | 120.9 | 120.4468 | 120.9869 | 120.7993 | 120.9 | 120.8267 | 121.0464 | -0.54016 | -0.46234
1773.2812 | 120.9961 | -120.6528 | 0.32959 | -0.010757 | 0.021578 | 0.012294 | 0.021117 | -0.0052551 | -0.0079254 | 0.014734 | 0.086975 | 0.43945 | -0.26093 | 0.21515 | 0.082397 | 0.13733 | 0.09613 | 0.32044 | 0.48523 | -0.17853 | 120.3918 | 0.10986 | 120.7397 | 120.8679 | -0.24719 | 120.4742 | 0.15564 | 0.3479 | 120.7489 | 120.9732 | 120.7352 | 121.0922 | 120.7397 | 121.138 | 120.7901 | 120.4742 | 121.0922 | 120.7397 | 120.7901 | 120.7352 | 121.138 | -0.59052 | -0.50812
1774.9688 | 120.9915 | -120.6848 | 0.33875 | 0.0045011 | 0.022005 | 0.0082351 | 0.021544 | -0.0067505 | -0.0074982 | 0.015374 | 0.11902 | 0.43488 | -0.22888 | 0.22888 | 0.086975 | 0.14648 | 0.091553 | 0.32959 | 0.48523 | -0.18768 | 120.4559 | 0.09613 | 120.8038 | 120.9137 | -0.25177 | 120.4971 | 0.14648 | 0.3479 | 120.7764 | 121.0144 | 120.7718 | 121.1197 | 120.8038 | 121.17 | 120.8313 | 120.4971 | 121.1197 | 120.8038 | 120.8313 | 120.7718 | 121.17 | -0.56763 | -0.52643
1776.7031 | 121.0236 | -120.6757 | 0.32044 | -0.0031279 | 0.021365 | 0.0026809 | 0.019408 | -0.0058961 | -0.005362 | 0.016015 | 0.082397 | 0.43488 | -0.24719 | 0.18768 | 0.073242 | 0.13733 | 0.12817 | 0.3067 | 0.48523 | -0.19684 | 120.4285 | 0.11444 | 120.7581 | 120.8633 | -0.24719 | 120.4788 | 0.16479 | 0.32959 | 120.8038 | 120.9824 | 120.7489 | 121.1105 | 120.7581 | 121.1609 | 120.813 | 120.4788 | 121.1105 | 120.7581 | 120.813 | 120.7489 | 121.1609 | -0.56763 | -0.51727
1778.4531 | 121.0922 | -120.694 | 0.31128 | 0.0045011 | 0.019656 | 0.0041763 | 0.010435 | -0.0099549 | -0.0060028 | 0.015374 | 0.17853 | 0.39825 | -0.19226 | 0.32044 | 0.22888 | 0.29755 | -0.032043 | 0.5127 | 0.44403 | -0.16022 | 120.5017 | 0.086975 | 120.8725 | 121.0144 | -0.082397 | 120.5338 | 0.13275 | 0.37079 | 120.6619 | 121.2067 | 120.9229 | 121.0922 | 120.8725 | 121.138 | 120.9915 | 120.5338 | 121.0922 | 120.8725 | 120.9915 | 120.9229 | 121.138 | -0.50354 | -0.4715
1780.2188 | 121.1243 | -120.7031 | 0.3067 | 0.0045011 | 0.019442 | -0.0013779 | 0.012572 | -0.0091003 | -0.0030122 | 0.012384 | 0.17395 | 0.40741 | -0.1831 | 0.33875 | 0.23346 | 0.29297 | -0.032043 | 0.50354 | 0.45319 | -0.15564 | 120.52 | 0.10071 | 120.8771 | 121.0419 | -0.073243 | 120.5475 | 0.14648 | 0.35706 | 120.6711 | 121.2067 | 120.9366 | 121.1105 | 120.8771 | 121.1563 | 120.9961 | 120.5475 | 121.1105 | 120.8771 | 120.9961 | 120.9366 | 121.1563 | -0.48981 | -0.46234
1781.9688 | 121.0373 | -120.7718 | 0.33417 | -0.010757 | 0.017306 | 0.0080215 | 0.017912 | -0.0069641 | -0.0057892 | 0.012597 | 0.20599 | 0.40283 | -0.17395 | 0.34332 | 0.21515 | 0.30212 | -0.082397 | 0.46234 | 0.42572 | -0.15106 | 120.5978 | 0.068665 | 120.9778 | 121.1151 | -0.11902 | 120.6207 | 0.091553 | 0.37994 | 120.6894 | 121.2341 | 120.9869 | 121.1746 | 120.9778 | 121.1975 | 121.0739 | 120.6207 | 121.1746 | 120.9778 | 121.0739 | 120.9869 | 121.1975 | -0.50812 | -0.48523
1783.6562 | 121.2021 | -120.7443 | 0.3067 | 0.01976 | 0.016665 | 0.0035355 | 0.014067 | -0.0071777 | -0.0083526 | 0.012811 | 0.13275 | 0.40741 | -0.19226 | 0.27008 | 0.17395 | 0.26093 | 0.009155 | 0.43488 | 0.45776 | -0.15106 | 120.5521 | 0.10071 | 120.8771 | 121.0144 | -0.13275 | 120.5933 | 0.15106 | 0.32501 | 120.7535 | 121.1792 | 120.9183 | 121.1517 | 120.8771 | 121.2021 | 121.0052 | 120.5933 | 121.1517 | 120.8771 | 121.0052 | 120.9183 | 121.2021 | -0.49896 | -0.45776
1785.4062 | 121.2341 | -120.7672 | 0.31128 | 0.0045011 | 0.018587 | 0.0035355 | 0.01663 | -0.010382 | -0.0049348 | 0.01217 | 0.11902 | 0.42572 | -0.21973 | 0.22888 | 0.11444 | 0.17395 | 0.15564 | 0.38452 | 0.49439 | -0.19226 | 120.5475 | 0.11444 | 120.8862 | 120.9961 | -0.19684 | 120.575 | 0.18311 | 0.33875 | 120.9229 | 121.1517 | 120.8817 | 121.1929 | 120.8862 | 121.2616 | 120.9412 | 120.575 | 121.1929 | 120.8862 | 120.9412 | 120.8817 | 121.2616 | -0.53101 | -0.50354
1787.0938 | 121.1151 | -120.7947 | 0.3479 | -0.0031279 | 0.02286 | 0.0058853 | 0.018339 | -0.0052551 | -0.0068574 | 0.013665 | 0.15564 | 0.43945 | -0.2243 | 0.30212 | 0.17395 | 0.27008 | -0.022888 | 0.43488 | 0.46692 | -0.14191 | 120.5704 | 0.091553 | 120.9503 | 121.0968 | -0.17395 | 120.6528 | 0.11902 | 0.37994 | 120.7718 | 121.2296 | 120.9686 | 121.2341 | 120.9503 | 121.2616 | 121.0648 | 120.6528 | 121.2341 | 120.9503 | 121.0648 | 120.9686 | 121.2616 | -0.5722 | -0.48981
1788.8438 | 121.2021 | -120.813 | 0.32501 | -0.0031279 | 0.021365 | 0.00011747 | 0.015349 | -0.0099549 | -0.0057892 | 0.012384 | 0.22888 | 0.41199 | -0.17395 | 0.36621 | 0.24261 | 0.31586 | -0.009155 | 0.52185 | 0.4715 | -0.13275 | 120.639 | 0.086975 | 121.0419 | 121.1792 | -0.082397 | 120.6802 | 0.14648 | 0.40283 | 120.8038 | 121.3348 | 121.0556 | 121.225 | 121.0419 | 121.2845 | 121.1288 | 120.6802 | 121.225 | 121.0419 | 121.1288 | 121.0556 | 121.2845 | -0.49896 | -0.45776
1790.5938 | 121.1334 | -120.8313 | 0.35248 | -0.0031279 | 0.017947 | 0.0052445 | 0.019408 | -0.0084595 | -0.005362 | 0.011956 | 0.20599 | 0.43945 | -0.1831 | 0.34332 | 0.21515 | 0.3067 | -0.054932 | 0.46692 | 0.45319 | -0.12817 | 120.6482 | 0.086975 | 121.0373 | 121.1746 | -0.13733 | 120.7031 | 0.10071 | 0.3891 | 120.7764 | 121.2982 | 121.0464 | 121.2708 | 121.0373 | 121.2845 | 121.138 | 120.7031 | 121.2708 | 121.0373 | 121.138 | 121.0464 | 121.2845 | -0.53558 | -0.48065
1792.2812 | 121.2891 | -120.8359 | 0.32959 | 0.0045011 | 0.018587 | 0.0024673 | 0.016844 | -0.010809 | -0.0049348 | 0.013665 | 0.17395 | 0.42572 | -0.16479 | 0.29297 | 0.17853 | 0.22888 | 0.1236 | 0.44403 | 0.50354 | -0.15106 | 120.6711 | 0.09613 | 121.0098 | 121.1288 | -0.15106 | 120.6848 | 0.17395 | 0.33874 | 120.9595 | 121.2799 | 121.0144 | 121.2616 | 121.0098 | 121.3394 | 121.0648 | 120.6848 | 121.2616 | 121.0098 | 121.0648 | 121.0144 | 121.3394 | -0.49438 | -0.48065
1794.0469 | 121.2799 | -120.8313 | 0.33875 | 0.0045011 | 0.019015 | -0.0013779 | 0.015349 | -0.011023 | -0.0068574 | 0.013238 | 0.21057 | 0.43945 | -0.17395 | 0.34332 | 0.23804 | 0.27924 | 0.073242 | 0.51727 | 0.48065 | -0.14648 | 120.6573 | 0.10071 | 121.0419 | 121.1746 | -0.10071 | 120.6848 | 0.14191 | 0.38452 | 120.9045 | 121.3486 | 121.0693 | 121.2708 | 121.0419 | 121.312 | 121.1105 | 120.6848 | 121.2708 | 121.0419 | 121.1105 | 121.0693 | 121.312 | -0.5127 | -0.48523
1795.8125 | 121.2158 | -120.8954 | 0.37079 | 0.012131 | 0.02051 | 0.0046037 | 0.020262 | -0.0076049 | -0.0094208 | 0.013025 | 0.17395 | 0.46234 | -0.20142 | 0.31128 | 0.17853 | 0.24719 | 0.091553 | 0.44861 | 0.50812 | -0.14191 | 120.694 | 0.091552 | 121.0693 | 121.2067 | -0.19226 | 120.7535 | 0.13733 | 0.37537 | 120.9869 | 121.344 | 121.0739 | 121.3577 | 121.0693 | 121.4035 | 121.1426 | 120.7535 | 121.3577 | 121.0693 | 121.1426 | 121.0739 | 121.4035 | -0.5722 | -0.5127
1797.5625 | 121.2845 | -120.8633 | 0.33875 | 0.0045011 | 0.017092 | 0.0063125 | 0.014494 | -0.0097413 | -0.0060028 | 0.014734 | 0.21057 | 0.4303 | -0.17853 | 0.35706 | 0.25177 | 0.31586 | 0.022888 | 0.51727 | 0.46692 | -0.12817 | 120.6848 | 0.091553 | 121.0739 | 121.2204 | -0.086975 | 120.7352 | 0.12817 | 0.3891 | 120.8862 | 121.3806 | 121.1151 | 121.2936 | 121.0739 | 121.3303 | 121.1792 | 120.7352 | 121.2936 | 121.0739 | 121.1792 | 121.1151 | 121.3303 | -0.51727 | -0.46692
1799.2656 | 121.3257 | -120.8679 | 0.37079 | 0.0045011 | 0.020296 | 0.0046037 | 0.015349 | -0.0099549 | -0.00643 | 0.011743 | 0.2243 | 0.44861 | -0.15106 | 0.36163 | 0.24261 | 0.32959 | 0.027466 | 0.52643 | 0.48065 | -0.11902 | 120.7169 | 0.077819 | 121.0922 | 121.2296 | -0.12817 | 120.7489 | 0.10986 | 0.37537 | 120.8954 | 121.3943 | 121.1105 | 121.3165 | 121.0922 | 121.3486 | 121.1975 | 120.7489 | 121.3165 | 121.0922 | 121.1975 | 121.1105 | 121.3486 | -0.52185 | -0.48981
1801.0312 | 121.376 | -120.8633 | 0.32044 | -0.010757 | 0.019015 | 0.00011747 | 0.015776 | -0.0065369 | -0.0040802 | 0.013025 | 0.1831 | 0.46692 | -0.15106 | 0.29755 | 0.19684 | 0.27924 | 0.041199 | 0.46692 | 0.48523 | -0.11444 | 120.7123 | 0.14648 | 121.0464 | 121.1609 | -0.1236 | 120.7489 | 0.16479 | 0.33417 | 120.9045 | 121.3303 | 121.0602 | 121.3303 | 121.0464 | 121.3486 | 121.1426 | 120.7489 | 121.3303 | 121.0464 | 121.1426 | 121.0602 | 121.3486 | -0.4715 | -0.43488
1802.7656 | 121.376 | -120.8817 | 0.32959 | 0.0045011 | 0.018587 | 0.0039627 | 0.015349 | -0.010382 | -0.0034394 | 0.014306 | 0.16479 | 0.43488 | -0.16022 | 0.31586 | 0.21057 | 0.30212 | 0.027466 | 0.46234 | 0.47607 | -0.1236 | 120.7214 | 0.10529 | 121.0464 | 121.1975 | -0.11902 | 120.7581 | 0.14648 | 0.32501 | 120.9091 | 121.344 | 121.0922 | 121.3165 | 121.0464 | 121.3577 | 121.1838 | 120.7581 | 121.3165 | 121.0464 | 121.1838 | 121.0922 | 121.3577 | -0.48981 | -0.45319
1804.4531 | 121.3211 | -120.9366 | 0.36621 | 0.0045011 | 0.02051 | 0.0046037 | 0.02133 | -0.0073913 | -0.0068574 | 0.013879 | 0.13275 | 0.47607 | -0.17853 | 0.2655 | 0.11902 | 0.19684 | 0.15564 | 0.37537 | 0.51727 | -0.1236 | 120.7581 | 0.10986 | 121.0693 | 121.2021 | -0.24719 | 120.813 | 0.15106 | 0.31128 | 121.0922 | 121.3119 | 121.0556 | 121.4127 | 121.0693 | 121.4539 | 121.1334 | 120.813 | 121.4127 | 121.0693 | 121.1334 | 121.0556 | 121.4539 | -0.54474 | -0.48981
1806.2031 | 121.3303 | -120.932 | 0.36163 | 0.0045011 | 0.021792 | 0.0075943 | 0.018553 | -0.0067505 | -0.0074982 | 0.014093 | 0.13733 | 0.48065 | -0.19226 | 0.25635 | 0.16022 | 0.21515 | 0.11444 | 0.38452 | 0.52185 | -0.13275 | 120.7397 | 0.11902 | 121.0693 | 121.1884 | -0.20142 | 120.7993 | 0.16022 | 0.32959 | 121.0464 | 121.3165 | 121.0922 | 121.4127 | 121.0693 | 121.4539 | 121.1472 | 120.7993 | 121.4127 | 121.0693 | 121.1472 | 121.0922 | 121.4539 | -0.55389 | -0.49438
1807.9688 | 121.431 | -120.9503 | 0.35706 | 0.012131 | 0.020296 | 0.0035355 | 0.017699 | -0.0095277 | -0.0083526 | 0.014093 | 0.1236 | 0.48523 | -0.19684 | 0.25635 | 0.16022 | 0.20599 | 0.19684 | 0.40741 | 0.51727 | -0.16022 | 120.7535 | 0.12817 | 121.0739 | 121.2067 | -0.19684 | 120.7901 | 0.16022 | 0.32043 | 121.1472 | 121.3577 | 121.1105 | 121.4355 | 121.0739 | 121.4676 | 121.1563 | 120.7901 | 121.4355 | 121.0739 | 121.1563 | 121.1105 | 121.4676 | -0.55389 | -0.51727
1809.7188 | 121.4035 | -120.9595 | 0.35706 | 0.012131 | 0.019442 | 0.0026809 | 0.012358 | -0.0086731 | -0.004721 | 0.013452 | 0.25177 | 0.44403 | -0.15106 | 0.40741 | 0.30212 | 0.36163 | 0.004578 | 0.55847 | 0.48065 | -0.10071 | 120.8084 | 0.086975 | 121.2112 | 121.3669 | -0.054932 | 120.8588 | 0.1236 | 0.40283 | 120.9641 | 121.5179 | 121.2616 | 121.4035 | 121.2112 | 121.4401 | 121.3211 | 120.8588 | 121.4035 | 121.2112 | 121.3211 | 121.2616 | 121.4401 | -0.50812 | -0.45776
1811.4688 | 121.4539 | -120.9778 | 0.35706 | 0.0045011 | 0.019869 | -9.6132e-05 | 0.019621 | -0.0054687 | -0.0096344 | 0.012384 | 0.16022 | 0.45776 | -0.20142 | 0.29297 | 0.17395 | 0.23346 | 0.19684 | 0.4303 | 0.53101 | -0.14648 | 120.7764 | 0.10071 | 121.138 | 121.2708 | -0.18311 | 120.8313 | 0.17395 | 0.36163 | 121.1746 | 121.4081 | 121.1517 | 121.4355 | 121.138 | 121.5088 | 121.2112 | 120.8313 | 121.4355 | 121.138 | 121.2112 | 121.1517 | 121.5088 | -0.55847 | -0.50354
1813.1562 | 121.3715 | -121.0144 | 0.39825 | -0.0031279 | 0.022433 | 0.0037491 | 0.018767 | -0.0065369 | -0.0096344 | 0.013879 | 0.19684 | 0.4715 | -0.17853 | 0.32044 | 0.1831 | 0.25635 | 0.11902 | 0.46234 | 0.51727 | -0.12817 | 120.8359 | 0.073243 | 121.2112 | 121.3348 | -0.21515 | 120.8862 | 0.11902 | 0.37537 | 121.1334 | 121.4767 | 121.1975 | 121.4859 | 121.2112 | 121.5317 | 121.2708 | 120.8862 | 121.4859 | 121.2112 | 121.2708 | 121.1975 | 121.5317 | -0.57678 | -0.52643
1814.9062 | 121.4813 | -121.019 | 0.32959 | -0.010757 | 0.022219 | 0.0020401 | 0.01663 | -0.0069641 | -0.00643 | 0.013665 | 0.20142 | 0.45319 | -0.15564 | 0.32501 | 0.21515 | 0.2655 | 0.14648 | 0.48065 | 0.51727 | -0.12817 | 120.8633 | 0.1236 | 121.2204 | 121.344 | -0.11444 | 120.8908 | 0.18768 | 0.35706 | 121.1655 | 121.4996 | 121.2341 | 121.4722 | 121.2204 | 121.5363 | 121.2845 | 120.8908 | 121.4722 | 121.2204 | 121.2845 | 121.2341 | 121.5363 | -0.48523 | -0.45776
1816.6406 | 121.3898 | -121.051 | 0.37537 | -0.0031279 | 0.022433 | 0.0065263 | 0.019621 | -0.0048279 | -0.0094208 | 0.013238 | 0.18768 | 0.48065 | -0.19226 | 0.27924 | 0.15564 | 0.21515 | 0.12817 | 0.40283 | 0.52185 | -0.13275 | 120.8588 | 0.10529 | 121.2387 | 121.3303 | -0.21973 | 120.9183 | 0.14648 | 0.37994 | 121.1792 | 121.4539 | 121.2067 | 121.5317 | 121.2387 | 121.5729 | 121.2662 | 120.9183 | 121.5317 | 121.2387 | 121.2662 | 121.2067 | 121.5729 | -0.56763 | -0.50812
1818.3906 | 121.4722 | -121.0464 | 0.34332 | 0.0045011 | 0.020083 | 0.0046037 | 0.012572 | -0.0099549 | -0.0085664 | 0.013025 | 0.26093 | 0.43945 | -0.13733 | 0.3891 | 0.27924 | 0.34332 | 0.027466 | 0.56305 | 0.4715 | -0.11444 | 120.9091 | 0.09613 | 121.3074 | 121.4355 | -0.064087 | 120.932 | 0.12817 | 0.39825 | 121.0739 | 121.6095 | 121.3257 | 121.4859 | 121.3074 | 121.5179 | 121.3898 | 120.932 | 121.4859 | 121.3074 | 121.3898 | 121.3257 | 121.5179 | -0.48065 | -0.45776
1820.1406 | 121.4264 | -121.0693 | 0.39368 | 0.0045011 | 0.02051 | 0.0054581 | 0.020476 | -0.0061097 | -0.0068574 | 0.014947 | 0.20142 | 0.44861 | -0.16022 | 0.33417 | 0.21973 | 0.28839 | 0.018311 | 0.47607 | 0.49896 | -0.11444 | 120.9091 | 0.054931 | 121.2708 | 121.4035 | -0.17395 | 120.9549 | 0.10529 | 0.36163 | 121.0876 | 121.5454 | 121.2891 | 121.5179 | 121.2708 | 121.5683 | 121.3577 | 120.9549 | 121.5179 | 121.2708 | 121.3577 | 121.2891 | 121.5683 | -0.55389 | -0.50812
1821.8906 | 121.5134 | -121.0419 | 0.37994 | 0.0045011 | 0.019656 | 0.0069535 | 0.015562 | -0.0097413 | -0.005362 | 0.011102 | 0.24719 | 0.45776 | -0.13275 | 0.38452 | 0.27466 | 0.3479 | 0.041199 | 0.56305 | 0.49896 | -0.10071 | 120.9091 | 0.07782 | 121.2891 | 121.4264 | -0.10529 | 120.9412 | 0.11902 | 0.37994 | 121.0831 | 121.6049 | 121.3165 | 121.4996 | 121.2891 | 121.5408 | 121.3898 | 120.9412 | 121.4996 | 121.2891 | 121.3898 | 121.3165 | 121.5408 | -0.5127 | -0.48065
1823.5625 | 121.4813 | -121.0693 | 0.38452 | 0.012131 | 0.021578 | 0.0013993 | 0.019835 | -0.0080323 | -0.009848 | 0.01452 | 0.14648 | 0.48523 | -0.17853 | 0.28839 | 0.16022 | 0.25635 | 0.082397 | 0.41199 | 0.53101 | -0.10986 | 120.8908 | 0.10071 | 121.2158 | 121.3577 | -0.2243 | 120.9595 | 0.14648 | 0.32501 | 121.1517 | 121.4813 | 121.2296 | 121.5546 | 121.2158 | 121.6003 | 121.3257 | 120.9595 | 121.5546 | 121.2158 | 121.3257 | 121.2296 | 121.6003 | -0.56305 | -0.49438
1825.3281 | 121.582 | -121.0373 | 0.3479 | 0.0045011 | 0.022219 | 0.0043899 | 0.016417 | -0.0073913 | -0.008139 | 0.011956 | 0.13733 | 0.48523 | -0.18768 | 0.2655 | 0.17853 | 0.19684 | 0.20599 | 0.42114 | 0.54474 | -0.14191 | 120.8496 | 0.13733 | 121.1746 | 121.3028 | -0.16937 | 120.8954 | 0.19684 | 0.32501 | 121.2433 | 121.4584 | 121.2158 | 121.5225 | 121.1746 | 121.582 | 121.2341 | 120.8954 | 121.5225 | 121.1746 | 121.2341 | 121.2158 | 121.582 | -0.53558 | -0.48981
1827.0781 | 121.5866 | -121.0968 | 0.36163 | 0.0045011 | 0.019656 | 0.0043899 | 0.017271 | -0.0067505 | -0.0057892 | 0.013025 | 0.11902 | 0.48523 | -0.18768 | 0.28381 | 0.16022 | 0.21515 | 0.1831 | 0.42572 | 0.54016 | -0.15106 | 120.9091 | 0.1236 | 121.2158 | 121.3806 | -0.20142 | 120.9457 | 0.17853 | 0.3067 | 121.2799 | 121.5225 | 121.257 | 121.582 | 121.2158 | 121.637 | 121.312 | 120.9457 | 121.582 | 121.2158 | 121.312 | 121.257 | 121.637 | -0.54932 | -0.5127
1828.75 | 121.5271 | -121.1334 | 0.37994 | 0.012131 | 0.01816 | 0.0075943 | 0.018339 | -0.0067505 | -0.0062164 | 0.015588 | 0.13733 | 0.47607 | -0.19684 | 0.21515 | 0.1236 | 0.20142 | 0.17395 | 0.35248 | 0.52185 | -0.15106 | 120.9366 | 0.09613 | 121.2708 | 121.3486 | -0.25635 | 120.9824 | 0.14191 | 0.33417 | 121.3074 | 121.4859 | 121.257 | 121.6095 | 121.2708 | 121.6553 | 121.3348 | 120.9824 | 121.6095 | 121.2708 | 121.3348 | 121.257 | 121.6553 | -0.57678 | -0.53101
1830.5156 | 121.6507 | -121.1197 | 0.33417 | 0.012131 | 0.018801 | -0.00052333 | 0.014281 | -0.0086731 | -0.007071 | 0.013238 | 0.10529 | 0.49439 | -0.20142 | 0.26093 | 0.15564 | 0.20599 | 0.21515 | 0.40283 | 0.52643 | -0.16479 | 120.9183 | 0.16022 | 121.225 | 121.3806 | -0.17853 | 120.9549 | 0.19226 | 0.3067 | 121.3348 | 121.5225 | 121.2753 | 121.6141 | 121.225 | 121.6461 | 121.3257 | 120.9549 | 121.6141 | 121.225 | 121.3257 | 121.2753 | 121.6461 | -0.53558 | -0.49896
1832.2031 | 121.4996 | -121.17 | 0.36163 | 0.0045011 | 0.019656 | 0.0039627 | 0.014921 | -0.0069641 | -0.0068574 | 0.014306 | 0.23804 | 0.42114 | -0.15106 | 0.35706 | 0.25635 | 0.33875 | -0.041199 | 0.52643 | 0.48065 | -0.091553 | 121.019 | 0.05951 | 121.4081 | 121.5271 | -0.10528 | 121.0785 | 0.11902 | 0.3891 | 121.1288 | 121.6965 | 121.4264 | 121.5912 | 121.4081 | 121.6507 | 121.5088 | 121.0785 | 121.5912 | 121.4081 | 121.5088 | 121.4264 | 121.6507 | -0.5127 | -0.45319
1833.9531 | 121.6278 | -121.138 | 0.35706 | -0.0031279 | 0.019228 | 0.00097207 | 0.017912 | -0.0088867 | -0.0083526 | 0.012384 | 0.21515 | 0.45319 | -0.14191 | 0.32959 | 0.21515 | 0.28381 | 0.13733 | 0.50354 | 0.50354 | -0.1236 | 120.9961 | 0.09613 | 121.3531 | 121.4676 | -0.14191 | 121.0144 | 0.14648 | 0.35706 | 121.2753 | 121.6415 | 121.3531 | 121.5912 | 121.3531 | 121.6415 | 121.4218 | 121.0144 | 121.5912 | 121.3531 | 121.4218 | 121.3531 | 121.6415 | -0.49896 | -0.48065
1835.7031 | 121.5866 | -121.1655 | 0.37994 | -0.0031279 | 0.01816 | 0.0052445 | 0.014708 | -0.010382 | -0.0038666 | 0.012811 | 0.20142 | 0.42572 | -0.16479 | 0.32501 | 0.22888 | 0.31586 | 0.022888 | 0.4715 | 0.48065 | -0.09613 | 121.0007 | 0.045776 | 121.3669 | 121.4905 | -0.15106 | 121.0693 | 0.10071 | 0.36621 | 121.1884 | 121.637 | 121.3943 | 121.5912 | 121.3669 | 121.6461 | 121.4813 | 121.0693 | 121.5912 | 121.3669 | 121.4813 | 121.3943 | 121.6461 | -0.54474 | -0.47607
1837.4375 | 121.6736 | -121.1609 | 0.3479 | 0.0045011 | 0.017519 | 0.0031083 | 0.017271 | -0.012305 | -0.0042938 | 0.014947 | 0.18768 | 0.43945 | -0.14648 | 0.32044 | 0.20599 | 0.30212 | 0.054932 | 0.48065 | 0.50812 | -0.11444 | 121.0144 | 0.091553 | 121.3486 | 121.4813 | -0.14191 | 121.0464 | 0.16022 | 0.33417 | 121.2158 | 121.6415 | 121.3669 | 121.6003 | 121.3486 | 121.669 | 121.463 | 121.0464 | 121.6003 | 121.3486 | 121.463 | 121.3669 | 121.669 | -0.49438 | -0.46234
1839.125 | 121.6187 | -121.1929 | 0.37994 | 0.0045011 | 0.021151 | 0.0058853 | 0.022185 | -0.0095277 | -0.0045074 | 0.014306 | 0.13275 | 0.48981 | -0.19684 | 0.26093 | 0.13275 | 0.20599 | 0.14648 | 0.37079 | 0.51727 | -0.1236 | 120.9961 | 0.10986 | 121.3257 | 121.4539 | -0.24719 | 121.0693 | 0.13733 | 0.32959 | 121.3394 | 121.5637 | 121.3257 | 121.6827 | 121.3257 | 121.7102 | 121.3989 | 121.0693 | 121.6827 | 121.3257 | 121.3989 | 121.3257 | 121.7102 | -0.57678 | -0.50354
1840.8906 | 121.6415 | -121.2112 | 0.37079 | -0.0031279 | 0.021792 | 0.0028947 | 0.020903 | -0.010382 | -0.0057892 | 0.011102 | 0.15106 | 0.46234 | -0.20142 | 0.29755 | 0.19226 | 0.22888 | 0.17853 | 0.46234 | 0.5127 | -0.1236 | 121.0098 | 0.091552 | 121.3623 | 121.5088 | -0.17853 | 121.0876 | 0.14191 | 0.35248 | 121.3898 | 121.6736 | 121.4035 | 121.6736 | 121.3623 | 121.7239 | 121.4401 | 121.0876 | 121.6736 | 121.3623 | 121.4401 | 121.4035 | 121.7239 | -0.5722 | -0.49438
1842.6406 | 121.582 | -121.2341 | 0.37537 | 0.0045011 | 0.019015 | 0.0067399 | 0.01898 | -0.0056823 | -0.0066438 | 0.013879 | 0.16937 | 0.45319 | -0.20142 | 0.28839 | 0.18768 | 0.25635 | 0.041199 | 0.42114 | 0.52643 | -0.1236 | 121.0327 | 0.07782 | 121.4035 | 121.5225 | -0.18768 | 121.1105 | 0.15106 | 0.37079 | 121.2753 | 121.6553 | 121.4218 | 121.6873 | 121.4035 | 121.7606 | 121.4905 | 121.1105 | 121.6873 | 121.4035 | 121.4905 | 121.4218 | 121.7606 | -0.57678 | -0.49896
1844.3281 | 121.6644 | -121.2158 | 0.3479 | 0.0045011 | 0.021151 | 0.0033219 | 0.013213 | -0.0088867 | -0.0032258 | 0.013238 | 0.22888 | 0.44861 | -0.13733 | 0.37537 | 0.27466 | 0.32959 | 0.036621 | 0.54016 | 0.48065 | -0.10071 | 121.0785 | 0.10071 | 121.4447 | 121.5912 | -0.073242 | 121.1151 | 0.13275 | 0.36621 | 121.2524 | 121.756 | 121.4905 | 121.6644 | 121.4447 | 121.6965 | 121.5454 | 121.1151 | 121.6644 | 121.4447 | 121.5454 | 121.4905 | 121.6965 | -0.48523 | -0.44861
1846.0781 | 121.6324 | -121.2616 | 0.37537 | -0.0031279 | 0.020724 | 0.0054581 | 0.021117 | -0.0069641 | -0.0066438 | 0.013025 | 0.11444 | 0.46692 | -0.1831 | 0.27008 | 0.1236 | 0.17853 | 0.13733 | 0.36621 | 0.52185 | -0.14191 | 121.0785 | 0.091553 | 121.376 | 121.5317 | -0.25177 | 121.1197 | 0.14648 | 0.29755 | 121.3989 | 121.6278 | 121.3852 | 121.7285 | 121.376 | 121.7834 | 121.4401 | 121.1197 | 121.7285 | 121.376 | 121.4401 | 121.3852 | 121.7834 | -0.55847 | -0.51727
1847.8281 | 121.6827 | -121.2708 | 0.35706 | -0.0031279 | 0.019869 | 0.0031083 | 0.014708 | -0.0097413 | -0.0045074 | 0.01217 | 0.21973 | 0.4303 | -0.15564 | 0.37079 | 0.25177 | 0.32501 | 0.013733 | 0.54474 | 0.4715 | -0.12817 | 121.1151 | 0.073242 | 121.4905 | 121.6415 | -0.10529 | 121.1426 | 0.11444 | 0.37537 | 121.2845 | 121.8155 | 121.5225 | 121.701 | 121.4905 | 121.7422 | 121.5958 | 121.1426 | 121.701 | 121.4905 | 121.5958 | 121.5225 | 121.7422 | -0.5127 | -0.48523
1849.5156 | 121.7422 | -121.2616 | 0.31586 | 0.012131 | 0.015597 | 0.0056717 | 0.014921 | -0.0086731 | -0.0051484 | 0.014093 | 0.14648 | 0.41657 | -0.16479 | 0.29755 | 0.20599 | 0.27466 | 0.036621 | 0.46692 | 0.50354 | -0.1236 | 121.0968 | 0.10071 | 121.4081 | 121.5591 | -0.10986 | 121.138 | 0.18768 | 0.31128 | 121.2982 | 121.7285 | 121.4676 | 121.6782 | 121.4081 | 121.7651 | 121.5363 | 121.138 | 121.6782 | 121.4081 | 121.5363 | 121.4676 | 121.7651 | -0.48065 | -0.43945
1851.2031 | 121.6324 | -121.312 | 0.34332 | 0.0045011 | 0.020083 | 0.0050309 | 0.017699 | -0.0080323 | -0.0055756 | 0.013025 | 0.2243 | 0.41657 | -0.16937 | 0.36163 | 0.21515 | 0.31128 | -0.032043 | 0.4715 | 0.45776 | -0.12817 | 121.1426 | 0.073242 | 121.5363 | 121.6736 | -0.12817 | 121.1838 | 0.11444 | 0.39368 | 121.2799 | 121.7834 | 121.5271 | 121.7285 | 121.5363 | 121.7697 | 121.6232 | 121.1838 | 121.7285 | 121.5363 | 121.6232 | 121.5271 | 121.7697 | -0.5127 | -0.4715
1852.9531 | 121.7422 | -121.3211 | 0.33417 | 0.012131 | 0.022005 | 0.0043899 | 0.01663 | -0.010596 | -0.0074982 | 0.01452 | 0.23346 | 0.40741 | -0.17853 | 0.35248 | 0.22888 | 0.28839 | 0.050354 | 0.51727 | 0.47607 | -0.13733 | 121.1426 | 0.073243 | 121.5546 | 121.6736 | -0.10528 | 121.1838 | 0.14191 | 0.41199 | 121.3715 | 121.8384 | 121.55 | 121.7285 | 121.5546 | 121.7972 | 121.6095 | 121.1838 | 121.7285 | 121.5546 | 121.6095 | 121.55 | 121.7972 | -0.5127 | -0.4715
1854.7031 | 121.6461 | -121.3577 | 0.36163 | -0.0031279 | 0.019442 | 0.0013993 | 0.019621 | -0.0073913 | -0.0072846 | 0.01452 | 0.19226 | 0.41199 | -0.17395 | 0.34332 | 0.19226 | 0.28839 | -0.027466 | 0.4715 | 0.45319 | -0.13733 | 121.1838 | 0.050354 | 121.55 | 121.701 | -0.16937 | 121.2204 | 0.091553 | 0.36621 | 121.3303 | 121.8292 | 121.55 | 121.7697 | 121.55 | 121.8109 | 121.6461 | 121.2204 | 121.7697 | 121.55 | 121.6461 | 121.55 | 121.8109 | -0.53558 | -0.49896
1856.4531 | 121.7239 | -121.3531 | 0.32501 | 0.012131 | 0.02051 | 0.0080215 | 0.015349 | -0.0063233 | -0.0066438 | 0.014093 | 0.21515 | 0.39368 | -0.16479 | 0.35706 | 0.24719 | 0.31586 | 0 | 0.53558 | 0.44403 | -0.14191 | 121.1884 | 0.068665 | 121.5683 | 121.7102 | -0.07782 | 121.2112 | 0.11902 | 0.37994 | 121.3531 | 121.8887 | 121.6003 | 121.7468 | 121.5683 | 121.7972 | 121.669 | 121.2112 | 121.7468 | 121.5683 | 121.669 | 121.6003 | 121.7972 | -0.48981 | -0.46692
1858.1406 | 121.756 | -121.3348 | 0.32044 | -0.0031279 | 0.019442 | -0.0035141 | 0.015135 | -0.0091003 | -0.004721 | 0.011956 | 0.20599 | 0.40741 | -0.16479 | 0.37079 | 0.24719 | 0.31128 | -0.013733 | 0.52185 | 0.46234 | -0.15106 | 121.17 | 0.086975 | 121.5408 | 121.7056 | -0.073243 | 121.1838 | 0.14191 | 0.37079 | 121.3211 | 121.8567 | 121.582 | 121.7422 | 121.5408 | 121.7972 | 121.6461 | 121.1838 | 121.7422 | 121.5408 | 121.6461 | 121.582 | 121.7972 | -0.48523 | -0.4715
1859.8906 | 121.7331 | -121.3852 | 0.35706 | 0.0045011 | 0.019228 | 0.0031083 | 0.023039 | -0.0091003 | -0.0062164 | 0.014306 | 0.10071 | 0.44861 | -0.21515 | 0.23804 | 0.09613 | 0.16479 | 0.11902 | 0.32044 | 0.48981 | -0.17395 | 121.17 | 0.091552 | 121.4859 | 121.6232 | -0.26093 | 121.2112 | 0.13275 | 0.31586 | 121.5042 | 121.7056 | 121.4813 | 121.8338 | 121.4859 | 121.875 | 121.55 | 121.2112 | 121.8338 | 121.4859 | 121.55 | 121.4813 | 121.875 | -0.5722 | -0.53101
1861.6406 | 121.8018 | -121.3531 | 0.29297 | 0.0045011 | 0.021151 | 0.0041763 | 0.012358 | -0.0093139 | -0.0034394 | 0.015374 | 0.16937 | 0.41199 | -0.18768 | 0.32501 | 0.2243 | 0.29297 | -0.004578 | 0.49439 | 0.46692 | -0.15106 | 121.1655 | 0.11902 | 121.5225 | 121.6782 | -0.068665 | 121.2021 | 0.17395 | 0.35706 | 121.3486 | 121.8475 | 121.5775 | 121.7651 | 121.5225 | 121.8201 | 121.6461 | 121.2021 | 121.7651 | 121.5225 | 121.6461 | 121.5775 | 121.8201 | -0.48065 | -0.44403
1863.4062 | 121.7834 | -121.4035 | 0.32501 | 0.0045011 | 0.020296 | -0.00030973 | 0.022185 | -0.0067505 | -0.0077118 | 0.012384 | 0.12817 | 0.43488 | -0.2243 | 0.27466 | 0.15106 | 0.20599 | 0.10071 | 0.42114 | 0.48981 | -0.16022 | 121.1792 | 0.10986 | 121.5317 | 121.6782 | -0.17395 | 121.2433 | 0.16479 | 0.35248 | 121.5042 | 121.8246 | 121.5546 | 121.8384 | 121.5317 | 121.8933 | 121.6095 | 121.2433 | 121.8384 | 121.5317 | 121.6095 | 121.5546 | 121.8933 | -0.54932 | -0.48523
1865.1094 | 121.7377 | -121.4447 | 0.33875 | -0.0031279 | 0.021365 | 0.0084489 | 0.020476 | -0.0037597 | -0.0079254 | 0.014306 | 0.11902 | 0.41657 | -0.21973 | 0.2243 | 0.10529 | 0.14648 | 0.11902 | 0.37079 | 0.47607 | -0.15564 | 121.225 | 0.07782 | 121.5637 | 121.669 | -0.23346 | 121.2891 | 0.13733 | 0.33875 | 121.5637 | 121.8155 | 121.55 | 121.8613 | 121.5637 | 121.9208 | 121.5912 | 121.2891 | 121.8613 | 121.5637 | 121.5912 | 121.55 | 121.9208 | -0.55847 | -0.49439
1866.8594 | 121.7102 | -121.4447 | 0.3479 | 0.0045011 | 0.022646 | 0.0031083 | 0.019835 | -0.0058961 | -0.0089936 | 0.014306 | 0.15564 | 0.41657 | -0.21057 | 0.28381 | 0.15106 | 0.21057 | 0.068665 | 0.40741 | 0.48065 | -0.15564 | 121.2341 | 0.068665 | 121.6003 | 121.7285 | -0.19684 | 121.2891 | 0.13275 | 0.36621 | 121.5134 | 121.8521 | 121.5958 | 121.8613 | 121.6003 | 121.9254 | 121.6553 | 121.2891 | 121.8613 | 121.6003 | 121.6553 | 121.5958 | 121.9254 | -0.55847 | -0.50354
1868.5469 | 121.8475 | -121.3898 | 0.3067 | 0.0045011 | 0.020724 | 0.0056717 | 0.015135 | -0.0099549 | -0.0083526 | 0.01452 | 0.10071 | 0.43945 | -0.23804 | 0.22888 | 0.12817 | 0.17853 | 0.16022 | 0.37079 | 0.49896 | -0.18768 | 121.1517 | 0.13275 | 121.4905 | 121.6187 | -0.17853 | 121.2021 | 0.19226 | 0.33875 | 121.55 | 121.7606 | 121.5179 | 121.8292 | 121.4905 | 121.8887 | 121.5683 | 121.2021 | 121.8292 | 121.4905 | 121.5683 | 121.5179 | 121.8887 | -0.54474 | -0.49438
1870.3125 | 121.7239 | -121.4722 | 0.32959 | 0.012131 | 0.018374 | 0.0052445 | 0.014921 | -0.0065369 | -0.0068574 | 0.014306 | 0.19226 | 0.39825 | -0.19226 | 0.32044 | 0.21973 | 0.30212 | -0.073242 | 0.47607 | 0.44861 | -0.1236 | 121.2799 | 0.068664 | 121.6644 | 121.7926 | -0.10986 | 121.3486 | 0.11902 | 0.38452 | 121.3989 | 121.9482 | 121.6919 | 121.8704 | 121.6644 | 121.9208 | 121.7743 | 121.3486 | 121.8704 | 121.6644 | 121.7743 | 121.6919 | 121.9208 | -0.52185 | -0.45319
1872 | 121.8109 | -121.4539 | 0.31128 | 0.0045011 | 0.02051 | 0.0078079 | 0.021117 | -0.0088867 | -0.007071 | 0.012384 | 0.068665 | 0.44403 | -0.23804 | 0.21515 | 0.10986 | 0.16479 | 0.10071 | 0.32044 | 0.48065 | -0.17853 | 121.2158 | 0.13275 | 121.5225 | 121.669 | -0.20142 | 121.2753 | 0.16937 | 0.3067 | 121.5546 | 121.7743 | 121.5637 | 121.8979 | 121.5225 | 121.9345 | 121.6187 | 121.2753 | 121.8979 | 121.5225 | 121.6187 | 121.5637 | 121.9345 | -0.54932 | -0.48981
1873.7344 | 121.7514 | -121.4813 | 0.31586 | 0.012131 | 0.019228 | 0.0041763 | 0.01663 | -0.0082459 | -0.007071 | 0.01452 | 0.19226 | 0.37994 | -0.20599 | 0.31128 | 0.21515 | 0.32044 | -0.073242 | 0.4715 | 0.43488 | -0.15564 | 121.2753 | 0.064087 | 121.6736 | 121.7926 | -0.10071 | 121.3257 | 0.11902 | 0.39826 | 121.4081 | 121.9528 | 121.6965 | 121.8613 | 121.6736 | 121.9162 | 121.8018 | 121.3257 | 121.8613 | 121.6736 | 121.8018 | 121.6965 | 121.9162 | -0.52185 | -0.4715
1875.5 | 121.7697 | -121.4859 | 0.32501 | 0.012131 | 0.021578 | 0.0035355 | 0.018126 | -0.0078187 | -0.0062164 | 0.013665 | 0.14648 | 0.41199 | -0.2243 | 0.2655 | 0.15564 | 0.21515 | 0.059509 | 0.41199 | 0.46234 | -0.16022 | 121.2616 | 0.086975 | 121.6324 | 121.7514 | -0.16937 | 121.3257 | 0.13733 | 0.37079 | 121.5454 | 121.8979 | 121.6415 | 121.8979 | 121.6324 | 121.9482 | 121.701 | 121.3257 | 121.8979 | 121.6324 | 121.701 | 121.6415 | 121.9482 | -0.54932 | -0.48523
1877.1875 | 121.8475 | -121.4584 | 0.31128 | -0.0031279 | 0.017092 | 0.0011857 | 0.014067 | -0.0073913 | -0.0083526 | 0.014093 | 0.19226 | 0.37079 | -0.19684 | 0.32959 | 0.2243 | 0.30212 | -0.004578 | 0.49896 | 0.44861 | -0.17395 | 121.2616 | 0.05951 | 121.6507 | 121.788 | -0.086975 | 121.2845 | 0.13733 | 0.3891 | 121.4539 | 121.9574 | 121.6827 | 121.8292 | 121.6507 | 121.907 | 121.7606 | 121.2845 | 121.8292 | 121.6507 | 121.7606 | 121.6827 | 121.907 | -0.50812 | -0.48523
1878.9219 | 121.9254 | -121.4767 | 0.30212 | 0.0045011 | 0.022433 | 0.00097207 | 0.017058 | -0.0086731 | -0.004721 | 0.014306 | 0.091553 | 0.44403 | -0.2243 | 0.21515 | 0.10529 | 0.14191 | 0.17395 | 0.37079 | 0.4715 | -0.18768 | 121.2524 | 0.14191 | 121.5683 | 121.6919 | -0.19684 | 121.2891 | 0.16937 | 0.31586 | 121.6507 | 121.8475 | 121.582 | 121.9208 | 121.5683 | 121.9482 | 121.6187 | 121.2891 | 121.9208 | 121.5683 | 121.6187 | 121.582 | 121.9482 | -0.52643 | -0.48981
1880.6719 | 121.8018 | -121.5225 | 0.32044 | 0.012131 | 0.019869 | 0.0058853 | 0.015776 | -0.0054687 | -0.0068574 | 0.013879 | 0.17853 | 0.37994 | -0.20142 | 0.32959 | 0.20599 | 0.30212 | -0.082397 | 0.46234 | 0.44861 | -0.13733 | 121.3211 | 0.059509 | 121.701 | 121.8521 | -0.11444 | 121.3852 | 0.12817 | 0.37994 | 121.4401 | 121.9849 | 121.7285 | 121.9025 | 121.701 | 121.9711 | 121.8246 | 121.3852 | 121.9025 | 121.701 | 121.8246 | 121.7285 | 121.9711 | -0.52185 | -0.45776
1882.3594 | 121.8155 | -121.5408 | 0.33875 | 0.012131 | 0.020083 | 0.0060989 | 0.020903 | -0.0080323 | -0.0089936 | 0.012811 | 0.14648 | 0.39825 | -0.24719 | 0.24261 | 0.13275 | 0.19684 | 0.091553 | 0.37537 | 0.46692 | -0.17853 | 121.2936 | 0.059509 | 121.6873 | 121.7834 | -0.20599 | 121.3623 | 0.12817 | 0.39368 | 121.6324 | 121.9162 | 121.6736 | 121.9391 | 121.6873 | 122.0078 | 121.7377 | 121.3623 | 121.9391 | 121.6873 | 121.7377 | 121.6736 | 122.0078 | -0.58594 | -0.51727
1884.1094 | 121.8109 | -121.5134 | 0.33875 | 0.012131 | 0.021365 | 0.0026809 | 0.016844 | -0.0048279 | -0.0060028 | 0.013238 | 0.16022 | 0.40283 | -0.20599 | 0.28839 | 0.1831 | 0.2655 | -0.045776 | 0.4303 | 0.43945 | -0.14648 | 121.3074 | 0.064087 | 121.6736 | 121.8018 | -0.15564 | 121.3669 | 0.10071 | 0.36621 | 121.4676 | 121.9437 | 121.6965 | 121.9162 | 121.6736 | 121.9528 | 121.7789 | 121.3669 | 121.9162 | 121.6736 | 121.7789 | 121.6965 | 121.9528 | -0.54474 | -0.48523
1885.875 | 121.9528 | -121.4813 | 0.29297 | 0.0045011 | 0.017306 | 0.0065263 | 0.016417 | -0.0093139 | -0.007071 | 0.014734 | 0.068665 | 0.43488 | -0.24719 | 0.20599 | 0.10529 | 0.16022 | 0.16937 | 0.35706 | 0.48523 | -0.16479 | 121.2341 | 0.14191 | 121.55 | 121.6873 | -0.18768 | 121.3165 | 0.19226 | 0.31586 | 121.6507 | 121.8384 | 121.5866 | 121.9162 | 121.55 | 121.9666 | 121.6415 | 121.3165 | 121.9162 | 121.55 | 121.6415 | 121.5866 | 121.9666 | -0.54016 | -0.45776
1888.9531 | 121.843 | -121.5729 | 0.33875 | 0.0045011 | 0.019869 | 0.0069535 | 0.017699 | -0.0056823 | -0.0072846 | 0.015161 | 0.15564 | 0.42572 | -0.23804 | 0.2655 | 0.14191 | 0.21973 | 0.086975 | 0.42572 | 0.46234 | -0.16022 | 121.3348 | 0.086975 | 121.7285 | 121.8384 | -0.19684 | 121.4127 | 0.1236 | 0.39368 | 121.6599 | 121.9986 | 121.7148 | 121.9986 | 121.7285 | 122.0352 | 121.7926 | 121.4127 | 121.9986 | 121.7285 | 121.7926 | 121.7148 | 122.0352 | -0.57678 | -0.49896
1892.9375 | 121.9803 | -121.55 | 0.3067 | 0.0045011 | 0.019442 | 0.0037491 | 0.017058 | -0.0076049 | -0.0057892 | 0.014947 | 0.054932 | 0.44403 | -0.22888 | 0.21973 | 0.10986 | 0.16479 | 0.17395 | 0.37994 | 0.46692 | -0.20142 | 121.3211 | 0.13733 | 121.6049 | 121.7697 | -0.19684 | 121.3486 | 0.16022 | 0.28381 | 121.7239 | 121.9299 | 121.6599 | 121.994 | 121.6049 | 122.0169 | 121.7148 | 121.3486 | 121.994 | 121.6049 | 121.7148 | 121.6599 | 122.0169 | -0.53558 | -0.50812
1899.2812 | 121.8933 | -121.5866 | 0.31586 | 0.0045011 | 0.019869 | 0.0016129 | 0.017271 | -0.0082459 | -0.0079254 | 0.014734 | 0.14648 | 0.3891 | -0.20142 | 0.27924 | 0.17853 | 0.27466 | -0.036621 | 0.44403 | 0.45319 | -0.15106 | 121.3852 | 0.073242 | 121.7331 | 121.8658 | -0.13733 | 121.4355 | 0.13733 | 0.3479 | 121.55 | 122.0306 | 121.7651 | 121.9757 | 121.7331 | 122.0398 | 121.8613 | 121.4355 | 121.9757 | 121.7331 | 121.8613 | 121.7651 | 122.0398 | -0.51727 | -0.46692
1900.9844 | 121.9345 | -121.6049 | 0.32959 | 0.012131 | 0.018587 | 0.0052445 | 0.01898 | -0.0084595 | -0.00643 | 0.016015 | 0.082397 | 0.43488 | -0.23804 | 0.19684 | 0.086975 | 0.16937 | 0.09613 | 0.32501 | 0.48523 | -0.1831 | 121.3669 | 0.10529 | 121.6873 | 121.8018 | -0.24261 | 121.4218 | 0.15564 | 0.32043 | 121.701 | 121.9299 | 121.6919 | 122.0398 | 121.6873 | 122.0901 | 121.7743 | 121.4218 | 122.0398 | 121.6873 | 121.7743 | 121.6919 | 122.0901 | -0.56763 | -0.5127
1902.75 | 122.0169 | -121.582 | 0.29297 | -0.0031279 | 0.02051 | 0.0043899 | 0.011717 | -0.0097413 | -0.0040802 | 0.014734 | 0.15106 | 0.38452 | -0.19684 | 0.27008 | 0.17853 | 0.24261 | -0.004578 | 0.42114 | 0.44403 | -0.16479 | 121.3852 | 0.091552 | 121.7331 | 121.8521 | -0.11444 | 121.4172 | 0.15106 | 0.3479 | 121.5775 | 122.0032 | 121.7606 | 121.9666 | 121.7331 | 122.0261 | 121.8246 | 121.4172 | 121.9666 | 121.7331 | 121.8246 | 121.7606 | 122.0261 | -0.48981 | -0.45776
1904.4375 | 121.9208 | -121.6232 | 0.32044 | 0.012131 | 0.021792 | 0.0056717 | 0.018553 | -0.0071777 | -0.0055756 | 0.013025 | 0.091553 | 0.40741 | -0.23346 | 0.21973 | 0.1236 | 0.20599 | 0.009155 | 0.36621 | 0.45319 | -0.17853 | 121.3898 | 0.086975 | 121.7148 | 121.843 | -0.19684 | 121.4447 | 0.13275 | 0.32501 | 121.6324 | 121.9894 | 121.7468 | 122.0306 | 121.7148 | 122.0764 | 121.8292 | 121.4447 | 122.0306 | 121.7148 | 121.8292 | 121.7468 | 122.0764 | -0.55389 | -0.49896
1906.125 | 121.9162 | -121.637 | 0.33417 | 0.0045011 | 0.019442 | 0.0058853 | 0.019835 | -0.0084595 | -0.0079254 | 0.013665 | 0.13275 | 0.42114 | -0.2243 | 0.27466 | 0.14648 | 0.21515 | 0.082397 | 0.41657 | 0.44861 | -0.17395 | 121.4127 | 0.086976 | 121.7697 | 121.9116 | -0.18768 | 121.463 | 0.11444 | 0.35706 | 121.7194 | 122.0535 | 121.7834 | 122.0581 | 121.7697 | 122.0856 | 121.8521 | 121.463 | 122.0581 | 121.7697 | 121.8521 | 121.7834 | 122.0856 | -0.55847 | -0.50812
1907.8906 | 122.049 | -121.5958 | 0.29297 | -0.0031279 | 0.017947 | 0.0018265 | 0.017912 | -0.0082459 | -0.00643 | 0.013452 | 0.07782 | 0.42572 | -0.24719 | 0.23346 | 0.11444 | 0.16479 | 0.15106 | 0.3891 | 0.46234 | -0.19684 | 121.3486 | 0.13275 | 121.6736 | 121.8292 | -0.17853 | 121.3989 | 0.16937 | 0.32501 | 121.7468 | 121.9849 | 121.7102 | 122.0215 | 121.6736 | 122.0581 | 121.7606 | 121.3989 | 122.0215 | 121.6736 | 121.7606 | 121.7102 | 122.0581 | -0.54016 | -0.48981
1909.6406 | 121.9299 | -121.6507 | 0.32959 | -0.010757 | 0.020937 | 0.0056717 | 0.018339 | -0.0084595 | -0.0057892 | 0.013665 | 0.13733 | 0.39825 | -0.20142 | 0.29297 | 0.18768 | 0.26093 | -0.041199 | 0.4303 | 0.4303 | -0.16479 | 121.4493 | 0.068664 | 121.788 | 121.9437 | -0.14191 | 121.4859 | 0.10071 | 0.33875 | 121.6095 | 122.081 | 121.8384 | 122.0489 | 121.788 | 122.081 | 121.9116 | 121.4859 | 122.0489 | 121.788 | 121.9116 | 121.8384 | 122.081 | -0.53101 | -0.49438
1911.3906 | 122.0764 | -121.6095 | 0.28381 | 0.012131 | 0.018801 | 0.0048173 | 0.016203 | -0.0073913 | -0.00878 | 0.01217 | 0.064087 | 0.42114 | -0.24719 | 0.20599 | 0.10071 | 0.15106 | 0.17853 | 0.36163 | 0.48523 | -0.17395 | 121.3623 | 0.13733 | 121.6736 | 121.8155 | -0.1831 | 121.4355 | 0.20142 | 0.31128 | 121.788 | 121.9711 | 121.7102 | 122.0306 | 121.6736 | 122.0947 | 121.7606 | 121.4355 | 122.0306 | 121.6736 | 121.7606 | 121.7102 | 122.0947 | -0.531 | -0.45776
1913.0781 | 122.0947 | -121.582 | 0.28839 | 0.0045011 | 0.02051 | 0.0031083 | 0.014494 | -0.0099549 | -0.0038666 | 0.012811 | 0.10529 | 0.4303 | -0.22888 | 0.21973 | 0.11902 | 0.17395 | 0.15106 | 0.3891 | 0.48065 | -0.17853 | 121.3531 | 0.14191 | 121.6873 | 121.8018 | -0.16937 | 121.4035 | 0.19226 | 0.33417 | 121.7331 | 121.9711 | 121.701 | 122.0123 | 121.6873 | 122.0627 | 121.756 | 121.4035 | 122.0123 | 121.6873 | 121.756 | 121.701 | 122.0627 | -0.51727 | -0.46692
1914.8125 | 122.0901 | -121.6141 | 0.27924 | -0.010757 | 0.022433 | 0.0063125 | 0.014281 | -0.0091003 | -0.0045074 | 0.013879 | 0.082397 | 0.41199 | -0.23346 | 0.21973 | 0.11902 | 0.15564 | 0.16479 | 0.37537 | 0.46692 | -0.1831 | 121.3806 | 0.13275 | 121.6965 | 121.8338 | -0.16022 | 121.431 | 0.18768 | 0.31586 | 121.7789 | 121.9894 | 121.7331 | 122.0261 | 121.6965 | 122.081 | 121.7697 | 121.431 | 122.0261 | 121.6965 | 121.7697 | 121.7331 | 122.081 | -0.5127 | -0.46234
1916.5781 | 122.0718 | -121.6278 | 0.32044 | -0.010757 | 0.01816 | 0.0075943 | 0.011931 | -0.0097413 | -0.004721 | 0.014093 | 0.14191 | 0.38452 | -0.18768 | 0.27924 | 0.16479 | 0.26093 | -0.004578 | 0.42572 | 0.44403 | -0.16479 | 121.4401 | 0.064086 | 121.7697 | 121.907 | -0.15564 | 121.463 | 0.1236 | 0.32959 | 121.6232 | 122.0535 | 121.7926 | 122.0123 | 121.7697 | 122.0718 | 121.8887 | 121.463 | 122.0123 | 121.7697 | 121.8887 | 121.7926 | 122.0718 | -0.50812 | -0.48523
1918.2656 | 121.9482 | -121.6827 | 0.34332 | -0.0031279 | 0.022005 | 0.0058853 | 0.01898 | -0.0097413 | -0.0057892 | 0.012811 | 0.21057 | 0.38452 | -0.19226 | 0.32501 | 0.21057 | 0.29755 | -0.09613 | 0.46692 | 0.44861 | -0.14191 | 121.4905 | 0.041198 | 121.8933 | 122.0078 | -0.13275 | 121.5408 | 0.10529 | 0.40283 | 121.5866 | 122.1497 | 121.8933 | 122.0673 | 121.8933 | 122.1313 | 121.9803 | 121.5408 | 122.0673 | 121.8933 | 121.9803 | 121.8933 | 122.1313 | -0.53558 | -0.48523
1920.0156 | 122.0627 | -121.6827 | 0.31128 | 0.0045011 | 0.021365 | 0.0069535 | 0.021757 | -0.0061097 | -0.0038666 | 0.014306 | 0.1236 | 0.4303 | -0.20599 | 0.26093 | 0.15106 | 0.20599 | 0.11902 | 0.41199 | 0.47607 | -0.19226 | 121.4767 | 0.11902 | 121.8063 | 121.9437 | -0.16022 | 121.4905 | 0.1648 | 0.32959 | 121.8018 | 122.0947 | 121.8338 | 122.113 | 121.8063 | 122.1588 | 121.8887 | 121.4905 | 122.113 | 121.8063 | 121.8887 | 121.8338 | 122.1588 | -0.51727 | -0.50354
1921.7656 | 122.1222 | -121.6553 | 0.29755 | -0.0031279 | 0.020083 | 0.0028947 | 0.017271 | -0.0091003 | -0.0040802 | 0.014093 | 0.082397 | 0.43945 | -0.21973 | 0.21973 | 0.12817 | 0.16479 | 0.16022 | 0.39368 | 0.48065 | -0.19226 | 121.4355 | 0.14191 | 121.7377 | 121.875 | -0.16937 | 121.463 | 0.18311 | 0.30212 | 121.8155 | 122.0489 | 121.7834 | 122.0947 | 121.7377 | 122.1359 | 121.8201 | 121.463 | 122.0947 | 121.7377 | 121.8201 | 121.7834 | 122.1359 | -0.51727 | -0.48981
1923.5156 | 122.1176 | -121.6415 | 0.27466 | -0.0031279 | 0.020937 | 0.0031083 | 0.017912 | -0.0061097 | -0.0049348 | 0.012384 | 0.082397 | 0.45776 | -0.23346 | 0.2243 | 0.10986 | 0.15106 | 0.16022 | 0.36621 | 0.48065 | -0.18768 | 121.4081 | 0.18311 | 121.7239 | 121.8658 | -0.1648 | 121.4539 | 0.20599 | 0.31586 | 121.8018 | 122.0078 | 121.7514 | 122.0993 | 121.7239 | 122.1222 | 121.7926 | 121.4539 | 122.0993 | 121.7239 | 121.7926 | 121.7514 | 122.1222 | -0.50812 | -0.46234
1925.2031 | 121.9894 | -121.7331 | 0.3479 | -0.0031279 | 0.020296 | 0.0013993 | 0.019408 | -0.0067505 | -0.008139 | 0.013665 | 0.14648 | 0.41657 | -0.22888 | 0.27466 | 0.15106 | 0.21057 | 0.082397 | 0.42572 | 0.46234 | -0.16479 | 121.5042 | 0.068665 | 121.8796 | 122.0078 | -0.19684 | 121.5683 | 0.11444 | 0.37537 | 121.8155 | 122.1588 | 121.8842 | 122.1497 | 121.8796 | 122.1954 | 121.9437 | 121.5683 | 122.1497 | 121.8796 | 121.9437 | 121.8842 | 122.1954 | -0.57678 | -0.5127
1926.9375 | 122.0947 | -121.6873 | 0.28839 | 0.012131 | 0.016024 | 0.0046037 | 0.011076 | -0.010809 | -0.0062164 | 0.013665 | 0.16022 | 0.37994 | -0.1831 | 0.31128 | 0.23346 | 0.28839 | -0.041199 | 0.50812 | 0.43488 | -0.15106 | 121.5042 | 0.091553 | 121.8475 | 121.9986 | -0.054932 | 121.5363 | 0.14648 | 0.34332 | 121.6461 | 122.1954 | 121.9208 | 122.0673 | 121.8475 | 122.1222 | 121.9757 | 121.5363 | 122.0673 | 121.8475 | 121.9757 | 121.9208 | 122.1222 | -0.4715 | -0.43945
1928.6875 | 122.1222 | -121.669 | 0.3067 | 0.0045011 | 0.019228 | 0.0013993 | 0.012572 | -0.010596 | -0.0055756 | 0.012597 | 0.16022 | 0.38452 | -0.19684 | 0.28381 | 0.17395 | 0.23804 | -0.004578 | 0.43488 | 0.44861 | -0.16479 | 121.4722 | 0.077819 | 121.8292 | 121.9528 | -0.13275 | 121.5042 | 0.14191 | 0.35706 | 121.6644 | 122.1039 | 121.843 | 122.0535 | 121.8292 | 122.1176 | 121.907 | 121.5042 | 122.0535 | 121.8292 | 121.907 | 121.843 | 122.1176 | -0.50354 | -0.4715
1930.4375 | 122.168 | -121.6736 | 0.30212 | 0.0045011 | 0.020083 | 0.0031083 | 0.017271 | -0.010382 | -0.00643 | 0.01452 | 0.082397 | 0.4303 | -0.24261 | 0.22888 | 0.10986 | 0.16479 | 0.17395 | 0.36621 | 0.48523 | -0.19226 | 121.431 | 0.12817 | 121.756 | 121.9025 | -0.19226 | 121.4813 | 0.18311 | 0.32501 | 121.8475 | 122.0398 | 121.7834 | 122.1039 | 121.756 | 122.1588 | 121.8384 | 121.4813 | 122.1039 | 121.756 | 121.8384 | 121.7834 | 122.1588 | -0.54474 | -0.49438
1932.1406 | 122.168 | -121.7056 | 0.27924 | 0.012131 | 0.017306 | 0.0018265 | 0.019835 | -0.0099549 | -0.0085664 | 0.013238 | 0.068665 | 0.43945 | -0.23346 | 0.21515 | 0.1236 | 0.16479 | 0.1831 | 0.36621 | 0.48523 | -0.1831 | 121.4722 | 0.16022 | 121.7743 | 121.9208 | -0.15564 | 121.5225 | 0.20599 | 0.30212 | 121.8887 | 122.0718 | 121.8292 | 122.1451 | 121.7743 | 122.1909 | 121.8704 | 121.5225 | 122.1451 | 121.7743 | 121.8704 | 121.8292 | 122.1909 | -0.5127 | -0.46234
1933.8906 | 122.0627 | -121.7331 | 0.31128 | 0.0045011 | 0.01816 | 0.0031083 | 0.017912 | -0.0054687 | -0.0072846 | 0.012597 | 0.10529 | 0.42572 | -0.23346 | 0.25635 | 0.13275 | 0.20142 | 0.022888 | 0.36621 | 0.46234 | -0.15564 | 121.4996 | 0.11444 | 121.8384 | 121.9894 | -0.17853 | 121.5775 | 0.15106 | 0.33875 | 121.756 | 122.0993 | 121.8658 | 122.1588 | 121.8384 | 122.1954 | 121.9345 | 121.5775 | 122.1588 | 121.8384 | 121.9345 | 121.8658 | 122.1954 | -0.54474 | -0.46692
1935.625 | 122.1313 | -121.7056 | 0.28839 | 0.012131 | 0.017947 | 0.0043899 | 0.013426 | -0.0088867 | -0.0072846 | 0.012811 | 0.16479 | 0.3891 | -0.20599 | 0.32501 | 0.21973 | 0.29297 | -0.004578 | 0.49439 | 0.43945 | -0.16022 | 121.4996 | 0.10071 | 121.8704 | 122.0306 | -0.068664 | 121.5454 | 0.15106 | 0.37079 | 121.701 | 122.2 | 121.9254 | 122.0947 | 121.8704 | 122.1451 | 121.9986 | 121.5454 | 122.0947 | 121.8704 | 121.9986 | 121.9254 | 122.1451 | -0.49439 | -0.44861
1937.375 | 122.1451 | -121.7056 | 0.28381 | 0.012131 | 0.018374 | 0.0073807 | 0.014494 | -0.011664 | -0.0049348 | 0.015588 | 0.14648 | 0.40283 | -0.19226 | 0.27924 | 0.1831 | 0.23804 | -0.013733 | 0.4303 | 0.4303 | -0.15106 | 121.5134 | 0.11902 | 121.8521 | 121.9849 | -0.10071 | 121.5546 | 0.14649 | 0.33874 | 121.6919 | 122.1359 | 121.8887 | 122.1085 | 121.8521 | 122.1359 | 121.9437 | 121.5546 | 122.1085 | 121.8521 | 121.9437 | 121.8887 | 122.1359 | -0.47607 | -0.43488
1939.0625 | 122.0673 | -121.7422 | 0.33417 | 0.0045011 | 0.023287 | 0.0058853 | 0.018767 | -0.0093139 | -0.0045074 | 0.014306 | 0.13733 | 0.4303 | -0.21973 | 0.23346 | 0.11902 | 0.18768 | 0.050354 | 0.35706 | 0.48523 | -0.19226 | 121.5225 | 0.096131 | 121.8796 | 121.9757 | -0.21515 | 121.55 | 0.15106 | 0.35706 | 121.7926 | 122.0993 | 121.8613 | 122.1725 | 121.8796 | 122.2275 | 121.9299 | 121.55 | 122.1725 | 121.8796 | 121.9299 | 121.8613 | 122.2275 | -0.55389 | -0.52643
1940.8125 | 122.1176 | -121.7377 | 0.32044 | 0.0045011 | 0.022219 | 0.0058853 | 0.018767 | -0.0061097 | -0.0060028 | 0.014306 | 0.10986 | 0.43488 | -0.23804 | 0.21515 | 0.09613 | 0.15564 | 0.09613 | 0.33417 | 0.48981 | -0.16937 | 121.4996 | 0.11444 | 121.8475 | 121.9528 | -0.22431 | 121.5683 | 0.16937 | 0.3479 | 121.8338 | 122.0718 | 121.8338 | 122.1725 | 121.8475 | 122.2275 | 121.8933 | 121.5683 | 122.1725 | 121.8475 | 121.8933 | 121.8338 | 122.2275 | -0.55847 | -0.48981
1942.5625 | 122.1909 | -121.7331 | 0.28839 | 0.012131 | 0.019442 | 0.0037491 | 0.014921 | -0.010382 | -0.004721 | 0.013452 | 0.091553 | 0.44861 | -0.24261 | 0.2243 | 0.10986 | 0.15564 | 0.16022 | 0.37079 | 0.47607 | -0.17853 | 121.4905 | 0.16022 | 121.8246 | 121.9574 | -0.17853 | 121.5546 | 0.18768 | 0.33417 | 121.8933 | 122.1039 | 121.843 | 122.1817 | 121.8246 | 122.2092 | 121.8887 | 121.5546 | 122.1817 | 121.8246 | 121.8887 | 121.843 | 122.2092 | -0.53101 | -0.46692
1944.25 | 122.1909 | -121.7102 | 0.29297 | -0.0031279 | 0.019442 | 0.00097207 | 0.012785 | -0.0086731 | -0.003653 | 0.012811 | 0.14648 | 0.38452 | -0.17395 | 0.27466 | 0.17853 | 0.24261 | 0.018311 | 0.43488 | 0.44403 | -0.14648 | 121.5363 | 0.091552 | 121.8567 | 121.9849 | -0.11444 | 121.5637 | 0.15106 | 0.32043 | 121.7285 | 122.1451 | 121.8887 | 122.0947 | 121.8567 | 122.1542 | 121.9528 | 121.5637 | 122.0947 | 121.8567 | 121.9528 | 121.8887 | 122.1542 | -0.46692 | -0.43945
1946.0156 | 122.1588 | -121.7422 | 0.29755 | -0.0031279 | 0.020937 | 0.0028947 | 0.013853 | -0.0065369 | -0.0051484 | 0.014734 | 0.19684 | 0.37994 | -0.18768 | 0.35248 | 0.24261 | 0.28839 | -0.009155 | 0.52185 | 0.44403 | -0.14191 | 121.5546 | 0.082398 | 121.9391 | 122.0947 | -0.054931 | 121.6003 | 0.14649 | 0.38452 | 121.7331 | 122.2641 | 121.9849 | 122.1222 | 121.9391 | 122.1863 | 122.0306 | 121.6003 | 122.1222 | 121.9391 | 122.0306 | 121.9849 | 122.1863 | -0.48523 | -0.43945
1947.7188 | 122.113 | -121.7743 | 0.32501 | -0.0031279 | 0.018374 | 0.0097305 | 0.019621 | -0.0071777 | -0.0060028 | 0.014093 | 0.10529 | 0.41657 | -0.24261 | 0.23346 | 0.10986 | 0.18768 | 0.041199 | 0.34332 | 0.4715 | -0.1831 | 121.5317 | 0.091553 | 121.8796 | 122.0078 | -0.21515 | 121.5912 | 0.14648 | 0.3479 | 121.8155 | 122.1176 | 121.8842 | 122.1909 | 121.8796 | 122.2458 | 121.962 | 121.5912 | 122.1909 | 121.8796 | 121.962 | 121.8842 | 122.2458 | -0.56763 | -0.50812
1949.4531 | 122.1863 | -121.7651 | 0.28839 | 0.0045011 | 0.020083 | 0.0020401 | 0.011931 | -0.0080323 | -0.0060028 | 0.011956 | 0.16937 | 0.39825 | -0.20599 | 0.32044 | 0.2243 | 0.27008 | -0.009155 | 0.48523 | 0.42572 | -0.13733 | 121.5591 | 0.10986 | 121.9345 | 122.0856 | -0.064087 | 121.6278 | 0.13733 | 0.37537 | 121.756 | 122.2504 | 121.9894 | 122.1634 | 121.9345 | 122.1909 | 122.0352 | 121.6278 | 122.1634 | 121.9345 | 122.0352 | 121.9894 | 122.1909 | -0.49439 | -0.42572
1951.2031 | 122.0764 | -121.8338 | 0.32044 | 0.01976 | 0.016238 | 0.0088761 | 0.018339 | -0.0071777 | -0.0072846 | 0.014306 | 0.20142 | 0.33875 | -0.17395 | 0.32501 | 0.21973 | 0.31128 | -0.10529 | 0.4715 | 0.42572 | -0.11902 | 121.6599 | 0.01831 | 122.0352 | 122.1588 | -0.10071 | 121.7148 | 0.10528 | 0.37537 | 121.7285 | 122.3053 | 122.0535 | 122.1725 | 122.0352 | 122.2595 | 122.1451 | 121.7148 | 122.1725 | 122.0352 | 122.1451 | 122.0535 | 122.2595 | -0.49439 | -0.43945
1952.9531 | 122.2046 | -121.788 | 0.28839 | 0.0045011 | 0.017092 | 0.0026809 | 0.016203 | -0.0091003 | -0.0077118 | 0.013879 | 0.16479 | 0.37994 | -0.18768 | 0.32959 | 0.2243 | 0.28839 | -0.018311 | 0.50354 | 0.43488 | -0.15564 | 121.6003 | 0.091553 | 121.9528 | 122.1176 | -0.064087 | 121.6324 | 0.14648 | 0.35248 | 121.7697 | 122.2916 | 122.0123 | 122.168 | 121.9528 | 122.2229 | 122.0764 | 121.6324 | 122.168 | 121.9528 | 122.0764 | 122.0123 | 122.2229 | -0.47607 | -0.44403
1954.6406 | 122.168 | -121.8018 | 0.32044 | 0.0045011 | 0.021578 | 0.0046037 | 0.02133 | -0.0080323 | -0.0085664 | 0.015161 | 0.09613 | 0.41657 | -0.20599 | 0.2243 | 0.07782 | 0.15564 | 0.10071 | 0.32959 | 0.46692 | -0.18768 | 121.5958 | 0.09613 | 121.8979 | 122.0261 | -0.24262 | 121.6141 | 0.14648 | 0.30212 | 121.9025 | 122.1313 | 121.8796 | 122.2183 | 121.8979 | 122.2687 | 121.9574 | 121.6141 | 122.2183 | 121.8979 | 121.9574 | 121.8796 | 122.2687 | -0.52643 | -0.50812
1956.4062 | 122.2321 | -121.7651 | 0.29755 | 0.0045011 | 0.021151 | 0.0013993 | 0.015562 | -0.010809 | -0.005362 | 0.013238 | 0.14191 | 0.38452 | -0.1831 | 0.28839 | 0.17853 | 0.26093 | -0.004578 | 0.43945 | 0.4303 | -0.17853 | 121.582 | 0.086975 | 121.907 | 122.0535 | -0.11902 | 121.5866 | 0.13275 | 0.32501 | 121.7606 | 122.2046 | 121.9437 | 122.1497 | 121.907 | 122.1954 | 122.0261 | 121.5866 | 122.1497 | 121.907 | 122.0261 | 121.9437 | 122.1954 | -0.48065 | -0.47607
1958.0938 | 122.1725 | -121.8292 | 0.31586 | 0.0045011 | 0.022433 | 0.0046037 | 0.021544 | -0.0080323 | -0.0083526 | 0.013879 | 0.1236 | 0.42114 | -0.23804 | 0.24719 | 0.11444 | 0.1831 | 0.064087 | 0.36163 | 0.48065 | -0.16479 | 121.5912 | 0.10529 | 121.9528 | 122.0764 | -0.20142 | 121.6644 | 0.1648 | 0.36163 | 121.8933 | 122.1909 | 121.9437 | 122.2504 | 121.9528 | 122.3099 | 122.0123 | 121.6644 | 122.2504 | 121.9528 | 122.0123 | 121.9437 | 122.3099 | -0.55389 | -0.48065
1959.8438 | 122.1497 | -121.8201 | 0.31128 | 0.0045011 | 0.019228 | 0.0024673 | 0.015776 | -0.0069641 | -0.0085664 | 0.013879 | 0.19226 | 0.39368 | -0.19226 | 0.31128 | 0.21057 | 0.27466 | -0.064087 | 0.45319 | 0.4303 | -0.14191 | 121.6278 | 0.082398 | 122.0123 | 122.1313 | -0.10071 | 121.6782 | 0.11902 | 0.38452 | 121.756 | 122.2733 | 122.0306 | 122.2137 | 122.0123 | 122.2504 | 122.0947 | 121.6782 | 122.2137 | 122.0123 | 122.0947 | 122.0306 | 122.2504 | -0.50354 | -0.45319
1961.6094 | 122.2504 | -121.8475 | 0.3067 | 0.0045011 | 0.020083 | 0.0052445 | 0.015135 | -0.0078187 | -0.0060028 | 0.014947 | 0.16022 | 0.3891 | -0.21973 | 0.3067 | 0.17853 | 0.23804 | 0.091553 | 0.44861 | 0.46234 | -0.16937 | 121.6278 | 0.082397 | 122.0078 | 122.1542 | -0.12817 | 121.6782 | 0.15564 | 0.37994 | 121.9391 | 122.2961 | 122.0261 | 122.2366 | 122.0078 | 122.3099 | 122.0856 | 121.6782 | 122.2366 | 122.0078 | 122.0856 | 122.0261 | 122.3099 | -0.52643 | -0.47607
1963.3594 | 122.1268 | -121.8567 | 0.32501 | 0.012131 | 0.017733 | 0.0033219 | 0.020048 | -0.0082459 | -0.0083526 | 0.015161 | 0.16022 | 0.42114 | -0.23346 | 0.2655 | 0.13733 | 0.20599 | 0.073242 | 0.37994 | 0.45776 | -0.16022 | 121.6232 | 0.096131 | 122.0169 | 122.1222 | -0.18768 | 121.6965 | 0.13275 | 0.39368 | 121.9299 | 122.2366 | 121.994 | 122.2778 | 122.0169 | 122.3145 | 122.0627 | 121.6965 | 122.2778 | 122.0169 | 122.0627 | 121.994 | 122.3145 | -0.55847 | -0.48523
1965.0469 | 122.2137 | -121.8521 | 0.30212 | 0.0045011 | 0.017947 | 0.0020401 | 0.01364 | -0.010809 | -0.0066438 | 0.013452 | 0.21515 | 0.37994 | -0.17395 | 0.3479 | 0.24261 | 0.31128 | -0.032043 | 0.52185 | 0.43945 | -0.14648 | 121.6782 | 0.07782 | 122.0673 | 122.2 | -0.059509 | 121.7056 | 0.13733 | 0.3891 | 121.8201 | 122.374 | 122.0947 | 122.2321 | 122.0673 | 122.2916 | 122.1634 | 121.7056 | 122.2321 | 122.0673 | 122.1634 | 122.0947 | 122.2916 | -0.47607 | -0.44861
1966.7969 | 122.1405 | -121.8658 | 0.34332 | 0.0045011 | 0.020296 | 0.0011857 | 0.020903 | -0.0078187 | -0.0074982 | 0.013238 | 0.16479 | 0.41657 | -0.21973 | 0.27008 | 0.15564 | 0.21515 | 0.068665 | 0.42114 | 0.4715 | -0.16022 | 121.6461 | 0.073242 | 122.0306 | 122.1359 | -0.18768 | 121.7056 | 0.12817 | 0.38452 | 121.9345 | 122.287 | 122.0215 | 122.2824 | 122.0306 | 122.3373 | 122.081 | 121.7056 | 122.2824 | 122.0306 | 122.081 | 122.0215 | 122.3373 | -0.56305 | -0.50354
1968.5469 | 122.1451 | -121.8979 | 0.33875 | -0.010757 | 0.024142 | 0.0056717 | 0.017699 | -0.0063233 | -0.0079254 | 0.013452 | 0.16022 | 0.40741 | -0.24261 | 0.2655 | 0.16937 | 0.21057 | 0.073242 | 0.43488 | 0.45319 | -0.15564 | 121.6553 | 0.068665 | 122.0581 | 122.1634 | -0.16937 | 121.7422 | 0.11444 | 0.40283 | 121.9711 | 122.3328 | 122.0673 | 122.3053 | 122.0581 | 122.3511 | 122.1085 | 121.7422 | 122.3053 | 122.0581 | 122.1085 | 122.0673 | 122.3511 | -0.58136 | -0.49439
1970.2188 | 122.2458 | -121.8384 | 0.3067 | 0.012131 | 0.017519 | -0.0033005 | 0.014281 | -0.0095277 | -0.0051484 | 0.015161 | 0.20142 | 0.37537 | -0.17395 | 0.33417 | 0.26093 | 0.31586 | -0.018311 | 0.53101 | 0.43945 | -0.17395 | 121.6644 | 0.068664 | 122.0398 | 122.1725 | -0.045777 | 121.6644 | 0.13275 | 0.37537 | 121.8201 | 122.3694 | 122.0993 | 122.2137 | 122.0398 | 122.2778 | 122.1542 | 121.6644 | 122.2137 | 122.0398 | 122.1542 | 122.0993 | 122.2778 | -0.48065 | -0.48065
1971.9688 | 122.2 | -121.875 | 0.32044 | 0.0045011 | 0.018801 | 0.0039627 | 0.014708 | -0.0067505 | -0.0066438 | 0.013025 | 0.19226 | 0.3891 | -0.19226 | 0.30212 | 0.19684 | 0.28381 | -0.041199 | 0.43488 | 0.4303 | -0.16022 | 121.6827 | 0.068664 | 122.0673 | 122.1771 | -0.1236 | 121.7148 | 0.10986 | 0.38452 | 121.8338 | 122.3099 | 122.0718 | 122.2641 | 122.0673 | 122.3053 | 122.1588 | 121.7148 | 122.2641 | 122.0673 | 122.1588 | 122.0718 | 122.3053 | -0.5127 | -0.48065
1973.6719 | 122.2046 | -121.8796 | 0.32501 | 0.012131 | 0.020724 | 0.0033219 | 0.023466 | -0.0056823 | -0.00878 | 0.013452 | 0.10529 | 0.40741 | -0.23804 | 0.19684 | 0.10071 | 0.15564 | 0.1236 | 0.32501 | 0.48065 | -0.17853 | 121.6415 | 0.082398 | 121.9849 | 122.0764 | -0.2243 | 121.701 | 0.15564 | 0.34332 | 122.0032 | 122.2046 | 121.9803 | 122.287 | 121.9849 | 122.3602 | 122.0352 | 121.701 | 122.287 | 121.9849 | 122.0352 | 121.9803 | 122.3602 | -0.56305 | -0.50354
1975.4375 | 122.2229 | -121.875 | 0.33417 | 0.0045011 | 0.017947 | 0.00075827 | 0.019621 | -0.0073913 | -0.009848 | 0.014093 | 0.14648 | 0.42572 | -0.21057 | 0.27466 | 0.16479 | 0.20142 | 0.10071 | 0.42114 | 0.4715 | -0.16022 | 121.6644 | 0.091553 | 122.0215 | 122.1497 | -0.16937 | 121.7148 | 0.13733 | 0.35706 | 121.9757 | 122.2961 | 122.0398 | 122.3007 | 122.0215 | 122.3465 | 122.0764 | 121.7148 | 122.3007 | 122.0215 | 122.0764 | 122.0398 | 122.3465 | -0.54474 | -0.49438
1977.125 | 122.3145 | -121.8521 | 0.3067 | 0.012131 | 0.021151 | 0.0024673 | 0.017485 | -0.0082459 | -0.0062164 | 0.015374 | 0.10071 | 0.42572 | -0.23346 | 0.22888 | 0.13275 | 0.15106 | 0.1831 | 0.37079 | 0.49896 | -0.16937 | 121.6187 | 0.11902 | 121.9528 | 122.081 | -0.17395 | 121.6827 | 0.19226 | 0.33417 | 122.0352 | 122.2229 | 121.9849 | 122.2778 | 121.9528 | 122.3511 | 122.0032 | 121.6827 | 122.2778 | 121.9528 | 122.0032 | 121.9849 | 122.3511 | -0.54016 | -0.47607
1978.875 | 122.2275 | -121.875 | 0.32501 | 0.012131 | 0.021365 | 0.0048173 | 0.019194 | -0.0065369 | -0.0074982 | 0.013025 | 0.12817 | 0.4303 | -0.22888 | 0.21057 | 0.082397 | 0.15564 | 0.1236 | 0.32959 | 0.48523 | -0.17395 | 121.6461 | 0.10529 | 122.0032 | 122.0856 | -0.24262 | 121.701 | 0.16022 | 0.35706 | 121.9986 | 122.2046 | 121.9574 | 122.3053 | 122.0032 | 122.3602 | 122.0306 | 121.701 | 122.3053 | 122.0032 | 122.0306 | 121.9574 | 122.3602 | -0.55389 | -0.49896
1980.625 | 122.1909 | -121.907 | 0.32044 | 0.0045011 | 0.019656 | 0.0084489 | 0.017699 | -0.0067505 | -0.0057892 | 0.015161 | 0.23346 | 0.39368 | -0.17395 | 0.33417 | 0.21973 | 0.31128 | -0.073242 | 0.48065 | 0.4303 | -0.12817 | 121.7331 | 0.073242 | 122.1405 | 122.2412 | -0.10071 | 121.7789 | 0.10986 | 0.40741 | 121.8338 | 122.3877 | 122.1268 | 122.3007 | 122.1405 | 122.3373 | 122.2183 | 121.7789 | 122.3007 | 122.1405 | 122.2183 | 122.1268 | 122.3373 | -0.49439 | -0.44861
1982.3281 | 122.1817 | -121.907 | 0.33417 | 0.0045011 | 0.022219 | 0.0080215 | 0.01898 | -0.0065369 | -0.0079254 | 0.012597 | 0.17395 | 0.4303 | -0.18768 | 0.30212 | 0.18768 | 0.25635 | -0.018311 | 0.4303 | 0.44861 | -0.14648 | 121.7194 | 0.096131 | 122.081 | 122.2092 | -0.14648 | 121.7606 | 0.11444 | 0.36163 | 121.8887 | 122.3373 | 122.0947 | 122.3373 | 122.081 | 122.3557 | 122.1634 | 121.7606 | 122.3373 | 122.081 | 122.1634 | 122.0947 | 122.3557 | -0.52185 | -0.48065
1984.0781 | 122.3419 | -121.8796 | 0.30212 | 0.0045011 | 0.019869 | 0.0056717 | 0.017271 | -0.0091003 | -0.0062164 | 0.014734 | 0.16479 | 0.41199 | -0.19684 | 0.25177 | 0.16022 | 0.21515 | 0.13275 | 0.42572 | 0.48065 | -0.16937 | 121.6827 | 0.10986 | 122.0444 | 122.1313 | -0.14191 | 121.7102 | 0.17853 | 0.36163 | 122.0123 | 122.3053 | 122.0398 | 122.2916 | 122.0444 | 122.3602 | 122.0947 | 121.7102 | 122.2916 | 122.0444 | 122.0947 | 122.0398 | 122.3602 | -0.49896 | -0.4715
1985.8125 | 122.2092 | -121.8887 | 0.33417 | 0.0045011 | 0.019869 | 0.0050309 | 0.017912 | -0.0063233 | -0.007071 | 0.014947 | 0.14191 | 0.40741 | -0.19226 | 0.30212 | 0.18768 | 0.27008 | -0.013733 | 0.45319 | 0.4715 | -0.15106 | 121.6965 | 0.073243 | 122.0306 | 122.1909 | -0.14648 | 121.7377 | 0.13733 | 0.33417 | 121.875 | 122.3419 | 122.0764 | 122.2961 | 122.0306 | 122.3602 | 122.1588 | 121.7377 | 122.2961 | 122.0306 | 122.1588 | 122.0764 | 122.3602 | -0.52643 | -0.48523
1987.5 | 122.2504 | -121.9299 | 0.32501 | -0.0031279 | 0.02051 | 0.00097207 | 0.013853 | -0.0078187 | -0.012412 | 0.015374 | 0.20142 | 0.39368 | -0.1831 | 0.29297 | 0.20142 | 0.28381 | -0.027466 | 0.45776 | 0.44403 | -0.14648 | 121.7468 | 0.068665 | 122.1313 | 122.2229 | -0.1236 | 121.7834 | 0.11902 | 0.38452 | 121.9025 | 122.3877 | 122.1313 | 122.3236 | 122.1313 | 122.374 | 122.2137 | 121.7834 | 122.3236 | 122.1313 | 122.2137 | 122.1313 | 122.374 | -0.50812 | -0.4715
1989.25 | 122.2366 | -121.8979 | 0.32044 | -0.0031279 | 0.017306 | 0.0095169 | 0.018126 | -0.0086731 | -0.0055756 | 0.014093 | 0.21057 | 0.37537 | -0.17395 | 0.3479 | 0.20599 | 0.29297 | -0.041199 | 0.46692 | 0.44403 | -0.14191 | 121.7239 | 0.054931 | 122.1085 | 122.2458 | -0.11444 | 121.756 | 0.1236 | 0.38452 | 121.8567 | 122.3648 | 122.1039 | 122.2733 | 122.1085 | 122.3419 | 122.1909 | 121.756 | 122.2733 | 122.1085 | 122.1909 | 122.1039 | 122.3419 | -0.49439 | -0.46234
1990.9375 | 122.2687 | -121.9162 | 0.32501 | 0.012131 | 0.020724 | 0.0031083 | 0.02368 | -0.0084595 | -0.0062164 | 0.013879 | 0.10986 | 0.43945 | -0.21515 | 0.22888 | 0.10986 | 0.16479 | 0.12817 | 0.33875 | 0.48981 | -0.16937 | 121.7011 | 0.11444 | 122.0261 | 122.1451 | -0.21515 | 121.7468 | 0.16479 | 0.32501 | 122.0444 | 122.2549 | 122.0261 | 122.3557 | 122.0261 | 122.406 | 122.081 | 121.7468 | 122.3557 | 122.0261 | 122.081 | 122.0261 | 122.406 | -0.54016 | -0.49439
1992.6875 | 122.3145 | -121.9254 | 0.30212 | 0.0045011 | 0.019442 | 0.00097207 | 0.014494 | -0.0088867 | -0.005362 | 0.01217 | 0.22888 | 0.3891 | -0.19226 | 0.35248 | 0.23804 | 0.30212 | 0.013733 | 0.52643 | 0.44403 | -0.13733 | 121.7331 | 0.086975 | 122.1542 | 122.2778 | -0.064087 | 121.788 | 0.14191 | 0.42114 | 121.9391 | 122.4518 | 122.1634 | 122.3145 | 122.1542 | 122.3694 | 122.2275 | 121.788 | 122.3145 | 122.1542 | 122.2275 | 122.1634 | 122.3694 | -0.49438 | -0.43945
1994.4375 | 122.2412 | -121.9391 | 0.35248 | 0.012131 | 0.019656 | 0.0056717 | 0.020903 | -0.0091003 | -0.0089936 | 0.014947 | 0.16937 | 0.40741 | -0.20599 | 0.29755 | 0.16937 | 0.21973 | 0.09613 | 0.43488 | 0.47607 | -0.17395 | 121.7331 | 0.054932 | 122.1085 | 122.2366 | -0.18311 | 121.7651 | 0.1236 | 0.37537 | 122.0352 | 122.374 | 122.1085 | 122.3465 | 122.1085 | 122.4152 | 122.1588 | 121.7651 | 122.3465 | 122.1085 | 122.1588 | 122.1085 | 122.4152 | -0.55847 | -0.52643
1996.1406 | 122.2412 | -121.9666 | 0.34332 | 0.012131 | 0.018587 | 0.0031083 | 0.020689 | -0.0056823 | -0.008139 | 0.016229 | 0.16022 | 0.39825 | -0.20142 | 0.27008 | 0.16022 | 0.21057 | 0.086975 | 0.42572 | 0.46234 | -0.16479 | 121.7651 | 0.054931 | 122.1268 | 122.2366 | -0.18311 | 121.8018 | 0.11902 | 0.36163 | 122.0535 | 122.3923 | 122.1268 | 122.3648 | 122.1268 | 122.4289 | 122.1771 | 121.8018 | 122.3648 | 122.1268 | 122.1771 | 122.1268 | 122.4289 | -0.54474 | -0.50812
1997.8906 | 122.3648 | -121.875 | 0.28381 | -0.0031279 | 0.02051 | 0.00033107 | 0.012999 | -0.0073913 | -0.0055756 | 0.012384 | 0.17853 | 0.38452 | -0.19226 | 0.2655 | 0.17853 | 0.25177 | 0.032043 | 0.44403 | 0.45776 | -0.16022 | 121.6827 | 0.10071 | 122.0535 | 122.1405 | -0.10528 | 121.7148 | 0.17395 | 0.37079 | 121.907 | 122.319 | 122.0535 | 122.2595 | 122.0535 | 122.3328 | 122.1268 | 121.7148 | 122.2595 | 122.0535 | 122.1268 | 122.0535 | 122.3328 | -0.47607 | -0.44403
1999.6406 | 122.2824 | -121.9482 | 0.33875 | 0.0045011 | 0.019656 | 0.0086625 | 0.021757 | -0.0061097 | -0.0077118 | 0.01452 | 0.13733 | 0.39825 | -0.2243 | 0.21973 | 0.11444 | 0.17853 | 0.12817 | 0.3479 | 0.48065 | -0.1831 | 121.7239 | 0.059509 | 122.0856 | 122.168 | -0.2243 | 121.7651 | 0.14191 | 0.36163 | 122.0764 | 122.2961 | 122.0627 | 122.3465 | 122.0856 | 122.4289 | 122.1268 | 121.7651 | 122.3465 | 122.0856 | 122.1268 | 122.0627 | 122.4289 | -0.56305 | -0.52185
2001.3906 | 122.3328 | -121.9299 | 0.31128 | -0.0031279 | 0.019442 | 0.0022537 | 0.017485 | -0.010168 | -0.0068574 | 0.013452 | 0.21973 | 0.37994 | -0.16937 | 0.31586 | 0.24261 | 0.31586 | -0.009155 | 0.52643 | 0.4303 | -0.1236 | 121.7606 | 0.068665 | 122.1497 | 122.2458 | -0.068664 | 121.8063 | 0.11902 | 0.3891 | 121.9208 | 122.4564 | 122.1725 | 122.3099 | 122.1497 | 122.3602 | 122.2458 | 121.8063 | 122.3099 | 122.1497 | 122.2458 | 122.1725 | 122.3602 | -0.48065 | -0.43487
2003.0781 | 122.3053 | -121.962 | 0.33875 | -0.0031279 | 0.022005 | 0.0046037 | 0.022185 | -0.0069641 | -0.0042938 | 0.013665 | 0.13733 | 0.44403 | -0.21973 | 0.20599 | 0.082397 | 0.14191 | 0.1236 | 0.31586 | 0.47607 | -0.18768 | 121.7422 | 0.10529 | 122.0993 | 122.168 | -0.25635 | 121.7743 | 0.13733 | 0.35706 | 122.0856 | 122.2778 | 122.0444 | 122.406 | 122.0993 | 122.438 | 122.1039 | 121.7743 | 122.406 | 122.0993 | 122.1039 | 122.0444 | 122.438 | -0.55847 | -0.52643
2004.8281 | 122.2916 | -121.9757 | 0.33417 | 0.012131 | 0.022433 | 0.010371 | 0.020048 | -0.0048279 | -0.0066438 | 0.013879 | 0.1236 | 0.40741 | -0.22888 | 0.21973 | 0.10529 | 0.16937 | 0.11444 | 0.3479 | 0.47607 | -0.16022 | 121.7468 | 0.073243 | 122.0993 | 122.1954 | -0.22888 | 121.8155 | 0.14191 | 0.35248 | 122.0901 | 122.3236 | 122.081 | 122.3831 | 122.0993 | 122.4518 | 122.1451 | 121.8155 | 122.3831 | 122.0993 | 122.1451 | 122.081 | 122.4518 | -0.56305 | -0.49438
2006.5312 | 122.2687 | -121.9711 | 0.33417 | -0.0031279 | 0.019228 | 0.0041763 | 0.01663 | -0.0088867 | -0.0055756 | 0.015161 | 0.21057 | 0.38452 | -0.17395 | 0.32501 | 0.22888 | 0.30212 | -0.059509 | 0.47607 | 0.4303 | -0.12817 | 121.7972 | 0.050354 | 122.1817 | 122.2961 | -0.10528 | 121.843 | 0.096131 | 0.38452 | 121.9116 | 122.4472 | 122.2 | 122.3557 | 122.1817 | 122.4014 | 122.2733 | 121.843 | 122.3557 | 122.1817 | 122.2733 | 122.2 | 122.4014 | -0.50812 | -0.46234
2008.2969 | 122.3145 | -121.9711 | 0.31128 | 0.0045011 | 0.018587 | 0.0013993 | 0.019621 | -0.0080323 | -0.0068574 | 0.013665 | 0.15106 | 0.42114 | -0.22888 | 0.27008 | 0.15106 | 0.21515 | 0.10071 | 0.40283 | 0.46692 | -0.17395 | 121.7422 | 0.10986 | 122.1222 | 122.2412 | -0.16022 | 121.7972 | 0.15564 | 0.37994 | 122.0718 | 122.374 | 122.1222 | 122.3923 | 122.1222 | 122.438 | 122.1863 | 121.7972 | 122.3923 | 122.1222 | 122.1863 | 122.1222 | 122.438 | -0.54016 | -0.48523
2010.0469 | 122.3099 | -121.9849 | 0.32044 | 0.0045011 | 0.019015 | 0.0046037 | 0.01898 | -0.0061097 | -0.0051484 | 0.016443 | 0.11444 | 0.44403 | -0.23346 | 0.21973 | 0.091553 | 0.18768 | 0.091553 | 0.3479 | 0.47607 | -0.17395 | 121.7514 | 0.1236 | 122.0993 | 122.2046 | -0.22888 | 121.8109 | 0.15564 | 0.3479 | 122.0764 | 122.3328 | 122.0764 | 122.4289 | 122.0993 | 122.4609 | 122.1725 | 121.8109 | 122.4289 | 122.0993 | 122.1725 | 122.0764 | 122.4609 | -0.55389 | -0.49439
2011.7969 | 122.287 | -122.0215 | 0.33875 | -0.010757 | 0.022219 | 0.0052445 | 0.02133 | -0.0069641 | -0.00643 | 0.013879 | 0.14648 | 0.40741 | -0.20142 | 0.24719 | 0.13275 | 0.1831 | 0.10071 | 0.36621 | 0.4715 | -0.18768 | 121.8201 | 0.068665 | 122.168 | 122.2687 | -0.20599 | 121.8338 | 0.13275 | 0.3479 | 122.1222 | 122.3877 | 122.1542 | 122.4289 | 122.168 | 122.493 | 122.2046 | 121.8338 | 122.4289 | 122.168 | 122.2046 | 122.1542 | 122.493 | -0.54016 | -0.52643
2013.4844 | 122.3557 | -121.9711 | 0.29755 | 0.012131 | 0.017947 | 0.0041763 | 0.012572 | -0.0099549 | -0.0042938 | 0.014306 | 0.15106 | 0.38452 | -0.1831 | 0.27008 | 0.1831 | 0.27008 | -0.013733 | 0.4303 | 0.45319 | -0.14191 | 121.788 | 0.086975 | 122.1222 | 122.2412 | -0.11444 | 121.8292 | 0.15564 | 0.33417 | 121.9574 | 122.4014 | 122.1542 | 122.3557 | 122.1222 | 122.4243 | 122.2412 | 121.8292 | 122.3557 | 122.1222 | 122.2412 | 122.1542 | 122.4243 | -0.48065 | -0.43945
2015.2344 | 122.4197 | -121.9666 | 0.29297 | -0.0031279 | 0.017947 | 0.0037491 | 0.015349 | -0.0097413 | -0.007071 | 0.013238 | 0.14191 | 0.38452 | -0.20142 | 0.22888 | 0.13733 | 0.1831 | 0.12817 | 0.40283 | 0.48523 | -0.18768 | 121.7651 | 0.091552 | 122.1085 | 122.1954 | -0.15564 | 121.7789 | 0.19226 | 0.34332 | 122.0947 | 122.3694 | 122.1039 | 122.3511 | 122.1085 | 122.4518 | 122.1497 | 121.7789 | 122.3511 | 122.1085 | 122.1497 | 122.1039 | 122.4518 | -0.49438 | -0.48065
2017 | 122.4152 | -121.9803 | 0.28839 | -0.0031279 | 0.020296 | 0.0046037 | 0.014067 | -0.0073913 | -0.0057892 | 0.014734 | 0.16479 | 0.3891 | -0.1831 | 0.27008 | 0.1831 | 0.24719 | 0.009155 | 0.4303 | 0.45319 | -0.14648 | 121.7972 | 0.10071 | 122.1451 | 122.2504 | -0.10529 | 121.8338 | 0.16479 | 0.3479 | 121.9894 | 122.4106 | 122.1634 | 122.3694 | 122.1451 | 122.4335 | 122.2275 | 121.8338 | 122.3694 | 122.1451 | 122.2275 | 122.1634 | 122.4335 | -0.4715 | -0.43488
2018.7031 | 122.4197 | -121.9849 | 0.31128 | 0.0045011 | 0.018587 | 0.0046037 | 0.019408 | -0.0091003 | -0.0079254 | 0.012811 | 0.16937 | 0.40283 | -0.19684 | 0.27008 | 0.16022 | 0.22888 | 0.10986 | 0.43488 | 0.46234 | -0.16479 | 121.788 | 0.091553 | 122.1542 | 122.2549 | -0.15106 | 121.8201 | 0.15106 | 0.36621 | 122.0947 | 122.4197 | 122.1451 | 122.3877 | 122.1542 | 122.4472 | 122.2137 | 121.8201 | 122.3877 | 122.1542 | 122.2137 | 122.1451 | 122.4472 | -0.50812 | -0.47607
2020.4531 | 122.1817 | -122.113 | 0.25177 | 0.0045011 | 0.020083 | 0.0048173 | 0.0053085 | -0.0050415 | -0.008139 | 0.012811 | 0.15564 | 0.28381 | -0.2655 | 0.25177 | 0.12817 | 0.2243 | -0.18768 | 0.37537 | 0.33875 | -0.2243 | 121.8475 | 0.032043 | 122.2687 | 122.3648 | -0.1236 | 121.8887 | 0.086975 | 0.42114 | 121.9254 | 122.4884 | 122.2412 | 122.3969 | 122.2687 | 122.4518 | 122.3373 | 121.8887 | 122.3969 | 122.2687 | 122.3373 | 122.2412 | 122.4518 | -0.51727 | -0.47607
2022.1406 | 122.2916 | -122.0947 | 0.22888 | 0.0045011 | 0.019442 | 0.0071671 | 0.0085129 | -0.0039735 | -0.0068574 | 0.012597 | 0.022888 | 0.32501 | -0.32501 | 0.13275 | -0.004578 | 0.059509 | 0.022888 | 0.2243 | 0.39368 | -0.26093 | 121.7697 | 0.09613 | 122.1176 | 122.2275 | -0.23346 | 121.8338 | 0.16479 | 0.3479 | 122.1176 | 122.319 | 122.0901 | 122.4197 | 122.1176 | 122.4884 | 122.1542 | 121.8338 | 122.4197 | 122.1176 | 122.1542 | 122.0901 | 122.4884 | -0.55389 | -0.48981
2023.9062 | 122.4106 | -122.0581 | 0.19684 | -0.0031279 | 0.016665 | 0.0031083 | 0.0029587 | -0.0086731 | -0.0055756 | 0.011743 | 0.041199 | 0.31128 | -0.31128 | 0.15564 | 0.050354 | 0.086975 | 0.045776 | 0.31586 | 0.38452 | -0.2655 | 121.7468 | 0.11444 | 122.0993 | 122.2137 | -0.14648 | 121.7926 | 0.18768 | 0.35248 | 122.1039 | 122.374 | 122.1085 | 122.3694 | 122.0993 | 122.4426 | 122.1451 | 121.7926 | 122.3694 | 122.0993 | 122.1451 | 122.1085 | 122.4426 | -0.50812 | -0.46234
2025.6562 | 122.4106 | -122.0856 | 0.20599 | -0.010757 | 0.016665 | 0.0050309 | 0.0050949 | -0.0088867 | -0.0062164 | 0.01217 | 0.086975 | 0.31586 | -0.3067 | 0.19684 | 0.082397 | 0.13733 | 0.004578 | 0.3479 | 0.36163 | -0.2655 | 121.7789 | 0.10986 | 122.1725 | 122.2824 | -0.1236 | 121.8201 | 0.15564 | 0.39368 | 122.0901 | 122.4335 | 122.168 | 122.4014 | 122.1725 | 122.4472 | 122.2229 | 121.8201 | 122.4014 | 122.1725 | 122.2229 | 122.168 | 122.4472 | -0.5127 | -0.4715
2027.3438 | 122.4472 | -122.0535 | 0.21973 | -0.0031279 | 0.019656 | 0.0035355 | 0.0048813 | -0.0069641 | -0.0038666 | 0.013238 | 0.064087 | 0.3067 | -0.28381 | 0.22888 | 0.082397 | 0.16479 | -0.10071 | 0.36163 | 0.35706 | -0.24261 | 121.7697 | 0.086975 | 122.1176 | 122.2824 | -0.13733 | 121.8109 | 0.13733 | 0.3479 | 121.9528 | 122.4152 | 122.1359 | 122.3602 | 122.1176 | 122.4106 | 122.2183 | 121.8109 | 122.3602 | 122.1176 | 122.2183 | 122.1359 | 122.4106 | -0.50354 | -0.46234
2029.0781 | 122.3145 | -122.1542 | 0.22888 | -0.0031279 | 0.018587 | 0.0022537 | 0.010863 | -0.0084595 | -0.0096344 | 0.013238 | 0.064087 | 0.31586 | -0.32044 | 0.18768 | 0.041199 | 0.11444 | -0.009155 | 0.29755 | 0.35706 | -0.26093 | 121.8338 | 0.086975 | 122.2183 | 122.3419 | -0.18768 | 121.8933 | 0.12817 | 0.38452 | 122.1451 | 122.4518 | 122.1954 | 122.4701 | 122.2183 | 122.5113 | 122.2687 | 121.8933 | 122.4701 | 122.2183 | 122.2687 | 122.1954 | 122.5113 | -0.54932 | -0.48981
2030.8281 | 122.3236 | -122.1222 | 0.22888 | 0.012131 | 0.018801 | -0.00030973 | 0.0080857 | -0.0076049 | -0.004721 | 0.012384 | 0.10529 | 0.27924 | -0.26093 | 0.2243 | 0.10071 | 0.20599 | -0.16937 | 0.37994 | 0.34332 | -0.23346 | 121.8613 | 0.050354 | 122.2275 | 122.3465 | -0.12817 | 121.8887 | 0.11444 | 0.36621 | 121.9528 | 122.5021 | 122.2229 | 122.4014 | 122.2275 | 122.4655 | 122.3282 | 121.8887 | 122.4014 | 122.2275 | 122.3282 | 122.2229 | 122.4655 | -0.48981 | -0.46234
2032.5781 | 122.319 | -122.1405 | 0.23804 | 0.012131 | 0.020083 | 0.0067399 | 0.013213 | -0.0069641 | -0.0094208 | 0.014093 | 0.082397 | 0.32959 | -0.3067 | 0.19684 | 0.059509 | 0.13733 | -0.032043 | 0.31128 | 0.36163 | -0.26093 | 121.8338 | 0.091553 | 122.2229 | 122.3373 | -0.17853 | 121.8796 | 0.1236 | 0.3891 | 122.1085 | 122.4518 | 122.2 | 122.4701 | 122.2229 | 122.5021 | 122.2778 | 121.8796 | 122.4701 | 122.2229 | 122.2778 | 122.2 | 122.5021 | -0.54474 | -0.49896
2034.3281 | 122.4518 | -122.1039 | 0.19684 | 0.01976 | 0.016238 | 0.0056717 | 0.0018905 | -0.0084595 | -0.0066438 | 0.013879 | 0.032043 | 0.27008 | -0.31586 | 0.18768 | 0.082397 | 0.15564 | -0.086975 | 0.33417 | 0.3479 | -0.24719 | 121.788 | 0.073243 | 122.1359 | 122.2916 | -0.11444 | 121.8567 | 0.15106 | 0.3479 | 122.0169 | 122.438 | 122.1863 | 122.374 | 122.1359 | 122.4518 | 122.2595 | 121.8567 | 122.374 | 122.1359 | 122.2595 | 122.1863 | 122.4518 | -0.5127 | -0.44403
2036.0156 | 122.374 | -122.1359 | 0.21057 | -0.0031279 | 0.018587 | 0.0071671 | 0.0065903 | -0.0088867 | -0.005362 | 0.014947 | 0.11902 | 0.3067 | -0.27466 | 0.20599 | 0.091553 | 0.17853 | -0.15106 | 0.35248 | 0.3479 | -0.23346 | 121.8613 | 0.096131 | 122.2549 | 122.3419 | -0.11902 | 121.9025 | 0.13733 | 0.39368 | 121.9849 | 122.4884 | 122.2275 | 122.4426 | 122.2549 | 122.4838 | 122.3145 | 121.9025 | 122.4426 | 122.2549 | 122.3145 | 122.2275 | 122.4838 | -0.48523 | -0.44403
2037.7656 | 122.4472 | -122.1268 | 0.21973 | 0.0045011 | 0.019656 | 0.0065263 | 0.0085129 | -0.0067505 | -0.0074982 | 0.01452 | 0.018311 | 0.31128 | -0.32501 | 0.17395 | 0.036621 | 0.086975 | 0.032043 | 0.31586 | 0.37994 | -0.26093 | 121.8018 | 0.091552 | 122.1451 | 122.3007 | -0.18311 | 121.8658 | 0.16022 | 0.34332 | 122.1588 | 122.4426 | 122.1634 | 122.438 | 122.1451 | 122.5067 | 122.2137 | 121.8658 | 122.438 | 122.1451 | 122.2137 | 122.1634 | 122.5067 | -0.54474 | -0.48065
2039.4531 | 122.374 | -122.1222 | 0.2243 | 0.012131 | 0.019869 | 0.0060989 | 0.0082993 | -0.0088867 | -0.0066438 | 0.016229 | 0.013733 | 0.32044 | -0.32044 | 0.15564 | 0.009155 | 0.10071 | -0.050354 | 0.26093 | 0.37079 | -0.26093 | 121.8018 | 0.096131 | 122.1359 | 122.2778 | -0.21515 | 121.8613 | 0.14648 | 0.33417 | 122.0718 | 122.3831 | 122.1313 | 122.4426 | 122.1359 | 122.493 | 122.2229 | 121.8613 | 122.4426 | 122.1359 | 122.2229 | 122.1313 | 122.493 | -0.54474 | -0.48523
2041.2031 | 122.3785 | -122.1542 | 0.22888 | 0.0045011 | 0.017519 | 0.0031083 | 0.0085129 | -0.0052551 | -0.0074982 | 0.017938 | -0.004578 | 0.32959 | -0.32501 | 0.1236 | 0.027466 | 0.07782 | -0.018311 | 0.23804 | 0.39368 | -0.27466 | 121.8292 | 0.10071 | 122.1497 | 122.2778 | -0.20142 | 121.8796 | 0.16479 | 0.32043 | 122.1359 | 122.3923 | 122.1817 | 122.4838 | 122.1497 | 122.5479 | 122.2321 | 121.8796 | 122.4838 | 122.1497 | 122.2321 | 122.1817 | 122.5479 | -0.55389 | -0.50354
2042.9531 | 122.3831 | -122.1725 | 0.2243 | 0.0045011 | 0.019442 | -0.0011643 | 0.0085129 | -0.0078187 | -0.0085664 | 0.016015 | 0.032043 | 0.29755 | -0.32501 | 0.15106 | 0.032043 | 0.10986 | -0.082397 | 0.27924 | 0.37994 | -0.24719 | 121.8475 | 0.073242 | 122.2046 | 122.3236 | -0.19226 | 121.9254 | 0.15564 | 0.35706 | 122.0901 | 122.4518 | 122.2046 | 122.4701 | 122.2046 | 122.5525 | 122.2824 | 121.9254 | 122.4701 | 122.2046 | 122.2824 | 122.2046 | 122.5525 | -0.54932 | -0.4715
2044.7031 | 122.3557 | -122.1863 | 0.24261 | 0.012131 | 0.021792 | 0.0046037 | 0.010008 | -0.0058961 | -0.0066438 | 0.014734 | 0.073242 | 0.31586 | -0.3067 | 0.1831 | 0.032043 | 0.10986 | -0.009155 | 0.29297 | 0.37994 | -0.27008 | 121.8796 | 0.073242 | 122.2595 | 122.3694 | -0.21057 | 121.9162 | 0.13733 | 0.37994 | 122.1771 | 122.4792 | 122.2183 | 122.5021 | 122.2595 | 122.5662 | 122.2961 | 121.9162 | 122.5021 | 122.2595 | 122.2961 | 122.2183 | 122.5662 | -0.54932 | -0.5127
2046.3906 | 122.3557 | -122.1909 | 0.21515 | 0.0045011 | 0.01581 | 0.0054581 | 0.0074447 | -0.0056823 | -0.0042938 | 0.015374 | 0.11902 | 0.29297 | -0.26093 | 0.23804 | 0.13275 | 0.21057 | -0.16937 | 0.37079 | 0.33417 | -0.24719 | 121.9299 | 0.07782 | 122.3099 | 122.4289 | -0.082398 | 121.9437 | 0.11902 | 0.37994 | 122.0215 | 122.5616 | 122.3236 | 122.4838 | 122.3099 | 122.525 | 122.4014 | 121.9437 | 122.4838 | 122.3099 | 122.4014 | 122.3236 | 122.525 | -0.47607 | -0.46234
2048.1406 | 122.5067 | -122.1405 | 0.20142 | 0.0045011 | 0.015383 | 0.0052445 | 0.00082248 | -0.0097413 | -0.00643 | 0.014093 | 0.022888 | 0.29755 | -0.30212 | 0.20599 | 0.10986 | 0.15564 | -0.09613 | 0.35248 | 0.33875 | -0.25635 | 121.8384 | 0.09613 | 122.1634 | 122.3465 | -0.091553 | 121.8842 | 0.13733 | 0.32501 | 122.0444 | 122.493 | 122.2504 | 122.438 | 122.1634 | 122.4792 | 122.2961 | 121.8842 | 122.438 | 122.1634 | 122.2961 | 122.2504 | 122.4792 | -0.50354 | -0.45776
2049.8281 | 122.3694 | -122.1909 | 0.22888 | 0.0045011 | 0.019015 | 0.0060989 | 0.0087265 | -0.0063233 | -0.0074982 | 0.016229 | 0.10071 | 0.28839 | -0.29755 | 0.22888 | 0.09613 | 0.20142 | -0.14648 | 0.35706 | 0.33417 | -0.24261 | 121.8933 | 0.059509 | 122.2916 | 122.4197 | -0.13275 | 121.9482 | 0.10528 | 0.39825 | 122.0444 | 122.5479 | 122.287 | 122.4792 | 122.2916 | 122.525 | 122.3923 | 121.9482 | 122.4792 | 122.2916 | 122.3923 | 122.287 | 122.525 | -0.52643 | -0.4715
2051.5781 | 122.4472 | -122.1451 | 0.21057 | -0.0031279 | 0.016878 | 0.00011747 | 0.0031723 | -0.0091003 | -0.0055756 | 0.011956 | 0.11444 | 0.28381 | -0.28381 | 0.2655 | 0.13733 | 0.2243 | -0.13275 | 0.43488 | 0.33875 | -0.25177 | 121.8613 | 0.073242 | 122.2595 | 122.4106 | -0.073242 | 121.8933 | 0.12817 | 0.39825 | 122.0123 | 122.58 | 122.2824 | 122.4289 | 122.2595 | 122.4838 | 122.3694 | 121.8933 | 122.4289 | 122.2595 | 122.3694 | 122.2824 | 122.4838 | -0.49438 | -0.46234
2053.3281 | 122.4838 | -122.1771 | 0.20599 | 0.0045011 | 0.018587 | 0.0050309 | 0.0070175 | -0.0099549 | -0.0060028 | 0.013452 | 0.11444 | 0.29755 | -0.27466 | 0.24261 | 0.1236 | 0.18768 | -0.059509 | 0.39825 | 0.32959 | -0.25635 | 121.9025 | 0.091552 | 122.2916 | 122.4197 | -0.082398 | 121.9208 | 0.1236 | 0.3891 | 122.1176 | 122.5754 | 122.3007 | 122.4747 | 122.2916 | 122.5067 | 122.3648 | 121.9208 | 122.4747 | 122.2916 | 122.3648 | 122.3007 | 122.5067 | -0.48065 | -0.46234
2055.0781 | 122.3877 | -122.1863 | 0.2243 | 0.012131 | 0.020083 | 0.0037491 | 0.0093673 | -0.0069641 | -0.0079254 | 0.015374 | 0.064087 | 0.31128 | -0.31128 | 0.19684 | 0.064087 | 0.15564 | -0.1236 | 0.32044 | 0.33417 | -0.25177 | 121.875 | 0.086975 | 122.2504 | 122.3831 | -0.16022 | 121.9345 | 0.10986 | 0.37537 | 122.0627 | 122.5067 | 122.2504 | 122.4976 | 122.2504 | 122.5204 | 122.3419 | 121.9345 | 122.4976 | 122.2504 | 122.3419 | 122.2504 | 122.5204 | -0.53558 | -0.47607
2056.7656 | 122.3923 | -122.2366 | 0.23346 | 0.0045011 | 0.021151 | 0.0046037 | 0.011717 | -0.0078187 | -0.00878 | 0.014093 | 0.068665 | 0.30212 | -0.31586 | 0.19684 | 0.068665 | 0.13733 | -0.022888 | 0.32959 | 0.36621 | -0.25635 | 121.9208 | 0.068665 | 122.3053 | 122.4335 | -0.16479 | 121.9803 | 0.13275 | 0.38452 | 122.2137 | 122.5662 | 122.3053 | 122.5388 | 122.3053 | 122.6028 | 122.374 | 121.9803 | 122.5388 | 122.3053 | 122.374 | 122.3053 | 122.6028 | -0.54932 | -0.48981
2058.5156 | 122.5113 | -122.1725 | 0.21515 | 0.0045011 | 0.017947 | 0.0069535 | 0.0074447 | -0.0084595 | -0.0049348 | 0.013452 | 0 | 0.34332 | -0.32501 | 0.14191 | 0.027466 | 0.068665 | 0.059509 | 0.27924 | 0.38452 | -0.27924 | 121.8475 | 0.12817 | 122.1725 | 122.3145 | -0.18768 | 121.8933 | 0.16937 | 0.32501 | 122.2321 | 122.4518 | 122.2 | 122.5159 | 122.1725 | 122.5571 | 122.2412 | 121.8933 | 122.5159 | 122.1725 | 122.2412 | 122.2 | 122.5571 | -0.54016 | -0.49438
2060.25 | 122.3923 | -122.1954 | 0.22888 | -0.010757 | 0.017519 | 0.0028947 | 0.0053085 | -0.0056823 | -0.0066438 | 0.013238 | 0.10986 | 0.27466 | -0.2655 | 0.25177 | 0.13275 | 0.21515 | -0.1831 | 0.37994 | 0.34332 | -0.23804 | 121.9299 | 0.045776 | 122.3053 | 122.4472 | -0.096131 | 121.9574 | 0.11444 | 0.37537 | 122.0123 | 122.5754 | 122.3282 | 122.4701 | 122.3053 | 122.5388 | 122.4106 | 121.9574 | 122.4701 | 122.3053 | 122.4106 | 122.3282 | 122.5388 | -0.49438 | -0.46692
2062 | 122.3969 | -122.2137 | 0.21973 | 0.0045011 | 0.020296 | 0.010799 | 0.010649 | -0.0061097 | -0.0094208 | 0.013025 | 0.073242 | 0.29755 | -0.31128 | 0.19226 | 0.041199 | 0.11444 | -0.009155 | 0.30212 | 0.36621 | -0.26093 | 121.9025 | 0.077819 | 122.287 | 122.406 | -0.17853 | 121.9528 | 0.14648 | 0.38452 | 122.2046 | 122.5159 | 122.2549 | 122.5113 | 122.287 | 122.58 | 122.3282 | 121.9528 | 122.5113 | 122.287 | 122.3282 | 122.2549 | 122.58 | -0.53101 | -0.48065
2063.6875 | 122.4884 | -122.2092 | 0.20142 | -0.0031279 | 0.019015 | 0.0016129 | 0.0029587 | -0.010168 | -0.0049348 | 0.014093 | 0.10071 | 0.28839 | -0.2655 | 0.2655 | 0.15564 | 0.21973 | -0.14191 | 0.42572 | 0.33417 | -0.25177 | 121.9437 | 0.086975 | 122.3099 | 122.4747 | -0.045776 | 121.9574 | 0.13275 | 0.36621 | 122.0673 | 122.6349 | 122.3648 | 122.4976 | 122.3099 | 122.5433 | 122.4289 | 121.9574 | 122.4976 | 122.3099 | 122.4289 | 122.3648 | 122.5433 | -0.46692 | -0.45319
2065.4375 | 122.5388 | -122.1725 | 0.19684 | 0.0045011 | 0.019228 | 0.00075827 | 0.0080857 | -0.0095277 | -0.0066438 | 0.013452 | -0.022888 | 0.31128 | -0.32044 | 0.13733 | 0 | 0.086975 | 0.07782 | 0.28381 | 0.37994 | -0.27466 | 121.8521 | 0.11444 | 122.1497 | 122.3099 | -0.19684 | 121.8979 | 0.18311 | 0.29755 | 122.2504 | 122.4564 | 122.1725 | 122.4838 | 122.1497 | 122.5525 | 122.2595 | 121.8979 | 122.4838 | 122.1497 | 122.2595 | 122.1725 | 122.5525 | -0.51727 | -0.4715
2067.2031 | 122.5433 | -122.1954 | 0.20599 | -0.0031279 | 0.017947 | 0.00011747 | 0.0040269 | -0.0084595 | -0.00643 | 0.013452 | 0.027466 | 0.3067 | -0.31586 | 0.15106 | 0.045776 | 0.09613 | 0.050354 | 0.29297 | 0.3891 | -0.28381 | 121.8796 | 0.10071 | 122.2229 | 122.3465 | -0.16022 | 121.9116 | 0.1831 | 0.34332 | 122.2458 | 122.4884 | 122.2412 | 122.5021 | 122.2229 | 122.5845 | 122.2916 | 121.9116 | 122.5021 | 122.2229 | 122.2916 | 122.2412 | 122.5845 | -0.52185 | -0.48981
2068.8906 | 122.5708 | -122.1909 | 0.19226 | 0.02739 | 0.019869 | -0.00030973 | 0.0070175 | -0.0073913 | -0.0079254 | 0.013665 | 0.009155 | 0.32501 | -0.31586 | 0.14191 | 0.022888 | 0.082397 | 0.059509 | 0.28839 | 0.38452 | -0.29297 | 121.875 | 0.13275 | 122.2 | 122.3328 | -0.16937 | 121.8979 | 0.19226 | 0.32501 | 122.2504 | 122.4792 | 122.2137 | 122.5159 | 122.2 | 122.5754 | 122.2733 | 121.8979 | 122.5159 | 122.2 | 122.2733 | 122.2137 | 122.5754 | -0.50812 | -0.48523
2070.6406 | 122.4564 | -122.2412 | 0.22888 | 0.0045011 | 0.020724 | 0.0067399 | 0.012358 | -0.0065369 | -0.00878 | 0.014306 | 0.050354 | 0.31586 | -0.32501 | 0.13733 | 0 | 0.073242 | 0.018311 | 0.25635 | 0.37994 | -0.2655 | 121.9162 | 0.086975 | 122.2916 | 122.3785 | -0.22888 | 121.9757 | 0.15106 | 0.37537 | 122.2595 | 122.4976 | 122.2412 | 122.5571 | 122.2916 | 122.6212 | 122.3145 | 121.9757 | 122.5571 | 122.2916 | 122.3145 | 122.2412 | 122.6212 | -0.55389 | -0.49438
2072.3906 | 122.5113 | -122.1817 | 0.2243 | -0.0031279 | 0.020296 | 0.0013993 | 0.0048813 | -0.0099549 | -0.0079254 | 0.014093 | 0.10071 | 0.28381 | -0.27466 | 0.25635 | 0.14648 | 0.20599 | -0.10071 | 0.41199 | 0.32959 | -0.24261 | 121.907 | 0.059509 | 122.2824 | 122.4381 | -0.07782 | 121.9391 | 0.10529 | 0.37537 | 122.081 | 122.5937 | 122.3282 | 122.4655 | 122.2824 | 122.5113 | 122.3877 | 121.9391 | 122.4655 | 122.2824 | 122.3877 | 122.3282 | 122.5113 | -0.49896 | -0.46692
2074.0781 | 122.5204 | -122.2137 | 0.19226 | 0.0045011 | 0.019869 | 0.0022537 | 0.010222 | -0.0088867 | -0.0066438 | 0.016443 | 0.004578 | 0.31586 | -0.32501 | 0.15564 | 0.036621 | 0.086975 | 0.073242 | 0.29755 | 0.37079 | -0.27466 | 121.8887 | 0.1236 | 122.2183 | 122.3694 | -0.15564 | 121.9391 | 0.17853 | 0.32959 | 122.287 | 122.5113 | 122.2504 | 122.5296 | 122.2183 | 122.5845 | 122.3007 | 121.9391 | 122.5296 | 122.2183 | 122.3007 | 122.2504 | 122.5845 | -0.51727 | -0.46692
2075.8281 | 122.438 | -122.2412 | 0.23346 | 0.012131 | 0.019869 | 0.0075943 | 0.010008 | -0.0065369 | -0.0083526 | 0.014947 | 0.050354 | 0.32044 | -0.32044 | 0.16937 | 0.036621 | 0.10529 | -0.004578 | 0.27924 | 0.36621 | -0.27466 | 121.9208 | 0.086976 | 122.2916 | 122.4106 | -0.19684 | 121.9666 | 0.13275 | 0.37079 | 122.2366 | 122.5204 | 122.2778 | 122.5616 | 122.2916 | 122.6074 | 122.3465 | 121.9666 | 122.5616 | 122.2916 | 122.3465 | 122.2778 | 122.6074 | -0.55389 | -0.50812
2077.5781 | 122.438 | -122.2366 | 0.2243 | 0.0045011 | 0.020083 | 0.0065263 | 0.0082993 | -0.0061097 | -0.0060028 | 0.015161 | 0.064087 | 0.3067 | -0.28839 | 0.21057 | 0.086975 | 0.17395 | -0.13275 | 0.34332 | 0.34332 | -0.25635 | 121.9482 | 0.082398 | 122.3007 | 122.4472 | -0.13733 | 121.9803 | 0.11902 | 0.35248 | 122.1039 | 122.58 | 122.3236 | 122.5433 | 122.3007 | 122.58 | 122.4106 | 121.9803 | 122.5433 | 122.3007 | 122.4106 | 122.3236 | 122.58 | -0.5127 | -0.48065
2079.2656 | 122.4884 | -122.2321 | 0.21515 | -0.0031279 | 0.019015 | 0.0043899 | 0.0085129 | -0.0086731 | -0.0068574 | 0.014734 | -0.013733 | 0.32501 | -0.32501 | 0.10529 | 0 | 0.068665 | 0 | 0.23346 | 0.36621 | -0.27466 | 121.907 | 0.10986 | 122.2183 | 122.3373 | -0.21515 | 121.9574 | 0.15106 | 0.31128 | 122.2321 | 122.4655 | 122.2321 | 122.5571 | 122.2183 | 122.5983 | 122.3007 | 121.9574 | 122.5571 | 122.2183 | 122.3007 | 122.2321 | 122.5983 | -0.54016 | -0.48981
2081.0312 | 122.4426 | -122.2641 | 0.21973 | -0.0031279 | 0.020937 | 0.0031083 | 0.0093673 | -0.0058961 | -0.0079254 | 0.015161 | 0.064087 | 0.29297 | -0.32044 | 0.16937 | 0.059509 | 0.12817 | -0.013733 | 0.31586 | 0.37079 | -0.25177 | 121.9437 | 0.073242 | 122.3282 | 122.4335 | -0.16022 | 122.0123 | 0.15106 | 0.38452 | 122.2504 | 122.58 | 122.3236 | 122.5571 | 122.3282 | 122.6349 | 122.3923 | 122.0123 | 122.5571 | 122.3282 | 122.3923 | 122.3236 | 122.6349 | -0.54016 | -0.4715
2082.7656 | 122.4472 | -122.2687 | 0.23346 | -0.0031279 | 0.020083 | 0.00075827 | 0.0078721 | -0.0056823 | -0.0068574 | 0.015802 | 0.013733 | 0.29755 | -0.3067 | 0.16937 | 0.045776 | 0.14191 | -0.091553 | 0.29755 | 0.35248 | -0.23346 | 121.962 | 0.064087 | 122.2824 | 122.438 | -0.18768 | 122.0352 | 0.11902 | 0.32043 | 122.1771 | 122.5662 | 122.3145 | 122.5662 | 122.2824 | 122.6212 | 122.4106 | 122.0352 | 122.5662 | 122.2824 | 122.4106 | 122.3145 | 122.6212 | -0.54016 | -0.46692
2084.5156 | 122.4472 | -122.2687 | 0.22888 | 0.012131 | 0.017306 | 0.0052445 | 0.0097947 | -0.0065369 | -0.0096344 | 0.014734 | 0.059509 | 0.31128 | -0.31586 | 0.16479 | 0.045776 | 0.11902 | -0.004578 | 0.27924 | 0.35706 | -0.27924 | 121.9528 | 0.082397 | 122.3282 | 122.4335 | -0.18311 | 121.9894 | 0.12817 | 0.37537 | 122.2641 | 122.5479 | 122.3145 | 122.58 | 122.3282 | 122.6257 | 122.3877 | 121.9894 | 122.58 | 122.3282 | 122.3877 | 122.3145 | 122.6257 | -0.54474 | -0.50812
2086.2031 | 122.493 | -122.2549 | 0.21973 | 0.0045011 | 0.019656 | 0.0078079 | 0.0078721 | -0.0061097 | -0.005362 | 0.015802 | -0.018311 | 0.32959 | -0.31586 | 0.091553 | -0.013733 | 0.054932 | 0.013733 | 0.2243 | 0.37994 | -0.28381 | 121.9391 | 0.10986 | 122.2366 | 122.3465 | -0.23346 | 121.9711 | 0.16022 | 0.29755 | 122.2687 | 122.4792 | 122.2412 | 122.5845 | 122.2366 | 122.6349 | 122.3099 | 121.9711 | 122.5845 | 122.2366 | 122.3099 | 122.2412 | 122.6349 | -0.53558 | -0.50354
2087.9531 | 122.5891 | -122.2092 | 0.1831 | 0.012131 | 0.018801 | 0.0018265 | 0.0010361 | -0.0073913 | -0.0030122 | 0.013879 | 0.054932 | 0.30212 | -0.28381 | 0.18768 | 0.10529 | 0.17395 | -0.086975 | 0.36163 | 0.34332 | -0.25177 | 121.9254 | 0.11902 | 122.2641 | 122.3969 | -0.077819 | 121.9574 | 0.16022 | 0.33874 | 122.1222 | 122.5708 | 122.3145 | 122.5113 | 122.2641 | 122.5525 | 122.3831 | 121.9574 | 122.5113 | 122.2641 | 122.3831 | 122.3145 | 122.5525 | -0.46692 | -0.43488
2089.7188 | 122.5891 | -122.2183 | 0.19684 | -0.0031279 | 0.018801 | 0.0046037 | 0.0042405 | -0.0093139 | -0.0060028 | 0.013879 | 0.059509 | 0.30212 | -0.28381 | 0.18768 | 0.07782 | 0.16937 | -0.09613 | 0.33417 | 0.33417 | -0.2655 | 121.9345 | 0.10529 | 122.2778 | 122.406 | -0.11902 | 121.9528 | 0.13733 | 0.34332 | 122.1222 | 122.5525 | 122.2961 | 122.5204 | 122.2778 | 122.5525 | 122.3877 | 121.9528 | 122.5204 | 122.2778 | 122.3877 | 122.2961 | 122.5525 | -0.48065 | -0.46234
2091.4062 | 122.5616 | -122.2366 | 0.18768 | 0.0045011 | 0.01816 | 0.0031083 | 0.0044541 | -0.011877 | -0.0042938 | 0.01452 | 0.07782 | 0.28381 | -0.28381 | 0.23804 | 0.13275 | 0.21973 | -0.11444 | 0.41657 | 0.33417 | -0.2655 | 121.9528 | 0.09613 | 122.3145 | 122.4747 | -0.054932 | 121.9711 | 0.14648 | 0.36163 | 122.1222 | 122.6532 | 122.3694 | 122.5204 | 122.3145 | 122.5708 | 122.4564 | 121.9711 | 122.5204 | 122.3145 | 122.4564 | 122.3694 | 122.5708 | -0.4715 | -0.45319
2093.1562 | 122.5388 | -122.287 | 0.19684 | 0.0045011 | 0.018374 | 0.0028947 | 0.0095811 | -0.0069641 | -0.0051484 | 0.014093 | 0.018311 | 0.31128 | -0.3067 | 0.17853 | 0.032043 | 0.09613 | 0.004578 | 0.3067 | 0.38452 | -0.27008 | 121.9803 | 0.11444 | 122.3053 | 122.4655 | -0.1648 | 122.0169 | 0.18768 | 0.32501 | 122.2916 | 122.5937 | 122.319 | 122.5983 | 122.3053 | 122.6715 | 122.3831 | 122.0169 | 122.5983 | 122.3053 | 122.3831 | 122.319 | 122.6715 | -0.50354 | -0.46692
2094.9062 | 122.4609 | -122.2824 | 0.2243 | 0.012131 | 0.016665 | 0.0022537 | 0.0046677 | -0.0069641 | -0.0077118 | 0.014734 | 0.11902 | 0.27008 | -0.27008 | 0.23346 | 0.10986 | 0.21057 | -0.16479 | 0.38452 | 0.3067 | -0.25177 | 122.0123 | 0.045777 | 122.4014 | 122.5159 | -0.11444 | 122.0306 | 0.082398 | 0.3891 | 122.1176 | 122.6669 | 122.3923 | 122.5525 | 122.4014 | 122.5891 | 122.493 | 122.0306 | 122.5525 | 122.4014 | 122.493 | 122.3923 | 122.5891 | -0.49439 | -0.47607
2096.5938 | 122.4701 | -122.2778 | 0.21515 | 0.0045011 | 0.020937 | 0.0060989 | 0.011931 | -0.0088867 | -0.0062164 | 0.013665 | 0.064087 | 0.30212 | -0.31128 | 0.17395 | 0.009155 | 0.10986 | -0.018311 | 0.28839 | 0.36163 | -0.28381 | 121.9666 | 0.086975 | 122.3419 | 122.4518 | -0.20599 | 121.994 | 0.14648 | 0.37537 | 122.2595 | 122.5662 | 122.287 | 122.58 | 122.3419 | 122.6395 | 122.3877 | 121.994 | 122.58 | 122.3419 | 122.3877 | 122.287 | 122.6395 | -0.52643 | -0.49896
2098.2812 | 122.5021 | -122.2961 | 0.22888 | 0.01976 | 0.019442 | 0.0016129 | 0.010863 | -0.0065369 | -0.0066438 | 0.015374 | 0.050354 | 0.31586 | -0.31586 | 0.19684 | 0.059509 | 0.13733 | -0.004578 | 0.32044 | 0.37079 | -0.25177 | 121.9803 | 0.086975 | 122.3465 | 122.493 | -0.16937 | 122.0444 | 0.14191 | 0.36621 | 122.2916 | 122.6166 | 122.3557 | 122.612 | 122.3465 | 122.6669 | 122.4335 | 122.0444 | 122.612 | 122.3465 | 122.4335 | 122.3557 | 122.6669 | -0.54474 | -0.48065
2100.0469 | 122.5296 | -122.2916 | 0.23804 | 0.012131 | 0.019442 | 0.0022537 | 0.010222 | -0.0084595 | -0.0034394 | 0.014734 | 0 | 0.32501 | -0.3067 | 0.11902 | -0.004578 | 0.059509 | 0.013733 | 0.21515 | 0.37537 | -0.27924 | 121.9849 | 0.086975 | 122.2916 | 122.4106 | -0.24261 | 122.0123 | 0.13733 | 0.3067 | 122.3053 | 122.5067 | 122.287 | 122.6166 | 122.2916 | 122.6669 | 122.3511 | 122.0123 | 122.6166 | 122.2916 | 122.3511 | 122.287 | 122.6669 | -0.54474 | -0.51727
2101.7969 | 122.4884 | -122.3099 | 0.22888 | 0.0045011 | 0.018587 | 0.0048173 | 0.0070175 | -0.0078187 | -0.0042938 | 0.013238 | 0.064087 | 0.28839 | -0.3067 | 0.22888 | 0.10529 | 0.1831 | -0.15564 | 0.3479 | 0.32959 | -0.23346 | 122.0032 | 0.059509 | 122.374 | 122.5388 | -0.1236 | 122.0764 | 0.10071 | 0.37079 | 122.1542 | 122.6578 | 122.4152 | 122.5983 | 122.374 | 122.6395 | 122.493 | 122.0764 | 122.5983 | 122.374 | 122.493 | 122.4152 | 122.6395 | -0.53558 | -0.46234
2103.5469 | 122.4884 | -122.319 | 0.22888 | 0.0045011 | 0.018801 | 0.0054581 | 0.0082993 | -0.0093139 | -0.008139 | 0.014947 | 0.050354 | 0.31128 | -0.3067 | 0.1831 | 0.064087 | 0.1236 | -0.032043 | 0.31586 | 0.37079 | -0.25177 | 122.0123 | 0.082397 | 122.3694 | 122.5021 | -0.16479 | 122.0673 | 0.14191 | 0.35706 | 122.287 | 122.6349 | 122.3831 | 122.6303 | 122.3694 | 122.6898 | 122.4426 | 122.0673 | 122.6303 | 122.3694 | 122.4426 | 122.3831 | 122.6898 | -0.53558 | -0.48065
2105.2344 | 122.493 | -122.3328 | 0.2655 | 0.0045011 | 0.019228 | -9.6132e-05 | 0.0082993 | -0.0082459 | -0.008139 | 0.016443 | 0.064087 | 0.29755 | -0.31128 | 0.17395 | 0.054932 | 0.11902 | -0.013733 | 0.3067 | 0.37994 | -0.26093 | 122.0215 | 0.032043 | 122.3969 | 122.5067 | -0.21057 | 122.0718 | 0.11444 | 0.37537 | 122.319 | 122.6395 | 122.3877 | 122.6303 | 122.3969 | 122.7127 | 122.4518 | 122.0718 | 122.6303 | 122.3969 | 122.4518 | 122.3877 | 122.7127 | -0.57678 | -0.52643
2106.9844 | 122.5754 | -122.2916 | 0.19684 | -0.0031279 | 0.017306 | 0.0024673 | 0.0014633 | -0.0078187 | -0.0040802 | 0.016015 | 0.09613 | 0.28839 | -0.28381 | 0.23804 | 0.14191 | 0.21515 | -0.12817 | 0.42572 | 0.33875 | -0.24719 | 122.0078 | 0.091553 | 122.3877 | 122.5296 | -0.054931 | 122.0444 | 0.14191 | 0.37994 | 122.1634 | 122.7173 | 122.4335 | 122.58 | 122.3877 | 122.6303 | 122.5067 | 122.0444 | 122.58 | 122.3877 | 122.5067 | 122.4335 | 122.6303 | -0.48065 | -0.44403
2108.7344 | 122.58 | -122.2824 | 0.21515 | 0.0045011 | 0.016238 | 0.00011747 | 0.0053085 | -0.0093139 | -0.0066438 | 0.012811 | 0.10986 | 0.25635 | -0.27924 | 0.25635 | 0.14191 | 0.21973 | -0.11444 | 0.43488 | 0.33417 | -0.25177 | 122.0032 | 0.041199 | 122.3923 | 122.5388 | -0.073242 | 122.0306 | 0.11902 | 0.3891 | 122.168 | 122.7173 | 122.4243 | 122.5388 | 122.3923 | 122.6166 | 122.5021 | 122.0306 | 122.5388 | 122.3923 | 122.5021 | 122.4243 | 122.6166 | -0.49438 | -0.46692
2110.4375 | 122.5983 | -122.2916 | 0.20599 | 0.012131 | 0.01346 | 0.0024673 | 0.0065903 | -0.0088867 | -0.0060028 | 0.01452 | 0.10071 | 0.27466 | -0.29297 | 0.23346 | 0.11444 | 0.18768 | -0.041199 | 0.39368 | 0.33875 | -0.25177 | 121.9986 | 0.068664 | 122.3923 | 122.525 | -0.091553 | 122.0398 | 0.13275 | 0.39368 | 122.2504 | 122.6852 | 122.406 | 122.5662 | 122.3923 | 122.6303 | 122.4792 | 122.0398 | 122.5662 | 122.3923 | 122.4792 | 122.406 | 122.6303 | -0.49896 | -0.45776
2112.1875 | 122.5342 | -122.3007 | 0.20599 | -0.0031279 | 0.017306 | -0.00030973 | 0.0048813 | -0.0084595 | -0.0060028 | 0.013665 | 0.086975 | 0.25635 | -0.26093 | 0.21057 | 0.10986 | 0.18768 | -0.13275 | 0.3479 | 0.32501 | -0.21973 | 122.0398 | 0.050354 | 122.3877 | 122.5113 | -0.096131 | 122.081 | 0.11902 | 0.3479 | 122.168 | 122.6486 | 122.4106 | 122.5571 | 122.3877 | 122.6257 | 122.4884 | 122.081 | 122.5571 | 122.3877 | 122.4884 | 122.4106 | 122.6257 | -0.46692 | -0.42572
2113.9531 | 122.5388 | -122.3511 | 0.21515 | 0.012131 | 0.01816 | 0.0039627 | 0.0082993 | -0.0073913 | -0.0062164 | 0.015802 | 0.068665 | 0.27924 | -0.27466 | 0.21515 | 0.091553 | 0.19684 | -0.14648 | 0.36621 | 0.33417 | -0.23804 | 122.0764 | 0.064087 | 122.4197 | 122.5662 | -0.1236 | 122.113 | 0.11902 | 0.34332 | 122.2046 | 122.7173 | 122.4426 | 122.6303 | 122.4197 | 122.6852 | 122.5479 | 122.113 | 122.6303 | 122.4197 | 122.5479 | 122.4426 | 122.6852 | -0.48981 | -0.45319
2115.7031 | 122.6395 | -122.3099 | 0.1831 | 0.012131 | 0.016024 | 0.0022537 | 0.0074447 | -0.010596 | -0.00643 | 0.013665 | 0.054932 | 0.29297 | -0.28839 | 0.21973 | 0.073242 | 0.14191 | 0 | 0.35706 | 0.36163 | -0.25177 | 122.0215 | 0.10986 | 122.3648 | 122.5296 | -0.10986 | 122.0581 | 0.17853 | 0.34332 | 122.3099 | 122.6669 | 122.3831 | 122.6028 | 122.3648 | 122.6715 | 122.4518 | 122.0581 | 122.6028 | 122.3648 | 122.4518 | 122.3831 | 122.6715 | -0.4715 | -0.43488
2117.3906 | 122.5296 | -122.3328 | 0.20599 | -0.0031279 | 0.01816 | 0.0024673 | 0.0074447 | -0.0082459 | -0.0049348 | 0.013025 | 0.1236 | 0.27008 | -0.27008 | 0.2655 | 0.1236 | 0.20599 | -0.17395 | 0.3891 | 0.32501 | -0.21515 | 122.0627 | 0.064087 | 122.4564 | 122.5983 | -0.082398 | 122.1176 | 0.11902 | 0.39368 | 122.1588 | 122.7219 | 122.4564 | 122.6028 | 122.4564 | 122.6578 | 122.5388 | 122.1176 | 122.6028 | 122.4564 | 122.5388 | 122.4564 | 122.6578 | -0.47608 | -0.42114
2119.1406 | 122.6212 | -122.2916 | 0.20142 | 0.0045011 | 0.018374 | 0.0054581 | 0.0055221 | -0.0091003 | -0.0055756 | 0.01217 | 0.064087 | 0.28381 | -0.28381 | 0.19684 | 0.082397 | 0.16479 | -0.10529 | 0.35706 | 0.33875 | -0.27008 | 122.0078 | 0.082397 | 122.3557 | 122.4884 | -0.11902 | 122.0215 | 0.13733 | 0.3479 | 122.1863 | 122.6486 | 122.374 | 122.5754 | 122.3557 | 122.6303 | 122.4564 | 122.0215 | 122.5754 | 122.3557 | 122.4564 | 122.374 | 122.6303 | -0.48523 | -0.4715
2120.8906 | 122.6578 | -122.3007 | 0.20599 | 0.01976 | 0.018374 | 0.0037491 | 0.0097947 | -0.0099549 | -0.0055756 | 0.014093 | 0 | 0.31128 | -0.3067 | 0.14648 | 0.013733 | 0.068665 | 0.064087 | 0.28839 | 0.37079 | -0.28839 | 121.994 | 0.10528 | 122.3007 | 122.4472 | -0.19226 | 122.0123 | 0.16479 | 0.3067 | 122.3648 | 122.5891 | 122.3145 | 122.612 | 122.3007 | 122.6715 | 122.3694 | 122.0123 | 122.612 | 122.3007 | 122.3694 | 122.3145 | 122.6715 | -0.5127 | -0.49439
2122.5781 | 122.6074 | -122.319 | 0.21057 | -0.0031279 | 0.01816 | 0.0013993 | 0.0048813 | -0.0082459 | -0.0049348 | 0.013025 | 0.13733 | 0.28381 | -0.28839 | 0.27924 | 0.16022 | 0.21973 | -0.11444 | 0.42572 | 0.33875 | -0.24261 | 122.0306 | 0.073242 | 122.4564 | 122.5983 | -0.050354 | 122.0764 | 0.12817 | 0.42572 | 122.2046 | 122.7448 | 122.4792 | 122.6028 | 122.4564 | 122.6578 | 122.5388 | 122.0764 | 122.6028 | 122.4564 | 122.5388 | 122.4792 | 122.6578 | -0.49896 | -0.45319
2124.3438 | 122.6624 | -122.3236 | 0.19684 | 0.012131 | 0.017733 | -0.0013779 | 0.0061631 | -0.0076049 | -0.0094208 | 0.012811 | 0.041199 | 0.29755 | -0.29297 | 0.17395 | 0.045776 | 0.09613 | 0.013733 | 0.31586 | 0.37537 | -0.27008 | 122.0306 | 0.10071 | 122.3648 | 122.4976 | -0.15106 | 122.0535 | 0.17853 | 0.33417 | 122.3373 | 122.6395 | 122.3694 | 122.6212 | 122.3648 | 122.699 | 122.4197 | 122.0535 | 122.6212 | 122.3648 | 122.4197 | 122.3694 | 122.699 | -0.48981 | -0.46692
2126.0938 | 122.6395 | -122.3145 | 0.19226 | 0.012131 | 0.01581 | 0.0048173 | 0.0040269 | -0.011236 | -0.0057892 | 0.012811 | 0.07782 | 0.27924 | -0.27924 | 0.24261 | 0.13275 | 0.18768 | -0.11902 | 0.40283 | 0.34332 | -0.26093 | 122.0352 | 0.086975 | 122.3923 | 122.5571 | -0.05951 | 122.0535 | 0.15106 | 0.35706 | 122.1954 | 122.7173 | 122.4472 | 122.5937 | 122.3923 | 122.6578 | 122.5021 | 122.0535 | 122.5937 | 122.3923 | 122.5021 | 122.4472 | 122.6578 | -0.4715 | -0.45319
2127.8438 | 122.5708 | -122.3419 | 0.20142 | 0.012131 | 0.018374 | 0.0060989 | 0.012572 | -0.0082459 | -0.0072846 | 0.013452 | 0.018311 | 0.32044 | -0.32044 | 0.16022 | 0 | 0.073242 | -0.036621 | 0.23346 | 0.38452 | -0.2655 | 122.0215 | 0.11902 | 122.3602 | 122.5021 | -0.20142 | 122.0764 | 0.1831 | 0.33875 | 122.3053 | 122.5754 | 122.3419 | 122.6624 | 122.3602 | 122.7264 | 122.4152 | 122.0764 | 122.6624 | 122.3602 | 122.4152 | 122.3419 | 122.7264 | -0.52185 | -0.46692
2129.5469 | 122.5845 | -122.3419 | 0.22888 | 0.012131 | 0.020724 | 0.0056717 | 0.010649 | -0.0063233 | -0.007071 | 0.016443 | 0.004578 | 0.32501 | -0.32959 | 0.13733 | -0.018311 | 0.064087 | 0.009155 | 0.22888 | 0.37537 | -0.27466 | 122.0123 | 0.09613 | 122.3465 | 122.4792 | -0.24719 | 122.0673 | 0.14648 | 0.33417 | 122.3511 | 122.5708 | 122.3236 | 122.6669 | 122.3465 | 122.7173 | 122.406 | 122.0673 | 122.6669 | 122.3465 | 122.406 | 122.3236 | 122.7173 | -0.55847 | -0.50354
2131.2969 | 122.644 | -122.3145 | 0.20142 | -0.0031279 | 0.017092 | 0.0058853 | 0.0048813 | -0.0091003 | -0.0051484 | 0.014306 | 0.11902 | 0.27924 | -0.27466 | 0.24719 | 0.1236 | 0.18768 | -0.050354 | 0.37994 | 0.36163 | -0.26093 | 122.0398 | 0.07782 | 122.4335 | 122.5616 | -0.07782 | 122.0535 | 0.16022 | 0.39368 | 122.2641 | 122.6944 | 122.438 | 122.5937 | 122.4335 | 122.6761 | 122.5021 | 122.0535 | 122.5937 | 122.4335 | 122.5021 | 122.438 | 122.6761 | -0.47607 | -0.46234
2133.0469 | 122.5296 | -122.3511 | 0.22888 | -0.0031279 | 0.018801 | 0.0039627 | 0.011931 | -0.0061097 | -0.0083526 | 0.014093 | 0.073242 | 0.30212 | -0.3067 | 0.20142 | 0.064087 | 0.13733 | -0.036621 | 0.32959 | 0.37994 | -0.25635 | 122.0444 | 0.073242 | 122.4243 | 122.5525 | -0.16479 | 122.0947 | 0.15106 | 0.37994 | 122.3145 | 122.6807 | 122.4152 | 122.6532 | 122.4243 | 122.731 | 122.4884 | 122.0947 | 122.6532 | 122.4243 | 122.4884 | 122.4152 | 122.731 | -0.53558 | -0.48523
2134.8125 | 122.5388 | -122.3831 | 0.23346 | 0.0045011 | 0.020083 | 0.0058853 | 0.010222 | -0.0069641 | -0.0066438 | 0.01452 | 0.059509 | 0.30212 | -0.32501 | 0.21057 | 0.073242 | 0.10986 | -0.022888 | 0.32959 | 0.36163 | -0.24261 | 122.0581 | 0.068665 | 122.4426 | 122.5937 | -0.16022 | 122.1405 | 0.12817 | 0.38452 | 122.3602 | 122.7127 | 122.4564 | 122.6852 | 122.4426 | 122.7448 | 122.493 | 122.1405 | 122.6852 | 122.4426 | 122.493 | 122.4564 | 122.7448 | -0.55847 | -0.47607
2136.5156 | 122.5479 | -122.374 | 0.20599 | -0.0031279 | 0.02051 | 0.0067399 | 0.0059495 | -0.0058961 | -0.0055756 | 0.016443 | 0.12817 | 0.27924 | -0.25177 | 0.23804 | 0.14648 | 0.20599 | -0.1831 | 0.37994 | 0.32044 | -0.23346 | 122.1222 | 0.073242 | 122.5021 | 122.612 | -0.05951 | 122.1405 | 0.11444 | 0.37994 | 122.1909 | 122.7539 | 122.5204 | 122.6532 | 122.5021 | 122.6944 | 122.58 | 122.1405 | 122.6532 | 122.5021 | 122.58 | 122.5204 | 122.6944 | -0.45776 | -0.43945
2138.2656 | 122.5525 | -122.3831 | 0.22888 | 0.012131 | 0.018374 | 0.0080215 | 0.010222 | -0.0080323 | -0.0092072 | 0.015161 | 0.064087 | 0.31128 | -0.31128 | 0.19684 | 0.064087 | 0.14191 | -0.013733 | 0.32959 | 0.35706 | -0.2655 | 122.0718 | 0.082397 | 122.4472 | 122.58 | -0.16479 | 122.1176 | 0.12817 | 0.37537 | 122.3694 | 122.7127 | 122.4472 | 122.6944 | 122.4472 | 122.7402 | 122.525 | 122.1176 | 122.6944 | 122.4472 | 122.525 | 122.4472 | 122.7402 | -0.54016 | -0.49438
2140.0312 | 122.5983 | -122.3511 | 0.21057 | 0.01976 | 0.021578 | 0.00054467 | 0.0055221 | -0.0086731 | -0.0055756 | 0.01687 | 0.09613 | 0.27924 | -0.27008 | 0.21057 | 0.10529 | 0.19226 | -0.14191 | 0.33875 | 0.32044 | -0.25177 | 122.081 | 0.068665 | 122.4472 | 122.5616 | -0.10529 | 122.0993 | 0.10986 | 0.36621 | 122.2092 | 122.6898 | 122.4564 | 122.6303 | 122.4472 | 122.6715 | 122.5433 | 122.0993 | 122.6303 | 122.4472 | 122.5433 | 122.4564 | 122.6715 | -0.48065 | -0.46234
2141.7188 | 122.6028 | -122.3694 | 0.20599 | -0.0031279 | 0.021151 | 0.0080215 | 0.0082993 | -0.0069641 | -0.0068574 | 0.013665 | -0.004578 | 0.28839 | -0.32501 | 0.13733 | 0.022888 | 0.091553 | -0.009155 | 0.25635 | 0.37994 | -0.2655 | 122.0444 | 0.082397 | 122.3648 | 122.5067 | -0.18311 | 122.1039 | 0.17395 | 0.32043 | 122.3602 | 122.6257 | 122.3923 | 122.6578 | 122.3648 | 122.7493 | 122.4609 | 122.1039 | 122.6578 | 122.3648 | 122.4609 | 122.3923 | 122.7493 | -0.53101 | -0.4715
2143.4844 | 122.6715 | -122.3145 | 0.18768 | 0.012131 | 0.017092 | 0.0039627 | 0.0016769 | -0.0099549 | -0.0049348 | 0.014306 | 0.059509 | 0.30212 | -0.25177 | 0.20599 | 0.10071 | 0.16479 | -0.10071 | 0.33875 | 0.34332 | -0.26093 | 122.0627 | 0.11444 | 122.374 | 122.5204 | -0.086975 | 122.0535 | 0.15564 | 0.31128 | 122.2137 | 122.6532 | 122.4152 | 122.6166 | 122.374 | 122.6578 | 122.4792 | 122.0535 | 122.6166 | 122.374 | 122.4792 | 122.4152 | 122.6578 | -0.43945 | -0.44861
2145.1719 | 122.5754 | -122.3831 | 0.21515 | -0.0031279 | 0.01581 | 0.0073807 | 0.0048813 | -0.0073913 | -0.0089936 | 0.013238 | 0.12817 | 0.27466 | -0.27924 | 0.24719 | 0.12817 | 0.21973 | -0.16022 | 0.37994 | 0.33417 | -0.23346 | 122.1039 | 0.059509 | 122.5113 | 122.6303 | -0.086975 | 122.1497 | 0.11902 | 0.40741 | 122.2229 | 122.7631 | 122.5113 | 122.6578 | 122.5113 | 122.7173 | 122.6028 | 122.1497 | 122.6578 | 122.5113 | 122.6028 | 122.5113 | 122.7173 | -0.49438 | -0.44861
2146.9062 | 122.5891 | -122.3831 | 0.2243 | 0.012131 | 0.01581 | 0.0043899 | 0.0053085 | -0.0063233 | -0.0092072 | 0.015588 | 0.10529 | 0.27466 | -0.2655 | 0.21973 | 0.10986 | 0.18768 | -0.14191 | 0.35248 | 0.34332 | -0.23346 | 122.1176 | 0.050354 | 122.4884 | 122.6028 | -0.11444 | 122.1497 | 0.11902 | 0.37079 | 122.2412 | 122.7356 | 122.493 | 122.6578 | 122.4884 | 122.7264 | 122.5708 | 122.1497 | 122.6578 | 122.4884 | 122.5708 | 122.493 | 122.7264 | -0.48981 | -0.45776
2148.6562 | 122.7081 | -122.3511 | 0.18768 | 0.0045011 | 0.01816 | 0.0031083 | 0.0072311 | -0.0071777 | -0.0079254 | 0.016443 | 0.064087 | 0.28839 | -0.28839 | 0.17853 | 0.064087 | 0.13275 | 0 | 0.32501 | 0.36163 | -0.24261 | 122.0627 | 0.10071 | 122.4152 | 122.5296 | -0.1236 | 122.1085 | 0.17395 | 0.35248 | 122.3511 | 122.6761 | 122.4152 | 122.6395 | 122.4152 | 122.7127 | 122.4838 | 122.1085 | 122.6395 | 122.4152 | 122.4838 | 122.4152 | 122.7127 | -0.47607 | -0.4303
2150.4219 | 122.6624 | -122.3511 | 0.20599 | 0.012131 | 0.017306 | 0.00011747 | 0.0063767 | -0.0095277 | -0.0049348 | 0.01217 | 0.1236 | 0.27924 | -0.24719 | 0.25635 | 0.12817 | 0.1831 | -0.11444 | 0.42114 | 0.33417 | -0.22888 | 122.1039 | 0.073242 | 122.4747 | 122.6074 | -0.07782 | 122.1222 | 0.12817 | 0.37079 | 122.2366 | 122.7722 | 122.4792 | 122.6303 | 122.4747 | 122.6852 | 122.5342 | 122.1222 | 122.6303 | 122.4747 | 122.5342 | 122.4792 | 122.6852 | -0.45319 | -0.43488
2152.1094 | 122.5525 | -122.4152 | 0.2243 | 0.012131 | 0.019442 | 0.0058853 | 0.0095811 | -0.0073913 | -0.008139 | 0.015161 | 0.1236 | 0.27466 | -0.27924 | 0.26093 | 0.1236 | 0.21057 | -0.18768 | 0.37994 | 0.33417 | -0.22888 | 122.1359 | 0.050354 | 122.5388 | 122.6761 | -0.10071 | 122.1863 | 0.10986 | 0.40283 | 122.2275 | 122.7951 | 122.5388 | 122.6898 | 122.5388 | 122.7493 | 122.6257 | 122.1863 | 122.6898 | 122.5388 | 122.6257 | 122.5388 | 122.7493 | -0.50354 | -0.45319
2153.8594 | 122.5937 | -122.374 | 0.22888 | -0.010757 | 0.020083 | 0.0063125 | 0.0072311 | -0.0071777 | -0.0060028 | 0.015588 | 0.10529 | 0.28381 | -0.27924 | 0.24261 | 0.10986 | 0.21057 | -0.16479 | 0.36621 | 0.32959 | -0.23804 | 122.0947 | 0.054931 | 122.4792 | 122.6166 | -0.11902 | 122.1359 | 0.10071 | 0.38452 | 122.2092 | 122.7402 | 122.4838 | 122.6578 | 122.4792 | 122.7036 | 122.5845 | 122.1359 | 122.6578 | 122.4792 | 122.5845 | 122.4838 | 122.7036 | -0.50812 | -0.46692
2155.6094 | 122.6486 | -122.3831 | 0.21973 | 0.012131 | 0.01816 | 0.0041763 | 0.0050949 | -0.010168 | -0.005362 | 0.01452 | 0.068665 | 0.27924 | -0.26093 | 0.21515 | 0.086975 | 0.18768 | -0.11902 | 0.3479 | 0.3479 | -0.24261 | 122.1222 | 0.059509 | 122.4518 | 122.5983 | -0.13275 | 122.1405 | 0.12817 | 0.32959 | 122.2641 | 122.731 | 122.4701 | 122.6624 | 122.4518 | 122.731 | 122.5708 | 122.1405 | 122.6624 | 122.4518 | 122.5708 | 122.4701 | 122.731 | -0.48065 | -0.46234
2157.3594 | 122.5845 | -122.4014 | 0.23804 | 0.012131 | 0.019228 | 0.0058853 | 0.012572 | -0.0097413 | -0.009848 | 0.014306 | 0.073242 | 0.29755 | -0.3067 | 0.20142 | 0.050354 | 0.12817 | -0.022888 | 0.32501 | 0.35706 | -0.26093 | 122.0947 | 0.059509 | 122.4747 | 122.6028 | -0.18768 | 122.1405 | 0.11902 | 0.37994 | 122.3785 | 122.7264 | 122.4518 | 122.699 | 122.4747 | 122.7585 | 122.5296 | 122.1405 | 122.699 | 122.4747 | 122.5296 | 122.4518 | 122.7585 | -0.54474 | -0.49896
2159.0469 | 122.699 | -122.3785 | 0.21515 | 0.0045011 | 0.020083 | 0.0065263 | 0.0085129 | -0.0078187 | -0.0083526 | 0.013238 | 0.022888 | 0.32501 | -0.31586 | 0.17853 | 0.032043 | 0.086975 | 0.054932 | 0.31128 | 0.38452 | -0.27466 | 122.0627 | 0.10986 | 122.4014 | 122.5571 | -0.18311 | 122.1039 | 0.16937 | 0.33875 | 122.4335 | 122.6898 | 122.4106 | 122.7036 | 122.4014 | 122.7631 | 122.4655 | 122.1039 | 122.7036 | 122.4014 | 122.4655 | 122.4106 | 122.7631 | -0.53101 | -0.48981
2160.7969 | 122.6761 | -122.3831 | 0.21515 | -0.0031279 | 0.018801 | -0.0015915 | 0.0025315 | -0.0086731 | -0.0055756 | 0.01452 | 0.14191 | 0.2655 | -0.25635 | 0.2655 | 0.15106 | 0.2243 | -0.11902 | 0.43945 | 0.3479 | -0.24261 | 122.1268 | 0.050354 | 122.525 | 122.6486 | -0.064087 | 122.1405 | 0.13275 | 0.39826 | 122.2641 | 122.8226 | 122.5342 | 122.6486 | 122.525 | 122.731 | 122.6074 | 122.1405 | 122.6486 | 122.525 | 122.6074 | 122.5342 | 122.731 | -0.4715 | -0.45776
2162.5312 | 122.6898 | -122.3969 | 0.21515 | 0.0045011 | 0.021365 | 0.0056717 | 0.0068039 | -0.0078187 | -0.00878 | 0.013025 | 0.022888 | 0.33875 | -0.33417 | 0.16479 | 0.041199 | 0.10071 | 0.045776 | 0.28839 | 0.37994 | -0.26093 | 122.0627 | 0.1236 | 122.4197 | 122.5616 | -0.17395 | 122.1359 | 0.16479 | 0.35706 | 122.4426 | 122.6852 | 122.4381 | 122.7356 | 122.4197 | 122.7768 | 122.4976 | 122.1359 | 122.7356 | 122.4197 | 122.4976 | 122.4381 | 122.7768 | -0.54932 | -0.47607
2164.2812 | 122.5983 | -122.3923 | 0.21057 | 0.012131 | 0.022433 | 0.0024673 | 0.0078721 | -0.0086731 | -0.0062164 | 0.014734 | 0.10071 | 0.29297 | -0.28839 | 0.22888 | 0.10986 | 0.19684 | -0.15106 | 0.36621 | 0.33417 | -0.22888 | 122.1039 | 0.082398 | 122.493 | 122.6212 | -0.10071 | 122.1634 | 0.1236 | 0.3891 | 122.2412 | 122.7585 | 122.5021 | 122.6852 | 122.493 | 122.7264 | 122.5891 | 122.1634 | 122.6852 | 122.493 | 122.5891 | 122.5021 | 122.7264 | -0.49896 | -0.43945
2166.0469 | 122.6166 | -122.4152 | 0.21973 | 0.012131 | 0.019442 | 0.0054581 | 0.011076 | -0.0054687 | -0.0083526 | 0.014306 | 0.064087 | 0.31586 | -0.28381 | 0.16479 | 0.018311 | 0.10529 | 0.009155 | 0.27924 | 0.3891 | -0.27466 | 122.1313 | 0.09613 | 122.4792 | 122.58 | -0.20142 | 122.1405 | 0.16937 | 0.3479 | 122.4243 | 122.6944 | 122.4335 | 122.731 | 122.4792 | 122.8043 | 122.5204 | 122.1405 | 122.731 | 122.4792 | 122.5204 | 122.4335 | 122.8043 | -0.50354 | -0.49439
2167.75 | 122.612 | -122.4243 | 0.25177 | 0.0045011 | 0.019656 | 0.0031083 | 0.01129 | -0.0082459 | -0.008139 | 0.014734 | 0.082397 | 0.29755 | -0.32044 | 0.1831 | 0.064087 | 0.13275 | -0.009155 | 0.3067 | 0.36621 | -0.25635 | 122.1039 | 0.045776 | 122.5067 | 122.6074 | -0.18768 | 122.168 | 0.11444 | 0.40283 | 122.4152 | 122.731 | 122.4884 | 122.7219 | 122.5067 | 122.7905 | 122.5571 | 122.168 | 122.7219 | 122.5067 | 122.5571 | 122.4884 | 122.7905 | -0.57221 | -0.50812
2169.5156 | 122.6624 | -122.4289 | 0.21515 | -0.0031279 | 0.017947 | 0.0020401 | 0.0059495 | -0.0067505 | -0.007071 | 0.014306 | 0.041199 | 0.31586 | -0.3067 | 0.16937 | 0.068665 | 0.1236 | 0.004578 | 0.32044 | 0.37079 | -0.26093 | 122.1222 | 0.10071 | 122.4701 | 122.5983 | -0.14648 | 122.168 | 0.15564 | 0.3479 | 122.4335 | 122.7493 | 122.4976 | 122.7448 | 122.4701 | 122.7997 | 122.5525 | 122.168 | 122.7448 | 122.4701 | 122.5525 | 122.4976 | 122.7997 | -0.52185 | -0.47607
2171.2031 | 122.7722 | -122.3785 | 0.20599 | -0.0031279 | 0.020083 | 0.00054467 | 0.0025315 | -0.011236 | -0.0055756 | 0.01217 | 0.013733 | 0.32044 | -0.32501 | 0.13733 | 0.036621 | 0.09613 | 0.073242 | 0.29755 | 0.38452 | -0.27924 | 122.0535 | 0.11444 | 122.3923 | 122.5159 | -0.16937 | 122.0993 | 0.17853 | 0.33875 | 122.4518 | 122.6761 | 122.4152 | 122.699 | 122.3923 | 122.7631 | 122.4747 | 122.0993 | 122.699 | 122.3923 | 122.4747 | 122.4152 | 122.7631 | -0.53101 | -0.48523
2172.9531 | 122.6349 | -122.4243 | 0.2243 | -0.0031279 | 0.022646 | 0.0024673 | 0.0095811 | -0.0069641 | -0.0062164 | 0.01217 | 0.068665 | 0.32501 | -0.29755 | 0.20142 | 0.068665 | 0.12817 | -0.009155 | 0.32044 | 0.37079 | -0.25177 | 122.1268 | 0.10071 | 122.493 | 122.6257 | -0.15564 | 122.1725 | 0.14648 | 0.36621 | 122.4152 | 122.7448 | 122.493 | 122.7493 | 122.493 | 122.7951 | 122.5525 | 122.1725 | 122.7493 | 122.493 | 122.5525 | 122.493 | 122.7951 | -0.52185 | -0.47607
2174.6406 | 122.6074 | -122.4518 | 0.21973 | 0.0045011 | 0.01816 | 0.0028947 | 0.0065903 | -0.0056823 | -0.008139 | 0.014306 | 0.12817 | 0.27466 | -0.29297 | 0.24719 | 0.13733 | 0.23346 | -0.1831 | 0.39368 | 0.32959 | -0.22888 | 122.1588 | 0.054931 | 122.58 | 122.699 | -0.082398 | 122.2229 | 0.10986 | 0.42114 | 122.2687 | 122.8455 | 122.5891 | 122.7264 | 122.58 | 122.7814 | 122.6852 | 122.2229 | 122.7264 | 122.58 | 122.6852 | 122.5891 | 122.7814 | -0.5127 | -0.44861
2176.4062 | 122.6257 | -122.438 | 0.22888 | 0.0045011 | 0.022005 | 0.0048173 | 0.0065903 | -0.0058961 | -0.0057892 | 0.013238 | 0.041199 | 0.32044 | -0.28839 | 0.1831 | 0.064087 | 0.14191 | -0.07782 | 0.29755 | 0.36163 | -0.25177 | 122.1497 | 0.091553 | 122.4792 | 122.6212 | -0.16479 | 122.1863 | 0.13275 | 0.32959 | 122.3602 | 122.7356 | 122.5021 | 122.7585 | 122.4792 | 122.7997 | 122.58 | 122.1863 | 122.7585 | 122.4792 | 122.58 | 122.5021 | 122.7997 | -0.51727 | -0.48065
2178.1562 | 122.7448 | -122.3877 | 0.20599 | -0.0031279 | 0.018801 | 0.0039627 | 0.0021043 | -0.0091003 | -0.0062164 | 0.014947 | 0.045776 | 0.27924 | -0.27466 | 0.19226 | 0.10071 | 0.15564 | -0.082397 | 0.35706 | 0.33875 | -0.24719 | 122.113 | 0.073242 | 122.4335 | 122.58 | -0.10529 | 122.1405 | 0.13275 | 0.32043 | 122.3053 | 122.7448 | 122.4884 | 122.6669 | 122.4335 | 122.7264 | 122.5433 | 122.1405 | 122.6669 | 122.4335 | 122.5433 | 122.4884 | 122.7264 | -0.48065 | -0.45319
2179.9219 | 122.7631 | -122.3969 | 0.1831 | 0.0045011 | 0.018374 | 0.00097207 | 0.0055221 | -0.0095277 | -0.0057892 | 0.013665 | 0.027466 | 0.30212 | -0.32959 | 0.14648 | 0.022888 | 0.086975 | 0.068665 | 0.31128 | 0.39368 | -0.27924 | 122.0673 | 0.11902 | 122.4243 | 122.5433 | -0.16022 | 122.1176 | 0.21057 | 0.35706 | 122.4655 | 122.7081 | 122.4197 | 122.699 | 122.4243 | 122.7905 | 122.4838 | 122.1176 | 122.699 | 122.4243 | 122.4838 | 122.4197 | 122.7905 | -0.5127 | -0.46234
2181.6094 | 122.7493 | -122.3831 | 0.20599 | -0.0031279 | 0.018587 | 0.0011857 | 0.0031723 | -0.010168 | -0.0057892 | 0.013879 | 0.068665 | 0.29755 | -0.27008 | 0.21057 | 0.086975 | 0.18768 | -0.091553 | 0.37079 | 0.33417 | -0.25177 | 122.113 | 0.091552 | 122.4518 | 122.5937 | -0.11902 | 122.1313 | 0.12817 | 0.33875 | 122.2916 | 122.7539 | 122.4701 | 122.6807 | 122.4518 | 122.7173 | 122.5708 | 122.1313 | 122.6807 | 122.4518 | 122.5708 | 122.4701 | 122.7173 | -0.47608 | -0.45776
2183.3594 | 122.7081 | -122.406 | 0.20599 | -0.0031279 | 0.017733 | -0.0045821 | 0.0038131 | -0.0091003 | -0.0049348 | 0.012597 | 0.10986 | 0.27008 | -0.27466 | 0.27466 | 0.14648 | 0.21973 | -0.11902 | 0.4303 | 0.32501 | -0.22888 | 122.1313 | 0.064087 | 122.5159 | 122.6807 | -0.05951 | 122.1771 | 0.11902 | 0.38452 | 122.287 | 122.8363 | 122.5525 | 122.6761 | 122.5159 | 122.731 | 122.6257 | 122.1771 | 122.6761 | 122.5159 | 122.6257 | 122.5525 | 122.731 | -0.48065 | -0.43488
2185.125 | 122.6532 | -122.4564 | 0.23346 | 0.0045011 | 0.019442 | 0.0095169 | 0.0065903 | -0.0086731 | -0.0062164 | 0.016229 | 0.12817 | 0.28381 | -0.27008 | 0.24719 | 0.10529 | 0.21515 | -0.16022 | 0.38452 | 0.32501 | -0.2243 | 122.1863 | 0.050354 | 122.5845 | 122.7036 | -0.12817 | 122.2321 | 0.091553 | 0.39826 | 122.2961 | 122.8409 | 122.5616 | 122.7402 | 122.5845 | 122.7814 | 122.6715 | 122.2321 | 122.7402 | 122.5845 | 122.6715 | 122.5616 | 122.7814 | -0.50354 | -0.45776
2186.8125 | 122.7814 | -122.4152 | 0.19226 | 0.012131 | 0.017947 | -9.6132e-05 | 0.0065903 | -0.010809 | -0.0049348 | 0.015161 | -0.004578 | 0.32044 | -0.32044 | 0.14191 | 0.036621 | 0.07782 | 0.082397 | 0.29297 | 0.3891 | -0.28381 | 122.0947 | 0.12817 | 122.4106 | 122.5571 | -0.15564 | 122.1313 | 0.19684 | 0.31586 | 122.4976 | 122.7081 | 122.4518 | 122.7356 | 122.4106 | 122.8043 | 122.493 | 122.1313 | 122.7356 | 122.4106 | 122.493 | 122.4518 | 122.8043 | -0.5127 | -0.47607
2188.5781 | 122.731 | -122.3969 | 0.19684 | -0.0031279 | 0.016878 | -0.00052333 | 0.0076585 | -0.010168 | -0.0032258 | 0.014947 | 0.10986 | 0.28839 | -0.27466 | 0.27008 | 0.15106 | 0.21515 | -0.11444 | 0.41657 | 0.36163 | -0.22888 | 122.1222 | 0.091553 | 122.5067 | 122.6669 | -0.045776 | 122.168 | 0.16479 | 0.38452 | 122.2824 | 122.8134 | 122.5479 | 122.6852 | 122.5067 | 122.7585 | 122.612 | 122.168 | 122.6852 | 122.5067 | 122.612 | 122.5479 | 122.7585 | -0.4715 | -0.42572
2190.3438 | 122.7448 | -122.4197 | 0.19226 | -0.0031279 | 0.019015 | 0.0041763 | 0.0046677 | -0.010382 | -0.0055756 | 0.01452 | 0.064087 | 0.28381 | -0.27466 | 0.20142 | 0.10071 | 0.16022 | -0.09613 | 0.3479 | 0.32959 | -0.27008 | 122.1451 | 0.091552 | 122.4838 | 122.6212 | -0.091553 | 122.1497 | 0.13733 | 0.33875 | 122.3236 | 122.7676 | 122.5204 | 122.7036 | 122.4838 | 122.7493 | 122.58 | 122.1497 | 122.7036 | 122.4838 | 122.58 | 122.5204 | 122.7493 | -0.46692 | -0.46234
2192.0938 | 122.7997 | -122.4197 | 0.18768 | 0.0045011 | 0.018587 | 0.0026809 | 0.0076585 | -0.010809 | -0.0066438 | 0.012811 | -0.018311 | 0.33417 | -0.31586 | 0.15106 | 0.027466 | 0.064087 | 0.073242 | 0.30212 | 0.39825 | -0.27008 | 122.1039 | 0.14648 | 122.4014 | 122.5708 | -0.16022 | 122.1497 | 0.21057 | 0.29755 | 122.493 | 122.7219 | 122.4472 | 122.7539 | 122.4014 | 122.818 | 122.4838 | 122.1497 | 122.7539 | 122.4014 | 122.4838 | 122.4472 | 122.818 | -0.50354 | -0.45776
2193.7969 | 122.7722 | -122.406 | 0.20142 | -0.0031279 | 0.01816 | 0.0024673 | 0.0061631 | -0.0082459 | -0.0077118 | 0.01452 | 0.07782 | 0.30212 | -0.28381 | 0.17395 | 0.064087 | 0.12817 | 0.013733 | 0.33875 | 0.36163 | -0.24719 | 122.1222 | 0.10071 | 122.4838 | 122.58 | -0.13733 | 122.1588 | 0.16022 | 0.36163 | 122.4197 | 122.7448 | 122.4701 | 122.7081 | 122.4838 | 122.7676 | 122.5342 | 122.1588 | 122.7081 | 122.4838 | 122.5342 | 122.4701 | 122.7676 | -0.48523 | -0.44861
2195.5469 | 122.7448 | -122.4152 | 0.20142 | -0.0031279 | 0.017733 | 0.0020401 | 0.0046677 | -0.0093139 | -0.00643 | 0.015161 | 0.09613 | 0.27466 | -0.27008 | 0.26093 | 0.15106 | 0.21515 | -0.11444 | 0.41657 | 0.34332 | -0.24719 | 122.1451 | 0.073242 | 122.5113 | 122.6761 | -0.050354 | 122.168 | 0.14191 | 0.36621 | 122.3007 | 122.8317 | 122.5662 | 122.6898 | 122.5113 | 122.7585 | 122.6303 | 122.168 | 122.6898 | 122.5113 | 122.6303 | 122.5662 | 122.7585 | -0.4715 | -0.44861
2197.2969 | 122.7676 | -122.4289 | 0.19684 | 0.0045011 | 0.017519 | 0.0058853 | 0.0063767 | -0.0097413 | -0.007071 | 0.014093 | 0.068665 | 0.30212 | -0.28839 | 0.19226 | 0.064087 | 0.11902 | 0.018311 | 0.32959 | 0.37079 | -0.28381 | 122.1405 | 0.10529 | 122.4976 | 122.6212 | -0.13275 | 122.1451 | 0.17395 | 0.35706 | 122.4472 | 122.7585 | 122.493 | 122.731 | 122.4976 | 122.7997 | 122.5479 | 122.1451 | 122.731 | 122.4976 | 122.5479 | 122.493 | 122.7997 | -0.48523 | -0.48065
2199.0625 | 122.644 | -122.4884 | 0.24719 | -0.0031279 | 0.016878 | 0.0073807 | 0.0076585 | -0.0082459 | -0.0077118 | 0.015374 | 0.13275 | 0.27466 | -0.27466 | 0.2655 | 0.13275 | 0.22888 | -0.16937 | 0.37994 | 0.32044 | -0.22888 | 122.2137 | 0.027466 | 122.6212 | 122.7539 | -0.11444 | 122.2595 | 0.073243 | 0.40741 | 122.319 | 122.8683 | 122.6212 | 122.7631 | 122.6212 | 122.8088 | 122.7173 | 122.2595 | 122.7631 | 122.6212 | 122.7173 | 122.6212 | 122.8088 | -0.52185 | -0.47607
2200.75 | 122.7768 | -122.438 | 0.20142 | 0.0045011 | 0.018374 | 0.0080215 | 0.0038131 | -0.0088867 | -0.0077118 | 0.014093 | 0.064087 | 0.28381 | -0.27008 | 0.20599 | 0.09613 | 0.16479 | -0.09613 | 0.34332 | 0.3479 | -0.24719 | 122.168 | 0.082397 | 122.5021 | 122.644 | -0.10529 | 122.1909 | 0.14648 | 0.33417 | 122.3419 | 122.7814 | 122.5342 | 122.7219 | 122.5021 | 122.7859 | 122.6028 | 122.1909 | 122.7219 | 122.5021 | 122.6028 | 122.5342 | 122.7859 | -0.4715 | -0.44861
2202.5 | 122.6303 | -122.4701 | 0.23346 | 0.012131 | 0.019015 | 0.0054581 | 0.0087265 | -0.0088867 | -0.0068574 | 0.014734 | 0.12817 | 0.27466 | -0.27008 | 0.26093 | 0.13275 | 0.21515 | -0.18768 | 0.37994 | 0.32044 | -0.2243 | 122.2 | 0.041199 | 122.5983 | 122.731 | -0.10071 | 122.2458 | 0.086976 | 0.39826 | 122.2824 | 122.85 | 122.6028 | 122.7448 | 122.5983 | 122.7905 | 122.6852 | 122.2458 | 122.7448 | 122.5983 | 122.6852 | 122.6028 | 122.7905 | -0.50354 | -0.45776
2204.25 | 122.8043 | -122.4335 | 0.19684 | -0.010757 | 0.019869 | 0.0050309 | 0.0074447 | -0.0095277 | -0.0060028 | 0.015161 | -0.004578 | 0.32959 | -0.34332 | 0.16479 | 0.032043 | 0.07782 | 0.07782 | 0.29755 | 0.37537 | -0.29297 | 122.0901 | 0.13275 | 122.4289 | 122.5983 | -0.1648 | 122.1405 | 0.17853 | 0.33874 | 122.5113 | 122.731 | 122.4655 | 122.7631 | 122.4289 | 122.8088 | 122.5113 | 122.1405 | 122.7631 | 122.4289 | 122.5113 | 122.4655 | 122.8088 | -0.54016 | -0.48981
2205.9531 | 122.7127 | -122.4518 | 0.20142 | 0.0045011 | 0.023074 | 0.0063125 | 0.010008 | -0.0067505 | -0.0079254 | 0.014093 | 0.032043 | 0.31586 | -0.31128 | 0.16022 | 0.009155 | 0.086975 | 0.004578 | 0.25177 | 0.37079 | -0.28839 | 122.1405 | 0.11444 | 122.4838 | 122.612 | -0.19226 | 122.1634 | 0.16937 | 0.34332 | 122.4564 | 122.7036 | 122.4609 | 122.7676 | 122.4838 | 122.8226 | 122.5388 | 122.1634 | 122.7676 | 122.4838 | 122.5388 | 122.4609 | 122.8226 | -0.5127 | -0.48981
2207.7031 | 122.6303 | -122.5021 | 0.22888 | 0.012131 | 0.017306 | 0.0050309 | 0.0068039 | -0.0058961 | -0.0074982 | 0.01452 | 0.12817 | 0.27924 | -0.25177 | 0.26093 | 0.13733 | 0.21057 | -0.1831 | 0.3891 | 0.32501 | -0.21973 | 122.2504 | 0.050354 | 122.6303 | 122.7631 | -0.091553 | 122.2824 | 0.09613 | 0.37994 | 122.319 | 122.8912 | 122.6395 | 122.7814 | 122.6303 | 122.8271 | 122.7127 | 122.2824 | 122.7814 | 122.6303 | 122.7127 | 122.6395 | 122.8271 | -0.48065 | -0.44861
2209.3906 | 122.6624 | -122.5021 | 0.23346 | 0.012131 | 0.021365 | 0.0024673 | 0.0089401 | -0.0082459 | -0.0089936 | 0.016229 | 0.064087 | 0.31586 | -0.31586 | 0.19684 | 0.068665 | 0.14191 | -0.018311 | 0.33417 | 0.35248 | -0.24719 | 122.1863 | 0.082398 | 122.5662 | 122.699 | -0.16479 | 122.2549 | 0.11902 | 0.37994 | 122.4838 | 122.8363 | 122.5708 | 122.818 | 122.5662 | 122.8546 | 122.644 | 122.2549 | 122.818 | 122.5662 | 122.644 | 122.5708 | 122.8546 | -0.54932 | -0.48065
2211.1406 | 122.6669 | -122.5159 | 0.21973 | -0.0031279 | 0.016665 | 0.0033219 | 0.0091537 | -0.0056823 | -0.00878 | 0.016229 | 0.059509 | 0.32501 | -0.3067 | 0.19226 | 0.073242 | 0.13733 | -0.027466 | 0.33417 | 0.3479 | -0.27008 | 122.2092 | 0.10529 | 122.5754 | 122.7081 | -0.14649 | 122.2458 | 0.12817 | 0.36621 | 122.4884 | 122.85 | 122.5891 | 122.8409 | 122.5754 | 122.8638 | 122.6532 | 122.2458 | 122.8409 | 122.5754 | 122.6532 | 122.5891 | 122.8638 | -0.52643 | -0.48981
2212.8125 | 122.8134 | -122.4609 | 0.20142 | 0.01976 | 0.018801 | 0.0024673 | 0.0010361 | -0.0069641 | -0.0057892 | 0.011956 | 0.050354 | 0.28381 | -0.27008 | 0.18768 | 0.09613 | 0.17395 | -0.082397 | 0.34332 | 0.32501 | -0.27466 | 122.1909 | 0.082397 | 122.5113 | 122.6486 | -0.10529 | 122.1863 | 0.1236 | 0.32044 | 122.3785 | 122.8043 | 122.5571 | 122.7447 | 122.5113 | 122.7859 | 122.6349 | 122.1863 | 122.7447 | 122.5113 | 122.6349 | 122.5571 | 122.7859 | -0.4715 | -0.47607
2214.5625 | 122.7448 | -122.4792 | 0.21515 | 0.0045011 | 0.017519 | 0.00075827 | 0.0035995 | -0.0086731 | -0.0083526 | 0.014093 | 0.1236 | 0.27924 | -0.2655 | 0.2655 | 0.15564 | 0.2243 | -0.10986 | 0.44403 | 0.33875 | -0.23346 | 122.2137 | 0.064087 | 122.6028 | 122.7448 | -0.059509 | 122.2458 | 0.1236 | 0.3891 | 122.3694 | 122.9233 | 122.6349 | 122.7585 | 122.6028 | 122.818 | 122.7036 | 122.2458 | 122.7585 | 122.6028 | 122.7036 | 122.6349 | 122.818 | -0.48065 | -0.44861
2216.3281 | 122.8226 | -122.4564 | 0.20142 | 0.0045011 | 0.01816 | 0.0018265 | 0.0050949 | -0.0082459 | -0.0077118 | 0.015374 | 0.013733 | 0.3067 | -0.32044 | 0.15106 | 0.050354 | 0.091553 | 0.073242 | 0.31128 | 0.39368 | -0.27924 | 122.1359 | 0.10529 | 122.4701 | 122.6074 | -0.15106 | 122.1771 | 0.19226 | 0.33417 | 122.5296 | 122.7676 | 122.5067 | 122.7631 | 122.4701 | 122.85 | 122.5479 | 122.1771 | 122.7631 | 122.4701 | 122.5479 | 122.5067 | 122.85 | -0.52185 | -0.48065
2218.0781 | 122.7905 | -122.4472 | 0.18768 | 0.0045011 | 0.016878 | 0.0013993 | 0.0029587 | -0.0086731 | -0.00643 | 0.013879 | 0.068665 | 0.27924 | -0.28839 | 0.19684 | 0.086975 | 0.16937 | -0.09613 | 0.34332 | 0.35248 | -0.24719 | 122.1588 | 0.091553 | 122.5159 | 122.644 | -0.10071 | 122.2 | 0.1648 | 0.35706 | 122.3511 | 122.7905 | 122.5342 | 122.7264 | 122.5159 | 122.7997 | 122.6166 | 122.2 | 122.7264 | 122.5159 | 122.6166 | 122.5342 | 122.7997 | -0.47607 | -0.43488
2219.7656 | 122.7356 | -122.4838 | 0.22888 | 0.012131 | 0.019228 | 0.0050309 | 0.010222 | -0.0073913 | -0.0092072 | 0.013879 | 0.022888 | 0.3067 | -0.31586 | 0.12817 | 0.009155 | 0.07782 | 0.004578 | 0.24261 | 0.37537 | -0.25177 | 122.168 | 0.07782 | 122.5067 | 122.612 | -0.21973 | 122.2321 | 0.14648 | 0.33875 | 122.4884 | 122.7264 | 122.493 | 122.7905 | 122.5067 | 122.8592 | 122.5616 | 122.2321 | 122.7905 | 122.5067 | 122.5616 | 122.493 | 122.8592 | -0.54474 | -0.48065
2221.5469 | 122.7036 | -122.4747 | 0.21973 | 0.012131 | 0.018374 | 0.0065263 | 0.0097947 | -0.0088867 | -0.0096344 | 0.013665 | 0.041199 | 0.29755 | -0.31128 | 0.21057 | 0.059509 | 0.13733 | -0.018311 | 0.33417 | 0.36163 | -0.24261 | 122.1634 | 0.077819 | 122.5159 | 122.6852 | -0.16022 | 122.2321 | 0.14191 | 0.35248 | 122.4564 | 122.8088 | 122.5342 | 122.7722 | 122.5159 | 122.8363 | 122.612 | 122.2321 | 122.7722 | 122.5159 | 122.612 | 122.5342 | 122.8363 | -0.53101 | -0.46234
2223.2969 | 122.8317 | -122.4564 | 0.21057 | -0.0031279 | 0.019656 | 0.00054467 | 0.0050949 | -0.0084595 | -0.0060028 | 0.012597 | 0.032043 | 0.32501 | -0.3067 | 0.16022 | 0.036621 | 0.09613 | 0.082397 | 0.28381 | 0.3891 | -0.27008 | 122.1497 | 0.11444 | 122.4884 | 122.6166 | -0.17395 | 122.1863 | 0.17853 | 0.33874 | 122.5388 | 122.7402 | 122.493 | 122.7814 | 122.4884 | 122.8455 | 122.5525 | 122.1863 | 122.7814 | 122.4884 | 122.5525 | 122.493 | 122.8455 | -0.51727 | -0.48065
2225.0469 | 122.7768 | -122.4655 | 0.21057 | 0.012131 | 0.019015 | 0.0056717 | 0.0018905 | -0.0082459 | -0.0055756 | 0.014093 | 0.11444 | 0.27924 | -0.27008 | 0.25177 | 0.15106 | 0.2243 | -0.1236 | 0.43945 | 0.32959 | -0.23804 | 122.1954 | 0.068665 | 122.58 | 122.7173 | -0.059509 | 122.2275 | 0.11902 | 0.38452 | 122.3419 | 122.905 | 122.6166 | 122.7448 | 122.58 | 122.7951 | 122.6898 | 122.2275 | 122.7448 | 122.58 | 122.6898 | 122.6166 | 122.7951 | -0.48065 | -0.44861
2226.7344 | 122.7539 | -122.4747 | 0.2243 | 0.0045011 | 0.019015 | 0.0052445 | 0.010008 | -0.0046143 | -0.0083526 | 0.014734 | 0.022888 | 0.31586 | -0.32044 | 0.14648 | 0.022888 | 0.07782 | 0.009155 | 0.24261 | 0.38452 | -0.27924 | 122.1542 | 0.091553 | 122.4976 | 122.6212 | -0.20142 | 122.1954 | 0.16022 | 0.34332 | 122.4838 | 122.7173 | 122.4976 | 122.7905 | 122.4976 | 122.8592 | 122.5525 | 122.1954 | 122.7905 | 122.4976 | 122.5525 | 122.4976 | 122.8592 | -0.54474 | -0.50354
2228.4844 | 122.8226 | -122.493 | 0.19684 | -0.0031279 | 0.016878 | 0.0024673 | 0.0050949 | -0.0063233 | -0.0074982 | 0.014947 | 0.054932 | 0.3067 | -0.30212 | 0.16479 | 0.054932 | 0.10529 | 0.036621 | 0.31128 | 0.36163 | -0.27008 | 122.1909 | 0.10986 | 122.5479 | 122.6578 | -0.14191 | 122.2229 | 0.16479 | 0.35706 | 122.5296 | 122.8043 | 122.5479 | 122.7997 | 122.5479 | 122.8546 | 122.5983 | 122.2229 | 122.7997 | 122.5479 | 122.5983 | 122.5479 | 122.8546 | -0.49896 | -0.46692
2230.2344 | 122.699 | -122.5067 | 0.23346 | -0.0031279 | 0.019228 | 0.0037491 | 0.0093673 | -0.0058961 | -0.008139 | 0.016229 | 0.068665 | 0.3067 | -0.31586 | 0.19226 | 0.054932 | 0.11444 | -0.004578 | 0.29755 | 0.35706 | -0.27008 | 122.1909 | 0.073243 | 122.5754 | 122.699 | -0.17853 | 122.2366 | 0.1236 | 0.38452 | 122.5021 | 122.8043 | 122.5616 | 122.8134 | 122.5754 | 122.8638 | 122.6212 | 122.2366 | 122.8134 | 122.5754 | 122.6212 | 122.5616 | 122.8638 | -0.54932 | -0.50354
2232 | 122.6944 | -122.5342 | 0.24261 | -0.0031279 | 0.020937 | 0.0088761 | 0.0091537 | -0.0078187 | -0.0072846 | 0.015802 | 0.068665 | 0.29755 | -0.32501 | 0.19684 | 0.068665 | 0.14191 | -0.009155 | 0.3479 | 0.37079 | -0.2655 | 122.2092 | 0.054931 | 122.6028 | 122.731 | -0.17395 | 122.2687 | 0.12817 | 0.39368 | 122.525 | 122.8821 | 122.6028 | 122.8317 | 122.6028 | 122.905 | 122.6761 | 122.2687 | 122.8317 | 122.6028 | 122.6761 | 122.6028 | 122.905 | -0.56763 | -0.50812
2233.6875 | 122.8226 | -122.4609 | 0.19684 | 0.01976 | 0.02051 | -0.00030973 | 0.0078721 | -0.0080323 | -0.0062164 | 0.016656 | 0.013733 | 0.33417 | -0.32501 | 0.14191 | 0.041199 | 0.073242 | 0.064087 | 0.28381 | 0.36163 | -0.28381 | 122.1359 | 0.13733 | 122.4747 | 122.6028 | -0.15564 | 122.1771 | 0.16479 | 0.33875 | 122.525 | 122.7447 | 122.5021 | 122.7951 | 122.4747 | 122.8226 | 122.5342 | 122.1771 | 122.7951 | 122.4747 | 122.5342 | 122.5021 | 122.8226 | -0.52185 | -0.48065
2235.4375 | 122.731 | -122.5021 | 0.2243 | 0.0045011 | 0.018374 | 0.0048173 | 0.0033859 | -0.0084595 | -0.0066438 | 0.01452 | 0.11444 | 0.27008 | -0.24719 | 0.21515 | 0.12817 | 0.20599 | -0.13733 | 0.37994 | 0.32959 | -0.23346 | 122.2549 | 0.045777 | 122.6166 | 122.7173 | -0.09613 | 122.2687 | 0.10529 | 0.36163 | 122.3648 | 122.8821 | 122.6303 | 122.7722 | 122.6166 | 122.8317 | 122.7081 | 122.2687 | 122.7722 | 122.6166 | 122.7081 | 122.6303 | 122.8317 | -0.4715 | -0.45776
2237.1875 | 122.7676 | -122.5067 | 0.22888 | 0.012131 | 0.017733 | 0.0033219 | 0.0097947 | -0.0071777 | -0.0079254 | 0.015802 | -0.004578 | 0.30212 | -0.30212 | 0.12817 | 0.004578 | 0.091553 | 0.004578 | 0.27008 | 0.37537 | -0.26093 | 122.2046 | 0.073242 | 122.5021 | 122.6349 | -0.2243 | 122.2458 | 0.14648 | 0.29755 | 122.5113 | 122.7768 | 122.5113 | 122.8088 | 122.5021 | 122.8821 | 122.5983 | 122.2458 | 122.8088 | 122.5021 | 122.5983 | 122.5113 | 122.8821 | -0.53101 | -0.48981
2238.9531 | 122.7676 | -122.4976 | 0.2243 | 0.0045011 | 0.014956 | 0.0022537 | 0.0033859 | -0.0099549 | -0.0051484 | 0.015374 | 0.073242 | 0.29297 | -0.27008 | 0.20599 | 0.09613 | 0.17853 | -0.10986 | 0.35706 | 0.3479 | -0.2243 | 122.2275 | 0.068665 | 122.5708 | 122.7036 | -0.12817 | 122.2733 | 0.1236 | 0.34332 | 122.3877 | 122.8546 | 122.5937 | 122.7905 | 122.5708 | 122.8455 | 122.6761 | 122.2733 | 122.7905 | 122.5708 | 122.6761 | 122.5937 | 122.8455 | -0.49439 | -0.44861
2240.6406 | 122.8088 | -122.493 | 0.21515 | 0.012131 | 0.017947 | 0.011226 | 0.0085129 | -0.0088867 | -0.0068574 | 0.014306 | 0.041199 | 0.32959 | -0.31586 | 0.16479 | 0.054932 | 0.10529 | 0.045776 | 0.32044 | 0.36163 | -0.25177 | 122.1771 | 0.11444 | 122.5342 | 122.6578 | -0.16022 | 122.2412 | 0.14648 | 0.35706 | 122.5388 | 122.8134 | 122.5479 | 122.8226 | 122.5342 | 122.8546 | 122.5983 | 122.2412 | 122.8226 | 122.5342 | 122.5983 | 122.5479 | 122.8546 | -0.53101 | -0.46692
2242.3906 | 122.7539 | -122.5388 | 0.21057 | -0.010757 | 0.02051 | 0.0011857 | 0.0070175 | -0.0063233 | -0.00878 | 0.016656 | 0.059509 | 0.31586 | -0.30212 | 0.18768 | 0.059509 | 0.13275 | -0.009155 | 0.33417 | 0.36621 | -0.25635 | 122.2366 | 0.10529 | 122.5983 | 122.7264 | -0.15106 | 122.2824 | 0.15564 | 0.36163 | 122.5296 | 122.8729 | 122.5983 | 122.8546 | 122.5983 | 122.905 | 122.6715 | 122.2824 | 122.8546 | 122.5983 | 122.6715 | 122.5983 | 122.905 | -0.5127 | -0.46692
2244.1406 | 122.699 | -122.5433 | 0.24719 | 0.0045011 | 0.019869 | 0.0035355 | 0.0080857 | -0.0080323 | -0.0062164 | 0.015374 | 0.073242 | 0.29297 | -0.31586 | 0.19684 | 0.073242 | 0.14648 | -0.013733 | 0.33417 | 0.36621 | -0.27466 | 122.2275 | 0.045777 | 122.6166 | 122.7402 | -0.17395 | 122.2687 | 0.11902 | 0.3891 | 122.5296 | 122.8775 | 122.6166 | 122.8363 | 122.6166 | 122.9095 | 122.6898 | 122.2687 | 122.8363 | 122.6166 | 122.6898 | 122.6166 | 122.9095 | -0.56305 | -0.52185
2245.8281 | 122.7539 | -122.4976 | 0.23804 | -0.0031279 | 0.015383 | 0.0054581 | 0.0025315 | -0.0091003 | -0.0045074 | 0.016015 | 0.07782 | 0.28839 | -0.27466 | 0.20142 | 0.10071 | 0.19684 | -0.11902 | 0.37079 | 0.32959 | -0.22888 | 122.2229 | 0.050354 | 122.5754 | 122.699 | -0.13733 | 122.2687 | 0.091553 | 0.35248 | 122.3785 | 122.8683 | 122.5983 | 122.7859 | 122.5754 | 122.8271 | 122.6944 | 122.2687 | 122.7859 | 122.5754 | 122.6944 | 122.5983 | 122.8271 | -0.5127 | -0.46692
2247.5781 | 122.7081 | -122.5433 | 0.2243 | -0.0031279 | 0.017092 | 0.0020401 | 0.0055221 | -0.0056823 | -0.00878 | 0.017938 | 0.12817 | 0.26093 | -0.2655 | 0.24261 | 0.1236 | 0.21973 | -0.18768 | 0.40741 | 0.33417 | -0.22888 | 122.2778 | 0.036621 | 122.6715 | 122.7859 | -0.10071 | 122.3145 | 0.10986 | 0.39368 | 122.3557 | 122.9507 | 122.6669 | 122.8043 | 122.6715 | 122.8775 | 122.7631 | 122.3145 | 122.8043 | 122.6715 | 122.7631 | 122.6669 | 122.8775 | -0.48981 | -0.45319
2249.3281 | 122.7905 | -122.525 | 0.21973 | 0.0045011 | 0.016451 | 0.0080215 | 0.0078721 | -0.0073913 | -0.0060028 | 0.014093 | 0.009155 | 0.32501 | -0.31586 | 0.13275 | 0.013733 | 0.086975 | 0.018311 | 0.25635 | 0.37079 | -0.27924 | 122.2092 | 0.10529 | 122.5342 | 122.6578 | -0.20599 | 122.2458 | 0.15106 | 0.32501 | 122.5433 | 122.7814 | 122.5388 | 122.85 | 122.5342 | 122.8958 | 122.612 | 122.2458 | 122.85 | 122.5342 | 122.612 | 122.5388 | 122.8958 | -0.53558 | -0.49896
2251.0781 | 122.7585 | -122.5525 | 0.24261 | 0.012131 | 0.019228 | 0.0018265 | 0.0065903 | -0.0056823 | -0.010275 | 0.015588 | 0.054932 | 0.3067 | -0.31586 | 0.15106 | 0.004578 | 0.086975 | 0.018311 | 0.25635 | 0.36621 | -0.24719 | 122.2366 | 0.064087 | 122.6074 | 122.7036 | -0.23804 | 122.3053 | 0.1236 | 0.37079 | 122.5708 | 122.8088 | 122.5571 | 122.8592 | 122.6074 | 122.9187 | 122.6395 | 122.3053 | 122.8592 | 122.6074 | 122.6395 | 122.5571 | 122.9187 | -0.55847 | -0.48981
2252.75 | 122.7814 | -122.5296 | 0.20142 | 0.012131 | 0.016878 | 0.0080215 | -0.00024572 | -0.0076049 | -0.00643 | 0.013665 | 0.10986 | 0.27466 | -0.2655 | 0.21057 | 0.09613 | 0.17853 | -0.1236 | 0.37537 | 0.3479 | -0.24719 | 122.2641 | 0.073242 | 122.6395 | 122.7402 | -0.10529 | 122.2824 | 0.14648 | 0.37537 | 122.406 | 122.905 | 122.6257 | 122.8043 | 122.6395 | 122.8775 | 122.7081 | 122.2824 | 122.8043 | 122.6395 | 122.7081 | 122.6257 | 122.8775 | -0.46692 | -0.44861
2254.5 | 122.8638 | -122.4976 | 0.19226 | 0.0045011 | 0.017947 | 0.00011747 | 0.0029587 | -0.0076049 | -0.0051484 | 0.014306 | 0.064087 | 0.28839 | -0.28381 | 0.19684 | 0.091553 | 0.17853 | -0.082397 | 0.36163 | 0.35248 | -0.24719 | 122.2137 | 0.09613 | 122.5616 | 122.6944 | -0.10071 | 122.2504 | 0.16022 | 0.3479 | 122.4152 | 122.8592 | 122.5891 | 122.7859 | 122.5616 | 122.85 | 122.6761 | 122.2504 | 122.7859 | 122.5616 | 122.6761 | 122.5891 | 122.85 | -0.47607 | -0.43945
2256.25 | 122.7585 | -122.5479 | 0.20599 | -0.010757 | 0.016878 | 0.0065263 | 0.0042405 | -0.0082459 | -0.00643 | 0.014947 | 0.10986 | 0.27466 | -0.2655 | 0.23346 | 0.15564 | 0.19226 | -0.15106 | 0.37994 | 0.33875 | -0.22888 | 122.2824 | 0.068664 | 122.6578 | 122.7814 | -0.050354 | 122.319 | 0.13275 | 0.37537 | 122.3969 | 122.9279 | 122.7036 | 122.8226 | 122.6578 | 122.8867 | 122.7402 | 122.319 | 122.8226 | 122.6578 | 122.7402 | 122.7036 | 122.8867 | -0.4715 | -0.43488
2258 | 122.7768 | -122.5433 | 0.24261 | -0.0031279 | 0.022005 | 0.0043899 | 0.010649 | -0.0067505 | -0.008139 | 0.013879 | 0.041199 | 0.32044 | -0.31128 | 0.15106 | 0.018311 | 0.07782 | 0 | 0.27008 | 0.36621 | -0.2655 | 122.2321 | 0.07782 | 122.5845 | 122.6944 | -0.2243 | 122.2778 | 0.1236 | 0.35248 | 122.5433 | 122.8134 | 122.5616 | 122.8638 | 122.5845 | 122.9095 | 122.6212 | 122.2778 | 122.8638 | 122.5845 | 122.6212 | 122.5616 | 122.9095 | -0.55389 | -0.50812
2259.7031 | 122.8134 | -122.5159 | 0.23346 | 0.0045011 | 0.019228 | 0.00075827 | 0.0061631 | -0.010809 | -0.0074982 | 0.016015 | 0.054932 | 0.32501 | -0.31128 | 0.20142 | 0.059509 | 0.10986 | 0.009155 | 0.31586 | 0.37994 | -0.26093 | 122.2046 | 0.091553 | 122.5708 | 122.7173 | -0.17395 | 122.2549 | 0.14649 | 0.36621 | 122.525 | 122.8317 | 122.5754 | 122.8409 | 122.5708 | 122.8958 | 122.6257 | 122.2549 | 122.8409 | 122.5708 | 122.6257 | 122.5754 | 122.8958 | -0.54474 | -0.49438
2261.4688 | 122.8592 | -122.5021 | 0.19226 | -0.0031279 | 0.019656 | 0.0037491 | -0.00045932 | -0.01145 | -0.0038666 | 0.016015 | 0.064087 | 0.30212 | -0.27466 | 0.20142 | 0.082397 | 0.16937 | -0.073242 | 0.33875 | 0.33417 | -0.23346 | 122.2275 | 0.10986 | 122.5662 | 122.7036 | -0.10986 | 122.2687 | 0.14191 | 0.33875 | 122.4289 | 122.8409 | 122.5845 | 122.8043 | 122.5662 | 122.8363 | 122.6715 | 122.2687 | 122.8043 | 122.5662 | 122.6715 | 122.5845 | 122.8363 | -0.46692 | -0.42572
2263.2031 | 122.8867 | -122.5113 | 0.19684 | 0.0045011 | 0.022646 | 0.0022537 | 0.0040269 | -0.0093139 | -0.0049348 | 0.013025 | 0.013733 | 0.31586 | -0.3067 | 0.15564 | 0.027466 | 0.091553 | 0.07782 | 0.30212 | 0.38452 | -0.27924 | 122.2046 | 0.11902 | 122.525 | 122.6669 | -0.16937 | 122.2321 | 0.18768 | 0.32043 | 122.5891 | 122.8134 | 122.5388 | 122.8271 | 122.525 | 122.8958 | 122.6028 | 122.2321 | 122.8271 | 122.525 | 122.6028 | 122.5388 | 122.8958 | -0.50354 | -0.47607
2264.9688 | 122.8821 | -122.5296 | 0.20142 | 0.0045011 | 0.022646 | 0.0033219 | 0.0023179 | -0.0093139 | -0.0060028 | 0.013452 | 0.086975 | 0.3067 | -0.30212 | 0.1831 | 0.054932 | 0.11444 | 0.045776 | 0.32501 | 0.37079 | -0.27924 | 122.2275 | 0.10529 | 122.6166 | 122.7127 | -0.14648 | 122.2504 | 0.16937 | 0.3891 | 122.5754 | 122.8546 | 122.5845 | 122.8363 | 122.6166 | 122.9004 | 122.644 | 122.2504 | 122.8363 | 122.6166 | 122.644 | 122.5845 | 122.9004 | -0.50354 | -0.48065
2266.6562 | 122.8592 | -122.5388 | 0.21515 | -0.0031279 | 0.02286 | 0.0093033 | 0.0012497 | -0.0086731 | -0.0066438 | 0.012384 | 0.12817 | 0.27924 | -0.27924 | 0.2655 | 0.13733 | 0.20599 | -0.073242 | 0.41199 | 0.32959 | -0.25177 | 122.2595 | 0.064087 | 122.6669 | 122.8043 | -0.07782 | 122.287 | 0.11444 | 0.40741 | 122.4655 | 122.9507 | 122.6761 | 122.818 | 122.6669 | 122.8683 | 122.7448 | 122.287 | 122.818 | 122.6669 | 122.7448 | 122.6761 | 122.8683 | -0.49438 | -0.46692
2268.4062 | 122.7905 | -122.58 | 0.2243 | 0.012131 | 0.022433 | 0.0054581 | 0.0063767 | -0.0065369 | -0.010062 | 0.012597 | 0.022888 | 0.3067 | -0.32959 | 0.14191 | 0.009155 | 0.068665 | 0.013733 | 0.24261 | 0.38452 | -0.26093 | 122.2504 | 0.082398 | 122.6028 | 122.7219 | -0.21515 | 122.319 | 0.16022 | 0.35248 | 122.5937 | 122.8226 | 122.5891 | 122.8867 | 122.6028 | 122.9645 | 122.6486 | 122.319 | 122.8867 | 122.6028 | 122.6486 | 122.5891 | 122.9645 | -0.55389 | -0.48523
2270.1562 | 122.8317 | -122.5479 | 0.19226 | 0.0045011 | 0.020083 | -9.6132e-05 | 0.00082248 | -0.0099549 | -0.0066438 | 0.015161 | 0.11902 | 0.29297 | -0.2655 | 0.27008 | 0.16022 | 0.22888 | -0.11444 | 0.43945 | 0.3479 | -0.21973 | 122.2824 | 0.10071 | 122.6669 | 122.818 | -0.032044 | 122.3282 | 0.15564 | 0.38452 | 122.4335 | 122.9874 | 122.7081 | 122.8409 | 122.6669 | 122.8958 | 122.7768 | 122.3282 | 122.8409 | 122.6669 | 122.7768 | 122.7081 | 122.8958 | -0.45776 | -0.41199
2271.8438 | 122.905 | -122.5342 | 0.18768 | 0.012131 | 0.022646 | 0.0033219 | 0.0044541 | -0.0061097 | -0.009848 | 0.012811 | 0.018311 | 0.32959 | -0.30212 | 0.15106 | 0.022888 | 0.082397 | 0.068665 | 0.28839 | 0.39368 | -0.27008 | 122.2321 | 0.14191 | 122.5525 | 122.6852 | -0.16479 | 122.2641 | 0.20599 | 0.32044 | 122.6028 | 122.8226 | 122.5571 | 122.8638 | 122.5525 | 122.9279 | 122.6166 | 122.2641 | 122.8638 | 122.5525 | 122.6166 | 122.5571 | 122.9279 | -0.48981 | -0.45776
2273.5781 | 122.731 | -122.5616 | 0.24261 | 0.0045011 | 0.019869 | 0.0050309 | 0.0046677 | -0.0073913 | -0.0079254 | 0.015374 | 0.1236 | 0.27008 | -0.28381 | 0.24719 | 0.1236 | 0.2243 | -0.17395 | 0.38452 | 0.34332 | -0.23346 | 122.2778 | 0.027466 | 122.6852 | 122.8088 | -0.11902 | 122.3282 | 0.10071 | 0.40741 | 122.3877 | 122.9462 | 122.6852 | 122.8317 | 122.6852 | 122.905 | 122.7859 | 122.3282 | 122.8317 | 122.6852 | 122.7859 | 122.6852 | 122.905 | -0.52643 | -0.47607
2275.3281 | 122.8409 | -122.5571 | 0.21057 | 0.0045011 | 0.019869 | 0.0041763 | -0.00024572 | -0.0069641 | -0.0051484 | 0.016015 | 0.13733 | 0.27008 | -0.2655 | 0.26093 | 0.15106 | 0.23346 | -0.1236 | 0.43945 | 0.35248 | -0.23804 | 122.2916 | 0.05951 | 122.6944 | 122.818 | -0.059509 | 122.319 | 0.14191 | 0.40283 | 122.4335 | 122.9965 | 122.7081 | 122.8271 | 122.6944 | 122.9095 | 122.7905 | 122.319 | 122.8271 | 122.6944 | 122.7905 | 122.7081 | 122.9095 | -0.47607 | -0.44861
2277.0938 | 122.905 | -122.525 | 0.20599 | 0.0045011 | 0.022433 | -0.0028731 | 0.0042405 | -0.010168 | -0.0089936 | 0.015161 | 0.013733 | 0.32959 | -0.31128 | 0.15106 | 0.041199 | 0.07782 | 0.068665 | 0.3067 | 0.3891 | -0.27008 | 122.2137 | 0.1236 | 122.5388 | 122.6761 | -0.1648 | 122.2549 | 0.1831 | 0.32501 | 122.5937 | 122.8317 | 122.5662 | 122.8546 | 122.5388 | 122.9141 | 122.6028 | 122.2549 | 122.8546 | 122.5388 | 122.6028 | 122.5662 | 122.9141 | -0.51727 | -0.47608
2278.8438 | 122.8683 | -122.5296 | 0.1831 | 0.0045011 | 0.020083 | 0.0039627 | 0.00039528 | -0.0082459 | -0.004721 | 0.015161 | 0.082397 | 0.29755 | -0.27924 | 0.20142 | 0.10529 | 0.16937 | -0.09613 | 0.35706 | 0.34332 | -0.23804 | 122.2504 | 0.11444 | 122.612 | 122.731 | -0.077819 | 122.2916 | 0.16022 | 0.36163 | 122.4335 | 122.8867 | 122.6349 | 122.8271 | 122.612 | 122.8729 | 122.699 | 122.2916 | 122.8271 | 122.612 | 122.699 | 122.6349 | 122.8729 | -0.46234 | -0.42114
2280.5312 | 122.8134 | -122.5616 | 0.21515 | 0.0045011 | 0.020937 | 0.0031083 | 0.0070175 | -0.0069641 | -0.0094208 | 0.015161 | 0.022888 | 0.31586 | -0.30212 | 0.15564 | 0.022888 | 0.091553 | 0.004578 | 0.24719 | 0.38452 | -0.27008 | 122.2595 | 0.10071 | 122.5845 | 122.7173 | -0.19226 | 122.2916 | 0.16937 | 0.32501 | 122.5662 | 122.8088 | 122.5845 | 122.8775 | 122.5845 | 122.9462 | 122.6532 | 122.2916 | 122.8775 | 122.5845 | 122.6532 | 122.5845 | 122.9462 | -0.51727 | -0.48523
2282.2812 | 122.8958 | -122.5616 | 0.23346 | 0.0045011 | 0.019442 | 0.0013993 | 0.0035995 | -0.0093139 | -0.0057892 | 0.015802 | 0.032043 | 0.3067 | -0.30212 | 0.15564 | 0.036621 | 0.091553 | 0.059509 | 0.30212 | 0.35706 | -0.27008 | 122.2595 | 0.073243 | 122.5937 | 122.7173 | -0.19684 | 122.2916 | 0.1236 | 0.33417 | 122.6212 | 122.8638 | 122.5983 | 122.8683 | 122.5937 | 122.9187 | 122.6532 | 122.2916 | 122.8683 | 122.5937 | 122.6532 | 122.5983 | 122.9187 | -0.53558 | -0.50354
2284.0469 | 122.8546 | -122.5525 | 0.20599 | -0.0031279 | 0.019442 | 0.0031083 | -0.0017411 | -0.0063233 | -0.004721 | 0.014734 | 0.064087 | 0.27466 | -0.25635 | 0.21515 | 0.09613 | 0.18768 | -0.10986 | 0.36621 | 0.35706 | -0.24261 | 122.2961 | 0.068664 | 122.6166 | 122.7676 | -0.10986 | 122.3099 | 0.15106 | 0.32044 | 122.4426 | 122.9187 | 122.6486 | 122.8271 | 122.6166 | 122.9095 | 122.7402 | 122.3099 | 122.8271 | 122.6166 | 122.7402 | 122.6486 | 122.9095 | -0.46234 | -0.44861
2285.7344 | 122.7814 | -122.5571 | 0.22888 | 0.0045011 | 0.018587 | 0.0052445 | 0.0072311 | -0.0076049 | -0.009848 | 0.01452 | 0.041199 | 0.29755 | -0.31586 | 0.16937 | 0.036621 | 0.10529 | -0.073242 | 0.27466 | 0.36621 | -0.27008 | 122.2412 | 0.068664 | 122.5983 | 122.7264 | -0.19226 | 122.287 | 0.13733 | 0.35706 | 122.4838 | 122.8317 | 122.5937 | 122.8546 | 122.5983 | 122.9233 | 122.6624 | 122.287 | 122.8546 | 122.5983 | 122.6624 | 122.5937 | 122.9233 | -0.54474 | -0.49896
2287.4844 | 122.8912 | -122.5113 | 0.18768 | 0.0045011 | 0.020296 | 0.0031083 | 0.0016769 | -0.0086731 | -0.0057892 | 0.015374 | 0.07782 | 0.27924 | -0.26093 | 0.21973 | 0.10529 | 0.18768 | -0.09613 | 0.37079 | 0.32959 | -0.25177 | 122.2504 | 0.091553 | 122.5891 | 122.731 | -0.082397 | 122.2595 | 0.14191 | 0.33875 | 122.4152 | 122.8821 | 122.6166 | 122.7905 | 122.5891 | 122.8409 | 122.699 | 122.2595 | 122.7905 | 122.5891 | 122.699 | 122.6166 | 122.8409 | -0.44861 | -0.43945
2289.2344 | 122.7722 | -122.5983 | 0.24719 | 0.0045011 | 0.017733 | 0.0067399 | 0.0089401 | -0.0046143 | -0.0089936 | 0.013238 | 0.11902 | 0.27466 | -0.27008 | 0.27008 | 0.1236 | 0.21973 | -0.16937 | 0.37537 | 0.35248 | -0.2243 | 122.3282 | 0.027466 | 122.7173 | 122.8683 | -0.1236 | 122.374 | 0.10529 | 0.3891 | 122.4289 | 122.9736 | 122.7219 | 122.8729 | 122.7173 | 122.9507 | 122.818 | 122.374 | 122.8729 | 122.7173 | 122.818 | 122.7219 | 122.9507 | -0.51727 | -0.4715
2290.9844 | 122.7722 | -122.5937 | 0.21515 | 0.012131 | 0.016878 | 0.0056717 | 0.0055221 | -0.0088867 | -0.0066438 | 0.017297 | 0.1236 | 0.25177 | -0.2655 | 0.24719 | 0.13275 | 0.21515 | -0.17395 | 0.39825 | 0.32959 | -0.2243 | 122.3282 | 0.036621 | 122.7173 | 122.8409 | -0.082398 | 122.3694 | 0.11444 | 0.3891 | 122.4197 | 122.9919 | 122.7264 | 122.8455 | 122.7173 | 122.9233 | 122.8088 | 122.3694 | 122.8455 | 122.7173 | 122.8088 | 122.7264 | 122.9233 | -0.48065 | -0.43945
2292.6719 | 122.8134 | -122.5616 | 0.20599 | 0.0045011 | 0.020937 | 0.0065263 | 0.0080857 | -0.0097413 | -0.0074982 | 0.013879 | 0.045776 | 0.3067 | -0.32044 | 0.17395 | 0.050354 | 0.10986 | -0.073242 | 0.29755 | 0.35248 | -0.2655 | 122.2412 | 0.10071 | 122.6074 | 122.7356 | -0.15564 | 122.2961 | 0.14648 | 0.36621 | 122.4884 | 122.8592 | 122.612 | 122.8683 | 122.6074 | 122.9141 | 122.6715 | 122.2961 | 122.8683 | 122.6074 | 122.6715 | 122.612 | 122.9141 | -0.52643 | -0.4715
2294.4375 | 122.8088 | -122.6212 | 0.24261 | 0.0045011 | 0.020937 | 0.0037491 | 0.0074447 | -0.0080323 | -0.0083526 | 0.015374 | 0.050354 | 0.30212 | -0.31128 | 0.15106 | 0.018311 | 0.10071 | -0.004578 | 0.27008 | 0.36621 | -0.25635 | 122.3099 | 0.059509 | 122.6715 | 122.7722 | -0.2243 | 122.3648 | 0.1236 | 0.36163 | 122.6166 | 122.8912 | 122.6395 | 122.9233 | 122.6715 | 122.9874 | 122.7219 | 122.3648 | 122.9233 | 122.6715 | 122.7219 | 122.6395 | 122.9874 | -0.55389 | -0.49896
2296.125 | 122.8043 | -122.6028 | 0.23804 | 0.0045011 | 0.020724 | 0.0041763 | 0.0074447 | -0.0071777 | -0.00643 | 0.017083 | 0.064087 | 0.30212 | -0.32501 | 0.16937 | 0.041199 | 0.10986 | -0.004578 | 0.29755 | 0.36621 | -0.25177 | 122.2778 | 0.064087 | 122.6669 | 122.7722 | -0.19684 | 122.3511 | 0.12817 | 0.3891 | 122.5983 | 122.9004 | 122.644 | 122.905 | 122.6669 | 122.9691 | 122.7127 | 122.3511 | 122.905 | 122.6669 | 122.7127 | 122.644 | 122.9691 | -0.56305 | -0.48981
2297.875 | 122.8455 | -122.6028 | 0.21515 | -0.0031279 | 0.021151 | 0.0046037 | 0.0057357 | -0.0073913 | -0.00643 | 0.014093 | 0.013733 | 0.31586 | -0.32044 | 0.13733 | 0 | 0.068665 | 0 | 0.25177 | 0.37537 | -0.28381 | 122.2824 | 0.10071 | 122.6166 | 122.7402 | -0.21515 | 122.319 | 0.16022 | 0.33417 | 122.6028 | 122.8546 | 122.6028 | 122.9187 | 122.6166 | 122.9782 | 122.6715 | 122.319 | 122.9187 | 122.6166 | 122.6715 | 122.6028 | 122.9782 | -0.53558 | -0.49896
2299.625 | 122.8363 | -122.6028 | 0.2243 | 0.0045011 | 0.02051 | 0.0046037 | 0.0053085 | -0.0086731 | -0.008139 | 0.014306 | 0.054932 | 0.33417 | -0.31128 | 0.17853 | 0.073242 | 0.12817 | 0.004578 | 0.33417 | 0.37994 | -0.25177 | 122.2916 | 0.10986 | 122.6578 | 122.7814 | -0.15106 | 122.3511 | 0.15564 | 0.36621 | 122.6074 | 122.937 | 122.6761 | 122.937 | 122.6578 | 122.9828 | 122.731 | 122.3511 | 122.937 | 122.6578 | 122.731 | 122.6761 | 122.9828 | -0.53558 | -0.47607
2301.375 | 122.8775 | -122.5479 | 0.19226 | -0.0031279 | 0.018801 | 0.0031083 | 0.0018905 | -0.0088867 | -0.004721 | 0.01687 | 0.10071 | 0.29297 | -0.27466 | 0.25177 | 0.16022 | 0.22888 | -0.11902 | 0.44861 | 0.31586 | -0.2243 | 122.2733 | 0.10071 | 122.6486 | 122.7997 | -0.032044 | 122.3236 | 0.1236 | 0.37537 | 122.4289 | 122.9965 | 122.7081 | 122.8409 | 122.6486 | 122.8638 | 122.7768 | 122.3236 | 122.8409 | 122.6486 | 122.7768 | 122.7081 | 122.8638 | -0.46692 | -0.41656
2303.1406 | 122.8775 | -122.5525 | 0.21515 | -0.0031279 | 0.018801 | 0.0026809 | 0.0010361 | -0.011664 | -0.0055756 | 0.015588 | 0.11902 | 0.27924 | -0.27008 | 0.27466 | 0.16479 | 0.23346 | -0.1236 | 0.44403 | 0.34332 | -0.24261 | 122.2824 | 0.064087 | 122.6715 | 122.8271 | -0.050354 | 122.3099 | 0.12817 | 0.3891 | 122.4289 | 122.9965 | 122.7173 | 122.8317 | 122.6715 | 122.8958 | 122.7859 | 122.3099 | 122.8317 | 122.6715 | 122.7859 | 122.7173 | 122.8958 | -0.48523 | -0.45776
2304.8438 | 122.818 | -122.58 | 0.2243 | -0.0031279 | 0.019015 | 0.0054581 | 0.0055221 | -0.0091003 | -0.0068574 | 0.014093 | 0.11444 | 0.2655 | -0.27008 | 0.23804 | 0.10986 | 0.21515 | -0.15564 | 0.3891 | 0.32501 | -0.24719 | 122.3099 | 0.041199 | 122.6944 | 122.818 | -0.11444 | 122.3328 | 0.10071 | 0.38452 | 122.4243 | 122.9691 | 122.6898 | 122.8455 | 122.6944 | 122.905 | 122.7951 | 122.3328 | 122.8455 | 122.6944 | 122.7951 | 122.6898 | 122.905 | -0.49439 | -0.4715
2306.5938 | 122.7814 | -122.6074 | 0.23804 | 0.0045011 | 0.019442 | 0.0048173 | 0.0057357 | -0.0080323 | -0.0068574 | 0.016229 | 0.11902 | 0.27466 | -0.25635 | 0.24261 | 0.12817 | 0.22888 | -0.18768 | 0.39825 | 0.33875 | -0.21515 | 122.3511 | 0.036621 | 122.7264 | 122.85 | -0.10986 | 122.3923 | 0.10071 | 0.37537 | 122.4197 | 123.0057 | 122.7356 | 122.8821 | 122.7264 | 122.9462 | 122.8363 | 122.3923 | 122.8821 | 122.7264 | 122.8363 | 122.7356 | 122.9462 | -0.49439 | -0.45319
2308.3438 | 122.9462 | -122.5571 | 0.20142 | 0.0045011 | 0.016451 | 0.0024673 | 0.0048813 | -0.0095277 | -0.0074982 | 0.014306 | 0.013733 | 0.30212 | -0.32501 | 0.14191 | 0.022888 | 0.082397 | 0.068665 | 0.3067 | 0.37994 | -0.28839 | 122.2321 | 0.10071 | 122.5708 | 122.699 | -0.17853 | 122.2687 | 0.17853 | 0.33875 | 122.6257 | 122.8638 | 122.58 | 122.8592 | 122.5708 | 122.937 | 122.6395 | 122.2687 | 122.8592 | 122.5708 | 122.6395 | 122.58 | 122.937 | -0.52643 | -0.48981
2310.0938 | 122.8088 | -122.6212 | 0.23346 | 0.012131 | 0.017306 | 0.0028947 | 0.0046677 | -0.0046143 | -0.0066438 | 0.014093 | 0.1236 | 0.27008 | -0.27008 | 0.25177 | 0.11444 | 0.21973 | -0.14648 | 0.39825 | 0.32959 | -0.23346 | 122.3511 | 0.036622 | 122.7448 | 122.8729 | -0.11902 | 122.3877 | 0.096131 | 0.39368 | 122.4747 | 123.0194 | 122.7356 | 122.8912 | 122.7448 | 122.9507 | 122.8409 | 122.3877 | 122.8912 | 122.7448 | 122.8409 | 122.7356 | 122.9507 | -0.50354 | -0.46692
2311.8438 | 122.8546 | -122.5845 | 0.20599 | -0.0031279 | 0.020083 | 0.0037491 | 0.0033859 | -0.0091003 | -0.00643 | 0.014734 | 0.086975 | 0.27924 | -0.27008 | 0.21973 | 0.10071 | 0.1831 | -0.1236 | 0.36621 | 0.34332 | -0.23804 | 122.3145 | 0.073242 | 122.6715 | 122.8043 | -0.10529 | 122.3465 | 0.13733 | 0.35706 | 122.4609 | 122.9507 | 122.6852 | 122.8638 | 122.6715 | 122.9279 | 122.7676 | 122.3465 | 122.8638 | 122.6715 | 122.7676 | 122.6852 | 122.9279 | -0.47608 | -0.44403
2313.5312 | 122.9141 | -122.6028 | 0.20599 | -0.0031279 | 0.018374 | 0.0088761 | 0.0027451 | -0.0093139 | -0.0055756 | 0.013452 | 0.086975 | 0.28839 | -0.27008 | 0.24719 | 0.11902 | 0.19684 | -0.10529 | 0.42114 | 0.32044 | -0.24719 | 122.3328 | 0.082397 | 122.6898 | 122.85 | -0.086975 | 122.3557 | 0.11444 | 0.35706 | 122.4976 | 123.024 | 122.7219 | 122.8912 | 122.6898 | 122.9233 | 122.7997 | 122.3557 | 122.8912 | 122.6898 | 122.7997 | 122.7219 | 122.9233 | -0.47608 | -0.45319
2315.2656 | 122.9279 | -122.5845 | 0.20599 | 0.0045011 | 0.017733 | 0.0026809 | 0.0055221 | -0.0095277 | -0.0085664 | 0.011956 | 0.086975 | 0.29755 | -0.3067 | 0.19226 | 0.059509 | 0.13275 | 0.022888 | 0.32959 | 0.36621 | -0.27466 | 122.2778 | 0.091552 | 122.6715 | 122.7768 | -0.14649 | 122.3099 | 0.16022 | 0.39368 | 122.6074 | 122.9141 | 122.644 | 122.8821 | 122.6715 | 122.9507 | 122.7173 | 122.3099 | 122.8821 | 122.6715 | 122.7173 | 122.644 | 122.9507 | -0.5127 | -0.48065
2317.0312 | 122.85 | -122.6257 | 0.23804 | 0.01976 | 0.020937 | 0.0067399 | 0.0093673 | -0.0069641 | -0.0092072 | 0.016015 | 0.068665 | 0.32044 | -0.3067 | 0.21057 | 0.068665 | 0.1236 | -0.009155 | 0.34332 | 0.38452 | -0.26093 | 122.319 | 0.082398 | 122.6944 | 122.8363 | -0.16937 | 122.3648 | 0.14648 | 0.37537 | 122.6166 | 122.9691 | 122.6944 | 122.9462 | 122.6944 | 123.0103 | 122.7493 | 122.3648 | 122.9462 | 122.6944 | 122.7493 | 122.6944 | 123.0103 | -0.54474 | -0.49896
2318.7188 | 122.8134 | -122.6349 | 0.22888 | -0.0031279 | 0.019228 | 0.0022537 | 0.0078721 | -0.0061097 | -0.0096344 | 0.01452 | 0.068665 | 0.30212 | -0.30212 | 0.19226 | 0.068665 | 0.13733 | 0 | 0.35248 | 0.35706 | -0.26093 | 122.3328 | 0.073242 | 122.7036 | 122.8271 | -0.16022 | 122.374 | 0.12817 | 0.37079 | 122.6349 | 122.9874 | 122.7036 | 122.937 | 122.7036 | 122.9919 | 122.7722 | 122.374 | 122.937 | 122.7036 | 122.7722 | 122.7036 | 122.9919 | -0.53101 | -0.48981
2320.4688 | 122.8363 | -122.6028 | 0.2243 | -0.0031279 | 0.021151 | 0.0058853 | 0.0061631 | -0.0050415 | -0.0051484 | 0.017083 | 0.064087 | 0.31586 | -0.29755 | 0.1831 | 0.059509 | 0.14191 | -0.082397 | 0.29755 | 0.35248 | -0.25177 | 122.3053 | 0.091553 | 122.6669 | 122.7859 | -0.16479 | 122.3511 | 0.12817 | 0.36163 | 122.5204 | 122.9004 | 122.6624 | 122.9187 | 122.6669 | 122.9553 | 122.7448 | 122.3511 | 122.9187 | 122.6669 | 122.7448 | 122.6624 | 122.9553 | -0.52185 | -0.47607
2322.2344 | 122.9462 | -122.5845 | 0.18768 | 0.0045011 | 0.020296 | 0.0056717 | -0.00045932 | -0.0078187 | -0.0051484 | 0.016656 | 0.054932 | 0.28381 | -0.26093 | 0.20599 | 0.10071 | 0.17853 | -0.086975 | 0.37079 | 0.32501 | -0.26093 | 122.3236 | 0.09613 | 122.6395 | 122.7905 | -0.086975 | 122.3236 | 0.13733 | 0.31586 | 122.4976 | 122.9553 | 122.6852 | 122.8683 | 122.6395 | 122.9095 | 122.7631 | 122.3236 | 122.8683 | 122.6395 | 122.7631 | 122.6852 | 122.9095 | -0.44861 | -0.44861
2323.9219 | 122.9599 | -122.6074 | 0.18768 | 0.0045011 | 0.019442 | 0.00054467 | 0.0033859 | -0.0093139 | -0.0079254 | 0.017511 | 0.059509 | 0.32501 | -0.29755 | 0.1831 | 0.050354 | 0.11444 | 0.036621 | 0.32959 | 0.36163 | -0.27008 | 122.3099 | 0.13733 | 122.6669 | 122.7905 | -0.13733 | 122.3373 | 0.17395 | 0.35705 | 122.644 | 122.937 | 122.6578 | 122.9324 | 122.6669 | 122.9691 | 122.7219 | 122.3373 | 122.9324 | 122.6669 | 122.7219 | 122.6578 | 122.9691 | -0.48523 | -0.45776
2325.6719 | 122.8775 | -122.6074 | 0.19684 | 0.0045011 | 0.017306 | 0.0063125 | 0.0016769 | -0.010382 | -0.0074982 | 0.012811 | 0.11444 | 0.28839 | -0.24719 | 0.25635 | 0.15106 | 0.21057 | -0.11444 | 0.43488 | 0.33417 | -0.24261 | 122.3602 | 0.091553 | 122.7219 | 122.8638 | -0.045776 | 122.3648 | 0.13733 | 0.36163 | 122.493 | 123.0423 | 122.7585 | 122.8958 | 122.7219 | 122.9416 | 122.818 | 122.3648 | 122.8958 | 122.7219 | 122.818 | 122.7585 | 122.9416 | -0.44403 | -0.43945
2327.4219 | 122.8088 | -122.6486 | 0.22888 | 0.0045011 | 0.019015 | 0.0048173 | 0.0068039 | -0.0082459 | -0.0083526 | 0.015374 | 0.13275 | 0.2655 | -0.27008 | 0.26093 | 0.11444 | 0.2243 | -0.18768 | 0.38452 | 0.32044 | -0.22888 | 122.3785 | 0.036621 | 122.7814 | 122.9095 | -0.11444 | 122.4197 | 0.091553 | 0.40283 | 122.4609 | 123.0331 | 122.7631 | 122.9141 | 122.7814 | 122.9691 | 122.8729 | 122.4197 | 122.9141 | 122.7814 | 122.8729 | 122.7631 | 122.9691 | -0.49896 | -0.45776
2329.125 | 122.85 | -122.6257 | 0.20599 | 0.0045011 | 0.020083 | 0.0037491 | 0.0053085 | -0.0065369 | -0.003653 | 0.015374 | 0.10529 | 0.27924 | -0.2655 | 0.23346 | 0.11444 | 0.17853 | -0.13275 | 0.37079 | 0.33417 | -0.23346 | 122.3602 | 0.073242 | 122.731 | 122.8592 | -0.091553 | 122.3923 | 0.12817 | 0.37079 | 122.493 | 122.9965 | 122.7402 | 122.905 | 122.731 | 122.9599 | 122.8043 | 122.3923 | 122.905 | 122.731 | 122.8043 | 122.7402 | 122.9599 | -0.4715 | -0.43945
2330.875 | 122.905 | -122.612 | 0.17853 | 0.0045011 | 0.018374 | 0.0018265 | 0.0040269 | -0.0086731 | -0.0074982 | 0.013879 | 0.13275 | 0.26093 | -0.27008 | 0.2655 | 0.16022 | 0.22888 | -0.14191 | 0.46234 | 0.33417 | -0.24261 | 122.3419 | 0.082397 | 122.7448 | 122.8775 | -0.018311 | 122.3694 | 0.15564 | 0.40283 | 122.4701 | 123.0743 | 122.7722 | 122.8729 | 122.7448 | 122.9462 | 122.8409 | 122.3694 | 122.8729 | 122.7448 | 122.8409 | 122.7722 | 122.9462 | -0.44861 | -0.42114
2332.625 | 122.8592 | -122.6257 | 0.22888 | 0.0045011 | 0.021151 | 0.0073807 | 0.0091537 | -0.0082459 | -0.0072846 | 0.017083 | 0.032043 | 0.32044 | -0.29755 | 0.16937 | 0.045776 | 0.11902 | -0.091553 | 0.29297 | 0.3479 | -0.23804 | 122.3282 | 0.091553 | 122.6578 | 122.7951 | -0.18311 | 122.3877 | 0.11902 | 0.32959 | 122.5342 | 122.9187 | 122.6715 | 122.9462 | 122.6578 | 122.9736 | 122.7448 | 122.3877 | 122.9462 | 122.6578 | 122.7448 | 122.6715 | 122.9736 | -0.52643 | -0.46692
2334.375 | 122.9691 | -122.6074 | 0.1831 | 0.012131 | 0.018801 | 0.00075827 | 0.0029587 | -0.0086731 | -0.0072846 | 0.017938 | 0.036621 | 0.31586 | -0.29297 | 0.15564 | 0.036621 | 0.086975 | 0.054932 | 0.31128 | 0.37994 | -0.28381 | 122.3145 | 0.13275 | 122.644 | 122.7631 | -0.14648 | 122.3236 | 0.19684 | 0.32959 | 122.6624 | 122.9187 | 122.644 | 122.9233 | 122.644 | 122.9874 | 122.6944 | 122.3236 | 122.9233 | 122.644 | 122.6944 | 122.644 | 122.9874 | -0.47607 | -0.46692
2336.125 | 122.818 | -122.6532 | 0.2243 | 0.0045011 | 0.019015 | 0.0031083 | 0.0053085 | -0.0050415 | -0.0066438 | 0.014947 | 0.12817 | 0.29297 | -0.27008 | 0.24719 | 0.1236 | 0.21973 | -0.16022 | 0.3891 | 0.32044 | -0.23346 | 122.3831 | 0.068665 | 122.7814 | 122.9004 | -0.10071 | 122.4197 | 0.096131 | 0.39826 | 122.493 | 123.0423 | 122.7768 | 122.9462 | 122.7814 | 122.9736 | 122.8729 | 122.4197 | 122.9462 | 122.7814 | 122.8729 | 122.7768 | 122.9736 | -0.49439 | -0.45776
2337.8281 | 122.8271 | -122.6395 | 0.2243 | -0.0031279 | 0.021151 | -0.0015915 | 0.0068039 | -0.0071777 | -0.00643 | 0.013879 | 0.07782 | 0.29755 | -0.27924 | 0.23346 | 0.10071 | 0.19226 | -0.14191 | 0.36163 | 0.33875 | -0.23804 | 122.3602 | 0.073242 | 122.7173 | 122.8729 | -0.1236 | 122.4014 | 0.11444 | 0.35706 | 122.4976 | 123.0011 | 122.7402 | 122.937 | 122.7173 | 122.9782 | 122.8317 | 122.4014 | 122.937 | 122.7173 | 122.8317 | 122.7402 | 122.9782 | -0.50354 | -0.46234
2339.5625 | 122.9416 | -122.6074 | 0.20142 | 0.0045011 | 0.018801 | 0.0069535 | 0.00060888 | -0.0080323 | -0.0057892 | 0.011743 | 0.073242 | 0.27466 | -0.28381 | 0.20599 | 0.09613 | 0.16937 | -0.091553 | 0.35706 | 0.32959 | -0.24719 | 122.3236 | 0.073242 | 122.6807 | 122.8134 | -0.10529 | 122.3602 | 0.12817 | 0.35706 | 122.5159 | 122.9645 | 122.7036 | 122.8821 | 122.6807 | 122.937 | 122.7768 | 122.3602 | 122.8821 | 122.6807 | 122.7768 | 122.7036 | 122.937 | -0.48523 | -0.44861
2341.25 | 122.8867 | -122.644 | 0.20142 | 0.0045011 | 0.018801 | 0.0069535 | 0.0057357 | -0.0097413 | -0.004721 | 0.016229 | 0.10071 | 0.27466 | -0.26093 | 0.2243 | 0.10986 | 0.18768 | -0.12817 | 0.37079 | 0.32959 | -0.24719 | 122.3831 | 0.073242 | 122.7448 | 122.8683 | -0.091553 | 122.3969 | 0.12817 | 0.36163 | 122.5159 | 123.0148 | 122.7539 | 122.9187 | 122.7448 | 122.9736 | 122.8317 | 122.3969 | 122.9187 | 122.7448 | 122.8317 | 122.7539 | 122.9736 | -0.46234 | -0.44861
2343.0156 | 122.9507 | -122.6303 | 0.19226 | -0.010757 | 0.018374 | 0.0037491 | 0.0033859 | -0.0086731 | -0.00643 | 0.013665 | 0.054932 | 0.27008 | -0.27924 | 0.21057 | 0.09613 | 0.16479 | -0.09613 | 0.36163 | 0.35706 | -0.23804 | 122.3511 | 0.07782 | 122.6852 | 122.8409 | -0.096131 | 122.3923 | 0.16479 | 0.33417 | 122.5342 | 122.9919 | 122.7264 | 122.9004 | 122.6852 | 122.9874 | 122.7951 | 122.3923 | 122.9004 | 122.6852 | 122.7951 | 122.7264 | 122.9874 | -0.4715 | -0.4303
2344.7656 | 122.9736 | -122.6212 | 0.21057 | -0.0031279 | 0.01816 | 0.0013993 | 0.0070175 | -0.0086731 | -0.0094208 | 0.014947 | 0.018311 | 0.32959 | -0.32044 | 0.17853 | 0.032043 | 0.07782 | 0.054932 | 0.29755 | 0.37079 | -0.2655 | 122.3007 | 0.11902 | 122.6395 | 122.7997 | -0.17853 | 122.3557 | 0.16022 | 0.33875 | 122.6761 | 122.9187 | 122.6532 | 122.9507 | 122.6395 | 122.9919 | 122.699 | 122.3557 | 122.9507 | 122.6395 | 122.699 | 122.6532 | 122.9919 | -0.53101 | -0.47607
2346.5312 | 122.9462 | -122.644 | 0.19226 | 0.0045011 | 0.018587 | 0.00075827 | 0.0053085 | -0.0097413 | -0.007071 | 0.01452 | 0.041199 | 0.31586 | -0.29297 | 0.1831 | 0.045776 | 0.10071 | 0.041199 | 0.32501 | 0.37994 | -0.26093 | 122.3511 | 0.1236 | 122.6852 | 122.8271 | -0.14648 | 122.3831 | 0.18768 | 0.33417 | 122.6852 | 122.9691 | 122.6898 | 122.9599 | 122.6852 | 123.024 | 122.7448 | 122.3831 | 122.9599 | 122.6852 | 122.7448 | 122.6898 | 123.024 | -0.48523 | -0.45319
2348.2344 | 122.8592 | -122.6624 | 0.21973 | -0.010757 | 0.019869 | 0.0013993 | 0.0031723 | -0.0067505 | -0.0062164 | 0.016015 | 0.10986 | 0.27924 | -0.25177 | 0.23346 | 0.11902 | 0.19684 | -0.15564 | 0.37537 | 0.32501 | -0.24719 | 122.4106 | 0.059509 | 122.7722 | 122.8958 | -0.10071 | 122.4152 | 0.10529 | 0.36163 | 122.5067 | 123.0377 | 122.7814 | 122.9416 | 122.7722 | 122.9874 | 122.8592 | 122.4152 | 122.9416 | 122.7722 | 122.8592 | 122.7814 | 122.9874 | -0.4715 | -0.46692
2349.9844 | 122.9279 | -122.6166 | 0.20599 | 0.012131 | 0.016878 | -0.00052333 | 0.00060888 | -0.0078187 | -0.007071 | 0.014306 | 0.13275 | 0.27924 | -0.26093 | 0.27466 | 0.16937 | 0.24261 | -0.13275 | 0.45319 | 0.32501 | -0.23346 | 122.3557 | 0.073242 | 122.7493 | 122.8912 | -0.036621 | 122.3831 | 0.11902 | 0.39368 | 122.4838 | 123.0698 | 122.7859 | 122.8958 | 122.7493 | 122.9416 | 122.8592 | 122.3831 | 122.8958 | 122.7493 | 122.8592 | 122.7859 | 122.9416 | -0.46692 | -0.43945
2351.7344 | 122.9095 | -122.6578 | 0.21057 | -0.010757 | 0.019656 | -0.0026595 | 0.0029587 | -0.0097413 | -0.0072846 | 0.016443 | 0.07782 | 0.29297 | -0.25635 | 0.2243 | 0.10529 | 0.1831 | -0.1236 | 0.36163 | 0.35248 | -0.24261 | 122.4014 | 0.082398 | 122.7356 | 122.8821 | -0.10529 | 122.4152 | 0.14191 | 0.33417 | 122.5342 | 123.0194 | 122.7631 | 122.9507 | 122.7356 | 123.0103 | 122.8409 | 122.4152 | 122.9507 | 122.7356 | 122.8409 | 122.7631 | 123.0103 | -0.46692 | -0.45319
2353.4219 | 122.9645 | -122.6349 | 0.18768 | -0.0031279 | 0.017947 | 0.0071671 | 0.0044541 | -0.0067505 | -0.0051484 | 0.014734 | 0.073242 | 0.28839 | -0.26093 | 0.21515 | 0.10071 | 0.16479 | -0.086975 | 0.35706 | 0.32501 | -0.24261 | 122.374 | 0.10071 | 122.7081 | 122.85 | -0.086975 | 122.3923 | 0.13733 | 0.33417 | 122.5479 | 122.9919 | 122.7356 | 122.9233 | 122.7081 | 122.9599 | 122.7997 | 122.3923 | 122.9233 | 122.7081 | 122.7997 | 122.7356 | 122.9599 | -0.44861 | -0.4303
2355.1562 | 122.9736 | -122.612 | 0.21515 | -0.0031279 | 0.02051 | 0.0026809 | 0.0061631 | -0.0097413 | -0.00878 | 0.014306 | 0.013733 | 0.31586 | -0.32959 | 0.16479 | 0.027466 | 0.073242 | 0.064087 | 0.3067 | 0.38452 | -0.2655 | 122.2824 | 0.10071 | 122.6257 | 122.7768 | -0.18768 | 122.3465 | 0.16937 | 0.34332 | 122.6761 | 122.9187 | 122.6395 | 122.9279 | 122.6257 | 122.9965 | 122.6852 | 122.3465 | 122.9279 | 122.6257 | 122.6852 | 122.6395 | 122.9965 | -0.54474 | -0.48065
2356.9062 | 122.9233 | -122.6303 | 0.1831 | 0.0045011 | 0.019442 | 0.0035355 | 0.00018148 | -0.0091003 | -0.0068574 | 0.015374 | 0.12817 | 0.28839 | -0.27008 | 0.28839 | 0.16479 | 0.23804 | -0.11444 | 0.46234 | 0.33875 | -0.25177 | 122.3602 | 0.10529 | 122.7585 | 122.9187 | -0.01831 | 122.3785 | 0.15564 | 0.39826 | 122.5159 | 123.0927 | 122.7951 | 122.9187 | 122.7585 | 122.9691 | 122.8683 | 122.3785 | 122.9187 | 122.7585 | 122.8683 | 122.7951 | 122.9691 | -0.45319 | -0.43488
2358.6719 | 122.9004 | -122.6669 | 0.23346 | -0.0031279 | 0.019015 | 0.0071671 | 0.010435 | -0.0076049 | -0.0083526 | 0.014947 | 0.032043 | 0.32959 | -0.31586 | 0.14191 | 0.009155 | 0.059509 | 0.027466 | 0.24719 | 0.36621 | -0.27466 | 122.3511 | 0.096131 | 122.699 | 122.8088 | -0.2243 | 122.3923 | 0.13275 | 0.3479 | 122.6944 | 122.9141 | 122.6761 | 122.9965 | 122.699 | 123.0331 | 122.7264 | 122.3923 | 122.9965 | 122.699 | 122.7264 | 122.6761 | 123.0331 | -0.54932 | -0.50812
2360.3594 | 122.8546 | -122.6807 | 0.21973 | 0.012131 | 0.022219 | 0.0018265 | 0.0061631 | -0.0069641 | -0.0094208 | 0.014734 | 0.07782 | 0.3067 | -0.29297 | 0.18768 | 0.059509 | 0.12817 | 0 | 0.32501 | 0.35706 | -0.26093 | 122.3877 | 0.086975 | 122.7585 | 122.8683 | -0.16022 | 122.4197 | 0.13733 | 0.37079 | 122.6807 | 123.0057 | 122.7402 | 122.9874 | 122.7585 | 123.0377 | 122.8088 | 122.4197 | 122.9874 | 122.7585 | 122.8088 | 122.7402 | 123.0377 | -0.5127 | -0.48065
2362.1094 | 122.9782 | -122.612 | 0.18768 | 0.0045011 | 0.01816 | 0.0043899 | -0.0019547 | -0.0084595 | -0.0055756 | 0.015161 | 0.059509 | 0.28839 | -0.27924 | 0.20599 | 0.10071 | 0.17395 | -0.086975 | 0.36163 | 0.34332 | -0.23804 | 122.3328 | 0.10071 | 122.6715 | 122.818 | -0.086975 | 122.374 | 0.15564 | 0.33874 | 122.525 | 122.9736 | 122.7127 | 122.9004 | 122.6715 | 122.9553 | 122.7859 | 122.374 | 122.9004 | 122.6715 | 122.7859 | 122.7127 | 122.9553 | -0.46692 | -0.42572
2363.8125 | 122.937 | -122.6303 | 0.21515 | -0.0031279 | 0.015597 | 0.0056717 | 0.0031723 | -0.0084595 | -0.0066438 | 0.014947 | 0.12817 | 0.29755 | -0.28381 | 0.2655 | 0.15106 | 0.21515 | -0.10071 | 0.44861 | 0.32959 | -0.24261 | 122.3465 | 0.082397 | 122.7585 | 122.8958 | -0.064087 | 122.3877 | 0.11444 | 0.41199 | 122.5296 | 123.0789 | 122.7814 | 122.9279 | 122.7585 | 122.9599 | 122.8455 | 122.3877 | 122.9279 | 122.7585 | 122.8455 | 122.7814 | 122.9599 | -0.49896 | -0.45776
2365.5625 | 122.9782 | -122.644 | 0.20599 | 0.0045011 | 0.019015 | 0.0035355 | 0.0038131 | -0.010596 | -0.00878 | 0.014947 | 0.091553 | 0.29297 | -0.27466 | 0.21057 | 0.082397 | 0.16022 | 0.009155 | 0.36163 | 0.35248 | -0.25635 | 122.3694 | 0.086975 | 122.7356 | 122.8546 | -0.1236 | 122.3877 | 0.14648 | 0.36621 | 122.6532 | 123.0057 | 122.7264 | 122.937 | 122.7356 | 122.9965 | 122.8043 | 122.3877 | 122.937 | 122.7356 | 122.8043 | 122.7264 | 122.9965 | -0.48065 | -0.46234
2367.3281 | 122.9553 | -122.6486 | 0.20599 | 0.0045011 | 0.016451 | 0.0028947 | 0.0025315 | -0.0091003 | -0.0062164 | 0.013025 | 0.10986 | 0.29755 | -0.25177 | 0.25635 | 0.13275 | 0.20599 | -0.064087 | 0.42114 | 0.34332 | -0.24261 | 122.3969 | 0.091552 | 122.7585 | 122.905 | -0.073243 | 122.406 | 0.13733 | 0.36163 | 122.5845 | 123.0698 | 122.7814 | 122.9462 | 122.7585 | 122.9919 | 122.8546 | 122.406 | 122.9462 | 122.7585 | 122.8546 | 122.7814 | 122.9919 | -0.45776 | -0.44861
2369.0312 | 122.8363 | -122.6852 | 0.2243 | 0.0045011 | 0.017306 | 0.0035355 | 0.0063767 | -0.0063233 | -0.007071 | 0.013238 | 0.10986 | 0.28381 | -0.26093 | 0.26093 | 0.11444 | 0.20599 | -0.15106 | 0.37537 | 0.32959 | -0.21973 | 122.4243 | 0.059509 | 122.7951 | 122.9462 | -0.10986 | 122.4655 | 0.10529 | 0.37079 | 122.5342 | 123.0606 | 122.7997 | 122.9691 | 122.7951 | 123.0148 | 122.8912 | 122.4655 | 122.9691 | 122.7951 | 122.8912 | 122.7997 | 123.0148 | -0.48523 | -0.44403
2370.7656 | 122.8775 | -122.6624 | 0.21973 | 0.0045011 | 0.018801 | 0.0031083 | 0.0027451 | -0.0071777 | -0.0072846 | 0.014093 | 0.11902 | 0.28839 | -0.25177 | 0.24719 | 0.1236 | 0.21973 | -0.16022 | 0.37079 | 0.32501 | -0.23804 | 122.4106 | 0.068664 | 122.7814 | 122.9095 | -0.096131 | 122.4243 | 0.10529 | 0.37079 | 122.5021 | 123.0331 | 122.7859 | 122.9507 | 122.7814 | 122.9874 | 122.8821 | 122.4243 | 122.9507 | 122.7814 | 122.8821 | 122.7859 | 122.9874 | -0.4715 | -0.45776
2372.4531 | 122.9279 | -122.6578 | 0.21057 | 0.0045011 | 0.016024 | 0.00054467 | 0.0044541 | -0.010382 | -0.0068574 | 0.013452 | 0.1236 | 0.2655 | -0.2655 | 0.27466 | 0.16022 | 0.2243 | -0.10986 | 0.45319 | 0.34332 | -0.21973 | 122.3923 | 0.054932 | 122.7814 | 122.9324 | -0.050354 | 122.438 | 0.13275 | 0.3891 | 122.5479 | 123.111 | 122.818 | 122.9233 | 122.7814 | 123.0011 | 122.8821 | 122.438 | 122.9233 | 122.7814 | 122.8821 | 122.818 | 123.0011 | -0.47607 | -0.4303
2374.2031 | 122.905 | -122.6898 | 0.2243 | 0.012131 | 0.021578 | 0.0075943 | 0.0065903 | -0.0086731 | -0.0074982 | 0.016015 | 0.032043 | 0.29755 | -0.29297 | 0.15106 | 0.013733 | 0.10071 | -0.018311 | 0.27008 | 0.37994 | -0.27924 | 122.3969 | 0.073242 | 122.7219 | 122.8409 | -0.21057 | 122.4106 | 0.15564 | 0.32501 | 122.6715 | 122.9599 | 122.7036 | 122.9874 | 122.7219 | 123.0698 | 122.7905 | 122.4106 | 122.9874 | 122.7219 | 122.7905 | 122.7036 | 123.0698 | -0.51727 | -0.50354
2375.9531 | 122.9919 | -122.6349 | 0.21057 | 0.0045011 | 0.020296 | 0.0035355 | 0.0042405 | -0.0086731 | -0.00643 | 0.014947 | 0.004578 | 0.32959 | -0.31586 | 0.15564 | 0.022888 | 0.07782 | 0.068665 | 0.29297 | 0.37079 | -0.27466 | 122.319 | 0.11902 | 122.6395 | 122.7905 | -0.18768 | 122.3602 | 0.16022 | 0.32044 | 122.7036 | 122.9279 | 122.6578 | 122.9645 | 122.6395 | 123.0057 | 122.7127 | 122.3602 | 122.9645 | 122.6395 | 122.7127 | 122.6578 | 123.0057 | -0.52643 | -0.48523
2377.6406 | 122.905 | -122.6715 | 0.25177 | -0.0031279 | 0.016878 | 0.0035355 | 0.0070175 | -0.0061097 | -0.0094208 | 0.014734 | 0.018311 | 0.3067 | -0.29755 | 0.14191 | -0.009155 | 0.064087 | 0.018311 | 0.23346 | 0.37994 | -0.27924 | 122.374 | 0.054932 | 122.6898 | 122.8134 | -0.26093 | 122.3923 | 0.12817 | 0.31586 | 122.6898 | 122.905 | 122.6624 | 122.9782 | 122.6898 | 123.0515 | 122.7356 | 122.3923 | 122.9782 | 122.6898 | 122.7356 | 122.6624 | 123.0515 | -0.54932 | -0.53101
2379.3906 | 123.0057 | -122.6578 | 0.19226 | 0.0045011 | 0.021151 | 0.00033107 | -0.0011001 | -0.0071777 | -0.0074982 | 0.017083 | 0.068665 | 0.27466 | -0.2655 | 0.2243 | 0.11444 | 0.16937 | -0.10529 | 0.38452 | 0.32959 | -0.26093 | 122.3923 | 0.082397 | 122.7264 | 122.8821 | -0.07782 | 122.3969 | 0.13733 | 0.33417 | 122.5525 | 123.0423 | 122.7722 | 122.9324 | 122.7264 | 122.9874 | 122.8271 | 122.3969 | 122.9324 | 122.7264 | 122.8271 | 122.7722 | 122.9874 | -0.45776 | -0.45319
2381.1406 | 122.9141 | -122.6624 | 0.23346 | 0.0045011 | 0.018587 | 0.0043899 | 0.0078721 | -0.0065369 | -0.0077118 | 0.01687 | 0.022888 | 0.30212 | -0.3067 | 0.13733 | 0.022888 | 0.073242 | 0.009155 | 0.27008 | 0.34332 | -0.27008 | 122.3557 | 0.068665 | 122.6852 | 122.7997 | -0.21057 | 122.3923 | 0.10986 | 0.32959 | 122.6715 | 122.9324 | 122.6852 | 122.9645 | 122.6852 | 123.0057 | 122.7356 | 122.3923 | 122.9645 | 122.6852 | 122.7356 | 122.6852 | 123.0057 | -0.54016 | -0.50354
2382.8281 | 122.9233 | -122.6807 | 0.22888 | 0.0045011 | 0.019228 | 0.0080215 | 0.0042405 | -0.0065369 | -0.010916 | 0.017511 | 0.004578 | 0.3067 | -0.31586 | 0.13733 | 0 | 0.07782 | 0.036621 | 0.23346 | 0.36163 | -0.27008 | 122.3648 | 0.07782 | 122.6852 | 122.818 | -0.22888 | 122.4106 | 0.13275 | 0.32044 | 122.7173 | 122.9141 | 122.6807 | 122.9874 | 122.6852 | 123.0423 | 122.7585 | 122.4106 | 122.9874 | 122.6852 | 122.7585 | 122.6807 | 123.0423 | -0.54474 | -0.49896
2384.5781 | 122.9507 | -122.6669 | 0.20142 | 0.012131 | 0.016024 | -0.00073693 | 0.00018148 | -0.0054687 | -0.0079254 | 0.014947 | 0.10986 | 0.28381 | -0.25635 | 0.26093 | 0.13275 | 0.20599 | -0.091553 | 0.43488 | 0.32044 | -0.22888 | 122.4106 | 0.082397 | 122.7768 | 122.9279 | -0.068665 | 122.438 | 0.11902 | 0.36621 | 122.5754 | 123.1018 | 122.7997 | 122.9507 | 122.7768 | 122.9874 | 122.8729 | 122.438 | 122.9507 | 122.7768 | 122.8729 | 122.7997 | 122.9874 | -0.45776 | -0.4303
2386.3438 | 122.8683 | -122.7081 | 0.2243 | 0.0045011 | 0.019656 | 0.0020401 | 0.0080857 | -0.0046143 | -0.0092072 | 0.014306 | 0.068665 | 0.32044 | -0.30212 | 0.19226 | 0.045776 | 0.10529 | -0.004578 | 0.30212 | 0.36621 | -0.2655 | 122.406 | 0.096131 | 122.7768 | 122.9004 | -0.17853 | 122.4426 | 0.14191 | 0.37079 | 122.7036 | 123.0103 | 122.7539 | 123.0286 | 122.7768 | 123.0743 | 122.8134 | 122.4426 | 123.0286 | 122.7768 | 122.8134 | 122.7539 | 123.0743 | -0.52643 | -0.48981
2388.0312 | 122.9187 | -122.6852 | 0.21515 | 0.012131 | 0.020724 | -9.6132e-05 | 0.00039528 | -0.0095277 | -0.0049348 | 0.013665 | 0.086975 | 0.26093 | -0.27466 | 0.21515 | 0.11444 | 0.17853 | -0.11902 | 0.36621 | 0.32501 | -0.23804 | 122.4106 | 0.045776 | 122.7722 | 122.9004 | -0.10071 | 122.4472 | 0.10986 | 0.36163 | 122.5662 | 123.0515 | 122.7997 | 122.9462 | 122.7722 | 123.0103 | 122.8638 | 122.4472 | 122.9462 | 122.7722 | 122.8638 | 122.7997 | 123.0103 | -0.48981 | -0.45319
2389.7812 | 123.0331 | -122.6761 | 0.18768 | 0.0045011 | 0.019015 | 0.0028947 | 0.0035995 | -0.0095277 | -0.0079254 | 0.016229 | 0 | 0.31586 | -0.30212 | 0.14648 | 0.041199 | 0.073242 | 0.068665 | 0.3067 | 0.37537 | -0.2655 | 122.374 | 0.12817 | 122.6761 | 122.8226 | -0.14648 | 122.4106 | 0.18768 | 0.30212 | 122.7448 | 122.9828 | 122.7173 | 122.9919 | 122.6761 | 123.0515 | 122.7493 | 122.4106 | 122.9919 | 122.6761 | 122.7493 | 122.7173 | 123.0515 | -0.48981 | -0.45319
2391.5312 | 122.9691 | -122.6715 | 0.21057 | -0.0031279 | 0.019656 | 0.0058853 | 0.00082248 | -0.010168 | -0.0051484 | 0.017083 | 0.1236 | 0.2655 | -0.2655 | 0.27466 | 0.14648 | 0.24719 | -0.13275 | 0.43488 | 0.31128 | -0.24261 | 122.406 | 0.054932 | 122.7951 | 122.9462 | -0.064087 | 122.4289 | 0.10071 | 0.3891 | 122.5388 | 123.1064 | 122.818 | 122.937 | 122.7951 | 122.9828 | 122.9187 | 122.4289 | 122.937 | 122.7951 | 122.9187 | 122.818 | 122.9828 | -0.47607 | -0.45319
2393.2812 | 122.9324 | -122.6852 | 0.23804 | -0.0031279 | 0.020724 | 0.0041763 | 0.0042405 | -0.0082459 | -0.0057892 | 0.014734 | 0.10071 | 0.27008 | -0.25635 | 0.22888 | 0.10071 | 0.19226 | -0.13733 | 0.37537 | 0.32044 | -0.23346 | 122.4289 | 0.032044 | 122.7859 | 122.9141 | -0.13733 | 122.4518 | 0.082398 | 0.35706 | 122.5479 | 123.0606 | 122.7859 | 122.9553 | 122.7859 | 123.0057 | 122.8775 | 122.4518 | 122.9553 | 122.7859 | 122.8775 | 122.7859 | 123.0057 | -0.49439 | -0.4715
2395.0312 | 122.9645 | -122.7081 | 0.21057 | 0.0045011 | 0.017306 | 0.0037491 | 0.0023179 | -0.010809 | -0.0060028 | 0.016229 | 0.086975 | 0.2655 | -0.26093 | 0.21515 | 0.091553 | 0.16937 | -0.10071 | 0.37079 | 0.32501 | -0.26093 | 122.4472 | 0.054932 | 122.7951 | 122.9233 | -0.11902 | 122.4472 | 0.11444 | 0.3479 | 122.6074 | 123.0789 | 122.7997 | 122.9736 | 122.7951 | 123.0331 | 122.8775 | 122.4472 | 122.9736 | 122.7951 | 122.8775 | 122.7997 | 123.0331 | -0.4715 | -0.4715
2396.7188 | 122.8958 | -122.731 | 0.23804 | -0.0031279 | 0.019015 | 0.0041763 | 0.0093673 | -0.0088867 | -0.0074982 | 0.015161 | 0.07782 | 0.29297 | -0.30212 | 0.21057 | 0.059509 | 0.14191 | -0.022888 | 0.33875 | 0.36163 | -0.26093 | 122.4289 | 0.054932 | 122.8088 | 122.9416 | -0.17853 | 122.4701 | 0.1236 | 0.37994 | 122.7081 | 123.0698 | 122.7905 | 123.024 | 122.8088 | 123.0927 | 122.8729 | 122.4701 | 123.024 | 122.8088 | 122.8729 | 122.7905 | 123.0927 | -0.54016 | -0.49896
2398.4844 | 122.9645 | -122.6578 | 0.22888 | 0.0045011 | 0.020937 | 0.0058853 | 0.0078721 | -0.010168 | -0.004721 | 0.013665 | 0.045776 | 0.31586 | -0.29755 | 0.18768 | 0.032043 | 0.10986 | 0.018311 | 0.31128 | 0.36163 | -0.27924 | 122.3602 | 0.086975 | 122.7036 | 122.8455 | -0.19684 | 122.3785 | 0.13275 | 0.34332 | 122.6761 | 122.9691 | 122.6898 | 122.9736 | 122.7036 | 123.0194 | 122.7676 | 122.3785 | 122.9736 | 122.7036 | 122.7676 | 122.6898 | 123.0194 | -0.52643 | -0.50812
2400.2344 | 123.0103 | -122.6486 | 0.19684 | -0.0031279 | 0.019228 | 0.0020401 | -0.0021683 | -0.0091003 | -0.005362 | 0.013452 | 0.045776 | 0.27924 | -0.27466 | 0.21973 | 0.10529 | 0.17395 | -0.09613 | 0.37537 | 0.31586 | -0.24719 | 122.374 | 0.082398 | 122.6944 | 122.8683 | -0.091552 | 122.4014 | 0.11902 | 0.32043 | 122.5525 | 123.024 | 122.7539 | 122.9279 | 122.6944 | 122.9645 | 122.8226 | 122.4014 | 122.9279 | 122.6944 | 122.8226 | 122.7539 | 122.9645 | -0.4715 | -0.44403
2401.9844 | 122.9553 | -122.7036 | 0.2243 | 0.0045011 | 0.020937 | 0.0050309 | 0.0091537 | -0.0054687 | -0.0089936 | 0.015588 | 0.022888 | 0.31586 | -0.32044 | 0.14191 | 0.004578 | 0.086975 | 0.004578 | 0.25635 | 0.36163 | -0.26093 | 122.3831 | 0.091553 | 122.7264 | 122.8455 | -0.21973 | 122.4426 | 0.13733 | 0.34332 | 122.7081 | 122.9599 | 122.7081 | 123.0194 | 122.7264 | 123.0652 | 122.7905 | 122.4426 | 123.0194 | 122.7264 | 122.7905 | 122.7081 | 123.0652 | -0.54474 | -0.48523
2403.6875 | 122.9279 | -122.7264 | 0.21973 | 0.0045011 | 0.020724 | 0.0069535 | 0.0078721 | -0.0076049 | -0.0068574 | 0.015374 | 0.064087 | 0.30212 | -0.30212 | 0.15564 | 0.018311 | 0.10529 | 0.013733 | 0.27924 | 0.36163 | -0.2655 | 122.4243 | 0.082397 | 122.7905 | 122.8821 | -0.20142 | 122.4609 | 0.14191 | 0.36621 | 122.7402 | 123.0057 | 122.7448 | 123.0286 | 122.7905 | 123.0881 | 122.8317 | 122.4609 | 123.0286 | 122.7905 | 122.8317 | 122.7448 | 123.0881 | -0.52185 | -0.48523
2405.4375 | 123.0057 | -122.6852 | 0.19226 | -0.0031279 | 0.016024 | 0.00033107 | -0.00088652 | -0.0067505 | -0.0049348 | 0.015802 | 0.068665 | 0.27008 | -0.28381 | 0.23804 | 0.1236 | 0.21057 | -0.10071 | 0.40283 | 0.33417 | -0.23804 | 122.4014 | 0.07782 | 122.7539 | 122.9233 | -0.068665 | 122.4472 | 0.14191 | 0.35248 | 122.5845 | 123.0881 | 122.8088 | 122.9553 | 122.7539 | 123.0194 | 122.8958 | 122.4472 | 122.9553 | 122.7539 | 122.8958 | 122.8088 | 123.0194 | -0.47607 | -0.4303
2407.125 | 123.0286 | -122.6944 | 0.19226 | 0.0045011 | 0.019015 | 0.0033219 | 0.0031723 | -0.011236 | -0.0072846 | 0.014947 | 0.091553 | 0.3067 | -0.27008 | 0.21057 | 0.091553 | 0.14191 | 0.004578 | 0.35248 | 0.3479 | -0.27008 | 122.4243 | 0.11444 | 122.7859 | 122.905 | -0.10071 | 122.4243 | 0.15564 | 0.36163 | 122.699 | 123.0469 | 122.7859 | 123.0011 | 122.7859 | 123.0423 | 122.8363 | 122.4243 | 123.0011 | 122.7859 | 122.8363 | 122.7859 | 123.0423 | -0.46234 | -0.46234
2408.875 | 122.9416 | -122.7081 | 0.23346 | 0.012131 | 0.020724 | 0.0054581 | 0.0057357 | -0.0080323 | -0.0068574 | 0.013879 | 0 | 0.3067 | -0.3067 | 0.14648 | 0.009155 | 0.086975 | 0.018311 | 0.26093 | 0.37537 | -0.26093 | 122.4014 | 0.073243 | 122.7081 | 122.8546 | -0.2243 | 122.4472 | 0.14191 | 0.3067 | 122.7264 | 122.9691 | 122.7173 | 123.0148 | 122.7081 | 123.0835 | 122.7951 | 122.4472 | 123.0148 | 122.7081 | 122.7951 | 122.7173 | 123.0835 | -0.54016 | -0.49438
2410.5625 | 122.9187 | -122.731 | 0.23346 | -0.0031279 | 0.022219 | 0.0071671 | 0.0074447 | -0.0063233 | -0.0074982 | 0.015374 | 0.082397 | 0.31586 | -0.29297 | 0.19684 | 0.073242 | 0.1236 | -0.009155 | 0.32959 | 0.37537 | -0.25635 | 122.438 | 0.082398 | 122.8134 | 122.9279 | -0.16022 | 122.4747 | 0.14191 | 0.37537 | 122.7219 | 123.0606 | 122.8043 | 123.0469 | 122.8134 | 123.1064 | 122.8546 | 122.4747 | 123.0469 | 122.8134 | 122.8546 | 122.8043 | 123.1064 | -0.52643 | -0.48981
2412.2969 | 122.8867 | -122.7173 | 0.21515 | -0.010757 | 0.016878 | 0.0041763 | 0.0033859 | -0.0071777 | -0.003653 | 0.015802 | 0.1236 | 0.26093 | -0.24261 | 0.25635 | 0.1236 | 0.20599 | -0.16937 | 0.3891 | 0.31586 | -0.22888 | 122.4747 | 0.045776 | 122.8409 | 122.9736 | -0.091553 | 122.4884 | 0.10071 | 0.36621 | 122.5479 | 123.1064 | 122.8409 | 122.9782 | 122.8409 | 123.0331 | 122.9233 | 122.4884 | 122.9782 | 122.8409 | 122.9233 | 122.8409 | 123.0331 | -0.45776 | -0.44403
2414.0469 | 122.9416 | -122.7173 | 0.22888 | 0.012131 | 0.017733 | 0.00097207 | 0.0044541 | -0.0052551 | -0.007071 | 0.017297 | 0.022888 | 0.31586 | -0.30212 | 0.13733 | 0.004578 | 0.082397 | 0.013733 | 0.25177 | 0.36621 | -0.26093 | 122.4152 | 0.086975 | 122.7402 | 122.8546 | -0.2243 | 122.4564 | 0.13733 | 0.32501 | 122.731 | 122.9691 | 122.7219 | 123.0331 | 122.7402 | 123.0835 | 122.7997 | 122.4564 | 123.0331 | 122.7402 | 122.7997 | 122.7219 | 123.0835 | -0.53101 | -0.48981
2415.7344 | 122.9279 | -122.7127 | 0.21973 | 0.0045011 | 0.019228 | 0.0026809 | 0.0046677 | -0.0082459 | -0.0042938 | 0.015374 | 0.041199 | 0.31128 | -0.28381 | 0.16937 | 0.045776 | 0.1236 | -0.086975 | 0.31586 | 0.3479 | -0.24719 | 122.4289 | 0.091552 | 122.7539 | 122.8821 | -0.17395 | 122.4655 | 0.12817 | 0.32501 | 122.6257 | 123.0286 | 122.7585 | 123.024 | 122.7539 | 123.0606 | 122.8363 | 122.4655 | 123.024 | 122.7539 | 122.8363 | 122.7585 | 123.0606 | -0.50354 | -0.46692
2417.4844 | 123.0057 | -122.7036 | 0.21057 | 0.0045011 | 0.017306 | 0.0058853 | -0.00045932 | -0.0088867 | -0.00643 | 0.013452 | 0.11902 | 0.27924 | -0.26093 | 0.25177 | 0.15106 | 0.2243 | -0.091553 | 0.43488 | 0.32959 | -0.22888 | 122.4426 | 0.068665 | 122.8226 | 122.9553 | -0.059509 | 122.4747 | 0.11902 | 0.37994 | 122.612 | 123.1384 | 122.8546 | 122.9828 | 122.8226 | 123.0331 | 122.9279 | 122.4747 | 122.9828 | 122.8226 | 122.9279 | 122.8546 | 123.0331 | -0.4715 | -0.43945
2419.2656 | 123.0103 | -122.7036 | 0.20599 | 0.01976 | 0.017092 | 0.0060989 | 0.0012497 | -0.0091003 | -0.0072846 | 0.01452 | 0.10986 | 0.27466 | -0.27466 | 0.26093 | 0.11902 | 0.20599 | -0.073242 | 0.43488 | 0.34332 | -0.22888 | 122.4289 | 0.068664 | 122.8134 | 122.9645 | -0.086975 | 122.4747 | 0.13733 | 0.38452 | 122.6303 | 123.1384 | 122.8226 | 122.9782 | 122.8134 | 123.0469 | 122.9095 | 122.4747 | 122.9782 | 122.8134 | 122.9095 | 122.8226 | 123.0469 | -0.48065 | -0.43488
2420.9531 | 123.0469 | -122.6944 | 0.19226 | 0.012131 | 0.01346 | 0.0033219 | -0.0021683 | -0.010168 | -0.0045074 | 0.015374 | 0.054932 | 0.27924 | -0.27466 | 0.20599 | 0.09613 | 0.16937 | -0.091553 | 0.35248 | 0.36621 | -0.23346 | 122.4197 | 0.086975 | 122.7493 | 122.9004 | -0.096131 | 122.4609 | 0.17395 | 0.32959 | 122.6028 | 123.0469 | 122.7905 | 122.9736 | 122.7493 | 123.0606 | 122.8638 | 122.4609 | 122.9736 | 122.7493 | 122.8638 | 122.7905 | 123.0606 | -0.46692 | -0.42572
2422.7031 | 123.0377 | -122.7036 | 0.21515 | 0.012131 | 0.021792 | 0.0037491 | 0.0053085 | -0.010168 | -0.0074982 | 0.015161 | 0.013733 | 0.32044 | -0.32044 | 0.16479 | 0.036621 | 0.091553 | 0.054932 | 0.32044 | 0.37079 | -0.27466 | 122.3831 | 0.10529 | 122.7173 | 122.8683 | -0.17853 | 122.4289 | 0.15564 | 0.33417 | 122.7585 | 123.024 | 122.7402 | 123.024 | 122.7173 | 123.0743 | 122.7951 | 122.4289 | 123.024 | 122.7173 | 122.7951 | 122.7402 | 123.0743 | -0.53558 | -0.48981
2424.4062 | 122.9599 | -122.7173 | 0.21057 | 0.012131 | 0.018587 | 0.0056717 | 0.0055221 | -0.0071777 | -0.0062164 | 0.01452 | 0.022888 | 0.30212 | -0.3067 | 0.14648 | 0.013733 | 0.073242 | 0.013733 | 0.25635 | 0.36163 | -0.27466 | 122.4106 | 0.091553 | 122.7402 | 122.8638 | -0.19684 | 122.4426 | 0.15106 | 0.32959 | 122.731 | 122.9736 | 122.731 | 123.0194 | 122.7402 | 123.0789 | 122.7905 | 122.4426 | 123.0194 | 122.7402 | 122.7905 | 122.731 | 123.0789 | -0.51727 | -0.48523
2426.1719 | 122.937 | -122.7493 | 0.2243 | 0.0045011 | 0.019442 | 0.0063125 | 0.0042405 | -0.0056823 | -0.010062 | 0.015161 | 0.073242 | 0.30212 | -0.29755 | 0.19226 | 0.054932 | 0.13275 | 0.004578 | 0.3479 | 0.37079 | -0.25177 | 122.4518 | 0.07782 | 122.8226 | 122.9416 | -0.16937 | 122.4976 | 0.14648 | 0.37079 | 122.7539 | 123.0972 | 122.8043 | 123.0515 | 122.8226 | 123.1201 | 122.8821 | 122.4976 | 123.0515 | 122.8226 | 122.8821 | 122.8043 | 123.1201 | -0.52185 | -0.47607
2427.875 | 122.9645 | -122.7448 | 0.2243 | 0.012131 | 0.022433 | 0.0020401 | 0.0050949 | -0.0052551 | -0.0085664 | 0.015374 | 0.027466 | 0.31586 | -0.3067 | 0.15106 | 0.013733 | 0.10071 | 0 | 0.26093 | 0.36621 | -0.27008 | 122.438 | 0.091553 | 122.7722 | 122.8958 | -0.21057 | 122.4747 | 0.14191 | 0.33417 | 122.7448 | 123.0057 | 122.7585 | 123.0606 | 122.7722 | 123.111 | 122.8455 | 122.4747 | 123.0606 | 122.7722 | 122.8455 | 122.7585 | 123.111 | -0.53101 | -0.49439
2429.6406 | 122.9782 | -122.7264 | 0.23346 | 0.012131 | 0.020296 | 0.0035355 | 0.0042405 | -0.0076049 | -0.0057892 | 0.017297 | 0.009155 | 0.3067 | -0.31128 | 0.10986 | -0.004578 | 0.068665 | 0.027466 | 0.26093 | 0.37537 | -0.2655 | 122.4152 | 0.073243 | 122.7356 | 122.8363 | -0.23804 | 122.4609 | 0.14191 | 0.32043 | 122.7539 | 122.9874 | 122.7219 | 123.0331 | 122.7356 | 123.1018 | 122.7951 | 122.4609 | 123.0331 | 122.7356 | 122.7951 | 122.7219 | 123.1018 | -0.54474 | -0.49896
2431.4062 | 123.0057 | -122.7173 | 0.20142 | -0.0031279 | 0.019015 | -0.0028731 | -0.0017411 | -0.0084595 | -0.0049348 | 0.013665 | 0.11902 | 0.27924 | -0.25635 | 0.23804 | 0.15564 | 0.23346 | -0.10986 | 0.46692 | 0.33417 | -0.22888 | 122.4609 | 0.07782 | 122.8363 | 122.9553 | -0.045776 | 122.4884 | 0.13275 | 0.37537 | 122.6074 | 123.1842 | 122.8729 | 122.9965 | 122.8363 | 123.0515 | 122.9507 | 122.4884 | 122.9965 | 122.8363 | 122.9507 | 122.8729 | 123.0515 | -0.45776 | -0.4303
2433.1562 | 122.9874 | -122.7264 | 0.20599 | 0.0045011 | 0.019656 | 0.0054581 | 0.0063767 | -0.0071777 | -0.00643 | 0.014947 | 0.022888 | 0.32501 | -0.3067 | 0.14648 | 0.013733 | 0.091553 | 0.013733 | 0.25635 | 0.36621 | -0.27924 | 122.4197 | 0.11902 | 122.7493 | 122.8729 | -0.19226 | 122.4472 | 0.16022 | 0.32959 | 122.7402 | 122.9828 | 122.7402 | 123.0515 | 122.7493 | 123.0927 | 122.818 | 122.4472 | 123.0515 | 122.7493 | 122.818 | 122.7402 | 123.0927 | -0.5127 | -0.48523
2434.8594 | 122.9691 | -122.7402 | 0.2243 | -0.0031279 | 0.020083 | 0.0067399 | 0.0057357 | -0.0088867 | -0.0060028 | 0.01687 | 0.027466 | 0.30212 | -0.29297 | 0.13733 | 0.013733 | 0.086975 | 0.009155 | 0.25177 | 0.37537 | -0.27924 | 122.4472 | 0.07782 | 122.7676 | 122.8775 | -0.21057 | 122.4609 | 0.15106 | 0.32043 | 122.7493 | 122.9919 | 122.7539 | 123.0423 | 122.7676 | 123.1155 | 122.8271 | 122.4609 | 123.0423 | 122.7676 | 122.8271 | 122.7539 | 123.1155 | -0.51727 | -0.50354
2436.625 | 122.9324 | -122.7493 | 0.22888 | 0.0045011 | 0.02051 | 0.0035355 | 0.0059495 | -0.0054687 | -0.0089936 | 0.014947 | 0.07782 | 0.31586 | -0.29297 | 0.17853 | 0.050354 | 0.11444 | -0.013733 | 0.3067 | 0.36163 | -0.2655 | 122.4564 | 0.086975 | 122.8271 | 122.9279 | -0.17853 | 122.4838 | 0.13275 | 0.37079 | 122.7356 | 123.056 | 122.7997 | 123.0652 | 122.8271 | 123.111 | 122.8638 | 122.4838 | 123.0652 | 122.8271 | 122.8638 | 122.7997 | 123.111 | -0.52185 | -0.49438
2438.3125 | 122.9736 | -122.7631 | 0.23804 | -0.0031279 | 0.02051 | 0.0069535 | 0.0040269 | -0.0061097 | -0.0092072 | 0.017297 | 0.054932 | 0.31586 | -0.30212 | 0.1831 | 0.064087 | 0.12817 | -0.009155 | 0.34332 | 0.37079 | -0.27924 | 122.4609 | 0.07782 | 122.818 | 122.9462 | -0.17395 | 122.4838 | 0.13275 | 0.35706 | 122.7539 | 123.1064 | 122.8271 | 123.0789 | 122.818 | 123.1339 | 122.8912 | 122.4838 | 123.0789 | 122.818 | 122.8912 | 122.8271 | 123.1339 | -0.54016 | -0.51727
2440.0625 | 122.937 | -122.7493 | 0.23804 | 0.012131 | 0.020937 | 0.0093033 | 0.0050949 | -0.0065369 | -0.00643 | 0.014734 | 0.054932 | 0.29755 | -0.30212 | 0.17395 | 0.045776 | 0.11444 | 0.004578 | 0.31586 | 0.36163 | -0.27008 | 122.4472 | 0.059509 | 122.8043 | 122.9233 | -0.19226 | 122.4792 | 0.1236 | 0.35706 | 122.7539 | 123.0652 | 122.7951 | 123.0469 | 122.8043 | 123.111 | 122.8638 | 122.4792 | 123.0469 | 122.8043 | 122.8638 | 122.7951 | 123.111 | -0.54016 | -0.50812
2441.8125 | 123.0194 | -122.7036 | 0.21057 | -0.0031279 | 0.017519 | 0.0024673 | -0.0017411 | -0.0076049 | -0.0057892 | 0.013452 | 0.1236 | 0.25635 | -0.25635 | 0.23346 | 0.14191 | 0.21515 | -0.086975 | 0.43945 | 0.32959 | -0.24261 | 122.4472 | 0.045777 | 122.8271 | 122.937 | -0.068664 | 122.4609 | 0.11902 | 0.37994 | 122.6166 | 123.143 | 122.8455 | 122.9599 | 122.8271 | 123.0331 | 122.9187 | 122.4609 | 122.9599 | 122.8271 | 122.9187 | 122.8455 | 123.0331 | -0.46692 | -0.45319
2443.5156 | 123.0011 | -122.731 | 0.20599 | 0.012131 | 0.023074 | 0.0011857 | 0.0059495 | -0.0078187 | -0.0060028 | 0.015161 | 0.082397 | 0.31128 | -0.32501 | 0.17853 | 0.059509 | 0.11902 | 0.009155 | 0.34332 | 0.36163 | -0.28839 | 122.406 | 0.10528 | 122.8134 | 122.9095 | -0.14649 | 122.4426 | 0.15564 | 0.40741 | 122.7402 | 123.0743 | 122.7905 | 123.0423 | 122.8134 | 123.0927 | 122.85 | 122.4426 | 123.0423 | 122.8134 | 122.85 | 122.7905 | 123.0927 | -0.53101 | -0.49439
2445.2812 | 123.0743 | -122.7081 | 0.18768 | 0.0045011 | 0.019228 | 0.0024673 | -0.0017411 | -0.0084595 | -0.0062164 | 0.015588 | 0.059509 | 0.29297 | -0.26093 | 0.20142 | 0.11902 | 0.18768 | -0.082397 | 0.37537 | 0.33417 | -0.25635 | 122.4472 | 0.10529 | 122.7676 | 122.9095 | -0.068664 | 122.4518 | 0.14648 | 0.32043 | 122.6257 | 123.0835 | 122.8271 | 123.0011 | 122.7676 | 123.0423 | 122.8958 | 122.4518 | 123.0011 | 122.7676 | 122.8958 | 122.8271 | 123.0423 | -0.44861 | -0.44403
2447.0469 | 123.024 | -122.7264 | 0.20599 | 0.0045011 | 0.020296 | 0.0013993 | 0.00082248 | -0.010809 | -0.0060028 | 0.013665 | 0.10529 | 0.28839 | -0.26093 | 0.27008 | 0.14648 | 0.2243 | -0.10071 | 0.45319 | 0.32501 | -0.23804 | 122.4655 | 0.082397 | 122.8317 | 122.9965 | -0.05951 | 122.4884 | 0.11902 | 0.36621 | 122.6257 | 123.1796 | 122.8729 | 123.0148 | 122.8317 | 123.0515 | 122.9507 | 122.4884 | 123.0148 | 122.8317 | 122.9507 | 122.8729 | 123.0515 | -0.46692 | -0.44403
2448.75 | 123.0469 | -122.7219 | 0.19226 | 0.0045011 | 0.019869 | 0.0069535 | 0.0027451 | -0.0093139 | -0.0066438 | 0.014306 | 0.11444 | 0.28839 | -0.25177 | 0.24719 | 0.11902 | 0.19684 | -0.045776 | 0.42572 | 0.32044 | -0.24261 | 122.4701 | 0.09613 | 122.8363 | 122.9691 | -0.073242 | 122.4792 | 0.12817 | 0.36621 | 122.6761 | 123.1476 | 122.8409 | 123.0103 | 122.8363 | 123.0423 | 122.9187 | 122.4792 | 123.0103 | 122.8363 | 122.9187 | 122.8409 | 123.0423 | -0.44403 | -0.43488
2450.5 | 122.9462 | -122.7539 | 0.2243 | -0.010757 | 0.017092 | 0.0078079 | 0.0040269 | -0.0086731 | -0.0060028 | 0.015588 | 0.1236 | 0.25635 | -0.24719 | 0.24261 | 0.10529 | 0.21973 | -0.15564 | 0.39825 | 0.32044 | -0.2243 | 122.5067 | 0.032044 | 122.8775 | 122.9965 | -0.11902 | 122.5296 | 0.096131 | 0.37079 | 122.5983 | 123.1522 | 122.8592 | 123.0103 | 122.8775 | 123.0743 | 122.9736 | 122.5296 | 123.0103 | 122.8775 | 122.9736 | 122.8592 | 123.0743 | -0.4715 | -0.44861
2452.25 | 122.9599 | -122.7631 | 0.21515 | -0.0031279 | 0.021365 | 0.0043899 | 0.0018905 | -0.0065369 | -0.008139 | 0.015588 | 0.064087 | 0.29755 | -0.29755 | 0.19226 | 0.07782 | 0.16937 | -0.10986 | 0.3479 | 0.34332 | -0.25177 | 122.4655 | 0.082397 | 122.8271 | 122.9553 | -0.13733 | 122.5113 | 0.12817 | 0.36163 | 122.6532 | 123.111 | 122.8409 | 123.0606 | 122.8271 | 123.1064 | 122.9324 | 122.5113 | 123.0606 | 122.8271 | 122.9324 | 122.8409 | 123.1064 | -0.5127 | -0.46692
2454.0156 | 123.0148 | -122.7219 | 0.20142 | 0.0045011 | 0.019869 | 0.0058853 | -0.00045932 | -0.010168 | -0.0066438 | 0.013025 | 0.12817 | 0.28839 | -0.27008 | 0.24719 | 0.14648 | 0.2243 | -0.10529 | 0.44403 | 0.31586 | -0.24719 | 122.4518 | 0.086975 | 122.85 | 122.9691 | -0.054932 | 122.4747 | 0.11444 | 0.39826 | 122.6166 | 123.1659 | 122.8683 | 123.0103 | 122.85 | 123.0377 | 122.9462 | 122.4747 | 123.0103 | 122.85 | 122.9462 | 122.8683 | 123.0377 | -0.4715 | -0.44861
2455.7031 | 123.0148 | -122.731 | 0.19684 | 0.0045011 | 0.024142 | 0.0071671 | -0.0032363 | -0.0093139 | -0.004721 | 0.014947 | 0.1236 | 0.27466 | -0.27924 | 0.27924 | 0.16022 | 0.21973 | -0.13275 | 0.44861 | 0.32959 | -0.23346 | 122.4518 | 0.07782 | 122.8546 | 123.0103 | -0.036621 | 122.4976 | 0.13275 | 0.40283 | 122.5983 | 123.1796 | 122.8912 | 123.0057 | 122.8546 | 123.0606 | 122.9507 | 122.4976 | 123.0057 | 122.8546 | 122.9507 | 122.8912 | 123.0606 | -0.47607 | -0.4303
2457.4531 | 122.9462 | -122.7768 | 0.21973 | -0.0031279 | 0.025423 | 0.0037491 | 0.0033859 | -0.0069641 | -0.0092072 | 0.01452 | 0.073242 | 0.29297 | -0.29297 | 0.21057 | 0.054932 | 0.13733 | -0.022888 | 0.3479 | 0.37079 | -0.27466 | 122.4838 | 0.073242 | 122.85 | 122.9874 | -0.16479 | 122.5021 | 0.15106 | 0.36621 | 122.7539 | 123.1247 | 122.8317 | 123.0698 | 122.85 | 123.1476 | 122.9141 | 122.5021 | 123.0698 | 122.85 | 122.9141 | 122.8317 | 123.1476 | -0.5127 | -0.49439
2459.2344 | 122.9782 | -122.7676 | 0.22888 | -0.0031279 | 0.026919 | 0.0013993 | -0.00045932 | -0.0065369 | -0.007071 | 0.013879 | 0.054932 | 0.31128 | -0.3067 | 0.15106 | 0.009155 | 0.09613 | 0.009155 | 0.2655 | 0.37537 | -0.27924 | 122.4609 | 0.082397 | 122.8226 | 122.9187 | -0.21973 | 122.4884 | 0.14648 | 0.36163 | 122.7768 | 123.0331 | 122.7768 | 123.0789 | 122.8226 | 123.143 | 122.8638 | 122.4884 | 123.0789 | 122.8226 | 122.8638 | 122.7768 | 123.143 | -0.53558 | -0.50812
2460.9219 | 123.0377 | -122.7493 | 0.20599 | 0.0045011 | 0.029055 | 0.0022537 | -0.0011001 | -0.0048279 | -0.0074982 | 0.01452 | 0.064087 | 0.31128 | -0.30212 | 0.19226 | 0.059509 | 0.12817 | 0.013733 | 0.32959 | 0.36621 | -0.27008 | 122.4472 | 0.10528 | 122.8134 | 122.9416 | -0.14649 | 122.4792 | 0.16022 | 0.36621 | 122.7631 | 123.0789 | 122.8088 | 123.0606 | 122.8134 | 123.1155 | 122.8775 | 122.4792 | 123.0606 | 122.8134 | 122.8775 | 122.8088 | 123.1155 | -0.50812 | -0.47608

## Thermal Data
Fire Time | B Position - Conduit - 3' | B Position - Conduit - Middle | B Position - Conduit - 7'
-0.5271 | 11.6684 | 11.7016 | 11.6881
0.4729 | 11.6674 | 11.7078 | 11.695
1.4729 | 11.6623 | 11.707 | 11.694
2.4729 | 11.6672 | 11.7067 | 11.692
3.4729 | 11.6672 | 11.7052 | 11.6977
4.4729 | 11.667 | 11.7093 | 11.6941
5.4729 | 11.6706 | 11.7155 | 11.6912
6.4729 | 11.6682 | 11.7078 | 11.6932
7.4729 | 11.6721 | 11.712 | 11.6942
8.4729 | 11.6672 | 11.704 | 11.7015
9.4729 | 11.683 | 11.724 | 11.7096
10.4729 | 11.6871 | 11.9308 | 11.73
11.4729 | 11.7979 | 12.4178 | 11.8907
12.4729 | 12.0759 | 12.2346 | 11.9
13.4729 | 12.1563 | 12.5211 | 12.0341
14.4729 | 12.2707 | 12.6722 | 12.1085
15.4729 | 12.2544 | 12.954 | 12.1314
16.4729 | 12.3131 | 12.8368 | 12.2567
17.4729 | 12.3007 | 13.2633 | 12.4261
18.4729 | 12.3537 | 13.1859 | 12.4594
19.4729 | 12.6478 | 13.727 | 12.5889
20.4885 | 12.5689 | 13.8863 | 12.6218
21.4885 | 12.8853 | 14.1987 | 12.6604
22.4729 | 12.9882 | 14.6848 | 12.7238
23.4729 | 12.9194 | 14.9238 | 12.9646
24.4729 | 13.0526 | 15.2028 | 12.856
25.4729 | 13.2223 | 15.1665 | 12.9709
26.4729 | 13.3266 | 15.5653 | 13.3126
27.4729 | 13.3463 | 16.0862 | 13.2488
28.4729 | 13.3835 | 16.1947 | 13.3848
29.4729 | 13.4213 | 16.2491 | 13.4145
30.4729 | 13.5185 | 16.5926 | 13.4554
31.4729 | 13.6191 | 16.8811 | 13.7902
32.4729 | 13.6862 | 17.3307 | 13.8228
33.4729 | 13.6058 | 17.4797 | 13.9364
34.4729 | 13.5558 | 17.6241 | 14.1342
35.4729 | 13.6036 | 18.1883 | 14.4434
36.4729 | 13.7569 | 18.604 | 14.4165
37.4729 | 13.8061 | 19.4886 | 14.6915
38.4729 | 13.9817 | 19.2281 | 14.7285
39.4729 | 14.187 | 19.9151 | 14.8204
40.4729 | 14.3184 | 20.0061 | 14.9692
41.4729 | 14.5646 | 20.7938 | 15.1187
42.4729 | 14.6915 | 21.4227 | 15.3384
43.4729 | 14.7944 | 21.6433 | 15.4408
44.4729 | 14.754 | 22.1456 | 15.5227
45.4729 | 15.0113 | 22.4565 | 15.7518
46.4729 | 15.0471 | 22.884 | 15.9397
47.4729 | 15.082 | 23.7886 | 16.1313
48.4729 | 15.4804 | 24.6505 | 16.1622
49.4729 | 15.5282 | 25.8992 | 16.5661
50.4729 | 15.6811 | 26.5927 | 16.566
51.4729 | 15.5944 | 26.6485 | 16.6737
52.4729 | 16.0646 | 27.8342 | 16.8823
53.4729 | 16.0402 | 28.7437 | 16.8988
54.4729 | 16.086 | 28.7156 | 17.1418
55.4729 | 16.0514 | 29.3849 | 17.2937
56.4729 | 16.5607 | 30.4555 | 17.2541
57.4729 | 16.4589 | 30.42 | 17.6134
58.4729 | 16.5277 | 30.5103 | 17.8703
59.4729 | 16.7424 | 31.1275 | 17.9774
60.4729 | 16.8408 | 31.9408 | 18.1528
61.4729 | 16.9328 | 32.2179 | 18.1354
62.4729 | 16.9178 | 32.8251 | 18.7233
63.4729 | 16.925 | 33.838 | 18.7155
64.4729 | 17.0779 | 34.1753 | 18.8327
65.4729 | 17.3617 | 35.3592 | 18.8948
66.4729 | 17.9087 | 36.9598 | 19.1421
67.4729 | 17.9568 | 37.9601 | 19.3039
68.4729 | 18.2872 | 37.5786 | 19.323
69.4729 | 18.4631 | 37.6569 | 19.4492
70.4729 | 18.76 | 38.4353 | 19.5862
71.4729 | 18.8115 | 38.8979 | 19.5805
72.4729 | 18.8461 | 39.6225 | 19.9517
73.4729 | 19.2327 | 39.6529 | 20.0647
74.4729 | 19.3305 | 40.1917 | 20.1304
75.4729 | 19.8038 | 40.8299 | 20.3111
76.4729 | 19.7749 | 41.9511 | 20.579
77.4729 | 19.8804 | 42.6735 | 20.5544
78.4729 | 20.0919 | 42.6079 | 20.7045
79.4729 | 20.1936 | 43.1782 | 20.8286
80.4729 | 20.3328 | 43.1518 | 20.9273
81.4729 | 20.5833 | 43.6386 | 21.0191
82.4729 | 20.8402 | 44.0741 | 21.246
83.4729 | 21.1581 | 45.4689 | 21.3569
84.4729 | 21.4773 | 45.6883 | 21.4987
85.4729 | 21.5854 | 46.1167 | 21.612
86.4729 | 21.7049 | 46.7758 | 21.656
87.4729 | 21.9122 | 47.7933 | 21.8617
88.4729 | 21.7969 | 48.2977 | 22.0082
89.4729 | 21.9977 | 48.4537 | 22.2126
90.4729 | 21.9586 | 49.1444 | 22.4288
91.4729 | 22.0413 | 49.274 | 22.3926
92.4729 | 22.6323 | 49.8471 | 22.4929
93.4729 | 22.8857 | 49.979 | 22.6358
94.4729 | 22.8276 | 51.0239 | 22.7609
95.4729 | 23.0877 | 51.6559 | 22.8258
96.4729 | 23.0788 | 52.7712 | 22.9592
97.4729 | 23.3657 | 52.1374 | 23.21
98.4729 | 23.5923 | 52.9457 | 23.1428
99.4729 | 23.9301 | 53.3121 | 23.3439
100.4729 | 23.8514 | 54.0827 | 23.4747
101.4729 | 23.8034 | 54.2782 | 23.6962
102.4729 | 23.8408 | 54.8728 | 23.8131
103.4729 | 24.121 | 55.5555 | 23.9158
104.4729 | 24.4441 | 56.2853 | 24.075
105.4729 | 24.6932 | 56.1652 | 24.0642
106.4729 | 24.9021 | 56.784 | 24.1723
107.4729 | 24.7196 | 57.0486 | 24.4431
108.4729 | 25.0032 | 57.9416 | 24.51
109.4729 | 24.85 | 59.2135 | 24.6887
110.4885 | 25.0502 | 59.0757 | 24.8439
111.4729 | 25.2148 | 59.9063 | 24.9236
112.4729 | 25.2929 | 60.3195 | 25.0409
113.4729 | 25.6411 | 60.8411 | 25.0763
114.4729 | 25.5164 | 60.8793 | 25.3273
115.4729 | 25.6019 | 61.5381 | 25.6127
116.4729 | 25.8598 | 62.1232 | 25.5876
117.4729 | 26.3844 | 62.7252 | 25.6809
118.4729 | 26.3164 | 63.861 | 25.8509
119.4729 | 26.2358 | 63.9454 | 26.0875
120.4729 | 26.3507 | 64.5989 | 26.3497
121.4729 | 26.545 | 65.4956 | 26.3634
122.4729 | 27.0787 | 65.5932 | 26.5218
123.4729 | 27.2444 | 66.0418 | 26.5718
124.4729 | 27.5285 | 66.8468 | 26.7439
125.4729 | 27.726 | 67.244 | 26.9156
126.4729 | 27.8555 | 67.3182 | 27.2528
127.4729 | 27.9073 | 68.81 | 27.2085
128.4729 | 28.0656 | 68.8001 | 27.4728
129.4729 | 28.1077 | 69.2228 | 27.5939
130.4729 | 28.4307 | 70.7656 | 27.7225
131.4729 | 28.5123 | 71.0494 | 27.7205
132.4729 | 28.9045 | 71.8539 | 28.0604
133.4729 | 29.124 | 71.797 | 28.1275
134.4729 | 29.1858 | 72.9003 | 28.3397
135.4729 | 29.096 | 73.5202 | 28.4471
136.4729 | 29.3749 | 74.2563 | 28.7176
137.4729 | 29.5786 | 74.2892 | 28.7953
138.4729 | 29.6959 | 75.0821 | 29.1139
139.4729 | 29.946 | 76.0037 | 29.1107
140.4729 | 30.1285 | 76.8493 | 29.353
141.4729 | 30.1043 | 77.275 | 29.4664
142.4729 | 30.3449 | 78.0776 | 29.6665
143.4729 | 30.3003 | 79.1939 | 29.923
144.4729 | 30.585 | 79.483 | 30.1006
145.4729 | 31.027 | 80.1164 | 30.3096
146.4729 | 31.5914 | 80.9087 | 30.337
147.4729 | 31.3888 | 81.5413 | 30.5742
148.4729 | 31.3966 | 82.4956 | 30.7372
149.4729 | 31.3323 | 82.8634 | 30.8357
150.4729 | 31.417 | 84.2071 | 31.1446
151.4729 | 31.5863 | 84.5679 | 31.3434
152.4729 | 32.0139 | 85.0817 | 31.5192
153.4729 | 32.5261 | 85.664 | 31.6158
154.4729 | 32.7526 | 86.8303 | 31.7813
155.4729 | 32.859 | 87.5557 | 32.0277
156.4729 | 33.019 | 88.0652 | 32.3056
157.4729 | 32.9827 | 88.7634 | 32.3856
158.4729 | 33.2514 | 89.5071 | 32.6572
159.4729 | 33.3274 | 90.2754 | 32.7859
160.4729 | 33.7718 | 91.2252 | 33.0073
161.4729 | 33.8426 | 91.9867 | 33.206
162.4729 | 34.2126 | 92.5988 | 33.4551
163.4729 | 34.2181 | 93.8632 | 33.4801
164.4729 | 34.2914 | 93.8743 | 33.7658
165.4729 | 34.3025 | 94.4872 | 33.9505
166.4729 | 34.5728 | 96.3329 | 34.2354
167.4729 | 35.0692 | 96.9723 | 34.2682
168.4729 | 35.3843 | 97.3862 | 34.5274
169.4729 | 35.4942 | 97.7541 | 34.597
170.4885 | 25.5966 | 27.3443 | 26.5137
171.4729 | 25.6151 | 25.9354 | 26.315
172.4729 | 26.3104 | 27.7065 | 27.0415
173.4729 | 36.4524 | 101.0823 | 35.2044
174.4729 | 36.2474 | 102.4099 | 35.7651
175.4729 | 36.5124 | 102.4406 | 35.8002
176.4729 | 37.1279 | 103.4906 | 35.971
177.4729 | 37.1933 | 104.6437 | 36.1512
178.4729 | 37.6792 | 105.5506 | 36.2909
179.4729 | 37.7587 | 106.8935 | 36.5244
180.4729 | 37.8114 | 108.274 | 36.9756
181.4729 | 38.4322 | 108.0329 | 36.9054
182.4729 | 39.0309 | 108.922 | 37.2777
183.4729 | 39.1477 | 110.0801 | 37.8538
184.4729 | 39.3119 | 110.7522 | 37.7086
185.4729 | 39.3957 | 112.1937 | 37.7429
186.4729 | 39.4188 | 112.7138 | 38.0665
187.4729 | 39.3251 | 113.8668 | 38.1745
188.4729 | 39.4096 | 114.37 | 38.2874
189.4729 | 39.6436 | 115.3439 | 38.6111
190.4729 | 40.0045 | 115.8712 | 38.735
191.4729 | 40.3383 | 116.5134 | 38.9543
192.4729 | 40.622 | 117.3637 | 39.0452
193.4729 | 40.7084 | 119.3682 | 39.398
194.4729 | 41.0967 | 119.9508 | 39.584
195.4729 | 41.3672 | 120.6786 | 39.8807
196.4729 | 41.2865 | 121.8369 | 40.0121
197.4729 | 41.561 | 122.8611 | 40.3355
198.4729 | 41.7862 | 123.7167 | 40.3919
199.4729 | 42.2392 | 123.581 | 40.7181
200.4729 | 42.5426 | 124.7565 | 40.7497
201.4729 | 42.7327 | 124.8752 | 40.9472
202.4729 | 42.8544 | 126.8128 | 41.1222
203.4729 | 43.3711 | 128.2311 | 41.344
204.4729 | 43.3493 | 128.5504 | 41.5507
205.4729 | 43.3862 | 129.3151 | 41.6249
206.4729 | 43.5792 | 130.5034 | 42.0316
207.4729 | 43.8762 | 131.7988 | 42.3896
208.4729 | 44.0126 | 133.6504 | 42.559
209.4729 | 43.8969 | 133.7904 | 42.8119
210.4729 | 43.915 | 134.9638 | 43.0663
211.4729 | 44.5211 | 136.6849 | 43.1245
212.4729 | 44.8992 | 136.0604 | 43.387
213.4729 | 45.1317 | 138.4815 | 43.4942
214.4729 | 45.2591 | 139.2797 | 43.8072
215.4729 | 45.6963 | 140.0007 | 43.8981
216.4729 | 45.8089 | 140.489 | 44.1082
217.4729 | 46.1934 | 141.3259 | 44.3964
218.4729 | 46.0725 | 142.8952 | 44.4856
219.4729 | 46.4717 | 143.075 | 44.6277
220.4729 | 46.6581 | 143.9689 | 44.7753
221.4729 | 47.2482 | 145.7121 | 44.9857
222.4729 | 46.9418 | 145.9057 | 45.3063
223.4729 | 47.7131 | 147.1273 | 45.7221
224.4729 | 47.7668 | 148.1163 | 45.6204
225.4729 | 48.0193 | 148.3665 | 46.0569
226.4729 | 47.9855 | 149.7932 | 46.1204
227.4729 | 48.2362 | 151.6639 | 46.2972
228.4729 | 48.2495 | 152.198 | 46.485
229.4729 | 48.6475 | 153.2828 | 46.6373
230.4729 | 48.346 | 154.7859 | 47.0153
231.4729 | 49.0615 | 155.2987 | 47.2237
232.4729 | 49.2698 | 155.8176 | 47.3775
233.4729 | 49.3967 | 157.1766 | 47.5005
234.4729 | 50.2025 | 158.7288 | 47.8112
235.4729 | 50.0905 | 160.3123 | 48.1946
236.4729 | 50.1056 | 161.6234 | 48.4536
237.4729 | 50.2982 | 162.1616 | 48.4503
238.4729 | 50.6225 | 162.951 | 48.8778
239.4729 | 50.894 | 165.0301 | 49.0751
240.4729 | 51.0617 | 166.5626 | 49.5996
241.4729 | 50.915 | 166.8681 | 49.6553
242.4729 | 51.3521 | 168.4948 | 49.7799
243.4729 | 51.6588 | 169.6158 | 50.3304
244.4729 | 51.9255 | 170.7167 | 50.4644
245.4729 | 52.0159 | 171.2328 | 50.5405
246.4729 | 52.2677 | 172.8789 | 50.8835
247.4729 | 52.3487 | 174.383 | 51.0781
248.4729 | 52.4841 | 174.7146 | 51.3384
249.4729 | 53.0464 | 176.264 | 51.5357
250.4729 | 53.3094 | 177.0078 | 51.7221
251.4729 | 53.8841 | 178.3542 | 51.9028
252.4729 | 54.2802 | 178.8687 | 52.0227
253.4729 | 54.2924 | 180.4429 | 52.5222
254.4729 | 54.5889 | 181.1461 | 52.5709
255.4729 | 54.914 | 182.8393 | 52.9371
256.4729 | 55.1117 | 184.1762 | 53.1715
257.4729 | 55.0419 | 185.1027 | 53.3958
258.4729 | 55.102 | 185.7 | 53.6147
259.4729 | 55.4764 | 187.8835 | 53.9112
260.4729 | 55.8874 | 189.2304 | 54.074
261.4729 | 56.4942 | 190.9799 | 54.5846
262.4729 | 56.5501 | 192.0042 | 54.7591
263.4729 | 57.2321 | 193.1413 | 54.8478
264.4729 | 57.1334 | 194.2164 | 55.0404
265.4729 | 57.9704 | 194.895 | 55.2596
266.4729 | 58.0948 | 195.2792 | 55.4736
267.4729 | 58.2035 | 195.5942 | 55.7114
268.4729 | 58.4126 | 196.8955 | 56.0023
269.4729 | 58.8396 | 200.314 | 56.4698
270.4729 | 58.9282 | 202.1982 | 56.69
271.4729 | 58.7766 | 201.8431 | 56.9885
272.4729 | 58.7472 | 202.29 | 57.3016
273.4729 | 59.2881 | 202.6766 | 57.5457
274.4729 | 59.5032 | 203.5573 | 57.5322
275.4729 | 59.9202 | 205.0241 | 57.8632
276.4729 | 60.0307 | 205.5773 | 58.1195
277.4729 | 60.5139 | 205.9011 | 58.1636
278.4729 | 61.2113 | 206.9755 | 58.5079
279.4729 | 61.389 | 207.5535 | 58.7921
280.4729 | 61.6677 | 210.2806 | 59.1816
281.4729 | 61.929 | 210.1342 | 59.2312
282.4729 | 62.0964 | 211.4957 | 59.4169
283.4729 | 62.5411 | 212.4684 | 59.8643
284.4729 | 62.6589 | 213.5398 | 60.1634
285.4729 | 62.815 | 213.9527 | 60.3756
286.4729 | 62.8821 | 216.2165 | 60.6368
287.4729 | 63.0835 | 217.6441 | 60.9026
288.4729 | 63.2519 | 219.0645 | 61.1188
289.4729 | 63.5798 | 218.9981 | 61.5384
290.4885 | 63.8432 | 220.2793 | 61.8758
291.4729 | 64.3068 | 222.2179 | 62.0298
292.4729 | 64.6056 | 223.1014 | 62.3427
293.4729 | 64.7724 | 222.9765 | 62.3501
294.4729 | 64.8911 | 224.1534 | 62.7446
295.4729 | 65.0783 | 225.6772 | 63.2
296.4729 | 66.2298 | 226.7152 | 63.3512
297.4729 | 66.2818 | 226.9305 | 63.8806
298.4729 | 66.0586 | 228.7294 | 64.0361
299.4729 | 66.2898 | 229.1383 | 64.2732
300.4729 | 66.6193 | 230.8978 | 64.674
301.4729 | 66.8601 | 231.2261 | 64.8551
302.4729 | 66.8383 | 232.0334 | 64.8311
303.4729 | 67.2254 | 232.7103 | 65.1606
304.4729 | 67.6749 | 233.3717 | 65.4094
305.4729 | 68.1959 | 234.3683 | 65.7693
306.4729 | 68.3179 | 235.0639 | 65.9439
307.4729 | 68.5145 | 235.4279 | 66.1855
308.4729 | 69.0015 | 236.2734 | 66.494
309.4729 | 69.0243 | 237.2475 | 66.8701
310.4729 | 69.1885 | 237.7798 | 67.0333
311.4729 | 69.5026 | 239.3095 | 67.4789
312.4729 | 70.1201 | 240.0366 | 67.8442
313.4729 | 70.1999 | 240.6587 | 68.0418
314.4729 | 70.4686 | 242.1338 | 68.4127
315.4729 | 70.5271 | 242.5946 | 68.5871
316.4729 | 70.5856 | 242.6895 | 69.0477
317.4729 | 70.8385 | 243.4279 | 69.452
318.4729 | 71.6678 | 244.2708 | 69.5206
319.4729 | 72.149 | 245.084 | 69.9085
320.4729 | 72.0639 | 246.5104 | 70.3566
321.4729 | 72.1806 | 247.052 | 70.4711
322.4729 | 72.9856 | 248.5464 | 70.8238
323.4729 | 73.0202 | 250.5396 | 71.1039
324.4729 | 73.1278 | 252.2791 | 71.5319
325.4729 | 73.175 | 253.3361 | 71.8079
326.4729 | 73.3125 | 253.835 | 72.1672
327.4729 | 73.4449 | 254.0846 | 72.3642
328.4729 | 73.9633 | 255.5337 | 72.7284
329.4729 | 73.8743 | 256.4393 | 73.1457
330.4729 | 74.4771 | 256.2701 | 73.2414
331.4729 | 74.8449 | 255.9214 | 73.5635
332.4729 | 74.9567 | 257.1038 | 73.6062
333.4729 | 75.6455 | 257.5897 | 74.2339
334.4729 | 75.9213 | 258.294 | 74.6097
335.4729 | 76.161 | 259.296 | 74.7587
336.4729 | 76.3099 | 259.6501 | 75.0988
337.4729 | 76.3645 | 260.1865 | 75.3432
338.4729 | 76.4263 | 260.5425 | 75.8493
339.4729 | 76.7211 | 261.5251 | 76.1712
340.4729 | 77.4411 | 262.3473 | 76.2699
341.4729 | 77.9216 | 265.2751 | 76.6006
342.4729 | 77.9881 | 265.3085 | 77.0529
343.4729 | 78.2964 | 265.7621 | 77.48
344.4729 | 78.7452 | 266.683 | 77.71
345.4729 | 79.0579 | 267.4233 | 77.8846
346.4729 | 79.2104 | 267.7774 | 78.1784
347.4729 | 79.1444 | 269.2697 | 78.5412
348.4729 | 79.2818 | 269.5638 | 79.0467
349.4729 | 79.591 | 270.0103 | 79.487
350.4885 | 80.2738 | 270.8315 | 79.6607
351.4729 | 80.3107 | 270.844 | 79.9881
352.4729 | 81.1126 | 271.4212 | 80.1331
353.4729 | 81.6161 | 272.7109 | 80.5964
354.4729 | 81.9375 | 273.7462 | 81.1953
355.4729 | 81.9002 | 274.4514 | 81.3834
356.4729 | 81.8002 | 274.6981 | 81.6973
357.4729 | 82.024 | 275.9102 | 82.0232
358.4729 | 82.1261 | 277.636 | 82.0937
359.4729 | 82.4867 | 277.3685 | 82.3579
360.4729 | 82.6783 | 278.1994 | 82.9028
361.4729 | 83.2522 | 279.4504 | 83.3723
362.4729 | 83.8127 | 279.2655 | 83.658
363.4729 | 84.2968 | 280.2942 | 83.7358
364.4729 | 84.5287 | 281.7645 | 84.227
365.4729 | 84.5873 | 282.964 | 84.4755
366.4729 | 85.1678 | 284.5992 | 84.6072
367.4729 | 85.1549 | 284.5326 | 84.941
368.4729 | 85.672 | 286.2632 | 85.2873
369.4729 | 85.7364 | 287.9254 | 86.083
370.4729 | 85.8671 | 288.6447 | 86.5238
371.4729 | 85.7913 | 288.3838 | 86.8564
372.4729 | 86.1083 | 289.1218 | 86.9396
373.4729 | 86.8419 | 291.2307 | 87.2344
374.4729 | 87.3421 | 292.132 | 87.7475
375.4729 | 87.2087 | 293.0385 | 88.5846
376.4729 | 87.643 | 293.1325 | 88.6312
377.4729 | 87.9522 | 294.664 | 88.8478
378.4729 | 88.1558 | 294.6104 | 89.4244
379.4729 | 88.8728 | 295.6054 | 90.0902
380.4729 | 88.9112 | 296.967 | 90.0092
381.4729 | 89.3194 | 298.7733 | 90.4984
382.4729 | 89.5194 | 299.2964 | 91.0869
383.4729 | 89.6869 | 299.9957 | 91.3608
384.4729 | 89.7352 | 299.8819 | 91.8137
385.4729 | 90.022 | 301.4722 | 92.1237
386.4729 | 90.286 | 302.5773 | 92.744
387.4729 | 90.6991 | 302.6999 | 92.8926
388.4729 | 91.5256 | 303.0978 | 93.2357
389.4729 | 91.8413 | 303.1648 | 93.5405
390.4729 | 91.7805 | 304.3118 | 93.779
391.4729 | 92.5486 | 305.1063 | 94.0131
392.4729 | 93.144 | 305.813 | 94.4829
393.4729 | 93.1585 | 306.6475 | 94.8671
394.4729 | 93.1829 | 306.9109 | 95.2684
395.4729 | 93.318 | 309.0853 | 95.5703
396.4729 | 94.0499 | 309.5761 | 95.9668
397.4729 | 93.8057 | 309.5495 | 96.3749
398.4729 | 94.4596 | 309.646 | 96.6782
399.4729 | 94.7802 | 310.8455 | 97.0778
400.4729 | 94.9045 | 311.7202 | 97.4159
401.4729 | 95.1525 | 312.5751 | 97.7931
402.4729 | 95.4361 | 313.284 | 98.4969
403.4729 | 95.7312 | 314.0754 | 99.0189
404.4729 | 96.4446 | 315.2629 | 99.2061
405.4729 | 96.3293 | 315.1722 | 99.6043
406.4729 | 96.7166 | 316.4337 | 99.8165
407.4729 | 96.7797 | 316.9001 | 100.317
408.4729 | 96.8826 | 317.5266 | 100.9952
409.4729 | 97.2025 | 318.1035 | 101.3636
410.4885 | 97.4701 | 318.78 | 101.9976
411.4729 | 97.9518 | 319.7755 | 102.1818
412.4729 | 98.7147 | 319.9583 | 102.716
413.4729 | 98.7331 | 320.986 | 103.3428
414.4729 | 98.7713 | 321.0574 | 103.8022
415.4729 | 99.4993 | 322.2922 | 104.1388
416.4729 | 99.9146 | 322.7669 | 104.8649
417.4729 | 99.8502 | 322.4153 | 105.1293
418.4729 | 99.8968 | 323.1785 | 105.5206
419.4729 | 100.5789 | 324.0909 | 106.0773
420.4729 | 101.0165 | 325.2634 | 106.6307
421.4729 | 100.9559 | 324.6037 | 106.81
422.4729 | 101.7993 | 324.8927 | 107.3825
423.4729 | 102.5733 | 326.003 | 108.0853
424.4729 | 103.1111 | 326.4791 | 108.4409
425.4729 | 102.997 | 326.5172 | 108.4439
426.4729 | 102.5785 | 327.1873 | 108.9094
427.4729 | 103.0712 | 327.3312 | 109.0352
428.4729 | 103.6591 | 327.3298 | 109.4935
429.4729 | 103.9623 | 328.6235 | 109.7912
430.4729 | 104.1798 | 329.8022 | 110.1257
431.4729 | 104.3805 | 329.7137 | 110.7207
432.4729 | 105.1403 | 330.8539 | 111.1467
433.4729 | 105.4052 | 331.4542 | 111.7698
434.4729 | 105.222 | 332.3005 | 112.7314
435.4729 | 105.7896 | 332.6402 | 112.8408
436.4729 | 106.2397 | 333.1842 | 113.2977
437.4729 | 106.1929 | 334.038 | 113.4115
438.4729 | 106.7972 | 333.792 | 113.7898
439.4729 | 107.1843 | 335.2837 | 114.6035
440.4729 | 107.7702 | 337.289 | 115.1836
441.4729 | 107.7809 | 337.5257 | 115.6237
442.4729 | 108.2649 | 336.8017 | 116.0821
443.4729 | 108.8265 | 337.8945 | 116.601
444.4729 | 108.7484 | 338.5325 | 117.1409
445.4729 | 108.7146 | 338.0834 | 117.3906
446.4729 | 109.4837 | 339.6102 | 117.9562
447.4729 | 109.8215 | 338.8589 | 118.4582
448.4729 | 110.644 | 339.5978 | 119.1501
449.4729 | 110.368 | 340.2376 | 119.3776
450.4729 | 110.4558 | 340.5024 | 119.881
451.4729 | 111.039 | 340.9438 | 120.019
452.4729 | 111.6352 | 342.139 | 120.9015
453.4729 | 111.846 | 343.1335 | 121.3653
454.4729 | 111.8357 | 342.7697 | 121.9477
455.4729 | 112.2832 | 343.2933 | 122.405
456.4729 | 112.6043 | 343.7487 | 122.7687
457.4729 | 113.0232 | 344.1415 | 123.0108
458.4729 | 113.6394 | 344.8517 | 123.5471
459.4729 | 113.8057 | 344.9692 | 124.093
460.4729 | 113.8843 | 345.4207 | 124.3989
461.4729 | 114.2193 | 345.379 | 124.8741
462.4729 | 114.5143 | 346.9227 | 125.0512
463.4729 | 114.8056 | 347.151 | 125.9035
464.4729 | 114.9675 | 347.2383 | 126.4245
465.4729 | 115.2967 | 348.8608 | 126.8604
466.4729 | 115.4412 | 348.0903 | 127.5346
467.4729 | 115.8117 | 348.6203 | 128.0535
468.4729 | 116.2308 | 348.8856 | 128.4534
469.4729 | 116.4872 | 349.4146 | 128.7195
470.4729 | 116.8882 | 349.785 | 129.1159
471.4729 | 117.444 | 351.1345 | 129.6438
472.4729 | 117.8437 | 351.8627 | 130.5051
473.4729 | 118.1403 | 351.3728 | 130.6928
474.4729 | 118.3983 | 352.2644 | 131.4502
475.4729 | 118.5048 | 352.6707 | 131.6057
476.4729 | 118.8769 | 352.9158 | 132.4583
477.4729 | 118.9338 | 354.0152 | 133.4084
478.4729 | 119.1276 | 354.302 | 133.753
479.4729 | 119.3123 | 354.8591 | 134.3086
480.4729 | 119.7349 | 355.6521 | 134.7425
481.4729 | 119.9267 | 355.9315 | 135.2619
482.4729 | 120.3242 | 355.8166 | 136.0172
483.4729 | 120.7 | 357.4618 | 136.4813
484.4729 | 120.8009 | 357.5495 | 136.957
485.4729 | 121.0044 | 358.4546 | 137.4197
486.4729 | 121.6228 | 360.4032 | 137.8315
487.4729 | 122.1558 | 360.2031 | 138.2835
488.4729 | 121.9655 | 360.6233 | 138.6957
489.4729 | 122.2774 | 361.68 | 139.3249
490.4729 | 122.4709 | 361.616 | 139.529
491.4729 | 122.7661 | 361.9862 | 140.2247
492.4729 | 122.9421 | 362.5914 | 140.5689
493.4729 | 123.5673 | 364.1962 | 141.2448
494.4729 | 123.8569 | 363.7533 | 141.6822
495.4729 | 124.0131 | 364.5161 | 142.2012
496.4729 | 124.3804 | 364.5882 | 142.6022
497.4729 | 124.8468 | 364.8024 | 143.0092
498.4729 | 125.3263 | 365.3403 | 143.5687
499.4729 | 125.485 | 365.0688 | 143.863
500.4729 | 125.6833 | 366.1672 | 144.3942
501.4729 | 126.1194 | 366.0596 | 145.0318
502.4729 | 126.9073 | 366.5551 | 145.5281
503.4729 | 127.2691 | 366.3895 | 146.0749
504.4729 | 127.3593 | 366.9104 | 146.5012
505.4729 | 127.686 | 366.9805 | 147.007
506.4729 | 127.8572 | 367.3881 | 147.4736
507.4885 | 127.9827 | 368.0058 | 147.9751
508.4729 | 128.5965 | 367.9245 | 148.5317
509.4729 | 128.9315 | 368.6727 | 148.9486
510.4729 | 129.2766 | 368.6766 | 149.3433
511.4729 | 129.3191 | 368.9561 | 149.743
512.4729 | 129.6665 | 369.8426 | 150.3588
513.4729 | 130.3955 | 369.6938 | 150.399
514.4729 | 130.3863 | 370.9774 | 150.9172
515.4729 | 130.9326 | 371.095 | 151.235
516.4729 | 131.1099 | 370.8163 | 152.1539
517.4729 | 131.3956 | 371.0258 | 152.3928
518.4729 | 131.6829 | 371.3737 | 152.9588
519.4729 | 131.8339 | 372.1566 | 153.2381
520.4729 | 131.8607 | 371.9163 | 153.6612
521.4729 | 132.1092 | 372.3319 | 154.27
522.4729 | 132.3925 | 372.4661 | 154.403
523.4729 | 132.5047 | 372.4431 | 154.9366
524.4729 | 132.6634 | 372.8417 | 155.4501
525.4729 | 133.1802 | 373.442 | 155.9626
526.4729 | 133.3017 | 373.8029 | 156.5801
527.4729 | 134.0852 | 373.6741 | 156.8873
528.4729 | 134.4958 | 374.2799 | 157.3531
529.4729 | 134.5441 | 374.7808 | 157.7198
530.4885 | 134.6856 | 375.2925 | 158.5633
531.4729 | 135.1796 | 375.4884 | 158.7358
532.4729 | 135.4787 | 375.3234 | 159.2342
533.4729 | 135.6117 | 375.5532 | 159.6216
534.4729 | 135.8766 | 375.7836 | 159.9284
535.4729 | 136.0252 | 376.4427 | 160.4583
536.4729 | 136.4479 | 376.9262 | 160.8175
537.4729 | 137.0671 | 377.2581 | 161.341
538.4729 | 137.1442 | 377.5042 | 162.0428
539.4729 | 137.3088 | 377.3982 | 162.1323
540.4729 | 137.4752 | 377.564 | 162.698
541.4729 | 138.0909 | 378.0592 | 163.2013
542.4729 | 138.3102 | 378.2798 | 163.3629
543.4729 | 138.3446 | 378.7765 | 163.9521
544.4729 | 138.7376 | 378.9508 | 164.5699
545.4729 | 138.567 | 379.1144 | 164.5897
546.4729 | 138.7988 | 379.2277 | 165.1651
547.4729 | 139.1432 | 379.4264 | 165.6071
548.4729 | 139.1994 | 380.4738 | 166.1781
549.4729 | 139.3639 | 380.5324 | 166.6038
550.4729 | 139.7194 | 380.8123 | 167.0998
551.4729 | 140.0821 | 381.5962 | 167.6061
552.4729 | 140.3597 | 381.7608 | 167.7919
553.4729 | 140.9449 | 381.8489 | 168.5158
554.4729 | 141.4349 | 382.1057 | 169.1603
555.4729 | 141.5782 | 383.028 | 169.5265
556.4729 | 141.7761 | 382.5686 | 169.9479
557.4729 | 142.1367 | 383.2078 | 170.1961
558.4729 | 142.3512 | 382.9983 | 170.5043
559.4729 | 142.5319 | 383.0129 | 170.6689
560.4729 | 142.793 | 383.415 | 171.218
561.4729 | 142.8449 | 383.4029 | 171.8372
562.4729 | 143.0146 | 383.5448 | 172.0942
563.4729 | 143.042 | 383.9594 | 172.6516
564.4729 | 143.4405 | 384.2376 | 173.1783
565.4729 | 143.6813 | 384.2758 | 173.5925
566.4729 | 143.9152 | 384.253 | 173.7159
567.4729 | 144.3403 | 384.4773 | 174.3947
568.4729 | 144.6732 | 384.7809 | 174.7197
569.4729 | 144.6294 | 384.8975 | 175.4044
570.4729 | 144.9672 | 385.5407 | 175.7335
571.4729 | 145.5003 | 385.3062 | 176.0004
572.4729 | 145.8158 | 385.547 | 176.4674
573.4729 | 146.1574 | 385.8054 | 176.8044
574.4729 | 146.3395 | 385.7529 | 177.4024
575.4729 | 146.6169 | 386.004 | 177.9219
576.4729 | 146.6862 | 386.1826 | 178.0572
577.4729 | 146.918 | 386.565 | 178.4832
578.4729 | 147.3526 | 386.6078 | 179.1754
579.4729 | 147.6567 | 387.0507 | 179.644
580.4729 | 147.7309 | 387.0024 | 179.9298
581.4729 | 148.2414 | 387.2497 | 180.2326
582.4729 | 148.2539 | 387.5842 | 180.9034
583.4729 | 148.4597 | 387.7136 | 181.2423
584.4729 | 148.8049 | 387.7879 | 181.6871
585.4729 | 148.9076 | 388.2136 | 182.3839
586.4729 | 149.1865 | 387.9008 | 182.5107
587.4729 | 149.0916 | 388.0663 | 182.8421
588.4729 | 149.4194 | 388.4824 | 183.147
589.4729 | 149.7565 | 389.6135 | 183.5689
590.4729 | 150.0151 | 390.0337 | 184.2324
591.4729 | 150.3335 | 389.6196 | 184.7388
592.4729 | 150.7824 | 389.6434 | 184.7395
593.4729 | 150.9873 | 389.5731 | 185.2878
594.4729 | 151.1977 | 389.8141 | 185.7879
595.4729 | 151.3926 | 389.6438 | 186.1025
596.4729 | 151.5037 | 389.8673 | 186.5942
597.4729 | 151.5293 | 390.4213 | 187.2777
598.4729 | 151.9411 | 390.868 | 187.508
599.4729 | 152.2673 | 391.0854 | 188.1263
600.4729 | 152.5163 | 391.3133 | 188.6604
601.4729 | 152.7113 | 391.6342 | 189.1643
602.4729 | 152.8631 | 391.5678 | 189.4577
603.4729 | 153.4271 | 392.5225 | 190.0892
604.4729 | 153.75 | 392.2778 | 190.4464
605.4729 | 154.2166 | 392.385 | 190.8753
606.4729 | 154.7304 | 393.1639 | 191.446
607.4729 | 155.1596 | 393.4148 | 191.7722
608.4729 | 155.0916 | 394.0007 | 192.1327
609.4729 | 155.3052 | 394.0294 | 192.8746
610.4729 | 155.5454 | 394.2234 | 193.4758
611.4729 | 155.7515 | 394.7651 | 193.9537
612.4729 | 155.9799 | 394.6184 | 194.3193
613.4729 | 156.3212 | 394.654 | 194.9444
614.4885 | 156.7987 | 395.3316 | 195.3716
615.4729 | 156.9957 | 394.9905 | 195.6249
616.4729 | 157.656 | 395.0867 | 196.2692
617.4729 | 157.9059 | 395.3205 | 196.8144
618.4729 | 157.9857 | 395.3458 | 197.2874
619.4729 | 157.897 | 395.4382 | 197.5566
620.4729 | 158.1938 | 396.1909 | 197.9319
621.4729 | 158.2793 | 396.3751 | 198.0611
622.4729 | 158.5042 | 396.1742 | 198.5865
623.4729 | 159.0277 | 396.5792 | 199.3057
624.4729 | 159.1701 | 396.7756 | 199.6866
625.4729 | 159.5515 | 397.0669 | 200.0601
626.4729 | 159.6029 | 397.8242 | 200.6434
627.4729 | 159.827 | 397.6234 | 201.2574
628.4729 | 160.1967 | 397.8208 | 201.3981
629.4729 | 161.0261 | 398.1308 | 201.7187
630.4729 | 161.1574 | 398.299 | 202.2561
631.4729 | 161.5749 | 398.2894 | 202.7517
632.4729 | 162.119 | 398.6172 | 203.5587
633.4729 | 162.6233 | 398.9869 | 203.6619
634.4729 | 162.5082 | 399.731 | 204.3144
635.4729 | 162.5603 | 400.7305 | 204.7367
636.4729 | 162.7422 | 400.9212 | 205.4431
637.4729 | 163.1164 | 401.1243 | 205.7835
638.4729 | 163.3048 | 401.2176 | 205.9749
639.4729 | 163.3822 | 401.6495 | 206.5524
640.4729 | 163.6492 | 401.953 | 207.0818
641.4729 | 163.9886 | 402.2422 | 207.5666
642.4729 | 164.2873 | 403.2216 | 207.8016
643.4729 | 164.8052 | 403.466 | 208.3077
644.5042 | 164.8005 | 403.6751 | 208.9265
645.4729 | 164.8905 | 404.1262 | 209.764
646.4729 | 165.0899 | 403.9275 | 209.8618
647.4729 | 165.2524 | 403.7836 | 210.3993
648.4729 | 165.6726 | 404.3579 | 211.0064
649.4729 | 166.258 | 404.9433 | 211.3138
650.4729 | 166.4978 | 405.4648 | 212.1561
651.4729 | 166.9179 | 405.749 | 212.4498
652.4729 | 167.2218 | 405.405 | 212.6145
653.4729 | 167.1588 | 405.6857 | 212.8443
654.4729 | 167.3865 | 405.9547 | 213.4408
655.4729 | 167.5137 | 406.3145 | 213.9298
656.4729 | 167.7583 | 406.5011 | 214.3042
657.4729 | 168.151 | 406.7861 | 214.8233
658.4729 | 168.5901 | 407.96 | 215.5037
659.4729 | 168.801 | 407.789 | 216.1271
660.4729 | 168.891 | 407.492 | 216.3696
661.4729 | 169.1909 | 407.8909 | 216.5756
662.4729 | 169.3092 | 407.6717 | 216.8
663.4729 | 169.3914 | 407.8626 | 217.2359
664.4729 | 169.8725 | 408.056 | 217.5706
665.4729 | 170.4656 | 408.5428 | 218.132
666.4729 | 170.3389 | 408.679 | 218.4048
667.4729 | 170.4832 | 408.7519 | 219.333
668.4729 | 171.0859 | 409.2913 | 219.8875
669.4729 | 171.2321 | 409.3277 | 219.975
670.4729 | 171.2918 | 409.3792 | 220.6333
671.4729 | 171.4633 | 409.336 | 221.1213
672.4729 | 171.6545 | 409.9356 | 221.4326
673.4729 | 172.098 | 409.7914 | 222.1606
674.4729 | 172.3632 | 409.9769 | 222.0795
675.4729 | 172.1351 | 410.0394 | 222.2323
676.4729 | 172.2633 | 409.8772 | 222.8683
677.4729 | 172.4474 | 409.8493 | 223.0699
678.4729 | 172.7682 | 410.3006 | 223.6123
679.4729 | 173.0018 | 410.3188 | 224.1689
680.4729 | 173.5956 | 410.6196 | 225.0522
681.4729 | 173.9715 | 410.7182 | 225.2449
682.4729 | 174.5021 | 411.1485 | 225.4558
683.4729 | 174.3141 | 412.1332 | 226.1396
684.4729 | 174.4452 | 412.3068 | 226.6185
685.4729 | 174.5703 | 411.8708 | 226.5463
686.4729 | 174.5508 | 411.964 | 227.2459
687.4729 | 174.8182 | 412.1682 | 228.1747
688.4729 | 174.9877 | 412.5816 | 228.2565
689.4729 | 175.3451 | 413.6896 | 228.7002
690.4729 | 175.6353 | 413.6767 | 228.8239
691.4729 | 175.9009 | 413.2268 | 229.2759
692.4729 | 176.0963 | 413.2528 | 230.0297
693.4729 | 176.322 | 413.4048 | 230.0898
694.4729 | 176.6686 | 413.9459 | 230.6071
695.4729 | 176.6511 | 413.7968 | 231.2423
696.4729 | 176.6747 | 413.7138 | 231.5093
697.4729 | 177.2098 | 414.0206 | 232.1975
698.4729 | 177.2867 | 414.3544 | 232.4122
699.4729 | 177.6093 | 414.3781 | 232.9737
700.4729 | 177.6824 | 414.4986 | 233.5731
701.4729 | 177.6748 | 414.3886 | 233.9776
702.4729 | 177.8926 | 414.5164 | 234.4107
703.4729 | 178.183 | 414.6043 | 234.6561
704.4885 | 178.5328 | 414.714 | 235.0812
705.4729 | 178.7747 | 414.5309 | 235.4343
706.4729 | 178.9009 | 414.7185 | 236.0448
707.4729 | 179.6072 | 414.9114 | 236.6453
708.4729 | 179.6652 | 415.2822 | 236.8412
709.4729 | 179.8619 | 415.2034 | 237.0453
710.4729 | 180.2703 | 415.2236 | 237.6348
711.4729 | 180.2965 | 415.0762 | 238.0034
712.4729 | 180.4683 | 415.1422 | 238.3087
713.4729 | 180.2838 | 414.9873 | 238.865
714.4729 | 180.4841 | 415.1697 | 239.1288
715.4729 | 180.746 | 415.2321 | 239.9837
716.4729 | 180.9998 | 415.3508 | 239.9315
717.4729 | 181.4161 | 415.5224 | 240.6878
718.4729 | 182.2089 | 416.3399 | 240.739
719.4729 | 182.4396 | 416.8125 | 241.246
720.4729 | 182.5927 | 416.9726 | 241.4985
721.4729 | 182.794 | 417.2418 | 242.0448
722.4729 | 182.8475 | 417.5549 | 242.6057
723.4729 | 183.0992 | 417.6454 | 242.9713
724.4729 | 183.3883 | 418.1605 | 243.2554
725.4729 | 183.7494 | 417.8976 | 243.8466
726.4729 | 184.0672 | 418.2287 | 244.1535
727.4729 | 184.2055 | 418.2474 | 244.56
728.4729 | 184.4455 | 418.0202 | 244.8374
729.4729 | 184.316 | 418.1043 | 245.1623
730.4729 | 184.7102 | 418.4789 | 245.7523
731.4729 | 185.0418 | 418.98 | 246.3334
732.4729 | 185.2245 | 418.5719 | 246.3741
733.4729 | 185.3047 | 418.5047 | 246.7906
734.4885 | 185.6874 | 418.7268 | 247.3039
735.4729 | 185.9525 | 419.1614 | 247.7472
736.4729 | 186.4888 | 419.6377 | 248.1535
737.4729 | 187.1775 | 420.0022 | 248.7647
738.4729 | 187.344 | 420.2911 | 249.1545
739.4729 | 187.949 | 421.717 | 249.5866
740.4729 | 188.2416 | 421.6055 | 249.6584
741.4729 | 188.4538 | 421.2367 | 250.217
742.4729 | 188.6486 | 420.8329 | 250.712
743.4729 | 188.7211 | 421.378 | 251.3233
744.4729 | 189.2321 | 421.6167 | 251.7065
745.4729 | 189.4367 | 421.3842 | 251.907
746.4729 | 189.5448 | 421.4336 | 252.539
747.4885 | 189.7532 | 421.6081 | 252.9216
748.4885 | 189.7351 | 422.0417 | 253.2529
749.4729 | 189.8704 | 421.615 | 253.7413
750.4729 | 189.9762 | 421.5262 | 254.1665
751.4729 | 190.0097 | 421.9701 | 254.2523
752.4729 | 190.1936 | 421.965 | 254.7101
753.4729 | 190.5105 | 422.1742 | 255.1005
754.4729 | 190.6952 | 422.3593 | 255.5148
755.4729 | 190.9246 | 422.4742 | 255.7068
756.4729 | 191.0343 | 422.6616 | 256.0813
757.4729 | 191.474 | 422.5636 | 256.8054
758.4729 | 191.8508 | 424.1524 | 256.9029
759.4729 | 192.1104 | 423.3785 | 257.2904
760.4729 | 192.3755 | 423.4583 | 257.5877
761.4729 | 192.5164 | 423.4681 | 258.1964
762.4729 | 192.9336 | 423.5192 | 258.743
763.4729 | 193.1264 | 423.6091 | 259.1911
764.4885 | 193.24 | 423.5317 | 259.4773
765.4729 | 193.3097 | 423.679 | 259.8533
766.4729 | 193.5534 | 423.8922 | 260.1933
767.4729 | 194.0769 | 424.2618 | 260.5962
768.4729 | 194.4562 | 424.294 | 260.9831
769.4729 | 194.6256 | 424.5452 | 261.4515
770.4729 | 194.8181 | 424.8495 | 262.1067
771.4729 | 195.0335 | 424.7165 | 262.1798
772.4729 | 195.134 | 425.0571 | 262.4053
773.4729 | 195.3221 | 424.7972 | 262.5873
774.4729 | 195.296 | 424.6139 | 262.9538
775.4729 | 195.3894 | 424.623 | 263.2294
776.4729 | 195.6265 | 424.9827 | 263.8599
777.4729 | 195.8221 | 424.6672 | 264.0831
778.4729 | 196.0679 | 424.7087 | 264.1956
779.4729 | 196.5162 | 424.8594 | 264.8425
780.4729 | 196.4688 | 424.5091 | 264.9125
781.4729 | 196.4983 | 424.7105 | 265.1502
782.4729 | 196.6583 | 425.1153 | 265.6267
783.4729 | 197.0817 | 425.1025 | 266.0982
784.4729 | 197.3161 | 424.9627 | 266.4895
785.4729 | 197.5237 | 425.1026 | 266.9257
786.4729 | 197.763 | 425.0682 | 267.0522
787.4729 | 197.9622 | 425.6292 | 267.4105
788.4729 | 198.3753 | 425.951 | 267.7814
789.4729 | 198.6723 | 425.914 | 268.6026
790.4729 | 198.8283 | 425.5436 | 268.6597
791.4729 | 198.7799 | 426.0117 | 269.1112
792.4729 | 198.8698 | 425.6982 | 269.687
793.4729 | 199.2124 | 425.8821 | 270.3525
794.4729 | 199.2936 | 425.857 | 270.5705
795.4729 | 199.3421 | 425.6039 | 270.8269
796.4729 | 199.4097 | 425.6236 | 271.076
797.4729 | 199.7586 | 425.6426 | 271.5029
798.4729 | 200.1635 | 426.21 | 271.5308
799.4729 | 200.7282 | 428.0558 | 272.0251
800.4729 | 200.9417 | 427.3988 | 272.4484
801.4729 | 200.8994 | 426.8312 | 272.5429
802.4729 | 200.9377 | 426.8231 | 272.8398
803.4729 | 201.1561 | 427.5627 | 273.4274
804.4729 | 201.3214 | 426.9768 | 273.8168
805.4729 | 201.4943 | 427.1606 | 274.2977
806.4729 | 201.5661 | 427.1569 | 274.9333
807.4729 | 202.0035 | 427.3994 | 275.5154
808.4729 | 202.4034 | 427.2811 | 275.5197
809.4729 | 202.6552 | 427.4764 | 275.8095
810.4729 | 202.8679 | 427.2402 | 276.2244
811.4729 | 203.005 | 427.1535 | 276.6652
812.4729 | 203.1369 | 427.3019 | 277.1598
813.4729 | 203.2834 | 427.1819 | 277.5477
814.4729 | 203.5144 | 427.5796 | 277.6814
815.4729 | 203.6256 | 427.6416 | 278.022
816.4729 | 204.0229 | 428.367 | 278.417
817.4729 | 204.6696 | 428.7719 | 278.9915
818.4729 | 204.9023 | 428.687 | 279.992
819.4729 | 205.1799 | 428.8646 | 279.6961
820.4729 | 205.5705 | 429.1418 | 279.8008
821.4729 | 205.6865 | 429.0518 | 280.0974
822.4729 | 205.7168 | 429.1954 | 280.7463
823.4729 | 205.8272 | 429.0274 | 280.9953
824.4729 | 205.8425 | 428.6962 | 281.1707
825.4729 | 205.9486 | 428.7026 | 281.5621
826.4729 | 206.2285 | 429.1599 | 282.1896
827.4729 | 206.3753 | 428.5734 | 282.5376
828.4729 | 206.4736 | 428.5523 | 282.7818
829.4729 | 206.486 | 428.4751 | 283.0429
830.4729 | 206.7092 | 428.7001 | 283.4541
831.4729 | 207.2384 | 428.974 | 283.8459
832.4729 | 207.5679 | 429.6043 | 284.2689
833.4729 | 207.7913 | 429.9568 | 284.6498
834.4729 | 208.2515 | 429.5469 | 284.797
835.4729 | 208.5056 | 429.6423 | 285.0439
836.4729 | 208.8783 | 430.1018 | 285.3426
837.4729 | 208.9927 | 429.8294 | 285.7673
838.4729 | 209.3074 | 430.3335 | 286.0963
839.4729 | 209.384 | 430.4099 | 286.3875
840.4729 | 209.4872 | 430.0615 | 286.7663
841.4729 | 209.754 | 430.5123 | 286.9535
842.4729 | 209.8938 | 431.2821 | 287.3769
843.4729 | 210.0087 | 431.0213 | 287.9753
844.4729 | 210.2773 | 431.348 | 288.4381
845.4729 | 210.3398 | 430.866 | 288.7442
846.4729 | 210.7939 | 431.4016 | 288.8576
847.4729 | 211.2026 | 431.3043 | 289.3398
848.4729 | 211.5726 | 430.9917 | 289.442
849.4729 | 211.7068 | 431.6166 | 289.7389
850.4729 | 211.9339 | 431.3103 | 290.2388
851.4729 | 212.3069 | 431.6691 | 290.686
852.4729 | 212.8434 | 431.7184 | 290.9669
853.4729 | 212.794 | 431.5827 | 291.1675
854.4885 | 213.2107 | 431.7776 | 291.8795
855.4729 | 213.2476 | 431.6555 | 292.18
856.4729 | 213.0655 | 431.2935 | 292.2285
857.4729 | 213.1817 | 431.4468 | 292.861
858.4729 | 213.3981 | 431.6924 | 292.9593
859.4729 | 213.7915 | 431.7736 | 293.2141
860.4729 | 214.0919 | 431.5334 | 293.6498
861.4729 | 214.2396 | 431.6634 | 294.0006
862.4729 | 214.5617 | 431.6932 | 294.593
863.4729 | 214.7193 | 431.8508 | 294.6011
864.4729 | 215.0463 | 432.0006 | 294.9348
865.4729 | 215.2425 | 431.9595 | 295.4098
866.4729 | 215.2802 | 432.0396 | 295.7198
867.4729 | 215.4802 | 432.0185 | 296.0256
868.4729 | 215.6519 | 432.0418 | 296.4181
869.4729 | 215.8614 | 432.0682 | 296.8045
870.4729 | 215.9566 | 431.7743 | 297.1994
871.4729 | 216.0142 | 431.864 | 297.2007
872.4729 | 216.5294 | 432.1774 | 297.6728
873.4729 | 216.7653 | 432.7912 | 297.8526
874.4729 | 216.8355 | 432.346 | 298.2008
875.4729 | 217.0156 | 432.1147 | 298.3464
876.4729 | 217.1647 | 432.1206 | 298.6878
877.4729 | 217.2681 | 432.4918 | 299.0492
878.4729 | 217.676 | 432.5424 | 299.5448
879.4729 | 218.0229 | 432.8181 | 299.8712
880.4729 | 218.3667 | 432.7857 | 299.9688
881.4729 | 218.6132 | 432.9001 | 300.2346
882.4729 | 218.9421 | 433.9024 | 300.8929
883.4729 | 219.0208 | 433.651 | 301.1081
884.4729 | 219.0438 | 433.4136 | 301.1997
885.4729 | 219.1623 | 433.3186 | 301.6702
886.4729 | 219.2601 | 433.3276 | 302.1191
887.4729 | 219.5727 | 433.382 | 302.481
888.4729 | 219.8776 | 433.5914 | 302.9007
889.4729 | 220.1614 | 433.4212 | 303.1896
890.4729 | 220.252 | 433.3108 | 303.3629
891.4729 | 220.2909 | 433.2026 | 303.7626
892.4729 | 220.4646 | 433.0815 | 304.1133
893.4729 | 220.4855 | 433.2585 | 304.7264
894.4729 | 220.8232 | 433.1891 | 304.9938
895.4729 | 221.0445 | 433.0936 | 305.4551
896.4729 | 221.1319 | 433.0119 | 305.992
897.4729 | 221.1123 | 433.0099 | 306.3643
898.4729 | 221.3285 | 432.8754 | 306.5541
899.4729 | 221.3278 | 432.7486 | 306.7335
900.4729 | 221.5976 | 432.6368 | 307.0636
901.4729 | 221.8746 | 432.552 | 307.3261
902.4729 | 222.0754 | 432.7236 | 307.7485
903.4729 | 222.3157 | 433.1664 | 308.1687
904.4729 | 222.6319 | 433.0405 | 308.4914
905.4729 | 222.9098 | 433.5794 | 308.8706
906.4729 | 223.0583 | 432.9199 | 309.1535
907.4729 | 223.2576 | 432.7191 | 309.3037
908.4729 | 223.3274 | 432.9245 | 309.7605
909.4729 | 223.3592 | 432.7717 | 309.9246
910.4729 | 223.4187 | 432.5203 | 310.1148
911.4729 | 223.5607 | 432.8261 | 310.7668
912.4729 | 223.6815 | 432.8544 | 310.9955
913.4729 | 224.101 | 433.218 | 311.4792
914.4729 | 224.4951 | 433.2439 | 311.5066
915.4729 | 224.71 | 433.1682 | 311.8194
916.4729 | 224.7952 | 432.848 | 312.1996
917.4729 | 224.8901 | 433.0689 | 312.5138
918.4729 | 225.1294 | 433.3299 | 312.8028
919.4729 | 225.2085 | 432.9788 | 313.0967
920.4729 | 225.3206 | 432.8399 | 313.6551
921.4729 | 225.3969 | 432.6938 | 314.0847
922.4729 | 225.6242 | 432.6342 | 314.7112
923.4729 | 225.8462 | 432.5722 | 314.7396
924.4729 | 225.9845 | 432.5455 | 315.2691
925.4729 | 226.1828 | 432.6592 | 315.4132
926.4729 | 226.3421 | 432.6326 | 315.973
927.4729 | 226.5951 | 432.9385 | 316.0921
928.4729 | 226.8389 | 432.51 | 316.4469
929.4729 | 226.9004 | 432.9625 | 316.4396
930.4729 | 226.9545 | 432.6652 | 316.8651
931.4729 | 227.2826 | 432.509 | 317.0989
932.4729 | 227.7406 | 432.9421 | 317.5101
933.4729 | 227.9128 | 433.2233 | 317.6644
934.4729 | 227.9355 | 432.9425 | 318.2208
935.4729 | 228.0596 | 432.8189 | 318.3572
936.4729 | 228.3065 | 433.0322 | 318.9445
937.4729 | 228.4617 | 432.9723 | 319.0304
938.4729 | 228.7645 | 432.9706 | 319.7199
939.4729 | 228.9214 | 432.9077 | 319.9516
940.4729 | 229.0505 | 432.9387 | 320.1701
941.4729 | 229.2976 | 432.7331 | 320.4973
942.4729 | 229.5113 | 432.6099 | 320.6959
943.4729 | 229.5863 | 432.8334 | 320.7241
944.4729 | 229.8314 | 432.8175 | 321.0073
945.4729 | 230.0289 | 433.4977 | 321.5765
946.4729 | 230.3935 | 433.0209 | 321.6561
947.4729 | 230.4134 | 433.0567 | 322.2226
948.4729 | 230.5722 | 432.8383 | 322.4662
949.4729 | 231.0141 | 432.9099 | 322.6346
950.4729 | 231.2929 | 432.9881 | 322.9837
951.4729 | 231.2348 | 433.0621 | 323.0949
952.4729 | 231.2274 | 433.3356 | 323.3164
953.4729 | 231.3248 | 433.4456 | 323.6232
954.4729 | 231.4948 | 433.9591 | 323.7831
955.4729 | 231.8319 | 435.3772 | 324.2907
956.4729 | 232.1015 | 433.9806 | 324.6312
957.4729 | 232.1837 | 434.3187 | 324.9072
958.4729 | 232.2885 | 433.7566 | 325.0057
959.4729 | 232.1904 | 433.6525 | 325.2194
960.4729 | 232.2616 | 433.3333 | 325.464
961.4729 | 232.437 | 433.4353 | 326.1525
962.4729 | 232.8218 | 433.5448 | 326.3233
963.4729 | 232.9209 | 433.5151 | 326.7386
964.4729 | 232.9649 | 433.2471 | 326.9166
965.4729 | 233.0169 | 433.0815 | 327.2277
966.4729 | 233.2096 | 433.9686 | 327.8031
967.4729 | 233.6323 | 434.1581 | 327.9613
968.4729 | 233.6853 | 433.9496 | 328.1433
969.4729 | 233.804 | 434.0957 | 328.2562
970.4729 | 234.1297 | 433.8893 | 328.5271
971.4729 | 234.1163 | 433.3443 | 328.8757
972.4729 | 234.1103 | 433.516 | 328.8946
973.4729 | 234.3772 | 433.4824 | 329.3793
974.4729 | 234.5477 | 433.7323 | 329.7687
975.4729 | 234.5992 | 433.5484 | 330.1783
976.4729 | 234.6937 | 433.6486 | 330.3081
977.4729 | 234.6772 | 433.3152 | 330.4616
978.4729 | 234.9461 | 433.593 | 330.5266
979.4729 | 235.3972 | 433.3532 | 330.8782
980.4729 | 235.6705 | 434.7176 | 331.3453
981.4729 | 235.8587 | 434.2504 | 331.6506
982.4729 | 235.9166 | 433.7094 | 331.8261
983.4729 | 236.0698 | 433.5771 | 332.0785
984.4729 | 236.1584 | 433.9032 | 332.4254
985.4729 | 236.3133 | 434.7187 | 332.6346
986.4729 | 236.5362 | 435.1157 | 333.0649
987.4729 | 237.2473 | 435.1796 | 333.4175
988.4729 | 237.3011 | 434.3572 | 333.5554
989.4729 | 237.3929 | 435.3133 | 333.7489
990.4729 | 237.6948 | 436.1951 | 334.0678
991.4729 | 237.9578 | 435.3725 | 334.2856
992.4729 | 238.1419 | 435.5861 | 334.4532
993.4729 | 238.2583 | 435.6995 | 334.7877
994.4729 | 238.2165 | 435.2211 | 335.4341
995.4729 | 238.2176 | 435.0143 | 335.7157
996.4729 | 238.3331 | 435.0604 | 335.7609
997.4729 | 238.3929 | 434.9913 | 336.0625
998.4729 | 238.6686 | 435.4074 | 336.3265
999.4729 | 238.6703 | 435.6311 | 336.7212
1000.4729 | 238.8258 | 435.451 | 336.6384
1001.4729 | 238.9639 | 435.3578 | 336.9047
1002.4729 | 239.191 | 435.0267 | 337.2302
1003.4729 | 239.3202 | 435.0708 | 337.5337
1004.4729 | 239.4853 | 435.3252 | 338.3514
1005.4729 | 239.6856 | 435.3336 | 338.4279
1006.4729 | 239.938 | 435.7669 | 338.5777
1007.4729 | 240.1614 | 435.4139 | 338.7822
1008.4729 | 240.41 | 436.0902 | 338.9083
1009.4729 | 240.4658 | 435.573 | 338.9194
1010.4729 | 240.5348 | 435.3894 | 339.3014
1011.4729 | 240.5553 | 435.141 | 339.4339
1012.4729 | 240.7361 | 435.3394 | 339.8389
1013.4729 | 241.0676 | 435.3887 | 340.2035
1014.4729 | 241.3641 | 435.4327 | 340.6018
1015.4729 | 241.4125 | 435.0091 | 340.6418
1016.4729 | 241.4947 | 435.2768 | 340.9829
1017.4729 | 241.6493 | 435.2269 | 341.0865
1018.4729 | 241.7407 | 435.2999 | 341.3709
1019.4729 | 242.1116 | 435.2879 | 341.667
1020.4729 | 242.356 | 435.7159 | 341.9236
1021.4729 | 242.5891 | 436.1076 | 342.34
1022.4729 | 242.7377 | 435.9861 | 342.6541
1023.4729 | 242.7969 | 436.4585 | 342.763
1024.4729 | 242.9698 | 435.9022 | 342.7558
1025.4729 | 242.9383 | 435.9971 | 343.0889
1026.4729 | 243.0837 | 436.0823 | 343.6377
1027.4729 | 243.2892 | 436.3931 | 343.7259
1028.4729 | 243.3837 | 435.8779 | 344.1094
1029.4729 | 243.6006 | 435.989 | 344.1731
1030.4729 | 243.8307 | 436.1453 | 344.7802
1031.4729 | 243.7744 | 435.8097 | 344.5846
1032.4729 | 243.8978 | 435.7689 | 344.7483
1033.4729 | 244.1238 | 435.9039 | 345.3101
1034.4729 | 244.3871 | 435.6512 | 345.496
1035.4729 | 244.3385 | 435.478 | 345.507
1036.4729 | 244.4092 | 435.6393 | 345.6974
1037.4729 | 244.603 | 435.5138 | 346.0941
1038.4729 | 244.9246 | 435.9214 | 346.4542
1039.4729 | 245.182 | 435.7568 | 346.5651
1040.4729 | 245.3513 | 435.8035 | 346.4365
1041.4729 | 245.6784 | 435.8646 | 346.7495
1042.4729 | 245.7724 | 435.5104 | 347.0413
1043.4729 | 245.8302 | 435.5682 | 347.3653
1044.4729 | 245.8413 | 435.4694 | 347.3901
1045.4729 | 245.8826 | 435.8647 | 347.7796
1046.4729 | 246.0617 | 435.7362 | 348.0867
1047.4729 | 246.1735 | 435.2973 | 348.178
1048.4729 | 246.3579 | 435.4915 | 348.2832
1049.4729 | 246.4164 | 435.4526 | 349.1069
1050.4729 | 246.5211 | 435.9879 | 349.0042
1051.4729 | 246.5259 | 435.1384 | 348.9266
1052.4729 | 246.5822 | 435.0428 | 349.3102
1053.4729 | 246.7465 | 435.1184 | 349.643
1054.4729 | 247.0444 | 435.1238 | 349.7473
1055.4729 | 247.1145 | 435.2677 | 349.9486
1056.4729 | 247.1452 | 434.9941 | 350.0933
1057.4729 | 247.157 | 434.8308 | 350.2245
1058.4729 | 247.2383 | 434.8511 | 350.5685
1059.4729 | 247.4536 | 434.8262 | 350.7278
1060.4729 | 247.7899 | 434.6491 | 350.8688
1061.4729 | 247.9288 | 435.0833 | 350.9573
1062.4729 | 248.1403 | 434.8986 | 351.2799
1063.4729 | 248.2416 | 435.301 | 351.6408
1064.4729 | 248.2431 | 435.5666 | 351.7835
1065.4729 | 248.2787 | 435.0723 | 351.9079
1066.4729 | 248.3967 | 434.9558 | 351.9131
1067.4729 | 248.7194 | 435.2061 | 352.1119
1068.4729 | 249.0112 | 435.0531 | 352.3136
1069.4729 | 249.4878 | 435.0025 | 352.6086
1070.4729 | 249.7492 | 435.7652 | 352.6298
1071.4729 | 249.7995 | 435.3751 | 353.1693
1072.4729 | 249.633 | 435.7692 | 353.3526
1073.4729 | 249.6954 | 436.7601 | 353.6591
1074.4729 | 249.9787 | 435.9323 | 354.0989
1075.4729 | 250.2145 | 435.8569 | 354.3134
1076.4729 | 250.4331 | 436.6378 | 354.3399
1077.4729 | 250.7672 | 436.5564 | 354.5487
1078.4729 | 251.1011 | 436.8652 | 354.66
1079.4729 | 251.2607 | 436.6117 | 355.0586
1080.4729 | 251.2234 | 436.6135 | 354.9485
1081.4729 | 251.2709 | 436.5051 | 355.4274
1082.4729 | 251.3631 | 436.4299 | 355.7806
1083.4885 | 251.615 | 436.3954 | 355.7047
1084.4729 | 251.8876 | 436.2279 | 355.8777
1085.4729 | 252.0653 | 436.4098 | 356.0525
1086.4729 | 252.1901 | 436.4201 | 356.151
1087.4729 | 252.3318 | 436.3674 | 356.7728
1088.4729 | 252.3313 | 436.2176 | 356.646
1089.4729 | 252.4645 | 436.1524 | 356.9341
1090.4729 | 252.6044 | 436.2127 | 357.0338
1091.4729 | 252.6807 | 436.5491 | 357.4218
1092.4729 | 252.785 | 436.1992 | 357.4294
1093.4729 | 252.9679 | 436.1322 | 357.5501
1094.4729 | 253.1793 | 436.4182 | 357.7378
1095.4729 | 253.6135 | 436.8839 | 357.8794
1096.4729 | 253.8502 | 437.0572 | 358.1571
1097.4729 | 254.0519 | 437.1359 | 358.3996
1098.4729 | 254.3775 | 438.2932 | 358.8967
1099.4729 | 254.9898 | 438.2173 | 359.1155
1100.4729 | 255.0693 | 438.2116 | 359.1853
1101.4729 | 254.8519 | 437.5876 | 359.3428
1102.4729 | 254.7225 | 437.8593 | 359.6625
1103.4729 | 254.8847 | 438.0353 | 359.7967
1104.4729 | 254.9277 | 438.0326 | 360.07
1105.4729 | 255.2134 | 438.0666 | 360.3636
1106.4729 | 255.4043 | 438.3711 | 360.3864
1107.4729 | 255.8824 | 438.2405 | 360.7603
1108.4729 | 256.0803 | 438.1688 | 361.4755
1109.4729 | 256.2031 | 438.6463 | 361.8599
1110.4729 | 256.4331 | 438.9951 | 361.9388
1111.4729 | 256.5508 | 438.9867 | 362.0703
1112.4729 | 256.6011 | 439.3417 | 362.1819
1113.4729 | 256.786 | 439.2524 | 362.3643
1114.4729 | 257.029 | 439.3859 | 362.6239
1115.4729 | 257.2955 | 439.1304 | 362.7094
1116.4729 | 257.5947 | 439.0529 | 362.9267
1117.4729 | 257.9243 | 438.9846 | 363.2716
1118.4729 | 257.806 | 439.1324 | 363.8813
1119.4729 | 257.8368 | 439.2533 | 364.1694
1120.4729 | 257.948 | 440.6729 | 364.2295
1121.4729 | 257.9904 | 439.9341 | 364.5285
1122.4729 | 258.1608 | 439.4324 | 364.8522
1123.4729 | 258.4392 | 439.8355 | 364.9966
1124.4729 | 258.7819 | 441.0968 | 365.3656
1125.4729 | 258.812 | 440.8233 | 365.5456
1126.4729 | 258.9087 | 440.602 | 365.6906
1127.4729 | 259.3331 | 441.3725 | 366.2649
1128.4729 | 259.6719 | 441.7299 | 366.4699
1129.4729 | 260.0337 | 441.8822 | 366.6403
1130.4729 | 260.1366 | 441.7188 | 366.5942
1131.4729 | 260.2668 | 442.0337 | 367.0965
1132.4729 | 260.6643 | 441.7688 | 367.1655
1133.4729 | 260.9162 | 442.2126 | 367.2786
1134.4729 | 261.0562 | 442.3579 | 367.6692
1135.4729 | 261.0672 | 442.1136 | 367.6307
1136.4729 | 260.8994 | 441.8564 | 367.734
1137.4729 | 261.0974 | 442.0845 | 367.9613
1138.4729 | 261.1824 | 442.2474 | 368.3192
1139.4729 | 261.4017 | 443.3661 | 368.6379
1140.4729 | 261.9343 | 444.7354 | 369.1265
1141.4729 | 262.17 | 443.7414 | 369.1334
1142.4729 | 262.1853 | 442.9664 | 369.4668
1143.4729 | 262.188 | 443.4205 | 369.4466
1144.4729 | 262.3375 | 443.4027 | 369.6824
1145.4729 | 262.5852 | 443.5253 | 370.0425
1146.4729 | 262.739 | 443.724 | 370.3301
1147.4729 | 262.8967 | 443.6078 | 370.3825
1148.4729 | 263.0661 | 443.2673 | 370.6013
1149.4729 | 263.3008 | 443.5429 | 370.933
1150.4729 | 263.4287 | 443.6991 | 371.5867
1151.4729 | 263.519 | 443.5991 | 371.8732
1152.4729 | 263.5438 | 443.4861 | 372.4786
1153.4729 | 263.752 | 443.7202 | 372.7642
1154.4729 | 263.7865 | 443.965 | 372.9328
1155.4729 | 263.9415 | 444.2333 | 373.2269
1156.4729 | 264.2646 | 444.7325 | 373.2476
1157.4729 | 264.4207 | 444.4872 | 373.2553
1158.4729 | 264.6796 | 445.984 | 373.5584
1159.4729 | 264.7255 | 445.1386 | 373.9428
1160.4729 | 264.9015 | 445.193 | 374.1632
1161.4729 | 265.0766 | 444.9416 | 374.7596
1162.4729 | 265.3365 | 444.9072 | 374.9655
1163.4729 | 265.5918 | 444.7946 | 375.2087
1164.4729 | 265.673 | 444.7001 | 375.4674
1165.4729 | 265.9261 | 445.0563 | 375.7507
1166.4729 | 266.5415 | 445.9906 | 376.364
1167.4729 | 266.4958 | 445.523 | 376.7863
1168.4729 | 267.0124 | 445.5578 | 376.9351
1169.4729 | 266.977 | 445.3287 | 377.2769
1170.4729 | 267.0453 | 445.2746 | 377.4949
1171.4729 | 267.0331 | 445.2289 | 377.8325
1172.4729 | 267.221 | 446.1212 | 378.4188
1173.4729 | 267.4292 | 446.2509 | 378.903
1174.4729 | 267.535 | 445.7329 | 379.0766
1175.4729 | 267.7262 | 445.3924 | 379.1058
1176.4729 | 267.962 | 445.5296 | 379.2423
1177.4729 | 268.0747 | 445.4926 | 379.3638
1178.4729 | 268.2435 | 445.4168 | 379.6805
1179.4729 | 268.4996 | 445.5454 | 379.7361
1180.4729 | 268.5682 | 445.4802 | 379.8839
1181.4729 | 268.7597 | 445.5494 | 380.3159
1182.4729 | 269.0307 | 445.7464 | 380.4923
1183.4729 | 269.3114 | 445.9574 | 381.2201
1184.4729 | 269.544 | 445.8128 | 381.5585
1185.4729 | 269.7524 | 445.8427 | 381.554
1186.4729 | 269.8168 | 445.6781 | 381.6479
1187.4729 | 269.9545 | 445.7446 | 382.1164
1188.4729 | 270.0796 | 445.5081 | 382.0339
1189.4729 | 270.1523 | 445.5312 | 382.379
1190.4729 | 270.2744 | 445.4352 | 382.7793
1191.4729 | 270.3629 | 445.4272 | 383.1352
1192.4729 | 270.6353 | 445.4274 | 383.3887
1193.4729 | 270.6487 | 445.2941 | 383.344
1194.4729 | 270.7124 | 445.5526 | 384.1815
1195.4729 | 271.1063 | 445.5348 | 384.3253
1196.4729 | 271.431 | 445.8706 | 384.4853
1197.4729 | 271.6822 | 445.7711 | 384.4493
1198.4729 | 271.9407 | 446.1163 | 385.0667
1199.4729 | 272.107 | 445.8997 | 384.8642
1200.4729 | 272.3553 | 445.6775 | 385.1138
1201.4729 | 272.5653 | 446.0379 | 385.5119
1202.4729 | 272.6748 | 446.5622 | 385.7951
1203.4729 | 273.0317 | 446.3885 | 385.7629
1204.4729 | 273.0693 | 445.9434 | 386.2209
1205.4729 | 273.1272 | 446.1126 | 386.5218
1206.4729 | 273.3527 | 446.7793 | 386.9097
1207.4729 | 273.5006 | 446.3698 | 387.1544
1208.4729 | 273.7643 | 446.5543 | 387.1127
1209.4729 | 273.9551 | 446.3499 | 387.4939
1210.4729 | 274.0108 | 446.7451 | 387.6445
1211.4729 | 274.2848 | 446.6559 | 387.9316
1212.4729 | 274.5116 | 446.5791 | 387.99
1213.4729 | 274.7054 | 446.5966 | 388.5001
1214.4729 | 274.7309 | 446.3985 | 388.5271
1215.4729 | 274.8764 | 446.3745 | 388.9372
1216.4729 | 274.9215 | 446.3487 | 389.1672
1217.4729 | 275.1935 | 446.6629 | 389.3013
1218.4729 | 275.623 | 446.8857 | 389.4969
1219.4729 | 275.6967 | 446.6386 | 389.8516
1220.4729 | 275.8082 | 446.6754 | 389.893
1221.4729 | 276.2208 | 446.9181 | 389.9473
1222.4729 | 276.628 | 448.7276 | 390.3062
1223.4729 | 277.0245 | 448.8759 | 390.7574
1224.4729 | 277.0458 | 448.3354 | 391.2578
1225.4729 | 277.2149 | 448.3137 | 391.4629
1226.4729 | 277.5268 | 448.217 | 391.7432
1227.4729 | 277.5889 | 448.1368 | 391.9432
1228.4885 | 277.6421 | 448.1264 | 392.2328
1229.4729 | 277.8333 | 448.4652 | 392.6375
1230.4885 | 277.8366 | 448.1387 | 392.7114
1231.4885 | 277.9562 | 447.9917 | 392.7879
1232.4729 | 278.1926 | 448.0975 | 392.9026
1233.4729 | 278.5179 | 448.3662 | 393.1987
1234.4729 | 278.6382 | 448.3588 | 393.5169
1235.4729 | 279.1179 | 449.0896 | 393.6681
1236.4729 | 279.3654 | 449.1983 | 394.0143
1237.4729 | 279.5664 | 449.2121 | 394.2857
1238.4729 | 280.065 | 449.6919 | 394.7096
1239.4729 | 280.2513 | 450.0705 | 394.6848
1240.4729 | 280.4109 | 450.2657 | 394.8136
1241.4729 | 280.5115 | 450.8013 | 395.041
1242.4729 | 280.724 | 450.0309 | 395.5286
1243.4729 | 280.989 | 450.1948 | 395.5283
1244.4729 | 281.3604 | 450.4977 | 396.0061
1245.4729 | 281.3873 | 450.337 | 396.2904
1246.4729 | 281.3409 | 450.1305 | 396.6322
1247.4729 | 281.3326 | 450.0316 | 397.0013
1248.4729 | 281.5342 | 450.028 | 397.458
1249.4729 | 281.8329 | 450.1803 | 397.3891
1250.4729 | 282.0575 | 450.2297 | 397.3839
1251.4729 | 282.4457 | 450.5697 | 397.7268
1252.4729 | 282.4671 | 450.3802 | 398.0799
1253.4729 | 282.7375 | 450.2463 | 398.2636
1254.4729 | 282.9931 | 450.431 | 398.4143
1255.4729 | 283.1935 | 450.5878 | 398.9023
1256.4729 | 283.5521 | 450.8029 | 399.4139
1257.4729 | 283.612 | 450.7104 | 399.3264
1258.4729 | 283.9565 | 450.8516 | 399.9874
1259.4729 | 284.0457 | 450.9213 | 399.9455
1260.4729 | 284.1338 | 450.9492 | 399.9989
1261.4729 | 284.4577 | 451.2799 | 400.2746
1262.4729 | 284.9324 | 451.2907 | 400.55
1263.4885 | 285.0632 | 451.2656 | 400.7321
1264.4729 | 285.1163 | 451.1329 | 400.9325
1265.4729 | 285.1215 | 451.0649 | 401.408
1266.4729 | 285.2147 | 451.0975 | 402.3663
1267.4729 | 285.4498 | 451.1827 | 402.3831
1268.4729 | 285.5501 | 451.148 | 402.3642
1269.4729 | 285.7592 | 451.5308 | 403.089
1270.4729 | 286.0276 | 451.7715 | 403.0432
1271.4729 | 286.2348 | 451.6766 | 403.558
1272.4729 | 286.555 | 451.5793 | 403.7562
1273.4729 | 286.7248 | 451.6022 | 403.8918
1274.4729 | 287.0268 | 451.807 | 404.0206
1275.4729 | 287.2013 | 452.1778 | 404.4085
1276.4729 | 287.4477 | 451.8864 | 404.6705
1277.4729 | 287.5181 | 452.0541 | 404.9868
1278.4729 | 287.7907 | 452.5604 | 405.0122
1279.4729 | 288.0738 | 452.0998 | 405.2588
1280.4729 | 288.1965 | 452.0378 | 405.6215
1281.4729 | 288.2987 | 452.0283 | 405.9421
1282.4729 | 288.274 | 451.8717 | 405.8491
1283.4729 | 288.4329 | 451.9536 | 406.2578
1284.4729 | 288.7457 | 452.1209 | 406.8094
1285.4729 | 288.9373 | 452.3833 | 407.0665
1286.4729 | 289.2608 | 452.4028 | 407.2201
1287.4729 | 289.4816 | 452.4171 | 407.2269
1288.4729 | 289.7302 | 452.436 | 407.7727
1289.4729 | 290.098 | 452.5038 | 407.9059
1290.4729 | 290.3575 | 453.0059 | 408.3401
1291.4729 | 290.3243 | 452.5224 | 408.585
1292.4729 | 290.3916 | 452.5337 | 408.6393
1293.4729 | 290.7536 | 452.7471 | 409.0703
1294.4729 | 291.2986 | 453.3426 | 409.2398
1295.4729 | 291.4275 | 453.2726 | 409.2236
1296.4729 | 291.4935 | 453.3453 | 409.2584
1297.4729 | 291.8298 | 453.5423 | 410.0569
1298.4729 | 292.1822 | 453.5399 | 410.5096
1299.4729 | 292.1233 | 453.4747 | 410.6762
1300.4729 | 292.155 | 454.091 | 410.8705
1301.4729 | 292.4288 | 454.3536 | 411.3534
1302.4729 | 292.5072 | 453.7834 | 411.5933
1303.4729 | 292.7204 | 453.8672 | 411.6978
1304.4729 | 292.9902 | 453.9964 | 411.792
1305.4729 | 293.1863 | 454.5129 | 412.1299
1306.4729 | 293.3735 | 454.6189 | 412.4265
1307.4729 | 293.4911 | 454.4544 | 412.5057
1308.4729 | 293.5605 | 454.2471 | 412.8764
1309.4729 | 293.7479 | 454.3021 | 413.0875
1310.4729 | 294.0274 | 454.5602 | 413.2578
1311.4729 | 294.3432 | 455.0873 | 413.6422
1312.4729 | 294.4742 | 454.8131 | 413.3781
1313.4729 | 294.7075 | 454.8718 | 413.8851
1314.4729 | 294.9537 | 455.9023 | 413.9946
1315.4729 | 295.2228 | 455.9165 | 414.5781
1316.4729 | 295.2828 | 455.1171 | 414.9372
1317.4729 | 295.297 | 455.0635 | 415.4511
1318.4729 | 295.4156 | 455.2242 | 415.7202
1319.4729 | 295.6032 | 455.3426 | 416.2077
1320.4729 | 295.7458 | 455.4443 | 416.3861
1321.4729 | 295.9052 | 455.2704 | 416.6613
1322.4729 | 296.119 | 455.1879 | 416.8057
1323.4729 | 296.2725 | 455.3104 | 416.9089
1324.4729 | 296.4119 | 455.4191 | 417.259
1325.4729 | 296.4714 | 455.384 | 417.5482
1326.4729 | 296.7015 | 455.4304 | 417.8292
1327.4729 | 296.9804 | 455.5268 | 417.7831
1328.4729 | 297.0648 | 455.3396 | 417.9926
1329.4729 | 297.1886 | 455.3666 | 418.2679
1330.4729 | 297.2124 | 455.4476 | 418.7926
1331.4729 | 297.3449 | 455.5865 | 419.2303
1332.4729 | 297.6673 | 456.0332 | 419.4476
1333.4729 | 297.8606 | 456.0134 | 419.6153
1334.4729 | 298.0428 | 455.8528 | 420.1392
1335.4729 | 298.2508 | 455.6449 | 419.8864
1336.4729 | 298.4021 | 455.6594 | 419.939
1337.4729 | 298.5747 | 455.8092 | 420.2245
1338.4729 | 298.7298 | 455.7086 | 420.5118
1339.4729 | 298.9253 | 455.7355 | 421.0965
1340.4729 | 299.0477 | 455.7299 | 421.0988
1341.4729 | 299.1635 | 455.6346 | 421.5475
1342.4729 | 299.1698 | 455.7011 | 422.5668
1343.4729 | 299.3868 | 455.9486 | 423.2074
1344.4729 | 299.6064 | 455.9864 | 422.5776
1345.4729 | 299.9803 | 455.8577 | 422.3741
1346.4729 | 300.0727 | 455.829 | 422.8556
1347.4729 | 300.2603 | 455.8367 | 423.0918
1348.4729 | 300.4415 | 456.0701 | 423.3133
1349.4729 | 300.5145 | 456.5318 | 423.5746
1350.4729 | 300.6215 | 456.3969 | 423.9984
1351.4729 | 300.7477 | 456.4818 | 423.7659
1352.4729 | 300.8028 | 456.3818 | 424.3104
1353.4729 | 300.9866 | 456.3718 | 424.6269
1354.4729 | 301.1709 | 456.3101 | 424.4401
1355.4729 | 301.5018 | 456.4353 | 424.8626
1356.4885 | 301.7153 | 456.6619 | 424.8012
1357.4885 | 301.9805 | 456.8313 | 424.9819
1358.4729 | 302.3424 | 457.0275 | 425.748
1359.4729 | 302.3752 | 456.6969 | 425.8296
1360.4729 | 302.4971 | 456.6492 | 425.7023
1361.4885 | 302.728 | 457.0344 | 426.2033
1362.4729 | 302.7416 | 457.1079 | 426.239
1363.4729 | 302.8814 | 457.257 | 426.7124
1364.4729 | 303.1083 | 457.4086 | 426.839
1365.4729 | 303.0595 | 456.8954 | 427.0665
1366.4729 | 303.1062 | 456.9854 | 427.0136
1367.4729 | 303.3588 | 457.6399 | 427.3369
1368.4729 | 303.5116 | 457.7743 | 427.8622
1369.4729 | 303.5935 | 457.8181 | 428.236
1370.4729 | 303.9121 | 458.6448 | 428.4376
1371.4729 | 304.1662 | 458.2242 | 428.6766
1372.4729 | 304.5799 | 458.3813 | 428.7239
1373.4729 | 304.7504 | 458.3327 | 429.0564
1374.4729 | 304.8126 | 458.0912 | 428.7094
1375.4729 | 304.8641 | 458.1979 | 429.0838
1376.4729 | 305.0698 | 458.2748 | 429.2991
1377.4729 | 305.0949 | 458.1549 | 429.3
1378.4729 | 305.1659 | 458.4496 | 429.6662
1379.4729 | 305.474 | 458.7278 | 429.6315
1380.4729 | 305.7825 | 458.6289 | 429.7684
1381.4729 | 305.8345 | 458.3505 | 429.8853
1382.4729 | 306.0065 | 458.4679 | 430.1939
1383.4729 | 306.4669 | 459.2013 | 430.2631
1384.4729 | 306.8591 | 459.328 | 430.4045
1385.4729 | 306.9372 | 459.1252 | 430.4932
1386.4729 | 307.1512 | 458.8698 | 430.5545
1387.4729 | 307.3335 | 458.7967 | 430.7145
1388.4729 | 307.379 | 458.7701 | 430.779
1389.4729 | 307.4124 | 458.8317 | 431.0886
1390.4729 | 307.5215 | 458.9386 | 431.3044
1391.4729 | 307.8141 | 459.2392 | 431.6742
1392.4729 | 308.0594 | 459.249 | 432.0462
1393.4729 | 308.4214 | 459.5956 | 431.976
1394.4729 | 308.5534 | 459.2897 | 432.0456
1395.4729 | 308.9248 | 460.2957 | 432.4469
1396.4729 | 309.0329 | 459.7328 | 432.3326
1397.4729 | 309.0614 | 459.6359 | 432.2337
1398.4729 | 309.2371 | 459.6969 | 432.2364
1399.4729 | 309.6412 | 460.3052 | 432.3522
1400.4729 | 310.0137 | 460.177 | 432.9813
1401.4729 | 310.175 | 460.0687 | 432.8781
1402.4729 | 310.3807 | 460.1149 | 432.922
1403.4729 | 310.5598 | 460.187 | 432.9764
1404.4729 | 310.6413 | 460.177 | 433.0192
1405.4729 | 310.7446 | 460.156 | 433.2157
1406.4729 | 310.7035 | 460.2416 | 433.4623
1407.4729 | 310.8147 | 460.6168 | 433.4705
1408.4729 | 311.0652 | 460.2683 | 433.2473
1409.4729 | 311.1088 | 460.392 | 433.498
1410.4729 | 311.1684 | 460.2932 | 433.572
1411.4729 | 311.221 | 460.6138 | 433.7905
1412.4729 | 311.4307 | 460.3823 | 433.7603
1413.4729 | 311.5296 | 460.186 | 433.954
1414.4729 | 311.6892 | 460.3767 | 433.9748
1415.4729 | 312.2289 | 460.3476 | 433.9251
1416.4729 | 312.4704 | 460.5538 | 434.0483
1417.4729 | 312.5077 | 460.5097 | 434.3659
1418.4729 | 312.6673 | 460.431 | 434.6413
1419.4729 | 312.5644 | 460.2368 | 434.5459
1420.4729 | 312.615 | 460.2146 | 434.8455
1421.4729 | 312.6367 | 460.1736 | 434.6927
1422.4729 | 312.8126 | 460.1641 | 434.8403
1423.4729 | 312.8994 | 460.0745 | 434.8733
1424.4729 | 313.3851 | 460.152 | 434.8212
1425.4729 | 313.8949 | 460.5407 | 434.9325
1426.4729 | 314.2156 | 460.5194 | 435.191
1427.4729 | 314.3069 | 460.3471 | 435.2676
1428.4729 | 314.7387 | 460.2811 | 435.2319
1429.4729 | 314.7182 | 460.2376 | 435.45
1430.4729 | 314.6756 | 460.382 | 435.6086
1431.4729 | 314.6494 | 460.2747 | 435.5597
1432.4729 | 314.5732 | 460.3571 | 435.7691
1433.4729 | 314.497 | 460.0227 | 435.9014
1434.4729 | 314.5238 | 459.9453 | 436.0206
1435.4729 | 314.6582 | 460.2408 | 436.3341
1436.4729 | 315.0207 | 461.7093 | 436.4662
1437.4729 | 315.1205 | 460.6196 | 436.3459
1438.4729 | 315.0844 | 460.3685 | 436.3152
1439.4729 | 315.4499 | 460.7383 | 436.3158
1440.4729 | 315.6557 | 460.5342 | 436.5875
1441.4729 | 315.8236 | 460.7685 | 436.5965
1442.4729 | 316.1164 | 461.3213 | 436.6674
1443.4729 | 316.1955 | 461.248 | 436.7588
1444.4729 | 316.3516 | 460.8953 | 436.7106
1445.4729 | 316.4388 | 460.9709 | 436.7156
1446.4729 | 316.6178 | 461.084 | 437.0705
1447.4729 | 316.5525 | 460.7259 | 437.0754
1448.4729 | 316.5427 | 460.8806 | 437.0437
1449.4729 | 316.5557 | 460.9245 | 437.2001
1450.4729 | 316.6417 | 461.1121 | 437.7146
1451.4729 | 316.8524 | 461.3238 | 437.4788
1452.4729 | 317.1077 | 461.2611 | 437.3276
1453.4729 | 317.1822 | 461.0259 | 437.4248
1454.4729 | 317.252 | 461.0762 | 437.6395
1455.4729 | 317.3378 | 460.8799 | 437.7323
1456.4729 | 317.3922 | 460.8347 | 437.791
1457.4729 | 317.4814 | 460.6636 | 437.8762
1458.4729 | 317.5766 | 460.7266 | 437.9029
1459.4729 | 317.6386 | 460.554 | 437.9571
1460.4729 | 317.7144 | 460.7533 | 438.3437
1461.4729 | 317.7823 | 460.6123 | 438.5174
1462.4729 | 317.7771 | 460.5266 | 438.5747
1463.4729 | 317.9087 | 460.6143 | 438.6176
1464.4729 | 318.1043 | 460.7806 | 438.6504
1465.4729 | 318.1657 | 460.538 | 438.6444
1466.4729 | 318.2667 | 460.4398 | 438.6624
1467.4729 | 318.3092 | 460.3602 | 438.9256
1468.4729 | 318.4109 | 460.2054 | 439.0185
1469.4729 | 318.4453 | 460.2353 | 439.4004
1470.4729 | 318.6041 | 460.2665 | 439.3314
1471.4729 | 318.8923 | 460.4055 | 439.171
1472.4729 | 319.0442 | 460.2561 | 439.6186
1473.4729 | 319.0446 | 460.398 | 439.8258
1474.4729 | 319.2267 | 460.2226 | 439.9116
1475.4729 | 319.3374 | 460.0259 | 439.8046
1476.4729 | 319.4494 | 459.9883 | 439.779
1477.4729 | 319.5315 | 459.801 | 439.6567
1478.4729 | 319.7111 | 459.825 | 439.8037
1479.4729 | 320.0688 | 459.877 | 440.129
1480.4729 | 320.4383 | 459.9077 | 440.009
1481.4729 | 320.8154 | 460.1642 | 439.9954
1482.4729 | 320.9708 | 459.8714 | 439.9413
1483.4729 | 320.9361 | 459.8087 | 439.891
1484.4729 | 320.737 | 459.7997 | 440.1739
1485.4729 | 320.6884 | 460.0158 | 440.0619
1486.4729 | 320.8472 | 459.9379 | 440.1178
1487.4729 | 320.9703 | 459.8172 | 440.1518
1488.4729 | 321.0327 | 459.7295 | 440.3136
1489.4729 | 321.2624 | 459.7184 | 440.2642
1490.4729 | 321.3338 | 459.5764 | 440.42
1491.4729 | 321.4255 | 459.4097 | 440.522
1492.4729 | 321.5648 | 459.5364 | 440.6686
1493.4729 | 321.6856 | 459.6347 | 440.569
1494.4729 | 321.7248 | 459.3759 | 440.442
1495.4729 | 321.8077 | 459.322 | 440.5454
1496.4729 | 321.8725 | 459.2099 | 440.7167
1497.4729 | 321.9562 | 459.211 | 440.5753
1498.4729 | 322.1131 | 459.2415 | 440.5302
1499.4729 | 322.1758 | 459.1839 | 440.5143
1500.4729 | 322.3884 | 459.4015 | 440.5
1501.4729 | 322.5939 | 459.4504 | 440.6953
1502.4729 | 322.736 | 459.2921 | 440.5839
1503.4729 | 322.8682 | 459.2979 | 440.5846
1504.4729 | 323.0029 | 459.1297 | 440.9087
1505.4729 | 326.3317 | 460.2165 | 441.1838
1506.4729 | 322.8949 | 458.8586 | 440.9806
1507.4729 | 322.9185 | 458.7313 | 441.0966
1508.4729 | 322.932 | 458.7729 | 441.0049
1509.4729 | 323.0985 | 458.8966 | 441.133
1510.4729 | 323.2749 | 458.7649 | 441.4342
1511.4729 | 323.6077 | 458.771 | 441.369
1512.4729 | 323.8176 | 459.1862 | 441.6816
1513.4729 | 323.9282 | 458.9125 | 441.3764
1514.4729 | 324.1426 | 458.9132 | 441.5643
1515.4729 | 324.1535 | 459.044 | 441.852
1516.4729 | 324.4269 | 458.9234 | 441.9976
1517.4729 | 324.316 | 458.7889 | 442.0203
1518.4729 | 324.1829 | 458.5563 | 441.5636
1519.4729 | 324.3082 | 458.4312 | 441.7179
1520.4729 | 324.3959 | 458.4591 | 441.8132
1521.4729 | 324.5783 | 458.4553 | 442.1371
1522.4729 | 324.9244 | 458.3615 | 442.1122
1523.4729 | 325.2536 | 458.3685 | 442.1805
1524.4729 | 325.3534 | 458.3371 | 442.1666
1525.4729 | 325.5174 | 458.4261 | 442.1647
1526.4729 | 325.8149 | 458.3583 | 442.2384
1527.4729 | 325.8546 | 458.349 | 442.3562
1528.4729 | 325.7126 | 458.0794 | 442.2099
1529.4729 | 325.7124 | 458.0315 | 442.2861
1530.4729 | 325.7489 | 457.8647 | 442.4173
1531.4729 | 325.8712 | 457.9823 | 442.2849
1532.4729 | 326.0634 | 457.9227 | 442.7436
1533.4729 | 326.3884 | 457.8853 | 442.5177
1534.4729 | 326.6823 | 458.0339 | 442.7496
1535.4729 | 327.1774 | 458.2328 | 442.8168
1536.4729 | 327.1201 | 458.0549 | 442.7771
1537.4729 | 327.0698 | 458.48 | 442.9966
1538.4729 | 327.1856 | 459.4712 | 443.3379
1539.4729 | 327.3172 | 459.1233 | 443.3823
1540.4729 | 327.3884 | 458.5365 | 443.3441
1541.4729 | 327.729 | 458.377 | 443.2975
1542.4729 | 328.1262 | 458.5039 | 443.2755
1543.4729 | 327.8318 | 458.2215 | 443.1431
1544.4729 | 327.5348 | 458.0329 | 443.0636
1545.4729 | 328.0993 | 458.1559 | 443.0872
1546.4729 | 327.8652 | 457.9993 | 443.134
1547.4729 | 328.1816 | 458.0847 | 443.3596
1548.4729 | 328.2839 | 458.0162 | 443.4405
1549.4729 | 328.1372 | 457.9227 | 443.5139
1550.4729 | 328.0867 | 457.9905 | 443.362
1551.4729 | 328.2362 | 457.8131 | 443.6149
1552.4729 | 328.1752 | 457.4369 | 443.2967
1553.4729 | 328.3522 | 457.7154 | 443.7263
1554.4729 | 328.4642 | 457.6544 | 443.8609
1555.4729 | 328.558 | 457.5904 | 443.889
1556.4729 | 328.6843 | 457.4882 | 444.35
1557.4729 | 328.8077 | 457.4234 | 444.3341
1558.4729 | 329.0132 | 457.422 | 444.4466
1559.4729 | 329.0575 | 457.3937 | 444.7021
1560.4729 | 329.1151 | 457.3573 | 444.4535
1561.4729 | 329.1825 | 457.3449 | 444.531
1562.4729 | 329.2634 | 457.191 | 444.5695
1563.4729 | 329.295 | 457.1304 | 444.6547
1564.4729 | 329.3171 | 457.0027 | 444.6868
1565.4729 | 329.393 | 456.9996 | 445.2409
1566.4729 | 329.5179 | 456.8963 | 445.1681
1567.4729 | 329.6313 | 456.9766 | 445.3093
1568.4729 | 329.8787 | 457.1067 | 445.644
1569.4729 | 330.2402 | 456.9916 | 445.4315
1570.4729 | 330.119 | 456.8268 | 445.2967
1571.4729 | 330.0785 | 456.7093 | 445.2582
1572.4729 | 330.0346 | 456.6527 | 445.1993
1573.4729 | 330.074 | 456.4456 | 445.167
1574.4729 | 330.2666 | 456.5349 | 445.7336
1575.4729 | 330.6017 | 456.6199 | 445.9483
1576.4729 | 330.6796 | 457.1257 | 445.805
1577.4729 | 330.7205 | 456.6653 | 445.9133
1578.4729 | 330.825 | 456.6484 | 445.8445
1579.4729 | 330.942 | 456.7765 | 445.8895
1580.4729 | 331.1172 | 456.6534 | 445.818
1581.4729 | 331.2219 | 456.7799 | 445.6975
1582.4729 | 331.4357 | 456.786 | 445.8175
1583.4729 | 331.5224 | 456.7782 | 445.9168
1584.4729 | 331.5079 | 456.8477 | 445.8403
1585.4729 | 331.6749 | 456.5784 | 445.8038
1586.4729 | 331.8104 | 456.5752 | 446.3508
1587.4729 | 331.8605 | 456.6689 | 446.2927
1588.4729 | 331.8683 | 456.6815 | 446.1797
1589.4729 | 331.9742 | 456.5232 | 446.266
1590.4729 | 332.0527 | 456.5225 | 446.263
1591.4729 | 332.0874 | 456.37 | 446.2573
1592.4729 | 332.093 | 456.2418 | 446.3025
1593.4729 | 332.155 | 456.2662 | 446.259
1594.4729 | 332.3215 | 456.9019 | 446.3585
1595.4729 | 332.48 | 456.4321 | 446.6111
1596.4729 | 332.5678 | 456.7075 | 446.7292
1597.4729 | 332.7942 | 457.2653 | 447.0349
1598.4729 | 332.8555 | 456.7299 | 446.8174
1599.4729 | 332.8449 | 456.84 | 446.9074
1600.4729 | 333.0169 | 457.5955 | 447.0373
1601.4885 | 333.2227 | 457.1654 | 446.914
1602.4729 | 333.3562 | 457.1269 | 446.7673
1603.4729 | 333.5988 | 456.9279 | 446.866
1604.4729 | 333.6791 | 456.9351 | 446.9776
1605.4729 | 333.6461 | 456.831 | 446.9415
1606.4729 | 333.5829 | 457.2247 | 447.4179
1607.4729 | 333.6779 | 457.0151 | 447.0838
1608.4729 | 333.6999 | 456.9474 | 447.0454
1609.4729 | 333.931 | 456.9629 | 447.0472
1610.4729 | 333.972 | 457.0477 | 447.1597
1611.4729 | 334.1978 | 456.9376 | 447.185
1612.4729 | 334.3538 | 456.8011 | 447.0856
1613.4729 | 334.4653 | 457.0834 | 447.4189
1614.4729 | 334.5867 | 458.2872 | 447.6579
1615.4729 | 334.7957 | 457.836 | 447.3542
1616.4729 | 334.9407 | 457.5091 | 447.1805
1617.4729 | 335.2082 | 457.7641 | 447.3584
1618.4729 | 335.2029 | 457.8271 | 447.5654
1619.4729 | 335.274 | 457.6388 | 447.6495
1620.4729 | 335.4691 | 457.8046 | 447.5384
1621.4729 | 335.7755 | 458.2027 | 447.6246
1622.4729 | 335.6298 | 458.2386 | 447.5628
1623.4729 | 335.797 | 458.1425 | 447.6419
1624.4729 | 335.7352 | 457.9194 | 447.5098
1625.4729 | 335.7045 | 457.8134 | 447.7294
1626.4729 | 335.7093 | 458.1058 | 447.8758
1627.4729 | 335.8429 | 458.0019 | 447.6813
1628.4729 | 336.1644 | 457.9674 | 447.5043
1629.4729 | 336.2809 | 458.5349 | 447.5131
1630.4729 | 336.3261 | 458.2349 | 447.5083
1631.4729 | 336.2388 | 458.0166 | 447.5637
1632.4729 | 336.1641 | 457.9404 | 447.8392
1633.4729 | 336.1954 | 457.9251 | 447.6386
1634.4729 | 336.2588 | 458.0866 | 447.7078
1635.4729 | 336.2638 | 457.8075 | 447.7763
1636.4729 | 336.5619 | 458.073 | 447.6422
1637.4729 | 336.5844 | 457.891 | 447.5512
1638.4729 | 336.6756 | 458.3458 | 447.6765
1639.4729 | 336.8113 | 458.7089 | 447.8317
1640.4729 | 337.1447 | 459.0358 | 447.6997
1641.4729 | 337.1332 | 458.5838 | 447.7478
1642.4729 | 337.1258 | 458.3628 | 447.5523
1643.4729 | 337.1605 | 458.7815 | 447.8522
1644.4729 | 337.2796 | 458.8513 | 448.0086
1645.4729 | 337.3724 | 458.7048 | 448.2088
1646.4729 | 337.4678 | 458.7156 | 448.1639
1647.4729 | 337.465 | 459.0529 | 448.534
1648.4729 | 337.5437 | 459.0483 | 448.6284
1649.4729 | 337.6038 | 459.043 | 448.5479
1650.4729 | 337.7561 | 458.9947 | 448.6094
1651.4729 | 337.8993 | 459.0688 | 448.4812
1652.4729 | 338.0528 | 458.9422 | 448.6308
1653.4729 | 338.1537 | 459.0469 | 448.6147
1654.4729 | 338.2353 | 459.0105 | 448.7099
1655.4729 | 338.334 | 459.0441 | 448.764
1656.4729 | 338.4326 | 459.0757 | 448.8378
1657.4729 | 338.3512 | 458.989 | 449.154
1658.4729 | 338.319 | 459.0983 | 449.2555
1659.4729 | 338.3418 | 459.218 | 449.6863
1660.4729 | 338.4423 | 459.1326 | 449.5196
1661.4729 | 338.6849 | 459.3239 | 449.7076
1662.4729 | 338.7726 | 459.1873 | 449.7873
1663.4729 | 338.8431 | 459.3562 | 450.2211
1664.4729 | 338.9078 | 459.39 | 449.9517
1665.4885 | 338.9968 | 459.1816 | 450.0224
1666.4729 | 339.0521 | 459.2575 | 449.8838
1667.4729 | 339.1442 | 459.3195 | 449.8353
1668.4729 | 339.239 | 459.1906 | 449.6226
1669.4729 | 339.4748 | 459.1351 | 449.6681
1670.4729 | 339.5907 | 459.423 | 449.7945
1671.4729 | 339.6801 | 459.1812 | 449.8865
1672.4729 | 339.7531 | 459.8452 | 449.7933
1673.4729 | 339.9298 | 459.5609 | 449.7672
1674.4729 | 339.8535 | 459.6281 | 449.8616
1675.4729 | 339.8886 | 459.4352 | 449.8629
1676.4729 | 340.0488 | 459.3757 | 449.817
1677.4729 | 340.1696 | 459.4161 | 449.8296
1678.4729 | 340.2779 | 459.613 | 449.6594
1679.4729 | 340.593 | 459.7143 | 450.0941
1680.4729 | 340.7053 | 459.9437 | 450.101
1681.4729 | 340.6714 | 459.6901 | 450.0292
1682.4729 | 340.6711 | 459.7084 | 450.1607
1683.4729 | 340.8209 | 459.6829 | 450.3687
1684.4729 | 340.9477 | 459.6711 | 450.4391
1685.4729 | 341.0745 | 459.5455 | 450.4132
1686.4729 | 341.1274 | 459.8249 | 450.3177
1687.4729 | 341.289 | 459.9325 | 450.2691
1688.4729 | 341.4361 | 460.0102 | 450.2446
1689.4729 | 341.559 | 460.0424 | 450.5535
1690.4729 | 341.7139 | 459.918 | 450.4513
1691.4729 | 341.6715 | 460.1797 | 450.7902
1692.4729 | 341.7797 | 460.08 | 451.0367
1693.4729 | 341.7829 | 459.9052 | 451.3778
1694.4729 | 341.7975 | 460.3094 | 451.1491
1695.4885 | 342.0038 | 460.4189 | 451.1806
1696.4729 | 342.0698 | 461.3683 | 451.1004
1697.4729 | 342.3298 | 460.7838 | 451.1907
1698.4729 | 342.3936 | 461.1922 | 451.4085
1699.4729 | 342.5437 | 461.0674 | 451.6305
1700.4729 | 342.4776 | 460.8766 | 451.7512
1701.4729 | 342.4985 | 460.6164 | 451.9619
1702.4729 | 342.5882 | 460.7036 | 452.2372
1703.4729 | 342.5644 | 460.6719 | 452.0164
1704.4729 | 342.7151 | 461.0107 | 451.9927
1705.4729 | 342.8722 | 460.8564 | 452.338
1706.4729 | 343.0334 | 460.713 | 452.246
1707.4729 | 343.1977 | 460.6745 | 452.0511
1708.4729 | 343.2815 | 460.6733 | 452.3286
1709.4729 | 343.3816 | 460.8653 | 452.2176
1710.4729 | 343.5081 | 460.8025 | 452.1976
1711.4729 | 343.6355 | 460.7977 | 452.2117
1712.4729 | 343.7711 | 460.9385 | 452.642
1713.4729 | 343.7975 | 461.0103 | 452.3588
1714.4729 | 343.8806 | 461.034 | 452.6799
1715.4729 | 344.013 | 460.946 | 452.6363
1716.4729 | 344.0775 | 461.1534 | 452.9602
1717.4729 | 344.2285 | 461.0098 | 452.9016
1718.4729 | 344.2766 | 461.0435 | 453.1634
1719.4729 | 344.3402 | 460.9369 | 453.0481
1720.4729 | 344.3651 | 460.9182 | 452.9803
1721.4729 | 344.5316 | 460.899 | 453.2051
1722.4729 | 344.5927 | 460.9287 | 453.5941
1723.4729 | 344.5726 | 460.7536 | 453.2413
1724.4729 | 344.6459 | 460.7508 | 453.2841
1725.4729 | 344.8262 | 460.9261 | 453.5897
1726.4729 | 344.8382 | 460.7543 | 453.5115
1727.4729 | 344.9025 | 460.8686 | 453.7159
1728.4729 | 345.0912 | 460.8512 | 453.6297
1729.4729 | 345.3235 | 461.0442 | 453.795
1730.4729 | 345.3657 | 461.0385 | 453.8048
1731.4729 | 345.3667 | 461.0034 | 453.8613
1732.4729 | 345.355 | 461.1018 | 454.0888
1733.4729 | 345.685 | 461.8302 | 454.0617
1734.4729 | 345.8922 | 461.4813 | 453.9399
1735.4729 | 346.0193 | 461.5038 | 454.0864
1736.4729 | 346.0032 | 461.3788 | 454.2261
1737.4729 | 346.0344 | 461.2922 | 454.3966
1738.4729 | 346.1123 | 461.4481 | 454.2131
1739.4729 | 346.2107 | 462.0525 | 454.4837
1740.4729 | 346.3203 | 462.1167 | 454.7061
1741.4729 | 346.4592 | 461.9573 | 454.5029
1742.4729 | 346.5337 | 461.7724 | 454.6489
1743.4729 | 346.6253 | 461.9446 | 454.5735
1744.4729 | 346.8444 | 461.9616 | 454.7415
1745.4729 | 346.8623 | 461.794 | 454.8236
1746.4729 | 346.9321 | 461.9166 | 454.9973
1747.4729 | 347.0781 | 461.8278 | 454.934
1748.4729 | 347.1855 | 462.1176 | 455.1328
1749.4729 | 347.3173 | 462.3775 | 455.031
1750.4729 | 347.367 | 462.4839 | 455.1574
1751.4729 | 347.5396 | 462.0956 | 455.2302
1752.4729 | 347.6979 | 462.1704 | 455.5773
1753.4729 | 347.8126 | 462.3984 | 455.8528
1754.4729 | 347.9277 | 462.3009 | 455.5403
1755.4885 | 347.9975 | 462.2004 | 455.5316
1756.4729 | 348.0854 | 462.3247 | 455.6483
1757.4729 | 348.0982 | 462.383 | 455.8353
1758.4729 | 348.2039 | 462.3324 | 455.7687
1759.4729 | 348.3521 | 462.4255 | 455.8349
1760.4729 | 348.411 | 462.4355 | 455.9427
1761.4729 | 348.47 | 462.4801 | 456.2832
1762.4729 | 348.4682 | 462.4194 | 456.3793
1763.4729 | 348.43 | 462.3524 | 456.0441
1764.4729 | 348.5648 | 462.6972 | 456.4367
1765.4729 | 348.783 | 463.276 | 456.4029
1766.4729 | 349.0291 | 463.5866 | 456.3932
1767.4729 | 349.1854 | 463.1826 | 456.3925
1768.4729 | 349.2812 | 463.3008 | 456.7598
1769.4729 | 349.26 | 463.2207 | 456.8324
1770.4729 | 349.4278 | 463.374 | 456.6981
1771.4729 | 349.4477 | 463.402 | 456.9338
1772.4729 | 349.5295 | 463.6914 | 457.0214
1773.4729 | 349.6992 | 463.5088 | 456.8217
1774.4729 | 349.9513 | 463.4308 | 456.8436
1775.4729 | 350.1946 | 463.4867 | 456.8472
1776.4729 | 350.2231 | 463.9341 | 456.9986
1777.4729 | 350.2442 | 464.0216 | 457.0269
1778.4729 | 350.4252 | 464.0333 | 456.8302
1779.4729 | 350.4714 | 464.4897 | 456.8832
1780.4729 | 350.6057 | 465.0255 | 456.8693
1781.4729 | 350.6183 | 464.2961 | 457.1614
1782.4729 | 350.6396 | 464.7375 | 457.298
1783.4729 | 350.7438 | 465.4842 | 457.3855
1784.4729 | 350.8774 | 464.9031 | 457.3018
1785.4729 | 350.9716 | 464.8416 | 457.2467
1786.4729 | 350.9986 | 464.7625 | 457.4423
1787.4729 | 351.0839 | 465.1267 | 457.8531
1788.4729 | 351.1385 | 465.2601 | 457.8433
1789.4729 | 351.1775 | 464.9865 | 457.9837
1790.4729 | 351.2025 | 464.9836 | 457.8471
1791.4729 | 351.2899 | 465.3244 | 457.9819
1792.4729 | 351.4255 | 465.9459 | 458.0284
1793.4729 | 351.5788 | 465.4388 | 457.9089
1794.4729 | 351.6382 | 465.5313 | 458.1963
1795.4729 | 351.5685 | 465.4778 | 458.3913
1796.4729 | 351.6947 | 465.483 | 458.4561
1797.4729 | 351.8008 | 465.6281 | 458.6156
1798.4729 | 351.8766 | 465.8084 | 458.5795
1799.4729 | 351.8787 | 465.7539 | 458.2793
1800.4729 | 351.9916 | 466.155 | 458.4082
1801.4729 | 352.1586 | 466.0484 | 458.4861
1802.4729 | 352.3991 | 466.2938 | 458.4413
1803.4729 | 352.5045 | 466.3792 | 458.5451
1804.4729 | 352.5044 | 466.221 | 458.6557
1805.4729 | 352.5951 | 466.192 | 458.5671
1806.4729 | 352.7279 | 466.1997 | 458.7725
1807.4729 | 352.8752 | 466.1472 | 458.9009
1808.4729 | 352.8657 | 466.0895 | 458.9524
1809.4729 | 352.7682 | 466.0177 | 458.7986
1810.4729 | 352.7306 | 465.9654 | 458.9241
1811.4729 | 352.9538 | 466.14 | 458.9073
1812.4729 | 353.0392 | 466.1873 | 458.9287
1813.4729 | 353.2171 | 466.185 | 458.8973
1814.4729 | 353.3372 | 466.4304 | 459.1696
1815.4729 | 353.416 | 466.4704 | 459.2039
1816.4729 | 353.5395 | 466.4639 | 459.1333
1817.4729 | 353.6856 | 466.4356 | 459.2726
1818.4729 | 353.8506 | 466.8646 | 459.4588
1819.4729 | 354.0646 | 466.8642 | 459.8765
1820.4729 | 354.2741 | 467.4253 | 459.3869
1821.4729 | 354.39 | 467.1981 | 459.5254
1822.4729 | 354.3256 | 467.2216 | 459.3206
1823.4729 | 354.2651 | 467.2843 | 459.8368
1824.4729 | 354.2465 | 467.7375 | 459.609
1825.4729 | 354.3492 | 467.283 | 460.0283
1826.4729 | 354.4274 | 467.2593 | 459.7604
1827.4729 | 354.5253 | 468.0761 | 460.0694
1828.4729 | 354.9027 | 469.5528 | 459.8854
1829.4729 | 355.0182 | 468.6876 | 460.052
1830.4729 | 355.0056 | 468.1351 | 459.8237
1831.4729 | 355.0255 | 467.9965 | 459.9959
1832.4729 | 355.0404 | 468.1738 | 460.1801
1833.4729 | 355.2034 | 468.3795 | 460.5204
1834.4729 | 355.2952 | 468.2509 | 460.2417
1835.4729 | 355.3943 | 468.1902 | 460.2648
1836.4729 | 355.5191 | 468.1869 | 460.1874
1837.4729 | 355.5979 | 468.3309 | 460.4391
1838.4729 | 355.6481 | 468.303 | 460.3164
1839.4729 | 355.7244 | 468.3734 | 460.3466
1840.4729 | 355.7427 | 468.5857 | 460.5843
1841.4729 | 355.8238 | 468.9622 | 460.4454
1842.4729 | 355.9775 | 468.4556 | 460.4446
1843.4729 | 356.0766 | 468.8854 | 460.4405
1844.4729 | 356.1817 | 468.9209 | 460.7955
1845.4729 | 356.2472 | 468.849 | 460.5922
1846.4729 | 356.3226 | 468.9619 | 460.6676
1847.4729 | 356.4544 | 468.9986 | 460.9063
1848.4729 | 356.4481 | 468.8868 | 461.0013
1849.4729 | 356.5474 | 469.0426 | 460.7513
1850.4729 | 356.7131 | 469.3954 | 460.8799
1851.4729 | 356.8064 | 469.2927 | 461.3945
1852.4729 | 356.9136 | 469.5179 | 461.0927
1853.4729 | 357.0041 | 469.3731 | 461.6305
1854.4729 | 357.0646 | 469.5052 | 461.4319
1855.4729 | 357.1176 | 469.6219 | 461.9731
1856.4729 | 357.1636 | 469.5658 | 461.5493
1857.4729 | 357.1591 | 469.3084 | 461.3406
1858.4729 | 357.2717 | 469.4593 | 461.3552
1859.4729 | 357.3938 | 469.6362 | 461.5827
1860.4729 | 357.62 | 469.7341 | 461.6095
1861.4729 | 357.7086 | 469.6693 | 461.7283
1862.4885 | 357.9488 | 469.7705 | 461.9122
1863.4729 | 357.9325 | 469.846 | 461.9917
1864.4729 | 357.9833 | 469.9419 | 461.889
1865.4729 | 358.2037 | 470.1362 | 461.8572
1866.4729 | 358.3578 | 470.4919 | 462.5167
1867.4729 | 358.4434 | 470.169 | 462.3506
1868.4729 | 358.3701 | 470.3124 | 462.5203
1869.4729 | 358.5278 | 471.1312 | 462.7248
1870.4729 | 358.6597 | 470.539 | 462.8741
1871.4729 | 358.8619 | 470.5722 | 462.5467
1872.4729 | 358.9641 | 471.1694 | 462.9306
1873.4729 | 359.0122 | 471.4714 | 462.9801
1874.4729 | 359.126 | 470.9681 | 463.3332
1875.4729 | 359.1461 | 470.7636 | 463.5769
1876.4729 | 359.1283 | 471.0287 | 463.1655
1877.4729 | 359.3208 | 471.3057 | 463.0438
1878.4729 | 359.5575 | 472.018 | 463.4128
1879.4729 | 359.7657 | 471.462 | 463.4005
1880.4729 | 359.8668 | 471.5279 | 463.3405
1881.4729 | 359.9688 | 471.6796 | 463.4839
1882.4729 | 359.9883 | 471.8055 | 463.7825
1883.4729 | 360.2267 | 472.2266 | 463.9684
1884.4729 | 360.5184 | 472.0624 | 464.2551
1885.4729 | 360.6542 | 472.4522 | 464.0142
1886.4729 | 360.886 | 472.4464 | 464.1456
1887.4729 | 361.0332 | 472.4777 | 463.9594
1888.4729 | 360.9726 | 472.7139 | 464.4975
1889.4729 | 360.9894 | 472.8471 | 464.8846
1890.4729 | 360.9267 | 473.3254 | 464.8063
1891.4729 | 361.1766 | 473.2651 | 464.7193
1892.4729 | 361.354 | 472.9358 | 464.8681
1893.4729 | 361.3528 | 473.1894 | 465.6654
1894.4729 | 361.3979 | 474.0056 | 465.7539
1895.4729 | 361.6351 | 475.1498 | 466.0131
1896.4729 | 361.6915 | 474.0438 | 465.796
1897.4729 | 361.7432 | 474.0217 | 465.7997
1898.4729 | 361.7947 | 474.1718 | 465.9728
1899.4729 | 362.0554 | 474.7157 | 465.8705
1900.4729 | 362.1878 | 475.066 | 466.4281
1901.4729 | 362.4273 | 474.5473 | 465.9308
1902.4729 | 362.6946 | 475.1041 | 466.1045
1903.4729 | 362.9518 | 475.6735 | 466.4254
1904.4729 | 363.1641 | 476.4375 | 466.5354
1905.4885 | 363.2242 | 475.8084 | 466.9264
1906.4729 | 363.1646 | 476.2874 | 466.6342
1907.4729 | 363.1604 | 476.0617 | 466.5735
1908.4729 | 363.4416 | 476.6029 | 466.9609
1909.4729 | 363.5938 | 476.2634 | 467.1348
1910.4729 | 363.7061 | 476.498 | 467.1743
1911.4729 | 363.973 | 476.375 | 467.1054
1912.4729 | 364.0671 | 476.479 | 467.5463
1913.4729 | 364.2616 | 476.5814 | 467.3002
1914.4729 | 364.399 | 476.7205 | 467.1935
1915.4729 | 364.5157 | 476.7182 | 467.4775
1916.4729 | 364.4619 | 476.8492 | 467.6977
1917.4729 | 364.4442 | 476.9353 | 467.5522
1918.4729 | 364.6492 | 477.2791 | 467.934
1919.4729 | 365.0809 | 478.148 | 467.8212
1920.4729 | 365.5577 | 478.6201 | 468.1094
1921.4729 | 365.6082 | 477.9403 | 468.2401
1922.4729 | 365.4956 | 477.663 | 468.0642
1923.4729 | 365.4748 | 478.0363 | 467.9504
1924.4729 | 365.8146 | 478.2637 | 468.0809
1925.4729 | 366.0861 | 478.8999 | 468.4606
1926.4729 | 366.1932 | 478.8452 | 468.6217
1927.4729 | 366.2016 | 478.6653 | 468.9343
1928.4729 | 366.2593 | 479.5219 | 468.8373
1929.4729 | 366.4956 | 479.3813 | 468.9492
1930.4729 | 367.0579 | 479.4854 | 468.7684
1931.4729 | 367.2823 | 479.8274 | 468.8576
1932.4729 | 367.2195 | 480.1475 | 468.932
1933.4729 | 367.2259 | 479.9792 | 469.0885
1934.4729 | 367.3479 | 480.0605 | 469.1034
1935.4885 | 367.2163 | 480.0539 | 469.924
1936.4729 | 367.1976 | 480.0126 | 470.1135
1937.4729 | 367.3755 | 480.5308 | 469.9254
1938.4729 | 367.5227 | 480.5203 | 470.0793
1939.4729 | 367.7067 | 480.3984 | 470.0233
1940.4885 | 367.6595 | 480.5088 | 470.5269
1941.4885 | 367.7138 | 480.1449 | 470.5185
1942.4729 | 367.7213 | 480.3479 | 470.2656
1943.4729 | 367.7179 | 481.7025 | 470.9575
1944.4729 | 367.7087 | 480.9667 | 470.6672
1945.4729 | 367.7666 | 481.1063 | 471.1244
1946.4729 | 368.1343 | 481.2259 | 471.0599
1947.4885 | 368.2195 | 481.0671 | 471.0979
1948.4729 | 368.4049 | 481.1855 | 471.4933
1949.4729 | 368.546 | 481.4721 | 471.3988
1950.4729 | 368.67 | 482.2172 | 471.8491
1951.4729 | 369.0746 | 482.6007 | 471.6321
1952.4729 | 369.077 | 482.074 | 471.7775
1953.4729 | 369.0163 | 482.0077 | 471.8488
1954.4729 | 369.1457 | 481.9334 | 472.1187
1955.4729 | 369.3062 | 482.1244 | 472.7831
1956.4729 | 369.4918 | 482.3528 | 472.6906
1957.4729 | 369.5161 | 482.3373 | 472.9942
1958.4729 | 369.4485 | 482.2318 | 473.3846
1959.4729 | 369.5137 | 482.3322 | 472.9684
1960.4729 | 369.9693 | 482.5861 | 473.196
1961.4729 | 370.2379 | 483.0329 | 473.0587
1962.4729 | 370.1216 | 483.1745 | 473.0653
1963.4729 | 370.1987 | 482.8373 | 473.4016
1964.4729 | 370.3636 | 482.89 | 473.9537
1965.4885 | 370.3178 | 482.8519 | 473.6616
1966.4729 | 370.4736 | 482.9199 | 473.7389
1967.4729 | 370.6169 | 483.0031 | 473.6093
1968.4729 | 371.1342 | 483.2562 | 473.5023
1969.4729 | 371.7073 | 483.6504 | 473.5
1970.4729 | 371.8669 | 484.0235 | 473.5288
1971.4729 | 371.9962 | 485.864 | 474.3178
1972.4729 | 372.0847 | 486.3881 | 474.5219
1973.4729 | 371.9489 | 487.1725 | 475.157
1974.4729 | 371.9999 | 486.8512 | 475.5206
1975.4729 | 372.0231 | 486.1229 | 475.1274
1976.4729 | 372.2052 | 486.2569 | 475.118
1977.4729 | 372.4518 | 486.9177 | 475.2842
1978.4729 | 372.3961 | 486.8374 | 475.6157
1979.4729 | 372.4929 | 486.3264 | 475.4616
1980.4729 | 372.53 | 486.4629 | 475.6505
1981.4729 | 372.7114 | 486.3933 | 476.238
1982.4729 | 372.8571 | 486.7558 | 476.7444
1983.4885 | 372.7778 | 486.5691 | 476.7195
1984.4729 | 372.8433 | 486.519 | 477.099
1985.4729 | 373.2054 | 487.4558 | 476.8058
1986.4729 | 373.1935 | 486.8787 | 477.0747
1987.4729 | 373.2763 | 486.7845 | 477.0345
1988.4729 | 373.5162 | 487.4024 | 477.0186
1989.4729 | 373.7469 | 487.3053 | 477.4679
1990.4729 | 373.7555 | 487.5015 | 477.6217
1991.4729 | 373.8688 | 487.7534 | 477.3802
1992.4729 | 374.0451 | 487.6465 | 478.8911
1993.4729 | 374.0321 | 487.7244 | 478.6981
1994.4729 | 374.1138 | 487.4543 | 478.7132
1995.4885 | 374.3349 | 487.352 | 478.2632
1996.4729 | 374.6579 | 487.6444 | 478.2783
1997.4729 | 374.6698 | 487.4983 | 478.3821
1998.4729 | 374.7135 | 487.6951 | 478.532
1999.4729 | 374.8477 | 487.7565 | 478.474
2000.4729 | 374.9636 | 487.7316 | 478.5596
2001.4729 | 375.0429 | 487.8472 | 478.6631
2002.4729 | 375.2186 | 487.6873 | 478.6649
2003.4729 | 375.6541 | 488.0878 | 478.6526
2004.4729 | 375.5957 | 488.2964 | 479.5408
2005.4729 | 375.6007 | 488.0909 | 479.2251
2006.4729 | 375.709 | 487.8093 | 479.1701
2007.4729 | 375.8192 | 487.9683 | 479.0855
2008.4729 | 375.9268 | 488.3072 | 479.0782
2009.4729 | 376.1999 | 488.623 | 479.0913
2010.4729 | 376.4018 | 489.2124 | 479.3792
2011.4729 | 376.7102 | 489.5941 | 479.4867
2012.4729 | 377.0595 | 489.117 | 480.1891
2013.4729 | 376.9063 | 488.9763 | 479.839
2014.4729 | 376.8563 | 489.5947 | 480.02
2015.4729 | 376.9148 | 489.7901 | 480.4212
2016.4729 | 377.0956 | 489.4921 | 480.3254
2017.4729 | 377.2973 | 489.6909 | 480.6982
2018.4729 | 377.3529 | 489.6851 | 480.9776
2019.4729 | 377.4187 | 489.4964 | 481.2072
2020.4729 | 377.5032 | 489.5066 | 480.7948
2021.4729 | 377.7453 | 490.1232 | 480.9844
2022.4729 | 377.9829 | 491.0167 | 481.4967
2023.4729 | 378.2133 | 490.8523 | 481.8441
2024.4729 | 378.5899 | 490.628 | 481.8611
2025.4885 | 378.6349 | 490.4052 | 481.8945
2026.4729 | 378.9399 | 490.3974 | 481.7274
2027.4729 | 379.0253 | 490.4143 | 481.8675
2028.4729 | 379.0303 | 490.2858 | 481.6993
2029.4729 | 379.1105 | 490.3618 | 481.7805
2030.4729 | 379.2553 | 490.3774 | 481.969
2031.4729 | 379.5173 | 490.7037 | 482.1071
2032.4729 | 379.6227 | 490.822 | 482.2146
2033.4729 | 379.6574 | 490.6401 | 482.3628
2034.4729 | 379.7055 | 490.5635 | 482.2476
2035.4729 | 379.9127 | 490.6045 | 482.4978
2036.4729 | 379.9372 | 490.7505 | 482.5907
2037.4729 | 380.4738 | 491.2145 | 482.6569
2038.4729 | 380.7194 | 491.1477 | 482.6856
2039.4729 | 380.7456 | 491.4733 | 482.6924
2040.4729 | 380.7886 | 491.8546 | 483.2595
2041.4729 | 380.6556 | 491.4426 | 483.4144
2042.4729 | 380.5721 | 491.4949 | 483.7016
2043.4729 | 380.7685 | 491.3782 | 483.4906
2044.4729 | 381.1883 | 491.4005 | 483.6599
2045.4729 | 381.8084 | 491.634 | 483.7635
2046.4729 | 381.9891 | 491.8658 | 483.9634
2047.4729 | 382.2299 | 492.2341 | 484.3988
2048.4729 | 382.1743 | 492.2824 | 484.3944
2049.4729 | 382.3385 | 491.9506 | 484.4525
2050.4729 | 382.6182 | 492.0058 | 484.2255
2051.4729 | 383.4417 | 492.7094 | 484.4675
2052.4729 | 383.4014 | 493.1807 | 484.755
2053.4729 | 383.6156 | 493.5622 | 484.4077
2054.4729 | 383.9783 | 492.9786 | 484.3595
2055.4729 | 383.8385 | 492.9298 | 484.3467
2056.4729 | 383.6447 | 492.963 | 484.4792
2057.4729 | 383.5215 | 492.8211 | 484.7279
2058.4729 | 383.5794 | 492.8048 | 484.8117
2059.4729 | 383.8339 | 492.841 | 484.9058
2060.4729 | 384.0874 | 493.3018 | 484.9777
2061.4729 | 384.4395 | 493.305 | 485.042
2062.4729 | 384.5403 | 493.2378 | 485.163
2063.4729 | 384.7596 | 493.4594 | 485.1337
2064.4729 | 384.6223 | 493.4558 | 485.247
2065.4729 | 384.7668 | 493.741 | 485.4
2066.4729 | 385.1158 | 494.2388 | 485.4534
2067.4729 | 385.59 | 494.0521 | 485.4911
2068.4729 | 385.9983 | 494.0818 | 485.5281
2069.4729 | 386.0926 | 494.1494 | 485.6449
2070.4729 | 386.2255 | 494.3869 | 485.7946
2071.4729 | 386.7895 | 495.5502 | 486.24
2072.4729 | 386.6484 | 494.7976 | 486.3138
2073.4729 | 386.4973 | 494.6764 | 486.4597
2074.4729 | 386.5092 | 494.6366 | 486.2718
2075.4729 | 386.8061 | 495.3984 | 486.3087
2076.4729 | 387.4258 | 495.2167 | 486.4216
2077.4729 | 387.2769 | 495.1871 | 486.75
2078.4729 | 387.4894 | 495.5482 | 486.5334
2079.4729 | 387.6025 | 495.5286 | 487.1401
2080.4729 | 387.5878 | 495.6121 | 487.15
2081.4729 | 387.8087 | 495.976 | 486.8632
2082.4729 | 387.9728 | 495.9759 | 486.8929
2083.4729 | 387.7926 | 496.3711 | 486.9972
2084.4729 | 388.0317 | 496.8113 | 487.3305
2085.4729 | 388.549 | 496.2831 | 487.107
2086.4729 | 388.3932 | 496.4899 | 487.8257
2087.4729 | 388.5971 | 496.3302 | 487.4892
2088.4729 | 388.5692 | 496.3187 | 487.5593
2089.4729 | 388.4651 | 496.1982 | 487.7161
2090.4729 | 388.7305 | 496.4596 | 487.4693
2091.4729 | 388.9876 | 496.6065 | 487.4677
2092.4729 | 388.9713 | 496.5309 | 487.7728
2093.4729 | 389.1141 | 496.4437 | 487.8001
2094.4729 | 389.1427 | 496.4364 | 487.8504
2095.4729 | 389.5961 | 497.0869 | 488.2388
2096.4729 | 389.9543 | 497.4371 | 488.1706
2097.4729 | 390.1292 | 497.2138 | 488.3686
2098.4729 | 390.088 | 497.2299 | 488.4837
2099.4729 | 389.9556 | 497.7913 | 488.3529
2100.4729 | 390.2787 | 497.6238 | 488.3849
2101.4729 | 390.5174 | 497.6354 | 488.6195
2102.4729 | 390.8506 | 498.4103 | 488.8836
2103.4729 | 390.9587 | 498.8288 | 488.8481
2104.4729 | 391.1408 | 499.4219 | 489.0983
2105.4729 | 391.1227 | 498.6013 | 488.9127
2106.4729 | 391.0135 | 498.5947 | 488.6892
2107.4729 | 391.3737 | 499.2042 | 489.0644
2108.4729 | 391.7757 | 499.3144 | 489.3377
2109.4729 | 391.6119 | 498.9781 | 489.6916
2110.4729 | 391.6699 | 498.86 | 489.791
2111.4729 | 391.5328 | 499.0222 | 491.2433
2112.4729 | 391.2272 | 498.7868 | 491.0384
2113.4729 | 391.3577 | 498.9576 | 490.3873
2114.4729 | 391.7541 | 499.4702 | 490.2078
2115.4729 | 391.8659 | 499.6458 | 491.1965
2116.4729 | 391.9671 | 499.374 | 490.9029
2117.4729 | 392.143 | 499.3885 | 490.8551
2118.4729 | 393.1717 | 499.8928 | 490.6896
2119.4729 | 393.1864 | 499.9032 | 490.8335
2120.4729 | 393.5192 | 499.9918 | 490.6875
2121.4729 | 393.6486 | 499.9987 | 490.8917
2122.4729 | 393.7834 | 499.9871 | 490.8056
2123.4729 | 393.6963 | 499.9702 | 490.6665
2124.4729 | 394.0389 | 500.4669 | 490.8054
2125.4729 | 394.4741 | 500.5833 | 491.0417
2126.4729 | 394.6294 | 500.4028 | 491.2721
2127.4729 | 394.4161 | 500.9217 | 491.3505
2128.4729 | 394.7204 | 501.3603 | 491.4096
2129.4729 | 395.0174 | 501.2255 | 491.1832
2130.4729 | 395.1626 | 501.3175 | 491.1515
2131.4729 | 395.2431 | 501.1968 | 491.6326
2132.4729 | 395.2996 | 501.2528 | 491.6195
2133.4729 | 395.5225 | 502.1747 | 491.726
2134.4729 | 395.6886 | 502.6725 | 492.1344
2135.4729 | 395.8163 | 504.6103 | 492.6395
2136.4729 | 395.9577 | 503.9342 | 492.3985
2137.4729 | 396.281 | 504.8606 | 492.9215
2138.4729 | 396.5695 | 503.6206 | 493.0548
2139.4729 | 396.7485 | 503.3816 | 492.6083
2140.4729 | 396.8178 | 503.2761 | 492.6497
2141.4729 | 396.9732 | 503.5369 | 492.7627
2142.4729 | 397.0644 | 503.6747 | 492.8604
2143.4729 | 397.2104 | 503.604 | 493.2198
2144.4729 | 397.1388 | 503.7069 | 493.0474
2145.4729 | 397.4479 | 504.2966 | 492.9565
2146.4729 | 397.6969 | 504.4305 | 492.9804
2147.4729 | 397.8785 | 504.204 | 493.0354
2148.4729 | 398.0621 | 504.2582 | 493.2002
2149.4729 | 397.6621 | 504.2059 | 493.092
2150.4729 | 397.6376 | 504.5969 | 493.2563
2151.4729 | 398.1371 | 504.6823 | 493.4818
2152.4729 | 398.0301 | 504.7147 | 493.5347
2153.4729 | 398.0599 | 504.5071 | 493.4041
2154.4729 | 398.1943 | 504.5084 | 493.6101
2155.4729 | 398.8696 | 504.9504 | 494.3547
2156.4729 | 398.9967 | 505.6691 | 493.7523
2157.4729 | 399.6095 | 505.7438 | 493.7765
2158.4729 | 399.4555 | 505.5169 | 493.7647
2159.4729 | 399.7172 | 505.4503 | 493.97
2160.4729 | 400.2169 | 505.5564 | 494.2575
2161.4729 | 400.0844 | 505.6677 | 494.2307
2162.4729 | 399.8829 | 506.0449 | 494.3784
2163.4729 | 399.811 | 505.8974 | 494.7323
2164.4729 | 399.9676 | 506.3676 | 494.3218
2165.4729 | 400.6852 | 507.1575 | 494.4237
2166.4729 | 401.04 | 507.2854 | 494.8333
2167.4729 | 401.106 | 506.991 | 495.0613
2168.4729 | 401.02 | 507.2145 | 494.7318
2169.4729 | 400.861 | 506.5506 | 494.8259
2170.4729 | 400.9519 | 506.5733 | 495.3856
2171.4729 | 401.2972 | 506.9566 | 495.0556
2172.4729 | 402.0594 | 507.2061 | 495.4132
2173.4729 | 401.9658 | 506.953 | 495.2856
2174.4729 | 401.8706 | 507.3005 | 495.5737
2175.4729 | 402.3341 | 507.7014 | 495.5288
2176.4729 | 402.9212 | 508.8278 | 495.7983
2177.4729 | 403.0797 | 508.6297 | 496.1207
2178.4729 | 403.5473 | 508.1189 | 495.8341
2179.4729 | 404.3529 | 508.13 | 495.9193
2180.4729 | 404.6388 | 508.014 | 496.3408
2181.4729 | 404.5175 | 508.7392 | 496.2749
2182.4729 | 404.2531 | 508.5649 | 496.4356
2183.4729 | 404.3285 | 508.8532 | 496.3906
2184.4729 | 404.5148 | 509.4038 | 496.582
2185.4729 | 404.9507 | 509.7154 | 496.5038
2186.4729 | 404.7403 | 508.8457 | 497.0717
2187.4729 | 404.6331 | 508.9159 | 496.7397
2188.4729 | 405.289 | 509.2647 | 497.1839
2189.4729 | 405.3649 | 509.4262 | 497.3318
2190.4729 | 405.5066 | 510.319 | 497.9784
2191.4729 | 405.3649 | 510.0179 | 498.1152
2192.4729 | 406.9921 | 509.531 | 497.9421
2193.4729 | 407.2936 | 509.8279 | 497.6207
2194.4729 | 407.0329 | 509.8595 | 497.6222
2195.4729 | 407.1663 | 510.9301 | 498.2221
2196.4729 | 407.2668 | 511.4581 | 498.3422
2197.4729 | 406.9571 | 511.7627 | 498.2634
2198.4729 | 407.2442 | 510.8277 | 498.2058
2199.4729 | 408.2771 | 511.9574 | 498.2763
2200.4729 | 408.5438 | 512.3096 | 498.1549
2201.4729 | 408.8169 | 511.397 | 497.9444
2202.4729 | 408.8699 | 511.4348 | 497.8936
2203.4729 | 409.3435 | 511.3685 | 498.0925
2204.4729 | 409.6023 | 512.1047 | 498.7914
2205.4729 | 409.7279 | 512.6689 | 498.6677
2206.4729 | 409.2746 | 512.0091 | 498.5117
2207.4729 | 410.3841 | 512.9821 | 498.5583
2208.4729 | 410.1468 | 512.6433 | 498.4668
2209.4729 | 409.8066 | 513.1699 | 498.5316
2210.4729 | 409.8427 | 513.3624 | 498.5097
2211.4729 | 410.2205 | 512.8661 | 498.5546
2212.4729 | 410.5783 | 513.7458 | 498.956
2213.4729 | 412.2697 | 514.4106 | 499.4263
2214.4729 | 412.0487 | 514.1693 | 498.9723
2215.4729 | 412.5373 | 513.7863 | 499.2481
2216.4729 | 412.5862 | 514.0764 | 500.3746
2217.4729 | 412.5804 | 514.6349 | 499.9744
2218.4729 | 412.6127 | 514.7038 | 500.0575
2219.4729 | 413.4607 | 514.3468 | 499.8237
2220.4729 | 413.7202 | 514.3163 | 499.8726
2221.4729 | 413.6166 | 514.4397 | 499.8216
2222.4729 | 413.2059 | 514.9252 | 499.9579
2223.4729 | 413.3699 | 514.7791 | 500.0179
2224.4729 | 413.5186 | 514.5655 | 500.4286
2225.4729 | 413.6216 | 514.5671 | 499.9782
2226.4729 | 414.1884 | 514.8708 | 499.941
2227.4729 | 414.7377 | 514.7623 | 499.8123
2228.4729 | 414.8606 | 515.1786 | 499.889
2229.4729 | 414.426 | 514.9296 | 500.0728
2230.4729 | 414.3709 | 514.9646 | 500.1811
2231.4729 | 414.2475 | 515.62 | 500.4788
2232.4729 | 414.2449 | 515.4547 | 500.8404
2233.4729 | 415.0227 | 515.7972 | 500.5464
2234.4729 | 415.6313 | 516.0012 | 500.3765
2235.4729 | 415.9795 | 516.2868 | 501.0114
2236.4729 | 416.0136 | 516.0139 | 500.9937
2237.4729 | 415.7483 | 516.0844 | 501.0961
2238.4729 | 415.8633 | 516.6971 | 501.4462
2239.4729 | 416.0969 | 516.2501 | 501.1547
2240.4729 | 415.9376 | 517.4525 | 501.5912
2241.4729 | 416.7638 | 517.1249 | 501.5202
2242.4729 | 417.0548 | 516.7329 | 501.5964
2243.4729 | 417.7727 | 516.7969 | 501.6659
2244.4729 | 418.4847 | 517.0321 | 502.0728
2245.4729 | 418.511 | 517.2347 | 502.0465
2246.4729 | 418.7054 | 517.4524 | 501.7122
2247.4729 | 417.9266 | 516.8823 | 501.6962
2248.4729 | 417.9833 | 517.0346 | 502.0188
2249.4729 | 418.4739 | 516.7573 | 501.8517
2250.4729 | 419.1501 | 516.9476 | 501.9435
2251.4729 | 419.481 | 517.2156 | 502.2098
2252.4729 | 420.205 | 517.1708 | 501.9382
2253.4729 | 419.9448 | 517.0409 | 501.9829
2254.4729 | 420.2087 | 517.4791 | 502.0733
2255.4729 | 420.9763 | 517.52 | 502.0901
2256.4729 | 421.3534 | 518.0259 | 502.1862
2257.4729 | 421.868 | 517.8676 | 502.1791
2258.4729 | 421.4168 | 517.4119 | 502.1899
2259.4729 | 421.2841 | 517.5326 | 502.0733
2260.4729 | 420.9646 | 517.5949 | 502.5982
2261.4729 | 420.869 | 517.6714 | 502.3882
2262.4729 | 421.622 | 517.6636 | 502.5164
2263.4729 | 422.5115 | 517.9647 | 502.483
2264.4729 | 422.515 | 518.0784 | 503.0026
2265.4729 | 422.5909 | 517.7683 | 503.0966
2266.4729 | 422.8961 | 517.8628 | 502.6206
2267.4729 | 423.1598 | 518.059 | 502.4892
2268.4729 | 424.0041 | 518.5607 | 502.922
2269.4729 | 423.993 | 518.374 | 503.1674
2270.4729 | 425.5151 | 518.4269 | 503.1837
2271.4729 | 425.8129 | 518.4252 | 503.577
2272.4729 | 425.2746 | 518.4942 | 503.2392
2273.4729 | 424.6396 | 518.8308 | 503.2754
2274.4729 | 424.8139 | 518.4167 | 503.3507
2275.4729 | 425.1776 | 518.77 | 503.3465
2276.4729 | 425.673 | 518.6709 | 503.1435
2277.4729 | 425.7233 | 518.4351 | 503.5214
2278.4729 | 425.3875 | 518.8756 | 503.7725
2279.4729 | 426.7987 | 519.3061 | 503.9012
2280.4729 | 426.2789 | 519.005 | 503.6936
2281.4729 | 426.9761 | 519.3605 | 503.9595
2282.4729 | 427.0908 | 520.3301 | 504.0546
2283.4729 | 426.9146 | 519.8267 | 504.1857
2284.4729 | 427.461 | 520.0354 | 504.0226
2285.4729 | 427.7786 | 519.5017 | 504.9374
2286.4729 | 428.263 | 519.7478 | 504.6076
2287.4729 | 428.637 | 520.6445 | 504.6817
2288.4729 | 428.2976 | 520.2314 | 504.7269
2289.4729 | 428.2515 | 520.3348 | 504.4968
2290.4729 | 428.6713 | 520.4155 | 504.6001
2291.4729 | 428.9157 | 521.7913 | 504.8179
2292.4729 | 429.2368 | 522.3063 | 504.8874
2293.4729 | 429.0223 | 521.9521 | 505.1234
2294.4729 | 428.9642 | 522.1825 | 505.1371
2295.4729 | 429.584 | 521.6713 | 505.2099
2296.4729 | 431.0956 | 521.5609 | 504.9738
2297.4729 | 430.5442 | 522.4765 | 505.1871
2298.4729 | 431.8663 | 523.4443 | 505.5319
2299.4729 | 432.5339 | 522.8424 | 505.2696
2300.4729 | 433.2107 | 523.811 | 506.0104
2301.4729 | 433.1128 | 523.4098 | 505.4192
2302.4729 | 433.1155 | 523.9951 | 505.2514
2303.4729 | 432.56 | 524.6809 | 505.8011
2304.4729 | 433.0227 | 523.7639 | 505.4305
2305.4729 | 432.8176 | 525.606 | 505.2812
2306.4729 | 432.8635 | 525.001 | 505.6798
2307.4729 | 433.4816 | 526.2979 | 505.9
2308.4729 | 434.2211 | 525.4683 | 506.1847
2309.4729 | 434.0088 | 525.1362 | 505.9468
2310.4729 | 434.2388 | 525.8085 | 506.6361
2311.4729 | 433.6645 | 526.0912 | 507.2402
2312.4729 | 434.5047 | 526.4558 | 507.0932
2313.4729 | 434.3104 | 525.7332 | 506.8056
2314.4729 | 434.3101 | 525.5023 | 506.8157
2315.4729 | 434.2073 | 525.3157 | 506.6368
2316.4729 | 434.1322 | 525.1944 | 506.6413
2317.4729 | 435.0933 | 525.2639 | 507.1103
2318.4729 | 435.6011 | 525.392 | 506.7956
2319.4729 | 435.654 | 525.4801 | 506.6927
2320.4729 | 435.5903 | 526.3642 | 507.0453
2321.4729 | 435.7901 | 526.1398 | 506.9062
2322.4729 | 436.4151 | 526.2943 | 507.1846
2323.4729 | 437.8827 | 525.7647 | 506.9442
2324.4729 | 439.1124 | 525.8011 | 506.9473
2325.4729 | 438.7652 | 525.9773 | 507.991
2326.4729 | 439.7772 | 526.4916 | 507.8414
2327.4729 | 439.4625 | 526.9553 | 507.4895
2328.4729 | 440.0614 | 526.3068 | 507.5777
2329.4729 | 440.488 | 526.8663 | 507.5465
2330.4729 | 440.1682 | 526.4809 | 507.2457
2331.4729 | 440.3596 | 527.3359 | 507.5083
2332.4729 | 439.7575 | 528.1472 | 507.4443
2333.4729 | 440.3279 | 529.2369 | 507.3965
2334.4729 | 440.4837 | 527.997 | 507.6856
2335.4729 | 441.1606 | 527.683 | 508.0753
2336.4729 | 441.0599 | 527.4586 | 507.8616
2337.4729 | 441.3215 | 527.0831 | 507.7184
2338.4729 | 441.5002 | 527.1311 | 507.7241
2339.4729 | 441.3053 | 527.232 | 507.5237
2340.4729 | 441.4899 | 527.284 | 507.7403
2341.4729 | 441.9726 | 527.3124 | 508.0972
2342.4729 | 442.0595 | 527.0831 | 507.6514
2343.4729 | 441.7907 | 527.1806 | 508.0607
2344.4729 | 441.4815 | 527.3759 | 508.0354
2345.4729 | 441.9815 | 527.2108 | 507.915
2346.4729 | 441.971 | 526.9388 | 507.8031
2347.4729 | 441.9696 | 526.6857 | 507.799
2348.4729 | 442.8913 | 526.5582 | 507.8145
2349.4729 | 443.2035 | 526.5763 | 507.8695
2350.4729 | 444.4619 | 526.7439 | 507.7164
2351.4729 | 443.6161 | 526.7307 | 508.0056
2352.4729 | 443.2815 | 527.3017 | 507.9155
2353.4729 | 444.1601 | 527.3516 | 507.7538
2354.4729 | 444.1793 | 527.0286 | 507.6432
2355.4729 | 443.8243 | 526.7106 | 507.44
2356.4729 | 444.5503 | 527.2908 | 507.9754
2357.4729 | 445.0917 | 526.8318 | 507.8406
2358.4729 | 445.3357 | 526.9143 | 508.0312
2359.4729 | 444.9061 | 526.7403 | 508.1528
2360.4729 | 444.6893 | 526.8705 | 508.3602
2361.4729 | 444.8337 | 527.1923 | 508.1512
2362.4729 | 444.9637 | 526.9677 | 507.8596
2363.4729 | 444.2909 | 527.0873 | 508.0311
2364.4729 | 445.1633 | 527.9713 | 509.266
2365.4729 | 445.9486 | 527.5861 | 508.6245
2366.4729 | 446.7153 | 527.3247 | 508.449
2367.4729 | 448.6309 | 527.039 | 509.1248
2368.4729 | 448.2456 | 526.9354 | 508.5974
2369.4729 | 448.3056 | 527.0435 | 508.6944
2370.4729 | 448.7581 | 526.8936 | 508.8248
2371.4729 | 448.0201 | 527.2584 | 509.1423
2372.4729 | 449.5526 | 526.7473 | 508.8
2373.4729 | 449.6214 | 526.8407 | 509.019
2374.4729 | 451.4844 | 526.8557 | 508.604
2375.4729 | 450.2688 | 527.4536 | 508.5842
2376.4729 | 449.5058 | 528.1858 | 508.7478
2377.4729 | 449.9481 | 527.7051 | 508.6451
2378.4729 | 450.6465 | 527.389 | 508.9688
2379.4729 | 450.5454 | 527.7325 | 509.3666
2380.4729 | 451.3221 | 527.3998 | 509.526
2381.4729 | 452.3321 | 529.0424 | 509.5169
2382.4729 | 451.8785 | 528.6501 | 509.5489
2383.4729 | 451.8171 | 528.8551 | 509.609
2384.4729 | 451.0885 | 529.0372 | 510.0824
2385.4729 | 451.6992 | 529.7898 | 509.7699
2386.4729 | 452.0216 | 529.6163 | 509.2827
2387.4729 | 452.2207 | 529.1397 | 509.1188
2388.4729 | 451.84 | 528.9796 | 509.1752
2389.4729 | 450.9922 | 528.7782 | 509.4496
2390.4729 | 452.2009 | 529.1636 | 509.7665
2391.4729 | 454.261 | 529.2119 | 509.8008
2392.4729 | 454.7652 | 529.5047 | 510.3166
2393.4729 | 454.0149 | 529.4536 | 510.2751
2394.4729 | 455.6586 | 529.9058 | 510.793
2395.4729 | 455.6765 | 531.0592 | 510.6693
2396.4729 | 455.0575 | 531.1616 | 510.4057
2397.4729 | 455.4924 | 530.1523 | 510.4236
2398.4729 | 456.6948 | 530.3843 | 511.2415
2399.4729 | 455.4814 | 530.0774 | 510.9449
2400.4729 | 455.4965 | 530.0573 | 511.0701
2401.4885 | 456.0018 | 529.6588 | 511.3266
2402.4729 | 455.9693 | 529.4733 | 510.9125
2403.4729 | 457.0338 | 529.8201 | 510.8188
2404.4729 | 457.7483 | 529.7194 | 510.9045
2405.4729 | 457.4072 | 529.593 | 510.9756
2406.4729 | 457.0963 | 529.8392 | 511.0187
2407.4729 | 457.5569 | 529.6834 | 511.0279
2408.4729 | 457.5073 | 530.8351 | 510.966
2409.4729 | 457.4737 | 531.5498 | 511.1208
2410.4729 | 457.5507 | 530.5654 | 511.4601
2411.4729 | 457.8864 | 530.1011 | 511.0833
2412.4729 | 458.3064 | 529.7991 | 511.0738
2413.4729 | 458.4454 | 529.925 | 510.862
2414.4729 | 458.007 | 529.7747 | 510.998
2415.4729 | 457.15 | 529.9509 | 511.0351
2416.4729 | 458.9579 | 529.6477 | 510.9111
2417.4729 | 459.3611 | 529.5367 | 511.0975
2418.4729 | 460.0488 | 529.5498 | 510.8923
2419.4729 | 459.6614 | 529.4861 | 511.0533
2420.4729 | 459.6985 | 529.6253 | 511.618
2421.4729 | 460.8362 | 529.6463 | 512.038
2422.4729 | 460.9351 | 529.5811 | 511.3438
2423.4729 | 460.2711 | 530.2337 | 511.3785
2424.4729 | 460.0632 | 530.3833 | 512.0273
2425.4729 | 459.8475 | 529.8326 | 511.6562
2426.4729 | 461.0028 | 529.9549 | 511.8821
2427.4729 | 462.3128 | 530.4464 | 511.6947
2428.4729 | 462.0049 | 529.979 | 511.416
2429.4729 | 462.9608 | 529.7806 | 511.328
2430.4729 | 462.6198 | 529.8249 | 511.3352
2431.4729 | 462.9427 | 530.052 | 511.5739
2432.4729 | 463.5375 | 529.8194 | 511.4561
2433.4729 | 463.1929 | 529.8867 | 511.4238
2434.4729 | 463.1193 | 529.7869 | 511.901
2435.4729 | 463.3925 | 529.6865 | 511.6558
2436.4729 | 463.958 | 529.5238 | 511.7238
2437.4729 | 463.1901 | 529.5531 | 512.013
2438.4729 | 462.9417 | 529.3998 | 511.796
2439.4729 | 463.4472 | 529.182 | 511.4937
2440.4729 | 463.9662 | 529.2524 | 511.4402
2441.4729 | 463.8831 | 529.0787 | 511.5729
2442.4729 | 464.0207 | 528.8427 | 511.5595
2443.4729 | 464.6164 | 528.7487 | 511.5806
2444.4729 | 465.5217 | 528.8837 | 511.766
2445.4729 | 466.7635 | 528.8777 | 511.7019
2446.4729 | 467.0457 | 529.2187 | 511.6488
2447.4729 | 466.5572 | 529.1939 | 511.8712
2448.4729 | 467.3474 | 529.0815 | 511.7424
2449.4729 | 467.4469 | 529.5852 | 511.5658
2450.4729 | 467.2155 | 529.5706 | 511.4569
2451.4729 | 466.3092 | 529.2332 | 511.5291
2452.4729 | 467.8529 | 529.2145 | 511.864
2453.4729 | 467.9512 | 529.6758 | 512.0803
2454.4729 | 468.279 | 529.2074 | 511.8282
2455.4729 | 469.9104 | 529.9823 | 512.0066
2456.4729 | 468.6957 | 530.1805 | 512.6835
2457.4729 | 470.6708 | 530.326 | 512.5537
2458.4729 | 469.8176 | 530.2841 | 512.3151
2459.4729 | 469.0697 | 530.5951 | 512.4176
2460.4729 | 469.4877 | 530.5477 | 513.1058