## Test Conditions
DESIREE-FIRE Intermediate Scale Test Number 6 - Circuit Simulator Data Only
Test Date: | 2010-03-03
DCSim DAQ Start Time | 13:38
DCSim Time for Synchronization | 14:06
Heat Source Synchronization | 0:00 | hour:minutes:seconds
Heat Source DAQ Start Time | 14:05
Fire Time | 14:34
Offset | 0:56 | hour:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 3360 | seconds
Heat Source Offset | 0:29 | hour:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 1740 | seconds
Heat Source Stop Time | 15:15
Test Duration | 0:41 | hour:minutes:seconds
| 2460 | seconds
CT500 turns | 2 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 turns | 5 | 1 or 5
Pre-Test Baseline: | Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit number | Cable Type |  | Cable TC channel | Air TC Channel
MOV 1 | PE/PVC, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 5, 6, and 7 represents the air temperature 3', 5', and 7' down the tray located in C Position. These are labeled as "C Position - 3'", "C Position - Middle", "C Position - 7'", respectively.
MOV 2 | PE/PVC, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 0 represents the air temperature at the center of the tray located in A Position. Is it labeled as "A Position - Middle".
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | MOV-1_CT500 | MOV-1a_CT35_1_P | MOV-1a_CT35_2_N | MOV-1b_CT35_1_G | MOV-1b_CT35_2_R | MOV-1b_CT35_3_YO | MOV-1b_CT35_4_YC | MOV-2_CT500 | MOV-2a_CT35_1_P | MOV-2a_CT35_2_N | MOV-2b_CT35_1_G | MOV-2b_CT35_2_R | MOV-2b_CT35_3_YO | 2b_CT35_4_YC1 | MOV-1a_VT7_1_SP | MOV-1a_VTU_1_P | MOV-1a_VTU_2_N | MOV-1b_VT7_1_G | MOV-1b_VT7_2_R | MOV-1b_VT7_3_YO1 | MOV-1b_VT7_4_YC1 | MOV-2a_VT7_1_SP | MOV-2a_VTU_1_P | MOV-2a_VTU_2_N | MOV-2b_VT7_1_G | MOV-2b_VT7_2_R | 2b_VT7_3_YO1 | MOV-2b_VT7_4_YC1 | {MOV1} V(N) - V(Batt -) | {MOV1} V(P) - V(Batt +) | {MOV1} V(G) - V(Batt +) | {MOV1} V(R) - V(Batt -) | {MOV1} V(YC1) - V(Batt -) | {MOV1} V(YO1) - V(Batt -) | {MOV1} V(YC1) - V(N) | {MOV1} V(YO1) - V(N) | {MOV2} V(N) - V(Batt -) | {MOV2} V(P) - V(Batt +) | {MOV2} V(G) - V(Batt +) | {MOV2} V(R) - V(Batt -) | {MOV2} V(YC1) - V(Batt -) | {MOV2} V(YO1) - V(Batt -) | {MOV2} V(YC1) - V(N) | {MOV2} V(YO1) - V(N) | {MOV-1} V(R) - V(N) | {MOV-1} V(G) - V(N) | {MOV-2} V(R) - V(N) | {MOV-2} V(G) - V(N) | {MOV-1} V(P) - V(N) | {MOV-2} V(P) - V(N) | {MOV-1} V(P) - V(Batt -) | {MOV-2} V(P) - V(Batt -) | {MOV-1} V(N) - V(Batt +) | {MOV-2} V(N) - V(Batt +) | {MOV-1} V(G) - V(Batt -) | {MOV2} V(G) - V(Batt-) | {MOV1} V(SP) - V(Batt -) | {MOV2} V(SP) - V(Batt -)
-0.96875 | 123.587 | -61.6653 | 61.6882 | -0.0041962 | 0.0049646 | 0.068945 | 0.065273 | 0.0058725 | -0.0019333 | -0.00077335 | 0.0046998 | -0.00021141 | 0.070128 | 0.061041 | -0.00025213 | 0.0097326 | -0.00012381 | -0.022888 | 61.7523 | -61.8256 | 61.6425 | -61.3129 | -61.7157 | -61.7569 | 0.082397 | 61.6608 | -61.7065 | 61.7615 | -61.5189 | -61.5097 | -61.3907 | -0.16022 | 0.064087 | -0.045776 | 0.35248 | -0.091553 | -0.050354 | 0.068665 | 0.10986 | -0.041199 | -0.027465 | 0.073243 | 0.14648 | 0.27466 | 0.15564 | 0.31586 | 0.19684 | 0.5127 | 123.468 | 0.18768 | 123.468 | 123.5779 | 123.3673 | 123.4177 | 123.3261 | -123.5138 | -123.3948 | 123.3078 | 123.4268 | 61.6425 | 61.7477
0.70312 | 123.5001 | -61.7157 | 61.6608 | 0.04158 | 0.0051782 | 0.068731 | 0.067195 | 0.0041635 | -0.0036423 | 0.00072205 | 0.013855 | 0.0047018 | 0.070342 | 0.050146 | -0.00025213 | 0.0082374 | -0.0026874 | -0.009155 | 61.8027 | -61.908 | 61.5555 | -61.4777 | -61.8301 | -61.8668 | -0.050354 | 61.6882 | -61.7844 | 61.6287 | -61.6379 | -61.6562 | -61.496 | -0.19226 | 0.14191 | -0.10529 | 0.23804 | -0.15106 | -0.11444 | 0.041199 | 0.07782 | -0.068665 | 0.027465 | -0.032044 | 0.07782 | 0.21973 | 0.059509 | 0.28839 | 0.12817 | 0.4303 | 123.4634 | 0.14648 | 123.4131 | 123.7106 | 123.4726 | 123.5184 | 123.4039 | -123.5687 | -123.4451 | 123.2712 | 123.3444 | 61.7065 | 61.6653
2.4375 | 123.4543 | -61.7157 | 61.7157 | -0.0041962 | 0.0041102 | 0.069372 | 0.064418 | 0.0033089 | -0.0021469 | -0.00055975 | 0.019959 | 0.005129 | 0.072478 | 0.056982 | -0.0055927 | 0.0080236 | -0.00033761 | -0.082397 | 61.8073 | -61.8759 | 61.4914 | -61.4868 | -61.8347 | -61.8576 | -0.050354 | 61.7065 | -61.7798 | 61.6196 | -61.6699 | -61.6699 | -61.5143 | -0.16022 | 0.091553 | -0.2243 | 0.22888 | -0.14191 | -0.11902 | 0.018311 | 0.041199 | -0.064087 | -0.009155 | -0.09613 | 0.045776 | 0.20142 | 0.045776 | 0.2655 | 0.10986 | 0.3891 | 123.3673 | 0.10986 | 123.3994 | 123.6832 | 123.4863 | 123.5229 | 123.4222 | -123.5916 | -123.4955 | 123.2071 | 123.3353 | 61.6333 | 61.6653
4.1562 | 123.5184 | -61.6974 | 61.6882 | 0.04158 | 0.0038966 | 0.069372 | 0.06805 | 0.0043771 | -0.0012925 | -0.0012006 | 0.02301 | 0.0042746 | 0.069701 | 0.054846 | -0.00089293 | 0.009519 | 0.0017988 | -0.045776 | 61.8073 | -61.8942 | 61.5234 | -61.4685 | -61.8576 | -61.8576 | -0.059509 | 61.7065 | -61.8027 | 61.6333 | -61.6562 | -61.6608 | -61.5005 | -0.19684 | 0.11902 | -0.16479 | 0.22888 | -0.16022 | -0.16022 | 0.036621 | 0.036621 | -0.10529 | 0.018311 | -0.054931 | 0.041199 | 0.19684 | 0.036621 | 0.30212 | 0.14191 | 0.42572 | 123.4177 | 0.14648 | 123.436 | 123.7015 | 123.5092 | 123.5046 | 123.4039 | -123.5825 | -123.4909 | 123.2208 | 123.3307 | 61.6516 | 61.6379
5.8906 | 123.5779 | -61.6653 | 61.6608 | 0.04921 | 0.00646 | 0.071295 | 0.068477 | 0.0030953 | -1.0686e-05 | 0.00072205 | 0.013855 | 0.0025656 | 0.070555 | 0.066808 | 0.0020979 | 0.009519 | 0.0024396 | -0.050354 | 61.7661 | -61.8576 | 61.6241 | -61.3449 | -61.7706 | -61.7889 | 0.059509 | 61.6196 | -61.7615 | 61.7386 | -61.5555 | -61.5692 | -61.4227 | -0.19226 | 0.10529 | -0.036621 | 0.32043 | -0.1236 | -0.10529 | 0.068665 | 0.086975 | -0.096131 | -0.041199 | 0.077819 | 0.10986 | 0.24262 | 0.09613 | 0.33875 | 0.19226 | 0.5127 | 123.4818 | 0.20599 | 123.5001 | 123.6237 | 123.381 | 123.4314 | 123.2849 | -123.5184 | -123.4222 | 123.2895 | 123.4039 | 61.615 | 61.7249
7.5781 | 123.5321 | -61.647 | 61.6516 | 0.033951 | 0.0073144 | 0.073858 | 0.065486 | 0.00095914 | -0.00022429 | 0.00072205 | 0.016907 | 0.0042746 | 0.067351 | 0.06574 | -0.0015337 | 0.010374 | -0.0018328 | -0.07782 | 61.7249 | -61.8759 | 61.5967 | -61.3586 | -61.7935 | -61.7981 | 0.032043 | 61.6516 | -61.7844 | 61.7157 | -61.5829 | -61.5784 | -61.441 | -0.22888 | 0.073243 | -0.054931 | 0.28839 | -0.15106 | -0.14648 | 0.07782 | 0.082398 | -0.13733 | 0 | 0.064087 | 0.064087 | 0.20599 | 0.068665 | 0.34332 | 0.20599 | 0.51727 | 123.4726 | 0.20142 | 123.5001 | 123.6008 | 123.436 | 123.3719 | 123.2986 | -123.5275 | -123.436 | 123.2437 | 123.3627 | 61.5692 | 61.6791
9.3125 | 123.5229 | -61.6562 | 61.6745 | 0.026321 | 0.001333 | 0.068517 | 0.065273 | 0.0024545 | -0.0025741 | -0.0016278 | 0.0077514 | 0.0014976 | 0.068633 | 0.060827 | -0.0019611 | 0.0099462 | -0.00461 | -0.09613 | 61.7889 | -61.8484 | 61.5692 | -61.4136 | -61.8118 | -61.8256 | -0.050354 | 61.6653 | -61.7249 | 61.6928 | -61.6058 | -61.5875 | -61.4548 | -0.19226 | 0.11444 | -0.10529 | 0.24262 | -0.16937 | -0.15564 | 0.022888 | 0.036621 | -0.068665 | -0.009156 | 0.01831 | 0.050354 | 0.20142 | 0.068665 | 0.27008 | 0.13733 | 0.43488 | 123.4177 | 0.11902 | 123.4177 | 123.6374 | 123.3902 | 123.4451 | 123.3215 | -123.523 | -123.3994 | 123.2254 | 123.349 | 61.5601 | 61.6058
11.0469 | 123.4543 | -61.7249 | 61.6745 | 0.018692 | 0.0073144 | 0.070654 | 0.067409 | 0.0048043 | -0.0012925 | 0.0013628 | -0.0014038 | 0.0027792 | 0.071624 | 0.060827 | -0.00025213 | 0.0088782 | -0.0050372 | -0.036621 | 61.7661 | -61.8988 | 61.5234 | -61.4594 | -61.8805 | -61.8988 | -0.050354 | 61.647 | -61.7706 | 61.6104 | -61.7111 | -61.7065 | -61.528 | -0.17395 | 0.091552 | -0.15106 | 0.2655 | -0.17395 | -0.15564 | 0 | 0.018311 | -0.045776 | -0.027466 | -0.064087 | 0.013733 | 0.19684 | 0.018311 | 0.24261 | 0.064087 | 0.43945 | 123.4222 | 0.059509 | 123.381 | 123.6649 | 123.4177 | 123.4909 | 123.3719 | -123.5733 | -123.4451 | 123.2483 | 123.3353 | 61.6882 | 61.6745
12.7188 | 123.4818 | -61.702 | 61.6882 | 0.026321 | 0.0060328 | 0.070013 | 0.066768 | 0.0058725 | -0.0019333 | 0.00029485 | 0.0077514 | 0.0038474 | 0.069487 | 0.051428 | -0.0030291 | 0.0093054 | -0.0014056 | -0.013733 | 61.7615 | -61.8988 | 61.5372 | -61.4594 | -61.8576 | -61.8622 | -0.004578 | 61.6608 | -61.7935 | 61.6425 | -61.6425 | -61.6745 | -61.5005 | -0.19684 | 0.073243 | -0.15106 | 0.24261 | -0.16022 | -0.15564 | 0.036621 | 0.041199 | -0.091553 | -0.027465 | -0.045776 | 0.059509 | 0.20142 | 0.027465 | 0.29297 | 0.11902 | 0.43945 | 123.436 | 0.15106 | 123.436 | 123.6603 | 123.4543 | 123.4634 | 123.3627 | -123.587 | -123.4818 | 123.2391 | 123.3444 | 61.6882 | 61.6974
14.4531 | 123.4131 | -61.7203 | 61.6791 | 0.011063 | 0.00646 | 0.068517 | 0.066127 | 0.0037363 | -0.0032151 | -0.0024824 | 0.001648 | 0.0047018 | 0.069487 | 0.06339 | 0.0010297 | 0.0097326 | 0.0043622 | -0.10071 | 61.7569 | -61.908 | 61.4685 | -61.5326 | -61.9446 | -61.9492 | -0.12817 | 61.6425 | -61.7752 | 61.5738 | -61.7294 | -61.7249 | -61.5326 | -0.18768 | 0.07782 | -0.21057 | 0.18768 | -0.22888 | -0.2243 | -0.041199 | -0.036621 | -0.054932 | -0.036621 | -0.10529 | -0.009155 | 0.18768 | -0.004578 | 0.24262 | 0.050354 | 0.37537 | 123.3765 | 0.045777 | 123.349 | 123.6649 | 123.4177 | 123.4772 | 123.3627 | -123.587 | -123.4543 | 123.1888 | 123.2941 | 61.6196 | 61.5921
16.1875 | 123.4634 | -61.7157 | 61.6425 | 0.0034333 | 0.0053918 | 0.070013 | 0.066982 | 0.0026681 | 0.0016983 | -0.003764 | 0.0046998 | 0.0034202 | 0.072692 | 0.059759 | 0.0012433 | 0.0069556 | 0.0035078 | -0.12817 | 61.7661 | -61.8988 | 61.4365 | -61.5372 | -61.9492 | -61.9308 | -0.13275 | 61.6425 | -61.7981 | 61.6013 | -61.7157 | -61.7065 | -61.5326 | -0.18311 | 0.1236 | -0.20599 | 0.17853 | -0.21515 | -0.23346 | -0.032043 | -0.050354 | -0.082398 | 0 | -0.041199 | 0 | 0.18311 | 0.009155 | 0.2655 | 0.091553 | 0.36163 | 123.3353 | 0.082398 | 123.3994 | 123.6649 | 123.4406 | 123.4818 | 123.3582 | -123.5413 | -123.4406 | 123.1522 | 123.317 | 61.5875 | 61.5829
17.9375 | 123.4314 | -61.6837 | 61.7157 | 0.0034333 | 0.0049646 | 0.069799 | 0.064204 | 0.0026681 | -0.0042831 | -0.0012006 | 0.001648 | 0.0025656 | 0.069274 | 0.059332 | -0.0028155 | 0.009519 | 8.9786e-05 | -0.09613 | 61.7981 | -61.8713 | 61.4685 | -61.4822 | -61.8484 | -61.8622 | -0.086975 | 61.6791 | -61.7523 | 61.6058 | -61.6653 | -61.6425 | -61.5143 | -0.18768 | 0.082398 | -0.24719 | 0.20142 | -0.17853 | -0.16479 | 0.009155 | 0.022888 | -0.068664 | -0.036621 | -0.10986 | 0.018311 | 0.16937 | 0.041199 | 0.23804 | 0.10986 | 0.3891 | 123.3398 | 0.086975 | 123.3582 | 123.6694 | 123.4314 | 123.4818 | 123.3627 | -123.587 | -123.468 | 123.1522 | 123.2895 | 61.5875 | 61.5967
19.6094 | 123.5596 | -61.6562 | 61.6333 | 0.011063 | 0.0051782 | 0.069799 | 0.064418 | 0.0028817 | -1.0686e-05 | 0.00029485 | -0.0014038 | 0.00064299 | 0.067992 | 0.068304 | 0.0038067 | 0.010374 | 0.00073059 | -0.064087 | 61.7111 | -61.8347 | 61.5692 | -61.3861 | -61.821 | -61.821 | -0.009155 | 61.6013 | -61.7615 | 61.7249 | -61.5875 | -61.5692 | -61.4182 | -0.17853 | 0.07782 | -0.064087 | 0.27008 | -0.1648 | -0.1648 | 0.013733 | 0.013733 | -0.10529 | -0.032044 | 0.091553 | 0.068665 | 0.23804 | 0.086975 | 0.34332 | 0.19226 | 0.44861 | 123.4039 | 0.17395 | 123.4863 | 123.5458 | 123.3627 | 123.3673 | 123.2574 | -123.468 | -123.3948 | 123.2254 | 123.381 | 61.5921 | 61.647
21.3438 | 123.468 | -61.6837 | 61.6745 | 0.033951 | 0.0049646 | 0.06809 | 0.0657 | 0.0077951 | 0.00020291 | 0.0020038 | 0.010803 | 0.0012838 | 0.069915 | 0.063604 | -0.0030291 | 0.0080236 | 0.001585 | -0.032043 | 61.8256 | -61.9263 | 61.5326 | -61.4365 | -61.8118 | -61.8393 | -0.027466 | 61.6837 | -61.7889 | 61.6241 | -61.6425 | -61.6379 | -61.4868 | -0.24262 | 0.15106 | -0.14191 | 0.24719 | -0.15564 | -0.12817 | 0.086976 | 0.11444 | -0.10528 | 0.009155 | -0.050354 | 0.041199 | 0.19684 | 0.045777 | 0.30212 | 0.15106 | 0.48981 | 123.4589 | 0.14648 | 123.4131 | 123.7518 | 123.4726 | 123.5092 | 123.3673 | -123.6008 | -123.4634 | 123.2162 | 123.3078 | 61.6516 | 61.6562
23.0156 | 123.4497 | -61.7111 | 61.6562 | 0.0034333 | 0.004751 | 0.068304 | 0.067409 | 0.0054453 | -0.0017197 | -0.0016278 | -0.0014038 | 0.0032064 | 0.071196 | 0.062963 | -0.00089293 | 0.011014 | -0.0035418 | -0.10986 | 61.7523 | -61.8896 | 61.4365 | -61.5509 | -61.9583 | -61.94 | -0.13275 | 61.6425 | -61.7981 | 61.5692 | -61.734 | -61.7065 | -61.5326 | -0.17853 | 0.09613 | -0.21973 | 0.16022 | -0.22888 | -0.24719 | -0.050354 | -0.068665 | -0.086975 | -0.013733 | -0.086975 | -0.022888 | 0.17853 | 0.004578 | 0.2655 | 0.091553 | 0.33875 | 123.3261 | 0.064087 | 123.3673 | 123.642 | 123.4406 | 123.4634 | 123.3536 | -123.5458 | -123.4543 | 123.1476 | 123.2803 | 61.6013 | 61.5784
24.7344 | 123.436 | -61.6928 | 61.6379 | -0.0041962 | 0.0060328 | 0.070013 | 0.069118 | 0.0048043 | -0.00065149 | -0.0033368 | -0.0014038 | 0.0036338 | 0.067992 | 0.059332 | 0.00060247 | 0.0086646 | 8.9786e-05 | -0.082397 | 61.7615 | -61.8988 | 61.4456 | -61.528 | -61.9354 | -61.9354 | -0.10071 | 61.6287 | -61.7798 | 61.5692 | -61.7065 | -61.7203 | -61.5234 | -0.20599 | 0.1236 | -0.19226 | 0.16479 | -0.24262 | -0.24262 | -0.036621 | -0.036621 | -0.086975 | -0.009155 | -0.068664 | -0.013733 | 0.16937 | -0.027466 | 0.25635 | 0.059509 | 0.37079 | 123.3444 | 0.073242 | 123.349 | 123.6603 | 123.4085 | 123.4543 | 123.3215 | -123.5367 | -123.4177 | 123.1384 | 123.262 | 61.6104 | 61.5921
26.4688 | 123.5733 | -61.6287 | 61.6653 | 0.0034333 | 0.0028284 | 0.070654 | 0.062282 | 0.00095914 | -0.0010789 | -0.0031232 | 0.001648 | 0.00085659 | 0.068206 | 0.068304 | -0.0015337 | 0.0097326 | 0.00030339 | -0.041199 | 61.7569 | -61.8347 | 61.615 | -61.29 | -61.702 | -61.7157 | 0.082397 | 61.6333 | -61.6974 | 61.7615 | -61.4868 | -61.4777 | -61.377 | -0.20599 | 0.091553 | -0.050354 | 0.33875 | -0.086975 | -0.073242 | 0.11902 | 0.13275 | -0.068665 | -0.032043 | 0.096131 | 0.14191 | 0.25177 | 0.15106 | 0.32043 | 0.21973 | 0.54474 | 123.4497 | 0.21057 | 123.4589 | 123.5916 | 123.3307 | 123.3856 | 123.262 | -123.5001 | -123.3627 | 123.2437 | 123.3902 | 61.5875 | 61.7111
28.2031 | 123.4772 | -61.6974 | 61.6425 | 0.026321 | 0.0090234 | 0.069586 | 0.067409 | 0.0035227 | -0.0021469 | -0.00034615 | 0.0077514 | 0.0036338 | 0.067778 | 0.059972 | -0.0017475 | 0.0088782 | -0.0026874 | -0.004578 | 61.7569 | -61.8942 | 61.5189 | -61.441 | -61.8393 | -61.8256 | -0.009155 | 61.6653 | -61.7615 | 61.647 | -61.6425 | -61.6287 | -61.4731 | -0.19684 | 0.11444 | -0.1236 | 0.25635 | -0.12817 | -0.14191 | 0.068664 | 0.054932 | -0.064087 | 0.022888 | 0.004578 | 0.054932 | 0.2243 | 0.068665 | 0.28839 | 0.13275 | 0.45319 | 123.4131 | 0.11902 | 123.4085 | 123.6511 | 123.4268 | 123.4543 | 123.3627 | -123.5367 | -123.4039 | 123.2162 | 123.3444 | 61.6928 | 61.6882
29.9375 | 123.468 | -61.6882 | 61.6608 | 0.033951 | 0.0077418 | 0.067877 | 0.067195 | 0.0060861 | -0.0040695 | 0.0013628 | 0.010803 | 0.0038474 | 0.069487 | 0.058904 | 0.0012433 | 0.0082374 | -0.0016192 | -0.027466 | 61.7661 | -61.908 | 61.5234 | -61.4273 | -61.8393 | -61.8668 | 0 | 61.6425 | -61.7523 | 61.6425 | -61.6516 | -61.6379 | -61.4868 | -0.21973 | 0.10529 | -0.13733 | 0.26093 | -0.17853 | -0.15106 | 0.041199 | 0.068665 | -0.064087 | -0.018311 | -0.018311 | 0.036621 | 0.20142 | 0.050354 | 0.2655 | 0.11444 | 0.48065 | 123.4314 | 0.10071 | 123.3948 | 123.674 | 123.3948 | 123.4543 | 123.3307 | -123.5687 | -123.4131 | 123.2117 | 123.3307 | 61.6608 | 61.6882
31.6094 | 123.5367 | -61.6608 | 61.6379 | 0.011063 | 0.0049646 | 0.069799 | 0.064845 | 0.0062997 | -0.00065149 | -0.00055975 | 0.001648 | 0.0029928 | 0.067992 | 0.061254 | 0.00038887 | 0.010801 | -0.00033761 | -0.10529 | 61.7249 | -61.8713 | 61.5234 | -61.4365 | -61.8393 | -61.8668 | -0.032043 | 61.5921 | -61.7249 | 61.6882 | -61.6013 | -61.5875 | -61.4182 | -0.21057 | 0.086976 | -0.11444 | 0.22431 | -0.20599 | -0.17853 | 0.004578 | 0.032044 | -0.064087 | -0.045776 | 0.050354 | 0.05951 | 0.24262 | 0.073243 | 0.3067 | 0.13733 | 0.43488 | 123.3948 | 0.1236 | 123.4131 | 123.5962 | 123.317 | 123.3856 | 123.2529 | -123.5092 | -123.3627 | 123.1842 | 123.349 | 61.5555 | 61.6287
33.3438 | 123.4818 | -61.647 | 61.7111 | -0.0041962 | 0.0024012 | 0.067877 | 0.064632 | 0.0022409 | -0.0019333 | 0.002431 | -0.0014038 | 0.0014976 | 0.069701 | 0.058691 | -0.0032427 | 0.0097326 | 0.00030339 | -0.032043 | 61.7386 | -61.8164 | 61.6058 | -61.3403 | -61.734 | -61.7706 | 0.036621 | 61.647 | -61.702 | 61.6882 | -61.5601 | -61.5463 | -61.4319 | -0.16937 | 0.027465 | -0.10529 | 0.3067 | -0.1236 | -0.086975 | 0.045776 | 0.082397 | -0.054931 | -0.064087 | -0.022889 | 0.086975 | 0.21515 | 0.10071 | 0.27008 | 0.15564 | 0.47607 | 123.4222 | 0.14191 | 123.3902 | 123.555 | 123.349 | 123.3856 | 123.2941 | -123.5275 | -123.4131 | 123.2529 | 123.3353 | 61.615 | 61.6837
35.0156 | 123.5275 | -61.6287 | 61.647 | 0.033951 | 0.0060328 | 0.070226 | 0.066768 | 0.0084359 | -0.0012925 | -0.0012006 | 0.019959 | 0.0034202 | 0.068419 | 0.056127 | 0.00060247 | 0.0093054 | 0.00051699 | -0.054932 | 61.7569 | -61.8301 | 61.5875 | -61.3449 | -61.7798 | -61.7889 | 0.032043 | 61.6196 | -61.7432 | 61.6928 | -61.5784 | -61.5555 | -61.4319 | -0.20142 | 0.10986 | -0.05951 | 0.28381 | -0.16022 | -0.15106 | 0.041199 | 0.050354 | -0.11444 | -0.027466 | 0.045776 | 0.050354 | 0.19684 | 0.073242 | 0.31128 | 0.18768 | 0.48523 | 123.4177 | 0.16479 | 123.436 | 123.587 | 123.3627 | 123.3856 | 123.2483 | -123.4772 | -123.3902 | 123.2162 | 123.3215 | 61.5738 | 61.6608
36.75 | 123.4497 | -61.6882 | 61.647 | 0.026321 | 0.0073144 | 0.069586 | 0.064845 | 0.0060861 | -0.0030015 | -0.0035504 | 0.0077514 | 0.0044882 | 0.068846 | 0.064886 | -0.0021747 | 0.0082374 | -0.0039692 | -0.018311 | 61.7477 | -61.8759 | 61.5097 | -61.4365 | -61.8439 | -61.8576 | 0.022888 | 61.6241 | -61.7661 | 61.647 | -61.6333 | -61.6333 | -61.4731 | -0.18768 | 0.10071 | -0.13733 | 0.25177 | -0.16937 | -0.15564 | 0.018311 | 0.032044 | -0.07782 | -0.022888 | 0 | 0.054931 | 0.21515 | 0.054931 | 0.29297 | 0.13275 | 0.43945 | 123.3856 | 0.13275 | 123.4131 | 123.6237 | 123.3902 | 123.436 | 123.3124 | -123.5229 | -123.4131 | 123.1979 | 123.3353 | 61.6699 | 61.7111
38.4219 | 123.5046 | -61.6196 | 61.6791 | -0.0041962 | 0.0045374 | 0.065527 | 0.06335 | 0.0069405 | -0.0019333 | 0.00050845 | -0.0014038 | 0.00085659 | 0.069487 | 0.059972 | -0.0017475 | 0.010374 | 8.9786e-05 | -0.013733 | 61.7386 | -61.8301 | 61.6104 | -61.3312 | -61.7477 | -61.7432 | 0.036621 | 61.647 | -61.6882 | 61.702 | -61.528 | -61.5097 | -61.3815 | -0.21057 | 0.059509 | -0.068664 | 0.28839 | -0.1236 | -0.12817 | 0.086975 | 0.082397 | -0.068664 | -0.032043 | 0.022888 | 0.091553 | 0.23804 | 0.10986 | 0.3067 | 0.17853 | 0.49896 | 123.4406 | 0.16022 | 123.3902 | 123.5687 | 123.3353 | 123.3582 | 123.2666 | -123.5092 | -123.3673 | 123.23 | 123.3215 | 61.6058 | 61.6562
40.0781 | 123.4909 | -61.6562 | 61.6745 | 0.026321 | 0.0077418 | 0.069158 | 0.064632 | 0.00053194 | -0.00022429 | -0.0014142 | 0.0077514 | 0.0019248 | 0.069915 | 0.067236 | -0.00025213 | 0.0093054 | -0.00012381 | -0.068665 | 61.7477 | -61.8118 | 61.5646 | -61.377 | -61.7889 | -61.8027 | -0.027466 | 61.6562 | -61.7203 | 61.6837 | -61.5921 | -61.5601 | -61.4227 | -0.15564 | 0.073242 | -0.10986 | 0.27924 | -0.14648 | -0.13275 | 0.009156 | 0.022889 | -0.064087 | -0.018311 | 0.009155 | 0.064087 | 0.23346 | 0.09613 | 0.29755 | 0.16022 | 0.43488 | 123.3765 | 0.12817 | 123.4039 | 123.5596 | 123.3765 | 123.4039 | 123.3124 | -123.4863 | -123.3948 | 123.2208 | 123.3398 | 61.5875 | 61.6287
41.8125 | 123.5321 | -61.6653 | 61.6241 | 0.0034333 | 0.0060328 | 0.068945 | 0.0657 | 0.012708 | 0.00020291 | -0.00013235 | 0.0046998 | 0.0029928 | 0.068633 | 0.062536 | 0.0048749 | 0.00781 | 0.001585 | -0.10529 | 61.7523 | -61.8576 | 61.5051 | -61.4502 | -61.8668 | -61.8484 | -0.036621 | 61.6333 | -61.7386 | 61.6745 | -61.6104 | -61.5921 | -61.4136 | -0.19226 | 0.12817 | -0.11902 | 0.21515 | -0.18311 | -0.20142 | 0.009155 | -0.009155 | -0.073242 | 0.009155 | 0.050354 | 0.054931 | 0.25177 | 0.073242 | 0.32501 | 0.14648 | 0.40741 | 123.3627 | 0.12817 | 123.4131 | 123.6099 | 123.3719 | 123.4177 | 123.2986 | -123.4818 | -123.3627 | 123.1705 | 123.3398 | 61.5601 | 61.6287
43.5469 | 123.4772 | -61.6196 | 61.6974 | 0.011063 | 0.0041102 | 0.070654 | 0.063136 | 0.0043771 | -0.0030015 | 0.0013628 | 0.0046998 | 0.0012838 | 0.069274 | 0.059118 | -0.0017475 | 0.011014 | 0.00094419 | -0.022888 | 61.7294 | -61.8301 | 61.6013 | -61.3403 | -61.734 | -61.7477 | 0.032043 | 61.6516 | -61.702 | 61.6745 | -61.5601 | -61.5509 | -61.4227 | -0.21057 | 0.032043 | -0.096131 | 0.27924 | -0.12817 | -0.11444 | 0.082397 | 0.09613 | -0.082397 | -0.045777 | -0.022888 | 0.059509 | 0.19684 | 0.068665 | 0.27924 | 0.15106 | 0.48981 | 123.4314 | 0.14191 | 123.3765 | 123.5596 | 123.3536 | 123.349 | 123.2712 | -123.5275 | -123.3994 | 123.2208 | 123.2941 | 61.5967 | 61.6516
45.2188 | 123.4497 | -61.6425 | 61.6928 | 0.0034333 | 0.0062464 | 0.070226 | 0.065273 | 0.0022409 | -0.00065149 | -0.00055975 | 0.0046998 | 0.0032064 | 0.068419 | 0.056127 | -0.0032427 | 0.010587 | -0.0016192 | -0.018311 | 61.7569 | -61.8256 | 61.5509 | -61.377 | -61.7752 | -61.7889 | -0.018311 | 61.6928 | -61.7294 | 61.6104 | -61.6058 | -61.6058 | -61.4731 | -0.18311 | 0.064087 | -0.14191 | 0.2655 | -0.14648 | -0.13275 | 0.036622 | 0.050354 | -0.086975 | 0 | -0.082397 | 0.036621 | 0.16937 | 0.036621 | 0.25635 | 0.1236 | 0.44861 | 123.3765 | 0.1236 | 123.3398 | 123.5825 | 123.4222 | 123.3994 | 123.3353 | -123.5184 | -123.4222 | 123.1934 | 123.2529 | 61.6241 | 61.6241
46.9375 | 123.5275 | -61.6333 | 61.6241 | 0.0034333 | 0.0058192 | 0.070654 | 0.065486 | 0.0069405 | -0.0021469 | -0.00098695 | 0.001648 | 0.0049154 | 0.066497 | 0.068304 | 0.0027387 | 0.01251 | -0.005678 | -0.10529 | 61.7294 | -61.8576 | 61.5417 | -61.4182 | -61.853 | -61.8484 | 0 | 61.6058 | -61.7432 | 61.6928 | -61.5784 | -61.5601 | -61.4044 | -0.2243 | 0.10528 | -0.082398 | 0.21515 | -0.21515 | -0.21973 | 0.009155 | 0.004578 | -0.10986 | -0.018311 | 0.068664 | 0.054932 | 0.22888 | 0.073242 | 0.33875 | 0.1831 | 0.43945 | 123.3994 | 0.16479 | 123.436 | 123.587 | 123.349 | 123.3627 | 123.2391 | -123.4818 | -123.3673 | 123.175 | 123.3261 | 61.528 | 61.6333
48.6719 | 123.4177 | -61.702 | 61.6333 | 0.011063 | 0.0053918 | 0.070867 | 0.065486 | 0.0069405 | -0.00043789 | -0.0048322 | -0.0014038 | 0.0038474 | 0.06906 | 0.056982 | 0.0014569 | 0.013578 | -0.0020464 | -0.1236 | 61.7477 | -61.9034 | 61.4136 | -61.5234 | -61.9308 | -61.9217 | -0.09613 | 61.6287 | -61.7844 | 61.5829 | -61.6928 | -61.6791 | -61.5189 | -0.20142 | 0.11444 | -0.21973 | 0.17853 | -0.21973 | -0.22888 | -0.018311 | -0.027466 | -0.082398 | -0.004578 | -0.050354 | 0.009155 | 0.18311 | 0.022888 | 0.2655 | 0.10529 | 0.37994 | 123.317 | 0.091553 | 123.3673 | 123.6511 | 123.4131 | 123.4497 | 123.3307 | -123.5367 | -123.4177 | 123.1155 | 123.2849 | 61.5784 | 61.6058
50.4219 | 123.5413 | -61.6425 | 61.6287 | 0.011063 | 0.0051782 | 0.07044 | 0.065059 | 0.0069405 | 0.00020291 | 0.00050845 | 0.02301 | 0.0029928 | 0.072478 | 0.061254 | -0.00046573 | 0.011228 | -0.0035418 | -0.050354 | 61.7065 | -61.8805 | 61.5692 | -61.3632 | -61.8118 | -61.8073 | 0.050354 | 61.6425 | -61.7706 | 61.7111 | -61.5509 | -61.5463 | -61.409 | -0.23804 | 0.07782 | -0.059509 | 0.27924 | -0.16479 | -0.16937 | 0.073242 | 0.068664 | -0.12817 | 0.013733 | 0.082398 | 0.091553 | 0.23346 | 0.09613 | 0.36163 | 0.2243 | 0.51727 | 123.4497 | 0.21973 | 123.4818 | 123.587 | 123.4131 | 123.349 | 123.2849 | -123.5092 | -123.3994 | 123.2117 | 123.3536 | 61.5921 | 61.6928
52.0938 | 123.4772 | -61.6241 | 61.6699 | 0.026321 | 0.0051782 | 0.070226 | 0.066768 | 0.0028817 | -0.0040695 | -0.00013235 | 0.0046998 | 0.0042746 | 0.06906 | 0.061254 | -0.00067933 | 0.011228 | -0.002901 | -0.09613 | 61.7569 | -61.8347 | 61.5509 | -61.3815 | -61.7706 | -61.7889 | -0.018311 | 61.6425 | -61.702 | 61.6608 | -61.5784 | -61.5601 | -61.4273 | -0.21057 | 0.086975 | -0.11902 | 0.24262 | -0.16479 | -0.14648 | 0.045777 | 0.064087 | -0.077819 | -0.027466 | -0.009155 | 0.045777 | 0.19684 | 0.064087 | 0.27466 | 0.14191 | 0.45319 | 123.3856 | 0.1236 | 123.3627 | 123.5916 | 123.3444 | 123.381 | 123.2666 | -123.5046 | -123.3719 | 123.175 | 123.2849 | 61.528 | 61.6058
53.8125 | 123.5367 | -61.6104 | 61.6562 | -0.0041962 | 0.0021876 | 0.070226 | 0.065273 | 0.0037363 | -0.0010789 | -0.0020552 | 0.0046998 | 0.0034202 | 0.06906 | 0.063818 | -0.0023883 | 0.01016 | 0.0017988 | -0.022888 | 61.7111 | -61.8164 | 61.6013 | -61.2671 | -61.6837 | -61.702 | 0.11902 | 61.6333 | -61.6608 | 61.734 | -61.4822 | -61.4777 | -61.3495 | -0.20599 | 0.054932 | -0.054932 | 0.34332 | -0.091552 | -0.073242 | 0.11444 | 0.13275 | -0.050354 | -0.022888 | 0.07782 | 0.12817 | 0.26093 | 0.13275 | 0.31128 | 0.18311 | 0.54932 | 123.4177 | 0.17853 | 123.3948 | 123.5275 | 123.2941 | 123.3215 | 123.2437 | -123.4726 | -123.317 | 123.2117 | 123.3444 | 61.5875 | 61.7294
55.5469 | 123.3902 | -61.6699 | 61.6379 | 0.011063 | 0.0060328 | 0.067663 | 0.068263 | 0.0065133 | -0.00086509 | -0.0033368 | -0.0014038 | 0.0038474 | 0.070342 | 0.057836 | -0.00046573 | 0.0097326 | 0.0011578 | -0.10071 | 61.7065 | -61.9125 | 61.4273 | -61.5189 | -61.9171 | -61.9217 | -0.12817 | 61.6425 | -61.7477 | 61.5509 | -61.7111 | -61.6928 | -61.5097 | -0.24262 | 0.068665 | -0.21057 | 0.15106 | -0.25177 | -0.24719 | -0.009155 | -0.004577 | -0.07782 | 0.004578 | -0.086975 | -0.041199 | 0.16022 | -0.022888 | 0.23804 | 0.054932 | 0.39368 | 123.3398 | 0.036621 | 123.2986 | 123.6191 | 123.3902 | 123.3765 | 123.3124 | -123.5504 | -123.3856 | 123.0972 | 123.2208 | 61.5692 | 61.5417
57.2969 | 123.4589 | -61.6791 | 61.6425 | 0.0034333 | 0.0066736 | 0.070867 | 0.065273 | 0.0037363 | -0.0047103 | 0.00050845 | 0.001648 | 0.0049154 | 0.067992 | 0.064672 | -0.00089293 | 0.01016 | 0.00030339 | -0.10986 | 61.7386 | -61.8576 | 61.441 | -61.4868 | -61.9125 | -61.8851 | -0.09613 | 61.615 | -61.7569 | 61.6241 | -61.6333 | -61.6379 | -61.4548 | -0.17853 | 0.09613 | -0.20142 | 0.19226 | -0.20599 | -0.23346 | -0.027466 | -0.054932 | -0.07782 | -0.027466 | -0.01831 | 0.045776 | 0.2243 | 0.041199 | 0.30212 | 0.11902 | 0.37079 | 123.2986 | 0.1236 | 123.381 | 123.5962 | 123.3719 | 123.4177 | 123.2941 | -123.5001 | -123.3994 | 123.1201 | 123.3032 | 61.5692 | 61.5829
58.9688 | 123.436 | -61.647 | 61.647 | 0.033951 | 0.0049646 | 0.071081 | 0.068691 | 0.0088631 | -0.0023605 | 0.00050845 | 0.013855 | 0.0055564 | 0.071624 | 0.057409 | -3.8532e-05 | 0.010374 | -0.0065326 | -0.041199 | 61.7706 | -61.8713 | 61.4822 | -61.4365 | -61.8118 | -61.8301 | -0.045776 | 61.6745 | -61.7432 | 61.6013 | -61.6333 | -61.6104 | -61.4502 | -0.2243 | 0.1236 | -0.16479 | 0.21057 | -0.18311 | -0.1648 | 0.041199 | 0.059509 | -0.09613 | 0.027466 | -0.045777 | 0.013733 | 0.19684 | 0.036621 | 0.29297 | 0.13275 | 0.43488 | 123.3536 | 0.10986 | 123.3444 | 123.642 | 123.4177 | 123.4177 | 123.3215 | -123.5184 | -123.3902 | 123.1293 | 123.2483 | 61.6058 | 61.6013
60.6875 | 123.5046 | -61.5829 | 61.6562 | 0.0034333 | 0.0060328 | 0.069799 | 0.06335 | 0.0011727 | -0.0025741 | 0.00050845 | -0.0014038 | 0.0025656 | 0.067351 | 0.064459 | -0.0026019 | 0.01016 | -0.002901 | -0.036621 | 61.7111 | -61.8027 | 61.6287 | -61.2442 | -61.6608 | -61.6974 | 0.091553 | 61.6333 | -61.6425 | 61.7157 | -61.4731 | -61.4777 | -61.3632 | -0.21973 | 0.054932 | -0.027466 | 0.33874 | -0.11444 | -0.07782 | 0.10529 | 0.14191 | -0.059509 | -0.022888 | 0.059509 | 0.10986 | 0.21973 | 0.10529 | 0.27924 | 0.1648 | 0.55847 | 123.4314 | 0.16937 | 123.3582 | 123.5138 | 123.2758 | 123.2941 | 123.2162 | -123.4589 | -123.2986 | 123.2117 | 123.2986 | 61.5463 | 61.6745
62.4375 | 123.4497 | -61.6241 | 61.6425 | 0.026321 | 0.0041102 | 0.071295 | 0.066768 | 0.0052315 | -0.00043789 | -0.00013235 | 0.019959 | 0.004061 | 0.069274 | 0.058477 | 0.0018841 | 0.011869 | -0.00012381 | -0.054932 | 61.702 | -61.8622 | 61.5692 | -61.322 | -61.7661 | -61.7569 | 0.022888 | 61.6196 | -61.7065 | 61.6745 | -61.5646 | -61.5509 | -61.3907 | -0.23804 | 0.059509 | -0.073242 | 0.30213 | -0.13275 | -0.14191 | 0.10529 | 0.096131 | -0.082397 | -0.022888 | 0.032044 | 0.05951 | 0.23346 | 0.073243 | 0.31586 | 0.15564 | 0.54016 | 123.4314 | 0.14191 | 123.381 | 123.5641 | 123.3261 | 123.3261 | 123.2437 | -123.5046 | -123.349 | 123.1934 | 123.2986 | 61.5692 | 61.647
64.1719 | 123.4177 | -61.6699 | 61.647 | 0.018692 | 0.0043238 | 0.070013 | 0.066127 | 0.0056589 | -0.0017197 | 0.00029485 | -0.0014038 | 0.0038474 | 0.068633 | 0.058477 | -3.8532e-05 | 0.0086646 | -0.0016192 | -0.018311 | 61.7111 | -61.8713 | 61.4914 | -61.4182 | -61.8393 | -61.8439 | -0.022888 | 61.6196 | -61.7249 | 61.5875 | -61.647 | -61.6425 | -61.4777 | -0.20142 | 0.064087 | -0.15564 | 0.25177 | -0.17395 | -0.16937 | 0.027466 | 0.032044 | -0.054932 | -0.027466 | -0.05951 | 0.022888 | 0.19226 | 0.027466 | 0.24719 | 0.082398 | 0.45319 | 123.3627 | 0.07782 | 123.3124 | 123.5825 | 123.3444 | 123.381 | 123.2895 | -123.5184 | -123.3719 | 123.1613 | 123.2574 | 61.6516 | 61.647
65.8281 | 123.3673 | -61.6562 | 61.702 | -0.011826 | 0.0032556 | 0.068517 | 0.064632 | 0.0054453 | -0.0017197 | 0.0017902 | 0.001648 | 0.0042746 | 0.069274 | 0.055273 | -0.0034563 | 0.0065284 | 0.0011578 | -0.082397 | 61.7432 | -61.8073 | 61.4685 | -61.4365 | -61.8164 | -61.8256 | -0.064087 | 61.6745 | -61.7294 | 61.5692 | -61.647 | -61.6058 | -61.4594 | -0.15106 | 0.041199 | -0.23346 | 0.21973 | -0.16937 | -0.16022 | -0.018311 | -0.009155 | -0.073242 | -0.027465 | -0.13275 | 0.009155 | 0.19684 | 0.050354 | 0.27008 | 0.1236 | 0.37079 | 123.2758 | 0.082397 | 123.2986 | 123.5504 | 123.4039 | 123.3994 | 123.3307 | -123.5092 | -123.4314 | 123.1247 | 123.2254 | 61.5738 | 61.5921
67.5625 | 123.436 | -61.6516 | 61.6699 | 0.0034333 | 0.0053918 | 0.067236 | 0.063564 | 0.00031834 | -0.0030015 | -0.00055975 | 0.001648 | 0.002352 | 0.067778 | 0.059545 | -0.0021747 | 0.0088782 | -0.0026874 | -0.004578 | 61.7111 | -61.7798 | 61.5738 | -61.3083 | -61.7111 | -61.7294 | 0.027466 | 61.6241 | -61.6837 | 61.6516 | -61.5372 | -61.5463 | -61.3998 | -0.12817 | 0.041199 | -0.09613 | 0.34332 | -0.07782 | -0.05951 | 0.050354 | 0.068664 | -0.032044 | -0.045776 | -0.018311 | 0.11444 | 0.25177 | 0.10529 | 0.28381 | 0.13733 | 0.4715 | 123.3536 | 0.14648 | 123.3353 | 123.4909 | 123.3078 | 123.3627 | 123.2758 | -123.4497 | -123.3536 | 123.2254 | 123.3032 | 61.647 | 61.6791
69.2344 | 123.4589 | -61.6058 | 61.6287 | 0.04158 | 0.0045374 | 0.07044 | 0.066127 | 0.0073679 | 0.0014847 | 0.0017902 | 0.013855 | 0.0025656 | 0.069915 | 0.065313 | 0.0014569 | 0.0073828 | 0.00051699 | -0.064087 | 61.7065 | -61.8256 | 61.5509 | -61.322 | -61.7661 | -61.7569 | -0.004578 | 61.615 | -61.7294 | 61.6699 | -61.5509 | -61.5326 | -61.3998 | -0.21973 | 0.07782 | -0.07782 | 0.28381 | -0.15106 | -0.16022 | 0.068665 | 0.05951 | -0.1236 | -0.013733 | 0.041199 | 0.054932 | 0.20599 | 0.073242 | 0.32959 | 0.19684 | 0.50354 | 123.3765 | 0.17853 | 123.3994 | 123.5321 | 123.3444 | 123.3124 | 123.2208 | -123.4543 | -123.3582 | 123.1567 | 123.2758 | 61.5417 | 61.6013
70.9688 | 123.4543 | -61.5921 | 61.6333 | 0.018692 | 0.0045374 | 0.068731 | 0.0657 | 0.00074554 | -0.0021469 | -0.00055975 | -0.0014038 | 0.0019248 | 0.068846 | 0.065099 | -0.00046573 | 0.0073828 | -0.001192 | -0.09613 | 61.7294 | -61.7935 | 61.5097 | -61.3632 | -61.7798 | -61.7706 | -0.050354 | 61.6104 | -61.6882 | 61.6608 | -61.5326 | -61.496 | -61.3724 | -0.20142 | 0.09613 | -0.1236 | 0.22888 | -0.17853 | -0.18768 | 0.022888 | 0.013733 | -0.09613 | -0.022888 | 0.027466 | 0.059509 | 0.21973 | 0.09613 | 0.31586 | 0.19226 | 0.4303 | 123.3032 | 0.15564 | 123.349 | 123.5229 | 123.2986 | 123.3215 | 123.2025 | -123.4268 | -123.3215 | 123.1018 | 123.2529 | 61.496 | 61.5417
72.7188 | 123.5046 | -61.5601 | 61.6562 | -0.011826 | 0.004751 | 0.070226 | 0.063136 | 0.0026681 | -0.0030015 | 0.00093565 | 0.001648 | 0.0019248 | 0.068846 | 0.061254 | -0.0021747 | 0.0080236 | -0.0024738 | -0.032043 | 61.7111 | -61.7935 | 61.6058 | -61.2305 | -61.6562 | -61.6974 | 0.07782 | 61.5967 | -61.6791 | 61.7065 | -61.4639 | -61.4548 | -61.3449 | -0.23346 | 0.054932 | -0.050354 | 0.32959 | -0.13733 | -0.09613 | 0.09613 | 0.13733 | -0.11902 | -0.059509 | 0.050354 | 0.096131 | 0.21515 | 0.10529 | 0.33417 | 0.2243 | 0.56305 | 123.3994 | 0.21515 | 123.3856 | 123.5046 | 123.2758 | 123.2712 | 123.1567 | -123.4497 | -123.3353 | 123.1659 | 123.2666 | 61.528 | 61.6379
74.3906 | 123.3444 | -61.6745 | 61.6241 | 0.011063 | 0.0058192 | 0.070654 | 0.06805 | 0.0058725 | -0.0027877 | -0.00077335 | 0.001648 | 0.0042746 | 0.069701 | 0.052496 | -0.0013201 | 0.0082374 | -0.0041828 | -0.082397 | 61.702 | -61.8759 | 61.4136 | -61.5005 | -61.8851 | -61.9125 | -0.10529 | 61.6196 | -61.7432 | 61.5463 | -61.6882 | -61.6699 | -61.496 | -0.20142 | 0.077819 | -0.21057 | 0.17395 | -0.23804 | -0.21057 | -0.036621 | -0.009155 | -0.068664 | -0.004578 | -0.07782 | -0.013732 | 0.17853 | 0.004578 | 0.24719 | 0.073242 | 0.37537 | 123.2895 | 0.054932 | 123.2895 | 123.5779 | 123.3627 | 123.3765 | 123.2941 | -123.5001 | -123.3673 | 123.0881 | 123.2208 | 61.5921 | 61.5692
76.125 | 123.4497 | -61.6196 | 61.6287 | 0.026321 | 0.0026148 | 0.071935 | 0.064632 | 0.0033089 | -0.0023605 | 0.0026446 | 0.001648 | 0.0027792 | 0.069701 | 0.058477 | -0.00046573 | 0.0093054 | -0.0037554 | -0.09613 | 61.7111 | -61.8164 | 61.5143 | -61.3632 | -61.7523 | -61.7661 | -0.041199 | 61.6287 | -61.6653 | 61.6653 | -61.5097 | -61.5143 | -61.3632 | -0.19684 | 0.082398 | -0.11444 | 0.25635 | -0.14648 | -0.13275 | 0.050354 | 0.064087 | -0.045776 | 0 | 0.036621 | 0.10986 | 0.25635 | 0.10529 | 0.30212 | 0.15106 | 0.45319 | 123.3307 | 0.15564 | 123.3307 | 123.5275 | 123.2941 | 123.3307 | 123.2483 | -123.4451 | -123.2941 | 123.1338 | 123.2849 | 61.5234 | 61.5784
77.7969 | 123.4039 | -61.6379 | 61.6333 | 0.033951 | 0.0060328 | 0.069372 | 0.069972 | 0.0039499 | -0.0012925 | -0.00034615 | 0.013855 | 0.0042746 | 0.068846 | 0.057195 | -0.00089293 | 0.009519 | -0.0020464 | -0.032043 | 61.7844 | -61.8805 | 61.4731 | -61.4227 | -61.7798 | -61.7889 | -0.036621 | 61.6699 | -61.7294 | 61.5967 | -61.5921 | -61.6104 | -61.441 | -0.24262 | 0.15106 | -0.16022 | 0.21515 | -0.15106 | -0.14191 | 0.091553 | 0.10071 | -0.091553 | 0.036621 | -0.036621 | 0.045776 | 0.19684 | 0.027465 | 0.28839 | 0.11902 | 0.45776 | 123.3536 | 0.13733 | 123.3261 | 123.6649 | 123.3994 | 123.4222 | 123.3078 | -123.5138 | -123.3627 | 123.111 | 123.2346 | 61.6058 | 61.6013
79.5312 | 123.436 | -61.5921 | 61.647 | 0.04158 | 0.0045374 | 0.07044 | 0.066768 | 0.0039499 | -0.0015061 | 0.00093565 | 0.016907 | 0.002352 | 0.068633 | 0.067236 | -0.00067933 | 0.010801 | -0.0018328 | -0.082397 | 61.6928 | -61.8118 | 61.528 | -61.3129 | -61.7661 | -61.7615 | -0.032043 | 61.6104 | -61.7065 | 61.6516 | -61.5372 | -61.5417 | -61.3861 | -0.21973 | 0.045776 | -0.11902 | 0.27924 | -0.16937 | -0.17395 | 0.050354 | 0.045777 | -0.11444 | -0.036621 | 0.004577 | 0.054932 | 0.20599 | 0.050354 | 0.32044 | 0.1648 | 0.49896 | 123.3398 | 0.16937 | 123.3582 | 123.5046 | 123.317 | 123.2849 | 123.2025 | -123.4589 | -123.3536 | 123.1201 | 123.2437 | 61.5097 | 61.5601
81.2031 | 123.349 | -61.6882 | 61.6196 | 0.0034333 | 0.0068872 | 0.069586 | 0.069118 | 0.0026681 | -0.0010789 | -0.0018414 | 0.001648 | 0.005129 | 0.067565 | 0.061681 | -0.00025213 | 0.0090918 | -0.00076481 | -0.11902 | 61.6974 | -61.8484 | 61.3953 | -61.5189 | -61.9217 | -61.9125 | -0.15106 | 61.6013 | -61.7386 | 61.5417 | -61.6837 | -61.6928 | -61.4868 | -0.16022 | 0.07782 | -0.2243 | 0.16937 | -0.22431 | -0.23346 | -0.064087 | -0.073242 | -0.050354 | -0.018311 | -0.07782 | 0.004577 | 0.20142 | -0.004578 | 0.25177 | 0.045776 | 0.32959 | 123.2437 | 0.054931 | 123.2803 | 123.5458 | 123.3398 | 123.3856 | 123.2895 | -123.468 | -123.3582 | 123.0835 | 123.23 | 61.5692 | 61.5372
83 | 123.349 | -61.6837 | 61.5875 | -0.0041962 | 0.0077418 | 0.069799 | 0.066127 | 0.0011727 | -0.0015061 | -0.0022688 | 0.001648 | 0.0036338 | 0.070342 | 0.054632 | 0.0010297 | 0.010374 | -0.0033282 | -0.11902 | 61.6882 | -61.8851 | 61.3861 | -61.5189 | -61.9125 | -61.8988 | -0.15106 | 61.5875 | -61.7432 | 61.5463 | -61.6837 | -61.6745 | -61.4822 | -0.20142 | 0.10071 | -0.20142 | 0.1648 | -0.21515 | -0.22888 | -0.013733 | -0.027466 | -0.059509 | 0 | -0.041198 | 0 | 0.20142 | 0.009155 | 0.26093 | 0.068664 | 0.36621 | 123.2712 | 0.059509 | 123.2895 | 123.5733 | 123.3307 | 123.3719 | 123.2712 | -123.4726 | -123.3307 | 123.0698 | 123.23 | 61.5646 | 61.5326
84.6875 | 123.3856 | -61.6425 | 61.6333 | 0.026321 | 0.0068872 | 0.068945 | 0.066768 | 0.0037363 | -0.0021469 | -0.00013235 | 0.019959 | 0.005129 | 0.068846 | 0.060827 | -0.0015337 | 0.0088782 | -0.00033761 | -0.032043 | 61.7798 | -61.8668 | 61.4777 | -61.4182 | -61.7844 | -61.8027 | -0.054932 | 61.6562 | -61.734 | 61.5967 | -61.6013 | -61.5921 | -61.4273 | -0.2243 | 0.14648 | -0.15564 | 0.2243 | -0.16022 | -0.14191 | 0.064087 | 0.082397 | -0.091553 | 0.022888 | -0.036621 | 0.041199 | 0.21515 | 0.050354 | 0.3067 | 0.14191 | 0.44861 | 123.3444 | 0.13275 | 123.3307 | 123.6465 | 123.3902 | 123.4222 | 123.2986 | -123.5001 | -123.3673 | 123.1201 | 123.2391 | 61.6104 | 61.5875
86.4844 | 123.4039 | -61.6425 | 61.5967 | 0.0034333 | 0.0060328 | 0.070013 | 0.064204 | 0.0069405 | -0.0032151 | -0.0022688 | 0.0046998 | 0.0053428 | 0.06906 | 0.060827 | 0.00017507 | 0.01016 | 0.0024396 | -0.11902 | 61.7065 | -61.8484 | 61.4227 | -61.4594 | -61.8805 | -61.8713 | -0.086975 | 61.5829 | -61.7294 | 61.6013 | -61.6058 | -61.6013 | -61.4365 | -0.20599 | 0.10986 | -0.17395 | 0.18311 | -0.22888 | -0.23804 | -0.022888 | -0.032043 | -0.086975 | -0.013733 | 0.004577 | 0.036621 | 0.20599 | 0.041199 | 0.29297 | 0.12817 | 0.3891 | 123.2712 | 0.1236 | 123.3307 | 123.555 | 123.3124 | 123.349 | 123.2254 | -123.4451 | -123.3261 | 123.0652 | 123.2437 | 61.5234 | 61.5555
88.2188 | 123.3261 | -61.6425 | 61.6653 | 0.0034333 | 0.0053918 | 0.068731 | 0.063991 | 0.0026681 | -0.0036423 | 0.00072205 | 0.001648 | 0.0036338 | 0.071196 | 0.050573 | -0.0036701 | 0.008451 | -0.00076481 | -0.059509 | 61.7661 | -61.7798 | 61.4594 | -61.3907 | -61.7798 | -61.7981 | -0.059509 | 61.6241 | -61.7249 | 61.5646 | -61.6058 | -61.5921 | -61.441 | -0.13733 | 0.10071 | -0.20599 | 0.25177 | -0.15564 | -0.13733 | -0.018311 | 0 | -0.082398 | -0.041198 | -0.10071 | 0.036621 | 0.20142 | 0.050354 | 0.28381 | 0.13275 | 0.3891 | 123.2391 | 0.11902 | 123.2895 | 123.5458 | 123.349 | 123.4085 | 123.2666 | -123.4451 | -123.3902 | 123.1018 | 123.2071 | 61.5829 | 61.5829
90 | 123.4726 | -61.5738 | 61.6379 | -0.0041962 | 0.004751 | 0.067449 | 0.06335 | 0.0048043 | -0.00043789 | 0.00072205 | 0.001648 | 0.002352 | 0.06906 | 0.065954 | -0.0023883 | 0.010587 | -0.0014056 | -0.022888 | 61.6974 | -61.7569 | 61.5921 | -61.2579 | -61.6516 | -61.6974 | 0.07782 | 61.6104 | -61.6562 | 61.6882 | -61.4639 | -61.4639 | -61.322 | -0.18311 | 0.05951 | -0.045776 | 0.31586 | -0.1236 | -0.077819 | 0.059509 | 0.10529 | -0.082397 | -0.027465 | 0.050354 | 0.10986 | 0.25177 | 0.10986 | 0.33417 | 0.19226 | 0.49896 | 123.349 | 0.19226 | 123.3444 | 123.4543 | 123.2666 | 123.2712 | 123.1842 | -123.3948 | -123.2941 | 123.1659 | 123.262 | 61.5509 | 61.6516
91.7969 | 123.4314 | -61.5921 | 61.6013 | 0.04921 | 0.00646 | 0.072363 | 0.067195 | 0.0045907 | -0.0036423 | 0.00093565 | 0.013855 | 0.004061 | 0.070342 | 0.061895 | 0.0023115 | 0.01016 | -0.0020464 | -0.050354 | 61.6882 | -61.821 | 61.5555 | -61.3037 | -61.7386 | -61.7294 | 0.041199 | 61.6058 | -61.702 | 61.6608 | -61.5326 | -61.5234 | -61.3724 | -0.22888 | 0.086975 | -0.045776 | 0.28839 | -0.13733 | -0.14648 | 0.091553 | 0.082398 | -0.10986 | 0.004578 | 0.05951 | 0.059509 | 0.21973 | 0.068665 | 0.32959 | 0.17853 | 0.51727 | 123.3765 | 0.16937 | 123.3627 | 123.5092 | 123.3078 | 123.2803 | 123.1979 | -123.4222 | -123.3032 | 123.1476 | 123.2529 | 61.5417 | 61.6333
93.5938 | 123.3856 | -61.6333 | 61.6013 | 0.018692 | 0.0077418 | 0.069372 | 0.066554 | 0.0095041 | -0.0027877 | 0.002431 | 0.0077514 | 0.005129 | 0.069915 | 0.057836 | -0.0013201 | 0.008451 | -0.0020464 | -0.018311 | 61.6974 | -61.8576 | 61.4914 | -61.3678 | -61.7798 | -61.8027 | 0.004578 | 61.6013 | -61.7111 | 61.5921 | -61.5875 | -61.5784 | -61.4273 | -0.2243 | 0.096131 | -0.10986 | 0.2655 | -0.16937 | -0.14648 | 0.054932 | 0.07782 | -0.07782 | 0 | -0.009155 | 0.045777 | 0.20599 | 0.054932 | 0.28381 | 0.13275 | 0.48981 | 123.349 | 0.1236 | 123.3032 | 123.555 | 123.3124 | 123.3307 | 123.2346 | -123.4589 | -123.3124 | 123.1247 | 123.2254 | 61.615 | 61.6379
95.2656 | 123.4543 | -61.5692 | 61.6333 | 0.0034333 | 0.0017602 | 0.07044 | 0.064418 | 0.0035227 | -0.0012925 | 0.00072205 | -0.0014038 | 0.0036338 | 0.066497 | 0.066595 | -0.0015337 | 0.010587 | 0.0052166 | -0.07782 | 61.7249 | -61.7935 | 61.528 | -61.3037 | -61.6974 | -61.6882 | 0.036621 | 61.6241 | -61.6699 | 61.7065 | -61.4731 | -61.441 | -61.3083 | -0.2243 | 0.091553 | -0.10529 | 0.2655 | -0.11902 | -0.12817 | 0.10529 | 0.09613 | -0.10071 | -0.009155 | 0.073242 | 0.096131 | 0.26093 | 0.12817 | 0.36163 | 0.22888 | 0.48981 | 123.3215 | 0.19684 | 123.3765 | 123.5184 | 123.2941 | 123.2941 | 123.1934 | -123.4268 | -123.3032 | 123.0972 | 123.2758 | 61.4914 | 61.6058
97 | 123.4314 | -61.5875 | 61.6104 | 0.04158 | 0.0053918 | 0.070867 | 0.0657 | 0.0043771 | -0.0012925 | 0.00072205 | 0.016907 | 0.0036338 | 0.070342 | 0.062322 | 0.0014569 | 0.009519 | 0.00051699 | -0.059509 | 61.6928 | -61.8118 | 61.5601 | -61.2854 | -61.734 | -61.7294 | 0.045776 | 61.5875 | -61.6928 | 61.6653 | -61.528 | -61.5234 | -61.3586 | -0.22431 | 0.082397 | -0.050354 | 0.30212 | -0.14191 | -0.14648 | 0.082398 | 0.07782 | -0.10529 | -0.022889 | 0.054931 | 0.059509 | 0.22888 | 0.064087 | 0.33417 | 0.16937 | 0.52643 | 123.3719 | 0.16479 | 123.3582 | 123.5046 | 123.2803 | 123.2803 | 123.175 | -123.4222 | -123.3032 | 123.1476 | 123.2529 | 61.528 | 61.6333
98.6719 | 123.4772 | -61.5372 | 61.6516 | 0.0034333 | 0.0053918 | 0.066168 | 0.065273 | 0.0033089 | -0.0025741 | -0.00034615 | 0.001648 | 0.0014976 | 0.069487 | 0.063604 | 0.0020979 | 0.0099462 | -0.001192 | -0.073242 | 61.6837 | -61.7752 | 61.5372 | -61.2946 | -61.7065 | -61.6837 | 0.041199 | 61.6241 | -61.6379 | 61.7111 | -61.4548 | -61.4273 | -61.3129 | -0.23804 | 0.032044 | -0.11444 | 0.24261 | -0.14648 | -0.16937 | 0.091553 | 0.068665 | -0.10071 | -0.027465 | 0.05951 | 0.082397 | 0.2243 | 0.10986 | 0.32501 | 0.21057 | 0.48065 | 123.3124 | 0.1831 | 123.349 | 123.4589 | 123.262 | 123.2208 | 123.1613 | -123.4268 | -123.2895 | 123.0743 | 123.2483 | 61.4639 | 61.5784
100.3906 | 123.3627 | -61.6379 | 61.6241 | 0.026321 | 0.0043238 | 0.069799 | 0.067622 | 0.0062997 | -0.0021469 | -0.00098695 | 0.0077514 | 0.0049154 | 0.07141 | 0.05805 | 0.00060247 | 0.008451 | -0.0037554 | -0.009155 | 61.7157 | -61.821 | 61.496 | -61.3541 | -61.7844 | -61.7844 | 0.018311 | 61.6241 | -61.6837 | 61.5921 | -61.5692 | -61.5784 | -61.409 | -0.18311 | 0.091552 | -0.12817 | 0.28381 | -0.14648 | -0.14648 | 0.036621 | 0.036621 | -0.045777 | 0 | -0.032044 | 0.068664 | 0.22888 | 0.059509 | 0.27466 | 0.10529 | 0.46692 | 123.317 | 0.11444 | 123.2758 | 123.5367 | 123.3078 | 123.3536 | 123.262 | -123.4451 | -123.3078 | 123.1338 | 123.23 | 61.6287 | 61.6562
102.1875 | 123.3582 | -61.6196 | 61.6013 | -0.0041962 | 0.003042 | 0.067449 | 0.067622 | 0.0054453 | -0.0010789 | -0.00034615 | -0.0014038 | 0.0036338 | 0.070555 | 0.060186 | -0.00046573 | 0.01251 | -0.0018328 | -0.13275 | 61.7203 | -61.8668 | 61.4182 | -61.4456 | -61.8622 | -61.8484 | -0.10529 | 61.5921 | -61.7157 | 61.6013 | -61.6104 | -61.5967 | -61.4182 | -0.24719 | 0.11902 | -0.1831 | 0.17395 | -0.22888 | -0.24262 | 0.01831 | 0.004577 | -0.09613 | -0.009155 | 0 | 0.009155 | 0.20142 | 0.022888 | 0.29755 | 0.11902 | 0.42114 | 123.2849 | 0.10529 | 123.317 | 123.587 | 123.3078 | 123.3398 | 123.2117 | -123.468 | -123.317 | 123.0377 | 123.2208 | 61.4868 | 61.5143
103.8438 | 123.3215 | -61.6058 | 61.6745 | 0.0034333 | 0.0049646 | 0.069158 | 0.064632 | 0.0035227 | -0.0017197 | -0.0031232 | 0.001648 | 0.0027792 | 0.069915 | 0.053777 | -0.0045245 | 0.0075964 | -0.0018328 | -0.054932 | 61.7249 | -61.7981 | 61.4731 | -61.3724 | -61.7615 | -61.7661 | -0.054932 | 61.6608 | -61.6791 | 61.5692 | -61.5875 | -61.5829 | -61.4227 | -0.19226 | 0.050354 | -0.20142 | 0.23346 | -0.16022 | -0.15564 | 0.032044 | 0.036621 | -0.073242 | -0.013733 | -0.10529 | 0.018311 | 0.18311 | 0.022888 | 0.25635 | 0.09613 | 0.42572 | 123.2712 | 0.091553 | 123.2483 | 123.523 | 123.3398 | 123.3307 | 123.2666 | -123.4726 | -123.3536 | 123.0789 | 123.175 | 61.5509 | 61.5509
105.5156 | 123.381 | -61.6104 | 61.6241 | 0.011063 | 0.0068872 | 0.068945 | 0.064418 | 0.00095914 | -0.0034287 | -0.00013235 | 0.013855 | 0.0049154 | 0.069487 | 0.056982 | -0.00067933 | 0.0069556 | -0.0033282 | -0.022888 | 61.7249 | -61.8484 | 61.4731 | -61.3678 | -61.7752 | -61.7935 | 0 | 61.5967 | -61.702 | 61.5784 | -61.5784 | -61.5738 | -61.409 | -0.23804 | 0.10071 | -0.15106 | 0.24262 | -0.1831 | -0.16479 | 0.054932 | 0.073242 | -0.091552 | -0.027466 | -0.045777 | 0.032044 | 0.20142 | 0.036621 | 0.29297 | 0.12817 | 0.48065 | 123.3215 | 0.1236 | 123.2803 | 123.5733 | 123.2986 | 123.3353 | 123.2071 | -123.4726 | -123.3261 | 123.0835 | 123.1888 | 61.5875 | 61.6104
107.1875 | 123.3536 | -61.6241 | 61.6196 | 0.018692 | 0.0045374 | 0.071935 | 0.066768 | 0.0024545 | -0.00086509 | 0.0011492 | 0.0077514 | 0.0036338 | 0.070769 | 0.0604 | -3.8532e-05 | 0.0082374 | -0.0031146 | -0.032043 | 61.7065 | -61.821 | 61.4914 | -61.3541 | -61.7661 | -61.7935 | 0.018311 | 61.6287 | -61.7111 | 61.6013 | -61.5738 | -61.5738 | -61.3998 | -0.19684 | 0.086975 | -0.12817 | 0.27008 | -0.16937 | -0.14191 | 0.027466 | 0.054932 | -0.086975 | 0.009155 | -0.018311 | 0.050354 | 0.22431 | 0.050354 | 0.31128 | 0.13733 | 0.46692 | 123.3124 | 0.13733 | 123.3124 | 123.5275 | 123.3398 | 123.3307 | 123.2529 | -123.4406 | -123.3307 | 123.1155 | 123.2254 | 61.5921 | 61.6425
108.8438 | 123.4268 | -61.5829 | 61.5829 | -0.011826 | 0.0060328 | 0.070867 | 0.065059 | -0.00053626 | -0.0027877 | 0.0022174 | 0.019959 | 0.0029928 | 0.069701 | 0.062963 | 0.0014569 | 0.0097326 | 0.0035078 | -0.064087 | 61.6837 | -61.7615 | 61.528 | -61.3129 | -61.7294 | -61.7294 | 0.032043 | 61.5829 | -61.7111 | 61.6791 | -61.496 | -61.4777 | -61.3358 | -0.17853 | 0.10071 | -0.054932 | 0.27008 | -0.14648 | -0.14648 | 0.032044 | 0.032044 | -0.12817 | 0 | 0.09613 | 0.086975 | 0.24719 | 0.10529 | 0.37537 | 0.23346 | 0.44861 | 123.2895 | 0.21515 | 123.3902 | 123.4451 | 123.2941 | 123.2666 | 123.1659 | -123.3444 | -123.2941 | 123.111 | 123.262 | 61.5189 | 61.615
110.5156 | 123.317 | -61.647 | 61.5967 | 0.011063 | 0.0079554 | 0.068945 | 0.066127 | 0.0026681 | -0.0025741 | 0.00029485 | -0.0014038 | 0.0025656 | 0.066497 | 0.056768 | -0.0011065 | 0.010587 | 0.0020124 | -0.10071 | 61.6974 | -61.8301 | 61.3998 | -61.4548 | -61.8576 | -61.8668 | -0.1236 | 61.5875 | -61.7249 | 61.5417 | -61.6516 | -61.647 | -61.4685 | -0.18311 | 0.10071 | -0.19684 | 0.19226 | -0.21973 | -0.21057 | -0.036621 | -0.027466 | -0.07782 | -0.009156 | -0.054932 | -0.004577 | 0.17853 | 0 | 0.25635 | 0.07782 | 0.37537 | 123.23 | 0.073243 | 123.2666 | 123.5275 | 123.3124 | 123.3444 | 123.2346 | -123.4268 | -123.3215 | 123.0469 | 123.1888 | 61.5463 | 61.5234
112.1875 | 123.4497 | -61.5555 | 61.6425 | -0.0041962 | 0.0036828 | 0.067236 | 0.065273 | 0.0015999 | -0.0012925 | -0.0012006 | 0.001648 | 0.0032064 | 0.067778 | 0.06574 | -0.0013201 | 0.01016 | -0.00033761 | -0.086975 | 61.7249 | -61.7706 | 61.5417 | -61.2854 | -61.6608 | -61.6882 | 0.027466 | 61.6104 | -61.6196 | 61.6928 | -61.441 | -61.4273 | -61.3037 | -0.21515 | 0.082398 | -0.10071 | 0.27008 | -0.13275 | -0.10529 | 0.082398 | 0.10986 | -0.064087 | -0.032043 | 0.050354 | 0.11444 | 0.25177 | 0.12817 | 0.31586 | 0.19226 | 0.48523 | 123.3124 | 0.17853 | 123.3124 | 123.4955 | 123.23 | 123.2803 | 123.1659 | -123.4131 | -123.262 | 123.0972 | 123.2483 | 61.4685 | 61.5829
113.8594 | 123.3719 | -61.6013 | 61.6104 | 0.011063 | 0.0073144 | 0.070013 | 0.0657 | 0.0075815 | -0.0012925 | -0.00034615 | 0.0077514 | 0.00577 | 0.067778 | 0.062322 | -0.00025213 | 0.011442 | -0.00033761 | -0.022888 | 61.7111 | -61.8073 | 61.4868 | -61.3541 | -61.7752 | -61.7844 | -0.009155 | 61.647 | -61.702 | 61.6013 | -61.5555 | -61.5509 | -61.3815 | -0.20599 | 0.10071 | -0.1236 | 0.24719 | -0.18311 | -0.17395 | 0.022888 | 0.032043 | -0.10071 | 0.036621 | -0.009156 | 0.045776 | 0.21973 | 0.050354 | 0.32043 | 0.15106 | 0.45319 | 123.2941 | 0.14648 | 123.3032 | 123.5184 | 123.349 | 123.3124 | 123.2483 | -123.4177 | -123.3124 | 123.0881 | 123.2025 | 61.5784 | 61.5921
115.5781 | 123.3536 | -61.6287 | 61.6333 | 0.033951 | 0.0049646 | 0.069799 | 0.067622 | 0.0039499 | -0.0017197 | 0.00050845 | 0.0077514 | 0.0042746 | 0.069915 | 0.060186 | 0.00017507 | 0.0080236 | -0.0035418 | -0.027466 | 61.7294 | -61.8484 | 61.4639 | -61.3632 | -61.7661 | -61.7752 | 0.009155 | 61.6241 | -61.7157 | 61.6104 | -61.5692 | -61.5417 | -61.3953 | -0.21973 | 0.09613 | -0.16937 | 0.2655 | -0.14648 | -0.13733 | 0.073242 | 0.082398 | -0.086975 | -0.009155 | -0.022888 | 0.059509 | 0.23346 | 0.086975 | 0.32043 | 0.17395 | 0.48523 | 123.3124 | 0.14648 | 123.3261 | 123.5779 | 123.3398 | 123.3582 | 123.2529 | -123.4818 | -123.349 | 123.0927 | 123.2391 | 61.6013 | 61.6379
117.25 | 123.381 | -61.5692 | 61.615 | 0.026321 | 0.0038966 | 0.070013 | 0.0657 | 0.0071541 | -0.0010789 | 0.0013628 | 0.0046998 | 0.0025656 | 0.069701 | 0.06574 | 0.0014569 | 0.0093054 | 0.0017988 | -0.09613 | 61.734 | -61.7752 | 61.5234 | -61.2946 | -61.7065 | -61.702 | -0.004578 | 61.6241 | -61.6653 | 61.6333 | -61.5143 | -61.4822 | -61.3449 | -0.20599 | 0.11902 | -0.091553 | 0.27466 | -0.13275 | -0.13733 | 0.073243 | 0.068665 | -0.09613 | 0.009156 | 0.018311 | 0.054932 | 0.2243 | 0.086975 | 0.32043 | 0.1831 | 0.48065 | 123.2986 | 0.15106 | 123.2986 | 123.5092 | 123.2895 | 123.3032 | 123.1934 | -123.3902 | -123.2803 | 123.0927 | 123.2025 | 61.4731 | 61.5646
118.9375 | 123.4314 | -61.5417 | 61.6241 | 0.0034333 | 0.0045374 | 0.071722 | 0.0657 | 0.0043771 | -0.00043789 | 0.0011492 | 0.001648 | 0.002352 | 0.067351 | 0.067663 | -0.0026019 | 0.01016 | -0.00055121 | -0.004578 | 61.7157 | -61.7203 | 61.5784 | -61.2396 | -61.6425 | -61.6562 | 0.068665 | 61.615 | -61.5967 | 61.6882 | -61.4273 | -61.4136 | -61.3037 | -0.17853 | 0.091552 | -0.045777 | 0.30212 | -0.11444 | -0.10071 | 0.064087 | 0.07782 | -0.054932 | -0.009156 | 0.064086 | 0.11444 | 0.23804 | 0.12817 | 0.29297 | 0.18311 | 0.48065 | 123.2986 | 0.16937 | 123.2849 | 123.436 | 123.2117 | 123.2574 | 123.1567 | -123.3444 | -123.2208 | 123.1201 | 123.23 | 61.5372 | 61.6104
120.6094 | 123.381 | -61.5601 | 61.6333 | 0.033951 | 0.004751 | 0.068304 | 0.066341 | 0.0073679 | -0.0010789 | -0.003764 | 0.0077514 | 0.0014976 | 0.069274 | 0.06339 | -0.00046573 | 0.010587 | 0.0020124 | -0.068665 | 61.7111 | -61.7477 | 61.528 | -61.2946 | -61.7386 | -61.7111 | -0.032043 | 61.6058 | -61.647 | 61.6516 | -61.5189 | -61.4914 | -61.3358 | -0.18768 | 0.07782 | -0.10529 | 0.2655 | -0.15106 | -0.17853 | 0.036621 | 0.009156 | -0.086975 | -0.027466 | 0.01831 | 0.041199 | 0.22431 | 0.068665 | 0.31128 | 0.15564 | 0.45319 | 123.2758 | 0.12817 | 123.2986 | 123.4589 | 123.2529 | 123.2712 | 123.1659 | -123.381 | -123.2803 | 123.0881 | 123.2117 | 61.4914 | 61.528
122.3125 | 123.4497 | -61.5417 | 61.6196 | -0.0041962 | 0.0053918 | 0.068304 | 0.065486 | 0.0011727 | -0.0027877 | -0.00098695 | 0.0046998 | 2.194e-06 | 0.068633 | 0.063818 | -0.0021747 | 0.0093054 | -0.00097841 | -0.027466 | 61.7065 | -61.7294 | 61.5738 | -61.2213 | -61.6333 | -61.6516 | 0.064087 | 61.6058 | -61.6196 | 61.7157 | -61.3953 | -61.3815 | -61.2717 | -0.18768 | 0.086975 | -0.045776 | 0.32043 | -0.10986 | -0.091553 | 0.07782 | 0.09613 | -0.07782 | -0.013733 | 0.09613 | 0.14648 | 0.27008 | 0.16022 | 0.3479 | 0.23804 | 0.50812 | 123.3032 | 0.2243 | 123.3353 | 123.436 | 123.2254 | 123.2483 | 123.1476 | -123.349 | -123.2391 | 123.1155 | 123.2574 | 61.5143 | 61.6058
123.9844 | 123.2986 | -61.615 | 61.6196 | 0.0034333 | 0.0051782 | 0.071722 | 0.067622 | 0.0082223 | 0.00063011 | -0.0033368 | 0.001648 | 0.0049154 | 0.068206 | 0.053137 | 0.00017507 | 0.0093054 | -0.0018328 | -0.09613 | 61.6837 | -61.8347 | 61.4319 | -61.4273 | -61.8347 | -61.8393 | -0.11444 | 61.6287 | -61.702 | 61.5555 | -61.6196 | -61.6196 | -61.4273 | -0.21973 | 0.064087 | -0.18768 | 0.18768 | -0.2243 | -0.21973 | -0.004577 | 0 | -0.086975 | 0.009155 | -0.064087 | -0.004578 | 0.18768 | -0.004578 | 0.27466 | 0.082397 | 0.40741 | 123.2666 | 0.082397 | 123.2574 | 123.5184 | 123.3307 | 123.2986 | 123.2437 | -123.4543 | -123.3215 | 123.0469 | 123.1705 | 61.5189 | 61.5005
125.6875 | 123.4314 | -61.5692 | 61.5784 | -0.0041962 | 0.0034692 | 0.071295 | 0.064204 | 0.0033089 | -0.0032151 | -0.0016278 | 0.0046998 | 0.0042746 | 0.069274 | 0.061895 | 0.0042341 | 0.011228 | -0.0016192 | -0.054932 | 61.6791 | -61.7569 | 61.528 | -61.29 | -61.7249 | -61.7249 | 0.022888 | 61.5646 | -61.6516 | 61.6974 | -61.4685 | -61.4731 | -61.3129 | -0.18768 | 0.10071 | -0.050354 | 0.27924 | -0.15564 | -0.15564 | 0.032043 | 0.032043 | -0.082397 | -0.013733 | 0.11902 | 0.10071 | 0.25635 | 0.096131 | 0.33875 | 0.17853 | 0.46692 | 123.2849 | 0.18311 | 123.349 | 123.436 | 123.2162 | 123.2483 | 123.1338 | -123.3353 | -123.23 | 123.0972 | 123.2666 | 61.5143 | 61.5921
127.3594 | 123.2986 | -61.5555 | 61.6653 | 0.0034333 | 0.004751 | 0.071295 | 0.066768 | 0.0033089 | -0.0012925 | 8.125e-05 | 0.001648 | 0.0012838 | 0.067351 | 0.058904 | -0.0032427 | 0.0097326 | 0.00094419 | -0.07782 | 61.7523 | -61.7523 | 61.4639 | -61.3449 | -61.7294 | -61.7615 | -0.050354 | 61.6516 | -61.6287 | 61.5738 | -61.5555 | -61.5326 | -61.3907 | -0.19684 | 0.086975 | -0.20142 | 0.21057 | -0.20599 | -0.17395 | -0.009156 | 0.022888 | -0.073242 | -0.013733 | -0.091552 | 0 | 0.16479 | 0.022888 | 0.23804 | 0.09613 | 0.40741 | 123.2162 | 0.073242 | 123.2025 | 123.5046 | 123.2803 | 123.3078 | 123.2071 | -123.4177 | -123.2941 | 123.0194 | 123.1293 | 61.4777 | 61.5051
129.0312 | 123.3261 | -61.5967 | 61.6379 | 0.0034333 | 0.0028284 | 0.070013 | 0.066768 | 0.0045907 | -0.0010789 | -0.002696 | -0.0014038 | 0.0044882 | 0.069701 | 0.072149 | -0.00046573 | 0.0099462 | -0.00055121 | -0.1236 | 61.7157 | -61.7798 | 61.409 | -61.4044 | -61.8256 | -61.8118 | -0.10986 | 61.5921 | -61.6562 | 61.5784 | -61.5784 | -61.5921 | -61.3724 | -0.1831 | 0.07782 | -0.22888 | 0.19226 | -0.21515 | -0.22888 | -0.032044 | -0.045777 | -0.059509 | -0.045776 | -0.059509 | 0.018311 | 0.22431 | 0.004578 | 0.28381 | 0.064087 | 0.37537 | 123.1888 | 0.07782 | 123.2346 | 123.4955 | 123.2483 | 123.3124 | 123.1888 | -123.4177 | -123.2941 | 123.0057 | 123.175 | 61.4731 | 61.4868
130.75 | 123.3856 | -61.528 | 61.647 | 0.033951 | 0.0066736 | 0.069799 | 0.066554 | 0.0073679 | -0.0012925 | 0.00050845 | 0.013855 | 0.0017112 | 0.067778 | 0.061254 | -0.0015337 | 0.0097326 | -0.0026874 | -0.068665 | 61.7111 | -61.7294 | 61.5646 | -61.2305 | -61.6837 | -61.6745 | 0.036621 | 61.6013 | -61.6287 | 61.6699 | -61.4731 | -61.4456 | -61.3083 | -0.20142 | 0.064087 | -0.082398 | 0.29755 | -0.14648 | -0.15564 | 0.054931 | 0.045776 | -0.10071 | -0.045777 | 0.022888 | 0.054932 | 0.21973 | 0.082397 | 0.32043 | 0.1831 | 0.49896 | 123.2941 | 0.15564 | 123.2986 | 123.4406 | 123.23 | 123.2391 | 123.1293 | -123.3765 | -123.2758 | 123.0927 | 123.1979 | 61.4594 | 61.5646
132.4219 | 123.3307 | -61.5921 | 61.6791 | 0.033951 | 0.0058192 | 0.07044 | 0.067836 | 0.0048043 | -0.0021469 | -0.00034615 | 0.0046998 | 0.0053428 | 0.071624 | 0.053777 | -0.0019611 | 0.0073828 | 8.9786e-05 | -0.022888 | 61.734 | -61.7889 | 61.5051 | -61.3083 | -61.7294 | -61.7294 | 0.004578 | 61.6516 | -61.647 | 61.615 | -61.5051 | -61.5051 | -61.3449 | -0.19684 | 0.054932 | -0.17395 | 0.28381 | -0.13733 | -0.13733 | 0.059509 | 0.059509 | -0.054932 | -0.027466 | -0.064087 | 0.086975 | 0.24719 | 0.086975 | 0.30212 | 0.14191 | 0.48065 | 123.2941 | 0.14191 | 123.262 | 123.5229 | 123.2986 | 123.3261 | 123.2437 | -123.468 | -123.3261 | 123.0972 | 123.2071 | 61.5692 | 61.5967
134.125 | 123.2849 | -61.5372 | 61.6974 | 0.0034333 | 0.0036828 | 0.068517 | 0.065273 | 0.0060861 | -0.0019333 | 0.0013628 | 0.001648 | 0.0029928 | 0.066924 | 0.064459 | -0.0047381 | 0.0088782 | 8.9786e-05 | -0.022888 | 61.7661 | -61.7111 | 61.5326 | -61.2671 | -61.6653 | -61.6745 | -0.013733 | 61.6699 | -61.6058 | 61.6196 | -61.5097 | -61.4914 | -61.3495 | -0.17395 | 0.068664 | -0.16479 | 0.27008 | -0.13733 | -0.12817 | 0.036621 | 0.045777 | -0.068665 | -0.027466 | -0.07782 | 0.027465 | 0.18768 | 0.045776 | 0.25635 | 0.11444 | 0.44403 | 123.2437 | 0.09613 | 123.2254 | 123.4772 | 123.2758 | 123.3032 | 123.2071 | -123.4085 | -123.3032 | 123.0698 | 123.1567 | 61.5143 | 61.5234
135.8438 | 123.2849 | -61.5509 | 61.7065 | 0.0034333 | 0.0049646 | 0.068945 | 0.065486 | 0.0033089 | -0.0030015 | -0.002696 | 0.02301 | 0.0053428 | 0.07141 | 0.059972 | -0.0030291 | 0.008451 | 0.00094419 | -0.07782 | 61.8073 | -61.7294 | 61.5051 | -61.3129 | -61.6837 | -61.6928 | -0.050354 | 61.7111 | -61.6287 | 61.6104 | -61.528 | -61.5143 | -61.3495 | -0.17853 | 0.10071 | -0.20142 | 0.23804 | -0.14191 | -0.13275 | 0.036621 | 0.045776 | -0.07782 | 0.004578 | -0.09613 | 0.022888 | 0.20142 | 0.036621 | 0.27924 | 0.11444 | 0.41656 | 123.2346 | 0.10071 | 123.2391 | 123.5367 | 123.3398 | 123.3582 | 123.262 | -123.436 | -123.3353 | 123.056 | 123.1613 | 61.4731 | 61.5005
137.5312 | 123.2574 | -61.5829 | 61.6699 | 0.0034333 | 0.0053918 | 0.068517 | 0.063564 | 0.0097177 | -0.0021469 | -0.0022688 | 0.0046998 | 0.0025656 | 0.067992 | 0.059972 | -0.0023883 | 0.010374 | -0.00033761 | -0.09613 | 61.7569 | -61.7569 | 61.4502 | -61.3907 | -61.7935 | -61.7935 | -0.14191 | 61.6837 | -61.6287 | 61.5692 | -61.5875 | -61.5784 | -61.3861 | -0.17395 | 0.086975 | -0.21973 | 0.19226 | -0.21057 | -0.21057 | -0.036621 | -0.036621 | -0.045776 | 0.013733 | -0.10071 | -0.004577 | 0.19684 | 0.004578 | 0.24262 | 0.050354 | 0.36621 | 123.2071 | 0.041199 | 123.1979 | 123.5138 | 123.3124 | 123.3398 | 123.2666 | -123.4268 | -123.2986 | 123.0331 | 123.1522 | 61.4868 | 61.441
139.2031 | 123.3582 | -61.4914 | 61.6882 | 0.026321 | 0.0024012 | 0.068731 | 0.064632 | 0.0050179 | -0.00022429 | -0.0016278 | 0.0046998 | 0.0019248 | 0.069487 | 0.065099 | -0.0015337 | 0.0097326 | -0.0020464 | -0.09613 | 61.7569 | -61.6653 | 61.5601 | -61.2305 | -61.6425 | -61.6379 | -0.027466 | 61.6699 | -61.5463 | 61.7065 | -61.4365 | -61.4182 | -61.2762 | -0.17395 | 0.068665 | -0.12817 | 0.26093 | -0.14648 | -0.15106 | 0.027466 | 0.022888 | -0.054932 | -0.01831 | 0.018311 | 0.054932 | 0.21515 | 0.073242 | 0.27008 | 0.12817 | 0.43487 | 123.2254 | 0.10986 | 123.2529 | 123.4222 | 123.2162 | 123.2483 | 123.1613 | -123.3536 | -123.2346 | 123.0515 | 123.1979 | 61.3953 | 61.4639
140.875 | 123.2712 | -61.4822 | 61.7523 | -0.0041962 | 0.0049646 | 0.068304 | 0.066341 | 0.0039499 | -0.0044967 | -0.00055975 | 0.001648 | 0.0042746 | 0.069274 | 0.059972 | -0.0026019 | 0.0088782 | -0.00033761 | -0.059509 | 61.7935 | -61.6837 | 61.5372 | -61.2762 | -61.6562 | -61.6653 | -0.054932 | 61.7294 | -61.5601 | 61.6425 | -61.4685 | -61.4685 | -61.3174 | -0.20142 | 0.041199 | -0.21515 | 0.20599 | -0.1831 | -0.17395 | 0.018311 | 0.027466 | -0.07782 | -0.022888 | -0.10986 | 0.013733 | 0.16479 | 0.013733 | 0.24262 | 0.091553 | 0.40741 | 123.2208 | 0.091553 | 123.2025 | 123.4772 | 123.2895 | 123.2758 | 123.2117 | -123.436 | -123.3124 | 123.0194 | 123.1247 | 61.4227 | 61.4273
142.5469 | 123.3582 | -61.4548 | 61.7157 | 0.018692 | 0.0034692 | 0.069586 | 0.067195 | -0.00010886 | -1.0686e-05 | -0.003764 | 0.0077514 | 0.0053428 | 0.068846 | 0.057195 | -0.00025213 | 0.011655 | 0.00030339 | -0.082397 | 61.821 | -61.6425 | 61.5784 | -61.2122 | -61.6058 | -61.6104 | -0.032043 | 61.6837 | -61.5372 | 61.7157 | -61.409 | -61.377 | -61.2488 | -0.18768 | 0.10529 | -0.13733 | 0.24262 | -0.15564 | -0.15106 | 0.032043 | 0.036621 | -0.082397 | -0.032043 | 0 | 0.045776 | 0.20599 | 0.07782 | 0.28839 | 0.16022 | 0.4303 | 123.2208 | 0.12817 | 123.2529 | 123.4634 | 123.2208 | 123.2758 | 123.1384 | -123.3582 | -123.2529 | 123.0331 | 123.1705 | 61.3724 | 61.4227
144.2031 | 123.2666 | -61.496 | 61.7249 | 0.0034333 | 0.0071008 | 0.069586 | 0.066554 | 0.0043771 | -0.0023605 | -0.0024824 | 0.0046998 | 0.0049154 | 0.066924 | 0.0557 | -0.0015337 | 0.0090918 | -0.0037554 | -0.086975 | 61.7935 | -61.7249 | 61.4914 | -61.2991 | -61.7294 | -61.7386 | -0.09613 | 61.7203 | -61.5784 | 61.6379 | -61.5234 | -61.5097 | -61.3037 | -0.22888 | 0.068664 | -0.23346 | 0.19684 | -0.24261 | -0.23346 | -0.013732 | -0.004577 | -0.082397 | -0.004578 | -0.086976 | -0.027465 | 0.19226 | -0.013733 | 0.27466 | 0.068664 | 0.42572 | 123.2162 | 0.054932 | 123.2162 | 123.5184 | 123.2986 | 123.2895 | 123.2162 | -123.4497 | -123.3032 | 122.9874 | 123.1338 | 61.409 | 61.3998
145.875 | 123.3765 | -61.4273 | 61.7157 | 0.011063 | 0.0038966 | 0.069158 | 0.063991 | 0.0050179 | -0.0021469 | 0.00029485 | 0.010803 | 0.0019248 | 0.070555 | 0.065527 | -0.0021747 | 0.01016 | -0.0016192 | -0.091553 | 61.8347 | -61.6562 | 61.6058 | -61.1755 | -61.5875 | -61.5967 | -0.045776 | 61.734 | -61.5143 | 61.7477 | -61.3724 | -61.3449 | -61.1801 | -0.22888 | 0.11902 | -0.10986 | 0.25177 | -0.16937 | -0.16022 | 0.059509 | 0.068665 | -0.086975 | 0.018311 | 0.032044 | 0.054932 | 0.24719 | 0.082397 | 0.33417 | 0.16937 | 0.48065 | 123.262 | 0.14191 | 123.262 | 123.4909 | 123.2483 | 123.262 | 123.1613 | -123.3719 | -123.23 | 123.0331 | 123.175 | 61.3358 | 61.3815
147.5469 | 123.317 | -61.4365 | 61.7477 | 0.026321 | 0.0073144 | 0.068517 | 0.067409 | 0.0067269 | 0.00020291 | -0.0024824 | 0.0077514 | 0.0044882 | 0.068419 | 0.059332 | 0.00017507 | 0.0069556 | -0.0016192 | -0.032043 | 61.8805 | -61.6699 | 61.5967 | -61.2259 | -61.6104 | -61.6287 | -0.022888 | 61.734 | -61.5417 | 61.702 | -61.409 | -61.3953 | -61.2396 | -0.23346 | 0.13275 | -0.15106 | 0.21057 | -0.19226 | -0.17395 | 0.041199 | 0.059509 | -0.10529 | -0.013733 | -0.045777 | 0.027465 | 0.19684 | 0.041198 | 0.30212 | 0.14648 | 0.44403 | 123.2666 | 0.13275 | 123.2437 | 123.5504 | 123.2758 | 123.317 | 123.1705 | -123.4177 | -123.2895 | 123.0331 | 123.1384 | 61.4044 | 61.4136
149.25 | 123.262 | -61.4639 | 61.7569 | -0.0041962 | 0.0049646 | 0.070013 | 0.066982 | 0.0028817 | -0.0021469 | 0.0011492 | 0.001648 | 0.0034202 | 0.068846 | 0.059332 | -3.8532e-05 | 0.011442 | -0.00097841 | -0.10071 | 61.8439 | -61.6608 | 61.5143 | -61.29 | -61.702 | -61.6791 | -0.10071 | 61.7294 | -61.5509 | 61.6837 | -61.4594 | -61.4822 | -61.2717 | -0.19684 | 0.086975 | -0.24262 | 0.17395 | -0.21515 | -0.23804 | -0.01831 | -0.041198 | -0.086975 | -0.027466 | -0.073242 | 0.004577 | 0.19226 | -0.018311 | 0.27924 | 0.068664 | 0.37079 | 123.175 | 0.091552 | 123.2346 | 123.5046 | 123.2803 | 123.3078 | 123.1934 | -123.4177 | -123.3078 | 122.9782 | 123.1476 | 61.3632 | 61.3632
150.9844 | 123.2803 | -61.409 | 61.8301 | 0.0034333 | 0.0071008 | 0.070226 | 0.062923 | 0.0018137 | -0.0044967 | -0.0022688 | 0.0046998 | 0.0038474 | 0.067565 | 0.059759 | -0.0036701 | 0.0080236 | 0.0013714 | -0.07782 | 61.8988 | -61.6104 | 61.5784 | -61.1984 | -61.6013 | -61.5829 | -0.073242 | 61.7935 | -61.4914 | 61.7157 | -61.3998 | -61.3815 | -61.2305 | -0.20142 | 0.068665 | -0.25177 | 0.21057 | -0.17395 | -0.19226 | 0.027466 | 0.009156 | -0.082397 | -0.036621 | -0.11444 | 0.009156 | 0.17853 | 0.027466 | 0.26093 | 0.10986 | 0.41199 | 123.1888 | 0.091553 | 123.2071 | 123.5092 | 123.2849 | 123.3078 | 123.2025 | -123.4406 | -123.3215 | 122.9874 | 123.1247 | 61.3312 | 61.3358
152.6875 | 123.3307 | -61.3586 | 61.7798 | 0.011063 | 0.0036828 | 0.069372 | 0.065059 | 0.0069405 | -0.0012925 | -0.0016278 | 0.0046998 | 0.0021384 | 0.068206 | 0.061254 | 0.00060247 | 0.01016 | 0.002226 | -0.11902 | 61.8668 | -61.6058 | 61.6379 | -61.1389 | -61.528 | -61.5372 | -0.041199 | 61.7615 | -61.4502 | 61.7844 | -61.322 | -61.2991 | -61.1435 | -0.24719 | 0.086975 | -0.14191 | 0.21973 | -0.17853 | -0.16937 | 0.068665 | 0.07782 | -0.091552 | -0.01831 | 0.004578 | 0.036622 | 0.21515 | 0.05951 | 0.3067 | 0.15106 | 0.46692 | 123.2437 | 0.12817 | 123.2346 | 123.4726 | 123.2117 | 123.2254 | 123.1201 | -123.3856 | -123.23 | 122.9965 | 123.143 | 61.2396 | 61.3174
154.3594 | 123.3398 | -61.4319 | 61.7065 | 0.033951 | 0.0088098 | 0.072576 | 0.065913 | 0.0054453 | -0.00086509 | -0.00013235 | 0.013855 | 0.0027792 | 0.068633 | 0.064459 | 0.0012433 | 0.010801 | -0.001192 | -0.068665 | 61.8439 | -61.5829 | 61.6745 | -61.0886 | -61.5326 | -61.528 | 0.045776 | 61.7294 | -61.4914 | 61.8164 | -61.322 | -61.3129 | -61.1526 | -0.15106 | 0.13733 | -0.032043 | 0.34332 | -0.09613 | -0.10071 | 0.054932 | 0.050354 | -0.059509 | 0.022888 | 0.10986 | 0.10986 | 0.27924 | 0.11902 | 0.33875 | 0.17853 | 0.49438 | 123.2574 | 0.16937 | 123.3078 | 123.4268 | 123.2208 | 123.2758 | 123.1613 | -123.2895 | -123.1979 | 123.1064 | 123.2483 | 61.3632 | 61.4777
156.0625 | 123.1293 | -69.4244 | 54.538 | -0.0041962 | 0.0036828 | 0.067877 | 0.068904 | 0.0050179 | -0.0023605 | 0.0017902 | 0.016907 | 0.0061972 | 0.068633 | 0.058477 | -0.0036701 | 0.0071692 | 8.9786e-05 | 4.4174 | 55.4031 | -67.7628 | 58.2779 | -63.9038 | -64.5126 | -64.2151 | 8.7845 | 60.0357 | -63.0753 | 42.8055 | -72.6837 | -68.6279 | -67.8452 | 1.6617 | 0.86517 | 3.7399 | 5.5206 | 5.2094 | 4.9118 | 3.5477 | 3.2501 | 6.3492 | 5.4977 | -11.7325 | -3.2593 | 1.5793 | 0.79651 | -4.7699 | -5.5527 | 3.8589 | 126.0406 | -9.6085 | 105.8807 | 123.1659 | 123.111 | 124.8276 | 129.4601 | -122.3007 | -117.6132 | 127.7023 | 112.2299 | 73.8419 | 78.2089
157.7656 | 123.381 | -119.0414 | 4.1428 | 0.011063 | 0.0021876 | 0.06809 | 0.067836 | 0.0024545 | -0.0019333 | -0.0020552 | 0.001648 | 0.0027792 | 0.069915 | 0.087743 | -0.0021747 | 0.0093054 | 0.00030339 | -0.34332 | 4.1565 | -119.3253 | 3.9322 | -118.4738 | -119.0506 | -119.1513 | -0.30212 | 4.1336 | -119.2337 | 3.9551 | -118.7714 | -118.7668 | -118.5379 | -0.28381 | 0.013733 | -0.21057 | 0.56763 | -0.10986 | -0.009155 | 0.17395 | 0.27466 | -0.19226 | -0.009155 | -0.18768 | 0.27008 | 0.50354 | 0.27466 | 0.6958 | 0.46692 | 0.85144 | 123.2574 | 0.46234 | 123.1888 | 123.4817 | 123.3673 | 123.1979 | 123.175 | -123.468 | -123.3765 | 122.9736 | 122.9965 | 118.6981 | 118.7393
159.4531 | 123.3124 | -119.3069 | 3.9185 | -0.0041962 | 0.0045374 | 0.06809 | 0.069118 | 0.0020273 | -0.0015061 | -0.0020552 | 0.001648 | 0.004061 | 0.066924 | 0.086035 | 0.00081607 | 0.0090918 | 0.0017988 | -0.35706 | 3.9688 | -119.5587 | 3.6072 | -118.7576 | -119.3436 | -119.3985 | -0.36163 | 3.9276 | -119.4717 | 3.7216 | -119.0506 | -119.0598 | -118.7714 | -0.25177 | 0.050354 | -0.31128 | 0.54932 | -0.091553 | -0.036621 | 0.16022 | 0.21515 | -0.16479 | 0.009155 | -0.19684 | 0.25635 | 0.53558 | 0.24719 | 0.70038 | 0.41199 | 0.80109 | 123.1659 | 0.42114 | 123.1934 | 123.5275 | 123.3994 | 123.2758 | 123.2346 | -123.4772 | -123.3902 | 122.9141 | 123.0286 | 118.9499 | 118.9453
161.125 | 123.3078 | -120.195 | 3.0899 | 0.079727 | 0.00646 | 0.070013 | 0.06805 | 0.0041635 | -0.0015061 | 0.00072205 | 0.026062 | 0.0059836 | 0.07141 | 0.084112 | -0.0026019 | 0.0071692 | -0.00076481 | -0.24719 | 3.1906 | -120.4559 | 2.829 | -119.5724 | -120.1309 | -120.2362 | -0.25635 | 3.1219 | -120.3278 | 2.861 | -119.8791 | -119.8837 | -119.6091 | -0.26093 | 0.10071 | -0.26093 | 0.62256 | -0.041199 | 0.064087 | 0.21973 | 0.32501 | -0.13275 | 0.032043 | -0.22888 | 0.31586 | 0.58594 | 0.31128 | 0.71869 | 0.44403 | 0.88348 | 123.2849 | 0.44861 | 123.1888 | 123.6465 | 123.4497 | 123.3856 | 123.317 | -123.5458 | -123.4177 | 123.024 | 123.056 | 119.9478 | 119.9387
162.7969 | 123.2758 | -119.4122 | 3.8544 | -0.0041962 | 0.0049646 | 0.069586 | 0.065486 | -0.0013907 | -0.0040695 | 0.0020038 | -0.0014038 | 0.00064299 | 0.069274 | 0.086889 | -0.0015337 | 0.008451 | -0.00055121 | -0.27924 | 3.891 | -119.6594 | 3.5706 | -118.7943 | -119.3756 | -119.4672 | -0.27008 | 3.8681 | -119.5175 | 3.653 | -119.101 | -119.0735 | -118.8263 | -0.24719 | 0.036621 | -0.28381 | 0.61798 | -0.054932 | 0.036621 | 0.19226 | 0.28381 | -0.10529 | 0.013733 | -0.20142 | 0.31128 | 0.58594 | 0.33875 | 0.69122 | 0.44403 | 0.86517 | 123.23 | 0.41656 | 123.1705 | 123.5504 | 123.3856 | 123.3032 | 123.2803 | -123.5138 | -123.3719 | 122.9828 | 123.0652 | 119.133 | 119.1422
164.5312 | 123.3078 | -118.9636 | 4.2892 | 0.0034333 | 0.004751 | 0.071722 | 0.062923 | 0.0013863 | -0.0021469 | -0.00013235 | 0.001648 | 0.00042939 | 0.069915 | 0.093725 | -0.0034563 | 0.010587 | -0.001192 | -0.24261 | 4.3076 | -119.1513 | 4.0878 | -118.2861 | -118.8675 | -118.9636 | -0.2243 | 4.2755 | -119.0643 | 4.129 | -118.6066 | -118.6066 | -118.3411 | -0.18768 | 0.01831 | -0.20142 | 0.67749 | 0 | 0.09613 | 0.18768 | 0.28381 | -0.10071 | -0.013733 | -0.16022 | 0.35706 | 0.62256 | 0.35706 | 0.72327 | 0.45776 | 0.86517 | 123.2391 | 0.45776 | 123.1934 | 123.4589 | 123.3398 | 123.2712 | 123.2391 | -123.4406 | -123.3536 | 123.0515 | 123.0927 | 118.721 | 118.7393
166.2031 | 123.4497 | -119.7784 | 3.3783 | 0.011063 | 0.001333 | 0.071508 | 0.063777 | 0.0028817 | -0.00086509 | -0.0029096 | -0.0044556 | 0.0019248 | 0.069487 | 0.16636 | 0.00081607 | 0.010374 | -0.0024738 | -0.27008 | 3.7262 | -119.87 | 3.2455 | -119.5633 | -120.1904 | -119.7327 | -0.41199 | 3.3234 | -120.1401 | 3.36 | -119.7327 | -119.8013 | -119.1467 | -0.091553 | 0.3479 | -0.13275 | 0.21515 | 0.045776 | -0.41199 | 0.13733 | -0.32044 | -0.36163 | -0.054932 | -0.018311 | 0.045776 | 0.63171 | -0.022889 | 0.99335 | 0.33874 | 0.3067 | 123.1155 | 0.40741 | 123.5001 | 123.5962 | 123.4634 | 123.5046 | 123.1018 | -123.2483 | -123.5184 | 123.024 | 123.1384 | 119.5084 | 119.3665
167.8906 | 123.2254 | -57.3853 | 65.5838 | 0.0034333 | 0.0066736 | 0.065527 | 0.062923 | 0.0035227 | -0.00043789 | -0.012095 | 0.0046998 | -0.0012796 | 0.070769 | 0.064886 | -0.0023883 | 0.0088782 | -0.001192 | -0.34332 | 61.6608 | -60.7727 | 68.5135 | -55.3345 | -56.5201 | -55.4489 | 4.1473 | 68.9163 | -54.0802 | 68.2526 | -59.0836 | -58.5297 | -56.3324 | -3.3875 | -3.923 | 2.9297 | 2.0508 | 1.9363 | 0.86517 | 5.3238 | 4.2526 | 3.3051 | 3.3325 | 2.6688 | -1.6983 | 1.0529 | -1.1444 | -2.2522 | -4.4495 | 5.4382 | 129.2862 | -5.0034 | 122.3328 | 122.4335 | 122.9965 | 119.046 | 126.3016 | -126.3565 | -119.664 | 125.8987 | 125.6378 | 57.0419 | 61.5326
169.5625 | 123.4589 | -118.7485 | 4.3579 | 0.018692 | 0.0038966 | 0.071081 | 0.066127 | 0.0015999 | -0.0027877 | -0.00034615 | 0.0077514 | 0.0017112 | 0.068633 | 0.15824 | 0.00081607 | 0.011869 | -0.00097841 | -0.2655 | 4.3671 | -119.046 | 4.1885 | -117.9245 | -118.5104 | -118.5471 | -0.19684 | 4.2801 | -119.0048 | 4.2572 | -118.2816 | -118.19 | -117.9337 | -0.29755 | 0.009155 | -0.16937 | 0.82397 | 0.20142 | 0.23804 | 0.49896 | 0.53558 | -0.25635 | -0.07782 | -0.10071 | 0.46692 | 0.81482 | 0.55847 | 1.0712 | 0.81482 | 1.1215 | 123.2346 | 0.72327 | 123.262 | 123.4131 | 123.2849 | 123.1155 | 123.0286 | -123.4039 | -123.3627 | 122.937 | 123.0057 | 118.483 | 118.5516
171.25 | 123.3032 | -118.6661 | 4.5044 | 0.0034333 | 0.0056054 | 0.071722 | 0.066768 | -0.0028861 | -0.0021469 | -0.005473 | 0.001648 | -0.0017068 | 0.071837 | 0.15012 | 0.0010297 | 0.013151 | -0.001192 | -0.27924 | 4.5776 | -118.9133 | 4.2252 | -118.0252 | -118.515 | -118.9682 | -0.31128 | 4.5273 | -118.8126 | 4.3579 | -118.1717 | -117.952 | -117.7689 | -0.24719 | 0.073242 | -0.27924 | 0.64087 | -0.30212 | 0.15106 | -0.054932 | 0.39825 | -0.14648 | 0.022888 | -0.14648 | 0.49439 | 0.89722 | 0.71411 | 1.0437 | 0.8606 | 0.88806 | 123.1384 | 0.64087 | 123.1705 | 123.4909 | 123.3398 | 123.2437 | 123.1934 | -123.4177 | -123.317 | 122.8912 | 123.024 | 118.3868 | 118.3548
173 | 123.3078 | -118.8354 | 4.3762 | 0.0034333 | 0.0049646 | 0.071935 | 0.0704 | -0.00032266 | 0.0014847 | -0.0012006 | 0.010803 | 0.0042746 | 0.068419 | 0.1561 | -0.00046573 | 0.0097326 | -0.00012381 | -0.28381 | 4.4083 | -119.0781 | 4.0695 | -117.8787 | -118.483 | -118.4738 | -0.27466 | 4.3671 | -118.9545 | 4.1977 | -118.5425 | -118.2724 | -117.8787 | -0.24262 | 0.032043 | -0.3067 | 0.95673 | 0.36163 | 0.35248 | 0.60425 | 0.59509 | -0.11902 | -0.009156 | -0.17853 | 0.29297 | 0.95673 | 0.56305 | 1.0757 | 0.68207 | 1.1993 | 123.1476 | 0.41199 | 123.1522 | 123.4863 | 123.3215 | 123.2437 | 123.2025 | -123.4543 | -123.3307 | 122.905 | 123.0331 | 118.5516 | 118.5608
174.6719 | 123.2803 | -118.9911 | 4.2709 | 0.018692 | 0.0036828 | 0.070867 | 0.068477 | 0.0084359 | -0.0030015 | 0.00029485 | 0.0077514 | 0.004061 | 0.069701 | 0.15183 | 0.00017507 | 0.010374 | 0.0024396 | -0.27008 | 4.3442 | -119.1605 | 3.978 | -118.0618 | -118.6386 | -118.5883 | -0.30212 | 4.2847 | -119.0369 | 4.0878 | -118.7027 | -118.4647 | -118.0389 | -0.16937 | 0.073242 | -0.29297 | 0.92926 | 0.40283 | 0.35248 | 0.5722 | 0.52185 | -0.045776 | 0.013733 | -0.1831 | 0.28839 | 0.95215 | 0.52643 | 0.99793 | 0.5722 | 1.0986 | 123.1384 | 0.33417 | 123.1247 | 123.5046 | 123.3215 | 123.3353 | 123.2758 | -123.4314 | -123.3078 | 122.9691 | 123.0789 | 118.721 | 118.689
176.3438 | 123.2986 | -118.8675 | 4.3716 | 0.072098 | 0.0073144 | 0.073004 | 0.070186 | 0.00074554 | -0.0021469 | -0.0014142 | 0.032166 | 0.0053428 | 0.071196 | 0.15268 | -0.0021747 | 0.009519 | -0.0014056 | -0.27008 | 4.4769 | -119.1376 | 4.129 | -117.9703 | -118.5104 | -118.4967 | -0.24261 | 4.4174 | -118.9728 | 4.184 | -118.5104 | -118.3136 | -117.8558 | -0.27008 | 0.10529 | -0.24261 | 0.89722 | 0.37079 | 0.35706 | 0.64087 | 0.62714 | -0.10529 | 0.045776 | -0.18768 | 0.35706 | 1.0117 | 0.55389 | 1.1169 | 0.65918 | 1.1673 | 123.2666 | 0.46234 | 123.1567 | 123.6145 | 123.3902 | 123.3444 | 123.2849 | -123.5092 | -123.3444 | 122.9965 | 123.0515 | 118.5974 | 118.6249
178.0469 | 123.3078 | -119.1055 | 4.129 | 0.04158 | 0.00646 | 0.071295 | 0.068477 | 0.0041635 | -0.0019333 | 0.0011492 | 0.019959 | 0.0055564 | 0.069915 | 0.15845 | -0.00025213 | 0.010587 | -0.00097841 | -0.17395 | 4.1794 | -119.3481 | 3.9139 | -118.1259 | -118.6798 | -118.6523 | -0.15106 | 4.1153 | -119.1971 | 3.9963 | -118.7347 | -118.5425 | -118.0481 | -0.24262 | 0.050354 | -0.21515 | 0.97961 | 0.45319 | 0.42572 | 0.6958 | 0.66833 | -0.091553 | -0.013733 | -0.13275 | 0.37079 | 1.0574 | 0.56305 | 1.149 | 0.6546 | 1.2222 | 123.262 | 0.46234 | 123.1934 | 123.5275 | 123.3124 | 123.2849 | 123.2208 | -123.4772 | -123.3261 | 123.0194 | 123.1018 | 118.9316 | 118.9545
179.7188 | 123.4131 | -118.7576 | 4.4128 | 0.011063 | 0.0017602 | 0.071935 | 0.065273 | 0.0039499 | -0.0017197 | 0.0022174 | 0.0046998 | 0.0010702 | 0.06671 | 0.16102 | -3.8532e-05 | 0.011228 | -0.0024738 | -0.23346 | 4.454 | -118.959 | 4.2984 | -118.0252 | -118.634 | -118.721 | -0.10986 | 4.3991 | -118.8354 | 4.3533 | -118.3182 | -118.309 | -118.0801 | -0.20142 | 0.041199 | -0.11444 | 0.73242 | 0.036621 | 0.1236 | 0.23804 | 0.32501 | -0.07782 | -0.013733 | -0.059509 | 0.43945 | 0.67749 | 0.44861 | 0.75531 | 0.52643 | 0.93384 | 123.2574 | 0.51727 | 123.1888 | 123.4131 | 123.2346 | 123.2117 | 123.1567 | -123.3719 | -123.2483 | 123.056 | 123.111 | 118.5242 | 118.6478
181.3906 | 123.3124 | -119.3802 | 3.7903 | 0.064468 | 0.0066736 | 0.070654 | 0.067195 | 0.0030953 | 0.00063011 | -0.00013235 | 0.035217 | 0.0032064 | 0.070983 | 0.15354 | 0.00060247 | 0.0097326 | -0.0024738 | -0.24719 | 3.8589 | -119.6091 | 3.6987 | -118.6432 | -119.2841 | -119.3436 | -0.14648 | 3.8315 | -119.4809 | 3.7125 | -119.014 | -119.0002 | -118.7256 | -0.22888 | 0.068665 | -0.091553 | 0.737 | 0.036621 | 0.09613 | 0.2655 | 0.32501 | -0.10071 | 0.041199 | -0.07782 | 0.36621 | 0.6546 | 0.37994 | 0.75531 | 0.48065 | 0.96588 | 123.3078 | 0.46692 | 123.1934 | 123.468 | 123.3124 | 123.2391 | 123.2117 | -123.3994 | -123.2712 | 123.0789 | 123.0927 | 119.133 | 119.2337
183.0781 | 123.349 | -119.0735 | 4.1199 | 0.011063 | 0.004751 | 0.070654 | 0.066127 | 0.0039499 | 0.00084391 | 8.125e-05 | 0.0046998 | 0.0010702 | 0.070128 | 0.16016 | 0.00017507 | 0.011442 | 0.0028668 | -0.31586 | 4.1611 | -119.3069 | 3.9185 | -118.4326 | -119.014 | -119.0689 | -0.27466 | 4.0878 | -119.1513 | 4.0146 | -118.7027 | -118.6661 | -118.4097 | -0.23346 | 0.041199 | -0.20142 | 0.64087 | 0.004577 | 0.059509 | 0.23804 | 0.29297 | -0.07782 | -0.032043 | -0.10529 | 0.37079 | 0.66376 | 0.40741 | 0.74158 | 0.48523 | 0.87433 | 123.2254 | 0.44861 | 123.1659 | 123.468 | 123.2391 | 123.2346 | 123.1613 | -123.4268 | -123.2712 | 122.9919 | 123.0881 | 118.7576 | 118.7988
184.75 | 123.2712 | -119.2154 | 4.01 | 0.056839 | 0.0068872 | 0.073644 | 0.070186 | 0.0075815 | -0.0015061 | -0.0012006 | 0.019959 | 0.0049154 | 0.069274 | 0.15226 | -3.8532e-05 | 0.0080236 | 0.00051699 | -0.15106 | 4.0833 | -119.4351 | 3.8177 | -118.5379 | -119.0964 | -118.9957 | -0.20142 | 4.0237 | -119.2978 | 3.8681 | -118.8492 | -118.8538 | -118.4463 | -0.21973 | 0.073242 | -0.19226 | 0.67749 | 0.21973 | 0.11902 | 0.43945 | 0.33875 | -0.082398 | 0.013733 | -0.14191 | 0.36621 | 0.76904 | 0.36163 | 0.85144 | 0.44403 | 0.89722 | 123.2529 | 0.44861 | 123.1659 | 123.5184 | 123.3215 | 123.2986 | 123.2391 | -123.4451 | -123.3078 | 123.0331 | 123.0835 | 119.0643 | 119.014
186.4219 | 123.2712 | -119.2657 | 3.9276 | 0.0034333 | 0.0043238 | 0.069799 | 0.064632 | 0.0028817 | -0.0042831 | 0.0022174 | 0.001648 | 0.00042939 | 0.06906 | 0.1561 | -0.0015337 | 0.011014 | 8.9786e-05 | -0.23804 | 3.9413 | -119.4672 | 3.7674 | -118.5608 | -119.1513 | -119.2429 | -0.2243 | 3.9047 | -119.3527 | 3.7949 | -118.8812 | -118.8675 | -118.602 | -0.20142 | 0.013733 | -0.16022 | 0.70496 | 0.022888 | 0.11444 | 0.2243 | 0.31586 | -0.086975 | -0.022888 | -0.13275 | 0.38452 | 0.66376 | 0.39825 | 0.75073 | 0.48523 | 0.90637 | 123.2346 | 0.4715 | 123.1476 | 123.4085 | 123.2574 | 123.2071 | 123.1705 | -123.3948 | -123.2803 | 123.0331 | 123.0606 | 119.0277 | 119.0414
188.0938 | 123.2346 | -119.2657 | 3.9459 | 0.011063 | 0.0049646 | 0.071081 | 0.064418 | 0.0028817 | -0.00086509 | 0.0013628 | 0.0046998 | 0.0036338 | 0.069701 | 0.15546 | -0.0038837 | 0.009519 | 0.0024396 | -0.19684 | 3.9917 | -119.4351 | 3.7674 | -118.5699 | -119.1467 | -119.2657 | -0.27924 | 3.9551 | -119.3207 | 3.7582 | -118.9362 | -118.8812 | -118.6478 | -0.16937 | 0.045776 | -0.17853 | 0.6958 | 0 | 0.11902 | 0.16937 | 0.28839 | -0.054932 | 0.009155 | -0.18768 | 0.32959 | 0.61798 | 0.38452 | 0.67291 | 0.43945 | 0.86517 | 123.2025 | 0.38452 | 123.0789 | 123.4268 | 123.2758 | 123.2574 | 123.2208 | -123.381 | -123.2666 | 123.0331 | 123.024 | 119.0689 | 118.9865
189.7656 | 123.2986 | -119.1513 | 4.0146 | 0.026321 | 0.0043238 | 0.070867 | 0.067409 | 0.0054453 | -0.00022429 | 8.125e-05 | 0.010803 | 0.0014976 | 0.067992 | 0.15674 | -0.0011065 | 0.0093054 | 0.0030804 | -0.28839 | 4.0833 | -119.3756 | 3.8223 | -118.5242 | -119.0872 | -119.1696 | -0.34332 | 4.0054 | -119.2383 | 3.9001 | -118.8034 | -118.7714 | -118.5013 | -0.2243 | 0.068665 | -0.19226 | 0.62714 | -0.018311 | 0.064087 | 0.20599 | 0.28839 | -0.086975 | -0.009155 | -0.11444 | 0.3479 | 0.65002 | 0.37994 | 0.737 | 0.46692 | 0.85144 | 123.1979 | 0.43488 | 123.1384 | 123.4589 | 123.2437 | 123.2346 | 123.1567 | -123.3902 | -123.2529 | 122.9736 | 123.0515 | 118.8629 | 118.808
191.4375 | 123.4039 | -122.2916 | 0.79193 | 0.011063 | 0.0043238 | 0.072363 | 0.067195 | 0.0033089 | -0.0038559 | 0.0015764 | 0.0077514 | 0.0029928 | 0.067137 | 0.10889 | 0.0040205 | 0.0097326 | -0.0022602 | -0.26093 | 0.8194 | -122.5891 | 0.62714 | -121.7102 | -122.3282 | -122.4152 | -0.26093 | 0.78735 | -122.4792 | 0.73242 | -122.0078 | -121.9849 | -121.6827 | -0.29755 | 0.027466 | -0.1648 | 0.58136 | -0.1236 | -0.036621 | 0.17395 | 0.26093 | -0.18768 | -0.004577 | -0.059509 | 0.28381 | 0.60883 | 0.3067 | 0.79651 | 0.49438 | 0.87891 | 123.2162 | 0.4715 | 123.2117 | 123.4085 | 123.2666 | 123.111 | 123.0789 | -123.381 | -123.2712 | 122.9187 | 123.024 | 122.0306 | 122.0306
193.1562 | 123.262 | -122.3099 | 0.92468 | 0.011063 | 0.004751 | 0.071295 | 0.067195 | 0.0065133 | -0.00022429 | 8.125e-05 | 0.001648 | 0.0036338 | 0.066069 | 0.099493 | 0.0010297 | 0.012083 | -0.001192 | -0.27924 | 0.94757 | -122.5433 | 0.60425 | -121.788 | -122.3557 | -122.3236 | -0.4303 | 0.91553 | -122.4106 | 0.70038 | -122.0764 | -122.0627 | -121.7285 | -0.23346 | 0.022888 | -0.32044 | 0.52185 | -0.013733 | -0.045777 | 0.21973 | 0.18768 | -0.10071 | -0.009156 | -0.22431 | 0.23346 | 0.58136 | 0.24719 | 0.68207 | 0.3479 | 0.75531 | 123.1476 | 0.33417 | 123.111 | 123.4909 | 123.3261 | 123.2574 | 123.2254 | -123.468 | -123.3353 | 122.9141 | 123.0103 | 122.0306 | 121.8796
194.9688 | 123.3994 | -122.2092 | 0.95673 | 0.011063 | 0.0032556 | 0.071508 | 0.067622 | 0.0033089 | 0.00084391 | 0.00093565 | 0.0046998 | 0.0021384 | 0.066283 | 0.10483 | 0.0023115 | 0.0099462 | 0.00073059 | -0.24261 | 0.97046 | -122.4289 | 0.79651 | -121.5591 | -122.1863 | -122.2549 | -0.25635 | 0.92926 | -122.3145 | 0.9201 | -121.843 | -121.8338 | -121.5317 | -0.21973 | 0.013733 | -0.16022 | 0.65002 | -0.045777 | 0.022888 | 0.17395 | 0.24262 | -0.10529 | -0.027466 | -0.036621 | 0.36621 | 0.67749 | 0.37537 | 0.78278 | 0.48065 | 0.86975 | 123.2254 | 0.4715 | 123.2346 | 123.3994 | 123.2437 | 123.1796 | 123.1384 | -123.3856 | -123.2712 | 123.0057 | 123.1293 | 121.9666 | 121.9528
196.7031 | 123.3765 | -122.1451 | 1.0254 | 0.011063 | 0.0045374 | 0.071935 | 0.065273 | 0.0028817 | -0.0021469 | 0.0013628 | 0.041321 | 0.0038474 | 0.072692 | 0.10718 | 0.00081607 | 0.011869 | -0.002901 | -0.21515 | 1.0483 | -122.3694 | 0.87891 | -121.4218 | -122.0627 | -122.1268 | -0.17853 | 1.0803 | -122.2778 | 0.99335 | -121.7651 | -121.7514 | -121.4539 | -0.2243 | 0.022888 | -0.14648 | 0.72327 | 0.018311 | 0.082398 | 0.24262 | 0.3067 | -0.13275 | 0.054931 | -0.032044 | 0.37994 | 0.69122 | 0.39368 | 0.82398 | 0.52643 | 0.94757 | 123.2483 | 0.5127 | 123.2712 | 123.4177 | 123.3582 | 123.1934 | 123.2254 | -123.3948 | -123.3032 | 123.024 | 123.1384 | 121.9299 | 121.9666
198.3906 | 123.2666 | -122.3328 | 0.92926 | 0.011063 | 0.0085962 | 0.071935 | 0.06805 | 0.0045907 | -0.0012925 | -0.0012006 | 0.0046998 | 0.0038474 | 0.069701 | 0.10462 | 0.00038887 | 0.011655 | 0.002226 | -0.20599 | 0.9613 | -122.5708 | 0.66834 | -121.7056 | -122.3053 | -122.3785 | -0.24719 | 0.93842 | -122.3877 | 0.74158 | -122.0169 | -122.0261 | -121.7148 | -0.23804 | 0.032044 | -0.26092 | 0.62714 | -0.045776 | 0.027466 | 0.19226 | 0.2655 | -0.054931 | 0.009156 | -0.18768 | 0.31586 | 0.61798 | 0.3067 | 0.67291 | 0.36163 | 0.86517 | 123.2391 | 0.37079 | 123.1293 | 123.5321 | 123.3261 | 123.2941 | 123.2712 | -123.5001 | -123.317 | 123.0011 | 123.0743 | 122.1268 | 122.0856
200.125 | 123.2758 | -122.2549 | 0.99335 | 0.04158 | 0.0066736 | 0.071722 | 0.065913 | 0.0062997 | -0.0025741 | 0.00029485 | 0.016907 | 0.004061 | 0.06906 | 0.10419 | -0.00067933 | 0.010587 | -0.00055121 | -0.18768 | 1.03 | -122.4884 | 0.7782 | -121.5729 | -122.1863 | -122.2824 | -0.17853 | 1.0071 | -122.3419 | 0.85144 | -121.8933 | -121.9025 | -121.5958 | -0.23346 | 0.036621 | -0.21515 | 0.68207 | -0.027466 | 0.068665 | 0.20599 | 0.30212 | -0.086975 | 0.013733 | -0.14191 | 0.36163 | 0.65918 | 0.35248 | 0.74616 | 0.43945 | 0.91553 | 123.2666 | 0.44861 | 123.1934 | 123.5184 | 123.349 | 123.2849 | 123.262 | -123.4818 | -123.3353 | 123.0331 | 123.1064 | 122.0673 | 122.0764
201.8438 | 123.381 | -122.374 | 0.82855 | 0.011063 | 0.0060328 | 0.07044 | 0.067622 | 0.0026681 | 0.00020291 | 0.0013628 | 0.0046998 | 0.0010702 | 0.068633 | 0.097357 | 0.0014569 | 0.011228 | 0.0026532 | -0.2243 | 0.8606 | -122.5845 | 0.66834 | -121.6644 | -122.3007 | -122.3923 | -0.15564 | 0.80109 | -122.4884 | 0.78278 | -121.9528 | -121.9482 | -121.6599 | -0.21057 | 0.032044 | -0.16022 | 0.70953 | -0.018311 | 0.073242 | 0.19226 | 0.28381 | -0.11444 | -0.027466 | -0.045776 | 0.42114 | 0.71411 | 0.42572 | 0.82855 | 0.54016 | 0.92011 | 123.2529 | 0.53558 | 123.2712 | 123.4451 | 123.2895 | 123.2346 | 123.175 | -123.4131 | -123.317 | 123.0423 | 123.1567 | 122.1497 | 122.2183
203.5781 | 123.2529 | -122.3602 | 0.94757 | 0.018692 | 0.0079554 | 0.068304 | 0.066127 | 0.0041635 | -0.0030015 | -0.0029096 | 0.0046998 | 0.0038474 | 0.070342 | 0.10291 | 0.00038887 | 0.0090918 | -0.0016192 | -0.23804 | 0.94299 | -122.5845 | 0.60883 | -121.7514 | -122.3511 | -122.4289 | -0.27008 | 0.92468 | -122.4335 | 0.6958 | -122.0444 | -122.0398 | -121.7102 | -0.22431 | -0.004578 | -0.33875 | 0.60883 | -0.068665 | 0.009155 | 0.15564 | 0.23346 | -0.073243 | -0.022888 | -0.25177 | 0.31586 | 0.65002 | 0.32043 | 0.72327 | 0.39368 | 0.83313 | 123.1934 | 0.3891 | 123.1293 | 123.5275 | 123.3582 | 123.3032 | 123.2849 | -123.5321 | -123.381 | 122.9691 | 123.056 | 122.1222 | 122.0901
205.25 | 123.3582 | -122.3328 | 0.86975 | 0.011063 | 0.0051782 | 0.069799 | 0.064418 | 0.0052315 | -0.0021469 | 0.00050845 | 0.0046998 | 0.0019248 | 0.067351 | 0.099706 | -0.0015337 | 0.011655 | 0.0011578 | -0.20599 | 0.89722 | -122.5525 | 0.72784 | -121.6232 | -122.2275 | -122.3282 | -0.10986 | 0.86975 | -122.4426 | 0.7782 | -121.907 | -121.8979 | -121.6599 | -0.21973 | 0.027466 | -0.14191 | 0.70953 | 0.004578 | 0.10529 | 0.2243 | 0.32501 | -0.10986 | 0 | -0.091553 | 0.42572 | 0.67291 | 0.43488 | 0.78278 | 0.54474 | 0.92926 | 123.2803 | 0.53558 | 123.2208 | 123.4497 | 123.3124 | 123.23 | 123.2025 | -123.4222 | -123.3124 | 123.0606 | 123.111 | 122.1268 | 122.2229
206.9844 | 123.2895 | -122.3831 | 0.89264 | 0.04158 | 0.0056054 | 0.071722 | 0.067622 | 0.0067269 | -0.0010789 | -0.00077335 | 0.013855 | 0.0053428 | 0.07141 | 0.097784 | 0.0012433 | 0.010374 | 8.9786e-05 | -0.18768 | 0.91553 | -122.6395 | 0.6546 | -121.6965 | -122.3099 | -122.3969 | -0.11902 | 0.87891 | -122.4701 | 0.71869 | -122.0169 | -122.0123 | -121.701 | -0.25635 | 0.022888 | -0.23804 | 0.68665 | -0.013733 | 0.073243 | 0.24261 | 0.32959 | -0.086975 | -0.013733 | -0.17395 | 0.36621 | 0.68207 | 0.37079 | 0.76904 | 0.45776 | 0.94299 | 123.2941 | 0.45319 | 123.1888 | 123.555 | 123.349 | 123.2986 | 123.262 | -123.5321 | -123.3627 | 123.0377 | 123.1018 | 122.1954 | 122.2641
208.7188 | 123.317 | -122.3053 | 0.91553 | 0.026321 | 0.0026148 | 0.07044 | 0.065486 | 0.0018137 | -1.0686e-05 | -0.00055975 | 0.013855 | 0.00064299 | 0.070769 | 0.10184 | -0.00025213 | 0.01016 | 0.0017988 | -0.27924 | 0.96588 | -122.5525 | 0.70953 | -121.637 | -122.2321 | -122.3145 | -0.19684 | 0.93384 | -122.4106 | 0.78735 | -121.9254 | -121.9299 | -121.6278 | -0.24719 | 0.050354 | -0.20599 | 0.66833 | -0.009155 | 0.073242 | 0.23804 | 0.32043 | -0.10529 | 0.018311 | -0.12817 | 0.37994 | 0.67749 | 0.37537 | 0.78278 | 0.48065 | 0.91553 | 123.262 | 0.48523 | 123.1979 | 123.5184 | 123.3444 | 123.2712 | 123.2391 | -123.468 | -123.3261 | 123.0148 | 123.0927 | 122.0261 | 122.1085
210.4531 | 123.3536 | -122.2321 | 0.97046 | 0.026321 | 0.004751 | 0.070013 | 0.065486 | 0.0030953 | -0.00065149 | 0.0013628 | 0.001648 | 0.0014976 | 0.070769 | 0.10142 | -3.8532e-05 | 0.011228 | 0.003294 | -0.27008 | 1.0117 | -122.4655 | 0.7782 | -121.5866 | -122.1725 | -122.2549 | -0.15106 | 0.9613 | -122.3282 | 0.8606 | -121.8338 | -121.8018 | -121.5408 | -0.23346 | 0.041199 | -0.19226 | 0.64545 | -0.022888 | 0.05951 | 0.21057 | 0.29297 | -0.09613 | -0.009155 | -0.10986 | 0.39826 | 0.69122 | 0.4303 | 0.78735 | 0.52643 | 0.87891 | 123.2437 | 0.49439 | 123.1888 | 123.4772 | 123.2895 | 123.2437 | 123.1934 | -123.436 | -123.2986 | 123.0103 | 123.0927 | 121.962 | 122.081
212.1094 | 123.2437 | -122.2412 | 1.03 | 0.0034333 | 0.0060328 | 0.070013 | 0.06805 | 0.0056589 | -0.0012925 | 0.00050845 | 0.0046998 | 0.0032064 | 0.072264 | 0.10676 | 0.00081607 | 0.011014 | -0.00055121 | -0.27008 | 1.0666 | -122.4838 | 0.70953 | -121.6644 | -122.2733 | -122.3236 | -0.26093 | 1.0071 | -122.3282 | 0.81024 | -121.9391 | -121.9208 | -121.5866 | -0.24261 | 0.036621 | -0.32043 | 0.57678 | -0.082397 | -0.032043 | 0.16022 | 0.21057 | -0.086975 | -0.022888 | -0.21973 | 0.30212 | 0.6546 | 0.32044 | 0.74158 | 0.40741 | 0.8194 | 123.1934 | 0.3891 | 123.1384 | 123.5504 | 123.3353 | 123.3078 | 123.2483 | -123.5138 | -123.3582 | 122.9507 | 123.0515 | 121.9711 | 121.9803
213.7812 | 123.2941 | -121.6782 | 1.5976 | 0.087356 | 0.0060328 | 0.072149 | 0.066982 | 0.0052315 | 0.00041651 | 0.0011492 | 0.02301 | 0.005129 | 0.071196 | 0.087316 | 0.00017507 | 0.0090918 | -0.0024738 | -0.1831 | 1.6342 | -121.9437 | 1.3184 | -121.0556 | -121.6003 | -121.6782 | -0.16022 | 1.6251 | -121.7972 | 1.3779 | -121.3577 | -121.3211 | -121.0144 | -0.2655 | 0.036621 | -0.27924 | 0.62256 | 0 | 0.07782 | 0.2655 | 0.34332 | -0.11902 | 0.027466 | -0.21973 | 0.32044 | 0.66376 | 0.35706 | 0.78278 | 0.47607 | 0.88806 | 123.262 | 0.43945 | 123.175 | 123.5779 | 123.4222 | 123.3124 | 123.3032 | -123.5413 | -123.3948 | 122.9965 | 123.056 | 121.4951 | 121.5179
215.4688 | 123.3994 | -121.6141 | 1.5564 | 0.011063 | 0.0026148 | 0.071295 | 0.066341 | 0.0033089 | -0.0017197 | 0.0013628 | 0.001648 | 0.00064299 | 0.069487 | 0.083257 | 0.00038887 | 0.0086646 | 0.0026532 | -0.28381 | 1.5976 | -121.907 | 1.3596 | -121.0007 | -121.582 | -121.669 | -0.14648 | 1.5427 | -121.7606 | 1.4603 | -121.2387 | -121.2341 | -120.9366 | -0.29297 | 0.041199 | -0.19684 | 0.6134 | -0.054931 | 0.032044 | 0.23804 | 0.32501 | -0.14648 | -0.013732 | -0.09613 | 0.37537 | 0.67749 | 0.37994 | 0.82398 | 0.52643 | 0.90637 | 123.2666 | 0.52185 | 123.2208 | 123.5046 | 123.3032 | 123.2117 | 123.1567 | -123.4634 | -123.317 | 122.9736 | 123.0743 | 121.3303 | 121.4676
217.1406 | 123.3948 | -120.3369 | 2.7374 | 0.033951 | 0.0041102 | 0.07279 | 0.066127 | 0.0073679 | -0.00022429 | -0.00034615 | 0.019959 | 0.0025656 | 0.069701 | 0.076421 | 0.0012433 | 0.010801 | 0.56555 | -0.21973 | 2.8107 | -120.6253 | 2.655 | -119.6823 | -120.2866 | -120.3918 | -0.27008 | 2.8015 | -120.4697 | 2.6871 | -120.0027 | -119.9478 | -35.1288 | -0.28839 | 0.073242 | -0.082398 | 0.6546 | -0.054932 | 0.050354 | 0.23346 | 0.33875 | -0.13275 | 0.064087 | -0.050354 | 0.33417 | 85.2081 | 0.3891 | 85.3409 | 0.52185 | 0.94299 | 123.2803 | 0.46692 | 123.1567 | 123.436 | 123.2712 | 123.1476 | 123.1384 | -123.3627 | -123.2071 | 122.9919 | 123.024 | 120.1172 | 120.0668
218.8125 | 123.3261 | -120.6802 | 2.4216 | 0.0034333 | 0.0066736 | 0.070226 | 0.066554 | 0.0097177 | -0.0017197 | -0.00013235 | 0.001648 | 0.00085659 | 0.069701 | 0.078344 | 0.00017507 | 0.010587 | 0.55188 | -0.28839 | 2.4673 | -120.9549 | 2.2522 | -120.0851 | -120.6894 | -120.7581 | -0.15106 | 2.4078 | -120.7397 | 2.3575 | -120.2728 | -120.2408 | -33.847 | -0.27466 | 0.045776 | -0.16937 | 0.59509 | -0.07782 | -0.009155 | 0.19684 | 0.2655 | -0.059509 | -0.013733 | -0.064087 | 0.40741 | 86.8332 | 0.43945 | 86.8927 | 0.49896 | 0.86975 | 123.2071 | 0.46692 | 123.0972 | 123.4222 | 123.1476 | 123.1476 | 123.0881 | -123.3765 | -123.1613 | 122.9324 | 123.0377 | 120.3918 | 120.5292
220.5625 | 123.1979 | -120.8771 | 2.2797 | 0.018692 | 0.00646 | 0.070226 | 0.0657 | 0.0050179 | -0.00086509 | -0.00034615 | 0.001648 | 0.002352 | 0.068419 | 0.081335 | -3.8532e-05 | 0.0086646 | 0.57474 | -0.18768 | 2.2934 | -121.1334 | 2.0279 | -120.2682 | -120.8817 | -120.9595 | 0.15106 | 2.2751 | -120.9503 | 2.1057 | -120.4834 | -120.4239 | -24.5041 | -0.25635 | 0.013733 | -0.25177 | 0.60883 | -0.082398 | -0.004578 | 0.17395 | 0.25177 | -0.073242 | -0.004578 | -0.17395 | 0.39368 | 96.373 | 0.45319 | 96.4462 | 0.52643 | 0.86517 | 123.1613 | 0.46692 | 123.056 | 123.4268 | 123.2254 | 123.1705 | 123.1522 | -123.4131 | -123.23 | 122.905 | 122.9828 | 120.6894 | 121.0281
222.2188 | 123.1796 | -120.5109 | 2.6688 | 0.011063 | 0.0043238 | 0.067877 | 0.064845 | 0.0033089 | -0.0032151 | 0.00093565 | 0.026062 | 0.0034202 | 0.070983 | 0.079626 | -0.0036701 | 0.009519 | 0.56961 | -0.24261 | 2.7054 | -120.7535 | 2.3712 | -119.9112 | -120.4697 | -120.5109 | 0.15106 | 2.7191 | -120.5978 | 2.4353 | -120.1355 | -120.163 | -24.0097 | -0.24262 | 0.036621 | -0.29755 | 0.59967 | 0 | 0.041198 | 0.24262 | 0.28381 | -0.086975 | 0.050354 | -0.23346 | 0.37537 | 96.5012 | 0.3479 | 96.5881 | 0.43487 | 0.84229 | 123.1247 | 0.46234 | 123.0331 | 123.4589 | 123.317 | 123.2162 | 123.23 | -123.4222 | -123.2666 | 122.8821 | 122.9462 | 120.2682 | 120.6619
223.9531 | 123.2803 | -120.7352 | 2.3071 | 0.018692 | 0.0028284 | 0.070867 | 0.063564 | 0.0033089 | -0.00086509 | -0.00034615 | 0.001648 | 0.00064299 | 0.070769 | 0.076421 | -0.00067933 | 0.010587 | 0.55337 | -0.23346 | 2.3438 | -120.9869 | 2.179 | -120.0577 | -120.6482 | -120.7306 | -0.09613 | 2.3163 | -120.7901 | 2.2705 | -120.282 | -120.2728 | -33.4534 | -0.25177 | 0.036621 | -0.12817 | 0.67749 | 0.004577 | 0.086975 | 0.25635 | 0.33874 | -0.054932 | 0.009155 | -0.036621 | 0.45319 | 87.2818 | 0.46234 | 87.3367 | 0.51727 | 0.92926 | 123.1659 | 0.50812 | 123.0606 | 123.3307 | 123.1064 | 123.0789 | 123.0515 | -123.2941 | -123.0972 | 122.9141 | 123.0057 | 120.5017 | 120.639
225.625 | 123.2483 | -120.7535 | 2.3529 | 0.018692 | 0.004751 | 0.070013 | 0.066768 | 0.0082223 | -0.0055649 | -0.00077335 | 0.0046998 | 0.0021384 | 0.068206 | 0.073431 | 0.0010297 | 0.008451 | 0.58371 | -0.25635 | 2.4033 | -121.0052 | 2.1057 | -120.1767 | -120.7718 | -120.8496 | -0.49896 | 2.3575 | -120.8221 | 2.1606 | -120.4514 | -120.5154 | -34.4788 | -0.25177 | 0.050354 | -0.24719 | 0.57678 | -0.09613 | -0.018311 | 0.15564 | 0.23346 | -0.068665 | 0.004578 | -0.19226 | 0.30212 | 86.2747 | 0.23804 | 86.3434 | 0.3067 | 0.82855 | 123.111 | 0.37079 | 122.9828 | 123.4085 | 123.1796 | 123.1567 | 123.111 | -123.3582 | -123.175 | 122.8592 | 122.9141 | 120.4971 | 120.2545
227.3594 | 123.1659 | -120.5429 | 2.5726 | 0.018692 | 0.0056054 | 0.073217 | 0.068263 | 0.0065133 | -0.0010789 | -0.00077335 | 0.0077514 | 0.0044882 | 0.068206 | 0.078558 | 0.0014569 | 0.010374 | 0.60187 | -0.21515 | 2.5635 | -120.7901 | 2.3712 | -119.8883 | -120.5154 | -120.5795 | 0 | 2.5497 | -120.5795 | 2.4216 | -120.1126 | -120.1035 | -21.2677 | -0.24719 | -0.009155 | -0.20142 | 0.6546 | -0.036621 | 0.027466 | 0.21057 | 0.27466 | -0.036621 | -0.022888 | -0.15106 | 0.4303 | 99.2752 | 0.43945 | 99.3118 | 0.47607 | 0.90179 | 123.1613 | 0.46692 | 123.0011 | 123.3536 | 123.1293 | 123.1064 | 123.0927 | -123.3627 | -123.1522 | 122.9141 | 122.9645 | 120.3278 | 120.5429
229.0781 | 123.1018 | -120.9 | 2.2385 | 0.0034333 | 0.0041102 | 0.070013 | 0.065273 | 0.0065133 | -0.0040695 | -0.0029096 | 0.0046998 | 0.00064299 | 0.07141 | 0.068731 | -0.0023883 | 0.0090918 | 0.55551 | -0.27466 | 2.2522 | -121.0831 | 1.9455 | -120.2866 | -120.8542 | -120.932 | 0.22888 | 2.243 | -120.8862 | 2.0004 | -120.4926 | -120.5063 | -23.7122 | -0.18311 | 0.013733 | -0.29297 | 0.6134 | -0.032044 | 0.045776 | 0.15106 | 0.22888 | 0.013733 | 0.004578 | -0.23804 | 0.40741 | 97.1878 | 0.39368 | 97.1741 | 0.37994 | 0.79651 | 123.0286 | 0.39368 | 122.8867 | 123.3353 | 123.1293 | 123.1522 | 123.143 | -123.3215 | -123.1247 | 122.8455 | 122.9004 | 120.6253 | 121.1288
230.75 | 123.1476 | -119.2978 | 3.598 | 0.026321 | 0.00069217 | 0.073004 | 0.064632 | 0.0067269 | -0.0030015 | -0.00098695 | 0.010803 | 0.0014976 | 0.018645 | 0.043524 | 0.0014569 | 0.0097326 | 0.001585 | -0.31128 | 3.6301 | -119.545 | 3.4103 | -118.6661 | -119.1788 | -119.1605 | 0.041199 | 3.6163 | -0.1236 | 3.4973 | 0.10529 | 0.041199 | 0.1831 | -0.24719 | 0.032044 | -0.18768 | 0.63171 | 0.13733 | 0.11902 | 0.38452 | 0.36621 | 119.1742 | 0.018311 | -0.10071 | 119.4031 | 119.4809 | 119.339 | 0.3067 | 0.16479 | 0.87891 | 122.9553 | 0.22888 | 3.6209 | 123.175 | 3.7399 | 122.9279 | 122.9141 | -123.143 | -3.7216 | 122.7081 | 122.7951 | 118.9865 | 119.339
232.4844 | 123.3032 | -118.515 | 4.4998 | 0.018692 | 0.0041102 | 0.073004 | 0.06805 | 0.010145 | -0.0040695 | -0.00034615 | 0.0077514 | 0.0027792 | 0.019713 | 0.046514 | 0.0035931 | 0.011869 | 0.0026532 | -0.17853 | 4.5364 | -118.7485 | 4.422 | -117.7048 | -118.2129 | -118.1808 | 0.091553 | 4.5136 | -0.09613 | 4.5044 | 0.15564 | 0.10071 | 0.22888 | -0.23346 | 0.036621 | -0.07782 | 0.81024 | 0.33417 | 0.30212 | 0.56763 | 0.53558 | 118.4189 | 0.013733 | 0.004578 | 118.6707 | 118.7439 | 118.6157 | 0.32501 | 0.19684 | 1.0437 | 123.1705 | 0.25177 | 4.6005 | 123.2849 | 4.6097 | 123.0515 | 123.0286 | -123.2483 | -4.5959 | 122.937 | 123.0194 | 118.3365 | 118.6066
234.2188 | 123.2025 | -118.1992 | 4.9164 | 0.018692 | 0.0053918 | 0.072149 | 0.069759 | -0.010149 | -0.0032151 | -0.0065412 | 0.0046998 | -0.014524 | 0.017363 | 0.028356 | -0.0043109 | 0.0054602 | -0.0018328 | -0.17853 | 4.9713 | -118.428 | 4.747 | -117.1005 | -118.2587 | -109.0668 | 0.082397 | 4.9255 | -0.059509 | 4.7928 | 0.068665 | -0.20599 | -0.21515 | -0.22888 | 0.054931 | -0.16937 | 1.0986 | 9.1324 | -0.059509 | 9.3613 | 0.16937 | 118.1396 | 0.009155 | -0.1236 | 118.2678 | 117.984 | 117.9932 | -0.15564 | -0.14649 | 1.3275 | 123.175 | 0.12817 | 4.8523 | 123.3994 | 4.985 | 123.1705 | 123.1247 | -123.3444 | -4.9759 | 122.9462 | 122.9919 | 118.0206 | 118.2816
235.9531 | 123.2025 | -118.2724 | 4.9026 | 0.018692 | 0.0036828 | 0.070013 | 0.065913 | 0.0043771 | -0.0049241 | 0.0017902 | 0.010803 | 0.00085659 | 0.019927 | 0.04096 | -0.0026019 | 0.0088782 | 0.0043622 | -0.23346 | 4.9164 | -118.483 | 4.6692 | -117.6498 | -118.0573 | -117.9749 | -0.004578 | 4.9026 | -0.16022 | 4.7104 | 0.059509 | -0.027466 | 0.091553 | -0.21057 | 0.013733 | -0.23346 | 0.62256 | 0.29755 | 0.21515 | 0.50812 | 0.42572 | 118.1122 | 0 | -0.19226 | 118.3319 | 118.364 | 118.2449 | 0.25177 | 0.13275 | 0.83313 | 123.1522 | 0.21973 | 4.8706 | 123.3994 | 5.0629 | 123.1888 | 123.175 | -123.3856 | -5.0629 | 122.9416 | 122.9828 | 118.0389 | 118.2678
237.6875 | 123.2758 | -118.5745 | 4.5547 | 0.018692 | 0.0015466 | 0.071081 | 0.064845 | 0.0028817 | -0.0027877 | 0.00050845 | 0.0046998 | -0.00042521 | 0.01715 | 0.042669 | -0.0015337 | 0.0093054 | 0.001585 | -0.19684 | 4.5822 | -118.7576 | 4.4449 | -117.8558 | -118.4509 | -118.4052 | 0.091553 | 4.5547 | -0.11902 | 4.454 | 0.15106 | 0.073242 | 0.1831 | -0.1831 | 0.027465 | -0.10986 | 0.71869 | 0.16937 | 0.1236 | 0.35248 | 0.3067 | 118.4555 | 0 | -0.10071 | 118.7256 | 118.7576 | 118.6478 | 0.30212 | 0.19226 | 0.90179 | 123.2025 | 0.27008 | 4.5731 | 123.3398 | 4.6738 | 123.1567 | 123.1293 | -123.3124 | -4.6738 | 123.0194 | 123.0286 | 118.3777 | 118.6661
239.3594 | 123.2346 | -118.1763 | 5.0079 | 0.033951 | 0.0056054 | 0.072576 | 0.06805 | 0.0045907 | -0.0021469 | 8.125e-05 | 0.0077514 | -0.001066 | 0.0195 | 0.040106 | -0.0073017 | 0.0069556 | 0.0028668 | -0.14191 | 5.0354 | -118.4006 | 4.8065 | -117.3889 | -117.7826 | -117.8055 | 0.073242 | 4.9988 | -0.13733 | 4.8935 | 0.10529 | 0.009155 | 0.004578 | -0.2243 | 0.027465 | -0.20142 | 0.78735 | 0.37079 | 0.39368 | 0.59509 | 0.61798 | 118.0389 | -0.009156 | -0.11444 | 118.2816 | 118.1808 | 118.1854 | 0.14191 | 0.14648 | 1.0117 | 123.2071 | 0.24262 | 5.0308 | 123.436 | 5.1361 | 123.2117 | 123.175 | -123.4085 | -5.1453 | 122.9828 | 123.0698 | 118.0344 | 118.2495
241.0938 | 123.2437 | -115.1825 | 7.9742 | 0.011063 | 0.0049646 | 0.068945 | 0.066768 | 0.0071541 | -0.0030015 | 0.0013628 | 0.0046998 | 0.0019248 | 0.016936 | 0.041387 | 0.0023115 | 0.011869 | 0.0020124 | -0.27466 | 8.0017 | -115.3839 | 7.7545 | -114.6103 | -115.1733 | -115.004 | -0.022888 | 7.9788 | -0.14648 | 7.9147 | 0.10071 | -0.009155 | 0.15564 | -0.20142 | 0.027466 | -0.21973 | 0.5722 | 0.17853 | 0.009155 | 0.37994 | 0.21057 | 115.036 | 0.004578 | -0.059509 | 115.2832 | 115.3381 | 115.1733 | 0.30212 | 0.13733 | 0.77362 | 123.1384 | 0.24719 | 8.0612 | 123.3856 | 8.1253 | 123.1842 | 123.1613 | -123.3582 | -8.1207 | 122.937 | 123.0972 | 114.9078 | 115.1596
242.8438 | 123.2895 | -115.8142 | 7.2968 | 0.04158 | 0.004751 | 0.072363 | 0.063777 | 0.0050179 | -0.0023605 | 0.00029485 | 0.010803 | 0.00042939 | 0.020995 | 0.040533 | 0.0027387 | 0.011442 | 0.0020124 | -0.27008 | 7.3151 | -116.0614 | 7.164 | -115.1962 | -115.8005 | -115.8691 | 0 | 7.2739 | -0.11444 | 7.2189 | 0.1236 | 0.032043 | 0.16479 | -0.24719 | 0.01831 | -0.13275 | 0.61798 | -0.054932 | 0.013733 | 0.19226 | 0.26093 | 115.6998 | -0.022888 | -0.07782 | 115.9378 | 115.979 | 115.8463 | 0.27924 | 0.14648 | 0.86517 | 123.2254 | 0.23804 | 7.3334 | 123.3765 | 7.3883 | 123.1293 | 123.0881 | -123.3582 | -7.4112 | 122.9782 | 123.0331 | 115.5441 | 115.8142
244.5312 | 123.0469 | -94.7067 | 28.3997 | 0.018692 | 0.0053918 | 0.070013 | 0.063136 | 0.0058725 | -0.0015061 | -0.00013235 | 0.001648 | -0.00063881 | 0.019927 | 0.034765 | -0.00025213 | 0.011442 | -0.00097841 | -0.091553 | 28.4363 | -94.9173 | 28.3813 | -94.1345 | -94.6472 | -94.6884 | 0.13733 | 28.3585 | -0.09613 | 28.4729 | 0.23804 | 0.15564 | 0.19684 | -0.21057 | 0.036621 | -0.01831 | 0.5722 | 0.01831 | 0.059509 | 0.22888 | 0.27008 | 94.6106 | -0.041199 | 0.073242 | 94.9448 | 94.9036 | 94.8624 | 0.29297 | 0.25177 | 0.78278 | 123.2986 | 0.33417 | 28.569 | 123.3536 | 28.4546 | 123.143 | 123.0652 | -123.317 | -28.4958 | 123.0881 | 123.1796 | 94.6152 | 94.8441
246.2656 | 123.0331 | -94.6426 | 28.4454 | 0.011063 | 0.0073144 | 0.070867 | 0.066127 | 0.0054453 | -0.0017197 | -0.00055975 | 0.0046998 | 0.0025656 | 0.019072 | 0.026861 | 0.0027387 | 0.011442 | -0.0033282 | -0.17395 | 28.5141 | -94.8578 | 28.3813 | -94.1895 | -94.6976 | -94.7296 | 0.064087 | 28.4042 | -0.10071 | 28.5233 | 0.19684 | 0.11444 | 0.19684 | -0.21515 | 0.068664 | -0.064087 | 0.45319 | -0.086975 | -0.054932 | 0.12817 | 0.16022 | 94.5419 | -0.041199 | 0.077819 | 94.8395 | 94.8395 | 94.7571 | 0.29755 | 0.21515 | 0.66833 | 123.2391 | 0.29755 | 28.624 | 123.3719 | 28.5049 | 123.1567 | 123.0469 | -123.3032 | -28.5461 | 123.024 | 123.1659 | 94.4687 | 94.7067
248.0156 | 123.2986 | -94.5786 | 28.4821 | 0.04158 | 0.00646 | 0.073431 | 0.066982 | 0.0026681 | 0.00063011 | -0.00034615 | 0.0077514 | 0.0034202 | 0.018645 | 0.03861 | 0.00081607 | 0.012083 | -0.00097841 | -0.027466 | 28.4958 | -94.8349 | 28.3493 | -94.0933 | -94.5877 | -94.6198 | 0.17395 | 28.418 | -0.091553 | 28.5599 | 0.21057 | 0.086975 | 0.18768 | -0.25635 | 0.013733 | -0.13275 | 0.48523 | -0.041199 | -0.009156 | 0.21515 | 0.24719 | 94.487 | -0.064087 | 0.077819 | 94.7891 | 94.7662 | 94.6655 | 0.27924 | 0.17853 | 0.74158 | 123.1842 | 0.30212 | 28.6514 | 123.3307 | 28.5095 | 123.0743 | 122.9965 | -123.317 | -28.5736 | 122.9279 | 123.1384 | 94.5511 | 94.7525
249.6875 | 123.2986 | -94.4962 | 28.5828 | 0.011063 | 0.0034692 | 0.07044 | 0.065486 | 0.0041635 | -0.0023605 | 0.00029485 | 0.0046998 | -0.001066 | 0.020995 | 0.036901 | 0.00038887 | 0.0099462 | 0.0017988 | -0.19226 | 28.6285 | -94.7388 | 28.5233 | -94.043 | -94.5419 | -94.574 | 0.027466 | 28.5645 | -0.10986 | 28.6331 | 0.18768 | 0.11444 | 0.16937 | -0.24262 | 0.045776 | -0.05951 | 0.45319 | -0.07782 | -0.045776 | 0.16479 | 0.19684 | 94.3863 | -0.018311 | 0.050354 | 94.6838 | 94.6655 | 94.6106 | 0.27924 | 0.2243 | 0.6958 | 123.262 | 0.29755 | 28.743 | 123.3673 | 28.6743 | 123.1247 | 123.0606 | -123.3215 | -28.6926 | 123.0194 | 123.1293 | 94.3039 | 94.5236
251.4219 | 123.3215 | -117.0364 | 6.0471 | 0.0034333 | 0.0051782 | 0.070013 | 0.065486 | 0.0033089 | -0.0036423 | 0.0011492 | 0.0046998 | 0.00042939 | 0.017791 | 0.039678 | -0.0030291 | 0.010374 | 0.0017988 | -0.20599 | 6.0562 | -117.3248 | 5.9143 | -116.4459 | -117.0135 | -117.1005 | 0.050354 | 6.0333 | -0.10986 | 5.9418 | 0.13275 | 0.050354 | 0.16479 | -0.28839 | 0.009155 | -0.13275 | 0.59052 | -0.064087 | 0.022888 | 0.2243 | 0.31128 | 116.9266 | -0.013733 | -0.10529 | 117.1692 | 117.2012 | 117.0868 | 0.27466 | 0.16022 | 0.87891 | 123.2391 | 0.24261 | 6.0516 | 123.381 | 6.1432 | 123.0927 | 123.0698 | -123.3719 | -6.1569 | 122.9507 | 122.9782 | 116.8304 | 117.0868
253.1719 | 123.2391 | -117.3935 | 5.7999 | 0.011063 | 0.0053918 | 0.071722 | 0.066982 | 0.0035227 | -0.0042831 | -0.0016278 | 0.001648 | 0.0012838 | 0.019286 | 0.040106 | -0.0028155 | 0.0086646 | 0.0013714 | -0.21973 | 5.7999 | -117.6453 | 5.5893 | -116.7938 | -117.3386 | -117.4301 | -0.009155 | 5.7953 | -0.12817 | 5.6259 | 0.059509 | -0.018311 | 0.10529 | -0.25177 | 0 | -0.21057 | 0.59967 | -0.036621 | 0.054932 | 0.21515 | 0.3067 | 117.2653 | -0.004578 | -0.17395 | 117.453 | 117.4988 | 117.3752 | 0.23346 | 0.10986 | 0.85144 | 123.2346 | 0.18768 | 5.7541 | 123.4451 | 5.9235 | 123.1934 | 123.1888 | -123.4451 | -5.928 | 122.9828 | 123.0194 | 117.1738 | 117.3843
254.9062 | 123.23 | -117.3065 | 5.8685 | 0.018692 | 0.0068872 | 0.071081 | 0.068904 | 0.00010474 | -0.00022429 | -0.00098695 | 0.0077514 | 0.0017112 | 0.020354 | 0.038183 | 0.00017507 | 0.0099462 | -0.00033761 | -0.22888 | 5.9006 | -117.54 | 5.6396 | -116.748 | -117.3294 | -117.4072 | -0.041199 | 5.8685 | -0.11902 | 5.6808 | 0.036621 | -0.059509 | 0.09613 | -0.23346 | 0.032044 | -0.22888 | 0.55847 | -0.10071 | -0.022888 | 0.13275 | 0.21057 | 117.1875 | 0 | -0.18768 | 117.3431 | 117.4026 | 117.247 | 0.21515 | 0.05951 | 0.79193 | 123.1796 | 0.15564 | 5.7999 | 123.4406 | 5.9875 | 123.2071 | 123.175 | -123.4085 | -5.9875 | 122.9462 | 122.9874 | 117.0776 | 117.2653
256.6094 | 123.2391 | -117.0914 | 6.102 | 0.011063 | 0.008169 | 0.072149 | 0.068477 | 0.0067269 | -0.00086509 | -0.0014142 | 0.010803 | 0.0027792 | 0.024199 | 0.046514 | 0.00038887 | 0.01016 | 0.0026532 | -0.1831 | 6.1386 | -117.3386 | 5.896 | -116.4917 | -117.0868 | -117.1417 | -0.004578 | 6.1111 | -0.13733 | 5.9418 | 0.041199 | -0.045776 | 0.10986 | -0.24719 | 0.036621 | -0.20599 | 0.59967 | -0.050354 | 0.004578 | 0.19684 | 0.25177 | 116.954 | 0.009155 | -0.16022 | 117.1326 | 117.2012 | 117.0456 | 0.24719 | 0.091553 | 0.84686 | 123.2346 | 0.17853 | 6.0791 | 123.4772 | 6.2485 | 123.23 | 123.2025 | -123.4406 | -6.2393 | 122.9874 | 123.0331 | 116.9083 | 117.0868
258.2812 | 123.2483 | -117.1005 | 6.1295 | 0.026321 | 0.004751 | 0.069158 | 0.064632 | 0.00095914 | -0.0017197 | -0.0022688 | 0.010803 | 0.0014976 | 0.020995 | 0.037115 | -0.00025213 | 0.011228 | -0.0014056 | -0.2243 | 6.1798 | -117.3477 | 5.8685 | -116.51 | -117.0639 | -117.1371 | -0.045776 | 6.134 | -0.16479 | 5.9372 | 0.059509 | -0.013733 | 0.11902 | -0.24719 | 0.050354 | -0.26093 | 0.59052 | -0.036621 | 0.036621 | 0.21057 | 0.28381 | 116.9357 | 0.004577 | -0.19226 | 117.16 | 117.2195 | 117.0868 | 0.28381 | 0.15106 | 0.83771 | 123.2162 | 0.2243 | 6.102 | 123.5275 | 6.2988 | 123.2803 | 123.2346 | -123.4772 | -6.2943 | 122.9691 | 123.0377 | 116.8762 | 117.0547
260.0312 | 123.3444 | -117.0959 | 6.0516 | 0.011063 | 0.004751 | 0.070226 | 0.066982 | 0.0045907 | -0.0023605 | 0.0020038 | 0.010803 | 0.002352 | 0.0195 | 0.041174 | 0.0025251 | 0.011014 | -0.0016192 | -0.27008 | 6.0974 | -117.3615 | 5.8685 | -116.5054 | -117.0822 | -117.1509 | 0.004578 | 6.0333 | -0.10986 | 6.015 | 0.15564 | 0.07782 | 0.21515 | -0.2655 | 0.045776 | -0.18311 | 0.59051 | -0.054932 | 0.013733 | 0.21057 | 0.27924 | 116.9861 | -0.018311 | -0.036621 | 117.2516 | 117.3111 | 117.1738 | 0.32501 | 0.18768 | 0.85602 | 123.23 | 0.2655 | 6.1249 | 123.4589 | 6.1432 | 123.1934 | 123.1293 | -123.4131 | -6.1615 | 122.9645 | 123.111 | 116.8259 | 117.1005
261.7344 | 123.3032 | -116.1713 | 6.9901 | 0.018692 | 0.0041102 | 0.073004 | 0.065273 | 0.0037363 | -0.0023605 | -0.00077335 | 0.0077514 | 0.0014976 | 0.020354 | 0.043524 | -0.0017475 | 0.012296 | 0.00094419 | -0.24719 | 6.9992 | -116.4276 | 6.8756 | -115.5121 | -116.1301 | -116.1987 | 0.054932 | 6.9443 | -0.11902 | 6.9214 | 0.12817 | 0.045776 | 0.1831 | -0.25635 | 0.009156 | -0.11444 | 0.65918 | -0.027465 | 0.041199 | 0.22888 | 0.29755 | 116.0522 | -0.045776 | -0.068664 | 116.2994 | 116.3544 | 116.217 | 0.30212 | 0.16479 | 0.91553 | 123.3032 | 0.24719 | 7.0404 | 123.4268 | 7.0633 | 123.1705 | 123.1155 | -123.4177 | -7.1091 | 123.0469 | 123.0927 | 115.9241 | 116.2262
263.4062 | 123.2529 | -116.8716 | 6.2942 | 0.018692 | 0.0051782 | 0.070226 | 0.0657 | 0.0056589 | -0.0036423 | 8.125e-05 | 0.0077514 | 0.0034202 | 0.020354 | 0.038824 | 0.0014569 | 0.010587 | 0.001585 | -0.15564 | 6.3538 | -117.1051 | 6.134 | -116.2308 | -116.8213 | -116.9128 | 0.032043 | 6.308 | -0.11902 | 6.2073 | 0.09613 | 0.009155 | 0.15106 | -0.23346 | 0.05951 | -0.16022 | 0.64087 | -0.041199 | 0.050354 | 0.19226 | 0.28381 | 116.7526 | 0.013733 | -0.086975 | 116.9678 | 117.0227 | 116.8808 | 0.27008 | 0.12817 | 0.87433 | 123.2391 | 0.21515 | 6.3263 | 123.4589 | 6.427 | 123.2254 | 123.1796 | -123.3994 | -6.4133 | 123.0057 | 123.0789 | 116.716 | 116.9037
265.125 | 123.3582 | -116.1987 | 6.9397 | 0.018692 | 0.0038966 | 0.070867 | 0.065059 | 0.00095914 | -0.0025741 | 0.00414 | 0.001648 | -0.00042521 | 0.017577 | 0.048437 | 0.00081607 | 0.011655 | -0.00033761 | -0.19684 | 6.958 | -116.4459 | 6.8893 | -115.4846 | -116.0751 | -116.1575 | 0.10529 | 6.9351 | -0.09613 | 6.926 | 0.20599 | 0.12817 | 0.20142 | -0.24719 | 0.018311 | -0.050354 | 0.71411 | 0.041198 | 0.1236 | 0.28839 | 0.37079 | 116.1026 | -0.004577 | -0.013733 | 116.4047 | 116.4001 | 116.3269 | 0.29755 | 0.2243 | 0.9613 | 123.3353 | 0.30212 | 7.0221 | 123.4039 | 7.0312 | 123.1567 | 123.1338 | -123.3856 | -7.0358 | 123.0881 | 123.1247 | 116.0019 | 116.304
266.8594 | 123.2529 | -116.098 | 7.1091 | 0.026321 | 0.0036828 | 0.068731 | 0.066982 | 0.0028817 | -0.0030015 | 0.0013628 | 0.010803 | 0.0038474 | 0.018859 | 0.046941 | -0.00089293 | 0.0082374 | 0.00094419 | -0.20142 | 7.1594 | -116.3498 | 6.9031 | -115.5212 | -116.0614 | -116.1392 | -0.068665 | 7.1228 | -0.13733 | 6.9443 | 0.09613 | 0 | 0.13275 | -0.25177 | 0.050354 | -0.20599 | 0.57678 | -0.041199 | 0.036621 | 0.21057 | 0.28839 | 115.9607 | 0.013733 | -0.16479 | 116.1942 | 116.2308 | 116.098 | 0.27008 | 0.13733 | 0.82855 | 123.2529 | 0.23346 | 7.0816 | 123.5092 | 7.2601 | 123.2574 | 123.2208 | -123.4589 | -7.2464 | 123.0011 | 123.0423 | 115.8966 | 116.0294
268.5469 | 123.2529 | -117.4438 | 5.7541 | 0.018692 | 0.0056054 | 0.070654 | 0.067622 | 0.0039499 | -0.0042831 | 0.00029485 | 0.0046998 | 0.002352 | 0.020995 | 0.037328 | 0.0038067 | 0.011228 | 0.00030339 | -0.19684 | 5.7816 | -117.6636 | 5.5527 | -116.803 | -117.3981 | -117.4942 | -0.009155 | 5.7632 | -0.11902 | 5.6259 | 0.082397 | -0.004578 | 0.12817 | -0.21973 | 0.027466 | -0.20142 | 0.64087 | -0.050354 | 0.045777 | 0.16937 | 0.2655 | 117.3248 | 0.009156 | -0.12817 | 117.5262 | 117.572 | 117.4393 | 0.24719 | 0.11444 | 0.8606 | 123.2162 | 0.20142 | 5.7449 | 123.4451 | 5.8823 | 123.2254 | 123.2071 | -123.4177 | -5.8731 | 122.9965 | 123.0698 | 117.247 | 117.4347
270.2344 | 123.2803 | -117.2928 | 5.8456 | 0.033951 | 0.0045374 | 0.073644 | 0.066127 | 0.0028817 | 0.0012711 | 0.0020038 | 0.013855 | 0.00085659 | 0.022277 | 0.039892 | 0.0014569 | 0.011655 | 0.0035078 | -0.24261 | 5.8823 | -117.5125 | 5.7587 | -116.6107 | -117.2333 | -117.2882 | 0.082397 | 5.8319 | -0.11444 | 5.7816 | 0.14191 | 0.073242 | 0.16937 | -0.21973 | 0.036621 | -0.086975 | 0.68207 | 0.004578 | 0.05951 | 0.2243 | 0.27924 | 117.1783 | -0.013733 | -0.064087 | 117.4347 | 117.4622 | 117.366 | 0.28381 | 0.18768 | 0.90179 | 123.2712 | 0.25635 | 5.896 | 123.3948 | 5.9463 | 123.175 | 123.1247 | -123.3582 | -5.9601 | 123.0515 | 123.0743 | 117.0502 | 117.3752
272.0156 | 123.3124 | -117.2928 | 5.8868 | 0.0034333 | 0.0032556 | 0.071081 | 0.063991 | 0.00095914 | -0.0034287 | 0.00050845 | -0.0014038 | -0.001066 | 0.018859 | 0.050146 | 0.0014569 | 0.010374 | 0.001585 | -0.29297 | 5.9052 | -117.5262 | 5.7312 | -116.6565 | -117.2241 | -117.2882 | 0.009155 | 5.864 | -0.10529 | 5.809 | 0.16479 | 0.082397 | 0.18768 | -0.23346 | 0.01831 | -0.15564 | 0.63629 | 0.004578 | 0.068665 | 0.23804 | 0.30212 | 117.1875 | -0.022888 | -0.07782 | 117.4576 | 117.4805 | 117.3752 | 0.29297 | 0.18768 | 0.86975 | 123.2574 | 0.27008 | 5.9143 | 123.4314 | 5.9692 | 123.1979 | 123.1567 | -123.4131 | -5.9921 | 123.024 | 123.1018 | 116.9998 | 117.3019
273.7188 | 123.2071 | -116.4322 | 6.7657 | 0.011063 | 0.0036828 | 0.07044 | 0.068477 | 0.0060861 | -0.0021469 | -0.0012006 | 0.0046998 | 0.0027792 | 0.020781 | 0.042669 | 0.00017507 | 0.0088782 | -0.00055121 | -0.21057 | 6.8024 | -116.6565 | 6.5094 | -115.9378 | -116.4871 | -116.5237 | -0.09613 | 6.7841 | -0.15106 | 6.6055 | 0.027466 | -0.045776 | 0.10529 | -0.2243 | 0.036621 | -0.25635 | 0.49439 | -0.091553 | -0.054932 | 0.13275 | 0.16937 | 116.2811 | 0.018311 | -0.16022 | 116.4597 | 116.5375 | 116.3864 | 0.25635 | 0.10529 | 0.71869 | 123.1659 | 0.17853 | 6.7566 | 123.4589 | 6.9351 | 123.2346 | 123.2162 | -123.4222 | -6.9168 | 122.9416 | 123.0377 | 116.2216 | 116.3361
275.4062 | 123.2895 | -116.6382 | 6.5369 | 0.0034333 | 0.0028284 | 0.068731 | 0.06805 | 0.0075815 | -0.0027877 | 0.0017902 | 0.0046998 | 0.0019248 | 0.019286 | 0.040746 | 0.0010297 | 0.012083 | -0.00055121 | -0.27008 | 6.5643 | -116.8945 | 6.3126 | -116.0797 | -116.684 | -116.7297 | -0.022888 | 6.5414 | -0.11902 | 6.4545 | 0.10986 | 0.022888 | 0.15106 | -0.25635 | 0.027466 | -0.2243 | 0.55847 | -0.091552 | -0.045776 | 0.16479 | 0.21057 | 116.5192 | 0.004578 | -0.082397 | 116.748 | 116.7892 | 116.6611 | 0.27008 | 0.14191 | 0.81482 | 123.2071 | 0.22888 | 6.5735 | 123.4589 | 6.6605 | 123.2025 | 123.1796 | -123.4314 | -6.6559 | 122.9507 | 123.0927 | 116.3681 | 116.6153
277.0781 | 123.3353 | -116.2857 | 6.8527 | 0.011063 | 0.0045374 | 0.069586 | 0.066768 | 0.0069405 | 0.00020291 | -0.00013235 | 0.001648 | 0.00064299 | 0.018859 | 0.040106 | 0.0029523 | 0.011655 | 0.00030339 | -0.20599 | 6.8527 | -116.5421 | 6.7474 | -115.6494 | -116.2628 | -116.3223 | 0.086975 | 6.8161 | -0.12817 | 6.839 | 0.17395 | 0.086975 | 0.21057 | -0.25635 | 0 | -0.10529 | 0.63629 | -0.036621 | 0.022889 | 0.21973 | 0.27924 | 116.1575 | -0.036621 | -0.013733 | 116.4597 | 116.4963 | 116.3727 | 0.33875 | 0.21515 | 0.89264 | 123.2895 | 0.30212 | 6.9672 | 123.3948 | 6.9443 | 123.1384 | 123.1018 | -123.3948 | -6.9809 | 123.0331 | 123.1247 | 116.0797 | 116.3727
278.7656 | 123.0057 | -94.5969 | 28.5278 | 0.018692 | 0.0062464 | 0.069158 | 0.065273 | 0.0028817 | -0.0030015 | -0.00013235 | 0.0046998 | 0.0025656 | 0.018218 | 0.033697 | 0.0016705 | 0.011442 | -0.00076481 | -0.086975 | 28.5736 | -94.8303 | 28.4775 | -94.0842 | -94.6152 | -94.6564 | 0.050354 | 28.4912 | -0.064087 | 28.624 | 0.21515 | 0.1236 | 0.19226 | -0.23346 | 0.045776 | -0.050354 | 0.5127 | -0.059509 | -0.01831 | 0.17395 | 0.21515 | 94.5328 | -0.036621 | 0.09613 | 94.812 | 94.7891 | 94.7205 | 0.25635 | 0.18768 | 0.74616 | 123.3078 | 0.27924 | 28.688 | 123.4039 | 28.5553 | 123.1705 | 123.0881 | -123.3582 | -28.5919 | 123.0743 | 123.2208 | 94.5099 | 94.6472
280.4375 | 123.2941 | -94.6198 | 28.537 | 0.018692 | 0.0053918 | 0.069799 | 0.064632 | 0.0045907 | 0.00063011 | -0.00077335 | 0.001648 | 0.00085659 | 0.019286 | 0.030493 | -0.0011065 | 0.011228 | 0.00051699 | -0.18768 | 28.5645 | -94.8212 | 28.4592 | -94.1116 | -94.6289 | -94.6564 | -0.018311 | 28.4912 | -0.086975 | 28.5553 | 0.19684 | 0.11902 | 0.16022 | -0.20142 | 0.027466 | -0.07782 | 0.50812 | -0.036621 | -0.009155 | 0.16479 | 0.19226 | 94.5328 | -0.045776 | 0.018311 | 94.8166 | 94.78 | 94.7388 | 0.24719 | 0.20599 | 0.70953 | 123.2803 | 0.28381 | 28.6423 | 123.3856 | 28.5782 | 123.1842 | 123.111 | -123.3582 | -28.624 | 123.0789 | 123.175 | 94.4321 | 94.6014
282.1406 | 123.2803 | -94.5694 | 28.5233 | 0.011063 | 0.0056054 | 0.070013 | 0.062496 | 0.0028817 | -0.00065149 | 0.00050845 | 0.0046998 | 0.002352 | 0.018859 | 0.027288 | -0.0011065 | 0.010374 | 0.00073059 | -0.15564 | 28.5553 | -94.7983 | 28.4683 | -94.1071 | -94.6243 | -94.6655 | -0.009155 | 28.5095 | -0.10529 | 28.537 | 0.1831 | 0.11444 | 0.16479 | -0.22888 | 0.032044 | -0.054931 | 0.46234 | -0.09613 | -0.054932 | 0.13275 | 0.17395 | 94.4641 | -0.013733 | 0.013733 | 94.7525 | 94.7342 | 94.6838 | 0.27008 | 0.21973 | 0.69122 | 123.2666 | 0.28839 | 28.6423 | 123.3536 | 28.6148 | 123.1247 | 123.0789 | -123.3215 | -28.6285 | 123.0377 | 123.1064 | 94.4138 | 94.5602
283.8125 | 123.1934 | -95.6131 | 27.5894 | 0.011063 | 0.0017602 | 0.067236 | 0.066982 | 0.0037363 | -0.0027877 | -0.00077335 | 0.001648 | 0.004061 | 0.022704 | 0.027288 | -0.0038837 | 0.0080236 | -0.00033761 | 0.2655 | 28.2806 | -95.1782 | 27.2369 | -95.3705 | -95.9015 | -96.0571 | -0.10071 | 27.3651 | -0.1236 | 27.3605 | 0.091553 | 0.009155 | 0.086975 | 0.43487 | 0.69122 | -0.35248 | 0.24262 | -0.44403 | -0.28839 | -0.87891 | -0.72327 | 95.4895 | -0.22431 | -0.22888 | 95.7047 | 95.7001 | 95.6223 | 0.21057 | 0.13275 | -0.19226 | 122.4152 | 0.21515 | 27.4841 | 123.4589 | 27.4887 | 123.8937 | 122.9782 | -122.7676 | -27.713 | 122.85 | 122.9736 | 95.8786 | 95.5124
285.4844 | 123.2986 | -115.9012 | 7.1869 | 0.018692 | 0.0036828 | 0.071081 | 0.066982 | 0.0050179 | -0.00022429 | 0.0015764 | 0.010803 | 0.0025656 | 0.020995 | 0.039251 | -0.00025213 | 0.011228 | -0.00055121 | -0.20142 | 7.2647 | -116.2445 | 7.0587 | -115.3656 | -115.9287 | -116.0202 | 0.009155 | 7.2098 | -0.11444 | 7.1091 | 0.082397 | 0 | 0.14191 | -0.34332 | 0.077819 | -0.12817 | 0.53558 | -0.11902 | -0.027466 | 0.2243 | 0.31586 | 115.7867 | 0.022888 | -0.07782 | 115.9836 | 116.0431 | 115.9012 | 0.25635 | 0.11444 | 0.87891 | 123.3032 | 0.19684 | 7.2235 | 123.5092 | 7.3242 | 123.1659 | 123.111 | -123.4314 | -7.3013 | 122.9599 | 123.0103 | 115.6998 | 115.9103
287.1719 | 123.2712 | -94.5969 | 28.5049 | 0.026321 | 0.0056054 | 0.071081 | 0.066554 | 0.0039499 | -0.00022429 | -0.00055975 | 0.010803 | 0.0019248 | 0.022917 | 0.031988 | 0.0010297 | 0.011869 | 0.0017988 | -0.16479 | 28.5553 | -94.7891 | 28.5141 | -94.0475 | -94.5969 | -94.6381 | 0.059509 | 28.5004 | -0.07782 | 28.5782 | 0.18768 | 0.10529 | 0.15564 | -0.19226 | 0.050354 | 0.009155 | 0.54932 | -0.041199 | 0 | 0.15106 | 0.19226 | 94.519 | -0.004578 | 0.073242 | 94.7845 | 94.7525 | 94.7021 | 0.23346 | 0.18311 | 0.74158 | 123.3032 | 0.2655 | 28.656 | 123.3444 | 28.5782 | 123.1522 | 123.0972 | -123.2941 | -28.5828 | 123.111 | 123.175 | 94.4321 | 94.6564
288.875 | 123.317 | -94.5648 | 28.5141 | 0.011063 | 0.0021876 | 0.068945 | 0.064418 | 0.0054453 | -0.0040695 | -0.00013235 | 0.001648 | -0.00085241 | 0.022063 | 0.035406 | 0.00060247 | 0.0088782 | -0.00012381 | -0.14191 | 28.5507 | -94.8029 | 28.5599 | -93.988 | -94.5099 | -94.5602 | 0.073242 | 28.5004 | -0.064087 | 28.624 | 0.25635 | 0.16022 | 0.19684 | -0.23804 | 0.036621 | 0.045776 | 0.57678 | 0.004577 | 0.054931 | 0.24261 | 0.29297 | 94.5007 | -0.013733 | 0.10986 | 94.8212 | 94.7617 | 94.725 | 0.26093 | 0.2243 | 0.81482 | 123.3627 | 0.32044 | 28.688 | 123.3536 | 28.5645 | 123.1155 | 123.0652 | -123.317 | -28.5782 | 123.1247 | 123.1888 | 94.4229 | 94.6381
290.5469 | 123.2849 | -94.5602 | 28.5324 | 0.0034333 | 0.0058192 | 0.071508 | 0.066982 | 0.0028817 | -0.0010789 | 0.00072205 | 0.0046998 | 0.0019248 | 0.019927 | 0.03092 | -0.0026019 | 0.0069556 | 0.00030339 | -0.1236 | 28.5736 | -94.7937 | 28.5461 | -94.0201 | -94.5511 | -94.606 | 0.036621 | 28.5049 | -0.082397 | 28.5919 | 0.24261 | 0.12817 | 0.17853 | -0.23346 | 0.041198 | 0.013733 | 0.54016 | -0.045776 | 0.009156 | 0.18768 | 0.24262 | 94.4778 | -0.027466 | 0.059509 | 94.8029 | 94.7388 | 94.6884 | 0.26092 | 0.21057 | 0.77362 | 123.3398 | 0.32501 | 28.6743 | 123.3673 | 28.5873 | 123.1338 | 123.0652 | -123.3261 | -28.6148 | 123.1064 | 123.1522 | 94.4366 | 94.5969
292.2188 | 123.317 | -94.6014 | 28.5278 | 0.011063 | 0.0058192 | 0.071295 | 0.065913 | 0.0045907 | -0.0025741 | -0.00013235 | -0.0014038 | 0.0010702 | 0.022063 | 0.034765 | -0.0013201 | 0.010374 | -0.00012381 | -0.12817 | 28.5782 | -94.7983 | 28.5507 | -94.0018 | -94.519 | -94.5831 | 0.054932 | 28.5049 | -0.073242 | 28.6102 | 0.24719 | 0.16479 | 0.19226 | -0.19684 | 0.050354 | 0.022888 | 0.59967 | 0.01831 | 0.082397 | 0.21515 | 0.27924 | 94.5282 | -0.022888 | 0.082397 | 94.8486 | 94.7937 | 94.7662 | 0.2655 | 0.23804 | 0.79651 | 123.349 | 0.32043 | 28.6835 | 123.3765 | 28.5782 | 123.1796 | 123.1064 | -123.3261 | -28.6011 | 123.1522 | 123.2117 | 94.4733 | 94.6564
293.9219 | 123.2803 | -94.5602 | 28.537 | 0.011063 | 0.0049646 | 0.070654 | 0.064845 | 0.0024545 | -0.0040695 | 0.00093565 | 0.0046998 | 0.0021384 | 0.022063 | 0.036474 | 0.0012433 | 0.01016 | -0.0035418 | -0.1831 | 28.569 | -94.8029 | 28.5004 | -94.0842 | -94.6106 | -94.6335 | 0.009155 | 28.4958 | -0.091553 | 28.5828 | 0.17853 | 0.082397 | 0.16479 | -0.24261 | 0.032044 | -0.036621 | 0.47608 | -0.073242 | -0.050354 | 0.16937 | 0.19226 | 94.4687 | -0.041198 | 0.045777 | 94.7388 | 94.725 | 94.6426 | 0.25635 | 0.17395 | 0.71869 | 123.3032 | 0.27008 | 28.6743 | 123.3719 | 28.5873 | 123.1293 | 123.056 | -123.3398 | -28.6285 | 123.0606 | 123.143 | 94.3771 | 94.5694
295.625 | 123.2346 | -94.6243 | 28.537 | 0.018692 | 0.008169 | 0.069372 | 0.066768 | 0.0015999 | -0.0055649 | 0.0022174 | 0.0046998 | 0.0032064 | 0.02014 | 0.025579 | 0.00017507 | 0.0093054 | -0.0041828 | -0.11444 | 28.6011 | -94.8624 | 28.4317 | -94.1528 | -94.6518 | -94.6838 | -0.027466 | 28.5233 | -0.082397 | 28.5324 | 0.16937 | 0.059509 | 0.14648 | -0.23804 | 0.064087 | -0.10528 | 0.4715 | -0.059509 | -0.027465 | 0.17853 | 0.21057 | 94.5419 | -0.013733 | -0.004577 | 94.7937 | 94.7708 | 94.6838 | 0.22888 | 0.14191 | 0.70953 | 123.2941 | 0.25177 | 28.6148 | 123.4634 | 28.6057 | 123.2254 | 123.1476 | -123.3994 | -28.6194 | 123.056 | 123.1567 | 94.5099 | 94.5969
297.3438 | 123.2986 | -94.5648 | 28.5416 | 0.018692 | 0.0045374 | 0.069158 | 0.064418 | 0.0011727 | -0.0012925 | -0.0014142 | 0.0046998 | 0.00064299 | 0.021209 | 0.026434 | -0.00089293 | 0.010587 | 0.0017988 | -0.13275 | 28.5873 | -94.8166 | 28.5233 | -94.0384 | -94.5511 | -94.5969 | 0.045776 | 28.4958 | -0.068665 | 28.5965 | 0.23346 | 0.14648 | 0.17853 | -0.25177 | 0.045776 | -0.018311 | 0.52643 | -0.032044 | 0.013733 | 0.21973 | 0.2655 | 94.4962 | -0.045776 | 0.054932 | 94.7983 | 94.7433 | 94.7113 | 0.24719 | 0.21515 | 0.7782 | 123.3398 | 0.30212 | 28.6652 | 123.4039 | 28.5645 | 123.1522 | 123.0606 | -123.3582 | -28.6102 | 123.0881 | 123.1613 | 94.4321 | 94.6106
299.0469 | 123.1934 | -94.6289 | 28.5461 | 0.0034333 | 0.00646 | 0.070013 | 0.066768 | 0.0039499 | -0.0015061 | 0.00072205 | 0.0046998 | 0.0042746 | 0.022277 | 0.03092 | 0.0014569 | 0.010374 | -0.00097841 | -0.1831 | 28.5873 | -94.8532 | 28.3859 | -94.2078 | -94.7342 | -94.7617 | -0.11902 | 28.5324 | -0.09613 | 28.4592 | 0.07782 | -0.027466 | 0.073242 | -0.2243 | 0.041198 | -0.16022 | 0.42114 | -0.13275 | -0.10529 | 0.091552 | 0.11902 | 94.5328 | -0.013733 | -0.086976 | 94.7067 | 94.7021 | 94.6014 | 0.16937 | 0.068664 | 0.64545 | 123.2391 | 0.17395 | 28.5553 | 123.4406 | 28.6285 | 123.2162 | 123.1613 | -123.3994 | -28.6423 | 123.0148 | 123.0881 | 94.4458 | 94.5099
300.7344 | 123.3124 | -94.574 | 28.4866 | 0.026321 | 0.0062464 | 0.071935 | 0.067409 | 0.0041635 | -0.0010789 | 0.0015764 | 0.013855 | 0.0014976 | 0.020568 | 0.029852 | 0.00060247 | 0.010801 | -0.00076481 | -0.14648 | 28.5553 | -94.8349 | 28.5233 | -94.0659 | -94.6014 | -94.6335 | 0.068665 | 28.4775 | -0.068665 | 28.6057 | 0.21973 | 0.1236 | 0.18768 | -0.26093 | 0.068665 | 0.036621 | 0.50812 | -0.059509 | -0.027465 | 0.20142 | 0.23346 | 94.5053 | -0.009155 | 0.11902 | 94.7937 | 94.7617 | 94.6976 | 0.25635 | 0.19226 | 0.76904 | 123.3582 | 0.28839 | 28.6743 | 123.3902 | 28.5461 | 123.1293 | 123.0515 | -123.3215 | -28.5553 | 123.0972 | 123.1796 | 94.4275 | 94.6426
302.4062 | 123.2986 | -94.5877 | 28.5187 | 0.018692 | 0.0051782 | 0.070654 | 0.066554 | 0.0028817 | -0.0019333 | 0.003499 | 0.0046998 | 0.0019248 | 0.023345 | 0.031561 | 0.0014569 | 0.010801 | 0.0054304 | -0.19684 | 28.5736 | -94.8257 | 28.4912 | -94.0887 | -94.6198 | -94.6472 | 0.013733 | 28.5049 | -0.073242 | 28.5599 | 0.16937 | 0.10529 | 0.16022 | -0.23804 | 0.054931 | -0.027466 | 0.49896 | -0.059509 | -0.032043 | 0.17853 | 0.20599 | 94.5145 | -0.013733 | 0.041198 | 94.7571 | 94.7479 | 94.693 | 0.23346 | 0.17853 | 0.737 | 123.317 | 0.24261 | 28.6331 | 123.3994 | 28.5782 | 123.1613 | 123.0927 | -123.3444 | -28.5919 | 123.0789 | 123.1476 | 94.3909 | 94.6014
304.1094 | 123.1979 | -94.6106 | 28.5324 | 0.018692 | 0.0068872 | 0.070867 | 0.069118 | 0.0050179 | -0.00086509 | -0.0014142 | 0.0046998 | 0.0038474 | 0.021422 | 0.030065 | -0.00025213 | 0.0082374 | 0.00051699 | -0.13275 | 28.5599 | -94.8624 | 28.3951 | -94.2078 | -94.7021 | -94.7617 | -0.07782 | 28.5004 | -0.09613 | 28.4866 | 0.091553 | -0.013733 | 0.10071 | -0.25177 | 0.027465 | -0.13733 | 0.40283 | -0.15106 | -0.091552 | 0.10071 | 0.16022 | 94.5145 | -0.032044 | -0.045777 | 94.7021 | 94.7113 | 94.5969 | 0.19684 | 0.082397 | 0.6546 | 123.2574 | 0.18768 | 28.5828 | 123.4222 | 28.5965 | 123.1705 | 123.111 | -123.3948 | -28.6285 | 123.0057 | 123.0972 | 94.4778 | 94.5328
305.7969 | 123.3444 | -94.5602 | 28.5095 | 0.011063 | 0.0028284 | 0.070226 | 0.066341 | 0.0024545 | -0.0023605 | -0.00013235 | 0.001648 | -0.00021141 | 0.020354 | 0.028356 | 0.0010297 | 0.010801 | 0.00094419 | -0.16022 | 28.5324 | -94.7845 | 28.5095 | -94.0247 | -94.5465 | -94.5969 | 0.082397 | 28.5049 | -0.064087 | 28.6148 | 0.2655 | 0.18768 | 0.20142 | -0.2243 | 0.022889 | 0 | 0.53558 | -0.036621 | 0.013733 | 0.18768 | 0.23804 | 94.4962 | -0.004577 | 0.10529 | 94.8257 | 94.7617 | 94.7479 | 0.2655 | 0.25177 | 0.75989 | 123.2941 | 0.32959 | 28.6789 | 123.317 | 28.569 | 123.0927 | 123.0652 | -123.2941 | -28.5736 | 123.0698 | 123.175 | 94.4 | 94.6426
307.5156 | 123.2208 | -94.6198 | 28.5233 | 0.011063 | 0.0062464 | 0.070013 | 0.067622 | 0.0043771 | -0.0027877 | 8.125e-05 | 0.001648 | 0.0019248 | 0.021209 | 0.02622 | 0.00060247 | 0.0090918 | -0.0024738 | -0.2243 | 28.5736 | -94.8532 | 28.363 | -94.2215 | -94.725 | -94.7433 | -0.086975 | 28.4958 | -0.091553 | 28.4683 | 0.10071 | 0.009155 | 0.10071 | -0.23346 | 0.050354 | -0.16022 | 0.39825 | -0.1236 | -0.10529 | 0.10986 | 0.12817 | 94.5282 | -0.027465 | -0.054931 | 94.7205 | 94.7205 | 94.6289 | 0.19226 | 0.10071 | 0.63171 | 123.2162 | 0.19226 | 28.5599 | 123.4268 | 28.5873 | 123.1934 | 123.1155 | -123.3765 | -28.6148 | 122.9828 | 123.0881 | 94.3954 | 94.5328
309.1875 | 123.262 | -94.5786 | 28.5233 | 0.011063 | 0.0049646 | 0.070654 | 0.062709 | 0.0060861 | 0.00063011 | -0.0018414 | 0.001648 | 0.0025656 | 0.019927 | 0.031988 | 0.00017507 | 0.011442 | 0.0043622 | -0.23346 | 28.5461 | -94.8349 | 28.4363 | -94.1162 | -94.6014 | -94.6609 | -0.032043 | 28.5095 | -0.07782 | 28.537 | 0.17395 | 0.07782 | 0.15106 | -0.25635 | 0.022889 | -0.086975 | 0.46234 | -0.082398 | -0.022888 | 0.17395 | 0.23346 | 94.5007 | -0.013733 | 0.013733 | 94.7525 | 94.7296 | 94.6564 | 0.22888 | 0.15564 | 0.71869 | 123.2712 | 0.25177 | 28.6148 | 123.381 | 28.5873 | 123.1247 | 123.0881 | -123.3582 | -28.6011 | 123.0148 | 123.1155 | 94.3451 | 94.5465
310.875 | 123.2758 | -94.574 | 28.5233 | 0.011063 | 0.0041102 | 0.071935 | 0.067195 | 0.0062997 | -0.00065149 | -0.0018414 | 0.0077514 | 0.002352 | 0.020568 | 0.038824 | -0.00046573 | 0.0099462 | 0.002226 | -0.19684 | 28.5553 | -94.8395 | 28.4683 | -94.0979 | -94.6198 | -94.6701 | 0 | 28.4683 | -0.082397 | 28.5507 | 0.16937 | 0.086975 | 0.15106 | -0.2655 | 0.032044 | -0.054931 | 0.47608 | -0.09613 | -0.045776 | 0.16937 | 0.21973 | 94.4916 | -0.054931 | 0.027466 | 94.7433 | 94.725 | 94.6609 | 0.23346 | 0.16937 | 0.74158 | 123.3078 | 0.25177 | 28.6331 | 123.3948 | 28.5507 | 123.1293 | 123.0423 | -123.3627 | -28.6057 | 123.0423 | 123.1247 | 94.3771 | 94.574
312.5781 | 123.2391 | -94.606 | 28.5187 | 0.018692 | 0.0051782 | 0.069586 | 0.066127 | 0.0015999 | -0.0023605 | 0.00072205 | 0.0077514 | 0.0029928 | 0.022917 | 0.029638 | 0.00038887 | 0.0069556 | -0.0039692 | -0.11902 | 28.569 | -94.8486 | 28.4271 | -94.1483 | -94.6335 | -94.6884 | -0.018311 | 28.4912 | -0.073242 | 28.4912 | 0.15564 | 0.064087 | 0.14191 | -0.24262 | 0.050354 | -0.091553 | 0.45776 | -0.082398 | -0.027466 | 0.16022 | 0.21515 | 94.5328 | -0.027466 | -0.027466 | 94.7617 | 94.7479 | 94.6701 | 0.21515 | 0.13733 | 0.70038 | 123.2758 | 0.22888 | 28.5645 | 123.4177 | 28.5645 | 123.175 | 123.0972 | -123.3673 | -28.5919 | 123.0331 | 123.0972 | 94.487 | 94.5877
314.25 | 123.2849 | -94.5877 | 28.4775 | 0.0034333 | 0.0021876 | 0.070654 | 0.066554 | -0.0028861 | -0.0010789 | -0.00077335 | 0.001648 | 0.00042939 | 0.021849 | 0.035192 | -0.00046573 | 0.010374 | -0.00033761 | -0.20599 | 28.5141 | -94.8395 | 28.4317 | -94.1071 | -94.6198 | -94.6472 | -0.009155 | 28.4683 | -0.082397 | 28.5416 | 0.17853 | 0.1236 | 0.17395 | -0.25177 | 0.036621 | -0.045776 | 0.48065 | -0.059509 | -0.032043 | 0.19226 | 0.21973 | 94.5053 | -0.009155 | 0.064087 | 94.7662 | 94.7617 | 94.7113 | 0.25635 | 0.20599 | 0.73242 | 123.2712 | 0.26092 | 28.624 | 123.3536 | 28.5507 | 123.1018 | 123.056 | -123.317 | -28.5599 | 123.0194 | 123.1293 | 94.3817 | 94.5786
315.9844 | 123.2346 | -94.6152 | 28.4637 | 0.026321 | 0.0045374 | 0.069799 | 0.066341 | 0.0041635 | -0.0025741 | 8.125e-05 | 0.001648 | 0.004061 | 0.02014 | 0.027075 | 0.0014569 | 0.01016 | 0.0013714 | -0.2243 | 28.5645 | -94.8715 | 28.3585 | -94.2078 | -94.7296 | -94.7433 | -0.050354 | 28.4821 | -0.086975 | 28.5095 | 0.15564 | 0.054932 | 0.15106 | -0.25635 | 0.10071 | -0.10529 | 0.40741 | -0.12817 | -0.11444 | 0.12817 | 0.14191 | 94.5282 | 0.018311 | 0.045776 | 94.7708 | 94.7662 | 94.6701 | 0.23804 | 0.14191 | 0.66376 | 123.23 | 0.24261 | 28.5965 | 123.436 | 28.569 | 123.1796 | 123.0972 | -123.3353 | -28.5507 | 122.9736 | 123.1247 | 94.3909 | 94.5648
317.6562 | 123.3353 | -94.6106 | 28.4729 | 0.018692 | 0.0066736 | 0.07044 | 0.0657 | 0.0041635 | -0.00065149 | -0.0012006 | 0.0077514 | 0.0032064 | 0.021209 | 0.037542 | 0.00081607 | 0.011014 | -0.00012381 | -0.14648 | 28.5004 | -94.8074 | 28.4866 | -94.0796 | -94.6152 | -94.6472 | 0.073242 | 28.4683 | -0.045776 | 28.5736 | 0.22888 | 0.12817 | 0.21515 | -0.19684 | 0.027466 | 0.013733 | 0.53101 | -0.036621 | -0.004577 | 0.16022 | 0.19226 | 94.5648 | -0.004577 | 0.10071 | 94.8395 | 94.8257 | 94.7388 | 0.26093 | 0.17395 | 0.72784 | 123.2941 | 0.27466 | 28.6194 | 123.3078 | 28.5141 | 123.111 | 123.0789 | -123.2803 | -28.5187 | 123.0972 | 123.1842 | 94.4641 | 94.6838
319.375 | 123.1888 | -94.6518 | 28.5416 | 0.011063 | 0.0053918 | 0.068945 | 0.064845 | 0.0062997 | -0.0030015 | -0.0020552 | 0.0046998 | 0.0042746 | 0.018645 | 0.031133 | -0.0026019 | 0.008451 | 0.00030339 | -0.16479 | 28.5507 | -94.8624 | 28.363 | -94.1757 | -94.6838 | -94.7159 | -0.082397 | 28.4866 | -0.091553 | 28.4363 | 0.10071 | 0.022888 | 0.068665 | -0.21057 | 0.009155 | -0.17853 | 0.47607 | -0.064087 | -0.032044 | 0.14648 | 0.17853 | 94.5602 | -0.054932 | -0.10529 | 94.7525 | 94.7205 | 94.6747 | 0.16022 | 0.11444 | 0.68665 | 123.2254 | 0.19226 | 28.5278 | 123.4131 | 28.5782 | 123.2025 | 123.1384 | -123.4039 | -28.6331 | 123.0148 | 123.0881 | 94.487 | 94.5694
321.0625 | 123.2986 | -94.5877 | 28.4729 | 0.0034333 | 0.0024012 | 0.068945 | 0.064418 | 0.0052315 | -0.0021469 | 0.00029485 | -0.0014038 | 0.00021579 | 0.022704 | 0.035619 | 0.0023115 | 0.0088782 | 0.0011578 | -0.20599 | 28.5233 | -94.8395 | 28.4317 | -94.1025 | -94.6198 | -94.6609 | -0.009155 | 28.4637 | -0.073242 | 28.537 | 0.23346 | 0.14191 | 0.1831 | -0.25177 | 0.050354 | -0.041198 | 0.48523 | -0.073242 | -0.032043 | 0.17853 | 0.21973 | 94.5145 | -0.009155 | 0.064087 | 94.8212 | 94.7708 | 94.7296 | 0.25635 | 0.21515 | 0.737 | 123.2712 | 0.3067 | 28.6102 | 123.3627 | 28.537 | 123.111 | 123.0515 | -123.3124 | -28.5461 | 123.0194 | 123.1247 | 94.3817 | 94.5786
322.7188 | 123.1613 | -94.6472 | 28.5049 | 0.0034333 | 0.007528 | 0.071295 | 0.067409 | 0.0018137 | -0.0030015 | -0.00034615 | 0.0046998 | 0.0029928 | 0.022917 | 0.02622 | 0.00081607 | 0.011014 | 0.00073059 | -0.17853 | 28.537 | -94.8944 | 28.3264 | -94.2673 | -94.7571 | -94.7983 | -0.12817 | 28.4866 | -0.082397 | 28.4042 | 0.064087 | -0.036621 | 0.073242 | -0.24719 | 0.032043 | -0.17853 | 0.37994 | -0.15106 | -0.10986 | 0.09613 | 0.13733 | 94.5648 | -0.018311 | -0.10071 | 94.7113 | 94.7205 | 94.6106 | 0.15564 | 0.045776 | 0.62714 | 123.2208 | 0.14648 | 28.4866 | 123.4314 | 28.569 | 123.1842 | 123.1338 | -123.3994 | -28.5873 | 122.9736 | 123.0515 | 94.4687 | 94.519
324.4688 | 123.3032 | -94.5923 | 28.4683 | 0.0034333 | 0.0062464 | 0.073217 | 0.065486 | 0.00031834 | -0.0032151 | -0.002696 | 0.0046998 | 0.002352 | 0.020781 | 0.040319 | -0.00046573 | 0.0093054 | -0.0024738 | -0.21057 | 28.5004 | -94.8624 | 28.4088 | -94.1162 | -94.6289 | -94.6609 | 0.009155 | 28.45 | -0.082397 | 28.5233 | 0.2243 | 0.13275 | 0.16937 | -0.27008 | 0.032043 | -0.05951 | 0.47607 | -0.068665 | -0.036621 | 0.20142 | 0.23346 | 94.5099 | -0.018311 | 0.054931 | 94.8166 | 94.7617 | 94.725 | 0.25177 | 0.21515 | 0.74615 | 123.2712 | 0.3067 | 28.6057 | 123.3627 | 28.5324 | 123.0927 | 123.0423 | -123.3307 | -28.5507 | 123.0011 | 123.1155 | 94.3817 | 94.6014
326.1562 | 123.1659 | -94.6564 | 28.4592 | 0.0034333 | 0.0053918 | 0.071081 | 0.068263 | 0.0052315 | -0.0025741 | -0.00013235 | 0.001648 | 0.0038474 | 0.021209 | 0.031988 | -0.00025213 | 0.009519 | 0.0030804 | -0.20142 | 28.5233 | -94.9127 | 28.3081 | -94.2856 | -94.7845 | -94.8257 | -0.13733 | 28.4592 | -0.10071 | 28.4042 | 0.068665 | -0.009155 | 0.086975 | -0.25635 | 0.064087 | -0.15106 | 0.37079 | -0.16937 | -0.12817 | 0.086975 | 0.12817 | 94.5557 | 0 | -0.054931 | 94.725 | 94.7433 | 94.6472 | 0.18768 | 0.091553 | 0.62714 | 123.2208 | 0.16937 | 28.5049 | 123.436 | 28.5599 | 123.1796 | 123.1155 | -123.3719 | -28.5599 | 122.9645 | 123.0606 | 94.455 | 94.519
327.8281 | 123.2986 | -94.6335 | 28.4363 | 0.011063 | 0.0049646 | 0.07044 | 0.065913 | 0.0035227 | -0.0019333 | -0.00077335 | 0.001648 | 0.0032064 | 0.019927 | 0.039678 | 0.0027387 | 0.010801 | -0.0016192 | -0.17853 | 28.4729 | -94.8853 | 28.4225 | -94.1345 | -94.6426 | -94.6976 | 0.036621 | 28.4409 | -0.054932 | 28.537 | 0.2243 | 0.11902 | 0.21057 | -0.25177 | 0.036621 | -0.013733 | 0.49896 | -0.064087 | -0.009155 | 0.18768 | 0.24262 | 94.5786 | 0.004578 | 0.10071 | 94.8578 | 94.8441 | 94.7525 | 0.2655 | 0.17395 | 0.75073 | 123.3078 | 0.27924 | 28.5919 | 123.3582 | 28.4958 | 123.1064 | 123.0743 | -123.3215 | -28.4912 | 123.056 | 123.1705 | 94.455 | 94.6701
329.5469 | 123.1979 | -94.6472 | 28.4775 | 0.0034333 | 0.003042 | 0.068304 | 0.064845 | 0.0028817 | -0.0019333 | -0.00013235 | 0.0046998 | 0.0025656 | 0.020995 | 0.028997 | -0.0017475 | 0.0088782 | 0.00073059 | -0.11444 | 28.4866 | -94.8532 | 28.3859 | -94.1483 | -94.6381 | -94.6838 | -0.041199 | 28.4454 | -0.07782 | 28.418 | 0.12817 | 0.059509 | 0.10529 | -0.20599 | 0.009155 | -0.091553 | 0.49896 | -0.036621 | 0.009155 | 0.16937 | 0.21515 | 94.5694 | -0.032043 | -0.059509 | 94.7754 | 94.7525 | 94.7067 | 0.18311 | 0.13733 | 0.70496 | 123.2391 | 0.20599 | 28.4958 | 123.3398 | 28.5233 | 123.1338 | 123.0927 | -123.3307 | -28.5553 | 123.0331 | 123.0652 | 94.5328 | 94.606
331.2188 | 123.1934 | -94.6564 | 28.4592 | 0.018692 | 0.0041102 | 0.068945 | 0.06805 | 0.0052315 | -0.0049241 | 0.00093565 | 0.0077514 | 0.002352 | 0.022704 | 0.026647 | -0.0028155 | 0.0090918 | -0.001192 | -0.16022 | 28.5324 | -94.9081 | 28.3127 | -94.2398 | -94.7021 | -94.7525 | -0.10071 | 28.4592 | -0.10986 | 28.4088 | 0.091553 | 0.027466 | 0.091553 | -0.25177 | 0.073243 | -0.14648 | 0.41657 | -0.09613 | -0.045776 | 0.15564 | 0.20599 | 94.5465 | 0 | -0.050354 | 94.7479 | 94.7479 | 94.6838 | 0.20142 | 0.13733 | 0.66833 | 123.2208 | 0.20142 | 28.5187 | 123.4406 | 28.569 | 123.1888 | 123.1155 | -123.3673 | -28.569 | 122.9691 | 123.0652 | 94.4962 | 94.5557
332.8906 | 123.3582 | -94.6152 | 28.4363 | -0.0041962 | 0.0043238 | 0.070013 | 0.064204 | 0.0020273 | -0.0036423 | 0.00093565 | 0.001648 | 0.0021384 | 0.018218 | 0.031133 | -0.0011065 | 0.0090918 | -0.0018328 | -0.14648 | 28.4775 | -94.8624 | 28.4363 | -94.0659 | -94.5969 | -94.6426 | 0.086975 | 28.4088 | -0.059509 | 28.5233 | 0.24719 | 0.16937 | 0.1831 | -0.24719 | 0.041199 | 0 | 0.54932 | -0.027466 | 0.01831 | 0.21973 | 0.2655 | 94.5557 | -0.027466 | 0.086975 | 94.8624 | 94.7983 | 94.7845 | 0.24261 | 0.22888 | 0.79651 | 123.2986 | 0.3067 | 28.5828 | 123.3398 | 28.4683 | 123.0927 | 123.024 | -123.2986 | -28.4958 | 123.0515 | 123.1384 | 94.4687 | 94.7021
334.5781 | 123.2025 | -94.6655 | 28.45 | 0.011063 | 0.0073144 | 0.070867 | 0.064204 | -0.0022453 | -0.0032151 | 0.0011492 | 0.001648 | -0.00021141 | 0.020995 | 0.026861 | -0.00067933 | 0.008451 | 8.9786e-05 | -0.13733 | 28.4866 | -94.8715 | 28.3997 | -94.1483 | -94.6426 | -94.6884 | -0.036621 | 28.4363 | -0.068665 | 28.4317 | 0.15106 | 0.059509 | 0.1236 | -0.20599 | 0.036621 | -0.050354 | 0.51727 | -0.022889 | 0.022888 | 0.1831 | 0.22888 | 94.5969 | -0.013733 | -0.01831 | 94.8166 | 94.7891 | 94.725 | 0.19226 | 0.12817 | 0.72327 | 123.2712 | 0.21973 | 28.5004 | 123.3582 | 28.5049 | 123.1522 | 123.1018 | -123.3215 | -28.5187 | 123.0652 | 123.0972 | 94.5282 | 94.6289
336.2656 | 123.2346 | -122.8775 | 0.3067 | -0.0041962 | 0.0062464 | 0.070013 | 0.069545 | 0.0058725 | -0.0010789 | 0.003499 | 0.0077514 | 0.032473 | 0.017577 | 0.012975 | 0.00060247 | 0.0080236 | 8.9786e-05 | -0.27924 | 0.31586 | -123.1659 | 0.041199 | -122.2778 | -122.8867 | -122.9736 | -0.036621 | 0.29755 | -0.11902 | 0.10529 | 0.050354 | -0.045776 | 0.2243 | -0.28839 | 0.009155 | -0.2655 | 0.59967 | -0.096131 | -0.009156 | 0.19226 | 0.27924 | 122.7585 | -0.009156 | -0.20142 | 122.9279 | 123.1018 | 122.8317 | 0.34332 | 0.073243 | 0.88806 | 123.2071 | 0.16937 | 0.22431 | 123.4818 | 0.41656 | 123.1934 | 123.175 | -123.4726 | -0.42572 | 122.9187 | 122.9828 | 122.5983 | 122.8409
338.125 | 123.317 | -122.8683 | 0.26093 | 0.0034333 | 0.0045374 | 0.068517 | 0.064632 | 0.00010474 | -0.00065149 | 0.00414 | -0.0014038 | 0.028841 | 0.021849 | 0.014257 | -0.0013201 | 0.0088782 | -0.0039692 | -0.2655 | 0.29755 | -123.1293 | 0.11444 | -122.1588 | -122.7676 | -122.8592 | 0.054932 | 0.25177 | -0.09613 | 0.21973 | 0.18768 | 0.10986 | 0.32044 | -0.26093 | 0.036621 | -0.14648 | 0.70953 | 0.009155 | 0.10071 | 0.27008 | 0.36163 | 122.7722 | -0.009155 | -0.041198 | 123.056 | 123.1888 | 122.9782 | 0.41657 | 0.20599 | 0.97046 | 123.2437 | 0.28381 | 0.31586 | 123.4268 | 0.3479 | 123.1659 | 123.1201 | -123.3902 | -0.35706 | 122.9828 | 123.0881 | 122.6028 | 122.9233
339.8906 | 123.2803 | -122.8912 | 0.27466 | 0.011063 | 0.0028284 | 0.070013 | 0.0657 | 0.0035227 | -0.00043789 | 0.0020038 | 0.0046998 | 0.028414 | 0.018859 | 0.012335 | -0.00067933 | 0.011442 | 0.00051699 | -0.33417 | 0.30212 | -123.143 | 0.045776 | -122.2641 | -122.8409 | -122.9324 | -0.018311 | 0.27466 | -0.10529 | 0.15564 | 0.1236 | 0.036621 | 0.27008 | -0.25177 | 0.027466 | -0.22888 | 0.62714 | -0.041199 | 0.050354 | 0.21057 | 0.30212 | 122.7859 | 0 | -0.11902 | 123.0148 | 123.1613 | 122.9279 | 0.37537 | 0.14191 | 0.87891 | 123.1888 | 0.22888 | 0.26093 | 123.4451 | 0.37994 | 123.1934 | 123.1659 | -123.4177 | -0.37994 | 122.937 | 123.0469 | 122.5571 | 122.8729
341.5781 | 123.3078 | -122.8867 | 0.27466 | 0.0034333 | 0.004751 | 0.069799 | 0.064204 | 0.0022409 | -0.0025741 | -0.00055975 | -0.0014038 | 0.0282 | 0.018218 | 0.01383 | -0.0017475 | 0.0099462 | -0.001192 | -0.24719 | 0.31128 | -123.111 | 0.13733 | -122.1542 | -122.7448 | -122.85 | 0.068665 | 0.27466 | -0.09613 | 0.21515 | 0.19684 | 0.11902 | 0.31586 | -0.2243 | 0.036621 | -0.13733 | 0.73242 | 0.036621 | 0.14191 | 0.26093 | 0.36621 | 122.7905 | 0 | -0.059509 | 123.0835 | 123.2025 | 123.0057 | 0.41199 | 0.21515 | 0.95673 | 123.2483 | 0.29297 | 0.31128 | 123.4222 | 0.37079 | 123.1979 | 123.1613 | -123.3856 | -0.37079 | 123.024 | 123.1018 | 122.6395 | 122.9553
343.3281 | 123.2071 | -122.9004 | 0.32501 | 0.011063 | 0.0053918 | 0.071081 | 0.066341 | 0.0015999 | -0.0047103 | -0.0012006 | 0.001648 | 0.030123 | 0.016936 | 0.012975 | 0.00017507 | 0.0088782 | 0.00094419 | -0.24719 | 0.32044 | -123.1293 | 0.050354 | -122.2366 | -122.8317 | -122.9095 | -0.032043 | 0.33417 | -0.1236 | 0.11444 | 0.07782 | -0.027466 | 0.2243 | -0.22888 | -0.004577 | -0.27466 | 0.66376 | -0.009155 | 0.068665 | 0.21973 | 0.29755 | 122.7768 | 0.009155 | -0.21057 | 122.9782 | 123.1247 | 122.8729 | 0.3479 | 0.09613 | 0.89264 | 123.1796 | 0.20142 | 0.23804 | 123.4497 | 0.45776 | 123.2208 | 123.2346 | -123.4543 | -0.44861 | 122.9507 | 123.0148 | 122.6532 | 122.8683
345.0781 | 123.3078 | -122.8546 | 0.29755 | 0.0034333 | 0.004751 | 0.072149 | 0.064632 | 0.0054453 | -0.0025741 | -0.00055975 | 0.0046998 | 0.029482 | 0.018645 | 0.018316 | 0.0044477 | 0.0086646 | -0.00097841 | -0.24261 | 0.32044 | -123.0835 | 0.15564 | -122.1359 | -122.7585 | -122.8363 | 0.064087 | 0.29755 | -0.082397 | 0.2655 | 0.17395 | 0.09613 | 0.35706 | -0.22888 | 0.022889 | -0.14191 | 0.71869 | 0.01831 | 0.09613 | 0.24719 | 0.32501 | 122.7722 | 0 | -0.032043 | 123.0286 | 123.2117 | 122.9507 | 0.43945 | 0.17853 | 0.94757 | 123.2391 | 0.25635 | 0.3479 | 123.4039 | 0.37994 | 123.175 | 123.1522 | -123.381 | -0.37994 | 123.0103 | 123.1201 | 122.612 | 122.9187
346.75 | 123.1842 | -122.9004 | 0.34332 | 0.018692 | 0.0034692 | 0.072363 | 0.065486 | 0.0043771 | -0.0044967 | 0.0026446 | 0.0046998 | 0.018801 | 0.0195 | 0.028143 | -0.0015337 | 0.0086646 | 0.0045758 | -0.2655 | 0.35248 | -123.0972 | 0.050354 | -122.2504 | -122.818 | -122.905 | -0.086975 | 0.32501 | -0.1236 | 0.12817 | 0.073242 | 0.11902 | 0.23804 | -0.19684 | 0.009155 | -0.29297 | 0.65002 | -0.004577 | 0.082398 | 0.19226 | 0.27924 | 122.7768 | -0.018311 | -0.21515 | 122.9736 | 123.1384 | 123.0194 | 0.36163 | 0.24261 | 0.84686 | 123.1476 | 0.19684 | 0.25177 | 123.4497 | 0.44861 | 123.2529 | 123.2254 | -123.4406 | -0.46692 | 122.9507 | 123.0286 | 122.6349 | 122.8134
348.5 | 123.175 | -122.8867 | 0.33875 | 0.0034333 | 0.007528 | 0.070226 | 0.068691 | 0.0048043 | -0.0030015 | -0.002696 | 0.001648 | 0.01816 | 0.019072 | 0.023657 | 0.0012433 | 0.0073828 | 0.00094419 | -0.22888 | 0.36163 | -123.1018 | 0.073242 | -122.2229 | -122.8226 | -122.9141 | -0.022888 | 0.32501 | -0.11902 | 0.16022 | 0.064087 | 0.11444 | 0.2655 | -0.21515 | 0.022888 | -0.2655 | 0.66376 | -0.027466 | 0.064087 | 0.18768 | 0.27924 | 122.7676 | -0.013733 | -0.17853 | 122.9507 | 123.1522 | 123.0011 | 0.38452 | 0.23346 | 0.87891 | 123.175 | 0.18311 | 0.27924 | 123.4634 | 0.44403 | 123.2483 | 123.2117 | -123.4406 | -0.45776 | 122.9599 | 123.0469 | 122.6578 | 122.8638
350.1875 | 123.2803 | -122.8271 | 0.3479 | 0.0034333 | 0.0038966 | 0.071508 | 0.064632 | 0.0030953 | -0.0038559 | -0.0031232 | -0.0014038 | 0.016024 | 0.018218 | 0.026861 | -0.0017475 | 0.0099462 | 0.002226 | -0.23346 | 0.33875 | -123.0881 | 0.16937 | -122.1085 | -122.7036 | -122.8134 | 0.068665 | 0.31586 | -0.10071 | 0.24261 | 0.18768 | 0.25177 | 0.35706 | -0.26093 | -0.009155 | -0.17853 | 0.71869 | 0.013732 | 0.1236 | 0.27466 | 0.38452 | 122.7264 | -0.032043 | -0.10528 | 123.0148 | 123.1842 | 123.0789 | 0.45776 | 0.35248 | 0.97962 | 123.2574 | 0.28839 | 0.34332 | 123.4268 | 0.41657 | 123.1659 | 123.143 | -123.436 | -0.44861 | 122.9965 | 123.0698 | 122.5937 | 122.8958
351.9219 | 123.1934 | -122.8958 | 0.34332 | 0.026321 | 0.0036828 | 0.070226 | 0.065913 | 0.0024545 | -0.0027877 | -0.00098695 | 0.0046998 | 0.019655 | 0.0195 | 0.025152 | -0.0019611 | 0.008451 | -0.00097841 | -0.25177 | 0.37537 | -123.1247 | 0.027466 | -122.2641 | -122.8363 | -122.9095 | -0.073242 | 0.35248 | -0.12817 | 0.14191 | 0.082397 | 0.13275 | 0.25635 | -0.22888 | 0.032043 | -0.31586 | 0.63171 | -0.013733 | 0.059509 | 0.21515 | 0.28839 | 122.7676 | 0.009155 | -0.20142 | 122.9782 | 123.1522 | 123.0286 | 0.38452 | 0.26093 | 0.8606 | 123.1522 | 0.21057 | 0.27008 | 123.5001 | 0.48065 | 123.2712 | 123.2483 | -123.468 | -0.4715 | 122.9233 | 123.0377 | 122.644 | 122.8226
353.6094 | 123.2712 | -122.8409 | 0.28381 | 0.011063 | 0.004751 | 0.072576 | 0.065273 | 0.0013863 | -0.0015061 | -0.00055975 | 0.0046998 | 0.017092 | 0.021209 | 0.03092 | 0.0018841 | 0.01016 | 0.0035078 | -0.31586 | 0.34332 | -123.0927 | 0.07782 | -122.2092 | -122.8317 | -122.8912 | 0.018311 | 0.3067 | -0.10071 | 0.23346 | 0.15564 | 0.21057 | 0.35248 | -0.25177 | 0.05951 | -0.20599 | 0.63171 | -0.050354 | 0.009155 | 0.20142 | 0.26093 | 122.7402 | 0.022889 | -0.050354 | 122.9965 | 123.1934 | 123.0515 | 0.45319 | 0.31128 | 0.88348 | 123.1705 | 0.25635 | 0.33417 | 123.436 | 0.40741 | 123.1842 | 123.1476 | -123.3765 | -0.38452 | 122.9187 | 123.0743 | 122.525 | 122.8592
355.3594 | 123.1522 | -122.8821 | 0.32959 | 0.011063 | 0.0051782 | 0.07044 | 0.066982 | 0.0086495 | -0.0010789 | 0.00072205 | 0.010803 | 0.015597 | 0.019713 | 0.022588 | 0.0012433 | 0.01251 | 0.0024396 | -0.2655 | 0.3479 | -123.1247 | 0.009155 | -122.3099 | -122.8958 | -122.9691 | -0.10071 | 0.33875 | -0.1236 | 0.09613 | 0.027466 | 0.059509 | 0.21973 | -0.24262 | 0.01831 | -0.32043 | 0.5722 | -0.086975 | -0.013733 | 0.15564 | 0.22888 | 122.7585 | 0.009155 | -0.23346 | 122.9095 | 123.1018 | 122.9416 | 0.34332 | 0.1831 | 0.81482 | 123.1339 | 0.15106 | 0.21973 | 123.4726 | 0.46234 | 123.23 | 123.2208 | -123.4543 | -0.45319 | 122.8912 | 122.9782 | 122.6166 | 122.7814
357.1094 | 123.2529 | -122.8592 | 0.28839 | 0.018692 | 0.0068872 | 0.071508 | 0.066768 | 0.0033089 | -0.0019333 | -0.00013235 | 0.0077514 | 0.016665 | 0.018431 | 0.021307 | 0.0029523 | 0.010374 | 0.0017988 | -0.27008 | 0.3067 | -123.0881 | 0.12817 | -122.1405 | -122.7951 | -122.8455 | 0.07782 | 0.27924 | -0.10071 | 0.22888 | 0.16937 | 0.20142 | 0.3067 | -0.22888 | 0.018311 | -0.16022 | 0.71869 | 0.013733 | 0.064087 | 0.24262 | 0.29297 | 122.7585 | -0.009155 | -0.059509 | 123.0286 | 123.1659 | 123.0606 | 0.40741 | 0.30212 | 0.94757 | 123.2162 | 0.27008 | 0.32959 | 123.3948 | 0.37994 | 123.1659 | 123.1384 | -123.3765 | -0.3891 | 122.9874 | 123.0881 | 122.5891 | 122.937
358.7969 | 123.317 | -122.8546 | 0.30212 | 0.018692 | 0.0045374 | 0.068945 | 0.064632 | 0.0065133 | -0.0036423 | -0.00098695 | 0.001648 | 0.016024 | 0.01715 | 0.026647 | -0.0017475 | 0.010374 | -0.002901 | -0.27008 | 0.31128 | -123.111 | 0.11902 | -122.1588 | -122.7493 | -122.8317 | 0.068665 | 0.2655 | -0.09613 | 0.2243 | 0.21057 | 0.24261 | 0.35248 | -0.25635 | 0.009155 | -0.18311 | 0.6958 | 0.022888 | 0.10528 | 0.27924 | 0.36163 | 122.7585 | -0.036621 | -0.07782 | 123.0652 | 123.2071 | 123.0972 | 0.44861 | 0.33874 | 0.95215 | 123.23 | 0.3067 | 0.32043 | 123.4222 | 0.36163 | 123.1659 | 123.1201 | -123.4131 | -0.39825 | 122.9736 | 123.0789 | 122.5845 | 122.9233
360.5625 | 123.2941 | -122.8592 | 0.31586 | 0.0034333 | 0.0045374 | 0.07044 | 0.065059 | -0.00096346 | -0.0040695 | -0.00077335 | 0.0046998 | 0.015383 | 0.019713 | 0.025793 | -0.00089293 | 0.0090918 | 0.0011578 | -0.22888 | 0.32501 | -123.1201 | 0.15106 | -122.0901 | -122.7036 | -122.7951 | 0.10529 | 0.28839 | -0.091553 | 0.23346 | 0.21515 | 0.2655 | 0.34332 | -0.26093 | 0.009155 | -0.16479 | 0.76904 | 0.064087 | 0.15564 | 0.32501 | 0.41656 | 122.7676 | -0.027466 | -0.082398 | 123.0743 | 123.2025 | 123.1247 | 0.43488 | 0.35706 | 1.03 | 123.2712 | 0.3067 | 0.32501 | 123.4451 | 0.37994 | 123.1842 | 123.1476 | -123.436 | -0.40741 | 123.0103 | 123.0927 | 122.6303 | 122.9645
362.25 | 123.2803 | -122.818 | 0.33417 | 0.0034333 | 0.0053918 | 0.071295 | 0.067622 | 0.0080087 | -0.00022429 | -0.0012006 | 0.0046998 | 0.016665 | 0.018859 | 0.02857 | 0.0040205 | 0.00781 | 0.00051699 | -0.24261 | 0.33875 | -123.0469 | 0.1831 | -122.1176 | -122.7356 | -122.8043 | 0.091553 | 0.29755 | -0.091553 | 0.27924 | 0.19226 | 0.24261 | 0.36621 | -0.22888 | 0.004578 | -0.15106 | 0.70038 | 0.013733 | 0.082397 | 0.24262 | 0.31128 | 122.7264 | -0.036621 | -0.054931 | 123.0103 | 123.1842 | 123.0606 | 0.45776 | 0.33417 | 0.92926 | 123.23 | 0.28381 | 0.37079 | 123.3856 | 0.3891 | 123.1567 | 123.1155 | -123.381 | -0.42572 | 123.0011 | 123.0972 | 122.5754 | 122.9095
363.9844 | 123.1567 | -122.8363 | 0.36163 | 0.0034333 | 0.0053918 | 0.072149 | 0.066341 | 0.0054453 | 0.00020291 | 0.0028582 | -0.0014038 | 0.019442 | 0.018431 | 0.026647 | 0.00017507 | 0.011869 | 8.9786e-05 | -0.21515 | 0.37537 | -123.0789 | 0.10071 | -122.2137 | -122.8226 | -122.905 | -0.045776 | 0.36163 | -0.11902 | 0.16479 | 0.073242 | 0.12817 | 0.27466 | -0.24261 | 0.013733 | -0.26092 | 0.62256 | -0.068664 | 0.013733 | 0.17395 | 0.25635 | 122.7173 | 0 | -0.19684 | 122.9095 | 123.111 | 122.9645 | 0.39368 | 0.24719 | 0.86517 | 123.1796 | 0.19226 | 0.28381 | 123.4543 | 0.48065 | 123.2117 | 123.1979 | -123.4406 | -0.48065 | 122.937 | 123.0011 | 122.6212 | 122.7905
365.6875 | 123.2483 | -122.7997 | 0.33875 | 0.0034333 | 0.0071008 | 0.072363 | 0.067622 | 0.0058725 | -0.0019333 | -0.0020552 | 0.010803 | 0.015597 | 0.021636 | 0.027929 | 0.0012433 | 0.011014 | 0.0041486 | -0.27466 | 0.36163 | -123.0423 | 0.16937 | -122.1176 | -122.7493 | -122.8134 | 0.041199 | 0.34332 | -0.10986 | 0.23346 | 0.14648 | 0.21515 | 0.34332 | -0.24261 | 0.022888 | -0.16937 | 0.68207 | -0.013733 | 0.050354 | 0.22888 | 0.29297 | 122.6898 | 0.004578 | -0.10529 | 122.9462 | 123.143 | 123.0148 | 0.45319 | 0.32501 | 0.92468 | 123.2117 | 0.25635 | 0.34332 | 123.4039 | 0.45319 | 123.1613 | 123.143 | -123.381 | -0.44861 | 122.9691 | 123.0331 | 122.525 | 122.8409
367.4219 | 123.2437 | -122.7859 | 0.37537 | 0.018692 | 0.00646 | 0.07279 | 0.065059 | 0.0065133 | -0.0015061 | 0.0013628 | 0.0046998 | 0.017092 | 0.018431 | 0.020025 | 0.0020979 | 0.010801 | 0.0062848 | -0.28381 | 0.37994 | -123.0103 | 0.18768 | -122.081 | -122.7081 | -122.7997 | 0.036621 | 0.36621 | -0.086975 | 0.27008 | 0.15564 | 0.25635 | 0.37537 | -0.2243 | 0.004578 | -0.18768 | 0.70496 | -0.013733 | 0.07782 | 0.21057 | 0.30212 | 122.699 | -0.009155 | -0.10528 | 122.9416 | 123.1613 | 123.0423 | 0.46234 | 0.34332 | 0.92926 | 123.1979 | 0.24261 | 0.35706 | 123.3902 | 0.45319 | 123.1659 | 123.1522 | -123.3856 | -0.46234 | 122.9736 | 123.056 | 122.5021 | 122.8226
369.0938 | 123.1705 | -122.7951 | 0.40283 | -0.0041962 | 0.0036828 | 0.070013 | 0.061855 | 0.0030953 | -0.0021469 | -0.00013235 | 0.0046998 | 0.01816 | 0.0195 | 0.030706 | -0.0036701 | 0.0080236 | 0.0037214 | -0.2243 | 0.39368 | -123.056 | 0.16022 | -122.1268 | -122.7036 | -122.8043 | -0.009155 | 0.41199 | -0.11902 | 0.19226 | 0.086975 | 0.20599 | 0.29755 | -0.26093 | -0.009155 | -0.24262 | 0.66834 | -0.009155 | 0.091553 | 0.25177 | 0.35248 | 122.6761 | 0.009155 | -0.21057 | 122.8821 | 123.0927 | 123.0011 | 0.41656 | 0.32501 | 0.92926 | 123.2162 | 0.20599 | 0.31128 | 123.4497 | 0.53101 | 123.1888 | 123.2071 | -123.4589 | -0.52185 | 122.9553 | 122.9874 | 122.5708 | 122.7859
370.8281 | 123.1888 | -122.9004 | 0.31128 | 0.018692 | 0.0043238 | 0.070226 | 0.068477 | 0.0028817 | -0.0034287 | 0.0017902 | 0.001648 | 0.017733 | 0.019927 | 0.021948 | -0.0021747 | 0.0099462 | 0.0026532 | -0.23804 | 0.35706 | -123.1567 | 0.009155 | -122.2824 | -122.8546 | -122.9324 | -0.09613 | 0.30212 | -0.11444 | 0.10986 | 0.068665 | 0.09613 | 0.23804 | -0.25635 | 0.045777 | -0.30212 | 0.61798 | -0.032043 | 0.045777 | 0.2243 | 0.30212 | 122.7859 | -0.009155 | -0.20142 | 122.9691 | 123.1384 | 122.9965 | 0.35248 | 0.21057 | 0.87433 | 123.1659 | 0.18311 | 0.2243 | 123.5138 | 0.41657 | 123.2574 | 123.2025 | -123.468 | -0.42572 | 122.9095 | 123.0103 | 122.6624 | 122.8043
372.5 | 123.2803 | -122.8363 | 0.28381 | 0.011063 | 0.0053918 | 0.070013 | 0.065486 | 0.0067269 | 0.0023391 | 0.0020038 | 0.0046998 | 0.017092 | 0.017791 | 0.033056 | 0.0042341 | 0.01016 | 0.0035078 | -0.25177 | 0.31586 | -123.0515 | 0.14648 | -122.1222 | -122.7493 | -122.8134 | 0.091553 | 0.30212 | -0.07782 | 0.25177 | 0.19226 | 0.21515 | 0.35248 | -0.21515 | 0.032044 | -0.13733 | 0.71411 | 0.022888 | 0.086975 | 0.23804 | 0.30212 | 122.7585 | 0.018311 | -0.032043 | 123.0286 | 123.1888 | 123.0515 | 0.4303 | 0.29297 | 0.92926 | 123.1979 | 0.27008 | 0.32959 | 123.3673 | 0.37994 | 123.1522 | 123.1384 | -123.3353 | -0.36163 | 122.9828 | 123.0881 | 122.5845 | 122.9279
374.2344 | 123.1842 | -122.7951 | 0.39368 | 0.0034333 | 0.0041102 | 0.071508 | 0.066554 | 0.0045907 | -0.0012925 | -0.0024824 | 0.001648 | 0.019442 | 0.018859 | 0.025579 | 0.0014569 | 0.011014 | -0.00076481 | -0.29755 | 0.4303 | -123.024 | 0.068665 | -122.2137 | -122.8088 | -122.8821 | -0.068665 | 0.41657 | -0.13733 | 0.19684 | 0.059509 | 0.16479 | 0.31586 | -0.22888 | 0.036621 | -0.32501 | 0.58136 | -0.086975 | -0.013733 | 0.14191 | 0.21515 | 122.6578 | 0.022888 | -0.19684 | 122.8546 | 123.111 | 122.9599 | 0.45319 | 0.30212 | 0.81024 | 123.0927 | 0.19684 | 0.33417 | 123.4543 | 0.55389 | 123.2254 | 123.2117 | -123.4177 | -0.53101 | 122.8638 | 122.9919 | 122.4976 | 122.7264
375.9219 | 123.143 | -122.8546 | 0.33875 | -0.0041962 | 0.0058192 | 0.071295 | 0.063564 | 0.0050179 | -0.0038559 | -0.00077335 | 0.001648 | 0.015597 | 0.019072 | 0.027502 | -0.0040973 | 0.0088782 | 0.0020124 | -0.24719 | 0.36163 | -123.0789 | 0.054932 | -122.2046 | -122.7859 | -122.8683 | -0.054932 | 0.36163 | -0.10986 | 0.13733 | 0.073242 | 0.13733 | 0.26093 | -0.2243 | 0.022888 | -0.28381 | 0.65002 | -0.013733 | 0.068664 | 0.21057 | 0.29297 | 122.7448 | 0.022888 | -0.20142 | 122.9279 | 123.1155 | 122.9919 | 0.37079 | 0.24719 | 0.87433 | 123.1338 | 0.18311 | 0.24719 | 123.4406 | 0.4715 | 123.2162 | 123.2162 | -123.4177 | -0.44861 | 122.9095 | 122.9919 | 122.6074 | 122.7997
377.6719 | 123.1979 | -122.85 | 0.33875 | 0.018692 | 0.0056054 | 0.070867 | 0.065059 | 0.0050179 | -0.0019333 | -0.00034615 | 0.0077514 | 0.018801 | 0.020354 | 0.028997 | -0.0036701 | 0.0088782 | 0.00030339 | -0.20599 | 0.37537 | -123.0789 | 0.086975 | -122.1909 | -122.7676 | -122.8683 | 0.004578 | 0.3479 | -0.12817 | 0.19226 | 0.11902 | 0.17853 | 0.30212 | -0.22888 | 0.036621 | -0.25177 | 0.65918 | -0.01831 | 0.082398 | 0.21057 | 0.31128 | 122.7219 | 0.009155 | -0.14648 | 122.9691 | 123.1522 | 123.0286 | 0.4303 | 0.3067 | 0.88806 | 123.1659 | 0.24719 | 0.32044 | 123.4543 | 0.47607 | 123.2254 | 123.1979 | -123.4177 | -0.46692 | 122.937 | 123.0423 | 122.644 | 122.8546
379.3594 | 123.1384 | -122.8592 | 0.34332 | 0.011063 | 0.0056054 | 0.068945 | 0.065486 | 0.0043771 | -0.0032151 | -0.0014142 | -0.0014038 | 0.016665 | 0.019927 | 0.02387 | 0.0014569 | 0.010801 | 0.0035078 | -0.3067 | 0.35248 | -123.0835 | 0.013733 | -122.2595 | -122.8638 | -122.9233 | -0.07782 | 0.33417 | -0.1236 | 0.13733 | 0.19226 | 0.11444 | 0.26093 | -0.2243 | 0.009155 | -0.32959 | 0.59967 | -0.064087 | -0.004578 | 0.16022 | 0.21973 | 122.7356 | -0.009156 | -0.20599 | 123.0515 | 123.1201 | 122.9736 | 0.38452 | 0.23804 | 0.82397 | 123.0972 | 0.31586 | 0.26093 | 123.436 | 0.45776 | 123.2117 | 123.1934 | -123.4268 | -0.46692 | 122.8729 | 122.9965 | 122.5525 | 122.7814
381.1094 | 123.2758 | -122.8043 | 0.32501 | 0.018692 | 0.004751 | 0.071081 | 0.062496 | 0.0039499 | -0.0032151 | -0.00055975 | 0.001648 | 0.014956 | 0.017791 | 0.032415 | -0.0017475 | 0.0090918 | 0.001585 | -0.31586 | 0.34332 | -123.0972 | 0.10986 | -122.1451 | -122.7585 | -122.8271 | 0.004578 | 0.3067 | -0.11902 | 0.22888 | 0.31586 | 0.24719 | 0.35248 | -0.29297 | 0.018311 | -0.21515 | 0.65918 | -0.022888 | 0.045776 | 0.27008 | 0.33875 | 122.6852 | -0.01831 | -0.09613 | 123.1201 | 123.1567 | 123.0515 | 0.4715 | 0.36621 | 0.95215 | 123.2071 | 0.43488 | 0.3479 | 123.4406 | 0.42572 | 123.1476 | 123.111 | -123.4222 | -0.44403 | 122.9141 | 123.0331 | 122.4884 | 122.8088
382.7812 | 123.175 | -122.8821 | 0.33417 | 0.018692 | 0.0017602 | 0.070226 | 0.0657 | 0.0065133 | -0.0030015 | 0.00093565 | 0.001648 | 0.017306 | 0.020995 | 0.031561 | -0.0023883 | 0.0075964 | 0.0017988 | -0.25635 | 0.38452 | -123.111 | 0.022888 | -122.2458 | -122.8134 | -122.8912 | -0.064087 | 0.35706 | -0.1236 | 0.11902 | 0.22888 | 0.13275 | 0.2655 | -0.22888 | 0.050354 | -0.31128 | 0.63629 | -0.009155 | 0.068664 | 0.21973 | 0.29755 | 122.7585 | 0.022889 | -0.21515 | 123.111 | 123.1476 | 123.0148 | 0.3891 | 0.25635 | 0.86517 | 123.1338 | 0.35248 | 0.24261 | 123.4955 | 0.48065 | 123.2666 | 123.2391 | -123.4451 | -0.45776 | 122.905 | 123.0011 | 122.6257 | 122.818
384.5312 | 123.2025 | -122.8271 | 0.30212 | 0.026321 | 0.0011194 | 0.069799 | 0.064418 | 0.0011727 | -0.0010789 | -0.002696 | 0.0046998 | 0.01346 | 0.016082 | 0.028997 | 0.00060247 | 0.01016 | 0.0030804 | -0.3067 | 0.33875 | -123.0606 | 0.091553 | -122.1909 | -122.7814 | -122.8363 | -0.004578 | 0.31586 | -0.10071 | 0.18768 | 0.27008 | 0.17853 | 0.32044 | -0.23346 | 0.036621 | -0.21057 | 0.63629 | -0.009156 | 0.045776 | 0.2243 | 0.27924 | 122.7264 | 0.013733 | -0.11444 | 123.0972 | 123.1476 | 123.0057 | 0.42114 | 0.27924 | 0.86975 | 123.1522 | 0.37079 | 0.28839 | 123.3994 | 0.41657 | 123.1659 | 123.143 | -123.3627 | -0.40283 | 122.9187 | 123.0148 | 122.5204 | 122.8226
386.2344 | 123.2666 | -122.8592 | 0.31128 | 0.0034333 | 0.0026148 | 0.071508 | 0.065486 | -0.0011771 | -0.0030015 | 0.0017902 | 0.0077514 | 0.016665 | 0.018859 | 0.033483 | 0.00081607 | 0.009519 | -0.00033761 | -0.29755 | 0.29755 | -123.0927 | 0.10071 | -122.1588 | -122.7539 | -122.8271 | 0.036621 | 0.28839 | -0.11444 | 0.21973 | 0.29755 | 0.22888 | 0.33417 | -0.23346 | -0.013733 | -0.21057 | 0.70038 | 0.032044 | 0.10529 | 0.2655 | 0.33875 | 122.7448 | -0.022888 | -0.091552 | 123.1567 | 123.1934 | 123.0881 | 0.44861 | 0.34332 | 0.93384 | 123.1934 | 0.41199 | 0.33417 | 123.3902 | 0.40283 | 123.1567 | 123.1476 | -123.4039 | -0.42572 | 122.9599 | 123.0789 | 122.5616 | 122.8958
387.9844 | 123.2254 | -122.8455 | 0.28381 | 0.0034333 | 0.0041102 | 0.071081 | 0.065913 | 0.0024545 | -0.0025741 | 8.125e-05 | 0.0077514 | 0.01816 | 0.020568 | 0.027075 | 0.00017507 | 0.010587 | -0.0016192 | -0.31128 | 0.31586 | -123.143 | 0.064087 | -122.2046 | -122.8043 | -122.8729 | -0.004578 | 0.27924 | -0.10071 | 0.16479 | 0.24719 | 0.16479 | 0.29297 | -0.29755 | 0.032044 | -0.21973 | 0.64087 | -0.027466 | 0.041199 | 0.27008 | 0.33875 | 122.7448 | -0.004577 | -0.11902 | 123.0927 | 123.1384 | 123.0103 | 0.39368 | 0.2655 | 0.93842 | 123.2071 | 0.3479 | 0.2655 | 123.4589 | 0.37994 | 123.1613 | 123.1247 | -123.4268 | -0.38452 | 122.9095 | 123.0103 | 122.5342 | 122.8409
389.7188 | 123.1384 | -122.8683 | 0.30212 | 0.018692 | 0.0051782 | 0.070867 | 0.066127 | 0.0043771 | -0.0032151 | -0.0012006 | 0.001648 | 0.018587 | 0.018431 | 0.032201 | 0.0010297 | 0.011442 | 0.00073059 | -0.25177 | 0.32501 | -123.1522 | 0 | -122.2824 | -122.8775 | -122.9462 | -0.07782 | 0.32044 | -0.11444 | 0.091553 | 0.13275 | 0.045776 | 0.20599 | -0.28381 | 0.022888 | -0.30212 | 0.58594 | -0.07782 | -0.009155 | 0.20599 | 0.27466 | 122.7539 | 0.018311 | -0.21057 | 123.0011 | 123.0743 | 122.9141 | 0.32044 | 0.16022 | 0.86975 | 123.1522 | 0.24719 | 0.20599 | 123.4772 | 0.43488 | 123.1934 | 123.1888 | -123.4543 | -0.41657 | 122.8683 | 122.9599 | 122.6166 | 122.7905
391.4688 | 123.2254 | -122.8455 | 0.27924 | 0.011063 | 0.0062464 | 0.071935 | 0.065913 | 0.0065133 | -0.0023605 | 0.0030718 | 0.0046998 | 0.017092 | 0.019286 | 0.029638 | 0.00060247 | 0.011655 | 0.0013714 | -0.27924 | 0.30212 | -123.0881 | 0.10529 | -122.1725 | -122.7951 | -122.8592 | 0.15564 | 0.26093 | -0.091553 | 0.16937 | 0.24719 | 0.16937 | 0.28381 | -0.24262 | 0.022888 | -0.17395 | 0.67291 | -0.013733 | 0.050354 | 0.22888 | 0.29297 | 122.7539 | -0.018311 | -0.10986 | 123.0927 | 123.1293 | 123.0148 | 0.37537 | 0.26093 | 0.91553 | 123.1934 | 0.33874 | 0.26093 | 123.3902 | 0.35248 | 123.1476 | 123.1064 | -123.3673 | -0.37079 | 122.9507 | 123.0148 | 122.5662 | 123.0011
393.2188 | 123.143 | -122.8867 | 0.29755 | 0.011063 | 0.0036828 | 0.071722 | 0.063136 | 0.0018137 | -0.0036423 | -0.0022688 | -0.0014038 | 0.018374 | 0.018431 | 0.030279 | -0.0047381 | 0.0088782 | 8.9786e-05 | -0.23804 | 0.31128 | -123.1384 | 0.018311 | -122.2366 | -122.818 | -122.905 | 0.059509 | 0.29297 | -0.12817 | 0.10071 | 0.18768 | 0.07782 | 0.21057 | -0.25177 | 0.013733 | -0.27923 | 0.65002 | -0.01831 | 0.068665 | 0.23346 | 0.32044 | 122.7585 | -0.004577 | -0.19684 | 123.0743 | 123.0972 | 122.9645 | 0.33875 | 0.20599 | 0.9018 | 123.1567 | 0.31586 | 0.22888 | 123.4497 | 0.42114 | 123.1979 | 123.1796 | -123.436 | -0.42572 | 122.905 | 122.9874 | 122.6486 | 122.9462
394.8906 | 123.2758 | -122.8455 | 0.25177 | 0.0034333 | 0.0049646 | 0.070226 | 0.06335 | 0.00031834 | -0.0023605 | -0.00055975 | 0.0077514 | 0.016237 | 0.019713 | 0.026647 | -0.00046573 | 0.0090918 | 8.9786e-05 | -0.2655 | 0.27008 | -123.1064 | 0.10986 | -122.1497 | -122.731 | -122.8043 | 0.21973 | 0.27008 | -0.09613 | 0.21515 | 0.32044 | 0.23804 | 0.32501 | -0.26093 | 0.018311 | -0.14191 | 0.6958 | 0.041199 | 0.11444 | 0.30212 | 0.37537 | 122.7493 | 0.018311 | -0.036621 | 123.1659 | 123.1705 | 123.0835 | 0.42114 | 0.33417 | 0.95673 | 123.2162 | 0.41657 | 0.31128 | 123.3765 | 0.36621 | 123.1155 | 123.1155 | -123.3582 | -0.3479 | 122.9553 | 123.0606 | 122.58 | 123.0652
396.6406 | 123.1705 | -122.8867 | 0.28381 | -0.0041962 | 0.0034692 | 0.070226 | 0.063136 | 0.00031834 | -0.0032151 | -0.0016278 | 0.0046998 | 0.017306 | 0.020354 | 0.021948 | -0.0049517 | 0.0075964 | 0.0028668 | -0.21973 | 0.28839 | -123.1018 | 0.068665 | -122.1817 | -122.7585 | -122.85 | 0.11444 | 0.27466 | -0.11444 | 0.09613 | 0.21057 | 0.11444 | 0.22888 | -0.21515 | 0.004578 | -0.21515 | 0.70496 | 0.036621 | 0.12817 | 0.25177 | 0.34332 | 122.7722 | -0.009155 | -0.18768 | 123.0972 | 123.1155 | 123.0011 | 0.34332 | 0.22888 | 0.9201 | 123.1705 | 0.32501 | 0.21057 | 123.3902 | 0.3891 | 123.175 | 123.1613 | -123.3856 | -0.39825 | 122.9553 | 122.9828 | 122.6669 | 123.0011
398.3906 | 123.2391 | -122.8317 | 0.27466 | -0.0041962 | 0.0026148 | 0.070867 | 0.064418 | 0.0022409 | -0.0019333 | -0.00013235 | 0.001648 | 0.018374 | 0.020354 | 0.027502 | 0.0018841 | 0.0097326 | -0.00055121 | -0.3067 | 0.28839 | -123.1064 | 0.082397 | -122.1817 | -122.7859 | -122.8546 | 0.13733 | 0.27466 | -0.09613 | 0.17853 | 0.27008 | 0.19684 | 0.31128 | -0.27466 | 0.013733 | -0.19226 | 0.65002 | -0.022888 | 0.045776 | 0.25177 | 0.32043 | 122.7356 | 0 | -0.09613 | 123.1018 | 123.143 | 123.0286 | 0.40741 | 0.29297 | 0.92468 | 123.1888 | 0.36621 | 0.27466 | 123.3948 | 0.37079 | 123.1201 | 123.1064 | -123.381 | -0.37079 | 122.9141 | 123.0103 | 122.525 | 122.9691
400.1406 | 123.2529 | -122.8226 | 0.28839 | -0.0041962 | 0.0032556 | 0.069799 | 0.065913 | 0.0030953 | -0.0017197 | 0.00050845 | -0.0014038 | 0.017733 | 0.019286 | 0.02622 | -0.0017475 | 0.0080236 | -0.0016192 | -0.21057 | 0.27924 | -123.0789 | 0.14648 | -122.113 | -122.7036 | -122.7951 | 0.19226 | 0.29297 | -0.09613 | 0.20142 | 0.31128 | 0.23346 | 0.31586 | -0.25635 | -0.009155 | -0.14191 | 0.70953 | 0.027466 | 0.11902 | 0.28381 | 0.37537 | 122.7264 | 0.004578 | -0.086975 | 123.1338 | 123.1384 | 123.056 | 0.41199 | 0.32959 | 0.96588 | 123.2254 | 0.40741 | 0.29755 | 123.3582 | 0.3891 | 123.1018 | 123.1155 | -123.3673 | -0.38452 | 122.9691 | 123.024 | 122.612 | 123.0148
401.8281 | 123.1201 | -122.8729 | 0.32959 | -0.0041962 | 0.0051782 | 0.073004 | 0.068263 | 0.0030953 | -0.0047103 | -0.0018414 | 0.001648 | 0.019228 | 0.020781 | 0.027502 | 0.00081607 | 0.011442 | -0.0016192 | -0.23804 | 0.31586 | -123.0927 | 0.036621 | -122.2549 | -122.8592 | -122.9324 | 0.07782 | 0.31586 | -0.13275 | 0.10529 | 0.16022 | 0.064087 | 0.23346 | -0.21973 | -0.013733 | -0.29297 | 0.61798 | -0.059509 | 0.013733 | 0.16022 | 0.23346 | 122.7402 | -0.013733 | -0.2243 | 123.0331 | 123.1064 | 122.937 | 0.36621 | 0.19684 | 0.83771 | 123.1293 | 0.29297 | 0.23804 | 123.4085 | 0.44861 | 123.1888 | 123.1888 | -123.4222 | -0.46234 | 122.9095 | 122.9782 | 122.6349 | 122.9507
403.5781 | 123.1338 | -122.8683 | 0.29755 | 0.011063 | 0.004751 | 0.067663 | 0.0657 | 0.0043771 | -0.0017197 | -0.00055975 | -0.0014038 | 0.017733 | 0.019286 | 0.026006 | -0.0040973 | 0.006742 | -0.00033761 | -0.27924 | 0.32959 | -123.1476 | -0.013733 | -122.2687 | -122.8455 | -122.9187 | 0.032043 | 0.3067 | -0.14191 | 0.07782 | 0.16022 | 0.086975 | 0.20142 | -0.27924 | 0.032044 | -0.31128 | 0.59967 | -0.050354 | 0.022888 | 0.22888 | 0.30212 | 122.7264 | 0.009156 | -0.21973 | 123.0286 | 123.0698 | 122.9553 | 0.34332 | 0.22888 | 0.87891 | 123.1338 | 0.30212 | 0.21973 | 123.4772 | 0.44861 | 123.1979 | 123.175 | -123.4451 | -0.43945 | 122.8546 | 122.9462 | 122.5891 | 122.9004
405.2656 | 123.1659 | -122.8821 | 0.28839 | 0.0034333 | 0.0060328 | 0.070654 | 0.067622 | 0.00074554 | -0.00022429 | -0.00013235 | 0.0046998 | 0.017519 | 0.02014 | 0.026434 | 0.00060247 | 0.009519 | 0.0035078 | -0.21515 | 0.30212 | -123.0927 | 0.050354 | -122.2183 | -122.8088 | -122.905 | 0.1236 | 0.28839 | -0.10986 | 0.15106 | 0.20599 | 0.10071 | 0.2655 | -0.21057 | 0.013733 | -0.23804 | 0.66376 | -0.022888 | 0.073242 | 0.18768 | 0.28381 | 122.7722 | 0 | -0.13733 | 123.0881 | 123.1476 | 122.9828 | 0.37537 | 0.21057 | 0.87433 | 123.143 | 0.31586 | 0.26093 | 123.3948 | 0.39825 | 123.1842 | 123.1705 | -123.381 | -0.39825 | 122.9324 | 123.0331 | 122.6669 | 123.0057
407.0156 | 123.2391 | -122.8409 | 0.25177 | 0.0034333 | 0.0062464 | 0.072149 | 0.065059 | 0.0043771 | -0.00043789 | 0.00072205 | -0.0044556 | 0.017946 | 0.016509 | 0.030065 | 0.0020979 | 0.010801 | -0.0014056 | -0.26093 | 0.27924 | -123.0698 | 0.09613 | -122.1634 | -122.7768 | -122.8409 | 0.16937 | 0.25177 | -0.07782 | 0.21515 | 0.29755 | 0.1831 | 0.32501 | -0.22888 | 0.027466 | -0.15564 | 0.67749 | 0 | 0.064087 | 0.22888 | 0.29297 | 122.7631 | 0 | -0.036621 | 123.1384 | 123.1659 | 123.024 | 0.40283 | 0.26092 | 0.90637 | 123.1659 | 0.37537 | 0.29297 | 123.349 | 0.32959 | 123.1201 | 123.0927 | -123.3215 | -0.32959 | 122.937 | 123.056 | 122.58 | 123.0103
408.7031 | 123.2574 | -122.8683 | 0.26093 | 0.0034333 | 0.0032556 | 0.069372 | 0.063991 | 0.0045907 | -0.0021469 | 0.00050845 | 0.001648 | 0.01581 | 0.017577 | 0.035619 | -0.00025213 | 0.011228 | -0.00076481 | -0.30212 | 0.27924 | -123.1064 | 0.073242 | -122.1817 | -122.7676 | -122.8317 | 0.14648 | 0.2655 | -0.091553 | 0.17853 | 0.28839 | 0.19226 | 0.31586 | -0.23804 | 0.018311 | -0.18768 | 0.68664 | 0.036621 | 0.10071 | 0.27466 | 0.33875 | 122.7768 | 0.004578 | -0.082397 | 123.1567 | 123.1842 | 123.0606 | 0.40741 | 0.28381 | 0.92468 | 123.1796 | 0.37994 | 0.27008 | 123.3856 | 0.35706 | 123.1476 | 123.1338 | -123.3673 | -0.35248 | 122.9416 | 123.0469 | 122.5662 | 123.0148
410.4531 | 123.1567 | -122.905 | 0.27924 | 0.011063 | 0.0043238 | 0.070226 | 0.067836 | 0.0026681 | -0.0034287 | -0.00077335 | 0.0077514 | 0.019015 | 0.019927 | 0.023229 | -0.00025213 | 0.011228 | 0.0024396 | -0.23346 | 0.31586 | -123.143 | -0.004578 | -122.287 | -122.8455 | -122.9004 | 0.027466 | 0.27924 | -0.10986 | 0.086975 | 0.17853 | 0.086975 | 0.21515 | -0.23804 | 0.036621 | -0.28381 | 0.61798 | 0.004577 | 0.059509 | 0.24261 | 0.29755 | 122.7951 | 0 | -0.19226 | 123.0835 | 123.1201 | 122.9919 | 0.32501 | 0.19684 | 0.85602 | 123.1384 | 0.28839 | 0.19684 | 123.4589 | 0.3891 | 123.2208 | 123.1842 | -123.4222 | -0.3891 | 122.9004 | 122.9919 | 122.6715 | 122.9324
412.2031 | 123.2391 | -122.85 | 0.25635 | 0.018692 | 0.0036828 | 0.071722 | 0.064204 | 0.0030953 | -0.0034287 | -0.00013235 | 0.0046998 | 0.017519 | 0.020781 | 0.026434 | 0.00038887 | 0.0097326 | -0.00012381 | -0.24719 | 0.27924 | -123.0835 | 0.10986 | -122.1268 | -122.7768 | -122.8317 | 0.19226 | 0.26093 | -0.068665 | 0.20599 | 0.27924 | 0.17395 | 0.31586 | -0.23346 | 0.022888 | -0.14649 | 0.72327 | 0.018311 | 0.073243 | 0.25177 | 0.3067 | 122.7814 | 0.004577 | -0.050354 | 123.1293 | 123.1659 | 123.024 | 0.38452 | 0.24261 | 0.95673 | 123.1934 | 0.3479 | 0.27466 | 123.3627 | 0.32959 | 123.1293 | 123.111 | -123.3398 | -0.32501 | 122.9599 | 123.056 | 122.6028 | 123.0423
413.9531 | 123.1522 | -122.8729 | 0.27466 | -0.0041962 | 0.004751 | 0.071081 | 0.068477 | 0.0058725 | -0.0019333 | 0.003499 | 0.001648 | 0.019015 | 0.020781 | 0.022161 | 0.00081607 | 0.0086646 | 0.0011578 | -0.21973 | 0.29297 | -123.1384 | 0.009155 | -122.2595 | -122.85 | -122.9279 | 0.073242 | 0.27008 | -0.12817 | 0.10986 | 0.15106 | 0.068665 | 0.2243 | -0.2655 | 0.018311 | -0.2655 | 0.6134 | -0.054931 | 0.022888 | 0.21057 | 0.28839 | 122.7448 | -0.004577 | -0.1648 | 123.024 | 123.0972 | 122.9416 | 0.35248 | 0.19684 | 0.87891 | 123.1476 | 0.27924 | 0.23804 | 123.4314 | 0.39826 | 123.1659 | 123.143 | -123.4131 | -0.40283 | 122.8821 | 122.9828 | 122.6532 | 122.9462
415.6875 | 123.1155 | -122.8912 | 0.31128 | 0.011063 | 0.0053918 | 0.070654 | 0.066768 | 0.0086495 | -0.00043789 | 0.0017902 | 0.001648 | 0.018374 | 0.021209 | 0.021307 | -0.0015337 | 0.011442 | 0.0026532 | -0.23346 | 0.30212 | -123.1201 | 0 | -122.2687 | -122.8867 | -122.9416 | 0.036621 | 0.29755 | -0.10986 | 0.086975 | 0.15564 | 0.036621 | 0.19684 | -0.22888 | -0.009155 | -0.31128 | 0.62256 | -0.050354 | 0.004577 | 0.17853 | 0.23346 | 122.7814 | -0.013733 | -0.2243 | 123.0469 | 123.0881 | 122.9279 | 0.3067 | 0.14648 | 0.85144 | 123.1201 | 0.2655 | 0.19684 | 123.4222 | 0.40741 | 123.1934 | 123.1888 | -123.4314 | -0.42114 | 122.8912 | 122.9782 | 122.6578 | 122.9279
417.375 | 123.2162 | -122.8775 | 0.23804 | 0.011063 | 0.0034692 | 0.070013 | 0.064418 | 0.0033089 | -0.0017197 | 8.125e-05 | 0.0046998 | 0.016665 | 0.019286 | 0.028784 | -3.8532e-05 | 0.011228 | 0.0017988 | -0.31586 | 0.25635 | -123.1247 | 0.018311 | -122.2183 | -122.8317 | -122.8775 | 0.091553 | 0.24719 | -0.086975 | 0.13733 | 0.24261 | 0.16022 | 0.27008 | -0.24719 | 0.018311 | -0.21973 | 0.65918 | 0 | 0.045776 | 0.24719 | 0.29297 | 122.7905 | 0.009155 | -0.10071 | 123.1201 | 123.1476 | 123.0377 | 0.35706 | 0.24719 | 0.90637 | 123.143 | 0.32959 | 0.2243 | 123.381 | 0.33417 | 123.1339 | 123.1247 | -123.3627 | -0.32501 | 122.8958 | 123.0148 | 122.5616 | 122.9691
419.1094 | 123.2346 | -122.8821 | 0.23804 | 0.026321 | 0.004751 | 0.069799 | 0.063991 | 0.0043771 | -0.0017197 | -0.0031232 | 0.001648 | 0.016878 | 0.018859 | 0.034124 | 0.0025251 | 0.010374 | 0.00073059 | -0.2655 | 0.25177 | -123.1064 | 0.091553 | -122.1725 | -122.7768 | -122.8638 | 0.16937 | 0.22888 | -0.10529 | 0.17395 | 0.25635 | 0.16022 | 0.27008 | -0.2243 | 0.013733 | -0.14648 | 0.70953 | 0.01831 | 0.10529 | 0.24261 | 0.32959 | 122.7768 | -0.009155 | -0.064087 | 123.1384 | 123.1522 | 123.0423 | 0.37537 | 0.2655 | 0.93384 | 123.1979 | 0.36163 | 0.27924 | 123.3582 | 0.33417 | 123.1338 | 123.111 | -123.3444 | -0.34332 | 122.9736 | 123.056 | 122.6166 | 123.0515
420.7812 | 123.2025 | -122.8821 | 0.2243 | 0.026321 | 0.00646 | 0.071081 | 0.063991 | 0.0054453 | -0.0015061 | -0.0012006 | 0.0046998 | 0.017946 | 0.019713 | 0.028997 | 0.0012433 | 0.0088782 | 0.0024396 | -0.29297 | 0.25635 | -123.111 | 0.036621 | -122.2092 | -122.8134 | -122.8821 | 0.10529 | 0.24261 | -0.09613 | 0.11444 | 0.20142 | 0.11902 | 0.24719 | -0.22888 | 0.032044 | -0.18768 | 0.67291 | 0 | 0.068664 | 0.22888 | 0.29755 | 122.7859 | 0.018311 | -0.10986 | 123.0835 | 123.1293 | 123.0011 | 0.34332 | 0.21515 | 0.9018 | 123.1476 | 0.29755 | 0.21057 | 123.3673 | 0.33874 | 123.1384 | 123.1247 | -123.3353 | -0.32043 | 122.9187 | 122.9965 | 122.5891 | 122.9874
422.5156 | 123.1247 | -122.9233 | 0.26093 | 0.0034333 | 0.0051782 | 0.070013 | 0.0657 | 0.00095914 | -0.0044967 | 0.00029485 | -0.0014038 | 0.016878 | 0.019713 | 0.021948 | -0.0017475 | 0.006101 | 0.0011578 | -0.21973 | 0.24719 | -123.1201 | 0.009155 | -122.2321 | -122.8088 | -122.9004 | 0.036621 | 0.26093 | -0.11444 | 0.050354 | 0.13733 | 0.073242 | 0.17853 | -0.19684 | -0.013733 | -0.25177 | 0.69122 | 0.022888 | 0.11444 | 0.21973 | 0.31128 | 122.8088 | 0 | -0.21057 | 123.0606 | 123.1018 | 122.9965 | 0.29297 | 0.18768 | 0.88806 | 123.1293 | 0.25177 | 0.16479 | 123.3673 | 0.37537 | 123.1705 | 123.1842 | -123.381 | -0.37537 | 122.9324 | 122.9736 | 122.7036 | 122.9599
424.25 | 123.1934 | -122.9095 | 0.23346 | 0.011063 | 0.0032556 | 0.070013 | 0.065273 | 0.0018137 | -0.0017197 | -0.0029096 | 0.001648 | 0.017092 | 0.019072 | 0.028997 | -0.0013201 | 0.0073828 | 0.0026532 | -0.2243 | 0.23346 | -123.1476 | 0.064087 | -122.1909 | -122.7768 | -122.8683 | 0.07782 | 0.21515 | -0.041199 | 0.086975 | 0.18768 | 0.10986 | 0.21973 | -0.23804 | 0 | -0.16937 | 0.71869 | 0.041199 | 0.13275 | 0.27924 | 0.37079 | 122.8683 | -0.01831 | -0.14648 | 123.0972 | 123.1293 | 123.0194 | 0.26093 | 0.15106 | 0.95673 | 123.2117 | 0.22888 | 0.12817 | 123.381 | 0.25635 | 123.143 | 123.1247 | -123.381 | -0.27466 | 122.9736 | 122.9965 | 122.6852 | 122.9874
425.9844 | 123.1705 | -122.9233 | 0.24261 | 0.018692 | 0.0038966 | 0.07044 | 0.064632 | 0.0022409 | -0.0027877 | -0.00098695 | 0.001648 | 0.02051 | 0.02014 | 0.025366 | -0.0019611 | 0.0088782 | 8.9786e-05 | -0.19684 | 0.26093 | -123.1705 | 0 | -122.2504 | -122.8317 | -122.9279 | 0.064087 | 0.24719 | -0.059509 | 0.091553 | 0.16479 | 0.059509 | 0.19684 | -0.24719 | 0.01831 | -0.24261 | 0.67291 | -0.004577 | 0.091553 | 0.24262 | 0.33875 | 122.8638 | 0.004577 | -0.15106 | 123.0881 | 123.1201 | 122.9828 | 0.25635 | 0.11902 | 0.92011 | 123.1705 | 0.2243 | 0.15106 | 123.4314 | 0.3067 | 123.1842 | 123.1705 | -123.4131 | -0.30212 | 122.9233 | 123.0148 | 122.7264 | 122.9874
427.6719 | 123.1567 | -122.9416 | 0.24261 | 0.018692 | 0.0073144 | 0.069158 | 0.0657 | 0.0039499 | -0.0032151 | -0.0014142 | 0.010803 | 0.01816 | 0.022277 | 0.027715 | 0.0010297 | 0.0071692 | -0.0018328 | -0.2243 | 0.26093 | -123.2117 | -0.054932 | -122.2961 | -122.8592 | -122.9324 | 0 | 0.25177 | -0.073242 | 0.07782 | 0.14648 | 0.050354 | 0.20599 | -0.27008 | 0.01831 | -0.29755 | 0.64545 | 0.009155 | 0.082397 | 0.27924 | 0.35248 | 122.8683 | 0.009155 | -0.16479 | 123.0881 | 123.1476 | 122.9919 | 0.27924 | 0.1236 | 0.91553 | 123.1567 | 0.21973 | 0.15106 | 123.4726 | 0.32501 | 123.2025 | 123.1934 | -123.4543 | -0.31586 | 122.8867 | 123.0194 | 122.7173 | 122.9416
429.4062 | 123.2025 | -122.8958 | 0.23804 | 0.0034333 | 0.0041102 | 0.070867 | 0.063777 | 0.0077951 | -0.0030015 | -0.0039778 | -0.0014038 | 0.014956 | 0.021636 | 0.031988 | -0.0011065 | 0.0073828 | 0.0035078 | -0.22888 | 0.24719 | -123.1247 | 0.059509 | -122.1634 | -122.7722 | -122.85 | 0.1236 | 0.21973 | -0.041199 | 0.10986 | 0.21973 | 0.14191 | 0.24719 | -0.22888 | 0.009155 | -0.17853 | 0.73242 | 0.045776 | 0.1236 | 0.27466 | 0.35248 | 122.8546 | -0.01831 | -0.12817 | 123.1155 | 123.143 | 123.0377 | 0.28839 | 0.18311 | 0.9613 | 123.1842 | 0.26093 | 0.15106 | 123.3719 | 0.26093 | 123.143 | 123.1155 | -123.3627 | -0.27924 | 122.9553 | 123.0057 | 122.6669 | 123.0194
431.1562 | 123.262 | -122.8775 | 0.2243 | 0.011063 | 0.0049646 | 0.068945 | 0.064418 | 0.0035227 | -0.0062057 | -0.00077335 | 0.0046998 | 0.015597 | 0.018645 | 0.031774 | 0.00081607 | 0.0073828 | -0.0018328 | -0.24261 | 0.23346 | -123.1155 | 0.10529 | -122.1176 | -122.7402 | -122.818 | 0.16937 | 0.23804 | -0.022888 | 0.17395 | 0.27924 | 0.19226 | 0.27466 | -0.23804 | 0.009155 | -0.11902 | 0.75989 | 0.059509 | 0.13733 | 0.29755 | 0.37537 | 122.8546 | 0.013733 | -0.050354 | 123.1567 | 123.1522 | 123.0698 | 0.29755 | 0.21515 | 0.99792 | 123.2208 | 0.30212 | 0.19684 | 123.349 | 0.26093 | 123.111 | 123.1155 | -123.3398 | -0.24719 | 122.9828 | 123.0515 | 122.6349 | 123.0469
432.8438 | 123.2758 | -122.8729 | 0.21973 | 0.0034333 | 0.0028284 | 0.067877 | 0.064845 | 0.0071541 | -0.0021469 | -0.0016278 | -0.0044556 | 0.016024 | 0.022063 | 0.024725 | -0.0013201 | 0.0097326 | -0.0016192 | -0.24719 | 0.23804 | -123.111 | 0.064087 | -122.1771 | -122.731 | -122.8271 | 0.1831 | 0.21057 | -0.036621 | 0.17395 | 0.28839 | 0.20142 | 0.29297 | -0.23804 | 0.01831 | -0.15564 | 0.6958 | 0.045777 | 0.14191 | 0.28381 | 0.37994 | 122.8363 | -0.009156 | -0.045777 | 123.1613 | 123.1659 | 123.0743 | 0.32959 | 0.23804 | 0.93384 | 123.175 | 0.32501 | 0.21057 | 123.349 | 0.24719 | 123.111 | 123.0835 | -123.3307 | -0.25635 | 122.937 | 123.0469 | 122.6257 | 123.056
434.5781 | 123.2437 | -122.8546 | 0.22888 | 0.011063 | 0.0049646 | 0.069799 | 0.064632 | 0.0020273 | -0.0021469 | 0.00072205 | -0.0014038 | 0.017092 | 0.020354 | 0.032201 | -0.0011065 | 0.010374 | 8.9786e-05 | -0.28839 | 0.25177 | -123.1201 | 0.041199 | -122.2092 | -122.7722 | -122.8455 | 0.11902 | 0.20142 | -0.036621 | 0.15564 | 0.24261 | 0.17395 | 0.27924 | -0.2655 | 0.022888 | -0.18768 | 0.64545 | 0.009155 | 0.082397 | 0.27466 | 0.3479 | 122.818 | -0.027466 | -0.073242 | 123.0972 | 123.1338 | 123.0286 | 0.31586 | 0.21057 | 0.91095 | 123.1613 | 0.27924 | 0.19226 | 123.3719 | 0.23804 | 123.1064 | 123.056 | -123.349 | -0.2655 | 122.8958 | 123.0103 | 122.5662 | 122.9736
436.3125 | 123.2483 | -122.85 | 0.21973 | 0.011063 | 0.0066736 | 0.071081 | 0.065913 | 0.0041635 | -0.0012925 | -0.0016278 | 0.0077514 | 0.018374 | 0.020568 | 0.032201 | 0.0031659 | 0.011655 | 0.0026532 | -0.24261 | 0.25177 | -123.0743 | 0.09613 | -122.1634 | -122.7722 | -122.8455 | 0.15564 | 0.22888 | -0.036621 | 0.17853 | 0.24261 | 0.16022 | 0.27466 | -0.2243 | 0.032043 | -0.1236 | 0.68665 | 0.004578 | 0.07782 | 0.22888 | 0.30212 | 122.8134 | 0.009155 | -0.041199 | 123.0927 | 123.1247 | 123.0103 | 0.31128 | 0.19684 | 0.91095 | 123.1705 | 0.27924 | 0.21515 | 123.3261 | 0.2655 | 123.1018 | 123.0789 | -123.2941 | -0.25635 | 122.9462 | 123.0286 | 122.6074 | 123.0057
438.0625 | 123.1567 | -122.8867 | 0.24261 | 0.011063 | 0.0062464 | 0.070654 | 0.069118 | 0.0056589 | -0.0025741 | 8.125e-05 | 0.0046998 | 0.019442 | 0.022704 | 0.021307 | -0.00067933 | 0.0088782 | -0.00097841 | -0.21057 | 0.28839 | -123.1567 | 0 | -122.2778 | -122.8409 | -122.905 | 0.032043 | 0.26093 | -0.064087 | 0.07782 | 0.17853 | 0.086975 | 0.21515 | -0.27008 | 0.045776 | -0.24261 | 0.60883 | -0.01831 | 0.045777 | 0.25177 | 0.31586 | 122.8226 | 0.01831 | -0.16479 | 123.0652 | 123.1018 | 122.9736 | 0.27924 | 0.15106 | 0.87891 | 123.1567 | 0.24261 | 0.14191 | 123.4451 | 0.32501 | 123.175 | 123.1476 | -123.3994 | -0.3067 | 122.8867 | 122.9645 | 122.6761 | 122.9187
439.75 | 123.1018 | -122.905 | 0.2655 | 0.0034333 | 0.004751 | 0.071295 | 0.06805 | 0.0050179 | -0.0012925 | 0.0011492 | 0.001648 | 0.019655 | 0.020995 | 0.024084 | 0.00060247 | 0.0073828 | -0.00097841 | -0.28381 | 0.27924 | -123.143 | -0.036621 | -122.3511 | -122.9141 | -122.9782 | -0.041199 | 0.26093 | -0.064087 | 0.050354 | 0.091553 | 0 | 0.1831 | -0.23804 | 0.013733 | -0.30212 | 0.55389 | -0.073242 | -0.009156 | 0.16479 | 0.22888 | 122.8409 | -0.004578 | -0.21515 | 122.9965 | 123.0881 | 122.905 | 0.24719 | 0.064087 | 0.79193 | 123.1064 | 0.15564 | 0.11444 | 123.4222 | 0.32501 | 123.1842 | 123.1659 | -123.4085 | -0.32959 | 122.8683 | 122.9553 | 122.6212 | 122.8638
441.4844 | 123.1567 | -122.905 | 0.25635 | 0.018692 | 0.0036828 | 0.069158 | 0.065059 | 0.0062997 | 0.00020291 | 0.0013628 | 0.0046998 | 0.016237 | 0.021209 | 0.021734 | -0.00067933 | 0.0088782 | 0.0045758 | -0.24261 | 0.30212 | -123.1659 | -0.022888 | -122.2824 | -122.8363 | -122.9095 | 0.027466 | 0.25177 | -0.050354 | 0.082397 | 0.16479 | 0.068665 | 0.20142 | -0.26093 | 0.045776 | -0.27924 | 0.62256 | -0.004578 | 0.068664 | 0.25635 | 0.32959 | 122.8546 | -0.004578 | -0.17395 | 123.0698 | 123.1064 | 122.9736 | 0.25177 | 0.11902 | 0.88348 | 123.143 | 0.21515 | 0.13275 | 123.468 | 0.30212 | 123.2071 | 123.1567 | -123.4222 | -0.3067 | 122.8821 | 122.9874 | 122.6624 | 122.9324
443.2344 | 123.1338 | -122.8958 | 0.24719 | 0.011063 | 0.0036828 | 0.069586 | 0.066341 | 0.0043771 | -0.0010789 | 8.125e-05 | 0.001648 | 0.018587 | 0.020995 | 0.027502 | 0.0012433 | 0.008451 | 0.0011578 | -0.3067 | 0.28839 | -123.1522 | -0.064087 | -122.3053 | -122.8958 | -122.9507 | -0.009155 | 0.23346 | -0.045776 | 0.082397 | 0.14191 | 0.027466 | 0.20142 | -0.25635 | 0.041199 | -0.31128 | 0.59052 | -0.054932 | 0 | 0.20142 | 0.25635 | 122.85 | -0.013733 | -0.16479 | 123.0377 | 123.0972 | 122.9233 | 0.24719 | 0.073242 | 0.84686 | 123.0881 | 0.18768 | 0.12817 | 123.4406 | 0.27924 | 123.1842 | 123.1293 | -123.3994 | -0.29297 | 122.8317 | 122.9782 | 122.5891 | 122.8867
444.9844 | 123.143 | -122.9095 | 0.26093 | 0.011063 | 0.0058192 | 0.070226 | 0.066768 | 0.0045907 | -0.00065149 | -0.00077335 | 0.010803 | 0.015383 | 0.021209 | 0.028143 | -0.0028155 | 0.0086646 | 0.0011578 | -0.25177 | 0.30212 | -123.1613 | -0.041199 | -122.2824 | -122.8363 | -122.9279 | 0.009155 | 0.27924 | -0.064087 | 0.059509 | 0.16479 | 0.054932 | 0.1831 | -0.25177 | 0.041199 | -0.30212 | 0.62714 | -0.01831 | 0.073242 | 0.23346 | 0.32501 | 122.8455 | 0.018311 | -0.20142 | 123.0743 | 123.0927 | 122.9645 | 0.24719 | 0.11902 | 0.87891 | 123.1201 | 0.22888 | 0.1236 | 123.4634 | 0.34332 | 123.2117 | 123.1888 | -123.4222 | -0.32501 | 122.8683 | 122.9691 | 122.6578 | 122.9187
446.6719 | 123.1796 | -122.8729 | 0.20599 | 0.018692 | 0.0045374 | 0.070013 | 0.063136 | 0.0015999 | -0.0021469 | -0.00013235 | 0.0077514 | 0.017092 | 0.020568 | 0.035192 | 0.0018841 | 0.010587 | -0.0033282 | -0.26093 | 0.23804 | -123.0972 | 0.082397 | -122.1542 | -122.7768 | -122.818 | 0.16022 | 0.23346 | -0.022888 | 0.18768 | 0.23804 | 0.15564 | 0.27008 | -0.2243 | 0.032043 | -0.1236 | 0.71869 | 0.054932 | 0.096131 | 0.27924 | 0.32044 | 122.85 | 0.027465 | -0.018311 | 123.111 | 123.143 | 123.0286 | 0.29297 | 0.17853 | 0.94299 | 123.1796 | 0.26093 | 0.21057 | 123.3353 | 0.25635 | 123.111 | 123.1064 | -123.3032 | -0.22888 | 122.9553 | 123.0606 | 122.612 | 123.0331
448.4062 | 123.2208 | -122.8683 | 0.21973 | 0.011063 | 0.0049646 | 0.070654 | 0.065486 | 0.0065133 | -0.0015061 | 0.0013628 | 0.0046998 | 0.017092 | 0.020781 | 0.031133 | 0.0042341 | 0.0097326 | 0.00051699 | -0.24261 | 0.23346 | -123.0972 | 0.082397 | -122.1405 | -122.7631 | -122.8317 | 0.17395 | 0.21973 | -0.032043 | 0.19226 | 0.25635 | 0.15564 | 0.27924 | -0.22888 | 0.013732 | -0.13733 | 0.72784 | 0.036621 | 0.10528 | 0.2655 | 0.33417 | 122.8363 | 0 | -0.027466 | 123.1247 | 123.1476 | 123.024 | 0.31128 | 0.18768 | 0.95673 | 123.1796 | 0.28839 | 0.2243 | 123.3307 | 0.25177 | 123.1018 | 123.0881 | -123.317 | -0.25177 | 122.9507 | 123.0606 | 122.6257 | 123.0423
450.1562 | 123.2391 | -122.8592 | 0.25177 | 0.0034333 | 0.0028284 | 0.070654 | 0.063564 | 0.0041635 | -0.0040695 | -0.0029096 | -0.0014038 | 0.014101 | 0.018645 | 0.030706 | -0.00025213 | 0.0093054 | 0.0020124 | -0.3067 | 0.25177 | -123.1293 | 0.027466 | -122.1863 | -122.7676 | -122.8409 | 0.12817 | 0.22888 | -0.022888 | 0.15564 | 0.25635 | 0.17853 | 0.27924 | -0.27008 | 0 | -0.2243 | 0.67291 | 0.018311 | 0.091553 | 0.28839 | 0.36163 | 122.8363 | -0.022888 | -0.09613 | 123.1155 | 123.1384 | 123.0377 | 0.30212 | 0.20142 | 0.94299 | 123.1567 | 0.27924 | 0.17853 | 123.381 | 0.25177 | 123.111 | 123.0881 | -123.381 | -0.27466 | 122.8867 | 123.0148 | 122.5525 | 122.9874
451.8438 | 123.2346 | -122.8592 | 0.24261 | 0.011063 | 0.0026148 | 0.070654 | 0.066127 | 0.0030953 | -0.0010789 | -0.00013235 | 0.001648 | 0.015169 | 0.020568 | 0.03092 | 0.0027387 | 0.0090918 | -0.00076481 | -0.22888 | 0.25177 | -123.0972 | 0.10071 | -122.1359 | -122.7676 | -122.8226 | 0.1831 | 0.21973 | -0.018311 | 0.18768 | 0.27466 | 0.17395 | 0.28381 | -0.23804 | 0.009155 | -0.14191 | 0.72327 | 0.036621 | 0.091553 | 0.27466 | 0.32959 | 122.8409 | -0.022888 | -0.054932 | 123.1338 | 123.143 | 123.0331 | 0.30212 | 0.19226 | 0.9613 | 123.1979 | 0.29297 | 0.20599 | 123.349 | 0.23804 | 123.111 | 123.0789 | -123.3398 | -0.26093 | 122.9599 | 123.0469 | 122.6303 | 123.0423
453.5781 | 123.0972 | -122.9141 | 0.25635 | -0.0041962 | 0.0026148 | 0.070226 | 0.061641 | 0.00095914 | -0.0025741 | 0.00050845 | 0.0046998 | 0.016878 | 0.020354 | 0.036047 | -0.0045245 | 0.009519 | 0.003294 | -0.27924 | 0.28381 | -123.1659 | -0.045776 | -122.2641 | -122.8317 | -122.905 | 0 | 0.27924 | -0.059509 | 0.045776 | 0.12817 | 0.045776 | 0.18768 | -0.25177 | 0.027465 | -0.30212 | 0.65002 | 0.009156 | 0.082398 | 0.26093 | 0.33417 | 122.8546 | 0.022888 | -0.21057 | 123.0423 | 123.1018 | 122.9599 | 0.24719 | 0.10528 | 0.90179 | 123.1201 | 0.18768 | 0.10528 | 123.4497 | 0.33874 | 123.1979 | 123.1934 | -123.4222 | -0.31586 | 122.8683 | 122.9599 | 122.6349 | 122.9141
455.3281 | 123.2071 | -122.8363 | 0.23804 | 0.011063 | 0.004751 | 0.072149 | 0.064632 | 0.0043771 | -0.0030015 | -0.0014142 | 0.0046998 | 0.016451 | 0.018431 | 0.027929 | -0.0017475 | 0.0069556 | -0.0048236 | -0.2243 | 0.26093 | -123.1155 | 0.10071 | -122.1359 | -122.7173 | -122.8088 | 0.15106 | 0.22888 | -0.027466 | 0.16022 | 0.26093 | 0.17853 | 0.27466 | -0.27924 | 0.022888 | -0.13733 | 0.70038 | 0.027466 | 0.11902 | 0.3067 | 0.39825 | 122.8088 | -0.009155 | -0.07782 | 123.0972 | 123.111 | 123.0148 | 0.30212 | 0.20599 | 0.97961 | 123.2162 | 0.28839 | 0.18768 | 123.3765 | 0.25635 | 123.0972 | 123.0652 | -123.3536 | -0.2655 | 122.937 | 122.9965 | 122.612 | 122.9874
457.0625 | 123.2391 | -122.8409 | 0.23346 | 0.018692 | 0.0038966 | 0.070226 | 0.064845 | 0.0028817 | -0.0032151 | -0.0016278 | 0.0077514 | 0.016451 | 0.02014 | 0.027502 | -0.00046573 | 0.0086646 | -0.00055121 | -0.24261 | 0.23346 | -123.0881 | 0.07782 | -122.0947 | -122.699 | -122.7951 | 0.1831 | 0.22888 | -0.013733 | 0.17853 | 0.28839 | 0.20599 | 0.28839 | -0.24719 | 0 | -0.15564 | 0.74615 | 0.045776 | 0.14191 | 0.29297 | 0.3891 | 122.8271 | -0.004577 | -0.054931 | 123.1293 | 123.1293 | 123.0469 | 0.30212 | 0.21973 | 0.99335 | 123.1659 | 0.30212 | 0.19226 | 123.3215 | 0.24261 | 123.0743 | 123.0698 | -123.3215 | -0.24719 | 122.9187 | 123.0194 | 122.5983 | 123.024
458.7344 | 123.1476 | -122.8821 | 0.27008 | 0.018692 | 0.0024012 | 0.068945 | 0.067195 | 0.0052315 | -0.0019333 | -0.00034615 | 0.0046998 | 0.016665 | 0.021422 | 0.017248 | -0.0013201 | 0.009519 | -0.0026874 | -0.24719 | 0.29755 | -123.1613 | -0.036621 | -122.2778 | -122.8271 | -122.8867 | 0 | 0.28381 | -0.059509 | 0.064087 | 0.15564 | 0.07782 | 0.21057 | -0.27924 | 0.027465 | -0.3067 | 0.60425 | -0.004578 | 0.054932 | 0.27466 | 0.33417 | 122.8226 | 0.013732 | -0.20599 | 123.0377 | 123.0927 | 122.9599 | 0.27008 | 0.13733 | 0.88348 | 123.1247 | 0.21515 | 0.1236 | 123.4589 | 0.34332 | 123.1796 | 123.1659 | -123.4314 | -0.32959 | 122.8455 | 122.9462 | 122.6349 | 122.8821
460.5 | 123.2025 | -122.8455 | 0.25635 | 0.0034333 | 0.0026148 | 0.071508 | 0.062282 | 0.0039499 | -0.0034287 | 0.0017902 | 0.001648 | 0.015597 | 0.019927 | 0.024725 | 0.0014569 | 0.010801 | 0.003935 | -0.3067 | 0.27924 | -123.0972 | 0.036621 | -122.1909 | -122.7859 | -122.8409 | 0.10071 | 0.23346 | -0.032043 | 0.16022 | 0.24719 | 0.15564 | 0.27466 | -0.25177 | 0.022888 | -0.21973 | 0.6546 | 0.004578 | 0.059509 | 0.25635 | 0.31128 | 122.8134 | -0.022889 | -0.096131 | 123.0927 | 123.1201 | 123.0011 | 0.3067 | 0.18768 | 0.90637 | 123.1338 | 0.27924 | 0.19226 | 123.3765 | 0.2655 | 123.1247 | 123.0789 | -123.3536 | -0.28839 | 122.8821 | 123.0057 | 122.5388 | 122.9462
462.1719 | 123.1155 | -122.8775 | 0.26093 | 0.011063 | 0.0053918 | 0.069586 | 0.067622 | 0.0026681 | -0.0017197 | -0.0012006 | 0.0046998 | 0.020083 | 0.020781 | 0.029424 | 0.0018841 | 0.009519 | -0.0014056 | -0.29297 | 0.3067 | -123.1522 | -0.032043 | -122.2916 | -122.8821 | -122.9279 | 0.022888 | 0.26093 | -0.041199 | 0.086975 | 0.14191 | 0.036621 | 0.20142 | -0.27466 | 0.045777 | -0.29297 | 0.58594 | -0.050354 | -0.004578 | 0.22431 | 0.27008 | 122.8363 | 0 | -0.17395 | 123.0194 | 123.0789 | 122.9141 | 0.24262 | 0.07782 | 0.8606 | 123.1201 | 0.18311 | 0.12817 | 123.4589 | 0.30212 | 123.1842 | 123.1384 | -123.4131 | -0.30212 | 122.8455 | 122.9645 | 122.5845 | 122.9004
463.9062 | 123.2162 | -122.8363 | 0.2243 | 0.011063 | 0.0036828 | 0.071295 | 0.066982 | 0.0088631 | -0.0023605 | -0.003764 | 0.0046998 | 0.014956 | 0.018859 | 0.027502 | 0.0035931 | 0.0086646 | 0.0028668 | -0.26093 | 0.26093 | -123.1018 | 0.073242 | -122.1542 | -122.7859 | -122.8409 | 0.16022 | 0.23346 | 0 | 0.21515 | 0.25177 | 0.15106 | 0.30212 | -0.2655 | 0.036621 | -0.15106 | 0.68207 | -0.004577 | 0.050354 | 0.26093 | 0.31586 | 122.8363 | 0.009155 | -0.009155 | 123.0881 | 123.1384 | 122.9874 | 0.30212 | 0.15106 | 0.94757 | 123.175 | 0.25177 | 0.21515 | 123.3627 | 0.23346 | 123.0972 | 123.0698 | -123.3261 | -0.2243 | 122.9095 | 123.0515 | 122.5754 | 122.9965
465.6562 | 123.1979 | -122.8409 | 0.23346 | -0.0041962 | 0.0041102 | 0.070226 | 0.066982 | 0.0035227 | -0.0012925 | 0.00072205 | 0.001648 | 0.016451 | 0.020354 | 0.024297 | 0.0029523 | 0.011655 | 8.9786e-05 | -0.24719 | 0.23346 | -123.0698 | 0.10529 | -122.1359 | -122.7539 | -122.818 | 0.17395 | 0.23804 | -0.013733 | 0.19226 | 0.26093 | 0.16937 | 0.28839 | -0.22888 | 0 | -0.12817 | 0.70496 | 0.022888 | 0.086975 | 0.25177 | 0.31586 | 122.8271 | 0.004578 | -0.041198 | 123.1018 | 123.1293 | 123.0103 | 0.30212 | 0.18311 | 0.93384 | 123.175 | 0.27466 | 0.20599 | 123.3032 | 0.25177 | 123.0743 | 123.0789 | -123.3032 | -0.24719 | 122.9462 | 123.0331 | 122.5937 | 123.0148
467.3906 | 123.1979 | -122.8683 | 0.24261 | 0.011063 | 0.0060328 | 0.071935 | 0.064418 | 0.0041635 | -0.0017197 | 0.003499 | 0.0046998 | 0.016878 | 0.021209 | 0.03092 | 0.00060247 | 0.0090918 | 0.00073059 | -0.25177 | 0.22888 | -123.0881 | 0.09613 | -122.1176 | -122.731 | -122.8088 | 0.16479 | 0.23346 | -0.013733 | 0.19684 | 0.25635 | 0.16022 | 0.28381 | -0.21973 | -0.013733 | -0.14649 | 0.75073 | 0.059509 | 0.13733 | 0.27924 | 0.35706 | 122.8546 | -0.009156 | -0.045777 | 123.1247 | 123.1522 | 123.0286 | 0.29755 | 0.17395 | 0.97046 | 123.1842 | 0.27008 | 0.21057 | 123.317 | 0.24719 | 123.0972 | 123.1018 | -123.3307 | -0.25635 | 122.9645 | 123.0652 | 122.6166 | 123.0331
469.125 | 123.2117 | -122.8226 | 0.24261 | 0.011063 | 0.0041102 | 0.068304 | 0.066768 | 0.0048043 | -0.0012925 | 0.0015764 | 0.0046998 | 0.017306 | 0.018859 | 0.02622 | 0.00060247 | 0.0090918 | -0.0031146 | -0.28839 | 0.27924 | -123.1201 | 0.064087 | -122.1725 | -122.7768 | -122.85 | 0.13275 | 0.23804 | -0.013733 | 0.20142 | 0.26093 | 0.15106 | 0.29755 | -0.29755 | 0.036621 | -0.17853 | 0.65002 | -0.027466 | 0.045777 | 0.27008 | 0.34332 | 122.8088 | -0.004578 | -0.041199 | 123.0835 | 123.1201 | 122.9736 | 0.31128 | 0.16479 | 0.94757 | 123.1842 | 0.27466 | 0.21515 | 123.3994 | 0.25177 | 123.1018 | 123.0606 | -123.3627 | -0.25635 | 122.8867 | 123.024 | 122.5342 | 122.9553
470.7969 | 123.1155 | -122.8546 | 0.26093 | 0.011063 | 0.0062464 | 0.070013 | 0.067622 | 0.0041635 | -0.00043789 | -0.0022688 | 0.0046998 | 0.017946 | 0.021636 | 0.022375 | -0.0021747 | 0.0093054 | 0.0017988 | -0.28839 | 0.31586 | -123.1201 | -0.041199 | -122.2687 | -122.8729 | -122.9324 | 0.018311 | 0.27924 | -0.032043 | 0.07782 | 0.13275 | 0.036621 | 0.21057 | -0.2655 | 0.054932 | -0.30212 | 0.58594 | -0.07782 | -0.018311 | 0.18768 | 0.24719 | 122.8226 | 0.018311 | -0.18311 | 122.9874 | 123.0652 | 122.8912 | 0.24261 | 0.068664 | 0.85144 | 123.0789 | 0.16479 | 0.10986 | 123.436 | 0.31128 | 123.1705 | 123.1338 | -123.381 | -0.29297 | 122.8134 | 122.9324 | 122.5662 | 122.8729
472.5469 | 123.1064 | -122.8317 | 0.27924 | 0.0034333 | 0.0036828 | 0.06809 | 0.062068 | 0.0035227 | -0.0021469 | 0.00050845 | 0.001648 | 0.017519 | 0.018859 | 0.031133 | -0.0032427 | 0.0097326 | -0.0024738 | -0.23346 | 0.28381 | -123.0743 | 0.045776 | -122.1542 | -122.7402 | -122.8271 | 0.073242 | 0.29297 | -0.004578 | 0.091553 | 0.18768 | 0.10529 | 0.21973 | -0.24262 | 0.004577 | -0.23346 | 0.67749 | 0.004578 | 0.091553 | 0.24719 | 0.33417 | 122.8271 | 0.013733 | -0.18768 | 123.0194 | 123.0515 | 122.937 | 0.22431 | 0.10986 | 0.92011 | 123.1201 | 0.19226 | 0.096131 | 123.3582 | 0.29755 | 123.1155 | 123.1247 | -123.3536 | -0.28381 | 122.8775 | 122.9233 | 122.5983 | 122.905
474.2188 | 123.0881 | -122.8226 | 0.29755 | 0.0034333 | 0.0058192 | 0.071508 | 0.066554 | 0.0071541 | 0.00084391 | 0.00093565 | 0.0077514 | 0.016878 | 0.022277 | 0.031347 | -0.00046573 | 0.0099462 | 0.001585 | -0.25635 | 0.32501 | -123.0743 | 0.027466 | -122.2092 | -122.8317 | -122.8821 | 0.059509 | 0.30212 | -0.013733 | 0.09613 | 0.16022 | 0.064087 | 0.21057 | -0.25177 | 0.027466 | -0.27008 | 0.6134 | -0.059509 | -0.009155 | 0.19226 | 0.24262 | 122.8088 | 0.004578 | -0.20142 | 122.9828 | 123.0331 | 122.8867 | 0.2243 | 0.07782 | 0.86517 | 123.1018 | 0.17395 | 0.10986 | 123.3994 | 0.31586 | 123.1476 | 123.1247 | -123.3719 | -0.31128 | 122.85 | 122.9187 | 122.5662 | 122.8821
475.9688 | 123.1659 | -122.7859 | 0.28381 | 0.0034333 | 0.0038966 | 0.067877 | 0.064632 | 0.0041635 | -0.0012925 | 0.00050845 | 0.001648 | 0.017946 | 0.022917 | 0.032842 | -3.8532e-05 | 0.01016 | -0.0020464 | -0.3067 | 0.32501 | -123.056 | 0.013733 | -122.2137 | -122.8271 | -122.8775 | 0.091553 | 0.28381 | 0 | 0.16022 | 0.2243 | 0.15564 | 0.29755 | -0.27008 | 0.041199 | -0.27008 | 0.5722 | -0.091552 | -0.041198 | 0.17853 | 0.22888 | 122.7859 | 0 | -0.1236 | 123.0103 | 123.0835 | 122.9416 | 0.29755 | 0.15564 | 0.84229 | 123.0698 | 0.2243 | 0.16022 | 123.381 | 0.28381 | 123.111 | 123.0698 | -123.3398 | -0.28381 | 122.7997 | 122.9462 | 122.4792 | 122.8775
477.6562 | 123.111 | -122.8455 | 0.31128 | 0.018692 | 0.0036828 | 0.071722 | 0.065273 | 0.0011727 | -0.0032151 | 0.0045672 | -0.0014038 | 0.016024 | 0.020781 | 0.025793 | -0.0032427 | 0.0073828 | 0.00073059 | -0.21973 | 0.29297 | -123.056 | 0.068665 | -122.1313 | -122.7173 | -122.818 | 0.11444 | 0.26093 | 0 | 0.11444 | 0.20599 | 0.11902 | 0.24261 | -0.21057 | -0.01831 | -0.24261 | 0.71411 | 0.027466 | 0.12817 | 0.23804 | 0.33875 | 122.8455 | -0.050354 | -0.19684 | 123.0515 | 123.0881 | 122.9645 | 0.24261 | 0.11902 | 0.92468 | 123.1247 | 0.20599 | 0.11444 | 123.349 | 0.26093 | 123.1384 | 123.1064 | -123.3673 | -0.31128 | 122.9141 | 122.9599 | 122.6257 | 122.9599
479.4062 | 123.1705 | -122.8088 | 0.27466 | 0.0034333 | 0.004751 | 0.068731 | 0.065486 | 0.0054453 | -0.0021469 | -0.00013235 | -0.0014038 | 0.016237 | 0.022704 | 0.031774 | -0.00046573 | 0.0075964 | -0.0039692 | -0.32959 | 0.29755 | -123.056 | 0.059509 | -122.1588 | -122.7585 | -122.8226 | 0.12817 | 0.29297 | 0 | 0.15106 | 0.24719 | 0.16479 | 0.29755 | -0.24719 | 0.022888 | -0.21515 | 0.65002 | -0.013733 | 0.050354 | 0.23346 | 0.29755 | 122.8088 | 0.018311 | -0.1236 | 123.056 | 123.1064 | 122.9736 | 0.29755 | 0.16479 | 0.89722 | 123.1155 | 0.24719 | 0.15106 | 123.3536 | 0.29297 | 123.1064 | 123.1018 | -123.3307 | -0.27466 | 122.8683 | 122.9599 | 122.4792 | 122.937
481.1562 | 123.1934 | -122.8043 | 0.2655 | 0.0034333 | 0.0028284 | 0.071508 | 0.063777 | 0.0026681 | -0.0023605 | -0.00034615 | 0.0046998 | 0.014742 | 0.021422 | 0.029424 | -0.00025213 | 0.0086646 | -0.00055121 | -0.30212 | 0.29297 | -123.0835 | 0.068665 | -122.1542 | -122.7219 | -122.7997 | 0.13275 | 0.27466 | 0.018311 | 0.17853 | 0.29297 | 0.21515 | 0.3067 | -0.27924 | 0.027466 | -0.19684 | 0.65002 | 0.004577 | 0.082397 | 0.28381 | 0.36163 | 122.8226 | 0.009155 | -0.086975 | 123.0972 | 123.111 | 123.0194 | 0.28839 | 0.19684 | 0.92926 | 123.1522 | 0.27466 | 0.16022 | 123.3765 | 0.25635 | 123.0972 | 123.0789 | -123.349 | -0.24719 | 122.8729 | 122.9828 | 122.5021 | 122.937
482.9062 | 123.1338 | -122.7859 | 0.27924 | 0.0034333 | 0.0049646 | 0.07044 | 0.069118 | 0.0054453 | -0.0032151 | 8.125e-05 | 0.0046998 | 0.017306 | 0.020354 | 0.031774 | 0.0027387 | 0.0090918 | -0.00055121 | -0.31128 | 0.32044 | -123.0652 | 0.004578 | -122.2137 | -122.8271 | -122.8729 | 0.086975 | 0.28381 | -0.004578 | 0.14648 | 0.21057 | 0.11902 | 0.27008 | -0.27924 | 0.041199 | -0.27466 | 0.5722 | -0.086975 | -0.041198 | 0.19226 | 0.23804 | 122.7814 | 0.004577 | -0.13275 | 122.9965 | 123.056 | 122.905 | 0.27466 | 0.1236 | 0.85144 | 123.0698 | 0.21515 | 0.15106 | 123.3856 | 0.28839 | 123.1064 | 123.0698 | -123.3444 | -0.28381 | 122.7905 | 122.9324 | 122.4747 | 122.8729
484.5781 | 123.1934 | -122.7814 | 0.27924 | 0.011063 | 0.0049646 | 0.069372 | 0.065486 | 0.0020273 | -0.0019333 | -0.0022688 | 0.001648 | 0.01581 | 0.020568 | 0.031347 | 0.0018841 | 0.010374 | 0.00094419 | -0.3067 | 0.3067 | -123.0469 | 0.068665 | -122.1542 | -122.7356 | -122.7905 | 0.12817 | 0.27466 | 0.013733 | 0.16479 | 0.23804 | 0.16022 | 0.30212 | -0.2655 | 0.027466 | -0.21057 | 0.62714 | -0.009155 | 0.045776 | 0.25635 | 0.31128 | 122.7951 | -0.004578 | -0.11444 | 123.0194 | 123.0835 | 122.9416 | 0.28839 | 0.14648 | 0.89264 | 123.1155 | 0.2243 | 0.15106 | 123.3536 | 0.26093 | 123.0881 | 123.056 | -123.3261 | -0.2655 | 122.85 | 122.9462 | 122.4747 | 122.9095
486.3125 | 123.0743 | -122.8226 | 0.27924 | -0.0041962 | 0.004751 | 0.070013 | 0.067622 | 0.0024545 | -0.0019333 | 0.0032854 | 0.0046998 | 0.01816 | 0.023345 | 0.027075 | 0.0016705 | 0.008451 | -0.00055121 | -0.28381 | 0.33875 | -123.0789 | -0.009155 | -122.2824 | -122.8546 | -122.9095 | 0.018311 | 0.30212 | 0 | 0.091553 | 0.14648 | 0.054932 | 0.22888 | -0.25635 | 0.059509 | -0.28839 | 0.54016 | -0.086975 | -0.032043 | 0.16937 | 0.2243 | 122.8226 | 0.022888 | -0.18768 | 122.9691 | 123.0515 | 122.8775 | 0.22888 | 0.054932 | 0.79651 | 123.0698 | 0.14648 | 0.091553 | 123.4177 | 0.30212 | 123.1613 | 123.1247 | -123.3582 | -0.27924 | 122.8134 | 122.9141 | 122.5388 | 122.8409
488.0625 | 123.1659 | -122.7722 | 0.28381 | 0.026321 | 0.0049646 | 0.07279 | 0.064418 | 0.0018137 | -0.00086509 | -0.0022688 | 0.001648 | 0.017092 | 0.021636 | 0.034124 | 0.0012433 | 0.010374 | 0.00030339 | -0.27924 | 0.27924 | -123.0377 | 0.11902 | -122.081 | -122.7448 | -122.7905 | 0.1831 | 0.27008 | 0.013733 | 0.19226 | 0.25635 | 0.16937 | 0.29297 | -0.2655 | -0.004577 | -0.16479 | 0.69122 | -0.01831 | 0.027466 | 0.24719 | 0.29297 | 122.7859 | -0.013732 | -0.091552 | 123.0286 | 123.0652 | 122.9416 | 0.27924 | 0.15564 | 0.95673 | 123.1567 | 0.24262 | 0.17853 | 123.317 | 0.25635 | 123.0515 | 123.0423 | -123.3215 | -0.27008 | 122.8912 | 122.9645 | 122.493 | 122.9553
489.7344 | 123.2162 | -122.8226 | 0.27008 | 0.0034333 | 0.0058192 | 0.071722 | 0.06335 | 0.0018137 | -0.0034287 | -0.0012006 | 0.0077514 | 0.016024 | 0.0195 | 0.029424 | -0.0023883 | 0.008451 | 0.00073059 | -0.22888 | 0.28839 | -123.056 | 0.11902 | -122.0673 | -122.6715 | -122.7585 | 0.17853 | 0.26093 | 0.009155 | 0.19226 | 0.30212 | 0.21515 | 0.3067 | -0.23346 | 0.01831 | -0.15106 | 0.75531 | 0.064087 | 0.15106 | 0.29755 | 0.38452 | 122.8317 | -0.009156 | -0.07782 | 123.1247 | 123.1293 | 123.0377 | 0.29755 | 0.20599 | 0.98877 | 123.175 | 0.29297 | 0.18311 | 123.3444 | 0.25177 | 123.111 | 123.0835 | -123.3261 | -0.26093 | 122.9416 | 123.0148 | 122.5937 | 123.0011
491.4688 | 123.1979 | -122.7997 | 0.24261 | 0.0034333 | 0.0036828 | 0.070654 | 0.064418 | 0.0050179 | -0.0015061 | 0.0015764 | 0.0077514 | 0.014956 | 0.020568 | 0.028143 | 0.0018841 | 0.0099462 | -0.005678 | -0.24719 | 0.25635 | -123.0377 | 0.11444 | -122.1039 | -122.731 | -122.7905 | 0.18768 | 0.23804 | 0.009155 | 0.21515 | 0.28381 | 0.19226 | 0.33875 | -0.23804 | 0.013733 | -0.12817 | 0.6958 | 0.009156 | 0.068665 | 0.24719 | 0.3067 | 122.8088 | -0.004578 | -0.027466 | 123.0835 | 123.1384 | 122.9919 | 0.32959 | 0.18311 | 0.93384 | 123.1522 | 0.27466 | 0.20599 | 123.2941 | 0.22888 | 123.056 | 123.0377 | -123.2803 | -0.23346 | 122.9141 | 123.0148 | 122.5525 | 122.9874
493.2344 | 123.0606 | -122.85 | 0.31128 | 0.011063 | 0.0056054 | 0.071935 | 0.06805 | 0.0056589 | -0.00065149 | -0.0012006 | -0.0014038 | 0.018374 | 0.020354 | 0.023016 | -0.0011065 | 0.01016 | -0.0014056 | -0.26093 | 0.31586 | -123.0835 | -0.013733 | -122.2778 | -122.8592 | -122.9141 | -0.009155 | 0.28839 | -0.032043 | 0.07782 | 0.12817 | 0.041199 | 0.21515 | -0.23346 | 0.004578 | -0.32501 | 0.5722 | -0.064087 | -0.009155 | 0.16937 | 0.2243 | 122.818 | -0.022888 | -0.23346 | 122.9782 | 123.0652 | 122.8912 | 0.24719 | 0.073242 | 0.80566 | 123.0698 | 0.16022 | 0.10986 | 123.3994 | 0.32043 | 123.1659 | 123.1384 | -123.3948 | -0.34332 | 122.8363 | 122.9279 | 122.5891 | 122.8409
494.9844 | 123.0698 | -122.8317 | 0.27466 | 0.0034333 | 0.0028284 | 0.070013 | 0.066768 | 0.0075815 | 0.00063011 | -0.0024824 | 0.001648 | 0.017733 | 0.020354 | 0.028997 | -0.0013201 | 0.011014 | 8.9786e-05 | -0.28381 | 0.29297 | -123.1018 | -0.045776 | -122.287 | -122.8729 | -122.905 | 0 | 0.27466 | -0.064087 | 0.07782 | 0.10529 | 0.022888 | 0.20142 | -0.27008 | 0.018311 | -0.32043 | 0.54474 | -0.073242 | -0.041199 | 0.19684 | 0.22888 | 122.7676 | 0 | -0.19684 | 122.937 | 123.0331 | 122.8546 | 0.2655 | 0.086975 | 0.81482 | 123.056 | 0.16937 | 0.14191 | 123.3948 | 0.33875 | 123.1247 | 123.1064 | -123.3765 | -0.33875 | 122.7859 | 122.9095 | 122.5479 | 122.8317
496.6562 | 123.0606 | -122.8638 | 0.27924 | 0.011063 | 0.0062464 | 0.069586 | 0.069118 | 0.0054453 | -0.0010789 | 0.0013628 | 0.0046998 | 0.016451 | 0.021636 | 0.016393 | 0.00038887 | 0.0080236 | 0.00094419 | -0.28839 | 0.28381 | -123.1064 | -0.045776 | -122.2824 | -122.8638 | -122.905 | 0.004578 | 0.27924 | -0.032043 | 0.064087 | 0.11444 | 0.018311 | 0.19684 | -0.24261 | 0.004577 | -0.32501 | 0.58136 | -0.041198 | 0 | 0.20142 | 0.24261 | 122.8317 | 0 | -0.21515 | 122.9782 | 123.0606 | 122.8821 | 0.22888 | 0.050354 | 0.82397 | 123.0606 | 0.14648 | 0.09613 | 123.3902 | 0.31128 | 123.1476 | 123.143 | -123.3856 | -0.31128 | 122.818 | 122.9279 | 122.5754 | 122.8683
498.4062 | 123.1979 | -122.8271 | 0.24719 | 0.0034333 | 0.0045374 | 0.068945 | 0.062709 | 0.0075815 | -0.0025741 | 8.125e-05 | 0.0046998 | 0.015383 | 0.02249 | 0.029852 | -0.0026019 | 0.0086646 | -0.0033282 | -0.25177 | 0.25177 | -123.0835 | 0.086975 | -122.0856 | -122.7036 | -122.7676 | 0.16022 | 0.24261 | -0.004578 | 0.17853 | 0.28381 | 0.19684 | 0.29297 | -0.25635 | 0.004578 | -0.16022 | 0.74158 | 0.059509 | 0.1236 | 0.31586 | 0.37994 | 122.8226 | -0.004577 | -0.068664 | 123.111 | 123.1201 | 123.024 | 0.29755 | 0.20142 | 0.99792 | 123.1705 | 0.28839 | 0.18311 | 123.3353 | 0.24719 | 123.0789 | 123.0698 | -123.3307 | -0.25177 | 122.9141 | 123.0057 | 122.5754 | 122.9874
500.1562 | 123.0743 | -122.8546 | 0.27924 | -0.011826 | 0.0026148 | 0.068945 | 0.0657 | 0.0056589 | -0.0030015 | 0.00050845 | 0.0046998 | 0.016878 | 0.022704 | 0.029211 | -0.0030291 | 0.010374 | 0.0013714 | -0.25635 | 0.28839 | -123.143 | -0.027466 | -122.2504 | -122.8134 | -122.8775 | 0.004578 | 0.27008 | -0.041199 | 0.082397 | 0.15106 | 0.059509 | 0.20599 | -0.28839 | 0.009155 | -0.3067 | 0.60425 | -0.022888 | 0.041198 | 0.2655 | 0.32959 | 122.8134 | -0.009155 | -0.19684 | 123.0057 | 123.0606 | 122.9141 | 0.24719 | 0.10071 | 0.89264 | 123.1155 | 0.19226 | 0.1236 | 123.4314 | 0.31128 | 123.143 | 123.1247 | -123.4222 | -0.32043 | 122.8271 | 122.937 | 122.5983 | 122.8592
501.8281 | 123.1201 | -122.8363 | 0.27924 | 0.018692 | 0.0043238 | 0.068304 | 0.065059 | 0.0041635 | -0.0036423 | 0.002431 | 0.001648 | 0.01816 | 0.022063 | 0.020666 | 0.0010297 | 0.010374 | 0.0013714 | -0.21515 | 0.3067 | -123.0881 | 0.009155 | -122.1771 | -122.7631 | -122.8409 | 0.086975 | 0.27466 | -0.027466 | 0.10986 | 0.19684 | 0.10986 | 0.23804 | -0.25177 | 0.027466 | -0.27008 | 0.65918 | -0.004577 | 0.073242 | 0.24719 | 0.32501 | 122.8088 | -0.004578 | -0.16937 | 123.0331 | 123.0743 | 122.9462 | 0.2655 | 0.13733 | 0.91095 | 123.0972 | 0.2243 | 0.13733 | 123.3948 | 0.30212 | 123.143 | 123.111 | -123.3673 | -0.3067 | 122.8455 | 122.9462 | 122.6212 | 122.9233
503.5781 | 123.1155 | -122.8317 | 0.28381 | 0.011063 | 0.0049646 | 0.070867 | 0.065059 | 0.0045907 | 0.00084391 | 8.125e-05 | 0.0046998 | 0.016878 | 0.020995 | 0.021307 | -0.00046573 | 0.00781 | 0.00030339 | -0.25635 | 0.32044 | -123.0972 | -0.013733 | -122.2046 | -122.7722 | -122.85 | 0.032043 | 0.28381 | -0.050354 | 0.086975 | 0.1831 | 0.082397 | 0.22888 | -0.2655 | 0.036622 | -0.29755 | 0.62714 | -0.018311 | 0.059509 | 0.24719 | 0.32501 | 122.7814 | 0 | -0.19684 | 123.0148 | 123.0606 | 122.9141 | 0.27924 | 0.13275 | 0.89264 | 123.0835 | 0.23346 | 0.13733 | 123.4177 | 0.33417 | 123.1522 | 123.1155 | -123.381 | -0.33417 | 122.818 | 122.9187 | 122.5754 | 122.8638
505.3281 | 123.0743 | -122.8592 | 0.28381 | 0.011063 | 0.0045374 | 0.070226 | 0.065486 | 0.0080087 | -0.0019333 | 0.0022174 | 0.0046998 | 0.018374 | 0.022277 | 0.023657 | -3.8532e-05 | 0.0082374 | -0.00076481 | -0.27008 | 0.29755 | -123.1018 | -0.036621 | -122.2458 | -122.8546 | -122.9141 | -0.013733 | 0.25635 | -0.041199 | 0.050354 | 0.10071 | 0.022888 | 0.19226 | -0.24262 | 0.013733 | -0.32043 | 0.6134 | -0.054932 | 0.004578 | 0.18768 | 0.24719 | 122.818 | -0.027465 | -0.23346 | 122.9599 | 123.0515 | 122.8821 | 0.23346 | 0.064087 | 0.85602 | 123.0652 | 0.14191 | 0.091553 | 123.3994 | 0.29755 | 123.1567 | 123.1155 | -123.3856 | -0.32501 | 122.8226 | 122.9095 | 122.5891 | 122.8455
507.0625 | 123.1567 | -122.818 | 0.2243 | 0.018692 | 0.0066736 | 0.07279 | 0.063136 | 0.0037363 | -0.00086509 | -0.0020552 | 0.001648 | 0.016878 | 0.021636 | 0.03092 | 0.0012433 | 0.010587 | -0.001192 | -0.27924 | 0.2655 | -123.0469 | 0.073242 | -122.1222 | -122.7448 | -122.8088 | 0.14648 | 0.24261 | -0.027466 | 0.16479 | 0.23346 | 0.14191 | 0.2655 | -0.22888 | 0.041199 | -0.15106 | 0.6958 | 0.009155 | 0.073242 | 0.23804 | 0.30212 | 122.7905 | 0.018311 | -0.059509 | 123.0515 | 123.0835 | 122.9599 | 0.29297 | 0.16937 | 0.92468 | 123.1201 | 0.26093 | 0.19226 | 123.3124 | 0.27008 | 123.0835 | 123.0606 | -123.2712 | -0.25177 | 122.8912 | 122.9828 | 122.5388 | 122.9645
508.75 | 123.1201 | -122.8363 | 0.25635 | 0.018692 | 0.007528 | 0.070013 | 0.064845 | 0.00095914 | -0.00065149 | 0.00072205 | 0.0046998 | 0.016237 | 0.021209 | 0.023229 | -3.8532e-05 | 0.0090918 | -0.0018328 | -0.21973 | 0.27008 | -123.0972 | 0.018311 | -122.1954 | -122.7814 | -122.8455 | 0.068665 | 0.2655 | -0.050354 | 0.11444 | 0.18768 | 0.09613 | 0.23804 | -0.26093 | 0.013733 | -0.23804 | 0.64087 | -0.009155 | 0.054932 | 0.25177 | 0.31586 | 122.7859 | 0.009155 | -0.14191 | 123.024 | 123.0743 | 122.9324 | 0.28839 | 0.14648 | 0.90179 | 123.1155 | 0.23804 | 0.16479 | 123.3673 | 0.31586 | 123.1064 | 123.1018 | -123.3536 | -0.3067 | 122.8546 | 122.9507 | 122.6166 | 122.905
510.5 | 123.143 | -122.8592 | 0.24261 | 0.0034333 | 0.0026148 | 0.071081 | 0.065059 | 0.0050179 | -0.00022429 | -0.0035504 | 0.0046998 | 0.014101 | 0.02249 | 0.034765 | -0.0011065 | 0.0097326 | 0.0024396 | -0.31128 | 0.25635 | -123.0881 | 0.004578 | -122.1817 | -122.7814 | -122.8317 | 0.054932 | 0.23346 | -0.036621 | 0.11902 | 0.19226 | 0.13275 | 0.25177 | -0.22888 | 0.013733 | -0.23804 | 0.67749 | 0.027466 | 0.07782 | 0.25635 | 0.3067 | 122.8226 | -0.009156 | -0.1236 | 123.0515 | 123.111 | 122.9919 | 0.28839 | 0.16937 | 0.90637 | 123.0927 | 0.22888 | 0.15564 | 123.3444 | 0.27008 | 123.1155 | 123.0927 | -123.3307 | -0.27924 | 122.8638 | 122.9782 | 122.5479 | 122.9141
512.2344 | 123.1796 | -122.8226 | 0.21057 | 0.0034333 | 0.0034692 | 0.069158 | 0.063991 | 0.0048043 | -0.0015061 | -0.0029096 | 0.001648 | 0.015383 | 0.019286 | 0.035192 | 0.00060247 | 0.0099462 | 8.9786e-05 | -0.28839 | 0.24261 | -123.0835 | 0.054932 | -122.1405 | -122.7264 | -122.7905 | 0.13275 | 0.2243 | -0.018311 | 0.17853 | 0.26093 | 0.17395 | 0.27924 | -0.26093 | 0.032044 | -0.15564 | 0.68207 | 0.032044 | 0.096131 | 0.29297 | 0.35706 | 122.8043 | 0.013733 | -0.032043 | 123.0835 | 123.1018 | 122.9965 | 0.29755 | 0.19226 | 0.94299 | 123.1384 | 0.27924 | 0.19684 | 123.3261 | 0.24261 | 123.0652 | 123.0469 | -123.2941 | -0.22888 | 122.8775 | 123.0011 | 122.5342 | 122.9553
513.9844 | 123.0515 | -122.85 | 0.2655 | 0.011063 | 0.0058192 | 0.070226 | 0.066982 | 0.0011727 | -0.0036423 | -0.0018414 | -0.0044556 | 0.017946 | 0.019072 | 0.025579 | -0.00046573 | 0.0073828 | 0.0011578 | -0.30212 | 0.27924 | -123.0972 | -0.064087 | -122.3053 | -122.8775 | -122.9416 | -0.009155 | 0.27008 | -0.064087 | 0.054932 | 0.10529 | 0.013733 | 0.18768 | -0.24719 | 0.013733 | -0.32959 | 0.54474 | -0.091552 | -0.027465 | 0.15564 | 0.21973 | 122.7859 | 0.004578 | -0.21057 | 122.9553 | 123.0377 | 122.8638 | 0.25177 | 0.07782 | 0.79193 | 123.0331 | 0.16937 | 0.11902 | 123.3765 | 0.33417 | 123.1293 | 123.1201 | -123.3627 | -0.32959 | 122.7859 | 122.905 | 122.5479 | 122.8409
515.6719 | 123.1064 | -122.8226 | 0.25177 | 0.0034333 | 0.0049646 | 0.071081 | 0.066554 | 0.0050179 | -0.0023605 | -0.0014142 | -0.0014038 | 0.017092 | 0.020781 | 0.025793 | 0.0035931 | 0.011228 | 0.0030804 | -0.3067 | 0.29755 | -123.0789 | -0.036621 | -122.2458 | -122.8409 | -122.8821 | 0.018311 | 0.2655 | -0.036621 | 0.10071 | 0.14648 | 0.045776 | 0.21973 | -0.25635 | 0.045776 | -0.28839 | 0.57678 | -0.059509 | -0.01831 | 0.19684 | 0.23804 | 122.7859 | 0.013733 | -0.15106 | 122.9691 | 123.0423 | 122.8683 | 0.25635 | 0.082397 | 0.83313 | 123.0423 | 0.18311 | 0.13733 | 123.3765 | 0.30212 | 123.1201 | 123.0881 | -123.3307 | -0.28839 | 122.7859 | 122.9233 | 122.5159 | 122.8409
517.4062 | 123.0515 | -122.85 | 0.25177 | -0.011826 | 0.0051782 | 0.071295 | 0.066554 | 0.0035227 | -0.0021469 | -0.0022688 | 0.001648 | 0.01816 | 0.022063 | 0.02622 | -0.0019611 | 0.0090918 | -0.0043964 | -0.27466 | 0.29755 | -123.0927 | -0.045776 | -122.2595 | -122.8592 | -122.9095 | -0.018311 | 0.26093 | -0.054932 | 0.054932 | 0.11902 | 0.013733 | 0.1831 | -0.24261 | 0.045776 | -0.29755 | 0.59052 | -0.059509 | -0.009155 | 0.1831 | 0.23346 | 122.7951 | 0.009155 | -0.19684 | 122.9691 | 123.0331 | 122.8638 | 0.23804 | 0.068665 | 0.83313 | 123.0469 | 0.17395 | 0.10986 | 123.3902 | 0.31586 | 123.1476 | 123.111 | -123.3444 | -0.3067 | 122.8043 | 122.905 | 122.5754 | 122.8317
519.1406 | 123.0743 | -122.8409 | 0.25177 | 0.011063 | 0.0045374 | 0.071081 | 0.067622 | 0.0062997 | -0.00086509 | -0.00077335 | 0.001648 | 0.016878 | 0.019713 | 0.020452 | 0.0018841 | 0.011014 | 0.001585 | -0.3067 | 0.28839 | -123.1064 | -0.054932 | -122.2778 | -122.8638 | -122.9141 | -0.013733 | 0.25635 | -0.059509 | 0.050354 | 0.10529 | 0.022888 | 0.19226 | -0.2655 | 0.036621 | -0.3067 | 0.56305 | -0.073243 | -0.022889 | 0.19226 | 0.24261 | 122.7814 | 0.004578 | -0.20142 | 122.9462 | 123.0331 | 122.8638 | 0.25177 | 0.082397 | 0.82855 | 123.0515 | 0.16479 | 0.10986 | 123.3948 | 0.31586 | 123.1293 | 123.0972 | -123.3582 | -0.31128 | 122.7859 | 122.8912 | 122.5342 | 122.8271
520.8125 | 123.0469 | -122.8409 | 0.25177 | 0.0034333 | 0.0062464 | 0.068517 | 0.065486 | 0.0039499 | -0.0027877 | -0.0041914 | 0.0046998 | 0.016665 | 0.019713 | 0.033483 | -0.00046573 | 0.0086646 | 0.005644 | -0.27924 | 0.28381 | -123.1018 | -0.054932 | -122.2687 | -122.8683 | -122.9187 | -0.045776 | 0.27466 | -0.064087 | 0.036621 | 0.10071 | 0.004578 | 0.17853 | -0.26093 | 0.032043 | -0.3067 | 0.5722 | -0.07782 | -0.027466 | 0.18311 | 0.23346 | 122.7768 | 0.022888 | -0.21515 | 122.9416 | 123.0194 | 122.8455 | 0.24261 | 0.068665 | 0.83313 | 123.0469 | 0.1648 | 0.10071 | 123.3856 | 0.33875 | 123.1247 | 123.1155 | -123.3536 | -0.31586 | 122.7859 | 122.8775 | 122.5616 | 122.7951
522.5625 | 123.1705 | -122.8271 | 0.21057 | 0.0034333 | 0.0032556 | 0.068731 | 0.062068 | 0.0018137 | -0.0034287 | 0.00072205 | -0.0014038 | 0.015169 | 0.021422 | 0.024938 | -0.0028155 | 0.009519 | -0.0020464 | -0.23346 | 0.24261 | -123.056 | 0.086975 | -122.0718 | -122.6852 | -122.7676 | 0.16022 | 0.2243 | -0.032043 | 0.17395 | 0.28381 | 0.19226 | 0.29297 | -0.22888 | 0.032044 | -0.1236 | 0.75531 | 0.059509 | 0.14191 | 0.28839 | 0.37079 | 122.7951 | 0.013733 | -0.036621 | 123.111 | 123.1201 | 123.0194 | 0.32501 | 0.2243 | 0.98419 | 123.143 | 0.31586 | 0.20599 | 123.2986 | 0.25635 | 123.0698 | 123.0515 | -123.2666 | -0.24261 | 122.9141 | 123.0011 | 122.5937 | 122.9874
524.3125 | 123.0652 | -122.8638 | 0.25635 | 0.0034333 | 0.0043238 | 0.07044 | 0.065913 | 0.0030953 | -0.0012925 | 0.00093565 | 0.0046998 | 0.019442 | 0.019713 | 0.030065 | -0.0019611 | 0.0090918 | 0.0020124 | -0.26093 | 0.27008 | -123.1064 | -0.018311 | -122.2046 | -122.8088 | -122.8546 | 0.004578 | 0.25635 | -0.054932 | 0.045776 | 0.14191 | 0.050354 | 0.17853 | -0.24261 | 0.013733 | -0.27466 | 0.65918 | 0.009156 | 0.054932 | 0.25177 | 0.29755 | 122.8088 | 0 | -0.21057 | 123.0057 | 123.0423 | 122.9141 | 0.23346 | 0.10529 | 0.90179 | 123.0881 | 0.19684 | 0.10071 | 123.3765 | 0.31128 | 123.1339 | 123.1201 | -123.3627 | -0.31128 | 122.8455 | 122.9095 | 122.6028 | 122.8683
526 | 123.0652 | -122.8592 | 0.24719 | 0.0034333 | 0.0062464 | 0.072149 | 0.067836 | 0.00053194 | -0.0021469 | 0.00072205 | 0.001648 | 0.019655 | 0.02014 | 0.02857 | 0.0012433 | 0.0088782 | -0.00033761 | -0.23804 | 0.27008 | -123.0789 | 0.009155 | -122.1954 | -122.7951 | -122.8638 | 0.050354 | 0.24261 | -0.050354 | 0.07782 | 0.14648 | 0.050354 | 0.20599 | -0.21973 | 0.022889 | -0.23804 | 0.66376 | -0.004578 | 0.064087 | 0.21515 | 0.28381 | 122.8088 | -0.004577 | -0.16937 | 123.0057 | 123.0652 | 122.9095 | 0.25635 | 0.10071 | 0.88348 | 123.0881 | 0.19684 | 0.12817 | 123.349 | 0.29297 | 123.1293 | 123.1018 | -123.3261 | -0.29755 | 122.8683 | 122.937 | 122.6212 | 122.9095
527.75 | 123.1934 | -122.8134 | 0.2243 | 0.011063 | 0.0034692 | 0.069158 | 0.064418 | 0.0041635 | -0.0025741 | -0.0029096 | 0.0046998 | 0.016451 | 0.018218 | 0.021307 | -0.0021747 | 0.0086646 | -0.002901 | -0.27008 | 0.24261 | -123.0652 | 0.073242 | -122.0718 | -122.6898 | -122.7676 | 0.16022 | 0.21973 | -0.004578 | 0.16479 | 0.28381 | 0.19226 | 0.28381 | -0.25177 | 0.018311 | -0.15106 | 0.74158 | 0.045777 | 0.1236 | 0.29755 | 0.37537 | 122.8088 | -0.004577 | -0.059509 | 123.0972 | 123.0972 | 123.0057 | 0.28839 | 0.19684 | 0.99335 | 123.1384 | 0.28839 | 0.16937 | 123.3078 | 0.22431 | 123.056 | 123.0331 | -123.2895 | -0.22888 | 122.8867 | 122.9782 | 122.5433 | 122.9736
529.4844 | 123.1842 | -122.8088 | 0.2243 | -0.0041962 | 0.0024012 | 0.069586 | 0.062496 | 0.0026681 | -0.0034287 | -0.00034615 | -0.0014038 | 0.015383 | 0.019927 | 0.030065 | -0.0011065 | 0.009519 | -0.00012381 | -0.3067 | 0.24719 | -123.0606 | 0.022888 | -122.1588 | -122.7402 | -122.7859 | 0.10529 | 0.2243 | -0.013733 | 0.15106 | 0.24719 | 0.17395 | 0.29297 | -0.25177 | 0.022888 | -0.20142 | 0.65002 | 0.022888 | 0.068665 | 0.27466 | 0.32044 | 122.7951 | 0 | -0.073242 | 123.056 | 123.1018 | 122.9828 | 0.3067 | 0.18768 | 0.9018 | 123.0835 | 0.26093 | 0.16479 | 123.3078 | 0.23804 | 123.056 | 123.0331 | -123.2849 | -0.23804 | 122.8317 | 122.9599 | 122.5021 | 122.9141
531.2188 | 123.1659 | -122.8134 | 0.22888 | 0.0034333 | 0.0053918 | 0.069158 | 0.063991 | 0.0013863 | -0.0044967 | -0.00077335 | -0.0014038 | 0.016451 | 0.020568 | 0.031133 | 0.00017507 | 0.0073828 | 8.9786e-05 | -0.21515 | 0.22888 | -123.0789 | 0.064087 | -122.1085 | -122.7127 | -122.7859 | 0.1236 | 0.20142 | -0.032043 | 0.12817 | 0.23804 | 0.15564 | 0.2655 | -0.2655 | 0 | -0.16479 | 0.70496 | 0.027466 | 0.10071 | 0.29297 | 0.36621 | 122.7814 | -0.027466 | -0.10071 | 123.0515 | 123.0789 | 122.9691 | 0.29755 | 0.18768 | 0.97046 | 123.143 | 0.27008 | 0.16022 | 123.3078 | 0.23346 | 123.0423 | 123.0148 | -123.3078 | -0.26093 | 122.8775 | 122.9416 | 122.5983 | 122.937
532.9844 | 123.1476 | -122.8134 | 0.22888 | -0.0041962 | 0.0066736 | 0.070013 | 0.064418 | 0.0043771 | -0.0010789 | -0.00098695 | 0.0046998 | 0.016024 | 0.021209 | 0.029638 | 0.00038887 | 0.0080236 | 0.002226 | -0.21057 | 0.23346 | -123.0606 | 0.064087 | -122.1085 | -122.7173 | -122.7951 | 0.12817 | 0.23346 | -0.032043 | 0.12817 | 0.22888 | 0.15106 | 0.25635 | -0.24719 | 0.004577 | -0.16479 | 0.70496 | 0.018311 | 0.096131 | 0.2655 | 0.34332 | 122.7814 | 0.004577 | -0.10071 | 123.0423 | 123.0698 | 122.9645 | 0.28839 | 0.18311 | 0.95215 | 123.1247 | 0.26093 | 0.16022 | 123.2941 | 0.2655 | 123.0469 | 123.0469 | -123.2895 | -0.26093 | 122.8775 | 122.9416 | 122.6028 | 122.9416
534.7188 | 123.2208 | -122.8134 | 0.2243 | 0.011063 | 0.0015466 | 0.070013 | 0.064845 | 0.0020273 | -0.0021469 | -0.00077335 | 0.0046998 | 0.014315 | 0.019927 | 0.023016 | 0.00081607 | 0.0075964 | -0.001192 | -0.25177 | 0.2243 | -123.0835 | 0.073242 | -122.0901 | -122.6807 | -122.7722 | 0.1831 | 0.22888 | -0.027466 | 0.16479 | 0.26093 | 0.16937 | 0.27008 | -0.27008 | 0 | -0.15106 | 0.72327 | 0.041199 | 0.13275 | 0.31128 | 0.40283 | 122.7859 | 0.004578 | -0.059509 | 123.0743 | 123.0835 | 122.9828 | 0.29755 | 0.19684 | 0.99335 | 123.1567 | 0.28839 | 0.19226 | 123.3078 | 0.25635 | 123.0377 | 123.0423 | -123.3078 | -0.25177 | 122.8867 | 122.9782 | 122.5616 | 122.9965
536.3906 | 123.0331 | -122.8592 | 0.2243 | 0.0034333 | 0.0049646 | 0.074072 | 0.068904 | 0.0011727 | -0.00086509 | -0.0024824 | -0.0044556 | 0.017733 | 0.020995 | 0.02152 | 0.0035931 | 0.008451 | 0.00094419 | -0.27466 | 0.25635 | -123.1338 | -0.07782 | -122.3053 | -122.8867 | -122.9324 | -0.054932 | 0.25635 | -0.086975 | 0.018311 | 0.064087 | -0.009155 | 0.13275 | -0.27466 | 0.032044 | -0.30212 | 0.55389 | -0.073242 | -0.027466 | 0.20142 | 0.24719 | 122.7722 | 0.032044 | -0.20599 | 122.9233 | 122.9919 | 122.85 | 0.21973 | 0.07782 | 0.82855 | 123.056 | 0.15106 | 0.10529 | 123.3902 | 0.34332 | 123.1155 | 123.1155 | -123.3582 | -0.31128 | 122.7814 | 122.8775 | 122.5845 | 122.8043
538.1406 | 123.0515 | -122.8775 | 0.24261 | 0.0034333 | 0.0026148 | 0.07044 | 0.064418 | 0.0035227 | -0.0034287 | 0.00029485 | -0.0014038 | 0.016878 | 0.019927 | 0.025366 | -0.0015337 | 0.011228 | 0.001585 | -0.29755 | 0.2655 | -123.1018 | -0.068665 | -122.2549 | -122.8271 | -122.8775 | -0.018311 | 0.23346 | -0.082397 | 0.018311 | 0.10986 | 0.041199 | 0.16937 | -0.2243 | 0.022888 | -0.31128 | 0.62256 | 0 | 0.050354 | 0.2243 | 0.27466 | 122.7951 | -0.009156 | -0.2243 | 122.9874 | 123.0469 | 122.9187 | 0.25177 | 0.1236 | 0.84686 | 123.0331 | 0.19226 | 0.10071 | 123.3673 | 0.31586 | 123.143 | 123.111 | -123.3444 | -0.32501 | 122.8088 | 122.8958 | 122.58 | 122.8592
539.8125 | 123.0469 | -122.8546 | 0.2243 | 0.011063 | 0.0051782 | 0.070654 | 0.068691 | 0.0041635 | -0.0021469 | -0.0029096 | 0.001648 | 0.01816 | 0.020354 | 0.024938 | -3.8532e-05 | 0.0090918 | -0.0020464 | -0.23804 | 0.2655 | -123.1155 | -0.045776 | -122.2458 | -122.8363 | -122.9004 | 0.013733 | 0.24719 | -0.054932 | 0.050354 | 0.10071 | 0.018311 | 0.16937 | -0.26093 | 0.041199 | -0.27008 | 0.60882 | -0.045777 | 0.01831 | 0.21515 | 0.27924 | 122.7997 | 0.022888 | -0.17395 | 122.9553 | 123.024 | 122.8729 | 0.22431 | 0.073243 | 0.86975 | 123.0698 | 0.15564 | 0.10529 | 123.381 | 0.30212 | 123.1201 | 123.1018 | -123.3398 | -0.27924 | 122.8088 | 122.905 | 122.6166 | 122.8683
541.5469 | 123.0743 | -122.8546 | 0.2243 | 0.011063 | 0.0045374 | 0.070013 | 0.066768 | 0.0030953 | -0.0027877 | -0.0022688 | 0.001648 | 0.015383 | 0.018431 | 0.026861 | -0.00067933 | 0.0082374 | 0.0030804 | -0.26093 | 0.27008 | -123.111 | -0.064087 | -122.2412 | -122.8043 | -122.8912 | -0.022888 | 0.25177 | -0.082397 | 0.041199 | 0.13275 | 0.045776 | 0.1831 | -0.25635 | 0.045777 | -0.28839 | 0.6134 | -0.036621 | 0.050354 | 0.21973 | 0.3067 | 122.7722 | 0.027466 | -0.18311 | 122.9874 | 123.0377 | 122.9004 | 0.2655 | 0.12817 | 0.86975 | 123.0469 | 0.21515 | 0.1236 | 123.381 | 0.33417 | 123.1247 | 123.1064 | -123.3353 | -0.3067 | 122.7905 | 122.8958 | 122.5937 | 122.8317
543.3281 | 123.0972 | -122.8546 | 0.21973 | 0.0034333 | 0.0058192 | 0.071508 | 0.066768 | 0.0056589 | -0.0019333 | 0.00050845 | 0.0077514 | 0.019228 | 0.021849 | 0.032629 | 0.00038887 | 0.0099462 | 0.0035078 | -0.2243 | 0.25635 | -123.0972 | 0.004578 | -122.1817 | -122.7814 | -122.85 | 0.059509 | 0.23346 | -0.050354 | 0.091553 | 0.16022 | 0.064087 | 0.20599 | -0.24262 | 0.036621 | -0.21515 | 0.67291 | 0.004577 | 0.073242 | 0.24719 | 0.31586 | 122.8043 | 0.013732 | -0.12817 | 123.0148 | 123.0606 | 122.9187 | 0.25635 | 0.11444 | 0.91553 | 123.1018 | 0.21057 | 0.14191 | 123.3536 | 0.28381 | 123.111 | 123.0881 | -123.317 | -0.27008 | 122.8592 | 122.9462 | 122.6303 | 122.9141
545.0625 | 123.0881 | -122.8363 | 0.22888 | 0.0034333 | 0.0038966 | 0.069372 | 0.068477 | 0.0067269 | -0.0027877 | -0.0014142 | -0.0044556 | 0.016024 | 0.0195 | 0.024297 | 0.0025251 | 0.010801 | 0.0013714 | -0.32044 | 0.27466 | -123.0972 | -0.059509 | -122.2412 | -122.8455 | -122.905 | 0.018311 | 0.24261 | -0.059509 | 0.10986 | 0.16479 | 0.059509 | 0.21057 | -0.26093 | 0.045776 | -0.28839 | 0.59509 | -0.068664 | -0.009155 | 0.19226 | 0.25177 | 122.7768 | 0.013733 | -0.11902 | 123.0011 | 123.0469 | 122.8958 | 0.27008 | 0.11902 | 0.85602 | 123.0377 | 0.2243 | 0.16937 | 123.3719 | 0.30212 | 123.111 | 123.0789 | -123.3261 | -0.28839 | 122.7768 | 122.9462 | 122.5159 | 122.8546
546.7969 | 123.1064 | -122.8363 | 0.25177 | 0.018692 | 0.0060328 | 0.070654 | 0.06805 | 0.0022409 | -0.00086509 | -0.0018414 | 0.001648 | 0.016878 | 0.020995 | 0.018102 | -0.0017475 | 0.0097326 | -0.0050372 | -0.21515 | 0.28381 | -123.0972 | -0.004578 | -122.1817 | -122.7722 | -122.8363 | 0.07782 | 0.24261 | -0.036621 | 0.10529 | 0.17853 | 0.10071 | 0.2243 | -0.26093 | 0.032043 | -0.25635 | 0.6546 | 0 | 0.064087 | 0.26093 | 0.32501 | 122.7997 | -0.009155 | -0.14648 | 123.0148 | 123.0606 | 122.937 | 0.26093 | 0.13733 | 0.91553 | 123.0927 | 0.21515 | 0.14191 | 123.381 | 0.27924 | 123.1201 | 123.0789 | -123.349 | -0.28839 | 122.8317 | 122.9416 | 122.6212 | 122.9141
548.4844 | 123.1888 | -122.7859 | 0.23346 | 0.0034333 | 0.0036828 | 0.069158 | 0.063136 | 0.0024545 | -0.0021469 | -0.002696 | -0.0014038 | 0.016024 | 0.020568 | 0.031133 | -3.8532e-05 | 0.01016 | -0.00097841 | -0.24261 | 0.21515 | -123.0377 | 0.091553 | -122.0581 | -122.6761 | -122.7219 | 0.17395 | 0.21057 | -0.013733 | 0.16479 | 0.28381 | 0.19684 | 0.26093 | -0.25177 | -0.01831 | -0.14191 | 0.72785 | 0.064087 | 0.10986 | 0.31586 | 0.36163 | 122.7722 | -0.022888 | -0.068664 | 123.0698 | 123.0469 | 122.9828 | 0.27466 | 0.21057 | 0.97961 | 123.1293 | 0.29755 | 0.17853 | 123.2529 | 0.2243 | 123.0011 | 122.9965 | -123.2712 | -0.24719 | 122.8775 | 122.9507 | 122.5433 | 122.9599
550.1562 | 123.056 | -122.8546 | 0.24261 | 0.026321 | 0.0036828 | 0.069158 | 0.067409 | 0.0056589 | -0.0017197 | -0.00077335 | 0.0046998 | 0.018587 | 0.021636 | 0.023229 | -0.00067933 | 0.0090918 | 0.0030804 | -0.26093 | 0.27008 | -123.1338 | -0.054932 | -122.2595 | -122.8226 | -122.8775 | -0.027466 | 0.25635 | -0.086975 | 0.032043 | 0.11444 | 0.045776 | 0.1831 | -0.27924 | 0.027466 | -0.29755 | 0.59509 | -0.022888 | 0.032043 | 0.25635 | 0.31128 | 122.7676 | 0.013733 | -0.21057 | 122.9691 | 123.0377 | 122.9004 | 0.27008 | 0.13275 | 0.87433 | 123.0789 | 0.20142 | 0.11902 | 123.4039 | 0.34332 | 123.1247 | 123.111 | -123.3765 | -0.32959 | 122.7997 | 122.8867 | 122.5937 | 122.8271
551.8906 | 123.1476 | -122.8043 | 0.21057 | 0.018692 | 0.0049646 | 0.071081 | 0.064632 | 0.0015999 | -0.0021469 | 0.00050845 | 0.0077514 | 0.016878 | 0.021636 | 0.031347 | 0.0014569 | 0.01016 | -0.0014056 | -0.28839 | 0.26093 | -123.0515 | 0.045776 | -122.0901 | -122.7264 | -122.7768 | 0.16022 | 0.2243 | -0.050354 | 0.15106 | 0.22888 | 0.13733 | 0.2655 | -0.24719 | 0.050354 | -0.1648 | 0.71411 | 0.027466 | 0.07782 | 0.27466 | 0.32501 | 122.7539 | 0.013733 | -0.059509 | 123.0331 | 123.0698 | 122.9416 | 0.31586 | 0.18768 | 0.9613 | 123.0972 | 0.27924 | 0.20142 | 123.3124 | 0.27466 | 123.0652 | 123.0286 | -123.262 | -0.26093 | 122.85 | 122.9553 | 122.5159 | 122.9645
553.5781 | 123.0331 | -122.8546 | 0.24261 | 0.011063 | 0.0062464 | 0.069586 | 0.064632 | 0.0071541 | -0.0010789 | -0.00098695 | -0.0044556 | 0.01816 | 0.021209 | 0.029852 | -0.00025213 | 0.0090918 | -0.0058918 | -0.31128 | 0.26093 | -123.0881 | -0.068665 | -122.3007 | -122.8683 | -122.8958 | -0.036621 | 0.25177 | -0.082397 | 0.050354 | 0.091553 | 0 | 0.17853 | -0.23346 | 0.01831 | -0.31128 | 0.55389 | -0.041199 | -0.013733 | 0.19226 | 0.21973 | 122.7722 | 0.009155 | -0.19226 | 122.9462 | 123.0331 | 122.8546 | 0.26092 | 0.082397 | 0.78735 | 123.0194 | 0.17395 | 0.13275 | 123.349 | 0.33417 | 123.1155 | 123.1064 | -123.3307 | -0.32501 | 122.7859 | 122.905 | 122.5433 | 122.818
555.3281 | 123.1888 | -122.7859 | 0.22888 | 0.0034333 | 0.0034692 | 0.070867 | 0.061855 | 0.0041635 | -0.0044967 | -0.0029096 | 0.0046998 | 0.016237 | 0.019286 | 0.026861 | -0.0011065 | 0.010587 | -0.0033282 | -0.26093 | 0.21515 | -123.0698 | 0.064087 | -122.0581 | -122.6761 | -122.7539 | 0.17395 | 0.19226 | -0.018311 | 0.17853 | 0.28839 | 0.21057 | 0.29755 | -0.28381 | -0.013733 | -0.16479 | 0.72785 | 0.032044 | 0.10986 | 0.31586 | 0.39368 | 122.7676 | -0.036621 | -0.050354 | 123.0743 | 123.0835 | 122.9965 | 0.31586 | 0.22888 | 1.0117 | 123.1338 | 0.3067 | 0.19684 | 123.2849 | 0.21057 | 123.0011 | 122.9782 | -123.2986 | -0.24719 | 122.85 | 122.9645 | 122.525 | 122.9599
557.0781 | 123.143 | -122.8226 | 0.23804 | -0.0041962 | 0.0038966 | 0.070867 | 0.064204 | -0.0011771 | -0.0038559 | -0.0018414 | 0.001648 | 0.01581 | 0.021422 | 0.020025 | -0.0028155 | 0.01016 | 0.0035078 | -0.21515 | 0.25635 | -123.0331 | 0.07782 | -122.081 | -122.6898 | -122.7676 | 0.13275 | 0.19684 | -0.041199 | 0.14191 | 0.24719 | 0.17853 | 0.27008 | -0.21057 | 0.018311 | -0.16022 | 0.74158 | 0.054932 | 0.13275 | 0.2655 | 0.34332 | 122.7814 | -0.041199 | -0.09613 | 123.0698 | 123.0927 | 123.0011 | 0.31128 | 0.21973 | 0.95215 | 123.111 | 0.28839 | 0.18311 | 123.2895 | 0.23804 | 123.0789 | 123.0194 | -123.2712 | -0.27924 | 122.9004 | 122.9645 | 122.6074 | 122.9553
558.7656 | 123.0835 | -122.8088 | 0.25177 | 0.0034333 | 0.0071008 | 0.068304 | 0.065273 | 0.0080087 | -0.0015061 | -0.00055975 | 0.0077514 | 0.016878 | 0.022063 | 0.030279 | -0.00046573 | 0.011014 | -0.0024738 | -0.21057 | 0.29755 | -123.0652 | 0.004578 | -122.168 | -122.7768 | -122.8409 | 0.054932 | 0.25177 | -0.054932 | 0.09613 | 0.1831 | 0.091553 | 0.23346 | -0.25635 | 0.045776 | -0.24719 | 0.64087 | -0.032043 | 0.032044 | 0.22431 | 0.28839 | 122.7539 | 0 | -0.15564 | 122.9919 | 123.0423 | 122.9004 | 0.28839 | 0.14649 | 0.89722 | 123.0698 | 0.23804 | 0.15106 | 123.3627 | 0.3067 | 123.1064 | 123.0606 | -123.317 | -0.3067 | 122.8134 | 122.905 | 122.5983 | 122.8638
560.5156 | 123.1659 | -122.8043 | 0.21515 | 0.011063 | 0.0038966 | 0.071081 | 0.066982 | 0.0028817 | -0.0036423 | -0.0016278 | -0.0014038 | 0.014101 | 0.019927 | 0.031988 | 0.00060247 | 0.0090918 | 8.9786e-05 | -0.30212 | 0.23804 | -123.0743 | 0.027466 | -122.1176 | -122.7127 | -122.7631 | 0.11444 | 0.20142 | -0.045776 | 0.15564 | 0.24719 | 0.16937 | 0.27924 | -0.27008 | 0.022888 | -0.18768 | 0.68664 | 0.041198 | 0.091552 | 0.31128 | 0.36163 | 122.7585 | -0.013733 | -0.059509 | 123.0515 | 123.0835 | 122.9736 | 0.32501 | 0.21515 | 0.95673 | 123.1018 | 0.29297 | 0.20142 | 123.3124 | 0.24719 | 123.0423 | 123.0057 | -123.2895 | -0.26093 | 122.8317 | 122.9599 | 122.5021 | 122.9187
562.1875 | 123.0469 | -122.8592 | 0.25177 | 0.0034333 | 0.0045374 | 0.070226 | 0.065059 | -0.0011771 | -0.0027877 | -0.00055975 | 0.001648 | 0.016878 | 0.020568 | 0.024511 | -0.0026019 | 0.010587 | -0.0035418 | -0.29755 | 0.25635 | -123.0881 | -0.059509 | -122.2183 | -122.7951 | -122.8638 | -0.013733 | 0.23804 | -0.059509 | 0.013733 | 0.1236 | 0.041199 | 0.15564 | -0.22888 | 0.004578 | -0.31128 | 0.64087 | -0.004578 | 0.064087 | 0.2243 | 0.29297 | 122.7997 | -0.013733 | -0.23804 | 122.9828 | 123.0148 | 122.9004 | 0.21515 | 0.10071 | 0.86975 | 123.0286 | 0.1831 | 0.073242 | 123.3444 | 0.29755 | 123.1155 | 123.0972 | -123.3398 | -0.31128 | 122.7997 | 122.8729 | 122.5616 | 122.8455
563.9375 | 123.0194 | -122.8409 | 0.22888 | 0.011063 | 0.0058192 | 0.071722 | 0.069759 | 0.0058725 | -0.0021469 | 0.00029485 | -0.0014038 | 0.018587 | 0.022063 | 0.031561 | 0.00081607 | 0.010587 | -0.0016192 | -0.23346 | 0.25635 | -123.0927 | -0.032043 | -122.2229 | -122.8271 | -122.8867 | 0.018311 | 0.23346 | -0.059509 | 0.059509 | 0.11902 | 0 | 0.17395 | -0.25177 | 0.027466 | -0.26093 | 0.61798 | -0.045777 | 0.013733 | 0.20599 | 0.2655 | 122.7814 | 0.004577 | -0.16937 | 122.9599 | 123.0148 | 122.8409 | 0.23346 | 0.059509 | 0.86975 | 123.0606 | 0.17853 | 0.11902 | 123.349 | 0.29297 | 123.0972 | 123.0743 | -123.3215 | -0.28839 | 122.8088 | 122.9004 | 122.6074 | 122.8592
565.625 | 123.0927 | -122.8226 | 0.22888 | 0.018692 | 0.0045374 | 0.070226 | 0.066127 | 0.0084359 | -0.0038559 | -0.00034615 | 0.001648 | 0.017306 | 0.018645 | 0.027929 | 0.0025251 | 0.0075964 | -0.0031146 | -0.20599 | 0.24719 | -123.1155 | -0.036621 | -122.1817 | -122.7814 | -122.8592 | 0.050354 | 0.2243 | -0.059509 | 0.082397 | 0.17395 | 0.059509 | 0.19684 | -0.29297 | 0.01831 | -0.2655 | 0.64087 | -0.036621 | 0.041199 | 0.25635 | 0.33417 | 122.7631 | -0.004578 | -0.14649 | 122.9965 | 123.0194 | 122.8821 | 0.25635 | 0.11902 | 0.93384 | 123.0789 | 0.23346 | 0.14191 | 123.3627 | 0.28381 | 123.0698 | 123.0469 | -123.3444 | -0.28839 | 122.7859 | 122.905 | 122.6166 | 122.8729
567.3594 | 123.024 | -122.85 | 0.23804 | 0.011063 | 0.0073144 | 0.069372 | 0.068263 | 0.0062997 | -0.0032151 | -0.002696 | -0.0014038 | 0.017092 | 0.0195 | 0.020239 | 0.0010297 | 0.01016 | -0.00033761 | -0.27466 | 0.26093 | -123.0972 | -0.054932 | -122.2321 | -122.8409 | -122.905 | -0.027466 | 0.24261 | -0.054932 | 0.050354 | 0.09613 | 0 | 0.16937 | -0.24719 | 0.022888 | -0.29297 | 0.61798 | -0.054931 | 0.009156 | 0.19226 | 0.25635 | 122.7951 | 0.004578 | -0.18768 | 122.9462 | 123.0194 | 122.85 | 0.22431 | 0.054932 | 0.86517 | 123.0423 | 0.15106 | 0.10529 | 123.3582 | 0.29755 | 123.111 | 123.0927 | -123.3353 | -0.29297 | 122.7951 | 122.9004 | 122.5754 | 122.8226
569.1094 | 123.1659 | -122.7997 | 0.20599 | 0.011063 | 0.0028284 | 0.071081 | 0.065913 | 0.0041635 | -0.00086509 | -0.00098695 | 0.001648 | 0.01346 | 0.020781 | 0.029852 | 0.0016705 | 0.009519 | 0.0017988 | -0.27924 | 0.24261 | -123.0606 | 0.022888 | -122.1313 | -122.7585 | -122.8088 | 0.11902 | 0.19226 | -0.036621 | 0.16937 | 0.2243 | 0.13275 | 0.28381 | -0.26093 | 0.036621 | -0.18311 | 0.66833 | -0.009155 | 0.041199 | 0.25177 | 0.30212 | 122.7631 | -0.013733 | -0.036621 | 123.024 | 123.0835 | 122.9324 | 0.32043 | 0.16937 | 0.92926 | 123.0835 | 0.26093 | 0.20599 | 123.3032 | 0.22888 | 123.0423 | 122.9919 | -123.2666 | -0.24262 | 122.8226 | 122.9691 | 122.5204 | 122.9187
570.8438 | 123.0423 | -122.8455 | 0.21973 | 0.011063 | 0.0058192 | 0.068945 | 0.066554 | 0.0052315 | -0.0012925 | -0.00034615 | 0.001648 | 0.017306 | 0.021636 | 0.026861 | -0.00089293 | 0.0099462 | 0.0017988 | -0.30212 | 0.25177 | -123.1064 | -0.09613 | -122.2733 | -122.8683 | -122.8867 | -0.018311 | 0.23346 | -0.07782 | 0.041199 | 0.09613 | 0 | 0.16479 | -0.26093 | 0.032043 | -0.31586 | 0.57221 | -0.041199 | -0.022888 | 0.21973 | 0.23804 | 122.7676 | 0.013732 | -0.17853 | 122.9416 | 123.0103 | 122.8455 | 0.24261 | 0.07782 | 0.83313 | 123.0103 | 0.17395 | 0.11902 | 123.3582 | 0.31128 | 123.0972 | 123.0789 | -123.3261 | -0.29755 | 122.7493 | 122.8867 | 122.5433 | 122.8271
572.5156 | 123.1705 | -122.8043 | 0.20599 | 0.0034333 | 0.0062464 | 0.070867 | 0.065273 | 0.0048043 | 0.00020291 | -0.0014142 | 0.0046998 | 0.014742 | 0.020354 | 0.032415 | 0.00038887 | 0.012083 | 0.00051699 | -0.25635 | 0.19226 | -123.0423 | 0.059509 | -122.1176 | -122.7402 | -122.7905 | 0.14191 | 0.20599 | -0.050354 | 0.16022 | 0.23804 | 0.13733 | 0.2655 | -0.23804 | -0.013733 | -0.14649 | 0.68664 | 0.013733 | 0.064087 | 0.25177 | 0.30212 | 122.7539 | 0 | -0.045777 | 123.0423 | 123.0698 | 122.9416 | 0.31586 | 0.18768 | 0.92468 | 123.1018 | 0.28839 | 0.21057 | 123.2346 | 0.25635 | 122.9965 | 123.0103 | -123.2483 | -0.25635 | 122.8638 | 122.9645 | 122.5479 | 122.9462
574.2656 | 123.0423 | -122.8363 | 0.23804 | 0.0034333 | 0.0049646 | 0.068304 | 0.065913 | 0.0077951 | 0.0010575 | -0.00098695 | 0.0046998 | 0.01816 | 0.020568 | 0.02857 | 0.00081607 | 0.011014 | -0.00055121 | -0.3067 | 0.27466 | -123.111 | -0.07782 | -122.2733 | -122.85 | -122.8867 | -0.018311 | 0.24261 | -0.054932 | 0.045776 | 0.086975 | 0.018311 | 0.17853 | -0.27466 | 0.036621 | -0.31586 | 0.56305 | -0.050354 | -0.013733 | 0.2243 | 0.26093 | 122.7814 | 0.004578 | -0.19226 | 122.9233 | 123.0148 | 122.8546 | 0.23346 | 0.073243 | 0.83771 | 123.0331 | 0.14191 | 0.10071 | 123.3856 | 0.29755 | 123.111 | 123.0789 | -123.349 | -0.29297 | 122.7585 | 122.8821 | 122.5296 | 122.818
576 | 123.1247 | -122.7905 | 0.2243 | -0.0041962 | 0.003042 | 0.071295 | 0.06335 | 0.0050179 | -0.0015061 | -0.00013235 | 0.001648 | 0.014956 | 0.021849 | 0.029852 | -0.00089293 | 0.011442 | 0.00094419 | -0.31586 | 0.23346 | -123.0652 | -0.004578 | -122.1542 | -122.7493 | -122.7951 | 0.082397 | 0.21515 | -0.032043 | 0.10986 | 0.20599 | 0.12817 | 0.24261 | -0.27466 | 0.009155 | -0.22888 | 0.63629 | -0.004578 | 0.041198 | 0.27008 | 0.31586 | 122.7585 | -0.009155 | -0.11444 | 122.9965 | 123.0331 | 122.9187 | 0.27466 | 0.16022 | 0.91095 | 123.0606 | 0.23804 | 0.14191 | 123.2986 | 0.24719 | 123.024 | 123.0057 | -123.2895 | -0.25635 | 122.7859 | 122.9004 | 122.4747 | 122.8729
577.75 | 123.1064 | -122.8088 | 0.2243 | -0.0041962 | 0.0034692 | 0.069799 | 0.063777 | 0.0030953 | -1.0686e-05 | -0.0014142 | 0.001648 | 0.015597 | 0.019072 | 0.025152 | -0.0019611 | 0.0090918 | -0.0022602 | -0.2243 | 0.22888 | -123.0743 | 0.036621 | -122.0993 | -122.7081 | -122.7814 | 0.09613 | 0.2243 | -0.059509 | 0.091553 | 0.20142 | 0.11902 | 0.2243 | -0.2655 | 0.004578 | -0.18768 | 0.70953 | 0.027466 | 0.10071 | 0.29297 | 0.36621 | 122.7493 | 0 | -0.13275 | 123.0103 | 123.0331 | 122.9279 | 0.28381 | 0.17853 | 0.97504 | 123.111 | 0.26093 | 0.15106 | 123.3032 | 0.28381 | 123.0377 | 123.0331 | -123.2986 | -0.28381 | 122.8455 | 122.9004 | 122.5845 | 122.905
579.5 | 123.0469 | -122.8317 | 0.21515 | -0.0041962 | 0.0043238 | 0.070226 | 0.066554 | 0.0035227 | -0.0027877 | -0.00055975 | 0.001648 | 0.017946 | 0.020568 | 0.023016 | 0.0020979 | 0.0099462 | 0.001585 | -0.32959 | 0.27924 | -123.0972 | -0.068665 | -122.2366 | -122.85 | -122.8867 | -0.013733 | 0.23346 | -0.068665 | 0.068665 | 0.11444 | 0.013733 | 0.1831 | -0.2655 | 0.064087 | -0.28381 | 0.59509 | -0.054932 | -0.018311 | 0.21057 | 0.24719 | 122.7631 | 0.01831 | -0.14648 | 122.9462 | 123.0148 | 122.8455 | 0.25177 | 0.082398 | 0.8606 | 123.0286 | 0.18311 | 0.13733 | 123.3765 | 0.30212 | 123.111 | 123.0652 | -123.3124 | -0.28381 | 122.7631 | 122.9004 | 122.5021 | 122.818
581.1719 | 123.143 | -122.8134 | 0.20599 | 0.0034333 | 0.0043238 | 0.070013 | 0.063991 | 0.0043771 | -0.0027877 | -0.00013235 | 0.0046998 | 0.016665 | 0.020781 | 0.031347 | -0.00025213 | 0.01016 | -0.00097841 | -0.32501 | 0.23346 | -123.0835 | 0.004578 | -122.1497 | -122.731 | -122.7814 | 0.07782 | 0.21057 | -0.064087 | 0.12817 | 0.2243 | 0.16022 | 0.25177 | -0.27008 | 0.027465 | -0.20142 | 0.66376 | 0.032044 | 0.082398 | 0.30212 | 0.35248 | 122.7493 | 0.004577 | -0.07782 | 123.0377 | 123.0652 | 122.9736 | 0.31586 | 0.2243 | 0.93384 | 123.0881 | 0.28839 | 0.19226 | 123.317 | 0.27466 | 123.0469 | 123.024 | -123.2895 | -0.27008 | 122.818 | 122.9416 | 122.4884 | 122.8912
582.9062 | 123.0835 | -122.8409 | 0.2243 | -0.0041962 | 0.0049646 | 0.070867 | 0.065913 | 0.0050179 | -0.0021469 | 0.00093565 | 0.0046998 | 0.017519 | 0.019927 | 0.018743 | -0.0043109 | 0.0073828 | 0.0028668 | -0.21973 | 0.21515 | -123.0835 | 0.036621 | -122.1222 | -122.7081 | -122.7631 | 0.07782 | 0.20599 | -0.059509 | 0.07782 | 0.16479 | 0.082397 | 0.18768 | -0.24262 | -0.009155 | -0.18768 | 0.71869 | 0.077819 | 0.13275 | 0.32043 | 0.37537 | 122.7814 | -0.01831 | -0.14648 | 123.0057 | 123.0286 | 122.9233 | 0.24719 | 0.14191 | 0.9613 | 123.1201 | 0.2243 | 0.13733 | 123.2986 | 0.2655 | 123.056 | 123.0469 | -123.3078 | -0.28381 | 122.8775 | 122.9187 | 122.6212 | 122.9187
584.5938 | 123.0377 | -122.8455 | 0.23804 | 0.0034333 | 0.0071008 | 0.070867 | 0.066341 | 0.0043771 | -0.0019333 | -0.00055975 | 0.0046998 | 0.019015 | 0.020995 | 0.029211 | -0.00025213 | 0.009519 | -0.0022602 | -0.2243 | 0.25177 | -123.1064 | -0.018311 | -122.2092 | -122.7951 | -122.8546 | 0.022888 | 0.23804 | -0.073242 | 0.050354 | 0.1236 | 0.013733 | 0.1831 | -0.26093 | 0.013733 | -0.25635 | 0.63629 | -0.009155 | 0.050354 | 0.25177 | 0.31128 | 122.7722 | 0 | -0.18768 | 122.9691 | 123.0286 | 122.8592 | 0.25635 | 0.086975 | 0.89722 | 123.0881 | 0.19684 | 0.1236 | 123.3582 | 0.31128 | 123.0972 | 123.0835 | -123.3444 | -0.31128 | 122.8271 | 122.8958 | 122.6212 | 122.8683
586.3438 | 123.0286 | -122.8409 | 0.21973 | 0.011063 | 0.0073144 | 0.071295 | 0.064845 | 0.0062997 | -0.0025741 | -0.00013235 | 0.0046998 | 0.015597 | 0.021422 | 0.027075 | 0.0016705 | 0.0093054 | 0.0020124 | -0.32044 | 0.26093 | -123.0972 | -0.086975 | -122.2641 | -122.8592 | -122.8958 | -0.018311 | 0.24719 | -0.091553 | 0.041199 | 0.09613 | -0.004578 | 0.16479 | -0.25635 | 0.041198 | -0.3067 | 0.57678 | -0.054932 | -0.018311 | 0.20142 | 0.23804 | 122.7493 | 0.027465 | -0.17853 | 122.937 | 123.0057 | 122.8363 | 0.25635 | 0.086975 | 0.83313 | 123.0103 | 0.18768 | 0.13275 | 123.3582 | 0.33874 | 123.1018 | 123.0881 | -123.317 | -0.31128 | 122.7539 | 122.8821 | 122.5204 | 122.8226
588.0938 | 122.9919 | -122.8546 | 0.23804 | 0.011063 | 0.0071008 | 0.071081 | 0.068263 | 0.0075815 | -0.0019333 | -0.0012006 | 0.001648 | 0.018587 | 0.022704 | 0.02622 | -0.00046573 | 0.0097326 | -0.00076481 | -0.28839 | 0.23346 | -123.0927 | -0.082397 | -122.2458 | -122.8592 | -122.9095 | -0.045776 | 0.22888 | -0.082397 | 0.004578 | 0.082397 | -0.009155 | 0.15106 | -0.23804 | -0.004578 | -0.32043 | 0.60882 | -0.054932 | -0.004578 | 0.1831 | 0.23346 | 122.7722 | -0.009155 | -0.23346 | 122.937 | 123.0057 | 122.8455 | 0.23346 | 0.073242 | 0.84686 | 123.0103 | 0.16479 | 0.086975 | 123.3261 | 0.31128 | 123.0881 | 123.0835 | -123.3307 | -0.32043 | 122.7722 | 122.8592 | 122.5662 | 122.8088
589.7812 | 123.0331 | -122.85 | 0.23346 | 0.018692 | 0.0024012 | 0.070013 | 0.064632 | 0.0022409 | -0.0027877 | 0.003499 | 0.0077514 | 0.020296 | 0.020995 | 0.031347 | -0.0030291 | 0.0099462 | 0.0030804 | -0.2655 | 0.25635 | -123.0972 | -0.07782 | -122.2504 | -122.8134 | -122.8775 | -0.022888 | 0.22888 | -0.091553 | 0.036621 | 0.10986 | 0.032043 | 0.15564 | -0.24719 | 0.022889 | -0.31128 | 0.59967 | -0.027465 | 0.036621 | 0.21973 | 0.28381 | 122.7585 | -0.004577 | -0.19684 | 122.9599 | 123.0057 | 122.8821 | 0.24719 | 0.1236 | 0.84686 | 123.0194 | 0.20142 | 0.12817 | 123.3536 | 0.32044 | 123.1064 | 123.0789 | -123.3307 | -0.32501 | 122.7722 | 122.8867 | 122.5845 | 122.8271
591.5156 | 122.9919 | -122.8363 | 0.23804 | 0.0034333 | 0.0058192 | 0.070867 | 0.066554 | 0.0035227 | 0.00063011 | -0.00055975 | 0.001648 | 0.018801 | 0.020781 | 0.020879 | -3.8532e-05 | 0.0075964 | -0.0014056 | -0.30212 | 0.25177 | -123.1018 | -0.09613 | -122.2824 | -122.85 | -122.9004 | -0.07782 | 0.22888 | -0.064087 | 0.027466 | 0.073242 | -0.013733 | 0.15106 | -0.2655 | 0.013733 | -0.33417 | 0.55389 | -0.064087 | -0.013733 | 0.20142 | 0.25177 | 122.7722 | -0.009155 | -0.21057 | 122.9095 | 122.9874 | 122.8226 | 0.21515 | 0.050354 | 0.8194 | 123.0057 | 0.13733 | 0.091553 | 123.3536 | 0.29297 | 123.0881 | 123.0652 | -123.3398 | -0.30212 | 122.7402 | 122.8638 | 122.5342 | 122.7585
593.2031 | 123.1659 | -122.8088 | 0.20599 | 0.011063 | 0.0045374 | 0.070654 | 0.062282 | 0.0048043 | -0.0032151 | 8.125e-05 | 0.001648 | 0.015597 | 0.021636 | 0.028356 | -0.00089293 | 0.01016 | 0.0017988 | -0.27924 | 0.21973 | -123.0652 | 0.045776 | -122.0627 | -122.6807 | -122.7356 | 0.13733 | 0.19226 | -0.050354 | 0.16022 | 0.27466 | 0.19226 | 0.27466 | -0.25635 | 0.013733 | -0.16022 | 0.74615 | 0.073242 | 0.12817 | 0.32959 | 0.38452 | 122.7585 | -0.013733 | -0.045777 | 123.0835 | 123.0835 | 123.0011 | 0.32501 | 0.24261 | 1.0025 | 123.111 | 0.32501 | 0.21057 | 123.2849 | 0.24261 | 123.0286 | 123.0011 | -123.2712 | -0.25635 | 122.8546 | 122.9691 | 122.5296 | 122.9462
594.9531 | 123.0286 | -122.8363 | 0.21515 | 0.0034333 | 0.0043238 | 0.072363 | 0.066982 | 0.0024545 | -0.0017197 | 0.0013628 | 0.001648 | 0.01581 | 0.020995 | 0.023229 | -3.8532e-05 | 0.01016 | -0.00097841 | -0.24261 | 0.2243 | -123.0927 | -0.027466 | -122.1863 | -122.7951 | -122.8683 | 0.018311 | 0.23346 | -0.073242 | 0.045776 | 0.1236 | 0.018311 | 0.16937 | -0.25635 | 0.009155 | -0.24261 | 0.65002 | -0.032043 | 0.041199 | 0.2243 | 0.29755 | 122.7631 | 0.01831 | -0.16937 | 122.9599 | 123.0057 | 122.8546 | 0.24261 | 0.091553 | 0.90637 | 123.0652 | 0.19684 | 0.11902 | 123.317 | 0.3067 | 123.0606 | 123.0698 | -123.3078 | -0.28839 | 122.8088 | 122.8821 | 122.5937 | 122.8546
596.6875 | 123.143 | -122.7951 | 0.1831 | 0.0034333 | 0.0028284 | 0.071081 | 0.062709 | 0.0030953 | -0.0027877 | -0.00098695 | 0.001648 | 0.015597 | 0.020568 | 0.02857 | 0.0014569 | 0.0093054 | 0.00051699 | -0.27924 | 0.21057 | -123.0377 | 0.018311 | -122.0993 | -122.6944 | -122.7539 | 0.13275 | 0.1831 | -0.054932 | 0.15106 | 0.25635 | 0.16479 | 0.25635 | -0.24261 | 0.027466 | -0.16479 | 0.6958 | 0.041199 | 0.10071 | 0.28381 | 0.34332 | 122.7402 | 0 | -0.032043 | 123.0515 | 123.0515 | 122.9599 | 0.31128 | 0.21973 | 0.93842 | 123.056 | 0.31128 | 0.20599 | 123.2483 | 0.23804 | 123.0057 | 122.9782 | -123.2208 | -0.23804 | 122.8134 | 122.9462 | 122.5159 | 122.9279
598.4375 | 123.0331 | -122.8409 | 0.24719 | 0.011063 | 0.0056054 | 0.068945 | 0.0657 | 0.0020273 | -0.0042831 | -0.00013235 | 0.001648 | 0.016665 | 0.021849 | 0.021734 | -0.0013201 | 0.0093054 | -0.0039692 | -0.2655 | 0.25635 | -123.0835 | -0.07782 | -122.2275 | -122.8043 | -122.8455 | -0.045776 | 0.23346 | -0.07782 | 0.036621 | 0.10529 | 0.013733 | 0.14648 | -0.24262 | 0.009156 | -0.32501 | 0.6134 | -0.004578 | 0.036621 | 0.23804 | 0.27924 | 122.7631 | -0.013733 | -0.21057 | 122.9462 | 122.9874 | 122.8546 | 0.2243 | 0.091553 | 0.85602 | 123.0057 | 0.18311 | 0.11444 | 123.3398 | 0.31128 | 123.0972 | 123.0743 | -123.3307 | -0.32501 | 122.7631 | 122.8775 | 122.5754 | 122.7951
600.125 | 123.0103 | -122.8546 | 0.2243 | 0.011063 | 0.004751 | 0.068945 | 0.066768 | 0.00095914 | -0.0027877 | -0.00055975 | -0.0014038 | 0.017092 | 0.021422 | 0.027075 | -0.00067933 | 0.009519 | -0.00076481 | -0.24261 | 0.2243 | -123.0743 | -0.018311 | -122.1497 | -122.7402 | -122.8134 | 0.018311 | 0.23804 | -0.064087 | 0.022888 | 0.12817 | 0.036621 | 0.16937 | -0.21973 | 0 | -0.24261 | 0.70496 | 0.041198 | 0.11444 | 0.26093 | 0.33417 | 122.7905 | 0.013733 | -0.20142 | 122.9828 | 123.024 | 122.8912 | 0.23346 | 0.10071 | 0.92468 | 123.056 | 0.19226 | 0.086975 | 123.2986 | 0.30212 | 123.0789 | 123.0927 | -123.2986 | -0.28839 | 122.8363 | 122.8775 | 122.612 | 122.8729
601.8594 | 123.1018 | -122.818 | 0.20599 | 0.0034333 | 0.0056054 | 0.071081 | 0.065059 | 0.0018137 | -0.0032151 | -0.002696 | 0.001648 | 0.015383 | 0.019072 | 0.031347 | -0.00089293 | 0.01016 | -0.00055121 | -0.31586 | 0.21057 | -123.056 | -0.009155 | -122.1725 | -122.7676 | -122.8088 | 0.050354 | 0.20599 | -0.068665 | 0.09613 | 0.18768 | 0.10071 | 0.23346 | -0.23804 | 0.004577 | -0.21515 | 0.64545 | 0.009155 | 0.050354 | 0.24719 | 0.28839 | 122.7493 | 0 | -0.10986 | 123.0057 | 123.0515 | 122.9187 | 0.30212 | 0.16937 | 0.88348 | 123.0469 | 0.25635 | 0.16479 | 123.2666 | 0.27466 | 123.0286 | 123.024 | -123.262 | -0.27466 | 122.8088 | 122.9141 | 122.5021 | 122.8683
603.5938 | 123.0835 | -122.818 | 0.20142 | 0.018692 | 0.0043238 | 0.068304 | 0.068477 | 0.0052315 | -0.0017197 | -0.00077335 | 0.0046998 | 0.016237 | 0.022704 | 0.025793 | 0.00081607 | 0.006742 | 0.00094419 | -0.28839 | 0.19684 | -123.0835 | 0 | -122.1497 | -122.7676 | -122.8043 | 0.07782 | 0.17395 | -0.068665 | 0.091553 | 0.16937 | 0.091553 | 0.20142 | -0.2655 | -0.004578 | -0.20142 | 0.66833 | 0.013733 | 0.050354 | 0.27924 | 0.31586 | 122.7493 | -0.027466 | -0.10986 | 122.9874 | 123.0194 | 122.9095 | 0.27008 | 0.16022 | 0.93384 | 123.0835 | 0.23804 | 0.16022 | 123.2803 | 0.24261 | 123.0148 | 122.9919 | -123.2849 | -0.27008 | 122.818 | 122.9095 | 122.5296 | 122.8958
605.2812 | 123.0881 | -122.8317 | 0.1831 | 0.018692 | 0.003042 | 0.070654 | 0.065913 | 0.0052315 | -0.0038559 | -0.00013235 | 0.0046998 | 0.018374 | 0.021849 | 0.023443 | -0.00089293 | 0.0090918 | -0.0014056 | -0.33875 | 0.19226 | -123.0835 | -0.036621 | -122.1863 | -122.7676 | -122.818 | 0.018311 | 0.17395 | -0.07782 | 0.073242 | 0.13275 | 0.068665 | 0.18768 | -0.25177 | 0.009156 | -0.21973 | 0.64545 | 0.013733 | 0.064087 | 0.2655 | 0.31586 | 122.7539 | -0.009155 | -0.10986 | 122.9645 | 123.0194 | 122.9004 | 0.2655 | 0.14649 | 0.89722 | 123.0469 | 0.21057 | 0.15106 | 123.2758 | 0.25177 | 123.024 | 123.0057 | -123.2666 | -0.26092 | 122.7951 | 122.905 | 122.493 | 122.85
607.0312 | 123.0606 | -122.8409 | 0.19684 | 0.0034333 | 0.0056054 | 0.071295 | 0.065059 | 0.0015999 | -0.0021469 | 0.00029485 | -0.0014038 | 0.017519 | 0.019713 | 0.026647 | 0.0012433 | 0.0080236 | 0.00073059 | -0.21515 | 0.21515 | -123.1201 | -0.041199 | -122.2 | -122.7905 | -122.8592 | 0.018311 | 0.20142 | -0.07782 | 0.032043 | 0.1236 | 0.036621 | 0.16937 | -0.27924 | 0.018311 | -0.23804 | 0.64087 | -0.018311 | 0.050354 | 0.26093 | 0.32959 | 122.7631 | 0.004578 | -0.1648 | 122.9645 | 123.0103 | 122.8775 | 0.24719 | 0.11444 | 0.9201 | 123.0789 | 0.20142 | 0.10986 | 123.3353 | 0.27924 | 123.056 | 123.0423 | -123.317 | -0.27466 | 122.7997 | 122.8729 | 122.6257 | 122.8592
608.7812 | 122.9919 | -122.8683 | 0.21515 | 0.0034333 | 0.0051782 | 0.069586 | 0.065486 | 0.0077951 | -0.0017197 | 0.0020038 | 0.001648 | 0.019655 | 0.021209 | 0.018957 | -0.0011065 | 0.011228 | 8.9786e-05 | -0.27924 | 0.21515 | -123.1293 | -0.12817 | -122.2824 | -122.8683 | -122.9324 | -0.086975 | 0.21515 | -0.12817 | -0.018311 | 0.032043 | -0.054932 | 0.11902 | -0.26093 | 0 | -0.34332 | 0.58594 | -0.064087 | 0 | 0.19684 | 0.26093 | 122.7402 | 0 | -0.23346 | 122.9004 | 122.9874 | 122.8134 | 0.24719 | 0.073242 | 0.84686 | 123.0011 | 0.16022 | 0.10986 | 123.3444 | 0.34332 | 123.0835 | 123.0835 | -123.3444 | -0.34332 | 122.7402 | 122.85 | 122.5891 | 122.7814
610.4688 | 123.0881 | -122.85 | 0.16937 | -0.0041962 | 0.0043238 | 0.069372 | 0.065273 | 0.0045907 | -0.00065149 | -0.0014142 | -0.0014038 | 0.013247 | 0.0195 | 0.022375 | -0.0028155 | 0.0099462 | 0.0011578 | -0.24719 | 0.17853 | -123.0743 | 0 | -122.1313 | -122.7219 | -122.7859 | 0.036621 | 0.17853 | -0.091553 | 0.059509 | 0.16022 | 0.073242 | 0.17395 | -0.2243 | 0.009155 | -0.16937 | 0.71869 | 0.064087 | 0.12817 | 0.28839 | 0.35248 | 122.7585 | 0.009155 | -0.10986 | 123.0103 | 123.024 | 122.9233 | 0.2655 | 0.16479 | 0.94299 | 123.0743 | 0.25177 | 0.15106 | 123.2529 | 0.27008 | 123.0286 | 123.0286 | -123.2437 | -0.26093 | 122.85 | 122.9095 | 122.6028 | 122.8867
612.2188 | 123.0194 | -122.8775 | 0.18768 | 0.011063 | 0.0058192 | 0.069372 | 0.065273 | 0.0033089 | -0.0021469 | 0.0017902 | 0.001648 | 0.017092 | 0.021209 | 0.021948 | -0.0019611 | 0.0086646 | 0.003294 | -0.27008 | 0.23346 | -123.1384 | -0.10529 | -122.2595 | -122.8363 | -122.8958 | -0.068665 | 0.21057 | -0.13275 | -0.009155 | 0.082397 | -0.013733 | 0.12817 | -0.26093 | 0.045776 | -0.29297 | 0.61798 | -0.018311 | 0.041198 | 0.24262 | 0.30212 | 122.7448 | 0.022888 | -0.19684 | 122.9599 | 123.0057 | 122.8638 | 0.26093 | 0.11902 | 0.87891 | 123.0331 | 0.21515 | 0.1236 | 123.3719 | 0.34332 | 123.111 | 123.0881 | -123.3261 | -0.32043 | 122.7722 | 122.8683 | 122.6074 | 122.8088
613.9062 | 123.1247 | -122.8043 | 0.17395 | 0.011063 | 0.0036828 | 0.070867 | 0.06335 | 0.0015999 | -0.0040695 | -0.00034615 | 0.0046998 | 0.01581 | 0.020995 | 0.034765 | 0.0020979 | 0.0088782 | -0.0039692 | -0.29297 | 0.17853 | -123.1018 | -0.009155 | -122.113 | -122.7264 | -122.7814 | 0.086975 | 0.16022 | -0.09613 | 0.11444 | 0.23346 | 0.12817 | 0.23804 | -0.29755 | 0.004578 | -0.1831 | 0.69122 | 0.022888 | 0.07782 | 0.32043 | 0.37537 | 122.7081 | -0.013733 | -0.059509 | 123.0377 | 123.0423 | 122.9324 | 0.33417 | 0.2243 | 0.98877 | 123.0927 | 0.32959 | 0.21057 | 123.2803 | 0.25635 | 122.9828 | 122.9645 | -123.2758 | -0.27008 | 122.7951 | 122.9187 | 122.5113 | 122.8912
615.6406 | 123.1247 | -122.8409 | 0.16022 | 0.011063 | 0.0060328 | 0.069799 | 0.065059 | 0.0033089 | -0.0032151 | -0.0022688 | 0.001648 | 0.015383 | 0.018859 | 0.028997 | -0.00025213 | 0.0090918 | -0.001192 | -0.32044 | 0.17395 | -123.0743 | -0.045776 | -122.1817 | -122.7539 | -122.818 | 0.018311 | 0.16937 | -0.09613 | 0.082397 | 0.16937 | 0.086975 | 0.19684 | -0.23346 | 0.013733 | -0.20599 | 0.65918 | 0.022888 | 0.086975 | 0.25635 | 0.32044 | 122.7448 | 0.009156 | -0.07782 | 123.0103 | 123.0377 | 122.9279 | 0.29297 | 0.1831 | 0.89264 | 123.0286 | 0.2655 | 0.17853 | 123.2483 | 0.2655 | 123.0148 | 123.0103 | -123.2346 | -0.25635 | 122.7951 | 122.9233 | 122.5204 | 122.8592
617.3906 | 123.0606 | -122.8363 | 0.19684 | 0.011063 | 0.004751 | 0.071081 | 0.068904 | 0.0030953 | -0.0044967 | -0.00098695 | 0.001648 | 0.017733 | 0.020568 | 0.03327 | -0.0013201 | 0.0080236 | 0.00094419 | -0.23346 | 0.21515 | -123.143 | -0.054932 | -122.2321 | -122.7951 | -122.8455 | -0.013733 | 0.19684 | -0.09613 | 0.036621 | 0.12817 | 0.027466 | 0.15106 | -0.3067 | 0.018311 | -0.25177 | 0.60425 | -0.009155 | 0.041199 | 0.29755 | 0.3479 | 122.7402 | 0 | -0.16022 | 122.9645 | 122.9874 | 122.8638 | 0.24719 | 0.1236 | 0.91095 | 123.0881 | 0.2243 | 0.13275 | 123.3582 | 0.29297 | 123.0515 | 123.0331 | -123.3398 | -0.29297 | 122.7814 | 122.8729 | 122.6028 | 122.8226
619.0781 | 123.0194 | -122.8729 | 0.19226 | 0.011063 | 0.0032556 | 0.070226 | 0.0657 | 0.0035227 | -0.0036423 | 0.00050845 | 0.001648 | 0.017946 | 0.022277 | 0.021734 | -0.0045245 | 0.0088782 | -0.00033761 | -0.23346 | 0.17853 | -123.1018 | -0.045776 | -122.168 | -122.7631 | -122.818 | -0.009155 | 0.19684 | -0.09613 | -0.004578 | 0.09613 | 0.013733 | 0.13275 | -0.22888 | -0.013733 | -0.23804 | 0.70496 | 0.054932 | 0.10986 | 0.28381 | 0.33874 | 122.7768 | 0.004577 | -0.19684 | 122.9691 | 123.0057 | 122.8867 | 0.22888 | 0.10986 | 0.93384 | 123.056 | 0.19226 | 0.091552 | 123.2803 | 0.29297 | 123.0515 | 123.0698 | -123.2941 | -0.28839 | 122.8271 | 122.8683 | 122.6395 | 122.8638
620.8125 | 123.0148 | -122.85 | 0.20599 | 0.011063 | 0.0049646 | 0.071081 | 0.067409 | 0.0067269 | -0.00043789 | -0.00013235 | 0.001648 | 0.019015 | 0.022277 | 0.024725 | 0.0016705 | 0.0088782 | -0.002901 | -0.30212 | 0.23346 | -123.1064 | -0.11902 | -122.2595 | -122.8546 | -122.905 | -0.059509 | 0.17853 | -0.14191 | 0.004578 | 0.059509 | -0.013733 | 0.11902 | -0.25635 | 0.027465 | -0.32501 | 0.59052 | -0.054931 | -0.004577 | 0.20142 | 0.25177 | 122.7081 | -0.027466 | -0.20142 | 122.9095 | 122.9691 | 122.8363 | 0.26093 | 0.12817 | 0.84686 | 122.9874 | 0.20142 | 0.14649 | 123.3398 | 0.32044 | 123.0835 | 123.0286 | -123.3124 | -0.3479 | 122.731 | 122.8546 | 122.5479 | 122.7905
622.5625 | 123.1338 | -122.8271 | 0.15564 | -0.0041962 | 0.0019738 | 0.070013 | 0.064632 | 0.0033089 | -0.0032151 | -0.002696 | 0.0046998 | 0.015383 | 0.019286 | 0.034338 | -0.0013201 | 0.010801 | 0.001585 | -0.31586 | 0.20142 | -123.0652 | -0.022888 | -122.1542 | -122.7448 | -122.7905 | 0.054932 | 0.17395 | -0.091553 | 0.091553 | 0.20599 | 0.10986 | 0.23346 | -0.23804 | 0.045776 | -0.17853 | 0.67291 | 0.036621 | 0.082397 | 0.27466 | 0.32044 | 122.7356 | 0.01831 | -0.064087 | 123.0331 | 123.0606 | 122.937 | 0.32501 | 0.20142 | 0.91095 | 123.0423 | 0.29755 | 0.18311 | 123.2666 | 0.2655 | 123.0286 | 123.0011 | -123.2208 | -0.24719 | 122.8043 | 122.9187 | 122.5113 | 122.8821
624.25 | 123.1293 | -122.7951 | 0.16937 | 0.011063 | 0.0041102 | 0.068945 | 0.067195 | 0.0048043 | -0.0023605 | -0.0018414 | -0.0014038 | 0.016878 | 0.018004 | 0.032201 | 0.0038067 | 0.0097326 | 0.0024396 | -0.27008 | 0.17853 | -123.056 | 0.009155 | -122.1405 | -122.7264 | -122.8043 | 0.082397 | 0.16937 | -0.07782 | 0.11444 | 0.20142 | 0.10529 | 0.23346 | -0.26093 | 0.009155 | -0.16022 | 0.6546 | -0.009155 | 0.068665 | 0.25177 | 0.32959 | 122.7173 | 0 | -0.054932 | 122.9965 | 123.0286 | 122.9004 | 0.31128 | 0.18311 | 0.91553 | 123.0652 | 0.27924 | 0.19226 | 123.2346 | 0.24719 | 122.9736 | 122.9645 | -123.2254 | -0.24719 | 122.8043 | 122.9095 | 122.525 | 122.8775
626 | 123.0515 | -122.8546 | 0.17395 | 0.018692 | 0.0060328 | 0.071081 | 0.068904 | 0.0015999 | -0.0030015 | -0.00077335 | 0.0077514 | 0.02051 | 0.021422 | 0.021948 | 0.0012433 | 0.0080236 | 0.00030339 | -0.21973 | 0.21057 | -123.1155 | -0.041199 | -122.1863 | -122.7859 | -122.8271 | 0.027466 | 0.19684 | -0.086975 | 0.041199 | 0.14191 | 0.032043 | 0.17853 | -0.26093 | 0.036621 | -0.21515 | 0.66833 | 0.027466 | 0.068664 | 0.28839 | 0.32959 | 122.7676 | 0.022888 | -0.13275 | 122.9965 | 123.0331 | 122.8867 | 0.2655 | 0.11902 | 0.92926 | 123.0743 | 0.22888 | 0.12817 | 123.3261 | 0.28381 | 123.0652 | 123.0515 | -123.2895 | -0.26092 | 122.8134 | 122.8958 | 122.6349 | 122.8821
627.75 | 123.1064 | -122.8363 | 0.16479 | 0.011063 | 0.0062464 | 0.070867 | 0.067622 | 0.0058725 | -0.00043789 | -0.0016278 | -0.0014038 | 0.016024 | 0.020354 | 0.027715 | 0.00060247 | 0.01016 | 0.0030804 | -0.32044 | 0.20599 | -123.1201 | -0.086975 | -122.2183 | -122.8271 | -122.8683 | 0 | 0.20599 | -0.10071 | 0.073242 | 0.14191 | 0.054932 | 0.19684 | -0.28381 | 0.041199 | -0.25177 | 0.61798 | -0.032043 | 0.009156 | 0.25177 | 0.29297 | 122.7356 | 0.041199 | -0.091553 | 122.9782 | 123.0331 | 122.8912 | 0.29755 | 0.15564 | 0.90179 | 123.0331 | 0.24262 | 0.17395 | 123.3261 | 0.3067 | 123.0423 | 123.0423 | -123.2849 | -0.2655 | 122.7493 | 122.9095 | 122.5159 | 122.8363
629.4375 | 123.0011 | -122.818 | 0.18768 | 0.0034333 | 0.007528 | 0.071508 | 0.067409 | 0.0050179 | -0.00022429 | 8.125e-05 | 0.001648 | 0.016878 | 0.02014 | 0.021307 | -0.00067933 | 0.010801 | 0.00051699 | -0.26093 | 0.20599 | -123.111 | -0.091553 | -122.2229 | -122.8317 | -122.9004 | -0.064087 | 0.20599 | -0.11444 | -0.004578 | 0.064087 | -0.022888 | 0.10071 | -0.29297 | 0.018311 | -0.27924 | 0.59509 | -0.082398 | -0.013733 | 0.21057 | 0.27924 | 122.7036 | 0.018311 | -0.19226 | 122.8821 | 122.9187 | 122.7951 | 0.21515 | 0.091553 | 0.88806 | 123.0194 | 0.17853 | 0.10986 | 123.317 | 0.32044 | 123.024 | 123.024 | -123.2986 | -0.30212 | 122.7264 | 122.8134 | 122.5571 | 122.7539
631.1875 | 123.1155 | -122.8226 | 0.17395 | 0.0034333 | 0.0038966 | 0.070867 | 0.064204 | -0.0011771 | 0.00020291 | -0.0020552 | 0.0046998 | 0.016024 | 0.020354 | 0.033483 | -0.0021747 | 0.010587 | 0.00051699 | -0.33417 | 0.18768 | -123.1018 | -0.027466 | -122.1588 | -122.7539 | -122.7951 | 0.027466 | 0.16937 | -0.086975 | 0.07782 | 0.17853 | 0.10529 | 0.20599 | -0.27924 | 0.013733 | -0.20142 | 0.66376 | 0.027466 | 0.068665 | 0.3067 | 0.3479 | 122.7356 | -0.004577 | -0.09613 | 123.0011 | 123.0286 | 122.9279 | 0.29297 | 0.19226 | 0.94299 | 123.0743 | 0.2655 | 0.16479 | 123.2895 | 0.25635 | 123.0103 | 122.9919 | -123.2758 | -0.26092 | 122.7951 | 122.9004 | 122.4884 | 122.85
632.9219 | 123.1155 | -122.8317 | 0.16479 | 0.0034333 | 0.0026148 | 0.069372 | 0.065059 | 0.0013863 | -0.0023605 | -0.0024824 | 0.001648 | 0.01581 | 0.022277 | 0.034979 | -0.0013201 | 0.0088782 | 0.0062848 | -0.30212 | 0.17853 | -123.0652 | -0.018311 | -122.1405 | -122.7264 | -122.7722 | 0.059509 | 0.16479 | -0.091553 | 0.091553 | 0.18768 | 0.11902 | 0.24261 | -0.23346 | 0.013733 | -0.18311 | 0.69122 | 0.059509 | 0.10529 | 0.29297 | 0.33875 | 122.7402 | 0 | -0.073242 | 123.0194 | 123.0743 | 122.9507 | 0.33417 | 0.21057 | 0.92468 | 123.0469 | 0.27924 | 0.18311 | 123.2437 | 0.25635 | 123.0103 | 122.9965 | -123.23 | -0.25635 | 122.8134 | 122.9233 | 122.5296 | 122.8912
634.6094 | 123.0011 | -122.85 | 0.21057 | 0.0034333 | 0.0041102 | 0.071295 | 0.066127 | 0.0028817 | -0.0021469 | -0.0012006 | 0.0077514 | 0.018587 | 0.021422 | 0.024084 | 0.0020979 | 0.0097326 | -0.00076481 | -0.29755 | 0.21057 | -123.1155 | -0.11902 | -122.2687 | -122.8683 | -122.9141 | -0.068665 | 0.19684 | -0.10986 | -0.018311 | 0.045776 | -0.041199 | 0.1236 | -0.2655 | 0 | -0.32959 | 0.58136 | -0.064087 | -0.01831 | 0.20142 | 0.24719 | 122.7402 | -0.013733 | -0.22888 | 122.8958 | 122.9736 | 122.8088 | 0.23346 | 0.068664 | 0.84686 | 122.9965 | 0.15564 | 0.091552 | 123.3261 | 0.3067 | 123.0606 | 123.0469 | -123.3261 | -0.32043 | 122.731 | 122.8317 | 122.5525 | 122.7814
636.3438 | 123.0423 | -122.818 | 0.20142 | -0.0041962 | 0.0062464 | 0.070013 | 0.067409 | 0.0041635 | -0.0049241 | 0.00072205 | 0.010803 | 0.015169 | 0.020568 | 0.015112 | -0.0028155 | 0.0088782 | -0.0035418 | -0.25177 | 0.24261 | -123.1064 | -0.086975 | -122.2183 | -122.7768 | -122.8455 | -0.045776 | 0.2243 | -0.10529 | 0.027466 | 0.10986 | 0.022888 | 0.16937 | -0.28839 | 0.041199 | -0.28839 | 0.59967 | -0.027466 | 0.041199 | 0.26093 | 0.32959 | 122.7127 | 0.022888 | -0.17395 | 122.9279 | 122.9874 | 122.8409 | 0.27466 | 0.12817 | 0.88806 | 123.0194 | 0.21515 | 0.13275 | 123.349 | 0.32959 | 123.0606 | 123.0423 | -123.3078 | -0.3067 | 122.731 | 122.8455 | 122.5662 | 122.7722
638.0312 | 123.0057 | -122.818 | 0.22888 | -0.019455 | 0.0028284 | 0.070226 | 0.066768 | 0.0065133 | -0.0023605 | -0.0014142 | 0.0046998 | 0.016665 | 0.020995 | 0.026647 | 0.00038887 | 0.0082374 | -0.00012381 | -0.3067 | 0.23346 | -123.0698 | -0.10986 | -122.2549 | -122.85 | -122.8683 | -0.059509 | 0.21057 | -0.086975 | 0.022888 | 0.068665 | -0.013733 | 0.15106 | -0.25177 | 0.004577 | -0.33875 | 0.56305 | -0.050354 | -0.032044 | 0.20142 | 0.21973 | 122.731 | -0.018311 | -0.20599 | 122.8867 | 122.9691 | 122.8043 | 0.23804 | 0.073242 | 0.81482 | 122.9599 | 0.15564 | 0.10986 | 123.3032 | 0.29755 | 123.0515 | 123.0286 | -123.2986 | -0.31586 | 122.7081 | 122.8409 | 122.5113 | 122.7585
639.7812 | 123.1201 | -122.7951 | 0.18768 | 0.011063 | 0.0026148 | 0.072363 | 0.064845 | 0.0067269 | -0.0017197 | 0.0011492 | -0.0014038 | 0.014956 | 0.022063 | 0.031347 | -0.0023883 | 0.0088782 | 0.001585 | -0.33417 | 0.19684 | -123.0698 | -0.009155 | -122.1359 | -122.7219 | -122.7676 | 0.050354 | 0.19226 | -0.068665 | 0.11444 | 0.21515 | 0.12817 | 0.23346 | -0.27466 | 0.009155 | -0.19684 | 0.65918 | 0.027466 | 0.073242 | 0.30212 | 0.3479 | 122.7264 | 0.004578 | -0.073242 | 123.0103 | 123.0286 | 122.9233 | 0.30212 | 0.19684 | 0.93384 | 123.0606 | 0.28381 | 0.18311 | 123.2666 | 0.26093 | 122.9919 | 122.9874 | -123.2574 | -0.25635 | 122.7859 | 122.9095 | 122.4609 | 122.8455
641.4531 | 123.0423 | -122.8088 | 0.21973 | 0.026321 | 0.0045374 | 0.06809 | 0.065486 | 0.0022409 | -0.00086509 | -0.00098695 | 0.0046998 | 0.018587 | 0.020781 | 0.022588 | -0.0011065 | 0.0082374 | -0.002901 | -0.26093 | 0.24719 | -123.0972 | -0.059509 | -122.1725 | -122.7402 | -122.818 | -0.013733 | 0.21973 | -0.091553 | 0.041199 | 0.12817 | 0.045776 | 0.17395 | -0.28839 | 0.027465 | -0.27924 | 0.63629 | -0.009155 | 0.068665 | 0.27924 | 0.35706 | 122.7173 | 0 | -0.17853 | 122.937 | 122.9828 | 122.8546 | 0.2655 | 0.13733 | 0.92468 | 123.0377 | 0.21973 | 0.13275 | 123.3444 | 0.31128 | 123.056 | 123.0286 | -123.317 | -0.31128 | 122.7493 | 122.85 | 122.5479 | 122.7951
643.1406 | 123.1338 | -122.7814 | 0.18768 | -0.011826 | 0.0060328 | 0.070226 | 0.064418 | 0.0039499 | -0.0025741 | -0.00098695 | 0.001648 | 0.017306 | 0.022063 | 0.031774 | -0.00067933 | 0.0097326 | -0.00033761 | -0.29755 | 0.21515 | -123.0515 | 0.027466 | -122.081 | -122.6715 | -122.7264 | 0.11444 | 0.19226 | -0.068665 | 0.14191 | 0.26093 | 0.15564 | 0.26093 | -0.27008 | 0.027466 | -0.16022 | 0.70038 | 0.054932 | 0.10986 | 0.32501 | 0.37994 | 122.7127 | 0.004578 | -0.045776 | 123.0423 | 123.0423 | 122.937 | 0.32959 | 0.22431 | 0.97046 | 123.0789 | 0.32959 | 0.21057 | 123.2666 | 0.26093 | 122.9965 | 122.9736 | -123.2391 | -0.25635 | 122.8088 | 122.9233 | 122.4838 | 122.8958
644.8906 | 122.9919 | -122.8363 | 0.21973 | 0.018692 | 0.0056054 | 0.069158 | 0.067409 | 0.0062997 | -0.0032151 | -0.00055975 | 0.0077514 | 0.016665 | 0.019072 | 0.026006 | -0.00046573 | 0.0086646 | 0.00094419 | -0.27008 | 0.2655 | -123.0972 | -0.07782 | -122.2137 | -122.7814 | -122.8363 | -0.045776 | 0.21973 | -0.086975 | 0.018311 | 0.09613 | 0.013733 | 0.15106 | -0.26093 | 0.045776 | -0.29755 | 0.62256 | 0 | 0.054932 | 0.26093 | 0.31586 | 122.7493 | 0 | -0.20142 | 122.9324 | 122.9874 | 122.85 | 0.23804 | 0.10071 | 0.88348 | 123.0194 | 0.1831 | 0.10529 | 123.3627 | 0.3067 | 123.1018 | 123.056 | -123.317 | -0.3067 | 122.7585 | 122.8546 | 122.5662 | 122.7905
646.5781 | 123.1064 | -122.7676 | 0.1831 | 0.018692 | 0.0049646 | 0.071722 | 0.063777 | 0.0041635 | -0.00022429 | 0.002431 | -0.0014038 | 0.018587 | 0.021849 | 0.030706 | 0.0031659 | 0.010587 | -0.00012381 | -0.2655 | 0.20599 | -123.0194 | 0.036621 | -122.0673 | -122.7081 | -122.7356 | 0.1236 | 0.17395 | -0.064087 | 0.15106 | 0.21515 | 0.11444 | 0.22888 | -0.25177 | 0.022889 | -0.14648 | 0.70038 | 0.032043 | 0.059509 | 0.28381 | 0.31128 | 122.7036 | -0.009155 | -0.032043 | 122.9828 | 122.9965 | 122.8821 | 0.29297 | 0.17853 | 0.95215 | 123.056 | 0.27924 | 0.21515 | 123.2254 | 0.23804 | 122.9736 | 122.9416 | -123.2025 | -0.24719 | 122.8043 | 122.9187 | 122.5021 | 122.8912
648.2656 | 122.9691 | -122.8226 | 0.23346 | 0.0034333 | 0.004751 | 0.072149 | 0.067195 | 0.0050179 | -0.00043789 | 0.0013628 | -0.0014038 | 0.017519 | 0.022063 | 0.019598 | 0.0020979 | 0.009519 | -0.0018328 | -0.29297 | 0.24261 | -123.0698 | -0.086975 | -122.2824 | -122.8409 | -122.8867 | -0.054932 | 0.23346 | -0.091553 | 0 | 0.050354 | -0.013733 | 0.13733 | -0.24719 | 0.009156 | -0.32043 | 0.54016 | -0.064087 | -0.01831 | 0.1831 | 0.22888 | 122.731 | 0 | -0.23346 | 122.8729 | 122.9599 | 122.8088 | 0.22888 | 0.07782 | 0.78735 | 122.9828 | 0.14191 | 0.091553 | 123.3124 | 0.32501 | 123.0652 | 123.056 | -123.3032 | -0.32501 | 122.7356 | 122.8226 | 122.5296 | 122.7676
650.0156 | 123.0927 | -122.7859 | 0.18768 | -0.0041962 | 0.0058192 | 0.070226 | 0.062068 | 0.0052315 | -0.0032151 | -0.00034615 | 0.001648 | 0.015169 | 0.022704 | 0.026647 | -0.00089293 | 0.0065284 | -0.00012381 | -0.24719 | 0.20599 | -123.0515 | 0.045776 | -122.0627 | -122.6669 | -122.731 | 0.09613 | 0.18768 | -0.068665 | 0.11444 | 0.21973 | 0.14191 | 0.2243 | -0.2655 | 0.018311 | -0.14191 | 0.72327 | 0.054932 | 0.11902 | 0.32043 | 0.38452 | 122.7173 | 0 | -0.073242 | 123.0057 | 123.0103 | 122.9279 | 0.29297 | 0.21057 | 0.98877 | 123.0972 | 0.28839 | 0.18311 | 123.2574 | 0.25635 | 122.9919 | 122.9736 | -123.2391 | -0.25635 | 122.8317 | 122.9004 | 122.5388 | 122.8821
651.75 | 123.0057 | -122.818 | 0.21515 | 0.0034333 | 0.0056054 | 0.071081 | 0.062068 | 0.00095914 | -0.0025741 | 0.00029485 | -0.0014038 | 0.016237 | 0.020995 | 0.01853 | -0.0028155 | 0.0090918 | -0.001192 | -0.2655 | 0.21515 | -123.0652 | -0.045776 | -122.1634 | -122.7448 | -122.8043 | -0.022888 | 0.21973 | -0.07782 | 0.018311 | 0.1236 | 0.027466 | 0.13275 | -0.24719 | 0 | -0.26093 | 0.6546 | 0.013733 | 0.073242 | 0.26093 | 0.32044 | 122.7402 | 0.004578 | -0.19684 | 122.9416 | 122.9507 | 122.8455 | 0.21057 | 0.10529 | 0.90179 | 123.0194 | 0.20142 | 0.096131 | 123.2803 | 0.29755 | 123.0331 | 123.0377 | -123.2803 | -0.29297 | 122.7722 | 122.8363 | 122.5525 | 122.7951
653.5 | 123.1064 | -122.7631 | 0.17395 | 0.011063 | 0.0045374 | 0.069799 | 0.065486 | 0.0013863 | -0.0025741 | -0.00077335 | 0.001648 | 0.016237 | 0.020781 | 0.026434 | 0.0020979 | 0.0093054 | -0.002901 | -0.30212 | 0.21973 | -123.0469 | -0.013733 | -122.1313 | -122.731 | -122.7951 | 0.086975 | 0.19226 | -0.059509 | 0.14648 | 0.20142 | 0.10071 | 0.24719 | -0.28381 | 0.045777 | -0.18768 | 0.63171 | -0.032043 | 0.032044 | 0.25177 | 0.31586 | 122.7036 | 0.018311 | -0.027466 | 122.9645 | 123.0103 | 122.8638 | 0.3067 | 0.16022 | 0.91553 | 123.0331 | 0.26093 | 0.20599 | 123.2666 | 0.25177 | 122.9828 | 122.9553 | -123.2208 | -0.23346 | 122.7493 | 122.9095 | 122.4609 | 122.85
655.2031 | 123.0652 | -122.7859 | 0.19226 | -0.0041962 | 0.004751 | 0.070013 | 0.066982 | 0.0035227 | -0.0012925 | 0.00050845 | 0.0046998 | 0.018587 | 0.018218 | 0.030493 | 0.0014569 | 0.010374 | 0.00094419 | -0.32959 | 0.24719 | -123.0743 | -0.073242 | -122.1954 | -122.8088 | -122.8363 | 0.018311 | 0.21057 | -0.086975 | 0.082397 | 0.14648 | 0.073242 | 0.21515 | -0.28839 | 0.054931 | -0.2655 | 0.59051 | -0.050354 | -0.022888 | 0.23804 | 0.2655 | 122.699 | 0.01831 | -0.10986 | 122.9324 | 123.0011 | 122.8592 | 0.30212 | 0.16022 | 0.87891 | 123.0011 | 0.23346 | 0.16937 | 123.3215 | 0.29755 | 123.0331 | 122.9965 | -123.2666 | -0.27924 | 122.7127 | 122.8683 | 122.4564 | 122.8043
656.9375 | 123.0011 | -122.8226 | 0.20599 | 0.0034333 | 0.0058192 | 0.071081 | 0.066341 | 0.0050179 | -0.0023605 | -0.0029096 | -0.0014038 | 0.017733 | 0.021849 | 0.026434 | -0.00046573 | 0.011869 | 0.003294 | -0.32959 | 0.23346 | -123.111 | -0.09613 | -122.2366 | -122.8271 | -122.8683 | -0.045776 | 0.2243 | -0.091553 | 0.022888 | 0.068665 | -0.032043 | 0.15106 | -0.28839 | 0.027465 | -0.30212 | 0.58594 | -0.045776 | -0.004577 | 0.24262 | 0.28381 | 122.731 | 0.01831 | -0.18311 | 122.8912 | 122.9736 | 122.7905 | 0.24261 | 0.05951 | 0.87433 | 123.0148 | 0.16022 | 0.11444 | 123.3444 | 0.31586 | 123.056 | 123.0469 | -123.317 | -0.29755 | 122.7264 | 122.8455 | 122.493 | 122.7768
658.6719 | 123.0331 | -122.8088 | 0.21973 | 0.0034333 | 0.0043238 | 0.072363 | 0.065913 | 0.0043771 | -0.0012925 | 0.00050845 | -0.0014038 | 0.01816 | 0.02014 | 0.018316 | -0.0019611 | 0.0080236 | 0.0024396 | -0.24719 | 0.24261 | -123.0515 | -0.022888 | -122.1405 | -122.7539 | -122.7951 | 0.032043 | 0.2243 | -0.082397 | 0.068665 | 0.13275 | 0.045776 | 0.1831 | -0.24262 | 0.022888 | -0.24261 | 0.66833 | 0.013733 | 0.054932 | 0.25635 | 0.29755 | 122.7264 | 0.004577 | -0.15106 | 122.9416 | 122.9919 | 122.8546 | 0.2655 | 0.12817 | 0.91095 | 123.0286 | 0.21515 | 0.15106 | 123.2941 | 0.3067 | 123.0515 | 123.0331 | -123.2712 | -0.30212 | 122.7859 | 122.8775 | 122.5616 | 122.8409
660.3594 | 122.9874 | -122.7859 | 0.21515 | 0.018692 | 0.0068872 | 0.071295 | 0.067409 | 0.0067269 | -0.0027877 | -0.0012006 | 0.0046998 | 0.018801 | 0.022917 | 0.02622 | 0.00081607 | 0.0097326 | -0.00097841 | -0.27008 | 0.21973 | -123.0652 | -0.091553 | -122.2137 | -122.8088 | -122.8683 | -0.041199 | 0.22888 | -0.09613 | 0.013733 | 0.073242 | -0.018311 | 0.14648 | -0.27924 | 0.004578 | -0.3067 | 0.5722 | -0.082397 | -0.022888 | 0.19684 | 0.25635 | 122.6898 | 0.013733 | -0.20142 | 122.8592 | 122.9324 | 122.7676 | 0.24261 | 0.077819 | 0.85144 | 122.9736 | 0.16937 | 0.10986 | 123.2849 | 0.32501 | 123.0057 | 123.0148 | -123.2803 | -0.31128 | 122.6944 | 122.7997 | 122.5159 | 122.7448
662.0938 | 123.0881 | -122.7768 | 0.19684 | -0.0041962 | 0.00646 | 0.071081 | 0.065273 | 0.0067269 | -0.0019333 | 8.125e-05 | 0.001648 | 0.017092 | 0.019072 | 0.029424 | -0.00046573 | 0.010801 | 0.002226 | -0.29755 | 0.21057 | -123.0377 | 0.018311 | -122.0718 | -122.7081 | -122.7539 | 0.11444 | 0.1831 | -0.059509 | 0.11444 | 0.19684 | 0.10071 | 0.21973 | -0.26093 | 0.013733 | -0.17853 | 0.70496 | 0.022888 | 0.068664 | 0.28381 | 0.32959 | 122.7173 | -0.013733 | -0.082397 | 122.9736 | 122.9965 | 122.8775 | 0.27924 | 0.16022 | 0.96588 | 123.056 | 0.25635 | 0.17395 | 123.2483 | 0.24261 | 122.9874 | 122.9599 | -123.2346 | -0.25635 | 122.7951 | 122.8912 | 122.4792 | 122.8912
663.7812 | 122.9874 | -122.8409 | 0.21515 | -0.0041962 | 0.0056054 | 0.070226 | 0.062068 | 0.0043771 | -0.0030015 | -0.0018414 | -0.0014038 | 0.016237 | 0.02014 | 0.028997 | -0.0043109 | 0.0080236 | 0.0024396 | -0.25635 | 0.23346 | -123.0743 | -0.045776 | -122.1497 | -122.7264 | -122.7997 | 0 | 0.21057 | -0.086975 | 0 | 0.11444 | 0.018311 | 0.14191 | -0.23346 | 0.01831 | -0.26093 | 0.69122 | 0.041198 | 0.11444 | 0.27466 | 0.3479 | 122.7539 | -0.004578 | -0.21515 | 122.9553 | 122.9828 | 122.8592 | 0.22888 | 0.10529 | 0.92468 | 123.0286 | 0.20142 | 0.086975 | 123.3078 | 0.29755 | 123.0743 | 123.0515 | -123.2895 | -0.30212 | 122.7951 | 122.8409 | 122.5845 | 122.8409
665.5312 | 123.111 | -122.7676 | 0.17853 | 0.0034333 | 0.0034692 | 0.068945 | 0.0657 | 0.0015999 | -0.0017197 | -0.0016278 | 0.0046998 | 0.016024 | 0.020568 | 0.034551 | -0.0013201 | 0.009519 | -0.00097841 | -0.2655 | 0.20142 | -123.0469 | 0.045776 | -122.0261 | -122.6395 | -122.699 | 0.13733 | 0.19226 | -0.050354 | 0.15564 | 0.24719 | 0.15564 | 0.25177 | -0.27924 | 0.022888 | -0.13275 | 0.74158 | 0.068664 | 0.12817 | 0.3479 | 0.40741 | 122.7173 | 0.013733 | -0.022888 | 123.0148 | 123.0194 | 122.9233 | 0.30212 | 0.20599 | 1.0208 | 123.0927 | 0.29755 | 0.20599 | 123.2483 | 0.24261 | 122.9691 | 122.9599 | -123.2254 | -0.22888 | 122.8134 | 122.9233 | 122.5021 | 122.905
667.2656 | 123.0148 | -122.8134 | 0.21973 | -0.0041962 | 0.0038966 | 0.070867 | 0.064204 | 0.0026681 | -0.0017197 | -0.0031232 | 0.001648 | 0.014742 | 0.019927 | 0.024938 | -0.0019611 | 0.006101 | 8.9786e-05 | -0.23346 | 0.21057 | -123.0606 | -0.009155 | -122.0993 | -122.6807 | -122.7585 | 0.036621 | 0.21057 | -0.082397 | 0.027466 | 0.13733 | 0.045776 | 0.15106 | -0.24719 | -0.009156 | -0.22888 | 0.71411 | 0.054932 | 0.13275 | 0.30212 | 0.37994 | 122.731 | -0.009156 | -0.19226 | 122.9507 | 122.9645 | 122.8592 | 0.23346 | 0.12817 | 0.9613 | 123.0515 | 0.21973 | 0.10986 | 123.2712 | 0.29297 | 123.024 | 123.024 | -123.2803 | -0.30212 | 122.8043 | 122.8409 | 122.58 | 122.85
669.0156 | 123.0652 | -122.7768 | 0.19684 | 0.018692 | 0.0026148 | 0.070867 | 0.066554 | 0.0026681 | -0.0027877 | 0.00093565 | 0.001648 | 0.015169 | 0.020354 | 0.031988 | 0.0010297 | 0.0090918 | -0.00097841 | -0.3067 | 0.21057 | -123.0148 | 0 | -122.081 | -122.7173 | -122.7539 | 0.082397 | 0.19226 | -0.064087 | 0.11444 | 0.16937 | 0.082397 | 0.21057 | -0.23804 | 0.013733 | -0.19684 | 0.6958 | 0.022888 | 0.059509 | 0.26093 | 0.29755 | 122.7127 | -0.004577 | -0.082397 | 122.9462 | 122.9874 | 122.8592 | 0.27466 | 0.14648 | 0.93384 | 123.0148 | 0.23346 | 0.17853 | 123.2254 | 0.25635 | 122.9874 | 122.9691 | -123.2117 | -0.26093 | 122.7768 | 122.8912 | 122.4701 | 122.8592
670.7031 | 122.9599 | -122.8043 | 0.20599 | 0.011063 | 0.0051782 | 0.070654 | 0.067409 | 0.0022409 | -0.0032151 | -0.0014142 | -0.0014038 | 0.018587 | 0.020568 | 0.031347 | 0.0018841 | 0.0086646 | 8.9786e-05 | -0.3067 | 0.25177 | -123.0927 | -0.1236 | -122.2595 | -122.8409 | -122.8729 | -0.059509 | 0.21515 | -0.10071 | 0.013733 | 0.054932 | -0.018311 | 0.14648 | -0.28839 | 0.045776 | -0.32959 | 0.54474 | -0.068665 | -0.036621 | 0.21973 | 0.25177 | 122.7036 | 0.009155 | -0.19226 | 122.8592 | 122.9507 | 122.7859 | 0.24719 | 0.082397 | 0.83313 | 122.9691 | 0.15564 | 0.11444 | 123.3444 | 0.31586 | 123.056 | 123.0194 | -123.2986 | -0.3067 | 122.6807 | 122.818 | 122.4976 | 122.7448
672.4531 | 123.0057 | -122.7905 | 0.21973 | 0.011063 | 0.0034692 | 0.068945 | 0.066982 | 0.0011727 | -0.0032151 | 0.00029485 | 0.0046998 | 0.017946 | 0.022704 | 0.020879 | -0.00046573 | 0.0093054 | 0.0017988 | -0.27008 | 0.23804 | -123.0835 | -0.086975 | -122.2229 | -122.7722 | -122.8088 | -0.045776 | 0.23346 | -0.091553 | 0.022888 | 0.091553 | 0.009155 | 0.14648 | -0.29297 | 0.01831 | -0.3067 | 0.56763 | -0.018311 | 0.01831 | 0.27466 | 0.31128 | 122.699 | 0.013732 | -0.19684 | 122.8821 | 122.937 | 122.7997 | 0.23804 | 0.10071 | 0.8606 | 122.9965 | 0.18311 | 0.11444 | 123.3215 | 0.32501 | 123.0286 | 123.024 | -123.3032 | -0.31128 | 122.7036 | 122.8134 | 122.5204 | 122.7448
674.1406 | 123.056 | -122.7676 | 0.19684 | 0.0034333 | 0.003042 | 0.070226 | 0.066127 | 0.0037363 | -0.0021469 | 0.00029485 | -0.0014038 | 0.018801 | 0.019713 | 0.031561 | -3.8532e-05 | 0.010587 | 0.005003 | -0.33417 | 0.24719 | -123.056 | -0.068665 | -122.1863 | -122.7905 | -122.8363 | 0.004578 | 0.20599 | -0.064087 | 0.082397 | 0.15564 | 0.064087 | 0.19684 | -0.28839 | 0.050354 | -0.2655 | 0.58136 | -0.068665 | -0.022888 | 0.21973 | 0.2655 | 122.7036 | 0.009156 | -0.11444 | 122.9233 | 122.9645 | 122.8317 | 0.26093 | 0.12817 | 0.86975 | 122.9874 | 0.21973 | 0.14648 | 123.3032 | 0.27008 | 123.0148 | 122.9736 | -123.2529 | -0.26093 | 122.699 | 122.85 | 122.4335 | 122.7722
675.8906 | 123.0606 | -122.7402 | 0.18768 | 0.011063 | 0.0049646 | 0.072363 | 0.065486 | 0.0095041 | -0.0015061 | -0.00034615 | 0.001648 | 0.016878 | 0.020354 | 0.029852 | 0.0025251 | 0.011014 | -0.00076481 | -0.29297 | 0.22888 | -123.0377 | 0.027466 | -122.0535 | -122.6898 | -122.7402 | 0.11902 | 0.1831 | -0.054932 | 0.14191 | 0.18768 | 0.10986 | 0.22888 | -0.29755 | 0.041199 | -0.16022 | 0.68664 | 0 | 0.050354 | 0.29755 | 0.3479 | 122.6852 | -0.004578 | -0.045776 | 122.9279 | 122.9691 | 122.85 | 0.28381 | 0.16479 | 0.98419 | 123.0652 | 0.24261 | 0.19684 | 123.2666 | 0.23804 | 122.9691 | 122.9233 | -123.2254 | -0.24261 | 122.7676 | 122.8821 | 122.4472 | 122.8592
677.625 | 122.9736 | -122.7951 | 0.20142 | 0.011063 | 0.0051782 | 0.070654 | 0.066982 | 0.0052315 | -0.0015061 | 0.00029485 | -0.0014038 | 0.01816 | 0.020781 | 0.025793 | -0.0011065 | 0.0086646 | 0.003935 | -0.30212 | 0.23804 | -123.0606 | -0.082397 | -122.2412 | -122.8271 | -122.8638 | -0.059509 | 0.24261 | -0.086975 | 0.009155 | 0.064087 | -0.036621 | 0.14648 | -0.2655 | 0.036621 | -0.28381 | 0.55389 | -0.068665 | -0.032043 | 0.19684 | 0.23346 | 122.7081 | 0.041199 | -0.19226 | 122.8592 | 122.9416 | 122.7585 | 0.23346 | 0.050354 | 0.8194 | 122.9782 | 0.15106 | 0.09613 | 123.2986 | 0.32959 | 123.0331 | 123.0377 | -123.262 | -0.28839 | 122.7127 | 122.8043 | 122.493 | 122.7356
679.3594 | 122.9645 | -122.7997 | 0.23804 | 0.011063 | 0.004751 | 0.07044 | 0.067195 | 0.0033089 | -0.0030015 | -0.0016278 | 0.0046998 | 0.017519 | 0.021209 | 0.029211 | 0.0010297 | 0.010374 | 0.001585 | -0.31586 | 0.25177 | -123.0698 | -0.09613 | -122.2275 | -122.818 | -122.8455 | -0.050354 | 0.2243 | -0.10071 | 0.022888 | 0.068665 | -0.018311 | 0.14648 | -0.27008 | 0.013733 | -0.33417 | 0.5722 | -0.045776 | -0.01831 | 0.2243 | 0.25177 | 122.699 | -0.013733 | -0.21515 | 122.8683 | 122.9462 | 122.7814 | 0.24719 | 0.082397 | 0.84228 | 122.9736 | 0.16937 | 0.1236 | 123.3215 | 0.32501 | 123.0515 | 123.024 | -123.3078 | -0.33875 | 122.7036 | 122.8226 | 122.4838 | 122.7493
681.1094 | 123.111 | -122.7585 | 0.16937 | 0.011063 | 0.0032556 | 0.070013 | 0.066127 | 0.0045907 | -0.00065149 | -0.00098695 | 0.0046998 | 0.015383 | 0.020781 | 0.029424 | 0.0020979 | 0.010587 | -0.00076481 | -0.27466 | 0.19684 | -123.0286 | 0.022888 | -122.0535 | -122.6807 | -122.7493 | 0.1236 | 0.19226 | -0.068665 | 0.14191 | 0.21057 | 0.13275 | 0.26093 | -0.27008 | 0.027465 | -0.14649 | 0.70496 | 0.009155 | 0.07782 | 0.27923 | 0.3479 | 122.6898 | 0.022888 | -0.027466 | 122.9691 | 123.0194 | 122.8912 | 0.32959 | 0.20142 | 0.97504 | 123.0515 | 0.27924 | 0.21057 | 123.2254 | 0.26093 | 122.9553 | 122.9507 | -123.1979 | -0.23804 | 122.7814 | 122.9004 | 122.4838 | 122.8821
682.8594 | 123.0698 | -122.7676 | 0.20142 | 0.011063 | 0.0034692 | 0.070867 | 0.065273 | 0.0056589 | -0.0027877 | 0.00093565 | 0.001648 | 0.015169 | 0.020354 | 0.030493 | 0.00017507 | 0.0099462 | 0.00051699 | -0.29755 | 0.21515 | -123.0286 | 0.013733 | -122.0673 | -122.6807 | -122.731 | 0.11444 | 0.18768 | -0.064087 | 0.11902 | 0.18768 | 0.10071 | 0.22888 | -0.26093 | 0.013733 | -0.18768 | 0.70038 | 0.036621 | 0.086975 | 0.29755 | 0.3479 | 122.7036 | -0.013733 | -0.082397 | 122.9553 | 122.9965 | 122.8683 | 0.29297 | 0.1648 | 0.9613 | 123.0423 | 0.25177 | 0.18311 | 123.2437 | 0.25177 | 122.9828 | 122.9553 | -123.23 | -0.2655 | 122.7814 | 122.8867 | 122.4701 | 122.8821
684.5469 | 123.0835 | -122.7539 | 0.20142 | 0.018692 | 0.0049646 | 0.068945 | 0.064204 | 0.0054453 | -0.0040695 | 8.125e-05 | 0.001648 | 0.01581 | 0.019286 | 0.024938 | -0.0017475 | 0.0093054 | -0.001192 | -0.23804 | 0.21057 | -123.0469 | 0.045776 | -122.0444 | -122.6395 | -122.7173 | 0.10071 | 0.17395 | -0.059509 | 0.12817 | 0.22888 | 0.14648 | 0.23804 | -0.29297 | 0.009155 | -0.15564 | 0.70953 | 0.036621 | 0.11444 | 0.32959 | 0.40741 | 122.6944 | -0.027466 | -0.073242 | 122.9828 | 122.9919 | 122.9004 | 0.29755 | 0.20599 | 1.0025 | 123.0927 | 0.28839 | 0.18768 | 123.2574 | 0.23346 | 122.9645 | 122.9279 | -123.2483 | -0.26093 | 122.7997 | 122.8821 | 122.5159 | 122.8546
686.2969 | 122.9599 | -122.7814 | 0.21973 | 0.0034333 | 0.0062464 | 0.070867 | 0.068263 | 0.0069405 | -0.0017197 | -0.002696 | -0.0014038 | 0.01816 | 0.019713 | 0.01853 | 0.0012433 | 0.01016 | 0.00030339 | -0.27924 | 0.22888 | -123.0606 | -0.10071 | -122.2321 | -122.8134 | -122.8592 | -0.068665 | 0.21515 | -0.09613 | 0 | 0.050354 | -0.045776 | 0.1236 | -0.27924 | 0.009155 | -0.32044 | 0.54932 | -0.07782 | -0.032044 | 0.20142 | 0.24719 | 122.6852 | -0.004578 | -0.21973 | 122.8317 | 122.905 | 122.7356 | 0.21973 | 0.050354 | 0.82855 | 122.9599 | 0.14648 | 0.09613 | 123.2895 | 0.31128 | 123.0103 | 122.9965 | -123.2803 | -0.31586 | 122.6807 | 122.7814 | 122.5021 | 122.7127
688.0469 | 123.0835 | -122.7631 | 0.17395 | 0.011063 | 0.0036828 | 0.07044 | 0.064632 | 0.0050179 | -0.0025741 | -0.00077335 | -0.0014038 | 0.015169 | 0.02014 | 0.029211 | -0.00025213 | 0.0075964 | 0.002226 | -0.33875 | 0.21973 | -123.024 | -0.013733 | -122.1222 | -122.6807 | -122.7493 | 0.041199 | 0.17395 | -0.068665 | 0.09613 | 0.19684 | 0.12817 | 0.21973 | -0.26093 | 0.045777 | -0.18768 | 0.64087 | 0.013733 | 0.082398 | 0.27466 | 0.34332 | 122.6944 | 0 | -0.07782 | 122.9599 | 122.9828 | 122.8912 | 0.28839 | 0.19684 | 0.9018 | 123.0103 | 0.2655 | 0.16479 | 123.2437 | 0.24261 | 122.9828 | 122.937 | -123.1979 | -0.24261 | 122.7493 | 122.8592 | 122.4243 | 122.8043
689.75 | 122.9599 | -122.8043 | 0.21515 | 0.011063 | 0.0058192 | 0.07044 | 0.067195 | 0.0039499 | -0.00022429 | 0.00029485 | 0.010803 | 0.017306 | 0.021636 | 0.025579 | -0.00067933 | 0.009519 | 0.0013714 | -0.30212 | 0.24261 | -123.0515 | -0.11444 | -122.2504 | -122.8271 | -122.8729 | -0.073242 | 0.21973 | -0.09613 | 0.027466 | 0.059509 | -0.036621 | 0.13733 | -0.24719 | 0.027466 | -0.32959 | 0.55389 | -0.068665 | -0.022888 | 0.17853 | 0.22431 | 122.7081 | 0.004578 | -0.18768 | 122.8638 | 122.9416 | 122.7676 | 0.23346 | 0.059509 | 0.80109 | 122.937 | 0.15564 | 0.1236 | 123.2941 | 0.31586 | 123.0469 | 123.024 | -123.2666 | -0.31128 | 122.6898 | 122.8317 | 122.5021 | 122.731
691.4844 | 122.937 | -122.7859 | 0.19684 | -0.0041962 | 0.0060328 | 0.071508 | 0.0657 | 0.0050179 | -0.00086509 | 0.00093565 | -0.0014038 | 0.017519 | 0.022704 | 0.022588 | -0.00046573 | 0.0088782 | 0.00051699 | -0.30212 | 0.22888 | -123.0515 | -0.09613 | -122.2321 | -122.8088 | -122.8592 | -0.09613 | 0.2243 | -0.09613 | 0.013733 | 0.059509 | -0.022888 | 0.13275 | -0.2655 | 0.032044 | -0.29297 | 0.55389 | -0.073242 | -0.022888 | 0.19226 | 0.24262 | 122.6898 | 0.027466 | -0.18311 | 122.8455 | 122.9187 | 122.7631 | 0.22888 | 0.073242 | 0.8194 | 122.9553 | 0.15564 | 0.10986 | 123.2803 | 0.32043 | 123.0148 | 123.0103 | -123.2483 | -0.29297 | 122.6898 | 122.7997 | 122.4838 | 122.6898
693.2188 | 123.0286 | -122.7814 | 0.20599 | 0.011063 | 0.0011194 | 0.071722 | 0.064845 | 0.0039499 | -0.00065149 | -0.0024824 | 0.001648 | 0.017733 | 0.021636 | 0.032629 | 0.00081607 | 0.0082374 | 0.0020124 | -0.36163 | 0.20599 | -123.0423 | -0.027466 | -122.1222 | -122.7081 | -122.7585 | 0.022888 | 0.19226 | -0.073242 | 0.07782 | 0.16022 | 0.068665 | 0.19226 | -0.26093 | 0 | -0.23346 | 0.65918 | 0.022888 | 0.073242 | 0.28381 | 0.33417 | 122.7081 | -0.013733 | -0.12817 | 122.9416 | 122.9736 | 122.85 | 0.2655 | 0.14191 | 0.92011 | 123.0148 | 0.23346 | 0.15106 | 123.2483 | 0.2655 | 122.9874 | 122.9736 | -123.2483 | -0.27924 | 122.7539 | 122.8592 | 122.4197 | 122.8043
694.9688 | 122.937 | -122.7768 | 0.21057 | 0.018692 | 0.0062464 | 0.071935 | 0.065059 | 0.0037363 | -0.0038559 | -0.0016278 | 0.0046998 | 0.017733 | 0.02249 | 0.020666 | -0.00089293 | 0.0099462 | 0.001585 | -0.3067 | 0.23346 | -123.0469 | -0.10071 | -122.2321 | -122.8043 | -122.8546 | -0.073242 | 0.21515 | -0.086975 | 0.004578 | 0.032043 | -0.041199 | 0.13275 | -0.27008 | 0.022888 | -0.31128 | 0.54474 | -0.07782 | -0.027466 | 0.19226 | 0.24262 | 122.6898 | 0.004578 | -0.20599 | 122.8088 | 122.9095 | 122.7356 | 0.21973 | 0.045776 | 0.81482 | 122.9462 | 0.11902 | 0.091553 | 123.2803 | 0.30212 | 123.0103 | 122.9919 | -123.2574 | -0.29755 | 122.6761 | 122.7814 | 122.4701 | 122.7036
696.7031 | 122.9507 | -122.7997 | 0.21057 | 0.011063 | 0.0038966 | 0.069586 | 0.065486 | 0.0067269 | -0.00022429 | 0.00029485 | 0.0046998 | 0.017092 | 0.021209 | 0.019598 | -0.0034563 | 0.00781 | -0.0054644 | -0.31128 | 0.23804 | -123.0606 | -0.07782 | -122.1817 | -122.7493 | -122.7951 | -0.036621 | 0.22888 | -0.10986 | -0.004578 | 0.10529 | 0 | 0.13275 | -0.26093 | 0.027466 | -0.28839 | 0.61798 | 0.004578 | 0.050354 | 0.2655 | 0.31128 | 122.6898 | 0.018311 | -0.21515 | 122.905 | 122.9324 | 122.7997 | 0.24261 | 0.10986 | 0.87891 | 122.9828 | 0.21515 | 0.10529 | 123.2986 | 0.33875 | 123.0377 | 123.0286 | -123.2712 | -0.32043 | 122.7219 | 122.7951 | 122.4884 | 122.7631
698.4062 | 123.0011 | -122.7814 | 0.21973 | 0.018692 | 0.0051782 | 0.070867 | 0.066341 | 0.0035227 | -0.0017197 | -0.0014142 | 0.010803 | 0.016665 | 0.01715 | 0.024297 | -0.0011065 | 0.0080236 | -0.00055121 | -0.2655 | 0.24261 | -123.0606 | -0.082397 | -122.1771 | -122.731 | -122.7905 | -0.041199 | 0.23346 | -0.09613 | 0.036621 | 0.11902 | 0.027466 | 0.16937 | -0.27924 | 0.022888 | -0.30212 | 0.60425 | -0.009155 | 0.050354 | 0.27008 | 0.32959 | 122.6852 | 0.013732 | -0.18311 | 122.9004 | 122.9507 | 122.8088 | 0.2655 | 0.1236 | 0.88348 | 122.9782 | 0.21515 | 0.13275 | 123.3032 | 0.32959 | 123.024 | 123.0148 | -123.2803 | -0.31586 | 122.699 | 122.818 | 122.5159 | 122.7402
700.1562 | 123.0652 | -122.7722 | 0.17395 | 0.018692 | 0.0062464 | 0.069372 | 0.066554 | 0.0015999 | -0.0023605 | 0.0013628 | 0.0046998 | 0.016237 | 0.019072 | 0.027502 | 0.0014569 | 0.0086646 | 0.0030804 | -0.29755 | 0.19684 | -123.0103 | 0.027466 | -122.0444 | -122.6807 | -122.731 | 0.11444 | 0.17395 | -0.050354 | 0.13733 | 0.20142 | 0.11444 | 0.21057 | -0.23804 | 0.022888 | -0.14648 | 0.72784 | 0.041199 | 0.091553 | 0.27924 | 0.32959 | 122.7219 | 0 | -0.036621 | 122.9736 | 122.9828 | 122.8867 | 0.26093 | 0.16479 | 0.96588 | 123.0377 | 0.25177 | 0.18768 | 123.2071 | 0.2243 | 122.9691 | 122.9462 | -123.1842 | -0.2243 | 122.7997 | 122.9095 | 122.4747 | 122.8867
701.8281 | 123.0789 | -122.7905 | 0.16479 | 0.011063 | 0.0036828 | 0.071935 | 0.063136 | 0.0022409 | -0.0036423 | -0.00055975 | -0.0014038 | 0.013033 | 0.019072 | 0.031988 | -3.8532e-05 | 0.0097326 | 0.0013714 | -0.33875 | 0.19684 | -123.0331 | -0.013733 | -122.0993 | -122.6852 | -122.7264 | 0.050354 | 0.17395 | -0.07782 | 0.10071 | 0.20142 | 0.12817 | 0.21973 | -0.24262 | 0.032043 | -0.17853 | 0.69122 | 0.064087 | 0.10528 | 0.3067 | 0.3479 | 122.7127 | 0.009155 | -0.064087 | 122.9919 | 123.0103 | 122.9187 | 0.29755 | 0.20599 | 0.93384 | 123.0194 | 0.27924 | 0.17853 | 123.23 | 0.25177 | 122.9874 | 122.9645 | -123.1979 | -0.24261 | 122.7768 | 122.8912 | 122.4518 | 122.8409
703.5625 | 122.9507 | -122.8317 | 0.23346 | 0.0034333 | 0.003042 | 0.068731 | 0.064204 | 0.0069405 | -0.0047103 | -0.0052594 | -0.0014038 | 0.017092 | 0.018859 | 0.022802 | -0.0034563 | 0.0086646 | 0.0011578 | -0.29297 | 0.21515 | -123.056 | -0.064087 | -122.1817 | -122.7402 | -122.8043 | -0.036621 | 0.21057 | -0.082397 | -0.004578 | 0.091553 | 0.009155 | 0.13275 | -0.2243 | -0.01831 | -0.29755 | 0.65002 | 0.027466 | 0.091553 | 0.25177 | 0.31586 | 122.7493 | -0.022888 | -0.23804 | 122.9233 | 122.9645 | 122.8409 | 0.21515 | 0.091552 | 0.87433 | 122.9919 | 0.17395 | 0.077819 | 123.2712 | 0.29297 | 123.0469 | 123.0423 | -123.2895 | -0.31586 | 122.7676 | 122.8271 | 122.5388 | 122.7951
705.25 | 123.056 | -122.7539 | 0.1831 | -0.011826 | 0.0032556 | 0.072149 | 0.063136 | 0.0048043 | -0.0049241 | -0.00013235 | 0.0046998 | 0.016878 | 0.0195 | 0.030706 | -0.0013201 | 0.0088782 | 0.0011578 | -0.26093 | 0.17853 | -123.0103 | 0.036621 | -122.0398 | -122.644 | -122.7081 | 0.086975 | 0.17853 | -0.073242 | 0.10986 | 0.21515 | 0.12817 | 0.2243 | -0.25635 | -0.004577 | -0.14648 | 0.71411 | 0.045776 | 0.10986 | 0.30212 | 0.36621 | 122.6807 | -0.004577 | -0.073242 | 122.9691 | 122.9782 | 122.8821 | 0.29755 | 0.20142 | 0.97046 | 123.0469 | 0.28839 | 0.18311 | 123.1888 | 0.25177 | 122.9324 | 122.9324 | -123.1934 | -0.25635 | 122.7905 | 122.8638 | 122.493 | 122.8409
707 | 123.0881 | -122.7356 | 0.1831 | 0.011063 | 0.0034692 | 0.069372 | 0.065486 | 0.0028817 | 0.00084391 | -0.0014142 | -0.0014038 | 0.014315 | 0.021636 | 0.030065 | 0.0042341 | 0.011228 | 0.0020124 | -0.26093 | 0.19684 | -123.0194 | 0.032043 | -122.049 | -122.6624 | -122.7356 | 0.10986 | 0.20142 | -0.073242 | 0.14648 | 0.21515 | 0.11902 | 0.2655 | -0.28381 | 0.013733 | -0.15106 | 0.68665 | 0 | 0.073242 | 0.28381 | 0.35706 | 122.6624 | 0.018311 | -0.036621 | 122.9507 | 123.0011 | 122.8546 | 0.33874 | 0.19226 | 0.97046 | 123.0515 | 0.28839 | 0.21973 | 123.2162 | 0.27466 | 122.9324 | 122.937 | -123.2025 | -0.25635 | 122.7676 | 122.8821 | 122.4747 | 122.8455
708.7344 | 123.0789 | -122.7448 | 0.1831 | 0.0034333 | 0.0038966 | 0.071722 | 0.065059 | 0.0026681 | -0.0012925 | 0.0015764 | 0.0077514 | 0.014956 | 0.02014 | 0.027715 | 0.0010297 | 0.0082374 | 0.0028668 | -0.27008 | 0.18768 | -122.9919 | 0.041199 | -122.049 | -122.6761 | -122.7219 | 0.11902 | 0.20599 | -0.064087 | 0.15106 | 0.21057 | 0.10986 | 0.26093 | -0.24719 | 0.004578 | -0.14191 | 0.6958 | 0.022888 | 0.068665 | 0.27008 | 0.31586 | 122.6807 | 0.022889 | -0.032043 | 122.9553 | 123.0057 | 122.8546 | 0.32501 | 0.17395 | 0.94299 | 123.0331 | 0.27466 | 0.21515 | 123.1796 | 0.27008 | 122.9324 | 122.9507 | -123.175 | -0.24719 | 122.7859 | 122.8958 | 122.4747 | 122.8638
710.4844 | 123.0881 | -122.731 | 0.19226 | 0.011063 | 0.0051782 | 0.071508 | 0.067622 | 0.010145 | -0.0010789 | 0.00050845 | 0.001648 | 0.017733 | 0.022063 | 0.027929 | 0.00038887 | 0.011228 | -0.00033761 | -0.27008 | 0.19684 | -123.0331 | 0.036621 | -122.0627 | -122.6669 | -122.7264 | 0.10529 | 0.19226 | -0.073242 | 0.15106 | 0.20599 | 0.10986 | 0.25635 | -0.30212 | 0.004577 | -0.15564 | 0.66833 | 0.004578 | 0.064087 | 0.3067 | 0.36621 | 122.6578 | 0 | -0.041199 | 122.937 | 122.9874 | 122.8409 | 0.32959 | 0.18311 | 0.97046 | 123.0698 | 0.27924 | 0.2243 | 123.23 | 0.2655 | 122.9279 | 122.9233 | -123.2254 | -0.2655 | 122.7676 | 122.8821 | 122.4609 | 122.8363
712.1719 | 123.0835 | -122.7448 | 0.19684 | -0.011826 | 0.0041102 | 0.068517 | 0.063564 | 0.0037363 | -0.0021469 | -0.0012006 | 0.0077514 | 0.015169 | 0.020995 | 0.025366 | -0.0038837 | 0.0086646 | 0.003294 | -0.24719 | 0.20142 | -123.0331 | 0.041199 | -122.0444 | -122.6349 | -122.7081 | 0.10986 | 0.16937 | -0.059509 | 0.1236 | 0.20142 | 0.13733 | 0.2243 | -0.28839 | 0.004578 | -0.15564 | 0.70038 | 0.036621 | 0.10986 | 0.32501 | 0.39825 | 122.6852 | -0.027465 | -0.073242 | 122.9462 | 122.9691 | 122.8821 | 0.28381 | 0.19684 | 0.98877 | 123.0743 | 0.26093 | 0.1831 | 123.2346 | 0.22888 | 122.9462 | 122.9141 | -123.23 | -0.25635 | 122.7859 | 122.8683 | 122.4976 | 122.8546
713.9219 | 123.1064 | -122.7402 | 0.17853 | 0.0034333 | 0.0026148 | 0.069799 | 0.063564 | 0.0024545 | -0.0049241 | -0.003764 | -0.0014038 | 0.013674 | 0.018431 | 0.030493 | -0.0011065 | 0.009519 | 0.0013714 | -0.28381 | 0.20599 | -123.0286 | 0.036621 | -122.0215 | -122.6212 | -122.6944 | 0.13733 | 0.17395 | -0.073242 | 0.14648 | 0.25635 | 0.17395 | 0.25177 | -0.28839 | 0.027466 | -0.14191 | 0.71869 | 0.045776 | 0.11902 | 0.33417 | 0.40741 | 122.6669 | -0.004578 | -0.032044 | 122.9965 | 122.9919 | 122.9141 | 0.32501 | 0.24719 | 1.0071 | 123.0652 | 0.32959 | 0.21973 | 123.2346 | 0.24719 | 122.9462 | 122.9141 | -123.2071 | -0.25177 | 122.7768 | 122.8867 | 122.4564 | 122.8775
715.6719 | 123.0606 | -122.7585 | 0.19226 | -0.0041962 | 0.0041102 | 0.072363 | 0.065273 | 0.0030953 | -0.0025741 | -0.0024824 | -0.0014038 | 0.015597 | 0.021849 | 0.029852 | -0.0032427 | 0.01016 | 0.0035078 | -0.33417 | 0.20599 | -123.0286 | -0.018311 | -122.0993 | -122.699 | -122.731 | 0.054932 | 0.1831 | -0.068665 | 0.091553 | 0.1831 | 0.10071 | 0.21973 | -0.27008 | 0.013733 | -0.21057 | 0.65918 | 0.027466 | 0.059509 | 0.29755 | 0.32959 | 122.6898 | -0.009156 | -0.10071 | 122.9416 | 122.9782 | 122.8592 | 0.28839 | 0.16937 | 0.92926 | 123.0103 | 0.25177 | 0.16022 | 123.2346 | 0.25177 | 122.9645 | 122.9416 | -123.2208 | -0.26093 | 122.7402 | 122.85 | 122.4243 | 122.8134
717.3438 | 123.0423 | -122.7539 | 0.17853 | -0.0041962 | 0.0043238 | 0.071508 | 0.066554 | 0.0024545 | -0.0030015 | -0.00077335 | 0.001648 | 0.01581 | 0.019927 | 0.031347 | -0.0028155 | 0.0086646 | -0.00055121 | -0.23804 | 0.18768 | -123.024 | 0.036621 | -122.049 | -122.6395 | -122.7264 | 0.10529 | 0.1831 | -0.054932 | 0.082397 | 0.20599 | 0.10071 | 0.21515 | -0.27008 | 0.009155 | -0.14191 | 0.70496 | 0.027466 | 0.11444 | 0.29755 | 0.38452 | 122.699 | 0.004577 | -0.096131 | 122.9599 | 122.9691 | 122.8546 | 0.27008 | 0.15564 | 0.97504 | 123.0606 | 0.26093 | 0.13733 | 123.2117 | 0.23804 | 122.9416 | 122.937 | -123.2025 | -0.23346 | 122.7905 | 122.8363 | 122.5159 | 122.8592
719.0781 | 122.9507 | -122.7997 | 0.2243 | 0.0034333 | 0.0024012 | 0.070013 | 0.0657 | 0.0013863 | -0.0025741 | -0.0022688 | -0.0014038 | 0.018801 | 0.022277 | 0.027502 | -0.0034563 | 0.0052466 | 0.0041486 | -0.28381 | 0.23804 | -123.0377 | -0.059509 | -122.1588 | -122.7402 | -122.7951 | -0.036621 | 0.2243 | -0.091553 | 0 | 0.086975 | 0.009155 | 0.13275 | -0.23804 | 0.013733 | -0.28381 | 0.64087 | 0.004578 | 0.05951 | 0.24261 | 0.29755 | 122.7081 | 0 | -0.2243 | 122.8867 | 122.9324 | 122.8088 | 0.2243 | 0.10071 | 0.87891 | 122.9782 | 0.17853 | 0.091553 | 123.2758 | 0.31586 | 123.0377 | 123.024 | -123.262 | -0.31586 | 122.7402 | 122.7997 | 122.5159 | 122.7631
720.8281 | 123.0469 | -122.7356 | 0.17853 | 0.011063 | 0.0036828 | 0.071722 | 0.066768 | 0.0052315 | -0.0010789 | 0.00050845 | 0.001648 | 0.016665 | 0.021636 | 0.022375 | 0.0029523 | 0.010587 | 0.0028668 | -0.32959 | 0.24261 | -123.0469 | -0.059509 | -122.1451 | -122.7493 | -122.7951 | 0.027466 | 0.19684 | -0.059509 | 0.10071 | 0.16479 | 0.068665 | 0.21057 | -0.31128 | 0.064087 | -0.23804 | 0.59051 | -0.059509 | -0.013733 | 0.25177 | 0.29755 | 122.6761 | 0.01831 | -0.07782 | 122.9004 | 122.9462 | 122.8043 | 0.27008 | 0.12817 | 0.90179 | 122.9874 | 0.2243 | 0.16022 | 123.2895 | 0.25635 | 122.9782 | 122.9324 | -123.2254 | -0.23804 | 122.6761 | 122.8363 | 122.406 | 122.7631
722.5781 | 122.9782 | -122.731 | 0.21057 | -0.0041962 | 0.004751 | 0.070867 | 0.068263 | 0.0071541 | -0.0021469 | -0.0029096 | 0.001648 | 0.016665 | 0.0195 | 0.026647 | 0.0031659 | 0.0093054 | 0.0011578 | -0.32044 | 0.21057 | -123.0698 | -0.10071 | -122.1863 | -122.7722 | -122.8271 | -0.027466 | 0.20599 | -0.082397 | 0.050354 | 0.091553 | 0.004578 | 0.17853 | -0.33874 | 0 | -0.31128 | 0.54474 | -0.09613 | -0.041199 | 0.24262 | 0.29755 | 122.6486 | -0.004577 | -0.16022 | 122.8226 | 122.9095 | 122.7356 | 0.26092 | 0.086975 | 0.88348 | 122.9691 | 0.17395 | 0.13275 | 123.2803 | 0.28839 | 122.9416 | 122.937 | -123.2803 | -0.29297 | 122.6303 | 122.7814 | 122.4106 | 122.7036
724.2656 | 122.9645 | -122.7814 | 0.21515 | 0.018692 | 0.0066736 | 0.071295 | 0.067409 | 0.0035227 | -0.0042831 | -0.00077335 | 0.001648 | 0.017519 | 0.0195 | 0.020452 | -0.0040973 | 0.0073828 | -0.00097841 | -0.29755 | 0.25177 | -123.0469 | -0.086975 | -122.1725 | -122.7493 | -122.7951 | -0.054932 | 0.21515 | -0.09613 | 0.004578 | 0.10986 | 0.004578 | 0.15564 | -0.2655 | 0.036621 | -0.30212 | 0.60883 | -0.013733 | 0.032043 | 0.25177 | 0.29755 | 122.6852 | 0 | -0.21057 | 122.8912 | 122.937 | 122.7859 | 0.25177 | 0.10071 | 0.87433 | 122.9599 | 0.20599 | 0.10071 | 123.2986 | 0.31128 | 123.0331 | 122.9965 | -123.262 | -0.31128 | 122.6944 | 122.7859 | 122.4838 | 122.7264
726.0156 | 122.9828 | -122.7859 | 0.20142 | 0.0034333 | 0.0034692 | 0.068945 | 0.065913 | 0.0045907 | -0.0040695 | 0.0013628 | -0.0014038 | 0.017946 | 0.020568 | 0.017248 | 0.00060247 | 0.0080236 | 0.0013714 | -0.28381 | 0.24261 | -123.0789 | -0.068665 | -122.1588 | -122.7219 | -122.7859 | -0.041199 | 0.23346 | -0.10071 | 0.027466 | 0.11902 | 0.018311 | 0.16937 | -0.29297 | 0.041199 | -0.27008 | 0.62714 | 0 | 0.064087 | 0.29297 | 0.35706 | 122.6852 | 0.032043 | -0.17395 | 122.905 | 122.9553 | 122.8043 | 0.27008 | 0.11902 | 0.92011 | 123.0103 | 0.21973 | 0.12817 | 123.3215 | 0.33417 | 123.0286 | 123.0194 | -123.2803 | -0.30212 | 122.7173 | 122.8134 | 122.5021 | 122.7448
727.6875 | 123.0469 | -122.7448 | 0.17853 | 0.018692 | 0.0077418 | 0.073858 | 0.063991 | 0.0045907 | 0.00020291 | 8.125e-05 | 0.0046998 | 0.016237 | 0.020568 | 0.032842 | 0.0027387 | 0.0097326 | 0.0026532 | -0.29297 | 0.19684 | -123.0057 | 0.027466 | -122.0306 | -122.6532 | -122.7173 | 0.12817 | 0.17395 | -0.050354 | 0.14191 | 0.21973 | 0.11902 | 0.23346 | -0.26093 | 0.01831 | -0.15106 | 0.71411 | 0.027466 | 0.091553 | 0.28839 | 0.35248 | 122.6944 | -0.004578 | -0.036621 | 122.9645 | 122.9782 | 122.8638 | 0.28381 | 0.16937 | 0.97504 | 123.0331 | 0.27008 | 0.19226 | 123.2025 | 0.2243 | 122.9416 | 122.9187 | -123.1842 | -0.22888 | 122.7722 | 122.8867 | 122.4518 | 122.8729
729.4219 | 123.0743 | -122.7356 | 0.1831 | -0.0041962 | 0.0051782 | 0.071081 | 0.066768 | 0.00010474 | -0.0017197 | 0.0028582 | 0.001648 | 0.016665 | 0.022063 | 0.031133 | 0.0020979 | 0.011655 | -0.00097841 | -0.27008 | 0.19226 | -123.0011 | 0.027466 | -122.0444 | -122.6715 | -122.7264 | 0.10529 | 0.1831 | -0.059509 | 0.13733 | 0.2243 | 0.10529 | 0.25635 | -0.2655 | 0.009156 | -0.15564 | 0.69122 | 0.009156 | 0.064087 | 0.27466 | 0.32959 | 122.6761 | 0 | -0.045776 | 122.9599 | 122.9919 | 122.8409 | 0.31586 | 0.16479 | 0.95673 | 123.0286 | 0.28381 | 0.19684 | 123.1934 | 0.24261 | 122.9279 | 122.9187 | -123.1842 | -0.24261 | 122.7631 | 122.8729 | 122.4655 | 122.8409
731.1094 | 122.9599 | -122.7768 | 0.21515 | 0.011063 | 0.0043238 | 0.07044 | 0.064845 | 0.0045907 | -0.0047103 | -0.0020552 | 0.0046998 | 0.016024 | 0.020781 | 0.01917 | -0.0019611 | 0.0093054 | -0.0022602 | -0.28839 | 0.24719 | -123.0698 | -0.10071 | -122.1863 | -122.7448 | -122.7951 | -0.054932 | 0.21973 | -0.091553 | 0.009155 | 0.091553 | 0.022888 | 0.13733 | -0.29297 | 0.032043 | -0.31586 | 0.59051 | -0.018311 | 0.032043 | 0.27466 | 0.32501 | 122.6852 | 0.004578 | -0.20599 | 122.8683 | 122.9141 | 122.7997 | 0.22888 | 0.11444 | 0.88348 | 122.9691 | 0.18311 | 0.10071 | 123.317 | 0.31128 | 123.024 | 122.9965 | -123.2849 | -0.3067 | 122.6761 | 122.7859 | 122.4884 | 122.7219
732.8438 | 123.056 | -122.7768 | 0.19226 | 0.018692 | 0.0041102 | 0.071508 | 0.065913 | 0.0037363 | -0.0032151 | -0.00013235 | 0.0046998 | 0.013888 | 0.018645 | 0.023229 | -0.0015337 | 0.0090918 | -0.001192 | -0.26093 | 0.19684 | -123.0148 | 0.032043 | -122.0352 | -122.6212 | -122.7036 | 0.09613 | 0.19226 | -0.059509 | 0.10071 | 0.2243 | 0.12817 | 0.24261 | -0.23804 | 0.004577 | -0.16022 | 0.74158 | 0.073242 | 0.15564 | 0.31128 | 0.39368 | 122.7173 | 0 | -0.091553 | 123.0011 | 123.0194 | 122.905 | 0.30212 | 0.18768 | 0.97961 | 123.0469 | 0.28381 | 0.16022 | 123.2117 | 0.25177 | 122.9736 | 122.9691 | -123.2071 | -0.25177 | 122.8088 | 122.8775 | 122.5159 | 122.8729
734.5938 | 122.9416 | -122.7676 | 0.21057 | 0.026321 | 0.003042 | 0.070013 | 0.066341 | 0.0011727 | -0.0027877 | -0.0024824 | 0.0046998 | 0.016237 | 0.022277 | 0.024297 | -0.0021747 | 0.0052466 | -0.0035418 | -0.28839 | 0.24261 | -123.0652 | -0.10529 | -122.168 | -122.7402 | -122.7905 | -0.059509 | 0.21515 | -0.10529 | 0 | 0.086975 | 0 | 0.16022 | -0.29755 | 0.032044 | -0.31586 | 0.59967 | -0.022888 | 0.027466 | 0.27466 | 0.32501 | 122.6624 | 0.004578 | -0.21057 | 122.8546 | 122.9279 | 122.7676 | 0.2655 | 0.10529 | 0.89722 | 122.9599 | 0.19226 | 0.10529 | 123.3078 | 0.32044 | 123.0103 | 122.9828 | -123.2758 | -0.31586 | 122.6624 | 122.7676 | 122.4792 | 122.7081
736.2812 | 123.0515 | -122.7219 | 0.18768 | 0.011063 | 0.0045374 | 0.072363 | 0.0657 | 0.0065133 | -0.0040695 | 0.0030718 | 0.001648 | 0.015383 | 0.021849 | 0.030065 | -0.0017475 | 0.0099462 | -0.0035418 | -0.25635 | 0.21515 | -123.0286 | 0.027466 | -122.0215 | -122.612 | -122.7036 | 0.09613 | 0.18768 | -0.068665 | 0.12817 | 0.21973 | 0.1236 | 0.23804 | -0.3067 | 0.027466 | -0.16022 | 0.70038 | 0.018311 | 0.10986 | 0.32501 | 0.41656 | 122.6532 | 0 | -0.059509 | 122.9416 | 122.9599 | 122.8455 | 0.3067 | 0.19226 | 1.0071 | 123.056 | 0.28839 | 0.19684 | 123.2437 | 0.25635 | 122.937 | 122.9095 | -123.2162 | -0.25635 | 122.7493 | 122.85 | 122.4655 | 122.818
738.0312 | 123.0606 | -122.7127 | 0.17853 | -0.0041962 | 0.0038966 | 0.069372 | 0.065273 | 0.00053194 | -0.0019333 | 0.0017902 | 0.0046998 | 0.015169 | 0.019286 | 0.018316 | -0.00067933 | 0.008451 | -0.001192 | -0.26093 | 0.19684 | -123.0057 | 0.022888 | -122.0078 | -122.612 | -122.6761 | 0.11444 | 0.16022 | -0.059509 | 0.11902 | 0.23804 | 0.14191 | 0.22888 | -0.29297 | 0.01831 | -0.15564 | 0.70496 | 0.036622 | 0.10071 | 0.32959 | 0.39368 | 122.6532 | -0.018311 | -0.059509 | 122.9507 | 122.9416 | 122.8546 | 0.28839 | 0.20142 | 0.99792 | 123.0286 | 0.29755 | 0.17853 | 123.2025 | 0.21973 | 122.9095 | 122.8729 | -123.1842 | -0.23804 | 122.7356 | 122.8317 | 122.4518 | 122.8271
739.7031 | 122.9645 | -122.7676 | 0.19684 | 0.011063 | 0.0051782 | 0.068304 | 0.065059 | 0.0041635 | -0.0032151 | 0.0011492 | 0.0077514 | 0.019015 | 0.022063 | 0.020666 | -0.00067933 | 0.0082374 | -0.00055121 | -0.26093 | 0.23804 | -123.056 | -0.073242 | -122.1359 | -122.6898 | -122.7768 | -0.004578 | 0.21515 | -0.091553 | 0.050354 | 0.13275 | 0.041199 | 0.17853 | -0.28839 | 0.041199 | -0.27008 | 0.63171 | -0.009155 | 0.07782 | 0.27924 | 0.36621 | 122.6761 | 0.018311 | -0.14648 | 122.9004 | 122.9462 | 122.8088 | 0.27008 | 0.13275 | 0.92011 | 122.9828 | 0.2243 | 0.14191 | 123.2941 | 0.3067 | 123.0057 | 122.9828 | -123.2529 | -0.28839 | 122.6944 | 122.818 | 122.5067 | 122.7631
741.4531 | 122.9507 | -122.7585 | 0.2243 | 0.011063 | 0.0056054 | 0.070867 | 0.065059 | 0.0037363 | -0.0019333 | -0.0014142 | 0.001648 | 0.017306 | 0.020354 | 0.030493 | -0.00025213 | 0.0082374 | 0.00051699 | -0.32959 | 0.23346 | -123.0103 | -0.10986 | -122.1863 | -122.7676 | -122.8134 | -0.027466 | 0.20142 | -0.091553 | 0.045776 | 0.086975 | -0.004578 | 0.15106 | -0.25177 | 0.009155 | -0.33417 | 0.5722 | -0.054932 | -0.009155 | 0.19684 | 0.24262 | 122.6669 | -0.022888 | -0.17853 | 122.8455 | 122.9095 | 122.7539 | 0.24261 | 0.086975 | 0.82398 | 122.9004 | 0.17853 | 0.13733 | 123.2437 | 0.29297 | 122.9919 | 122.9599 | -123.2346 | -0.31586 | 122.6486 | 122.8043 | 122.4289 | 122.731
743.1406 | 122.9828 | -122.7722 | 0.20599 | 0.011063 | 0.0058192 | 0.071295 | 0.066982 | 0.0052315 | -0.0030015 | -0.0016278 | 0.001648 | 0.016024 | 0.019286 | 0.022588 | 0.0027387 | 0.0086646 | 0.00051699 | -0.23804 | 0.24719 | -123.0377 | -0.054932 | -122.1176 | -122.6944 | -122.7631 | 0.032043 | 0.20142 | -0.082397 | 0.07782 | 0.14191 | 0.045776 | 0.1831 | -0.2655 | 0.041198 | -0.26093 | 0.6546 | 0.009155 | 0.07782 | 0.27466 | 0.34332 | 122.6898 | -0.004578 | -0.12817 | 122.9141 | 122.9553 | 122.818 | 0.2655 | 0.12817 | 0.9201 | 122.9828 | 0.2243 | 0.16022 | 123.2849 | 0.28381 | 123.0194 | 122.9736 | -123.2437 | -0.28839 | 122.7173 | 122.85 | 122.5342 | 122.8043
744.8906 | 122.9462 | -122.7539 | 0.21515 | -0.0041962 | 0.0051782 | 0.07044 | 0.065913 | 0.0052315 | -0.00065149 | -0.00098695 | 0.0046998 | 0.017519 | 0.022063 | 0.028997 | -0.0026019 | 0.008451 | -0.00097841 | -0.29755 | 0.24261 | -123.0606 | -0.10529 | -122.1634 | -122.731 | -122.7722 | -0.073242 | 0.21515 | -0.10071 | 0.004578 | 0.09613 | 0.018311 | 0.15106 | -0.3067 | 0.027466 | -0.32044 | 0.59051 | -0.018311 | 0.022888 | 0.28839 | 0.32959 | 122.6532 | 0 | -0.21057 | 122.85 | 122.905 | 122.7722 | 0.25177 | 0.11902 | 0.89722 | 122.9553 | 0.19684 | 0.10529 | 123.3032 | 0.31586 | 122.9965 | 122.9691 | -123.2758 | -0.31586 | 122.6486 | 122.7585 | 122.4564 | 122.6807
746.5938 | 122.9736 | -122.7768 | 0.19226 | 0.011063 | 0.0053918 | 0.071508 | 0.063777 | 0.0030953 | -0.0027877 | 0.00029485 | 0.001648 | 0.017733 | 0.022063 | 0.016393 | -0.0015337 | 0.0090918 | 0.0013714 | -0.24719 | 0.24261 | -123.0331 | -0.027466 | -122.113 | -122.7036 | -122.7585 | 0.032043 | 0.2243 | -0.10529 | 0.068665 | 0.14191 | 0.054932 | 0.17853 | -0.25635 | 0.050354 | -0.21973 | 0.66376 | 0.01831 | 0.073242 | 0.27466 | 0.32959 | 122.6715 | 0.032043 | -0.1236 | 122.9187 | 122.9553 | 122.8317 | 0.28381 | 0.16022 | 0.9201 | 123.0057 | 0.24719 | 0.17395 | 123.2758 | 0.32959 | 123.0194 | 123.0011 | -123.2254 | -0.29755 | 122.7493 | 122.8455 | 122.5296 | 122.8088
748.3438 | 122.9645 | -122.7676 | 0.1831 | -0.0041962 | 0.00646 | 0.070867 | 0.067409 | -0.00010886 | -0.0040695 | -0.0012006 | 0.001648 | 0.017306 | 0.019927 | 0.024938 | 0.00017507 | 0.010587 | 0.0024396 | -0.25177 | 0.22888 | -123.0286 | -0.041199 | -122.0947 | -122.699 | -122.7631 | 0.041199 | 0.19684 | -0.091553 | 0.082397 | 0.15106 | 0.045776 | 0.17853 | -0.26093 | 0.045777 | -0.2243 | 0.67291 | 0.004577 | 0.068664 | 0.2655 | 0.32959 | 122.6761 | 0.013733 | -0.10071 | 122.9187 | 122.9462 | 122.8134 | 0.27008 | 0.13733 | 0.93384 | 122.9874 | 0.24261 | 0.17395 | 123.2574 | 0.28839 | 122.9965 | 122.9645 | -123.2117 | -0.27466 | 122.7264 | 122.85 | 122.5159 | 122.8088
750.0938 | 123.0606 | -122.7036 | 0.1831 | -0.0041962 | 0.0053918 | 0.072149 | 0.066341 | 0.0035227 | -0.00022429 | -0.0012006 | 0.0046998 | 0.016451 | 0.020354 | 0.027288 | 0.0012433 | 0.01016 | 0.0043622 | -0.28381 | 0.18768 | -122.9828 | 0.027466 | -122.0215 | -122.6303 | -122.7173 | 0.11444 | 0.1831 | -0.07782 | 0.16937 | 0.22888 | 0.13275 | 0.25177 | -0.27924 | 0.004578 | -0.15564 | 0.68207 | -0.013733 | 0.073242 | 0.2655 | 0.35248 | 122.6257 | 0 | -0.013732 | 122.9324 | 122.9553 | 122.8363 | 0.32959 | 0.21057 | 0.9613 | 123.0103 | 0.3067 | 0.24719 | 123.1705 | 0.26092 | 122.8912 | 122.8867 | -123.1659 | -0.26092 | 122.731 | 122.8729 | 122.4197 | 122.818
751.7656 | 123.0194 | -122.7539 | 0.19684 | -0.011826 | 0.0045374 | 0.070654 | 0.067622 | 0.0058725 | -0.0015061 | 0.00029485 | 0.0046998 | 0.018374 | 0.020781 | 0.027502 | -0.0011065 | 0.0082374 | 0.00094419 | -0.25635 | 0.21057 | -123.0286 | -0.050354 | -122.1313 | -122.7264 | -122.7768 | 0.004578 | 0.21973 | -0.091553 | 0.032043 | 0.091553 | 0 | 0.15106 | -0.27466 | 0.013733 | -0.24719 | 0.62256 | -0.022888 | 0.027466 | 0.25177 | 0.30212 | 122.6624 | 0.022889 | -0.1648 | 122.8455 | 122.905 | 122.7539 | 0.24261 | 0.091553 | 0.89722 | 122.9782 | 0.18311 | 0.1236 | 123.2391 | 0.31128 | 122.9645 | 122.9736 | -123.2254 | -0.28839 | 122.7036 | 122.7859 | 122.4976 | 122.7585
753.5156 | 123.056 | -122.7219 | 0.17853 | 0.011063 | 0.0043238 | 0.069799 | 0.0657 | 0.0028817 | -0.0017197 | -0.00013235 | -0.0014038 | 0.014529 | 0.020354 | 0.027502 | 0.0018841 | 0.011228 | -0.00012381 | -0.32501 | 0.21057 | -122.9965 | -0.027466 | -122.0947 | -122.6807 | -122.7402 | 0.073242 | 0.17853 | -0.073242 | 0.12817 | 0.21973 | 0.10986 | 0.25177 | -0.27466 | 0.032043 | -0.20599 | 0.62714 | -0.01831 | 0.041199 | 0.25635 | 0.31586 | 122.6486 | 0 | -0.050354 | 122.9416 | 122.9736 | 122.8317 | 0.32501 | 0.18311 | 0.90179 | 122.9691 | 0.29297 | 0.20142 | 123.2071 | 0.25177 | 122.9324 | 122.9004 | -123.175 | -0.25177 | 122.6944 | 122.85 | 122.3969 | 122.7951
755.2656 | 123.0423 | -122.7173 | 0.1831 | 0.0034333 | 0.0053918 | 0.071295 | 0.064632 | 0.0060861 | -0.0019333 | 0.00050845 | 0.001648 | 0.016878 | 0.0195 | 0.026647 | 0.00060247 | 0.011014 | 0.0043622 | -0.33875 | 0.2243 | -123.0148 | -0.054932 | -122.1039 | -122.7036 | -122.7493 | 0.054932 | 0.1831 | -0.082397 | 0.11444 | 0.18768 | 0.091553 | 0.23804 | -0.29755 | 0.041199 | -0.23804 | 0.6134 | -0.032044 | 0.013733 | 0.2655 | 0.31128 | 122.6349 | 0 | -0.068664 | 122.905 | 122.9553 | 122.8088 | 0.32043 | 0.17395 | 0.91095 | 122.9599 | 0.27008 | 0.19684 | 123.2391 | 0.2655 | 122.9416 | 122.9004 | -123.1979 | -0.2655 | 122.6624 | 122.8317 | 122.3785 | 122.7722
757.0312 | 122.9736 | -122.7448 | 0.21057 | 0.0034333 | 0.0060328 | 0.070867 | 0.066768 | 0.0054453 | 0.00020291 | 0.003499 | 0.001648 | 0.016237 | 0.022063 | 0.019598 | -0.0026019 | 0.010587 | 0.0013714 | -0.24261 | 0.23804 | -123.0286 | -0.050354 | -122.0947 | -122.7036 | -122.7631 | 0.036621 | 0.20599 | -0.073242 | 0.064087 | 0.15106 | 0.059509 | 0.19684 | -0.28381 | 0.027466 | -0.26093 | 0.65002 | -0.018311 | 0.041199 | 0.2655 | 0.32501 | 122.6715 | -0.004577 | -0.14648 | 122.8958 | 122.9416 | 122.8043 | 0.27008 | 0.13275 | 0.93384 | 122.9782 | 0.2243 | 0.13733 | 123.2666 | 0.27924 | 122.9828 | 122.9507 | -123.2391 | -0.28381 | 122.6944 | 122.8088 | 122.5021 | 122.7814
758.7656 | 122.9691 | -122.7676 | 0.19684 | 0.018692 | 0.0028284 | 0.070226 | 0.06335 | 0.0060861 | -0.0038559 | -0.0033368 | 0.0077514 | 0.01816 | 0.019927 | 0.025579 | 0.00081607 | 0.0082374 | 0.0043622 | -0.28381 | 0.24261 | -123.0515 | -0.073242 | -122.1268 | -122.6898 | -122.7585 | 0 | 0.20599 | -0.10071 | 0.045776 | 0.13275 | 0.032043 | 0.1831 | -0.28381 | 0.045777 | -0.27008 | 0.64087 | 0.009155 | 0.07782 | 0.29297 | 0.36163 | 122.6669 | 0.009156 | -0.15106 | 122.9004 | 122.9507 | 122.7997 | 0.28381 | 0.13275 | 0.92468 | 122.9782 | 0.23346 | 0.14648 | 123.2941 | 0.3067 | 123.0103 | 122.9736 | -123.2483 | -0.29755 | 122.6944 | 122.8134 | 122.4838 | 122.7676
760.4531 | 122.937 | -122.7722 | 0.20599 | 0.0034333 | 0.0058192 | 0.069799 | 0.06805 | 0.0060861 | -0.0023605 | -0.00055975 | 0.001648 | 0.019655 | 0.022277 | 0.020239 | -0.00046573 | 0.011869 | 0.00073059 | -0.2655 | 0.23346 | -123.0377 | -0.050354 | -122.1313 | -122.7356 | -122.7951 | -0.013733 | 0.20599 | -0.10529 | 0.009155 | 0.091553 | -0.004578 | 0.13275 | -0.2655 | 0.027465 | -0.25635 | 0.64087 | -0.022888 | 0.036621 | 0.24261 | 0.30212 | 122.6669 | 0 | -0.19684 | 122.8638 | 122.905 | 122.7676 | 0.23804 | 0.10071 | 0.90637 | 122.9874 | 0.19684 | 0.11444 | 123.2712 | 0.31128 | 123.0057 | 122.9782 | -123.2437 | -0.31128 | 122.7219 | 122.7814 | 122.5067 | 122.7585
762.2031 | 123.0789 | -122.7081 | 0.16937 | 0.011063 | 0.0043238 | 0.071295 | 0.0657 | 0.00095914 | -0.0025741 | 8.125e-05 | 0.001648 | 0.012606 | 0.018859 | 0.02622 | -0.00089293 | 0.009519 | -0.001192 | -0.28839 | 0.18768 | -122.9965 | 0.013733 | -122.0032 | -122.5845 | -122.6624 | 0.15564 | 0.17395 | -0.045776 | 0.1236 | 0.23804 | 0.14648 | 0.24261 | -0.28839 | 0.01831 | -0.15564 | 0.70496 | 0.045776 | 0.1236 | 0.33417 | 0.41199 | 122.6624 | 0.004577 | -0.045777 | 122.9462 | 122.9507 | 122.8546 | 0.28839 | 0.19226 | 0.99335 | 123.0103 | 0.28381 | 0.16937 | 123.1842 | 0.21973 | 122.8958 | 122.8821 | -123.1659 | -0.21515 | 122.7219 | 122.8317 | 122.4197 | 122.8638
763.9531 | 122.9187 | -122.7676 | 0.21973 | 0.0034333 | 0.0077418 | 0.067022 | 0.067622 | 0.0043771 | -0.0019333 | -0.00055975 | 0.001648 | 0.016237 | 0.02014 | 0.034765 | 0.0014569 | 0.010374 | -0.001192 | -0.30212 | 0.21973 | -123.0148 | -0.10071 | -122.1725 | -122.7722 | -122.8088 | -0.073242 | 0.21973 | -0.091553 | 0.004578 | 0.064087 | -0.027466 | 0.1236 | -0.24719 | 0 | -0.32044 | 0.59509 | -0.041199 | -0.004578 | 0.20599 | 0.24262 | 122.6761 | 0 | -0.21515 | 122.8317 | 122.8912 | 122.7402 | 0.21515 | 0.064087 | 0.84229 | 122.9141 | 0.15564 | 0.096131 | 123.2346 | 0.31128 | 122.9874 | 122.9874 | -123.2346 | -0.31128 | 122.6669 | 122.7722 | 122.4655 | 122.6944
765.625 | 123.024 | -122.7264 | 0.17853 | 0.011063 | 0.0051782 | 0.07044 | 0.063564 | 0.0033089 | 0.00041651 | -0.002696 | 0.001648 | 0.016237 | 0.0195 | 0.029638 | 0.0027387 | 0.011228 | 0.0013714 | -0.30212 | 0.21515 | -122.9416 | 0.032043 | -122.0123 | -122.6395 | -122.6852 | 0.11444 | 0.16937 | -0.068665 | 0.13275 | 0.21515 | 0.10529 | 0.23346 | -0.21515 | 0.036621 | -0.14648 | 0.71411 | 0.041198 | 0.086975 | 0.25635 | 0.30212 | 122.6578 | -0.009155 | -0.045777 | 122.9416 | 122.9599 | 122.8317 | 0.30212 | 0.17395 | 0.92926 | 122.9736 | 0.28381 | 0.20142 | 123.1567 | 0.23804 | 122.9416 | 122.8958 | -123.1201 | -0.24719 | 122.7585 | 122.8592 | 122.4243 | 122.8409
767.375 | 122.9187 | -122.7859 | 0.20599 | -0.011826 | 0.0034692 | 0.068945 | 0.0657 | 0.0067269 | -0.0012925 | 8.125e-05 | 0.0077514 | 0.015169 | 0.022063 | 0.027715 | -0.0028155 | 0.0071692 | 0.00030339 | -0.31128 | 0.23346 | -123.0423 | -0.091553 | -122.1359 | -122.7219 | -122.7768 | -0.041199 | 0.21973 | -0.091553 | 0 | 0.10071 | 0.027466 | 0.12817 | -0.25635 | 0.027465 | -0.29755 | 0.65002 | 0.009156 | 0.064087 | 0.2655 | 0.32043 | 122.6944 | 0.013733 | -0.20599 | 122.8867 | 122.9141 | 122.8134 | 0.21973 | 0.11902 | 0.90637 | 122.9507 | 0.19226 | 0.091553 | 123.2758 | 0.31128 | 123.0194 | 123.0057 | -123.2483 | -0.29755 | 122.6944 | 122.7859 | 122.4747 | 122.7448
769.125 | 123.0469 | -122.7264 | 0.18768 | 0.011063 | 0.00047857 | 0.069586 | 0.065273 | 0.0018137 | -0.0010789 | -0.00098695 | -0.0014038 | 0.015169 | 0.02014 | 0.024725 | 0.00081607 | 0.010587 | 0.0017988 | -0.35248 | 0.20142 | -123.0103 | -0.032043 | -122.0673 | -122.6532 | -122.7081 | 0.068665 | 0.18768 | -0.073242 | 0.10529 | 0.20142 | 0.11902 | 0.2243 | -0.28381 | 0.013733 | -0.21973 | 0.65918 | 0.01831 | 0.073242 | 0.30212 | 0.35706 | 122.6532 | 0 | -0.082397 | 122.9279 | 122.9507 | 122.8455 | 0.29755 | 0.19226 | 0.94299 | 122.9782 | 0.27466 | 0.17853 | 123.2117 | 0.26092 | 122.9279 | 122.9141 | -123.1979 | -0.26092 | 122.6944 | 122.8317 | 122.374 | 122.7951
770.8125 | 122.9507 | -122.7493 | 0.17395 | 0.0034333 | 0.0060328 | 0.068517 | 0.068263 | 0.0039499 | -0.0025741 | -0.0020552 | 0.001648 | 0.016878 | 0.021636 | 0.026006 | 0.0020979 | 0.0090918 | 0.00094419 | -0.24719 | 0.2243 | -123.0331 | -0.027466 | -122.0993 | -122.6807 | -122.7356 | 0.045776 | 0.20599 | -0.073242 | 0.07782 | 0.1236 | 0.036621 | 0.17853 | -0.28381 | 0.050354 | -0.20142 | 0.65002 | 0.013733 | 0.068665 | 0.29755 | 0.35248 | 122.6761 | 0.032044 | -0.09613 | 122.8729 | 122.9279 | 122.7859 | 0.25177 | 0.10986 | 0.93384 | 123.0057 | 0.19684 | 0.15106 | 123.2574 | 0.27924 | 122.9736 | 122.9553 | -123.2071 | -0.24719 | 122.7219 | 122.8271 | 122.5021 | 122.7951
772.5625 | 122.9507 | -122.7493 | 0.2243 | 0.018692 | 0.0045374 | 0.070013 | 0.065913 | 0.0045907 | -0.0032151 | -0.0012006 | 0.001648 | 0.017306 | 0.020781 | 0.024297 | -0.00025213 | 0.0090918 | 0.001585 | -0.27924 | 0.24261 | -123.0286 | -0.086975 | -122.1634 | -122.7036 | -122.7722 | -0.059509 | 0.2243 | -0.086975 | 0.018311 | 0.11444 | 0.013733 | 0.15564 | -0.27923 | 0.018311 | -0.31128 | 0.58594 | -0.022888 | 0.045777 | 0.25635 | 0.32501 | 122.6624 | 0 | -0.20599 | 122.8638 | 122.905 | 122.7631 | 0.24261 | 0.10071 | 0.86517 | 122.9416 | 0.20142 | 0.10529 | 123.2712 | 0.31128 | 122.9919 | 122.9736 | -123.2529 | -0.31128 | 122.6624 | 122.7676 | 122.4701 | 122.6898
774.3125 | 123.024 | -122.7356 | 0.19226 | 0.011063 | 0.0028284 | 0.070654 | 0.064418 | 0.0013863 | -0.0012925 | -0.0012006 | 0.0046998 | 0.014315 | 0.018645 | 0.026434 | 0.00060247 | 0.0093054 | 0.0024396 | -0.35248 | 0.20599 | -122.9874 | -0.041199 | -122.081 | -122.6669 | -122.7173 | 0.022888 | 0.1831 | -0.068665 | 0.082397 | 0.19226 | 0.10529 | 0.21057 | -0.25177 | 0.013733 | -0.23346 | 0.6546 | 0.018311 | 0.068665 | 0.27008 | 0.32043 | 122.6669 | -0.009156 | -0.10986 | 122.9279 | 122.9462 | 122.8409 | 0.27924 | 0.17395 | 0.90637 | 122.9462 | 0.26093 | 0.15106 | 123.1934 | 0.25177 | 122.9416 | 122.9187 | -123.1796 | -0.26093 | 122.6944 | 122.818 | 122.3831 | 122.7585
776 | 122.9874 | -122.7356 | 0.20142 | 0.0034333 | 0.0062464 | 0.071508 | 0.064418 | 0.0058725 | -0.0015061 | -0.00098695 | -0.0044556 | 0.015597 | 0.017791 | 0.031561 | -0.00046573 | 0.009519 | 0.0011578 | -0.33875 | 0.20142 | -122.9919 | -0.022888 | -122.0627 | -122.6715 | -122.7127 | 0.041199 | 0.18768 | -0.064087 | 0.07782 | 0.14648 | 0.073242 | 0.19226 | -0.25635 | 0 | -0.2243 | 0.67291 | 0.022888 | 0.064087 | 0.27923 | 0.32043 | 122.6715 | -0.013733 | -0.1236 | 122.8821 | 122.9279 | 122.8088 | 0.25635 | 0.13733 | 0.92926 | 122.9691 | 0.21057 | 0.14191 | 123.1934 | 0.25177 | 122.937 | 122.9233 | -123.1934 | -0.2655 | 122.7127 | 122.8134 | 122.3969 | 122.7768
777.7344 | 123.0377 | -122.7585 | 0.19226 | 0.0034333 | 0.0032556 | 0.069586 | 0.064418 | 0.0033089 | -0.0025741 | -0.00013235 | -0.0014038 | 0.014101 | 0.017577 | 0.027288 | 0.00060247 | 0.011228 | 0.0020124 | -0.33875 | 0.20599 | -122.9965 | -0.027466 | -122.0901 | -122.644 | -122.6898 | 0.050354 | 0.1831 | -0.068665 | 0.10529 | 0.20142 | 0.10986 | 0.22888 | -0.23804 | 0.013733 | -0.21973 | 0.66833 | 0.068665 | 0.11444 | 0.3067 | 0.35248 | 122.6898 | -0.009156 | -0.086975 | 122.9599 | 122.9874 | 122.8683 | 0.29755 | 0.17853 | 0.90637 | 122.9691 | 0.27008 | 0.17395 | 123.2025 | 0.25177 | 122.9645 | 122.9416 | -123.1888 | -0.26093 | 122.731 | 122.8638 | 122.4197 | 122.8088
779.4688 | 122.9233 | -122.7676 | 0.21515 | -0.0041962 | 0.0032556 | 0.068731 | 0.064204 | 0.0045907 | -0.0012925 | -0.0022688 | -0.0014038 | 0.015383 | 0.021636 | 0.030493 | -0.00089293 | 0.009519 | -0.0041828 | -0.25635 | 0.21057 | -123.0194 | -0.036621 | -122.0993 | -122.6578 | -122.731 | 0.013733 | 0.20142 | -0.10529 | 0.004578 | 0.10986 | 0.013733 | 0.1236 | -0.25177 | -0.004578 | -0.25177 | 0.66833 | 0.036621 | 0.10986 | 0.28839 | 0.36163 | 122.6624 | -0.013733 | -0.21057 | 122.8775 | 122.8912 | 122.7814 | 0.22888 | 0.11902 | 0.9201 | 122.9828 | 0.21515 | 0.10986 | 123.23 | 0.3067 | 122.9782 | 122.9691 | -123.2346 | -0.32044 | 122.731 | 122.7722 | 122.5113 | 122.7814
781.2188 | 122.9416 | -122.7631 | 0.23346 | 0.011063 | 0.0058192 | 0.069799 | 0.065486 | 0.0067269 | -0.0012925 | -0.0050458 | 0.0046998 | 0.019442 | 0.021636 | 0.021093 | -0.0015337 | 0.0088782 | -0.0016192 | -0.28381 | 0.23804 | -123.0606 | -0.10071 | -122.1497 | -122.7173 | -122.7722 | -0.036621 | 0.2243 | -0.11444 | 0.018311 | 0.10986 | 0.013733 | 0.15564 | -0.29755 | 0.004578 | -0.33417 | 0.6134 | -0.009155 | 0.045777 | 0.28839 | 0.34332 | 122.6486 | -0.009155 | -0.21515 | 122.8729 | 122.9187 | 122.7768 | 0.27008 | 0.12817 | 0.91095 | 122.9599 | 0.2243 | 0.13275 | 123.2986 | 0.33875 | 123.0011 | 122.9874 | -123.2941 | -0.3479 | 122.6624 | 122.7814 | 122.4792 | 122.7264
782.9688 | 122.9919 | -122.7264 | 0.17853 | 0.0034333 | 0.0051782 | 0.070654 | 0.064845 | 0.0065133 | -0.0023605 | -0.0012006 | 0.0046998 | 0.016237 | 0.020995 | 0.028784 | 0.0010297 | 0.0082374 | 0.00094419 | -0.31128 | 0.1831 | -122.9736 | 0.022888 | -122.0398 | -122.6624 | -122.7127 | 0.10071 | 0.17853 | -0.064087 | 0.11444 | 0.1831 | 0.086975 | 0.19684 | -0.24719 | 0.004577 | -0.15564 | 0.68664 | 0.013732 | 0.064086 | 0.26093 | 0.31128 | 122.6624 | 0 | -0.064087 | 122.9095 | 122.9233 | 122.8134 | 0.26093 | 0.15106 | 0.93384 | 122.9965 | 0.24719 | 0.17853 | 123.1567 | 0.24261 | 122.9095 | 122.905 | -123.1522 | -0.24261 | 122.7493 | 122.8409 | 122.4152 | 122.8271
784.6406 | 122.9507 | -122.7448 | 0.21057 | -0.0041962 | 0.0049646 | 0.069372 | 0.065273 | 0.0037363 | -0.0019333 | -0.0016278 | 0.001648 | 0.016665 | 0.02014 | 0.028356 | 0.00081607 | 0.0099462 | -0.0026874 | -0.33417 | 0.24261 | -123.0194 | -0.091553 | -122.168 | -122.7631 | -122.7997 | -0.018311 | 0.21057 | -0.086975 | 0.054932 | 0.09613 | 0.004578 | 0.15106 | -0.27466 | 0.032044 | -0.30212 | 0.57678 | -0.054932 | -0.018311 | 0.21973 | 0.25635 | 122.6578 | 0 | -0.15564 | 122.8409 | 122.8958 | 122.7493 | 0.23804 | 0.091553 | 0.85144 | 122.9279 | 0.1831 | 0.14191 | 123.262 | 0.29755 | 122.9874 | 122.9553 | -123.23 | -0.29755 | 122.6532 | 122.7997 | 122.4106 | 122.7264
786.4062 | 122.9553 | -122.7219 | 0.21057 | 0.011063 | 0.00646 | 0.070654 | 0.065273 | 0.0033089 | -0.0034287 | 8.125e-05 | 0.0046998 | 0.017092 | 0.020995 | 0.026434 | 0.00017507 | 0.0097326 | -0.005678 | -0.25177 | 0.22888 | -123.0423 | -0.041199 | -122.1176 | -122.6944 | -122.7493 | 0.018311 | 0.20599 | -0.082397 | 0.050354 | 0.14648 | 0.036621 | 0.19226 | -0.32043 | 0.018311 | -0.25177 | 0.60425 | -0.027466 | 0.027466 | 0.29297 | 0.3479 | 122.6395 | -0.004577 | -0.16022 | 122.8683 | 122.9141 | 122.7585 | 0.27466 | 0.11902 | 0.92468 | 123.0011 | 0.22888 | 0.13275 | 123.2712 | 0.28839 | 122.9507 | 122.9279 | -123.2529 | -0.29297 | 122.6807 | 122.7722 | 122.4701 | 122.7402
788.0938 | 122.9965 | -122.7173 | 0.19226 | 0.018692 | 0.0017602 | 0.071722 | 0.065486 | 0.0067269 | -0.00065149 | 0.00093565 | 0.0046998 | 0.015383 | 0.022277 | 0.019598 | -0.00025213 | 0.0093054 | 0.001585 | -0.32044 | 0.18768 | -122.9736 | 0.004578 | -122.0306 | -122.6715 | -122.7219 | 0.10986 | 0.20142 | -0.054932 | 0.10071 | 0.1831 | 0.091553 | 0.21515 | -0.25635 | -0.004578 | -0.18768 | 0.68664 | -0.004578 | 0.045776 | 0.25177 | 0.30212 | 122.6624 | 0.009155 | -0.091553 | 122.9004 | 122.9324 | 122.8088 | 0.27008 | 0.14649 | 0.94299 | 122.9782 | 0.23804 | 0.15564 | 123.1613 | 0.25635 | 122.905 | 122.9187 | -123.1659 | -0.24719 | 122.7219 | 122.818 | 122.3969 | 122.8271
789.8438 | 122.9736 | -122.731 | 0.18768 | 0.0034333 | 0.0058192 | 0.070226 | 0.063991 | 0.0043771 | -0.00086509 | 0.00072205 | 0.001648 | 0.01346 | 0.020354 | 0.025793 | -0.0017475 | 0.010374 | -0.00055121 | -0.35248 | 0.21515 | -122.9828 | -0.032043 | -122.0947 | -122.6624 | -122.699 | 0.036621 | 0.21057 | -0.068665 | 0.059509 | 0.18768 | 0.091553 | 0.21515 | -0.25177 | 0.027466 | -0.21973 | 0.63629 | 0.032043 | 0.068664 | 0.28381 | 0.32043 | 122.6624 | 0.022888 | -0.12817 | 122.9187 | 122.9462 | 122.8226 | 0.28381 | 0.16022 | 0.88806 | 122.9507 | 0.25635 | 0.12817 | 123.1979 | 0.27924 | 122.9462 | 122.9416 | -123.1705 | -0.25635 | 122.699 | 122.7905 | 122.3785 | 122.7676
791.5781 | 122.9187 | -122.7539 | 0.20142 | 0.011063 | 0.0038966 | 0.071081 | 0.061855 | 0.0033089 | -0.0059921 | -0.00098695 | 0.0046998 | 0.016878 | 0.02014 | 0.034338 | -0.0045245 | 0.008451 | 0.0028668 | -0.27008 | 0.20142 | -123.0057 | -0.022888 | -122.0673 | -122.644 | -122.7173 | 0.009155 | 0.21057 | -0.073242 | 0.022888 | 0.13275 | 0.041199 | 0.12817 | -0.25177 | 0 | -0.2243 | 0.68664 | 0.036621 | 0.10986 | 0.28839 | 0.36163 | 122.6807 | 0.009155 | -0.17853 | 122.8867 | 122.8821 | 122.7951 | 0.20142 | 0.11444 | 0.93841 | 122.9828 | 0.20599 | 0.09613 | 123.2071 | 0.28381 | 122.9553 | 122.9645 | -123.2071 | -0.27466 | 122.731 | 122.7768 | 122.4838 | 122.7631
793.2812 | 123.056 | -122.7173 | 0.18768 | 0.0034333 | 0.0049646 | 0.071081 | 0.063136 | 0.0015999 | -0.0032151 | 0.00050845 | 0.001648 | 0.016024 | 0.019072 | 0.021948 | 0.0018841 | 0.0071692 | 0.0020124 | -0.33875 | 0.20142 | -122.9828 | 0.013733 | -122.0306 | -122.6074 | -122.6532 | 0.082397 | 0.18768 | -0.064087 | 0.12817 | 0.2243 | 0.14191 | 0.24719 | -0.2655 | 0.013733 | -0.17395 | 0.68664 | 0.064087 | 0.10986 | 0.32959 | 0.37537 | 122.6532 | 0 | -0.059509 | 122.9416 | 122.9645 | 122.8592 | 0.31128 | 0.20599 | 0.95215 | 122.9965 | 0.28839 | 0.19226 | 123.1842 | 0.25177 | 122.9187 | 122.905 | -123.1705 | -0.25177 | 122.731 | 122.8455 | 122.3785 | 122.7997
795.0156 | 122.9187 | -122.7493 | 0.19684 | 0.0034333 | 0.0038966 | 0.070654 | 0.066127 | 0.0056589 | -0.00065149 | -0.0018414 | -0.0014038 | 0.017946 | 0.02014 | 0.029852 | -3.8532e-05 | 0.008451 | 0.00094419 | -0.34332 | 0.24261 | -123.0103 | -0.10071 | -122.1542 | -122.7448 | -122.7814 | -0.045776 | 0.2243 | -0.09613 | 0.036621 | 0.086975 | 0 | 0.15106 | -0.26093 | 0.045777 | -0.29755 | 0.59509 | -0.032043 | 0.004578 | 0.22888 | 0.2655 | 122.6532 | 0.027466 | -0.16022 | 122.8363 | 122.9004 | 122.7493 | 0.24719 | 0.09613 | 0.85602 | 122.9095 | 0.1831 | 0.13275 | 123.2529 | 0.32043 | 122.9919 | 122.9736 | -123.2071 | -0.29297 | 122.6486 | 122.7859 | 122.406 | 122.7036
796.7656 | 122.9874 | -122.7219 | 0.19226 | 0.0034333 | 0.0038966 | 0.071508 | 0.0657 | 0.0041635 | -0.00022429 | 0.0026446 | 0.0046998 | 0.016024 | 0.023558 | 0.030493 | 0.00017507 | 0.0082374 | -0.00055121 | -0.32501 | 0.21515 | -123.0011 | 0.018311 | -122.0169 | -122.6486 | -122.699 | 0.091553 | 0.19684 | -0.054932 | 0.10071 | 0.18768 | 0.091553 | 0.21057 | -0.27924 | 0.022888 | -0.17395 | 0.70496 | 0.022888 | 0.073242 | 0.30212 | 0.35248 | 122.6669 | 0.004577 | -0.091553 | 122.9095 | 122.9324 | 122.8134 | 0.2655 | 0.14649 | 0.98419 | 123.0194 | 0.24261 | 0.15564 | 123.2162 | 0.25177 | 122.937 | 122.9187 | -123.1934 | -0.24719 | 122.7402 | 122.8226 | 122.3969 | 122.8134
798.5312 | 122.9645 | -122.7127 | 0.19226 | 0.0034333 | 0.0058192 | 0.069586 | 0.066982 | 0.0043771 | -0.0017197 | -0.00098695 | 0.001648 | 0.016665 | 0.019713 | 0.026006 | -0.0015337 | 0.008451 | -0.0041828 | -0.25635 | 0.21057 | -123.0377 | -0.036621 | -122.0764 | -122.6715 | -122.7264 | 0.036621 | 0.21515 | -0.086975 | 0.064087 | 0.15106 | 0.059509 | 0.19226 | -0.32501 | 0.01831 | -0.22888 | 0.63629 | -0.013732 | 0.041199 | 0.31128 | 0.36621 | 122.6257 | 0.022888 | -0.12817 | 122.8638 | 122.905 | 122.7722 | 0.27924 | 0.14648 | 0.9613 | 123.0011 | 0.23804 | 0.15106 | 123.2483 | 0.30212 | 122.9233 | 122.9279 | -123.23 | -0.27924 | 122.6761 | 122.7768 | 122.4564 | 122.7493
800.2188 | 122.9507 | -122.7264 | 0.20599 | 0.0034333 | 0.0056054 | 0.068517 | 0.066341 | 0.0071541 | -0.0027877 | -0.00077335 | 0.001648 | 0.017306 | 0.021636 | 0.030065 | -0.0011065 | 0.0097326 | -0.001192 | -0.26093 | 0.23804 | -123.0148 | -0.050354 | -122.0901 | -122.6578 | -122.731 | 0.018311 | 0.22888 | -0.091553 | 0.050354 | 0.15564 | 0.045776 | 0.17395 | -0.28839 | 0.032043 | -0.25635 | 0.63629 | -0.004578 | 0.068664 | 0.28381 | 0.35706 | 122.6349 | 0.022888 | -0.15564 | 122.8821 | 122.9004 | 122.7722 | 0.2655 | 0.13733 | 0.92468 | 122.9645 | 0.24719 | 0.14191 | 123.2529 | 0.32044 | 122.9645 | 122.9553 | -123.2208 | -0.29755 | 122.6761 | 122.7768 | 122.4655 | 122.7448
801.9531 | 122.9828 | -122.6944 | 0.19684 | 0.018692 | 0.003042 | 0.069586 | 0.064845 | 0.0024545 | -0.0021469 | -0.0022688 | 0.0046998 | 0.016024 | 0.021422 | 0.024938 | -0.00067933 | 0.0097326 | 0.0043622 | -0.37079 | 0.17853 | -122.9691 | -0.027466 | -122.0718 | -122.6532 | -122.7081 | 0.041199 | 0.17395 | -0.086975 | 0.082397 | 0.15564 | 0.082397 | 0.19684 | -0.27466 | -0.01831 | -0.2243 | 0.62256 | -0.013733 | 0.041199 | 0.26093 | 0.31586 | 122.6074 | -0.022888 | -0.11444 | 122.85 | 122.8912 | 122.7768 | 0.28381 | 0.16937 | 0.89722 | 122.9416 | 0.24261 | 0.16937 | 123.1476 | 0.26092 | 122.8729 | 122.8683 | -123.1659 | -0.28381 | 122.6669 | 122.7768 | 122.3236 | 122.7356
803.6406 | 122.8958 | -122.7539 | 0.21515 | 0.0034333 | 0.0038966 | 0.070867 | 0.066768 | 0.0024545 | -0.0023605 | -0.00077335 | 0.0046998 | 0.016665 | 0.0195 | 0.018316 | -0.0013201 | 0.0071692 | 0.0043622 | -0.31586 | 0.25177 | -123.0286 | -0.07782 | -122.1313 | -122.6944 | -122.7585 | -0.059509 | 0.21515 | -0.10529 | -0.009155 | 0.086975 | -0.004578 | 0.13733 | -0.27466 | 0.036621 | -0.29297 | 0.62256 | -0.004578 | 0.059509 | 0.27008 | 0.33417 | 122.6486 | 0 | -0.2243 | 122.8409 | 122.8912 | 122.7493 | 0.24262 | 0.10071 | 0.89722 | 122.9507 | 0.19226 | 0.096131 | 123.2803 | 0.32044 | 123.0057 | 122.9691 | -123.2437 | -0.32044 | 122.6761 | 122.7448 | 122.438 | 122.6944
805.3906 | 122.9095 | -122.7127 | 0.21057 | 0.0034333 | 0.0071008 | 0.068945 | 0.068263 | 0.0018137 | -0.0023605 | -0.0020552 | 0.0046998 | 0.018801 | 0.020354 | 0.022802 | 0.0010297 | 0.0080236 | -0.0022602 | -0.29297 | 0.22888 | -122.9965 | -0.064087 | -122.1176 | -122.7127 | -122.7768 | -0.018311 | 0.2243 | -0.09613 | 0.027466 | 0.086975 | -0.013733 | 0.14191 | -0.28381 | 0.018311 | -0.27466 | 0.59509 | -0.064086 | 0 | 0.21973 | 0.28381 | 122.6166 | 0.013733 | -0.18311 | 122.7997 | 122.8546 | 122.699 | 0.23804 | 0.082397 | 0.87891 | 122.9324 | 0.1831 | 0.1236 | 123.2254 | 0.32043 | 122.9416 | 122.937 | -123.2071 | -0.3067 | 122.6486 | 122.7402 | 122.4197 | 122.6944
807.1562 | 123.0103 | -122.7081 | 0.17853 | 0.011063 | 0.0049646 | 0.072363 | 0.063777 | 0.0060861 | -0.0025741 | 0.00093565 | 0.001648 | 0.014315 | 0.019286 | 0.030493 | -0.0019611 | 0.00781 | 0.0011578 | -0.29297 | 0.18768 | -122.9462 | 0.032043 | -121.9482 | -122.58 | -122.6349 | 0.12817 | 0.1831 | -0.073242 | 0.13275 | 0.24719 | 0.15564 | 0.23346 | -0.23804 | 0.009155 | -0.14648 | 0.75989 | 0.073242 | 0.12817 | 0.31128 | 0.36621 | 122.6349 | 0.004577 | -0.045777 | 122.9553 | 122.9416 | 122.8638 | 0.3067 | 0.22888 | 0.99793 | 122.9782 | 0.32043 | 0.20599 | 123.1339 | 0.25635 | 122.8958 | 122.8912 | -123.1247 | -0.25177 | 122.7402 | 122.8409 | 122.4152 | 122.8363
808.8281 | 122.9416 | -122.7539 | 0.21057 | 0.018692 | 0.0051782 | 0.067877 | 0.068904 | -0.00032266 | -0.0030015 | -0.00098695 | 0.001648 | 0.016451 | 0.021422 | 0.026861 | -0.0021747 | 0.0080236 | -0.0014056 | -0.29297 | 0.24261 | -123.0286 | -0.09613 | -122.1313 | -122.6852 | -122.731 | -0.050354 | 0.22888 | -0.11444 | 0.032043 | 0.11902 | 0.018311 | 0.16937 | -0.27466 | 0.032044 | -0.3067 | 0.62256 | 0.022888 | 0.068664 | 0.29755 | 0.34332 | 122.6395 | 0.018311 | -0.17853 | 122.8729 | 122.9233 | 122.7722 | 0.28381 | 0.13275 | 0.89722 | 122.9324 | 0.23346 | 0.14648 | 123.2712 | 0.34332 | 122.9965 | 122.9828 | -123.2391 | -0.32501 | 122.6578 | 122.7859 | 122.4609 | 122.7036
810.5625 | 122.9279 | -122.7402 | 0.21515 | 0.0034333 | 0.0051782 | 0.070013 | 0.062709 | -0.00032266 | -0.0021469 | -0.00013235 | 0.0046998 | 0.014529 | 0.0195 | 0.02387 | -0.0013201 | 0.00781 | 0.0017988 | -0.29297 | 0.19684 | -122.9736 | -0.036621 | -122.0444 | -122.6303 | -122.6944 | 0.004578 | 0.20142 | -0.091553 | 0.032043 | 0.13733 | 0.027466 | 0.15106 | -0.23346 | -0.018311 | -0.25177 | 0.6958 | 0.045776 | 0.10986 | 0.27924 | 0.34332 | 122.6486 | -0.013733 | -0.18311 | 122.8775 | 122.8912 | 122.7676 | 0.24261 | 0.11902 | 0.92926 | 122.937 | 0.22888 | 0.1236 | 123.1705 | 0.29297 | 122.937 | 122.9416 | -123.1888 | -0.3067 | 122.7036 | 122.7722 | 122.4472 | 122.7448
812.3125 | 122.905 | -122.7585 | 0.1831 | 0.0034333 | 0.0058192 | 0.071722 | 0.067622 | 0.0082223 | -1.0686e-05 | 0.0011492 | -0.0044556 | 0.017519 | 0.022277 | 0.019384 | 0.0031659 | 0.010587 | 0.003294 | -0.35248 | 0.23346 | -123.0194 | -0.11902 | -122.2 | -122.7768 | -122.8043 | -0.068665 | 0.20142 | -0.10529 | 0.004578 | 0.059509 | -0.036621 | 0.13275 | -0.26093 | 0.050354 | -0.30212 | 0.55847 | -0.045776 | -0.01831 | 0.21515 | 0.24262 | 122.6532 | 0.018311 | -0.17853 | 122.818 | 122.8912 | 122.7219 | 0.23804 | 0.068665 | 0.8194 | 122.9004 | 0.16479 | 0.10986 | 123.2529 | 0.3067 | 122.9919 | 122.9599 | -123.2025 | -0.28839 | 122.6395 | 122.7631 | 122.406 | 122.6898
814.0625 | 123.0148 | -122.7219 | 0.17395 | 0.0034333 | 0.0058192 | 0.071295 | 0.064632 | 0.0022409 | -0.0012925 | 0.00093565 | 0.001648 | 0.016024 | 0.02014 | 0.029638 | 0.0023115 | 0.010801 | -0.002901 | -0.35706 | 0.2243 | -122.9736 | -0.059509 | -122.0947 | -122.6807 | -122.7356 | 0.059509 | 0.17853 | -0.086975 | 0.10529 | 0.1831 | 0.086975 | 0.21973 | -0.25177 | 0.050354 | -0.23346 | 0.62714 | -0.013733 | 0.041199 | 0.23804 | 0.29297 | 122.6349 | 0.004578 | -0.068664 | 122.905 | 122.9416 | 122.8088 | 0.3067 | 0.17395 | 0.87891 | 122.9141 | 0.27008 | 0.19226 | 123.1979 | 0.2655 | 122.9462 | 122.9004 | -123.1476 | -0.26092 | 122.6624 | 122.8271 | 122.3648 | 122.7814
815.75 | 123.0286 | -122.7036 | 0.17853 | -0.0041962 | 0.0021876 | 0.072576 | 0.062496 | 0.0013863 | -0.0027877 | 0.0011492 | 0.0046998 | 0.014956 | 0.0195 | 0.025366 | -0.00046573 | 0.00781 | 0.00073059 | -0.29755 | 0.16937 | -122.9965 | 0.013733 | -121.962 | -122.5708 | -122.6212 | 0.1236 | 0.1831 | -0.073242 | 0.13275 | 0.25177 | 0.15564 | 0.23346 | -0.29297 | -0.009155 | -0.16479 | 0.74158 | 0.082397 | 0.13275 | 0.37537 | 0.42572 | 122.6303 | 0.004577 | -0.045777 | 122.9553 | 122.937 | 122.8592 | 0.3067 | 0.22888 | 1.0345 | 123.0103 | 0.32501 | 0.20599 | 123.1659 | 0.25635 | 122.8729 | 122.8867 | -123.175 | -0.25177 | 122.7173 | 122.8363 | 122.406 | 122.8271
817.5 | 122.9279 | -122.7402 | 0.21973 | 0.0034333 | 0.00646 | 0.069158 | 0.066127 | 0.0015999 | -0.0023605 | -0.0020552 | 0.0046998 | 0.019015 | 0.019713 | 0.026434 | 0.00081607 | 0.0099462 | -0.00055121 | -0.25635 | 0.20142 | -123.0194 | -0.059509 | -122.0947 | -122.6578 | -122.7264 | 0.018311 | 0.19684 | -0.086975 | 0.041199 | 0.1236 | 0.022888 | 0.16479 | -0.27924 | -0.018311 | -0.27924 | 0.64545 | 0.013733 | 0.082397 | 0.29297 | 0.36163 | 122.6532 | -0.022889 | -0.17853 | 122.8638 | 122.905 | 122.7631 | 0.25177 | 0.10986 | 0.92468 | 122.9599 | 0.21057 | 0.12817 | 123.2208 | 0.28381 | 122.9416 | 122.937 | -123.2391 | -0.3067 | 122.6807 | 122.7814 | 122.4838 | 122.7585
819.25 | 122.9828 | -122.7219 | 0.20142 | 0.011063 | 0.0043238 | 0.071081 | 0.065273 | 0.0020273 | -0.0010789 | 0.00093565 | 0.0046998 | 0.014529 | 0.020781 | 0.025366 | -0.0013201 | 0.0082374 | 0.0024396 | -0.34332 | 0.19684 | -122.9782 | -0.013733 | -122.0352 | -122.6486 | -122.6852 | 0.054932 | 0.20142 | -0.068665 | 0.086975 | 0.16022 | 0.07782 | 0.19684 | -0.25635 | -0.004578 | -0.21515 | 0.68665 | 0.036621 | 0.073242 | 0.29297 | 0.32959 | 122.6532 | 0 | -0.11444 | 122.8821 | 122.9187 | 122.7997 | 0.2655 | 0.14649 | 0.94299 | 122.9645 | 0.22888 | 0.15564 | 123.175 | 0.27008 | 122.9187 | 122.9233 | -123.1796 | -0.27008 | 122.7081 | 122.8088 | 122.3785 | 122.7768
820.9375 | 122.9095 | -122.7585 | 0.22888 | 0.018692 | 0.0038966 | 0.070013 | 0.0657 | 0.0035227 | -0.0047103 | 0.00072205 | 0.0077514 | 0.017306 | 0.023131 | 0.022161 | -0.0028155 | 0.0080236 | 0.0013714 | -0.3067 | 0.24261 | -123.0606 | -0.1236 | -122.1497 | -122.6898 | -122.7539 | -0.068665 | 0.22888 | -0.11902 | 0.009155 | 0.091553 | 0.009155 | 0.14648 | -0.30212 | 0.013733 | -0.35248 | 0.60883 | 0.004578 | 0.068665 | 0.3067 | 0.37079 | 122.6395 | 0 | -0.21973 | 122.85 | 122.905 | 122.7676 | 0.2655 | 0.12817 | 0.91095 | 122.937 | 0.21057 | 0.12817 | 123.3032 | 0.3479 | 123.0011 | 122.9874 | -123.2895 | -0.3479 | 122.6349 | 122.7676 | 122.4518 | 122.6898
822.6875 | 123.0057 | -122.6944 | 0.17395 | 0.026321 | 0.0021876 | 0.071508 | 0.067622 | 0.0013863 | -0.0032151 | 0.0015764 | 0.0046998 | 0.016451 | 0.021849 | 0.026647 | -0.00067933 | 0.008451 | 0.00051699 | -0.33875 | 0.19684 | -122.9828 | -0.027466 | -122.0535 | -122.6166 | -122.6807 | 0.045776 | 0.17395 | -0.07782 | 0.091553 | 0.19684 | 0.1236 | 0.22888 | -0.28839 | 0.022888 | -0.20142 | 0.64087 | 0.013733 | 0.07782 | 0.30212 | 0.36621 | 122.6166 | 0 | -0.082397 | 122.8912 | 122.9233 | 122.818 | 0.3067 | 0.20142 | 0.92926 | 122.9553 | 0.27466 | 0.16937 | 123.1796 | 0.25177 | 122.8912 | 122.8683 | -123.1567 | -0.25177 | 122.6669 | 122.7859 | 122.3557 | 122.7402
824.4375 | 123.0377 | -122.6852 | 0.16937 | 0.011063 | 0.0034692 | 0.07044 | 0.063991 | 0.0024545 | -0.0030015 | -0.0029096 | 0.001648 | 0.015597 | 0.019072 | 0.031561 | -0.0023883 | 0.0097326 | 0.0011578 | -0.32501 | 0.19226 | -122.9782 | 0.004578 | -122.0169 | -122.5845 | -122.6349 | 0.09613 | 0.15106 | -0.068665 | 0.1236 | 0.23804 | 0.14648 | 0.23804 | -0.29297 | 0.022888 | -0.16479 | 0.66833 | 0.050354 | 0.10071 | 0.34332 | 0.39368 | 122.6166 | -0.018311 | -0.045777 | 122.9233 | 122.9233 | 122.8317 | 0.3067 | 0.21515 | 0.9613 | 122.9828 | 0.3067 | 0.19226 | 123.1705 | 0.21973 | 122.8775 | 122.8363 | -123.1476 | -0.23804 | 122.6898 | 122.8088 | 122.3602 | 122.7814
826.125 | 122.9553 | -122.7127 | 0.20142 | 0.018692 | 0.0066736 | 0.070654 | 0.066127 | 0.0028817 | -0.0021469 | 0.00050845 | 0.0046998 | 0.018374 | 0.020995 | 0.028143 | -0.00025213 | 0.009519 | -0.0020464 | -0.2655 | 0.23346 | -122.9919 | -0.036621 | -122.081 | -122.6715 | -122.7264 | 0.036621 | 0.21515 | -0.091553 | 0.068665 | 0.13733 | 0.045776 | 0.19226 | -0.27923 | 0.032043 | -0.23804 | 0.63171 | -0.013732 | 0.041199 | 0.2655 | 0.32043 | 122.6212 | 0.013733 | -0.13275 | 122.85 | 122.905 | 122.7585 | 0.28381 | 0.13733 | 0.91095 | 122.9553 | 0.22888 | 0.16022 | 123.2254 | 0.3067 | 122.9462 | 122.9279 | -123.1934 | -0.29297 | 122.6761 | 122.7814 | 122.4472 | 122.7493
827.8906 | 122.8363 | -122.7768 | 0.21973 | 0.018692 | 0.0053918 | 0.071935 | 0.067836 | 0.0015999 | -1.0686e-05 | 0.0015764 | 0.0046998 | 0.03525 | 0.022063 | 0.02387 | 0.00038887 | 0.010801 | 0.0026532 | -0.28381 | 0.2243 | -122.9553 | -0.050354 | -122.0352 | -122.6257 | -122.6807 | 0.027466 | 0.21515 | -0.10071 | 0.059509 | 0.14191 | 0.036621 | 0.1831 | -0.17853 | 0.004577 | -0.27008 | 0.74158 | 0.09613 | 0.15106 | 0.27466 | 0.32959 | 122.6761 | -0.004578 | -0.16022 | 122.9187 | 122.9599 | 122.8134 | 0.28381 | 0.13733 | 0.9201 | 122.905 | 0.24262 | 0.16022 | 123.1796 | 0.31586 | 123.0011 | 122.9919 | -123.175 | -0.32044 | 122.7264 | 122.8363 | 122.493 | 122.8043
829.5781 | 122.8317 | -122.7448 | 0.21057 | 0.0034333 | 0.0041102 | 0.071935 | 0.066982 | 0.0067269 | -0.0017197 | -0.0020552 | 0.0077514 | 0.037173 | 0.019072 | 0.032629 | 0.0014569 | 0.01251 | -0.0037554 | -0.34332 | 0.21973 | -122.9919 | -0.13275 | -122.1405 | -122.7264 | -122.7722 | -0.054932 | 0.21057 | -0.10986 | 0.027466 | 0.07782 | -0.009155 | 0.14191 | -0.24719 | 0.009156 | -0.34332 | 0.60425 | -0.027466 | 0.018311 | 0.21973 | 0.2655 | 122.6349 | 0 | -0.18311 | 122.8226 | 122.8867 | 122.7356 | 0.25177 | 0.10071 | 0.85144 | 122.8592 | 0.18768 | 0.13733 | 123.2117 | 0.32043 | 122.9645 | 122.9553 | -123.2025 | -0.32043 | 122.612 | 122.7722 | 122.4014 | 122.6898
831.3281 | 122.9645 | -122.6944 | 0.16022 | 0.0034333 | 0.0045374 | 0.070867 | 0.062282 | 0.0026681 | -0.0038559 | -0.002696 | 0.001648 | 0.035036 | 0.021422 | 0.029424 | -3.8532e-05 | 0.0086646 | 0.0041486 | -0.35248 | 0.18768 | -122.9736 | -0.022888 | -122.0078 | -122.5937 | -122.6349 | 0.068665 | 0.17395 | -0.086975 | 0.10986 | 0.2243 | 0.12817 | 0.23346 | -0.27924 | 0.027466 | -0.1831 | 0.68665 | 0.059509 | 0.10071 | 0.33875 | 0.37994 | 122.6074 | 0.013733 | -0.050354 | 122.9187 | 122.9279 | 122.8226 | 0.32043 | 0.21515 | 0.96588 | 122.9507 | 0.31128 | 0.19684 | 123.1613 | 0.26092 | 122.8821 | 122.8683 | -123.1339 | -0.24719 | 122.6715 | 122.8043 | 122.3419 | 122.7631
833.0625 | 122.85 | -122.7173 | 0.23346 | 0.0034333 | 0.0034692 | 0.069158 | 0.065059 | 0.0045907 | -0.0044967 | -0.00055975 | 0.0046998 | 0.037173 | 0.021209 | 0.023229 | -0.0028155 | 0.0080236 | 0.0020124 | -0.33417 | 0.23346 | -123.0148 | -0.09613 | -122.1222 | -122.6486 | -122.7173 | -0.041199 | 0.21057 | -0.10986 | -0.004578 | 0.07782 | -0.013733 | 0.12817 | -0.29755 | 0 | -0.32959 | 0.59509 | 0 | 0.068664 | 0.29755 | 0.36621 | 122.6074 | -0.022888 | -0.23804 | 122.7951 | 122.8455 | 122.7036 | 0.23804 | 0.09613 | 0.89264 | 122.9187 | 0.18768 | 0.10529 | 123.2483 | 0.32043 | 122.9507 | 122.9279 | -123.2483 | -0.34332 | 122.6212 | 122.7127 | 122.3831 | 122.6761
834.7344 | 122.85 | -122.7264 | 0.21515 | 0.011063 | 0.0049646 | 0.069586 | 0.067836 | 0.0033089 | -0.0032151 | 0.00029485 | 0.001648 | 0.036532 | 0.021636 | 0.025152 | -0.00046573 | 0.009519 | 0.0013714 | -0.32044 | 0.2243 | -122.9736 | -0.1236 | -122.1725 | -122.7493 | -122.7768 | -0.073242 | 0.20142 | -0.11444 | 0 | 0.068665 | -0.041199 | 0.14191 | -0.24719 | 0.009155 | -0.33875 | 0.55389 | -0.050354 | -0.022889 | 0.19684 | 0.2243 | 122.612 | -0.013733 | -0.21515 | 122.7951 | 122.8683 | 122.6852 | 0.25635 | 0.073242 | 0.80109 | 122.85 | 0.18311 | 0.11444 | 123.1979 | 0.31586 | 122.9507 | 122.9279 | -123.1888 | -0.32959 | 122.6028 | 122.7264 | 122.406 | 122.6532
836.4844 | 122.9279 | -122.6898 | 0.20599 | 0.011063 | 0.003042 | 0.071295 | 0.063991 | 0.0041635 | -0.0010789 | 0.00072205 | 0.001648 | 0.034182 | 0.020781 | 0.028784 | -0.0023883 | 0.00781 | 0.00094419 | -0.27466 | 0.19226 | -122.9645 | 0.009155 | -121.9803 | -122.5662 | -122.6395 | 0.064087 | 0.19226 | -0.07782 | 0.059509 | 0.17853 | 0.09613 | 0.19226 | -0.27466 | -0.013733 | -0.19684 | 0.70953 | 0.050354 | 0.1236 | 0.32501 | 0.39826 | 122.612 | -0.013733 | -0.14649 | 122.8683 | 122.8821 | 122.7859 | 0.27008 | 0.17395 | 0.98419 | 122.9736 | 0.25635 | 0.13733 | 123.1567 | 0.27008 | 122.8821 | 122.8821 | -123.1705 | -0.28381 | 122.699 | 122.7493 | 122.4152 | 122.7539
838.25 | 123.0148 | -122.6578 | 0.17853 | 0.011063 | 0.0028284 | 0.068731 | 0.06335 | 0.0043771 | -0.0030015 | -0.00034615 | -0.0014038 | 0.035677 | 0.021849 | 0.035192 | 0.00060247 | 0.0088782 | -0.00012381 | -0.31586 | 0.1831 | -122.9507 | 0.009155 | -121.9666 | -122.5616 | -122.6074 | 0.1236 | 0.16937 | -0.059509 | 0.13733 | 0.25177 | 0.16479 | 0.24261 | -0.29297 | 0.004577 | -0.16937 | 0.69122 | 0.050354 | 0.09613 | 0.34332 | 0.3891 | 122.5983 | -0.009155 | -0.041199 | 122.9095 | 122.9004 | 122.8226 | 0.30212 | 0.2243 | 0.98419 | 122.9599 | 0.31128 | 0.19684 | 123.1338 | 0.22888 | 122.8409 | 122.8271 | -123.1293 | -0.23804 | 122.6669 | 122.7951 | 122.3419 | 122.7814
839.9375 | 122.8775 | -122.6807 | 0.20599 | 0.0034333 | 0.0053918 | 0.071722 | 0.06805 | 0.0095041 | -0.0010789 | -0.0022688 | 0.001648 | 0.035036 | 0.021849 | 0.026647 | 0.0018841 | 0.0080236 | 0.0037214 | -0.35706 | 0.21973 | -123.0011 | -0.11444 | -122.1909 | -122.7539 | -122.7631 | -0.064087 | 0.19226 | -0.091553 | 0.009155 | 0.064087 | -0.032043 | 0.1236 | -0.32044 | 0.013733 | -0.32044 | 0.48981 | -0.082398 | -0.073242 | 0.23804 | 0.24719 | 122.5891 | -0.013733 | -0.19684 | 122.7448 | 122.8043 | 122.6486 | 0.21515 | 0.05951 | 0.81024 | 122.8867 | 0.15564 | 0.10071 | 123.2208 | 0.28381 | 122.9004 | 122.8729 | -123.2071 | -0.29755 | 122.5662 | 122.6898 | 122.3236 | 122.6166
841.6719 | 122.9874 | -122.6898 | 0.15564 | 0.033951 | 0.004751 | 0.07279 | 0.065486 | 0.0043771 | -0.0017197 | 0.0011492 | 0.0046998 | 0.036104 | 0.020995 | 0.037115 | 0.00017507 | 0.011228 | 0.0017988 | -0.3067 | 0.1831 | -122.9507 | 0.009155 | -121.9666 | -122.5845 | -122.6349 | 0.12817 | 0.16937 | -0.068665 | 0.1236 | 0.21515 | 0.10529 | 0.23804 | -0.26093 | 0.027465 | -0.14649 | 0.72327 | 0.054931 | 0.10528 | 0.31586 | 0.36621 | 122.6212 | 0.013733 | -0.032044 | 122.905 | 122.9279 | 122.7951 | 0.3067 | 0.17395 | 0.98419 | 122.9599 | 0.28381 | 0.19226 | 123.1338 | 0.23804 | 122.8729 | 122.8592 | -123.1064 | -0.22431 | 122.699 | 122.8134 | 122.3831 | 122.818
843.4219 | 122.9233 | -122.699 | 0.21057 | -0.0041962 | 0.00646 | 0.071295 | 0.066982 | 0.0035227 | -0.0027877 | -0.0052594 | 0.001648 | 0.036318 | 0.019927 | 0.026006 | 0.00038887 | 0.0097326 | -0.00076481 | -0.26093 | 0.23346 | -122.9965 | -0.068665 | -122.0856 | -122.6212 | -122.7081 | 0 | 0.21057 | -0.091553 | 0.036621 | 0.12817 | 0.036621 | 0.17853 | -0.29755 | 0.022888 | -0.27924 | 0.6134 | -0.009155 | 0.07782 | 0.28839 | 0.37537 | 122.6074 | 0 | -0.17395 | 122.8271 | 122.8775 | 122.7356 | 0.27008 | 0.12817 | 0.91095 | 122.9279 | 0.21973 | 0.12817 | 123.23 | 0.30212 | 122.9324 | 122.9095 | -123.2071 | -0.30212 | 122.6303 | 122.7356 | 122.4381 | 122.699
845.1094 | 122.9462 | -122.6761 | 0.19226 | 0.0034333 | 0.004751 | 0.068945 | 0.064632 | 0.0033089 | -0.0021469 | -0.00077335 | -0.0014038 | 0.035677 | 0.021636 | 0.032201 | -0.00089293 | 0.0088782 | 0.002226 | -0.37079 | 0.19226 | -122.9782 | -0.041199 | -122.0535 | -122.644 | -122.6715 | 0.022888 | 0.16937 | -0.082397 | 0.064087 | 0.15564 | 0.050354 | 0.19684 | -0.30212 | 0 | -0.23346 | 0.62256 | 0.004577 | 0.032043 | 0.3067 | 0.33417 | 122.5937 | -0.022888 | -0.12817 | 122.8317 | 122.8729 | 122.7264 | 0.27924 | 0.13275 | 0.92468 | 122.937 | 0.23804 | 0.14648 | 123.1705 | 0.25177 | 122.8683 | 122.8455 | -123.1705 | -0.27466 | 122.6349 | 122.7402 | 122.3053 | 122.699
846.8438 | 123.0057 | -122.6898 | 0.17395 | 0.0034333 | 0.0019738 | 0.07044 | 0.064418 | 0.0043771 | -0.0038559 | -0.00055975 | 0.001648 | 0.034609 | 0.022704 | 0.027929 | -0.0036701 | 0.006742 | -0.00012381 | -0.3067 | 0.18768 | -122.9553 | 0.022888 | -121.9437 | -122.5571 | -122.6166 | 0.09613 | 0.17853 | -0.050354 | 0.1236 | 0.22888 | 0.15564 | 0.24719 | -0.2655 | 0.013733 | -0.15106 | 0.74615 | 0.073242 | 0.13275 | 0.33874 | 0.39825 | 122.6395 | 0.004578 | -0.050354 | 122.9187 | 122.937 | 122.8455 | 0.29755 | 0.20599 | 1.0117 | 122.9782 | 0.27924 | 0.17395 | 123.143 | 0.22888 | 122.8775 | 122.8683 | -123.1293 | -0.2243 | 122.7127 | 122.8134 | 122.3831 | 122.7859
848.5312 | 122.8683 | -122.731 | 0.18768 | 0.018692 | 0.0068872 | 0.070013 | 0.066982 | 0.0052315 | -0.0017197 | -0.00077335 | -0.0014038 | 0.036532 | 0.0195 | 0.026861 | 0.0014569 | 0.0099462 | -0.0026874 | -0.32501 | 0.21515 | -122.9736 | -0.10986 | -122.1405 | -122.7264 | -122.7676 | -0.073242 | 0.20599 | -0.10071 | -0.013733 | 0.045776 | -0.041199 | 0.13733 | -0.24262 | 0.027466 | -0.29755 | 0.59052 | -0.036621 | 0.004578 | 0.20599 | 0.24719 | 122.6303 | 0.018311 | -0.20142 | 122.7768 | 122.8683 | 122.6898 | 0.23804 | 0.059509 | 0.83313 | 122.8638 | 0.14648 | 0.086975 | 123.1888 | 0.3067 | 122.9462 | 122.937 | -123.1613 | -0.28839 | 122.6212 | 122.7173 | 122.406 | 122.6578
850.2656 | 122.8546 | -122.6944 | 0.20142 | -0.0041962 | 0.0045374 | 0.071295 | 0.066554 | 0.0054453 | -0.00022429 | 0.00029485 | 0.001648 | 0.036318 | 0.021422 | 0.033056 | 0.00081607 | 0.0086646 | 0.0024396 | -0.3479 | 0.22888 | -122.9691 | -0.12817 | -122.1268 | -122.7081 | -122.7493 | -0.068665 | 0.19226 | -0.10986 | 0.009155 | 0.068665 | -0.027466 | 0.1236 | -0.27466 | 0.027466 | -0.32959 | 0.56763 | -0.054932 | -0.013733 | 0.21973 | 0.26093 | 122.5845 | -0.009155 | -0.19226 | 122.7631 | 122.818 | 122.6669 | 0.23346 | 0.082397 | 0.84229 | 122.8409 | 0.17853 | 0.11902 | 123.1979 | 0.30212 | 122.9233 | 122.8867 | -123.1705 | -0.31128 | 122.5662 | 122.7036 | 122.3465 | 122.6257
851.9531 | 123.0331 | -122.6532 | 0.1831 | 0.0034333 | 0.0024012 | 0.069799 | 0.062282 | 0.0013863 | -0.0030015 | -0.00098695 | 0.001648 | 0.033968 | 0.021849 | 0.032201 | -0.0019611 | 0.009519 | 0.0058576 | -0.32044 | 0.16479 | -122.9645 | 0.018311 | -121.9391 | -122.5433 | -122.6028 | 0.13275 | 0.17395 | -0.073242 | 0.13733 | 0.22888 | 0.1236 | 0.23346 | -0.31128 | -0.01831 | -0.16479 | 0.71411 | 0.050354 | 0.10986 | 0.36163 | 0.42114 | 122.58 | -0.009155 | -0.045776 | 122.8821 | 122.8867 | 122.7768 | 0.3067 | 0.19684 | 1.0254 | 122.9828 | 0.30212 | 0.21057 | 123.1293 | 0.24719 | 122.818 | 122.8271 | -123.1476 | -0.25635 | 122.6715 | 122.7905 | 122.3328 | 122.7859
853.7031 | 122.9599 | -122.6852 | 0.1831 | 0.011063 | 0.0024012 | 0.069799 | 0.066768 | 0.0039499 | -0.0010789 | 0.002431 | 0.0077514 | 0.033327 | 0.020995 | 0.03861 | 0.0025251 | 0.0080236 | -0.00097841 | -0.34332 | 0.20599 | -122.9553 | -0.009155 | -121.994 | -122.6212 | -122.6578 | 0.07782 | 0.17853 | -0.073242 | 0.082397 | 0.16479 | 0.073242 | 0.19684 | -0.27008 | 0.022889 | -0.19226 | 0.69122 | 0.027466 | 0.064087 | 0.29755 | 0.33417 | 122.612 | -0.004577 | -0.10071 | 122.85 | 122.8821 | 122.7585 | 0.27008 | 0.14648 | 0.9613 | 122.9462 | 0.23804 | 0.15564 | 123.1613 | 0.25177 | 122.8912 | 122.8638 | -123.1384 | -0.25635 | 122.6761 | 122.7676 | 122.3419 | 122.7631
855.4531 | 122.9599 | -122.7036 | 0.15106 | 0.018692 | 0.0049646 | 0.071295 | 0.065486 | 0.0080087 | -0.0010789 | 8.125e-05 | 0.0077514 | 0.037173 | 0.023558 | 0.029424 | -0.00089293 | 0.0093054 | 0.0047894 | -0.33417 | 0.16022 | -122.9645 | 0.018311 | -121.9849 | -122.612 | -122.6624 | 0.086975 | 0.17395 | -0.091553 | 0.10529 | 0.17853 | 0.091553 | 0.21515 | -0.26093 | 0.009155 | -0.13275 | 0.71869 | 0.041198 | 0.091552 | 0.30212 | 0.35248 | 122.612 | 0.022888 | -0.045776 | 122.8821 | 122.9187 | 122.7951 | 0.3067 | 0.18311 | 0.97961 | 122.9828 | 0.27008 | 0.19684 | 123.1247 | 0.2655 | 122.8638 | 122.8775 | -123.1155 | -0.24261 | 122.7219 | 122.8088 | 122.3694 | 122.7905
857.2031 | 122.8729 | -122.699 | 0.21057 | 0.0034333 | 0.0058192 | 0.069799 | 0.067622 | 0.0077951 | -0.0010789 | -0.0018414 | 0.001648 | 0.038241 | 0.021849 | 0.031133 | -0.00089293 | 0.0093054 | 0.00051699 | -0.28839 | 0.20599 | -122.9782 | -0.086975 | -122.0947 | -122.6807 | -122.7493 | -0.022888 | 0.19226 | -0.07782 | 0 | 0.068665 | -0.022888 | 0.1236 | -0.27923 | -0.004577 | -0.29755 | 0.60425 | -0.050354 | 0.018311 | 0.22888 | 0.29755 | 122.6212 | -0.01831 | -0.21057 | 122.7676 | 122.8226 | 122.6761 | 0.20142 | 0.054932 | 0.88348 | 122.8912 | 0.14649 | 0.07782 | 123.1842 | 0.27008 | 122.905 | 122.8912 | -123.1888 | -0.28839 | 122.612 | 122.699 | 122.4106 | 122.6761
858.875 | 122.9553 | -122.6898 | 0.17395 | 0.011063 | 0.004751 | 0.071295 | 0.065913 | 0.0024545 | -0.0023605 | -0.00077335 | 0.001648 | 0.035036 | 0.021849 | 0.028356 | -0.0026019 | 0.0093054 | 0.003294 | -0.37994 | 0.20599 | -122.9736 | -0.054932 | -122.049 | -122.6212 | -122.6761 | 0 | 0.18768 | -0.091553 | 0.054932 | 0.15564 | 0.064087 | 0.19226 | -0.28381 | 0.032044 | -0.22888 | 0.64087 | 0.013733 | 0.068664 | 0.29755 | 0.35248 | 122.5983 | 0.013733 | -0.11902 | 122.8455 | 122.8821 | 122.7539 | 0.28381 | 0.15564 | 0.92468 | 122.9187 | 0.24719 | 0.14649 | 123.1796 | 0.27924 | 122.8958 | 122.8775 | -123.1476 | -0.2655 | 122.6349 | 122.7448 | 122.3099 | 122.6898
860.6094 | 122.9507 | -122.6669 | 0.17853 | 0.011063 | 0.0049646 | 0.071081 | 0.063777 | 0.0039499 | -0.0023605 | 8.125e-05 | 0.001648 | 0.035464 | 0.021422 | 0.024297 | 0.00038887 | 0.006742 | -0.001192 | -0.36163 | 0.19684 | -122.9416 | -0.041199 | -122.0215 | -122.644 | -122.6944 | 0.036621 | 0.1831 | -0.10071 | 0.068665 | 0.14191 | 0.064087 | 0.18768 | -0.27466 | 0.01831 | -0.21973 | 0.64545 | -0.027466 | 0.022888 | 0.24719 | 0.29755 | 122.5662 | 0.004577 | -0.10986 | 122.8088 | 122.8546 | 122.731 | 0.28839 | 0.1648 | 0.9201 | 122.9004 | 0.24262 | 0.16937 | 123.1384 | 0.28381 | 122.8638 | 122.85 | -123.1201 | -0.27924 | 122.6257 | 122.7356 | 122.3053 | 122.7036
862.2969 | 122.8226 | -122.7127 | 0.21973 | 0.011063 | 0.0077418 | 0.070654 | 0.066341 | 0.0028817 | -0.0019333 | 0.00050845 | -0.0014038 | 0.037813 | 0.021209 | 0.021734 | 0.00017507 | 0.009519 | -0.00033761 | -0.33417 | 0.2243 | -122.9919 | -0.11902 | -122.1497 | -122.7356 | -122.7768 | -0.10529 | 0.21057 | -0.10071 | 0.004578 | 0.045776 | -0.041199 | 0.1236 | -0.27923 | 0.004577 | -0.33875 | 0.56305 | -0.064086 | -0.022888 | 0.21515 | 0.25635 | 122.612 | -0.009156 | -0.21515 | 122.7585 | 122.8363 | 122.6715 | 0.2243 | 0.059509 | 0.84229 | 122.8729 | 0.14648 | 0.10529 | 123.2162 | 0.31128 | 122.937 | 122.9233 | -123.2117 | -0.32044 | 122.5937 | 122.7173 | 122.3785 | 122.6074
864.0469 | 123.0331 | -122.6761 | 0.17395 | -0.0041962 | 0.0026148 | 0.068517 | 0.063991 | 0.0037363 | 0.00041651 | 0.00072205 | 0.0046998 | 0.032686 | 0.020354 | 0.029211 | -0.0015337 | 0.0080236 | 0.00094419 | -0.32044 | 0.1831 | -122.9782 | 0.022888 | -121.9299 | -122.5388 | -122.612 | 0.12817 | 0.1831 | -0.064087 | 0.1236 | 0.22888 | 0.13733 | 0.24719 | -0.30212 | 0.009155 | -0.15106 | 0.74615 | 0.064086 | 0.13733 | 0.36621 | 0.43945 | 122.612 | 0.009155 | -0.050354 | 122.905 | 122.9233 | 122.8134 | 0.31128 | 0.20142 | 1.0483 | 123.0011 | 0.29297 | 0.18768 | 123.1613 | 0.24719 | 122.8592 | 122.8592 | -123.1522 | -0.23804 | 122.699 | 122.7997 | 122.3557 | 122.8043
865.7188 | 122.8683 | -122.699 | 0.20599 | 0.0034333 | 0.0062464 | 0.071722 | 0.065273 | 0.0037363 | -0.0017197 | -0.0014142 | 0.001648 | 0.037813 | 0.020995 | 0.027075 | 0.00060247 | 0.0090918 | 0.002226 | -0.35706 | 0.21973 | -123.0057 | -0.11444 | -122.1634 | -122.731 | -122.7539 | -0.07782 | 0.20142 | -0.11444 | 0.013733 | 0.041199 | -0.036621 | 0.13733 | -0.3067 | 0.013733 | -0.32044 | 0.53558 | -0.054931 | -0.032043 | 0.25177 | 0.27466 | 122.5845 | -0.004578 | -0.19226 | 122.7402 | 122.8363 | 122.6624 | 0.25177 | 0.07782 | 0.84228 | 122.8912 | 0.15564 | 0.12817 | 123.2254 | 0.31586 | 122.9187 | 122.9004 | -123.2117 | -0.32044 | 122.5845 | 122.7127 | 122.3419 | 122.6212
867.4688 | 122.8867 | -122.7173 | 0.21057 | -0.0041962 | 0.0041102 | 0.072149 | 0.064204 | 0.0052315 | -0.0021469 | 0.00093565 | -0.0014038 | 0.035036 | 0.021849 | 0.026861 | 0.0031659 | 0.0090918 | 0.0041486 | -0.36621 | 0.21973 | -122.9782 | -0.10986 | -122.1451 | -122.7219 | -122.7539 | -0.050354 | 0.19684 | -0.10986 | 0.018311 | 0.068665 | -0.032043 | 0.14648 | -0.26093 | 0.009156 | -0.32043 | 0.5722 | -0.036621 | -0.004578 | 0.2243 | 0.25635 | 122.6074 | -0.013733 | -0.19226 | 122.7859 | 122.8638 | 122.6852 | 0.25635 | 0.07782 | 0.83313 | 122.8683 | 0.17853 | 0.12817 | 123.1979 | 0.3067 | 122.937 | 122.9141 | -123.1888 | -0.32043 | 122.6074 | 122.7356 | 122.3511 | 122.6669
869.1562 | 122.9965 | -122.6852 | 0.17853 | 0.011063 | 0.0034692 | 0.070867 | 0.06335 | 0.00053194 | -0.0030015 | 0.00029485 | 0.0046998 | 0.033755 | 0.020568 | 0.036474 | -0.0023883 | 0.0086646 | -0.0014056 | -0.30212 | 0.18768 | -122.9691 | 0.022888 | -121.9711 | -122.5616 | -122.6212 | 0.09613 | 0.16022 | -0.073242 | 0.10071 | 0.21515 | 0.1236 | 0.23346 | -0.28381 | 0.009155 | -0.15564 | 0.71411 | 0.064087 | 0.1236 | 0.3479 | 0.40741 | 122.612 | -0.018311 | -0.07782 | 122.9004 | 122.9187 | 122.8088 | 0.3067 | 0.19684 | 0.99792 | 122.9919 | 0.28839 | 0.17395 | 123.1567 | 0.23346 | 122.8729 | 122.8455 | -123.1476 | -0.25177 | 122.7081 | 122.7859 | 122.3831 | 122.7814
870.8906 | 122.9691 | -122.6761 | 0.20599 | 0.011063 | 0.0060328 | 0.071295 | 0.065486 | 0.0028817 | -0.0010789 | -0.0035504 | 0.0077514 | 0.034395 | 0.019072 | 0.032842 | -3.8532e-05 | 0.0082374 | 0.0013714 | -0.37994 | 0.17853 | -122.9691 | -0.050354 | -122.049 | -122.6395 | -122.6669 | 0.018311 | 0.17395 | -0.086975 | 0.07782 | 0.16479 | 0.07782 | 0.20142 | -0.29297 | -0.027466 | -0.25635 | 0.62714 | 0.009155 | 0.036621 | 0.30212 | 0.32959 | 122.5891 | -0.032044 | -0.12817 | 122.8409 | 122.8775 | 122.7539 | 0.28839 | 0.16479 | 0.9201 | 122.9187 | 0.25177 | 0.16479 | 123.1476 | 0.26092 | 122.8546 | 122.85 | -123.175 | -0.29297 | 122.6257 | 122.7539 | 122.2961 | 122.6944
872.6406 | 122.8592 | -122.7264 | 0.18768 | 0.018692 | 0.0045374 | 0.07044 | 0.066982 | 0.0041635 | -0.0023605 | 0.003499 | -0.0014038 | 0.038027 | 0.022704 | 0.032201 | -0.00025213 | 0.011014 | 0.0011578 | -0.35248 | 0.21973 | -122.9874 | -0.12817 | -122.1634 | -122.7402 | -122.7722 | -0.07782 | 0.21973 | -0.091553 | 0.004578 | 0.050354 | -0.050354 | 0.12817 | -0.26093 | 0.032044 | -0.31586 | 0.56305 | -0.045777 | -0.013733 | 0.21515 | 0.24719 | 122.6349 | 0.032044 | -0.1831 | 122.7768 | 122.8546 | 122.6761 | 0.21973 | 0.041199 | 0.82397 | 122.8592 | 0.14191 | 0.096131 | 123.2071 | 0.31128 | 122.9462 | 122.9462 | -123.175 | -0.27924 | 122.5983 | 122.731 | 122.374 | 122.6486
874.3125 | 122.8867 | -122.7173 | 0.21973 | 0.0034333 | 0.0034692 | 0.069158 | 0.065486 | 0.0041635 | -0.0049241 | -0.0018414 | -0.0014038 | 0.036745 | 0.020781 | 0.028784 | -0.0047381 | 0.0075964 | 0.0028668 | -0.32959 | 0.21057 | -122.9782 | -0.10071 | -122.0901 | -122.6578 | -122.731 | -0.059509 | 0.20599 | -0.091553 | -0.009155 | 0.086975 | 0 | 0.11902 | -0.26093 | -0.009156 | -0.32044 | 0.62714 | -0.013733 | 0.059509 | 0.24719 | 0.32043 | 122.6257 | -0.013733 | -0.22888 | 122.8043 | 122.8363 | 122.7173 | 0.21057 | 0.091553 | 0.88806 | 122.8775 | 0.17853 | 0.082398 | 123.1888 | 0.29755 | 122.9279 | 122.9233 | -123.1979 | -0.31128 | 122.6166 | 122.7081 | 122.3877 | 122.6578
876.0625 | 122.8821 | -122.7081 | 0.19226 | 0.0034333 | 0.00646 | 0.07279 | 0.067409 | 0.0054453 | -0.0021469 | 0.0022174 | -0.0014038 | 0.038027 | 0.022277 | 0.024511 | -0.0017475 | 0.0099462 | -0.0035418 | -0.30212 | 0.21515 | -122.9782 | -0.09613 | -122.0901 | -122.6944 | -122.7539 | -0.032043 | 0.20599 | -0.10529 | 0.013733 | 0.068665 | -0.027466 | 0.1236 | -0.27008 | 0.022888 | -0.28839 | 0.61798 | -0.045776 | 0.013733 | 0.2243 | 0.28381 | 122.6028 | 0.013733 | -0.17853 | 122.7768 | 122.8317 | 122.6807 | 0.22888 | 0.07782 | 0.88806 | 122.8821 | 0.17395 | 0.11902 | 123.1934 | 0.31128 | 122.9233 | 122.9141 | -123.1705 | -0.29755 | 122.612 | 122.7219 | 122.406 | 122.6761
877.75 | 122.8683 | -122.7127 | 0.21057 | 0.018692 | 0.0051782 | 0.068517 | 0.065486 | 0.0043771 | -0.0047103 | 0.0011492 | 0.0077514 | 0.036745 | 0.019713 | 0.027929 | -0.0036701 | 0.010374 | 0.00073059 | -0.33875 | 0.23346 | -123.0103 | -0.1236 | -122.0993 | -122.6532 | -122.7264 | -0.064087 | 0.21973 | -0.1236 | -0.013733 | 0.086975 | -0.018311 | 0.11444 | -0.29755 | 0.022888 | -0.33417 | 0.6134 | -0.013732 | 0.05951 | 0.28381 | 0.35706 | 122.5891 | 0.009156 | -0.2243 | 122.7997 | 122.8271 | 122.6944 | 0.23804 | 0.10528 | 0.91095 | 122.8867 | 0.21057 | 0.10986 | 123.2437 | 0.34332 | 122.9462 | 122.9324 | -123.2208 | -0.33417 | 122.5891 | 122.699 | 122.374 | 122.6486
879.5 | 122.9828 | -122.6486 | 0.16937 | 0.026321 | 0.0053918 | 0.071935 | 0.064418 | 0.0050179 | -0.0012925 | -0.0022688 | 0.0077514 | 0.034823 | 0.021849 | 0.033483 | 0.0014569 | 0.0080236 | -0.0022602 | -0.32044 | 0.1831 | -122.9233 | 0.018311 | -121.962 | -122.5845 | -122.6349 | 0.10986 | 0.15564 | -0.10071 | 0.13275 | 0.19684 | 0.10986 | 0.23346 | -0.27466 | 0.013732 | -0.15106 | 0.68665 | 0.013733 | 0.064087 | 0.28839 | 0.33874 | 122.5479 | -0.013733 | -0.036622 | 122.8455 | 122.8821 | 122.7585 | 0.33417 | 0.21057 | 0.9613 | 122.9416 | 0.29755 | 0.23346 | 123.1064 | 0.25635 | 122.8317 | 122.8043 | -123.0927 | -0.27008 | 122.6669 | 122.7814 | 122.3282 | 122.7585
881.25 | 122.937 | -122.6807 | 0.16479 | 0.011063 | 0.0049646 | 0.069586 | 0.064845 | 0.0065133 | -0.0017197 | 0.00029485 | 0.001648 | 0.034182 | 0.019072 | 0.034979 | 0.00038887 | 0.01016 | 0.0026532 | -0.3479 | 0.1831 | -122.9507 | 0.004578 | -121.9986 | -122.6303 | -122.6486 | 0.082397 | 0.17395 | -0.073242 | 0.09613 | 0.16022 | 0.064087 | 0.20142 | -0.27008 | 0.01831 | -0.16022 | 0.68207 | 0.032043 | 0.050354 | 0.30212 | 0.32044 | 122.6074 | 0.009155 | -0.068665 | 122.8409 | 122.8821 | 122.7448 | 0.27466 | 0.13733 | 0.95215 | 122.9553 | 0.23346 | 0.16937 | 123.1338 | 0.24719 | 122.8638 | 122.8546 | -123.1155 | -0.23804 | 122.6852 | 122.7768 | 122.3328 | 122.7631
883 | 122.8867 | -122.7127 | 0.20599 | 0.018692 | 0.0043238 | 0.070226 | 0.064845 | 0.00074554 | -0.0032151 | 0.0015764 | 0.0077514 | 0.036959 | 0.018859 | 0.02622 | -3.8532e-05 | 0.00781 | -0.00076481 | -0.29755 | 0.20599 | -123.0148 | -0.086975 | -122.0764 | -122.6395 | -122.6852 | -0.036621 | 0.21973 | -0.10071 | 0.027466 | 0.10529 | 0.009155 | 0.16022 | -0.30212 | 0 | -0.29297 | 0.63629 | 0.027466 | 0.073243 | 0.32959 | 0.37537 | 122.612 | 0.013733 | -0.17853 | 122.818 | 122.8729 | 122.7219 | 0.26093 | 0.10986 | 0.93842 | 122.9279 | 0.20599 | 0.12817 | 123.2208 | 0.32044 | 122.9187 | 122.9324 | -123.2208 | -0.3067 | 122.6257 | 122.7402 | 122.4152 | 122.6761
884.6719 | 122.85 | -122.7264 | 0.20599 | -0.0041962 | 0.0051782 | 0.072149 | 0.065913 | 0.0039499 | -0.0015061 | 0.0011492 | 0.0046998 | 0.037386 | 0.021209 | 0.02622 | 0.00060247 | 0.0097326 | -0.001192 | -0.32501 | 0.21057 | -122.9874 | -0.10986 | -122.1222 | -122.7127 | -122.7585 | -0.082397 | 0.19684 | -0.10071 | -0.013733 | 0.050354 | -0.050354 | 0.11902 | -0.26093 | 0.004577 | -0.31586 | 0.60425 | -0.032044 | 0.013732 | 0.22888 | 0.27466 | 122.6257 | -0.009156 | -0.21973 | 122.7768 | 122.8455 | 122.6761 | 0.21973 | 0.050354 | 0.86517 | 122.8775 | 0.15106 | 0.086975 | 123.1979 | 0.29755 | 122.937 | 122.9233 | -123.1934 | -0.3067 | 122.6166 | 122.7127 | 122.4014 | 122.644
886.4219 | 122.9599 | -122.6715 | 0.17395 | 0.026321 | 0.0043238 | 0.069372 | 0.063564 | 0.0035227 | -0.0017197 | 0.0011492 | -0.0014038 | 0.033541 | 0.021849 | 0.025579 | -0.00067933 | 0.0088782 | 8.9786e-05 | -0.37994 | 0.19684 | -122.9782 | -0.036621 | -122.0123 | -122.612 | -122.6624 | 0.027466 | 0.1831 | -0.086975 | 0.073242 | 0.13275 | 0.068665 | 0.18768 | -0.3067 | 0.022888 | -0.21057 | 0.65918 | 0.009155 | 0.059509 | 0.31586 | 0.36621 | 122.5845 | 0.009155 | -0.10071 | 122.8043 | 122.8592 | 122.7402 | 0.27466 | 0.15564 | 0.96588 | 122.9416 | 0.21973 | 0.16022 | 123.175 | 0.27008 | 122.8683 | 122.8546 | -123.1522 | -0.26092 | 122.6349 | 122.7448 | 122.2916 | 122.699
888.1719 | 122.905 | -122.7081 | 0.18768 | 0.018692 | 0.0094508 | 0.072576 | 0.064204 | 0.0033089 | -0.00065149 | 0.00093565 | 0.0046998 | 0.035891 | 0.02014 | 0.026006 | -0.00025213 | 0.0099462 | 0.0020124 | -0.28381 | 0.21515 | -123.0011 | -0.041199 | -122.0444 | -122.6349 | -122.699 | 0.009155 | 0.17853 | -0.091553 | 0.050354 | 0.10986 | 0.022888 | 0.16022 | -0.29297 | 0.027466 | -0.22888 | 0.66376 | 0.009155 | 0.073242 | 0.30212 | 0.36621 | 122.6166 | -0.009155 | -0.13733 | 122.818 | 122.8683 | 122.731 | 0.25177 | 0.11444 | 0.95673 | 122.9599 | 0.20142 | 0.14191 | 123.2162 | 0.27008 | 122.9233 | 122.8867 | -123.1888 | -0.27924 | 122.6669 | 122.7585 | 122.4243 | 122.7173
889.9062 | 123.0011 | -122.6532 | 0.17395 | 0.0034333 | 0.0045374 | 0.069372 | 0.064204 | 0.0028817 | -0.0025741 | -0.0012006 | -0.0044556 | 0.036318 | 0.019286 | 0.035619 | 0.0020979 | 0.01016 | 8.9786e-05 | -0.33417 | 0.1831 | -122.9553 | -0.022888 | -121.9894 | -122.5983 | -122.644 | 0.091553 | 0.16479 | -0.068665 | 0.13733 | 0.18768 | 0.10071 | 0.24261 | -0.30212 | 0.009155 | -0.19684 | 0.66376 | 0.009155 | 0.054931 | 0.31128 | 0.35705 | 122.5845 | -0.009155 | -0.036621 | 122.8409 | 122.8958 | 122.7539 | 0.31128 | 0.16937 | 0.96588 | 122.9324 | 0.25635 | 0.20599 | 123.1384 | 0.23346 | 122.8363 | 122.818 | -123.1293 | -0.24261 | 122.6303 | 122.7905 | 122.319 | 122.7448
891.5938 | 122.9095 | -122.7081 | 0.20142 | 0.011063 | 0.0056054 | 0.071935 | 0.069545 | 0.0060861 | -0.0034287 | 0.00029485 | 0.0046998 | 0.035036 | 0.020995 | 0.023229 | -3.8532e-05 | 0.0080236 | -0.001192 | -0.2655 | 0.21515 | -122.9645 | -0.054932 | -122.0306 | -122.6303 | -122.6898 | 0.036621 | 0.19684 | -0.09613 | 0.068665 | 0.13733 | 0.036621 | 0.17853 | -0.25635 | 0.013733 | -0.25635 | 0.67749 | 0.018311 | 0.07782 | 0.27466 | 0.33417 | 122.612 | -0.004578 | -0.13275 | 122.8455 | 122.8867 | 122.7448 | 0.27466 | 0.13275 | 0.93384 | 122.9095 | 0.23346 | 0.16479 | 123.1796 | 0.29297 | 122.9233 | 122.905 | -123.1659 | -0.29755 | 122.6532 | 122.7768 | 122.4426 | 122.7448
893.3594 | 122.9462 | -122.6852 | 0.16479 | 0.0034333 | 0.004751 | 0.069158 | 0.064845 | -0.00096346 | -0.0010789 | -0.0012006 | 0.001648 | 0.034395 | 0.019713 | 0.030279 | -0.00089293 | 0.011014 | 0.0035078 | -0.29755 | 0.16479 | -122.9416 | -0.004578 | -121.9711 | -122.5662 | -122.6349 | 0.068665 | 0.16479 | -0.068665 | 0.10529 | 0.20599 | 0.11902 | 0.20599 | -0.25635 | 0 | -0.16937 | 0.71411 | 0.050354 | 0.11902 | 0.3067 | 0.37537 | 122.6166 | 0 | -0.059509 | 122.8912 | 122.8912 | 122.8043 | 0.27466 | 0.18768 | 0.97046 | 122.937 | 0.27466 | 0.17395 | 123.1064 | 0.23346 | 122.85 | 122.85 | -123.1064 | -0.23346 | 122.6807 | 122.7905 | 122.3877 | 122.7539
895.0312 | 122.8958 | -122.7127 | 0.19226 | 0.026321 | 0.0051782 | 0.069799 | 0.065059 | 0.0071541 | -0.0025741 | -0.0014142 | 0.0077514 | 0.03525 | 0.020995 | 0.028356 | 0.00017507 | 0.00781 | 0.00073059 | -0.30212 | 0.2243 | -123.0148 | -0.10986 | -122.0856 | -122.6303 | -122.6944 | -0.045776 | 0.20142 | -0.1236 | 0.027466 | 0.11444 | 0.013733 | 0.15564 | -0.30212 | 0.032043 | -0.30212 | 0.62714 | 0.018311 | 0.082398 | 0.32044 | 0.38452 | 122.5891 | 0.009155 | -0.16479 | 122.8271 | 122.8683 | 122.7264 | 0.27924 | 0.13733 | 0.92926 | 122.905 | 0.23804 | 0.15106 | 123.2391 | 0.32501 | 122.937 | 122.9141 | -123.2071 | -0.31586 | 122.6028 | 122.7402 | 122.4106 | 122.6669
896.7656 | 122.9004 | -122.699 | 0.20142 | 0.011063 | 0.0073144 | 0.070867 | 0.066554 | 0.0077951 | -0.0025741 | 0.0020038 | 0.0046998 | 0.036104 | 0.0195 | 0.024084 | -0.0017475 | 0.0099462 | -0.0037554 | -0.29297 | 0.21057 | -122.9965 | -0.068665 | -122.0444 | -122.6349 | -122.6807 | 0.013733 | 0.19684 | -0.086975 | 0.050354 | 0.13733 | 0.022888 | 0.15106 | -0.29755 | 0.009155 | -0.27008 | 0.6546 | 0.018311 | 0.064087 | 0.31586 | 0.36163 | 122.612 | -0.004578 | -0.15106 | 122.8363 | 122.85 | 122.7219 | 0.23804 | 0.10986 | 0.95215 | 122.9279 | 0.2243 | 0.13733 | 123.2071 | 0.28381 | 122.9095 | 122.8958 | -123.1979 | -0.28839 | 122.6303 | 122.7493 | 122.406 | 122.7127
898.5156 | 122.9416 | -122.6761 | 0.17395 | 0.0034333 | 0.0041102 | 0.07279 | 0.062282 | 0.0028817 | -0.0012925 | -0.0012006 | 0.001648 | 0.033755 | 0.021849 | 0.035833 | -0.0015337 | 0.011014 | 0.0028668 | -0.40283 | 0.19226 | -122.9507 | -0.050354 | -122.0535 | -122.6212 | -122.6715 | 0.009155 | 0.1831 | -0.091553 | 0.050354 | 0.14191 | 0.054932 | 0.19684 | -0.27466 | 0.018311 | -0.2243 | 0.62256 | 0.004577 | 0.054931 | 0.27924 | 0.32959 | 122.5845 | 0.009155 | -0.1236 | 122.818 | 122.8729 | 122.731 | 0.28839 | 0.14649 | 0.89722 | 122.9004 | 0.23346 | 0.14191 | 123.143 | 0.27466 | 122.8683 | 122.8592 | -123.1247 | -0.2655 | 122.6257 | 122.7264 | 122.2733 | 122.6852
900.2656 | 122.9599 | -122.6761 | 0.16937 | 0.018692 | 0.004751 | 0.07279 | 0.06335 | 0.0026681 | -0.0019333 | -0.00013235 | 0.001648 | 0.036532 | 0.021209 | 0.030279 | 0.0029523 | 0.0090918 | 0.0026532 | -0.33875 | 0.17853 | -122.9599 | 0.004578 | -121.9666 | -122.5891 | -122.6212 | 0.10071 | 0.16022 | -0.082397 | 0.1236 | 0.16937 | 0.082397 | 0.2243 | -0.28381 | 0.009155 | -0.16479 | 0.70953 | 0.054931 | 0.086975 | 0.33875 | 0.37079 | 122.5937 | -0.009156 | -0.045777 | 122.8455 | 122.9004 | 122.7585 | 0.3067 | 0.16479 | 0.99335 | 122.9645 | 0.25177 | 0.20599 | 123.1384 | 0.24261 | 122.8546 | 122.8363 | -123.1293 | -0.25177 | 122.6807 | 122.7997 | 122.3373 | 122.7768
902.0156 | 122.8683 | -122.7356 | 0.2243 | 0.011063 | 0.003042 | 0.068517 | 0.065273 | 0.0030953 | -0.0047103 | -0.00098695 | 0.001648 | 0.036959 | 0.020568 | 0.026647 | -0.0043109 | 0.00781 | -0.001192 | -0.3479 | 0.19684 | -122.9645 | -0.11444 | -122.1039 | -122.6532 | -122.7081 | -0.068665 | 0.18768 | -0.11902 | -0.018311 | 0.082397 | -0.009155 | 0.10986 | -0.22888 | -0.027466 | -0.33875 | 0.63171 | 0.027466 | 0.082398 | 0.25635 | 0.31128 | 122.6166 | -0.036621 | -0.24261 | 122.818 | 122.8455 | 122.7264 | 0.22888 | 0.10986 | 0.8606 | 122.85 | 0.20142 | 0.10071 | 123.1613 | 0.3067 | 122.9324 | 122.9233 | -123.1888 | -0.34332 | 122.6212 | 122.7173 | 122.3877 | 122.6669
903.7656 | 123.0148 | -122.6624 | 0.16937 | 0.018692 | 0.0045374 | 0.071722 | 0.065059 | 0.0035227 | -0.00022429 | 0.00029485 | 0.0046998 | 0.035677 | 0.022704 | 0.03092 | 0.0025251 | 0.011442 | -0.00012381 | -0.31128 | 0.17395 | -122.9279 | 0.018311 | -121.9711 | -122.58 | -122.6303 | 0.10986 | 0.15564 | -0.073242 | 0.11902 | 0.21057 | 0.086975 | 0.22888 | -0.2655 | 0.004577 | -0.15106 | 0.69122 | 0.032044 | 0.082398 | 0.29755 | 0.3479 | 122.5891 | -0.013733 | -0.050354 | 122.8729 | 122.8912 | 122.7493 | 0.30212 | 0.16022 | 0.95673 | 122.9462 | 0.28381 | 0.19226 | 123.1018 | 0.22888 | 122.8363 | 122.818 | -123.0972 | -0.24261 | 122.6807 | 122.7814 | 122.3511 | 122.7722
905.4531 | 122.8592 | -122.731 | 0.21973 | 0.018692 | 0.0062464 | 0.070013 | 0.064632 | -0.00032266 | -0.0036423 | 0.00072205 | 0.001648 | 0.036532 | 0.021849 | 0.02152 | -0.0023883 | 0.0069556 | -0.00461 | -0.35248 | 0.2243 | -122.9828 | -0.1236 | -122.0947 | -122.6669 | -122.7173 | -0.050354 | 0.21057 | -0.1236 | -0.022888 | 0.064087 | -0.013733 | 0.10986 | -0.25177 | 0.004577 | -0.34332 | 0.63629 | 0.013733 | 0.064087 | 0.2655 | 0.31586 | 122.6074 | -0.009156 | -0.24261 | 122.7951 | 122.8409 | 122.7173 | 0.23346 | 0.10986 | 0.88806 | 122.8592 | 0.18768 | 0.10071 | 123.2071 | 0.33417 | 122.9553 | 122.9416 | -123.2025 | -0.34332 | 122.6074 | 122.7081 | 122.3785 | 122.6807
907.2031 | 122.8592 | -122.7264 | 0.20599 | 0.0034333 | 0.0058192 | 0.071295 | 0.0657 | 0.0018137 | -0.0017197 | -0.0018414 | 0.010803 | 0.037386 | 0.021849 | 0.02152 | -0.0015337 | 0.005033 | -0.0026874 | -0.35706 | 0.20599 | -122.9874 | -0.11444 | -122.0901 | -122.6486 | -122.6944 | -0.059509 | 0.21515 | -0.12817 | -0.022888 | 0.073242 | -0.009155 | 0.11902 | -0.26093 | 0 | -0.32044 | 0.63629 | 0.032043 | 0.077819 | 0.29297 | 0.33874 | 122.5983 | 0.009155 | -0.22888 | 122.7997 | 122.8455 | 122.7173 | 0.24719 | 0.11902 | 0.89722 | 122.8729 | 0.20142 | 0.10529 | 123.1934 | 0.34332 | 122.9324 | 122.9416 | -123.1934 | -0.33417 | 122.612 | 122.7036 | 122.3694 | 122.6669
908.9531 | 122.9736 | -122.6852 | 0.1831 | 0.018692 | 0.00047857 | 0.070013 | 0.067195 | 0.00095914 | -0.0034287 | -0.0014142 | 0.0077514 | 0.034823 | 0.021636 | 0.031561 | 0.00017507 | 0.0093054 | 0.00094419 | -0.3891 | 0.19684 | -122.9736 | -0.054932 | -122.0306 | -122.6166 | -122.644 | 0.013733 | 0.1831 | -0.091553 | 0.073242 | 0.1831 | 0.091553 | 0.19684 | -0.28839 | 0.013733 | -0.23804 | 0.6546 | 0.041199 | 0.068665 | 0.32959 | 0.35706 | 122.5937 | 0 | -0.10986 | 122.8683 | 122.8821 | 122.7768 | 0.28839 | 0.18311 | 0.94299 | 122.9187 | 0.27466 | 0.16479 | 123.1705 | 0.27466 | 122.8821 | 122.8683 | -123.1567 | -0.27466 | 122.6303 | 122.7585 | 122.2961 | 122.699
910.625 | 122.9874 | -122.6807 | 0.18768 | 0.0034333 | 0.0036828 | 0.070226 | 0.063991 | -0.00053626 | -0.0040695 | -0.00055975 | 0.0046998 | 0.034823 | 0.019286 | 0.031988 | -0.00067933 | 0.0082374 | 0.00051699 | -0.29297 | 0.15106 | -122.9691 | 0.027466 | -121.9528 | -122.5342 | -122.612 | 0.09613 | 0.17395 | -0.086975 | 0.11444 | 0.21973 | 0.1236 | 0.21515 | -0.28839 | -0.036621 | -0.16022 | 0.72784 | 0.068664 | 0.14648 | 0.35706 | 0.43487 | 122.5937 | -0.013733 | -0.073242 | 122.9004 | 122.8958 | 122.8043 | 0.30212 | 0.21057 | 1.0162 | 122.9965 | 0.3067 | 0.20142 | 123.1201 | 0.26092 | 122.8317 | 122.8546 | -123.1567 | -0.27466 | 122.7081 | 122.7951 | 122.3877 | 122.7768
912.3594 | 122.8638 | -122.7219 | 0.17853 | 0.011063 | 0.0032556 | 0.067663 | 0.065273 | 0.0020273 | -0.0034287 | -0.0012006 | 0.010803 | 0.0376 | 0.021636 | 0.027715 | -0.0030291 | 0.0082374 | 0.0037214 | -0.36163 | 0.22888 | -123.0011 | -0.11444 | -122.0901 | -122.6486 | -122.7081 | -0.054932 | 0.21973 | -0.1236 | -0.013733 | 0.068665 | -0.013733 | 0.10986 | -0.27924 | 0.050354 | -0.29297 | 0.63171 | 0.013733 | 0.073242 | 0.29297 | 0.35248 | 122.5983 | 0.041199 | -0.19226 | 122.7905 | 122.8317 | 122.7081 | 0.23346 | 0.10986 | 0.91095 | 122.8867 | 0.19226 | 0.10986 | 123.23 | 0.34332 | 122.9507 | 122.9416 | -123.1796 | -0.30212 | 122.6074 | 122.7081 | 122.3602 | 122.6669
914.0938 | 122.85 | -122.7081 | 0.20599 | 0.018692 | 0.0073144 | 0.067877 | 0.064204 | 0.0054453 | -0.0040695 | -0.00098695 | -0.0014038 | 0.036959 | 0.021849 | 0.021734 | -0.0053789 | 0.009519 | 0.005003 | -0.37537 | 0.20142 | -122.9828 | -0.10529 | -122.0856 | -122.6624 | -122.7081 | -0.068665 | 0.21515 | -0.10529 | -0.018311 | 0.073242 | -0.027466 | 0.10529 | -0.27466 | -0.004578 | -0.31128 | 0.62256 | 0 | 0.045776 | 0.27466 | 0.32043 | 122.6028 | 0.009155 | -0.22431 | 122.7814 | 122.8134 | 122.6807 | 0.21057 | 0.07782 | 0.89722 | 122.8775 | 0.17853 | 0.086975 | 123.1842 | 0.32044 | 122.9095 | 122.9233 | -123.1888 | -0.31128 | 122.6028 | 122.6898 | 122.3328 | 122.6395
915.7656 | 122.85 | -122.7173 | 0.19684 | -0.0041962 | 0.0066736 | 0.071722 | 0.066127 | 0.0033089 | -0.0021469 | -0.0031232 | -0.0014038 | 0.036745 | 0.019927 | 0.024297 | 0.00038887 | 0.010801 | 0.003935 | -0.36621 | 0.21057 | -122.9507 | -0.13275 | -122.1588 | -122.7127 | -122.7631 | -0.11444 | 0.21057 | -0.1236 | 0.009155 | 0.059509 | -0.050354 | 0.13275 | -0.23346 | 0.013733 | -0.32959 | 0.55847 | -0.045777 | 0.004577 | 0.18768 | 0.23804 | 122.5937 | 0.013733 | -0.18768 | 122.7768 | 122.85 | 122.6669 | 0.25635 | 0.073242 | 0.79193 | 122.818 | 0.1831 | 0.13275 | 123.1613 | 0.33417 | 122.9279 | 122.9279 | -123.1476 | -0.32043 | 122.5845 | 122.7264 | 122.3511 | 122.6028
917.5 | 122.8455 | -122.6944 | 0.20142 | 0.0034333 | 0.0053918 | 0.071081 | 0.066554 | 0.0062997 | -0.0019333 | 0.00072205 | 0.0046998 | 0.038882 | 0.019927 | 0.028784 | 0.0010297 | 0.009519 | 0.002226 | -0.34332 | 0.21973 | -122.9599 | -0.1236 | -122.1085 | -122.7127 | -122.7493 | -0.086975 | 0.19684 | -0.11902 | 0 | 0.050354 | -0.045776 | 0.09613 | -0.2655 | 0.018311 | -0.32501 | 0.58594 | -0.054932 | -0.018311 | 0.21057 | 0.24719 | 122.5754 | -0.004578 | -0.20142 | 122.7448 | 122.7905 | 122.6486 | 0.21515 | 0.073243 | 0.85144 | 122.8363 | 0.16937 | 0.11902 | 123.1796 | 0.31586 | 122.9141 | 122.8912 | -123.1613 | -0.32044 | 122.5708 | 122.6944 | 122.3511 | 122.6074
919.25 | 122.9645 | -122.6715 | 0.17853 | 0.0034333 | 0.0045374 | 0.070654 | 0.059932 | 0.0048043 | -0.0015061 | -0.00034615 | 0.001648 | 0.033968 | 0.020995 | 0.034979 | 0.00017507 | 0.00781 | -0.00076481 | -0.32044 | 0.18768 | -122.9279 | 0 | -121.9482 | -122.5479 | -122.6028 | 0.07782 | 0.14648 | -0.07782 | 0.11902 | 0.21973 | 0.1236 | 0.21515 | -0.25635 | 0.009155 | -0.17853 | 0.72327 | 0.068665 | 0.1236 | 0.32501 | 0.37994 | 122.5937 | -0.032044 | -0.059509 | 122.8912 | 122.8867 | 122.7951 | 0.29297 | 0.20142 | 0.97961 | 122.9279 | 0.29755 | 0.19684 | 123.1155 | 0.2243 | 122.8592 | 122.818 | -123.1064 | -0.25635 | 122.6715 | 122.7905 | 122.3511 | 122.7493
921 | 122.8546 | -122.7036 | 0.17853 | 0.026321 | 0.0049646 | 0.071295 | 0.066341 | 0.0020273 | -0.0012925 | 8.125e-05 | 0.001648 | 0.036745 | 0.021209 | 0.029638 | 0.0029523 | 0.0086646 | -0.001192 | -0.36621 | 0.21515 | -122.9645 | -0.14191 | -122.1405 | -122.7264 | -122.7676 | -0.10986 | 0.2243 | -0.1236 | 0.009155 | 0.045776 | -0.050354 | 0.1236 | -0.26093 | 0.036621 | -0.32044 | 0.56305 | -0.064087 | -0.022888 | 0.19684 | 0.23804 | 122.58 | 0.045776 | -0.16937 | 122.7493 | 122.8271 | 122.6532 | 0.24719 | 0.073242 | 0.82398 | 122.8226 | 0.16937 | 0.13275 | 123.1796 | 0.3479 | 122.9187 | 122.9279 | -123.143 | -0.30212 | 122.5616 | 122.7127 | 122.3373 | 122.5937
922.6719 | 122.8317 | -122.6669 | 0.19226 | 0.0034333 | 0.0077418 | 0.071081 | 0.064845 | 0.0048043 | -0.0012925 | 0.00093565 | -0.0014038 | 0.035464 | 0.020568 | 0.02857 | -0.0015337 | 0.0086646 | 0.0017988 | -0.35706 | 0.19684 | -122.9691 | -0.10986 | -122.081 | -122.6944 | -122.7356 | -0.068665 | 0.21057 | -0.10529 | 0.009155 | 0.059509 | -0.054932 | 0.1236 | -0.30212 | 0.004577 | -0.30212 | 0.58594 | -0.068665 | -0.027466 | 0.23346 | 0.27466 | 122.5616 | 0.01831 | -0.18311 | 122.7264 | 122.7905 | 122.612 | 0.22888 | 0.050354 | 0.88806 | 122.8592 | 0.16479 | 0.11444 | 123.1659 | 0.31586 | 122.8638 | 122.8775 | -123.1613 | -0.29755 | 122.5571 | 122.6761 | 122.3099 | 122.5983
924.4375 | 122.9279 | -122.6807 | 0.15564 | 0.026321 | 0.004751 | 0.070867 | 0.06335 | 0.0041635 | -0.0015061 | 0.0015764 | 0.0077514 | 0.034395 | 0.021209 | 0.032415 | 0.00017507 | 0.0093054 | -0.0014056 | -0.39368 | 0.19226 | -122.9187 | -0.027466 | -121.9894 | -122.612 | -122.6395 | 0.050354 | 0.1831 | -0.091553 | 0.07782 | 0.15564 | 0.064087 | 0.18768 | -0.23804 | 0.036621 | -0.18311 | 0.69122 | 0.041199 | 0.068664 | 0.27924 | 0.3067 | 122.5891 | 0.027465 | -0.07782 | 122.8363 | 122.8683 | 122.7448 | 0.27924 | 0.15564 | 0.92926 | 122.8912 | 0.24719 | 0.16937 | 123.111 | 0.27466 | 122.8729 | 122.8638 | -123.0743 | -0.24719 | 122.6532 | 122.7585 | 122.287 | 122.731
926.125 | 122.937 | -122.6944 | 0.17395 | 0.018692 | 0.0045374 | 0.070013 | 0.064632 | -0.00010886 | 0.0010575 | -0.0029096 | 0.001648 | 0.034395 | 0.020995 | 0.028143 | -3.8532e-05 | 0.0086646 | -0.0020464 | -0.39368 | 0.19684 | -122.9324 | -0.073242 | -122.0306 | -122.6303 | -122.6578 | -0.004578 | 0.17853 | -0.086975 | 0.064087 | 0.14648 | 0.054932 | 0.17853 | -0.23804 | 0.022888 | -0.24719 | 0.66376 | 0.036621 | 0.064087 | 0.27466 | 0.30212 | 122.6074 | 0.004578 | -0.10986 | 122.8409 | 122.8729 | 122.7493 | 0.2655 | 0.14191 | 0.90179 | 122.8592 | 0.23346 | 0.15106 | 123.1293 | 0.2655 | 122.8912 | 122.8729 | -123.1064 | -0.26092 | 122.6212 | 122.7585 | 122.3007 | 122.6898
927.8594 | 122.8546 | -122.7081 | 0.21057 | 0.011063 | 0.0056054 | 0.069372 | 0.065059 | 0.0045907 | -0.0015061 | 0.002431 | 0.0046998 | 0.039095 | 0.021209 | 0.027288 | -0.0023883 | 0.0075964 | 0.00051699 | -0.33417 | 0.2243 | -123.0194 | -0.10986 | -122.0947 | -122.644 | -122.7036 | -0.064087 | 0.21973 | -0.13275 | 0 | 0.073242 | -0.009155 | 0.1236 | -0.31128 | 0.013733 | -0.32043 | 0.6134 | 0.004578 | 0.064087 | 0.31586 | 0.37537 | 122.5754 | 0.009156 | -0.21057 | 122.7814 | 122.8317 | 122.699 | 0.25635 | 0.1236 | 0.92468 | 122.9095 | 0.20599 | 0.13275 | 123.2437 | 0.35248 | 122.9324 | 122.9279 | -123.23 | -0.34332 | 122.5983 | 122.7081 | 122.374 | 122.644
929.6094 | 122.9553 | -122.612 | 0.17395 | 0.011063 | 0.0051782 | 0.071295 | 0.066554 | 0.0058725 | -0.0030015 | -0.00034615 | -0.0014038 | 0.035677 | 0.019713 | 0.037542 | 0.0027387 | 0.011442 | 0.00051699 | -0.40283 | 0.20142 | -122.9507 | -0.07782 | -122.0673 | -122.6715 | -122.6944 | 0.022888 | 0.17853 | -0.1236 | 0.10529 | 0.15564 | 0.064087 | 0.20599 | -0.33875 | 0.027466 | -0.25177 | 0.54474 | -0.082397 | -0.059509 | 0.25635 | 0.27924 | 122.4884 | 0.004578 | -0.068664 | 122.7676 | 122.818 | 122.6761 | 0.32959 | 0.18768 | 0.88348 | 122.8729 | 0.27924 | 0.22888 | 123.1522 | 0.30212 | 122.8134 | 122.7905 | -123.1247 | -0.29755 | 122.5342 | 122.7173 | 122.2092 | 122.6349
931.3594 | 122.8546 | -122.7081 | 0.20142 | 0.018692 | 0.004751 | 0.070867 | 0.062709 | 0.0043771 | -0.0015061 | -0.00098695 | 0.0046998 | 0.0376 | 0.021636 | 0.034124 | -0.0036701 | 0.0088782 | 0.0035078 | -0.3479 | 0.21515 | -122.9919 | -0.1236 | -122.0856 | -122.6532 | -122.7081 | -0.068665 | 0.2243 | -0.11902 | -0.013733 | 0.07782 | -0.018311 | 0.12817 | -0.28381 | 0.013733 | -0.32501 | 0.62256 | 0 | 0.054932 | 0.28381 | 0.33875 | 122.5891 | 0.022888 | -0.21515 | 122.7859 | 122.8363 | 122.6898 | 0.24719 | 0.10071 | 0.90637 | 122.8683 | 0.19684 | 0.10529 | 123.2071 | 0.34332 | 122.9233 | 122.9324 | -123.1934 | -0.32044 | 122.5845 | 122.6944 | 122.3602 | 122.6395
933.1094 | 122.8729 | -122.6898 | 0.21515 | 0.011063 | 0.0043238 | 0.068945 | 0.066127 | 0.0054453 | -0.0025741 | 0.00072205 | 0.0077514 | 0.038241 | 0.020781 | 0.027075 | -0.0021747 | 0.009519 | 0.00094419 | -0.3479 | 0.2243 | -122.9691 | -0.1236 | -122.0901 | -122.6578 | -122.699 | -0.050354 | 0.21057 | -0.12817 | 0 | 0.09613 | -0.009155 | 0.13275 | -0.27924 | 0.009155 | -0.33875 | 0.59967 | -0.009156 | 0.032043 | 0.27008 | 0.31128 | 122.5616 | -0.004578 | -0.21515 | 122.7859 | 122.8226 | 122.6807 | 0.26093 | 0.11902 | 0.87891 | 122.8455 | 0.2243 | 0.12817 | 123.1934 | 0.33875 | 122.9141 | 122.9004 | -123.1842 | -0.34332 | 122.5662 | 122.6898 | 122.3419 | 122.6395
934.8438 | 122.8775 | -122.6944 | 0.19226 | 0.018692 | 0.0036828 | 0.068731 | 0.066127 | 0.0033089 | -0.0032151 | -0.002696 | 0.0077514 | 0.037813 | 0.020995 | 0.026647 | -0.0032427 | 0.0097326 | -0.0018328 | -0.3479 | 0.20599 | -122.9965 | -0.12817 | -122.0947 | -122.6486 | -122.6852 | -0.073242 | 0.21973 | -0.11902 | 0 | 0.091553 | 0 | 0.12817 | -0.30212 | 0.013733 | -0.32044 | 0.59967 | 0.009155 | 0.045776 | 0.31128 | 0.3479 | 122.5754 | 0.027466 | -0.19226 | 122.7859 | 122.8226 | 122.6944 | 0.24719 | 0.11902 | 0.90179 | 122.8683 | 0.21057 | 0.11902 | 123.2025 | 0.33875 | 122.9004 | 122.9141 | -123.1888 | -0.31128 | 122.5662 | 122.6944 | 122.3465 | 122.6212
936.5938 | 122.9736 | -122.644 | 0.15564 | 0.011063 | 0.0034692 | 0.06809 | 0.06335 | 0.0022409 | 0.00041651 | -0.00077335 | -0.0014038 | 0.037386 | 0.021209 | 0.037969 | -0.0015337 | 0.008451 | -0.00055121 | -0.37079 | 0.15106 | -122.9416 | -0.013733 | -121.9482 | -122.5204 | -122.6074 | 0.10529 | 0.14191 | -0.086975 | 0.1236 | 0.23346 | 0.13733 | 0.22888 | -0.29755 | -0.004578 | -0.16937 | 0.6958 | 0.036621 | 0.1236 | 0.33417 | 0.42114 | 122.5571 | -0.013733 | -0.032044 | 122.8775 | 122.8729 | 122.7814 | 0.31586 | 0.2243 | 0.99335 | 122.9279 | 0.32043 | 0.21057 | 123.0927 | 0.22888 | 122.7951 | 122.7859 | -123.0972 | -0.24261 | 122.6303 | 122.7676 | 122.2733 | 122.7493
938.2812 | 122.9507 | -122.6486 | 0.17853 | 0.011063 | 0.0045374 | 0.071081 | 0.06335 | 0.0028817 | -0.0025741 | 0.00072205 | -0.0014038 | 0.03525 | 0.019286 | 0.030706 | 0.0029523 | 0.00781 | 0.0045758 | -0.38452 | 0.18768 | -122.9279 | -0.054932 | -122.0215 | -122.6303 | -122.6578 | 0.036621 | 0.16479 | -0.082397 | 0.11902 | 0.17395 | 0.086975 | 0.2243 | -0.27923 | 0.009155 | -0.23346 | 0.62714 | -0.009155 | 0.018311 | 0.27008 | 0.29755 | 122.5662 | -0.013733 | -0.059509 | 122.8226 | 122.8729 | 122.7356 | 0.3067 | 0.16937 | 0.90637 | 122.8729 | 0.25635 | 0.20142 | 123.1155 | 0.24719 | 122.8363 | 122.8134 | -123.1064 | -0.26092 | 122.5937 | 122.7676 | 122.2641 | 122.6852
940.0312 | 122.8363 | -122.7219 | 0.20599 | 0.0034333 | 0.004751 | 0.067663 | 0.066127 | -0.00053626 | -0.0032151 | 0.0015764 | 0.001648 | 0.035464 | 0.020354 | 0.025366 | -0.0032427 | 0.0090918 | -0.00033761 | -0.37994 | 0.21515 | -122.9507 | -0.11902 | -122.0718 | -122.6532 | -122.699 | -0.073242 | 0.21057 | -0.10986 | -0.032043 | 0.07782 | -0.013733 | 0.11444 | -0.22888 | 0.009155 | -0.32501 | 0.65002 | 0.022888 | 0.068665 | 0.25177 | 0.29755 | 122.612 | 0.004577 | -0.23804 | 122.7997 | 122.8363 | 122.7081 | 0.2243 | 0.09613 | 0.87891 | 122.8317 | 0.18768 | 0.07782 | 123.1659 | 0.32043 | 122.937 | 122.9324 | -123.1567 | -0.31586 | 122.6028 | 122.6898 | 122.3419 | 122.6486
941.7188 | 122.8775 | -122.6715 | 0.16937 | -0.011826 | 0.0056054 | 0.069799 | 0.065059 | 0.0048043 | -0.0025741 | -0.0024824 | -0.0014038 | 0.036959 | 0.021636 | 0.031561 | 0.0027387 | 0.0086646 | 0.001585 | -0.40741 | 0.20599 | -122.9507 | -0.11444 | -122.0901 | -122.6852 | -122.7173 | -0.032043 | 0.18768 | -0.12817 | 0.050354 | 0.10529 | 0.013733 | 0.16479 | -0.27924 | 0.036621 | -0.28381 | 0.58136 | -0.045776 | -0.013733 | 0.23346 | 0.2655 | 122.5433 | 0.01831 | -0.11902 | 122.7768 | 122.8363 | 122.6852 | 0.29297 | 0.14191 | 0.8606 | 122.8363 | 0.23346 | 0.17853 | 123.1567 | 0.31586 | 122.8775 | 122.8592 | -123.1201 | -0.29755 | 122.5571 | 122.7219 | 122.2641 | 122.6395
943.4688 | 122.8455 | -122.699 | 0.20599 | 0.011063 | 0.0049646 | 0.066808 | 0.062923 | 0.0028817 | -0.0040695 | 0.002431 | 0.0077514 | 0.037173 | 0.019927 | 0.024297 | -0.0015337 | 0.0088782 | 0.00073059 | -0.37994 | 0.20599 | -122.9965 | -0.11444 | -122.0764 | -122.6532 | -122.7036 | -0.086975 | 0.21973 | -0.12817 | -0.027466 | 0.07782 | -0.004578 | 0.11902 | -0.29755 | 0 | -0.32044 | 0.62256 | -0.004577 | 0.045777 | 0.29297 | 0.34332 | 122.5708 | 0.013733 | -0.23346 | 122.7768 | 122.818 | 122.6944 | 0.24719 | 0.1236 | 0.92011 | 122.8821 | 0.20599 | 0.10071 | 123.2025 | 0.3479 | 122.905 | 122.9187 | -123.2025 | -0.33417 | 122.5845 | 122.6715 | 122.319 | 122.612
945.2031 | 122.8363 | -122.6852 | 0.18768 | 0.0034333 | 0.004751 | 0.070226 | 0.0657 | 0.0020273 | -0.0040695 | 0.00072205 | 0.010803 | 0.035891 | 0.021849 | 0.026647 | -0.0021747 | 0.0088782 | -0.00012381 | -0.3891 | 0.2243 | -122.9874 | -0.11902 | -122.081 | -122.644 | -122.699 | -0.073242 | 0.22888 | -0.10986 | 0 | 0.07782 | -0.022888 | 0.11902 | -0.30212 | 0.036621 | -0.3067 | 0.60425 | -0.013733 | 0.041199 | 0.28839 | 0.34332 | 122.5754 | 0.041199 | -0.18768 | 122.7631 | 122.8043 | 122.6624 | 0.22888 | 0.086975 | 0.90637 | 122.8683 | 0.18768 | 0.10986 | 123.2117 | 0.33875 | 122.9095 | 122.9141 | -123.175 | -0.29755 | 122.5662 | 122.6852 | 122.2961 | 122.612
946.9375 | 122.9324 | -122.6578 | 0.16937 | 0.011063 | 0.007528 | 0.073431 | 0.066341 | 0.0037363 | -0.0021469 | 0.00072205 | 0.010803 | 0.033755 | 0.02014 | 0.030065 | 0.0012433 | 0.0097326 | -0.0018328 | -0.37079 | 0.1831 | -122.9095 | 0 | -121.9437 | -122.5754 | -122.6212 | 0.086975 | 0.16022 | -0.082397 | 0.11444 | 0.1831 | 0.086975 | 0.20142 | -0.25177 | 0.013732 | -0.16937 | 0.71411 | 0.036621 | 0.082398 | 0.28839 | 0.33417 | 122.5754 | -0.009156 | -0.054932 | 122.8409 | 122.8592 | 122.7448 | 0.28381 | 0.16937 | 0.96588 | 122.9095 | 0.2655 | 0.19684 | 123.0927 | 0.24261 | 122.8409 | 122.818 | -123.0789 | -0.25177 | 122.6578 | 122.7722 | 122.287 | 122.7448
948.625 | 122.9691 | -122.6669 | 0.14648 | 0.0034333 | 0.0019738 | 0.071722 | 0.063777 | 0.0026681 | -0.00065149 | -0.0022688 | 0.001648 | 0.034395 | 0.022277 | 0.03391 | 0.00017507 | 0.0082374 | 0.0017988 | -0.37994 | 0.17853 | -122.9462 | -0.032043 | -121.9757 | -122.5571 | -122.6028 | 0.054932 | 0.17853 | -0.09613 | 0.10529 | 0.19226 | 0.11902 | 0.24261 | -0.27924 | 0.032044 | -0.17853 | 0.69122 | 0.064087 | 0.10986 | 0.34332 | 0.3891 | 122.5708 | 0.032044 | -0.041198 | 122.8592 | 122.9095 | 122.7859 | 0.33874 | 0.21515 | 0.97046 | 122.9141 | 0.28839 | 0.20142 | 123.1247 | 0.27466 | 122.8455 | 122.8455 | -123.0927 | -0.24261 | 122.6349 | 122.7722 | 122.287 | 122.7219
950.3125 | 122.8912 | -122.6669 | 0.17853 | 0.026321 | 0.0036828 | 0.068304 | 0.067409 | -0.0011771 | -0.0032151 | 0.0030718 | 0.0046998 | 0.038882 | 0.018859 | 0.027075 | 0.0018841 | 0.0080236 | -0.0020464 | -0.30212 | 0.21057 | -122.9645 | -0.045776 | -122.0261 | -122.612 | -122.6807 | 0.018311 | 0.19684 | -0.10071 | 0.045776 | 0.1236 | 0.022888 | 0.16479 | -0.29755 | 0.032043 | -0.2243 | 0.64087 | -0.013733 | 0.054931 | 0.28381 | 0.35248 | 122.5662 | 0.01831 | -0.13275 | 122.7905 | 122.8317 | 122.6898 | 0.2655 | 0.1236 | 0.93842 | 122.9187 | 0.2243 | 0.14648 | 123.175 | 0.29755 | 122.8775 | 122.8638 | -123.143 | -0.27924 | 122.6212 | 122.7127 | 122.3648 | 122.6852
952.0625 | 122.8592 | -122.6852 | 0.16937 | 0.011063 | 0.0032556 | 0.070867 | 0.066341 | 0.0058725 | -0.00043789 | 0.00029485 | 0.001648 | 0.036532 | 0.02249 | 0.029424 | 0.0014569 | 0.0088782 | 0.003294 | -0.41657 | 0.22888 | -122.9736 | -0.12817 | -122.113 | -122.6898 | -122.7219 | -0.059509 | 0.1831 | -0.1236 | 0.018311 | 0.068665 | -0.027466 | 0.14191 | -0.28839 | 0.059509 | -0.29755 | 0.5722 | -0.036621 | -0.004577 | 0.25177 | 0.28381 | 122.5616 | 0.013732 | -0.15106 | 122.7539 | 122.8271 | 122.6578 | 0.2655 | 0.09613 | 0.8606 | 122.8455 | 0.19226 | 0.14191 | 123.2025 | 0.3067 | 122.9141 | 122.8683 | -123.143 | -0.29297 | 122.5571 | 122.7036 | 122.2687 | 122.6257
953.75 | 122.905 | -122.6715 | 0.1831 | 0.011063 | 0.0041102 | 0.068517 | 0.065273 | 0.0035227 | -0.00065149 | 8.125e-05 | 0.0046998 | 0.038668 | 0.023131 | 0.022161 | 0.00081607 | 0.0090918 | -0.002901 | -0.31128 | 0.21515 | -122.9599 | -0.07782 | -122.0306 | -122.612 | -122.6852 | 0.036621 | 0.19226 | -0.10986 | 0.054932 | 0.13733 | 0.041199 | 0.16937 | -0.28839 | 0.032044 | -0.26092 | 0.64087 | -0.013733 | 0.059509 | 0.27466 | 0.3479 | 122.5616 | 0.009156 | -0.12817 | 122.8088 | 122.8409 | 122.7127 | 0.27924 | 0.15106 | 0.92926 | 122.8821 | 0.24719 | 0.16479 | 123.175 | 0.30212 | 122.8867 | 122.8638 | -123.143 | -0.29297 | 122.5937 | 122.7264 | 122.3602 | 122.7081
955.5 | 122.85 | -122.6532 | 0.19226 | 0.018692 | 0.0036828 | 0.071722 | 0.064632 | 0.0026681 | -0.0025741 | 0.00050845 | 0.001648 | 0.037173 | 0.022704 | 0.032629 | 0.00038887 | 0.0097326 | -0.00012381 | -0.39825 | 0.21057 | -122.9553 | -0.13733 | -122.113 | -122.6852 | -122.7356 | -0.07782 | 0.20599 | -0.11902 | 0 | 0.064087 | -0.045776 | 0.13275 | -0.30212 | 0.01831 | -0.32959 | 0.54016 | -0.082398 | -0.032044 | 0.21973 | 0.27008 | 122.5342 | 0.013733 | -0.19226 | 122.7173 | 122.7859 | 122.6074 | 0.25177 | 0.073243 | 0.84228 | 122.818 | 0.18311 | 0.11902 | 123.1659 | 0.32501 | 122.8638 | 122.8592 | -123.1476 | -0.31128 | 122.5159 | 122.6532 | 122.2549 | 122.5754
957.1875 | 122.9553 | -122.6669 | 0.17395 | -0.0041962 | 0.0026148 | 0.070013 | 0.062496 | 0.0048043 | -0.0044967 | 0.00029485 | 0.001648 | 0.035036 | 0.021849 | 0.031774 | -0.00067933 | 0.010587 | 0.0017988 | -0.42572 | 0.19226 | -122.9279 | -0.054932 | -121.9894 | -122.5708 | -122.6257 | 0.041199 | 0.17395 | -0.091553 | 0.091553 | 0.20142 | 0.10986 | 0.2243 | -0.26093 | 0.018311 | -0.22888 | 0.67749 | 0.041199 | 0.09613 | 0.30212 | 0.35706 | 122.5754 | 0 | -0.082397 | 122.8683 | 122.8912 | 122.7768 | 0.31586 | 0.20142 | 0.93842 | 122.8729 | 0.29297 | 0.18311 | 123.1201 | 0.2655 | 122.8592 | 122.8409 | -123.1018 | -0.2655 | 122.612 | 122.7585 | 122.2412 | 122.7081
958.9375 | 122.905 | -122.6807 | 0.1831 | 0.011063 | 0.0034692 | 0.069158 | 0.065913 | 0.0056589 | -0.00043789 | -0.0018414 | 0.0046998 | 0.037173 | 0.020781 | 0.028997 | 0.00081607 | 0.0080236 | 0.00051699 | -0.32959 | 0.2243 | -122.9736 | -0.054932 | -122.0306 | -122.612 | -122.6578 | 0.009155 | 0.20142 | -0.091553 | 0.064087 | 0.14648 | 0.041199 | 0.16022 | -0.29297 | 0.041199 | -0.23804 | 0.65002 | 0.022888 | 0.068664 | 0.31586 | 0.36163 | 122.5891 | 0.018311 | -0.11902 | 122.8271 | 122.8409 | 122.7219 | 0.25177 | 0.13275 | 0.94299 | 122.9187 | 0.23804 | 0.15564 | 123.1979 | 0.29297 | 122.905 | 122.8821 | -123.1567 | -0.27466 | 122.6257 | 122.7448 | 122.3511 | 122.6898
960.6719 | 122.8317 | -122.7127 | 0.20599 | 0.0034333 | 0.0056054 | 0.069372 | 0.0657 | 0.0020273 | -0.0021469 | -0.00013235 | -0.0014038 | 0.036104 | 0.021636 | 0.023657 | -0.0021747 | 0.0097326 | -0.007387 | -0.3891 | 0.19684 | -122.9507 | -0.12817 | -122.081 | -122.6303 | -122.6898 | -0.054932 | 0.21515 | -0.11902 | -0.018311 | 0.073242 | -0.009155 | 0.09613 | -0.23804 | -0.009156 | -0.33417 | 0.63171 | 0.022889 | 0.082398 | 0.26093 | 0.32044 | 122.5937 | 0.009155 | -0.22431 | 122.7859 | 122.8088 | 122.7036 | 0.21515 | 0.10986 | 0.86975 | 122.8226 | 0.19226 | 0.10071 | 123.1476 | 0.33417 | 122.9095 | 122.9279 | -123.1567 | -0.32501 | 122.5845 | 122.6944 | 122.3236 | 122.6578
962.4062 | 122.8867 | -122.6624 | 0.19226 | 0.0034333 | 0.0058192 | 0.070226 | 0.066554 | 0.0048043 | -0.0034287 | -0.00013235 | 0.0046998 | 0.036532 | 0.021422 | 0.027715 | 0.0018841 | 0.0099462 | 0.00073059 | -0.42114 | 0.20599 | -122.9691 | -0.1236 | -122.081 | -122.6852 | -122.699 | -0.036621 | 0.18768 | -0.09613 | 0.045776 | 0.10071 | -0.004578 | 0.16022 | -0.3067 | 0.013733 | -0.31586 | 0.58136 | -0.036621 | -0.022888 | 0.27008 | 0.28381 | 122.5662 | -0.004578 | -0.14648 | 122.7631 | 122.8226 | 122.6578 | 0.25635 | 0.091552 | 0.88806 | 122.8455 | 0.19684 | 0.14191 | 123.175 | 0.28381 | 122.8683 | 122.85 | -123.1613 | -0.28839 | 122.5388 | 122.7081 | 122.2412 | 122.6257
964.0938 | 122.8317 | -122.731 | 0.20599 | -0.0041962 | 0.00646 | 0.07044 | 0.064418 | 0.0088631 | -0.0023605 | -0.0012006 | -0.0014038 | 0.037386 | 0.02249 | 0.028356 | -0.00067933 | 0.0086646 | 0.00073059 | -0.37994 | 0.20142 | -122.937 | -0.13275 | -122.113 | -122.7036 | -122.7448 | -0.10529 | 0.19684 | -0.1236 | -0.018311 | 0.041199 | -0.059509 | 0.10986 | -0.20599 | -0.004578 | -0.33875 | 0.61798 | -0.013733 | 0.027466 | 0.19226 | 0.23346 | 122.6074 | -0.009156 | -0.22431 | 122.7722 | 122.8409 | 122.6715 | 0.23346 | 0.064087 | 0.82397 | 122.8043 | 0.16479 | 0.10528 | 123.1384 | 0.32043 | 122.9324 | 122.9279 | -123.143 | -0.32959 | 122.5983 | 122.7127 | 122.3511 | 122.6257
965.8281 | 122.8867 | -122.6761 | 0.19684 | 0.018692 | 0.0049646 | 0.071508 | 0.064418 | 0.0035227 | -0.00065149 | -0.00055975 | -0.0014038 | 0.037173 | 0.020568 | 0.025579 | 0.00017507 | 0.0073828 | 8.9786e-05 | -0.31586 | 0.2243 | -122.9507 | -0.068665 | -122.0215 | -122.6028 | -122.6669 | 0 | 0.18768 | -0.11444 | 0.050354 | 0.13275 | 0.022888 | 0.16937 | -0.27466 | 0.027466 | -0.2655 | 0.6546 | 0.009155 | 0.073242 | 0.28381 | 0.3479 | 122.5616 | -0.009155 | -0.14648 | 122.8088 | 122.8455 | 122.699 | 0.28381 | 0.13733 | 0.92926 | 122.8821 | 0.24719 | 0.16479 | 123.175 | 0.30212 | 122.9004 | 122.8638 | -123.1476 | -0.31128 | 122.6074 | 122.7264 | 122.3602 | 122.6761
967.5781 | 122.9507 | -122.644 | 0.16022 | 0.018692 | 0.0051782 | 0.071935 | 0.064845 | 0.0071541 | -0.0042831 | 0.00093565 | 0.001648 | 0.036959 | 0.019072 | 0.036047 | 0.0020979 | 0.01016 | 0.00094419 | -0.42572 | 0.20599 | -122.9324 | -0.09613 | -122.049 | -122.6578 | -122.6715 | 0.018311 | 0.17395 | -0.091553 | 0.10071 | 0.17395 | 0.041199 | 0.21973 | -0.28839 | 0.045777 | -0.25635 | 0.59509 | -0.027466 | -0.013733 | 0.26093 | 0.27466 | 122.5525 | 0.013733 | -0.059509 | 122.818 | 122.8638 | 122.6852 | 0.31128 | 0.13275 | 0.88348 | 122.8363 | 0.2655 | 0.19226 | 123.1384 | 0.2655 | 122.85 | 122.818 | -123.0927 | -0.25177 | 122.5479 | 122.7448 | 122.2183 | 122.6624
969.2656 | 122.9965 | -122.644 | 0.15564 | 0.0034333 | 0.0026148 | 0.068731 | 0.063136 | 0.0033089 | -0.0017197 | -0.0018414 | -0.0014038 | 0.035677 | 0.021849 | 0.032201 | -0.0013201 | 0.012083 | -0.0020464 | -0.37079 | 0.16022 | -122.9416 | 0.009155 | -121.9162 | -122.5296 | -122.5754 | 0.11902 | 0.15564 | -0.086975 | 0.10986 | 0.21057 | 0.13733 | 0.21515 | -0.29755 | 0.004577 | -0.14649 | 0.72784 | 0.068665 | 0.11444 | 0.36621 | 0.41199 | 122.5571 | 0 | -0.045777 | 122.8546 | 122.8592 | 122.7814 | 0.30212 | 0.2243 | 1.0254 | 122.9507 | 0.29755 | 0.19684 | 123.1018 | 0.24261 | 122.8043 | 122.7997 | -123.0972 | -0.24261 | 122.6532 | 122.7539 | 122.2733 | 122.7631
971 | 122.8867 | -122.6852 | 0.19226 | 0.0034333 | 0.0058192 | 0.071081 | 0.067195 | 0.0050179 | -0.0021469 | 0.0013628 | 0.0046998 | 0.038027 | 0.019713 | 0.022802 | -0.0017475 | 0.0093054 | -0.0018328 | -0.32044 | 0.20599 | -122.9553 | -0.054932 | -122.0123 | -122.612 | -122.6715 | 0.027466 | 0.17853 | -0.1236 | 0.050354 | 0.13733 | 0.022888 | 0.16022 | -0.27008 | 0.013733 | -0.24719 | 0.67291 | 0.013733 | 0.073242 | 0.28381 | 0.34332 | 122.5616 | -0.013733 | -0.14191 | 122.8226 | 122.8455 | 122.7081 | 0.28381 | 0.14648 | 0.94299 | 122.9004 | 0.26093 | 0.17395 | 123.1613 | 0.30212 | 122.8912 | 122.8638 | -123.1476 | -0.31586 | 122.6303 | 122.7356 | 122.3648 | 122.7127
972.75 | 122.8638 | -122.699 | 0.20142 | 0.018692 | 0.0060328 | 0.068731 | 0.064418 | 0.0075815 | -0.0023605 | 0.00093565 | 0.013855 | 0.037386 | 0.022917 | 0.027075 | -0.0013201 | 0.00781 | -0.00076481 | -0.36163 | 0.25177 | -122.9874 | -0.09613 | -122.0673 | -122.6028 | -122.6715 | -0.054932 | 0.20599 | -0.12817 | 0.022888 | 0.11902 | 0.013733 | 0.15564 | -0.28839 | 0.050354 | -0.29755 | 0.63171 | 0.027466 | 0.096131 | 0.31586 | 0.38452 | 122.5708 | 0.004578 | -0.17853 | 122.818 | 122.8546 | 122.7127 | 0.28381 | 0.14191 | 0.9201 | 122.8912 | 0.24719 | 0.15106 | 123.2391 | 0.33417 | 122.9507 | 122.905 | -123.1888 | -0.32959 | 122.6028 | 122.7219 | 122.3373 | 122.644
974.5156 | 122.937 | -122.6486 | 0.1831 | 0.018692 | 0.00090577 | 0.070867 | 0.062923 | 0.00053194 | -0.0015061 | 8.125e-05 | -0.0014038 | 0.033541 | 0.0195 | 0.035833 | -0.00089293 | 0.010374 | -0.0016192 | -0.44403 | 0.1831 | -122.9187 | -0.059509 | -122.0169 | -122.5891 | -122.6303 | 0.009155 | 0.16479 | -0.09613 | 0.07782 | 0.17853 | 0.091553 | 0.17853 | -0.27008 | 0 | -0.24261 | 0.63171 | 0.018311 | 0.05951 | 0.28839 | 0.32959 | 122.5525 | -0.01831 | -0.10528 | 122.8271 | 122.8271 | 122.7402 | 0.27466 | 0.18768 | 0.90179 | 122.8592 | 0.27466 | 0.17395 | 123.1018 | 0.26092 | 122.8317 | 122.8134 | -123.1018 | -0.27924 | 122.5891 | 122.7264 | 122.2046 | 122.6578
976.2031 | 122.937 | -122.6624 | 0.14191 | 0.011063 | 0.0049646 | 0.07044 | 0.065059 | 0.0041635 | 0.0019119 | -0.00055975 | 0.0077514 | 0.035677 | 0.020781 | 0.027929 | 0.0014569 | 0.009519 | 0.0035078 | -0.37079 | 0.17395 | -122.9187 | 0.009155 | -121.9299 | -122.5662 | -122.5983 | 0.086975 | 0.17395 | -0.09613 | 0.11902 | 0.1831 | 0.073242 | 0.21515 | -0.25635 | 0.032043 | -0.13275 | 0.73242 | 0.064087 | 0.096131 | 0.32043 | 0.35248 | 122.5662 | 0.032043 | -0.022888 | 122.8455 | 122.8775 | 122.7356 | 0.31128 | 0.16937 | 0.98877 | 122.9279 | 0.27924 | 0.21515 | 123.0927 | 0.27008 | 122.8363 | 122.8363 | -123.0606 | -0.23804 | 122.6715 | 122.7814 | 122.2916 | 122.7493
977.9531 | 122.9416 | -122.6074 | 0.16479 | 0.011063 | 0.0041102 | 0.071935 | 0.0657 | 0.0015999 | -0.0027877 | 0.0013628 | 0.010803 | 0.034609 | 0.020354 | 0.034124 | 0.0031659 | 0.011014 | 0.0035078 | -0.36621 | 0.17395 | -122.9233 | 0.018311 | -121.9528 | -122.5479 | -122.5983 | 0.10071 | 0.15564 | -0.086975 | 0.1236 | 0.20599 | 0.091553 | 0.22888 | -0.31586 | 0.009155 | -0.14648 | 0.6546 | 0.009155 | 0.059509 | 0.32501 | 0.37537 | 122.5204 | -0.009155 | -0.041199 | 122.8134 | 122.8363 | 122.699 | 0.31586 | 0.17853 | 0.97046 | 122.9416 | 0.29297 | 0.21057 | 123.0972 | 0.24261 | 122.7814 | 122.7631 | -123.0881 | -0.25177 | 122.6257 | 122.731 | 122.2412 | 122.7081
979.7188 | 122.9187 | -122.6578 | 0.16937 | 0.0034333 | 0.0060328 | 0.070013 | 0.067409 | 0.0035227 | -0.00043789 | -0.0016278 | 0.0046998 | 0.037173 | 0.022063 | 0.029638 | 0.0014569 | 0.010374 | 0.00094419 | -0.43488 | 0.20599 | -122.9462 | -0.07782 | -122.0535 | -122.6578 | -122.6944 | 0.013733 | 0.16937 | -0.09613 | 0.07782 | 0.16479 | 0.045776 | 0.20599 | -0.28839 | 0.036621 | -0.24719 | 0.60425 | -0.036621 | 0 | 0.25177 | 0.28839 | 122.5616 | 0 | -0.091553 | 122.8226 | 122.8638 | 122.7036 | 0.30212 | 0.14191 | 0.89264 | 122.8683 | 0.26092 | 0.17395 | 123.1522 | 0.2655 | 122.8638 | 122.8271 | -123.1155 | -0.2655 | 122.58 | 122.7356 | 122.2229 | 122.6715
981.4062 | 122.8592 | -122.6715 | 0.21057 | 0.018692 | 0.0034692 | 0.070654 | 0.067622 | 0.0028817 | -0.0030015 | -0.00034615 | 0.0077514 | 0.036959 | 0.020995 | 0.023229 | -0.0032427 | 0.00781 | -0.0014056 | -0.37537 | 0.21973 | -122.9828 | -0.10529 | -122.0764 | -122.6212 | -122.6761 | -0.050354 | 0.19684 | -0.13275 | -0.013733 | 0.10071 | -0.004578 | 0.15106 | -0.31128 | 0.009156 | -0.31586 | 0.59509 | -0.004577 | 0.050354 | 0.3067 | 0.36163 | 122.5388 | -0.013733 | -0.2243 | 122.7722 | 122.8226 | 122.6669 | 0.28381 | 0.12817 | 0.90637 | 122.8775 | 0.23346 | 0.11902 | 123.2025 | 0.32959 | 122.8912 | 122.8683 | -123.1934 | -0.34332 | 122.5662 | 122.6578 | 122.2961 | 122.6212
983.0781 | 122.9553 | -122.6257 | 0.14648 | 0.018692 | 0.0060328 | 0.073004 | 0.06335 | 0.0022409 | -0.0019333 | -0.002696 | 0.0077514 | 0.034395 | 0.017791 | 0.037115 | 0.0020979 | 0.011228 | 0.001585 | -0.37994 | 0.1831 | -122.9187 | 0.013733 | -121.9437 | -122.5479 | -122.5891 | 0.09613 | 0.17853 | -0.10071 | 0.10529 | 0.19684 | 0.086975 | 0.21515 | -0.29297 | 0.036621 | -0.13275 | 0.68207 | 0.036621 | 0.077819 | 0.32959 | 0.37079 | 122.525 | 0.032044 | -0.041198 | 122.8226 | 122.8409 | 122.7127 | 0.31586 | 0.18768 | 0.97504 | 122.9324 | 0.29755 | 0.20599 | 123.1018 | 0.27924 | 122.8088 | 122.8043 | -123.0652 | -0.24719 | 122.6395 | 122.731 | 122.2458 | 122.7219
984.8281 | 122.9004 | -122.6578 | 0.17853 | 0.0034333 | 0.0034692 | 0.071508 | 0.06335 | -0.0011771 | -0.0044967 | -0.00098695 | 0.010803 | 0.034395 | 0.019927 | 0.034765 | -0.0021747 | 0.0093054 | 0.00073059 | -0.44861 | 0.19226 | -122.9462 | -0.059509 | -122.0123 | -122.6074 | -122.6257 | 0 | 0.16937 | -0.10529 | 0.045776 | 0.13275 | 0.041199 | 0.1831 | -0.28839 | 0.013733 | -0.23804 | 0.64545 | 0.032044 | 0.050354 | 0.32044 | 0.33875 | 122.5525 | -0.009155 | -0.13275 | 122.7905 | 122.8409 | 122.699 | 0.28839 | 0.14649 | 0.93384 | 122.8867 | 0.23804 | 0.15106 | 123.1384 | 0.27466 | 122.85 | 122.8271 | -123.1247 | -0.28381 | 122.5983 | 122.7036 | 122.2092 | 122.6578
986.5781 | 122.9462 | -122.6578 | 0.15564 | 0.0034333 | 0.0058192 | 0.070013 | 0.067409 | 0.0071541 | 0.0021255 | -0.00013235 | 0.0046998 | 0.036318 | 0.021209 | 0.031988 | 0.0029523 | 0.009519 | 0.00030339 | -0.39368 | 0.18768 | -122.9141 | -0.013733 | -121.9666 | -122.58 | -122.612 | 0.082397 | 0.13275 | -0.086975 | 0.11902 | 0.16937 | 0.091553 | 0.24719 | -0.25635 | 0.032043 | -0.16937 | 0.69122 | 0.045776 | 0.07782 | 0.30212 | 0.33417 | 122.5708 | -0.022889 | -0.036621 | 122.8271 | 122.905 | 122.7493 | 0.33417 | 0.17853 | 0.94757 | 122.9004 | 0.25635 | 0.20599 | 123.1018 | 0.21973 | 122.8455 | 122.7905 | -123.0698 | -0.24261 | 122.644 | 122.7768 | 122.2641 | 122.7402
988.2969 | 122.8226 | -122.6898 | 0.18768 | 0.011063 | 0.0026148 | 0.069158 | 0.065486 | 0.0048043 | -0.0012925 | -0.00013235 | 0.0046998 | 0.036532 | 0.023558 | 0.020452 | -0.0043109 | 0.0086646 | 0.003935 | -0.40741 | 0.23346 | -122.9691 | -0.1236 | -122.0673 | -122.6257 | -122.6898 | -0.064087 | 0.2243 | -0.14648 | -0.027466 | 0.073242 | -0.027466 | 0.11902 | -0.27924 | 0.045776 | -0.31128 | 0.62256 | 0 | 0.064087 | 0.27924 | 0.34332 | 122.5433 | 0.036621 | -0.21515 | 122.7631 | 122.8088 | 122.6624 | 0.2655 | 0.11902 | 0.90179 | 122.8455 | 0.21973 | 0.11902 | 123.2025 | 0.37079 | 122.9233 | 122.9141 | -123.1567 | -0.33417 | 122.5662 | 122.6624 | 122.2824 | 122.6257
990.0156 | 122.8592 | -122.6624 | 0.17853 | 0.026321 | 0.0060328 | 0.070013 | 0.066554 | 0.0039499 | -0.0023605 | 8.125e-05 | 0.0046998 | 0.037173 | 0.02014 | 0.021307 | -0.0011065 | 0.0086646 | -0.0031146 | -0.36621 | 0.23346 | -122.9965 | -0.068665 | -122.0261 | -122.612 | -122.6715 | -0.027466 | 0.21515 | -0.11902 | 0.036621 | 0.1236 | 0.013733 | 0.15564 | -0.33417 | 0.054931 | -0.24719 | 0.63629 | -0.009155 | 0.050354 | 0.32501 | 0.38452 | 122.5433 | 0.036621 | -0.14191 | 122.7859 | 122.818 | 122.6761 | 0.27466 | 0.13275 | 0.97046 | 122.9279 | 0.24261 | 0.15564 | 123.23 | 0.33417 | 122.8958 | 122.8775 | -123.175 | -0.29755 | 122.5937 | 122.699 | 122.2961 | 122.6349
991.7812 | 122.9645 | -122.6486 | 0.16022 | -0.011826 | 0.0024012 | 0.068517 | 0.064204 | 0.0056589 | -0.0042831 | -0.0029096 | -0.0014038 | 0.035464 | 0.018218 | 0.034338 | -0.0011065 | 0.0090918 | 0.00030339 | -0.3891 | 0.17395 | -122.9279 | 0.013733 | -121.9116 | -122.5113 | -122.5662 | 0.11444 | 0.16022 | -0.082397 | 0.09613 | 0.20599 | 0.13733 | 0.22888 | -0.27923 | 0.013733 | -0.14648 | 0.737 | 0.082398 | 0.13733 | 0.36163 | 0.41656 | 122.5662 | 0 | -0.064087 | 122.8546 | 122.8775 | 122.7859 | 0.31128 | 0.21973 | 1.0162 | 122.9416 | 0.28839 | 0.17853 | 123.1018 | 0.24261 | 122.8226 | 122.8088 | -123.0881 | -0.24261 | 122.6624 | 122.7448 | 122.2595 | 122.7631
993.4688 | 122.8638 | -122.6761 | 0.18768 | 0.0034333 | 0.0058192 | 0.070226 | 0.065913 | 0.0048043 | -0.0017197 | -0.0018414 | 0.0046998 | 0.037813 | 0.021849 | 0.025579 | 0.00060247 | 0.0086646 | 0.00051699 | -0.3479 | 0.21057 | -122.937 | -0.059509 | -122.0169 | -122.6166 | -122.6486 | 0.032043 | 0.18768 | -0.10529 | 0.054932 | 0.1236 | 0.032043 | 0.16022 | -0.26093 | 0.022888 | -0.24719 | 0.65918 | 0.027465 | 0.059509 | 0.28839 | 0.32043 | 122.5708 | 0 | -0.13275 | 122.7997 | 122.8363 | 122.7081 | 0.2655 | 0.13733 | 0.9201 | 122.8775 | 0.22888 | 0.16022 | 123.1476 | 0.29297 | 122.8867 | 122.8638 | -123.1247 | -0.29297 | 122.6166 | 122.731 | 122.3282 | 122.7081
995.2188 | 122.9324 | -122.6715 | 0.16937 | -0.0041962 | 0.0015466 | 0.070654 | 0.063991 | 0.0069405 | -0.0019333 | -0.0012006 | 0.001648 | 0.034395 | 0.02014 | 0.034765 | -0.0013201 | 0.010374 | -0.00033761 | -0.44403 | 0.18768 | -122.9187 | -0.059509 | -121.9757 | -122.5662 | -122.6166 | 0.009155 | 0.15564 | -0.10071 | 0.07782 | 0.1831 | 0.07782 | 0.18768 | -0.24719 | 0.01831 | -0.22888 | 0.6958 | 0.054932 | 0.10529 | 0.30212 | 0.35248 | 122.5708 | -0.013733 | -0.091553 | 122.8546 | 122.8592 | 122.7493 | 0.28839 | 0.17853 | 0.94299 | 122.8592 | 0.28381 | 0.17853 | 123.1064 | 0.25635 | 122.8592 | 122.8271 | -123.0881 | -0.27008 | 122.612 | 122.7493 | 122.2275 | 122.6807
996.9688 | 122.9782 | -122.6395 | 0.17395 | 0.0034333 | 0.0032556 | 0.070226 | 0.062282 | 0.0024545 | -0.0030015 | -0.002696 | 0.0077514 | 0.035036 | 0.019713 | 0.030706 | -0.0017475 | 0.0088782 | 0.005003 | -0.37994 | 0.17853 | -122.9141 | 0.004578 | -121.8979 | -122.5204 | -122.5525 | 0.12817 | 0.16479 | -0.073242 | 0.10529 | 0.2243 | 0.1236 | 0.20599 | -0.27466 | 0.004578 | -0.16937 | 0.74158 | 0.086975 | 0.11902 | 0.36163 | 0.39368 | 122.5662 | -0.009155 | -0.068664 | 122.8638 | 122.8455 | 122.7631 | 0.27924 | 0.19684 | 1.0162 | 122.9187 | 0.29755 | 0.17853 | 123.0927 | 0.23804 | 122.818 | 122.8043 | -123.0881 | -0.24719 | 122.644 | 122.7448 | 122.2595 | 122.7676
998.6562 | 122.9324 | -122.6349 | 0.15106 | 0.018692 | 0.0060328 | 0.070867 | 0.065486 | 0.0054453 | -0.0030015 | 0.0028582 | 0.001648 | 0.036104 | 0.023131 | 0.029852 | 0.0025251 | 0.009519 | 0.00051699 | -0.37994 | 0.1831 | -122.9004 | 0.009155 | -121.9345 | -122.5433 | -122.58 | 0.10529 | 0.16937 | -0.086975 | 0.10986 | 0.1831 | 0.09613 | 0.21515 | -0.2655 | 0.032043 | -0.14191 | 0.70038 | 0.054932 | 0.091553 | 0.32044 | 0.35706 | 122.5479 | 0.018311 | -0.041199 | 122.818 | 122.85 | 122.731 | 0.30212 | 0.1831 | 0.96588 | 122.9095 | 0.27008 | 0.19684 | 123.0835 | 0.25635 | 122.818 | 122.8043 | -123.0515 | -0.23804 | 122.644 | 122.7448 | 122.2549 | 122.7402
1000.4062 | 122.8088 | -122.6807 | 0.20142 | 0.0034333 | 0.0058192 | 0.070226 | 0.066127 | 0.0077951 | -0.0015061 | 0.00072205 | -0.0014038 | 0.038241 | 0.020995 | 0.030706 | -0.00046573 | 0.0080236 | -0.00012381 | -0.42114 | 0.21973 | -122.9462 | -0.11902 | -122.1222 | -122.699 | -122.7448 | -0.086975 | 0.21057 | -0.11444 | -0.018311 | 0.032043 | -0.068665 | 0.10529 | -0.2655 | 0.018311 | -0.32044 | 0.55847 | -0.064087 | -0.018311 | 0.20142 | 0.24719 | 122.5662 | 0.009155 | -0.21973 | 122.7127 | 122.7859 | 122.612 | 0.21973 | 0.045776 | 0.82398 | 122.8271 | 0.14648 | 0.09613 | 123.1659 | 0.32501 | 122.9004 | 122.8912 | -123.1476 | -0.31586 | 122.5616 | 122.6624 | 122.2595 | 122.5937
1002.1562 | 122.9462 | -122.6257 | 0.15564 | 0.018692 | 0.0034692 | 0.071722 | 0.066127 | 0.0015999 | -0.0010789 | -0.0016278 | 0.001648 | 0.034823 | 0.019286 | 0.029852 | 0.0016705 | 0.01251 | 0.0026532 | -0.3891 | 0.19684 | -122.9095 | -0.004578 | -121.9482 | -122.5616 | -122.612 | 0.09613 | 0.16022 | -0.086975 | 0.11444 | 0.19226 | 0.09613 | 0.23346 | -0.28381 | 0.041198 | -0.16022 | 0.67749 | 0.013732 | 0.064086 | 0.29755 | 0.3479 | 122.5388 | 0.004577 | -0.041199 | 122.818 | 122.8592 | 122.7219 | 0.32043 | 0.1831 | 0.9613 | 122.905 | 0.27924 | 0.20142 | 123.1064 | 0.24719 | 122.8226 | 122.7859 | -123.0652 | -0.24261 | 122.6212 | 122.7402 | 122.2366 | 122.7219
1003.8438 | 122.8867 | -122.6578 | 0.16937 | -0.0041962 | 0.0066736 | 0.068731 | 0.065273 | 0.0026681 | -0.00043789 | 0.0017902 | 0.001648 | 0.0376 | 0.020568 | 0.02857 | 0.0018841 | 0.010801 | -0.00033761 | -0.44861 | 0.20599 | -122.9553 | -0.10986 | -122.0856 | -122.6624 | -122.7081 | -0.041199 | 0.19226 | -0.11444 | 0.036621 | 0.091553 | -0.004578 | 0.14191 | -0.29755 | 0.036621 | -0.27924 | 0.5722 | -0.050354 | -0.004578 | 0.24719 | 0.29297 | 122.5433 | 0.022888 | -0.13275 | 122.7493 | 122.7997 | 122.6532 | 0.25635 | 0.10986 | 0.86975 | 122.8455 | 0.20599 | 0.15106 | 123.1613 | 0.3067 | 122.8638 | 122.85 | -123.1247 | -0.28381 | 122.5479 | 122.6944 | 122.2092 | 122.6166
1005.5781 | 122.9141 | -122.644 | 0.15564 | 0.0034333 | 0.0071008 | 0.071508 | 0.0657 | 0.0041635 | -0.0034287 | 0.00093565 | 0.001648 | 0.036745 | 0.023345 | 0.02622 | 0.0040205 | 0.0097326 | -0.00055121 | -0.46234 | 0.19684 | -122.9462 | -0.068665 | -122.0215 | -122.6349 | -122.6624 | 0.032043 | 0.17395 | -0.086975 | 0.086975 | 0.16937 | 0.068665 | 0.21973 | -0.30212 | 0.041198 | -0.22431 | 0.62256 | -0.018311 | 0.009155 | 0.28381 | 0.31128 | 122.5571 | 0.01831 | -0.068665 | 122.8134 | 122.8638 | 122.7127 | 0.3067 | 0.15564 | 0.92468 | 122.8775 | 0.25635 | 0.17395 | 123.143 | 0.26092 | 122.8409 | 122.818 | -123.1018 | -0.24261 | 122.5754 | 122.731 | 122.1817 | 122.6761
1007.2656 | 122.9507 | -122.6303 | 0.16022 | -0.011826 | 0.0032556 | 0.069372 | 0.063564 | 0.0013863 | -0.0036423 | -0.00077335 | 0.001648 | 0.03525 | 0.019713 | 0.030065 | -0.0015337 | 0.0093054 | -0.0033282 | -0.3891 | 0.17395 | -122.9279 | 0.009155 | -121.8979 | -122.5067 | -122.5708 | 0.10529 | 0.17395 | -0.086975 | 0.11444 | 0.23346 | 0.11902 | 0.21973 | -0.29755 | 0.013733 | -0.15106 | 0.73242 | 0.059509 | 0.1236 | 0.35706 | 0.42114 | 122.5433 | 0.013733 | -0.045776 | 122.8638 | 122.85 | 122.7493 | 0.3067 | 0.20599 | 1.03 | 122.937 | 0.32043 | 0.20142 | 123.1018 | 0.26092 | 122.8043 | 122.8043 | -123.0881 | -0.24719 | 122.6395 | 122.7448 | 122.2412 | 122.7356
1009.0156 | 122.9416 | -122.6257 | 0.16022 | 0.0034333 | 0.0026148 | 0.070013 | 0.064845 | 0.0028817 | -0.0038559 | -0.0012006 | -0.0044556 | 0.032686 | 0.018859 | 0.034338 | -0.0023883 | 0.010374 | -0.00076481 | -0.3891 | 0.17853 | -122.9095 | 0.022888 | -121.8933 | -122.4976 | -122.5754 | 0.10529 | 0.16479 | -0.073242 | 0.09613 | 0.2243 | 0.13275 | 0.2243 | -0.28381 | 0.018311 | -0.13733 | 0.73242 | 0.050354 | 0.12817 | 0.33417 | 0.41199 | 122.5525 | 0.004578 | -0.064087 | 122.85 | 122.85 | 122.7585 | 0.29755 | 0.20599 | 1.0162 | 122.9324 | 0.29755 | 0.16937 | 123.0881 | 0.23804 | 122.8043 | 122.7905 | -123.0698 | -0.23346 | 122.6486 | 122.7219 | 122.2366 | 122.731
1010.6875 | 122.8363 | -122.6761 | 0.19684 | 0.026321 | 0.0032556 | 0.069799 | 0.067622 | 0.0052315 | -0.0027877 | 8.125e-05 | 0.010803 | 0.035891 | 0.021209 | 0.026861 | -0.0028155 | 0.0086646 | 8.9786e-05 | -0.40741 | 0.20599 | -122.9782 | -0.1236 | -122.0627 | -122.644 | -122.6898 | -0.082397 | 0.21057 | -0.1236 | -0.022888 | 0.07782 | 0 | 0.12817 | -0.30212 | 0.009156 | -0.32043 | 0.6134 | -0.013733 | 0.032043 | 0.28839 | 0.33417 | 122.5525 | 0.013733 | -0.21973 | 122.7539 | 122.8043 | 122.6761 | 0.25177 | 0.1236 | 0.91553 | 122.8546 | 0.20142 | 0.10071 | 123.1842 | 0.33417 | 122.8821 | 122.8867 | -123.175 | -0.32043 | 122.5525 | 122.6532 | 122.2687 | 122.5937
1012.4375 | 122.8363 | -122.6486 | 0.19684 | 0.0034333 | 0.0051782 | 0.069799 | 0.064845 | 0.0026681 | -0.0032151 | 0.0013628 | 0.001648 | 0.038241 | 0.023345 | 0.029638 | 0.00081607 | 0.0080236 | -0.0026874 | -0.36621 | 0.20599 | -122.9462 | -0.082397 | -122.0123 | -122.6074 | -122.6715 | -0.022888 | 0.1831 | -0.11444 | 0.027466 | 0.091553 | -0.027466 | 0.14191 | -0.29755 | 0.009156 | -0.27924 | 0.63629 | -0.022888 | 0.041199 | 0.27466 | 0.33875 | 122.5342 | -0.013733 | -0.16937 | 122.7402 | 122.7905 | 122.6212 | 0.25635 | 0.086975 | 0.93384 | 122.8638 | 0.20599 | 0.14191 | 123.1522 | 0.29755 | 122.8546 | 122.8317 | -123.143 | -0.31128 | 122.5662 | 122.6761 | 122.2824 | 122.6257
1014.2031 | 122.8271 | -122.6715 | 0.19684 | 0.011063 | 0.0034692 | 0.070226 | 0.0657 | 0.0039499 | -0.0012925 | -0.00098695 | 0.001648 | 0.03525 | 0.020354 | 0.030493 | -0.0045245 | 0.0075964 | -0.0033282 | -0.37994 | 0.17853 | -122.9416 | -0.054932 | -121.9757 | -122.5708 | -122.6212 | -0.022888 | 0.18768 | -0.10529 | 0.004578 | 0.10986 | 0.013733 | 0.13275 | -0.27008 | -0.01831 | -0.25177 | 0.6958 | 0.050354 | 0.10071 | 0.32043 | 0.37079 | 122.5662 | -0.009155 | -0.19226 | 122.7814 | 122.8043 | 122.6852 | 0.23804 | 0.11902 | 0.96588 | 122.8867 | 0.21515 | 0.10986 | 123.1201 | 0.29297 | 122.85 | 122.8592 | -123.1384 | -0.30212 | 122.6166 | 122.6761 | 122.2916 | 122.6486
1015.9531 | 122.9095 | -122.6532 | 0.17853 | 0.018692 | 0.0034692 | 0.070226 | 0.064204 | 0.0043771 | -0.0017197 | -0.00055975 | 0.001648 | 0.034395 | 0.021636 | 0.034551 | 0.0018841 | 0.009519 | 8.9786e-05 | -0.42572 | 0.17395 | -122.905 | -0.009155 | -121.9254 | -122.5525 | -122.5983 | 0.086975 | 0.16937 | -0.086975 | 0.10071 | 0.1831 | 0.07782 | 0.19684 | -0.25177 | -0.004578 | -0.18768 | 0.72784 | 0.054931 | 0.10071 | 0.3067 | 0.35248 | 122.5662 | -0.009155 | -0.07782 | 122.8363 | 122.85 | 122.731 | 0.28381 | 0.16479 | 0.97961 | 122.8958 | 0.27008 | 0.18768 | 123.0789 | 0.25635 | 122.8271 | 122.8226 | -123.0835 | -0.2655 | 122.644 | 122.7539 | 122.2275 | 122.7402
1017.625 | 122.85 | -122.6624 | 0.17395 | 0.018692 | 0.003042 | 0.068731 | 0.064845 | 0.0058725 | -0.00086509 | -0.00034615 | 0.0046998 | 0.037173 | 0.018431 | 0.028143 | 0.0012433 | 0.0069556 | -0.00012381 | -0.36163 | 0.21057 | -122.9416 | -0.068665 | -122.0123 | -122.5891 | -122.6486 | -0.018311 | 0.18768 | -0.11444 | 0.041199 | 0.1236 | 0.018311 | 0.16937 | -0.27923 | 0.036621 | -0.24261 | 0.65002 | 0.013733 | 0.073243 | 0.29297 | 0.35248 | 122.5479 | 0.013733 | -0.13275 | 122.7859 | 122.8317 | 122.6807 | 0.28381 | 0.13275 | 0.92926 | 122.8729 | 0.23804 | 0.15564 | 123.1522 | 0.30212 | 122.8729 | 122.85 | -123.1155 | -0.28839 | 122.5937 | 122.7036 | 122.3007 | 122.644
1019.3906 | 122.9095 | -122.612 | 0.16937 | 0.011063 | 0.0051782 | 0.070013 | 0.066768 | 0.0050179 | -0.0019333 | -0.0016278 | 0.001648 | 0.035891 | 0.019286 | 0.031561 | 0.00017507 | 0.0097326 | -0.0020464 | -0.45776 | 0.20142 | -122.9279 | -0.073242 | -122.0352 | -122.6212 | -122.644 | 0.009155 | 0.16479 | -0.10529 | 0.082397 | 0.16479 | 0.050354 | 0.19226 | -0.31586 | 0.032043 | -0.24261 | 0.57678 | -0.032043 | -0.009155 | 0.28381 | 0.3067 | 122.5067 | -0.004578 | -0.086976 | 122.7768 | 122.8043 | 122.6624 | 0.29755 | 0.15564 | 0.89264 | 122.8546 | 0.27008 | 0.18768 | 123.1293 | 0.27008 | 122.8134 | 122.7768 | -123.0972 | -0.27466 | 122.5388 | 122.6944 | 122.1542 | 122.6212
1021.0781 | 122.8683 | -122.6715 | 0.19684 | 0.018692 | 0.0043238 | 0.071508 | 0.064418 | 0.0095041 | -0.0017197 | 0.00093565 | 0.010803 | 0.036532 | 0.022917 | 0.024511 | -0.0017475 | 0.00781 | -0.00055121 | -0.38452 | 0.21515 | -122.9462 | -0.09613 | -122.0169 | -122.5845 | -122.6486 | -0.018311 | 0.20142 | -0.10529 | 0.018311 | 0.13733 | 0.022888 | 0.16479 | -0.27466 | 0.018311 | -0.29297 | 0.6546 | 0.022888 | 0.086975 | 0.29755 | 0.36163 | 122.5662 | 0.004578 | -0.17853 | 122.8088 | 122.8363 | 122.6944 | 0.27008 | 0.12817 | 0.92926 | 122.85 | 0.24262 | 0.1236 | 123.1613 | 0.3067 | 122.8867 | 122.8729 | -123.143 | -0.30212 | 122.5754 | 122.6898 | 122.287 | 122.6532
1022.8125 | 122.8867 | -122.644 | 0.17395 | 0.0034333 | 0.0021876 | 0.069799 | 0.062923 | 0.0050179 | -0.0015061 | 0.0020038 | 0.0046998 | 0.03525 | 0.023986 | 0.030706 | -0.0023883 | 0.010374 | -0.001192 | -0.48523 | 0.20142 | -122.9095 | -0.07782 | -121.9757 | -122.5708 | -122.6166 | 0.009155 | 0.1831 | -0.10071 | 0.045776 | 0.15564 | 0.041199 | 0.19226 | -0.2655 | 0.027466 | -0.25177 | 0.66833 | 0.027466 | 0.073242 | 0.29297 | 0.33875 | 122.5433 | 0.009155 | -0.12817 | 122.7997 | 122.8363 | 122.6852 | 0.29297 | 0.14191 | 0.93384 | 122.8317 | 0.25635 | 0.14648 | 123.111 | 0.28381 | 122.8455 | 122.8271 | -123.0835 | -0.27466 | 122.5662 | 122.6898 | 122.1588 | 122.6532
1024.5625 | 122.8043 | -122.6761 | 0.1831 | 0.0034333 | 0.0085962 | 0.070654 | 0.065059 | 0.0071541 | -0.0010789 | -0.0020552 | -0.0014038 | 0.035891 | 0.0195 | 0.029424 | 0.00038887 | 0.010374 | 0.0013714 | -0.4303 | 0.20599 | -122.9279 | -0.14191 | -122.0993 | -122.6944 | -122.7219 | -0.09613 | 0.20599 | -0.1236 | 0 | 0.041199 | -0.054932 | 0.11902 | -0.25177 | 0.022889 | -0.32501 | 0.57678 | -0.045777 | -0.018311 | 0.20599 | 0.23346 | 122.5525 | 0.022889 | -0.1831 | 122.7173 | 122.7951 | 122.6212 | 0.24261 | 0.068664 | 0.82855 | 122.7859 | 0.16479 | 0.1236 | 123.1339 | 0.32959 | 122.8821 | 122.8821 | -123.111 | -0.3067 | 122.5342 | 122.6761 | 122.2458 | 122.58
1026.3125 | 122.9462 | -122.6028 | 0.17395 | -0.0041962 | 0.0024012 | 0.071722 | 0.063777 | 0.0022409 | -0.00065149 | -0.00077335 | -0.0014038 | 0.033755 | 0.021636 | 0.032842 | -0.0019611 | 0.00781 | 0.0013714 | -0.40741 | 0.17395 | -122.8958 | 0.004578 | -121.875 | -122.4838 | -122.5571 | 0.091553 | 0.16937 | -0.082397 | 0.10986 | 0.2243 | 0.12817 | 0.22888 | -0.29297 | 0 | -0.16937 | 0.72784 | 0.045776 | 0.11902 | 0.33875 | 0.41199 | 122.5204 | -0.004577 | -0.064087 | 122.8271 | 122.8317 | 122.731 | 0.31128 | 0.21057 | 1.0208 | 122.9004 | 0.3067 | 0.19226 | 123.0698 | 0.25177 | 122.7768 | 122.7722 | -123.0698 | -0.25635 | 122.6074 | 122.7127 | 122.1954 | 122.6944
1028.0625 | 122.8088 | -122.6624 | 0.20142 | 0.026321 | 0.0051782 | 0.070226 | 0.062282 | 0.00031834 | -0.0027877 | -0.00077335 | 0.001648 | 0.035036 | 0.022704 | 0.026861 | -0.0043109 | 0.006742 | 0.0030804 | -0.40283 | 0.20142 | -122.9095 | -0.09613 | -121.9986 | -122.58 | -122.6303 | -0.036621 | 0.18768 | -0.11444 | -0.027466 | 0.09613 | -0.009155 | 0.10529 | -0.24719 | 0 | -0.29755 | 0.66376 | 0.032044 | 0.082398 | 0.27924 | 0.32959 | 122.5479 | -0.013733 | -0.22888 | 122.7585 | 122.7676 | 122.6532 | 0.21973 | 0.10529 | 0.91095 | 122.8134 | 0.21057 | 0.086975 | 123.111 | 0.30212 | 122.8638 | 122.85 | -123.111 | -0.31586 | 122.5662 | 122.6349 | 122.2595 | 122.6257
1029.75 | 122.9233 | -122.612 | 0.16937 | 0.0034333 | 0.0038966 | 0.07044 | 0.064845 | 0.0015999 | -0.0025741 | -0.0014142 | 0.0046998 | 0.035891 | 0.022063 | 0.023016 | -0.0019611 | 0.009519 | -0.0050372 | -0.39368 | 0.16937 | -122.9004 | 0.004578 | -121.907 | -122.5067 | -122.5662 | 0.086975 | 0.16479 | -0.07782 | 0.10529 | 0.21973 | 0.12817 | 0.20599 | -0.28839 | 0 | -0.16479 | 0.70496 | 0.045777 | 0.10529 | 0.33417 | 0.39368 | 122.5342 | -0.004578 | -0.064087 | 122.8317 | 122.818 | 122.7402 | 0.28381 | 0.20599 | 0.99335 | 122.905 | 0.29755 | 0.18311 | 123.0698 | 0.24261 | 122.7814 | 122.7768 | -123.0698 | -0.24719 | 122.6166 | 122.7173 | 122.2183 | 122.699
1031.5 | 122.9553 | -122.612 | 0.16479 | -0.0041962 | 0.0062464 | 0.069799 | 0.063564 | -0.00096346 | -0.0023605 | -0.00013235 | 0.001648 | 0.036532 | 0.020781 | 0.030493 | 0.00017507 | 0.0080236 | 0.0013714 | -0.4303 | 0.1831 | -122.9004 | 0.013733 | -121.8887 | -122.4976 | -122.5479 | 0.10986 | 0.17395 | -0.07782 | 0.12817 | 0.22888 | 0.14648 | 0.24719 | -0.28839 | 0.01831 | -0.15106 | 0.72327 | 0.064087 | 0.11444 | 0.35248 | 0.40283 | 122.5342 | 0.009155 | -0.036621 | 122.8409 | 122.8592 | 122.7585 | 0.32501 | 0.2243 | 1.0117 | 122.9141 | 0.3067 | 0.20599 | 123.0835 | 0.25177 | 122.7951 | 122.7859 | -123.0652 | -0.24261 | 122.6257 | 122.7402 | 122.1817 | 122.7219
1033.1875 | 122.8455 | -122.6578 | 0.16022 | 0.0034333 | 0.00646 | 0.071722 | 0.066982 | 0.0054453 | -0.0027877 | -0.00077335 | 0.001648 | 0.037386 | 0.018645 | 0.031774 | 0.0012433 | 0.006742 | -0.00055121 | -0.38452 | 0.21973 | -122.9553 | -0.073242 | -122.0123 | -122.5937 | -122.6349 | -0.004578 | 0.19684 | -0.10071 | 0.050354 | 0.13275 | 0.013733 | 0.16022 | -0.29755 | 0.05951 | -0.23346 | 0.64545 | 0.022888 | 0.064087 | 0.32043 | 0.36163 | 122.5571 | 0.036621 | -0.10986 | 122.7905 | 122.818 | 122.6715 | 0.26093 | 0.11444 | 0.94299 | 122.8821 | 0.23346 | 0.15106 | 123.175 | 0.29755 | 122.8775 | 122.8546 | -123.1155 | -0.26093 | 122.5845 | 122.7081 | 122.2733 | 122.6532
1034.9375 | 122.9141 | -122.6303 | 0.14191 | 0.011063 | 0.004751 | 0.070867 | 0.065059 | -0.0024589 | -0.0032151 | 0.00050845 | -0.0014038 | 0.034609 | 0.021636 | 0.031561 | -0.0017475 | 0.009519 | 0.0047894 | -0.4715 | 0.18768 | -122.8683 | -0.018311 | -121.9482 | -122.5204 | -122.5754 | 0.064087 | 0.16937 | -0.086975 | 0.09613 | 0.19684 | 0.11902 | 0.23804 | -0.23804 | 0.045776 | -0.16022 | 0.68207 | 0.054932 | 0.10986 | 0.29297 | 0.3479 | 122.5433 | 0.027466 | -0.045777 | 122.8271 | 122.8683 | 122.7493 | 0.32501 | 0.20599 | 0.92011 | 122.85 | 0.28381 | 0.1831 | 123.056 | 0.25635 | 122.818 | 122.7997 | -123.0103 | -0.22888 | 122.612 | 122.7264 | 122.1588 | 122.6944
1036.6875 | 122.7997 | -122.6624 | 0.19226 | 0.0034333 | 0.00646 | 0.071081 | 0.066127 | 0.0022409 | -0.0010789 | 0.00072205 | -0.0014038 | 0.0376 | 0.02249 | 0.026006 | 0.0029523 | 0.0071692 | 8.9786e-05 | -0.4715 | 0.22888 | -122.9141 | -0.12817 | -122.113 | -122.6944 | -122.7173 | -0.068665 | 0.19684 | -0.11444 | 0 | 0.045776 | -0.059509 | 0.11902 | -0.25177 | 0.036621 | -0.32044 | 0.54932 | -0.054931 | -0.032043 | 0.19684 | 0.21973 | 122.5479 | 0.004577 | -0.19226 | 122.7081 | 122.7814 | 122.6028 | 0.23346 | 0.054932 | 0.80109 | 122.7859 | 0.16022 | 0.11444 | 123.143 | 0.31128 | 122.8912 | 122.8592 | -123.1064 | -0.3067 | 122.5342 | 122.6624 | 122.1909 | 122.5937
1038.4375 | 122.8455 | -122.6486 | 0.16022 | 0.0034333 | 0.0056054 | 0.073217 | 0.065913 | 0.0065133 | -0.0015061 | 0.00050845 | 0.001648 | 0.036959 | 0.018859 | 0.027929 | 0.00060247 | 0.0097326 | -0.00097841 | -0.38452 | 0.19226 | -122.9416 | -0.045776 | -121.9666 | -122.5891 | -122.644 | 0.013733 | 0.19684 | -0.10986 | 0.045776 | 0.11902 | 0.022888 | 0.16022 | -0.29297 | 0.032044 | -0.20599 | 0.68207 | 0.004578 | 0.05951 | 0.29755 | 0.35248 | 122.5388 | 0.036621 | -0.11444 | 122.7676 | 122.8088 | 122.6715 | 0.27008 | 0.13275 | 0.97504 | 122.8958 | 0.22888 | 0.15564 | 123.1338 | 0.3067 | 122.8409 | 122.8455 | -123.1018 | -0.27008 | 122.6028 | 122.6944 | 122.2641 | 122.6624
1040.1875 | 122.937 | -122.6074 | 0.17395 | -0.0041962 | 0.0028284 | 0.071722 | 0.063777 | 0.0039499 | -0.0023605 | -0.0016278 | 0.0046998 | 0.033968 | 0.021422 | 0.03626 | 0.00060247 | 0.009519 | -0.0020464 | -0.4715 | 0.1831 | -122.905 | -0.027466 | -121.9482 | -122.5296 | -122.5662 | 0.036621 | 0.17853 | -0.09613 | 0.10071 | 0.19684 | 0.10986 | 0.22888 | -0.29755 | 0.009155 | -0.20142 | 0.65918 | 0.041199 | 0.07782 | 0.33875 | 0.37537 | 122.5113 | 0.004578 | -0.073242 | 122.8043 | 122.8363 | 122.7173 | 0.32501 | 0.20599 | 0.95673 | 122.8775 | 0.29297 | 0.19684 | 123.0881 | 0.27466 | 122.7905 | 122.7859 | -123.0789 | -0.27008 | 122.58 | 122.7081 | 122.1359 | 122.644
1041.9219 | 122.8409 | -122.644 | 0.18768 | 0.018692 | 0.0038966 | 0.070013 | 0.065486 | 0.0028817 | -0.0032151 | -0.0024824 | 0.001648 | 0.035891 | 0.020568 | 0.025579 | -0.0017475 | 0.0075964 | 0.00051699 | -0.43488 | 0.21973 | -122.9828 | -0.10986 | -122.0352 | -122.6166 | -122.6624 | -0.064087 | 0.20599 | -0.10529 | 0 | 0.11444 | -0.013733 | 0.14648 | -0.33875 | 0.032044 | -0.29755 | 0.60883 | -0.018311 | 0.027466 | 0.32043 | 0.36621 | 122.5388 | 0.018311 | -0.18768 | 122.7585 | 122.7905 | 122.6303 | 0.25177 | 0.091553 | 0.94757 | 122.8729 | 0.21973 | 0.10529 | 123.2025 | 0.31128 | 122.8638 | 122.85 | -123.1705 | -0.29297 | 122.5342 | 122.644 | 122.2092 | 122.58
1043.6562 | 122.9279 | -122.6395 | 0.15564 | 0.011063 | 0.0034692 | 0.071081 | 0.065059 | 0.00074554 | -0.0034287 | -0.0020552 | -0.0014038 | 0.033327 | 0.019072 | 0.032201 | 0.00038887 | 0.0093054 | 0.00030339 | -0.42114 | 0.17853 | -122.8912 | 0.009155 | -121.8933 | -122.4976 | -122.5479 | 0.091553 | 0.17395 | -0.064087 | 0.11444 | 0.23346 | 0.12817 | 0.21973 | -0.25177 | 0.022888 | -0.14649 | 0.74615 | 0.091552 | 0.14191 | 0.34332 | 0.39368 | 122.5754 | 0.01831 | -0.041199 | 122.8729 | 122.8592 | 122.7676 | 0.28381 | 0.19226 | 0.99792 | 122.9004 | 0.29755 | 0.17853 | 123.0698 | 0.23804 | 122.818 | 122.8134 | -123.0469 | -0.21973 | 122.6486 | 122.7539 | 122.2183 | 122.731
1045.3438 | 122.8683 | -122.6212 | 0.17853 | 0.0034333 | 0.0051782 | 0.070867 | 0.066554 | -0.00010886 | -0.0025741 | -0.0020552 | 0.001648 | 0.036104 | 0.021209 | 0.029424 | 0.0046613 | 0.0088782 | -0.001192 | -0.48523 | 0.20599 | -122.905 | -0.11444 | -122.049 | -122.6486 | -122.6669 | -0.032043 | 0.18768 | -0.10071 | 0.059509 | 0.12817 | 0.013733 | 0.16022 | -0.28381 | 0.027466 | -0.29297 | 0.5722 | -0.045776 | -0.027466 | 0.23804 | 0.25635 | 122.5204 | 0.009155 | -0.11902 | 122.7493 | 122.7814 | 122.6349 | 0.26093 | 0.11444 | 0.85602 | 122.7905 | 0.22888 | 0.16022 | 123.111 | 0.28839 | 122.8271 | 122.8088 | -123.0835 | -0.27924 | 122.5067 | 122.6807 | 122.1359 | 122.5891
1047.0938 | 122.818 | -122.6715 | 0.1831 | 0.018692 | 0.0038966 | 0.069586 | 0.064632 | 0.0022409 | -0.0059921 | -0.00034615 | 0.0046998 | 0.036745 | 0.021209 | 0.026647 | -0.0023883 | 0.008451 | 0.001585 | -0.44403 | 0.23346 | -122.9736 | -0.11902 | -122.0352 | -122.612 | -122.6578 | -0.07782 | 0.21057 | -0.15106 | -0.022888 | 0.082397 | -0.009155 | 0.12817 | -0.30212 | 0.050354 | -0.30212 | 0.63629 | 0.013733 | 0.059509 | 0.31586 | 0.36163 | 122.5204 | 0.027466 | -0.20599 | 122.7539 | 122.7997 | 122.6624 | 0.27924 | 0.14191 | 0.93842 | 122.8546 | 0.23346 | 0.12817 | 123.2071 | 0.36163 | 122.905 | 122.8821 | -123.1567 | -0.33417 | 122.5525 | 122.6486 | 122.2275 | 122.5937
1048.7656 | 122.8088 | -122.6532 | 0.19684 | 0.011063 | 0.0045374 | 0.07044 | 0.067195 | 0.0028817 | -0.0032151 | 0.002431 | 0.010803 | 0.036318 | 0.020354 | 0.023229 | -0.0026019 | 0.0073828 | 0.0030804 | -0.48523 | 0.2243 | -122.9095 | -0.1236 | -122.0398 | -122.5983 | -122.6486 | -0.086975 | 0.19226 | -0.13275 | -0.022888 | 0.07782 | -0.013733 | 0.11444 | -0.25635 | 0.027466 | -0.32043 | 0.6134 | 0.004577 | 0.054931 | 0.26093 | 0.31128 | 122.5204 | -0.004577 | -0.21973 | 122.731 | 122.7676 | 122.6395 | 0.24719 | 0.11902 | 0.86975 | 122.7859 | 0.21057 | 0.10986 | 123.1339 | 0.32501 | 122.8775 | 122.8455 | -123.1064 | -0.32959 | 122.5296 | 122.6303 | 122.168 | 122.5662
1050.5156 | 122.8729 | -122.6395 | 0.17395 | 0.018692 | 0.0036828 | 0.071508 | 0.06335 | 0.0011727 | -0.0023605 | 0.0011492 | 0.0046998 | 0.034823 | 0.021636 | 0.025579 | 0.0027387 | 0.0097326 | 0.00051699 | -0.49896 | 0.17853 | -122.8821 | -0.036621 | -121.9666 | -122.5616 | -122.612 | 0.013733 | 0.17853 | -0.10071 | 0.054932 | 0.12817 | 0.054932 | 0.18768 | -0.24262 | 0.004578 | -0.21057 | 0.67291 | 0.027465 | 0.077819 | 0.27008 | 0.32043 | 122.5388 | 0.004578 | -0.11902 | 122.7676 | 122.8271 | 122.6944 | 0.28839 | 0.15564 | 0.91553 | 122.8455 | 0.22888 | 0.15564 | 123.0606 | 0.27924 | 122.818 | 122.818 | -123.056 | -0.27466 | 122.6028 | 122.6944 | 122.1405 | 122.6532
1052.2656 | 122.8043 | -122.6669 | 0.19226 | -0.011826 | 0.0034692 | 0.069799 | 0.065059 | 0.0033089 | -0.0038559 | 0.0015764 | 0.001648 | 0.035036 | 0.021209 | 0.025152 | -0.0026019 | 0.0080236 | -0.00033761 | -0.44403 | 0.20142 | -122.9187 | -0.11444 | -122.0215 | -122.612 | -122.6486 | -0.064087 | 0.18768 | -0.11902 | -0.018311 | 0.064087 | -0.004578 | 0.09613 | -0.25177 | 0.009155 | -0.3067 | 0.64545 | 0.01831 | 0.054931 | 0.27008 | 0.3067 | 122.5479 | -0.004578 | -0.21057 | 122.731 | 122.7631 | 122.6624 | 0.21515 | 0.11444 | 0.89722 | 122.8043 | 0.18311 | 0.10071 | 123.1201 | 0.3067 | 122.8683 | 122.8546 | -123.111 | -0.31128 | 122.5525 | 122.6486 | 122.2229 | 122.6028
1054.0156 | 122.8958 | -122.6028 | 0.16479 | 0.011063 | 0.0045374 | 0.071508 | 0.07104 | 0.0058725 | -0.0010789 | 0.00029485 | -0.0014038 | 0.038027 | 0.020568 | 0.029211 | 0.0033795 | 0.0093054 | 0.0011578 | -0.50354 | 0.19684 | -122.9187 | -0.07782 | -122.0261 | -122.6257 | -122.6486 | -0.004578 | 0.16937 | -0.10529 | 0.07782 | 0.14648 | 0.059509 | 0.20599 | -0.31586 | 0.032043 | -0.24261 | 0.57678 | -0.045777 | -0.022888 | 0.27008 | 0.29297 | 122.4976 | 0.004578 | -0.086975 | 122.7493 | 122.8088 | 122.6624 | 0.31128 | 0.16479 | 0.89264 | 122.8409 | 0.25177 | 0.18311 | 123.1155 | 0.27466 | 122.7997 | 122.7722 | -123.0835 | -0.27008 | 122.525 | 122.6807 | 122.0993 | 122.5983
1055.7188 | 122.8821 | -122.6212 | 0.16479 | 0.018692 | 0.004751 | 0.072576 | 0.064418 | 0.0058725 | 0.0012711 | -0.00098695 | 0.0077514 | 0.035891 | 0.020568 | 0.030279 | -0.0017475 | 0.0088782 | 0.0024396 | -0.46234 | 0.19684 | -122.8683 | -0.018311 | -121.9299 | -122.5662 | -122.5983 | 0.059509 | 0.16479 | -0.091553 | 0.073242 | 0.16022 | 0.059509 | 0.16937 | -0.24719 | 0.032043 | -0.18311 | 0.69122 | 0.022888 | 0.054932 | 0.27008 | 0.30212 | 122.5296 | 0 | -0.091553 | 122.7814 | 122.7905 | 122.6807 | 0.26093 | 0.15106 | 0.93842 | 122.85 | 0.25177 | 0.16479 | 123.0652 | 0.25635 | 122.818 | 122.7859 | -123.0331 | -0.25635 | 122.6028 | 122.6944 | 122.1588 | 122.6807
1057.4531 | 122.8546 | -122.6395 | 0.15564 | 0.0034333 | 0.0041102 | 0.072363 | 0.066768 | 0.0013863 | -0.0023605 | -0.00098695 | 0.0046998 | 0.038668 | 0.020781 | 0.024297 | 0.0029523 | 0.010587 | -0.00076481 | -0.49896 | 0.21973 | -122.9416 | -0.10986 | -122.0444 | -122.6486 | -122.6578 | -0.032043 | 0.20142 | -0.11444 | 0.054932 | 0.10071 | 0.013733 | 0.17853 | -0.30212 | 0.064087 | -0.2655 | 0.59509 | -0.018311 | -0.009156 | 0.28381 | 0.29297 | 122.525 | 0.045776 | -0.10071 | 122.7402 | 122.818 | 122.6532 | 0.29297 | 0.12817 | 0.89722 | 122.8317 | 0.21515 | 0.16937 | 123.1613 | 0.31586 | 122.8592 | 122.8409 | -123.0972 | -0.27008 | 122.5296 | 122.6944 | 122.1405 | 122.6074
1059.2031 | 122.8455 | -122.612 | 0.17395 | 0.0034333 | 0.0043238 | 0.070867 | 0.066982 | -0.0011771 | -0.0015061 | -0.0014142 | -0.0014038 | 0.038027 | 0.022063 | 0.028784 | 0.0016705 | 0.01016 | -0.001192 | -0.49439 | 0.21057 | -122.9507 | -0.12817 | -122.0535 | -122.6395 | -122.6624 | -0.054932 | 0.16937 | -0.10986 | 0.041199 | 0.10071 | 0 | 0.15564 | -0.33875 | 0.036621 | -0.30212 | 0.55847 | -0.050354 | -0.027465 | 0.28839 | 0.31128 | 122.5021 | -0.004577 | -0.13275 | 122.7127 | 122.7676 | 122.612 | 0.2655 | 0.10986 | 0.89722 | 122.8226 | 0.21057 | 0.15106 | 123.1613 | 0.27924 | 122.8226 | 122.7814 | -123.1247 | -0.28381 | 122.4838 | 122.6532 | 122.1176 | 122.5571
1060.9531 | 122.7951 | -122.6624 | 0.19684 | -0.0041962 | 0.0041102 | 0.069158 | 0.065273 | 0.0024545 | -0.0038559 | 8.125e-05 | -0.0014038 | 0.036959 | 0.021849 | 0.032842 | -0.0019611 | 0.0090918 | 0.0035078 | -0.48065 | 0.18768 | -122.905 | -0.11902 | -122.0169 | -122.5937 | -122.6578 | -0.068665 | 0.19226 | -0.13275 | -0.032043 | 0.082397 | -0.022888 | 0.10529 | -0.24261 | -0.009155 | -0.31586 | 0.64545 | 0.004578 | 0.068665 | 0.24719 | 0.31128 | 122.5296 | -0.004577 | -0.22888 | 122.7448 | 122.7676 | 122.6395 | 0.23804 | 0.10986 | 0.88806 | 122.7859 | 0.21515 | 0.10071 | 123.0927 | 0.32501 | 122.85 | 122.8546 | -123.1018 | -0.32959 | 122.5433 | 122.6303 | 122.1817 | 122.5937
1062.7031 | 122.818 | -122.6807 | 0.19226 | 0.011063 | 0.0051782 | 0.071722 | 0.065486 | 0.0030953 | -0.0025741 | 8.125e-05 | 0.001648 | 0.036745 | 0.019927 | 0.038824 | -0.00046573 | 0.0097326 | -0.0043964 | -0.39825 | 0.20599 | -122.9095 | -0.073242 | -121.9711 | -122.5754 | -122.6349 | 0.009155 | 0.17853 | -0.11902 | 0.036621 | 0.1236 | 0.009155 | 0.15106 | -0.22888 | 0.013733 | -0.2655 | 0.70953 | 0.045776 | 0.10529 | 0.27466 | 0.33417 | 122.5616 | -0.013733 | -0.15564 | 122.8043 | 122.8317 | 122.6898 | 0.27008 | 0.12817 | 0.93842 | 122.8363 | 0.24261 | 0.15564 | 123.1155 | 0.29755 | 122.8867 | 122.8592 | -123.1018 | -0.31128 | 122.6074 | 122.7173 | 122.2824 | 122.6898
1064.3906 | 122.7905 | -122.6715 | 0.20142 | 0.011063 | 0.0032556 | 0.071081 | 0.065913 | 0.0062997 | -0.0017197 | 0.00072205 | 0.0077514 | 0.036532 | 0.02014 | 0.033697 | -0.0030291 | 0.0075964 | 0.00073059 | -0.46692 | 0.21973 | -122.9507 | -0.11902 | -122.0352 | -122.5937 | -122.6624 | -0.07782 | 0.21515 | -0.14648 | -0.018311 | 0.073242 | -0.022888 | 0.12817 | -0.27924 | 0.018311 | -0.32044 | 0.63629 | 0.009155 | 0.07782 | 0.28839 | 0.35706 | 122.525 | 0.013733 | -0.21973 | 122.7448 | 122.7997 | 122.6486 | 0.27466 | 0.1236 | 0.91553 | 122.8317 | 0.21973 | 0.12817 | 123.1705 | 0.36163 | 122.8912 | 122.8867 | -123.1522 | -0.3479 | 122.5525 | 122.6532 | 122.2046 | 122.5937
1066.1406 | 122.9187 | -122.6074 | 0.16937 | 0.011063 | 0.0049646 | 0.072363 | 0.063991 | 0.0033089 | -0.0015061 | -0.0018414 | 0.0077514 | 0.035036 | 0.021209 | 0.035833 | 0.0027387 | 0.011014 | 0.00073059 | -0.45776 | 0.17853 | -122.8867 | -0.009155 | -121.8979 | -122.5388 | -122.5662 | 0.10071 | 0.16937 | -0.10071 | 0.13733 | 0.19226 | 0.09613 | 0.24719 | -0.27924 | 0.009155 | -0.17853 | 0.70953 | 0.041199 | 0.068665 | 0.32044 | 0.3479 | 122.5067 | 0 | -0.032044 | 122.7997 | 122.8546 | 122.7036 | 0.3479 | 0.19684 | 0.98877 | 122.8775 | 0.29297 | 0.23804 | 123.0652 | 0.27008 | 122.7859 | 122.7768 | -123.056 | -0.27008 | 122.5983 | 122.7448 | 122.1497 | 122.7081
1067.8906 | 122.9141 | -122.5983 | 0.15564 | 0.011063 | 0.0060328 | 0.072149 | 0.064204 | 0.0062997 | -0.0027877 | -0.00055975 | 0.001648 | 0.036745 | 0.021849 | 0.03626 | 0.0012433 | 0.009519 | 0.00094419 | -0.45776 | 0.16479 | -122.9004 | -0.018311 | -121.9254 | -122.5388 | -122.5845 | 0.091553 | 0.14648 | -0.09613 | 0.12817 | 0.18768 | 0.091553 | 0.24261 | -0.30212 | 0.009155 | -0.17395 | 0.67291 | 0.013733 | 0.05951 | 0.31586 | 0.36163 | 122.5021 | -0.009156 | -0.027466 | 122.786 | 122.8409 | 122.6898 | 0.33874 | 0.18768 | 0.97504 | 122.8821 | 0.28381 | 0.2243 | 123.0652 | 0.24261 | 122.7631 | 122.7448 | -123.056 | -0.25177 | 122.58 | 122.7264 | 122.1405 | 122.6898
1069.5781 | 122.9141 | -122.612 | 0.17395 | 0.0034333 | 0.0058192 | 0.068304 | 0.062923 | 0.0052315 | -0.0012925 | 0.0013628 | 0.001648 | 0.034823 | 0.021209 | 0.025793 | -0.0011065 | 0.01016 | 0.001585 | -0.45776 | 0.16022 | -122.8958 | -0.004578 | -121.875 | -122.493 | -122.5388 | 0.07782 | 0.15564 | -0.091553 | 0.10071 | 0.21515 | 0.1236 | 0.21515 | -0.28381 | -0.013733 | -0.17853 | 0.737 | 0.073243 | 0.11902 | 0.35706 | 0.40283 | 122.5204 | -0.01831 | -0.073242 | 122.8271 | 122.8271 | 122.7356 | 0.3067 | 0.21515 | 1.0208 | 122.8912 | 0.3067 | 0.19226 | 123.056 | 0.24719 | 122.7722 | 122.7676 | -123.0698 | -0.2655 | 122.6074 | 122.7127 | 122.1542 | 122.6898
1071.3438 | 122.818 | -122.6532 | 0.19684 | 0.0034333 | 0.0041102 | 0.071081 | 0.065913 | 0.0060861 | -0.0047103 | -0.0012006 | 0.0046998 | 0.035677 | 0.021849 | 0.030279 | -0.0032427 | 0.006742 | 0.001585 | -0.44861 | 0.21515 | -122.9553 | -0.11444 | -122.0169 | -122.5845 | -122.6486 | -0.054932 | 0.21515 | -0.1236 | 0.018311 | 0.10529 | -0.009155 | 0.13275 | -0.30212 | 0.018311 | -0.31128 | 0.63629 | 0.004577 | 0.068664 | 0.3067 | 0.37079 | 122.5296 | 0.018311 | -0.17853 | 122.7585 | 122.7859 | 122.644 | 0.25635 | 0.11444 | 0.93841 | 122.8409 | 0.22888 | 0.14191 | 123.1705 | 0.33875 | 122.8683 | 122.8683 | -123.1522 | -0.32043 | 122.5388 | 122.6715 | 122.2046 | 122.5983
1073.0781 | 122.818 | -122.644 | 0.19684 | 0.011063 | 0.0041102 | 0.069586 | 0.066341 | 0.0060861 | -0.0023605 | -0.00013235 | 0.0046998 | 0.037386 | 0.020995 | 0.022161 | 0.0012433 | 0.0086646 | -0.00055121 | -0.42114 | 0.2243 | -122.8958 | -0.073242 | -121.9803 | -122.5891 | -122.644 | 0.004578 | 0.19684 | -0.10986 | 0.027466 | 0.10071 | -0.013733 | 0.16022 | -0.25177 | 0.027466 | -0.27008 | 0.66376 | 0 | 0.054932 | 0.25177 | 0.3067 | 122.5342 | 0 | -0.16937 | 122.7448 | 122.8043 | 122.6303 | 0.27008 | 0.09613 | 0.91553 | 122.8226 | 0.21057 | 0.13733 | 123.1201 | 0.3067 | 122.8683 | 122.8409 | -123.0927 | -0.3067 | 122.5708 | 122.6715 | 122.2229 | 122.6486
1074.8281 | 122.8363 | -122.6532 | 0.17395 | 0.0034333 | 0.0049646 | 0.068731 | 0.0657 | 0.0080087 | -0.0017197 | -0.003764 | 0.001648 | 0.036959 | 0.020354 | 0.032415 | -0.00025213 | 0.0086646 | -0.0022602 | -0.42572 | 0.20599 | -122.905 | -0.064087 | -121.9711 | -122.5662 | -122.6166 | 0.022888 | 0.19684 | -0.11444 | 0.054932 | 0.11444 | 0.004578 | 0.15106 | -0.25177 | 0.032044 | -0.23804 | 0.68207 | 0.036621 | 0.086975 | 0.28839 | 0.33875 | 122.5388 | 0.022888 | -0.11902 | 122.7676 | 122.8043 | 122.6578 | 0.2655 | 0.11902 | 0.93384 | 122.8409 | 0.22888 | 0.16937 | 123.111 | 0.31128 | 122.8592 | 122.85 | -123.0789 | -0.28839 | 122.5891 | 122.7081 | 122.2275 | 122.6761
1076.5156 | 122.9233 | -122.5983 | 0.16479 | 0.018692 | 0.0032556 | 0.070867 | 0.062923 | -0.00032266 | -0.0023605 | -0.00098695 | -0.0014038 | 0.034823 | 0.022277 | 0.029638 | -0.0013201 | 0.008451 | 0.0017988 | -0.46692 | 0.16479 | -122.8958 | 0.009155 | -121.8658 | -122.4884 | -122.525 | 0.12817 | 0.15564 | -0.086975 | 0.091553 | 0.23804 | 0.13275 | 0.23804 | -0.29755 | 0 | -0.15564 | 0.73242 | 0.073243 | 0.10986 | 0.37079 | 0.40741 | 122.5113 | -0.009155 | -0.073242 | 122.8363 | 122.8363 | 122.731 | 0.32501 | 0.21973 | 1.03 | 122.905 | 0.32501 | 0.17853 | 123.0606 | 0.24261 | 122.7631 | 122.7539 | -123.0606 | -0.25177 | 122.6074 | 122.6898 | 122.1313 | 122.7264
1078.2656 | 122.7859 | -122.6349 | 0.18768 | 0.018692 | 0.0053918 | 0.07044 | 0.0657 | 0.0022409 | -0.0025741 | -0.00034615 | 0.0046998 | 0.037386 | 0.017577 | 0.025579 | -0.0021747 | 0.0071692 | 0.0028668 | -0.47607 | 0.23804 | -122.905 | -0.11444 | -122.0306 | -122.5891 | -122.6486 | -0.07782 | 0.21057 | -0.12817 | -0.022888 | 0.054932 | -0.009155 | 0.13733 | -0.27008 | 0.050354 | -0.30212 | 0.60425 | -0.013733 | 0.045777 | 0.25635 | 0.31586 | 122.5067 | 0.022888 | -0.21057 | 122.6898 | 122.7722 | 122.6257 | 0.2655 | 0.11902 | 0.87433 | 122.7905 | 0.18311 | 0.10529 | 123.143 | 0.33875 | 122.8729 | 122.8455 | -123.0927 | -0.31586 | 122.5204 | 122.612 | 122.1588 | 122.5571
1080.0156 | 122.9233 | -122.6028 | 0.16022 | 0.0034333 | 0.0026148 | 0.069372 | 0.064204 | -0.00010886 | -0.0036423 | 0.0011492 | -0.0014038 | 0.034823 | 0.022063 | 0.026861 | -3.8532e-05 | 0.0069556 | 0.00094419 | -0.50812 | 0.16022 | -122.8867 | -0.027466 | -121.9162 | -122.4976 | -122.5433 | 0.059509 | 0.16479 | -0.09613 | 0.11444 | 0.20142 | 0.1236 | 0.2243 | -0.28381 | 0 | -0.18768 | 0.68664 | 0.059509 | 0.10529 | 0.34332 | 0.3891 | 122.5067 | 0.004578 | -0.045776 | 122.8043 | 122.8271 | 122.7264 | 0.32043 | 0.21973 | 0.97046 | 122.8592 | 0.29755 | 0.21057 | 123.0469 | 0.26092 | 122.7631 | 122.7676 | -123.0469 | -0.25635 | 122.5754 | 122.7173 | 122.0947 | 122.6624
1081.7656 | 122.9095 | -122.5983 | 0.15106 | 0.0034333 | 0.0041102 | 0.070654 | 0.065059 | 0.0080087 | -0.0019333 | 8.125e-05 | -0.0014038 | 0.035036 | 0.018431 | 0.03327 | 0.0025251 | 0.0099462 | 0.0011578 | -0.45776 | 0.14648 | -122.8455 | -0.004578 | -121.9116 | -122.5204 | -122.5754 | 0.082397 | 0.16022 | -0.07782 | 0.13275 | 0.19226 | 0.09613 | 0.23346 | -0.24719 | -0.004578 | -0.15564 | 0.68665 | 0.022889 | 0.07782 | 0.27008 | 0.32501 | 122.5204 | 0.009155 | -0.018311 | 122.7905 | 122.8317 | 122.6944 | 0.31128 | 0.17395 | 0.93384 | 122.8409 | 0.27008 | 0.21057 | 122.9919 | 0.23804 | 122.7448 | 122.7585 | -122.9965 | -0.22888 | 122.5937 | 122.731 | 122.1405 | 122.6807
1083.4375 | 122.9279 | -122.612 | 0.16022 | -0.0041962 | 0.0021876 | 0.070013 | 0.064845 | 0.00074554 | -0.0019333 | -0.00013235 | -0.0014038 | 0.035891 | 0.019927 | 0.029211 | -0.00046573 | 0.0088782 | -0.001192 | -0.48065 | 0.17853 | -122.9095 | -0.009155 | -121.8796 | -122.493 | -122.5388 | 0.11444 | 0.15106 | -0.07782 | 0.10529 | 0.2243 | 0.14648 | 0.21515 | -0.29755 | 0.018311 | -0.16937 | 0.73242 | 0.073243 | 0.11902 | 0.37079 | 0.41657 | 122.5342 | -0.009155 | -0.054931 | 122.8363 | 122.8271 | 122.7585 | 0.29297 | 0.2243 | 1.03 | 122.9004 | 0.30212 | 0.18311 | 123.0881 | 0.22888 | 122.7905 | 122.7631 | -123.0698 | -0.23804 | 122.6028 | 122.7173 | 122.1313 | 122.7264
1085.1875 | 122.8317 | -122.6532 | 0.19684 | 0.011063 | 0.0049646 | 0.072149 | 0.064632 | 0.0020273 | -0.0010789 | 0.00093565 | 0.001648 | 0.035677 | 0.022277 | 0.031988 | -0.0026019 | 0.0063148 | -0.0016192 | -0.42572 | 0.21973 | -122.937 | -0.086975 | -122.0032 | -122.5662 | -122.6303 | -0.004578 | 0.20142 | -0.11902 | 0.041199 | 0.13733 | 0.009155 | 0.16022 | -0.28381 | 0.022889 | -0.28381 | 0.65002 | 0.022888 | 0.086975 | 0.3067 | 0.37079 | 122.5342 | 0.004578 | -0.15564 | 122.7905 | 122.8134 | 122.6624 | 0.27924 | 0.12817 | 0.93384 | 122.85 | 0.25635 | 0.16022 | 123.1567 | 0.32044 | 122.8729 | 122.8546 | -123.1338 | -0.31586 | 122.5662 | 122.6944 | 122.2275 | 122.6486
1086.9219 | 122.7768 | -122.6578 | 0.19226 | 0.0034333 | 0.0041102 | 0.067877 | 0.064845 | 0.0050179 | -0.0023605 | -0.00013235 | 0.0077514 | 0.0376 | 0.019713 | 0.034551 | -0.0032427 | 0.00781 | -0.001192 | -0.53101 | 0.21515 | -122.9324 | -0.13275 | -122.0352 | -122.5891 | -122.6395 | -0.073242 | 0.2243 | -0.1236 | -0.022888 | 0.059509 | -0.013733 | 0.10529 | -0.27466 | 0.022888 | -0.32501 | 0.62256 | 0.018311 | 0.068665 | 0.29297 | 0.34332 | 122.5342 | 0.032043 | -0.21515 | 122.7173 | 122.7631 | 122.644 | 0.22888 | 0.10986 | 0.89722 | 122.7997 | 0.1831 | 0.10071 | 123.1476 | 0.3479 | 122.8729 | 122.8821 | -123.1247 | -0.31586 | 122.525 | 122.6349 | 122.1268 | 122.5845
1088.5938 | 122.7905 | -122.6624 | 0.16937 | 0.0034333 | 0.0045374 | 0.071935 | 0.0657 | 0.0011727 | -0.0034287 | -0.0016278 | 0.0046998 | 0.037813 | 0.021209 | 0.032201 | 0.0010297 | 0.009519 | 0.0017988 | -0.52643 | 0.20599 | -122.9141 | -0.13275 | -122.0718 | -122.6624 | -122.6852 | -0.082397 | 0.20142 | -0.1236 | 0 | 0.041199 | -0.036621 | 0.1236 | -0.25177 | 0.036621 | -0.30212 | 0.59052 | -0.022888 | 0 | 0.22888 | 0.25177 | 122.5388 | 0.032043 | -0.16937 | 122.7036 | 122.7859 | 122.6257 | 0.24719 | 0.086975 | 0.84229 | 122.7814 | 0.16479 | 0.1236 | 123.1201 | 0.32501 | 122.8683 | 122.8638 | -123.0835 | -0.29297 | 122.5296 | 122.6624 | 122.1359 | 122.58
1090.3438 | 122.7905 | -122.6532 | 0.20599 | -0.0041962 | 0.0058192 | 0.071508 | 0.067195 | 0.0033089 | -0.0040695 | -0.0018414 | -0.0014038 | 0.035464 | 0.022063 | 0.021734 | 0.00017507 | 0.0080236 | 0.00094419 | -0.51727 | 0.22888 | -122.9279 | -0.14191 | -122.0856 | -122.6624 | -122.6944 | -0.10071 | 0.21057 | -0.11444 | -0.004578 | 0.032043 | -0.064087 | 0.11902 | -0.27466 | 0.022888 | -0.3479 | 0.56763 | -0.041199 | -0.009156 | 0.23346 | 0.2655 | 122.5388 | 0.004577 | -0.21057 | 122.6852 | 122.7722 | 122.5891 | 0.23346 | 0.050354 | 0.84229 | 122.7859 | 0.14648 | 0.10986 | 123.1567 | 0.32501 | 122.8821 | 122.8638 | -123.1339 | -0.32044 | 122.5113 | 122.6486 | 122.1359 | 122.5525
1092.0938 | 122.9095 | -122.6166 | 0.16937 | 0.018692 | 0.0043238 | 0.073431 | 0.067622 | 0.0086495 | -0.0019333 | -0.00098695 | 0.0077514 | 0.036318 | 0.020568 | 0.036474 | 0.0014569 | 0.0099462 | 0.005003 | -0.48065 | 0.17395 | -122.8638 | 0.022888 | -121.8887 | -122.5067 | -122.5616 | 0.11444 | 0.16479 | -0.086975 | 0.11444 | 0.19684 | 0.091553 | 0.22888 | -0.24719 | 0.004577 | -0.14649 | 0.72784 | 0.054931 | 0.10986 | 0.30212 | 0.35706 | 122.5296 | -0.004578 | -0.054932 | 122.8134 | 122.8455 | 122.7081 | 0.31586 | 0.17853 | 0.97504 | 122.8867 | 0.28381 | 0.20142 | 123.0377 | 0.25177 | 122.7905 | 122.7814 | -123.0331 | -0.25635 | 122.6395 | 122.731 | 122.1359 | 122.731
1093.7812 | 122.8363 | -122.644 | 0.1831 | 0.011063 | 0.0056054 | 0.070654 | 0.066127 | 0.0041635 | -0.0053513 | -0.00013235 | 0.0077514 | 0.037813 | 0.021849 | 0.02857 | -0.00089293 | 0.0090918 | -0.0014056 | -0.44403 | 0.21515 | -122.9233 | -0.082397 | -121.9757 | -122.5479 | -122.6212 | -0.004578 | 0.20142 | -0.11444 | 0.041199 | 0.14191 | 0.032043 | 0.16937 | -0.27924 | 0.032044 | -0.2655 | 0.66833 | 0.022888 | 0.09613 | 0.30212 | 0.37537 | 122.5296 | 0.018311 | -0.14191 | 122.7859 | 122.8134 | 122.6761 | 0.28381 | 0.14648 | 0.94757 | 122.8409 | 0.25635 | 0.15564 | 123.1384 | 0.31586 | 122.8592 | 122.8455 | -123.1064 | -0.29755 | 122.5616 | 122.6852 | 122.2 | 122.6395
1095.5312 | 122.9187 | -122.6212 | 0.16022 | 0.011063 | 0.0028284 | 0.07044 | 0.061855 | 0.0024545 | -0.0034287 | -0.0018414 | 0.0046998 | 0.033327 | 0.020568 | 0.034551 | -0.00025213 | 0.0099462 | -0.0018328 | -0.54016 | 0.16937 | -122.8912 | -0.022888 | -121.9025 | -122.4976 | -122.5296 | 0.068665 | 0.15564 | -0.07782 | 0.10986 | 0.21057 | 0.11902 | 0.2243 | -0.27008 | 0.009156 | -0.1831 | 0.71869 | 0.091553 | 0.1236 | 0.36163 | 0.39368 | 122.5433 | -0.004577 | -0.050354 | 122.8317 | 122.8455 | 122.7402 | 0.30212 | 0.19684 | 0.98877 | 122.8683 | 0.28839 | 0.18768 | 123.0606 | 0.23346 | 122.7905 | 122.7768 | -123.0515 | -0.23804 | 122.5983 | 122.731 | 122.081 | 122.6898
1097.2188 | 122.7951 | -122.6349 | 0.1831 | 0.0034333 | 0.0049646 | 0.070867 | 0.064204 | -0.00096346 | -0.0025741 | -0.0012006 | 0.001648 | 0.035036 | 0.020568 | 0.034551 | -0.0040973 | 0.006742 | 0.0030804 | -0.48065 | 0.18768 | -122.9004 | -0.086975 | -121.9757 | -122.5479 | -122.6166 | -0.041199 | 0.17853 | -0.1236 | -0.009155 | 0.07782 | -0.009155 | 0.11444 | -0.2655 | 0.004578 | -0.27008 | 0.65918 | 0.018311 | 0.086975 | 0.28381 | 0.35248 | 122.5113 | -0.004577 | -0.19226 | 122.7127 | 122.7493 | 122.6257 | 0.23804 | 0.11444 | 0.92468 | 122.8134 | 0.20142 | 0.11444 | 123.0881 | 0.30212 | 122.8226 | 122.8134 | -123.0835 | -0.3067 | 122.5479 | 122.6257 | 122.1542 | 122.5937
1098.9531 | 122.9004 | -122.5891 | 0.16022 | -0.011826 | 0.004751 | 0.068945 | 0.062068 | 0.0024545 | -0.0053513 | 8.125e-05 | -0.0044556 | 0.03525 | 0.02014 | 0.03092 | -0.0023883 | 0.00781 | -0.0014056 | -0.48065 | 0.16937 | -122.8683 | 0 | -121.8842 | -122.4564 | -122.5296 | 0.09613 | 0.16022 | -0.082397 | 0.10529 | 0.20599 | 0.11902 | 0.21973 | -0.27924 | 0.009156 | -0.16022 | 0.70496 | 0.059509 | 0.13275 | 0.33875 | 0.41199 | 122.5067 | 0 | -0.054931 | 122.7951 | 122.8088 | 122.7081 | 0.30212 | 0.20142 | 0.98419 | 122.8683 | 0.28839 | 0.18768 | 123.0377 | 0.24261 | 122.7585 | 122.7493 | -123.0286 | -0.24261 | 122.5891 | 122.6944 | 122.1085 | 122.6852
1100.7031 | 122.9095 | -122.612 | 0.17395 | 0.033951 | 0.0043238 | 0.071935 | 0.0657 | 0.0037363 | -0.0010789 | -0.00034615 | 0.0046998 | 0.036745 | 0.019072 | 0.036474 | 0.0033795 | 0.0088782 | -0.00055121 | -0.48523 | 0.19684 | -122.8867 | 0 | -121.8842 | -122.5159 | -122.5525 | 0.10986 | 0.16022 | -0.082397 | 0.11444 | 0.19226 | 0.10986 | 0.21515 | -0.27466 | 0.022888 | -0.17395 | 0.72784 | 0.05951 | 0.096131 | 0.33417 | 0.37079 | 122.5296 | -0.013733 | -0.059509 | 122.8043 | 122.8271 | 122.7219 | 0.29755 | 0.19226 | 1.0025 | 122.8867 | 0.27466 | 0.19684 | 123.0835 | 0.24261 | 122.8088 | 122.7722 | -123.0606 | -0.25635 | 122.612 | 122.7264 | 122.1268 | 122.7219
1102.375 | 122.818 | -122.6212 | 0.19226 | 0.011063 | 0.004751 | 0.071722 | 0.064845 | 0.0050179 | -0.0019333 | 8.125e-05 | 0.0077514 | 0.037173 | 0.022277 | 0.021734 | -0.0030291 | 0.0088782 | -0.0020464 | -0.47607 | 0.20142 | -122.9416 | -0.10529 | -122.0123 | -122.5708 | -122.6303 | -0.050354 | 0.20599 | -0.1236 | 0.018311 | 0.10986 | 0.004578 | 0.15106 | -0.32043 | 0.009155 | -0.29755 | 0.60883 | -0.009155 | 0.050354 | 0.31128 | 0.37079 | 122.4976 | 0.013733 | -0.17395 | 122.731 | 122.7722 | 122.6257 | 0.27466 | 0.12817 | 0.92926 | 122.8363 | 0.23346 | 0.14191 | 123.143 | 0.32959 | 122.8226 | 122.8271 | -123.1338 | -0.31586 | 122.5159 | 122.6395 | 122.1451 | 122.5708
1104.125 | 122.7859 | -122.6166 | 0.19684 | -0.0041962 | 0.0032556 | 0.071508 | 0.067622 | 0.0058725 | -0.0019333 | 0.00050845 | 0.001648 | 0.037813 | 0.021209 | 0.018316 | -0.00025213 | 0.0069556 | 0.0017988 | -0.54474 | 0.21515 | -122.9095 | -0.13275 | -122.0673 | -122.6349 | -122.6715 | -0.07782 | 0.20599 | -0.13733 | -0.004578 | 0.059509 | -0.032043 | 0.11902 | -0.29297 | 0.018311 | -0.32959 | 0.54932 | -0.054932 | -0.018311 | 0.23804 | 0.27466 | 122.4792 | 0.009156 | -0.20142 | 122.6761 | 122.7356 | 122.5845 | 0.25635 | 0.10529 | 0.84229 | 122.7768 | 0.19684 | 0.13275 | 123.1247 | 0.34332 | 122.8317 | 122.8226 | -123.1064 | -0.33417 | 122.4838 | 122.612 | 122.0718 | 122.5388
1105.8906 | 122.8867 | -122.612 | 0.16937 | 0.0034333 | 0.0060328 | 0.071295 | 0.066341 | 0.00074554 | -0.0038559 | 0.0013628 | 0.001648 | 0.038668 | 0.020354 | 0.031561 | 0.0027387 | 0.01016 | -0.00033761 | -0.56305 | 0.20142 | -122.8958 | -0.086975 | -121.9849 | -122.6074 | -122.6395 | 0.009155 | 0.17853 | -0.1236 | 0.086975 | 0.15564 | 0.050354 | 0.20599 | -0.28381 | 0.032043 | -0.25635 | 0.62714 | -0.027465 | 0.004578 | 0.25635 | 0.28839 | 122.4884 | 0.009155 | -0.082398 | 122.7676 | 122.818 | 122.6624 | 0.32959 | 0.17395 | 0.91095 | 122.8088 | 0.27924 | 0.21057 | 123.0972 | 0.30212 | 122.8134 | 122.7905 | -123.0652 | -0.29297 | 122.525 | 122.699 | 122.049 | 122.6212
1107.6406 | 122.8592 | -122.5937 | 0.17853 | 0.018692 | 0.0060328 | 0.07044 | 0.064418 | 0.00074554 | -0.0012925 | 8.125e-05 | 0.0046998 | 0.034609 | 0.022704 | 0.031988 | -0.00025213 | 0.009519 | 0.001585 | -0.56305 | 0.19226 | -122.9004 | -0.059509 | -121.9528 | -122.5479 | -122.5754 | 0 | 0.1831 | -0.11902 | 0.059509 | 0.14191 | 0.050354 | 0.17853 | -0.3067 | 0.013733 | -0.23804 | 0.64087 | 0.018311 | 0.045776 | 0.32501 | 0.35248 | 122.4747 | 0.004577 | -0.11902 | 122.7356 | 122.7722 | 122.644 | 0.29755 | 0.16937 | 0.94757 | 122.8409 | 0.26093 | 0.17853 | 123.0927 | 0.30212 | 122.7859 | 122.7768 | -123.0789 | -0.29755 | 122.5342 | 122.6532 | 122.0306 | 122.5937
1109.3125 | 122.7814 | -122.6578 | 0.18768 | -0.011826 | 0.0028284 | 0.069372 | 0.065059 | 0.0013863 | -0.0021469 | -0.0022688 | 0.0077514 | 0.038454 | 0.021636 | 0.028997 | -0.0013201 | 0.0075964 | 0.00073059 | -0.54016 | 0.21057 | -122.9187 | -0.11444 | -121.9986 | -122.5891 | -122.6395 | -0.050354 | 0.21057 | -0.12817 | -0.027466 | 0.073242 | -0.013733 | 0.10071 | -0.26093 | 0.022888 | -0.30212 | 0.65918 | 0.018311 | 0.068665 | 0.27924 | 0.32959 | 122.5296 | 0.022888 | -0.21515 | 122.731 | 122.7585 | 122.644 | 0.22888 | 0.11444 | 0.9201 | 122.8043 | 0.20142 | 0.10071 | 123.1293 | 0.33875 | 122.8683 | 122.8683 | -123.1064 | -0.31586 | 122.5433 | 122.6303 | 122.1176 | 122.6074
1111.0625 | 122.8821 | -122.612 | 0.17395 | 0.011063 | 0.003042 | 0.070654 | 0.065059 | 0.0013863 | -0.0023605 | 0.0015764 | 0.001648 | 0.035891 | 0.02014 | 0.034124 | -0.00046573 | 0.0097326 | -0.0016192 | -0.57678 | 0.19226 | -122.8775 | -0.068665 | -121.9574 | -122.5388 | -122.5662 | 0.004578 | 0.1831 | -0.10071 | 0.073242 | 0.17395 | 0.082397 | 0.19684 | -0.2655 | 0.018311 | -0.24261 | 0.6546 | 0.045777 | 0.073243 | 0.31128 | 0.33875 | 122.5113 | 0.009155 | -0.10071 | 122.7859 | 122.8088 | 122.6944 | 0.29755 | 0.18311 | 0.92011 | 122.8088 | 0.27466 | 0.17395 | 123.0698 | 0.28381 | 122.8043 | 122.7951 | -123.0515 | -0.27466 | 122.5433 | 122.6852 | 122.0352 | 122.6166
1112.75 | 122.8363 | -122.6257 | 0.19684 | 0.011063 | 0.0045374 | 0.069586 | 0.0657 | 0.0024545 | -0.0044967 | -0.0014142 | 0.001648 | 0.035036 | 0.02014 | 0.031988 | -0.0028155 | 0.0090918 | 0.0026532 | -0.48523 | 0.16479 | -122.9095 | -0.022888 | -121.8979 | -122.5021 | -122.5708 | 0.027466 | 0.17395 | -0.10986 | 0.027466 | 0.13733 | 0.050354 | 0.16022 | -0.28381 | -0.032043 | -0.21973 | 0.72784 | 0.054931 | 0.1236 | 0.33875 | 0.40741 | 122.5159 | -0.022888 | -0.16937 | 122.7631 | 122.7859 | 122.6761 | 0.27008 | 0.16022 | 1.0117 | 122.8867 | 0.24719 | 0.13733 | 123.0743 | 0.28381 | 122.7905 | 122.7997 | -123.1064 | -0.3067 | 122.6028 | 122.6532 | 122.1405 | 122.6532
1114.5312 | 122.8592 | -122.6166 | 0.16022 | 0.018692 | 0.0041102 | 0.072149 | 0.064418 | 0.0037363 | -0.0027877 | -0.00034615 | 0.010803 | 0.036532 | 0.020995 | 0.029852 | 0.0010297 | 0.0093054 | 0.00073059 | -0.54016 | 0.1831 | -122.8729 | -0.009155 | -121.8979 | -122.5388 | -122.5891 | 0.07782 | 0.15564 | -0.10529 | 0.10529 | 0.16022 | 0.07782 | 0.1831 | -0.25635 | 0.022888 | -0.16937 | 0.71869 | 0.027466 | 0.07782 | 0.28381 | 0.33417 | 122.5113 | -0.004577 | -0.054931 | 122.7768 | 122.7997 | 122.6944 | 0.28839 | 0.18311 | 0.97504 | 122.8638 | 0.2655 | 0.21057 | 123.056 | 0.26093 | 122.7997 | 122.7722 | -123.0331 | -0.2655 | 122.6074 | 122.7219 | 122.0764 | 122.6944
1116.2188 | 122.8867 | -122.6028 | 0.16479 | 0.011063 | 0.0038966 | 0.068731 | 0.065273 | 0.0041635 | -0.0030015 | -0.003764 | -0.0044556 | 0.034395 | 0.021849 | 0.032201 | 0.00081607 | 0.0080236 | -0.00097841 | -0.58594 | 0.1831 | -122.8821 | -0.059509 | -121.9254 | -122.525 | -122.5754 | 0.022888 | 0.16479 | -0.10071 | 0.07782 | 0.17395 | 0.091553 | 0.21515 | -0.27924 | 0.01831 | -0.2243 | 0.67749 | 0.027466 | 0.07782 | 0.3067 | 0.35706 | 122.5021 | 0 | -0.086975 | 122.7768 | 122.818 | 122.6944 | 0.31586 | 0.19226 | 0.95673 | 122.8226 | 0.27466 | 0.17853 | 123.0652 | 0.2655 | 122.7859 | 122.7676 | -123.0469 | -0.2655 | 122.5433 | 122.6807 | 122.0169 | 122.6257
1117.9531 | 122.8638 | -122.5983 | 0.17395 | 0.011063 | 0.0056054 | 0.071935 | 0.064418 | 0.0065133 | -0.0021469 | 0.0011492 | 0.0077514 | 0.035677 | 0.020781 | 0.029852 | 0.0016705 | 0.0088782 | -0.00055121 | -0.53558 | 0.16937 | -122.85 | -0.009155 | -121.8796 | -122.5067 | -122.5479 | 0.091553 | 0.16479 | -0.082397 | 0.10986 | 0.1831 | 0.082397 | 0.20599 | -0.25177 | -0.004577 | -0.1831 | 0.71869 | 0.050354 | 0.091553 | 0.30212 | 0.34332 | 122.5159 | -0.009155 | -0.064087 | 122.7814 | 122.8043 | 122.6807 | 0.28839 | 0.16479 | 0.97046 | 122.8409 | 0.2655 | 0.19226 | 123.0194 | 0.24719 | 122.7676 | 122.7631 | -123.024 | -0.25635 | 122.5891 | 122.7081 | 122.0627 | 122.6898
1119.6875 | 122.9233 | -122.6028 | 0.17853 | 0.011063 | 0.0032556 | 0.069586 | 0.064418 | 0.0035227 | -0.0038559 | 0.00050845 | -0.0014038 | 0.034395 | 0.020568 | 0.028143 | -0.0015337 | 0.0086646 | -0.001192 | -0.48981 | 0.19684 | -122.8867 | 0 | -121.8338 | -122.4472 | -122.493 | 0.10529 | 0.15564 | -0.091553 | 0.11902 | 0.21973 | 0.12817 | 0.20599 | -0.28381 | 0.01831 | -0.17853 | 0.76904 | 0.10986 | 0.15564 | 0.39368 | 0.43945 | 122.5113 | -0.022888 | -0.059509 | 122.8226 | 122.8088 | 122.731 | 0.29755 | 0.21973 | 1.0529 | 122.8867 | 0.31128 | 0.21057 | 123.0835 | 0.24719 | 122.7997 | 122.7585 | -123.0652 | -0.27008 | 122.6028 | 122.7219 | 122.113 | 122.7081
1121.4375 | 122.7905 | -122.6257 | 0.17853 | 0.011063 | 0.0041102 | 0.070867 | 0.065059 | 0.00031834 | -0.0036423 | -0.0020552 | -0.0014038 | 0.035036 | 0.022063 | 0.026434 | -0.00089293 | 0.006742 | -0.00012381 | -0.50812 | 0.16937 | -122.9141 | -0.050354 | -121.9391 | -122.5296 | -122.5845 | -0.004578 | 0.16479 | -0.11444 | 0 | 0.10986 | 0.018311 | 0.1236 | -0.28839 | -0.009155 | -0.22888 | 0.68664 | 0.041198 | 0.09613 | 0.32959 | 0.38452 | 122.5113 | -0.013733 | -0.17853 | 122.7356 | 122.7493 | 122.644 | 0.23804 | 0.13275 | 0.97504 | 122.8638 | 0.2243 | 0.11444 | 123.0835 | 0.27924 | 122.7951 | 122.7905 | -123.0927 | -0.29297 | 122.5754 | 122.6257 | 122.1176 | 122.6212
1123.1875 | 122.7905 | -122.6212 | 0.19226 | 0.018692 | 0.004751 | 0.069799 | 0.0657 | 0.00031834 | -0.0023605 | -0.0024824 | 0.010803 | 0.036532 | 0.022277 | 0.028356 | -0.0049517 | 0.0080236 | 0.0013714 | -0.52643 | 0.22888 | -122.9095 | -0.10529 | -122.0078 | -122.5754 | -122.6395 | -0.064087 | 0.20599 | -0.1236 | -0.013733 | 0.082397 | -0.032043 | 0.11902 | -0.28839 | 0.036621 | -0.29755 | 0.6134 | -0.01831 | 0.045777 | 0.27008 | 0.33417 | 122.4976 | 0.013733 | -0.20599 | 122.7036 | 122.7402 | 122.5891 | 0.24261 | 0.091553 | 0.9018 | 122.8043 | 0.20599 | 0.10986 | 123.1384 | 0.32959 | 122.85 | 122.8271 | -123.1018 | -0.31586 | 122.5159 | 122.6074 | 122.0947 | 122.5571
1124.8594 | 122.8226 | -122.6028 | 0.19684 | 0.018692 | 0.004751 | 0.070867 | 0.064204 | 0.0048043 | -0.0032151 | 0.0022174 | 0.0077514 | 0.041445 | 0.021422 | 0.030493 | 0.0012433 | 0.0088782 | -0.0014056 | -0.51727 | 0.22888 | -122.9416 | -0.064087 | -121.962 | -122.5433 | -122.6028 | -0.009155 | 0.20142 | -0.1236 | 0.027466 | 0.11902 | 0.027466 | 0.16479 | -0.33874 | 0.032044 | -0.26093 | 0.64087 | 0 | 0.059509 | 0.33874 | 0.39825 | 122.4792 | 0.004578 | -0.16937 | 122.7219 | 122.7676 | 122.6303 | 0.28839 | 0.15106 | 0.97961 | 122.8775 | 0.24261 | 0.15106 | 123.1705 | 0.32501 | 122.8317 | 122.8043 | -123.1384 | -0.32043 | 122.5388 | 122.6303 | 122.0856 | 122.5937
1126.6094 | 122.8546 | -122.5983 | 0.1831 | 0.018692 | 0.004751 | 0.069799 | 0.065486 | 0.0026681 | -0.0049241 | -0.0014142 | 0.001648 | 0.0376 | 0.020781 | 0.034338 | 0.0029523 | 0.0097326 | -0.00033761 | -0.60883 | 0.17395 | -122.8683 | -0.054932 | -121.9437 | -122.5388 | -122.5754 | -0.004578 | 0.1831 | -0.10986 | 0.050354 | 0.14191 | 0.050354 | 0.1831 | -0.27008 | -0.009155 | -0.23804 | 0.6546 | 0.022889 | 0.05951 | 0.29297 | 0.32959 | 122.4884 | 0 | -0.13275 | 122.7402 | 122.7814 | 122.6486 | 0.29297 | 0.16022 | 0.92468 | 122.8134 | 0.25177 | 0.16022 | 123.0423 | 0.29297 | 122.7722 | 122.7814 | -123.0515 | -0.29297 | 122.5433 | 122.6486 | 121.9894 | 122.5937
1128.3594 | 122.7768 | -122.644 | 0.19684 | 0.011063 | 0.0056054 | 0.071508 | 0.067622 | 0.0039499 | -0.0017197 | 8.125e-05 | 0.001648 | 0.037813 | 0.020781 | 0.025793 | -0.0019611 | 0.0088782 | 0.0013714 | -0.50812 | 0.20142 | -122.9187 | -0.068665 | -121.962 | -122.5754 | -122.6303 | -0.013733 | 0.19226 | -0.10529 | 0.013733 | 0.082397 | -0.013733 | 0.14648 | -0.27466 | 0.004578 | -0.2655 | 0.68207 | 0.013733 | 0.068665 | 0.28839 | 0.34332 | 122.5388 | -0.004577 | -0.18311 | 122.7264 | 122.7905 | 122.6303 | 0.25177 | 0.091553 | 0.95673 | 122.85 | 0.18768 | 0.11902 | 123.1201 | 0.29755 | 122.8455 | 122.8363 | -123.1155 | -0.30212 | 122.5754 | 122.6578 | 122.1359 | 122.6303
1130.0469 | 122.8867 | -122.6028 | 0.16479 | 0.011063 | 0.0032556 | 0.070013 | 0.06335 | 0.0033089 | -0.0030015 | -0.0012006 | -0.0014038 | 0.036318 | 0.018859 | 0.032415 | -0.0013201 | 0.009519 | -0.0020464 | -0.59052 | 0.1831 | -122.8638 | -0.036621 | -121.9162 | -122.5067 | -122.5342 | 0.027466 | 0.17853 | -0.09613 | 0.10529 | 0.21057 | 0.10986 | 0.21515 | -0.26093 | 0.01831 | -0.20142 | 0.68664 | 0.068664 | 0.09613 | 0.32959 | 0.35706 | 122.5067 | 0.013733 | -0.059509 | 122.8134 | 122.818 | 122.7127 | 0.31128 | 0.20599 | 0.94757 | 122.8271 | 0.3067 | 0.20142 | 123.0469 | 0.27466 | 122.7859 | 122.7814 | -123.0286 | -0.26092 | 122.5662 | 122.7081 | 122.0123 | 122.6303
1131.7969 | 122.9095 | -122.5754 | 0.15564 | 0.0034333 | 0.0043238 | 0.071508 | 0.065059 | 0.0022409 | -0.0019333 | 8.125e-05 | 0.010803 | 0.036532 | 0.022704 | 0.034124 | 0.0048749 | 0.0099462 | 0.00094419 | -0.54932 | 0.16937 | -122.8409 | 0.009155 | -121.8887 | -122.493 | -122.5571 | 0.10986 | 0.16937 | -0.09613 | 0.13275 | 0.19226 | 0.09613 | 0.23346 | -0.2655 | 0.013733 | -0.14649 | 0.68664 | 0.01831 | 0.082397 | 0.28381 | 0.3479 | 122.4792 | 0.013733 | -0.022889 | 122.7676 | 122.8088 | 122.6715 | 0.32959 | 0.19226 | 0.95215 | 122.85 | 0.28839 | 0.22888 | 123.0103 | 0.2655 | 122.7448 | 122.7448 | -122.9965 | -0.25177 | 122.5845 | 122.7081 | 122.0261 | 122.6852
1133.5469 | 122.8867 | -122.5845 | 0.17395 | 0.018692 | 0.0043238 | 0.068945 | 0.062709 | -0.0011771 | -0.0042831 | 0.00029485 | -0.0044556 | 0.033968 | 0.019286 | 0.030279 | -0.0013201 | 0.009519 | -0.0037554 | -0.59967 | 0.1831 | -122.8958 | -0.054932 | -121.9254 | -122.5113 | -122.5571 | 0.041199 | 0.16479 | -0.10529 | 0.091553 | 0.19684 | 0.11444 | 0.20599 | -0.31128 | 0.009155 | -0.22888 | 0.65918 | 0.027466 | 0.073242 | 0.33875 | 0.38452 | 122.4792 | -0.009155 | -0.082397 | 122.7814 | 122.7905 | 122.699 | 0.31128 | 0.21973 | 0.97046 | 122.8409 | 0.30212 | 0.19684 | 123.0789 | 0.27008 | 122.7676 | 122.7493 | -123.0698 | -0.27924 | 122.5296 | 122.6761 | 121.9849 | 122.6257
1135.2344 | 122.8226 | -122.6212 | 0.1831 | 0.0034333 | 0.0066736 | 0.071935 | 0.066982 | 0.0077951 | -0.0010789 | -0.00055975 | 0.001648 | 0.038241 | 0.02014 | 0.026434 | -3.8532e-05 | 0.0080236 | 0.0013714 | -0.48981 | 0.19226 | -122.8775 | -0.054932 | -121.9437 | -122.5525 | -122.6074 | 0.032043 | 0.1831 | -0.10529 | 0.050354 | 0.1236 | 0.018311 | 0.16479 | -0.25635 | 0.009156 | -0.23804 | 0.67749 | 0.013733 | 0.068665 | 0.27008 | 0.32501 | 122.5159 | 0 | -0.13275 | 122.7448 | 122.7859 | 122.6395 | 0.27008 | 0.1236 | 0.93384 | 122.8226 | 0.22888 | 0.15564 | 123.0698 | 0.28839 | 122.8134 | 122.8043 | -123.0606 | -0.28839 | 122.5662 | 122.6715 | 122.1313 | 122.6532
1136.9844 | 122.8455 | -122.5891 | 0.16937 | 0.011063 | 0.0043238 | 0.071508 | 0.063564 | 0.00095914 | -0.0021469 | 0.00093565 | 0.001648 | 0.035036 | 0.021422 | 0.034551 | 0.00081607 | 0.0071692 | 0.003294 | -0.61798 | 0.18768 | -122.9004 | -0.054932 | -121.9345 | -122.5342 | -122.5754 | 0.009155 | 0.17853 | -0.10986 | 0.059509 | 0.14191 | 0.050354 | 0.16022 | -0.31128 | 0.01831 | -0.22431 | 0.6546 | 0.013733 | 0.054931 | 0.32501 | 0.36621 | 122.4792 | 0.009155 | -0.10986 | 122.731 | 122.7493 | 122.6395 | 0.27008 | 0.16022 | 0.96588 | 122.8455 | 0.25177 | 0.16937 | 123.0881 | 0.28839 | 122.7768 | 122.7676 | -123.0698 | -0.27924 | 122.5342 | 122.6486 | 121.9711 | 122.5983
1138.7188 | 122.8775 | -122.5754 | 0.15564 | 0.018692 | 0.0068872 | 0.070013 | 0.066768 | 0.0028817 | -0.0010789 | 0.00029485 | 0.001648 | 0.036532 | 0.023558 | 0.030493 | -3.8532e-05 | 0.0093054 | 0.00094419 | -0.55847 | 0.1831 | -122.8683 | 0.013733 | -121.8658 | -122.4976 | -122.5296 | 0.10529 | 0.17853 | -0.09613 | 0.11444 | 0.18768 | 0.091553 | 0.21515 | -0.29297 | 0.027465 | -0.14191 | 0.70953 | 0.045776 | 0.077819 | 0.33875 | 0.37079 | 122.4792 | 0.022888 | -0.041199 | 122.7631 | 122.7905 | 122.6669 | 0.31128 | 0.18768 | 1.0025 | 122.8821 | 0.28381 | 0.21057 | 123.0515 | 0.27466 | 122.7585 | 122.7539 | -123.024 | -0.25177 | 122.5891 | 122.6898 | 122.0169 | 122.6807
1140.4688 | 122.8546 | -122.5662 | 0.16937 | 0.0034333 | 0.0049646 | 0.070226 | 0.062282 | 0.0052315 | -0.0038559 | 0.0020038 | -0.0044556 | 0.037173 | 0.02014 | 0.022588 | -0.0017475 | 0.008451 | -0.0016192 | -0.51727 | 0.19684 | -122.8821 | -0.009155 | -121.8842 | -122.4747 | -122.5159 | 0.059509 | 0.16937 | -0.091553 | 0.07782 | 0.18768 | 0.091553 | 0.17395 | -0.31586 | 0.027465 | -0.17853 | 0.68207 | 0.050354 | 0.091553 | 0.36621 | 0.40741 | 122.4747 | 0 | -0.091553 | 122.7539 | 122.7402 | 122.6578 | 0.2655 | 0.18311 | 0.99792 | 122.8729 | 0.27924 | 0.16937 | 123.0789 | 0.26093 | 122.7631 | 122.7356 | -123.0515 | -0.26093 | 122.5571 | 122.644 | 122.0489 | 122.6257
1142.2188 | 122.8821 | -122.5754 | 0.15106 | 0.011063 | 0.0017602 | 0.071722 | 0.065273 | 0.0054453 | -0.0025741 | 0.00050845 | 0.0046998 | 0.034395 | 0.02014 | 0.03391 | -0.0021747 | 0.0071692 | -0.0022602 | -0.58594 | 0.1831 | -122.8775 | -0.009155 | -121.8887 | -122.4609 | -122.5159 | 0.086975 | 0.16479 | -0.07782 | 0.11902 | 0.23346 | 0.13275 | 0.23346 | -0.30212 | 0.032043 | -0.16022 | 0.68664 | 0.059509 | 0.11444 | 0.36163 | 0.41657 | 122.4976 | 0.013733 | -0.032043 | 122.8088 | 122.8088 | 122.7081 | 0.31128 | 0.21057 | 0.98877 | 122.8683 | 0.31128 | 0.19684 | 123.0606 | 0.24261 | 122.7585 | 122.7402 | -123.0286 | -0.22888 | 122.5662 | 122.6944 | 121.9894 | 122.6624
1143.9062 | 122.7631 | -122.6303 | 0.19684 | 0.0034333 | 0.0051782 | 0.072149 | 0.066982 | 0.0052315 | -0.0034287 | -0.0018414 | 0.001648 | 0.036959 | 0.022063 | 0.028997 | 0.0031659 | 0.00781 | -0.0037554 | -0.58136 | 0.20142 | -122.8958 | -0.10986 | -122.0169 | -122.6166 | -122.6715 | -0.064087 | 0.20142 | -0.11444 | -0.009155 | 0.050354 | -0.059509 | 0.10986 | -0.2655 | 0.004578 | -0.3067 | 0.6134 | -0.041199 | 0.013733 | 0.2243 | 0.27924 | 122.5159 | 0.004578 | -0.20599 | 122.6807 | 122.7402 | 122.5708 | 0.2243 | 0.054932 | 0.87891 | 122.7859 | 0.16479 | 0.10529 | 123.0972 | 0.31586 | 122.8317 | 122.8317 | -123.0927 | -0.31128 | 122.5204 | 122.6212 | 122.0489 | 122.5662
1145.6562 | 122.7997 | -122.612 | 0.17853 | 0.011063 | 0.0066736 | 0.072576 | 0.064204 | 0.0052315 | -0.0010789 | -0.00077335 | 0.0046998 | 0.0376 | 0.021209 | 0.029852 | -0.00025213 | 0.0080236 | -0.0014056 | -0.52185 | 0.21515 | -122.905 | -0.064087 | -121.9345 | -122.5433 | -122.6074 | 0.013733 | 0.18768 | -0.11444 | 0.036621 | 0.11902 | 0.018311 | 0.15564 | -0.29297 | 0.036621 | -0.24261 | 0.67749 | 0.004578 | 0.068665 | 0.29755 | 0.36163 | 122.4976 | 0.009155 | -0.14191 | 122.731 | 122.7676 | 122.6303 | 0.27008 | 0.13275 | 0.97046 | 122.8409 | 0.23346 | 0.15106 | 123.1201 | 0.30212 | 122.8271 | 122.7997 | -123.0835 | -0.29297 | 122.5479 | 122.6486 | 122.0901 | 122.6257
1147.3438 | 122.818 | -122.6212 | 0.1831 | 0.026321 | 0.0053918 | 0.072576 | 0.066341 | 0.0045907 | -0.0030015 | -0.00098695 | 0.0077514 | 0.036104 | 0.02249 | 0.029638 | 0.00081607 | 0.0097326 | -0.0033282 | -0.55847 | 0.24261 | -122.9141 | -0.091553 | -121.9711 | -122.5388 | -122.5891 | -0.009155 | 0.20599 | -0.1236 | 0.032043 | 0.11902 | 0.018311 | 0.16022 | -0.29297 | 0.05951 | -0.27466 | 0.65002 | 0.032044 | 0.082398 | 0.32501 | 0.37537 | 122.4976 | 0.022889 | -0.15106 | 122.7402 | 122.7814 | 122.6395 | 0.28381 | 0.14191 | 0.94299 | 122.8226 | 0.24261 | 0.15564 | 123.1567 | 0.32959 | 122.8638 | 122.8271 | -123.0972 | -0.3067 | 122.5296 | 122.6532 | 122.0627 | 122.612
1149.0781 | 122.8683 | -122.5845 | 0.16479 | 0.011063 | 0.0066736 | 0.073644 | 0.065059 | 0.0054453 | -0.00043789 | 0.00050845 | 0.001648 | 0.037173 | 0.019927 | 0.03327 | 0.0016705 | 0.0097326 | 0.0026532 | -0.64087 | 0.21515 | -122.8821 | -0.10986 | -121.9757 | -122.5937 | -122.6257 | 0.009155 | 0.16022 | -0.09613 | 0.091553 | 0.15106 | 0.050354 | 0.20142 | -0.29755 | 0.050354 | -0.27466 | 0.60883 | -0.041198 | -0.009155 | 0.25635 | 0.28839 | 122.4884 | -0.004578 | -0.073242 | 122.7356 | 122.7859 | 122.6349 | 0.29755 | 0.14648 | 0.90637 | 122.7722 | 0.24719 | 0.18768 | 123.0972 | 0.25635 | 122.7997 | 122.7448 | -123.0469 | -0.26092 | 122.4747 | 122.6761 | 121.9437 | 122.5937
1150.75 | 122.7676 | -122.612 | 0.19226 | -0.011826 | 0.004751 | 0.071295 | 0.064204 | 0.0030953 | -0.0030015 | -0.0022688 | 0.0046998 | 0.035677 | 0.020995 | 0.027288 | -0.0017475 | 0.00781 | 0.0037214 | -0.60425 | 0.21515 | -122.8775 | -0.11902 | -121.9849 | -122.5662 | -122.5937 | -0.045776 | 0.20599 | -0.11444 | -0.013733 | 0.09613 | -0.013733 | 0.10986 | -0.2655 | 0.022888 | -0.31128 | 0.62714 | 0.018311 | 0.045777 | 0.28381 | 0.31128 | 122.4976 | 0.013733 | -0.20599 | 122.7081 | 122.7219 | 122.5983 | 0.2243 | 0.10071 | 0.89264 | 122.7585 | 0.21057 | 0.10071 | 123.0927 | 0.32044 | 122.8271 | 122.818 | -123.0698 | -0.3067 | 122.493 | 122.5983 | 122.0078 | 122.5662
1152.5 | 122.7859 | -122.612 | 0.21515 | 0.0034333 | 0.0058192 | 0.070013 | 0.065486 | 0.0039499 | -0.0021469 | 0.0015764 | 0.001648 | 0.037813 | 0.02249 | 0.024297 | -0.0028155 | 0.0071692 | 0.0035078 | -0.57678 | 0.2243 | -122.9004 | -0.11902 | -122.0032 | -122.5708 | -122.6212 | -0.068665 | 0.21515 | -0.1236 | 0 | 0.10071 | 0 | 0.1236 | -0.28839 | 0.009155 | -0.33417 | 0.60883 | -0.009155 | 0.041199 | 0.27924 | 0.32959 | 122.4884 | 0 | -0.21515 | 122.7127 | 122.7356 | 122.612 | 0.24719 | 0.1236 | 0.89722 | 122.7814 | 0.2243 | 0.1236 | 123.1247 | 0.33875 | 122.8363 | 122.8271 | -123.1155 | -0.33875 | 122.493 | 122.612 | 122.0352 | 122.5433
1154.25 | 122.7631 | -122.4792 | 0.29755 | 0.0034333 | 0.0051782 | 0.071935 | 0.066554 | 0.0022409 | -0.0027877 | 0.00093565 | -0.0014038 | 0.24845 | 0.021209 | 0.21784 | 0.0014569 | 0.0071692 | 0.0024396 | -0.64545 | 0.32501 | -122.7539 | -0.07782 | -121.8521 | -122.4335 | -122.5021 | -0.036621 | 0.27008 | -0.082397 | 0.10529 | 0.11444 | 0.013733 | 0.16937 | -0.27466 | 0.027466 | -0.37537 | 0.62714 | -0.022888 | 0.045776 | 0.25177 | 0.32043 | 122.3969 | -0.027465 | -0.19226 | 122.5937 | 122.6486 | 122.493 | 0.25177 | 0.09613 | 0.90179 | 122.6761 | 0.19684 | 0.18768 | 123.0789 | 0.35248 | 122.8043 | 122.7493 | -123.0515 | -0.37994 | 122.4014 | 122.5845 | 121.8338 | 122.4426
1156 | 122.8088 | -122.5891 | 0.17853 | 0.0034333 | 0.0062464 | 0.070867 | 0.064845 | 0.0033089 | -0.0021469 | -0.00055975 | 0.001648 | 0.033541 | 0.021849 | 0.039037 | -0.0030291 | 0.0071692 | -0.0026874 | -0.55847 | 0.18768 | -122.8409 | -0.009155 | -121.8521 | -122.4335 | -122.5021 | 0.050354 | 0.17395 | -0.10986 | 0.045776 | 0.1831 | 0.091553 | 0.17853 | -0.25177 | 0.009155 | -0.18768 | 0.737 | 0.086975 | 0.15564 | 0.33875 | 0.40741 | 122.4792 | -0.004578 | -0.13275 | 122.7722 | 122.7676 | 122.6807 | 0.28839 | 0.20142 | 0.98877 | 122.8317 | 0.29297 | 0.15564 | 123.0286 | 0.28381 | 122.7768 | 122.7631 | -123.0194 | -0.28839 | 122.58 | 122.6349 | 122.0306 | 122.6395
1157.6875 | 122.8821 | -122.5708 | 0.16937 | 0.0034333 | 0.0034692 | 0.070867 | 0.063991 | 0.0030953 | -0.0012925 | -0.0016278 | 0.0046998 | 0.034395 | 0.020781 | 0.034551 | 0.0010297 | 0.0071692 | 0.0028668 | -0.65002 | 0.17395 | -122.8683 | -0.032043 | -121.8887 | -122.4655 | -122.525 | 0.036621 | 0.16479 | -0.082397 | 0.091553 | 0.20142 | 0.10071 | 0.21057 | -0.29755 | 0.004577 | -0.20142 | 0.68207 | 0.045777 | 0.10529 | 0.34332 | 0.40283 | 122.4884 | -0.004578 | -0.07782 | 122.7722 | 122.7814 | 122.6715 | 0.29297 | 0.18311 | 0.97961 | 122.8363 | 0.28381 | 0.17395 | 123.0423 | 0.24719 | 122.7448 | 122.7356 | -123.0377 | -0.25177 | 122.5388 | 122.6624 | 121.9208 | 122.6074
1159.4219 | 122.7356 | -122.6303 | 0.19226 | -0.0041962 | 0.0043238 | 0.06809 | 0.06335 | 0.0030953 | -0.0017197 | -0.0031232 | 0.001648 | 0.037813 | 0.020568 | 0.022375 | -0.0036701 | 0.006101 | 0.0011578 | -0.63171 | 0.18768 | -122.8867 | -0.14648 | -121.9803 | -122.5616 | -122.5983 | -0.073242 | 0.21515 | -0.12817 | -0.027466 | 0.082397 | -0.013733 | 0.10529 | -0.25635 | -0.004578 | -0.33874 | 0.65002 | 0.032043 | 0.068664 | 0.28839 | 0.32501 | 122.5021 | 0.022888 | -0.21973 | 122.7127 | 122.7356 | 122.6166 | 0.23346 | 0.11444 | 0.90637 | 122.7402 | 0.21057 | 0.10071 | 123.0743 | 0.34332 | 122.818 | 122.8455 | -123.0789 | -0.32044 | 122.4838 | 122.6028 | 121.9986 | 122.5571
1161.1719 | 122.8226 | -122.3373 | 0.36163 | 0.033951 | 0.0024012 | 0.070867 | 0.063777 | 0.0041635 | -0.0012925 | -0.00077335 | 0.0046998 | 0.39841 | 0.0195 | 0.33939 | 0.0027387 | 0.0082374 | -0.0016192 | -0.737 | 0.37994 | -122.6532 | 0.050354 | -121.6965 | -122.2092 | -122.1954 | 0.050354 | 0.27924 | -0.045776 | 0.21973 | 0.24261 | 0.16022 | 0.24719 | -0.31586 | 0.018311 | -0.31128 | 0.64087 | 0.14191 | 0.12817 | 0.45776 | 0.44403 | 122.2916 | -0.082397 | -0.14191 | 122.58 | 122.5845 | 122.4976 | 0.29297 | 0.20599 | 0.95673 | 122.7036 | 0.28839 | 0.2655 | 123.0331 | 0.32501 | 122.7173 | 122.6166 | -123.0148 | -0.40741 | 122.3877 | 122.5571 | 121.6003 | 122.3877
1162.8594 | 122.6898 | -122.3511 | 0.36621 | 0.0034333 | 0.0034692 | 0.070013 | 0.066554 | 0.0033089 | -0.0021469 | 0.0011492 | -0.0014038 | 0.38346 | 0.0195 | 0.33106 | 0.0014569 | 0.00781 | -0.0014056 | -0.68665 | 0.36163 | -122.6349 | 0.022888 | -121.7148 | -122.319 | -122.406 | -0.054932 | 0.32501 | -0.064087 | 0.1236 | 0.09613 | -0.041199 | 0.16479 | -0.28381 | -0.004578 | -0.34332 | 0.63629 | -0.054932 | 0.032043 | 0.22888 | 0.31586 | 122.287 | -0.041199 | -0.24262 | 122.4472 | 122.5159 | 122.3099 | 0.22888 | 0.022888 | 0.92011 | 122.6578 | 0.16022 | 0.18768 | 122.9965 | 0.3891 | 122.7127 | 122.6761 | -123.0011 | -0.4303 | 122.374 | 122.4747 | 121.6644 | 122.2961
1164.5938 | 122.6212 | -122.2366 | 0.42114 | 0.079727 | 0.0062464 | 0.07279 | 0.067409 | 0.0062997 | -0.00022429 | 0.00072205 | 0.016907 | 0.44327 | 0.022063 | 0.38126 | -0.0011065 | 0.0099462 | 0.0013714 | -0.59967 | 0.47607 | -122.6303 | 0.059509 | -121.6599 | -122.1542 | -122.2366 | 0.032043 | 0.38452 | -0.11444 | 0.2243 | 0.1236 | 0.068665 | 0.16022 | -0.39368 | 0.054931 | -0.36163 | 0.57678 | 0 | 0.082397 | 0.39368 | 0.47607 | 122.1222 | -0.036622 | -0.19684 | 122.3602 | 122.3969 | 122.3053 | 0.27466 | 0.18311 | 0.97046 | 122.6898 | 0.23804 | 0.33875 | 123.1064 | 0.49896 | 122.7127 | 122.6212 | -123.0515 | -0.53558 | 122.2961 | 122.4609 | 121.637 | 122.2687
1166.3438 | 122.6303 | -121.5454 | 0.92468 | 0.011063 | 0.0024012 | 0.070013 | 0.066982 | 0.0030953 | -0.0051377 | 0.002431 | 0.001648 | 1.3298 | 0.022063 | 1.1603 | 0.0014569 | 0.01016 | 0.00051699 | -0.76446 | 0.84228 | -121.875 | 0.50354 | -121.1517 | -121.6965 | -121.5271 | 0.091553 | 0.60883 | 0.036621 | 0.49896 | 0.32044 | 0.36163 | 0.3479 | -0.32959 | -0.082398 | -0.42114 | 0.39368 | 0.01831 | -0.15106 | 0.3479 | 0.17853 | 121.582 | -0.31586 | -0.42572 | 121.8658 | 121.8933 | 121.907 | 0.31128 | 0.32501 | 0.72327 | 122.3785 | 0.28381 | 0.46234 | 122.7173 | 0.5722 | 122.3877 | 122.1542 | -122.7997 | -0.88806 | 122.049 | 122.0444 | 120.7809 | 121.637
1168.0312 | 122.612 | -44.1788 | 78.154 | 0.011063 | 0.0045374 | 0.067877 | 0.060146 | 0.0052315 | -0.0019333 | -0.0018414 | 0.0046998 | 0.011324 | 0.0195 | 0.02152 | -0.0011065 | 0.011442 | -0.00076481 | -0.068665 | 78.1952 | -44.4855 | 77.948 | -44.1513 | -44.4946 | -44.4397 | -0.045776 | 0.13733 | -0.14191 | 0 | 0.10986 | 0 | 0.13275 | -0.3067 | 0.041198 | -0.20599 | 0.027466 | -0.26093 | -0.31586 | 0.045777 | -0.009155 | 44.0369 | -78.0167 | -78.154 | 44.2886 | 44.3115 | 44.1788 | 0.27466 | 0.14191 | 0.33417 | 122.4335 | 0.25177 | 0.14191 | 122.6807 | 0.27924 | 122.374 | 44.3161 | -122.6395 | -78.2959 | 122.1268 | 44.1788 | 44.1101 | 44.133
1169.7812 | 122.6532 | -3.9139 | 118.689 | -0.0041962 | 0.0068872 | 0.068517 | 0.062709 | 0.0024545 | -0.00086509 | -0.00013235 | 0.001648 | 0.012606 | 0.021422 | 0.015966 | -0.0013201 | 0.0082374 | 0.00051699 | 0.38452 | 118.7622 | -4.0833 | 118.4052 | -3.6026 | -3.8086 | -3.7628 | 0.036621 | 0.086975 | -0.16479 | 0.013733 | 0.16479 | 0.064087 | 0.15106 | -0.16937 | 0.073242 | -0.28381 | 0.31128 | 0.15106 | 0.10529 | 0.32043 | 0.27466 | 3.7491 | -118.602 | -118.6752 | 4.0787 | 4.0649 | 3.978 | 0.31586 | 0.22888 | 0.48065 | 122.4884 | 0.32959 | 0.17853 | 122.8455 | 0.25177 | 122.6761 | 4.0009 | -122.7722 | -118.8538 | 122.319 | 3.9276 | 4.2984 | 3.9505
1171.5312 | 122.6761 | -10.0204 | 112.5137 | 0.011063 | 0.004751 | 0.07044 | 0.062923 | 0.0018137 | -0.0017197 | -0.00013235 | 0.0046998 | 0.014315 | 0.022063 | 0.016821 | 0.0044477 | 0.0086646 | 0.00094419 | 0.25635 | 112.6099 | -10.2127 | 112.262 | -9.874 | -10.0891 | -10.0479 | 0.032043 | 0.082397 | -0.15564 | 0.045776 | 0.14648 | 0.022888 | 0.16479 | -0.19226 | 0.09613 | -0.25177 | 0.14649 | -0.027466 | -0.068664 | 0.16479 | 0.1236 | 9.8648 | -112.4313 | -112.468 | 10.1669 | 10.1852 | 10.0433 | 0.32044 | 0.17853 | 0.33875 | 122.4747 | 0.30212 | 0.20142 | 122.8226 | 0.23804 | 122.6303 | 10.1028 | -122.7264 | -112.6694 | 122.2824 | 10.0662 | 10.2768 | 10.0525
1173.2656 | 122.7036 | -9.7549 | 112.793 | -0.0041962 | 0.0073144 | 0.073644 | 0.064204 | 0.0033089 | -0.0017197 | -0.0012006 | -0.0014038 | 0.012179 | 0.020568 | 0.024297 | 0.0014569 | 0.0097326 | -0.00012381 | 0.20599 | 112.8937 | -9.9792 | 112.5366 | -9.5993 | -9.8236 | -9.7641 | 0.018311 | 0.10071 | -0.15106 | 0.022888 | 0.13733 | 0.041199 | 0.15564 | -0.2243 | 0.10071 | -0.25635 | 0.15564 | -0.009155 | -0.068664 | 0.21515 | 0.15564 | 9.6039 | -112.6923 | -112.7701 | 9.8923 | 9.9106 | 9.7961 | 0.3067 | 0.19226 | 0.37994 | 122.5159 | 0.28839 | 0.17395 | 122.8729 | 0.25177 | 122.6486 | 9.8557 | -122.7722 | -112.944 | 122.2916 | 9.7778 | 9.9609 | 9.7733
1175.0156 | 122.731 | -10.144 | 112.4268 | 0.0034333 | 0.0053918 | 0.069158 | 0.062923 | 0.0022409 | -0.0027877 | -0.00055975 | 0.0046998 | 0.011538 | 0.021422 | 0.0082758 | -0.0036701 | 0.0086646 | -0.0039692 | 0.21973 | 112.5046 | -10.3638 | 112.207 | -9.9472 | -10.1395 | -10.1074 | 0.036621 | 0.068665 | -0.16479 | 0.013733 | 0.17395 | 0.054932 | 0.15106 | -0.21973 | 0.07782 | -0.21973 | 0.19684 | 0.036621 | 0.004578 | 0.25635 | 0.22431 | 9.9792 | -112.3581 | -112.413 | 10.318 | 10.2951 | 10.199 | 0.31586 | 0.21973 | 0.41657 | 122.5708 | 0.33874 | 0.17853 | 122.8683 | 0.23346 | 122.6486 | 10.2127 | -122.7905 | -112.5916 | 122.3511 | 10.1578 | 10.3638 | 10.1807
1176.7656 | 122.6074 | -13.1882 | 109.4696 | 0.0034333 | 0.0066736 | 0.07044 | 0.066768 | 0.0058725 | -0.0042831 | -0.0022688 | 0.001648 | 0.014742 | 0.019927 | 0.01917 | 0.0023115 | 0.0052466 | -0.00055121 | 0.15106 | 109.5978 | -13.3804 | 109.0576 | -13.2248 | -13.4033 | -13.3347 | -0.16479 | 0.13275 | -0.19684 | -0.091553 | -0.018311 | -0.11444 | 0.054932 | -0.19226 | 0.12817 | -0.41199 | -0.036621 | -0.14649 | -0.21515 | 0.045776 | -0.022888 | 12.9913 | -109.3369 | -109.5612 | 13.1699 | 13.2431 | 13.0737 | 0.25177 | 0.082397 | 0.15564 | 122.438 | 0.17853 | 0.10529 | 122.9782 | 0.32959 | 122.7859 | 13.3209 | -122.85 | -109.6664 | 122.2458 | 13.0966 | 13.3392 | 13.0234
1178.4375 | 122.7127 | -13.4537 | 109.1537 | 0.011063 | 0.0036828 | 0.069158 | 0.064632 | 0.0030953 | -0.0015061 | 0.0030718 | 0.001648 | 0.011751 | 0.019927 | 0.014044 | -0.00046573 | 0.01016 | -0.0026874 | 0.10986 | 109.2911 | -13.6459 | 108.8425 | -13.4033 | -13.5956 | -13.5361 | -0.082397 | 0.10529 | -0.17853 | -0.022888 | 0.091553 | -0.004578 | 0.10986 | -0.19226 | 0.13733 | -0.31128 | 0.050354 | -0.082398 | -0.14191 | 0.10986 | 0.050354 | 13.2751 | -109.0485 | -109.1766 | 13.5452 | 13.5635 | 13.4491 | 0.28839 | 0.17395 | 0.24261 | 122.4884 | 0.27008 | 0.15564 | 122.937 | 0.28381 | 122.7448 | 13.559 | -122.7997 | -109.3323 | 122.2961 | 13.4308 | 13.5635 | 13.3713
1180.1719 | 122.699 | -11.3342 | 111.2869 | -0.0041962 | 0.0045374 | 0.07044 | 0.063777 | 0.0043771 | -0.0012925 | -0.0014142 | 0.0046998 | 0.014315 | 0.021636 | 0.015753 | -0.0011065 | 0.0097326 | 0.0026532 | 0.14191 | 111.4014 | -11.5082 | 110.9848 | -11.2289 | -11.4304 | -11.3892 | -0.073242 | 0.082397 | -0.16022 | -0.027466 | 0.068665 | -0.004578 | 0.10071 | -0.17395 | 0.11444 | -0.30212 | 0.10529 | -0.054931 | -0.09613 | 0.11902 | 0.07782 | 11.174 | -111.2045 | -111.3144 | 11.4029 | 11.4349 | 11.3297 | 0.26093 | 0.15564 | 0.27924 | 122.493 | 0.22888 | 0.13275 | 122.9095 | 0.24261 | 122.7356 | 11.4166 | -122.7951 | -111.4471 | 122.319 | 11.3068 | 11.4761 | 11.261
1181.9219 | 122.6395 | -11.1053 | 111.5799 | 0.011063 | 0.0062464 | 0.069372 | 0.066341 | 0.0037363 | -0.0036423 | 8.125e-05 | -0.0014038 | 0.012392 | 0.021422 | 0.012335 | -0.0026019 | 0.0073828 | 0.0028668 | 0.21057 | 111.6669 | -11.2747 | 111.2549 | -10.9497 | -11.1145 | -11.1008 | -0.086975 | 0.1236 | -0.18768 | -0.086975 | 0.041199 | -0.064087 | 0.059509 | -0.16937 | 0.086975 | -0.32501 | 0.15564 | 0.004578 | -0.009155 | 0.17395 | 0.16022 | 10.9177 | -111.4563 | -111.6669 | 11.1465 | 11.1649 | 11.0413 | 0.24719 | 0.1236 | 0.32501 | 122.5296 | 0.22888 | 0.10071 | 122.9416 | 0.31128 | 122.7722 | 11.2289 | -122.8546 | -111.7676 | 122.3602 | 11.0184 | 11.3159 | 11.0184
1183.6719 | 122.6852 | -11.4304 | 111.2228 | 0.0034333 | 0.0066736 | 0.069586 | 0.068691 | 0.0067269 | -0.0025741 | 0.0011492 | 0.0046998 | 0.01346 | 0.0195 | 0.01148 | 0.0012433 | 0.0073828 | -0.0033282 | 0.21515 | 111.3693 | -11.618 | 110.907 | -11.3205 | -11.5128 | -11.4853 | -0.054932 | 0.10071 | -0.17853 | -0.018311 | 0.059509 | -0.032043 | 0.082397 | -0.18768 | 0.14649 | -0.31586 | 0.10986 | -0.054932 | -0.082397 | 0.13275 | 0.10529 | 11.2518 | -111.1221 | -111.2411 | 11.4899 | 11.5128 | 11.3983 | 0.26092 | 0.14648 | 0.29755 | 122.525 | 0.23804 | 0.16022 | 122.9874 | 0.27924 | 122.7997 | 11.5311 | -122.8409 | -111.4014 | 122.3373 | 11.412 | 11.6455 | 11.3754
1185.3594 | 122.7676 | -11.3983 | 111.1862 | 0.0034333 | 0.0032556 | 0.070867 | 0.0657 | 0.0043771 | -0.0023605 | -0.0029096 | 0.0046998 | 0.013888 | 0.021849 | 0.02152 | 0.0031659 | 0.0080236 | 0.001585 | 0.16937 | 111.3327 | -11.6135 | 110.9344 | -11.2976 | -11.5036 | -11.4532 | 0 | 0.10071 | -0.16479 | 0.041199 | 0.14648 | 0.027466 | 0.15564 | -0.21515 | 0.14648 | -0.25177 | 0.10071 | -0.054932 | -0.10529 | 0.16022 | 0.10986 | 11.2335 | -111.0855 | -111.145 | 11.5448 | 11.554 | 11.4258 | 0.32044 | 0.19226 | 0.31586 | 122.5479 | 0.31128 | 0.20599 | 122.9462 | 0.2655 | 122.731 | 11.499 | -122.7997 | -111.351 | 122.3328 | 11.4395 | 11.5677 | 11.3983
1187.1094 | 122.7036 | -11.0916 | 111.5616 | -0.0041962 | 0.00646 | 0.068945 | 0.065913 | 0.0071541 | -0.0025741 | -0.00013235 | 0.001648 | 0.01346 | 0.020781 | 0.019598 | -0.0026019 | 0.0088782 | -0.0031146 | 0.21057 | 111.6898 | -11.3205 | 111.2091 | -11.0138 | -11.174 | -11.1557 | -0.073242 | 0.10071 | -0.18768 | -0.045776 | 0.064087 | -0.059509 | 0.09613 | -0.22888 | 0.12817 | -0.35248 | 0.07782 | -0.064087 | -0.082397 | 0.16479 | 0.14649 | 10.9039 | -111.4609 | -111.6074 | 11.1557 | 11.1877 | 11.0321 | 0.28381 | 0.12817 | 0.3067 | 122.5296 | 0.25177 | 0.14191 | 123.0103 | 0.28839 | 122.7814 | 11.1923 | -122.8821 | -111.7493 | 122.3007 | 11.0458 | 11.3022 | 11.0184
1188.8594 | 122.7219 | -8.1894 | 114.4638 | -0.0041962 | 0.0056054 | 0.070226 | 0.065913 | 0.0045907 | 0.00041651 | 0.00029485 | 0.001648 | 0.013247 | 0.022277 | 0.016393 | 0.0020979 | 0.0093054 | -0.001192 | 0.15106 | 114.6515 | -8.4045 | 114.1022 | -8.1024 | -8.2855 | -8.226 | -0.09613 | 0.10986 | -0.17853 | -0.032043 | 0.050354 | -0.050354 | 0.10529 | -0.21515 | 0.18768 | -0.36163 | 0.086975 | -0.036621 | -0.09613 | 0.17853 | 0.11902 | 8.0109 | -114.3539 | -114.4958 | 8.2397 | 8.2947 | 8.139 | 0.28381 | 0.12817 | 0.30212 | 122.5067 | 0.22888 | 0.14648 | 123.056 | 0.28839 | 122.8409 | 8.2993 | -122.8683 | -114.6423 | 122.2916 | 8.1573 | 8.3405 | 8.0933
1190.6094 | 122.6715 | -7.8094 | 114.8804 | 0.0034333 | 0.0088098 | 0.069372 | 0.066982 | 0.0043771 | -0.00065149 | 0.00050845 | 0.001648 | 0.01581 | 0.021422 | 0.012548 | -0.0017475 | 0.0080236 | -0.00076481 | 0.23346 | 115.0406 | -7.9742 | 114.5416 | -7.6401 | -7.8415 | -7.782 | -0.07782 | 0.11444 | -0.18768 | -0.036621 | 0.041199 | -0.082397 | 0.068665 | -0.1648 | 0.16022 | -0.33875 | 0.16937 | 0.027466 | -0.032044 | 0.19226 | 0.13275 | 7.6218 | -114.7659 | -114.917 | 7.8506 | 7.8781 | 7.7271 | 0.25635 | 0.10529 | 0.33417 | 122.5159 | 0.22888 | 0.15106 | 123.0148 | 0.30212 | 122.85 | 7.9239 | -122.8546 | -115.0681 | 122.3511 | 7.7728 | 8.0429 | 7.7316
1192.3594 | 122.6944 | -8.2718 | 114.4363 | 0.011063 | 0.0062464 | 0.067449 | 0.066341 | 0.0030953 | -0.0040695 | -0.0046186 | 0.0046998 | 0.01346 | 0.022917 | 0.011053 | -0.00046573 | 0.00781 | -0.00055121 | 0.17395 | 114.5691 | -8.4503 | 114.0427 | -8.1436 | -8.3084 | -8.2718 | -0.1236 | 0.1236 | -0.17853 | -0.059509 | 0.050354 | -0.050354 | 0.082397 | -0.17853 | 0.13275 | -0.39368 | 0.12817 | 0 | -0.036621 | 0.17853 | 0.14191 | 8.0933 | -114.3127 | -114.4958 | 8.3221 | 8.3542 | 8.2214 | 0.26092 | 0.12817 | 0.3067 | 122.493 | 0.22888 | 0.11902 | 123.0194 | 0.30212 | 122.8409 | 8.3954 | -122.8867 | -114.6149 | 122.3145 | 8.2123 | 8.4457 | 8.1482
1194.0469 | 122.7631 | -8.1161 | 114.537 | 0.018692 | 0.0053918 | 0.07044 | 0.060787 | 0.0039499 | -0.0015061 | 0.00050845 | 0.0046998 | 0.012179 | 0.021849 | 0.01853 | -0.0013201 | 0.0080236 | -0.00076481 | 0.11444 | 114.6469 | -8.313 | 114.1983 | -7.9605 | -8.1161 | -8.0887 | -0.064087 | 0.091553 | -0.17395 | 0 | 0.1236 | 0.032043 | 0.13275 | -0.19684 | 0.10986 | -0.33875 | 0.15564 | 0.027466 | 0 | 0.2243 | 0.19684 | 7.9422 | -114.4455 | -114.537 | 8.2397 | 8.2489 | 8.1482 | 0.3067 | 0.20599 | 0.35248 | 122.5113 | 0.29755 | 0.17395 | 122.9599 | 0.2655 | 122.7631 | 8.2077 | -122.85 | -114.711 | 122.3145 | 8.1161 | 8.2306 | 8.0521
1195.7969 | 122.7264 | -8.3176 | 114.3631 | 0.0034333 | 0.0043238 | 0.069158 | 0.062282 | 0.00095914 | -0.0038559 | -0.0024824 | 0.0046998 | 0.011751 | 0.021849 | 0.021948 | -0.0023883 | 0.0073828 | 0.00030339 | 0.21973 | 114.4547 | -8.4961 | 114.0884 | -8.0933 | -8.2764 | -8.2581 | -0.009155 | 0.082397 | -0.17853 | -0.027466 | 0.10529 | 0.018311 | 0.11902 | -0.17853 | 0.091553 | -0.27466 | 0.2243 | 0.059509 | 0.041199 | 0.23804 | 0.21973 | 8.139 | -114.2807 | -114.3906 | 8.4229 | 8.4366 | 8.3359 | 0.29755 | 0.19684 | 0.40283 | 122.5845 | 0.28381 | 0.15106 | 122.9507 | 0.26092 | 122.7722 | 8.4 | -122.8592 | -114.5416 | 122.406 | 8.2901 | 8.5373 | 8.3084
1197.5 | 122.7859 | -8.2901 | 114.3539 | 0.0034333 | 0.004751 | 0.067449 | 0.062709 | 0.0039499 | -0.0051377 | 0.0015764 | 0.0046998 | 0.011538 | 0.020568 | 0.016821 | 0.00081607 | 0.0065284 | 0.0026532 | 0.21515 | 114.4592 | -8.4824 | 114.0747 | -8.0795 | -8.2626 | -8.2535 | 0.036621 | 0.082397 | -0.14648 | 0.022888 | 0.16022 | 0.064087 | 0.14191 | -0.19226 | 0.10529 | -0.27924 | 0.21057 | 0.036621 | 0.027466 | 0.22888 | 0.21973 | 8.1436 | -114.2715 | -114.3311 | 8.4503 | 8.432 | 8.3542 | 0.28839 | 0.21057 | 0.40283 | 122.5571 | 0.3067 | 0.16937 | 122.9416 | 0.22888 | 122.7493 | 8.3725 | -122.8363 | -114.5004 | 122.3648 | 8.313 | 8.5052 | 8.3267
1199.2656 | 122.7951 | -8.5327 | 114.1251 | 0.0034333 | 0.004751 | 0.069372 | 0.062496 | 0.0033089 | -0.0025741 | 0.0011492 | -0.0014038 | 0.012392 | 0.021422 | 0.017248 | 0.0018841 | 0.0088782 | 8.9786e-05 | 0.14648 | 114.2487 | -8.7158 | 113.8275 | -8.3588 | -8.5236 | -8.4732 | -0.018311 | 0.10986 | -0.1831 | 0.009155 | 0.14648 | 0.041199 | 0.15106 | -0.18311 | 0.1236 | -0.29755 | 0.17395 | 0.059509 | 0.009155 | 0.24261 | 0.19226 | 8.3496 | -114.0152 | -114.1159 | 8.6792 | 8.6838 | 8.5739 | 0.33417 | 0.2243 | 0.35706 | 122.5433 | 0.32959 | 0.19226 | 122.9645 | 0.29297 | 122.7814 | 8.6426 | -122.8409 | -114.3082 | 122.3602 | 8.5419 | 8.6792 | 8.5144
1201.0156 | 122.7768 | -8.3496 | 114.2761 | -0.0041962 | 0.0036828 | 0.071295 | 0.066341 | 0.0041635 | -0.0027877 | 0.00072205 | 0.0077514 | 0.013674 | 0.02249 | 0.018316 | 0.0029523 | 0.009519 | -0.0014056 | 0.13733 | 114.4592 | -8.5419 | 113.974 | -8.2306 | -8.4091 | -8.3633 | -0.027466 | 0.091553 | -0.16022 | 0.009155 | 0.11444 | 0.009155 | 0.12817 | -0.19226 | 0.18311 | -0.30212 | 0.11902 | -0.013733 | -0.05951 | 0.17853 | 0.13275 | 8.1894 | -114.1846 | -114.267 | 8.464 | 8.4778 | 8.3588 | 0.28839 | 0.16937 | 0.31128 | 122.5159 | 0.27466 | 0.16937 | 123.0011 | 0.25177 | 122.8088 | 8.4412 | -122.818 | -114.4363 | 122.3236 | 8.3588 | 8.4869 | 8.3221
1202.7031 | 122.7036 | -8.1207 | 114.5828 | -0.0041962 | 0.0068872 | 0.06809 | 0.067836 | -0.00010886 | -0.0040695 | -0.00013235 | 0.0046998 | 0.014529 | 0.020568 | 0.021093 | -0.0013201 | 0.006742 | -0.002901 | 0.23804 | 114.7293 | -8.2947 | 114.212 | -7.9605 | -8.1482 | -8.1253 | -0.054932 | 0.1236 | -0.1831 | -0.032043 | 0.059509 | -0.045776 | 0.091553 | -0.17395 | 0.14648 | -0.37079 | 0.16022 | -0.004577 | -0.027465 | 0.16937 | 0.14649 | 7.9376 | -114.4592 | -114.6149 | 8.1802 | 8.2123 | 8.075 | 0.27466 | 0.13733 | 0.33417 | 122.5067 | 0.24261 | 0.15106 | 123.024 | 0.3067 | 122.85 | 8.2443 | -122.8775 | -114.7659 | 122.3328 | 8.0887 | 8.3588 | 8.0658
1204.4531 | 122.7859 | -8.02 | 114.6332 | 0.011063 | 0.0034692 | 0.072363 | 0.063136 | 0.0018137 | -0.0019333 | -0.00034615 | 0.001648 | 0.01282 | 0.018004 | 0.020452 | -0.0028155 | 0.00781 | 0.0028668 | 0.1236 | 114.798 | -8.2123 | 114.3219 | -7.8552 | -8.0383 | -7.988 | -0.045776 | 0.10071 | -0.17853 | 0.009155 | 0.11902 | 0.036621 | 0.14191 | -0.19226 | 0.16479 | -0.31128 | 0.1648 | 0.032044 | -0.01831 | 0.2243 | 0.17395 | 7.8415 | -114.5325 | -114.624 | 8.139 | 8.1619 | 8.0566 | 0.32044 | 0.21515 | 0.35705 | 122.5342 | 0.29755 | 0.18768 | 123.0103 | 0.27924 | 122.818 | 8.1207 | -122.8455 | -114.8117 | 122.3419 | 8.0292 | 8.1436 | 7.9742
1206.1875 | 122.8134 | -8.0978 | 114.537 | 0.0034333 | 0.0041102 | 0.068517 | 0.064204 | 0.0030953 | -0.0038559 | -0.00098695 | -0.0014038 | 0.013888 | 0.020781 | 0.014898 | -3.8532e-05 | 0.0093054 | -0.00033761 | 0.19684 | 114.6744 | -8.2809 | 114.3082 | -7.8644 | -8.0658 | -8.0246 | 0.022888 | 0.091553 | -0.14648 | 0.022888 | 0.16022 | 0.059509 | 0.14191 | -0.18311 | 0.13733 | -0.22888 | 0.23346 | 0.073242 | 0.032043 | 0.25635 | 0.21515 | 7.9514 | -114.4455 | -114.5142 | 8.2581 | 8.2397 | 8.1573 | 0.28839 | 0.20599 | 0.41656 | 122.5891 | 0.3067 | 0.16937 | 122.9553 | 0.23804 | 122.7722 | 8.1894 | -122.818 | -114.6835 | 122.406 | 8.1207 | 8.2947 | 8.1207
1207.875 | 122.7219 | -9.3155 | 113.3652 | -0.0041962 | 0.0024012 | 0.068517 | 0.066768 | 0.0024545 | -0.0032151 | -0.00034615 | 0.010803 | 0.01581 | 0.020781 | 0.02387 | -0.00025213 | 0.0075964 | 0.00073059 | 0.17395 | 113.475 | -9.4849 | 113.031 | -9.1827 | -9.3246 | -9.3246 | -0.054932 | 0.10071 | -0.17853 | -0.07782 | 0.050354 | -0.041199 | 0.068665 | -0.16937 | 0.10986 | -0.33417 | 0.13275 | -0.009155 | -0.009155 | 0.16022 | 0.16022 | 9.137 | -113.2645 | -113.443 | 9.3658 | 9.3842 | 9.2743 | 0.24719 | 0.13733 | 0.30212 | 122.5159 | 0.22888 | 0.10071 | 122.9599 | 0.27924 | 122.7905 | 9.4162 | -122.85 | -113.5437 | 122.3465 | 9.2377 | 9.4894 | 9.2606
1209.625 | 122.7356 | -8.1207 | 114.5187 | 0.0034333 | 0.0051782 | 0.068731 | 0.065273 | 0.0028817 | -0.0012925 | -0.00034615 | -0.0014038 | 0.013033 | 0.02249 | 0.014257 | 0.0012433 | 0.01016 | 0.001585 | 0.14191 | 114.6469 | -8.3038 | 114.212 | -7.9788 | -8.1573 | -8.0887 | -0.064087 | 0.09613 | -0.17853 | -0.022888 | 0.064087 | -0.027466 | 0.10529 | -0.1831 | 0.12817 | -0.3067 | 0.14191 | 0.032044 | -0.036621 | 0.21515 | 0.14648 | 7.9422 | -114.4226 | -114.5416 | 8.1848 | 8.226 | 8.0933 | 0.28381 | 0.15106 | 0.32501 | 122.5159 | 0.24261 | 0.15564 | 122.9507 | 0.27466 | 122.7676 | 8.2169 | -122.8226 | -114.6973 | 122.3328 | 8.0978 | 8.2626 | 8.0566
1211.3125 | 122.7081 | -8.4641 | 114.267 | 0.018692 | 0.0062464 | 0.070013 | 0.068263 | 0.0054453 | -0.0038559 | -0.00013235 | 0.0046998 | 0.014742 | 0.022277 | 0.015753 | 0.00060247 | 0.0080236 | 0.00094419 | 0.20142 | 114.3997 | -8.6151 | 113.9145 | -8.2901 | -8.4641 | -8.4549 | -0.045776 | 0.12817 | -0.1831 | -0.041199 | 0.045776 | -0.068665 | 0.073242 | -0.15106 | 0.13275 | -0.35248 | 0.17395 | 0.009155 | 0 | 0.16022 | 0.15106 | 8.2809 | -114.1388 | -114.3082 | 8.5098 | 8.5373 | 8.3954 | 0.25635 | 0.11444 | 0.32501 | 122.5296 | 0.22888 | 0.14191 | 123.0148 | 0.31128 | 122.8638 | 8.5922 | -122.8821 | -114.4501 | 122.3785 | 8.4229 | 8.6655 | 8.4183
1213.0625 | 122.7493 | -8.5236 | 114.1571 | 0.011063 | 0.0085962 | 0.071081 | 0.065273 | 0.00095914 | -0.0034287 | 0.0015764 | 0.001648 | 0.011538 | 0.020354 | 0.011907 | 0.0010297 | 0.01016 | 0.0045758 | 0.12817 | 114.3173 | -8.6884 | 113.8046 | -8.3908 | -8.5785 | -8.5098 | -0.082397 | 0.091553 | -0.17395 | -0.027466 | 0.064087 | -0.022888 | 0.091553 | -0.16479 | 0.16022 | -0.35248 | 0.13275 | 0.013733 | -0.054931 | 0.17853 | 0.10986 | 8.3496 | -114.0656 | -114.1846 | 8.5876 | 8.6151 | 8.5007 | 0.2655 | 0.15106 | 0.29755 | 122.493 | 0.23804 | 0.14648 | 123.0057 | 0.2655 | 122.8409 | 8.6151 | -122.8455 | -114.3311 | 122.3282 | 8.4961 | 8.6517 | 8.4412
1214.7969 | 122.7539 | -9.407 | 113.2736 | 0.011063 | 0.0043238 | 0.069372 | 0.066768 | 0.0052315 | -0.0027877 | 0.00050845 | 0.001648 | 0.011324 | 0.020995 | 0.025366 | 0.0012433 | 0.0086646 | 0.001585 | 0.16022 | 113.3789 | -9.613 | 112.8937 | -9.3018 | -9.4803 | -9.4528 | -0.059509 | 0.091553 | -0.16022 | -0.018311 | 0.073242 | -0.018311 | 0.091553 | -0.20599 | 0.10528 | -0.37994 | 0.10529 | -0.045777 | -0.073243 | 0.16022 | 0.13275 | 9.2468 | -113.1821 | -113.2919 | 9.4803 | 9.4986 | 9.3887 | 0.25177 | 0.14191 | 0.31128 | 122.5067 | 0.23346 | 0.14191 | 122.9919 | 0.25177 | 122.7859 | 9.4986 | -122.8867 | -113.4338 | 122.3007 | 9.3887 | 9.5673 | 9.3475
1216.5 | 122.6852 | -8.7662 | 113.9557 | 0.011063 | 0.00646 | 0.068304 | 0.066341 | 0.0030953 | -0.0036423 | -0.0022688 | 0.0046998 | 0.015169 | 0.021636 | 0.014471 | -0.0030291 | 0.0080236 | -0.00055121 | 0.19226 | 114.1159 | -8.9539 | 113.5437 | -8.6655 | -8.8165 | -8.7708 | -0.16022 | 0.12817 | -0.21057 | -0.091553 | 0.004578 | -0.10071 | 0.041199 | -0.18768 | 0.16022 | -0.41199 | 0.10071 | -0.004578 | -0.050354 | 0.1831 | 0.13733 | 8.5556 | -113.8275 | -114.0472 | 8.7708 | 8.8074 | 8.6655 | 0.25177 | 0.10986 | 0.28839 | 122.4976 | 0.21515 | 0.11902 | 123.0698 | 0.33875 | 122.8821 | 8.8943 | -122.9095 | -114.1663 | 122.3099 | 8.6746 | 8.9584 | 8.606
1218.25 | 122.6669 | -8.6609 | 114.0747 | 0.0034333 | 0.0073144 | 0.07044 | 0.064845 | 0.0035227 | -0.00022429 | 0.00072205 | 0.0077514 | 0.014529 | 0.022063 | 0.019598 | 0.00060247 | 0.0075964 | 0.00073059 | 0.25177 | 114.1983 | -8.8303 | 113.6948 | -8.5007 | -8.6792 | -8.6655 | -0.050354 | 0.13275 | -0.16479 | -0.036621 | 0.068665 | -0.045776 | 0.091553 | -0.16937 | 0.1236 | -0.37994 | 0.16022 | -0.004577 | -0.01831 | 0.16479 | 0.15106 | 8.4961 | -113.942 | -114.1113 | 8.7296 | 8.7524 | 8.6151 | 0.25635 | 0.11902 | 0.32959 | 122.525 | 0.23346 | 0.12817 | 123.0286 | 0.29755 | 122.8592 | 8.7936 | -122.905 | -114.2395 | 122.3557 | 8.6243 | 8.9127 | 8.6105
1220 | 122.7631 | -8.5419 | 114.1571 | 0.011063 | 0.0041102 | 0.071722 | 0.065273 | 0.0013863 | -0.0036423 | 0.00072205 | 0.0046998 | 0.01282 | 0.020781 | 0.017462 | -3.8532e-05 | 0.0090918 | 0.0041486 | 0.12817 | 114.2761 | -8.7296 | 113.7909 | -8.3862 | -8.5785 | -8.519 | -0.054932 | 0.086975 | -0.19684 | -0.013733 | 0.10986 | 0.013733 | 0.1236 | -0.18768 | 0.11902 | -0.36621 | 0.15564 | 0.022888 | -0.036621 | 0.21057 | 0.15106 | 8.345 | -114.0701 | -114.1708 | 8.6517 | 8.6655 | 8.5556 | 0.32043 | 0.21057 | 0.34332 | 122.5204 | 0.3067 | 0.18311 | 123.0057 | 0.28381 | 122.818 | 8.6288 | -122.8867 | -114.3539 | 122.3328 | 8.5281 | 8.67 | 8.4869
1221.7656 | 122.6395 | -8.5098 | 114.2624 | 0.011063 | 0.00646 | 0.068731 | 0.066127 | 0.00053194 | -0.0038559 | -0.00013235 | 0.0077514 | 0.015169 | 0.022277 | 0.01618 | -0.0028155 | 0.0071692 | -0.0058918 | 0.16022 | 114.3814 | -8.6746 | 113.8229 | -8.3908 | -8.5464 | -8.4915 | -0.14191 | 0.13275 | -0.20142 | -0.11902 | 0.009155 | -0.091553 | 0.036621 | -0.16479 | 0.11902 | -0.43945 | 0.11902 | 0.018311 | -0.036621 | 0.18311 | 0.12817 | 8.3084 | -114.1296 | -114.3814 | 8.519 | 8.5464 | 8.4183 | 0.23804 | 0.10986 | 0.28381 | 122.4976 | 0.21057 | 0.082397 | 123.056 | 0.33417 | 122.8912 | 8.6426 | -122.937 | -114.4638 | 122.3328 | 8.3908 | 8.67 | 8.3679
1223.4531 | 122.7036 | -8.6334 | 114.0747 | -0.0041962 | 0.0058192 | 0.069586 | 0.065913 | 0.0048043 | -0.0019333 | 0.0022174 | 0.0077514 | 0.015383 | 0.021422 | 0.016607 | -0.00025213 | 0.0071692 | -0.0014056 | 0.21515 | 114.2349 | -8.8257 | 113.7085 | -8.4915 | -8.67 | -8.6472 | -0.045776 | 0.10986 | -0.17395 | -0.036621 | 0.054932 | -0.027466 | 0.091553 | -0.19226 | 0.16022 | -0.36621 | 0.14191 | -0.013733 | -0.036621 | 0.17853 | 0.15564 | 8.4595 | -113.9648 | -114.1113 | 8.6884 | 8.725 | 8.606 | 0.2655 | 0.14648 | 0.33417 | 122.5342 | 0.22888 | 0.13733 | 123.0606 | 0.28381 | 122.8683 | 8.7433 | -122.9004 | -114.2487 | 122.3419 | 8.5968 | 8.8486 | 8.5876
1225.2031 | 122.7905 | -8.6105 | 114.0472 | 0.0034333 | 0.0028284 | 0.068304 | 0.063136 | 0.0037363 | -0.0032151 | -0.00055975 | -0.0014038 | 0.013674 | 0.019927 | 0.019384 | -0.0011065 | 0.0090918 | 8.9786e-05 | 0.1831 | 114.2075 | -8.7708 | 113.7726 | -8.3908 | -8.5785 | -8.5327 | 0.027466 | 0.09613 | -0.16937 | 0.027466 | 0.16022 | 0.068665 | 0.15564 | -0.16022 | 0.16022 | -0.27466 | 0.21973 | 0.07782 | 0.032044 | 0.23804 | 0.19226 | 8.4412 | -113.9511 | -114.0198 | 8.7708 | 8.7662 | 8.6792 | 0.32501 | 0.23804 | 0.37994 | 122.5433 | 0.32959 | 0.19684 | 122.9782 | 0.2655 | 122.818 | 8.7067 | -122.818 | -114.2166 | 122.3831 | 8.638 | 8.7936 | 8.638
1226.9062 | 122.644 | -8.7341 | 114.0152 | 0.011063 | 0.0066736 | 0.071508 | 0.066554 | 0.0050179 | -0.0015061 | 0.00029485 | 0.0046998 | 0.015169 | 0.02249 | 0.011053 | 0.00060247 | 0.0080236 | -0.0018328 | 0.16479 | 114.1663 | -8.8898 | 113.5757 | -8.6563 | -8.8211 | -8.7982 | -0.19226 | 0.13733 | -0.18768 | -0.10529 | -0.013733 | -0.11902 | 0.054932 | -0.15564 | 0.15106 | -0.43945 | 0.07782 | -0.064087 | -0.086975 | 0.091553 | 0.068665 | 8.5464 | -113.8779 | -114.1205 | 8.7204 | 8.7891 | 8.6151 | 0.24261 | 0.068664 | 0.23346 | 122.4655 | 0.17395 | 0.082397 | 123.056 | 0.32501 | 122.9004 | 8.8715 | -122.905 | -114.2029 | 122.3099 | 8.6288 | 8.8989 | 8.5419
1228.6406 | 122.699 | -8.6334 | 114.0839 | 0.0034333 | 0.0058192 | 0.069158 | 0.066127 | 0.0039499 | -0.0025741 | -0.0018414 | 0.001648 | 0.014742 | 0.021636 | 0.020452 | -0.0028155 | 0.0093054 | 0.00051699 | 0.19226 | 114.2395 | -8.7982 | 113.6856 | -8.5419 | -8.6884 | -8.6517 | -0.14648 | 0.10986 | -0.19226 | -0.068665 | 0.036621 | -0.064087 | 0.07782 | -0.16479 | 0.15564 | -0.39825 | 0.091553 | -0.01831 | -0.054931 | 0.14649 | 0.10986 | 8.4412 | -113.974 | -114.1525 | 8.67 | 8.7112 | 8.5693 | 0.27008 | 0.12817 | 0.25635 | 122.4838 | 0.22888 | 0.1236 | 123.0377 | 0.30212 | 122.8729 | 8.7433 | -122.8821 | -114.2761 | 122.319 | 8.5648 | 8.8257 | 8.4869
1230.3906 | 122.7448 | -8.7708 | 113.9008 | 0.011063 | 0.0056054 | 0.070654 | 0.0657 | 0.0026681 | -0.0023605 | -0.00055975 | 0.0046998 | 0.012392 | 0.020568 | 0.020452 | 0.0027387 | 0.0097326 | 0.0013714 | 0.12817 | 114.0839 | -8.9813 | 113.5162 | -8.6838 | -8.876 | -8.8257 | -0.068665 | 0.10986 | -0.19226 | -0.013733 | 0.064087 | -0.027466 | 0.12817 | -0.21057 | 0.1831 | -0.38452 | 0.086975 | -0.054932 | -0.10529 | 0.15564 | 0.10529 | 8.5785 | -113.7909 | -113.9145 | 8.8348 | 8.8989 | 8.7433 | 0.32044 | 0.16479 | 0.29755 | 122.4976 | 0.25635 | 0.17853 | 123.0652 | 0.30212 | 122.8546 | 8.8806 | -122.8821 | -114.093 | 122.287 | 8.757 | 8.8989 | 8.7021
1232.0938 | 122.7585 | -8.5922 | 114.0701 | 0.011063 | 0.0024012 | 0.069372 | 0.06335 | 0.0052315 | -0.0025741 | 0.0017902 | 0.001648 | 0.012606 | 0.018431 | 0.017675 | 0.00038887 | 0.008451 | -0.00033761 | 0.09613 | 114.2212 | -8.7616 | 113.7451 | -8.4503 | -8.6334 | -8.5648 | -0.086975 | 0.10071 | -0.17853 | -0.022888 | 0.073242 | -0.013733 | 0.10529 | -0.16937 | 0.15106 | -0.32501 | 0.14191 | 0.027466 | -0.041199 | 0.19684 | 0.12817 | 8.4137 | -113.9694 | -114.093 | 8.6655 | 8.6975 | 8.5785 | 0.28381 | 0.16479 | 0.31128 | 122.5067 | 0.25177 | 0.15564 | 122.9828 | 0.27924 | 122.8134 | 8.6929 | -122.8317 | -114.2487 | 122.3373 | 8.5693 | 8.6884 | 8.5052
1233.8438 | 122.6761 | -8.9584 | 113.7863 | 0.0034333 | 0.0073144 | 0.069158 | 0.066554 | 0.0026681 | -0.0032151 | -0.0018414 | 0.001648 | 0.015383 | 0.021422 | 0.012548 | -0.0026019 | 0.0080236 | -0.0020464 | 0.14648 | 113.8962 | -9.1415 | 113.3331 | -8.876 | -9.0088 | -8.9905 | -0.14648 | 0.13275 | -0.21057 | -0.09613 | 0.004578 | -0.068665 | 0.064087 | -0.18311 | 0.10986 | -0.45319 | 0.082397 | -0.032044 | -0.050354 | 0.15106 | 0.13275 | 8.7479 | -113.6536 | -113.8824 | 8.963 | 9.0225 | 8.8898 | 0.27466 | 0.14191 | 0.2655 | 122.4747 | 0.21515 | 0.11444 | 123.0377 | 0.34332 | 122.8546 | 9.0912 | -122.9279 | -113.9969 | 122.2916 | 8.8623 | 9.1049 | 8.812
1235.5156 | 122.7493 | -8.757 | 113.9099 | -0.0041962 | 0.0049646 | 0.069799 | 0.063777 | 0.0013863 | -0.0034287 | 0.00072205 | 0.0046998 | 0.011538 | 0.02014 | 0.02152 | -0.00046573 | 0.0088782 | -0.00076481 | 0.11444 | 114.0244 | -8.931 | 113.5483 | -8.6426 | -8.8165 | -8.7616 | -0.07782 | 0.10529 | -0.17395 | -0.004578 | 0.086975 | 0.004578 | 0.11444 | -0.17395 | 0.11444 | -0.36163 | 0.11444 | -0.004578 | -0.059509 | 0.16937 | 0.11444 | 8.5831 | -113.8046 | -113.9145 | 8.844 | 8.8715 | 8.7616 | 0.28839 | 0.17853 | 0.28839 | 122.4792 | 0.26092 | 0.16937 | 122.9553 | 0.27924 | 122.7814 | 8.8623 | -122.8409 | -114.0839 | 122.3053 | 8.7524 | 8.8715 | 8.6792
1237.2656 | 122.7997 | -8.8348 | 113.8092 | 0.018692 | 0.0077418 | 0.070867 | 0.066341 | 0.0041635 | 0.0019119 | -0.00098695 | -0.0014038 | 0.014101 | 0.020354 | 0.024938 | 0.0029523 | 0.0088782 | -0.001192 | 0.19226 | 113.9557 | -8.9951 | 113.5345 | -8.6655 | -8.8577 | -8.8165 | 0.032043 | 0.064087 | -0.14648 | 0.045776 | 0.11902 | 0.032043 | 0.16479 | -0.16022 | 0.14648 | -0.27466 | 0.16937 | 0.018311 | -0.022888 | 0.17853 | 0.13733 | 8.6884 | -113.7451 | -113.7634 | 8.9539 | 8.9996 | 8.8669 | 0.31128 | 0.17853 | 0.32959 | 122.5296 | 0.2655 | 0.19226 | 122.9507 | 0.21057 | 122.7905 | 8.8989 | -122.8043 | -113.9557 | 122.3694 | 8.8806 | 9.0271 | 8.8669
1239.0156 | 122.7585 | -9.3475 | 113.3286 | 0.0034333 | 0.0077418 | 0.068945 | 0.066341 | 0.0030953 | -0.0040695 | -0.00077335 | 0.0046998 | 0.013888 | 0.020995 | 0.020452 | 0.0014569 | 0.008451 | 0.00030339 | 0.13733 | 113.4521 | -9.5352 | 112.9715 | -9.1827 | -9.4025 | -9.343 | -0.032043 | 0.10071 | -0.16022 | -0.004578 | 0.07782 | -0.013733 | 0.11902 | -0.18768 | 0.1236 | -0.35706 | 0.16479 | 0.004577 | -0.054932 | 0.19226 | 0.13275 | 9.1873 | -113.2278 | -113.3331 | 9.4254 | 9.4666 | 9.3338 | 0.27924 | 0.14648 | 0.35248 | 122.5067 | 0.23804 | 0.15564 | 122.9874 | 0.26093 | 122.7997 | 9.4482 | -122.8638 | -113.4888 | 122.319 | 9.343 | 9.4849 | 9.3155
1240.6875 | 122.7448 | -9.2331 | 113.4613 | -0.0041962 | 0.0058192 | 0.069799 | 0.063136 | 0.0050179 | -0.0038559 | -0.0016278 | 0.0046998 | 0.013033 | 0.022063 | 0.01917 | -0.0030291 | 0.008451 | 0.00073059 | 0.21057 | 113.5986 | -9.3658 | 113.1775 | -9.0225 | -9.1919 | -9.1599 | -0.013733 | 0.10529 | -0.16937 | -0.036621 | 0.07782 | -0.009155 | 0.10071 | -0.13275 | 0.13733 | -0.28381 | 0.21057 | 0.073242 | 0.041198 | 0.20599 | 0.17395 | 9.0637 | -113.356 | -113.4979 | 9.3109 | 9.3338 | 9.2239 | 0.27008 | 0.16022 | 0.34332 | 122.5433 | 0.24719 | 0.13275 | 122.9645 | 0.27466 | 122.8317 | 9.3384 | -122.8271 | -113.6307 | 122.4106 | 9.1965 | 9.4437 | 9.2194
1242.4375 | 122.7768 | -8.8577 | 113.8138 | 0.0034333 | 0.0071008 | 0.067022 | 0.066127 | 0.0022409 | -0.0023605 | 0.00093565 | -0.0014038 | 0.013247 | 0.021849 | 0.014898 | 0.0010297 | 0.0073828 | -0.0018328 | 0.21973 | 113.942 | -9.0088 | 113.53 | -8.6563 | -8.8257 | -8.7982 | -0.013733 | 0.082397 | -0.17853 | 0.009155 | 0.11902 | 0.022888 | 0.12817 | -0.15106 | 0.12817 | -0.28381 | 0.20142 | 0.059509 | 0.032043 | 0.21057 | 0.1831 | 8.6792 | -113.7314 | -113.8046 | 8.9767 | 8.9859 | 8.8806 | 0.3067 | 0.20142 | 0.35248 | 122.5388 | 0.29755 | 0.18768 | 122.9507 | 0.26092 | 122.7997 | 8.9401 | -122.8226 | -113.9923 | 122.3877 | 8.8669 | 9.0775 | 8.844
1244.125 | 122.7814 | -9.0225 | 113.5803 | -0.0041962 | 0.0060328 | 0.070013 | 0.066982 | 0.0018137 | -0.0027877 | 0.0017902 | 0.0046998 | 0.013674 | 0.02014 | 0.01853 | 0.0010297 | 0.0082374 | 0.0030804 | 0.15106 | 113.7817 | -9.256 | 113.2828 | -8.931 | -9.1278 | -9.0775 | -0.032043 | 0.086975 | -0.16937 | 0.036621 | 0.10986 | 0 | 0.16479 | -0.23346 | 0.20142 | -0.29755 | 0.091553 | -0.054932 | -0.10529 | 0.17853 | 0.12817 | 8.8531 | -113.4933 | -113.5437 | 9.1324 | 9.1873 | 9.0225 | 0.33417 | 0.16937 | 0.32501 | 122.5388 | 0.27924 | 0.20599 | 123.0377 | 0.25635 | 122.8043 | 9.1095 | -122.8363 | -113.7497 | 122.3053 | 9.0591 | 9.1736 | 8.9905
1245.875 | 122.7951 | -8.9218 | 113.7039 | 0.011063 | 0.0043238 | 0.071081 | 0.066554 | 0.0065133 | -0.00086509 | -0.0033368 | -0.0014038 | 0.013674 | 0.022277 | 0.020666 | 0.0025251 | 0.0086646 | 0.00094419 | 0.20599 | 113.8641 | -9.0866 | 113.4201 | -8.7524 | -8.9584 | -8.931 | 0.004578 | 0.082397 | -0.15564 | 0.045776 | 0.13733 | 0.018311 | 0.16479 | -0.16479 | 0.16022 | -0.28381 | 0.16937 | -0.009155 | -0.036621 | 0.15564 | 0.12817 | 8.7662 | -113.6215 | -113.6581 | 9.0591 | 9.0866 | 8.9401 | 0.32044 | 0.17395 | 0.33417 | 122.5067 | 0.29297 | 0.20142 | 122.9507 | 0.23804 | 122.7859 | 9.0042 | -122.7905 | -113.8596 | 122.3419 | 8.9676 | 9.1278 | 8.9264
1247.6406 | 122.7859 | -8.9722 | 113.6765 | 0.0034333 | 0.0051782 | 0.070013 | 0.065913 | 0.0015999 | -0.0040695 | -0.003764 | 0.0046998 | 0.011965 | 0.020995 | 0.017675 | 0.0020979 | 0.011014 | -0.00033761 | 0.1831 | 113.8458 | -9.137 | 113.4018 | -8.7891 | -8.9996 | -8.9584 | 0.004578 | 0.082397 | -0.16022 | 0.045776 | 0.11444 | 0.018311 | 0.16937 | -0.16479 | 0.16937 | -0.27466 | 0.18311 | 0.013733 | -0.027466 | 0.17853 | 0.13733 | 8.812 | -113.5941 | -113.6307 | 9.0866 | 9.1415 | 8.9905 | 0.32959 | 0.17853 | 0.3479 | 122.5388 | 0.27466 | 0.20599 | 122.9828 | 0.24261 | 122.818 | 9.0546 | -122.8134 | -113.8367 | 122.374 | 9.0179 | 9.1553 | 8.9767
1249.4062 | 122.7631 | -8.9172 | 113.7451 | 0.011063 | 0.0038966 | 0.069372 | 0.067195 | 0.0056589 | -0.0012925 | -0.00034615 | 0.0046998 | 0.015597 | 0.020354 | 0.023443 | 0.00081607 | 0.010587 | -0.00033761 | 0.14191 | 113.9557 | -9.0958 | 113.3698 | -8.8257 | -9.0225 | -8.963 | -0.054932 | 0.09613 | -0.16479 | 0 | 0.086975 | -0.032043 | 0.11902 | -0.17853 | 0.21057 | -0.37537 | 0.091552 | -0.045777 | -0.10529 | 0.13275 | 0.073242 | 8.7524 | -113.649 | -113.7451 | 9.0042 | 9.0363 | 8.8852 | 0.28381 | 0.13275 | 0.27008 | 122.4655 | 0.25177 | 0.16479 | 123.0515 | 0.26092 | 122.8729 | 9.0134 | -122.8409 | -113.9099 | 122.287 | 8.9172 | 9.0591 | 8.8623
1251.1562 | 122.7905 | -8.8394 | 113.8046 | 0.0034333 | 0.0062464 | 0.067449 | 0.062923 | 0.0026681 | -0.0021469 | -0.00034615 | 0.001648 | 0.012606 | 0.021209 | 0.018957 | -0.0017475 | 0.0069556 | -0.0033282 | 0.21973 | 113.9236 | -9.0179 | 113.5254 | -8.638 | -8.812 | -8.8028 | 0.018311 | 0.082397 | -0.17395 | 0.022888 | 0.14191 | 0.036621 | 0.14191 | -0.17853 | 0.11902 | -0.27923 | 0.20142 | 0.036622 | 0.027466 | 0.21515 | 0.20599 | 8.6655 | -113.7222 | -113.7817 | 8.9813 | 8.9813 | 8.876 | 0.31586 | 0.21057 | 0.37994 | 122.5433 | 0.31586 | 0.19684 | 122.9416 | 0.25635 | 122.7631 | 8.9218 | -122.8226 | -113.9786 | 122.3648 | 8.8623 | 9.0591 | 8.8577
1252.9062 | 122.7127 | -8.8303 | 113.9145 | 0.011063 | 0.0062464 | 0.067663 | 0.065913 | 0.0060861 | -0.0025741 | -0.0014142 | -0.0014038 | 0.016237 | 0.020781 | 0.012121 | -0.0036701 | 0.0071692 | 0.002226 | 0.18768 | 114.0427 | -9.0042 | 113.4888 | -8.7158 | -8.8715 | -8.8531 | -0.13275 | 0.1236 | -0.1831 | -0.064087 | 0.041199 | -0.07782 | 0.09613 | -0.17395 | 0.12817 | -0.42572 | 0.11444 | -0.022888 | -0.041199 | 0.15106 | 0.13275 | 8.6472 | -113.7909 | -113.9786 | 8.8715 | 8.9264 | 8.7524 | 0.27924 | 0.10528 | 0.28839 | 122.493 | 0.2243 | 0.11902 | 123.0469 | 0.3067 | 122.8729 | 8.9539 | -122.9187 | -114.0976 | 122.319 | 8.7662 | 9.0179 | 8.6975
1254.6562 | 122.7997 | -8.8577 | 113.7588 | 0.011063 | 0.0060328 | 0.070226 | 0.065913 | 0.0035227 | -0.0017197 | 0.0015764 | 0.001648 | 0.014742 | 0.021849 | 0.02622 | 0.0014569 | 0.00781 | -0.0014056 | 0.21973 | 113.9694 | -9.0454 | 113.5025 | -8.6838 | -8.9035 | -8.8577 | 0.022888 | 0.07782 | -0.16022 | 0.036621 | 0.13275 | 0.018311 | 0.16479 | -0.18768 | 0.21057 | -0.25635 | 0.17395 | 0 | -0.045776 | 0.18768 | 0.14191 | 8.6975 | -113.681 | -113.7222 | 8.9905 | 9.0225 | 8.876 | 0.32501 | 0.17853 | 0.36163 | 122.5479 | 0.29297 | 0.19684 | 123.0148 | 0.23804 | 122.8271 | 8.9355 | -122.8043 | -113.9191 | 122.3602 | 8.8943 | 9.0775 | 8.8806
1256.3438 | 122.7127 | -8.7753 | 113.942 | -0.0041962 | 0.0051782 | 0.070654 | 0.065273 | 0.0030953 | -0.0036423 | -0.0029096 | 0.001648 | 0.014101 | 0.020354 | 0.015112 | -0.00046573 | 0.0090918 | 0.00073059 | 0.21973 | 114.0518 | -8.9722 | 113.5483 | -8.638 | -8.8028 | -8.7936 | -0.068665 | 0.10986 | -0.19226 | -0.045776 | 0.059509 | -0.041199 | 0.091553 | -0.19684 | 0.10986 | -0.39368 | 0.13733 | -0.01831 | -0.027465 | 0.17853 | 0.16937 | 8.5831 | -113.8321 | -113.9877 | 8.8348 | 8.8669 | 8.7341 | 0.28381 | 0.15106 | 0.33417 | 122.5204 | 0.25177 | 0.14648 | 123.024 | 0.30212 | 122.8271 | 8.8852 | -122.9141 | -114.1342 | 122.3236 | 8.7296 | 8.9951 | 8.7067
1258.0781 | 122.6624 | -8.8486 | 113.8824 | 0.011063 | 0.0079554 | 0.069799 | 0.064418 | 0.0069405 | -0.0015061 | 0.0017902 | 0.001648 | 0.014101 | 0.021636 | 0.010626 | -0.0015337 | 0.0073828 | 0.0013714 | 0.16022 | 114.0427 | -9.0042 | 113.4476 | -8.757 | -8.9355 | -8.8943 | -0.15106 | 0.10986 | -0.18768 | -0.091553 | -0.018311 | -0.12817 | 0.041199 | -0.15564 | 0.16022 | -0.43488 | 0.091553 | -0.045776 | -0.086975 | 0.10986 | 0.068664 | 8.6609 | -113.7726 | -113.974 | 8.8303 | 8.8898 | 8.7204 | 0.22888 | 0.059509 | 0.24719 | 122.4518 | 0.16937 | 0.09613 | 123.0469 | 0.29755 | 122.8912 | 8.9584 | -122.8867 | -114.0701 | 122.2961 | 8.757 | 9.0088 | 8.6975
1259.7656 | 122.7676 | -9.2834 | 113.4064 | -0.0041962 | 0.0043238 | 0.069372 | 0.063564 | 0.0033089 | -0.0032151 | -0.0014142 | -0.0014038 | 0.013888 | 0.020995 | 0.013403 | -0.0011065 | 0.0056738 | -0.00012381 | 0.19684 | 113.5208 | -9.3933 | 113.1134 | -9.0591 | -9.2422 | -9.2102 | -0.004578 | 0.09613 | -0.16937 | 0.009155 | 0.11902 | 0.032043 | 0.13275 | -0.10986 | 0.11444 | -0.29297 | 0.2243 | 0.073242 | 0.041198 | 0.18311 | 0.15106 | 9.1141 | -113.3102 | -113.3972 | 9.4025 | 9.4162 | 9.3155 | 0.30212 | 0.20142 | 0.33417 | 122.5067 | 0.28839 | 0.17853 | 122.9141 | 0.2655 | 122.8043 | 9.3796 | -122.7997 | -113.5757 | 122.3969 | 9.2926 | 9.4803 | 9.2789
1261.5312 | 122.7539 | -9.3933 | 113.2645 | 0.0034333 | 0.0036828 | 0.066381 | 0.063136 | 0.0015999 | -0.0034287 | -0.00013235 | 0.0046998 | 0.012179 | 0.020995 | 0.027288 | 0.0012433 | 0.0082374 | -0.00097841 | 0.1236 | 113.4018 | -9.5673 | 112.9211 | -9.2651 | -9.4482 | -9.4025 | -0.064087 | 0.082397 | -0.16937 | -0.013733 | 0.09613 | 0 | 0.11902 | -0.17395 | 0.13733 | -0.34332 | 0.12817 | -0.009155 | -0.054931 | 0.16479 | 0.11902 | 9.2239 | -113.1821 | -113.2782 | 9.4894 | 9.5123 | 9.3933 | 0.28839 | 0.16937 | 0.30212 | 122.4884 | 0.2655 | 0.15564 | 122.9691 | 0.25177 | 122.7951 | 9.4757 | -122.8317 | -113.4338 | 122.3145 | 9.3796 | 9.5169 | 9.3292
1263.2188 | 122.7768 | -9.4162 | 113.1958 | 0.011063 | 0.00646 | 0.070226 | 0.065273 | 0.0090767 | -0.0023605 | -0.00034615 | -0.0014038 | 0.013247 | 0.022277 | 0.014471 | 0.0014569 | 0.0088782 | -0.001192 | 0.16937 | 113.3789 | -9.581 | 112.9395 | -9.2377 | -9.4711 | -9.4116 | 0.013733 | 0.073242 | -0.14191 | 0.036621 | 0.12817 | 0.027466 | 0.14648 | -0.16479 | 0.1831 | -0.25635 | 0.17853 | 0.004578 | -0.054931 | 0.16937 | 0.10986 | 9.2743 | -113.1226 | -113.1592 | 9.5444 | 9.5627 | 9.4437 | 0.28839 | 0.16937 | 0.34332 | 122.5204 | 0.27008 | 0.17853 | 122.9599 | 0.21515 | 122.7951 | 9.4894 | -122.7768 | -113.3377 | 122.3557 | 9.4528 | 9.5856 | 9.4299
1264.9688 | 122.7081 | -9.4849 | 113.2004 | 0.011063 | 0.00646 | 0.06809 | 0.064418 | 0.0020273 | -0.0030015 | -0.0012006 | 0.001648 | 0.012606 | 0.020781 | 0.013189 | -0.0021747 | 0.0075964 | 0.0047894 | 0.22888 | 113.3331 | -9.6497 | 112.8754 | -9.3018 | -9.4757 | -9.4528 | -0.036621 | 0.11444 | -0.17395 | -0.041199 | 0.068665 | -0.027466 | 0.082397 | -0.16479 | 0.13275 | -0.32501 | 0.18311 | 0.032043 | 0.009155 | 0.19684 | 0.17395 | 9.3109 | -113.0859 | -113.2416 | 9.5535 | 9.5673 | 9.4574 | 0.25635 | 0.14648 | 0.3479 | 122.525 | 0.24261 | 0.13275 | 122.9828 | 0.28839 | 122.818 | 9.5993 | -122.85 | -113.3743 | 122.3602 | 9.4437 | 9.7137 | 9.4482
1266.7344 | 122.8088 | -9.2789 | 113.3606 | 0.0034333 | 0.0062464 | 0.071081 | 0.063564 | 0.0013863 | -0.0030015 | 0.00050845 | 0.0077514 | 0.013033 | 0.022063 | 0.018957 | -0.0015337 | 0.008451 | 0.00073059 | 0.17853 | 113.4842 | -9.4666 | 113.0768 | -9.0958 | -9.2651 | -9.2468 | 0.027466 | 0.07782 | -0.16479 | 0.041199 | 0.15564 | 0.054932 | 0.16022 | -0.18768 | 0.1236 | -0.28381 | 0.18311 | 0.032044 | 0.013733 | 0.21973 | 0.20142 | 9.1141 | -113.2828 | -113.3194 | 9.4345 | 9.4391 | 9.3338 | 0.32501 | 0.21973 | 0.37079 | 122.5433 | 0.32044 | 0.20599 | 122.9507 | 0.24261 | 122.7631 | 9.3567 | -122.8271 | -113.5254 | 122.3557 | 9.3201 | 9.4574 | 9.3063
1268.4219 | 122.8043 | -9.2468 | 113.3835 | -0.0041962 | 0.0034692 | 0.07044 | 0.064632 | 0.0043771 | -0.0042831 | -0.00013235 | 0.001648 | 0.014956 | 0.018431 | 0.017462 | -0.0026019 | 0.0088782 | -0.0037554 | 0.17853 | 113.5437 | -9.4345 | 113.1226 | -9.0408 | -9.2148 | -9.1919 | 0.054932 | 0.09613 | -0.16937 | 0.050354 | 0.16937 | 0.059509 | 0.16022 | -0.18768 | 0.16022 | -0.26093 | 0.20599 | 0.054931 | 0.032043 | 0.24261 | 0.21973 | 9.0775 | -113.2874 | -113.3331 | 9.4162 | 9.407 | 9.3063 | 0.32959 | 0.22888 | 0.39368 | 122.5571 | 0.33875 | 0.21973 | 122.9782 | 0.2655 | 122.7905 | 9.343 | -122.818 | -113.5529 | 122.3694 | 9.2972 | 9.4254 | 9.3018
1270.1719 | 122.7356 | -9.343 | 113.3102 | 0.018692 | 0.0058192 | 0.070654 | 0.066341 | 0.0018137 | -0.0027877 | 0.00093565 | -0.0014038 | 0.014742 | 0.021636 | 0.020666 | 0.0012433 | 0.00781 | 0.0028668 | 0.14191 | 113.4842 | -9.4849 | 113.0035 | -9.169 | -9.3796 | -9.3384 | 0 | 0.082397 | -0.17395 | -0.004578 | 0.086975 | -0.004578 | 0.11444 | -0.14191 | 0.17395 | -0.3067 | 0.17395 | 0.004578 | -0.036621 | 0.14648 | 0.10529 | 9.169 | -113.2278 | -113.3148 | 9.4299 | 9.4574 | 9.3384 | 0.28839 | 0.16937 | 0.31586 | 122.4884 | 0.26092 | 0.16937 | 122.9691 | 0.25635 | 122.8271 | 9.4254 | -122.7951 | -113.4842 | 122.3465 | 9.3384 | 9.4849 | 9.343
1271.9219 | 122.7539 | -9.2834 | 113.3835 | 0.011063 | 0.0045374 | 0.070867 | 0.066554 | 0.0035227 | -0.0017197 | 0.00072205 | -0.0014038 | 0.014315 | 0.021209 | 0.018316 | 0.00081607 | 0.010801 | -0.0026874 | 0.12817 | 113.5208 | -9.4482 | 113.0539 | -9.1461 | -9.3338 | -9.2743 | -0.050354 | 0.091553 | -0.1831 | -0.018311 | 0.059509 | -0.018311 | 0.10071 | -0.16479 | 0.13733 | -0.32959 | 0.13733 | 0.009155 | -0.050354 | 0.17395 | 0.11444 | 9.1003 | -113.2919 | -113.4018 | 9.343 | 9.3842 | 9.2651 | 0.28381 | 0.16479 | 0.30212 | 122.5021 | 0.24261 | 0.16479 | 122.9691 | 0.27466 | 122.8043 | 9.375 | -122.8317 | -113.5666 | 122.3373 | 9.2651 | 9.4116 | 9.2331
1273.6719 | 122.8043 | -9.1415 | 113.4567 | 0.0034333 | 0.003042 | 0.070654 | 0.064845 | 0.00053194 | -0.0034287 | 0.00072205 | 0.0077514 | 0.014956 | 0.019713 | 0.021734 | -0.0013201 | 0.0082374 | 8.9786e-05 | 0.16937 | 113.6536 | -9.288 | 113.2233 | -8.931 | -9.1187 | -9.082 | 0.045776 | 0.091553 | -0.16022 | 0.045776 | 0.16479 | 0.073242 | 0.15106 | -0.14648 | 0.19684 | -0.23346 | 0.21057 | 0.05951 | 0.022889 | 0.20599 | 0.16937 | 8.9813 | -113.3652 | -113.4109 | 9.3063 | 9.2926 | 9.2148 | 0.31128 | 0.23346 | 0.35706 | 122.5113 | 0.32501 | 0.20599 | 122.9416 | 0.25177 | 122.7951 | 9.2331 | -122.7448 | -113.6169 | 122.3648 | 9.1873 | 9.3109 | 9.1873
1275.3594 | 122.644 | -8.8074 | 113.8916 | 0.0034333 | 0.00646 | 0.071081 | 0.067836 | 0.0050179 | -0.0017197 | 0.0017902 | -0.0014038 | 0.013247 | 0.022704 | 0.018743 | -3.8532e-05 | 0.0054602 | -0.00033761 | 0.17395 | 114.0976 | -8.963 | 113.4842 | -8.7341 | -8.9035 | -8.8669 | -0.15564 | 0.13733 | -0.20599 | -0.10071 | -0.018311 | -0.13733 | 0.041199 | -0.15564 | 0.20599 | -0.40741 | 0.073242 | -0.059509 | -0.09613 | 0.096131 | 0.05951 | 8.6014 | -113.7543 | -113.9923 | 8.7891 | 8.8486 | 8.67 | 0.24719 | 0.068665 | 0.22888 | 122.4472 | 0.18768 | 0.10529 | 123.0606 | 0.34332 | 122.905 | 8.9447 | -122.8546 | -114.0976 | 122.2916 | 8.7067 | 8.9813 | 8.6517
1277.0469 | 122.6669 | -9.256 | 113.4705 | 0.011063 | 0.0051782 | 0.07044 | 0.066982 | 0.0022409 | -0.0019333 | -0.0018414 | -0.0014038 | 0.014956 | 0.022917 | 0.014898 | 0.00038887 | 0.0075964 | 0.0028668 | 0.16479 | 113.649 | -9.4025 | 113.0722 | -9.1461 | -9.3155 | -9.3018 | -0.11444 | 0.12817 | -0.16479 | -0.07782 | -0.009155 | -0.10529 | 0.054932 | -0.14649 | 0.17853 | -0.39825 | 0.10986 | -0.045777 | -0.05951 | 0.10071 | 0.086975 | 9.0912 | -113.3423 | -113.5483 | 9.2468 | 9.3109 | 9.1507 | 0.21973 | 0.059509 | 0.25635 | 122.4747 | 0.15564 | 0.086975 | 123.0515 | 0.29297 | 122.905 | 9.3842 | -122.8729 | -113.6353 | 122.3282 | 9.1782 | 9.4208 | 9.1415
1278.7344 | 122.7905 | -8.931 | 113.7131 | 0.0034333 | 0.0043238 | 0.069158 | 0.064845 | 0.0026681 | -0.0027877 | 0.0013628 | 0.0046998 | 0.012179 | 0.021422 | 0.020025 | -0.0011065 | 0.008451 | -0.0031146 | 0.13275 | 113.8824 | -9.0958 | 113.4338 | -8.757 | -8.9172 | -8.8715 | 0 | 0.091553 | -0.16937 | 0.027466 | 0.13733 | 0.054932 | 0.15564 | -0.1648 | 0.16937 | -0.27924 | 0.17395 | 0.059509 | 0.013733 | 0.2243 | 0.17853 | 8.7616 | -113.6215 | -113.6856 | 9.0683 | 9.0866 | 8.9859 | 0.32501 | 0.22431 | 0.33875 | 122.5296 | 0.3067 | 0.19684 | 122.9782 | 0.26093 | 122.8134 | 9.0225 | -122.8088 | -113.8824 | 122.3648 | 8.9584 | 9.0637 | 8.931
1280.4219 | 122.7173 | -9.2011 | 113.5071 | 0.0034333 | 0.0066736 | 0.068945 | 0.064845 | 0.00095914 | -0.0044967 | -0.00013235 | 0.001648 | 0.014956 | 0.021849 | 0.014471 | -0.00046573 | 0.0086646 | 0.00030339 | 0.21057 | 113.6444 | -9.3796 | 113.1226 | -9.0866 | -9.256 | -9.2148 | -0.073242 | 0.13733 | -0.17853 | -0.027466 | 0.054932 | -0.045776 | 0.091553 | -0.17853 | 0.13733 | -0.38452 | 0.11444 | -0.013733 | -0.054931 | 0.16479 | 0.1236 | 9.0225 | -113.3698 | -113.5345 | 9.256 | 9.2926 | 9.1553 | 0.27008 | 0.13275 | 0.29297 | 122.5021 | 0.23346 | 0.15106 | 123.024 | 0.31586 | 122.8455 | 9.3384 | -122.8867 | -113.6856 | 122.3236 | 9.1736 | 9.4116 | 9.1278
1282.1094 | 122.8043 | -9.2468 | 113.3835 | -0.0041962 | 0.0034692 | 0.070013 | 0.065059 | 0.0026681 | -0.0036423 | -0.00013235 | 0.001648 | 0.012606 | 0.022063 | 0.023229 | -3.8532e-05 | 0.0071692 | -0.00033761 | 0.19684 | 113.5208 | -9.4299 | 113.1088 | -9.0317 | -9.2331 | -9.1919 | 0.050354 | 0.073242 | -0.15106 | 0.054932 | 0.17395 | 0.054932 | 0.14191 | -0.18311 | 0.13733 | -0.27466 | 0.21515 | 0.054931 | 0.013733 | 0.23804 | 0.19684 | 9.0958 | -113.3102 | -113.3286 | 9.4208 | 9.3887 | 9.3018 | 0.29297 | 0.20599 | 0.39826 | 122.5388 | 0.32501 | 0.20599 | 122.9507 | 0.2243 | 122.7676 | 9.3201 | -122.8134 | -113.5345 | 122.3557 | 9.3018 | 9.4437 | 9.2972
1283.8594 | 122.7814 | -9.2743 | 113.3698 | 0.011063 | 0.0041102 | 0.068945 | 0.065913 | 0.00074554 | -0.0038559 | -0.00055975 | -0.0014038 | 0.014529 | 0.020995 | 0.019811 | -0.0019611 | 0.0082374 | 0.0024396 | 0.21973 | 113.5208 | -9.4391 | 113.1134 | -9.0591 | -9.256 | -9.2285 | 0.032043 | 0.086975 | -0.16022 | 0.032043 | 0.13733 | 0.059509 | 0.16022 | -0.16479 | 0.15106 | -0.25635 | 0.21515 | 0.045776 | 0.018311 | 0.21057 | 0.18311 | 9.1141 | -113.2828 | -113.3377 | 9.4116 | 9.4345 | 9.3338 | 0.32043 | 0.21973 | 0.37994 | 122.5525 | 0.29755 | 0.19226 | 122.9599 | 0.24719 | 122.7951 | 9.3613 | -122.8088 | -113.53 | 122.3877 | 9.3063 | 9.494 | 9.3063
1285.5312 | 122.7951 | -9.3338 | 113.2736 | -0.0041962 | 0.007528 | 0.072363 | 0.063991 | 0.0018137 | -0.00065149 | -0.00055975 | -0.0014038 | 0.013674 | 0.020781 | 0.018957 | 0.0018841 | 0.0090918 | -0.0022602 | 0.19684 | 113.4247 | -9.4894 | 113.0173 | -9.169 | -9.375 | -9.3338 | 0.009155 | 0.091553 | -0.16022 | 0.054932 | 0.13733 | 0.036621 | 0.17395 | -0.15564 | 0.15106 | -0.25635 | 0.16479 | 0 | -0.041199 | 0.15564 | 0.11444 | 9.1736 | -113.1821 | -113.2187 | 9.4711 | 9.5078 | 9.3704 | 0.33417 | 0.19684 | 0.32043 | 122.5067 | 0.29755 | 0.21515 | 122.9141 | 0.25177 | 122.7585 | 9.4254 | -122.7631 | -113.4338 | 122.3511 | 9.3887 | 9.5306 | 9.343
1287.2969 | 122.7676 | -9.288 | 113.3331 | 0.018692 | 0.0051782 | 0.070226 | 0.064632 | 0.0052315 | -0.0044967 | 0.0026446 | 0.0046998 | 0.01581 | 0.02014 | 0.021948 | 0.0027387 | 0.01016 | -0.0016192 | 0.14191 | 113.5254 | -9.4757 | 113.0081 | -9.1736 | -9.3658 | -9.3109 | -0.032043 | 0.10071 | -0.16022 | 0.013733 | 0.09613 | 0 | 0.15106 | -0.18768 | 0.19226 | -0.32501 | 0.11444 | -0.022888 | -0.07782 | 0.16479 | 0.10986 | 9.1278 | -113.2324 | -113.3194 | 9.3842 | 9.4391 | 9.288 | 0.31128 | 0.16022 | 0.30212 | 122.4838 | 0.25635 | 0.17395 | 123.0011 | 0.26093 | 122.8134 | 9.3887 | -122.8088 | -113.4933 | 122.2961 | 9.3018 | 9.4299 | 9.256
1288.9844 | 122.7036 | -9.3796 | 113.2645 | 0.0034333 | 0.0049646 | 0.071081 | 0.066982 | 0.0041635 | -0.0030015 | 0.0011492 | 0.0046998 | 0.013888 | 0.020995 | 0.006994 | 0.0033795 | 0.010587 | -0.00055121 | 0.11902 | 113.4659 | -9.5535 | 112.8754 | -9.3338 | -9.5261 | -9.4757 | -0.086975 | 0.10986 | -0.18768 | -0.036621 | 0.041199 | -0.073242 | 0.086975 | -0.17395 | 0.20142 | -0.3891 | 0.045777 | -0.09613 | -0.14648 | 0.07782 | 0.027466 | 9.1919 | -113.1546 | -113.3011 | 9.4208 | 9.4666 | 9.3063 | 0.27466 | 0.11444 | 0.21973 | 122.4289 | 0.22888 | 0.15106 | 123.0194 | 0.29755 | 122.8455 | 9.4894 | -122.818 | -113.4521 | 122.2549 | 9.343 | 9.4986 | 9.2926
1290.7188 | 122.7631 | -9.2834 | 113.3652 | 0.0034333 | 0.0045374 | 0.070013 | 0.065059 | 0.0048043 | -0.0027877 | 0.0011492 | -0.0014038 | 0.014529 | 0.02249 | 0.016607 | -0.00089293 | 0.008451 | 0.0026532 | 0.1236 | 113.5574 | -9.4803 | 112.9944 | -9.2011 | -9.3796 | -9.343 | -0.054932 | 0.10071 | -0.16937 | 0.009155 | 0.073242 | -0.004578 | 0.13275 | -0.19684 | 0.19226 | -0.37079 | 0.082397 | -0.05951 | -0.096131 | 0.13733 | 0.10071 | 9.1141 | -113.2645 | -113.356 | 9.3567 | 9.4162 | 9.2789 | 0.30212 | 0.16479 | 0.27924 | 122.4747 | 0.24261 | 0.17853 | 123.0377 | 0.27008 | 122.8409 | 9.3842 | -122.8455 | -113.5345 | 122.2778 | 9.2926 | 9.407 | 9.2285
1292.4688 | 122.7036 | -14.4974 | 108.1467 | 0.011063 | 0.008169 | 0.070013 | 0.067195 | 0.0035227 | -0.0030015 | -0.00098695 | -0.0014038 | 0.013888 | 0.020995 | 0.01618 | -0.0013201 | 0.0080236 | 8.9786e-05 | 0.16937 | 108.3481 | -14.6988 | 107.8171 | -14.4379 | -14.6484 | -14.6118 | -0.064087 | 0.1236 | -0.18768 | -0.022888 | 0.064087 | -0.045776 | 0.086975 | -0.20142 | 0.20142 | -0.32959 | 0.059509 | -0.11444 | -0.15106 | 0.086976 | 0.050355 | 14.3097 | -108.0231 | -108.1696 | 14.5615 | 14.5844 | 14.4516 | 0.27466 | 0.14191 | 0.26093 | 122.5159 | 0.25177 | 0.16479 | 123.0469 | 0.31128 | 122.8455 | 14.621 | -122.8455 | -108.3344 | 122.3145 | 14.4745 | 14.6667 | 14.4333
1294.1562 | 122.7448 | -13.5544 | 109.0805 | -0.0041962 | 0.0049646 | 0.069158 | 0.064418 | 0.0082223 | -0.0019333 | -0.0018414 | 0.001648 | 0.012392 | 0.023131 | 0.017034 | -0.0026019 | 0.0090918 | 0.00030339 | 0.050354 | 109.2224 | -13.7421 | 108.7234 | -13.504 | -13.7054 | -13.6551 | -0.068665 | 0.091553 | -0.1831 | -0.022888 | 0.07782 | 0 | 0.11902 | -0.18768 | 0.14191 | -0.35706 | 0.050354 | -0.10071 | -0.15106 | 0.086975 | 0.036621 | 13.3713 | -108.989 | -109.1034 | 13.6322 | 13.6734 | 13.5544 | 0.30212 | 0.1831 | 0.23804 | 122.4655 | 0.26092 | 0.16022 | 122.9645 | 0.27466 | 122.7768 | 13.6459 | -122.8226 | -109.2636 | 122.2778 | 13.5315 | 13.6047 | 13.4857
1295.8906 | 122.6669 | -12.8723 | 109.8404 | -0.0041962 | 0.0068872 | 0.068517 | 0.062923 | 0.0037363 | -0.0034287 | 0.0015764 | 0.0046998 | 0.013888 | 0.021422 | 0.017462 | -0.0034563 | 0.0056738 | 0.00094419 | 0.14648 | 109.9319 | -13.0096 | 109.4421 | -12.7853 | -12.9639 | -12.9456 | -0.09613 | 0.11902 | -0.19226 | -0.091553 | 0.022888 | -0.073242 | 0.054932 | -0.13733 | 0.091553 | -0.39825 | 0.086975 | -0.073243 | -0.091553 | 0.064087 | 0.045777 | 12.6801 | -109.7214 | -109.9319 | 12.8952 | 12.9272 | 12.7991 | 0.24719 | 0.11902 | 0.2243 | 122.4518 | 0.21515 | 0.10071 | 122.9416 | 0.31128 | 122.8043 | 12.9913 | -122.85 | -110.0327 | 122.3145 | 12.7808 | 13.0188 | 12.7762
1297.5781 | 122.7585 | -12.7213 | 109.9091 | 0.0034333 | 0.0036828 | 0.071935 | 0.065486 | 0.0041635 | -0.0032151 | 0.00093565 | 0.001648 | 0.013033 | 0.0195 | 0.015966 | 0.00017507 | 0.0080236 | 0.0026532 | 0.059509 | 110.0784 | -12.8815 | 109.5749 | -12.6526 | -12.8586 | -12.7991 | -0.064087 | 0.1236 | -0.15564 | -0.004578 | 0.091553 | -0.004578 | 0.1236 | -0.16022 | 0.16937 | -0.33417 | 0.068664 | -0.07782 | -0.13733 | 0.082398 | 0.022888 | 12.5656 | -109.7855 | -109.9136 | 12.8128 | 12.8448 | 12.7167 | 0.27924 | 0.15106 | 0.22888 | 122.4564 | 0.24719 | 0.15106 | 122.9599 | 0.27924 | 122.7997 | 12.8448 | -122.7905 | -110.0647 | 122.2961 | 12.7167 | 12.7808 | 12.6572
1299.3438 | 122.7905 | -12.7579 | 109.8267 | 0.011063 | 0.0056054 | 0.070654 | 0.065273 | 0.0092905 | -0.0019333 | 0.00093565 | 0.0077514 | 0.01346 | 0.022704 | 0.020452 | 0.0014569 | 0.0075964 | -0.0024738 | 0.14648 | 110.0143 | -12.9089 | 109.6069 | -12.6343 | -12.8448 | -12.8128 | 0.027466 | 0.091553 | -0.16479 | 0.050354 | 0.13275 | 0.032043 | 0.14648 | -0.15106 | 0.18768 | -0.21973 | 0.1236 | -0.054931 | -0.086975 | 0.096131 | 0.064087 | 12.5931 | -109.7351 | -109.7763 | 12.8906 | 12.9044 | 12.7899 | 0.31128 | 0.19684 | 0.27466 | 122.5159 | 0.29755 | 0.21515 | 122.9233 | 0.25635 | 122.7722 | 12.8494 | -122.7356 | -109.9915 | 122.3648 | 12.8082 | 12.9044 | 12.7853
1301.0938 | 122.6761 | -12.4832 | 110.2203 | 0.018692 | 0.0071008 | 0.068731 | 0.064845 | 0.0086495 | -0.0032151 | 0.0015764 | 0.0046998 | 0.01282 | 0.020995 | 0.019384 | 0.0010297 | 0.0082374 | -0.00076481 | 0.07782 | 110.3943 | -12.6434 | 109.7946 | -12.4512 | -12.6389 | -12.5977 | -0.10986 | 0.11444 | -0.18768 | -0.045776 | 0 | -0.10071 | 0.068665 | -0.16022 | 0.17395 | -0.42572 | 0.032043 | -0.11444 | -0.15564 | 0.045777 | 0.004578 | 12.2955 | -110.1059 | -110.2661 | 12.4832 | 12.5519 | 12.3825 | 0.25635 | 0.086975 | 0.19226 | 122.4381 | 0.18768 | 0.14191 | 123.0377 | 0.30212 | 122.8775 | 12.5977 | -122.8638 | -110.408 | 122.2778 | 12.4374 | 12.561 | 12.3734
1302.7812 | 122.6761 | -12.5702 | 110.1151 | -0.0041962 | 0.0041102 | 0.067663 | 0.066554 | 0.0037363 | -0.0047103 | -0.0029096 | -0.0014038 | 0.014742 | 0.022063 | 0.010626 | -0.0026019 | 0.0082374 | 0.0017988 | 0.14191 | 110.2661 | -12.7533 | 109.6802 | -12.5702 | -12.7213 | -12.6801 | -0.14191 | 0.12817 | -0.20142 | -0.086975 | 0.013733 | -0.073242 | 0.064087 | -0.18311 | 0.15106 | -0.43487 | 0 | -0.10986 | -0.15106 | 0.073242 | 0.032044 | 12.3688 | -109.9869 | -110.202 | 12.5839 | 12.6343 | 12.4969 | 0.2655 | 0.12817 | 0.18311 | 122.4335 | 0.21515 | 0.11444 | 123.0194 | 0.32959 | 122.8363 | 12.6984 | -122.8683 | -110.3165 | 122.2504 | 12.4832 | 12.7121 | 12.4283
1304.5469 | 122.7219 | -8.9401 | 113.6902 | 0.011063 | 0.0051782 | 0.070867 | 0.065913 | 0.0013863 | -0.0015061 | -0.0022688 | 0.0046998 | 0.01581 | 0.021422 | 0.023016 | 0.0020979 | 0.0075964 | -0.00033761 | 0.16479 | 113.8504 | -9.1232 | 113.3698 | -8.7708 | -8.9859 | -8.9493 | -0.013733 | 0.086975 | -0.16937 | -0.004578 | 0.086975 | -0.004578 | 0.11444 | -0.1831 | 0.16022 | -0.32044 | 0.16937 | -0.009155 | -0.045776 | 0.17395 | 0.13733 | 8.7708 | -113.6032 | -113.6948 | 9.0271 | 9.0546 | 8.9355 | 0.28381 | 0.16479 | 0.35248 | 122.493 | 0.25635 | 0.16479 | 122.9736 | 0.25635 | 122.7905 | 9.0271 | -122.8134 | -113.8596 | 122.3099 | 8.9355 | 9.1049 | 8.9264
1306.2344 | 122.6486 | -9.137 | 113.5986 | 0.0034333 | 0.0062464 | 0.068517 | 0.064418 | 0.0020273 | -0.0027877 | 0.00072205 | -0.0014038 | 0.01282 | 0.019927 | 0.01383 | -0.0045245 | 0.0082374 | -0.00012381 | 0.15564 | 113.7405 | -9.2651 | 113.1592 | -8.9951 | -9.1644 | -9.1324 | -0.14191 | 0.14191 | -0.1831 | -0.09613 | 0.004578 | -0.086975 | 0.036621 | -0.12817 | 0.14191 | -0.43945 | 0.14191 | 0.004578 | -0.027466 | 0.13275 | 0.10071 | 8.9539 | -113.4567 | -113.6948 | 9.1415 | 9.1736 | 9.05 | 0.21973 | 0.09613 | 0.27008 | 122.4243 | 0.18768 | 0.086975 | 123.0057 | 0.32501 | 122.8775 | 9.2789 | -122.8638 | -113.7817 | 122.2961 | 9.0408 | 9.2926 | 8.9951
1307.9844 | 122.6944 | -9.1003 | 113.5849 | 0.011063 | 0.0056054 | 0.06809 | 0.064418 | -0.00096346 | -0.0019333 | 0.0017902 | 0.0046998 | 0.014529 | 0.022277 | 0.012762 | -0.00089293 | 0.0088782 | -0.00055121 | 0.18768 | 113.7726 | -9.256 | 113.1821 | -9.0179 | -9.1507 | -9.1187 | -0.11444 | 0.13275 | -0.19226 | -0.059509 | 0.054932 | -0.064087 | 0.082397 | -0.15564 | 0.18768 | -0.40283 | 0.082398 | -0.01831 | -0.050354 | 0.13733 | 0.10529 | 8.9081 | -113.4521 | -113.6444 | 9.1553 | 9.1827 | 9.0363 | 0.27466 | 0.12817 | 0.23804 | 122.438 | 0.24719 | 0.13275 | 123.0286 | 0.32501 | 122.8729 | 9.2331 | -122.8409 | -113.7772 | 122.2824 | 9.0408 | 9.288 | 8.9859
1309.7344 | 122.644 | -9.2514 | 113.443 | -0.0041962 | 0.0068872 | 0.068731 | 0.066768 | 0.00031834 | -0.0034287 | -0.00098695 | 0.001648 | 0.015597 | 0.021422 | 0.012548 | 0.0014569 | 0.00781 | -0.0014056 | 0.18768 | 113.5849 | -9.4162 | 113.0402 | -9.1461 | -9.3475 | -9.3155 | -0.11444 | 0.11902 | -0.17853 | -0.082397 | -0.004578 | -0.10071 | 0.054932 | -0.16479 | 0.14191 | -0.40283 | 0.10529 | -0.064087 | -0.09613 | 0.10071 | 0.068665 | 9.0729 | -113.324 | -113.5254 | 9.2468 | 9.3063 | 9.1507 | 0.23346 | 0.07782 | 0.27008 | 122.4564 | 0.17395 | 0.096131 | 123.0011 | 0.29755 | 122.8363 | 9.3704 | -122.8592 | -113.6215 | 122.2916 | 9.169 | 9.4391 | 9.137
1311.5 | 122.6852 | -9.2194 | 113.4888 | 0.011063 | 0.0053918 | 0.069158 | 0.065059 | 0.0035227 | -0.0027877 | 0.0043536 | 0.0077514 | 0.016237 | 0.020781 | 0.011266 | 0.0010297 | 0.006101 | -0.0018328 | 0.2243 | 113.6353 | -9.4025 | 113.0768 | -9.0729 | -9.2606 | -9.2331 | -0.059509 | 0.10529 | -0.1831 | -0.032043 | 0.054932 | -0.045776 | 0.082397 | -0.18311 | 0.14648 | -0.41199 | 0.14648 | -0.013733 | -0.041199 | 0.16937 | 0.14191 | 9.0363 | -113.3835 | -113.5208 | 9.2743 | 9.3018 | 9.1736 | 0.2655 | 0.13733 | 0.32959 | 122.4792 | 0.23804 | 0.15106 | 123.0377 | 0.28839 | 122.8546 | 9.3246 | -122.8912 | -113.6719 | 122.2961 | 9.1873 | 9.4437 | 9.1599
1313.2344 | 122.731 | -9.2102 | 113.4567 | 0.0034333 | 0.0021876 | 0.069799 | 0.062496 | 0.0020273 | -0.0040695 | -0.0016278 | 0.001648 | 0.012392 | 0.020568 | 0.024511 | -0.00089293 | 0.0071692 | 0.0026532 | 0.11444 | 113.6078 | -9.3613 | 113.0814 | -9.0775 | -9.2331 | -9.1965 | -0.064087 | 0.091553 | -0.17395 | -0.018311 | 0.07782 | -0.022888 | 0.11902 | -0.15106 | 0.15106 | -0.37537 | 0.13275 | 0.013733 | -0.022888 | 0.16479 | 0.12817 | 9.0363 | -113.3652 | -113.475 | 9.288 | 9.3292 | 9.1873 | 0.29297 | 0.15106 | 0.28381 | 122.4426 | 0.25177 | 0.15564 | 122.9691 | 0.2655 | 122.818 | 9.3018 | -122.818 | -113.6307 | 122.2916 | 9.1919 | 9.3246 | 9.1461
1314.9062 | 122.7448 | -9.2056 | 113.4659 | 0.011063 | 0.0062464 | 0.068945 | 0.062282 | 0.0052315 | -0.0019333 | 0.00093565 | 0.001648 | 0.011965 | 0.018218 | 0.025366 | -0.0026019 | 0.0080236 | 0.0028668 | 0.21057 | 113.6032 | -9.3475 | 113.1409 | -9.0088 | -9.1644 | -9.1461 | 0.004578 | 0.068665 | -0.17395 | 0.004578 | 0.12817 | 0.022888 | 0.13275 | -0.14191 | 0.13733 | -0.32501 | 0.19684 | 0.059509 | 0.041198 | 0.20142 | 0.1831 | 9.0317 | -113.3972 | -113.4613 | 9.3338 | 9.3384 | 9.2285 | 0.3067 | 0.19684 | 0.33874 | 122.4884 | 0.30212 | 0.17853 | 122.9507 | 0.24261 | 122.8088 | 9.2743 | -122.8134 | -113.6398 | 122.3465 | 9.2102 | 9.4162 | 9.2102
1316.6562 | 122.6349 | -9.1736 | 113.4888 | 0.011063 | 0.0049646 | 0.069799 | 0.065913 | 0.0030953 | -0.0010789 | -0.0016278 | -0.0014038 | 0.01282 | 0.023558 | 0.012762 | 0.0018841 | 0.008451 | -0.0018328 | 0.19226 | 113.7039 | -9.343 | 113.031 | -9.137 | -9.288 | -9.256 | -0.15106 | 0.10071 | -0.20599 | -0.082397 | -0.018311 | -0.11902 | 0.059509 | -0.16937 | 0.21515 | -0.45776 | 0.036621 | -0.082397 | -0.11444 | 0.086976 | 0.054932 | 8.9676 | -113.3881 | -113.5712 | 9.1553 | 9.2331 | 9.0546 | 0.2655 | 0.086975 | 0.20599 | 122.374 | 0.18768 | 0.1236 | 123.0469 | 0.3067 | 122.8775 | 9.2743 | -122.8317 | -113.6948 | 122.2046 | 9.0912 | 9.3658 | 9.0225
1318.4219 | 122.7631 | -9.3933 | 113.2416 | 0.011063 | 0.0026148 | 0.069372 | 0.065273 | 0.0041635 | -0.0032151 | 8.125e-05 | 0.001648 | 0.012392 | 0.019072 | 0.025793 | -0.0015337 | 0.0080236 | -0.0016192 | 0.25177 | 113.3606 | -9.5444 | 112.9578 | -9.169 | -9.3475 | -9.3475 | 0.032043 | 0.07782 | -0.15106 | 0.032043 | 0.16022 | 0.054932 | 0.13275 | -0.15106 | 0.11902 | -0.28381 | 0.22431 | 0.045777 | 0.045777 | 0.19684 | 0.19684 | 9.2422 | -113.1638 | -113.2095 | 9.5535 | 9.5261 | 9.4482 | 0.28381 | 0.20599 | 0.37537 | 122.5021 | 0.31128 | 0.18311 | 122.905 | 0.22888 | 122.7539 | 9.4711 | -122.786 | -113.3926 | 122.3511 | 9.4254 | 9.6451 | 9.4254
1320.1094 | 122.6624 | -9.4574 | 113.2233 | 0.0034333 | 0.0060328 | 0.072363 | 0.066341 | 0.0045907 | -0.0023605 | -0.00013235 | 0.001648 | 0.016878 | 0.022063 | 0.02152 | -0.00067933 | 0.0063148 | -0.0016192 | 0.25177 | 113.4338 | -9.5993 | 112.8342 | -9.3246 | -9.5123 | -9.4803 | -0.082397 | 0.10986 | -0.18768 | -0.059509 | 0.018311 | -0.10071 | 0.054932 | -0.14191 | 0.21057 | -0.3891 | 0.13275 | -0.022889 | -0.054932 | 0.11902 | 0.086975 | 9.2697 | -113.1134 | -113.2828 | 9.4757 | 9.5123 | 9.3567 | 0.24261 | 0.086975 | 0.27466 | 122.4335 | 0.20599 | 0.12817 | 123.0331 | 0.29755 | 122.8912 | 9.5673 | -122.8226 | -113.411 | 122.2916 | 9.3979 | 9.7092 | 9.375
1321.8594 | 122.7127 | -9.4482 | 113.1775 | 0.011063 | 0.0051782 | 0.070226 | 0.064632 | 0.0043771 | -0.0042831 | 0.0015764 | -0.0014038 | 0.013033 | 0.020995 | 0.019384 | -0.00067933 | 0.01016 | -0.0024738 | 0.16022 | 113.3469 | -9.6222 | 112.8387 | -9.3063 | -9.5032 | -9.4528 | -0.073242 | 0.07782 | -0.19226 | -0.022888 | 0.07782 | -0.032043 | 0.09613 | -0.17395 | 0.16937 | -0.33875 | 0.14191 | -0.004578 | -0.054932 | 0.16937 | 0.11902 | 9.256 | -113.0997 | -113.2004 | 9.5261 | 9.5444 | 9.4162 | 0.28839 | 0.16022 | 0.31586 | 122.4609 | 0.27008 | 0.16937 | 122.9691 | 0.27008 | 122.7951 | 9.5261 | -122.7997 | -113.3698 | 122.287 | 9.4254 | 9.6085 | 9.375
1323.625 | 122.699 | -9.5581 | 113.1226 | 0.0034333 | 0.0051782 | 0.069799 | 0.065486 | 0.0052315 | -0.0047103 | -0.0012006 | 0.0046998 | 0.014956 | 0.023131 | 0.01618 | -0.0017475 | 0.0080236 | -0.00012381 | 0.27924 | 113.2919 | -9.7137 | 112.7335 | -9.4254 | -9.613 | -9.6039 | -0.059509 | 0.1236 | -0.19226 | -0.041199 | 0.068665 | -0.045776 | 0.09613 | -0.15564 | 0.16937 | -0.3891 | 0.13275 | -0.045777 | -0.054932 | 0.10986 | 0.10071 | 9.3658 | -112.999 | -113.1638 | 9.6268 | 9.6542 | 9.5123 | 0.28839 | 0.14648 | 0.28839 | 122.4472 | 0.26093 | 0.15106 | 123.0057 | 0.31586 | 122.85 | 9.6817 | -122.8363 | -113.3148 | 122.2916 | 9.5169 | 9.8373 | 9.4986
1325.375 | 122.7676 | -12.4603 | 110.1196 | 0.011063 | 0.0041102 | 0.069799 | 0.065059 | 0.0062997 | -0.0017197 | 0.0017902 | 0.0046998 | 0.01346 | 0.018218 | 0.022375 | 0.0025251 | 0.010587 | 0.0020124 | 0.17853 | 110.3073 | -12.6434 | 109.8495 | -12.3505 | -12.5839 | -12.5427 | 0.018311 | 0.073242 | -0.15564 | 0.032043 | 0.1236 | 0.018311 | 0.15106 | -0.18311 | 0.18768 | -0.27008 | 0.10986 | -0.082398 | -0.1236 | 0.10071 | 0.05951 | 12.3047 | -110.0464 | -110.0876 | 12.5839 | 12.6114 | 12.4786 | 0.3067 | 0.17395 | 0.29297 | 122.493 | 0.27924 | 0.18768 | 122.9507 | 0.22888 | 122.7676 | 12.5336 | -122.7631 | -110.2753 | 122.3099 | 12.4924 | 12.6389 | 12.4786
1327.125 | 122.7722 | -12.2269 | 110.4034 | 0.0034333 | 0.0043238 | 0.070226 | 0.0657 | 0.0052315 | -0.0032151 | 0.0011492 | 0.0077514 | 0.012392 | 0.020781 | 0.017462 | 0.00060247 | 0.009519 | -0.0020464 | 0.12817 | 110.5637 | -12.3779 | 110.0647 | -12.149 | -12.3093 | -12.2635 | -0.050354 | 0.086975 | -0.16937 | -0.004578 | 0.09613 | 0.027466 | 0.12817 | -0.15106 | 0.16022 | -0.33875 | 0.07782 | -0.036621 | -0.082397 | 0.11444 | 0.068665 | 12.0575 | -110.3165 | -110.408 | 12.323 | 12.355 | 12.2543 | 0.29755 | 0.19684 | 0.22888 | 122.4426 | 0.2655 | 0.16479 | 122.9416 | 0.25635 | 122.7905 | 12.3138 | -122.7814 | -110.5728 | 122.2916 | 12.2223 | 12.355 | 12.1765
1328.7969 | 122.6395 | -12.1811 | 110.5179 | 0.011063 | 0.0071008 | 0.070654 | 0.0657 | 0.0035227 | -0.0032151 | 0.003499 | 0.0046998 | 0.015383 | 0.022704 | 0.015753 | -0.00025213 | 0.0071692 | 0.001585 | 0.12817 | 110.6964 | -12.3367 | 110.0693 | -12.1582 | -12.3322 | -12.2772 | -0.16479 | 0.13275 | -0.20142 | -0.09613 | -0.036621 | -0.12817 | 0.041199 | -0.15564 | 0.17853 | -0.44861 | 0.022888 | -0.096131 | -0.15106 | 0.059509 | 0.004578 | 11.9797 | -110.3851 | -110.614 | 12.1445 | 12.2223 | 12.0529 | 0.24262 | 0.073242 | 0.17853 | 122.406 | 0.1648 | 0.10529 | 123.0331 | 0.33417 | 122.8775 | 12.3138 | -122.8546 | -110.7193 | 122.2504 | 12.085 | 12.3093 | 12.0163
1330.5469 | 122.7814 | -11.9385 | 110.6461 | 0.0034333 | 0.0062464 | 0.070654 | 0.065273 | 0.0011727 | -0.0021469 | -0.00034615 | -0.0014038 | 0.014742 | 0.021209 | 0.017889 | 0.0025251 | 0.0097326 | 0.001585 | 0.19226 | 110.8612 | -12.1078 | 110.3897 | -11.8057 | -12.0255 | -11.9888 | 0.018311 | 0.07782 | -0.15106 | 0.045776 | 0.1236 | 0.013733 | 0.16022 | -0.16937 | 0.21515 | -0.25635 | 0.13275 | -0.050354 | -0.086975 | 0.11902 | 0.082397 | 11.7874 | -110.5682 | -110.6003 | 12.0621 | 12.0987 | 11.9522 | 0.31128 | 0.16479 | 0.30212 | 122.4976 | 0.27466 | 0.19684 | 122.9691 | 0.22888 | 122.7997 | 12.0163 | -122.7539 | -110.7971 | 122.3282 | 11.9843 | 12.1307 | 11.9568
1332.2344 | 122.7722 | -12.5656 | 110.0693 | 0.0034333 | 0.0060328 | 0.069586 | 0.0657 | 0.0028817 | -0.00086509 | 0.0011492 | 0.001648 | 0.013247 | 0.020995 | 0.01618 | -0.0019611 | 0.010587 | -0.00076481 | 0.21057 | 110.1974 | -12.7213 | 109.79 | -12.4283 | -12.6114 | -12.5885 | -0.004578 | 0.11444 | -0.16937 | 0.009155 | 0.1236 | 0.018311 | 0.13733 | -0.15564 | 0.12817 | -0.27924 | 0.13733 | -0.022888 | -0.045776 | 0.13275 | 0.10986 | 12.3962 | -109.9548 | -110.0601 | 12.6892 | 12.7029 | 12.5839 | 0.3067 | 0.18768 | 0.29297 | 122.5113 | 0.29297 | 0.17853 | 122.9187 | 0.28381 | 122.7631 | 12.6801 | -122.7905 | -110.2386 | 122.3557 | 12.5748 | 12.7762 | 12.561
1333.9844 | 122.7768 | -13.0783 | 109.52 | 0.0034333 | 0.0041102 | 0.069586 | 0.066127 | 0.0035227 | -0.0015061 | 0.00029485 | 0.0046998 | 0.016665 | 0.021209 | 0.022802 | 0.0042341 | 0.01016 | 0.00073059 | 0.086975 | 109.7076 | -13.2797 | 109.1995 | -13.0142 | -13.2202 | -13.1744 | -0.032043 | 0.09613 | -0.15564 | 0.041199 | 0.10529 | 0.018311 | 0.15564 | -0.20142 | 0.18768 | -0.32043 | 0.064087 | -0.09613 | -0.14191 | 0.10529 | 0.059509 | 12.9227 | -109.4238 | -109.4788 | 13.1836 | 13.2339 | 13.0966 | 0.31128 | 0.17395 | 0.2655 | 122.4792 | 0.26093 | 0.19684 | 122.9874 | 0.25177 | 122.786 | 13.1744 | -122.7997 | -109.6756 | 122.2778 | 13.1195 | 13.1653 | 13.0463
1335.7188 | 122.7264 | -12.7075 | 109.9548 | -0.0041962 | 0.0043238 | 0.071508 | 0.06335 | 0.0022409 | -0.00022429 | 0.00072205 | 0.0046998 | 0.01282 | 0.018218 | 0.014471 | 0.0016705 | 0.010587 | -0.0018328 | 0.13733 | 110.1013 | -12.8632 | 109.584 | -12.6251 | -12.8174 | -12.7716 | -0.068665 | 0.10529 | -0.16937 | -0.036621 | 0.068665 | -0.018311 | 0.10071 | -0.15564 | 0.14648 | -0.37079 | 0.082398 | -0.064086 | -0.10986 | 0.091553 | 0.045776 | 12.5381 | -109.8495 | -109.9915 | 12.7762 | 12.8082 | 12.6892 | 0.27008 | 0.15106 | 0.23804 | 122.4472 | 0.23804 | 0.13275 | 122.9645 | 0.27466 | 122.8088 | 12.8128 | -122.818 | -110.1242 | 122.2916 | 12.6709 | 12.8448 | 12.6389
1337.4688 | 122.7951 | -12.4603 | 110.1471 | -0.0041962 | 0.0049646 | 0.070654 | 0.062709 | 0.00074554 | -0.0042831 | -0.0012006 | -0.0014038 | 0.012179 | 0.018859 | 0.023016 | -0.0015337 | 0.010801 | -0.00033761 | 0.1831 | 110.2524 | -12.648 | 109.8541 | -12.355 | -12.529 | -12.5061 | 0.009155 | 0.091553 | -0.17853 | 0.013733 | 0.11902 | 0.054932 | 0.17395 | -0.18768 | 0.10529 | -0.29297 | 0.10529 | -0.045777 | -0.068665 | 0.14191 | 0.11902 | 12.2818 | -110.0555 | -110.1334 | 12.5793 | 12.6343 | 12.5153 | 0.35248 | 0.23346 | 0.29297 | 122.5021 | 0.29755 | 0.19226 | 122.9004 | 0.27008 | 122.7127 | 12.5519 | -122.7951 | -110.3256 | 122.3145 | 12.4741 | 12.6434 | 12.4695
1339.1562 | 122.699 | -12.3642 | 110.3302 | 0.0034333 | 0.0077418 | 0.068517 | 0.0657 | 0.0048043 | -0.0034287 | 0.0013628 | 0.001648 | 0.01581 | 0.021209 | 0.017034 | -0.0013201 | 0.0056738 | -0.0022602 | 0.21515 | 110.4813 | -12.5427 | 109.9182 | -12.3367 | -12.4924 | -12.4603 | -0.10071 | 0.12817 | -0.1831 | -0.054932 | 0.036621 | -0.059509 | 0.07782 | -0.17853 | 0.15106 | -0.41199 | 0.027466 | -0.09613 | -0.12817 | 0.082398 | 0.050354 | 12.1811 | -110.202 | -110.3851 | 12.4008 | 12.442 | 12.3047 | 0.26092 | 0.1236 | 0.20599 | 122.4609 | 0.21973 | 0.12817 | 123.024 | 0.31128 | 122.8455 | 12.4924 | -122.8729 | -110.5133 | 122.2824 | 12.3093 | 12.5793 | 12.2635
1340.8906 | 122.6898 | -12.4786 | 110.2249 | 0.0034333 | 0.0036828 | 0.069372 | 0.064418 | 0.0043771 | -0.0023605 | -0.0014142 | 0.0046998 | 0.015169 | 0.021636 | 0.014044 | -0.00067933 | 0.006742 | -0.0039692 | 0.18768 | 110.3531 | -12.648 | 109.7717 | -12.4603 | -12.616 | -12.6068 | -0.13733 | 0.11444 | -0.19684 | -0.09613 | 0.009155 | -0.07782 | 0.068665 | -0.16937 | 0.12817 | -0.45319 | 0.018311 | -0.12817 | -0.13733 | 0.041198 | 0.032043 | 12.2818 | -110.1105 | -110.321 | 12.4878 | 12.5473 | 12.4008 | 0.2655 | 0.11902 | 0.18768 | 122.4197 | 0.20599 | 0.10071 | 123.0011 | 0.31128 | 122.8317 | 12.5931 | -122.8729 | -110.4218 | 122.2504 | 12.3825 | 12.6663 | 12.3413
1342.625 | 122.7127 | -12.9547 | 109.7076 | 0.011063 | 0.0058192 | 0.068945 | 0.066982 | 0.0039499 | -0.0038559 | -0.00077335 | 0.001648 | 0.014742 | 0.020995 | 0.020025 | -0.0013201 | 0.0073828 | -0.0024738 | 0.2243 | 109.9136 | -13.1149 | 109.3552 | -12.8769 | -13.0783 | -13.0417 | -0.068665 | 0.13275 | -0.17853 | -0.027466 | 0.068665 | -0.041199 | 0.09613 | -0.16022 | 0.20599 | -0.35248 | 0.07782 | -0.086975 | -0.1236 | 0.073242 | 0.036621 | 12.7762 | -109.5749 | -109.7351 | 13.0234 | 13.0508 | 12.9135 | 0.27466 | 0.13733 | 0.23804 | 122.4701 | 0.24719 | 0.15106 | 123.0286 | 0.31128 | 122.8683 | 13.0875 | -122.8226 | -109.8862 | 122.3099 | 12.9272 | 13.179 | 12.886
1344.3125 | 122.699 | -12.8311 | 109.8679 | 0.0034333 | 0.0036828 | 0.066595 | 0.065059 | 0.0050179 | -0.0062057 | -0.00034615 | 0.0046998 | 0.01581 | 0.022277 | 0.015112 | -0.0013201 | 0.0080236 | -0.00097841 | 0.16479 | 110.051 | -12.9776 | 109.4421 | -12.8036 | -12.9456 | -12.9181 | -0.14191 | 0.13733 | -0.20142 | -0.07782 | 0.027466 | -0.07782 | 0.064087 | -0.14648 | 0.1831 | -0.42572 | 0.027466 | -0.086975 | -0.11444 | 0.059509 | 0.032043 | 12.6297 | -109.7305 | -109.9457 | 12.8586 | 12.8952 | 12.7533 | 0.2655 | 0.1236 | 0.17395 | 122.4197 | 0.22888 | 0.1236 | 123.0286 | 0.33875 | 122.8821 | 12.9684 | -122.8455 | -110.0693 | 122.2733 | 12.7533 | 12.9959 | 12.6892
1346.0625 | 122.7356 | -12.6251 | 109.9915 | 0.011063 | 0.0038966 | 0.070226 | 0.063564 | -0.00010886 | -0.0017197 | 0.003499 | 0.010803 | 0.013247 | 0.022277 | 0.022375 | 0.0016705 | 0.0090918 | 0.00051699 | 0.073242 | 110.1608 | -12.7625 | 109.6939 | -12.5015 | -12.7396 | -12.6984 | -0.032043 | 0.086975 | -0.16937 | -0.004578 | 0.09613 | -0.009155 | 0.10529 | -0.13733 | 0.16937 | -0.29755 | 0.1236 | -0.073242 | -0.11444 | 0.064087 | 0.022888 | 12.4557 | -109.9045 | -109.996 | 12.7213 | 12.7304 | 12.616 | 0.27466 | 0.16022 | 0.26093 | 122.4564 | 0.2655 | 0.16479 | 122.9233 | 0.25635 | 122.7859 | 12.7121 | -122.7539 | -110.1608 | 122.319 | 12.6205 | 12.6984 | 12.5931
1347.8125 | 122.7859 | -12.6389 | 109.9915 | -0.0041962 | 0.0036828 | 0.069372 | 0.064204 | 0.0013863 | -0.0053513 | -0.0022688 | 0.0046998 | 0.011324 | 0.020354 | 0.017889 | -0.0017475 | 0.0086646 | -0.0026874 | 0.082397 | 110.1562 | -12.8082 | 109.6939 | -12.5107 | -12.6846 | -12.6709 | -0.004578 | 0.10071 | -0.15564 | 0.032043 | 0.14191 | 0.054932 | 0.16479 | -0.16937 | 0.16479 | -0.29755 | 0.12817 | -0.032043 | -0.045776 | 0.13733 | 0.1236 | 12.4832 | -109.8907 | -109.9594 | 12.7808 | 12.8036 | 12.6938 | 0.32044 | 0.21057 | 0.29755 | 122.5021 | 0.29755 | 0.18768 | 122.9645 | 0.25635 | 122.7951 | 12.7396 | -122.7997 | -110.1471 | 122.3328 | 12.6709 | 12.7213 | 12.6343
1349.5156 | 122.6852 | -12.5107 | 110.2112 | 0.0034333 | 0.0036828 | 0.067663 | 0.064632 | 0.0026681 | -0.0023605 | -0.0020552 | 0.0046998 | 0.013674 | 0.020354 | 0.014257 | -0.00025213 | 0.006742 | -0.0020464 | 0.21057 | 110.3989 | -12.6389 | 109.7763 | -12.4695 | -12.5977 | -12.5748 | -0.14191 | 0.13275 | -0.19684 | -0.10986 | 0.018311 | -0.073242 | 0.054932 | -0.12817 | 0.18768 | -0.43488 | 0.041199 | -0.064087 | -0.086975 | 0.064087 | 0.041199 | 12.3138 | -110.0784 | -110.321 | 12.529 | 12.5656 | 12.4374 | 0.25177 | 0.1236 | 0.16937 | 122.4152 | 0.21515 | 0.086975 | 123.0377 | 0.32959 | 122.9095 | 12.6434 | -122.85 | -110.408 | 122.287 | 12.4008 | 12.7213 | 12.3688
1351.2656 | 122.7676 | -12.2864 | 110.3302 | -0.0041962 | 0.0060328 | 0.069799 | 0.064845 | 0.0062997 | -0.0019333 | -0.00098695 | 0.001648 | 0.012606 | 0.020568 | 0.01853 | 0.0053021 | 0.009519 | 0.00030339 | 0.1236 | 110.5591 | -12.4695 | 109.9777 | -12.2269 | -12.4374 | -12.3825 | -0.041199 | 0.10071 | -0.16937 | 0.022888 | 0.09613 | 0 | 0.14648 | -0.1831 | 0.22888 | -0.35248 | 0.059509 | -0.09613 | -0.15106 | 0.086975 | 0.032043 | 12.117 | -110.2295 | -110.3073 | 12.3825 | 12.4329 | 12.2864 | 0.31586 | 0.16937 | 0.24261 | 122.4472 | 0.2655 | 0.19226 | 123.0286 | 0.27008 | 122.8455 | 12.3871 | -122.7997 | -110.4996 | 122.2641 | 12.3093 | 12.41 | 12.2452
1352.9375 | 122.6624 | -12.1445 | 110.582 | 0.0034333 | 0.0051782 | 0.069158 | 0.065486 | -0.0020315 | -0.0040695 | 0.00093565 | 0.001648 | 0.014742 | 0.022063 | 0.01853 | -0.0026019 | 0.0069556 | -0.00097841 | 0.13733 | 110.7422 | -12.2726 | 110.1242 | -12.085 | -12.2589 | -12.2223 | -0.15106 | 0.13275 | -0.19226 | -0.11444 | 0.009155 | -0.10071 | 0.041199 | -0.12817 | 0.16022 | -0.45776 | 0.059509 | -0.07782 | -0.11444 | 0.050354 | 0.013733 | 11.9522 | -110.4492 | -110.6964 | 12.1536 | 12.1857 | 12.0438 | 0.23346 | 0.091553 | 0.18768 | 122.3969 | 0.20142 | 0.07782 | 123.0148 | 0.32501 | 122.8867 | 12.2772 | -122.8546 | -110.7742 | 122.2687 | 12.03 | 12.2818 | 11.9934
1354.7031 | 122.6715 | -12.0163 | 110.733 | 0.011063 | 0.0058192 | 0.068731 | 0.0657 | 0.0022409 | -0.0074875 | 0.00029485 | 0.001648 | 0.014315 | 0.022917 | 0.015753 | -0.0030291 | 0.0071692 | -0.0014056 | 0.21973 | 110.8521 | -12.1399 | 110.321 | -11.8973 | -12.0712 | -12.0438 | -0.091553 | 0.1236 | -0.20599 | -0.086975 | 0.013733 | -0.082397 | 0.036621 | -0.1236 | 0.11902 | -0.41199 | 0.11902 | -0.027466 | -0.054932 | 0.096131 | 0.068665 | 11.8103 | -110.6094 | -110.82 | 12.03 | 12.0529 | 11.9339 | 0.24262 | 0.1236 | 0.24262 | 122.4609 | 0.21973 | 0.11902 | 122.9919 | 0.32959 | 122.8683 | 12.1399 | -122.8729 | -110.939 | 122.3373 | 11.9293 | 12.236 | 11.9247
1356.375 | 122.6578 | -11.7188 | 110.9802 | 0.0034333 | 0.0058192 | 0.069799 | 0.0657 | 0.0058725 | -0.0017197 | -0.00077335 | 0.0046998 | 0.017092 | 0.021209 | 0.0089166 | 0.0012433 | 0.0063148 | -0.00055121 | 0.26093 | 111.1221 | -11.9202 | 110.5133 | -11.7096 | -11.8973 | -11.8607 | -0.13733 | 0.11902 | -0.19684 | -0.086975 | -0.013733 | -0.1236 | 0.041199 | -0.20142 | 0.14191 | -0.46692 | 0.009155 | -0.14191 | -0.17853 | 0.059509 | 0.022888 | 11.5219 | -110.8612 | -111.0672 | 11.705 | 11.7599 | 11.5952 | 0.23804 | 0.073242 | 0.21057 | 122.4335 | 0.18311 | 0.10986 | 123.0423 | 0.31586 | 122.8409 | 11.8378 | -122.9004 | -111.1771 | 122.2321 | 11.6318 | 11.9797 | 11.5814
1358.125 | 122.7722 | -11.6272 | 111.026 | -0.0041962 | 0.004751 | 0.070654 | 0.062709 | 0.0037363 | -0.0040695 | 0.0020038 | 0.0046998 | 0.011111 | 0.020354 | 0.01853 | -0.00025213 | 0.0071692 | 0.003294 | 0.24261 | 111.1359 | -11.8332 | 110.6827 | -11.4853 | -11.6913 | -11.6684 | 0.027466 | 0.091553 | -0.16479 | 0.018311 | 0.15564 | 0.064087 | 0.15106 | -0.20599 | 0.10986 | -0.34332 | 0.14191 | -0.041199 | -0.064087 | 0.16479 | 0.14191 | 11.4624 | -110.9344 | -111.0077 | 11.7828 | 11.7783 | 11.6913 | 0.31586 | 0.22888 | 0.3479 | 122.5159 | 0.32044 | 0.18311 | 122.9691 | 0.25635 | 122.7631 | 11.7188 | -122.8592 | -111.1908 | 122.3099 | 11.6455 | 11.8698 | 11.6547
1359.8125 | 122.7997 | -11.6455 | 110.9848 | 0.0034333 | 0.0017602 | 0.068731 | 0.066127 | 0.0060861 | -0.0019333 | -0.00098695 | 0.001648 | 0.013888 | 0.021849 | 0.020879 | 0.0042341 | 0.0086646 | -0.0016192 | 0.19226 | 111.1404 | -11.8515 | 110.6598 | -11.554 | -11.7462 | -11.7233 | 0.004578 | 0.091553 | -0.16479 | 0.041199 | 0.10986 | 0.013733 | 0.16937 | -0.20599 | 0.15564 | -0.32501 | 0.091553 | -0.07782 | -0.10071 | 0.12817 | 0.10529 | 11.4807 | -110.8932 | -110.9436 | 11.7554 | 11.8149 | 11.6592 | 0.33417 | 0.17853 | 0.29755 | 122.5113 | 0.27466 | 0.20599 | 122.9919 | 0.25635 | 122.7859 | 11.7371 | -122.8363 | -111.1496 | 122.3053 | 11.6867 | 11.8378 | 11.6501
1361.5625 | 122.7173 | -11.6501 | 111.0443 | 0.0034333 | 0.0045374 | 0.069799 | 0.067195 | 0.0065133 | -0.0030015 | -0.00013235 | -0.0014038 | 0.013247 | 0.020781 | 0.015325 | 0.00017507 | 0.0088782 | -0.0048236 | 0.20599 | 111.1496 | -11.8744 | 110.6094 | -11.6272 | -11.8103 | -11.7691 | -0.091553 | 0.12817 | -0.17853 | -0.050354 | 0.050354 | -0.050354 | 0.082397 | -0.2243 | 0.10528 | -0.43488 | 0.022888 | -0.11902 | -0.16022 | 0.10529 | 0.064087 | 11.4716 | -110.9161 | -111.0947 | 11.7004 | 11.7325 | 11.5997 | 0.26092 | 0.12817 | 0.24719 | 122.4838 | 0.22888 | 0.12817 | 123.024 | 0.3067 | 122.7997 | 11.7783 | -122.9187 | -111.2228 | 122.2595 | 11.5997 | 11.8561 | 11.5585
1363.2344 | 122.6715 | -11.5723 | 111.1038 | -0.0041962 | 0.0028284 | 0.068945 | 0.06805 | 0.0056589 | -0.0023605 | 0.00093565 | 0.0046998 | 0.015383 | 0.021849 | 0.015966 | 0.00017507 | 0.0065284 | -0.0014056 | 0.26093 | 111.2686 | -11.7599 | 110.7376 | -11.467 | -11.6592 | -11.6364 | -0.064087 | 0.12817 | -0.16937 | -0.027466 | 0.050354 | -0.068665 | 0.07782 | -0.18768 | 0.16479 | -0.36621 | 0.10529 | -0.064087 | -0.086975 | 0.1236 | 0.10071 | 11.4029 | -110.9756 | -111.1313 | 11.6226 | 11.6501 | 11.5036 | 0.24719 | 0.10071 | 0.29297 | 122.4976 | 0.21973 | 0.14191 | 123.0286 | 0.29755 | 122.8409 | 11.7004 | -122.8638 | -111.2732 | 122.3099 | 11.5448 | 11.8332 | 11.5082
1365 | 122.7905 | -11.5723 | 111.0718 | 0.0034333 | 0.0053918 | 0.068945 | 0.062496 | 0.0035227 | -0.0036423 | -0.0022688 | 0.001648 | 0.012606 | 0.023986 | 0.020879 | -0.0023883 | 0.0073828 | -0.00012381 | 0.2243 | 111.2 | -11.7416 | 110.7422 | -11.4075 | -11.6226 | -11.6318 | 0.018311 | 0.10071 | -0.16022 | 0.022888 | 0.16022 | 0.059509 | 0.14648 | -0.16937 | 0.12817 | -0.32959 | 0.1648 | -0.059509 | -0.050354 | 0.10986 | 0.11902 | 11.412 | -110.9711 | -111.0489 | 11.7325 | 11.7188 | 11.6318 | 0.3067 | 0.21973 | 0.33417 | 122.4838 | 0.32043 | 0.1831 | 122.9416 | 0.26093 | 122.7722 | 11.673 | -122.8134 | -111.232 | 122.3145 | 11.5952 | 11.7966 | 11.5906
1366.6875 | 122.7905 | -11.5128 | 111.1313 | 0.011063 | 0.0043238 | 0.070013 | 0.064845 | 0.0045907 | -0.0027877 | -0.00013235 | 0.0046998 | 0.011751 | 0.019713 | 0.022161 | -0.00089293 | 0.0086646 | 0.00051699 | 0.21515 | 111.2412 | -11.705 | 110.7925 | -11.3846 | -11.5677 | -11.5631 | 0.009155 | 0.091553 | -0.15564 | 0.027466 | 0.15564 | 0.059509 | 0.16022 | -0.19226 | 0.10986 | -0.33875 | 0.12817 | -0.050354 | -0.054932 | 0.14191 | 0.13733 | 11.3571 | -111.0397 | -111.1038 | 11.6684 | 11.673 | 11.5723 | 0.31586 | 0.21515 | 0.32043 | 122.4976 | 0.31128 | 0.18311 | 122.9462 | 0.24719 | 122.7539 | 11.6043 | -122.8363 | -111.2869 | 122.3053 | 11.5402 | 11.7279 | 11.5219
1368.4375 | 122.7814 | -11.4944 | 111.145 | 0.011063 | 0.007528 | 0.068731 | 0.064845 | 0.00053194 | -0.0021469 | -0.0016278 | 0.001648 | 0.013033 | 0.020354 | 0.014044 | -0.0023883 | 0.00781 | 0.00030339 | 0.23804 | 111.2869 | -11.6959 | 110.8337 | -11.3617 | -11.5265 | -11.499 | -0.004578 | 0.091553 | -0.14191 | 0.018311 | 0.11902 | 0.032043 | 0.13733 | -0.20142 | 0.14191 | -0.31128 | 0.13275 | -0.004577 | -0.032043 | 0.19684 | 0.16937 | 11.3525 | -111.0535 | -111.1267 | 11.6135 | 11.6318 | 11.5265 | 0.27924 | 0.17395 | 0.33417 | 122.5296 | 0.26093 | 0.16022 | 122.9828 | 0.23346 | 122.7814 | 11.586 | -122.8409 | -111.2869 | 122.3282 | 11.5128 | 11.7325 | 11.4899
1370.125 | 122.6486 | -11.4487 | 111.2549 | 0.011063 | 0.0056054 | 0.072149 | 0.069118 | 0.0043771 | -0.0010789 | -0.00098695 | 0.001648 | 0.013888 | 0.023345 | 0.015325 | 0.0031659 | 0.0073828 | 0.0017988 | 0.19684 | 111.3556 | -11.6776 | 110.7193 | -11.4853 | -11.6821 | -11.6364 | -0.16479 | 0.11444 | -0.1831 | -0.09613 | -0.022888 | -0.13275 | 0.045776 | -0.22888 | 0.10071 | -0.53558 | -0.036622 | -0.18768 | -0.23346 | 0.041198 | -0.004578 | 11.2656 | -111.1404 | -111.351 | 11.4258 | 11.4944 | 11.3159 | 0.22888 | 0.050354 | 0.19226 | 122.3969 | 0.16022 | 0.086975 | 123.0331 | 0.29755 | 122.8043 | 11.5631 | -122.9324 | -111.438 | 122.168 | 11.3525 | 11.6455 | 11.2839
1371.875 | 122.7219 | -11.7004 | 110.9619 | 0.0034333 | 0.007528 | 0.070226 | 0.064418 | 0.0015999 | -0.0038559 | 0.00072205 | 0.001648 | 0.013888 | 0.020568 | 0.021307 | -0.0023883 | 0.0054602 | -0.00097841 | 0.23346 | 111.0306 | -11.9019 | 110.6049 | -11.5997 | -11.792 | -11.7737 | -0.041199 | 0.082397 | -0.16937 | -0.027466 | 0.064087 | -0.009155 | 0.10071 | -0.20142 | 0.068665 | -0.35706 | 0.10071 | -0.073243 | -0.091553 | 0.12817 | 0.10986 | 11.5311 | -110.8795 | -110.9894 | 11.7645 | 11.8011 | 11.6913 | 0.27008 | 0.16022 | 0.30212 | 122.5067 | 0.23346 | 0.14191 | 122.9324 | 0.25177 | 122.731 | 11.7828 | -122.8638 | -111.1313 | 122.3053 | 11.673 | 11.9339 | 11.6592
1373.5469 | 122.7264 | -11.6043 | 111.0397 | -0.011826 | 0.0034692 | 0.070867 | 0.063991 | 0.0018137 | -0.0044967 | 0.00072205 | 0.0046998 | 0.014101 | 0.020995 | 0.025366 | 0.00038887 | 0.0090918 | 0.0035078 | 0.14648 | 111.2091 | -11.7599 | 110.6827 | -11.5219 | -11.7096 | -11.6455 | -0.07782 | 0.09613 | -0.17395 | -0.045776 | 0.07782 | -0.022888 | 0.10986 | -0.15564 | 0.16937 | -0.35706 | 0.082397 | -0.041199 | -0.10529 | 0.11444 | 0.050354 | 11.4304 | -110.9436 | -111.0855 | 11.6821 | 11.7142 | 11.5814 | 0.28381 | 0.15106 | 0.23804 | 122.4426 | 0.25177 | 0.12817 | 122.9691 | 0.27008 | 122.8134 | 11.7004 | -122.7997 | -111.2137 | 122.287 | 11.5585 | 11.7508 | 11.5265
1375.2812 | 122.8043 | -11.5219 | 111.1313 | 0.0034333 | 0.0034692 | 0.070226 | 0.063136 | 0.00031834 | -0.00086509 | -0.0024824 | 0.0046998 | 0.01346 | 0.021422 | 0.021734 | 0.00060247 | 0.0075964 | 8.9786e-05 | 0.16479 | 111.2503 | -11.7142 | 110.7742 | -11.412 | -11.5997 | -11.5494 | -0.009155 | 0.082397 | -0.17853 | 0.032043 | 0.13275 | 0.036621 | 0.13275 | -0.19226 | 0.11902 | -0.35706 | 0.10986 | -0.027465 | -0.077819 | 0.16479 | 0.11444 | 11.3434 | -111.0489 | -111.0992 | 11.6547 | 11.6547 | 11.5585 | 0.31128 | 0.21515 | 0.30212 | 122.4884 | 0.31128 | 0.21057 | 122.9645 | 0.26092 | 122.7722 | 11.6043 | -122.8455 | -111.3098 | 122.2961 | 11.554 | 11.6867 | 11.5128
1377.0469 | 122.6715 | -11.5631 | 111.1313 | 0.0034333 | 0.0073144 | 0.068517 | 0.063777 | 0.0039499 | -0.0027877 | -0.00013235 | 0.0046998 | 0.014529 | 0.021422 | 0.013403 | -0.0023883 | 0.006742 | 0.00051699 | 0.19684 | 111.3052 | -11.6821 | 110.7605 | -11.4304 | -11.618 | -11.5906 | -0.11444 | 0.12817 | -0.1831 | -0.091553 | 0.022888 | -0.091553 | 0.050354 | -0.11902 | 0.17395 | -0.37079 | 0.13275 | -0.027466 | -0.054932 | 0.091553 | 0.064087 | 11.38 | -111.0031 | -111.2228 | 11.586 | 11.6135 | 11.4716 | 0.23346 | 0.091552 | 0.25177 | 122.4426 | 0.20599 | 0.091552 | 122.9874 | 0.31128 | 122.8683 | 11.6913 | -122.8134 | -111.3144 | 122.3236 | 11.4716 | 11.7599 | 11.4487
1378.7969 | 122.7356 | -11.467 | 111.1954 | -0.0041962 | 0.0053918 | 0.067877 | 0.065059 | 0.0022409 | -0.0023605 | -0.0014142 | 0.0046998 | 0.011538 | 0.020781 | 0.023229 | 0.0016705 | 0.006742 | 0.00073059 | 0.17853 | 111.3876 | -11.5906 | 110.8566 | -11.348 | -11.5356 | -11.4853 | -0.082397 | 0.091553 | -0.17853 | -0.013733 | 0.064087 | -0.032043 | 0.10529 | -0.1236 | 0.19226 | -0.33875 | 0.11902 | -0.018311 | -0.068665 | 0.10529 | 0.054931 | 11.2885 | -111.1038 | -111.2091 | 11.5311 | 11.5723 | 11.4349 | 0.28381 | 0.14648 | 0.24262 | 122.4472 | 0.24261 | 0.16479 | 122.9782 | 0.27008 | 122.8546 | 11.5585 | -122.7859 | -111.3739 | 122.3236 | 11.4532 | 11.6455 | 11.3846
1380.4844 | 122.699 | -11.5036 | 111.2091 | -0.011826 | 0.0045374 | 0.069372 | 0.068691 | 0.0020273 | -0.0023605 | 0.0017902 | 0.0046998 | 0.01581 | 0.021636 | 0.015966 | -3.8532e-05 | 0.0088782 | 0.00051699 | 0.1831 | 111.3602 | -11.6867 | 110.788 | -11.4304 | -11.5952 | -11.5768 | -0.091553 | 0.11902 | -0.19226 | -0.041199 | 0.041199 | -0.054932 | 0.09613 | -0.18311 | 0.15106 | -0.42114 | 0.073242 | -0.073242 | -0.091553 | 0.10986 | 0.091553 | 11.3113 | -111.0901 | -111.2503 | 11.5448 | 11.5997 | 11.4487 | 0.28839 | 0.13733 | 0.25635 | 122.4747 | 0.23346 | 0.15106 | 123.0469 | 0.31128 | 122.8638 | 11.6226 | -122.8958 | -111.4014 | 122.2916 | 11.4624 | 11.6867 | 11.412
1382.2344 | 122.7448 | -11.7554 | 110.8841 | 0.0034333 | 0.0071008 | 0.068945 | 0.064204 | 0.0067269 | -0.0017197 | 0.0013628 | 0.0046998 | 0.01346 | 0.021422 | 0.022375 | 0.0018841 | 0.0090918 | 0.0011578 | 0.10529 | 110.9894 | -11.9568 | 110.5041 | -11.6867 | -11.8973 | -11.8561 | -0.004578 | 0.091553 | -0.17395 | 0.009155 | 0.10071 | -0.004578 | 0.10529 | -0.20142 | 0.10529 | -0.37994 | 0.068664 | -0.10071 | -0.14191 | 0.10071 | 0.059509 | 11.5814 | -110.7925 | -110.8749 | 11.8561 | 11.8607 | 11.7508 | 0.27924 | 0.16937 | 0.27008 | 122.4609 | 0.27466 | 0.1831 | 122.9462 | 0.2655 | 122.7448 | 11.8469 | -122.8409 | -111.058 | 122.2595 | 11.7645 | 11.8607 | 11.7508
1383.9844 | 122.7722 | -11.586 | 111.0535 | 0.0034333 | 0.0049646 | 0.069586 | 0.062282 | 0.0024545 | -0.0027877 | -0.0022688 | 0.001648 | 0.011965 | 0.019927 | 0.023443 | 0.00081607 | 0.0082374 | 0.0028668 | 0.14191 | 111.2503 | -11.7462 | 110.701 | -11.499 | -11.6913 | -11.6364 | -0.068665 | 0.09613 | -0.16479 | -0.004578 | 0.10071 | 0.009155 | 0.11902 | -0.16022 | 0.19684 | -0.35248 | 0.086976 | -0.050354 | -0.10529 | 0.10986 | 0.054932 | 11.4212 | -110.9573 | -111.058 | 11.6867 | 11.705 | 11.5952 | 0.28381 | 0.17395 | 0.24719 | 122.4472 | 0.2655 | 0.16022 | 122.9965 | 0.26092 | 122.8363 | 11.6821 | -122.7997 | -111.2183 | 122.287 | 11.5814 | 11.7279 | 11.5173
1385.7188 | 122.699 | -11.7096 | 110.9619 | 0.011063 | 0.0058192 | 0.069799 | 0.064632 | 0.0054453 | -0.0032151 | -0.00034615 | 0.001648 | 0.01581 | 0.02014 | 0.0091302 | -3.8532e-05 | 0.006742 | 0.003294 | 0.20599 | 111.1221 | -11.9385 | 110.527 | -11.6821 | -11.8607 | -11.8378 | -0.082397 | 0.14648 | -0.19226 | -0.041199 | 0.059509 | -0.07782 | 0.10986 | -0.22888 | 0.16022 | -0.43487 | 0.027466 | -0.12817 | -0.15106 | 0.10071 | 0.07782 | 11.5173 | -110.8154 | -111.0031 | 11.7691 | 11.8195 | 11.6318 | 0.30212 | 0.11444 | 0.25635 | 122.4655 | 0.25177 | 0.15106 | 123.0606 | 0.33874 | 122.8317 | 11.8561 | -122.9004 | -111.1542 | 122.2366 | 11.6684 | 11.9156 | 11.6272
1387.4062 | 122.7905 | -11.4761 | 111.1404 | 0.011063 | 0.0051782 | 0.069158 | 0.064845 | -0.0033133 | -0.0015061 | -0.0022688 | 0.0046998 | 0.015169 | 0.020995 | 0.021093 | -3.8532e-05 | 0.0080236 | 0.001585 | 0.21057 | 111.3007 | -11.6409 | 110.8429 | -11.3388 | -11.5356 | -11.4944 | 0.018311 | 0.091553 | -0.15106 | 0.036621 | 0.14191 | 0.064087 | 0.15564 | -0.1648 | 0.16022 | -0.29755 | 0.13733 | -0.018311 | -0.05951 | 0.14648 | 0.10529 | 11.3251 | -111.0489 | -111.1038 | 11.618 | 11.6318 | 11.5402 | 0.3067 | 0.21515 | 0.30212 | 122.4838 | 0.29297 | 0.18768 | 122.9416 | 0.24261 | 122.7768 | 11.5677 | -122.7814 | -111.2915 | 122.319 | 11.5128 | 11.6867 | 11.4944
1389.1719 | 122.6578 | -11.6547 | 111.0764 | -0.0041962 | 0.0053918 | 0.07044 | 0.067622 | 0.0041635 | -0.0036423 | 0.00072205 | 0.0046998 | 0.016024 | 0.023772 | 0.015966 | 0.00081607 | 0.0075964 | -0.0024738 | 0.17853 | 111.2732 | -11.8011 | 110.5957 | -11.5997 | -11.7783 | -11.7279 | -0.12817 | 0.12817 | -0.1831 | -0.086975 | -0.009155 | -0.10071 | 0.054932 | -0.14648 | 0.19684 | -0.48065 | 0.054932 | -0.073242 | -0.1236 | 0.073242 | 0.022888 | 11.4716 | -110.9482 | -111.1633 | 11.6455 | 11.7096 | 11.554 | 0.23804 | 0.082397 | 0.20142 | 122.3969 | 0.17395 | 0.09613 | 123.0743 | 0.31128 | 122.9279 | 11.7828 | -122.8775 | -111.2595 | 122.2504 | 11.5677 | 11.8332 | 11.5265
1390.8594 | 122.7264 | -11.3525 | 111.2915 | 0.0034333 | 0.0051782 | 0.070867 | 0.064845 | -0.00032266 | -0.0040695 | -0.0014142 | 0.0077514 | 0.01282 | 0.02249 | 0.017034 | -3.8532e-05 | 0.006742 | -0.00012381 | 0.19684 | 111.3876 | -11.5723 | 110.8932 | -11.2656 | -11.4944 | -11.4441 | -0.022888 | 0.091553 | -0.16022 | -0.018311 | 0.091553 | -0.018311 | 0.11444 | -0.21973 | 0.09613 | -0.39825 | 0.086975 | -0.091553 | -0.14191 | 0.12817 | 0.07782 | 11.1923 | -111.2 | -111.3098 | 11.4441 | 11.467 | 11.3342 | 0.27466 | 0.14191 | 0.3067 | 122.4655 | 0.25177 | 0.14191 | 122.9599 | 0.25177 | 122.7402 | 11.4441 | -122.8638 | -111.4517 | 122.2458 | 11.3342 | 11.5494 | 11.3297
1392.5938 | 122.7264 | -11.5585 | 111.0901 | -0.0041962 | 0.0062464 | 0.069799 | 0.063136 | 0.0043771 | -0.0053513 | -0.0024824 | 0.001648 | 0.013247 | 0.020781 | 0.015539 | -0.00089293 | 0.0093054 | 8.9786e-05 | 0.10071 | 111.2549 | -11.7188 | 110.733 | -11.4761 | -11.6501 | -11.5952 | -0.054932 | 0.09613 | -0.16479 | -0.032043 | 0.064087 | -0.018311 | 0.10986 | -0.16022 | 0.1648 | -0.35706 | 0.082398 | -0.036621 | -0.091552 | 0.1236 | 0.068665 | 11.3937 | -110.994 | -111.1221 | 11.6226 | 11.6684 | 11.5402 | 0.27466 | 0.14648 | 0.24262 | 122.4518 | 0.22888 | 0.13275 | 122.9736 | 0.26092 | 122.8134 | 11.6547 | -122.8088 | -111.2549 | 122.2916 | 11.5265 | 11.6592 | 11.5036
1394.3438 | 122.7951 | -11.4304 | 111.1954 | 0.0034333 | 0.0062464 | 0.073004 | 0.0657 | 0.0058725 | -0.0036423 | 8.125e-05 | 0.001648 | 0.015383 | 0.020354 | 0.017462 | 0.0046613 | 0.010374 | -0.0018328 | 0.16022 | 111.3739 | -11.6226 | 110.8795 | -11.3251 | -11.5265 | -11.5082 | -0.004578 | 0.082397 | -0.16022 | 0.050354 | 0.11902 | 0.018311 | 0.16937 | -0.19226 | 0.17853 | -0.31586 | 0.10529 | -0.07782 | -0.09613 | 0.11444 | 0.096131 | 11.2701 | -111.113 | -111.145 | 11.5494 | 11.5997 | 11.4487 | 0.32959 | 0.17853 | 0.29755 | 122.5021 | 0.27924 | 0.21057 | 122.9965 | 0.24261 | 122.8043 | 11.5128 | -122.818 | -111.3556 | 122.3099 | 11.4807 | 11.5906 | 11.4258
1396.0938 | 122.7905 | -11.4349 | 111.1954 | 0.0034333 | 0.0045374 | 0.069158 | 0.065273 | 0.0050179 | -0.0032151 | 0.0028582 | 0.001648 | 0.013033 | 0.022704 | 0.015966 | -0.0026019 | 0.00781 | -0.00012381 | 0.17853 | 111.3876 | -11.5265 | 110.9894 | -11.1832 | -11.3846 | -11.38 | 0.036621 | 0.086975 | -0.16022 | 0.032043 | 0.16022 | 0.059509 | 0.15106 | -0.091552 | 0.19226 | -0.20599 | 0.25177 | 0.054932 | 0.050354 | 0.14648 | 0.14191 | 11.2747 | -111.1084 | -111.1633 | 11.5952 | 11.586 | 11.4944 | 0.31128 | 0.21973 | 0.34332 | 122.5159 | 0.32043 | 0.19226 | 122.9141 | 0.24719 | 122.8226 | 11.5219 | -122.7219 | -111.3556 | 122.4243 | 11.467 | 11.6135 | 11.4716
1397.7812 | 122.7127 | -11.4532 | 111.232 | 0.018692 | 0.0043238 | 0.069158 | 0.064632 | 0.0028817 | -0.0036423 | -0.00077335 | 0.0046998 | 0.013888 | 0.019713 | 0.016393 | 0.00038887 | 0.0063148 | -0.0026874 | 0.2243 | 111.5158 | -11.5036 | 110.8932 | -11.3525 | -11.5311 | -11.5173 | -0.054932 | 0.1236 | -0.20142 | -0.036621 | 0.068665 | -0.045776 | 0.09613 | -0.050354 | 0.28381 | -0.33875 | 0.10071 | -0.064087 | -0.07782 | -0.013733 | -0.027466 | 11.2518 | -111.1084 | -111.2686 | 11.5219 | 11.5494 | 11.4075 | 0.29755 | 0.15564 | 0.15106 | 122.3969 | 0.27008 | 0.1648 | 123.0194 | 0.32501 | 122.9691 | 11.5768 | -122.7356 | -111.4334 | 122.3465 | 11.4166 | 11.6776 | 11.3983
1399.5469 | 122.6852 | -11.4532 | 111.2228 | 0.0034333 | 0.00646 | 0.070013 | 0.064845 | 0.00010474 | -0.0036423 | 0.00029485 | -0.0014038 | 0.01282 | 0.021209 | 0.021307 | -0.0019611 | 0.006742 | -0.00076481 | 0.37537 | 111.3831 | -11.586 | 110.8566 | -11.2976 | -11.4441 | -11.467 | -0.064087 | 0.10529 | -0.17853 | -0.050354 | 0.054932 | -0.041199 | 0.07782 | -0.13275 | 0.16022 | -0.36621 | 0.15564 | -0.013733 | 0.009155 | 0.11902 | 0.14191 | 11.2747 | -111.1176 | -111.2732 | 11.5082 | 11.5311 | 11.412 | 0.25635 | 0.13733 | 0.28839 | 122.4426 | 0.23346 | 0.12817 | 122.9691 | 0.28381 | 122.8363 | 11.5585 | -122.8088 | -111.4014 | 122.3099 | 11.4029 | 11.8286 | 11.3892
1401.2969 | 122.7859 | -11.3159 | 111.3007 | 0.0034333 | 0.00646 | 0.070226 | 0.066554 | 0.00095914 | -0.0036423 | 8.125e-05 | 0.0077514 | 0.014529 | 0.020995 | 0.015325 | 0.0048749 | 0.0090918 | 0.0030804 | 0.33417 | 111.5112 | -11.4944 | 110.9985 | -11.1877 | -11.4075 | -11.3663 | -0.004578 | 0.091553 | -0.16937 | 0.054932 | 0.1236 | 0.004578 | 0.16022 | -0.17853 | 0.21057 | -0.30212 | 0.12817 | -0.050354 | -0.091553 | 0.12817 | 0.086975 | 11.1465 | -111.2091 | -111.2457 | 11.4395 | 11.4761 | 11.3205 | 0.32959 | 0.17395 | 0.3067 | 122.493 | 0.29297 | 0.22431 | 123.0057 | 0.26093 | 122.8271 | 11.4075 | -122.7951 | -111.47 | 122.3145 | 11.3709 | 11.6501 | 11.3113
1402.9688 | 122.7264 | -11.348 | 111.3281 | 0.0034333 | 0.0068872 | 0.070226 | 0.065486 | 0.0056589 | -0.0023605 | -0.0029096 | 0.001648 | 0.016024 | 0.019927 | 0.015325 | -0.0017475 | 0.0069556 | -0.00097841 | 0.39368 | 111.4792 | -11.5356 | 110.9344 | -11.2793 | -11.4853 | -11.4853 | -0.068665 | 0.1236 | -0.18768 | -0.050354 | 0.059509 | -0.045776 | 0.086975 | -0.18768 | 0.15106 | -0.39368 | 0.068664 | -0.13733 | -0.13733 | 0.050354 | 0.050354 | 11.1603 | -111.2045 | -111.3785 | 11.4075 | 11.4349 | 11.3022 | 0.27466 | 0.14191 | 0.25635 | 122.4701 | 0.24719 | 0.13733 | 123.0148 | 0.31128 | 122.8271 | 11.4716 | -122.8638 | -111.5158 | 122.2824 | 11.2976 | 11.7416 | 11.2793
1404.7188 | 122.7905 | -11.4304 | 111.2045 | 0.0034333 | 0.0062464 | 0.073217 | 0.065273 | 0.0084359 | -0.0032151 | 0.00050845 | 0.0046998 | 0.012392 | 0.021422 | 0.01853 | 0.0012433 | 0.0086646 | -0.00055121 | 0.27924 | 111.4059 | -11.586 | 110.907 | -11.2656 | -11.499 | -11.4578 | 0.018311 | 0.082397 | -0.14648 | 0.041199 | 0.12817 | 0.009155 | 0.13733 | -0.15564 | 0.20142 | -0.29755 | 0.16479 | -0.027466 | -0.068664 | 0.12817 | 0.086976 | 11.2839 | -111.1221 | -111.1633 | 11.5585 | 11.5677 | 11.4395 | 0.28381 | 0.15564 | 0.32043 | 122.493 | 0.27466 | 0.18768 | 122.9919 | 0.22888 | 122.8363 | 11.5128 | -122.7905 | -111.351 | 122.3373 | 11.4716 | 11.7096 | 11.4487
1406.4688 | 122.6944 | -11.348 | 111.3419 | 0.018692 | 0.0051782 | 0.068945 | 0.066554 | 0.0060861 | -0.0044967 | 0.00072205 | 0.001648 | 0.012392 | 0.022063 | 0.019384 | 0.0040205 | 0.009519 | 0.0035078 | 0.24261 | 111.5387 | -11.5128 | 110.907 | -11.3022 | -11.4944 | -11.4487 | -0.11444 | 0.12817 | -0.19684 | -0.073242 | 0.009155 | -0.10986 | 0.050354 | -0.16479 | 0.19684 | -0.43488 | 0.045776 | -0.10071 | -0.14649 | 0.064087 | 0.01831 | 11.1511 | -111.2137 | -111.4151 | 11.3571 | 11.3983 | 11.2381 | 0.24719 | 0.086975 | 0.21057 | 122.4197 | 0.20599 | 0.1236 | 123.0515 | 0.32501 | 122.8867 | 11.4761 | -122.8546 | -111.5387 | 122.2549 | 11.2747 | 11.5906 | 11.2335
1408.2188 | 122.7356 | -11.2839 | 111.4197 | 0.0034333 | 0.0038966 | 0.071081 | 0.068691 | 0.0080087 | 0.0014847 | -0.0012006 | 0.001648 | 0.013033 | 0.02014 | 0.016393 | 0.0010297 | 0.006101 | -0.002901 | 0.18768 | 111.644 | -11.4441 | 111.0214 | -11.2152 | -11.412 | -11.3617 | -0.10529 | 0.10529 | -0.18768 | -0.032043 | 0.050354 | -0.059509 | 0.086975 | -0.16022 | 0.2243 | -0.39826 | 0.068665 | -0.077819 | -0.12817 | 0.082398 | 0.032044 | 11.0962 | -111.3144 | -111.4517 | 11.3342 | 11.3709 | 11.2244 | 0.27466 | 0.12817 | 0.22888 | 122.4655 | 0.23804 | 0.15564 | 123.0881 | 0.29297 | 122.9279 | 11.3892 | -122.8638 | -111.6074 | 122.3053 | 11.2518 | 11.4716 | 11.1786
1409.9844 | 122.6486 | -11.348 | 111.3739 | 0.011063 | 0.0079554 | 0.070226 | 0.0657 | 0.0033089 | -0.0027877 | 0.0013628 | 0.001648 | 0.015383 | 0.023131 | 0.012548 | -0.0013201 | 0.0065284 | -0.00076481 | 0.27466 | 111.5753 | -11.5265 | 110.8154 | -11.4166 | -11.5768 | -11.5448 | -0.16479 | 0.11444 | -0.19684 | -0.09613 | -0.036621 | -0.13275 | 0.022888 | -0.17853 | 0.20142 | -0.55847 | -0.068665 | -0.19684 | -0.22888 | -0.018311 | -0.050354 | 11.1511 | -111.2595 | -111.47 | 11.3113 | 11.3708 | 11.2152 | 0.21973 | 0.064087 | 0.10986 | 122.3419 | 0.16022 | 0.10071 | 123.1018 | 0.31128 | 122.9233 | 11.4624 | -122.9004 | -111.5707 | 122.1634 | 11.2518 | 11.6226 | 11.1832
1411.7344 | 122.6761 | -11.4487 | 111.3007 | -0.0041962 | 0.0041102 | 0.06809 | 0.066554 | -0.00053626 | -0.0030015 | -0.00077335 | 0.0046998 | 0.011538 | 0.020781 | 0.011053 | -0.0060199 | 0.0073828 | 0.0011578 | 0.24719 | 111.4151 | -11.5952 | 110.8566 | -11.3297 | -11.5082 | -11.4944 | -0.1236 | 0.13275 | -0.19684 | -0.09613 | 0.009155 | -0.064087 | 0.032043 | -0.14649 | 0.11444 | -0.44403 | 0.11902 | -0.045777 | -0.05951 | 0.10071 | 0.086975 | 11.2518 | -111.1679 | -111.3968 | 11.4578 | 11.4807 | 11.3846 | 0.22888 | 0.13275 | 0.2655 | 122.4518 | 0.20599 | 0.10071 | 123.0103 | 0.32959 | 122.8638 | 11.5814 | -122.8958 | -111.4975 | 122.3053 | 11.3525 | 11.6959 | 11.3251
1413.4219 | 122.6578 | -11.2885 | 111.438 | 0.0034333 | 0.0062464 | 0.071508 | 0.06805 | 0.0075815 | -0.0021469 | 0.0026446 | 0.001648 | 0.015169 | 0.023986 | 0.015753 | 0.00081607 | 0.0073828 | 0.001585 | 0.23346 | 111.6806 | -11.3983 | 110.9848 | -11.2106 | -11.3571 | -11.3022 | -0.15564 | 0.13275 | -0.21515 | -0.10071 | -0.050354 | -0.14191 | 0.054932 | -0.10986 | 0.24262 | -0.45319 | 0.07782 | -0.013733 | -0.068665 | 0.09613 | 0.041198 | 11.0733 | -111.3052 | -111.5387 | 11.2381 | 11.3434 | 11.1465 | 0.27008 | 0.073242 | 0.18768 | 122.3831 | 0.16479 | 0.11444 | 123.0789 | 0.3479 | 122.9691 | 11.4212 | -122.8363 | -111.6531 | 122.2733 | 11.1877 | 11.5219 | 11.1328
1415.1719 | 122.6898 | -11.3617 | 111.3876 | -0.011826 | 0.0053918 | 0.070226 | 0.064632 | 0.00095914 | -0.0042831 | -0.00055975 | 0.001648 | 0.015597 | 0.021849 | 0.012762 | -0.0013201 | 0.0075964 | 0.0011578 | 0.24261 | 111.5662 | -11.4853 | 110.9894 | -11.2335 | -11.3983 | -11.38 | -0.13275 | 0.14191 | -0.21057 | -0.086975 | 0.018311 | -0.082397 | 0.059509 | -0.1236 | 0.17853 | -0.39825 | 0.12817 | -0.018311 | -0.036621 | 0.10529 | 0.086976 | 11.1511 | -111.2457 | -111.4746 | 11.38 | 11.4212 | 11.2793 | 0.27008 | 0.12817 | 0.25177 | 122.4747 | 0.22888 | 0.1236 | 123.0515 | 0.35248 | 122.9279 | 11.5036 | -122.8729 | -111.5982 | 122.3511 | 11.2747 | 11.6043 | 11.2289
1416.8594 | 122.8134 | -11.2793 | 111.3464 | 0.011063 | 0.0056054 | 0.069799 | 0.064845 | 0.0077951 | -0.0015061 | 0.00029485 | -0.0014038 | 0.014742 | 0.018859 | 0.01853 | 0.0050885 | 0.010587 | -0.0037554 | 0.23346 | 111.5387 | -11.412 | 111.0626 | -11.142 | -11.3571 | -11.3159 | 0.013733 | 0.064087 | -0.15564 | 0.041199 | 0.13275 | 0.009155 | 0.14648 | -0.13275 | 0.19226 | -0.28381 | 0.13733 | -0.036621 | -0.07782 | 0.09613 | 0.054931 | 11.1237 | -111.2823 | -111.3052 | 11.412 | 11.4258 | 11.2885 | 0.30212 | 0.16479 | 0.27008 | 122.4747 | 0.28839 | 0.19684 | 122.9507 | 0.21973 | 122.818 | 11.3434 | -122.7585 | -111.5021 | 122.3419 | 11.3205 | 11.5128 | 11.293
1418.6094 | 122.7585 | -11.2793 | 111.3968 | 0.011063 | 0.0068872 | 0.070013 | 0.063564 | 0.0024545 | -0.0042831 | 0.00093565 | 0.0077514 | 0.014529 | 0.021849 | 0.012762 | 0.0010297 | 0.0097326 | -0.002901 | 0.23346 | 111.5204 | -11.4441 | 111.0214 | -11.1557 | -11.412 | -11.3617 | -0.009155 | 0.086975 | -0.16479 | 0.004578 | 0.07782 | -0.022888 | 0.10986 | -0.16479 | 0.1236 | -0.37537 | 0.1236 | -0.082397 | -0.13275 | 0.082398 | 0.032044 | 11.1145 | -111.3098 | -111.3922 | 11.3571 | 11.3892 | 11.2564 | 0.27466 | 0.14191 | 0.28839 | 122.4655 | 0.24261 | 0.16937 | 122.9645 | 0.25177 | 122.7997 | 11.3663 | -122.8409 | -111.5616 | 122.3007 | 11.2839 | 11.5128 | 11.2701
1420.2969 | 122.7631 | -11.5036 | 111.1725 | 0.0034333 | 0.0062464 | 0.069586 | 0.065913 | 0.0035227 | -0.0023605 | -0.00034615 | 0.0046998 | 0.01047 | 0.020781 | 0.023443 | -0.00025213 | 0.0073828 | 0.0017988 | 0.24261 | 111.3556 | -11.6318 | 110.8429 | -11.348 | -11.5494 | -11.5128 | -0.022888 | 0.10529 | -0.16937 | -0.022888 | 0.068665 | -0.018311 | 0.09613 | -0.12817 | 0.18311 | -0.32959 | 0.15564 | -0.009155 | -0.045776 | 0.11902 | 0.082398 | 11.3342 | -111.0672 | -111.1954 | 11.5723 | 11.5997 | 11.4853 | 0.2655 | 0.15106 | 0.28381 | 122.4747 | 0.23804 | 0.14649 | 122.9874 | 0.27466 | 122.8592 | 11.6089 | -122.8043 | -111.3419 | 122.3465 | 11.4807 | 11.7462 | 11.4807
1422.0469 | 122.7127 | -11.3709 | 111.3281 | 0.0034333 | 0.0062464 | 0.069799 | 0.067836 | 0.0024545 | -0.0032151 | -0.00055975 | 0.0046998 | 0.014315 | 0.023131 | 0.012762 | -0.00067933 | 0.00781 | -0.00055121 | 0.28381 | 111.525 | -11.5265 | 110.9482 | -11.2885 | -11.4258 | -11.3983 | -0.068665 | 0.12817 | -0.17853 | -0.050354 | 0.045776 | -0.059509 | 0.086975 | -0.15564 | 0.19684 | -0.37994 | 0.082398 | -0.027465 | -0.054931 | 0.12817 | 0.10071 | 11.1923 | -111.2 | -111.3785 | 11.4166 | 11.4578 | 11.3113 | 0.2655 | 0.11902 | 0.23804 | 122.4747 | 0.2243 | 0.12817 | 123.0515 | 0.3067 | 122.8958 | 11.499 | -122.8546 | -111.5067 | 122.319 | 11.3205 | 11.6547 | 11.3022
1423.7344 | 122.7859 | -11.4075 | 111.2503 | 0.0034333 | 0.0043238 | 0.067022 | 0.0657 | 0.0022409 | -0.0036423 | -0.0016278 | 0.001648 | 0.01282 | 0.020354 | 0.018743 | 0.00017507 | 0.0088782 | 0.00030339 | 0.15106 | 111.4426 | -11.5494 | 110.9207 | -11.3434 | -11.4761 | -11.4258 | -0.050354 | 0.10529 | -0.17395 | -0.004578 | 0.11902 | 0.032043 | 0.13275 | -0.14191 | 0.19226 | -0.32959 | 0.064087 | -0.01831 | -0.068664 | 0.1236 | 0.073242 | 11.2335 | -111.145 | -111.2549 | 11.5265 | 11.5402 | 11.4395 | 0.3067 | 0.20599 | 0.20599 | 122.4701 | 0.29297 | 0.16937 | 122.9919 | 0.27924 | 122.85 | 11.5128 | -122.7997 | -111.4243 | 122.3282 | 11.4029 | 11.5585 | 11.3571
1425.4844 | 122.6715 | -11.3297 | 111.3556 | 0.0034333 | 0.0045374 | 0.068517 | 0.064632 | 0.0041635 | -0.0027877 | -0.0012006 | 0.0046998 | 0.013247 | 0.021422 | 0.019598 | -0.0028155 | 0.006742 | -0.00055121 | 0.3067 | 111.5021 | -11.4899 | 110.9619 | -11.3068 | -11.4349 | -11.3983 | -0.11444 | 0.11444 | -0.20142 | -0.10071 | 0 | -0.091553 | 0.050354 | -0.16022 | 0.14648 | -0.39368 | 0.022888 | -0.068664 | -0.10529 | 0.091553 | 0.054931 | 11.1282 | -111.2412 | -111.4563 | 11.3297 | 11.38 | 11.2381 | 0.25177 | 0.10986 | 0.1831 | 122.4518 | 0.20142 | 0.10071 | 122.9919 | 0.31586 | 122.8317 | 11.4441 | -122.8455 | -111.557 | 122.2916 | 11.2289 | 11.6364 | 11.2152
1427.1719 | 122.7173 | -11.261 | 111.4014 | 0.011063 | 0.004751 | 0.068517 | 0.065486 | -0.00032266 | -0.0027877 | 0.002431 | 0.0046998 | 0.013033 | 0.019927 | 0.016393 | -0.0023883 | 0.0082374 | -0.00055121 | 0.14191 | 111.6165 | -11.4349 | 110.9436 | -11.3388 | -11.4441 | -11.4258 | -0.12817 | 0.11444 | -0.20599 | -0.068665 | 0.041199 | -0.059509 | 0.073242 | -0.17395 | 0.21515 | -0.45776 | -0.07782 | -0.16479 | -0.18311 | 0.009156 | -0.009155 | 11.055 | -111.2869 | -111.47 | 11.3022 | 11.3342 | 11.2015 | 0.27924 | 0.14649 | 0.096131 | 122.3785 | 0.24719 | 0.13733 | 123.0515 | 0.32044 | 122.8775 | 11.3754 | -122.8363 | -111.6074 | 122.2046 | 11.1923 | 11.4029 | 11.1328
1428.9062 | 122.7127 | -11.2061 | 111.5158 | 0.011063 | 0.0021876 | 0.070226 | 0.066554 | 0.0030953 | -0.0057785 | -0.00055975 | -0.0014038 | 0.01282 | 0.020995 | 0.016821 | -0.0013201 | 0.0063148 | -0.00097841 | 0.22888 | 111.644 | -11.4395 | 111.0397 | -11.2244 | -11.3388 | -11.3113 | -0.10071 | 0.10529 | -0.19684 | -0.045776 | 0.045776 | -0.054932 | 0.082397 | -0.23346 | 0.12817 | -0.47607 | -0.01831 | -0.10529 | -0.13275 | 0.12817 | 0.10071 | 11.0092 | -111.4105 | -111.5616 | 11.2518 | 11.2885 | 11.1511 | 0.27924 | 0.14191 | 0.21515 | 122.4792 | 0.24261 | 0.15106 | 123.0835 | 0.30212 | 122.85 | 11.3113 | -122.9553 | -111.7126 | 122.2458 | 11.1603 | 11.4349 | 11.1053
1430.6562 | 122.7997 | -11.087 | 111.5707 | 0.011063 | 0.0060328 | 0.071295 | 0.065273 | 0.0071541 | -0.0017197 | 0.00072205 | -0.0014038 | 0.011965 | 0.021849 | 0.01383 | 0.0035931 | 0.0088782 | -0.0024738 | 0.20142 | 111.6669 | -11.3022 | 111.2549 | -10.9955 | -11.174 | -11.1282 | 0.022888 | 0.082397 | -0.15106 | 0.045776 | 0.13733 | 0.018311 | 0.16479 | -0.21515 | 0.09613 | -0.31586 | 0.091553 | -0.041199 | -0.086975 | 0.17395 | 0.12817 | 10.936 | -111.4883 | -111.525 | 11.2244 | 11.2518 | 11.1053 | 0.31586 | 0.16937 | 0.3067 | 122.5571 | 0.28839 | 0.19684 | 122.9691 | 0.23346 | 122.7539 | 11.1694 | -122.8729 | -111.7218 | 122.3419 | 11.1328 | 11.2885 | 11.1099
1432.3438 | 122.6852 | -11.2061 | 111.5112 | 0.011063 | 0.0056054 | 0.068731 | 0.0657 | 0.0015999 | -0.0025741 | 0.0011492 | 0.010803 | 0.015597 | 0.021636 | 0.020239 | -0.0023883 | 0.0086646 | -0.00076481 | 0.29297 | 111.6898 | -11.3617 | 111.1221 | -11.1465 | -11.2885 | -11.2701 | -0.07782 | 0.1236 | -0.17853 | -0.059509 | 0.032043 | -0.09613 | 0.054932 | -0.15564 | 0.17853 | -0.3891 | 0.05951 | -0.064087 | -0.082397 | 0.091552 | 0.073242 | 11.0275 | -111.3876 | -111.5707 | 11.2381 | 11.261 | 11.1099 | 0.23346 | 0.082398 | 0.21515 | 122.4838 | 0.21057 | 0.11902 | 123.0515 | 0.30212 | 122.8958 | 11.3297 | -122.8729 | -111.6898 | 122.3282 | 11.1465 | 11.499 | 11.1282
1434.0781 | 122.7493 | -11.3617 | 111.2915 | 0.0034333 | 0.0051782 | 0.07044 | 0.066127 | 0.00031834 | -0.0010789 | -0.00098695 | 0.001648 | 0.011965 | 0.021636 | 0.010198 | -0.00025213 | 0.0075964 | 0.0035078 | 0.086975 | 111.4517 | -11.5219 | 110.9665 | -11.2701 | -11.4395 | -11.38 | -0.036621 | 0.082397 | -0.17853 | -0.009155 | 0.09613 | -0.004578 | 0.10529 | -0.16022 | 0.16022 | -0.32501 | 0.091552 | -0.018311 | -0.07782 | 0.14191 | 0.082398 | 11.1832 | -111.2091 | -111.3007 | 11.4578 | 11.467 | 11.3571 | 0.28381 | 0.17395 | 0.25177 | 122.4884 | 0.27466 | 0.16937 | 122.9736 | 0.26092 | 122.8134 | 11.4441 | -122.8134 | -111.47 | 122.3282 | 11.3525 | 11.4487 | 11.3251
1435.7656 | 122.8043 | -11.0779 | 111.5341 | -0.011826 | 0.0060328 | 0.070013 | 0.066554 | 0.0028817 | -0.0030015 | -0.0012006 | 0.001648 | 0.01282 | 0.019713 | 0.025152 | 0.0040205 | 0.0097326 | -0.00012381 | 0.27466 | 111.795 | -11.2381 | 111.2595 | -10.9817 | -11.1282 | -11.1053 | 0.013733 | 0.082397 | -0.17853 | 0.036621 | 0.1236 | 0.013733 | 0.16479 | -0.16022 | 0.26093 | -0.27466 | 0.096131 | -0.027466 | -0.050354 | 0.13275 | 0.10986 | 10.8994 | -111.4517 | -111.4975 | 11.2015 | 11.2427 | 11.0916 | 0.34332 | 0.19226 | 0.25635 | 122.4976 | 0.30212 | 0.21515 | 123.0331 | 0.26092 | 122.8729 | 11.1603 | -122.7722 | -111.7126 | 122.3373 | 11.1145 | 11.3525 | 11.0916
1437.5 | 122.6761 | -10.9772 | 111.7584 | 0.0034333 | 0.0045374 | 0.069799 | 0.064632 | 0.0054453 | -0.0036423 | -0.00077335 | -0.0014038 | 0.014956 | 0.021849 | 0.012335 | -0.0045245 | 0.0069556 | 0.003294 | 0.22888 | 111.8729 | -11.1603 | 111.264 | -11.0046 | -11.1145 | -11.1008 | -0.13733 | 0.1236 | -0.18768 | -0.10986 | 0.009155 | -0.09613 | 0.036621 | -0.1831 | 0.11444 | -0.49438 | -0.027466 | -0.1236 | -0.13733 | 0.059509 | 0.045776 | 10.7895 | -111.6348 | -111.8683 | 10.9863 | 11.0138 | 10.881 | 0.2243 | 0.091553 | 0.15564 | 122.4243 | 0.19684 | 0.07782 | 123.0331 | 0.31128 | 122.85 | 11.1008 | -122.9187 | -111.9461 | 122.2412 | 10.8673 | 11.2061 | 10.8398
1439.25 | 122.6852 | -11.1374 | 111.5753 | 0.0034333 | 0.0060328 | 0.068945 | 0.065913 | 0.0011727 | -0.0025741 | 0.0013628 | 0.0077514 | 0.014742 | 0.021849 | 0.011907 | 0.00038887 | 0.00781 | -0.0020464 | 0.28839 | 111.8179 | -11.2198 | 111.2091 | -11.0641 | -11.2061 | -11.2473 | -0.11444 | 0.1236 | -0.19684 | -0.07782 | 0.004578 | -0.11902 | 0.045776 | -0.082398 | 0.24262 | -0.36621 | 0.073242 | -0.10986 | -0.068665 | -0.027465 | 0.013733 | 10.9406 | -111.4517 | -111.6531 | 11.142 | 11.1832 | 11.0184 | 0.24261 | 0.077819 | 0.15564 | 122.4289 | 0.20142 | 0.11902 | 123.0377 | 0.32043 | 122.9553 | 11.261 | -122.7951 | -111.7722 | 122.3465 | 11.0596 | 11.4258 | 11.0229
1441.0156 | 122.8271 | -11.0046 | 111.6486 | 0.011063 | 0.0049646 | 0.07044 | 0.0657 | 0.0024545 | -0.0044967 | -0.00034615 | 0.001648 | 0.011965 | 0.020995 | 0.022375 | -0.00067933 | 0.010374 | 0.003935 | 0.24261 | 111.7035 | -11.293 | 111.2503 | -10.9543 | -11.1099 | -11.0458 | 0.013733 | 0.082397 | -0.16479 | 0.022888 | 0.14648 | 0.068665 | 0.15564 | -0.28839 | 0.054931 | -0.39826 | 0.050354 | -0.041198 | -0.10529 | 0.24719 | 0.18311 | 10.8398 | -111.5662 | -111.6257 | 11.1511 | 11.1603 | 11.0733 | 0.32044 | 0.23346 | 0.33874 | 122.5433 | 0.31128 | 0.18768 | 122.9965 | 0.24719 | 122.7081 | 11.087 | -122.9416 | -111.8134 | 122.2549 | 11.0275 | 11.2473 | 11.0184
1442.7031 | 122.8271 | -10.817 | 111.8591 | 0.011063 | 0.0028284 | 0.070226 | 0.063777 | 0.00095914 | -0.0030015 | 0.00072205 | -0.0014038 | 0.011538 | 0.0195 | 0.024084 | -0.0011065 | 0.0063148 | 0.00073059 | 0.29755 | 111.9324 | -11.0641 | 111.4471 | -10.7712 | -10.9222 | -10.8902 | 0.027466 | 0.082397 | -0.16937 | 0.036621 | 0.16022 | 0.064087 | 0.15564 | -0.24719 | 0.073242 | -0.41199 | 0.045777 | -0.073242 | -0.10529 | 0.17395 | 0.14191 | 10.6476 | -111.7767 | -111.8225 | 10.9772 | 10.9726 | 10.881 | 0.32501 | 0.23346 | 0.29297 | 122.5113 | 0.32959 | 0.20599 | 122.9965 | 0.25177 | 122.7493 | 10.8994 | -122.9233 | -112.0285 | 122.2641 | 10.8536 | 11.1145 | 10.8444
1444.4531 | 122.6807 | -10.7895 | 111.9781 | -0.0041962 | 0.0049646 | 0.069372 | 0.064845 | 0.0035227 | -0.0027877 | -0.0016278 | 0.001648 | 0.015169 | 0.023131 | 0.020666 | -0.0017475 | 0.0069556 | -0.00076481 | 0.28381 | 112.1521 | -10.9451 | 111.5112 | -10.73 | -10.8353 | -10.8032 | -0.15106 | 0.10529 | -0.20142 | -0.1236 | 0 | -0.086975 | 0.032043 | -0.15564 | 0.17395 | -0.46692 | 0.05951 | -0.013733 | -0.045776 | 0.14191 | 0.10986 | 10.5881 | -111.8729 | -112.1017 | 10.7895 | 10.8215 | 10.7025 | 0.23346 | 0.11444 | 0.21515 | 122.4564 | 0.20142 | 0.07782 | 123.0972 | 0.3067 | 122.9416 | 10.8948 | -122.9233 | -112.1796 | 122.3007 | 10.6659 | 11.0733 | 10.6384
1446.2031 | 122.7676 | -10.675 | 111.9827 | 0.0034333 | 0.004751 | 0.070654 | 0.064632 | 0.0022409 | -0.0047103 | -0.00055975 | 0.0077514 | 0.014742 | 0.020568 | 0.024725 | -3.8532e-05 | 0.0082374 | 0.00051699 | 0.2243 | 112.0651 | -10.9268 | 111.5433 | -10.6613 | -10.8673 | -10.8261 | -0.009155 | 0.09613 | -0.16479 | -0.009155 | 0.086975 | -0.018311 | 0.10071 | -0.25177 | 0.082398 | -0.43945 | 0.013733 | -0.15106 | -0.19226 | 0.10071 | 0.059509 | 10.5103 | -111.8866 | -111.9919 | 10.762 | 10.7758 | 10.6567 | 0.2655 | 0.14648 | 0.2655 | 122.4701 | 0.25177 | 0.15564 | 122.9919 | 0.26092 | 122.7402 | 10.7712 | -122.9095 | -112.1475 | 122.2183 | 10.6659 | 10.8994 | 10.6659
1447.8906 | 122.6761 | -10.9726 | 111.7859 | -0.0041962 | 0.0060328 | 0.069799 | 0.066768 | 0.0054453 | -0.0034287 | -0.0029096 | 0.0046998 | 0.014956 | 0.02014 | 0.011053 | 0.0020979 | 0.0071692 | 0.002226 | 0.21515 | 111.9919 | -11.1053 | 111.319 | -10.9589 | -11.087 | -11.0367 | -0.16022 | 0.11444 | -0.20142 | -0.086975 | -0.027466 | -0.13275 | 0.050354 | -0.13275 | 0.20599 | -0.46692 | 0.013733 | -0.064087 | -0.11444 | 0.068665 | 0.018311 | 10.7712 | -111.6714 | -111.8729 | 10.9451 | 11.0229 | 10.8398 | 0.25177 | 0.068665 | 0.14649 | 122.4243 | 0.17395 | 0.11444 | 123.0972 | 0.31586 | 122.9645 | 11.087 | -122.8912 | -111.9873 | 122.2916 | 10.8856 | 11.1877 | 10.8124
1449.6406 | 122.818 | -10.7758 | 111.8317 | 0.011063 | 0.0043238 | 0.068517 | 0.064632 | 0.00053194 | -0.0036423 | 0.0015764 | -0.0044556 | 0.012606 | 0.022704 | 0.02387 | -0.00046573 | 0.008451 | -0.0022602 | 0.30212 | 112.0193 | -10.9772 | 111.6074 | -10.6018 | -10.7666 | -10.7208 | 0.018311 | 0.07782 | -0.16479 | 0.032043 | 0.14648 | 0.054932 | 0.13275 | -0.20142 | 0.18768 | -0.2243 | 0.17395 | 0.054932 | 0.009155 | 0.25635 | 0.21057 | 10.611 | -111.7538 | -111.7996 | 10.9222 | 10.9085 | 10.8307 | 0.29755 | 0.21973 | 0.37537 | 122.5845 | 0.31128 | 0.19684 | 122.9965 | 0.24261 | 122.7951 | 10.8536 | -122.8088 | -111.9965 | 122.3831 | 10.8078 | 11.0779 | 10.7941
1451.375 | 122.6852 | -10.611 | 112.0743 | 0.0034333 | 0.0053918 | 0.069799 | 0.063564 | 0.0043771 | -0.0019333 | -0.00013235 | 0.001648 | 0.01282 | 0.019927 | 0.014684 | -0.0032427 | 0.0080236 | -0.00097841 | 0.32959 | 112.2437 | -10.7803 | 111.6806 | -10.5698 | -10.7071 | -10.6613 | -0.1236 | 0.1236 | -0.19684 | -0.09613 | 0.022888 | -0.07782 | 0.045776 | -0.16937 | 0.16937 | -0.39368 | 0.041199 | -0.050354 | -0.09613 | 0.11902 | 0.073242 | 10.4141 | -111.9507 | -112.1704 | 10.6339 | 10.6567 | 10.5331 | 0.24261 | 0.11902 | 0.21057 | 122.4609 | 0.21973 | 0.10071 | 123.024 | 0.32043 | 122.8546 | 10.7346 | -122.8546 | -112.2711 | 122.2916 | 10.5148 | 10.9406 | 10.4874
1453.1094 | 122.6761 | -10.5377 | 112.2162 | 0.018692 | 0.0083826 | 0.069586 | 0.068904 | 0.0052315 | -0.0038559 | 0.0015764 | -0.0044556 | 0.015597 | 0.020995 | 0.014257 | 0.0023115 | 0.00781 | 0.0017988 | 0.3067 | 112.3901 | -10.6934 | 111.7447 | -10.524 | -10.6293 | -10.5972 | -0.16022 | 0.11902 | -0.20599 | -0.09613 | -0.022888 | -0.13275 | 0.041199 | -0.15564 | 0.17395 | -0.4715 | 0.013733 | -0.059509 | -0.091552 | 0.09613 | 0.064087 | 10.3317 | -112.0972 | -112.3123 | 10.5148 | 10.5789 | 10.405 | 0.24719 | 0.073243 | 0.16937 | 122.438 | 0.18311 | 0.10986 | 123.0835 | 0.32501 | 122.9279 | 10.6567 | -122.9095 | -112.4222 | 122.2824 | 10.4416 | 10.8444 | 10.3775
1454.8594 | 122.7081 | -10.5103 | 112.2299 | 0.0034333 | 0.0036828 | 0.068731 | 0.064418 | 0.0067269 | -0.0032151 | -0.00013235 | -0.0014038 | 0.012606 | 0.02249 | 0.012762 | -0.00089293 | 0.00781 | -0.00033761 | 0.34332 | 112.413 | -10.6476 | 111.731 | -10.5331 | -10.611 | -10.5881 | -0.14648 | 0.12817 | -0.21515 | -0.086975 | 0.045776 | -0.07782 | 0.054932 | -0.13733 | 0.18311 | -0.49896 | -0.022888 | -0.07782 | -0.10071 | 0.059509 | 0.036621 | 10.2951 | -112.1017 | -112.3169 | 10.556 | 10.5652 | 10.4324 | 0.27008 | 0.13733 | 0.11444 | 122.3785 | 0.26093 | 0.12817 | 123.0606 | 0.34332 | 122.9233 | 10.6384 | -122.8775 | -112.4451 | 122.2412 | 10.4233 | 10.8536 | 10.3638
1456.5312 | 122.8043 | -10.6293 | 112.0468 | -0.0041962 | 0.0073144 | 0.070226 | 0.064632 | 0.00053194 | -0.0012925 | 0.00093565 | 0.0046998 | 0.010897 | 0.0195 | 0.015325 | 0.0010297 | 0.0097326 | -0.0026874 | 0.23346 | 112.2253 | -10.7758 | 111.6577 | -10.6018 | -10.73 | -10.6659 | -0.045776 | 0.086975 | -0.16022 | 0.009155 | 0.13733 | 0.032043 | 0.12817 | -0.14649 | 0.17853 | -0.3891 | 0.027465 | -0.036622 | -0.10071 | 0.10986 | 0.045777 | 10.4691 | -111.9598 | -112.0377 | 10.7666 | 10.7574 | 10.6613 | 0.28839 | 0.19226 | 0.17395 | 122.4335 | 0.29755 | 0.16937 | 123.0011 | 0.24719 | 122.8546 | 10.7162 | -122.8226 | -112.207 | 122.287 | 10.6384 | 10.8627 | 10.5835
1458.2812 | 122.6532 | -10.8536 | 111.882 | 0.0034333 | 0.0073144 | 0.070013 | 0.068477 | 0.0062997 | -0.0019333 | 0.0028582 | 0.0077514 | 0.014529 | 0.021849 | 0.012762 | 0.0014569 | 0.0082374 | -0.00033761 | 0.18768 | 112.0514 | -11.0092 | 111.438 | -10.8673 | -11.0092 | -10.9772 | -0.15564 | 0.11902 | -0.19684 | -0.10986 | -0.045776 | -0.14191 | 0.027466 | -0.15564 | 0.16937 | -0.44403 | -0.013733 | -0.1236 | -0.15564 | 0.032043 | 0 | 10.6567 | -111.763 | -111.9919 | 10.8078 | 10.881 | 10.7117 | 0.2243 | 0.054931 | 0.14191 | 122.4472 | 0.15106 | 0.086975 | 123.0606 | 0.31586 | 122.905 | 10.9726 | -122.8912 | -112.0789 | 122.2916 | 10.7437 | 11.0413 | 10.6979
1459.9531 | 122.6807 | -10.7712 | 111.9553 | 0.0034333 | 0.0066736 | 0.070654 | 0.065273 | 0.0013863 | -0.0055649 | -0.00034615 | 0.001648 | 0.013247 | 0.019927 | 0.012548 | -0.0026019 | 0.006101 | -0.0033282 | 0.32959 | 112.207 | -10.849 | 111.6074 | -10.6201 | -10.7574 | -10.7346 | -0.13275 | 0.11902 | -0.19684 | -0.10071 | 0.022888 | -0.086975 | 0.032043 | -0.07782 | 0.25177 | -0.3479 | 0.15106 | 0.036621 | 0.013733 | 0.11444 | 0.091553 | 10.5743 | -111.8362 | -112.056 | 10.7941 | 10.8032 | 10.6842 | 0.22888 | 0.10986 | 0.22888 | 122.4564 | 0.21973 | 0.09613 | 123.056 | 0.31586 | 122.9782 | 10.8902 | -122.8043 | -112.1521 | 122.3785 | 10.6705 | 11.1008 | 10.6384
1461.7031 | 122.8043 | -10.8398 | 111.8042 | 0.011063 | 0.0043238 | 0.071508 | 0.065486 | 0.0039499 | -0.0019333 | -0.003764 | 0.0046998 | 0.013674 | 0.021636 | 0.02622 | 0.0018841 | 0.0086646 | 0.001585 | 0.2655 | 111.969 | -11.0184 | 111.4975 | -10.7208 | -10.9177 | -10.881 | 0.013733 | 0.07782 | -0.15106 | 0.032043 | 0.1236 | 0.018311 | 0.15564 | -0.17853 | 0.16479 | -0.3067 | 0.11902 | -0.041198 | -0.07782 | 0.13733 | 0.10071 | 10.6888 | -111.7264 | -111.7722 | 10.9634 | 10.9955 | 10.8582 | 0.3067 | 0.16937 | 0.29755 | 122.5159 | 0.27466 | 0.18311 | 122.9874 | 0.22888 | 122.8088 | 10.9177 | -122.8226 | -111.9553 | 122.3373 | 10.8719 | 11.1053 | 10.8536
1463.375 | 122.7127 | -10.6247 | 112.1155 | 0.018692 | 0.0056054 | 0.070013 | 0.065913 | 0.0011727 | -0.0040695 | -0.00034615 | 0.0046998 | 0.013247 | 0.020781 | 0.014898 | -0.0023883 | 0.0071692 | 0.0030804 | 0.36621 | 112.2849 | -10.7758 | 111.6486 | -10.6064 | -10.7208 | -10.6934 | -0.13733 | 0.14191 | -0.21973 | -0.091553 | 0.022888 | -0.07782 | 0.045776 | -0.15106 | 0.16937 | -0.46692 | 0.018311 | -0.068664 | -0.09613 | 0.082398 | 0.054932 | 10.405 | -111.9736 | -112.207 | 10.6476 | 10.6705 | 10.5469 | 0.2655 | 0.14191 | 0.16937 | 122.4243 | 0.24261 | 0.12817 | 123.0606 | 0.36163 | 122.9095 | 10.7666 | -122.8912 | -112.3352 | 122.2733 | 10.5331 | 10.9909 | 10.4874
1465.125 | 122.7814 | -10.8124 | 111.8774 | 0.0034333 | 0.0041102 | 0.070867 | 0.063991 | 0.0069405 | -0.00065149 | 0.00029485 | 0.001648 | 0.014315 | 0.02249 | 0.019811 | 0.00081607 | 0.0099462 | 0.0035078 | 0.21973 | 111.9781 | -10.9955 | 111.4838 | -10.7437 | -10.9268 | -10.8673 | -0.013733 | 0.07782 | -0.16022 | 0 | 0.07782 | -0.013733 | 0.11902 | -0.1831 | 0.10071 | -0.39368 | 0.068665 | -0.054932 | -0.11444 | 0.12817 | 0.068664 | 10.6522 | -111.7996 | -111.8774 | 10.8902 | 10.9314 | 10.7986 | 0.27924 | 0.14648 | 0.25177 | 122.4792 | 0.23804 | 0.16022 | 122.9736 | 0.23804 | 122.7905 | 10.8902 | -122.8729 | -112.0377 | 122.2961 | 10.8124 | 11.0321 | 10.7986
1466.875 | 122.6761 | -10.7254 | 112.0377 | 0.011063 | 0.007528 | 0.071295 | 0.067836 | 0.0048043 | -0.0025741 | -0.00098695 | -0.0014038 | 0.014529 | 0.021849 | 0.016607 | -3.8532e-05 | 0.0071692 | 0.0011578 | 0.27466 | 112.1521 | -10.8994 | 111.5295 | -10.7346 | -10.8765 | -10.849 | -0.13733 | 0.14648 | -0.17853 | -0.082397 | -0.009155 | -0.13733 | 0.041199 | -0.17395 | 0.11444 | -0.50812 | -0.009155 | -0.1236 | -0.15106 | 0.050354 | 0.022888 | 10.5469 | -111.8912 | -112.1201 | 10.7162 | 10.7666 | 10.5881 | 0.21973 | 0.041199 | 0.16479 | 122.4289 | 0.16937 | 0.096131 | 123.0515 | 0.32501 | 122.8775 | 10.8719 | -122.937 | -112.2162 | 122.2549 | 10.643 | 11.0001 | 10.5881
1468.5625 | 122.8134 | -10.3409 | 112.3306 | -0.0041962 | 0.0043238 | 0.070013 | 0.062923 | 0.00010474 | -0.0030015 | 0.00050845 | 0.001648 | 0.01346 | 0.02014 | 0.027075 | -0.0013201 | 0.009519 | -0.00055121 | 0.35248 | 112.3993 | -10.5743 | 111.8774 | -10.3363 | -10.5057 | -10.4736 | 0.027466 | 0.073242 | -0.14648 | 0.036621 | 0.16022 | 0.050354 | 0.14191 | -0.23346 | 0.068665 | -0.45319 | 0.004577 | -0.13275 | -0.16479 | 0.10071 | 0.068665 | 10.1944 | -112.2574 | -112.294 | 10.5011 | 10.4828 | 10.3912 | 0.28839 | 0.19684 | 0.23804 | 122.4518 | 0.3067 | 0.18311 | 122.9736 | 0.21973 | 122.7402 | 10.4141 | -122.905 | -112.4771 | 122.2183 | 10.3775 | 10.6934 | 10.3683
1470.3125 | 122.8271 | -10.4416 | 112.2116 | 0.0034333 | 0.0073144 | 0.07044 | 0.065059 | 0.0030953 | -0.0023605 | -0.0012006 | 0.010803 | 0.014101 | 0.020995 | 0.021093 | 0.0025251 | 0.009519 | 0.0020124 | 0.31128 | 112.4817 | -10.4736 | 112.0148 | -10.231 | -10.4004 | -10.3592 | 0.009155 | 0.07782 | -0.15564 | 0.054932 | 0.13275 | 0.018311 | 0.17395 | -0.032044 | 0.27008 | -0.19684 | 0.21057 | 0.082397 | 0.041198 | 0.11444 | 0.073242 | 10.2859 | -112.1338 | -112.1567 | 10.5743 | 10.6155 | 10.4599 | 0.32959 | 0.17395 | 0.24261 | 122.4884 | 0.28839 | 0.21057 | 122.9553 | 0.23346 | 122.9233 | 10.5194 | -122.6852 | -112.3672 | 122.4564 | 10.4965 | 10.7529 | 10.4507
1472.0625 | 122.8134 | -10.3134 | 112.3489 | 0.0034333 | 0.0049646 | 0.069372 | 0.063991 | 0.0045907 | -0.0027877 | 0.00072205 | -0.0014038 | 0.013033 | 0.018859 | 0.021734 | -0.0023883 | 0.0069556 | 0.00094419 | 0.32044 | 112.5 | -10.4645 | 112.056 | -10.1669 | -10.3363 | -10.2905 | 0.027466 | 0.082397 | -0.18768 | 0.032043 | 0.15106 | 0.059509 | 0.14191 | -0.15106 | 0.15106 | -0.29297 | 0.14649 | 0.022889 | -0.022888 | 0.17395 | 0.12817 | 10.1257 | -112.2665 | -112.3169 | 10.4645 | 10.4553 | 10.3729 | 0.32959 | 0.24719 | 0.29755 | 122.5204 | 0.33874 | 0.21973 | 122.9645 | 0.27008 | 122.8134 | 10.3958 | -122.8134 | -112.5366 | 122.3694 | 10.3455 | 10.6339 | 10.3409
1473.75 | 122.7173 | -10.2859 | 112.4634 | -0.0041962 | 0.0056054 | 0.069799 | 0.063991 | 0.0022409 | -0.0019333 | 0.00029485 | -0.0014038 | 0.012606 | 0.018218 | 0.016821 | -0.00067933 | 0.0054602 | -0.0035418 | 0.37079 | 112.6328 | -10.4553 | 112.001 | -10.2768 | -10.3683 | -10.3409 | -0.10986 | 0.11902 | -0.18768 | -0.041199 | 0.036621 | -0.059509 | 0.073242 | -0.16937 | 0.16937 | -0.46234 | 0.009156 | -0.054931 | -0.082397 | 0.11444 | 0.086975 | 10.0983 | -112.3444 | -112.5046 | 10.3226 | 10.3592 | 10.2264 | 0.26092 | 0.12817 | 0.17853 | 122.4564 | 0.2243 | 0.14648 | 123.0881 | 0.3067 | 122.9187 | 10.405 | -122.9187 | -112.6511 | 122.287 | 10.2448 | 10.6567 | 10.1761
1475.5156 | 122.6852 | -10.1257 | 112.6282 | 0.0034333 | 0.0045374 | 0.068517 | 0.065059 | 0.0065133 | -0.0034287 | -0.002696 | -0.0014038 | 0.01346 | 0.023345 | 0.015966 | -0.0034563 | 0.00781 | 8.9786e-05 | 0.37079 | 112.793 | -10.2814 | 112.1521 | -10.0845 | -10.2127 | -10.1669 | -0.13733 | 0.1236 | -0.21515 | -0.10071 | -0.004578 | -0.10071 | 0.036621 | -0.15564 | 0.16479 | -0.47607 | 0.041198 | -0.041199 | -0.086976 | 0.11444 | 0.068664 | 9.9106 | -112.5046 | -112.7289 | 10.1212 | 10.1624 | 10.025 | 0.25177 | 0.11444 | 0.19684 | 122.4335 | 0.21057 | 0.11444 | 123.0743 | 0.33875 | 122.9187 | 10.2493 | -122.9095 | -112.8433 | 122.2778 | 10.025 | 10.4965 | 9.9884
1477.2188 | 122.7356 | -10.0754 | 112.6328 | 0.018692 | 0.004751 | 0.068731 | 0.066554 | 0.0082223 | -0.0027877 | -0.0039778 | 0.0046998 | 0.014956 | 0.021422 | 0.01917 | -0.00046573 | 0.006742 | -0.0041828 | 0.4303 | 112.8937 | -10.1852 | 112.294 | -9.9335 | -10.0708 | -10.0525 | -0.07782 | 0.11444 | -0.20142 | -0.041199 | 0.045776 | -0.054932 | 0.073242 | -0.10986 | 0.26093 | -0.33875 | 0.14191 | 0.022888 | 0.004577 | 0.13275 | 0.11444 | 9.874 | -112.5183 | -112.674 | 10.1212 | 10.1486 | 10.0204 | 0.27466 | 0.14648 | 0.25177 | 122.4792 | 0.24719 | 0.16022 | 123.0789 | 0.31586 | 122.9691 | 10.1898 | -122.818 | -112.8342 | 122.3694 | 10.0342 | 10.5057 | 9.9976
1478.9844 | 122.6669 | -10.0983 | 112.6556 | 0.0034333 | 0.0060328 | 0.070013 | 0.066341 | 0.0050179 | -0.0027877 | -0.00098695 | 0.0046998 | 0.014529 | 0.021209 | 0.01383 | 0.0020979 | 0.0093054 | -0.00097841 | 0.32501 | 112.9028 | -10.2036 | 112.2528 | -10.0571 | -10.231 | -10.1898 | -0.17853 | 0.13733 | -0.21515 | -0.10529 | -0.032043 | -0.12817 | 0.045776 | -0.10529 | 0.24719 | -0.40283 | 0.041199 | -0.091552 | -0.13275 | 0.013733 | -0.027466 | 9.8831 | -112.5183 | -112.7609 | 10.0662 | 10.144 | 9.9701 | 0.26093 | 0.086975 | 0.14648 | 122.4564 | 0.18311 | 0.10986 | 123.1064 | 0.35248 | 123.0011 | 10.2356 | -122.8592 | -112.8708 | 122.3511 | 9.993 | 10.4233 | 9.9197
1480.6562 | 122.699 | -10.1486 | 112.5778 | -0.0041962 | 0.11007 | 0.070226 | 0.061855 | 0.0033089 | -0.0044967 | 0.10262 | 0.0077514 | 0.010897 | 0.021849 | 0.0093438 | -0.0032427 | 0.0080236 | 0.00051699 | 2.6138 | 112.7426 | -10.2722 | 112.1704 | -10.025 | 4.303 | 112.5137 | -0.082397 | 0.10986 | -0.19684 | -0.064087 | 0.041199 | -0.059509 | 0.041199 | -0.1236 | 0.16479 | -0.40741 | 0.1236 | 122.6624 | 14.4516 | 122.7859 | 14.5752 | 9.9518 | -112.468 | -112.6419 | 10.1898 | 10.1898 | 10.0891 | 0.23804 | 0.13733 | 0.24719 | 122.4426 | 0.23804 | 0.13275 | 123.0148 | 0.3067 | 122.8912 | 10.2585 | -122.85 | -112.7747 | 122.319 | 10.0845 | 12.7625 | 10.0662
1482.4062 | 122.7036 | -10.0891 | 112.619 | 0.0034333 | 0.11135 | 0.070226 | 0.064845 | 0.0067269 | -0.0023605 | 0.1054 | 0.001648 | 0.014956 | 0.020354 | 0.018102 | 0.0012433 | 0.0090918 | -0.001192 | 2.6276 | 112.7792 | -10.2448 | 112.1796 | -10.0204 | 4.3076 | 112.4908 | -0.064087 | 0.11444 | -0.18768 | -0.045776 | 0.032043 | -0.082397 | 0.064087 | -0.15564 | 0.16022 | -0.43945 | 0.068664 | 122.58 | 14.3967 | 122.7356 | 14.5523 | 9.9014 | -112.5046 | -112.6648 | 10.1212 | 10.1532 | 10.0067 | 0.25177 | 0.10529 | 0.2243 | 122.4243 | 0.21973 | 0.14191 | 123.024 | 0.30212 | 122.8683 | 10.2036 | -122.8638 | -112.8067 | 122.2687 | 10.0433 | 12.7167 | 10.025
1484.0938 | 122.7081 | -10.2722 | 112.4313 | -0.0041962 | 0.1075 | 0.068945 | 0.064845 | 0.0018137 | -0.0015061 | 0.10518 | 0.001648 | 0.012392 | 0.020995 | 0.019598 | -0.00025213 | 0.0073828 | 0.00073059 | 2.6321 | 112.5458 | -10.4095 | 112.0331 | -10.1349 | 4.4083 | 112.3901 | -0.050354 | 0.10986 | -0.16937 | -0.045776 | 0.059509 | -0.032043 | 0.073242 | -0.13733 | 0.11444 | -0.39825 | 0.13733 | 122.6624 | 14.6805 | 122.7997 | 14.8178 | 10.1028 | -112.3215 | -112.4771 | 10.3317 | 10.3455 | 10.2402 | 0.24261 | 0.13733 | 0.27466 | 122.4426 | 0.22888 | 0.1236 | 122.9553 | 0.27924 | 122.818 | 10.3821 | -122.8409 | -112.6007 | 122.3053 | 10.2264 | 12.9044 | 10.2219
1485.8281 | 122.6944 | -10.1578 | 112.5458 | -0.0041962 | 0.11263 | 0.069372 | 0.064632 | -0.00032266 | -0.0021469 | 0.10732 | 0.001648 | 0.013888 | 0.020995 | 0.0082758 | 0.00060247 | 0.0056738 | -0.0026874 | 2.6596 | 112.7014 | -10.3088 | 112.0972 | -10.0983 | 4.3579 | 112.4268 | -0.10071 | 0.10986 | -0.1831 | -0.082397 | 0.009155 | -0.10071 | 0.041199 | -0.15106 | 0.15564 | -0.44861 | 0.059509 | 122.5845 | 14.5157 | 122.7356 | 14.6667 | 9.9747 | -112.4359 | -112.6282 | 10.1669 | 10.199 | 10.0571 | 0.2243 | 0.082397 | 0.21057 | 122.406 | 0.19226 | 0.10071 | 123.0103 | 0.29297 | 122.8592 | 10.2676 | -122.8546 | -112.7289 | 122.2549 | 10.0754 | 12.8174 | 10.0571
1487.5625 | 122.699 | -10.0708 | 112.5961 | 0.011063 | 0.11071 | 0.072149 | 0.062709 | 0.0026681 | -0.0025741 | 0.10668 | 0.001648 | 0.014315 | 0.019927 | 0.01383 | 0.0014569 | 0.0075964 | -0.0020464 | 2.6779 | 112.7609 | -10.2722 | 112.1658 | -10.025 | 4.4266 | 112.5 | -0.059509 | 0.11444 | -0.1831 | -0.045776 | 0.045776 | -0.050354 | 0.082397 | -0.20142 | 0.16479 | -0.4303 | 0.045777 | 122.5708 | 14.4974 | 122.7722 | 14.6988 | 9.8877 | -112.4817 | -112.6419 | 10.1166 | 10.1532 | 10.0204 | 0.2655 | 0.13275 | 0.24719 | 122.4381 | 0.22888 | 0.13733 | 123.0331 | 0.29755 | 122.8317 | 10.1852 | -122.8683 | -112.7792 | 122.2366 | 10.025 | 12.7487 | 10.0113
1489.2969 | 122.7905 | -10.0662 | 112.5641 | 0.011063 | 0.10814 | 0.073004 | 0.064845 | 0.0056589 | -0.00086509 | 0.10647 | 0.001648 | 0.012606 | 0.023345 | 0.019384 | 0.0029523 | 0.009519 | -0.00055121 | 2.6184 | 112.7655 | -10.2631 | 112.1521 | -10.0388 | 4.4128 | 112.4954 | -0.054932 | 0.082397 | -0.16937 | 0.041199 | 0.091553 | 0.013733 | 0.14648 | -0.19684 | 0.20142 | -0.41199 | 0.027466 | 122.5616 | 14.4791 | 122.7585 | 14.6759 | 9.8969 | -112.4817 | -112.5229 | 10.1578 | 10.2127 | 10.08 | 0.31586 | 0.18311 | 0.2243 | 122.4152 | 0.26093 | 0.21057 | 123.0286 | 0.25177 | 122.8317 | 10.1486 | -122.8271 | -112.7335 | 122.2183 | 10.1074 | 12.6846 | 10.0113
1491.0469 | 122.6532 | -10.1578 | 112.5732 | 0.0034333 | 0.10964 | 0.068731 | 0.062068 | 0.0020273 | -0.0049241 | 0.10711 | 0.0046998 | 0.01346 | 0.021636 | 0.013616 | -0.0021747 | 0.0080236 | 0.0017988 | 2.6001 | 112.7106 | -10.2768 | 112.0605 | -10.1212 | 4.4769 | 112.4451 | -0.14191 | 0.13275 | -0.21515 | -0.10529 | -0.009155 | -0.10071 | 0.041199 | -0.11902 | 0.13733 | -0.51269 | 0.036621 | 122.6028 | 14.6347 | 122.7219 | 14.7537 | 9.9426 | -112.4405 | -112.6785 | 10.1486 | 10.199 | 10.0571 | 0.25635 | 0.11444 | 0.15564 | 122.3373 | 0.20599 | 0.10986 | 122.9874 | 0.3479 | 122.8683 | 10.2905 | -122.85 | -112.7884 | 122.2183 | 10.0525 | 12.7579 | 10.0159
1492.7188 | 122.7356 | -10.2264 | 112.4176 | 0.011063 | 0.10879 | 0.069586 | 0.064418 | 0.0028817 | -0.0023605 | 0.10347 | 0.001648 | 0.011751 | 0.021209 | 0.019598 | 0.0014569 | 0.0075964 | 0.00073059 | 2.6138 | 112.6373 | -10.3317 | 112.0605 | -10.1028 | 4.4815 | 112.4405 | -0.027466 | 0.086975 | -0.1831 | 0 | 0.07782 | -0.022888 | 0.10986 | -0.10529 | 0.21973 | -0.35706 | 0.1236 | 122.6669 | 14.7079 | 122.7722 | 14.8132 | 10.0433 | -112.3306 | -112.4176 | 10.3043 | 10.3363 | 10.2036 | 0.29297 | 0.16022 | 0.22888 | 122.3923 | 0.26092 | 0.1831 | 122.9691 | 0.27008 | 122.8638 | 10.3134 | -122.7493 | -112.6007 | 122.287 | 10.2264 | 12.8403 | 10.199
1494.4688 | 122.7814 | -10.1074 | 112.5641 | 0.026321 | 0.10857 | 0.07044 | 0.063136 | 0.00031834 | -0.0023605 | 0.10711 | 0.001648 | 0.0094016 | 0.020354 | 0.020452 | -0.0021747 | 0.0056738 | 0.0026532 | 2.7512 | 112.6877 | -10.2448 | 112.2345 | -9.9335 | 4.6829 | 112.5824 | 0 | 0.07782 | -0.16937 | 0.009155 | 0.13275 | 0.041199 | 0.13733 | -0.13733 | 0.1236 | -0.32959 | 0.17395 | 122.6898 | 14.7903 | 122.8271 | 14.9277 | 9.938 | -112.4863 | -112.5549 | 10.2402 | 10.2448 | 10.1486 | 0.3067 | 0.21057 | 0.31128 | 122.4792 | 0.30212 | 0.17853 | 122.9324 | 0.24719 | 122.7951 | 10.1852 | -122.8088 | -112.7335 | 122.3419 | 10.1166 | 12.8586 | 10.1074
1496.2188 | 122.731 | -10.1532 | 112.4817 | 0.0034333 | 0.10451 | 0.069372 | 0.063564 | 0.0050179 | -0.0047103 | 0.10262 | 0.0046998 | 0.013247 | 0.02014 | 0.017248 | -0.0015337 | 0.00781 | 0.00073059 | 2.5589 | 112.6511 | -10.3043 | 112.1292 | -10.0479 | 4.5456 | 112.5137 | -0.082397 | 0.07782 | -0.18768 | -0.032043 | 0.07782 | -0.013733 | 0.10529 | -0.15106 | 0.16937 | -0.35248 | 0.10529 | 122.6669 | 14.6988 | 122.818 | 14.8499 | 9.9655 | -112.4039 | -112.5137 | 10.231 | 10.2585 | 10.1395 | 0.29297 | 0.17395 | 0.25635 | 122.4335 | 0.2655 | 0.15564 | 122.9553 | 0.2655 | 122.8043 | 10.231 | -122.7859 | -112.6694 | 122.2824 | 10.1212 | 12.7121 | 10.0708
1497.9062 | 122.6944 | -10.0937 | 112.5824 | 0.018692 | 0.10558 | 0.069586 | 0.0704 | 0.0043771 | -0.0040695 | 0.1054 | 0.001648 | 0.013888 | 0.021422 | 0.014044 | 0.00038887 | 0.0075964 | 0.0060712 | 2.7557 | 112.8113 | -10.2402 | 112.1658 | -10.0159 | 4.747 | 112.5229 | -0.054932 | 0.1236 | -0.19684 | -0.041199 | 0.045776 | -0.059509 | 0.082397 | -0.14648 | 0.22888 | -0.41656 | 0.07782 | 122.6166 | 14.8407 | 122.7631 | 14.9872 | 9.8969 | -112.4588 | -112.6236 | 10.1395 | 10.1761 | 10.0342 | 0.27924 | 0.13733 | 0.2243 | 122.406 | 0.24261 | 0.15564 | 123.0515 | 0.32043 | 122.905 | 10.2173 | -122.8226 | -112.7792 | 122.2595 | 10.0525 | 12.8494 | 10.0388
1499.6562 | 122.6624 | -10.1486 | 112.5504 | 0.018692 | 0.10131 | 0.072149 | 0.071895 | 0.0082223 | -0.0019333 | 0.10369 | 0.0046998 | 0.014315 | 0.023345 | 0.018957 | 0.00081607 | 0.0086646 | -0.0018328 | 2.5589 | 112.7609 | -10.2768 | 112.0743 | -10.1532 | 4.7012 | 112.413 | -0.16479 | 0.13733 | -0.21057 | -0.082397 | -0.013733 | -0.1236 | 0.041199 | -0.12817 | 0.21057 | -0.47607 | -0.004577 | 122.5616 | 14.8499 | 122.6898 | 14.978 | 9.9381 | -112.413 | -112.6328 | 10.1349 | 10.1898 | 10.025 | 0.25177 | 0.086975 | 0.1236 | 122.3511 | 0.19684 | 0.12817 | 123.0377 | 0.3479 | 122.9095 | 10.2859 | -122.8271 | -112.7609 | 122.2229 | 10.0662 | 12.7075 | 9.9838
1501.4219 | 122.7081 | -13.4354 | 109.2316 | 0.011063 | 0.10259 | 0.070226 | 0.069118 | 0.0011727 | -0.0049241 | 0.10219 | 0.0077514 | 0.01282 | 0.02014 | 0.016821 | -0.0032427 | 0.0073828 | -0.005678 | 2.4216 | 109.4833 | -13.4491 | 108.9706 | -13.266 | 4.7104 | 109.2957 | -0.064087 | 0.11902 | -0.1831 | -0.059509 | 0.041199 | -0.054932 | 0.068665 | -0.013733 | 0.25177 | -0.26093 | 0.16937 | 122.731 | 18.1458 | 122.7448 | 18.1595 | 13.2523 | -109.1125 | -109.2911 | 13.4766 | 13.504 | 13.3804 | 0.25177 | 0.12817 | 0.18311 | 122.4197 | 0.2243 | 0.1236 | 122.9324 | 0.30212 | 122.9187 | 13.5544 | -122.6807 | -109.4147 | 122.406 | 13.3759 | 15.8569 | 13.3713
1503.1719 | 122.6944 | -12.3642 | 110.3119 | 0.0034333 | 0.10088 | 0.069158 | 0.069972 | 0.0052315 | -0.0040695 | 0.10561 | 0.0046998 | 0.015597 | 0.023558 | 0.015325 | -0.00025213 | 0.006101 | 0.0028668 | 2.4033 | 110.463 | -12.529 | 109.8907 | -12.3138 | 4.7745 | 110.2386 | -0.054932 | 0.1236 | -0.17853 | -0.013733 | 0.073242 | -0.036621 | 0.09613 | -0.16479 | 0.15106 | -0.42114 | 0.050354 | 122.6028 | 17.1387 | 122.7676 | 17.3035 | 12.1857 | -110.1883 | -110.3256 | 12.4374 | 12.4603 | 12.3276 | 0.27466 | 0.14191 | 0.21515 | 122.4197 | 0.25177 | 0.16479 | 122.9919 | 0.30212 | 122.8271 | 12.4878 | -122.8409 | -110.4904 | 122.2549 | 12.3505 | 14.7675 | 12.3093
1504.9219 | 122.6761 | -8.9264 | 113.7588 | -0.0041962 | 0.10088 | 0.070654 | 0.071681 | 0.0054453 | -0.0027877 | 0.10647 | 0.0077514 | 0.015169 | 0.021849 | 0.01383 | -0.00046573 | 0.0052466 | 8.9786e-05 | 2.6367 | 113.9786 | -9.0454 | 113.3286 | -8.8165 | 5.1407 | 113.6673 | -0.054932 | 0.1236 | -0.18768 | -0.036621 | 0.054932 | -0.050354 | 0.09613 | -0.11902 | 0.21973 | -0.4303 | 0.10986 | 122.5937 | 14.0671 | 122.7127 | 14.1861 | 8.7387 | -113.6353 | -113.7955 | 8.9813 | 9.0225 | 8.876 | 0.28381 | 0.13733 | 0.22888 | 122.374 | 0.24261 | 0.15106 | 123.024 | 0.31128 | 122.905 | 9.05 | -122.8043 | -113.9465 | 122.2549 | 8.8898 | 11.5631 | 8.8715
1506.6094 | 122.6257 | -8.9905 | 113.7085 | 0.0034333 | -0.057841 | 0.011694 | 0.03152 | 0.0050179 | -0.0023605 | 0.0011492 | 0.001648 | 0.015169 | 0.020568 | 0.010839 | -0.0026019 | 0.0058874 | -0.0026874 | 0.30212 | 0.81482 | 0.30212 | 0.3479 | 0.53101 | 0.39368 | 0.48065 | -0.14191 | 0.11902 | -0.20599 | -0.082397 | 0.018311 | -0.091553 | 0.054932 | 9.2926 | -112.8937 | -113.3606 | 9.5215 | 9.4711 | 9.3842 | 0.17853 | 0.091553 | 8.7845 | -113.5895 | -113.7909 | 9.0088 | 9.0454 | 8.8989 | 0.26093 | 0.11444 | 0.22888 | 0.045776 | 0.22431 | 0.1236 | 0.51269 | 0.32501 | 9.8053 | 9.1095 | -113.4064 | -113.9145 | 9.3384 | 8.9081 | 9.2926 | 8.8486
1508.3438 | 122.6578 | -9.0866 | 113.5941 | -0.0041962 | -0.061259 | 0.012975 | 0.028743 | 0.0041635 | -0.0036423 | 0.00072205 | -0.0014038 | 0.012179 | 0.020995 | 0.015112 | -0.0011065 | 0.0063148 | 0.00051699 | 0.3891 | 0.79651 | 0.2655 | 0.31128 | 0.48981 | 0.36621 | 0.44861 | -0.14191 | 0.1236 | -0.21057 | -0.07782 | 0.027466 | -0.07782 | 0.073242 | 9.3521 | -112.7975 | -113.2828 | 9.5764 | 9.5352 | 9.4528 | 0.18311 | 0.10071 | 8.876 | -113.4705 | -113.6719 | 9.1141 | 9.1599 | 9.0088 | 0.28381 | 0.13275 | 0.2243 | 0.045776 | 0.23804 | 0.13275 | 0.53101 | 0.33417 | 9.8831 | 9.2102 | -113.3286 | -113.8046 | 9.3979 | 9.0088 | 9.4757 | 8.9447
1510.0781 | 122.644 | -9.1049 | 113.5986 | 0.0034333 | -0.060618 | 0.012975 | 0.029811 | -0.00074986 | -0.0062057 | 0.00093565 | -0.0044556 | 0.011324 | 0.020568 | 0.015325 | -0.0028155 | 0.006742 | 0.005003 | 0.63629 | 0.73242 | 0.25177 | 0.30212 | 0.50354 | 0.37079 | 0.44403 | -0.13733 | 0.11444 | -0.18768 | -0.10529 | 0.004578 | -0.07782 | 0.045776 | 9.3567 | -112.8662 | -113.2965 | 9.6085 | 9.549 | 9.4757 | 0.19226 | 0.11902 | 8.9172 | -113.4842 | -113.7039 | 9.1095 | 9.1507 | 9.0271 | 0.23346 | 0.10986 | 0.25177 | 0.050354 | 0.19226 | 0.082397 | 0.48065 | 0.30212 | 9.8373 | 9.2194 | -113.3469 | -113.7863 | 9.407 | 8.9996 | 9.7412 | 8.9676
1511.8281 | 122.7173 | -8.9951 | 113.6719 | 0.0034333 | -0.056772 | 0.013189 | 0.030238 | 0.0041635 | -0.0025741 | 0.0030718 | 0.001648 | 0.014315 | 0.022063 | 0.019384 | 0.0018841 | 0.0088782 | 0.001585 | 0.58594 | 0.56305 | 0.12817 | 0.24719 | 0.45319 | 0.27924 | 0.37537 | -0.045776 | 0.082397 | -0.17395 | -0.018311 | 0.073242 | -0.009155 | 0.10071 | 9.1232 | -113.1088 | -113.4247 | 9.4482 | 9.3704 | 9.2743 | 0.24719 | 0.15106 | 8.8211 | -113.5895 | -113.6902 | 9.0683 | 9.0958 | 8.9859 | 0.27466 | 0.16479 | 0.32501 | 0.11902 | 0.24719 | 0.15564 | 0.43488 | 0.25635 | 9.5581 | 9.0775 | -113.5437 | -113.8458 | 9.2422 | 8.9767 | 9.581 | 8.9493
1513.5156 | 122.6898 | -9.5489 | 113.1638 | 0.0034333 | -0.061045 | 0.012975 | 0.030452 | 0.0062997 | -0.0034287 | 0.0020038 | 0.001648 | 0.014101 | 0.019713 | 0.020879 | -0.0015337 | 0.0082374 | 0.0041486 | 0.49896 | 0.76446 | 0.25635 | 0.3479 | 0.5127 | 0.38452 | 0.4303 | -0.086975 | 0.1236 | -0.16479 | -0.036621 | 0.059509 | -0.054932 | 0.09613 | 9.8053 | -112.3993 | -112.8159 | 10.0616 | 9.9792 | 9.9335 | 0.17395 | 0.12817 | 9.3842 | -113.0402 | -113.2004 | 9.6085 | 9.6451 | 9.494 | 0.26092 | 0.10986 | 0.25635 | 0.091552 | 0.2243 | 0.12817 | 0.50812 | 0.28839 | 10.3134 | 9.6725 | -112.9074 | -113.3286 | 9.8968 | 9.5123 | 10.0479 | 9.462
1515.25 | 122.6898 | -12.2726 | 110.408 | 0.018692 | -0.057627 | 0.012335 | 0.031947 | 0.0028817 | -0.0047103 | -0.00013235 | 0.0046998 | 0.014742 | 0.022704 | 0.020239 | 0.0025251 | 0.0086646 | 0.00030339 | 0.32044 | 0.59967 | 0.10529 | 0.16022 | 0.32959 | 0.19226 | 0.28381 | -0.10986 | 0.13733 | -0.19684 | -0.059509 | 0.018311 | -0.09613 | 0.068665 | 12.3779 | -109.8083 | -110.2478 | 12.6022 | 12.5565 | 12.4649 | 0.17853 | 0.086975 | 12.0758 | -110.2707 | -110.4675 | 12.291 | 12.3413 | 12.1765 | 0.2655 | 0.10071 | 0.2243 | 0.054931 | 0.21515 | 0.13733 | 0.49438 | 0.33417 | 12.8723 | 12.41 | -110.3027 | -110.6049 | 12.4329 | 12.2131 | 12.5931 | 12.1628
1517 | 122.6715 | -10.8353 | 111.8408 | 0.011063 | -0.058909 | 0.013403 | 0.030238 | 0.0020273 | -0.00043789 | -0.0016278 | 0.0046998 | 0.016237 | 0.022704 | 0.018102 | 0.0025251 | 0.0086646 | -0.0037554 | 0.33417 | 0.60883 | 0.10986 | 0.16022 | 0.35706 | 0.21057 | 0.28381 | -0.1236 | 0.13275 | -0.19226 | -0.064087 | 0 | -0.11444 | 0.064087 | 10.9451 | -111.232 | -111.6806 | 11.1923 | 11.1191 | 11.0458 | 0.17395 | 0.10071 | 10.643 | -111.7081 | -111.9049 | 10.8353 | 10.8994 | 10.7208 | 0.25635 | 0.07782 | 0.24719 | 0.050354 | 0.19226 | 0.12817 | 0.49896 | 0.32501 | 11.4441 | 10.968 | -111.731 | -112.0331 | 10.9955 | 10.7712 | 11.1694 | 10.7117
1518.7344 | 122.7219 | -7.6538 | 115.0635 | 0.011063 | -0.056772 | 0.013403 | 0.030025 | 0.0048043 | -0.0034287 | 0.0013628 | 0.0046998 | 0.014315 | 0.0195 | 0.020452 | 0.0025251 | 0.0073828 | -0.00055121 | 0.3479 | 0.62256 | 0.15106 | 0.20599 | 0.3891 | 0.21973 | 0.32959 | -0.059509 | 0.10529 | -0.1831 | 0.004578 | 0.07782 | -0.022888 | 0.11444 | 7.8049 | -114.4409 | -114.8575 | 8.0429 | 7.9834 | 7.8735 | 0.17853 | 0.068665 | 7.4707 | -114.9582 | -115.0589 | 7.7316 | 7.7683 | 7.6309 | 0.29755 | 0.16022 | 0.23804 | 0.054932 | 0.26092 | 0.18768 | 0.4715 | 0.28839 | 8.2764 | 7.7591 | -114.9124 | -115.2466 | 7.8598 | 7.6584 | 8.0017 | 7.5943
1520.4844 | 122.7173 | -7.5439 | 115.1184 | 0.018692 | -0.058054 | 0.012975 | 0.029811 | 0.0048043 | -0.0015061 | 0.0015764 | 0.0046998 | 0.014315 | 0.022917 | 0.020239 | -0.0011065 | 0.011014 | 0.00051699 | 0.33875 | 0.54474 | 0.15564 | 0.24719 | 0.44403 | 0.27924 | 0.36163 | -0.027466 | 0.073242 | -0.16022 | 0 | 0.086975 | -0.009155 | 0.10986 | 7.6996 | -114.5737 | -114.8712 | 7.988 | 7.9056 | 7.8232 | 0.20599 | 0.1236 | 7.3837 | -115.0452 | -115.1184 | 7.6309 | 7.6538 | 7.5348 | 0.27008 | 0.15106 | 0.28839 | 0.091552 | 0.24719 | 0.16022 | 0.3891 | 0.23346 | 8.0887 | 7.6172 | -114.9628 | -115.2786 | 7.7911 | 7.5439 | 7.8827 | 7.5165
1522.1719 | 122.7219 | -9.1507 | 113.5071 | -0.0041962 | -0.057627 | 0.013189 | 0.03152 | 0.0065133 | -0.0012925 | 8.125e-05 | 0.001648 | 0.012179 | 0.022917 | 0.018957 | 0.00038887 | 0.0086646 | -0.00012381 | 0.3479 | 0.55389 | 0.16937 | 0.27466 | 0.45776 | 0.28839 | 0.37537 | -0.068665 | 0.086975 | -0.16937 | -0.022888 | 0.064087 | -0.027466 | 0.10071 | 9.3201 | -112.9532 | -113.2324 | 9.6085 | 9.5261 | 9.4391 | 0.20599 | 0.11902 | 8.9813 | -113.4201 | -113.53 | 9.2148 | 9.2514 | 9.1232 | 0.27008 | 0.14191 | 0.28839 | 0.10529 | 0.23346 | 0.14649 | 0.38452 | 0.25635 | 9.7046 | 9.2377 | -113.3377 | -113.6765 | 9.4254 | 9.1278 | 9.4986 | 9.082
1523.9062 | 122.7493 | -8.519 | 114.1479 | 0.011063 | -0.05955 | 0.011907 | 0.028102 | 0.0015999 | -0.0030015 | 0.0039264 | 0.0046998 | 0.011751 | 0.023131 | 0.022588 | -0.0017475 | 0.008451 | 0.0047894 | 0.39825 | 0.64087 | 0.21057 | 0.30212 | 0.48523 | 0.32501 | 0.40283 | -0.064087 | 0.091553 | -0.17853 | -0.032043 | 0.073242 | -0.032043 | 0.10986 | 8.7296 | -113.5071 | -113.8458 | 9.0042 | 8.9218 | 8.844 | 0.19226 | 0.11444 | 8.3405 | -114.0564 | -114.18 | 8.5922 | 8.6288 | 8.4869 | 0.28839 | 0.14648 | 0.27466 | 0.091553 | 0.25177 | 0.14648 | 0.4303 | 0.27008 | 9.1599 | 8.6105 | -113.9374 | -114.3265 | 8.8211 | 8.4869 | 8.9172 | 8.4549
1525.6562 | 122.6578 | -7.9514 | 114.8117 | 0.0034333 | -0.058909 | 0.013403 | 0.032588 | 0.0043771 | -0.0019333 | 8.125e-05 | 0.001648 | 0.01581 | 0.021636 | 0.012762 | 0.0012433 | 0.0054602 | -0.00097841 | 0.40741 | 0.66834 | 0.19226 | 0.24719 | 0.42572 | 0.27466 | 0.32959 | -0.14648 | 0.12817 | -0.20599 | -0.082397 | -0.036621 | -0.14191 | 0.027466 | 8.1436 | -114.1434 | -114.5645 | 8.3771 | 8.2809 | 8.226 | 0.13733 | 0.082397 | 7.7454 | -114.6835 | -114.8941 | 7.9147 | 7.9788 | 7.8094 | 0.23346 | 0.064087 | 0.23346 | 0.054931 | 0.16937 | 0.1236 | 0.47607 | 0.33417 | 8.6197 | 8.0795 | -114.6194 | -115.0177 | 8.1985 | 7.869 | 8.3588 | 7.8049
1527.3438 | 122.6898 | -7.8369 | 114.8987 | 0.011063 | -0.061045 | 0.0097712 | 0.031093 | 0.0058725 | -0.00065149 | 0.0015764 | 0.0046998 | 0.013674 | 0.019927 | 0.015539 | 0.00038887 | 0.00781 | -0.0014056 | 0.48981 | 0.70953 | 0.23804 | 0.3479 | 0.54932 | 0.38452 | 0.44861 | -0.064087 | 0.1236 | -0.1831 | -0.041199 | 0.045776 | -0.054932 | 0.07782 | 8.075 | -114.1891 | -114.5508 | 8.3862 | 8.2855 | 8.2214 | 0.21057 | 0.14648 | 7.6538 | -114.7751 | -114.9399 | 7.8827 | 7.9147 | 7.782 | 0.26092 | 0.12817 | 0.31128 | 0.10986 | 0.22888 | 0.14191 | 0.4715 | 0.3067 | 8.5464 | 7.9605 | -114.6606 | -115.0818 | 8.1848 | 7.7957 | 8.3267 | 7.7728
1529.0938 | 122.7676 | -7.6447 | 115.004 | 0.0034333 | -0.061472 | 0.011267 | 0.02917 | 0.0018137 | -0.0027877 | -0.00055975 | 0.0077514 | 0.01282 | 0.022277 | 0.015753 | -0.0015337 | 0.0088782 | 0.00030339 | 0.42114 | 0.63629 | 0.22888 | 0.34332 | 0.53558 | 0.39368 | 0.46692 | -0.050354 | 0.10071 | -0.1831 | 0 | 0.1236 | 0.041199 | 0.15106 | 7.8735 | -114.3677 | -114.6606 | 8.1802 | 8.1116 | 8.0383 | 0.23804 | 0.16479 | 7.4615 | -114.9033 | -115.004 | 7.7682 | 7.7957 | 7.6859 | 0.33417 | 0.2243 | 0.3067 | 0.11444 | 0.3067 | 0.1831 | 0.40741 | 0.28381 | 8.2809 | 7.7454 | -114.7751 | -115.1871 | 7.988 | 7.6447 | 8.0658 | 7.5943
1530.7812 | 122.699 | -7.5943 | 115.1093 | 0.011063 | -0.057413 | 0.010198 | 0.03152 | 0.00095914 | -0.0040695 | -0.00055975 | 0.001648 | 0.015383 | 0.023345 | 0.017248 | 0.0027387 | 0.006101 | 0.0043622 | 0.3891 | 0.67749 | 0.20142 | 0.22888 | 0.4303 | 0.26093 | 0.35248 | -0.09613 | 0.11444 | -0.19684 | -0.045776 | 0.045776 | -0.050354 | 0.10529 | 7.7957 | -114.4318 | -114.8804 | 8.0246 | 7.9468 | 7.8552 | 0.15106 | 0.059509 | 7.3975 | -114.9948 | -115.155 | 7.6401 | 7.6996 | 7.5439 | 0.30212 | 0.14648 | 0.22888 | 0.027466 | 0.24261 | 0.15106 | 0.47607 | 0.31128 | 8.2718 | 7.7087 | -114.9078 | -115.3061 | 7.8232 | 7.5485 | 7.9834 | 7.4982
1532.5312 | 122.7997 | -7.4844 | 115.1459 | 0.0034333 | -0.059977 | 0.008703 | 0.028102 | 0.0037363 | -0.0030015 | 0.0026446 | 0.001648 | 0.014101 | 0.019713 | 0.021307 | -0.0017475 | 0.006742 | -0.00055121 | 0.54932 | 0.72327 | 0.31586 | 0.46692 | 0.70038 | 0.52643 | 0.57678 | 0.032043 | 0.091553 | -0.17395 | 0.027466 | 0.14191 | 0.064087 | 0.14191 | 7.8003 | -114.4226 | -114.679 | 8.1848 | 8.0612 | 8.0109 | 0.26093 | 0.21057 | 7.3105 | -115.0543 | -115.1184 | 7.6263 | 7.6263 | 7.5485 | 0.31586 | 0.23804 | 0.38452 | 0.15106 | 0.31586 | 0.20142 | 0.40741 | 0.2655 | 8.2077 | 7.576 | -114.83 | -115.3198 | 7.9514 | 7.5119 | 8.0338 | 7.5165
1534.2812 | 122.7814 | -7.5119 | 115.1001 | 0.0034333 | -0.060618 | 0.013403 | 0.029598 | 0.0035227 | -0.0019333 | -0.00013235 | 0.0077514 | 0.012606 | 0.023986 | 0.012975 | 0.0033795 | 0.0090918 | 0.0030804 | 0.45319 | 0.62256 | 0.23346 | 0.3479 | 0.54474 | 0.36621 | 0.43488 | 0.027466 | 0.10071 | -0.16022 | 0.041199 | 0.12817 | 0.027466 | 0.15564 | 7.7454 | -114.4775 | -114.7522 | 8.0566 | 7.9468 | 7.8781 | 0.20142 | 0.13275 | 7.3517 | -114.9994 | -115.0589 | 7.6401 | 7.6675 | 7.5394 | 0.31586 | 0.18768 | 0.31128 | 0.11444 | 0.28839 | 0.20142 | 0.3891 | 0.26093 | 8.1345 | 7.6126 | -114.8666 | -115.2603 | 7.8598 | 7.5531 | 7.9651 | 7.5394
1536.0469 | 122.7585 | -7.402 | 115.2649 | 0.011063 | -0.059122 | 0.010198 | 0.027248 | 0.00010474 | -0.0034287 | 0.0011492 | -0.0014038 | 0.012606 | 0.020354 | 0.029424 | -0.0023883 | 0.0058874 | 8.9786e-05 | 0.48065 | 0.67749 | 0.28381 | 0.39368 | 0.58136 | 0.45319 | 0.50354 | -0.050354 | 0.11444 | -0.1831 | -0.009155 | 0.10529 | 0.004578 | 0.13275 | 7.6859 | -114.5874 | -114.8712 | 7.9834 | 7.9056 | 7.8552 | 0.21973 | 0.16937 | 7.2189 | -115.1505 | -115.274 | 7.5073 | 7.5348 | 7.4066 | 0.31586 | 0.18768 | 0.29755 | 0.10986 | 0.28839 | 0.17395 | 0.39368 | 0.29755 | 8.0795 | 7.5165 | -114.9811 | -115.448 | 7.7957 | 7.3929 | 7.8827 | 7.3517
1537.7344 | 122.6669 | -105.098 | 17.3904 | 0.018692 | -0.06019 | 0.013189 | 0.029811 | 0.0056589 | -0.0047103 | 0.0026446 | 0.001648 | 0.014315 | 0.020995 | 0.022161 | 0.0044477 | 0.0090918 | 0.00030339 | -0.46234 | -0.086975 | -0.52185 | -0.4303 | -0.20142 | -0.33875 | -0.28839 | 0.022888 | 0.15564 | -0.10986 | 0.082397 | 0.16937 | 0.064087 | 0.19684 | 104.5761 | -17.4774 | -17.8207 | 104.8965 | 104.8096 | 104.7592 | 0.23346 | 0.18311 | 104.9881 | -17.2348 | -17.308 | 105.2673 | 105.2948 | 105.162 | 0.3067 | 0.17395 | 0.32043 | 0.091553 | 0.27924 | 0.19226 | 0.43488 | 0.2655 | 105.011 | 105.2536 | -17.9123 | -17.5003 | 104.6677 | 105.1804 | 104.6356 | 105.1208
1539.4844 | 122.6898 | -122.1405 | 0.55847 | 0.0034333 | -0.06019 | 0.0093438 | 0.030452 | 0.0037363 | -0.0036423 | 0.0026446 | 0.001648 | 0.014956 | 0.02249 | 0.017034 | 0.00017507 | 0.0073828 | 0.001585 | -0.43945 | -0.073242 | -0.54016 | -0.40283 | -0.28839 | -0.40741 | -0.31586 | -0.022888 | 0.20599 | -0.11902 | 0.013733 | 0.10986 | -0.004578 | 0.16022 | 121.6003 | -0.63171 | -0.9613 | 121.8521 | 121.8246 | 121.7331 | 0.2243 | 0.13275 | 122.0215 | -0.35248 | -0.54474 | 122.2504 | 122.3007 | 122.1359 | 0.27924 | 0.11444 | 0.25177 | 0.13733 | 0.22888 | 0.13275 | 0.46692 | 0.32501 | 122.0673 | 122.3465 | -1.0986 | -0.67749 | 121.7377 | 122.1542 | 121.701 | 122.1176
1541.25 | 122.7768 | -122.1176 | 0.51727 | 0.0034333 | -0.060831 | 0.0091302 | 0.027034 | -0.00074986 | -0.0034287 | -0.0012006 | 0.001648 | 0.013888 | 0.02014 | 0.019384 | -0.0030291 | 0.0093054 | -0.00097841 | -0.40741 | -0.13733 | -0.54016 | -0.39825 | -0.1236 | -0.33875 | -0.27008 | 0.09613 | 0.14648 | -0.10071 | 0.091553 | 0.21515 | 0.11902 | 0.21515 | 121.5775 | -0.6546 | -0.91553 | 121.994 | 121.8475 | 121.7789 | 0.27008 | 0.20142 | 122.0169 | -0.37079 | -0.42572 | 122.3328 | 122.3328 | 122.2366 | 0.31586 | 0.21973 | 0.41657 | 0.14191 | 0.31586 | 0.19226 | 0.40283 | 0.24719 | 121.9803 | 122.2641 | -1.0574 | -0.61798 | 121.7194 | 122.2092 | 121.7102 | 122.2137
1543 | 122.5616 | -119.0964 | 3.5477 | 0.0034333 | -0.06254 | 0.013616 | 0.032375 | 0.0037363 | -0.0021469 | 8.125e-05 | 0.001648 | 0.016665 | 0.02249 | 0.018316 | 0.0018841 | 0.006742 | -0.0014056 | -0.54474 | -0.16479 | -0.63629 | -0.59052 | -0.42572 | -0.55847 | -0.47607 | -0.045776 | 0.17853 | -0.11444 | 0.018311 | 0.059509 | -0.045776 | 0.1236 | 118.4601 | -3.7125 | -4.1382 | 118.6707 | 118.6203 | 118.5379 | 0.16022 | 0.07782 | 118.9819 | -3.3691 | -3.5294 | 119.1559 | 119.22 | 119.0506 | 0.23804 | 0.068665 | 0.21057 | 0.045777 | 0.17395 | 0.13275 | 0.4715 | 0.29297 | 118.9316 | 119.2749 | -4.184 | -3.6621 | 118.5059 | 119.1147 | 118.5516 | 119.0506
1544.6719 | 122.525 | -118.0161 | 4.3854 | -0.0041962 | -0.05955 | 0.014471 | 0.028529 | 0.0018137 | -0.0059921 | 0.00072205 | 0.0077514 | 0.010897 | 0.021636 | 0.017462 | -0.0015337 | 0.0065284 | 0.00094419 | -0.33875 | -0.10529 | -0.48065 | -0.35248 | -0.15564 | -0.32959 | -0.24261 | 0.09613 | 0.14191 | -0.09613 | 0.11444 | 0.21973 | 0.1236 | 0.21515 | 117.5354 | -4.4907 | -4.7379 | 117.8604 | 117.7734 | 117.6865 | 0.23804 | 0.15106 | 117.9199 | -4.2435 | -4.2709 | 118.2358 | 118.2312 | 118.1396 | 0.31128 | 0.21973 | 0.32501 | 0.12817 | 0.31586 | 0.21057 | 0.37537 | 0.23804 | 117.9108 | 118.158 | -4.866 | -4.4815 | 117.6636 | 118.1305 | 117.6773 | 118.1122
1546.4219 | 122.3282 | -118.0573 | 4.1519 | 0.011063 | -0.059763 | 0.013189 | 0.028529 | -0.00032266 | -0.0025741 | 8.125e-05 | 0.001648 | 0.012392 | 0.019927 | 0.019384 | -0.0011065 | 0.006742 | 0.003294 | -0.46234 | -0.16937 | -0.56763 | -0.48981 | -0.30212 | -0.44861 | -0.36621 | 0.013733 | 0.16937 | -0.1236 | 0.050354 | 0.14648 | 0.050354 | 0.17853 | 117.4896 | -4.3213 | -4.6417 | 117.7551 | 117.691 | 117.6086 | 0.20142 | 0.11902 | 117.9337 | -3.9825 | -4.1016 | 118.2037 | 118.2358 | 118.1076 | 0.30212 | 0.17395 | 0.2655 | 0.07782 | 0.27008 | 0.17395 | 0.39825 | 0.29297 | 117.8879 | 118.2266 | -4.7195 | -4.2755 | 117.5674 | 118.1076 | 117.5949 | 118.071
1548.1562 | 122.1268 | -118.3411 | 3.7811 | 0.011063 | -0.057627 | 0.0097712 | 0.029598 | 0.0054453 | -0.0040695 | -0.00013235 | 0.0046998 | 0.013888 | 0.020568 | 0.01618 | -0.0015337 | 0.0071692 | 0.0020124 | -0.25635 | 0.059509 | -0.39825 | -0.32959 | -0.16022 | -0.27466 | -0.19684 | -0.054932 | 0.20142 | -0.11902 | 0.009155 | 0.10529 | 0.018311 | 0.16022 | 117.9428 | -3.7216 | -4.1107 | 118.1808 | 118.1442 | 118.0664 | 0.20142 | 0.1236 | 118.222 | -3.5797 | -3.772 | 118.4464 | 118.5013 | 118.3594 | 0.27924 | 0.13733 | 0.23804 | 0.068664 | 0.22431 | 0.12817 | 0.45776 | 0.32044 | 118.4006 | 118.5425 | -4.1794 | -3.9001 | 118.0115 | 118.3502 | 118.0847 | 118.2861
1549.8438 | 122.1634 | -118.4967 | 3.479 | 0.0034333 | -0.059977 | 0.011267 | 0.027675 | 0.0015999 | -0.0032151 | -0.00055975 | 0.0046998 | 0.011324 | 0.023558 | 0.020452 | -3.8532e-05 | 0.0054602 | 0.0011578 | -0.27466 | -0.059509 | -0.44403 | -0.29755 | -0.086975 | -0.23804 | -0.1831 | 0.086975 | 0.16022 | -0.09613 | 0.10529 | 0.2243 | 0.11902 | 0.21973 | 118.0527 | -3.5385 | -3.7766 | 118.4097 | 118.3136 | 118.2587 | 0.26093 | 0.20599 | 118.4006 | -3.3188 | -3.3737 | 118.721 | 118.7164 | 118.6157 | 0.31586 | 0.21515 | 0.35706 | 0.14649 | 0.32043 | 0.20142 | 0.38452 | 0.25635 | 118.4372 | 118.6569 | -3.923 | -3.5751 | 118.1992 | 118.602 | 118.222 | 118.5837
1551.5938 | 121.9757 | -118.6386 | 3.4287 | 0.0034333 | -0.058054 | 0.011907 | 0.028743 | 0.0033089 | -0.0055649 | -0.00077335 | 0.0046998 | 0.015169 | 0.022704 | 0.015753 | -0.0032427 | 0.0056738 | -0.00012381 | -0.2243 | -0.004578 | -0.41657 | -0.29297 | -0.082397 | -0.23804 | -0.19226 | -0.004578 | 0.1831 | -0.10529 | 0 | 0.10529 | 0.013733 | 0.13733 | 118.222 | -3.4332 | -3.7216 | 118.5562 | 118.4463 | 118.4006 | 0.2243 | 0.17853 | 118.5333 | -3.2455 | -3.4287 | 118.7439 | 118.7759 | 118.6523 | 0.24262 | 0.11902 | 0.33417 | 0.1236 | 0.21057 | 0.10529 | 0.41199 | 0.28839 | 118.634 | 118.8217 | -3.8452 | -3.5339 | 118.3456 | 118.6386 | 118.4143 | 118.634
1553.3594 | 122.0078 | -118.515 | 3.4882 | 0.011063 | -0.059122 | 0.011267 | 0.032802 | 0.0065133 | -0.0030015 | 0.0011492 | 0.001648 | 0.014742 | 0.021636 | 0.016607 | 0.0012433 | 0.0080236 | -0.00012381 | -0.40741 | -0.10529 | -0.54474 | -0.49896 | -0.32501 | -0.48523 | -0.39368 | -0.059509 | 0.18768 | -0.1236 | 0.009155 | 0.07782 | -0.027466 | 0.13275 | 117.9703 | -3.5934 | -3.9871 | 118.19 | 118.1213 | 118.0298 | 0.15106 | 0.05951 | 118.3914 | -3.3005 | -3.479 | 118.5928 | 118.6478 | 118.4875 | 0.25635 | 0.09613 | 0.21973 | 0.045777 | 0.20142 | 0.13275 | 0.43945 | 0.31128 | 118.4097 | 118.7027 | -4.0329 | -3.6118 | 118.0161 | 118.5242 | 118.1076 | 118.4555
1555.1094 | 122.081 | -118.5837 | 3.3371 | 0.0034333 | -0.061899 | 0.010412 | 0.027889 | 0.0071541 | -0.0032151 | 0.00029485 | 0.001648 | 0.011965 | 0.021849 | 0.022588 | -0.00025213 | 0.0046058 | 0.0035078 | -0.34332 | -0.10529 | -0.48523 | -0.38452 | -0.17853 | -0.32501 | -0.26093 | 0.018311 | 0.16937 | -0.10986 | 0.068665 | 0.1831 | 0.10529 | 0.21057 | 118.0984 | -3.4424 | -3.7216 | 118.4052 | 118.3228 | 118.2587 | 0.2243 | 0.16022 | 118.4738 | -3.1677 | -3.2684 | 118.7668 | 118.7943 | 118.689 | 0.32043 | 0.21515 | 0.3067 | 0.10071 | 0.29297 | 0.17853 | 0.37994 | 0.27924 | 118.4784 | 118.7531 | -3.8223 | -3.447 | 118.1992 | 118.6523 | 118.2404 | 118.602
1556.8125 | 122.0261 | -117.2745 | 4.5868 | 0.011063 | -0.06019 | 0.013403 | 0.029598 | 0.0024545 | -0.0019333 | -0.00034615 | 0.001648 | 0.013033 | 0.022063 | 0.019811 | -0.0017475 | 0.0073828 | 0.001585 | -0.37079 | -0.11444 | -0.49896 | -0.3891 | -0.21057 | -0.36621 | -0.28381 | 0 | 0.16937 | -0.10986 | 0.064087 | 0.14648 | 0.068665 | 0.18768 | 116.7755 | -4.7012 | -4.9759 | 117.0639 | 116.9907 | 116.9083 | 0.21515 | 0.13275 | 117.1646 | -4.4174 | -4.5227 | 117.421 | 117.4622 | 117.3431 | 0.29755 | 0.17853 | 0.28839 | 0.10986 | 0.25635 | 0.17395 | 0.38452 | 0.27924 | 117.16 | 117.4438 | -5.0858 | -4.6967 | 116.8854 | 117.3386 | 116.9037 | 117.2745
1558.5625 | 122.0078 | -118.1717 | 3.6896 | 0.0034333 | -0.060831 | 0.014471 | 0.029811 | 0.0022409 | -0.0019333 | 0.0017902 | 0.0046998 | 0.011538 | 0.022704 | 0.022375 | 0.0018841 | 0.0075964 | -0.00076481 | -0.3479 | -0.19226 | -0.53558 | -0.40283 | -0.19226 | -0.3891 | -0.30212 | 0.086975 | 0.14648 | -0.086975 | 0.10529 | 0.17853 | 0.07782 | 0.21515 | 117.6361 | -3.8818 | -4.0924 | 117.9794 | 117.8696 | 117.7826 | 0.23346 | 0.14648 | 118.0847 | -3.5431 | -3.5843 | 118.3502 | 118.3868 | 118.2495 | 0.30212 | 0.16479 | 0.34332 | 0.13275 | 0.2655 | 0.19226 | 0.34332 | 0.23346 | 117.9794 | 118.3182 | -4.2252 | -3.7765 | 117.7689 | 118.277 | 117.8238 | 118.2587
1560.3125 | 122.0123 | -118.0573 | 3.7399 | 0.0034333 | -0.059763 | 0.01383 | 0.02917 | 0.0030953 | -0.0036423 | -0.00055975 | -0.0014038 | 0.015169 | 0.022277 | 0.016393 | -0.0017475 | 0.0071692 | -0.0043964 | -0.23346 | -0.059509 | -0.4303 | -0.27924 | -0.064087 | -0.23804 | -0.17853 | 0.10071 | 0.16937 | -0.082397 | 0.10529 | 0.21057 | 0.14191 | 0.21515 | 117.627 | -3.7994 | -4.0192 | 117.9932 | 117.8787 | 117.8192 | 0.25177 | 0.19226 | 117.9749 | -3.5706 | -3.6346 | 118.2678 | 118.2724 | 118.1992 | 0.29755 | 0.2243 | 0.36621 | 0.15106 | 0.29297 | 0.18768 | 0.37079 | 0.25177 | 117.9977 | 118.2266 | -4.1702 | -3.8223 | 117.778 | 118.1625 | 117.8238 | 118.158
1562.0156 | 121.875 | -118.0573 | 3.804 | 0.0034333 | -0.060618 | 0.012121 | 0.029811 | 0.0022409 | -0.0059921 | -0.0020552 | 0.0046998 | 0.014101 | 0.021209 | 0.018743 | -0.0051653 | 0.006742 | -0.0016192 | -0.2243 | -0.022888 | -0.40283 | -0.27924 | -0.091553 | -0.21057 | -0.1831 | 0.009155 | 0.17395 | -0.11902 | 0.004578 | 0.10529 | 0.018311 | 0.13275 | 117.6544 | -3.8269 | -4.0833 | 117.9657 | 117.8741 | 117.8467 | 0.21973 | 0.19226 | 117.9382 | -3.6301 | -3.7994 | 118.1625 | 118.19 | 118.0756 | 0.25177 | 0.13733 | 0.31128 | 0.1236 | 0.22431 | 0.1236 | 0.37994 | 0.29297 | 118.0344 | 118.2312 | -4.2068 | -3.923 | 117.778 | 118.0618 | 117.8329 | 118.0664
1563.7656 | 121.9162 | -118.2266 | 3.6072 | 0.0034333 | -0.060618 | 0.011053 | 0.028957 | 0.0015999 | -0.0053513 | -0.00098695 | -0.0014038 | 0.014101 | 0.022277 | 0.017462 | -0.0013201 | 0.0071692 | 0.0011578 | -0.21973 | -0.032043 | -0.4303 | -0.28381 | -0.082397 | -0.21973 | -0.17853 | 0.059509 | 0.16479 | -0.10529 | 0.045776 | 0.16022 | 0.064087 | 0.16937 | 117.7963 | -3.6392 | -3.891 | 118.1442 | 118.0481 | 118.0069 | 0.25177 | 0.21057 | 118.1213 | -3.4424 | -3.5614 | 118.3868 | 118.396 | 118.2907 | 0.27466 | 0.16937 | 0.3479 | 0.14649 | 0.2655 | 0.15106 | 0.39826 | 0.27008 | 118.1946 | 118.3914 | -4.0375 | -3.7125 | 117.9428 | 118.2724 | 118.0069 | 118.2861
1565.5312 | 121.9894 | -2.0096 | 119.989 | 0.011063 | -0.060831 | 0.0082758 | 0.028743 | 0.0024545 | -0.0038559 | 0.0015764 | -0.0014038 | 0.01282 | 0.019072 | 0.017248 | 0.0014569 | 0.0086646 | -0.00097841 | 0.25635 | 0.57678 | 0.16479 | 0.28381 | 0.46692 | 0.3067 | 0.37994 | -0.082397 | 0.082397 | -0.18768 | -0.022888 | 0.064087 | -0.032043 | 0.10529 | 2.1744 | -119.4122 | -119.7052 | 2.4765 | 2.3895 | 2.3163 | 0.21515 | 0.14191 | 1.8219 | -119.9066 | -120.0119 | 2.0737 | 2.1149 | 1.9775 | 0.29297 | 0.15564 | 0.30212 | 0.11902 | 0.25177 | 0.16479 | 0.41199 | 0.27008 | 2.5864 | 2.092 | -119.8242 | -120.1767 | 2.2934 | 1.9867 | 2.2659 | 1.9272
1567.2344 | 122.0535 | -2.3392 | 119.8151 | -0.0041962 | -0.059763 | 0.011053 | 0.029598 | 0.0054453 | -0.0042831 | 0.0013628 | 0.001648 | 0.015597 | 0.023345 | 0.018102 | -0.0011065 | 0.006742 | 0.00030339 | 0.3067 | 0.72784 | 0.24719 | 0.31586 | 0.46234 | 0.34332 | 0.40283 | -0.16022 | 0.11444 | -0.21057 | -0.082397 | 0.027466 | -0.086975 | 0.059509 | 2.5864 | -119.0872 | -119.4992 | 2.8015 | 2.742 | 2.6825 | 0.15564 | 0.096131 | 2.1286 | -119.7006 | -119.8975 | 2.3666 | 2.3987 | 2.2522 | 0.27008 | 0.1236 | 0.21515 | 0.068665 | 0.23804 | 0.12817 | 0.48065 | 0.32501 | 3.067 | 2.4536 | -119.5679 | -120.0256 | 2.655 | 2.2568 | 2.6459 | 2.179
1569 | 122.1863 | -2.4719 | 119.6594 | 0.011063 | -0.057413 | 0.01383 | 0.032161 | 0.0073679 | -0.0023605 | -0.00055975 | -0.0014038 | 0.015597 | 0.021636 | 0.022802 | 0.0014569 | 0.0088782 | -0.0024738 | 0.21057 | 0.51727 | 0.11902 | 0.24719 | 0.43945 | 0.24261 | 0.32044 | -0.018311 | 0.09613 | -0.16937 | 0.027466 | 0.11902 | 0.004578 | 0.14648 | 2.5909 | -119.1422 | -119.4122 | 2.9114 | 2.7924 | 2.7145 | 0.20142 | 0.1236 | 2.3026 | -119.5633 | -119.632 | 2.5909 | 2.6184 | 2.4765 | 0.31586 | 0.17395 | 0.32043 | 0.12817 | 0.28839 | 0.19684 | 0.39825 | 0.2655 | 2.9892 | 2.5681 | -119.5404 | -119.8288 | 2.7191 | 2.4994 | 2.6825 | 2.4536
1570.6719 | 122.2092 | -2.4948 | 119.6594 | 0.0034333 | -0.059122 | 0.011267 | 0.028316 | 0.0033089 | -0.0042831 | 0.0020038 | -0.0014038 | 0.01346 | 0.022277 | 0.025793 | -0.0015337 | 0.0058874 | -0.00033761 | 0.32959 | 0.61798 | 0.25177 | 0.40283 | 0.63171 | 0.46692 | 0.51727 | 0.032043 | 0.086975 | -0.17853 | 0.022888 | 0.16479 | 0.059509 | 0.14191 | 2.7466 | -119.0414 | -119.2566 | 3.1265 | 3.0121 | 2.9617 | 0.2655 | 0.21515 | 2.3163 | -119.5724 | -119.6365 | 2.6596 | 2.6367 | 2.5543 | 0.32044 | 0.23804 | 0.37994 | 0.15106 | 0.34332 | 0.20142 | 0.36621 | 0.2655 | 3.1128 | 2.5818 | -119.4077 | -119.838 | 2.8976 | 2.5177 | 2.8244 | 2.5269
1572.4219 | 122.1954 | -2.5223 | 119.6274 | 0.0034333 | -0.060404 | 0.012975 | 0.030025 | 0.0035227 | -0.0027877 | 0.00050845 | 0.0046998 | 0.013888 | 0.02249 | 0.020452 | 0.00060247 | 0.00781 | -0.00033761 | 0.24719 | 0.48981 | 0.10986 | 0.27466 | 0.48523 | 0.28839 | 0.36163 | 0.018311 | 0.082397 | -0.17395 | 0.018311 | 0.12817 | 0.022888 | 0.13733 | 2.6321 | -119.1376 | -119.3527 | 3.0075 | 2.8839 | 2.8107 | 0.25177 | 0.17853 | 2.3483 | -119.545 | -119.6091 | 2.6505 | 2.6596 | 2.5452 | 0.31128 | 0.19684 | 0.37537 | 0.1648 | 0.30212 | 0.19226 | 0.37994 | 0.25635 | 3.0121 | 2.6047 | -119.5175 | -119.8013 | 2.7969 | 2.5406 | 2.7695 | 2.5406
1574.1562 | 122.2229 | -2.5177 | 119.6503 | 0.011063 | -0.058695 | 0.01148 | 0.032375 | 0.0045907 | -0.0034287 | -0.00077335 | 0.001648 | 0.011965 | 0.021422 | 0.018102 | -0.0036701 | 0.0071692 | -0.001192 | 0.37994 | 0.62256 | 0.24719 | 0.43488 | 0.63171 | 0.4715 | 0.49896 | 0.022888 | 0.07782 | -0.1831 | 0.027466 | 0.15106 | 0.045776 | 0.12817 | 2.7649 | -119.0277 | -119.2154 | 3.1494 | 3.0167 | 2.9892 | 0.25177 | 0.22431 | 2.3346 | -119.5724 | -119.6228 | 2.6688 | 2.6459 | 2.5635 | 0.31128 | 0.22888 | 0.38452 | 0.18768 | 0.33417 | 0.21057 | 0.37537 | 0.26092 | 3.1403 | 2.5955 | -119.4031 | -119.8334 | 2.9526 | 2.5452 | 2.8976 | 2.5406
1575.8438 | 122.1863 | -2.449 | 119.7052 | -0.0041962 | -0.061259 | 0.010839 | 0.030238 | 0.0065133 | -0.0015061 | 0.0032854 | 0.001648 | 0.014742 | 0.021636 | 0.025152 | -3.8532e-05 | 0.0093054 | 0.00051699 | 0.25177 | 0.56763 | 0.16022 | 0.28381 | 0.45776 | 0.29755 | 0.37079 | -0.068665 | 0.082397 | -0.19684 | -0.027466 | 0.068665 | -0.018311 | 0.09613 | 2.6093 | -119.1376 | -119.4214 | 2.9068 | 2.8198 | 2.7466 | 0.21057 | 0.13733 | 2.2522 | -119.6228 | -119.7327 | 2.5177 | 2.5452 | 2.4307 | 0.29297 | 0.17853 | 0.29755 | 0.1236 | 0.2655 | 0.16937 | 0.40741 | 0.27924 | 3.0167 | 2.5314 | -119.545 | -119.902 | 2.7328 | 2.4216 | 2.7008 | 2.3804
1577.6094 | 122.168 | -2.4536 | 119.7601 | 0.018692 | -0.05955 | 0.014044 | 0.032161 | 0.0054453 | -0.0012925 | 0.00414 | 0.0046998 | 0.017092 | 0.023772 | 0.011053 | 0.0010297 | 0.005033 | -0.0048236 | 0.33875 | 0.65918 | 0.21973 | 0.32501 | 0.50812 | 0.35248 | 0.41199 | -0.050354 | 0.086975 | -0.18768 | -0.045776 | 0.050354 | -0.054932 | 0.086975 | 2.6733 | -119.101 | -119.4351 | 2.9617 | 2.8656 | 2.8061 | 0.19226 | 0.13275 | 2.2659 | -119.6732 | -119.8059 | 2.504 | 2.5406 | 2.3987 | 0.27466 | 0.13275 | 0.28839 | 0.10529 | 0.23804 | 0.14191 | 0.43945 | 0.27466 | 3.1128 | 2.5406 | -119.5404 | -119.9478 | 2.7786 | 2.4078 | 2.7924 | 2.4033
1579.2969 | 122.1725 | -2.4536 | 119.7693 | 0.011063 | -0.061686 | 0.012548 | 0.029384 | 0.0035227 | -0.0036423 | 0.0026446 | 0.0046998 | 0.016451 | 0.023345 | 0.017248 | 0.00017507 | 0.0071692 | -0.0020464 | 0.35706 | 0.71869 | 0.24719 | 0.36163 | 0.50812 | 0.37537 | 0.42572 | -0.10986 | 0.10986 | -0.18768 | -0.050354 | 0.059509 | -0.059509 | 0.082397 | 2.7008 | -119.0506 | -119.4077 | 2.9617 | 2.8793 | 2.829 | 0.17853 | 0.12817 | 2.2659 | -119.6594 | -119.8196 | 2.5131 | 2.536 | 2.3941 | 0.27008 | 0.12817 | 0.26093 | 0.11444 | 0.24719 | 0.13733 | 0.4715 | 0.29755 | 3.1723 | 2.5635 | -119.5221 | -119.957 | 2.8152 | 2.4033 | 2.8107 | 2.3438
1581.0312 | 122.2 | -2.4124 | 119.7739 | 0.0034333 | -0.062327 | 0.010839 | 0.031734 | 0.0035227 | -0.0038559 | 0.00093565 | 0.0077514 | 0.014315 | 0.020568 | 0.017248 | 0.0020979 | 0.006742 | 0.0024396 | 0.2243 | 0.58136 | 0.13275 | 0.1831 | 0.35706 | 0.17853 | 0.25635 | -0.068665 | 0.1236 | -0.21057 | -0.004578 | 0.068665 | -0.022888 | 0.11444 | 2.5452 | -119.1925 | -119.5908 | 2.7695 | 2.6688 | 2.5909 | 0.1236 | 0.045777 | 2.2018 | -119.6503 | -119.7784 | 2.4811 | 2.5269 | 2.3895 | 0.32501 | 0.18768 | 0.2243 | 0.050354 | 0.27924 | 0.20599 | 0.44861 | 0.33417 | 2.9938 | 2.536 | -119.6411 | -119.9844 | 2.5955 | 2.4078 | 2.6367 | 2.3438
1582.7812 | 122.2504 | -2.3712 | 119.7739 | 0.0034333 | -0.05955 | 0.012121 | 0.029384 | 0.0024545 | -0.0025741 | -0.00013235 | 0.001648 | 0.012606 | 0.022063 | 0.021093 | -3.8532e-05 | 0.0088782 | 0.0043622 | 0.37537 | 0.62714 | 0.22888 | 0.3891 | 0.62714 | 0.44861 | 0.5127 | 0 | 0.07782 | -0.16479 | 0.018311 | 0.16479 | 0.054932 | 0.15106 | 2.6001 | -119.1467 | -119.3848 | 2.9984 | 2.8839 | 2.8198 | 0.28381 | 0.21973 | 2.2064 | -119.696 | -119.7556 | 2.536 | 2.5223 | 2.4261 | 0.31586 | 0.21973 | 0.39825 | 0.16022 | 0.32959 | 0.18311 | 0.39825 | 0.24261 | 2.9984 | 2.449 | -119.545 | -119.9387 | 2.7603 | 2.3895 | 2.7466 | 2.3712
1584.4844 | 122.2092 | -2.3712 | 119.8013 | 0.0034333 | -0.061472 | 0.012121 | 0.028316 | 0.00095914 | -0.0036423 | -0.00034615 | 0.0046998 | 0.011965 | 0.02014 | 0.020239 | -0.00025213 | 0.0071692 | 8.9786e-05 | 0.26093 | 0.52643 | 0.15564 | 0.27008 | 0.46234 | 0.28839 | 0.37079 | -0.064087 | 0.07782 | -0.18768 | -0.018311 | 0.064087 | -0.027466 | 0.09613 | 2.5269 | -119.2749 | -119.5312 | 2.8336 | 2.742 | 2.6596 | 0.21515 | 0.13275 | 2.1835 | -119.7235 | -119.8196 | 2.4353 | 2.4673 | 2.3438 | 0.28381 | 0.16022 | 0.3067 | 0.11444 | 0.25177 | 0.16937 | 0.37079 | 0.2655 | 2.8976 | 2.449 | -119.6457 | -119.989 | 2.6413 | 2.3529 | 2.6321 | 2.3071
1586.25 | 122.2046 | -2.3987 | 119.7693 | 0.018692 | -0.059336 | 0.012335 | 0.031093 | 0.0045907 | -0.0042831 | -0.00077335 | 0.0046998 | 0.01346 | 0.0195 | 0.024084 | 0.00060247 | 0.0088782 | 0.003935 | 0.29755 | 0.55389 | 0.1831 | 0.27924 | 0.47607 | 0.29755 | 0.39368 | -0.07782 | 0.091553 | -0.19226 | -0.032043 | 0.068665 | -0.018311 | 0.10529 | 2.5818 | -119.2154 | -119.4901 | 2.8748 | 2.7924 | 2.6962 | 0.21057 | 0.11444 | 2.2064 | -119.6777 | -119.8013 | 2.4673 | 2.504 | 2.3804 | 0.29755 | 0.17395 | 0.29297 | 0.096131 | 0.26093 | 0.16022 | 0.37079 | 0.28381 | 2.9526 | 2.4902 | -119.5862 | -119.9615 | 2.6779 | 2.3666 | 2.6962 | 2.3209
1588 | 122.1268 | -2.4307 | 119.7922 | 0.0034333 | -0.0572 | 0.014471 | 0.032375 | 0.00095914 | -0.0023605 | 0.0017902 | 0.0046998 | 0.016451 | 0.022704 | 0.020452 | 0.0012433 | 0.006101 | -0.00012381 | 0.29755 | 0.6134 | 0.17395 | 0.21973 | 0.40283 | 0.2243 | 0.3067 | -0.17395 | 0.13733 | -0.20599 | -0.09613 | -0.027466 | -0.14191 | 0.022888 | 2.6047 | -119.1788 | -119.5724 | 2.8336 | 2.7374 | 2.655 | 0.13275 | 0.050354 | 2.2247 | -119.6548 | -119.8883 | 2.4033 | 2.4536 | 2.2888 | 0.22888 | 0.064087 | 0.22888 | 0.045777 | 0.17853 | 0.10986 | 0.43945 | 0.34332 | 3.0441 | 2.5681 | -119.6182 | -119.9982 | 2.6505 | 2.3346 | 2.7283 | 2.2568
1589.6875 | 122.2641 | -2.3712 | 119.7968 | 0.011063 | -0.061045 | 0.012762 | 0.028102 | 0.00010474 | -0.0021469 | 0.0020038 | 0.001648 | 0.012606 | 0.022917 | 0.021093 | -0.0017475 | 0.0073828 | -0.00461 | 0.3891 | 0.62256 | 0.23804 | 0.40283 | 0.61798 | 0.46692 | 0.51727 | 0.013733 | 0.07782 | -0.17853 | 0.027466 | 0.15106 | 0.050354 | 0.13733 | 2.6093 | -119.1742 | -119.3939 | 2.9892 | 2.8885 | 2.8381 | 0.27924 | 0.22888 | 2.1927 | -119.7189 | -119.7693 | 2.5223 | 2.5085 | 2.4216 | 0.31586 | 0.22888 | 0.37994 | 0.1648 | 0.32959 | 0.20599 | 0.38452 | 0.25635 | 2.9938 | 2.449 | -119.5587 | -119.9753 | 2.774 | 2.3987 | 2.7603 | 2.3849
1591.4375 | 122.1725 | -2.4765 | 119.7601 | 0.0034333 | -0.058695 | 0.011053 | 0.030666 | 0.0024545 | -0.0053513 | 0.00093565 | 0.001648 | 0.016237 | 0.020568 | 0.014044 | 0.00038887 | 0.0056738 | -0.00055121 | 0.3891 | 0.70038 | 0.24261 | 0.32044 | 0.49896 | 0.37994 | 0.44403 | -0.13733 | 0.13733 | -0.2243 | -0.059509 | 0.027466 | -0.07782 | 0.07782 | 2.7191 | -119.0598 | -119.4397 | 2.9755 | 2.9205 | 2.8564 | 0.20142 | 0.13733 | 2.2522 | -119.6228 | -119.8196 | 2.504 | 2.5543 | 2.3987 | 0.30212 | 0.14648 | 0.25635 | 0.07782 | 0.25177 | 0.16479 | 0.45776 | 0.36163 | 3.1769 | 2.6138 | -119.5175 | -119.9844 | 2.7969 | 2.417 | 2.8656 | 2.3392
1593.1875 | 122.2366 | -2.4353 | 119.7372 | -0.0041962 | -0.058695 | 0.012335 | 0.02917 | 0.00031834 | -0.0036423 | -0.0012006 | -0.0014038 | 0.016024 | 0.022063 | 0.022375 | -0.00067933 | 0.0075964 | 0.001585 | 0.31586 | 0.55847 | 0.16479 | 0.27008 | 0.45319 | 0.31128 | 0.39368 | -0.082397 | 0.10529 | -0.17395 | -0.032043 | 0.082397 | -0.018311 | 0.09613 | 2.6001 | -119.1788 | -119.4672 | 2.8885 | 2.829 | 2.7466 | 0.22888 | 0.14648 | 2.2614 | -119.632 | -119.7693 | 2.5177 | 2.5314 | 2.417 | 0.27008 | 0.15564 | 0.28839 | 0.10529 | 0.25635 | 0.14191 | 0.39368 | 0.27924 | 2.9938 | 2.5406 | -119.5724 | -119.9112 | 2.7054 | 2.4033 | 2.7512 | 2.3529
1594.9219 | 122.1909 | -2.4445 | 119.7922 | 0.011063 | -0.06019 | 0.012762 | 0.030025 | 0.0043771 | -0.0047103 | 0.0017902 | 0.0046998 | 0.016237 | 0.022917 | 0.013616 | -0.00089293 | 0.008451 | -0.0022602 | 0.42114 | 0.69122 | 0.26093 | 0.32959 | 0.51727 | 0.36163 | 0.43488 | -0.10071 | 0.1236 | -0.18768 | -0.054932 | 0.045776 | -0.045776 | 0.086975 | 2.7054 | -119.101 | -119.4626 | 2.9617 | 2.8793 | 2.8061 | 0.17395 | 0.10071 | 2.2568 | -119.6686 | -119.8471 | 2.4902 | 2.5314 | 2.3987 | 0.27466 | 0.14191 | 0.25635 | 0.068665 | 0.23346 | 0.13275 | 0.4303 | 0.31128 | 3.1357 | 2.5681 | -119.5312 | -119.9799 | 2.774 | 2.3895 | 2.8656 | 2.3438
1596.6875 | 122.1771 | -2.4628 | 119.7601 | 0.018692 | -0.058054 | 0.012335 | 0.032802 | 0.0039499 | -0.0044967 | -0.00013235 | 0.0046998 | 0.014529 | 0.022063 | 0.021093 | 0.0014569 | 0.0065284 | -0.0016192 | 0.38452 | 0.63629 | 0.21057 | 0.3067 | 0.49439 | 0.33417 | 0.39825 | -0.064087 | 0.10071 | -0.19226 | -0.054932 | 0.036621 | -0.059509 | 0.07782 | 2.6733 | -119.1238 | -119.4534 | 2.9572 | 2.861 | 2.7969 | 0.18768 | 0.1236 | 2.2705 | -119.6594 | -119.8151 | 2.4994 | 2.5406 | 2.4033 | 0.27008 | 0.13275 | 0.28381 | 0.096131 | 0.22888 | 0.13733 | 0.42572 | 0.29297 | 3.0991 | 2.5635 | -119.5496 | -119.9524 | 2.7695 | 2.4078 | 2.8473 | 2.3987
1598.375 | 122.2458 | -2.4078 | 119.8105 | -0.0041962 | -0.059336 | 0.011907 | 0.030452 | -0.0011771 | -0.0025741 | -0.00077335 | 0.001648 | 0.013247 | 0.022277 | 0.011907 | -0.0015337 | 0.0082374 | 0.00094419 | 0.41657 | 0.64087 | 0.27008 | 0.3891 | 0.60883 | 0.45319 | 0.5127 | 0.009155 | 0.091553 | -0.17395 | 0.013733 | 0.1236 | 0.036621 | 0.1236 | 2.6779 | -119.1696 | -119.4214 | 3.0167 | 2.9205 | 2.861 | 0.24261 | 0.1831 | 2.2339 | -119.7189 | -119.7968 | 2.5314 | 2.5314 | 2.4445 | 0.29755 | 0.21057 | 0.33874 | 0.11902 | 0.29755 | 0.18768 | 0.37079 | 0.2655 | 3.0487 | 2.4994 | -119.5404 | -119.9844 | 2.7969 | 2.4216 | 2.8244 | 2.417
1600.1094 | 122.1863 | -2.4399 | 119.8288 | 0.011063 | -0.057841 | 0.010412 | 0.031093 | 0.0024545 | -0.0059921 | 0.0011492 | 0.0046998 | 0.012392 | 0.020568 | 0.015325 | -0.00025213 | 0.006101 | 8.9786e-05 | 0.3891 | 0.69122 | 0.23804 | 0.32501 | 0.50354 | 0.3891 | 0.4303 | -0.11902 | 0.14191 | -0.21515 | -0.036621 | 0.045776 | -0.068665 | 0.073242 | 2.6779 | -119.1376 | -119.5038 | 2.9434 | 2.8702 | 2.829 | 0.19226 | 0.15106 | 2.2247 | -119.6869 | -119.8654 | 2.4857 | 2.5131 | 2.3712 | 0.28839 | 0.14648 | 0.2655 | 0.086975 | 0.26093 | 0.17853 | 0.45319 | 0.35706 | 3.1311 | 2.5818 | -119.5908 | -120.0439 | 2.7649 | 2.4033 | 2.829 | 2.3209
1601.875 | 122.1405 | -2.4445 | 119.8151 | 0.011063 | -0.058054 | 0.011907 | 0.030238 | 0.0075815 | -0.0038559 | 0.00029485 | 0.0046998 | 0.015169 | 0.023772 | 0.015112 | 0.0012433 | 0.006101 | -0.0022602 | 0.35706 | 0.6134 | 0.19684 | 0.25177 | 0.43945 | 0.27466 | 0.33417 | -0.09613 | 0.10986 | -0.18768 | -0.073242 | 0.009155 | -0.11902 | 0.059509 | 2.6413 | -119.2017 | -119.5633 | 2.8839 | 2.7786 | 2.7191 | 0.13733 | 0.07782 | 2.2568 | -119.7052 | -119.8883 | 2.4536 | 2.504 | 2.3254 | 0.24719 | 0.068664 | 0.24261 | 0.054932 | 0.19684 | 0.11444 | 0.41657 | 0.29755 | 3.0579 | 2.5543 | -119.6182 | -120.0027 | 2.6962 | 2.3712 | 2.8015 | 2.3483
1603.5625 | 122.0856 | -68.4998 | 53.7598 | 0.0034333 | -0.059977 | 0.020239 | 0.030238 | 0.0030953 | -0.0036423 | 0.017598 | 0.0046998 | 0.014101 | 0.023131 | 0.023229 | 0.0031659 | 0.0082374 | -0.0022602 | -0.65918 | -0.13733 | -0.50354 | -0.73242 | -0.48065 | -0.41199 | -0.23804 | 0.041199 | 0.11902 | -0.11902 | 0.041199 | 0.14191 | 0.027466 | 0.15106 | 67.9962 | -53.8971 | -54.4922 | 68.0191 | 68.2617 | 68.0878 | 0.2655 | 0.091553 | 68.3807 | -53.6407 | -53.7186 | 68.6417 | 68.6508 | 68.5272 | 0.27008 | 0.14649 | 0.022888 | -0.22888 | 0.26093 | 0.16022 | 0.36621 | 0.23804 | 68.3624 | 68.6188 | -54.2633 | -53.8788 | 67.7673 | 68.541 | 67.8406 | 68.541
1605.3125 | 121.9986 | -111.2823 | 10.4416 | 0.033951 | -0.056132 | 0.015325 | 0.03152 | 0.0037363 | -0.0023605 | 0.0017902 | 0.001648 | 0.015597 | 0.02014 | 0.0095574 | 0.0018841 | 0.0073828 | -0.0024738 | -0.54016 | -0.20599 | -0.59967 | -0.72327 | -0.51727 | -0.6134 | -0.48981 | -0.11444 | 0.19684 | -0.14191 | -0.022888 | 0.022888 | -0.068665 | 0.11444 | 110.6827 | -10.6476 | -11.1649 | 110.7651 | 110.7925 | 110.6689 | 0.10986 | -0.013733 | 111.1404 | -10.2448 | -10.4645 | 111.3052 | 111.3968 | 111.2137 | 0.25635 | 0.073242 | 0.082397 | -0.1236 | 0.16479 | 0.11902 | 0.39368 | 0.33875 | 111.0764 | 111.4792 | -11.0413 | -10.5835 | 110.5591 | 111.2595 | 110.7422 | 111.1679
1607.0781 | 122.1039 | -0.74158 | 120.6894 | 0.018692 | -0.060618 | 0.014257 | 0.028529 | 0.0015999 | -0.0049241 | 0.002431 | 0.0046998 | 0.012179 | 0.0195 | 0.026647 | 0.00081607 | 0.009519 | 0.00051699 | 0.33417 | 0.5127 | 0.15106 | 0.28381 | 0.50812 | 0.30212 | 0.37994 | 0.022888 | 0.073242 | -0.10071 | 0.050354 | 0.13275 | 0.018311 | 0.15106 | 0.89264 | -120.1767 | -120.4056 | 1.2497 | 1.1215 | 1.0437 | 0.22888 | 0.15106 | 0.64087 | -120.6162 | -120.639 | 0.87433 | 0.89264 | 0.75989 | 0.25177 | 0.11902 | 0.35706 | 0.13275 | 0.23346 | 0.15106 | 0.36163 | 0.17395 | 1.2543 | 0.81482 | -120.5383 | -120.7901 | 1.0254 | 0.79193 | 1.0757 | 0.76447
1608.8281 | 122.1588 | -0.79651 | 121.2936 | 0.0034333 | -0.056986 | 0.013616 | 0.030238 | -0.00096346 | -0.0027877 | 0.002431 | -0.0014038 | 0.01346 | 0.020354 | 0.023229 | 0.0038067 | 0.0090918 | -0.0016192 | 0.3479 | 0.5127 | 0.16022 | 0.28381 | 0.47607 | 0.28381 | 0.35248 | 0.022888 | 0.082397 | -0.16479 | 0.064087 | 0.15106 | 0.041199 | 0.16479 | 0.95673 | -120.7809 | -121.0098 | 1.2726 | 1.149 | 1.0803 | 0.19226 | 0.1236 | 0.63171 | -121.2112 | -121.2296 | 0.94757 | 0.9613 | 0.83771 | 0.32959 | 0.20599 | 0.31586 | 0.1236 | 0.31586 | 0.22888 | 0.35248 | 0.24719 | 1.3092 | 0.87891 | -121.1334 | -121.4584 | 1.0803 | 0.8606 | 1.1444 | 0.8194
1610.5156 | 122.0261 | -0.88806 | 121.3074 | 0.0034333 | -0.06019 | 0.011267 | 0.030666 | -0.0013907 | -0.0032151 | 0.0020038 | 0.0046998 | 0.015169 | 0.021849 | 0.016393 | -0.0047381 | 0.0065284 | 0.00094419 | 0.40283 | 0.68207 | 0.24261 | 0.33417 | 0.50812 | 0.37994 | 0.45776 | -0.13275 | 0.1236 | -0.20599 | -0.09613 | 0.022888 | -0.082397 | 0.027466 | 1.1307 | -120.6253 | -120.9732 | 1.3962 | 1.3458 | 1.268 | 0.21515 | 0.13733 | 0.68207 | -121.1838 | -121.4035 | 0.91095 | 0.91553 | 0.80567 | 0.23346 | 0.1236 | 0.2655 | 0.091552 | 0.22888 | 0.10986 | 0.43945 | 0.32959 | 1.5701 | 1.0117 | -121.0648 | -121.5134 | 1.2222 | 0.79193 | 1.2909 | 0.75531
1612.2812 | 122.1268 | -0.83313 | 121.2845 | 0.0034333 | -0.058909 | 0.012762 | 0.031947 | 0.0052315 | -0.0023605 | 0.0015764 | 0.0077514 | 0.013888 | 0.019072 | 0.019598 | 0.0012433 | 0.0063148 | 0.0011578 | 0.35706 | 0.54932 | 0.17853 | 0.27008 | 0.48065 | 0.28381 | 0.36163 | -0.022888 | 0.086975 | -0.16937 | 0 | 0.091553 | -0.004578 | 0.11444 | 1.0117 | -120.7352 | -121.0144 | 1.3138 | 1.1948 | 1.1169 | 0.1831 | 0.10528 | 0.66376 | -121.1975 | -121.2845 | 0.92468 | 0.94757 | 0.82855 | 0.28381 | 0.16479 | 0.30212 | 0.091553 | 0.26093 | 0.16937 | 0.37079 | 0.25635 | 1.3824 | 0.92011 | -121.106 | -121.4539 | 1.1032 | 0.83313 | 1.1902 | 0.81024
1614.0312 | 122.1359 | -0.87891 | 121.2799 | 0.011063 | -0.05955 | 0.013189 | 0.032375 | 0.0045907 | -0.0023605 | -0.0012006 | 0.0046998 | 0.015169 | 0.020354 | 0.016607 | 0.0012433 | 0.0073828 | -0.0014056 | 0.33875 | 0.53558 | 0.16479 | 0.28839 | 0.46234 | 0.30212 | 0.38452 | -0.036621 | 0.09613 | -0.16022 | -0.013733 | 0.068665 | -0.004578 | 0.12817 | 1.0437 | -120.7443 | -120.9915 | 1.3412 | 1.2634 | 1.181 | 0.21973 | 0.13733 | 0.71869 | -121.1838 | -121.2936 | 0.94757 | 1.0071 | 0.87433 | 0.28839 | 0.15564 | 0.29755 | 0.1236 | 0.22888 | 0.14648 | 0.37079 | 0.25635 | 1.4145 | 0.97504 | -121.1151 | -121.4401 | 1.1673 | 0.86517 | 1.2177 | 0.84228
1615.7188 | 122.113 | -0.86517 | 121.3074 | 0.011063 | -0.0572 | 0.011053 | 0.031093 | 0.0082223 | -0.00043789 | -0.0016278 | 0.0046998 | 0.014315 | 0.019072 | 0.017462 | -0.0013201 | 0.006742 | 0.0028668 | 0.43488 | 0.66834 | 0.24719 | 0.32959 | 0.49896 | 0.38452 | 0.42114 | -0.059509 | 0.12817 | -0.18768 | -0.022888 | 0.073242 | -0.041199 | 0.10071 | 1.1124 | -120.639 | -120.9778 | 1.3641 | 1.2863 | 1.2497 | 0.17395 | 0.13733 | 0.67749 | -121.1792 | -121.3303 | 0.93841 | 0.96588 | 0.82397 | 0.28839 | 0.14648 | 0.25177 | 0.082398 | 0.26092 | 0.16479 | 0.42114 | 0.31586 | 1.5335 | 0.99335 | -121.0602 | -121.4951 | 1.1948 | 0.84228 | 1.3 | 0.80566
1617.5 | 122.0947 | -0.85144 | 121.3486 | 0.0034333 | -0.058268 | 0.011694 | 0.032802 | 0.0062997 | -0.0023605 | 0.0017902 | 0.0077514 | 0.016024 | 0.021849 | 0.01618 | -0.00067933 | 0.0056738 | -0.0018328 | 0.4303 | 0.64545 | 0.21057 | 0.31586 | 0.49896 | 0.34332 | 0.39825 | -0.045776 | 0.11444 | -0.19684 | -0.050354 | 0.036621 | -0.041199 | 0.086975 | 1.062 | -120.7031 | -121.0327 | 1.3504 | 1.2497 | 1.1948 | 0.18768 | 0.13275 | 0.6546 | -121.2341 | -121.3989 | 0.88806 | 0.93841 | 0.81024 | 0.28381 | 0.15564 | 0.28839 | 0.10529 | 0.23346 | 0.14648 | 0.43488 | 0.31128 | 1.4969 | 0.96588 | -121.138 | -121.5454 | 1.1673 | 0.80109 | 1.2817 | 0.80566
1619.2031 | 122.0947 | -0.85144 | 121.3394 | 0.011063 | -0.057627 | 0.012548 | 0.033229 | 0.0088631 | -0.00043789 | 0.002431 | 0.001648 | 0.01581 | 0.020354 | 0.015539 | 0.00060247 | 0.0065284 | 8.9786e-05 | 0.42572 | 0.62256 | 0.21057 | 0.30212 | 0.49439 | 0.33875 | 0.38452 | -0.054932 | 0.11444 | -0.18768 | -0.050354 | 0.059509 | -0.068665 | 0.091553 | 1.062 | -120.7169 | -121.0373 | 1.3458 | 1.236 | 1.1902 | 0.17395 | 0.12817 | 0.66376 | -121.225 | -121.3898 | 0.91095 | 0.94299 | 0.78277 | 0.27924 | 0.11902 | 0.28381 | 0.091553 | 0.24719 | 0.13733 | 0.41199 | 0.30212 | 1.474 | 0.96588 | -121.1288 | -121.5271 | 1.1536 | 0.80109 | 1.2772 | 0.79651
1620.9375 | 122.1954 | -0.82855 | 121.2891 | 0.011063 | -0.056559 | 0.011694 | 0.03152 | 0.0011727 | -0.0042831 | 0.003499 | 0.001648 | 0.014742 | 0.02014 | 0.021734 | 0.0031659 | 0.0086646 | 0.00073059 | 0.35706 | 0.5127 | 0.15564 | 0.28839 | 0.4715 | 0.29297 | 0.36163 | -0.004578 | 0.086975 | -0.15106 | 0.050354 | 0.14191 | 0.036621 | 0.16479 | 0.98419 | -120.7764 | -121.0007 | 1.3 | 1.1902 | 1.1215 | 0.20599 | 0.13733 | 0.67749 | -121.2021 | -121.2387 | 0.97046 | 0.99335 | 0.86517 | 0.31586 | 0.18768 | 0.31586 | 0.13275 | 0.29297 | 0.20142 | 0.35706 | 0.23804 | 1.3412 | 0.91553 | -121.1334 | -121.4401 | 1.1169 | 0.87891 | 1.1856 | 0.82397
1622.625 | 122.1497 | -0.84228 | 121.2936 | 0.026321 | -0.059977 | 0.011053 | 0.029384 | 0.0099313 | -0.0023605 | 0.0013628 | 0.001648 | 0.012392 | 0.021422 | 0.022161 | -0.0030291 | 0.0069556 | -0.00012381 | 0.4715 | 0.64545 | 0.28381 | 0.40741 | 0.59967 | 0.46234 | 0.49896 | -0.022888 | 0.07782 | -0.16937 | -0.022888 | 0.09613 | 0.027466 | 0.1236 | 1.1261 | -120.6482 | -120.8862 | 1.442 | 1.3412 | 1.3046 | 0.21515 | 0.17853 | 0.67291 | -121.2158 | -121.3165 | 0.93841 | 0.96588 | 0.86975 | 0.29297 | 0.19684 | 0.31586 | 0.1236 | 0.2655 | 0.14649 | 0.36163 | 0.24719 | 1.4877 | 0.9201 | -121.0098 | -121.463 | 1.2497 | 0.8194 | 1.3138 | 0.8194
1624.3906 | 122.081 | -0.87891 | 121.3303 | 0.0034333 | -0.061259 | 0.012762 | 0.031307 | 0.0037363 | -0.0019333 | 0.002431 | 0.001648 | 0.014742 | 0.023131 | 0.012121 | 0.0031659 | 0.0075964 | 8.9786e-05 | 0.32959 | 0.58594 | 0.13275 | 0.1831 | 0.36621 | 0.21057 | 0.28381 | -0.13733 | 0.14648 | -0.19684 | -0.064087 | -0.004578 | -0.091553 | 0.068665 | 1.0117 | -120.7443 | -121.1472 | 1.2451 | 1.1627 | 1.0895 | 0.15106 | 0.07782 | 0.68207 | -121.1838 | -121.3943 | 0.87433 | 0.94757 | 0.78735 | 0.2655 | 0.10529 | 0.23346 | 0.050354 | 0.19226 | 0.13275 | 0.45319 | 0.34332 | 1.4648 | 1.0254 | -121.1975 | -121.5271 | 1.062 | 0.81482 | 1.2085 | 0.74158
1626.125 | 122.1405 | -0.82855 | 121.3028 | 0.011063 | -0.057841 | 0.01148 | 0.031307 | 0.0062997 | -0.0025741 | 0.0013628 | 0.001648 | 0.013033 | 0.020995 | 0.020666 | 0.0038067 | 0.009519 | 0.00094419 | 0.35248 | 0.59052 | 0.13275 | 0.19226 | 0.3891 | 0.2243 | 0.3067 | -0.086975 | 0.10986 | -0.19684 | -0.027466 | 0.059509 | -0.036621 | 0.10986 | 0.9613 | -120.7123 | -121.1105 | 1.2177 | 1.1353 | 1.0529 | 0.17395 | 0.091553 | 0.63171 | -121.1929 | -121.3303 | 0.88806 | 0.93841 | 0.79193 | 0.3067 | 0.16022 | 0.25635 | 0.05951 | 0.25635 | 0.16937 | 0.45776 | 0.3067 | 1.4191 | 0.93841 | -121.17 | -121.4996 | 1.0208 | 0.80109 | 1.181 | 0.74158
1627.875 | 122.1405 | -0.83771 | 121.2799 | 0.0034333 | -0.059336 | 0.012548 | 0.031734 | 0.0050179 | -0.0042831 | 0.0011492 | 0.0046998 | 0.014315 | 0.022277 | 0.020025 | 0.00060247 | 0.0086646 | 0.0011578 | 0.3891 | 0.54932 | 0.18768 | 0.28839 | 0.49896 | 0.31586 | 0.37079 | -0.013733 | 0.082397 | -0.16479 | -0.009155 | 0.086975 | 0.004578 | 0.13275 | 1.0254 | -120.7306 | -120.9915 | 1.3367 | 1.2085 | 1.1536 | 0.18311 | 0.12817 | 0.67291 | -121.1975 | -121.2891 | 0.92468 | 0.97046 | 0.84229 | 0.29755 | 0.16937 | 0.31128 | 0.10071 | 0.25177 | 0.15564 | 0.36163 | 0.24719 | 1.387 | 0.9201 | -121.0922 | -121.4447 | 1.1261 | 0.82855 | 1.2268 | 0.82398
1629.625 | 122.1405 | -0.88806 | 121.2662 | 0.011063 | -0.061259 | 0.012121 | 0.027248 | 0.0024545 | -0.0015061 | 0.00093565 | -0.0014038 | 0.013033 | 0.021849 | 0.019598 | -0.0013201 | 0.0075964 | 0.00094419 | 0.37537 | 0.59967 | 0.20142 | 0.3067 | 0.48981 | 0.33875 | 0.40741 | -0.064087 | 0.10986 | -0.18768 | -0.018311 | 0.09613 | 0.004578 | 0.11444 | 1.0895 | -120.6665 | -120.9595 | 1.3779 | 1.2955 | 1.2268 | 0.20599 | 0.13733 | 0.70038 | -121.1563 | -121.2845 | 0.98419 | 1.0025 | 0.89264 | 0.30212 | 0.19226 | 0.28839 | 0.10529 | 0.28381 | 0.16937 | 0.39825 | 0.29755 | 1.4877 | 0.99793 | -121.0648 | -121.4539 | 1.1948 | 0.86975 | 1.2634 | 0.82398
1631.3125 | 122.113 | -0.89722 | 121.2845 | 0.0034333 | -0.058054 | 0.010198 | 0.032375 | 0.0056589 | -0.0025741 | 0.00093565 | -0.0014038 | 0.015169 | 0.021209 | 0.01618 | 0.00017507 | 0.006101 | -0.00012381 | 0.43488 | 0.65918 | 0.22888 | 0.31586 | 0.49896 | 0.33875 | 0.39825 | -0.054932 | 0.12817 | -0.17395 | -0.050354 | 0.027466 | -0.068665 | 0.068665 | 1.1261 | -120.6253 | -120.9686 | 1.3962 | 1.2955 | 1.236 | 0.16937 | 0.10986 | 0.72327 | -121.1563 | -121.3348 | 0.92468 | 0.96588 | 0.82855 | 0.24261 | 0.10528 | 0.27008 | 0.086975 | 0.20142 | 0.1236 | 0.4303 | 0.30212 | 1.5564 | 1.0254 | -121.0556 | -121.4584 | 1.2131 | 0.84686 | 1.3321 | 0.84229
1633.0781 | 122.1405 | -0.88348 | 121.2753 | 0.0034333 | -0.058909 | 0.011907 | 0.028529 | 0.0026681 | -0.0042831 | 8.125e-05 | 0.001648 | 0.014956 | 0.022063 | 0.01917 | -0.0019611 | 0.0075964 | 0.003294 | 0.48981 | 0.65002 | 0.28381 | 0.40283 | 0.62714 | 0.46692 | 0.51727 | -0.022888 | 0.11444 | -0.16937 | -0.032043 | 0.082397 | 0.009155 | 0.10986 | 1.1673 | -120.6253 | -120.8725 | 1.5106 | 1.4008 | 1.3504 | 0.23346 | 0.18311 | 0.71411 | -121.1609 | -121.3074 | 0.96588 | 0.99335 | 0.89264 | 0.27924 | 0.17853 | 0.34332 | 0.11902 | 0.25177 | 0.13733 | 0.36621 | 0.28381 | 1.5335 | 0.99793 | -120.9915 | -121.4447 | 1.2863 | 0.85144 | 1.3733 | 0.8606
1634.7656 | 122.0673 | -0.92468 | 121.2708 | 0.011063 | -0.059977 | 0.013616 | 0.030452 | 0.0052315 | -0.0038559 | 0.0015764 | 0.0046998 | 0.016237 | 0.021849 | 0.016821 | -0.00046573 | 0.0058874 | -0.00076481 | 0.43945 | 0.66834 | 0.2243 | 0.3067 | 0.48981 | 0.32501 | 0.37994 | -0.082397 | 0.1236 | -0.19226 | -0.054932 | 0 | -0.091553 | 0.050354 | 1.149 | -120.6024 | -120.9641 | 1.4145 | 1.3046 | 1.2497 | 0.15564 | 0.10071 | 0.73242 | -121.1472 | -121.3257 | 0.92468 | 0.97504 | 0.83313 | 0.24261 | 0.10071 | 0.2655 | 0.082398 | 0.19226 | 0.13733 | 0.44403 | 0.31586 | 1.593 | 1.0483 | -121.0464 | -121.463 | 1.2314 | 0.86975 | 1.3641 | 0.84229
1636.5156 | 122.1405 | -0.88348 | 121.2341 | 0.018692 | -0.058909 | 0.013189 | 0.031307 | 0.0048043 | -0.0019333 | -0.00077335 | 0.0046998 | 0.013674 | 0.021209 | 0.018743 | 0.0018841 | 0.009519 | 8.9786e-05 | 0.39368 | 0.53558 | 0.20142 | 0.28381 | 0.50354 | 0.3067 | 0.3891 | -0.013733 | 0.091553 | -0.16022 | -0.013733 | 0.086975 | 0.004578 | 0.1236 | 1.0849 | -120.6985 | -120.9503 | 1.387 | 1.2726 | 1.1902 | 0.18768 | 0.10529 | 0.72327 | -121.1426 | -121.2479 | 0.97046 | 1.0071 | 0.88806 | 0.28381 | 0.16479 | 0.30212 | 0.082397 | 0.24719 | 0.14648 | 0.33417 | 0.25177 | 1.4191 | 0.97504 | -121.0327 | -121.3943 | 1.1673 | 0.86975 | 1.2772 | 0.86975
1638.2031 | 122.2183 | -0.89264 | 121.2387 | 0.011063 | -0.056772 | 0.014471 | 0.030879 | 0.0037363 | -0.00043789 | 0.00093565 | 0.0046998 | 0.013033 | 0.020568 | 0.023443 | 0.00017507 | 0.0097326 | 0.0011578 | 0.091553 | 0.25177 | -0.082397 | 0.050354 | 0.25635 | 0.064087 | 0.14648 | 0.018311 | 0.10071 | -0.16479 | 0.027466 | 0.10071 | 0.022888 | 0.13733 | 0.81024 | -120.9869 | -121.1884 | 1.149 | 1.0391 | 0.95673 | 0.22888 | 0.14648 | 0.72784 | -121.138 | -121.2112 | 0.99335 | 1.03 | 0.91553 | 0.30212 | 0.18768 | 0.33875 | 0.13275 | 0.2655 | 0.19226 | 0.33417 | 0.2655 | 1.1444 | 0.99335 | -121.3211 | -121.4035 | 0.94299 | 0.9201 | 0.98419 | 0.91095
1639.9531 | 122.1771 | -1.0483 | 121.1975 | 0.0034333 | -0.058909 | 0.012975 | 0.030025 | 0.0060861 | -0.0023605 | 0.00029485 | 0.001648 | 0.01346 | 0.023131 | 0.020025 | -0.0049517 | 0.0071692 | -0.0039692 | 0.20599 | 0.39368 | 0.013733 | 0.15564 | 0.33875 | 0.20599 | 0.25635 | -0.050354 | 0.11902 | -0.17853 | -0.054932 | 0.045776 | -0.050354 | 0.082397 | 1.062 | -120.8038 | -121.0419 | 1.387 | 1.3046 | 1.2543 | 0.24262 | 0.19226 | 0.86975 | -121.0785 | -121.2524 | 1.0941 | 1.1307 | 0.99792 | 0.26092 | 0.12817 | 0.32501 | 0.14191 | 0.2243 | 0.1236 | 0.37994 | 0.29755 | 1.442 | 1.1673 | -121.1838 | -121.376 | 1.2039 | 0.99335 | 1.2543 | 0.99792
1641.7031 | 122.168 | -0.93384 | 121.3211 | 0.026321 | -0.058695 | 0.013189 | 0.03152 | 0.0045907 | -0.0027877 | 0.0037128 | 0.0046998 | 0.014956 | 0.021209 | 0.014898 | 0.0018841 | 0.0056738 | 0.00094419 | 0.036621 | 0.32501 | -0.10986 | -0.064087 | 0.09613 | -0.064087 | 0.036621 | -0.13733 | 0.15564 | -0.19226 | -0.07782 | 0 | -0.10986 | 0.064087 | 0.82397 | -120.9961 | -121.3852 | 1.03 | 0.97046 | 0.86975 | 0.14648 | 0.045776 | 0.74158 | -121.1655 | -121.3989 | 0.93384 | 0.99792 | 0.82397 | 0.25635 | 0.082398 | 0.20599 | 0.045776 | 0.19226 | 0.11444 | 0.43488 | 0.3479 | 1.2589 | 1.0895 | -121.431 | -121.5134 | 0.86975 | 0.85602 | 0.97046 | 0.79651
1643.3906 | 122.1863 | -1.236 | 121.0373 | 0.0034333 | -0.059763 | 0.014257 | 0.032588 | 0.0033089 | -0.0025741 | 0.0028582 | 0.001648 | 0.015383 | 0.023558 | 0.017462 | 0.0020979 | 0.0069556 | 0.0024396 | 0.041199 | 0.33875 | -0.11444 | -0.064087 | 0.10071 | -0.045776 | 0.041199 | -0.13275 | 0.1236 | -0.19226 | -0.07782 | 0 | -0.10071 | 0.054932 | 1.1215 | -120.6985 | -121.1014 | 1.3367 | 1.2772 | 1.1902 | 0.15564 | 0.068665 | 1.0437 | -120.9137 | -121.1151 | 1.236 | 1.2909 | 1.1353 | 0.24719 | 0.091553 | 0.21515 | 0.050354 | 0.19226 | 0.11444 | 0.45319 | 0.31586 | 1.5747 | 1.3596 | -121.1517 | -121.2296 | 1.1719 | 1.1581 | 1.2772 | 1.1032
1645.1406 | 122.1909 | -0.94299 | 121.3623 | 0.011063 | -0.058054 | 0.012335 | 0.03152 | 0.0028817 | -0.0042831 | -0.00034615 | 0.0046998 | 0.013247 | 0.022917 | 0.014684 | -3.8532e-05 | 0.006742 | -0.00012381 | 0.050354 | 0.34332 | -0.10529 | -0.059509 | 0.091553 | -0.045776 | 0.018311 | -0.15564 | 0.14648 | -0.19684 | -0.086975 | -0.018311 | -0.12817 | 0.054932 | 0.83771 | -121.019 | -121.4218 | 1.0345 | 0.9613 | 0.89722 | 0.1236 | 0.05951 | 0.74615 | -121.2158 | -121.4493 | 0.92468 | 0.99792 | 0.81482 | 0.25177 | 0.068664 | 0.19684 | 0.045777 | 0.17853 | 0.10986 | 0.44861 | 0.34332 | 1.2863 | 1.0895 | -121.4676 | -121.5591 | 0.88348 | 0.85602 | 0.99335 | 0.78735
1646.8906 | 122.1634 | -1.2222 | 121.0876 | 0.011063 | -0.056132 | 0.0099848 | 0.032161 | 0.0073679 | -0.0038559 | -0.002696 | 0.0046998 | 0.016451 | 0.022277 | 0.009771 | 0.00017507 | 0.0071692 | -0.0037554 | 0.068665 | 0.36621 | -0.082397 | -0.050354 | 0.09613 | -0.032043 | 0.022888 | -0.16937 | 0.1236 | -0.21057 | -0.082397 | -0.032043 | -0.13733 | 0.045776 | 1.1398 | -120.7214 | -121.138 | 1.3184 | 1.2451 | 1.1902 | 0.10528 | 0.050354 | 1.0117 | -120.9641 | -121.17 | 1.1902 | 1.268 | 1.0849 | 0.25635 | 0.073242 | 0.17853 | 0.032043 | 0.17853 | 0.12817 | 0.44861 | 0.33417 | 1.5884 | 1.3458 | -121.17 | -121.2982 | 1.1719 | 1.1398 | 1.2909 | 1.0529
1648.5781 | 122.2046 | -0.95215 | 121.3898 | 0.011063 | -0.061899 | 0.012335 | 0.029598 | 0.0011727 | -0.0015061 | 0.0020038 | 0.001648 | 0.01282 | 0.020354 | 0.015325 | 0.0027387 | 0.0080236 | -0.001192 | 0.036621 | 0.35248 | -0.09613 | -0.054932 | 0.1236 | -0.032043 | 0.045776 | -0.14648 | 0.1236 | -0.19226 | -0.068665 | 0.004578 | -0.10986 | 0.054932 | 0.85602 | -121.0373 | -121.4447 | 1.0757 | 0.99792 | 0.9201 | 0.14191 | 0.064087 | 0.75989 | -121.2662 | -121.4584 | 0.95673 | 1.0071 | 0.84228 | 0.24719 | 0.082398 | 0.21973 | 0.041198 | 0.19684 | 0.1236 | 0.44861 | 0.31586 | 1.3046 | 1.0757 | -121.4859 | -121.582 | 0.89722 | 0.88348 | 0.98877 | 0.80566
1650.3125 | 122.3373 | -0.97046 | 121.2433 | 0.0034333 | -0.056986 | 0.014471 | 0.030666 | 0.0075815 | -0.0036423 | 0.0028582 | 0.0046998 | 0.013674 | 0.020995 | 0.020666 | 0.0018841 | 0.0080236 | 0.0028668 | 0.14191 | 0.29755 | -0.054932 | 0.041199 | 0.24719 | 0.050354 | 0.16022 | 0.036621 | 0.082397 | -0.1831 | 0.045776 | 0.12817 | 0.032043 | 0.15106 | 0.91553 | -120.9457 | -121.2021 | 1.2177 | 1.1307 | 1.0208 | 0.21515 | 0.10529 | 0.78735 | -121.1609 | -121.1975 | 1.0986 | 1.1215 | 1.0025 | 0.33417 | 0.21515 | 0.30212 | 0.096131 | 0.31128 | 0.22888 | 0.35248 | 0.2655 | 1.268 | 1.0529 | -121.2982 | -121.4264 | 1.0117 | 1.0162 | 1.1124 | 1.0071
1652 | 122.3373 | -1.2863 | 121.0007 | 0.011063 | -0.058695 | 0.012121 | 0.028316 | -0.00010886 | -0.0023605 | -0.00034615 | -0.0014038 | 0.014742 | 0.021636 | 0.018316 | -0.00089293 | 0.0097326 | 0.00051699 | 0.16479 | 0.38452 | 0.032043 | 0.1831 | 0.41657 | 0.23804 | 0.30212 | 0.036621 | 0.07782 | -0.16479 | 0.027466 | 0.16022 | 0.054932 | 0.14191 | 1.3184 | -120.6161 | -120.8176 | 1.7029 | 1.5884 | 1.5244 | 0.27008 | 0.20599 | 1.1215 | -120.9229 | -120.9732 | 1.4465 | 1.4282 | 1.3412 | 0.3067 | 0.21973 | 0.38452 | 0.15106 | 0.32501 | 0.19226 | 0.35248 | 0.24261 | 1.6708 | 1.3641 | -120.9686 | -121.1655 | 1.4694 | 1.3138 | 1.4511 | 1.3229
1653.75 | 122.2229 | -2.1927 | 120.1263 | 0.0034333 | -0.058054 | 0.0097712 | 0.030879 | 0.0026681 | -0.0025741 | -0.00034615 | 0.0077514 | 0.014742 | 0.019072 | 0.014684 | -3.8532e-05 | 0.0075964 | -0.00076481 | 0.14191 | 0.48523 | 0.068665 | 0.091553 | 0.2655 | 0.14648 | 0.20142 | -0.14648 | 0.14191 | -0.20599 | -0.091553 | 0.009155 | -0.07782 | 0.054932 | 2.2614 | -119.6411 | -120.0348 | 2.4582 | 2.3941 | 2.3392 | 0.13275 | 0.077819 | 1.9867 | -119.9844 | -120.2179 | 2.2018 | 2.2476 | 2.1149 | 0.26093 | 0.12817 | 0.19684 | 0.022888 | 0.21515 | 0.11444 | 0.41656 | 0.3479 | 2.6779 | 2.3346 | -120.0577 | -120.3323 | 2.2842 | 2.1011 | 2.3346 | 2.0462
1655.5 | 122.3099 | -1.1948 | 121.0419 | 0.0034333 | -0.059977 | 0.011053 | 0.031307 | 0.00010474 | -0.0027877 | 0.00072205 | 0.001648 | 0.013888 | 0.020995 | 0.022375 | -0.00025213 | 0.00781 | -0.001192 | 0.068665 | 0.36621 | -0.022888 | 0.09613 | 0.27924 | 0.13733 | 0.18768 | -0.059509 | 0.10071 | -0.16479 | -0.004578 | 0.11444 | 0.027466 | 0.14191 | 1.1719 | -120.6757 | -120.9457 | 1.474 | 1.3824 | 1.3321 | 0.21057 | 0.16022 | 1.03 | -120.9412 | -121.0464 | 1.3092 | 1.3367 | 1.2222 | 0.3067 | 0.19226 | 0.30212 | 0.11902 | 0.27924 | 0.16022 | 0.3891 | 0.2655 | 1.561 | 1.2955 | -121.0648 | -121.2067 | 1.2909 | 1.1902 | 1.2634 | 1.1353
1657.2031 | 122.2641 | -1.4603 | 120.8679 | 0.011063 | -0.057841 | 0.010626 | 0.031307 | 0.0060861 | -0.00043789 | -0.00098695 | 0.010803 | 0.014956 | 0.021849 | 0.01917 | 0.0020979 | 0.0069556 | -0.00097841 | 0.13733 | 0.42572 | 0.013733 | 0.10986 | 0.28839 | 0.13275 | 0.1831 | -0.045776 | 0.10986 | -0.19226 | -0.022888 | 0.068665 | -0.045776 | 0.09613 | 1.474 | -120.4422 | -120.7581 | 1.7487 | 1.6434 | 1.593 | 0.16937 | 0.11902 | 1.268 | -120.7581 | -120.8908 | 1.5289 | 1.5564 | 1.4145 | 0.28839 | 0.14648 | 0.27466 | 0.09613 | 0.26093 | 0.16937 | 0.41199 | 0.30212 | 1.886 | 1.5701 | -120.8542 | -121.0602 | 1.5701 | 1.4374 | 1.5976 | 1.4145
1658.9688 | 122.2412 | -2.0142 | 120.2591 | -0.0041962 | -0.05955 | 0.012548 | 0.029598 | 0.00074554 | -0.0040695 | 0.0015764 | 0.0046998 | 0.014956 | 0.019713 | 0.018743 | -0.0028155 | 0.0075964 | -0.00033761 | 0.17395 | 0.47607 | 0.068665 | 0.11444 | 0.28839 | 0.16937 | 0.2243 | -0.086975 | 0.11444 | -0.18768 | -0.054932 | 0.059509 | -0.050354 | 0.086975 | 2.0828 | -119.783 | -120.1447 | 2.3026 | 2.2385 | 2.1835 | 0.15564 | 0.10071 | 1.8265 | -120.1447 | -120.314 | 2.0737 | 2.1011 | 1.9638 | 0.27466 | 0.13733 | 0.21973 | 0.045776 | 0.24719 | 0.13275 | 0.40741 | 0.30212 | 2.4902 | 2.1286 | -120.1904 | -120.4468 | 2.1286 | 1.9592 | 2.1881 | 1.9272
1660.6562 | 122.3328 | -2.0462 | 120.2042 | 0.011063 | -0.059977 | 0.011053 | 0.030238 | 0.0039499 | -0.0027877 | -0.00034615 | 0.001648 | 0.01282 | 0.024199 | 0.01853 | 0.0029523 | 0.00781 | 0.0011578 | 0.068665 | 0.29297 | -0.050354 | 0.068665 | 0.26093 | 0.086975 | 0.14191 | 0.018311 | 0.09613 | -0.16022 | 0.059509 | 0.13275 | 0.022888 | 0.16479 | 1.9958 | -119.9112 | -120.1355 | 2.3071 | 2.1881 | 2.1332 | 0.19226 | 0.13733 | 1.886 | -120.108 | -120.1447 | 2.179 | 2.211 | 2.0691 | 0.32501 | 0.1831 | 0.31128 | 0.11902 | 0.29297 | 0.21973 | 0.34332 | 0.25635 | 2.3392 | 2.1423 | -120.2545 | -120.3644 | 2.1149 | 2.1057 | 2.1149 | 2.0645
1662.4219 | 122.3145 | -3.6392 | 118.5974 | 0.011063 | -0.05955 | 0.012762 | 0.02682 | 0.0054453 | -0.0023605 | 0.00029485 | 0.0046998 | 0.01282 | 0.023345 | 0.017034 | -0.0030291 | 0.0082374 | -0.0016192 | 0.17395 | 0.41199 | 0.054932 | 0.19684 | 0.3891 | 0.24719 | 0.29297 | -0.004578 | 0.09613 | -0.15564 | -0.004578 | 0.12817 | 0.027466 | 0.12817 | 3.6942 | -118.1854 | -118.4006 | 4.0283 | 3.9322 | 3.8864 | 0.23804 | 0.19226 | 3.4836 | -118.5013 | -118.602 | 3.7674 | 3.7674 | 3.6667 | 0.28381 | 0.18311 | 0.33417 | 0.14191 | 0.28381 | 0.15106 | 0.35706 | 0.25177 | 4.0512 | 3.7354 | -118.5425 | -118.7531 | 3.8361 | 3.6346 | 3.8132 | 3.6346
1664.1719 | 122.2778 | -1.355 | 121.0327 | 0.011063 | -0.055491 | 0.012121 | 0.030238 | 0.0037363 | -0.0042831 | 0.0011492 | -0.0014038 | 0.014742 | 0.021422 | 0.021093 | -0.0015337 | 0.0056738 | -0.00055121 | 0.16937 | 0.48523 | 0.036621 | 0.1236 | 0.28839 | 0.16022 | 0.21057 | -0.068665 | 0.1236 | -0.18768 | -0.041199 | 0.050354 | -0.050354 | 0.10071 | 1.3916 | -120.5475 | -120.9091 | 1.6434 | 1.5656 | 1.5152 | 0.17395 | 0.1236 | 1.1673 | -120.9091 | -121.0739 | 1.4053 | 1.4557 | 1.3046 | 0.28839 | 0.13733 | 0.25177 | 0.086975 | 0.23804 | 0.14648 | 0.44861 | 0.31128 | 1.8402 | 1.4786 | -120.9961 | -121.2204 | 1.4786 | 1.3138 | 1.5244 | 1.2863
1665.9219 | 122.3557 | -0.86517 | 121.3852 | 0.018692 | -0.059336 | 0.015539 | 0.030452 | 0.0026681 | -0.0021469 | -0.00077335 | 0.001648 | 0.01346 | 0.022277 | 0.022375 | 0.0038067 | 0.010587 | -0.00033761 | 0.064087 | 0.3067 | -0.022888 | 0.082397 | 0.27924 | 0.068665 | 0.15564 | 0.032043 | 0.091553 | -0.14648 | 0.041199 | 0.13733 | 0.022888 | 0.17395 | 0.84228 | -121.0785 | -121.3028 | 1.1444 | 1.0208 | 0.93384 | 0.17853 | 0.091553 | 0.71869 | -121.2936 | -121.344 | 1.0025 | 1.0391 | 0.88806 | 0.32043 | 0.16937 | 0.30212 | 0.10528 | 0.28381 | 0.18768 | 0.32959 | 0.23804 | 1.1719 | 0.95673 | -121.4081 | -121.5317 | 0.94757 | 0.90637 | 0.92926 | 0.89722
1667.6094 | 122.3282 | -0.94299 | 121.3669 | 0.0034333 | -0.058054 | 0.012975 | 0.030238 | 0.0045907 | -0.0015061 | -0.0016278 | 0.0046998 | 0.015169 | 0.020568 | 0.022588 | 0.00017507 | 0.0088782 | 0.002226 | 0.045776 | 0.37537 | -0.082397 | -0.022888 | 0.16479 | 0 | 0.082397 | -0.082397 | 0.10986 | -0.20142 | -0.027466 | 0.068665 | -0.041199 | 0.11902 | 0.8606 | -120.9915 | -121.3898 | 1.1078 | 1.0254 | 0.94299 | 0.16479 | 0.082397 | 0.74158 | -121.257 | -121.3943 | 1.0117 | 1.062 | 0.90179 | 0.32044 | 0.16022 | 0.24719 | 0.059509 | 0.27008 | 0.17395 | 0.45776 | 0.31128 | 1.3184 | 1.0529 | -121.4493 | -121.5683 | 0.9201 | 0.91553 | 0.98877 | 0.8606
1669.3594 | 122.2733 | -0.98877 | 121.4035 | 0.0034333 | -0.056772 | 0.011267 | 0.028529 | 0.0026681 | -0.0021469 | 0.00093565 | 0.0046998 | 0.017092 | 0.021636 | 0.016393 | -0.0038837 | 0.0069556 | -0.0018328 | 0.16937 | 0.52185 | 0.050354 | 0.1236 | 0.29755 | 0.17853 | 0.23346 | -0.14191 | 0.13733 | -0.19226 | -0.091553 | 0.018311 | -0.064087 | 0.059509 | 1.0391 | -120.8817 | -121.2799 | 1.2863 | 1.2222 | 1.1673 | 0.1831 | 0.12817 | 0.79651 | -121.2662 | -121.4951 | 1.0071 | 1.0483 | 0.92468 | 0.25177 | 0.12817 | 0.24719 | 0.073242 | 0.21057 | 0.10071 | 0.4715 | 0.32959 | 1.5106 | 1.1261 | -121.3531 | -121.5958 | 1.1124 | 0.89722 | 1.1581 | 0.84686
1671.0938 | 122.3831 | -0.86517 | 121.431 | 0.0034333 | -0.058481 | 0.012762 | 0.031093 | 0.0058725 | -0.0034287 | -0.00077335 | 0.001648 | 0.013033 | 0.021209 | 0.009771 | 0.0035931 | 0.0082374 | 0.001585 | 0.082397 | 0.32959 | -0.032043 | 0.091553 | 0.27466 | 0.09613 | 0.17853 | 0.004578 | 0.086975 | -0.15106 | 0.054932 | 0.1236 | 0.022888 | 0.14648 | 0.83313 | -121.1014 | -121.3394 | 1.1398 | 1.0437 | 0.9613 | 0.21057 | 0.12817 | 0.71411 | -121.344 | -121.376 | 0.98877 | 1.0117 | 0.88806 | 0.29755 | 0.17395 | 0.3067 | 0.1236 | 0.27466 | 0.20599 | 0.36163 | 0.23804 | 1.1948 | 0.95215 | -121.463 | -121.582 | 0.95673 | 0.9201 | 0.94757 | 0.86975
1672.7812 | 122.374 | -0.87433 | 121.4264 | 0.0034333 | -0.058054 | 0.01383 | 0.02917 | 0.0043771 | -0.0010789 | 0.0013628 | 0.0046998 | 0.013674 | 0.023131 | 0.023016 | -0.00089293 | 0.0086646 | 0.0026532 | 0.086975 | 0.3067 | -0.064087 | 0.10986 | 0.31128 | 0.11902 | 0.1831 | 0.022888 | 0.10071 | -0.16022 | 0.032043 | 0.12817 | 0.032043 | 0.14191 | 0.81024 | -121.1197 | -121.3165 | 1.1856 | 1.0574 | 0.99335 | 0.24719 | 0.18311 | 0.71411 | -121.3257 | -121.3943 | 1.0025 | 1.0162 | 0.90637 | 0.30212 | 0.19226 | 0.37537 | 0.17395 | 0.28839 | 0.19226 | 0.37079 | 0.26093 | 1.181 | 0.97504 | -121.4905 | -121.5866 | 0.98419 | 0.90637 | 0.9613 | 0.89722
1674.5469 | 122.4014 | -0.86517 | 121.4539 | 0.0034333 | -0.060831 | 0.01148 | 0.028529 | 0.0056589 | -0.0023605 | 0.002431 | 0.0046998 | 0.013888 | 0.020781 | 0.017889 | -0.0028155 | 0.00781 | -0.00012381 | 0.19226 | 0.41199 | 0.068665 | 0.20142 | 0.43945 | 0.28381 | 0.3479 | 0.059509 | 0.082397 | -0.16022 | 0.018311 | 0.14191 | 0.054932 | 0.14648 | 0.93384 | -121.0419 | -121.2524 | 1.3046 | 1.2131 | 1.149 | 0.27924 | 0.21515 | 0.70496 | -121.3715 | -121.4355 | 1.0071 | 1.0117 | 0.9201 | 0.3067 | 0.21515 | 0.37079 | 0.13275 | 0.30212 | 0.17853 | 0.34332 | 0.24261 | 1.2772 | 0.94757 | -121.3852 | -121.6141 | 1.0666 | 0.88348 | 1.0574 | 0.92468
1676.2969 | 122.2687 | -0.92926 | 121.5134 | 0.011063 | -0.058695 | 0.012121 | 0.030238 | 0.0030953 | -0.0044967 | 0.00029485 | 0.0046998 | 0.013247 | 0.019286 | 0.017675 | -0.0045245 | 0.0069556 | 0.00030339 | 0.14191 | 0.50354 | 0.068665 | 0.11444 | 0.31128 | 0.20142 | 0.27008 | -0.14191 | 0.13733 | -0.19684 | -0.1236 | 0.004578 | -0.07782 | 0.036621 | 0.99792 | -121.0098 | -121.3989 | 1.2405 | 1.1993 | 1.1307 | 0.20142 | 0.13275 | 0.73242 | -121.376 | -121.637 | 0.93384 | 0.96588 | 0.85144 | 0.23346 | 0.11902 | 0.24261 | 0.045776 | 0.20142 | 0.073242 | 0.43488 | 0.33417 | 1.4328 | 1.0666 | -121.4447 | -121.7102 | 1.0437 | 0.80566 | 1.0712 | 0.78735
1678.0625 | 122.319 | -0.91095 | 121.5134 | 0.011063 | -0.058054 | 0.010198 | 0.030666 | 0.0035227 | -0.0017197 | 0.0020038 | 0.0077514 | 0.014956 | 0.023772 | 0.01148 | -0.0021747 | 0.006742 | 0.00051699 | 0.17395 | 0.50354 | 0.068665 | 0.13733 | 0.30212 | 0.17853 | 0.25177 | -0.1236 | 0.13275 | -0.1831 | -0.064087 | 0.032043 | -0.059509 | 0.082397 | 0.97962 | -121.0098 | -121.376 | 1.2131 | 1.1627 | 1.0895 | 0.1831 | 0.10986 | 0.72785 | -121.3806 | -121.5775 | 0.94299 | 0.99335 | 0.85144 | 0.2655 | 0.1236 | 0.23346 | 0.068664 | 0.21515 | 0.11902 | 0.43488 | 0.31586 | 1.4145 | 1.0437 | -121.4447 | -121.6965 | 1.0483 | 0.84686 | 1.0849 | 0.78735
1679.75 | 122.406 | -0.89264 | 121.4493 | 0.0034333 | -0.06019 | 0.010839 | 0.030452 | 0.0035227 | -0.0042831 | 0.0017902 | 0.0046998 | 0.014101 | 0.020354 | 0.022375 | -0.0017475 | 0.0088782 | 0.00030339 | 0.16022 | 0.40741 | 0.045776 | 0.17853 | 0.39825 | 0.22888 | 0.31586 | 0.036621 | 0.082397 | -0.17853 | 0.045776 | 0.15564 | 0.059509 | 0.16022 | 0.93841 | -121.0419 | -121.2708 | 1.2909 | 1.2085 | 1.1215 | 0.27008 | 0.18311 | 0.71411 | -121.3669 | -121.4035 | 1.0483 | 1.0529 | 0.95215 | 0.33874 | 0.23804 | 0.35248 | 0.13275 | 0.33417 | 0.2243 | 0.36163 | 0.26092 | 1.3 | 0.97504 | -121.4035 | -121.6278 | 1.0712 | 0.93841 | 1.0529 | 0.92926
1681.5 | 122.3007 | -0.91095 | 121.4905 | 0.018692 | -0.059763 | 0.011694 | 0.031947 | 0.0065133 | -0.0010789 | 0.0022174 | 0.0046998 | 0.016024 | 0.022277 | 0.023016 | 0.0016705 | 0.00781 | 0.00094419 | 0.045776 | 0.38452 | -0.064087 | -0.009155 | 0.16022 | 0 | 0.09613 | -0.13275 | 0.13275 | -0.21515 | -0.068665 | 0.004578 | -0.11444 | 0.073242 | 0.84686 | -121.106 | -121.4996 | 1.0712 | 1.0071 | 0.91095 | 0.16022 | 0.064087 | 0.6958 | -121.3577 | -121.5591 | 0.91553 | 0.98419 | 0.79651 | 0.28839 | 0.10071 | 0.2243 | 0.054932 | 0.21973 | 0.14648 | 0.44861 | 0.3479 | 1.2955 | 1.0437 | -121.5546 | -121.7056 | 0.9018 | 0.84229 | 0.95673 | 0.7782
1683.2031 | 122.3145 | -0.89264 | 121.5088 | 0.011063 | -0.056772 | 0.014257 | 0.031307 | 0.0033089 | -1.0686e-05 | -0.00077335 | 0.001648 | 0.016237 | 0.02014 | 0.018743 | 0.00038887 | 0.0063148 | -0.00055121 | 0.16022 | 0.43488 | 0.013733 | 0.11902 | 0.30212 | 0.14191 | 0.19684 | -0.068665 | 0.13275 | -0.18768 | -0.050354 | 0.027466 | -0.07782 | 0.07782 | 0.90637 | -121.0739 | -121.3898 | 1.1948 | 1.0895 | 1.0345 | 0.18311 | 0.12817 | 0.70496 | -121.376 | -121.5591 | 0.9201 | 0.97046 | 0.81482 | 0.2655 | 0.10986 | 0.28839 | 0.10529 | 0.21515 | 0.13733 | 0.42114 | 0.32043 | 1.3275 | 1.0254 | -121.4951 | -121.6965 | 1.0117 | 0.84228 | 1.0529 | 0.82397
1684.9531 | 122.3969 | -0.83313 | 121.4905 | 0.011063 | -0.061259 | 0.012548 | 0.02917 | 0.0026681 | -1.0686e-05 | -0.00013235 | 0.010803 | 0.014742 | 0.020354 | 0.01917 | 0.00081607 | 0.011869 | 0.0047894 | 0.086975 | 0.3067 | -0.013733 | 0.086975 | 0.27924 | 0.091553 | 0.16022 | 0.013733 | 0.086975 | -0.15564 | 0.036621 | 0.13733 | 0.022888 | 0.16022 | 0.8194 | -121.1838 | -121.4035 | 1.1124 | 0.99335 | 0.92468 | 0.17395 | 0.10529 | 0.67749 | -121.4035 | -121.4539 | 0.97046 | 0.99335 | 0.85602 | 0.31586 | 0.17853 | 0.29297 | 0.10071 | 0.29297 | 0.19226 | 0.32043 | 0.24261 | 1.1398 | 0.92011 | -121.5042 | -121.6461 | 0.92011 | 0.86975 | 0.92011 | 0.84686
1686.7031 | 122.4243 | -0.82855 | 121.4951 | -0.0041962 | -0.057627 | 0.013403 | 0.030452 | -0.00053626 | -0.0025741 | 0.0011492 | 0.001648 | 0.011751 | 0.019713 | 0.015753 | 0.0014569 | 0.011228 | 0.00094419 | 0.07782 | 0.33875 | -0.045776 | 0.091553 | 0.27924 | 0.09613 | 0.18768 | -0.004578 | 0.09613 | -0.15106 | 0.045776 | 0.1236 | 0.027466 | 0.17395 | 0.78278 | -121.1563 | -121.4035 | 1.1078 | 1.0162 | 0.92468 | 0.23346 | 0.14191 | 0.67749 | -121.3989 | -121.4493 | 0.95215 | 1.0025 | 0.85602 | 0.32501 | 0.17853 | 0.32501 | 0.13733 | 0.27466 | 0.19684 | 0.38452 | 0.24719 | 1.1673 | 0.92468 | -121.5408 | -121.6461 | 0.9201 | 0.87433 | 0.90637 | 0.82397
1688.4531 | 122.3511 | -0.87891 | 121.5271 | 0.011063 | -0.060831 | 0.013403 | 0.031307 | 0.0062997 | -0.0030015 | 0.0026446 | 0.0077514 | 0.015169 | 0.0195 | 0.012762 | -0.0021747 | 0.0063148 | -0.0050372 | 0.19684 | 0.52643 | 0.07782 | 0.14191 | 0.32501 | 0.19226 | 0.24261 | -0.086975 | 0.14191 | -0.20142 | -0.036621 | 0.068665 | -0.059509 | 0.086975 | 0.95673 | -121.0007 | -121.3852 | 1.2039 | 1.1215 | 1.0712 | 0.16479 | 0.11444 | 0.67749 | -121.3852 | -121.5637 | 0.94757 | 0.96588 | 0.8194 | 0.28839 | 0.14191 | 0.24719 | 0.064087 | 0.27008 | 0.1648 | 0.44861 | 0.34332 | 1.4053 | 1.0208 | -121.4493 | -121.7285 | 1.0208 | 0.84228 | 1.0757 | 0.79193
1690.2031 | 122.4335 | -0.85602 | 121.4951 | 0.011063 | -0.060404 | 0.01383 | 0.031734 | 0.0045907 | -0.0010789 | 0.002431 | 0.0046998 | 0.013888 | 0.019072 | 0.020025 | 0.0033795 | 0.008451 | 8.9786e-05 | 0.09613 | 0.33417 | -0.022888 | 0.10986 | 0.29755 | 0.10529 | 0.17853 | 0.009155 | 0.09613 | -0.16937 | 0.050354 | 0.13275 | 0.018311 | 0.16022 | 0.83313 | -121.1609 | -121.3852 | 1.1536 | 1.0345 | 0.9613 | 0.20142 | 0.12817 | 0.68664 | -121.3989 | -121.4447 | 0.98877 | 1.0162 | 0.87433 | 0.32959 | 0.18768 | 0.32043 | 0.13275 | 0.30212 | 0.21973 | 0.35706 | 0.2655 | 1.1902 | 0.95215 | -121.5179 | -121.6644 | 0.96588 | 0.90637 | 0.95215 | 0.86517
1691.9531 | 122.3373 | -2.5452 | 119.8425 | 0.018692 | -0.059977 | 0.01148 | 0.030879 | 0.0060861 | -0.0023605 | -0.0016278 | 0.0046998 | 0.01581 | 0.020995 | 0.017675 | -0.0013201 | 0.0071692 | -0.00033761 | 0.1831 | 0.43945 | 0.041199 | 0.14648 | 0.32044 | 0.17395 | 0.21973 | -0.045776 | 0.11902 | -0.1831 | -0.022888 | 0.050354 | -0.059509 | 0.091553 | 2.5864 | -119.4031 | -119.696 | 2.8656 | 2.7649 | 2.7191 | 0.17853 | 0.13275 | 2.3621 | -119.7235 | -119.8654 | 2.5955 | 2.6367 | 2.4857 | 0.27466 | 0.1236 | 0.27924 | 0.10529 | 0.23346 | 0.16022 | 0.39825 | 0.30212 | 2.9846 | 2.6642 | -119.8013 | -120.0256 | 2.6917 | 2.5223 | 2.7283 | 2.4994
1693.6406 | 122.3007 | -0.94299 | 121.4355 | 0.011063 | -0.056986 | 0.012335 | 0.030666 | 0.0050179 | -0.0034287 | 0.0047808 | 0.0046998 | 0.015597 | 0.022277 | 0.012975 | -0.0013201 | 0.006101 | 0.0013714 | 0.15106 | 0.4715 | 0.050354 | 0.09613 | 0.30212 | 0.10986 | 0.1831 | -0.09613 | 0.13275 | -0.18768 | -0.073242 | 0.027466 | -0.091553 | 0.064087 | 0.99335 | -120.9641 | -121.3394 | 1.2451 | 1.1261 | 1.0529 | 0.13275 | 0.059509 | 0.75531 | -121.3028 | -121.5088 | 0.97046 | 1.0071 | 0.85144 | 0.25177 | 0.09613 | 0.25177 | 0.045776 | 0.21515 | 0.11444 | 0.42114 | 0.32043 | 1.4145 | 1.0757 | -121.3852 | -121.6232 | 1.0391 | 0.86975 | 1.0941 | 0.84686
1695.3906 | 122.3145 | -1.1215 | 121.2524 | 0.0034333 | -0.058268 | 0.010839 | 0.029384 | -0.0018179 | -0.0053513 | 0.0032854 | 0.0046998 | 0.013674 | 0.020995 | 0.01917 | -0.0040973 | 0.0065284 | 0.0028668 | 0.2243 | 0.52185 | 0.1236 | 0.19226 | 0.37994 | 0.23346 | 0.28839 | -0.1236 | 0.13733 | -0.18768 | -0.091553 | 0.022888 | -0.068665 | 0.050354 | 1.2451 | -120.7306 | -121.0602 | 1.5015 | 1.4099 | 1.355 | 0.1648 | 0.10986 | 0.93384 | -121.1151 | -121.344 | 1.1444 | 1.1719 | 1.0529 | 0.23804 | 0.11902 | 0.25635 | 0.068665 | 0.21057 | 0.09613 | 0.39825 | 0.32501 | 1.6434 | 1.2589 | -121.1288 | -121.4401 | 1.3138 | 1.03 | 1.3458 | 0.99792
1697.1406 | 122.2824 | -0.91095 | 121.5317 | 0.0034333 | -0.056559 | 0.012335 | 0.032375 | 0.0039499 | -0.0015061 | 0.0013628 | 0.0046998 | 0.015597 | 0.021422 | 0.018102 | 0.0023115 | 0.0075964 | -0.00097841 | 0.09613 | 0.44403 | 0.013733 | 0.036621 | 0.21515 | 0.068665 | 0.10529 | -0.16937 | 0.13275 | -0.21973 | -0.09613 | -0.009155 | -0.13733 | 0.041199 | 0.92468 | -121.0876 | -121.4951 | 1.1261 | 1.0162 | 0.97962 | 0.091553 | 0.054932 | 0.69122 | -121.3989 | -121.6278 | 0.9018 | 0.95215 | 0.77362 | 0.26093 | 0.082398 | 0.20142 | 0.022888 | 0.21057 | 0.1236 | 0.4303 | 0.35248 | 1.355 | 1.0437 | -121.5179 | -121.7514 | 0.94757 | 0.81482 | 1.0071 | 0.74158
1698.8281 | 122.4243 | -0.88348 | 121.5088 | 0.026321 | -0.059336 | 0.014471 | 0.02917 | 0.0013863 | -0.0027877 | 0.0015764 | 0.0046998 | 0.01346 | 0.020995 | 0.025793 | -0.0040973 | 0.0071692 | -0.0018328 | 0.2243 | 0.45776 | 0.10986 | 0.25177 | 0.4715 | 0.3067 | 0.35248 | 0.013733 | 0.091553 | -0.15564 | 0.013733 | 0.15106 | 0.050354 | 0.14191 | 0.99335 | -121.051 | -121.257 | 1.355 | 1.236 | 1.1902 | 0.24262 | 0.19684 | 0.72784 | -121.4172 | -121.4951 | 1.0345 | 1.0254 | 0.93384 | 0.29755 | 0.20599 | 0.36163 | 0.14191 | 0.3067 | 0.16937 | 0.3479 | 0.24719 | 1.3412 | 0.97504 | -121.3989 | -121.6644 | 1.1353 | 0.89722 | 1.1078 | 0.89722
1700.5781 | 122.2595 | -16.0584 | 106.1691 | 0.011063 | -0.060831 | 0.0097712 | 0.02917 | 0.0041635 | -0.0059921 | 0.0011492 | 0.0046998 | 0.013674 | 0.020781 | 0.01917 | -0.0023883 | 0.0058874 | -0.00033761 | 0.11902 | 0.56763 | 0.13733 | 0.11444 | 0.32959 | 0.21515 | 0.27466 | -0.1236 | 0.14648 | -0.19226 | -0.091553 | 0.013733 | -0.091553 | 0.050354 | 16.1957 | -105.6015 | -106.0547 | 16.3879 | 16.333 | 16.2735 | 0.13733 | 0.07782 | 15.8661 | -106.0226 | -106.2607 | 16.0721 | 16.1087 | 15.9668 | 0.24261 | 0.10071 | 0.19226 | -0.022888 | 0.20599 | 0.10071 | 0.4303 | 0.33874 | 16.626 | 16.2048 | -106.0318 | -106.3614 | 16.1728 | 15.9668 | 16.1774 | 15.9348
1702.3281 | 122.3419 | -2.2476 | 120.1721 | 0.0034333 | -0.057627 | 0.010839 | 0.029384 | 0.0026681 | -0.0049241 | 0.0028582 | 0.001648 | 0.015383 | 0.019072 | 0.017889 | -0.00067933 | 0.0075964 | -0.00055121 | 0.21515 | 0.52643 | 0.09613 | 0.16022 | 0.33417 | 0.23804 | 0.28839 | -0.11902 | 0.15106 | -0.21057 | -0.050354 | 0.041199 | -0.036621 | 0.09613 | 2.3438 | -119.6457 | -120.0119 | 2.5818 | 2.536 | 2.4857 | 0.19226 | 0.14191 | 2.037 | -120.0211 | -120.2225 | 2.2888 | 2.3438 | 2.211 | 0.3067 | 0.17395 | 0.23804 | 0.064087 | 0.25177 | 0.16022 | 0.4303 | 0.36163 | 2.774 | 2.3987 | -120.076 | -120.3827 | 2.4078 | 2.1973 | 2.4628 | 2.1286
1704.0781 | 122.406 | -2.3621 | 119.8929 | 0.011063 | -0.058909 | 0.011694 | 0.029598 | 0.0018137 | -0.0030015 | -0.00098695 | 0.0077514 | 0.013033 | 0.020995 | 0.020452 | -0.00067933 | 0.00781 | 0.0020124 | 0.11444 | 0.40741 | 0.018311 | 0.10529 | 0.3067 | 0.15106 | 0.25635 | -0.068665 | 0.086975 | -0.17395 | -0.032043 | 0.068665 | -0.009155 | 0.10986 | 2.3804 | -119.4855 | -119.7876 | 2.6688 | 2.6184 | 2.5131 | 0.23804 | 0.13275 | 2.1881 | -119.8059 | -119.9249 | 2.4307 | 2.4719 | 2.3529 | 0.28381 | 0.16479 | 0.28839 | 0.086975 | 0.24261 | 0.14191 | 0.3891 | 0.26092 | 2.7695 | 2.449 | -119.8746 | -120.0668 | 2.4673 | 2.33 | 2.4765 | 2.2934
1705.7656 | 122.4518 | -2.0691 | 120.3552 | 0.011063 | -0.058268 | 0.012548 | 0.030879 | 0.0024545 | -0.0012925 | -0.00013235 | 0.001648 | 0.013033 | 0.019927 | 0.01917 | 0.0033795 | 0.0071692 | -0.0037554 | 0.11444 | 0.35248 | -0.018311 | 0.09613 | 0.27924 | 0.11902 | 0.20142 | 0 | 0.10529 | -0.1831 | 0.050354 | 0.11902 | 0.032043 | 0.16937 | 2.0508 | -120.0027 | -120.2591 | 2.3483 | 2.2705 | 2.1881 | 0.21973 | 0.13733 | 1.886 | -120.2499 | -120.3049 | 2.1881 | 2.2385 | 2.1011 | 0.35248 | 0.21515 | 0.29755 | 0.11444 | 0.30212 | 0.23346 | 0.37079 | 0.28839 | 2.4216 | 2.1744 | -120.3735 | -120.5383 | 2.1652 | 2.1194 | 2.1835 | 2.0691
1707.5469 | 122.3419 | -1.9547 | 120.5383 | 0.0034333 | -0.057627 | 0.011267 | 0.032161 | 0.0018137 | -0.0047103 | 0.00093565 | 0.0077514 | 0.016237 | 0.022277 | 0.012548 | 0.00038887 | 0.0073828 | -0.00055121 | 0.11444 | 0.4715 | 0.022888 | 0.050354 | 0.19226 | 0.041199 | 0.13275 | -0.17853 | 0.15564 | -0.21057 | -0.082397 | -0.036621 | -0.12817 | 0.054932 | 1.9775 | -120.0668 | -120.488 | 2.1469 | 2.0874 | 1.9958 | 0.10986 | 0.018311 | 1.7441 | -120.3827 | -120.6207 | 1.918 | 2.0096 | 1.8265 | 0.2655 | 0.082397 | 0.16937 | 0.027466 | 0.17395 | 0.12817 | 0.44861 | 0.36621 | 2.4261 | 2.1103 | -120.5154 | -120.7489 | 2.005 | 1.8723 | 2.0691 | 1.7761
1709.25 | 122.4243 | -1.5747 | 120.7672 | 0.011063 | -0.059763 | 0.015539 | 0.032161 | 0.0065133 | -0.0023605 | 0.00029485 | 0.0077514 | 0.013674 | 0.019713 | 0.017248 | 0.0018841 | 0.0099462 | 0.0011578 | 0.10529 | 0.37537 | 0.009155 | 0.15564 | 0.36163 | 0.17395 | 0.2243 | 0.013733 | 0.091553 | -0.17395 | 0.045776 | 0.14191 | 0.018311 | 0.16937 | 1.5839 | -120.3918 | -120.6116 | 1.9363 | 1.799 | 1.7487 | 0.21515 | 0.16479 | 1.4008 | -120.6757 | -120.7214 | 1.7166 | 1.7441 | 1.593 | 0.34332 | 0.19226 | 0.35248 | 0.14649 | 0.31586 | 0.21973 | 0.36621 | 0.2655 | 1.9501 | 1.6663 | -120.7581 | -120.9412 | 1.7303 | 1.6205 | 1.68 | 1.5884
1711 | 122.3969 | -1.7075 | 120.4742 | 0.011063 | -0.058054 | 0.010626 | 0.030452 | 0.0011727 | -0.0051377 | 0.0017902 | 0.0077514 | 0.017092 | 0.020995 | 0.013403 | -0.0019611 | 0.0058874 | 0.0035078 | 0.24719 | 0.58594 | 0.15106 | 0.17395 | 0.31128 | 0.2243 | 0.32959 | -0.15106 | 0.13275 | -0.21057 | -0.09613 | 0.013733 | -0.082397 | 0.054932 | 1.8585 | -119.8883 | -120.3003 | 2.0187 | 2.037 | 1.9318 | 0.17853 | 0.073242 | 1.4969 | -120.3415 | -120.5704 | 1.7212 | 1.7624 | 1.6251 | 0.2655 | 0.12817 | 0.16022 | 0.022888 | 0.2243 | 0.11444 | 0.43488 | 0.34332 | 2.2934 | 1.8402 | -120.3232 | -120.6848 | 1.8814 | 1.6113 | 1.9546 | 1.5564
1712.6875 | 122.4655 | -1.9775 | 120.5658 | 0.0034333 | -0.061045 | 0.015966 | 0.030879 | 0.0030953 | -0.0021469 | 0.0013628 | 0.001648 | 0.015169 | 0.021849 | 0.016393 | 0.0033795 | 0.010374 | 0.0013714 | 0.20599 | 0.37537 | 0.050354 | 0.16022 | 0.32501 | 0.18768 | 0.24719 | 0.013733 | 0.086975 | -0.16479 | 0.054932 | 0.14191 | 0.032043 | 0.16479 | 2.0279 | -120.1904 | -120.4056 | 2.3026 | 2.2247 | 2.1652 | 0.19684 | 0.13733 | 1.8127 | -120.4788 | -120.5109 | 2.1194 | 2.1423 | 2.0096 | 0.32959 | 0.19684 | 0.27466 | 0.10986 | 0.3067 | 0.21973 | 0.32501 | 0.25177 | 2.3529 | 2.0645 | -120.5154 | -120.7306 | 2.1378 | 2.0325 | 2.1835 | 1.9913
1714.4375 | 122.3373 | -2.298 | 120.1859 | 0.011063 | -0.061472 | 0.011907 | 0.030238 | 0.0039499 | -0.0051377 | 0.00050845 | 0.0077514 | 0.014101 | 0.021422 | 0.01148 | -0.0028155 | 0.004392 | 0.0026532 | 0.24719 | 0.5722 | 0.16022 | 0.22888 | 0.39825 | 0.27008 | 0.33875 | -0.13733 | 0.14191 | -0.20142 | -0.10986 | -0.013733 | -0.091553 | 0.032043 | 2.4582 | -119.6136 | -119.957 | 2.6962 | 2.6367 | 2.5681 | 0.17853 | 0.10986 | 2.0966 | -120.0439 | -120.2957 | 2.2842 | 2.33 | 2.2064 | 0.23346 | 0.10986 | 0.23804 | 0.068665 | 0.18768 | 0.091553 | 0.41199 | 0.34332 | 2.8702 | 2.4399 | -120.0256 | -120.3873 | 2.5269 | 2.1881 | 2.5452 | 2.1606
1716.125 | 122.5113 | -1.9089 | 120.5429 | 0.011063 | -0.060831 | 0.012975 | 0.028529 | 0.0024545 | -0.0044967 | 0.00072205 | 0.0046998 | 0.012606 | 0.019927 | 0.022802 | -0.0015337 | 0.0082374 | -0.0048236 | 0.2243 | 0.50812 | 0.15106 | 0.27466 | 0.46234 | 0.31128 | 0.36621 | 0.004578 | 0.09613 | -0.17853 | 0.009155 | 0.14191 | 0.054932 | 0.16479 | 2.0599 | -120.0348 | -120.2682 | 2.3712 | 2.2751 | 2.2202 | 0.21515 | 0.16022 | 1.7303 | -120.4468 | -120.5338 | 2.0508 | 2.0737 | 1.9638 | 0.34332 | 0.23346 | 0.31128 | 0.1236 | 0.32044 | 0.18768 | 0.35706 | 0.27466 | 2.417 | 2.005 | -120.3918 | -120.7214 | 2.1835 | 1.918 | 2.1332 | 1.9135
1717.875 | 122.3236 | -3.7537 | 118.6478 | 0.011063 | -0.057413 | 0.014684 | 0.029811 | 0.0041635 | -0.0034287 | -0.00013235 | 0.001648 | 0.015597 | 0.021849 | 0.016821 | 0.0010297 | 0.0071692 | 0.0035078 | 0.16479 | 0.46692 | 0.059509 | 0.086975 | 0.26093 | 0.10071 | 0.17853 | -0.11444 | 0.13275 | -0.18768 | -0.10071 | -0.022888 | -0.1236 | 0.041199 | 3.8132 | -118.1808 | -118.5608 | 4.0146 | 3.9322 | 3.8544 | 0.11902 | 0.041199 | 3.566 | -118.515 | -118.7485 | 3.7308 | 3.7949 | 3.6301 | 0.22888 | 0.064087 | 0.20142 | 0.027466 | 0.16479 | 0.086975 | 0.40741 | 0.32043 | 4.2206 | 3.8864 | -118.5883 | -118.8354 | 3.8406 | 3.653 | 3.9185 | 3.6392
1719.6094 | 122.3465 | -3.6026 | 118.7805 | 0.011063 | -0.057841 | 0.012762 | 0.029811 | 0.0035227 | -0.0038559 | 0.00072205 | 0.0077514 | 0.013888 | 0.023772 | 0.012548 | -0.0015337 | 0.0063148 | -0.00012381 | 0.25177 | 0.54016 | 0.13275 | 0.1831 | 0.39368 | 0.23804 | 0.30212 | -0.064087 | 0.11902 | -0.19226 | -0.032043 | 0.059509 | -0.036621 | 0.10071 | 3.7354 | -118.2404 | -118.5974 | 3.9963 | 3.9047 | 3.8406 | 0.16937 | 0.10529 | 3.4103 | -118.6615 | -118.8126 | 3.6621 | 3.7033 | 3.566 | 0.29297 | 0.15564 | 0.26093 | 0.050354 | 0.25177 | 0.16022 | 0.40741 | 0.31128 | 4.1428 | 3.7216 | -118.6478 | -118.9728 | 3.7857 | 3.5706 | 3.8544 | 3.5385
1721.3594 | 118.2999 | -26.1795 | 91.8503 | 0.018692 | -0.06019 | 0.012335 | 0.030879 | 0.0033089 | -0.0032151 | 0.0032854 | 0.001648 | 0.014315 | 0.020354 | 0.021093 | 0.0040205 | 0.008451 | 8.9786e-05 | 0.064087 | 0.32959 | -0.041199 | 0.068665 | 0.24261 | 0.091553 | 0.15106 | 0 | 0.11444 | -0.15106 | 0.073242 | 0.1236 | 0.027466 | 0.18768 | 26.1383 | -91.5207 | -91.7816 | 26.4221 | 26.3306 | 26.2711 | 0.19226 | 0.13275 | 26.0284 | -91.7358 | -91.777 | 26.3031 | 26.3672 | 26.207 | 0.33874 | 0.17853 | 0.28381 | 0.10986 | 0.27466 | 0.2243 | 0.37079 | 0.2655 | 26.5091 | 26.2939 | -91.8915 | -92.0013 | 26.2482 | 26.2527 | 26.2436 | 26.1795
1723.1094 | 117.659 | -26.7838 | 90.8203 | 0.0034333 | -0.059122 | 0.013189 | 0.031734 | 0.0039499 | -0.0053513 | 8.125e-05 | 0.0046998 | 0.014956 | 0.021209 | 0.01853 | 0.0020979 | 0.0088782 | 0.00073059 | 0.045776 | 0.38452 | -0.041199 | 0.013733 | 0.15564 | 0.004578 | 0.10071 | -0.13733 | 0.15106 | -0.19226 | -0.068665 | -0.022888 | -0.10986 | 0.054932 | 26.7426 | -90.4358 | -90.8066 | 26.9394 | 26.8845 | 26.7883 | 0.14191 | 0.045777 | 26.5915 | -90.6693 | -90.889 | 26.7609 | 26.8387 | 26.6739 | 0.24719 | 0.082398 | 0.19684 | 0.054932 | 0.16937 | 0.1236 | 0.42572 | 0.34332 | 27.1683 | 26.9348 | -90.8615 | -91.0126 | 26.7975 | 26.7151 | 26.8295 | 26.6464
1724.8438 | 117.3157 | -29.6585 | 87.3825 | 0.0034333 | -0.061259 | 0.011053 | 0.028102 | 0.0018137 | -0.0030015 | -0.0031232 | 0.001648 | 0.012179 | 0.019927 | 0.021734 | -0.0011065 | 0.0075964 | 0.0026532 | 0.10986 | 0.36621 | 0.032043 | 0.15106 | 0.35248 | 0.18768 | 0.23346 | -0.041199 | 0.10529 | -0.16479 | 0.013733 | 0.1236 | 0.036621 | 0.16479 | 29.6906 | -87.0163 | -87.2314 | 30.011 | 29.892 | 29.8462 | 0.20142 | 0.15564 | 29.4937 | -87.2772 | -87.3688 | 29.7821 | 29.8233 | 29.6951 | 0.32959 | 0.20142 | 0.32044 | 0.11902 | 0.28839 | 0.17853 | 0.33417 | 0.27008 | 30.0247 | 29.7638 | -87.3505 | -87.5473 | 29.8096 | 29.6722 | 29.7684 | 29.6173
1726.5156 | 115.535 | -77.0828 | 38.3881 | 0.011063 | -0.058695 | 0.010626 | 0.030879 | 0.0037363 | -0.0034287 | 0.0020038 | 0.0046998 | 0.01581 | 0.020354 | 0.013616 | -0.0017475 | 0.006101 | -0.00033761 | -0.14648 | 0.054932 | -0.32959 | -0.17395 | 0.036621 | -0.082397 | -0.036621 | -0.009155 | 0.14648 | -0.15564 | -0.009155 | 0.086975 | 0 | 0.13275 | 76.7532 | -38.3331 | -38.562 | 77.1194 | 77.0462 | 77.0004 | 0.29297 | 0.24719 | 76.9272 | -38.2416 | -38.3972 | 77.1698 | 77.2156 | 77.0828 | 0.28839 | 0.15564 | 0.36621 | 0.15564 | 0.24261 | 0.14649 | 0.38452 | 0.30212 | 77.1378 | 77.2293 | -38.7177 | -38.5437 | 76.9089 | 77.0737 | 76.9363 | 77.0737
1728.2812 | 119.6594 | -119.1696 | 0.27466 | 0.0034333 | -0.059977 | 0.012975 | 0.031947 | -0.00010886 | -0.0027877 | 0.0015764 | 0.0077514 | 0.015169 | 0.02014 | 0.021948 | -0.00089293 | 0.0086646 | 0.00051699 | -0.17853 | 0.12817 | -0.23804 | -0.16937 | 0.022888 | -0.13275 | -0.050354 | -0.036621 | 0.16937 | -0.11444 | 0.022888 | 0.14191 | 0.027466 | 0.17395 | 118.9316 | -0.14648 | -0.44403 | 119.1925 | 119.1193 | 119.0369 | 0.18768 | 0.10529 | 119.0552 | -0.10529 | -0.25177 | 119.3115 | 119.3436 | 119.1971 | 0.28839 | 0.14191 | 0.26093 | 0.068664 | 0.25635 | 0.13733 | 0.36621 | 0.28381 | 119.2978 | 119.339 | -0.5127 | -0.3891 | 119.0002 | 119.1925 | 118.9911 | 119.133
1729.9531 | 120.0485 | -119.6045 | 0.21515 | 0.0034333 | -0.061259 | 0.011907 | 0.030666 | 0.0043771 | -0.0015061 | 0.0043536 | 0.0046998 | 0.01346 | 0.020781 | 0.020879 | 0.0016705 | 0.01016 | -0.001192 | -0.19226 | 0.073242 | -0.29297 | -0.17395 | 0.009155 | -0.17395 | -0.091553 | 0.041199 | 0.15106 | -0.10986 | 0.10071 | 0.16022 | 0.068665 | 0.21515 | 119.3115 | -0.14191 | -0.3891 | 119.6136 | 119.5129 | 119.4305 | 0.20142 | 0.11902 | 119.4946 | -0.064087 | -0.11444 | 119.7647 | 119.8196 | 119.6732 | 0.32501 | 0.17853 | 0.30212 | 0.11902 | 0.27008 | 0.21057 | 0.36621 | 0.26093 | 119.6777 | 119.7556 | -0.50812 | -0.32501 | 119.4305 | 119.7052 | 119.4122 | 119.6457
1731.7031 | 120.1172 | -119.8059 | 0.25635 | 0.0034333 | -0.058054 | 0.011053 | 0.028957 | 0.0033089 | -0.0025741 | -0.00013235 | -0.0014038 | 0.016451 | 0.017363 | 0.01618 | -0.0013201 | 0.0063148 | -0.00033761 | -0.082397 | 0.21973 | -0.19226 | -0.1236 | 0.045776 | -0.059509 | -0.009155 | -0.086975 | 0.1831 | -0.13275 | 0 | 0.07782 | -0.018311 | 0.14648 | 119.6136 | -0.036621 | -0.37994 | 119.8517 | 119.7968 | 119.7464 | 0.18311 | 0.13275 | 119.6732 | -0.073243 | -0.25635 | 119.8837 | 119.9524 | 119.7876 | 0.27924 | 0.11444 | 0.23804 | 0.068665 | 0.21057 | 0.13275 | 0.41199 | 0.31586 | 120.0256 | 119.989 | -0.44861 | -0.3891 | 119.6823 | 119.8059 | 119.7235 | 119.7189
1733.3906 | 120.2545 | -119.8883 | 0.21973 | 0.011063 | -0.059336 | 0.013403 | 0.02917 | 0.00031834 | -0.0036423 | 0.00072205 | -0.0014038 | 0.011324 | 0.019713 | 0.020452 | -0.00025213 | 0.0075964 | 0.0024396 | -0.17395 | 0.13733 | -0.24261 | -0.16937 | 0.027466 | -0.12817 | -0.036621 | -0.022888 | 0.15106 | -0.11444 | 0.041199 | 0.14191 | 0.045776 | 0.16479 | 119.6457 | -0.082398 | -0.3891 | 119.9158 | 119.8517 | 119.7601 | 0.20599 | 0.11444 | 119.7739 | -0.068665 | -0.17853 | 120.0302 | 120.0531 | 119.9341 | 0.27924 | 0.16022 | 0.27008 | 0.073242 | 0.25635 | 0.15564 | 0.37994 | 0.2655 | 120.0256 | 120.0394 | -0.46234 | -0.33417 | 119.7189 | 119.9295 | 119.7144 | 119.8654
1735.1406 | 120.2271 | -119.9982 | 0.22888 | 0.011063 | -0.058695 | 0.012975 | 0.032375 | 0.0030953 | -0.0047103 | 0.0013628 | 0.001648 | 0.014956 | 0.018859 | 0.0074212 | 0.0010297 | 0.009519 | 8.9786e-05 | -0.1236 | 0.19226 | -0.24261 | -0.19226 | -0.022888 | -0.18768 | -0.1236 | -0.054932 | 0.19684 | -0.13733 | -0.004578 | 0.045776 | -0.073242 | 0.10529 | 119.7556 | -0.036621 | -0.42114 | 119.9753 | 119.8746 | 119.8105 | 0.11902 | 0.054932 | 119.8608 | -0.032044 | -0.23346 | 120.0439 | 120.1035 | 119.9249 | 0.24262 | 0.064087 | 0.21973 | 0.050354 | 0.18311 | 0.13275 | 0.43488 | 0.33417 | 120.1904 | 120.195 | -0.4715 | -0.36621 | 119.8059 | 119.9936 | 119.8746 | 119.9432
1736.8125 | 120.3873 | -120.0485 | 0.21515 | 0.0034333 | -0.059122 | 0.013189 | 0.030238 | 0.0026681 | -0.0042831 | -0.0016278 | 0.0046998 | 0.012606 | 0.020995 | 0.018957 | -0.0023883 | 0.0073828 | 0.0028668 | -0.054932 | 0.17395 | -0.15564 | -0.041199 | 0.17395 | 0.004578 | 0.045776 | 0.054932 | 0.15564 | -0.11444 | 0.050354 | 0.15106 | 0.064087 | 0.17395 | 119.8929 | -0.041199 | -0.25635 | 120.2225 | 120.0943 | 120.0531 | 0.20142 | 0.16022 | 119.9341 | -0.059509 | -0.16479 | 120.1996 | 120.2225 | 120.1126 | 0.28839 | 0.17853 | 0.32959 | 0.11444 | 0.2655 | 0.16479 | 0.32959 | 0.27008 | 120.2225 | 120.2042 | -0.37079 | -0.32959 | 120.0073 | 120.0989 | 119.9936 | 120.1035
1738.5625 | 120.4102 | -120.1035 | 0.24261 | 0.0034333 | -0.058481 | 0.012762 | 0.028957 | 0.0054453 | -0.00086509 | 0.0032854 | 0.001648 | 0.012179 | 0.019286 | 0.021307 | -0.00025213 | 0.0058874 | -0.00097841 | -0.16937 | 0.086975 | -0.24719 | -0.16022 | 0.022888 | -0.13275 | -0.054932 | 0.004578 | 0.14648 | -0.12817 | 0.059509 | 0.12817 | 0.036621 | 0.15564 | 119.8563 | -0.15564 | -0.40283 | 120.1263 | 120.0485 | 119.9707 | 0.19226 | 0.11444 | 119.9753 | -0.096131 | -0.18311 | 120.2316 | 120.2591 | 120.1401 | 0.28381 | 0.1648 | 0.27008 | 0.086975 | 0.25635 | 0.18768 | 0.33417 | 0.27466 | 120.1904 | 120.2499 | -0.48981 | -0.37079 | 119.9432 | 120.163 | 119.9341 | 120.108
1740.3281 | 120.4422 | -120.1813 | 0.23804 | 0.0034333 | -0.060831 | 0.011694 | 0.030025 | 0.0043771 | -0.00086509 | 8.125e-05 | 0.001648 | 0.014315 | 0.020781 | 0.018102 | -0.0034563 | 0.006101 | 0.0013714 | -0.050354 | 0.1831 | -0.16937 | -0.059509 | 0.15564 | 0.018311 | 0.054932 | 0.018311 | 0.16022 | -0.1236 | 0.045776 | 0.14648 | 0.041199 | 0.16937 | 120.0119 | -0.054932 | -0.29755 | 120.3369 | 120.2362 | 120.1996 | 0.22431 | 0.18768 | 120.0577 | -0.07782 | -0.19226 | 120.3278 | 120.3506 | 120.2225 | 0.29297 | 0.16479 | 0.32501 | 0.10986 | 0.27008 | 0.16937 | 0.35248 | 0.28381 | 120.3644 | 120.3415 | -0.40741 | -0.36163 | 120.1218 | 120.2271 | 120.1309 | 120.1996
1742.0156 | 120.5383 | -120.195 | 0.22888 | 0.011063 | -0.05955 | 0.01148 | 0.029811 | 0.0028817 | -0.0036423 | -0.00034615 | 0.0046998 | 0.012392 | 0.019927 | 0.022375 | 0.00060247 | 0.0082374 | -0.00055121 | -0.064087 | 0.17395 | -0.17395 | -0.027466 | 0.1831 | 0.022888 | 0.07782 | 0.07782 | 0.14648 | -0.10986 | 0.10071 | 0.20599 | 0.10529 | 0.20142 | 120.0211 | -0.054932 | -0.25635 | 120.3781 | 120.2728 | 120.2179 | 0.25177 | 0.19684 | 120.0851 | -0.082398 | -0.12817 | 120.401 | 120.3964 | 120.3003 | 0.31128 | 0.21515 | 0.35706 | 0.14648 | 0.31586 | 0.21057 | 0.3479 | 0.25635 | 120.369 | 120.3415 | -0.40283 | -0.33875 | 120.1675 | 120.2957 | 120.1309 | 120.2728
1743.7656 | 120.5795 | -120.2087 | 0.21515 | 0.011063 | -0.060404 | 0.012975 | 0.030025 | 0.0054453 | -0.0015061 | -0.00098695 | 0.0046998 | 0.01282 | 0.0195 | 0.015753 | -0.0021747 | 0.0082374 | -0.0026874 | -0.045776 | 0.16479 | -0.17853 | -0.013733 | 0.17395 | 0.018311 | 0.073242 | 0.068665 | 0.15106 | -0.091553 | 0.10071 | 0.17853 | 0.09613 | 0.19684 | 120.0302 | -0.050354 | -0.22888 | 120.3827 | 120.282 | 120.2271 | 0.25177 | 0.19684 | 120.1172 | -0.064087 | -0.11444 | 120.3873 | 120.4056 | 120.3049 | 0.28839 | 0.18768 | 0.35248 | 0.16479 | 0.27008 | 0.19226 | 0.34332 | 0.24261 | 120.3735 | 120.3598 | -0.39368 | -0.3067 | 120.195 | 120.3094 | 120.163 | 120.2774
1745.5312 | 120.6162 | -120.2454 | 0.22888 | 0.011063 | -0.056772 | 0.013616 | 0.031307 | 0.0037363 | -0.0021469 | 0.00029485 | -0.0014038 | 0.01346 | 0.018645 | 0.017462 | 0.0025251 | 0.0071692 | -0.00097841 | -0.16479 | 0.068665 | -0.27008 | -0.14648 | 0.054932 | -0.14191 | -0.054932 | 0.068665 | 0.14191 | -0.10529 | 0.09613 | 0.17395 | 0.064087 | 0.18768 | 119.9753 | -0.16022 | -0.37537 | 120.3003 | 120.1904 | 120.1035 | 0.21515 | 0.12817 | 120.1401 | -0.086975 | -0.13275 | 120.4193 | 120.433 | 120.3094 | 0.29297 | 0.16937 | 0.32501 | 0.1236 | 0.27924 | 0.20142 | 0.33875 | 0.24719 | 120.314 | 120.3873 | -0.49896 | -0.33417 | 120.0989 | 120.3415 | 120.0806 | 120.314
1747.2031 | 120.5887 | -120.3278 | 0.24261 | -0.011826 | -0.058481 | 0.010412 | 0.030666 | 0.0030953 | -0.0012925 | 0.0026446 | 0.0046998 | 0.015597 | 0.02014 | 0.014257 | 0.00081607 | 0.0073828 | -0.0037554 | -0.07782 | 0.21973 | -0.1831 | -0.1236 | 0.064087 | -0.082397 | -0.022888 | -0.009155 | 0.17853 | -0.13733 | 0.032043 | 0.10986 | 0.004578 | 0.16022 | 120.1447 | -0.022888 | -0.36621 | 120.3918 | 120.3049 | 120.2454 | 0.16022 | 0.10071 | 120.1904 | -0.064087 | -0.21057 | 120.4376 | 120.488 | 120.3323 | 0.29755 | 0.14191 | 0.24719 | 0.059509 | 0.24719 | 0.16937 | 0.40283 | 0.31586 | 120.5475 | 120.5063 | -0.42572 | -0.37994 | 120.2042 | 120.3598 | 120.2499 | 120.3186
1748.9531 | 120.7031 | -120.3003 | 0.22888 | 0.011063 | -0.06019 | 0.011053 | 0.027889 | 0.0043771 | -0.0042831 | 0.00072205 | -0.0014038 | 0.013033 | 0.019286 | 0.019384 | 0.00017507 | 0.0082374 | 0.0026532 | -0.059509 | 0.15564 | -0.15106 | -0.059509 | 0.1831 | 0.018311 | 0.07782 | 0.09613 | 0.15564 | -0.11444 | 0.091553 | 0.21515 | 0.10071 | 0.19684 | 120.1492 | -0.073242 | -0.28839 | 120.4834 | 120.3781 | 120.3186 | 0.22888 | 0.16937 | 120.1859 | -0.073242 | -0.13733 | 120.5154 | 120.4971 | 120.401 | 0.31128 | 0.21515 | 0.33417 | 0.091553 | 0.32959 | 0.20599 | 0.3067 | 0.27008 | 120.4559 | 120.4559 | -0.37994 | -0.34332 | 120.2408 | 120.3918 | 120.2408 | 120.3964
1750.6875 | 120.6802 | -120.3415 | 0.25635 | 0.0034333 | -0.061472 | 0.012762 | 0.030879 | 0.0050179 | -0.0012925 | -0.0014142 | 0.0046998 | 0.015383 | 0.020781 | 0.021307 | 0.00081607 | 0.0063148 | -0.001192 | -0.16937 | 0.1236 | -0.24261 | -0.16022 | 0.022888 | -0.13275 | -0.045776 | -0.018311 | 0.13733 | -0.13275 | 0.027466 | 0.12817 | 0.013733 | 0.15564 | 120.0989 | -0.13275 | -0.41657 | 120.3644 | 120.2957 | 120.2087 | 0.19684 | 0.10986 | 120.2087 | -0.11902 | -0.22888 | 120.4697 | 120.4971 | 120.3552 | 0.28839 | 0.14648 | 0.2655 | 0.082398 | 0.26093 | 0.16022 | 0.36621 | 0.27008 | 120.4651 | 120.4788 | -0.49896 | -0.3891 | 120.1813 | 120.369 | 120.1721 | 120.3232
1752.4375 | 120.6482 | -120.401 | 0.27466 | 0.011063 | -0.057627 | 0.010412 | 0.028957 | -0.0011771 | -0.0032151 | 0.00029485 | 0.0077514 | 0.012179 | 0.020781 | 0.016821 | -0.0047381 | 0.006742 | -0.0014056 | -0.027466 | 0.20142 | -0.16479 | -0.045776 | 0.12817 | -0.013733 | 0.054932 | -0.009155 | 0.17853 | -0.13733 | -0.009155 | 0.091553 | -0.022888 | 0.11902 | 120.2362 | -0.073242 | -0.32043 | 120.5292 | 120.4559 | 120.3873 | 0.21973 | 0.15106 | 120.2637 | -0.09613 | -0.28381 | 120.4926 | 120.52 | 120.3781 | 0.25635 | 0.11444 | 0.29297 | 0.11902 | 0.22888 | 0.12817 | 0.36621 | 0.31586 | 120.6024 | 120.5795 | -0.43945 | -0.41199 | 120.3552 | 120.3918 | 120.3735 | 120.3918
1754.1875 | 120.7809 | -120.3552 | 0.2655 | 0.011063 | -0.058695 | 0.012335 | 0.031307 | 0.0039499 | -0.0047103 | 0.0011492 | 0.001648 | 0.017519 | 0.019927 | 0.021734 | 0.0038067 | 0.0088782 | 0.002226 | -0.17395 | 0.082397 | -0.28839 | -0.17853 | 0.013733 | -0.17395 | -0.10071 | 0.045776 | 0.15564 | -0.11444 | 0.10529 | 0.17853 | 0.059509 | 0.20599 | 120.0668 | -0.18311 | -0.44403 | 120.369 | 120.2545 | 120.1813 | 0.18768 | 0.11444 | 120.2408 | -0.10986 | -0.16022 | 120.5338 | 120.5612 | 120.4147 | 0.32044 | 0.17395 | 0.30212 | 0.10986 | 0.29297 | 0.21973 | 0.37079 | 0.27008 | 120.4376 | 120.5109 | -0.55389 | -0.37994 | 120.1767 | 120.4605 | 120.1813 | 120.401
1755.9375 | 120.7489 | -120.4239 | 0.29297 | 0.0034333 | -0.060618 | 0.012335 | 0.03152 | 0.0052315 | -0.0012925 | -0.00013235 | -0.0014038 | 0.015169 | 0.021422 | 0.022375 | -0.0015337 | 0.0058874 | 0.0024396 | -0.07782 | 0.2243 | -0.1831 | -0.1236 | 0.054932 | -0.068665 | -0.018311 | -0.059509 | 0.1831 | -0.15106 | 0.009155 | 0.09613 | -0.022888 | 0.13275 | 120.2408 | -0.068665 | -0.41656 | 120.4788 | 120.4056 | 120.3552 | 0.16479 | 0.11444 | 120.2728 | -0.10986 | -0.28381 | 120.52 | 120.5566 | 120.401 | 0.28381 | 0.12817 | 0.23804 | 0.059509 | 0.24719 | 0.16022 | 0.40741 | 0.33417 | 120.6482 | 120.607 | -0.47607 | -0.44403 | 120.3003 | 120.433 | 120.3461 | 120.3644
1757.625 | 120.8084 | -120.4239 | 0.27924 | -0.011826 | -0.060831 | 0.012548 | 0.030879 | 0.0030953 | -0.0023605 | -0.0012006 | 0.001648 | 0.011538 | 0.019927 | 0.013403 | -0.00025213 | 0.00781 | 0.00030339 | -0.17853 | 0.10529 | -0.23346 | -0.16937 | 0.027466 | -0.1236 | -0.045776 | -0.013733 | 0.15106 | -0.11444 | 0.027466 | 0.13275 | 0.018311 | 0.14648 | 120.1904 | -0.17395 | -0.44861 | 120.4514 | 120.3781 | 120.3003 | 0.18768 | 0.10986 | 120.3094 | -0.12817 | -0.25177 | 120.5566 | 120.5704 | 120.4422 | 0.26093 | 0.13275 | 0.26093 | 0.064086 | 0.24719 | 0.14191 | 0.33875 | 0.2655 | 120.5292 | 120.575 | -0.5127 | -0.39368 | 120.2545 | 120.4514 | 120.2454 | 120.4102
1759.3906 | 120.8588 | -120.4514 | 0.28381 | 0.011063 | -0.059763 | 0.010839 | 0.027461 | 0.0013863 | -0.0025741 | -0.00077335 | -0.0014038 | 0.011324 | 0.018859 | 0.016607 | -0.00067933 | 0.0090918 | -0.005678 | -0.064087 | 0.16479 | -0.16937 | -0.027466 | 0.1831 | 0.018311 | 0.07782 | 0.068665 | 0.15106 | -0.11902 | 0.091553 | 0.21057 | 0.10071 | 0.19684 | 120.282 | -0.11902 | -0.31128 | 120.6345 | 120.5292 | 120.4697 | 0.24719 | 0.18768 | 120.3323 | -0.13275 | -0.19226 | 120.6619 | 120.6482 | 120.5521 | 0.31586 | 0.21973 | 0.35248 | 0.14191 | 0.32959 | 0.21057 | 0.33417 | 0.27008 | 120.6162 | 120.6024 | -0.45319 | -0.40283 | 120.4239 | 120.5429 | 120.3873 | 120.52
1761.0781 | 120.7993 | -120.4926 | 0.29297 | 0.011063 | -0.060404 | 0.01383 | 0.029811 | 0.00053194 | -0.0044967 | 0.0017902 | 0.0046998 | 0.016878 | 0.020781 | 0.013616 | -3.8532e-05 | 0.0063148 | 0.0011578 | -0.082397 | 0.23804 | -0.18768 | -0.11902 | 0.041199 | -0.073242 | -0.013733 | -0.07782 | 0.18768 | -0.16479 | 0.004578 | 0.10986 | -0.036621 | 0.12817 | 120.3049 | -0.054932 | -0.41199 | 120.5338 | 120.4788 | 120.4193 | 0.17395 | 0.11444 | 120.3278 | -0.10529 | -0.28839 | 120.6024 | 120.6207 | 120.4559 | 0.29297 | 0.12817 | 0.22888 | 0.068664 | 0.27466 | 0.16937 | 0.42572 | 0.35248 | 120.7306 | 120.6802 | -0.48065 | -0.45776 | 120.3735 | 120.4971 | 120.4102 | 120.4147
1762.8281 | 120.813 | -120.5246 | 0.31586 | 0.011063 | -0.058481 | 0.01148 | 0.030238 | 0.00010474 | -0.0038559 | 0.0037128 | 0.0077514 | 0.014956 | 0.022704 | 0.016393 | -0.0040973 | 0.006742 | 0.0013714 | -0.09613 | 0.22888 | -0.16937 | -0.13275 | 0.064087 | -0.068665 | -0.009155 | -0.073242 | 0.19684 | -0.15106 | -0.022888 | 0.068665 | -0.054932 | 0.082397 | 120.3552 | -0.086975 | -0.44861 | 120.5887 | 120.5154 | 120.4559 | 0.16022 | 0.10071 | 120.3735 | -0.11902 | -0.33875 | 120.5933 | 120.607 | 120.4697 | 0.23346 | 0.09613 | 0.23346 | 0.036622 | 0.21973 | 0.12817 | 0.39826 | 0.3479 | 120.7535 | 120.7214 | -0.48523 | -0.46692 | 120.3918 | 120.5017 | 120.4285 | 120.4514
1764.5781 | 120.932 | -120.5154 | 0.28381 | 0.011063 | -0.059336 | 0.012548 | 0.030452 | 0.0062997 | -0.0030015 | 0.00072205 | 0.0077514 | 0.013888 | 0.023558 | 0.015966 | 0.0040205 | 0.006742 | -0.001192 | -0.20142 | 0.09613 | -0.29297 | -0.21973 | -0.032043 | -0.21515 | -0.12817 | 0.004578 | 0.16479 | -0.12817 | 0.07782 | 0.16479 | 0.054932 | 0.19684 | 120.2225 | -0.18768 | -0.50354 | 120.4834 | 120.3873 | 120.3003 | 0.16479 | 0.07782 | 120.3873 | -0.11902 | -0.20599 | 120.6802 | 120.7123 | 120.5704 | 0.32501 | 0.18311 | 0.26093 | 0.073242 | 0.29297 | 0.20599 | 0.3891 | 0.29297 | 120.6116 | 120.6802 | -0.57678 | -0.41199 | 120.2957 | 120.5933 | 120.314 | 120.52
1766.3281 | 120.9778 | -120.5383 | 0.30212 | 0.0034333 | -0.060404 | 0.011053 | 0.030452 | -0.00053626 | -0.0057785 | 0.0062762 | 0.0046998 | 0.011111 | 0.019286 | 0.021307 | 0.00017507 | 0.0063148 | -0.00012381 | -0.059509 | 0.16937 | -0.17853 | -0.036621 | 0.1831 | 0.022888 | 0.07782 | 0.10529 | 0.13275 | -0.11902 | 0.10986 | 0.23346 | 0.11444 | 0.20599 | 120.3598 | -0.13275 | -0.33875 | 120.7214 | 120.6162 | 120.5612 | 0.25635 | 0.20142 | 120.4193 | -0.16937 | -0.19226 | 120.7718 | 120.7443 | 120.6528 | 0.32501 | 0.23346 | 0.36163 | 0.14191 | 0.35248 | 0.22888 | 0.3479 | 0.25177 | 120.7077 | 120.6711 | -0.48065 | -0.42114 | 120.5017 | 120.6482 | 120.4788 | 120.6436
1768.0781 | 120.9869 | -120.5612 | 0.28839 | 0.011063 | -0.058054 | 0.01148 | 0.030238 | 0.0073679 | -0.0019333 | 0.0013628 | -0.0014038 | 0.014315 | 0.021209 | 0.020452 | 0.0029523 | 0.0082374 | 0.00073059 | -0.18768 | 0.073242 | -0.29755 | -0.1831 | 0.004578 | -0.15106 | -0.09613 | 0.054932 | 0.15106 | -0.11902 | 0.09613 | 0.17853 | 0.064087 | 0.20142 | 120.2637 | -0.21515 | -0.4715 | 120.5658 | 120.4651 | 120.4102 | 0.20142 | 0.14648 | 120.4422 | -0.13733 | -0.19226 | 120.7397 | 120.7626 | 120.6253 | 0.32044 | 0.18311 | 0.30212 | 0.11444 | 0.29755 | 0.21515 | 0.37079 | 0.27008 | 120.6345 | 120.7123 | -0.58594 | -0.40741 | 120.3781 | 120.6573 | 120.3735 | 120.6161
1769.7656 | 120.9595 | -120.6207 | 0.31128 | 0.018692 | -0.057627 | 0.011694 | 0.032375 | 0.0022409 | -0.0032151 | -0.00077335 | 0.0046998 | 0.015169 | 0.021849 | 0.01917 | 0.0012433 | 0.0080236 | 0.00030339 | -0.21057 | 0.14648 | -0.29755 | -0.24719 | -0.07782 | -0.23346 | -0.15106 | -0.050354 | 0.16937 | -0.1236 | 0.013733 | 0.086975 | -0.013733 | 0.14191 | 120.3232 | -0.16479 | -0.55847 | 120.5429 | 120.4697 | 120.3873 | 0.14648 | 0.064087 | 120.4971 | -0.14191 | -0.29755 | 120.7077 | 120.7626 | 120.607 | 0.2655 | 0.10986 | 0.21973 | 0.050354 | 0.21057 | 0.13733 | 0.44403 | 0.29297 | 120.7672 | 120.7901 | -0.60882 | -0.43487 | 120.3735 | 120.6345 | 120.4102 | 120.5704
1771.5312 | 121.0052 | -120.6024 | 0.3067 | -0.011826 | -0.058054 | 0.012335 | 0.031093 | 0.00053194 | -0.0032151 | -0.0014142 | 0.0046998 | 0.014315 | 0.019927 | 0.024511 | -0.0021747 | 0.0080236 | -0.00076481 | -0.17853 | 0.09613 | -0.25177 | -0.16022 | 0.022888 | -0.14191 | -0.064087 | -0.009155 | 0.13733 | -0.11902 | 0.036621 | 0.13733 | 0.018311 | 0.15564 | 120.3506 | -0.21057 | -0.46692 | 120.6253 | 120.5383 | 120.4605 | 0.18768 | 0.10986 | 120.4834 | -0.16937 | -0.27008 | 120.7397 | 120.7581 | 120.6207 | 0.27466 | 0.13733 | 0.27466 | 0.091553 | 0.25635 | 0.15564 | 0.3479 | 0.25635 | 120.6985 | 120.7397 | -0.55847 | -0.42572 | 120.4422 | 120.639 | 120.4239 | 120.5933
1773.2812 | 120.9961 | -120.6528 | 0.32959 | 0.0034333 | -0.056772 | 0.012762 | 0.032375 | 0.0075815 | -0.0038559 | 0.00093565 | 0.0077514 | 0.016024 | 0.020568 | 0.014898 | -0.0011065 | 0.0063148 | -0.0014056 | -0.050354 | 0.2243 | -0.19226 | -0.09613 | 0.082397 | -0.073242 | -0.027466 | 0.004578 | 0.16937 | -0.11902 | 0.022888 | 0.11444 | 0.004578 | 0.13733 | 120.4605 | -0.10529 | -0.42572 | 120.7352 | 120.6253 | 120.5795 | 0.16479 | 0.11902 | 120.5338 | -0.16022 | -0.3067 | 120.7672 | 120.7901 | 120.6573 | 0.25635 | 0.1236 | 0.27466 | 0.096131 | 0.23346 | 0.14191 | 0.41656 | 0.28839 | 120.8771 | 120.8221 | -0.52185 | -0.44861 | 120.5566 | 120.6757 | 120.6024 | 120.6573
1774.9688 | 120.9915 | -120.6848 | 0.33875 | -0.0041962 | -0.061899 | 0.012121 | 0.03152 | 0.0041635 | -0.0053513 | -0.00098695 | 0.001648 | 0.015383 | 0.023131 | 0.018316 | -3.8532e-05 | 0.0046058 | -0.0024738 | -0.07782 | 0.2655 | -0.16022 | -0.13275 | 0.041199 | -0.082397 | -0.018311 | -0.07782 | 0.18768 | -0.16022 | -0.036621 | 0.07782 | -0.036621 | 0.10986 | 120.5246 | -0.073242 | -0.4715 | 120.726 | 120.6665 | 120.6024 | 0.14191 | 0.07782 | 120.5246 | -0.15106 | -0.37537 | 120.7626 | 120.7947 | 120.6482 | 0.27008 | 0.1236 | 0.20142 | 0.027466 | 0.23804 | 0.1236 | 0.42572 | 0.3479 | 120.9503 | 120.8725 | -0.49896 | -0.49896 | 120.5521 | 120.6482 | 120.607 | 120.607
1776.7031 | 121.0236 | -120.6757 | 0.32044 | 0.011063 | -0.060831 | 0.011907 | 0.02917 | 0.0045907 | -0.0062057 | 0.00050845 | 0.001648 | 0.014101 | 0.0195 | 0.014257 | -0.00025213 | 0.0063148 | 0.002226 | -0.07782 | 0.24719 | -0.17853 | -0.10986 | 0.050354 | -0.064087 | -0.022888 | -0.045776 | 0.17853 | -0.14648 | 0.018311 | 0.11444 | 0.004578 | 0.13275 | 120.4971 | -0.073243 | -0.4303 | 120.726 | 120.6528 | 120.6116 | 0.15564 | 0.11444 | 120.5292 | -0.14191 | -0.30212 | 120.7901 | 120.8084 | 120.6802 | 0.27924 | 0.15106 | 0.22888 | 0.068665 | 0.26093 | 0.16479 | 0.42572 | 0.32501 | 120.9229 | 120.8542 | -0.49896 | -0.46692 | 120.5658 | 120.694 | 120.5978 | 120.6299
1778.4531 | 121.0922 | -120.694 | 0.31128 | 0.011063 | -0.061045 | 0.011907 | 0.028102 | 0.0024545 | -0.0015061 | -0.00055975 | 0.001648 | 0.014742 | 0.021422 | 0.018316 | -3.8532e-05 | 0.0073828 | 0.0011578 | -0.16479 | 0.11902 | -0.23346 | -0.17853 | 0.022888 | -0.13733 | -0.041199 | -0.009155 | 0.15106 | -0.1236 | 0.022888 | 0.13275 | 0.032043 | 0.15564 | 120.4605 | -0.19226 | -0.48981 | 120.7169 | 120.6528 | 120.5566 | 0.19226 | 0.09613 | 120.5704 | -0.16022 | -0.28839 | 120.8267 | 120.8496 | 120.726 | 0.27924 | 0.15564 | 0.25635 | 0.054931 | 0.25635 | 0.14648 | 0.35248 | 0.27466 | 120.813 | 120.845 | -0.54474 | -0.43487 | 120.5154 | 120.7169 | 120.5292 | 120.6848
1780.2188 | 121.1243 | -120.7031 | 0.3067 | 0.0034333 | -0.058909 | 0.011053 | 0.028529 | 0.0022409 | -0.0032151 | 0.0026446 | 0.001648 | 0.014529 | 0.018645 | 0.014471 | 0.0016705 | 0.0073828 | 0.0024396 | -0.15564 | 0.082397 | -0.2655 | -0.15106 | 0.054932 | -0.13733 | -0.054932 | 0.050354 | 0.15106 | -0.10529 | 0.086975 | 0.16937 | 0.059509 | 0.17395 | 120.4376 | -0.2243 | -0.45776 | 120.7581 | 120.6482 | 120.5658 | 0.21057 | 0.12817 | 120.5978 | -0.15564 | -0.21973 | 120.8725 | 120.8771 | 120.7626 | 0.27924 | 0.16479 | 0.32043 | 0.11444 | 0.27466 | 0.19226 | 0.3479 | 0.25635 | 120.7855 | 120.8542 | -0.5722 | -0.41199 | 120.5521 | 120.7901 | 120.5475 | 120.7535
1781.9688 | 121.0373 | -120.7718 | 0.33417 | 0.018692 | -0.055918 | 0.012762 | 0.032375 | 0.0065133 | -0.0036423 | 0.0022174 | -0.0014038 | 0.015383 | 0.020995 | 0.0095574 | 0.0010297 | 0.0086646 | 0.0045758 | -0.17853 | 0.13275 | -0.27924 | -0.23346 | -0.068665 | -0.21973 | -0.14191 | -0.10986 | 0.20142 | -0.15106 | -0.041199 | 0.018311 | -0.082397 | 0.086975 | 120.4926 | -0.20142 | -0.56763 | 120.7031 | 120.6299 | 120.5521 | 0.13733 | 0.059509 | 120.6207 | -0.13275 | -0.37537 | 120.7901 | 120.8588 | 120.6894 | 0.23804 | 0.068665 | 0.21057 | 0.045777 | 0.16937 | 0.10986 | 0.41199 | 0.35248 | 120.9045 | 120.9732 | -0.6134 | -0.48523 | 120.5383 | 120.7306 | 120.5933 | 120.6619
1783.6562 | 121.2021 | -120.7443 | 0.3067 | 0.011063 | -0.06254 | 0.012335 | 0.027248 | 0.0026681 | -0.0023605 | 0.0022174 | -0.0014038 | 0.014315 | 0.021849 | 0.015753 | 0.0046613 | 0.0090918 | -0.001192 | -0.20142 | 0.064087 | -0.29755 | -0.19226 | 0.004578 | -0.16479 | -0.10986 | 0.036621 | 0.14191 | -0.10986 | 0.09613 | 0.16022 | 0.041199 | 0.21515 | 120.4468 | -0.24261 | -0.49896 | 120.7489 | 120.6345 | 120.5795 | 0.18768 | 0.13275 | 120.6345 | -0.16479 | -0.21057 | 120.9045 | 120.9595 | 120.7855 | 0.32501 | 0.15106 | 0.30212 | 0.10528 | 0.27008 | 0.20599 | 0.36163 | 0.25177 | 120.8084 | 120.8862 | -0.60425 | -0.41656 | 120.5521 | 120.8405 | 120.5429 | 120.7809
1785.4062 | 121.2341 | -120.7672 | 0.31128 | 0.0034333 | -0.060831 | 0.010626 | 0.028316 | 0.0062997 | -0.00065149 | 0.00093565 | -0.0014038 | 0.013247 | 0.020568 | 0.016607 | -0.0019611 | 0.0071692 | 0.00030339 | -0.09613 | 0.14191 | -0.21057 | -0.068665 | 0.13733 | -0.018311 | 0.041199 | 0.064087 | 0.15106 | -0.13275 | 0.09613 | 0.20599 | 0.11902 | 0.22888 | 120.5566 | -0.16937 | -0.37994 | 120.9045 | 120.8084 | 120.7489 | 0.25177 | 0.19226 | 120.6345 | -0.16022 | -0.21515 | 120.9732 | 120.9961 | 120.8862 | 0.36163 | 0.25177 | 0.3479 | 0.14191 | 0.33875 | 0.22888 | 0.35248 | 0.28381 | 120.9091 | 120.9183 | -0.52185 | -0.44403 | 120.6985 | 120.8633 | 120.6711 | 120.8313
1787.0938 | 121.1151 | -120.7947 | 0.3479 | 0.011063 | -0.056986 | 0.012121 | 0.03152 | 0.0030953 | -0.0044967 | 0.00414 | 0.0046998 | 0.016237 | 0.022704 | 0.017462 | -0.0021747 | 0.0058874 | 0.002226 | -0.11902 | 0.16937 | -0.24261 | -0.17395 | -0.004578 | -0.16022 | -0.09613 | -0.036621 | 0.19226 | -0.12817 | -0.027466 | 0.050354 | -0.068665 | 0.10529 | 120.5521 | -0.17853 | -0.52185 | 120.7901 | 120.6985 | 120.6345 | 0.14649 | 0.082398 | 120.6665 | -0.15564 | -0.37537 | 120.845 | 120.9 | 120.726 | 0.23346 | 0.059509 | 0.23804 | 0.068665 | 0.17853 | 0.10071 | 0.41199 | 0.32044 | 120.9641 | 120.9869 | -0.59052 | -0.47607 | 120.6207 | 120.7672 | 120.6757 | 120.7581
1788.8438 | 121.2021 | -120.813 | 0.32501 | 0.0034333 | -0.059122 | 0.011694 | 0.029811 | 0.0026681 | -0.0032151 | 0.0011492 | 0.001648 | 0.013674 | 0.020354 | 0.019598 | 0.00038887 | 0.0063148 | 0.0035078 | -0.1831 | 0.11444 | -0.25177 | -0.1831 | 0.022888 | -0.13275 | -0.045776 | -0.032043 | 0.15564 | -0.13733 | 0.032043 | 0.13733 | 0.027466 | 0.15106 | 120.5612 | -0.21057 | -0.50812 | 120.8359 | 120.7672 | 120.6802 | 0.20599 | 0.11902 | 120.6757 | -0.16937 | -0.29297 | 120.9503 | 120.9641 | 120.8405 | 0.28839 | 0.16479 | 0.27466 | 0.068665 | 0.27466 | 0.16937 | 0.36621 | 0.29297 | 120.9274 | 120.9686 | -0.57678 | -0.46234 | 120.6299 | 120.845 | 120.6299 | 120.7809
1790.5938 | 121.1334 | -120.8313 | 0.35248 | 0.011063 | -0.059763 | 0.012548 | 0.030452 | 0.0080087 | -0.0023605 | -0.00055975 | 0.0046998 | 0.014315 | 0.021849 | 0.011266 | -3.8532e-05 | 0.0075964 | -0.0022602 | -0.16022 | 0.16022 | -0.2655 | -0.22888 | -0.041199 | -0.20142 | -0.13733 | -0.10071 | 0.18768 | -0.14191 | -0.032043 | 0.050354 | -0.07782 | 0.086975 | 120.5658 | -0.19226 | -0.58136 | 120.7901 | 120.694 | 120.6299 | 0.12817 | 0.064087 | 120.6894 | -0.1648 | -0.38452 | 120.8817 | 120.9183 | 120.7535 | 0.22888 | 0.064087 | 0.2243 | 0.036621 | 0.19226 | 0.10986 | 0.42572 | 0.32959 | 120.9915 | 121.019 | -0.61798 | -0.49439 | 120.6024 | 120.7993 | 120.6711 | 120.7306
1792.2812 | 121.2891 | -120.8359 | 0.32959 | 0.011063 | -0.059977 | 0.011907 | 0.027675 | 0.0018137 | -0.0025741 | 0.00029485 | -0.0044556 | 0.01047 | 0.022063 | 0.015112 | -0.0026019 | 0.0056738 | 0.00073059 | -0.13275 | 0.1236 | -0.21515 | -0.11444 | 0.10986 | -0.064087 | 0.013733 | 0.041199 | 0.16937 | -0.11902 | 0.064087 | 0.1831 | 0.082397 | 0.20599 | 120.6207 | -0.20599 | -0.44403 | 120.9457 | 120.8496 | 120.7718 | 0.22888 | 0.15106 | 120.7169 | -0.16022 | -0.2655 | 121.019 | 121.0419 | 120.9183 | 0.32501 | 0.20142 | 0.32501 | 0.10071 | 0.30212 | 0.18311 | 0.33875 | 0.28839 | 120.9595 | 121.0052 | -0.54474 | -0.44861 | 120.7214 | 120.9 | 120.7031 | 120.8771
1794.0469 | 121.2799 | -120.8313 | 0.33875 | -0.0041962 | -0.058481 | 0.010626 | 0.029598 | 0.00053194 | -0.0040695 | 0.0039264 | 0.001648 | 0.013033 | 0.02249 | 0.019384 | 0.0016705 | 0.008451 | 0.00030339 | -0.16479 | 0.10986 | -0.21057 | -0.13733 | 0.045776 | -0.10071 | -0.027466 | -0.004578 | 0.15564 | -0.1236 | 0.073242 | 0.14191 | 0.059509 | 0.17395 | 120.6207 | -0.22888 | -0.47607 | 120.8771 | 120.8038 | 120.7306 | 0.18311 | 0.10986 | 120.7077 | -0.18311 | -0.2655 | 120.9732 | 121.0052 | 120.8908 | 0.29755 | 0.1831 | 0.25635 | 0.073242 | 0.2655 | 0.19684 | 0.32043 | 0.27924 | 120.9412 | 120.9869 | -0.54932 | -0.46234 | 120.694 | 120.9045 | 120.6665 | 120.8267
1795.8125 | 121.2158 | -120.8954 | 0.37079 | 0.011063 | -0.059763 | 0.0095576 | 0.029384 | 0.0058725 | -0.0051377 | 0.0013628 | -0.0044556 | 0.013888 | 0.019713 | 0.010839 | -0.0019611 | 0.0063148 | -0.0026874 | -0.086975 | 0.21515 | -0.18768 | -0.13275 | 0.068665 | -0.082397 | -0.004578 | -0.073242 | 0.19226 | -0.13275 | -0.036621 | 0.054932 | -0.027466 | 0.082397 | 120.7077 | -0.15564 | -0.50354 | 120.9641 | 120.8908 | 120.813 | 0.1831 | 0.10529 | 120.7626 | -0.17853 | -0.40741 | 120.9503 | 120.9778 | 120.8679 | 0.21515 | 0.10529 | 0.25635 | 0.054932 | 0.18768 | 0.09613 | 0.40283 | 0.32501 | 121.1105 | 121.0876 | -0.55847 | -0.50354 | 120.7626 | 120.8588 | 120.8084 | 120.8221
1797.5625 | 121.2845 | -120.8633 | 0.33875 | 0.0034333 | -0.060831 | 0.0089166 | 0.028316 | 0.0033089 | -0.0038559 | 0.0022174 | 0.001648 | 0.012606 | 0.023772 | 0.017248 | 0.00081607 | 0.0071692 | 0.003935 | -0.16479 | 0.11902 | -0.23804 | -0.15106 | 0.022888 | -0.14191 | -0.045776 | -0.009155 | 0.13275 | -0.12817 | 0.036621 | 0.15106 | 0.041199 | 0.16937 | 120.6253 | -0.21973 | -0.48981 | 120.8862 | 120.8176 | 120.7214 | 0.19226 | 0.09613 | 120.7352 | -0.20599 | -0.30212 | 121.0144 | 121.0327 | 120.9045 | 0.29755 | 0.16937 | 0.26093 | 0.086975 | 0.27924 | 0.1648 | 0.35706 | 0.26093 | 120.9824 | 120.9961 | -0.57678 | -0.46692 | 120.7123 | 120.9 | 120.6985 | 120.8542
1799.2656 | 121.3257 | -120.8679 | 0.37079 | 0.0034333 | -0.061259 | 0.010839 | 0.027034 | 0.00031834 | -0.0055649 | 0.0011492 | 0.0046998 | 0.012179 | 0.022063 | 0.02152 | -0.0013201 | 0.0041784 | 0.003935 | -0.16479 | 0.10529 | -0.23804 | -0.16479 | 0.022888 | -0.12817 | -0.050354 | -0.009155 | 0.14191 | -0.13275 | 0.050354 | 0.14648 | 0.041199 | 0.17395 | 120.6299 | -0.2655 | -0.53558 | 120.8908 | 120.8176 | 120.7397 | 0.18768 | 0.10986 | 120.7352 | -0.22888 | -0.32043 | 121.0144 | 121.0419 | 120.9091 | 0.3067 | 0.17395 | 0.26093 | 0.073242 | 0.27924 | 0.18311 | 0.34332 | 0.27466 | 120.9732 | 121.0098 | -0.60883 | -0.50354 | 120.7031 | 120.9183 | 120.7031 | 120.8588
1801.0312 | 121.376 | -120.8633 | 0.32044 | 0.011063 | -0.059763 | 0.012762 | 0.031093 | 0.0067269 | -0.0010789 | 0.002431 | 0.001648 | 0.015169 | 0.020995 | 0.022802 | 0.0042341 | 0.006101 | -0.00055121 | -0.17853 | 0.07782 | -0.28381 | -0.16479 | 0.036621 | -0.14191 | -0.073242 | 0.054932 | 0.15564 | -0.10986 | 0.10071 | 0.17853 | 0.068665 | 0.20599 | 120.5795 | -0.24262 | -0.48523 | 120.9 | 120.7901 | 120.7214 | 0.21057 | 0.14191 | 120.7535 | -0.1648 | -0.21973 | 121.0419 | 121.0693 | 120.932 | 0.31586 | 0.17853 | 0.32043 | 0.11902 | 0.28839 | 0.21057 | 0.36163 | 0.2655 | 120.9412 | 121.019 | -0.60425 | -0.4303 | 120.6985 | 120.9641 | 120.6848 | 120.9183
1802.7656 | 121.376 | -120.8817 | 0.32959 | 0.0034333 | -0.058909 | 0.01618 | 0.031307 | 0.0071541 | -0.0025741 | 0.00029485 | 0.001648 | 0.013247 | 0.021209 | 0.015539 | 0.00081607 | 0.0069556 | -0.00033761 | -0.21057 | 0.068665 | -0.27008 | -0.20142 | -0.013733 | -0.17853 | -0.10529 | 0.041199 | 0.16022 | -0.1236 | 0.09613 | 0.16479 | 0.059509 | 0.21057 | 120.6116 | -0.26092 | -0.53101 | 120.8679 | 120.7764 | 120.7031 | 0.1648 | 0.091553 | 120.7581 | -0.16937 | -0.23346 | 121.0464 | 121.0922 | 120.9412 | 0.33417 | 0.1831 | 0.25635 | 0.068665 | 0.28839 | 0.21973 | 0.33875 | 0.28381 | 120.9503 | 121.0419 | -0.59967 | -0.45319 | 120.6802 | 120.9778 | 120.6711 | 120.9229
1804.4531 | 121.3211 | -120.9366 | 0.36621 | 0.0034333 | -0.058481 | 0.010412 | 0.03152 | 0.0056589 | -0.0025741 | 0.00072205 | 0.0046998 | 0.014742 | 0.019286 | 0.014471 | -0.0017475 | 0.00781 | -0.0024738 | -0.10529 | 0.22888 | -0.20142 | -0.12817 | 0.041199 | -0.07782 | -0.027466 | -0.064087 | 0.19684 | -0.13733 | -0.009155 | 0.10071 | -0.022888 | 0.1236 | 120.7352 | -0.13733 | -0.49439 | 120.9778 | 120.9091 | 120.8588 | 0.17395 | 0.1236 | 120.7993 | -0.16937 | -0.37537 | 121.0373 | 121.0602 | 120.9137 | 0.26093 | 0.11444 | 0.24262 | 0.073242 | 0.23804 | 0.12817 | 0.4303 | 0.33417 | 121.1655 | 121.1334 | -0.56763 | -0.50354 | 120.8084 | 120.9274 | 120.8313 | 120.8725
1806.2031 | 121.3303 | -120.932 | 0.36163 | 0.0034333 | -0.057413 | 0.013616 | 0.031307 | 0.0080087 | -0.0023605 | 0.0017902 | 0.001648 | 0.016237 | 0.022277 | 0.01383 | -0.00046573 | 0.0069556 | 0.0035078 | -0.10071 | 0.1831 | -0.23346 | -0.12817 | 0.045776 | -0.10071 | -0.036621 | 0.013733 | 0.1831 | -0.14191 | 0.032043 | 0.11902 | -0.009155 | 0.1236 | 120.6985 | -0.17853 | -0.48981 | 120.9778 | 120.8954 | 120.8313 | 0.19684 | 0.13275 | 120.7901 | -0.17853 | -0.32959 | 121.051 | 121.0556 | 120.9229 | 0.2655 | 0.13275 | 0.27924 | 0.10528 | 0.26093 | 0.17395 | 0.41656 | 0.32501 | 121.1151 | 121.1151 | -0.59509 | -0.50354 | 120.8038 | 120.9641 | 120.8313 | 120.9457
1807.9688 | 121.431 | -120.9503 | 0.35706 | -0.0041962 | -0.060618 | 0.012121 | 0.029384 | 0.0037363 | -0.0027877 | 0.00029485 | -0.0014038 | 0.014315 | 0.019927 | 0.017034 | -0.0013201 | 0.0080236 | 0.0041486 | -0.073242 | 0.15106 | -0.20599 | -0.041199 | 0.1831 | 0.013733 | 0.054932 | 0.086975 | 0.16022 | -0.10986 | 0.091553 | 0.2243 | 0.10986 | 0.20142 | 120.7443 | -0.20599 | -0.39825 | 121.1334 | 121.0052 | 120.9641 | 0.26093 | 0.21973 | 120.8405 | -0.19684 | -0.2655 | 121.1746 | 121.1517 | 121.0602 | 0.31128 | 0.21973 | 0.3891 | 0.1648 | 0.33417 | 0.20142 | 0.35706 | 0.27008 | 121.1014 | 121.1105 | -0.56305 | -0.46692 | 120.9091 | 121.0419 | 120.8771 | 121.0373
1809.7188 | 121.4035 | -120.9595 | 0.35706 | 0.0034333 | -0.05955 | 0.013189 | 0.030666 | 0.0033089 | -0.0017197 | 0.0017902 | 0.010803 | 0.014529 | 0.021636 | 0.015112 | -0.0015337 | 0.0069556 | 0.0041486 | -0.1831 | 0.073242 | -0.26093 | -0.16937 | 0.036621 | -0.14648 | -0.064087 | 0.013733 | 0.14648 | -0.12817 | 0.041199 | 0.13275 | 0.027466 | 0.15106 | 120.6985 | -0.28381 | -0.52643 | 120.9961 | 120.8954 | 120.813 | 0.19684 | 0.11444 | 120.8313 | -0.21057 | -0.31586 | 121.0922 | 121.1105 | 120.9869 | 0.27924 | 0.15564 | 0.29755 | 0.091552 | 0.26093 | 0.16937 | 0.33417 | 0.27466 | 121.0327 | 121.106 | -0.61798 | -0.48523 | 120.7901 | 121.0007 | 120.7764 | 120.9732
1811.4688 | 121.4539 | -120.9778 | 0.35706 | -0.011826 | -0.06019 | 0.011907 | 0.028102 | 0.0075815 | -0.0025741 | -0.00098695 | 0.0046998 | 0.014742 | 0.020568 | 0.017248 | 0.0023115 | 0.005033 | -0.001192 | -0.073242 | 0.17853 | -0.16479 | -0.036621 | 0.16479 | 0 | 0.059509 | 0.054932 | 0.15106 | -0.11444 | 0.064087 | 0.17395 | 0.082397 | 0.18768 | 120.813 | -0.17853 | -0.39368 | 121.1426 | 121.0373 | 120.9778 | 0.2243 | 0.16479 | 120.8633 | -0.20599 | -0.29297 | 121.1517 | 121.1655 | 121.0602 | 0.30212 | 0.19684 | 0.32959 | 0.12817 | 0.28839 | 0.17853 | 0.34332 | 0.2655 | 121.1563 | 121.1288 | -0.52185 | -0.4715 | 120.9412 | 121.0419 | 120.9045 | 121.0327
1813.1562 | 121.3715 | -121.0144 | 0.39825 | 0.0034333 | -0.060404 | 0.01148 | 0.027889 | 0.00074554 | -0.0030015 | -0.00055975 | -0.0014038 | 0.01346 | 0.021849 | 0.016607 | -0.0036701 | 0.005033 | -0.00097841 | -0.07782 | 0.19226 | -0.16937 | -0.10986 | 0.068665 | -0.068665 | 0.004578 | -0.068665 | 0.18768 | -0.13733 | -0.032043 | 0.068665 | -0.032043 | 0.09613 | 120.845 | -0.20599 | -0.50812 | 121.0831 | 121.019 | 120.9457 | 0.17395 | 0.10071 | 120.8771 | -0.21057 | -0.4303 | 121.0831 | 121.1105 | 120.9824 | 0.23346 | 0.10529 | 0.23804 | 0.05951 | 0.20599 | 0.10529 | 0.36163 | 0.32501 | 121.2067 | 121.2021 | -0.56763 | -0.53558 | 120.9045 | 120.9824 | 120.9366 | 120.9457
1814.9062 | 121.4813 | -121.019 | 0.32959 | 0.0034333 | -0.059336 | 0.013616 | 0.029598 | 0.00074554 | -0.0010789 | 0.0017902 | 0.0046998 | 0.01282 | 0.02014 | 0.019384 | -3.8532e-05 | 0.0058874 | 0.005003 | -0.14191 | 0.12817 | -0.23346 | -0.11444 | 0.059509 | -0.07782 | 0.009155 | 0.018311 | 0.14648 | -0.1236 | 0.073242 | 0.18768 | 0.086975 | 0.19684 | 120.7855 | -0.20142 | -0.44403 | 121.0785 | 121.0281 | 120.9412 | 0.24261 | 0.15564 | 120.8954 | -0.18311 | -0.25635 | 121.2067 | 121.2158 | 121.106 | 0.32043 | 0.21057 | 0.29297 | 0.11902 | 0.31128 | 0.19684 | 0.36163 | 0.27008 | 121.1472 | 121.1655 | -0.56305 | -0.45319 | 120.9045 | 121.0922 | 120.8771 | 121.0373
1816.6406 | 121.3898 | -121.051 | 0.37537 | 0.018692 | -0.05955 | 0.010626 | 0.031093 | 0.0045907 | -0.0047103 | 0.0020038 | -0.0014038 | 0.016665 | 0.021209 | 0.0093438 | -0.0017475 | 0.0058874 | -0.0016192 | -0.10071 | 0.23804 | -0.17395 | -0.16022 | 0.027466 | -0.082397 | -0.036621 | -0.086975 | 0.20599 | -0.15106 | -0.018311 | 0.073242 | -0.032043 | 0.1236 | 120.8771 | -0.13733 | -0.53558 | 121.0785 | 121.0144 | 120.9686 | 0.13733 | 0.091553 | 120.9 | -0.16937 | -0.39368 | 121.1243 | 121.1746 | 121.019 | 0.27466 | 0.11902 | 0.20142 | 0.013733 | 0.2243 | 0.13275 | 0.41199 | 0.35706 | 121.2891 | 121.257 | -0.54932 | -0.52643 | 120.8908 | 121.0327 | 120.9503 | 120.9641
1818.3906 | 121.4722 | -121.0464 | 0.34332 | 0.011063 | -0.060404 | 0.010412 | 0.029811 | 0.0028817 | -0.0023605 | 0.003499 | 0.001648 | 0.01346 | 0.021209 | 0.020025 | 0.0010297 | 0.00781 | 0.0028668 | -0.1831 | 0.10986 | -0.24719 | -0.16479 | 0.022888 | -0.13275 | -0.050354 | -0.041199 | 0.15564 | -0.13275 | 0.041199 | 0.12817 | 0.032043 | 0.15564 | 120.7993 | -0.23346 | -0.50812 | 121.0693 | 120.9961 | 120.9137 | 0.19684 | 0.11444 | 120.9137 | -0.18768 | -0.30212 | 121.1746 | 121.2021 | 121.0785 | 0.28839 | 0.16479 | 0.27008 | 0.082397 | 0.26093 | 0.17395 | 0.35706 | 0.28839 | 121.1563 | 121.2021 | -0.59052 | -0.47607 | 120.8817 | 121.0876 | 120.8633 | 121.0052
1820.1406 | 121.4264 | -121.0693 | 0.39368 | -0.0041962 | -0.058695 | 0.011267 | 0.032161 | 0.0058725 | -0.0042831 | 0.0013628 | -0.0044556 | 0.015169 | 0.020354 | 0.014898 | 0.0016705 | 0.0071692 | -0.0016192 | -0.13733 | 0.14191 | -0.24261 | -0.17395 | -0.009155 | -0.16937 | -0.10529 | -0.059509 | 0.1831 | -0.13733 | -0.004578 | 0.054932 | -0.059509 | 0.10071 | 120.8267 | -0.25177 | -0.56763 | 121.0602 | 120.9641 | 120.9 | 0.13733 | 0.073242 | 120.932 | -0.21057 | -0.39826 | 121.1243 | 121.17 | 121.0098 | 0.23804 | 0.07782 | 0.23346 | 0.068665 | 0.19226 | 0.13275 | 0.38452 | 0.32043 | 121.2112 | 121.2524 | -0.63629 | -0.53101 | 120.8954 | 121.0648 | 120.932 | 121.0098
1821.8906 | 121.5134 | -121.0419 | 0.37994 | -0.0041962 | -0.06019 | 0.011694 | 0.028743 | 0.0043771 | -0.0040695 | -0.00055975 | 0.0046998 | 0.012179 | 0.020781 | 0.021734 | 0.00038887 | 0.0075964 | -0.0026874 | -0.17853 | 0.11444 | -0.25635 | -0.16937 | 0.032043 | -0.1236 | -0.068665 | -0.022888 | 0.16022 | -0.14191 | 0.027466 | 0.14191 | 0.009155 | 0.17395 | 120.7855 | -0.2655 | -0.54932 | 121.0739 | 120.9732 | 120.9183 | 0.18768 | 0.13275 | 120.9 | -0.21973 | -0.35248 | 121.1838 | 121.2158 | 121.051 | 0.31586 | 0.15106 | 0.28839 | 0.086975 | 0.28381 | 0.16937 | 0.37079 | 0.30212 | 121.1563 | 121.2021 | -0.63629 | -0.52185 | 120.8725 | 121.0693 | 120.8633 | 121.019
1823.5625 | 121.4813 | -121.0693 | 0.38452 | 0.0034333 | -0.059977 | 0.012121 | 0.031093 | 0.0024545 | -0.0034287 | -0.00034615 | 0.001648 | 0.016665 | 0.018431 | 0.012762 | -0.0015337 | 0.008451 | -0.0065326 | -0.10986 | 0.16022 | -0.22888 | -0.15564 | 0.032043 | -0.12817 | -0.073242 | -0.009155 | 0.19226 | -0.14191 | 0.022888 | 0.10071 | -0.041199 | 0.12817 | 120.8405 | -0.2243 | -0.54016 | 121.1014 | 120.9961 | 120.9412 | 0.15564 | 0.10071 | 120.9274 | -0.19226 | -0.36163 | 121.17 | 121.1975 | 121.0281 | 0.27008 | 0.10071 | 0.26093 | 0.073242 | 0.24262 | 0.16479 | 0.3891 | 0.33417 | 121.2296 | 121.2616 | -0.6134 | -0.52643 | 120.9137 | 121.0922 | 120.9595 | 121.0602
1825.3281 | 121.582 | -121.0373 | 0.3479 | 0.0034333 | -0.05955 | 0.01148 | 0.027461 | 0.0020273 | -0.0038559 | 8.125e-05 | 0.0046998 | 0.011538 | 0.019286 | 0.01618 | -0.00089293 | 0.0071692 | -0.0022602 | -0.086975 | 0.13275 | -0.19226 | -0.054932 | 0.17395 | 0.018311 | 0.054932 | 0.059509 | 0.15106 | -0.10071 | 0.09613 | 0.20142 | 0.10986 | 0.21057 | 120.845 | -0.21515 | -0.40283 | 121.2112 | 121.0922 | 121.0556 | 0.24719 | 0.21057 | 120.9366 | -0.19684 | -0.25177 | 121.2387 | 121.2479 | 121.1472 | 0.31128 | 0.21057 | 0.36621 | 0.13733 | 0.30212 | 0.19684 | 0.32501 | 0.25177 | 121.17 | 121.1884 | -0.54016 | -0.44861 | 120.9824 | 121.1334 | 120.9503 | 121.0968
1827.0781 | 121.5866 | -121.0968 | 0.36163 | 0.018692 | -0.060404 | 0.013403 | 0.028529 | 0.0039499 | -0.0042831 | 0.0020038 | 0.001648 | 0.012392 | 0.0195 | 0.020452 | -0.00046573 | 0.00781 | -0.0054644 | -0.064087 | 0.15106 | -0.17395 | -0.041199 | 0.16479 | 0.004578 | 0.050354 | 0.064087 | 0.13733 | -0.10071 | 0.091553 | 0.19684 | 0.086975 | 0.19684 | 120.9229 | -0.21057 | -0.40283 | 121.2616 | 121.1472 | 121.1014 | 0.2243 | 0.17853 | 120.9961 | -0.2243 | -0.27008 | 121.2936 | 121.2936 | 121.1838 | 0.29755 | 0.18768 | 0.33874 | 0.13275 | 0.29755 | 0.19226 | 0.32501 | 0.23804 | 121.2479 | 121.2341 | -0.53558 | -0.46234 | 121.0556 | 121.1884 | 121.0327 | 121.1609
1828.75 | 121.5271 | -121.1334 | 0.37994 | -0.0041962 | -0.06019 | 0.010412 | 0.029811 | 0.0035227 | -0.0057785 | -0.00034615 | 0.0046998 | 0.016237 | 0.018859 | 0.014471 | 0.00081607 | 0.0069556 | 0.0013714 | -0.10529 | 0.23804 | -0.19684 | -0.12817 | 0.041199 | -0.073242 | -0.022888 | -0.050354 | 0.18768 | -0.14191 | 0.004578 | 0.10529 | 0.009155 | 0.14191 | 120.9366 | -0.14191 | -0.50812 | 121.1746 | 121.1105 | 121.0602 | 0.17395 | 0.1236 | 120.9915 | -0.19226 | -0.37537 | 121.2387 | 121.2753 | 121.1426 | 0.28381 | 0.15106 | 0.23804 | 0.068664 | 0.24719 | 0.14649 | 0.43488 | 0.32959 | 121.3715 | 121.3211 | -0.57678 | -0.52185 | 121.0052 | 121.138 | 121.0281 | 121.0831
1830.5156 | 121.6507 | -121.1197 | 0.33417 | 0.0034333 | -0.059977 | 0.010412 | 0.030452 | -0.00053626 | -0.0038559 | 0.0026446 | 0.0046998 | 0.011538 | 0.020354 | 0.021307 | -0.0019611 | 0.0058874 | -0.0037554 | -0.086975 | 0.14191 | -0.20599 | -0.054932 | 0.16479 | 0 | 0.050354 | 0.10071 | 0.14191 | -0.09613 | 0.10529 | 0.21057 | 0.10986 | 0.21057 | 120.9137 | -0.19226 | -0.3891 | 121.2845 | 121.17 | 121.1197 | 0.25635 | 0.20599 | 121.0236 | -0.19226 | -0.22888 | 121.3303 | 121.3303 | 121.2296 | 0.3067 | 0.20599 | 0.37079 | 0.15106 | 0.3067 | 0.20142 | 0.3479 | 0.23804 | 121.2616 | 121.2616 | -0.54016 | -0.4303 | 121.0648 | 121.225 | 121.0327 | 121.2204
1832.2031 | 121.4996 | -121.17 | 0.36163 | 0.0034333 | -0.058054 | 0.012762 | 0.033656 | 0.0073679 | -0.0049241 | 8.125e-05 | 0.0046998 | 0.016878 | 0.020568 | 0.014044 | 0.0031659 | 0.006101 | -0.0031146 | -0.20142 | 0.1236 | -0.29297 | -0.27008 | -0.10529 | -0.2655 | -0.17395 | -0.09613 | 0.19684 | -0.15564 | -0.022888 | 0.032043 | -0.068665 | 0.091553 | 120.8771 | -0.23804 | -0.63171 | 121.0648 | 120.9961 | 120.9045 | 0.11902 | 0.027466 | 121.0144 | -0.16479 | -0.38452 | 121.2021 | 121.2616 | 121.1014 | 0.24719 | 0.086975 | 0.18768 | 0.022888 | 0.18768 | 0.13275 | 0.41656 | 0.35248 | 121.2936 | 121.3669 | -0.6546 | -0.51727 | 120.9 | 121.1472 | 120.9686 | 121.0739
1833.9531 | 121.6278 | -121.138 | 0.35706 | 0.0034333 | -0.062327 | 0.011267 | 0.028957 | -0.00010886 | -0.0030015 | 0.00029485 | 0.0077514 | 0.01282 | 0.020354 | 0.020025 | -3.8532e-05 | 0.0063148 | 0.0024396 | -0.15106 | 0.1236 | -0.24261 | -0.15106 | 0.045776 | -0.086975 | -0.036621 | 0.022888 | 0.15564 | -0.11444 | 0.07782 | 0.17853 | 0.082397 | 0.19684 | 120.8954 | -0.23346 | -0.50812 | 121.1838 | 121.1014 | 121.051 | 0.20599 | 0.15564 | 121.0236 | -0.20142 | -0.27924 | 121.3165 | 121.3348 | 121.2204 | 0.31128 | 0.19684 | 0.28839 | 0.091553 | 0.29297 | 0.19226 | 0.36621 | 0.27008 | 121.2616 | 121.2936 | -0.59967 | -0.4715 | 120.9869 | 121.2158 | 120.9869 | 121.1609
1835.7031 | 121.5866 | -121.1655 | 0.37994 | 0.018692 | -0.058909 | 0.011907 | 0.030879 | 0.0026681 | -0.0038559 | -0.0035504 | 0.001648 | 0.015383 | 0.022063 | 0.01917 | 0.0023115 | 0.00781 | 0.001585 | -0.20142 | 0.10986 | -0.30212 | -0.26093 | -0.068665 | -0.24719 | -0.16479 | -0.027466 | 0.19684 | -0.12817 | 0.022888 | 0.082397 | -0.027466 | 0.13733 | 120.8633 | -0.27008 | -0.64087 | 121.0968 | 121.0007 | 120.9183 | 0.13733 | 0.054932 | 121.0373 | -0.18311 | -0.35706 | 121.2479 | 121.3028 | 121.138 | 0.2655 | 0.10071 | 0.23346 | 0.041199 | 0.21057 | 0.15106 | 0.41199 | 0.32501 | 121.2753 | 121.3623 | -0.68207 | -0.50812 | 120.9045 | 121.1884 | 120.9641 | 121.138
1837.4375 | 121.6736 | -121.1609 | 0.3479 | 0.011063 | -0.05955 | 0.012975 | 0.030452 | 0.0020273 | -0.0049241 | 0.0020038 | 0.001648 | 0.014101 | 0.020568 | 0.022161 | 0.0046613 | 0.0065284 | -0.0018328 | -0.16479 | 0.073242 | -0.27924 | -0.15564 | 0.036621 | -0.15106 | -0.086975 | 0.068665 | 0.15564 | -0.10986 | 0.11902 | 0.19226 | 0.068665 | 0.20599 | 120.8817 | -0.27466 | -0.50354 | 121.1975 | 121.0739 | 121.0098 | 0.19226 | 0.12817 | 121.051 | -0.19226 | -0.22888 | 121.3531 | 121.3669 | 121.2296 | 0.31586 | 0.17853 | 0.31586 | 0.1236 | 0.30212 | 0.22888 | 0.35248 | 0.2655 | 121.2341 | 121.3165 | -0.62714 | -0.45776 | 121.0052 | 121.2799 | 120.9961 | 121.2296
1839.125 | 121.6187 | -121.1929 | 0.37994 | 0.0034333 | -0.055918 | 0.013403 | 0.030666 | 0.0058725 | -0.0049241 | 0.0030718 | 0.001648 | 0.014315 | 0.020568 | 0.015112 | -0.00089293 | 0.0073828 | 0.0013714 | -0.09613 | 0.16479 | -0.21515 | -0.14191 | 0.041199 | -0.11444 | -0.054932 | 0.013733 | 0.19226 | -0.11902 | 0.022888 | 0.10986 | 0.004578 | 0.15564 | 120.9778 | -0.21515 | -0.52185 | 121.2341 | 121.138 | 121.0785 | 0.16022 | 0.10071 | 121.0739 | -0.18768 | -0.35706 | 121.3028 | 121.3486 | 121.1975 | 0.27466 | 0.1236 | 0.25635 | 0.073242 | 0.22888 | 0.14191 | 0.37994 | 0.31128 | 121.3577 | 121.3852 | -0.59509 | -0.49896 | 121.051 | 121.2158 | 121.0968 | 121.2067
1840.8906 | 121.6415 | -121.2112 | 0.37079 | 0.0034333 | -0.059336 | 0.014257 | 0.027889 | 0.0062997 | -0.0036423 | -0.00034615 | 0.0046998 | 0.011965 | 0.02014 | 0.015112 | -0.0030291 | 0.008451 | 0.0030804 | -0.068665 | 0.15564 | -0.19684 | -0.050354 | 0.13275 | 0.004578 | 0.036621 | 0.054932 | 0.14648 | -0.11444 | 0.050354 | 0.17853 | 0.068665 | 0.1831 | 121.0144 | -0.21515 | -0.42114 | 121.344 | 121.2479 | 121.2158 | 0.23346 | 0.20142 | 121.0968 | -0.2243 | -0.32043 | 121.3898 | 121.3943 | 121.2799 | 0.29755 | 0.18311 | 0.32959 | 0.14648 | 0.29297 | 0.16479 | 0.35248 | 0.26093 | 121.3669 | 121.3577 | -0.56763 | -0.48523 | 121.1609 | 121.2616 | 121.1426 | 121.2662
1842.6406 | 121.582 | -121.2341 | 0.37537 | 0.0034333 | -0.059763 | 0.01148 | 0.029811 | 0.0028817 | -0.0030015 | 0.0017902 | 0.001648 | 0.016451 | 0.021209 | 0.013403 | 0.0014569 | 0.0063148 | -0.0024738 | -0.10986 | 0.15564 | -0.21973 | -0.17395 | 0.013733 | -0.14191 | -0.091553 | -0.013733 | 0.18768 | -0.1236 | 0.018311 | 0.086975 | -0.041199 | 0.10529 | 121.0144 | -0.21973 | -0.54932 | 121.2479 | 121.1426 | 121.0922 | 0.12817 | 0.07782 | 121.1105 | -0.18768 | -0.35705 | 121.3211 | 121.3394 | 121.1929 | 0.22888 | 0.082397 | 0.23346 | 0.045777 | 0.21057 | 0.14191 | 0.37537 | 0.31128 | 121.3898 | 121.4218 | -0.59509 | -0.49896 | 121.0602 | 121.2524 | 121.1243 | 121.2204
1844.3281 | 121.6644 | -121.2158 | 0.3479 | -0.011826 | -0.060404 | 0.012975 | 0.030452 | 0.0020273 | -0.0025741 | 0.0017902 | 0.0046998 | 0.013888 | 0.020354 | 0.022375 | 0.00017507 | 0.0065284 | 0.0028668 | -0.17853 | 0.11902 | -0.25177 | -0.17395 | 0.013733 | -0.13733 | -0.064087 | -0.013733 | 0.15106 | -0.10529 | 0.041199 | 0.15106 | 0.045776 | 0.17395 | 120.9641 | -0.22888 | -0.52185 | 121.2296 | 121.1517 | 121.0785 | 0.18768 | 0.11444 | 121.1105 | -0.19684 | -0.3067 | 121.3669 | 121.3898 | 121.2616 | 0.27924 | 0.15106 | 0.2655 | 0.07782 | 0.25635 | 0.14649 | 0.37079 | 0.25635 | 121.3348 | 121.3669 | -0.59967 | -0.45319 | 121.0419 | 121.257 | 121.0373 | 121.2021
1846.0781 | 121.6324 | -121.2616 | 0.37537 | 0.011063 | -0.0572 | 0.013616 | 0.028957 | 0.0013863 | -0.0030015 | 8.125e-05 | 0.0046998 | 0.014315 | 0.023558 | 0.011907 | -0.0021747 | 0.006742 | 0.002226 | -0.09613 | 0.21515 | -0.2243 | -0.14191 | 0.045776 | -0.10986 | -0.045776 | -0.009155 | 0.1831 | -0.14191 | 0.022888 | 0.1236 | 0 | 0.15106 | 121.0373 | -0.16022 | -0.51727 | 121.3074 | 121.2158 | 121.1517 | 0.17853 | 0.11444 | 121.1197 | -0.19226 | -0.35248 | 121.3852 | 121.4127 | 121.2616 | 0.29297 | 0.14191 | 0.27008 | 0.082397 | 0.2655 | 0.16479 | 0.43945 | 0.32501 | 121.4767 | 121.4447 | -0.59967 | -0.51727 | 121.1197 | 121.2845 | 121.1655 | 121.2524
1847.8281 | 121.6827 | -121.2708 | 0.35706 | 0.0034333 | -0.05955 | 0.01383 | 0.028743 | 0.0043771 | -0.0023605 | 0.0017902 | -0.0014038 | 0.014101 | 0.021849 | 0.022802 | -0.00025213 | 0.0075964 | 0.00094419 | -0.17853 | 0.10071 | -0.24261 | -0.16937 | 0.022888 | -0.13733 | -0.064087 | -0.018311 | 0.16479 | -0.12817 | 0.022888 | 0.12817 | 0.018311 | 0.16022 | 121.0281 | -0.25635 | -0.52643 | 121.2936 | 121.2067 | 121.1334 | 0.17853 | 0.10529 | 121.1426 | -0.19226 | -0.33417 | 121.3989 | 121.431 | 121.2891 | 0.28839 | 0.14649 | 0.2655 | 0.073242 | 0.25635 | 0.15106 | 0.34332 | 0.29297 | 121.3715 | 121.4355 | -0.59967 | -0.48523 | 121.1014 | 121.2936 | 121.0922 | 121.2524
1849.5156 | 121.7422 | -121.2616 | 0.31586 | 0.0034333 | -0.059122 | 0.012548 | 0.031093 | 0.0075815 | -0.0017197 | 0.0013628 | 0.001648 | 0.015169 | 0.02249 | 0.014471 | 0.0031659 | 0.0082374 | -0.0035418 | -0.17395 | 0.059509 | -0.29297 | -0.17395 | 0.018311 | -0.16022 | -0.07782 | 0.059509 | 0.17395 | -0.1236 | 0.11444 | 0.16937 | 0.068665 | 0.21973 | 120.9686 | -0.25635 | -0.48981 | 121.2799 | 121.1838 | 121.1014 | 0.21515 | 0.13275 | 121.138 | -0.14191 | -0.20142 | 121.431 | 121.4813 | 121.3303 | 0.34332 | 0.19226 | 0.31128 | 0.11902 | 0.29297 | 0.23804 | 0.35248 | 0.29755 | 121.3211 | 121.4355 | -0.60883 | -0.43945 | 121.0876 | 121.376 | 121.0876 | 121.3211
1851.2031 | 121.6324 | -121.312 | 0.34332 | 0.018692 | -0.058481 | 0.012335 | 0.033656 | 0.0052315 | -0.0040695 | 0.00050845 | 0.001648 | 0.014315 | 0.023345 | 0.018316 | -0.00025213 | 0.0080236 | 0.00030339 | -0.20599 | 0.10986 | -0.31586 | -0.27466 | -0.091553 | -0.25635 | -0.16937 | -0.07782 | 0.20142 | -0.13733 | -0.022888 | 0.041199 | -0.059509 | 0.10986 | 120.9961 | -0.23346 | -0.61798 | 121.2204 | 121.1426 | 121.0556 | 0.14648 | 0.059509 | 121.1746 | -0.14191 | -0.36621 | 121.3531 | 121.4218 | 121.2524 | 0.24719 | 0.07782 | 0.2243 | 0.041199 | 0.17853 | 0.11444 | 0.42572 | 0.33875 | 121.4218 | 121.5134 | -0.65918 | -0.48065 | 121.0373 | 121.2891 | 121.106 | 121.2341
1852.9531 | 121.7422 | -121.3211 | 0.33417 | -0.011826 | -0.061472 | 0.01148 | 0.02917 | 0.0022409 | -0.0027877 | 8.125e-05 | 0.0046998 | 0.012179 | 0.019927 | 0.025579 | 0.00060247 | 0.0054602 | -0.00055121 | -0.17853 | 0.10529 | -0.25635 | -0.16937 | 0.018311 | -0.13275 | -0.050354 | -0.013733 | 0.16479 | -0.14648 | 0.041199 | 0.15106 | 0.050354 | 0.16022 | 121.0648 | -0.22888 | -0.50354 | 121.3394 | 121.2708 | 121.1884 | 0.20599 | 0.1236 | 121.1746 | -0.16937 | -0.29297 | 121.4722 | 121.4813 | 121.3715 | 0.3067 | 0.19684 | 0.27466 | 0.086975 | 0.29755 | 0.18768 | 0.36163 | 0.31128 | 121.4264 | 121.4859 | -0.59052 | -0.48065 | 121.1517 | 121.3623 | 121.1426 | 121.3074
1854.7031 | 121.6461 | -121.3577 | 0.36163 | 0.0034333 | -0.058909 | 0.01148 | 0.031093 | 0.0043771 | -0.0030015 | 0.0013628 | 0.0077514 | 0.016024 | 0.022917 | 0.020025 | 0.0023115 | 0.0063148 | -0.0026874 | -0.17395 | 0.14648 | -0.26093 | -0.2243 | -0.059509 | -0.2243 | -0.14648 | -0.082397 | 0.20599 | -0.12817 | -0.022888 | 0.045776 | -0.07782 | 0.11444 | 121.0968 | -0.21515 | -0.58594 | 121.2982 | 121.2112 | 121.1334 | 0.11444 | 0.036621 | 121.2296 | -0.15564 | -0.38452 | 121.4035 | 121.4722 | 121.2799 | 0.24262 | 0.050354 | 0.20142 | 0.036621 | 0.17395 | 0.10529 | 0.40741 | 0.33417 | 121.5042 | 121.5637 | -0.62256 | -0.48981 | 121.1334 | 121.3348 | 121.1838 | 121.2753
1856.4531 | 121.7239 | -121.3531 | 0.32501 | -0.0041962 | -0.061899 | 0.012548 | 0.030025 | 0.0030953 | -0.0055649 | -0.00098695 | 0.0046998 | 0.013674 | 0.02014 | 0.023016 | -0.00025213 | 0.0093054 | 0.002226 | -0.19684 | 0.10071 | -0.24719 | -0.17853 | 0.004578 | -0.12817 | -0.054932 | -0.022888 | 0.15106 | -0.11902 | 0.036621 | 0.12817 | 0.009155 | 0.15564 | 121.106 | -0.2243 | -0.50354 | 121.3577 | 121.2982 | 121.225 | 0.19226 | 0.11902 | 121.2341 | -0.17395 | -0.28839 | 121.4813 | 121.5088 | 121.3623 | 0.27466 | 0.12817 | 0.25177 | 0.068664 | 0.24719 | 0.15564 | 0.3479 | 0.27008 | 121.4539 | 121.5042 | -0.5722 | -0.44403 | 121.1746 | 121.3898 | 121.1563 | 121.3303
1858.1406 | 121.756 | -121.3348 | 0.32044 | 0.011063 | -0.059977 | 0.012975 | 0.030238 | 0.0037363 | -0.00086509 | 8.125e-05 | 0.001648 | 0.013674 | 0.023131 | 0.019811 | -0.00067933 | 0.0073828 | 0.003294 | -0.16479 | 0.050354 | -0.25635 | -0.15106 | 0.059509 | -0.11902 | -0.059509 | 0.054932 | 0.15106 | -0.13275 | 0.082397 | 0.15564 | 0.050354 | 0.17395 | 121.0785 | -0.27008 | -0.4715 | 121.3943 | 121.2753 | 121.2158 | 0.19684 | 0.13733 | 121.2021 | -0.16937 | -0.23804 | 121.4905 | 121.5088 | 121.3852 | 0.3067 | 0.18311 | 0.31586 | 0.10529 | 0.28839 | 0.21515 | 0.3067 | 0.28381 | 121.3852 | 121.4859 | -0.57678 | -0.45319 | 121.1838 | 121.4172 | 121.17 | 121.3898
1859.8906 | 121.7331 | -121.3852 | 0.35706 | 0.0034333 | -0.058909 | 0.013189 | 0.030025 | 0.0024545 | -0.0044967 | -0.00034615 | 0.001648 | 0.015597 | 0.020781 | 0.01917 | 0.00017507 | 0.0063148 | 0.00051699 | -0.10529 | 0.21515 | -0.20599 | -0.14191 | 0.032043 | -0.082397 | -0.032043 | -0.045776 | 0.19226 | -0.14191 | 0.009155 | 0.10986 | 0 | 0.14648 | 121.1792 | -0.14191 | -0.49896 | 121.4172 | 121.3531 | 121.3028 | 0.17395 | 0.1236 | 121.2433 | -0.16479 | -0.3479 | 121.4951 | 121.5317 | 121.3852 | 0.28839 | 0.14191 | 0.23804 | 0.064087 | 0.25177 | 0.15106 | 0.42114 | 0.33417 | 121.6003 | 121.5775 | -0.56305 | -0.49896 | 121.2433 | 121.3943 | 121.2799 | 121.3394
1861.6406 | 121.8018 | -121.3531 | 0.29297 | -0.0041962 | -0.057627 | 0.012975 | 0.025539 | 0.0035227 | -0.0030015 | 0.00050845 | 0.0046998 | 0.015383 | 0.0195 | 0.017675 | 0.0016705 | 0.009519 | 0.0024396 | -0.16479 | 0.045776 | -0.27466 | -0.15106 | 0.054932 | -0.12817 | -0.059509 | 0.07782 | 0.14648 | -0.10529 | 0.086975 | 0.1831 | 0.068665 | 0.20599 | 121.0785 | -0.24719 | -0.44403 | 121.4081 | 121.2936 | 121.225 | 0.21515 | 0.14648 | 121.2479 | -0.14648 | -0.20599 | 121.5363 | 121.5591 | 121.4218 | 0.31128 | 0.17395 | 0.32959 | 0.1236 | 0.28839 | 0.19226 | 0.32043 | 0.25177 | 121.3989 | 121.4996 | -0.56763 | -0.39825 | 121.2021 | 121.4401 | 121.1884 | 121.431
1863.4062 | 121.7834 | -121.4035 | 0.32501 | -0.011826 | -0.058268 | 0.012335 | 0.028529 | 0.0024545 | -0.0040695 | -0.0016278 | 0.001648 | 0.01346 | 0.020995 | 0.017675 | -0.0034563 | 0.0065284 | 0.00094419 | -0.07782 | 0.15564 | -0.18768 | -0.073242 | 0.12817 | -0.004578 | 0.022888 | 0.027466 | 0.17395 | -0.11444 | 0.032043 | 0.16022 | 0.054932 | 0.16022 | 121.2158 | -0.16937 | -0.39825 | 121.5317 | 121.4264 | 121.3989 | 0.21057 | 0.1831 | 121.2891 | -0.15106 | -0.29297 | 121.5637 | 121.5637 | 121.4584 | 0.27466 | 0.16937 | 0.31586 | 0.11444 | 0.27466 | 0.14648 | 0.34332 | 0.28839 | 121.5591 | 121.5775 | -0.5127 | -0.43945 | 121.3303 | 121.4355 | 121.3257 | 121.431
1865.1094 | 121.7377 | -121.4447 | 0.33875 | 0.0034333 | -0.061899 | 0.010198 | 0.032161 | 0.0058725 | -0.0019333 | 0.0026446 | 0.0046998 | 0.016878 | 0.020568 | 0.0082758 | -0.0034563 | 0.006742 | 8.9786e-05 | -0.11444 | 0.21515 | -0.20142 | -0.15564 | 0.013733 | -0.10529 | -0.041199 | -0.086975 | 0.1831 | -0.16022 | -0.013733 | 0.091553 | -0.036621 | 0.1236 | 121.2433 | -0.1236 | -0.49439 | 121.4584 | 121.4035 | 121.3394 | 0.16022 | 0.09613 | 121.2845 | -0.15564 | -0.35248 | 121.5363 | 121.5683 | 121.4081 | 0.28381 | 0.1236 | 0.21515 | 0.045776 | 0.25177 | 0.14648 | 0.41657 | 0.34332 | 121.6599 | 121.6278 | -0.54016 | -0.49896 | 121.2891 | 121.431 | 121.3303 | 121.3577
1866.8594 | 121.7102 | -121.4447 | 0.3479 | 0.011063 | -0.060831 | 0.012121 | 0.029811 | 0.0018137 | -0.0036423 | 8.125e-05 | 0.0077514 | 0.013888 | 0.019713 | 0.012975 | -0.0026019 | 0.0037512 | 0.00051699 | -0.14191 | 0.20599 | -0.20599 | -0.16479 | 0.036621 | -0.091553 | -0.009155 | -0.086975 | 0.18768 | -0.16022 | -0.036621 | 0.07782 | -0.036621 | 0.10071 | 121.2387 | -0.14191 | -0.5127 | 121.4813 | 121.4355 | 121.3531 | 0.19684 | 0.11444 | 121.2845 | -0.16022 | -0.38452 | 121.5225 | 121.5454 | 121.4081 | 0.26093 | 0.1236 | 0.24262 | 0.041199 | 0.23804 | 0.1236 | 0.41199 | 0.3479 | 121.6507 | 121.6324 | -0.55389 | -0.50812 | 121.2799 | 121.4081 | 121.3028 | 121.3577
1868.5469 | 121.8475 | -121.3898 | 0.3067 | 0.026321 | -0.05955 | 0.011694 | 0.027889 | 0.0030953 | -0.0042831 | -0.00055975 | 0.001648 | 0.011965 | 0.0195 | 0.025366 | -0.00089293 | 0.00781 | -0.0020464 | -0.10071 | 0.13275 | -0.18768 | -0.064087 | 0.16022 | 0 | 0.054932 | 0.064087 | 0.14648 | -0.11902 | 0.09613 | 0.21515 | 0.10986 | 0.18768 | 121.2021 | -0.17395 | -0.37079 | 121.55 | 121.4447 | 121.3898 | 0.24261 | 0.18768 | 121.2708 | -0.16022 | -0.21057 | 121.6049 | 121.5775 | 121.4996 | 0.3067 | 0.22888 | 0.3479 | 0.1236 | 0.33417 | 0.21515 | 0.32043 | 0.2655 | 121.5225 | 121.5363 | -0.49438 | -0.42572 | 121.3257 | 121.4859 | 121.2891 | 121.4539
1870.3125 | 121.7239 | -121.4722 | 0.32959 | -0.0041962 | -0.057841 | 0.014257 | 0.028957 | 0.0071541 | -0.0023605 | -0.00013235 | 0.001648 | 0.014315 | 0.021636 | 0.018743 | -0.00046573 | 0.006101 | 0.0017988 | -0.18768 | 0.13275 | -0.27924 | -0.24719 | -0.068665 | -0.2243 | -0.16022 | -0.10529 | 0.17395 | -0.14648 | -0.054932 | 0.045776 | -0.082397 | 0.10071 | 121.1929 | -0.19684 | -0.57678 | 121.4035 | 121.312 | 121.2479 | 0.11902 | 0.054932 | 121.3257 | -0.15564 | -0.38452 | 121.5179 | 121.5729 | 121.3898 | 0.24719 | 0.064087 | 0.21057 | 0.032044 | 0.19226 | 0.091552 | 0.41199 | 0.32043 | 121.6049 | 121.6461 | -0.60883 | -0.47607 | 121.225 | 121.4172 | 121.2845 | 121.3669
1872 | 121.8109 | -121.4539 | 0.31128 | 0.011063 | -0.060831 | 0.012121 | 0.031947 | 0.00010474 | -0.0055649 | -0.00077335 | 0.001648 | 0.016237 | 0.021209 | 0.01853 | 0.0016705 | 0.0039648 | -0.001192 | -0.11444 | 0.18768 | -0.21515 | -0.15106 | 0.045776 | -0.091553 | -0.032043 | 0 | 0.16937 | -0.15106 | 0.022888 | 0.10986 | 0.004578 | 0.14191 | 121.2387 | -0.1236 | -0.46234 | 121.4996 | 121.4218 | 121.3623 | 0.18311 | 0.1236 | 121.3028 | -0.14191 | -0.28839 | 121.5637 | 121.5958 | 121.4584 | 0.29297 | 0.15564 | 0.26093 | 0.064087 | 0.26093 | 0.17395 | 0.40283 | 0.32044 | 121.6415 | 121.6232 | -0.52643 | -0.46234 | 121.3028 | 121.4767 | 121.3394 | 121.4539
1873.7344 | 121.7514 | -121.4813 | 0.31586 | 0.0034333 | -0.05955 | 0.014044 | 0.030238 | 0.0015999 | -0.0021469 | 0.0011492 | 0.0046998 | 0.014742 | 0.024413 | 0.01618 | 0.0027387 | 0.0090918 | -0.0022602 | -0.21057 | 0.12817 | -0.29297 | -0.26093 | -0.10986 | -0.23804 | -0.17395 | -0.10986 | 0.19684 | -0.15564 | -0.027466 | 0.036621 | -0.082397 | 0.10529 | 121.1884 | -0.18768 | -0.57678 | 121.3715 | 121.3074 | 121.2433 | 0.11902 | 0.054932 | 121.3257 | -0.11902 | -0.34332 | 121.5179 | 121.5866 | 121.3989 | 0.26093 | 0.073243 | 0.18311 | 0.032044 | 0.19226 | 0.12817 | 0.42114 | 0.35248 | 121.6095 | 121.6782 | -0.60883 | -0.4715 | 121.2204 | 121.4539 | 121.2708 | 121.3715
1875.5 | 121.7697 | -121.4859 | 0.32501 | 0.0034333 | -0.061045 | 0.011694 | 0.030452 | 0.0018137 | -0.0040695 | -0.00013235 | 0.001648 | 0.014101 | 0.0195 | 0.0074212 | -0.0032427 | 0.0058874 | 0.0045758 | -0.14191 | 0.18768 | -0.21515 | -0.17395 | 0.032043 | -0.091553 | -0.022888 | -0.091553 | 0.20142 | -0.15106 | -0.032043 | 0.054932 | -0.032043 | 0.091553 | 121.2708 | -0.13733 | -0.49896 | 121.5179 | 121.463 | 121.3943 | 0.19226 | 0.1236 | 121.3348 | -0.1236 | -0.35706 | 121.5408 | 121.5775 | 121.4539 | 0.24261 | 0.11902 | 0.24719 | 0.041199 | 0.20599 | 0.11902 | 0.40283 | 0.35248 | 121.6736 | 121.6873 | -0.54016 | -0.47607 | 121.312 | 121.4539 | 121.344 | 121.3943
1877.1875 | 121.8475 | -121.4584 | 0.31128 | -0.0041962 | -0.061472 | 0.012121 | 0.02682 | 0.0058725 | -0.0032151 | 0.0011492 | 0.001648 | 0.011324 | 0.020568 | 0.013403 | 0.00017507 | 0.006742 | -0.0026874 | -0.18768 | 0.10071 | -0.23346 | -0.18768 | 0.022888 | -0.13275 | -0.068665 | -0.032043 | 0.15106 | -0.13733 | 0.041199 | 0.12817 | 0.022888 | 0.15106 | 121.225 | -0.21057 | -0.49896 | 121.4813 | 121.3898 | 121.3257 | 0.16479 | 0.10071 | 121.3211 | -0.16022 | -0.27008 | 121.5866 | 121.6095 | 121.4813 | 0.28839 | 0.16022 | 0.25635 | 0.045776 | 0.2655 | 0.17853 | 0.33417 | 0.28839 | 121.5591 | 121.6095 | -0.54474 | -0.44861 | 121.2708 | 121.4996 | 121.2708 | 121.4264
1878.9219 | 121.9254 | -121.4767 | 0.30212 | -0.0041962 | -0.060618 | 0.0099848 | 0.02917 | -0.00010886 | -0.0019333 | -0.00034615 | 0.0046998 | 0.013247 | 0.019072 | 0.01618 | -0.00025213 | 0.0056738 | 0.00030339 | -0.091553 | 0.10529 | -0.1831 | -0.059509 | 0.16937 | -0.004578 | 0.041199 | 0.091553 | 0.15106 | -0.09613 | 0.10071 | 0.21515 | 0.11444 | 0.20599 | 121.2936 | -0.19684 | -0.36163 | 121.6461 | 121.5179 | 121.4722 | 0.2243 | 0.17853 | 121.3806 | -0.15106 | -0.20142 | 121.6919 | 121.6827 | 121.5912 | 0.30212 | 0.21057 | 0.35248 | 0.1236 | 0.31128 | 0.19684 | 0.28839 | 0.24719 | 121.582 | 121.6278 | -0.48523 | -0.39825 | 121.4172 | 121.5775 | 121.3852 | 121.5683
1880.6719 | 121.8018 | -121.5225 | 0.32044 | 0.0034333 | -0.0572 | 0.013403 | 0.032161 | 0.0030953 | -0.0044967 | 0.0013628 | 0.0046998 | 0.013888 | 0.021636 | 0.019811 | 0.0025251 | 0.00781 | -0.00033761 | -0.17395 | 0.13275 | -0.26093 | -0.24719 | -0.064087 | -0.21515 | -0.14648 | -0.10529 | 0.19684 | -0.14191 | -0.018311 | 0.032043 | -0.086975 | 0.086975 | 121.2616 | -0.18768 | -0.56763 | 121.4584 | 121.376 | 121.3074 | 0.11444 | 0.045776 | 121.3806 | -0.1236 | -0.33875 | 121.5546 | 121.6095 | 121.4355 | 0.22888 | 0.054932 | 0.19684 | 0.013733 | 0.17395 | 0.1236 | 0.39368 | 0.33875 | 121.6553 | 121.7194 | -0.58136 | -0.46234 | 121.2753 | 121.5042 | 121.3486 | 121.4172
1882.3594 | 121.8155 | -121.5408 | 0.33875 | -0.0041962 | -0.061686 | 0.010198 | 0.02917 | 0.0018137 | -0.0036423 | 8.125e-05 | -0.0044556 | 0.01581 | 0.020568 | 0.008703 | -0.0026019 | 0.006101 | -0.0014056 | -0.11902 | 0.21515 | -0.19684 | -0.15106 | 0.041199 | -0.068665 | -0.032043 | -0.10529 | 0.18768 | -0.14648 | -0.027466 | 0.059509 | -0.054932 | 0.091553 | 121.344 | -0.1236 | -0.48981 | 121.582 | 121.5088 | 121.4722 | 0.1648 | 0.12817 | 121.3943 | -0.15106 | -0.36621 | 121.6003 | 121.6324 | 121.4859 | 0.23804 | 0.091552 | 0.23804 | 0.045776 | 0.20599 | 0.11902 | 0.41199 | 0.33417 | 121.756 | 121.7285 | -0.53558 | -0.48523 | 121.3898 | 121.5134 | 121.4218 | 121.4355
1884.1094 | 121.8109 | -121.5134 | 0.33875 | 0.011063 | -0.056345 | 0.011694 | 0.03387 | 0.0045907 | -0.0036423 | 0.0039264 | 0.0046998 | 0.017306 | 0.022277 | 0.011266 | -0.0011065 | 0.0058874 | -0.0018328 | -0.14191 | 0.14648 | -0.23804 | -0.19684 | -0.032043 | -0.19226 | -0.12817 | -0.059509 | 0.18768 | -0.15106 | -0.013733 | 0.045776 | -0.073242 | 0.10529 | 121.2753 | -0.19226 | -0.53558 | 121.4813 | 121.3852 | 121.3211 | 0.10986 | 0.045776 | 121.3623 | -0.15106 | -0.35248 | 121.5591 | 121.6187 | 121.4401 | 0.25635 | 0.07782 | 0.20599 | 0.041199 | 0.19684 | 0.13733 | 0.38452 | 0.33874 | 121.6599 | 121.7011 | -0.57678 | -0.48981 | 121.3165 | 121.4996 | 121.3715 | 121.4539
1885.875 | 121.9528 | -121.4813 | 0.29297 | 0.0034333 | -0.059763 | 0.01148 | 0.029811 | 0.0050179 | -0.0040695 | -0.00055975 | 0.0046998 | 0.012392 | 0.02014 | 0.019598 | -3.8532e-05 | 0.006101 | -0.0024738 | -0.073242 | 0.12817 | -0.17853 | -0.059509 | 0.17395 | 0.013733 | 0.054932 | 0.064087 | 0.15564 | -0.10529 | 0.086975 | 0.21973 | 0.10529 | 0.21057 | 121.3028 | -0.16479 | -0.35248 | 121.6553 | 121.5363 | 121.4951 | 0.23346 | 0.19226 | 121.376 | -0.13733 | -0.20599 | 121.7011 | 121.6919 | 121.5866 | 0.31586 | 0.21057 | 0.35248 | 0.11902 | 0.32501 | 0.19226 | 0.3067 | 0.26093 | 121.6095 | 121.637 | -0.4715 | -0.39825 | 121.4218 | 121.5683 | 121.4081 | 121.5454
1888.9531 | 121.843 | -121.5729 | 0.33875 | -0.0041962 | -0.059122 | 0.014898 | 0.030452 | 0.0015999 | -0.0051377 | 0.0015764 | 0.0046998 | 0.013247 | 0.019927 | 0.013616 | -0.0028155 | 0.004392 | 0.0011578 | -0.086975 | 0.1831 | -0.18768 | -0.13275 | 0.059509 | -0.073242 | -0.018311 | -0.068665 | 0.1831 | -0.13275 | -0.041199 | 0.073242 | -0.018311 | 0.091553 | 121.3852 | -0.15564 | -0.4715 | 121.6324 | 121.5546 | 121.4996 | 0.16937 | 0.11444 | 121.4401 | -0.15564 | -0.37994 | 121.6461 | 121.6644 | 121.5546 | 0.2243 | 0.11444 | 0.24719 | 0.054932 | 0.20599 | 0.091552 | 0.37079 | 0.31586 | 121.756 | 121.756 | -0.52643 | -0.4715 | 121.4401 | 121.5317 | 121.4859 | 121.5042
1892.9375 | 121.9803 | -121.55 | 0.3067 | -0.0041962 | -0.060404 | 0.012548 | 0.031093 | 0.0062997 | -0.0019333 | 0.0011492 | 0.001648 | 0.01346 | 0.021849 | 0.020452 | 0.00060247 | 0.0056738 | 0.0024396 | -0.082397 | 0.13275 | -0.18768 | -0.050354 | 0.17853 | 0 | 0.045776 | 0.082397 | 0.13733 | -0.11444 | 0.091553 | 0.21515 | 0.10071 | 0.20599 | 121.3623 | -0.17395 | -0.35706 | 121.7285 | 121.5958 | 121.55 | 0.23346 | 0.18768 | 121.4355 | -0.16937 | -0.21515 | 121.7651 | 121.756 | 121.6507 | 0.32044 | 0.21515 | 0.36621 | 0.13733 | 0.32959 | 0.20599 | 0.32043 | 0.25177 | 121.6827 | 121.6873 | -0.49438 | -0.42114 | 121.4996 | 121.6415 | 121.4676 | 121.6324
1899.2812 | 121.8933 | -121.5866 | 0.31586 | 0.0034333 | -0.059122 | 0.012121 | 0.03152 | 0.0043771 | -0.0030015 | -0.002696 | 0.001648 | 0.015597 | 0.021209 | 0.014684 | -3.8532e-05 | 0.0069556 | 0.0026532 | -0.12817 | 0.16022 | -0.23804 | -0.21057 | -0.022888 | -0.20142 | -0.12817 | -0.045776 | 0.1831 | -0.11902 | -0.018311 | 0.054932 | -0.054932 | 0.09613 | 121.3486 | -0.15564 | -0.52643 | 121.5637 | 121.4584 | 121.3852 | 0.10986 | 0.036621 | 121.4676 | -0.13275 | -0.33417 | 121.6415 | 121.6827 | 121.5317 | 0.21515 | 0.064087 | 0.21515 | 0.027466 | 0.17395 | 0.10071 | 0.39825 | 0.30212 | 121.7468 | 121.7697 | -0.55389 | -0.43488 | 121.376 | 121.5683 | 121.4584 | 121.5408
1900.9844 | 121.9345 | -121.6049 | 0.32959 | 0.011063 | -0.058695 | 0.011907 | 0.030238 | 0.0062997 | -0.0047103 | 0.002431 | 0.001648 | 0.014956 | 0.021209 | 0.010839 | -0.00089293 | 0.00781 | -0.001192 | -0.11444 | 0.17853 | -0.21973 | -0.16479 | 0.036621 | -0.12817 | -0.050354 | 0 | 0.18768 | -0.13275 | 0.036621 | 0.1236 | 0.018311 | 0.16022 | 121.3852 | -0.15106 | -0.49438 | 121.6415 | 121.5546 | 121.4767 | 0.16937 | 0.091553 | 121.4722 | -0.14191 | -0.29297 | 121.7285 | 121.7651 | 121.6232 | 0.29297 | 0.15106 | 0.25635 | 0.054932 | 0.25635 | 0.16937 | 0.39826 | 0.32043 | 121.7834 | 121.7926 | -0.54932 | -0.46234 | 121.4401 | 121.6415 | 121.4905 | 121.6049
1902.75 | 122.0169 | -121.582 | 0.29297 | 0.011063 | -0.058481 | 0.012121 | 0.030452 | 0.0037363 | -0.0012925 | 8.125e-05 | 0.001648 | 0.014101 | 0.021849 | 0.020025 | 0.0025251 | 0.0086646 | 0.001585 | -0.21057 | 0.091553 | -0.29297 | -0.21973 | -0.018311 | -0.1831 | -0.10529 | 0.018311 | 0.16937 | -0.10071 | 0.10071 | 0.16479 | 0.068665 | 0.19684 | 121.2891 | -0.20142 | -0.5127 | 121.5637 | 121.4767 | 121.3989 | 0.18768 | 0.10986 | 121.4813 | -0.1236 | -0.19226 | 121.7468 | 121.7789 | 121.6507 | 0.29755 | 0.16937 | 0.27466 | 0.073242 | 0.2655 | 0.20142 | 0.38452 | 0.27008 | 121.6736 | 121.7514 | -0.58594 | -0.39368 | 121.3623 | 121.6827 | 121.3715 | 121.6003
1904.4375 | 121.9208 | -121.6232 | 0.32044 | -0.0041962 | -0.058054 | 0.01148 | 0.030879 | 0.0037363 | -0.0038559 | 0.00093565 | 0.001648 | 0.014101 | 0.019072 | 0.010412 | 0.00060247 | 0.0071692 | -0.0050372 | -0.11902 | 0.16479 | -0.23804 | -0.18768 | 0.018311 | -0.12817 | -0.07782 | -0.022888 | 0.17853 | -0.12817 | 0.004578 | 0.07782 | -0.027466 | 0.12817 | 121.3852 | -0.15564 | -0.50812 | 121.6415 | 121.5454 | 121.4951 | 0.16022 | 0.10986 | 121.4951 | -0.14191 | -0.31586 | 121.7011 | 121.7514 | 121.5958 | 0.25635 | 0.10071 | 0.25635 | 0.050354 | 0.20599 | 0.13275 | 0.40283 | 0.3067 | 121.788 | 121.8018 | -0.55847 | -0.44861 | 121.4355 | 121.6278 | 121.5042 | 121.6003
1906.125 | 121.9162 | -121.637 | 0.33417 | -0.011826 | -0.061259 | 0.011907 | 0.027675 | 0.0037363 | -0.0047103 | 0.0013628 | -0.0014038 | 0.01346 | 0.02014 | 0.012335 | -0.0013201 | 0.0065284 | 0.0011578 | -0.073242 | 0.20599 | -0.17853 | -0.1236 | 0.082397 | -0.054932 | -0.022888 | -0.045776 | 0.1831 | -0.14648 | -0.022888 | 0.073242 | -0.027466 | 0.10529 | 121.4584 | -0.12817 | -0.45776 | 121.7194 | 121.6141 | 121.582 | 0.15564 | 0.1236 | 121.4905 | -0.15106 | -0.35706 | 121.7102 | 121.7422 | 121.6095 | 0.25177 | 0.11902 | 0.26092 | 0.054932 | 0.21973 | 0.1236 | 0.38452 | 0.32959 | 121.843 | 121.8201 | -0.5127 | -0.48065 | 121.5134 | 121.6141 | 121.5637 | 121.5912
1907.8906 | 122.049 | -121.5958 | 0.29297 | 0.011063 | -0.061472 | 0.011053 | 0.027675 | 0.0039499 | -0.0019333 | 0.0026446 | 0.0046998 | 0.014101 | 0.020568 | 0.02152 | -0.0011065 | 0.006742 | 0.0011578 | -0.073242 | 0.15106 | -0.1831 | -0.068665 | 0.13733 | 0.004578 | 0.041199 | 0.064087 | 0.16022 | -0.1236 | 0.086975 | 0.20142 | 0.10529 | 0.19226 | 121.4127 | -0.14191 | -0.36163 | 121.7331 | 121.637 | 121.6003 | 0.2243 | 0.18768 | 121.4722 | -0.13275 | -0.20599 | 121.7972 | 121.788 | 121.7011 | 0.31586 | 0.22888 | 0.32043 | 0.11444 | 0.32501 | 0.21057 | 0.33417 | 0.28381 | 121.7468 | 121.756 | -0.47607 | -0.41656 | 121.5271 | 121.6827 | 121.5225 | 121.6599
1909.6406 | 121.9299 | -121.6507 | 0.32959 | 0.0034333 | -0.057413 | 0.014257 | 0.031734 | 0.0077951 | -0.0038559 | 0.0015764 | 0.0077514 | 0.017733 | 0.020995 | 0.016821 | -0.00089293 | 0.005033 | 0.00051699 | -0.13275 | 0.13733 | -0.20599 | -0.19226 | -0.013733 | -0.17853 | -0.11902 | -0.064087 | 0.18768 | -0.14191 | -0.018311 | 0.041199 | -0.064087 | 0.09613 | 121.4447 | -0.19226 | -0.52185 | 121.637 | 121.5317 | 121.4722 | 0.086975 | 0.027466 | 121.5088 | -0.14191 | -0.3479 | 121.6919 | 121.7468 | 121.5866 | 0.23804 | 0.07782 | 0.19226 | 0.013733 | 0.18311 | 0.1236 | 0.34332 | 0.32959 | 121.788 | 121.8384 | -0.53558 | -0.4715 | 121.4584 | 121.6324 | 121.5179 | 121.5866
1911.3906 | 122.0764 | -121.6095 | 0.28381 | 0.0034333 | -0.059977 | 0.013403 | 0.027034 | 0.00053194 | -0.0030015 | 0.0017902 | 0.001648 | 0.012179 | 0.020781 | 0.017675 | -0.0011065 | 0.0080236 | 0.003935 | -0.082397 | 0.1236 | -0.18768 | -0.059509 | 0.17395 | 0.009155 | 0.050354 | 0.082397 | 0.13733 | -0.11444 | 0.082397 | 0.20142 | 0.10529 | 0.21057 | 121.4218 | -0.16022 | -0.34332 | 121.7834 | 121.6599 | 121.6187 | 0.23804 | 0.19684 | 121.4951 | -0.14648 | -0.20142 | 121.8109 | 121.8201 | 121.7148 | 0.32501 | 0.21973 | 0.36163 | 0.12817 | 0.31586 | 0.19684 | 0.31128 | 0.25177 | 121.7331 | 121.7468 | -0.4715 | -0.39825 | 121.55 | 121.6919 | 121.5271 | 121.6919
1913.0781 | 122.0947 | -121.582 | 0.28839 | 0.011063 | -0.061259 | 0.012335 | 0.030025 | 0.0041635 | -0.0034287 | -0.00098695 | 0.0046998 | 0.01282 | 0.018645 | 0.010839 | -0.0023883 | 0.0065284 | 0.0035078 | -0.10071 | 0.12817 | -0.21057 | -0.091553 | 0.12817 | -0.032043 | 0.041199 | 0.054932 | 0.15564 | -0.11444 | 0.09613 | 0.21515 | 0.11444 | 0.20142 | 121.3715 | -0.16022 | -0.37994 | 121.7102 | 121.6232 | 121.55 | 0.25177 | 0.17853 | 121.4676 | -0.13275 | -0.19226 | 121.7972 | 121.7834 | 121.6965 | 0.31586 | 0.22888 | 0.33875 | 0.11902 | 0.32959 | 0.21057 | 0.33875 | 0.27008 | 121.7102 | 121.7377 | -0.49896 | -0.40283 | 121.4905 | 121.6782 | 121.4813 | 121.637
1914.8125 | 122.0901 | -121.6141 | 0.27924 | 0.0034333 | -0.061259 | 0.012975 | 0.029811 | 0.0037363 | -0.0042831 | -0.00077335 | 0.001648 | 0.011538 | 0.02014 | 0.017889 | -0.0021747 | 0.0048194 | 0.0041486 | -0.086975 | 0.12817 | -0.19226 | -0.068665 | 0.13275 | -0.027466 | 0.054932 | 0.11902 | 0.15106 | -0.11902 | 0.10071 | 0.2243 | 0.11444 | 0.22888 | 121.4218 | -0.15106 | -0.3479 | 121.7468 | 121.669 | 121.5866 | 0.24719 | 0.16479 | 121.4951 | -0.12817 | -0.17853 | 121.8384 | 121.843 | 121.7285 | 0.3479 | 0.23346 | 0.32501 | 0.1236 | 0.34332 | 0.21973 | 0.32044 | 0.27008 | 121.7422 | 121.7651 | -0.4715 | -0.39825 | 121.5454 | 121.7148 | 121.5271 | 121.7331
1916.5781 | 122.0718 | -121.6278 | 0.32044 | -0.0041962 | -0.059763 | 0.012548 | 0.030238 | 0.0045907 | -0.0025741 | 0.0015764 | 0.001648 | 0.014529 | 0.020995 | 0.01917 | 0.0016705 | 0.006742 | -0.0033282 | -0.19684 | 0.11444 | -0.29755 | -0.23804 | -0.07782 | -0.24719 | -0.14648 | -0.018311 | 0.16479 | -0.13275 | 0.068665 | 0.13275 | 0.041199 | 0.1831 | 121.3303 | -0.20599 | -0.55847 | 121.55 | 121.4813 | 121.3806 | 0.15106 | 0.050354 | 121.4951 | -0.15564 | -0.25177 | 121.7606 | 121.8109 | 121.669 | 0.31586 | 0.17395 | 0.21973 | 0.059509 | 0.2655 | 0.20142 | 0.41199 | 0.29755 | 121.7422 | 121.7926 | -0.61798 | -0.45319 | 121.3898 | 121.6965 | 121.431 | 121.6095
1918.2656 | 121.9482 | -121.6827 | 0.34332 | 0.0034333 | -0.058054 | 0.013616 | 0.030452 | 0.0054453 | -0.0027877 | -0.0018414 | 0.001648 | 0.014101 | 0.020781 | 0.016821 | -0.00089293 | 0.0073828 | 0.00030339 | -0.16937 | 0.12817 | -0.24261 | -0.24261 | -0.07782 | -0.21973 | -0.16479 | -0.10529 | 0.16937 | -0.15106 | -0.041199 | 0.032043 | -0.09613 | 0.09613 | 121.4401 | -0.21515 | -0.58594 | 121.6049 | 121.5179 | 121.463 | 0.07782 | 0.022888 | 121.5317 | -0.17395 | -0.38452 | 121.7148 | 121.7789 | 121.5866 | 0.24719 | 0.054932 | 0.16479 | 0 | 0.18311 | 0.10986 | 0.37079 | 0.32044 | 121.8109 | 121.8521 | -0.58594 | -0.49438 | 121.4401 | 121.6415 | 121.5134 | 121.5775
1920.0156 | 122.0627 | -121.6827 | 0.31128 | 0.011063 | -0.060618 | 0.012762 | 0.029384 | 0.0043771 | -0.0034287 | -0.00034615 | 0.001648 | 0.012606 | 0.02014 | 0.020239 | -0.0030291 | 0.006742 | 0.0013714 | -0.068665 | 0.14648 | -0.18768 | -0.073242 | 0.14648 | 0 | 0.032043 | 0.041199 | 0.16022 | -0.1236 | 0.018311 | 0.15106 | 0.054932 | 0.16022 | 121.4951 | -0.16479 | -0.38452 | 121.8292 | 121.7148 | 121.6827 | 0.21973 | 0.18768 | 121.5591 | -0.15106 | -0.29297 | 121.8338 | 121.843 | 121.7377 | 0.28381 | 0.17853 | 0.33417 | 0.11444 | 0.27466 | 0.14191 | 0.33417 | 0.28381 | 121.8292 | 121.843 | -0.49896 | -0.43487 | 121.6095 | 121.701 | 121.6141 | 121.7239
1921.7656 | 122.1222 | -121.6553 | 0.29755 | 0.018692 | -0.060618 | 0.013189 | 0.027461 | 0.0024545 | -0.0032151 | -0.00034615 | -0.0014038 | 0.013033 | 0.021209 | 0.020025 | -0.0013201 | 0.006742 | -0.001192 | -0.10986 | 0.11902 | -0.20142 | -0.07782 | 0.1236 | -0.022888 | 0.036621 | 0.086975 | 0.14648 | -0.1236 | 0.10071 | 0.21973 | 0.11902 | 0.20599 | 121.4539 | -0.17853 | -0.37537 | 121.7789 | 121.6919 | 121.6324 | 0.23804 | 0.17853 | 121.5317 | -0.15106 | -0.19684 | 121.875 | 121.8613 | 121.7743 | 0.32959 | 0.24261 | 0.32501 | 0.1236 | 0.34332 | 0.2243 | 0.32044 | 0.27008 | 121.7743 | 121.8018 | -0.49896 | -0.42114 | 121.5775 | 121.756 | 121.5454 | 121.7422
1923.5156 | 122.1176 | -121.6415 | 0.27466 | 0.0034333 | -0.059122 | 0.011907 | 0.027889 | 0.0033089 | -0.0051377 | -0.00034615 | 0.001648 | 0.014956 | 0.021422 | 0.014898 | -0.00067933 | 0.0065284 | 0.00094419 | -0.091553 | 0.14191 | -0.20142 | -0.07782 | 0.15106 | -0.018311 | 0.032043 | 0.07782 | 0.13733 | -0.11444 | 0.091553 | 0.21515 | 0.11902 | 0.20599 | 121.4401 | -0.13275 | -0.35248 | 121.7926 | 121.6736 | 121.6232 | 0.23346 | 0.18311 | 121.5271 | -0.13733 | -0.18311 | 121.8567 | 121.8475 | 121.7606 | 0.32044 | 0.23346 | 0.35248 | 0.1236 | 0.32959 | 0.20599 | 0.34332 | 0.25177 | 121.7834 | 121.7789 | -0.47607 | -0.3891 | 121.5637 | 121.7331 | 121.55 | 121.7194
1925.2031 | 121.9894 | -121.7331 | 0.3479 | 0.011063 | -0.058695 | 0.012762 | 0.02917 | 0.0022409 | -0.0062057 | 0.00029485 | 0.0046998 | 0.016451 | 0.022277 | 0.015966 | -0.0030291 | 0.004392 | 8.9786e-05 | -0.12817 | 0.20599 | -0.20599 | -0.16022 | 0.032043 | -0.10071 | -0.036621 | -0.09613 | 0.19226 | -0.16479 | -0.041199 | 0.054932 | -0.041199 | 0.09613 | 121.5271 | -0.14191 | -0.50812 | 121.7651 | 121.6965 | 121.6324 | 0.16937 | 0.10529 | 121.5683 | -0.15564 | -0.3891 | 121.788 | 121.8292 | 121.6919 | 0.26092 | 0.1236 | 0.23804 | 0.045777 | 0.21973 | 0.1236 | 0.41199 | 0.35706 | 121.9391 | 121.9254 | -0.55389 | -0.5127 | 121.5729 | 121.6919 | 121.6049 | 121.637
1926.9375 | 122.0947 | -121.6873 | 0.28839 | 0.011063 | -0.058695 | 0.012975 | 0.030452 | 0.0088631 | -0.0030015 | 0.00029485 | 0.001648 | 0.014315 | 0.021209 | 0.024297 | 0.0038067 | 0.0063148 | -0.00055121 | -0.15564 | 0.064087 | -0.2655 | -0.15106 | 0.064087 | -0.12817 | -0.054932 | 0.086975 | 0.14648 | -0.12817 | 0.082397 | 0.16022 | 0.068665 | 0.1831 | 121.4218 | -0.2243 | -0.43945 | 121.7514 | 121.6324 | 121.5591 | 0.21057 | 0.13733 | 121.5591 | -0.14191 | -0.20599 | 121.8475 | 121.8704 | 121.756 | 0.31128 | 0.19684 | 0.32959 | 0.11444 | 0.28839 | 0.21057 | 0.32959 | 0.27466 | 121.7514 | 121.8338 | -0.55389 | -0.41657 | 121.5363 | 121.7697 | 121.5317 | 121.7743
1928.6875 | 122.1222 | -121.669 | 0.3067 | 0.0034333 | -0.056345 | 0.013616 | 0.031093 | 0.0026681 | -0.0021469 | 0.0015764 | -0.0014038 | 0.01282 | 0.02014 | 0.015112 | 0.0031659 | 0.0075964 | -0.00097841 | -0.1831 | 0.073242 | -0.29297 | -0.20599 | -0.009155 | -0.18768 | -0.11444 | 0.027466 | 0.15564 | -0.11902 | 0.091553 | 0.16479 | 0.045776 | 0.20599 | 121.376 | -0.23346 | -0.5127 | 121.6599 | 121.5546 | 121.4813 | 0.17853 | 0.10529 | 121.55 | -0.15106 | -0.21515 | 121.8338 | 121.875 | 121.7148 | 0.32501 | 0.16479 | 0.28381 | 0.086975 | 0.28381 | 0.21057 | 0.36621 | 0.27466 | 121.7422 | 121.8246 | -0.59967 | -0.42572 | 121.463 | 121.7606 | 121.4859 | 121.6965
1930.4375 | 122.168 | -121.6736 | 0.30212 | -0.0041962 | -0.059122 | 0.011267 | 0.030452 | 0.0073679 | -0.0019333 | -0.00013235 | -0.0014038 | 0.012392 | 0.021422 | 0.016821 | 0.00060247 | 0.0071692 | -0.001192 | -0.086975 | 0.12817 | -0.19226 | -0.054932 | 0.16937 | -0.009155 | 0.064087 | 0.10071 | 0.15106 | -0.11902 | 0.082397 | 0.21515 | 0.10986 | 0.19226 | 121.4813 | -0.17395 | -0.35706 | 121.843 | 121.7377 | 121.6644 | 0.25635 | 0.18311 | 121.5546 | -0.15106 | -0.21973 | 121.8887 | 121.8658 | 121.7834 | 0.31128 | 0.22888 | 0.36163 | 0.13733 | 0.33417 | 0.20142 | 0.32044 | 0.27008 | 121.8018 | 121.8246 | -0.49438 | -0.42114 | 121.6187 | 121.756 | 121.5866 | 121.7743
1932.1406 | 122.168 | -121.7056 | 0.27924 | 0.0034333 | -0.058695 | 0.012335 | 0.030879 | 0.0015999 | -0.0036423 | -0.00055975 | 0.0046998 | 0.012606 | 0.019286 | 0.018743 | -0.0023883 | 0.00781 | -0.002901 | -0.09613 | 0.13733 | -0.19684 | -0.059509 | 0.18768 | 0 | 0.059509 | 0.10986 | 0.14648 | -0.10529 | 0.082397 | 0.20599 | 0.11444 | 0.20142 | 121.5088 | -0.14191 | -0.33874 | 121.8933 | 121.7651 | 121.7056 | 0.25635 | 0.19684 | 121.6003 | -0.13275 | -0.19684 | 121.9116 | 121.907 | 121.8201 | 0.3067 | 0.21973 | 0.38452 | 0.13733 | 0.31128 | 0.18768 | 0.33417 | 0.25177 | 121.843 | 121.8521 | -0.47607 | -0.38452 | 121.6461 | 121.788 | 121.6095 | 121.8155
1933.8906 | 122.0627 | -121.7331 | 0.31128 | 0.0034333 | -0.058054 | 0.011694 | 0.031734 | 0.0043771 | -0.0036423 | 0.0032854 | 0.001648 | 0.015383 | 0.021209 | 0.017034 | 0.0010297 | 0.006101 | -0.0035418 | -0.10071 | 0.16022 | -0.22888 | -0.16022 | 0.027466 | -0.1236 | -0.086975 | -0.004578 | 0.17853 | -0.13733 | 0.013733 | 0.086975 | -0.041199 | 0.12817 | 121.5042 | -0.15106 | -0.4715 | 121.7606 | 121.6461 | 121.6095 | 0.14191 | 0.10529 | 121.5958 | -0.13275 | -0.29755 | 121.8201 | 121.8613 | 121.6919 | 0.2655 | 0.09613 | 0.25635 | 0.068665 | 0.2243 | 0.15106 | 0.3891 | 0.31586 | 121.8933 | 121.9116 | -0.54016 | -0.44861 | 121.5729 | 121.7468 | 121.6324 | 121.7285
1935.625 | 122.1313 | -121.7056 | 0.28839 | 0.011063 | -0.05955 | 0.014684 | 0.030666 | 0.0067269 | -0.0040695 | 0.00093565 | 0.001648 | 0.014315 | 0.020781 | 0.01917 | 0.0023115 | 0.00781 | -0.001192 | -0.15564 | 0.064087 | -0.2655 | -0.14648 | 0.059509 | -0.11902 | -0.050354 | 0.07782 | 0.13733 | -0.091553 | 0.082397 | 0.16022 | 0.059509 | 0.20599 | 121.4401 | -0.2243 | -0.43488 | 121.7651 | 121.6553 | 121.5866 | 0.21515 | 0.14648 | 121.6141 | -0.15106 | -0.20599 | 121.8658 | 121.9116 | 121.7651 | 0.29755 | 0.15106 | 0.32501 | 0.11902 | 0.25177 | 0.17395 | 0.32959 | 0.22888 | 121.7697 | 121.843 | -0.55389 | -0.37994 | 121.5591 | 121.788 | 121.55 | 121.7834
1937.375 | 122.1451 | -121.7056 | 0.28381 | -0.0041962 | -0.059763 | 0.0099848 | 0.030879 | 0.0043771 | -0.0030015 | -0.00013235 | 0.001648 | 0.013247 | 0.020354 | 0.02152 | 0.0023115 | 0.009519 | 0.005003 | -0.2243 | 0.086975 | -0.29755 | -0.21515 | -0.041199 | -0.21057 | -0.12817 | 0.022888 | 0.16022 | -0.1236 | 0.07782 | 0.14648 | 0.050354 | 0.20599 | 121.4081 | -0.19684 | -0.49896 | 121.6644 | 121.5775 | 121.4951 | 0.16937 | 0.086975 | 121.582 | -0.1236 | -0.20599 | 121.8521 | 121.9116 | 121.756 | 0.32959 | 0.17395 | 0.25635 | 0.082397 | 0.27008 | 0.20142 | 0.38452 | 0.28381 | 121.7926 | 121.8658 | -0.58136 | -0.40741 | 121.4905 | 121.7834 | 121.4813 | 121.7285
1939.0625 | 122.0673 | -121.7422 | 0.33417 | 0.0034333 | -0.059977 | 0.011694 | 0.030666 | 0.0054453 | -0.00065149 | -0.00098695 | -0.0044556 | 0.016024 | 0.024199 | 0.010626 | -0.00067933 | 0.0065284 | -0.0020464 | -0.11444 | 0.14648 | -0.23346 | -0.16022 | 0.036621 | -0.1236 | -0.068665 | -0.013733 | 0.17853 | -0.14648 | 0.032043 | 0.10529 | -0.013733 | 0.13275 | 121.5088 | -0.18768 | -0.49438 | 121.7789 | 121.6736 | 121.6187 | 0.16479 | 0.10986 | 121.5958 | -0.15564 | -0.30212 | 121.8475 | 121.875 | 121.7285 | 0.27924 | 0.13275 | 0.27008 | 0.073242 | 0.25177 | 0.17853 | 0.37994 | 0.32501 | 121.8887 | 121.9208 | -0.56763 | -0.48065 | 121.582 | 121.7743 | 121.6278 | 121.7285
1940.8125 | 122.1176 | -121.7377 | 0.32044 | 0.0034333 | -0.059763 | 0.014044 | 0.029598 | 0.0048043 | -0.0015061 | -0.00034615 | 0.001648 | 0.015383 | 0.021849 | 0.013616 | -0.0013201 | 0.0052466 | -0.0020464 | -0.10529 | 0.16479 | -0.21973 | -0.15564 | 0.050354 | -0.11444 | -0.050354 | -0.009155 | 0.18768 | -0.13733 | 0.022888 | 0.11902 | 0.018311 | 0.15106 | 121.5179 | -0.15564 | -0.47608 | 121.788 | 121.6873 | 121.6232 | 0.16937 | 0.10529 | 121.6003 | -0.13275 | -0.29755 | 121.8567 | 121.8887 | 121.756 | 0.28839 | 0.15564 | 0.27008 | 0.064087 | 0.25635 | 0.16022 | 0.38452 | 0.32501 | 121.9025 | 121.9254 | -0.54016 | -0.45776 | 121.582 | 121.7606 | 121.6324 | 121.7285
1942.5625 | 122.1909 | -121.7331 | 0.28839 | 0.0034333 | -0.06254 | 0.012121 | 0.027248 | 0.0033089 | -0.0051377 | 0.00093565 | 0.001648 | 0.01346 | 0.020354 | 0.01383 | -0.0011065 | 0.0054602 | -0.00033761 | -0.091553 | 0.13275 | -0.19684 | -0.059509 | 0.16022 | 0.013733 | 0.041199 | 0.082397 | 0.14648 | -0.11444 | 0.091553 | 0.21057 | 0.11902 | 0.20142 | 121.5363 | -0.15564 | -0.3479 | 121.8933 | 121.7743 | 121.7468 | 0.23804 | 0.21057 | 121.6187 | -0.14191 | -0.19684 | 121.9437 | 121.9345 | 121.8521 | 0.31586 | 0.23346 | 0.35706 | 0.13733 | 0.32501 | 0.20599 | 0.32959 | 0.26093 | 121.8658 | 121.8796 | -0.48523 | -0.40283 | 121.6736 | 121.8246 | 121.6415 | 121.8155
1944.25 | 122.1909 | -121.7102 | 0.29297 | -0.0041962 | -0.057413 | 0.013616 | 0.029384 | 0.0026681 | -0.0025741 | -0.0014142 | 0.001648 | 0.014101 | 0.022277 | 0.017462 | 0.0018841 | 0.0063148 | 0.0011578 | -0.14648 | 0.054932 | -0.27008 | -0.14648 | 0.045776 | -0.13733 | -0.068665 | 0.064087 | 0.14191 | -0.11902 | 0.11444 | 0.19226 | 0.068665 | 0.23804 | 121.4401 | -0.23804 | -0.43945 | 121.756 | 121.6415 | 121.5729 | 0.20142 | 0.13275 | 121.5912 | -0.15106 | -0.17853 | 121.9025 | 121.9482 | 121.7789 | 0.35706 | 0.18768 | 0.31586 | 0.1236 | 0.31128 | 0.23346 | 0.32501 | 0.26093 | 121.7651 | 121.8521 | -0.56305 | -0.41199 | 121.5637 | 121.8246 | 121.5637 | 121.7743
1946.0156 | 122.1588 | -121.7422 | 0.29755 | 0.0034333 | -0.059977 | 0.012548 | 0.029384 | 0.0033089 | -0.0040695 | 0.00029485 | 0.001648 | 0.012606 | 0.020354 | 0.019384 | -0.0030291 | 0.006742 | 0.0052166 | -0.17395 | 0.10529 | -0.26093 | -0.17853 | 0.009155 | -0.13275 | -0.059509 | -0.018311 | 0.16022 | -0.1236 | 0.036621 | 0.13733 | 0.032043 | 0.16479 | 121.4813 | -0.19226 | -0.47607 | 121.7514 | 121.6827 | 121.6095 | 0.20142 | 0.12817 | 121.6187 | -0.13733 | -0.26092 | 121.8796 | 121.907 | 121.7743 | 0.28839 | 0.15564 | 0.27008 | 0.082397 | 0.26093 | 0.16022 | 0.36621 | 0.28381 | 121.8475 | 121.9025 | -0.55847 | -0.42114 | 121.5637 | 121.7789 | 121.5683 | 121.7239
1947.7188 | 122.113 | -121.7743 | 0.32501 | 0.0034333 | -0.057627 | 0.011267 | 0.030666 | 0.0041635 | -0.0036423 | 0.0026446 | 0.001648 | 0.016665 | 0.021209 | 0.014898 | 0.00038887 | 0.0073828 | -0.0014056 | -0.10529 | 0.15106 | -0.22888 | -0.13733 | 0.027466 | -0.10529 | -0.073242 | -0.013733 | 0.17395 | -0.12817 | 0.018311 | 0.10071 | -0.018311 | 0.13275 | 121.5454 | -0.17395 | -0.46234 | 121.8018 | 121.7011 | 121.669 | 0.15564 | 0.1236 | 121.6461 | -0.15106 | -0.3067 | 121.875 | 121.907 | 121.756 | 0.26093 | 0.10986 | 0.25635 | 0.091553 | 0.22888 | 0.14649 | 0.37994 | 0.30212 | 121.9254 | 121.9482 | -0.55389 | -0.45319 | 121.637 | 121.7926 | 121.669 | 121.7606
1949.4531 | 122.1863 | -121.7651 | 0.28839 | 0.011063 | -0.0572 | 0.013189 | 0.030452 | 0.0026681 | -0.0023605 | 0.002431 | 0.0046998 | 0.015169 | 0.022704 | 0.019384 | 0.0018841 | 0.0069556 | 0.00051699 | -0.16022 | 0.054932 | -0.25635 | -0.13275 | 0.064087 | -0.12817 | -0.064087 | 0.073242 | 0.13275 | -0.10071 | 0.10986 | 0.16479 | 0.068665 | 0.20142 | 121.5088 | -0.23346 | -0.42114 | 121.8292 | 121.701 | 121.637 | 0.19226 | 0.12817 | 121.6644 | -0.15564 | -0.17853 | 121.9299 | 121.9666 | 121.8338 | 0.30212 | 0.16937 | 0.32044 | 0.1236 | 0.2655 | 0.21057 | 0.31128 | 0.23346 | 121.8201 | 121.8979 | -0.54474 | -0.3891 | 121.6324 | 121.875 | 121.6049 | 121.8384
1951.2031 | 122.0764 | -121.8338 | 0.32044 | 0.0034333 | -0.059763 | 0.012975 | 0.030666 | 0.0056589 | -1.0686e-05 | -0.00013235 | -0.0014038 | 0.016878 | 0.021422 | 0.019598 | 0.00081607 | 0.0082374 | -0.00033761 | -0.1831 | 0.13733 | -0.25177 | -0.27008 | -0.09613 | -0.25177 | -0.16937 | -0.12817 | 0.19226 | -0.15564 | -0.032043 | 0.036621 | -0.082397 | 0.10986 | 121.582 | -0.18311 | -0.59052 | 121.7377 | 121.6644 | 121.582 | 0.082397 | 0 | 121.6782 | -0.12817 | -0.35248 | 121.8704 | 121.9437 | 121.7514 | 0.2655 | 0.073243 | 0.15564 | -0.018311 | 0.19226 | 0.1236 | 0.3891 | 0.3479 | 121.9711 | 122.0261 | -0.57221 | -0.47608 | 121.5637 | 121.8018 | 121.6507 | 121.7056
1952.9531 | 122.2046 | -121.788 | 0.28839 | -0.0041962 | -0.05955 | 0.014471 | 0.028957 | 0.0028817 | -0.0027877 | 0.002431 | -0.0044556 | 0.014101 | 0.020354 | 0.018316 | 0.00060247 | 0.0086646 | -0.00055121 | -0.13733 | 0.054932 | -0.25177 | -0.13733 | 0.073242 | -0.13275 | -0.036621 | 0.07782 | 0.13733 | -0.1236 | 0.09613 | 0.16479 | 0.068665 | 0.20142 | 121.5363 | -0.23346 | -0.42572 | 121.8613 | 121.7514 | 121.6553 | 0.21515 | 0.11902 | 121.6644 | -0.15106 | -0.19226 | 121.9528 | 121.9894 | 121.8567 | 0.32501 | 0.19226 | 0.32501 | 0.11444 | 0.28839 | 0.21973 | 0.3067 | 0.26093 | 121.843 | 121.9254 | -0.54016 | -0.41199 | 121.6507 | 121.8842 | 121.6507 | 121.8658
1954.6406 | 122.168 | -121.8018 | 0.32044 | -0.0041962 | -0.056986 | 0.011267 | 0.028957 | 0.0039499 | -0.0021469 | -0.00013235 | 0.0046998 | 0.017733 | 0.021209 | 0.01383 | 0.0012433 | 0.0069556 | -0.0016192 | -0.10529 | 0.15564 | -0.20599 | -0.14191 | 0.036621 | -0.11444 | -0.036621 | 0 | 0.18768 | -0.14648 | 0.045776 | 0.10071 | -0.004578 | 0.16937 | 121.5958 | -0.1648 | -0.46234 | 121.8384 | 121.7651 | 121.6873 | 0.16937 | 0.091553 | 121.6553 | -0.13275 | -0.27466 | 121.9025 | 121.9711 | 121.7972 | 0.31586 | 0.14191 | 0.24262 | 0.064087 | 0.24719 | 0.19226 | 0.36163 | 0.33417 | 121.9574 | 121.9894 | -0.52643 | -0.46692 | 121.6599 | 121.8475 | 121.6965 | 121.8018
1956.4062 | 122.2321 | -121.7651 | 0.29755 | 0.011063 | -0.059122 | 0.014044 | 0.030879 | 0.0050179 | -0.0023605 | 0.00029485 | 0.001648 | 0.014315 | 0.020354 | 0.020239 | 0.0023115 | 0.0086646 | -0.0026874 | -0.19226 | 0.09613 | -0.27924 | -0.2243 | -0.018311 | -0.16479 | -0.11902 | 0.027466 | 0.16022 | -0.12817 | 0.09613 | 0.16022 | 0.059509 | 0.21515 | 121.4859 | -0.20142 | -0.52185 | 121.7468 | 121.6461 | 121.6003 | 0.16022 | 0.11444 | 121.637 | -0.13733 | -0.20142 | 121.9254 | 121.9803 | 121.8246 | 0.34332 | 0.18768 | 0.26092 | 0.054932 | 0.28839 | 0.2243 | 0.37537 | 0.28839 | 121.8613 | 121.9254 | -0.57678 | -0.42572 | 121.5408 | 121.8613 | 121.5729 | 121.7926
1958.0938 | 122.1725 | -121.8292 | 0.31586 | 0.011063 | -0.059336 | 0.012121 | 0.030025 | 0.0048043 | -0.0015061 | -0.00055975 | 0.0046998 | 0.014315 | 0.019072 | 0.022802 | -0.0015337 | 0.0075964 | -0.0043964 | -0.10529 | 0.16022 | -0.20599 | -0.15564 | 0.041199 | -0.10986 | -0.073242 | -0.013733 | 0.1831 | -0.13733 | 0.036621 | 0.11902 | -0.027466 | 0.12817 | 121.6232 | -0.15564 | -0.4715 | 121.8704 | 121.756 | 121.7194 | 0.13275 | 0.096131 | 121.6919 | -0.13275 | -0.27924 | 121.9482 | 121.9574 | 121.8018 | 0.2655 | 0.10986 | 0.24719 | 0.050354 | 0.25635 | 0.17395 | 0.36621 | 0.32043 | 121.9894 | 122.0123 | -0.52185 | -0.45319 | 121.6736 | 121.8658 | 121.7239 | 121.8155
1959.8438 | 122.1497 | -121.8201 | 0.31128 | 0.0034333 | -0.058695 | 0.013403 | 0.031734 | 0.0080087 | -0.00043789 | 0.0028582 | -0.0044556 | 0.01581 | 0.02249 | 0.022802 | 0.00081607 | 0.0069556 | 0.00030339 | -0.21515 | 0.11902 | -0.30212 | -0.25177 | -0.09613 | -0.23804 | -0.15106 | -0.068665 | 0.19226 | -0.1236 | -0.018311 | 0.045776 | -0.041199 | 0.1236 | 121.5179 | -0.19226 | -0.56305 | 121.7239 | 121.669 | 121.582 | 0.15106 | 0.064087 | 121.6965 | -0.11902 | -0.32959 | 121.8658 | 121.9437 | 121.7789 | 0.24719 | 0.082397 | 0.20599 | 0.050354 | 0.16937 | 0.10528 | 0.42114 | 0.31586 | 121.9391 | 122.0123 | -0.6134 | -0.43487 | 121.5683 | 121.8018 | 121.6049 | 121.7514
1961.6094 | 122.2504 | -121.8475 | 0.3067 | 0.011063 | -0.06019 | 0.011907 | 0.028529 | 0.0039499 | -0.0062057 | 0.003499 | -0.0014038 | 0.01346 | 0.021209 | 0.020239 | -0.00089293 | 0.008451 | -0.0014056 | -0.15106 | 0.1236 | -0.21515 | -0.14191 | 0.054932 | -0.07782 | 0 | 0.018311 | 0.16022 | -0.13275 | 0.07782 | 0.18768 | 0.073242 | 0.20142 | 121.6324 | -0.18311 | -0.44861 | 121.9025 | 121.8475 | 121.7697 | 0.21515 | 0.13733 | 121.7148 | -0.14648 | -0.22888 | 122.0352 | 122.0489 | 121.9208 | 0.33417 | 0.20599 | 0.27008 | 0.073242 | 0.32043 | 0.21057 | 0.33875 | 0.29297 | 121.9711 | 122.0078 | -0.52185 | -0.43945 | 121.7056 | 121.9254 | 121.6965 | 121.8658
1963.3594 | 122.1268 | -121.8567 | 0.32501 | 0.011063 | -0.059122 | 0.012548 | 0.030879 | 0.0030953 | -0.0032151 | -0.0012006 | 0.0046998 | 0.015383 | 0.020568 | 0.012335 | -0.0030291 | 0.0035376 | -0.00055121 | -0.11902 | 0.2243 | -0.19226 | -0.15106 | 0.022888 | -0.091553 | -0.027466 | -0.07782 | 0.20599 | -0.16022 | -0.050354 | 0.050354 | -0.041199 | 0.10529 | 121.6644 | -0.10071 | -0.47607 | 121.8796 | 121.8292 | 121.7651 | 0.16479 | 0.10071 | 121.6965 | -0.11902 | -0.37537 | 121.907 | 121.962 | 121.8155 | 0.2655 | 0.11902 | 0.21515 | 0.041199 | 0.21057 | 0.10986 | 0.41656 | 0.36621 | 122.081 | 122.0627 | -0.51727 | -0.48523 | 121.7056 | 121.8063 | 121.7377 | 121.7789
1965.0469 | 122.2137 | -121.8521 | 0.30212 | -0.0041962 | -0.061259 | 0.012121 | 0.028743 | 0.00053194 | -0.0051377 | 0.0011492 | 0.001648 | 0.01282 | 0.022704 | 0.02387 | -0.00025213 | 0.0082374 | -0.00012381 | -0.19684 | 0.091553 | -0.23346 | -0.16937 | 0.018311 | -0.12817 | -0.050354 | -0.013733 | 0.16022 | -0.11444 | 0.036621 | 0.13733 | 0.036621 | 0.15106 | 121.6187 | -0.21057 | -0.4715 | 121.8704 | 121.8018 | 121.7239 | 0.1831 | 0.10528 | 121.7377 | -0.14191 | -0.2655 | 121.9894 | 122.0032 | 121.8887 | 0.2655 | 0.15106 | 0.25177 | 0.064086 | 0.25177 | 0.15106 | 0.32501 | 0.27466 | 121.9437 | 122.0123 | -0.53558 | -0.41657 | 121.6827 | 121.8887 | 121.6553 | 121.8384
1966.7969 | 122.1405 | -121.8658 | 0.34332 | 0.018692 | -0.05955 | 0.010626 | 0.030025 | 0.0035227 | -0.0049241 | 0.0030718 | 0.0046998 | 0.014956 | 0.021636 | 0.015539 | -0.0051653 | 0.0039648 | 0.0024396 | -0.12817 | 0.1831 | -0.21973 | -0.16479 | 0.036621 | -0.10529 | -0.032043 | -0.09613 | 0.19226 | -0.13733 | -0.041199 | 0.068665 | -0.041199 | 0.10071 | 121.6461 | -0.16022 | -0.50812 | 121.9025 | 121.8338 | 121.7606 | 0.18768 | 0.11444 | 121.7285 | -0.15106 | -0.38452 | 121.9345 | 121.9666 | 121.8246 | 0.23804 | 0.09613 | 0.25635 | 0.054932 | 0.20599 | 0.09613 | 0.40283 | 0.32959 | 122.0489 | 122.0581 | -0.56305 | -0.48065 | 121.701 | 121.8246 | 121.7377 | 121.7697
1968.5469 | 122.1451 | -121.8979 | 0.33875 | -0.011826 | -0.058054 | 0.010626 | 0.030025 | -0.00074986 | -0.0030015 | 0.00072205 | -0.0044556 | 0.011965 | 0.020568 | 0.01383 | -0.0019611 | 0.005033 | 0.00094419 | -0.14191 | 0.18768 | -0.21973 | -0.16479 | 0.041199 | -0.10986 | -0.027466 | -0.073242 | 0.17853 | -0.15106 | -0.027466 | 0.064087 | -0.036621 | 0.10529 | 121.6782 | -0.15106 | -0.50354 | 121.9391 | 121.8704 | 121.788 | 0.19226 | 0.10986 | 121.7468 | -0.16022 | -0.36621 | 121.962 | 122.0032 | 121.8613 | 0.25635 | 0.11444 | 0.26093 | 0.054932 | 0.21515 | 0.1236 | 0.40741 | 0.32959 | 122.0856 | 122.0764 | -0.55847 | -0.48981 | 121.7331 | 121.8704 | 121.756 | 121.8246
1970.2188 | 122.2458 | -121.8384 | 0.3067 | -0.0041962 | -0.058268 | 0.011053 | 0.029811 | 0.0041635 | -0.0047103 | -0.0014142 | 0.0046998 | 0.011751 | 0.021849 | 0.014044 | -0.00046573 | 0.0058874 | -0.00033761 | -0.16937 | 0.09613 | -0.24719 | -0.17395 | 0.022888 | -0.13733 | -0.059509 | -0.004578 | 0.15564 | -0.12817 | 0.036621 | 0.14191 | 0.022888 | 0.16937 | 121.5912 | -0.21057 | -0.48065 | 121.8613 | 121.7789 | 121.7011 | 0.18768 | 0.10986 | 121.7102 | -0.15106 | -0.27008 | 121.9803 | 122.0078 | 121.8613 | 0.29755 | 0.15106 | 0.27008 | 0.073242 | 0.27008 | 0.1648 | 0.34332 | 0.28381 | 121.9345 | 121.994 | -0.55389 | -0.43488 | 121.6644 | 121.875 | 121.669 | 121.8338
1971.9688 | 122.2 | -121.875 | 0.32044 | -0.0041962 | -0.06019 | 0.014044 | 0.029598 | 0.0039499 | -0.0030015 | 0.0015764 | -0.0014038 | 0.017946 | 0.02249 | 0.022802 | 0.00038887 | 0.0073828 | 0.002226 | -0.19684 | 0.09613 | -0.30212 | -0.24719 | -0.073242 | -0.23804 | -0.15564 | -0.064087 | 0.17395 | -0.15106 | 0.004578 | 0.068665 | -0.045776 | 0.13275 | 121.5729 | -0.22431 | -0.56763 | 121.8018 | 121.7194 | 121.637 | 0.14648 | 0.064087 | 121.7239 | -0.14649 | -0.31586 | 121.9437 | 122.0078 | 121.8292 | 0.28381 | 0.10529 | 0.22888 | 0.054932 | 0.21973 | 0.15564 | 0.39825 | 0.32501 | 121.9711 | 122.049 | -0.62256 | -0.4715 | 121.6278 | 121.8796 | 121.6782 | 121.8109
1973.6719 | 122.2046 | -121.8796 | 0.32501 | 0.011063 | -0.060404 | 0.010839 | 0.030238 | 0.0045907 | -0.0040695 | -0.0012006 | 0.001648 | 0.016451 | 0.021636 | 0.015966 | -0.0019611 | 0.0073828 | -0.0014056 | -0.10071 | 0.19226 | -0.20599 | -0.13275 | 0.036621 | -0.082397 | -0.032043 | -0.036621 | 0.1831 | -0.14648 | 0.018311 | 0.10529 | -0.004578 | 0.13733 | 121.6736 | -0.13275 | -0.45776 | 121.9162 | 121.8475 | 121.7972 | 0.17395 | 0.1236 | 121.7331 | -0.14191 | -0.3067 | 121.9849 | 122.0169 | 121.875 | 0.28381 | 0.14191 | 0.24262 | 0.073243 | 0.25177 | 0.16479 | 0.39826 | 0.32959 | 122.0718 | 122.0627 | -0.53101 | -0.4715 | 121.7468 | 121.8979 | 121.7789 | 121.843
1975.4375 | 122.2229 | -121.875 | 0.33417 | -0.011826 | -0.06019 | 0.013189 | 0.028529 | 0.0028817 | -0.0030015 | 0.0013628 | 0.0077514 | 0.011965 | 0.020995 | 0.019384 | -0.0017475 | 0.004392 | 0.00094419 | -0.091553 | 0.14648 | -0.19226 | -0.059509 | 0.13733 | -0.009155 | 0.036621 | 0.004578 | 0.1831 | -0.12817 | 0.004578 | 0.10071 | 0.004578 | 0.14191 | 121.6827 | -0.18768 | -0.39368 | 122.0123 | 121.9116 | 121.8658 | 0.22888 | 0.18311 | 121.7468 | -0.15106 | -0.32959 | 121.9757 | 122.0169 | 121.8796 | 0.27008 | 0.13275 | 0.32959 | 0.13275 | 0.22888 | 0.13275 | 0.33874 | 0.31128 | 122.0215 | 122.0581 | -0.52643 | -0.46234 | 121.8155 | 121.8796 | 121.7834 | 121.8796
1977.125 | 122.3145 | -121.8521 | 0.3067 | -0.0041962 | -0.061899 | 0.013189 | 0.027889 | 0.00095914 | -0.0051377 | -0.00034615 | 0.001648 | 0.014101 | 0.020354 | 0.015112 | 0.0018841 | 0.0063148 | 0.0011578 | -0.086975 | 0.13275 | -0.19226 | -0.045776 | 0.17395 | -0.009155 | 0.041199 | 0.073242 | 0.15106 | -0.10986 | 0.10071 | 0.22888 | 0.11902 | 0.21057 | 121.6599 | -0.17395 | -0.35248 | 122.0261 | 121.8933 | 121.843 | 0.23346 | 0.18311 | 121.7422 | -0.15564 | -0.20599 | 122.081 | 122.0627 | 121.9711 | 0.32043 | 0.22888 | 0.36621 | 0.14648 | 0.33875 | 0.21057 | 0.32501 | 0.26093 | 121.9849 | 122.0032 | -0.49896 | -0.41656 | 121.8063 | 121.9528 | 121.7651 | 121.9254
1978.875 | 122.2275 | -121.875 | 0.32501 | 0.0034333 | -0.059122 | 0.011267 | 0.02917 | 0.0011727 | -0.0032151 | 0.00072205 | 0.001648 | 0.016024 | 0.020995 | 0.020666 | 0.00081607 | 0.006742 | 0.00051699 | -0.11444 | 0.18768 | -0.21515 | -0.14648 | 0.027466 | -0.10071 | -0.045776 | -0.054932 | 0.1831 | -0.13275 | 0.013733 | 0.10529 | -0.004578 | 0.14191 | 121.6599 | -0.13733 | -0.4715 | 121.9025 | 121.8292 | 121.7743 | 0.16937 | 0.11444 | 121.7422 | -0.14191 | -0.31128 | 121.9803 | 122.0169 | 121.8704 | 0.27466 | 0.12817 | 0.24261 | 0.068665 | 0.23804 | 0.14648 | 0.40283 | 0.31586 | 122.0627 | 122.0581 | -0.54016 | -0.45776 | 121.7285 | 121.8887 | 121.7606 | 121.8201
1980.625 | 122.1909 | -121.907 | 0.32044 | 0.0034333 | -0.058695 | 0.012335 | 0.028957 | 0.0030953 | -0.0017197 | 0.0017902 | -0.0014038 | 0.016451 | 0.023131 | 0.020025 | 0.0035931 | 0.0088782 | -0.0018328 | -0.20142 | 0.1236 | -0.28381 | -0.28381 | -0.11902 | -0.24261 | -0.16479 | -0.10986 | 0.19226 | -0.15106 | -0.018311 | 0.036621 | -0.064087 | 0.091553 | 121.6232 | -0.19684 | -0.60425 | 121.788 | 121.7422 | 121.6644 | 0.11902 | 0.041198 | 121.756 | -0.12817 | -0.33875 | 121.9437 | 121.9986 | 121.843 | 0.24261 | 0.086975 | 0.16479 | 0 | 0.18768 | 0.13275 | 0.40741 | 0.34332 | 122.0306 | 122.0993 | -0.60425 | -0.4715 | 121.6232 | 121.8887 | 121.7056 | 121.7972
1982.3281 | 122.1817 | -121.907 | 0.33417 | 0.011063 | -0.058695 | 0.015112 | 0.033656 | 0.0037363 | -0.0012925 | 0.0022174 | 0.001648 | 0.015169 | 0.022277 | 0.014257 | -3.8532e-05 | 0.008451 | -0.00033761 | -0.13733 | 0.13275 | -0.2243 | -0.21057 | -0.027466 | -0.16937 | -0.10986 | -0.064087 | 0.18768 | -0.13275 | -0.009155 | 0.050354 | -0.050354 | 0.11444 | 121.6827 | -0.20142 | -0.54474 | 121.8796 | 121.7972 | 121.7377 | 0.11444 | 0.054931 | 121.7743 | -0.14648 | -0.34332 | 121.9574 | 122.0215 | 121.8567 | 0.24719 | 0.082397 | 0.19684 | 0.013733 | 0.18311 | 0.1236 | 0.35706 | 0.32043 | 122.0398 | 122.0947 | -0.55847 | -0.46692 | 121.6965 | 121.8979 | 121.7697 | 121.843
1984.0781 | 122.3419 | -121.8796 | 0.30212 | 0.0034333 | -0.062113 | 0.013616 | 0.026607 | 0.0056589 | -0.0062057 | 0.0022174 | 0.001648 | 0.011965 | 0.020781 | 0.018102 | -0.0013201 | 0.0071692 | 0.00073059 | -0.15564 | 0.10986 | -0.22888 | -0.12817 | 0.086975 | -0.059509 | 0.009155 | 0.050354 | 0.15564 | -0.1236 | 0.082397 | 0.20599 | 0.09613 | 0.21515 | 121.6507 | -0.19226 | -0.4303 | 121.9666 | 121.8887 | 121.8201 | 0.23804 | 0.16937 | 121.756 | -0.14648 | -0.21973 | 122.0856 | 122.0947 | 121.9757 | 0.33875 | 0.21973 | 0.31586 | 0.10071 | 0.32959 | 0.20599 | 0.33875 | 0.27924 | 121.9894 | 122.0352 | -0.53101 | -0.42572 | 121.7514 | 121.962 | 121.7239 | 121.9299
1985.8125 | 122.2092 | -121.8887 | 0.33417 | -0.0041962 | -0.058481 | 0.01383 | 0.03387 | 0.0065133 | -0.0051377 | -0.00034615 | 0.0046998 | 0.014956 | 0.02014 | 0.017889 | 0.0014569 | 0.006101 | -0.0031146 | -0.14648 | 0.14191 | -0.23804 | -0.21057 | -0.018311 | -0.19226 | -0.11902 | -0.054932 | 0.17853 | -0.1236 | -0.013733 | 0.050354 | -0.059509 | 0.10529 | 121.6507 | -0.19226 | -0.54474 | 121.8704 | 121.7697 | 121.6965 | 0.11902 | 0.045776 | 121.7651 | -0.15564 | -0.3479 | 121.9391 | 121.994 | 121.8292 | 0.22888 | 0.064087 | 0.21973 | 0.027466 | 0.17395 | 0.10986 | 0.37994 | 0.30212 | 122.0306 | 122.0673 | -0.5722 | -0.45776 | 121.6782 | 121.875 | 121.7422 | 121.8338
1987.5 | 122.2504 | -121.9299 | 0.32501 | 0.0034333 | -0.059977 | 0.012762 | 0.031093 | 0.0054453 | -0.0027877 | 0.00050845 | 0.0077514 | 0.013888 | 0.023986 | 0.01853 | 0.0010297 | 0.006101 | 0.001585 | -0.21973 | 0.11444 | -0.27466 | -0.2655 | -0.073242 | -0.22888 | -0.14648 | -0.054932 | 0.16937 | -0.13275 | 0.009155 | 0.073242 | -0.036621 | 0.12817 | 121.6553 | -0.21057 | -0.59052 | 121.8567 | 121.7834 | 121.701 | 0.12817 | 0.045776 | 121.7972 | -0.15564 | -0.31586 | 122.0032 | 122.0581 | 121.8933 | 0.26093 | 0.09613 | 0.20142 | 0.009155 | 0.20599 | 0.14191 | 0.3891 | 0.30212 | 122.0444 | 122.0993 | -0.59967 | -0.45776 | 121.6644 | 121.9391 | 121.7102 | 121.875
1989.25 | 122.2366 | -121.8979 | 0.32044 | 0.0034333 | -0.058054 | 0.010839 | 0.030666 | 0.0062997 | -0.0027877 | 0.0022174 | 0.001648 | 0.014101 | 0.021636 | 0.022802 | 0.0010297 | 0.0080236 | 0.0035078 | -0.19684 | 0.10071 | -0.27924 | -0.27008 | -0.091553 | -0.24261 | -0.15564 | -0.07782 | 0.19684 | -0.13275 | -0.004578 | 0.050354 | -0.059509 | 0.13733 | 121.6187 | -0.21973 | -0.59052 | 121.8063 | 121.7422 | 121.6553 | 0.1236 | 0.036621 | 121.7651 | -0.1236 | -0.32501 | 121.9482 | 122.0352 | 121.8384 | 0.27008 | 0.073242 | 0.18768 | 0.009155 | 0.18311 | 0.12817 | 0.37994 | 0.32959 | 121.9986 | 122.0947 | -0.59967 | -0.45319 | 121.6278 | 121.8933 | 121.701 | 121.8201
1990.9375 | 122.2687 | -121.9162 | 0.32501 | 0.011063 | -0.059122 | 0.012121 | 0.029811 | 0.0028817 | -0.0027877 | 0.00093565 | -0.0014038 | 0.014101 | 0.025054 | 0.010412 | -0.0013201 | 0.0073828 | -0.00033761 | -0.11444 | 0.19684 | -0.20142 | -0.16479 | 0.027466 | -0.10529 | -0.050354 | -0.013733 | 0.19226 | -0.14191 | 0 | 0.10986 | 0 | 0.14648 | 121.7148 | -0.12817 | -0.48981 | 121.9437 | 121.8658 | 121.8109 | 0.15106 | 0.09613 | 121.7743 | -0.13275 | -0.32501 | 122.0261 | 122.0627 | 121.9162 | 0.28839 | 0.14191 | 0.22888 | 0.036621 | 0.25177 | 0.14191 | 0.39825 | 0.33417 | 122.113 | 122.1085 | -0.52643 | -0.46692 | 121.7514 | 121.9162 | 121.8018 | 121.9025
1992.6875 | 122.3145 | -121.9254 | 0.30212 | 0.011063 | -0.061472 | 0.012335 | 0.027889 | 0.00053194 | -0.0023605 | -0.0012006 | -0.0014038 | 0.011751 | 0.022917 | 0.018316 | -0.00046573 | 0.0075964 | 0.0062848 | -0.17853 | 0.09613 | -0.24719 | -0.1831 | 0.018311 | -0.13275 | -0.054932 | -0.032043 | 0.15106 | -0.11902 | 0.032043 | 0.15106 | 0.041199 | 0.17395 | 121.6782 | -0.20599 | -0.48523 | 121.9437 | 121.8704 | 121.7926 | 0.19226 | 0.11444 | 121.8063 | -0.15106 | -0.27008 | 122.0764 | 122.0993 | 121.9666 | 0.29297 | 0.16022 | 0.2655 | 0.064087 | 0.27008 | 0.15106 | 0.34332 | 0.27008 | 122.0215 | 122.0764 | -0.54932 | -0.42114 | 121.7422 | 121.9574 | 121.7468 | 121.8933
1994.4375 | 122.2412 | -121.9391 | 0.35248 | 0.011063 | -0.058909 | 0.012335 | 0.028102 | -0.00032266 | -0.0025741 | 0.0022174 | -0.0014038 | 0.013674 | 0.020995 | 0.014044 | -0.0032427 | 0.0046058 | 0.0013714 | -0.11902 | 0.16937 | -0.20599 | -0.16022 | 0.032043 | -0.091553 | -0.032043 | -0.068665 | 0.19226 | -0.14191 | -0.041199 | 0.07782 | -0.027466 | 0.10071 | 121.7331 | -0.18311 | -0.5127 | 121.9711 | 121.907 | 121.8475 | 0.17395 | 0.11444 | 121.7972 | -0.16022 | -0.39368 | 122.0169 | 122.0398 | 121.9116 | 0.24262 | 0.11444 | 0.23804 | 0.045777 | 0.21973 | 0.10071 | 0.37537 | 0.33417 | 122.1085 | 122.1313 | -0.55847 | -0.49439 | 121.7789 | 121.8979 | 121.8201 | 121.8704
1996.1406 | 122.2412 | -121.9666 | 0.34332 | 0.0034333 | -0.059336 | 0.011053 | 0.030025 | 0.0062997 | -0.0038559 | -0.0014142 | 0.0077514 | 0.014742 | 0.020781 | 0.0076348 | -0.0043109 | 0.0046058 | -0.001192 | -0.16479 | 0.18768 | -0.20599 | -0.17395 | 0.004578 | -0.10986 | -0.041199 | -0.086975 | 0.19684 | -0.14648 | -0.041199 | 0.054932 | -0.027466 | 0.091553 | 121.7606 | -0.15564 | -0.51727 | 121.9711 | 121.9254 | 121.8567 | 0.1648 | 0.096131 | 121.8201 | -0.14648 | -0.38452 | 122.0215 | 122.0581 | 121.9391 | 0.23804 | 0.11902 | 0.21057 | 0.032044 | 0.20142 | 0.10529 | 0.39368 | 0.34332 | 122.1542 | 122.1634 | -0.54932 | -0.48981 | 121.7926 | 121.9254 | 121.8018 | 121.8796
1997.8906 | 122.3648 | -121.875 | 0.28381 | 0.011063 | -0.059977 | 0.014257 | 0.031307 | 0.0052315 | -0.0034287 | 0.0011492 | 0.001648 | 0.013674 | 0.019713 | 0.018102 | 0.0040205 | 0.006742 | -0.0026874 | -0.14191 | 0.059509 | -0.25177 | -0.16022 | 0.045776 | -0.12817 | -0.054932 | 0.073242 | 0.15106 | -0.1236 | 0.11444 | 0.17853 | 0.073242 | 0.21973 | 121.6232 | -0.2243 | -0.44403 | 121.9208 | 121.8201 | 121.7468 | 0.19684 | 0.1236 | 121.7514 | -0.13275 | -0.16937 | 122.0535 | 122.0947 | 121.9482 | 0.34332 | 0.19684 | 0.29755 | 0.091553 | 0.30212 | 0.23804 | 0.31128 | 0.27466 | 121.9345 | 122.0261 | -0.53558 | -0.40741 | 121.7148 | 121.9894 | 121.7331 | 121.9482
1999.6406 | 122.2824 | -121.9482 | 0.33875 | -0.011826 | -0.058054 | 0.010626 | 0.028529 | 0.0037363 | -0.0032151 | 0.0026446 | 0.001648 | 0.014956 | 0.02249 | 0.016607 | -0.0032427 | 0.0054602 | -0.0037554 | -0.1236 | 0.19684 | -0.21515 | -0.17395 | -0.013733 | -0.11444 | -0.068665 | -0.086975 | 0.1831 | -0.15106 | -0.027466 | 0.054932 | -0.027466 | 0.13275 | 121.7331 | -0.14191 | -0.5127 | 121.9345 | 121.8796 | 121.8338 | 0.14648 | 0.10071 | 121.7972 | -0.15564 | -0.36621 | 122.0032 | 122.081 | 121.9208 | 0.28381 | 0.1236 | 0.20142 | 0.041199 | 0.20599 | 0.1236 | 0.41199 | 0.33417 | 122.1451 | 122.1313 | -0.55389 | -0.48981 | 121.7743 | 121.9208 | 121.8246 | 121.8613
2001.3906 | 122.3328 | -121.9299 | 0.31128 | 0.018692 | -0.063822 | 0.012335 | 0.030666 | 0.0050179 | -0.0030015 | 0.0013628 | -0.0014038 | 0.012179 | 0.020995 | 0.021948 | 0.0012433 | 0.006742 | 0.0026532 | -0.17395 | 0.10529 | -0.23346 | -0.16937 | 0.018311 | -0.1236 | -0.050354 | -0.013733 | 0.16479 | -0.12817 | 0.027466 | 0.12817 | 0.036621 | 0.16937 | 121.6965 | -0.20599 | -0.48065 | 121.9482 | 121.8796 | 121.8063 | 0.1831 | 0.10986 | 121.8018 | -0.14648 | -0.28381 | 122.0581 | 122.0993 | 121.9666 | 0.29755 | 0.1648 | 0.25177 | 0.064086 | 0.25635 | 0.15564 | 0.33875 | 0.29297 | 122.0352 | 122.0947 | -0.54474 | -0.43945 | 121.7606 | 121.9574 | 121.756 | 121.9162
2003.0781 | 122.3053 | -121.962 | 0.33875 | 0.0034333 | -0.058481 | 0.0095576 | 0.03152 | 0.0056589 | -0.0025741 | 0.0026446 | -0.0014038 | 0.01581 | 0.02014 | 0.012975 | -0.00067933 | 0.0063148 | -0.0024738 | -0.10529 | 0.19226 | -0.21057 | -0.13733 | 0.009155 | -0.10986 | -0.059509 | -0.041199 | 0.19226 | -0.14648 | 0.022888 | 0.10529 | -0.004578 | 0.14648 | 121.7514 | -0.14648 | -0.47607 | 121.9711 | 121.9025 | 121.8521 | 0.15106 | 0.10071 | 121.8155 | -0.14648 | -0.31586 | 122.0673 | 122.1085 | 121.9574 | 0.29297 | 0.14191 | 0.21973 | 0.073242 | 0.25177 | 0.16937 | 0.40283 | 0.33874 | 122.1542 | 122.1542 | -0.54932 | -0.48523 | 121.8246 | 121.9849 | 121.8567 | 121.9208
2004.8281 | 122.2916 | -121.9757 | 0.33417 | -0.0041962 | -0.057841 | 0.010412 | 0.028316 | 0.0030953 | -0.0049241 | 0.0011492 | 0.0077514 | 0.012392 | 0.02014 | 0.017034 | -0.00067933 | 0.0037512 | -0.002901 | -0.13733 | 0.19226 | -0.2243 | -0.17853 | 0.018311 | -0.11902 | -0.050354 | -0.082397 | 0.19684 | -0.14191 | -0.022888 | 0.086975 | -0.004578 | 0.13733 | 121.7514 | -0.14191 | -0.5127 | 121.994 | 121.9254 | 121.8567 | 0.17395 | 0.10529 | 121.8338 | -0.13733 | -0.35706 | 122.0627 | 122.113 | 121.9711 | 0.27924 | 0.13733 | 0.24261 | 0.045776 | 0.22888 | 0.11902 | 0.41656 | 0.33875 | 122.168 | 122.1725 | -0.55847 | -0.47607 | 121.7972 | 121.9528 | 121.8384 | 121.8933
2006.5312 | 122.2687 | -121.9711 | 0.33417 | 0.0034333 | -0.060404 | 0.011694 | 0.030666 | 0.0071541 | -0.0027877 | -0.00013235 | -0.0014038 | 0.014315 | 0.022063 | 0.013189 | -0.00025213 | 0.0073828 | 0.00094419 | -0.20599 | 0.11444 | -0.29297 | -0.26093 | -0.10071 | -0.25177 | -0.15564 | -0.091553 | 0.19684 | -0.13733 | -0.022888 | 0.045776 | -0.064087 | 0.11444 | 121.6782 | -0.21973 | -0.59509 | 121.8704 | 121.8155 | 121.7194 | 0.13733 | 0.041199 | 121.8338 | -0.13733 | -0.35706 | 122.0169 | 122.0856 | 121.907 | 0.25177 | 0.073242 | 0.19226 | 0.032044 | 0.18311 | 0.11444 | 0.40741 | 0.33417 | 122.0856 | 122.168 | -0.62714 | -0.4715 | 121.7102 | 121.9482 | 121.7651 | 121.8796
2008.2969 | 122.3145 | -121.9711 | 0.31128 | -0.0041962 | -0.057841 | 0.012762 | 0.029598 | 0.0015999 | -0.0036423 | 0.0030718 | 0.0077514 | 0.015169 | 0.02249 | 0.018102 | -0.0019611 | 0.0052466 | 0.00030339 | -0.086975 | 0.14648 | -0.21057 | -0.10986 | 0.1236 | -0.022888 | 0.018311 | 0.022888 | 0.16022 | -0.11902 | 0.013733 | 0.1236 | 0.027466 | 0.15564 | 121.7606 | -0.16479 | -0.42114 | 122.0947 | 121.9894 | 121.9482 | 0.22888 | 0.18768 | 121.8521 | -0.15106 | -0.29755 | 122.0947 | 122.1268 | 121.9986 | 0.27466 | 0.14649 | 0.33417 | 0.10071 | 0.24261 | 0.13275 | 0.35706 | 0.27924 | 122.1176 | 122.1313 | -0.52185 | -0.4303 | 121.8613 | 121.9849 | 121.8842 | 121.994
2010.0469 | 122.3099 | -121.9849 | 0.32044 | -0.0041962 | -0.058695 | 0.014044 | 0.031947 | 0.0054453 | -0.0027877 | -0.0029096 | -0.0014038 | 0.014742 | 0.019286 | 0.016393 | 0.0012433 | 0.0048194 | -0.00033761 | -0.11902 | 0.14648 | -0.22888 | -0.15106 | 0.032043 | -0.11444 | -0.050354 | 0.009155 | 0.18768 | -0.1236 | 0.032043 | 0.10986 | 0 | 0.13275 | 121.756 | -0.17395 | -0.4715 | 122.0169 | 121.9345 | 121.8704 | 0.17853 | 0.11444 | 121.8613 | -0.13275 | -0.28839 | 122.0947 | 122.1176 | 121.9849 | 0.25635 | 0.1236 | 0.26093 | 0.07782 | 0.23346 | 0.15564 | 0.37537 | 0.31128 | 122.1313 | 122.1725 | -0.54932 | -0.44403 | 121.8338 | 122.0169 | 121.8658 | 121.994
2011.7969 | 122.287 | -122.0215 | 0.33875 | 0.026321 | -0.059763 | 0.010839 | 0.029598 | 0.0022409 | -0.0049241 | 8.125e-05 | -0.0014038 | 0.014101 | 0.021636 | 0.014257 | -0.0026019 | 0.0058874 | -0.0020464 | -0.12817 | 0.20599 | -0.20142 | -0.1831 | -0.009155 | -0.10986 | -0.054932 | -0.10529 | 0.20599 | -0.15106 | -0.027466 | 0.068665 | -0.041199 | 0.11902 | 121.8201 | -0.13275 | -0.52185 | 122.0123 | 121.9666 | 121.9116 | 0.14648 | 0.091553 | 121.8704 | -0.13275 | -0.36621 | 122.0901 | 122.1405 | 121.9803 | 0.27008 | 0.10986 | 0.19226 | 0.018311 | 0.21973 | 0.1236 | 0.40741 | 0.35706 | 122.2275 | 122.2275 | -0.54016 | -0.48981 | 121.8384 | 121.994 | 121.8933 | 121.9162
2013.4844 | 122.3557 | -121.9711 | 0.29755 | 0.0034333 | -0.06019 | 0.012335 | 0.033229 | 0.0026681 | -0.0049241 | -0.0014142 | 0.0046998 | 0.013247 | 0.021209 | 0.023443 | 0.0050885 | 0.0071692 | 0.0013714 | -0.20599 | 0.091553 | -0.28839 | -0.2655 | -0.064087 | -0.24261 | -0.13733 | -0.013733 | 0.1831 | -0.1236 | 0.059509 | 0.11902 | 0.018311 | 0.17395 | 121.6827 | -0.20599 | -0.56305 | 121.907 | 121.8338 | 121.7285 | 0.15106 | 0.045776 | 121.8475 | -0.11444 | -0.23804 | 122.0901 | 122.1451 | 121.9894 | 0.29755 | 0.14191 | 0.2243 | 0.022888 | 0.24261 | 0.1831 | 0.37994 | 0.3067 | 122.0627 | 122.1542 | -0.58594 | -0.42114 | 121.7056 | 122.0306 | 121.7651 | 121.9574
2015.2344 | 122.4197 | -121.9666 | 0.29297 | -0.011826 | -0.059336 | 0.013403 | 0.026607 | 0.0035227 | -0.0042831 | 8.125e-05 | -0.0014038 | 0.013247 | 0.019927 | 0.019384 | 0.0010297 | 0.0048194 | 0.003294 | -0.13733 | 0.10529 | -0.21973 | -0.11902 | 0.086975 | -0.045776 | 0.027466 | 0.050354 | 0.15564 | -0.10529 | 0.086975 | 0.20142 | 0.10529 | 0.21515 | 121.7468 | -0.18768 | -0.41199 | 122.0535 | 121.994 | 121.9208 | 0.24719 | 0.17395 | 121.8613 | -0.13733 | -0.20599 | 122.168 | 122.1817 | 122.0718 | 0.32044 | 0.21057 | 0.3067 | 0.10071 | 0.3067 | 0.19226 | 0.32501 | 0.26093 | 122.0718 | 122.1222 | -0.5127 | -0.39825 | 121.8475 | 122.0535 | 121.8292 | 122.0169
2017 | 122.4152 | -121.9803 | 0.28839 | -0.0041962 | -0.058054 | 0.013403 | 0.02917 | 0.0035227 | -0.0025741 | 0.00050845 | 0.0046998 | 0.015169 | 0.021422 | 0.020452 | 0.0040205 | 0.008451 | 0.00051699 | -0.18768 | 0.082397 | -0.27466 | -0.17853 | 0.009155 | -0.16022 | -0.068665 | 0.050354 | 0.15564 | -0.10986 | 0.09613 | 0.1831 | 0.07782 | 0.20599 | 121.7056 | -0.20599 | -0.46692 | 121.9894 | 121.9116 | 121.8201 | 0.20599 | 0.11444 | 121.8704 | -0.13275 | -0.19226 | 122.1634 | 122.1863 | 122.0581 | 0.31586 | 0.18768 | 0.28381 | 0.09613 | 0.29297 | 0.20599 | 0.35706 | 0.2655 | 122.0627 | 122.1359 | -0.56305 | -0.39825 | 121.8018 | 122.0764 | 121.7926 | 122.0306
2018.7031 | 122.4197 | -121.9849 | 0.31128 | 0.0034333 | -0.060618 | 0.010626 | 0.027248 | 0.0013863 | -0.0032151 | 0.00029485 | 0.0046998 | 0.01346 | 0.022277 | 0.017034 | -0.0032427 | 0.006742 | -0.00012381 | -0.15106 | 0.12817 | -0.21057 | -0.13275 | 0.059509 | -0.068665 | 0.004578 | 0.018311 | 0.16479 | -0.1236 | 0.073242 | 0.18768 | 0.086975 | 0.19684 | 121.7743 | -0.1831 | -0.44403 | 122.0444 | 121.9894 | 121.9162 | 0.21515 | 0.14191 | 121.8613 | -0.14648 | -0.23804 | 122.1725 | 122.1817 | 122.0718 | 0.32043 | 0.21057 | 0.27008 | 0.07782 | 0.31128 | 0.19684 | 0.33875 | 0.28839 | 122.113 | 122.1497 | -0.52185 | -0.43487 | 121.8521 | 122.0581 | 121.8338 | 122.0032
2020.4531 | 122.1817 | -122.113 | 0.25177 | 0.011063 | -0.056132 | 0.012548 | 0.029384 | 0.0086495 | -0.00086509 | 0.003499 | 0.001648 | 0.012179 | 0.020781 | 0.0093438 | -0.00067933 | 0.0056738 | -0.0024738 | -0.17853 | 0.14191 | -0.27008 | -0.24719 | -0.09613 | -0.24261 | -0.16022 | -0.11444 | 0.18768 | -0.15564 | -0.022888 | 0.036621 | -0.059509 | 0.11444 | 121.843 | -0.10986 | -0.49896 | 122.0169 | 121.9528 | 121.8704 | 0.10986 | 0.027466 | 121.9574 | -0.064087 | -0.27466 | 122.1497 | 122.2275 | 122.0535 | 0.27008 | 0.096131 | 0.17395 | 0.022889 | 0.19226 | 0.13275 | 0.41199 | 0.34332 | 122.2549 | 122.3007 | -0.52185 | -0.40741 | 121.8658 | 122.0901 | 121.9345 | 121.9986
2022.1406 | 122.2916 | -122.0947 | 0.22888 | 0.011063 | -0.057627 | 0.010626 | 0.029384 | 0.0037363 | -0.0055649 | -0.00098695 | 0.0046998 | 0.014529 | 0.021849 | 0.016393 | -0.0028155 | 0.0063148 | -0.00055121 | -0.1236 | 0.19226 | -0.19684 | -0.14191 | 0.032043 | -0.10986 | -0.041199 | -0.036621 | 0.18768 | -0.15564 | 0.013733 | 0.11444 | 0 | 0.14648 | 121.8979 | -0.036621 | -0.37079 | 122.1268 | 122.0535 | 121.9849 | 0.15564 | 0.086975 | 121.9391 | -0.041199 | -0.21515 | 122.2092 | 122.2412 | 122.0947 | 0.30212 | 0.15564 | 0.22888 | 0.054931 | 0.27008 | 0.16937 | 0.3891 | 0.34332 | 122.287 | 122.2824 | -0.42572 | -0.38452 | 121.9528 | 122.1085 | 121.9711 | 122.0581
2023.9062 | 122.4106 | -122.0581 | 0.19684 | 0.0034333 | -0.060404 | 0.012975 | 0.027889 | 0.0035227 | -0.0025741 | -0.0016278 | 0.0046998 | 0.01282 | 0.019927 | 0.012548 | -0.0019611 | 0.0065284 | 0.001585 | -0.13275 | 0.10071 | -0.21515 | -0.10071 | 0.10529 | -0.07782 | 0.027466 | 0.045776 | 0.15106 | -0.13275 | 0.068665 | 0.18768 | 0.10529 | 0.19684 | 121.843 | -0.09613 | -0.29755 | 122.1634 | 122.0856 | 121.9803 | 0.24261 | 0.13733 | 121.9254 | -0.045776 | -0.12817 | 122.2458 | 122.2549 | 122.1634 | 0.32959 | 0.23804 | 0.32044 | 0.11444 | 0.32043 | 0.20142 | 0.31586 | 0.28381 | 122.1588 | 122.2092 | -0.41199 | -0.32959 | 121.9574 | 122.1268 | 121.9254 | 122.1039
2025.6562 | 122.4106 | -122.0856 | 0.20599 | 0.0034333 | -0.062754 | 0.0099848 | 0.029384 | 0.0058725 | -0.0025741 | 0.0011492 | 0.0046998 | 0.011751 | 0.0195 | 0.023229 | -0.00089293 | 0.0080236 | -0.0016192 | -0.14191 | 0.11444 | -0.22888 | -0.1236 | 0.068665 | -0.086975 | 0.004578 | 0.018311 | 0.15564 | -0.13733 | 0.054932 | 0.1831 | 0.11444 | 0.19684 | 121.8567 | -0.091553 | -0.32959 | 122.1542 | 122.0901 | 121.9986 | 0.23346 | 0.14191 | 121.9482 | -0.050354 | -0.15106 | 122.2687 | 122.2824 | 122.2 | 0.33417 | 0.25177 | 0.29755 | 0.10529 | 0.32043 | 0.19226 | 0.34332 | 0.29297 | 122.2 | 122.2412 | -0.43488 | -0.34332 | 121.962 | 122.1405 | 121.9437 | 122.1039
2027.3438 | 122.4472 | -122.0535 | 0.21973 | 0.0034333 | -0.058268 | 0.013616 | 0.031307 | 0.0090767 | -0.0012925 | 0.0011492 | -0.0014038 | 0.014742 | 0.021422 | 0.025793 | 0.0048749 | 0.0058874 | -0.0016192 | -0.13275 | 0.073242 | -0.24719 | -0.14191 | 0.059509 | -0.13275 | -0.054932 | 0.09613 | 0.16022 | -0.086975 | 0.09613 | 0.19226 | 0.082397 | 0.20599 | 121.8063 | -0.14649 | -0.36163 | 122.113 | 121.9986 | 121.9208 | 0.19226 | 0.11444 | 121.9666 | -0.05951 | -0.1236 | 122.2458 | 122.2595 | 122.1359 | 0.29297 | 0.16937 | 0.3067 | 0.10528 | 0.27924 | 0.1831 | 0.32043 | 0.24719 | 122.1268 | 122.2137 | -0.46692 | -0.3067 | 121.9116 | 122.1497 | 121.9208 | 122.1497
2029.0781 | 122.3145 | -122.1542 | 0.22888 | 0.011063 | -0.059336 | 0.010626 | 0.031734 | 0.0033089 | -0.0027877 | -0.0016278 | 0.0046998 | 0.014529 | 0.022063 | 0.01618 | -0.0017475 | 0.0056738 | -0.00076481 | -0.11902 | 0.19226 | -0.20599 | -0.16022 | 0.004578 | -0.11902 | -0.059509 | -0.091553 | 0.20142 | -0.16022 | -0.036621 | 0.059509 | -0.045776 | 0.10986 | 121.9482 | -0.036621 | -0.3891 | 122.1588 | 122.0947 | 122.0352 | 0.14649 | 0.086975 | 121.994 | -0.027466 | -0.2655 | 122.2137 | 122.2641 | 122.1085 | 0.27008 | 0.11444 | 0.21057 | 0.045777 | 0.21973 | 0.1236 | 0.39826 | 0.36163 | 122.3465 | 122.3557 | -0.43488 | -0.3891 | 121.994 | 122.1176 | 122.0352 | 122.0627
2030.8281 | 122.3236 | -122.1222 | 0.22888 | 0.011063 | -0.057627 | 0.013189 | 0.030238 | 0.0045907 | -0.0027877 | 8.125e-05 | 0.0046998 | 0.016451 | 0.021636 | 0.013403 | 0.00081607 | 0.006742 | 0.00073059 | -0.21057 | 0.11902 | -0.28381 | -0.26093 | -0.09613 | -0.26093 | -0.16937 | -0.082397 | 0.16937 | -0.14648 | -0.032043 | 0.050354 | -0.07782 | 0.10986 | 121.8384 | -0.10986 | -0.48981 | 122.0261 | 121.9528 | 121.8613 | 0.11444 | 0.022888 | 121.9757 | -0.059509 | -0.26093 | 122.1725 | 122.2321 | 122.0444 | 0.25635 | 0.068664 | 0.18768 | 0.022888 | 0.19684 | 0.11444 | 0.40283 | 0.31586 | 122.2412 | 122.2916 | -0.5127 | -0.37537 | 121.8613 | 122.0901 | 121.9116 | 122.0398
2032.5781 | 122.319 | -122.1405 | 0.23804 | 0.0034333 | -0.056986 | 0.0099848 | 0.028316 | 0.0035227 | -0.0051377 | 0.00050845 | 0.010803 | 0.014742 | 0.022704 | 0.018102 | -0.0030291 | 0.004392 | 0.0030804 | -0.16479 | 0.16937 | -0.21515 | -0.17853 | 0.027466 | -0.10071 | -0.045776 | -0.082397 | 0.20599 | -0.16022 | -0.059509 | 0.068665 | -0.036621 | 0.082397 | 121.9254 | -0.068664 | -0.41656 | 122.168 | 122.0947 | 122.0398 | 0.16937 | 0.11444 | 121.9803 | -0.032043 | -0.29755 | 122.2092 | 122.2229 | 122.1039 | 0.24261 | 0.1236 | 0.24261 | 0.036621 | 0.22888 | 0.10071 | 0.38452 | 0.36621 | 122.3099 | 122.3465 | -0.45319 | -0.39825 | 121.962 | 122.081 | 121.9757 | 122.0581
2034.3281 | 122.4518 | -122.1039 | 0.19684 | 0.0034333 | -0.058054 | 0.013403 | 0.028316 | 0.0043771 | -0.0034287 | -0.00034615 | 0.0046998 | 0.014101 | 0.0195 | 0.018743 | 0.0031659 | 0.00781 | 0.0011578 | -0.14191 | 0.059509 | -0.26093 | -0.15564 | 0.054932 | -0.12817 | -0.059509 | 0.059509 | 0.14191 | -0.11444 | 0.10529 | 0.17853 | 0.068665 | 0.21057 | 121.843 | -0.13733 | -0.35248 | 122.1588 | 122.0444 | 121.9757 | 0.20142 | 0.13275 | 121.9894 | -0.054931 | -0.091552 | 122.2824 | 122.3145 | 122.1725 | 0.32501 | 0.18311 | 0.31586 | 0.10529 | 0.29297 | 0.21973 | 0.32043 | 0.25635 | 122.1634 | 122.2458 | -0.45776 | -0.31128 | 121.9482 | 122.2092 | 121.962 | 122.1634
2036.0156 | 122.374 | -122.1359 | 0.21057 | 0.018692 | -0.05955 | 0.014684 | 0.032375 | 0.0050179 | -0.0025741 | 0.00050845 | 0.0046998 | 0.013888 | 0.02249 | 0.01383 | 0.0029523 | 0.0065284 | 0.00030339 | -0.19684 | 0.10071 | -0.27924 | -0.24261 | -0.064087 | -0.23346 | -0.14648 | -0.064087 | 0.19226 | -0.16022 | 0.004578 | 0.064087 | -0.054932 | 0.12817 | 121.8567 | -0.10986 | -0.45319 | 122.0718 | 121.9894 | 121.9025 | 0.13275 | 0.045777 | 121.9757 | -0.01831 | -0.20599 | 122.2 | 122.2641 | 122.081 | 0.28839 | 0.10528 | 0.21515 | 0.036621 | 0.2243 | 0.16479 | 0.37994 | 0.35248 | 122.2366 | 122.3282 | -0.48981 | -0.37079 | 121.8933 | 122.1405 | 121.9391 | 122.0718
2037.7656 | 122.4472 | -122.1268 | 0.21973 | 0.0034333 | -0.061259 | 0.014044 | 0.02917 | 0.00095914 | -0.0034287 | 0.003499 | 0.001648 | 0.013033 | 0.021849 | 0.01853 | -0.0030291 | 0.006101 | 0.00094419 | -0.073242 | 0.14191 | -0.19226 | -0.073242 | 0.1236 | -0.027466 | 0.027466 | 0.050354 | 0.13733 | -0.10986 | 0.054932 | 0.16937 | 0.07782 | 0.20142 | 121.9345 | -0.07782 | -0.29297 | 122.2504 | 122.1542 | 122.0993 | 0.21973 | 0.16479 | 122.0169 | -0.082398 | -0.16479 | 122.2961 | 122.3282 | 122.2046 | 0.31128 | 0.18768 | 0.31586 | 0.11902 | 0.27924 | 0.16479 | 0.33417 | 0.24719 | 122.2687 | 122.2641 | -0.41199 | -0.32959 | 122.0535 | 122.1817 | 122.0535 | 122.1771
2039.4531 | 122.374 | -122.1222 | 0.2243 | 0.018692 | -0.058909 | 0.01383 | 0.032588 | 0.0037363 | -0.0023605 | 0.00050845 | 0.0046998 | 0.013888 | 0.022277 | 0.01853 | 0.0020979 | 0.006742 | -0.0018328 | -0.1236 | 0.13733 | -0.23346 | -0.16937 | 0.045776 | -0.13275 | -0.073242 | -0.009155 | 0.17395 | -0.13275 | 0.009155 | 0.091553 | -0.032043 | 0.12817 | 121.8887 | -0.086975 | -0.39368 | 122.168 | 122.049 | 121.9894 | 0.16022 | 0.10071 | 121.9894 | -0.050354 | -0.21515 | 122.2137 | 122.2504 | 122.0901 | 0.26093 | 0.10071 | 0.27924 | 0.064086 | 0.2243 | 0.14191 | 0.37079 | 0.3067 | 122.2595 | 122.2961 | -0.45776 | -0.35706 | 121.9528 | 122.1313 | 121.9986 | 122.113
2041.2031 | 122.3785 | -122.1542 | 0.22888 | 0.0034333 | -0.058054 | 0.014471 | 0.028529 | 0.0030953 | -0.0025741 | 0.0011492 | 0.001648 | 0.014315 | 0.022277 | 0.015325 | 0.00038887 | 0.0058874 | -0.00055121 | -0.11444 | 0.15564 | -0.23346 | -0.15564 | 0.032043 | -0.10986 | -0.054932 | 0.018311 | 0.16937 | -0.13733 | 0.013733 | 0.10986 | 0.004578 | 0.14648 | 121.9208 | -0.073242 | -0.38452 | 122.1863 | 122.0993 | 122.0444 | 0.17853 | 0.1236 | 122.0169 | -0.059509 | -0.21515 | 122.2641 | 122.3007 | 122.1588 | 0.28381 | 0.14191 | 0.2655 | 0.077819 | 0.24719 | 0.15106 | 0.3891 | 0.3067 | 122.3099 | 122.3236 | -0.46234 | -0.36621 | 121.9986 | 122.168 | 122.0398 | 122.1725
2042.9531 | 122.3831 | -122.1725 | 0.2243 | 0.011063 | -0.056986 | 0.013189 | 0.031947 | 0.0030953 | -0.0055649 | 0.0043536 | 0.001648 | 0.014101 | 0.023772 | 0.017462 | -0.0013201 | 0.004392 | 0.0011578 | -0.13275 | 0.13733 | -0.21973 | -0.16479 | 0.022888 | -0.13733 | -0.086975 | -0.027466 | 0.17395 | -0.13733 | 0.009155 | 0.07782 | -0.027466 | 0.11444 | 121.9528 | -0.086975 | -0.3891 | 122.1954 | 122.0856 | 122.0352 | 0.13275 | 0.082398 | 122.0352 | -0.050354 | -0.21515 | 122.2504 | 122.287 | 122.1451 | 0.25177 | 0.10986 | 0.24261 | 0.054932 | 0.21515 | 0.14648 | 0.35706 | 0.31128 | 122.3099 | 122.3465 | -0.44403 | -0.36163 | 122.0078 | 122.1817 | 122.0398 | 122.1451
2044.7031 | 122.3557 | -122.1863 | 0.24261 | -0.0041962 | -0.061472 | 0.011267 | 0.028102 | 0.0022409 | -0.0042831 | -0.00013235 | 0.001648 | 0.013888 | 0.020995 | 0.014471 | -0.0017475 | 0.0056738 | 0.001585 | -0.14648 | 0.18768 | -0.21515 | -0.16022 | 0.027466 | -0.10529 | -0.054932 | -0.10986 | 0.18768 | -0.16022 | -0.050354 | 0.045776 | -0.041199 | 0.09613 | 121.9711 | -0.054932 | -0.40283 | 122.2137 | 122.1313 | 122.081 | 0.16022 | 0.10986 | 122.0261 | -0.054932 | -0.29297 | 122.2321 | 122.2824 | 122.1451 | 0.25635 | 0.11902 | 0.24261 | 0.054932 | 0.20599 | 0.10986 | 0.40283 | 0.3479 | 122.374 | 122.374 | -0.45776 | -0.40283 | 122.0261 | 122.1359 | 122.0398 | 122.0764
2046.3906 | 122.3557 | -122.1909 | 0.21515 | 0.0034333 | -0.060404 | 0.012335 | 0.030452 | 0.0028817 | -0.0040695 | -0.0012006 | 0.001648 | 0.015169 | 0.021636 | 0.020239 | -0.00089293 | 0.006742 | -0.0014056 | -0.19684 | 0.10986 | -0.26093 | -0.24261 | -0.054932 | -0.2243 | -0.16022 | -0.10986 | 0.17395 | -0.15564 | -0.032043 | 0.022888 | -0.09613 | 0.09613 | 121.9299 | -0.10529 | -0.45776 | 122.1359 | 122.0306 | 121.9666 | 0.10071 | 0.036621 | 122.0352 | -0.041199 | -0.24719 | 122.2137 | 122.287 | 122.0947 | 0.25177 | 0.05951 | 0.20599 | 0.01831 | 0.17853 | 0.1236 | 0.37079 | 0.32959 | 122.3007 | 122.3648 | -0.47607 | -0.37079 | 121.9482 | 122.1588 | 121.994 | 122.081
2048.1406 | 122.5067 | -122.1405 | 0.20142 | 0.0034333 | -0.0572 | 0.012975 | 0.030025 | 0.0037363 | -0.0038559 | 0.0015764 | 0.001648 | 0.01346 | 0.019927 | 0.018957 | 0.00081607 | 0.0075964 | -0.0014056 | -0.13275 | 0.064087 | -0.23804 | -0.15564 | 0.050354 | -0.13275 | -0.073242 | 0.086975 | 0.15106 | -0.10529 | 0.10071 | 0.19226 | 0.07782 | 0.21973 | 121.9025 | -0.13733 | -0.35706 | 122.1909 | 122.0673 | 122.0078 | 0.16479 | 0.10529 | 122.0352 | -0.050354 | -0.10071 | 122.3328 | 122.3602 | 122.2183 | 0.32501 | 0.18311 | 0.28839 | 0.082397 | 0.29755 | 0.20599 | 0.30212 | 0.25635 | 122.2046 | 122.2916 | -0.43945 | -0.3067 | 121.9849 | 122.2412 | 122.0078 | 122.2275
2049.8281 | 122.3694 | -122.1909 | 0.22888 | -0.0041962 | -0.058054 | 0.011694 | 0.02917 | 0.0067269 | -0.0012925 | 0.00029485 | 0.0046998 | 0.015169 | 0.021849 | 0.0089166 | 0.00038887 | 0.0071692 | -0.00076481 | -0.16937 | 0.13275 | -0.26093 | -0.23804 | -0.036621 | -0.20142 | -0.14648 | -0.073242 | 0.16937 | -0.14191 | -0.018311 | 0.050354 | -0.054932 | 0.091553 | 121.9299 | -0.096131 | -0.46692 | 122.1542 | 122.0444 | 121.9894 | 0.11444 | 0.059509 | 122.0489 | -0.059509 | -0.24719 | 122.2412 | 122.2824 | 122.1359 | 0.23346 | 0.086975 | 0.2243 | 0.022888 | 0.19226 | 0.1236 | 0.39368 | 0.31128 | 122.3236 | 122.3602 | -0.48981 | -0.37079 | 121.9528 | 122.1725 | 122.0215 | 122.1176
2051.5781 | 122.4472 | -122.1451 | 0.21057 | 0.0034333 | -0.058909 | 0.012335 | 0.028743 | 0.0058725 | -0.0010789 | 0.00050845 | -0.0014038 | 0.01346 | 0.022704 | 0.024511 | 0.0012433 | 0.0080236 | 0.0020124 | -0.15564 | 0.07782 | -0.23804 | -0.16022 | 0.064087 | -0.14191 | -0.050354 | 0.045776 | 0.14648 | -0.12817 | 0.064087 | 0.13275 | 0.041199 | 0.16479 | 121.907 | -0.13275 | -0.37079 | 122.2092 | 122.0947 | 122.0032 | 0.18768 | 0.09613 | 122.0169 | -0.064087 | -0.14648 | 122.2778 | 122.3099 | 122.1863 | 0.29297 | 0.16937 | 0.30212 | 0.07782 | 0.26093 | 0.19226 | 0.31586 | 0.27466 | 122.2229 | 122.2916 | -0.44861 | -0.33875 | 121.9849 | 122.2092 | 121.9894 | 122.1909
2053.3281 | 122.4838 | -122.1771 | 0.20599 | 0.0034333 | -0.058268 | 0.011694 | 0.027034 | 0.0054453 | -0.0025741 | 0.0022174 | -0.0014038 | 0.012392 | 0.021209 | 0.026861 | -0.00025213 | 0.0054602 | 0.0013714 | -0.17395 | 0.10986 | -0.24719 | -0.16937 | 0.032043 | -0.11902 | -0.022888 | -0.004578 | 0.16479 | -0.13275 | 0.036621 | 0.15564 | 0.054932 | 0.17853 | 121.9299 | -0.096131 | -0.37537 | 122.2092 | 122.1542 | 122.0581 | 0.2243 | 0.12817 | 122.0444 | -0.041199 | -0.16937 | 122.3328 | 122.3557 | 122.2321 | 0.31128 | 0.18768 | 0.27924 | 0.077819 | 0.28839 | 0.16937 | 0.35706 | 0.29755 | 122.287 | 122.3419 | -0.45319 | -0.33875 | 122.0078 | 122.2137 | 122.0032 | 122.1725
2055.0781 | 122.3877 | -122.1863 | 0.2243 | 0.011063 | -0.058481 | 0.011694 | 0.031734 | 0.0050179 | -0.0047103 | 0.00050845 | 0.001648 | 0.014742 | 0.021422 | 0.01618 | 0.00038887 | 0.0054602 | -0.0014056 | -0.13275 | 0.14191 | -0.23346 | -0.20599 | -0.018311 | -0.16022 | -0.10986 | -0.045776 | 0.17395 | -0.13733 | -0.022888 | 0.054932 | -0.064087 | 0.10071 | 121.9528 | -0.082397 | -0.4303 | 122.168 | 122.0764 | 122.0261 | 0.1236 | 0.073242 | 122.049 | -0.050354 | -0.24719 | 122.2412 | 122.287 | 122.1222 | 0.23804 | 0.073242 | 0.21515 | 0.027465 | 0.19226 | 0.11444 | 0.37537 | 0.31128 | 122.3282 | 122.3602 | -0.45776 | -0.36163 | 121.9803 | 122.1634 | 122.0535 | 122.1405
2056.7656 | 122.3923 | -122.2366 | 0.23346 | 0.0034333 | -0.060618 | 0.010839 | 0.031093 | 0.0030953 | -0.0019333 | 0.0017902 | 0.001648 | 0.013888 | 0.020995 | 0.01618 | -0.0051653 | 0.0063148 | 0.00051699 | -0.15106 | 0.16937 | -0.20599 | -0.1831 | 0.022888 | -0.10986 | -0.041199 | -0.086975 | 0.20142 | -0.14648 | -0.050354 | 0.064087 | -0.027466 | 0.082397 | 122.0306 | -0.064086 | -0.41656 | 122.2595 | 122.1954 | 122.1268 | 0.1648 | 0.096131 | 122.0901 | -0.032043 | -0.28381 | 122.3007 | 122.319 | 122.2092 | 0.22888 | 0.11902 | 0.22888 | 0.022889 | 0.21057 | 0.09613 | 0.37537 | 0.3479 | 122.406 | 122.438 | -0.43945 | -0.37994 | 122.0535 | 122.1863 | 122.0856 | 122.1497
2058.5156 | 122.5113 | -122.1725 | 0.21515 | 0.011063 | -0.058481 | 0.011694 | 0.02917 | 0.0052315 | -0.0040695 | -0.00034615 | 0.0046998 | 0.013674 | 0.02249 | 0.015112 | -0.0021747 | 0.0039648 | -0.00033761 | -0.09613 | 0.11444 | -0.18768 | -0.059509 | 0.15564 | -0.004578 | 0.054932 | 0.073242 | 0.14191 | -0.11444 | 0.082397 | 0.20142 | 0.11444 | 0.21515 | 121.9849 | -0.10071 | -0.27466 | 122.3282 | 122.2275 | 122.168 | 0.24261 | 0.1831 | 122.0581 | -0.073242 | -0.13275 | 122.374 | 122.3877 | 122.287 | 0.32959 | 0.22888 | 0.34332 | 0.12817 | 0.31586 | 0.19684 | 0.30212 | 0.25635 | 122.287 | 122.3145 | -0.40283 | -0.32959 | 122.113 | 122.2549 | 122.0764 | 122.2458
2060.25 | 122.3923 | -122.1954 | 0.22888 | -0.0041962 | -0.057627 | 0.01383 | 0.032588 | 0.0028817 | -0.0055649 | 0.0030718 | 0.0046998 | 0.014956 | 0.022917 | 0.013403 | 0.00060247 | 0.0052466 | 0.0013714 | -0.20142 | 0.14191 | -0.27466 | -0.25635 | -0.10071 | -0.23346 | -0.16479 | -0.11444 | 0.19226 | -0.15564 | -0.032043 | 0.032043 | -0.07782 | 0.10986 | 121.9208 | -0.086975 | -0.48523 | 122.0947 | 122.0306 | 121.962 | 0.10986 | 0.041199 | 122.0398 | -0.036621 | -0.26093 | 122.2275 | 122.3053 | 122.1176 | 0.2655 | 0.07782 | 0.17395 | 0.01831 | 0.18768 | 0.1236 | 0.41657 | 0.3479 | 122.3373 | 122.3877 | -0.50354 | -0.38452 | 121.9391 | 122.1634 | 121.994 | 122.081
2062 | 122.3969 | -122.2137 | 0.21973 | 0.0034333 | -0.05955 | 0.013403 | 0.028316 | 0.0024545 | -0.0036423 | -0.00098695 | 0.001648 | 0.01581 | 0.023986 | 0.018743 | -0.0032427 | 0.0052466 | -0.0022602 | -0.14191 | 0.2243 | -0.21973 | -0.17395 | 0.009155 | -0.11444 | -0.045776 | -0.09613 | 0.17853 | -0.14648 | -0.036621 | 0.050354 | -0.027466 | 0.09613 | 121.994 | 0.004577 | -0.39368 | 122.2229 | 122.168 | 122.0993 | 0.17395 | 0.10529 | 122.0673 | -0.041199 | -0.25635 | 122.2641 | 122.3099 | 122.1863 | 0.24261 | 0.11902 | 0.22888 | 0.045777 | 0.19684 | 0.10986 | 0.44403 | 0.32501 | 122.438 | 122.3923 | -0.43945 | -0.36621 | 122.0398 | 122.1771 | 122.0718 | 122.1176
2063.6875 | 122.4884 | -122.2092 | 0.20142 | -0.0041962 | -0.055704 | 0.012975 | 0.02917 | 0.0039499 | -0.0025741 | 0.0011492 | 0.0046998 | 0.01346 | 0.019713 | 0.019598 | 0.00060247 | 0.0063148 | 0.00094419 | -0.15564 | 0.064087 | -0.21057 | -0.15564 | 0.059509 | -0.11444 | -0.050354 | 0.064087 | 0.16022 | -0.13275 | 0.059509 | 0.14648 | 0.054932 | 0.16479 | 121.9986 | -0.13733 | -0.35706 | 122.2687 | 122.1588 | 122.0947 | 0.16022 | 0.09613 | 122.0764 | -0.041199 | -0.14191 | 122.3557 | 122.374 | 122.2641 | 0.29755 | 0.18768 | 0.27008 | 0.054931 | 0.27924 | 0.19226 | 0.27466 | 0.29297 | 122.2733 | 122.3694 | -0.41199 | -0.33417 | 122.0535 | 122.2687 | 122.0535 | 122.2733
2065.4375 | 122.5388 | -122.1725 | 0.19684 | 0.011063 | -0.061259 | 0.010198 | 0.029811 | 0.0092905 | -0.0047103 | -0.0014142 | 0.0046998 | 0.014101 | 0.020995 | 0.019598 | -0.0028155 | 0.006742 | -0.0014056 | -0.086975 | 0.11444 | -0.17853 | -0.064087 | 0.16937 | -0.004578 | 0.054932 | 0.091553 | 0.14648 | -0.11902 | 0.091553 | 0.21973 | 0.11444 | 0.19684 | 121.994 | -0.082397 | -0.26093 | 122.3419 | 122.2275 | 122.168 | 0.23346 | 0.17395 | 122.0535 | -0.050354 | -0.10529 | 122.3923 | 122.3694 | 122.287 | 0.31586 | 0.23346 | 0.3479 | 0.11444 | 0.33875 | 0.21057 | 0.29297 | 0.2655 | 122.287 | 122.319 | -0.37537 | -0.31586 | 122.1085 | 122.2641 | 122.0856 | 122.2641
2067.2031 | 122.5433 | -122.1954 | 0.20599 | -0.0041962 | -0.059336 | 0.010839 | 0.029598 | 0.0011727 | -0.0064193 | 0.00029485 | 0.0046998 | 0.012179 | 0.021422 | 0.015325 | -0.0017475 | 0.0041784 | 8.9786e-05 | -0.1236 | 0.12817 | -0.19226 | -0.086975 | 0.11902 | -0.032043 | 0.027466 | 0.059509 | 0.13733 | -0.12817 | 0.091553 | 0.20142 | 0.10986 | 0.2243 | 122.0032 | -0.07782 | -0.29297 | 122.3145 | 122.2229 | 122.1634 | 0.21973 | 0.16022 | 122.0673 | -0.068665 | -0.11444 | 122.3969 | 122.4197 | 122.3053 | 0.35248 | 0.23804 | 0.31128 | 0.10529 | 0.32959 | 0.21973 | 0.32044 | 0.2655 | 122.3236 | 122.3328 | -0.39826 | -0.33417 | 122.1085 | 122.287 | 122.0718 | 122.2549
2068.8906 | 122.5708 | -122.1909 | 0.19226 | -0.0041962 | -0.062968 | 0.0093438 | 0.027461 | 0.0022409 | -0.0038559 | -0.0014142 | 0.0046998 | 0.012179 | 0.020568 | 0.018743 | 0.0012433 | 0.0065284 | 0.00051699 | -0.10071 | 0.1236 | -0.1831 | -0.082397 | 0.12817 | -0.032043 | 0.036621 | 0.07782 | 0.14191 | -0.12817 | 0.091553 | 0.20599 | 0.10529 | 0.21057 | 122.0078 | -0.068665 | -0.27466 | 122.319 | 122.2275 | 122.1588 | 0.21973 | 0.15106 | 122.0627 | -0.050354 | -0.10071 | 122.3969 | 122.4014 | 122.2961 | 0.33875 | 0.23346 | 0.31128 | 0.10071 | 0.33417 | 0.21973 | 0.3067 | 0.27008 | 122.3145 | 122.3328 | -0.37537 | -0.32044 | 122.1085 | 122.2824 | 122.0901 | 122.2687
2070.6406 | 122.4564 | -122.2412 | 0.22888 | 0.0034333 | -0.058695 | 0.011694 | 0.030025 | 0.0015999 | -0.0051377 | -0.0018414 | 0.001648 | 0.014315 | 0.020995 | 0.018316 | -3.8532e-05 | 0.0035376 | 0.002226 | -0.13275 | 0.19684 | -0.21515 | -0.16479 | -0.004578 | -0.12817 | -0.059509 | -0.082397 | 0.1831 | -0.16022 | -0.027466 | 0.07782 | -0.041199 | 0.11444 | 122.0261 | -0.032044 | -0.39368 | 122.2366 | 122.1817 | 122.113 | 0.15564 | 0.086975 | 122.081 | -0.045777 | -0.25635 | 122.319 | 122.3557 | 122.2 | 0.27466 | 0.11902 | 0.21057 | 0.050354 | 0.23804 | 0.13275 | 0.41199 | 0.34332 | 122.438 | 122.4243 | -0.44403 | -0.3891 | 122.0764 | 122.2137 | 122.1085 | 122.1588
2072.3906 | 122.5113 | -122.1817 | 0.2243 | 0.0034333 | -0.059977 | 0.011267 | 0.028957 | 0.0082223 | -0.0021469 | 0.0015764 | -0.0014038 | 0.012392 | 0.023772 | 0.019598 | 0.00081607 | 0.0071692 | -0.00076481 | -0.16022 | 0.10071 | -0.23804 | -0.16479 | 0.032043 | -0.13275 | -0.054932 | -0.022888 | 0.17395 | -0.11902 | 0.027466 | 0.13733 | 0.027466 | 0.15564 | 121.9437 | -0.1236 | -0.3891 | 122.2137 | 122.1268 | 122.049 | 0.1831 | 0.10529 | 122.0627 | -0.050354 | -0.19684 | 122.319 | 122.3373 | 122.2092 | 0.27466 | 0.14649 | 0.27008 | 0.073242 | 0.25635 | 0.14649 | 0.33875 | 0.29297 | 122.2824 | 122.3557 | -0.46234 | -0.34332 | 122.0169 | 122.2092 | 122.0215 | 122.1588
2074.0781 | 122.5204 | -122.2137 | 0.19226 | 0.0034333 | -0.060831 | 0.012335 | 0.030025 | 0.0024545 | -0.0021469 | -0.00013235 | 0.0077514 | 0.013674 | 0.019927 | 0.015325 | -0.0017475 | 0.0069556 | -0.0016192 | -0.091553 | 0.12817 | -0.17395 | -0.054932 | 0.14191 | -0.022888 | 0.045776 | 0.064087 | 0.16022 | -0.11902 | 0.064087 | 0.19226 | 0.086975 | 0.19684 | 122.0398 | -0.064087 | -0.24719 | 122.3557 | 122.2595 | 122.1909 | 0.21973 | 0.15106 | 122.0947 | -0.032044 | -0.12817 | 122.406 | 122.4106 | 122.3007 | 0.31586 | 0.20599 | 0.31586 | 0.11902 | 0.31128 | 0.18311 | 0.30212 | 0.27924 | 122.3419 | 122.374 | -0.36621 | -0.31128 | 122.1588 | 122.2778 | 122.1222 | 122.2778
2075.8281 | 122.438 | -122.2412 | 0.23346 | 0.018692 | -0.060404 | 0.010198 | 0.030879 | 0.00031834 | -0.0038559 | 0.00093565 | 0.0046998 | 0.016451 | 0.02249 | 0.013189 | -0.0013201 | 0.00781 | -0.0022602 | -0.1236 | 0.19684 | -0.20142 | -0.16479 | 0.009155 | -0.1236 | -0.041199 | -0.09613 | 0.19226 | -0.16022 | -0.036621 | 0.068665 | -0.050354 | 0.10529 | 122.0398 | -0.036621 | -0.39825 | 122.2504 | 122.2 | 122.1176 | 0.16022 | 0.07782 | 122.081 | -0.041198 | -0.27008 | 122.3099 | 122.3465 | 122.1909 | 0.2655 | 0.10986 | 0.21057 | 0.036621 | 0.22888 | 0.1236 | 0.39825 | 0.35248 | 122.438 | 122.4335 | -0.43488 | -0.39368 | 122.0764 | 122.2046 | 122.1176 | 122.1451
2077.5781 | 122.438 | -122.2366 | 0.2243 | 0.0034333 | -0.059763 | 0.011907 | 0.033656 | 0.0039499 | 0.0023391 | 0.002431 | -0.0014038 | 0.014956 | 0.0195 | 0.017675 | 0.00017507 | 0.0058874 | -0.00012381 | -0.14648 | 0.13275 | -0.27008 | -0.20142 | -0.018311 | -0.18768 | -0.13275 | -0.050354 | 0.19226 | -0.15106 | -0.022888 | 0.059509 | -0.059509 | 0.091553 | 121.9666 | -0.091553 | -0.42572 | 122.2183 | 122.1039 | 122.0489 | 0.13733 | 0.082398 | 122.0856 | -0.032043 | -0.24719 | 122.2961 | 122.3282 | 122.1771 | 0.24261 | 0.091553 | 0.25177 | 0.068665 | 0.21057 | 0.12817 | 0.40283 | 0.34332 | 122.3694 | 122.4289 | -0.49439 | -0.37537 | 122.0352 | 122.2137 | 122.0901 | 122.1863
2079.2656 | 122.4884 | -122.2321 | 0.21515 | 0.011063 | -0.05955 | 0.012335 | 0.031734 | 0.0069405 | -0.0021469 | 0.0013628 | 0.0046998 | 0.014742 | 0.024413 | 0.01383 | -0.00067933 | 0.0065284 | -0.00097841 | -0.10529 | 0.15106 | -0.21057 | -0.16022 | 0.054932 | -0.10986 | -0.064087 | -0.009155 | 0.17395 | -0.12817 | 0.018311 | 0.11444 | 0 | 0.15106 | 122.0215 | -0.064087 | -0.37537 | 122.287 | 122.168 | 122.1222 | 0.14648 | 0.10071 | 122.1039 | -0.041199 | -0.19684 | 122.3465 | 122.3831 | 122.2321 | 0.27924 | 0.12817 | 0.2655 | 0.050354 | 0.24262 | 0.14649 | 0.36163 | 0.30212 | 122.3831 | 122.406 | -0.42572 | -0.34332 | 122.0718 | 122.2504 | 122.1268 | 122.2229
2081.0312 | 122.4426 | -122.2641 | 0.21973 | 0.0034333 | -0.058268 | 0.013616 | 0.030879 | 0.0022409 | -0.0062057 | 0.00050845 | 0.010803 | 0.015383 | 0.021636 | 0.018316 | -0.0028155 | 0.0046058 | -0.00055121 | -0.13733 | 0.17395 | -0.19684 | -0.15564 | 0.013733 | -0.10071 | -0.036621 | -0.064087 | 0.17853 | -0.14191 | -0.032043 | 0.07782 | -0.041199 | 0.073242 | 122.0673 | -0.045777 | -0.37537 | 122.2778 | 122.2275 | 122.1634 | 0.16022 | 0.09613 | 122.1222 | -0.041199 | -0.25177 | 122.3419 | 122.3373 | 122.2229 | 0.21515 | 0.10071 | 0.21057 | 0.041198 | 0.21973 | 0.10986 | 0.37079 | 0.32044 | 122.438 | 122.4426 | -0.41657 | -0.36163 | 122.1085 | 122.2321 | 122.1268 | 122.2
2082.7656 | 122.4472 | -122.2687 | 0.23346 | 0.0034333 | -0.058268 | 0.012121 | 0.033229 | 0.0020273 | -0.0036423 | 0.0020038 | 0.0046998 | 0.016451 | 0.021209 | 0.008703 | 0.00017507 | 0.005033 | -0.0016192 | -0.12817 | 0.13275 | -0.21973 | -0.17853 | 0.022888 | -0.14191 | -0.09613 | -0.018311 | 0.19684 | -0.13275 | 0 | 0.059509 | -0.041199 | 0.11444 | 122.0489 | -0.10071 | -0.41199 | 122.2916 | 122.1725 | 122.1268 | 0.1236 | 0.07782 | 122.1359 | -0.036621 | -0.23346 | 122.3282 | 122.3831 | 122.2275 | 0.24719 | 0.091552 | 0.24261 | 0.041199 | 0.19226 | 0.13275 | 0.35248 | 0.32959 | 122.4014 | 122.4655 | -0.45319 | -0.36621 | 122.0901 | 122.2687 | 122.1405 | 122.2504
2084.5156 | 122.4472 | -122.2687 | 0.22888 | 0.0034333 | -0.060618 | 0.010626 | 0.030025 | 0.00074554 | -0.0038559 | -0.0022688 | -0.0044556 | 0.011965 | 0.021849 | 0.020025 | -0.0036701 | 0.0028968 | 8.9786e-05 | -0.13733 | 0.21973 | -0.20142 | -0.19226 | 0.027466 | -0.11444 | -0.041199 | -0.11444 | 0.20142 | -0.16479 | -0.036621 | 0.059509 | -0.041199 | 0.10986 | 122.0673 | -0.009155 | -0.42114 | 122.2961 | 122.2275 | 122.1542 | 0.16022 | 0.086975 | 122.1039 | -0.027466 | -0.2655 | 122.3282 | 122.3785 | 122.2275 | 0.27466 | 0.1236 | 0.22888 | 0.009155 | 0.2243 | 0.12817 | 0.42114 | 0.36621 | 122.4884 | 122.4701 | -0.4303 | -0.39368 | 122.0764 | 122.2321 | 122.1313 | 122.1542
2086.2031 | 122.493 | -122.2549 | 0.21973 | 0.011063 | -0.059122 | 0.010839 | 0.029384 | 0.0033089 | -0.0040695 | 0.00029485 | 0.001648 | 0.014315 | 0.022063 | 0.010412 | 0.00081607 | 0.0039648 | 0.0030804 | -0.10986 | 0.19684 | -0.21515 | -0.17395 | 0.027466 | -0.10529 | -0.059509 | -0.022888 | 0.19684 | -0.13275 | 0.009155 | 0.10071 | 0.009155 | 0.15106 | 122.0398 | -0.022889 | -0.39368 | 122.2824 | 122.1954 | 122.1497 | 0.15564 | 0.10986 | 122.1222 | -0.022889 | -0.21057 | 122.3557 | 122.406 | 122.2641 | 0.28381 | 0.14191 | 0.24261 | 0.041199 | 0.23346 | 0.14191 | 0.41199 | 0.32959 | 122.4518 | 122.4518 | -0.43488 | -0.35248 | 122.081 | 122.2641 | 122.1451 | 122.2321
2087.9531 | 122.5891 | -122.2092 | 0.1831 | 0.018692 | -0.061686 | 0.014684 | 0.029811 | 0.0022409 | -0.0015061 | -0.00077335 | 0.0077514 | 0.010897 | 0.02249 | 0.01853 | 0.0023115 | 0.006742 | 0.005003 | -0.13733 | 0.07782 | -0.24719 | -0.14191 | 0.07782 | -0.1236 | -0.050354 | 0.082397 | 0.13733 | -0.10529 | 0.10986 | 0.20142 | 0.068665 | 0.21515 | 121.962 | -0.10528 | -0.32501 | 122.287 | 122.1588 | 122.0856 | 0.19684 | 0.1236 | 122.1039 | -0.045776 | -0.073242 | 122.4106 | 122.4243 | 122.2778 | 0.32044 | 0.17395 | 0.32501 | 0.10528 | 0.3067 | 0.21515 | 0.32501 | 0.24262 | 122.287 | 122.3465 | -0.4303 | -0.28839 | 122.0673 | 122.319 | 122.0718 | 122.2916
2089.7188 | 122.5891 | -122.2183 | 0.19684 | 0.0034333 | -0.06019 | 0.011694 | 0.031093 | 0.0067269 | -0.0047103 | -0.0033368 | 0.001648 | 0.011538 | 0.021422 | 0.017675 | 0.0029523 | 0.0082374 | 0.0024396 | -0.14191 | 0.073242 | -0.24719 | -0.15106 | 0.041199 | -0.13275 | -0.045776 | 0.073242 | 0.16022 | -0.11444 | 0.10529 | 0.17853 | 0.064087 | 0.21973 | 121.9711 | -0.1236 | -0.3479 | 122.2595 | 122.1725 | 122.0856 | 0.20142 | 0.11444 | 122.1039 | -0.036621 | -0.091552 | 122.3969 | 122.4381 | 122.2824 | 0.33417 | 0.17853 | 0.28839 | 0.09613 | 0.29297 | 0.21973 | 0.32043 | 0.27466 | 122.2916 | 122.3785 | -0.44403 | -0.31128 | 122.0673 | 122.3236 | 122.0764 | 122.2916
2091.4062 | 122.5616 | -122.2366 | 0.18768 | 0.018692 | -0.060404 | 0.014898 | 0.028529 | 0.0024545 | -0.0025741 | 0.00093565 | 0.001648 | 0.01346 | 0.019713 | 0.017034 | -0.00089293 | 0.009519 | -0.00055121 | -0.13275 | 0.059509 | -0.24261 | -0.1236 | 0.091553 | -0.10529 | -0.036621 | 0.086975 | 0.14191 | -0.09613 | 0.082397 | 0.17395 | 0.068665 | 0.19684 | 121.994 | -0.12817 | -0.31128 | 122.3282 | 122.2 | 122.1313 | 0.20599 | 0.13733 | 122.1405 | -0.045776 | -0.10529 | 122.4106 | 122.4335 | 122.3053 | 0.29297 | 0.16479 | 0.33417 | 0.11902 | 0.27008 | 0.17853 | 0.30212 | 0.23804 | 122.2961 | 122.3785 | -0.4303 | -0.28381 | 122.113 | 122.319 | 122.1039 | 122.3236
2093.1562 | 122.5388 | -122.287 | 0.19684 | -0.0041962 | -0.058268 | 0.012335 | 0.031093 | 0.00074554 | -0.0032151 | -0.00034615 | 0.001648 | 0.013674 | 0.0195 | 0.017675 | -0.0047381 | 0.0054602 | -0.001192 | -0.086975 | 0.15564 | -0.20142 | -0.064087 | 0.14648 | -0.009155 | 0.045776 | 0.045776 | 0.17395 | -0.1236 | 0.041199 | 0.15106 | 0.073242 | 0.17853 | 122.0856 | -0.041198 | -0.26093 | 122.4335 | 122.3328 | 122.2778 | 0.24719 | 0.19226 | 122.1634 | -0.022888 | -0.15564 | 122.438 | 122.4655 | 122.3602 | 0.30212 | 0.19684 | 0.3479 | 0.13733 | 0.27466 | 0.16479 | 0.35706 | 0.29755 | 122.4426 | 122.4609 | -0.39825 | -0.32043 | 122.2229 | 122.3282 | 122.2 | 122.3328
2094.9062 | 122.4609 | -122.2824 | 0.2243 | 0.0034333 | -0.057413 | 0.013189 | 0.029598 | 0.0030953 | -0.0023605 | 0.00093565 | 0.001648 | 0.017092 | 0.021636 | 0.016393 | 0.0018841 | 0.0071692 | -0.0014056 | -0.18768 | 0.1236 | -0.2655 | -0.24261 | -0.091553 | -0.23804 | -0.15106 | -0.091553 | 0.20142 | -0.14191 | -0.027466 | 0.027466 | -0.064087 | 0.10071 | 122.0169 | -0.10071 | -0.46692 | 122.1909 | 122.1313 | 122.0444 | 0.11444 | 0.027466 | 122.1405 | -0.022888 | -0.25177 | 122.3099 | 122.3831 | 122.2183 | 0.24262 | 0.07782 | 0.17395 | 0.022888 | 0.16937 | 0.11444 | 0.3891 | 0.34332 | 122.406 | 122.4838 | -0.48981 | -0.36621 | 122.0398 | 122.2549 | 122.0947 | 122.1909
2096.5938 | 122.4701 | -122.2778 | 0.21515 | 0.018692 | -0.058909 | 0.011907 | 0.030025 | 0.0020273 | -0.0049241 | -0.00013235 | 0.0077514 | 0.014101 | 0.021849 | 0.015753 | -0.0013201 | 0.0058874 | 0.00051699 | -0.12817 | 0.20599 | -0.19684 | -0.17853 | 0.004578 | -0.10071 | -0.045776 | -0.082397 | 0.19684 | -0.16937 | -0.032043 | 0.050354 | -0.036621 | 0.09613 | 122.081 | -0.009155 | -0.39368 | 122.2824 | 122.2321 | 122.1771 | 0.15106 | 0.09613 | 122.1085 | -0.018311 | -0.24719 | 122.3282 | 122.374 | 122.2412 | 0.2655 | 0.13275 | 0.20142 | 0.01831 | 0.21973 | 0.13733 | 0.40283 | 0.36621 | 122.4838 | 122.4747 | -0.41199 | -0.38452 | 122.0993 | 122.2458 | 122.1497 | 122.1954
2098.2812 | 122.5021 | -122.2961 | 0.22888 | 0.011063 | -0.061472 | 0.013403 | 0.028316 | 0.0018137 | -0.0040695 | 0.00072205 | 0.0046998 | 0.014742 | 0.022277 | 0.018957 | -0.0028155 | 0.006742 | -0.00076481 | -0.064087 | 0.15106 | -0.16479 | -0.086975 | 0.11902 | -0.009155 | 0.032043 | 0 | 0.16479 | -0.13275 | 0.009155 | 0.11902 | 0 | 0.13275 | 122.1313 | -0.07782 | -0.31586 | 122.4152 | 122.3282 | 122.287 | 0.19684 | 0.15564 | 122.1634 | -0.064087 | -0.21973 | 122.4152 | 122.4289 | 122.2961 | 0.2655 | 0.13275 | 0.28381 | 0.07782 | 0.25177 | 0.14191 | 0.31586 | 0.29755 | 122.4472 | 122.4609 | -0.39368 | -0.36163 | 122.2092 | 122.3053 | 122.2321 | 122.2961
2100.0469 | 122.5296 | -122.2916 | 0.23804 | -0.0041962 | -0.057841 | 0.011267 | 0.029598 | 0.0050179 | -0.0044967 | 0.0015764 | 0.001648 | 0.013674 | 0.0195 | 0.011266 | 0.00060247 | 0.0063148 | -0.0026874 | -0.10986 | 0.1831 | -0.21515 | -0.13275 | 0.032043 | -0.091553 | -0.041199 | -0.036621 | 0.1831 | -0.14191 | 0.004578 | 0.11444 | 0.004578 | 0.14191 | 122.0764 | -0.054932 | -0.37079 | 122.3236 | 122.2504 | 122.2 | 0.17395 | 0.1236 | 122.1497 | -0.054932 | -0.23346 | 122.406 | 122.4335 | 122.2961 | 0.28381 | 0.14649 | 0.24719 | 0.082398 | 0.25635 | 0.14649 | 0.39825 | 0.32501 | 122.4747 | 122.4747 | -0.45319 | -0.37994 | 122.1588 | 122.2961 | 122.1817 | 122.2549
2101.7969 | 122.4884 | -122.3099 | 0.22888 | 0.011063 | -0.05955 | 0.013403 | 0.031093 | 0.0073679 | -0.0027877 | 0.00029485 | -0.0014038 | 0.014742 | 0.021422 | 0.016821 | -3.8532e-05 | 0.0073828 | -0.0026874 | -0.14191 | 0.13733 | -0.24719 | -0.2243 | -0.032043 | -0.20142 | -0.11444 | -0.068665 | 0.20142 | -0.14191 | -0.032043 | 0.027466 | -0.064087 | 0.09613 | 122.0627 | -0.091553 | -0.45319 | 122.2778 | 122.1954 | 122.1085 | 0.13275 | 0.045776 | 122.168 | -0.027466 | -0.26093 | 122.3373 | 122.406 | 122.2458 | 0.23804 | 0.07782 | 0.21515 | 0.022888 | 0.16937 | 0.10986 | 0.38452 | 0.34332 | 122.4472 | 122.5113 | -0.47607 | -0.37079 | 122.0856 | 122.2778 | 122.168 | 122.2412
2103.5469 | 122.4884 | -122.319 | 0.22888 | -0.0041962 | -0.060404 | 0.012121 | 0.029384 | 0.0018137 | -0.0038559 | -0.00013235 | -0.0014038 | 0.01282 | 0.020995 | 0.017675 | -0.0038837 | 0.005033 | 0.0035078 | -0.15106 | 0.19226 | -0.1831 | -0.17395 | 0.032043 | -0.11444 | -0.036621 | -0.091553 | 0.19684 | -0.13733 | -0.045776 | 0.068665 | -0.022888 | 0.086975 | 122.1359 | -0.036621 | -0.40283 | 122.3511 | 122.2824 | 122.2046 | 0.14648 | 0.068664 | 122.1817 | -0.032044 | -0.27466 | 122.3877 | 122.406 | 122.2961 | 0.2243 | 0.11444 | 0.21515 | 0.009155 | 0.20599 | 0.091553 | 0.37537 | 0.33417 | 122.5113 | 122.5159 | -0.41199 | -0.36621 | 122.1451 | 122.2733 | 122.168 | 122.2275
2105.2344 | 122.493 | -122.3328 | 0.2655 | -0.0041962 | -0.0572 | 0.010198 | 0.030238 | -0.00074986 | -0.0047103 | 0.00029485 | 0.001648 | 0.014315 | 0.021209 | 0.01853 | -0.0023883 | 0.005033 | 0.0030804 | -0.13275 | 0.21057 | -0.17853 | -0.16937 | 0.027466 | -0.091553 | -0.018311 | -0.10071 | 0.20599 | -0.14191 | -0.041199 | 0.045776 | -0.050354 | 0.10071 | 122.1542 | -0.054932 | -0.43488 | 122.3602 | 122.3145 | 122.2412 | 0.16022 | 0.086975 | 122.1909 | -0.059509 | -0.3067 | 122.3785 | 122.4335 | 122.2824 | 0.24262 | 0.091553 | 0.20599 | 0.009155 | 0.18768 | 0.10071 | 0.3891 | 0.3479 | 122.5433 | 122.5388 | -0.44403 | -0.40741 | 122.1634 | 122.2916 | 122.2 | 122.2321
2106.9844 | 122.5754 | -122.2916 | 0.19684 | 0.018692 | -0.061686 | 0.012335 | 0.027034 | 0.0033089 | -0.00065149 | 0.0011492 | 0.0077514 | 0.011111 | 0.020781 | 0.027288 | 0.0038067 | 0.005033 | 0.0041486 | -0.16022 | 0.068665 | -0.21973 | -0.14191 | 0.091553 | -0.11444 | -0.027466 | 0.068665 | 0.15106 | -0.11444 | 0.068665 | 0.15564 | 0.041199 | 0.17395 | 122.0718 | -0.12817 | -0.33875 | 122.3831 | 122.2641 | 122.1771 | 0.19226 | 0.10529 | 122.1771 | -0.045776 | -0.12817 | 122.4472 | 122.4655 | 122.3328 | 0.28839 | 0.15564 | 0.31128 | 0.07782 | 0.27008 | 0.18311 | 0.28839 | 0.2655 | 122.3602 | 122.4426 | -0.41657 | -0.31128 | 122.1497 | 122.3602 | 122.1313 | 122.3602
2108.7344 | 122.58 | -122.2824 | 0.21515 | 0.0034333 | -0.060831 | 0.010839 | 0.028957 | 0.0030953 | -0.0055649 | -0.0016278 | 0.001648 | 0.011538 | 0.019927 | 0.018102 | 0.0016705 | 0.0046058 | 8.9786e-05 | -0.15106 | 0.10529 | -0.21057 | -0.16022 | 0.036621 | -0.11902 | -0.041199 | -0.032043 | 0.16937 | -0.1236 | 0.027466 | 0.11902 | 0.018311 | 0.15106 | 122.0718 | -0.10986 | -0.37537 | 122.319 | 122.2412 | 122.1634 | 0.16937 | 0.091552 | 122.1588 | -0.045776 | -0.18768 | 122.4014 | 122.4335 | 122.3007 | 0.27466 | 0.14191 | 0.24719 | 0.050354 | 0.24261 | 0.15106 | 0.31586 | 0.29297 | 122.3877 | 122.4518 | -0.42572 | -0.33875 | 122.1222 | 122.3099 | 122.1313 | 122.2504
2110.4375 | 122.5983 | -122.2916 | 0.20599 | 0.011063 | -0.06019 | 0.012762 | 0.028102 | 0.0054453 | -0.0025741 | 0.00050845 | 0.0046998 | 0.015169 | 0.022063 | 0.023229 | -0.0015337 | 0.0056738 | 0.0020124 | -0.16022 | 0.10071 | -0.22888 | -0.14191 | 0.041199 | -0.10529 | -0.013733 | 0.004578 | 0.14648 | -0.13275 | 0.059509 | 0.16479 | 0.073242 | 0.18768 | 122.0627 | -0.10529 | -0.3479 | 122.3328 | 122.2778 | 122.1863 | 0.21515 | 0.1236 | 122.1588 | -0.05951 | -0.14649 | 122.4564 | 122.4792 | 122.3648 | 0.32043 | 0.20599 | 0.27008 | 0.086975 | 0.29755 | 0.19226 | 0.32959 | 0.27924 | 122.3923 | 122.438 | -0.43488 | -0.33875 | 122.1497 | 122.3511 | 122.1313 | 122.2961
2112.1875 | 122.5342 | -122.3007 | 0.20599 | 0.0034333 | -0.059122 | 0.011267 | 0.03152 | 0.0035227 | -0.0021469 | -0.00055975 | 0.001648 | 0.014742 | 0.022277 | 0.021307 | 0.0040205 | 0.0073828 | 0.00030339 | -0.19226 | 0.12817 | -0.27008 | -0.23804 | -0.054932 | -0.20142 | -0.1236 | -0.054932 | 0.17853 | -0.14191 | 0 | 0.073242 | -0.045776 | 0.1236 | 122.0306 | -0.07782 | -0.44403 | 122.2458 | 122.1771 | 122.0993 | 0.14649 | 0.068665 | 122.1588 | -0.027466 | -0.20599 | 122.374 | 122.4243 | 122.2549 | 0.2655 | 0.096131 | 0.21515 | 0.032044 | 0.21515 | 0.14191 | 0.39826 | 0.32044 | 122.4289 | 122.4792 | -0.47608 | -0.3479 | 122.0627 | 122.3007 | 122.1085 | 122.2458
2113.9531 | 122.5388 | -122.3511 | 0.21515 | 0.0034333 | -0.059763 | 0.012121 | 0.031093 | 0.0060861 | -0.00043789 | 0.00072205 | 0.0046998 | 0.014315 | 0.02014 | 0.015325 | 0.0025251 | 0.0058874 | -0.0022602 | -0.17853 | 0.12817 | -0.26093 | -0.24261 | -0.050354 | -0.22888 | -0.1236 | -0.050354 | 0.18768 | -0.13733 | -0.004578 | 0.073242 | -0.050354 | 0.13733 | 122.0901 | -0.086975 | -0.45776 | 122.3007 | 122.2275 | 122.1222 | 0.13733 | 0.032043 | 122.2137 | -0.027466 | -0.21973 | 122.4243 | 122.4884 | 122.3007 | 0.27466 | 0.086975 | 0.21057 | 0.01831 | 0.21057 | 0.13275 | 0.3891 | 0.32501 | 122.4792 | 122.5388 | -0.47607 | -0.35248 | 122.1085 | 122.3465 | 122.1725 | 122.3007
2115.7031 | 122.6395 | -122.3099 | 0.1831 | 0.018692 | -0.059977 | 0.013616 | 0.026393 | 0.0060861 | -0.0036423 | 0.00029485 | 0.0046998 | 0.014315 | 0.022704 | 0.018957 | -0.00046573 | 0.0080236 | -0.00012381 | -0.14191 | 0.11444 | -0.22888 | -0.11902 | 0.07782 | -0.073242 | 0.018311 | 0.027466 | 0.15564 | -0.1236 | 0.068665 | 0.19684 | 0.07782 | 0.21057 | 122.081 | -0.068664 | -0.30212 | 122.3877 | 122.3282 | 122.2366 | 0.24719 | 0.15564 | 122.1863 | -0.027465 | -0.11444 | 122.5067 | 122.5204 | 122.3877 | 0.33417 | 0.20142 | 0.3067 | 0.10986 | 0.32043 | 0.19226 | 0.34332 | 0.27924 | 122.4243 | 122.4655 | -0.41199 | -0.3067 | 122.1909 | 122.3785 | 122.168 | 122.3373
2117.3906 | 122.5296 | -122.3328 | 0.20599 | 0.011063 | -0.058695 | 0.012121 | 0.031307 | 0.0033089 | -0.0012925 | 0.0011492 | 0.001648 | 0.014956 | 0.021209 | 0.017034 | -0.00046573 | 0.006742 | 0.00051699 | -0.18768 | 0.12817 | -0.2655 | -0.24261 | -0.10529 | -0.23346 | -0.14648 | -0.091553 | 0.18768 | -0.14648 | -0.032043 | 0.027466 | -0.07782 | 0.10071 | 122.0673 | -0.07782 | -0.44861 | 122.2275 | 122.1863 | 122.0993 | 0.11902 | 0.032044 | 122.1863 | -0.018311 | -0.23804 | 122.3602 | 122.4335 | 122.2549 | 0.24719 | 0.068664 | 0.16022 | 0.022888 | 0.17395 | 0.11444 | 0.39368 | 0.33417 | 122.4609 | 122.5204 | -0.4715 | -0.35248 | 122.0901 | 122.3007 | 122.1451 | 122.2412
2119.1406 | 122.6212 | -122.2916 | 0.20142 | -0.0041962 | -0.058481 | 0.013403 | 0.029598 | 0.0028817 | -0.0042831 | -0.0018414 | 0.0046998 | 0.01346 | 0.021209 | 0.020025 | 0.0023115 | 0.0073828 | -0.0018328 | -0.17395 | 0.10071 | -0.25635 | -0.18768 | 0.009155 | -0.17853 | -0.091553 | 0.036621 | 0.17395 | -0.1236 | 0.086975 | 0.16022 | 0.050354 | 0.21515 | 122.0352 | -0.10071 | -0.3891 | 122.3007 | 122.2 | 122.113 | 0.1648 | 0.07782 | 122.168 | -0.027466 | -0.11444 | 122.4518 | 122.5067 | 122.3419 | 0.33875 | 0.17395 | 0.2655 | 0.068665 | 0.28381 | 0.21057 | 0.35706 | 0.29755 | 122.3923 | 122.4655 | -0.45776 | -0.32501 | 122.1039 | 122.3785 | 122.1176 | 122.3282
2120.8906 | 122.6578 | -122.3007 | 0.20599 | 0.011063 | -0.061686 | 0.013403 | 0.027889 | -0.00074986 | -0.0027877 | 0.0017902 | 0.001648 | 0.012606 | 0.021849 | 0.017675 | -0.0015337 | 0.0075964 | 0.00094419 | -0.10529 | 0.12817 | -0.18768 | -0.059509 | 0.15564 | -0.004578 | 0.050354 | 0.11444 | 0.15564 | -0.1236 | 0.10071 | 0.20599 | 0.13733 | 0.21057 | 122.113 | -0.07782 | -0.2655 | 122.4564 | 122.3511 | 122.2961 | 0.23804 | 0.1831 | 122.1771 | -0.050354 | -0.10529 | 122.5067 | 122.5113 | 122.438 | 0.33417 | 0.26093 | 0.34332 | 0.12817 | 0.32959 | 0.2243 | 0.31586 | 0.27924 | 122.4289 | 122.4564 | -0.39368 | -0.32959 | 122.2412 | 122.4014 | 122.1954 | 122.4152
2122.5781 | 122.6074 | -122.319 | 0.21057 | 0.011063 | -0.055918 | 0.013616 | 0.028743 | 0.00053194 | -0.0032151 | 0.00050845 | 0.0046998 | 0.014956 | 0.021849 | 0.018316 | -0.0013201 | 0.0075964 | -0.00033761 | -0.15106 | 0.09613 | -0.21973 | -0.14191 | 0.054932 | -0.13275 | -0.059509 | -0.004578 | 0.14191 | -0.10986 | 0.041199 | 0.12817 | 0.027466 | 0.15106 | 122.0993 | -0.11444 | -0.35248 | 122.374 | 122.2595 | 122.1863 | 0.16022 | 0.086976 | 122.2092 | -0.068664 | -0.16937 | 122.4472 | 122.4701 | 122.3465 | 0.26093 | 0.13733 | 0.27466 | 0.07782 | 0.23804 | 0.15106 | 0.31586 | 0.25177 | 122.4152 | 122.4609 | -0.4303 | -0.32043 | 122.1771 | 122.3602 | 122.168 | 122.3145
2124.3438 | 122.6624 | -122.3236 | 0.19684 | 0.0034333 | -0.059122 | 0.011694 | 0.028743 | 0.0058725 | -0.0025741 | 8.125e-05 | 0.001648 | 0.012179 | 0.020995 | 0.020452 | -0.0034563 | 0.006101 | -0.0022602 | -0.13275 | 0.13275 | -0.20142 | -0.10529 | 0.10986 | -0.045776 | 0.036621 | 0.041199 | 0.13733 | -0.11902 | 0.07782 | 0.1831 | 0.091553 | 0.20142 | 122.1222 | -0.064087 | -0.30212 | 122.4335 | 122.3602 | 122.2778 | 0.23804 | 0.15564 | 122.2046 | -0.059509 | -0.11902 | 122.5067 | 122.525 | 122.4152 | 0.32044 | 0.21057 | 0.31128 | 0.09613 | 0.30212 | 0.19684 | 0.33417 | 0.25635 | 122.4564 | 122.4609 | -0.39825 | -0.31586 | 122.2183 | 122.4014 | 122.1909 | 122.3648
2126.0938 | 122.6395 | -122.3145 | 0.19226 | 0.026321 | -0.057841 | 0.01148 | 0.02917 | 0.0054453 | -0.0019333 | 0.002431 | -0.0044556 | 0.014101 | 0.02249 | 0.017675 | 0.00060247 | 0.006742 | -0.00076481 | -0.11902 | 0.059509 | -0.23346 | -0.10986 | 0.091553 | -0.10071 | -0.004578 | 0.064087 | 0.15106 | -0.1236 | 0.086975 | 0.16022 | 0.073242 | 0.1831 | 122.081 | -0.13275 | -0.30212 | 122.406 | 122.3099 | 122.2137 | 0.22888 | 0.13275 | 122.1909 | -0.041199 | -0.10529 | 122.4747 | 122.4976 | 122.3877 | 0.3067 | 0.19684 | 0.32501 | 0.1236 | 0.28381 | 0.21057 | 0.29297 | 0.27466 | 122.374 | 122.4655 | -0.42572 | -0.31586 | 122.2046 | 122.4014 | 122.1954 | 122.3785
2127.8438 | 122.5708 | -122.3419 | 0.20142 | 0.0034333 | -0.059122 | 0.013403 | 0.02917 | 0.0052315 | -0.0034287 | 0.00050845 | 0.0046998 | 0.01581 | 0.021209 | 0.011907 | 0.0012433 | 0.0048194 | 0.0020124 | -0.10986 | 0.15564 | -0.21973 | -0.1236 | 0.054932 | -0.10071 | -0.068665 | 0 | 0.19226 | -0.12817 | 0.022888 | 0.09613 | -0.009155 | 0.15564 | 122.1222 | -0.045776 | -0.32501 | 122.3969 | 122.2733 | 122.2412 | 0.15106 | 0.11902 | 122.2137 | -0.009155 | -0.17853 | 122.438 | 122.4976 | 122.3328 | 0.28381 | 0.11902 | 0.27466 | 0.096131 | 0.2243 | 0.15106 | 0.37537 | 0.32044 | 122.4976 | 122.5342 | -0.42114 | -0.32959 | 122.2183 | 122.3648 | 122.2321 | 122.3419
2129.5469 | 122.5845 | -122.3419 | 0.22888 | 0.0034333 | -0.060404 | 0.012121 | 0.028529 | 0.0054453 | -0.0049241 | 0.0020038 | 0.001648 | 0.016451 | 0.020781 | 0.01853 | -0.0036701 | 0.0056738 | 0.00030339 | -0.12817 | 0.20142 | -0.19226 | -0.12817 | 0.027466 | -0.086975 | -0.045776 | -0.036621 | 0.19684 | -0.14191 | 0 | 0.09613 | -0.004578 | 0.13733 | 122.1497 | -0.027466 | -0.35706 | 122.3694 | 122.2961 | 122.2549 | 0.14648 | 0.10529 | 122.2 | -0.032044 | -0.22888 | 122.438 | 122.4792 | 122.3373 | 0.27924 | 0.13733 | 0.21973 | 0.064087 | 0.23804 | 0.14191 | 0.39368 | 0.33875 | 122.5433 | 122.5388 | -0.42114 | -0.37079 | 122.2137 | 122.3419 | 122.2137 | 122.3053
2131.2969 | 122.644 | -122.3145 | 0.20142 | 0.0034333 | -0.060831 | 0.011907 | 0.027248 | -0.00096346 | -0.0010789 | -0.00034615 | 0.001648 | 0.011965 | 0.020995 | 0.023657 | -0.0017475 | 0.0063148 | -0.002901 | -0.15564 | 0.13275 | -0.22888 | -0.12817 | 0.059509 | -0.09613 | -0.013733 | -0.009155 | 0.16479 | -0.13275 | 0.041199 | 0.13733 | 0.086975 | 0.17395 | 122.0856 | -0.068665 | -0.32959 | 122.374 | 122.3007 | 122.2183 | 0.21515 | 0.13275 | 122.1817 | -0.036621 | -0.16022 | 122.4518 | 122.4884 | 122.4014 | 0.3067 | 0.21973 | 0.28839 | 0.10071 | 0.27008 | 0.17395 | 0.36163 | 0.29755 | 122.4472 | 122.4792 | -0.4303 | -0.33417 | 122.1863 | 122.3557 | 122.1588 | 122.3053
2133.0469 | 122.5296 | -122.3511 | 0.22888 | 0.0034333 | -0.059122 | 0.010839 | 0.030025 | 0.0052315 | -0.0055649 | -0.00013235 | -0.0014038 | 0.013888 | 0.021849 | 0.016607 | -0.0047381 | 0.0037512 | 0.00030339 | -0.14648 | 0.18768 | -0.19684 | -0.16022 | 0.036621 | -0.11444 | -0.032043 | -0.073242 | 0.18768 | -0.14648 | -0.050354 | 0.045776 | -0.036621 | 0.09613 | 122.1542 | -0.041199 | -0.3891 | 122.3877 | 122.319 | 122.2366 | 0.1648 | 0.082397 | 122.2046 | -0.041199 | -0.27924 | 122.3969 | 122.4472 | 122.3145 | 0.24261 | 0.10986 | 0.23346 | 0.036621 | 0.19226 | 0.09613 | 0.38452 | 0.33417 | 122.5388 | 122.5388 | -0.42572 | -0.37537 | 122.1909 | 122.3007 | 122.2046 | 122.2778
2134.8125 | 122.5388 | -122.3831 | 0.23346 | 0.011063 | -0.058909 | 0.011053 | 0.029811 | 0.00074554 | -0.0034287 | 0.00072205 | 0.0046998 | 0.015169 | 0.023131 | 0.01383 | -0.0030291 | 0.0048194 | -0.001192 | -0.14191 | 0.18768 | -0.22888 | -0.16479 | 0.027466 | -0.10986 | -0.050354 | -0.09613 | 0.19226 | -0.15106 | -0.045776 | 0.059509 | -0.050354 | 0.068665 | 122.1542 | -0.045776 | -0.39825 | 122.4106 | 122.3328 | 122.2733 | 0.17853 | 0.11902 | 122.2321 | -0.041198 | -0.27924 | 122.4426 | 122.4518 | 122.3328 | 0.21973 | 0.10071 | 0.25635 | 0.064087 | 0.21057 | 0.10529 | 0.41656 | 0.34332 | 122.5708 | 122.5754 | -0.46234 | -0.38452 | 122.2183 | 122.3373 | 122.2412 | 122.287
2136.5156 | 122.5479 | -122.374 | 0.20599 | -0.0041962 | -0.059763 | 0.01383 | 0.031307 | 0.0045907 | -0.0015061 | 0.00050845 | 0.0046998 | 0.016024 | 0.023131 | 0.014684 | 0.0033795 | 0.0071692 | -0.00055121 | -0.19684 | 0.14648 | -0.24719 | -0.24261 | -0.082397 | -0.23346 | -0.13733 | -0.10529 | 0.17395 | -0.13733 | -0.027466 | 0.013733 | -0.073242 | 0.10071 | 122.1268 | -0.05951 | -0.44861 | 122.2916 | 122.2366 | 122.1405 | 0.10986 | 0.013733 | 122.2366 | -0.032044 | -0.23346 | 122.3877 | 122.4747 | 122.3007 | 0.23804 | 0.064087 | 0.16479 | 0.004577 | 0.15106 | 0.10986 | 0.39368 | 0.31128 | 122.5204 | 122.5479 | -0.45319 | -0.34332 | 122.1313 | 122.3465 | 122.1771 | 122.2687
2138.2656 | 122.5525 | -122.3831 | 0.22888 | 0.011063 | -0.061472 | 0.012762 | 0.028957 | 0.0024545 | -0.0059921 | 0.0026446 | 0.0046998 | 0.015597 | 0.020781 | 0.0084894 | -0.0013201 | 0.0065284 | -0.00097841 | -0.10071 | 0.16022 | -0.18768 | -0.16937 | 0.041199 | -0.11444 | -0.032043 | -0.068665 | 0.17395 | -0.14648 | -0.036621 | 0.082397 | -0.027466 | 0.086975 | 122.1954 | -0.068665 | -0.39826 | 122.4243 | 122.3511 | 122.2687 | 0.15564 | 0.073242 | 122.2366 | -0.054932 | -0.2655 | 122.4655 | 122.4701 | 122.3557 | 0.23346 | 0.11902 | 0.22888 | 0.01831 | 0.22888 | 0.10986 | 0.3479 | 0.32043 | 122.5433 | 122.5571 | -0.41656 | -0.37537 | 122.2137 | 122.3465 | 122.2824 | 122.3145
2140.0312 | 122.5983 | -122.3511 | 0.21057 | 0.0034333 | -0.056772 | 0.01383 | 0.031093 | 0.0035227 | -0.0025741 | 0.0017902 | 0.001648 | 0.013888 | 0.021636 | 0.014471 | 0.0033795 | 0.0058874 | -0.0022602 | -0.20142 | 0.11902 | -0.27924 | -0.23804 | -0.07782 | -0.21973 | -0.11902 | -0.059509 | 0.19226 | -0.14191 | 0 | 0.064087 | -0.045776 | 0.12817 | 122.0718 | -0.091552 | -0.44861 | 122.2733 | 122.2321 | 122.1313 | 0.16022 | 0.059509 | 122.2092 | -0.01831 | -0.21057 | 122.4152 | 122.4792 | 122.3053 | 0.27008 | 0.096131 | 0.20142 | 0.041199 | 0.20599 | 0.14191 | 0.39825 | 0.33417 | 122.4701 | 122.5433 | -0.48981 | -0.35248 | 122.113 | 122.3511 | 122.1497 | 122.2916
2141.7188 | 122.6028 | -122.3694 | 0.20599 | 0.0034333 | -0.057841 | 0.012548 | 0.031307 | 0.0024545 | -0.0038559 | 0.00029485 | 0.0046998 | 0.015383 | 0.02249 | 0.01618 | -3.8532e-05 | 0.0058874 | -0.00055121 | -0.10986 | 0.16022 | -0.2243 | -0.15106 | 0.059509 | -0.09613 | -0.068665 | 0 | 0.18768 | -0.13275 | 0.027466 | 0.11444 | -0.004578 | 0.14648 | 122.1451 | -0.045777 | -0.35706 | 122.4289 | 122.3007 | 122.2733 | 0.15564 | 0.12817 | 122.2366 | -0.018311 | -0.17853 | 122.4838 | 122.5159 | 122.3648 | 0.27924 | 0.12817 | 0.28381 | 0.073242 | 0.24719 | 0.16022 | 0.38452 | 0.32043 | 122.5296 | 122.5571 | -0.4303 | -0.33875 | 122.2183 | 122.3969 | 122.2595 | 122.3694
2143.4844 | 122.6715 | -122.3145 | 0.18768 | 0.011063 | -0.058268 | 0.013616 | 0.030238 | 0.0041635 | -0.0019333 | 0.0013628 | -0.0014038 | 0.014315 | 0.021422 | 0.022802 | 0.0020979 | 0.008451 | 0.0037214 | -0.19226 | 0.10529 | -0.25635 | -0.19684 | 0 | -0.15564 | -0.07782 | 0.032043 | 0.15106 | -0.11902 | 0.064087 | 0.16479 | 0.045776 | 0.20142 | 122.0581 | -0.082397 | -0.38452 | 122.3145 | 122.2366 | 122.1588 | 0.17853 | 0.10071 | 122.1954 | -0.036621 | -0.1236 | 122.4792 | 122.5159 | 122.3602 | 0.32044 | 0.16479 | 0.25635 | 0.05951 | 0.28381 | 0.18311 | 0.36163 | 0.27008 | 122.4197 | 122.4655 | -0.44403 | -0.3067 | 122.1176 | 122.3785 | 122.1222 | 122.3465
2145.1719 | 122.5754 | -122.3831 | 0.21515 | 0.011063 | -0.056986 | 0.011053 | 0.028102 | 0.0035227 | -0.0015061 | -0.00013235 | 0.001648 | 0.01346 | 0.022917 | 0.011907 | 0.0025251 | 0.0065284 | 0.0011578 | -0.19684 | 0.14191 | -0.24719 | -0.23804 | -0.068665 | -0.2243 | -0.14191 | -0.091553 | 0.17853 | -0.14648 | -0.018311 | 0.041199 | -0.068665 | 0.10071 | 122.1359 | -0.073242 | -0.45319 | 122.3145 | 122.2412 | 122.1588 | 0.10528 | 0.022888 | 122.2366 | -0.036621 | -0.23346 | 122.4243 | 122.4838 | 122.3145 | 0.24719 | 0.077819 | 0.17853 | 0.009155 | 0.18768 | 0.12817 | 0.3891 | 0.32501 | 122.525 | 122.5616 | -0.46234 | -0.36163 | 122.1451 | 122.3648 | 122.1863 | 122.2916
2146.9062 | 122.5891 | -122.3831 | 0.2243 | -0.0041962 | -0.059336 | 0.011694 | 0.031734 | 0.0037363 | -0.0015061 | 8.125e-05 | 0.0046998 | 0.014529 | 0.020781 | 0.020239 | 0.0018841 | 0.006742 | 0.0013714 | -0.20142 | 0.13275 | -0.27924 | -0.24719 | -0.041199 | -0.22888 | -0.10986 | -0.073242 | 0.18768 | -0.14191 | 0.013733 | 0.068665 | -0.045776 | 0.12817 | 122.1039 | -0.091553 | -0.4715 | 122.3419 | 122.2733 | 122.1542 | 0.16937 | 0.050354 | 122.2412 | -0.036621 | -0.21057 | 122.4518 | 122.5113 | 122.3373 | 0.27008 | 0.096131 | 0.23804 | 0.032044 | 0.21057 | 0.15564 | 0.41199 | 0.32959 | 122.5159 | 122.5708 | -0.50354 | -0.36621 | 122.1359 | 122.3969 | 122.1817 | 122.3099
2148.6562 | 122.7081 | -122.3511 | 0.18768 | 0.011063 | -0.059336 | 0.01148 | 0.028743 | 0.00095914 | -0.0019333 | -0.00013235 | 0.0046998 | 0.011965 | 0.021209 | 0.020666 | -0.0019611 | 0.0065284 | -0.00076481 | -0.12817 | 0.11902 | -0.21057 | -0.11902 | 0.091553 | -0.054932 | 0.013733 | 0.018311 | 0.14648 | -0.11444 | 0.059509 | 0.20142 | 0.07782 | 0.20142 | 122.1405 | -0.068664 | -0.3067 | 122.4426 | 122.3648 | 122.2961 | 0.2243 | 0.15564 | 122.2366 | -0.041199 | -0.12817 | 122.5525 | 122.5525 | 122.4289 | 0.31586 | 0.19226 | 0.30212 | 0.091552 | 0.31586 | 0.17395 | 0.32959 | 0.26093 | 122.4701 | 122.4976 | -0.39825 | -0.30212 | 122.2321 | 122.4106 | 122.2229 | 122.3694
2150.4219 | 122.6624 | -122.3511 | 0.20599 | 0.0034333 | -0.05955 | 0.012548 | 0.029598 | 0.00074554 | -0.0047103 | -0.00034615 | 0.001648 | 0.013888 | 0.020568 | 0.022802 | -0.0015337 | 0.0071692 | 0.0026532 | -0.16022 | 0.12817 | -0.21057 | -0.16022 | 0.054932 | -0.10986 | -0.032043 | -0.018311 | 0.15564 | -0.14648 | 0.032043 | 0.13733 | 0.041199 | 0.16022 | 122.1405 | -0.07782 | -0.36621 | 122.406 | 122.319 | 122.2412 | 0.17853 | 0.10071 | 122.2046 | -0.050354 | -0.17395 | 122.4884 | 122.5113 | 122.3923 | 0.3067 | 0.18768 | 0.2655 | 0.050354 | 0.28381 | 0.17853 | 0.33875 | 0.30212 | 122.4792 | 122.5067 | -0.41657 | -0.35248 | 122.1909 | 122.3831 | 122.1909 | 122.3328
2152.1094 | 122.5525 | -122.4152 | 0.2243 | 0.011063 | -0.058054 | 0.014471 | 0.031093 | 0.0028817 | -0.0047103 | 0.0011492 | 0.0046998 | 0.01581 | 0.020354 | 0.01383 | 0.0016705 | 0.0048194 | -0.00033761 | -0.16479 | 0.15564 | -0.2655 | -0.23346 | -0.073242 | -0.19684 | -0.13733 | -0.11902 | 0.19226 | -0.13733 | -0.045776 | 0.036621 | -0.091553 | 0.07782 | 122.1497 | -0.068664 | -0.45776 | 122.3419 | 122.2778 | 122.2183 | 0.12817 | 0.068665 | 122.2778 | -0.032043 | -0.27008 | 122.4518 | 122.493 | 122.3236 | 0.21515 | 0.045776 | 0.19226 | 0.032044 | 0.17395 | 0.091553 | 0.42114 | 0.32959 | 122.5708 | 122.6074 | -0.48981 | -0.36163 | 122.1817 | 122.3694 | 122.2504 | 122.2961
2153.8594 | 122.5937 | -122.374 | 0.22888 | 0.0034333 | -0.059122 | 0.014257 | 0.03152 | 0.0022409 | -0.0027877 | 0.0015764 | 0.001648 | 0.014315 | 0.022704 | 0.017889 | 0.00081607 | 0.0069556 | 0.003294 | -0.21515 | 0.12817 | -0.2655 | -0.24261 | -0.050354 | -0.21057 | -0.12817 | -0.07782 | 0.16937 | -0.16022 | -0.009155 | 0.064087 | -0.036621 | 0.1236 | 122.1085 | -0.10071 | -0.4715 | 122.3236 | 122.2458 | 122.1634 | 0.13733 | 0.054932 | 122.2137 | -0.059509 | -0.23804 | 122.438 | 122.4976 | 122.3373 | 0.28381 | 0.1236 | 0.21515 | 0.022888 | 0.2243 | 0.15106 | 0.39368 | 0.32959 | 122.5021 | 122.5433 | -0.49438 | -0.3891 | 122.1313 | 122.3648 | 122.1588 | 122.2961
2155.6094 | 122.6486 | -122.3831 | 0.21973 | 0.0034333 | -0.058909 | 0.01148 | 0.03152 | 0.0013863 | -1.0686e-05 | 0.00093565 | -0.0014038 | 0.014315 | 0.022063 | 0.023443 | 0.0012433 | 0.0088782 | 0.00030339 | -0.1831 | 0.13275 | -0.26093 | -0.21973 | -0.041199 | -0.21515 | -0.1236 | -0.009155 | 0.17395 | -0.15106 | 0.041199 | 0.10986 | 0.018311 | 0.16937 | 122.1222 | -0.086976 | -0.43945 | 122.3419 | 122.2595 | 122.168 | 0.13733 | 0.045776 | 122.2321 | -0.045777 | -0.17853 | 122.493 | 122.5525 | 122.4014 | 0.32044 | 0.16937 | 0.21973 | 0.041198 | 0.26093 | 0.19226 | 0.39368 | 0.32501 | 122.5159 | 122.5571 | -0.48065 | -0.37079 | 122.1634 | 122.4243 | 122.2 | 122.374
2157.3594 | 122.5845 | -122.4014 | 0.23804 | -0.0041962 | -0.059977 | 0.012762 | 0.027461 | -0.0024589 | -0.0072739 | -0.00034615 | 0.0046998 | 0.013033 | 0.022704 | 0.0099848 | -0.0040973 | 0.0058874 | 0.0020124 | -0.15106 | 0.19226 | -0.21515 | -0.16937 | 0.045776 | -0.09613 | -0.032043 | -0.07782 | 0.20599 | -0.15564 | -0.059509 | 0.059509 | -0.041199 | 0.091553 | 122.1863 | -0.045776 | -0.40741 | 122.4472 | 122.3694 | 122.3053 | 0.18311 | 0.11902 | 122.2458 | -0.032043 | -0.29755 | 122.4609 | 122.493 | 122.3602 | 0.24719 | 0.11444 | 0.26093 | 0.045776 | 0.21515 | 0.096131 | 0.40741 | 0.36163 | 122.5937 | 122.6074 | -0.45319 | -0.39368 | 122.2321 | 122.3419 | 122.2504 | 122.3236
2159.0469 | 122.699 | -122.3785 | 0.21515 | -0.011826 | -0.05955 | 0.012975 | 0.02682 | 0.0054453 | -0.0059921 | 0.0037128 | 0.0046998 | 0.012606 | 0.023558 | 0.014044 | -0.0028155 | 0.006101 | -0.00012381 | -0.068665 | 0.13733 | -0.1831 | -0.059509 | 0.14191 | 0.009155 | 0.059509 | 0.064087 | 0.13733 | -0.12817 | 0.068665 | 0.20142 | 0.10071 | 0.18768 | 122.1954 | -0.07782 | -0.27466 | 122.5204 | 122.438 | 122.3877 | 0.24261 | 0.19226 | 122.2504 | -0.07782 | -0.14648 | 122.58 | 122.5662 | 122.4792 | 0.31586 | 0.22888 | 0.32501 | 0.1236 | 0.32959 | 0.19684 | 0.32043 | 0.2655 | 122.5159 | 122.5159 | -0.39825 | -0.34332 | 122.319 | 122.4472 | 122.3099 | 122.4426
2160.7969 | 122.6761 | -122.3831 | 0.21515 | 0.0034333 | -0.061045 | 0.013616 | 0.027889 | 0.0043771 | -0.0038559 | 8.125e-05 | 0.001648 | 0.014315 | 0.021849 | 0.01383 | 0.00060247 | 0.0054602 | 0.00030339 | -0.16937 | 0.10529 | -0.2243 | -0.14648 | 0.050354 | -0.1236 | -0.027466 | -0.018311 | 0.13733 | -0.13275 | 0.018311 | 0.13275 | 0.018311 | 0.15564 | 122.1588 | -0.10986 | -0.36163 | 122.4335 | 122.3557 | 122.2595 | 0.19684 | 0.10071 | 122.2504 | -0.07782 | -0.19684 | 122.5159 | 122.5388 | 122.4014 | 0.28839 | 0.15106 | 0.27466 | 0.07782 | 0.2655 | 0.15106 | 0.32959 | 0.27008 | 122.4884 | 122.5204 | -0.43945 | -0.3479 | 122.2366 | 122.4014 | 122.2137 | 122.3648
2162.5312 | 122.6898 | -122.3969 | 0.21515 | 0.011063 | -0.059763 | 0.01148 | 0.027248 | -0.0022453 | -0.0047103 | 0.0032854 | 0.001648 | 0.011538 | 0.02014 | 0.022588 | 0.00017507 | 0.0058874 | -0.00012381 | -0.064087 | 0.14648 | -0.15106 | -0.068665 | 0.14191 | -0.009155 | 0.036621 | 0.050354 | 0.15564 | -0.1236 | 0.073242 | 0.19226 | 0.086975 | 0.19226 | 122.2458 | -0.068665 | -0.28381 | 122.5388 | 122.4335 | 122.3877 | 0.18768 | 0.14191 | 122.2733 | -0.059509 | -0.14191 | 122.5891 | 122.5891 | 122.4838 | 0.31586 | 0.21057 | 0.29297 | 0.082397 | 0.31586 | 0.19684 | 0.29755 | 0.27924 | 122.5433 | 122.5525 | -0.36621 | -0.33875 | 122.3282 | 122.4701 | 122.3328 | 122.4472
2164.2812 | 122.5983 | -122.3923 | 0.21057 | 0.011063 | -0.058695 | 0.012335 | 0.032375 | 0.0048043 | -0.0036423 | -0.0031232 | 0.0046998 | 0.013247 | 0.021849 | 0.01618 | 0.0012433 | 0.0063148 | -0.0018328 | -0.1236 | 0.13733 | -0.21973 | -0.19226 | -0.018311 | -0.1831 | -0.10986 | -0.054932 | 0.16937 | -0.14191 | -0.009155 | 0.054932 | -0.073242 | 0.10529 | 122.1725 | -0.073242 | -0.40283 | 122.374 | 122.2824 | 122.2092 | 0.10986 | 0.036622 | 122.2504 | -0.041198 | -0.21973 | 122.4472 | 122.4976 | 122.319 | 0.24719 | 0.068665 | 0.20142 | 0.027466 | 0.19684 | 0.13275 | 0.35706 | 0.31128 | 122.5296 | 122.5616 | -0.4303 | -0.35248 | 122.2 | 122.3831 | 122.2687 | 122.3373
2166.0469 | 122.6166 | -122.4152 | 0.21973 | -0.0041962 | -0.059977 | 0.011907 | 0.030452 | 0.0037363 | -0.0025741 | 0.0017902 | -0.0014038 | 0.014956 | 0.0195 | 0.014684 | -0.0017475 | 0.005033 | 0.00094419 | -0.11444 | 0.21515 | -0.21057 | -0.17395 | -0.004578 | -0.11902 | -0.050354 | -0.10529 | 0.20142 | -0.16022 | -0.027466 | 0.059509 | -0.027466 | 0.10529 | 122.2046 | -0.004578 | -0.39368 | 122.4106 | 122.3648 | 122.2961 | 0.16022 | 0.091552 | 122.2549 | -0.018311 | -0.24719 | 122.4747 | 122.5204 | 122.3877 | 0.2655 | 0.13275 | 0.20599 | 0.036621 | 0.21973 | 0.13275 | 0.42572 | 0.36163 | 122.6303 | 122.6166 | -0.4303 | -0.37994 | 122.2412 | 122.3877 | 122.3007 | 122.3099
2167.75 | 122.612 | -122.4243 | 0.25177 | 0.0034333 | -0.059977 | 0.012121 | 0.028529 | 0.0035227 | -0.0030015 | -0.0022688 | -0.0014038 | 0.013888 | 0.021209 | 0.011266 | -0.0038837 | 0.0046058 | -0.00033761 | -0.15564 | 0.19684 | -0.20142 | -0.17853 | 0.022888 | -0.10529 | -0.032043 | -0.10071 | 0.19226 | -0.16937 | -0.054932 | 0.059509 | -0.032043 | 0.091553 | 122.2229 | -0.054932 | -0.4303 | 122.4472 | 122.3923 | 122.319 | 0.16937 | 0.09613 | 122.2549 | -0.059509 | -0.3067 | 122.4838 | 122.5159 | 122.3923 | 0.26093 | 0.13733 | 0.2243 | 0.022888 | 0.22888 | 0.11444 | 0.39825 | 0.36163 | 122.6212 | 122.6166 | -0.45319 | -0.42114 | 122.2458 | 122.3694 | 122.2687 | 122.3236
2169.5156 | 122.6624 | -122.4289 | 0.21515 | -0.0041962 | -0.058481 | 0.013189 | 0.029598 | 0.0024545 | -0.0023605 | 0.0020038 | 0.0046998 | 0.01346 | 0.021422 | 0.014898 | -0.0023883 | 0.005033 | 0.00051699 | -0.073242 | 0.14191 | -0.16937 | -0.07782 | 0.11444 | -0.018311 | 0.045776 | 0.009155 | 0.15564 | -0.12817 | 0.022888 | 0.13275 | 0.032043 | 0.14648 | 122.2595 | -0.073242 | -0.29297 | 122.5433 | 122.4747 | 122.4106 | 0.21515 | 0.15106 | 122.3007 | -0.059509 | -0.19226 | 122.5616 | 122.5754 | 122.4609 | 0.27466 | 0.16022 | 0.28381 | 0.091553 | 0.26093 | 0.15106 | 0.31128 | 0.28381 | 122.5708 | 122.5845 | -0.38452 | -0.34332 | 122.3511 | 122.4518 | 122.3557 | 122.438
2171.2031 | 122.7722 | -122.3785 | 0.20599 | 0.018692 | -0.05955 | 0.013189 | 0.027461 | -0.00096346 | -0.0021469 | -0.00055975 | -0.0014038 | 0.011751 | 0.02014 | 0.015539 | 0.0014569 | 0.0058874 | 0.00073059 | -0.091553 | 0.11902 | -0.19226 | -0.064087 | 0.14648 | -0.004578 | 0.068665 | 0.10071 | 0.14191 | -0.13733 | 0.10529 | 0.2243 | 0.13275 | 0.2243 | 122.1863 | -0.086975 | -0.27008 | 122.525 | 122.4472 | 122.374 | 0.26093 | 0.18768 | 122.2412 | -0.064087 | -0.10071 | 122.6028 | 122.6028 | 122.5113 | 0.36163 | 0.27008 | 0.33874 | 0.12817 | 0.36163 | 0.24262 | 0.31128 | 0.27924 | 122.4976 | 122.5204 | -0.39826 | -0.34332 | 122.3145 | 122.4838 | 122.287 | 122.4792
2172.9531 | 122.6349 | -122.4243 | 0.2243 | 0.0034333 | -0.061045 | 0.010839 | 0.029811 | 0.0039499 | -0.0038559 | 0.0017902 | -0.0014038 | 0.01346 | 0.019072 | 0.018316 | -0.0017475 | 0.0048194 | -0.00097841 | -0.068665 | 0.15564 | -0.16479 | -0.10529 | 0.09613 | -0.036621 | 0 | -0.022888 | 0.17395 | -0.15564 | -0.004578 | 0.086975 | -0.022888 | 0.1236 | 122.2595 | -0.068664 | -0.32959 | 122.5204 | 122.4243 | 122.3877 | 0.16479 | 0.12817 | 122.2687 | -0.050354 | -0.22888 | 122.5113 | 122.5479 | 122.4014 | 0.27924 | 0.13275 | 0.26092 | 0.059509 | 0.24261 | 0.15106 | 0.32044 | 0.32959 | 122.58 | 122.5983 | -0.3891 | -0.37994 | 122.319 | 122.4197 | 122.3557 | 122.4014
2174.6406 | 122.6074 | -122.4518 | 0.21973 | 0.018692 | -0.058481 | 0.01383 | 0.032802 | 0.0033089 | -0.00086509 | 0.0013628 | -0.0014038 | 0.016665 | 0.020995 | 0.013616 | 0.0014569 | 0.0052466 | 0.0026532 | -0.16479 | 0.16479 | -0.23804 | -0.22888 | -0.064087 | -0.20599 | -0.16022 | -0.11444 | 0.19226 | -0.16022 | -0.064087 | 0.027466 | -0.073242 | 0.086975 | 122.2137 | -0.054932 | -0.44861 | 122.3877 | 122.2916 | 122.2458 | 0.07782 | 0.032043 | 122.2916 | -0.027466 | -0.28381 | 122.4792 | 122.5388 | 122.3785 | 0.24719 | 0.086975 | 0.17395 | 0.009155 | 0.18768 | 0.09613 | 0.40283 | 0.35248 | 122.6166 | 122.644 | -0.45776 | -0.37994 | 122.2229 | 122.3877 | 122.287 | 122.3373
2176.4062 | 122.6257 | -122.438 | 0.22888 | 0.0034333 | -0.057627 | 0.011053 | 0.029811 | 0.0060861 | -0.0034287 | 0.002431 | 0.001648 | 0.016237 | 0.020995 | 0.014898 | 0.0016705 | 0.006101 | -0.0016192 | -0.1236 | 0.14648 | -0.21057 | -0.16937 | 0.045776 | -0.13275 | -0.073242 | -0.027466 | 0.18768 | -0.14191 | 0.004578 | 0.073242 | -0.045776 | 0.11444 | 122.2275 | -0.082398 | -0.39826 | 122.4838 | 122.3648 | 122.3053 | 0.13733 | 0.07782 | 122.2961 | -0.041199 | -0.2243 | 122.5113 | 122.5525 | 122.3923 | 0.25635 | 0.096131 | 0.25635 | 0.041198 | 0.21515 | 0.14649 | 0.35706 | 0.32959 | 122.5845 | 122.6257 | -0.43945 | -0.37079 | 122.2687 | 122.4426 | 122.3145 | 122.4106
2178.1562 | 122.7448 | -122.3877 | 0.20599 | 0.0034333 | -0.06019 | 0.014044 | 0.029384 | 0.0033089 | -0.0042831 | -0.0022688 | 0.001648 | 0.013033 | 0.020568 | 0.022802 | 0.0061567 | 0.008451 | 0.00030339 | -0.1236 | 0.082397 | -0.22888 | -0.10529 | 0.073242 | -0.10529 | -0.041199 | 0.082397 | 0.12817 | -0.11444 | 0.11444 | 0.1831 | 0.064087 | 0.21515 | 122.1588 | -0.1236 | -0.31128 | 122.4609 | 122.3465 | 122.2824 | 0.18768 | 0.1236 | 122.2733 | -0.07782 | -0.091553 | 122.5708 | 122.6028 | 122.4518 | 0.32959 | 0.17853 | 0.30212 | 0.1236 | 0.29755 | 0.22888 | 0.31128 | 0.24262 | 122.4701 | 122.5159 | -0.43488 | -0.32044 | 122.2824 | 122.5021 | 122.2641 | 122.4701
2179.9219 | 122.7631 | -122.3969 | 0.1831 | -0.0041962 | -0.060618 | 0.010626 | 0.027889 | -0.00074986 | -0.0040695 | 0.00093565 | 0.001648 | 0.013247 | 0.020995 | 0.022588 | 0.00017507 | 0.0048194 | -0.00055121 | -0.10529 | 0.14191 | -0.19684 | -0.09613 | 0.13275 | -0.027466 | 0.045776 | 0.068665 | 0.15106 | -0.11444 | 0.082397 | 0.21515 | 0.10529 | 0.21057 | 122.2 | -0.041198 | -0.27924 | 122.5296 | 122.4426 | 122.3694 | 0.24261 | 0.16937 | 122.2824 | -0.032043 | -0.10071 | 122.612 | 122.6074 | 122.5021 | 0.32501 | 0.21973 | 0.32959 | 0.10071 | 0.32959 | 0.19684 | 0.33875 | 0.2655 | 122.5388 | 122.5479 | -0.37994 | -0.29755 | 122.3007 | 122.4792 | 122.2916 | 122.4655
2181.6094 | 122.7493 | -122.3831 | 0.20599 | 0.011063 | -0.058268 | 0.01383 | 0.030452 | 0.0035227 | -0.0025741 | 0.0022174 | -0.0014038 | 0.01282 | 0.021636 | 0.019384 | 0.0023115 | 0.008451 | 0.0017988 | -0.10529 | 0.082397 | -0.22888 | -0.10986 | 0.064087 | -0.11444 | -0.032043 | 0.082397 | 0.16937 | -0.10071 | 0.11444 | 0.1831 | 0.073242 | 0.21057 | 122.1542 | -0.1236 | -0.31586 | 122.4472 | 122.3511 | 122.2687 | 0.19684 | 0.11444 | 122.2824 | -0.036621 | -0.091553 | 122.5662 | 122.5937 | 122.4564 | 0.31128 | 0.17395 | 0.29297 | 0.11902 | 0.28381 | 0.21515 | 0.31128 | 0.27008 | 122.4655 | 122.5525 | -0.43488 | -0.3067 | 122.2733 | 122.4976 | 122.2778 | 122.4655
2183.3594 | 122.7081 | -122.406 | 0.20599 | 0.026321 | -0.060618 | 0.011694 | 0.027889 | 0.00074554 | -0.0012925 | -0.00055975 | 0.001648 | 0.013247 | 0.020781 | 0.016393 | -0.0017475 | 0.0065284 | 0.0013714 | -0.15106 | 0.11444 | -0.19684 | -0.15106 | 0.041199 | -0.11444 | -0.036621 | -0.018311 | 0.15564 | -0.12817 | 0.032043 | 0.13733 | 0.022888 | 0.15564 | 122.2092 | -0.091553 | -0.35706 | 122.4472 | 122.3694 | 122.2916 | 0.16022 | 0.082397 | 122.2778 | -0.050354 | -0.17395 | 122.5433 | 122.5616 | 122.4289 | 0.28381 | 0.15106 | 0.23804 | 0.045776 | 0.2655 | 0.16022 | 0.31128 | 0.28381 | 122.5204 | 122.5616 | -0.40283 | -0.33417 | 122.2549 | 122.438 | 122.2549 | 122.3877
2185.125 | 122.6532 | -122.4564 | 0.23346 | 0.0034333 | -0.058909 | 0.014257 | 0.031734 | 0.0039499 | -0.0015061 | 0.00072205 | 0.001648 | 0.013888 | 0.021849 | 0.0093438 | 0.0016705 | 0.0054602 | -0.00033761 | -0.17395 | 0.13733 | -0.27466 | -0.22888 | -0.064087 | -0.22888 | -0.13733 | -0.073242 | 0.19684 | -0.15106 | -0.022888 | 0.036621 | -0.064087 | 0.09613 | 122.1817 | -0.09613 | -0.46234 | 122.3923 | 122.319 | 122.2275 | 0.13733 | 0.045776 | 122.3053 | -0.036621 | -0.25635 | 122.493 | 122.5525 | 122.3923 | 0.24719 | 0.086975 | 0.21057 | 0.045776 | 0.18768 | 0.12817 | 0.41199 | 0.3479 | 122.5937 | 122.6532 | -0.50812 | -0.38452 | 122.2275 | 122.4335 | 122.2824 | 122.3831
2186.8125 | 122.7814 | -122.4152 | 0.19226 | 0.0034333 | -0.061472 | 0.012548 | 0.028957 | 0.0033089 | -0.0023605 | 8.125e-05 | 0.0046998 | 0.01282 | 0.021636 | 0.023229 | -0.0030291 | 0.0071692 | -0.00012381 | -0.086975 | 0.13275 | -0.19226 | -0.059509 | 0.16479 | 0 | 0.054932 | 0.11444 | 0.14648 | -0.10986 | 0.09613 | 0.21973 | 0.10529 | 0.19684 | 122.2229 | -0.05951 | -0.25177 | 122.58 | 122.4701 | 122.4152 | 0.24719 | 0.19226 | 122.3053 | -0.045777 | -0.096131 | 122.6349 | 122.612 | 122.5204 | 0.3067 | 0.21515 | 0.35706 | 0.13275 | 0.32959 | 0.20599 | 0.32501 | 0.25635 | 122.5479 | 122.5616 | -0.38452 | -0.30212 | 122.3557 | 122.5113 | 122.3282 | 122.5296
2188.5781 | 122.731 | -122.3969 | 0.19684 | 0.011063 | -0.056345 | 0.013189 | 0.031093 | 0.0035227 | -0.0025741 | 0.00093565 | 0.0077514 | 0.01346 | 0.018645 | 0.022588 | 0.0027387 | 0.0052466 | -0.0014056 | -0.11902 | 0.086975 | -0.21057 | -0.11444 | 0.07782 | -0.10071 | -0.013733 | 0.068665 | 0.13733 | -0.11444 | 0.082397 | 0.17395 | 0.041199 | 0.17853 | 122.1863 | -0.10986 | -0.31128 | 122.4747 | 122.3831 | 122.2961 | 0.19684 | 0.10986 | 122.2824 | -0.059509 | -0.11444 | 122.5708 | 122.5754 | 122.4381 | 0.29297 | 0.15564 | 0.28839 | 0.09613 | 0.28839 | 0.19684 | 0.29755 | 0.25177 | 122.4838 | 122.5342 | -0.40741 | -0.31128 | 122.2824 | 122.4792 | 122.2778 | 122.4655
2190.3438 | 122.7448 | -122.4197 | 0.19226 | 0.018692 | -0.058054 | 0.011694 | 0.031947 | 0.0030953 | -0.0042831 | 0.00093565 | -0.0014038 | 0.013247 | 0.021422 | 0.024938 | 0.0027387 | 0.008451 | 0.0020124 | -0.16022 | 0.10529 | -0.25177 | -0.14191 | 0.036621 | -0.14191 | -0.059509 | 0.064087 | 0.16022 | -0.11902 | 0.086975 | 0.17395 | 0.064087 | 0.21057 | 122.168 | -0.086975 | -0.33417 | 122.4564 | 122.3602 | 122.2778 | 0.19226 | 0.10986 | 122.3007 | -0.032044 | -0.10529 | 122.5937 | 122.6303 | 122.4838 | 0.32959 | 0.18311 | 0.28839 | 0.10986 | 0.29297 | 0.20599 | 0.35706 | 0.27924 | 122.525 | 122.58 | -0.44403 | -0.31128 | 122.2778 | 122.5067 | 122.2595 | 122.4838
2192.0938 | 122.7997 | -122.4197 | 0.18768 | -0.0041962 | -0.060618 | 0.012762 | 0.028316 | 0.0050179 | -0.0027877 | 0.00072205 | 0.0046998 | 0.012606 | 0.019713 | 0.013403 | -0.00046573 | 0.0058874 | -0.00033761 | -0.082397 | 0.14648 | -0.18768 | -0.059509 | 0.17395 | -0.013733 | 0.064087 | 0.10529 | 0.14648 | -0.13275 | 0.07782 | 0.20599 | 0.091553 | 0.21057 | 122.2321 | -0.041199 | -0.24719 | 122.5937 | 122.4838 | 122.406 | 0.25177 | 0.17395 | 122.287 | -0.041199 | -0.10986 | 122.6257 | 122.6303 | 122.5113 | 0.34332 | 0.2243 | 0.36163 | 0.12817 | 0.33875 | 0.21057 | 0.33417 | 0.27924 | 122.5662 | 122.5662 | -0.37537 | -0.32043 | 122.3602 | 122.4976 | 122.3373 | 122.525
2193.7969 | 122.7722 | -122.406 | 0.20142 | 0.0034333 | -0.06019 | 0.010626 | 0.028957 | 0.00095914 | -0.0032151 | -0.00034615 | 0.0046998 | 0.015383 | 0.022277 | 0.023016 | -0.0019611 | 0.0065284 | 0.00030339 | -0.1236 | 0.1236 | -0.18768 | -0.10071 | 0.091553 | -0.064087 | 0.022888 | 0.018311 | 0.16022 | -0.14191 | 0.082397 | 0.18768 | 0.09613 | 0.19684 | 122.2183 | -0.07782 | -0.30212 | 122.4976 | 122.4289 | 122.3419 | 0.21057 | 0.1236 | 122.2641 | -0.041199 | -0.11902 | 122.5937 | 122.6028 | 122.5021 | 0.33875 | 0.23804 | 0.27924 | 0.086975 | 0.32959 | 0.2243 | 0.31128 | 0.30212 | 122.5296 | 122.5662 | -0.3891 | -0.34332 | 122.3053 | 122.4884 | 122.2824 | 122.4243
2195.5469 | 122.7448 | -122.4152 | 0.20142 | -0.0041962 | -0.061259 | 0.011267 | 0.030452 | 0.0041635 | -0.0038559 | 0.0020038 | -0.0014038 | 0.01282 | 0.019927 | 0.023443 | 0.0020979 | 0.0052466 | -0.00097841 | -0.1236 | 0.068665 | -0.20142 | -0.10986 | 0.10071 | -0.10071 | -0.022888 | 0.07782 | 0.16479 | -0.11902 | 0.082397 | 0.17395 | 0.059509 | 0.1831 | 122.2137 | -0.13275 | -0.31128 | 122.5159 | 122.3923 | 122.3145 | 0.17853 | 0.10071 | 122.2961 | -0.036621 | -0.11902 | 122.5891 | 122.5983 | 122.4747 | 0.30212 | 0.17853 | 0.30212 | 0.091553 | 0.29297 | 0.20142 | 0.27008 | 0.28381 | 122.4838 | 122.58 | -0.40283 | -0.32044 | 122.3053 | 122.4976 | 122.2916 | 122.493
2197.2969 | 122.7676 | -122.4289 | 0.19684 | -0.0041962 | -0.058695 | 0.012548 | 0.027889 | 0.0022409 | -0.0032151 | 0.0020038 | 0.0046998 | 0.010897 | 0.021422 | 0.023657 | -0.0038837 | 0.006101 | 0.0011578 | -0.13733 | 0.12817 | -0.20599 | -0.10529 | 0.09613 | -0.064087 | 0.018311 | 0.032043 | 0.16022 | -0.13733 | 0.073242 | 0.1831 | 0.086975 | 0.20599 | 122.2229 | -0.068664 | -0.30212 | 122.525 | 122.4472 | 122.3648 | 0.22431 | 0.14191 | 122.2916 | -0.036621 | -0.1236 | 122.612 | 122.6349 | 122.5159 | 0.34332 | 0.2243 | 0.30212 | 0.10071 | 0.32043 | 0.21057 | 0.33417 | 0.29755 | 122.5571 | 122.5891 | -0.40283 | -0.33417 | 122.3236 | 122.5021 | 122.2916 | 122.4609
2199.0625 | 122.644 | -122.4884 | 0.24719 | 0.018692 | -0.056986 | 0.011267 | 0.033229 | 0.0035227 | -0.00065149 | 0.0037128 | 0.0046998 | 0.016878 | 0.022917 | 0.013616 | 0.0012433 | 0.0063148 | 0.002226 | -0.16022 | 0.15564 | -0.22888 | -0.19226 | -0.045776 | -0.20599 | -0.12817 | -0.10071 | 0.1831 | -0.16022 | -0.027466 | 0.036621 | -0.07782 | 0.07782 | 122.2595 | -0.091552 | -0.43945 | 122.4426 | 122.3602 | 122.2824 | 0.10071 | 0.022888 | 122.3282 | -0.064087 | -0.27466 | 122.525 | 122.5662 | 122.4106 | 0.23804 | 0.082397 | 0.18311 | 0.036621 | 0.19684 | 0.13275 | 0.38452 | 0.34332 | 122.644 | 122.6715 | -0.47607 | -0.40741 | 122.2961 | 122.4609 | 122.3282 | 122.3877
2200.75 | 122.7768 | -122.438 | 0.20142 | -0.0041962 | -0.059977 | 0.012975 | 0.029384 | 0.0033089 | -0.0023605 | -0.00013235 | 0.001648 | 0.013247 | 0.023345 | 0.022161 | 0.0040205 | 0.0056738 | 0.00094419 | -0.16022 | 0.1236 | -0.25177 | -0.16479 | 0.022888 | -0.14648 | -0.068665 | 0.022888 | 0.16022 | -0.1236 | 0.091553 | 0.16937 | 0.041199 | 0.20142 | 122.1863 | -0.07782 | -0.36621 | 122.4609 | 122.3694 | 122.2916 | 0.1831 | 0.10529 | 122.3145 | -0.041199 | -0.10986 | 122.6074 | 122.6395 | 122.4792 | 0.32501 | 0.16479 | 0.27466 | 0.086975 | 0.29297 | 0.21515 | 0.37537 | 0.28381 | 122.5616 | 122.5983 | -0.45319 | -0.32501 | 122.2733 | 122.5296 | 122.2778 | 122.4609
2202.5 | 122.6303 | -122.4701 | 0.23346 | 0.0034333 | -0.059336 | 0.01148 | 0.029811 | 0.0086495 | -0.0017197 | 0.00029485 | 0.0046998 | 0.013888 | 0.021636 | 0.017034 | 0.00060247 | 0.0088782 | -0.002901 | -0.16022 | 0.15106 | -0.25177 | -0.21515 | -0.045776 | -0.21515 | -0.12817 | -0.10529 | 0.18768 | -0.14648 | -0.032043 | 0.022888 | -0.10071 | 0.086975 | 122.2183 | -0.082397 | -0.44861 | 122.4243 | 122.3419 | 122.2549 | 0.1236 | 0.036621 | 122.3236 | -0.045776 | -0.2655 | 122.493 | 122.5571 | 122.3694 | 0.23346 | 0.045776 | 0.20599 | 0.036621 | 0.16937 | 0.11444 | 0.40283 | 0.33417 | 122.6212 | 122.6578 | -0.48523 | -0.37994 | 122.2549 | 122.4381 | 122.3099 | 122.3648
2204.25 | 122.8043 | -122.4335 | 0.19684 | 0.011063 | -0.060404 | 0.013616 | 0.030025 | -0.00032266 | -0.0055649 | -0.00077335 | 0.001648 | 0.014101 | 0.020354 | 0.017462 | -0.0015337 | 0.005033 | 0.001585 | -0.086975 | 0.12817 | -0.1831 | -0.054932 | 0.17395 | -0.004578 | 0.068665 | 0.10071 | 0.13733 | -0.13733 | 0.07782 | 0.20142 | 0.10986 | 0.19684 | 122.2504 | -0.068664 | -0.25177 | 122.6074 | 122.5021 | 122.4289 | 0.25177 | 0.17853 | 122.2961 | -0.059509 | -0.11902 | 122.6349 | 122.6303 | 122.5433 | 0.33417 | 0.24719 | 0.35706 | 0.12817 | 0.33875 | 0.21515 | 0.31128 | 0.27466 | 122.5616 | 122.5708 | -0.37994 | -0.33417 | 122.3785 | 122.5113 | 122.3465 | 122.5342
2205.9531 | 122.7127 | -122.4518 | 0.20142 | 0.0034333 | -0.058695 | 0.01383 | 0.030879 | 0.0013863 | -0.0030015 | 0.002431 | 0.0046998 | 0.014529 | 0.02249 | 0.009771 | 0.0020979 | 0.0052466 | -0.0016192 | -0.10071 | 0.15106 | -0.20142 | -0.12817 | 0.07782 | -0.10529 | -0.041199 | 0.004578 | 0.1831 | -0.13275 | 0.032043 | 0.11902 | 0.009155 | 0.13733 | 122.2504 | -0.050354 | -0.32959 | 122.5296 | 122.4106 | 122.3465 | 0.16022 | 0.09613 | 122.319 | -0.018311 | -0.16937 | 122.5708 | 122.5891 | 122.4609 | 0.27008 | 0.14191 | 0.27924 | 0.073242 | 0.25177 | 0.16479 | 0.35248 | 0.31586 | 122.6028 | 122.6349 | -0.40283 | -0.33417 | 122.3236 | 122.4838 | 122.3511 | 122.4564
2207.7031 | 122.6303 | -122.5021 | 0.22888 | 0.0034333 | -0.055704 | 0.015112 | 0.030452 | 0.0015999 | -0.0015061 | 0.0043536 | 0.001648 | 0.013888 | 0.020354 | 0.014044 | 0.00060247 | 0.0052466 | 0.002226 | -0.16479 | 0.15106 | -0.22888 | -0.21515 | -0.059509 | -0.21057 | -0.14191 | -0.12817 | 0.18768 | -0.15564 | -0.032043 | 0.022888 | -0.068665 | 0.10071 | 122.2733 | -0.07782 | -0.44403 | 122.4426 | 122.3602 | 122.2916 | 0.086975 | 0.018311 | 122.3465 | -0.041199 | -0.26093 | 122.525 | 122.6028 | 122.4335 | 0.25635 | 0.086975 | 0.16937 | 0.013733 | 0.17853 | 0.1236 | 0.37994 | 0.34332 | 122.6532 | 122.6898 | -0.45776 | -0.38452 | 122.287 | 122.4701 | 122.3373 | 122.374
2209.3906 | 122.6624 | -122.5021 | 0.23346 | -0.0041962 | -0.061259 | 0.01148 | 0.028102 | 0.0041635 | -0.0017197 | 0.0026446 | 0.001648 | 0.015383 | 0.022704 | 0.012548 | -0.0047381 | 0.0035376 | -0.00076481 | -0.13275 | 0.16937 | -0.20142 | -0.17395 | 0.041199 | -0.10529 | -0.036621 | -0.082397 | 0.18768 | -0.13275 | -0.045776 | 0.07782 | -0.036621 | 0.10529 | 122.3007 | -0.064086 | -0.40741 | 122.5433 | 122.4655 | 122.3968 | 0.1648 | 0.09613 | 122.3694 | -0.045776 | -0.27924 | 122.58 | 122.6074 | 122.4655 | 0.23804 | 0.09613 | 0.24262 | 0.027466 | 0.21057 | 0.086975 | 0.37079 | 0.32043 | 122.6715 | 122.6898 | -0.43488 | -0.36621 | 122.3282 | 122.4564 | 122.3694 | 122.4197
2211.1406 | 122.6669 | -122.5159 | 0.21973 | -0.0041962 | -0.058909 | 0.010626 | 0.028743 | 0.0030953 | -0.0044967 | 0.0022174 | 0.0046998 | 0.01581 | 0.023131 | 0.017248 | -0.0015337 | 0.0020422 | 0.00094419 | -0.1236 | 0.20142 | -0.19684 | -0.17395 | 0.041199 | -0.09613 | -0.036621 | -0.082397 | 0.18768 | -0.14191 | -0.050354 | 0.064087 | -0.036621 | 0.086975 | 122.319 | -0.018311 | -0.39368 | 122.5571 | 122.4792 | 122.4197 | 0.16022 | 0.10071 | 122.374 | -0.032044 | -0.27008 | 122.58 | 122.6028 | 122.4792 | 0.22888 | 0.10529 | 0.23804 | 0.022888 | 0.20599 | 0.091553 | 0.39825 | 0.32959 | 122.7173 | 122.7036 | -0.41657 | -0.36163 | 122.3419 | 122.4655 | 122.3923 | 122.4335
2212.8125 | 122.8134 | -122.4609 | 0.20142 | 0.026321 | -0.059763 | 0.013403 | 0.032161 | 0.0039499 | -0.0027877 | -0.0020552 | 0.001648 | 0.01346 | 0.020781 | 0.014684 | 0.0044477 | 0.0073828 | -0.0071734 | -0.1236 | 0.09613 | -0.20599 | -0.1236 | 0.086975 | -0.091553 | -0.013733 | 0.064087 | 0.15106 | -0.11902 | 0.10071 | 0.17395 | 0.068665 | 0.21515 | 122.2549 | -0.10529 | -0.32501 | 122.5479 | 122.4472 | 122.3694 | 0.19226 | 0.11444 | 122.3419 | -0.050354 | -0.10071 | 122.6349 | 122.6761 | 122.5296 | 0.33417 | 0.18768 | 0.29297 | 0.082398 | 0.29297 | 0.21973 | 0.30212 | 0.27008 | 122.5571 | 122.612 | -0.40741 | -0.32044 | 122.3373 | 122.5616 | 122.3373 | 122.525
2214.5625 | 122.7448 | -122.4792 | 0.21515 | 0.0034333 | -0.060404 | 0.012762 | 0.027461 | 0.00031834 | -0.00065149 | -0.00077335 | 0.0046998 | 0.012606 | 0.02014 | 0.015325 | 0.00017507 | 0.0065284 | 0.003935 | -0.15106 | 0.11902 | -0.20599 | -0.14191 | 0.064087 | -0.091553 | -0.018311 | -0.009155 | 0.16479 | -0.13275 | 0.041199 | 0.13275 | 0.032043 | 0.17395 | 122.2733 | -0.09613 | -0.35706 | 122.5433 | 122.4609 | 122.3877 | 0.18768 | 0.11444 | 122.3465 | -0.050354 | -0.17395 | 122.612 | 122.6532 | 122.5113 | 0.3067 | 0.16479 | 0.27008 | 0.064087 | 0.2655 | 0.17395 | 0.32501 | 0.29755 | 122.5983 | 122.644 | -0.42114 | -0.3479 | 122.3373 | 122.5204 | 122.3282 | 122.4701
2216.3281 | 122.8226 | -122.4564 | 0.20142 | 0.011063 | -0.058695 | 0.011907 | 0.027034 | 0.0030953 | -0.0053513 | -0.0020552 | -0.0014038 | 0.014742 | 0.021209 | 0.017034 | -0.0011065 | 0.0037512 | -0.0014056 | -0.10529 | 0.14648 | -0.1831 | -0.054932 | 0.14648 | -0.009155 | 0.068665 | 0.091553 | 0.14648 | -0.10986 | 0.10071 | 0.21973 | 0.10986 | 0.21515 | 122.2733 | -0.054932 | -0.25635 | 122.6028 | 122.525 | 122.4472 | 0.25177 | 0.17395 | 122.3465 | -0.054932 | -0.10071 | 122.6761 | 122.6715 | 122.5662 | 0.32501 | 0.21973 | 0.32959 | 0.12817 | 0.32959 | 0.21057 | 0.32959 | 0.25635 | 122.6028 | 122.6028 | -0.38452 | -0.31128 | 122.4014 | 122.5571 | 122.3511 | 122.5479
2218.0781 | 122.7905 | -122.4472 | 0.18768 | 0.011063 | -0.056772 | 0.012762 | 0.029598 | 0.0071541 | -0.0030015 | 0.0028582 | 0.0077514 | 0.014529 | 0.022277 | 0.012335 | 0.0029523 | 0.006101 | -0.00012381 | -0.10986 | 0.1236 | -0.21515 | -0.12817 | 0.073242 | -0.10986 | -0.027466 | 0.059509 | 0.16479 | -0.1236 | 0.10071 | 0.17395 | 0.068665 | 0.20599 | 122.2321 | -0.064087 | -0.31586 | 122.5204 | 122.4197 | 122.3373 | 0.18768 | 0.10529 | 122.3236 | -0.022888 | -0.086975 | 122.6212 | 122.6532 | 122.5159 | 0.32959 | 0.19226 | 0.28839 | 0.086975 | 0.29755 | 0.2243 | 0.33875 | 0.28839 | 122.5708 | 122.612 | -0.40283 | -0.31128 | 122.319 | 122.5479 | 122.3373 | 122.5067
2219.7656 | 122.7356 | -122.4838 | 0.22888 | 0.011063 | -0.056345 | 0.01148 | 0.029811 | 0.0048043 | -0.0030015 | 8.125e-05 | 0.001648 | 0.013888 | 0.022063 | 0.015753 | 0.0012433 | 0.0065284 | -0.00055121 | -0.07782 | 0.16937 | -0.19684 | -0.12817 | 0.068665 | -0.086975 | -0.036621 | 0 | 0.18768 | -0.15564 | 0.036621 | 0.11444 | 0.009155 | 0.13275 | 122.287 | -0.059509 | -0.35706 | 122.5525 | 122.4472 | 122.3969 | 0.16022 | 0.10986 | 122.3282 | -0.041199 | -0.19226 | 122.5983 | 122.6166 | 122.493 | 0.28839 | 0.16479 | 0.2655 | 0.068664 | 0.27008 | 0.19226 | 0.36621 | 0.34332 | 122.6532 | 122.6715 | -0.42572 | -0.38452 | 122.3557 | 122.5204 | 122.406 | 122.4838
2221.5469 | 122.7036 | -122.4747 | 0.21973 | -0.0041962 | -0.059122 | 0.012335 | 0.027889 | 0.0054453 | -0.0027877 | 0.0013628 | -0.0014038 | 0.011751 | 0.022704 | 0.011694 | -0.0028155 | 0.0052466 | -0.0037554 | -0.068665 | 0.15106 | -0.18768 | -0.10529 | 0.09613 | -0.036621 | 0.009155 | -0.027466 | 0.19226 | -0.15106 | -0.018311 | 0.082397 | 0.009155 | 0.11444 | 122.287 | -0.068665 | -0.32501 | 122.5708 | 122.4838 | 122.438 | 0.19684 | 0.15106 | 122.3236 | -0.027466 | -0.23804 | 122.5571 | 122.5891 | 122.4838 | 0.2655 | 0.16022 | 0.28381 | 0.082397 | 0.23346 | 0.13275 | 0.33874 | 0.34332 | 122.6257 | 122.6669 | -0.40741 | -0.37079 | 122.3694 | 122.4564 | 122.406 | 122.4472
2223.2969 | 122.8317 | -122.4564 | 0.21057 | 0.011063 | -0.059977 | 0.011053 | 0.028529 | 0.00010474 | 0.00020291 | 0.0013628 | 0.0046998 | 0.01282 | 0.020568 | 0.014684 | -3.8532e-05 | 0.006101 | -0.00055121 | -0.07782 | 0.15106 | -0.15564 | -0.064087 | 0.16022 | 0.009155 | 0.064087 | 0.09613 | 0.12817 | -0.11444 | 0.11444 | 0.21515 | 0.10529 | 0.20599 | 122.3007 | -0.059509 | -0.27466 | 122.6166 | 122.5204 | 122.4655 | 0.21973 | 0.16479 | 122.3419 | -0.082397 | -0.09613 | 122.6715 | 122.6624 | 122.5616 | 0.32044 | 0.21973 | 0.31586 | 0.091553 | 0.32959 | 0.22888 | 0.3067 | 0.24262 | 122.6074 | 122.5845 | -0.36621 | -0.32501 | 122.3923 | 122.5708 | 122.3785 | 122.5525
2225.0469 | 122.7768 | -122.4655 | 0.21057 | 0.026321 | -0.058268 | 0.011694 | 0.029598 | 0.0052315 | -0.0025741 | -0.0024824 | 0.001648 | 0.012606 | 0.020568 | 0.015966 | 0.00038887 | 0.0069556 | 0.00073059 | -0.11444 | 0.10071 | -0.20142 | -0.10986 | 0.10071 | -0.10071 | -0.009155 | 0.045776 | 0.16022 | -0.12817 | 0.068665 | 0.14648 | 0.045776 | 0.17853 | 122.2641 | -0.10986 | -0.32043 | 122.5662 | 122.4564 | 122.3648 | 0.19226 | 0.10071 | 122.3373 | -0.050354 | -0.14191 | 122.612 | 122.644 | 122.5113 | 0.3067 | 0.17395 | 0.30212 | 0.091553 | 0.27466 | 0.19684 | 0.30212 | 0.28839 | 122.5662 | 122.6257 | -0.41199 | -0.33875 | 122.3557 | 122.5342 | 122.3511 | 122.5113
2226.7344 | 122.7539 | -122.4747 | 0.2243 | 0.0034333 | -0.058909 | 0.012335 | 0.030666 | 0.0015999 | -0.0036423 | 8.125e-05 | 0.001648 | 0.016024 | 0.024626 | 0.014898 | 0.00081607 | 0.0056738 | -0.00076481 | -0.091553 | 0.16937 | -0.21057 | -0.14648 | 0.064087 | -0.09613 | -0.032043 | 0 | 0.1831 | -0.13275 | 0.027466 | 0.11444 | 0 | 0.14191 | 122.2641 | -0.054931 | -0.37079 | 122.5388 | 122.4426 | 122.3785 | 0.17853 | 0.11444 | 122.3419 | -0.041199 | -0.19684 | 122.5891 | 122.6166 | 122.4747 | 0.27466 | 0.13275 | 0.27466 | 0.064087 | 0.24719 | 0.16022 | 0.37994 | 0.31586 | 122.644 | 122.6578 | -0.43488 | -0.35706 | 122.3282 | 122.5021 | 122.3831 | 122.4747
2228.4844 | 122.8226 | -122.493 | 0.19684 | 0.0034333 | -0.061472 | 0.01148 | 0.02917 | -0.00032266 | -0.0042831 | -0.00034615 | 0.001648 | 0.013033 | 0.021422 | 0.026861 | 0.00017507 | 0.0056738 | 0.0043622 | -0.10986 | 0.15106 | -0.1831 | -0.07782 | 0.12817 | -0.027466 | 0.032043 | 0.050354 | 0.14191 | -0.11902 | 0.082397 | 0.19684 | 0.086975 | 0.21515 | 122.3099 | -0.045776 | -0.27466 | 122.6212 | 122.525 | 122.4655 | 0.21515 | 0.15564 | 122.374 | -0.054931 | -0.11444 | 122.6898 | 122.7081 | 122.58 | 0.33417 | 0.20599 | 0.31128 | 0.10528 | 0.31586 | 0.20142 | 0.33417 | 0.26093 | 122.644 | 122.6349 | -0.37994 | -0.31586 | 122.4152 | 122.5754 | 122.3831 | 122.5433
2230.2344 | 122.699 | -122.5067 | 0.23346 | 0.0034333 | -0.059336 | 0.011053 | 0.031307 | 0.0037363 | -0.0053513 | 0.0013628 | -0.0014038 | 0.014956 | 0.019286 | 0.0091302 | -0.00025213 | 0.0046058 | 0.0035078 | -0.1236 | 0.20142 | -0.19226 | -0.16022 | 0.022888 | -0.10529 | -0.036621 | -0.09613 | 0.19684 | -0.15564 | -0.045776 | 0.041199 | -0.050354 | 0.10529 | 122.3145 | -0.032043 | -0.39368 | 122.5296 | 122.4701 | 122.4014 | 0.15564 | 0.086975 | 122.3511 | -0.036621 | -0.27924 | 122.5479 | 122.612 | 122.4564 | 0.26093 | 0.10529 | 0.21515 | 0.032044 | 0.19684 | 0.10986 | 0.39368 | 0.35248 | 122.7081 | 122.7036 | -0.42572 | -0.3891 | 122.3465 | 122.4609 | 122.3831 | 122.4106
2232 | 122.6944 | -122.5342 | 0.24261 | 0.011063 | -0.059122 | 0.012548 | 0.031093 | 0.0039499 | -0.0038559 | 0.0011492 | 0.0046998 | 0.014956 | 0.020354 | 0.016393 | -0.0036701 | 0.0041784 | -0.0018328 | -0.11444 | 0.16937 | -0.18768 | -0.15564 | 0.041199 | -0.091553 | -0.022888 | -0.091553 | 0.18768 | -0.14648 | -0.032043 | 0.068665 | -0.032043 | 0.086975 | 122.3465 | -0.073242 | -0.39826 | 122.5754 | 122.5113 | 122.4426 | 0.16479 | 0.09613 | 122.3877 | -0.054932 | -0.27466 | 122.6028 | 122.6212 | 122.5021 | 0.23346 | 0.11444 | 0.22888 | 0.032043 | 0.21515 | 0.11444 | 0.35706 | 0.33417 | 122.7036 | 122.7219 | -0.4303 | -0.3891 | 122.3785 | 122.5021 | 122.4197 | 122.4426
2233.6875 | 122.8226 | -122.4609 | 0.19684 | 0.0034333 | -0.058909 | 0.012548 | 0.029811 | 0.0054453 | -0.0053513 | 0.0013628 | 0.0046998 | 0.01346 | 0.018645 | 0.018102 | -0.0028155 | 0.0041784 | 0.0026532 | -0.07782 | 0.13733 | -0.16937 | -0.050354 | 0.15564 | 0.004578 | 0.050354 | 0.068665 | 0.16479 | -0.091553 | 0.09613 | 0.19684 | 0.091553 | 0.19684 | 122.2916 | -0.059509 | -0.24719 | 122.6166 | 122.5113 | 122.4655 | 0.21973 | 0.17395 | 122.3694 | -0.032043 | -0.10071 | 122.6578 | 122.6578 | 122.5525 | 0.28839 | 0.18311 | 0.32501 | 0.11902 | 0.28839 | 0.18768 | 0.3067 | 0.25635 | 122.5983 | 122.6257 | -0.36621 | -0.28839 | 122.4106 | 122.5571 | 122.3831 | 122.5296
2235.4375 | 122.731 | -122.5021 | 0.2243 | 0.0034333 | -0.060618 | 0.011694 | 0.028529 | 0.0054453 | -0.0027877 | 0.0047808 | 0.001648 | 0.014956 | 0.023131 | 0.015325 | 0.0025251 | 0.0052466 | 0.00094419 | -0.1831 | 0.12817 | -0.2655 | -0.22888 | -0.064087 | -0.21973 | -0.1236 | -0.068665 | 0.19226 | -0.16022 | -0.013733 | 0.036621 | -0.064087 | 0.11444 | 122.2366 | -0.09613 | -0.45319 | 122.438 | 122.3785 | 122.2824 | 0.14191 | 0.045776 | 122.3419 | -0.032043 | -0.23804 | 122.5388 | 122.6166 | 122.438 | 0.27466 | 0.09613 | 0.20142 | 0.036621 | 0.19684 | 0.14648 | 0.39368 | 0.35248 | 122.6303 | 122.6944 | -0.48981 | -0.38452 | 122.2733 | 122.4884 | 122.319 | 122.4335
2237.1875 | 122.7676 | -122.5067 | 0.22888 | 0.011063 | -0.057627 | 0.012548 | 0.031307 | 0.0037363 | -0.0021469 | 0.0028582 | 0.0046998 | 0.015169 | 0.021422 | 0.016393 | 0.0027387 | 0.006742 | 8.9786e-05 | -0.086975 | 0.16022 | -0.20599 | -0.13733 | 0.045776 | -0.11902 | -0.041199 | 0.004578 | 0.17853 | -0.12817 | 0.027466 | 0.11902 | -0.004578 | 0.16022 | 122.3007 | -0.068665 | -0.36621 | 122.5525 | 122.4655 | 122.3877 | 0.1648 | 0.086975 | 122.3785 | -0.050354 | -0.20142 | 122.6257 | 122.6669 | 122.5021 | 0.28839 | 0.1236 | 0.25177 | 0.068665 | 0.24719 | 0.15564 | 0.36621 | 0.3067 | 122.6669 | 122.6852 | -0.43488 | -0.35706 | 122.3694 | 122.5342 | 122.4197 | 122.5113
2238.9531 | 122.7676 | -122.4976 | 0.2243 | 0.011063 | -0.059763 | 0.014257 | 0.030666 | 0.0024545 | -0.0047103 | 0.0026446 | 0.0077514 | 0.01346 | 0.02249 | 0.019811 | 0.00081607 | 0.0071692 | -0.0016192 | -0.18768 | 0.13733 | -0.25177 | -0.21515 | -0.036621 | -0.21057 | -0.1236 | -0.045776 | 0.1831 | -0.14191 | 0.041199 | 0.091553 | -0.004578 | 0.13733 | 122.2458 | -0.086975 | -0.43945 | 122.4609 | 122.374 | 122.287 | 0.12817 | 0.041199 | 122.3557 | -0.041199 | -0.18311 | 122.5891 | 122.6349 | 122.493 | 0.27924 | 0.13733 | 0.21515 | 0.036621 | 0.23346 | 0.18311 | 0.3891 | 0.32501 | 122.6349 | 122.6807 | -0.47607 | -0.36621 | 122.2824 | 122.5388 | 122.3099 | 122.4518
2240.6406 | 122.8088 | -122.493 | 0.21515 | 0.018692 | -0.058268 | 0.012121 | 0.028957 | 0.0013863 | -0.0019333 | 0.0026446 | 0.001648 | 0.013888 | 0.020995 | 0.024511 | -0.0021747 | 0.0052466 | -0.00012381 | -0.064087 | 0.12817 | -0.1831 | -0.068665 | 0.14191 | -0.004578 | 0.036621 | 0.064087 | 0.15564 | -0.13275 | 0.07782 | 0.1831 | 0.07782 | 0.1831 | 122.3099 | -0.086975 | -0.28381 | 122.6349 | 122.5296 | 122.4884 | 0.21973 | 0.17853 | 122.3602 | -0.059509 | -0.13733 | 122.6761 | 122.6761 | 122.5708 | 0.31586 | 0.21057 | 0.32501 | 0.11444 | 0.31586 | 0.21057 | 0.31128 | 0.28839 | 122.6212 | 122.6486 | -0.39825 | -0.3479 | 122.4243 | 122.5708 | 122.4289 | 122.5571
2242.3906 | 122.7539 | -122.5388 | 0.21057 | 0.011063 | -0.05955 | 0.013616 | 0.030452 | 0.0052315 | -0.0023605 | 8.125e-05 | -0.0014038 | 0.014315 | 0.021209 | 0.022161 | -0.0030291 | 0.0046058 | 0.0041486 | -0.068665 | 0.13275 | -0.17853 | -0.086975 | 0.12817 | -0.027466 | 0.018311 | 0.009155 | 0.16022 | -0.1236 | 0.009155 | 0.10986 | 0.013733 | 0.13275 | 122.3602 | -0.07782 | -0.29755 | 122.6669 | 122.5571 | 122.5113 | 0.19684 | 0.15106 | 122.4152 | -0.050354 | -0.20142 | 122.6486 | 122.6715 | 122.5525 | 0.25635 | 0.13733 | 0.3067 | 0.091553 | 0.23346 | 0.13275 | 0.31128 | 0.28381 | 122.6715 | 122.699 | -0.3891 | -0.33417 | 122.4518 | 122.5479 | 122.4701 | 122.5479
2244.1406 | 122.699 | -122.5433 | 0.24719 | -0.0041962 | -0.058909 | 0.012548 | 0.030666 | 0.0056589 | -0.0059921 | 0.00029485 | -0.0014038 | 0.014529 | 0.020354 | 0.011694 | -0.0030291 | 0.0048194 | 0.00051699 | -0.10986 | 0.16937 | -0.20142 | -0.17395 | 0.054932 | -0.086975 | -0.022888 | -0.07782 | 0.18768 | -0.13275 | -0.041199 | 0.07782 | -0.018311 | 0.091553 | 122.3419 | -0.077819 | -0.42114 | 122.5983 | 122.5204 | 122.4564 | 0.17853 | 0.11444 | 122.4106 | -0.059509 | -0.28839 | 122.6212 | 122.6349 | 122.525 | 0.2243 | 0.11444 | 0.25635 | 0.027466 | 0.21057 | 0.091552 | 0.37079 | 0.32043 | 122.7127 | 122.731 | -0.44861 | -0.37994 | 122.3694 | 122.5021 | 122.4335 | 122.4655
2245.8281 | 122.7539 | -122.4976 | 0.23804 | 0.018692 | -0.059336 | 0.013189 | 0.031734 | 0.00053194 | -0.0030015 | -0.0012006 | 0.001648 | 0.015169 | 0.024413 | 0.016393 | 0.00081607 | 0.0052466 | -0.0037554 | -0.16479 | 0.1236 | -0.24261 | -0.21973 | -0.036621 | -0.20142 | -0.13275 | -0.045776 | 0.19226 | -0.14191 | 0.018311 | 0.064087 | -0.027466 | 0.14648 | 122.2549 | -0.11444 | -0.45776 | 122.4609 | 122.3648 | 122.2961 | 0.10986 | 0.041199 | 122.3557 | -0.045776 | -0.21973 | 122.5616 | 122.644 | 122.4701 | 0.28839 | 0.11444 | 0.20599 | 0.022888 | 0.20599 | 0.16022 | 0.36621 | 0.33417 | 122.6212 | 122.6898 | -0.48065 | -0.37994 | 122.2778 | 122.5159 | 122.3328 | 122.4518
2247.5781 | 122.7081 | -122.5433 | 0.2243 | -0.0041962 | -0.059336 | 0.013189 | 0.030238 | 0.0039499 | -0.0032151 | 0.005208 | 0.001648 | 0.017092 | 0.020781 | 0.019384 | 0.0029523 | 0.006742 | -0.00055121 | -0.17853 | 0.14648 | -0.24261 | -0.2243 | -0.073242 | -0.22888 | -0.14191 | -0.11902 | 0.18768 | -0.14648 | -0.022888 | 0.045776 | -0.073242 | 0.09613 | 122.3007 | -0.07782 | -0.44861 | 122.4701 | 122.4014 | 122.3145 | 0.10071 | 0.013733 | 122.3969 | -0.036621 | -0.24719 | 122.5891 | 122.6395 | 122.4701 | 0.24261 | 0.073242 | 0.16937 | 0.018311 | 0.19226 | 0.1236 | 0.3891 | 0.33417 | 122.6898 | 122.731 | -0.46692 | -0.37079 | 122.319 | 122.5204 | 122.3648 | 122.4243
2249.3281 | 122.7905 | -122.525 | 0.21973 | 0.0034333 | -0.059122 | 0.012975 | 0.029598 | 0.0011727 | -0.0036423 | -0.0039778 | -0.0014038 | 0.015169 | 0.02249 | 0.019384 | 0.00081607 | 0.0069556 | 0.0013714 | -0.091553 | 0.16479 | -0.20599 | -0.13733 | 0.064087 | -0.10986 | -0.054932 | 0 | 0.19226 | -0.16022 | 0.027466 | 0.13275 | 0.009155 | 0.13733 | 122.319 | -0.054932 | -0.35706 | 122.5891 | 122.4701 | 122.4152 | 0.15106 | 0.096131 | 122.3648 | -0.027466 | -0.19226 | 122.6578 | 122.6624 | 122.5342 | 0.29755 | 0.16937 | 0.27008 | 0.068665 | 0.29297 | 0.18768 | 0.37079 | 0.35248 | 122.6898 | 122.7173 | -0.42572 | -0.37994 | 122.3877 | 122.5525 | 122.4335 | 122.525
2251.0781 | 122.7585 | -122.5525 | 0.24261 | 0.011063 | -0.05955 | 0.011694 | 0.02917 | 0.0069405 | -0.0047103 | -0.002696 | 0.0046998 | 0.015383 | 0.022704 | 0.018957 | -0.0019611 | 0.0046058 | 8.9786e-05 | -0.14191 | 0.20142 | -0.19226 | -0.18768 | 0 | -0.11902 | -0.041199 | -0.082397 | 0.20142 | -0.14191 | -0.036621 | 0.082397 | -0.032043 | 0.11902 | 122.3602 | -0.041199 | -0.4303 | 122.5525 | 122.5113 | 122.4335 | 0.15106 | 0.073242 | 122.4106 | -0.041199 | -0.27924 | 122.6349 | 122.6715 | 122.5204 | 0.26093 | 0.10986 | 0.19226 | 0.004578 | 0.2243 | 0.10529 | 0.39368 | 0.34332 | 122.7539 | 122.7539 | -0.43488 | -0.38452 | 122.3648 | 122.5159 | 122.4106 | 122.4701
2252.75 | 122.7814 | -122.5296 | 0.20142 | -0.0041962 | -0.056986 | 0.011694 | 0.031093 | 0.0020273 | -0.0030015 | 0.0015764 | -0.0014038 | 0.013033 | 0.019286 | 0.027502 | 0.0040205 | 0.0039648 | 0.0037214 | -0.19226 | 0.13275 | -0.25177 | -0.23346 | -0.041199 | -0.20599 | -0.10529 | -0.059509 | 0.1831 | -0.15106 | 0.036621 | 0.082397 | -0.009155 | 0.14191 | 122.2778 | -0.068665 | -0.43488 | 122.4884 | 122.4243 | 122.3236 | 0.14648 | 0.045776 | 122.3785 | -0.018311 | -0.1648 | 122.612 | 122.6715 | 122.5204 | 0.29297 | 0.14191 | 0.21057 | 0.018311 | 0.23346 | 0.18768 | 0.38452 | 0.33417 | 122.6624 | 122.7127 | -0.45319 | -0.35248 | 122.2961 | 122.5662 | 122.3373 | 122.4701
2254.5 | 122.8638 | -122.4976 | 0.19226 | 0.0034333 | -0.05955 | 0.014684 | 0.030238 | 0.0024545 | -0.00065149 | 0.0020038 | 0.001648 | 0.013674 | 0.021636 | 0.025793 | 0.0038067 | 0.006742 | 0.0026532 | -0.10986 | 0.10071 | -0.2243 | -0.10986 | 0.064087 | -0.10071 | -0.032043 | 0.045776 | 0.12817 | -0.10071 | 0.10071 | 0.17853 | 0.07782 | 0.21973 | 122.2733 | -0.091553 | -0.30212 | 122.5616 | 122.4655 | 122.3969 | 0.19226 | 0.1236 | 122.3969 | -0.064087 | -0.091553 | 122.6761 | 122.7173 | 122.5754 | 0.32044 | 0.17853 | 0.28839 | 0.11444 | 0.27924 | 0.20142 | 0.32501 | 0.22888 | 122.5983 | 122.6257 | -0.41656 | -0.29297 | 122.3877 | 122.5983 | 122.3877 | 122.5433
2256.25 | 122.7585 | -122.5479 | 0.20599 | 0.0034333 | -0.060404 | 0.012975 | 0.030238 | 0.0058725 | -0.0019333 | -0.00077335 | -0.0014038 | 0.014529 | 0.022704 | 0.020452 | 0.0012433 | 0.0046058 | -0.0026874 | -0.17853 | 0.1236 | -0.24261 | -0.23804 | -0.050354 | -0.20599 | -0.1236 | -0.064087 | 0.19226 | -0.13733 | 0.009155 | 0.064087 | -0.059509 | 0.12817 | 122.3053 | -0.082398 | -0.44403 | 122.4976 | 122.4243 | 122.3419 | 0.11902 | 0.036621 | 122.4106 | -0.013733 | -0.19684 | 122.612 | 122.6761 | 122.4884 | 0.2655 | 0.07782 | 0.19226 | 0.004578 | 0.20142 | 0.14648 | 0.36621 | 0.32959 | 122.6715 | 122.7402 | -0.44861 | -0.34332 | 122.3099 | 122.5571 | 122.3694 | 122.4838
2258 | 122.7768 | -122.5433 | 0.24261 | 0.026321 | -0.059336 | 0.0099848 | 0.028743 | 0.0041635 | -0.0049241 | -0.0012006 | 0.001648 | 0.014742 | 0.019927 | 0.013189 | -0.0049517 | 0.0069556 | -0.00012381 | -0.12817 | 0.19684 | -0.20142 | -0.17395 | 0.004578 | -0.11444 | -0.050354 | -0.082397 | 0.1831 | -0.16022 | -0.027466 | 0.086975 | -0.013733 | 0.1236 | 122.3419 | -0.045777 | -0.41656 | 122.5479 | 122.493 | 122.4289 | 0.15106 | 0.086975 | 122.3831 | -0.05951 | -0.27008 | 122.6303 | 122.6669 | 122.5296 | 0.28381 | 0.14648 | 0.20599 | 0.027466 | 0.24719 | 0.13275 | 0.39825 | 0.34332 | 122.7402 | 122.7264 | -0.44403 | -0.40283 | 122.3694 | 122.5159 | 122.4152 | 122.4609
2259.7031 | 122.8134 | -122.5159 | 0.23346 | 0.011063 | -0.060404 | 0.011053 | 0.02618 | 0.0043771 | -0.0023605 | 0.0022174 | 0.0046998 | 0.010683 | 0.022277 | 0.020239 | -0.0019611 | 0.005033 | 0.00030339 | -0.086975 | 0.13733 | -0.17853 | -0.082397 | 0.11902 | -0.027466 | 0.045776 | 0.022888 | 0.16479 | -0.11444 | 0.032043 | 0.13733 | 0.050354 | 0.15106 | 122.3373 | -0.09613 | -0.31586 | 122.6349 | 122.5616 | 122.4884 | 0.2243 | 0.15106 | 122.4014 | -0.068664 | -0.20142 | 122.6532 | 122.6669 | 122.5662 | 0.2655 | 0.16479 | 0.29755 | 0.096131 | 0.25177 | 0.14648 | 0.31586 | 0.27924 | 122.6532 | 122.6807 | -0.41199 | -0.3479 | 122.4335 | 122.5479 | 122.4289 | 122.5388
2261.4688 | 122.8592 | -122.5021 | 0.19226 | 0.0034333 | -0.061259 | 0.013189 | 0.028957 | 0.0071541 | -0.0034287 | 0.00093565 | 0.0046998 | 0.013888 | 0.019927 | 0.019598 | 0.0023115 | 0.0056738 | -0.0016192 | -0.1236 | 0.073242 | -0.23346 | -0.13275 | 0.068665 | -0.13275 | -0.032043 | 0.064087 | 0.14191 | -0.10529 | 0.10986 | 0.16937 | 0.054932 | 0.21515 | 122.2687 | -0.11902 | -0.32501 | 122.5708 | 122.4701 | 122.3694 | 0.20142 | 0.10071 | 122.3968 | -0.050354 | -0.082398 | 122.6715 | 122.7173 | 122.5571 | 0.32044 | 0.16022 | 0.30212 | 0.10071 | 0.27466 | 0.21515 | 0.3067 | 0.24719 | 122.5754 | 122.644 | -0.42572 | -0.29755 | 122.3694 | 122.612 | 122.3785 | 122.5662
2263.2031 | 122.8867 | -122.5113 | 0.19684 | 0.0034333 | -0.060831 | 0.011907 | 0.028316 | 0.0011727 | -0.0017197 | 0.00029485 | 0.0046998 | 0.011965 | 0.019286 | 0.018102 | -0.0038837 | 0.008451 | -0.0031146 | -0.10071 | 0.14191 | -0.19226 | -0.073242 | 0.13275 | -0.032043 | 0.050354 | 0.07782 | 0.15106 | -0.11902 | 0.10071 | 0.20142 | 0.10986 | 0.20142 | 122.319 | -0.054931 | -0.27008 | 122.644 | 122.5616 | 122.4792 | 0.24261 | 0.16022 | 122.3923 | -0.045776 | -0.09613 | 122.7127 | 122.7127 | 122.6212 | 0.32044 | 0.22888 | 0.32501 | 0.11902 | 0.32044 | 0.21973 | 0.33417 | 0.27008 | 122.6532 | 122.6624 | -0.3891 | -0.31586 | 122.4381 | 122.612 | 122.4106 | 122.5891
2264.9688 | 122.8821 | -122.5296 | 0.20142 | 0.011063 | -0.060404 | 0.013403 | 0.028102 | 0.0041635 | -0.0059921 | 0.0015764 | -0.0014038 | 0.01346 | 0.020354 | 0.019384 | -0.00046573 | 0.0071692 | 0.00030339 | -0.12817 | 0.12817 | -0.19684 | -0.086975 | 0.10529 | -0.041199 | 0.032043 | 0.045776 | 0.15106 | -0.13275 | 0.082397 | 0.1831 | 0.09613 | 0.20599 | 122.3328 | -0.073242 | -0.28839 | 122.6349 | 122.5616 | 122.4884 | 0.22888 | 0.15564 | 122.3969 | -0.050354 | -0.11902 | 122.7127 | 122.7356 | 122.6257 | 0.33875 | 0.22888 | 0.30212 | 0.10986 | 0.31586 | 0.21515 | 0.32501 | 0.28381 | 122.6578 | 122.6807 | -0.39825 | -0.33417 | 122.4426 | 122.612 | 122.4014 | 122.5754
2266.6562 | 122.8592 | -122.5388 | 0.21515 | -0.0041962 | -0.06019 | 0.01383 | 0.029811 | 0.0048043 | -0.0023605 | -0.00055975 | 0.0046998 | 0.012179 | 0.021636 | 0.017462 | -0.00025213 | 0.006742 | 0.0028668 | -0.15106 | 0.11444 | -0.20599 | -0.14191 | 0.036621 | -0.09613 | -0.013733 | -0.004578 | 0.15564 | -0.12817 | 0.041199 | 0.14648 | 0.041199 | 0.17395 | 122.3328 | -0.10071 | -0.35706 | 122.5754 | 122.525 | 122.4426 | 0.19226 | 0.10986 | 122.4106 | -0.059509 | -0.17395 | 122.6852 | 122.7127 | 122.58 | 0.30212 | 0.16937 | 0.24262 | 0.064087 | 0.27466 | 0.16937 | 0.32044 | 0.28381 | 122.6532 | 122.6944 | -0.42114 | -0.34332 | 122.3969 | 122.58 | 122.3877 | 122.5342
2268.4062 | 122.7905 | -122.58 | 0.2243 | 0.0034333 | -0.058268 | 0.010626 | 0.033656 | 0.0050179 | -0.0032151 | 0.0011492 | -0.0014038 | 0.016024 | 0.020354 | 0.022375 | -0.0017475 | 0.0048194 | 0.00094419 | -0.1236 | 0.17395 | -0.20599 | -0.14648 | 0.013733 | -0.10071 | -0.041199 | -0.059509 | 0.19226 | -0.15106 | -0.004578 | 0.09613 | -0.022888 | 0.13275 | 122.374 | -0.050354 | -0.37079 | 122.5937 | 122.5388 | 122.4792 | 0.1648 | 0.10529 | 122.4289 | -0.032043 | -0.22888 | 122.6761 | 122.7127 | 122.5571 | 0.28381 | 0.12817 | 0.21973 | 0.05951 | 0.24719 | 0.14648 | 0.37994 | 0.34332 | 122.7539 | 122.7722 | -0.4303 | -0.37537 | 122.4335 | 122.5754 | 122.4564 | 122.5204
2270.1562 | 122.8317 | -122.5479 | 0.19226 | 0.018692 | -0.060618 | 0.014257 | 0.02917 | 0.00095914 | -0.0025741 | 0.00029485 | 0.0046998 | 0.012179 | 0.020568 | 0.025579 | 0.00017507 | 0.0054602 | -0.0014056 | -0.15106 | 0.10986 | -0.20142 | -0.14191 | 0.036621 | -0.11444 | -0.022888 | 0 | 0.15106 | -0.13275 | 0.041199 | 0.11902 | 0.027466 | 0.16022 | 122.3465 | -0.082398 | -0.33417 | 122.5845 | 122.525 | 122.4335 | 0.17853 | 0.086975 | 122.4152 | -0.041199 | -0.15106 | 122.6669 | 122.7081 | 122.5754 | 0.29297 | 0.16022 | 0.23804 | 0.059509 | 0.25177 | 0.17395 | 0.31128 | 0.28381 | 122.6578 | 122.699 | -0.39368 | -0.32501 | 122.406 | 122.5891 | 122.3969 | 122.5479
2271.8438 | 122.905 | -122.5342 | 0.18768 | -0.0041962 | -0.059122 | 0.010626 | 0.029384 | 0.00053194 | -0.0036423 | -0.00098695 | 0.001648 | 0.013674 | 0.021422 | 0.023229 | -0.0017475 | 0.0073828 | -0.0039692 | -0.050354 | 0.1236 | -0.16937 | -0.064087 | 0.16937 | -0.004578 | 0.045776 | 0.09613 | 0.14648 | -0.11902 | 0.091553 | 0.21515 | 0.10071 | 0.20142 | 122.3648 | -0.064087 | -0.25177 | 122.7036 | 122.58 | 122.5296 | 0.21515 | 0.16479 | 122.4152 | -0.041199 | -0.09613 | 122.7493 | 122.7356 | 122.6349 | 0.32044 | 0.21973 | 0.33875 | 0.10529 | 0.33417 | 0.21057 | 0.29297 | 0.2655 | 122.6578 | 122.6807 | -0.35706 | -0.3067 | 122.4701 | 122.6257 | 122.4838 | 122.6303
2273.5781 | 122.731 | -122.5616 | 0.24261 | 0.0034333 | -0.058909 | 0.012762 | 0.031947 | 0.0054453 | -0.0025741 | 0.00029485 | 0.0046998 | 0.015597 | 0.021636 | 0.008703 | 0.0025251 | 0.0052466 | 8.9786e-05 | -0.15106 | 0.14191 | -0.23804 | -0.21515 | -0.032043 | -0.20599 | -0.12817 | -0.10986 | 0.18768 | -0.14648 | -0.032043 | 0.027466 | -0.082397 | 0.10071 | 122.3236 | -0.10071 | -0.45776 | 122.5296 | 122.4335 | 122.3557 | 0.10986 | 0.032043 | 122.4152 | -0.054932 | -0.27466 | 122.5891 | 122.6624 | 122.4792 | 0.24719 | 0.064087 | 0.20599 | 0.022888 | 0.17395 | 0.11444 | 0.37994 | 0.33417 | 122.7036 | 122.7493 | -0.48065 | -0.3891 | 122.3465 | 122.5296 | 122.4106 | 122.4518
2275.3281 | 122.8409 | -122.5571 | 0.21057 | 0.0034333 | -0.06019 | 0.015112 | 0.028957 | 0.0018137 | -0.00086509 | -0.00013235 | 0.0046998 | 0.012606 | 0.021636 | 0.020879 | 0.00038887 | 0.0058874 | 0.00094419 | -0.15564 | 0.10071 | -0.21515 | -0.13275 | 0.054932 | -0.12817 | -0.050354 | -0.009155 | 0.15564 | -0.11444 | 0.036621 | 0.12817 | 0.018311 | 0.15106 | 122.3419 | -0.10986 | -0.34332 | 122.612 | 122.5067 | 122.4289 | 0.16479 | 0.086975 | 122.4426 | -0.054931 | -0.17395 | 122.6852 | 122.7081 | 122.5754 | 0.2655 | 0.13275 | 0.27008 | 0.082398 | 0.24262 | 0.15106 | 0.31586 | 0.27008 | 122.6578 | 122.7127 | -0.42572 | -0.32501 | 122.4243 | 122.5937 | 122.4014 | 122.5479
2277.0938 | 122.905 | -122.525 | 0.20599 | 0.011063 | -0.060618 | 0.012121 | 0.028316 | 0.0037363 | -0.0042831 | 0.0037128 | 0.001648 | 0.011538 | 0.021209 | 0.015112 | -0.0011065 | 0.0063148 | -0.00012381 | -0.09613 | 0.12817 | -0.17395 | -0.054932 | 0.16022 | -0.009155 | 0.064087 | 0.091553 | 0.13733 | -0.12817 | 0.10529 | 0.21515 | 0.11444 | 0.20599 | 122.3511 | -0.07782 | -0.26093 | 122.6852 | 122.5891 | 122.5159 | 0.23804 | 0.16479 | 122.3969 | -0.068665 | -0.10071 | 122.7402 | 122.731 | 122.6395 | 0.33417 | 0.24262 | 0.33417 | 0.11902 | 0.34332 | 0.23346 | 0.30212 | 0.2655 | 122.6532 | 122.6624 | -0.37994 | -0.33417 | 122.4701 | 122.6303 | 122.4289 | 122.6166
2278.8438 | 122.8683 | -122.5296 | 0.1831 | 0.011063 | -0.060831 | 0.011053 | 0.031734 | 0.0048043 | -0.0012925 | 0.0013628 | 0.001648 | 0.014101 | 0.022277 | 0.015325 | 0.0038067 | 0.0056738 | -0.0016192 | -0.1831 | 0.086975 | -0.24261 | -0.14648 | 0.022888 | -0.14648 | -0.059509 | 0.018311 | 0.17395 | -0.11902 | 0.091553 | 0.16479 | 0.045776 | 0.19684 | 122.287 | -0.09613 | -0.32959 | 122.5525 | 122.4701 | 122.3831 | 0.18311 | 0.096131 | 122.4106 | -0.009155 | -0.091552 | 122.6944 | 122.7264 | 122.5754 | 0.31586 | 0.16479 | 0.2655 | 0.096131 | 0.28381 | 0.21057 | 0.32959 | 0.29297 | 122.6166 | 122.7036 | -0.42572 | -0.30212 | 122.3831 | 122.6212 | 122.3465 | 122.5479
2280.5312 | 122.8134 | -122.5616 | 0.21515 | 0.0034333 | -0.059977 | 0.013403 | 0.029598 | 0.0026681 | -0.0034287 | 0.0022174 | -0.0014038 | 0.015169 | 0.020354 | 0.016607 | -0.00046573 | 0.006101 | -0.0026874 | -0.10071 | 0.15564 | -0.21515 | -0.14191 | 0.064087 | -0.10071 | -0.036621 | 0.009155 | 0.20142 | -0.16022 | 0.022888 | 0.10071 | -0.004578 | 0.13733 | 122.3465 | -0.059509 | -0.35706 | 122.6257 | 122.525 | 122.4609 | 0.17853 | 0.11444 | 122.4014 | -0.013733 | -0.19226 | 122.6624 | 122.699 | 122.5571 | 0.29755 | 0.15564 | 0.27924 | 0.073242 | 0.26093 | 0.1831 | 0.37079 | 0.36163 | 122.7173 | 122.7631 | -0.4303 | -0.37537 | 122.4197 | 122.5845 | 122.4609 | 122.5708
2282.2812 | 122.8958 | -122.5616 | 0.23346 | -0.0041962 | -0.05955 | 0.01148 | 0.027461 | 0.0065133 | -0.0023605 | 0.003499 | -0.0014038 | 0.012179 | 0.022917 | 0.011053 | -0.0043109 | 0.0056738 | -0.00055121 | -0.091553 | 0.12817 | -0.18768 | -0.082397 | 0.11444 | -0.027466 | 0.041199 | 0.059509 | 0.15564 | -0.12817 | 0.091553 | 0.20142 | 0.10986 | 0.20142 | 122.374 | -0.10528 | -0.31586 | 122.6761 | 122.6028 | 122.5342 | 0.22888 | 0.16022 | 122.4335 | -0.077819 | -0.14191 | 122.7631 | 122.7631 | 122.6715 | 0.32959 | 0.23804 | 0.30212 | 0.10529 | 0.32959 | 0.21973 | 0.31586 | 0.28381 | 122.6898 | 122.7173 | -0.42114 | -0.36163 | 122.4792 | 122.6532 | 122.4701 | 122.6212
2284.0469 | 122.8546 | -122.5525 | 0.20599 | 0.0034333 | -0.057413 | 0.01383 | 0.029811 | 0.0071541 | -0.0025741 | -0.00034615 | 0.001648 | 0.014742 | 0.02249 | 0.014044 | 0.0029523 | 0.0052466 | 0.003935 | -0.16479 | 0.14648 | -0.24719 | -0.20142 | -0.036621 | -0.21515 | -0.10986 | -0.018311 | 0.18768 | -0.14191 | 0.045776 | 0.1236 | 0.013733 | 0.16937 | 122.3053 | -0.05951 | -0.40741 | 122.5159 | 122.4426 | 122.3373 | 0.13733 | 0.032043 | 122.4106 | -0.018311 | -0.16022 | 122.6761 | 122.7219 | 122.5662 | 0.31128 | 0.15564 | 0.21057 | 0.045776 | 0.2655 | 0.18768 | 0.39368 | 0.32959 | 122.699 | 122.7402 | -0.45319 | -0.3479 | 122.3511 | 122.5983 | 122.3877 | 122.5342
2285.7344 | 122.7814 | -122.5571 | 0.22888 | 0.0034333 | -0.058909 | 0.01148 | 0.032375 | 0.0030953 | -0.0034287 | 0.0037128 | 0.0077514 | 0.016024 | 0.022063 | 0.014898 | 0.0010297 | 0.005033 | 0.00073059 | -0.09613 | 0.16479 | -0.19226 | -0.15106 | 0.041199 | -0.11902 | -0.064087 | -0.018311 | 0.16937 | -0.13275 | 0.004578 | 0.082397 | -0.036621 | 0.1236 | 122.3648 | -0.064087 | -0.37994 | 122.5983 | 122.493 | 122.438 | 0.12817 | 0.073242 | 122.4243 | -0.059509 | -0.2243 | 122.6395 | 122.6807 | 122.5204 | 0.25635 | 0.09613 | 0.23346 | 0.041199 | 0.21515 | 0.13733 | 0.35706 | 0.30212 | 122.7219 | 122.7264 | -0.42114 | -0.36163 | 122.406 | 122.5616 | 122.4609 | 122.5388
2287.4844 | 122.8912 | -122.5113 | 0.18768 | 0.0034333 | -0.060618 | 0.013403 | 0.027461 | 0.00095914 | -0.0010789 | 0.0017902 | 0.0046998 | 0.012392 | 0.022063 | 0.017034 | 0.0029523 | 0.0063148 | -0.0026874 | -0.10529 | 0.07782 | -0.2243 | -0.10986 | 0.09613 | -0.11444 | -0.036621 | 0.082397 | 0.16479 | -0.10986 | 0.10529 | 0.18768 | 0.082397 | 0.19684 | 122.287 | -0.10986 | -0.29755 | 122.6074 | 122.4747 | 122.3969 | 0.18768 | 0.10986 | 122.4014 | -0.022888 | -0.082397 | 122.699 | 122.7081 | 122.5937 | 0.3067 | 0.19226 | 0.32043 | 0.11444 | 0.29755 | 0.21515 | 0.30212 | 0.27466 | 122.5891 | 122.6761 | -0.41199 | -0.29755 | 122.4014 | 122.6166 | 122.406 | 122.5937
2289.2344 | 122.7722 | -122.5983 | 0.24719 | 0.0034333 | -0.058481 | 0.013189 | 0.031734 | 0.00074554 | -0.0023605 | 0.00050845 | 0.001648 | 0.014956 | 0.022063 | 0.017034 | 0.0010297 | 0.0071692 | 8.9786e-05 | -0.16479 | 0.15106 | -0.23804 | -0.20142 | -0.013733 | -0.18768 | -0.11902 | -0.10071 | 0.1831 | -0.14191 | -0.032043 | 0.027466 | -0.086975 | 0.09613 | 122.3602 | -0.09613 | -0.44861 | 122.5845 | 122.4792 | 122.4106 | 0.11902 | 0.050354 | 122.4564 | -0.064087 | -0.27924 | 122.6257 | 122.6944 | 122.5113 | 0.23804 | 0.054932 | 0.2243 | 0.036621 | 0.16937 | 0.10986 | 0.3891 | 0.32501 | 122.7493 | 122.7814 | -0.48523 | -0.3891 | 122.3969 | 122.5662 | 122.4335 | 122.4976
2290.9844 | 122.7722 | -122.5937 | 0.21515 | 0.011063 | -0.058054 | 0.014257 | 0.031307 | 0.0039499 | -0.0017197 | 0.0015764 | 0.001648 | 0.014956 | 0.024413 | 0.014898 | 0.00017507 | 0.0052466 | -0.001192 | -0.1831 | 0.1236 | -0.23346 | -0.2243 | -0.068665 | -0.21057 | -0.11902 | -0.09613 | 0.18768 | -0.16479 | -0.032043 | 0.027466 | -0.073242 | 0.10986 | 122.3602 | -0.091553 | -0.43945 | 122.525 | 122.4747 | 122.3831 | 0.11444 | 0.022888 | 122.4289 | -0.027466 | -0.24719 | 122.6212 | 122.7036 | 122.5204 | 0.27466 | 0.091553 | 0.16479 | 0.009155 | 0.19226 | 0.13275 | 0.35706 | 0.35248 | 122.7173 | 122.7814 | -0.44861 | -0.37994 | 122.3694 | 122.5616 | 122.4106 | 122.4976
2292.6719 | 122.8134 | -122.5616 | 0.20599 | -0.0041962 | -0.058054 | 0.014257 | 0.031734 | 0.0065133 | -0.0030015 | 0.0015764 | 0.0046998 | 0.016024 | 0.023131 | 0.018316 | -0.0013201 | 0.0075964 | 0.0020124 | -0.10529 | 0.16479 | -0.19226 | -0.15564 | 0.054932 | -0.1236 | -0.050354 | -0.013733 | 0.17395 | -0.15106 | 0.004578 | 0.073242 | -0.027466 | 0.13733 | 122.3694 | -0.041199 | -0.36163 | 122.6166 | 122.5113 | 122.438 | 0.14191 | 0.068665 | 122.4106 | -0.032044 | -0.20142 | 122.6349 | 122.699 | 122.5342 | 0.28839 | 0.1236 | 0.24719 | 0.036621 | 0.2243 | 0.15564 | 0.35706 | 0.32501 | 122.7264 | 122.7356 | -0.39826 | -0.35706 | 122.406 | 122.5662 | 122.4564 | 122.5479
2294.4375 | 122.8088 | -122.6212 | 0.24261 | 0.011063 | -0.059977 | 0.011053 | 0.031093 | 0.0043771 | -0.0036423 | 8.125e-05 | -0.0014038 | 0.014956 | 0.022917 | 0.012762 | -0.0032427 | 0.003324 | -0.001192 | -0.12817 | 0.19226 | -0.1831 | -0.17853 | 0.009155 | -0.1236 | -0.045776 | -0.091553 | 0.19684 | -0.15106 | -0.032043 | 0.073242 | -0.032043 | 0.1236 | 122.4381 | -0.050354 | -0.42114 | 122.6303 | 122.5754 | 122.4976 | 0.13733 | 0.059509 | 122.4701 | -0.045777 | -0.27466 | 122.6944 | 122.7448 | 122.5891 | 0.27466 | 0.11902 | 0.19226 | 0.004577 | 0.2243 | 0.11902 | 0.37537 | 0.3479 | 122.8134 | 122.818 | -0.42572 | -0.39368 | 122.4426 | 122.5891 | 122.493 | 122.5296
2296.125 | 122.8043 | -122.6028 | 0.23804 | -0.0041962 | -0.060404 | 0.01148 | 0.030025 | 0.0026681 | -0.0049241 | 0.0011492 | 0.001648 | 0.01581 | 0.021209 | 0.011907 | -0.0023883 | 0.0035376 | -0.00076481 | -0.1236 | 0.20142 | -0.1831 | -0.17853 | 0.022888 | -0.11902 | -0.050354 | -0.10071 | 0.20142 | -0.16937 | -0.045776 | 0.050354 | -0.036621 | 0.09613 | 122.4197 | -0.036621 | -0.41656 | 122.6257 | 122.5525 | 122.4838 | 0.13275 | 0.064086 | 122.4335 | -0.036621 | -0.28381 | 122.6532 | 122.699 | 122.5662 | 0.2655 | 0.13275 | 0.20599 | 0.004577 | 0.21973 | 0.1236 | 0.38452 | 0.37079 | 122.8043 | 122.8043 | -0.42114 | -0.40741 | 122.4243 | 122.5571 | 122.4792 | 122.5021
2297.875 | 122.8455 | -122.6028 | 0.21515 | 0.0034333 | -0.058909 | 0.011694 | 0.030879 | 0.0039499 | -0.0059921 | -0.00055975 | 0.0046998 | 0.017092 | 0.0195 | 0.014684 | 0.00017507 | 0.0052466 | -0.001192 | -0.086975 | 0.15564 | -0.19684 | -0.14648 | 0.073242 | -0.10071 | -0.050354 | -0.004578 | 0.16022 | -0.14191 | 0.022888 | 0.10986 | 0 | 0.16022 | 122.406 | -0.059509 | -0.36163 | 122.6761 | 122.5525 | 122.5021 | 0.14648 | 0.09613 | 122.4609 | -0.054932 | -0.19226 | 122.7127 | 122.7631 | 122.6028 | 0.30212 | 0.14191 | 0.27008 | 0.050354 | 0.25177 | 0.16479 | 0.35248 | 0.30212 | 122.7585 | 122.7631 | -0.41199 | -0.35706 | 122.4564 | 122.6257 | 122.5159 | 122.5983
2299.625 | 122.8363 | -122.6028 | 0.2243 | 0.0034333 | -0.061686 | 0.011907 | 0.027461 | 0.00010474 | -0.0049241 | -0.0020552 | 0.001648 | 0.012606 | 0.020568 | 0.0099848 | -0.00089293 | 0.006101 | 0.0028668 | -0.07782 | 0.1236 | -0.18768 | -0.086975 | 0.13275 | -0.004578 | 0.022888 | 0.004578 | 0.17853 | -0.1236 | -0.004578 | 0.1236 | 0.036621 | 0.14648 | 122.4152 | -0.10071 | -0.31128 | 122.7356 | 122.6257 | 122.5983 | 0.21057 | 0.1831 | 122.4792 | -0.045776 | -0.22888 | 122.7264 | 122.7493 | 122.6395 | 0.27008 | 0.16022 | 0.32043 | 0.10071 | 0.24719 | 0.11902 | 0.31128 | 0.30212 | 122.7264 | 122.7814 | -0.41199 | -0.3479 | 122.5159 | 122.5983 | 122.525 | 122.6074
2301.375 | 122.8775 | -122.5479 | 0.19226 | -0.0041962 | -0.058481 | 0.014471 | 0.029811 | 0.0030953 | -0.0021469 | 0.0011492 | 0.001648 | 0.011324 | 0.020995 | 0.020025 | -0.00025213 | 0.0069556 | 0.0013714 | -0.1236 | 0.09613 | -0.1831 | -0.11902 | 0.091553 | -0.10071 | -0.032043 | 0.059509 | 0.14191 | -0.10986 | 0.054932 | 0.14648 | 0.036621 | 0.17395 | 122.3648 | -0.096131 | -0.31128 | 122.6395 | 122.5159 | 122.4472 | 0.15106 | 0.082397 | 122.438 | -0.050354 | -0.13733 | 122.6944 | 122.7219 | 122.5845 | 0.28381 | 0.14648 | 0.27466 | 0.064086 | 0.25635 | 0.16479 | 0.27924 | 0.25177 | 122.644 | 122.6898 | -0.37537 | -0.30212 | 122.4289 | 122.6028 | 122.4243 | 122.6074
2303.1406 | 122.8775 | -122.5525 | 0.21515 | 0.011063 | -0.060404 | 0.01383 | 0.030238 | 0.0022409 | -0.0027877 | 0.0013628 | 0.0046998 | 0.013033 | 0.019072 | 0.017462 | -3.8532e-05 | 0.0056738 | -0.001192 | -0.12817 | 0.082397 | -0.20599 | -0.1236 | 0.073242 | -0.10529 | -0.022888 | 0.013733 | 0.13275 | -0.11902 | 0.050354 | 0.13275 | 0.041199 | 0.15106 | 122.3465 | -0.13275 | -0.33875 | 122.6257 | 122.5296 | 122.4472 | 0.18311 | 0.10071 | 122.4335 | -0.082398 | -0.16479 | 122.6852 | 122.7036 | 122.5937 | 0.27008 | 0.16022 | 0.27924 | 0.082398 | 0.25177 | 0.16937 | 0.28839 | 0.25177 | 122.6349 | 122.6852 | -0.42114 | -0.33417 | 122.4289 | 122.6028 | 122.4243 | 122.5662
2304.8438 | 122.818 | -122.58 | 0.2243 | 0.0034333 | -0.058695 | 0.012975 | 0.032375 | 0.0067269 | -0.00065149 | -0.002696 | 0.0046998 | 0.01581 | 0.021849 | 0.014471 | 0.0014569 | 0.0046058 | -0.00033761 | -0.17395 | 0.14191 | -0.26093 | -0.23346 | -0.054932 | -0.21515 | -0.1236 | -0.086975 | 0.19226 | -0.17395 | -0.018311 | 0.041199 | -0.059509 | 0.09613 | 122.319 | -0.082397 | -0.45776 | 122.525 | 122.4564 | 122.3648 | 0.13733 | 0.045776 | 122.406 | -0.032043 | -0.24261 | 122.6212 | 122.6761 | 122.5204 | 0.27008 | 0.11444 | 0.20599 | 0.027466 | 0.21515 | 0.15564 | 0.40283 | 0.36621 | 122.7219 | 122.7722 | -0.48523 | -0.39825 | 122.3465 | 122.5616 | 122.406 | 122.493
2306.5938 | 122.7814 | -122.6074 | 0.23804 | 0.0034333 | -0.058909 | 0.015539 | 0.031307 | 0.0097177 | -0.0034287 | -0.00034615 | 0.001648 | 0.014101 | 0.022704 | 0.023229 | -0.00046573 | 0.0052466 | -0.00076481 | -0.16937 | 0.16022 | -0.25177 | -0.23804 | -0.068665 | -0.21515 | -0.15564 | -0.12817 | 0.1831 | -0.16022 | -0.022888 | 0.050354 | -0.082397 | 0.10529 | 122.3557 | -0.07782 | -0.47607 | 122.5388 | 122.4518 | 122.3923 | 0.09613 | 0.036621 | 122.4472 | -0.054932 | -0.26093 | 122.6578 | 122.7127 | 122.525 | 0.2655 | 0.07782 | 0.1831 | 0.013733 | 0.21057 | 0.13733 | 0.41199 | 0.34332 | 122.7676 | 122.7905 | -0.48981 | -0.39825 | 122.3694 | 122.5845 | 122.438 | 122.4792
2308.3438 | 122.9462 | -122.5571 | 0.20142 | 0.0034333 | -0.05955 | 0.012335 | 0.027034 | 0.0039499 | -0.0027877 | -0.0018414 | -0.0014038 | 0.011965 | 0.018218 | 0.018957 | -0.00089293 | 0.00781 | -0.0031146 | -0.091553 | 0.13275 | -0.1831 | -0.064087 | 0.14648 | -0.009155 | 0.054932 | 0.07782 | 0.13275 | -0.11444 | 0.091553 | 0.22888 | 0.091553 | 0.21057 | 122.374 | -0.068665 | -0.2655 | 122.7036 | 122.612 | 122.5479 | 0.23804 | 0.17395 | 122.4426 | -0.068665 | -0.10986 | 122.7859 | 122.7676 | 122.6486 | 0.32501 | 0.20599 | 0.32959 | 0.11902 | 0.34332 | 0.20599 | 0.31586 | 0.24719 | 122.6898 | 122.6898 | -0.38452 | -0.31586 | 122.493 | 122.6486 | 122.4655 | 122.6349
2310.0938 | 122.8088 | -122.6212 | 0.23346 | 0.0034333 | -0.059122 | 0.01383 | 0.03152 | 0.0058725 | -0.0015061 | -0.0016278 | 0.001648 | 0.016237 | 0.019713 | 0.012975 | 0.0016705 | 0.0037512 | 0.00051699 | -0.16479 | 0.16022 | -0.21973 | -0.2243 | -0.064087 | -0.20142 | -0.1236 | -0.091553 | 0.16937 | -0.16479 | -0.036621 | 0.027466 | -0.073242 | 0.10529 | 122.4014 | -0.073242 | -0.45776 | 122.5571 | 122.4976 | 122.4197 | 0.096131 | 0.018311 | 122.4564 | -0.064086 | -0.27008 | 122.6486 | 122.7264 | 122.5479 | 0.27008 | 0.091553 | 0.15564 | -0.004577 | 0.19226 | 0.12817 | 0.37994 | 0.33417 | 122.7814 | 122.7905 | -0.45319 | -0.39825 | 122.3969 | 122.5845 | 122.4564 | 122.5296
2311.8438 | 122.8546 | -122.5845 | 0.20599 | 0.011063 | -0.061686 | 0.014898 | 0.027461 | 0.0090767 | -0.0015061 | 0.00072205 | 0.001648 | 0.014742 | 0.022704 | 0.015753 | 0.0010297 | 0.0056738 | 0.00030339 | -0.17395 | 0.15106 | -0.24261 | -0.20142 | -0.032043 | -0.20142 | -0.11444 | -0.050354 | 0.17853 | -0.12817 | 0.018311 | 0.086975 | -0.027466 | 0.14191 | 122.3419 | -0.054932 | -0.40741 | 122.5525 | 122.4701 | 122.3831 | 0.12817 | 0.041199 | 122.4564 | -0.027466 | -0.18768 | 122.6715 | 122.7264 | 122.5571 | 0.27008 | 0.10071 | 0.21057 | 0.041199 | 0.21515 | 0.14649 | 0.39368 | 0.3067 | 122.7356 | 122.7631 | -0.44861 | -0.33417 | 122.3831 | 122.6028 | 122.4106 | 122.5342
2313.5312 | 122.9141 | -122.6028 | 0.20599 | -0.0041962 | -0.058054 | 0.013189 | 0.027675 | 0.0065133 | -0.0030015 | 0.0015764 | -0.0014038 | 0.013247 | 0.022704 | 0.015966 | -0.00067933 | 0.0065284 | 0.002226 | -0.10986 | 0.091553 | -0.20599 | -0.10986 | 0.10529 | -0.064087 | -0.004578 | 0.082397 | 0.15564 | -0.11444 | 0.082397 | 0.17853 | 0.050354 | 0.19684 | 122.3969 | -0.11444 | -0.31586 | 122.7081 | 122.5983 | 122.5388 | 0.20142 | 0.14191 | 122.4884 | -0.050354 | -0.1236 | 122.7814 | 122.7997 | 122.6532 | 0.31128 | 0.16479 | 0.31128 | 0.096131 | 0.29297 | 0.19684 | 0.29755 | 0.27008 | 122.6944 | 122.7585 | -0.41199 | -0.32044 | 122.493 | 122.6852 | 122.493 | 122.6852
2315.2656 | 122.9279 | -122.5845 | 0.20599 | 0.0034333 | -0.060831 | 0.013616 | 0.030879 | 0.0052315 | -0.0036423 | 0.0022174 | 0.001648 | 0.01346 | 0.019927 | 0.014257 | -0.00046573 | 0.0046058 | -0.0026874 | -0.11902 | 0.12817 | -0.18768 | -0.082397 | 0.086975 | -0.054932 | 0.032043 | 0.050354 | 0.15564 | -0.13275 | 0.068665 | 0.19226 | 0.082397 | 0.18768 | 122.3969 | -0.07782 | -0.28839 | 122.6715 | 122.6166 | 122.5296 | 0.21973 | 0.13275 | 122.4518 | -0.050354 | -0.13733 | 122.7768 | 122.7722 | 122.6669 | 0.32043 | 0.21515 | 0.27466 | 0.10529 | 0.32501 | 0.20142 | 0.31586 | 0.28839 | 122.7127 | 122.7402 | -0.39368 | -0.33875 | 122.5021 | 122.6532 | 122.4655 | 122.6349
2317.0312 | 122.85 | -122.6257 | 0.23804 | 0.0034333 | -0.058268 | 0.011694 | 0.029384 | -0.00010886 | -0.0040695 | -0.00013235 | 0.001648 | 0.014742 | 0.021422 | 0.018957 | -0.0038837 | 0.0041784 | 0.00051699 | -0.07782 | 0.17395 | -0.17853 | -0.082397 | 0.10986 | -0.032043 | 0.013733 | -0.009155 | 0.16022 | -0.13733 | -0.004578 | 0.09613 | -0.022888 | 0.1236 | 122.4472 | -0.064087 | -0.32043 | 122.7356 | 122.6395 | 122.5937 | 0.19226 | 0.14648 | 122.4884 | -0.07782 | -0.24261 | 122.7219 | 122.7493 | 122.6028 | 0.26093 | 0.11444 | 0.28839 | 0.096131 | 0.23346 | 0.13275 | 0.35248 | 0.29755 | 122.7997 | 122.7859 | -0.41656 | -0.37537 | 122.5433 | 122.6212 | 122.5479 | 122.6166
2318.7188 | 122.8134 | -122.6349 | 0.22888 | 0.011063 | -0.06019 | 0.011267 | 0.02917 | 0.0033089 | -0.0057785 | 0.0013628 | -0.0014038 | 0.01346 | 0.023131 | 0.0095574 | -0.0032427 | 0.005033 | 0.001585 | -0.086975 | 0.17853 | -0.17395 | -0.13275 | 0.064087 | -0.07782 | -0.018311 | -0.050354 | 0.17853 | -0.14648 | -0.041199 | 0.064087 | -0.036621 | 0.10071 | 122.4609 | -0.050354 | -0.36163 | 122.699 | 122.6166 | 122.5571 | 0.15564 | 0.09613 | 122.4884 | -0.050354 | -0.27008 | 122.699 | 122.7356 | 122.5983 | 0.24719 | 0.10986 | 0.23804 | 0.041199 | 0.21057 | 0.10529 | 0.35248 | 0.32501 | 122.8134 | 122.8134 | -0.40283 | -0.37537 | 122.5021 | 122.5937 | 122.5479 | 122.5845
2320.4688 | 122.8363 | -122.6028 | 0.2243 | 0.0034333 | -0.057841 | 0.012335 | 0.032588 | 0.0054453 | -0.0040695 | -0.0020552 | 0.001648 | 0.016878 | 0.022063 | 0.0093438 | -0.00025213 | 0.004392 | -0.0033282 | -0.09613 | 0.15564 | -0.19226 | -0.14648 | 0.032043 | -0.1236 | -0.068665 | -0.032043 | 0.17853 | -0.14191 | -0.009155 | 0.073242 | -0.045776 | 0.11902 | 122.4106 | -0.068664 | -0.37079 | 122.6349 | 122.5342 | 122.4792 | 0.1236 | 0.068665 | 122.4609 | -0.045776 | -0.23346 | 122.6761 | 122.7219 | 122.5571 | 0.26093 | 0.096131 | 0.2243 | 0.045777 | 0.21515 | 0.13275 | 0.3479 | 0.32044 | 122.7585 | 122.7814 | -0.41656 | -0.36621 | 122.4564 | 122.5937 | 122.5067 | 122.5708
2322.2344 | 122.9462 | -122.5845 | 0.18768 | 0.0034333 | -0.058909 | 0.014044 | 0.027889 | 0.0015999 | -0.0025741 | 0.002431 | 0.001648 | 0.012392 | 0.021422 | 0.015112 | 0.0038067 | 0.006101 | -0.0033282 | -0.09613 | 0.068665 | -0.19684 | -0.09613 | 0.091553 | -0.086975 | -0.027466 | 0.068665 | 0.13733 | -0.1236 | 0.10071 | 0.18768 | 0.068665 | 0.19684 | 122.3877 | -0.11902 | -0.28381 | 122.6761 | 122.5571 | 122.4976 | 0.16937 | 0.10986 | 122.4609 | -0.050354 | -0.086975 | 122.7722 | 122.7814 | 122.6532 | 0.32043 | 0.19226 | 0.28839 | 0.10071 | 0.31128 | 0.2243 | 0.2655 | 0.26093 | 122.6532 | 122.7219 | -0.38452 | -0.31128 | 122.4884 | 122.6852 | 122.4884 | 122.6532
2323.9219 | 122.9599 | -122.6074 | 0.18768 | 0.0034333 | -0.060618 | 0.012975 | 0.028957 | 0.0050179 | -0.0034287 | -0.00055975 | 0.001648 | 0.013674 | 0.022704 | 0.024511 | -0.0038837 | 0.005033 | 0.0047894 | -0.10986 | 0.14191 | -0.16937 | -0.07782 | 0.11444 | -0.041199 | 0.045776 | 0.027466 | 0.15564 | -0.12817 | 0.07782 | 0.19226 | 0.082397 | 0.20599 | 122.438 | -0.045776 | -0.2655 | 122.7219 | 122.6532 | 122.5662 | 0.21515 | 0.12817 | 122.4792 | -0.032043 | -0.10986 | 122.7997 | 122.8134 | 122.6898 | 0.33417 | 0.21057 | 0.28381 | 0.091553 | 0.32044 | 0.20599 | 0.31128 | 0.28381 | 122.7493 | 122.7631 | -0.35706 | -0.31586 | 122.5296 | 122.6852 | 122.4976 | 122.6349
2325.6719 | 122.8775 | -122.6074 | 0.19684 | -0.0041962 | -0.060618 | 0.012121 | 0.030025 | 0.0011727 | -0.0025741 | -0.00055975 | -0.0014038 | 0.012392 | 0.022277 | 0.018743 | -0.0021747 | 0.0075964 | -0.0014056 | -0.13733 | 0.13733 | -0.19684 | -0.14648 | 0.050354 | -0.09613 | -0.022888 | -0.013733 | 0.14648 | -0.14191 | 0.032043 | 0.12817 | 0.013733 | 0.14648 | 122.4106 | -0.059509 | -0.34332 | 122.6578 | 122.5845 | 122.5113 | 0.17395 | 0.10071 | 122.4655 | -0.050354 | -0.1648 | 122.7356 | 122.7539 | 122.6212 | 0.28839 | 0.15564 | 0.24719 | 0.050354 | 0.27008 | 0.17395 | 0.33417 | 0.28839 | 122.7448 | 122.7539 | -0.39368 | -0.33875 | 122.4609 | 122.6395 | 122.4701 | 122.5937
2327.4219 | 122.8088 | -122.6486 | 0.22888 | 0.0034333 | -0.058909 | 0.01383 | 0.032161 | 0.0045907 | -0.0032151 | 0.0028582 | 0.0046998 | 0.016665 | 0.022917 | 0.009771 | 0.0020979 | 0.0058874 | 0.0020124 | -0.14648 | 0.16022 | -0.24261 | -0.21515 | -0.059509 | -0.19684 | -0.14191 | -0.10986 | 0.18768 | -0.16479 | -0.036621 | 0.027466 | -0.07782 | 0.086975 | 122.406 | -0.068665 | -0.44403 | 122.5891 | 122.5067 | 122.4518 | 0.10071 | 0.045777 | 122.4838 | -0.041199 | -0.2655 | 122.6761 | 122.7356 | 122.5708 | 0.25177 | 0.086975 | 0.18311 | 0.027466 | 0.19226 | 0.12817 | 0.40283 | 0.35248 | 122.8088 | 122.8363 | -0.4715 | -0.39368 | 122.4335 | 122.612 | 122.5021 | 122.5388
2329.125 | 122.85 | -122.6257 | 0.20599 | 0.0034333 | -0.059336 | 0.013616 | 0.029384 | 0.0065133 | -0.0019333 | 0.0032854 | 0.001648 | 0.012392 | 0.021209 | 0.015753 | 0.00038887 | 0.0063148 | -0.0033282 | -0.16937 | 0.14191 | -0.24719 | -0.21515 | -0.018311 | -0.18768 | -0.10529 | -0.064087 | 0.1831 | -0.15106 | 0.004578 | 0.064087 | -0.045776 | 0.13275 | 122.3785 | -0.064087 | -0.42114 | 122.6074 | 122.5204 | 122.438 | 0.14191 | 0.059509 | 122.4747 | -0.022889 | -0.20142 | 122.6898 | 122.7585 | 122.58 | 0.28381 | 0.10529 | 0.22888 | 0.032043 | 0.21515 | 0.15564 | 0.3891 | 0.33417 | 122.7676 | 122.8088 | -0.45319 | -0.35706 | 122.4106 | 122.6303 | 122.4564 | 122.5616
2330.875 | 122.905 | -122.612 | 0.17853 | -0.0041962 | -0.061686 | 0.012335 | 0.027889 | 0.0026681 | -0.0012925 | 0.0026446 | -0.0014038 | 0.014956 | 0.021209 | 0.019811 | 0.00017507 | 0.0063148 | -0.0020464 | -0.13275 | 0.1236 | -0.21057 | -0.10986 | 0.082397 | -0.11444 | -0.013733 | 0.018311 | 0.14648 | -0.1236 | 0.045776 | 0.15106 | 0.022888 | 0.16022 | 122.4014 | -0.054932 | -0.28839 | 122.6944 | 122.5983 | 122.4976 | 0.19684 | 0.09613 | 122.4884 | -0.032044 | -0.13275 | 122.7631 | 122.7722 | 122.6349 | 0.28381 | 0.14648 | 0.29297 | 0.10071 | 0.27466 | 0.16937 | 0.33417 | 0.27008 | 122.7356 | 122.7585 | -0.3891 | -0.30212 | 122.5021 | 122.6578 | 122.4792 | 122.6303
2332.625 | 122.8592 | -122.6257 | 0.22888 | -0.0041962 | -0.058481 | 0.011694 | 0.030879 | 0.0071541 | -0.0019333 | 0.0020038 | 0.001648 | 0.013888 | 0.020568 | 0.012975 | -3.8532e-05 | 0.0073828 | 0.003294 | -0.10071 | 0.16937 | -0.1831 | -0.14648 | 0.054932 | -0.1236 | -0.064087 | -0.013733 | 0.16479 | -0.13733 | 0.004578 | 0.086975 | -0.036621 | 0.11444 | 122.4426 | -0.059509 | -0.37537 | 122.6807 | 122.5616 | 122.5021 | 0.11902 | 0.059509 | 122.4884 | -0.064087 | -0.2243 | 122.7127 | 122.7402 | 122.5891 | 0.25177 | 0.10071 | 0.23804 | 0.036621 | 0.2243 | 0.14191 | 0.35248 | 0.30212 | 122.7951 | 122.7905 | -0.41199 | -0.36621 | 122.4792 | 122.6303 | 122.525 | 122.612
2334.375 | 122.9691 | -122.6074 | 0.1831 | 0.0034333 | -0.062113 | 0.013189 | 0.027675 | 0.0054453 | -0.0032151 | -0.00034615 | 0.001648 | 0.013033 | 0.019713 | 0.017889 | -0.0019611 | 0.0046058 | -0.00097841 | -0.09613 | 0.13733 | -0.17853 | -0.082397 | 0.14191 | -0.013733 | 0.059509 | 0.068665 | 0.15106 | -0.1236 | 0.091553 | 0.19684 | 0.10529 | 0.21515 | 122.4289 | -0.045776 | -0.2655 | 122.7493 | 122.6669 | 122.5937 | 0.23804 | 0.16479 | 122.4838 | -0.032043 | -0.091552 | 122.8043 | 122.8226 | 122.7127 | 0.33875 | 0.22888 | 0.32044 | 0.096131 | 0.32043 | 0.21515 | 0.31586 | 0.27466 | 122.7448 | 122.7585 | -0.36163 | -0.3067 | 122.525 | 122.699 | 122.5113 | 122.6761
2336.125 | 122.818 | -122.6532 | 0.2243 | 0.0034333 | -0.05955 | 0.010198 | 0.032161 | 0.0082223 | -0.0036423 | -0.0012006 | 0.001648 | 0.015383 | 0.019713 | 0.014471 | -3.8532e-05 | 0.004392 | 0.0013714 | -0.14648 | 0.16479 | -0.21973 | -0.20142 | -0.013733 | -0.19226 | -0.10529 | -0.09613 | 0.19684 | -0.14191 | -0.036621 | 0.022888 | -0.091553 | 0.09613 | 122.4335 | -0.059509 | -0.42572 | 122.6395 | 122.5479 | 122.4609 | 0.11444 | 0.027466 | 122.5113 | -0.027466 | -0.26093 | 122.6761 | 122.7493 | 122.5616 | 0.23804 | 0.050354 | 0.20599 | 0.018311 | 0.16479 | 0.10529 | 0.38452 | 0.33875 | 122.818 | 122.85 | -0.44403 | -0.36621 | 122.4518 | 122.6166 | 122.5067 | 122.5571
2337.8281 | 122.8271 | -122.6395 | 0.2243 | -0.0041962 | -0.057627 | 0.011267 | 0.031734 | 0.0058725 | -0.0027877 | 0.00093565 | -0.0014038 | 0.016451 | 0.023772 | 0.014898 | -0.0013201 | 0.0058874 | -0.0018328 | -0.10529 | 0.16937 | -0.20599 | -0.16479 | -0.004578 | -0.16479 | -0.09613 | -0.041199 | 0.18768 | -0.14191 | -0.013733 | 0.045776 | -0.068665 | 0.10071 | 122.4335 | -0.054931 | -0.3891 | 122.6349 | 122.5433 | 122.4747 | 0.10986 | 0.041199 | 122.4976 | -0.036621 | -0.23804 | 122.6852 | 122.7402 | 122.5708 | 0.24262 | 0.073242 | 0.20142 | 0.041199 | 0.18768 | 0.12817 | 0.37537 | 0.32959 | 122.8088 | 122.8271 | -0.4303 | -0.36621 | 122.4747 | 122.6257 | 122.5342 | 122.5983
2339.5625 | 122.9416 | -122.6074 | 0.20142 | 0.011063 | -0.059336 | 0.014044 | 0.031093 | 0.0041635 | -0.0012925 | 0.0011492 | 0.0046998 | 0.014315 | 0.021636 | 0.017248 | 0.0023115 | 0.0069556 | -0.0018328 | -0.15106 | 0.13733 | -0.21057 | -0.16937 | 0.036621 | -0.1236 | -0.050354 | 0.013733 | 0.15564 | -0.1236 | 0.086975 | 0.15564 | 0.036621 | 0.20142 | 122.3969 | -0.064087 | -0.37079 | 122.644 | 122.5571 | 122.4838 | 0.16022 | 0.086975 | 122.4838 | -0.045776 | -0.11444 | 122.7631 | 122.8088 | 122.644 | 0.32501 | 0.16022 | 0.24719 | 0.041198 | 0.27924 | 0.21057 | 0.3479 | 0.27924 | 122.7448 | 122.7631 | -0.41199 | -0.32501 | 122.438 | 122.6944 | 122.4564 | 122.6212
2341.25 | 122.8867 | -122.644 | 0.20142 | 0.011063 | -0.058695 | 0.014044 | 0.033016 | 0.0041635 | -0.0036423 | 0.0030718 | -0.0014038 | 0.014742 | 0.02249 | 0.014684 | 0.0010297 | 0.004392 | 0.0013714 | -0.16022 | 0.16937 | -0.24261 | -0.20142 | -0.013733 | -0.17853 | -0.10529 | -0.050354 | 0.16937 | -0.16479 | 0 | 0.07782 | -0.032043 | 0.1236 | 122.4014 | -0.032043 | -0.40283 | 122.6303 | 122.5388 | 122.4655 | 0.13733 | 0.064087 | 122.4792 | -0.032043 | -0.20142 | 122.7219 | 122.7676 | 122.612 | 0.28839 | 0.13275 | 0.22888 | 0.041199 | 0.24261 | 0.16479 | 0.41199 | 0.33417 | 122.8134 | 122.8134 | -0.44403 | -0.36621 | 122.4426 | 122.644 | 122.4838 | 122.5937
2343.0156 | 122.9507 | -122.6303 | 0.19226 | 0.011063 | -0.061259 | 0.011907 | 0.029811 | 0.0056589 | -0.0036423 | 0.00029485 | 0.001648 | 0.013888 | 0.020995 | 0.017889 | 0.0020979 | 0.0082374 | 0.0011578 | -0.15106 | 0.12817 | -0.21973 | -0.15564 | 0.045776 | -0.1236 | -0.036621 | 0.027466 | 0.15106 | -0.12817 | 0.082397 | 0.16479 | 0.045776 | 0.21057 | 122.4106 | -0.064087 | -0.3479 | 122.6761 | 122.5937 | 122.5067 | 0.18311 | 0.096131 | 122.5021 | -0.041199 | -0.10986 | 122.7951 | 122.8409 | 122.6761 | 0.33875 | 0.17395 | 0.2655 | 0.064087 | 0.29297 | 0.21057 | 0.3479 | 0.27924 | 122.7585 | 122.7814 | -0.41199 | -0.32044 | 122.4747 | 122.7127 | 122.4792 | 122.6578
2344.7656 | 122.9736 | -122.6212 | 0.21057 | 0.011063 | -0.060831 | 0.010626 | 0.028316 | 0.0035227 | -0.0036423 | 0.0030718 | 0.001648 | 0.012179 | 0.019713 | 0.015539 | -0.0030291 | 0.0048194 | -0.00076481 | -0.054932 | 0.13733 | -0.15564 | -0.050354 | 0.18768 | 0.013733 | 0.064087 | 0.086975 | 0.16022 | -0.12817 | 0.082397 | 0.20599 | 0.10071 | 0.20142 | 122.4655 | -0.073242 | -0.26093 | 122.8088 | 122.6852 | 122.6349 | 0.21973 | 0.16937 | 122.493 | -0.050354 | -0.12817 | 122.8271 | 122.8226 | 122.7219 | 0.32959 | 0.22888 | 0.34332 | 0.10529 | 0.33417 | 0.21057 | 0.29297 | 0.28839 | 122.7585 | 122.7814 | -0.36621 | -0.33875 | 122.5708 | 122.7036 | 122.5662 | 122.7081
2346.5312 | 122.9462 | -122.644 | 0.19226 | 0.0034333 | -0.059763 | 0.013403 | 0.027461 | 0.00095914 | -0.0032151 | 0.0028582 | 0.001648 | 0.013247 | 0.020781 | 0.018102 | -0.0032427 | 0.0048194 | -0.0020464 | -0.059509 | 0.13733 | -0.15564 | -0.045776 | 0.16022 | 0.004578 | 0.050354 | 0.045776 | 0.14648 | -0.1236 | 0.054932 | 0.1831 | 0.082397 | 0.17853 | 122.4884 | -0.054932 | -0.23804 | 122.8043 | 122.6944 | 122.6486 | 0.20599 | 0.16022 | 122.5204 | -0.045777 | -0.13733 | 122.8271 | 122.8226 | 122.7264 | 0.30212 | 0.20599 | 0.31586 | 0.10986 | 0.3067 | 0.17853 | 0.29297 | 0.27008 | 122.7814 | 122.7905 | -0.3479 | -0.31586 | 122.5983 | 122.699 | 122.5845 | 122.6898
2348.2344 | 122.8592 | -122.6624 | 0.21973 | 0.011063 | -0.060831 | 0.013403 | 0.031093 | 0.0041635 | -0.0019333 | 0.0022174 | -0.0014038 | 0.017306 | 0.021636 | 0.015966 | 0.0023115 | 0.0052466 | 0.0037214 | -0.14648 | 0.16479 | -0.21515 | -0.20599 | -0.036621 | -0.19684 | -0.10071 | -0.07782 | 0.19226 | -0.15106 | 0 | 0.054932 | -0.064087 | 0.10529 | 122.4472 | -0.054932 | -0.42572 | 122.6257 | 122.5616 | 122.4655 | 0.11444 | 0.018311 | 122.5113 | -0.027466 | -0.21973 | 122.7173 | 122.7676 | 122.5983 | 0.25635 | 0.086975 | 0.17853 | 0.009155 | 0.20599 | 0.15106 | 0.37994 | 0.34332 | 122.8271 | 122.8546 | -0.43488 | -0.37079 | 122.4564 | 122.6624 | 122.5159 | 122.5845
2349.9844 | 122.9279 | -122.6166 | 0.20599 | 0.011063 | -0.061472 | 0.012335 | 0.030879 | 0.0054453 | -0.0036423 | 0.0017902 | -0.0014038 | 0.013247 | 0.022277 | 0.012335 | 0.00060247 | 0.0069556 | 8.9786e-05 | -0.10986 | 0.11444 | -0.17395 | -0.11444 | 0.082397 | -0.086975 | -0.004578 | 0.032043 | 0.13275 | -0.10986 | 0.036621 | 0.13275 | 0.027466 | 0.16937 | 122.4426 | -0.091553 | -0.32044 | 122.699 | 122.612 | 122.5296 | 0.16937 | 0.086975 | 122.5067 | -0.073243 | -0.16937 | 122.7493 | 122.7859 | 122.644 | 0.27924 | 0.13733 | 0.25635 | 0.059509 | 0.24261 | 0.14648 | 0.28839 | 0.24261 | 122.731 | 122.7493 | -0.37994 | -0.31586 | 122.5021 | 122.6532 | 122.5067 | 122.6486
2351.7344 | 122.9095 | -122.6578 | 0.21057 | 0.011063 | -0.06019 | 0.014898 | 0.030666 | 0.0082223 | -0.0012925 | -0.0018414 | 0.001648 | 0.012606 | 0.020995 | 0.017034 | 0.00060247 | 0.0086646 | 0.001585 | -0.15106 | 0.16022 | -0.2243 | -0.18768 | -0.018311 | -0.17853 | -0.091553 | -0.036621 | 0.17853 | -0.13275 | 0.041199 | 0.10071 | -0.009155 | 0.14648 | 122.4335 | -0.050354 | -0.39825 | 122.6395 | 122.5662 | 122.4792 | 0.13275 | 0.045776 | 122.525 | -0.032043 | -0.16937 | 122.7585 | 122.8043 | 122.6486 | 0.27924 | 0.1236 | 0.20599 | 0.036621 | 0.23346 | 0.17395 | 0.38452 | 0.31128 | 122.818 | 122.8363 | -0.43488 | -0.34332 | 122.4701 | 122.699 | 122.5067 | 122.6212
2353.4219 | 122.9645 | -122.6349 | 0.18768 | -0.0041962 | -0.059977 | 0.011267 | 0.030238 | 0.0041635 | -0.0021469 | 0.00050845 | -0.0014038 | 0.013033 | 0.021422 | 0.015325 | 0.0010297 | 0.006742 | 0.0017988 | -0.13275 | 0.14648 | -0.21973 | -0.13275 | 0.050354 | -0.11444 | -0.022888 | 0.036621 | 0.15106 | -0.13733 | 0.082397 | 0.16479 | 0.050354 | 0.21515 | 122.4152 | -0.041199 | -0.32043 | 122.6852 | 122.612 | 122.5204 | 0.19684 | 0.10529 | 122.4976 | -0.036621 | -0.10529 | 122.7997 | 122.85 | 122.6852 | 0.35248 | 0.18768 | 0.27008 | 0.086976 | 0.30212 | 0.21973 | 0.36621 | 0.28839 | 122.7814 | 122.7859 | -0.40741 | -0.32501 | 122.5021 | 122.7173 | 122.5021 | 122.6715
2355.1562 | 122.9736 | -122.612 | 0.21515 | 0.011063 | -0.057627 | 0.011907 | 0.026607 | 0.00053194 | -0.0027877 | 0.0026446 | 0.001648 | 0.013033 | 0.02249 | 0.013189 | -0.0026019 | 0.0054602 | -0.00012381 | -0.073242 | 0.16937 | -0.15564 | -0.045776 | 0.17853 | 0.009155 | 0.073242 | 0.073242 | 0.15564 | -0.10071 | 0.07782 | 0.20142 | 0.09613 | 0.19684 | 122.4564 | -0.045776 | -0.26093 | 122.7905 | 122.6852 | 122.6212 | 0.22888 | 0.16479 | 122.5113 | -0.059509 | -0.13733 | 122.8134 | 122.8088 | 122.7081 | 0.29755 | 0.19684 | 0.33417 | 0.10986 | 0.30212 | 0.17853 | 0.32501 | 0.25635 | 122.7814 | 122.7676 | -0.37079 | -0.31586 | 122.5662 | 122.6898 | 122.5388 | 122.6852
2356.9062 | 122.9233 | -122.6303 | 0.1831 | 0.011063 | -0.059336 | 0.011907 | 0.030666 | 0.0033089 | -0.0025741 | -0.00098695 | 0.0046998 | 0.014529 | 0.019072 | 0.012975 | 0.0014569 | 0.006101 | -0.00012381 | -0.10986 | 0.11902 | -0.16937 | -0.11902 | 0.10529 | -0.10529 | 0 | 0.041199 | 0.14191 | -0.10986 | 0.054932 | 0.13275 | 0.041199 | 0.16937 | 122.4609 | -0.064086 | -0.30212 | 122.7356 | 122.6303 | 122.525 | 0.16937 | 0.064087 | 122.5204 | -0.041198 | -0.12817 | 122.7631 | 122.7997 | 122.6715 | 0.27924 | 0.15106 | 0.27466 | 0.050354 | 0.24261 | 0.16479 | 0.28839 | 0.25177 | 122.7493 | 122.7722 | -0.35248 | -0.29297 | 122.5113 | 122.6852 | 122.5204 | 122.6715
2358.6719 | 122.9004 | -122.6669 | 0.23346 | 0.018692 | -0.059336 | 0.010626 | 0.030452 | 0.0022409 | -0.0038559 | 0.002431 | 0.0046998 | 0.015169 | 0.019072 | 0.0093438 | 0.00017507 | 0.0028968 | -0.0014056 | -0.10529 | 0.21057 | -0.1831 | -0.14191 | 0.036621 | -0.07782 | -0.013733 | -0.054932 | 0.20142 | -0.14191 | -0.013733 | 0.10529 | -0.009155 | 0.14191 | 122.4838 | -0.022888 | -0.37537 | 122.7036 | 122.6532 | 122.5891 | 0.16937 | 0.10528 | 122.525 | -0.032043 | -0.24719 | 122.7722 | 122.8088 | 122.6578 | 0.28381 | 0.13275 | 0.21973 | 0.041198 | 0.24719 | 0.12817 | 0.39368 | 0.34332 | 122.8775 | 122.8683 | -0.41656 | -0.37537 | 122.525 | 122.6532 | 122.5616 | 122.612
2360.3594 | 122.8546 | -122.6807 | 0.21973 | 0.0034333 | -0.06019 | 0.0097712 | 0.031307 | 0.0033089 | -0.0025741 | 0.0015764 | -0.0014038 | 0.016024 | 0.022277 | 0.0084894 | -0.0011065 | 0.0028968 | 0.0017988 | -0.1236 | 0.20599 | -0.19684 | -0.16022 | 0.027466 | -0.09613 | -0.022888 | -0.07782 | 0.16022 | -0.17395 | -0.045776 | 0.059509 | -0.045776 | 0.10529 | 122.4838 | -0.013733 | -0.37994 | 122.7081 | 122.6578 | 122.5845 | 0.17395 | 0.10071 | 122.5067 | -0.05951 | -0.2655 | 122.7402 | 122.7859 | 122.6349 | 0.27924 | 0.12817 | 0.2243 | 0.036621 | 0.23346 | 0.12817 | 0.40283 | 0.33417 | 122.8867 | 122.8409 | -0.41657 | -0.39368 | 122.5204 | 122.6349 | 122.5571 | 122.6028
2362.1094 | 122.9782 | -122.612 | 0.18768 | 0.0034333 | -0.058268 | 0.013616 | 0.030238 | 0.0054453 | -0.0042831 | -0.00055975 | 0.0046998 | 0.01282 | 0.020781 | 0.015753 | 0.0031659 | 0.0065284 | -0.001192 | -0.064087 | 0.11444 | -0.17853 | -0.086975 | 0.1236 | -0.068665 | 0.004578 | 0.068665 | 0.15106 | -0.10986 | 0.09613 | 0.18768 | 0.064087 | 0.21973 | 122.4335 | -0.073242 | -0.27466 | 122.7356 | 122.6166 | 122.5433 | 0.18311 | 0.10986 | 122.5021 | -0.036621 | -0.091553 | 122.7997 | 122.8317 | 122.6761 | 0.32959 | 0.17395 | 0.30212 | 0.091553 | 0.29755 | 0.20599 | 0.29297 | 0.26093 | 122.7264 | 122.7631 | -0.36621 | -0.29755 | 122.525 | 122.7081 | 122.5479 | 122.6807
2363.8125 | 122.937 | -122.6303 | 0.21515 | 0.0034333 | -0.061899 | 0.010198 | 0.028529 | 0.0030953 | -0.0040695 | -0.00098695 | 0.001648 | 0.012179 | 0.02014 | 0.013616 | -0.0015337 | 0.0073828 | -0.00097841 | -0.12817 | 0.14191 | -0.1831 | -0.11902 | 0.068665 | -0.086975 | -0.018311 | -0.036621 | 0.16479 | -0.13733 | 0.027466 | 0.13275 | 0.032043 | 0.16022 | 122.4472 | -0.073242 | -0.33417 | 122.699 | 122.612 | 122.5433 | 0.16479 | 0.09613 | 122.493 | -0.050354 | -0.18768 | 122.7631 | 122.7905 | 122.6624 | 0.29755 | 0.16937 | 0.25177 | 0.064086 | 0.27008 | 0.16479 | 0.32501 | 0.30212 | 122.7722 | 122.7951 | -0.39825 | -0.35248 | 122.5113 | 122.6578 | 122.5021 | 122.5937
2365.5625 | 122.9782 | -122.644 | 0.20599 | 0.011063 | -0.059336 | 0.010198 | 0.02917 | 0.0065133 | -0.0023605 | 0.0026446 | 0.001648 | 0.013888 | 0.021849 | 0.021734 | -0.00067933 | 0.0048194 | 0.001585 | -0.10529 | 0.15564 | -0.17395 | -0.091553 | 0.10071 | -0.036621 | 0.041199 | 0.032043 | 0.16022 | -0.11902 | 0.054932 | 0.1831 | 0.073242 | 0.19684 | 122.4701 | -0.050354 | -0.29755 | 122.7448 | 122.6852 | 122.6074 | 0.21515 | 0.13733 | 122.525 | -0.045777 | -0.15106 | 122.8271 | 122.8409 | 122.7173 | 0.31586 | 0.19226 | 0.27466 | 0.082397 | 0.30212 | 0.17395 | 0.32959 | 0.27924 | 122.7997 | 122.8043 | -0.37994 | -0.32501 | 122.5525 | 122.699 | 122.5388 | 122.6761
2367.3281 | 122.9553 | -122.6486 | 0.20599 | 0.0034333 | -0.061045 | 0.011267 | 0.028529 | 0.0028817 | -0.0017197 | -0.00013235 | 0.0046998 | 0.012392 | 0.019713 | 0.016607 | 0.00081607 | 0.0041784 | 0.00094419 | -0.1236 | 0.13275 | -0.17395 | -0.1236 | 0.045776 | -0.09613 | 0 | -0.018311 | 0.16022 | -0.10986 | 0.036621 | 0.12817 | 0.027466 | 0.16022 | 122.4747 | -0.073243 | -0.32959 | 122.6944 | 122.6486 | 122.5525 | 0.17395 | 0.07782 | 122.5388 | -0.045777 | -0.16937 | 122.7768 | 122.8088 | 122.6761 | 0.27008 | 0.13733 | 0.21973 | 0.050354 | 0.23804 | 0.14648 | 0.3067 | 0.27008 | 122.7814 | 122.8088 | -0.37994 | -0.31586 | 122.525 | 122.6852 | 122.525 | 122.6303
2369.0312 | 122.8363 | -122.6852 | 0.2243 | 0.0034333 | -0.060404 | 0.015966 | 0.031093 | 0.0026681 | -0.00065149 | 0.0013628 | 0.0046998 | 0.016451 | 0.020568 | 0.014898 | 0.00060247 | 0.0056738 | -0.00076481 | -0.11902 | 0.18768 | -0.20142 | -0.17395 | 0 | -0.16479 | -0.086975 | -0.068665 | 0.20599 | -0.13275 | -0.050354 | 0.027466 | -0.073242 | 0.09613 | 122.4838 | -0.036621 | -0.39825 | 122.6852 | 122.5983 | 122.5204 | 0.11444 | 0.036621 | 122.5525 | -0.01831 | -0.27466 | 122.7127 | 122.7814 | 122.612 | 0.22888 | 0.059509 | 0.20142 | 0.027466 | 0.16022 | 0.082397 | 0.3891 | 0.33875 | 122.8729 | 122.8912 | -0.42572 | -0.35706 | 122.5113 | 122.6349 | 122.5662 | 122.6166
2370.7656 | 122.8775 | -122.6624 | 0.21973 | 0.0034333 | -0.059977 | 0.012548 | 0.030452 | 0.0058725 | -0.0042831 | 8.125e-05 | 0.0046998 | 0.015169 | 0.022704 | 0.02152 | 0.00017507 | 0.0075964 | -0.0014056 | -0.15106 | 0.17395 | -0.21515 | -0.19684 | -0.027466 | -0.1831 | -0.082397 | -0.068665 | 0.20142 | -0.14191 | -0.009155 | 0.045776 | -0.054932 | 0.10071 | 122.4472 | -0.045777 | -0.41657 | 122.6349 | 122.58 | 122.4792 | 0.13275 | 0.032044 | 122.5204 | -0.018311 | -0.22888 | 122.7081 | 122.7631 | 122.6074 | 0.24262 | 0.086975 | 0.18768 | 0.018311 | 0.18768 | 0.13275 | 0.3891 | 0.34332 | 122.8363 | 122.8638 | -0.43488 | -0.36163 | 122.4655 | 122.6532 | 122.5113 | 122.5937
2372.4531 | 122.9279 | -122.6578 | 0.21057 | 0.0034333 | -0.060618 | 0.013616 | 0.029598 | 0.0015999 | -0.0023605 | 0.0022174 | 0.001648 | 0.011965 | 0.021422 | 0.020452 | 0.0014569 | 0.0080236 | -0.0014056 | -0.11902 | 0.15564 | -0.1831 | -0.10986 | 0.07782 | -0.091553 | -0.004578 | -0.018311 | 0.16937 | -0.12817 | 0.041199 | 0.12817 | 0.018311 | 0.15106 | 122.4747 | -0.054931 | -0.32043 | 122.7356 | 122.6532 | 122.5662 | 0.17853 | 0.091552 | 122.5296 | -0.041198 | -0.16937 | 122.7859 | 122.8088 | 122.6761 | 0.27924 | 0.14649 | 0.26092 | 0.073242 | 0.25635 | 0.16937 | 0.33874 | 0.29755 | 122.8134 | 122.8271 | -0.39368 | -0.33875 | 122.5479 | 122.699 | 122.5388 | 122.6395
2374.2031 | 122.905 | -122.6898 | 0.2243 | 0.0034333 | -0.059336 | 0.01148 | 0.029811 | 0.0015999 | -0.0019333 | -0.0012006 | 0.001648 | 0.015383 | 0.021636 | 0.013403 | 0.00038887 | 0.005033 | -0.0024738 | -0.07782 | 0.18768 | -0.20142 | -0.091553 | 0.082397 | -0.073242 | -0.013733 | 0.004578 | 0.19684 | -0.13733 | 0.009155 | 0.10529 | -0.009155 | 0.13275 | 122.4884 | -0.036621 | -0.31586 | 122.7722 | 122.6761 | 122.6166 | 0.18768 | 0.12817 | 122.5525 | -0.027466 | -0.21515 | 122.7951 | 122.8226 | 122.6807 | 0.27008 | 0.12817 | 0.28381 | 0.10986 | 0.24262 | 0.14648 | 0.3891 | 0.33417 | 122.8775 | 122.8867 | -0.42572 | -0.36163 | 122.5983 | 122.699 | 122.612 | 122.6944
2375.9531 | 122.9919 | -122.6349 | 0.21057 | -0.011826 | -0.063395 | 0.012121 | 0.02917 | 0.0043771 | -0.0044967 | 0.00414 | 0.0077514 | 0.01282 | 0.022063 | 0.022802 | -0.0021747 | 0.0056738 | -0.00461 | -0.045776 | 0.14191 | -0.15106 | -0.045776 | 0.19226 | 0.013733 | 0.059509 | 0.082397 | 0.14648 | -0.1236 | 0.091553 | 0.2243 | 0.10071 | 0.20142 | 122.4838 | -0.068664 | -0.25635 | 122.8271 | 122.6944 | 122.6486 | 0.21057 | 0.16479 | 122.5113 | -0.064087 | -0.11902 | 122.8592 | 122.8363 | 122.7356 | 0.32501 | 0.2243 | 0.34332 | 0.10529 | 0.3479 | 0.21515 | 0.29297 | 0.27008 | 122.7768 | 122.7814 | -0.36163 | -0.33417 | 122.5891 | 122.7264 | 122.5891 | 122.7173
2377.6406 | 122.905 | -122.6715 | 0.25177 | 0.011063 | -0.060618 | 0.012762 | 0.029384 | 0.0026681 | -0.0021469 | 0.00414 | 0.0046998 | 0.016878 | 0.020781 | 0.013616 | -0.00025213 | 0.0039648 | -0.0014056 | -0.086975 | 0.18768 | -0.17853 | -0.12817 | 0.054932 | -0.073242 | -0.032043 | -0.036621 | 0.16937 | -0.14648 | 0.013733 | 0.091553 | -0.004578 | 0.1236 | 122.493 | -0.064087 | -0.37994 | 122.7264 | 122.6395 | 122.5983 | 0.14648 | 0.10529 | 122.525 | -0.082397 | -0.23804 | 122.7631 | 122.7951 | 122.6669 | 0.27008 | 0.14191 | 0.23346 | 0.050354 | 0.23804 | 0.16022 | 0.36621 | 0.31586 | 122.8592 | 122.8409 | -0.4303 | -0.39825 | 122.5433 | 122.6852 | 122.5845 | 122.6349
2379.3906 | 123.0057 | -122.6578 | 0.19226 | 0.011063 | -0.062327 | 0.012762 | 0.028957 | 0.0022409 | -0.0034287 | 0.0032854 | 0.001648 | 0.013033 | 0.021209 | 0.024511 | 0.0023115 | 0.0063148 | -0.00097841 | -0.082397 | 0.13275 | -0.17395 | -0.073242 | 0.10986 | -0.068665 | -0.004578 | 0.064087 | 0.13275 | -0.10071 | 0.10071 | 0.1831 | 0.07782 | 0.21057 | 122.4838 | -0.05951 | -0.2655 | 122.7676 | 122.6532 | 122.5891 | 0.16937 | 0.10528 | 122.5571 | -0.05951 | -0.091553 | 122.8409 | 122.8683 | 122.7356 | 0.31128 | 0.17853 | 0.28381 | 0.10071 | 0.28381 | 0.20142 | 0.3067 | 0.23346 | 122.7905 | 122.7905 | -0.36621 | -0.29297 | 122.5845 | 122.7585 | 122.5754 | 122.7219
2381.1406 | 122.9141 | -122.6624 | 0.23346 | 0.0034333 | -0.058695 | 0.010626 | 0.028957 | 0.0037363 | -0.0049241 | 0.0013628 | 0.001648 | 0.015597 | 0.022277 | 0.012335 | -0.0021747 | 0.0058874 | -0.0020464 | -0.11444 | 0.19226 | -0.19684 | -0.14191 | 0.013733 | -0.086975 | -0.032043 | -0.064087 | 0.17395 | -0.16479 | -0.004578 | 0.10071 | -0.013733 | 0.14191 | 122.4655 | -0.041198 | -0.37537 | 122.6761 | 122.6303 | 122.5754 | 0.1648 | 0.10986 | 122.4976 | -0.059509 | -0.23804 | 122.7631 | 122.8043 | 122.6486 | 0.3067 | 0.15106 | 0.21057 | 0.054931 | 0.2655 | 0.16022 | 0.3891 | 0.33874 | 122.8546 | 122.8363 | -0.4303 | -0.39825 | 122.5204 | 122.6578 | 122.5479 | 122.5983
2382.8281 | 122.9233 | -122.6807 | 0.22888 | 0.011063 | -0.062327 | 0.012975 | 0.030666 | 0.00074554 | -0.0027877 | 0.00414 | -0.0014038 | 0.015597 | 0.019927 | 0.017462 | -0.00089293 | 0.0039648 | 0.0011578 | -0.086975 | 0.20599 | -0.18768 | -0.1236 | 0.041199 | -0.086975 | -0.027466 | -0.041199 | 0.20142 | -0.13275 | 0.009155 | 0.09613 | 0.009155 | 0.14191 | 122.493 | -0.022888 | -0.35248 | 122.7219 | 122.6532 | 122.5937 | 0.16022 | 0.10071 | 122.5479 | -0.027466 | -0.21973 | 122.7768 | 122.8226 | 122.6898 | 0.27466 | 0.14191 | 0.22888 | 0.064087 | 0.22888 | 0.14191 | 0.39368 | 0.33417 | 122.8867 | 122.8821 | -0.41656 | -0.36163 | 122.5571 | 122.6898 | 122.5937 | 122.6395
2384.5781 | 122.9507 | -122.6669 | 0.20142 | -0.0041962 | -0.062754 | 0.012975 | 0.028743 | 0.0052315 | -0.0038559 | 0.00029485 | 0.0046998 | 0.012606 | 0.021209 | 0.024938 | -0.00089293 | 0.0075964 | 0.0013714 | -0.12817 | 0.16022 | -0.16937 | -0.1236 | 0.073242 | -0.09613 | 0.004578 | -0.027466 | 0.15564 | -0.12817 | 0.036621 | 0.14648 | 0.045776 | 0.16937 | 122.4976 | -0.041199 | -0.32501 | 122.7402 | 122.6715 | 122.5708 | 0.17395 | 0.073243 | 122.5388 | -0.045776 | -0.1648 | 122.8134 | 122.8363 | 122.7127 | 0.29755 | 0.17395 | 0.24261 | 0.045777 | 0.27466 | 0.1648 | 0.32959 | 0.28381 | 122.8271 | 122.8226 | -0.37079 | -0.32959 | 122.5433 | 122.7036 | 122.5388 | 122.6395
2386.3438 | 122.8683 | -122.7081 | 0.2243 | 0.0034333 | -0.061472 | 0.010198 | 0.030025 | 0.0039499 | -0.0057785 | -0.0014142 | 0.001648 | 0.013888 | 0.023986 | 0.009771 | -0.0040973 | 0.0048194 | 0.00094419 | -0.11902 | 0.20599 | -0.1831 | -0.15106 | 0.022888 | -0.10071 | -0.036621 | -0.082397 | 0.18768 | -0.15106 | -0.032043 | 0.064087 | -0.054932 | 0.10986 | 122.525 | -0.01831 | -0.37537 | 122.731 | 122.6715 | 122.6074 | 0.14648 | 0.082397 | 122.5571 | -0.036621 | -0.25635 | 122.7722 | 122.818 | 122.6532 | 0.26093 | 0.09613 | 0.20599 | 0.032043 | 0.21515 | 0.11902 | 0.3891 | 0.33874 | 122.9141 | 122.8958 | -0.40741 | -0.37537 | 122.5571 | 122.6761 | 122.5891 | 122.6257
2388.0312 | 122.9187 | -122.6852 | 0.21515 | 0.0034333 | -0.06019 | 0.012548 | 0.028529 | 0.0028817 | -0.0015061 | 0.0015764 | 0.001648 | 0.01346 | 0.021636 | 0.023016 | 0.0033795 | 0.0069556 | -0.00055121 | -0.14191 | 0.16937 | -0.20142 | -0.17853 | -0.004578 | -0.1831 | -0.07782 | -0.041199 | 0.16937 | -0.14648 | 0.018311 | 0.091553 | -0.022888 | 0.14648 | 122.4838 | -0.045776 | -0.39368 | 122.6807 | 122.6074 | 122.5021 | 0.1236 | 0.018311 | 122.5388 | -0.045776 | -0.19684 | 122.7768 | 122.8317 | 122.6624 | 0.29297 | 0.1236 | 0.19684 | 0.022888 | 0.23804 | 0.16479 | 0.37079 | 0.31586 | 122.8546 | 122.8546 | -0.41657 | -0.36163 | 122.5067 | 122.7036 | 122.5433 | 122.644
2389.7812 | 123.0331 | -122.6761 | 0.18768 | -0.0041962 | -0.05955 | 0.010198 | 0.027675 | -0.00096346 | -0.0038559 | -0.0039778 | -0.0014038 | 0.014101 | 0.021849 | 0.023657 | -0.0013201 | 0.005033 | 0.0011578 | -0.064087 | 0.15106 | -0.15564 | -0.041199 | 0.18768 | 0.009155 | 0.082397 | 0.09613 | 0.13733 | -0.10986 | 0.091553 | 0.20142 | 0.10529 | 0.19226 | 122.5204 | -0.036621 | -0.22888 | 122.8638 | 122.7585 | 122.6852 | 0.23804 | 0.16479 | 122.5662 | -0.050354 | -0.09613 | 122.8775 | 122.8683 | 122.7814 | 0.30212 | 0.21515 | 0.34332 | 0.11444 | 0.31128 | 0.20142 | 0.3067 | 0.24719 | 122.8271 | 122.8134 | -0.34332 | -0.29755 | 122.6349 | 122.7676 | 122.612 | 122.7722
2391.5312 | 122.9691 | -122.6715 | 0.21057 | 0.0034333 | -0.05955 | 0.013189 | 0.031307 | 0.0058725 | -0.0047103 | 0.002431 | 0.0046998 | 0.014956 | 0.021636 | 0.029852 | 0.00081607 | 0.0075964 | -0.00012381 | -0.091553 | 0.12817 | -0.1831 | -0.091553 | 0.11902 | -0.082397 | -0.013733 | 0.032043 | 0.15564 | -0.11902 | 0.059509 | 0.12817 | 0.041199 | 0.17853 | 122.4884 | -0.082397 | -0.30212 | 122.7905 | 122.6578 | 122.5891 | 0.16937 | 0.10071 | 122.5525 | -0.054931 | -0.15106 | 122.7997 | 122.85 | 122.7127 | 0.29755 | 0.16022 | 0.30212 | 0.091552 | 0.24719 | 0.17853 | 0.31128 | 0.27466 | 122.7997 | 122.8271 | -0.39368 | -0.32959 | 122.58 | 122.731 | 122.58 | 122.7036
2393.2812 | 122.9324 | -122.6852 | 0.23804 | 0.0034333 | -0.06019 | 0.01383 | 0.031307 | 0.00053194 | -0.0030015 | 0.0013628 | 0.001648 | 0.016665 | 0.020781 | 0.018102 | 0.0018841 | 0.006101 | -0.0020464 | -0.14191 | 0.16937 | -0.21973 | -0.19226 | -0.009155 | -0.16022 | -0.091553 | -0.054932 | 0.1831 | -0.16022 | -0.009155 | 0.068665 | -0.045776 | 0.1236 | 122.4655 | -0.068664 | -0.4303 | 122.6761 | 122.5937 | 122.525 | 0.12817 | 0.05951 | 122.525 | -0.054932 | -0.24719 | 122.7539 | 122.8088 | 122.6395 | 0.28381 | 0.11444 | 0.21057 | 0.027466 | 0.22888 | 0.15106 | 0.3891 | 0.34332 | 122.8546 | 122.8683 | -0.45776 | -0.39825 | 122.493 | 122.6761 | 122.5433 | 122.6303
2395.0312 | 122.9645 | -122.7081 | 0.21057 | -0.0041962 | -0.061899 | 0.011907 | 0.031093 | 0.0077951 | -0.0012925 | -0.0029096 | -0.0014038 | 0.012179 | 0.023558 | 0.020452 | 0.0029523 | 0.0046058 | 8.9786e-05 | -0.14191 | 0.16022 | -0.21973 | -0.16937 | 0 | -0.15564 | -0.082397 | -0.009155 | 0.17395 | -0.12817 | 0.032043 | 0.10986 | 0.004578 | 0.16022 | 122.4884 | -0.050354 | -0.37994 | 122.7081 | 122.6257 | 122.5525 | 0.13733 | 0.064087 | 122.58 | -0.036621 | -0.17853 | 122.818 | 122.8683 | 122.7127 | 0.28839 | 0.13275 | 0.21973 | 0.050354 | 0.23804 | 0.16022 | 0.37994 | 0.30212 | 122.8683 | 122.8821 | -0.4303 | -0.33875 | 122.5388 | 122.7402 | 122.5662 | 122.699
2396.7188 | 122.8958 | -122.731 | 0.23804 | -0.0041962 | -0.059122 | 0.011053 | 0.029384 | 0.0082223 | -0.0042831 | 0.0028582 | 0.001648 | 0.01346 | 0.020568 | 0.015966 | -0.0045245 | 0.0041784 | 0.00051699 | -0.11444 | 0.17853 | -0.16937 | -0.15564 | 0.054932 | -0.09613 | -0.027466 | -0.07782 | 0.20599 | -0.14648 | -0.041199 | 0.064087 | -0.032043 | 0.10071 | 122.5616 | -0.059509 | -0.39368 | 122.7859 | 122.7036 | 122.6349 | 0.14191 | 0.073243 | 122.5845 | -0.032043 | -0.27924 | 122.7951 | 122.8317 | 122.699 | 0.24719 | 0.11444 | 0.22431 | 0.013733 | 0.21057 | 0.10529 | 0.3479 | 0.35248 | 122.9095 | 122.937 | -0.40741 | -0.38452 | 122.5754 | 122.6898 | 122.6166 | 122.6532
2398.4844 | 122.9645 | -122.6578 | 0.22888 | 0.011063 | -0.057627 | 0.0097712 | 0.027675 | 0.0041635 | -0.0023605 | 0.0011492 | 0.0046998 | 0.012606 | 0.021209 | 0.017675 | -0.0032427 | 0.0058874 | -0.00076481 | -0.041199 | 0.15564 | -0.15106 | -0.050354 | 0.14191 | 0 | 0.054932 | 0.045776 | 0.16022 | -0.13275 | 0.036621 | 0.17395 | 0.050354 | 0.16479 | 122.5067 | -0.073242 | -0.27924 | 122.7997 | 122.7127 | 122.6578 | 0.20599 | 0.15106 | 122.525 | -0.068665 | -0.19226 | 122.8317 | 122.8226 | 122.7081 | 0.29755 | 0.18311 | 0.29297 | 0.10071 | 0.3067 | 0.16937 | 0.3067 | 0.29297 | 122.8134 | 122.818 | -0.37994 | -0.36163 | 122.6074 | 122.6944 | 122.6166 | 122.7036
2400.2344 | 123.0103 | -122.6486 | 0.19684 | -0.0041962 | -0.06019 | 0.012335 | 0.028316 | 0.0069405 | -0.0038559 | -0.0012006 | 0.001648 | 0.015169 | 0.020781 | 0.016393 | 0.0029523 | 0.0075964 | -0.001192 | -0.054932 | 0.13275 | -0.17395 | -0.068665 | 0.11444 | -0.064087 | 0.022888 | 0.086975 | 0.15564 | -0.10986 | 0.10529 | 0.19226 | 0.082397 | 0.19684 | 122.4747 | -0.064087 | -0.2655 | 122.7631 | 122.6715 | 122.5845 | 0.19684 | 0.10986 | 122.5388 | -0.041198 | -0.091552 | 122.8409 | 122.8455 | 122.731 | 0.3067 | 0.19226 | 0.28839 | 0.10528 | 0.30212 | 0.21515 | 0.3067 | 0.2655 | 122.7814 | 122.8043 | -0.37079 | -0.3067 | 122.58 | 122.7539 | 122.5937 | 122.7356
2401.9844 | 122.9553 | -122.7036 | 0.2243 | 0.0034333 | -0.056345 | 0.011267 | 0.030452 | 0.0048043 | -0.0032151 | -0.00055975 | -0.0014038 | 0.01581 | 0.020781 | 0.01917 | -3.8532e-05 | 0.0058874 | 0.00030339 | -0.07782 | 0.21515 | -0.1831 | -0.10986 | 0.07782 | -0.07782 | -0.004578 | -0.004578 | 0.18768 | -0.13733 | 0.027466 | 0.11444 | -0.009155 | 0.13733 | 122.5204 | -0.009155 | -0.33417 | 122.7814 | 122.699 | 122.6257 | 0.17853 | 0.10528 | 122.5662 | -0.036621 | -0.19684 | 122.818 | 122.8409 | 122.6944 | 0.27466 | 0.12817 | 0.26092 | 0.073242 | 0.25177 | 0.16479 | 0.39825 | 0.32501 | 122.9187 | 122.8912 | -0.40741 | -0.36163 | 122.5937 | 122.731 | 122.6257 | 122.699
2403.6875 | 122.9279 | -122.7264 | 0.21973 | 0.011063 | -0.058695 | 0.012121 | 0.02917 | 0.0013863 | -0.0059921 | 0.0017902 | 0.0077514 | 0.014956 | 0.023986 | 0.010198 | -0.0028155 | 0.006742 | 0.0011578 | -0.11902 | 0.21515 | -0.1831 | -0.15564 | 0.013733 | -0.10986 | -0.041199 | -0.086975 | 0.19684 | -0.15106 | -0.050354 | 0.07782 | -0.027466 | 0.10986 | 122.5433 | -0.004578 | -0.37537 | 122.7402 | 122.6852 | 122.6166 | 0.14191 | 0.073242 | 122.5754 | -0.022889 | -0.27008 | 122.8043 | 122.8363 | 122.699 | 0.26093 | 0.1236 | 0.19684 | 0.027465 | 0.22888 | 0.10071 | 0.39825 | 0.3479 | 122.9416 | 122.9233 | -0.40283 | -0.37079 | 122.5708 | 122.6761 | 122.6074 | 122.6395
2405.4375 | 123.0057 | -122.6852 | 0.19226 | -0.0041962 | -0.060831 | 0.012335 | 0.030025 | 0.0073679 | -0.0021469 | 0.0026446 | 0.010803 | 0.013888 | 0.023345 | 0.015112 | 0.0042341 | 0.0056738 | -0.00076481 | -0.068665 | 0.13275 | -0.17853 | -0.064087 | 0.12817 | -0.045776 | 0.018311 | 0.073242 | 0.15106 | -0.10529 | 0.10071 | 0.17853 | 0.064087 | 0.19684 | 122.5067 | -0.05951 | -0.25635 | 122.8134 | 122.7036 | 122.6395 | 0.19684 | 0.13275 | 122.58 | -0.041199 | -0.091553 | 122.8638 | 122.8821 | 122.7493 | 0.30212 | 0.16937 | 0.3067 | 0.11444 | 0.28381 | 0.20599 | 0.31128 | 0.25635 | 122.818 | 122.8363 | -0.37079 | -0.29755 | 122.6212 | 122.7859 | 122.6166 | 122.7585
2407.125 | 123.0286 | -122.6944 | 0.19226 | 0.0034333 | -0.06254 | 0.012335 | 0.02618 | 0.0026681 | -0.0019333 | 0.0022174 | 0.001648 | 0.013674 | 0.020995 | 0.020025 | -0.00089293 | 0.0071692 | 0.0030804 | -0.11444 | 0.17395 | -0.16937 | -0.09613 | 0.10071 | -0.036621 | 0.041199 | 0.018311 | 0.15106 | -0.1236 | 0.054932 | 0.17853 | 0.068665 | 0.21057 | 122.525 | -0.018311 | -0.28839 | 122.7951 | 122.7356 | 122.6578 | 0.21057 | 0.13275 | 122.5708 | -0.041199 | -0.13733 | 122.8729 | 122.905 | 122.7631 | 0.33417 | 0.19226 | 0.27008 | 0.073243 | 0.30212 | 0.17853 | 0.34332 | 0.27466 | 122.8683 | 122.8455 | -0.36163 | -0.31586 | 122.5983 | 122.7493 | 122.58 | 122.7127
2408.875 | 122.9416 | -122.7081 | 0.23346 | 0.018692 | -0.058054 | 0.014471 | 0.02917 | 0.0071541 | -0.0021469 | 0.0011492 | 0.001648 | 0.013888 | 0.022277 | 0.014257 | 0.00060247 | 0.005033 | -0.0016192 | -0.086975 | 0.20142 | -0.19226 | -0.12817 | 0.064087 | -0.073242 | -0.018311 | -0.009155 | 0.18768 | -0.14191 | 0.027466 | 0.11444 | -0.004578 | 0.15106 | 122.5159 | -0.032043 | -0.36163 | 122.7722 | 122.6898 | 122.6349 | 0.17395 | 0.11902 | 122.5662 | -0.045776 | -0.20599 | 122.8226 | 122.8592 | 122.7036 | 0.29297 | 0.13733 | 0.25635 | 0.064087 | 0.25635 | 0.16937 | 0.39368 | 0.32959 | 122.9095 | 122.8958 | -0.42572 | -0.37537 | 122.58 | 122.7356 | 122.6212 | 122.699
2410.5625 | 122.9187 | -122.731 | 0.23346 | -0.0041962 | -0.059977 | 0.011267 | 0.029598 | 0.0028817 | -0.0040695 | -0.00055975 | 0.0046998 | 0.013888 | 0.019286 | 0.0054986 | -0.0026019 | 0.0041784 | -0.0016192 | -0.10986 | 0.18768 | -0.16937 | -0.13733 | 0.036621 | -0.086975 | -0.022888 | -0.07782 | 0.19226 | -0.16022 | -0.045776 | 0.059509 | -0.032043 | 0.086975 | 122.5616 | -0.045776 | -0.37079 | 122.7676 | 122.7081 | 122.644 | 0.14649 | 0.082398 | 122.5708 | -0.041198 | -0.27924 | 122.7905 | 122.818 | 122.699 | 0.24719 | 0.12817 | 0.20599 | 0.032044 | 0.21973 | 0.11444 | 0.35706 | 0.35248 | 122.9187 | 122.9233 | -0.40283 | -0.39368 | 122.5937 | 122.6852 | 122.6212 | 122.6532
2412.2969 | 122.8867 | -122.7173 | 0.21515 | 0.018692 | -0.058268 | 0.010839 | 0.030452 | 0.0030953 | -0.00022429 | 0.0043536 | 0.001648 | 0.015169 | 0.023131 | 0.01148 | 0.0012433 | 0.005033 | -0.00076481 | -0.11902 | 0.17395 | -0.20599 | -0.19226 | -0.009155 | -0.15564 | -0.086975 | -0.10071 | 0.20142 | -0.15564 | -0.022888 | 0.036621 | -0.086975 | 0.091553 | 122.5113 | -0.041199 | -0.40741 | 122.7081 | 122.6303 | 122.5616 | 0.11902 | 0.050354 | 122.5616 | -0.013733 | -0.23804 | 122.7539 | 122.8088 | 122.6303 | 0.24719 | 0.068665 | 0.19684 | 0.013733 | 0.19226 | 0.13275 | 0.37994 | 0.35706 | 122.8912 | 122.9187 | -0.42114 | -0.37079 | 122.525 | 122.6944 | 122.5983 | 122.6166
2414.0469 | 122.9416 | -122.7173 | 0.22888 | 0.0034333 | -0.059336 | 0.012548 | 0.029384 | 0.0060861 | -0.0057785 | 0.0022174 | 0.001648 | 0.013674 | 0.021849 | 0.010839 | 0.0010297 | 0.0041784 | -0.00076481 | -0.07782 | 0.17395 | -0.16937 | -0.10529 | 0.091553 | -0.086975 | -0.032043 | 0.013733 | 0.1831 | -0.13275 | 0.013733 | 0.10529 | -0.004578 | 0.12817 | 122.5479 | -0.054932 | -0.33417 | 122.8088 | 122.6852 | 122.6303 | 0.13733 | 0.082398 | 122.5845 | -0.045777 | -0.21515 | 122.8226 | 122.8455 | 122.7127 | 0.26093 | 0.12817 | 0.26093 | 0.064087 | 0.23804 | 0.14648 | 0.34332 | 0.31586 | 122.8912 | 122.9004 | -0.39826 | -0.36163 | 122.612 | 122.731 | 122.6395 | 122.731
2415.7344 | 122.9279 | -122.7127 | 0.21973 | 0.018692 | -0.058909 | 0.011267 | 0.030238 | 0.0045907 | -0.0034287 | 0.00029485 | -0.0014038 | 0.014315 | 0.020781 | 0.014684 | 0.0029523 | 0.0048194 | -0.00033761 | -0.07782 | 0.1831 | -0.1831 | -0.13733 | 0.054932 | -0.10071 | -0.036621 | -0.013733 | 0.17853 | -0.13733 | 0.018311 | 0.07782 | -0.036621 | 0.12817 | 122.5296 | -0.036622 | -0.35706 | 122.7676 | 122.6761 | 122.612 | 0.14648 | 0.082397 | 122.5754 | -0.041199 | -0.20142 | 122.7905 | 122.8409 | 122.6761 | 0.2655 | 0.10071 | 0.23804 | 0.045776 | 0.21515 | 0.15564 | 0.36621 | 0.31586 | 122.8958 | 122.8912 | -0.40283 | -0.35706 | 122.5754 | 122.731 | 122.6349 | 122.699
2417.4844 | 123.0057 | -122.7036 | 0.21057 | -0.011826 | -0.062754 | 0.011694 | 0.029811 | -0.0028861 | -0.0036423 | -0.00055975 | 0.0077514 | 0.011324 | 0.018859 | 0.017248 | 0.0020979 | 0.0099462 | 0.0013714 | -0.12817 | 0.14648 | -0.17853 | -0.11444 | 0.073242 | -0.082397 | 0.004578 | -0.018311 | 0.14191 | -0.12817 | 0.032043 | 0.14191 | 0.013733 | 0.15564 | 122.525 | -0.064087 | -0.32501 | 122.7768 | 122.7081 | 122.6212 | 0.18311 | 0.096131 | 122.5754 | -0.068664 | -0.17853 | 122.8455 | 122.8592 | 122.7173 | 0.28381 | 0.14191 | 0.25177 | 0.064087 | 0.27008 | 0.16022 | 0.32501 | 0.27008 | 122.85 | 122.8455 | -0.3891 | -0.33875 | 122.5891 | 122.7356 | 122.5754 | 122.6852
2419.2656 | 123.0103 | -122.7036 | 0.20599 | 0.0034333 | -0.061045 | 0.012762 | 0.028102 | 0.0039499 | -0.0019333 | -0.00013235 | 0.0046998 | 0.013033 | 0.019927 | 0.017248 | 0.0012433 | 0.0056738 | -0.002901 | -0.13275 | 0.13733 | -0.17853 | -0.10986 | 0.064087 | -0.073242 | 0.009155 | -0.013733 | 0.15564 | -0.12817 | 0.027466 | 0.14648 | 0.041199 | 0.16937 | 122.525 | -0.068665 | -0.31586 | 122.7676 | 122.7127 | 122.6303 | 0.18768 | 0.10529 | 122.5754 | -0.050354 | -0.17853 | 122.85 | 122.8729 | 122.7448 | 0.29755 | 0.16937 | 0.24261 | 0.068665 | 0.27466 | 0.15564 | 0.31586 | 0.28381 | 122.8409 | 122.8592 | -0.38452 | -0.33417 | 122.5937 | 122.731 | 122.5708 | 122.6898
2420.9531 | 123.0469 | -122.6944 | 0.19226 | 0.0034333 | -0.058909 | 0.013189 | 0.03152 | 0.00095914 | -0.0036423 | 0.0011492 | -0.0014038 | 0.014742 | 0.020995 | 0.015112 | 0.0035931 | 0.00781 | -0.0031146 | -0.082397 | 0.1236 | -0.1831 | -0.07782 | 0.10529 | -0.064087 | 0.013733 | 0.068665 | 0.14191 | -0.10986 | 0.10071 | 0.18768 | 0.068665 | 0.21515 | 122.5113 | -0.068665 | -0.27008 | 122.7997 | 122.7081 | 122.6303 | 0.19684 | 0.11902 | 122.5845 | -0.050354 | -0.091553 | 122.8821 | 122.9095 | 122.7631 | 0.32501 | 0.17853 | 0.28839 | 0.10528 | 0.29755 | 0.21057 | 0.3067 | 0.25177 | 122.818 | 122.8363 | -0.37537 | -0.30212 | 122.6166 | 122.7951 | 122.612 | 122.7631
2422.7031 | 123.0377 | -122.7036 | 0.21515 | 0.0034333 | -0.060404 | 0.011053 | 0.030025 | 0.00095914 | -0.0049241 | -0.00034615 | 0.001648 | 0.013888 | 0.020568 | 0.01917 | -0.0019611 | 0.005033 | -0.00033761 | -0.054932 | 0.15106 | -0.15106 | -0.032043 | 0.1831 | 0.013733 | 0.073242 | 0.07782 | 0.16022 | -0.11902 | 0.091553 | 0.20142 | 0.09613 | 0.19684 | 122.5525 | -0.064087 | -0.24719 | 122.8867 | 122.7768 | 122.7173 | 0.2243 | 0.16479 | 122.5845 | -0.054932 | -0.1236 | 122.905 | 122.9004 | 122.7997 | 0.31586 | 0.21515 | 0.33417 | 0.11902 | 0.32044 | 0.21057 | 0.30212 | 0.27924 | 122.8546 | 122.8638 | -0.36621 | -0.33417 | 122.6715 | 122.7951 | 122.6486 | 122.7814
2424.4062 | 122.9599 | -122.7173 | 0.21057 | 0.0034333 | -0.06019 | 0.012121 | 0.029811 | 0.0030953 | -0.0034287 | 0.00093565 | 0.0046998 | 0.014956 | 0.022063 | 0.014257 | -0.00067933 | 0.0046058 | -0.0016192 | -0.07782 | 0.18768 | -0.17395 | -0.10986 | 0.07782 | -0.073242 | -0.013733 | -0.009155 | 0.1831 | -0.1236 | 0.018311 | 0.11902 | -0.009155 | 0.15564 | 122.5433 | -0.022888 | -0.32043 | 122.7951 | 122.7036 | 122.644 | 0.16022 | 0.10071 | 122.5937 | -0.027466 | -0.19226 | 122.8363 | 122.8729 | 122.7081 | 0.27924 | 0.11444 | 0.25177 | 0.064087 | 0.24261 | 0.14191 | 0.36163 | 0.3067 | 122.905 | 122.9004 | -0.38452 | -0.33417 | 122.6074 | 122.7356 | 122.6395 | 122.7081
2426.1719 | 122.937 | -122.7493 | 0.2243 | 0.0034333 | -0.060831 | 0.013189 | 0.028102 | 0.00053194 | -0.0064193 | 0.0030718 | -0.0014038 | 0.015383 | 0.021636 | 0.017675 | -0.0047381 | 0.0054602 | 0.0013714 | -0.082397 | 0.16937 | -0.16479 | -0.11902 | 0.073242 | -0.054932 | -0.009155 | -0.068665 | 0.19684 | -0.17395 | -0.027466 | 0.073242 | -0.032043 | 0.082397 | 122.5845 | -0.054931 | -0.34332 | 122.8226 | 122.7402 | 122.6944 | 0.15564 | 0.10986 | 122.5754 | -0.027466 | -0.25177 | 122.8226 | 122.8317 | 122.7173 | 0.25635 | 0.14191 | 0.23804 | 0.045776 | 0.24719 | 0.14648 | 0.33417 | 0.37079 | 122.9187 | 122.9462 | -0.3891 | -0.39825 | 122.6303 | 122.7219 | 122.6669 | 122.6807
2427.875 | 122.9645 | -122.7448 | 0.2243 | 0.0034333 | -0.058268 | 0.012762 | 0.032588 | 0.0028817 | -0.0025741 | -0.0033368 | -0.0014038 | 0.014956 | 0.019286 | 0.016607 | 0.0010297 | 0.0039648 | 0.0011578 | -0.073242 | 0.16479 | -0.17395 | -0.12817 | 0.086975 | -0.073242 | -0.018311 | 0.009155 | 0.16937 | -0.14648 | 0.027466 | 0.10986 | 0.013733 | 0.13275 | 122.5708 | -0.059509 | -0.35248 | 122.8317 | 122.7264 | 122.6715 | 0.15564 | 0.10071 | 122.5983 | -0.054931 | -0.19684 | 122.8546 | 122.8775 | 122.7585 | 0.27924 | 0.16022 | 0.26092 | 0.045776 | 0.25635 | 0.17395 | 0.33874 | 0.31586 | 122.9095 | 122.9141 | -0.39825 | -0.37079 | 122.6166 | 122.7722 | 122.6715 | 122.7539
2429.6406 | 122.9782 | -122.7264 | 0.23346 | -0.0041962 | -0.058481 | 0.0095576 | 0.030452 | 0.0037363 | -0.0059921 | 0.00029485 | 0.001648 | 0.014742 | 0.021422 | 0.015325 | -0.0017475 | 0.0048194 | 0.00030339 | -0.086975 | 0.20599 | -0.16937 | -0.14191 | 0.045776 | -0.07782 | -0.004578 | -0.013733 | 0.1831 | -0.13275 | 0.022888 | 0.11902 | -0.009155 | 0.14191 | 122.5571 | -0.027465 | -0.37537 | 122.7722 | 122.7219 | 122.6486 | 0.16479 | 0.091553 | 122.5937 | -0.050354 | -0.21057 | 122.8455 | 122.8683 | 122.7173 | 0.27466 | 0.1236 | 0.21515 | 0.027466 | 0.25177 | 0.15564 | 0.37537 | 0.31586 | 122.9324 | 122.9095 | -0.40283 | -0.36621 | 122.5845 | 122.7493 | 122.6395 | 122.7127
2431.4062 | 123.0057 | -122.7173 | 0.20142 | 0.011063 | -0.058268 | 0.012335 | 0.029384 | 0.0052315 | -0.0030015 | 0.00072205 | 0.0046998 | 0.014101 | 0.022917 | 0.021093 | -3.8532e-05 | 0.0069556 | 0.0017988 | -0.10986 | 0.13733 | -0.16479 | -0.12817 | 0.082397 | -0.086975 | 0 | -0.004578 | 0.15106 | -0.12817 | 0.041199 | 0.15106 | 0.027466 | 0.16937 | 122.5525 | -0.064087 | -0.32959 | 122.7997 | 122.7173 | 122.6303 | 0.16479 | 0.07782 | 122.5891 | -0.050354 | -0.16022 | 122.8683 | 122.8867 | 122.7448 | 0.29755 | 0.15564 | 0.24719 | 0.036621 | 0.27924 | 0.16937 | 0.30212 | 0.27924 | 122.8546 | 122.8683 | -0.36621 | -0.32959 | 122.5891 | 122.7585 | 122.6074 | 122.7127
2433.1562 | 122.9874 | -122.7264 | 0.20599 | 0.011063 | -0.055704 | 0.014471 | 0.030238 | 0.0082223 | -0.0036423 | 0.0011492 | -0.0014038 | 0.014101 | 0.021849 | 0.014898 | -0.00089293 | 0.0041784 | -0.00055121 | -0.059509 | 0.17395 | -0.17853 | -0.11902 | 0.073242 | -0.086975 | -0.022888 | 0.009155 | 0.17853 | -0.14191 | 0.036621 | 0.11902 | 0.009155 | 0.16479 | 122.5479 | -0.032044 | -0.32501 | 122.7997 | 122.7036 | 122.6395 | 0.15564 | 0.091553 | 122.5845 | -0.027466 | -0.16937 | 122.8455 | 122.8912 | 122.7356 | 0.3067 | 0.15106 | 0.25177 | 0.059509 | 0.26093 | 0.17853 | 0.35248 | 0.32044 | 122.9004 | 122.905 | -0.38452 | -0.3479 | 122.6074 | 122.7631 | 122.6669 | 122.7356
2434.8594 | 122.9691 | -122.7402 | 0.2243 | -0.0041962 | -0.058481 | 0.013189 | 0.029811 | 0.0052315 | -0.0040695 | 8.125e-05 | 0.0046998 | 0.016237 | 0.02014 | 0.017462 | -0.0015337 | 0.0048194 | -0.00055121 | -0.07782 | 0.18768 | -0.1831 | -0.10986 | 0.086975 | -0.082397 | -0.036621 | 0 | 0.19226 | -0.14648 | 0.018311 | 0.11902 | -0.009155 | 0.13275 | 122.5571 | -0.036621 | -0.33417 | 122.8271 | 122.7036 | 122.6578 | 0.14648 | 0.10071 | 122.5937 | -0.032043 | -0.20599 | 122.8592 | 122.8729 | 122.731 | 0.27924 | 0.13733 | 0.27008 | 0.073242 | 0.2655 | 0.16479 | 0.37079 | 0.33874 | 122.9279 | 122.9324 | -0.40741 | -0.37079 | 122.6303 | 122.7585 | 122.6624 | 122.7402
2436.625 | 122.9324 | -122.7493 | 0.22888 | 0.0034333 | -0.058054 | 0.0093438 | 0.029384 | 0.0050179 | -0.0030015 | 0.0015764 | 0.001648 | 0.015597 | 0.0195 | 0.010839 | -0.0019611 | 0.0028968 | -0.0022602 | -0.11902 | 0.21515 | -0.16479 | -0.14648 | 0.045776 | -0.10529 | -0.027466 | -0.10529 | 0.1831 | -0.16022 | -0.045776 | 0.059509 | -0.041199 | 0.10529 | 122.5845 | -0.013733 | -0.37537 | 122.7951 | 122.7219 | 122.644 | 0.13733 | 0.059509 | 122.5891 | -0.045777 | -0.27466 | 122.8088 | 122.8546 | 122.7081 | 0.2655 | 0.11902 | 0.21057 | 0.018311 | 0.21973 | 0.11444 | 0.37994 | 0.34332 | 122.9645 | 122.9324 | -0.39368 | -0.3891 | 122.6028 | 122.7036 | 122.6303 | 122.644
2438.3125 | 122.9736 | -122.7631 | 0.23804 | 0.0034333 | -0.060404 | 0.011267 | 0.028316 | 0.0043771 | -0.0038559 | -0.00055975 | -0.0014038 | 0.013033 | 0.020781 | 0.022375 | -0.0038837 | 0.005033 | -0.0014056 | -0.050354 | 0.13733 | -0.15564 | -0.091553 | 0.13733 | -0.013733 | 0.041199 | 0 | 0.15564 | -0.1236 | -0.004578 | 0.11444 | 0.004578 | 0.12817 | 122.6074 | -0.10071 | -0.32959 | 122.9004 | 122.8043 | 122.7493 | 0.19684 | 0.14191 | 122.6395 | -0.082397 | -0.24261 | 122.8775 | 122.8912 | 122.7676 | 0.25177 | 0.12817 | 0.29297 | 0.064087 | 0.23804 | 0.11902 | 0.29297 | 0.27924 | 122.9004 | 122.9187 | -0.39368 | -0.36163 | 122.6715 | 122.7585 | 122.7127 | 122.7631
2440.0625 | 122.937 | -122.7493 | 0.23804 | 0.0034333 | -0.059763 | 0.0091302 | 0.031093 | 0.0043771 | -0.0074875 | 0.00029485 | 0.0077514 | 0.016451 | 0.021209 | 0.013616 | 0.0010297 | 0.0041784 | -0.0024738 | -0.11902 | 0.2243 | -0.16022 | -0.16479 | 0.032043 | -0.10529 | -0.036621 | -0.09613 | 0.18768 | -0.16022 | -0.022888 | 0.059509 | -0.032043 | 0.10529 | 122.5891 | -0.013733 | -0.40283 | 122.7814 | 122.7127 | 122.644 | 0.1236 | 0.054931 | 122.5891 | -0.050354 | -0.26093 | 122.8088 | 122.8546 | 122.7173 | 0.2655 | 0.12817 | 0.19226 | -0.004578 | 0.21973 | 0.13733 | 0.38452 | 0.3479 | 122.9736 | 122.937 | -0.39825 | -0.39825 | 122.5845 | 122.7264 | 122.6303 | 122.6532
2441.8125 | 123.0194 | -122.7036 | 0.21057 | -0.0041962 | -0.060618 | 0.010626 | 0.028529 | 0.0077951 | -0.0032151 | 0.00093565 | 0.001648 | 0.012392 | 0.019713 | 0.016393 | -0.00089293 | 0.0054602 | -0.00076481 | -0.11902 | 0.15106 | -0.16479 | -0.1236 | 0.068665 | -0.07782 | 0.009155 | -0.027466 | 0.15564 | -0.14191 | 0.050354 | 0.14191 | 0.022888 | 0.17853 | 122.5388 | -0.059509 | -0.33417 | 122.7722 | 122.7127 | 122.6257 | 0.17395 | 0.086975 | 122.5616 | -0.054931 | -0.16022 | 122.8455 | 122.8821 | 122.7264 | 0.32044 | 0.16479 | 0.23346 | 0.041199 | 0.28381 | 0.19226 | 0.31586 | 0.29755 | 122.8546 | 122.8592 | -0.37537 | -0.35248 | 122.58 | 122.7539 | 122.5845 | 122.6761
2443.5156 | 123.0011 | -122.731 | 0.20599 | 0.0034333 | -0.058909 | 0.014471 | 0.027889 | 0.0022409 | -0.0023605 | 0.0017902 | 0.0046998 | 0.012392 | 0.020568 | 0.020452 | -0.0011065 | 0.0048194 | 0.0024396 | -0.045776 | 0.16937 | -0.13733 | -0.045776 | 0.14648 | 0.013733 | 0.07782 | 0.013733 | 0.16022 | -0.11902 | 0.032043 | 0.1236 | 0.032043 | 0.16479 | 122.5937 | -0.036621 | -0.25177 | 122.8775 | 122.8088 | 122.7448 | 0.21515 | 0.15106 | 122.612 | -0.045777 | -0.17395 | 122.8546 | 122.8958 | 122.7631 | 0.28381 | 0.15106 | 0.28381 | 0.091553 | 0.24261 | 0.15106 | 0.3067 | 0.27924 | 122.9004 | 122.8912 | -0.34332 | -0.32501 | 122.6852 | 122.7631 | 122.6852 | 122.7448
2445.2812 | 123.0743 | -122.7081 | 0.18768 | 0.0034333 | -0.057841 | 0.012335 | 0.030238 | 0.0067269 | -0.0017197 | -0.0016278 | 0.0046998 | 0.015597 | 0.018859 | 0.017248 | 0.0020979 | 0.0058874 | 0.002226 | -0.041199 | 0.12817 | -0.16479 | -0.082397 | 0.11444 | -0.068665 | 0.022888 | 0.073242 | 0.13733 | -0.11902 | 0.11902 | 0.19226 | 0.07782 | 0.21057 | 122.5433 | -0.059509 | -0.27008 | 122.8226 | 122.731 | 122.6395 | 0.18768 | 0.09613 | 122.5891 | -0.050354 | -0.068664 | 122.9004 | 122.9187 | 122.7859 | 0.32959 | 0.19684 | 0.27924 | 0.082398 | 0.31128 | 0.23804 | 0.29297 | 0.25635 | 122.8363 | 122.8455 | -0.35248 | -0.3067 | 122.6257 | 122.8271 | 122.6669 | 122.7814
2447.0469 | 123.024 | -122.7264 | 0.20599 | 0.011063 | -0.058054 | 0.013189 | 0.030452 | 0.0030953 | -0.0023605 | -0.00034615 | 0.0046998 | 0.01346 | 0.019927 | 0.022375 | 0.0012433 | 0.0041784 | 0.0062848 | -0.1236 | 0.14191 | -0.1831 | -0.11444 | 0.073242 | -0.082397 | 0.004578 | -0.022888 | 0.16022 | -0.1236 | 0.045776 | 0.1236 | 0.018311 | 0.15564 | 122.5433 | -0.064087 | -0.32044 | 122.7997 | 122.731 | 122.644 | 0.18768 | 0.10071 | 122.6028 | -0.045777 | -0.16022 | 122.85 | 122.8821 | 122.7448 | 0.27924 | 0.14191 | 0.25635 | 0.068664 | 0.24719 | 0.16937 | 0.32501 | 0.28381 | 122.8683 | 122.8867 | -0.3891 | -0.32959 | 122.612 | 122.7722 | 122.6028 | 122.7036
2448.75 | 123.0469 | -122.7219 | 0.19226 | 0.011063 | -0.058909 | 0.011267 | 0.028102 | 0.0065133 | -0.0051377 | 0.0020038 | -0.0014038 | 0.011751 | 0.020781 | 0.013403 | -0.0017475 | 0.0065284 | 0.00073059 | -0.10986 | 0.13275 | -0.18768 | -0.10986 | 0.07782 | -0.068665 | 0.027466 | 0 | 0.16479 | -0.1236 | 0.041199 | 0.14191 | 0.059509 | 0.17853 | 122.5342 | -0.05951 | -0.30212 | 122.7997 | 122.7493 | 122.6532 | 0.21515 | 0.11902 | 122.5983 | -0.027466 | -0.15106 | 122.8638 | 122.9004 | 122.7814 | 0.30212 | 0.1831 | 0.2655 | 0.07782 | 0.2655 | 0.16479 | 0.32043 | 0.28839 | 122.8546 | 122.8867 | -0.37994 | -0.31586 | 122.612 | 122.7631 | 122.612 | 122.7219
2450.5 | 122.9462 | -122.7539 | 0.2243 | 0.011063 | -0.059122 | 0.011907 | 0.031093 | 0.0069405 | -0.0030015 | 0.0017902 | 0.0077514 | 0.016237 | 0.021636 | 0.017889 | 0.00081607 | 0.0071692 | 0.0026532 | -0.11902 | 0.16022 | -0.21057 | -0.17853 | -0.041199 | -0.1831 | -0.086975 | -0.086975 | 0.19226 | -0.15106 | -0.013733 | 0.041199 | -0.073242 | 0.10986 | 122.5433 | -0.064087 | -0.40283 | 122.7127 | 122.6669 | 122.5708 | 0.1236 | 0.027466 | 122.6028 | -0.032043 | -0.23804 | 122.7951 | 122.8638 | 122.6807 | 0.26093 | 0.07782 | 0.16937 | 0.032043 | 0.19226 | 0.13733 | 0.37079 | 0.34332 | 122.9141 | 122.9462 | -0.43488 | -0.37537 | 122.5754 | 122.7402 | 122.6349 | 122.6669
2452.25 | 122.9599 | -122.7631 | 0.21515 | -0.0041962 | -0.059336 | 0.012548 | 0.031947 | 0.0062997 | -0.0040695 | 0.002431 | 0.001648 | 0.014315 | 0.02249 | 0.010626 | -0.00046573 | 0.0046058 | 0.0011578 | -0.086975 | 0.17853 | -0.16479 | -0.13275 | 0.036621 | -0.11444 | -0.050354 | -0.032043 | 0.17853 | -0.15106 | -0.013733 | 0.050354 | -0.059509 | 0.11902 | 122.5983 | -0.036621 | -0.3479 | 122.7997 | 122.7127 | 122.6486 | 0.11444 | 0.050354 | 122.612 | -0.036621 | -0.22888 | 122.8134 | 122.8821 | 122.7036 | 0.27008 | 0.091553 | 0.20142 | 0.032044 | 0.20142 | 0.13733 | 0.34332 | 0.32959 | 122.9416 | 122.9416 | -0.37994 | -0.36621 | 122.6303 | 122.7493 | 122.6761 | 122.731
2454.0156 | 123.0148 | -122.7219 | 0.20142 | 0.018692 | -0.059977 | 0.014257 | 0.029811 | 0.0028817 | -0.0040695 | 0.0028582 | -0.0014038 | 0.013674 | 0.021849 | 0.017675 | 0.00060247 | 0.006742 | 0.00030339 | -0.10529 | 0.12817 | -0.17395 | -0.10986 | 0.086975 | -0.07782 | 0.022888 | 0.004578 | 0.14648 | -0.12817 | 0.041199 | 0.12817 | 0.027466 | 0.16479 | 122.5479 | -0.073242 | -0.31128 | 122.8088 | 122.7448 | 122.644 | 0.19684 | 0.09613 | 122.5937 | -0.054932 | -0.16022 | 122.85 | 122.8867 | 122.7493 | 0.29297 | 0.15564 | 0.26092 | 0.064087 | 0.25635 | 0.16937 | 0.30212 | 0.27466 | 122.85 | 122.8683 | -0.37537 | -0.32959 | 122.612 | 122.7631 | 122.6166 | 122.7264
2455.7031 | 123.0148 | -122.731 | 0.19684 | -0.011826 | -0.062327 | 0.014684 | 0.02917 | 0.0039499 | -0.00086509 | 0.00072205 | 0.001648 | 0.012606 | 0.021636 | 0.011694 | 0.00081607 | 0.0054602 | 8.9786e-05 | -0.086975 | 0.13733 | -0.16937 | -0.091553 | 0.11444 | -0.073242 | 0.013733 | 0.032043 | 0.14191 | -0.12817 | 0.059509 | 0.14191 | 0.041199 | 0.17395 | 122.5616 | -0.059509 | -0.28839 | 122.8455 | 122.7448 | 122.6578 | 0.18311 | 0.096131 | 122.6028 | -0.054931 | -0.13733 | 122.8729 | 122.905 | 122.7722 | 0.30212 | 0.16937 | 0.28381 | 0.07782 | 0.27008 | 0.18768 | 0.3067 | 0.27008 | 122.8683 | 122.8729 | -0.36621 | -0.32501 | 122.6395 | 122.7905 | 122.644 | 122.7631
2457.4531 | 122.9462 | -122.7768 | 0.21973 | 0.0034333 | -0.05955 | 0.011907 | 0.029384 | 0.0054453 | -0.0042831 | 8.125e-05 | 0.0046998 | 0.013888 | 0.019713 | 0.01148 | -0.0038837 | 0.0056738 | 0.00051699 | -0.07782 | 0.17853 | -0.16937 | -0.12817 | 0.068665 | -0.082397 | -0.022888 | -0.045776 | 0.19684 | -0.14648 | -0.045776 | 0.064087 | -0.045776 | 0.086975 | 122.6074 | -0.041199 | -0.3479 | 122.8455 | 122.7539 | 122.6944 | 0.14649 | 0.086976 | 122.6303 | -0.022889 | -0.2655 | 122.8409 | 122.8638 | 122.731 | 0.23346 | 0.10071 | 0.23804 | 0.041199 | 0.21057 | 0.10071 | 0.3479 | 0.34332 | 122.9553 | 122.9736 | -0.3891 | -0.36621 | 122.6486 | 122.731 | 122.699 | 122.731
2459.2344 | 122.9782 | -122.7676 | 0.22888 | -0.019455 | -0.059763 | 0.011694 | 0.030025 | 0.0045907 | -0.0055649 | -0.00013235 | 0.001648 | 0.013888 | 0.02249 | 0.017034 | -0.0019611 | 0.003324 | 0.00030339 | -0.10529 | 0.19684 | -0.18768 | -0.14648 | 0.027466 | -0.09613 | -0.041199 | -0.086975 | 0.19226 | -0.16479 | -0.013733 | 0.073242 | -0.036621 | 0.10071 | 122.58 | -0.032044 | -0.37537 | 122.7951 | 122.7264 | 122.6715 | 0.14648 | 0.091553 | 122.6028 | -0.036621 | -0.24261 | 122.8409 | 122.8683 | 122.731 | 0.2655 | 0.12817 | 0.21515 | 0.041199 | 0.23804 | 0.15106 | 0.38452 | 0.35706 | 122.9645 | 122.9599 | -0.41656 | -0.39368 | 122.6212 | 122.7539 | 122.6624 | 122.6807
2460.9219 | 123.0377 | -122.7493 | 0.20599 | -0.0041962 | -0.058268 | 0.013403 | 0.027461 | 0.0039499 | -0.0034287 | -0.00013235 | 0.001648 | 0.01282 | 0.020354 | 0.016607 | -0.0015337 | 0.0041784 | 0.00051699 | -0.050354 | 0.16479 | -0.15564 | -0.036621 | 0.15564 | 0.018311 | 0.059509 | 0.041199 | 0.16022 | -0.12817 | 0.041199 | 0.15106 | 0.050354 | 0.16022 | 122.5937 | -0.041199 | -0.24262 | 122.905 | 122.8088 | 122.7676 | 0.21515 | 0.17395 | 122.6212 | -0.045777 | -0.1648 | 122.9004 | 122.9095 | 122.7997 | 0.28839 | 0.17853 | 0.31128 | 0.11902 | 0.27924 | 0.16937 | 0.32044 | 0.28839 | 122.9141 | 122.9095 | -0.36163 | -0.33417 | 122.7127 | 122.7905 | 122.699 | 122.7905

## Thermal Data
Fire Time | A Position - Middle | C Position - 3' | C Position - Middle | C Position - 7'
-0.5271 | 12.7138 | 12.186 | 12.2066 | 12.1332
0.4729 | 12.7071 | 12.1848 | 12.2114 | 12.1324
1.4729 | 12.6282 | 12.1923 | 12.2163 | 12.1333
2.4729 | 12.7377 | 12.1834 | 12.22 | 12.1301
3.4729 | 12.6267 | 12.1896 | 12.2169 | 12.131
4.4729 | 12.7336 | 12.1867 | 12.2252 | 12.1346
5.4729 | 12.7715 | 12.1965 | 12.2284 | 12.1404
6.4729 | 12.6475 | 12.1991 | 12.2343 | 12.1463
7.4729 | 12.7115 | 12.2074 | 12.2406 | 12.1453
8.4729 | 13.1029 | 12.2173 | 12.2596 | 12.1561
9.4729 | 13.4656 | 12.28 | 12.3095 | 12.1573
10.4729 | 17.2731 | 12.3515 | 12.4105 | 12.1762
11.4729 | 24.0907 | 12.6484 | 12.6386 | 12.4285
12.4729 | 30.8708 | 13.2223 | 13.0231 | 12.7121
13.4729 | 40.5472 | 13.8423 | 13.2978 | 13.1979
14.4729 | 47.1629 | 14.684 | 13.9267 | 14.0629
15.4729 | 52.4953 | 15.7879 | 14.8901 | 14.8611
16.4729 | 56.537 | 16.5889 | 16.1999 | 15.5548
17.4729 | 62.016 | 17.8187 | 17.0878 | 16.2512
18.4729 | 65.4405 | 18.6441 | 17.9926 | 17.6522
19.4729 | 70.906 | 19.7085 | 19.0439 | 18.518
20.4885 | 75.0478 | 20.8014 | 20.3043 | 20.0951
21.4885 | 80.1671 | 22.6137 | 21.2824 | 21.8405
22.4729 | 89.3533 | 24.4548 | 22.8356 | 24.1429
23.4729 | 91.9658 | 26.4534 | 24.5636 | 25.5281
24.4729 | 97.208 | 28.4783 | 26.3315 | 26.9187
25.4729 | 104.455 | 30.4069 | 28.4617 | 28.6681
26.4729 | 107.9484 | 33.1135 | 30.8499 | 31.2463
27.4729 | 113.5725 | 35.1715 | 32.7684 | 33.4937
28.4729 | 116.946 | 36.7454 | 34.1197 | 35.4249
29.4729 | 123.9411 | 38.2788 | 35.5168 | 36.6958
30.4729 | 127.8746 | 40.5705 | 37.1951 | 38.8075
31.4729 | 132.2836 | 42.2286 | 39.465 | 41.3434
32.4729 | 137.1631 | 44.1573 | 42.1356 | 43.9276
33.4729 | 144.7636 | 46.1515 | 43.7026 | 46.5755
34.4729 | 148.681 | 48.1545 | 45.0768 | 49.2528
35.4729 | 159.6487 | 50.1984 | 46.561 | 51.6688
36.4729 | 162.9732 | 52.06 | 48.105 | 53.9229
37.4729 | 166.5165 | 54.3979 | 50.0023 | 55.4543
38.4729 | 169.7673 | 56.5502 | 52.374 | 57.3226
39.4729 | 174.8321 | 58.1495 | 54.503 | 59.2008
40.4729 | 177.1349 | 60.5451 | 57.1463 | 61.0513
41.4729 | 181.1846 | 62.3082 | 59.163 | 63.1967
42.4729 | 186.1471 | 64.4036 | 60.7054 | 65.1255
43.4729 | 192.5958 | 66.9255 | 62.6088 | 66.9148
44.4729 | 193.0769 | 68.2489 | 64.1484 | 68.7999
45.4729 | 195.2774 | 69.8109 | 66.1619 | 71.4564
46.4729 | 199.5001 | 71.4041 | 68.278 | 72.6818
47.4729 | 201.2946 | 73.4749 | 70.1165 | 74.27
48.4729 | 203.4076 | 75.6441 | 72.5254 | 75.706
49.4729 | 206.2602 | 77.534 | 73.4768 | 78.2741
50.4729 | 206.3612 | 78.7966 | 74.828 | 80.5642
51.4729 | 208.3152 | 81.7578 | 77.5745 | 82.8645
52.4729 | 212.4378 | 85.1395 | 78.9183 | 84.3149
53.4729 | 216.1684 | 86.8718 | 80.6811 | 85.9261
54.4729 | 218.5647 | 88.6568 | 82.6312 | 88.4077
55.4729 | 223.5841 | 90.5069 | 84.8508 | 89.8415
56.4729 | 230.0168 | 92.0902 | 86.2952 | 91.4491
57.4729 | 234.505 | 93.9432 | 88.1331 | 92.9169
58.4729 | 237.7046 | 94.8221 | 89.6898 | 93.899
59.4729 | 243.1268 | 96.7252 | 91.5673 | 95.8459
60.4729 | 250.7594 | 97.5579 | 93.5056 | 96.8572
61.4729 | 249.8655 | 98.6543 | 94.6776 | 98.4248
62.4729 | 253.7957 | 100.3117 | 96.2738 | 99.3842
63.4729 | 254.041 | 101.4769 | 97.5126 | 100.2072
64.4729 | 254.8303 | 103.6834 | 98.2468 | 101.2191
65.4729 | 258.0611 | 104.536 | 99.5498 | 102.327
66.4729 | 260.4526 | 106.0161 | 100.64 | 103.6619
67.4729 | 265.1907 | 107.2706 | 101.8933 | 104.8909
68.4729 | 264.0602 | 108.448 | 102.9012 | 107.2642
69.4729 | 264.2976 | 110.3032 | 103.9355 | 109.9787
70.4729 | 261.7176 | 111.5025 | 105.6819 | 111.4873
71.4729 | 261.0273 | 112.6688 | 107.0692 | 112.5087
72.4729 | 263.0459 | 113.2681 | 108.1949 | 113.4935
73.4729 | 260.2992 | 114.3751 | 109.7803 | 114.4214
74.4729 | 259.4617 | 115.3577 | 110.9273 | 115.0956
75.4729 | 257.7189 | 116.3151 | 111.8771 | 115.8948
76.4729 | 256.2628 | 118.0397 | 113.1663 | 117.4147
77.4729 | 253.633 | 118.4535 | 114.2664 | 117.8419
78.4729 | 251.8573 | 119.1474 | 114.9677 | 118.8799
79.4729 | 251.7385 | 119.7256 | 116.2678 | 120.2384
80.4729 | 253.3152 | 119.8271 | 117.0946 | 121.064
81.4729 | 253.0427 | 120.0261 | 118.1831 | 121.4847
82.4729 | 252.8035 | 120.7647 | 118.8149 | 122.0617
83.4729 | 253.3573 | 121.9187 | 119.5018 | 122.4821
84.4729 | 251.0755 | 122.5667 | 120.2352 | 123.1345
85.4729 | 250.031 | 123.9083 | 121.1934 | 123.4072
86.4729 | 247.9447 | 124.9105 | 122.4978 | 123.9039
87.4729 | 245.8236 | 126.5321 | 122.9755 | 124.8079
88.4729 | 243.2541 | 127.4138 | 123.1824 | 126.3745
89.4729 | 240.4367 | 127.9791 | 123.4047 | 127.4417
90.4729 | 238.7647 | 127.9713 | 124.232 | 128.5443
91.4729 | 237.0478 | 128.4071 | 125.1235 | 129.1573
92.4729 | 238.1805 | 128.5002 | 125.9188 | 129.5941
93.4729 | 237.3367 | 128.9768 | 126.7433 | 129.5659
94.4729 | 234.9084 | 129.5212 | 127.2728 | 130.0045
95.4729 | 232.4845 | 130.1249 | 127.6417 | 129.857
96.4729 | 231.5642 | 130.6223 | 128.3245 | 130.0563
97.4729 | 231.3073 | 130.651 | 128.5887 | 130.8066
98.4729 | 230.8492 | 131.6289 | 128.9341 | 132.0906
99.4729 | 233.8029 | 131.9289 | 129.5688 | 132.4145
100.4729 | 236.166 | 132.5096 | 130.4505 | 132.8847
101.4729 | 237.1092 | 133.4469 | 130.4407 | 133.0576
102.4729 | 236.5993 | 133.4368 | 130.72 | 133.1416
103.4729 | 238.6551 | 134.0049 | 131.2058 | 133.3307
104.4729 | 240.666 | 134.3249 | 131.8161 | 133.7403
105.4729 | 241.6565 | 134.8961 | 132.2302 | 134.0716
106.4729 | 246.0266 | 134.8392 | 132.4895 | 134.3247
107.4729 | 248.1959 | 135.2407 | 132.9876 | 134.6312
108.4729 | 251.1222 | 135.6212 | 133.3249 | 135.2541
109.4729 | 253.0351 | 135.8416 | 133.0151 | 135.1011
110.4885 | 257.1862 | 135.4571 | 133.0996 | 134.93
111.4729 | 258.8456 | 135.7358 | 133.2761 | 135.0123
112.4729 | 260.3881 | 135.8664 | 133.2906 | 134.9398
113.4729 | 262.1443 | 136.1012 | 133.5523 | 135.5052
114.4729 | 265.9913 | 136.377 | 134.0951 | 135.7831
115.4729 | 271.5923 | 136.1975 | 134.4502 | 136.4287
116.4729 | 273.8465 | 136.7566 | 134.8798 | 137.0759
117.4729 | 278.1198 | 136.7948 | 134.7237 | 137.1509
118.4729 | 280.3669 | 137.0223 | 135.3062 | 136.9867
119.4729 | 280.4501 | 137.2968 | 135.6187 | 137.1912
120.4729 | 282.0152 | 137.1175 | 135.978 | 137.392
121.4729 | 282.0512 | 137.1153 | 136.2357 | 137.3666
122.4729 | 283.3971 | 136.7495 | 136.4587 | 137.3426
123.4729 | 286.2829 | 136.984 | 136.7896 | 137.5985
124.4729 | 287.5599 | 137.2517 | 137.7693 | 137.6163
125.4729 | 289.6891 | 137.495 | 138.2138 | 137.8446
126.4729 | 293.0718 | 137.568 | 138.455 | 138.0275
127.4729 | 295.4587 | 137.6997 | 139.133 | 138.1658
128.4729 | 296.8958 | 137.9925 | 139.4484 | 138.4546
129.4729 | 296.6707 | 138.7476 | 139.7114 | 139.0177
130.4729 | 295.5892 | 138.4704 | 140.1691 | 139.3865
131.4729 | 297.5868 | 138.446 | 139.8768 | 139.4609
132.4729 | 296.7139 | 138.4998 | 139.7889 | 139.7328
133.4729 | 297.4883 | 138.8442 | 139.8003 | 139.5581
134.4729 | 300.8002 | 139.5394 | 140.0649 | 140.0099
135.4729 | 303.2409 | 139.7607 | 140.2919 | 139.9979
136.4729 | 305.1399 | 139.7349 | 140.7192 | 140.5702
137.4729 | 306.3609 | 139.9292 | 141.153 | 141.2991
138.4729 | 307.5222 | 140.1927 | 141.1528 | 141.46
139.4729 | 312.2537 | 140.3676 | 141.99 | 141.5781
140.4729 | 317.5032 | 140.0406 | 142.5826 | 141.7673
141.4729 | 318.0546 | 140.4006 | 143.2011 | 142.4418
142.4729 | 320.171 | 140.6076 | 142.8394 | 142.3409
143.4729 | 319.971 | 140.448 | 143.2646 | 142.3365
144.4729 | 322.4692 | 140.869 | 143.6745 | 142.596
145.4729 | 321.727 | 141.7543 | 143.8558 | 143.0318
146.4729 | 322.1013 | 142.6709 | 143.7471 | 143.502
147.4729 | 323.625 | 144.107 | 144.3158 | 144.0601
148.4729 | 327.5429 | 144.2796 | 144.7342 | 144.2105
149.4729 | 331.6404 | 145.1272 | 145.1899 | 144.8105
150.4729 | 331.8748 | 145.1829 | 145.7147 | 145.2202
151.4729 | 335.8879 | 145.3336 | 145.7101 | 145.3324
152.4729 | 337.2706 | 146.5211 | 146.5915 | 145.7468
153.4729 | 359.1949 | 147.3705 | 147.2256 | 145.9627
154.4729 | 359.5468 | 148.093 | 148.1793 | 146.9321
155.4729 | 358.2652 | 148.589 | 149.1319 | 147.6918
156.4729 | 365.7749 | 148.6051 | 148.9633 | 147.6766
157.4729 | 367.1494 | 149.5195 | 149.2986 | 148.4418
158.4729 | 365.2439 | 149.1983 | 149.6109 | 149.5706
159.4729 | 362.564 | 149.1419 | 149.6734 | 150.3295
160.4729 | 363.6173 | 150.0398 | 150.1912 | 150.3944
161.4729 | 362.7387 | 150.4807 | 150.4805 | 151.0915
162.4729 | 363.8547 | 151.1787 | 151.2265 | 151.7169
163.4729 | 380.7564 | 152.0348 | 151.7798 | 151.7504
164.4729 | 378.0008 | 152.6703 | 152.5507 | 152.732
165.4729 | 373.567 | 153.0834 | 153.1166 | 153.4061
166.4729 | 373.3802 | 153.2556 | 153.5805 | 153.5813
167.4729 | 386.4905 | 154.1306 | 153.6911 | 154.0481
168.4729 | 385.4613 | 154.6485 | 153.7416 | 154.2458
169.4729 | 394.1164 | 155.6082 | 154.4674 | 155.2399
170.4885 | 45.212 | 125.8561 | 161.4877 | 28.5835
171.4729 | 26.0543 | 125.8186 | 161.1238 | 26.0471
172.4729 | 383.7022 | 152.632 | 157.1917 | 28.6768
173.4729 | 382.9477 | 158.0488 | 156.2223 | 158.1229
174.4729 | 385.1805 | 158.4749 | 157.7846 | 158.7389
175.4729 | 381.8388 | 158.8048 | 158.2667 | 159.729
176.4729 | 384.7623 | 159.6976 | 159.2021 | 161.065
177.4729 | 391.7747 | 160.1255 | 160.0821 | 161.0148
178.4729 | 393.0261 | 161.4153 | 161.3066 | 162.4869
179.4729 | 404.5358 | 161.9389 | 161.5344 | 163.8723
180.4729 | 405.4264 | 162.5769 | 162.281 | 164.3238
181.4729 | 407.7945 | 163.4306 | 163.2748 | 166.0692
182.4729 | 411.877 | 163.9485 | 163.9149 | 167.0942
183.4729 | 411.5939 | 164.8543 | 164.3178 | 168.0656
184.4729 | 413.0875 | 165.9657 | 164.9592 | 167.4051
185.4729 | 414.4348 | 166.7003 | 165.0116 | 168.2838
186.4729 | 412.0424 | 166.5234 | 165.4002 | 168.2131
187.4729 | 413.8122 | 167.03 | 165.4863 | 168.6793
188.4729 | 415.5818 | 167.4841 | 165.7359 | 168.7959
189.4729 | 414.3434 | 168.0616 | 165.7451 | 168.7102
190.4729 | 411.7053 | 169.0097 | 165.3084 | 169.1805
191.4729 | 409.468 | 169.5864 | 165.2792 | 169.2414
192.4729 | 412.0143 | 169.6359 | 165.6053 | 168.7057
193.4729 | 412.2185 | 170.1907 | 166.1411 | 168.9268
194.4729 | 408.8564 | 170.7792 | 166.0513 | 168.9662
195.4729 | 408.9647 | 170.941 | 165.9593 | 168.7483
196.4729 | 408.3527 | 172.6152 | 166.2459 | 169.3988
197.4729 | 409.0545 | 172.9474 | 166.3251 | 169.5165
198.4729 | 415.0043 | 173.7291 | 167.1092 | 170.3947
199.4729 | 414.9512 | 174.2195 | 167.5195 | 171.3389
200.4729 | 416.2528 | 174.4531 | 167.4895 | 171.1594
201.4729 | 415.2731 | 175.349 | 168.7584 | 172.2824
202.4729 | 412.6833 | 175.3138 | 169.401 | 172.8355
203.4729 | 417.5798 | 175.5575 | 169.3562 | 173.1331
204.4729 | 417.0182 | 174.9195 | 169.1658 | 172.8081
205.4729 | 423.8579 | 175.2818 | 170.3605 | 173.4263
206.4729 | 421.7777 | 175.3329 | 170.7507 | 172.8333
207.4729 | 421.4072 | 174.9682 | 171.1245 | 172.8751
208.4729 | 422.0933 | 175.4748 | 171.1203 | 172.8414
209.4729 | 425.2179 | 175.4504 | 171.4419 | 173.4868
210.4729 | 428.5098 | 175.3134 | 171.4142 | 173.5377
211.4729 | 426.4834 | 175.884 | 171.8603 | 174.6634
212.4729 | 435.3906 | 176.4079 | 171.8723 | 175.0222
213.4729 | 432.3988 | 176.0902 | 172.5772 | 175.2315
214.4729 | 431.9013 | 176.0537 | 172.9225 | 175.6959
215.4729 | 430.3662 | 175.7632 | 172.9229 | 176.7411
216.4729 | 437.9336 | 175.6212 | 173.2958 | 176.5349
217.4729 | 440.3401 | 175.5374 | 173.5605 | 177.1659
218.4729 | 444.439 | 176.23 | 174.0294 | 177.4534
219.4729 | 447.1629 | 176.4148 | 174.8011 | 177.6375
220.4729 | 455.1877 | 176.3167 | 175.2736 | 177.4225
221.4729 | 458.6005 | 176.4955 | 175.2327 | 177.3837
222.4729 | 455.0676 | 176.59 | 175.36 | 178.025
223.4729 | 457.7737 | 177.0165 | 175.2217 | 177.9282
224.4729 | 454.0506 | 177.6088 | 175.4178 | 178.0739
225.4729 | 464.0163 | 177.992 | 175.3596 | 178.2283
226.4729 | 462.8534 | 177.9885 | 175.0783 | 177.9742
227.4729 | 463.2473 | 178.2106 | 175.0555 | 178.9129
228.4729 | 474.3359 | 178.8845 | 176.0031 | 179.0845
229.4729 | 475.4686 | 179.4049 | 176.1169 | 179.6741
230.4729 | 485.3487 | 180.24 | 176.533 | 180.2177
231.4729 | 499.4431 | 179.5279 | 176.6174 | 180.6546
232.4729 | 508.8787 | 179.9616 | 177.3226 | 180.1881
233.4729 | 512.7938 | 180.7316 | 177.4977 | 180.4658
234.4729 | 529.458 | 180.7247 | 177.4819 | 179.7831
235.4729 | 534.394 | 182.0649 | 177.9213 | 179.8899
236.4729 | 552.3829 | 182.6605 | 178.3558 | 180.2564
237.4729 | 562.9403 | 184.0058 | 179.536 | 180.9176
238.4729 | 567.8045 | 183.5975 | 179.5628 | 180.9805
239.4729 | 589.4885 | 184.7171 | 180.349 | 181.5583
240.4729 | 585.2442 | 184.3713 | 180.6821 | 181.6903
241.4729 | 600.3373 | 184.2477 | 180.5516 | 181.7499
242.4729 | 612.4282 | 184.2681 | 180.179 | 182.5068
243.4729 | 628.996 | 184.6936 | 180.764 | 182.8806
244.4729 | 644.5468 | 185.5242 | 180.6767 | 183.1557
245.4729 | 655.7866 | 185.685 | 180.5029 | 182.6677
246.4729 | 643.6532 | 187.1962 | 181.2857 | 183.2057
247.4729 | 638.8461 | 186.93 | 182.053 | 182.9816
248.4729 | 642.1766 | 186.9643 | 182.1164 | 182.9357
249.4729 | 654.2033 | 186.9144 | 182.3879 | 183.4976
250.4729 | 670.5386 | 186.9684 | 183.3345 | 184.8809
251.4729 | 690.3177 | 187.1748 | 183.5807 | 184.9015
252.4729 | 694.2604 | 187.6051 | 183.5449 | 185.2409
253.4729 | 690.8749 | 188.2872 | 183.2122 | 185.0061
254.4729 | 695.3035 | 188.2366 | 183.1658 | 184.9444
255.4729 | 691.1042 | 188.0598 | 182.7917 | 184.5494
256.4729 | 694.8372 | 188.4127 | 182.8738 | 184.9067
257.4729 | 709.2557 | 188.9593 | 183.3169 | 186.3099
258.4729 | 702.6301 | 189.1457 | 183.5006 | 186.264
259.4729 | 716.3119 | 189.2038 | 184.4423 | 186.533
260.4729 | 712.2514 | 189.8616 | 185.6761 | 187.4586
261.4729 | 705.2572 | 190.5235 | 186.5976 | 189.095
262.4729 | 695.2059 | 190.1395 | 186.5457 | 189.2591
263.4729 | 695.0189 | 190.377 | 187.7472 | 189.7545
264.4729 | 697.9185 | 190.3976 | 189.0372 | 191.0328
265.4729 | 717.1279 | 190.6792 | 189.3148 | 191.6791
266.4729 | 723.7521 | 191.3705 | 190.3671 | 191.7477
267.4729 | 721.6389 | 191.4736 | 190.5742 | 193.0331
268.4729 | 726.1059 | 191.512 | 190.6472 | 193.4723
269.4729 | 712.1645 | 192.1094 | 190.8743 | 193.2513
270.4729 | 704.4965 | 192.847 | 190.813 | 194.4507
271.4729 | 692.8387 | 192.5262 | 190.3824 | 194.2832
272.4729 | 681.3262 | 193.4483 | 190.6693 | 194.8157
273.4729 | 673.7753 | 194.091 | 190.988 | 195.5901
274.4729 | 678.8144 | 193.717 | 191.3807 | 194.9578
275.4729 | 687.7671 | 193.4085 | 191.6669 | 195.0001
276.4729 | 697.5693 | 194.1698 | 191.9439 | 195.1954
277.4729 | 707.8358 | 194.0522 | 191.8724 | 194.7341
278.4729 | 723.5791 | 194.9199 | 192.8167 | 195.1851
279.4729 | 724.9902 | 194.9589 | 192.6288 | 195.5907
280.4729 | 726.0857 | 195.5381 | 193.2197 | 195.8217
281.4729 | 722.1619 | 195.2607 | 192.9598 | 195.3326
282.4729 | 731.9677 | 195.6441 | 193.0956 | 195.5185
283.4729 | 727.6152 | 195.8639 | 193.55 | 195.5904
284.4729 | 719.5387 | 195.1768 | 193.5972 | 195.5538
285.4729 | 721.5261 | 194.8372 | 193.1896 | 195.4047
286.4729 | 713.8807 | 194.6063 | 194.8172 | 196.7174
287.4729 | 722.9764 | 194.9139 | 194.9869 | 196.2979
288.4729 | 707.5902 | 195.3305 | 195.2605 | 195.9257
289.4729 | 713.8908 | 195.3015 | 195.9944 | 196.1266
290.4885 | 718.2017 | 195.3722 | 195.8294 | 196.2717
291.4729 | 730.5667 | 196.5556 | 196.2087 | 196.5871
292.4729 | 748.1562 | 196.4967 | 196.5842 | 196.7574
293.4729 | 751.9174 | 196.591 | 196.7688 | 197.9854
294.4729 | 742.1589 | 196.7857 | 196.8672 | 197.789
295.4729 | 735.9862 | 196.6896 | 197.2483 | 197.7811
296.4729 | 738.2652 | 197.8222 | 197.5303 | 197.7676
297.4729 | 735.3599 | 198.2442 | 197.0696 | 197.4997
298.4729 | 744.9786 | 198.0676 | 196.8008 | 197.3919
299.4729 | 745.6745 | 198.6144 | 196.8699 | 197.76
300.4729 | 735.3479 | 198.277 | 196.9307 | 197.5019
301.4729 | 739.2534 | 198.0645 | 196.8415 | 197.9417
302.4729 | 748.3084 | 197.8969 | 197.3402 | 198.6282
303.4729 | 757.4529 | 198.6139 | 196.8644 | 198.6681
304.4729 | 751.4601 | 199.656 | 198.3689 | 198.9452
305.4729 | 763.2174 | 199.953 | 198.296 | 198.8999
306.4729 | 771.0962 | 200.7136 | 199.3195 | 199.2643
307.4729 | 783.4243 | 200.6275 | 199.0348 | 199.2423
308.4729 | 781.8862 | 201.1188 | 199.098 | 198.8694
309.4729 | 786.7069 | 201.2634 | 198.6736 | 198.4415
310.4729 | 791.4818 | 200.9251 | 198.517 | 198.0943
311.4729 | 797.1506 | 200.7759 | 198.2018 | 198.3324
312.4729 | 799.8887 | 201.0324 | 197.9859 | 197.9534
313.4729 | 779.6677 | 200.7794 | 198.1787 | 198.1586
314.4729 | 780.9448 | 200.4511 | 198.4129 | 197.9614
315.4729 | 773.5653 | 200.2509 | 198.0822 | 198.4208
316.4729 | 764.9578 | 200.2027 | 198.0172 | 198.6746
317.4729 | 777.3914 | 200.105 | 198.2729 | 198.5414
318.4729 | 784.2129 | 200.2548 | 197.8252 | 199.2001
319.4729 | 793.1097 | 200.2215 | 197.8702 | 199.1044
320.4729 | 800.5696 | 200.965 | 198.8522 | 199.1069
321.4729 | 805.8373 | 200.8962 | 198.3351 | 199.4206
322.4729 | 813.9341 | 200.4648 | 198.1571 | 199.7301
323.4729 | 796.6409 | 200.4686 | 198.1807 | 199.3903
324.4729 | 789.628 | 201.819 | 198.422 | 199.7653
325.4729 | 780.3313 | 203.0589 | 198.0201 | 199.7896
326.4729 | 775.7917 | 202.8964 | 198.8222 | 199.3648
327.4729 | 774.6488 | 202.6293 | 200.0821 | 199.9366
328.4729 | 772.4667 | 203.1968 | 199.8512 | 200.1692
329.4729 | 790.5081 | 202.9996 | 199.5445 | 200.373
330.4729 | 786.8114 | 203.3006 | 200.2089 | 200.0587
331.4729 | 785.9291 | 203.4196 | 201.3132 | 200.5195
332.4729 | 795.716 | 203.9123 | 202.0081 | 200.7654
333.4729 | 795.2127 | 204.8497 | 202.3638 | 200.9831
334.4729 | 787.2515 | 205.7291 | 201.9497 | 200.7698
335.4729 | 788.0835 | 205.9271 | 201.6036 | 200.4018
336.4729 | 787.8497 | 205.3896 | 201.1225 | 201.4528
337.4729 | 787.1986 | 205.204 | 200.82 | 201.8523
338.4729 | 779.542 | 204.9566 | 200.5051 | 201.1627
339.4729 | 781.8778 | 205.5215 | 200.6843 | 201.323
340.4729 | 788.6663 | 205.6453 | 201.5485 | 202.3425
341.4729 | 791.8152 | 205.9247 | 201.599 | 202.5395
342.4729 | 776.0762 | 205.5876 | 201.5981 | 202.9895
343.4729 | 769.1268 | 205.8588 | 201.5641 | 202.8285
344.4729 | 769.8746 | 206.87 | 202.0948 | 203.9261
345.4729 | 771.677 | 206.023 | 202.0492 | 203.6011
346.4729 | 764.0694 | 205.3519 | 202.2448 | 203.4963
347.4729 | 763.7831 | 206.5927 | 202.899 | 203.0974
348.4729 | 761.6089 | 206.3363 | 203.0748 | 202.9594
349.4729 | 756.784 | 206.4935 | 203.7956 | 202.9622
350.4885 | 757.323 | 206.4472 | 204.0192 | 203.0033
351.4729 | 751.1622 | 206.3268 | 204.5946 | 203.0771
352.4729 | 745.1621 | 206.8849 | 204.5835 | 203.392
353.4729 | 736.6855 | 206.8338 | 204.195 | 203.8013
354.4729 | 734.8056 | 206.7683 | 205.0079 | 204.7764
355.4729 | 727.705 | 206.7333 | 204.2663 | 204.74
356.4729 | 723.888 | 207.3665 | 203.8036 | 205.8285
357.4729 | 725.8421 | 207.4441 | 204.3021 | 205.8564
358.4729 | 735.508 | 207.4609 | 203.8595 | 206.0596
359.4729 | 731.8894 | 207.3135 | 203.3655 | 205.9527
360.4729 | 732.034 | 206.8022 | 202.5964 | 205.6356
361.4729 | 739.63 | 206.755 | 202.3437 | 206.2538
362.4729 | 747.893 | 206.8766 | 203.2099 | 205.8703
363.4729 | 751.9451 | 206.959 | 203.0283 | 206.2203
364.4729 | 756.3156 | 206.7937 | 204.3476 | 206.3677
365.4729 | 767.9851 | 207.5071 | 204.0213 | 206.189
366.4729 | 764.5356 | 208.0758 | 204.3255 | 205.6607
367.4729 | 761.4332 | 208.5249 | 204.2409 | 205.5677
368.4729 | 762.8387 | 208.413 | 204.4386 | 206.5368
369.4729 | 767.0498 | 208.8716 | 204.5196 | 206.788
370.4729 | 763.3692 | 209.0888 | 204.8314 | 208.2171
371.4729 | 770.4009 | 209.3088 | 204.7744 | 208.2746
372.4729 | 774.1546 | 209.3496 | 204.7785 | 208.2366
373.4729 | 783.5827 | 209.6639 | 205.7898 | 208.746
374.4729 | 789.6691 | 209.6035 | 205.8885 | 208.1234
375.4729 | 786.1238 | 209.4973 | 205.5395 | 207.454
376.4729 | 770.7224 | 209.2192 | 205.4845 | 207.7304
377.4729 | 784.1891 | 208.578 | 205.6212 | 207.5673
378.4729 | 782.0701 | 208.4444 | 205.4001 | 207.6859
379.4729 | 779.7986 | 208.3312 | 205.7924 | 207.8324
380.4729 | 782.486 | 208.6731 | 205.8635 | 208.5903
381.4729 | 787.6551 | 208.7144 | 206.3817 | 208.5971
382.4729 | 796.0782 | 209.3017 | 206.563 | 208.998
383.4729 | 791.1888 | 209.2144 | 206.9134 | 209.5105
384.4729 | 790.1667 | 209.1023 | 207.4228 | 210.4209
385.4729 | 778.9363 | 208.8897 | 207.3242 | 210.5168
386.4729 | 775.8445 | 208.6461 | 207.7325 | 210.581
387.4729 | 776.0434 | 208.8911 | 207.6619 | 210.2068
388.4729 | 773.5092 | 209.2432 | 207.4404 | 210.4734
389.4729 | 774.3968 | 209.5079 | 207.4681 | 211.241
390.4729 | 773.7146 | 209.7758 | 207.8547 | 211.0882
391.4729 | 773.2766 | 209.6769 | 208.4288 | 210.9637
392.4729 | 771.7603 | 209.5534 | 208.4862 | 210.6131
393.4729 | 773.8039 | 209.5711 | 208.1704 | 210.507
394.4729 | 765.8365 | 209.7735 | 208.5549 | 210.9372
395.4729 | 766.4433 | 210.2951 | 208.8837 | 210.7289
396.4729 | 763.731 | 210.2038 | 208.4989 | 210.329
397.4729 | 761.3347 | 210.3321 | 208.4853 | 211.2502
398.4729 | 765.5873 | 210.6 | 209.251 | 211.1766
399.4729 | 767.6625 | 210.9845 | 209.1043 | 211.7307
400.4729 | 769.1446 | 211.3139 | 208.9912 | 211.2471
401.4729 | 767.6715 | 211.8865 | 208.7574 | 210.8239
402.4729 | 757.8339 | 212.6303 | 208.8199 | 210.8261
403.4729 | 754.0656 | 213.7753 | 209.0398 | 210.6527
404.4729 | 754.2335 | 214.3994 | 210.1618 | 210.7594
405.4729 | 758.5412 | 214.2646 | 210.055 | 210.9034
406.4729 | 759.5157 | 214.388 | 210.5657 | 211.5873
407.4729 | 761.3064 | 214.8369 | 210.8859 | 211.5806
408.4729 | 756.8542 | 215.6009 | 211.3112 | 212.1145
409.4729 | 758.2498 | 216.0874 | 211.163 | 212.2831
410.4885 | 765.8242 | 216.6393 | 210.9579 | 212.0978
411.4729 | 763.986 | 216.8365 | 210.9492 | 212.7096
412.4729 | 762.0532 | 217.2032 | 210.9732 | 212.7238
413.4729 | 760.6928 | 217.8034 | 210.6754 | 212.8713
414.4729 | 761.1129 | 217.8366 | 210.3706 | 213.2942
415.4729 | 764.3117 | 218.1369 | 210.3547 | 213.5786
416.4729 | 754.1748 | 218.8477 | 210.1508 | 213.3311
417.4729 | 743.4796 | 218.2177 | 209.7913 | 212.8131
418.4729 | 740.2398 | 217.7352 | 209.6812 | 212.5498
419.4729 | 739.5555 | 217.6621 | 209.6865 | 212.2074
420.4729 | 739.6413 | 217.7893 | 209.6845 | 213.3179
421.4729 | 736.8662 | 217.4274 | 209.632 | 213.0425
422.4729 | 731.474 | 217.6107 | 210.1828 | 213.4943
423.4729 | 732.9952 | 217.8414 | 209.7415 | 212.7041
424.4729 | 731.177 | 218.4508 | 209.745 | 213.3486
425.4729 | 733.5443 | 218.0161 | 209.3996 | 213.1027
426.4729 | 738.3708 | 217.4584 | 208.9317 | 213.0704
427.4729 | 737.537 | 217.1395 | 209.7496 | 213.6066
428.4729 | 736.5765 | 217.4212 | 209.6153 | 213.8883
429.4729 | 740.0869 | 217.6008 | 209.4611 | 213.4335
430.4729 | 744.1139 | 217.6201 | 209.2546 | 213.5523
431.4729 | 746.4614 | 217.4479 | 208.9678 | 213.8288
432.4729 | 747.9759 | 217.5389 | 208.8617 | 214.0503
433.4729 | 744.3701 | 217.996 | 209.7653 | 213.778
434.4729 | 742.5973 | 217.929 | 210.1778 | 214.6812
435.4729 | 740.8813 | 218.234 | 210.1524 | 213.9929
436.4729 | 742.9511 | 218.2603 | 210.3815 | 214.1093
437.4729 | 751.3893 | 218.8824 | 210.386 | 214.7286
438.4729 | 745.9194 | 219.4095 | 210.3138 | 214.4645
439.4729 | 741.9009 | 218.9837 | 210.4224 | 214.4896
440.4729 | 739.5587 | 219.2258 | 210.8683 | 214.7555
441.4729 | 735.0523 | 219.6164 | 211.5432 | 215.5358
442.4729 | 735.1962 | 220.5077 | 211.948 | 216.5339
443.4729 | 735.2162 | 221.6985 | 213.588 | 216.9629
444.4729 | 730.2289 | 222.0114 | 214.6166 | 218.0768
445.4729 | 730.1962 | 221.7 | 214.9028 | 217.8542
446.4729 | 730.6236 | 221.2342 | 215.1839 | 218.3705
447.4729 | 727.3448 | 221.8317 | 215.3938 | 218.618
448.4729 | 724.5585 | 221.7841 | 216.4607 | 218.8654
449.4729 | 723.5243 | 222.3224 | 216.025 | 218.6185
450.4729 | 720.8548 | 222.9726 | 216.171 | 218.6229
451.4729 | 717.2589 | 223.2751 | 216.1847 | 218.418
452.4729 | 716.9259 | 223.44 | 216.101 | 217.8951
453.4729 | 716.7206 | 224.4818 | 216.7114 | 218.302
454.4729 | 712.7041 | 224.1525 | 216.4676 | 217.8861
455.4729 | 714.2737 | 223.6196 | 217.0899 | 218.0695
456.4729 | 716.9787 | 223.984 | 217.697 | 218.319
457.4729 | 718.6812 | 223.7479 | 217.7889 | 218.231
458.4729 | 715.834 | 223.7533 | 217.9359 | 218.3886
459.4729 | 714.07 | 223.9356 | 218.2336 | 218.3959
460.4729 | 717.3178 | 224.0286 | 218.7123 | 219.0725
461.4729 | 715.6322 | 223.9423 | 218.2094 | 219.2172
462.4729 | 714.5778 | 224.3263 | 218.1548 | 219.0979
463.4729 | 712.7742 | 224.914 | 218.0049 | 219.557
464.4729 | 710.3885 | 225.0529 | 218.509 | 219.6002
465.4729 | 709.0319 | 225.8156 | 218.1049 | 219.9455
466.4729 | 709.9679 | 225.7183 | 218.256 | 220.0494
467.4729 | 712.7084 | 226.7665 | 219.1544 | 219.8305
468.4729 | 713.2693 | 226.449 | 218.8276 | 219.4317
469.4729 | 715.9182 | 226.0828 | 218.7526 | 219.0639
470.4729 | 715.2347 | 225.864 | 218.8616 | 218.8861
471.4729 | 712.5863 | 225.7528 | 218.6433 | 218.8663
472.4729 | 710.6268 | 226.1833 | 218.745 | 219.5027
473.4729 | 705.5911 | 226.0295 | 218.8544 | 220.2214
474.4729 | 703.4776 | 227.1521 | 219.006 | 220.399
475.4729 | 702.6011 | 227.2889 | 218.9621 | 220.4994
476.4729 | 700.7864 | 226.7688 | 218.9755 | 221.0171
477.4729 | 698.8952 | 226.7839 | 219.2869 | 220.952
478.4729 | 702.8421 | 227.3932 | 219.0936 | 220.5098
479.4729 | 703.2359 | 227.8906 | 220.1301 | 220.4088
480.4729 | 703.9087 | 228.3425 | 219.8342 | 220.5571
481.4729 | 701.9037 | 228.7658 | 220.0854 | 221.9694
482.4729 | 698.5601 | 228.9336 | 220.2955 | 222.3027
483.4729 | 700.5692 | 229.7821 | 220.1981 | 222.3182
484.4729 | 704.273 | 230.0493 | 220.4065 | 221.9373
485.4729 | 701.6732 | 230.03 | 220.4679 | 222.1966
486.4729 | 701.3684 | 229.6982 | 221.1817 | 222.9496
487.4729 | 700.949 | 229.3816 | 221.4826 | 222.9451
488.4729 | 699.7134 | 229.1806 | 222.2118 | 222.7299
489.4729 | 698.8 | 229.9424 | 222.5056 | 222.6457
490.4729 | 698.8475 | 229.6825 | 222.887 | 223.2664
491.4729 | 697.4706 | 229.1277 | 223.2675 | 223.206
492.4729 | 698.998 | 229.0202 | 223.6656 | 223.0706
493.4729 | 700.8002 | 229.2436 | 223.8536 | 223.1077
494.4729 | 700.258 | 229.1692 | 223.5973 | 222.8101
495.4729 | 698.2905 | 229.2791 | 224.1574 | 222.6164
496.4729 | 697.2589 | 229.6749 | 224.2101 | 222.8877
497.4729 | 695.1813 | 229.5749 | 224.2859 | 223.6852
498.4729 | 694.8558 | 229.6424 | 224.1611 | 223.6171
499.4729 | 697.8376 | 230.2309 | 224.0155 | 224.1756
500.4729 | 696.1898 | 229.8968 | 223.7164 | 224.1387
501.4729 | 696.2453 | 230.4725 | 223.5042 | 224.2318
502.4729 | 696.1322 | 230.8013 | 223.6685 | 223.9291
503.4729 | 703.4078 | 230.8258 | 224.059 | 224.0522
504.4729 | 701.0641 | 231.0675 | 223.8813 | 224.6773
505.4729 | 697.3589 | 231.3296 | 224.0585 | 225.0458
506.4729 | 697.316 | 231.1377 | 224.4996 | 224.7325
507.4885 | 700.8928 | 230.9861 | 225.2045 | 225.0373
508.4729 | 699.5241 | 231.5213 | 226.073 | 225.6976
509.4729 | 699.767 | 231.4558 | 226.7883 | 225.7915
510.4729 | 698.1631 | 231.4847 | 227.503 | 225.8996
511.4729 | 697.6309 | 231.9332 | 227.6784 | 225.6209
512.4729 | 696.6986 | 232.17 | 227.1702 | 225.5493
513.4729 | 695.6782 | 232.3665 | 227.1476 | 225.8592
514.4729 | 694.7893 | 232.8742 | 227.3359 | 225.6261
515.4729 | 693.4555 | 233.6054 | 227.8693 | 226.5495
516.4729 | 693.529 | 233.9444 | 227.5984 | 226.6192
517.4729 | 692.248 | 234.3786 | 228.8484 | 227.7479
518.4729 | 691.2336 | 234.1543 | 229.1735 | 228.1494
519.4729 | 689.3031 | 234.7575 | 229.5133 | 228.613
520.4729 | 687.4717 | 234.9945 | 230.1142 | 229.3184
521.4729 | 689.3702 | 235.929 | 230.8472 | 229.6208
522.4729 | 690.1968 | 236.0473 | 231.3331 | 229.8375
523.4729 | 688.5178 | 235.9684 | 231.5873 | 230.3427
524.4729 | 687.6181 | 235.9058 | 232.1126 | 230.8653
525.4729 | 685.7897 | 236.287 | 231.9787 | 231.5617
526.4729 | 687.8432 | 236.8972 | 231.9199 | 231.9492
527.4729 | 687.0064 | 237.3572 | 231.8542 | 232.8072
528.4729 | 687.4076 | 237.8088 | 232.2924 | 234.0559
529.4729 | 687.5962 | 237.9152 | 232.0208 | 234.0048
530.4885 | 686.7784 | 237.8148 | 231.6451 | 233.985
531.4729 | 684.8345 | 238.4108 | 231.9078 | 234.0059
532.4729 | 683.0257 | 238.8042 | 231.8113 | 234.1859
533.4729 | 681.8314 | 238.5134 | 231.4888 | 234.1967
534.4729 | 679.4987 | 238.404 | 231.351 | 234.0314
535.4729 | 682.1064 | 238.3523 | 231.5424 | 233.8462
536.4729 | 681.9768 | 238.5902 | 232.0195 | 234.2873
537.4729 | 682.1 | 238.3843 | 231.4897 | 233.8908
538.4729 | 680.8995 | 238.0803 | 231.5467 | 233.3139
539.4729 | 679.5852 | 237.8219 | 231.8266 | 233.3895
540.4729 | 678.7486 | 237.7255 | 231.6017 | 233.7379
541.4729 | 678.5804 | 237.4389 | 231.5638 | 233.8974
542.4729 | 676.9647 | 237.6714 | 231.1996 | 234.327
543.4729 | 681.1032 | 237.7974 | 231.4081 | 234.0485
544.4729 | 679.7311 | 237.5752 | 231.8987 | 234.9186
545.4729 | 678.8191 | 237.5516 | 232.7147 | 235.9115
546.4729 | 679.0824 | 237.3893 | 232.5651 | 235.968
547.4729 | 676.9923 | 237.3859 | 232.2173 | 235.8304
548.4729 | 678.6637 | 237.5917 | 232.1631 | 235.1916
549.4729 | 679.886 | 237.3475 | 231.9863 | 234.2675
550.4729 | 678.1667 | 237.0404 | 231.7011 | 233.8999
551.4729 | 677.822 | 236.9855 | 231.1992 | 234.0067
552.4729 | 675.8013 | 237.1383 | 230.6965 | 233.6752
553.4729 | 676.3162 | 237.4482 | 230.9643 | 234.1108
554.4729 | 686.1473 | 237.703 | 231.4591 | 234.5964
555.4729 | 686.2702 | 238.4939 | 231.8092 | 234.5936
556.4729 | 687.7937 | 238.6012 | 232.0109 | 234.5173
557.4729 | 686.7043 | 238.8784 | 232.1002 | 234.3119
558.4729 | 691.4109 | 238.8473 | 231.7833 | 234.1795
559.4729 | 689.2591 | 238.6543 | 232.2137 | 234.6416
560.4729 | 686.619 | 239.0263 | 232.8719 | 234.2478
561.4729 | 684.3993 | 238.996 | 233.0414 | 235.0771
562.4729 | 683.0283 | 239.246 | 232.6504 | 235.0912
563.4729 | 681.1403 | 239.0691 | 232.7556 | 234.9468
564.4729 | 680.862 | 239.1993 | 232.5511 | 234.4638
565.4729 | 680.9177 | 239.1447 | 233.0253 | 234.3976
566.4729 | 679.3209 | 238.8059 | 232.7335 | 234.2539
567.4729 | 684.9263 | 238.5259 | 232.6469 | 234.1995
568.4729 | 684.3353 | 238.3575 | 232.2695 | 234.2551
569.4729 | 685.4666 | 238.4069 | 232.7133 | 234.2149
570.4729 | 684.4932 | 238.4662 | 232.3761 | 234.6409
571.4729 | 681.0784 | 238.6235 | 232.255 | 234.4226
572.4729 | 680.4395 | 238.3572 | 232.2553 | 234.5028
573.4729 | 678.0875 | 239.2926 | 232.8301 | 234.9328
574.4729 | 678.4295 | 239.3122 | 232.7841 | 235.115
575.4729 | 679.355 | 239.2957 | 232.8748 | 235.3661
576.4729 | 676.0274 | 239.2919 | 233.1166 | 235.3811
577.4729 | 674.3892 | 239.5146 | 233.1539 | 235.6183
578.4729 | 676.1601 | 239.1573 | 233.5507 | 235.8445
579.4729 | 675.2109 | 239.0459 | 233.095 | 235.5084
580.4729 | 679.4044 | 238.8721 | 232.7963 | 235.8648
581.4729 | 680.2998 | 238.9301 | 232.7975 | 235.7809
582.4729 | 681.816 | 238.7514 | 232.1822 | 235.2331
583.4729 | 679.954 | 238.3946 | 231.6561 | 234.6877
584.4729 | 679.4007 | 238.2107 | 231.0566 | 234.8919
585.4729 | 678.0512 | 238.4492 | 231.5427 | 235.3239
586.4729 | 678.134 | 238.3621 | 231.3934 | 235.0018
587.4729 | 677.7497 | 238.5003 | 231.5003 | 235.3936
588.4729 | 678.319 | 238.5121 | 231.8318 | 235.5897
589.4729 | 677.3824 | 238.8161 | 231.5054 | 235.5554
590.4729 | 678.1226 | 239.2342 | 231.4231 | 235.2937
591.4729 | 679.4721 | 239.247 | 232.1838 | 235.3232
592.4729 | 679.79 | 239.5001 | 232.7265 | 235.5976
593.4729 | 685.2566 | 239.9362 | 232.8181 | 235.7163
594.4729 | 682.6255 | 240.0983 | 232.7566 | 236.3857
595.4729 | 678.4929 | 240.4217 | 232.8829 | 236.5774
596.4729 | 677.6266 | 240.346 | 233.2752 | 236.2522
597.4729 | 677.293 | 240.1438 | 233.1887 | 236.8003
598.4729 | 679.0956 | 240.4177 | 233.1411 | 237.1851
599.4729 | 682.245 | 239.8282 | 232.6883 | 236.7302
600.4729 | 680.4874 | 239.7243 | 232.4876 | 236.8925
601.4729 | 680.502 | 239.7042 | 232.6003 | 237.1508
602.4729 | 680.9568 | 239.8548 | 232.5605 | 236.9858
603.4729 | 685.0912 | 240.0052 | 232.7091 | 236.8356
604.4729 | 687.658 | 240.4381 | 232.7501 | 237.1737
605.4729 | 686.4379 | 240.769 | 233.3521 | 237.1083
606.4729 | 694.2351 | 241.1535 | 234.14 | 237.0398
607.4729 | 693.1059 | 240.7257 | 234.1727 | 236.9303
608.4729 | 691.0873 | 240.5882 | 234.5062 | 237.4404
609.4729 | 688.5013 | 240.8521 | 234.7713 | 236.9752
610.4729 | 686.621 | 241.4458 | 234.352 | 236.7514
611.4729 | 692.2369 | 241.8492 | 234.2272 | 236.9675
612.4729 | 688.0974 | 241.9806 | 234.7426 | 237.1046
613.4729 | 682.2162 | 242.6019 | 234.4642 | 237.3232
614.4885 | 681.3642 | 242.4965 | 234.7142 | 236.8814
615.4729 | 677.8464 | 242.9793 | 234.6352 | 236.7105
616.4729 | 675.2026 | 243.5208 | 234.7585 | 236.298
617.4729 | 673.7216 | 243.6822 | 234.687 | 236.874
618.4729 | 671.9683 | 243.7228 | 234.7714 | 236.6824
619.4729 | 671.4292 | 243.9562 | 235.368 | 237.2687
620.4729 | 668.9208 | 243.7358 | 235.3209 | 238.0806
621.4729 | 669.9634 | 243.7823 | 235.1438 | 238.0577
622.4729 | 668.4273 | 243.8556 | 235.8082 | 238.3897
623.4729 | 667.4765 | 243.5863 | 235.6958 | 238.4103
624.4729 | 666.7141 | 243.8359 | 235.823 | 238.489
625.4729 | 665.4724 | 243.8324 | 236.0699 | 238.4286
626.4729 | 666.1675 | 244.015 | 236.0337 | 238.2444
627.4729 | 666.0065 | 244.3673 | 235.8338 | 237.676
628.4729 | 665.1228 | 244.1759 | 235.6146 | 237.4165
629.4729 | 671.763 | 243.953 | 235.8627 | 237.555
630.4729 | 672.4167 | 244.4618 | 236.2271 | 238.3127
631.4729 | 671.2716 | 244.6915 | 236.5042 | 238.3744
632.4729 | 670.5025 | 244.7845 | 236.602 | 238.7259
633.4729 | 667.1184 | 245.2278 | 236.7265 | 238.4606
634.4729 | 667.609 | 244.9024 | 237.2656 | 238.786
635.4729 | 667.6475 | 244.9259 | 237.1105 | 238.9481
636.4729 | 666.655 | 244.7831 | 237.7138 | 238.7287
637.4729 | 668.018 | 245.1186 | 238.3972 | 240.0665
638.4729 | 666.1235 | 245.6708 | 238.1662 | 240.2436
639.4729 | 666.3293 | 245.7689 | 238.1349 | 239.6236
640.4729 | 664.3793 | 245.7376 | 238.0064 | 239.6866
641.4729 | 663.376 | 245.1672 | 238.4873 | 239.5986
642.4729 | 664.2621 | 244.7505 | 237.8579 | 239.5348
643.4729 | 664.3583 | 244.7609 | 237.5911 | 239.2505
644.5042 | 664.8356 | 244.4844 | 237.1834 | 239.3601
645.4729 | 664.0941 | 243.83 | 237.6767 | 239.638
646.4729 | 662.5704 | 243.5324 | 237.244 | 239.3942
647.4729 | 660.9268 | 242.9028 | 237.391 | 239.8042
648.4729 | 663.6627 | 243.2033 | 237.4054 | 240.0821
649.4729 | 664.2763 | 243.0287 | 237.4835 | 239.586
650.4729 | 663.4852 | 243.0537 | 237.1456 | 239.4551
651.4729 | 663.0732 | 243.5737 | 236.9314 | 239.3637
652.4729 | 661.649 | 243.5102 | 237.4821 | 240.098
653.4729 | 659.5086 | 243.1056 | 237.3419 | 239.8919
654.4729 | 655.9785 | 243.2018 | 237.6421 | 240.0467
655.4729 | 658.6496 | 243.1075 | 237.5174 | 239.4866
656.4729 | 657.2908 | 243.1515 | 237.5737 | 239.099
657.4729 | 655.5623 | 243.0992 | 237.8733 | 239.6441
658.4729 | 656.2388 | 243.845 | 238.0803 | 239.3332
659.4729 | 657.2508 | 244.2455 | 238.0408 | 239.9827
660.4729 | 657.5056 | 243.894 | 237.7873 | 240.0497
661.4729 | 657.3709 | 243.8283 | 237.8374 | 240.9183
662.4729 | 655.8071 | 244.0363 | 237.9677 | 241.2737
663.4729 | 655.6916 | 243.6477 | 238.4863 | 241.9699
664.4729 | 654.895 | 243.9143 | 238.4009 | 242.7737
665.4729 | 653.2472 | 244.0892 | 238.5188 | 242.9985
666.4729 | 652.295 | 243.6681 | 239.5331 | 243.3552
667.4729 | 652.1774 | 243.7507 | 239.9044 | 244.2444
668.4729 | 652.085 | 243.9638 | 240.6519 | 244.7331
669.4729 | 650.2032 | 244.4891 | 240.6235 | 245.2249
670.4729 | 652.2469 | 244.7836 | 240.7623 | 245.0833
671.4729 | 651.0029 | 244.4543 | 240.9251 | 245.34
672.4729 | 653.2947 | 244.6641 | 240.8646 | 245.7113
673.4729 | 650.8789 | 245.2128 | 241.9267 | 246.1334
674.4729 | 651.0549 | 245.7133 | 242.0508 | 246.514
675.4729 | 652.9178 | 245.896 | 242.6862 | 246.848
676.4729 | 654.521 | 246.0862 | 243.3357 | 247.702
677.4729 | 653.3591 | 245.6692 | 243.1805 | 248.0159
678.4729 | 652.8807 | 245.6184 | 243.6962 | 248.3902
679.4729 | 655.6875 | 245.3457 | 243.6485 | 248.5969
680.4729 | 656.9614 | 244.833 | 243.6716 | 248.7918
681.4729 | 658.9596 | 245.5811 | 244.1173 | 249.1827
682.4729 | 658.0144 | 245.6066 | 245.5736 | 249.3205
683.4729 | 659.4977 | 246.5837 | 245.7627 | 249.5168
684.4729 | 659.5385 | 246.6678 | 245.6177 | 249.3354
685.4729 | 658.5121 | 247.5312 | 245.8125 | 249.7884
686.4729 | 664.2396 | 247.7924 | 246.2444 | 249.8371
687.4729 | 663.6479 | 248.0638 | 247.1069 | 250.3932
688.4729 | 663.7931 | 248.6143 | 247.1862 | 250.3428
689.4729 | 665.1929 | 248.3247 | 246.9672 | 250.4623
690.4729 | 664.0897 | 248.2857 | 247.0979 | 250.3409
691.4729 | 662.4231 | 248.6032 | 247.8058 | 250.2576
692.4729 | 659.9403 | 249.1503 | 248.0568 | 250.188
693.4729 | 659.7251 | 249.1456 | 248.5563 | 250.0633
694.4729 | 659.5812 | 249.5428 | 248.4651 | 249.9566
695.4729 | 659.5686 | 249.8779 | 248.3812 | 250.1648
696.4729 | 660.0637 | 249.765 | 247.744 | 250.5514
697.4729 | 658.5172 | 249.4652 | 247.436 | 250.4589
698.4729 | 659.0802 | 249.1438 | 247.2636 | 250.4913
699.4729 | 657.9176 | 250.0011 | 247.383 | 250.4966
700.4729 | 658.3005 | 249.4766 | 246.578 | 250.5307
701.4729 | 657.792 | 249.3275 | 246.3856 | 250.854
702.4729 | 660.8966 | 249.1625 | 246.4767 | 250.8137
703.4729 | 660.4727 | 249.0656 | 246.6276 | 251.2425
704.4885 | 660.2966 | 248.7247 | 246.4191 | 251.8013
705.4729 | 658.5454 | 248.6979 | 246.4007 | 252.1858
706.4729 | 658.4107 | 248.9645 | 246.6272 | 252.1315
707.4729 | 659.246 | 249.5055 | 247.2653 | 252.1943
708.4729 | 659.1649 | 249.2493 | 247.0561 | 252.0231
709.4729 | 657.5229 | 249.1955 | 246.7453 | 251.6459
710.4729 | 657.155 | 249.4082 | 247.4633 | 252.0444
711.4729 | 656.7448 | 249.4312 | 247.861 | 252.3871
712.4729 | 655.6589 | 249.5849 | 247.7802 | 252.7898
713.4729 | 655.7795 | 250.0098 | 247.9234 | 253.3114
714.4729 | 656.0439 | 249.8559 | 247.9925 | 253.5667
715.4729 | 655.6038 | 250.2998 | 248.1847 | 253.6524
716.4729 | 657.3798 | 250.3227 | 248.0576 | 253.6793
717.4729 | 657.8213 | 250.8199 | 248.3934 | 254.0666
718.4729 | 659.9888 | 250.9837 | 248.8786 | 254.3065
719.4729 | 661.2724 | 251.8256 | 248.9663 | 253.5228
720.4729 | 663.6537 | 251.4333 | 248.7327 | 253.0519
721.4729 | 663.2149 | 251.9234 | 249.1073 | 253.378
722.4729 | 663.4843 | 252.3472 | 249.3197 | 254.1371
723.4729 | 664.6302 | 252.3788 | 249.7531 | 254.399
724.4729 | 666.4899 | 252.5856 | 250.6438 | 254.776
725.4729 | 666.0538 | 252.198 | 250.811 | 254.842
726.4729 | 665.1254 | 252.4728 | 250.9153 | 255.0961
727.4729 | 665.3691 | 253.3473 | 251.4284 | 255.4229
728.4729 | 663.3998 | 253.6808 | 251.8089 | 255.8578
729.4729 | 662.6407 | 253.5213 | 252.1324 | 255.6037
730.4729 | 661.7014 | 253.6466 | 252.0832 | 255.5177
731.4729 | 660.5201 | 253.9262 | 252.1711 | 256.3538
732.4729 | 660.6812 | 254.283 | 252.201 | 256.4383
733.4729 | 659.8118 | 254.2556 | 251.4864 | 256.6617
734.4885 | 659.4792 | 254.6726 | 251.7698 | 256.7603
735.4729 | 659.5261 | 254.961 | 251.9124 | 256.6842
736.4729 | 659.5244 | 254.4593 | 251.5928 | 256.8847
737.4729 | 662.6801 | 254.2784 | 251.6384 | 257.0754
738.4729 | 663.8625 | 254.3861 | 251.6301 | 256.6343
739.4729 | 664.7646 | 254.8357 | 251.5036 | 256.9078
740.4729 | 665.047 | 254.6023 | 251.9712 | 257.5519
741.4729 | 664.9848 | 254.5733 | 251.8904 | 257.7974
742.4729 | 663.2034 | 254.8021 | 252.4794 | 258.2976
743.4729 | 661.8008 | 255.1584 | 252.7525 | 258.775
744.4729 | 665.2823 | 255.1802 | 252.5681 | 259.0675
745.4729 | 664.3698 | 255.3044 | 252.3557 | 258.9407
746.4729 | 662.4843 | 255.4694 | 253.0358 | 258.9341
747.4885 | 660.9636 | 255.1303 | 253.0861 | 258.6663
748.4885 | 659.9413 | 255.043 | 253.1608 | 258.9254
749.4729 | 660.2619 | 255.6832 | 254.0678 | 258.9866
750.4729 | 658.1514 | 255.5616 | 253.9899 | 258.9171
751.4729 | 657.9266 | 255.5448 | 253.5818 | 259.4701
752.4729 | 657.844 | 255.3094 | 254.0908 | 259.2425
753.4729 | 658.1359 | 255.0796 | 253.686 | 259.2002
754.4729 | 657.8041 | 255.0293 | 254.5076 | 259.5586
755.4729 | 657.7605 | 255.3871 | 254.1169 | 259.8695
756.4729 | 657.6452 | 255.3032 | 254.7536 | 259.4028
757.4729 | 656.6933 | 255.4879 | 254.7229 | 259.3084
758.4729 | 658.5506 | 255.5082 | 254.6239 | 259.3967
759.4729 | 658.4579 | 255.4331 | 254.2317 | 258.9923
760.4729 | 658.3739 | 255.3898 | 253.8766 | 259.0716
761.4729 | 659.4118 | 255.9077 | 254.9887 | 260.1832
762.4729 | 660.636 | 256.1682 | 254.2418 | 259.3943
763.4729 | 660.8637 | 256.537 | 255.141 | 259.5397
764.4885 | 660.2157 | 256.5054 | 255.1721 | 260.0962
765.4729 | 659.4034 | 257.1341 | 255.3002 | 259.54
766.4729 | 657.7623 | 257.301 | 255.5865 | 259.7524
767.4729 | 660.4298 | 257.1022 | 256.1167 | 259.7606
768.4729 | 659.5292 | 257.3276 | 255.7657 | 259.8127
769.4729 | 659.0294 | 257.522 | 255.1002 | 259.8424
770.4729 | 658.2901 | 257.997 | 254.8391 | 259.5932
771.4729 | 657.4475 | 258.2224 | 254.4463 | 259.7817
772.4729 | 656.933 | 257.9463 | 254.2003 | 259.7827
773.4729 | 657.4325 | 257.72 | 254.4375 | 260.0966
774.4729 | 656.5942 | 257.3388 | 254.223 | 259.7829
775.4729 | 656.8467 | 257.1822 | 254.3231 | 259.364
776.4729 | 657.6886 | 257.2077 | 253.8111 | 259.1192
777.4729 | 656.9941 | 257.0681 | 254.554 | 258.9129
778.4729 | 656.1658 | 256.9772 | 254.2481 | 258.7801
779.4729 | 654.6209 | 256.8082 | 253.613 | 258.6796
780.4729 | 655.7718 | 256.7002 | 254.5332 | 259.2763
781.4729 | 656.0935 | 256.3922 | 254.1207 | 259.2693
782.4729 | 657.2911 | 256.5964 | 254.221 | 259.8111
783.4729 | 657.0166 | 256.2591 | 253.9671 | 260.2794
784.4729 | 656.2068 | 256.1795 | 253.4378 | 259.4867
785.4729 | 656.6632 | 256.145 | 253.9175 | 259.8491
786.4729 | 656.8612 | 255.9216 | 254.48 | 259.8248
787.4729 | 656.9305 | 255.8841 | 254.7168 | 259.5914
788.4729 | 657.4921 | 255.9295 | 255.074 | 260.1828
789.4729 | 656.5352 | 256.0742 | 255.4518 | 260.6165
790.4729 | 655.8978 | 256.3881 | 255.2335 | 261.1256
791.4729 | 654.3935 | 256.4401 | 254.9284 | 261.6065
792.4729 | 653.7814 | 256.0542 | 255.4301 | 261.945
793.4729 | 652.5828 | 256.4459 | 255.8524 | 261.9986
794.4729 | 651.9694 | 256.6201 | 255.9866 | 261.7134
795.4729 | 651.6999 | 256.4487 | 255.6926 | 261.9247
796.4729 | 652.3912 | 256.3742 | 255.6876 | 262.1857
797.4729 | 653.0692 | 256.1035 | 255.5724 | 262.2212
798.4729 | 653.1457 | 256.2928 | 255.2739 | 262.4194
799.4729 | 656.0457 | 256.2455 | 255.2898 | 262.4901
800.4729 | 655.8976 | 256.5448 | 255.7057 | 262.7864
801.4729 | 655.4253 | 256.84 | 255.4754 | 262.856
802.4729 | 655.6679 | 257.1861 | 255.6728 | 262.9593
803.4729 | 656.5467 | 257.2171 | 256.2456 | 262.9573
804.4729 | 657.3588 | 257.1073 | 256.5826 | 263.4649
805.4729 | 656.3381 | 257.1604 | 256.7215 | 263.5251
806.4729 | 654.8127 | 257.5404 | 256.9134 | 263.435
807.4729 | 654.1231 | 257.8984 | 256.937 | 262.8844
808.4729 | 654.2735 | 257.6028 | 257.13 | 263.1043
809.4729 | 652.6532 | 257.6196 | 256.948 | 263.0635
810.4729 | 652.9805 | 257.6707 | 257.0444 | 262.4704
811.4729 | 652.3118 | 258.221 | 257.7944 | 261.9977
812.4729 | 652.0397 | 258.0217 | 258.0161 | 262.0703
813.4729 | 656.6227 | 258.0214 | 257.7993 | 262.2394
814.4729 | 655.5701 | 258.3058 | 257.2692 | 261.8609
815.4729 | 655.6035 | 258.5157 | 257.1623 | 261.8872
816.4729 | 655.9367 | 258.3845 | 257.1087 | 261.482
817.4729 | 655.3208 | 258.4662 | 257.1164 | 261.5872
818.4729 | 655.1162 | 258.6015 | 257.2557 | 261.7794
819.4729 | 655.1367 | 258.7125 | 257.365 | 262.4312
820.4729 | 655.8862 | 259.2377 | 257.3685 | 262.9075
821.4729 | 656.8709 | 260.5548 | 257.2336 | 263.3863
822.4729 | 655.9696 | 260.8349 | 257.5512 | 263.4335
823.4729 | 656.0415 | 260.7077 | 257.4739 | 263.915
824.4729 | 655.6401 | 260.7758 | 257.6054 | 264.1636
825.4729 | 655.9468 | 260.9354 | 257.6258 | 263.9492
826.4729 | 656.6381 | 260.9878 | 257.8992 | 263.5989
827.4729 | 658.4473 | 260.5285 | 257.8649 | 264.1478
828.4729 | 659.2227 | 260.0481 | 257.7006 | 264.5569
829.4729 | 661.4834 | 260.0219 | 258.0856 | 265.1118
830.4729 | 661.3168 | 260.1409 | 257.8379 | 265.4599
831.4729 | 662.2062 | 260.4699 | 257.5759 | 265.4824
832.4729 | 663.0796 | 260.3029 | 257.1846 | 265.9892
833.4729 | 661.958 | 260.5246 | 256.8444 | 265.91
834.4729 | 661.8099 | 260.8393 | 256.9037 | 265.4088
835.4729 | 662.1714 | 261.0428 | 257.2258 | 265.9153
836.4729 | 663.3746 | 261.1416 | 257.7783 | 265.9703
837.4729 | 664.3198 | 261.7344 | 258.4142 | 266.3331
838.4729 | 664.7605 | 261.3903 | 258.3757 | 266.1283
839.4729 | 665.0423 | 262.0066 | 258.4855 | 266.1012
840.4729 | 666.3285 | 262.1809 | 258.4224 | 266.4084
841.4729 | 666.9154 | 262.6101 | 259.4031 | 266.1159
842.4729 | 666.9296 | 262.5057 | 259.2149 | 266.205
843.4729 | 665.2905 | 262.5648 | 259.2247 | 266.4512
844.4729 | 665.5514 | 262.7735 | 259.3391 | 265.9529
845.4729 | 664.5801 | 262.9485 | 259.7563 | 266.2929
846.4729 | 663.0921 | 262.7667 | 260.1442 | 265.8983
847.4729 | 663.0839 | 262.77 | 260.2761 | 266.1723
848.4729 | 663.904 | 262.4887 | 260.3956 | 266.0553
849.4729 | 666.7416 | 262.9881 | 260.6973 | 266.5006
850.4729 | 668.5289 | 263.1322 | 260.7862 | 266.4035
851.4729 | 669.7025 | 263.7261 | 260.816 | 266.3649
852.4729 | 669.501 | 264.4059 | 261.1422 | 266.1044
853.4729 | 671.0154 | 264.4363 | 261.0608 | 265.8734
854.4885 | 669.0918 | 265.0462 | 261.7211 | 265.4888
855.4729 | 670.496 | 265.5667 | 262.6201 | 265.8788
856.4729 | 674.7022 | 265.5574 | 261.9704 | 265.9957
857.4729 | 674.4831 | 265.2921 | 262.6254 | 266.4051
858.4729 | 674.3755 | 265.3987 | 262.6778 | 266.5689
859.4729 | 674.1477 | 265.697 | 262.4407 | 266.3828
860.4729 | 673.3239 | 265.2695 | 262.5417 | 266.4605
861.4729 | 675.8869 | 265.2475 | 262.8863 | 266.0228
862.4729 | 676.988 | 265.6554 | 263.0655 | 266.6705
863.4729 | 676.2602 | 265.1585 | 263.2664 | 266.6375
864.4729 | 675.6007 | 265.2774 | 262.9084 | 266.008
865.4729 | 674.0455 | 265.2028 | 262.9495 | 265.9775
866.4729 | 675.5906 | 265.1911 | 263.0188 | 266.3221
867.4729 | 675.1482 | 265.0717 | 263.3423 | 266.5782
868.4729 | 673.6353 | 264.9572 | 263.1594 | 266.7987
869.4729 | 673.7045 | 264.9673 | 263.233 | 266.2304
870.4729 | 676.0604 | 264.7868 | 263.3433 | 266.3638
871.4729 | 678.9012 | 264.5723 | 262.9786 | 266.5763
872.4729 | 679.1975 | 264.5951 | 262.5718 | 266.0994
873.4729 | 680.3067 | 264.3583 | 262.4566 | 266.1413
874.4729 | 682.1825 | 264.586 | 262.2974 | 265.9227
875.4729 | 684.1298 | 264.2743 | 262.2308 | 266.0009
876.4729 | 685.5518 | 263.7736 | 261.7125 | 266.2848
877.4729 | 686.2085 | 263.3776 | 261.9839 | 266.2338
878.4729 | 686.4584 | 263.3493 | 261.7359 | 265.7419
879.4729 | 685.7011 | 263.2458 | 261.5943 | 265.3496
880.4729 | 684.6215 | 263.4084 | 262.5741 | 265.9435
881.4729 | 685.4823 | 263.7489 | 262.4795 | 265.9499
882.4729 | 685.5747 | 263.8283 | 262.9737 | 266.1098
883.4729 | 685.6021 | 263.6409 | 262.9727 | 266.2716
884.4729 | 686.9716 | 264.5197 | 263.6567 | 266.6412
885.4729 | 687.6723 | 264.4612 | 264.1785 | 266.9902
886.4729 | 688.9885 | 264.6261 | 263.9373 | 267.3402
887.4729 | 688.8131 | 264.6021 | 263.7216 | 267.092
888.4729 | 688.4675 | 264.1027 | 263.5769 | 267.094
889.4729 | 687.2353 | 264.3674 | 263.5079 | 267.5489
890.4729 | 684.9892 | 264.3692 | 263.4807 | 267.2846
891.4729 | 684.7624 | 264.9024 | 263.2289 | 266.9819
892.4729 | 685.3427 | 265.1428 | 263.5713 | 267.0325
893.4729 | 685.9105 | 264.9415 | 263.5958 | 266.9846
894.4729 | 684.8419 | 264.8488 | 263.558 | 267.1324
895.4729 | 684.8362 | 264.607 | 263.3588 | 267.2425
896.4729 | 685.2447 | 264.7921 | 263.5154 | 267.832
897.4729 | 688.5222 | 264.6237 | 263.5742 | 267.6335
898.4729 | 689.3859 | 264.5765 | 263.42 | 267.754
899.4729 | 691.1273 | 264.4717 | 263.2213 | 267.7987
900.4729 | 691.2709 | 264.1544 | 262.9966 | 267.8919
901.4729 | 692.5516 | 264.1871 | 263.0701 | 268.1033
902.4729 | 693.6181 | 263.712 | 264.0973 | 268.631
903.4729 | 695.1993 | 263.7632 | 264.0051 | 268.9652
904.4729 | 695.7605 | 263.8941 | 263.7768 | 269.1064
905.4729 | 695.8463 | 263.9216 | 263.8771 | 269.4749
906.4729 | 693.5272 | 264.5015 | 263.9281 | 269.6676
907.4729 | 693.2223 | 264.1855 | 263.7935 | 269.8676
908.4729 | 693.9467 | 264.0345 | 263.7452 | 270.0695
909.4729 | 693.308 | 263.9131 | 263.8191 | 270.1549
910.4729 | 694.7491 | 263.698 | 263.5955 | 269.9631
911.4729 | 694.0114 | 263.7298 | 263.3612 | 270.0117
912.4729 | 695.0058 | 264.2447 | 263.5193 | 270.2761
913.4729 | 695.1888 | 264.4336 | 264.1001 | 270.7718
914.4729 | 695.4437 | 264.7284 | 263.8848 | 271.1642
915.4729 | 695.1045 | 265.018 | 264.2058 | 271.3253
916.4729 | 694.4719 | 264.8557 | 263.9146 | 271.3083
917.4729 | 694.1194 | 265.3563 | 264.5646 | 270.8475
918.4729 | 694.2539 | 265.4661 | 265.0425 | 271.6306
919.4729 | 692.2626 | 265.8665 | 265.0786 | 271.9506
920.4729 | 691.8658 | 266.1809 | 264.9882 | 272.0314
921.4729 | 691.2449 | 266.0032 | 265.2286 | 272.3651
922.4729 | 692.2476 | 265.9173 | 265.225 | 271.9977
923.4729 | 694.7958 | 265.8835 | 265.0678 | 272.2899
924.4729 | 696.7372 | 265.3857 | 264.7789 | 272.0286
925.4729 | 695.5586 | 265.1793 | 264.9091 | 271.8356
926.4729 | 695.349 | 265.0144 | 264.6428 | 271.5851
927.4729 | 696.6272 | 265.1218 | 264.3918 | 271.0423
928.4729 | 698.6544 | 264.7644 | 264.4113 | 270.9921
929.4729 | 701.3482 | 264.4205 | 264.2926 | 271.456
930.4729 | 701.9967 | 264.2875 | 264.4137 | 271.8291
931.4729 | 704.5175 | 264.4172 | 265.1447 | 272.1023
932.4729 | 704.1841 | 264.4736 | 265.5457 | 272.351
933.4729 | 706.5912 | 264.4617 | 265.6652 | 272.6838
934.4729 | 705.4651 | 264.5748 | 265.346 | 273.0183
935.4729 | 704.9376 | 264.6568 | 265.005 | 272.1269
936.4729 | 704.8894 | 264.893 | 265.2822 | 272.295
937.4729 | 706.7839 | 264.9245 | 265.5186 | 272.0484
938.4729 | 708.9852 | 265.1183 | 265.774 | 271.1152
939.4729 | 708.5894 | 265.1067 | 265.6972 | 271.453
940.4729 | 708.4069 | 265.3381 | 265.792 | 271.1736
941.4729 | 708.4866 | 265.5137 | 266.1383 | 272.0349
942.4729 | 707.7876 | 265.6211 | 266.1124 | 271.9071
943.4729 | 707.5051 | 265.8836 | 266.6789 | 271.5976
944.4729 | 709.0366 | 266.5598 | 267.2599 | 271.6363
945.4729 | 708.9297 | 266.3805 | 267.5196 | 271.6008
946.4729 | 710.8235 | 266.4325 | 267.8052 | 271.75
947.4729 | 710.5147 | 266.5453 | 267.7662 | 271.3822
948.4729 | 710.2621 | 266.6496 | 268.4157 | 271.2625
949.4729 | 709.5262 | 267.0136 | 268.4221 | 271.5071
950.4729 | 709.2478 | 267.0459 | 267.7159 | 271.5693
951.4729 | 709.0753 | 267.1785 | 267.647 | 271.4199
952.4729 | 710.8068 | 267.1993 | 267.6409 | 271.3487
953.4729 | 708.9765 | 267.4914 | 267.538 | 271.3027
954.4729 | 708.7192 | 267.8836 | 267.3213 | 271.1531
955.4729 | 709.7575 | 268.0979 | 266.9872 | 271.7396
956.4729 | 710.7843 | 268.4676 | 266.8919 | 272.3016
957.4729 | 711.2022 | 268.5063 | 267.3534 | 272.7307
958.4729 | 711.3646 | 268.2634 | 267.6688 | 273.108
959.4729 | 711.6433 | 267.8418 | 266.9559 | 272.8388
960.4729 | 711.0031 | 267.5856 | 266.8399 | 272.7267
961.4729 | 713.0367 | 267.0848 | 266.9891 | 272.7284
962.4729 | 714.8985 | 267.1662 | 266.9535 | 272.7631
963.4729 | 716.5672 | 267.0236 | 266.8904 | 272.4559
964.4729 | 716.2793 | 266.481 | 266.3256 | 272.222
965.4729 | 714.6164 | 266.5496 | 266.131 | 271.9263
966.4729 | 714.5689 | 266.4149 | 266.6647 | 271.9834
967.4729 | 713.2704 | 266.839 | 266.5647 | 272.2995
968.4729 | 712.6391 | 266.8437 | 266.865 | 272.2264
969.4729 | 712.7633 | 267.1102 | 266.8694 | 272.4389
970.4729 | 713.095 | 268.0269 | 267.3908 | 273.01
971.4729 | 713.4067 | 268.0268 | 267.2485 | 272.8704
972.4729 | 714.5821 | 268.1113 | 267.2135 | 273.1198
973.4729 | 716.2973 | 268.0863 | 267.5261 | 273.2414
974.4729 | 716.7165 | 267.9574 | 267.1679 | 273.0673
975.4729 | 719.304 | 267.984 | 266.9505 | 272.9352
976.4729 | 720.6025 | 267.6756 | 266.8933 | 272.9634
977.4729 | 723.5978 | 267.4307 | 267.1725 | 273.4249
978.4729 | 723.2277 | 267.2901 | 267.0723 | 273.242
979.4729 | 722.7237 | 267.5056 | 267.2219 | 273.3471
980.4729 | 724.7681 | 267.1825 | 267.0884 | 272.9838
981.4729 | 725.2703 | 267.9383 | 267.4694 | 272.8991
982.4729 | 728.3426 | 267.8495 | 267.6553 | 273.0892
983.4729 | 732.0459 | 267.46 | 267.9666 | 273.489
984.4729 | 734.2214 | 267.754 | 267.716 | 273.5525
985.4729 | 734.4631 | 267.7756 | 267.3978 | 273.4046
986.4729 | 736.077 | 268.0646 | 267.643 | 273.7989
987.4729 | 738.0909 | 268.0302 | 267.7762 | 273.7927
988.4729 | 739.6147 | 268.4922 | 268.2253 | 274.7343
989.4729 | 740.6886 | 269.1987 | 268.442 | 274.8537
990.4729 | 740.6037 | 269.8318 | 268.487 | 274.7579
991.4729 | 738.7263 | 270.3543 | 268.5826 | 274.773
992.4729 | 736.8766 | 270.509 | 269.1953 | 274.8109
993.4729 | 736.3017 | 270.382 | 269.2325 | 275.1327
994.4729 | 737.9676 | 270.4738 | 269.4871 | 275.6124
995.4729 | 735.714 | 270.4826 | 270.0848 | 276.0503
996.4729 | 736.0848 | 270.4411 | 270.1047 | 275.6242
997.4729 | 735.8865 | 270.549 | 270.5051 | 275.9675
998.4729 | 736.3674 | 270.6642 | 270.3721 | 275.8091
999.4729 | 735.7473 | 270.4479 | 270.1954 | 275.9817
1000.4729 | 737.5018 | 270.3516 | 270.2368 | 276.3069
1001.4729 | 739.7858 | 270.5572 | 270.6946 | 276.2208
1002.4729 | 739.6747 | 270.4735 | 271.2816 | 276.5434
1003.4729 | 739.2596 | 270.3547 | 270.7899 | 276.326
1004.4729 | 739.5018 | 270.2477 | 270.8693 | 276.8162
1005.4729 | 739.927 | 269.9966 | 271.1551 | 276.2618
1006.4729 | 738.9281 | 269.9767 | 270.8144 | 276.1077
1007.4729 | 737.3001 | 269.8622 | 270.6049 | 275.7543
1008.4729 | 736.7508 | 269.9042 | 270.3477 | 275.8775
1009.4729 | 736.6861 | 270.3473 | 270.841 | 276.3669
1010.4729 | 737.8481 | 270.001 | 270.7043 | 276.2936
1011.4729 | 738.5158 | 269.8595 | 270.5818 | 276.1602
1012.4729 | 739.3806 | 269.8818 | 270.9663 | 276.2325
1013.4729 | 739.5423 | 269.7437 | 270.9222 | 276.1961
1014.4729 | 742.3561 | 270.0133 | 271.0923 | 276.6493
1015.4729 | 744.7436 | 270.1081 | 270.9555 | 276.9395
1016.4729 | 742.757 | 270.3379 | 270.7795 | 276.6119
1017.4729 | 740.8282 | 270.7033 | 271.2514 | 276.2739
1018.4729 | 741.5636 | 270.9101 | 271.2429 | 276.4355
1019.4729 | 741.2948 | 270.414 | 271.0346 | 276.1286
1020.4729 | 740.7492 | 270.4712 | 271.4007 | 276.2965
1021.4729 | 740.5136 | 270.263 | 271.2537 | 276.8241
1022.4729 | 742.6682 | 270.2955 | 271.3213 | 276.7229
1023.4729 | 744.0751 | 270.5083 | 272.1676 | 276.3636
1024.4729 | 747.5634 | 270.5568 | 272.2431 | 277.0279
1025.4729 | 752.4343 | 270.3783 | 272.2782 | 276.932
1026.4729 | 752.5163 | 270.325 | 271.8542 | 276.6127
1027.4729 | 751.1524 | 270.755 | 271.797 | 276.5614
1028.4729 | 753.3893 | 270.5315 | 271.8834 | 276.6405
1029.4729 | 755.2757 | 270.7186 | 271.7485 | 276.7419
1030.4729 | 756.7109 | 271.1765 | 272.2962 | 277.2366
1031.4729 | 759.6331 | 270.9228 | 272.0929 | 277.7064
1032.4729 | 759.865 | 271.077 | 272.3688 | 277.1026
1033.4729 | 757.1036 | 270.996 | 272.5966 | 276.9887
1034.4729 | 760.6821 | 270.6009 | 273.1101 | 277.2741
1035.4729 | 761.0512 | 270.3255 | 272.8377 | 276.6304
1036.4729 | 759.6587 | 270.8158 | 273.0098 | 276.2702
1037.4729 | 762.0242 | 270.8691 | 272.8422 | 275.5711
1038.4729 | 763.9842 | 271.1173 | 272.9747 | 275.3051
1039.4729 | 766.0448 | 271.2722 | 272.7663 | 275.8313
1040.4729 | 762.8901 | 271.4597 | 273.3053 | 275.8152
1041.4729 | 762.3505 | 271.8028 | 273.0315 | 275.4808
1042.4729 | 761.0458 | 271.8696 | 273.3237 | 276.1597
1043.4729 | 761.8496 | 271.9512 | 273.0613 | 275.7403
1044.4729 | 763.7691 | 271.6412 | 273.1791 | 275.9345
1045.4729 | 765.3979 | 271.5702 | 272.8989 | 275.9906
1046.4729 | 764.0374 | 271.9871 | 272.9197 | 276.2524
1047.4729 | 768.4863 | 272.0913 | 273.4276 | 276.8957
1048.4729 | 763.8091 | 272.4124 | 273.2209 | 276.52
1049.4729 | 761.5366 | 272.1754 | 273.053 | 276.4548
1050.4729 | 762.0338 | 272.4396 | 273.0446 | 276.5835
1051.4729 | 763.4131 | 272.5434 | 273.5578 | 276.864
1052.4729 | 762.812 | 272.3608 | 272.892 | 276.9685
1053.4729 | 763.7425 | 271.8866 | 272.9525 | 276.7335
1054.4729 | 763.7517 | 271.4988 | 273.0975 | 276.9449
1055.4729 | 764.2966 | 271.2963 | 272.5955 | 276.9997
1056.4729 | 766.3482 | 271.8096 | 272.9862 | 277.0476
1057.4729 | 764.3721 | 271.4609 | 273.0023 | 277.2023
1058.4729 | 763.5841 | 271.3395 | 272.7492 | 277.3344
1059.4729 | 768.3964 | 271.7191 | 273.1534 | 277.3277
1060.4729 | 774.6278 | 271.4063 | 272.9981 | 276.9804
1061.4729 | 770.4641 | 271.3644 | 272.5225 | 276.8568
1062.4729 | 771.4153 | 271.087 | 272.6554 | 276.7685
1063.4729 | 772.4262 | 270.7555 | 272.166 | 277.0197
1064.4729 | 770.9043 | 271.0868 | 272.3862 | 276.9324
1065.4729 | 775.4888 | 271.4697 | 271.9419 | 277.3462
1066.4729 | 777.7974 | 271.6928 | 271.8691 | 277.7588
1067.4729 | 784.3395 | 271.3844 | 271.9889 | 278.0178
1068.4729 | 788.3351 | 271.5989 | 272.0075 | 278.1704
1069.4729 | 787.2065 | 271.4751 | 271.8019 | 277.7335
1070.4729 | 785.0025 | 271.9913 | 272.0189 | 277.9148
1071.4729 | 786.1393 | 272.3784 | 271.9529 | 277.0381
1072.4729 | 782.7692 | 272.9103 | 272.5337 | 276.6182
1073.4729 | 782.9222 | 272.8193 | 272.2959 | 276.9049
1074.4729 | 777.6316 | 273.7445 | 272.468 | 277.3597
1075.4729 | 776.4996 | 273.7939 | 272.9294 | 277.9507
1076.4729 | 778.3891 | 274.2169 | 272.9474 | 278.5748
1077.4729 | 782.1149 | 274.8679 | 273.9255 | 279.4662
1078.4729 | 781.0676 | 275.3866 | 274.3867 | 279.7454
1079.4729 | 781.422 | 275.8136 | 275.2454 | 280.568
1080.4729 | 778.4239 | 276.2109 | 275.1182 | 280.8088
1081.4729 | 781.5132 | 275.9422 | 275.4704 | 281.3251
1082.4729 | 781.3896 | 276.2333 | 275.603 | 281.939
1083.4885 | 785.3319 | 276.0489 | 275.9732 | 282.6299
1084.4729 | 786.4818 | 276.3699 | 276.267 | 282.6758
1085.4729 | 791.5788 | 276.505 | 276.7648 | 282.708
1086.4729 | 793.7757 | 276.9873 | 277.2944 | 283.43
1087.4729 | 797.4076 | 278.0198 | 277.5243 | 282.9834
1088.4729 | 800.4391 | 278.4329 | 277.5247 | 283.1569
1089.4729 | 799.5588 | 278.1909 | 277.9329 | 283.3615
1090.4729 | 799.5871 | 278.607 | 278.7217 | 283.8036
1091.4729 | 807.3377 | 278.3558 | 279.0095 | 284.3707
1092.4729 | 807.5859 | 278.512 | 279.7345 | 285.0686
1093.4729 | 809.9364 | 278.7736 | 279.4725 | 284.6113
1094.4729 | 809.9892 | 279.0866 | 279.523 | 285.0866
1095.4729 | 810.5132 | 279.4353 | 279.6947 | 285.0067
1096.4729 | 814.8595 | 279.6738 | 279.6063 | 284.6581
1097.4729 | 812.3079 | 280.0932 | 279.8871 | 284.9622
1098.4729 | 811.0367 | 280.8452 | 280.163 | 285.6214
1099.4729 | 815.4888 | 281.2262 | 280.6915 | 286.5915
1100.4729 | 813.9423 | 282.2707 | 280.8457 | 286.9551
1101.4729 | 813.4676 | 282.7691 | 281.303 | 286.8482
1102.4729 | 810.3064 | 282.6991 | 281.2349 | 286.9949
1103.4729 | 807.8034 | 282.8092 | 281.2688 | 287.6915
1104.4729 | 808.0967 | 283.44 | 281.9854 | 288.3932
1105.4729 | 808.4112 | 283.4168 | 282.1726 | 288.4495
1106.4729 | 807.3846 | 283.9198 | 281.827 | 288.1367
1107.4729 | 808.8533 | 283.5418 | 281.6121 | 287.9017
1108.4729 | 809.7938 | 283.7721 | 282.5409 | 288.0897
1109.4729 | 811.6996 | 284.2774 | 283.2343 | 288.386
1110.4729 | 809.3099 | 284.7468 | 283.565 | 288.8725
1111.4729 | 811.2683 | 284.8239 | 284.1098 | 289.767
1112.4729 | 810.0588 | 285.0284 | 283.8996 | 289.581
1113.4729 | 811.6457 | 284.864 | 284.3213 | 290.3294
1114.4729 | 811.8992 | 284.8796 | 284.4467 | 290.1463
1115.4729 | 815.1198 | 285.6323 | 284.7734 | 290.5665
1116.4729 | 813.7373 | 285.8094 | 284.3218 | 290.6641
1117.4729 | 815.1665 | 285.602 | 283.999 | 290.8578
1118.4729 | 812.5904 | 285.6672 | 284.2779 | 291.276
1119.4729 | 812.1361 | 285.7536 | 284.1453 | 291.3717
1120.4729 | 824.7406 | 285.7954 | 284.3173 | 291.8718
1121.4729 | 834.2485 | 285.6448 | 285.5677 | 292.493
1122.4729 | 841.3598 | 285.9989 | 286.8814 | 293.3334
1123.4729 | 830.0088 | 286.2159 | 286.7092 | 293.5852
1124.4729 | 821.7268 | 286.6795 | 287.0902 | 294.4577
1125.4729 | 817.9071 | 287.8729 | 287.2635 | 294.8032
1126.4729 | 815.2463 | 288.2735 | 286.9512 | 294.4214
1127.4729 | 814.045 | 288.2508 | 286.9214 | 295.3947
1128.4729 | 812.4572 | 288.8425 | 287.4931 | 295.5762
1129.4729 | 810.7618 | 289.0321 | 287.8755 | 295.9166
1130.4729 | 809.7588 | 290.1053 | 288.9437 | 295.9311
1131.4729 | 808.5981 | 290.8331 | 289.074 | 296.3192
1132.4729 | 808.8385 | 291.1197 | 289.5188 | 297.2687
1133.4729 | 807.275 | 291.4896 | 290.0554 | 297.5283
1134.4729 | 805.6445 | 291.9327 | 291.0572 | 297.9994
1135.4729 | 805.9175 | 292.0313 | 291.073 | 298.0872
1136.4729 | 807.061 | 291.7729 | 291.648 | 298.4781
1137.4729 | 807.7259 | 291.4101 | 291.7676 | 298.609
1138.4729 | 808.0903 | 291.4577 | 291.6313 | 298.5331
1139.4729 | 807.7834 | 291.0044 | 291.8591 | 297.7215
1140.4729 | 809.6215 | 290.6316 | 292.3615 | 298.6297
1141.4729 | 809.7076 | 291.243 | 291.7193 | 298.4885
1142.4729 | 807.4447 | 292.0533 | 291.5508 | 299.2606
1143.4729 | 806.9056 | 292.1059 | 290.9485 | 299.9203
1144.4729 | 805.6345 | 292.0991 | 290.7384 | 299.8022
1145.4729 | 807.4826 | 292.1247 | 291.3726 | 299.8894
1146.4729 | 806.8285 | 292.2967 | 291.3845 | 300.0811
1147.4729 | 807.8238 | 292.195 | 291.7346 | 300.1105
1148.4729 | 808.1301 | 292.0602 | 292.5892 | 300.7189
1149.4729 | 808.9846 | 291.9881 | 293.1223 | 300.4638
1150.4729 | 808.9451 | 292.3012 | 292.8803 | 301.3147
1151.4729 | 808.0492 | 292.4803 | 292.9009 | 301.0552
1152.4729 | 808.2493 | 292.7672 | 293.1329 | 301.6992
1153.4729 | 808.2967 | 292.5102 | 293.0179 | 301.5717
1154.4729 | 808.3128 | 292.8858 | 293.5112 | 302.6244
1155.4729 | 807.7023 | 293.0954 | 294.3547 | 303.0263
1156.4729 | 808.5819 | 293.2412 | 294.9347 | 304.4853
1157.4729 | 809.4849 | 293.3454 | 295.6175 | 305.0967
1158.4729 | 809.1791 | 293.8759 | 296.3027 | 305.0532
1159.4729 | 810.5736 | 294.4137 | 296.1578 | 305.1299
1160.4729 | 812.5262 | 294.2634 | 295.8855 | 304.9963
1161.4729 | 813.2237 | 294.7073 | 295.824 | 305.12
1162.4729 | 815.2769 | 294.4327 | 295.9034 | 306.1766
1163.4729 | 823.1355 | 294.8493 | 296.5967 | 306.7489
1164.4729 | 824.7152 | 295.5968 | 297.7673 | 307.4158
1165.4729 | 822.9638 | 296.1299 | 299.0947 | 308.0384
1166.4729 | 819.7143 | 295.9268 | 299.5154 | 308.5369
1167.4729 | 818.4497 | 296.8806 | 299.1476 | 309.1884
1168.4729 | 817.2442 | 297.1664 | 299.3393 | 309.5245
1169.4729 | 816.1223 | 297.992 | 299.6377 | 310.0642
1170.4729 | 815.236 | 298.1237 | 299.7139 | 310.4272
1171.4729 | 815.1619 | 297.9871 | 300.1377 | 310.6436
1172.4729 | 813.5234 | 298.2077 | 301.4491 | 311.5538
1173.4729 | 813.9788 | 298.9141 | 301.6895 | 312.1832
1174.4729 | 814.3821 | 300.2811 | 303.2126 | 313.5543
1175.4729 | 816.0591 | 300.0809 | 304.2332 | 313.7272
1176.4729 | 818.8968 | 300.8861 | 304.765 | 313.7181
1177.4729 | 818.3417 | 301.2894 | 305.238 | 314.2556
1178.4729 | 819.7454 | 301.5402 | 304.9521 | 314.2583
1179.4729 | 819.7074 | 302.1368 | 305.4029 | 314.9683
1180.4729 | 822.1951 | 302.0713 | 305.5 | 315.0785
1181.4729 | 823.5512 | 301.8423 | 305.2472 | 315.0627
1182.4729 | 821.3112 | 302.0974 | 305.7438 | 315.1656
1183.4729 | 818.4258 | 302.6323 | 306.6458 | 315.7462
1184.4729 | 819.4796 | 303.102 | 306.8832 | 316.0993
1185.4729 | 818.1136 | 303.5496 | 307.0205 | 316.0806
1186.4729 | 819.1697 | 304.1424 | 307.6236 | 316.5144
1187.4729 | 819.7572 | 304.2587 | 308.2536 | 316.2783
1188.4729 | 819.8935 | 304.1955 | 307.6761 | 315.8797
1189.4729 | 820.334 | 304.377 | 307.9935 | 316.3283
1190.4729 | 823.214 | 304.1719 | 308.2593 | 316.9705
1191.4729 | 825.2528 | 304.448 | 307.8312 | 316.7966
1192.4729 | 826.1427 | 304.6014 | 308.5924 | 317.6801
1193.4729 | 831.6878 | 305.7051 | 309.1718 | 318.8361
1194.4729 | 833.3356 | 305.8475 | 309.8241 | 319.6989
1195.4729 | 834.3196 | 306.5558 | 310.1224 | 320.507
1196.4729 | 833.5485 | 307.186 | 310.6009 | 321.0696
1197.4729 | 832.3653 | 307.4388 | 310.817 | 321.3695
1198.4729 | 831.7601 | 307.8244 | 311.4325 | 321.5221
1199.4729 | 832.3206 | 307.8035 | 311.4559 | 322.2284
1200.4729 | 833.4887 | 308.1953 | 311.1727 | 322.0168
1201.4729 | 833.2216 | 308.0048 | 311.3013 | 322.8056
1202.4729 | 830.4797 | 308.5806 | 311.2359 | 322.4373
1203.4729 | 829.8976 | 308.794 | 311.8955 | 322.3119
1204.4729 | 830.0351 | 308.9576 | 311.6771 | 322.0596
1205.4729 | 830.7997 | 308.8524 | 311.1455 | 321.6663
1206.4729 | 829.0392 | 308.4128 | 311.8201 | 321.4026
1207.4729 | 830.7465 | 308.0279 | 311.4769 | 321.248
1208.4729 | 830.5106 | 308.0639 | 311.3767 | 321.8049
1209.4729 | 830.9744 | 308.3799 | 312.1066 | 321.6006
1210.4729 | 829.5854 | 308.9944 | 312.3815 | 321.792
1211.4729 | 828.5634 | 309.5806 | 312.1716 | 321.8877
1212.4729 | 828.1157 | 309.6548 | 312.3055 | 322.1609
1213.4729 | 826.0751 | 309.339 | 312.5336 | 321.9724
1214.4729 | 824.2469 | 309.6497 | 312.8833 | 321.4589
1215.4729 | 823.0761 | 310.1515 | 312.8976 | 321.4129
1216.4729 | 822.8698 | 310.5083 | 313.0553 | 321.8523
1217.4729 | 823.5695 | 310.6839 | 312.892 | 322.203
1218.4729 | 824.0554 | 310.5935 | 313.1661 | 322.5598
1219.4729 | 825.6214 | 310.8552 | 314.1322 | 322.9569
1220.4729 | 825.6707 | 310.6964 | 314.1592 | 323.5497
1221.4729 | 826.5559 | 311.3274 | 314.7056 | 323.7553
1222.4729 | 824.6951 | 311.362 | 315.3191 | 324.1102
1223.4729 | 824.8375 | 311.9162 | 315.0245 | 323.9759
1224.4729 | 824.0088 | 312.1186 | 315.2632 | 324.3487
1225.4729 | 825.7848 | 312.4948 | 315.6726 | 325.8297
1226.4729 | 827.7077 | 313.0101 | 316.8458 | 326.2678
1227.4729 | 830.4635 | 313.4729 | 317.5873 | 326.6331
1228.4885 | 830.9546 | 314.1537 | 317.7595 | 326.7046
1229.4729 | 832.1306 | 314.8398 | 318.3548 | 326.7372
1230.4885 | 831.3984 | 315.3307 | 318.8983 | 327.4261
1231.4885 | 829.9755 | 315.6621 | 318.7974 | 327.3041
1232.4729 | 830.84 | 316.168 | 319.1726 | 327.1666
1233.4729 | 830.5605 | 316.6318 | 319.5986 | 327.4957
1234.4729 | 830.8723 | 316.3009 | 319.7975 | 328.2168
1235.4729 | 831.7268 | 316.0801 | 319.6013 | 328.552
1236.4729 | 832.2434 | 316.4286 | 319.9311 | 328.128
1237.4729 | 831.2285 | 316.7678 | 320.1233 | 327.7173
1238.4729 | 833.6865 | 316.7254 | 320.3399 | 327.7851
1239.4729 | 833.8308 | 317.2454 | 320.5766 | 328.9551
1240.4729 | 836.6627 | 318.0563 | 320.8023 | 328.6035
1241.4729 | 838.6838 | 318.5606 | 320.6672 | 328.2194
1242.4729 | 841.0896 | 318.6368 | 320.6689 | 328.3356
1243.4729 | 840.4394 | 318.7265 | 320.6151 | 328.9721
1244.4729 | 839.6327 | 319.0442 | 320.8721 | 329.5804
1245.4729 | 842.5667 | 319.4757 | 320.7097 | 329.1837
1246.4729 | 840.8367 | 319.8249 | 320.7297 | 329.0283
1247.4729 | 839.0964 | 319.733 | 320.6614 | 329.1039
1248.4729 | 836.8233 | 319.2568 | 320.5614 | 329.0783
1249.4729 | 833.234 | 318.9043 | 320.3583 | 329.4448
1250.4729 | 830.9521 | 318.7692 | 321.0703 | 329.3869
1251.4729 | 831.2125 | 319.0455 | 321.113 | 329.1596
1252.4729 | 830.0736 | 319.693 | 321.3961 | 330.1771
1253.4729 | 827.3768 | 320.0043 | 321.4784 | 330.3542
1254.4729 | 823.8652 | 320.0536 | 320.9819 | 329.9904
1255.4729 | 823.7827 | 320.303 | 321.3265 | 329.7921
1256.4729 | 820.6714 | 320.1735 | 321.1337 | 330.6324
1257.4729 | 815.8044 | 320.5672 | 321.1575 | 330.8082
1258.4729 | 816.0377 | 321.0267 | 321.7883 | 331.3753
1259.4729 | 816.2962 | 321.5502 | 322.2693 | 331.9619
1260.4729 | 817.6924 | 321.8996 | 322.7516 | 332.6386
1261.4729 | 817.3891 | 321.6454 | 322.8246 | 332.4431
1262.4729 | 817.8741 | 322.188 | 323.1979 | 333.5979
1263.4885 | 818.9011 | 322.5524 | 323.5518 | 332.7336
1264.4729 | 819.0495 | 323.0079 | 323.625 | 332.5369
1265.4729 | 817.7838 | 323.0992 | 323.8555 | 332.4719
1266.4729 | 817.5178 | 323.4511 | 324.5216 | 332.3668
1267.4729 | 817.3846 | 323.3878 | 324.7338 | 333.19
1268.4729 | 819.325 | 323.5394 | 324.6828 | 334.1559
1269.4729 | 819.5041 | 323.7507 | 324.646 | 334.2265
1270.4729 | 820.3623 | 323.9854 | 325.015 | 335.9599
1271.4729 | 818.5866 | 324.3587 | 324.8271 | 337.0009
1272.4729 | 820.8312 | 324.4124 | 324.5758 | 336.8163
1273.4729 | 822.6675 | 324.4661 | 324.2496 | 336.6177
1274.4729 | 823.1077 | 324.4506 | 324.6877 | 337.4463
1275.4729 | 824.4938 | 324.9815 | 325.0718 | 337.3075
1276.4729 | 828.198 | 325.3558 | 325.4286 | 337.7671
1277.4729 | 829.1293 | 326.0435 | 325.7529 | 337.2653
1278.4729 | 829.5602 | 326.0077 | 326.1806 | 338.0378
1279.4729 | 827.6382 | 325.8397 | 326.0997 | 338.228
1280.4729 | 822.5447 | 325.7858 | 326.2536 | 338.4262
1281.4729 | 818.074 | 326.1709 | 326.1891 | 338.2966
1282.4729 | 816.4885 | 326.1744 | 326.1201 | 338.1263
1283.4729 | 815.1353 | 326.1426 | 326.3683 | 338.3922
1284.4729 | 817.9734 | 326.7816 | 326.776 | 338.6011
1285.4729 | 821.9507 | 326.9137 | 327.6513 | 338.4132
1286.4729 | 821.2091 | 327.1636 | 328.5516 | 339.9764
1287.4729 | 823.5168 | 327.0032 | 329.1125 | 340.9141
1288.4729 | 825.0671 | 327.3748 | 329.0593 | 340.5262
1289.4729 | 824.8851 | 328.1198 | 329.0705 | 341.0568
1290.4729 | 826.223 | 328.4973 | 329.483 | 341.1472
1291.4729 | 826.2464 | 329.3334 | 329.6312 | 340.9779
1292.4729 | 826.0706 | 329.1553 | 329.3278 | 340.919
1293.4729 | 826.2366 | 329.3608 | 329.5035 | 340.5838
1294.4729 | 826.9915 | 328.9535 | 329.5297 | 340.7738
1295.4729 | 827.4946 | 328.8018 | 329.3063 | 340.9694
1296.4729 | 827.4344 | 328.9289 | 329.1805 | 340.7412
1297.4729 | 832.3283 | 329.0425 | 329.5415 | 340.7796
1298.4729 | 833.1236 | 329.1219 | 329.7695 | 340.8105
1299.4729 | 830.4094 | 329.1161 | 329.2125 | 340.3643
1300.4729 | 829.483 | 328.8703 | 329.9617 | 340.3822
1301.4729 | 829.055 | 329.4665 | 329.8372 | 340.2309
1302.4729 | 826.8878 | 329.2447 | 330.2821 | 340.9355
1303.4729 | 825.1126 | 329.3481 | 330.1223 | 340.6186
1304.4729 | 822.8303 | 329.9262 | 329.7447 | 340.7322
1305.4729 | 821.1248 | 330.1795 | 329.7686 | 340.92
1306.4729 | 820.1931 | 330.2398 | 330.4417 | 340.9984
1307.4729 | 817.8589 | 330.6709 | 330.378 | 340.9349
1308.4729 | 818.9356 | 330.7861 | 331.0133 | 341.4213
1309.4729 | 818.7283 | 330.7601 | 331.285 | 341.744
1310.4729 | 818.3994 | 331.2518 | 331.6652 | 341.8087
1311.4729 | 819.3176 | 332.1271 | 332.5018 | 342.0678
1312.4729 | 816.4914 | 332.2145 | 332.7363 | 342.3343
1313.4729 | 816.5412 | 332.1353 | 333.6975 | 343.082
1314.4729 | 816.1534 | 332.4244 | 333.964 | 343.1968
1315.4729 | 815.5113 | 332.7893 | 334.0113 | 343.3051
1316.4729 | 814.4268 | 332.6671 | 333.7146 | 343.6053
1317.4729 | 816.1822 | 332.5304 | 333.2286 | 343.1621
1318.4729 | 814.602 | 332.3007 | 332.9313 | 342.0685
1319.4729 | 813.7365 | 332.2135 | 332.4158 | 342.2135
1320.4729 | 812.3337 | 332.7066 | 332.5115 | 342.9534
1321.4729 | 810.295 | 332.5194 | 333.0276 | 343.7602
1322.4729 | 809.7079 | 332.3457 | 332.8497 | 344.3488
1323.4729 | 808.4153 | 332.0445 | 332.9149 | 344.5421
1324.4729 | 809.2787 | 332.462 | 332.8602 | 344.9233
1325.4729 | 809.7477 | 332.2839 | 333.2045 | 344.7202
1326.4729 | 809.2384 | 331.8899 | 332.8602 | 344.3144
1327.4729 | 808.103 | 331.8129 | 332.2559 | 344.6505
1328.4729 | 810.3858 | 332.0954 | 332.1651 | 344.7631
1329.4729 | 809.3555 | 331.6374 | 332.4439 | 344.8599
1330.4729 | 807.5927 | 331.7301 | 332.9011 | 345.5683
1331.4729 | 807.8454 | 331.7067 | 332.8433 | 345.9158
1332.4729 | 807.9062 | 331.911 | 333.2339 | 346.4038
1333.4729 | 806.2584 | 331.9364 | 334.5562 | 346.4773
1334.4729 | 806.2325 | 332.042 | 334.824 | 345.8715
1335.4729 | 808.8598 | 332.5081 | 334.8021 | 346.2859
1336.4729 | 807.2725 | 332.6664 | 334.8042 | 346.4029
1337.4729 | 806.7433 | 332.3993 | 334.9396 | 345.9912
1338.4729 | 807.913 | 332.516 | 334.533 | 345.4323
1339.4729 | 808.0503 | 332.6299 | 335.3949 | 345.5939
1340.4729 | 808.3128 | 332.8381 | 335.4282 | 345.1044
1341.4729 | 805.5204 | 332.3068 | 335.2951 | 344.5701
1342.4729 | 805.4949 | 332.617 | 335.1172 | 345.0165
1343.4729 | 806.2666 | 332.8441 | 335.4342 | 345.9383
1344.4729 | 806.1451 | 333.1344 | 335.7761 | 347.0235
1345.4729 | 804.4972 | 333.2505 | 336.5655 | 346.9802
1346.4729 | 805.6992 | 333.5863 | 337.0904 | 347.4017
1347.4729 | 804.2994 | 333.7486 | 337.2262 | 347.9656
1348.4729 | 802.8397 | 333.9439 | 337.1573 | 348.1911
1349.4729 | 804.2691 | 334.3645 | 337.4569 | 348.7611
1350.4729 | 806.3105 | 334.187 | 337.6971 | 348.6992
1351.4729 | 805.9155 | 334.0498 | 338.0207 | 348.8914
1352.4729 | 806.4736 | 333.5214 | 337.5909 | 348.2577
1353.4729 | 808.0758 | 333.9653 | 337.2838 | 347.8664
1354.4729 | 808.7986 | 334.5566 | 338.0057 | 348.3692
1355.4729 | 811.4082 | 334.4239 | 337.981 | 348.0618
1356.4885 | 813.0427 | 334.4457 | 338.1889 | 348.2672
1357.4885 | 816.8189 | 334.4737 | 338.0435 | 348.0796
1358.4729 | 817.318 | 334.4677 | 337.9381 | 347.952
1359.4729 | 812.5602 | 334.5567 | 337.4669 | 347.1505
1360.4729 | 814.5516 | 334.4885 | 337.2245 | 347.148
1361.4885 | 814.2029 | 334.5266 | 337.7314 | 346.7046
1362.4729 | 814.6796 | 334.3263 | 338.1211 | 347.1592
1363.4729 | 814.104 | 333.7645 | 338.0721 | 347.2861
1364.4729 | 811.3599 | 333.8208 | 338.3014 | 347.6043
1365.4729 | 809.1442 | 334.4286 | 338.8561 | 347.992
1366.4729 | 808.9101 | 334.0586 | 338.7282 | 347.332
1367.4729 | 807.692 | 334.121 | 338.7823 | 346.9315
1368.4729 | 807.4348 | 333.9496 | 338.8904 | 347.282
1369.4729 | 805.3811 | 333.8243 | 339.1791 | 347.3615
1370.4729 | 803.8373 | 333.6565 | 339.6283 | 348.1196
1371.4729 | 804.7346 | 334.4564 | 340.0761 | 348.198
1372.4729 | 805.965 | 334.4457 | 340.8204 | 349.1979
1373.4729 | 806.1228 | 334.8964 | 340.6933 | 349.9719
1374.4729 | 804.0755 | 334.8356 | 341.0299 | 349.899
1375.4729 | 804.9796 | 334.8288 | 340.8928 | 349.6999
1376.4729 | 803.844 | 334.3704 | 340.6021 | 350.3206
1377.4729 | 805.3332 | 334.5939 | 340.6082 | 349.5833
1378.4729 | 809.4915 | 334.2651 | 340.1672 | 348.9791
1379.4729 | 811.4136 | 333.9968 | 339.9734 | 348.5763
1380.4729 | 808.8076 | 333.8499 | 340.1497 | 348.6822
1381.4729 | 809.7998 | 334.0274 | 339.7873 | 348.5811
1382.4729 | 810.9695 | 334.1645 | 339.6512 | 348.7374
1383.4729 | 810.601 | 334.308 | 339.9728 | 348.9121
1384.4729 | 808.9047 | 335.0757 | 340.4523 | 348.9603
1385.4729 | 806.1656 | 335.2564 | 340.5723 | 348.9727
1386.4729 | 804.4133 | 335.3219 | 340.3221 | 348.2226
1387.4729 | 801.0916 | 335.5641 | 339.7971 | 347.8525
1388.4729 | 799.7187 | 335.1849 | 339.6898 | 347.8162
1389.4729 | 796.8153 | 335.2412 | 339.6375 | 347.7723
1390.4729 | 798.2587 | 334.9799 | 339.7721 | 347.8552
1391.4729 | 798.0854 | 335.4304 | 340.1115 | 347.9891
1392.4729 | 795.405 | 335.4779 | 340.0855 | 348.4483
1393.4729 | 796.1055 | 335.6905 | 339.9425 | 347.9838
1394.4729 | 792.7822 | 335.8933 | 339.2776 | 348.1114
1395.4729 | 794.8327 | 336.2291 | 339.8735 | 348.6751
1396.4729 | 792.8205 | 336.4909 | 339.6155 | 349.8477
1397.4729 | 790.9175 | 336.4102 | 339.6575 | 349.8238
1398.4729 | 791.8723 | 336.519 | 339.755 | 349.8046
1399.4729 | 792.014 | 336.2663 | 339.8961 | 349.5488
1400.4729 | 792.2276 | 336.7097 | 340.3126 | 350.3022
1401.4729 | 792.1156 | 336.5854 | 340.0749 | 350.7891
1402.4729 | 789.6693 | 336.9921 | 339.7872 | 350.559
1403.4729 | 789.8697 | 337.1951 | 339.9042 | 349.6643
1404.4729 | 789.906 | 337.4496 | 339.8078 | 348.9662
1405.4729 | 790.0696 | 337.0605 | 340.0931 | 348.7266
1406.4729 | 791.5497 | 336.7273 | 339.7139 | 348.7329
1407.4729 | 793.8091 | 336.1651 | 338.9892 | 348.2665
1408.4729 | 792.9192 | 335.9416 | 339.3263 | 347.6077
1409.4729 | 794.0377 | 335.3103 | 338.645 | 346.9667
1410.4729 | 793.439 | 335.2496 | 338.2737 | 346.6338
1411.4729 | 793.9843 | 334.9786 | 338.1044 | 345.6997
1412.4729 | 794.3108 | 334.7055 | 337.5314 | 345.4015
1413.4729 | 792.9706 | 334.6472 | 337.4001 | 344.7394
1414.4729 | 791.3403 | 334.322 | 337.1749 | 344.483
1415.4729 | 790.0535 | 333.6409 | 336.555 | 344.0901
1416.4729 | 790.2524 | 333.4595 | 336.2499 | 343.5387
1417.4729 | 790.1181 | 333.1948 | 335.526 | 343.2923
1418.4729 | 789.4235 | 332.66 | 334.9386 | 342.291
1419.4729 | 791.1312 | 332.383 | 334.9917 | 342.4161
1420.4729 | 790.9489 | 331.9727 | 334.6944 | 342.276
1421.4729 | 790.7246 | 331.9403 | 334.8216 | 342.5912
1422.4729 | 792.8466 | 331.6514 | 335.0239 | 342.1604
1423.4729 | 794.4202 | 331.3149 | 334.8101 | 342.1693
1424.4729 | 799.8261 | 331.0544 | 334.5446 | 342.1598
1425.4729 | 798.2572 | 330.8444 | 334.4952 | 342.108
1426.4729 | 799.2386 | 331.253 | 334.5993 | 341.9451
1427.4729 | 799.8103 | 331.4071 | 334.7687 | 341.888
1428.4729 | 798.8169 | 332.1317 | 335.0678 | 342.591
1429.4729 | 799.4766 | 332.4306 | 335.2424 | 342.5612
1430.4729 | 798.2004 | 332.1096 | 334.4824 | 342.3817
1431.4729 | 796.1728 | 332.3943 | 334.1108 | 341.9019
1432.4729 | 794.5213 | 332.3524 | 334.2191 | 341.793
1433.4729 | 792.9881 | 332.2179 | 334.0995 | 341.5178
1434.4729 | 791.9115 | 332.0273 | 333.6021 | 341.7959
1435.4729 | 791.9765 | 331.5266 | 333.1168 | 341.3831
1436.4729 | 793.2312 | 331.7279 | 333.0045 | 341.1712
1437.4729 | 791.3559 | 331.9261 | 332.9272 | 341.1498
1438.4729 | 792.4822 | 331.5969 | 333.6022 | 341.2558
1439.4729 | 793.1186 | 331.3337 | 333.4595 | 340.9978
1440.4729 | 792.511 | 331.0897 | 333.4678 | 341.1357
1441.4729 | 794.8993 | 330.7674 | 333.0357 | 341.2584
1442.4729 | 796.0719 | 330.4466 | 332.4785 | 341.0301
1443.4729 | 798.9959 | 330.712 | 332.3973 | 341.4344
1444.4729 | 799.5378 | 330.5878 | 332.5767 | 341.293
1445.4729 | 799.4126 | 330.588 | 331.9859 | 341.1888
1446.4729 | 800.6041 | 330.6652 | 332.3622 | 341.4045
1447.4729 | 798.2444 | 330.4388 | 331.8371 | 340.7809
1448.4729 | 795.9602 | 330.2419 | 331.8993 | 340.8813
1449.4729 | 795.5135 | 330.0924 | 331.6341 | 340.9053
1450.4729 | 797.7353 | 330.1545 | 331.9133 | 340.8449
1451.4729 | 798.212 | 329.9608 | 332.1656 | 340.8221
1452.4729 | 800.4847 | 330.0265 | 332.144 | 340.5494
1453.4729 | 799.4254 | 329.8598 | 332.1196 | 340.5029
1454.4729 | 799.831 | 329.5189 | 331.7505 | 340.3037
1455.4729 | 799.0641 | 329.3571 | 331.5182 | 339.9268
1456.4729 | 797.6085 | 329.1114 | 331.2918 | 339.2307
1457.4729 | 796.2572 | 329.0862 | 331.0578 | 339.295
1458.4729 | 793.7829 | 328.9045 | 330.7312 | 339.5694
1459.4729 | 793.2017 | 328.7774 | 330.317 | 338.7906
1460.4729 | 792.43 | 328.5489 | 330.2523 | 338.4684
1461.4729 | 791.6817 | 328.2264 | 330.611 | 338.9959
1462.4729 | 790.0376 | 328.2187 | 330.4475 | 338.9023
1463.4729 | 788.615 | 328.2017 | 330.2054 | 338.9581
1464.4729 | 788.5003 | 328.6368 | 330.8457 | 339.414
1465.4729 | 787.2837 | 329.2191 | 330.8996 | 339.5762
1466.4729 | 785.4411 | 328.6966 | 330.4494 | 339.3633
1467.4729 | 784.2772 | 328.7205 | 330.3993 | 339.668
1468.4729 | 781.5521 | 328.6122 | 330.2256 | 339.2534
1469.4729 | 782.4095 | 328.644 | 329.9473 | 339.0343
1470.4729 | 783.3924 | 328.5325 | 329.7379 | 338.9618
1471.4729 | 783.8709 | 328.0767 | 329.5347 | 339.1614
1472.4729 | 782.2504 | 328.1927 | 329.5981 | 339.1333
1473.4729 | 782.8918 | 327.6835 | 329.6768 | 339.643
1474.4729 | 782.5619 | 327.1 | 329.339 | 339.1061
1475.4729 | 779.212 | 326.7778 | 328.7725 | 338.8666
1476.4729 | 777.0146 | 326.7971 | 328.9326 | 338.856
1477.4729 | 771.354 | 327.2299 | 329.0123 | 339.2467
1478.4729 | 769.3263 | 327.1273 | 329.3412 | 339.4397
1479.4729 | 772.092 | 327.2406 | 329.3392 | 339.3325
1480.4729 | 777.2034 | 327.0922 | 329.4594 | 339.5555
1481.4729 | 781.7028 | 327.243 | 329.3981 | 339.6422
1482.4729 | 786.0081 | 328.0035 | 329.3625 | 339.3478
1483.4729 | 785.1349 | 328.266 | 329.1764 | 339.2436
1484.4729 | 786.1802 | 328.3777 | 329.5069 | 339.7011
1485.4729 | 789.6431 | 327.9244 | 329.3804 | 339.783
1486.4729 | 791.2669 | 327.8865 | 329.0899 | 339.8074
1487.4729 | 792.3333 | 327.4898 | 329.1368 | 339.6409
1488.4729 | 792.7123 | 327.3983 | 329.8107 | 340.3208
1489.4729 | 795.9573 | 327.9956 | 329.9967 | 340.7858
1490.4729 | 792.6719 | 328.1307 | 330.0831 | 340.893
1491.4729 | 789.8731 | 328.0607 | 330.2832 | 341.2209
1492.4729 | 790.9544 | 328.0928 | 330.2431 | 341.0209
1493.4729 | 792.8045 | 328.0969 | 330.1513 | 340.9676
1494.4729 | 785.9089 | 328.5534 | 330.4452 | 340.5506
1495.4729 | 783.3826 | 328.3846 | 330.8058 | 341.032
1496.4729 | 781.2575 | 328.6607 | 330.9988 | 340.8735
1497.4729 | 781.162 | 328.8569 | 331.4045 | 341.5041
1498.4729 | 781.8513 | 328.4971 | 330.9835 | 341.1999
1499.4729 | 778.7749 | 328.9521 | 330.7189 | 341.0096
1500.4729 | 783.6365 | 328.7207 | 330.6729 | 340.7558
1501.4729 | 785.5962 | 328.6341 | 330.6888 | 340.7031
1502.4729 | 784.0238 | 328.4567 | 330.9794 | 340.8067
1503.4729 | 784.9735 | 328.7765 | 330.609 | 340.2804
1504.4729 | 782.0434 | 329.2751 | 330.427 | 340.4602
1505.4729 | 777.7291 | 327.0067 | 330.7911 | 339.0803
1506.4729 | 773.4322 | 328.8542 | 329.8787 | 339.9164
1507.4729 | 773.5909 | 328.8083 | 329.9418 | 339.8578
1508.4729 | 776.7369 | 328.9434 | 329.7598 | 339.9292
1509.4729 | 781.2766 | 328.7332 | 329.9448 | 339.6381
1510.4729 | 785.1583 | 328.4817 | 329.5585 | 339.3673
1511.4729 | 787.908 | 328.8454 | 329.3492 | 339.4975
1512.4729 | 790.5869 | 328.831 | 329.2142 | 339.7361
1513.4729 | 789.4744 | 328.5248 | 329.8114 | 339.8316
1514.4729 | 788.2723 | 328.7037 | 330.0368 | 339.3467
1515.4729 | 787.1791 | 328.2875 | 329.8109 | 339.3384
1516.4729 | 787.542 | 328.2363 | 329.6003 | 339.319
1517.4729 | 784.0087 | 328.2082 | 329.1522 | 339.9172
1518.4729 | 776.8599 | 328.3189 | 329.2318 | 340.3028
1519.4729 | 770.0732 | 328.5105 | 328.9879 | 340.1632
1520.4729 | 765.5925 | 328.5447 | 329.7726 | 340.453
1521.4729 | 760.8864 | 328.7177 | 330.5301 | 340.7154
1522.4729 | 761.0091 | 328.8902 | 330.8498 | 341.0783
1523.4729 | 766.1399 | 329.4793 | 331.6396 | 341.652
1524.4729 | 772.8108 | 330.0305 | 332.1548 | 342.3399
1525.4729 | 775.5282 | 330.4699 | 332.4182 | 343.0562
1526.4729 | 780.2804 | 330.9923 | 332.4784 | 343.1583
1527.4729 | 780.5567 | 331.6467 | 332.7956 | 343.2268
1528.4729 | 775.0427 | 332.3041 | 333.1674 | 343.8663
1529.4729 | 776.3724 | 332.1808 | 333.2406 | 343.8186
1530.4729 | 771.0219 | 332.0995 | 333.0544 | 343.784
1531.4729 | 763.4601 | 332.0746 | 332.8613 | 343.6714
1532.4729 | 761.8891 | 332.4245 | 333.2313 | 343.7656
1533.4729 | 762.8459 | 332.8351 | 334.317 | 344.7514
1534.4729 | 766.5264 | 332.8484 | 334.8127 | 345.1188
1535.4729 | 773.9909 | 332.8852 | 335.2761 | 345.5969
1536.4729 | 775.0293 | 333.6526 | 335.7854 | 346.1169
1537.4729 | 777.5742 | 333.89 | 336.1823 | 346.328
1538.4729 | 785.8666 | 334.0098 | 336.0155 | 346.1724
1539.4729 | 794.2124 | 334.4724 | 335.692 | 346.5661
1540.4729 | 793.5909 | 334.7525 | 335.5258 | 347.0716
1541.4729 | 788.6768 | 334.3137 | 336.2223 | 347.6331
1542.4729 | 785.4362 | 333.9937 | 336.4308 | 347.9163
1543.4729 | 780.5312 | 334.1952 | 336.4832 | 347.7467
1544.4729 | 779.2195 | 334.8802 | 336.4166 | 348.3887
1545.4729 | 779.6784 | 334.6661 | 336.819 | 348.3362
1546.4729 | 780.2572 | 334.8586 | 336.7497 | 347.8465
1547.4729 | 777.8812 | 335.1191 | 337.1893 | 347.9945
1548.4729 | 776.7182 | 335.2635 | 337.4044 | 347.6227
1549.4729 | 776.6563 | 335.7297 | 337.8575 | 347.8112
1550.4729 | 775.5157 | 335.6813 | 338.0941 | 348.3175
1551.4729 | 769.7946 | 335.9327 | 338.1244 | 348.2887
1552.4729 | 770.6439 | 336.4012 | 338.336 | 348.0497
1553.4729 | 776.6503 | 337.0736 | 339.2497 | 348.9676
1554.4729 | 784.1115 | 337.2792 | 339.1907 | 348.9778
1555.4729 | 787.2727 | 337.6186 | 339.4009 | 348.8824
1556.4729 | 788.8528 | 337.776 | 339.438 | 348.6167
1557.4729 | 784.3901 | 337.3339 | 339.3304 | 348.2038
1558.4729 | 785.1213 | 337.2529 | 339.2681 | 348.1302
1559.4729 | 788.0116 | 338.2905 | 339.1357 | 348.1703
1560.4729 | 790.6978 | 338.5184 | 338.9301 | 348.1026
1561.4729 | 788.56 | 338.5586 | 339.1973 | 348.4322
1562.4729 | 789.0065 | 338.9145 | 339.5743 | 348.5759
1563.4729 | 791.486 | 339.0459 | 339.7524 | 349.2483
1564.4729 | 794.2291 | 338.9638 | 340.1402 | 349.3968
1565.4729 | 792.8379 | 338.6048 | 340.0563 | 349.4602
1566.4729 | 790.1175 | 338.2795 | 339.7811 | 349.2098
1567.4729 | 790.4848 | 338.0317 | 340.1659 | 349.7184
1568.4729 | 792.3714 | 338.0939 | 339.8934 | 350.0557
1569.4729 | 790.7115 | 338.1147 | 339.9381 | 349.8638
1570.4729 | 780.8049 | 338.0339 | 340.0277 | 349.5099
1571.4729 | 778.6014 | 338.1157 | 340.0413 | 349.4365
1572.4729 | 773.2739 | 338.0995 | 340.4192 | 349.7631
1573.4729 | 776.1002 | 338.2369 | 340.4822 | 349.7958
1574.4729 | 788.2317 | 338.3088 | 340.6536 | 350.3638
1575.4729 | 804.2814 | 338.417 | 341.0876 | 351.1039
1576.4729 | 809.1158 | 338.735 | 341.3896 | 351.2839
1577.4729 | 806.6519 | 339.1556 | 341.778 | 351.186
1578.4729 | 807.2885 | 338.94 | 342.0788 | 351.3437
1579.4729 | 809.4158 | 339.1942 | 341.8004 | 351.5416
1580.4729 | 812.3944 | 339.4762 | 341.5463 | 351.5082
1581.4729 | 814.2961 | 339.2565 | 341.0341 | 351.2103
1582.4729 | 814.0018 | 339.4074 | 341.4192 | 351.1441
1583.4729 | 818.2912 | 339.5823 | 341.3157 | 351.0242
1584.4729 | 817.4584 | 339.6239 | 341.4457 | 351.0658
1585.4729 | 816.8981 | 339.7624 | 340.9731 | 350.8137
1586.4729 | 817.4996 | 339.792 | 341.1638 | 350.6038
1587.4729 | 818.7113 | 339.819 | 341.3871 | 350.9691
1588.4729 | 819.8422 | 339.9388 | 341.4225 | 351.1665
1589.4729 | 818.7015 | 339.8024 | 341.7456 | 351.2268
1590.4729 | 818.3378 | 340.1151 | 341.7713 | 351.3938
1591.4729 | 815.9133 | 340.1477 | 341.5517 | 351.1183
1592.4729 | 816.046 | 340.0151 | 341.3776 | 350.7984
1593.4729 | 819.6465 | 340.15 | 341.8623 | 351.314
1594.4729 | 823.4777 | 340.1016 | 342.0195 | 351.3737
1595.4729 | 820.0288 | 340.4325 | 342.5301 | 351.7434
1596.4729 | 823.0949 | 340.4384 | 342.8498 | 351.6462
1597.4729 | 829.3 | 340.8954 | 342.7957 | 352.2355
1598.4729 | 831.2428 | 341.2259 | 342.8761 | 352.7208
1599.4729 | 834.0821 | 341.0532 | 343.3987 | 353.3504
1600.4729 | 837.9813 | 341.0791 | 343.5766 | 353.2206
1601.4885 | 841.0568 | 340.8381 | 343.5121 | 353.3433
1602.4729 | 843.7269 | 340.6137 | 343.4735 | 352.9437
1603.4729 | 847.3119 | 340.3901 | 343.459 | 352.9176
1604.4729 | 845.6215 | 340.5451 | 343.5937 | 352.9155
1605.4729 | 845.7088 | 340.6015 | 343.589 | 352.9609
1606.4729 | 846.9022 | 340.6397 | 343.6593 | 353.1281
1607.4729 | 842.2809 | 341.1169 | 343.9957 | 353.3691
1608.4729 | 842.7404 | 341.0896 | 344.8282 | 353.77
1609.4729 | 843.173 | 340.829 | 344.3751 | 353.551
1610.4729 | 839.9451 | 340.7831 | 344.2837 | 353.28
1611.4729 | 833.1848 | 341.2506 | 344.2187 | 353.074
1612.4729 | 827.2405 | 341.0504 | 344.6226 | 353.2814
1613.4729 | 826.9627 | 341.2206 | 344.866 | 353.5027
1614.4729 | 830.4117 | 341.4839 | 344.8603 | 353.6412
1615.4729 | 839.8645 | 341.8116 | 345.3774 | 353.9476
1616.4729 | 843.9015 | 342.2951 | 345.3414 | 353.8611
1617.4729 | 847.6011 | 342.4986 | 344.8023 | 353.4336
1618.4729 | 848.4758 | 343.0435 | 344.9902 | 353.1187
1619.4729 | 847.9356 | 343.0623 | 344.7247 | 354.1384
1620.4729 | 849.8136 | 343.1429 | 344.8803 | 354.1847
1621.4729 | 853.5705 | 343.0634 | 344.6237 | 353.8465
1622.4729 | 853.1955 | 343.1347 | 344.4407 | 353.9916
1623.4729 | 851.4973 | 342.8574 | 344.546 | 353.9619
1624.4729 | 852.1381 | 342.6593 | 344.3041 | 354.0014
1625.4729 | 851.7792 | 342.6945 | 344.2352 | 353.6187
1626.4729 | 849.7045 | 342.4264 | 343.8886 | 353.9947
1627.4729 | 852.1926 | 342.0687 | 343.3493 | 353.9121
1628.4729 | 856.5191 | 341.9945 | 343.086 | 354.0448
1629.4729 | 856.5526 | 341.6051 | 342.7421 | 353.6408
1630.4729 | 854.643 | 341.4858 | 342.3009 | 353.5432
1631.4729 | 846.5061 | 341.0515 | 342.0865 | 352.982
1632.4729 | 848.4587 | 340.9805 | 342.2865 | 352.9289
1633.4729 | 845.3022 | 340.864 | 342.3104 | 352.5585
1634.4729 | 843.8162 | 340.8729 | 342.1548 | 352.402
1635.4729 | 850.6404 | 340.5477 | 342.3396 | 352.098
1636.4729 | 857.46 | 340.1245 | 342.0486 | 351.966
1637.4729 | 852.6743 | 339.9958 | 341.6383 | 352.0556
1638.4729 | 849.6463 | 339.4697 | 341.6994 | 352.0724
1639.4729 | 864.8161 | 339.3296 | 341.3579 | 352.0473
1640.4729 | 864.3811 | 339.0957 | 341.1872 | 352.0051
1641.4729 | 861.8966 | 339.1329 | 341.4676 | 352.0067
1642.4729 | 855.0015 | 338.9889 | 341.4411 | 352.1004
1643.4729 | 854.9006 | 338.8594 | 341.1683 | 351.9735
1644.4729 | 859.4959 | 339.036 | 340.9803 | 351.5525
1645.4729 | 859.2124 | 339.2353 | 341.0558 | 351.3471
1646.4729 | 855.3735 | 339.4974 | 341.4043 | 351.4029
1647.4729 | 845.6576 | 339.3779 | 341.7117 | 351.3791
1648.4729 | 843.3418 | 339.6005 | 341.7456 | 351.1685
1649.4729 | 841.0179 | 339.9201 | 342.1709 | 351.0735
1650.4729 | 840.5333 | 340.5379 | 342.7691 | 351.4712
1651.4729 | 842.4702 | 340.5755 | 342.9355 | 352.1371
1652.4729 | 845.9274 | 340.9964 | 342.9931 | 352.4476
1653.4729 | 854.2496 | 341.5014 | 343.0509 | 352.3986
1654.4729 | 858.2468 | 341.3689 | 342.6526 | 352.3856
1655.4729 | 853.362 | 341.5658 | 342.348 | 352.3878
1656.4729 | 855.2854 | 342.0361 | 342.6297 | 352.7964
1657.4729 | 848.2063 | 341.8657 | 342.6259 | 352.5941
1658.4729 | 836.7212 | 341.9457 | 342.5803 | 353.0957
1659.4729 | 834.0015 | 342.1621 | 343.1049 | 353.0468
1660.4729 | 833.7763 | 341.8251 | 343.1773 | 353.4292
1661.4729 | 825.9744 | 341.5595 | 342.908 | 353.5013
1662.4729 | 823.6311 | 341.688 | 342.8599 | 353.9301
1663.4729 | 828.271 | 341.6753 | 342.9016 | 354.0123
1664.4729 | 833.4835 | 342.0945 | 343.8465 | 354.5266
1665.4885 | 834.4124 | 342.0798 | 344.78 | 355.8361
1666.4729 | 838.3412 | 341.8457 | 344.5588 | 355.7529
1667.4729 | 829.0631 | 341.6754 | 344.452 | 355.623
1668.4729 | 839.5816 | 341.3072 | 344.418 | 355.2536
1669.4729 | 845.4393 | 341.3082 | 344.3703 | 355.2128
1670.4729 | 843.3336 | 341.2388 | 344.4251 | 355.235
1671.4729 | 837.8379 | 341.5222 | 344.4087 | 355.3892
1672.4729 | 841.5292 | 341.7231 | 344.2481 | 355.3667
1673.4729 | 841.0788 | 341.8992 | 344.4583 | 355.5551
1674.4729 | 835.734 | 341.98 | 344.3032 | 355.323
1675.4729 | 838.6398 | 342.1666 | 344.1667 | 355.2581
1676.4729 | 823.6026 | 342.1347 | 344.1739 | 355.334
1677.4729 | 809.8138 | 342.3036 | 344.9248 | 356.2153
1678.4729 | 812.6325 | 342.7163 | 345.4085 | 356.6495
1679.4729 | 818.2212 | 343.22 | 345.7254 | 356.5552
1680.4729 | 822.6241 | 344.1114 | 346.4712 | 357.6413
1681.4729 | 823.5133 | 344.8359 | 347.6523 | 357.8271
1682.4729 | 831.7499 | 345.7416 | 348.0546 | 357.6899
1683.4729 | 831.0197 | 345.774 | 348.0032 | 357.4117
1684.4729 | 830.9497 | 346.0302 | 348.2369 | 357.8843
1685.4729 | 832.9026 | 346.6033 | 348.8593 | 357.9854
1686.4729 | 837.9344 | 347.3698 | 349.1074 | 358.9893
1687.4729 | 843.1397 | 347.464 | 349.5034 | 359.1207
1688.4729 | 843.3238 | 347.5103 | 349.9328 | 359.5593
1689.4729 | 848.9448 | 347.765 | 350.03 | 359.1574
1690.4729 | 845.4671 | 347.7529 | 349.5487 | 359.249
1691.4729 | 846.4331 | 347.739 | 349.3671 | 359.1453
1692.4729 | 843.2678 | 347.5457 | 349.4619 | 359.1471
1693.4729 | 835.9728 | 347.3103 | 349.5567 | 358.9503
1694.4729 | 839.5617 | 347.2822 | 349.126 | 359.4788
1695.4885 | 847.3517 | 347.3698 | 348.9005 | 359.615
1696.4729 | 856.4266 | 346.9773 | 348.9666 | 360.0998
1697.4729 | 864.376 | 347.5356 | 349.0584 | 359.9298
1698.4729 | 869.9726 | 347.5977 | 348.9584 | 359.964
1699.4729 | 869.0943 | 348.206 | 348.8408 | 360.0744
1700.4729 | 863.3391 | 348.1974 | 349.0196 | 360.4945
1701.4729 | 860.0327 | 348.1754 | 349.2332 | 360.6326
1702.4729 | 849.2392 | 348.2405 | 349.2851 | 360.7829
1703.4729 | 845.0101 | 348.4003 | 349.109 | 360.8299
1704.4729 | 840.294 | 348.4897 | 349.7691 | 361.0896
1705.4729 | 841.8945 | 348.6329 | 349.6798 | 361.3858
1706.4729 | 839.4921 | 349.6051 | 349.9954 | 361.3209
1707.4729 | 833.4936 | 349.7719 | 350.2795 | 361.6068
1708.4729 | 833.8966 | 349.624 | 350.3862 | 361.3779
1709.4729 | 832.7632 | 349.7277 | 350.719 | 361.6107
1710.4729 | 826.2118 | 349.7585 | 350.7009 | 361.7557
1711.4729 | 830.3172 | 349.9822 | 350.6471 | 361.2395
1712.4729 | 830.6518 | 350.0825 | 351.3372 | 361.3723
1713.4729 | 832.9766 | 350.1669 | 351.5406 | 362.3328
1714.4729 | 837.3045 | 350.2431 | 351.305 | 362.1175
1715.4729 | 839.8438 | 350.6937 | 351.3883 | 362.7197
1716.4729 | 845.4308 | 350.918 | 351.8947 | 362.7004
1717.4729 | 849.9594 | 351.0317 | 352.0133 | 363.148
1718.4729 | 841.8943 | 351.647 | 351.9286 | 363.1591
1719.4729 | 833.4233 | 351.8524 | 352.2425 | 363.7003
1720.4729 | 837.3491 | 351.9033 | 352.2467 | 363.8349
1721.4729 | 840.131 | 351.8884 | 352.5022 | 363.6792
1722.4729 | 827.689 | 351.4955 | 352.2262 | 363.6063
1723.4729 | 827.8002 | 352.0655 | 352.3902 | 363.3878
1724.4729 | 828.6267 | 352.0172 | 352.1785 | 363.0592
1725.4729 | 832.9494 | 352.0661 | 351.9336 | 362.7667
1726.4729 | 833.6945 | 352.1662 | 351.9966 | 363.4064
1727.4729 | 836.388 | 352.1489 | 352.2067 | 363.2352
1728.4729 | 841.6027 | 351.7516 | 352.2309 | 363.7076
1729.4729 | 848.8405 | 351.8171 | 352.5221 | 363.439
1730.4729 | 846.8729 | 352.1002 | 352.4319 | 362.9739
1731.4729 | 843.0658 | 352.8453 | 352.4441 | 364.0292
1732.4729 | 845.8312 | 352.5932 | 352.7655 | 364.2767
1733.4729 | 849.0235 | 352.3551 | 352.7391 | 364.4273
1734.4729 | 851.6916 | 352.287 | 353.094 | 364.5781
1735.4729 | 850.4899 | 352.2586 | 353.7224 | 365.083
1736.4729 | 847.653 | 352.4446 | 354.0667 | 365.0043
1737.4729 | 848.0054 | 352.665 | 354.0647 | 365.0261
1738.4729 | 853.3052 | 353.1293 | 353.7223 | 364.9591
1739.4729 | 852.9307 | 353.0986 | 353.7469 | 364.9314
1740.4729 | 854.5515 | 353.4437 | 353.9915 | 365.4339
1741.4729 | 853.0298 | 353.5388 | 354.2477 | 365.7117
1742.4729 | 852.8132 | 353.5254 | 354.4875 | 365.4961
1743.4729 | 856.2782 | 353.5384 | 354.4477 | 365.8618
1744.4729 | 853.7974 | 353.6712 | 354.5352 | 365.435
1745.4729 | 849.7414 | 353.4114 | 354.1693 | 365.6672
1746.4729 | 847.8743 | 353.4151 | 353.8993 | 365.5201
1747.4729 | 834.8497 | 353.753 | 353.905 | 365.7818
1748.4729 | 840.6305 | 353.788 | 354.2699 | 366.4476
1749.4729 | 844.1231 | 354.133 | 354.8011 | 367.2399
1750.4729 | 858.8426 | 354.3243 | 355.4262 | 367.8584
1751.4729 | 857.0824 | 355.0309 | 355.8458 | 368.5388
1752.4729 | 852.7381 | 355.5284 | 356.7425 | 369.0004
1753.4729 | 844.7107 | 355.9725 | 357.0583 | 369.1055
1754.4729 | 837.8864 | 356.5514 | 357.7802 | 369.09
1755.4885 | 838.4914 | 356.6479 | 358.0297 | 369.2151
1756.4729 | 835.9629 | 357.2165 | 358.3408 | 369.3986
1757.4729 | 837.9281 | 357.9102 | 358.6075 | 369.8276
1758.4729 | 834.8647 | 357.7479 | 358.7863 | 369.7011
1759.4729 | 833.0331 | 357.6635 | 358.8663 | 370.3829
1760.4729 | 830.9353 | 357.708 | 358.9158 | 370.4606
1761.4729 | 832.9361 | 357.5903 | 359.3549 | 371.0864
1762.4729 | 842.4808 | 357.3344 | 359.5112 | 371.7368
1763.4729 | 847.522 | 357.1499 | 360.1826 | 372.232
1764.4729 | 851.8495 | 356.8775 | 360.3874 | 372.3364
1765.4729 | 855.4869 | 357.0141 | 360.3521 | 371.8895
1766.4729 | 861.195 | 357.2379 | 360.656 | 373.0215
1767.4729 | 863.1111 | 357.6425 | 360.7614 | 373.0629
1768.4729 | 861.8931 | 357.9922 | 360.9352 | 373.841
1769.4729 | 851.7843 | 358.5297 | 361.3146 | 373.9604
1770.4729 | 848.353 | 358.3924 | 361.1171 | 373.7871
1771.4729 | 850.775 | 358.4307 | 361.0306 | 373.7922
1772.4729 | 857.8797 | 358.5299 | 361.7463 | 374.7549
1773.4729 | 864.3412 | 358.4607 | 361.8123 | 374.4554
1774.4729 | 866.6277 | 358.5664 | 361.4398 | 374.0209
1775.4729 | 865.7986 | 358.764 | 361.2614 | 373.7531
1776.4729 | 865.7721 | 358.9207 | 361.7069 | 373.6347
1777.4729 | 867.8784 | 359.1017 | 361.8812 | 374.0961
1778.4729 | 874.9746 | 358.734 | 361.6339 | 373.8102
1779.4729 | 873.4953 | 358.906 | 361.8171 | 373.6104
1780.4729 | 866.1674 | 359.1022 | 362.1173 | 373.6903
1781.4729 | 859.4476 | 359.5401 | 362.4011 | 373.577
1782.4729 | 860.3521 | 359.6933 | 362.6161 | 373.389
1783.4729 | 864.1063 | 359.9026 | 362.9669 | 373.6576
1784.4729 | 862.3437 | 359.8568 | 363.251 | 373.9065
1785.4729 | 866.099 | 359.9404 | 363.1307 | 373.8898
1786.4729 | 866.5579 | 359.9799 | 363.3222 | 373.944
1787.4729 | 858.0547 | 360.1001 | 363.2628 | 373.9737
1788.4729 | 857.823 | 360.5513 | 363.6798 | 373.9537
1789.4729 | 856.3982 | 360.6547 | 363.3367 | 373.6382
1790.4729 | 849.3423 | 360.918 | 363.633 | 374.0672
1791.4729 | 845.3863 | 361.1663 | 363.8834 | 374.3428
1792.4729 | 842.8115 | 360.9653 | 363.8788 | 374.0627
1793.4729 | 843.6877 | 361.018 | 363.7827 | 373.8244
1794.4729 | 844.6006 | 360.659 | 363.5739 | 373.9637
1795.4729 | 842.631 | 360.8147 | 363.2087 | 373.9888
1796.4729 | 837.3862 | 360.7416 | 362.9275 | 373.8769
1797.4729 | 832.6118 | 360.8389 | 362.5531 | 373.6841
1798.4729 | 831.5986 | 361.1139 | 362.5581 | 373.5791
1799.4729 | 831.0745 | 361.0146 | 362.6923 | 373.4764
1800.4729 | 835.0982 | 361.2515 | 362.5968 | 373.5687
1801.4729 | 840.9764 | 361.2822 | 362.7048 | 373.5504
1802.4729 | 842.4988 | 360.9296 | 362.5919 | 373.1995
1803.4729 | 841.1709 | 361.3989 | 362.5667 | 373.2401
1804.4729 | 845.9826 | 361.2958 | 363.1297 | 373.6475
1805.4729 | 846.0816 | 361.4267 | 362.8992 | 373.6431
1806.4729 | 847.2573 | 361.5607 | 362.7489 | 374.4217
1807.4729 | 837.4422 | 361.9055 | 362.9329 | 374.7209
1808.4729 | 830.8335 | 362.5177 | 363.5639 | 375.3546
1809.4729 | 816.437 | 362.8885 | 363.7616 | 375.4699
1810.4729 | 819.7217 | 363.1514 | 363.8166 | 375.2462
1811.4729 | 823.1232 | 363.1648 | 363.9602 | 374.9573
1812.4729 | 831.9252 | 363.5313 | 364.4273 | 375.0102
1813.4729 | 827.6963 | 363.8806 | 364.7935 | 375.5498
1814.4729 | 837.1024 | 363.9383 | 364.8378 | 375.2722
1815.4729 | 841.1341 | 364.0134 | 364.5974 | 375.2684
1816.4729 | 849.7946 | 363.9763 | 364.3629 | 375.089
1817.4729 | 848.1343 | 363.7218 | 363.9865 | 374.9486
1818.4729 | 846.4514 | 363.7108 | 363.9247 | 375.2639
1819.4729 | 843.2227 | 363.614 | 364.1038 | 375.8033
1820.4729 | 848.0461 | 363.7328 | 364.2553 | 375.9557
1821.4729 | 851.0252 | 363.8202 | 364.6546 | 376.2638
1822.4729 | 851.4807 | 364.1152 | 365.0384 | 376.0215
1823.4729 | 850.8871 | 363.9386 | 365.2554 | 376.0648
1824.4729 | 847.2307 | 364.1127 | 365.3354 | 376.6008
1825.4729 | 844.032 | 364.2839 | 365.6157 | 376.4659
1826.4729 | 843.293 | 364.3108 | 365.8658 | 376.5979
1827.4729 | 848.9017 | 364.6103 | 365.9963 | 376.8363
1828.4729 | 853.5429 | 364.7629 | 366.0747 | 377.113
1829.4729 | 854.1956 | 365.0894 | 365.9293 | 377.2753
1830.4729 | 853.156 | 365.6532 | 366.7711 | 377.6904
1831.4729 | 842.4959 | 365.6681 | 366.8973 | 377.9115
1832.4729 | 844.0966 | 365.7301 | 368.0485 | 378.77
1833.4729 | 843.1857 | 366.0232 | 368.0497 | 378.1827
1834.4729 | 840.8225 | 366.1441 | 368.2681 | 378.1711
1835.4729 | 837.3691 | 366.2383 | 368.197 | 378.2975
1836.4729 | 835.9603 | 365.9864 | 368.8732 | 378.4806
1837.4729 | 841.3303 | 365.9414 | 368.8179 | 378.2908
1838.4729 | 843.7706 | 366.1878 | 368.839 | 378.3555
1839.4729 | 839.379 | 366.3067 | 369.4875 | 380.2109
1840.4729 | 841.2508 | 366.3741 | 369.6531 | 380.2315
1841.4729 | 840.0773 | 366.574 | 369.7043 | 380.2781
1842.4729 | 844.9417 | 366.6296 | 369.8807 | 380.1534
1843.4729 | 846.6756 | 366.4874 | 369.4382 | 379.9474
1844.4729 | 846.1003 | 366.4331 | 369.8021 | 380.2119
1845.4729 | 849.1836 | 366.4651 | 369.8116 | 380.0337
1846.4729 | 852.4764 | 366.5627 | 369.9414 | 380.0429
1847.4729 | 843.72 | 366.7162 | 369.8322 | 379.9733
1848.4729 | 838.9573 | 366.8148 | 369.8694 | 380.4762
1849.4729 | 842.8915 | 367.2223 | 370.2746 | 380.973
1850.4729 | 849.5865 | 367.6766 | 370.1622 | 380.8358
1851.4729 | 848.0113 | 368.2354 | 370.2587 | 380.917
1852.4729 | 851.3015 | 367.7814 | 370.22 | 380.7848
1853.4729 | 842.9449 | 367.6461 | 370.7804 | 380.9914
1854.4729 | 839.376 | 367.6114 | 370.3739 | 381.1721
1855.4729 | 837.2042 | 367.8306 | 370.6018 | 381.7191
1856.4729 | 838.3989 | 368.04 | 370.8644 | 381.7579
1857.4729 | 836.5817 | 367.8209 | 370.6798 | 381.7586
1858.4729 | 840.1246 | 367.4773 | 370.3051 | 381.1233
1859.4729 | 843.5611 | 367.3523 | 369.9603 | 380.7732
1860.4729 | 844.9435 | 367.4217 | 369.9061 | 381.1052
1861.4729 | 846.8093 | 367.4881 | 369.5384 | 380.8234
1862.4885 | 843.0588 | 367.6175 | 369.6923 | 380.9487
1863.4729 | 848.3389 | 367.7995 | 369.7924 | 380.6389
1864.4729 | 853.1102 | 367.8605 | 370.9039 | 381.1161
1865.4729 | 856.2808 | 367.9203 | 370.6627 | 381.2691
1866.4729 | 857.1037 | 368.469 | 370.5301 | 381.8188
1867.4729 | 859.5117 | 368.5945 | 370.8603 | 382.1661
1868.4729 | 857.2496 | 368.6528 | 371.3888 | 382.6107
1869.4729 | 859.7214 | 369.6756 | 371.8219 | 383.9325
1870.4729 | 867.6428 | 369.9342 | 372.5016 | 384.981
1871.4729 | 878.0943 | 369.8317 | 372.5201 | 385.3983
1872.4729 | 882.844 | 370.1186 | 372.628 | 385.8146
1873.4729 | 883.8057 | 370.7827 | 372.7579 | 386.5271
1874.4729 | 877.7457 | 371.7334 | 373.1722 | 386.4593
1875.4729 | 860.6937 | 371.5995 | 373.2106 | 386.6901
1876.4729 | 864.509 | 371.3688 | 373.1052 | 386.8827
1877.4729 | 866.0504 | 370.9804 | 373.1606 | 386.7508
1878.4729 | 866.4131 | 371.0079 | 373.1555 | 386.9231
1879.4729 | 864.327 | 370.9905 | 373.3693 | 387.4514
1880.4729 | 863.0888 | 371.4215 | 373.8565 | 387.6181
1881.4729 | 863.6728 | 371.9307 | 375.0307 | 388.4276
1882.4729 | 864.9804 | 371.9662 | 375.3985 | 388.1697
1883.4729 | 872.2939 | 372.0416 | 376.1678 | 389.0398
1884.4729 | 875.864 | 372.7377 | 376.8257 | 389.5607
1885.4729 | 881.2036 | 373.2392 | 376.8237 | 389.6493
1886.4729 | 885.8642 | 373.9101 | 377.1553 | 390.0995
1887.4729 | 880.6642 | 374.3704 | 377.9663 | 390.7483
1888.4729 | 873.9667 | 374.6437 | 378.182 | 390.6908
1889.4729 | 876.7072 | 374.4615 | 377.8728 | 390.393
1890.4729 | 877.0393 | 374.4969 | 378.0197 | 390.546
1891.4729 | 881.556 | 374.4442 | 378.6615 | 391.2023
1892.4729 | 878.1465 | 374.915 | 378.7648 | 391.1384
1893.4729 | 885.6533 | 375.1822 | 379.1637 | 391.911
1894.4729 | 883.9109 | 375.2964 | 379.0969 | 391.628
1895.4729 | 873.3872 | 375.6812 | 379.3719 | 392.0977
1896.4729 | 872.76 | 375.8413 | 379.5452 | 392.9746
1897.4729 | 870.1509 | 376.2978 | 379.6386 | 392.9815
1898.4729 | 869.2635 | 376.4588 | 379.5758 | 393.3241
1899.4729 | 873.7903 | 376.4376 | 379.7302 | 392.71
1900.4729 | 871.6787 | 377.4764 | 380.9713 | 392.8884
1901.4729 | 872.3037 | 377.7089 | 380.8771 | 393.1133
1902.4729 | 877.62 | 377.8599 | 381.1791 | 393.7761
1903.4729 | 882.6558 | 378.4816 | 381.5521 | 394.0521
1904.4729 | 888.3847 | 378.8369 | 382.603 | 394.4767
1905.4885 | 880.8773 | 379.1674 | 383.3136 | 394.5919
1906.4729 | 878.7989 | 379.6286 | 384.0501 | 395.3084
1907.4729 | 882.6941 | 379.9391 | 384.6908 | 395.3504
1908.4729 | 888.8808 | 380.1208 | 385.1917 | 395.2924
1909.4729 | 894.097 | 380.5258 | 385.5407 | 396.7954
1910.4729 | 905.5767 | 380.8358 | 385.5659 | 396.9639
1911.4729 | 894.7113 | 381.1155 | 385.2523 | 396.9178
1912.4729 | 883.0059 | 381.8272 | 385.1253 | 397.1577
1913.4729 | 871.6551 | 382.3443 | 385.1033 | 397.8399
1914.4729 | 873.0284 | 382.7033 | 385.4009 | 398.5514
1915.4729 | 864.8742 | 383.1247 | 385.2828 | 398.7888
1916.4729 | 853.7775 | 383.1754 | 385.752 | 399.3649
1917.4729 | 845.3007 | 383.5176 | 386 | 400.0089
1918.4729 | 854.3016 | 384.2028 | 386.3369 | 400.8031
1919.4729 | 864.3716 | 384.2776 | 386.6812 | 400.8816
1920.4729 | 872.8276 | 384.7271 | 387.3276 | 400.6484
1921.4729 | 870.265 | 384.8157 | 387.7263 | 400.3929
1922.4729 | 861.9379 | 385.564 | 387.7477 | 400.6149
1923.4729 | 868.7869 | 386.0894 | 387.8994 | 400.7964
1924.4729 | 876.3056 | 385.9478 | 388.2044 | 401.248
1925.4729 | 875.1666 | 385.8948 | 388.7051 | 402.0351
1926.4729 | 870.7983 | 386.246 | 388.5789 | 401.8468
1927.4729 | 874.5672 | 386.8495 | 388.7926 | 402.1749
1928.4729 | 880.659 | 386.9178 | 389.0452 | 402.0872
1929.4729 | 890.9017 | 387.0534 | 388.9048 | 401.6783
1930.4729 | 888.5296 | 387.098 | 388.938 | 401.6527
1931.4729 | 893.0718 | 387.2967 | 388.9792 | 401.922
1932.4729 | 890.4243 | 387.4148 | 389.2917 | 401.9261
1933.4729 | 886.9162 | 387.4413 | 389.7654 | 402.412
1934.4729 | 884.6971 | 387.115 | 389.4892 | 401.8917
1935.4885 | 879.7362 | 387.128 | 389.8768 | 402.2658
1936.4729 | 878.1126 | 386.9723 | 390.4248 | 402.9647
1937.4729 | 875.0153 | 386.692 | 390.5847 | 403.173
1938.4729 | 879.1163 | 386.6708 | 390.1405 | 402.8145
1939.4729 | 874.7691 | 387.1006 | 390.2117 | 402.7591
1940.4885 | 877.6408 | 387.159 | 390.4891 | 402.8713
1941.4885 | 875.2298 | 387.0792 | 390.4705 | 402.482
1942.4729 | 876.3156 | 386.5486 | 390.1746 | 402.1671
1943.4729 | 875.0135 | 385.8349 | 389.4715 | 402.3081
1944.4729 | 880.6195 | 385.5862 | 389.7262 | 403.0932
1945.4729 | 877.554 | 384.9433 | 389.3113 | 402.4087
1946.4729 | 870.0782 | 384.5173 | 389.2882 | 402.9825
1947.4885 | 869.217 | 384.5232 | 389.4272 | 402.7513
1948.4729 | 872.2886 | 384.4033 | 389.4088 | 402.7407
1949.4729 | 873.1501 | 384.741 | 389.2256 | 402.3561
1950.4729 | 877.0037 | 385.3718 | 389.5602 | 402.1003
1951.4729 | 882.7219 | 385.813 | 389.6341 | 402.2088
1952.4729 | 881.0363 | 386.2035 | 390.2265 | 402.4292
1953.4729 | 877.999 | 386.3973 | 390.3312 | 402.7021
1954.4729 | 886.6395 | 386.0844 | 390.8537 | 402.7513
1955.4729 | 880.971 | 386.1254 | 390.7519 | 402.3521
1956.4729 | 868.7353 | 386.6926 | 391.0334 | 403.0454
1957.4729 | 864.5575 | 387.5984 | 392.0527 | 403.3098
1958.4729 | 852.9265 | 388.0164 | 392.4622 | 404.0613
1959.4729 | 853.7357 | 388.0219 | 392.2041 | 404.0765
1960.4729 | 866.4956 | 388.0877 | 392.2807 | 404.9641
1961.4729 | 876.2931 | 387.9262 | 392.2609 | 405.3674
1962.4729 | 882.4814 | 388.3069 | 392.9309 | 405.4512
1963.4729 | 882.2689 | 388.5535 | 392.9817 | 405.9844
1964.4729 | 873.0069 | 388.6195 | 392.7681 | 406.336
1965.4885 | 872.5075 | 388.9259 | 392.9442 | 406.2949
1966.4729 | 865.1521 | 388.8545 | 392.8662 | 407.1513
1967.4729 | 875.4913 | 389.5318 | 393.739 | 408.0414
1968.4729 | 885.5804 | 390.0359 | 393.9192 | 408.4353
1969.4729 | 887.7494 | 389.9761 | 393.9055 | 408.8783
1970.4729 | 892.8735 | 390.6827 | 394.2897 | 408.6754
1971.4729 | 899.7297 | 391.2866 | 394.5902 | 408.3671
1972.4729 | 896.9243 | 391.7236 | 394.8365 | 408.2132
1973.4729 | 890.5605 | 392.0198 | 395.2303 | 408.3345
1974.4729 | 883.0043 | 392.7597 | 396.0698 | 408.6137
1975.4729 | 883.1559 | 392.873 | 396.452 | 409.1429
1976.4729 | 888.778 | 392.798 | 397.1778 | 409.6075
1977.4729 | 888.2717 | 392.7794 | 397.2373 | 410.1607
1978.4729 | 884.8083 | 392.8903 | 397.3784 | 411.0453
1979.4729 | 881.6892 | 393.0711 | 397.6125 | 411.7588
1980.4729 | 881.2726 | 393.1581 | 397.6269 | 412.062
1981.4729 | 888.4564 | 392.9426 | 397.7982 | 411.7428
1982.4729 | 881.9043 | 393.2986 | 397.6935 | 411.9213
1983.4885 | 868.4631 | 393.9268 | 397.4732 | 411.7245
1984.4729 | 866.9637 | 393.4864 | 397.3122 | 412.0796
1985.4729 | 872.0115 | 393.0548 | 397.2467 | 412.1345
1986.4729 | 872.8461 | 393.0049 | 397.522 | 412.818
1987.4729 | 874.0262 | 393.0295 | 398.1689 | 413.2313
1988.4729 | 875.6506 | 393.1262 | 398.4293 | 413.6448
1989.4729 | 877.7829 | 394.4198 | 398.7591 | 413.4125
1990.4729 | 877.8889 | 395.167 | 398.854 | 413.2846
1991.4729 | 882.5114 | 395.5148 | 398.6797 | 413.2721
1992.4729 | 875.8219 | 395.219 | 398.7986 | 413.5398
1993.4729 | 872.1432 | 395.3222 | 398.8166 | 412.9834
1994.4729 | 867.0019 | 395.0314 | 398.4815 | 412.5995
1995.4885 | 863.411 | 394.7816 | 398.5074 | 412.6054
1996.4729 | 864.6634 | 394.7149 | 398.9393 | 412.2218
1997.4729 | 862.3847 | 394.8323 | 398.6571 | 412.7303
1998.4729 | 867.778 | 395.5014 | 399.1622 | 412.7465
1999.4729 | 870.6235 | 395.1451 | 398.9945 | 413.0985
2000.4729 | 870.0737 | 394.8026 | 398.9269 | 412.9726
2001.4729 | 852.9961 | 394.6661 | 399.1215 | 413.3021
2002.4729 | 850.2373 | 394.7246 | 398.9339 | 413.2426
2003.4729 | 851.1108 | 394.6154 | 399.8531 | 413.297
2004.4729 | 850.6595 | 395.6018 | 399.808 | 415.0387
2005.4729 | 845.9316 | 396.2153 | 400.7939 | 415.2114
2006.4729 | 843.0092 | 395.9439 | 401.2537 | 416.2788
2007.4729 | 839.1611 | 396.0147 | 402.1914 | 416.8413
2008.4729 | 852.8188 | 395.9588 | 402.5909 | 416.923
2009.4729 | 857.4772 | 395.4999 | 402.151 | 416.9442
2010.4729 | 867.5334 | 395.3265 | 402.2353 | 416.7837
2011.4729 | 873.9261 | 395.5178 | 402.1379 | 416.7679
2012.4729 | 865.2962 | 395.739 | 402.1613 | 416.729
2013.4729 | 869.7377 | 395.963 | 401.9073 | 416.874
2014.4729 | 873.4827 | 396.3847 | 402.8665 | 416.9672
2015.4729 | 879.8825 | 396.5706 | 403.1641 | 416.9728
2016.4729 | 885.0649 | 396.477 | 403.7762 | 416.7441
2017.4729 | 885.8653 | 396.6586 | 403.8758 | 417.0929
2018.4729 | 876.5474 | 397.2973 | 403.8176 | 417.1617
2019.4729 | 865.5206 | 397.6381 | 403.4461 | 417.0031
2020.4729 | 865.6985 | 398.2392 | 403.4505 | 416.722
2021.4729 | 868.1295 | 398.3945 | 403.121 | 416.4813
2022.4729 | 867.7599 | 398.5001 | 403.0354 | 416.2428
2023.4729 | 863.459 | 398.8712 | 403.3027 | 416.6111
2024.4729 | 859.6831 | 399.2646 | 403.3366 | 417.1183
2025.4885 | 855.7995 | 399.3281 | 403.3189 | 417.5499
2026.4729 | 857.3332 | 400.0562 | 403.6309 | 418.0346
2027.4729 | 842.7923 | 400.3616 | 403.4764 | 417.8321
2028.4729 | 828.949 | 401.2084 | 404.0283 | 419.0258
2029.4729 | 817.1324 | 401.9299 | 404.484 | 420.1513
2030.4729 | 825.2824 | 403.4797 | 405.2583 | 421.1473
2031.4729 | 833.7774 | 403.8999 | 406.1042 | 421.2514
2032.4729 | 837.1625 | 404.2087 | 406.3049 | 421.8492
2033.4729 | 819.6075 | 404.7038 | 407.1197 | 421.4373
2034.4729 | 809.2813 | 404.6494 | 407.2656 | 422.1338
2035.4729 | 802.5822 | 404.734 | 407.7276 | 422.4192
2036.4729 | 819.8737 | 404.711 | 408.0763 | 422.4886
2037.4729 | 836.5355 | 404.9047 | 408.1517 | 422.0605
2038.4729 | 838.652 | 405.3448 | 408.1343 | 421.7896
2039.4729 | 846.7749 | 405.4782 | 409.5883 | 423.4323
2040.4729 | 847.1662 | 405.5777 | 409.8265 | 423.4417
2041.4729 | 839.9003 | 405.6947 | 409.5777 | 422.9739
2042.4729 | 838.2461 | 405.7996 | 409.2527 | 423.4089
2043.4729 | 841.788 | 405.6533 | 409.2953 | 423.517
2044.4729 | 840.7934 | 405.4465 | 409.115 | 422.7238
2045.4729 | 849.0669 | 405.6302 | 410.1118 | 423.3961
2046.4729 | 852.9212 | 405.4375 | 410.0986 | 423.1275
2047.4729 | 848.3991 | 404.9732 | 409.8309 | 423.0725
2048.4729 | 852.7196 | 404.6522 | 409.2252 | 422.4042
2049.4729 | 852.2759 | 404.6765 | 408.6591 | 422.2178
2050.4729 | 848.6957 | 404.0878 | 408.4286 | 422.1729
2051.4729 | 851.5979 | 404.5857 | 408.9648 | 422.2785
2052.4729 | 857.62 | 404.611 | 408.854 | 422.7237
2053.4729 | 869.4713 | 404.5113 | 408.5969 | 422.5058
2054.4729 | 878.2891 | 405.0299 | 408.1174 | 422.288
2055.4729 | 875.5598 | 405.7464 | 408.3595 | 422.586
2056.4729 | 869.0498 | 405.852 | 408.3149 | 422.3873
2057.4729 | 854.9044 | 405.6585 | 408.3956 | 422.9259
2058.4729 | 854.9807 | 405.6457 | 408.4119 | 422.7661
2059.4729 | 865.2245 | 405.7949 | 408.1187 | 423.4009
2060.4729 | 862.1027 | 406.0807 | 408.397 | 423.6912
2061.4729 | 859.0151 | 406.9383 | 408.6144 | 424.3987
2062.4729 | 844.2595 | 406.8385 | 408.7793 | 423.8785
2063.4729 | 824.2028 | 407.0656 | 409.4986 | 424.3302
2064.4729 | 831.3687 | 407.8218 | 410.303 | 425.2768
2065.4729 | 842.4907 | 408.3152 | 410.3541 | 425.8848
2066.4729 | 854.0124 | 408.3288 | 410.7494 | 425.4238
2067.4729 | 864.3085 | 408.0074 | 410.6024 | 425.6056
2068.4729 | 862.0977 | 407.9232 | 410.4061 | 425.3441
2069.4729 | 873.4297 | 407.7086 | 410.5161 | 425.1327
2070.4729 | 868.5105 | 407.791 | 410.5873 | 425.3892
2071.4729 | 873.928 | 407.514 | 410.3564 | 425.5661
2072.4729 | 882.9113 | 407.9091 | 411.2776 | 425.826
2073.4729 | 883.4512 | 408.0148 | 411.5221 | 425.746
2074.4729 | 880.2342 | 408.361 | 411.4381 | 426.0625
2075.4729 | 880.8865 | 408.3769 | 411.5185 | 426.7314
2076.4729 | 880.0382 | 408.681 | 411.4525 | 426.8334
2077.4729 | 883.5672 | 408.8944 | 411.6635 | 427.1449
2078.4729 | 887.6762 | 408.8824 | 411.5064 | 426.6608
2079.4729 | 889.3263 | 408.7432 | 411.5045 | 426.6054
2080.4729 | 891.5814 | 409.242 | 411.6054 | 426.7121
2081.4729 | 896.8519 | 409.1458 | 411.6937 | 426.2835
2082.4729 | 886.5221 | 409.3844 | 411.2849 | 426.5694
2083.4729 | 886.4344 | 409.5369 | 411.5399 | 426.95
2084.4729 | 890.8613 | 409.2154 | 411.3631 | 427.3593
2085.4729 | 879.4027 | 408.8298 | 410.9105 | 426.8438
2086.4729 | 887.4615 | 409.6031 | 410.8762 | 426.5901
2087.4729 | 883.8776 | 409.9227 | 411.0038 | 427.0588
2088.4729 | 863.7049 | 410.3558 | 411.9043 | 427.6565
2089.4729 | 860.5929 | 410.0621 | 412.1213 | 427.7244
2090.4729 | 855.8886 | 410.1753 | 412.2471 | 427.7172
2091.4729 | 864.5164 | 410.2899 | 411.9723 | 427.2575
2092.4729 | 861.5727 | 410.2901 | 412.0407 | 427.233
2093.4729 | 844.4555 | 410.2624 | 412.4741 | 427.0924
2094.4729 | 842.753 | 410.5054 | 412.8109 | 427.6727
2095.4729 | 855.4433 | 411.0318 | 413.289 | 429.0734
2096.4729 | 871.0886 | 411.0288 | 413.85 | 429.2862
2097.4729 | 881.3949 | 411.1413 | 414.2424 | 429.1788
2098.4729 | 878.1139 | 411.1158 | 414.5014 | 429.4017
2099.4729 | 886.7554 | 411.5768 | 414.4627 | 430.1321
2100.4729 | 889.5223 | 411.3062 | 414.5631 | 430.2004
2101.4729 | 883.575 | 410.9853 | 414.2779 | 430.1007
2102.4729 | 891.3513 | 411.1545 | 414.4379 | 430.3237
2103.4729 | 892.222 | 411.4958 | 414.5743 | 430.3941
2104.4729 | 894.9724 | 411.5133 | 414.7953 | 430.0576
2105.4729 | 891.2237 | 411.5689 | 415.0972 | 430.581
2106.4729 | 892.1103 | 411.9602 | 415.0502 | 430.6164
2107.4729 | 898.9256 | 411.8185 | 415.4645 | 430.4706
2108.4729 | 893.444 | 412.1819 | 415.5589 | 430.2867
2109.4729 | 892.8007 | 412.6425 | 415.8824 | 430.1962
2110.4729 | 888.5611 | 412.5892 | 415.5202 | 430.5411
2111.4729 | 870.0509 | 412.1788 | 415.3165 | 430.2307
2112.4729 | 857.9508 | 411.8897 | 414.7341 | 429.8997
2113.4729 | 860.0413 | 411.5997 | 414.0631 | 429.3249
2114.4729 | 861.2717 | 411.3838 | 413.667 | 429.1801
2115.4729 | 859.9824 | 411.5048 | 413.9171 | 428.8799
2116.4729 | 863.9396 | 411.451 | 414.2057 | 429.0259
2117.4729 | 860.6531 | 411.6535 | 414.2986 | 428.4676
2118.4729 | 866.3684 | 411.4976 | 414.2742 | 428.4572
2119.4729 | 871.5506 | 411.8319 | 414.4204 | 428.2342
2120.4729 | 875.3747 | 411.6177 | 414.504 | 428.2557
2121.4729 | 882.3452 | 411.8641 | 414.2662 | 428.1023
2122.4729 | 871.3834 | 411.9812 | 414.2294 | 427.7902
2123.4729 | 879.6696 | 411.8447 | 414.1785 | 427.9527
2124.4729 | 892.2454 | 411.6021 | 414.4431 | 427.4059
2125.4729 | 894.3876 | 411.7006 | 414.8032 | 427.4911
2126.4729 | 880.3532 | 411.6854 | 414.7509 | 427.2269
2127.4729 | 892.1607 | 411.617 | 414.5703 | 427.2764
2128.4729 | 899.2985 | 412.1568 | 414.4489 | 428.0397
2129.4729 | 905.7187 | 411.9167 | 414.647 | 428.0769
2130.4729 | 901.4753 | 412.2792 | 414.7245 | 427.9829
2131.4729 | 908.4705 | 412.3444 | 414.6168 | 427.872
2132.4729 | 900.5206 | 412.6412 | 415.0897 | 427.6204
2133.4729 | 900.7245 | 412.3334 | 415.264 | 428.0198
2134.4729 | 889.9485 | 412.5072 | 415.6121 | 428.315
2135.4729 | 894.0811 | 412.8611 | 416.5602 | 428.4158
2136.4729 | 899.1201 | 413.082 | 416.5313 | 428.8879
2137.4729 | 900.7867 | 413.3502 | 417.5305 | 428.7489
2138.4729 | 891.8336 | 413.5358 | 417.4994 | 429.2737
2139.4729 | 891.9449 | 413.3057 | 417.2438 | 429.3927
2140.4729 | 885.4641 | 413.681 | 417.02 | 430.27
2141.4729 | 888.468 | 413.5692 | 417.0533 | 430.6455
2142.4729 | 884.3929 | 413.6746 | 416.6299 | 430.3532
2143.4729 | 873.7824 | 413.7515 | 416.4798 | 430.8783
2144.4729 | 875.1373 | 413.7444 | 416.4799 | 430.9225
2145.4729 | 885.6502 | 413.9912 | 415.9406 | 430.5753
2146.4729 | 896.5186 | 414.1091 | 415.6627 | 430.6432
2147.4729 | 891.8834 | 414.0199 | 415.5305 | 429.886
2148.4729 | 883.904 | 413.7036 | 415.3293 | 430.3236
2149.4729 | 882.4714 | 414.1664 | 415.9176 | 430.5701
2150.4729 | 886.5305 | 413.893 | 416.1907 | 430.6793
2151.4729 | 883.877 | 413.6272 | 415.7914 | 430.4496
2152.4729 | 883.6724 | 413.2386 | 415.3808 | 430.7908
2153.4729 | 876.8034 | 413.7763 | 416.1852 | 431.4715
2154.4729 | 878.9281 | 413.9192 | 416.2522 | 430.7819
2155.4729 | 870.9858 | 413.9003 | 416.452 | 430.6509
2156.4729 | 875.806 | 413.845 | 416.4287 | 430.7313
2157.4729 | 882.9024 | 413.7705 | 416.4501 | 430.1364
2158.4729 | 889.4539 | 413.6247 | 415.9997 | 429.2879
2159.4729 | 884.7327 | 413.6952 | 416.0633 | 428.9465
2160.4729 | 899.038 | 413.9182 | 415.6682 | 428.9116
2161.4729 | 895.7459 | 414.6103 | 416.2479 | 428.8858
2162.4729 | 900.826 | 414.5326 | 416.1387 | 428.2934
2163.4729 | 905.4087 | 414.3332 | 416.5528 | 428.5342
2164.4729 | 917.7042 | 414.1848 | 416.4194 | 428.0703
2165.4729 | 905.9152 | 413.7522 | 415.837 | 428.01
2166.4729 | 901.0234 | 413.9893 | 415.5808 | 428.0125
2167.4729 | 901.1396 | 414.1955 | 415.2889 | 427.6805
2168.4729 | 888.4083 | 414.5728 | 415.1419 | 427.8102
2169.4729 | 900.8149 | 414.5859 | 415.4629 | 428.1155
2170.4729 | 896.1284 | 414.3866 | 415.3547 | 427.9353
2171.4729 | 887.4089 | 414.5706 | 415.365 | 427.2209
2172.4729 | 884.8288 | 414.1003 | 414.7315 | 426.412
2173.4729 | 884.2148 | 413.9198 | 415.0108 | 425.9486
2174.4729 | 887.7983 | 413.6617 | 414.4862 | 425.3644
2175.4729 | 887.9417 | 414.585 | 414.6417 | 425.2344
2176.4729 | 888.7906 | 414.5784 | 414.8781 | 425.2785
2177.4729 | 888.191 | 415.0129 | 415.169 | 425.6468
2178.4729 | 890.8426 | 415.3451 | 415.5897 | 426.1557
2179.4729 | 890.0178 | 415.4298 | 416.3825 | 427.221
2180.4729 | 888.4335 | 415.9435 | 416.6488 | 427.1242
2181.4729 | 888.3419 | 415.8361 | 416.758 | 427.4384
2182.4729 | 892.8805 | 416.1164 | 416.9928 | 427.6333
2183.4729 | 888.7821 | 416.4452 | 416.6484 | 428.1722
2184.4729 | 886.9145 | 416.7676 | 417.1614 | 428.2668
2185.4729 | 891.1944 | 417.3584 | 417.2195 | 428.3925
2186.4729 | 897.4131 | 417.3803 | 417.1269 | 428.7523
2187.4729 | 890.751 | 417.2079 | 417.0598 | 428.8715
2188.4729 | 906.5193 | 416.7091 | 416.8629 | 428.9404
2189.4729 | 896.5888 | 416.9252 | 416.5571 | 428.4944
2190.4729 | 894.2652 | 417.4542 | 417.2481 | 428.6685
2191.4729 | 889.6927 | 417.1115 | 417.278 | 428.4998
2192.4729 | 894.9705 | 417.2375 | 417.3239 | 428.9528
2193.4729 | 907.3966 | 416.8173 | 417.0772 | 428.7787
2194.4729 | 906.5489 | 416.7591 | 417.054 | 428.4747
2195.4729 | 907.1712 | 417.0989 | 417.3756 | 428.2298
2196.4729 | 906.8088 | 417.3931 | 417.251 | 428.2112
2197.4729 | 901.6338 | 417.499 | 417.2101 | 428.7224
2198.4729 | 895.018 | 417.6079 | 417.8616 | 428.8143
2199.4729 | 892.3706 | 417.3262 | 418.126 | 428.7912
2200.4729 | 895.9801 | 418.153 | 418.1947 | 428.7467
2201.4729 | 897.4097 | 417.8838 | 417.9216 | 428.3158
2202.4729 | 902.7848 | 418.1937 | 417.5965 | 428.1846
2203.4729 | 898.5458 | 418.3795 | 417.7621 | 428.5718
2204.4729 | 892.5146 | 418.5918 | 418.3818 | 428.8131
2205.4729 | 900.8198 | 418.6745 | 418.5665 | 428.7721
2206.4729 | 894.2809 | 418.2458 | 419.9448 | 429.649
2207.4729 | 898.4363 | 417.7859 | 419.4377 | 429.7284
2208.4729 | 905.1658 | 417.3364 | 419.0837 | 430.1948
2209.4729 | 895.1376 | 417.1678 | 418.7384 | 429.7818
2210.4729 | 889.232 | 417.422 | 418.6766 | 429.5708
2211.4729 | 890.5563 | 417.301 | 418.4275 | 428.7622
2212.4729 | 895.9216 | 417.2213 | 418.4825 | 428.718
2213.4729 | 903.6112 | 417.912 | 418.6288 | 428.8476
2214.4729 | 898.1701 | 418.108 | 418.3798 | 428.6586
2215.4729 | 903.7488 | 418.1333 | 418.3783 | 428.6613
2216.4729 | 911.4799 | 418.2735 | 418.5157 | 428.4872
2217.4729 | 903.9476 | 418.4125 | 419.2522 | 428.9517
2218.4729 | 902.0201 | 418.2896 | 419.1426 | 429.0758
2219.4729 | 902.2573 | 418.0817 | 419.0104 | 429.1128
2220.4729 | 899.9013 | 417.7361 | 418.5332 | 429.3493
2221.4729 | 904.8631 | 417.7919 | 418.1974 | 429.2514
2222.4729 | 903.4748 | 418.547 | 418.8567 | 429.8887
2223.4729 | 898.9725 | 418.3692 | 418.8304 | 429.6076
2224.4729 | 903.0108 | 418.5864 | 418.4419 | 429.5765
2225.4729 | 905.2907 | 418.5835 | 418.1118 | 429.4865
2226.4729 | 908.6285 | 418.6552 | 417.833 | 429.2349
2227.4729 | 905.5195 | 419.4065 | 418.075 | 428.8237
2228.4729 | 913.6777 | 419.7714 | 418.5723 | 429.1729
2229.4729 | 901.2173 | 420.1957 | 418.4693 | 428.5471
2230.4729 | 892.9123 | 420.1473 | 418.4226 | 428.3263
2231.4729 | 885.6567 | 420.1008 | 418.8399 | 428.4026
2232.4729 | 891.2254 | 420.3194 | 418.879 | 428.6702
2233.4729 | 897.1848 | 420.2006 | 419.115 | 429.0516
2234.4729 | 906.5742 | 420.5051 | 419.6796 | 429.7877
2235.4729 | 892.6013 | 421.6386 | 420.6899 | 429.9812
2236.4729 | 893.4224 | 421.6997 | 421.1059 | 430.0852
2237.4729 | 887.1378 | 421.7546 | 420.9903 | 430.026
2238.4729 | 880.7039 | 422.12 | 421.621 | 430.6239
2239.4729 | 871.8587 | 422.1378 | 421.3018 | 430.8761
2240.4729 | 871.3944 | 421.7931 | 420.9874 | 430.6085
2241.4729 | 875.4424 | 421.9737 | 421.095 | 430.9995
2242.4729 | 872.8366 | 421.9517 | 421.1894 | 430.8404
2243.4729 | 888.9442 | 421.595 | 421.0567 | 430.6075
2244.4729 | 893.3617 | 421.2901 | 421.175 | 429.7109
2245.4729 | 897.3095 | 421.2371 | 421.0146 | 429.2232
2246.4729 | 894.5071 | 421.2755 | 420.9755 | 429.8539
2247.4729 | 903.4078 | 420.9305 | 420.7786 | 429.4022
2248.4729 | 902.8752 | 420.8306 | 420.4704 | 429.1354
2249.4729 | 897.2653 | 420.8285 | 420.4629 | 429.3715
2250.4729 | 895.3744 | 420.8244 | 420.318 | 429.3101
2251.4729 | 898.7481 | 420.4397 | 419.9199 | 428.8135
2252.4729 | 909.1767 | 420.4733 | 420.0257 | 428.9336
2253.4729 | 903.7762 | 420.4337 | 420.1308 | 429.063
2254.4729 | 907.4665 | 420.8856 | 420.4519 | 429.5746
2255.4729 | 906.092 | 421.115 | 420.9764 | 429.9796
2256.4729 | 913.2009 | 420.9409 | 420.9581 | 430.0368
2257.4729 | 915.5464 | 422.2298 | 421.4947 | 430.2171
2258.4729 | 894.098 | 421.9043 | 421.3974 | 429.8952
2259.4729 | 884.3215 | 422.0353 | 421.3638 | 429.9745
2260.4729 | 891.599 | 422.4682 | 421.6718 | 429.8576
2261.4729 | 894.1059 | 422.3498 | 421.8787 | 430.1507
2262.4729 | 890.3636 | 422.1434 | 421.4928 | 429.5858
2263.4729 | 892.0436 | 421.8814 | 421.4671 | 429.3372
2264.4729 | 887.2517 | 421.7903 | 421.4732 | 429.0436
2265.4729 | 878.5976 | 421.8328 | 421.053 | 429.04
2266.4729 | 878.4334 | 421.4947 | 420.8136 | 429.0471
2267.4729 | 879.1334 | 421.1684 | 420.5446 | 428.7517
2268.4729 | 879.5785 | 421.5283 | 420.6085 | 428.5732
2269.4729 | 885.4887 | 421.9535 | 420.4489 | 428.3987
2270.4729 | 888.7686 | 422.334 | 420.7593 | 428.862
2271.4729 | 898.5179 | 422.2575 | 420.7925 | 429.0436
2272.4729 | 895.8146 | 422.3164 | 420.5161 | 429.2561
2273.4729 | 900.8035 | 422.2497 | 420.9065 | 429.2817
2274.4729 | 908.1936 | 421.9997 | 421.1363 | 429.5535
2275.4729 | 910.4392 | 422.057 | 420.8693 | 429.5326
2276.4729 | 918.5175 | 422.0977 | 420.5248 | 429.2637
2277.4729 | 906.6379 | 422.0449 | 420.2947 | 428.9748
2278.4729 | 895.009 | 422.3308 | 420.4235 | 429.1553
2279.4729 | 894.6591 | 422.6695 | 420.3662 | 428.8932
2280.4729 | 902.5032 | 422.6814 | 420.243 | 428.7013
2281.4729 | 894.3213 | 422.61 | 420.031 | 428.665
2282.4729 | 897.998 | 422.7029 | 419.8642 | 428.5334
2283.4729 | 904.7234 | 423.0742 | 420.7705 | 428.6354
2284.4729 | 901.5338 | 423.3473 | 420.7337 | 428.528
2285.4729 | 899.3394 | 423.7666 | 421.0201 | 429.0111
2286.4729 | 894.233 | 424.0304 | 422.2685 | 428.935
2287.4729 | 889.6652 | 424.4113 | 422.3816 | 429.3654
2288.4729 | 899.9487 | 424.0542 | 422.3321 | 429.6514
2289.4729 | 896.6679 | 424.2275 | 422.8839 | 429.8475
2290.4729 | 901.3807 | 424.7205 | 423.0452 | 429.9897
2291.4729 | 894.6885 | 424.76 | 423.4076 | 429.9617
2292.4729 | 892.7876 | 425.7028 | 423.8717 | 430.0605
2293.4729 | 889.7163 | 425.4204 | 424.35 | 430.3515
2294.4729 | 886.6959 | 425.3182 | 424.2513 | 430.9053
2295.4729 | 883.7294 | 425.1389 | 424.4934 | 432.1952
2296.4729 | 889.6931 | 425.543 | 425.0922 | 432.1437
2297.4729 | 891.1175 | 425.9816 | 425.5304 | 432.537
2298.4729 | 889.9734 | 426.8281 | 425.5873 | 432.2533
2299.4729 | 883.1629 | 426.7332 | 425.4568 | 432.0773
2300.4729 | 889.496 | 426.5899 | 425.6142 | 432.148
2301.4729 | 899.6726 | 426.7315 | 425.6797 | 432.5984
2302.4729 | 901.8305 | 426.8745 | 425.6273 | 432.8802
2303.4729 | 898.8988 | 426.9 | 425.9376 | 432.8556
2304.4729 | 899.0154 | 426.8084 | 425.6774 | 432.6928
2305.4729 | 905.9147 | 426.2287 | 425.6172 | 432.4035
2306.4729 | 911.5197 | 427.128 | 425.5621 | 432.5826
2307.4729 | 909.4929 | 427.114 | 426.1254 | 433.1073
2308.4729 | 912.2968 | 427.4665 | 426.3437 | 433.0158
2309.4729 | 908.6663 | 427.2447 | 426.4498 | 433.103
2310.4729 | 897.3536 | 427.1488 | 426.5205 | 433.3707
2311.4729 | 884.8925 | 427.2687 | 426.9236 | 433.6685
2312.4729 | 882.5532 | 426.9143 | 426.7775 | 434.0085
2313.4729 | 882.6008 | 426.7357 | 426.4052 | 434.427
2314.4729 | 887.6141 | 426.739 | 425.9919 | 434.723
2315.4729 | 896.3211 | 426.0481 | 425.5294 | 434.2138
2316.4729 | 891.1675 | 425.6178 | 425.1872 | 433.5067
2317.4729 | 877.8391 | 425.2379 | 424.4673 | 433.1426
2318.4729 | 873.6692 | 425.722 | 423.8906 | 432.897
2319.4729 | 875.38 | 425.8723 | 424.5679 | 433.0688
2320.4729 | 877.3786 | 425.3488 | 424.9963 | 432.9451
2321.4729 | 885.0229 | 424.8254 | 424.4254 | 432.2657
2322.4729 | 891.9397 | 424.3755 | 424.935 | 432.1879
2323.4729 | 888.4886 | 424.5013 | 424.6799 | 431.9913
2324.4729 | 881.0616 | 424.6454 | 424.8654 | 431.8417
2325.4729 | 875.7517 | 424.6983 | 424.9479 | 431.8673
2326.4729 | 878.1816 | 425.1695 | 424.2511 | 432.2022
2327.4729 | 887.5329 | 425.2736 | 424.9357 | 432.9319
2328.4729 | 884.3548 | 425.3948 | 424.9438 | 432.9891
2329.4729 | 891.4654 | 425.611 | 425.4588 | 432.9601
2330.4729 | 893.1313 | 425.9657 | 425.7673 | 432.6553
2331.4729 | 903.673 | 425.8849 | 425.687 | 432.3882
2332.4729 | 910.4841 | 426.6149 | 426.1368 | 432.542
2333.4729 | 903.1333 | 426.6664 | 426.4366 | 432.8064
2334.4729 | 910.9481 | 426.6557 | 426.7823 | 433.1626
2335.4729 | 907.48 | 426.7958 | 427.3197 | 433.3014
2336.4729 | 893.107 | 426.4256 | 427.6879 | 433.7543
2337.4729 | 891.0689 | 426.3681 | 426.9338 | 433.5784
2338.4729 | 891.1144 | 426.4711 | 427.0005 | 433.6981
2339.4729 | 883.2195 | 427.0502 | 427.3353 | 433.7066
2340.4729 | 879.2009 | 427.0879 | 427.3226 | 433.7991
2341.4729 | 883.3556 | 427.1302 | 427.0007 | 433.5486
2342.4729 | 873.3429 | 427.1556 | 426.7802 | 432.9352
2343.4729 | 860.3201 | 426.9823 | 426.9567 | 432.6646
2344.4729 | 850.6285 | 426.7927 | 427.1847 | 432.4421
2345.4729 | 852.4539 | 426.6779 | 426.8979 | 432.072
2346.4729 | 848.5404 | 426.2323 | 426.5122 | 431.2884
2347.4729 | 842.3682 | 426.0406 | 426.5004 | 431.819
2348.4729 | 849.2931 | 425.6825 | 426.5043 | 431.4146
2349.4729 | 863.395 | 425.043 | 425.8366 | 430.7832
2350.4729 | 858.9918 | 425.0502 | 425.7755 | 430.3455
2351.4729 | 863.8085 | 425.8695 | 425.8667 | 429.802
2352.4729 | 880.8652 | 425.7383 | 425.2312 | 429.6003
2353.4729 | 893.684 | 426.0015 | 425.398 | 429.5735
2354.4729 | 873.1453 | 425.9131 | 425.0523 | 429.4193
2355.4729 | 843.2017 | 425.5645 | 425.1807 | 429.3047
2356.4729 | 851.5339 | 425.3786 | 425.5112 | 429.8821
2357.4729 | 848.153 | 425.2102 | 425.6552 | 430.1023
2358.4729 | 837.5539 | 425.7549 | 425.559 | 429.7056
2359.4729 | 838.1213 | 425.7792 | 425.1665 | 429.1501
2360.4729 | 854.1513 | 426.1424 | 425.4549 | 429.6493
2361.4729 | 881.1681 | 426.0725 | 425.5628 | 429.6134
2362.4729 | 884.9941 | 425.6964 | 425.4241 | 429.4547
2363.4729 | 875.994 | 425.5743 | 425.0253 | 429.1881
2364.4729 | 875.6178 | 426.0458 | 424.6351 | 429.0113
2365.4729 | 867.8901 | 426.1932 | 424.9153 | 429.0342
2366.4729 | 872.4151 | 425.9258 | 425.2003 | 428.9196
2367.4729 | 867.6052 | 425.5764 | 425.0578 | 428.5983
2368.4729 | 877.5495 | 425.4454 | 424.882 | 428.5045
2369.4729 | 879.1065 | 424.9093 | 424.6936 | 428.5221
2370.4729 | 871.7641 | 425.3437 | 424.4083 | 428.2688
2371.4729 | 877.4727 | 425.0448 | 424.1236 | 428.0359
2372.4729 | 869.4725 | 425.3146 | 424.6767 | 428.0955
2373.4729 | 862.0826 | 425.6051 | 424.7068 | 428.328
2374.4729 | 863.6675 | 425.7606 | 424.818 | 428.2272
2375.4729 | 874.2268 | 425.9093 | 424.9083 | 427.9394
2376.4729 | 877.987 | 426.0398 | 425.0084 | 427.9242
2377.4729 | 883.3967 | 425.9851 | 424.8326 | 427.579
2378.4729 | 880.9236 | 425.9925 | 425.1441 | 427.1155
2379.4729 | 890.1242 | 425.5304 | 425.0094 | 426.7507
2380.4729 | 904.2221 | 425.6539 | 424.4742 | 426.8289
2381.4729 | 900.6684 | 425.2173 | 424.3925 | 427.5968
2382.4729 | 894.7524 | 425.0576 | 424.4108 | 428.5807
2383.4729 | 907.0166 | 425.0305 | 424.6685 | 429.3459
2384.4729 | 902.9051 | 424.9775 | 424.102 | 430.0082
2385.4729 | 911.6862 | 425.0504 | 424.2738 | 429.936
2386.4729 | 922.1765 | 425.1391 | 424.8455 | 430.8882
2387.4729 | 919.3802 | 425.4658 | 424.652 | 430.9971
2388.4729 | 910.0154 | 425.8376 | 424.806 | 431.1051
2389.4729 | 910.3673 | 426.3359 | 424.7971 | 430.9512
2390.4729 | 911.2885 | 426.1729 | 425.3424 | 431.1014
2391.4729 | 902.4714 | 426.6555 | 426.3284 | 431.1276
2392.4729 | 910.6578 | 426.1638 | 426.2001 | 431.3064
2393.4729 | 908.7734 | 426.2117 | 426.4526 | 432.2416
2394.4729 | 903.8908 | 426.4065 | 426.6272 | 432.6427
2395.4729 | 895.9433 | 426.781 | 428.1068 | 432.9534
2396.4729 | 898.7427 | 426.9042 | 428.6896 | 433.5469
2397.4729 | 903.0017 | 427.1413 | 428.3659 | 434.3454
2398.4729 | 900.8212 | 427.1736 | 428.5392 | 434.2437
2399.4729 | 895.6613 | 427.017 | 428.7113 | 434.2879
2400.4729 | 900.0897 | 426.6141 | 428.644 | 434.3291
2401.4885 | 898.635 | 426.0466 | 428.0429 | 433.8412
2402.4729 | 900.1512 | 425.6851 | 427.975 | 433.4786
2403.4729 | 908.2051 | 425.3747 | 427.7397 | 432.6745
2404.4729 | 911.1812 | 425.6913 | 427.3595 | 432.1499
2405.4729 | 901.7017 | 425.6889 | 427.085 | 431.7254
2406.4729 | 895.2269 | 425.6193 | 426.8017 | 431.3449
2407.4729 | 903.1813 | 425.4718 | 426.8885 | 430.9977
2408.4729 | 906.4508 | 425.3017 | 426.7351 | 431.0308
2409.4729 | 913.6957 | 425.5887 | 427.1098 | 431.5638
2410.4729 | 913.4721 | 425.602 | 427.038 | 431.3857
2411.4729 | 900.7245 | 425.6253 | 427.0769 | 431.7524
2412.4729 | 877.7924 | 426.196 | 426.9952 | 431.8344
2413.4729 | 861.2775 | 427.2228 | 427.7833 | 431.7779
2414.4729 | 854.2023 | 427.8489 | 428.2559 | 432.0717
2415.4729 | 862.8551 | 427.9448 | 428.6078 | 432.1225
2416.4729 | 854.8828 | 427.851 | 428.4961 | 431.6974
2417.4729 | 862.4732 | 427.7262 | 428.009 | 431.569
2418.4729 | 876.7568 | 427.1389 | 428.2913 | 431.278
2419.4729 | 875.6178 | 427.2996 | 427.7727 | 430.7378
2420.4729 | 867.8355 | 427.7039 | 427.7781 | 430.4871
2421.4729 | 868.635 | 427.6964 | 427.7662 | 430.6663
2422.4729 | 877.1518 | 427.4701 | 427.2177 | 430.8803
2423.4729 | 885.0995 | 427.335 | 427.4847 | 430.5681
2424.4729 | 878.5266 | 427.8542 | 427.946 | 430.6551
2425.4729 | 874.7151 | 427.5065 | 427.822 | 430.5615
2426.4729 | 875.882 | 426.81 | 427.8071 | 430.3903
2427.4729 | 887.1393 | 426.6523 | 427.766 | 430.1978
2428.4729 | 892.3308 | 426.5892 | 428.0263 | 430.0982
2429.4729 | 891.4797 | 426.4354 | 427.7104 | 430.1006
2430.4729 | 892.5346 | 426.7188 | 427.3683 | 429.5808
2431.4729 | 893.6902 | 427.3751 | 427.5212 | 429.1302
2432.4729 | 894.0031 | 427.0966 | 427.6249 | 429.0163
2433.4729 | 894.4958 | 426.8863 | 427.3643 | 428.7708
2434.4729 | 890.6287 | 426.4737 | 427.3173 | 428.9123
2435.4729 | 874.325 | 426.0555 | 426.9924 | 428.5835
2436.4729 | 864.9354 | 426.3535 | 426.7769 | 428.4984
2437.4729 | 861.6517 | 427.1161 | 427.0544 | 428.3447
2438.4729 | 861.8274 | 427.673 | 426.9244 | 427.9033
2439.4729 | 853.0594 | 427.6775 | 427.1082 | 427.6318
2440.4729 | 849.5737 | 427.1671 | 427.4226 | 427.3725
2441.4729 | 838.3075 | 427.4448 | 427.0963 | 427.115
2442.4729 | 833.3451 | 427.6473 | 427.248 | 426.958
2443.4729 | 841.9466 | 427.4979 | 427.3992 | 427.0153
2444.4729 | 854.3823 | 427.2433 | 427.1573 | 426.8196
2445.4729 | 858.9904 | 427.3616 | 426.9933 | 427.1648
2446.4729 | 865.4984 | 427.4201 | 426.5431 | 427.1952
2447.4729 | 873.9857 | 427.8706 | 426.7228 | 427.4134
2448.4729 | 890.8113 | 427.7897 | 426.4283 | 427.506
2449.4729 | 904.6631 | 427.3845 | 426.3283 | 427.6507
2450.4729 | 890.4672 | 427.5829 | 426.8121 | 427.7753
2451.4729 | 894.0658 | 427.4017 | 426.3712 | 427.5766
2452.4729 | 888.0283 | 427.6624 | 426.9106 | 427.5825
2453.4729 | 892.965 | 427.3177 | 427.1129 | 427.6756
2454.4729 | 899.2576 | 428.0469 | 427.2906 | 427.8897
2455.4729 | 896.1989 | 427.8371 | 427.3083 | 427.9666
2456.4729 | 892.1898 | 427.969 | 427.2982 | 428.4719
2457.4729 | 892.3142 | 428.053 | 427.598 | 429.2996
2458.4729 | 891.5408 | 427.965 | 428.1755 | 429.9588
2459.4729 | 888.1734 | 428.1458 | 428.3256 | 430.5771
2460.4729 | 886.4836 | 428.3873 | 428.757 | 431.3249