## Test Conditions
DESIREE-FIRE Intermediate Scale Test 6 - Circuit Simulator Data Only
Test Date: | 2010-03-03
DCSim DAQ Start Time | 13:38
DCSim Time for Synchronization | 14:06
Heat Source Synchronization | 0:00 | hour:minutes:seconds
Heat Source DAQ Start Time | 14:05
Fire Time | 14:34
Offset | 0:56 | hour:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 3360 | seconds
Heat Source Offset | 0:29 | hour:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 1740 | seconds
Heat Source Stop Time | 15:15
Test Duration | 0:41 | hour:minutes:seconds
| 2460 | seconds
CT500 turns | 2 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 turns | 5 | 1 or 5
Pre-Test Baseline: | Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
SOV 1 | PE/PVC, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 5, 6, and 7 represents the air temperature 3', 5', and 7' down the tray located in C Position. These are labeled as "C Position - 3'", "C Position - Middle", "C Position - 7'", respectively.
SOV 2 | PE/PVC, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 0 represents the air temperature at the center of the tray located in A Position. Is it labeled as "A Position - Middle".
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | SOV-1_CT500 | SOV-1_CT35_1_P | SOV-1_CT35_2_S1 | SOV-1_CT35_3_G | SOV-1_CT35_4_S2 | SOV-1_CT35_5_N | SOV-2_CT500 | SOV-2_CT35_1_P | SOV-2_CT35_2_S1 | SOV-2_CT35_3_G | SOV-2_CT35_4_S2 | SOV-2_CT35_5_N | SOV-1_VT7_1_R | SOV-1_VT7_2_SP | SOV-1_VT7_3_S | SOV-1_VTU_1_P | SOV-1_VTU_2_S1 | SOV-1_VTU_3_G | SOV-1_VTU_4_N | SOV-2_VT7_1_R | SOV-2_VT7_2_SP | SOV-2_VT7_3_S | SOV-2_VTU_1_P | SOV-2_VTU_2_S1 | SOV-2_VTU_3_G | SOV-2_VTU_4_N | {SOV1} V(N) - V(Batt -) | {SOV1} V(P) - V(Batt +) | {SOV1} V(R) - V(Batt -) | {SOV1} V(S) - V(Batt -) | {SOV1} V(S) - V(N) | {SOV1} V(S1) - V(Batt +) | {SOV1} V(G) - V(Batt +) | {SOV2} V(N) - V(Batt -) | {SOV2} V(P) - V(Batt +) | {SOV2} V(R) - V(Batt -) | {SOV2} V(S) - V(Batt -) | {SOV2} V(S) - V(N) | {SOV2} V(S1) - V(Batt +) | {SOV2} V(G) - V(Batt +) | {SOV1} V(P) - V(Batt -) | {SOV1} V(S1) - V(Batt -) | {SOV1} V(G) - V(Batt -) | {SOV1} V(SP) - V(Batt -) | {SOV1} V(N) - V(Batt +) | {SOV2} V(P) - V(Batt -) | {SOV2} V(S1) - V(Batt -) | {SOV1} V(G) - V(Batt -) | {SOV2} V(SP) - V(Batt -) | {SOV2} V(N) - V(Batt +)
-0.96875 | 123.587 | -61.6653 | 61.6882 | 1.4211e-13 | -0.0095768 | 0.00078429 | -0.0018334 | -0.0083543 | -0.0027221 | 0.0056466 | -0.0027666 | -0.0027563 | 0.062125 | 0.025519 | 0.058859 | -61.5554 | 0.010564 | -61.6778 | 61.6864 | 61.2023 | 61.4952 | -61.2604 | -61.6375 | 0.009516 | -61.6858 | 61.4501 | 61.7241 | 61.1 | -62.024 | 0.40496 | -0.001847 | 0.10997 | -0.012504 | -0.41746 | -0.48597 | -0.19299 | -0.35863 | -0.23815 | 0.0278 | -0.020442 | 0.33818 | 0.035879 | -0.58819 | 123.3517 | 122.8676 | 123.1606 | 61.6759 | -122.9486 | 123.1154 | 123.3895 | 122.7654 | 61.6749 | -123.7122
0.70312 | 123.5001 | -61.7157 | 61.6608 | 1.4211e-13 | -0.0097904 | 0.00035689 | -0.0016198 | -0.0081405 | -0.0029357 | 0.013277 | -0.002553 | -0.0025425 | 0.061911 | 0.025519 | 0.059287 | -61.5554 | 0.001407 | -61.6641 | 61.6864 | 61.2068 | 61.4952 | -61.265 | -61.6375 | 0.004938 | -61.6812 | 61.473 | 61.7241 | 61.1 | -62.0377 | 0.45074 | 0.025618 | 0.16032 | 0.051585 | -0.39915 | -0.45392 | -0.16553 | -0.32201 | -0.1878 | 0.078154 | 0.034491 | 0.3565 | 0.063344 | -0.56072 | 123.4021 | 122.9225 | 123.2109 | 61.7171 | -122.9257 | 123.1887 | 123.4398 | 122.8157 | 61.7206 | -123.6985
2.4375 | 123.4543 | -61.7157 | 61.7157 | 1.4211e-13 | -0.0093632 | 0.00035689 | -0.0018334 | -0.0081405 | -0.0027221 | 0.0056466 | -0.002553 | -0.0029699 | 0.061911 | 0.025733 | 0.059287 | -61.5462 | 0.010564 | -61.6733 | 61.691 | 61.1977 | 61.4998 | -61.2558 | -61.6284 | 0.000359 | -61.6904 | 61.4638 | 61.7241 | 61.0955 | -62.0377 | 0.45989 | -0.024735 | 0.16948 | 0.042428 | -0.41746 | -0.51801 | -0.21588 | -0.32201 | -0.25188 | 0.087311 | 0.025334 | 0.34734 | 0.008413 | -0.62023 | 123.4067 | 122.9134 | 123.2155 | 61.7263 | -122.9715 | 123.1795 | 123.4398 | 122.8112 | 61.7161 | -123.7534
4.1562 | 123.5184 | -61.6974 | 61.6882 | 1.4211e-13 | -0.0093632 | 0.00099789 | -0.0018334 | -0.0085679 | -0.0031493 | 0.0056466 | -0.0027666 | -0.0025425 | 0.061697 | 0.025519 | 0.059287 | -61.5508 | 0.010564 | -61.6595 | 61.6772 | 61.2068 | 61.4907 | -61.2558 | -61.633 | 0.004938 | -61.6858 | 61.4684 | 61.7241 | 61.1 | -62.0377 | 0.44158 | -0.011004 | 0.14659 | 0.037853 | -0.40373 | -0.48139 | -0.19757 | -0.34032 | -0.21984 | 0.064422 | 0.011602 | 0.35192 | 0.035879 | -0.58819 | 123.3746 | 122.9042 | 123.188 | 61.708 | -122.944 | 123.1658 | 123.4215 | 122.7974 | 61.7023 | -123.7259
5.8906 | 123.5779 | -61.6653 | 61.6608 | 1.4211e-13 | -0.0091494 | 0.00057049 | -0.0018334 | -0.0085679 | -0.0031493 | 0.0056466 | -0.0023394 | -0.0027563 | 0.061911 | 0.025733 | 0.059287 | -61.56 | 0.005985 | -61.6641 | 61.6818 | 61.2023 | 61.4907 | -61.2558 | -61.6284 | 0.009516 | -61.6812 | 61.4409 | 61.7241 | 61.1046 | -62.0377 | 0.40954 | 0.02104 | 0.10539 | 0.001231 | -0.40831 | -0.4585 | -0.17011 | -0.37236 | -0.21984 | 0.036957 | -0.015863 | 0.3565 | 0.063344 | -0.55614 | 123.3472 | 122.8676 | 123.156 | 61.6713 | -122.9166 | 123.1063 | 123.3895 | 122.77 | 61.6749 | -123.6985
7.5781 | 123.5321 | -61.647 | 61.6516 | 1.4211e-13 | -0.010004 | 0.00099789 | -0.0018334 | -0.0083543 | -0.0031493 | -0.0019839 | -0.002553 | -0.0025425 | 0.062125 | 0.025733 | 0.0595 | -61.5462 | 0.015142 | -61.6595 | 61.6818 | 61.2068 | 61.4861 | -61.2558 | -61.6284 | 0.004938 | -61.6766 | 61.3814 | 61.7195 | 61.1 | -62.0285 | 0.39123 | 0.030196 | 0.10081 | -0.012501 | -0.40373 | -0.44477 | -0.16553 | -0.38151 | -0.27021 | 0.018647 | -0.029594 | 0.35192 | 0.067922 | -0.55157 | 123.3288 | 122.8539 | 123.1331 | 61.6622 | -122.9074 | 123.0284 | 123.3666 | 122.7471 | 61.652 | -123.6802
9.3125 | 123.5229 | -61.6562 | 61.6745 | 1.4211e-13 | -0.0095768 | 0.00057049 | -0.0016198 | -0.0081405 | -0.0033631 | 0.013277 | -0.0027666 | -0.0025425 | 0.061697 | 0.025519 | 0.059073 | -61.5462 | 0.005985 | -61.6595 | 61.6772 | 61.1977 | 61.4861 | -61.2558 | -61.6375 | 0.004938 | -61.6858 | 61.4089 | 61.7241 | 61.1046 | -62.0331 | 0.40038 | 0.002728 | 0.10997 | -0.003346 | -0.40373 | -0.47682 | -0.18842 | -0.37694 | -0.26563 | 0.018645 | -0.029597 | 0.34734 | 0.049611 | -0.56988 | 123.3334 | 122.8539 | 123.1423 | 61.6622 | -122.9303 | 123.0651 | 123.3803 | 122.7608 | 61.6611 | -123.7076
11.0469 | 123.4543 | -61.7249 | 61.6745 | 1.4211e-13 | -0.0095768 | 0.00078429 | -0.0016198 | -0.0085679 | -0.0029357 | -0.0019839 | -0.0027666 | -0.0025425 | 0.061697 | 0.025733 | 0.058859 | -61.5462 | 0.010564 | -61.6641 | 61.6864 | 61.1977 | 61.4861 | -61.2512 | -61.6238 | 0.004938 | -61.6812 | 61.3814 | 61.7241 | 61.1 | -62.0331 | 0.47363 | 0.011885 | 0.17863 | 0.060741 | -0.41289 | -0.47682 | -0.18842 | -0.30827 | -0.2931 | 0.10105 | 0.043647 | 0.35192 | 0.049611 | -0.57446 | 123.4112 | 122.9225 | 123.2109 | 61.7354 | -122.9257 | 123.1063 | 123.449 | 122.8249 | 61.7298 | -123.7076
12.7188 | 123.4818 | -61.702 | 61.6882 | 1.4211e-13 | -0.0095768 | 0.00078429 | -0.0018334 | -0.0085679 | -0.0029357 | 0.0056466 | -0.0029802 | -0.0025425 | 0.062125 | 0.025946 | 0.058859 | -61.5462 | 0.005985 | -61.6641 | 61.6772 | 61.2023 | 61.4998 | -61.265 | -61.6284 | 0.018674 | -61.6812 | 61.4684 | 61.7241 | 61.1046 | -62.0331 | 0.437 | -0.011004 | 0.15575 | 0.037852 | -0.39915 | -0.48597 | -0.18841 | -0.33116 | -0.21984 | 0.073578 | 0.020758 | 0.35192 | 0.035879 | -0.58361 | 123.3792 | 122.9042 | 123.2018 | 61.708 | -122.9532 | 123.1704 | 123.4261 | 122.8066 | 61.7206 | -123.7214
14.4531 | 123.4131 | -61.7203 | 61.6791 | 1.4211e-13 | -0.0097904 | 0.00078429 | -0.0018334 | -0.0083543 | -0.0031493 | -0.0019839 | -0.002553 | -0.0027563 | 0.061697 | 0.025519 | 0.059073 | -61.5462 | 0.005985 | -61.6641 | 61.6726 | 61.2068 | 61.4815 | -61.2466 | -61.6192 | 0.009516 | -61.6858 | 61.4455 | 61.7195 | 61.0955 | -62.0377 | 0.47363 | -0.006427 | 0.17406 | 0.056163 | -0.41747 | -0.47223 | -0.19757 | -0.31743 | -0.23358 | 0.10105 | 0.03449 | 0.35192 | 0.040456 | -0.58361 | 123.3929 | 122.9271 | 123.2018 | 61.7263 | -122.9257 | 123.1658 | 123.4398 | 122.8157 | 61.7298 | -123.7168
16.1875 | 123.4634 | -61.7157 | 61.6425 | 1.4211e-13 | -0.010004 | 0.00078429 | -0.002047 | -0.0079269 | -0.0029357 | -0.0019839 | -0.002553 | -0.0027563 | 0.062125 | 0.025946 | 0.059073 | -61.5371 | 0.010564 | -61.6687 | 61.6818 | 61.2023 | 61.4907 | -61.2512 | -61.6284 | 0.004938 | -61.6812 | 61.3585 | 61.7195 | 61.1 | -62.0331 | 0.46447 | 0.039351 | 0.17863 | 0.047006 | -0.41747 | -0.44019 | -0.15179 | -0.31743 | -0.28395 | 0.087311 | 0.034491 | 0.35192 | 0.077077 | -0.54241 | 123.3975 | 122.918 | 123.2064 | 61.7263 | -122.8937 | 123.0742 | 123.4352 | 122.8157 | 61.7206 | -123.6756
17.9375 | 123.4314 | -61.6837 | 61.7157 | 1.4211e-13 | -0.0095768 | 0.00057049 | -0.0016198 | -0.0087815 | -0.0031493 | -0.0019839 | -0.002553 | -0.0027563 | 0.061697 | 0.025946 | 0.0595 | -61.5416 | 0.015142 | -61.6733 | 61.6635 | 61.1977 | 61.4861 | -61.2512 | -61.633 | 0.014095 | -61.6766 | 61.4776 | 61.7241 | 61.0909 | -62.0285 | 0.43243 | -0.052205 | 0.14201 | 0.010385 | -0.42204 | -0.51801 | -0.22962 | -0.34489 | -0.23815 | 0.050689 | 0.007027 | 0.35192 | 0.008413 | -0.62481 | 123.3471 | 122.8813 | 123.1697 | 61.6988 | -122.9669 | 123.1612 | 123.4078 | 122.7745 | 61.6977 | -123.7442
19.6094 | 123.5596 | -61.6562 | 61.6333 | 1.4211e-13 | -0.010004 | 0.00078429 | -0.0018334 | -0.0085679 | -0.0029357 | -0.0019839 | -0.0029802 | -0.0027563 | 0.061697 | 0.025946 | 0.059287 | -61.5508 | 0.010564 | -61.6687 | 61.6726 | 61.2068 | 61.5273 | -61.2512 | -61.6238 | 0.009516 | -61.6766 | 61.473 | 61.715 | 61.1 | -62.0285 | 0.40496 | 0.039349 | 0.10539 | -0.012503 | -0.41747 | -0.42646 | -0.10601 | -0.37236 | -0.16033 | 0.032381 | -0.020439 | 0.35192 | 0.081653 | -0.53326 | 123.3288 | 122.863 | 123.1835 | 61.6668 | -122.8845 | 123.1292 | 123.3711 | 122.7562 | 61.6657 | -123.6618
21.3438 | 123.468 | -61.6837 | 61.6745 | 1.4211e-13 | -0.0097904 | 0.00078429 | -0.0018334 | -0.0083543 | -0.0033631 | -0.0019839 | -0.0027666 | -0.0023289 | 0.061697 | 0.025733 | 0.059073 | -61.5371 | 0.010564 | -61.6641 | 61.6726 | 61.1839 | 61.509 | -61.2512 | -61.6284 | 0.004938 | -61.672 | 61.4638 | 61.7195 | 61.0909 | -62.024 | 0.43243 | -0.00185 | 0.14659 | 0.019542 | -0.41289 | -0.49055 | -0.16552 | -0.34031 | -0.21069 | 0.055268 | 0.011605 | 0.35192 | 0.045033 | -0.58361 | 123.3563 | 122.8676 | 123.1926 | 61.6942 | -122.9257 | 123.1475 | 123.4032 | 122.7745 | 61.6886 | -123.6985
23.0156 | 123.4497 | -61.7111 | 61.6562 | 1.4211e-13 | -0.0097904 | 0.00078429 | -0.0018334 | -0.0085679 | -0.0029357 | 0.0056466 | -0.0027666 | -0.0023289 | 0.061484 | 0.02616 | 0.0595 | -61.5371 | 0.001407 | -61.6733 | 61.6818 | 61.2023 | 61.4815 | -61.2512 | -61.6147 | 0.000359 | -61.6675 | 61.4684 | 61.7195 | 61.0909 | -62.0285 | 0.45989 | 0.025618 | 0.17406 | 0.037851 | -0.42204 | -0.45392 | -0.17468 | -0.31743 | -0.1878 | 0.09647 | 0.04365 | 0.36108 | 0.063344 | -0.5653 | 123.3929 | 122.9134 | 123.1926 | 61.7125 | -122.9074 | 123.1795 | 123.4307 | 122.802 | 61.7115 | -123.6847
24.7344 | 123.436 | -61.6928 | 61.6379 | 1.4211e-13 | -0.0097904 | 0.00035689 | -0.0016198 | -0.0085679 | -0.0029357 | 0.0056466 | -0.0027666 | -0.0027563 | 0.061697 | 0.025946 | 0.058859 | -61.5462 | 0.005985 | -61.6641 | 61.6726 | 61.2023 | 61.4815 | -61.2512 | -61.6147 | 0.004938 | -61.672 | 61.4592 | 61.7104 | 61.0909 | -62.0285 | 0.44158 | 0.034772 | 0.14659 | 0.028697 | -0.41289 | -0.43561 | -0.15637 | -0.33574 | -0.17864 | 0.078159 | 0.02076 | 0.3565 | 0.072497 | -0.54699 | 123.3655 | 122.8951 | 123.1743 | 61.6988 | -122.8891 | 123.152 | 123.4032 | 122.7837 | 61.6977 | -123.6664
26.4688 | 123.5733 | -61.6287 | 61.6653 | 1.4211e-13 | -0.0097904 | 0.00099789 | -0.0016198 | -0.0087815 | -0.0031493 | 0.013277 | -0.002553 | -0.0025425 | 0.062125 | 0.02616 | 0.059287 | -61.5416 | 0.010564 | -61.6641 | 61.6726 | 61.1931 | 61.4815 | -61.2512 | -61.6192 | 0.004938 | -61.6629 | 61.4318 | 61.715 | 61.0955 | -62.024 | 0.3775 | 0.007306 | 0.087081 | -0.03539 | -0.41289 | -0.47224 | -0.18384 | -0.39525 | -0.23358 | 0.009493 | -0.034169 | 0.36108 | 0.04961 | -0.56988 | 123.3014 | 122.8218 | 123.1102 | 61.6393 | -122.9166 | 123.0605 | 123.3437 | 122.7242 | 61.6337 | -123.6893
28.2031 | 123.4772 | -61.6974 | 61.6425 | 1.4211e-13 | -0.010004 | 0.00014309 | -0.001406 | -0.0083543 | -0.0029357 | -0.0019839 | -0.0027666 | -0.0025425 | 0.062125 | 0.025946 | 0.058859 | -61.5371 | 0.005985 | -61.6687 | 61.6635 | 61.1977 | 61.4861 | -61.2512 | -61.6147 | 0.004938 | -61.6766 | 61.4455 | 61.715 | 61.0955 | -62.0194 | 0.44616 | 0.021037 | 0.16032 | 0.028696 | -0.41747 | -0.44477 | -0.15637 | -0.322 | -0.19696 | 0.082737 | 0.02076 | 0.34276 | 0.072498 | -0.54699 | 123.3609 | 122.8951 | 123.1835 | 61.7034 | -122.8937 | 123.1429 | 123.4123 | 122.7929 | 61.7023 | -123.6618
29.9375 | 123.468 | -61.6882 | 61.6608 | 1.4211e-13 | -0.010004 | 0.00078429 | -0.0016198 | -0.0081405 | -0.0031493 | 0.013277 | -0.0027666 | -0.0025425 | 0.061697 | 0.02616 | 0.058646 | -61.5416 | 0.001407 | -61.6733 | 61.6635 | 61.1977 | 61.4861 | -61.2466 | -61.6147 | 0.018674 | -61.672 | 61.4501 | 61.715 | 61.0863 | -62.0194 | 0.44158 | 0.002726 | 0.14659 | 0.014962 | -0.42662 | -0.46308 | -0.17468 | -0.33116 | -0.21069 | 0.073581 | 0.016182 | 0.34734 | 0.054187 | -0.57446 | 123.3517 | 122.8859 | 123.1743 | 61.6896 | -122.9074 | 123.1383 | 123.4032 | 122.7745 | 61.7069 | -123.6802
31.6094 | 123.5367 | -61.6608 | 61.6379 | 1.4211e-13 | -0.010004 | 0.00057049 | -0.001406 | -0.0083543 | -0.0031493 | 0.013277 | -0.0027666 | -0.0031835 | 0.061911 | 0.02616 | 0.059287 | -61.5371 | 0.001407 | -61.6733 | 61.6681 | 61.1977 | 61.4815 | -61.2512 | -61.6055 | 0.004938 | -61.6675 | 61.3448 | 61.715 | 61.0909 | -62.0194 | 0.40954 | 0.030194 | 0.1237 | -0.012503 | -0.42204 | -0.44019 | -0.15637 | -0.35862 | -0.2931 | 0.055274 | -0.006704 | 0.35192 | 0.077076 | -0.54699 | 123.3288 | 122.8585 | 123.1423 | 61.6622 | -122.8891 | 123.0055 | 123.3757 | 122.7517 | 61.6657 | -123.6573
33.3438 | 123.4818 | -61.647 | 61.7111 | 1.4211e-13 | -0.010004 | 0.00078429 | -0.0016198 | -0.0081405 | -0.0033631 | -0.0096144 | -0.0027666 | -0.0025425 | 0.062125 | 0.026374 | 0.059073 | -61.5416 | 0.010564 | -61.6641 | 61.6681 | 61.1931 | 61.4861 | -61.2466 | -61.6147 | 0.009516 | -61.6675 | 61.473 | 61.7104 | 61.0909 | -62.024 | 0.40039 | -0.043049 | 0.10539 | -0.017079 | -0.41747 | -0.51801 | -0.22504 | -0.37694 | -0.23815 | 0.032383 | -0.020437 | 0.3565 | -0.000746 | -0.62023 | 123.3151 | 122.8401 | 123.1331 | 61.6576 | -122.9578 | 123.12 | 123.3574 | 122.7379 | 61.6565 | -123.7351
35.0156 | 123.5275 | -61.6287 | 61.647 | 1.4211e-13 | -0.010218 | 0.00078429 | -0.001406 | -0.0083543 | -0.0027221 | 0.0056466 | -0.002553 | -0.0025425 | 0.062125 | 0.026587 | 0.0595 | -61.5371 | 0.010564 | -61.6641 | 61.6772 | 61.1977 | 61.4815 | -61.2466 | -61.6101 | 0.009516 | -61.672 | 61.418 | 61.7104 | 61.0863 | -62.024 | 0.38208 | 0.030194 | 0.091659 | -0.03539 | -0.41747 | -0.44935 | -0.16553 | -0.39525 | -0.229 | 0.018651 | -0.043327 | 0.35192 | 0.063341 | -0.56073 | 123.306 | 122.8264 | 123.1102 | 61.6393 | -122.8937 | 123.0468 | 123.3391 | 122.715 | 61.6382 | -123.671
36.75 | 123.4497 | -61.6882 | 61.647 | 1.4211e-13 | -0.010004 | 0.00078429 | -0.0016198 | -0.0087815 | -0.0029357 | 0.013277 | -0.0027666 | -0.0025425 | 0.061911 | 0.02616 | 0.059287 | -61.5371 | 0.005985 | -61.6504 | 61.6772 | 61.1931 | 61.4861 | -61.2421 | -61.6147 | 0.009516 | -61.6583 | 61.4638 | 61.715 | 61.0863 | -62.0194 | 0.44616 | 0.030194 | 0.15117 | 0.037853 | -0.40831 | -0.45393 | -0.16095 | -0.33116 | -0.18322 | 0.073581 | 0.029919 | 0.36108 | 0.06792 | -0.56073 | 123.3655 | 122.8813 | 123.1743 | 61.6942 | -122.8891 | 123.152 | 123.4032 | 122.7745 | 61.6977 | -123.6664
38.4219 | 123.5046 | -61.6196 | 61.6791 | 1.4211e-13 | -0.010218 | 0.00057049 | -0.0016198 | -0.0085679 | -0.0031493 | -0.0019839 | -0.0029802 | -0.0025425 | 0.061911 | 0.02616 | 0.059287 | -61.5325 | 0.010564 | -61.6595 | 61.6681 | 61.1931 | 61.4861 | -61.2375 | -61.6101 | 0.014095 | -61.6629 | 61.4592 | 61.715 | 61.0863 | -62.0194 | 0.38208 | -0.011005 | 0.087083 | -0.039967 | -0.42205 | -0.48597 | -0.19299 | -0.39982 | -0.21984 | 0.009496 | -0.043324 | 0.3565 | 0.035877 | -0.59277 | 123.2876 | 122.8127 | 123.1057 | 61.6301 | -122.9166 | 123.0788 | 123.3345 | 122.7059 | 61.6337 | -123.6985
40.0781 | 123.4909 | -61.6562 | 61.6745 | 1.4211e-13 | -0.010431 | 0.00078429 | -0.001406 | -0.0081405 | -0.0033631 | -0.0019839 | -0.0027666 | -0.0027563 | 0.062125 | 0.026374 | 0.059073 | -61.5462 | 0.015142 | -61.655 | 61.6726 | 61.2023 | 61.4861 | -61.2421 | -61.6055 | 0.004938 | -61.6675 | 61.4638 | 61.715 | 61.0817 | -62.0148 | 0.41412 | -0.00185 | 0.10997 | 0.001232 | -0.41289 | -0.47224 | -0.18842 | -0.35862 | -0.21069 | 0.050696 | -0.011282 | 0.34734 | 0.040454 | -0.59277 | 123.3288 | 122.8585 | 123.1423 | 61.6713 | -122.9166 | 123.12 | 123.3711 | 122.7379 | 61.6611 | -123.6893
41.8125 | 123.5321 | -61.6653 | 61.6241 | 1.4211e-13 | -0.010218 | 0.00035689 | -0.001406 | -0.0083543 | -0.0035767 | 0.013277 | -0.002553 | -0.0025425 | 0.061697 | 0.026374 | 0.0595 | -61.5371 | 0.005985 | -61.6595 | 61.6681 | 61.1977 | 61.4723 | -61.2421 | -61.6101 | 0.014095 | -61.6675 | 61.4455 | 61.715 | 61.0817 | -62.0194 | 0.42328 | 0.043926 | 0.12828 | 0.005809 | -0.41747 | -0.42646 | -0.1518 | -0.35405 | -0.17865 | 0.055272 | -0.002127 | 0.35192 | 0.090808 | -0.54242 | 123.3334 | 122.863 | 123.1377 | 61.6713 | -122.8662 | 123.1108 | 123.3803 | 122.7471 | 61.6794 | -123.6435
43.5469 | 123.4772 | -61.6196 | 61.6974 | 1.4211e-13 | -0.010218 | 0.00057049 | -0.0016198 | -0.0087815 | -0.0033631 | 0.0056466 | -0.0027666 | -0.0027563 | 0.062338 | 0.02616 | 0.059287 | -61.5325 | 0.005985 | -61.6641 | 61.6681 | 61.1931 | 61.4907 | -61.2375 | -61.6101 | 0.014095 | -61.6583 | 61.4684 | 61.7104 | 61.0817 | -62.024 | 0.38208 | -0.029316 | 0.087083 | -0.044545 | -0.42662 | -0.50428 | -0.20673 | -0.4044 | -0.22899 | 0.009496 | -0.038745 | 0.36566 | 0.012987 | -0.61566 | 123.2876 | 122.8127 | 123.1102 | 61.6256 | -122.9349 | 123.088 | 123.3299 | 122.7013 | 61.6337 | -123.7214
45.2188 | 123.4497 | -61.6425 | 61.6928 | 1.4211e-13 | -0.010218 | 0.00078429 | -0.0016198 | -0.0085679 | -0.0031493 | 0.013277 | -0.0027666 | -0.0027563 | 0.062125 | 0.026587 | 0.059073 | -61.5371 | 0.010564 | -61.6641 | 61.6635 | 61.1931 | 61.4815 | -61.2466 | -61.6055 | 0.004938 | -61.6675 | 61.4409 | 61.715 | 61.0863 | -62.0148 | 0.39581 | -0.029317 | 0.10539 | -0.021657 | -0.41747 | -0.4997 | -0.21131 | -0.37235 | -0.25189 | 0.036963 | -0.025015 | 0.34734 | 0.022144 | -0.6065 | 123.3059 | 122.8356 | 123.124 | 61.653 | -122.9395 | 123.0834 | 123.3574 | 122.7288 | 61.6474 | -123.7076
46.9375 | 123.5275 | -61.6333 | 61.6241 | 1.4211e-13 | -0.010431 | 0.0012115 | -0.0016198 | -0.0087815 | -0.0031493 | -0.0019839 | -0.0027666 | -0.0025425 | 0.061697 | 0.026587 | 0.059287 | -61.5233 | 0.005985 | -61.6595 | 61.6726 | 61.1931 | 61.4815 | -61.2375 | -61.6009 | 0.014095 | -61.6629 | 61.4547 | 61.7104 | 61.0817 | -62.0148 | 0.39581 | 0.048504 | 0.10997 | -0.026234 | -0.42205 | -0.43104 | -0.14264 | -0.38151 | -0.16949 | 0.032386 | -0.029591 | 0.35192 | 0.086229 | -0.54242 | 123.306 | 122.8264 | 123.1148 | 61.6393 | -122.8616 | 123.088 | 123.3437 | 122.715 | 61.6474 | -123.639
48.6719 | 123.4177 | -61.702 | 61.6333 | 1.4211e-13 | -0.010218 | 0.00078429 | -0.0016198 | -0.0085679 | -0.0029357 | -0.0019839 | -0.0023394 | -0.0023289 | 0.061911 | 0.026587 | 0.058859 | -61.5279 | 0.010564 | -61.6641 | 61.6635 | 61.1977 | 61.4907 | -61.2375 | -61.5963 | 0.004938 | -61.6629 | 61.4501 | 61.7058 | 61.0863 | -62.0148 | 0.46448 | 0.030192 | 0.17406 | 0.037852 | -0.42662 | -0.43562 | -0.14264 | -0.31285 | -0.18322 | 0.10563 | 0.039073 | 0.35192 | 0.072496 | -0.54699 | 123.3655 | 122.8997 | 123.1926 | 61.7125 | -122.8708 | 123.152 | 123.4078 | 122.7883 | 61.7069 | -123.6481
50.4219 | 123.5413 | -61.6425 | 61.6287 | 1.4211e-13 | -0.010431 | 0.00035689 | -0.0016198 | -0.0085679 | -0.0029357 | 0.0056466 | -0.0027666 | -0.0027563 | 0.061697 | 0.026801 | 0.059073 | -61.5325 | 0.001407 | -61.655 | 61.6635 | 61.1839 | 61.4769 | -61.2421 | -61.6101 | 0.004938 | -61.6583 | 61.4363 | 61.7104 | 61.0817 | -62.0194 | 0.40039 | 0.03477 | 0.10997 | -0.012501 | -0.41289 | -0.44477 | -0.1518 | -0.37693 | -0.19238 | 0.032384 | -0.015857 | 0.36108 | 0.081652 | -0.54699 | 123.3059 | 122.8264 | 123.1194 | 61.6439 | -122.8708 | 123.0788 | 123.3528 | 122.7242 | 61.6474 | -123.6481
52.0938 | 123.4772 | -61.6241 | 61.6699 | 1.4211e-13 | -0.010004 | 0.00057049 | 0.065477 | -0.0085679 | 0.061804 | -0.0096144 | -0.0029802 | -0.0025425 | 0.061697 | 0.026587 | 0.059073 | -61.5004 | 0.005985 | -61.6504 | 61.6543 | 61.1794 | 61.4907 | -61.2238 | -61.6055 | 0.004938 | -61.6537 | 61.418 | 61.6966 | 61.0817 | -62.0102 | 0.40039 | -0.015586 | 0.12371 | -0.026233 | -0.42663 | -0.49055 | -0.17926 | -0.38609 | -0.25189 | 0.018653 | -0.029589 | 0.3565 | 0.026718 | -0.58819 | 123.2785 | 122.8035 | 123.1148 | 61.6301 | -122.8937 | 123.0422 | 123.3208 | 122.7059 | 61.6291 | -123.6802
53.8125 | 123.5367 | -61.6104 | 61.6562 | 1.4211e-13 | -0.010431 | 0.00099789 | 0.065904 | -0.0083543 | 0.06159 | 0.013277 | -0.002553 | -0.0025425 | 0.062125 | 0.026801 | 0.059073 | -61.505 | 0.010564 | -61.6366 | 61.6543 | 61.1839 | 61.4907 | -61.2192 | -61.6055 | 0.009516 | -61.6537 | 61.4501 | 61.7012 | 61.068 | -62.0057 | 0.39124 | -0.001853 | 0.1054 | -0.026231 | -0.41747 | -0.47224 | -0.16553 | -0.39524 | -0.20611 | 0.00492 | -0.043322 | 0.35192 | 0.045029 | -0.58819 | 123.2647 | 122.7944 | 123.1011 | 61.621 | -122.8754 | 123.0605 | 123.3116 | 122.6784 | 61.6199 | -123.6618
55.5469 | 123.3902 | -61.6699 | 61.6379 | 1.4211e-13 | -0.010431 | 0.00057049 | 0.066118 | -0.0087815 | 0.061377 | 0.0056466 | -0.002553 | -0.0027563 | 0.061911 | 0.026801 | 0.059073 | -61.505 | 0.005985 | -61.6366 | 61.6498 | 61.1794 | 61.4678 | -61.2192 | -61.5963 | 0.014095 | -61.6629 | 61.4592 | 61.7012 | 61.0772 | -62.0102 | 0.45075 | 0.01188 | 0.16491 | 0.033278 | -0.41747 | -0.45851 | -0.17011 | -0.34031 | -0.17864 | 0.073586 | 0.00703 | 0.34734 | 0.06334 | -0.56073 | 123.3197 | 122.8493 | 123.1377 | 61.6759 | -122.8571 | 123.1292 | 123.3711 | 122.7471 | 61.684 | -123.6481
57.2969 | 123.4589 | -61.6791 | 61.6425 | 1.4211e-13 | -0.010218 | 0.00057049 | 0.06569 | -0.0087815 | 0.061377 | -0.0019839 | -0.0029802 | -0.0025425 | 0.061911 | 0.026587 | 0.059073 | -61.505 | 0.005985 | -61.6458 | 61.6406 | 61.1839 | 61.454 | -61.2146 | -61.5963 | 0.023253 | -61.6537 | 61.4455 | 61.7058 | 61.068 | -62.0057 | 0.46448 | -0.001855 | 0.17406 | 0.033277 | -0.4312 | -0.45851 | -0.18842 | -0.32658 | -0.19696 | 0.082741 | 0.025342 | 0.35192 | 0.063341 | -0.57446 | 123.3197 | 122.863 | 123.1331 | 61.6851 | -122.8571 | 123.1246 | 123.3849 | 122.7471 | 61.7023 | -123.6481
58.9688 | 123.436 | -61.647 | 61.647 | 1.4211e-13 | -0.010218 | 0.00057049 | 0.066332 | -0.0083543 | 0.061163 | -0.0019839 | -0.0027666 | -0.0027563 | 0.061911 | 0.027015 | 0.058859 | -61.505 | 0.015142 | -61.6412 | 61.6406 | 61.1748 | 61.4632 | -61.2238 | -61.5918 | 0.004938 | -61.6492 | 61.4318 | 61.6966 | 61.068 | -62.0102 | 0.42328 | -0.006433 | 0.14202 | 0.005812 | -0.41747 | -0.47224 | -0.18384 | -0.3632 | -0.21527 | 0.055277 | -0.002122 | 0.36108 | 0.049606 | -0.57904 | 123.2876 | 122.8218 | 123.1102 | 61.6622 | -122.8708 | 123.0788 | 123.3437 | 122.715 | 61.652 | -123.6573
60.6875 | 123.5046 | -61.5829 | 61.6562 | 1.4211e-13 | -0.010645 | 0.00078429 | 0.06569 | -0.0085679 | 0.061163 | -0.0019839 | -0.002553 | -0.0027563 | 0.061697 | 0.026801 | 0.058859 | -61.505 | 0.005985 | -61.6366 | 61.6406 | 61.1702 | 61.4632 | -61.2146 | -61.5918 | 0.014095 | -61.6446 | 61.4363 | 61.6921 | 61.068 | -62.0011 | 0.36835 | -0.015588 | 0.077932 | -0.053697 | -0.42205 | -0.48598 | -0.193 | -0.41813 | -0.21984 | -0.00881 | -0.06163 | 0.3565 | 0.035872 | -0.58819 | 123.2235 | 122.7532 | 123.0461 | 61.5889 | -122.8708 | 123.0193 | 123.275 | 122.6509 | 61.597 | -123.6573
62.4375 | 123.4497 | -61.6241 | 61.6425 | 1.4211e-13 | -0.010218 | 0.00057049 | 0.06569 | -0.0085679 | 0.061804 | -0.0019839 | -0.0029802 | -0.0027563 | 0.061911 | 0.027228 | 0.058859 | -61.4821 | 0.005985 | -61.6412 | 61.6406 | 61.1794 | 61.4586 | -61.2192 | -61.5872 | 0.004938 | -61.6492 | 61.3951 | 61.7012 | 61.068 | -61.9919 | 0.40497 | -0.001855 | 0.14202 | -0.017076 | -0.42205 | -0.46309 | -0.18385 | -0.36777 | -0.24732 | 0.036967 | -0.02501 | 0.34276 | 0.058762 | -0.57446 | 123.2647 | 122.8035 | 123.0828 | 61.6301 | -122.8616 | 123.0193 | 123.3254 | 122.6921 | 61.6291 | -123.6344
64.1719 | 123.4177 | -61.6699 | 61.647 | 1.4211e-13 | -0.010218 | 0.00035689 | 0.065477 | -0.0083543 | 0.061377 | 0.013277 | -0.0029802 | -0.0029699 | 0.061697 | 0.026801 | 0.059287 | -61.4913 | 0.010564 | -61.6275 | 61.6406 | 61.1656 | 61.4632 | -61.2146 | -61.5826 | 0.014095 | -61.6446 | 61.418 | 61.7058 | 61.0634 | -62.0011 | 0.45533 | -0.006433 | 0.17864 | 0.042435 | -0.41289 | -0.4814 | -0.18384 | -0.33115 | -0.229 | 0.087322 | 0.025345 | 0.3565 | 0.058763 | -0.58362 | 123.3105 | 122.8356 | 123.1331 | 61.6805 | -122.8616 | 123.088 | 123.3757 | 122.7333 | 61.684 | -123.6481
65.8281 | 123.3673 | -61.6562 | 61.702 | 1.4211e-13 | -0.010645 | 0.00057049 | 0.06569 | -0.0085679 | 0.061163 | -0.0019839 | -0.0027666 | -0.0021153 | 0.061911 | 0.027015 | 0.058859 | -61.4959 | 0.015142 | -61.6366 | 61.6406 | 61.1702 | 61.4815 | -61.2146 | -61.5872 | 0.014095 | -61.6446 | 61.4409 | 61.6966 | 61.068 | -62.0011 | 0.44159 | -0.061364 | 0.16033 | 0.019545 | -0.42205 | -0.53175 | -0.22046 | -0.34489 | -0.26104 | 0.06901 | 0.011612 | 0.3565 | -0.005325 | -0.63397 | 123.2968 | 122.8264 | 123.1377 | 61.6713 | -122.9166 | 123.0971 | 123.3528 | 122.7242 | 61.6703 | -123.703
67.5625 | 123.436 | -61.6516 | 61.6699 | 1.4211e-13 | -0.010431 | 0.00057049 | 0.06569 | -0.0087815 | 0.061377 | -0.0019839 | -0.0027666 | -0.0025425 | 0.061911 | 0.026801 | 0.058859 | -61.4867 | 0.010564 | -61.6275 | 61.6406 | 61.1702 | 61.4861 | -61.21 | -61.5826 | 0.014095 | -61.6446 | 61.4455 | 61.6875 | 61.0634 | -61.9965 | 0.44159 | -0.029321 | 0.16491 | 0.024124 | -0.41747 | -0.49971 | -0.18384 | -0.34488 | -0.22442 | 0.069011 | 0.007034 | 0.35192 | 0.01756 | -0.60651 | 123.2922 | 122.8218 | 123.1377 | 61.6622 | -122.8799 | 123.0971 | 123.3391 | 122.715 | 61.6657 | -123.6664
69.2344 | 123.4589 | -61.6058 | 61.6287 | 1.4211e-13 | -0.010859 | 0.00057049 | 0.06569 | -0.0085679 | 0.061377 | -0.0019839 | -0.0029802 | -0.0023289 | 0.061697 | 0.027228 | 0.059073 | -61.4821 | 0.001407 | -61.6275 | 61.636 | 61.1656 | 61.454 | -61.2146 | -61.5918 | 0.014095 | -61.6354 | 61.4363 | 61.6875 | 61.068 | -61.9828 | 0.39124 | 0.0073 | 0.12371 | -0.021652 | -0.41289 | -0.46309 | -0.17469 | -0.37692 | -0.19238 | 0.014078 | -0.029585 | 0.34734 | 0.058759 | -0.56073 | 123.2419 | 122.7715 | 123.0599 | 61.6072 | -122.8433 | 123.0422 | 123.2933 | 122.6738 | 61.6199 | -123.6115
70.9688 | 123.4543 | -61.5921 | 61.6333 | 1.4211e-13 | -0.010645 | 0.00078429 | 0.065477 | -0.0087815 | 0.061377 | -0.0019839 | -0.0029802 | -0.0025425 | 0.061697 | 0.026801 | 0.059073 | -61.4867 | 0.010564 | -61.6366 | 61.6406 | 61.1656 | 61.4861 | -61.2054 | -61.5826 | 0.014095 | -61.6446 | 61.4501 | 61.6875 | 61.0497 | -61.9919 | 0.38666 | 0.0073 | 0.1054 | -0.044542 | -0.43121 | -0.46767 | -0.14722 | -0.39982 | -0.18322 | 0.009502 | -0.052475 | 0.34734 | 0.054181 | -0.58362 | 123.2327 | 122.7577 | 123.0782 | 61.6027 | -122.8387 | 123.0422 | 123.2796 | 122.6418 | 61.6062 | -123.6252
72.7188 | 123.5046 | -61.5601 | 61.6562 | 1.4211e-13 | -0.010431 | 0.00035689 | 0.06569 | -0.0089953 | 0.060949 | 0.0056466 | -0.002553 | -0.0027563 | 0.061484 | 0.026801 | 0.059073 | -61.4867 | 0.010564 | -61.6183 | 61.6314 | 61.1702 | 61.4723 | -61.2054 | -61.5826 | 0.014095 | -61.6354 | 61.4409 | 61.6829 | 61.0634 | -61.9965 | 0.35462 | -0.024745 | 0.073358 | -0.058272 | -0.41289 | -0.48598 | -0.18384 | -0.43644 | -0.21527 | -0.022541 | -0.075361 | 0.36108 | 0.026715 | -0.59277 | 123.1915 | 122.7303 | 123.0324 | 61.5706 | -122.8616 | 123.001 | 123.243 | 122.6235 | 61.5742 | -123.6527
74.3906 | 123.3444 | -61.6745 | 61.6241 | 1.4211e-13 | -0.010645 | 0.00078429 | 0.065477 | -0.0085679 | 0.060949 | -0.0019839 | -0.0029802 | -0.0027563 | 0.061484 | 0.027015 | 0.059073 | -61.4821 | 0.010564 | -61.6183 | 61.6314 | 61.1702 | 61.4586 | -61.2054 | -61.5826 | 0.009516 | -61.6354 | 61.4318 | 61.6875 | 61.0543 | -61.9828 | 0.46906 | 0.007298 | 0.19238 | 0.056169 | -0.41289 | -0.45393 | -0.16554 | -0.30826 | -0.19238 | 0.0919 | 0.03908 | 0.34734 | 0.063336 | -0.56989 | 123.3059 | 122.8447 | 123.1331 | 61.6851 | -122.8296 | 123.1063 | 123.362 | 122.7288 | 61.684 | -123.6069
76.125 | 123.4497 | -61.6196 | 61.6287 | 1.4211e-13 | -0.010859 | 0.00057049 | 0.065477 | -0.0087815 | 0.061163 | 0.0056466 | -0.0029802 | -0.0025425 | 0.061484 | 0.027015 | 0.058859 | -61.4821 | 0.005985 | -61.6229 | 61.636 | 61.1611 | 61.454 | -61.2054 | -61.5826 | 0.014095 | -61.6308 | 61.4318 | 61.6875 | 61.0543 | -61.9873 | 0.41413 | 0.0073 | 0.13744 | -0.003341 | -0.41747 | -0.46767 | -0.17469 | -0.36777 | -0.19696 | 0.036968 | -0.011273 | 0.3565 | 0.058759 | -0.57447 | 123.2556 | 122.7806 | 123.0736 | 61.6256 | -122.8342 | 123.0513 | 123.3071 | 122.6738 | 61.6337 | -123.6161
77.7969 | 123.4039 | -61.6379 | 61.6333 | 1.4211e-13 | -0.010645 | 0.00057049 | 0.065263 | -0.0087815 | 0.061377 | -0.0096144 | -0.0027666 | -0.0027563 | 0.061697 | 0.027228 | 0.0595 | -61.4821 | 0.010564 | -61.6275 | 61.6314 | 61.1565 | 61.4495 | -61.2009 | -61.5826 | 0.018674 | -61.6354 | 61.4318 | 61.6829 | 61.0543 | -61.9919 | 0.43702 | -0.001857 | 0.15575 | 0.010391 | -0.42663 | -0.47683 | -0.18385 | -0.35404 | -0.20154 | 0.055278 | 0.002458 | 0.3565 | 0.049603 | -0.57904 | 123.2693 | 122.7944 | 123.0873 | 61.6484 | -122.8342 | 123.0696 | 123.3208 | 122.6921 | 61.6566 | -123.6252
79.5312 | 123.436 | -61.5921 | 61.647 | 1.4211e-13 | -0.010218 | 0.00057049 | 0.06569 | -0.0085679 | 0.061377 | -0.0019839 | -0.0029802 | -0.0025425 | 0.061697 | 0.027015 | 0.058859 | -61.4821 | 0.005985 | -61.6138 | 61.6314 | 61.1656 | 61.4586 | -61.1963 | -61.578 | 0.009516 | -61.6308 | 61.4318 | 61.6783 | 61.0497 | -61.9919 | 0.39582 | -0.01559 | 0.10998 | -0.02165 | -0.41747 | -0.4814 | -0.18842 | -0.39982 | -0.21527 | 0.014081 | -0.038739 | 0.36108 | 0.031291 | -0.59736 | 123.2235 | 122.7577 | 123.0507 | 61.5981 | -122.8433 | 123.0239 | 123.2704 | 122.6418 | 61.6016 | -123.639
81.2031 | 123.349 | -61.6882 | 61.6196 | 1.4211e-13 | -0.010859 | 0.00078429 | 0.065904 | -0.0083543 | 0.061163 | -0.0019839 | -0.0027666 | -0.0027563 | 0.061697 | 0.027228 | 0.059073 | -61.4775 | 0.005985 | -61.6229 | 61.6314 | 61.1656 | 61.4723 | -61.2009 | -61.578 | 0.014095 | -61.6308 | 61.4226 | 61.6829 | 61.0543 | -61.9873 | 0.48737 | 0.011876 | 0.21069 | 0.065323 | -0.42205 | -0.45394 | -0.14722 | -0.29911 | -0.19696 | 0.11021 | 0.057391 | 0.3565 | 0.063336 | -0.56531 | 123.3197 | 122.8539 | 123.1606 | 61.6942 | -122.8204 | 123.1108 | 123.3711 | 122.7425 | 61.7023 | -123.6069
83 | 123.349 | -61.6837 | 61.5875 | 1.4211e-13 | -0.010431 | 0.00035689 | 0.065263 | -0.0087815 | 0.061163 | -0.0096144 | -0.0027666 | -0.0025425 | 0.061911 | 0.027442 | 0.058859 | -61.473 | 0.015142 | -61.6092 | 61.6269 | 61.1611 | 61.4495 | -61.1963 | -61.5734 | 0.004938 | -61.6263 | 61.4272 | 61.6829 | 61.0497 | -61.9828 | 0.48738 | 0.039342 | 0.21069 | 0.074481 | -0.4129 | -0.42647 | -0.13807 | -0.2991 | -0.16034 | 0.11021 | 0.057392 | 0.3565 | 0.09538 | -0.53785 | 123.3105 | 122.8447 | 123.1331 | 61.6988 | -122.7838 | 123.1108 | 123.3666 | 122.7333 | 61.6886 | -123.5703
84.6875 | 123.3856 | -61.6425 | 61.6333 | 1.4211e-13 | -0.010431 | 0.00057049 | 0.06569 | -0.0089953 | 0.060949 | -0.0019839 | -0.0029802 | -0.0023289 | 0.061484 | 0.027228 | 0.058646 | -61.4775 | 0.005985 | -61.6183 | 61.6269 | 61.1611 | 61.4449 | -61.2009 | -61.5689 | 0.014095 | -61.6263 | 61.4226 | 61.6829 | 61.0543 | -61.9782 | 0.4416 | -0.006435 | 0.16491 | 0.024125 | -0.41747 | -0.47225 | -0.18843 | -0.33572 | -0.21069 | 0.073592 | 0.016193 | 0.35192 | 0.049603 | -0.57904 | 123.2693 | 122.8035 | 123.0873 | 61.6484 | -122.8342 | 123.0651 | 123.3254 | 122.6967 | 61.6566 | -123.6115
86.4844 | 123.4039 | -61.6425 | 61.5967 | 1.4211e-13 | -0.010645 | 0.00035689 | 0.065263 | -0.0085679 | 0.060736 | 0.013277 | -0.0029802 | -0.0023289 | 0.061911 | 0.027015 | 0.058432 | -61.4684 | 0.010564 | -61.6183 | 61.6269 | 61.1656 | 61.4678 | -61.2009 | -61.5734 | 0.009516 | -61.6263 | 61.4135 | 61.6783 | 61.0497 | -61.9828 | 0.4416 | 0.030186 | 0.17407 | 0.024125 | -0.41747 | -0.43105 | -0.12891 | -0.3403 | -0.18323 | 0.069013 | 0.016193 | 0.3565 | 0.081645 | -0.547 | 123.2693 | 122.8081 | 123.1102 | 61.653 | -122.7975 | 123.0559 | 123.3208 | 122.6921 | 61.652 | -123.5794
88.2188 | 123.3261 | -61.6425 | 61.6653 | 1.4211e-13 | -0.010645 | 0.00035689 | 0.065049 | -0.0085679 | 0.060736 | -0.0096144 | -0.0029802 | -0.0027563 | 0.061484 | 0.027442 | 0.059073 | -61.473 | 0.005985 | -61.6138 | 61.6269 | 61.1565 | 61.4495 | -61.1963 | -61.578 | 0.018674 | -61.6263 | 61.3906 | 61.6737 | 61.0451 | -61.9828 | 0.44618 | -0.038478 | 0.16949 | 0.028704 | -0.41747 | -0.50887 | -0.21589 | -0.3403 | -0.27478 | 0.064435 | 0.016193 | 0.3565 | 0.008403 | -0.62024 | 123.2693 | 122.7989 | 123.0919 | 61.6484 | -122.8616 | 123.033 | 123.3162 | 122.6876 | 61.6611 | -123.6481
90 | 123.4726 | -61.5738 | 61.6379 | 1.4211e-13 | -0.010859 | 0.00057049 | 0.065049 | -0.0087815 | 0.060949 | -0.0019839 | -0.0029802 | -0.0025425 | 0.061697 | 0.027442 | 0.058859 | -61.473 | 0.001407 | -61.6092 | 61.6223 | 61.1519 | 61.4449 | -61.1963 | -61.5689 | 0.014095 | -61.6217 | 61.4272 | 61.6783 | 61.0451 | -61.9736 | 0.37751 | -0.01559 | 0.10083 | -0.035382 | -0.4129 | -0.48598 | -0.193 | -0.39981 | -0.21069 | 0.004928 | -0.047892 | 0.35192 | 0.040447 | -0.59278 | 123.1961 | 122.7257 | 123.0187 | 61.5752 | -122.8342 | 123.001 | 123.2521 | 122.6189 | 61.5879 | -123.6115
91.7969 | 123.4314 | -61.5921 | 61.6013 | 1.4211e-13 | -0.010859 | 0.00057049 | 0.06569 | -0.0085679 | 0.061377 | -0.0019839 | -0.0027666 | -0.0027563 | 0.061911 | 0.027228 | 0.058646 | -61.4775 | 0.001407 | -61.6138 | 61.6223 | 61.1519 | 61.4495 | -61.1963 | -61.5734 | 0.014095 | -61.6308 | 61.4226 | 61.6783 | 61.0405 | -61.9873 | 0.39582 | 0.021031 | 0.11456 | -0.02165 | -0.41747 | -0.44936 | -0.1518 | -0.39524 | -0.17865 | 0.018659 | -0.038739 | 0.3565 | 0.077068 | -0.56073 | 123.2144 | 122.744 | 123.0416 | 61.5935 | -122.7975 | 123.0147 | 123.2704 | 122.6326 | 61.6062 | -123.5886
93.5938 | 123.3856 | -61.6333 | 61.6013 | 1.4211e-13 | -0.011286 | 0.00035689 | 0.065263 | -0.0087815 | 0.061377 | 0.0056466 | -0.0029802 | -0.0027563 | 0.061697 | 0.027015 | 0.058859 | -61.4775 | 0.001407 | -61.6138 | 61.6177 | 61.1565 | 61.4495 | -61.1963 | -61.5689 | 0.009516 | -61.6171 | 61.4272 | 61.6737 | 61.0588 | -61.9782 | 0.43702 | 0.016452 | 0.15576 | 0.019549 | -0.41747 | -0.44478 | -0.1518 | -0.34488 | -0.17407 | 0.064437 | 0.016196 | 0.36108 | 0.07249 | -0.54242 | 123.251 | 122.7898 | 123.0828 | 61.6347 | -122.7975 | 123.0605 | 123.307 | 122.6921 | 61.6428 | -123.5794
95.2656 | 123.4543 | -61.5692 | 61.6333 | 1.4211e-13 | -0.010431 | 0.00078429 | 0.065263 | -0.0085679 | 0.060949 | 0.0056466 | -0.002553 | -0.0029699 | 0.061697 | 0.027442 | 0.059073 | -61.4775 | 0.005985 | -61.6183 | 61.6223 | 61.1519 | 61.4861 | -61.1871 | -61.5689 | 0.009516 | -61.6217 | 61.4272 | 61.6783 | 61.0405 | -61.9828 | 0.38209 | -0.011013 | 0.091669 | -0.049117 | -0.43121 | -0.48141 | -0.14722 | -0.41355 | -0.20611 | 0.00035 | -0.05247 | 0.36108 | 0.045024 | -0.59278 | 123.1915 | 122.7211 | 123.0553 | 61.5752 | -122.8204 | 122.9964 | 123.2475 | 122.6097 | 61.5787 | -123.6161
97 | 123.4314 | -61.5875 | 61.6104 | 1.4211e-13 | -0.010859 | 0.00078429 | 0.064836 | -0.0085679 | 0.060949 | -0.0019839 | -0.0029802 | -0.0029699 | 0.061697 | 0.027228 | 0.058646 | -61.4592 | 0.001407 | -61.6092 | 61.6223 | 61.1565 | 61.4815 | -61.1871 | -61.5597 | 0.004938 | -61.6217 | 61.3722 | 61.6737 | 61.0451 | -61.9736 | 0.4004 | 0.011875 | 0.12829 | -0.02165 | -0.42205 | -0.45394 | -0.12891 | -0.38608 | -0.23817 | 0.027818 | -0.03416 | 0.35192 | 0.063334 | -0.56531 | 123.2098 | 122.744 | 123.069 | 61.5889 | -122.7975 | 122.9598 | 123.2613 | 122.6326 | 61.5925 | -123.584
98.6719 | 123.4772 | -61.5372 | 61.6516 | 1.4211e-13 | -0.010859 | 0.00057049 | 0.065049 | -0.0083543 | 0.060949 | 0.020908 | -0.0029802 | -0.0027563 | 0.061697 | 0.027442 | 0.058432 | -61.4638 | 0.005985 | -61.6138 | 61.6269 | 61.1611 | 61.4678 | -61.1871 | -61.5597 | 0.014095 | -61.6171 | 61.4272 | 61.6829 | 61.0451 | -61.9736 | 0.35005 | -0.024745 | 0.073361 | -0.076582 | -0.42663 | -0.49056 | -0.18384 | -0.43643 | -0.22442 | -0.022536 | -0.079935 | 0.3565 | 0.031293 | -0.60651 | 123.164 | 122.6982 | 123.0049 | 61.5432 | -122.8387 | 122.9644 | 123.2201 | 122.5823 | 61.5513 | -123.6252
100.3906 | 123.3627 | -61.6379 | 61.6241 | 1.4211e-13 | -0.011073 | 0.00078429 | 0.064836 | -0.0085679 | 0.060949 | 0.013277 | -0.0031938 | -0.0027563 | 0.061697 | 0.027656 | 0.058646 | -61.4684 | 0.005985 | -61.6092 | 61.6177 | 61.1611 | 61.454 | -61.1825 | -61.546 | 0.014095 | -61.6125 | 61.4226 | 61.6783 | 61.0405 | -61.9736 | 0.45534 | -0.006437 | 0.16949 | 0.028704 | -0.42663 | -0.46309 | -0.17011 | -0.33572 | -0.20154 | 0.091908 | 0.025352 | 0.36108 | 0.054179 | -0.58362 | 123.2556 | 122.7989 | 123.0919 | 61.6439 | -122.8067 | 123.0605 | 123.3162 | 122.6784 | 61.652 | -123.5977
102.1875 | 123.3582 | -61.6196 | 61.6013 | 1.4211e-13 | -0.011073 | 0.00035689 | 0.064836 | -0.0087815 | 0.060949 | 0.0056466 | -0.0031938 | -0.0027563 | 0.061484 | 0.027442 | 0.058646 | -61.4592 | 0.001407 | -61.6046 | 61.6314 | 61.1656 | 61.4769 | -61.1825 | -61.546 | 0.009516 | -61.6125 | 61.4272 | 61.6875 | 61.0451 | -61.969 | 0.43703 | 0.030187 | 0.16034 | 0.014972 | -0.42205 | -0.43562 | -0.12433 | -0.34945 | -0.17407 | 0.073598 | 0.007042 | 0.3565 | 0.086225 | -0.55616 | 123.251 | 122.7852 | 123.0965 | 61.621 | -122.7838 | 123.0468 | 123.3071 | 122.6647 | 61.6291 | -123.5703
103.8438 | 123.3215 | -61.6058 | 61.6745 | 1.4211e-13 | -0.011286 | 0.00057049 | 0.064836 | -0.0089953 | 0.060949 | 0.0056466 | -0.0027666 | -0.0025425 | 0.061697 | 0.027656 | 0.058432 | -61.4592 | 0.005985 | -61.6092 | 61.6269 | 61.1611 | 61.454 | -61.1871 | -61.546 | 0.009516 | -61.6079 | 61.4318 | 61.6829 | 61.0451 | -61.9644 | 0.41871 | -0.047634 | 0.1466 | -0.003339 | -0.42205 | -0.51345 | -0.22047 | -0.35861 | -0.24274 | 0.059865 | -0.002113 | 0.3565 | 0.008404 | -0.6294 | 123.2327 | 122.7669 | 123.0599 | 61.6118 | -122.8616 | 123.0376 | 123.2887 | 122.6509 | 61.6154 | -123.6389
105.5156 | 123.381 | -61.6104 | 61.6241 | 1.4211e-13 | -0.011073 | 0.00078429 | 0.065263 | -0.0089953 | 0.060949 | -0.0019839 | -0.0029802 | -0.0025425 | 0.061911 | 0.027656 | 0.058432 | -61.4501 | 0.005985 | -61.6046 | 61.6269 | 61.1565 | 61.454 | -61.1734 | -61.5414 | 0.014095 | -61.6125 | 61.4318 | 61.6783 | 61.0451 | -61.9644 | 0.43703 | 0.00272 | 0.16034 | 0.005817 | -0.43121 | -0.46767 | -0.17011 | -0.35403 | -0.19238 | 0.069021 | -0.002113 | 0.35192 | 0.054179 | -0.57905 | 123.2373 | 122.7669 | 123.0644 | 61.6164 | -122.7975 | 123.0422 | 123.2887 | 122.6555 | 61.6245 | -123.5886
107.1875 | 123.3536 | -61.6241 | 61.6196 | 1.4211e-13 | -0.010859 | 0.00035689 | 0.064836 | -0.0087815 | 0.060736 | 0.0056466 | -0.0029802 | -0.0029699 | 0.061484 | 0.027442 | 0.058432 | -61.4547 | 0.010564 | -61.5954 | 61.6269 | 61.1565 | 61.4449 | -61.178 | -61.5368 | 0.009516 | -61.6079 | 61.4226 | 61.6783 | 61.0497 | -61.9644 | 0.44618 | 0.007298 | 0.16949 | 0.028707 | -0.41748 | -0.46309 | -0.17469 | -0.3403 | -0.19696 | 0.087333 | 0.016198 | 0.3565 | 0.058757 | -0.56989 | 123.251 | 122.7806 | 123.069 | 61.6347 | -122.7975 | 123.0468 | 123.3025 | 122.6738 | 61.6337 | -123.584
108.8438 | 123.4268 | -61.5829 | 61.5829 | 1.4211e-13 | -0.010859 | 0.00078429 | 0.065049 | -0.0083543 | 0.060949 | 0.0056466 | -0.0031938 | -0.0025425 | 0.061911 | 0.027442 | 0.058646 | -61.4547 | 0.001407 | -61.6 | 61.6223 | 61.1565 | 61.4449 | -61.178 | -61.546 | 0.018674 | -61.6034 | 61.4135 | 61.6829 | 61.0405 | -61.9644 | 0.40498 | 0.039341 | 0.12829 | -0.01707 | -0.42205 | -0.42647 | -0.13807 | -0.3815 | -0.1695 | 0.036977 | -0.020422 | 0.36107 | 0.099957 | -0.54242 | 123.2052 | 122.7394 | 123.0278 | 61.5844 | -122.7609 | 122.9964 | 123.2659 | 122.6235 | 61.6016 | -123.5474
110.5156 | 123.317 | -61.647 | 61.5967 | 1.4211e-13 | -0.011286 | 0.00035689 | 0.065049 | -0.0087815 | 0.060522 | -0.0019839 | -0.0023394 | -0.0025425 | 0.061697 | 0.027656 | 0.058432 | -61.4363 | 0.001407 | -61.6 | 61.6269 | 61.1611 | 61.4495 | -61.1734 | -61.546 | 0.018674 | -61.5988 | 61.4272 | 61.6783 | 61.0405 | -61.9599 | 0.47365 | 0.030186 | 0.2107 | 0.047017 | -0.42663 | -0.43563 | -0.14723 | -0.31283 | -0.16949 | 0.10106 | 0.048244 | 0.36108 | 0.081645 | -0.55616 | 123.2739 | 122.8081 | 123.0965 | 61.6484 | -122.7701 | 123.0742 | 123.3254 | 122.6876 | 61.6657 | -123.5565
112.1875 | 123.4497 | -61.5555 | 61.6425 | 1.4211e-13 | -0.011286 | 0.00078429 | 0.065049 | -0.0087815 | 0.060522 | 0.0056466 | -0.0027666 | -0.0023289 | 0.061911 | 0.027656 | 0.058432 | -61.4455 | -0.003172 | -61.6 | 61.6269 | 61.1565 | 61.4449 | -61.1734 | -61.5322 | 0.014095 | -61.5988 | 61.3768 | 61.6783 | 61.0405 | -61.9599 | 0.3821 | -0.01559 | 0.10999 | -0.044536 | -0.42663 | -0.48598 | -0.19758 | -0.40438 | -0.26563 | 0.023247 | -0.043309 | 0.36108 | 0.035869 | -0.60193 | 123.1823 | 122.712 | 123.0004 | 61.5523 | -122.8158 | 122.9323 | 123.2338 | 122.596 | 61.5696 | -123.6023
113.8594 | 123.3719 | -61.6013 | 61.6104 | 1.4211e-13 | -0.010859 | 0.00035689 | 0.065049 | -0.0089953 | 0.060736 | 0.0056466 | -0.002553 | -0.0023289 | 0.061697 | 0.027656 | 0.058432 | -61.4455 | 0.001407 | -61.5954 | 61.6269 | 61.1656 | 61.4403 | -61.1688 | -61.5277 | 0.018674 | -61.5896 | 61.4318 | 61.6875 | 61.0451 | -61.9507 | 0.43245 | 0.016453 | 0.15576 | 0.005818 | -0.42663 | -0.44478 | -0.17012 | -0.34945 | -0.17865 | 0.073602 | 0.011624 | 0.36107 | 0.077069 | -0.56531 | 123.2281 | 122.7669 | 123.0416 | 61.6027 | -122.7792 | 123.033 | 123.2887 | 122.6464 | 61.6199 | -123.5611
115.5781 | 123.3536 | -61.6287 | 61.6333 | 1.4211e-13 | -0.011286 | 0.00057049 | 0.065049 | -0.0087815 | 0.060736 | -0.0019839 | -0.0029802 | -0.0025425 | 0.061911 | 0.027656 | 0.058432 | -61.4501 | 0.010564 | -61.5863 | 61.6223 | 61.1656 | 61.4586 | -61.1642 | -61.5322 | 0.009516 | -61.5942 | 61.4272 | 61.6737 | 61.0497 | -61.9507 | 0.4645 | -0.011013 | 0.17865 | 0.04244 | -0.42206 | -0.46767 | -0.17469 | -0.32198 | -0.20611 | 0.096489 | 0.034511 | 0.3565 | 0.040446 | -0.58362 | 123.251 | 122.7944 | 123.0873 | 61.6393 | -122.7975 | 123.0559 | 123.3025 | 122.6784 | 61.6382 | -123.584
117.25 | 123.381 | -61.5692 | 61.615 | 1.4211e-13 | -0.011286 | 0.00035689 | 0.064408 | -0.0087815 | 0.060522 | -0.0019839 | -0.0029802 | -0.0027563 | 0.061697 | 0.028083 | 0.058646 | -61.4409 | 0.005985 | -61.5817 | 61.6269 | 61.1565 | 61.4861 | -61.1642 | -61.5231 | 0.018674 | -61.5896 | 61.4272 | 61.6829 | 61.0451 | -61.9461 | 0.40499 | 0.011876 | 0.1283 | -0.01249 | -0.41748 | -0.45851 | -0.12891 | -0.37691 | -0.1878 | 0.046137 | -0.020419 | 0.3565 | 0.067914 | -0.56989 | 123.1961 | 122.7257 | 123.0553 | 61.5752 | -122.7792 | 122.9964 | 123.2521 | 122.6143 | 61.5879 | -123.5611
118.9375 | 123.4314 | -61.5417 | 61.6241 | 1.4211e-13 | -0.011286 | 0.00099789 | 0.064836 | -0.0089953 | 0.060736 | -0.0019839 | -0.0027666 | -0.0031835 | 0.061697 | 0.027656 | 0.058218 | -61.4455 | 0.001407 | -61.5909 | 61.6269 | 61.1656 | 61.4632 | -61.1642 | -61.5093 | 0.004938 | -61.5851 | 61.4318 | 61.6829 | 61.0543 | -61.9415 | 0.37752 | 0.00272 | 0.096252 | -0.049113 | -0.42663 | -0.45851 | -0.16096 | -0.3998 | -0.19238 | 0.032407 | -0.043306 | 0.3565 | 0.058758 | -0.56989 | 123.1686 | 122.7074 | 123.0049 | 61.5432 | -122.7884 | 122.9735 | 123.2247 | 122.596 | 61.5467 | -123.5657
120.6094 | 123.381 | -61.5601 | 61.6333 | 1.4211e-13 | -0.010859 | 0.00057049 | 0.065049 | -0.0092089 | 0.060522 | -0.0019839 | -0.0027666 | -0.0025425 | 0.061484 | 0.027656 | 0.058432 | -61.4409 | 0.001407 | -61.5771 | 61.6314 | 61.1702 | 61.454 | -61.1505 | -61.5185 | 0.014095 | -61.5896 | 61.4363 | 61.6829 | 61.0497 | -61.9415 | 0.40957 | -0.001857 | 0.11914 | -0.017067 | -0.42664 | -0.46309 | -0.17927 | -0.38149 | -0.19696 | 0.041561 | -0.029574 | 0.35192 | 0.049603 | -0.58362 | 123.1915 | 122.7303 | 123.0141 | 61.5615 | -122.7838 | 122.9964 | 123.243 | 122.6097 | 61.5742 | -123.5749
122.3125 | 123.4497 | -61.5417 | 61.6196 | 1.4211e-13 | -0.011286 | 0.00057049 | 0.065049 | -0.0087815 | 0.060522 | -0.0019839 | -0.0027666 | -0.0025425 | 0.061697 | 0.028083 | 0.058432 | -61.4272 | 0.010564 | -61.5863 | 61.6314 | 61.1702 | 61.4723 | -61.1459 | -61.5093 | 0.014095 | -61.5851 | 61.4363 | 61.6829 | 61.0497 | -61.9415 | 0.39584 | 0.011876 | 0.11457 | -0.044535 | -0.44037 | -0.44936 | -0.14722 | -0.3998 | -0.18322 | 0.032407 | -0.043306 | 0.3565 | 0.063336 | -0.56989 | 123.1732 | 122.712 | 123.0141 | 61.5523 | -122.7655 | 122.9781 | 123.2247 | 122.5914 | 61.5558 | -123.5611
123.9844 | 123.2986 | -61.615 | 61.6196 | 1.4211e-13 | -0.011073 | 0.00014309 | 0.064408 | -0.0089953 | 0.060949 | -0.0019839 | -0.0027666 | -0.0025425 | 0.061911 | 0.027869 | 0.058432 | -61.4272 | 0.005985 | -61.5771 | 61.636 | 61.1748 | 61.4586 | -61.1459 | -61.5048 | 0.009516 | -61.5805 | 61.4363 | 61.6875 | 61.0543 | -61.937 | 0.46908 | 0.016455 | 0.18781 | 0.037864 | -0.43122 | -0.44478 | -0.16096 | -0.32198 | -0.18322 | 0.11023 | 0.034515 | 0.3565 | 0.067914 | -0.56531 | 123.251 | 122.7898 | 123.0736 | 61.621 | -122.7655 | 123.0513 | 123.3025 | 122.6692 | 61.6245 | -123.5565
125.6875 | 123.4314 | -61.5692 | 61.5784 | 1.4211e-13 | -0.0115 | 0.00078429 | 0.064836 | -0.0089953 | 0.060736 | -0.0019839 | -0.0023394 | -0.0031835 | 0.061697 | 0.027869 | 0.058646 | -61.4226 | -0.003172 | -61.5771 | 61.636 | 61.1656 | 61.4632 | -61.1459 | -61.491 | 0.014095 | -61.5805 | 61.4409 | 61.6829 | 61.0588 | -61.9324 | 0.4233 | 0.057654 | 0.14661 | -0.007912 | -0.43122 | -0.41274 | -0.11518 | -0.36318 | -0.13745 | 0.078188 | -0.011261 | 0.35192 | 0.10453 | -0.51953 | 123.2052 | 122.7348 | 123.0324 | 61.566 | -122.7243 | 123.0101 | 123.2521 | 122.6281 | 61.5833 | -123.5108
127.3594 | 123.2986 | -61.5555 | 61.6653 | 1.4211e-13 | -0.011714 | 0.00014309 | 0.064836 | -0.0089953 | 0.060522 | -0.0019839 | -0.0031938 | -0.0023289 | 0.061911 | 0.028083 | 0.058646 | -61.4272 | 0.010564 | -61.5771 | 61.636 | 61.1794 | 61.509 | -61.1505 | -61.4864 | 0.014095 | -61.5759 | 61.4135 | 61.6921 | 61.0543 | -61.9278 | 0.40499 | -0.029321 | 0.1283 | -0.021645 | -0.42664 | -0.48597 | -0.15637 | -0.37233 | -0.25189 | 0.069034 | -0.020416 | 0.35192 | 0.026717 | -0.61109 | 123.1915 | 122.7349 | 123.0645 | 61.566 | -122.8158 | 122.9689 | 123.2475 | 122.6097 | 61.5696 | -123.5932
129.0312 | 123.3261 | -61.5967 | 61.6379 | 1.4211e-13 | -0.011073 | 0.00014309 | 0.064836 | -0.0087815 | 0.060308 | -0.017245 | -0.0027666 | -0.0027563 | 0.06127 | 0.027656 | 0.058218 | -61.4043 | 0.005985 | -61.568 | 61.6452 | 61.1794 | 61.4723 | -61.1322 | -61.4773 | 0.004938 | -61.5713 | 61.4501 | 61.6966 | 61.0588 | -61.9187 | 0.46451 | 0.007302 | 0.19239 | 0.02871 | -0.4358 | -0.45851 | -0.16553 | -0.32198 | -0.1878 | 0.11939 | 0.025362 | 0.34734 | 0.058762 | -0.57904 | 123.2419 | 122.776 | 123.069 | 61.6027 | -122.7701 | 123.0468 | 123.2933 | 122.6555 | 61.6016 | -123.5565
130.75 | 123.3856 | -61.528 | 61.647 | 1.4211e-13 | -0.011714 | 0.00035689 | 0.064836 | -0.0087815 | 0.060522 | -0.0096144 | -0.0027666 | -0.0025425 | 0.061697 | 0.028083 | 0.058218 | -61.4089 | 0.005985 | -61.5588 | 61.6406 | 61.1977 | 61.5227 | -61.1368 | -61.4681 | 0.009516 | -61.5576 | 61.4501 | 61.6966 | 61.068 | -61.9095 | 0.39126 | -0.006433 | 0.11915 | -0.030798 | -0.42206 | -0.44935 | -0.12432 | -0.38148 | -0.19695 | 0.059883 | -0.029567 | 0.35192 | 0.049606 | -0.57904 | 123.1686 | 122.7257 | 123.0507 | 61.534 | -122.7838 | 122.9781 | 123.2247 | 122.596 | 61.5375 | -123.5565
132.4219 | 123.3307 | -61.5921 | 61.6791 | 1.4211e-13 | -0.011286 | 0.00035689 | 0.064408 | -0.0085679 | 0.060308 | 0.0056466 | -0.0027666 | -0.0027563 | 0.061697 | 0.027869 | 0.058646 | -61.3997 | 0.010564 | -61.5451 | 61.6498 | 61.1885 | 61.4769 | -61.123 | -61.4544 | 0.018674 | -61.553 | 61.4501 | 61.7058 | 61.0634 | -61.9095 | 0.46909 | -0.029319 | 0.19239 | 0.047024 | -0.42206 | -0.49055 | -0.20215 | -0.3174 | -0.229 | 0.13771 | 0.039099 | 0.3565 | 0.02672 | -0.61566 | 123.2419 | 122.7806 | 123.069 | 61.6027 | -122.8021 | 123.0422 | 123.2979 | 122.6555 | 61.6108 | -123.5886
134.125 | 123.2849 | -61.5372 | 61.6974 | 1.4211e-13 | -0.011286 | 0.00057049 | 0.064408 | -0.0087815 | 0.060949 | -0.0019839 | -0.0029802 | -0.0029699 | 0.061697 | 0.027656 | 0.058218 | -61.3951 | 0.010564 | -61.5405 | 61.6635 | 61.1931 | 61.4861 | -61.1139 | -61.4498 | 0.009516 | -61.5438 | 61.4592 | 61.7104 | 61.0817 | -61.9003 | 0.42331 | -0.033895 | 0.14204 | -0.00333 | -0.42664 | -0.50428 | -0.2113 | -0.36317 | -0.23815 | 0.087353 | -0.006676 | 0.35649 | 0.012987 | -0.61566 | 123.2007 | 122.7303 | 123.0233 | 61.5477 | -122.8112 | 122.9964 | 123.2475 | 122.6189 | 61.5467 | -123.5977
135.8438 | 123.2849 | -61.5509 | 61.7065 | 1.4211e-13 | -0.011286 | 0.00014309 | 0.064836 | -0.0089953 | 0.060522 | 0.0056466 | -0.0027666 | -0.0027563 | 0.061697 | 0.028297 | 0.058218 | -61.3768 | 0.005985 | -61.5313 | 61.6681 | 61.2023 | 61.5319 | -61.1001 | -61.4269 | 0.009516 | -61.5301 | 61.473 | 61.7241 | 61.0863 | -61.8912 | 0.45078 | -0.038471 | 0.17408 | 0.01956 | -0.43122 | -0.50428 | -0.17467 | -0.34028 | -0.23357 | 0.12398 | 0.020793 | 0.36107 | 0.017568 | -0.62024 | 123.219 | 122.7532 | 123.0828 | 61.5569 | -122.8067 | 123.0239 | 123.275 | 122.6372 | 61.5604 | -123.5977
137.5312 | 123.2574 | -61.5829 | 61.6699 | 1.4211e-13 | -0.011286 | 0.00057049 | 0.064408 | -0.0089953 | 0.060095 | -0.0019839 | -0.0027666 | -0.0027563 | 0.061697 | 0.027869 | 0.058859 | -61.3722 | 0.005985 | -61.5313 | 61.6726 | 61.2068 | 61.5136 | -61.1001 | -61.4132 | 0.009516 | -61.5255 | 61.4776 | 61.7333 | 61.0909 | -61.882 | 0.48283 | 0.002728 | 0.2107 | 0.051604 | -0.43122 | -0.46308 | -0.15637 | -0.29908 | -0.19237 | 0.16976 | 0.057416 | 0.3565 | 0.063346 | -0.57903 | 123.2556 | 122.7898 | 123.0965 | 61.5889 | -122.77 | 123.0605 | 123.3162 | 122.6738 | 61.5925 | -123.5519
139.2031 | 123.3582 | -61.4914 | 61.6882 | 1.4211e-13 | -0.0115 | 0.00035689 | 0.064836 | -0.0089953 | 0.060736 | 0.013277 | -0.0029802 | -0.0027563 | 0.061697 | 0.028297 | 0.058432 | -61.3585 | 0.005985 | -61.513 | 61.6864 | 61.2206 | 61.5181 | -61.0772 | -61.3857 | 0.009516 | -61.5164 | 61.4821 | 61.747 | 61.0955 | -61.8729 | 0.41417 | -0.001847 | 0.13289 | -0.021636 | -0.4358 | -0.46765 | -0.1701 | -0.38147 | -0.2061 | 0.10568 | -0.024979 | 0.35649 | 0.058772 | -0.59277 | 123.1778 | 122.712 | 123.0095 | 61.4974 | -122.7655 | 122.9735 | 123.2384 | 122.5869 | 61.5009 | -123.5611
140.875 | 123.2712 | -61.4822 | 61.7523 | 1.4211e-13 | -0.011073 | 0.00035689 | 0.064836 | -0.0089953 | 0.060736 | 0.0056466 | -0.0027666 | -0.0027563 | 0.061911 | 0.027869 | 0.058646 | -61.3494 | 0.010564 | -61.4993 | 61.7001 | 61.2252 | 61.5273 | -61.0681 | -61.3674 | 0.014095 | -61.4981 | 61.4776 | 61.747 | 61.1092 | -61.8546 | 0.41417 | -0.052199 | 0.13289 | -0.017056 | -0.43123 | -0.52716 | -0.22503 | -0.37231 | -0.27477 | 0.11484 | -0.01582 | 0.35649 | -0.005315 | -0.64312 | 123.1824 | 122.7074 | 123.0095 | 61.4928 | -122.8204 | 122.9598 | 123.2292 | 122.5914 | 61.4963 | -123.6069
142.5469 | 123.3582 | -61.4548 | 61.7157 | 1.4211e-13 | -0.0115 | 0.00035689 | 0.064408 | -0.0089953 | 0.060308 | 0.0056466 | -0.0027666 | -0.0027563 | 0.061697 | 0.028297 | 0.058432 | -61.3356 | 0.005985 | -61.4901 | 61.7047 | 61.2481 | 61.5364 | -61.0635 | -61.3445 | 0.014095 | -61.4843 | 61.5096 | 61.7653 | 61.1275 | -61.8408 | 0.39128 | -0.010999 | 0.11916 | -0.035366 | -0.42665 | -0.46764 | -0.17925 | -0.38604 | -0.2061 | 0.11027 | -0.029549 | 0.35649 | 0.049621 | -0.58818 | 123.1595 | 122.7028 | 122.9912 | 61.4608 | -122.7792 | 122.9644 | 123.2201 | 122.5823 | 61.4689 | -123.5565
144.2031 | 123.2666 | -61.496 | 61.7249 | 1.4211e-13 | -0.0115 | 0.00078429 | 0.064408 | -0.0085679 | 0.060522 | -0.0019839 | -0.0029802 | -0.0029699 | 0.061484 | 0.028083 | 0.058432 | -61.3173 | 0.010564 | -61.4718 | 61.7184 | 61.2572 | 61.5731 | -61.0452 | -61.317 | 0.014095 | -61.4614 | 61.5233 | 61.7745 | 61.1413 | -61.8179 | 0.4508 | -0.00642 | 0.17867 | 0.024146 | -0.42665 | -0.46764 | -0.15178 | -0.32195 | -0.20152 | 0.17894 | 0.034543 | 0.35649 | 0.049622 | -0.5836 | 123.2144 | 122.7532 | 123.069 | 61.5065 | -122.77 | 123.0193 | 123.2704 | 122.6372 | 61.5101 | -123.5428
145.875 | 123.3765 | -61.4273 | 61.7157 | 1.4211e-13 | -0.011286 | 0.00078429 | 0.064408 | -0.0089953 | 0.060308 | 0.0056466 | -0.0031938 | -0.0025425 | 0.061697 | 0.027869 | 0.058218 | -61.3081 | 0.005985 | -61.4581 | 61.7322 | 61.2664 | 61.6005 | -61.0269 | -61.2941 | 0.014095 | -61.4523 | 61.5371 | 61.7836 | 61.1504 | -61.8133 | 0.40045 | 0.016471 | 0.11916 | -0.030784 | -0.43123 | -0.44933 | -0.11515 | -0.38604 | -0.17863 | 0.13317 | -0.024965 | 0.36107 | 0.067935 | -0.56529 | 123.1595 | 122.6937 | 123.0279 | 61.4333 | -122.7426 | 122.9644 | 123.2109 | 122.5777 | 61.4414 | -123.529
147.5469 | 123.317 | -61.4365 | 61.7477 | 1.4211e-13 | -0.0115 | 0.00057049 | 0.064195 | -0.0089953 | 0.060522 | 0.0056466 | -0.0027666 | -0.0025425 | 0.061697 | 0.028083 | 0.058646 | -61.2944 | 0.010564 | -61.4444 | 61.7367 | 61.2755 | 61.6005 | -61.0177 | -61.2712 | 0.014095 | -61.4523 | 61.5233 | 61.7882 | 61.1596 | -61.795 | 0.41876 | -0.010995 | 0.14205 | -0.007894 | -0.42665 | -0.47222 | -0.14719 | -0.35857 | -0.22441 | 0.16521 | -0.01581 | 0.34276 | 0.04047 | -0.58818 | 123.1732 | 122.712 | 123.037 | 61.447 | -122.7654 | 122.9598 | 123.2247 | 122.596 | 61.4506 | -123.5428
149.25 | 123.262 | -61.4639 | 61.7569 | 1.4211e-13 | -0.0115 | 0.00078429 | 0.064622 | -0.0089953 | 0.060736 | -0.0019839 | -0.0027666 | -0.0025425 | 0.061697 | 0.027869 | 0.058218 | -61.2761 | 0.005985 | -61.4306 | 61.7551 | 61.2893 | 61.5914 | -61.004 | -61.2621 | 0.014095 | -61.434 | 61.5508 | 61.8111 | 61.1825 | -61.7859 | 0.45996 | -0.001836 | 0.18783 | 0.033307 | -0.42666 | -0.46763 | -0.16551 | -0.32194 | -0.20609 | 0.20184 | 0.029971 | 0.35191 | 0.054208 | -0.57444 | 123.219 | 122.7532 | 123.0553 | 61.4699 | -122.7609 | 123.0147 | 123.275 | 122.6464 | 61.478 | -123.5428
150.9844 | 123.2803 | -61.409 | 61.8301 | 1.4211e-13 | -0.011073 | 0.00035689 | 0.064195 | -0.0089953 | 0.060736 | 0.0056466 | -0.0029802 | -0.0025425 | 0.061484 | 0.028297 | 0.058432 | -61.2669 | 0.005985 | -61.4169 | 61.7734 | 61.2984 | 61.6005 | -60.9902 | -61.2255 | 0.014095 | -61.4111 | 61.5645 | 61.834 | 61.187 | -61.7767 | 0.41877 | -0.056765 | 0.14206 | -0.007889 | -0.42666 | -0.53172 | -0.22959 | -0.36772 | -0.2656 | 0.18354 | -0.002066 | 0.36565 | 0.003859 | -0.6431 | 123.1824 | 122.7074 | 123.0095 | 61.415 | -122.8204 | 122.9735 | 123.243 | 122.596 | 61.4231 | -123.6069
152.6875 | 123.3307 | -61.3586 | 61.7798 | 1.4211e-13 | -0.011714 | 0.00057049 | 0.064195 | -0.0089953 | 0.060736 | 0.0056466 | -0.0029802 | -0.0029699 | 0.061484 | 0.02851 | 0.058432 | -61.2578 | 0.010564 | -61.4077 | 61.778 | 61.3076 | 61.6005 | -60.9811 | -61.2071 | 0.018674 | -61.4111 | 61.5737 | 61.8203 | 61.1962 | -61.763 | 0.37757 | -0.001832 | 0.10086 | -0.049087 | -0.42666 | -0.4722 | -0.17924 | -0.40433 | -0.20609 | 0.1515 | -0.05242 | 0.35191 | 0.040477 | -0.58359 | 123.1366 | 122.6662 | 122.9592 | 61.3692 | -122.7609 | 122.9323 | 123.1789 | 122.5548 | 61.3773 | -123.5428
154.3594 | 123.3398 | -61.4319 | 61.7065 | 1.4211e-13 | -0.0115 | 0.00057049 | 0.064408 | -0.0089953 | 0.060522 | -0.0019839 | -0.0029802 | -0.0025425 | 0.061484 | 0.02851 | 0.058646 | -61.2715 | 0.005985 | -61.4306 | 61.7596 | 61.2893 | 61.5822 | -60.9948 | -61.2255 | 0.009516 | -61.434 | 61.5554 | 61.8065 | 61.1825 | -61.7813 | 0.43708 | 0.053096 | 0.16037 | 0.001264 | -0.43582 | -0.41728 | -0.12431 | -0.34941 | -0.15116 | 0.20642 | -0.002072 | 0.34734 | 0.099983 | -0.52408 | 123.1915 | 122.7211 | 123.0141 | 61.4379 | -122.7013 | 122.9873 | 123.2384 | 122.6143 | 61.4414 | -123.4878
156.0625 | 123.1293 | -69.4244 | 54.538 | 1.4211e-13 | -0.011714 | 0.00057049 | 0.064622 | -0.0092089 | 0.060522 | -0.0019839 | -0.0029802 | -0.0027563 | 0.061911 | 0.02851 | 0.058432 | -66.8434 | -0.30536 | -66.9749 | 56.2518 | 56.0143 | 56.239 | -67.0481 | -66.8619 | -0.31099 | -67.0017 | 55.9834 | 56.2298 | 55.9079 | -67.3995 | 2.3763 | 1.7139 | 2.581 | 2.4495 | 0.073225 | 1.4764 | 1.701 | 2.0249 | 1.4454 | 2.5626 | 2.4228 | 0.39783 | 1.6918 | 1.3699 | 125.6763 | 125.4388 | 125.6634 | 69.1191 | -121.5861 | 125.4078 | 125.6542 | 125.3323 | 69.1134 | -121.9375
157.7656 | 123.381 | -119.0414 | 4.1428 | 1.4211e-13 | -0.012141 | -7.051e-05 | 0.063554 | -0.0087815 | 0.060736 | 0.013277 | -0.0034076 | -0.0036109 | 0.061056 | 0.028083 | 0.059287 | -118.1534 | -0.255 | -118.5721 | 4.4886 | 4.4465 | 4.6565 | -118.8495 | -118.1709 | -0.25147 | -118.4526 | 4.3929 | 4.5191 | 4.4627 | -119.163 | 0.19192 | 0.34582 | 0.88804 | 0.4693 | 0.27738 | 0.30373 | 0.51371 | -0.12159 | 0.25011 | 0.87057 | 0.58881 | 0.7104 | 0.37629 | 0.31997 | 123.53 | 123.4879 | 123.6979 | 118.7864 | -122.9923 | 123.4343 | 123.5605 | 123.5042 | 118.79 | -123.3058
159.4531 | 123.3124 | -119.3069 | 3.9185 | 1.4211e-13 | -0.011714 | 0.00014309 | 0.063767 | -0.0096363 | 0.060736 | 0.013277 | -0.0036212 | -0.0033973 | 0.061056 | 0.028724 | 0.059287 | -118.8219 | -0.17716 | -119.2772 | 3.843 | 3.865 | 4.0521 | -119.5638 | -118.8348 | -0.16448 | -119.1349 | 3.7977 | 3.9193 | 3.8996 | -119.859 | -0.25688 | -0.075424 | 0.48509 | 0.02975 | 0.28663 | -0.053486 | 0.13364 | -0.55206 | -0.12079 | 0.47216 | 0.17209 | 0.72415 | 0.000797 | -0.018894 | 123.15 | 123.1719 | 123.359 | 119.1298 | -123.4823 | 123.1046 | 123.2262 | 123.2065 | 119.1425 | -123.7775
161.125 | 123.3078 | -120.195 | 3.0899 | 1.4211e-13 | -0.012355 | 0.00035689 | 0.063981 | -0.0089953 | 0.060949 | 0.020908 | -0.0036212 | -0.0033973 | 0.061056 | 0.028724 | 0.059287 | -119.3987 | -0.16342 | -119.8495 | 3.2387 | 3.2834 | 3.4752 | -120.1316 | -119.4392 | -0.1599 | -119.7118 | 3.2299 | 3.3424 | 3.3135 | -120.4451 | 0.06339 | 0.14878 | 0.79628 | 0.34553 | 0.28214 | 0.19354 | 0.38528 | -0.25009 | 0.14003 | 0.75583 | 0.48323 | 0.73332 | 0.25245 | 0.2236 | 123.4337 | 123.4785 | 123.6702 | 120.0316 | -123.2215 | 123.4249 | 123.5374 | 123.5085 | 120.0351 | -123.535
162.7969 | 123.2758 | -119.4122 | 3.8544 | 1.4211e-13 | -0.012355 | -7.051e-05 | 0.063767 | -0.0089953 | 0.060949 | -0.0019839 | -0.0036212 | -0.0029699 | 0.061056 | 0.02851 | 0.059287 | -118.8402 | -0.14969 | -119.2909 | 3.7972 | 3.4483 | 4.0292 | -119.3715 | -118.7615 | -0.137 | -119.1486 | 3.7885 | 3.9009 | 3.2998 | -119.8636 | 0.040716 | -0.057121 | 0.57207 | 0.1213 | 0.080584 | -0.40608 | 0.17483 | -0.45136 | -0.065859 | 0.6507 | 0.26364 | 0.71499 | 0.04657 | -0.5546 | 123.2095 | 122.8605 | 123.4414 | 119.2625 | -123.2259 | 123.2007 | 123.3132 | 122.712 | 119.2752 | -123.718
164.5312 | 123.3078 | -118.9636 | 4.2892 | 1.4211e-13 | -0.012141 | -7.051e-05 | 0.063767 | -0.0089953 | 0.061163 | -0.0019839 | -0.0036212 | -0.0031835 | 0.061056 | 0.028724 | 0.0595 | -117.952 | -0.14969 | -118.389 | 4.6946 | 4.3458 | 4.9312 | -118.3687 | -117.7954 | -0.1599 | -118.2512 | 4.6813 | 4.8029 | 4.1834 | -118.9432 | 0.59489 | 0.40537 | 1.0117 | 0.57461 | -0.020278 | 0.056512 | 0.64194 | 0.020377 | 0.39207 | 1.1682 | 0.71246 | 0.69208 | 0.51368 | -0.10581 | 123.6582 | 123.3094 | 123.8948 | 118.8139 | -122.658 | 123.6449 | 123.7665 | 123.1471 | 118.8037 | -123.2325
166.2031 | 123.4497 | -119.7784 | 3.3783 | 1.4211e-13 | -0.012782 | -7.051e-05 | 0.063767 | -0.0092089 | 0.061163 | -0.0096144 | -0.0038348 | -0.0033973 | 0.060843 | 0.028724 | 0.10202 | -118.7898 | -0.14969 | -119.236 | 3.9117 | 3.897 | 4.0933 | -119.518 | -40.9326 | -0.15532 | -119.0799 | 3.8389 | 3.9559 | 3.9225 | -112.4596 | 0.2604 | 0.53341 | 0.98864 | 0.54245 | 0.28205 | 0.51873 | 0.715 | 7.3188 | 0.46058 | 78.8458 | 0.69853 | -6.6203 | 0.57759 | 0.54416 | 123.6902 | 123.6755 | 123.8717 | 119.6288 | -122.8963 | 123.6173 | 123.7343 | 123.7009 | 119.6231 | -115.8379
167.8906 | 123.2254 | -57.3853 | 65.5838 | 1.4211e-13 | -0.011927 | 0.00035689 | 0.064195 | -0.0094225 | 0.060308 | 0.0056466 | -0.0029802 | -0.0027563 | 0.061484 | 0.028297 | 0.072106 | -56.7481 | 0.17539 | -56.9073 | 66.3884 | 66.3627 | 66.3943 | -56.9058 | -32.7505 | 0.19724 | -56.8461 | 66.2163 | 66.4034 | 66.37 | -55.1695 | 0.47943 | 0.80459 | 0.63718 | 0.47797 | -0.001453 | 0.77891 | 0.81054 | 2.2158 | 0.63249 | 24.6348 | 0.53917 | -1.6766 | 0.81964 | 0.78622 | 123.7736 | 123.748 | 123.7796 | 57.5606 | -122.4896 | 123.6015 | 123.7887 | 123.7553 | 57.5825 | -120.7533
169.5625 | 123.4589 | -118.7485 | 4.3579 | 1.4211e-13 | -0.011927 | -7.051e-05 | 0.063981 | -0.0089953 | 0.060949 | 0.013277 | -0.0031938 | -0.0031835 | 0.060629 | 0.028724 | 0.12231 | -118.277 | -0.17716 | -118.7186 | 4.4062 | 4.3961 | 4.5878 | -118.9915 | -3.4696 | -0.17363 | -118.5534 | 4.3379 | 4.4641 | 4.4307 | -119.2912 | -0.24299 | 0.048265 | 0.47145 | 0.029829 | 0.27282 | 0.038217 | 0.22988 | -0.54276 | -0.01998 | 115.2789 | 0.19511 | 0.73787 | 0.1062 | 0.072771 | 123.1546 | 123.1446 | 123.3363 | 118.5713 | -123.3494 | 123.0864 | 123.2126 | 123.1792 | 118.5748 | -123.6491
171.25 | 123.3032 | -118.6661 | 4.5044 | 1.4211e-13 | -0.011714 | -0.00028411 | 0.063767 | -0.0083543 | 0.060736 | 0.0056466 | -0.0031938 | -0.0031835 | 0.060629 | 0.028724 | 0.12296 | -118.0664 | -0.14511 | -118.508 | 4.6214 | 4.5976 | 4.7709 | -118.79 | -2.8515 | -0.12327 | -118.3656 | 4.544 | 4.661 | 4.6276 | -119.0943 | -0.12391 | 0.11696 | 0.59966 | 0.15803 | 0.28195 | 0.093204 | 0.26654 | -0.42827 | 0.039567 | 115.8146 | 0.30044 | 0.72871 | 0.15659 | 0.12317 | 123.2874 | 123.2637 | 123.437 | 118.521 | -123.2944 | 123.21 | 123.3271 | 123.2936 | 118.5428 | -123.5987
173 | 123.3078 | -118.8354 | 4.3762 | 1.4211e-13 | -0.012568 | 0.00014309 | 0.063554 | -0.0087815 | 0.060522 | -0.0019839 | -0.0038348 | -0.0033973 | 0.060843 | 0.028724 | 0.12274 | -118.2587 | -0.13595 | -118.7003 | 4.3558 | 4.4099 | 4.5924 | -118.9823 | -2.9888 | -0.11869 | -118.5488 | 4.3471 | 4.4733 | 4.4398 | -119.2775 | -0.14686 | -0.020409 | 0.57674 | 0.13512 | 0.28198 | 0.033642 | 0.21615 | -0.44205 | -0.029134 | 115.8466 | 0.28667 | 0.72872 | 0.097044 | 0.063617 | 123.1913 | 123.2453 | 123.4278 | 118.6995 | -123.3585 | 123.1825 | 123.3087 | 123.2753 | 118.7168 | -123.6537
174.6719 | 123.2803 | -118.9911 | 4.2709 | 1.4211e-13 | -0.011927 | -7.051e-05 | 0.063981 | -0.0089953 | 0.060522 | -0.0019839 | -0.0034076 | -0.0031835 | 0.060843 | 0.028724 | 0.12338 | -118.3777 | -0.11764 | -118.8239 | 4.223 | 3.9062 | 4.4642 | -118.6435 | -2.6867 | -0.11869 | -118.677 | 4.2235 | 4.3405 | 3.7622 | -119.4194 | 0.34762 | -0.047896 | 0.61334 | 0.16714 | -0.18048 | -0.36475 | 0.19323 | -0.42835 | -0.047467 | 116.3044 | 0.3141 | 0.74246 | 0.069551 | -0.50873 | 123.2141 | 122.8973 | 123.4553 | 118.8735 | -122.9144 | 123.2146 | 123.3316 | 122.7533 | 118.8724 | -123.6904
176.3438 | 123.2986 | -118.8675 | 4.3716 | 1.4211e-13 | -0.012141 | 0.00014309 | 0.063554 | -0.0089953 | 0.060949 | 0.0056466 | -0.0031938 | -0.0031835 | 0.061056 | 0.028938 | 0.12274 | -118.0939 | -0.12679 | -118.5447 | 4.5161 | 4.2496 | 4.748 | -118.355 | -2.8194 | -0.11869 | -118.3794 | 4.4982 | 4.6289 | 4.014 | -119.131 | 0.5125 | 0.14441 | 0.7736 | 0.32282 | -0.18968 | -0.12204 | 0.3764 | -0.26348 | 0.12653 | 116.0481 | 0.48812 | 0.75161 | 0.2573 | -0.35762 | 123.3835 | 123.1171 | 123.6155 | 118.7407 | -122.7266 | 123.3657 | 123.4964 | 122.8815 | 118.7488 | -123.5026
178.0469 | 123.3078 | -119.1055 | 4.129 | 1.4211e-13 | -0.012355 | 0.00014309 | 0.063767 | -0.0092089 | 0.060522 | 0.013277 | -0.0034076 | -0.0031835 | 0.060629 | 0.02851 | 0.12296 | -118.4006 | -0.12222 | -118.8331 | 4.2047 | 3.897 | 4.4367 | -118.6572 | -2.9797 | -0.11869 | -118.6861 | 4.196 | 4.3084 | 3.7073 | -119.4332 | 0.44833 | 0.075697 | 0.70489 | 0.27243 | -0.1759 | -0.232 | 0.30767 | -0.32765 | 0.066969 | 116.1258 | 0.41939 | 0.74703 | 0.17941 | -0.42177 | 123.3103 | 123.0026 | 123.5422 | 118.9833 | -122.7862 | 123.3015 | 123.414 | 122.8128 | 118.9868 | -123.5622
179.7188 | 123.4131 | -118.7576 | 4.4128 | 1.4211e-13 | -0.012141 | 0.00014309 | 0.063554 | -0.0094225 | 0.060736 | 0.0056466 | -0.0034076 | -0.0038245 | 0.061056 | 0.028724 | 0.12253 | -118.1305 | -0.12222 | -118.5767 | 4.4748 | 4.1214 | 4.6931 | -118.4328 | -2.9476 | -0.10953 | -118.4252 | 4.4524 | 4.5786 | 3.9682 | -119.163 | 0.32479 | 0.062008 | 0.62711 | 0.18091 | -0.14388 | -0.29145 | 0.28025 | -0.4054 | 0.03955 | 115.81 | 0.33247 | 0.73787 | 0.16573 | -0.4446 | 123.2325 | 122.879 | 123.4507 | 118.6354 | -122.8457 | 123.21 | 123.3362 | 122.7259 | 118.6481 | -123.5759
181.3906 | 123.3124 | -119.3802 | 3.7903 | 1.4211e-13 | -0.011927 | 0.00014309 | 0.063554 | -0.0087815 | 0.060736 | 0.013277 | -0.0034076 | -0.0036109 | 0.060843 | 0.028938 | 0.12274 | -118.6937 | -0.13137 | -119.1444 | 3.9071 | 3.5994 | 4.1391 | -118.9503 | -3.1949 | -0.11869 | -118.9883 | 3.8892 | 4.02 | 3.4051 | -119.7308 | 0.42993 | 0.11685 | 0.68653 | 0.23576 | -0.19417 | -0.19089 | 0.3488 | -0.35061 | 0.098955 | 116.1853 | 0.39185 | 0.74246 | 0.2297 | -0.38521 | 123.2873 | 122.9796 | 123.5193 | 119.2488 | -122.7405 | 123.2694 | 123.4002 | 122.7853 | 119.2615 | -123.5211
183.0781 | 123.349 | -119.0735 | 4.1199 | 1.4211e-13 | -0.012355 | 0.00057049 | 0.063981 | -0.0089953 | 0.060308 | -0.0019839 | -0.0034076 | -0.0031835 | 0.060843 | 0.028938 | 0.12296 | -118.538 | -0.10848 | -118.975 | 4.0582 | 3.6727 | 4.2215 | -118.7991 | -2.9522 | -0.10495 | -118.8189 | 4.0495 | 4.1665 | 3.5607 | -119.566 | 0.27434 | -0.061656 | 0.53549 | 0.098457 | -0.17588 | -0.44722 | 0.10163 | -0.49248 | -0.070388 | 116.1213 | 0.25456 | 0.74704 | 0.046626 | -0.55913 | 123.1317 | 122.7461 | 123.295 | 118.965 | -122.919 | 123.123 | 123.24 | 122.6342 | 118.9685 | -123.6858
184.75 | 123.2712 | -119.2154 | 4.01 | 1.4211e-13 | -0.012568 | 0.00014309 | 0.063554 | -0.0089953 | 0.060522 | 0.0056466 | -0.0036212 | -0.0038245 | 0.060843 | 0.028938 | 0.12296 | -118.9638 | -0.11306 | -119.4237 | 3.6141 | 3.3933 | 3.7774 | -119.257 | -2.9751 | -0.10037 | -119.2631 | 3.6099 | 3.7315 | 3.1212 | -120.0193 | -0.041649 | -0.3959 | 0.25161 | -0.20831 | -0.16666 | -0.61667 | -0.23263 | -0.80387 | -0.40006 | 116.2403 | -0.047669 | 0.75621 | -0.27848 | -0.88881 | 122.8295 | 122.6087 | 122.9928 | 119.1023 | -123.2671 | 122.8253 | 122.9469 | 122.3366 | 119.115 | -124.0293
186.4219 | 123.2712 | -119.2657 | 3.9276 | 1.4211e-13 | -0.012568 | 0.00014309 | 0.063126 | -0.0087815 | 0.060736 | 0.0056466 | -0.0038348 | -0.0031835 | 0.06127 | 0.028724 | 0.12274 | -118.5517 | -0.11764 | -119.0025 | 4.0262 | 3.6314 | 4.194 | -118.8266 | -3.053 | -0.11411 | -118.8418 | 4.0266 | 4.1436 | 3.5333 | -119.5889 | 0.43912 | 0.098556 | 0.71402 | 0.26325 | -0.17588 | -0.29617 | 0.26642 | -0.32311 | 0.09898 | 116.2128 | 0.42393 | 0.74704 | 0.21599 | -0.39434 | 123.2919 | 122.8972 | 123.4598 | 119.1481 | -122.7542 | 123.2923 | 123.4094 | 122.799 | 119.1516 | -123.5165
188.0938 | 123.2346 | -119.2657 | 3.9459 | 1.4211e-13 | -0.012141 | -7.051e-05 | 0.059921 | -0.0089953 | 0.056676 | -0.0019839 | -0.0038348 | -0.0036109 | 0.060843 | 0.029365 | 0.12274 | -118.6937 | -0.12222 | -119.149 | 3.8888 | 3.5307 | 4.0567 | -118.964 | -3.1903 | -0.10953 | -118.9792 | 3.8801 | 4.0017 | 3.3959 | -119.7262 | 0.30176 | -0.057106 | 0.57209 | 0.11674 | -0.18501 | -0.41521 | 0.11075 | -0.46048 | -0.065842 | 116.0754 | 0.28657 | 0.74704 | 0.055746 | -0.55001 | 123.1546 | 122.7965 | 123.3224 | 119.1435 | -122.9099 | 123.1458 | 123.2674 | 122.6617 | 119.1562 | -123.6721
189.7656 | 123.2986 | -119.1513 | 4.0146 | 1.4211e-13 | -0.012355 | 0.00035689 | 0.06334 | -0.0089953 | 0.060736 | 0.0056466 | -0.0036212 | -0.0033973 | 0.060843 | 0.029151 | 0.12274 | -118.5746 | -0.11764 | -119.0117 | 4.0033 | 3.6635 | 4.1757 | -118.8724 | -3.1857 | -0.10953 | -118.8556 | 4.0083 | 4.1207 | 3.5195 | -119.6072 | 0.27889 | -0.011311 | 0.57669 | 0.13965 | -0.13924 | -0.35109 | 0.16113 | -0.45587 | -0.006309 | 115.9656 | 0.29575 | 0.75162 | 0.10613 | -0.49505 | 123.1546 | 122.8148 | 123.327 | 119.0337 | -122.887 | 123.1596 | 123.272 | 122.6708 | 119.0418 | -123.6218
191.4375 | 123.4039 | -122.2916 | 0.79193 | 1.4211e-13 | -0.012141 | -7.051e-05 | 0.06334 | -0.0087815 | 0.060522 | -0.0019839 | -0.0034076 | -0.0036109 | -0.0038927 | 0.028938 | 0.0073689 | -121.8161 | -0.13137 | -122.2805 | 0.83961 | 0.81999 | 1.0119 | -122.563 | 0.11094 | 0.096512 | -0.010564 | 0.78044 | 0.89738 | 0.86395 | -0.13668 | -0.27146 | 0.047679 | 0.47545 | 0.011017 | 0.28248 | 0.028055 | 0.21997 | 122.1549 | -0.011492 | 122.4025 | 122.281 | 0.12611 | 0.10545 | 0.072018 | 123.1312 | 123.1116 | 123.3035 | 122.1602 | -123.355 | 123.072 | 123.1889 | 123.1555 | 122.3881 | -0.92861
193.1562 | 123.262 | -122.3099 | 0.92468 | 1.4211e-13 | -0.012782 | -7.051e-05 | -0.0022608 | -0.0089953 | -0.0027221 | -0.0019839 | 1.0612e-05 | 0.00044874 | -0.0038927 | 0.029151 | 0.0075825 | -121.7429 | -0.12679 | -122.2119 | 0.8625 | 0.9253 | 1.1172 | -122.4943 | 0.76569 | 0.046146 | 0.026066 | 0.87201 | 0.98895 | 0.95552 | -0.095467 | -0.18447 | -0.062181 | 0.56701 | 0.098001 | 0.28247 | 0.000619 | 0.19252 | 122.2144 | -0.052674 | 123.0756 | 122.3359 | 0.12153 | 0.064266 | 0.030838 | 123.1724 | 123.2352 | 123.4271 | 122.1831 | -123.419 | 123.1819 | 123.2988 | 123.2654 | 122.356 | -1.0202
194.9688 | 123.3994 | -122.2092 | 0.95673 | 1.4211e-13 | -0.012141 | -0.00028411 | -0.0022608 | -0.0089953 | -0.0025083 | 0.020908 | -0.00041659 | 2.134e-05 | -0.0036791 | 0.029365 | 0.0073689 | -121.7062 | -0.12222 | -122.1707 | 0.90829 | 0.97109 | 1.1584 | -121.9815 | 0.80232 | 0.014095 | 0.030644 | 0.91779 | 1.0347 | 0.63044 | -0.086309 | 0.22766 | -0.04844 | 0.50293 | 0.038498 | -0.18917 | 0.014365 | 0.20169 | 122.1229 | -0.038932 | 123.0115 | 122.2398 | 0.11695 | 0.078009 | -0.32628 | 123.1175 | 123.1803 | 123.3676 | 122.087 | -122.9382 | 123.127 | 123.2439 | 122.8396 | 122.2233 | -1.043
196.7031 | 123.3765 | -122.1451 | 1.0254 | 1.4211e-13 | -0.012568 | -7.051e-05 | -0.0024744 | -0.0092089 | -0.0025083 | -0.0019839 | 0.0015062 | 0.0017305 | -0.0038927 | 0.029365 | 0.0069417 | -121.6238 | -0.13137 | -122.0791 | 0.9907 | 0.58646 | 1.2408 | -121.8945 | 0.89848 | -0.00422 | 0.030644 | 1.0002 | 1.1126 | 0.50682 | -0.077151 | 0.25058 | -0.034694 | 0.52126 | 0.065978 | -0.1846 | -0.43893 | 0.21544 | 122.0679 | -0.025184 | 123.0436 | 122.1757 | 0.1078 | 0.08718 | -0.51857 | 123.1358 | 122.7315 | 123.3859 | 122.0137 | -122.9199 | 123.1453 | 123.2577 | 122.6519 | 122.1409 | -1.1025
198.3906 | 123.2666 | -122.3328 | 0.92926 | 1.4211e-13 | -0.012355 | -7.051e-05 | -0.0024744 | -0.0089953 | -0.0025083 | 0.013277 | 0.00086521 | 0.0013033 | -0.0038927 | 0.028938 | 0.0075825 | -121.7566 | -0.11764 | -122.2165 | 0.86708 | 0.44451 | 1.1081 | -122.041 | 0.76111 | -0.00422 | 0.035223 | 0.86743 | 0.97979 | 0.36488 | -0.077151 | 0.29174 | -0.062179 | 0.57617 | 0.11631 | -0.17542 | -0.48474 | 0.17879 | 122.2556 | -0.061829 | 123.0939 | 122.368 | 0.11237 | 0.050532 | -0.56438 | 123.1998 | 122.7773 | 123.4408 | 122.2151 | -122.9703 | 123.2002 | 123.3126 | 122.6976 | 122.3285 | -1.0064
200.125 | 123.2758 | -122.2549 | 0.99335 | 1.4211e-13 | -0.012355 | -7.051e-05 | -0.0022608 | -0.0087815 | -0.0022947 | 0.0056466 | 0.0010788 | 0.0015169 | -0.0038927 | 0.029151 | 0.0073689 | -121.6605 | -0.12222 | -122.1203 | 0.96781 | 0.54983 | 1.2042 | -121.9494 | 0.85727 | -0.017956 | 0.030644 | 0.96816 | 1.0805 | 0.47019 | -0.08173 | 0.30549 | -0.025542 | 0.59449 | 0.13464 | -0.17086 | -0.44352 | 0.21086 | 122.1732 | -0.025189 | 123.1122 | 122.2856 | 0.11237 | 0.087174 | -0.52316 | 123.2227 | 122.8048 | 123.4591 | 122.1327 | -122.9428 | 123.2231 | 123.3355 | 122.7251 | 122.237 | -1.0751
201.8438 | 123.381 | -122.374 | 0.82855 | 1.4211e-13 | -0.012568 | -7.051e-05 | -0.0029018 | -0.0092089 | -0.0022947 | 0.0056466 | 0.00086521 | 0.0010897 | -0.0041063 | 0.029365 | 0.0073689 | -121.8207 | -0.12222 | -122.2805 | 0.81214 | 0.39415 | 0.82876 | -122.1051 | 0.70617 | -0.017956 | 0.035223 | 0.80333 | 0.91569 | 0.31452 | -0.08173 | 0.26883 | -0.016412 | 0.55327 | 0.093414 | -0.17542 | -0.43441 | 0.000204 | 122.2922 | -0.02522 | 123.0801 | 122.4092 | 0.11695 | 0.087139 | -0.51404 | 123.1861 | 122.7681 | 123.2027 | 122.2517 | -122.9337 | 123.1773 | 123.2897 | 122.6885 | 122.356 | -0.91028
203.5781 | 123.2529 | -122.3602 | 0.94757 | 1.4211e-13 | -0.012782 | 0.00014309 | -0.0024744 | -0.0085679 | -0.0025083 | 0.013277 | 0.00086521 | 0.0019443 | -0.0043199 | 0.029365 | 0.0073689 | -121.807 | -0.11764 | -122.2622 | 0.83045 | 0.4033 | 0.94322 | -122.0868 | 0.71991 | -0.017956 | 0.035223 | 0.82622 | 0.94316 | 0.33283 | -0.072572 | 0.27341 | -0.11712 | 0.55327 | 0.097994 | -0.17542 | -0.54427 | -0.00435 | 122.2877 | -0.12135 | 123.0801 | 122.3955 | 0.1078 | -0.004408 | -0.61474 | 123.1907 | 122.7635 | 123.3034 | 122.2426 | -123.0344 | 123.1865 | 123.3034 | 122.6931 | 122.3423 | -1.0201
205.25 | 123.3582 | -122.3328 | 0.86975 | 1.4211e-13 | -0.012996 | 0.00014309 | -0.0026882 | -0.0094225 | -0.0025083 | 0.013277 | 0.0012926 | 0.0017305 | -0.0038927 | 0.029151 | 0.0073689 | -121.7474 | -0.13137 | -122.221 | 0.87166 | 0.45367 | 1.0027 | -122.0456 | 0.77485 | -0.027113 | 0.035223 | 0.87201 | 0.99353 | 0.3832 | -0.08173 | 0.28716 | 0.001908 | 0.58532 | 0.11173 | -0.17542 | -0.41608 | 0.13299 | 122.251 | 0.002258 | 123.1076 | 122.368 | 0.11695 | 0.12378 | -0.48656 | 123.2044 | 122.7864 | 123.3355 | 122.2014 | -122.9154 | 123.2048 | 123.3263 | 122.716 | 122.3057 | -0.95148
206.9844 | 123.2895 | -122.3831 | 0.89264 | 1.4211e-13 | -0.012782 | -0.00028411 | -0.0024744 | -0.0089953 | -0.0022947 | 0.0056466 | 0.0012926 | 0.0015169 | -0.0038927 | 0.029579 | 0.0073689 | -121.7978 | -0.12222 | -122.2622 | 0.84419 | 0.42162 | 0.96611 | -122.0822 | 0.73822 | -0.031692 | 0.026066 | 0.84912 | 0.96148 | 0.34199 | -0.063415 | 0.30088 | -0.04845 | 0.58531 | 0.12088 | -0.18 | -0.47102 | 0.073475 | 122.3197 | -0.043522 | 123.1213 | 122.4092 | 0.089481 | 0.068838 | -0.55065 | 123.2273 | 122.8047 | 123.3492 | 122.2609 | -122.9749 | 123.2322 | 123.3446 | 122.7251 | 122.3514 | -0.95605
208.7188 | 123.317 | -122.3053 | 0.91553 | 1.4211e-13 | -0.012782 | -7.051e-05 | -0.0022608 | -0.0089953 | -0.0022947 | 0.013277 | 0.0015062 | 0.0019443 | -0.0041063 | 0.028938 | 0.0075825 | -121.7246 | -0.12222 | -122.189 | 0.90829 | 0.4903 | 1.0165 | -122.0181 | 0.8069 | -0.031692 | 0.039802 | 0.8949 | 1.0302 | 0.40609 | -0.067994 | 0.28716 | -0.007241 | 0.58075 | 0.11632 | -0.17085 | -0.42522 | 0.10095 | 122.2373 | -0.020625 | 123.1122 | 122.3451 | 0.1078 | 0.11463 | -0.50944 | 123.2136 | 122.7956 | 123.3218 | 122.1831 | -122.9337 | 123.2002 | 123.3355 | 122.7114 | 122.2736 | -0.98352
210.4531 | 123.3536 | -122.2321 | 0.97046 | 1.4211e-13 | -0.012782 | -0.00028411 | -0.0026882 | -0.0089953 | -0.0022947 | 0.0056466 | 0.0017198 | 0.0019443 | -0.0036791 | 0.029151 | 0.0073689 | -121.6879 | -0.12222 | -122.1524 | 0.94491 | 0.52694 | 1.0943 | -121.9769 | 0.84353 | -0.040849 | 0.039802 | 0.95442 | 1.053 | 0.45645 | -0.072572 | 0.25513 | -0.025546 | 0.54413 | 0.0797 | -0.17543 | -0.44352 | 0.12386 | 122.1595 | -0.016037 | 123.0756 | 122.2719 | 0.11237 | 0.08259 | -0.514 | 123.177 | 122.759 | 123.3264 | 122.1098 | -122.9474 | 123.1865 | 123.2851 | 122.6885 | 122.1912 | -1.043
212.1094 | 123.2437 | -122.2412 | 1.03 | 1.4211e-13 | -0.012355 | -0.00028411 | -0.0022608 | -0.0092089 | -0.0020811 | -0.0096144 | 0.002147 | 0.0021579 | -0.0038927 | 0.029579 | 0.0073689 | -121.6559 | -0.12679 | -122.1157 | 0.98154 | 0.56815 | 1.0943 | -121.9357 | 0.87558 | -0.031692 | 0.035223 | 0.98647 | 1.0943 | 0.48392 | -0.067994 | 0.3055 | -0.048428 | 0.58534 | 0.12548 | -0.18002 | -0.46182 | 0.064347 | 122.1732 | -0.043496 | 123.1168 | 122.2764 | 0.10322 | 0.064289 | -0.54604 | 123.2228 | 122.8094 | 123.3355 | 122.1144 | -122.9657 | 123.2277 | 123.3355 | 122.7251 | 122.2095 | -1.098
213.7812 | 123.2941 | -121.6782 | 1.5976 | 1.4211e-13 | -0.012782 | 0.00014309 | -0.0024744 | -0.0089953 | -0.0022947 | 0.0056466 | 0.005779 | 0.0068583 | -0.0036791 | 0.029792 | 0.0075825 | -121.166 | -0.11764 | -121.6304 | 1.4623 | 1.0581 | 1.6163 | -121.4503 | 1.3563 | -0.031692 | 0.039802 | 1.4626 | 1.5659 | 0.97384 | -0.058836 | 0.22782 | -0.13532 | 0.51217 | 0.04773 | -0.18009 | -0.5395 | 0.018681 | 121.6193 | -0.13496 | 123.0345 | 121.718 | 0.098638 | -0.031742 | -0.62376 | 123.1404 | 122.7363 | 123.2944 | 121.5605 | -123.0479 | 123.1408 | 123.244 | 122.652 | 121.6465 | -1.6564
215.4688 | 123.3994 | -121.6141 | 1.5564 | 1.4211e-13 | -0.012782 | -7.051e-05 | -0.0022608 | -0.0092089 | -0.0025083 | 0.0056466 | 0.010479 | 0.011132 | -0.0032517 | 0.029579 | 0.0071553 | -121.079 | -0.12679 | -121.5389 | 1.5538 | 1.1588 | 1.7216 | -121.3633 | 1.4525 | -0.031692 | 0.026066 | 1.545 | 1.662 | 1.0563 | -0.067994 | 0.25073 | -0.002557 | 0.53508 | 0.075209 | -0.17552 | -0.39757 | 0.16519 | 121.5461 | -0.011348 | 123.0666 | 121.6401 | 0.09406 | 0.10561 | -0.50014 | 123.1679 | 122.7729 | 123.3357 | 121.4873 | -122.9197 | 123.1591 | 123.2761 | 122.6703 | 121.5824 | -1.6244
217.1406 | 123.3948 | -120.3369 | 2.7374 | 1.4211e-13 | -0.013209 | -7.051e-05 | -0.0024744 | -0.0094225 | -0.0025083 | 0.0056466 | 0.28394 | 0.29231 | -0.0030381 | 0.029792 | 0.0071553 | -119.852 | -0.11306 | -120.3073 | 2.7396 | 2.3539 | 2.8708 | -120.3239 | 2.5239 | -0.027113 | 0.044381 | 2.6759 | 2.7838 | 2.1872 | -0.16873 | 0.012983 | 0.002214 | 0.48492 | 0.029605 | 0.016622 | -0.3835 | 0.13339 | 120.1682 | -0.061491 | 122.8608 | 120.3813 | 0.21311 | 0.046334 | -0.55026 | 123.0766 | 122.6908 | 123.2077 | 120.2239 | -123.0614 | 123.0128 | 123.1207 | 122.5241 | 120.3098 | -2.9062
218.8125 | 123.3261 | -120.6802 | 2.4216 | 1.4211e-13 | -0.012996 | -0.00028411 | -0.0026882 | -0.0089953 | -0.0025083 | -0.0019839 | 0.29398 | 0.30171 | -0.0030381 | 0.029579 | 0.0073689 | -120.0763 | -0.12222 | -120.5316 | 2.4833 | 2.1021 | 2.6648 | -120.5162 | 2.2767 | -0.036271 | 0.044381 | 2.415 | 2.5319 | 1.9308 | -0.17331 | 0.16399 | 0.061682 | 0.60391 | 0.14859 | -0.015399 | -0.31948 | 0.24321 | 120.5069 | -0.006608 | 122.9569 | 120.7246 | 0.21769 | 0.11037 | -0.49081 | 123.1635 | 122.7823 | 123.345 | 120.558 | -122.9378 | 123.0952 | 123.2122 | 122.611 | 120.644 | -2.5949
220.5625 | 123.1979 | -120.8771 | 2.2797 | 1.4211e-13 | -0.013209 | 0.00014309 | -0.0024744 | -0.0094225 | -0.0022947 | -0.0019839 | 0.2959 | 0.30406 | -0.0034653 | 0.029365 | 0.0073689 | -120.2686 | -0.11764 | -120.7331 | 2.2818 | 1.8777 | 2.445 | -120.7544 | 2.0569 | -0.031692 | 0.039802 | 2.2044 | 2.3167 | 1.7201 | -0.17788 | 0.12273 | 0.00214 | 0.60845 | 0.14399 | 0.021261 | -0.40195 | 0.16534 | 120.6992 | -0.075312 | 122.934 | 120.9169 | 0.21769 | 0.037081 | -0.55952 | 123.1589 | 122.7548 | 123.3221 | 120.7594 | -123.034 | 123.0814 | 123.1938 | 122.5972 | 120.8454 | -2.4575
222.2188 | 123.1796 | -120.5109 | 2.6688 | 1.4211e-13 | -0.012996 | -0.00028411 | -0.0024744 | -0.0089953 | -0.0027221 | -0.0096144 | 0.2818 | 0.28889 | -0.0032517 | 0.029579 | 0.0069417 | -119.9664 | -0.11306 | -120.4355 | 2.5611 | 2.1708 | 2.738 | -120.4292 | 2.3499 | -0.017956 | 0.044381 | 2.502 | 2.6144 | 2.0086 | -0.14125 | 0.081617 | -0.10768 | 0.54441 | 0.075363 | -0.006254 | -0.49799 | 0.069272 | 120.3696 | -0.16681 | 122.8608 | 120.5552 | 0.18564 | -0.054409 | -0.66016 | 123.0719 | 122.6816 | 123.2489 | 120.3978 | -123.098 | 123.0128 | 123.1252 | 122.5195 | 120.4929 | -2.81
223.9531 | 123.2803 | -120.7352 | 2.3071 | 1.4211e-13 | -0.012782 | -0.00028411 | -0.0026882 | -0.0089953 | -0.0025083 | -0.0019839 | 0.28522 | 0.29359 | -0.0032517 | 0.029579 | 0.0073689 | -120.1999 | -0.11306 | -120.6644 | 2.3139 | 1.9693 | 2.4954 | -120.5666 | 2.0981 | -0.031692 | 0.039802 | 2.2547 | 2.3625 | 1.7522 | -0.18246 | 0.16855 | 0.006722 | 0.53522 | 0.070753 | -0.097801 | -0.33783 | 0.18824 | 120.5527 | -0.052414 | 122.8333 | 120.775 | 0.22227 | 0.055401 | -0.55493 | 123.049 | 122.7045 | 123.2305 | 120.6221 | -122.8737 | 122.9899 | 123.0977 | 122.4874 | 120.7035 | -2.4896
225.625 | 123.2483 | -120.7535 | 2.3529 | 1.4211e-13 | -0.012996 | -7.051e-05 | -0.0026882 | -0.0092089 | -0.0027221 | 0.0056466 | 0.30017 | 0.30876 | -0.0032517 | 0.029579 | 0.0071553 | -120.1175 | -0.11764 | -120.582 | 2.3825 | 2.0013 | 2.5457 | -120.5758 | 2.1576 | -0.027113 | 0.035223 | 2.3097 | 2.4312 | 1.8209 | -0.16873 | 0.17771 | 0.029622 | 0.63594 | 0.17147 | -0.006234 | -0.35156 | 0.19283 | 120.5848 | -0.043248 | 122.9111 | 120.7887 | 0.20395 | 0.078304 | -0.53203 | 123.136 | 122.7548 | 123.2992 | 120.6358 | -122.9287 | 123.0631 | 123.1847 | 122.5744 | 120.7264 | -2.5216
227.3594 | 123.1659 | -120.5429 | 2.5726 | 1.4211e-13 | -0.012782 | -0.00028411 | -0.0022608 | -0.0087815 | -0.0029357 | 0.013277 | 0.29483 | 0.30277 | -0.0032517 | 0.029365 | 0.0069417 | -120.0305 | -0.11306 | -120.4904 | 2.4649 | 2.0792 | 2.6327 | -120.4521 | 2.2584 | -0.027113 | 0.048959 | 2.3966 | 2.5136 | 1.9033 | -0.16415 | 0.090767 | -0.10769 | 0.51236 | 0.052468 | -0.038299 | -0.49344 | 0.060094 | 120.3788 | -0.17598 | 122.8013 | 120.5919 | 0.21311 | -0.059009 | -0.66934 | 123.0078 | 122.6221 | 123.1756 | 120.4298 | -123.0248 | 122.9396 | 123.0565 | 122.4462 | 120.5158 | -2.7368
229.0781 | 123.1018 | -120.9 | 2.2385 | 1.4211e-13 | -0.013423 | -0.00028411 | -0.0026882 | -0.0089953 | -0.0029357 | 0.013277 | 0.27966 | 0.28782 | -0.0038927 | 0.029365 | 0.0071553 | -120.3098 | -0.11764 | -120.7697 | 2.1811 | 1.7861 | 2.3351 | -120.5941 | 1.979 | -0.031692 | 0.039802 | 2.1128 | 2.2343 | 1.6286 | -0.17788 | 0.30588 | -0.057386 | 0.59013 | 0.13025 | -0.17563 | -0.45232 | 0.096653 | 120.7221 | -0.12568 | 122.879 | 120.9398 | 0.21769 | -0.004135 | -0.60989 | 123.081 | 122.6861 | 123.2351 | 120.7823 | -122.8326 | 123.0127 | 123.1343 | 122.5285 | 120.8683 | -2.4163
230.75 | 123.1476 | -119.2978 | 3.598 | 1.4211e-13 | -0.014705 | -0.00071151 | -0.0024744 | -0.010277 | -0.0029357 | -0.0019839 | 0.21109 | 0.22436 | -0.0041063 | 0.029792 | 0.0073689 | -112.1328 | -0.47019 | -112.5105 | 10.326 | 10.1244 | 10.4713 | -113.0205 | 0.66038 | -0.013377 | -0.001407 | 0.79417 | 0.93401 | 0.76322 | -0.20536 | 6.2772 | 6.728 | 7.165 | 6.7873 | 0.51005 | 6.5263 | 6.8733 | 119.0924 | -2.8038 | 119.9582 | 119.2964 | 0.20395 | -2.664 | -2.8348 | 129.6238 | 129.4222 | 129.7691 | 118.8276 | -116.6186 | 120.092 | 120.2318 | 120.061 | 119.2844 | -3.8034
232.4844 | 123.3032 | -118.515 | 4.4998 | 1.4211e-13 | -0.013209 | -7.051e-05 | -0.0024744 | -0.0094225 | -0.0027221 | 0.0056466 | 0.0077016 | 0.0096359 | -0.0041063 | 0.029792 | 0.0071553 | -118.1214 | -0.1039 | -118.563 | 4.4977 | 4.4831 | 4.6656 | -118.79 | 0.078886 | -0.022535 | -0.001407 | 0.14861 | 0.26095 | 0.2321 | -0.22825 | -0.27498 | -0.002075 | 0.39366 | -0.047969 | 0.22701 | -0.016691 | 0.16581 | 118.2868 | -4.3512 | 118.5939 | 118.5136 | 0.22685 | -4.2389 | -4.2677 | 123.0128 | 122.9981 | 123.1806 | 118.4111 | -123.2898 | 118.6636 | 118.776 | 118.7471 | 118.4925 | -4.7281
234.2188 | 123.2025 | -118.1992 | 4.9164 | 1.4211e-13 | -0.012996 | -7.051e-05 | -0.0026882 | -0.0092089 | -0.0027221 | 0.0056466 | 0.0077016 | 0.0092087 | -0.0043199 | 0.029792 | 0.0073689 | -117.6727 | -0.1039 | -118.0685 | 4.9602 | 4.9456 | 5.1326 | -118.3413 | 0.083464 | -0.027113 | -0.001407 | 0.14861 | 0.26553 | -0.17997 | -0.24199 | -0.1421 | 0.043777 | 0.52648 | 0.13063 | 0.27273 | 0.029215 | 0.21626 | 117.9572 | -4.7678 | 118.2826 | 118.1978 | 0.24058 | -4.6509 | -5.0964 | 123.1593 | 123.1448 | 123.3318 | 118.0953 | -123.2576 | 118.3478 | 118.4647 | 118.0192 | 118.172 | -5.1584
235.9531 | 123.2025 | -118.2724 | 4.9026 | 1.4211e-13 | -0.013209 | -7.051e-05 | -0.0026882 | -0.0089953 | -0.0027221 | 0.0056466 | 0.0079152 | 0.0098495 | -0.0045337 | 0.029792 | 0.0075825 | -117.7368 | -0.099323 | -118.1418 | 4.9098 | 4.8952 | 5.0777 | -118.4145 | 0.078886 | -0.022535 | 0.003172 | 0.14403 | 0.25637 | -0.17081 | -0.23283 | -0.14212 | 0.007148 | 0.53563 | 0.13062 | 0.27274 | -0.00742 | 0.17505 | 118.0396 | -4.7586 | 118.3513 | 118.2756 | 0.236 | -4.6463 | -5.0735 | 123.1822 | 123.1676 | 123.3501 | 118.1731 | -123.3172 | 118.4164 | 118.5288 | 118.1016 | 118.2499 | -5.1355
237.6875 | 123.2758 | -118.5745 | 4.5547 | 1.4211e-13 | -0.012996 | -7.051e-05 | -0.0022608 | -0.0094225 | -0.0029357 | -0.0019839 | 0.0077016 | 0.0098495 | -0.0047473 | 0.029579 | 0.0071553 | -118.0298 | -0.11764 | -118.4256 | 4.5756 | 4.6159 | 4.803 | -118.6984 | 0.06515 | -0.017956 | -0.005985 | 0.13945 | 0.25179 | -0.17081 | -0.22825 | -0.12389 | 0.020826 | 0.54473 | 0.14889 | 0.27278 | 0.061166 | 0.24823 | 118.3463 | -4.4153 | 118.6397 | 118.5685 | 0.22227 | -4.303 | -4.7256 | 123.1501 | 123.1904 | 123.3775 | 118.4569 | -123.2532 | 118.714 | 118.8263 | 118.4037 | 118.5566 | -4.783
239.3594 | 123.2346 | -118.1763 | 5.0079 | 1.4211e-13 | -0.012996 | -0.00028411 | -0.0024744 | -0.0092089 | -0.0027221 | -0.0019839 | 0.0077016 | 0.0096359 | -0.0043199 | 0.030006 | 0.0073689 | -118.071 | -0.099323 | -118.4714 | 4.5344 | 4.5839 | 4.7572 | -118.7442 | 0.069728 | -0.017956 | -0.005985 | 0.13487 | 0.25179 | -0.16624 | -0.22825 | -0.56793 | -0.47357 | 0.10527 | -0.29515 | 0.27278 | -0.42407 | -0.25074 | 117.948 | -4.8731 | 118.246 | 118.1703 | 0.22227 | -4.7561 | -5.1742 | 122.7106 | 122.7601 | 122.9335 | 118.0769 | -123.7521 | 118.3111 | 118.4281 | 118.01 | 118.1583 | -5.2362
241.0938 | 123.2437 | -115.1825 | 7.9742 | 1.4211e-13 | -0.012782 | 0.00014309 | -0.0026882 | -0.0092089 | -0.0025083 | 0.0056466 | 0.0079152 | 0.0098495 | -0.0045337 | 0.029579 | 0.0071553 | -114.7105 | -0.090166 | -115.0926 | 7.9132 | 7.9631 | 8.1408 | -114.8979 | 0.069728 | -0.017956 | -0.015143 | 0.13945 | 0.26553 | -0.17539 | -0.22367 | 0.28459 | -0.061023 | 0.47204 | 0.089848 | -0.19474 | -0.011134 | 0.16654 | 114.9588 | -7.8348 | 115.2522 | 115.1674 | 0.20853 | -7.7087 | -8.1496 | 123.0957 | 123.1456 | 123.3233 | 115.0923 | -122.8721 | 115.3219 | 115.448 | 115.0071 | 115.1645 | -8.1979
242.8438 | 123.2895 | -115.8142 | 7.2968 | 1.4211e-13 | -0.012782 | -7.051e-05 | -0.0024744 | -0.0089953 | -0.0029357 | 0.0056466 | 0.0079152 | 0.0092087 | -0.0043199 | 0.029792 | 0.0071553 | -115.2736 | -0.1039 | -115.6558 | 7.3547 | 7.1252 | 7.5776 | -115.4611 | 0.060571 | -0.022535 | -0.005985 | 0.13945 | 0.25637 | -0.16624 | -0.23283 | 0.3531 | 0.057903 | 0.54061 | 0.15843 | -0.19466 | -0.17159 | 0.28086 | 115.5814 | -7.1573 | 115.8748 | 115.8082 | 0.22685 | -7.0404 | -7.463 | 123.1689 | 122.9394 | 123.3918 | 115.7103 | -122.7579 | 115.9537 | 116.0706 | 115.648 | 115.7917 | -7.5296
244.5312 | 123.0469 | -94.7067 | 28.3997 | 1.4211e-13 | -0.012782 | 0.00014309 | -0.0016198 | -0.0092089 | -0.0027221 | -0.0096144 | 0.0077016 | 0.0094223 | -0.0049609 | 0.029792 | 0.0071553 | -94.4236 | -0.016908 | -94.6964 | 28.3191 | 27.9043 | 28.3828 | -94.4576 | 0.042256 | -0.017956 | -0.019721 | 0.12114 | 0.24721 | -0.17081 | -0.25572 | 0.24914 | -0.080564 | 0.2831 | 0.010318 | -0.23882 | -0.49533 | -0.016872 | 94.451 | -28.2785 | 94.749 | 94.687 | 0.236 | -28.1524 | -28.5705 | 123.0258 | 122.6111 | 123.0895 | 94.6898 | -122.8572 | 94.8279 | 94.9539 | 94.5359 | 94.6888 | -28.6554
246.2656 | 123.0331 | -94.6426 | 28.4454 | 1.4211e-13 | -0.013209 | 0.00035689 | -0.0024744 | -0.0092089 | -0.0029357 | -0.0019839 | 0.008129 | 0.0096359 | -0.0045337 | 0.029792 | 0.0071553 | -94.3321 | -0.026065 | -94.6048 | 28.4152 | 28.0005 | 28.511 | -94.334 | 0.046835 | -0.017956 | -0.019721 | 0.12571 | 0.23806 | -0.17081 | -0.25572 | 0.30868 | -0.030195 | 0.31058 | 0.037797 | -0.27089 | -0.44495 | 0.065552 | 94.3869 | -28.3197 | 94.6895 | 94.6229 | 0.236 | -28.2074 | -28.6163 | 123.0579 | 122.6431 | 123.1536 | 94.6166 | -122.7794 | 94.7684 | 94.8807 | 94.4718 | 94.6247 | -28.7012
248.0156 | 123.2986 | -94.5786 | 28.4821 | 1.4211e-13 | -0.012996 | -7.051e-05 | -0.0022608 | -0.0089953 | -0.0029357 | 0.0056466 | 0.008129 | 0.0096359 | -0.0045337 | 0.030006 | 0.0071553 | -94.4648 | -0.035222 | -94.7285 | 28.2916 | 27.9639 | 28.3874 | -94.7232 | 0.046835 | -0.017956 | -0.019721 | 0.12114 | 0.24264 | -0.17081 | -0.25115 | -0.14461 | -0.19043 | 0.11372 | -0.1499 | -0.005291 | -0.51821 | -0.094691 | 94.3274 | -28.3609 | 94.6254 | 94.5588 | 0.23142 | -28.2394 | -28.6529 | 122.8702 | 122.5424 | 122.9659 | 94.5433 | -123.2052 | 94.6997 | 94.8212 | 94.4077 | 94.5606 | -28.7332
249.6875 | 123.2986 | -94.4962 | 28.5828 | 1.4211e-13 | -0.013209 | 0.00035689 | -0.0024744 | -0.0092089 | -0.0031493 | 0.0056466 | 0.0085562 | 0.0096359 | -0.0045337 | 0.030006 | 0.0071553 | -94.2084 | -0.035222 | -94.4675 | 28.5526 | 28.1424 | 28.5797 | -94.2332 | 0.042256 | -0.017956 | -0.028879 | 0.12571 | 0.24264 | -0.16624 | -0.24657 | 0.26294 | -0.030172 | 0.28772 | 0.028662 | -0.23427 | -0.44034 | -0.003098 | 94.2496 | -28.4571 | 94.5384 | 94.4673 | 0.21769 | -28.3401 | -28.749 | 123.0487 | 122.6386 | 123.0758 | 94.4609 | -122.816 | 94.6219 | 94.7388 | 94.3299 | 94.4782 | -28.8293
251.4219 | 123.3215 | -117.0364 | 6.0471 | 1.4211e-13 | -0.012782 | 0.00014309 | -0.0022608 | -0.0092089 | -0.0027221 | 0.0056466 | 0.0085562 | 0.0096359 | -0.0043199 | 0.03022 | 0.0067279 | -116.5922 | -0.13137 | -116.9881 | 6.0498 | 6.1041 | 6.2727 | -117.2561 | 0.060571 | -0.017956 | -0.005985 | 0.13945 | 0.25179 | -0.17539 | -0.23283 | -0.21961 | 0.002758 | 0.44426 | 0.048383 | 0.268 | 0.057007 | 0.22566 | 116.8036 | -5.9076 | 117.097 | 117.0305 | 0.22685 | -5.7953 | -6.2225 | 123.0863 | 123.1405 | 123.3092 | 116.9051 | -123.3031 | 117.1759 | 117.2882 | 116.861 | 117.0185 | -6.2799
253.1719 | 123.2391 | -117.3935 | 5.7999 | 1.4211e-13 | -0.013209 | -7.051e-05 | -0.0024744 | -0.0092089 | -0.0027221 | 0.0056466 | 0.0083426 | 0.0096359 | -0.0043199 | 0.029792 | 0.0069417 | -116.8944 | -0.12679 | -117.2902 | 5.7614 | 5.4584 | 5.9797 | -117.1004 | 0.060571 | -0.013377 | -0.001407 | 0.14403 | 0.26553 | -0.17539 | -0.23283 | 0.29313 | -0.038489 | 0.49914 | 0.10327 | -0.18985 | -0.34143 | 0.17982 | 117.1607 | -5.6558 | 117.4541 | 117.3921 | 0.23142 | -5.5343 | -5.9753 | 123.1549 | 122.8519 | 123.3732 | 117.2667 | -122.9002 | 117.5375 | 117.659 | 117.2181 | 117.3801 | -6.0327
254.9062 | 123.23 | -117.3065 | 5.8685 | 1.4211e-13 | -0.013209 | 0.00014309 | -0.0022608 | -0.0092089 | -0.0027221 | 0.013277 | 0.0083426 | 0.0096359 | -0.0043199 | 0.03022 | 0.0073689 | -116.8211 | -0.11306 | -117.2124 | 5.8346 | 5.463 | 6.0026 | -117.0225 | 0.060571 | -0.022535 | -0.005985 | 0.14403 | 0.27011 | -0.16624 | -0.23283 | 0.28399 | -0.033898 | 0.48542 | 0.094128 | -0.18986 | -0.40551 | 0.13405 | 117.0737 | -5.7245 | 117.3671 | 117.3005 | 0.22685 | -5.5984 | -6.0348 | 123.1412 | 122.7695 | 123.3091 | 117.1935 | -122.8911 | 117.4505 | 117.5766 | 117.1403 | 117.284 | -6.1014
256.6094 | 123.2391 | -117.0914 | 6.102 | 1.4211e-13 | -0.012996 | -7.051e-05 | -0.0022608 | -0.0094225 | -0.0027221 | -0.0019839 | 0.0087698 | 0.0098495 | -0.0049609 | 0.030006 | 0.0069417 | -116.5922 | -0.11306 | -116.9881 | 6.0636 | 5.7606 | 6.2269 | -116.789 | 0.06515 | -0.008798 | -0.005985 | 0.13945 | 0.25637 | -0.17539 | -0.23283 | 0.30237 | -0.038439 | 0.49919 | 0.10331 | -0.19905 | -0.34134 | 0.12494 | 116.8585 | -5.9625 | 117.1565 | 117.0854 | 0.22685 | -5.8456 | -6.2774 | 123.1549 | 122.852 | 123.3183 | 116.9783 | -122.891 | 117.2308 | 117.3477 | 116.916 | 117.0826 | -6.3348
258.2812 | 123.2483 | -117.1005 | 6.1295 | 1.4211e-13 | -0.013423 | 0.00014309 | -0.0029018 | -0.0094225 | -0.0022947 | 0.0056466 | 0.0085562 | 0.0096359 | -0.0045337 | 0.029792 | 0.0073689 | -116.5098 | -0.12222 | -116.9011 | 6.1414 | 5.8156 | 6.3048 | -116.7341 | 0.060571 | -0.008798 | -0.010564 | 0.13945 | 0.26095 | -0.16624 | -0.22825 | 0.36647 | 0.011928 | 0.59076 | 0.19946 | -0.16701 | -0.31386 | 0.17531 | 116.8723 | -5.99 | 117.1611 | 117.09 | 0.21769 | -5.8685 | -6.2957 | 123.2419 | 122.9161 | 123.4053 | 116.9783 | -122.8635 | 117.24 | 117.3615 | 116.9343 | 117.0917 | -6.3577
260.0312 | 123.3444 | -117.0959 | 6.0516 | 1.4211e-13 | -0.012996 | 0.00014309 | -0.0026882 | -0.0092089 | -0.0029357 | 0.0056466 | 0.0085562 | 0.0096359 | -0.0043199 | 0.03022 | 0.0071553 | -116.2946 | -0.12679 | -116.6767 | 6.3657 | 6.0216 | 6.5337 | -116.4914 | 0.060571 | -0.008798 | -0.001407 | 0.14403 | 0.25637 | -0.17539 | -0.23283 | 0.60457 | 0.31409 | 0.80136 | 0.41921 | -0.18536 | -0.029991 | 0.48206 | 116.8631 | -5.9076 | 117.1565 | 117.0945 | 0.23142 | -5.7953 | -6.227 | 123.4617 | 123.1176 | 123.6296 | 116.9692 | -122.543 | 117.24 | 117.3523 | 116.9206 | 117.0871 | -6.2845
261.7344 | 123.3032 | -116.1713 | 6.9901 | 1.4211e-13 | -0.013423 | 0.00014309 | -0.0022608 | -0.0094225 | -0.0027221 | 0.0056466 | 0.0083426 | 0.0096359 | -0.0045337 | 0.029792 | 0.0071553 | -115.6673 | -0.099323 | -116.1182 | 6.9289 | 6.5803 | 7.0831 | -115.9236 | 0.051413 | -0.017956 | -0.005985 | 0.13945 | 0.25179 | -0.17539 | -0.22367 | 0.24768 | -0.061185 | 0.50392 | 0.053083 | -0.1946 | -0.40978 | 0.093076 | 115.9476 | -6.8506 | 116.2227 | 116.1653 | 0.21769 | -6.7383 | -7.1654 | 123.1001 | 122.7515 | 123.2544 | 116.0719 | -122.9136 | 116.3107 | 116.4231 | 115.9959 | 116.1533 | -7.2137
263.4062 | 123.2529 | -116.8716 | 6.2942 | 1.4211e-13 | -0.012996 | -7.051e-05 | -0.0026882 | -0.0092089 | -0.0029357 | 0.013277 | 0.0087698 | 0.0098495 | -0.0043199 | 0.030006 | 0.0069417 | -116.3175 | -0.10848 | -116.7729 | 6.2742 | 5.9163 | 6.4421 | -116.5875 | 0.055992 | -0.013377 | -0.001407 | 0.14861 | 0.26095 | -0.17081 | -0.22825 | 0.28411 | -0.020093 | 0.55417 | 0.098767 | -0.18535 | -0.37792 | 0.14787 | 116.6434 | -6.1456 | 116.9276 | 116.8702 | 0.22685 | -6.0333 | -6.4651 | 123.1458 | 122.788 | 123.3138 | 116.7632 | -122.8818 | 117.0203 | 117.1326 | 116.7008 | 116.8583 | -6.5225
265.125 | 123.3582 | -116.1987 | 6.9397 | 1.4211e-13 | -0.013209 | 0.00014309 | -0.0022608 | -0.0094225 | -0.0027221 | -0.0019839 | 0.0087698 | 0.0096359 | -0.0047473 | 0.03022 | 0.0069417 | -115.7406 | -0.10848 | -116.1823 | 6.8693 | 6.5391 | 7.0282 | -115.9923 | 0.060571 | -0.008798 | -0.010564 | 0.13945 | 0.26095 | -0.17081 | -0.23283 | 0.20646 | -0.07035 | 0.45813 | 0.016452 | -0.19001 | -0.40063 | 0.088487 | 115.9659 | -6.8002 | 116.2593 | 116.1882 | 0.22227 | -6.6787 | -7.1105 | 123.0681 | 122.7378 | 123.2269 | 116.0902 | -122.932 | 116.3382 | 116.4597 | 116.0279 | 116.1899 | -7.1725
266.8594 | 123.2529 | -116.098 | 7.1091 | 1.4211e-13 | -0.013209 | 0.00014309 | -0.0024744 | -0.0094225 | -0.0027221 | 0.0056466 | 0.0083426 | 0.010063 | -0.0047473 | 0.030433 | 0.0073689 | -115.5849 | -0.10848 | -116.0266 | 7.0296 | 6.6306 | 7.1793 | -115.8412 | 0.06515 | -0.008798 | -0.005985 | 0.13945 | 0.25637 | -0.17539 | -0.21452 | 0.25686 | -0.079479 | 0.51309 | 0.071405 | -0.18545 | -0.47843 | 0.070208 | 115.8835 | -6.9696 | 116.1632 | 116.092 | 0.20853 | -6.8527 | -7.2845 | 123.1276 | 122.7287 | 123.2773 | 115.9895 | -122.9502 | 116.2375 | 116.3544 | 115.9226 | 116.0892 | -7.3236
268.5469 | 123.2529 | -117.4438 | 5.7541 | 1.4211e-13 | -0.013637 | -7.051e-05 | -0.0031156 | -0.0089953 | -0.0027221 | -0.0096144 | 0.008129 | 0.0087813 | -0.0043199 | 0.030006 | 0.0069417 | -116.8577 | -0.11306 | -117.3085 | 5.7385 | 5.4081 | 5.911 | -117.1233 | 0.055992 | -0.008798 | -0.001407 | 0.13945 | 0.26095 | -0.17081 | -0.22367 | 0.32059 | -0.015604 | 0.58612 | 0.13531 | -0.18527 | -0.34602 | 0.15692 | 117.2202 | -5.6146 | 117.4998 | 117.4424 | 0.22227 | -5.4931 | -5.9249 | 123.1823 | 122.8519 | 123.3549 | 117.3308 | -122.8774 | 117.5833 | 117.7048 | 117.273 | 117.4351 | -5.9778
270.2344 | 123.2803 | -117.2928 | 5.8456 | 1.4211e-13 | -0.013423 | 0.00014309 | -0.0026882 | -0.0096363 | -0.0025083 | 0.013277 | 0.0085562 | 0.0081403 | -0.0047473 | 0.030433 | 0.0071553 | -116.789 | -0.11764 | -117.2444 | 5.8117 | 5.463 | 5.9843 | -117.0637 | 0.055992 | -0.00422 | -0.001407 | 0.14861 | 0.26095 | -0.17081 | -0.22367 | 0.22905 | -0.033902 | 0.50374 | 0.048347 | -0.1807 | -0.38263 | 0.13862 | 117.0691 | -5.697 | 117.3488 | 117.2914 | 0.22227 | -5.5847 | -6.0165 | 123.1045 | 122.7558 | 123.277 | 117.1751 | -122.9094 | 117.4414 | 117.5537 | 117.122 | 117.2886 | -6.0693
272.0156 | 123.3124 | -117.2928 | 5.8868 | 1.4211e-13 | -0.013423 | -7.051e-05 | -0.0026882 | -0.0098499 | -0.0025083 | 0.0056466 | 0.0085562 | 0.0083539 | -0.0045337 | 0.030006 | 0.0071553 | -116.7799 | -0.10848 | -117.2307 | 5.8255 | 5.4768 | 5.9843 | -117.0546 | 0.06515 | -0.008798 | -0.005985 | 0.13945 | 0.25637 | -0.17081 | -0.22825 | 0.23821 | -0.061366 | 0.51289 | 0.062082 | -0.17612 | -0.41009 | 0.097422 | 117.0645 | -5.7474 | 117.3579 | 117.2868 | 0.22227 | -5.6305 | -6.0577 | 123.1183 | 122.7695 | 123.277 | 117.1843 | -122.9414 | 117.4322 | 117.5492 | 117.122 | 117.284 | -6.1151
273.7188 | 123.2071 | -116.4322 | 6.7657 | 1.4211e-13 | -0.013423 | 0.00014309 | -0.0026882 | -0.0094225 | -0.0029357 | -0.0019839 | 0.0083426 | 0.0083539 | -0.0047473 | 0.03022 | 0.0073689 | -116.0061 | -0.10848 | -116.4661 | 6.6038 | 6.2597 | 6.7626 | -116.2624 | 0.055992 | -0.00422 | -0.005985 | 0.14403 | 0.25637 | -0.16624 | -0.23283 | 0.16977 | -0.16195 | 0.42605 | -0.033941 | -0.20371 | -0.506 | -0.003122 | 116.1994 | -6.6217 | 116.4882 | 116.4262 | 0.22685 | -6.5094 | -6.932 | 123.036 | 122.6919 | 123.1948 | 116.3237 | -123.0282 | 116.5762 | 116.6886 | 116.266 | 116.428 | -6.9986
275.4062 | 123.2895 | -116.6382 | 6.5369 | 1.4211e-13 | -0.013209 | -7.051e-05 | -0.0026882 | -0.0092089 | -0.0025083 | -0.0019839 | 0.0085562 | 0.0085677 | -0.0049609 | 0.030006 | 0.0071553 | -116.1664 | -0.1039 | -116.6264 | 6.4344 | 6.0583 | 6.5932 | -116.4273 | 0.055992 | 0.000359 | -0.005985 | 0.13029 | 0.25637 | -0.17081 | -0.22825 | 0.21092 | -0.10246 | 0.4718 | 0.011813 | -0.1991 | -0.47859 | 0.056352 | 116.4099 | -6.4066 | 116.6942 | 116.6322 | 0.22227 | -6.2805 | -6.7077 | 123.0726 | 122.6965 | 123.2314 | 116.5343 | -122.9641 | 116.7685 | 116.8946 | 116.4674 | 116.6385 | -6.7651
277.0781 | 123.3353 | -116.2857 | 6.8527 | 1.4211e-13 | -0.013423 | 0.00035689 | -0.0024744 | -0.0094225 | -0.0029357 | 0.0056466 | 0.0083426 | 0.0085677 | -0.0045337 | 0.030433 | 0.0071553 | -115.8367 | -0.10848 | -116.2738 | 6.7824 | 6.4154 | 6.9366 | -116.0793 | 0.060571 | -0.00422 | -0.001407 | 0.14403 | 0.25179 | -0.17539 | -0.22367 | 0.20644 | -0.070364 | 0.44896 | 0.011862 | -0.19458 | -0.43729 | 0.08389 | 116.062 | -6.7087 | 116.3463 | 116.2843 | 0.22227 | -6.6009 | -7.0281 | 123.0681 | 122.7011 | 123.2223 | 116.1772 | -122.932 | 116.4297 | 116.5375 | 116.1103 | 116.2815 | -7.0764
278.7656 | 123.0057 | -94.5969 | 28.5278 | 1.4211e-13 | -0.013209 | 0.00035689 | -0.0024744 | -0.0096363 | -0.0027221 | -0.0019839 | 0.0089834 | 0.0083539 | -0.0043199 | 0.03022 | 0.0069417 | -99.5972 | 0.26239 | -100.1125 | 22.9166 | 22.7347 | 22.948 | -99.7371 | 0.042256 | 0.018674 | -0.015143 | 0.13487 | 0.24264 | -0.16624 | -0.24657 | -5.1402 | -5.6112 | -5.0003 | -5.5157 | -0.37543 | -5.7931 | -5.5798 | 94.3503 | -28.393 | 94.6391 | 94.5817 | 0.23142 | -28.2852 | -28.6941 | 117.5135 | 117.3316 | 117.5448 | 94.8593 | -128.2649 | 94.7317 | 94.8395 | 94.4306 | 94.6155 | -28.7744
280.4375 | 123.2941 | -94.6198 | 28.537 | 1.4211e-13 | -0.013423 | 0.00014309 | -0.0024744 | -0.0089953 | -0.0027221 | 0.0056466 | 0.0085562 | 0.0083539 | -0.0047473 | 0.03022 | 0.0069417 | -94.2863 | -0.044379 | -94.5728 | 28.4931 | 28.1287 | 28.5751 | -94.3248 | 0.042256 | 0.018674 | -0.019721 | 0.12571 | 0.24264 | -0.17539 | -0.24199 | 0.29495 | -0.043914 | 0.33348 | 0.046957 | -0.248 | -0.40829 | 0.038101 | 94.3778 | -28.4113 | 94.662 | 94.6 | 0.22227 | -28.2944 | -28.7124 | 123.1128 | 122.7484 | 123.1948 | 94.5754 | -122.8618 | 94.7455 | 94.8624 | 94.4444 | 94.6384 | -28.779
282.1406 | 123.2803 | -94.5694 | 28.5233 | 1.4211e-13 | -0.013209 | 0.00014309 | -0.0024744 | -0.0096363 | -0.0029357 | 0.013277 | 0.0083426 | 0.0081403 | -0.0043199 | 0.03022 | 0.0073689 | -94.2909 | -0.044379 | -94.5728 | 28.4793 | 28.0875 | 28.5797 | -94.3385 | 0.051413 | 0.018674 | -0.0243 | 0.12571 | 0.2289 | -0.16624 | -0.24657 | 0.23086 | -0.043916 | 0.27855 | -0.003397 | -0.23426 | -0.43577 | 0.056412 | 94.3228 | -28.3975 | 94.6208 | 94.5451 | 0.22227 | -28.2944 | -28.6895 | 123.0487 | 122.6569 | 123.1491 | 94.525 | -122.8618 | 94.6951 | 94.7983 | 94.4032 | 94.5881 | -28.7698
283.8125 | 123.1934 | -95.6131 | 27.5894 | 1.4211e-13 | -0.013209 | 0.00014309 | -0.0029018 | -0.0096363 | -0.0033631 | -0.0019839 | 0.0083426 | 0.0085677 | -0.0045337 | 0.030647 | 0.0071553 | -94.6434 | -0.039801 | -94.9436 | 28.1268 | 27.7257 | 28.1813 | -94.8193 | 0.042256 | 0.023253 | -0.019721 | 0.12571 | 0.24264 | -0.17539 | -0.24199 | 0.79378 | 0.53739 | 0.96971 | 0.66946 | -0.12431 | 0.13633 | 0.59191 | 95.3711 | -27.4637 | 95.6554 | 95.5934 | 0.22227 | -27.3468 | -27.7648 | 123.7399 | 123.3388 | 123.7944 | 95.5733 | -122.4087 | 95.7388 | 95.8557 | 95.4377 | 95.6364 | -27.8314
285.4844 | 123.2986 | -115.9012 | 7.1869 | 1.4211e-13 | -0.013209 | -7.051e-05 | -0.0026882 | -0.0092089 | -0.0025083 | -0.0019839 | 0.0087698 | 0.0083539 | -0.0047473 | 0.03022 | 0.0069417 | -115.4018 | -0.13137 | -115.8618 | 7.2173 | 6.9145 | 7.4403 | -116.1113 | 0.051413 | 0.004938 | -0.001407 | 0.13945 | 0.25179 | -0.16624 | -0.22367 | -0.21014 | 0.030415 | 0.49939 | 0.039386 | 0.24952 | -0.27236 | 0.25337 | 115.6775 | -7.0474 | 115.9526 | 115.8998 | 0.22227 | -6.9351 | -7.3531 | 123.1185 | 122.8157 | 123.3414 | 115.7698 | -123.2982 | 116.0406 | 116.153 | 115.7349 | 115.9061 | -7.4106
287.1719 | 123.2712 | -94.5969 | 28.5049 | 1.4211e-13 | -0.013423 | 0.00035689 | -0.0024744 | -0.0092089 | -0.0027221 | -0.0019839 | 0.008129 | 0.0085677 | -0.0049609 | 0.03022 | 0.0069417 | -94.2909 | -0.048958 | -94.5774 | 28.4885 | 28.0737 | 28.5201 | -94.3294 | 0.046835 | 0.023253 | -0.019721 | 0.12571 | 0.23348 | -0.17081 | -0.23741 | 0.26749 | -0.016449 | 0.30601 | 0.019491 | -0.248 | -0.4312 | 0.0152 | 94.3595 | -28.3792 | 94.6437 | 94.5771 | 0.21769 | -28.2715 | -28.6758 | 123.0854 | 122.6706 | 123.117 | 94.5479 | -122.8343 | 94.7226 | 94.8303 | 94.426 | 94.6201 | -28.7424
288.875 | 123.317 | -94.5648 | 28.5141 | 1.4211e-13 | -0.013637 | 0.00014309 | -0.0024744 | -0.0098499 | -0.0029357 | -0.0019839 | 0.0083426 | 0.0083539 | -0.0047473 | 0.03022 | 0.0067279 | -94.2634 | -0.058115 | -94.5499 | 28.516 | 28.0921 | 28.5293 | -94.2882 | 0.046835 | 0.014095 | -0.010564 | 0.11656 | 0.23806 | -0.17081 | -0.23741 | 0.27665 | 0.001866 | 0.30144 | 0.014916 | -0.26174 | -0.42204 | 0.015203 | 94.3274 | -28.3975 | 94.6117 | 94.5543 | 0.22685 | -28.276 | -28.6849 | 123.0808 | 122.6569 | 123.0941 | 94.5067 | -122.8023 | 94.6814 | 94.8029 | 94.394 | 94.5789 | -28.7515
290.5469 | 123.2849 | -94.5602 | 28.5324 | 1.4211e-13 | -0.013423 | 0.00035689 | -0.002047 | -0.0094225 | -0.0031493 | 0.0056466 | 0.008129 | 0.0085677 | -0.0051745 | 0.030647 | 0.0071553 | -94.2634 | -0.058115 | -94.5453 | 28.516 | 28.0921 | 28.5934 | -94.3111 | 0.042256 | 0.023253 | -0.019721 | 0.12571 | 0.24264 | -0.17081 | -0.24657 | 0.24918 | -0.016445 | 0.29686 | 0.014918 | -0.23426 | -0.44035 | 0.060992 | 94.3137 | -28.4067 | 94.6025 | 94.5405 | 0.22685 | -28.2898 | -28.7032 | 123.0762 | 122.6523 | 123.1536 | 94.5021 | -122.8435 | 94.686 | 94.8029 | 94.3894 | 94.5835 | -28.779
292.2188 | 123.317 | -94.6014 | 28.5278 | 1.4211e-13 | -0.013423 | 0.00035689 | -0.0024744 | -0.0094225 | -0.0029357 | -0.0019839 | 0.0083426 | 0.0087813 | -0.0051745 | 0.030647 | 0.0071553 | -94.2634 | -0.058115 | -94.5499 | 28.5068 | 28.0921 | 28.5476 | -94.2973 | 0.037677 | 0.023253 | -0.0243 | 0.12114 | 0.23806 | -0.17081 | -0.24657 | 0.30412 | -0.021024 | 0.33806 | 0.051537 | -0.25258 | -0.43577 | 0.019784 | 94.3549 | -28.4067 | 94.6391 | 94.5771 | 0.22227 | -28.2898 | -28.6986 | 123.1082 | 122.6935 | 123.1491 | 94.5433 | -122.8252 | 94.7226 | 94.8395 | 94.4306 | 94.6247 | -28.7744
293.9219 | 123.2803 | -94.5602 | 28.537 | 1.4211e-13 | -0.013423 | 0.00014309 | -0.0022608 | -0.0096363 | -0.0027221 | -0.0019839 | 0.008129 | 0.0085677 | -0.0047473 | 0.030647 | 0.0065143 | -94.268 | -0.067272 | -94.5453 | 28.5068 | 28.0966 | 28.5888 | -94.3111 | 0.042256 | 0.018674 | -0.015143 | 0.12114 | 0.23806 | -0.16624 | -0.24199 | 0.24918 | -0.030179 | 0.29228 | 0.014918 | -0.23426 | -0.44035 | 0.051836 | 94.3183 | -28.4159 | 94.6025 | 94.5451 | 0.22685 | -28.2989 | -28.7032 | 123.067 | 122.6569 | 123.1491 | 94.493 | -122.848 | 94.6814 | 94.7983 | 94.394 | 94.5789 | -28.779
295.625 | 123.2346 | -94.6243 | 28.537 | 1.4211e-13 | -0.013637 | -7.051e-05 | -0.0024744 | -0.0096363 | -0.0029357 | 0.013277 | 0.0087698 | 0.0083539 | -0.0045337 | 0.03022 | 0.0071553 | -94.268 | -0.058115 | -94.5545 | 28.5114 | 28.0783 | 28.5476 | -94.3065 | 0.037677 | 0.023253 | -0.019721 | 0.12571 | 0.23348 | -0.16166 | -0.24199 | 0.31785 | -0.0256 | 0.35637 | 0.069848 | -0.248 | -0.45866 | 0.010629 | 94.3823 | -28.4113 | 94.662 | 94.6046 | 0.22227 | -28.3035 | -28.6986 | 123.1357 | 122.7027 | 123.1719 | 94.5662 | -122.8435 | 94.75 | 94.8578 | 94.4627 | 94.6476 | -28.779
297.3438 | 123.2986 | -94.5648 | 28.5416 | 1.4211e-13 | -0.013637 | -7.051e-05 | -0.0022608 | -0.0096363 | -0.0029357 | 0.013277 | 0.0083426 | 0.0085677 | -0.0045337 | 0.030647 | 0.0067279 | -94.2771 | -0.062694 | -94.5591 | 28.5068 | 28.0783 | 28.5476 | -94.3111 | 0.042256 | 0.027831 | -0.015143 | 0.12114 | 0.23806 | -0.17539 | -0.24199 | 0.25376 | -0.034757 | 0.2877 | 0.00576 | -0.248 | -0.46324 | 0.006051 | 94.3228 | -28.4204 | 94.6071 | 94.5497 | 0.22685 | -28.3035 | -28.717 | 123.0716 | 122.6431 | 123.1124 | 94.5021 | -122.8526 | 94.686 | 94.8029 | 94.3894 | 94.5927 | -28.7836
299.0469 | 123.1934 | -94.6289 | 28.5461 | 1.4211e-13 | -0.013637 | 0.00035689 | -0.0026882 | -0.0094225 | -0.0027221 | -0.0096144 | 0.0085562 | 0.0087813 | -0.0047473 | 0.030433 | 0.0067279 | -94.2725 | -0.062694 | -94.5591 | 28.5068 | 28.0921 | 28.5705 | -94.3019 | 0.042256 | 0.027831 | -0.0243 | 0.12571 | 0.23348 | -0.17081 | -0.23741 | 0.327 | -0.039335 | 0.35637 | 0.069847 | -0.25716 | -0.45408 | 0.024366 | 94.3915 | -28.4204 | 94.6712 | 94.6046 | 0.21311 | -28.3127 | -28.717 | 123.1357 | 122.721 | 123.1994 | 94.5662 | -122.848 | 94.7546 | 94.8624 | 94.4581 | 94.6567 | -28.7836
300.7344 | 123.3124 | -94.574 | 28.4866 | 1.4211e-13 | -0.013637 | 0.00014309 | -0.0022608 | -0.0094225 | -0.0029357 | 0.0056466 | 0.0083426 | 0.0085677 | -0.0047473 | 0.030433 | 0.0067279 | -94.2771 | -0.062694 | -94.5545 | 28.5068 | 28.0875 | 28.5888 | -94.2882 | 0.033099 | 0.027831 | -0.019721 | 0.12571 | 0.2289 | -0.16166 | -0.24199 | 0.28581 | 0.020175 | 0.29686 | 0.019494 | -0.26631 | -0.39915 | 0.10219 | 94.332 | -28.3609 | 94.6071 | 94.5543 | 0.22227 | -28.2577 | -28.6483 | 123.0808 | 122.6615 | 123.1628 | 94.5113 | -122.7748 | 94.6997 | 94.8029 | 94.4123 | 94.6018 | -28.7286
302.4062 | 123.2986 | -94.5877 | 28.5187 | 1.4211e-13 | -0.013209 | -7.051e-05 | 0.064408 | -0.0096363 | 0.061377 | -0.0019839 | 0.0087698 | 0.0085677 | -0.0047473 | 0.030433 | 0.0067279 | -94.2588 | -0.062694 | -94.5453 | 28.4885 | 28.0875 | 28.5522 | -94.3019 | 0.042256 | 0.041567 | -0.0243 | 0.12114 | 0.24264 | -0.16624 | -0.24199 | 0.28581 | -0.030182 | 0.32891 | 0.042384 | -0.24342 | -0.43119 | 0.033518 | 94.3457 | -28.3975 | 94.63 | 94.5634 | 0.21769 | -28.276 | -28.6849 | 123.0762 | 122.6752 | 123.1399 | 94.525 | -122.8206 | 94.7088 | 94.8303 | 94.4215 | 94.6293 | -28.7607
304.1094 | 123.1979 | -94.6106 | 28.5324 | 1.4211e-13 | -0.013637 | 0.00014309 | 0.064195 | -0.0096363 | 0.060736 | 0.0056466 | 0.0085562 | 0.0081403 | -0.0045337 | 0.030433 | 0.0069417 | -94.2542 | -0.062694 | -94.5453 | 28.4885 | 28.0692 | 28.5797 | -94.3111 | 0.042256 | 0.041567 | -0.019721 | 0.11656 | 0.23348 | -0.17539 | -0.24657 | 0.29954 | -0.043915 | 0.35637 | 0.065272 | -0.23426 | -0.46324 | 0.047256 | 94.364 | -28.4159 | 94.6529 | 94.5909 | 0.22685 | -28.2989 | -28.7078 | 123.0991 | 122.6798 | 123.1903 | 94.5479 | -122.8435 | 94.7272 | 94.8441 | 94.4352 | 94.6522 | -28.779
305.7969 | 123.3444 | -94.5602 | 28.5095 | 1.4211e-13 | -0.013423 | 0.00014309 | 0.064836 | -0.0096363 | 0.060949 | 0.0056466 | 0.0085562 | 0.0085677 | -0.0051745 | 0.030861 | 0.0069417 | -94.2588 | -0.067272 | -94.5499 | 28.4885 | 28.0646 | 28.5156 | -94.3156 | 0.037677 | 0.046146 | -0.0243 | 0.11656 | 0.2289 | -0.17081 | -0.23283 | 0.2446 | -0.021026 | 0.30144 | 0.010339 | -0.23426 | -0.44493 | 0.006045 | 94.3274 | -28.393 | 94.5979 | 94.5359 | 0.20853 | -28.2806 | -28.6803 | 123.0487 | 122.6248 | 123.0758 | 94.493 | -122.8252 | 94.6768 | 94.7891 | 94.3894 | 94.6064 | -28.7424
307.5156 | 123.2208 | -94.6198 | 28.5233 | 1.4211e-13 | -0.013423 | -7.051e-05 | 0.064195 | -0.0096363 | 0.060949 | -0.0019839 | 0.0085562 | 0.0083539 | -0.0047473 | 0.030433 | 0.0069417 | -94.2588 | -0.067272 | -94.5545 | 28.4839 | 28.0554 | 28.5568 | -94.3019 | 0.037677 | 0.050725 | -0.019721 | 0.12114 | 0.23348 | -0.17539 | -0.24657 | 0.31785 | -0.039338 | 0.36095 | 0.06527 | -0.25258 | -0.46782 | 0.033519 | 94.3732 | -28.4021 | 94.6574 | 94.6 | 0.22685 | -28.2898 | -28.6986 | 123.1037 | 122.6752 | 123.1765 | 94.5525 | -122.8252 | 94.7409 | 94.8532 | 94.4444 | 94.6705 | -28.7698
309.1875 | 123.262 | -94.5786 | 28.5233 | 1.4211e-13 | -0.013637 | 0.00014309 | 0.064195 | -0.0092089 | 0.060949 | -0.0096144 | 0.0085562 | 0.0083539 | -0.0043199 | 0.03022 | 0.0080099 | -94.2588 | -0.067272 | -94.5499 | 28.4793 | 28.0646 | 28.5797 | -94.3019 | 0.037677 | 0.055303 | -0.019721 | 0.12114 | 0.23348 | -0.17539 | -0.23741 | 0.27665 | -0.043916 | 0.31975 | 0.028649 | -0.248 | -0.45867 | 0.056412 | 94.3411 | -28.4021 | 94.6162 | 94.5588 | 0.21769 | -28.2898 | -28.6986 | 123.0579 | 122.6431 | 123.1582 | 94.5113 | -122.8252 | 94.6997 | 94.812 | 94.4032 | 94.6339 | -28.7607
310.875 | 123.2758 | -94.574 | 28.5233 | 1.4211e-13 | -0.013637 | -7.051e-05 | 0.064195 | -0.0094225 | 0.060736 | 0.0056466 | 0.0085562 | 0.0083539 | -0.0047473 | 0.030647 | 0.0080099 | -94.2588 | -0.058115 | -94.5499 | 28.4793 | 28.0646 | 28.5568 | -94.3156 | 0.042256 | 0.046146 | -0.015143 | 0.11656 | 0.23348 | -0.17081 | -0.23741 | 0.25834 | -0.043916 | 0.31517 | 0.024072 | -0.23426 | -0.45867 | 0.033519 | 94.3366 | -28.4067 | 94.6162 | 94.5588 | 0.22227 | -28.2898 | -28.6941 | 123.0533 | 122.6386 | 123.1307 | 94.5159 | -122.8389 | 94.6905 | 94.8075 | 94.4032 | 94.6201 | -28.7607
312.5781 | 123.2391 | -94.606 | 28.5187 | 1.4211e-13 | -0.013637 | -7.051e-05 | 0.064195 | -0.0092089 | 0.060736 | 0.0056466 | 0.0083426 | 0.0083539 | -0.0045337 | 0.030647 | 0.0077963 | -94.2634 | -0.062694 | -94.5499 | 28.4748 | 28.0554 | 28.5797 | -94.3111 | 0.037677 | 0.050725 | -0.0243 | 0.12114 | 0.23348 | -0.16624 | -0.24199 | 0.29496 | -0.043917 | 0.34264 | 0.056115 | -0.23884 | -0.46325 | 0.060989 | 94.364 | -28.3975 | 94.6437 | 94.5817 | 0.21769 | -28.2852 | -28.6849 | 123.0808 | 122.6614 | 123.1857 | 94.5433 | -122.8297 | 94.7272 | 94.8395 | 94.4398 | 94.6567 | -28.7607
314.25 | 123.2849 | -94.5877 | 28.4775 | 1.4211e-13 | -0.013637 | -0.00028411 | 0.063981 | -0.0096363 | 0.060736 | 0.0056466 | 0.0085562 | 0.0083539 | -0.0047473 | 0.030647 | 0.0080099 | -94.2176 | -0.062694 | -94.5591 | 28.4748 | 28.06 | 28.5385 | -94.3202 | 0.042256 | 0.06904 | -0.019721 | 0.11656 | 0.23348 | -0.17081 | -0.23741 | 0.26749 | -0.002718 | 0.37011 | 0.028649 | -0.23884 | -0.41747 | 0.060981 | 94.3503 | -28.3609 | 94.63 | 94.568 | 0.21769 | -28.244 | -28.6483 | 123.0625 | 122.6477 | 123.1262 | 94.525 | -122.7977 | 94.7043 | 94.8212 | 94.4169 | 94.6567 | -28.7149
315.9844 | 123.2346 | -94.6152 | 28.4637 | 1.4211e-13 | -0.01385 | -7.051e-05 | 0.064195 | -0.0094225 | 0.060949 | 0.0056466 | 0.0085562 | 0.0085677 | -0.0047473 | 0.030433 | 0.0075825 | -94.2176 | -0.071851 | -94.5682 | 28.4702 | 28.1058 | 28.5476 | -94.3019 | 0.033099 | 0.055303 | -0.028879 | 0.12114 | 0.2289 | -0.17081 | -0.23741 | 0.31327 | 0.006436 | 0.39758 | 0.046957 | -0.26631 | -0.35795 | 0.083871 | 94.3778 | -28.3426 | 94.6483 | 94.5863 | 0.20853 | -28.2348 | -28.6346 | 123.0854 | 122.721 | 123.1628 | 94.5433 | -122.7656 | 94.7363 | 94.8441 | 94.4444 | 94.6705 | -28.7012
317.6562 | 123.3353 | -94.6106 | 28.4729 | 1.4211e-13 | -0.013423 | -0.00028411 | 0.063981 | -0.010063 | 0.060736 | -0.0096144 | 0.0083426 | 0.0083539 | -0.0047473 | 0.030433 | 0.0080099 | -94.2222 | -0.067272 | -94.5682 | 28.461 | 28.0463 | 28.543 | -94.3294 | 0.02852 | 0.06904 | -0.0243 | 0.12571 | 0.23348 | -0.17997 | -0.23741 | 0.28122 | -0.011876 | 0.38842 | 0.04238 | -0.23884 | -0.42663 | 0.070137 | 94.3732 | -28.3472 | 94.6391 | 94.5863 | 0.21311 | -28.2394 | -28.6529 | 123.0716 | 122.6569 | 123.1536 | 94.5433 | -122.8023 | 94.7363 | 94.8441 | 94.4306 | 94.6796 | -28.7103
319.375 | 123.1888 | -94.6518 | 28.5416 | 1.4211e-13 | -0.013209 | -7.051e-05 | 0.064408 | -0.0098499 | 0.060736 | 0.020908 | 0.008129 | 0.0083539 | -0.0047473 | 0.030647 | 0.0075825 | -94.2268 | -0.058115 | -94.5728 | 28.461 | 28.0463 | 28.5614 | -94.334 | 0.042256 | 0.059882 | -0.0243 | 0.11656 | 0.23348 | -0.17539 | -0.23741 | 0.31784 | -0.080541 | 0.42504 | 0.079 | -0.23884 | -0.49529 | 0.019787 | 94.4144 | -28.425 | 94.694 | 94.6275 | 0.21311 | -28.3081 | -28.717 | 123.1128 | 122.6981 | 123.2131 | 94.5937 | -122.8755 | 94.7684 | 94.8853 | 94.4764 | 94.7117 | -28.779
321.0625 | 123.2986 | -94.5877 | 28.4729 | 1.4211e-13 | -0.014064 | 0.00014309 | 0.064408 | -0.0096363 | 0.060522 | -0.0096144 | 0.0083426 | 0.0085677 | -0.0051745 | 0.030647 | 0.0075825 | -94.2268 | -0.062694 | -94.5636 | 28.4519 | 28.0417 | 28.511 | -94.3294 | 0.037677 | 0.078197 | -0.019721 | 0.11656 | 0.2289 | -0.16624 | -0.24199 | 0.25833 | -0.021032 | 0.36096 | 0.024071 | -0.23426 | -0.43121 | 0.038087 | 94.3457 | -28.3563 | 94.6254 | 94.568 | 0.22227 | -28.244 | -28.6391 | 123.0396 | 122.6294 | 123.0987 | 94.525 | -122.8023 | 94.7043 | 94.8166 | 94.4215 | 94.6659 | -28.7149
322.7188 | 123.1613 | -94.6472 | 28.5049 | 1.4211e-13 | -0.01385 | -7.051e-05 | 0.064408 | -0.010063 | 0.060308 | -0.0019839 | 0.0085562 | 0.0079267 | -0.0047473 | 0.030647 | 0.0075825 | -94.2268 | -0.062694 | -94.5728 | 28.4473 | 28.028 | 28.5568 | -94.334 | 0.037677 | 0.06904 | -0.019721 | 0.12571 | 0.23348 | -0.17081 | -0.23741 | 0.31326 | -0.057655 | 0.42046 | 0.074423 | -0.23884 | -0.47699 | 0.051829 | 94.4098 | -28.3792 | 94.6849 | 94.6275 | 0.21769 | -28.2715 | -28.6758 | 123.0945 | 122.6752 | 123.204 | 94.5845 | -122.8389 | 94.7729 | 94.8807 | 94.4764 | 94.7163 | -28.7424
324.4688 | 123.3032 | -94.5923 | 28.4683 | 1.4211e-13 | -0.013637 | -0.00028411 | 0.064195 | -0.010063 | 0.060736 | -0.0019839 | 0.0087698 | 0.0087813 | -0.0049609 | 0.030433 | 0.0077963 | -94.2405 | -0.067272 | -94.5865 | 28.4381 | 28.0325 | 28.5522 | -94.3477 | 0.037677 | 0.000359 | -0.005985 | 0.12571 | 0.2289 | -0.17997 | -0.24199 | 0.24459 | -0.030191 | 0.3518 | 0.005756 | -0.23884 | -0.43579 | 0.083872 | 94.3503 | -28.3426 | 94.63 | 94.5863 | 0.236 | -28.2394 | -28.6483 | 123.0304 | 122.6248 | 123.1445 | 94.525 | -122.816 | 94.718 | 94.8212 | 94.4123 | 94.5926 | -28.7103
326.1562 | 123.1659 | -94.6564 | 28.4592 | 1.4211e-13 | -0.01385 | -0.00028411 | 0.064195 | -0.0098499 | 0.060522 | 0.0056466 | 0.0085562 | 0.0083539 | -0.0047473 | 0.030861 | 0.0077963 | -94.2496 | -0.067272 | -94.5911 | 28.4336 | 28.0142 | 28.5339 | -94.3523 | 0.046835 | 0.004938 | -0.0243 | 0.11656 | 0.23348 | -0.17539 | -0.24199 | 0.3041 | -0.025613 | 0.40673 | 0.065265 | -0.23884 | -0.44495 | 0.074713 | 94.4144 | -28.3426 | 94.7032 | 94.6321 | 0.21769 | -28.2257 | -28.6346 | 123.0899 | 122.6706 | 123.1903 | 94.5891 | -122.8114 | 94.7729 | 94.8899 | 94.481 | 94.6613 | -28.7012
327.8281 | 123.2986 | -94.6335 | 28.4363 | 1.4211e-13 | -0.01385 | 0.00014309 | 0.063981 | -0.0096363 | 0.060522 | 0.013277 | 0.0085562 | 0.0085677 | -0.0047473 | 0.030647 | 0.0075825 | -94.2496 | -0.067272 | -94.5957 | 28.429 | 28.0234 | 28.4973 | -94.3477 | 0.042256 | 0.004938 | -0.019721 | 0.12114 | 0.23348 | -0.17081 | -0.23741 | 0.28579 | -0.007303 | 0.38384 | 0.037799 | -0.24799 | -0.4129 | 0.060972 | 94.3961 | -28.3151 | 94.6757 | 94.6138 | 0.21769 | -28.2028 | -28.6071 | 123.0625 | 122.6569 | 123.1307 | 94.5662 | -122.784 | 94.7546 | 94.867 | 94.4627 | 94.6384 | -28.6737
329.5469 | 123.1979 | -94.6472 | 28.4775 | 1.4211e-13 | -0.01385 | -0.00028411 | 0.064195 | -0.010063 | 0.060949 | 0.013277 | 0.008129 | 0.0085677 | -0.0047473 | 0.030861 | 0.0075825 | -94.2496 | -0.058115 | -94.6003 | 28.429 | 28.0051 | 28.5293 | -94.3523 | 0.042256 | 0.004938 | -0.010564 | 0.11656 | 0.23806 | -0.17997 | -0.23741 | 0.29495 | -0.048502 | 0.39757 | 0.046953 | -0.24799 | -0.47242 | 0.051824 | 94.4098 | -28.3609 | 94.6895 | 94.6367 | 0.22685 | -28.2394 | -28.6575 | 123.0762 | 122.6523 | 123.1765 | 94.5891 | -122.8297 | 94.7638 | 94.8853 | 94.4672 | 94.6522 | -28.7149
331.2188 | 123.1934 | -94.6564 | 28.4592 | 1.4211e-13 | -0.013637 | -7.051e-05 | 0.063981 | -0.010277 | 0.060736 | 0.0056466 | 0.0083426 | 0.0085677 | -0.0047473 | 0.030861 | 0.0077963 | -94.2542 | -0.067272 | -94.6048 | 28.4244 | 28.0096 | 28.5293 | -94.3706 | 0.046835 | 0.004938 | -0.010564 | 0.12571 | 0.23348 | -0.17081 | -0.23741 | 0.28579 | -0.03477 | 0.40215 | 0.05153 | -0.23426 | -0.44953 | 0.070135 | 94.419 | -28.3335 | 94.7032 | 94.6458 | 0.22685 | -28.2257 | -28.63 | 123.0808 | 122.666 | 123.1857 | 94.5891 | -122.8298 | 94.7821 | 94.8899 | 94.4856 | 94.6613 | -28.6966
332.8906 | 123.3582 | -94.6152 | 28.4363 | 1.4211e-13 | -0.014064 | -7.051e-05 | 0.063981 | -0.0094225 | 0.060522 | 0.0056466 | 0.0083426 | 0.0083539 | -0.0047473 | 0.030861 | 0.0075825 | -94.2542 | -0.062694 | -94.6003 | 28.4198 | 28.0051 | 28.456 | -94.3477 | 0.051413 | 0.004938 | -0.019721 | 0.12571 | 0.23806 | -0.17081 | -0.23741 | 0.26748 | -0.01646 | 0.36095 | 0.014909 | -0.25257 | -0.43122 | 0.019765 | 94.3778 | -28.3106 | 94.6666 | 94.5955 | 0.21769 | -28.1982 | -28.6071 | 123.035 | 122.6202 | 123.0712 | 94.5525 | -122.784 | 94.7409 | 94.8532 | 94.4444 | 94.6201 | -28.6737
334.5781 | 123.2025 | -94.6655 | 28.45 | 1.4211e-13 | -0.01385 | -0.00028411 | 0.063981 | -0.0096363 | 0.060736 | 0.0056466 | 0.0083426 | 0.0085677 | -0.0049609 | 0.031074 | 0.0077963 | -94.2588 | -0.062694 | -94.6003 | 28.4152 | 28.0142 | 28.5247 | -94.3614 | 0.051413 | 0.004938 | -0.0243 | 0.12114 | 0.23348 | -0.16624 | -0.23741 | 0.3041 | -0.034772 | 0.40672 | 0.065263 | -0.23883 | -0.43579 | 0.074711 | 94.4281 | -28.3289 | 94.7169 | 94.6412 | 0.21311 | -28.2165 | -28.6162 | 123.0808 | 122.6797 | 123.1902 | 94.6028 | -122.8114 | 94.7867 | 94.899 | 94.4993 | 94.6705 | -28.6874
336.2656 | 123.2346 | -122.8775 | 0.3067 | 1.4211e-13 | -0.01385 | -0.00028411 | 0.063767 | -0.0096363 | 0.060736 | 0.0056466 | 0.0087698 | 0.0083539 | -0.0049609 | 0.030861 | 0.0077963 | -122.2831 | -0.16342 | -122.7842 | 0.27647 | -0.072904 | 0.52657 | -122.5951 | 0.055992 | 0.014095 | -0.001407 | 0.13945 | 0.26095 | -0.17539 | -0.2191 | 0.28242 | -0.030233 | 0.59439 | 0.093343 | -0.18908 | -0.37961 | 0.21987 | 122.6584 | -0.16725 | 122.9335 | 122.8761 | 0.21769 | -0.045751 | -0.48209 | 123.154 | 122.8046 | 123.4041 | 122.7141 | -122.9018 | 123.017 | 123.1385 | 122.7021 | 122.8916 | -0.5258
338.125 | 123.317 | -122.8683 | 0.26093 | 1.4211e-13 | -0.014064 | -0.00028411 | 0.06334 | -0.0098499 | 0.060522 | -0.0096144 | 0.0089834 | 0.0085677 | -0.0051745 | 0.031288 | 0.0073689 | -122.2877 | -0.15427 | -122.7933 | 0.26731 | -0.077483 | 0.39379 | -122.6088 | 0.055992 | 0.018674 | -0.001407 | 0.14403 | 0.25637 | -0.17081 | -0.21452 | 0.25953 | 0.006387 | 0.58065 | 0.075032 | -0.1845 | -0.33841 | 0.13286 | 122.6538 | -0.1169 | 122.9243 | 122.8669 | 0.21311 | -0.004553 | -0.43174 | 123.1357 | 122.7909 | 123.2621 | 122.7141 | -122.8697 | 123.0124 | 123.1247 | 122.6975 | 122.887 | -0.47544
339.8906 | 123.2803 | -122.8912 | 0.27466 | 1.4211e-13 | -0.014064 | -7.051e-05 | 0.063767 | -0.0098499 | 0.060736 | 0.0056466 | 0.0085562 | 0.0085677 | -0.0047473 | 0.030861 | 0.0077963 | -122.2923 | -0.14511 | -122.7979 | 0.25358 | -0.082062 | 0.31595 | -122.6088 | 0.060571 | 0.014095 | 0.003172 | 0.13945 | 0.25179 | -0.17539 | -0.22367 | 0.28242 | -0.021081 | 0.59896 | 0.093342 | -0.18908 | -0.35672 | 0.041295 | 122.6676 | -0.13521 | 122.9518 | 122.8944 | 0.22685 | -0.022864 | -0.45005 | 123.1448 | 122.8092 | 123.2072 | 122.7461 | -122.8835 | 123.0307 | 123.143 | 122.7158 | 122.9053 | -0.49833
341.5781 | 123.3078 | -122.8867 | 0.27466 | 1.4211e-13 | -0.01385 | -0.00049791 | 0.063554 | -0.0096363 | 0.060949 | -0.0019839 | 0.0085562 | 0.0085677 | -0.0049609 | 0.030647 | 0.0077963 | -122.2877 | -0.14511 | -122.7796 | 0.26731 | -0.082062 | 0.3709 | -122.6088 | 0.060571 | 0.018674 | -0.001407 | 0.14861 | 0.25637 | -0.17539 | -0.2191 | 0.27784 | -0.007346 | 0.59897 | 0.10708 | -0.17076 | -0.35672 | 0.096238 | 122.6676 | -0.12605 | 122.9472 | 122.8853 | 0.21769 | -0.018286 | -0.45005 | 123.154 | 122.8046 | 123.2576 | 122.7415 | -122.8835 | 123.0353 | 123.143 | 122.7113 | 122.9053 | -0.49375
343.3281 | 123.2071 | -122.9004 | 0.32501 | 1.4211e-13 | -0.013637 | 0.00014309 | 0.063767 | -0.0096363 | 0.060308 | -0.0019839 | 0.0085562 | 0.0083539 | -0.0045337 | 0.030647 | 0.0075825 | -122.274 | -0.14053 | -122.7704 | 0.28563 | -0.077483 | 0.35258 | -122.5905 | 0.055992 | 0.014095 | 0.003172 | 0.13487 | 0.25637 | -0.17539 | -0.2191 | 0.30989 | -0.039387 | 0.62643 | 0.12997 | -0.17993 | -0.4025 | 0.02757 | 122.6813 | -0.19014 | 122.9564 | 122.9036 | 0.22227 | -0.06864 | -0.5004 | 123.186 | 122.8229 | 123.253 | 122.7599 | -122.9155 | 123.0353 | 123.1568 | 122.725 | 122.9145 | -0.54411
345.0781 | 123.3078 | -122.8546 | 0.29755 | 1.4211e-13 | -0.014064 | -0.00049791 | 0.063554 | -0.0092089 | 0.060522 | 0.020908 | 0.0085562 | 0.0083539 | -0.0047473 | 0.030647 | 0.0073689 | -122.2465 | -0.13137 | -122.7521 | 0.2902 | -0.072904 | 0.435 | -122.563 | 0.055992 | 0.014095 | 0.007751 | 0.14861 | 0.25637 | -0.17539 | -0.22367 | 0.29159 | -0.007342 | 0.60813 | 0.1025 | -0.18909 | -0.37045 | 0.13745 | 122.6309 | -0.14894 | 122.9106 | 122.8624 | 0.23142 | -0.041174 | -0.47294 | 123.1448 | 122.7817 | 123.2896 | 122.7232 | -122.8606 | 123.0032 | 123.111 | 122.6792 | 122.8687 | -0.52122
346.75 | 123.1842 | -122.9004 | 0.34332 | 1.4211e-13 | -0.014064 | -0.00028411 | 0.06334 | -0.0098499 | 0.060949 | -0.0019839 | 0.0083426 | 0.0079267 | -0.0049609 | 0.030861 | 0.0075825 | -122.2602 | -0.13595 | -122.7521 | 0.29478 | -0.077483 | 0.45789 | -122.5768 | 0.069728 | 0.018674 | -0.001407 | 0.14403 | 0.25637 | -0.17081 | -0.22367 | 0.32363 | -0.048541 | 0.64017 | 0.14828 | -0.17535 | -0.42081 | 0.11457 | 122.6767 | -0.19929 | 122.9701 | 122.899 | 0.22227 | -0.086951 | -0.51414 | 123.1952 | 122.8229 | 123.3583 | 122.7644 | -122.9201 | 123.0444 | 123.1568 | 122.7296 | 122.9191 | -0.567
348.5 | 123.175 | -122.8867 | 0.33875 | 1.4211e-13 | -0.013637 | -0.00028411 | 0.063126 | -0.0094225 | 0.060736 | 0.013277 | 0.0085562 | 0.0085677 | -0.0043199 | 0.031074 | 0.0077963 | -122.2465 | -0.13595 | -122.743 | 0.29936 | -0.072904 | 0.45789 | -122.563 | 0.055992 | 0.018674 | 0.003172 | 0.13945 | 0.25637 | -0.17539 | -0.2191 | 0.32363 | -0.039384 | 0.64017 | 0.1437 | -0.17993 | -0.41165 | 0.11915 | 122.6676 | -0.1993 | 122.9427 | 122.8898 | 0.22227 | -0.082373 | -0.51414 | 123.186 | 122.8138 | 123.3445 | 122.7507 | -122.9018 | 123.0261 | 123.143 | 122.7113 | 122.9053 | -0.55784
350.1875 | 123.2803 | -122.8271 | 0.3479 | 1.4211e-13 | -0.01385 | -0.00049791 | 0.063554 | -0.010063 | 0.060308 | 0.013277 | 0.0085562 | 0.0083539 | -0.0049609 | 0.031288 | 0.0075825 | -122.2419 | -0.13137 | -122.7384 | 0.30852 | -0.072904 | 0.38921 | -122.563 | 0.06515 | 0.018674 | 0.003172 | 0.14861 | 0.25179 | -0.17997 | -0.20536 | 0.26412 | -0.039383 | 0.58524 | 0.088772 | -0.17535 | -0.4208 | 0.041311 | 122.6218 | -0.19929 | 122.8923 | 122.8303 | 0.20853 | -0.096106 | -0.52787 | 123.1357 | 122.7542 | 123.2164 | 122.6958 | -122.9109 | 122.9758 | 123.0789 | 122.6472 | 122.8458 | -0.55326
351.9219 | 123.1934 | -122.8958 | 0.34332 | 1.4211e-13 | -0.014064 | -7.051e-05 | 0.063554 | -0.0096363 | 0.060736 | 0.0056466 | 0.0085562 | 0.0085677 | -0.0049609 | 0.030861 | 0.0073689 | -122.2465 | -0.13137 | -122.7475 | 0.29478 | -0.068325 | 0.39379 | -122.5722 | 0.06515 | 0.014095 | 0.007751 | 0.13945 | 0.25637 | -0.16624 | -0.21452 | 0.32363 | -0.048541 | 0.64933 | 0.14828 | -0.17535 | -0.41165 | 0.050466 | 122.6813 | -0.20387 | 122.961 | 122.9036 | 0.22227 | -0.086951 | -0.50956 | 123.1906 | 122.8275 | 123.2896 | 122.7644 | -122.9155 | 123.0353 | 123.1522 | 122.7296 | 122.9099 | -0.55784
353.6094 | 123.2712 | -122.8409 | 0.28381 | 1.4211e-13 | -0.014064 | -0.00049791 | 0.06334 | -0.0094225 | 0.060736 | 0.0056466 | 0.0085562 | 0.0083539 | -0.0049609 | 0.030861 | 0.0071553 | -122.2556 | -0.12679 | -122.7521 | 0.2902 | -0.072904 | 0.42584 | -122.5722 | 0.06515 | 0.014095 | -0.001407 | 0.13945 | 0.25637 | -0.17539 | -0.21452 | 0.2687 | 0.006391 | 0.58524 | 0.08877 | -0.17993 | -0.35672 | 0.14203 | 122.6264 | -0.14436 | 122.906 | 122.8395 | 0.21311 | -0.027441 | -0.45921 | 123.1311 | 122.768 | 123.2667 | 122.7141 | -122.856 | 122.9803 | 123.0973 | 122.6655 | 122.855 | -0.49833
355.3594 | 123.1522 | -122.8821 | 0.32959 | 1.4211e-13 | -0.014278 | -0.00071151 | 0.063554 | -0.0096363 | 0.060736 | 0.013277 | 0.0087698 | 0.0085677 | -0.0047473 | 0.030647 | 0.0077963 | -122.2602 | -0.12679 | -122.7613 | 0.27647 | -0.082062 | 0.40295 | -122.5722 | 0.060571 | 0.018674 | 0.003172 | 0.14861 | 0.25179 | -0.17081 | -0.22367 | 0.3099 | -0.053121 | 0.62186 | 0.12081 | -0.18908 | -0.41165 | 0.073356 | 122.6584 | -0.18098 | 122.9427 | 122.8853 | 0.22685 | -0.077796 | -0.5004 | 123.1585 | 122.8 | 123.285 | 122.7553 | -122.9018 | 123.0307 | 123.1339 | 122.7113 | 122.9008 | -0.55326
357.1094 | 123.2529 | -122.8592 | 0.28839 | 1.4211e-13 | -0.01385 | -0.00028411 | 0.06334 | -0.0094225 | 0.060308 | -0.0019839 | 0.0085562 | 0.0081403 | -0.0051745 | 0.030861 | 0.0073689 | -122.2694 | -0.13595 | -122.775 | 0.26731 | -0.077483 | 0.38921 | -122.5905 | 0.06515 | 0.018674 | -0.001407 | 0.14403 | 0.25637 | -0.16624 | -0.2191 | 0.26869 | -0.021079 | 0.58981 | 0.08419 | -0.1845 | -0.36587 | 0.10082 | 122.6401 | -0.14436 | 122.9243 | 122.8578 | 0.21769 | -0.032019 | -0.45463 | 123.1265 | 122.7817 | 123.2484 | 122.7232 | -122.8789 | 123.0032 | 123.1156 | 122.693 | 122.8779 | -0.50749
358.7969 | 123.317 | -122.8546 | 0.30212 | 1.4211e-13 | -0.01385 | -7.051e-05 | 0.06334 | -0.0096363 | 0.060308 | -0.0019839 | 0.0085562 | 0.0081403 | -0.0045337 | 0.031288 | 0.0077963 | -122.2602 | -0.12679 | -122.775 | 0.26731 | -0.077483 | 0.34342 | -122.5905 | 0.06515 | 0.014095 | -0.001407 | 0.14403 | 0.26095 | -0.17539 | -0.21452 | 0.26412 | -0.034812 | 0.59439 | 0.079612 | -0.1845 | -0.37961 | 0.0413 | 122.6401 | -0.1581 | 122.9198 | 122.8532 | 0.21311 | -0.041173 | -0.47752 | 123.1219 | 122.7771 | 123.198 | 122.7278 | -122.8926 | 122.9986 | 123.1156 | 122.6792 | 122.8687 | -0.51664
360.5625 | 123.2941 | -122.8592 | 0.31586 | 1.4211e-13 | -0.014064 | -0.00049791 | 0.06334 | -0.0098499 | 0.060522 | 0.013277 | 0.0087698 | 0.0085677 | -0.0045337 | 0.031288 | 0.0075825 | -122.2602 | -0.12222 | -122.7704 | 0.27647 | -0.072904 | 0.38463 | -122.5859 | 0.06515 | 0.023253 | -0.001407 | 0.13945 | 0.25637 | -0.17539 | -0.2191 | 0.27327 | -0.039388 | 0.59897 | 0.088768 | -0.1845 | -0.38876 | 0.068775 | 122.6401 | -0.17641 | 122.9243 | 122.8578 | 0.21769 | -0.059485 | -0.49125 | 123.1357 | 122.7863 | 123.2438 | 122.737 | -122.9018 | 122.9986 | 123.1156 | 122.6838 | 122.8824 | -0.53495
362.25 | 123.2803 | -122.818 | 0.33417 | 1.4211e-13 | -0.014278 | -0.00071151 | 0.06334 | -0.0098499 | 0.060308 | 0.0056466 | 0.0085562 | 0.0083539 | -0.0049609 | 0.031074 | 0.0073689 | -122.2328 | -0.13137 | -122.7521 | 0.29936 | -0.068325 | 0.43042 | -122.5447 | 0.060571 | 0.014095 | 0.003172 | 0.14403 | 0.25637 | -0.17539 | -0.2191 | 0.27328 | -0.034806 | 0.58524 | 0.065882 | -0.2074 | -0.40249 | 0.096251 | 122.5989 | -0.19014 | 122.8786 | 122.8212 | 0.22227 | -0.077795 | -0.50956 | 123.1174 | 122.7497 | 123.2484 | 122.6866 | -122.8789 | 122.962 | 123.0744 | 122.6426 | 122.8321 | -0.55326
363.9844 | 123.1567 | -122.8363 | 0.36163 | 1.4211e-13 | -0.014064 | -7.051e-05 | 0.063554 | -0.0096363 | 0.060736 | 0.0056466 | 0.0085562 | 0.0087813 | -0.0047473 | 0.031074 | 0.0073689 | -122.2236 | -0.12679 | -122.7338 | 0.31767 | -0.068325 | 0.435 | -122.5356 | 0.06515 | 0.014095 | 0.003172 | 0.14861 | 0.26095 | -0.16624 | -0.22825 | 0.30075 | -0.043959 | 0.61271 | 0.10251 | -0.19825 | -0.42996 | 0.073364 | 122.6081 | -0.21303 | 122.9015 | 122.8395 | 0.23142 | -0.10068 | -0.52787 | 123.154 | 122.768 | 123.2713 | 122.7095 | -122.8972 | 122.9849 | 123.0973 | 122.6701 | 122.8504 | -0.58988
365.6875 | 123.2483 | -122.7997 | 0.33875 | 1.4211e-13 | -0.01385 | -7.051e-05 | 0.06334 | -0.0094225 | 0.060736 | 0.0056466 | 0.008129 | 0.0081403 | -0.0049609 | 0.031288 | 0.0075825 | -122.219 | -0.13137 | -122.7338 | 0.32225 | -0.068325 | 0.46705 | -122.5356 | 0.060571 | 0.014095 | 0.007751 | 0.14861 | 0.25637 | -0.17081 | -0.2191 | 0.26413 | -0.016492 | 0.58067 | 0.065885 | -0.19825 | -0.40707 | 0.1283 | 122.5806 | -0.19014 | 122.8603 | 122.8074 | 0.22685 | -0.082373 | -0.50956 | 123.1219 | 122.7314 | 123.2667 | 122.6683 | -122.8743 | 122.9483 | 123.0561 | 122.6289 | 122.8138 | -0.55784
367.4219 | 123.2437 | -122.7859 | 0.37537 | 1.4211e-13 | -0.01385 | -0.00071151 | 0.06334 | -0.010277 | 0.060522 | -0.0019839 | 0.0085562 | 0.0085677 | -0.0047473 | 0.031074 | 0.0075825 | -122.1824 | -0.12679 | -122.6972 | 0.34972 | -0.054588 | 0.45789 | -122.4943 | 0.060571 | 0.009516 | 0.007751 | 0.13945 | 0.26095 | -0.17081 | -0.21452 | 0.29161 | -0.025643 | 0.60356 | 0.088779 | -0.20283 | -0.42995 | 0.082524 | 122.5714 | -0.23592 | 122.8465 | 122.7937 | 0.22227 | -0.11441 | -0.54618 | 123.1357 | 122.7314 | 123.2438 | 122.6592 | -122.8697 | 122.9254 | 123.0469 | 122.6151 | 122.7955 | -0.58988
369.0938 | 123.1705 | -122.7951 | 0.40283 | 1.4211e-13 | -0.013637 | -0.00071151 | 0.063126 | -0.0098499 | 0.060308 | 0.013277 | 0.0083426 | 0.0083539 | -0.0051745 | 0.030861 | 0.0073689 | -122.1824 | -0.12679 | -122.7018 | 0.34972 | -0.050009 | 0.46247 | -122.4943 | 0.06515 | 0.014095 | 0.003172 | 0.14403 | 0.25179 | -0.17539 | -0.21452 | 0.30076 | -0.053109 | 0.61272 | 0.093355 | -0.20741 | -0.45284 | 0.059636 | 122.5806 | -0.2588 | 122.8603 | 122.7983 | 0.21769 | -0.15104 | -0.57822 | 123.1448 | 122.7451 | 123.2576 | 122.6683 | -122.8972 | 122.9391 | 123.0469 | 122.6197 | 122.8092 | -0.61735
370.8281 | 123.1888 | -122.9004 | 0.31128 | 1.4211e-13 | -0.014064 | -0.00049791 | 0.063554 | -0.0096363 | 0.060736 | 0.020908 | 0.008129 | 0.0083539 | -0.0049609 | 0.031502 | 0.0071553 | -122.2694 | -0.13137 | -122.7887 | 0.25816 | -0.082062 | 0.32969 | -122.5859 | 0.060571 | 0.014095 | 0.003172 | 0.14403 | 0.25179 | -0.16624 | -0.2191 | 0.31447 | -0.053124 | 0.63101 | 0.11165 | -0.20282 | -0.39334 | 0.01841 | 122.6813 | -0.16725 | 122.961 | 122.9036 | 0.22227 | -0.059485 | -0.47751 | 123.1585 | 122.8183 | 123.2301 | 122.769 | -122.8972 | 123.0444 | 123.1522 | 122.7342 | 122.9145 | -0.53037
372.5 | 123.2803 | -122.8363 | 0.28381 | 1.4211e-13 | -0.014064 | -0.00049791 | 0.06334 | -0.0096363 | 0.060308 | 0.0056466 | 0.0085562 | 0.0085677 | -0.0051745 | 0.031074 | 0.0075825 | -122.2419 | -0.13137 | -122.7704 | 0.28563 | -0.082062 | 0.43042 | -122.563 | 0.069728 | 0.009516 | -0.001407 | 0.14861 | 0.25637 | -0.17081 | -0.2191 | 0.27328 | 0.001812 | 0.5944 | 0.06588 | -0.2074 | -0.36587 | 0.14661 | 122.6172 | -0.13521 | 122.906 | 122.8349 | 0.21769 | -0.027441 | -0.45463 | 123.1219 | 122.7542 | 123.2667 | 122.7049 | -122.8468 | 122.9849 | 123.0927 | 122.6655 | 122.8458 | -0.50291
374.2344 | 123.1842 | -122.7951 | 0.39368 | 1.4211e-13 | -0.014064 | -0.00028411 | 0.06334 | -0.0096363 | 0.060095 | -0.0019839 | 0.0083426 | 0.0081403 | -0.0047473 | 0.031288 | 0.0073689 | -122.1778 | -0.13137 | -122.7063 | 0.33599 | -0.050009 | 0.42584 | -122.5035 | 0.06515 | 0.014095 | 0.003172 | 0.14861 | 0.25637 | -0.16624 | -0.22825 | 0.29161 | -0.057689 | 0.61729 | 0.088777 | -0.20283 | -0.44369 | 0.032162 | 122.5669 | -0.24507 | 122.8603 | 122.7983 | 0.23142 | -0.13731 | -0.55991 | 123.1311 | 122.7451 | 123.2209 | 122.6637 | -122.8972 | 122.9437 | 123.0515 | 122.6289 | 122.8092 | -0.62193
375.9219 | 123.143 | -122.8546 | 0.33875 | 1.4211e-13 | -0.014278 | -7.051e-05 | 0.063126 | -0.0094225 | 0.060522 | -0.0019839 | 0.0083426 | 0.0083539 | -0.0049609 | 0.031288 | 0.0073689 | -122.2053 | -0.12222 | -122.7384 | 0.32683 | -0.063746 | 0.46705 | -122.531 | 0.06515 | 0.014095 | -0.001407 | 0.13945 | 0.26095 | -0.17997 | -0.21452 | 0.32364 | -0.011914 | 0.64933 | 0.11624 | -0.2074 | -0.40249 | 0.1283 | 122.6401 | -0.1993 | 122.9198 | 122.8532 | 0.21311 | -0.077794 | -0.51872 | 123.1814 | 122.7909 | 123.3217 | 122.7324 | -122.8697 | 122.9941 | 123.1156 | 122.6746 | 122.8687 | -0.55326
377.6719 | 123.1979 | -122.85 | 0.33875 | 1.4211e-13 | -0.01385 | -0.00049791 | 0.063554 | -0.0094225 | 0.060522 | 0.013277 | 0.0085562 | 0.0085677 | -0.0047473 | 0.031288 | 0.0071553 | -122.2328 | -0.13137 | -122.7567 | 0.29936 | -0.068325 | 0.42126 | -122.5584 | 0.069728 | 0.004938 | -0.005985 | 0.14403 | 0.26553 | -0.16624 | -0.21452 | 0.29159 | -0.039384 | 0.61728 | 0.093348 | -0.19824 | -0.40707 | 0.082516 | 122.6355 | -0.19472 | 122.9198 | 122.8441 | 0.20853 | -0.073215 | -0.50498 | 123.1494 | 122.7817 | 123.2713 | 122.7187 | -122.8972 | 122.9941 | 123.1156 | 122.6838 | 122.855 | -0.55326
379.3594 | 123.1384 | -122.8592 | 0.34332 | 1.4211e-13 | -0.014278 | -0.00028411 | 0.063126 | -0.0098499 | 0.060522 | 0.0056466 | 0.008129 | 0.0087813 | -0.0049609 | 0.030861 | 0.0075825 | -122.2328 | -0.12679 | -122.7842 | 0.2902 | -0.072904 | 0.45789 | -122.5447 | 0.055992 | 0.018674 | 0.007751 | 0.13487 | 0.26553 | -0.17997 | -0.21452 | 0.31448 | -0.053119 | 0.62644 | 0.075033 | -0.23945 | -0.41623 | 0.11457 | 122.6447 | -0.20845 | 122.9152 | 122.8669 | 0.22227 | -0.077793 | -0.52329 | 123.1494 | 122.7863 | 123.3171 | 122.7324 | -122.888 | 122.9941 | 123.1247 | 122.6792 | 122.8779 | -0.55784
381.1094 | 123.2758 | -122.8043 | 0.32501 | 1.4211e-13 | -0.014278 | -7.051e-05 | 0.06334 | -0.0098499 | 0.060736 | -0.0019839 | 0.0087698 | 0.0085677 | -0.0053883 | 0.031502 | 0.0073689 | -122.2236 | -0.13137 | -122.7658 | 0.29936 | -0.086641 | 0.44415 | -122.5401 | 0.069728 | 0.009516 | 0.003172 | 0.14403 | 0.26095 | -0.17539 | -0.21452 | 0.26413 | -0.025651 | 0.58066 | 0.038415 | -0.22571 | -0.41165 | 0.11914 | 122.5897 | -0.18098 | 122.874 | 122.8074 | 0.21769 | -0.064061 | -0.5004 | 123.1036 | 122.7176 | 123.2484 | 122.6729 | -122.8651 | 122.9483 | 123.0652 | 122.6289 | 122.8138 | -0.53953
382.7812 | 123.175 | -122.8821 | 0.33417 | 1.4211e-13 | -0.014278 | -0.00028411 | 0.063126 | -0.0098499 | 0.060308 | 0.020908 | 0.0083426 | 0.0085677 | -0.0049609 | 0.031716 | 0.0075825 | -122.2328 | -0.12679 | -122.775 | 0.29478 | -0.077483 | 0.45331 | -122.5539 | 0.06515 | 0.014095 | 0.007751 | 0.14403 | 0.26553 | -0.17539 | -0.2191 | 0.32821 | -0.039385 | 0.64933 | 0.10708 | -0.22113 | -0.41165 | 0.11914 | 122.663 | -0.19014 | 122.9472 | 122.8898 | 0.22685 | -0.068637 | -0.50956 | 123.1769 | 122.8046 | 123.3354 | 122.7553 | -122.888 | 123.0261 | 123.1476 | 122.7067 | 122.8962 | -0.55326
384.5312 | 123.2025 | -122.8271 | 0.30212 | 1.4211e-13 | -0.014064 | -7.051e-05 | 0.06334 | -0.0092089 | 0.060308 | 0.0056466 | 0.0085562 | 0.0081403 | -0.0047473 | 0.031288 | 0.0073689 | -122.2236 | -0.13137 | -122.7842 | 0.2902 | -0.072904 | 0.44873 | -122.5539 | 0.06515 | 0.018674 | 0.003172 | 0.14403 | 0.26095 | -0.17081 | -0.21452 | 0.27328 | -0.01192 | 0.60355 | 0.042989 | -0.23029 | -0.37503 | 0.14661 | 122.6126 | -0.1581 | 122.8923 | 122.8303 | 0.21769 | -0.041173 | -0.47294 | 123.1174 | 122.7542 | 123.2759 | 122.6958 | -122.856 | 122.9712 | 123.0881 | 122.6563 | 122.8458 | -0.51664
386.2344 | 123.2666 | -122.8592 | 0.31128 | 1.4211e-13 | -0.013637 | -0.00049791 | 0.06334 | -0.0098499 | 0.060522 | 0.0056466 | 0.0085562 | 0.0083539 | -0.0049609 | 0.031502 | 0.0075825 | -122.2511 | -0.12679 | -122.7979 | 0.27647 | -0.086641 | 0.39837 | -122.5676 | 0.069728 | 0.018674 | 0.003172 | 0.13945 | 0.27011 | -0.17081 | -0.21452 | 0.29159 | -0.03481 | 0.60813 | 0.061299 | -0.23029 | -0.39792 | 0.087089 | 122.6447 | -0.17183 | 122.9289 | 122.8624 | 0.21769 | -0.041171 | -0.48209 | 123.1357 | 122.7726 | 123.2576 | 122.7324 | -122.8789 | 122.9986 | 123.1293 | 122.6884 | 122.8779 | -0.5258
387.9844 | 123.2254 | -122.8455 | 0.28381 | 1.4211e-13 | -0.014278 | -0.00028411 | 0.063554 | -0.0098499 | 0.060095 | 0.0056466 | 0.0085562 | 0.0079267 | -0.0049609 | 0.031288 | 0.0071553 | -122.2602 | -0.13137 | -122.8071 | 0.25816 | -0.077483 | 0.42126 | -122.5813 | 0.060571 | 0.014095 | 0.007751 | 0.14861 | 0.26095 | -0.17081 | -0.22825 | 0.26412 | -0.025658 | 0.58524 | 0.038409 | -0.22571 | -0.3613 | 0.13745 | 122.6172 | -0.13521 | 122.906 | 122.8532 | 0.236 | -0.022862 | -0.45463 | 123.1036 | 122.768 | 123.2667 | 122.7141 | -122.8652 | 122.9941 | 123.1064 | 122.6746 | 122.8596 | -0.51206
389.7188 | 123.1384 | -122.8683 | 0.30212 | 1.4211e-13 | -0.014278 | -7.051e-05 | 0.063126 | -0.0098499 | 0.060095 | 0.0056466 | 0.0085562 | 0.0085677 | -0.0049609 | 0.031288 | 0.0075825 | -122.2556 | -0.12222 | -122.8116 | 0.26273 | -0.077483 | 0.40295 | -122.5813 | 0.060571 | 0.009516 | -0.001407 | 0.14403 | 0.26095 | -0.16624 | -0.21452 | 0.28701 | -0.03939 | 0.6127 | 0.056719 | -0.23029 | -0.37961 | 0.10082 | 122.6538 | -0.1581 | 122.9289 | 122.8669 | 0.21311 | -0.041173 | -0.46836 | 123.1311 | 122.7909 | 123.2713 | 122.7461 | -122.8835 | 123.0124 | 123.1293 | 122.7021 | 122.8779 | -0.51664
391.4688 | 123.2254 | -122.8455 | 0.27924 | 1.4211e-13 | -0.014278 | -0.00049791 | 0.06334 | -0.0096363 | 0.060522 | 0.013277 | 0.0083426 | 0.0083539 | -0.0049609 | 0.031502 | 0.0073689 | -122.2602 | -0.13595 | -122.8071 | 0.25816 | -0.072904 | 0.40753 | -122.5722 | 0.06515 | 0.014095 | 0.003172 | 0.14403 | 0.25637 | -0.16624 | -0.21452 | 0.27328 | -0.021081 | 0.58524 | 0.038409 | -0.23487 | -0.35214 | 0.12829 | 122.6309 | -0.13521 | 122.9106 | 122.8486 | 0.21769 | -0.022864 | -0.44547 | 123.1036 | 122.7726 | 123.253 | 122.7095 | -122.8514 | 122.9895 | 123.1018 | 122.6792 | 122.8596 | -0.49375
393.2188 | 123.143 | -122.8867 | 0.29755 | 1.4211e-13 | -0.014064 | -0.00028411 | 0.06334 | -0.0098499 | 0.060308 | 0.013277 | 0.0083426 | 0.0083539 | -0.0051745 | 0.031502 | 0.0075825 | -122.2648 | -0.13137 | -122.8162 | 0.25358 | -0.077483 | 0.36632 | -122.5905 | 0.069728 | 0.018674 | 0.007751 | 0.13945 | 0.26095 | -0.17539 | -0.2191 | 0.29616 | -0.043969 | 0.62186 | 0.070451 | -0.22571 | -0.37503 | 0.068772 | 122.6676 | -0.1581 | 122.9564 | 122.8944 | 0.22685 | -0.036595 | -0.47294 | 123.1402 | 122.8092 | 123.253 | 122.7553 | -122.888 | 123.0261 | 123.1476 | 122.7113 | 122.9053 | -0.51664
394.8906 | 123.2758 | -122.8455 | 0.25177 | 1.4211e-13 | -0.014278 | -7.051e-05 | 0.063126 | -0.010063 | 0.060095 | 0.0056466 | 0.0083426 | 0.0085677 | -0.0047473 | 0.031502 | 0.0073689 | -122.2694 | -0.12679 | -122.8116 | 0.25816 | -0.077483 | 0.348 | -122.5951 | 0.06515 | 0.018674 | -0.001407 | 0.14861 | 0.25179 | -0.17997 | -0.2191 | 0.25038 | 0.006385 | 0.57608 | 0.033831 | -0.21655 | -0.32925 | 0.096233 | 122.6264 | -0.10316 | 122.9106 | 122.8441 | 0.21769 | 2.4e-05 | -0.43174 | 123.1036 | 122.768 | 123.1935 | 122.7187 | -122.8468 | 122.9941 | 123.0973 | 122.6655 | 122.8641 | -0.47086
396.6406 | 123.1705 | -122.8867 | 0.28381 | 1.4211e-13 | -0.014491 | 0.00014309 | 0.063554 | -0.010063 | 0.060308 | 0.013277 | 0.0083426 | 0.0081403 | -0.0049609 | 0.031502 | 0.0073689 | -122.2602 | -0.13595 | -122.8162 | 0.25358 | -0.082062 | 0.33885 | -122.5951 | 0.069728 | 0.018674 | 0.003172 | 0.13945 | 0.26095 | -0.17539 | -0.21452 | 0.29158 | -0.030236 | 0.62644 | 0.070451 | -0.22113 | -0.36587 | 0.055033 | 122.6721 | -0.14436 | 122.9564 | 122.8898 | 0.21769 | -0.022862 | -0.45921 | 123.1402 | 122.8046 | 123.2255 | 122.7507 | -122.8789 | 123.0261 | 123.1476 | 122.7113 | 122.9053 | -0.49833
398.3906 | 123.2391 | -122.8317 | 0.27466 | 1.4211e-13 | -0.014278 | -0.00028411 | 0.063126 | -0.010063 | 0.060522 | 0.013277 | 0.0083426 | 0.0083539 | -0.0053883 | 0.031502 | 0.0073689 | -122.2511 | -0.12679 | -122.8116 | 0.25816 | -0.077483 | 0.34342 | -122.5813 | 0.06515 | 0.014095 | 0.01233 | 0.14403 | 0.26095 | -0.16624 | -0.21452 | 0.25039 | -0.016503 | 0.58066 | 0.020098 | -0.23029 | -0.35214 | 0.068766 | 122.6172 | -0.13063 | 122.8969 | 122.8441 | 0.22685 | -0.013707 | -0.44089 | 123.0899 | 122.7542 | 123.1752 | 122.7049 | -122.856 | 122.9758 | 123.0927 | 122.6655 | 122.8458 | -0.48917
400.1406 | 123.2529 | -122.8226 | 0.28839 | 1.4211e-13 | -0.014064 | -0.00028411 | 0.062913 | -0.0098499 | 0.060522 | 0.013277 | 0.008129 | 0.0081403 | -0.0051745 | 0.031074 | 0.0073689 | -122.2465 | -0.13137 | -122.7979 | 0.27189 | -0.077483 | 0.35716 | -122.5722 | 0.06515 | 0.014095 | 0.003172 | 0.14403 | 0.25637 | -0.17539 | -0.21452 | 0.25039 | -0.016501 | 0.57608 | 0.024678 | -0.22571 | -0.36587 | 0.068769 | 122.6081 | -0.14436 | 122.8877 | 122.8257 | 0.21769 | -0.032019 | -0.46378 | 123.0945 | 122.7451 | 123.1797 | 122.6912 | -122.8606 | 122.9666 | 123.0789 | 122.6472 | 122.8367 | -0.50291
401.8281 | 123.1201 | -122.8729 | 0.32959 | 1.4211e-13 | -0.014064 | -0.00049791 | 0.063126 | -0.0096363 | 0.060095 | -0.0019839 | 0.0085562 | 0.0085677 | -0.0051745 | 0.031502 | 0.0073689 | -122.2373 | -0.12679 | -122.7933 | 0.26731 | -0.077483 | 0.435 | -122.563 | 0.055992 | 0.023253 | 0.007751 | 0.13945 | 0.26095 | -0.17081 | -0.20994 | 0.3099 | -0.062278 | 0.63559 | 0.07961 | -0.23029 | -0.40707 | 0.10541 | 122.663 | -0.19014 | 122.9289 | 122.8807 | 0.21769 | -0.068639 | -0.5004 | 123.1402 | 122.7954 | 123.3079 | 122.7461 | -122.8926 | 123.0124 | 123.1339 | 122.7021 | 122.8962 | -0.53953
403.5781 | 123.1338 | -122.8683 | 0.29755 | 1.4211e-13 | -0.014064 | -0.00028411 | 0.062913 | -0.0096363 | 0.060308 | 0.0056466 | 0.0083426 | 0.0085677 | -0.0045337 | 0.031716 | 0.0073689 | -122.2511 | -0.13137 | -122.7979 | 0.26273 | -0.082062 | 0.38005 | -122.5859 | 0.06515 | 0.014095 | 0.003172 | 0.14403 | 0.26095 | -0.17539 | -0.21452 | 0.28243 | -0.034812 | 0.61728 | 0.070454 | -0.21197 | -0.37961 | 0.082507 | 122.6538 | -0.15352 | 122.9335 | 122.8715 | 0.21769 | -0.036595 | -0.47294 | 123.1311 | 122.7863 | 123.2484 | 122.737 | -122.8835 | 123.0124 | 123.1293 | 122.693 | 122.8824 | -0.51206
405.2656 | 123.1659 | -122.8821 | 0.28839 | 1.4211e-13 | -0.014491 | -0.00071151 | 0.063126 | -0.0096363 | 0.060095 | -0.0019839 | 0.0083426 | 0.0083539 | -0.0049609 | 0.031288 | 0.0073689 | -122.2556 | -0.12679 | -122.8025 | 0.249 | -0.077483 | 0.35258 | -122.5813 | 0.060571 | 0.018674 | 0.003172 | 0.13945 | 0.26095 | -0.16624 | -0.2191 | 0.30074 | -0.039393 | 0.62644 | 0.079608 | -0.22113 | -0.36587 | 0.064191 | 122.663 | -0.14894 | 122.9427 | 122.8853 | 0.22227 | -0.02744 | -0.45463 | 123.1311 | 122.8046 | 123.2347 | 122.7553 | -122.8697 | 123.0215 | 123.143 | 122.7158 | 122.9008 | -0.50749
407.0156 | 123.2391 | -122.8409 | 0.25177 | 1.4211e-13 | -0.014064 | -0.00049791 | 0.063126 | -0.0098499 | 0.060308 | -0.0019839 | 0.0085562 | 0.0081403 | -0.0047473 | 0.031502 | 0.0073689 | -122.2694 | -0.13137 | -122.8025 | 0.24442 | -0.072904 | 0.28848 | -122.5905 | 0.060571 | 0.023253 | 0.003172 | 0.14861 | 0.26095 | -0.17081 | -0.2191 | 0.25038 | -0.00735 | 0.5715 | 0.038409 | -0.21197 | -0.32467 | 0.036711 | 122.6218 | -0.10316 | 122.9015 | 122.8441 | 0.22227 | 0.009181 | -0.42258 | 123.0853 | 122.768 | 123.1294 | 122.7095 | -122.8423 | 122.9895 | 123.1018 | 122.6701 | 122.8641 | -0.47086
408.7031 | 123.2574 | -122.8683 | 0.26093 | 1.4211e-13 | -0.014278 | -0.00028411 | 0.063554 | -0.010063 | 0.060522 | -0.0019839 | 0.0087698 | 0.0085677 | -0.0049609 | 0.031716 | 0.0075825 | -122.2648 | -0.13137 | -122.8116 | 0.249 | -0.082062 | 0.36632 | -122.5951 | 0.060571 | 0.014095 | 0.003172 | 0.15776 | 0.25637 | -0.17997 | -0.21452 | 0.27327 | -0.011927 | 0.60355 | 0.056719 | -0.21655 | -0.34299 | 0.10539 | 122.6538 | -0.10316 | 122.9289 | 122.8715 | 0.21769 | -0.004553 | -0.4409 | 123.1173 | 122.7863 | 123.2347 | 122.737 | -122.856 | 123.0261 | 123.1247 | 122.6884 | 122.8824 | -0.47544
410.4531 | 123.1567 | -122.905 | 0.27924 | 1.4211e-13 | -0.014278 | -0.00049791 | 0.06334 | -0.0096363 | 0.060308 | 0.013277 | 0.0083426 | 0.0085677 | -0.0049609 | 0.031502 | 0.0073689 | -122.2648 | -0.13595 | -122.8162 | 0.23526 | -0.086641 | 0.29306 | -122.5997 | 0.069728 | 0.023253 | 0.003172 | 0.15318 | 0.26095 | -0.17081 | -0.21452 | 0.30531 | -0.043973 | 0.64017 | 0.088761 | -0.21655 | -0.36588 | 0.013824 | 122.6905 | -0.12605 | 122.9747 | 122.9081 | 0.21769 | -0.018285 | -0.45005 | 123.1402 | 122.8183 | 123.198 | 122.769 | -122.8789 | 123.0582 | 123.1659 | 122.7342 | 122.9282 | -0.49375
412.2031 | 123.2391 | -122.85 | 0.25635 | 1.4211e-13 | -0.014064 | -7.051e-05 | 0.062913 | -0.0098499 | 0.060736 | 0.0056466 | 0.0085562 | 0.0085677 | -0.0049609 | 0.031502 | 0.0071553 | -122.2602 | -0.13137 | -122.8025 | 0.24442 | -0.082062 | 0.32511 | -122.5859 | 0.055992 | 0.018674 | 0.007751 | 0.15776 | 0.26553 | -0.17081 | -0.21452 | 0.26412 | -0.011928 | 0.58982 | 0.047565 | -0.21655 | -0.33841 | 0.068762 | 122.6355 | -0.098584 | 122.906 | 122.8578 | 0.22227 | 0.009182 | -0.42716 | 123.0945 | 122.768 | 123.1751 | 122.7187 | -122.8423 | 123.0078 | 123.1156 | 122.6792 | 122.8687 | -0.47086
413.9531 | 123.1522 | -122.8729 | 0.27466 | 1.4211e-13 | -0.014278 | -0.00028411 | 0.063126 | -0.0098499 | 0.060095 | 0.013277 | 0.0085562 | 0.0083539 | -0.0047473 | 0.031502 | 0.0071553 | -122.2602 | -0.13595 | -122.8025 | 0.249 | -0.082062 | 0.3709 | -122.5905 | 0.06515 | 0.018674 | 0.016908 | 0.15318 | 0.26553 | -0.17539 | -0.21452 | 0.28243 | -0.02566 | 0.6127 | 0.070453 | -0.21197 | -0.35672 | 0.096238 | 122.6584 | -0.12147 | 122.9381 | 122.8898 | 0.23142 | -0.009128 | -0.45005 | 123.1219 | 122.7909 | 123.2438 | 122.737 | -122.8652 | 123.0261 | 123.1385 | 122.6975 | 122.8916 | -0.48917
415.6875 | 123.1155 | -122.8912 | 0.31128 | 1.4211e-13 | -0.014064 | -7.051e-05 | 0.063554 | -0.010277 | 0.060095 | 0.013277 | 0.008129 | 0.0083539 | -0.0047473 | 0.031502 | 0.0073689 | -122.2511 | -0.13137 | -122.7979 | 0.24442 | -0.082062 | 0.35716 | -122.5813 | 0.060571 | 0.018674 | -0.001407 | 0.15776 | 0.25637 | -0.17081 | -0.2191 | 0.30989 | -0.066859 | 0.64017 | 0.093342 | -0.21655 | -0.39334 | 0.045881 | 122.6721 | -0.15351 | 122.9518 | 122.8898 | 0.21769 | -0.054907 | -0.48209 | 123.1357 | 122.8092 | 123.2484 | 122.7599 | -122.8926 | 123.049 | 123.1476 | 122.7204 | 122.9099 | -0.53037
417.375 | 123.2162 | -122.8775 | 0.23804 | 1.4211e-13 | -0.014278 | -0.00092531 | 0.063126 | -0.0098499 | 0.060095 | -0.0019839 | 0.0085562 | 0.0087813 | -0.0053883 | 0.031288 | 0.0071553 | -122.2648 | -0.14053 | -122.8208 | 0.22611 | -0.082062 | 0.38005 | -122.6042 | 0.069728 | 0.009516 | 0.003172 | 0.16234 | 0.26095 | -0.16624 | -0.2191 | 0.27327 | -0.011931 | 0.6127 | 0.056717 | -0.21655 | -0.3201 | 0.14202 | 122.6584 | -0.075695 | 122.9472 | 122.8807 | 0.22227 | 0.022914 | -0.40427 | 123.1036 | 122.7954 | 123.2576 | 122.737 | -122.8423 | 123.0398 | 123.1385 | 122.7113 | 122.887 | -0.45713
419.1094 | 123.2346 | -122.8821 | 0.23804 | 1.4211e-13 | -0.014491 | -0.00028411 | 0.063126 | -0.0098499 | 0.059881 | 0.013277 | 0.0087698 | 0.0081403 | -0.0051745 | 0.031716 | 0.0069417 | -122.274 | -0.12679 | -122.8162 | 0.23069 | -0.086641 | 0.30222 | -122.5997 | 0.060571 | 0.014095 | -0.001407 | 0.15776 | 0.26095 | -0.17081 | -0.21452 | 0.28242 | -0.007352 | 0.60812 | 0.065873 | -0.21655 | -0.32468 | 0.06418 | 122.6676 | -0.080273 | 122.9427 | 122.8807 | 0.21311 | 0.022914 | -0.40885 | 123.1128 | 122.7954 | 123.1843 | 122.7553 | -122.8377 | 123.0398 | 123.143 | 122.7113 | 122.8962 | -0.45255
420.7812 | 123.2025 | -122.8821 | 0.2243 | 1.4211e-13 | -0.014278 | -7.051e-05 | 0.063126 | -0.0096363 | 0.060308 | -0.0019839 | 0.0085562 | 0.0085677 | -0.0053883 | 0.031502 | 0.0071553 | -122.2785 | -0.13595 | -122.8162 | 0.22153 | -0.082062 | 0.35258 | -122.6088 | 0.074307 | 0.014095 | 0.007751 | 0.14861 | 0.26553 | -0.16624 | -0.22367 | 0.27326 | -0.002776 | 0.60354 | 0.065873 | -0.20739 | -0.30637 | 0.12828 | 122.6584 | -0.075697 | 122.9564 | 122.8898 | 0.23142 | 0.041226 | -0.39054 | 123.1036 | 122.8 | 123.2347 | 122.7461 | -122.8331 | 123.0307 | 123.1476 | 122.7158 | 122.8962 | -0.44798
422.5156 | 123.1247 | -122.9233 | 0.26093 | 1.4211e-13 | -0.014491 | 0.00014309 | 0.063126 | -0.0096363 | 0.059881 | -0.0019839 | 0.0087698 | 0.0079267 | -0.0053883 | 0.031929 | 0.0073689 | -122.2831 | -0.13137 | -122.8345 | 0.21695 | -0.09122 | 0.29764 | -122.618 | 0.06515 | 0.014095 | -0.001407 | 0.16234 | 0.25637 | -0.17081 | -0.20994 | 0.30531 | -0.043975 | 0.64016 | 0.088759 | -0.21655 | -0.35215 | 0.036713 | 122.7133 | -0.098583 | 122.9884 | 122.9219 | 0.20853 | -0.004553 | -0.43174 | 123.1402 | 122.8321 | 123.2209 | 122.7919 | -122.8789 | 123.0856 | 123.1797 | 122.7525 | 122.9374 | -0.47086
424.25 | 123.1934 | -122.9095 | 0.23346 | 1.4211e-13 | -0.014278 | -0.00071151 | 0.062913 | -0.010063 | 0.060308 | 0.0056466 | 0.008129 | 0.0081403 | -0.0049609 | 0.031716 | 0.0073689 | -122.2923 | -0.13595 | -122.8437 | 0.20321 | -0.095798 | 0.26559 | -122.6317 | 0.069728 | 0.023253 | 0.01233 | 0.15776 | 0.26095 | -0.17081 | -0.21452 | 0.27784 | -0.030245 | 0.61728 | 0.06587 | -0.21197 | -0.32926 | 0.032129 | 122.695 | -0.075695 | 122.9793 | 122.9219 | 0.22685 | 0.027492 | -0.40427 | 123.1128 | 122.8137 | 123.1751 | 122.7736 | -122.8652 | 123.0673 | 123.1705 | 122.7387 | 122.9328 | -0.44798
425.9844 | 123.1705 | -122.9233 | 0.24261 | 1.4211e-13 | -0.014278 | -0.00049791 | 0.063126 | -0.0098499 | 0.060308 | 0.0056466 | 0.0083426 | 0.0081403 | -0.0047473 | 0.031716 | 0.0073689 | -122.2968 | -0.13137 | -122.8391 | 0.21237 | -0.10038 | 0.33427 | -122.6271 | 0.060571 | 0.018674 | 0.007751 | 0.15776 | 0.27011 | -0.17081 | -0.20994 | 0.29615 | -0.030244 | 0.62643 | 0.084181 | -0.21197 | -0.34299 | 0.091652 | 122.7133 | -0.084851 | 122.9838 | 122.931 | 0.21769 | 0.027493 | -0.41343 | 123.1356 | 122.8229 | 123.2575 | 122.7919 | -122.8697 | 123.081 | 123.1934 | 122.7525 | 122.942 | -0.45255
427.6719 | 123.1567 | -122.9416 | 0.24261 | 1.4211e-13 | -0.014278 | -0.00049791 | 0.06334 | -0.0098499 | 0.060095 | 0.013277 | 0.0085562 | 0.0083539 | -0.0051745 | 0.031502 | 0.0069417 | -122.2923 | -0.13137 | -122.8437 | 0.20321 | -0.10038 | 0.32969 | -122.6271 | 0.06515 | 0.023253 | 0.003172 | 0.15318 | 0.26095 | -0.17997 | -0.2191 | 0.31446 | -0.039401 | 0.64932 | 0.097913 | -0.21655 | -0.34299 | 0.087074 | 122.7225 | -0.08943 | 123.0067 | 122.9448 | 0.22227 | 0.018336 | -0.42259 | 123.1448 | 122.8412 | 123.2713 | 122.8102 | -122.8697 | 123.0948 | 123.2025 | 122.7616 | 122.9648 | -0.46171
429.4062 | 123.2025 | -122.8958 | 0.23804 | 1.4211e-13 | -0.014491 | -0.00028411 | 0.06334 | -0.010063 | 0.060522 | -0.0096144 | 0.0083426 | 0.0081403 | -0.0051745 | 0.031716 | 0.0071553 | -122.2831 | -0.13137 | -122.8299 | 0.21237 | -0.09122 | 0.31137 | -122.6271 | 0.060571 | 0.018674 | 0.007751 | 0.15776 | 0.25637 | -0.17539 | -0.21452 | 0.26868 | -0.025666 | 0.6127 | 0.065872 | -0.20281 | -0.32926 | 0.073337 | 122.6813 | -0.080273 | 122.9564 | 122.9036 | 0.22227 | 0.018335 | -0.41343 | 123.1082 | 122.8046 | 123.2072 | 122.7644 | -122.8652 | 123.0536 | 123.1522 | 122.7204 | 122.9145 | -0.45255
431.1562 | 123.262 | -122.8775 | 0.2243 | 1.4211e-13 | -0.014491 | -0.00071151 | 0.062913 | -0.0098499 | 0.060095 | 0.0056466 | 0.0083426 | 0.0081403 | -0.0051745 | 0.031929 | 0.0071553 | -122.274 | -0.13595 | -122.8254 | 0.21237 | -0.095798 | 0.3068 | -122.6088 | 0.060571 | 0.023253 | -0.001407 | 0.15318 | 0.25637 | -0.17539 | -0.21452 | 0.26869 | -0.011933 | 0.60355 | 0.052139 | -0.21655 | -0.3201 | 0.082492 | 122.663 | -0.071119 | 122.9381 | 122.8761 | 0.21311 | 0.032068 | -0.3997 | 123.0899 | 122.7817 | 123.1843 | 122.7416 | -122.8331 | 123.0307 | 123.1339 | 122.7021 | 122.9008 | -0.43882
432.8438 | 123.2758 | -122.8729 | 0.21973 | 1.4211e-13 | -0.014705 | -0.00071151 | 0.062913 | -0.0096363 | 0.060308 | 0.013277 | 0.0087698 | 0.0083539 | -0.0051745 | 0.031716 | 0.0067279 | -122.2785 | -0.13595 | -122.8345 | 0.22153 | -0.095798 | 0.35258 | -122.618 | 0.060571 | 0.027831 | 0.01233 | 0.15776 | 0.26095 | -0.17081 | -0.21452 | 0.25495 | 0.001801 | 0.59439 | 0.038405 | -0.21655 | -0.31552 | 0.13286 | 122.6584 | -0.061963 | 122.9335 | 122.8853 | 0.22685 | 0.041224 | -0.39054 | 123.0945 | 122.7771 | 123.2255 | 122.737 | -122.8377 | 123.0307 | 123.1339 | 122.7021 | 122.9008 | -0.43424
434.5781 | 123.2437 | -122.8546 | 0.22888 | 1.4211e-13 | -0.014278 | -0.00049791 | 0.063126 | -0.0096363 | 0.060308 | 0.0056466 | 0.0083426 | 0.0081403 | -0.0049609 | 0.031716 | 0.0075825 | -122.2785 | -0.14053 | -122.8345 | 0.21695 | -0.095798 | 0.3068 | -122.6088 | 0.060571 | 0.023253 | 0.007751 | 0.15318 | 0.25637 | -0.17081 | -0.20994 | 0.2458 | -0.011932 | 0.57608 | 0.020094 | -0.2257 | -0.32468 | 0.077914 | 122.6447 | -0.075697 | 122.9152 | 122.8624 | 0.21769 | 0.02749 | -0.3997 | 123.0716 | 122.7588 | 123.1614 | 122.7141 | -122.8377 | 123.0078 | 123.111 | 122.6838 | 122.8779 | -0.43882
436.3125 | 123.2483 | -122.85 | 0.21973 | 1.4211e-13 | -0.014064 | -0.00049791 | 0.063126 | -0.0098499 | 0.060095 | 0.0056466 | 0.0085562 | 0.0083539 | -0.0049609 | 0.031716 | 0.0075825 | -122.2785 | -0.13137 | -122.8254 | 0.22153 | -0.09122 | 0.35716 | -122.6042 | 0.06515 | 0.023253 | 0.01233 | 0.15776 | 0.26553 | -0.17081 | -0.2191 | 0.2458 | 0.001801 | 0.5715 | 0.024674 | -0.22113 | -0.31095 | 0.13743 | 122.6309 | -0.061963 | 122.9152 | 122.8624 | 0.23143 | 0.045803 | -0.39054 | 123.0716 | 122.7588 | 123.2072 | 122.7187 | -122.824 | 123.0078 | 123.1156 | 122.6792 | 122.8733 | -0.43882
438.0625 | 123.1567 | -122.8867 | 0.24261 | 1.4211e-13 | -0.014491 | -0.00049791 | 0.063126 | -0.010063 | 0.060095 | 0.0056466 | 0.0085562 | 0.0085677 | -0.0053883 | 0.031716 | 0.0071553 | -122.2785 | -0.13137 | -122.8254 | 0.22153 | -0.09122 | 0.3068 | -122.6134 | 0.06515 | 0.027831 | 0.007751 | 0.16234 | 0.25637 | -0.17081 | -0.21452 | 0.27326 | -0.021087 | 0.60812 | 0.061295 | -0.21197 | -0.33383 | 0.064181 | 122.6721 | -0.080273 | 122.9518 | 122.8944 | 0.22227 | 0.013757 | -0.41343 | 123.1082 | 122.7954 | 123.1935 | 122.7553 | -122.856 | 123.049 | 123.143 | 122.7158 | 122.9145 | -0.45713
439.75 | 123.1018 | -122.905 | 0.2655 | 1.4211e-13 | -0.01385 | -0.00049791 | 0.063126 | -0.0098499 | 0.059881 | -0.0019839 | 0.0087698 | 0.0081403 | -0.0049609 | 0.031716 | 0.0071553 | -122.274 | -0.13595 | -122.8254 | 0.21695 | -0.09122 | 0.29764 | -122.5997 | 0.06515 | 0.018674 | 0.007751 | 0.15776 | 0.25637 | -0.16624 | -0.20994 | 0.30531 | -0.048553 | 0.63101 | 0.079605 | -0.22571 | -0.35672 | 0.032135 | 122.695 | -0.10774 | 122.9701 | 122.9127 | 0.21769 | -0.009131 | -0.43174 | 123.1219 | 122.8137 | 123.2026 | 122.769 | -122.8652 | 123.0627 | 123.1613 | 122.7387 | 122.9236 | -0.47544
441.4844 | 123.1567 | -122.905 | 0.25635 | 1.4211e-13 | -0.014705 | -0.00049791 | 0.063126 | -0.010063 | 0.060095 | 0.0056466 | 0.0083426 | 0.0081403 | -0.0051745 | 0.031929 | 0.0071553 | -122.2785 | -0.13137 | -122.8254 | 0.22153 | -0.086641 | 0.27932 | -122.6088 | 0.069728 | 0.023253 | 0.01233 | 0.15776 | 0.26553 | -0.16624 | -0.20994 | 0.29615 | -0.03482 | 0.62643 | 0.079605 | -0.21655 | -0.34299 | 0.022976 | 122.695 | -0.098584 | 122.9747 | 122.9173 | 0.22227 | 0.009182 | -0.42258 | 123.1265 | 122.8183 | 123.1843 | 122.7736 | -122.8652 | 123.0627 | 123.1705 | 122.7387 | 122.9282 | -0.46629
443.2344 | 123.1338 | -122.8958 | 0.24719 | 1.4211e-13 | -0.014278 | -0.00028411 | 0.062913 | -0.0098499 | 0.060308 | 0.0056466 | 0.0087698 | 0.0079267 | -0.0051745 | 0.031502 | 0.0075825 | -122.2694 | -0.13595 | -122.8254 | 0.22153 | -0.09122 | 0.31595 | -122.5951 | 0.06515 | 0.018674 | -0.001407 | 0.15318 | 0.26095 | -0.17081 | -0.21452 | 0.30074 | -0.025664 | 0.62643 | 0.07045 | -0.23028 | -0.33841 | 0.068761 | 122.6813 | -0.094007 | 122.961 | 122.8944 | 0.21311 | 0.013759 | -0.41801 | 123.1173 | 122.8046 | 123.2118 | 122.7599 | -122.8423 | 123.049 | 123.1568 | 122.725 | 122.9145 | -0.46171
444.9844 | 123.143 | -122.9095 | 0.26093 | 1.4211e-13 | -0.014491 | -0.00092531 | 0.062913 | -0.0098499 | 0.059881 | 0.013277 | 0.0083426 | 0.0083539 | -0.0049609 | 0.031716 | 0.0067279 | -122.2648 | -0.13137 | -122.8208 | 0.22611 | -0.086641 | 0.33427 | -122.5997 | 0.06515 | 0.023253 | 0.007751 | 0.15776 | 0.26095 | -0.17539 | -0.22367 | 0.30989 | -0.034819 | 0.64475 | 0.088761 | -0.22113 | -0.34757 | 0.073342 | 122.6859 | -0.10316 | 122.9747 | 122.9173 | 0.23142 | 2.6e-05 | -0.43632 | 123.1357 | 122.8229 | 123.2438 | 122.7782 | -122.8606 | 123.0673 | 123.1705 | 122.7342 | 122.9328 | -0.4846
446.6719 | 123.1796 | -122.8729 | 0.20599 | 1.4211e-13 | -0.014491 | -0.00028411 | 0.063126 | -0.0098499 | 0.060308 | -0.0019839 | 0.0083426 | 0.0081403 | -0.0053883 | 0.031929 | 0.0071553 | -122.2694 | -0.13137 | -122.8208 | 0.23069 | -0.09122 | 0.35258 | -122.6042 | 0.06515 | 0.018674 | 0.003172 | 0.15776 | 0.26095 | -0.16624 | -0.2191 | 0.26869 | 0.024691 | 0.60355 | 0.05214 | -0.21655 | -0.29721 | 0.14659 | 122.6538 | -0.04823 | 122.9381 | 122.8761 | 0.22227 | 0.054957 | -0.37223 | 123.1036 | 122.7817 | 123.2255 | 122.7416 | -122.8102 | 123.0307 | 123.1339 | 122.7067 | 122.8916 | -0.42509
448.4062 | 123.2208 | -122.8683 | 0.21973 | 1.4211e-13 | -0.014278 | -0.00028411 | 0.062913 | -0.010063 | 0.059881 | 0.0056466 | 0.0085562 | 0.0081403 | -0.0053883 | 0.031716 | 0.0073689 | -122.2694 | -0.13137 | -122.8299 | 0.22611 | -0.086641 | 0.31595 | -122.6042 | 0.060571 | 0.023253 | 0.003172 | 0.15776 | 0.26095 | -0.17081 | -0.21452 | 0.26411 | 0.006379 | 0.59897 | 0.038406 | -0.22571 | -0.30637 | 0.096226 | 122.6538 | -0.061963 | 122.9289 | 122.8715 | 0.21769 | 0.041224 | -0.39054 | 123.0945 | 122.7817 | 123.1843 | 122.737 | -122.824 | 123.0261 | 123.1293 | 122.6975 | 122.8916 | -0.43424
450.1562 | 123.2391 | -122.8592 | 0.25177 | 1.4211e-13 | -0.014278 | -0.00028411 | 0.063126 | -0.010063 | 0.059881 | 0.0056466 | 0.008129 | 0.0083539 | -0.0049609 | 0.032143 | 0.0071553 | -122.2648 | -0.13137 | -122.8254 | 0.22153 | -0.077483 | 0.28848 | -122.5997 | 0.06515 | 0.023253 | 0.003172 | 0.15776 | 0.26553 | -0.17997 | -0.2191 | 0.25953 | -0.030242 | 0.59439 | 0.033829 | -0.22571 | -0.32925 | 0.036711 | 122.6401 | -0.094006 | 122.9243 | 122.8624 | 0.22227 | 0.01376 | -0.43174 | 123.0807 | 122.7817 | 123.1477 | 122.7278 | -122.8514 | 123.017 | 123.1247 | 122.6792 | 122.8824 | -0.47086
451.8438 | 123.2346 | -122.8592 | 0.24261 | 1.4211e-13 | -0.014278 | -0.00028411 | 0.062699 | -0.0098499 | 0.059881 | -0.0019839 | 0.0085562 | 0.0083539 | -0.0049609 | 0.031716 | 0.0073689 | -122.2648 | -0.13137 | -122.8254 | 0.22153 | -0.086641 | 0.35258 | -122.5951 | 0.055992 | 0.023253 | 0.016908 | 0.16234 | 0.27011 | -0.17081 | -0.2191 | 0.26411 | -0.021087 | 0.59439 | 0.033829 | -0.23028 | -0.32926 | 0.10997 | 122.6401 | -0.080273 | 122.9152 | 122.8761 | 0.236 | 0.027493 | -0.41343 | 123.0807 | 122.7726 | 123.2118 | 122.7278 | -122.8377 | 123.0215 | 123.1293 | 122.6884 | 122.8824 | -0.46171
453.5781 | 123.0972 | -122.9141 | 0.25635 | 1.4211e-13 | -0.014491 | -0.00049791 | 0.062913 | -0.0098499 | 0.060095 | -0.0019839 | 0.0083426 | 0.0085677 | -0.0056019 | 0.031929 | 0.0071553 | -122.2556 | -0.13595 | -122.8071 | 0.22611 | -0.09122 | 0.27475 | -122.5951 | 0.06515 | 0.03241 | 0.01233 | 0.15776 | 0.26095 | -0.17539 | -0.2191 | 0.31905 | -0.030242 | 0.65848 | 0.10707 | -0.21197 | -0.34757 | 0.018397 | 122.695 | -0.098584 | 122.9793 | 122.9265 | 0.23143 | 0.004603 | -0.43174 | 123.1402 | 122.8229 | 123.1889 | 122.7782 | -122.8514 | 123.0719 | 123.1751 | 122.7387 | 122.9465 | -0.47544
455.3281 | 123.2071 | -122.8363 | 0.23804 | 1.4211e-13 | -0.014491 | -0.00028411 | 0.062699 | -0.010063 | 0.059881 | 0.013277 | 0.0085562 | 0.0081403 | -0.0053883 | 0.031929 | 0.0071553 | -122.2511 | -0.14053 | -122.8116 | 0.23069 | -0.086641 | 0.29306 | -122.5905 | 0.06515 | 0.027831 | 0.003172 | 0.15776 | 0.26553 | -0.17081 | -0.21452 | 0.24581 | -0.007352 | 0.58524 | 0.024676 | -0.22113 | -0.32468 | 0.055023 | 122.6218 | -0.080273 | 122.9015 | 122.8395 | 0.21769 | 0.027493 | -0.40885 | 123.067 | 122.7497 | 123.1294 | 122.6958 | -122.8285 | 122.9941 | 123.1018 | 122.6655 | 122.8641 | -0.45255
457.0625 | 123.2391 | -122.8409 | 0.23346 | 1.4211e-13 | -0.014491 | -0.00028411 | 0.062913 | -0.010063 | 0.060308 | -0.0096144 | 0.0083426 | 0.0083539 | -0.0049609 | 0.031929 | 0.0071553 | -122.2602 | -0.14053 | -122.8208 | 0.23526 | -0.082062 | 0.32969 | -122.5951 | 0.051413 | 0.03241 | 0.007751 | 0.15776 | 0.27011 | -0.17081 | -0.21452 | 0.2458 | 0.001804 | 0.58066 | 0.020096 | -0.22571 | -0.31552 | 0.09623 | 122.6264 | -0.075695 | 122.8923 | 122.8486 | 0.22227 | 0.036649 | -0.40427 | 123.0761 | 122.7588 | 123.1706 | 122.7004 | -122.8285 | 122.9986 | 123.111 | 122.6701 | 122.8733 | -0.44798
458.7344 | 123.1476 | -122.8821 | 0.27008 | 1.4211e-13 | -0.014491 | -0.00028411 | 0.062913 | -0.010063 | 0.059881 | -0.0096144 | 0.0085562 | 0.0087813 | -0.0053883 | 0.031716 | 0.0073689 | -122.2556 | -0.13595 | -122.8162 | 0.23069 | -0.086641 | 0.3068 | -122.5905 | 0.060571 | 0.027831 | 0.01233 | 0.15318 | 0.26553 | -0.17539 | -0.2191 | 0.29158 | -0.039396 | 0.62644 | 0.065873 | -0.22571 | -0.35672 | 0.036715 | 122.663 | -0.1169 | 122.9427 | 122.8944 | 0.23143 | -0.004551 | -0.44547 | 123.1128 | 122.7954 | 123.1889 | 122.7461 | -122.8606 | 123.0353 | 123.1476 | 122.7067 | 122.9099 | -0.48918
460.5 | 123.2025 | -122.8455 | 0.25635 | 1.4211e-13 | -0.014491 | -0.00028411 | 0.062699 | -0.010063 | 0.059881 | 0.013277 | 0.0083426 | 0.0081403 | -0.0051745 | 0.031502 | 0.0071553 | -122.2465 | -0.14053 | -122.8162 | 0.23069 | -0.082062 | 0.32969 | -122.5859 | 0.06515 | 0.018674 | 0.01233 | 0.15318 | 0.26095 | -0.17997 | -0.20536 | 0.25954 | -0.025663 | 0.59897 | 0.029252 | -0.23029 | -0.33841 | 0.073341 | 122.6401 | -0.10316 | 122.9106 | 122.8578 | 0.21769 | 0.004603 | -0.43632 | 123.0761 | 122.7634 | 123.1751 | 122.7049 | -122.8423 | 122.9986 | 123.1064 | 122.6655 | 122.8641 | -0.46171
462.1719 | 123.1155 | -122.8775 | 0.26093 | 1.4211e-13 | -0.014278 | -0.00071151 | 0.062913 | -0.010277 | 0.060095 | 0.0056466 | 0.0085562 | 0.0085677 | -0.0051745 | 0.031929 | 0.0069417 | -122.2465 | -0.13595 | -122.8071 | 0.23526 | -0.082062 | 0.3709 | -122.5813 | 0.060571 | 0.023253 | -0.001407 | 0.15776 | 0.26553 | -0.17081 | -0.22367 | 0.29616 | -0.025662 | 0.63102 | 0.070452 | -0.22571 | -0.34299 | 0.10997 | 122.6538 | -0.10316 | 122.9381 | 122.8761 | 0.22227 | 0.004605 | -0.43174 | 123.1128 | 122.7954 | 123.2484 | 122.7416 | -122.8423 | 123.0353 | 123.143 | 122.7067 | 122.9008 | -0.4846
463.9062 | 123.2162 | -122.8363 | 0.2243 | 1.4211e-13 | -0.014705 | -0.00071151 | 0.063126 | -0.010063 | 0.059667 | -0.0096144 | 0.0085562 | 0.0083539 | -0.0053883 | 0.031929 | 0.0071553 | -122.2419 | -0.13595 | -122.8071 | 0.23069 | -0.082062 | 0.27932 | -122.5722 | 0.06515 | 0.018674 | 0.007751 | 0.15776 | 0.26553 | -0.17539 | -0.2191 | 0.26412 | 0.006381 | 0.5944 | 0.029254 | -0.23487 | -0.30637 | 0.05502 | 122.6172 | -0.06654 | 122.9015 | 122.8441 | 0.22685 | 0.041226 | -0.3997 | 123.067 | 122.7542 | 123.1156 | 122.7004 | -122.7965 | 122.9941 | 123.1018 | 122.6609 | 122.855 | -0.4434
465.6562 | 123.1979 | -122.8409 | 0.23346 | 1.4211e-13 | -0.014064 | -0.00071151 | 0.063126 | -0.010063 | 0.059881 | 0.0056466 | 0.0085562 | 0.0085677 | -0.0051745 | 0.031929 | 0.0071553 | -122.2465 | -0.13595 | -122.8071 | 0.22153 | -0.082062 | 0.30222 | -122.5813 | 0.060571 | 0.014095 | -0.001407 | 0.16234 | 0.27011 | -0.17081 | -0.22367 | 0.25954 | -0.011931 | 0.59439 | 0.033831 | -0.22571 | -0.31552 | 0.068758 | 122.6172 | -0.071117 | 122.9015 | 122.8395 | 0.22227 | 0.036649 | -0.40427 | 123.0624 | 122.7588 | 123.1431 | 122.7049 | -122.8148 | 123.0032 | 123.111 | 122.6701 | 122.855 | -0.45713
467.3906 | 123.1979 | -122.8683 | 0.24261 | 1.4211e-13 | -0.014278 | -0.00028411 | 0.062699 | -0.010277 | 0.059881 | 0.0056466 | 0.0085562 | 0.0085677 | -0.0053883 | 0.031929 | 0.0069417 | -122.2465 | -0.13595 | -122.8025 | 0.23526 | -0.086641 | 0.27017 | -122.5768 | 0.060571 | 0.018674 | 0.007751 | 0.15318 | 0.27011 | -0.17997 | -0.2191 | 0.29158 | -0.007352 | 0.62186 | 0.065875 | -0.22571 | -0.32926 | 0.027552 | 122.6493 | -0.08943 | 122.9289 | 122.8761 | 0.22685 | 0.027493 | -0.42259 | 123.1036 | 122.7817 | 123.1385 | 122.7324 | -122.8194 | 123.0215 | 123.1385 | 122.6884 | 122.887 | -0.46171
469.125 | 123.2117 | -122.8226 | 0.24261 | 1.4211e-13 | -0.014491 | -7.051e-05 | 0.062913 | -0.010063 | 0.060095 | 0.0056466 | 0.0085562 | 0.0087813 | -0.0053883 | 0.031716 | 0.0071553 | -122.2465 | -0.13595 | -122.8025 | 0.22611 | -0.082062 | 0.30222 | -122.5722 | 0.060571 | 0.018674 | 0.003172 | 0.15776 | 0.27469 | -0.17539 | -0.22367 | 0.25039 | -0.016509 | 0.57608 | 0.020099 | -0.23029 | -0.32468 | 0.059602 | 122.5989 | -0.084851 | 122.8831 | 122.8257 | 0.22685 | 0.032072 | -0.41801 | 123.0487 | 122.7405 | 123.1248 | 122.6866 | -122.8148 | 122.9803 | 123.0973 | 122.6472 | 122.8412 | -0.46629
470.7969 | 123.1155 | -122.8546 | 0.26093 | 1.4211e-13 | -0.014491 | -0.00028411 | 0.063126 | -0.010277 | 0.059881 | 0.013277 | 0.0083426 | 0.0085677 | -0.0049609 | 0.031716 | 0.0073689 | -122.2465 | -0.13137 | -122.8025 | 0.23069 | -0.082062 | 0.30222 | -122.563 | 0.060571 | 0.023253 | 0.003172 | 0.16234 | 0.27469 | -0.16624 | -0.20994 | 0.29159 | -0.03024 | 0.60813 | 0.052142 | -0.23945 | -0.34299 | 0.041292 | 122.6447 | -0.098583 | 122.9152 | 122.8578 | 0.21311 | 0.013762 | -0.42716 | 123.0853 | 122.7726 | 123.1568 | 122.7232 | -122.824 | 123.017 | 123.1293 | 122.6884 | 122.8779 | -0.47086
472.5469 | 123.1064 | -122.8317 | 0.27924 | 1.4211e-13 | -0.014278 | -7.051e-05 | 0.062913 | -0.010063 | 0.060095 | -0.0019839 | 0.0085562 | 0.0081403 | -0.0051745 | 0.031929 | 0.0071553 | -122.2236 | -0.14053 | -122.7842 | 0.25358 | -0.077483 | 0.40295 | -122.5493 | 0.06515 | 0.027831 | 0.007751 | 0.15776 | 0.26095 | -0.17539 | -0.22367 | 0.28244 | -0.025659 | 0.60813 | 0.047567 | -0.23487 | -0.35672 | 0.12371 | 122.6081 | -0.12147 | 122.8969 | 122.8395 | 0.23142 | -0.018285 | -0.45463 | 123.0853 | 122.7542 | 123.2347 | 122.6912 | -122.8285 | 122.9895 | 123.0927 | 122.6563 | 122.8596 | -0.50291
474.2188 | 123.0881 | -122.8226 | 0.29755 | 1.4211e-13 | -0.014278 | -0.00028411 | 0.062699 | -0.010063 | 0.059881 | 0.0056466 | 0.0083426 | 0.0083539 | -0.0047473 | 0.032143 | 0.0071553 | -122.219 | -0.13137 | -122.775 | 0.25358 | -0.086641 | 0.36174 | -122.5493 | 0.069728 | 0.023253 | 0.003172 | 0.15776 | 0.26553 | -0.17539 | -0.20994 | 0.27328 | -0.043969 | 0.60356 | 0.047569 | -0.22571 | -0.38419 | 0.064193 | 122.6126 | -0.13978 | 122.8923 | 122.8257 | 0.21311 | -0.032016 | -0.47294 | 123.0761 | 122.7359 | 123.1843 | 122.6912 | -122.8468 | 122.9803 | 123.0881 | 122.6472 | 122.8458 | -0.50748
475.9688 | 123.1659 | -122.7859 | 0.28381 | 1.4211e-13 | -0.014278 | -0.00049791 | 0.063126 | -0.0098499 | 0.059881 | -0.0019839 | 0.0085562 | 0.0081403 | -0.0051745 | 0.032143 | 0.0069417 | -122.2144 | -0.13137 | -122.7658 | 0.26273 | -0.077483 | 0.38921 | -122.5493 | 0.060571 | 0.023253 | 0.007751 | 0.14861 | 0.26553 | -0.17539 | -0.2191 | 0.23666 | -0.021079 | 0.57151 | 0.020105 | -0.21656 | -0.3613 | 0.1054 | 122.5669 | -0.13521 | 122.8465 | 122.7937 | 0.22685 | -0.018283 | -0.45921 | 123.0487 | 122.7085 | 123.1752 | 122.6546 | -122.8331 | 122.9346 | 123.0515 | 122.6106 | 122.8092 | -0.50291
477.6562 | 123.111 | -122.8455 | 0.31128 | 1.4211e-13 | -0.014491 | -7.051e-05 | 0.062913 | -0.010063 | 0.060308 | 0.0056466 | 0.0087698 | 0.0081403 | -0.0049609 | 0.032357 | 0.0071553 | -122.219 | -0.14053 | -122.7704 | 0.26273 | -0.072904 | 0.38921 | -122.5539 | 0.069728 | 0.018674 | 0.007751 | 0.16692 | 0.26095 | -0.17539 | -0.21452 | 0.29159 | -0.048545 | 0.62644 | 0.075035 | -0.21656 | -0.38418 | 0.077932 | 122.6309 | -0.14436 | 122.9152 | 122.8532 | 0.22227 | -0.050328 | -0.48667 | 123.1082 | 122.7726 | 123.2347 | 122.7049 | -122.8651 | 123.0124 | 123.1064 | 122.6701 | 122.8641 | -0.5258
479.4062 | 123.1705 | -122.8088 | 0.27466 | 1.4211e-13 | -0.014278 | -0.00049791 | 0.063126 | -0.010277 | 0.060095 | 0.0056466 | 0.0085562 | 0.0083539 | -0.0051745 | 0.032143 | 0.0071553 | -122.2099 | -0.14053 | -122.7658 | 0.26273 | -0.072904 | 0.39379 | -122.5493 | 0.069728 | 0.023253 | 0.007751 | 0.15776 | 0.26553 | -0.16624 | -0.21452 | 0.25955 | -0.011924 | 0.59898 | 0.042993 | -0.21656 | -0.34756 | 0.11913 | 122.5943 | -0.11689 | 122.8786 | 122.8166 | 0.22227 | -0.009128 | -0.44089 | 123.0716 | 122.7359 | 123.2026 | 122.6683 | -122.8239 | 122.9666 | 123.0744 | 122.6426 | 122.8321 | -0.48917
481.1562 | 123.1934 | -122.8043 | 0.2655 | 1.4211e-13 | -0.014491 | -0.00028411 | 0.063126 | -0.010063 | 0.060095 | -0.0019839 | 0.0087698 | 0.0083539 | -0.0051745 | 0.031929 | 0.0069417 | -122.2099 | -0.13595 | -122.7613 | 0.26273 | -0.072904 | 0.41668 | -122.5401 | 0.069728 | 0.018674 | 0.007751 | 0.16234 | 0.26095 | -0.16624 | -0.20994 | 0.26413 | -0.002769 | 0.5944 | 0.042993 | -0.22114 | -0.33841 | 0.15118 | 122.5943 | -0.10316 | 122.874 | 122.812 | 0.21769 | -0.004552 | -0.43174 | 123.067 | 122.7314 | 123.2209 | 122.6683 | -122.8056 | 122.9666 | 123.0652 | 122.638 | 122.8229 | -0.47544
482.9062 | 123.1338 | -122.7859 | 0.27924 | 1.4211e-13 | -0.014491 | -0.00092531 | 0.062699 | -0.010491 | 0.059667 | 0.013277 | 0.0087698 | 0.0083539 | -0.0049609 | 0.032143 | 0.0071553 | -122.2053 | -0.13595 | -122.7567 | 0.26273 | -0.072904 | 0.35258 | -122.531 | 0.060571 | 0.023253 | 0.003172 | 0.15776 | 0.26553 | -0.17081 | -0.21452 | 0.25498 | -0.016502 | 0.58067 | 0.029261 | -0.22572 | -0.35214 | 0.073346 | 122.5714 | -0.12147 | 122.8465 | 122.7891 | 0.21769 | -0.013706 | -0.45005 | 123.0487 | 122.713 | 123.1385 | 122.65 | -122.8102 | 122.9437 | 123.0515 | 122.6151 | 122.8092 | -0.49375
484.5781 | 123.1934 | -122.7814 | 0.27924 | 1.4211e-13 | -0.014491 | -0.00028411 | 0.062913 | -0.010063 | 0.059881 | 0.0056466 | 0.0083426 | 0.0083539 | -0.0051745 | 0.032143 | 0.0071553 | -122.1961 | -0.14053 | -122.7567 | 0.26273 | -0.077483 | 0.39837 | -122.5264 | 0.06515 | 0.023253 | 0.007751 | 0.15776 | 0.26553 | -0.17081 | -0.2191 | 0.25498 | -0.016502 | 0.58525 | 0.024683 | -0.23029 | -0.35672 | 0.11913 | 122.5623 | -0.12147 | 122.8465 | 122.7891 | 0.22685 | -0.013706 | -0.45005 | 123.0441 | 122.7039 | 123.1797 | 122.6408 | -122.8056 | 122.9391 | 123.0469 | 122.6106 | 122.8046 | -0.49833
486.3125 | 123.0743 | -122.8226 | 0.27924 | 1.4211e-13 | -0.014705 | -0.00028411 | 0.062699 | -0.010063 | 0.060095 | 0.0056466 | 0.0085562 | 0.0083539 | -0.0051745 | 0.031929 | 0.0071553 | -122.2053 | -0.13137 | -122.7521 | 0.26273 | -0.072904 | 0.42584 | -122.531 | 0.069728 | 0.018674 | 0.007751 | 0.15776 | 0.26553 | -0.16624 | -0.2191 | 0.2916 | -0.016502 | 0.61729 | 0.07046 | -0.22114 | -0.35214 | 0.1466 | 122.6035 | -0.12147 | 122.8923 | 122.8303 | 0.22685 | -0.013706 | -0.44547 | 123.0853 | 122.7497 | 123.2484 | 122.6912 | -122.8102 | 122.9803 | 123.0881 | 122.6563 | 122.8412 | -0.49833
488.0625 | 123.1659 | -122.7722 | 0.28381 | 1.4211e-13 | -0.014064 | -0.00071151 | 0.062699 | -0.010277 | 0.059881 | -0.0019839 | 0.0085562 | 0.0085677 | -0.0051745 | 0.03257 | 0.0071553 | -122.2007 | -0.13595 | -122.7521 | 0.26273 | -0.077483 | 0.39837 | -122.5401 | 0.060571 | 0.014095 | 0.007751 | 0.15776 | 0.26095 | -0.17539 | -0.21452 | 0.23209 | -0.021079 | 0.57151 | 0.020106 | -0.21198 | -0.3613 | 0.11456 | 122.5577 | -0.12605 | 122.8328 | 122.78 | 0.22227 | -0.022862 | -0.45921 | 123.035 | 122.6947 | 123.1706 | 122.6363 | -122.8239 | 122.93 | 123.0332 | 122.5968 | 122.7863 | -0.49833
489.7344 | 123.2162 | -122.8226 | 0.27008 | 1.4211e-13 | -0.014491 | -0.00049791 | 0.063126 | -0.010277 | 0.059667 | 0.0056466 | 0.0085562 | 0.0085677 | -0.0051745 | 0.032143 | 0.0071553 | -122.2053 | -0.14053 | -122.7521 | 0.25358 | -0.077483 | 0.40753 | -122.5539 | 0.060571 | 0.014095 | 0.007751 | 0.15318 | 0.25637 | -0.17539 | -0.20994 | 0.2687 | -0.016504 | 0.61729 | 0.07046 | -0.19824 | -0.34756 | 0.13744 | 122.6126 | -0.1169 | 122.8831 | 122.8303 | 0.21769 | -0.013709 | -0.44547 | 123.0761 | 122.7451 | 123.2301 | 122.682 | -122.8239 | 122.9758 | 123.0789 | 122.6472 | 122.8367 | -0.48002
491.4688 | 123.1979 | -122.7997 | 0.24261 | 1.4211e-13 | -0.014705 | -0.00049791 | 0.062699 | -0.010277 | 0.059881 | 0.0056466 | 0.0087698 | 0.0083539 | -0.0051745 | 0.032143 | 0.0071553 | -122.2099 | -0.13595 | -122.7613 | 0.249 | -0.077483 | 0.37548 | -122.5447 | 0.060571 | 0.018674 | 0.007751 | 0.16234 | 0.27011 | -0.16624 | -0.21452 | 0.25497 | 0.006383 | 0.58982 | 0.038416 | -0.21656 | -0.3201 | 0.13286 | 122.5852 | -0.080273 | 122.8603 | 122.8074 | 0.22227 | 0.027493 | -0.40885 | 123.0487 | 122.7222 | 123.1752 | 122.6637 | -122.7873 | 122.962 | 123.0698 | 122.6334 | 122.8184 | -0.45713
493.2344 | 123.0606 | -122.85 | 0.31128 | 1.4211e-13 | -0.014491 | -7.051e-05 | 0.062913 | -0.0098499 | 0.060095 | -0.0019839 | 0.0085562 | 0.0085677 | -0.0051745 | 0.032143 | 0.0067279 | -122.2144 | -0.14053 | -122.7658 | 0.25358 | -0.086641 | 0.38005 | -122.5447 | 0.06515 | 0.018674 | 0.003172 | 0.15776 | 0.25179 | -0.17081 | -0.21452 | 0.30533 | -0.057702 | 0.6356 | 0.084192 | -0.22114 | -0.39792 | 0.068774 | 122.6355 | -0.15351 | 122.9152 | 122.8532 | 0.21769 | -0.059485 | -0.48209 | 123.1036 | 122.7634 | 123.2301 | 122.7095 | -122.856 | 123.0078 | 123.1018 | 122.6792 | 122.8687 | -0.5258
494.9844 | 123.0698 | -122.8317 | 0.27466 | 1.4211e-13 | -0.014705 | -0.00028411 | 0.062699 | -0.010277 | 0.059667 | 0.013277 | 0.0089834 | 0.0081403 | -0.0051745 | 0.031929 | 0.0071553 | -122.219 | -0.14511 | -122.775 | 0.23526 | -0.082062 | 0.39379 | -122.5539 | 0.06515 | 0.023253 | 0.01233 | 0.15318 | 0.26553 | -0.16624 | -0.2191 | 0.27786 | -0.039395 | 0.61271 | 0.056724 | -0.22113 | -0.35672 | 0.11913 | 122.6126 | -0.12147 | 122.8969 | 122.8441 | 0.23143 | -0.009128 | -0.44089 | 123.067 | 122.7497 | 123.2255 | 122.6866 | -122.8285 | 122.9849 | 123.0973 | 122.6655 | 122.855 | -0.49375
496.6562 | 123.0606 | -122.8638 | 0.27924 | 1.4211e-13 | -0.014491 | -0.00049791 | 0.062913 | -0.0098499 | 0.060095 | 0.013277 | 0.0085562 | 0.0083539 | -0.0053883 | 0.032143 | 0.0069417 | -122.219 | -0.14053 | -122.7658 | 0.23526 | -0.082062 | 0.33885 | -122.5539 | 0.060571 | 0.018674 | 0.016908 | 0.14861 | 0.25637 | -0.17081 | -0.21452 | 0.3099 | -0.043973 | 0.64475 | 0.097925 | -0.21198 | -0.3613 | 0.05961 | 122.6493 | -0.13063 | 122.9243 | 122.8807 | 0.23142 | -0.022864 | -0.45005 | 123.099 | 122.7817 | 123.2026 | 122.7232 | -122.8331 | 123.0124 | 123.1201 | 122.693 | 122.8824 | -0.49375
498.4062 | 123.1979 | -122.8271 | 0.24719 | 1.4211e-13 | -0.014705 | -0.00071151 | 0.062699 | -0.010063 | 0.060095 | 0.0056466 | 0.0083426 | 0.0083539 | -0.0053883 | 0.032143 | 0.0069417 | -122.2282 | -0.14053 | -122.7704 | 0.23984 | -0.086641 | 0.36632 | -122.5676 | 0.060571 | 0.023253 | 0.01233 | 0.15776 | 0.26095 | -0.16624 | -0.2191 | 0.25954 | -0.00735 | 0.59897 | 0.056724 | -0.20282 | -0.33383 | 0.11913 | 122.6081 | -0.089428 | 122.8877 | 122.8395 | 0.23143 | 0.013759 | -0.41343 | 123.067 | 122.7405 | 123.1935 | 122.6866 | -122.8148 | 122.9849 | 123.0881 | 122.6609 | 122.8504 | -0.46629
500.1562 | 123.0743 | -122.8546 | 0.27924 | 1.4211e-13 | -0.014919 | -0.00049791 | 0.062699 | -0.010063 | 0.059881 | 0.0056466 | 0.0083426 | 0.0081403 | -0.0053883 | 0.031929 | 0.0071553 | -122.2282 | -0.12679 | -122.7475 | 0.23526 | -0.077483 | 0.39837 | -122.5676 | 0.069728 | 0.018674 | 0.003172 | 0.15776 | 0.26095 | -0.17539 | -0.2191 | 0.28701 | -0.043973 | 0.62644 | 0.10708 | -0.17993 | -0.35672 | 0.11913 | 122.6355 | -0.12147 | 122.9243 | 122.8578 | 0.22227 | -0.018285 | -0.45463 | 123.0899 | 122.7771 | 123.253 | 122.7278 | -122.8468 | 123.0124 | 123.1156 | 122.6792 | 122.8733 | -0.49833
501.8281 | 123.1201 | -122.8363 | 0.27924 | 1.4211e-13 | -0.014278 | -0.00028411 | 0.062699 | -0.010277 | 0.059881 | 0.013277 | 0.0085562 | 0.0081403 | -0.0053883 | 0.031929 | 0.0069417 | -122.2099 | -0.13595 | -122.743 | 0.24442 | -0.077483 | 0.35258 | -122.5493 | 0.060571 | 0.018674 | 0.007751 | 0.15776 | 0.26553 | -0.17081 | -0.2191 | 0.28701 | -0.034816 | 0.62644 | 0.09335 | -0.19366 | -0.35672 | 0.073346 | 122.6172 | -0.12147 | 122.8969 | 122.8441 | 0.22685 | -0.013706 | -0.45005 | 123.0807 | 122.7588 | 123.1889 | 122.7004 | -122.8285 | 122.9941 | 123.1018 | 122.6655 | 122.855 | -0.49833
503.5781 | 123.1155 | -122.8317 | 0.28381 | 1.4211e-13 | -0.014705 | -0.00049791 | 0.063126 | -0.010063 | 0.059881 | -0.0019839 | 0.0083426 | 0.0083539 | -0.0053883 | 0.032357 | 0.0069417 | -122.2282 | -0.14053 | -122.7475 | 0.23069 | -0.09122 | 0.35716 | -122.5584 | 0.060571 | 0.023253 | 0.007751 | 0.16234 | 0.26095 | -0.17081 | -0.21452 | 0.27328 | -0.053128 | 0.60355 | 0.084194 | -0.18909 | -0.37503 | 0.073347 | 122.6172 | -0.12147 | 122.8923 | 122.8395 | 0.22227 | -0.022862 | -0.45463 | 123.0624 | 122.7405 | 123.1889 | 122.6912 | -122.8423 | 122.9941 | 123.0927 | 122.6609 | 122.855 | -0.49833
505.3281 | 123.0743 | -122.8592 | 0.28381 | 1.4211e-13 | -0.014705 | -0.00071151 | 0.062699 | -0.010277 | 0.060095 | 0.013277 | 0.0083426 | 0.0081403 | -0.0051745 | 0.032143 | 0.0067279 | -122.2236 | -0.14053 | -122.7475 | 0.23526 | -0.082062 | 0.348 | -122.5584 | 0.06515 | 0.018674 | -0.001407 | 0.15318 | 0.26095 | -0.17539 | -0.20994 | 0.30074 | -0.04855 | 0.6356 | 0.11166 | -0.18909 | -0.36587 | 0.06419 | 122.6493 | -0.13063 | 122.9243 | 122.8578 | 0.20853 | -0.022862 | -0.45921 | 123.0945 | 122.7771 | 123.2072 | 122.7187 | -122.8423 | 123.0124 | 123.1201 | 122.6838 | 122.8779 | -0.49375
507.0625 | 123.1567 | -122.818 | 0.2243 | 1.4211e-13 | -0.014705 | -0.00092531 | 0.062699 | -0.010491 | 0.059881 | 0.0056466 | 0.0083426 | 0.0081403 | -0.0051745 | 0.031929 | 0.0071553 | -122.219 | -0.13595 | -122.7567 | 0.23069 | -0.086641 | 0.33885 | -122.563 | 0.055992 | 0.018674 | 0.007751 | 0.15776 | 0.26095 | -0.17997 | -0.21452 | 0.25497 | 0.006381 | 0.59898 | 0.061304 | -0.19366 | -0.31095 | 0.11454 | 122.6035 | -0.06654 | 122.874 | 122.8257 | 0.22227 | 0.036647 | -0.40428 | 123.0487 | 122.7314 | 123.1568 | 122.682 | -122.7873 | 122.9758 | 123.0789 | 122.638 | 122.8367 | -0.43882
508.75 | 123.1201 | -122.8363 | 0.25635 | 1.4211e-13 | -0.014491 | -0.00049791 | 0.062699 | -0.010063 | 0.059881 | 0.0056466 | 0.0089834 | 0.0081403 | -0.0051745 | 0.032143 | 0.0069417 | -122.2282 | -0.13595 | -122.7613 | 0.22611 | -0.086641 | 0.29306 | -122.563 | 0.06515 | 0.027831 | 0.007751 | 0.15776 | 0.26553 | -0.17539 | -0.21452 | 0.27328 | -0.030242 | 0.60813 | 0.075037 | -0.19824 | -0.34299 | 0.036712 | 122.6218 | -0.098584 | 122.9015 | 122.8441 | 0.22227 | 0.009182 | -0.43174 | 123.0624 | 122.7497 | 123.1294 | 122.7004 | -122.8194 | 122.9941 | 123.1018 | 122.6609 | 122.8641 | -0.47086
510.5 | 123.143 | -122.8592 | 0.24261 | 1.4211e-13 | -0.014491 | -0.00028411 | 0.062699 | -0.010277 | 0.059881 | -0.0019839 | 0.0085562 | 0.0083539 | -0.0056019 | 0.031929 | 0.0069417 | -122.2282 | -0.14053 | -122.7613 | 0.22611 | -0.082062 | 0.31595 | -122.5676 | 0.06515 | 0.018674 | 0.003172 | 0.14861 | 0.26095 | -0.16624 | -0.21452 | 0.29159 | -0.016509 | 0.63102 | 0.097925 | -0.19366 | -0.32468 | 0.073338 | 122.6447 | -0.094008 | 122.9243 | 122.8624 | 0.21769 | 0.018336 | -0.40885 | 123.0853 | 122.7771 | 123.1751 | 122.7187 | -122.8102 | 123.0078 | 123.1201 | 122.693 | 122.8779 | -0.45713
512.2344 | 123.1796 | -122.8226 | 0.21057 | 1.4211e-13 | -0.014491 | -0.00028411 | 0.063126 | -0.010277 | 0.059454 | 0.013277 | 0.0085562 | 0.0085677 | -0.0051745 | 0.032143 | 0.0069417 | -122.2236 | -0.13595 | -122.7658 | 0.23069 | -0.09122 | 0.32511 | -122.5676 | 0.06515 | 0.023253 | 0.01233 | 0.15318 | 0.26553 | -0.17539 | -0.2191 | 0.25497 | 0.020114 | 0.59898 | 0.056726 | -0.19824 | -0.30179 | 0.11454 | 122.6035 | -0.057386 | 122.8877 | 122.8349 | 0.23143 | 0.054959 | -0.38596 | 123.0533 | 122.7314 | 123.1477 | 122.6866 | -122.7782 | 122.9758 | 123.0881 | 122.6472 | 122.8458 | -0.42967
513.9844 | 123.0515 | -122.85 | 0.2655 | 1.4211e-13 | -0.014491 | -0.00028411 | 0.062699 | -0.010491 | 0.060095 | -0.0019839 | 0.0083426 | 0.0085677 | -0.0053883 | 0.032143 | 0.0065143 | -122.2236 | -0.14053 | -122.7613 | 0.23069 | -0.086641 | 0.30222 | -122.5584 | 0.060571 | 0.027831 | -0.005985 | 0.15776 | 0.26095 | -0.16624 | -0.21452 | 0.29159 | -0.034818 | 0.62644 | 0.08877 | -0.20282 | -0.35214 | 0.036714 | 122.6355 | -0.10774 | 122.9106 | 122.8441 | 0.20853 | -0.004552 | -0.43174 | 123.0807 | 122.7634 | 123.1523 | 122.7095 | -122.8239 | 123.0078 | 123.111 | 122.6838 | 122.8779 | -0.48002
515.6719 | 123.1064 | -122.8226 | 0.25177 | 1.4211e-13 | -0.014919 | -0.00071151 | 0.062485 | -0.0096363 | 0.060095 | 0.013277 | 0.0085562 | 0.0085677 | -0.0049609 | 0.032357 | 0.0065143 | -122.2144 | -0.13595 | -122.7521 | 0.23526 | -0.082062 | 0.35716 | -122.5584 | 0.060571 | 0.023253 | 0.003172 | 0.15776 | 0.25637 | -0.17081 | -0.21452 | 0.26412 | -0.016507 | 0.60813 | 0.07046 | -0.19366 | -0.33383 | 0.10539 | 122.6081 | -0.094006 | 122.8831 | 122.8257 | 0.21769 | 0.004602 | -0.42258 | 123.0578 | 122.7405 | 123.1797 | 122.6866 | -122.8102 | 122.9803 | 123.0789 | 122.6518 | 122.8458 | -0.46629
517.4062 | 123.0515 | -122.85 | 0.25177 | 1.4211e-13 | -0.014705 | -0.00049791 | 0.062699 | -0.010277 | 0.059667 | 0.013277 | 0.0083426 | 0.0087813 | -0.0053883 | 0.032357 | 0.0067279 | -122.2236 | -0.14511 | -122.7658 | 0.23069 | -0.086641 | 0.29764 | -122.5584 | 0.060571 | 0.018674 | 0.003172 | 0.16234 | 0.27011 | -0.17081 | -0.2191 | 0.29159 | -0.021085 | 0.62644 | 0.084192 | -0.2074 | -0.33841 | 0.045868 | 122.6309 | -0.089428 | 122.9106 | 122.8532 | 0.22227 | 0.018338 | -0.42258 | 123.0807 | 122.7634 | 123.1477 | 122.7049 | -122.8102 | 123.0124 | 123.1201 | 122.6792 | 122.8687 | -0.47086
519.1406 | 123.0743 | -122.8409 | 0.25177 | 1.4211e-13 | -0.014705 | -0.00028411 | 0.063126 | -0.010491 | 0.059881 | -0.0019839 | 0.0083426 | 0.0085677 | -0.0053883 | 0.032143 | 0.0069417 | -122.2282 | -0.14053 | -122.7704 | 0.22153 | -0.082062 | 0.36632 | -122.563 | 0.06515 | 0.023253 | 0.007751 | 0.15318 | 0.27011 | -0.17997 | -0.21452 | 0.27786 | -0.030242 | 0.61271 | 0.070457 | -0.2074 | -0.33383 | 0.11455 | 122.6264 | -0.098585 | 122.906 | 122.8486 | 0.22227 | 0.018338 | -0.43174 | 123.0624 | 122.7588 | 123.2072 | 122.7004 | -122.8148 | 122.9941 | 123.111 | 122.6609 | 122.8641 | -0.46629
520.8125 | 123.0469 | -122.8409 | 0.25177 | 1.4211e-13 | -0.014491 | -0.00028411 | 0.062699 | -0.010277 | 0.059454 | 0.013277 | 0.0083426 | 0.0081403 | -0.0051745 | 0.032357 | 0.0069417 | -122.219 | -0.14053 | -122.7658 | 0.23069 | -0.082062 | 0.37548 | -122.563 | 0.060571 | 0.014095 | 0.003172 | 0.16234 | 0.27011 | -0.17539 | -0.21452 | 0.27786 | -0.021085 | 0.62186 | 0.075036 | -0.20282 | -0.33383 | 0.12371 | 122.6264 | -0.089428 | 122.9015 | 122.8441 | 0.21769 | 0.018338 | -0.42716 | 123.0716 | 122.7588 | 123.2164 | 122.7004 | -122.8148 | 123.0032 | 123.111 | 122.6655 | 122.855 | -0.46629
522.5625 | 123.1705 | -122.8271 | 0.21057 | 1.4211e-13 | -0.014705 | -0.00028411 | 0.062485 | -0.010063 | 0.059881 | 0.0056466 | 0.0083426 | 0.0085677 | -0.0053883 | 0.032143 | 0.0067279 | -122.2236 | -0.14053 | -122.775 | 0.23526 | -0.082062 | 0.31595 | -122.5584 | 0.060571 | 0.018674 | 0.007751 | 0.15318 | 0.27011 | -0.17539 | -0.20994 | 0.2687 | 0.024692 | 0.60355 | 0.052146 | -0.21655 | -0.29263 | 0.10538 | 122.6172 | -0.057386 | 122.8877 | 122.8349 | 0.21769 | 0.059537 | -0.38596 | 123.0624 | 122.7451 | 123.1431 | 122.6866 | -122.769 | 122.9803 | 123.0973 | 122.6518 | 122.8458 | -0.42051
524.3125 | 123.0652 | -122.8638 | 0.25635 | 1.4211e-13 | -0.015132 | -7.051e-05 | 0.062913 | -0.010491 | 0.059881 | -0.0096144 | 0.0085562 | 0.0083539 | -0.0051745 | 0.032357 | 0.0067279 | -122.2282 | -0.14053 | -122.775 | 0.22611 | -0.082062 | 0.33885 | -122.5722 | 0.06515 | 0.018674 | 0.003172 | 0.15776 | 0.27926 | -0.16624 | -0.22367 | 0.29159 | -0.030242 | 0.6356 | 0.088768 | -0.20282 | -0.33841 | 0.082498 | 122.6401 | -0.098584 | 122.9289 | 122.8669 | 0.22685 | 0.022917 | -0.42258 | 123.0899 | 122.7817 | 123.2026 | 122.7232 | -122.8285 | 123.0215 | 123.143 | 122.6975 | 122.8824 | -0.48002
526 | 123.0652 | -122.8592 | 0.24719 | 1.4211e-13 | -0.014491 | -7.051e-05 | 0.062699 | -0.010277 | 0.059881 | 0.0056466 | 0.0083426 | 0.0083539 | -0.0056019 | 0.031929 | 0.0069417 | -122.2236 | -0.14511 | -122.775 | 0.21695 | -0.086641 | 0.33427 | -122.563 | 0.060571 | 0.018674 | 0.003172 | 0.16234 | 0.27011 | -0.17539 | -0.2191 | 0.29617 | -0.030242 | 0.6356 | 0.08419 | -0.21198 | -0.33383 | 0.087075 | 122.6401 | -0.08485 | 122.9198 | 122.8624 | 0.22227 | 0.022916 | -0.42258 | 123.0761 | 122.7726 | 123.1935 | 122.7141 | -122.8102 | 123.0215 | 123.1293 | 122.6838 | 122.8779 | -0.46629
527.75 | 123.1934 | -122.8134 | 0.2243 | 1.4211e-13 | -0.015132 | -0.00049791 | 0.062913 | -0.010704 | 0.059881 | 0.013277 | 0.0085562 | 0.0081403 | -0.0056019 | 0.032357 | 0.0065143 | -122.2236 | -0.13595 | -122.7704 | 0.21237 | -0.086641 | 0.36174 | -122.5676 | 0.06515 | 0.023253 | 0.01233 | 0.15776 | 0.27011 | -0.17539 | -0.21452 | 0.24581 | -0.011933 | 0.58982 | 0.042992 | -0.20282 | -0.31095 | 0.13743 | 122.5989 | -0.06654 | 122.8786 | 122.8257 | 0.22685 | 0.045804 | -0.3997 | 123.0258 | 122.7268 | 123.1752 | 122.6775 | -122.7919 | 122.9712 | 123.0835 | 122.638 | 122.8367 | -0.43882
529.4844 | 123.1842 | -122.8088 | 0.2243 | 1.4211e-13 | -0.014705 | -0.00049791 | 0.062913 | -0.010277 | 0.059667 | 0.0056466 | 0.0083426 | 0.0085677 | -0.0053883 | 0.032357 | 0.0067279 | -122.2236 | -0.14053 | -122.7842 | 0.20779 | -0.09122 | 0.32969 | -122.5768 | 0.06515 | 0.018674 | 0.007751 | 0.15318 | 0.26095 | -0.16624 | -0.21452 | 0.23208 | -0.016511 | 0.58524 | 0.024679 | -0.2074 | -0.31552 | 0.10539 | 122.5943 | -0.071119 | 122.874 | 122.8166 | 0.22227 | 0.036647 | -0.39054 | 123.0166 | 122.7176 | 123.1385 | 122.6683 | -122.8011 | 122.962 | 123.0698 | 122.6426 | 122.8275 | -0.43882
531.2188 | 123.1659 | -122.8134 | 0.22888 | 1.4211e-13 | -0.014919 | -0.00049791 | 0.062913 | -0.010491 | 0.060095 | -0.0019839 | 0.0083426 | 0.0083539 | -0.0051745 | 0.03257 | 0.0071553 | -122.2373 | -0.14053 | -122.7842 | 0.20779 | -0.086641 | 0.29306 | -122.5768 | 0.069728 | 0.027831 | 0.003172 | 0.15776 | 0.26553 | -0.18455 | -0.2191 | 0.23665 | -0.021089 | 0.57609 | 0.029257 | -0.2074 | -0.31552 | 0.064178 | 122.5943 | -0.071118 | 122.8831 | 122.8166 | 0.22227 | 0.036648 | -0.41343 | 123.0212 | 122.7268 | 123.1065 | 122.6729 | -122.8056 | 122.9712 | 123.0789 | 122.6289 | 122.8412 | -0.44798
532.9844 | 123.1476 | -122.8134 | 0.22888 | 1.4211e-13 | -0.014919 | -0.00049791 | 0.062699 | -0.010277 | 0.060095 | -0.0019839 | 0.0079152 | 0.0085677 | -0.0056019 | 0.032357 | 0.0067279 | -122.219 | -0.14511 | -122.775 | 0.21237 | -0.09122 | 0.35716 | -122.5768 | 0.069728 | 0.023253 | 0.01233 | 0.14861 | 0.26553 | -0.17081 | -0.21452 | 0.23665 | -0.016511 | 0.5944 | 0.038414 | -0.19824 | -0.3201 | 0.12828 | 122.5989 | -0.080275 | 122.8831 | 122.8257 | 0.22685 | 0.036648 | -0.3997 | 123.0258 | 122.7222 | 123.1706 | 122.6683 | -122.8056 | 122.962 | 123.0789 | 122.6426 | 122.8367 | -0.4434
534.7188 | 123.2208 | -122.8134 | 0.2243 | 1.4211e-13 | -0.014491 | -0.00071151 | 0.062913 | -0.010277 | 0.060095 | -0.0019839 | 0.0083426 | 0.0079267 | -0.0051745 | 0.032357 | 0.0067279 | -122.2282 | -0.14053 | -122.7887 | 0.21237 | -0.082062 | 0.32511 | -122.5768 | 0.06515 | 0.018674 | 0.003172 | 0.15776 | 0.26553 | -0.17539 | -0.21452 | 0.23665 | -0.011933 | 0.58524 | 0.024679 | -0.21197 | -0.30637 | 0.10081 | 122.5989 | -0.06654 | 122.8786 | 122.8166 | 0.21769 | 0.041226 | -0.3997 | 123.0258 | 122.7314 | 123.1385 | 122.6729 | -122.8011 | 122.9712 | 123.0789 | 122.638 | 122.8321 | -0.43882
536.3906 | 123.0331 | -122.8592 | 0.2243 | 1.4211e-13 | -0.014919 | -0.00049791 | 0.062699 | -0.010277 | 0.059667 | 0.0056466 | 0.0085562 | 0.0083539 | -0.0056019 | 0.032357 | 0.0069417 | -122.2419 | -0.14053 | -122.7887 | 0.19864 | -0.09122 | 0.3068 | -122.5768 | 0.06515 | 0.027831 | 0.01233 | 0.16692 | 0.26095 | -0.16624 | -0.22367 | 0.28243 | -0.025668 | 0.61728 | 0.070455 | -0.21197 | -0.31552 | 0.082492 | 122.6355 | -0.057383 | 122.9243 | 122.8715 | 0.236 | 0.036647 | -0.39054 | 123.0578 | 122.768 | 123.166 | 122.7187 | -122.8011 | 123.0261 | 123.1201 | 122.693 | 122.887 | -0.44798
538.1406 | 123.0515 | -122.8775 | 0.24261 | 1.4211e-13 | -0.014705 | -0.00049791 | 0.062699 | -0.010277 | 0.060095 | 0.0056466 | 0.0085562 | 0.0081403 | -0.0053883 | 0.032357 | 0.0069417 | -122.2328 | -0.14511 | -122.7887 | 0.21237 | -0.09122 | 0.31595 | -122.5768 | 0.060571 | 0.023253 | 0.003172 | 0.16234 | 0.27926 | -0.17539 | -0.21452 | 0.30074 | -0.030244 | 0.64475 | 0.088765 | -0.21197 | -0.33383 | 0.073338 | 122.663 | -0.080273 | 122.9381 | 122.8807 | 0.21769 | 0.03665 | -0.41801 | 123.0899 | 122.7863 | 123.1935 | 122.7324 | -122.8194 | 123.0398 | 123.1568 | 122.7021 | 122.9008 | -0.45713
539.8125 | 123.0469 | -122.8546 | 0.2243 | 1.4211e-13 | -0.014919 | -0.00049791 | 0.062485 | -0.010063 | 0.059454 | 0.0056466 | 0.0087698 | 0.0083539 | -0.0053883 | 0.032143 | 0.0071553 | -122.2282 | -0.13595 | -122.7933 | 0.21237 | -0.086641 | 0.348 | -122.5768 | 0.069728 | 0.027831 | 0.007751 | 0.15776 | 0.27011 | -0.17081 | -0.21452 | 0.27785 | -0.011933 | 0.62644 | 0.061299 | -0.21655 | -0.31095 | 0.1237 | 122.6401 | -0.06654 | 122.9243 | 122.8624 | 0.22227 | 0.045804 | -0.39512 | 123.067 | 122.768 | 123.2026 | 122.7187 | -122.8011 | 123.0124 | 123.1247 | 122.6838 | 122.8824 | -0.43882
541.5469 | 123.0743 | -122.8546 | 0.2243 | 1.4211e-13 | -0.014919 | -0.00071151 | 0.062699 | -0.010277 | 0.059881 | 0.0056466 | 0.0083426 | 0.0083539 | -0.0056019 | 0.032357 | 0.0069417 | -122.2328 | -0.13595 | -122.7842 | 0.20779 | -0.086641 | 0.32053 | -122.5768 | 0.06515 | 0.027831 | 0.007751 | 0.16234 | 0.26553 | -0.17539 | -0.20994 | 0.27785 | -0.016511 | 0.62186 | 0.070455 | -0.2074 | -0.31095 | 0.096227 | 122.6447 | -0.061962 | 122.9198 | 122.8624 | 0.21769 | 0.041226 | -0.3997 | 123.0624 | 122.768 | 123.1751 | 122.7187 | -122.8011 | 123.017 | 123.1201 | 122.6792 | 122.8824 | -0.43424
543.3281 | 123.0972 | -122.8546 | 0.21973 | 1.4211e-13 | -0.014491 | -0.00049791 | 0.062699 | -0.010063 | 0.059667 | -0.0019839 | 0.008129 | 0.0081403 | -0.0056019 | 0.03257 | 0.0065143 | -122.2328 | -0.13137 | -122.7842 | 0.21237 | -0.09122 | 0.31595 | -122.5722 | 0.06515 | 0.027831 | 0.003172 | 0.16234 | 0.27469 | -0.17539 | -0.20536 | 0.28243 | -0.007356 | 0.62186 | 0.070455 | -0.21198 | -0.31095 | 0.096226 | 122.6493 | -0.057385 | 122.9198 | 122.8578 | 0.20853 | 0.05496 | -0.39512 | 123.067 | 122.7634 | 123.1706 | 122.7232 | -122.7919 | 123.017 | 123.1293 | 122.6792 | 122.8824 | -0.42509
545.0625 | 123.0881 | -122.8363 | 0.22888 | 1.4211e-13 | -0.014919 | -0.00049791 | 0.062485 | -0.010063 | 0.059454 | -0.0019839 | 0.0085562 | 0.0081403 | -0.0053883 | 0.032998 | 0.0069417 | -122.2236 | -0.13137 | -122.7796 | 0.20779 | -0.086641 | 0.36632 | -122.5584 | 0.06515 | 0.009516 | 0.016908 | 0.15318 | 0.26553 | -0.16624 | -0.20994 | 0.27786 | -0.021089 | 0.61271 | 0.056724 | -0.22113 | -0.31552 | 0.13744 | 122.6264 | -0.075697 | 122.9015 | 122.8532 | 0.22685 | 0.036648 | -0.39512 | 123.0441 | 122.7497 | 123.2026 | 122.7049 | -122.7873 | 122.9895 | 123.1018 | 122.6701 | 122.8458 | -0.43882
546.7969 | 123.1064 | -122.8363 | 0.25177 | 1.4211e-13 | -0.014919 | -0.00049791 | 0.062913 | -0.010918 | 0.060095 | 0.0056466 | 0.0085562 | 0.0081403 | -0.0049609 | 0.032357 | 0.0071553 | -122.2144 | -0.13595 | -122.775 | 0.22153 | -0.082062 | 0.36174 | -122.5584 | 0.060571 | 0.027831 | 0.007751 | 0.15776 | 0.26553 | -0.17081 | -0.20994 | 0.27786 | -0.030242 | 0.62187 | 0.061302 | -0.21655 | -0.33383 | 0.10997 | 122.6264 | -0.094006 | 122.8969 | 122.8441 | 0.21769 | 0.01376 | -0.42258 | 123.0578 | 122.7542 | 123.198 | 122.7004 | -122.8102 | 122.9941 | 123.1018 | 122.6655 | 122.8641 | -0.46171
548.4844 | 123.1888 | -122.7859 | 0.23346 | 1.4211e-13 | -0.014491 | -0.00049791 | 0.062485 | -0.010277 | 0.059881 | 0.0056466 | 0.0085562 | 0.0083539 | -0.0053883 | 0.032357 | 0.0069417 | -122.2236 | -0.13595 | -122.7704 | 0.22611 | -0.09122 | 0.3709 | -122.5584 | 0.060571 | 0.027831 | 0.007751 | 0.16234 | 0.27011 | -0.17081 | -0.2191 | 0.2275 | -0.007353 | 0.56235 | 0.015526 | -0.21198 | -0.32468 | 0.13744 | 122.5669 | -0.071117 | 122.8465 | 122.7937 | 0.22685 | 0.036649 | -0.40427 | 123.0121 | 122.6947 | 123.1568 | 122.65 | -122.7919 | 122.9483 | 123.0561 | 122.6151 | 122.8138 | -0.45255
550.1562 | 123.056 | -122.8546 | 0.24261 | 1.4211e-13 | -0.014491 | -0.00049791 | 0.062913 | -0.010491 | 0.059667 | -0.0019839 | 0.0083426 | 0.0081403 | -0.0053883 | 0.03257 | 0.0069417 | -122.219 | -0.14511 | -122.7842 | 0.20779 | -0.09122 | 0.34342 | -122.563 | 0.06515 | 0.027831 | 0.01233 | 0.16234 | 0.26095 | -0.16624 | -0.21452 | 0.29159 | -0.034822 | 0.6356 | 0.070455 | -0.22113 | -0.33383 | 0.10081 | 122.6401 | -0.080273 | 122.9198 | 122.8669 | 0.22685 | 0.018336 | -0.40885 | 123.0624 | 122.7634 | 123.198 | 122.7095 | -122.8056 | 123.017 | 123.1156 | 122.6884 | 122.8824 | -0.45713
551.8906 | 123.1476 | -122.8043 | 0.21057 | 1.4211e-13 | -0.015346 | -0.00071151 | 0.062485 | -0.010277 | 0.059881 | -0.0019839 | 0.0083426 | 0.0081403 | -0.0056019 | 0.032784 | 0.0069417 | -122.2099 | -0.14053 | -122.7796 | 0.22153 | -0.082062 | 0.348 | -122.5539 | 0.06515 | 0.023253 | 0.007751 | 0.16234 | 0.27011 | -0.17539 | -0.20994 | 0.25039 | 0.010957 | 0.5944 | 0.02468 | -0.22571 | -0.29263 | 0.13743 | 122.5943 | -0.048229 | 122.8694 | 122.812 | 0.21769 | 0.059537 | -0.38596 | 123.0258 | 122.7222 | 123.1523 | 122.6637 | -122.7644 | 122.9666 | 123.0744 | 122.6289 | 122.8275 | -0.42051
553.5781 | 123.0331 | -122.8546 | 0.24261 | 1.4211e-13 | -0.015132 | -0.00049791 | 0.062699 | -0.010491 | 0.060095 | 0.013277 | 0.0083426 | 0.0079267 | -0.0051745 | 0.032784 | 0.0067279 | -122.219 | -0.13595 | -122.775 | 0.22153 | -0.086641 | 0.34342 | -122.5584 | 0.069728 | 0.027831 | 0.01233 | 0.16234 | 0.26553 | -0.17997 | -0.20994 | 0.29617 | -0.021087 | 0.6356 | 0.079612 | -0.21655 | -0.32926 | 0.10081 | 122.6447 | -0.080273 | 122.9243 | 122.8669 | 0.22227 | 0.022915 | -0.42259 | 123.0761 | 122.768 | 123.198 | 122.7187 | -122.8011 | 123.017 | 123.1201 | 122.6746 | 122.8824 | -0.45255
555.3281 | 123.1888 | -122.7859 | 0.22888 | 1.4211e-13 | -0.015132 | -0.00028411 | 0.062485 | -0.010277 | 0.060095 | 0.020908 | 0.0085562 | 0.0081403 | -0.0053883 | 0.03257 | 0.0065143 | -122.2099 | -0.14053 | -122.7704 | 0.22153 | -0.086641 | 0.38921 | -122.563 | 0.069728 | 0.023253 | 0.007751 | 0.16234 | 0.26553 | -0.16166 | -0.22367 | 0.22292 | -0.007354 | 0.57609 | 0.015526 | -0.2074 | -0.31552 | 0.16033 | 122.5623 | -0.06654 | 122.8557 | 122.7937 | 0.23142 | 0.036648 | -0.39054 | 123.0075 | 122.6993 | 123.1752 | 122.6454 | -122.7919 | 122.9483 | 123.0515 | 122.6243 | 122.8092 | -0.45256
557.0781 | 123.143 | -122.8226 | 0.23804 | 1.4211e-13 | -0.014919 | -0.00049791 | 0.062699 | -0.010277 | 0.059667 | -0.0019839 | 0.0083426 | 0.0083539 | -0.0051745 | 0.032357 | 0.0065143 | -122.2144 | -0.14053 | -122.7704 | 0.21695 | -0.086641 | 0.38463 | -122.5539 | 0.06515 | 0.027831 | 0.016908 | 0.15318 | 0.25637 | -0.17081 | -0.20994 | 0.2687 | -0.021087 | 0.60813 | 0.052147 | -0.21656 | -0.32468 | 0.14659 | 122.6126 | -0.084852 | 122.8877 | 122.8395 | 0.22685 | 0.018335 | -0.40885 | 123.0395 | 122.7359 | 123.2072 | 122.682 | -122.7919 | 122.9758 | 123.0789 | 122.6518 | 122.8504 | -0.44797
558.7656 | 123.0835 | -122.8088 | 0.25177 | 1.4211e-13 | -0.014491 | -7.051e-05 | 0.063126 | -0.010491 | 0.059881 | -0.0019839 | 0.0083426 | 0.0083539 | -0.0053883 | 0.032143 | 0.0065143 | -122.2053 | -0.14053 | -122.7704 | 0.20779 | -0.086641 | 0.3709 | -122.5584 | 0.074307 | 0.023253 | 0.01233 | 0.15318 | 0.27011 | -0.17539 | -0.20994 | 0.25039 | -0.043977 | 0.60356 | 0.038414 | -0.21198 | -0.33841 | 0.11913 | 122.5989 | -0.098585 | 122.8831 | 122.8212 | 0.22227 | 0.018338 | -0.42716 | 123.0166 | 122.7222 | 123.1797 | 122.6683 | -122.8102 | 122.962 | 123.0789 | 122.6334 | 122.8321 | -0.46171
560.5156 | 123.1659 | -122.8043 | 0.21515 | 1.4211e-13 | -0.014705 | -0.00049791 | 0.062699 | -0.010277 | 0.059881 | 0.013277 | 0.0085562 | 0.0081403 | -0.0056019 | 0.032784 | 0.0069417 | -122.219 | -0.14053 | -122.775 | 0.21237 | -0.086641 | 0.32053 | -122.563 | 0.074307 | 0.027831 | 0.003172 | 0.16234 | 0.26553 | -0.17081 | -0.2191 | 0.24123 | -0.002778 | 0.58524 | 0.029258 | -0.21198 | -0.30179 | 0.10538 | 122.5852 | -0.052807 | 122.8786 | 122.8074 | 0.22227 | 0.050381 | -0.38596 | 123.0166 | 122.7176 | 123.1248 | 122.6637 | -122.7782 | 122.9666 | 123.0698 | 122.6334 | 122.8321 | -0.43424
562.1875 | 123.0469 | -122.8592 | 0.25177 | 1.4211e-13 | -0.014705 | -0.00028411 | 0.063126 | -0.010063 | 0.060095 | -0.0096144 | 0.0083426 | 0.0083539 | -0.0051745 | 0.032784 | 0.0069417 | -122.2144 | -0.13595 | -122.7704 | 0.20779 | -0.09122 | 0.32511 | -122.5539 | 0.06515 | 0.018674 | 0.01233 | 0.16234 | 0.26553 | -0.17081 | -0.21452 | 0.30532 | -0.043977 | 0.64475 | 0.088768 | -0.21656 | -0.34299 | 0.07334 | 122.6447 | -0.089428 | 122.9243 | 122.8715 | 0.22685 | 0.01376 | -0.42258 | 123.067 | 122.768 | 123.1843 | 122.7232 | -122.8056 | 123.0215 | 123.1247 | 122.6884 | 122.8779 | -0.46629
563.9375 | 123.0194 | -122.8409 | 0.22888 | 1.4211e-13 | -0.015132 | -0.00049791 | 0.062913 | -0.010277 | 0.060095 | 0.013277 | 0.008129 | 0.0083539 | -0.0053883 | 0.03257 | 0.0067279 | -122.2144 | -0.13595 | -122.7704 | 0.21237 | -0.086641 | 0.37548 | -122.5539 | 0.06515 | 0.027831 | 0.007751 | 0.16234 | 0.27469 | -0.17081 | -0.20994 | 0.28701 | -0.016511 | 0.62644 | 0.070457 | -0.21656 | -0.31552 | 0.14659 | 122.6309 | -0.06654 | 122.906 | 122.8486 | 0.21769 | 0.045805 | -0.3997 | 123.0533 | 122.7542 | 123.2164 | 122.7049 | -122.7827 | 123.0032 | 123.1156 | 122.6701 | 122.8687 | -0.43882
565.625 | 123.0927 | -122.8226 | 0.22888 | 1.4211e-13 | -0.015132 | -0.00028411 | 0.062913 | -0.010277 | 0.059881 | 0.0056466 | 0.0083426 | 0.0085677 | -0.0056019 | 0.03257 | 0.0067279 | -122.2236 | -0.13595 | -122.7796 | 0.19406 | -0.09122 | 0.35258 | -122.563 | 0.069728 | 0.023253 | 0.007751 | 0.16234 | 0.26553 | -0.17081 | -0.20994 | 0.25955 | -0.034824 | 0.59898 | 0.042991 | -0.21655 | -0.3201 | 0.1237 | 122.6126 | -0.06654 | 122.8923 | 122.8303 | 0.21769 | 0.036648 | -0.3997 | 123.0166 | 122.7314 | 123.1752 | 122.6866 | -122.7919 | 122.9849 | 123.0881 | 122.6518 | 122.8458 | -0.43882
567.3594 | 123.024 | -122.85 | 0.23804 | 1.4211e-13 | -0.014919 | -0.00028411 | 0.062485 | -0.010491 | 0.059881 | 0.0056466 | 0.0087698 | 0.0081403 | -0.0056019 | 0.032357 | 0.0065143 | -122.2144 | -0.14511 | -122.7613 | 0.20321 | -0.095798 | 0.32969 | -122.563 | 0.060571 | 0.018674 | 0.007751 | 0.16692 | 0.27011 | -0.16624 | -0.2191 | 0.28701 | -0.034823 | 0.6356 | 0.08877 | -0.19824 | -0.33383 | 0.091652 | 122.6309 | -0.071116 | 122.9106 | 122.8578 | 0.22685 | 0.032071 | -0.40427 | 123.0533 | 122.7542 | 123.1797 | 122.7049 | -122.8011 | 123.017 | 123.1201 | 122.6838 | 122.8687 | -0.45713
569.1094 | 123.1659 | -122.7997 | 0.20599 | 1.4211e-13 | -0.014705 | -0.00049791 | 0.062913 | -0.010277 | 0.059881 | 0.0056466 | 0.008129 | 0.0083539 | -0.0053883 | 0.032784 | 0.0065143 | -122.2144 | -0.14053 | -122.7658 | 0.19406 | -0.086641 | 0.36632 | -122.5584 | 0.074307 | 0.018674 | 0.007751 | 0.16692 | 0.27469 | -0.17539 | -0.20536 | 0.24124 | -0.011936 | 0.58525 | 0.033838 | -0.2074 | -0.29263 | 0.16032 | 122.5943 | -0.039073 | 122.874 | 122.8074 | 0.21311 | 0.068693 | -0.38139 | 122.9937 | 122.713 | 123.166 | 122.6592 | -122.7644 | 122.9666 | 123.0744 | 122.6243 | 122.8184 | -0.41135
570.8438 | 123.0423 | -122.8455 | 0.21973 | 1.4211e-13 | -0.014919 | -0.00028411 | 0.062699 | -0.010277 | 0.060095 | -0.0019839 | 0.0085562 | 0.0085677 | -0.0053883 | 0.03257 | 0.0067279 | -122.219 | -0.14053 | -122.7613 | 0.20321 | -0.09122 | 0.32053 | -122.5584 | 0.060571 | 0.023253 | 0.003172 | 0.16234 | 0.27011 | -0.17539 | -0.2191 | 0.28701 | -0.016513 | 0.62644 | 0.084192 | -0.20282 | -0.31095 | 0.1008 | 122.6264 | -0.057385 | 122.906 | 122.8486 | 0.22227 | 0.050381 | -0.39512 | 123.0487 | 122.7542 | 123.166 | 122.7049 | -122.7782 | 123.0078 | 123.1156 | 122.6701 | 122.8687 | -0.43882
572.5156 | 123.1705 | -122.8043 | 0.20599 | 1.4211e-13 | -0.014919 | -0.00071151 | 0.062699 | -0.010063 | 0.059881 | 0.0056466 | 0.0083426 | 0.0083539 | -0.0049609 | 0.032784 | 0.0067279 | -122.2144 | -0.14053 | -122.7613 | 0.19406 | -0.086641 | 0.30222 | -122.563 | 0.069728 | 0.018674 | 0.01233 | 0.16234 | 0.26553 | -0.17539 | -0.20994 | 0.24123 | -0.011936 | 0.58982 | 0.042993 | -0.19824 | -0.29263 | 0.096223 | 122.5943 | -0.043652 | 122.874 | 122.8166 | 0.22227 | 0.059536 | -0.38139 | 122.9983 | 122.7176 | 123.1065 | 122.6637 | -122.769 | 122.9666 | 123.0698 | 122.6289 | 122.8229 | -0.41593
574.2656 | 123.0423 | -122.8363 | 0.23804 | 1.4211e-13 | -0.014919 | -0.00028411 | 0.062485 | -0.010491 | 0.060095 | 0.0056466 | 0.0083426 | 0.0083539 | -0.0051745 | 0.032784 | 0.0067279 | -122.2144 | -0.13595 | -122.743 | 0.21237 | -0.09122 | 0.38005 | -122.5447 | 0.069728 | 0.027831 | 0.003172 | 0.16692 | 0.27011 | -0.17539 | -0.21452 | 0.29159 | -0.025666 | 0.62187 | 0.09335 | -0.19824 | -0.32926 | 0.14202 | 122.6218 | -0.071116 | 122.906 | 122.8395 | 0.21769 | 0.032071 | -0.41343 | 123.0487 | 122.7451 | 123.2164 | 122.7004 | -122.7827 | 123.0032 | 123.1064 | 122.6609 | 122.8641 | -0.45255
576 | 123.1247 | -122.7905 | 0.2243 | 1.4211e-13 | -0.014705 | -0.00049791 | 0.062699 | -0.010491 | 0.059881 | -0.0019839 | 0.0085562 | 0.0085677 | -0.0053883 | 0.032784 | 0.0067279 | -122.2099 | -0.14511 | -122.7521 | 0.20779 | -0.086641 | 0.33885 | -122.5493 | 0.069728 | 0.027831 | 0.007751 | 0.16692 | 0.27469 | -0.17081 | -0.21452 | 0.24124 | -0.016511 | 0.58067 | 0.038416 | -0.20282 | -0.31095 | 0.11454 | 122.576 | -0.057383 | 122.8603 | 122.7983 | 0.22227 | 0.050383 | -0.39512 | 122.9983 | 122.7039 | 123.1294 | 122.6454 | -122.7736 | 122.9574 | 123.0652 | 122.6197 | 122.8184 | -0.43882
577.75 | 123.1064 | -122.8088 | 0.2243 | 1.4211e-13 | -0.014705 | -7.051e-05 | 0.062913 | -0.010491 | 0.059881 | -0.0019839 | 0.008129 | 0.0079267 | -0.0056019 | 0.032784 | 0.0067279 | -122.219 | -0.14511 | -122.7521 | 0.19864 | -0.09122 | 0.36174 | -122.5722 | 0.06515 | 0.027831 | 0.01233 | 0.15318 | 0.27011 | -0.17539 | -0.21452 | 0.23665 | -0.025668 | 0.58982 | 0.056727 | -0.17993 | -0.31552 | 0.13743 | 122.5943 | -0.071119 | 122.874 | 122.8212 | 0.22685 | 0.045804 | -0.3997 | 123.0075 | 122.7176 | 123.1706 | 122.6637 | -122.7965 | 122.962 | 123.0789 | 122.6334 | 122.8367 | -0.43882
579.5 | 123.0469 | -122.8317 | 0.21515 | 1.4211e-13 | -0.014919 | -0.00049791 | 0.063126 | -0.010918 | 0.059454 | -0.0019839 | 0.0083426 | 0.0081403 | -0.0056019 | 0.032784 | 0.0067279 | -122.2144 | -0.14511 | -122.7475 | 0.19864 | -0.09122 | 0.33427 | -122.5584 | 0.06515 | 0.018674 | 0.007751 | 0.15776 | 0.26553 | -0.17539 | -0.20994 | 0.27328 | -0.016513 | 0.61729 | 0.084194 | -0.18909 | -0.30637 | 0.11912 | 122.6218 | -0.057385 | 122.8969 | 122.8395 | 0.21769 | 0.050381 | -0.39054 | 123.0304 | 122.7405 | 123.166 | 122.6866 | -122.7736 | 122.9895 | 123.0973 | 122.6563 | 122.8504 | -0.42509
581.1719 | 123.143 | -122.8134 | 0.20599 | 1.4211e-13 | -0.014919 | -0.00049791 | 0.062485 | -0.010491 | 0.059667 | -0.0096144 | 0.008129 | 0.0083539 | -0.0053883 | 0.032998 | 0.0063007 | -122.2099 | -0.14053 | -122.7475 | 0.20321 | -0.086641 | 0.31137 | -122.563 | 0.06515 | 0.023253 | 0.01233 | 0.16692 | 0.26553 | -0.17081 | -0.21452 | 0.25039 | -0.00278 | 0.60356 | 0.065884 | -0.18451 | -0.29263 | 0.10538 | 122.5989 | -0.039073 | 122.8786 | 122.8257 | 0.22685 | 0.059536 | -0.37681 | 123.0166 | 122.7268 | 123.1248 | 122.6729 | -122.769 | 122.9803 | 123.0789 | 122.6426 | 122.8367 | -0.42051
582.9062 | 123.0835 | -122.8409 | 0.2243 | 1.4211e-13 | -0.015132 | -0.00049791 | 0.062699 | -0.010491 | 0.059881 | 0.0056466 | 0.0085562 | 0.0083539 | -0.0056019 | 0.032784 | 0.0065143 | -122.2099 | -0.14511 | -122.7521 | 0.20321 | -0.095798 | 0.3709 | -122.563 | 0.06515 | 0.03241 | 0.007751 | 0.16234 | 0.26553 | -0.17997 | -0.2191 | 0.27786 | -0.02109 | 0.63102 | 0.08877 | -0.18909 | -0.3201 | 0.14659 | 122.6218 | -0.061962 | 122.906 | 122.8486 | 0.22685 | 0.041226 | -0.40428 | 123.0441 | 122.7451 | 123.2118 | 122.6958 | -122.7873 | 123.0032 | 123.1064 | 122.6609 | 122.8733 | -0.4434
584.5938 | 123.0377 | -122.8455 | 0.23804 | 1.4211e-13 | -0.015132 | -0.00049791 | 0.062699 | -0.010704 | 0.059881 | -0.0019839 | 0.0085562 | 0.0083539 | -0.0053883 | 0.032998 | 0.0065143 | -122.2144 | -0.13595 | -122.7521 | 0.20779 | -0.095798 | 0.348 | -122.5584 | 0.055992 | 0.018674 | 0.01233 | 0.15318 | 0.27011 | -0.17539 | -0.2191 | 0.28701 | -0.030244 | 0.63102 | 0.093348 | -0.19366 | -0.33383 | 0.10997 | 122.6264 | -0.084852 | 122.9015 | 122.8578 | 0.23143 | 0.032071 | -0.41343 | 123.0533 | 122.7497 | 123.1935 | 122.7095 | -122.7965 | 122.9986 | 123.1156 | 122.6701 | 122.8641 | -0.45713
586.3438 | 123.0286 | -122.8409 | 0.21973 | 1.4211e-13 | -0.015132 | -0.00049791 | 0.062699 | -0.010063 | 0.060095 | -0.0096144 | 0.0087698 | 0.0081403 | -0.0053883 | 0.032784 | 0.0065143 | -122.219 | -0.14053 | -122.7475 | 0.19864 | -0.095798 | 0.32969 | -122.5584 | 0.074307 | 0.018674 | 0.003172 | 0.16234 | 0.27011 | -0.16624 | -0.2191 | 0.28243 | -0.021091 | 0.62186 | 0.093349 | -0.18909 | -0.31552 | 0.10996 | 122.6218 | -0.057385 | 122.9152 | 122.8441 | 0.22227 | 0.050381 | -0.38596 | 123.0395 | 122.7451 | 123.1706 | 122.7004 | -122.7782 | 123.0032 | 123.111 | 122.6746 | 122.8596 | -0.43882
588.0938 | 122.9919 | -122.8546 | 0.23804 | 1.4211e-13 | -0.014919 | -0.00049791 | 0.062699 | -0.010918 | 0.059881 | 0.0056466 | 0.0083426 | 0.0083539 | -0.0058155 | 0.032998 | 0.0065143 | -122.2099 | -0.14053 | -122.7475 | 0.20321 | -0.086641 | 0.32969 | -122.5539 | 0.060571 | 0.023253 | 0.003172 | 0.15776 | 0.26095 | -0.16166 | -0.21452 | 0.30075 | -0.034823 | 0.64475 | 0.10708 | -0.19366 | -0.32468 | 0.091652 | 122.6401 | -0.080273 | 122.9152 | 122.8578 | 0.21769 | 0.022914 | -0.3997 | 123.0578 | 122.768 | 123.1843 | 122.7141 | -122.7919 | 123.0124 | 123.1156 | 122.693 | 122.8779 | -0.45255
589.7812 | 123.0331 | -122.85 | 0.23346 | 1.4211e-13 | -0.014919 | -0.00092531 | 0.062699 | -0.010491 | 0.059881 | -0.0019839 | 0.0085562 | 0.0085677 | -0.0056019 | 0.032998 | 0.0063007 | -122.2099 | -0.14511 | -122.7567 | 0.20321 | -0.086641 | 0.36632 | -122.5584 | 0.060571 | 0.027831 | 0.007751 | 0.16234 | 0.26095 | -0.16624 | -0.2191 | 0.29159 | -0.030245 | 0.64018 | 0.093348 | -0.19824 | -0.3201 | 0.13286 | 122.6309 | -0.071117 | 122.9106 | 122.8578 | 0.22685 | 0.027492 | -0.3997 | 123.0533 | 122.7634 | 123.2164 | 122.7049 | -122.7919 | 123.0124 | 123.111 | 122.6838 | 122.8779 | -0.45255
591.5156 | 122.9919 | -122.8363 | 0.23804 | 1.4211e-13 | -0.014919 | -0.00071151 | 0.06334 | -0.010491 | 0.059667 | -0.0019839 | 0.0087698 | 0.0081403 | -0.0056019 | 0.032784 | 0.0063007 | -122.2099 | -0.14053 | -122.7521 | 0.20321 | -0.09122 | 0.28848 | -122.5493 | 0.069728 | 0.014095 | 0.003172 | 0.16234 | 0.27011 | -0.17997 | -0.21452 | 0.28701 | -0.034823 | 0.62644 | 0.084193 | -0.20282 | -0.32926 | 0.050444 | 122.6218 | -0.075695 | 122.906 | 122.8395 | 0.21769 | 0.032071 | -0.41801 | 123.0395 | 122.7451 | 123.1248 | 122.6958 | -122.7873 | 122.9986 | 123.1064 | 122.6563 | 122.8504 | -0.45255
593.2031 | 123.1659 | -122.8088 | 0.20599 | 1.4211e-13 | -0.014919 | -7.051e-05 | 0.062485 | -0.010277 | 0.060095 | 0.0056466 | 0.0085562 | 0.0083539 | -0.0056019 | 0.033211 | 0.0063007 | -122.2099 | -0.14053 | -122.743 | 0.20321 | -0.09122 | 0.35716 | -122.5539 | 0.060571 | 0.023253 | 0.007751 | 0.15776 | 0.26095 | -0.17081 | -0.21452 | 0.25497 | -0.00278 | 0.59898 | 0.065884 | -0.18909 | -0.29721 | 0.15117 | 122.5943 | -0.04823 | 122.8694 | 122.8166 | 0.22227 | 0.054957 | -0.37681 | 123.0121 | 122.7176 | 123.166 | 122.6683 | -122.7599 | 122.9666 | 123.0698 | 122.638 | 122.8321 | -0.42051
594.9531 | 123.0286 | -122.8363 | 0.21515 | 1.4211e-13 | -0.014919 | -0.00028411 | 0.062699 | -0.010491 | 0.059667 | -0.0019839 | 0.0083426 | 0.0081403 | -0.0056019 | 0.032784 | 0.0063007 | -122.2053 | -0.13595 | -122.7567 | 0.20321 | -0.095798 | 0.34342 | -122.5584 | 0.06515 | 0.018674 | 0.007751 | 0.15776 | 0.26553 | -0.16624 | -0.21452 | 0.27786 | -0.011935 | 0.63102 | 0.079615 | -0.19824 | -0.31095 | 0.12828 | 122.6218 | -0.057385 | 122.9015 | 122.8441 | 0.22227 | 0.050381 | -0.38138 | 123.0395 | 122.7405 | 123.1797 | 122.7004 | -122.7736 | 122.9941 | 123.1018 | 122.6701 | 122.855 | -0.42967
596.6875 | 123.143 | -122.7951 | 0.1831 | 1.4211e-13 | -0.014919 | -0.00071151 | 0.062913 | -0.010277 | 0.059881 | 0.013277 | 0.008129 | 0.0083539 | -0.0056019 | 0.032998 | 0.0060869 | -122.2099 | -0.14053 | -122.7567 | 0.19406 | -0.09122 | 0.33885 | -122.5584 | 0.074307 | 0.027831 | 0.003172 | 0.15776 | 0.27011 | -0.16624 | -0.21452 | 0.23666 | 0.010953 | 0.58525 | 0.038416 | -0.19824 | -0.27432 | 0.15574 | 122.5806 | -0.025341 | 122.8694 | 122.7983 | 0.21769 | 0.087003 | -0.34934 | 122.9892 | 122.7039 | 123.134 | 122.6546 | -122.7416 | 122.9529 | 123.0652 | 122.6289 | 122.8229 | -0.39762
598.4375 | 123.0331 | -122.8409 | 0.24719 | 1.4211e-13 | -0.015346 | -0.00049791 | 0.062699 | -0.010704 | 0.059667 | -0.0019839 | 0.008129 | 0.0081403 | -0.0058155 | 0.032998 | 0.0065143 | -122.2099 | -0.14053 | -122.7521 | 0.19864 | -0.095798 | 0.29306 | -122.5584 | 0.069728 | 0.018674 | -0.001407 | 0.16692 | 0.27011 | -0.17081 | -0.21452 | 0.28243 | -0.048556 | 0.63102 | 0.08877 | -0.19366 | -0.34299 | 0.045868 | 122.6264 | -0.080271 | 122.9106 | 122.8395 | 0.21311 | 0.022916 | -0.41801 | 123.0395 | 122.7451 | 123.1339 | 122.7004 | -122.8056 | 123.0078 | 123.111 | 122.6701 | 122.8596 | -0.46171
600.125 | 123.0103 | -122.8546 | 0.2243 | 1.4211e-13 | -0.015132 | -0.00028411 | 0.062913 | -0.010704 | 0.059454 | -0.0019839 | 0.008129 | 0.0083539 | -0.0056019 | 0.032998 | 0.0065143 | -122.2053 | -0.14511 | -122.7613 | 0.19406 | -0.095798 | 0.36174 | -122.5584 | 0.069728 | 0.023253 | 0.016908 | 0.15776 | 0.27011 | -0.17081 | -0.20994 | 0.29617 | -0.030246 | 0.64933 | 0.093347 | -0.20282 | -0.3201 | 0.13743 | 122.6447 | -0.06654 | 122.9243 | 122.8715 | 0.22685 | 0.045804 | -0.39512 | 123.0487 | 122.7588 | 123.2164 | 122.7095 | -122.7828 | 123.0124 | 123.1247 | 122.6838 | 122.8779 | -0.43424
601.8594 | 123.1018 | -122.818 | 0.20599 | 1.4211e-13 | -0.015132 | -0.00049791 | 0.062699 | -0.010704 | 0.059881 | 0.0056466 | 0.0083426 | 0.0083539 | -0.0053883 | 0.032998 | 0.0063007 | -122.2099 | -0.13595 | -122.7658 | 0.18948 | -0.095798 | 0.36174 | -122.5676 | 0.060571 | 0.023253 | 0.01233 | 0.15776 | 0.26553 | -0.17539 | -0.21452 | 0.25039 | -0.016515 | 0.60813 | 0.052148 | -0.19824 | -0.30179 | 0.15574 | 122.6035 | -0.04823 | 122.8786 | 122.8303 | 0.22685 | 0.059536 | -0.38139 | 123.0075 | 122.7222 | 123.1797 | 122.682 | -122.7736 | 122.9758 | 123.0835 | 122.6426 | 122.8412 | -0.42051
603.5938 | 123.0835 | -122.818 | 0.20142 | 1.4211e-13 | -0.015132 | -0.00049791 | 0.062699 | -0.010704 | 0.059881 | 0.0056466 | 0.0083426 | 0.0085677 | -0.0053883 | 0.032784 | 0.0067279 | -122.2144 | -0.14053 | -122.7613 | 0.1849 | -0.10496 | 0.29306 | -122.5722 | 0.069728 | 0.023253 | 0.016908 | 0.15776 | 0.26553 | -0.16624 | -0.21452 | 0.24581 | -0.016515 | 0.60356 | 0.056726 | -0.18908 | -0.30637 | 0.091644 | 122.6035 | -0.043652 | 122.8877 | 122.8349 | 0.23142 | 0.064114 | -0.36765 | 123.0029 | 122.713 | 123.1111 | 122.6775 | -122.7736 | 122.9758 | 123.0835 | 122.6518 | 122.8412 | -0.41593
605.2812 | 123.0881 | -122.8317 | 0.1831 | 1.4211e-13 | -0.014705 | -0.00049791 | 0.062485 | -0.010491 | 0.059667 | 0.0056466 | 0.0083426 | 0.0081403 | -0.0053883 | 0.032998 | 0.0060869 | -122.2282 | -0.14969 | -122.7658 | 0.1849 | -0.10953 | 0.348 | -122.5676 | 0.06515 | 0.023253 | 0.007751 | 0.15776 | 0.27469 | -0.16624 | -0.21452 | 0.26412 | 0.001796 | 0.60355 | 0.065881 | -0.19824 | -0.29264 | 0.1649 | 122.6172 | -0.025341 | 122.8969 | 122.8395 | 0.22227 | 0.091582 | -0.34934 | 123.0166 | 122.7222 | 123.1797 | 122.682 | -122.7507 | 122.9895 | 123.1064 | 122.6655 | 122.855 | -0.39762
607.0312 | 123.0606 | -122.8409 | 0.19684 | 1.4211e-13 | -0.01556 | -0.00071151 | 0.062699 | -0.010491 | 0.059881 | 0.0056466 | 0.008129 | 0.0083539 | -0.0053883 | 0.03257 | 0.0063007 | -122.2282 | -0.14053 | -122.7796 | 0.17117 | -0.11411 | 0.30222 | -122.5768 | 0.069728 | 0.027831 | 0.007751 | 0.16234 | 0.27469 | -0.17081 | -0.21452 | 0.26412 | -0.025672 | 0.61271 | 0.061301 | -0.20282 | -0.31095 | 0.10538 | 122.6264 | -0.034496 | 122.9106 | 122.8486 | 0.22227 | 0.077849 | -0.36765 | 123.012 | 122.7268 | 123.1431 | 122.7004 | -122.7736 | 123.0032 | 123.1156 | 122.6701 | 122.8687 | -0.41135
608.7812 | 122.9919 | -122.8683 | 0.21515 | 1.4211e-13 | -0.015346 | -0.00049791 | 0.062699 | -0.010704 | 0.059667 | 0.0056466 | 0.0085562 | 0.0081403 | -0.0053883 | 0.033211 | 0.0065143 | -122.2373 | -0.14511 | -122.7796 | 0.17117 | -0.10953 | 0.32511 | -122.5813 | 0.069728 | 0.023253 | 0.01233 | 0.16234 | 0.27469 | -0.17539 | -0.2191 | 0.28701 | -0.043983 | 0.63102 | 0.088767 | -0.19824 | -0.32468 | 0.10996 | 122.6493 | -0.052807 | 122.9381 | 122.8807 | 0.23143 | 0.059538 | -0.39054 | 123.0395 | 122.7588 | 123.1935 | 122.7232 | -122.7965 | 123.0307 | 123.143 | 122.693 | 122.8916 | -0.43424
610.4688 | 123.0881 | -122.85 | 0.16937 | 1.4211e-13 | -0.015346 | -0.00071151 | 0.062699 | -0.010918 | 0.059881 | -0.0096144 | 0.0085562 | 0.0083539 | -0.0058155 | 0.032998 | 0.0063007 | -122.2328 | -0.14969 | -122.7933 | 0.17117 | -0.11411 | 0.32053 | -122.5905 | 0.06515 | 0.027831 | 0.007751 | 0.15776 | 0.27011 | -0.17539 | -0.22367 | 0.25954 | 0.001793 | 0.61728 | 0.056722 | -0.20282 | -0.28349 | 0.15116 | 122.6264 | -0.011609 | 122.9152 | 122.8578 | 0.23142 | 0.10074 | -0.34477 | 123.0212 | 122.7359 | 123.1706 | 122.7004 | -122.7599 | 123.0078 | 123.1201 | 122.6746 | 122.8779 | -0.39305
612.2188 | 123.0194 | -122.8775 | 0.18768 | 1.4211e-13 | -0.015132 | -0.00028411 | 0.062699 | -0.010704 | 0.059667 | 0.0056466 | 0.0085562 | 0.0079267 | -0.0053883 | 0.033211 | 0.0063007 | -122.2236 | -0.13595 | -122.775 | 0.16201 | -0.11869 | 0.31595 | -122.5813 | 0.069728 | 0.027831 | -0.001407 | 0.15318 | 0.27011 | -0.17081 | -0.2191 | 0.29616 | -0.025674 | 0.65391 | 0.1025 | -0.19366 | -0.30638 | 0.12827 | 122.6584 | -0.034498 | 122.9472 | 122.8761 | 0.21769 | 0.082425 | -0.3585 | 123.0395 | 122.7588 | 123.1935 | 122.7416 | -122.769 | 123.0307 | 123.1476 | 122.7067 | 122.9053 | -0.40678
613.9062 | 123.1247 | -122.8043 | 0.17395 | 1.4211e-13 | -0.015132 | -0.00028411 | 0.062913 | -0.010918 | 0.059881 | 0.0056466 | 0.0083426 | 0.0081403 | -0.0058155 | 0.033425 | 0.0060869 | -122.2328 | -0.13595 | -122.7704 | 0.16659 | -0.10953 | 0.28848 | -122.5813 | 0.06515 | 0.023253 | 0.003172 | 0.15776 | 0.27926 | -0.17539 | -0.20994 | 0.22292 | -0.007363 | 0.57151 | 0.033836 | -0.18908 | -0.28348 | 0.11453 | 122.5943 | -0.016186 | 122.8694 | 122.8074 | 0.21311 | 0.10531 | -0.34934 | 122.9708 | 122.6947 | 123.0927 | 122.6683 | -122.7553 | 122.962 | 123.0835 | 122.6289 | 122.8275 | -0.38389
615.6406 | 123.1247 | -122.8409 | 0.16022 | 1.4211e-13 | -0.015132 | -0.00028411 | 0.062485 | -0.010704 | 0.059667 | 0.013277 | 0.0085562 | 0.0081403 | -0.0056019 | 0.033211 | 0.0060869 | -122.2328 | -0.14511 | -122.775 | 0.16659 | -0.11411 | 0.33427 | -122.5813 | 0.060571 | 0.023253 | 0.003172 | 0.16234 | 0.27926 | -0.17081 | -0.21452 | 0.25954 | 0.00637 | 0.60813 | 0.065879 | -0.19366 | -0.27433 | 0.17405 | 122.6264 | 0.002125 | 122.9015 | 122.8441 | 0.21769 | 0.11905 | -0.33103 | 123.0075 | 122.7268 | 123.1751 | 122.6958 | -122.7416 | 123.0032 | 123.1201 | 122.6701 | 122.8641 | -0.37473
617.3906 | 123.0606 | -122.8363 | 0.19684 | 1.4211e-13 | -0.015132 | -0.00071151 | 0.062699 | -0.010491 | 0.059881 | -0.0019839 | 0.0087698 | 0.0081403 | -0.0056019 | 0.032784 | 0.0060869 | -122.2328 | -0.14511 | -122.775 | 0.16201 | -0.11411 | 0.33427 | -122.5768 | 0.06515 | 0.023253 | 0.01233 | 0.15776 | 0.27011 | -0.17539 | -0.20994 | 0.25954 | -0.034829 | 0.60355 | 0.061302 | -0.19824 | -0.31095 | 0.13743 | 122.6264 | -0.039074 | 122.9015 | 122.8486 | 0.22227 | 0.07327 | -0.37223 | 122.9983 | 122.7222 | 123.1706 | 122.6912 | -122.7736 | 122.9941 | 123.1064 | 122.6609 | 122.8596 | -0.40677
619.0781 | 123.0194 | -122.8729 | 0.19226 | 1.4211e-13 | -0.015132 | -0.00028411 | 0.062913 | -0.010491 | 0.059881 | 0.013277 | 0.0083426 | 0.0085677 | -0.0058155 | 0.032998 | 0.0060869 | -122.2328 | -0.13595 | -122.7658 | 0.17574 | -0.11411 | 0.32969 | -122.5859 | 0.069728 | 0.027831 | 0.007751 | 0.16234 | 0.27926 | -0.16624 | -0.21452 | 0.287 | -0.016517 | 0.64017 | 0.10708 | -0.17992 | -0.30637 | 0.13743 | 122.6584 | -0.029919 | 122.9427 | 122.8807 | 0.22227 | 0.087004 | -0.3585 | 123.0487 | 122.7588 | 123.2026 | 122.737 | -122.7782 | 123.0353 | 123.1522 | 122.7067 | 122.9008 | -0.40678
620.8125 | 123.0148 | -122.85 | 0.20599 | 1.4211e-13 | -0.015132 | -7.051e-05 | 0.062485 | -0.010704 | 0.059881 | -0.0019839 | 0.0083426 | 0.0083539 | -0.0056019 | 0.033211 | 0.0060869 | -122.2236 | -0.14511 | -122.7704 | 0.16659 | -0.10953 | 0.27932 | -122.5722 | 0.06515 | 0.027831 | -0.001407 | 0.16692 | 0.27011 | -0.16624 | -0.21452 | 0.27785 | -0.039407 | 0.62644 | 0.079613 | -0.19824 | -0.31553 | 0.07333 | 122.6355 | -0.039073 | 122.9152 | 122.8486 | 0.21311 | 0.064114 | -0.37223 | 123.0166 | 122.7405 | 123.1294 | 122.7049 | -122.7782 | 123.017 | 123.1201 | 122.6838 | 122.8779 | -0.42051
622.5625 | 123.1338 | -122.8271 | 0.15564 | 1.4211e-13 | -0.015132 | -0.00049791 | 0.062913 | -0.010918 | 0.059667 | 0.0056466 | 0.0083426 | 0.0083539 | -0.0056019 | 0.033211 | 0.0063007 | -122.2144 | -0.14969 | -122.7613 | 0.17117 | -0.10953 | 0.24269 | -122.5722 | 0.060571 | 0.023253 | 0.007751 | 0.16692 | 0.26553 | -0.16624 | -0.20994 | 0.25496 | 0.015526 | 0.61271 | 0.065881 | -0.18908 | -0.26517 | 0.087055 | 122.6172 | 0.011281 | 122.8877 | 122.8349 | 0.21769 | 0.10989 | -0.32188 | 122.9983 | 122.7176 | 123.0698 | 122.6775 | -122.7278 | 122.9941 | 123.0927 | 122.6609 | 122.8504 | -0.36558
624.25 | 123.1293 | -122.7951 | 0.16937 | 1.4211e-13 | -0.015132 | -0.00049791 | 0.062913 | -0.010491 | 0.060095 | -0.0019839 | 0.0085562 | 0.0081403 | -0.0056019 | 0.033211 | 0.0065143 | -122.2144 | -0.14969 | -122.7658 | 0.17117 | -0.10953 | 0.3068 | -122.5768 | 0.06515 | 0.041567 | 0.007751 | 0.15776 | 0.27011 | -0.17081 | -0.21452 | 0.21834 | 0.001793 | 0.58067 | 0.02926 | -0.18908 | -0.27891 | 0.13742 | 122.5806 | -0.011609 | 122.8603 | 122.8029 | 0.22227 | 0.10074 | -0.34019 | 122.9663 | 122.6856 | 123.1019 | 122.6454 | -122.7461 | 122.9529 | 123.0652 | 122.6243 | 122.8367 | -0.38389
626 | 123.0515 | -122.8546 | 0.17395 | 1.4211e-13 | -0.015132 | -0.00049791 | 0.062699 | -0.010918 | 0.059881 | 0.013277 | 0.0085562 | 0.0083539 | -0.0056019 | 0.032998 | 0.0065143 | -122.219 | -0.14511 | -122.7567 | 0.17117 | -0.11869 | 0.32969 | -122.5768 | 0.06515 | 0.036989 | 0.01233 | 0.16234 | 0.27926 | -0.16624 | -0.21452 | 0.27785 | -0.002784 | 0.6356 | 0.097925 | -0.17993 | -0.29264 | 0.15574 | 122.6401 | -0.011608 | 122.9198 | 122.8669 | 0.22685 | 0.10531 | -0.34019 | 123.0258 | 122.7359 | 123.1843 | 122.7095 | -122.7507 | 123.017 | 123.1339 | 122.6884 | 122.8916 | -0.38847
627.75 | 123.1064 | -122.8363 | 0.16479 | 1.4211e-13 | -0.014919 | -0.00049791 | 0.062485 | -0.010918 | 0.059667 | 0.0056466 | 0.0085562 | 0.0081403 | -0.0056019 | 0.032998 | 0.0065143 | -122.219 | -0.14969 | -122.7658 | 0.17574 | -0.11869 | 0.31595 | -122.5722 | 0.06515 | 0.036989 | 0.007751 | 0.15318 | 0.27011 | -0.16624 | -0.21452 | 0.26412 | 0.010949 | 0.61729 | 0.070459 | -0.19366 | -0.28349 | 0.15116 | 122.6218 | -0.01161 | 122.9015 | 122.8441 | 0.22227 | 0.10531 | -0.33103 | 123.012 | 122.7176 | 123.1523 | 122.6866 | -122.737 | 122.9895 | 123.1064 | 122.6701 | 122.8733 | -0.37931
629.4375 | 123.0011 | -122.818 | 0.18768 | 1.4211e-13 | -0.014919 | -0.00049791 | 0.062485 | -0.010704 | 0.060095 | 0.0056466 | 0.008129 | 0.0085677 | -0.0058155 | 0.033211 | 0.0063007 | -122.2236 | -0.14969 | -122.7658 | 0.17117 | -0.10953 | 0.31595 | -122.5722 | 0.060571 | 0.041567 | 0.007751 | 0.15776 | 0.27469 | -0.16624 | -0.2191 | 0.24581 | -0.016517 | 0.5944 | 0.052148 | -0.19366 | -0.29722 | 0.12827 | 122.5989 | -0.029919 | 122.8786 | 122.8257 | 0.22685 | 0.087004 | -0.35392 | 122.9892 | 122.7085 | 123.1339 | 122.6683 | -122.7599 | 122.9758 | 123.0927 | 122.6518 | 122.8596 | -0.40678
631.1875 | 123.1155 | -122.8226 | 0.17395 | 1.4211e-13 | -0.014919 | -0.00049791 | 0.062913 | -0.010491 | 0.059881 | 0.0056466 | 0.008129 | 0.0083539 | -0.0056019 | 0.032784 | 0.0063007 | -122.2144 | -0.14969 | -122.7567 | 0.18032 | -0.10953 | 0.3068 | -122.5676 | 0.06515 | 0.036989 | 0.01233 | 0.16234 | 0.27011 | -0.17539 | -0.2191 | 0.25497 | 0.006373 | 0.60813 | 0.065882 | -0.18908 | -0.28348 | 0.13285 | 122.6035 | -0.011608 | 122.8877 | 122.8349 | 0.23143 | 0.096158 | -0.34934 | 123.0029 | 122.713 | 123.1294 | 122.6729 | -122.7416 | 122.9849 | 123.0927 | 122.6472 | 122.8596 | -0.39304
632.9219 | 123.1155 | -122.8317 | 0.16479 | 1.4211e-13 | -0.015132 | -0.00049791 | 0.062272 | -0.010918 | 0.060095 | 0.0056466 | 0.008129 | 0.0081403 | -0.0056019 | 0.033211 | 0.0065143 | -122.2144 | -0.13137 | -122.7613 | 0.16659 | -0.11411 | 0.34342 | -122.5676 | 0.069728 | 0.041567 | 0.003172 | 0.16234 | 0.27011 | -0.17997 | -0.2191 | 0.26412 | 0.001792 | 0.61729 | 0.070459 | -0.19366 | -0.27891 | 0.17863 | 122.6126 | -0.002453 | 122.9015 | 122.8349 | 0.22227 | 0.10531 | -0.34477 | 122.9983 | 122.7176 | 123.1752 | 122.7004 | -122.7324 | 122.9941 | 123.1018 | 122.6518 | 122.8733 | -0.38389
634.6094 | 123.0011 | -122.85 | 0.21057 | 1.4211e-13 | -0.01556 | -7.051e-05 | 0.062699 | -0.010704 | 0.059667 | -0.0019839 | 0.0083426 | 0.0081403 | -0.0056019 | 0.033211 | 0.0063007 | -122.219 | -0.14511 | -122.7521 | 0.17117 | -0.11411 | 0.348 | -122.5584 | 0.069728 | 0.036989 | 0.007751 | 0.16234 | 0.26553 | -0.17539 | -0.2191 | 0.29159 | -0.039405 | 0.63102 | 0.097926 | -0.19366 | -0.32469 | 0.13743 | 122.6309 | -0.048229 | 122.9198 | 122.8578 | 0.22685 | 0.054959 | -0.38596 | 123.0212 | 122.7359 | 123.198 | 122.7049 | -122.769 | 123.0124 | 123.1156 | 122.6746 | 122.887 | -0.42967
636.3438 | 123.0423 | -122.818 | 0.20142 | 1.4211e-13 | -0.015346 | -0.00071151 | 0.062485 | -0.010704 | 0.059881 | -0.0019839 | 0.008129 | 0.0083539 | -0.0056019 | 0.033425 | 0.0063007 | -122.2144 | -0.14053 | -122.7567 | 0.17574 | -0.10496 | 0.33885 | -122.5676 | 0.06515 | 0.046146 | 0.01233 | 0.16234 | 0.27926 | -0.17081 | -0.21452 | 0.25039 | -0.025672 | 0.60356 | 0.061304 | -0.18908 | -0.30637 | 0.13743 | 122.6035 | -0.039074 | 122.8831 | 122.8303 | 0.22685 | 0.077849 | -0.37223 | 122.9937 | 122.713 | 123.1568 | 122.6775 | -122.769 | 122.9803 | 123.0973 | 122.6472 | 122.8641 | -0.41593
638.0312 | 123.0057 | -122.818 | 0.22888 | 1.4211e-13 | -0.015132 | -0.00071151 | 0.062699 | -0.010491 | 0.059881 | 0.0056466 | 0.0083426 | 0.0083539 | -0.0058155 | 0.033425 | 0.0060869 | -122.1961 | -0.14511 | -122.7292 | 0.18948 | -0.095798 | 0.36174 | -122.5493 | 0.069728 | 0.046146 | 0.007751 | 0.16692 | 0.27469 | -0.16624 | -0.21452 | 0.2687 | -0.039403 | 0.62187 | 0.088774 | -0.17993 | -0.32468 | 0.13286 | 122.6035 | -0.061961 | 122.8877 | 122.8257 | 0.22227 | 0.045805 | -0.39512 | 123.0075 | 122.7222 | 123.1797 | 122.6729 | -122.7782 | 122.9849 | 123.0927 | 122.6518 | 122.8641 | -0.4434
639.7812 | 123.1201 | -122.7951 | 0.18768 | 1.4211e-13 | -0.015132 | -0.00071151 | 0.062272 | -0.010918 | 0.059881 | 0.013277 | 0.008129 | 0.0081403 | -0.0056019 | 0.033425 | 0.0063007 | -122.1915 | -0.14511 | -122.7246 | 0.19406 | -0.10038 | 0.36632 | -122.5447 | 0.06515 | 0.041567 | -0.001407 | 0.15318 | 0.26553 | -0.17539 | -0.20994 | 0.2504 | 0.006375 | 0.60356 | 0.070464 | -0.17993 | -0.28806 | 0.17863 | 122.5852 | -0.034498 | 122.8603 | 122.7937 | 0.20853 | 0.077847 | -0.36308 | 122.9892 | 122.6947 | 123.1614 | 122.65 | -122.7324 | 122.9483 | 123.0606 | 122.6197 | 122.8367 | -0.39762
641.4531 | 123.0423 | -122.8088 | 0.21973 | 1.4211e-13 | -0.015346 | -0.00049791 | 0.062485 | -0.010918 | 0.059667 | -0.0019839 | 0.0085562 | 0.0081403 | -0.0058155 | 0.033211 | 0.0060869 | -122.1961 | -0.14511 | -122.7384 | 0.18948 | -0.095798 | 0.33427 | -122.5401 | 0.078886 | 0.046146 | 0.003172 | 0.1715 | 0.27011 | -0.17539 | -0.21452 | 0.26871 | -0.030248 | 0.61271 | 0.070462 | -0.19825 | -0.31552 | 0.11454 | 122.5943 | -0.048228 | 122.8877 | 122.812 | 0.21769 | 0.050381 | -0.39512 | 122.9983 | 122.713 | 123.1431 | 122.6637 | -122.7599 | 122.9803 | 123.0789 | 122.6334 | 122.855 | -0.43424
643.1406 | 123.1338 | -122.7814 | 0.18768 | 1.4211e-13 | -0.015346 | -0.00049791 | 0.062699 | -0.010704 | 0.060095 | -0.0019839 | 0.0085562 | 0.0081403 | -0.0056019 | 0.033425 | 0.0063007 | -122.2007 | -0.14511 | -122.7292 | 0.18948 | -0.10496 | 0.32511 | -122.5493 | 0.06515 | 0.036989 | 0.01233 | 0.16234 | 0.27469 | -0.17081 | -0.2191 | 0.23208 | 0.001796 | 0.58067 | 0.052153 | -0.17993 | -0.29264 | 0.13743 | 122.5623 | -0.025341 | 122.8465 | 122.7937 | 0.23143 | 0.087004 | -0.3585 | 122.9709 | 122.6764 | 123.1065 | 122.6363 | -122.737 | 122.9437 | 123.0561 | 122.6106 | 122.8184 | -0.40678
644.8906 | 122.9919 | -122.8363 | 0.21973 | 1.4211e-13 | -0.015346 | -0.00049791 | 0.062272 | -0.010491 | 0.059667 | 0.0056466 | 0.0083426 | 0.0079267 | -0.0056019 | 0.033425 | 0.0058733 | -122.1961 | -0.14511 | -122.7384 | 0.18948 | -0.095798 | 0.32511 | -122.5447 | 0.06515 | 0.041567 | 0.007751 | 0.16692 | 0.26553 | -0.17081 | -0.2191 | 0.29159 | -0.030248 | 0.64018 | 0.097928 | -0.19367 | -0.31552 | 0.10538 | 122.6172 | -0.052806 | 122.9015 | 122.8441 | 0.22685 | 0.045803 | -0.39054 | 123.0258 | 122.7405 | 123.1614 | 122.6912 | -122.7644 | 123.0032 | 123.1018 | 122.6655 | 122.8779 | -0.43882
646.5781 | 123.1064 | -122.7676 | 0.1831 | 1.4211e-13 | -0.014919 | -0.00071151 | 0.062913 | -0.010491 | 0.059667 | -0.0019839 | 0.0085562 | 0.0083539 | -0.0056019 | 0.032998 | 0.0063007 | -122.1915 | -0.15427 | -122.7292 | 0.18948 | -0.086641 | 0.31137 | -122.5401 | 0.06515 | 0.041567 | 0.007751 | 0.16234 | 0.27011 | -0.17997 | -0.21452 | 0.22751 | 0.006374 | 0.57609 | 0.03842 | -0.18909 | -0.26975 | 0.12827 | 122.5531 | -0.020763 | 122.8328 | 122.7754 | 0.22227 | 0.087003 | -0.36308 | 122.9571 | 122.681 | 123.079 | 122.6134 | -122.7232 | 122.93 | 123.0377 | 122.5877 | 122.8092 | -0.39762
648.2656 | 122.9691 | -122.8226 | 0.23346 | 1.4211e-13 | -0.015346 | -0.00028411 | 0.062485 | -0.010704 | 0.060095 | -0.0019839 | 0.0085562 | 0.0079267 | -0.0064565 | 0.032998 | 0.0065143 | -122.187 | -0.14511 | -122.7292 | 0.1849 | -0.09122 | 0.35258 | -122.5401 | 0.069728 | 0.046146 | 0.003172 | 0.16234 | 0.27469 | -0.17081 | -0.21452 | 0.28244 | -0.048558 | 0.6356 | 0.093352 | -0.18909 | -0.32468 | 0.11912 | 122.6081 | -0.071117 | 122.8923 | 122.8257 | 0.21769 | 0.041228 | -0.40427 | 123.0075 | 122.7314 | 123.1752 | 122.6775 | -122.7736 | 122.9849 | 123.0973 | 122.6518 | 122.8687 | -0.44798
650.0156 | 123.0927 | -122.7859 | 0.18768 | 1.4211e-13 | -0.015346 | -0.00071151 | 0.062913 | -0.010704 | 0.060095 | -0.0019839 | 0.0085562 | 0.0083539 | -0.0056019 | 0.033211 | 0.0060869 | -122.187 | -0.14511 | -122.7292 | 0.19406 | -0.095798 | 0.33427 | -122.5401 | 0.06515 | 0.036989 | 0.01233 | 0.16234 | 0.27011 | -0.17081 | -0.2191 | 0.24582 | 0.006375 | 0.59898 | 0.056731 | -0.18909 | -0.28348 | 0.14658 | 122.5669 | -0.025341 | 122.8511 | 122.7983 | 0.23143 | 0.082425 | -0.3585 | 122.98 | 122.6902 | 123.1202 | 122.6408 | -122.7278 | 122.9483 | 123.0561 | 122.6151 | 122.8229 | -0.40678
651.75 | 123.0057 | -122.818 | 0.21515 | 1.4211e-13 | -0.01556 | -0.00049791 | 0.062485 | -0.010918 | 0.060095 | 0.0056466 | 0.0083426 | 0.0083539 | -0.0060291 | 0.033211 | 0.0060869 | -122.187 | -0.14053 | -122.7292 | 0.18948 | -0.10038 | 0.32969 | -122.5356 | 0.069728 | 0.046146 | -0.001407 | 0.16692 | 0.27469 | -0.17081 | -0.21452 | 0.28244 | -0.02567 | 0.63103 | 0.088774 | -0.19367 | -0.31553 | 0.11454 | 122.6035 | -0.048228 | 122.8877 | 122.8166 | 0.21311 | 0.059538 | -0.38596 | 123.0075 | 122.7176 | 123.1477 | 122.6775 | -122.7507 | 122.9849 | 123.0927 | 122.6472 | 122.8641 | -0.42967
653.5 | 123.1064 | -122.7631 | 0.17395 | 1.4211e-13 | -0.015132 | -0.00049791 | 0.062699 | -0.010918 | 0.059881 | 0.0056466 | 0.0083426 | 0.0083539 | -0.0058155 | 0.033211 | 0.0063007 | -122.187 | -0.14969 | -122.7292 | 0.1849 | -0.086641 | 0.35716 | -122.5356 | 0.060571 | 0.041567 | 0.003172 | 0.16692 | 0.27469 | -0.18455 | -0.21452 | 0.22751 | 0.010951 | 0.57609 | 0.033843 | -0.19367 | -0.26059 | 0.18321 | 122.5485 | -0.007029 | 122.8236 | 122.7662 | 0.21769 | 0.10074 | -0.3585 | 122.948 | 122.6764 | 123.1202 | 122.6134 | -122.7095 | 122.93 | 123.0377 | 122.5785 | 122.8046 | -0.38847
655.2031 | 123.0652 | -122.7859 | 0.19226 | 1.4211e-13 | -0.015132 | -0.00071151 | 0.062699 | -0.010704 | 0.059667 | 0.013277 | 0.0083426 | 0.0081403 | -0.0053883 | 0.033211 | 0.0063007 | -122.187 | -0.14511 | -122.7246 | 0.1849 | -0.10038 | 0.32511 | -122.5356 | 0.074307 | 0.041567 | 0.007751 | 0.16234 | 0.27469 | -0.17081 | -0.21452 | 0.2504 | -0.00736 | 0.59898 | 0.061309 | -0.18909 | -0.29264 | 0.13285 | 122.5714 | -0.029919 | 122.8603 | 122.7937 | 0.22227 | 0.082426 | -0.36308 | 122.9709 | 122.6856 | 123.1111 | 122.6408 | -122.7278 | 122.9483 | 123.0606 | 122.6151 | 122.8275 | -0.40678
656.9375 | 123.0011 | -122.8226 | 0.20599 | 1.4211e-13 | -0.015346 | -0.00028411 | 0.063126 | -0.010704 | 0.059667 | 0.0056466 | 0.0083426 | 0.0083539 | -0.0058155 | 0.033211 | 0.0067279 | -122.187 | -0.15427 | -122.7246 | 0.19406 | -0.09122 | 0.36174 | -122.5401 | 0.06515 | 0.041567 | 0.007751 | 0.16692 | 0.27011 | -0.17081 | -0.20994 | 0.28244 | -0.011936 | 0.6356 | 0.09793 | -0.18451 | -0.29721 | 0.15574 | 122.6126 | -0.039073 | 122.8877 | 122.8303 | 0.21769 | 0.064114 | -0.37681 | 123.0166 | 122.7314 | 123.1843 | 122.6683 | -122.7461 | 122.9895 | 123.0927 | 122.6518 | 122.8641 | -0.41593
658.6719 | 123.0331 | -122.8088 | 0.21973 | 1.4211e-13 | -0.015346 | -0.00049791 | 0.062699 | -0.011345 | 0.059667 | -0.0019839 | 0.008129 | 0.0085677 | -0.0056019 | 0.032998 | 0.0058733 | -122.1824 | -0.13595 | -122.7246 | 0.18948 | -0.10038 | 0.36174 | -122.5401 | 0.06515 | 0.046146 | 0.007751 | 0.16692 | 0.27926 | -0.16624 | -0.21452 | 0.26871 | -0.030248 | 0.62645 | 0.084197 | -0.18451 | -0.3201 | 0.14201 | 122.5943 | -0.052806 | 122.874 | 122.8166 | 0.22227 | 0.059538 | -0.38596 | 122.9983 | 122.7085 | 123.1706 | 122.6729 | -122.7599 | 122.9758 | 123.0881 | 122.6426 | 122.855 | -0.43424
660.3594 | 122.9874 | -122.7859 | 0.21515 | 1.4211e-13 | -0.015346 | -0.00028411 | 0.063126 | -0.010704 | 0.059881 | 0.0056466 | 0.0085562 | 0.0081403 | -0.0058155 | 0.033425 | 0.0060869 | -122.1824 | -0.14511 | -122.7292 | 0.18948 | -0.09122 | 0.32969 | -122.5447 | 0.06515 | 0.041567 | 0.01233 | 0.16234 | 0.27011 | -0.17081 | -0.2191 | 0.24124 | -0.02567 | 0.60356 | 0.056731 | -0.18451 | -0.30637 | 0.11454 | 122.5669 | -0.052807 | 122.8511 | 122.7983 | 0.23143 | 0.054959 | -0.38596 | 122.9754 | 122.6947 | 123.1156 | 122.6408 | -122.7599 | 122.9483 | 123.0561 | 122.6151 | 122.8275 | -0.43424
662.0938 | 123.0881 | -122.7768 | 0.19684 | 1.4211e-13 | -0.01556 | -7.051e-05 | 0.063126 | -0.010491 | 0.060095 | 0.0056466 | 0.0089834 | 0.0083539 | -0.0056019 | 0.033425 | 0.0065143 | -122.1778 | -0.14969 | -122.7201 | 0.19406 | -0.10038 | 0.36632 | -122.531 | 0.06515 | 0.046146 | 0.007751 | 0.16234 | 0.27469 | -0.17081 | -0.22367 | 0.24582 | -0.00278 | 0.59898 | 0.056731 | -0.18909 | -0.29722 | 0.16948 | 122.5531 | -0.034496 | 122.8419 | 122.7845 | 0.23142 | 0.077849 | -0.36765 | 122.9709 | 122.6764 | 123.1431 | 122.6271 | -122.7278 | 122.9391 | 123.0515 | 122.606 | 122.8229 | -0.42051
663.7812 | 122.9874 | -122.8409 | 0.21515 | 1.4211e-13 | -0.015346 | -0.00028411 | 0.062485 | -0.010918 | 0.060095 | 0.013277 | 0.0085562 | 0.0083539 | -0.0058155 | 0.033211 | 0.0065143 | -122.1824 | -0.14053 | -122.7201 | 0.19406 | -0.095798 | 0.348 | -122.5401 | 0.078886 | 0.041567 | 0.007751 | 0.16234 | 0.27469 | -0.17539 | -0.20994 | 0.30075 | -0.021091 | 0.65849 | 0.12082 | -0.17993 | -0.31095 | 0.13285 | 122.6309 | -0.052807 | 122.9198 | 122.8486 | 0.21769 | 0.059538 | -0.39054 | 123.0349 | 122.7451 | 123.1889 | 122.7004 | -122.7553 | 123.0032 | 123.1156 | 122.6655 | 122.8824 | -0.42509
665.5312 | 123.111 | -122.7676 | 0.17853 | 1.4211e-13 | -0.015346 | -0.00049791 | 0.062485 | -0.010704 | 0.059881 | 0.0056466 | 0.0085562 | 0.0083539 | -0.0060291 | 0.033425 | 0.0063007 | -122.1824 | -0.14969 | -122.7155 | 0.1849 | -0.10038 | 0.33427 | -122.531 | 0.069728 | 0.046146 | 0.007751 | 0.16234 | 0.27011 | -0.17081 | -0.2191 | 0.23667 | 0.006373 | 0.58525 | 0.052155 | -0.18451 | -0.2789 | 0.15574 | 122.5485 | -0.016186 | 122.8374 | 122.7754 | 0.22685 | 0.09158 | -0.34934 | 122.9525 | 122.6673 | 123.1019 | 122.618 | -122.7095 | 122.93 | 123.0377 | 122.5968 | 122.8138 | -0.39762
667.2656 | 123.0148 | -122.8134 | 0.21973 | 1.4211e-13 | -0.015773 | -7.051e-05 | 0.062913 | -0.010704 | 0.060095 | -0.0096144 | 0.0083426 | 0.0081403 | -0.0058155 | 0.033425 | 0.0060869 | -122.1778 | -0.14969 | -122.7246 | 0.19406 | -0.095798 | 0.36174 | -122.5356 | 0.06515 | 0.041567 | 0.003172 | 0.16234 | 0.27011 | -0.16624 | -0.22367 | 0.27786 | -0.025669 | 0.6356 | 0.088775 | -0.18909 | -0.31552 | 0.14201 | 122.5897 | -0.057385 | 122.8786 | 122.8166 | 0.22685 | 0.050381 | -0.38596 | 123.0075 | 122.7176 | 123.1752 | 122.6637 | -122.7553 | 122.9758 | 123.0835 | 122.6472 | 122.855 | -0.4434
669.0156 | 123.0652 | -122.7768 | 0.19684 | 1.4211e-13 | -0.01556 | -0.00071151 | 0.062272 | -0.010918 | 0.059881 | 0.013277 | 0.008129 | 0.0083539 | -0.0058155 | 0.033425 | 0.0063007 | -122.1732 | -0.14969 | -122.7109 | 0.18948 | -0.095798 | 0.35716 | -122.5218 | 0.055992 | 0.036989 | 0.01233 | 0.16234 | 0.27469 | -0.17081 | -0.2191 | 0.25498 | -0.007359 | 0.60356 | 0.065888 | -0.18909 | -0.29264 | 0.16032 | 122.5577 | -0.034496 | 122.8328 | 122.7891 | 0.23143 | 0.077849 | -0.36765 | 122.9663 | 122.681 | 123.134 | 122.6271 | -122.7187 | 122.9391 | 123.0515 | 122.606 | 122.8138 | -0.41593
670.7031 | 122.9599 | -122.8043 | 0.20599 | 1.4211e-13 | -0.015773 | -0.00071151 | 0.062699 | -0.010704 | 0.059881 | -0.0019839 | 0.008129 | 0.0079267 | -0.0058155 | 0.033639 | 0.0063007 | -122.1824 | -0.14511 | -122.7109 | 0.19406 | -0.095798 | 0.32511 | -122.5264 | 0.06515 | 0.041567 | 0.003172 | 0.16692 | 0.27469 | -0.17081 | -0.20994 | 0.27787 | -0.011936 | 0.62187 | 0.093354 | -0.18451 | -0.30179 | 0.11912 | 122.5943 | -0.039073 | 122.8694 | 122.8074 | 0.21311 | 0.068693 | -0.37681 | 122.9983 | 122.7085 | 123.1294 | 122.6592 | -122.7324 | 122.9712 | 123.0789 | 122.6334 | 122.8458 | -0.41593
672.4531 | 123.0057 | -122.7905 | 0.21973 | 1.4211e-13 | -0.015773 | -0.00049791 | 0.062699 | -0.010918 | 0.059881 | -0.0019839 | 0.0083426 | 0.0083539 | -0.0058155 | 0.033211 | 0.0058733 | -122.1778 | -0.14969 | -122.7018 | 0.19406 | -0.086641 | 0.36632 | -122.5401 | 0.06515 | 0.046146 | 0.01233 | 0.16692 | 0.27926 | -0.17081 | -0.20994 | 0.2504 | -0.025669 | 0.61272 | 0.088777 | -0.16162 | -0.30637 | 0.14659 | 122.5806 | -0.052806 | 122.8557 | 122.8029 | 0.22227 | 0.059538 | -0.39054 | 122.9846 | 122.7039 | 123.1568 | 122.6408 | -122.7599 | 122.9574 | 123.0698 | 122.6197 | 122.8367 | -0.42966
674.1406 | 123.056 | -122.7676 | 0.19684 | 1.4211e-13 | -0.01556 | -0.00049791 | 0.062485 | -0.010704 | 0.059667 | -0.0019839 | 0.0083426 | 0.0081403 | -0.0058155 | 0.033425 | 0.0060869 | -122.1732 | -0.14511 | -122.7018 | 0.19406 | -0.09122 | 0.35258 | -122.5264 | 0.06515 | 0.046146 | 0.007751 | 0.16234 | 0.27011 | -0.17081 | -0.21452 | 0.24125 | -0.00278 | 0.59441 | 0.065889 | -0.17536 | -0.28806 | 0.15574 | 122.5531 | -0.034496 | 122.8328 | 122.7754 | 0.22227 | 0.07327 | -0.36765 | 122.9617 | 122.6764 | 123.1202 | 122.6225 | -122.7232 | 122.93 | 123.0377 | 122.5968 | 122.8138 | -0.41135
675.8906 | 123.0606 | -122.7402 | 0.18768 | 1.4211e-13 | -0.01556 | -0.00071151 | 0.062699 | -0.010918 | 0.059667 | 0.0056466 | 0.008129 | 0.0083539 | -0.0058155 | 0.033639 | 0.0063007 | -122.1641 | -0.14969 | -122.7063 | 0.18948 | -0.086641 | 0.36174 | -122.5218 | 0.069728 | 0.046146 | 0.01233 | 0.15776 | 0.27469 | -0.17081 | -0.2191 | 0.21836 | 0.001796 | 0.5761 | 0.033845 | -0.18451 | -0.27432 | 0.17406 | 122.5211 | -0.029919 | 122.8099 | 122.7525 | 0.23143 | 0.087004 | -0.3585 | 122.9297 | 122.6535 | 123.1019 | 122.5905 | -122.7095 | 122.8979 | 123.0149 | 122.5694 | 122.7863 | -0.40678
677.625 | 122.9736 | -122.7951 | 0.20142 | 1.4211e-13 | -0.015773 | -0.00028411 | 0.062699 | -0.010918 | 0.059454 | 0.013277 | 0.0083426 | 0.0083539 | -0.0060291 | 0.033425 | 0.0060869 | -122.1732 | -0.14969 | -122.7063 | 0.20321 | -0.086641 | 0.33427 | -122.5172 | 0.069728 | 0.041567 | 0.003172 | 0.16692 | 0.27011 | -0.17539 | -0.21452 | 0.27787 | 0.001798 | 0.62187 | 0.088777 | -0.18909 | -0.28806 | 0.13285 | 122.5806 | -0.034495 | 122.8648 | 122.7983 | 0.21769 | 0.068692 | -0.37681 | 122.9983 | 122.7085 | 123.1294 | 122.6454 | -122.7187 | 122.962 | 123.0652 | 122.6197 | 122.8367 | -0.41593
679.3594 | 122.9645 | -122.7997 | 0.23804 | 1.4211e-13 | -0.015773 | -0.00049791 | 0.062699 | -0.010491 | 0.059667 | 0.0056466 | 0.008129 | 0.0081403 | -0.0058155 | 0.033639 | 0.0060869 | -122.1687 | -0.14969 | -122.7109 | 0.19406 | -0.09122 | 0.348 | -122.5264 | 0.060571 | 0.041567 | 0.01233 | 0.16692 | 0.27469 | -0.17081 | -0.20994 | 0.27329 | -0.043979 | 0.63103 | 0.088777 | -0.18451 | -0.32926 | 0.10997 | 122.5897 | -0.071116 | 122.8603 | 122.812 | 0.22227 | 0.03665 | -0.40885 | 122.9937 | 122.7085 | 123.1477 | 122.65 | -122.7644 | 122.9666 | 123.0744 | 122.6289 | 122.8413 | -0.44797
681.1094 | 123.111 | -122.7585 | 0.16937 | 1.4211e-13 | -0.015773 | -0.00049791 | 0.062699 | -0.010918 | 0.059881 | 0.0056466 | 0.0083426 | 0.0083539 | -0.0056019 | 0.033425 | 0.0060869 | -122.1595 | -0.14511 | -122.7063 | 0.19406 | -0.09122 | 0.33427 | -122.5172 | 0.06515 | 0.046146 | 0.007751 | 0.16692 | 0.27469 | -0.17081 | -0.2191 | 0.24125 | 0.024685 | 0.59899 | 0.052156 | -0.18909 | -0.26059 | 0.16489 | 122.5394 | -0.002452 | 122.8236 | 122.7662 | 0.22685 | 0.10531 | -0.34019 | 122.9525 | 122.6673 | 123.0928 | 122.6134 | -122.6866 | 122.9254 | 123.0332 | 122.5877 | 122.8046 | -0.38847
682.8594 | 123.0698 | -122.7676 | 0.20142 | 1.4211e-13 | -0.01556 | -0.00071151 | 0.062913 | -0.010918 | 0.060095 | -0.0019839 | 0.0083426 | 0.0077131 | -0.0056019 | 0.033639 | 0.0058733 | -122.1732 | -0.14511 | -122.7155 | 0.18948 | -0.095798 | 0.36174 | -122.531 | 0.069728 | 0.041567 | 0.007751 | 0.16692 | 0.27469 | -0.17081 | -0.20994 | 0.23667 | -0.011937 | 0.59441 | 0.052155 | -0.18451 | -0.29721 | 0.16032 | 122.5577 | -0.034495 | 122.8374 | 122.7754 | 0.21769 | 0.073271 | -0.37223 | 122.9571 | 122.6718 | 123.1294 | 122.6225 | -122.7324 | 122.9346 | 123.0423 | 122.5968 | 122.8092 | -0.41135
684.5469 | 123.0835 | -122.7539 | 0.20142 | 1.4211e-13 | -0.015987 | -0.00049791 | 0.062699 | -0.011132 | 0.060095 | -0.0019839 | 0.0079152 | 0.0083539 | -0.0058155 | 0.033211 | 0.0058733 | -122.1641 | -0.15427 | -122.7109 | 0.19406 | -0.10038 | 0.36174 | -122.5218 | 0.06515 | 0.046146 | 0.01233 | 0.16692 | 0.27469 | -0.16624 | -0.21452 | 0.23209 | -0.007358 | 0.58983 | 0.043 | -0.18909 | -0.30179 | 0.16032 | 122.5394 | -0.034495 | 122.8191 | 122.7662 | 0.22685 | 0.073271 | -0.36765 | 122.948 | 122.6535 | 123.1156 | 122.5996 | -122.7232 | 122.9208 | 123.0286 | 122.5877 | 122.8001 | -0.41593
686.2969 | 122.9599 | -122.7814 | 0.21973 | 1.4211e-13 | -0.01556 | -0.00049791 | 0.062699 | -0.010918 | 0.060095 | 0.0056466 | 0.008129 | 0.0081403 | -0.0058155 | 0.033639 | 0.0065143 | -122.1595 | -0.14969 | -122.7018 | 0.19406 | -0.09122 | 0.35258 | -122.5264 | 0.069728 | 0.041567 | 0.007751 | 0.16692 | 0.27469 | -0.17539 | -0.21452 | 0.25498 | -0.025669 | 0.62188 | 0.079622 | -0.17536 | -0.31095 | 0.13286 | 122.5669 | -0.052806 | 122.8511 | 122.7891 | 0.22227 | 0.05496 | -0.39512 | 122.9754 | 122.6902 | 123.134 | 122.6317 | -122.7461 | 122.9483 | 123.0561 | 122.606 | 122.8229 | -0.43424
688.0469 | 123.0835 | -122.7631 | 0.17395 | 1.4211e-13 | -0.015773 | -0.00071151 | 0.062913 | -0.010704 | 0.059881 | 0.0056466 | 0.0085562 | 0.0081403 | -0.0056019 | 0.033425 | 0.0058733 | -122.1641 | -0.14511 | -122.6972 | 0.19406 | -0.095798 | 0.36632 | -122.5218 | 0.069728 | 0.041567 | 0.01233 | 0.16234 | 0.27926 | -0.17081 | -0.22367 | 0.24125 | 0.020108 | 0.59899 | 0.065891 | -0.17536 | -0.26975 | 0.19237 | 122.5394 | -0.011608 | 122.8328 | 122.7754 | 0.236 | 0.10531 | -0.34476 | 122.9571 | 122.6673 | 123.1294 | 122.618 | -122.6958 | 122.9254 | 123.0423 | 122.5922 | 122.8046 | -0.39762
689.75 | 122.9599 | -122.8043 | 0.21515 | 1.4211e-13 | -0.01556 | -0.00071151 | 0.062699 | -0.010918 | 0.059667 | 0.0056466 | 0.008129 | 0.0081403 | -0.0058155 | 0.033211 | 0.0060869 | -122.1778 | -0.14511 | -122.7018 | 0.19406 | -0.09122 | 0.31137 | -122.5172 | 0.06515 | 0.041567 | 0.007751 | 0.1715 | 0.27011 | -0.16166 | -0.22367 | 0.28702 | -0.021091 | 0.62645 | 0.10251 | -0.18451 | -0.30637 | 0.096225 | 122.5806 | -0.04365 | 122.8694 | 122.812 | 0.23142 | 0.054959 | -0.37681 | 122.9983 | 122.713 | 123.1156 | 122.6592 | -122.7324 | 122.9758 | 123.0744 | 122.6426 | 122.8458 | -0.43882
691.4844 | 122.937 | -122.7859 | 0.19684 | 1.4211e-13 | -0.015773 | -0.00049791 | 0.062699 | -0.010918 | 0.059667 | 0.0056466 | 0.0085562 | 0.0079267 | -0.0058155 | 0.033639 | 0.0063007 | -122.1687 | -0.14969 | -122.6972 | 0.18948 | -0.095798 | 0.32969 | -122.5264 | 0.060571 | 0.046146 | 0.01233 | 0.16692 | 0.27011 | -0.17539 | -0.2191 | 0.25956 | -0.007359 | 0.6173 | 0.088779 | -0.17078 | -0.29264 | 0.13285 | 122.5669 | -0.029917 | 122.8465 | 122.7983 | 0.23143 | 0.07327 | -0.37223 | 122.9754 | 122.6902 | 123.1156 | 122.6363 | -122.7232 | 122.9529 | 123.0561 | 122.6106 | 122.8321 | -0.41593
693.2188 | 123.0286 | -122.7814 | 0.20599 | 1.4211e-13 | -0.01556 | -0.00028411 | 0.062913 | -0.010918 | 0.059667 | -0.0019839 | 0.008129 | 0.0079267 | -0.0060291 | 0.033211 | 0.0056597 | -122.1641 | -0.15427 | -122.7018 | 0.18948 | -0.086641 | 0.34342 | -122.5172 | 0.060571 | 0.046146 | 0.007751 | 0.16692 | 0.27011 | -0.17081 | -0.21452 | 0.26414 | -0.016515 | 0.6173 | 0.079622 | -0.18451 | -0.29263 | 0.13743 | 122.5669 | -0.039073 | 122.8419 | 122.7891 | 0.22227 | 0.064114 | -0.37681 | 122.9709 | 122.6947 | 123.1248 | 122.6271 | -122.7232 | 122.9483 | 123.0515 | 122.6106 | 122.8275 | -0.42051
694.9688 | 122.937 | -122.7768 | 0.21057 | 1.4211e-13 | -0.015773 | -0.00071151 | 0.062485 | -0.010704 | 0.059667 | 0.013277 | 0.0085562 | 0.0083539 | -0.0060291 | 0.033639 | 0.0060869 | -122.1687 | -0.15427 | -122.7109 | 0.18948 | -0.09122 | 0.3709 | -122.5218 | 0.060571 | 0.055303 | -0.001407 | 0.16234 | 0.27011 | -0.17081 | -0.21452 | 0.25498 | -0.021092 | 0.60814 | 0.065888 | -0.18909 | -0.30179 | 0.16032 | 122.5623 | -0.048229 | 122.8374 | 122.7754 | 0.21311 | 0.059537 | -0.38139 | 122.9663 | 122.6856 | 123.1477 | 122.6225 | -122.7324 | 122.9391 | 123.0469 | 122.606 | 122.8321 | -0.42509
696.7031 | 122.9507 | -122.7997 | 0.21057 | 1.4211e-13 | -0.015987 | -0.00071151 | 0.063126 | -0.011132 | 0.060095 | 0.0056466 | 0.008129 | 0.0081403 | -0.0060291 | 0.033425 | 0.0060869 | -122.1641 | -0.15427 | -122.6972 | 0.18948 | -0.095798 | 0.35716 | -122.5264 | 0.060571 | 0.041567 | 0.01233 | 0.16692 | 0.27469 | -0.16624 | -0.20536 | 0.27329 | -0.021092 | 0.63561 | 0.10251 | -0.17078 | -0.30637 | 0.14659 | 122.5943 | -0.04365 | 122.8603 | 122.812 | 0.21769 | 0.064116 | -0.37681 | 122.9892 | 122.7039 | 123.1568 | 122.6454 | -122.737 | 122.9666 | 123.0744 | 122.6334 | 122.8413 | -0.41593
698.4062 | 123.0011 | -122.7814 | 0.21973 | 1.4211e-13 | -0.015773 | -0.00071151 | 0.062485 | -0.010918 | 0.059881 | -0.0019839 | 0.0085562 | 0.0081403 | -0.0058155 | 0.033425 | 0.0060869 | -122.1595 | -0.14969 | -122.7018 | 0.18948 | -0.09122 | 0.35716 | -122.5218 | 0.069728 | 0.055303 | 0.016908 | 0.15776 | 0.27011 | -0.16624 | -0.2191 | 0.25956 | -0.030248 | 0.62188 | 0.079622 | -0.17994 | -0.31095 | 0.13743 | 122.5623 | -0.061963 | 122.8511 | 122.7983 | 0.236 | 0.050381 | -0.38596 | 122.9709 | 122.6902 | 123.1385 | 122.6317 | -122.7415 | 122.9391 | 123.0515 | 122.6151 | 122.8367 | -0.43882
700.1562 | 123.0652 | -122.7722 | 0.17395 | 1.4211e-13 | -0.015773 | -0.00049791 | 0.062485 | -0.010918 | 0.059454 | 0.013277 | 0.008129 | 0.0083539 | -0.0060291 | 0.033211 | 0.0063007 | -122.1687 | -0.14511 | -122.7063 | 0.18948 | -0.09122 | 0.32969 | -122.5172 | 0.06515 | 0.046146 | 0.007751 | 0.16692 | 0.27469 | -0.17539 | -0.22367 | 0.25498 | 0.015529 | 0.60356 | 0.065889 | -0.18909 | -0.26517 | 0.15574 | 122.5485 | -0.007029 | 122.8374 | 122.78 | 0.23142 | 0.10074 | -0.34934 | 122.9617 | 122.681 | 123.1019 | 122.6271 | -122.6912 | 122.9391 | 123.0469 | 122.5968 | 122.8184 | -0.39762
701.8281 | 123.0789 | -122.7905 | 0.16479 | 1.4211e-13 | -0.015773 | -0.00028411 | 0.062699 | -0.010704 | 0.060095 | 0.0056466 | 0.008129 | 0.0081403 | -0.0060291 | 0.033852 | 0.0060869 | -122.1687 | -0.14969 | -122.6972 | 0.18948 | -0.09122 | 0.348 | -122.5218 | 0.069728 | 0.036989 | 0.01233 | 0.16234 | 0.27011 | -0.17539 | -0.2191 | 0.26871 | 0.024684 | 0.62187 | 0.093356 | -0.17536 | -0.25601 | 0.18321 | 122.5714 | -0.002453 | 122.8603 | 122.8029 | 0.23143 | 0.10531 | -0.34019 | 122.98 | 122.6993 | 123.1385 | 122.6408 | -122.6866 | 122.9529 | 123.0606 | 122.6151 | 122.8275 | -0.38389
703.5625 | 122.9507 | -122.8317 | 0.23346 | 1.4211e-13 | -0.01556 | -0.00049791 | 0.062272 | -0.010918 | 0.059454 | -0.0019839 | 0.0085562 | 0.0085677 | -0.0058155 | 0.033852 | 0.0060869 | -122.1595 | -0.14511 | -122.6972 | 0.18948 | -0.10038 | 0.31595 | -122.5218 | 0.069728 | 0.041567 | 0.007751 | 0.16234 | 0.27469 | -0.16624 | -0.20994 | 0.30991 | -0.04398 | 0.67223 | 0.13456 | -0.17536 | -0.33384 | 0.082494 | 122.6218 | -0.071117 | 122.9015 | 122.8395 | 0.21769 | 0.041228 | -0.3997 | 123.0212 | 122.7313 | 123.1477 | 122.6866 | -122.7553 | 122.9941 | 123.1064 | 122.6655 | 122.8733 | -0.4434
705.25 | 123.056 | -122.7539 | 0.1831 | 1.4211e-13 | -0.016414 | -0.00028411 | 0.062699 | -0.011132 | 0.059667 | 0.0056466 | 0.0083426 | 0.0083539 | -0.0058155 | 0.033852 | 0.0060869 | -122.1595 | -0.15884 | -122.6972 | 0.18948 | -0.10496 | 0.36632 | -122.5172 | 0.069728 | 0.046146 | 0.01233 | 0.16234 | 0.27011 | -0.17081 | -0.20994 | 0.23667 | 0.006374 | 0.59441 | 0.056735 | -0.17994 | -0.28806 | 0.18321 | 122.544 | -0.020763 | 122.8236 | 122.7662 | 0.22227 | 0.087003 | -0.35392 | 122.9434 | 122.6489 | 123.1202 | 122.5951 | -122.7003 | 122.9162 | 123.024 | 122.5831 | 122.8001 | -0.39304
707 | 123.0881 | -122.7356 | 0.1831 | 1.4211e-13 | -0.015987 | -0.00028411 | 0.063126 | -0.010918 | 0.059881 | 0.013277 | 0.008129 | 0.0079267 | -0.0058155 | 0.033639 | 0.0063007 | -122.1549 | -0.15427 | -122.7018 | 0.1849 | -0.095798 | 0.35258 | -122.5127 | 0.06515 | 0.041567 | 0.007751 | 0.16234 | 0.27469 | -0.17539 | -0.21452 | 0.22294 | 0.001796 | 0.58068 | 0.033846 | -0.18909 | -0.2789 | 0.16948 | 122.5211 | -0.020763 | 122.8007 | 122.7433 | 0.22227 | 0.091582 | -0.3585 | 122.9205 | 122.6398 | 123.0882 | 122.5813 | -122.6958 | 122.8979 | 123.0103 | 122.5602 | 122.7772 | -0.39762
708.7344 | 123.0789 | -122.7448 | 0.1831 | 1.4211e-13 | -0.01556 | -0.00049791 | 0.062485 | -0.010918 | 0.059881 | -0.0019839 | 0.0083426 | 0.0079267 | -0.0053883 | 0.033852 | 0.0058733 | -122.1595 | -0.15427 | -122.7018 | 0.1849 | -0.09122 | 0.36174 | -122.5172 | 0.069728 | 0.050725 | 0.007751 | 0.1715 | 0.27926 | -0.17081 | -0.21452 | 0.22751 | 0.001796 | 0.58525 | 0.043001 | -0.18451 | -0.27432 | 0.17863 | 122.5302 | -0.011606 | 122.8145 | 122.7525 | 0.22227 | 0.09616 | -0.35392 | 122.9297 | 122.6535 | 123.1065 | 122.5905 | -122.7003 | 122.9162 | 123.024 | 122.5739 | 122.7955 | -0.39762
710.4844 | 123.0881 | -122.731 | 0.19226 | 1.4211e-13 | -0.01556 | -0.00049791 | 0.062913 | -0.010704 | 0.059667 | 0.013277 | 0.0083426 | 0.0079267 | -0.0060291 | 0.033852 | 0.0058733 | -122.1503 | -0.14969 | -122.6972 | 0.1849 | -0.09122 | 0.33427 | -122.5081 | 0.06515 | 0.041567 | 0.007751 | 0.16234 | 0.27926 | -0.17539 | -0.2191 | 0.22294 | -0.00736 | 0.58068 | 0.033847 | -0.18909 | -0.28348 | 0.14201 | 122.5119 | -0.029919 | 122.7962 | 122.7388 | 0.22685 | 0.087004 | -0.36765 | 122.9159 | 122.6398 | 123.0653 | 122.5813 | -122.7003 | 122.8934 | 123.0103 | 122.5556 | 122.7726 | -0.41136
712.1719 | 123.0835 | -122.7448 | 0.19684 | 1.4211e-13 | -0.015773 | -0.00071151 | 0.062485 | -0.010918 | 0.059667 | 0.0056466 | 0.008129 | 0.0083539 | -0.0060291 | 0.033211 | 0.0060869 | -122.1503 | -0.15427 | -122.6926 | 0.18948 | -0.095798 | 0.36632 | -122.5127 | 0.060571 | 0.046146 | 0.01233 | 0.16234 | 0.27926 | -0.17539 | -0.20994 | 0.23209 | -0.007359 | 0.59441 | 0.052158 | -0.17994 | -0.29264 | 0.16948 | 122.5348 | -0.034496 | 122.8053 | 122.7571 | 0.22227 | 0.082427 | -0.37223 | 122.9342 | 122.649 | 123.1111 | 122.5905 | -122.7095 | 122.9071 | 123.024 | 122.5694 | 122.7909 | -0.40677
713.9219 | 123.1064 | -122.7402 | 0.17853 | 1.4211e-13 | -0.015987 | -0.00071151 | 0.062272 | -0.011132 | 0.059667 | 0.0056466 | 0.0083426 | 0.0083539 | -0.0056019 | 0.033639 | 0.0060869 | -122.1503 | -0.14969 | -122.6972 | 0.1849 | -0.095798 | 0.32053 | -122.5218 | 0.069728 | 0.046146 | 0.01233 | 0.16692 | 0.27926 | -0.17081 | -0.20994 | 0.21836 | 0.006373 | 0.58983 | 0.043002 | -0.17536 | -0.27433 | 0.142 | 122.5302 | -0.011607 | 122.8099 | 122.7525 | 0.22227 | 0.10074 | -0.34934 | 122.9251 | 122.6444 | 123.0607 | 122.5905 | -122.7003 | 122.9071 | 123.0194 | 122.5694 | 122.7863 | -0.38847
715.6719 | 123.0606 | -122.7585 | 0.19226 | 1.4211e-13 | -0.015987 | -0.00028411 | 0.062485 | -0.011132 | 0.059667 | 0.0056466 | 0.008129 | 0.0085677 | -0.0062429 | 0.033852 | 0.0060869 | -122.1503 | -0.15884 | -122.688 | 0.18032 | -0.09122 | 0.32969 | -122.5218 | 0.074307 | 0.036989 | 0.007751 | 0.16234 | 0.27469 | -0.17081 | -0.2191 | 0.23667 | -0.011938 | 0.60814 | 0.070469 | -0.1662 | -0.28348 | 0.13743 | 122.5394 | -0.029919 | 122.8328 | 122.7662 | 0.22685 | 0.082426 | -0.36308 | 122.9388 | 122.6673 | 123.0882 | 122.5996 | -122.7141 | 122.9208 | 123.0332 | 122.5877 | 122.7955 | -0.41136
717.3438 | 123.0423 | -122.7539 | 0.17853 | 1.4211e-13 | -0.015987 | -0.00092531 | 0.062485 | -0.010918 | 0.060095 | 0.0056466 | 0.0083426 | 0.0083539 | -0.0058155 | 0.033852 | 0.0058733 | -122.1503 | -0.14969 | -122.6926 | 0.19864 | -0.10038 | 0.348 | -122.5172 | 0.06515 | 0.041567 | 0.01233 | 0.16234 | 0.27926 | -0.16166 | -0.2191 | 0.23667 | 0.020108 | 0.60357 | 0.061313 | -0.17536 | -0.2789 | 0.16948 | 122.5348 | -0.016186 | 122.8191 | 122.7662 | 0.23143 | 0.10074 | -0.34019 | 122.9525 | 122.6535 | 123.1019 | 122.6042 | -122.6958 | 122.9162 | 123.0332 | 122.5922 | 122.7955 | -0.39762
719.0781 | 122.9507 | -122.7997 | 0.2243 | 1.4211e-13 | -0.015987 | -0.00049791 | 0.062272 | -0.010704 | 0.059454 | 0.0056466 | 0.0083426 | 0.0083539 | -0.0060291 | 0.033852 | 0.0058733 | -122.1549 | -0.14969 | -122.6972 | 0.19406 | -0.095798 | 0.35258 | -122.5127 | 0.06515 | 0.046146 | 0.007751 | 0.16692 | 0.28384 | -0.17081 | -0.20994 | 0.28703 | -0.030246 | 0.64476 | 0.10251 | -0.18451 | -0.3201 | 0.12828 | 122.5897 | -0.057383 | 122.8648 | 122.8074 | 0.21769 | 0.05954 | -0.39512 | 122.9937 | 122.7039 | 123.1523 | 122.65 | -122.737 | 122.9666 | 123.0835 | 122.6289 | 122.8458 | -0.43424
720.8281 | 123.0469 | -122.7356 | 0.17853 | 1.4211e-13 | -0.016201 | -0.00049791 | 0.062272 | -0.010491 | 0.059881 | 0.013277 | 0.0083426 | 0.0083539 | -0.0058155 | 0.033639 | 0.0058733 | -122.1458 | -0.14053 | -122.6834 | 0.18948 | -0.095798 | 0.34342 | -122.5081 | 0.06515 | 0.041567 | 0.01233 | 0.16692 | 0.27926 | -0.17997 | -0.21452 | 0.22752 | 0.010951 | 0.58983 | 0.05216 | -0.17536 | -0.27433 | 0.1649 | 122.5211 | -0.011607 | 122.8007 | 122.7479 | 0.22685 | 0.10074 | -0.3585 | 122.9251 | 122.6398 | 123.079 | 122.5951 | -122.6866 | 122.9025 | 123.0149 | 122.5556 | 122.7772 | -0.39304
722.5781 | 122.9782 | -122.731 | 0.21057 | 1.4211e-13 | -0.015773 | -0.00071151 | 0.062699 | -0.010918 | 0.059667 | -0.0019839 | 0.008129 | 0.0085677 | -0.0058155 | 0.034066 | 0.0058733 | -122.1503 | -0.14969 | -122.6926 | 0.18948 | -0.095798 | 0.34342 | -122.5127 | 0.06515 | 0.041567 | 0.003172 | 0.16234 | 0.28384 | -0.17539 | -0.21452 | 0.21836 | -0.021092 | 0.58068 | 0.038425 | -0.17994 | -0.30637 | 0.13285 | 122.5165 | -0.048229 | 122.7962 | 122.7342 | 0.21769 | 0.073273 | -0.38596 | 122.9205 | 122.6352 | 123.0744 | 122.5813 | -122.7232 | 122.8934 | 123.0149 | 122.5556 | 122.7726 | -0.42509
724.2656 | 122.9645 | -122.7814 | 0.21515 | 1.4211e-13 | -0.015773 | -0.00049791 | 0.062699 | -0.010704 | 0.059667 | -0.0096144 | 0.008129 | 0.0081403 | -0.0056019 | 0.03428 | 0.0065143 | -122.1549 | -0.14511 | -122.688 | 0.19406 | -0.10038 | 0.36632 | -122.5127 | 0.060571 | 0.046146 | 0.007751 | 0.16234 | 0.27469 | -0.17997 | -0.22367 | 0.26872 | -0.021091 | 0.62645 | 0.093357 | -0.17536 | -0.31553 | 0.15117 | 122.5577 | -0.052807 | 122.8419 | 122.7891 | 0.23142 | 0.059538 | -0.39512 | 122.9754 | 122.681 | 123.1477 | 122.6363 | -122.7278 | 122.9437 | 123.0561 | 122.6014 | 122.8275 | -0.43882
726.0156 | 122.9828 | -122.7859 | 0.20142 | 1.4211e-13 | -0.015987 | -0.00049791 | 0.062699 | -0.010704 | 0.059881 | -0.0019839 | 0.008129 | 0.0079267 | -0.0058155 | 0.034066 | 0.0058733 | -122.1458 | -0.14969 | -122.688 | 0.19406 | -0.09122 | 0.3709 | -122.5127 | 0.06515 | 0.046146 | 0.007751 | 0.15318 | 0.27926 | -0.17081 | -0.22367 | 0.27329 | -0.007358 | 0.64019 | 0.097935 | -0.17536 | -0.29264 | 0.16948 | 122.5623 | -0.048231 | 122.8511 | 122.7937 | 0.23142 | 0.077849 | -0.37223 | 122.98 | 122.6947 | 123.1568 | 122.6363 | -122.7141 | 122.9391 | 123.0652 | 122.6151 | 122.8321 | -0.42509
727.6875 | 123.0469 | -122.7448 | 0.17853 | 1.4211e-13 | -0.015987 | -0.00049791 | 0.062272 | -0.010704 | 0.060095 | 0.0056466 | 0.008129 | 0.0083539 | -0.0060291 | 0.034066 | 0.0060869 | -122.1458 | -0.14969 | -122.688 | 0.18948 | -0.09122 | 0.35716 | -122.5081 | 0.06515 | 0.041567 | 0.016908 | 0.16234 | 0.27926 | -0.17081 | -0.21452 | 0.23667 | 0.010951 | 0.59899 | 0.056736 | -0.17994 | -0.26975 | 0.17863 | 122.5302 | -0.016186 | 122.8099 | 122.7617 | 0.23142 | 0.10074 | -0.34934 | 122.9342 | 122.6535 | 123.1019 | 122.5951 | -122.6866 | 122.9071 | 123.024 | 122.5739 | 122.7863 | -0.39304
729.4219 | 123.0743 | -122.7356 | 0.1831 | 1.4211e-13 | -0.015773 | -0.00071151 | 0.062485 | -0.010918 | 0.059881 | -0.0019839 | 0.0083426 | 0.0081403 | -0.0062429 | 0.034066 | 0.0065143 | -122.1412 | -0.14969 | -122.688 | 0.1849 | -0.086641 | 0.36174 | -122.4989 | 0.06515 | 0.046146 | 0.01233 | 0.16234 | 0.28384 | -0.17081 | -0.2191 | 0.23668 | 0.001796 | 0.59441 | 0.047581 | -0.18909 | -0.26975 | 0.17863 | 122.5165 | -0.020763 | 122.8007 | 122.7479 | 0.23143 | 0.10074 | -0.35392 | 122.9205 | 122.649 | 123.0973 | 122.5859 | -122.682 | 122.8979 | 123.0194 | 122.5648 | 122.7817 | -0.4022
731.1094 | 122.9599 | -122.7768 | 0.21515 | 1.4211e-13 | -0.015987 | -0.00049791 | 0.062485 | -0.010918 | 0.060095 | 0.0056466 | 0.008129 | 0.0081403 | -0.0058155 | 0.03428 | 0.0063007 | -122.1503 | -0.14969 | -122.6972 | 0.18948 | -0.09122 | 0.348 | -122.5081 | 0.06515 | 0.041567 | 0.007751 | 0.16234 | 0.26553 | -0.17539 | -0.2191 | 0.26872 | -0.02567 | 0.62645 | 0.079623 | -0.18909 | -0.30637 | 0.13285 | 122.5577 | -0.052807 | 122.8419 | 122.7845 | 0.22685 | 0.050381 | -0.39054 | 122.9663 | 122.6856 | 123.1248 | 122.6271 | -122.7232 | 122.9391 | 123.0423 | 122.6014 | 122.8184 | -0.43424
732.8438 | 123.056 | -122.7768 | 0.19226 | 1.4211e-13 | -0.016201 | -0.00071151 | 0.062699 | -0.010918 | 0.059881 | 0.0056466 | 0.0077016 | 0.0079267 | -0.0062429 | 0.034066 | 0.0063007 | -122.1458 | -0.15427 | -122.6834 | 0.1849 | -0.09122 | 0.35258 | -122.5127 | 0.06515 | 0.046146 | 0.01233 | 0.16692 | 0.27469 | -0.17539 | -0.2191 | 0.26414 | -0.00736 | 0.63103 | 0.093358 | -0.17078 | -0.28348 | 0.16032 | 122.5577 | -0.02534 | 122.8419 | 122.7891 | 0.23143 | 0.082426 | -0.36765 | 122.9617 | 122.6856 | 123.1294 | 122.6225 | -122.7049 | 122.9437 | 123.0515 | 122.6014 | 122.8229 | -0.41136
734.5938 | 122.9416 | -122.7676 | 0.21057 | 1.4211e-13 | -0.015987 | -0.00049791 | 0.062913 | -0.010704 | 0.059881 | -0.0019839 | 0.0083426 | 0.0081403 | -0.0062429 | 0.03428 | 0.0060869 | -122.1458 | -0.15884 | -122.688 | 0.1849 | -0.086641 | 0.33885 | -122.5127 | 0.060571 | 0.036989 | 0.007751 | 0.1715 | 0.27469 | -0.16624 | -0.20994 | 0.25498 | -0.02567 | 0.62188 | 0.079624 | -0.17536 | -0.29721 | 0.12827 | 122.5577 | -0.039072 | 122.8282 | 122.7754 | 0.21769 | 0.064116 | -0.37681 | 122.9525 | 122.681 | 123.1065 | 122.6088 | -122.7232 | 122.9391 | 123.0423 | 122.6014 | 122.8046 | -0.42051
736.2812 | 123.0515 | -122.7219 | 0.18768 | 1.4211e-13 | -0.015987 | -0.00049791 | 0.062485 | -0.010918 | 0.059667 | 0.0056466 | 0.0083426 | 0.0077131 | -0.0062429 | 0.034066 | 0.0058733 | -122.1412 | -0.14969 | -122.688 | 0.1849 | -0.082062 | 0.32053 | -122.5218 | 0.074307 | 0.046146 | 0.007751 | 0.16692 | 0.27926 | -0.17081 | -0.21452 | 0.20005 | -0.002782 | 0.58068 | 0.033848 | -0.1662 | -0.26975 | 0.13285 | 122.5073 | -0.020762 | 122.7962 | 122.7296 | 0.22227 | 0.091582 | -0.3585 | 122.9068 | 122.6398 | 123.0424 | 122.5722 | -122.7095 | 122.8888 | 123.0011 | 122.551 | 122.768 | -0.4022
738.0312 | 123.0606 | -122.7127 | 0.17853 | 1.4211e-13 | -0.016201 | -0.00071151 | 0.062913 | -0.010918 | 0.059881 | 0.0056466 | 0.0085562 | 0.0081403 | -0.0060291 | 0.034066 | 0.0058733 | -122.132 | -0.15427 | -122.688 | 0.1849 | -0.095798 | 0.31595 | -122.5127 | 0.060571 | 0.046146 | 0.007751 | 0.16234 | 0.27926 | -0.17539 | -0.2191 | 0.20005 | 0.006373 | 0.58068 | 0.024693 | -0.17536 | -0.27433 | 0.13742 | 122.4936 | -0.016186 | 122.7733 | 122.7205 | 0.22685 | 0.10074 | -0.35392 | 122.8976 | 122.6169 | 123.0287 | 122.5584 | -122.6912 | 122.8751 | 122.992 | 122.5373 | 122.7589 | -0.39762
739.7031 | 122.9645 | -122.7676 | 0.19684 | 1.4211e-13 | -0.016201 | -0.00071151 | 0.062272 | -0.011345 | 0.059667 | 0.013277 | 0.008129 | 0.0081403 | -0.0060291 | 0.034066 | 0.0056597 | -122.1366 | -0.14511 | -122.6834 | 0.18948 | -0.095798 | 0.36174 | -122.5081 | 0.069728 | 0.036989 | -0.001407 | 0.16234 | 0.27469 | -0.17081 | -0.21452 | 0.25956 | -0.007359 | 0.63103 | 0.084203 | -0.17536 | -0.29264 | 0.1649 | 122.5531 | -0.034496 | 122.8374 | 122.7662 | 0.21311 | 0.077849 | -0.36765 | 122.9571 | 122.6718 | 123.1294 | 122.6225 | -122.7049 | 122.93 | 123.0423 | 122.5968 | 122.8046 | -0.41135
741.4531 | 122.9507 | -122.7585 | 0.2243 | 1.4211e-13 | -0.015987 | -0.00092531 | 0.062485 | -0.010918 | 0.059667 | -0.0019839 | 0.0079152 | 0.0081403 | -0.0062429 | 0.033852 | 0.0058733 | -122.1366 | -0.15884 | -122.6834 | 0.18948 | -0.095798 | 0.35258 | -122.5035 | 0.06515 | 0.046146 | 0.007751 | 0.17608 | 0.27469 | -0.16624 | -0.22367 | 0.25498 | -0.034825 | 0.62188 | 0.075048 | -0.17994 | -0.3201 | 0.12828 | 122.5348 | -0.048226 | 122.8236 | 122.7662 | 0.23142 | 0.050383 | -0.39054 | 122.948 | 122.6627 | 123.1111 | 122.5996 | -122.7278 | 122.9346 | 123.0332 | 122.5922 | 122.8046 | -0.44798
743.1406 | 122.9828 | -122.7722 | 0.20599 | 1.4211e-13 | -0.016201 | -0.00071151 | 0.062485 | -0.011132 | 0.059881 | 0.013277 | 0.008129 | 0.0081403 | -0.0058155 | 0.03428 | 0.0060869 | -122.1366 | -0.14969 | -122.6834 | 0.18948 | -0.10038 | 0.36174 | -122.5081 | 0.06515 | 0.046146 | 0.003172 | 0.16692 | 0.27926 | -0.17081 | -0.22367 | 0.26414 | -0.016515 | 0.63561 | 0.088781 | -0.17536 | -0.30637 | 0.15574 | 122.5485 | -0.039073 | 122.8374 | 122.7754 | 0.22685 | 0.073271 | -0.37681 | 122.9617 | 122.6718 | 123.134 | 122.6225 | -122.7141 | 122.9391 | 123.0515 | 122.6014 | 122.8184 | -0.42967
744.8906 | 122.9462 | -122.7539 | 0.21515 | 1.4211e-13 | -0.016414 | -0.00092531 | 0.062485 | -0.011132 | 0.059881 | 0.0056466 | 0.008129 | 0.0083539 | -0.0062429 | 0.03428 | 0.0060869 | -122.1366 | -0.15427 | -122.6834 | 0.18948 | -0.086641 | 0.36174 | -122.5127 | 0.060571 | 0.046146 | 0.003172 | 0.16234 | 0.27926 | -0.17997 | -0.21452 | 0.24125 | -0.02567 | 0.6173 | 0.07047 | -0.17078 | -0.30179 | 0.14659 | 122.5394 | -0.052807 | 122.8145 | 122.7571 | 0.21769 | 0.064116 | -0.39512 | 122.9434 | 122.6673 | 123.1156 | 122.5996 | -122.7278 | 122.9162 | 123.0332 | 122.5739 | 122.8001 | -0.42967
746.5938 | 122.9736 | -122.7768 | 0.19226 | 1.4211e-13 | -0.016201 | -7.051e-05 | 0.062485 | -0.010918 | 0.059667 | -0.0096144 | 0.008129 | 0.0081403 | -0.0058155 | 0.034493 | 0.0060869 | -122.132 | -0.14969 | -122.6834 | 0.19406 | -0.095798 | 0.33427 | -122.5127 | 0.06515 | 0.041567 | 0.007751 | 0.16234 | 0.27469 | -0.16166 | -0.2191 | 0.26414 | 0.001797 | 0.64477 | 0.093358 | -0.17078 | -0.28806 | 0.14201 | 122.5577 | -0.029919 | 122.8419 | 122.7845 | 0.22685 | 0.082426 | -0.35392 | 122.9709 | 122.681 | 123.1111 | 122.6271 | -122.7049 | 122.9391 | 123.0515 | 122.6151 | 122.8184 | -0.41136
748.3438 | 122.9645 | -122.7676 | 0.1831 | 1.4211e-13 | -0.015987 | -0.00049791 | 0.062699 | -0.011132 | 0.060095 | -0.0019839 | 0.0079152 | 0.0079267 | -0.0058155 | 0.034066 | 0.0060869 | -122.1412 | -0.15884 | -122.6789 | 0.19406 | -0.086641 | 0.36632 | -122.5081 | 0.060571 | 0.046146 | 0.003172 | 0.16234 | 0.27926 | -0.17081 | -0.2191 | 0.25956 | 0.010953 | 0.62646 | 0.088781 | -0.17078 | -0.26975 | 0.18321 | 122.5485 | -0.020763 | 122.8282 | 122.7708 | 0.22227 | 0.09616 | -0.35392 | 122.9617 | 122.681 | 123.134 | 122.6088 | -122.6912 | 122.93 | 123.0469 | 122.5968 | 122.8138 | -0.4022
750.0938 | 123.0606 | -122.7036 | 0.1831 | 1.4211e-13 | -0.015987 | -0.00049791 | 0.062699 | -0.010704 | 0.059667 | -0.0096144 | 0.0083426 | 0.0081403 | -0.0060291 | 0.03428 | 0.0060869 | -122.132 | -0.15884 | -122.6789 | 0.1849 | -0.086641 | 0.36174 | -122.4989 | 0.060571 | 0.046146 | 0.003172 | 0.16692 | 0.28384 | -0.17081 | -0.21452 | 0.20463 | 0.001796 | 0.57153 | 0.024694 | -0.17994 | -0.26975 | 0.17863 | 122.489 | -0.016184 | 122.7641 | 122.7067 | 0.21769 | 0.10074 | -0.35392 | 122.8885 | 122.6169 | 123.0653 | 122.5447 | -122.682 | 122.8705 | 122.9874 | 122.5327 | 122.7497 | -0.39762
751.7656 | 123.0194 | -122.7539 | 0.19684 | 1.4211e-13 | -0.016414 | -0.00049791 | 0.062913 | -0.010918 | 0.059881 | 0.013277 | 0.008129 | 0.0081403 | -0.0058155 | 0.03428 | 0.0058733 | -122.1366 | -0.14969 | -122.6789 | 0.18948 | -0.10038 | 0.34342 | -122.5035 | 0.069728 | 0.050725 | 0.01233 | 0.16692 | 0.27926 | -0.17997 | -0.2191 | 0.25041 | -0.007359 | 0.6173 | 0.075048 | -0.17536 | -0.29722 | 0.14659 | 122.5348 | -0.029917 | 122.8236 | 122.7662 | 0.23143 | 0.082427 | -0.37681 | 122.9434 | 122.6535 | 123.0973 | 122.6042 | -122.7003 | 122.9208 | 123.0332 | 122.5739 | 122.8046 | -0.41593
753.5156 | 123.056 | -122.7219 | 0.17853 | 1.4211e-13 | -0.016201 | -0.00071151 | 0.062485 | -0.011345 | 0.059667 | 0.013277 | 0.0077016 | 0.0081403 | -0.0060291 | 0.034066 | 0.0063007 | -122.1229 | -0.14969 | -122.6743 | 0.18032 | -0.09122 | 0.34342 | -122.4989 | 0.074307 | 0.046146 | 0.007751 | 0.16692 | 0.27926 | -0.17081 | -0.21452 | 0.22294 | 0.001795 | 0.59899 | 0.047583 | -0.17536 | -0.26975 | 0.1649 | 122.5073 | -0.011607 | 122.7962 | 122.7296 | 0.22227 | 0.10074 | -0.34934 | 122.9022 | 122.6306 | 123.0653 | 122.5722 | -122.6774 | 122.8888 | 123.0011 | 122.551 | 122.768 | -0.39304
755.2656 | 123.0423 | -122.7173 | 0.1831 | 1.4211e-13 | -0.016201 | -0.00049791 | 0.062913 | -0.011132 | 0.059881 | 0.0056466 | 0.0085562 | 0.0081403 | -0.0062429 | 0.03428 | 0.0060869 | -122.132 | -0.14969 | -122.6743 | 0.18032 | -0.10038 | 0.32969 | -122.4989 | 0.069728 | 0.041567 | -0.001407 | 0.16692 | 0.27926 | -0.17539 | -0.21452 | 0.21836 | -0.002782 | 0.58526 | 0.043005 | -0.17536 | -0.28348 | 0.14658 | 122.5028 | -0.016184 | 122.787 | 122.7159 | 0.21311 | 0.09616 | -0.3585 | 122.8976 | 122.6169 | 123.047 | 122.5676 | -122.682 | 122.8842 | 122.9965 | 122.5419 | 122.7589 | -0.39762
757.0312 | 122.9736 | -122.7448 | 0.21057 | 1.4211e-13 | -0.016414 | -0.00049791 | 0.062485 | -0.010918 | 0.059881 | 0.013277 | 0.008129 | 0.0083539 | -0.0058155 | 0.034493 | 0.0060869 | -122.132 | -0.16342 | -122.6743 | 0.19406 | -0.09122 | 0.35258 | -122.5035 | 0.06515 | 0.055303 | 0.007751 | 0.16692 | 0.27926 | -0.17539 | -0.2191 | 0.24125 | -0.016513 | 0.61272 | 0.070471 | -0.17078 | -0.30179 | 0.14201 | 122.5257 | -0.04365 | 122.8099 | 122.7525 | 0.22685 | 0.068694 | -0.38596 | 122.9388 | 122.6535 | 123.0973 | 122.5813 | -122.7141 | 122.9117 | 123.024 | 122.5694 | 122.8001 | -0.42967
758.7656 | 122.9691 | -122.7676 | 0.19684 | 1.4211e-13 | -0.015987 | -0.00049791 | 0.062699 | -0.010704 | 0.059667 | 0.0056466 | 0.008129 | 0.0081403 | -0.0058155 | 0.034066 | 0.0060869 | -122.1274 | -0.15884 | -122.6789 | 0.1849 | -0.086641 | 0.35716 | -122.5035 | 0.06515 | 0.046146 | 0.003172 | 0.16692 | 0.27926 | -0.17081 | -0.21452 | 0.26414 | -0.011937 | 0.64019 | 0.088781 | -0.17536 | -0.28348 | 0.16032 | 122.5531 | -0.029917 | 122.8328 | 122.7708 | 0.21769 | 0.082427 | -0.36765 | 122.9525 | 122.681 | 123.1248 | 122.6088 | -122.7003 | 122.9346 | 123.0469 | 122.5968 | 122.8138 | -0.41135
760.4531 | 122.937 | -122.7722 | 0.20599 | 1.4211e-13 | -0.016414 | -0.00049791 | 0.062699 | -0.011132 | 0.059454 | -0.0096144 | 0.008129 | 0.0083539 | -0.0060291 | 0.034066 | 0.0063007 | -122.1229 | -0.15427 | -122.6789 | 0.1849 | -0.095798 | 0.33885 | -122.5035 | 0.06515 | 0.036989 | -0.001407 | 0.16234 | 0.27926 | -0.17539 | -0.21452 | 0.26872 | -0.021093 | 0.64935 | 0.093359 | -0.17536 | -0.30179 | 0.13285 | 122.5577 | -0.043652 | 122.8374 | 122.7708 | 0.21311 | 0.073271 | -0.38139 | 122.9571 | 122.6764 | 123.1111 | 122.618 | -122.7095 | 122.9346 | 123.0515 | 122.5968 | 122.8092 | -0.42051
762.2031 | 123.0789 | -122.7081 | 0.16937 | 1.4211e-13 | -0.016201 | -0.00049791 | 0.062699 | -0.011345 | 0.059667 | -0.0019839 | 0.0077016 | 0.0081403 | -0.0062429 | 0.03428 | 0.0065143 | -122.1229 | -0.14969 | -122.6743 | 0.19406 | -0.09122 | 0.32511 | -122.4943 | 0.060571 | 0.046146 | 0.01233 | 0.16692 | 0.28384 | -0.16624 | -0.22367 | 0.21379 | 0.024685 | 0.58526 | 0.03385 | -0.17994 | -0.26059 | 0.15574 | 122.4845 | -0.002452 | 122.7687 | 122.7205 | 0.236 | 0.11447 | -0.33561 | 122.9022 | 122.6169 | 123.0332 | 122.5584 | -122.6637 | 122.8751 | 122.992 | 122.5419 | 122.7543 | -0.39305
763.9531 | 122.9187 | -122.7676 | 0.21973 | 1.4211e-13 | -0.016414 | -0.00071151 | 0.062699 | -0.011559 | 0.059667 | -0.0019839 | 0.0079152 | 0.0085677 | -0.0060291 | 0.03428 | 0.0060869 | -122.132 | -0.14511 | -122.6789 | 0.18032 | -0.095798 | 0.34342 | -122.4989 | 0.06515 | 0.03241 | 0.007751 | 0.17608 | 0.27469 | -0.16624 | -0.2191 | 0.26872 | -0.039404 | 0.63561 | 0.088781 | -0.17994 | -0.31552 | 0.1237 | 122.5485 | -0.043649 | 122.8328 | 122.7754 | 0.22685 | 0.05496 | -0.38596 | 122.948 | 122.6718 | 123.1111 | 122.6225 | -122.7186 | 122.9437 | 123.0423 | 122.6014 | 122.8 | -0.43882
765.625 | 123.024 | -122.7264 | 0.17853 | 1.4211e-13 | -0.016414 | -0.00071151 | 0.062699 | -0.010918 | 0.059667 | -0.0019839 | 0.0083426 | 0.0083539 | -0.0058155 | 0.034066 | 0.0063007 | -122.1183 | -0.14969 | -122.6697 | 0.18032 | -0.09122 | 0.35258 | -122.4898 | 0.069728 | 0.050725 | 0.007751 | 0.16692 | 0.28384 | -0.17081 | -0.21452 | 0.23668 | 0.001795 | 0.60815 | 0.056738 | -0.17994 | -0.26975 | 0.17405 | 122.5119 | -0.011607 | 122.7962 | 122.7342 | 0.22227 | 0.10532 | -0.34934 | 122.9068 | 122.6352 | 123.079 | 122.5768 | -122.6683 | 122.8934 | 123.0103 | 122.5556 | 122.7772 | -0.39304
767.375 | 122.9187 | -122.7859 | 0.20599 | 1.4211e-13 | -0.016201 | -0.00049791 | 0.062485 | -0.011132 | 0.059881 | -0.0019839 | 0.0083426 | 0.0079267 | -0.0058155 | 0.034493 | 0.0060869 | -122.1274 | -0.15884 | -122.6743 | 0.1849 | -0.09122 | 0.33885 | -122.5035 | 0.074307 | 0.050725 | 0.01233 | 0.17608 | 0.28384 | -0.16624 | -0.21452 | 0.28245 | -0.021093 | 0.6585 | 0.11167 | -0.17078 | -0.29721 | 0.13285 | 122.5714 | -0.029916 | 122.8603 | 122.7983 | 0.22685 | 0.07785 | -0.37223 | 122.9709 | 122.6947 | 123.1248 | 122.6271 | -122.7095 | 122.962 | 123.0698 | 122.6197 | 122.8367 | -0.42051
769.125 | 123.0469 | -122.7264 | 0.18768 | 1.4211e-13 | -0.016201 | -0.00049791 | 0.062699 | -0.011132 | 0.059881 | 0.013277 | 0.0085562 | 0.0081403 | -0.0064565 | 0.034493 | 0.0060869 | -122.1137 | -0.15884 | -122.6743 | 0.18948 | -0.086641 | 0.31137 | -122.4989 | 0.06515 | 0.050725 | 0.01233 | 0.16692 | 0.27926 | -0.16624 | -0.2191 | 0.22752 | 0.001796 | 0.61273 | 0.05216 | -0.17536 | -0.27432 | 0.12369 | 122.5073 | -0.020762 | 122.7916 | 122.7388 | 0.23143 | 0.091582 | -0.35392 | 122.9159 | 122.6398 | 123.0378 | 122.5676 | -122.6866 | 122.8934 | 123.0057 | 122.5602 | 122.7772 | -0.40678
770.8125 | 122.9507 | -122.7493 | 0.17395 | 1.4211e-13 | -0.016628 | -0.00071151 | 0.062272 | -0.011559 | 0.059881 | 0.0056466 | 0.008129 | 0.0083539 | -0.0058155 | 0.034493 | 0.0063007 | -122.1137 | -0.15427 | -122.6743 | 0.1849 | -0.10038 | 0.35716 | -122.4989 | 0.06515 | 0.046146 | 0.007751 | 0.16692 | 0.27926 | -0.17081 | -0.21452 | 0.25041 | 0.010951 | 0.63562 | 0.075049 | -0.17536 | -0.27433 | 0.18321 | 122.5348 | -0.007029 | 122.8145 | 122.7571 | 0.22227 | 0.10531 | -0.34476 | 122.9342 | 122.649 | 123.1065 | 122.5951 | -122.6729 | 122.9163 | 123.0286 | 122.5785 | 122.7955 | -0.38847
772.5625 | 122.9507 | -122.7493 | 0.2243 | 1.4211e-13 | -0.016201 | -0.00092531 | 0.062485 | -0.011559 | 0.059881 | -0.0019839 | 0.0079152 | 0.0081403 | -0.0056019 | 0.034493 | 0.0060869 | -122.1137 | -0.15884 | -122.6743 | 0.18948 | -0.086641 | 0.36174 | -122.5035 | 0.060571 | 0.046146 | 0.01233 | 0.1715 | 0.28384 | -0.17539 | -0.2191 | 0.24583 | -0.034825 | 0.63562 | 0.075049 | -0.17078 | -0.31095 | 0.13743 | 122.5302 | -0.052805 | 122.8099 | 122.7617 | 0.23143 | 0.05954 | -0.3997 | 122.9388 | 122.6627 | 123.1111 | 122.5905 | -122.7278 | 122.9208 | 123.0332 | 122.5739 | 122.7955 | -0.4434
774.3125 | 123.024 | -122.7356 | 0.19226 | 1.4211e-13 | -0.016414 | -0.00049791 | 0.062699 | -0.010918 | 0.059667 | 0.013277 | 0.0079152 | 0.0081403 | -0.0062429 | 0.03428 | 0.0063007 | -122.1183 | -0.15884 | -122.6651 | 0.1849 | -0.095798 | 0.35716 | -122.4898 | 0.074307 | 0.055303 | 0.007751 | 0.1715 | 0.26553 | -0.16624 | -0.20994 | 0.24583 | -0.00736 | 0.6173 | 0.070473 | -0.17536 | -0.28806 | 0.1649 | 122.5257 | -0.020762 | 122.8099 | 122.7433 | 0.21769 | 0.073269 | -0.3585 | 122.9205 | 122.6398 | 123.0928 | 122.5768 | -122.682 | 122.9071 | 123.0011 | 122.5694 | 122.7909 | -0.4022
776 | 122.9874 | -122.7356 | 0.20142 | 1.4211e-13 | -0.016842 | -0.00071151 | 0.062699 | -0.011132 | 0.060095 | 0.0056466 | 0.008129 | 0.0083539 | -0.0060291 | 0.034066 | 0.0065143 | -122.1229 | -0.14969 | -122.6697 | 0.1849 | -0.09122 | 0.36174 | -122.4943 | 0.06515 | 0.046146 | 0.007751 | 0.1715 | 0.27011 | -0.17997 | -0.22367 | 0.24125 | -0.016515 | 0.61273 | 0.065894 | -0.17536 | -0.29264 | 0.16032 | 122.5119 | -0.029917 | 122.8007 | 122.7433 | 0.23142 | 0.068692 | -0.38139 | 122.9205 | 122.6444 | 123.0973 | 122.5859 | -122.6958 | 122.9071 | 123.0057 | 122.5556 | 122.7817 | -0.42509
777.7344 | 123.0377 | -122.7585 | 0.19226 | 1.4211e-13 | -0.016414 | -0.00049791 | 0.062272 | -0.011345 | 0.059667 | -0.0019839 | 0.008129 | 0.0079267 | -0.0060291 | 0.034493 | 0.0063007 | -122.1183 | -0.15884 | -122.6651 | 0.18948 | -0.095798 | 0.35258 | -122.5035 | 0.069728 | 0.046146 | 0.01233 | 0.16692 | 0.27011 | -0.16166 | -0.22367 | 0.25498 | -0.002782 | 0.64019 | 0.093361 | -0.16162 | -0.28806 | 0.16032 | 122.5348 | -0.02534 | 122.8282 | 122.7708 | 0.236 | 0.077847 | -0.35392 | 122.948 | 122.6627 | 123.1111 | 122.5996 | -122.6958 | 122.9254 | 123.0286 | 122.5968 | 122.8046 | -0.41593
779.4688 | 122.9233 | -122.7676 | 0.21515 | 1.4211e-13 | -0.016842 | -0.00071151 | 0.062699 | -0.011132 | 0.059667 | 0.0056466 | 0.008129 | 0.0081403 | -0.0062429 | 0.034707 | 0.0063007 | -122.1183 | -0.14969 | -122.6697 | 0.19406 | -0.095798 | 0.36632 | -122.4943 | 0.06515 | 0.059882 | 0.007751 | 0.16692 | 0.28384 | -0.17997 | -0.22367 | 0.2733 | -0.021091 | 0.64935 | 0.097937 | -0.17536 | -0.31095 | 0.15117 | 122.544 | -0.048228 | 122.8328 | 122.7754 | 0.23142 | 0.068695 | -0.39512 | 122.9617 | 122.6718 | 123.134 | 122.618 | -122.7095 | 122.9346 | 123.0515 | 122.5877 | 122.8275 | -0.43882
781.2188 | 122.9416 | -122.7631 | 0.23346 | 1.4211e-13 | -0.016842 | -0.00071151 | 0.062699 | -0.011132 | 0.059667 | -0.0019839 | 0.0083426 | 0.0081403 | -0.0062429 | 0.034921 | 0.0060869 | -122.1229 | -0.15427 | -122.6697 | 0.1849 | -0.095798 | 0.35716 | -122.4943 | 0.060571 | 0.050725 | 0.01233 | 0.1715 | 0.28384 | -0.16624 | -0.20994 | 0.26872 | -0.048558 | 0.64019 | 0.09336 | -0.17536 | -0.32926 | 0.1237 | 122.5531 | -0.06196 | 122.8236 | 122.7754 | 0.22227 | 0.050385 | -0.3997 | 122.948 | 122.6673 | 123.1202 | 122.6088 | -122.7278 | 122.9346 | 123.0469 | 122.5968 | 122.8138 | -0.4434
782.9688 | 122.9919 | -122.7264 | 0.17853 | 1.4211e-13 | -0.016414 | -0.00071151 | 0.062485 | -0.011345 | 0.059667 | 0.0056466 | 0.008129 | 0.0085677 | -0.0058155 | 0.034493 | 0.0063007 | -122.1229 | -0.168 | -122.6789 | 0.1849 | -0.09122 | 0.36174 | -122.4852 | 0.069728 | 0.041567 | 0.01233 | 0.16692 | 0.27926 | -0.17081 | -0.21452 | 0.24126 | 0.006373 | 0.60357 | 0.047582 | -0.19367 | -0.26975 | 0.18321 | 122.5119 | -0.011607 | 122.7962 | 122.7388 | 0.22685 | 0.10074 | -0.34934 | 122.9113 | 122.6352 | 123.0882 | 122.5584 | -122.6637 | 122.8934 | 123.0057 | 122.5556 | 122.768 | -0.39304
784.6406 | 122.9507 | -122.7448 | 0.21057 | 1.4211e-13 | -0.016414 | -0.00028411 | 0.062699 | -0.011345 | 0.059881 | 0.0056466 | 0.0083426 | 0.0083539 | -0.0062429 | 0.03428 | 0.0060869 | -122.1183 | -0.16342 | -122.6743 | 0.1849 | -0.09122 | 0.34342 | -122.4943 | 0.06515 | 0.046146 | 0.003172 | 0.1715 | 0.27926 | -0.16624 | -0.2191 | 0.25041 | -0.02567 | 0.62646 | 0.070471 | -0.17994 | -0.30179 | 0.13285 | 122.5257 | -0.039072 | 122.8099 | 122.7479 | 0.22227 | 0.068694 | -0.37681 | 122.9297 | 122.6535 | 123.0882 | 122.5813 | -122.7049 | 122.9162 | 123.024 | 122.5785 | 122.7909 | -0.42967
786.4062 | 122.9553 | -122.7219 | 0.21057 | 1.4211e-13 | -0.016628 | -0.00092531 | 0.062913 | -0.011559 | 0.059881 | 0.0056466 | 0.008129 | 0.0081403 | -0.0060291 | 0.034493 | 0.0060869 | -122.1046 | -0.15884 | -122.6743 | 0.18948 | -0.09122 | 0.35258 | -122.4898 | 0.069728 | 0.046146 | 0.007751 | 0.15776 | 0.28842 | -0.17081 | -0.2191 | 0.2321 | -0.021092 | 0.61731 | 0.047583 | -0.18452 | -0.30179 | 0.14201 | 122.5028 | -0.052807 | 122.7916 | 122.7296 | 0.22685 | 0.077852 | -0.38139 | 122.9113 | 122.6306 | 123.0744 | 122.563 | -122.7003 | 122.8796 | 123.0103 | 122.551 | 122.768 | -0.42967
788.0938 | 122.9965 | -122.7173 | 0.19226 | 1.4211e-13 | -0.016201 | -0.00049791 | 0.062485 | -0.011132 | 0.059881 | -0.0019839 | 0.0083426 | 0.0079267 | -0.0060291 | 0.03428 | 0.0060869 | -122.1091 | -0.16342 | -122.6651 | 0.19406 | -0.082062 | 0.37548 | -122.4898 | 0.06515 | 0.046146 | 0.016908 | 0.15776 | 0.28384 | -0.16624 | -0.2191 | 0.22752 | 0.001797 | 0.60815 | 0.052162 | -0.17536 | -0.27432 | 0.18321 | 122.4982 | -0.034497 | 122.7824 | 122.7342 | 0.236 | 0.091583 | -0.3585 | 122.9113 | 122.6352 | 123.0928 | 122.5539 | -122.682 | 122.875 | 123.0011 | 122.551 | 122.7634 | -0.41136
789.8438 | 122.9736 | -122.731 | 0.18768 | 1.4211e-13 | -0.016414 | -0.00071151 | 0.062699 | -0.010918 | 0.060308 | 0.013277 | 0.0079152 | 0.0083539 | -0.0060291 | 0.034493 | 0.0065143 | -122.1046 | -0.15427 | -122.6651 | 0.18948 | -0.086641 | 0.33885 | -122.4806 | 0.06515 | 0.055303 | 0.007751 | 0.16692 | 0.27926 | -0.17539 | -0.22367 | 0.25041 | 0.001796 | 0.62646 | 0.065895 | -0.18452 | -0.27432 | 0.15116 | 122.5073 | -0.020762 | 122.7962 | 122.7388 | 0.23142 | 0.091582 | -0.36308 | 122.9205 | 122.6444 | 123.0699 | 122.5768 | -122.6683 | 122.8979 | 123.0103 | 122.5556 | 122.7863 | -0.41136
791.5781 | 122.9187 | -122.7539 | 0.20142 | 1.4211e-13 | -0.016628 | -0.00071151 | 0.062699 | -0.011345 | 0.059881 | -0.0019839 | 0.008129 | 0.0083539 | -0.0062429 | 0.034707 | 0.0060869 | -122.1091 | -0.14969 | -122.6697 | 0.19406 | -0.095798 | 0.3709 | -122.4806 | 0.06515 | 0.050725 | 0.01233 | 0.15776 | 0.28384 | -0.17081 | -0.21452 | 0.2733 | -0.007358 | 0.64477 | 0.084204 | -0.1891 | -0.29721 | 0.16948 | 122.5394 | -0.043652 | 122.8191 | 122.7662 | 0.22685 | 0.082428 | -0.37223 | 122.948 | 122.6581 | 123.1248 | 122.6042 | -122.682 | 122.9117 | 123.0378 | 122.5831 | 122.8046 | -0.41593
793.2812 | 123.056 | -122.7173 | 0.18768 | 1.4211e-13 | -0.016628 | -0.00071151 | 0.062485 | -0.011345 | 0.059667 | 0.0056466 | 0.0083426 | 0.0083539 | -0.0062429 | 0.034707 | 0.0060869 | -122.1183 | -0.14969 | -122.6651 | 0.19406 | -0.09122 | 0.32969 | -122.4806 | 0.074307 | 0.050725 | 0.01233 | 0.15776 | 0.293 | -0.17539 | -0.2191 | 0.23668 | 0.006375 | 0.59899 | 0.052162 | -0.18452 | -0.2789 | 0.14201 | 122.4982 | -0.029919 | 122.7916 | 122.7296 | 0.23143 | 0.10532 | -0.36308 | 122.9113 | 122.6261 | 123.047 | 122.5676 | -122.6683 | 122.875 | 123.0103 | 122.5419 | 122.768 | -0.40678
795.0156 | 122.9187 | -122.7493 | 0.19684 | 1.4211e-13 | -0.016414 | -0.00071151 | 0.062485 | -0.011559 | 0.059667 | 0.0056466 | 0.008129 | 0.0083539 | -0.0060291 | 0.034921 | 0.0060869 | -122.1046 | -0.15884 | -122.6651 | 0.19406 | -0.09122 | 0.3709 | -122.4806 | 0.074307 | 0.046146 | 0.01233 | 0.15318 | 0.28384 | -0.17081 | -0.21452 | 0.26872 | -0.00278 | 0.64477 | 0.084206 | -0.18452 | -0.28806 | 0.17406 | 122.5348 | -0.043653 | 122.8236 | 122.7617 | 0.22685 | 0.087006 | -0.36765 | 122.9434 | 122.6581 | 123.1202 | 122.5905 | -122.6774 | 122.9025 | 123.0332 | 122.5785 | 122.7955 | -0.41135
796.7656 | 122.9874 | -122.7219 | 0.19226 | 1.4211e-13 | -0.016414 | -0.00028411 | 0.062699 | -0.011559 | 0.059454 | -0.0019839 | 0.0083426 | 0.0079267 | -0.0062429 | 0.034707 | 0.0060869 | -122.1046 | -0.15884 | -122.6651 | 0.19864 | -0.086641 | 0.33427 | -122.4852 | 0.069728 | 0.050725 | 0.01233 | 0.16234 | 0.28384 | -0.17081 | -0.2191 | 0.23668 | 0.006375 | 0.61731 | 0.05674 | -0.17994 | -0.2789 | 0.14201 | 122.5028 | -0.029919 | 122.7916 | 122.7342 | 0.23143 | 0.091583 | -0.36308 | 122.9205 | 122.6352 | 123.0561 | 122.563 | -122.6774 | 122.8842 | 123.0057 | 122.551 | 122.7726 | -0.41136
798.5312 | 122.9645 | -122.7127 | 0.19226 | 1.4211e-13 | -0.016414 | -0.00071151 | 0.062485 | -0.011345 | 0.059881 | 0.020908 | 0.008129 | 0.0081403 | -0.0060291 | 0.034707 | 0.0056597 | -122.1046 | -0.15884 | -122.6743 | 0.19406 | -0.095798 | 0.348 | -122.4898 | 0.069728 | 0.050725 | 0.007751 | 0.15318 | 0.27926 | -0.17539 | -0.22367 | 0.22295 | 0.001797 | 0.60815 | 0.038428 | -0.18452 | -0.28806 | 0.15574 | 122.489 | -0.039076 | 122.7824 | 122.7205 | 0.23142 | 0.087004 | -0.36765 | 122.9068 | 122.6169 | 123.0607 | 122.5539 | -122.682 | 122.8659 | 122.992 | 122.5373 | 122.7634 | -0.41593
800.2188 | 122.9507 | -122.7264 | 0.20599 | 1.4211e-13 | -0.016628 | -0.00049791 | 0.062272 | -0.011559 | 0.059667 | 0.0056466 | 0.008129 | 0.0081403 | -0.0062429 | 0.034707 | 0.0060869 | -122.1046 | -0.168 | -122.656 | 0.19406 | -0.086641 | 0.36174 | -122.476 | 0.06515 | 0.046146 | 0.007751 | 0.16234 | 0.28384 | -0.17081 | -0.21452 | 0.25041 | -0.011936 | 0.62188 | 0.070473 | -0.17994 | -0.29263 | 0.15574 | 122.5119 | -0.043652 | 122.7916 | 122.7342 | 0.22227 | 0.07785 | -0.37681 | 122.9205 | 122.6398 | 123.0882 | 122.5584 | -122.682 | 122.8888 | 123.0103 | 122.5556 | 122.7726 | -0.42051
801.9531 | 122.9828 | -122.6944 | 0.19684 | 1.4211e-13 | -0.016414 | -0.00092531 | 0.062485 | -0.011559 | 0.059881 | 0.0056466 | 0.008129 | 0.0079267 | -0.0064565 | 0.034493 | 0.0063007 | -122.1046 | -0.15427 | -122.6697 | 0.19406 | -0.086641 | 0.36174 | -122.476 | 0.069728 | 0.046146 | 0.016908 | 0.16692 | 0.27926 | -0.17081 | -0.2191 | 0.21837 | -0.00278 | 0.58984 | 0.024695 | -0.19368 | -0.28348 | 0.1649 | 122.4753 | -0.029917 | 122.7641 | 122.7113 | 0.236 | 0.082427 | -0.36765 | 122.8885 | 122.6078 | 123.0561 | 122.5401 | -122.6729 | 122.8613 | 122.9737 | 122.5236 | 122.7405 | -0.41593
803.6406 | 122.8958 | -122.7539 | 0.21515 | 1.4211e-13 | -0.016201 | -0.00071151 | 0.062699 | -0.011559 | 0.059454 | 0.0056466 | 0.0083426 | 0.0079267 | -0.0060291 | 0.034493 | 0.0063007 | -122.0908 | -0.168 | -122.6605 | 0.19406 | -0.086641 | 0.35258 | -122.4852 | 0.074307 | 0.046146 | 0.007751 | 0.15776 | 0.27926 | -0.17081 | -0.2191 | 0.26872 | -0.021091 | 0.66308 | 0.093361 | -0.17536 | -0.30179 | 0.13743 | 122.5348 | -0.057385 | 122.8282 | 122.7617 | 0.22685 | 0.064116 | -0.38596 | 122.948 | 122.6673 | 123.1065 | 122.5859 | -122.7003 | 122.9117 | 123.0332 | 122.5831 | 122.8001 | -0.43424
805.3906 | 122.9095 | -122.7127 | 0.21057 | 1.4211e-13 | -0.016628 | -0.0011389 | 0.062699 | -0.011132 | 0.059881 | 0.0056466 | 0.0083426 | 0.0085677 | -0.0060291 | 0.034921 | 0.0060869 | -122.1 | -0.168 | -122.6651 | 0.19406 | -0.09122 | 0.33885 | -122.4806 | 0.069728 | 0.046146 | 0.016908 | 0.15776 | 0.28384 | -0.17081 | -0.2191 | 0.2321 | -0.016513 | 0.61273 | 0.047585 | -0.18452 | -0.30179 | 0.12827 | 122.4936 | -0.052807 | 122.7824 | 122.7296 | 0.236 | 0.073273 | -0.38139 | 122.9068 | 122.6215 | 123.0516 | 122.5447 | -122.6912 | 122.8705 | 122.9966 | 122.5419 | 122.7589 | -0.42967
807.1562 | 123.0103 | -122.7081 | 0.17853 | 1.4211e-13 | -0.016628 | -0.00028411 | 0.062699 | -0.011132 | 0.060095 | -0.0019839 | 0.008129 | 0.0083539 | -0.0056019 | 0.034707 | 0.0056597 | -122.1 | -0.14969 | -122.656 | 0.18948 | -0.086641 | 0.36174 | -122.4806 | 0.074307 | 0.050725 | 0.016908 | 0.15776 | 0.28842 | -0.17081 | -0.20536 | 0.22752 | 0.010951 | 0.60815 | 0.052163 | -0.17536 | -0.26517 | 0.18321 | 122.5028 | -0.020764 | 122.7824 | 122.725 | 0.22227 | 0.10989 | -0.34934 | 122.8976 | 122.6215 | 123.0699 | 122.5584 | -122.6591 | 122.8659 | 122.9966 | 122.5373 | 122.7589 | -0.38389
808.8281 | 122.9416 | -122.7539 | 0.21057 | 1.4211e-13 | -0.016414 | -0.00071151 | 0.062913 | -0.011132 | 0.059667 | 0.013277 | 0.0085562 | 0.0079267 | -0.0060291 | 0.034707 | 0.0058733 | -122.1046 | -0.16342 | -122.6651 | 0.1849 | -0.095798 | 0.36174 | -122.4898 | 0.074307 | 0.064461 | 0.021487 | 0.17608 | 0.29758 | -0.17539 | -0.20994 | 0.26414 | -0.02567 | 0.64935 | 0.088783 | -0.17536 | -0.30637 | 0.15117 | 122.544 | -0.034493 | 122.8282 | 122.7754 | 0.23142 | 0.087009 | -0.38596 | 122.9388 | 122.6581 | 123.1156 | 122.5905 | -122.7003 | 122.93 | 123.0515 | 122.5785 | 122.8184 | -0.42051
810.5625 | 122.9279 | -122.7402 | 0.21515 | 1.4211e-13 | -0.015987 | -0.00071151 | 0.062272 | -0.011132 | 0.059881 | 0.0056466 | 0.0083426 | 0.0081403 | -0.0064565 | 0.034921 | 0.0056597 | -122.1137 | -0.168 | -122.6605 | 0.18032 | -0.086641 | 0.3709 | -122.4852 | 0.078886 | 0.055303 | 0.021487 | 0.1715 | 0.28842 | -0.17539 | -0.20536 | 0.25499 | -0.034826 | 0.62646 | 0.079628 | -0.17536 | -0.30179 | 0.15575 | 122.5348 | -0.04365 | 122.8191 | 122.7617 | 0.22685 | 0.073274 | -0.39054 | 122.9205 | 122.6535 | 123.1111 | 122.5722 | -122.7003 | 122.9117 | 123.0286 | 122.5648 | 122.7955 | -0.42051
812.3125 | 122.905 | -122.7585 | 0.1831 | 1.4211e-13 | -0.016414 | -0.00028411 | 0.062699 | -0.011132 | 0.059667 | 0.0056466 | 0.0083426 | 0.0081403 | -0.0060291 | 0.034707 | 0.0058733 | -122.1 | -0.168 | -122.6605 | 0.17574 | -0.09122 | 0.32511 | -122.4806 | 0.074307 | 0.050725 | 0.016908 | 0.16234 | 0.28384 | -0.17539 | -0.21452 | 0.27788 | -0.007361 | 0.65851 | 0.097939 | -0.17994 | -0.27432 | 0.14201 | 122.544 | -0.020763 | 122.8328 | 122.7754 | 0.23142 | 0.10074 | -0.3585 | 122.9342 | 122.6673 | 123.0836 | 122.5905 | -122.6637 | 122.9208 | 123.0423 | 122.5831 | 122.8092 | -0.39762
814.0625 | 123.0148 | -122.7219 | 0.17395 | 1.4211e-13 | -0.016414 | -0.00049791 | 0.062699 | -0.011345 | 0.059454 | 0.013277 | 0.008129 | 0.0081403 | -0.0062429 | 0.034921 | 0.0056597 | -122.1046 | -0.16342 | -122.6651 | 0.18032 | -0.10038 | 0.35716 | -122.4806 | 0.06515 | 0.055303 | 0.016908 | 0.1715 | 0.28842 | -0.17997 | -0.20994 | 0.24126 | 0.006373 | 0.61731 | 0.05674 | -0.18452 | -0.27433 | 0.18321 | 122.5119 | -0.002451 | 122.787 | 122.7388 | 0.22685 | 0.11447 | -0.35392 | 122.9022 | 122.6215 | 123.079 | 122.5584 | -122.6546 | 122.8934 | 123.0103 | 122.5419 | 122.7772 | -0.38389
815.75 | 123.0286 | -122.7036 | 0.17853 | 1.4211e-13 | -0.016628 | -0.00049791 | 0.062699 | -0.011559 | 0.059667 | -0.0019839 | 0.0083426 | 0.0083539 | -0.0060291 | 0.034493 | 0.0052323 | -122.1046 | -0.16342 | -122.6651 | 0.18032 | -0.095798 | 0.36632 | -122.4898 | 0.074307 | 0.055303 | 0.016908 | 0.1715 | 0.28842 | -0.17081 | -0.20994 | 0.21379 | 0.001795 | 0.599 | 0.038429 | -0.17536 | -0.27433 | 0.18779 | 122.4936 | -0.007029 | 122.7779 | 122.7205 | 0.22685 | 0.10989 | -0.34934 | 122.8839 | 122.6078 | 123.0699 | 122.5401 | -122.6683 | 122.8751 | 122.992 | 122.5327 | 122.7589 | -0.38847
817.5 | 122.9279 | -122.7402 | 0.21973 | 1.4211e-13 | -0.016201 | -0.00049791 | 0.062485 | -0.011132 | 0.059881 | 0.0056466 | 0.0079152 | 0.0077131 | -0.0062429 | 0.034921 | 0.0058733 | -122.1046 | -0.16342 | -122.6651 | 0.1849 | -0.10038 | 0.35258 | -122.4898 | 0.069728 | 0.046146 | 0.016908 | 0.16234 | 0.28842 | -0.17081 | -0.20994 | 0.25041 | -0.034826 | 0.63562 | 0.07505 | -0.17536 | -0.3201 | 0.13286 | 122.5302 | -0.057385 | 122.8099 | 122.7571 | 0.22685 | 0.068696 | -0.39054 | 122.9251 | 122.6398 | 123.0928 | 122.5768 | -122.7095 | 122.9025 | 123.0286 | 122.5694 | 122.7863 | -0.42966
819.25 | 122.9828 | -122.7219 | 0.20142 | 1.4211e-13 | -0.016628 | -0.00092531 | 0.062699 | -0.011773 | 0.059881 | -0.0019839 | 0.008129 | 0.0083539 | -0.0062429 | 0.034707 | 0.0058733 | -122.1046 | -0.16342 | -122.6697 | 0.18032 | -0.086641 | 0.32511 | -122.4806 | 0.074307 | 0.050725 | 0.016908 | 0.16692 | 0.28384 | -0.16624 | -0.20994 | 0.24126 | -0.021093 | 0.61731 | 0.052161 | -0.1891 | -0.28806 | 0.12369 | 122.5119 | -0.034495 | 122.7962 | 122.7388 | 0.22685 | 0.082428 | -0.36765 | 122.9022 | 122.6352 | 123.047 | 122.5584 | -122.682 | 122.8888 | 123.0057 | 122.5556 | 122.7726 | -0.41135
820.9375 | 122.9095 | -122.7585 | 0.22888 | 1.4211e-13 | -0.016628 | -0.00071151 | 0.062058 | -0.011559 | 0.059667 | 0.013277 | 0.0079152 | 0.0083539 | -0.0058155 | 0.034707 | 0.0058733 | -122.0954 | -0.16342 | -122.6697 | 0.1849 | -0.095798 | 0.36174 | -122.4852 | 0.074307 | 0.059882 | 0.016908 | 0.16234 | 0.29758 | -0.17081 | -0.21452 | 0.2733 | -0.043981 | 0.66308 | 0.088782 | -0.18452 | -0.32468 | 0.13286 | 122.544 | -0.06654 | 122.8328 | 122.7754 | 0.23142 | 0.068698 | -0.3997 | 122.9434 | 122.6627 | 123.1202 | 122.5951 | -122.7141 | 122.9208 | 123.0561 | 122.5877 | 122.8184 | -0.4434
822.6875 | 123.0057 | -122.6944 | 0.17395 | 1.4211e-13 | -0.016628 | -0.00028411 | 0.062485 | -0.011559 | 0.059881 | -0.0019839 | 0.0079152 | 0.0083539 | -0.0060291 | 0.034707 | 0.0054461 | -122.0954 | -0.15884 | -122.6651 | 0.1849 | -0.10038 | 0.36174 | -122.5127 | 0.074307 | 0.050725 | 0.016908 | 0.16692 | 0.28384 | -0.17539 | -0.20994 | 0.18174 | 0.010951 | 0.599 | 0.029274 | -0.15247 | -0.27433 | 0.18779 | 122.4845 | -0.007029 | 122.7687 | 122.7113 | 0.22685 | 0.10989 | -0.34934 | 122.8793 | 122.594 | 123.0561 | 122.5356 | -122.6866 | 122.8613 | 122.9782 | 122.519 | 122.7451 | -0.38389
824.4375 | 123.0377 | -122.6852 | 0.16937 | 1.4211e-13 | -0.016628 | -0.00071151 | 0.062485 | -0.011345 | 0.059454 | 0.020908 | 0.0079152 | 0.0081403 | -0.0064565 | 0.034921 | 0.0056597 | -122.0908 | -0.16342 | -122.6651 | 0.18032 | -0.086641 | 0.36174 | -122.5356 | 0.074307 | 0.050725 | 0.021487 | 0.15776 | 0.28384 | -0.16624 | -0.2191 | 0.14969 | 0.01095 | 0.59442 | 0.020119 | -0.12957 | -0.25601 | 0.19237 | 122.4661 | -0.011609 | 122.7595 | 122.7067 | 0.24058 | 0.11447 | -0.33561 | 122.8656 | 122.5986 | 123.047 | 122.5218 | -122.7049 | 122.843 | 122.9691 | 122.519 | 122.736 | -0.38847
826.125 | 122.9553 | -122.7127 | 0.20142 | 1.4211e-13 | -0.016414 | -0.00049791 | 0.062913 | -0.011132 | 0.059881 | 0.0056466 | 0.0085562 | 0.0079267 | -0.0060291 | 0.034493 | 0.0058733 | -122.0954 | -0.15884 | -122.6651 | 0.18032 | -0.095798 | 0.35716 | -122.4898 | 0.069728 | 0.055303 | 0.016908 | 0.16692 | 0.28384 | -0.16624 | -0.20994 | 0.22295 | -0.021093 | 0.61731 | 0.047585 | -0.17536 | -0.29721 | 0.15574 | 122.5028 | -0.034495 | 122.7824 | 122.7296 | 0.22685 | 0.082428 | -0.36765 | 122.893 | 122.6169 | 123.0699 | 122.5539 | -122.6912 | 122.8796 | 122.9966 | 122.5465 | 122.768 | -0.41135
827.8906 | 122.8363 | -122.7768 | 0.21973 | 1.4211e-13 | -0.016414 | -0.00092531 | 0.062699 | -0.011559 | 0.059454 | 0.0056466 | 0.0079152 | 0.0079267 | -0.0062429 | 0.034707 | 0.0054461 | -122.0405 | -0.15884 | -122.5964 | 0.25358 | 0.24304 | 0.44415 | -122.8652 | 0.060571 | 0.041567 | 0.003172 | 0.16234 | 0.27469 | -0.17081 | -0.22367 | -0.088441 | 0.03385 | 0.73633 | 0.18034 | 0.26879 | 0.023315 | 0.22443 | 122.5531 | -0.057385 | 122.8374 | 122.78 | 0.22685 | 0.05496 | -0.39054 | 123.0304 | 123.0198 | 123.2209 | 122.6179 | -123.085 | 122.9391 | 123.0515 | 122.606 | 122.8184 | -0.4434
829.5781 | 122.8317 | -122.7448 | 0.21057 | 1.4211e-13 | -0.016414 | -0.00092531 | 0.062485 | -0.011345 | 0.059667 | -0.0019839 | 0.008129 | 0.0079267 | -0.0060291 | 0.034921 | 0.0056597 | -122.0817 | -0.15427 | -122.6422 | 0.17574 | 0.23846 | 0.435 | -122.4577 | 0.06515 | 0.041567 | 0.007751 | 0.15318 | 0.27011 | -0.16624 | -0.22367 | 0.28704 | -0.034827 | 0.66309 | 0.10252 | -0.18452 | 0.027892 | 0.22443 | 122.5211 | -0.057386 | 122.8099 | 122.7525 | 0.23142 | 0.059537 | -0.37681 | 122.9205 | 122.9832 | 123.1797 | 122.5905 | -122.6683 | 122.8979 | 123.0149 | 122.5785 | 122.7863 | -0.43424
831.3281 | 122.9645 | -122.6944 | 0.16022 | 1.4211e-13 | -0.015987 | -0.00049791 | 0.062913 | -0.010918 | 0.060095 | 0.0056466 | 0.0079152 | 0.0081403 | -0.0062429 | 0.034921 | 0.0054461 | -122.0817 | -0.15427 | -122.6468 | 0.19864 | -0.09122 | 0.435 | -122.4669 | 0.069728 | 0.046146 | 0.003172 | 0.15318 | 0.27469 | -0.17539 | -0.22367 | 0.22753 | 0.038419 | 0.61273 | 0.047587 | -0.17994 | -0.25144 | 0.27478 | 122.4707 | -0.007032 | 122.7641 | 122.6976 | 0.22685 | 0.11447 | -0.33561 | 122.893 | 122.6032 | 123.1294 | 122.5401 | -122.6271 | 122.8476 | 122.9691 | 122.519 | 122.7405 | -0.38389
833.0625 | 122.85 | -122.7173 | 0.23346 | 1.4211e-13 | -0.016201 | -0.00071151 | 0.062485 | -0.011345 | 0.059667 | 0.013277 | 0.0079152 | 0.0081403 | -0.0060291 | 0.035134 | 0.0056597 | -122.0954 | -0.16342 | -122.6468 | 0.1849 | -0.095798 | 0.36174 | -122.4669 | 0.06515 | 0.046146 | 0.003172 | 0.15318 | 0.27469 | -0.17081 | -0.22825 | 0.25042 | -0.048558 | 0.62189 | 0.070475 | -0.17994 | -0.32926 | 0.12828 | 122.489 | -0.080274 | 122.7824 | 122.7205 | 0.23142 | 0.041228 | -0.40427 | 122.9022 | 122.6215 | 123.079 | 122.5539 | -122.7003 | 122.8705 | 122.992 | 122.5465 | 122.7634 | -0.46171
834.7344 | 122.85 | -122.7264 | 0.21515 | 1.4211e-13 | -0.016414 | -0.0011389 | 0.062699 | -0.011132 | 0.05924 | 0.0056466 | 0.008129 | 0.0081403 | -0.0060291 | 0.034707 | 0.0054461 | -122.0954 | -0.16342 | -122.6514 | 0.1849 | -0.086641 | 0.36174 | -122.4623 | 0.069728 | 0.036989 | 0.003172 | 0.16234 | 0.27011 | -0.17081 | -0.2191 | 0.26415 | -0.030248 | 0.63104 | 0.075052 | -0.1891 | -0.30179 | 0.14659 | 122.5073 | -0.052807 | 122.7962 | 122.7296 | 0.22227 | 0.054959 | -0.38596 | 122.9113 | 122.6398 | 123.0882 | 122.563 | -122.6774 | 122.8888 | 122.9965 | 122.5556 | 122.7634 | -0.43424
836.4844 | 122.9279 | -122.6898 | 0.20599 | 1.4211e-13 | -0.016842 | -0.00071151 | 0.062485 | -0.011559 | 0.059881 | 0.0056466 | 0.0079152 | 0.0083539 | -0.0062429 | 0.034921 | 0.0054461 | -122.0908 | -0.16342 | -122.656 | 0.1849 | -0.10496 | 0.36174 | -122.4714 | 0.060571 | 0.046146 | 0.007751 | 0.15776 | 0.27011 | -0.17081 | -0.22367 | 0.21837 | -0.021093 | 0.599 | 0.033852 | -0.18452 | -0.31095 | 0.15574 | 122.4661 | -0.04823 | 122.7504 | 122.6976 | 0.23142 | 0.064114 | -0.37681 | 122.8747 | 122.5849 | 123.0516 | 122.5264 | -122.6774 | 122.8476 | 122.9599 | 122.519 | 122.736 | -0.42967
838.25 | 123.0148 | -122.6578 | 0.17853 | 1.4211e-13 | -0.016414 | -0.00092531 | 0.062699 | -0.011345 | 0.059667 | 0.013277 | 0.0079152 | 0.0083539 | -0.0060291 | 0.034921 | 0.0056597 | -122.0862 | -0.16342 | -122.656 | 0.18032 | -0.095798 | 0.36632 | -122.4623 | 0.060571 | 0.041567 | 0.003172 | 0.14403 | 0.27011 | -0.17081 | -0.2191 | 0.19549 | 0.001795 | 0.57153 | 0.001809 | -0.19368 | -0.27433 | 0.18779 | 122.4387 | -0.0345 | 122.7183 | 122.6609 | 0.22227 | 0.09158 | -0.34934 | 122.8381 | 122.562 | 123.0241 | 122.4944 | -122.6408 | 122.8018 | 122.9279 | 122.487 | 122.6993 | -0.39762
839.9375 | 122.8775 | -122.6807 | 0.20599 | 1.4211e-13 | -0.016414 | -0.00071151 | 0.062699 | -0.011559 | 0.059667 | 0.013277 | 0.0083426 | 0.0079267 | -0.0060291 | 0.034921 | 0.0058733 | -122.0862 | -0.15427 | -122.656 | 0.18032 | -0.086641 | 0.35716 | -122.4669 | 0.055992 | 0.036989 | 0.003172 | 0.14861 | 0.27011 | -0.17081 | -0.22367 | 0.2138 | -0.025671 | 0.59442 | 0.024697 | -0.1891 | -0.29263 | 0.15117 | 122.457 | -0.057387 | 122.7367 | 122.6838 | 0.22685 | 0.064114 | -0.37681 | 122.861 | 122.594 | 123.0378 | 122.5264 | -122.6729 | 122.8293 | 122.9508 | 122.5098 | 122.7177 | -0.42967
841.6719 | 122.9874 | -122.6898 | 0.15564 | 1.4211e-13 | -0.016628 | -0.00049791 | 0.062485 | -0.011132 | 0.059454 | -0.0019839 | 0.008129 | 0.0081403 | -0.0064565 | 0.034921 | 0.0056597 | -122.0862 | -0.168 | -122.656 | 0.1849 | -0.09122 | 0.31137 | -122.4669 | 0.060571 | 0.036989 | 0.007751 | 0.15776 | 0.28384 | -0.17539 | -0.23283 | 0.22295 | 0.029261 | 0.60358 | 0.033852 | -0.1891 | -0.24686 | 0.15573 | 122.457 | 0.002124 | 122.7504 | 122.6976 | 0.24058 | 0.1282 | -0.33103 | 122.8747 | 122.5986 | 123.0012 | 122.5218 | -122.6225 | 122.8476 | 122.9737 | 122.5144 | 122.7268 | -0.38847
843.4219 | 122.9233 | -122.699 | 0.21057 | 1.4211e-13 | -0.016842 | -0.00092531 | 0.062485 | -0.011773 | 0.059881 | 0.0056466 | 0.0083426 | 0.0083539 | -0.0060291 | 0.034707 | 0.0054461 | -122.0817 | -0.15427 | -122.6468 | 0.1849 | -0.09122 | 0.34342 | -122.4669 | 0.06515 | 0.046146 | 0.003172 | 0.16234 | 0.28842 | -0.17081 | -0.22367 | 0.23211 | -0.02567 | 0.61731 | 0.052165 | -0.17994 | -0.30179 | 0.13285 | 122.4753 | -0.048229 | 122.7641 | 122.7021 | 0.22685 | 0.077852 | -0.38139 | 122.8839 | 122.6078 | 123.0424 | 122.5447 | -122.6774 | 122.8613 | 122.9874 | 122.5282 | 122.7451 | -0.43424
845.1094 | 122.9462 | -122.6761 | 0.19226 | 1.4211e-13 | -0.016628 | -0.00071151 | 0.062485 | -0.011345 | 0.059667 | 0.0056466 | 0.0079152 | 0.0081403 | -0.0064565 | 0.035134 | 0.0056597 | -122.0817 | -0.168 | -122.6468 | 0.18032 | -0.10038 | 0.32969 | -122.4577 | 0.06515 | 0.036989 | 0.003172 | 0.16234 | 0.27926 | -0.17081 | -0.22367 | 0.21838 | -0.011938 | 0.59442 | 0.029276 | -0.1891 | -0.29264 | 0.13743 | 122.4524 | -0.029919 | 122.7412 | 122.6793 | 0.22685 | 0.087004 | -0.36308 | 122.8564 | 122.5757 | 123.0058 | 122.5081 | -122.65 | 122.8384 | 122.9554 | 122.5053 | 122.7131 | -0.41593
846.8438 | 123.0057 | -122.6898 | 0.17395 | 1.4211e-13 | -0.016842 | -0.00071151 | 0.062272 | -0.011559 | 0.059881 | 0.0056466 | 0.0077016 | 0.0081403 | -0.0062429 | 0.035134 | 0.0052323 | -122.0817 | -0.16342 | -122.656 | 0.17574 | -0.09122 | 0.3068 | -122.4623 | 0.069728 | 0.050725 | 0.01233 | 0.15776 | 0.27469 | -0.17539 | -0.22367 | 0.22753 | 0.001794 | 0.60815 | 0.033852 | -0.19368 | -0.26517 | 0.13285 | 122.4661 | -0.016186 | 122.7595 | 122.7021 | 0.236 | 0.10074 | -0.34934 | 122.8656 | 122.5986 | 122.9966 | 122.5264 | -122.6362 | 122.8476 | 122.9645 | 122.5144 | 122.7405 | -0.39762
848.5312 | 122.8683 | -122.731 | 0.18768 | 1.4211e-13 | -0.016414 | -0.00049791 | 0.062699 | -0.011559 | 0.059667 | 0.0056466 | 0.0079152 | 0.0083539 | -0.0062429 | 0.034921 | 0.0054461 | -122.0862 | -0.15884 | -122.6514 | 0.18032 | -0.10496 | 0.36174 | -122.4623 | 0.051413 | 0.046146 | 0.01233 | 0.15318 | 0.28384 | -0.17081 | -0.22367 | 0.26873 | -0.00736 | 0.64478 | 0.07963 | -0.1891 | -0.29264 | 0.17406 | 122.5073 | -0.034498 | 122.7824 | 122.7433 | 0.236 | 0.096161 | -0.3585 | 122.9113 | 122.6261 | 123.0928 | 122.5722 | -122.65 | 122.8842 | 123.0149 | 122.5602 | 122.7772 | -0.41136
850.2656 | 122.8546 | -122.6944 | 0.20142 | 1.4211e-13 | -0.016628 | -0.00092531 | 0.062485 | -0.011345 | 0.059881 | 0.0056466 | 0.0085562 | 0.0079267 | -0.0064565 | 0.034707 | 0.0058733 | -122.0496 | -0.16342 | -122.6056 | 0.18032 | -0.086641 | 0.36174 | -122.444 | 0.055992 | 0.041567 | 0.01233 | 0.15776 | 0.27926 | -0.17081 | -0.22367 | 0.25042 | -0.021093 | 0.64478 | 0.088791 | -0.16163 | -0.28806 | 0.16032 | 122.4707 | -0.043652 | 122.7504 | 122.7067 | 0.236 | 0.077849 | -0.37223 | 122.8747 | 122.6078 | 123.0561 | 122.531 | -122.6454 | 122.8522 | 122.9737 | 122.5236 | 122.736 | -0.42509
851.9531 | 123.0331 | -122.6532 | 0.1831 | 1.4211e-13 | -0.016842 | -0.00092531 | 0.062699 | -0.011132 | 0.060095 | 0.0056466 | 0.0079152 | 0.0079267 | -0.0060291 | 0.035134 | 0.0058733 | -122.0817 | -0.16342 | -122.6468 | 0.18948 | -0.086641 | 0.36632 | -122.4623 | 0.074307 | 0.041567 | 0.003172 | 0.15776 | 0.28842 | -0.17539 | -0.22367 | 0.19091 | 0.006374 | 0.57153 | 0.006388 | -0.18452 | -0.26975 | 0.18321 | 122.4295 | -0.025341 | 122.7275 | 122.6564 | 0.22685 | 0.10532 | -0.3585 | 122.8427 | 122.5666 | 123.0195 | 122.4898 | -122.6454 | 122.811 | 122.9416 | 122.4778 | 122.6948 | -0.40678
853.7031 | 122.9599 | -122.6852 | 0.1831 | 1.4211e-13 | -0.017055 | -0.00071151 | 0.062485 | -0.011559 | 0.059454 | -0.0019839 | 0.0077016 | 0.0081403 | -0.0064565 | 0.035134 | 0.0058733 | -122.0817 | -0.16342 | -122.6468 | 0.1849 | -0.095798 | 0.35716 | -122.4623 | 0.060571 | 0.041567 | 0.01233 | 0.15318 | 0.27926 | -0.16166 | -0.2191 | 0.22295 | 0.001796 | 0.60358 | 0.038432 | -0.18452 | -0.2789 | 0.17405 | 122.4661 | -0.02992 | 122.7458 | 122.6976 | 0.23143 | 0.09616 | -0.34476 | 122.8701 | 122.5894 | 123.0424 | 122.5218 | -122.6454 | 122.8384 | 122.9645 | 122.5236 | 122.7268 | -0.4022
855.4531 | 122.9599 | -122.7036 | 0.15106 | 1.4211e-13 | -0.016628 | -0.00092531 | 0.062699 | -0.011559 | 0.059667 | 0.0056466 | 0.0083426 | 0.0081403 | -0.0060291 | 0.034921 | 0.0056597 | -122.0862 | -0.16342 | -122.656 | 0.18032 | -0.095798 | 0.31595 | -122.4623 | 0.069728 | 0.050725 | 0.007751 | 0.16234 | 0.28384 | -0.17539 | -0.2191 | 0.24126 | 0.029261 | 0.61731 | 0.047585 | -0.19368 | -0.24686 | 0.16489 | 122.4845 | 0.01128 | 122.7733 | 122.7113 | 0.22685 | 0.13278 | -0.32645 | 122.8839 | 122.6078 | 123.0195 | 122.5401 | -122.6134 | 122.8659 | 122.9874 | 122.5282 | 122.7543 | -0.37016
857.2031 | 122.8729 | -122.699 | 0.21057 | 1.4211e-13 | -0.016414 | -0.00071151 | 0.062699 | -0.011559 | 0.059881 | 0.0056466 | 0.0083426 | 0.0081403 | -0.0066701 | 0.034921 | 0.0054461 | -122.0771 | -0.16342 | -122.6468 | 0.1849 | -0.095798 | 0.31595 | -122.4623 | 0.060571 | 0.041567 | 0.007751 | 0.15776 | 0.28842 | -0.17081 | -0.22367 | 0.23669 | -0.02567 | 0.62189 | 0.052165 | -0.18452 | -0.30637 | 0.10538 | 122.4753 | -0.052807 | 122.7595 | 122.7067 | 0.23142 | 0.077852 | -0.38139 | 122.8839 | 122.6032 | 123.0149 | 122.5356 | -122.6729 | 122.8567 | 122.9874 | 122.5282 | 122.7405 | -0.43424
858.875 | 122.9553 | -122.6898 | 0.17395 | 1.4211e-13 | -0.016628 | -0.00071151 | 0.062913 | -0.011559 | 0.059667 | 0.0056466 | 0.008129 | 0.0079267 | -0.0058155 | 0.034921 | 0.0054461 | -122.0817 | -0.17716 | -122.6514 | 0.17574 | -0.095798 | 0.31137 | -122.4577 | 0.069728 | 0.046146 | 0.003172 | 0.15776 | 0.28384 | -0.16624 | -0.2191 | 0.23211 | 0.001794 | 0.60815 | 0.038431 | -0.19368 | -0.26975 | 0.13742 | 122.4707 | -0.016186 | 122.7595 | 122.693 | 0.22227 | 0.10989 | -0.34019 | 122.8656 | 122.594 | 123.0012 | 122.5127 | -122.6317 | 122.8476 | 122.9737 | 122.5236 | 122.736 | -0.39304
860.6094 | 122.9507 | -122.6669 | 0.17853 | 1.4211e-13 | -0.017055 | -0.00092531 | 0.062699 | -0.011986 | 0.059881 | -0.0019839 | 0.0079152 | 0.0079267 | -0.0062429 | 0.035134 | 0.0054461 | -122.0817 | -0.16342 | -122.6468 | 0.18032 | -0.09122 | 0.35258 | -122.4623 | 0.069728 | 0.050725 | 0.016908 | 0.16234 | 0.28384 | -0.17539 | -0.22825 | 0.20464 | 0.001795 | 0.58527 | 0.020121 | -0.18452 | -0.26975 | 0.17405 | 122.4387 | -0.016186 | 122.7367 | 122.6838 | 0.24516 | 0.10532 | -0.35392 | 122.8473 | 122.5757 | 123.0195 | 122.5035 | -122.6408 | 122.8293 | 122.9508 | 122.4915 | 122.7177 | -0.40678
862.2969 | 122.8226 | -122.7127 | 0.21973 | 1.4211e-13 | -0.016628 | -0.00071151 | 0.062699 | -0.011986 | 0.059667 | 0.013277 | 0.0079152 | 0.0081403 | -0.0062429 | 0.034921 | 0.0054461 | -122.0817 | -0.16342 | -122.6468 | 0.18032 | -0.10038 | 0.32511 | -122.4577 | 0.055992 | 0.041567 | 0.007751 | 0.15776 | 0.28384 | -0.16624 | -0.22367 | 0.255 | -0.039404 | 0.63104 | 0.065898 | -0.1891 | -0.3201 | 0.10538 | 122.489 | -0.061963 | 122.7687 | 122.7205 | 0.23142 | 0.064117 | -0.38596 | 122.893 | 122.6123 | 123.0378 | 122.5493 | -122.6774 | 122.8705 | 122.9966 | 122.5465 | 122.7543 | -0.4434
864.0469 | 123.0331 | -122.6761 | 0.17395 | 1.4211e-13 | -0.016414 | -0.00092531 | 0.062699 | -0.011559 | 0.060095 | -0.0019839 | 0.008129 | 0.0083539 | -0.0062429 | 0.034921 | 0.0052323 | -122.0725 | -0.15884 | -122.6422 | 0.1849 | -0.10038 | 0.35716 | -122.4623 | 0.06515 | 0.041567 | 0.003172 | 0.14861 | 0.27926 | -0.17539 | -0.22825 | 0.2138 | 0.010951 | 0.60358 | 0.033854 | -0.17994 | -0.27433 | 0.18321 | 122.4478 | -0.025343 | 122.7412 | 122.6793 | 0.23142 | 0.10531 | -0.34934 | 122.861 | 122.5757 | 123.0332 | 122.5172 | -122.6362 | 122.8247 | 122.9554 | 122.5007 | 122.7177 | -0.4022
865.7188 | 122.8683 | -122.699 | 0.20599 | 1.4211e-13 | -0.016842 | -0.00071151 | 0.062485 | -0.011559 | 0.060095 | 0.0056466 | 0.008129 | 0.0077131 | -0.0064565 | 0.034921 | 0.0054461 | -122.0817 | -0.16342 | -122.656 | 0.17574 | -0.095798 | 0.34342 | -122.4531 | 0.069728 | 0.036989 | 0.003172 | 0.15318 | 0.28842 | -0.16624 | -0.22367 | 0.24584 | -0.03025 | 0.61731 | 0.043008 | -0.20284 | -0.30179 | 0.13743 | 122.4753 | -0.052809 | 122.7687 | 122.7021 | 0.22685 | 0.082429 | -0.37223 | 122.8747 | 122.6032 | 123.0424 | 122.5356 | -122.6591 | 122.8522 | 122.9874 | 122.5327 | 122.736 | -0.42967
867.4688 | 122.8867 | -122.7173 | 0.21057 | 1.4211e-13 | -0.016628 | -0.00049791 | 0.062485 | -0.011559 | 0.059881 | 0.013277 | 0.0079152 | 0.0081403 | -0.0062429 | 0.034921 | 0.0056597 | -122.0817 | -0.17258 | -122.6514 | 0.17574 | -0.095798 | 0.35716 | -122.4531 | 0.060571 | 0.046146 | 0.007751 | 0.15776 | 0.28842 | -0.17081 | -0.22367 | 0.26415 | -0.034827 | 0.63562 | 0.065897 | -0.19826 | -0.30637 | 0.14659 | 122.4936 | -0.052807 | 122.7779 | 122.725 | 0.23142 | 0.077852 | -0.38139 | 122.893 | 122.6215 | 123.0744 | 122.5447 | -122.6637 | 122.875 | 123.0057 | 122.5465 | 122.7634 | -0.43424
869.1562 | 122.9965 | -122.6852 | 0.17853 | 1.4211e-13 | -0.016628 | -0.00028411 | 0.062913 | -0.011345 | 0.059881 | 0.013277 | 0.0083426 | 0.0083539 | -0.0062429 | 0.035134 | 0.0058733 | -122.0817 | -0.15884 | -122.6514 | 0.1849 | -0.09122 | 0.32053 | -122.4577 | 0.060571 | 0.050725 | 0.003172 | 0.16692 | 0.28384 | -0.17081 | -0.22367 | 0.22753 | 0.006373 | 0.60358 | 0.033854 | -0.19368 | -0.26975 | 0.142 | 122.4616 | -0.011607 | 122.7458 | 122.6884 | 0.22685 | 0.10532 | -0.34934 | 122.8701 | 122.594 | 123.0058 | 122.5264 | -122.6362 | 122.8522 | 122.9691 | 122.5144 | 122.736 | -0.4022
870.8906 | 122.9691 | -122.6761 | 0.20599 | 1.4211e-13 | -0.016628 | -0.00071151 | 0.062699 | -0.011559 | 0.059881 | 0.013277 | 0.008129 | 0.0081403 | -0.0062429 | 0.034707 | 0.0056597 | -122.0862 | -0.168 | -122.656 | 0.17574 | -0.095798 | 0.32053 | -122.4623 | 0.069728 | 0.046146 | -0.001407 | 0.15776 | 0.28842 | -0.16624 | -0.22825 | 0.2138 | -0.03025 | 0.58984 | 0.020119 | -0.19368 | -0.30179 | 0.11454 | 122.4478 | -0.04823 | 122.7458 | 122.6747 | 0.22685 | 0.082429 | -0.37223 | 122.8518 | 122.5803 | 122.9966 | 122.5081 | -122.6683 | 122.8338 | 122.9645 | 122.5099 | 122.7222 | -0.43425
872.6406 | 122.8592 | -122.7264 | 0.18768 | 1.4211e-13 | -0.016414 | -0.00049791 | 0.062485 | -0.011345 | 0.059667 | -0.0019839 | 0.008129 | 0.0081403 | -0.0066701 | 0.035348 | 0.0054461 | -122.0817 | -0.17258 | -122.6468 | 0.18032 | -0.10038 | 0.35258 | -122.4577 | 0.069728 | 0.046146 | 0.003172 | 0.15776 | 0.293 | -0.17081 | -0.22367 | 0.26873 | -0.00736 | 0.64477 | 0.07963 | -0.1891 | -0.28806 | 0.1649 | 122.5028 | -0.029919 | 122.7962 | 122.7296 | 0.22685 | 0.10532 | -0.3585 | 122.9068 | 122.6261 | 123.079 | 122.5539 | -122.6454 | 122.8842 | 123.0194 | 122.5556 | 122.7726 | -0.41136
874.3125 | 122.8867 | -122.7173 | 0.21973 | 1.4211e-13 | -0.016628 | -0.00049791 | 0.062699 | -0.011559 | 0.059881 | -0.0019839 | 0.0079152 | 0.0081403 | -0.0062429 | 0.034921 | 0.0052323 | -122.0771 | -0.168 | -122.6468 | 0.18032 | -0.10038 | 0.348 | -122.4623 | 0.069728 | 0.041567 | 0.007751 | 0.15318 | 0.28842 | -0.17081 | -0.22367 | 0.255 | -0.039404 | 0.6402 | 0.070475 | -0.18452 | -0.3201 | 0.12828 | 122.4936 | -0.066542 | 122.787 | 122.725 | 0.23142 | 0.068696 | -0.39054 | 122.8976 | 122.6169 | 123.0653 | 122.5493 | -122.682 | 122.8705 | 123.0057 | 122.5465 | 122.7589 | -0.4434
876.0625 | 122.8821 | -122.7081 | 0.19226 | 1.4211e-13 | -0.017055 | -0.00071151 | 0.062485 | -0.011559 | 0.059881 | 0.013277 | 0.0083426 | 0.0079267 | -0.0062429 | 0.034921 | 0.0054461 | -122.0817 | -0.15884 | -122.6514 | 0.18032 | -0.10038 | 0.35258 | -122.4669 | 0.060571 | 0.041567 | 0.003172 | 0.15776 | 0.28842 | -0.17081 | -0.22825 | 0.24126 | -0.011938 | 0.62646 | 0.056742 | -0.18452 | -0.29264 | 0.16032 | 122.4799 | -0.034497 | 122.7687 | 122.7113 | 0.23142 | 0.096162 | -0.36308 | 122.8885 | 122.6078 | 123.0607 | 122.5493 | -122.6591 | 122.8659 | 122.9966 | 122.5373 | 122.7497 | -0.42051
877.75 | 122.8683 | -122.7127 | 0.21057 | 1.4211e-13 | -0.016842 | -0.00071151 | 0.062699 | -0.011559 | 0.060308 | -0.0019839 | 0.0079152 | 0.0083539 | -0.0064565 | 0.035134 | 0.0054461 | -122.0771 | -0.168 | -122.6377 | 0.1849 | -0.10038 | 0.31137 | -122.4623 | 0.06515 | 0.036989 | 0.007751 | 0.15776 | 0.28384 | -0.17081 | -0.22367 | 0.25042 | -0.02567 | 0.63562 | 0.075054 | -0.17536 | -0.31095 | 0.1008 | 122.489 | -0.052807 | 122.7779 | 122.7205 | 0.23142 | 0.073273 | -0.38139 | 122.8976 | 122.6123 | 123.0241 | 122.5447 | -122.6729 | 122.8705 | 122.9966 | 122.5419 | 122.7497 | -0.43424
879.5 | 122.9828 | -122.6486 | 0.16937 | 1.4211e-13 | -0.016628 | -0.00049791 | 0.062485 | -0.011559 | 0.059454 | -0.0019839 | 0.0079152 | 0.0079267 | -0.0060291 | 0.035348 | 0.0056597 | -122.0862 | -0.17258 | -122.6514 | 0.18032 | -0.10038 | 0.30222 | -122.4577 | 0.060571 | 0.041567 | 0.003172 | 0.16234 | 0.28842 | -0.17539 | -0.22825 | 0.19091 | 0.01095 | 0.56238 | -0.002767 | -0.19368 | -0.26975 | 0.13284 | 122.4204 | -0.007031 | 122.7092 | 122.6518 | 0.23142 | 0.11905 | -0.34477 | 122.8289 | 122.5482 | 122.9508 | 122.476 | -122.6271 | 122.811 | 122.937 | 122.4732 | 122.6902 | -0.39763
881.25 | 122.937 | -122.6807 | 0.16479 | 1.4211e-13 | -0.017055 | -0.00092531 | 0.062699 | -0.011345 | 0.059667 | -0.0019839 | 0.008129 | 0.0085677 | -0.0064565 | 0.035348 | 0.0052323 | -122.0862 | -0.15884 | -122.6422 | 0.18032 | -0.10038 | 0.32511 | -122.4531 | 0.06515 | 0.041567 | 0.003172 | 0.16692 | 0.27469 | -0.17081 | -0.23283 | 0.22753 | 0.015528 | 0.59442 | 0.038432 | -0.1891 | -0.26517 | 0.16032 | 122.4478 | 0.002126 | 122.7458 | 122.6838 | 0.236 | 0.10989 | -0.33561 | 122.861 | 122.5803 | 123.0058 | 122.5218 | -122.6179 | 122.8476 | 122.9554 | 122.5098 | 122.7222 | -0.39763
883 | 122.8867 | -122.7127 | 0.20599 | 1.4211e-13 | -0.016842 | -0.00092531 | 0.062699 | -0.011773 | 0.059881 | 0.0056466 | 0.008129 | 0.0079267 | -0.0064565 | 0.035348 | 0.0052323 | -122.0817 | -0.168 | -122.6422 | 0.17574 | -0.095798 | 0.3068 | -122.4623 | 0.060571 | 0.041567 | 0.016908 | 0.16234 | 0.28384 | -0.17539 | -0.22367 | 0.25042 | -0.03025 | 0.63104 | 0.070476 | -0.17994 | -0.30179 | 0.1008 | 122.489 | -0.043652 | 122.7733 | 122.7296 | 0.24058 | 0.07785 | -0.38139 | 122.8885 | 122.6169 | 123.0195 | 122.5447 | -122.6683 | 122.8751 | 122.9966 | 122.5373 | 122.7543 | -0.42967
884.6719 | 122.85 | -122.7264 | 0.20599 | 1.4211e-13 | -0.016628 | -0.00071151 | 0.062272 | -0.011559 | 0.059667 | 0.0056466 | 0.008129 | 0.0081403 | -0.0064565 | 0.035134 | 0.0052323 | -122.0862 | -0.168 | -122.6468 | 0.17574 | -0.086641 | 0.32511 | -122.4623 | 0.06515 | 0.03241 | 0.01233 | 0.15776 | 0.27926 | -0.17081 | -0.22367 | 0.26415 | -0.03025 | 0.6402 | 0.07963 | -0.18452 | -0.29263 | 0.11912 | 122.5028 | -0.04823 | 122.7916 | 122.7388 | 0.236 | 0.073271 | -0.37681 | 122.9022 | 122.6398 | 123.0515 | 122.5584 | -122.6683 | 122.8842 | 123.0057 | 122.5556 | 122.7588 | -0.42967
886.4219 | 122.9599 | -122.6715 | 0.17395 | 1.4211e-13 | -0.017269 | -0.00071151 | 0.062485 | -0.011345 | 0.059454 | -0.0019839 | 0.0077016 | 0.0083539 | -0.0062429 | 0.034921 | 0.0052323 | -122.0771 | -0.17258 | -122.6468 | 0.1849 | -0.09122 | 0.34342 | -122.4531 | 0.06515 | 0.036989 | 0.007751 | 0.16234 | 0.27469 | -0.17081 | -0.22367 | 0.21838 | 0.010951 | 0.59442 | 0.024699 | -0.19368 | -0.26517 | 0.16947 | 122.4478 | -0.011608 | 122.7367 | 122.6793 | 0.23142 | 0.10074 | -0.34476 | 122.8564 | 122.5803 | 123.0149 | 122.4989 | -122.6271 | 122.8339 | 122.9462 | 122.5007 | 122.7085 | -0.39762
888.1719 | 122.905 | -122.7081 | 0.18768 | 1.4211e-13 | -0.017269 | -0.00092531 | 0.062699 | -0.011345 | 0.060308 | 0.0056466 | 0.008129 | 0.0079267 | -0.0062429 | 0.035134 | 0.0054461 | -122.0817 | -0.168 | -122.6377 | 0.1849 | -0.10953 | 0.3068 | -122.4623 | 0.06515 | 0.036989 | 0.003172 | 0.15776 | 0.28384 | -0.17081 | -0.2191 | 0.24584 | -0.002782 | 0.62646 | 0.070476 | -0.17536 | -0.29722 | 0.11911 | 122.489 | -0.029919 | 122.7733 | 122.7113 | 0.22227 | 0.096161 | -0.3585 | 122.893 | 122.5986 | 123.0149 | 122.5401 | -122.65 | 122.8659 | 122.992 | 122.5373 | 122.7451 | -0.40678
889.9062 | 123.0011 | -122.6532 | 0.17395 | 1.4211e-13 | -0.016842 | -0.00092531 | 0.062485 | -0.011345 | 0.059881 | -0.0019839 | 0.008129 | 0.0079267 | -0.0062429 | 0.035134 | 0.0054461 | -122.0862 | -0.18174 | -122.6422 | 0.17574 | -0.09122 | 0.36174 | -122.4531 | 0.060571 | 0.036989 | 0.007751 | 0.16234 | 0.28384 | -0.17081 | -0.22825 | 0.20007 | 0.001794 | 0.56696 | 0.010966 | -0.1891 | -0.26517 | 0.18779 | 122.4249 | -0.011608 | 122.7138 | 122.6609 | 0.236 | 0.10989 | -0.34476 | 122.8289 | 122.562 | 123.0149 | 122.4715 | -122.6271 | 122.8155 | 122.937 | 122.4824 | 122.6902 | -0.4022
891.5938 | 122.9095 | -122.7081 | 0.20142 | 1.4211e-13 | -0.016842 | -0.0011389 | 0.062913 | -0.011773 | 0.059667 | 0.013277 | 0.0083426 | 0.0081403 | -0.0062429 | 0.035562 | 0.0054461 | -122.0771 | -0.17716 | -122.6422 | 0.17117 | -0.095798 | 0.36174 | -122.4577 | 0.060571 | 0.036989 | 0.007751 | 0.16234 | 0.28842 | -0.17539 | -0.22825 | 0.25042 | -0.03025 | 0.63104 | 0.065898 | -0.18452 | -0.29721 | 0.16032 | 122.4799 | -0.039074 | 122.7687 | 122.7159 | 0.236 | 0.087007 | -0.37681 | 122.8793 | 122.6123 | 123.0699 | 122.531 | -122.6591 | 122.8705 | 122.9966 | 122.5327 | 122.7451 | -0.42967
893.3594 | 122.9462 | -122.6852 | 0.16479 | 1.4211e-13 | -0.017269 | -0.00049791 | 0.062699 | -0.011559 | 0.059667 | 0.0056466 | 0.008129 | 0.0079267 | -0.0062429 | 0.035134 | 0.0056597 | -122.0771 | -0.168 | -122.6468 | 0.18032 | -0.095798 | 0.36174 | -122.4623 | 0.074307 | 0.041567 | 0.003172 | 0.15776 | 0.28384 | -0.17081 | -0.22825 | 0.22295 | 0.015528 | 0.60816 | 0.038432 | -0.18452 | -0.26059 | 0.19694 | 122.457 | -0.007031 | 122.7595 | 122.6884 | 0.23142 | 0.11905 | -0.33561 | 122.8656 | 122.5894 | 123.047 | 122.5172 | -122.6271 | 122.843 | 122.9691 | 122.5144 | 122.7268 | -0.39305
895.0312 | 122.8958 | -122.7127 | 0.19226 | 1.4211e-13 | -0.017055 | -0.00049791 | 0.062913 | -0.011345 | 0.060095 | -0.0019839 | 0.0079152 | 0.0079267 | -0.0064565 | 0.035562 | 0.0054461 | -122.0725 | -0.168 | -122.6422 | 0.17574 | -0.09122 | 0.32511 | -122.4623 | 0.069728 | 0.041567 | 0.007751 | 0.15776 | 0.27926 | -0.17997 | -0.22367 | 0.25042 | -0.016517 | 0.6402 | 0.070476 | -0.17994 | -0.28348 | 0.13285 | 122.489 | -0.034497 | 122.7824 | 122.7205 | 0.23142 | 0.087004 | -0.37223 | 122.8885 | 122.6215 | 123.0378 | 122.5447 | -122.6546 | 122.8705 | 122.992 | 122.5327 | 122.7543 | -0.41593
896.7656 | 122.9004 | -122.699 | 0.20142 | 1.4211e-13 | -0.016628 | -0.00049791 | 0.062485 | -0.011559 | 0.059454 | 0.0056466 | 0.008129 | 0.0079267 | -0.0064565 | 0.035134 | 0.0054461 | -122.0817 | -0.168 | -122.6514 | 0.18032 | -0.10038 | 0.35258 | -122.4577 | 0.060571 | 0.036989 | 0.003172 | 0.15776 | 0.28384 | -0.17539 | -0.23283 | 0.24126 | -0.021093 | 0.61731 | 0.047587 | -0.19368 | -0.30179 | 0.15117 | 122.4661 | -0.043652 | 122.7595 | 122.7021 | 0.236 | 0.082428 | -0.37681 | 122.8793 | 122.5986 | 123.0516 | 122.531 | -122.6591 | 122.8567 | 122.9828 | 122.5236 | 122.736 | -0.43425
898.5156 | 122.9416 | -122.6761 | 0.17395 | 1.4211e-13 | -0.016842 | -0.0011389 | 0.062485 | -0.011559 | 0.059881 | -0.0019839 | 0.008129 | 0.0083539 | -0.0060291 | 0.035348 | 0.0052323 | -122.0771 | -0.17716 | -122.6514 | 0.17574 | -0.10038 | 0.28848 | -122.4623 | 0.06515 | 0.041567 | -0.001407 | 0.16692 | 0.27926 | -0.17539 | -0.23283 | 0.2138 | 0.001794 | 0.599 | 0.024698 | -0.1891 | -0.27433 | 0.11453 | 122.4433 | -0.007029 | 122.7412 | 122.6747 | 0.23142 | 0.10531 | -0.34934 | 122.8518 | 122.5757 | 122.9646 | 122.4989 | -122.6362 | 122.843 | 122.9554 | 122.5007 | 122.7177 | -0.40678
900.2656 | 122.9599 | -122.6761 | 0.16937 | 1.4211e-13 | -0.017055 | -0.00092531 | 0.062699 | -0.011773 | 0.059667 | 0.020908 | 0.008129 | 0.0081403 | -0.0064565 | 0.035348 | 0.0052323 | -122.0817 | -0.17258 | -122.6468 | 0.17574 | -0.095798 | 0.33885 | -122.4531 | 0.06515 | 0.041567 | 0.003172 | 0.16234 | 0.27926 | -0.17081 | -0.22367 | 0.22295 | 0.006371 | 0.59442 | 0.029276 | -0.19368 | -0.26517 | 0.16947 | 122.4524 | -0.007031 | 122.7412 | 122.6793 | 0.22685 | 0.10989 | -0.34019 | 122.8518 | 122.5803 | 123.0149 | 122.5035 | -122.6225 | 122.8384 | 122.9554 | 122.5053 | 122.7177 | -0.39305
902.0156 | 122.8683 | -122.7356 | 0.2243 | 1.4211e-13 | -0.017269 | -0.00092531 | 0.062699 | -0.011345 | 0.060095 | 0.0056466 | 0.0079152 | 0.0079267 | -0.0064565 | 0.035134 | 0.0050187 | -122.0771 | -0.17716 | -122.6377 | 0.18032 | -0.10038 | 0.36174 | -122.4623 | 0.06515 | 0.041567 | 0.007751 | 0.16234 | 0.28384 | -0.17997 | -0.22825 | 0.27331 | -0.043981 | 0.65851 | 0.097942 | -0.17536 | -0.32468 | 0.13743 | 122.5073 | -0.061962 | 122.8007 | 122.7433 | 0.236 | 0.05954 | -0.40428 | 122.9159 | 122.6352 | 123.0973 | 122.5584 | -122.6866 | 122.8979 | 123.0194 | 122.5556 | 122.7772 | -0.45256
903.7656 | 123.0148 | -122.6624 | 0.16937 | 1.4211e-13 | -0.017055 | -0.00092531 | 0.062699 | -0.011345 | 0.059881 | -0.0019839 | 0.0083426 | 0.0083539 | -0.0066701 | 0.034921 | 0.0054461 | -122.0771 | -0.18174 | -122.6377 | 0.17574 | -0.095798 | 0.31595 | -122.4577 | 0.069728 | 0.041567 | -0.001407 | 0.16234 | 0.28384 | -0.17539 | -0.23283 | 0.20464 | 0.006371 | 0.58527 | 0.0247 | -0.17994 | -0.26517 | 0.14658 | 122.4295 | -0.007031 | 122.7321 | 122.6609 | 0.23142 | 0.11447 | -0.34477 | 122.8381 | 122.5666 | 122.9783 | 122.4806 | -122.6271 | 122.8247 | 122.9462 | 122.487 | 122.7039 | -0.4022
905.4531 | 122.8592 | -122.731 | 0.21973 | 1.4211e-13 | -0.017269 | -0.00071151 | 0.062913 | -0.011345 | 0.059881 | 0.0056466 | 0.0083426 | 0.0083539 | -0.0062429 | 0.035562 | 0.0054461 | -122.0771 | -0.17258 | -122.6377 | 0.17574 | -0.086641 | 0.36174 | -122.4577 | 0.055992 | 0.041567 | 0.007751 | 0.15776 | 0.293 | -0.17539 | -0.22367 | 0.27331 | -0.043983 | 0.65393 | 0.093364 | -0.17994 | -0.30637 | 0.14201 | 122.5073 | -0.061963 | 122.787 | 122.7388 | 0.23142 | 0.073274 | -0.39512 | 122.9068 | 122.6444 | 123.0928 | 122.5584 | -122.6774 | 122.8888 | 123.024 | 122.5556 | 122.7726 | -0.4434
907.2031 | 122.8592 | -122.7264 | 0.20599 | 1.4211e-13 | -0.017269 | -0.00092531 | 0.062699 | -0.011773 | 0.059667 | -0.0019839 | 0.0079152 | 0.0077131 | -0.0066701 | 0.035134 | 0.0052323 | -122.0771 | -0.18174 | -122.6377 | 0.17574 | -0.10038 | 0.33427 | -122.4623 | 0.06515 | 0.041567 | 0.007751 | 0.15776 | 0.28842 | -0.16624 | -0.22367 | 0.26415 | -0.03025 | 0.64935 | 0.088786 | -0.17536 | -0.30637 | 0.12827 | 122.5028 | -0.04823 | 122.7916 | 122.7342 | 0.23142 | 0.082429 | -0.37223 | 122.9022 | 122.6261 | 123.0607 | 122.5447 | -122.6683 | 122.8842 | 123.0149 | 122.5602 | 122.768 | -0.42967
908.9531 | 122.9736 | -122.6852 | 0.1831 | 1.4211e-13 | -0.017269 | -0.00071151 | 0.062699 | -0.011559 | 0.059881 | 0.013277 | 0.0083426 | 0.0081403 | -0.0066701 | 0.035562 | 0.0054461 | -122.0771 | -0.17716 | -122.6377 | 0.18032 | -0.09122 | 0.34342 | -122.4531 | 0.069728 | 0.036989 | 0.003172 | 0.16234 | 0.293 | -0.17081 | -0.22367 | 0.23211 | -0.002782 | 0.60816 | 0.047588 | -0.18452 | -0.27432 | 0.16032 | 122.4616 | -0.020763 | 122.755 | 122.6884 | 0.22685 | 0.1099 | -0.35392 | 122.8656 | 122.594 | 123.0287 | 122.5081 | -122.6362 | 122.8476 | 122.9782 | 122.5144 | 122.7222 | -0.40678
910.625 | 122.9874 | -122.6807 | 0.18768 | 1.4211e-13 | -0.016842 | -0.00071151 | 0.062913 | -0.011773 | 0.059881 | -0.0019839 | 0.0077016 | 0.0081403 | -0.0060291 | 0.035134 | 0.0054461 | -122.0679 | -0.18174 | -122.6285 | 0.17117 | -0.095798 | 0.34342 | -122.4531 | 0.06515 | 0.03241 | 0.01233 | 0.15776 | 0.27926 | -0.17081 | -0.22367 | 0.22753 | -0.016517 | 0.61273 | 0.052167 | -0.17537 | -0.28348 | 0.15574 | 122.457 | -0.029919 | 122.7458 | 122.693 | 0.236 | 0.091582 | -0.3585 | 122.8518 | 122.5849 | 123.0241 | 122.4989 | -122.6408 | 122.8384 | 122.9599 | 122.5098 | 122.7131 | -0.41136
912.3594 | 122.8638 | -122.7219 | 0.17853 | 1.4211e-13 | -0.017269 | -0.00071151 | 0.062699 | -0.011345 | 0.059881 | -0.0019839 | 0.008129 | 0.0081403 | -0.0064565 | 0.035775 | 0.0052323 | -122.0817 | -0.17716 | -122.6285 | 0.17574 | -0.095798 | 0.32511 | -122.4577 | 0.060571 | 0.036989 | 0.003172 | 0.15318 | 0.27926 | -0.17539 | -0.22367 | 0.26415 | -0.002784 | 0.6402 | 0.093366 | -0.17079 | -0.27433 | 0.14658 | 122.4982 | -0.025343 | 122.7824 | 122.725 | 0.22685 | 0.10074 | -0.35392 | 122.8976 | 122.6261 | 123.047 | 122.5447 | -122.6362 | 122.875 | 123.0011 | 122.5465 | 122.7589 | -0.4022
914.0938 | 122.85 | -122.7081 | 0.20599 | 1.4211e-13 | -0.017055 | -0.00092531 | 0.062699 | -0.011773 | 0.059667 | -0.0019839 | 0.0079152 | 0.0081403 | -0.0064565 | 0.035562 | 0.0054461 | -122.0862 | -0.18632 | -122.6285 | 0.17574 | -0.09122 | 0.35258 | -122.4577 | 0.074307 | 0.041567 | 0.003172 | 0.15318 | 0.293 | -0.16624 | -0.22825 | 0.25042 | -0.03025 | 0.62189 | 0.079633 | -0.17079 | -0.29721 | 0.14659 | 122.4799 | -0.052809 | 122.7824 | 122.7113 | 0.23142 | 0.087007 | -0.37223 | 122.8839 | 122.6169 | 123.0607 | 122.5218 | -122.6637 | 122.8613 | 123.0011 | 122.5419 | 122.7497 | -0.43425
915.7656 | 122.85 | -122.7173 | 0.19684 | 1.4211e-13 | -0.017055 | -0.0011389 | 0.062699 | -0.011773 | 0.059667 | 0.0056466 | 0.008129 | 0.0081403 | -0.0064565 | 0.035348 | 0.0056597 | -122.0725 | -0.168 | -122.6331 | 0.17574 | -0.10038 | 0.35258 | -122.4623 | 0.069728 | 0.036989 | 0.01233 | 0.16234 | 0.28384 | -0.17539 | -0.22367 | 0.255 | -0.021094 | 0.64478 | 0.08421 | -0.17079 | -0.29722 | 0.15574 | 122.4936 | -0.034496 | 122.787 | 122.7296 | 0.236 | 0.087006 | -0.37223 | 122.893 | 122.6169 | 123.0699 | 122.5493 | -122.6591 | 122.8796 | 123.0011 | 122.5419 | 122.7543 | -0.42051
917.5 | 122.8455 | -122.6944 | 0.20142 | 1.4211e-13 | -0.016842 | -0.0011389 | 0.062485 | -0.011559 | 0.059667 | -0.0096144 | 0.0079152 | 0.0083539 | -0.0060291 | 0.035562 | 0.0050187 | -122.0679 | -0.17716 | -122.6377 | 0.17574 | -0.09122 | 0.35716 | -122.4577 | 0.060571 | 0.041567 | 0.007751 | 0.15776 | 0.27926 | -0.16624 | -0.22825 | 0.23669 | -0.025672 | 0.62647 | 0.056743 | -0.17994 | -0.29264 | 0.15574 | 122.4661 | -0.043652 | 122.755 | 122.7021 | 0.236 | 0.077849 | -0.36765 | 122.8701 | 122.6032 | 123.0516 | 122.5172 | -122.6591 | 122.8522 | 122.9737 | 122.5282 | 122.736 | -0.42967
919.25 | 122.9645 | -122.6715 | 0.17853 | 1.4211e-13 | -0.017055 | -0.00071151 | 0.062485 | -0.011345 | 0.060308 | 0.013277 | 0.0079152 | 0.0077131 | -0.0062429 | 0.035348 | 0.0048051 | -122.0771 | -0.18174 | -122.6285 | 0.17117 | -0.09122 | 0.35258 | -122.4577 | 0.060571 | 0.041567 | 0.003172 | 0.16234 | 0.28842 | -0.17081 | -0.23283 | 0.2138 | -0.007362 | 0.59442 | 0.043012 | -0.17079 | -0.26975 | 0.17405 | 122.4387 | -0.016186 | 122.7321 | 122.6747 | 0.236 | 0.10989 | -0.34934 | 122.8427 | 122.5803 | 123.0241 | 122.4898 | -122.6362 | 122.8339 | 122.9599 | 122.5007 | 122.7131 | -0.41136
921 | 122.8546 | -122.7036 | 0.17853 | 1.4211e-13 | -0.017055 | -0.0011389 | 0.062485 | -0.011773 | 0.059667 | -0.0019839 | 0.007488 | 0.0083539 | -0.0062429 | 0.035134 | 0.0052323 | -122.0634 | -0.18174 | -122.6239 | 0.17574 | -0.095798 | 0.30222 | -122.444 | 0.06515 | 0.036989 | 0.007751 | 0.16234 | 0.293 | -0.17539 | -0.23283 | 0.25958 | -0.002784 | 0.6402 | 0.079633 | -0.17995 | -0.27433 | 0.12369 | 122.4707 | -0.016186 | 122.7687 | 122.7113 | 0.24058 | 0.11447 | -0.35392 | 122.8793 | 122.6078 | 123.0058 | 122.5218 | -122.6225 | 122.8659 | 122.9966 | 122.5282 | 122.7405 | -0.41136
922.6719 | 122.8317 | -122.6669 | 0.19226 | 1.4211e-13 | -0.016842 | -0.00092531 | 0.062699 | -0.011559 | 0.059667 | -0.0019839 | 0.008129 | 0.0079267 | -0.0062429 | 0.035134 | 0.0056597 | -122.0679 | -0.18632 | -122.6285 | 0.17117 | -0.10038 | 0.34342 | -122.4531 | 0.060571 | 0.041567 | 0.003172 | 0.15318 | 0.28842 | -0.17539 | -0.22825 | 0.2138 | -0.021095 | 0.599 | 0.038434 | -0.17537 | -0.29264 | 0.15116 | 122.4387 | -0.039076 | 122.7275 | 122.6701 | 0.23142 | 0.096162 | -0.36765 | 122.8381 | 122.5666 | 123.0104 | 122.4806 | -122.6454 | 122.8201 | 122.9554 | 122.4915 | 122.7085 | -0.42051
924.4375 | 122.9279 | -122.6807 | 0.15564 | 1.4211e-13 | -0.017055 | -0.00092531 | 0.062699 | -0.011773 | 0.060095 | 0.0056466 | 0.0083426 | 0.0079267 | -0.0062429 | 0.035562 | 0.0052323 | -122.0771 | -0.18632 | -122.6331 | 0.17117 | -0.10496 | 0.3068 | -122.4486 | 0.06515 | 0.036989 | 0.003172 | 0.1715 | 0.28842 | -0.17539 | -0.2191 | 0.23211 | 0.015526 | 0.60358 | 0.047589 | -0.18452 | -0.2606 | 0.15116 | 122.4616 | 0.015859 | 122.7458 | 122.6838 | 0.22227 | 0.13278 | -0.33103 | 122.8518 | 122.5757 | 122.9875 | 122.4943 | -122.6042 | 122.8522 | 122.9691 | 122.5053 | 122.7177 | -0.37474
926.125 | 122.937 | -122.6944 | 0.17395 | 1.4211e-13 | -0.017269 | -0.00092531 | 0.062913 | -0.011773 | 0.059667 | 0.013277 | 0.008129 | 0.0079267 | -0.0068837 | 0.035775 | 0.0052323 | -122.0679 | -0.18174 | -122.6193 | 0.17117 | -0.095798 | 0.31137 | -122.444 | 0.060571 | 0.03241 | 0.007751 | 0.16234 | 0.28384 | -0.17997 | -0.2191 | 0.25042 | -0.002784 | 0.62647 | 0.075056 | -0.17537 | -0.26975 | 0.13742 | 122.4753 | -0.011608 | 122.755 | 122.7021 | 0.22685 | 0.10989 | -0.35392 | 122.8656 | 122.5986 | 123.0058 | 122.5127 | -122.6179 | 122.8567 | 122.9782 | 122.5144 | 122.7268 | -0.39304
927.8594 | 122.8546 | -122.7081 | 0.21057 | 1.4211e-13 | -0.017055 | -0.0013525 | 0.062699 | -0.011986 | 0.059881 | -0.0096144 | 0.008129 | 0.0079267 | -0.0058155 | 0.035562 | 0.0056597 | -122.0679 | -0.18174 | -122.6239 | 0.17117 | -0.095798 | 0.35258 | -122.4531 | 0.060571 | 0.041567 | 0.007751 | 0.15776 | 0.293 | -0.17081 | -0.22825 | 0.255 | -0.039405 | 0.6402 | 0.084211 | -0.17079 | -0.30637 | 0.14201 | 122.4799 | -0.052807 | 122.7687 | 122.7159 | 0.236 | 0.08243 | -0.38139 | 122.8793 | 122.6123 | 123.0607 | 122.5264 | -122.6637 | 122.8659 | 123.0011 | 122.5373 | 122.7497 | -0.43882
929.6094 | 122.9553 | -122.612 | 0.17395 | 1.4211e-13 | -0.017055 | -0.00092531 | 0.062699 | -0.011773 | 0.059454 | 0.0056466 | 0.0079152 | 0.0081403 | -0.0064565 | 0.035562 | 0.0056597 | -122.0679 | -0.18174 | -122.6193 | 0.17574 | -0.095798 | 0.348 | -122.4486 | 0.055992 | 0.041567 | 0.007751 | 0.15776 | 0.293 | -0.16624 | -0.22367 | 0.16345 | 0.001794 | 0.54407 | -0.007341 | -0.17079 | -0.26975 | 0.17405 | 122.3883 | -0.016186 | 122.668 | 122.6198 | 0.23142 | 0.11905 | -0.34019 | 122.7877 | 122.5162 | 122.96 | 122.4303 | -122.6225 | 122.7698 | 122.905 | 122.4458 | 122.6536 | -0.39762
931.3594 | 122.8546 | -122.7081 | 0.20142 | 1.4211e-13 | -0.017269 | -0.00071151 | 0.062913 | -0.011559 | 0.059454 | 0.020908 | 0.008129 | 0.0081403 | -0.0064565 | 0.035562 | 0.0056597 | -122.0634 | -0.1909 | -122.6239 | 0.1849 | -0.095798 | 0.35716 | -122.4486 | 0.06515 | 0.036989 | 0.016908 | 0.16234 | 0.28384 | -0.17539 | -0.22825 | 0.25958 | -0.016515 | 0.64478 | 0.084211 | -0.17537 | -0.29721 | 0.15574 | 122.4799 | -0.039074 | 122.7733 | 122.725 | 0.24516 | 0.082428 | -0.37681 | 122.893 | 122.6123 | 123.0653 | 122.5172 | -122.65 | 122.8705 | 122.992 | 122.5327 | 122.7451 | -0.42967
933.1094 | 122.8729 | -122.6898 | 0.21515 | 1.4211e-13 | -0.017269 | -0.00092531 | 0.062485 | -0.011986 | 0.059881 | 0.0056466 | 0.008129 | 0.0081403 | -0.0066701 | 0.035775 | 0.0054461 | -122.0679 | -0.18174 | -122.6285 | 0.17574 | -0.09122 | 0.35716 | -122.4486 | 0.060571 | 0.041567 | 0.01233 | 0.16234 | 0.293 | -0.17081 | -0.23741 | 0.24127 | -0.039405 | 0.62189 | 0.061322 | -0.17994 | -0.30637 | 0.14201 | 122.4524 | -0.052807 | 122.7504 | 122.7021 | 0.24974 | 0.077852 | -0.38596 | 122.8656 | 122.5986 | 123.047 | 122.5081 | -122.6637 | 122.8522 | 122.9828 | 122.519 | 122.7314 | -0.45256
934.8438 | 122.8775 | -122.6944 | 0.19226 | 1.4211e-13 | -0.017055 | -0.00092531 | 0.062485 | -0.011559 | 0.059667 | 0.0056466 | 0.0077016 | 0.0081403 | -0.0066701 | 0.035562 | 0.0050187 | -122.0679 | -0.18632 | -122.6193 | 0.18032 | -0.10038 | 0.32969 | -122.4486 | 0.06515 | 0.041567 | 0.003172 | 0.15776 | 0.28384 | -0.16624 | -0.22825 | 0.24584 | -0.011938 | 0.62647 | 0.075056 | -0.17079 | -0.29264 | 0.13743 | 122.4661 | -0.034497 | 122.7595 | 122.6976 | 0.23142 | 0.091583 | -0.3585 | 122.8747 | 122.594 | 123.0241 | 122.5081 | -122.6408 | 122.8522 | 122.9782 | 122.5282 | 122.736 | -0.42051
936.5938 | 122.9736 | -122.644 | 0.15564 | 1.4211e-13 | -0.017269 | -0.00092531 | 0.062485 | -0.011986 | 0.059454 | -0.0019839 | 0.008129 | 0.0081403 | -0.0064565 | 0.035775 | 0.0052323 | -122.0771 | -0.18174 | -122.6193 | 0.17117 | -0.095798 | 0.348 | -122.4486 | 0.060571 | 0.041567 | 0.007751 | 0.15318 | 0.28384 | -0.17081 | -0.23283 | 0.19549 | 0.015526 | 0.56696 | 0.024702 | -0.17079 | -0.25144 | 0.19236 | 122.4112 | -0.002455 | 122.7046 | 122.6518 | 0.24058 | 0.1282 | -0.32645 | 122.8152 | 122.5482 | 122.992 | 122.4623 | -122.6042 | 122.7972 | 122.9279 | 122.4732 | 122.6856 | -0.38847
938.2812 | 122.9507 | -122.6486 | 0.17853 | 1.4211e-13 | -0.017269 | -0.00092531 | 0.062699 | -0.011773 | 0.059667 | -0.0019839 | 0.0079152 | 0.0079267 | -0.0064565 | 0.035775 | 0.0056597 | -122.0679 | -0.18632 | -122.6193 | 0.17574 | -0.086641 | 0.348 | -122.444 | 0.06515 | 0.041567 | 0.003172 | 0.15776 | 0.27926 | -0.16624 | -0.22825 | 0.20465 | -0.002784 | 0.58069 | 0.02928 | -0.17537 | -0.26517 | 0.16948 | 122.4204 | -0.020764 | 122.7138 | 122.6518 | 0.23142 | 0.10074 | -0.34476 | 122.8244 | 122.562 | 122.9966 | 122.4623 | -122.6225 | 122.8064 | 122.9279 | 122.4824 | 122.6902 | -0.40678
940.0312 | 122.8363 | -122.7219 | 0.20599 | 1.4211e-13 | -0.017269 | -0.0011389 | 0.062913 | -0.011773 | 0.059667 | 0.0056466 | 0.0079152 | 0.0087813 | -0.0062429 | 0.035775 | 0.0054461 | -122.0634 | -0.18632 | -122.6239 | 0.18032 | -0.086641 | 0.36174 | -122.4531 | 0.06515 | 0.036989 | 0.007751 | 0.16234 | 0.28384 | -0.17081 | -0.22367 | 0.26873 | -0.025671 | 0.65851 | 0.097944 | -0.17079 | -0.29263 | 0.15574 | 122.4982 | -0.043652 | 122.787 | 122.7296 | 0.23142 | 0.07785 | -0.37681 | 122.9022 | 122.6352 | 123.0836 | 122.5355 | -122.6591 | 122.8842 | 123.0057 | 122.551 | 122.7589 | -0.42967
941.7188 | 122.8775 | -122.6715 | 0.16937 | 1.4211e-13 | -0.017483 | -0.00092531 | 0.062699 | -0.011559 | 0.059454 | 0.013277 | 0.0079152 | 0.0079267 | -0.0062429 | 0.035562 | 0.0052323 | -122.0588 | -0.18632 | -122.6102 | 0.17574 | -0.10038 | 0.31595 | -122.4394 | 0.051413 | 0.03241 | -0.001407 | 0.15776 | 0.28842 | -0.16624 | -0.23741 | 0.23211 | 0.006371 | 0.61274 | 0.061325 | -0.17079 | -0.26975 | 0.14658 | 122.4341 | -0.011609 | 122.7229 | 122.6701 | 0.236 | 0.11905 | -0.33561 | 122.8473 | 122.5711 | 122.9875 | 122.4852 | -122.6088 | 122.8293 | 122.9599 | 122.5053 | 122.7039 | -0.40678
943.4688 | 122.8455 | -122.699 | 0.20599 | 1.4211e-13 | -0.017483 | -0.00092531 | 0.062699 | -0.011986 | 0.059667 | 0.0056466 | 0.0077016 | 0.0081403 | -0.0062429 | 0.035775 | 0.0050187 | -122.0634 | -0.18632 | -122.6102 | 0.18032 | -0.095798 | 0.36174 | -122.4577 | 0.060571 | 0.050725 | 0.007751 | 0.16234 | 0.28384 | -0.17081 | -0.22825 | 0.24126 | -0.025671 | 0.63562 | 0.088791 | -0.15247 | -0.30179 | 0.15574 | 122.4707 | -0.043652 | 122.7595 | 122.7067 | 0.236 | 0.07785 | -0.37681 | 122.8793 | 122.6032 | 123.0607 | 122.5127 | -122.6637 | 122.8613 | 122.9828 | 122.5282 | 122.7497 | -0.43425
945.2031 | 122.8363 | -122.6852 | 0.18768 | 1.4211e-13 | -0.017483 | -0.0011389 | 0.062699 | -0.011773 | 0.059881 | 0.013277 | 0.008129 | 0.0083539 | -0.0064565 | 0.035775 | 0.0052323 | -122.0634 | -0.18632 | -122.6193 | 0.17574 | -0.095798 | 0.35716 | -122.444 | 0.06515 | 0.041567 | 0.007751 | 0.15318 | 0.28384 | -0.16624 | -0.22367 | 0.24127 | -0.011939 | 0.62189 | 0.065901 | -0.17537 | -0.28348 | 0.16948 | 122.4616 | -0.034498 | 122.7504 | 122.693 | 0.23142 | 0.096161 | -0.35392 | 122.861 | 122.5894 | 123.0424 | 122.4989 | -122.6317 | 122.8384 | 122.9691 | 122.519 | 122.7268 | -0.41136
946.9375 | 122.9324 | -122.6578 | 0.16937 | 1.4211e-13 | -0.017483 | -0.0011389 | 0.062272 | -0.011773 | 0.059454 | 0.0056466 | 0.0079152 | 0.0081403 | -0.0060291 | 0.035775 | 0.0052323 | -122.0634 | -0.1909 | -122.6193 | 0.18032 | -0.095798 | 0.35716 | -122.444 | 0.060571 | 0.041567 | 0.007751 | 0.16234 | 0.28384 | -0.16624 | -0.22825 | 0.2138 | 0.01095 | 0.59443 | 0.038435 | -0.17537 | -0.26517 | 0.18779 | 122.4295 | -0.007031 | 122.7183 | 122.6655 | 0.236 | 0.11447 | -0.33561 | 122.8381 | 122.562 | 123.0149 | 122.4669 | -122.6133 | 122.8201 | 122.9416 | 122.4915 | 122.6993 | -0.39763
948.625 | 122.9691 | -122.6669 | 0.14648 | 1.4211e-13 | -0.017269 | -0.00092531 | 0.062485 | -0.011773 | 0.059881 | 0.013277 | 0.008129 | 0.0079267 | -0.0062429 | 0.035562 | 0.0054461 | -122.0496 | -0.1909 | -122.6102 | 0.17574 | -0.095798 | 0.3709 | -122.4486 | 0.06515 | 0.036989 | 0.01233 | 0.15318 | 0.28842 | -0.16624 | -0.22825 | 0.21838 | 0.02926 | 0.61732 | 0.056747 | -0.16163 | -0.24228 | 0.22441 | 122.4387 | 0.006701 | 122.7321 | 122.6793 | 0.24058 | 0.14194 | -0.31272 | 122.8427 | 122.5711 | 123.0378 | 122.476 | -122.595 | 122.8201 | 122.9554 | 122.5007 | 122.7039 | -0.37474
950.3125 | 122.8912 | -122.6669 | 0.17853 | 1.4211e-13 | -0.017269 | -0.00049791 | 0.062699 | -0.011773 | 0.059881 | -0.0019839 | 0.008129 | 0.0083539 | -0.0060291 | 0.035775 | 0.0052323 | -122.0588 | -0.18174 | -122.6056 | 0.17574 | -0.095798 | 0.34342 | -122.4486 | 0.06515 | 0.036989 | 0.007751 | 0.16692 | 0.28842 | -0.17081 | -0.23283 | 0.21838 | -0.002784 | 0.60816 | 0.061325 | -0.15705 | -0.27433 | 0.1649 | 122.4341 | -0.011607 | 122.7321 | 122.6747 | 0.24058 | 0.10989 | -0.34934 | 122.8427 | 122.5711 | 123.0104 | 122.4852 | -122.6271 | 122.8339 | 122.9554 | 122.4961 | 122.7039 | -0.41136
952.0625 | 122.8592 | -122.6852 | 0.16937 | 1.4211e-13 | -0.017696 | -0.00071151 | 0.062699 | -0.011559 | 0.059667 | 0.013277 | 0.0079152 | 0.0083539 | -0.0064565 | 0.035989 | 0.0050187 | -122.0634 | -0.1909 | -122.6148 | 0.1849 | -0.09122 | 0.35258 | -122.444 | 0.06515 | 0.046146 | -0.001407 | 0.16692 | 0.28384 | -0.17539 | -0.23283 | 0.24127 | 0.015528 | 0.62189 | 0.07048 | -0.17079 | -0.26059 | 0.18321 | 122.4524 | -0.002452 | 122.7504 | 122.6838 | 0.23142 | 0.11447 | -0.34477 | 122.8701 | 122.594 | 123.0378 | 122.4943 | -122.6133 | 122.8522 | 122.9691 | 122.5098 | 122.7314 | -0.4022
953.75 | 122.905 | -122.6715 | 0.1831 | 1.4211e-13 | -0.017696 | -0.00092531 | 0.062699 | -0.011773 | 0.059667 | 0.0056466 | 0.008129 | 0.0081403 | -0.0064565 | 0.035775 | 0.0052323 | -122.0634 | -0.1909 | -122.6193 | 0.17117 | -0.09122 | 0.348 | -122.444 | 0.06515 | 0.041567 | 0.007751 | 0.16234 | 0.28842 | -0.16624 | -0.23283 | 0.22754 | -0.011939 | 0.60816 | 0.052168 | -0.17537 | -0.27432 | 0.1649 | 122.4387 | -0.020763 | 122.7367 | 122.6793 | 0.24058 | 0.10532 | -0.34934 | 122.8427 | 122.5803 | 123.0195 | 122.4806 | -122.6271 | 122.8339 | 122.9599 | 122.5053 | 122.7131 | -0.41594
955.5 | 122.85 | -122.6532 | 0.19226 | 1.4211e-13 | -0.017483 | -0.00092531 | 0.062699 | -0.011773 | 0.059454 | 0.0056466 | 0.0083426 | 0.0079267 | -0.0066701 | 0.035562 | 0.0050187 | -122.0588 | -0.20005 | -122.6102 | 0.17574 | -0.09122 | 0.36174 | -122.4302 | 0.060571 | 0.036989 | -0.001407 | 0.15776 | 0.28842 | -0.16624 | -0.23741 | 0.22296 | -0.016517 | 0.59443 | 0.043014 | -0.17995 | -0.28348 | 0.16948 | 122.4158 | -0.034497 | 122.7138 | 122.6518 | 0.236 | 0.096162 | -0.3585 | 122.8289 | 122.562 | 123.0149 | 122.4531 | -122.6225 | 122.811 | 122.9416 | 122.487 | 122.6902 | -0.42967
957.1875 | 122.9553 | -122.6669 | 0.17395 | 1.4211e-13 | -0.017269 | -0.00071151 | 0.062485 | -0.0122 | 0.059667 | 0.0056466 | 0.0079152 | 0.0081403 | -0.0064565 | 0.035562 | 0.0052323 | -122.0588 | -0.19547 | -122.6102 | 0.18032 | -0.086641 | 0.33427 | -122.4394 | 0.060571 | 0.041567 | 0.007751 | 0.15318 | 0.27926 | -0.17081 | -0.2191 | 0.22754 | 0.006373 | 0.60816 | 0.056747 | -0.17079 | -0.26059 | 0.16032 | 122.4478 | -0.020765 | 122.7275 | 122.6747 | 0.22685 | 0.10531 | -0.34476 | 122.8473 | 122.5803 | 123.0012 | 122.4715 | -122.6133 | 122.8201 | 122.9462 | 122.4961 | 122.7085 | -0.39304
958.9375 | 122.905 | -122.6807 | 0.1831 | 1.4211e-13 | -0.01791 | -0.0011389 | 0.062699 | -0.011773 | 0.060095 | 0.0056466 | 0.0083426 | 0.0081403 | -0.0064565 | 0.036203 | 0.0052323 | -122.0634 | -0.20005 | -122.6056 | 0.17574 | -0.09122 | 0.32969 | -122.4394 | 0.060571 | 0.036989 | 0.007751 | 0.15776 | 0.28842 | -0.17539 | -0.23283 | 0.24127 | -0.007361 | 0.61731 | 0.075058 | -0.16621 | -0.27432 | 0.14658 | 122.4478 | -0.025341 | 122.7412 | 122.6884 | 0.24058 | 0.10532 | -0.3585 | 122.8564 | 122.5894 | 123.0104 | 122.4806 | -122.6225 | 122.8384 | 122.9691 | 122.5053 | 122.7177 | -0.41594
960.6719 | 122.8317 | -122.7127 | 0.20599 | 1.4211e-13 | -0.017696 | -0.00092531 | 0.062699 | -0.011559 | 0.059881 | -0.0019839 | 0.0079152 | 0.0077131 | -0.0064565 | 0.035989 | 0.0048051 | -122.0634 | -0.1909 | -122.6056 | 0.17117 | -0.10038 | 0.36174 | -122.444 | 0.069728 | 0.041567 | 0.007751 | 0.14861 | 0.28384 | -0.16166 | -0.23283 | 0.26873 | -0.034828 | 0.64936 | 0.1071 | -0.16163 | -0.30637 | 0.15574 | 122.4799 | -0.057387 | 122.7824 | 122.7205 | 0.24058 | 0.07785 | -0.36765 | 122.8839 | 122.6123 | 123.0744 | 122.5218 | -122.65 | 122.8613 | 122.9966 | 122.5511 | 122.7543 | -0.43883
962.4062 | 122.8867 | -122.6624 | 0.19226 | 1.4211e-13 | -0.017696 | -0.00092531 | 0.062913 | -0.011773 | 0.059454 | -0.0019839 | 0.0077016 | 0.0079267 | -0.0066701 | 0.036203 | 0.0052323 | -122.0588 | -0.19547 | -122.6056 | 0.17117 | -0.09122 | 0.32511 | -122.4348 | 0.060571 | 0.036989 | 0.007751 | 0.16234 | 0.28384 | -0.16624 | -0.22825 | 0.22754 | -0.021095 | 0.60358 | 0.056748 | -0.17079 | -0.28348 | 0.13285 | 122.4341 | -0.029919 | 122.7229 | 122.6701 | 0.236 | 0.091583 | -0.3585 | 122.8335 | 122.5711 | 122.9875 | 122.4669 | -122.6271 | 122.8247 | 122.9462 | 122.4961 | 122.6993 | -0.42051
964.0938 | 122.8317 | -122.731 | 0.20599 | 1.4211e-13 | -0.017269 | -0.00071151 | 0.062699 | -0.011986 | 0.05924 | -0.0019839 | 0.0083426 | 0.0077131 | -0.0060291 | 0.035775 | 0.0052323 | -122.0588 | -0.20005 | -122.6056 | 0.18032 | -0.086641 | 0.35716 | -122.4348 | 0.060571 | 0.041567 | 0.003172 | 0.15318 | 0.28384 | -0.17997 | -0.22825 | 0.2962 | -0.025671 | 0.67225 | 0.12541 | -0.17079 | -0.29263 | 0.15117 | 122.5028 | -0.052809 | 122.7916 | 122.7342 | 0.23142 | 0.07785 | -0.38597 | 122.9113 | 122.6444 | 123.0882 | 122.531 | -122.6408 | 122.8842 | 123.0149 | 122.551 | 122.7726 | -0.43425
965.8281 | 122.8867 | -122.6761 | 0.19684 | 1.4211e-13 | -0.017483 | -0.0013525 | 0.062699 | -0.011986 | 0.059881 | 0.0056466 | 0.008129 | 0.0083539 | -0.0062429 | 0.035775 | 0.0050187 | -122.0588 | -0.19547 | -122.601 | 0.17574 | -0.10038 | 0.36174 | -122.4302 | 0.060571 | 0.046146 | 0.003172 | 0.15776 | 0.28384 | -0.17081 | -0.23283 | 0.24585 | -0.021094 | 0.61731 | 0.075059 | -0.17079 | -0.29722 | 0.1649 | 122.4433 | -0.039074 | 122.7367 | 122.6793 | 0.236 | 0.087006 | -0.36765 | 122.8518 | 122.5757 | 123.0378 | 122.4806 | -122.6271 | 122.8338 | 122.9599 | 122.5053 | 122.7222 | -0.42967
967.5781 | 122.9507 | -122.644 | 0.16022 | 1.4211e-13 | -0.017696 | -0.00049791 | 0.062913 | -0.011773 | 0.059667 | 0.0056466 | 0.008129 | 0.0081403 | -0.0066701 | 0.035775 | 0.0050187 | -122.0542 | -0.20005 | -122.6102 | 0.18032 | -0.095798 | 0.348 | -122.4348 | 0.06515 | 0.03241 | 0.003172 | 0.15318 | 0.28842 | -0.17539 | -0.22367 | 0.20923 | 0.020106 | 0.58985 | 0.033859 | -0.17537 | -0.25601 | 0.18779 | 122.4204 | -0.007032 | 122.7092 | 122.6472 | 0.22685 | 0.12821 | -0.33561 | 122.8244 | 122.5482 | 122.992 | 122.444 | -122.595 | 122.7972 | 122.9325 | 122.4686 | 122.6765 | -0.38389
969.2656 | 122.9965 | -122.644 | 0.15564 | 1.4211e-13 | -0.017696 | -0.00071151 | 0.062699 | -0.011559 | 0.059667 | 0.013277 | 0.0077016 | 0.0083539 | -0.0060291 | 0.036203 | 0.0052323 | -122.0588 | -0.1909 | -122.6102 | 0.18032 | -0.086641 | 0.36174 | -122.4394 | 0.06515 | 0.046146 | 0.007751 | 0.16234 | 0.27469 | -0.17081 | -0.22367 | 0.20465 | 0.024683 | 0.58527 | 0.033859 | -0.17079 | -0.24228 | 0.2061 | 122.4204 | 0.006702 | 122.7092 | 122.6518 | 0.23142 | 0.11905 | -0.32645 | 122.8244 | 122.5574 | 123.0058 | 122.4531 | -122.595 | 122.8064 | 122.9187 | 122.4732 | 122.6902 | -0.37931
971 | 122.8867 | -122.6852 | 0.19226 | 1.4211e-13 | -0.017696 | -0.00092531 | 0.062485 | -0.011986 | 0.059667 | 0.0056466 | 0.008129 | 0.0081403 | -0.0062429 | 0.036203 | 0.0048051 | -122.0588 | -0.20005 | -122.601 | 0.18032 | -0.095798 | 0.36174 | -122.4302 | 0.06515 | 0.036989 | 0.003172 | 0.15318 | 0.28384 | -0.17081 | -0.23283 | 0.255 | -0.011938 | 0.62647 | 0.084215 | -0.17079 | -0.28806 | 0.16948 | 122.4524 | -0.039076 | 122.7504 | 122.6884 | 0.236 | 0.091583 | -0.36308 | 122.8656 | 122.5894 | 123.047 | 122.4852 | -122.6225 | 122.8384 | 122.9691 | 122.5144 | 122.7222 | -0.42509
972.75 | 122.8638 | -122.699 | 0.20142 | 1.4211e-13 | -0.017696 | -0.00092531 | 0.062699 | -0.011345 | 0.060095 | 0.0056466 | 0.008129 | 0.0079267 | -0.0064565 | 0.036203 | 0.0048051 | -122.0542 | -0.1909 | -122.6056 | 0.18032 | -0.095798 | 0.36632 | -122.4348 | 0.06515 | 0.041567 | 0.007751 | 0.15776 | 0.27926 | -0.17081 | -0.22825 | 0.26416 | -0.021093 | 0.64478 | 0.093369 | -0.17079 | -0.29721 | 0.1649 | 122.4707 | -0.043652 | 122.7641 | 122.7067 | 0.236 | 0.077849 | -0.37223 | 122.8793 | 122.6032 | 123.0653 | 122.5081 | -122.6362 | 122.8567 | 122.9782 | 122.5282 | 122.7405 | -0.42967
974.5156 | 122.937 | -122.6486 | 0.1831 | 1.4211e-13 | -0.017696 | -0.00092531 | 0.062272 | -0.011773 | 0.060095 | 0.013277 | 0.008129 | 0.0083539 | -0.0064565 | 0.035989 | 0.0050187 | -122.0634 | -0.20005 | -122.6056 | 0.18032 | -0.095798 | 0.36174 | -122.4302 | 0.06515 | 0.036989 | 0.003172 | 0.15318 | 0.28384 | -0.17081 | -0.22825 | 0.21838 | -0.002782 | 0.58527 | 0.043015 | -0.17537 | -0.2789 | 0.17863 | 122.4204 | -0.02992 | 122.7138 | 122.6518 | 0.23142 | 0.10074 | -0.35392 | 122.8289 | 122.5528 | 123.0104 | 122.4486 | -122.6133 | 122.8018 | 122.9325 | 122.4778 | 122.6856 | -0.41136
976.2031 | 122.937 | -122.6624 | 0.14191 | 1.4211e-13 | -0.01791 | -0.00049791 | 0.062272 | -0.011773 | 0.059667 | 0.0056466 | 0.0079152 | 0.0079267 | -0.0062429 | 0.036416 | 0.0052323 | -122.0588 | -0.19547 | -122.601 | 0.17117 | -0.09122 | 0.36174 | -122.4348 | 0.06515 | 0.03241 | 0.007751 | 0.15318 | 0.28384 | -0.17539 | -0.22825 | 0.22754 | 0.029259 | 0.60358 | 0.061327 | -0.16621 | -0.23313 | 0.21983 | 122.4341 | 0.011278 | 122.7275 | 122.6701 | 0.236 | 0.14194 | -0.3173 | 122.8335 | 122.5711 | 123.0241 | 122.4669 | -122.5767 | 122.8155 | 122.9462 | 122.487 | 122.6948 | -0.37016
977.9531 | 122.9416 | -122.6074 | 0.16479 | 1.4211e-13 | -0.017696 | -0.0011389 | 0.062485 | -0.011773 | 0.059454 | -0.0019839 | 0.0079152 | 0.0079267 | -0.0064565 | 0.036203 | 0.0054461 | -122.0634 | -0.20005 | -122.6056 | 0.18032 | -0.09122 | 0.36174 | -122.4257 | 0.060571 | 0.036989 | -0.001407 | 0.15776 | 0.27926 | -0.16624 | -0.22825 | 0.18176 | 0.015528 | 0.54407 | 0.001816 | -0.17995 | -0.25601 | 0.19694 | 122.3792 | -0.007031 | 122.668 | 122.606 | 0.22685 | 0.11447 | -0.33103 | 122.7877 | 122.5162 | 122.9692 | 122.4074 | -122.5905 | 122.7652 | 122.8867 | 122.4412 | 122.6444 | -0.39305
979.7188 | 122.9187 | -122.6578 | 0.16937 | 1.4211e-13 | -0.017696 | -0.00071151 | 0.062913 | -0.011986 | 0.059881 | -0.0019839 | 0.008129 | 0.0081403 | -0.0060291 | 0.036203 | 0.0052323 | -122.0634 | -0.20005 | -122.601 | 0.17574 | -0.095798 | 0.32511 | -122.4302 | 0.055992 | 0.03241 | 0.01233 | 0.16234 | 0.27926 | -0.16624 | -0.22825 | 0.22754 | 0.006371 | 0.59443 | 0.056749 | -0.17079 | -0.26517 | 0.15574 | 122.4295 | -0.007031 | 122.7138 | 122.6701 | 0.24058 | 0.10989 | -0.33561 | 122.8335 | 122.562 | 122.9829 | 122.4577 | -122.5996 | 122.8201 | 122.937 | 122.4915 | 122.6902 | -0.39763
981.4062 | 122.8592 | -122.6715 | 0.21057 | 1.4211e-13 | -0.01791 | -0.0011389 | 0.062699 | -0.011773 | 0.060095 | 0.0056466 | 0.0083426 | 0.0083539 | -0.0064565 | 0.036203 | 0.0048051 | -122.0588 | -0.20005 | -122.5964 | 0.18032 | -0.09122 | 0.32511 | -122.4348 | 0.06515 | 0.036989 | 0.003172 | 0.14861 | 0.28842 | -0.16624 | -0.22367 | 0.23669 | -0.030248 | 0.61274 | 0.07506 | -0.16163 | -0.30179 | 0.11454 | 122.4478 | -0.061964 | 122.7367 | 122.6747 | 0.22685 | 0.077852 | -0.37681 | 122.8518 | 122.5803 | 122.9966 | 122.4715 | -122.6454 | 122.8201 | 122.9599 | 122.5053 | 122.7085 | -0.43424
983.0781 | 122.9553 | -122.6257 | 0.14648 | 1.4211e-13 | -0.01791 | -0.0011389 | 0.062699 | -0.011559 | 0.059881 | 0.013277 | 0.0079152 | 0.0081403 | -0.0066701 | 0.035989 | 0.0052323 | -122.0542 | -0.20463 | -122.6056 | 0.17574 | -0.095798 | 0.348 | -122.4257 | 0.060571 | 0.03241 | 0.003172 | 0.16234 | 0.28384 | -0.17081 | -0.22367 | 0.20007 | 0.02926 | 0.57154 | 0.020126 | -0.17995 | -0.24228 | 0.20152 | 122.4021 | 0.015858 | 122.6863 | 122.6289 | 0.22685 | 0.13736 | -0.3173 | 122.8015 | 122.5299 | 122.9737 | 122.4211 | -122.5721 | 122.7881 | 122.9096 | 122.4549 | 122.6581 | -0.37016
984.8281 | 122.9004 | -122.6578 | 0.17853 | 1.4211e-13 | -0.018337 | -0.0011389 | 0.062913 | -0.011986 | 0.059881 | 0.013277 | 0.008129 | 0.0083539 | -0.0062429 | 0.036203 | 0.0048051 | -122.0588 | -0.20005 | -122.5964 | 0.18032 | -0.095798 | 0.36632 | -122.4348 | 0.06515 | 0.036989 | -0.001407 | 0.16234 | 0.28384 | -0.17539 | -0.23283 | 0.22296 | 0.001795 | 0.599 | 0.061327 | -0.16163 | -0.27433 | 0.18779 | 122.4249 | -0.016186 | 122.7229 | 122.6564 | 0.23142 | 0.10532 | -0.35392 | 122.8381 | 122.562 | 123.0241 | 122.4577 | -122.6133 | 122.8201 | 122.9416 | 122.4824 | 122.6948 | -0.41136
986.5781 | 122.9462 | -122.6578 | 0.15564 | 1.4211e-13 | -0.018124 | -0.00092531 | 0.062913 | -0.011986 | 0.059667 | 0.0056466 | 0.0083426 | 0.0081403 | -0.0068837 | 0.036203 | 0.0048051 | -122.0542 | -0.19547 | -122.5873 | 0.17574 | -0.082062 | 0.35258 | -122.4394 | 0.06515 | 0.046146 | 0.003172 | 0.16234 | 0.27926 | -0.16624 | -0.23741 | 0.21838 | 0.020104 | 0.60358 | 0.070483 | -0.1479 | -0.2377 | 0.19694 | 122.4204 | 0.006702 | 122.7229 | 122.6609 | 0.24058 | 0.12362 | -0.32188 | 122.8335 | 122.5757 | 123.0104 | 122.4623 | -122.595 | 122.8201 | 122.937 | 122.4915 | 122.7039 | -0.39305
988.2969 | 122.8226 | -122.6898 | 0.18768 | 1.4211e-13 | -0.01791 | -0.00092531 | 0.062485 | -0.011986 | 0.059454 | -0.0096144 | 0.0077016 | 0.0081403 | -0.0062429 | 0.036203 | 0.0048051 | -122.0542 | -0.20005 | -122.5919 | 0.17117 | -0.095798 | 0.32969 | -122.4302 | 0.060571 | 0.03241 | 0.007751 | 0.15776 | 0.27926 | -0.17081 | -0.22825 | 0.25958 | -0.016517 | 0.63563 | 0.097948 | -0.16163 | -0.28348 | 0.14201 | 122.4616 | -0.029919 | 122.7504 | 122.6976 | 0.236 | 0.091582 | -0.3585 | 122.861 | 122.594 | 123.0195 | 122.4898 | -122.6179 | 122.8476 | 122.9691 | 122.519 | 122.7222 | -0.41593
990.0156 | 122.8592 | -122.6624 | 0.17853 | 1.4211e-13 | -0.01791 | -0.00092531 | 0.062485 | -0.011986 | 0.059667 | 0.0056466 | 0.0077016 | 0.0079267 | -0.0064565 | 0.036416 | 0.0052323 | -122.0496 | -0.20921 | -122.5919 | 0.17574 | -0.10038 | 0.36632 | -122.4302 | 0.055992 | 0.036989 | 0.007751 | 0.15776 | 0.28384 | -0.17081 | -0.22825 | 0.23212 | -0.002784 | 0.61274 | 0.070483 | -0.16163 | -0.2789 | 0.18779 | 122.4341 | -0.020764 | 122.7183 | 122.6701 | 0.236 | 0.10532 | -0.34934 | 122.8381 | 122.562 | 123.0287 | 122.4531 | -122.6088 | 122.8201 | 122.9462 | 122.4915 | 122.6993 | -0.40678
991.7812 | 122.9645 | -122.6486 | 0.16022 | 1.4211e-13 | -0.017696 | -0.0013525 | 0.062913 | -0.011773 | 0.060095 | -0.0019839 | 0.008129 | 0.0083539 | -0.0066701 | 0.036416 | 0.0050187 | -122.045 | -0.20921 | -122.601 | 0.18032 | -0.095798 | 0.30222 | -122.4302 | 0.060571 | 0.036989 | 0.003172 | 0.16234 | 0.28842 | -0.17081 | -0.24199 | 0.21838 | 0.020106 | 0.60358 | 0.047594 | -0.17079 | -0.25601 | 0.142 | 122.4066 | 0.002125 | 122.7092 | 122.6518 | 0.24516 | 0.12821 | -0.33103 | 122.8289 | 122.5528 | 122.9508 | 122.4394 | -122.5905 | 122.811 | 122.937 | 122.4778 | 122.6856 | -0.40221
993.4688 | 122.8638 | -122.6761 | 0.18768 | 1.4211e-13 | -0.01791 | -0.0011389 | 0.062699 | -0.011986 | 0.059667 | -0.0019839 | 0.008129 | 0.0079267 | -0.0062429 | 0.036203 | 0.0048051 | -122.0542 | -0.20921 | -122.601 | 0.17574 | -0.09122 | 0.33885 | -122.4348 | 0.069728 | 0.036989 | 0.01233 | 0.15318 | 0.27926 | -0.17081 | -0.23741 | 0.24127 | -0.011939 | 0.62189 | 0.075059 | -0.16621 | -0.2789 | 0.15116 | 122.4387 | -0.034498 | 122.7458 | 122.6884 | 0.24974 | 0.091582 | -0.3585 | 122.8518 | 122.5849 | 123.0149 | 122.4669 | -122.6225 | 122.8293 | 122.9554 | 122.5053 | 122.7131 | -0.42509
995.2188 | 122.9324 | -122.6715 | 0.16937 | 1.4211e-13 | -0.018124 | -0.0011389 | 0.062699 | -0.011773 | 0.059881 | 0.0056466 | 0.008129 | 0.0079267 | -0.0062429 | 0.03663 | 0.0050187 | -122.0496 | -0.20921 | -122.5964 | 0.17117 | -0.086641 | 0.32053 | -122.4257 | 0.06515 | 0.03241 | 0.007751 | 0.15776 | 0.28384 | -0.17081 | -0.22825 | 0.24585 | 0.001793 | 0.62189 | 0.07506 | -0.17079 | -0.25601 | 0.15116 | 122.4433 | -0.011609 | 122.7367 | 122.6793 | 0.236 | 0.11447 | -0.34019 | 122.8427 | 122.5849 | 122.992 | 122.4623 | -122.595 | 122.8293 | 122.9554 | 122.5007 | 122.7039 | -0.39763
996.9688 | 122.9782 | -122.6395 | 0.17395 | 1.4211e-13 | -0.018124 | -0.0013525 | 0.062699 | -0.011773 | 0.059667 | 0.0056466 | 0.0079152 | 0.0077131 | -0.0062429 | 0.036416 | 0.0048051 | -122.0496 | -0.20921 | -122.5964 | 0.17574 | -0.086641 | 0.36174 | -122.4302 | 0.055992 | 0.018674 | 0.003172 | 0.15776 | 0.27926 | -0.17539 | -0.23283 | 0.20923 | 0.001794 | 0.58985 | 0.043016 | -0.16621 | -0.26059 | 0.18779 | 122.4066 | -0.016186 | 122.6955 | 122.6426 | 0.236 | 0.10531 | -0.34934 | 122.8152 | 122.5528 | 123.0012 | 122.4303 | -122.6042 | 122.7972 | 122.9187 | 122.4641 | 122.6581 | -0.40678
998.6562 | 122.9324 | -122.6349 | 0.15106 | 1.4211e-13 | -0.018337 | -0.00071151 | 0.062485 | -0.011773 | 0.060095 | -0.0019839 | 0.0077016 | 0.0083539 | -0.0062429 | 0.03663 | 0.0050187 | -122.0542 | -0.21379 | -122.5964 | 0.17117 | -0.082062 | 0.32969 | -122.4302 | 0.06515 | 0.018674 | 0.007751 | 0.15776 | 0.27926 | -0.17539 | -0.24199 | 0.20465 | 0.020104 | 0.58069 | 0.038439 | -0.16621 | -0.23312 | 0.17863 | 122.3929 | 0.006702 | 122.7 | 122.6426 | 0.24974 | 0.1282 | -0.32645 | 122.8061 | 122.5528 | 122.9646 | 122.4211 | -122.5813 | 122.7927 | 122.9142 | 122.4595 | 122.6536 | -0.39305
1000.4062 | 122.8088 | -122.6807 | 0.20142 | 1.4211e-13 | -0.018124 | -0.00092531 | 0.062699 | -0.011773 | 0.059881 | 0.013277 | 0.008129 | 0.0081403 | -0.0066701 | 0.03663 | 0.0052323 | -122.0496 | -0.20463 | -122.5827 | 0.17117 | -0.095798 | 0.30222 | -122.4211 | 0.055992 | 0.018674 | 0.003172 | 0.15776 | 0.28842 | -0.17539 | -0.23283 | 0.25958 | -0.03025 | 0.63105 | 0.09795 | -0.16163 | -0.29721 | 0.1008 | 122.4478 | -0.043652 | 122.7367 | 122.6838 | 0.236 | 0.087007 | -0.37681 | 122.8518 | 122.5849 | 122.9829 | 122.476 | -122.6225 | 122.8384 | 122.9691 | 122.5053 | 122.6993 | -0.43425
1002.1562 | 122.9462 | -122.6257 | 0.15564 | 1.4211e-13 | -0.018124 | -0.0011389 | 0.062699 | -0.011773 | 0.059881 | 0.0056466 | 0.0077016 | 0.0079267 | -0.0062429 | 0.03663 | 0.0050187 | -122.0496 | -0.20921 | -122.5827 | 0.17117 | -0.09122 | 0.34342 | -122.4257 | 0.060571 | 0.023253 | 0.003172 | 0.16234 | 0.28842 | -0.17081 | -0.22825 | 0.20007 | 0.015526 | 0.57612 | 0.043018 | -0.15706 | -0.24686 | 0.18778 | 122.3975 | 0.006702 | 122.6863 | 122.6289 | 0.23142 | 0.13278 | -0.32645 | 122.7969 | 122.5345 | 122.9692 | 122.4165 | -122.5813 | 122.7881 | 122.9142 | 122.4549 | 122.649 | -0.38389
1003.8438 | 122.8867 | -122.6578 | 0.16937 | 1.4211e-13 | -0.018337 | -0.00092531 | 0.062485 | -0.011986 | 0.059667 | -0.0096144 | 0.0079152 | 0.0081403 | -0.0064565 | 0.036416 | 0.0048051 | -122.0496 | -0.20921 | -122.5919 | 0.17117 | -0.086641 | 0.33427 | -122.4211 | 0.055992 | 0.027831 | 0.01233 | 0.16234 | 0.27926 | -0.16624 | -0.23283 | 0.2367 | 0.001793 | 0.60816 | 0.065905 | -0.17079 | -0.25601 | 0.16489 | 122.4249 | -0.007031 | 122.7138 | 122.6701 | 0.24516 | 0.10989 | -0.33561 | 122.8289 | 122.5711 | 122.992 | 122.4486 | -122.5905 | 122.8201 | 122.937 | 122.4915 | 122.6856 | -0.4022
1005.5781 | 122.9141 | -122.644 | 0.15564 | 1.4211e-13 | -0.018337 | -0.00092531 | 0.062699 | -0.0122 | 0.060095 | -0.017245 | 0.008129 | 0.0081403 | -0.0064565 | 0.036416 | 0.0050187 | -122.0542 | -0.21379 | -122.5964 | 0.18032 | -0.09122 | 0.32969 | -122.4257 | 0.060571 | 0.027831 | 0.007751 | 0.16692 | 0.28842 | -0.17081 | -0.22825 | 0.21838 | 0.024683 | 0.58985 | 0.047594 | -0.17079 | -0.24686 | 0.17405 | 122.4158 | 0.011281 | 122.7046 | 122.6518 | 0.236 | 0.13278 | -0.32645 | 122.8244 | 122.5528 | 122.9737 | 122.4303 | -122.5813 | 122.811 | 122.9325 | 122.4732 | 122.6719 | -0.38389
1007.2656 | 122.9507 | -122.6303 | 0.16022 | 1.4211e-13 | -0.018551 | -0.00049791 | 0.062699 | -0.011986 | 0.059667 | 0.013277 | 0.0079152 | 0.0077131 | -0.0064565 | 0.036844 | 0.0043777 | -122.0496 | -0.21837 | -122.5919 | 0.18032 | -0.09122 | 0.33427 | -122.4257 | 0.06515 | 0.023253 | 0.003172 | 0.16692 | 0.28384 | -0.17539 | -0.22825 | 0.20465 | 0.020106 | 0.58069 | 0.038439 | -0.16621 | -0.25144 | 0.17405 | 122.4021 | 0.006704 | 122.6955 | 122.6335 | 0.23142 | 0.12363 | -0.33561 | 122.8106 | 122.5391 | 122.9646 | 122.4119 | -122.5859 | 122.7972 | 122.9142 | 122.4549 | 122.6536 | -0.38847
1009.0156 | 122.9416 | -122.6257 | 0.16022 | 1.4211e-13 | -0.018551 | -0.00092531 | 0.062699 | -0.011773 | 0.060095 | -0.0019839 | 0.008129 | 0.0081403 | -0.0062429 | 0.03663 | 0.0050187 | -122.0496 | -0.21379 | -122.5873 | 0.18032 | -0.09122 | 0.35258 | -122.4257 | 0.06515 | 0.023253 | 0.007751 | 0.15776 | 0.28384 | -0.17081 | -0.22825 | 0.20007 | 0.020106 | 0.57612 | 0.038439 | -0.16164 | -0.25144 | 0.19237 | 122.3975 | -0.002453 | 122.6909 | 122.6335 | 0.236 | 0.12363 | -0.33103 | 122.8061 | 122.5345 | 122.9783 | 122.4119 | -122.5859 | 122.7835 | 122.9096 | 122.4549 | 122.649 | -0.38847
1010.6875 | 122.8363 | -122.6761 | 0.19684 | 1.4211e-13 | -0.01791 | -0.0011389 | 0.062913 | -0.011773 | 0.059881 | 0.0056466 | 0.008129 | 0.0079267 | -0.0064565 | 0.036203 | 0.0052323 | -122.0496 | -0.21379 | -122.5964 | 0.17574 | -0.095798 | 0.36174 | -122.4211 | 0.060571 | 0.027831 | 0.007751 | 0.15776 | 0.28842 | -0.16624 | -0.23283 | 0.25501 | -0.021094 | 0.62647 | 0.079637 | -0.17537 | -0.29264 | 0.1649 | 122.4433 | -0.039074 | 122.7367 | 122.6838 | 0.24058 | 0.091585 | -0.36307 | 122.8518 | 122.5803 | 123.0378 | 122.4623 | -122.6179 | 122.8338 | 122.9645 | 122.5099 | 122.7039 | -0.42967
1012.4375 | 122.8363 | -122.6486 | 0.19684 | 1.4211e-13 | -0.018551 | -0.00092531 | 0.062699 | -0.011559 | 0.059667 | 0.013277 | 0.0079152 | 0.0079267 | -0.0062429 | 0.036416 | 0.0052323 | -122.045 | -0.21837 | -122.5873 | 0.17574 | -0.095798 | 0.35716 | -122.4211 | 0.069728 | 0.027831 | 0.003172 | 0.1715 | 0.28842 | -0.16624 | -0.23741 | 0.22754 | -0.021094 | 0.60358 | 0.061328 | -0.16621 | -0.29264 | 0.16032 | 122.4112 | -0.025339 | 122.7183 | 122.6518 | 0.24058 | 0.091585 | -0.36307 | 122.8244 | 122.5528 | 123.0058 | 122.4303 | -122.6179 | 122.8201 | 122.937 | 122.4824 | 122.6765 | -0.43425
1014.2031 | 122.8271 | -122.6715 | 0.19684 | 1.4211e-13 | -0.018551 | -0.00092531 | 0.062699 | -0.011986 | 0.060095 | -0.0019839 | 0.0077016 | 0.0081403 | -0.0060291 | 0.036844 | 0.0048051 | -122.0313 | -0.20921 | -122.5919 | 0.17574 | -0.09122 | 0.33885 | -122.4211 | 0.069728 | 0.027831 | 0.003172 | 0.16692 | 0.28842 | -0.17081 | -0.23283 | 0.25043 | -0.021094 | 0.64021 | 0.079638 | -0.17079 | -0.28806 | 0.14201 | 122.4387 | -0.029917 | 122.7412 | 122.6747 | 0.236 | 0.091585 | -0.36765 | 122.8473 | 122.5803 | 123.0104 | 122.4623 | -122.6179 | 122.8384 | 122.9599 | 122.5007 | 122.6993 | -0.42967
1015.9531 | 122.9095 | -122.6532 | 0.17853 | 1.4211e-13 | -0.018551 | -0.0011389 | 0.062699 | -0.011773 | 0.059881 | 0.0056466 | 0.0077016 | 0.0081403 | -0.0062429 | 0.037057 | 0.0050187 | -122.045 | -0.20463 | -122.601 | 0.17574 | -0.09122 | 0.29764 | -122.4211 | 0.06515 | 0.018674 | -0.001407 | 0.16234 | 0.28384 | -0.16624 | -0.23283 | 0.23212 | -0.002784 | 0.60816 | 0.052171 | -0.17995 | -0.26975 | 0.11911 | 122.4204 | -0.016186 | 122.7183 | 122.6518 | 0.23142 | 0.10532 | -0.34476 | 122.8289 | 122.562 | 122.9508 | 122.4486 | -122.5996 | 122.8155 | 122.937 | 122.487 | 122.6719 | -0.41136
1017.625 | 122.85 | -122.6624 | 0.17395 | 1.4211e-13 | -0.018551 | -0.0011389 | 0.062699 | -0.011986 | 0.060095 | 0.0056466 | 0.0079152 | 0.0081403 | -0.0066701 | 0.03663 | 0.0052323 | -122.045 | -0.21379 | -122.5919 | 0.18032 | -0.095798 | 0.36632 | -122.4165 | 0.060571 | 0.023253 | 0.007751 | 0.16234 | 0.28842 | -0.17539 | -0.23283 | 0.24585 | 0.006373 | 0.61732 | 0.070483 | -0.17537 | -0.26975 | 0.19237 | 122.4295 | -0.011608 | 122.7229 | 122.6701 | 0.24058 | 0.11447 | -0.34934 | 122.8427 | 122.5666 | 123.0287 | 122.4486 | -122.5905 | 122.8247 | 122.9508 | 122.487 | 122.6856 | -0.40678
1019.3906 | 122.9095 | -122.612 | 0.16937 | 1.4211e-13 | -0.018765 | -0.0011389 | 0.062913 | -0.011559 | 0.059667 | 0.0056466 | 0.008129 | 0.0079267 | -0.0064565 | 0.03663 | 0.0048051 | -122.0405 | -0.21379 | -122.5919 | 0.17574 | -0.082062 | 0.3709 | -122.4165 | 0.060571 | 0.018674 | -0.001407 | 0.15776 | 0.28384 | -0.17539 | -0.23283 | 0.1955 | 0.006371 | 0.57154 | 0.020129 | -0.17537 | -0.25143 | 0.20152 | 122.3792 | -0.011609 | 122.6726 | 122.6106 | 0.23142 | 0.11447 | -0.34477 | 122.7877 | 122.5299 | 122.9829 | 122.3982 | -122.5859 | 122.7698 | 122.8958 | 122.4366 | 122.6307 | -0.4022
1021.0781 | 122.8683 | -122.6715 | 0.19684 | 1.4211e-13 | -0.018337 | -0.00071151 | 0.062699 | -0.011986 | 0.059881 | 0.013277 | 0.0079152 | 0.0081403 | -0.0062429 | 0.036844 | 0.0048051 | -122.045 | -0.22752 | -122.5919 | 0.16659 | -0.095798 | 0.36632 | -122.4211 | 0.06515 | 0.023253 | 0.003172 | 0.16234 | 0.28384 | -0.17081 | -0.23283 | 0.25043 | -0.030251 | 0.62647 | 0.079638 | -0.17079 | -0.29264 | 0.16948 | 122.4387 | -0.034496 | 122.7367 | 122.6747 | 0.236 | 0.087006 | -0.36765 | 122.8381 | 122.5757 | 123.0378 | 122.444 | -122.6179 | 122.8339 | 122.9554 | 122.5007 | 122.6948 | -0.42967
1022.8125 | 122.8867 | -122.644 | 0.17395 | 1.4211e-13 | -0.018551 | -0.0011389 | 0.062699 | -0.011773 | 0.059667 | 0.013277 | 0.008129 | 0.0081403 | -0.0066701 | 0.03663 | 0.0045915 | -122.045 | -0.22295 | -122.5919 | 0.18032 | -0.09122 | 0.35716 | -122.4165 | 0.060571 | 0.023253 | 0.003172 | 0.15776 | 0.28384 | -0.17081 | -0.22825 | 0.22754 | 0.006373 | 0.599 | 0.052172 | -0.17537 | -0.26517 | 0.18321 | 122.4158 | -0.016186 | 122.7046 | 122.6472 | 0.23142 | 0.10989 | -0.34476 | 122.8244 | 122.5528 | 123.0012 | 122.4211 | -122.5905 | 122.8018 | 122.9279 | 122.4732 | 122.6673 | -0.4022
1024.5625 | 122.8043 | -122.6761 | 0.1831 | 1.4211e-13 | -0.018124 | -0.00092531 | 0.062699 | -0.011773 | 0.059881 | -0.0096144 | 0.008129 | 0.0081403 | -0.0064565 | 0.037057 | 0.0050187 | -122.0405 | -0.21837 | -122.5919 | 0.18032 | -0.086641 | 0.36632 | -122.4119 | 0.060571 | 0.018674 | 0.003172 | 0.16234 | 0.28384 | -0.17081 | -0.23741 | 0.26416 | -0.002782 | 0.63563 | 0.084215 | -0.17995 | -0.26975 | 0.18321 | 122.4387 | -0.020763 | 122.7367 | 122.6793 | 0.24058 | 0.10074 | -0.35392 | 122.8564 | 122.5894 | 123.0424 | 122.4577 | -122.595 | 122.8384 | 122.9599 | 122.5053 | 122.6948 | -0.42051
1026.3125 | 122.9462 | -122.6028 | 0.17395 | 1.4211e-13 | -0.018551 | -0.0011389 | 0.062699 | -0.011986 | 0.060095 | -0.0096144 | 0.0079152 | 0.0083539 | -0.0062429 | 0.03663 | 0.0050187 | -122.0405 | -0.21837 | -122.5827 | 0.17117 | -0.09122 | 0.36174 | -122.4119 | 0.06515 | 0.023253 | 0.007751 | 0.15318 | 0.28384 | -0.17081 | -0.23283 | 0.19092 | -0.002784 | 0.56239 | 0.02013 | -0.17079 | -0.26517 | 0.18779 | 122.37 | -0.020765 | 122.668 | 122.6106 | 0.24058 | 0.10989 | -0.34476 | 122.774 | 122.5116 | 122.9646 | 122.3845 | -122.5859 | 122.756 | 122.8867 | 122.432 | 122.6261 | -0.40678
1028.0625 | 122.8088 | -122.6624 | 0.20142 | 1.4211e-13 | -0.018337 | -0.00092531 | 0.062485 | -0.0122 | 0.060095 | 0.0056466 | 0.0079152 | 0.0079267 | -0.0062429 | 0.036844 | 0.0050187 | -122.0313 | -0.21837 | -122.5919 | 0.17574 | -0.09122 | 0.35258 | -122.4165 | 0.06515 | 0.027831 | 0.003172 | 0.16692 | 0.27926 | -0.16624 | -0.22825 | 0.24585 | -0.025672 | 0.63105 | 0.070483 | -0.17537 | -0.29264 | 0.15117 | 122.4341 | -0.034495 | 122.7275 | 122.6655 | 0.23142 | 0.077849 | -0.36765 | 122.8381 | 122.5711 | 123.0149 | 122.444 | -122.6179 | 122.8293 | 122.9416 | 122.4961 | 122.6902 | -0.42967
1029.75 | 122.9233 | -122.612 | 0.16937 | 1.4211e-13 | -0.018551 | -0.0013525 | 0.062699 | -0.0122 | 0.060095 | -0.0019839 | 0.0079152 | 0.0081403 | -0.0062429 | 0.037057 | 0.0052323 | -122.0359 | -0.2321 | -122.5919 | 0.17117 | -0.09122 | 0.36174 | -122.4165 | 0.06515 | 0.023253 | 0.003172 | 0.15318 | 0.28384 | -0.17081 | -0.24657 | 0.1955 | 0.001793 | 0.57612 | 0.020129 | -0.17537 | -0.26059 | 0.19237 | 122.3654 | -0.016188 | 122.6771 | 122.6152 | 0.24974 | 0.11447 | -0.34019 | 122.7832 | 122.5208 | 122.9737 | 122.3799 | -122.5859 | 122.7652 | 122.8958 | 122.4412 | 122.6353 | -0.41594
1031.5 | 122.9553 | -122.612 | 0.16479 | 1.4211e-13 | -0.018551 | -0.00092531 | 0.063126 | -0.0122 | 0.059881 | 0.0056466 | 0.0083426 | 0.0079267 | -0.0064565 | 0.03663 | 0.0048051 | -122.0359 | -0.22752 | -122.5873 | 0.17574 | -0.095798 | 0.33885 | -122.4119 | 0.069728 | 0.018674 | 0.01233 | 0.16234 | 0.28384 | -0.17081 | -0.23283 | 0.20008 | 0.010949 | 0.57612 | 0.024707 | -0.17537 | -0.26059 | 0.17405 | 122.3792 | -0.002453 | 122.6817 | 122.6243 | 0.24516 | 0.11905 | -0.33561 | 122.7877 | 122.5162 | 122.9508 | 122.3845 | -122.5767 | 122.7743 | 122.8958 | 122.4412 | 122.6307 | -0.39763
1033.1875 | 122.8455 | -122.6578 | 0.16022 | 1.4211e-13 | -0.018551 | -0.00092531 | 0.062913 | -0.011986 | 0.059881 | 0.0056466 | 0.008129 | 0.0079267 | -0.0064565 | 0.037057 | 0.0045915 | -122.0359 | -0.21379 | -122.5919 | 0.17117 | -0.095798 | 0.33885 | -122.4028 | 0.060571 | 0.023253 | 0.007751 | 0.15318 | 0.28842 | -0.17081 | -0.22825 | 0.25501 | 0.010949 | 0.62189 | 0.065905 | -0.18911 | -0.25601 | 0.17863 | 122.4295 | -0.007032 | 122.7183 | 122.6655 | 0.236 | 0.12821 | -0.33103 | 122.8289 | 122.562 | 122.9966 | 122.444 | -122.563 | 122.811 | 122.9462 | 122.487 | 122.681 | -0.38847
1034.9375 | 122.9141 | -122.6303 | 0.14191 | 1.4211e-13 | -0.018337 | -0.00092531 | 0.062913 | -0.011773 | 0.059667 | -0.0019839 | 0.008129 | 0.0081403 | -0.0064565 | 0.036844 | 0.0048051 | -122.0267 | -0.22295 | -122.5827 | 0.1849 | -0.086641 | 0.3709 | -122.4119 | 0.06515 | 0.027831 | 0.007751 | 0.15776 | 0.27926 | -0.16624 | -0.23283 | 0.21839 | 0.042994 | 0.60359 | 0.047596 | -0.17079 | -0.22855 | 0.22899 | 122.3975 | 0.015857 | 122.6955 | 122.6381 | 0.24058 | 0.13736 | -0.30814 | 122.8152 | 122.5437 | 123.0012 | 122.4074 | -122.5538 | 122.7881 | 122.9096 | 122.4641 | 122.6581 | -0.37474
1036.6875 | 122.7997 | -122.6624 | 0.19226 | 1.4211e-13 | -0.018765 | -0.0011389 | 0.062913 | -0.011773 | 0.059667 | -0.0019839 | 0.0079152 | 0.0079267 | -0.0060291 | 0.037271 | 0.0048051 | -122.0405 | -0.21837 | -122.5827 | 0.17574 | -0.086641 | 0.35716 | -122.4028 | 0.06515 | 0.014095 | 0.007751 | 0.16692 | 0.27469 | -0.17081 | -0.23283 | 0.25959 | -0.016517 | 0.62189 | 0.07964 | -0.17995 | -0.2789 | 0.1649 | 122.4295 | -0.02534 | 122.7275 | 122.6701 | 0.24058 | 0.082426 | -0.36308 | 122.8381 | 122.5757 | 123.0195 | 122.444 | -122.595 | 122.8293 | 122.937 | 122.4915 | 122.6764 | -0.42509
1038.4375 | 122.8455 | -122.6486 | 0.16022 | 1.4211e-13 | -0.018765 | -0.00071151 | 0.062699 | -0.0122 | 0.059881 | 0.0056466 | 0.008129 | 0.0083539 | -0.0066701 | 0.037057 | 0.0045915 | -122.0267 | -0.22752 | -122.5781 | 0.18032 | -0.09122 | 0.35258 | -122.4119 | 0.060571 | 0.027831 | 0.003172 | 0.16234 | 0.28384 | -0.17081 | -0.23283 | 0.2367 | 0.020106 | 0.6219 | 0.070485 | -0.16621 | -0.25144 | 0.19237 | 122.4158 | 0.002125 | 122.7092 | 122.6518 | 0.236 | 0.12363 | -0.33103 | 122.8289 | 122.5574 | 123.0012 | 122.4211 | -122.5721 | 122.811 | 122.9325 | 122.4778 | 122.6765 | -0.39305
1040.1875 | 122.937 | -122.6074 | 0.17395 | 1.4211e-13 | -0.018765 | -0.0011389 | 0.062699 | -0.0122 | 0.059667 | 0.013277 | 0.008129 | 0.0083539 | -0.0064565 | 0.036844 | 0.0048051 | -122.0359 | -0.2321 | -122.5919 | 0.18032 | -0.095798 | 0.3709 | -122.4119 | 0.06515 | 0.027831 | 0.003172 | 0.16234 | 0.28384 | -0.17081 | -0.23283 | 0.1955 | 0.006373 | 0.57154 | 0.015551 | -0.17995 | -0.26975 | 0.19695 | 122.3746 | -0.011608 | 122.6726 | 122.6106 | 0.236 | 0.10989 | -0.34476 | 122.7877 | 122.5116 | 122.9783 | 122.3753 | -122.5859 | 122.7698 | 122.8913 | 122.4366 | 122.6353 | -0.40678
1041.9219 | 122.8409 | -122.644 | 0.18768 | 1.4211e-13 | -0.019192 | -0.00092531 | 0.062272 | -0.0122 | 0.059667 | 0.0056466 | 0.008129 | 0.0081403 | -0.0062429 | 0.037057 | 0.0048051 | -122.0221 | -0.2321 | -122.5873 | 0.17574 | -0.086641 | 0.3709 | -122.4119 | 0.06515 | 0.018674 | 0.007751 | 0.16234 | 0.28384 | -0.16624 | -0.23283 | 0.23212 | -0.011939 | 0.6219 | 0.05675 | -0.17537 | -0.27432 | 0.18321 | 122.4112 | -0.025341 | 122.7092 | 122.6518 | 0.24058 | 0.096161 | -0.35392 | 122.8198 | 122.5574 | 123.0149 | 122.4119 | -122.5996 | 122.8064 | 122.9279 | 122.4778 | 122.6627 | -0.42051
1043.6562 | 122.9279 | -122.6395 | 0.15564 | 1.4211e-13 | -0.019192 | -0.0013525 | 0.062699 | -0.011773 | 0.060095 | 0.0056466 | 0.0079152 | 0.0079267 | -0.0066701 | 0.037271 | 0.0048051 | -122.0221 | -0.22752 | -122.5781 | 0.18032 | -0.086641 | 0.3709 | -122.4211 | 0.060571 | 0.03241 | 0.01233 | 0.15776 | 0.28384 | -0.17081 | -0.23283 | 0.21839 | 0.024683 | 0.61732 | 0.061329 | -0.15706 | -0.24228 | 0.21526 | 122.4066 | 0.002124 | 122.7 | 122.6518 | 0.24516 | 0.1282 | -0.32645 | 122.8198 | 122.5528 | 123.0104 | 122.4119 | -122.5767 | 122.7972 | 122.9233 | 122.4686 | 122.6719 | -0.38847
1045.3438 | 122.8683 | -122.6212 | 0.17853 | 1.4211e-13 | -0.018765 | -0.0011389 | 0.063126 | -0.012414 | 0.059881 | 0.0056466 | 0.0079152 | 0.0081403 | -0.0066701 | 0.037057 | 0.0048051 | -122.0359 | -0.23668 | -122.5781 | 0.18032 | -0.09122 | 0.3709 | -122.4119 | 0.06515 | 0.018674 | 0.01233 | 0.15776 | 0.28384 | -0.17539 | -0.24199 | 0.20923 | 0.001795 | 0.58527 | 0.043019 | -0.16621 | -0.26975 | 0.19237 | 122.3792 | -0.020764 | 122.6863 | 122.6335 | 0.25432 | 0.10532 | -0.35392 | 122.8015 | 122.5299 | 122.9921 | 122.3845 | -122.5904 | 122.7789 | 122.905 | 122.4458 | 122.6398 | -0.42052
1047.0938 | 122.818 | -122.6715 | 0.1831 | 1.4211e-13 | -0.018765 | -0.00071151 | 0.063126 | -0.011986 | 0.059667 | 0.013277 | 0.0077016 | 0.0079267 | -0.0064565 | 0.036844 | 0.0052323 | -122.0313 | -0.23668 | -122.5873 | 0.17117 | -0.09122 | 0.36632 | -122.4119 | 0.06515 | 0.027831 | 0.003172 | 0.16234 | 0.29758 | -0.16624 | -0.23741 | 0.25959 | -0.011939 | 0.64021 | 0.084216 | -0.17537 | -0.27432 | 0.18321 | 122.4341 | -0.020763 | 122.7367 | 122.6747 | 0.24058 | 0.11448 | -0.34934 | 122.8427 | 122.5803 | 123.0378 | 122.4348 | -122.595 | 122.8339 | 122.9691 | 122.5053 | 122.6993 | -0.42051
1048.7656 | 122.8088 | -122.6532 | 0.19684 | 1.4211e-13 | -0.018978 | -0.00092531 | 0.062699 | -0.0122 | 0.059454 | 0.0056466 | 0.008129 | 0.0079267 | -0.0064565 | 0.036844 | 0.0050187 | -122.0267 | -0.2321 | -122.5736 | 0.17574 | -0.09122 | 0.38005 | -122.4119 | 0.060571 | 0.023253 | 0.007751 | 0.15776 | 0.28842 | -0.17539 | -0.22825 | 0.24128 | -0.021094 | 0.62647 | 0.07964 | -0.16164 | -0.28806 | 0.18321 | 122.4249 | -0.039074 | 122.7138 | 122.6609 | 0.236 | 0.091585 | -0.37223 | 122.8289 | 122.562 | 123.0333 | 122.4211 | -122.6088 | 122.811 | 122.9416 | 122.4778 | 122.6765 | -0.42509
1050.5156 | 122.8729 | -122.6395 | 0.17395 | 1.4211e-13 | -0.018765 | -0.0011389 | 0.062485 | -0.0122 | 0.059881 | 0.013277 | 0.007488 | 0.0079267 | -0.0062429 | 0.037057 | 0.0050187 | -122.0267 | -0.2321 | -122.5781 | 0.17574 | -0.095798 | 0.36174 | -122.4073 | 0.069728 | 0.027831 | 0.003172 | 0.16234 | 0.28842 | -0.17081 | -0.24657 | 0.23212 | 0.001794 | 0.61274 | 0.061329 | -0.17079 | -0.26975 | 0.18779 | 122.3929 | -0.011608 | 122.7092 | 122.6426 | 0.24974 | 0.11447 | -0.34476 | 122.8152 | 122.5437 | 123.0012 | 122.4074 | -122.5813 | 122.8018 | 122.9279 | 122.4686 | 122.6673 | -0.42052
1052.2656 | 122.8043 | -122.6669 | 0.19226 | 1.4211e-13 | -0.018978 | -0.0011389 | 0.062485 | -0.011986 | 0.059667 | 0.013277 | 0.008129 | 0.0081403 | -0.0064565 | 0.037271 | 0.0050187 | -122.0267 | -0.2321 | -122.569 | 0.18948 | -0.086641 | 0.3709 | -122.4028 | 0.06515 | 0.027831 | -0.001407 | 0.16234 | 0.28384 | -0.17081 | -0.24199 | 0.26417 | -0.002782 | 0.64021 | 0.097952 | -0.16622 | -0.2789 | 0.17864 | 122.4249 | -0.029919 | 122.7321 | 122.6655 | 0.24058 | 0.091583 | -0.36308 | 122.8564 | 122.5803 | 123.0378 | 122.4348 | -122.595 | 122.8293 | 122.9508 | 122.4961 | 122.6948 | -0.43425
1054.0156 | 122.8958 | -122.6028 | 0.16479 | 1.4211e-13 | -0.018337 | -0.00092531 | 0.062699 | -0.0122 | 0.059667 | -0.0019839 | 0.0079152 | 0.0079267 | -0.0064565 | 0.037271 | 0.0050187 | -122.0221 | -0.2321 | -122.5781 | 0.17574 | -0.09122 | 0.348 | -122.4028 | 0.060571 | 0.027831 | -0.001407 | 0.16234 | 0.28384 | -0.16624 | -0.23283 | 0.20008 | 0.010949 | 0.5807 | 0.024708 | -0.17537 | -0.25601 | 0.18321 | 122.37 | -0.002453 | 122.6634 | 122.6014 | 0.23142 | 0.11905 | -0.33103 | 122.7786 | 122.5116 | 122.9508 | 122.3707 | -122.5676 | 122.7652 | 122.8867 | 122.4366 | 122.6307 | -0.39763
1055.7188 | 122.8821 | -122.6212 | 0.16479 | 1.4211e-13 | -0.018978 | -0.00092531 | 0.062913 | -0.0122 | 0.059454 | 0.013277 | 0.008129 | 0.0079267 | -0.0066701 | 0.037057 | 0.0048051 | -122.0221 | -0.2321 | -122.5781 | 0.18032 | -0.095798 | 0.36632 | -122.4028 | 0.060571 | 0.027831 | -0.001407 | 0.15776 | 0.28842 | -0.17539 | -0.23741 | 0.21839 | 0.015528 | 0.59901 | 0.043019 | -0.17537 | -0.26059 | 0.20152 | 122.3837 | -0.007031 | 122.6817 | 122.6197 | 0.236 | 0.12363 | -0.34019 | 122.8015 | 122.5254 | 122.9875 | 122.3891 | -122.5676 | 122.7789 | 122.9096 | 122.4458 | 122.649 | -0.40221
1057.4531 | 122.8546 | -122.6395 | 0.15564 | 1.4211e-13 | -0.018551 | -0.00092531 | 0.062913 | -0.011773 | 0.059454 | 0.0056466 | 0.0079152 | 0.0081403 | -0.0066701 | 0.037057 | 0.0048051 | -122.0221 | -0.24126 | -122.5827 | 0.18032 | -0.09122 | 0.3709 | -122.3936 | 0.060571 | 0.027831 | -0.001407 | 0.15776 | 0.28384 | -0.17997 | -0.24199 | 0.24586 | 0.024683 | 0.61732 | 0.056751 | -0.18911 | -0.24686 | 0.21526 | 122.3975 | 0.002124 | 122.7 | 122.6381 | 0.24058 | 0.1282 | -0.33561 | 122.8198 | 122.5482 | 123.0104 | 122.3982 | -122.5492 | 122.7972 | 122.9233 | 122.4595 | 122.6673 | -0.39763
1059.2031 | 122.8455 | -122.612 | 0.17395 | 1.4211e-13 | -0.018765 | -0.0011389 | 0.062485 | -0.011986 | 0.059881 | -0.0019839 | 0.0079152 | 0.0083539 | -0.0064565 | 0.037485 | 0.0052323 | -122.0221 | -0.24584 | -122.5736 | 0.18032 | -0.09122 | 0.36632 | -122.3982 | 0.060571 | 0.018674 | -0.001407 | 0.15776 | 0.28842 | -0.17081 | -0.24199 | 0.21382 | 0.006373 | 0.58985 | 0.038442 | -0.17537 | -0.26517 | 0.19237 | 122.37 | -0.016186 | 122.6726 | 122.6106 | 0.24058 | 0.11447 | -0.34476 | 122.7923 | 122.5208 | 122.9783 | 122.3662 | -122.5721 | 122.7698 | 122.9004 | 122.4412 | 122.6307 | -0.41594
1060.9531 | 122.7951 | -122.6624 | 0.19684 | 1.4211e-13 | -0.018978 | -0.00092531 | 0.063126 | -0.0122 | 0.059881 | 0.013277 | 0.0077016 | 0.0081403 | -0.0068837 | 0.037057 | 0.0045915 | -122.0176 | -0.25042 | -122.5736 | 0.18032 | -0.086641 | 0.3709 | -122.4119 | 0.060571 | 0.023253 | 0.01233 | 0.16692 | 0.28842 | -0.17539 | -0.23741 | 0.25043 | -0.016515 | 0.64479 | 0.088796 | -0.16164 | -0.28348 | 0.17406 | 122.4249 | -0.029917 | 122.7229 | 122.6747 | 0.24974 | 0.091585 | -0.37223 | 122.8427 | 122.5757 | 123.0332 | 122.4119 | -122.6088 | 122.8293 | 122.9508 | 122.487 | 122.6856 | -0.43425
1062.7031 | 122.818 | -122.6807 | 0.19226 | 1.4211e-13 | -0.018551 | -0.00071151 | 0.062699 | -0.011986 | 0.059454 | -0.0019839 | 0.0077016 | 0.0074993 | -0.0062429 | 0.037485 | 0.0048051 | -122.0176 | -0.24126 | -122.5781 | 0.1849 | -0.09122 | 0.34342 | -122.4028 | 0.055992 | 0.027831 | 0.007751 | 0.15776 | 0.28842 | -0.17539 | -0.24199 | 0.2779 | -0.00736 | 0.6631 | 0.10253 | -0.17537 | -0.28348 | 0.15116 | 122.4387 | -0.034497 | 122.7367 | 122.6884 | 0.24974 | 0.096162 | -0.36765 | 122.8656 | 122.5894 | 123.0241 | 122.4394 | -122.595 | 122.8384 | 122.9691 | 122.5053 | 122.7085 | -0.43425
1064.3906 | 122.7905 | -122.6715 | 0.20142 | 1.4211e-13 | -0.018978 | -0.00092531 | 0.062699 | -0.011986 | 0.059454 | -0.0019839 | 0.0079152 | 0.0079267 | -0.0066701 | 0.037271 | 0.0050187 | -122.013 | -0.2321 | -122.5736 | 0.1849 | -0.095798 | 0.3709 | -122.4028 | 0.06515 | 0.023253 | 0.003172 | 0.15776 | 0.27469 | -0.16624 | -0.23741 | 0.26875 | -0.016515 | 0.65852 | 0.097951 | -0.1708 | -0.29721 | 0.16948 | 122.4341 | -0.043652 | 122.7367 | 122.6747 | 0.24058 | 0.073271 | -0.36765 | 122.8564 | 122.5757 | 123.0424 | 122.4394 | -122.6042 | 122.8293 | 122.9462 | 122.5053 | 122.6948 | -0.43883
1066.1406 | 122.9187 | -122.6074 | 0.16937 | 1.4211e-13 | -0.018765 | -0.00092531 | 0.062699 | -0.0122 | 0.059454 | 0.0056466 | 0.008129 | 0.0081403 | -0.0064565 | 0.037485 | 0.0050187 | -122.013 | -0.24126 | -122.5736 | 0.18032 | -0.09122 | 0.3709 | -122.3936 | 0.060571 | 0.023253 | -0.001407 | 0.16234 | 0.27926 | -0.17081 | -0.23741 | 0.21382 | 0.01095 | 0.59443 | 0.033864 | -0.17995 | -0.26059 | 0.20152 | 122.37 | -0.007031 | 122.668 | 122.606 | 0.236 | 0.10989 | -0.34019 | 122.7877 | 122.5162 | 122.9783 | 122.3662 | -122.563 | 122.7698 | 122.8867 | 122.4366 | 122.6307 | -0.40678
1067.8906 | 122.9141 | -122.5983 | 0.15564 | 1.4211e-13 | -0.018765 | -0.00092531 | 0.063126 | -0.011986 | 0.059454 | -0.0019839 | 0.0077016 | 0.0081403 | -0.0066701 | 0.037485 | 0.0052323 | -122.0176 | -0.25042 | -122.5736 | 0.1849 | -0.086641 | 0.37548 | -122.3936 | 0.055992 | 0.023253 | 0.003172 | 0.16234 | 0.28842 | -0.17539 | -0.23741 | 0.20466 | 0.029261 | 0.5807 | 0.024709 | -0.17995 | -0.24228 | 0.21984 | 122.3609 | 0.006702 | 122.6543 | 122.6014 | 0.24058 | 0.13278 | -0.33103 | 122.7832 | 122.5116 | 122.9737 | 122.3479 | -122.5492 | 122.7606 | 122.8867 | 122.4229 | 122.6215 | -0.39305
1069.5781 | 122.9141 | -122.612 | 0.17395 | 1.4211e-13 | -0.018978 | -0.0011389 | 0.062485 | -0.011986 | 0.059667 | 0.0056466 | 0.008129 | 0.0081403 | -0.0068837 | 0.037485 | 0.0048051 | -122.0176 | -0.24584 | -122.5873 | 0.18032 | -0.082062 | 0.37548 | -122.4028 | 0.060571 | 0.027831 | 0.007751 | 0.16692 | 0.28384 | -0.17081 | -0.23283 | 0.20924 | 0.006373 | 0.59443 | 0.024707 | -0.18453 | -0.25601 | 0.20153 | 122.3792 | -0.007029 | 122.6726 | 122.6198 | 0.24058 | 0.10989 | -0.34476 | 122.7923 | 122.5299 | 122.9875 | 122.3662 | -122.5767 | 122.7789 | 122.8958 | 122.4412 | 122.6398 | -0.40678
1071.3438 | 122.818 | -122.6532 | 0.19684 | 1.4211e-13 | -0.018978 | -0.0011389 | 0.062913 | -0.011986 | 0.059667 | -0.0019839 | 0.0079152 | 0.0081403 | -0.0062429 | 0.037485 | 0.0048051 | -122.0176 | -0.255 | -122.569 | 0.18032 | -0.086641 | 0.348 | -122.4028 | 0.060571 | 0.023253 | 0.003172 | 0.15776 | 0.28842 | -0.17997 | -0.23741 | 0.25044 | -0.016515 | 0.63563 | 0.084219 | -0.16622 | -0.28348 | 0.15116 | 122.4158 | -0.039074 | 122.7138 | 122.6564 | 0.24058 | 0.091585 | -0.37681 | 122.8335 | 122.5666 | 123.0012 | 122.3982 | -122.5996 | 122.811 | 122.9416 | 122.4732 | 122.6765 | -0.43425
1073.0781 | 122.818 | -122.644 | 0.19684 | 1.4211e-13 | -0.018978 | -0.0013525 | 0.062913 | -0.011986 | 0.059667 | -0.0096144 | 0.008129 | 0.0081403 | -0.0064565 | 0.037271 | 0.0048051 | -122.013 | -0.24584 | -122.569 | 0.16659 | -0.09122 | 0.3709 | -122.3936 | 0.060571 | 0.023253 | -0.005985 | 0.15318 | 0.28384 | -0.17081 | -0.23283 | 0.25044 | -0.030251 | 0.63105 | 0.075064 | -0.17537 | -0.28806 | 0.17406 | 122.4112 | -0.043653 | 122.7046 | 122.6381 | 0.22685 | 0.087006 | -0.36765 | 122.8106 | 122.5528 | 123.0149 | 122.3982 | -122.5904 | 122.7972 | 122.9279 | 122.4732 | 122.6673 | -0.42967
1074.8281 | 122.8363 | -122.6532 | 0.17395 | 1.4211e-13 | -0.018978 | -0.0011389 | 0.062485 | -0.011773 | 0.059454 | 0.0056466 | 0.0077016 | 0.0083539 | -0.0068837 | 0.037057 | 0.0045915 | -122.013 | -0.24126 | -122.5827 | 0.17574 | -0.09122 | 0.3709 | -122.3982 | 0.060571 | 0.027831 | 0.007751 | 0.15776 | 0.28384 | -0.17081 | -0.22825 | 0.25501 | 0.001794 | 0.64021 | 0.070484 | -0.18453 | -0.26517 | 0.19695 | 122.4249 | -0.016186 | 122.7138 | 122.6609 | 0.236 | 0.10989 | -0.34476 | 122.8289 | 122.562 | 123.0241 | 122.4119 | -122.5721 | 122.811 | 122.937 | 122.4824 | 122.681 | -0.4022
1076.5156 | 122.9233 | -122.5983 | 0.16479 | 1.4211e-13 | -0.018978 | -0.00092531 | 0.062485 | -0.011986 | 0.059881 | -0.0096144 | 0.0077016 | 0.0083539 | -0.0064565 | 0.037485 | 0.0048051 | -122.0176 | -0.255 | -122.5736 | 0.18032 | -0.086641 | 0.3709 | -122.4028 | 0.060571 | 0.027831 | 0.007751 | 0.16234 | 0.28842 | -0.17539 | -0.24199 | 0.1955 | 0.015528 | 0.5807 | 0.024709 | -0.1708 | -0.25144 | 0.2061 | 122.3563 | -0.002453 | 122.6588 | 122.606 | 0.24974 | 0.12363 | -0.34019 | 122.7786 | 122.5116 | 122.9692 | 122.3433 | -122.5676 | 122.7606 | 122.8867 | 122.4229 | 122.6261 | -0.40678
1078.2656 | 122.7859 | -122.6349 | 0.18768 | 1.4211e-13 | -0.019192 | -0.00092531 | 0.062699 | -0.0122 | 0.059667 | 0.0056466 | 0.008129 | 0.0079267 | -0.0066701 | 0.037485 | 0.0048051 | -122.013 | -0.25042 | -122.5736 | 0.1849 | -0.09122 | 0.33885 | -122.3936 | 0.060571 | 0.018674 | 0.003172 | 0.16234 | 0.28384 | -0.16624 | -0.23741 | 0.24128 | -0.002782 | 0.6219 | 0.06133 | -0.17995 | -0.2789 | 0.15116 | 122.3975 | -0.025341 | 122.6955 | 122.6381 | 0.24058 | 0.096161 | -0.35392 | 122.8198 | 122.5437 | 122.9737 | 122.3845 | -122.5813 | 122.7972 | 122.9187 | 122.4687 | 122.6536 | -0.42509
1080.0156 | 122.9233 | -122.6028 | 0.16022 | 1.4211e-13 | -0.018978 | -0.00092531 | 0.062485 | -0.0122 | 0.059454 | 0.0056466 | 0.0079152 | 0.0083539 | -0.0068837 | 0.037271 | 0.0045915 | -122.0176 | -0.25042 | -122.5781 | 0.1849 | -0.09122 | 0.38005 | -122.3982 | 0.060571 | 0.018674 | -0.001407 | 0.15776 | 0.293 | -0.17081 | -0.23741 | 0.20466 | 0.024684 | 0.58528 | 0.024708 | -0.17995 | -0.25144 | 0.21984 | 122.3654 | -0.002453 | 122.6634 | 122.6014 | 0.236 | 0.13278 | -0.33103 | 122.7877 | 122.5116 | 122.9829 | 122.3524 | -122.5584 | 122.7606 | 122.8958 | 122.432 | 122.6215 | -0.39763
1081.7656 | 122.9095 | -122.5983 | 0.15106 | 1.4211e-13 | -0.019192 | -0.0011389 | 0.062485 | -0.011986 | 0.059454 | -0.0019839 | 0.008129 | 0.0081403 | -0.0062429 | 0.037485 | 0.0048051 | -122.0221 | -0.255 | -122.5736 | 0.17574 | -0.09122 | 0.3709 | -122.3936 | 0.060571 | 0.018674 | 0.003172 | 0.15776 | 0.28384 | -0.17539 | -0.24199 | 0.20466 | 0.024682 | 0.57612 | 0.024709 | -0.17995 | -0.24228 | 0.21983 | 122.3563 | 0.006702 | 122.6588 | 122.6014 | 0.24516 | 0.13278 | -0.32645 | 122.774 | 122.507 | 122.9692 | 122.3433 | -122.5447 | 122.756 | 122.8821 | 122.4229 | 122.6169 | -0.39305
1083.4375 | 122.9279 | -122.612 | 0.16022 | 1.4211e-13 | -0.019192 | -0.0011389 | 0.062913 | -0.012414 | 0.059667 | -0.0019839 | 0.008129 | 0.0081403 | -0.0062429 | 0.037485 | 0.0050187 | -122.013 | -0.255 | -122.5781 | 0.17574 | -0.09122 | 0.36632 | -122.4028 | 0.06515 | 0.023253 | 0.003172 | 0.15776 | 0.29758 | -0.17081 | -0.23741 | 0.20924 | 0.015527 | 0.59901 | 0.033864 | -0.17537 | -0.25144 | 0.2061 | 122.3746 | -0.002453 | 122.6771 | 122.6152 | 0.24058 | 0.13736 | -0.33103 | 122.7877 | 122.5208 | 122.9783 | 122.357 | -122.563 | 122.7698 | 122.9096 | 122.4412 | 122.6353 | -0.39763
1085.1875 | 122.8317 | -122.6532 | 0.19684 | 1.4211e-13 | -0.018978 | -0.0013525 | 0.063126 | -0.011986 | 0.059881 | -0.0019839 | 0.0079152 | 0.0081403 | -0.0068837 | 0.037698 | 0.0050187 | -122.0084 | -0.25957 | -122.5781 | 0.18032 | -0.09122 | 0.36632 | -122.3982 | 0.060571 | 0.023253 | 0.003172 | 0.15776 | 0.28384 | -0.16166 | -0.23741 | 0.25501 | -0.016515 | 0.64479 | 0.075062 | -0.17995 | -0.28806 | 0.16948 | 122.4158 | -0.039074 | 122.7138 | 122.6564 | 0.24058 | 0.087006 | -0.3585 | 122.8335 | 122.562 | 123.0195 | 122.3936 | -122.595 | 122.811 | 122.937 | 122.4915 | 122.6765 | -0.43425
1086.9219 | 122.7768 | -122.6578 | 0.19226 | 1.4211e-13 | -0.019406 | -0.0011389 | 0.062485 | -0.012414 | 0.059454 | 0.0056466 | 0.0077016 | 0.0079267 | -0.0066701 | 0.037698 | 0.0048051 | -122.0084 | -0.25957 | -122.5736 | 0.18032 | -0.09122 | 0.3709 | -122.3982 | 0.06515 | 0.023253 | 0.003172 | 0.15776 | 0.28842 | -0.17081 | -0.23741 | 0.25959 | -0.011938 | 0.64937 | 0.084218 | -0.17537 | -0.28348 | 0.17864 | 122.4204 | -0.034497 | 122.7229 | 122.6609 | 0.24058 | 0.096162 | -0.36308 | 122.8381 | 122.5666 | 123.0287 | 122.3982 | -122.5904 | 122.8155 | 122.9462 | 122.487 | 122.681 | -0.42967
1088.5938 | 122.7905 | -122.6624 | 0.16937 | 1.4211e-13 | -0.019192 | -0.0011389 | 0.063126 | -0.0122 | 0.059667 | 0.0056466 | 0.0077016 | 0.0083539 | -0.0066701 | 0.037271 | 0.0050187 | -122.013 | -0.26415 | -122.5781 | 0.18032 | -0.086641 | 0.3709 | -122.3936 | 0.060571 | 0.023253 | 0.003172 | 0.15776 | 0.28384 | -0.17081 | -0.24199 | 0.26875 | 0.01095 | 0.64936 | 0.084218 | -0.18453 | -0.25601 | 0.20152 | 122.4204 | -0.011609 | 122.7229 | 122.6655 | 0.24516 | 0.11447 | -0.34019 | 122.8427 | 122.5757 | 123.0332 | 122.3982 | -122.563 | 122.8201 | 122.9462 | 122.4915 | 122.6856 | -0.41136
1090.3438 | 122.7905 | -122.6532 | 0.20599 | 1.4211e-13 | -0.019192 | -0.0011389 | 0.062913 | -0.0122 | 0.059454 | -0.0096144 | 0.0077016 | 0.0081403 | -0.0062429 | 0.037698 | 0.0045915 | -122.0176 | -0.25957 | -122.569 | 0.1849 | -0.086641 | 0.35258 | -122.3936 | 0.060571 | 0.023253 | 0.003172 | 0.15318 | 0.27926 | -0.17539 | -0.23741 | 0.25959 | -0.021093 | 0.63563 | 0.084219 | -0.17537 | -0.29263 | 0.14659 | 122.4158 | -0.052809 | 122.7138 | 122.6564 | 0.24058 | 0.073271 | -0.38139 | 122.8381 | 122.5666 | 123.0058 | 122.3936 | -122.5996 | 122.8064 | 122.9325 | 122.4778 | 122.6765 | -0.4434
1092.0938 | 122.9095 | -122.6166 | 0.16937 | 1.4211e-13 | -0.019192 | -0.0011389 | 0.062913 | -0.011986 | 0.059454 | 0.0056466 | 0.0077016 | 0.0079267 | -0.0066701 | 0.037271 | 0.0045915 | -122.013 | -0.25957 | -122.5781 | 0.1849 | -0.09122 | 0.3709 | -122.389 | 0.051413 | 0.023253 | 0.003172 | 0.15776 | 0.28842 | -0.16624 | -0.23283 | 0.22755 | 0.015528 | 0.60359 | 0.038441 | -0.18911 | -0.26059 | 0.20152 | 122.3837 | -0.011609 | 122.668 | 122.6197 | 0.236 | 0.11905 | -0.33561 | 122.8015 | 122.5254 | 122.9875 | 122.357 | -122.5584 | 122.7743 | 122.905 | 122.4503 | 122.6398 | -0.4022
1093.7812 | 122.8363 | -122.644 | 0.1831 | 1.4211e-13 | -0.019406 | -0.00071151 | 0.062485 | -0.0122 | 0.059667 | -0.0019839 | 0.007488 | 0.0081403 | -0.0064565 | 0.037698 | 0.0045915 | -122.0038 | -0.25957 | -122.5781 | 0.17117 | -0.086641 | 0.3709 | -122.3936 | 0.060571 | 0.018674 | 0.003172 | 0.1715 | 0.28842 | -0.16624 | -0.23283 | 0.25044 | -0.011939 | 0.64021 | 0.065907 | -0.18453 | -0.26975 | 0.18779 | 122.4112 | -0.011606 | 122.7046 | 122.6472 | 0.236 | 0.10532 | -0.34934 | 122.8152 | 122.5574 | 123.0149 | 122.3845 | -122.5767 | 122.8155 | 122.9325 | 122.4778 | 122.6627 | -0.41594
1095.5312 | 122.9187 | -122.6212 | 0.16022 | 1.4211e-13 | -0.019406 | -0.00092531 | 0.062913 | -0.0122 | 0.059454 | -0.0019839 | 0.0079152 | 0.0083539 | -0.0066701 | 0.037271 | 0.0048051 | -122.0084 | -0.255 | -122.569 | 0.17574 | -0.082062 | 0.36632 | -122.3982 | 0.06515 | 0.023253 | 0.01233 | 0.16692 | 0.28384 | -0.17081 | -0.23741 | 0.22297 | 0.015527 | 0.61274 | 0.052176 | -0.17079 | -0.24228 | 0.2061 | 122.3837 | 0.006704 | 122.6863 | 122.6335 | 0.24974 | 0.12363 | -0.33103 | 122.7969 | 122.5391 | 122.9875 | 122.3662 | -122.5584 | 122.7881 | 122.905 | 122.4503 | 122.6444 | -0.39763
1097.2188 | 122.7951 | -122.6349 | 0.1831 | 1.4211e-13 | -0.018978 | -0.0013525 | 0.062913 | -0.0122 | 0.05924 | 0.013277 | 0.0077016 | 0.0081403 | -0.0064565 | 0.037698 | 0.0045915 | -122.013 | -0.25957 | -122.5736 | 0.18032 | -0.086641 | 0.36632 | -122.389 | 0.060571 | 0.018674 | 0.007751 | 0.15776 | 0.28842 | -0.17081 | -0.23741 | 0.24586 | -0.002782 | 0.6219 | 0.06133 | -0.18453 | -0.26975 | 0.18321 | 122.3975 | -0.025341 | 122.6955 | 122.6426 | 0.24516 | 0.10532 | -0.35392 | 122.8152 | 122.5482 | 123.0012 | 122.3753 | -122.5721 | 122.7927 | 122.9233 | 122.4641 | 122.6536 | -0.42051
1098.9531 | 122.9004 | -122.5891 | 0.16022 | 1.4211e-13 | -0.018765 | -0.00092531 | 0.062913 | -0.0122 | 0.059667 | 0.0056466 | 0.0077016 | 0.0083539 | -0.0066701 | 0.037912 | 0.0048051 | -122.0084 | -0.26415 | -122.5736 | 0.17117 | -0.086641 | 0.3709 | -122.3936 | 0.060571 | 0.027831 | 0.007751 | 0.15776 | 0.28384 | -0.17539 | -0.23741 | 0.19551 | 0.010949 | 0.5807 | 0.015553 | -0.17995 | -0.24686 | 0.21068 | 122.3517 | -0.002453 | 122.6497 | 122.5969 | 0.24516 | 0.12363 | -0.33561 | 122.7603 | 122.5025 | 122.96 | 122.325 | -122.5538 | 122.7469 | 122.873 | 122.4137 | 122.6169 | -0.39763
1100.7031 | 122.9095 | -122.612 | 0.17395 | 1.4211e-13 | -0.019192 | -0.00092531 | 0.062485 | -0.011773 | 0.059881 | 0.0056466 | 0.0079152 | 0.0079267 | -0.0064565 | 0.037698 | 0.0045915 | -122.0084 | -0.26415 | -122.5736 | 0.18032 | -0.086641 | 0.37548 | -122.389 | 0.060571 | 0.023253 | 0.003172 | 0.16692 | 0.28842 | -0.17081 | -0.23283 | 0.22297 | 0.006373 | 0.60359 | 0.038442 | -0.18453 | -0.26059 | 0.20153 | 122.3792 | -0.007029 | 122.6726 | 122.6152 | 0.236 | 0.11447 | -0.34476 | 122.7923 | 122.5254 | 122.9875 | 122.3478 | -122.563 | 122.7789 | 122.9004 | 122.4412 | 122.6353 | -0.40678
1102.375 | 122.818 | -122.6212 | 0.19226 | 1.4211e-13 | -0.018978 | -0.00092531 | 0.063126 | -0.012627 | 0.059667 | 0.013277 | 0.0079152 | 0.0081403 | -0.0064565 | 0.037698 | 0.0045915 | -122.0084 | -0.26873 | -122.5736 | 0.18032 | -0.09122 | 0.3709 | -122.3936 | 0.06515 | 0.03241 | 0.003172 | 0.15776 | 0.28384 | -0.17539 | -0.23283 | 0.22755 | -0.011938 | 0.61274 | 0.047597 | -0.17995 | -0.28348 | 0.17864 | 122.3883 | -0.034497 | 122.6863 | 122.6243 | 0.236 | 0.091583 | -0.36765 | 122.8015 | 122.5299 | 122.9921 | 122.3524 | -122.5859 | 122.7789 | 122.905 | 122.4458 | 122.6536 | -0.42509
1104.125 | 122.7859 | -122.6166 | 0.19684 | 1.4211e-13 | -0.018978 | -0.0013525 | 0.062913 | -0.012414 | 0.05924 | -0.0019839 | 0.0079152 | 0.0081403 | -0.0066701 | 0.037912 | 0.0048051 | -122.0084 | -0.26873 | -122.5736 | 0.18032 | -0.086641 | 0.36174 | -122.389 | 0.055992 | 0.027831 | 0.007751 | 0.15776 | 0.28384 | -0.17081 | -0.24199 | 0.22755 | -0.016515 | 0.60817 | 0.043019 | -0.18453 | -0.28348 | 0.1649 | 122.3746 | -0.039074 | 122.6726 | 122.6243 | 0.24974 | 0.087006 | -0.36765 | 122.7969 | 122.5299 | 122.9783 | 122.3478 | -122.5859 | 122.7743 | 122.9004 | 122.4458 | 122.6444 | -0.43883
1105.8906 | 122.8867 | -122.612 | 0.16937 | 1.4211e-13 | -0.018978 | -0.0015663 | 0.062699 | -0.0122 | 0.059454 | -0.0019839 | 0.0077016 | 0.0083539 | -0.0064565 | 0.037485 | 0.0048051 | -122.0038 | -0.27331 | -122.569 | 0.17574 | -0.095798 | 0.37548 | -122.389 | 0.060571 | 0.03241 | -0.001407 | 0.16234 | 0.28842 | -0.17081 | -0.24199 | 0.22297 | 0.006371 | 0.60817 | 0.043021 | -0.17995 | -0.26517 | 0.2061 | 122.37 | -0.007031 | 122.6726 | 122.6106 | 0.24058 | 0.11905 | -0.34019 | 122.7877 | 122.5162 | 122.9875 | 122.3387 | -122.5584 | 122.7743 | 122.9004 | 122.4412 | 122.6444 | -0.41136
1107.6406 | 122.8592 | -122.5937 | 0.17853 | 1.4211e-13 | -0.019406 | -0.0011389 | 0.062699 | -0.011986 | 0.059454 | 0.0056466 | 0.008129 | 0.0081403 | -0.0066701 | 0.037698 | 0.0048051 | -121.9993 | -0.26873 | -122.5736 | 0.1849 | -0.086641 | 0.37548 | -122.3844 | 0.060571 | 0.023253 | 0.007751 | 0.16234 | 0.293 | -0.17081 | -0.23741 | 0.20924 | 0.006373 | 0.59444 | 0.020131 | -0.18911 | -0.26517 | 0.19695 | 122.3563 | -0.016186 | 122.6543 | 122.6014 | 0.24516 | 0.11447 | -0.34934 | 122.7786 | 122.507 | 122.9692 | 122.325 | -122.563 | 122.756 | 122.8867 | 122.4229 | 122.6169 | -0.41594
1109.3125 | 122.7814 | -122.6578 | 0.18768 | 1.4211e-13 | -0.019406 | -0.00071151 | 0.062699 | -0.0122 | 0.059667 | 0.0056466 | 0.007488 | 0.0079267 | -0.0064565 | 0.037912 | 0.0048051 | -121.9993 | -0.26873 | -122.569 | 0.17117 | -0.082062 | 0.38005 | -122.389 | 0.055992 | 0.027831 | 0.007751 | 0.15776 | 0.28842 | -0.17539 | -0.24199 | 0.26875 | -0.016517 | 0.65852 | 0.088797 | -0.17995 | -0.26975 | 0.19237 | 122.4158 | -0.029919 | 122.7138 | 122.6655 | 0.24974 | 0.10074 | -0.36308 | 122.8289 | 122.5757 | 123.0378 | 122.389 | -122.5767 | 122.8155 | 122.9462 | 122.4824 | 122.6856 | -0.42967
1111.0625 | 122.8821 | -122.612 | 0.17395 | 1.4211e-13 | -0.019192 | -0.00092531 | 0.062913 | -0.0122 | 0.059454 | 0.020908 | 0.008129 | 0.0081403 | -0.0066701 | 0.037698 | 0.0045915 | -122.0038 | -0.27331 | -122.569 | 0.18032 | -0.082062 | 0.37548 | -122.3844 | 0.06515 | 0.023253 | -0.001407 | 0.16234 | 0.28842 | -0.17081 | -0.24657 | 0.22755 | 0.006373 | 0.60817 | 0.043021 | -0.18453 | -0.25601 | 0.20153 | 122.3654 | -0.011608 | 122.6771 | 122.6106 | 0.24516 | 0.11447 | -0.34476 | 122.7923 | 122.5299 | 122.9875 | 122.3387 | -122.5584 | 122.7743 | 122.9004 | 122.4412 | 122.6353 | -0.42052
1112.75 | 122.8363 | -122.6257 | 0.19684 | 1.4211e-13 | -0.018978 | -0.0013525 | 0.062699 | -0.0122 | 0.059881 | 0.0056466 | 0.0077016 | 0.0079267 | -0.0066701 | 0.037485 | 0.0045915 | -121.9993 | -0.27789 | -122.569 | 0.17574 | -0.082062 | 0.3709 | -122.3844 | 0.069728 | 0.027831 | 0.01233 | 0.16234 | 0.28842 | -0.17081 | -0.23741 | 0.24129 | -0.021094 | 0.62648 | 0.056753 | -0.18453 | -0.2789 | 0.17406 | 122.3883 | -0.034496 | 122.6955 | 122.6381 | 0.24974 | 0.091585 | -0.36765 | 122.8015 | 122.5437 | 122.9966 | 122.3478 | -122.5813 | 122.7881 | 122.9142 | 122.4549 | 122.6536 | -0.43425
1114.5312 | 122.8592 | -122.6166 | 0.16022 | 1.4211e-13 | -0.019192 | -0.0013525 | 0.062913 | -0.0122 | 0.059454 | 0.0056466 | 0.0079152 | 0.0079267 | -0.0064565 | 0.037698 | 0.0048051 | -122.0038 | -0.27331 | -122.5736 | 0.18948 | -0.086641 | 0.37548 | -122.3799 | 0.060571 | 0.018674 | 0.007751 | 0.16234 | 0.28384 | -0.17081 | -0.23741 | 0.23671 | 0.029262 | 0.61275 | 0.043019 | -0.19369 | -0.24686 | 0.21526 | 122.3792 | 0.002125 | 122.6771 | 122.6243 | 0.24516 | 0.12363 | -0.33103 | 122.8061 | 122.5299 | 122.9921 | 122.3433 | -122.5401 | 122.7789 | 122.9004 | 122.4458 | 122.6353 | -0.39763
1116.2188 | 122.8867 | -122.6028 | 0.16479 | 1.4211e-13 | -0.018978 | -0.00092531 | 0.063126 | -0.011986 | 0.059454 | 0.0056466 | 0.008129 | 0.0083539 | -0.0066701 | 0.037698 | 0.0045915 | -121.9993 | -0.27789 | -122.569 | 0.18032 | -0.086641 | 0.3709 | -122.3844 | 0.060571 | 0.023253 | 0.007751 | 0.16234 | 0.28842 | -0.17081 | -0.23741 | 0.2184 | 0.015528 | 0.60359 | 0.033865 | -0.18453 | -0.25144 | 0.2061 | 122.3654 | -0.002453 | 122.6634 | 122.6106 | 0.24516 | 0.12363 | -0.33561 | 122.7832 | 122.5162 | 122.9737 | 122.325 | -122.5492 | 122.7652 | 122.8913 | 122.432 | 122.6261 | -0.40221
1117.9531 | 122.8638 | -122.5983 | 0.17395 | 1.4211e-13 | -0.019192 | -0.00092531 | 0.062485 | -0.012414 | 0.059454 | 0.013277 | 0.0077016 | 0.0081403 | -0.0062429 | 0.037485 | 0.0048051 | -121.9947 | -0.27789 | -122.5644 | 0.1849 | -0.09122 | 0.348 | -122.3753 | 0.060571 | 0.027831 | 0.003172 | 0.16234 | 0.28842 | -0.17997 | -0.24199 | 0.22298 | 0.010951 | 0.60359 | 0.033866 | -0.18911 | -0.26517 | 0.17405 | 122.3563 | -0.011608 | 122.6588 | 122.6014 | 0.24516 | 0.11447 | -0.35392 | 122.7832 | 122.507 | 122.9463 | 122.3204 | -122.5492 | 122.7606 | 122.8867 | 122.4183 | 122.6261 | -0.41594
1119.6875 | 122.9233 | -122.6028 | 0.17853 | 1.4211e-13 | -0.019406 | -0.0011389 | 0.062272 | -0.012414 | 0.059667 | -0.0096144 | 0.0079152 | 0.0083539 | -0.0064565 | 0.037912 | 0.0043777 | -121.9947 | -0.28704 | -122.5644 | 0.17574 | -0.095798 | 0.3709 | -122.3844 | 0.06515 | 0.03241 | 0.007751 | 0.1715 | 0.28842 | -0.17081 | -0.23283 | 0.2184 | -0.002784 | 0.60817 | 0.038443 | -0.17995 | -0.27433 | 0.19237 | 122.37 | -0.007029 | 122.668 | 122.6106 | 0.24058 | 0.10989 | -0.34934 | 122.7786 | 122.507 | 122.9737 | 122.3158 | -122.563 | 122.7743 | 122.8913 | 122.432 | 122.6353 | -0.41136
1121.4375 | 122.7905 | -122.6257 | 0.17853 | 1.4211e-13 | -0.018978 | -0.00092531 | 0.062699 | -0.0122 | 0.059454 | -0.0019839 | 0.0079152 | 0.0079267 | -0.0068837 | 0.038126 | 0.0045915 | -121.9901 | -0.28704 | -122.5736 | 0.18032 | -0.095798 | 0.348 | -122.389 | 0.069728 | 0.027831 | 0.003172 | 0.16234 | 0.28842 | -0.16624 | -0.24199 | 0.23671 | 0.001795 | 0.63563 | 0.052174 | -0.18453 | -0.27433 | 0.16948 | 122.3837 | -0.016186 | 122.6955 | 122.6289 | 0.24516 | 0.10989 | -0.34476 | 122.8061 | 122.5299 | 122.9737 | 122.3387 | -122.5676 | 122.7881 | 122.9142 | 122.4595 | 122.6536 | -0.42052
1123.1875 | 122.7905 | -122.6212 | 0.19226 | 1.4211e-13 | -0.018978 | -0.0015663 | 0.062699 | -0.012414 | 0.059881 | 0.013277 | 0.0079152 | 0.0081403 | -0.0068837 | 0.037912 | 0.0045915 | -121.9993 | -0.28704 | -122.5644 | 0.18948 | -0.082062 | 0.37548 | -122.3799 | 0.051413 | 0.027831 | 0.007751 | 0.16234 | 0.29758 | -0.17081 | -0.25115 | 0.24129 | -0.002782 | 0.6219 | 0.056754 | -0.18453 | -0.27432 | 0.18321 | 122.37 | -0.029919 | 122.6726 | 122.6289 | 0.2589 | 0.10532 | -0.36308 | 122.8106 | 122.5391 | 122.9966 | 122.3341 | -122.5721 | 122.7835 | 122.9187 | 122.4503 | 122.649 | -0.44341
1124.8594 | 122.8226 | -122.6028 | 0.19684 | 1.4211e-13 | -0.019192 | -0.0011389 | 0.062699 | -0.0122 | 0.059667 | 0.013277 | 0.0077016 | 0.0079267 | -0.0064565 | 0.037485 | 0.0050187 | -121.9947 | -0.29162 | -122.5644 | 0.1849 | -0.09122 | 0.37548 | -122.3799 | 0.055992 | 0.023253 | -0.001407 | 0.16234 | 0.29758 | -0.16624 | -0.24199 | 0.22298 | -0.011937 | 0.60817 | 0.038443 | -0.18453 | -0.28806 | 0.17864 | 122.3609 | -0.034496 | 122.6588 | 122.6014 | 0.24058 | 0.10074 | -0.36307 | 122.7877 | 122.5116 | 122.9783 | 122.3112 | -122.5767 | 122.7652 | 122.9004 | 122.4366 | 122.6261 | -0.43883
1126.6094 | 122.8546 | -122.5983 | 0.1831 | 1.4211e-13 | -0.019192 | -0.0011389 | 0.062699 | -0.011773 | 0.05924 | -0.0019839 | 0.0077016 | 0.0081403 | -0.0066701 | 0.037698 | 0.0048051 | -121.9947 | -0.29162 | -122.5644 | 0.18032 | -0.086641 | 0.36632 | -122.3707 | 0.060571 | 0.014095 | -0.001407 | 0.15318 | 0.29758 | -0.17081 | -0.24199 | 0.22756 | -0.002782 | 0.60359 | 0.033866 | -0.19369 | -0.26975 | 0.18321 | 122.3563 | -0.02992 | 122.6588 | 122.5969 | 0.24058 | 0.11448 | -0.35392 | 122.7786 | 122.5116 | 122.9646 | 122.3066 | -122.5538 | 122.7515 | 122.8958 | 122.4275 | 122.6124 | -0.42509
1128.3594 | 122.7768 | -122.644 | 0.19684 | 1.4211e-13 | -0.019406 | -0.0011389 | 0.062699 | -0.0122 | 0.059667 | 0.0056466 | 0.0077016 | 0.0081403 | -0.0066701 | 0.037698 | 0.0048051 | -121.9901 | -0.28704 | -122.5644 | 0.17574 | -0.09122 | 0.37548 | -122.3753 | 0.060571 | 0.023253 | 0.003172 | 0.16234 | 0.29758 | -0.17997 | -0.23741 | 0.26875 | -0.021094 | 0.65395 | 0.079642 | -0.18911 | -0.28806 | 0.17864 | 122.4066 | -0.034496 | 122.7046 | 122.6472 | 0.24058 | 0.10074 | -0.37681 | 122.8198 | 122.5528 | 123.0195 | 122.357 | -122.5721 | 122.8064 | 122.9416 | 122.4641 | 122.6673 | -0.43425
1130.0469 | 122.8867 | -122.6028 | 0.16479 | 1.4211e-13 | -0.018978 | -0.0013525 | 0.062699 | -0.012414 | 0.059667 | -0.0019839 | 0.0077016 | 0.0077131 | -0.0066701 | 0.037698 | 0.0048051 | -121.9901 | -0.30078 | -122.5552 | 0.18032 | -0.082062 | 0.37548 | -122.389 | 0.06515 | 0.023253 | 0.003172 | 0.16234 | 0.293 | -0.17081 | -0.23283 | 0.21382 | 0.015528 | 0.61275 | 0.047599 | -0.16622 | -0.24686 | 0.21068 | 122.37 | -0.002453 | 122.668 | 122.606 | 0.236 | 0.12821 | -0.33561 | 122.7832 | 122.5208 | 122.9783 | 122.3021 | -122.5538 | 122.7652 | 122.8958 | 122.432 | 122.6261 | -0.39763
1131.7969 | 122.9095 | -122.5754 | 0.15564 | 1.4211e-13 | -0.019192 | -0.00092531 | 0.062485 | -0.0122 | 0.059454 | 0.013277 | 0.008129 | 0.0081403 | -0.0068837 | 0.037912 | 0.0048051 | -121.9901 | -0.2962 | -122.5598 | 0.17574 | -0.082062 | 0.3709 | -122.3799 | 0.051413 | 0.018674 | 0.003172 | 0.1715 | 0.28384 | -0.17081 | -0.24199 | 0.19551 | 0.020104 | 0.58528 | 0.015555 | -0.17995 | -0.2377 | 0.21526 | 122.3334 | 0.015859 | 122.6268 | 122.5786 | 0.24516 | 0.1282 | -0.32645 | 122.7511 | 122.4933 | 122.9463 | 122.2792 | -122.5355 | 122.7469 | 122.8592 | 122.4046 | 122.5941 | -0.39763
1133.5469 | 122.8867 | -122.5845 | 0.17395 | 1.4211e-13 | -0.018978 | -0.00071151 | 0.062913 | -0.012414 | 0.059454 | 0.0056466 | 0.0077016 | 0.0079267 | -0.0066701 | 0.038126 | 0.0043777 | -121.9947 | -0.30078 | -122.5598 | 0.18032 | -0.086641 | 0.35716 | -122.3799 | 0.06515 | 0.018674 | -0.001407 | 0.15776 | 0.28384 | -0.17081 | -0.23741 | 0.20467 | 0.006373 | 0.58986 | 0.024711 | -0.17995 | -0.26059 | 0.18321 | 122.3471 | -0.016186 | 122.6497 | 122.5831 | 0.236 | 0.10989 | -0.34476 | 122.7649 | 122.4979 | 122.9417 | 122.2838 | -122.5538 | 122.7423 | 122.8684 | 122.4137 | 122.6032 | -0.41136
1135.2344 | 122.8226 | -122.6212 | 0.1831 | 1.4211e-13 | -0.018978 | -0.0011389 | 0.062913 | -0.011986 | 0.05924 | 0.0056466 | 0.0079152 | 0.0079267 | -0.0066701 | 0.037912 | 0.0048051 | -121.9901 | -0.30078 | -122.5552 | 0.17574 | -0.09122 | 0.36632 | -122.3799 | 0.06515 | 0.023253 | 0.003172 | 0.15776 | 0.28842 | -0.17081 | -0.23741 | 0.24129 | -0.007361 | 0.63106 | 0.06591 | -0.17538 | -0.27432 | 0.18321 | 122.3837 | -0.025341 | 122.6863 | 122.6243 | 0.24058 | 0.10532 | -0.35392 | 122.7969 | 122.5299 | 122.9875 | 122.3204 | -122.563 | 122.7789 | 122.9096 | 122.4503 | 122.6444 | -0.42051
1136.9844 | 122.8455 | -122.5891 | 0.16937 | 1.4211e-13 | -0.018978 | -0.0011389 | 0.062272 | -0.011986 | 0.059667 | 0.013277 | 0.0079152 | 0.0081403 | -0.0066701 | 0.037912 | 0.0048051 | -121.9947 | -0.30536 | -122.5598 | 0.17574 | -0.082062 | 0.35716 | -122.3799 | 0.060571 | 0.023253 | 0.003172 | 0.16234 | 0.28842 | -0.17539 | -0.24199 | 0.20924 | 0.006371 | 0.59444 | 0.029288 | -0.17995 | -0.25143 | 0.18779 | 122.3471 | -0.007031 | 122.6497 | 122.5923 | 0.24516 | 0.11905 | -0.34477 | 122.7649 | 122.507 | 122.9463 | 122.2838 | -122.5492 | 122.7515 | 122.8775 | 122.4137 | 122.6124 | -0.41136
1138.7188 | 122.8775 | -122.5754 | 0.15564 | 1.4211e-13 | -0.019406 | -0.00092531 | 0.062913 | -0.012627 | 0.059667 | 0.013277 | 0.0072744 | 0.0081403 | -0.0068837 | 0.037698 | 0.0048051 | -121.9947 | -0.2962 | -122.5552 | 0.17574 | -0.082062 | 0.35716 | -122.3707 | 0.060571 | 0.018674 | 0.003172 | 0.15776 | 0.293 | -0.17539 | -0.23283 | 0.20467 | 0.020104 | 0.5807 | 0.020133 | -0.18453 | -0.2377 | 0.20152 | 122.3425 | 0.002124 | 122.6359 | 122.5786 | 0.236 | 0.13736 | -0.33103 | 122.7511 | 122.4933 | 122.9325 | 122.2792 | -122.5264 | 122.7331 | 122.8684 | 122.4 | 122.5941 | -0.38847
1140.4688 | 122.8546 | -122.5662 | 0.16937 | 1.4211e-13 | -0.019192 | -0.00092531 | 0.062485 | -0.012414 | 0.059454 | 0.0056466 | 0.0077016 | 0.0081403 | -0.0066701 | 0.037912 | 0.0045915 | -121.9901 | -0.30536 | -122.5552 | 0.17574 | -0.09122 | 0.38463 | -122.3799 | 0.069728 | 0.023253 | 0.003172 | 0.16234 | 0.28842 | -0.16624 | -0.23741 | 0.18635 | 0.006371 | 0.57613 | 0.010978 | -0.17538 | -0.26059 | 0.21526 | 122.3288 | -0.007031 | 122.636 | 122.5694 | 0.24058 | 0.11905 | -0.33561 | 122.742 | 122.475 | 122.9509 | 122.2609 | -122.5492 | 122.7286 | 122.8546 | 122.4 | 122.5895 | -0.40678
1142.2188 | 122.8821 | -122.5754 | 0.15106 | 1.4211e-13 | -0.018978 | -0.0015663 | 0.062699 | -0.0122 | 0.05924 | 0.0056466 | 0.0083426 | 0.0081403 | -0.0066701 | 0.037485 | 0.0045915 | -121.9855 | -0.30536 | -122.5644 | 0.18032 | -0.082062 | 0.3709 | -122.3799 | 0.06515 | 0.023253 | 0.003172 | 0.16234 | 0.28842 | -0.17539 | -0.23283 | 0.19551 | 0.029261 | 0.58986 | 0.010977 | -0.18453 | -0.23312 | 0.21983 | 122.3425 | 0.01128 | 122.6405 | 122.5786 | 0.236 | 0.13736 | -0.32645 | 122.7557 | 122.4933 | 122.9463 | 122.27 | -122.5309 | 122.7377 | 122.8638 | 122.4 | 122.5986 | -0.38389
1143.9062 | 122.7631 | -122.6303 | 0.19684 | 1.4211e-13 | -0.018978 | -0.0011389 | 0.062913 | -0.0122 | 0.059667 | -0.0019839 | 0.0079152 | 0.0079267 | -0.0064565 | 0.038126 | 0.0045915 | -121.9901 | -0.30994 | -122.5552 | 0.18032 | -0.082062 | 0.37548 | -122.3753 | 0.055992 | 0.009516 | -0.001407 | 0.15318 | 0.28842 | -0.16624 | -0.24199 | 0.25502 | -0.016515 | 0.64021 | 0.075065 | -0.17995 | -0.2789 | 0.17864 | 122.3883 | -0.043653 | 122.6863 | 122.6289 | 0.24058 | 0.091585 | -0.36307 | 122.8106 | 122.5482 | 123.0058 | 122.3204 | -122.5721 | 122.7835 | 122.9187 | 122.4641 | 122.6398 | -0.43883
1145.6562 | 122.7997 | -122.612 | 0.17853 | 1.4211e-13 | -0.018765 | -0.00092531 | 0.062699 | -0.0122 | 0.059454 | 0.0056466 | 0.0077016 | 0.0079267 | -0.0068837 | 0.037912 | 0.0043777 | -121.9809 | -0.30994 | -122.5552 | 0.1849 | -0.09122 | 0.35258 | -122.3844 | 0.060571 | 0.018674 | 0.003172 | 0.1715 | 0.293 | -0.17081 | -0.23741 | 0.22755 | 0.006373 | 0.63106 | 0.056755 | -0.1708 | -0.26975 | 0.17405 | 122.3746 | -0.007029 | 122.6726 | 122.6152 | 0.24058 | 0.11447 | -0.34934 | 122.7969 | 122.5208 | 122.9646 | 122.3021 | -122.563 | 122.7835 | 122.905 | 122.4412 | 122.6307 | -0.41594
1147.3438 | 122.818 | -122.6212 | 0.1831 | 1.4211e-13 | -0.019406 | -0.0011389 | 0.062913 | -0.012414 | 0.059667 | 0.013277 | 0.008129 | 0.0079267 | -0.0068837 | 0.037698 | 0.0045915 | -121.9901 | -0.30536 | -122.5598 | 0.17574 | -0.086641 | 0.37548 | -122.3799 | 0.060571 | 0.018674 | 0.003172 | 0.16234 | 0.28384 | -0.16624 | -0.23741 | 0.24129 | -0.007361 | 0.63106 | 0.061332 | -0.17995 | -0.26975 | 0.19237 | 122.3837 | -0.020763 | 122.6817 | 122.6243 | 0.24058 | 0.10074 | -0.34934 | 122.7969 | 122.5345 | 122.9966 | 122.3158 | -122.563 | 122.7835 | 122.905 | 122.4549 | 122.6398 | -0.42051
1149.0781 | 122.8683 | -122.5845 | 0.16479 | 1.4211e-13 | -0.019192 | -0.0011389 | 0.062699 | -0.0122 | 0.059454 | 0.0056466 | 0.0079152 | 0.0079267 | -0.0068837 | 0.038126 | 0.0048051 | -121.9855 | -0.3191 | -122.5644 | 0.18032 | -0.09122 | 0.33885 | -122.3753 | 0.06515 | 0.018674 | 0.007751 | 0.15776 | 0.28842 | -0.17081 | -0.23741 | 0.20924 | 0.015528 | 0.59902 | 0.020133 | -0.18911 | -0.25601 | 0.17405 | 122.3471 | -0.007031 | 122.6497 | 122.5923 | 0.24516 | 0.12363 | -0.33561 | 122.7649 | 122.4933 | 122.9234 | 122.2654 | -122.5401 | 122.7423 | 122.873 | 122.4137 | 122.6032 | -0.40221
1150.75 | 122.7676 | -122.612 | 0.19226 | 1.4211e-13 | -0.019192 | -0.0011389 | 0.062913 | -0.012627 | 0.059667 | 0.013277 | 0.0077016 | 0.0079267 | -0.0068837 | 0.037912 | 0.0045915 | -121.9855 | -0.31452 | -122.5507 | 0.17574 | -0.09122 | 0.38005 | -122.3707 | 0.069728 | 0.018674 | 0.003172 | 0.16234 | 0.28842 | -0.17081 | -0.23741 | 0.24129 | -0.016517 | 0.62648 | 0.061334 | -0.17996 | -0.28348 | 0.18779 | 122.3746 | -0.029919 | 122.6817 | 122.6152 | 0.24058 | 0.096162 | -0.36308 | 122.7877 | 122.5208 | 122.9921 | 122.2975 | -122.563 | 122.7743 | 122.9004 | 122.4412 | 122.6307 | -0.42967
1152.5 | 122.7859 | -122.612 | 0.21515 | 1.4211e-13 | -0.019192 | -0.0011389 | 0.062913 | -0.013055 | 0.05924 | 0.013277 | 0.0077016 | 0.0081403 | -0.0062429 | 0.037485 | 0.0045915 | -121.9764 | -0.3191 | -122.5461 | 0.1849 | -0.09122 | 0.38005 | -122.7324 | 0.060571 | 0.023253 | -0.001407 | 0.16692 | 0.293 | -0.17539 | -0.23741 | -0.12045 | -0.030248 | 0.63564 | 0.065912 | 0.18636 | -0.30637 | 0.1649 | 122.3746 | -0.048228 | 122.6726 | 122.6106 | 0.236 | 0.077852 | -0.39054 | 122.7969 | 122.5208 | 122.9921 | 122.2929 | -122.9476 | 122.7789 | 122.905 | 122.4366 | 122.6353 | -0.45256
1154.25 | 122.7631 | -122.4792 | 0.29755 | 1.4211e-13 | -0.018978 | -0.00092531 | 0.062699 | -0.0122 | 0.059454 | -0.0019839 | 0.0079152 | 0.0081403 | -0.0068837 | 0.037485 | 0.0048051 | -121.807 | -0.3191 | -122.3813 | 0.29478 | -0.036272 | 0.4991 | -122.5905 | 0.069728 | 0.027831 | 0.01233 | 0.17608 | 0.30216 | -0.16624 | -0.22825 | -0.11125 | -0.002764 | 0.67229 | 0.097978 | 0.20923 | -0.33382 | 0.20155 | 122.251 | -0.12147 | 122.549 | 122.4916 | 0.24058 | 0.004612 | -0.46378 | 122.774 | 122.443 | 122.9783 | 122.1602 | -122.888 | 122.6553 | 122.7814 | 122.313 | 122.5071 | -0.5258
1156 | 122.8088 | -122.5891 | 0.17853 | 1.4211e-13 | -0.019192 | -0.00092531 | 0.062699 | -0.012841 | 0.059454 | -0.0019839 | 0.0079152 | 0.0081403 | -0.0066701 | 0.037912 | 0.0041641 | -121.958 | -0.3191 | -122.5324 | 0.18032 | -0.09122 | 0.37548 | -122.3524 | 0.060571 | 0.023253 | 0.01233 | 0.16692 | 0.28384 | -0.17997 | -0.24657 | 0.23672 | 0.001795 | 0.63106 | 0.056758 | -0.17996 | -0.26975 | 0.19695 | 122.3425 | -0.011607 | 122.6497 | 122.6014 | 0.2589 | 0.10532 | -0.3585 | 122.7694 | 122.4979 | 122.9646 | 122.27 | -122.5309 | 122.756 | 122.873 | 122.4091 | 122.6124 | -0.4251
1157.6875 | 122.8821 | -122.5708 | 0.16937 | 1.4211e-13 | -0.019192 | -0.0013525 | 0.062699 | -0.012627 | 0.059454 | 0.013277 | 0.0079152 | 0.0081403 | -0.0070975 | 0.038126 | 0.0043777 | -121.958 | -0.32367 | -122.5324 | 0.17574 | -0.082062 | 0.33885 | -122.357 | 0.060571 | 0.018674 | 0.003172 | 0.16234 | 0.28842 | -0.16624 | -0.23741 | 0.21383 | 0.006371 | 0.61275 | 0.038448 | -0.17538 | -0.25143 | 0.16947 | 122.3334 | -0.007031 | 122.6314 | 122.574 | 0.24058 | 0.11905 | -0.33561 | 122.7465 | 122.4887 | 122.9096 | 122.2471 | -122.5263 | 122.7331 | 122.8592 | 122.4046 | 122.5895 | -0.40678
1159.4219 | 122.7356 | -122.6303 | 0.19226 | 1.4211e-13 | -0.019192 | -0.0013525 | 0.062272 | -0.012627 | 0.059667 | 0.0056466 | 0.008129 | 0.0083539 | -0.0068837 | 0.038126 | 0.0045915 | -121.9672 | -0.32825 | -122.5461 | 0.18032 | -0.09122 | 0.37548 | -122.357 | 0.06515 | 0.023253 | 0.003172 | 0.16692 | 0.28842 | -0.16624 | -0.23283 | 0.27334 | -0.011938 | 0.6631 | 0.084222 | -0.18911 | -0.28348 | 0.18321 | 122.3975 | -0.02534 | 122.6955 | 122.6335 | 0.236 | 0.096162 | -0.3585 | 122.8106 | 122.5391 | 123.0058 | 122.3021 | -122.5492 | 122.7972 | 122.9187 | 122.4641 | 122.6536 | -0.42509
1161.1719 | 122.8226 | -122.3373 | 0.36163 | 1.4211e-13 | -0.019192 | -0.0011389 | 0.062699 | -0.012414 | 0.059667 | -0.0019839 | 0.008129 | 0.0077131 | -0.0062429 | 0.037912 | 0.0048051 | -121.7337 | -0.32367 | -122.3034 | 0.3543 | -0.00422 | 0.5632 | -122.5264 | 0.078886 | 0.041567 | 0.01233 | 0.18066 | 0.29758 | -0.17081 | -0.22825 | -0.18905 | -0.007332 | 0.60363 | 0.033902 | 0.22295 | -0.36585 | 0.20156 | 122.1091 | -0.18098 | 122.4162 | 122.3497 | 0.24058 | -0.064053 | -0.53245 | 122.6916 | 122.3331 | 122.9005 | 122.0137 | -122.888 | 122.518 | 122.6349 | 122.1665 | 122.3789 | -0.58988
1162.8594 | 122.6898 | -122.3511 | 0.36621 | 1.4211e-13 | -0.018765 | -0.00092531 | 0.063126 | -0.012414 | 0.05924 | 0.0056466 | 0.0079152 | 0.0079267 | -0.0068837 | 0.038126 | 0.0045915 | -121.7429 | -0.33283 | -122.3126 | 0.31767 | -0.017957 | 0.52657 | -122.5813 | 0.06515 | 0.027831 | 0.021487 | 0.1715 | 0.29758 | -0.17081 | -0.22367 | -0.23027 | -0.048537 | 0.60821 | 0.038478 | 0.26874 | -0.38417 | 0.16036 | 122.1274 | -0.19471 | 122.4162 | 122.3726 | 0.24516 | -0.068631 | -0.53703 | 122.6687 | 122.3331 | 122.8776 | 122.0182 | -122.9476 | 122.5226 | 122.6487 | 122.1803 | 122.3789 | -0.58988
1164.5938 | 122.6212 | -122.2366 | 0.42114 | 1.4211e-13 | -0.019192 | -0.00092531 | 0.062699 | -0.012414 | 0.059667 | -0.0019839 | 0.0077016 | 0.0079267 | -0.0068837 | 0.038126 | 0.0041641 | -121.6559 | -0.33283 | -122.2256 | 0.36346 | 0.000359 | 0.59067 | -122.4943 | 0.06515 | 0.036989 | 0.016908 | 0.1715 | 0.30674 | -0.17539 | -0.22367 | -0.25771 | -0.057685 | 0.58076 | 0.011025 | 0.26873 | -0.42078 | 0.16953 | 122.013 | -0.24964 | 122.3018 | 122.2535 | 0.24058 | -0.11441 | -0.59654 | 122.6001 | 122.237 | 122.8273 | 121.9038 | -122.9155 | 122.4081 | 122.5434 | 122.0612 | 122.2736 | -0.64482
1166.3438 | 122.6303 | -121.5454 | 0.92468 | 1.4211e-13 | -0.019406 | -0.0013525 | 0.062058 | -0.011986 | 0.05924 | 0.013277 | 0.0077016 | 0.0081403 | -0.0068837 | 0.038126 | 0.0048051 | -121.0241 | -0.33741 | -121.5801 | 0.83503 | 0.58188 | 1.0531 | -121.8624 | 0.10636 | 0.078197 | 0.044381 | 0.20813 | 0.33421 | -0.17081 | -0.18704 | -0.31704 | -0.089651 | 0.52135 | -0.034661 | 0.28238 | -0.3428 | 0.12842 | 121.3584 | -0.71656 | 121.6518 | 121.5898 | 0.23142 | -0.59047 | -1.0955 | 122.3804 | 122.1273 | 122.5985 | 121.208 | -122.7871 | 121.7535 | 121.8796 | 121.3746 | 121.6236 | -1.1117
1168.0312 | 122.612 | -44.1788 | 78.154 | 1.4211e-13 | -0.018765 | -0.00028411 | 0.062913 | -0.012414 | 0.058599 | 0.0056466 | 0.0079152 | 0.0079267 | -0.0068837 | 0.037698 | 0.0045915 | -43.9332 | 0.17081 | -44.056 | 78.5852 | 78.5564 | 78.6101 | -44.1444 | 0.010205 | -0.013377 | -0.042615 | 0.11656 | 0.24264 | -0.17539 | -0.29236 | 0.034408 | 0.43122 | 0.24561 | 0.12273 | 0.088318 | 0.4024 | 0.45606 | 43.8864 | -78.0374 | 44.189 | 44.1362 | 0.24974 | -77.9114 | -78.3294 | 122.764 | 122.7352 | 122.7888 | 44.3496 | -122.2984 | 44.2953 | 44.4214 | 44.0034 | 44.1654 | -78.4463
1169.7812 | 122.6532 | -3.9139 | 118.689 | 1.4211e-13 | -0.018124 | -0.00028411 | 0.063767 | -0.012627 | 0.058385 | 0.013277 | 0.0077016 | 0.0079267 | -0.0068837 | 0.038126 | 0.0045915 | -3.6754 | 0.39975 | -3.758 | 118.8613 | 118.3381 | 118.5584 | -3.5064 | 0.001048 | -0.040849 | -0.070087 | 0.07993 | 0.21974 | -0.17081 | -0.31525 | 0.40747 | 0.17233 | 0.23848 | 0.15586 | -0.25161 | -0.35088 | -0.1306 | 3.5986 | -118.609 | 3.9149 | 3.8438 | 0.24516 | -118.4692 | -118.8598 | 122.7752 | 122.252 | 122.4722 | 4.3136 | -122.1954 | 3.9938 | 4.1336 | 3.7431 | 3.873 | -119.0042
1171.5312 | 122.6761 | -10.0204 | 112.5137 | 1.4211e-13 | -0.018337 | -0.00049791 | 0.06334 | -0.012414 | 0.058172 | 0.013277 | 0.0079152 | 0.0081403 | -0.0066701 | 0.037912 | 0.0048051 | -9.9982 | 0.32649 | -10.1264 | 112.5981 | 112.097 | 112.3544 | -9.72 | 0.001048 | -0.036271 | -0.070087 | 0.093665 | 0.21974 | -0.17081 | -0.30609 | 0.30044 | 0.084325 | 0.022295 | -0.10596 | -0.4064 | -0.41672 | -0.15938 | 9.7144 | -112.4201 | 10.0215 | 9.9504 | 0.236 | -112.294 | -112.6845 | 122.6185 | 122.1175 | 122.3748 | 10.3469 | -122.2337 | 10.1141 | 10.2402 | 9.8496 | 9.9842 | -112.8198
1173.2656 | 122.7036 | -9.7549 | 112.793 | 1.4211e-13 | -0.018337 | -0.00028411 | 0.063554 | -0.012627 | 0.058172 | -0.0019839 | 0.0079152 | 0.0083539 | -0.0064565 | 0.037912 | 0.0045915 | -9.7326 | 0.30817 | -9.8151 | 112.8728 | 112.3855 | 112.597 | -9.4773 | -0.003531 | -0.031692 | -0.070087 | 0.093665 | 0.21516 | -0.17081 | -0.31525 | 0.27762 | 0.079792 | 0.022339 | -0.060142 | -0.33776 | -0.40749 | -0.19595 | 9.4397 | -112.6993 | 9.7514 | 9.6849 | 0.24516 | -112.5778 | -112.9638 | 122.6277 | 122.1404 | 122.352 | 10.0631 | -122.2703 | 9.8486 | 9.9701 | 9.5841 | 9.7233 | -113.1082
1175.0156 | 122.731 | -10.144 | 112.4268 | 1.4211e-13 | -0.018124 | -7.051e-05 | 0.06334 | -0.012841 | 0.058172 | 0.0056466 | 0.0077016 | 0.0079267 | -0.0070975 | 0.037912 | 0.0043777 | -10.0668 | 0.28528 | -10.1493 | 112.566 | 112.0695 | 112.3086 | -9.775 | 0.001048 | -0.036271 | -0.06093 | 0.089087 | 0.21516 | -0.17539 | -0.30609 | 0.36909 | 0.13925 | 0.077216 | -0.005258 | -0.37434 | -0.35722 | -0.11819 | 9.838 | -112.3377 | 10.1451 | 10.0831 | 0.24516 | -112.2116 | -112.6022 | 122.7101 | 122.2136 | 122.4526 | 10.4293 | -122.2017 | 10.2331 | 10.3592 | 9.9687 | 10.1078 | -112.7329
1176.7656 | 122.6074 | -13.1882 | 109.4696 | 1.4211e-13 | -0.018124 | -7.051e-05 | 0.063554 | -0.013055 | 0.058385 | 0.0056466 | 0.0077016 | 0.0081403 | -0.0064565 | 0.037698 | 0.0043777 | -13.2305 | 0.21202 | -13.3175 | 109.4481 | 108.9604 | 109.2043 | -12.9344 | 0.001048 | -0.031692 | -0.065509 | 0.093665 | 0.21974 | -0.17081 | -0.31067 | 0.25376 | -0.021477 | -0.042322 | -0.1293 | -0.38306 | -0.50916 | -0.26533 | 12.8775 | -109.3759 | 13.1892 | 13.1227 | 0.24516 | -109.2499 | -109.6404 | 122.6363 | 122.1486 | 122.3924 | 13.4002 | -122.404 | 13.2818 | 13.4079 | 13.0174 | 13.1565 | -109.7803
1178.4375 | 122.7127 | -13.4537 | 109.1537 | 1.4211e-13 | -0.018337 | -7.051e-05 | 0.06334 | -0.012627 | 0.058385 | 0.0056466 | 0.0079152 | 0.0085677 | -0.0068837 | 0.038126 | 0.0045915 | -13.5372 | 0.22118 | -13.6196 | 109.146 | 108.6628 | 108.8929 | -13.2 | 0.005626 | -0.031692 | -0.065509 | 0.098244 | 0.22432 | -0.16624 | -0.31525 | 0.25368 | -0.007794 | -0.083571 | -0.16596 | -0.41965 | -0.49093 | -0.26081 | 13.1384 | -109.0555 | 13.4593 | 13.3882 | 0.24974 | -108.9294 | -109.32 | 122.5996 | 122.1165 | 122.3466 | 13.6749 | -122.3537 | 13.5519 | 13.678 | 13.2874 | 13.422 | -109.469
1180.1719 | 122.699 | -11.3342 | 111.2869 | 1.4211e-13 | -0.018337 | -7.051e-05 | 0.06334 | -0.012414 | 0.058599 | -0.0019839 | 0.008129 | 0.0083539 | -0.0068837 | 0.037912 | 0.0043777 | -11.4083 | 0.23034 | -11.4862 | 111.2749 | 110.7829 | 111.0128 | -11.0937 | 0.001048 | -0.040849 | -0.070087 | 0.093665 | 0.21974 | -0.16166 | -0.31525 | 0.24054 | -0.012022 | -0.074066 | -0.15193 | -0.39247 | -0.50407 | -0.2741 | 11.019 | -111.1933 | 11.3353 | 11.2641 | 0.24516 | -111.0672 | -111.4486 | 122.6091 | 122.1171 | 122.3471 | 11.5646 | -122.3806 | 11.4279 | 11.554 | 11.1726 | 11.2934 | -111.6022
1181.9219 | 122.6395 | -11.1053 | 111.5799 | 1.4211e-13 | -0.018551 | -0.00028411 | 0.063554 | -0.012841 | 0.058599 | 0.0056466 | 0.0079152 | 0.0083539 | -0.0066701 | 0.037698 | 0.0045915 | -10.868 | 0.22576 | -10.9459 | 111.8106 | 111.3232 | 111.5485 | -10.5808 | -0.003531 | -0.031692 | -0.070087 | 0.098244 | 0.22432 | -0.16624 | -0.30609 | 0.5245 | 0.23068 | 0.2373 | 0.15943 | -0.36507 | -0.25672 | -0.031373 | 10.7993 | -111.4817 | 11.1018 | 11.0353 | 0.236 | -111.3556 | -111.7461 | 122.9159 | 122.4285 | 122.6539 | 11.3311 | -122.1607 | 11.2036 | 11.3297 | 10.9391 | 11.0737 | -111.886
1183.6719 | 122.6852 | -11.4304 | 111.2228 | 1.4211e-13 | -0.018337 | -7.051e-05 | 0.063554 | -0.013055 | 0.058599 | -0.0019839 | 0.0079152 | 0.0081403 | -0.0068837 | 0.037698 | 0.0045915 | -11.3808 | 0.22576 | -11.4541 | 111.3115 | 110.8103 | 111.0449 | -11.0571 | -0.003531 | -0.036271 | -0.070087 | 0.089087 | 0.21974 | -0.17539 | -0.31067 | 0.3733 | 0.088692 | 0.049534 | -0.023752 | -0.39706 | -0.41251 | -0.17796 | 11.1197 | -111.1338 | 11.4268 | 11.3603 | 0.24058 | -111.0031 | -111.3982 | 122.7419 | 122.2407 | 122.4752 | 11.6561 | -122.2799 | 11.5194 | 11.6501 | 11.255 | 11.3941 | -111.5335
1185.3594 | 122.7676 | -11.3983 | 111.1862 | 1.4211e-13 | -0.018551 | -0.00071151 | 0.063554 | -0.013055 | 0.058385 | 0.0056466 | 0.008129 | 0.0081403 | -0.0062429 | 0.037912 | 0.0045915 | -11.3991 | 0.2166 | -11.477 | 111.2795 | 110.8012 | 111.0403 | -11.112 | -0.00811 | -0.031692 | -0.070087 | 0.093665 | 0.22432 | -0.16624 | -0.30609 | 0.28631 | 0.093264 | -0.000823 | -0.078687 | -0.365 | -0.38504 | -0.14592 | 11.0922 | -111.0926 | 11.3902 | 11.3282 | 0.236 | -110.9619 | -111.3525 | 122.6778 | 122.1995 | 122.4386 | 11.6149 | -122.2982 | 11.492 | 11.6226 | 11.2321 | 11.3666 | -111.4923
1187.1094 | 122.7036 | -11.0916 | 111.5616 | 1.4211e-13 | -0.018551 | -0.00049791 | 0.063554 | -0.012627 | 0.058172 | -0.0019839 | 0.007488 | 0.0079267 | -0.0066701 | 0.037912 | 0.0043777 | -11.0466 | 0.22118 | -11.1382 | 111.6503 | 111.14 | 111.3745 | -10.7457 | 0.001048 | -0.036271 | -0.065509 | 0.089087 | 0.22432 | -0.17997 | -0.31067 | 0.34593 | 0.088748 | 0.045012 | -0.046595 | -0.39252 | -0.42157 | -0.18705 | 10.7809 | -111.4725 | 11.0927 | 11.0261 | 0.24516 | -111.3373 | -111.7416 | 122.7419 | 122.2316 | 122.4661 | 11.3128 | -122.3073 | 11.1807 | 11.3159 | 10.9116 | 11.0553 | -111.8723
1188.8594 | 122.7219 | -8.1894 | 114.4638 | 1.4211e-13 | -0.018337 | -7.051e-05 | 0.063554 | -0.012841 | 0.058385 | 0.013277 | 0.0077016 | 0.0079267 | -0.0066701 | 0.038126 | 0.0043777 | -8.2675 | 0.24865 | -8.3409 | 114.3974 | 113.9057 | 114.1263 | -8.0121 | 0.001048 | -0.040849 | -0.070087 | 0.089087 | 0.21974 | -0.16624 | -0.31525 | 0.17732 | -0.066441 | -0.078129 | -0.15149 | -0.32881 | -0.55812 | -0.33753 | 7.8741 | -114.3747 | 8.1904 | 8.1193 | 0.24516 | -114.2441 | -114.63 | 122.5868 | 122.0951 | 122.3157 | 8.438 | -122.4759 | 8.2785 | 8.4091 | 8.0232 | 8.1485 | -114.7791
1190.6094 | 122.6715 | -7.8094 | 114.8804 | 1.4211e-13 | -0.018124 | -0.00028411 | 0.063767 | -0.012414 | 0.058385 | -0.0019839 | 0.0077016 | 0.0079267 | -0.0068837 | 0.037698 | 0.0045915 | -7.6861 | 0.23949 | -7.7549 | 114.9834 | 114.4826 | 114.7123 | -7.4626 | -0.003531 | -0.031692 | -0.074666 | 0.089087 | 0.21059 | -0.16624 | -0.31067 | 0.34685 | 0.10303 | 0.12338 | 0.054588 | -0.29226 | -0.39774 | -0.16803 | 7.4988 | -114.7913 | 7.8059 | 7.7348 | 0.236 | -114.6698 | -115.0466 | 122.7928 | 122.2921 | 122.5218 | 8.0489 | -122.343 | 7.8985 | 8.02 | 7.6432 | 7.7778 | -115.191
1192.3594 | 122.6944 | -8.2718 | 114.4363 | 1.4211e-13 | -0.018551 | -0.00028411 | 0.063767 | -0.012841 | 0.058385 | 0.0056466 | 0.0079152 | 0.0074993 | -0.0068837 | 0.038126 | 0.0045915 | -8.121 | 0.23949 | -8.1898 | 114.553 | 114.0522 | 114.2911 | -7.8518 | 0.001048 | -0.036271 | -0.070087 | 0.093665 | 0.22432 | -0.17081 | -0.30609 | 0.41998 | 0.11669 | 0.15078 | 0.081993 | -0.33799 | -0.38413 | -0.14523 | 7.9657 | -114.3427 | 8.2728 | 8.2017 | 0.236 | -114.212 | -114.6072 | 122.8248 | 122.324 | 122.5629 | 8.5113 | -122.2881 | 8.3655 | 8.4961 | 8.101 | 8.2355 | -114.7424
1194.0469 | 122.7631 | -8.1161 | 114.537 | 1.4211e-13 | -0.018551 | -0.00028411 | 0.06334 | -0.012627 | 0.058599 | 0.0056466 | 0.008129 | 0.0081403 | -0.0068837 | 0.038339 | 0.0043777 | -8.0249 | 0.23949 | -8.1028 | 114.6538 | 114.1484 | 114.4193 | -7.774 | 0.001048 | -0.031692 | -0.06093 | 0.089087 | 0.21974 | -0.17081 | -0.31983 | 0.34218 | 0.11671 | 0.091284 | 0.013341 | -0.32884 | -0.38868 | -0.11774 | 7.7963 | -114.448 | 8.1172 | 8.0552 | 0.2589 | -114.3173 | -114.7079 | 122.7699 | 122.2645 | 122.5355 | 8.3556 | -122.311 | 8.2052 | 8.3359 | 7.9453 | 8.0845 | -114.8569
1195.7969 | 122.7264 | -8.3176 | 114.3631 | 1.4211e-13 | -0.018337 | -0.00028411 | 0.063554 | -0.012841 | 0.058385 | -0.0019839 | 0.0077016 | 0.0081403 | -0.0070975 | 0.038339 | 0.0041641 | -8.176 | 0.22576 | -8.2493 | 114.5027 | 114.0064 | 114.2316 | -7.9296 | -0.012689 | -0.036271 | -0.070087 | 0.093665 | 0.22432 | -0.17997 | -0.31067 | 0.38792 | 0.13957 | 0.14161 | 0.068252 | -0.31966 | -0.35668 | -0.13151 | 8.0069 | -114.2694 | 8.3049 | 8.2475 | 0.24058 | -114.1388 | -114.5431 | 122.8202 | 122.324 | 122.5491 | 8.5433 | -122.2927 | 8.4112 | 8.5419 | 8.1376 | 8.2813 | -114.6738
1197.5 | 122.7859 | -8.2901 | 114.3539 | 1.4211e-13 | -0.018551 | -0.00028411 | 0.063126 | -0.012627 | 0.058172 | 0.0056466 | 0.0077016 | 0.0077131 | -0.0066701 | 0.038339 | 0.0045915 | -8.6292 | 0.23492 | -8.698 | 114.0494 | 113.5577 | 113.7966 | -8.3646 | -0.003531 | -0.036271 | -0.06093 | 0.089087 | 0.21974 | -0.16624 | -0.30609 | -0.074547 | -0.30454 | -0.33911 | -0.40789 | -0.33334 | -0.79626 | -0.55733 | 7.984 | -114.2649 | 8.2866 | 8.2292 | 0.24516 | -114.1342 | -114.5202 | 122.3395 | 121.8478 | 122.0867 | 8.525 | -122.7186 | 8.3792 | 8.5098 | 8.1239 | 8.2538 | -114.66
1199.2656 | 122.7951 | -8.5327 | 114.1251 | 1.4211e-13 | -0.018337 | -0.00049791 | 0.06334 | -0.012414 | 0.058385 | -0.0019839 | 0.008129 | 0.0079267 | -0.0064565 | 0.038126 | 0.0043777 | -8.5056 | 0.23034 | -8.5744 | 114.1776 | 113.6905 | 113.9202 | -8.2456 | 0.001048 | -0.031692 | -0.065509 | 0.093665 | 0.21974 | -0.17539 | -0.31983 | 0.28712 | 0.052541 | 0.027118 | -0.041657 | -0.32878 | -0.43458 | -0.20482 | 8.2129 | -114.0314 | 8.5338 | 8.4672 | 0.25432 | -113.9053 | -114.3005 | 122.7103 | 122.2232 | 122.453 | 8.7631 | -122.3707 | 8.6264 | 8.7525 | 8.3573 | 8.501 | -114.4449
1201.0156 | 122.7768 | -8.3496 | 114.2761 | 1.4211e-13 | -0.018124 | -0.00028411 | 0.063554 | -0.012627 | 0.058385 | 0.0056466 | 0.0079152 | 0.0079267 | -0.0070975 | 0.038126 | 0.0045915 | -8.295 | 0.23034 | -8.3775 | 114.3791 | 113.8919 | 114.1217 | -8.0395 | -0.003531 | -0.036271 | -0.074666 | 0.089087 | 0.21974 | -0.17539 | -0.31983 | 0.31006 | 0.10293 | 0.054618 | -0.027897 | -0.33796 | -0.38417 | -0.15443 | 8.0298 | -114.187 | 8.3461 | 8.2749 | 0.24516 | -114.0564 | -114.4515 | 122.7287 | 122.2416 | 122.4713 | 8.5799 | -122.3157 | 8.4387 | 8.5694 | 8.1742 | 8.3133 | -114.596
1202.7031 | 122.7036 | -8.1207 | 114.5828 | 1.4211e-13 | -0.018551 | -0.00028411 | 0.063767 | -0.012841 | 0.058599 | -0.0019839 | 0.0079152 | 0.0081403 | -0.0068837 | 0.037912 | 0.0043777 | -7.9928 | 0.23034 | -8.0799 | 114.6812 | 114.185 | 114.4193 | -7.7373 | -0.003531 | -0.031692 | -0.065509 | 0.084508 | 0.21974 | -0.17539 | -0.31067 | 0.38339 | 0.0984 | 0.12791 | 0.04081 | -0.34258 | -0.39782 | -0.16352 | 7.8101 | -114.4983 | 8.1172 | 8.0552 | 0.24516 | -114.3631 | -114.7582 | 122.802 | 122.3057 | 122.54 | 8.3511 | -122.3202 | 8.2052 | 8.3405 | 7.9453 | 8.089 | -114.8935
1204.4531 | 122.7859 | -8.02 | 114.6332 | 1.4211e-13 | -0.018124 | -0.00049791 | 0.06334 | -0.012841 | 0.058385 | -0.0019839 | 0.0077016 | 0.0079267 | -0.0068837 | 0.038126 | 0.0043777 | -7.947 | 0.23034 | -8.0158 | 114.7362 | 114.2491 | 114.4971 | -7.687 | 0.001048 | -0.036271 | -0.070087 | 0.089087 | 0.22432 | -0.17081 | -0.31067 | 0.33305 | 0.10299 | 0.072986 | 0.004198 | -0.32885 | -0.38407 | -0.13604 | 7.7093 | -114.5441 | 8.0211 | 7.9499 | 0.24058 | -114.4089 | -114.804 | 122.7562 | 122.2691 | 122.5172 | 8.2504 | -122.3201 | 8.1091 | 8.2443 | 7.8492 | 7.9837 | -114.9438
1206.1875 | 122.8134 | -8.0978 | 114.537 | 1.4211e-13 | -0.018337 | -0.00049791 | 0.063767 | -0.012627 | 0.058172 | -0.0019839 | 0.0079152 | 0.0077131 | -0.0070975 | 0.038126 | 0.0041641 | -8.0249 | 0.23034 | -8.0937 | 114.6583 | 114.1713 | 114.4193 | -7.7831 | -0.00811 | -0.036271 | -0.070087 | 0.089087 | 0.22432 | -0.17081 | -0.31525 | 0.31472 | 0.12129 | 0.072973 | 0.004186 | -0.31053 | -0.36579 | -0.11774 | 7.7826 | -114.448 | 8.0897 | 8.0278 | 0.24516 | -114.3127 | -114.7079 | 122.7562 | 122.2691 | 122.5171 | 8.3282 | -122.3202 | 8.1869 | 8.3222 | 7.927 | 8.0616 | -114.8523
1207.875 | 122.7219 | -9.3155 | 113.3652 | 1.4211e-13 | -0.018124 | -0.00049791 | 0.063554 | -0.012841 | 0.058385 | 0.0056466 | 0.0079152 | 0.0079267 | -0.0070975 | 0.038126 | 0.0045915 | -9.0046 | 0.2166 | -9.0963 | 113.6786 | 113.1914 | 113.4715 | -8.7355 | -0.00811 | -0.036271 | -0.074666 | 0.084508 | 0.2289 | -0.16624 | -0.31525 | 0.57995 | 0.31338 | 0.31085 | 0.21919 | -0.36076 | -0.1738 | 0.10636 | 9.0002 | -113.2807 | 9.3074 | 9.2408 | 0.24058 | -113.1363 | -113.5314 | 122.994 | 122.5069 | 122.787 | 9.5321 | -122.1007 | 9.4 | 9.5444 | 9.1493 | 9.2792 | -113.6804
1209.625 | 122.7356 | -8.1207 | 114.5187 | 1.4211e-13 | -0.018124 | -7.051e-05 | 0.063554 | -0.012414 | 0.058385 | 0.013277 | 0.008129 | 0.0081403 | -0.0070975 | 0.038339 | 0.0045915 | -7.9882 | 0.22576 | -8.0662 | 114.6904 | 114.2125 | 114.4651 | -7.7328 | -0.003531 | -0.036271 | -0.065509 | 0.089087 | 0.22432 | -0.17081 | -0.31525 | 0.38797 | 0.17164 | 0.13249 | 0.054545 | -0.33343 | -0.30626 | -0.053646 | 7.8055 | -114.4297 | 8.1172 | 8.0552 | 0.24974 | -114.2944 | -114.6896 | 122.8111 | 122.3332 | 122.5858 | 8.3465 | -122.2515 | 8.2098 | 8.3451 | 7.9499 | 8.0845 | -114.834
1211.3125 | 122.7081 | -8.4641 | 114.267 | 1.4211e-13 | -0.018551 | -0.00071151 | 0.063554 | -0.012627 | 0.058172 | -0.0019839 | 0.008129 | 0.0079267 | -0.0066701 | 0.038126 | 0.0043777 | -8.2721 | 0.23034 | -8.3455 | 114.4157 | 113.9332 | 114.1675 | -8.0029 | 0.001048 | -0.027113 | -0.065509 | 0.093665 | 0.21974 | -0.17081 | -0.31983 | 0.46114 | 0.14871 | 0.19195 | 0.11859 | -0.34255 | -0.33381 | -0.099485 | 8.1442 | -114.1733 | 8.4651 | 8.3985 | 0.25432 | -114.0472 | -114.4378 | 122.8797 | 122.3972 | 122.6315 | 8.6944 | -122.2699 | 8.5577 | 8.6838 | 8.2932 | 8.4369 | -114.5868
1213.0625 | 122.7493 | -8.5236 | 114.1571 | 1.4211e-13 | -0.018337 | -0.00028411 | 0.063554 | -0.012841 | 0.058172 | -0.0019839 | 0.0077016 | 0.0079267 | -0.0070975 | 0.038126 | 0.0041641 | -8.3591 | 0.23034 | -8.4279 | 114.3333 | 113.8507 | 114.0851 | -8.122 | -0.00811 | -0.040849 | -0.06093 | 0.089087 | 0.21974 | -0.16624 | -0.31983 | 0.4016 | 0.17616 | 0.16447 | 0.095693 | -0.3059 | -0.30636 | -0.072036 | 8.2037 | -114.068 | 8.5154 | 8.4626 | 0.2589 | -113.9374 | -114.3233 | 122.8568 | 122.3743 | 122.6086 | 8.7539 | -122.2791 | 8.6126 | 8.7433 | 8.3573 | 8.4827 | -114.4769
1214.7969 | 122.7539 | -9.407 | 113.2736 | 1.4211e-13 | -0.018337 | -0.00049791 | 0.063554 | -0.012841 | 0.058599 | -0.0019839 | 0.0079152 | 0.0081403 | -0.0066701 | 0.037912 | 0.0043777 | -9.403 | 0.21202 | -9.4717 | 113.3077 | 112.8113 | 113.0549 | -9.1202 | 0.001048 | -0.031692 | -0.065509 | 0.07993 | 0.22432 | -0.16624 | -0.31067 | 0.28687 | 0.034087 | 0.004082 | -0.064672 | -0.35154 | -0.4623 | -0.21874 | 9.0964 | -113.1937 | 9.4081 | 9.3415 | 0.24516 | -113.0493 | -113.4399 | 122.7148 | 122.2184 | 122.4619 | 9.6191 | -122.3938 | 9.487 | 9.6314 | 9.2408 | 9.3754 | -113.5843
1216.5 | 122.6852 | -8.7662 | 113.9557 | 1.4211e-13 | -0.018765 | 0.00014309 | 0.063126 | -0.012627 | 0.058172 | -0.0019839 | 0.0079152 | 0.0081403 | -0.0070975 | 0.037912 | 0.0045915 | -8.881 | 0.22576 | -8.9544 | 113.8251 | 113.3287 | 113.5814 | -8.6165 | 0.001048 | -0.036271 | -0.065509 | 0.089087 | 0.22432 | -0.16624 | -0.31067 | 0.14969 | -0.13062 | -0.11485 | -0.1882 | -0.33788 | -0.62695 | -0.37427 | 8.4555 | -113.8666 | 8.7672 | 8.7007 | 0.24516 | -113.7314 | -114.1219 | 122.5912 | 122.0949 | 122.3476 | 8.9919 | -122.5722 | 8.8553 | 8.9905 | 8.5999 | 8.7299 | -114.2664
1218.25 | 122.6669 | -8.6609 | 114.0747 | 1.4211e-13 | -0.018337 | -0.00028411 | 0.063554 | -0.012841 | 0.058385 | -0.0019839 | 0.0079152 | 0.0079267 | -0.0068837 | 0.037912 | 0.0045915 | -8.5697 | 0.26697 | -8.6888 | 114.1227 | 113.6355 | 113.8745 | -8.3051 | 0.005626 | -0.040849 | -0.065509 | 0.089087 | 0.2289 | -0.16624 | -0.31067 | 0.35577 | 0.047954 | 0.091194 | -0.02794 | -0.38371 | -0.43918 | -0.20025 | 8.3502 | -113.9856 | 8.6665 | 8.5954 | 0.24516 | -113.8458 | -114.2409 | 122.7835 | 122.2964 | 122.5353 | 8.9279 | -122.3798 | 8.75 | 8.8898 | 8.4947 | 8.62 | -114.3854
1220 | 122.7631 | -8.5419 | 114.1571 | 1.4211e-13 | -0.018337 | -0.00049791 | 0.063767 | -0.012627 | 0.057958 | 0.013277 | 0.0079152 | 0.0081403 | -0.0068837 | 0.038339 | 0.0043777 | -8.4598 | 0.23492 | -8.579 | 114.2417 | 113.7546 | 113.9981 | -8.1861 | -0.00811 | -0.031692 | -0.074666 | 0.089087 | 0.22432 | -0.17081 | -0.31525 | 0.3558 | 0.084595 | 0.082057 | -0.037081 | -0.39288 | -0.40252 | -0.15903 | 8.2266 | -114.068 | 8.5338 | 8.4672 | 0.24058 | -113.9328 | -114.3279 | 122.7836 | 122.2965 | 122.5399 | 8.7768 | -122.3432 | 8.631 | 8.7662 | 8.3711 | 8.5102 | -114.4724
1221.7656 | 122.6395 | -8.5098 | 114.2624 | 1.4211e-13 | -0.018551 | -0.00028411 | 0.063554 | -0.012627 | 0.058385 | -0.0019839 | 0.007488 | 0.0081403 | -0.0068837 | 0.037912 | 0.0043777 | -8.3545 | 0.23492 | -8.437 | 114.3378 | 113.8553 | 114.108 | -8.0808 | -0.00811 | -0.031692 | -0.065509 | 0.089087 | 0.22432 | -0.17081 | -0.31067 | 0.42907 | 0.075455 | 0.15532 | 0.072803 | -0.35627 | -0.40707 | -0.15443 | 8.1992 | -114.1733 | 8.5017 | 8.4443 | 0.24516 | -114.0381 | -114.4332 | 122.8477 | 122.3651 | 122.6178 | 8.7447 | -122.3431 | 8.5989 | 8.7341 | 8.339 | 8.4781 | -114.5731
1223.4531 | 122.7036 | -8.6334 | 114.0747 | 1.4211e-13 | -0.018551 | -7.051e-05 | 0.063554 | -0.012627 | 0.058599 | 0.013277 | 0.0079152 | 0.0077131 | -0.0070975 | 0.038339 | 0.0041641 | -8.6109 | 0.23034 | -8.6888 | 114.086 | 113.6035 | 113.8607 | -8.3463 | -0.003531 | -0.040849 | -0.070087 | 0.098244 | 0.22432 | -0.17539 | -0.31525 | 0.28709 | 0.011327 | 0.022523 | -0.055406 | -0.3425 | -0.47123 | -0.21399 | 8.3182 | -113.9765 | 8.6299 | 8.5633 | 0.24516 | -113.8504 | -114.2501 | 122.7195 | 122.2369 | 122.4941 | 8.8638 | -122.421 | 8.7317 | 8.8577 | 8.458 | 8.5926 | -114.39
1225.2031 | 122.7905 | -8.6105 | 114.0472 | 1.4211e-13 | -0.018337 | -0.00049791 | 0.063767 | -0.012841 | 0.058172 | 0.0056466 | 0.0077016 | 0.0077131 | -0.0070975 | 0.038339 | 0.0043777 | -8.5651 | 0.22576 | -8.6339 | 114.1364 | 113.6538 | 113.8882 | -8.2822 | 0.001048 | -0.036271 | -0.06093 | 0.093665 | 0.21974 | -0.17997 | -0.32441 | 0.32831 | 0.089155 | 0.045419 | -0.023355 | -0.35166 | -0.3934 | -0.15905 | 8.2861 | -113.9536 | 8.6116 | 8.5496 | 0.26348 | -113.8275 | -114.2272 | 122.7469 | 122.2644 | 122.4987 | 8.8363 | -122.3295 | 8.7042 | 8.8303 | 8.4306 | 8.5743 | -114.3716
1226.9062 | 122.644 | -8.7341 | 114.0152 | 1.4211e-13 | -0.018124 | -0.00028411 | 0.063554 | -0.013055 | 0.058599 | 0.013277 | 0.0079152 | 0.0083539 | -0.0066701 | 0.038126 | 0.0043777 | -8.6567 | 0.23492 | -8.7346 | 114.0448 | 113.5531 | 113.792 | -8.3784 | 0.005626 | -0.036271 | -0.074666 | 0.098244 | 0.22432 | -0.17539 | -0.31067 | 0.35575 | 0.029631 | 0.077447 | -0.000481 | -0.35623 | -0.46209 | -0.22316 | 8.4235 | -113.917 | 8.7398 | 8.6595 | 0.236 | -113.7909 | -114.1906 | 122.779 | 122.2872 | 122.5262 | 8.969 | -122.3936 | 8.8324 | 8.9585 | 8.5587 | 8.6979 | -114.3259
1228.6406 | 122.699 | -8.6334 | 114.0839 | 1.4211e-13 | -0.018124 | -0.00028411 | 0.063554 | -0.013055 | 0.058385 | -0.0019839 | 0.0077016 | 0.0077131 | -0.0070975 | 0.038126 | 0.0045915 | -8.6201 | 0.23492 | -8.7117 | 114.0677 | 113.576 | 113.8195 | -8.3555 | -0.003531 | -0.036271 | -0.06093 | 0.089087 | 0.21974 | -0.16624 | -0.31067 | 0.27793 | -0.016141 | 0.013366 | -0.078298 | -0.35623 | -0.50786 | -0.26435 | 8.3228 | -113.9948 | 8.6299 | 8.5725 | 0.24974 | -113.8641 | -114.2501 | 122.7011 | 122.2094 | 122.4529 | 8.8683 | -122.4394 | 8.7225 | 8.8532 | 8.4672 | 8.5972 | -114.3945
1230.3906 | 122.7448 | -8.7708 | 113.9008 | 1.4211e-13 | -0.018765 | -0.00028411 | 0.063767 | -0.012627 | 0.058172 | 0.0056466 | 0.0077016 | 0.0077131 | -0.0073111 | 0.038553 | 0.0043777 | -8.7299 | 0.21202 | -8.8033 | 113.9762 | 113.4798 | 113.7463 | -8.4242 | -0.003531 | -0.031692 | -0.074666 | 0.093665 | 0.2289 | -0.16624 | -0.31525 | 0.34658 | 0.075396 | 0.040814 | -0.032534 | -0.37911 | -0.42091 | -0.15451 | 8.4555 | -113.8071 | 8.7672 | 8.6961 | 0.24058 | -113.6719 | -114.067 | 122.7469 | 122.2506 | 122.517 | 8.9828 | -122.3249 | 8.8644 | 8.9997 | 8.6045 | 8.7391 | -114.216
1232.0938 | 122.7585 | -8.5922 | 114.0701 | 1.4211e-13 | -0.018765 | -0.00049791 | 0.063767 | -0.012841 | 0.058385 | 0.013277 | 0.007488 | 0.0081403 | -0.0064565 | 0.037912 | 0.0045915 | -8.5148 | 0.23034 | -8.5881 | 114.1959 | 113.7088 | 113.9569 | -8.2227 | -0.003531 | -0.031692 | -0.065509 | 0.098244 | 0.21516 | -0.17539 | -0.31525 | 0.36952 | 0.12579 | 0.07747 | 0.004117 | -0.36541 | -0.36134 | -0.11326 | 8.277 | -113.9719 | 8.5887 | 8.5267 | 0.24974 | -113.855 | -114.2455 | 122.7881 | 122.301 | 122.5491 | 8.8226 | -122.2928 | 8.6905 | 8.8074 | 8.4168 | 8.5605 | -114.3854
1233.8438 | 122.6761 | -8.9584 | 113.7863 | 1.4211e-13 | -0.018765 | -0.00049791 | 0.063767 | -0.012841 | 0.058172 | -0.0019839 | 0.0079152 | 0.0083539 | -0.0070975 | 0.038339 | 0.0043777 | -8.7986 | 0.23034 | -8.8811 | 113.9121 | 113.4157 | 113.673 | -8.5112 | 0.005626 | -0.031692 | -0.070087 | 0.093665 | 0.21516 | -0.16624 | -0.31525 | 0.44726 | 0.12574 | 0.15982 | 0.077318 | -0.36994 | -0.37058 | -0.11332 | 8.6432 | -113.6927 | 8.9641 | 8.8883 | 0.24516 | -113.5712 | -113.9526 | 122.8705 | 122.3742 | 122.6314 | 9.1888 | -122.2975 | 9.0521 | 9.1736 | 8.7922 | 8.9267 | -114.1016
1235.5156 | 122.7493 | -8.757 | 113.9099 | 1.4211e-13 | -0.018551 | -7.051e-05 | 0.063554 | -0.012627 | 0.058172 | -0.0019839 | 0.0077016 | 0.0083539 | -0.0068837 | 0.037912 | 0.0045915 | -8.7666 | 0.23034 | -8.8445 | 113.9395 | 113.4661 | 113.6959 | -8.4791 | -0.003531 | -0.036271 | -0.065509 | 0.084508 | 0.21516 | -0.17081 | -0.31067 | 0.2779 | 0.029614 | -0.009546 | -0.087472 | -0.36537 | -0.4438 | -0.21403 | 8.4463 | -113.8254 | 8.7535 | 8.6915 | 0.24516 | -113.6947 | -114.0807 | 122.6965 | 122.2231 | 122.4529 | 8.9874 | -122.389 | 8.8415 | 8.9722 | 8.5862 | 8.7207 | -114.2206
1237.2656 | 122.7997 | -8.8348 | 113.8092 | 1.4211e-13 | -0.018765 | -0.00028411 | 0.06334 | -0.012414 | 0.057958 | -0.0019839 | 0.008129 | 0.0077131 | -0.0066701 | 0.038126 | 0.0043777 | -8.849 | 0.22118 | -8.9315 | 113.8525 | 113.37 | 113.6409 | -8.5753 | -0.003531 | -0.036271 | -0.065509 | 0.089087 | 0.22432 | -0.17539 | -0.31067 | 0.25956 | 0.043332 | -0.014137 | -0.096639 | -0.3562 | -0.43925 | -0.16826 | 8.5242 | -113.7201 | 8.8313 | 8.7693 | 0.24516 | -113.5849 | -113.9846 | 122.6874 | 122.2048 | 122.4758 | 9.056 | -122.3845 | 8.9239 | 9.0592 | 8.6594 | 8.7986 | -114.1199
1239.0156 | 122.7585 | -9.3475 | 113.3286 | 1.4211e-13 | -0.018765 | -0.00028411 | 0.063767 | -0.012627 | 0.058172 | 0.013277 | 0.0077016 | 0.0079267 | -0.0068837 | 0.038339 | 0.0043777 | -9.2885 | 0.22118 | -9.3756 | 113.4176 | 112.9395 | 113.1831 | -9.0652 | -0.00811 | -0.027113 | -0.065509 | 0.098244 | 0.22432 | -0.17539 | -0.31525 | 0.28231 | 0.089038 | 0.059033 | -0.028037 | -0.31035 | -0.38902 | -0.14547 | 9.0323 | -113.2303 | 9.3394 | 9.282 | 0.24974 | -113.1042 | -113.5039 | 122.7651 | 122.2871 | 122.5306 | 9.5687 | -122.3938 | 9.4458 | 9.5719 | 9.1721 | 9.3204 | -113.6438
1240.6875 | 122.7448 | -9.2331 | 113.4613 | 1.4211e-13 | -0.018551 | -0.00071151 | 0.063554 | -0.012841 | 0.058385 | 0.020908 | 0.0077016 | 0.0079267 | -0.0068837 | 0.037912 | 0.0045915 | -9.1786 | 0.23034 | -9.2657 | 113.5366 | 113.0494 | 113.2975 | -8.8821 | -0.00811 | -0.036271 | -0.070087 | 0.098244 | 0.2289 | -0.17539 | -0.30609 | 0.35103 | 0.075324 | 0.054473 | -0.0326 | -0.38363 | -0.41188 | -0.16375 | 8.927 | -113.3631 | 9.225 | 9.163 | 0.236 | -113.2324 | -113.6367 | 122.7697 | 122.2825 | 122.5306 | 9.4634 | -122.3434 | 9.3313 | 9.462 | 9.0577 | 9.1968 | -113.7674
1242.4375 | 122.7768 | -8.8577 | 113.8138 | 1.4211e-13 | -0.018337 | -0.00049791 | 0.063554 | -0.012841 | 0.057958 | 0.013277 | 0.0077016 | 0.0077131 | -0.0070975 | 0.038339 | 0.0041641 | -8.7986 | 0.22576 | -8.8857 | 113.9075 | 113.4203 | 113.6638 | -8.5341 | -0.003531 | -0.036271 | -0.065509 | 0.093665 | 0.21974 | -0.17539 | -0.31525 | 0.32366 | 0.093695 | 0.059113 | -0.027968 | -0.35163 | -0.39346 | -0.14995 | 8.5425 | -113.7201 | 8.8542 | 8.7922 | 0.24974 | -113.594 | -113.9892 | 122.7652 | 122.278 | 122.5216 | 9.0835 | -122.3479 | 8.9514 | 9.0775 | 8.6823 | 8.8215 | -114.129
1244.125 | 122.7814 | -9.0225 | 113.5803 | 1.4211e-13 | -0.018551 | -0.00028411 | 0.063981 | -0.012841 | 0.058599 | -0.0019839 | 0.0077016 | 0.0079267 | -0.0068837 | 0.037912 | 0.0041641 | -8.936 | 0.23034 | -9.0322 | 113.761 | 113.2784 | 113.5219 | -8.6669 | 0.001048 | -0.036271 | -0.074666 | 0.093665 | 0.21516 | -0.17081 | -0.30151 | 0.35567 | 0.18065 | 0.086556 | -0.009678 | -0.36534 | -0.30195 | -0.058422 | 8.721 | -113.4867 | 9.0236 | 8.9479 | 0.22685 | -113.3652 | -113.7511 | 122.7835 | 122.3009 | 122.5444 | 9.2529 | -122.2472 | 9.1162 | 9.2377 | 8.8517 | 8.9863 | -113.8818
1245.875 | 122.7951 | -8.9218 | 113.7039 | 1.4211e-13 | -0.018337 | -0.00049791 | 0.063767 | -0.012841 | 0.057958 | 0.0056466 | 0.0077016 | 0.0077131 | -0.0070975 | 0.038339 | 0.0041641 | -8.8948 | 0.23034 | -8.9773 | 113.8113 | 113.3196 | 113.5814 | -8.589 | 0.001048 | -0.027113 | -0.070087 | 0.089087 | 0.21516 | -0.17081 | -0.31525 | 0.3328 | 0.10741 | 0.027054 | -0.055447 | -0.38825 | -0.38433 | -0.1225 | 8.6066 | -113.6148 | 8.9229 | 8.8517 | 0.24516 | -113.4888 | -113.8747 | 122.7331 | 122.2414 | 122.5032 | 9.1522 | -122.2929 | 9.0109 | 9.137 | 8.751 | 8.8947 | -114.0192
1247.6406 | 122.7859 | -8.9722 | 113.6765 | 1.4211e-13 | -0.018337 | -0.00028411 | 0.063554 | -0.013055 | 0.058385 | -0.0096144 | 0.0077016 | 0.0074993 | -0.0070975 | 0.037912 | 0.0041641 | -8.881 | 0.22576 | -8.9681 | 113.8251 | 113.3425 | 113.5906 | -8.6119 | 0.001048 | -0.031692 | -0.065509 | 0.098244 | 0.22432 | -0.17081 | -0.31067 | 0.36026 | 0.14861 | 0.091143 | 0.004064 | -0.35619 | -0.33397 | -0.085874 | 8.6615 | -113.5782 | 8.9732 | 8.9067 | 0.24516 | -113.4521 | -113.8473 | 122.7972 | 122.3146 | 122.5627 | 9.1979 | -122.2884 | 9.0704 | 9.1965 | 8.8014 | 8.9405 | -113.9871
1249.4062 | 122.7631 | -8.9172 | 113.7451 | 1.4211e-13 | -0.018551 | -0.00028411 | 0.063981 | -0.012627 | 0.057958 | 0.013277 | 0.0079152 | 0.0077131 | -0.0068837 | 0.038126 | 0.0043777 | -8.8581 | 0.23034 | -8.9498 | 113.8434 | 113.3608 | 113.6089 | -8.5844 | -0.00811 | -0.036271 | -0.070087 | 0.089087 | 0.21974 | -0.17539 | -0.30609 | 0.3328 | 0.098263 | 0.059103 | -0.032555 | -0.36535 | -0.38432 | -0.13622 | 8.6111 | -113.656 | 8.9091 | 8.8471 | 0.236 | -113.5254 | -113.9205 | 122.7606 | 122.278 | 122.5261 | 9.1476 | -122.3296 | 9.0063 | 9.137 | 8.7418 | 8.881 | -114.0512
1251.1562 | 122.7905 | -8.8394 | 113.8046 | 1.4211e-13 | -0.018551 | -0.00071151 | 0.063554 | -0.013055 | 0.058172 | 0.0056466 | 0.008129 | 0.0083539 | -0.0066701 | 0.038339 | 0.0043777 | -8.8169 | 0.22576 | -8.9132 | 113.88 | 113.3928 | 113.6409 | -8.5524 | 0.001048 | -0.031692 | -0.065509 | 0.089087 | 0.22432 | -0.16624 | -0.30609 | 0.28703 | 0.075381 | 0.02249 | -0.073748 | -0.36078 | -0.41178 | -0.16368 | 8.5333 | -113.7155 | 8.8405 | 8.7739 | 0.24058 | -113.5803 | -113.9709 | 122.7194 | 122.2323 | 122.4804 | 9.0652 | -122.357 | 8.9285 | 9.0637 | 8.6732 | 8.8077 | -114.1107
1252.9062 | 122.7127 | -8.8303 | 113.9145 | 1.4211e-13 | -0.018765 | -0.00028411 | 0.063767 | -0.012841 | 0.058172 | 0.0056466 | 0.0077016 | 0.0079267 | -0.0070975 | 0.038553 | 0.0041641 | -8.6979 | 0.22576 | -8.7896 | 114.0036 | 113.5211 | 113.7554 | -8.4288 | -0.003531 | -0.031692 | -0.070087 | 0.093665 | 0.22432 | -0.16624 | -0.31525 | 0.40151 | 0.089133 | 0.13237 | 0.04071 | -0.3608 | -0.39343 | -0.15908 | 8.515 | -113.8208 | 8.8267 | 8.7602 | 0.24516 | -113.6902 | -114.0807 | 122.8339 | 122.3513 | 122.5857 | 9.056 | -122.3432 | 8.9239 | 9.0546 | 8.664 | 8.7986 | -114.2297
1254.6562 | 122.7997 | -8.8577 | 113.7588 | 1.4211e-13 | -0.018551 | -0.00049791 | 0.06334 | -0.012627 | 0.058599 | -0.0019839 | 0.0079152 | 0.0079267 | -0.0066701 | 0.038553 | 0.0039505 | -8.8536 | 0.22118 | -8.9452 | 113.8571 | 113.37 | 113.6135 | -8.5661 | -0.00811 | -0.031692 | -0.070087 | 0.093665 | 0.2289 | -0.17539 | -0.31067 | 0.29161 | 0.098265 | 0.004172 | -0.087486 | -0.37909 | -0.3889 | -0.14538 | 8.5471 | -113.6652 | 8.8496 | 8.7876 | 0.24058 | -113.5299 | -113.9342 | 122.7148 | 122.2277 | 122.4712 | 9.0789 | -122.325 | 8.9514 | 9.0866 | 8.6823 | 8.826 | -114.0695
1256.3438 | 122.7127 | -8.7753 | 113.942 | 1.4211e-13 | -0.018765 | -0.00028411 | 0.06334 | -0.012841 | 0.057958 | 0.013277 | 0.0079152 | 0.0081403 | -0.0073111 | 0.038126 | 0.0041641 | -8.6842 | 0.22576 | -8.7758 | 114.0082 | 113.5302 | 113.7783 | -8.4013 | 0.001048 | -0.040849 | -0.065509 | 0.089087 | 0.22432 | -0.17539 | -0.31983 | 0.37405 | 0.066246 | 0.091176 | -0.000487 | -0.37454 | -0.41174 | -0.16365 | 8.4555 | -113.8529 | 8.7764 | 8.7098 | 0.25432 | -113.7176 | -114.1173 | 122.7835 | 122.3055 | 122.5536 | 9.0011 | -122.3432 | 8.8644 | 8.9997 | 8.5999 | 8.7345 | -114.2618
1258.0781 | 122.6624 | -8.8486 | 113.8824 | 1.4211e-13 | -0.018337 | -0.00028411 | 0.063767 | -0.013055 | 0.058172 | -0.0019839 | 0.008129 | 0.0077131 | -0.0070975 | 0.038339 | 0.0043777 | -8.7208 | 0.23034 | -8.817 | 113.9807 | 113.4936 | 113.7417 | -8.4516 | -0.003531 | -0.031692 | -0.06093 | 0.098244 | 0.21974 | -0.16166 | -0.31525 | 0.39693 | 0.098285 | 0.12779 | 0.031551 | -0.36537 | -0.38886 | -0.14077 | 8.5333 | -113.7842 | 8.845 | 8.7876 | 0.25432 | -113.6627 | -114.0441 | 122.8293 | 122.3422 | 122.5902 | 9.0789 | -122.3341 | 8.9468 | 9.0683 | 8.6869 | 8.8169 | -114.1977
1259.7656 | 122.7676 | -9.2834 | 113.4064 | 1.4211e-13 | -0.018337 | -0.00049791 | 0.063767 | -0.012841 | 0.058172 | -0.0019839 | 0.008129 | 0.0079267 | -0.0068837 | 0.038126 | 0.0041641 | -9.1557 | 0.23492 | -9.2428 | 113.5595 | 113.0861 | 113.3616 | -8.8683 | 0.001048 | -0.036271 | -0.065509 | 0.093665 | 0.21974 | -0.17539 | -0.31067 | 0.41512 | 0.15315 | 0.12772 | 0.040646 | -0.37447 | -0.32031 | -0.044723 | 8.9728 | -113.3127 | 9.2845 | 9.2179 | 0.24516 | -113.1866 | -113.5818 | 122.843 | 122.3695 | 122.6451 | 9.5184 | -122.2747 | 9.3771 | 9.5032 | 9.1081 | 9.2472 | -113.717
1261.5312 | 122.7539 | -9.3933 | 113.2645 | 1.4211e-13 | -0.018551 | -0.00028411 | 0.063554 | -0.012414 | 0.057745 | 0.013277 | 0.0077016 | 0.0081403 | -0.0064565 | 0.038126 | 0.0045915 | -9.3206 | 0.23034 | -9.4122 | 113.3901 | 112.9029 | 113.1693 | -9.0332 | -0.00811 | -0.040849 | -0.070087 | 0.098244 | 0.22432 | -0.16624 | -0.31067 | 0.36014 | 0.12565 | 0.072761 | -0.018887 | -0.37903 | -0.36156 | -0.095117 | 9.0826 | -113.1662 | 9.3852 | 9.3232 | 0.24058 | -113.0401 | -113.4307 | 122.7834 | 122.2962 | 122.5627 | 9.6236 | -122.2976 | 9.4916 | 9.6176 | 9.2271 | 9.3525 | -113.5751
1263.2188 | 122.7768 | -9.4162 | 113.1958 | 1.4211e-13 | -0.018978 | -0.00049791 | 0.06334 | -0.013055 | 0.058172 | 0.0056466 | 0.0079152 | 0.0079267 | -0.0068837 | 0.038126 | 0.0043777 | -9.3343 | 0.23034 | -9.4717 | 113.3214 | 112.8571 | 113.0961 | -9.0973 | -0.003531 | -0.027113 | -0.070087 | 0.10282 | 0.22432 | -0.17081 | -0.31067 | 0.31892 | 0.12564 | 0.081914 | -0.055516 | -0.37444 | -0.33869 | -0.099711 | 9.1055 | -113.093 | 9.4127 | 9.3461 | 0.24058 | -112.9715 | -113.3666 | 122.7376 | 122.2733 | 122.5123 | 9.6465 | -122.2931 | 9.519 | 9.6405 | 9.2454 | 9.3891 | -113.5065
1264.9688 | 122.7081 | -9.4849 | 113.2004 | 1.4211e-13 | -0.018551 | -0.00071151 | 0.063767 | -0.013055 | 0.058385 | -0.0019839 | 0.0079152 | 0.0079267 | -0.0068837 | 0.038339 | 0.0043777 | -9.3618 | 0.23492 | -9.4946 | 113.3169 | 112.8251 | 113.0778 | -9.1202 | -0.003531 | -0.031692 | -0.065509 | 0.093665 | 0.2289 | -0.17997 | -0.31067 | 0.36469 | 0.11649 | 0.12311 | -0.009744 | -0.37444 | -0.37532 | -0.1226 | 9.1742 | -113.1067 | 9.4813 | 9.4194 | 0.24516 | -112.9715 | -113.3804 | 122.8017 | 122.3099 | 122.5626 | 9.7198 | -122.3205 | 9.5785 | 9.7138 | 9.3049 | 9.4532 | -113.511
1266.7344 | 122.8088 | -9.2789 | 113.3606 | 1.4211e-13 | -0.018551 | -0.00049791 | 0.063554 | -0.013055 | 0.057958 | 0.0056466 | 0.008129 | 0.0079267 | -0.0068837 | 0.038553 | 0.0039505 | -9.2107 | 0.23034 | -9.3389 | 113.4588 | 112.9899 | 113.2334 | -8.9828 | 0.001048 | -0.027113 | -0.065509 | 0.098244 | 0.23348 | -0.17081 | -0.31067 | 0.29607 | 0.098199 | 0.068201 | -0.060075 | -0.35614 | -0.37069 | -0.12715 | 8.9682 | -113.2624 | 9.2799 | 9.2134 | 0.24516 | -113.1271 | -113.5314 | 122.7377 | 122.2688 | 122.5123 | 9.5092 | -122.3434 | 9.3771 | 9.5123 | 9.1081 | 9.2518 | -113.6713
1268.4219 | 122.8043 | -9.2468 | 113.3835 | 1.4211e-13 | -0.018765 | -0.00028411 | 0.06334 | -0.013268 | 0.058385 | 0.013277 | 0.0079152 | 0.0079267 | -0.0070975 | 0.038126 | 0.0041641 | -9.1603 | 0.23492 | -9.284 | 113.5046 | 113.0357 | 113.2884 | -8.905 | -0.003531 | -0.040849 | -0.065509 | 0.093665 | 0.22432 | -0.17081 | -0.31525 | 0.34187 | 0.1211 | 0.086519 | -0.03718 | -0.37904 | -0.34779 | -0.095093 | 8.9316 | -113.2898 | 9.2433 | 9.1813 | 0.24974 | -113.1592 | -113.5543 | 122.7514 | 122.2825 | 122.5352 | 9.4817 | -122.2884 | 9.3405 | 9.4711 | 9.076 | 9.206 | -113.6987
1270.1719 | 122.7356 | -9.343 | 113.3102 | 1.4211e-13 | -0.018551 | -0.00049791 | 0.06334 | -0.012414 | 0.057958 | -0.0019839 | 0.0077016 | 0.0077131 | -0.0068837 | 0.038126 | 0.0041641 | -9.2519 | 0.23492 | -9.3847 | 113.4176 | 112.9304 | 113.1739 | -9.0377 | -0.003531 | -0.036271 | -0.070087 | 0.093665 | 0.22432 | -0.17081 | -0.31067 | 0.30521 | 0.10735 | 0.091083 | -0.041771 | -0.34698 | -0.37987 | -0.13632 | 9.0323 | -113.2166 | 9.3394 | 9.2729 | 0.24058 | -113.0859 | -113.4811 | 122.7605 | 122.2733 | 122.5169 | 9.5779 | -122.348 | 9.4366 | 9.5673 | 9.1721 | 9.3067 | -113.6209
1271.9219 | 122.7539 | -9.2834 | 113.3835 | 1.4211e-13 | -0.018551 | -0.00049791 | 0.06334 | -0.013055 | 0.058172 | 0.020908 | 0.0077016 | 0.0079267 | -0.0070975 | 0.038339 | 0.0039505 | -9.1557 | 0.23034 | -9.284 | 113.5092 | 113.0403 | 113.2838 | -8.905 | -0.003531 | -0.036271 | -0.06093 | 0.089087 | 0.22432 | -0.17081 | -0.31525 | 0.37849 | 0.12567 | 0.12772 | -0.000559 | -0.37904 | -0.34322 | -0.099671 | 8.9682 | -113.2944 | 9.2799 | 9.2225 | 0.25432 | -113.1592 | -113.5543 | 122.7926 | 122.3237 | 122.5673 | 9.5138 | -122.2884 | 9.3725 | 9.5078 | 9.1126 | 9.2472 | -113.6987
1273.6719 | 122.8043 | -9.1415 | 113.4567 | 1.4211e-13 | -0.018337 | -0.00028411 | 0.063767 | -0.013055 | 0.058172 | 0.0056466 | 0.0077016 | 0.0083539 | -0.0068837 | 0.038553 | 0.0039505 | -9.0596 | 0.23034 | -9.1924 | 113.6099 | 113.1273 | 113.38 | -8.7951 | 0.001048 | -0.031692 | -0.070087 | 0.093665 | 0.22432 | -0.17081 | -0.31067 | 0.34647 | 0.15316 | 0.081959 | -0.050899 | -0.39737 | -0.32946 | -0.076763 | 8.8309 | -113.3631 | 9.1426 | 9.0715 | 0.24058 | -113.2324 | -113.6275 | 122.7514 | 122.2688 | 122.5215 | 9.3719 | -122.2518 | 9.2352 | 9.3659 | 8.9707 | 9.1098 | -113.7674
1275.3594 | 122.644 | -8.8074 | 113.8916 | 1.4211e-13 | -0.018124 | -0.00049791 | 0.063767 | -0.012627 | 0.057958 | -0.0019839 | 0.0079152 | 0.0079267 | -0.0073111 | 0.038339 | 0.0039505 | -8.6384 | 0.23492 | -8.7667 | 114.0174 | 113.5485 | 113.792 | -8.4196 | 0.001048 | -0.036271 | -0.070087 | 0.093665 | 0.23348 | -0.16624 | -0.31067 | 0.38778 | 0.12576 | 0.169 | 0.040713 | -0.34707 | -0.34307 | -0.099564 | 8.4967 | -113.7979 | 8.8084 | 8.7373 | 0.24058 | -113.6581 | -114.0578 | 122.8247 | 122.3559 | 122.5994 | 9.0423 | -122.3112 | 8.901 | 9.0409 | 8.6411 | 8.7711 | -114.2023
1277.0469 | 122.6669 | -9.256 | 113.4705 | 1.4211e-13 | -0.018551 | -0.00028411 | 0.063554 | -0.013055 | 0.058172 | 0.0056466 | 0.0079152 | 0.0077131 | -0.0070975 | 0.038339 | 0.0041641 | -9.0642 | 0.22576 | -9.1879 | 113.5961 | 113.1181 | 113.3662 | -8.8042 | 0.001048 | -0.031692 | -0.070087 | 0.093665 | 0.23348 | -0.17539 | -0.31983 | 0.45176 | 0.12569 | 0.19182 | 0.068119 | -0.38364 | -0.35235 | -0.10423 | 8.9362 | -113.3768 | 9.257 | 9.1859 | 0.24974 | -113.237 | -113.6459 | 122.8521 | 122.3741 | 122.6222 | 9.4817 | -122.2747 | 9.3496 | 9.4895 | 9.0806 | 9.2243 | -113.7903
1278.7344 | 122.7905 | -8.931 | 113.7131 | 1.4211e-13 | -0.018337 | 0.00014309 | 0.063554 | -0.013055 | 0.058172 | -0.0096144 | 0.0077016 | 0.0077131 | -0.0068837 | 0.038339 | 0.0041641 | -8.8261 | 0.22576 | -8.9452 | 113.8434 | 113.3654 | 113.6455 | -8.5707 | -0.003531 | -0.027113 | -0.065509 | 0.089087 | 0.2289 | -0.17081 | -0.31067 | 0.36027 | 0.13031 | 0.10488 | -0.014244 | -0.37451 | -0.3477 | -0.067552 | 8.6203 | -113.624 | 8.9274 | 8.8655 | 0.24516 | -113.4842 | -113.8839 | 122.7743 | 122.2963 | 122.5765 | 9.1567 | -122.2838 | 9.0201 | 9.1599 | 8.7602 | 8.9039 | -114.0237
1280.4219 | 122.7173 | -9.2011 | 113.5071 | 1.4211e-13 | -0.018551 | -0.00028411 | 0.063554 | -0.012841 | 0.058385 | 0.013277 | 0.0079152 | 0.0079267 | -0.0070975 | 0.038339 | 0.0039505 | -9.0871 | 0.23034 | -9.2153 | 113.5778 | 113.1044 | 113.3525 | -8.8454 | 0.001048 | -0.040849 | -0.065509 | 0.098244 | 0.2289 | -0.17539 | -0.31067 | 0.35562 | 0.070753 | 0.114 | -0.014282 | -0.3699 | -0.40271 | -0.15459 | 8.8904 | -113.4088 | 9.2021 | 9.1355 | 0.24516 | -113.2782 | -113.6825 | 122.7789 | 122.3054 | 122.5535 | 9.4314 | -122.3525 | 9.2993 | 9.43 | 9.0257 | 9.1602 | -113.8178
1282.1094 | 122.8043 | -9.2468 | 113.3835 | 1.4211e-13 | -0.018551 | -0.00071151 | 0.063767 | -0.012841 | 0.058172 | -0.0096144 | 0.0077016 | 0.0077131 | -0.0070975 | 0.038553 | 0.0039505 | -9.1328 | 0.23034 | -9.2565 | 113.5366 | 113.0586 | 113.3113 | -8.8866 | -0.00811 | -0.036271 | -0.074666 | 0.098244 | 0.22432 | -0.16624 | -0.31525 | 0.36018 | 0.15314 | 0.11399 | -0.00971 | -0.36989 | -0.3249 | -0.0722 | 8.9316 | -113.2852 | 9.2387 | 9.1722 | 0.24058 | -113.1592 | -113.5497 | 122.7835 | 122.3054 | 122.5581 | 9.4772 | -122.2701 | 9.3451 | 9.4711 | 9.0806 | 9.2106 | -113.6987
1283.8594 | 122.7814 | -9.2743 | 113.3698 | 1.4211e-13 | -0.018551 | -0.00028411 | 0.063554 | -0.012841 | 0.058385 | 0.0056466 | 0.0077016 | 0.0077131 | -0.0068837 | 0.038339 | 0.0039505 | -9.1832 | 0.23492 | -9.3069 | 113.4954 | 113.0036 | 113.2701 | -8.9324 | 0.001048 | -0.031692 | -0.065509 | 0.1074 | 0.2289 | -0.17081 | -0.31525 | 0.34186 | 0.12567 | 0.091093 | -0.032605 | -0.37446 | -0.36611 | -0.099674 | 8.959 | -113.2623 | 9.2753 | 9.2088 | 0.24974 | -113.1409 | -113.5406 | 122.7697 | 122.2779 | 122.5444 | 9.5092 | -122.3022 | 9.3817 | 9.5032 | 9.1035 | 9.2426 | -113.685
1285.5312 | 122.7951 | -9.3338 | 113.2736 | 1.4211e-13 | -0.018551 | -0.00071151 | 0.06334 | -0.013055 | 0.058385 | -0.0019839 | 0.0077016 | 0.0079267 | -0.0070975 | 0.038126 | 0.0039505 | -9.229 | 0.22576 | -9.3573 | 113.4359 | 112.9533 | 113.206 | -8.9828 | -0.00811 | -0.031692 | -0.065509 | 0.098244 | 0.22432 | -0.17539 | -0.31525 | 0.351 | 0.16228 | 0.10482 | -0.023457 | -0.37446 | -0.32035 | -0.067644 | 9.0186 | -113.1754 | 9.3257 | 9.2683 | 0.24974 | -113.0493 | -113.449 | 122.7697 | 122.2871 | 122.5398 | 9.5596 | -122.2564 | 9.432 | 9.5581 | 9.1584 | 9.3021 | -113.5889
1287.2969 | 122.7676 | -9.288 | 113.3331 | 1.4211e-13 | -0.018337 | -0.00049791 | 0.063767 | -0.013055 | 0.058385 | 0.0056466 | 0.008129 | 0.0079267 | -0.0073111 | 0.038339 | 0.0039505 | -9.1969 | 0.23034 | -9.3161 | 113.4725 | 113.0036 | 113.2426 | -8.9645 | -0.00811 | -0.036271 | -0.070087 | 0.1074 | 0.2289 | -0.16624 | -0.31067 | 0.32354 | 0.1394 | 0.091091 | -0.028029 | -0.35157 | -0.32949 | -0.090525 | 8.9774 | -113.2257 | 9.2799 | 9.2179 | 0.24058 | -113.1042 | -113.4994 | 122.7606 | 122.2917 | 122.5306 | 9.5184 | -122.2976 | 9.3954 | 9.5169 | 9.1218 | 9.2518 | -113.6438
1288.9844 | 122.7036 | -9.3796 | 113.2645 | 1.4211e-13 | -0.018551 | -7.051e-05 | 0.063981 | -0.012841 | 0.058385 | -0.0019839 | 0.0079152 | 0.0079267 | -0.0068837 | 0.038339 | 0.0037369 | -9.2107 | 0.22576 | -9.3435 | 113.4588 | 112.9762 | 113.2197 | -8.9965 | -0.003531 | -0.031692 | -0.06093 | 0.098244 | 0.2289 | -0.17081 | -0.31067 | 0.38304 | 0.19433 | 0.16891 | 0.036055 | -0.34698 | -0.2883 | -0.044753 | 9.0689 | -113.1662 | 9.376 | 9.3186 | 0.24974 | -113.0356 | -113.4353 | 122.8384 | 122.3557 | 122.5993 | 9.6053 | -122.261 | 9.4778 | 9.6085 | 9.2088 | 9.3479 | -113.5751
1290.7188 | 122.7631 | -9.2834 | 113.3652 | 1.4211e-13 | -0.018124 | -0.00028411 | 0.06334 | -0.012627 | 0.057745 | -0.0019839 | 0.0079152 | 0.0077131 | -0.0073111 | 0.038553 | 0.0039505 | -9.1832 | 0.22576 | -9.3069 | 113.4908 | 113.0082 | 113.2518 | -8.9324 | -0.00811 | -0.022535 | -0.06093 | 0.093665 | 0.2289 | -0.17081 | -0.31067 | 0.35101 | 0.12567 | 0.10025 | -0.02345 | -0.37446 | -0.35696 | -0.11341 | 8.9728 | -113.2715 | 9.2753 | 9.2225 | 0.24974 | -113.1363 | -113.536 | 122.7743 | 122.2917 | 122.5352 | 9.5092 | -122.2976 | 9.3771 | 9.5123 | 9.1126 | 9.2609 | -113.6758
1292.4688 | 122.7036 | -14.4974 | 108.1467 | 1.4211e-13 | -0.018337 | -0.00028411 | 0.063767 | -0.013268 | 0.057958 | 0.0056466 | 0.0077016 | 0.0079267 | -0.0070975 | 0.038339 | 0.0041641 | -14.5628 | 0.17539 | -14.691 | 108.1524 | 107.6783 | 107.9406 | -14.2165 | 0.005626 | -0.031692 | -0.06093 | 0.10282 | 0.23348 | -0.16166 | -0.31525 | 0.28086 | 0.005776 | -0.065429 | -0.19358 | -0.47444 | -0.46832 | -0.20608 | 14.1821 | -108.0438 | 14.503 | 14.4364 | 0.25432 | -107.9132 | -108.3083 | 122.6498 | 122.1757 | 122.438 | 14.6728 | -122.3632 | 14.6002 | 14.7309 | 14.3357 | 14.4657 | -108.4619
1294.1562 | 122.7448 | -13.5544 | 109.0805 | 1.4211e-13 | -0.018551 | -0.00071151 | 0.063767 | -0.012841 | 0.058172 | 0.0056466 | 0.0079152 | 0.0081403 | -0.0070975 | 0.038126 | 0.0041641 | -13.5189 | 0.18455 | -13.6471 | 109.1963 | 108.7223 | 108.9753 | -13.1863 | 0.001048 | -0.027113 | -0.06093 | 0.093665 | 0.2289 | -0.17081 | -0.31067 | 0.36813 | 0.11581 | 0.03545 | -0.092725 | -0.46085 | -0.35816 | -0.10516 | 13.2437 | -108.9868 | 13.5554 | 13.4935 | 0.24974 | -108.8516 | -109.2513 | 122.7507 | 122.2767 | 122.5297 | 13.7389 | -122.2668 | 13.648 | 13.7833 | 13.3836 | 13.5273 | -109.3912
1295.8906 | 122.6669 | -12.8723 | 109.8404 | 1.4211e-13 | -0.018765 | -0.00049791 | 0.063767 | -0.013055 | 0.058385 | -0.0019839 | 0.007488 | 0.0079267 | -0.0068837 | 0.038339 | 0.0039505 | -12.7543 | 0.20286 | -12.878 | 109.9655 | 109.4824 | 109.7674 | -12.4536 | 0.001048 | -0.031692 | -0.065509 | 0.098244 | 0.22432 | -0.17081 | -0.31067 | 0.41869 | 0.12509 | 0.11797 | -0.005642 | -0.42433 | -0.35795 | -0.072947 | 12.5616 | -109.7421 | 12.8734 | 12.8068 | 0.24516 | -109.6161 | -110.0112 | 122.8378 | 122.3548 | 122.6398 | 13.0752 | -122.294 | 12.9706 | 13.0966 | 12.7015 | 12.8406 | -110.1511
1297.5781 | 122.7585 | -12.7213 | 109.9091 | 1.4211e-13 | -0.018765 | -0.00028411 | 0.063126 | -0.013055 | 0.058385 | 0.0056466 | 0.0079152 | 0.0081403 | -0.0068837 | 0.038553 | 0.0043777 | -12.6536 | 0.18913 | -12.7635 | 110.0662 | 109.5923 | 109.8453 | -12.3208 | 0.005626 | -0.031692 | -0.065509 | 0.10282 | 0.22432 | -0.17081 | -0.31525 | 0.40041 | 0.15715 | 0.067635 | -0.042247 | -0.44266 | -0.31672 | -0.063776 | 12.406 | -109.8062 | 12.7269 | 12.6557 | 0.24974 | -109.6847 | -110.0799 | 122.7875 | 122.3136 | 122.5665 | 12.9104 | -122.2299 | 12.8241 | 12.9456 | 12.5504 | 12.6896 | -110.2243
1299.3438 | 122.7905 | -12.7579 | 109.8267 | 1.4211e-13 | -0.018765 | -0.00049791 | 0.063554 | -0.012627 | 0.058385 | 0.0056466 | 0.0079152 | 0.0077131 | -0.0070975 | 0.038553 | 0.0041641 | -12.704 | 0.19829 | -12.8276 | 110.0067 | 109.5282 | 109.7858 | -12.3712 | 0.005626 | -0.031692 | -0.070087 | 0.098244 | 0.2289 | -0.17539 | -0.30609 | 0.38667 | 0.18003 | 0.053895 | -0.069721 | -0.45639 | -0.29843 | -0.0409 | 12.4518 | -109.7284 | 12.7635 | 12.6878 | 0.236 | -109.5978 | -110.0021 | 122.7646 | 122.2861 | 122.5436 | 12.9562 | -122.1979 | 12.8561 | 12.9868 | 12.5825 | 12.7262 | -110.1328
1301.0938 | 122.6761 | -12.4832 | 110.2203 | 1.4211e-13 | -0.018765 | -0.00071151 | 0.063554 | -0.012841 | 0.058172 | 0.0056466 | 0.0077016 | 0.0083539 | -0.0068837 | 0.038126 | 0.0039505 | -12.3972 | 0.20286 | -12.5163 | 110.3089 | 109.8304 | 110.0834 | -12.0965 | -0.003531 | -0.036271 | -0.070087 | 0.093665 | 0.2289 | -0.17081 | -0.31067 | 0.38674 | 0.088527 | 0.085988 | -0.033057 | -0.4198 | -0.38989 | -0.13697 | 12.1725 | -110.1267 | 12.4797 | 12.4131 | 0.24058 | -109.9914 | -110.3912 | 122.7921 | 122.3137 | 122.5666 | 12.6861 | -122.3168 | 12.5769 | 12.7121 | 12.3124 | 12.4469 | -110.531
1302.7812 | 122.6761 | -12.5702 | 110.1151 | 1.4211e-13 | -0.018765 | -0.00049791 | 0.063554 | -0.013268 | 0.058599 | 0.0056466 | 0.0077016 | 0.0079267 | -0.0070975 | 0.038553 | 0.0035231 | -12.498 | 0.20286 | -12.6307 | 110.2036 | 109.7389 | 109.9872 | -12.1972 | 0.001048 | -0.031692 | -0.065509 | 0.098244 | 0.2289 | -0.17081 | -0.31525 | 0.37298 | 0.08851 | 0.072239 | -0.060539 | -0.43352 | -0.37619 | -0.12783 | 12.2549 | -110.0168 | 12.5712 | 12.5047 | 0.24974 | -109.8862 | -110.2859 | 122.7738 | 122.3091 | 122.5574 | 12.7731 | -122.3123 | 12.6684 | 12.7991 | 12.3994 | 12.5385 | -110.4303
1304.5469 | 122.7219 | -8.9401 | 113.6902 | 1.4211e-13 | -0.018337 | -7.051e-05 | 0.063981 | -0.013055 | 0.058599 | -0.0019839 | 0.008129 | 0.0077131 | -0.0070975 | 0.038339 | 0.0039505 | -8.8627 | 0.23492 | -8.9681 | 113.8205 | 113.3333 | 113.5906 | -8.5936 | 0.001048 | -0.040849 | -0.070087 | 0.098244 | 0.21974 | -0.16624 | -0.31983 | 0.34653 | 0.1303 | 0.077414 | -0.027979 | -0.37451 | -0.35687 | -0.099607 | 8.6203 | -113.5919 | 8.9412 | 8.87 | 0.24974 | -113.4704 | -113.8564 | 122.7606 | 122.2734 | 122.5307 | 9.175 | -122.2838 | 9.0384 | 9.1599 | 8.7739 | 8.8993 | -114.01
1306.2344 | 122.6486 | -9.137 | 113.5986 | 1.4211e-13 | -0.018765 | -0.00028411 | 0.063554 | -0.013055 | 0.058599 | -0.0019839 | 0.0077016 | 0.0077131 | -0.0068837 | 0.038339 | 0.0041641 | -8.9589 | 0.23492 | -9.0734 | 113.7152 | 113.228 | 113.4853 | -8.7264 | 0.001048 | -0.036271 | -0.06093 | 0.093665 | 0.2289 | -0.17081 | -0.31067 | 0.41058 | 0.11655 | 0.17811 | 0.063558 | -0.34702 | -0.37063 | -0.11336 | 8.8263 | -113.505 | 9.138 | 9.076 | 0.24974 | -113.3697 | -113.7694 | 122.8521 | 122.365 | 122.6222 | 9.3719 | -122.325 | 9.2306 | 9.3659 | 8.9661 | 9.1007 | -113.9093
1307.9844 | 122.6944 | -9.1003 | 113.5849 | 1.4211e-13 | -0.018978 | -0.00028411 | 0.063554 | -0.012841 | 0.058172 | 0.013277 | 0.007488 | 0.0079267 | -0.0068837 | 0.038553 | 0.0037369 | -8.9451 | 0.23949 | -9.0642 | 113.7243 | 113.2417 | 113.499 | -8.7035 | 0.001048 | -0.031692 | -0.070087 | 0.098244 | 0.21974 | -0.17081 | -0.31525 | 0.39685 | 0.13944 | 0.15522 | 0.036094 | -0.36076 | -0.34316 | -0.085893 | 8.7851 | -113.4867 | 9.1014 | 9.0303 | 0.24516 | -113.3652 | -113.7557 | 122.8247 | 122.3421 | 122.5993 | 9.3398 | -122.2884 | 9.1986 | 9.3201 | 8.9295 | 9.0686 | -113.9002
1309.7344 | 122.644 | -9.2514 | 113.443 | 1.4211e-13 | -0.018337 | -0.00049791 | 0.063767 | -0.012841 | 0.058385 | 0.013277 | 0.0077016 | 0.0079267 | -0.0068837 | 0.038339 | 0.0039505 | -9.1145 | 0.23492 | -9.2336 | 113.5595 | 113.0769 | 113.3296 | -8.8683 | 0.001048 | -0.036271 | -0.074666 | 0.093665 | 0.2289 | -0.17081 | -0.30609 | 0.38308 | 0.11653 | 0.13688 | 0.017759 | -0.36532 | -0.36609 | -0.11339 | 8.9453 | -113.3493 | 9.2525 | 9.1767 | 0.23143 | -113.2141 | -113.6138 | 122.8109 | 122.3283 | 122.581 | 9.4863 | -122.3113 | 9.3451 | 9.4803 | 9.0806 | 9.2151 | -113.7491
1311.5 | 122.6852 | -9.2194 | 113.4888 | 1.4211e-13 | -0.018978 | -0.00049791 | 0.063554 | -0.012841 | 0.058172 | 0.0056466 | 0.0079152 | 0.0079267 | -0.0070975 | 0.038767 | 0.0041641 | -9.0871 | 0.23949 | -9.2108 | 113.5824 | 113.109 | 113.3525 | -8.8409 | 0.001048 | -0.036271 | -0.065509 | 0.098244 | 0.23348 | -0.16624 | -0.31525 | 0.3785 | 0.093641 | 0.13231 | 0.008607 | -0.3699 | -0.37982 | -0.13628 | 8.9041 | -113.3905 | 9.2204 | 9.1539 | 0.24974 | -113.2553 | -113.655 | 122.8018 | 122.3283 | 122.5719 | 9.4589 | -122.3296 | 9.3176 | 9.4528 | 9.0531 | 9.1831 | -113.804
1313.2344 | 122.731 | -9.2102 | 113.4567 | 1.4211e-13 | -0.018765 | -0.00049791 | 0.063554 | -0.012627 | 0.058599 | -0.0019839 | 0.007488 | 0.0079267 | -0.0073111 | 0.038339 | 0.0037369 | -9.0779 | 0.23949 | -9.1924 | 113.5916 | 113.1181 | 113.3891 | -8.8637 | -0.003531 | -0.036271 | -0.070087 | 0.098244 | 0.24264 | -0.17539 | -0.31067 | 0.34646 | 0.13484 | 0.13231 | 0.017765 | -0.32869 | -0.33862 | -0.067605 | 8.8995 | -113.3585 | 9.2067 | 9.1401 | 0.24058 | -113.2141 | -113.6321 | 122.8018 | 122.3283 | 122.5993 | 9.4497 | -122.3205 | 9.3084 | 9.4528 | 9.0348 | 9.1739 | -113.7674
1314.9062 | 122.7448 | -9.2056 | 113.4659 | 1.4211e-13 | -0.018765 | -0.00028411 | 0.063554 | -0.013055 | 0.058172 | 0.013277 | 0.0077016 | 0.0081403 | -0.0073111 | 0.038553 | 0.0039505 | -9.0916 | 0.23492 | -9.2153 | 113.5733 | 113.1044 | 113.3525 | -8.8775 | -0.00811 | -0.031692 | -0.070087 | 0.093665 | 0.22432 | -0.16624 | -0.32441 | 0.32814 | 0.10737 | 0.114 | -0.009705 | -0.33784 | -0.36151 | -0.11339 | 8.8812 | -113.3722 | 9.1975 | 9.1355 | 0.25432 | -113.2416 | -113.6321 | 122.7789 | 122.31 | 122.5581 | 9.4405 | -122.3434 | 9.2993 | 9.4299 | 9.0394 | 9.1739 | -113.7903
1316.6562 | 122.6349 | -9.1736 | 113.4888 | 1.4211e-13 | -0.019192 | -0.00049791 | 0.063554 | -0.013055 | 0.058385 | 0.0056466 | 0.0079152 | 0.0079267 | -0.0068837 | 0.038339 | 0.0039505 | -9.055 | 0.28986 | -9.1787 | 113.5961 | 113.1227 | 113.3662 | -8.8592 | -0.003531 | -0.045428 | -0.070087 | 0.089087 | 0.22432 | -0.16624 | -0.31067 | 0.31441 | 0.10738 | 0.11858 | -0.005121 | -0.31953 | -0.36608 | -0.12254 | 8.8629 | -113.3997 | 9.1701 | 9.1035 | 0.24058 | -113.2644 | -113.655 | 122.7697 | 122.2963 | 122.5398 | 9.4634 | -122.3479 | 9.2627 | 9.3979 | 9.0073 | 9.1282 | -113.7994
1318.4219 | 122.7631 | -9.3933 | 113.2416 | 1.4211e-13 | -0.018765 | -0.00028411 | 0.06334 | -0.012841 | 0.058172 | 0.0056466 | 0.007488 | 0.0079267 | -0.0073111 | 0.038767 | 0.0039505 | -9.2839 | 0.2807 | -9.403 | 113.381 | 112.9029 | 113.1968 | -9.0927 | -0.003531 | -0.027113 | -0.074666 | 0.089087 | 0.21059 | -0.16624 | -0.32441 | 0.30062 | 0.13938 | 0.10939 | -0.00973 | -0.31034 | -0.33868 | -0.044758 | 9.0689 | -113.1525 | 9.3898 | 9.3186 | 0.24974 | -113.031 | -113.4078 | 122.7743 | 122.2962 | 122.5901 | 9.674 | -122.3343 | 9.4824 | 9.6039 | 9.2271 | 9.3662 | -113.566
1320.1094 | 122.6624 | -9.4574 | 113.2233 | 1.4211e-13 | -0.018765 | -0.00028411 | 0.063554 | -0.012841 | 0.058385 | 0.0056466 | 0.007488 | 0.0079267 | -0.0070975 | 0.038339 | 0.0039505 | -9.2885 | 0.2807 | -9.4168 | 113.3718 | 112.8937 | 113.1465 | -9.0927 | -0.003531 | -0.031692 | -0.074666 | 0.093665 | 0.22432 | -0.17539 | -0.32441 | 0.3647 | 0.14854 | 0.1689 | 0.040621 | -0.32408 | -0.32952 | -0.076812 | 9.133 | -113.1296 | 9.4539 | 9.3827 | 0.24974 | -112.9989 | -113.3987 | 122.8292 | 122.3511 | 122.6039 | 9.7381 | -122.316 | 9.5511 | 9.6817 | 9.282 | 9.4257 | -113.5477
1321.8594 | 122.7127 | -9.4482 | 113.1775 | 1.4211e-13 | -0.018337 | -0.00028411 | 0.06334 | -0.013055 | 0.058385 | -0.0096144 | 0.007488 | 0.0077131 | -0.0070975 | 0.038767 | 0.0037369 | -9.3434 | 0.2807 | -9.4717 | 113.326 | 112.8525 | 113.0915 | -9.1293 | -0.003531 | -0.036271 | -0.074666 | 0.084508 | 0.22432 | -0.17539 | -0.31983 | 0.31891 | 0.14853 | 0.1048 | -0.023473 | -0.34239 | -0.32496 | -0.085979 | 9.1284 | -113.093 | 9.4447 | 9.3736 | 0.24516 | -112.9532 | -113.3529 | 122.7743 | 122.3008 | 122.5398 | 9.7289 | -122.3068 | 9.5328 | 9.6726 | 9.2728 | 9.412 | -113.4973
1323.625 | 122.699 | -9.5581 | 113.1226 | 1.4211e-13 | -0.018551 | -0.00028411 | 0.063554 | -0.012841 | 0.058172 | 0.0056466 | 0.0079152 | 0.0079267 | -0.0070975 | 0.038339 | 0.0039505 | -9.4579 | 0.2807 | -9.5816 | 113.2116 | 112.7426 | 112.9862 | -9.2346 | 0.001048 | -0.036271 | -0.074666 | 0.093665 | 0.22432 | -0.17081 | -0.32441 | 0.32346 | 0.089003 | 0.1002 | -0.023489 | -0.34695 | -0.37992 | -0.13635 | 9.2337 | -113.0289 | 9.5592 | 9.4834 | 0.24974 | -112.8982 | -113.2934 | 122.7697 | 122.3007 | 122.5443 | 9.8388 | -122.3572 | 9.6518 | 9.7824 | 9.3873 | 9.5218 | -113.447
1325.375 | 122.7676 | -12.4603 | 110.1196 | 1.4211e-13 | -0.018551 | -0.00049791 | 0.06334 | -0.013268 | 0.058599 | 0.0056466 | 0.0077016 | 0.0077131 | -0.0070975 | 0.038339 | 0.0037369 | -12.4613 | 0.24865 | -12.5849 | 110.2448 | 109.7755 | 110.0467 | -12.2018 | 0.001048 | -0.036271 | -0.070087 | 0.093665 | 0.22432 | -0.16166 | -0.31983 | 0.25854 | 0.12514 | -0.000997 | -0.12462 | -0.38316 | -0.34413 | -0.072888 | 12.1405 | -110.026 | 12.4614 | 12.3902 | 0.24974 | -109.8953 | -110.2813 | 122.7051 | 122.2358 | 122.5071 | 12.709 | -122.3214 | 12.554 | 12.6846 | 12.2987 | 12.4241 | -110.4395
1327.125 | 122.7722 | -12.2269 | 110.4034 | 1.4211e-13 | -0.019192 | -0.00049791 | 0.063126 | -0.013055 | 0.058172 | 0.020908 | 0.0077016 | 0.0079267 | -0.0070975 | 0.038339 | 0.0041641 | -12.1363 | 0.25781 | -12.2645 | 110.579 | 110.1006 | 110.381 | -11.8721 | -0.012689 | -0.031692 | -0.074666 | 0.089087 | 0.22432 | -0.16166 | -0.31525 | 0.35476 | 0.17555 | 0.090609 | -0.037598 | -0.39236 | -0.30284 | -0.022463 | 11.9116 | -110.3144 | 12.2142 | 12.1522 | 0.24058 | -110.1791 | -110.5651 | 122.8059 | 122.3275 | 122.6078 | 12.4847 | -122.2755 | 12.316 | 12.4512 | 12.0652 | 12.1952 | -110.7187
1328.7969 | 122.6395 | -12.1811 | 110.5179 | 1.4211e-13 | -0.018551 | -0.00049791 | 0.063554 | -0.012627 | 0.057958 | 0.0056466 | 0.0079152 | 0.0079267 | -0.0070975 | 0.038339 | 0.0037369 | -12.0859 | 0.24865 | -12.2187 | 110.6248 | 110.151 | 110.4039 | -11.8675 | -0.012689 | -0.031692 | -0.074666 | 0.093665 | 0.21516 | -0.17081 | -0.32441 | 0.31357 | 0.10689 | 0.095195 | -0.037593 | -0.35116 | -0.36691 | -0.11401 | 11.8567 | -110.4242 | 12.1684 | 12.1064 | 0.24974 | -110.3027 | -110.6887 | 122.8059 | 122.3321 | 122.585 | 12.4297 | -122.3854 | 12.2748 | 12.3963 | 12.0103 | 12.1494 | -110.8423
1330.5469 | 122.7814 | -11.9385 | 110.6461 | 1.4211e-13 | -0.018551 | -0.00028411 | 0.063554 | -0.012841 | 0.058172 | 0.0056466 | 0.007488 | 0.0079267 | -0.0073111 | 0.038553 | 0.0039505 | -11.8982 | 0.25781 | -12.0264 | 110.8125 | 110.3387 | 110.6328 | -11.6935 | 0.001048 | -0.036271 | -0.074666 | 0.098244 | 0.2289 | -0.17081 | -0.32441 | 0.24495 | 0.16643 | 0.040294 | -0.087919 | -0.33287 | -0.30735 | -0.013255 | 11.6141 | -110.5478 | 11.9395 | 11.8638 | 0.24974 | -110.4172 | -110.8169 | 122.751 | 122.2772 | 122.5713 | 12.1963 | -122.3396 | 12.0367 | 12.1674 | 11.7677 | 11.9022 | -110.9705
1332.2344 | 122.7722 | -12.5656 | 110.0693 | 1.4211e-13 | -0.019192 | -0.00071151 | 0.063554 | -0.013055 | 0.058385 | 0.013277 | 0.0077016 | 0.0081403 | -0.0070975 | 0.038767 | 0.0039505 | -12.5392 | 0.24865 | -12.6628 | 110.1852 | 109.716 | 110.001 | -12.3208 | -0.003531 | -0.040849 | -0.070087 | 0.098244 | 0.23348 | -0.17081 | -0.31525 | 0.24478 | 0.11597 | 0.026456 | -0.097164 | -0.34194 | -0.35331 | -0.06832 | 12.2504 | -109.971 | 12.5621 | 12.4955 | 0.24516 | -109.8358 | -110.2401 | 122.7509 | 122.2816 | 122.5666 | 12.8143 | -122.3901 | 12.6639 | 12.7991 | 12.3948 | 12.5248 | -110.3845
1333.9844 | 122.7768 | -13.0783 | 109.52 | 1.4211e-13 | -0.018978 | -0.00028411 | 0.063554 | -0.012841 | 0.057745 | 0.0056466 | 0.008129 | 0.0079267 | -0.0068837 | 0.038553 | 0.0039505 | -12.9787 | 0.23949 | -13.0977 | 109.7457 | 109.2672 | 109.5751 | -12.7421 | -0.003531 | -0.036271 | -0.074666 | 0.089087 | 0.2289 | -0.17081 | -0.31983 | 0.33621 | 0.22576 | 0.099626 | -0.019405 | -0.35561 | -0.25272 | 0.055187 | 12.7585 | -109.4309 | 13.0748 | 13.0036 | 0.24516 | -109.2911 | -109.6908 | 122.824 | 122.3455 | 122.6535 | 13.3178 | -122.2621 | 13.1674 | 13.3072 | 12.9075 | 13.042 | -109.8398
1335.7188 | 122.7264 | -12.7075 | 109.9548 | 1.4211e-13 | -0.018978 | 0.00014309 | 0.063554 | -0.013268 | 0.058172 | -0.0019839 | 0.0079152 | 0.0081403 | -0.0068837 | 0.038767 | 0.0037369 | -12.6811 | 0.24407 | -12.8001 | 110.0433 | 109.574 | 109.9231 | -12.449 | 0.001048 | -0.036271 | -0.074666 | 0.093665 | 0.22432 | -0.17539 | -0.31983 | 0.25847 | 0.088484 | 0.026433 | -0.092605 | -0.35108 | -0.38081 | -0.031715 | 12.3877 | -109.8612 | 12.7086 | 12.6329 | 0.24516 | -109.7305 | -110.1302 | 122.7508 | 122.2815 | 122.6306 | 12.9516 | -122.4039 | 12.8012 | 12.9318 | 12.5321 | 12.6712 | -110.2747
1337.4688 | 122.7951 | -12.4603 | 110.1471 | 1.4211e-13 | -0.019192 | -0.00049791 | 0.063767 | -0.013055 | 0.058172 | -0.0019839 | 0.0077016 | 0.0079267 | -0.0070975 | 0.038553 | 0.0039505 | -12.4522 | 0.24865 | -12.5712 | 110.2722 | 109.7938 | 110.1017 | -12.2613 | -0.003531 | -0.027113 | -0.065509 | 0.098244 | 0.22432 | -0.17081 | -0.31525 | 0.19901 | 0.12514 | 0.00816 | -0.11088 | -0.3099 | -0.35328 | -0.045411 | 12.1451 | -110.0489 | 12.4568 | 12.3948 | 0.24974 | -109.9228 | -110.3179 | 122.7326 | 122.2541 | 122.562 | 12.709 | -122.4084 | 12.5586 | 12.6846 | 12.2895 | 12.4332 | -110.4623
1339.1562 | 122.699 | -12.3642 | 110.3302 | 1.4211e-13 | -0.018978 | -0.00071151 | 0.063126 | -0.013268 | 0.058172 | -0.0019839 | 0.0077016 | 0.0077131 | -0.0073111 | 0.038553 | 0.0041641 | -12.2965 | 0.24865 | -12.4155 | 110.4279 | 109.9587 | 110.239 | -12.0461 | 0.001048 | -0.031692 | -0.065509 | 0.098244 | 0.2289 | -0.17081 | -0.32441 | 0.31809 | 0.097702 | 0.067695 | -0.051353 | -0.36945 | -0.37155 | -0.091158 | 12.0398 | -110.232 | 12.3652 | 12.2987 | 0.2589 | -110.1013 | -110.501 | 122.7921 | 122.3229 | 122.6032 | 12.6128 | -122.3763 | 12.4624 | 12.5931 | 12.1934 | 12.3325 | -110.6546
1340.8906 | 122.6898 | -12.4786 | 110.2249 | 1.4211e-13 | -0.019192 | -0.00092531 | 0.06334 | -0.013482 | 0.058385 | 0.013277 | 0.0079152 | 0.0079267 | -0.0070975 | 0.038767 | 0.0035231 | -12.4155 | 0.25323 | -12.5437 | 110.2997 | 109.8304 | 110.2345 | -12.2155 | -0.003531 | -0.036271 | -0.065509 | 0.10282 | 0.22432 | -0.16624 | -0.31525 | 0.26312 | 0.074792 | 0.063098 | -0.065104 | -0.32822 | -0.39447 | 0.009549 | 12.1634 | -110.1221 | 12.4751 | 12.4131 | 0.24974 | -110.0006 | -110.3912 | 122.7783 | 122.3091 | 122.7131 | 12.7319 | -122.4404 | 12.5815 | 12.703 | 12.3124 | 12.4424 | -110.5402
1342.625 | 122.7127 | -12.9547 | 109.7076 | 1.4211e-13 | -0.018978 | -0.00071151 | 0.06334 | -0.012841 | 0.058172 | -0.0019839 | 0.0077016 | 0.0077131 | -0.0068837 | 0.038767 | 0.0041641 | -12.8688 | 0.23949 | -13.0016 | 109.851 | 109.3771 | 109.685 | -12.7146 | -0.00811 | -0.036271 | -0.074666 | 0.098244 | 0.23806 | -0.17539 | -0.31525 | 0.24009 | 0.14338 | 0.085911 | -0.046858 | -0.28694 | -0.33051 | -0.022611 | 12.6395 | -109.6094 | 12.9466 | 12.88 | 0.24058 | -109.4696 | -109.883 | 122.8057 | 122.3318 | 122.6397 | 13.1942 | -122.4223 | 13.053 | 13.1928 | 12.7793 | 12.9184 | -110.0229
1344.3125 | 122.699 | -12.8311 | 109.8679 | 1.4211e-13 | -0.018978 | -0.00028411 | 0.06334 | -0.013055 | 0.058385 | -0.0019839 | 0.0079152 | 0.0079267 | -0.0068837 | 0.038339 | 0.0039505 | -12.736 | 0.25781 | -12.8551 | 109.993 | 109.5237 | 109.8544 | -12.4994 | 0.001048 | -0.027113 | -0.065509 | 0.098244 | 0.22432 | -0.17081 | -0.31525 | 0.3317 | 0.1251 | 0.095089 | -0.023949 | -0.35565 | -0.3442 | -0.013419 | 12.5159 | -109.7696 | 12.8322 | 12.7656 | 0.24974 | -109.6435 | -110.0387 | 122.8241 | 122.3548 | 122.6856 | 13.0889 | -122.3673 | 12.9294 | 13.0554 | 12.6603 | 12.804 | -110.1831
1346.0625 | 122.7356 | -12.6251 | 109.9915 | 1.4211e-13 | -0.018978 | -0.00071151 | 0.06334 | -0.013055 | 0.058385 | -0.0019839 | 0.0077016 | 0.0079267 | -0.0070975 | 0.038339 | 0.0041641 | -12.5712 | 0.25323 | -12.6902 | 110.1578 | 109.6839 | 110.0605 | -12.3529 | 0.001048 | -0.036271 | -0.074666 | 0.098244 | 0.22432 | -0.17539 | -0.31983 | 0.27223 | 0.16632 | 0.053916 | -0.065124 | -0.33736 | -0.30754 | 0.069022 | 12.3053 | -109.8932 | 12.6262 | 12.5505 | 0.24516 | -109.7671 | -110.1668 | 122.7829 | 122.309 | 122.6856 | 12.8784 | -122.3443 | 12.7234 | 12.8494 | 12.4497 | 12.5889 | -110.3113
1347.8125 | 122.7859 | -12.6389 | 109.9915 | 1.4211e-13 | -0.018978 | -0.00049791 | 0.06334 | -0.012841 | 0.058599 | 0.013277 | 0.0077016 | 0.0077131 | -0.0068837 | 0.038553 | 0.0041641 | -12.5071 | 0.25323 | -12.6445 | 110.2127 | 109.748 | 110.0467 | -12.275 | -0.003531 | -0.036271 | -0.065509 | 0.093665 | 0.22432 | -0.17539 | -0.31983 | 0.36381 | 0.22126 | 0.13175 | -0.005609 | -0.36942 | -0.24343 | 0.055286 | 12.319 | -109.8978 | 12.6353 | 12.5733 | 0.25432 | -109.7671 | -110.1668 | 122.8516 | 122.3869 | 122.6856 | 12.8921 | -122.2665 | 12.7325 | 12.8632 | 12.4635 | 12.6026 | -110.3113
1349.5156 | 122.6852 | -12.5107 | 110.2112 | 1.4211e-13 | -0.019406 | -0.00028411 | 0.063554 | -0.013055 | 0.058172 | 0.0056466 | 0.007488 | 0.0081403 | -0.0070975 | 0.038339 | 0.0039505 | -12.356 | 0.25323 | -12.4796 | 110.3684 | 109.8991 | 110.1887 | -12.1239 | 0.001048 | -0.031692 | -0.074666 | 0.089087 | 0.22432 | -0.17539 | -0.31525 | 0.38674 | 0.1572 | 0.15466 | 0.031035 | -0.3557 | -0.31206 | -0.022505 | 12.1954 | -110.1221 | 12.5117 | 12.436 | 0.24058 | -109.9869 | -110.3866 | 122.8791 | 122.4098 | 122.6994 | 12.7639 | -122.3351 | 12.5998 | 12.735 | 12.3353 | 12.479 | -110.5264
1351.2656 | 122.7676 | -12.2864 | 110.3302 | 1.4211e-13 | -0.019192 | -0.00049791 | 0.06334 | -0.013055 | 0.057958 | 0.0056466 | 0.007488 | 0.0079267 | -0.0070975 | 0.038767 | 0.0041641 | -12.237 | 0.25781 | -12.3606 | 110.4828 | 110.0182 | 110.2802 | -11.9866 | -0.00811 | -0.031692 | -0.065509 | 0.093665 | 0.2289 | -0.17997 | -0.31983 | 0.2998 | 0.15264 | 0.049394 | -0.074233 | -0.37403 | -0.31202 | -0.04995 | 11.9665 | -110.2365 | 12.2783 | 12.2209 | 0.25432 | -110.1013 | -110.5102 | 122.7692 | 122.3046 | 122.5666 | 12.5442 | -122.3168 | 12.38 | 12.5153 | 12.1064 | 12.2547 | -110.65
1352.9375 | 122.6624 | -12.1445 | 110.582 | 1.4211e-13 | -0.018978 | -7.051e-05 | 0.063554 | -0.013055 | 0.058599 | -0.0019839 | 0.0079152 | 0.0077131 | -0.0070975 | 0.03898 | 0.0035231 | -11.9577 | 0.26239 | -12.0905 | 110.7667 | 110.2838 | 110.6374 | -11.7851 | -0.003531 | -0.031692 | -0.065509 | 0.098244 | 0.2289 | -0.17539 | -0.31983 | 0.35937 | 0.18473 | 0.18677 | 0.053978 | -0.30539 | -0.29821 | 0.055411 | 11.8246 | -110.4837 | 12.1409 | 12.079 | 0.25432 | -110.3531 | -110.7574 | 122.9112 | 122.4282 | 122.7819 | 12.4069 | -122.3671 | 12.2427 | 12.3734 | 11.9691 | 12.1128 | -110.9018
1354.7031 | 122.6715 | -12.0163 | 110.733 | 1.4211e-13 | -0.018978 | -0.00049791 | 0.063554 | -0.013055 | 0.058599 | -0.0019839 | 0.007488 | 0.0079267 | -0.0070975 | 0.03898 | 0.0039505 | -11.8844 | 0.26697 | -12.0035 | 110.8445 | 110.3753 | 110.6557 | -11.6432 | -0.00811 | -0.036271 | -0.074666 | 0.093665 | 0.23348 | -0.16624 | -0.31983 | 0.37314 | 0.1115 | 0.13185 | 0.012792 | -0.36035 | -0.3577 | -0.077337 | 11.6965 | -110.6394 | 12.0082 | 11.9416 | 0.24516 | -110.4996 | -110.8993 | 122.8608 | 122.3916 | 122.672 | 12.2833 | -122.3762 | 12.11 | 12.2498 | 11.8501 | 11.98 | -111.0529
1356.375 | 122.6578 | -11.7188 | 110.9802 | 1.4211e-13 | -0.018978 | -0.00028411 | 0.063126 | -0.013268 | 0.057958 | 0.0056466 | 0.0077016 | 0.0079267 | -0.0073111 | 0.038767 | 0.0041641 | -11.6784 | 0.25781 | -11.8112 | 111.0322 | 110.5722 | 110.8572 | -11.4737 | -0.003531 | -0.031692 | -0.074666 | 0.093665 | 0.2289 | -0.16166 | -0.32441 | 0.24501 | 0.052024 | 0.04033 | -0.092467 | -0.33748 | -0.408 | -0.12307 | 11.3943 | -110.8866 | 11.7152 | 11.6441 | 0.24974 | -110.7513 | -111.1419 | 122.751 | 122.291 | 122.5759 | 11.9766 | -122.454 | 11.8124 | 11.9477 | 11.5571 | 11.6871 | -111.3046
1358.125 | 122.7722 | -11.6272 | 111.026 | 1.4211e-13 | -0.019192 | -7.051e-05 | 0.063126 | -0.013055 | 0.058385 | -0.0019839 | 0.007488 | 0.0079267 | -0.0073111 | 0.038767 | 0.0037369 | -11.6509 | 0.26239 | -11.7746 | 111.0689 | 110.6134 | 110.8892 | -11.4188 | -0.003531 | -0.031692 | -0.074666 | 0.093665 | 0.23348 | -0.17081 | -0.31983 | 0.20841 | 0.042876 | -0.023753 | -0.14739 | -0.3558 | -0.41256 | -0.1368 | 11.3074 | -110.9323 | 11.6237 | 11.5525 | 0.24516 | -110.7925 | -111.1968 | 122.6961 | 122.2406 | 122.5164 | 11.8896 | -122.4448 | 11.7209 | 11.8607 | 11.4564 | 11.5955 | -111.3458
1359.8125 | 122.7997 | -11.6455 | 110.9848 | 1.4211e-13 | -0.018765 | -0.00028411 | 0.063126 | -0.012841 | 0.058599 | 0.0056466 | 0.007488 | 0.0081403 | -0.0070975 | 0.038553 | 0.0037369 | -11.564 | 0.26697 | -11.683 | 111.1696 | 110.7004 | 111.0128 | -11.3547 | -0.00811 | -0.036271 | -0.065509 | 0.093665 | 0.2289 | -0.17081 | -0.31067 | 0.29082 | 0.1848 | 0.081548 | -0.037517 | -0.32834 | -0.28436 | 0.028024 | 11.3348 | -110.8911 | 11.6374 | 11.58 | 0.24516 | -110.7559 | -111.1556 | 122.8151 | 122.3459 | 122.6583 | 11.9125 | -122.3395 | 11.7392 | 11.8744 | 11.4747 | 11.6092 | -111.2955
1361.5625 | 122.7173 | -11.6501 | 111.0443 | 1.4211e-13 | -0.019192 | -0.00071151 | 0.063126 | -0.013055 | 0.058385 | 0.013277 | 0.007488 | 0.0079267 | -0.0073111 | 0.038553 | 0.0039505 | -11.5502 | 0.26697 | -11.6739 | 111.1788 | 110.705 | 110.9808 | -11.3684 | -0.003531 | -0.036271 | -0.065509 | 0.089087 | 0.22432 | -0.17539 | -0.31067 | 0.28166 | 0.13445 | 0.09986 | -0.023783 | -0.30545 | -0.33929 | -0.063536 | 11.3394 | -110.9552 | 11.6466 | 11.5846 | 0.24516 | -110.82 | -111.2197 | 122.8288 | 122.3551 | 122.6309 | 11.9171 | -122.4127 | 11.7392 | 11.8744 | 11.4747 | 11.6138 | -111.355
1363.2344 | 122.6715 | -11.5723 | 111.1038 | 1.4211e-13 | -0.018978 | -0.00028411 | 0.063554 | -0.012841 | 0.058385 | 0.0056466 | 0.0077016 | 0.0079267 | -0.0070975 | 0.038767 | 0.0035231 | -11.5319 | 0.26697 | -11.6647 | 111.1879 | 110.7096 | 110.9991 | -11.3272 | -0.012689 | -0.027113 | -0.070087 | 0.098244 | 0.22432 | -0.17081 | -0.31525 | 0.24505 | 0.084094 | 0.040355 | -0.092446 | -0.3375 | -0.39422 | -0.10473 | 11.257 | -111.0056 | 11.5596 | 11.5022 | 0.24516 | -110.8795 | -111.2746 | 122.7602 | 122.2819 | 122.5714 | 11.8392 | -122.431 | 11.6705 | 11.7966 | 11.4015 | 11.5452 | -111.4191
1365 | 122.7905 | -11.5723 | 111.0718 | 1.4211e-13 | -0.019192 | -0.00071151 | 0.063554 | -0.013268 | 0.057958 | -0.0096144 | 0.0077016 | 0.0079267 | -0.0066701 | 0.038339 | 0.0039505 | -11.4632 | 0.26239 | -11.5915 | 111.2429 | 110.7783 | 111.0678 | -11.286 | -0.00811 | -0.036271 | -0.070087 | 0.098244 | 0.21974 | -0.16624 | -0.32441 | 0.28627 | 0.17108 | 0.10903 | -0.019193 | -0.30546 | -0.2935 | -0.004008 | 11.2479 | -110.9735 | 11.5642 | 11.5022 | 0.25432 | -110.852 | -111.238 | 122.8151 | 122.3505 | 122.64 | 11.8347 | -122.3578 | 11.6705 | 11.792 | 11.406 | 11.536 | -111.3962
1366.6875 | 122.7905 | -11.5128 | 111.1313 | 1.4211e-13 | -0.018978 | -0.00028411 | 0.063554 | -0.013055 | 0.058385 | 0.013277 | 0.007488 | 0.0074993 | -0.0070975 | 0.038767 | 0.0037369 | -11.4312 | 0.26697 | -11.564 | 111.2795 | 110.8149 | 111.0952 | -11.199 | -0.00811 | -0.036271 | -0.074666 | 0.089087 | 0.2289 | -0.17081 | -0.31525 | 0.31375 | 0.1482 | 0.081569 | -0.051233 | -0.36499 | -0.31637 | -0.036046 | 11.1975 | -111.0422 | 11.5046 | 11.4381 | 0.24058 | -110.9024 | -111.3021 | 122.7922 | 122.3277 | 122.608 | 11.7797 | -122.3303 | 11.6018 | 11.7417 | 11.3419 | 11.4765 | -111.4465
1368.4375 | 122.7814 | -11.4944 | 111.145 | 1.4211e-13 | -0.018978 | -0.00071151 | 0.063554 | -0.012841 | 0.058385 | 0.013277 | 0.0077016 | 0.0077131 | -0.0070975 | 0.038767 | 0.0037369 | -11.4083 | 0.26697 | -11.5365 | 111.3024 | 110.8332 | 111.1593 | -11.2036 | -0.012689 | -0.027113 | -0.070087 | 0.098244 | 0.21974 | -0.17539 | -0.32441 | 0.29087 | 0.15735 | 0.086151 | -0.042074 | -0.33294 | -0.31179 | 0.014321 | 11.17 | -111.0468 | 11.4818 | 11.4244 | 0.25432 | -110.9253 | -111.3204 | 122.7968 | 122.3277 | 122.6538 | 11.7614 | -122.3486 | 11.5927 | 11.7142 | 11.3191 | 11.4673 | -111.4694
1370.125 | 122.6486 | -11.4487 | 111.2549 | 1.4211e-13 | -0.018978 | -0.00028411 | 0.063554 | -0.013055 | 0.058172 | -0.0019839 | 0.0077016 | 0.0081403 | -0.0070975 | 0.038553 | 0.0041641 | -11.3946 | 0.27154 | -11.5136 | 111.3298 | 110.8607 | 111.1364 | -11.2311 | -0.012689 | -0.031692 | -0.065509 | 0.093665 | 0.22432 | -0.17539 | -0.31983 | 0.21762 | 0.074962 | 0.054109 | -0.064959 | -0.28257 | -0.39418 | -0.11844 | 11.1288 | -111.1612 | 11.436 | 11.3832 | 0.25432 | -111.0306 | -111.4303 | 122.7785 | 122.3094 | 122.5851 | 11.7202 | -122.4859 | 11.5423 | 11.673 | 11.2733 | 11.417 | -111.5747
1371.875 | 122.7219 | -11.7004 | 110.9619 | 1.4211e-13 | -0.018978 | -0.00071151 | 0.063554 | -0.013055 | 0.058599 | 0.0056466 | 0.0077016 | 0.0079267 | -0.0073111 | 0.038339 | 0.0039505 | -11.6281 | 0.26697 | -11.7471 | 111.1009 | 110.6363 | 110.9533 | -11.3776 | -0.003531 | -0.036271 | -0.070087 | 0.098244 | 0.22432 | -0.16624 | -0.32899 | 0.32286 | 0.13901 | 0.072381 | -0.046682 | -0.36954 | -0.32558 | -0.00861 | 11.3715 | -110.8637 | 11.6969 | 11.6304 | 0.2589 | -110.7376 | -111.1281 | 122.8014 | 122.3368 | 122.6537 | 11.9674 | -122.3395 | 11.7987 | 11.9248 | 11.5342 | 11.6642 | -111.2909
1373.5469 | 122.7264 | -11.6043 | 111.0397 | 1.4211e-13 | -0.019406 | -0.00071151 | 0.06334 | -0.013268 | 0.058385 | -0.0019839 | 0.0077016 | 0.0079267 | -0.0068837 | 0.038339 | 0.0039505 | -11.5319 | 0.25781 | -11.6601 | 111.1925 | 110.7188 | 111.0357 | -11.3226 | 0.001048 | -0.036271 | -0.070087 | 0.093665 | 0.21516 | -0.17081 | -0.31525 | 0.28168 | 0.15276 | 0.072398 | -0.055824 | -0.3375 | -0.32098 | -0.004015 | 11.2891 | -110.9461 | 11.6054 | 11.5342 | 0.24516 | -110.8246 | -111.2105 | 122.7968 | 122.3231 | 122.64 | 11.8621 | -122.3624 | 11.698 | 11.8195 | 11.4335 | 11.568 | -111.355
1375.2812 | 122.8043 | -11.5219 | 111.1313 | 1.4211e-13 | -0.018978 | -0.00028411 | 0.063554 | -0.013268 | 0.058172 | -0.0096144 | 0.0077016 | 0.0079267 | -0.0073111 | 0.038553 | 0.0039505 | -11.4724 | 0.25323 | -11.596 | 111.252 | 110.7874 | 111.1181 | -11.2265 | -0.00811 | -0.027113 | -0.074666 | 0.093665 | 0.22432 | -0.17081 | -0.31983 | 0.29544 | 0.12072 | 0.04952 | -0.074125 | -0.36956 | -0.34385 | -0.013153 | 11.2021 | -111.0376 | 11.5138 | 11.4472 | 0.24516 | -110.907 | -111.3021 | 122.7739 | 122.3093 | 122.64 | 11.7751 | -122.3578 | 11.6156 | 11.7462 | 11.3511 | 11.4948 | -111.4511
1377.0469 | 122.6715 | -11.5631 | 111.1313 | 1.4211e-13 | -0.018978 | -0.0011389 | 0.063554 | -0.013055 | 0.058172 | -0.0019839 | 0.0079152 | 0.0079267 | -0.0073111 | 0.038767 | 0.0039505 | -11.4724 | 0.25781 | -11.6006 | 111.2474 | 110.7829 | 111.0907 | -11.2494 | -0.003531 | -0.027113 | -0.065509 | 0.098244 | 0.2289 | -0.16166 | -0.31983 | 0.31374 | 0.11615 | 0.090718 | -0.037506 | -0.35125 | -0.34843 | -0.040625 | 11.2433 | -111.033 | 11.5596 | 11.4976 | 0.25432 | -110.9024 | -111.2929 | 122.8105 | 122.346 | 122.6538 | 11.8209 | -122.3807 | 11.6614 | 11.792 | 11.4015 | 11.536 | -111.4511
1378.7969 | 122.7356 | -11.467 | 111.1954 | 1.4211e-13 | -0.018765 | -0.00028411 | 0.06334 | -0.013268 | 0.058385 | -0.0019839 | 0.0077016 | 0.0079267 | -0.0073111 | 0.038767 | 0.0039505 | -11.3991 | 0.25781 | -11.5228 | 111.3161 | 110.847 | 111.1685 | -11.1212 | -0.003531 | -0.036271 | -0.065509 | 0.093665 | 0.2289 | -0.17081 | -0.32441 | 0.34582 | 0.12073 | 0.067842 | -0.055805 | -0.40163 | -0.34841 | -0.026876 | 11.1426 | -111.1017 | 11.4634 | 11.4015 | 0.2589 | -110.9665 | -111.3662 | 122.7831 | 122.3139 | 122.6355 | 11.7248 | -122.3165 | 11.5606 | 11.6959 | 11.2962 | 11.4307 | -111.5198
1380.4844 | 122.699 | -11.5036 | 111.2091 | 1.4211e-13 | -0.018765 | -0.00092531 | 0.063126 | -0.012627 | 0.058385 | -0.0019839 | 0.0079152 | 0.0081403 | -0.0068837 | 0.038767 | 0.0039505 | -11.3717 | 0.25781 | -11.5045 | 111.3482 | 110.879 | 111.1364 | -11.1349 | -0.003531 | -0.036271 | -0.079245 | 0.098244 | 0.2289 | -0.17539 | -0.32441 | 0.3687 | 0.13905 | 0.13193 | -0.000871 | -0.36957 | -0.33009 | -0.072658 | 11.1792 | -111.1109 | 11.5001 | 11.4244 | 0.24516 | -110.9802 | -111.3845 | 122.8518 | 122.3826 | 122.64 | 11.7614 | -122.344 | 11.6018 | 11.7325 | 11.3282 | 11.4673 | -111.5335
1382.2344 | 122.7448 | -11.7554 | 110.8841 | 1.4211e-13 | -0.019192 | -0.00049791 | 0.06334 | -0.013055 | 0.058385 | 0.013277 | 0.0077016 | 0.0081403 | -0.0070975 | 0.038339 | 0.0037369 | -11.6555 | 0.25781 | -11.7883 | 111.0643 | 110.5951 | 110.9121 | -11.4463 | -0.00811 | -0.040849 | -0.074666 | 0.10282 | 0.2289 | -0.17081 | -0.31525 | 0.30911 | 0.1802 | 0.099843 | -0.032954 | -0.34206 | -0.28897 | 0.028003 | 11.4401 | -110.7813 | 11.7473 | 11.6807 | 0.24058 | -110.6552 | -111.0549 | 122.8197 | 122.3505 | 122.6675 | 12.0132 | -122.3304 | 11.8582 | 11.9843 | 11.5846 | 11.7145 | -111.1993
1383.9844 | 122.7722 | -11.586 | 111.0535 | 1.4211e-13 | -0.018978 | -0.00049791 | 0.06334 | -0.013055 | 0.058172 | -0.0019839 | 0.007488 | 0.0081403 | -0.0070975 | 0.03898 | 0.0037369 | -11.5777 | 0.25781 | -11.7105 | 111.1421 | 110.6867 | 110.9716 | -11.3043 | -0.003531 | -0.036271 | -0.074666 | 0.098244 | 0.23348 | -0.17997 | -0.32441 | 0.28168 | 0.088664 | 0.008304 | -0.1245 | -0.40618 | -0.36677 | -0.081848 | 11.2616 | -110.9552 | 11.5825 | 11.5113 | 0.24974 | -110.82 | -111.2334 | 122.7281 | 122.2727 | 122.5576 | 11.8438 | -122.3578 | 11.6842 | 11.8195 | 11.406 | 11.5497 | -111.3779
1385.7188 | 122.699 | -11.7096 | 110.9619 | 1.4211e-13 | -0.018765 | -0.00071151 | 0.06334 | -0.012841 | 0.058172 | -0.0019839 | 0.0077016 | 0.0074993 | -0.0070975 | 0.03898 | 0.0039505 | -11.6372 | 0.25781 | -11.77 | 111.0872 | 110.618 | 110.8938 | -11.4188 | -0.012689 | -0.031692 | -0.070087 | 0.093665 | 0.2289 | -0.16624 | -0.31983 | 0.29081 | 0.12528 | 0.072381 | -0.060417 | -0.35122 | -0.3439 | -0.068132 | 11.3898 | -110.8682 | 11.6969 | 11.6395 | 0.24974 | -110.733 | -111.1281 | 122.7968 | 122.3276 | 122.6034 | 11.9674 | -122.3807 | 11.8033 | 11.9385 | 11.5434 | 11.6779 | -111.2817
1387.4062 | 122.7905 | -11.4761 | 111.1404 | 1.4211e-13 | -0.018978 | -0.00071151 | 0.063767 | -0.013055 | 0.057958 | 0.0056466 | 0.0077016 | 0.0081403 | -0.0070975 | 0.038767 | 0.0039505 | -11.4907 | 0.25323 | -11.6098 | 111.2383 | 110.7691 | 111.0449 | -11.2356 | -0.003531 | -0.040849 | -0.070087 | 0.098244 | 0.23348 | -0.17081 | -0.32441 | 0.2405 | 0.097835 | -0.014571 | -0.13364 | -0.37414 | -0.37132 | -0.095566 | 11.1517 | -111.0422 | 11.4726 | 11.406 | 0.25432 | -110.907 | -111.3113 | 122.7144 | 122.2453 | 122.521 | 11.7294 | -122.3761 | 11.5744 | 11.7096 | 11.3053 | 11.4353 | -111.4648
1389.1719 | 122.6578 | -11.6547 | 111.0764 | 1.4211e-13 | -0.019192 | -0.00028411 | 0.063767 | -0.013055 | 0.058172 | 0.013277 | 0.0077016 | 0.0079267 | -0.0070975 | 0.039194 | 0.0037369 | -11.596 | 0.24865 | -11.7105 | 111.1376 | 110.6684 | 110.9533 | -11.2906 | -0.00811 | -0.040849 | -0.074666 | 0.098244 | 0.22432 | -0.16624 | -0.31983 | 0.36408 | 0.061197 | 0.058654 | -0.055831 | -0.41991 | -0.40797 | -0.12305 | 11.3348 | -110.9781 | 11.6466 | 11.58 | 0.24516 | -110.852 | -111.2426 | 122.7922 | 122.323 | 122.608 | 11.9033 | -122.3669 | 11.7529 | 11.879 | 11.4884 | 11.6138 | -111.3962
1390.8594 | 122.7264 | -11.3525 | 111.2915 | 1.4211e-13 | -0.019192 | -0.00028411 | 0.063554 | -0.012627 | 0.058385 | -0.0096144 | 0.007488 | 0.0074993 | -0.0073111 | 0.038767 | 0.0037369 | -11.4312 | 0.25781 | -11.5548 | 111.2886 | 110.8241 | 111.196 | -11.1349 | 0.001048 | -0.040849 | -0.074666 | 0.098244 | 0.22432 | -0.17081 | -0.31983 | 0.21764 | -0.002865 | -0.078648 | -0.20229 | -0.41994 | -0.46743 | -0.095534 | 11.0327 | -111.1933 | 11.3536 | 11.2779 | 0.24516 | -111.0672 | -111.4623 | 122.6412 | 122.1766 | 122.5485 | 11.6103 | -122.4264 | 11.4508 | 11.5769 | 11.1817 | 11.3117 | -111.6113
1392.5938 | 122.7264 | -11.5585 | 111.0901 | 1.4211e-13 | -0.018978 | -0.00049791 | 0.063126 | -0.013055 | 0.058599 | 0.0056466 | 0.0072744 | 0.0077131 | -0.0070975 | 0.03898 | 0.0037369 | -11.4449 | 0.26239 | -11.5503 | 111.2841 | 110.8241 | 111.1044 | -11.199 | -0.003531 | -0.045428 | -0.083823 | 0.098244 | 0.22432 | -0.17997 | -0.31983 | 0.35953 | 0.19397 | 0.11361 | 0.008278 | -0.35125 | -0.26602 | 0.01431 | 11.2387 | -110.9918 | 11.555 | 11.4747 | 0.23601 | -110.8658 | -111.2701 | 122.8426 | 122.3826 | 122.6629 | 11.8209 | -122.2891 | 11.6568 | 11.7829 | 11.3786 | 11.5131 | -111.4099
1394.3438 | 122.7951 | -11.4304 | 111.1954 | 1.4211e-13 | -0.018978 | -0.00049791 | 0.063554 | -0.013055 | 0.058172 | -0.0019839 | 0.0077016 | 0.0081403 | -0.0070975 | 0.038767 | 0.0037369 | -11.3808 | 0.26697 | -11.5091 | 111.3298 | 110.8699 | 111.2189 | -11.1624 | -0.003531 | -0.040849 | -0.070087 | 0.093665 | 0.22432 | -0.16624 | -0.32441 | 0.26799 | 0.13447 | 0.049534 | -0.078691 | -0.34668 | -0.32551 | 0.023489 | 11.106 | -111.1017 | 11.4268 | 11.3603 | 0.25432 | -110.9711 | -111.3616 | 122.7602 | 122.3002 | 122.6492 | 11.6973 | -122.3577 | 11.524 | 11.6547 | 11.2641 | 11.3895 | -111.5198
1396.0938 | 122.7905 | -11.4349 | 111.1954 | 1.4211e-13 | -0.019192 | -0.00071151 | 0.06334 | -0.013055 | 0.058813 | 0.0056466 | 0.007488 | 0.0081403 | -0.0070975 | 0.038553 | 0.0037369 | -11.3305 | 0.27154 | -11.445 | 111.3985 | 110.934 | 111.2234 | -11.0708 | -0.00811 | -0.040849 | -0.070087 | 0.098244 | 0.2289 | -0.17081 | -0.31983 | 0.36414 | 0.20315 | 0.10447 | -0.010017 | -0.37416 | -0.26141 | 0.028068 | 11.1151 | -111.0971 | 11.4268 | 11.3649 | 0.24974 | -110.9665 | -111.3662 | 122.8335 | 122.3689 | 122.6584 | 11.7065 | -122.2662 | 11.5332 | 11.6638 | 11.2641 | 11.3941 | -111.5152
1397.7812 | 122.7127 | -11.4532 | 111.232 | 1.4211e-13 | -0.019192 | -0.00049791 | 0.063554 | -0.013268 | 0.058385 | -0.0019839 | 0.0077016 | 0.0079267 | -0.0070975 | 0.038767 | 0.0037369 | -11.2755 | 0.27154 | -11.39 | 111.4535 | 110.9798 | 111.2967 | -11.0616 | -0.003531 | -0.040849 | -0.070087 | 0.098244 | 0.2289 | -0.17081 | -0.32441 | 0.39161 | 0.22147 | 0.17772 | 0.063232 | -0.32838 | -0.25224 | 0.064704 | 11.1288 | -111.1338 | 11.4497 | 11.3832 | 0.25432 | -111.0031 | -111.4028 | 122.9067 | 122.433 | 122.7499 | 11.7248 | -122.2936 | 11.5515 | 11.6821 | 11.2824 | 11.4124 | -111.5564
1399.5469 | 122.6852 | -11.4532 | 111.2228 | 1.4211e-13 | -0.0057306 | -0.0011389 | -0.0024744 | -0.013055 | 0.0098841 | -0.0019839 | 0.007488 | 0.0081403 | -0.0070975 | 0.038767 | 0.0039505 | 110.5004 | 1.1186 | 110.5479 | 111.3298 | 110.8561 | 111.1777 | 7.7394 | 0.005626 | -0.031692 | -0.070087 | 0.089087 | 0.21974 | -0.17081 | -0.31983 | 19.1927 | 0.10701 | 121.9537 | 122.0012 | 102.8085 | -0.36672 | -0.045183 | 11.1334 | -111.1338 | 11.4589 | 11.3832 | 0.24974 | -111.0031 | -111.3937 | 122.7831 | 122.3094 | 122.6309 | 12.5718 | -103.4834 | 11.5423 | 11.673 | 11.2824 | 11.4216 | -111.5427
1401.2969 | 122.7859 | -11.3159 | 111.3007 | 1.4211e-13 | -0.0059444 | -0.0013525 | -0.0026882 | -0.013482 | 0.010098 | 0.0056466 | 0.007488 | 0.0081403 | -0.0073111 | 0.038553 | 0.0037369 | 110.7889 | 0.98581 | 110.7997 | 111.3756 | 110.9065 | 111.2097 | 7.7715 | -0.012689 | -0.036271 | -0.070087 | 0.098244 | 0.2289 | -0.16624 | -0.32899 | 19.0874 | 0.07497 | 122.1048 | 122.1156 | 103.0282 | -0.39417 | -0.090953 | 10.9869 | -111.2024 | 11.3032 | 11.2458 | 0.2589 | -111.0718 | -111.4669 | 122.6915 | 122.2224 | 122.5256 | 12.3017 | -103.5292 | 11.4142 | 11.5448 | 11.1497 | 11.2796 | -111.6296
1402.9688 | 122.7264 | -11.348 | 111.3281 | 1.4211e-13 | -0.0057306 | -0.0011389 | -0.0022608 | -0.013268 | 0.0098841 | 0.013277 | 0.008129 | 0.0079267 | -0.0070975 | 0.03898 | 0.0037369 | 110.8667 | 0.95376 | 110.873 | 111.4443 | 110.9752 | 111.3196 | 7.7898 | -0.003531 | -0.036271 | -0.074666 | 0.093665 | 0.21974 | -0.17539 | -0.32441 | 19.1378 | 0.11618 | 122.2147 | 122.2209 | 103.0832 | -0.35295 | -0.008533 | 11.0236 | -111.2345 | 11.3444 | 11.2733 | 0.24974 | -111.1084 | -111.5035 | 122.7923 | 122.3231 | 122.6676 | 12.3017 | -103.5383 | 11.4416 | 11.5677 | 11.1726 | 11.3117 | -111.6525
1404.7188 | 122.7905 | -11.4304 | 111.2045 | 1.4211e-13 | -0.0044486 | -0.00092531 | -0.0022608 | -0.013268 | 0.010952 | 0.0056466 | 0.0077016 | 0.0079267 | -0.0075247 | 0.038553 | 0.0035231 | 110.8072 | 0.94002 | 110.8134 | 111.3756 | 110.9111 | 111.1685 | 7.7806 | -0.00811 | -0.045428 | -0.074666 | 0.093665 | 0.2289 | -0.17081 | -0.32899 | 19.211 | 0.1711 | 122.2375 | 122.2438 | 103.0328 | -0.29346 | -0.036031 | 11.1014 | -111.1109 | 11.4222 | 11.3557 | 0.25432 | -110.9756 | -111.3753 | 122.806 | 122.3414 | 122.5989 | 12.3704 | -103.4239 | 11.524 | 11.6593 | 11.2595 | 11.3849 | -111.5335
1406.4688 | 122.6944 | -11.348 | 111.3419 | 1.4211e-13 | -0.004235 | -0.0013525 | -0.0024744 | -0.013268 | 0.010952 | -0.0019839 | 0.007488 | 0.0081403 | -0.0070975 | 0.038767 | 0.0039505 | 110.8576 | 0.93544 | 110.8638 | 111.4214 | 110.9614 | 111.2967 | 7.7898 | -0.003531 | -0.040849 | -0.070087 | 0.089087 | 0.22432 | -0.17081 | -0.32899 | 19.1378 | 0.079554 | 122.2055 | 122.2118 | 103.074 | -0.38042 | -0.045159 | 11.019 | -111.2528 | 11.3444 | 11.2779 | 0.2589 | -111.1175 | -111.5127 | 122.7694 | 122.3094 | 122.6447 | 12.2834 | -103.5521 | 11.437 | 11.5723 | 11.1771 | 11.3071 | -111.6708
1408.2188 | 122.7356 | -11.2839 | 111.4197 | 1.4211e-13 | -0.0044486 | -0.0011389 | -0.0022608 | -0.013482 | 0.011166 | 0.013277 | 0.0077016 | 0.0079267 | -0.0070975 | 0.03898 | 0.0037369 | 110.9354 | 0.93544 | 110.9508 | 111.5038 | 111.0393 | 111.3333 | 7.7898 | -0.00811 | -0.045428 | -0.079245 | 0.089087 | 0.22432 | -0.17081 | -0.31983 | 19.0737 | 0.084145 | 122.2193 | 122.2347 | 103.161 | -0.3804 | -0.08635 | 10.964 | -111.3306 | 11.2758 | 11.2046 | 0.24058 | -111.1954 | -111.5905 | 122.7877 | 122.3232 | 122.6172 | 12.2193 | -103.6299 | 11.373 | 11.5082 | 11.1131 | 11.2384 | -111.7395
1409.9844 | 122.6486 | -11.348 | 111.3739 | 1.4211e-13 | -0.004876 | -0.0013525 | -0.0022608 | -0.013482 | 0.011166 | 0.0056466 | 0.0077016 | 0.0079267 | -0.0073111 | 0.038767 | 0.0037369 | 110.9308 | 0.92171 | 110.9325 | 111.4901 | 111.0164 | 111.3837 | 7.7898 | -0.012689 | -0.040849 | -0.074666 | 0.098244 | 0.22432 | -0.15708 | -0.32441 | 19.1378 | 0.11619 | 122.2788 | 122.2804 | 103.1427 | -0.35752 | 0.009792 | 11.0236 | -111.2757 | 11.3353 | 11.2733 | 0.24974 | -111.1496 | -111.531 | 122.838 | 122.3643 | 122.7317 | 12.2697 | -103.5841 | 11.4462 | 11.5723 | 11.1909 | 11.3071 | -111.6983
1411.7344 | 122.6761 | -11.4487 | 111.3007 | 1.4211e-13 | -0.004876 | -0.0011389 | -0.0022608 | -0.013268 | 0.011166 | -0.0019839 | 0.007488 | 0.0079267 | -0.0073111 | 0.038767 | 0.0037369 | 110.9033 | 0.93086 | 110.905 | 111.4672 | 111.0072 | 111.3013 | 7.7898 | 0.001048 | -0.036271 | -0.070087 | 0.098244 | 0.23348 | -0.16624 | -0.32899 | 19.2385 | 0.16654 | 122.352 | 122.3537 | 103.1152 | -0.29343 | 0.000619 | 11.1197 | -111.2024 | 11.4497 | 11.3786 | 0.2589 | -111.0672 | -111.4669 | 122.9159 | 122.4559 | 122.7499 | 12.3795 | -103.5109 | 11.5469 | 11.6821 | 11.2824 | 11.4124 | -111.6296
1413.4219 | 122.6578 | -11.2885 | 111.438 | 1.4211e-13 | -0.004876 | -0.0013525 | -0.0024744 | -0.013482 | 0.01138 | 0.013277 | 0.0079152 | 0.0077131 | -0.0073111 | 0.03898 | 0.0039505 | 110.9903 | 0.93086 | 110.992 | 111.5496 | 111.0942 | 111.3791 | 7.7944 | -0.003531 | -0.040849 | -0.074666 | 0.093665 | 0.22432 | -0.16624 | -0.32441 | 19.0828 | 0.11162 | 122.2788 | 122.2805 | 103.1976 | -0.34376 | -0.058874 | 10.964 | -111.3443 | 11.2849 | 11.2138 | 0.24974 | -111.2137 | -111.6042 | 122.8381 | 122.3827 | 122.6676 | 12.2193 | -103.6436 | 11.3821 | 11.5128 | 11.1222 | 11.2476 | -111.7624
1415.1719 | 122.6898 | -11.3617 | 111.3876 | 1.4211e-13 | -0.004876 | -0.0011389 | -0.0024744 | -0.012841 | 0.011166 | -0.0019839 | 0.007488 | 0.0081403 | -0.0073111 | 0.03898 | 0.0037369 | 111.0178 | 0.92171 | 111.0286 | 111.5771 | 111.108 | 111.4615 | 7.7944 | -0.003531 | -0.036271 | -0.079245 | 0.089087 | 0.22432 | -0.17081 | -0.32441 | 19.1561 | 0.18944 | 122.3795 | 122.3903 | 103.2343 | -0.27967 | 0.073895 | 11.0373 | -111.2985 | 11.3582 | 11.2824 | 0.24516 | -111.1633 | -111.5584 | 122.9388 | 122.4697 | 122.8232 | 12.2834 | -103.5933 | 11.4508 | 11.586 | 11.1909 | 11.3254 | -111.712
1416.8594 | 122.8134 | -11.2793 | 111.3464 | 1.4211e-13 | -0.004235 | -0.0011389 | -0.0024744 | -0.013696 | 0.010952 | -0.0096144 | 0.0079152 | 0.0074993 | -0.0070975 | 0.038767 | 0.0039505 | 110.972 | 0.93086 | 110.9737 | 111.5221 | 111.0759 | 111.4112 | 7.7852 | -0.003531 | -0.045428 | -0.074666 | 0.098244 | 0.2289 | -0.17081 | -0.32899 | 19.0645 | 0.1757 | 122.2513 | 122.253 | 103.1885 | -0.27052 | 0.064728 | 10.9503 | -111.2482 | 11.2758 | 11.2046 | 0.25432 | -111.1175 | -111.5173 | 122.8014 | 122.3552 | 122.6905 | 12.2102 | -103.5612 | 11.3775 | 11.5082 | 11.1085 | 11.2339 | -111.6754
1418.6094 | 122.7585 | -11.2793 | 111.3968 | 1.4211e-13 | -0.004235 | -0.0011389 | -0.0022608 | -0.013696 | 0.01138 | 0.0056466 | 0.0079152 | 0.0077131 | -0.0073111 | 0.03898 | 0.0035231 | 110.9903 | 0.92628 | 110.9828 | 111.545 | 111.0805 | 111.3974 | 7.7944 | -0.00811 | -0.040849 | -0.070087 | 0.089087 | 0.21974 | -0.17539 | -0.31525 | 19.0737 | 0.14824 | 122.2696 | 122.2621 | 103.1885 | -0.3163 | 0.000639 | 10.964 | -111.3077 | 11.2712 | 11.2092 | 0.24516 | -111.177 | -111.5722 | 122.8243 | 122.3598 | 122.6767 | 12.2056 | -103.6024 | 11.3684 | 11.499 | 11.1039 | 11.2384 | -111.712
1420.2969 | 122.7631 | -11.5036 | 111.1725 | 1.4211e-13 | -0.0046624 | -0.0011389 | -0.0024744 | -0.013482 | 0.010952 | -0.0019839 | 0.0079152 | 0.0077131 | -0.0073111 | 0.038767 | 0.0035231 | 110.7568 | 0.92171 | 110.7585 | 111.307 | 110.847 | 111.2143 | 7.7944 | -0.00811 | -0.031692 | -0.079245 | 0.089087 | 0.2289 | -0.17539 | -0.32441 | 19.298 | 0.13447 | 122.2604 | 122.2621 | 102.9641 | -0.32552 | 0.041799 | 11.1792 | -111.0834 | 11.4955 | 11.4244 | 0.24516 | -110.9436 | -111.3479 | 122.8106 | 122.3506 | 122.7179 | 12.4253 | -103.3781 | 11.5927 | 11.7325 | 11.3282 | 11.4719 | -111.4969
1422.0469 | 122.7127 | -11.3709 | 111.3281 | 1.4211e-13 | -0.0044486 | -0.0013525 | -0.0024744 | -0.014123 | 0.011166 | 0.0056466 | 0.007488 | 0.0079267 | -0.0070975 | 0.038767 | 0.0037369 | 110.8759 | 0.93544 | 110.873 | 111.426 | 110.9569 | 111.2784 | 7.799 | -0.00811 | -0.036271 | -0.070087 | 0.089087 | 0.21974 | -0.17081 | -0.32441 | 19.1698 | 0.097866 | 122.2467 | 122.2438 | 103.074 | -0.37127 | -0.04974 | 11.0464 | -111.239 | 11.3627 | 11.3008 | 0.25432 | -111.1084 | -111.4989 | 122.7968 | 122.3277 | 122.6492 | 12.3063 | -103.5292 | 11.4599 | 11.5906 | 11.2 | 11.3346 | -111.6525
1423.7344 | 122.7859 | -11.4075 | 111.2503 | 1.4211e-13 | -0.0044486 | -0.0011389 | -0.0024744 | -0.013482 | 0.011166 | -0.0019839 | 0.0079152 | 0.0074993 | -0.0073111 | 0.038767 | 0.0037369 | 110.94 | 0.92171 | 110.9416 | 111.4992 | 111.0393 | 111.3471 | 7.7944 | -0.003531 | -0.031692 | -0.079245 | 0.093665 | 0.2289 | -0.17081 | -0.31983 | 19.2018 | 0.24894 | 122.3474 | 122.3491 | 103.1473 | -0.21103 | 0.096759 | 11.0876 | -111.1566 | 11.4039 | 11.3282 | 0.24058 | -111.0214 | -111.4211 | 122.9067 | 122.4467 | 122.7545 | 12.3292 | -103.4559 | 11.5011 | 11.6364 | 11.2367 | 11.3758 | -111.5701
1425.4844 | 122.6715 | -11.3297 | 111.3556 | 1.4211e-13 | -0.004876 | -0.0011389 | -0.0024744 | -0.013696 | 0.010952 | -0.0096144 | 0.007488 | 0.0079267 | -0.0073111 | 0.03898 | 0.0037369 | 110.9537 | 0.93086 | 110.9554 | 111.5038 | 111.0439 | 111.4066 | 7.799 | -0.003531 | -0.045428 | -0.065509 | 0.093665 | 0.21974 | -0.17081 | -0.32441 | 19.1286 | 0.14823 | 122.2833 | 122.285 | 103.1564 | -0.31173 | 0.050995 | 11.0052 | -111.2619 | 11.3261 | 11.2641 | 0.2589 | -111.1358 | -111.5264 | 122.8335 | 122.3735 | 122.7362 | 12.2605 | -103.5566 | 11.4233 | 11.5494 | 11.1588 | 11.2842 | -111.68
1427.1719 | 122.7173 | -11.261 | 111.4014 | 1.4211e-13 | -0.004876 | -0.00071151 | -0.0022608 | -0.013482 | 0.011166 | -0.0019839 | 0.0077016 | 0.0079267 | -0.0075247 | 0.038767 | 0.0035231 | 111.0315 | 0.94002 | 111.0195 | 111.5908 | 111.1583 | 111.4386 | 7.831 | -0.00811 | -0.040849 | -0.079245 | 0.098244 | 0.22432 | -0.16624 | -0.31983 | 19.092 | 0.18945 | 122.2925 | 122.2805 | 103.1885 | -0.24304 | 0.037269 | 10.9412 | -111.3031 | 11.2529 | 11.1817 | 0.24058 | -111.177 | -111.5676 | 122.8518 | 122.4193 | 122.6996 | 12.201 | -103.5704 | 11.3592 | 11.4853 | 11.0948 | 11.2201 | -111.7212
1428.9062 | 122.7127 | -11.2061 | 111.5158 | 1.4211e-13 | -0.004876 | -0.00092531 | -0.0022608 | -0.013482 | 0.010739 | -0.0019839 | 0.0077016 | 0.0074993 | -0.0073111 | 0.03898 | 0.0039505 | 111.0682 | 0.93544 | 111.0607 | 111.6274 | 111.1721 | 111.5302 | 7.7944 | -0.003531 | -0.036271 | -0.074666 | 0.093665 | 0.2289 | -0.17539 | -0.32899 | 19.0004 | 0.11163 | 122.2742 | 122.2667 | 103.2663 | -0.34374 | 0.0144 | 10.8771 | -111.4221 | 11.2025 | 11.1314 | 0.25432 | -111.2869 | -111.6912 | 122.8335 | 122.3781 | 122.7363 | 12.1415 | -103.7214 | 11.2997 | 11.435 | 11.0307 | 11.1698 | -111.8448
1430.6562 | 122.7997 | -11.087 | 111.5707 | 1.4211e-13 | -0.0046624 | -0.00092531 | -0.0026882 | -0.013268 | 0.011166 | 0.013277 | 0.0079152 | 0.0077131 | -0.0075247 | 0.038767 | 0.0039505 | 111.2238 | 0.9446 | 111.2118 | 111.7923 | 111.3232 | 111.6355 | 7.8173 | -0.003531 | -0.036271 | -0.074666 | 0.093665 | 0.22432 | -0.17539 | -0.31983 | 18.9043 | 0.22152 | 122.3109 | 122.2988 | 103.3945 | -0.24757 | 0.064776 | 10.7672 | -111.4771 | 11.0835 | 11.0124 | 0.24516 | -111.3464 | -111.7461 | 122.8793 | 122.4102 | 122.7226 | 12.0316 | -103.7535 | 11.1807 | 11.3114 | 10.9116 | 11.0508 | -111.8906
1432.3438 | 122.6852 | -11.2061 | 111.5112 | 1.4211e-13 | -0.0044486 | -0.0011389 | -0.0024744 | -0.013482 | 0.01138 | 0.0056466 | 0.0072744 | 0.0079267 | -0.0073111 | 0.039408 | 0.0035231 | 111.1506 | 0.94002 | 111.1385 | 111.7099 | 111.2453 | 111.6584 | 7.7944 | -0.00811 | -0.040849 | -0.070087 | 0.089087 | 0.21516 | -0.17081 | -0.31983 | 19.0004 | 0.19862 | 122.3566 | 122.3446 | 103.3441 | -0.2659 | 0.14718 | 10.8862 | -111.4221 | 11.1979 | 11.136 | 0.24974 | -111.2961 | -111.682 | 122.9159 | 122.4514 | 122.8645 | 12.1461 | -103.7169 | 11.2951 | 11.4212 | 11.0352 | 11.1652 | -111.8311
1434.0781 | 122.7493 | -11.3617 | 111.2915 | 1.4211e-13 | -0.004235 | -0.00092531 | -0.0024744 | -0.013268 | 0.010952 | -0.0019839 | 0.0077016 | 0.0077131 | -0.0073111 | 0.03898 | 0.0037369 | 110.9812 | 0.94918 | 110.9783 | 111.5405 | 111.0805 | 111.457 | 7.7898 | -0.003531 | -0.036271 | -0.070087 | 0.10282 | 0.22432 | -0.17539 | -0.32899 | 19.1515 | 0.24895 | 122.3429 | 122.34 | 103.1885 | -0.21102 | 0.16545 | 11.0327 | -111.1887 | 11.3582 | 11.2916 | 0.2589 | -111.0672 | -111.4669 | 122.9021 | 122.4422 | 122.8186 | 12.3109 | -103.5017 | 11.4645 | 11.586 | 11.1863 | 11.3254 | -111.6205
1435.7656 | 122.8043 | -11.0779 | 111.5341 | 1.4211e-13 | -0.0044486 | -0.00092531 | -0.0029018 | -0.013268 | 0.011166 | 0.0056466 | 0.0072744 | 0.0079267 | -0.0068837 | 0.038767 | 0.0037369 | 111.1597 | 0.9446 | 111.1568 | 111.7282 | 111.2545 | 111.5806 | 7.7898 | 0.001048 | -0.027113 | -0.070087 | 0.089087 | 0.22432 | -0.17539 | -0.32441 | 18.8677 | 0.19405 | 122.2376 | 122.2347 | 103.367 | -0.27963 | 0.046454 | 10.7535 | -111.445 | 11.0789 | 11.0078 | 0.25432 | -111.3098 | -111.7095 | 122.806 | 122.3324 | 122.6585 | 12.0225 | -103.7443 | 11.167 | 11.3022 | 10.9025 | 11.0508 | -111.8585
1437.5 | 122.6761 | -10.9772 | 111.7584 | 1.4211e-13 | -0.0044486 | -0.00092531 | -0.0024744 | -0.013268 | 0.010952 | 0.0056466 | 0.007488 | 0.0077131 | -0.0073111 | 0.038553 | 0.0035231 | 111.1551 | 0.95833 | 111.1431 | 111.7099 | 111.2545 | 111.5943 | 7.799 | -0.003531 | -0.036271 | -0.070087 | 0.093665 | 0.22432 | -0.17081 | -0.32441 | 18.7761 | -0.048572 | 122.1323 | 122.1203 | 103.3441 | -0.50393 | -0.16411 | 10.6528 | -111.6648 | 10.9736 | 10.9071 | 0.25432 | -111.5341 | -111.9292 | 122.687 | 122.2317 | 122.5715 | 11.9355 | -103.9595 | 11.0708 | 11.2015 | 10.8064 | 10.9409 | -112.0828
1439.25 | 122.6852 | -11.1374 | 111.5753 | 1.4211e-13 | -0.0046624 | -0.0011389 | -0.0026882 | -0.013482 | 0.010952 | 0.013277 | 0.0077016 | 0.0079267 | -0.0070975 | 0.038553 | 0.0037369 | 111.233 | 0.95833 | 111.2255 | 111.7968 | 111.3323 | 111.6996 | 7.799 | -0.00811 | -0.040849 | -0.074666 | 0.093665 | 0.22432 | -0.17539 | -0.32899 | 18.9363 | 0.22152 | 122.3704 | 122.3629 | 103.4265 | -0.24299 | 0.1243 | 10.8084 | -111.4817 | 11.1293 | 11.0627 | 0.25432 | -111.351 | -111.7507 | 122.9342 | 122.4697 | 122.837 | 12.0957 | -103.7764 | 11.2311 | 11.3617 | 10.962 | 11.0965 | -111.9043
1441.0156 | 122.8271 | -11.0046 | 111.6486 | 1.4211e-13 | -0.0044486 | -0.00071151 | -0.0024744 | -0.013482 | 0.01138 | -0.0019839 | 0.007488 | 0.0081403 | -0.0073111 | 0.039194 | 0.0037369 | 111.2605 | 0.9446 | 111.2438 | 111.8106 | 111.3644 | 111.6767 | 7.799 | -0.00811 | -0.040849 | -0.074666 | 0.089087 | 0.22432 | -0.17081 | -0.31983 | 18.8036 | 0.16201 | 122.2651 | 122.2484 | 103.4449 | -0.28418 | 0.028163 | 10.6848 | -111.5595 | 10.9965 | 10.93 | 0.24516 | -111.4242 | -111.8194 | 122.8152 | 122.369 | 122.6814 | 11.9492 | -103.8496 | 11.0937 | 11.229 | 10.8338 | 10.9638 | -111.9684
1442.7031 | 122.8271 | -10.817 | 111.8591 | 1.4211e-13 | -0.0046624 | -0.0013525 | -0.0022608 | -0.013696 | 0.011166 | 0.0056466 | 0.0079152 | 0.0079267 | -0.0070975 | 0.03898 | 0.0037369 | 111.4115 | 0.94918 | 111.404 | 111.98 | 111.5201 | 111.8416 | 7.7898 | -0.012689 | -0.040849 | -0.079245 | 0.093665 | 0.21974 | -0.17539 | -0.32899 | 18.6068 | 0.12084 | 122.2285 | 122.221 | 103.6142 | -0.33907 | -0.017578 | 10.488 | -111.7655 | 10.8043 | 10.7377 | 0.24974 | -111.6394 | -112.0345 | 122.7969 | 122.337 | 122.6585 | 11.7661 | -104.0693 | 10.9106 | 11.0367 | 10.6416 | 10.7761 | -112.1881
1444.4531 | 122.6807 | -10.7895 | 111.9781 | 1.4211e-13 | -0.0050896 | -0.0011389 | -0.0024744 | -0.013268 | 0.011166 | 0.013277 | 0.0077016 | 0.0079267 | -0.0070975 | 0.039194 | 0.0037369 | 111.4436 | 0.95376 | 111.4269 | 112.012 | 111.5475 | 111.9057 | 7.8035 | -0.00811 | -0.036271 | -0.070087 | 0.098244 | 0.21974 | -0.17081 | -0.32441 | 18.593 | 0.033875 | 122.2331 | 122.2164 | 103.6234 | -0.43061 | -0.072496 | 10.4651 | -111.8799 | 10.7814 | 10.7194 | 0.25432 | -111.7584 | -112.149 | 122.8015 | 122.337 | 122.6951 | 11.7432 | -104.1746 | 10.8877 | 11.0092 | 10.6187 | 10.7532 | -112.3026
1446.2031 | 122.7676 | -10.675 | 111.9827 | 1.4211e-13 | -0.0044486 | -0.00092531 | -0.0022608 | -0.013268 | 0.010952 | -0.0019839 | 0.0079152 | 0.0074993 | -0.0070975 | 0.039408 | 0.0037369 | 111.5993 | 0.95376 | 111.578 | 112.1677 | 111.7078 | 112.0201 | 7.799 | -0.00811 | -0.036271 | -0.070087 | 0.089087 | 0.2289 | -0.17081 | -0.32899 | 18.474 | 0.18496 | 122.2743 | 122.2531 | 103.7791 | -0.27492 | 0.037392 | 10.3461 | -111.8936 | 10.6669 | 10.605 | 0.2589 | -111.7538 | -112.1535 | 122.8427 | 122.3829 | 122.6952 | 11.6288 | -104.1838 | 10.7641 | 10.904 | 10.5042 | 10.6388 | -112.3117
1447.8906 | 122.6761 | -10.9726 | 111.7859 | 1.4211e-13 | -0.0044486 | -0.00092531 | -0.002047 | -0.013696 | 0.011166 | 0.020908 | 0.0077016 | 0.0081403 | -0.0070975 | 0.038767 | 0.0041641 | 111.4527 | 0.94918 | 111.4224 | 112.012 | 111.5567 | 111.9285 | 7.799 | -0.00811 | -0.040849 | -0.074666 | 0.093665 | 0.22432 | -0.17081 | -0.32441 | 18.7716 | 0.22613 | 122.4253 | 122.395 | 103.6234 | -0.22919 | 0.14266 | 10.6482 | -111.6922 | 10.9645 | 10.8979 | 0.24974 | -111.5616 | -111.9567 | 122.9846 | 122.5293 | 122.9011 | 11.9218 | -103.9869 | 11.0663 | 11.1969 | 10.8018 | 10.9317 | -112.1103
1449.6406 | 122.818 | -10.7758 | 111.8317 | 1.4211e-13 | -0.0044486 | -0.0011389 | -0.0026882 | -0.013696 | 0.011166 | 0.0056466 | 0.007488 | 0.0081403 | -0.0077383 | 0.038767 | 0.0039505 | 111.3932 | 0.95376 | 111.3628 | 111.9571 | 111.4972 | 111.8507 | 7.8035 | -0.003531 | -0.036271 | -0.074666 | 0.093665 | 0.22432 | -0.17081 | -0.32441 | 18.5793 | 0.12542 | 122.169 | 122.1386 | 103.5593 | -0.33449 | 0.019045 | 10.4513 | -111.738 | 10.7722 | 10.7011 | 0.24974 | -111.6073 | -112.0025 | 122.7328 | 122.2729 | 122.6265 | 11.7295 | -104.0281 | 10.8694 | 11.0001 | 10.6049 | 10.7395 | -112.1561
1451.375 | 122.6852 | -10.611 | 112.0743 | 1.4211e-13 | -0.0044486 | -0.0013525 | -0.0024744 | -0.013909 | 0.010952 | 0.0056466 | 0.0077016 | 0.0081403 | -0.0070975 | 0.038767 | 0.0037369 | 111.6725 | 0.96291 | 111.6101 | 112.2364 | 111.7719 | 112.0934 | 7.8081 | -0.00811 | -0.031692 | -0.079245 | 0.093665 | 0.22432 | -0.16624 | -0.32441 | 18.4191 | 0.16209 | 122.2835 | 122.221 | 103.802 | -0.30237 | 0.019096 | 10.2866 | -111.9806 | 10.6029 | 10.5317 | 0.24516 | -111.85 | -112.2405 | 122.8473 | 122.3829 | 122.7043 | 11.5739 | -104.2662 | 10.7046 | 10.8353 | 10.4447 | 10.5793 | -112.3987
1453.1094 | 122.6761 | -10.5377 | 112.2162 | 1.4211e-13 | -0.004876 | -0.0011389 | -0.0024744 | -0.013482 | 0.011166 | 0.013277 | 0.0077016 | 0.0077131 | -0.0075247 | 0.03898 | 0.0037369 | 111.8053 | 0.96291 | 111.7428 | 112.3646 | 111.9184 | 112.2719 | 7.7944 | -0.003531 | -0.036271 | -0.083823 | 0.093665 | 0.22432 | -0.17081 | -0.32899 | 18.3321 | 0.14837 | 122.343 | 122.2806 | 103.9485 | -0.29775 | 0.055755 | 10.2087 | -112.1225 | 10.5342 | 10.4539 | 0.24516 | -111.9919 | -112.387 | 122.9023 | 122.4562 | 122.8097 | 11.5006 | -104.4218 | 10.6314 | 10.762 | 10.3669 | 10.5014 | -112.5452
1454.8594 | 122.7081 | -10.5103 | 112.2299 | 1.4211e-13 | -0.0044486 | -0.0013525 | -0.0026882 | -0.013696 | 0.010739 | -0.0019839 | 0.0079152 | 0.0074993 | -0.0070975 | 0.03898 | 0.0035231 | 111.8236 | 0.96749 | 111.7474 | 112.3875 | 111.923 | 112.2582 | 7.7898 | 0.001048 | -0.040849 | -0.079245 | 0.093665 | 0.22432 | -0.17081 | -0.32899 | 18.3001 | 0.15753 | 122.3338 | 122.2577 | 103.9576 | -0.30691 | 0.028287 | 10.1813 | -112.1363 | 10.5113 | 10.431 | 0.24974 | -112.0056 | -112.4007 | 122.8977 | 122.4333 | 122.7685 | 11.4777 | -104.4401 | 10.6039 | 10.7346 | 10.3394 | 10.4694 | -112.5589
1456.5312 | 122.8043 | -10.6293 | 112.0468 | 1.4211e-13 | -0.0044486 | -0.0011389 | -0.0026882 | -0.013696 | 0.01138 | -0.0096144 | 0.007488 | 0.0077131 | -0.0077383 | 0.03898 | 0.0035231 | 111.7137 | 0.97207 | 111.633 | 112.2821 | 111.8223 | 112.1529 | 7.8035 | -0.003531 | -0.036271 | -0.070087 | 0.098244 | 0.2289 | -0.16624 | -0.32441 | 18.4328 | 0.23534 | 122.343 | 122.2622 | 103.8294 | -0.22454 | 0.10608 | 10.3049 | -111.9486 | 10.6257 | 10.5592 | 0.25432 | -111.8179 | -112.213 | 122.9114 | 122.4515 | 122.7822 | 11.6013 | -104.2433 | 10.7275 | 10.8582 | 10.463 | 10.593 | -112.3712
1458.2812 | 122.6532 | -10.8536 | 111.882 | 1.4211e-13 | -0.0044486 | -0.0011389 | -0.0024744 | -0.013696 | 0.010952 | 0.0056466 | 0.007488 | 0.0077131 | -0.0070975 | 0.039194 | 0.0039505 | 111.5535 | 0.95833 | 111.459 | 112.1265 | 111.662 | 111.9789 | 7.8081 | -0.003531 | -0.031692 | -0.074666 | 0.10282 | 0.23806 | -0.17539 | -0.32441 | 18.6617 | 0.24447 | 122.407 | 122.3126 | 103.6509 | -0.22001 | 0.096892 | 10.5292 | -111.7792 | 10.85 | 10.7789 | 0.24974 | -111.644 | -112.0574 | 122.9801 | 122.5156 | 122.8325 | 11.8119 | -104.0739 | 10.9564 | 11.0916 | 10.6782 | 10.8219 | -112.2064
1459.9531 | 122.6807 | -10.7712 | 111.9553 | 1.4211e-13 | -0.0046624 | -0.0011389 | -0.0024744 | -0.013696 | 0.011166 | -0.0019839 | 0.0077016 | 0.0079267 | -0.0073111 | 0.039408 | 0.0037369 | 111.5764 | 0.97207 | 111.4727 | 112.1494 | 111.6895 | 111.9835 | 7.8035 | 0.001048 | -0.040849 | -0.070087 | 0.093665 | 0.23348 | -0.17539 | -0.32441 | 18.5747 | 0.19412 | 122.3475 | 122.2439 | 103.6692 | -0.26577 | 0.028229 | 10.4468 | -111.8616 | 10.7722 | 10.7011 | 0.25432 | -111.7218 | -112.1307 | 122.9206 | 122.4607 | 122.7547 | 11.7432 | -104.1517 | 10.8648 | 11.0047 | 10.5958 | 10.7303 | -112.2797
1461.7031 | 122.8043 | -10.8398 | 111.8042 | 1.4211e-13 | -0.0050896 | -0.0013525 | -0.0024744 | -0.013482 | 0.010525 | 0.013277 | 0.0072744 | 0.0079267 | -0.0066701 | 0.039194 | 0.0033095 | 111.4985 | 0.96749 | 111.3995 | 112.0624 | 111.6071 | 111.9606 | 7.8127 | -0.00811 | -0.036271 | -0.070087 | 0.098244 | 0.22432 | -0.17081 | -0.32441 | 18.6525 | 0.25819 | 122.3384 | 122.2393 | 103.5868 | -0.19713 | 0.1564 | 10.5154 | -111.706 | 10.8317 | 10.7698 | 0.25432 | -111.5799 | -111.975 | 122.9022 | 122.4469 | 122.8004 | 11.8073 | -103.9915 | 10.9381 | 11.0642 | 10.669 | 10.8036 | -112.1286
1463.375 | 122.7127 | -10.6247 | 112.1155 | 1.4211e-13 | -0.0044486 | -0.0013525 | -0.0026882 | -0.013482 | 0.01138 | 0.013277 | 0.007488 | 0.0077131 | -0.0073111 | 0.039408 | 0.0037369 | 111.6267 | 0.98581 | 111.4865 | 112.1997 | 111.7444 | 112.0705 | 7.7944 | -0.012689 | -0.031692 | -0.070087 | 0.098244 | 0.21974 | -0.17081 | -0.32441 | 18.4191 | 0.084259 | 122.2514 | 122.1112 | 103.6921 | -0.37105 | -0.044996 | 10.3003 | -112.0172 | 10.612 | 10.5546 | 0.25432 | -111.8957 | -112.2863 | 122.8244 | 122.3691 | 122.6952 | 11.6105 | -104.3211 | 10.7229 | 10.8444 | 10.4539 | 10.593 | -112.4399
1465.125 | 122.7814 | -10.8124 | 111.8774 | 1.4211e-13 | -0.004235 | -0.0011389 | -0.0024744 | -0.013482 | 0.011593 | -0.0019839 | 0.007488 | 0.0077131 | -0.0070975 | 0.03898 | 0.0035231 | 111.5901 | 0.99038 | 111.3903 | 112.1631 | 111.7078 | 112.0659 | 7.8081 | -0.003531 | -0.045428 | -0.070087 | 0.098244 | 0.23348 | -0.17081 | -0.33357 | 18.6205 | 0.28567 | 122.4025 | 122.2027 | 103.5822 | -0.16964 | 0.18846 | 10.4788 | -111.7792 | 10.8088 | 10.7423 | 0.26348 | -111.644 | -112.0483 | 122.9755 | 122.5202 | 122.8783 | 11.8028 | -104.0693 | 10.9106 | 11.0459 | 10.6416 | 10.767 | -112.211
1466.875 | 122.6761 | -10.7254 | 112.0377 | 1.4211e-13 | -0.0044486 | -0.0013525 | -0.0024744 | -0.013696 | 0.01138 | 0.0056466 | 0.0077016 | 0.0077131 | -0.0075247 | 0.039194 | 0.0037369 | 111.5352 | 0.98123 | 111.1934 | 112.1036 | 111.6483 | 112.0247 | 7.8081 | 0.005626 | -0.031692 | -0.074666 | 0.089087 | 0.2289 | -0.17081 | -0.31525 | 18.5335 | 0.065933 | 122.2606 | 121.9189 | 103.3853 | -0.38938 | -0.012962 | 10.4102 | -111.9486 | 10.731 | 10.6507 | 0.24058 | -111.8088 | -112.2085 | 122.829 | 122.3737 | 122.7501 | 11.7066 | -104.2295 | 10.8145 | 10.9543 | 10.5546 | 10.6937 | -112.3529
1468.5625 | 122.8134 | -10.3409 | 112.3306 | 1.4211e-13 | -0.0040214 | -0.0011389 | -0.0029018 | -0.013696 | 0.01138 | 0.013277 | 0.0077016 | 0.0077131 | -0.0070975 | 0.039408 | 0.0035231 | 111.9014 | 0.99954 | 111.4544 | 112.4699 | 112.01 | 112.3956 | 7.799 | 0.001048 | -0.045428 | -0.079245 | 0.089087 | 0.2289 | -0.16624 | -0.33357 | 18.1398 | 0.13924 | 122.2423 | 121.7953 | 103.6555 | -0.32062 | 0.064937 | 10.0073 | -112.2415 | 10.3419 | 10.2616 | 0.25432 | -112.1017 | -112.4969 | 122.8107 | 122.3509 | 122.7364 | 11.3404 | -104.5317 | 10.43 | 10.5698 | 10.1746 | 10.2955 | -112.6642
1470.3125 | 122.8271 | -10.4416 | 112.2116 | 1.4211e-13 | -0.0044486 | -0.0013525 | -0.0024744 | -0.013909 | 0.01138 | 0.013277 | 0.0077016 | 0.0079267 | -0.0070975 | 0.03898 | 0.0037369 | 111.8968 | 0.99038 | 111.3216 | 112.4744 | 112.0146 | 112.4139 | 7.799 | -0.00811 | -0.040849 | -0.074666 | 0.093665 | 0.22432 | -0.17081 | -0.32441 | 18.2405 | 0.26283 | 122.3384 | 121.7632 | 103.5227 | -0.19702 | 0.20227 | 10.1172 | -112.1179 | 10.4335 | 10.3669 | 0.24974 | -111.9873 | -112.3824 | 122.916 | 122.4562 | 122.8555 | 11.432 | -104.4127 | 10.5353 | 10.6659 | 10.2708 | 10.4007 | -112.536
1472.0625 | 122.8134 | -10.3134 | 112.3489 | 1.4211e-13 | -0.004235 | -0.00092531 | -0.0024744 | -0.013909 | 0.011166 | 0.013277 | 0.007488 | 0.0079267 | -0.0073111 | 0.03898 | 0.0037369 | 111.9564 | 0.99954 | 111.4498 | 112.5202 | 112.0695 | 112.4276 | 7.799 | -0.003531 | -0.045428 | -0.070087 | 0.10282 | 0.22432 | -0.17997 | -0.32441 | 18.1124 | 0.17129 | 122.2698 | 121.7632 | 103.6509 | -0.2794 | 0.078676 | 9.989 | -112.2461 | 10.3099 | 10.2433 | 0.25432 | -112.1246 | -112.5289 | 122.8336 | 122.383 | 122.741 | 11.313 | -104.55 | 10.4162 | 10.5377 | 10.1334 | 10.268 | -112.6733
1473.75 | 122.7173 | -10.2859 | 112.4634 | 1.4211e-13 | -0.0040214 | -0.0011389 | -0.0024744 | -0.014337 | 0.01138 | -0.0019839 | 0.0077016 | 0.0079267 | -0.0073111 | 0.039194 | 0.0037369 | 112.0067 | 0.99038 | 111.3308 | 112.5889 | 112.1245 | 112.4917 | 7.8081 | -0.003531 | -0.036271 | -0.074666 | 0.098244 | 0.2289 | -0.17081 | -0.31983 | 18.0941 | 0.12552 | 122.2927 | 121.6167 | 103.5227 | -0.3389 | 0.028336 | 9.9661 | -112.3651 | 10.2824 | 10.2113 | 0.24516 | -112.2345 | -112.6342 | 122.8749 | 122.4104 | 122.7777 | 11.2763 | -104.6553 | 10.3842 | 10.5149 | 10.1151 | 10.2497 | -112.7832
1475.5156 | 122.6852 | -10.1257 | 112.6282 | 1.4211e-13 | -0.0040214 | -0.0011389 | -0.0026882 | -0.014123 | 0.011807 | -0.0019839 | 0.0072744 | 0.0074993 | -0.0073111 | 0.039194 | 0.0033095 | 112.1807 | 1.0041 | 111.3537 | 112.7537 | 112.2985 | 112.684 | 7.8081 | -0.003531 | -0.036271 | -0.079245 | 0.098244 | 0.23348 | -0.17997 | -0.32899 | 17.9338 | 0.12555 | 122.3064 | 121.4794 | 103.5456 | -0.32969 | 0.055842 | 9.7967 | -112.5299 | 10.1222 | 10.0465 | 0.24974 | -112.3947 | -112.8081 | 122.8795 | 122.4242 | 122.8097 | 11.1299 | -104.8201 | 10.224 | 10.3592 | 9.9458 | 10.0895 | -112.9572
1477.2188 | 122.7356 | -10.0754 | 112.6328 | 1.4211e-13 | -0.004235 | -0.0013525 | -0.0024744 | -0.014123 | 0.012021 | -0.0019839 | 0.0077016 | 0.0079267 | -0.0070975 | 0.038767 | 0.0033095 | 112.2448 | 0.99038 | 111.3812 | 112.827 | 112.358 | 112.7115 | 7.8035 | -0.00811 | -0.036271 | -0.079245 | 0.089087 | 0.23348 | -0.17081 | -0.32441 | 17.8789 | 0.19423 | 122.3202 | 121.4565 | 103.5776 | -0.27474 | 0.078736 | 9.751 | -112.5437 | 10.0673 | 9.9961 | 0.24516 | -112.3993 | -112.8036 | 122.9024 | 122.4334 | 122.7869 | 11.0658 | -104.8292 | 10.1645 | 10.3089 | 9.9046 | 10.0391 | -112.9572
1478.9844 | 122.6669 | -10.0983 | 112.6556 | 1.4211e-13 | -0.0038076 | -0.0013525 | -0.0026882 | -0.014337 | 0.012021 | -0.0096144 | 0.0077016 | 0.0079267 | -0.0073111 | 0.038767 | 0.0037369 | 112.2906 | 0.99954 | 111.2987 | 112.8636 | 112.4038 | 112.7252 | 7.8997 | -0.012689 | -0.036271 | -0.070087 | 0.10282 | 0.23348 | -0.16624 | -0.32441 | 17.998 | 0.20797 | 122.3889 | 121.397 | 103.3991 | -0.25184 | 0.069583 | 9.7739 | -112.5528 | 10.0856 | 10.0282 | 0.25432 | -112.4222 | -112.8219 | 122.9619 | 122.5021 | 122.8235 | 11.0978 | -104.7559 | 10.2011 | 10.3317 | 9.932 | 10.062 | -112.98
1480.6562 | 122.699 | -10.1486 | 112.5778 | 1.4211e-13 | -0.0040214 | -0.0011389 | -0.0026882 | -0.01455 | 0.011593 | 0.0056466 | 0.007488 | 0.0079267 | -0.0077383 | 0.039194 | 0.0039505 | 112.0846 | 1.1415 | 110.9737 | 112.653 | 112.1977 | 112.5924 | 7.8173 | -0.00811 | -0.040849 | -0.079245 | 0.093665 | 0.2289 | -0.17539 | -0.32899 | 17.9659 | 0.075179 | 122.2332 | 121.1223 | 103.1564 | -0.38007 | 0.014624 | 9.8196 | -112.4842 | 10.1405 | 10.0694 | 0.24974 | -112.3489 | -112.7532 | 122.8016 | 122.3464 | 122.7411 | 11.2901 | -104.7605 | 10.2423 | 10.3775 | 9.9732 | 10.1078 | -112.9068
1482.4062 | 122.7036 | -10.0891 | 112.619 | 1.4211e-13 | -0.003594 | -0.0011389 | -0.0026882 | -0.014123 | 0.011807 | 0.0056466 | 0.0077016 | 0.0074993 | -0.0068837 | 0.039194 | 0.0035231 | 112.1624 | 1.1506 | 111.0012 | 112.7354 | 112.2756 | 112.652 | 7.8035 | -0.003531 | -0.040849 | -0.070087 | 0.093665 | 0.22432 | -0.17081 | -0.32441 | 17.8926 | 0.11639 | 122.2515 | 121.0903 | 103.1976 | -0.34343 | 0.032947 | 9.7647 | -112.5254 | 10.0856 | 10.019 | 0.25432 | -112.3947 | -112.7898 | 122.8245 | 122.3647 | 122.7411 | 11.2397 | -104.8155 | 10.1828 | 10.3134 | 9.9183 | 10.0483 | -112.9434
1484.0938 | 122.7081 | -10.2722 | 112.4313 | 1.4211e-13 | -0.0033802 | -0.00092531 | -0.0024744 | -0.01455 | 0.011807 | 0.013277 | 0.0077016 | 0.0079267 | -0.0075247 | 0.039408 | 0.0035231 | 112.0617 | 1.1552 | 110.7127 | 112.6393 | 112.1749 | 112.5741 | 7.8127 | -0.003531 | -0.036271 | -0.074666 | 0.093665 | 0.23348 | -0.16624 | -0.32441 | 18.0849 | 0.20793 | 122.3339 | 120.9849 | 102.9 | -0.25648 | 0.14279 | 9.9478 | -112.3377 | 10.2687 | 10.1976 | 0.24974 | -112.1979 | -112.5976 | 122.9115 | 122.4471 | 122.8463 | 11.4274 | -104.6186 | 10.3659 | 10.5057 | 10.106 | 10.2359 | -112.7557
1485.8281 | 122.6944 | -10.1578 | 112.5458 | 1.4211e-13 | -0.0033802 | -0.0011389 | -0.0029018 | -0.014764 | 0.012021 | 0.0056466 | 0.0079152 | 0.0081403 | -0.0077383 | 0.039194 | 0.0037369 | 112.0937 | 1.1415 | 110.5754 | 112.6622 | 112.2069 | 112.5924 | 7.8127 | -0.012689 | -0.036271 | -0.070087 | 0.098244 | 0.23348 | -0.17539 | -0.32441 | 17.9705 | 0.11638 | 122.2515 | 120.7332 | 102.7627 | -0.33887 | 0.046668 | 9.8334 | -112.4475 | 10.1451 | 10.0877 | 0.25432 | -112.3123 | -112.7212 | 122.8199 | 122.3647 | 122.7502 | 11.2993 | -104.7331 | 10.256 | 10.3913 | 9.9824 | 10.1215 | -112.8702
1487.5625 | 122.699 | -10.0708 | 112.5961 | 1.4211e-13 | -0.003594 | -0.0015663 | -0.0022608 | -0.01455 | 0.012021 | 0.0056466 | 0.0077016 | 0.0077131 | -0.0075247 | 0.03898 | 0.0037369 | 112.1899 | 1.1461 | 110.6212 | 112.7583 | 112.2985 | 112.6749 | 7.8081 | -0.003531 | -0.040849 | -0.074666 | 0.089087 | 0.23348 | -0.16624 | -0.33357 | 17.8789 | 0.16217 | 122.2607 | 120.692 | 102.813 | -0.29765 | 0.078729 | 9.7372 | -112.507 | 10.0673 | 9.9961 | 0.2589 | -112.3627 | -112.7624 | 122.8291 | 122.3693 | 122.7457 | 11.2169 | -104.788 | 10.1599 | 10.3043 | 9.9046 | 10.03 | -112.9297
1489.2969 | 122.7905 | -10.0662 | 112.5641 | 1.4211e-13 | -0.0031666 | -0.00092531 | -0.0026882 | -0.014978 | 0.012448 | 0.0056466 | 0.0077016 | 0.0081403 | -0.0075247 | 0.039408 | 0.0035231 | 112.1532 | 1.1461 | 110.2045 | 112.7263 | 112.2802 | 112.6382 | 7.8081 | -0.012689 | -0.040849 | -0.079245 | 0.098244 | 0.23348 | -0.17539 | -0.31983 | 17.8743 | 0.16217 | 122.2195 | 120.2708 | 102.3964 | -0.28392 | 0.074143 | 9.7464 | -112.4658 | 10.0535 | 9.987 | 0.24058 | -112.3306 | -112.7395 | 122.7925 | 122.3464 | 122.7045 | 11.2123 | -104.756 | 10.1645 | 10.2997 | 9.8908 | 10.0254 | -112.8839
1491.0469 | 122.6532 | -10.1578 | 112.5732 | 1.4211e-13 | -0.0033802 | -0.0013525 | -0.0026882 | -0.014978 | 0.012021 | -0.0019839 | 0.0072744 | 0.0081403 | -0.0068837 | 0.038767 | 0.0035231 | 112.1166 | 1.1552 | 110.2824 | 112.6805 | 112.2252 | 112.5787 | 7.8035 | -0.00811 | -0.045428 | -0.065509 | 0.098244 | 0.22432 | -0.17081 | -0.33357 | 17.9613 | 0.10723 | 122.2744 | 120.4401 | 102.4788 | -0.34802 | 0.005466 | 9.8242 | -112.475 | 10.1497 | 10.0923 | 0.26806 | -112.3489 | -112.7441 | 122.8382 | 122.383 | 122.7365 | 11.313 | -104.7697 | 10.256 | 10.3821 | 9.987 | 10.1123 | -112.9068
1492.7188 | 122.7356 | -10.2264 | 112.4176 | 1.4211e-13 | -0.003594 | -0.00092531 | -0.0024744 | -0.014764 | 0.012234 | 0.013277 | 0.007488 | 0.0077131 | -0.0075247 | 0.03898 | 0.0030959 | 112.0525 | 1.1552 | 110.1588 | 112.6255 | 112.1794 | 112.5375 | 7.8035 | -0.003531 | -0.040849 | -0.070087 | 0.093665 | 0.22432 | -0.17539 | -0.33357 | 18.03 | 0.20793 | 122.279 | 120.3852 | 102.3552 | -0.23817 | 0.1199 | 9.8929 | -112.3239 | 10.2229 | 10.1564 | 0.26348 | -112.1933 | -112.593 | 122.852 | 122.4059 | 122.7639 | 11.3817 | -104.6141 | 10.3201 | 10.4508 | 10.051 | 10.1856 | -112.7512
1494.4688 | 122.7814 | -10.1074 | 112.5641 | 1.4211e-13 | -0.0027392 | -0.0013525 | -0.0026882 | -0.015405 | 0.012662 | 0.0056466 | 0.007488 | 0.0074993 | -0.0070975 | 0.03898 | 0.0035231 | 112.167 | 1.1598 | 109.8932 | 112.7446 | 112.2847 | 112.6382 | 7.8035 | -0.00811 | -0.045428 | -0.070087 | 0.093665 | 0.22432 | -0.17539 | -0.32899 | 17.911 | 0.18048 | 122.2744 | 120.0006 | 102.0897 | -0.27934 | 0.074143 | 9.7784 | -112.4704 | 10.0993 | 10.0373 | 0.2589 | -112.3398 | -112.7395 | 122.852 | 122.3922 | 122.7457 | 11.2672 | -104.7606 | 10.2011 | 10.3317 | 9.932 | 10.062 | -112.8931
1496.2188 | 122.731 | -10.1532 | 112.4817 | 1.4211e-13 | -0.002953 | -0.0011389 | -0.0022608 | -0.014978 | 0.012662 | 0.0056466 | 0.007488 | 0.0077131 | -0.0070975 | 0.038767 | 0.0030959 | 112.2173 | 1.1506 | 110.0626 | 112.7949 | 112.3397 | 112.7481 | 7.8127 | -0.012689 | -0.036271 | -0.074666 | 0.098244 | 0.22432 | -0.17539 | -0.32441 | 17.9659 | 0.31324 | 122.3705 | 120.2158 | 102.2499 | -0.142 | 0.26643 | 9.8288 | -112.3834 | 10.1405 | 10.0785 | 0.24974 | -112.2574 | -112.6571 | 122.9481 | 122.4929 | 122.9013 | 11.3038 | -104.669 | 10.2514 | 10.3775 | 9.9778 | 10.1169 | -112.8061
1497.9062 | 122.6944 | -10.0937 | 112.5824 | 1.4211e-13 | -0.0027392 | -0.0011389 | -0.0026882 | -0.015405 | 0.012662 | 0.0056466 | 0.007488 | 0.0074993 | -0.0070975 | 0.03898 | 0.0033095 | 112.2356 | 1.1644 | 110.0351 | 112.8087 | 112.3626 | 112.7252 | 7.8081 | -0.003531 | -0.040849 | -0.079245 | 0.093665 | 0.22432 | -0.17539 | -0.33357 | 17.9018 | 0.22627 | 122.3293 | 120.1288 | 102.227 | -0.21981 | 0.14283 | 9.7601 | -112.4887 | 10.0902 | 10.0144 | 0.25432 | -112.3581 | -112.7578 | 122.9024 | 122.4563 | 122.8189 | 11.2581 | -104.7743 | 10.1874 | 10.318 | 9.9183 | 10.0528 | -112.916
1499.6562 | 122.6624 | -10.1486 | 112.5504 | 1.4211e-13 | -0.0025256 | -0.0013525 | -0.0026882 | -0.015191 | 0.012875 | 0.0056466 | 0.0077016 | 0.0077131 | -0.0070975 | 0.038767 | 0.0030959 | 112.1487 | 1.1598 | 109.7238 | 112.7263 | 112.2847 | 112.6062 | 7.8035 | -0.00811 | -0.040849 | -0.074666 | 0.098244 | 0.21974 | -0.16624 | -0.33357 | 17.9522 | 0.1759 | 122.2973 | 119.8724 | 101.9203 | -0.26561 | 0.055826 | 9.8151 | -112.4521 | 10.1405 | 10.074 | 0.2589 | -112.3306 | -112.7166 | 122.8749 | 122.4334 | 122.7548 | 11.3084 | -104.7468 | 10.2469 | 10.3684 | 9.9824 | 10.1078 | -112.8839
1501.4219 | 122.7081 | -13.4354 | 109.2316 | 1.4211e-13 | 0.073328 | -0.00092531 | -0.0024744 | -0.093606 | 0.088939 | 0.0056466 | 0.0079152 | 0.0081403 | -0.0075247 | 0.039621 | 0.0037369 | 108.7011 | 0.7523 | 3.4116 | 109.265 | 108.878 | 109.2226 | 7.8676 | -0.003531 | -0.036271 | -0.065509 | 0.089087 | 0.2289 | -0.16624 | -0.32441 | 21.303 | 0.033425 | 122.1365 | 16.8469 | -4.4561 | -0.35354 | -0.008975 | 13.111 | -109.1425 | 13.4318 | 13.3699 | 0.2589 | -109.0027 | -109.3978 | 122.7004 | 122.3134 | 122.658 | 14.1877 | -101.3639 | 13.5245 | 13.6643 | 13.2691 | 13.3991 | -109.556
1503.1719 | 122.6944 | -12.3642 | 110.3119 | 1.4211e-13 | 0.075038 | -0.0011389 | -0.0029018 | -0.095529 | 0.090649 | 0.0056466 | 0.0072744 | 0.0083539 | -0.0070975 | 0.03898 | 0.0033095 | 109.8732 | 0.77977 | 2.2349 | 110.46 | 109.9953 | 110.3764 | 7.799 | -0.00811 | -0.031692 | -0.070087 | 0.098244 | 0.23806 | -0.16624 | -0.32899 | 20.1632 | 0.14806 | 122.2374 | 14.5991 | -5.564 | -0.31661 | 0.06451 | 12.0352 | -110.2136 | 12.3561 | 12.2941 | 0.2589 | -110.0738 | -110.4781 | 122.8241 | 122.3595 | 122.7406 | 13.144 | -102.5129 | 12.4624 | 12.6023 | 12.198 | 12.3325 | -110.6409
1504.9219 | 122.6761 | -8.9264 | 113.7588 | 1.4211e-13 | 0.077388 | -0.0011389 | -0.0022608 | -0.097665 | 0.092785 | -0.0019839 | 0.0072744 | 0.0081403 | -0.0070975 | 0.038767 | 0.0033095 | 113.2887 | 0.83929 | 2.18 | 113.8937 | 113.4432 | 113.8332 | 7.8035 | 0.005626 | -0.040849 | -0.079245 | 0.098244 | 0.22432 | -0.17081 | -0.32441 | 16.7299 | 0.13489 | 122.2151 | 11.1064 | -5.6235 | -0.31564 | 0.074395 | 8.602 | -113.6606 | 8.932 | 8.8471 | 0.24516 | -113.5345 | -113.9297 | 122.8201 | 122.3696 | 122.7596 | 9.7657 | -105.9553 | 9.0246 | 9.1507 | 8.7556 | 8.8855 | -114.0833
1506.6094 | 122.6257 | -8.9905 | 113.7085 | 1.4211e-13 | 0.077174 | -0.00092531 | -0.0022608 | -0.097665 | 0.092785 | 0.0056466 | 0.007488 | 0.0077131 | -0.0073111 | 0.039194 | 0.0035231 | 113.2154 | 0.67446 | 2.2121 | 113.8159 | 113.3516 | 113.7875 | 7.8219 | -0.003531 | -0.036271 | -0.070087 | 0.093665 | 0.23348 | -0.17081 | -0.32441 | 16.8123 | 0.10741 | 122.2059 | 11.2025 | -5.6098 | -0.35686 | 0.078963 | 8.6661 | -113.6148 | 8.9869 | 8.9204 | 0.25432 | -113.475 | -113.8793 | 122.8064 | 122.3421 | 122.7779 | 9.6649 | -105.8866 | 9.0841 | 9.224 | 8.8197 | 8.9542 | -114.0329
1508.3438 | 122.6578 | -9.0866 | 113.5941 | 1.4211e-13 | 0.077174 | -0.00092531 | -0.0026882 | -0.098306 | 0.092358 | 0.013277 | 0.0079152 | 0.0081403 | -0.0075247 | 0.03898 | 0.0035231 | 113.1376 | 0.6882 | 2.2029 | 113.7381 | 113.283 | 113.6455 | 7.8173 | -0.003531 | -0.045428 | -0.074666 | 0.089087 | 0.2289 | -0.17081 | -0.32441 | 16.9039 | 0.14402 | 122.2242 | 11.2895 | -5.6144 | -0.3111 | 0.051467 | 8.7622 | -113.505 | 9.0831 | 9.0119 | 0.24974 | -113.3652 | -113.7649 | 122.8247 | 122.3696 | 122.7321 | 9.7748 | -105.7768 | 9.1757 | 9.3155 | 8.9158 | 9.0412 | -113.9185
1510.0781 | 122.644 | -9.1049 | 113.5986 | 1.4211e-13 | 0.076747 | -0.0011389 | -0.0024744 | -0.097879 | 0.092572 | 0.0056466 | 0.0072744 | 0.0077131 | -0.0070975 | 0.039194 | 0.0028821 | 113.0826 | 0.68362 | 2.267 | 113.6877 | 113.2234 | 113.6455 | 7.8722 | 0.001048 | -0.040849 | -0.074666 | 0.10282 | 0.22432 | -0.17081 | -0.31983 | 16.9771 | 0.089081 | 122.1876 | 11.3719 | -5.6052 | -0.37521 | 0.046889 | 8.7851 | -113.4958 | 9.106 | 9.0303 | 0.24516 | -113.3743 | -113.7694 | 122.7926 | 122.3283 | 122.7504 | 9.7885 | -105.7264 | 9.2077 | 9.3292 | 8.9341 | 9.0641 | -113.9185
1511.8281 | 122.7173 | -8.9951 | 113.6719 | 1.4211e-13 | 0.076961 | -0.0011389 | -0.0026882 | -0.097452 | 0.092358 | -0.0019839 | 0.0072744 | 0.0079267 | -0.0073111 | 0.03898 | 0.0030959 | 113.1834 | 0.6882 | 2.4089 | 113.7793 | 113.3287 | 113.6867 | 7.799 | -0.003531 | -0.040849 | -0.074666 | 0.098244 | 0.2289 | -0.16624 | -0.32441 | 16.794 | 0.10741 | 122.1784 | 11.404 | -5.39 | -0.34313 | 0.014855 | 8.6706 | -113.5736 | 8.9915 | 8.9204 | 0.24974 | -113.443 | -113.8381 | 122.7743 | 122.3238 | 122.6818 | 9.6833 | -105.8729 | 9.0933 | 9.224 | 8.8288 | 8.9542 | -113.9963
1513.5156 | 122.6898 | -9.5489 | 113.1638 | 1.4211e-13 | 0.076533 | -0.00092531 | -0.0024744 | -0.097452 | 0.091931 | -0.0019839 | 0.0077016 | 0.0077131 | -0.0073111 | 0.039408 | 0.0028821 | 112.7896 | 0.68362 | 2.4364 | 113.3855 | 112.935 | 113.325 | 7.8081 | 0.001048 | -0.040849 | -0.074666 | 0.10282 | 0.23348 | -0.17539 | -0.32899 | 17.3571 | 0.22178 | 122.3386 | 11.9853 | -5.3717 | -0.2288 | 0.16126 | 9.22 | -113.0609 | 9.55 | 9.4743 | 0.25432 | -112.9303 | -113.3392 | 122.9345 | 122.4839 | 122.874 | 10.2326 | -105.3556 | 9.6518 | 9.7824 | 9.3736 | 9.5081 | -113.4927
1515.25 | 122.6898 | -12.2726 | 110.408 | 1.4211e-13 | 0.073969 | -0.0011389 | -0.0022608 | -0.094888 | 0.089794 | 0.0056466 | 0.0077016 | 0.0079267 | -0.0073111 | 0.038767 | 0.0035231 | 109.8686 | 0.64699 | 2.441 | 110.405 | 109.9907 | 110.3535 | 7.8493 | 0.001048 | -0.040849 | -0.070087 | 0.093665 | 0.23348 | -0.17539 | -0.32441 | 20.122 | -0.00301 | 122.1413 | 14.7136 | -5.4084 | -0.41731 | -0.054513 | 11.9482 | -110.3144 | 12.2737 | 12.2026 | 0.25432 | -110.1745 | -110.5834 | 122.6777 | 122.2633 | 122.6262 | 12.9196 | -102.5587 | 12.3663 | 12.5061 | 12.0973 | 12.2318 | -110.7324
1517 | 122.6715 | -10.8353 | 111.8408 | 1.4211e-13 | 0.075251 | -0.0011389 | -0.0026882 | -0.09617 | 0.091076 | 0.013277 | 0.007488 | 0.0081403 | -0.0073111 | 0.03898 | 0.0035231 | 111.3749 | 0.6653 | 2.4043 | 111.9754 | 111.5201 | 111.924 | 7.8493 | -0.00811 | -0.036271 | -0.079245 | 0.093665 | 0.23348 | -0.16624 | -0.33357 | 18.6846 | 0.13458 | 122.2102 | 13.2396 | -5.445 | -0.32075 | 0.083148 | 10.5017 | -111.7472 | 10.8272 | 10.756 | 0.25432 | -111.6073 | -112.0071 | 122.8107 | 122.3553 | 122.7592 | 11.5006 | -103.9915 | 10.9289 | 11.0687 | 10.669 | 10.799 | -112.1744
1518.7344 | 122.7219 | -7.6538 | 115.0635 | 1.4211e-13 | 0.077816 | -0.00071151 | -0.0026882 | -0.098093 | 0.093426 | 0.0056466 | 0.0072744 | 0.0081403 | -0.0070975 | 0.039621 | 0.0033095 | 114.5889 | 0.68362 | 2.5051 | 115.2077 | 114.7574 | 115.1153 | 7.8035 | -0.00811 | -0.045428 | -0.070087 | 0.098244 | 0.23348 | -0.17539 | -0.33357 | 15.4573 | 0.14426 | 122.2427 | 10.1589 | -5.2985 | -0.30611 | 0.051777 | 7.3202 | -114.9652 | 7.6457 | 7.5837 | 0.26348 | -114.83 | -115.2389 | 122.8615 | 122.4112 | 122.7691 | 8.3374 | -107.2599 | 7.7521 | 7.8873 | 7.4784 | 7.6084 | -115.397
1520.4844 | 122.7173 | -7.5439 | 115.1184 | 1.4211e-13 | 0.077174 | -0.00092531 | -0.0022608 | -0.098306 | 0.092785 | -0.0019839 | 0.0077016 | 0.0077131 | -0.0073111 | 0.039194 | 0.0035231 | 114.5981 | 0.67904 | 2.5737 | 115.2169 | 114.7757 | 115.1198 | 7.8035 | -0.00811 | -0.036271 | -0.070087 | 0.098244 | 0.22432 | -0.17539 | -0.32441 | 15.3475 | 0.098488 | 122.142 | 10.1177 | -5.2298 | -0.34273 | 0.001424 | 7.2195 | -115.0202 | 7.5358 | 7.4739 | 0.25432 | -114.8941 | -115.2938 | 122.7608 | 122.3196 | 122.6638 | 8.223 | -107.3149 | 7.6422 | 7.7683 | 7.3686 | 7.5077 | -115.4428
1522.1719 | 122.7219 | -9.1507 | 113.5071 | 1.4211e-13 | 0.07632 | -0.00092531 | -0.0024744 | -0.097238 | 0.091503 | 0.0056466 | 0.0077016 | 0.0079267 | -0.0075247 | 0.039194 | 0.0033095 | 112.9911 | 0.6653 | 2.5417 | 113.587 | 113.141 | 113.4349 | 7.8035 | 0.001048 | -0.045428 | -0.070087 | 0.093665 | 0.23806 | -0.17539 | -0.33814 | 16.9542 | 0.07991 | 122.1418 | 11.6924 | -5.2618 | -0.36607 | -0.072173 | 8.8126 | -113.4134 | 9.1517 | 9.0806 | 0.26806 | -113.269 | -113.6825 | 122.7377 | 122.2917 | 122.5856 | 9.816 | -105.7035 | 9.2444 | 9.3888 | 8.9753 | 9.1053 | -113.8452
1523.9062 | 122.7493 | -8.519 | 114.1479 | 1.4211e-13 | 0.076747 | -0.0013525 | -0.0022608 | -0.097238 | 0.091503 | 0.0056466 | 0.0072744 | 0.0077131 | -0.0073111 | 0.039194 | 0.0028821 | 113.6595 | 0.6653 | 2.5554 | 114.2554 | 113.8095 | 114.1629 | 7.8035 | -0.00811 | -0.036271 | -0.074666 | 0.10282 | 0.2289 | -0.17081 | -0.33357 | 16.3225 | 0.10748 | 122.1785 | 11.0744 | -5.2481 | -0.33842 | 0.014955 | 8.1854 | -114.0451 | 8.5109 | 8.4443 | 0.2589 | -113.919 | -114.3188 | 122.7744 | 122.3285 | 122.6819 | 9.1843 | -106.3444 | 8.6218 | 8.7479 | 8.3482 | 8.4827 | -114.4815
1525.6562 | 122.6578 | -7.9514 | 114.8117 | 1.4211e-13 | 0.076533 | -0.00092531 | -0.0024744 | -0.097238 | 0.092358 | -0.0019839 | 0.0077016 | 0.0079267 | -0.0073111 | 0.039408 | 0.0033095 | 114.2913 | 0.66988 | 2.734 | 114.901 | 114.4781 | 114.8589 | 7.8173 | -0.00811 | -0.031692 | -0.070087 | 0.093665 | 0.23348 | -0.17539 | -0.32899 | 15.7686 | 0.08928 | 122.2427 | 10.6853 | -5.0833 | -0.33366 | 0.047145 | 7.6224 | -114.718 | 7.9432 | 7.8813 | 0.2589 | -114.5782 | -114.9871 | 122.8523 | 122.4294 | 122.8102 | 8.6212 | -106.9944 | 8.045 | 8.1848 | 7.776 | 7.9197 | -115.1407
1527.3438 | 122.6898 | -7.8369 | 114.8987 | 1.4211e-13 | 0.076747 | -0.0011389 | -0.0024744 | -0.097452 | 0.092144 | 0.013277 | 0.0077016 | 0.0072857 | -0.0070975 | 0.03898 | 0.0033095 | 114.415 | 0.6653 | 2.7981 | 115.0292 | 114.5742 | 114.8955 | 7.8127 | -0.003531 | -0.040849 | -0.070087 | 0.093665 | 0.2289 | -0.17081 | -0.31983 | 15.6496 | 0.1305 | 122.2519 | 10.635 | -5.0146 | -0.32447 | -0.003201 | 7.5171 | -114.805 | 7.8334 | 7.7668 | 0.24974 | -114.6698 | -115.0695 | 122.8661 | 122.4111 | 122.7324 | 8.5022 | -107.086 | 7.9306 | 8.0658 | 7.6661 | 7.7961 | -115.2185
1529.0938 | 122.7676 | -7.6447 | 115.004 | 1.4211e-13 | 0.077174 | -0.00092531 | -0.0024744 | -0.097452 | 0.092572 | -0.0019839 | 0.0079152 | 0.0074993 | -0.0075247 | 0.039194 | 0.0035231 | 114.5111 | 0.66073 | 2.6424 | 115.1162 | 114.6704 | 115.0328 | 7.8081 | -0.003531 | -0.031692 | -0.074666 | 0.089087 | 0.22432 | -0.17081 | -0.31983 | 15.4528 | 0.1122 | 122.1558 | 10.2871 | -5.1657 | -0.3336 | 0.028872 | 7.3248 | -114.9149 | 7.6411 | 7.57 | 0.24516 | -114.7796 | -115.1748 | 122.7608 | 122.315 | 122.6775 | 8.3054 | -107.1959 | 7.7337 | 7.869 | 7.4738 | 7.613 | -115.3238
1530.7812 | 122.699 | -7.5943 | 115.1093 | 1.4211e-13 | 0.076961 | -0.00071151 | -0.0026882 | -0.097238 | 0.092144 | 0.0056466 | 0.0079152 | 0.0079267 | -0.0070975 | 0.039408 | 0.0030959 | 114.6439 | 0.65157 | 2.7981 | 115.2673 | 114.8123 | 115.2068 | 7.8173 | -0.00811 | -0.040849 | -0.070087 | 0.098244 | 0.23348 | -0.16624 | -0.32441 | 15.4116 | 0.15801 | 122.2382 | 10.3924 | -5.0192 | -0.29694 | 0.097573 | 7.2699 | -115.011 | 7.5862 | 7.5242 | 0.25432 | -114.8758 | -115.2755 | 122.8616 | 122.4066 | 122.8011 | 8.2459 | -107.292 | 7.6925 | 7.8278 | 7.4281 | 7.5535 | -115.4337
1532.5312 | 122.7997 | -7.4844 | 115.1459 | 1.4211e-13 | 0.076961 | -0.00092531 | -0.002047 | -0.097665 | 0.092358 | -0.0019839 | 0.007488 | 0.0079267 | -0.0073111 | 0.03898 | 0.0035231 | 114.6714 | 0.65615 | 2.853 | 115.2993 | 114.8444 | 115.1931 | 7.8402 | -0.003531 | -0.040849 | -0.074666 | 0.089087 | 0.21974 | -0.17081 | -0.32441 | 15.3246 | 0.15343 | 122.1558 | 10.3375 | -4.9871 | -0.30151 | 0.047216 | 7.16 | -115.0568 | 7.4809 | 7.4098 | 0.24974 | -114.9261 | -115.3167 | 122.7837 | 122.3288 | 122.6775 | 8.1406 | -107.3057 | 7.5735 | 7.7042 | 7.3136 | 7.4436 | -115.4703
1534.2812 | 122.7814 | -7.5119 | 115.1001 | 1.4211e-13 | 0.076747 | -0.00092531 | -0.0022608 | -0.097238 | 0.092144 | -0.0019839 | 0.007488 | 0.0079267 | -0.0073111 | 0.039621 | 0.0033095 | 114.6897 | 0.65157 | 2.8805 | 115.313 | 114.8627 | 115.2114 | 7.8173 | -0.003531 | -0.036271 | -0.070087 | 0.10282 | 0.2289 | -0.16624 | -0.32899 | 15.3292 | 0.21294 | 122.2016 | 10.3924 | -4.9368 | -0.23742 | 0.11131 | 7.1829 | -114.9973 | 7.5084 | 7.4418 | 0.2589 | -114.8712 | -115.2663 | 122.8249 | 122.3746 | 122.7233 | 8.1635 | -107.2828 | 7.6147 | 7.7408 | 7.3457 | 7.4756 | -115.4291
1536.0469 | 122.7585 | -7.402 | 115.2649 | 1.4211e-13 | 0.076747 | -0.0011389 | -0.0024744 | -0.097238 | 0.092144 | -0.0096144 | 0.0077016 | 0.0081403 | -0.0073111 | 0.039621 | 0.0028821 | 114.7767 | 0.65157 | 2.8896 | 115.3955 | 114.9405 | 115.303 | 7.8127 | -0.003531 | -0.040849 | -0.070087 | 0.093665 | 0.22432 | -0.17539 | -0.33357 | 15.2147 | 0.13056 | 122.1787 | 10.2917 | -4.9231 | -0.32437 | 0.038084 | 7.0685 | -115.1712 | 7.3985 | 7.332 | 0.26348 | -115.0406 | -115.4403 | 122.7975 | 122.3426 | 122.705 | 8.0536 | -107.4522 | 7.4957 | 7.6264 | 7.2266 | 7.3612 | -115.5985
1537.7344 | 122.6669 | -105.098 | 17.3904 | 1.4211e-13 | -0.0059444 | -0.0022073 | 1.4019 | -0.013696 | 0.011166 | 0.0056466 | 0.0077016 | 0.0079267 | -0.0073111 | 0.039194 | 0.0033095 | 16.5794 | -0.021486 | 16.2857 | 16.7358 | 16.8783 | 16.9363 | 6.9061 | 0.051413 | 0.014095 | -0.010564 | 0.14861 | 0.28384 | -0.17081 | -0.25572 | 112.004 | -0.65467 | 121.6774 | 121.3837 | 9.3796 | -0.51217 | -0.45416 | 104.8422 | -17.2418 | 105.1494 | 105.0874 | 0.24516 | -17.1066 | -17.5613 | 121.8337 | 121.9762 | 122.0342 | 105.0765 | -10.4844 | 105.2466 | 105.3818 | 104.9271 | 105.1121 | -17.6462
1539.4844 | 122.6898 | -122.1405 | 0.55847 | 1.4211e-13 | -0.006799 | -0.0024209 | 0.077016 | -0.013268 | 0.010739 | 0.0056466 | 0.007488 | 0.0079267 | -0.0073111 | 0.039621 | 0.0035231 | 0.55503 | -0.20005 | 0.46773 | 0.79383 | 0.80167 | 1.076 | 0.21168 | 0.055992 | 0.018674 | -0.005985 | 0.16234 | 0.30216 | -0.17081 | -0.25572 | 122.3522 | 0.23535 | 122.6955 | 122.6082 | 0.25605 | 0.2432 | 0.51753 | 121.8848 | -0.39613 | 122.1965 | 122.1345 | 0.24974 | -0.25631 | -0.72929 | 122.9343 | 122.9422 | 123.2165 | 121.9405 | -0.34679 | 122.3028 | 122.4427 | 121.9697 | 122.1592 | -0.8142
1541.25 | 122.7768 | -122.1176 | 0.51727 | 1.4211e-13 | -0.006799 | -0.0022073 | 0.11655 | -0.013696 | 0.010739 | 0.0056466 | 0.007488 | 0.0083539 | -0.0073111 | 0.039621 | 0.0030959 | 0.4131 | -0.168 | 0.3487 | 0.5878 | 0.65972 | 0.92949 | 0.1201 | 0.046835 | 0.018674 | 0.003172 | 0.16234 | 0.30216 | -0.16624 | -0.25572 | 122.2377 | 0.070526 | 122.5307 | 122.4663 | 0.2286 | 0.14245 | 0.41221 | 121.8619 | -0.35493 | 122.1645 | 122.1208 | 0.2589 | -0.21512 | -0.68351 | 122.7054 | 122.7773 | 123.0471 | 121.9496 | -0.39717 | 122.28 | 122.4198 | 121.9514 | 122.1363 | -0.773
1543 | 122.5616 | -119.0964 | 3.5477 | 1.4211e-13 | -0.0065854 | -0.0024209 | 1.0734 | -0.013909 | 0.010952 | 0.013277 | 0.007488 | 0.0079267 | -0.0073111 | 0.03898 | 0.0028821 | 3.0777 | -0.10848 | 2.8255 | 3.257 | 3.1781 | 3.5805 | 2.7942 | 0.055992 | 0.014095 | -0.010564 | 0.16234 | 0.293 | -0.17081 | -0.26488 | 121.8906 | -0.29067 | 122.1741 | 121.9219 | 0.031354 | -0.36953 | 0.032828 | 118.8315 | -3.3853 | 119.1524 | 119.0858 | 0.25432 | -3.2547 | -3.7185 | 122.3534 | 122.2745 | 122.6769 | 118.9879 | -0.75348 | 119.2587 | 119.3894 | 118.9256 | 119.1105 | -3.8126
1544.6719 | 122.525 | -118.0161 | 4.3854 | 1.4211e-13 | -0.006158 | -0.0022073 | 3.2363 | -0.014123 | 0.011166 | 0.0056466 | 0.0077016 | 0.0079267 | -0.0075247 | 0.039408 | 0.0035231 | 3.6821 | -0.085587 | 2.9583 | 3.8522 | 3.778 | 4.1528 | 3.3849 | 0.060571 | 0.027831 | -0.005985 | 0.15776 | 0.29758 | -0.17539 | -0.2603 | 121.4009 | -0.53319 | 121.6981 | 120.9744 | -0.42656 | -0.6074 | -0.23255 | 117.7557 | -4.2276 | 118.0766 | 118.0101 | 0.25432 | -4.0878 | -4.5608 | 121.8682 | 121.794 | 122.1689 | 117.9305 | -1.0005 | 118.1738 | 118.3136 | 117.8407 | 118.0439 | -4.6457
1546.4219 | 122.3282 | -118.0573 | 4.1519 | 1.4211e-13 | -0.006158 | -0.0024209 | 4.4688 | -0.014123 | 0.01138 | 0.0056466 | 0.0077016 | 0.0077131 | -0.0070975 | 0.039408 | 0.0035231 | 3.5264 | -0.099323 | 2.5417 | 3.6965 | 3.6223 | 3.9971 | 3.2338 | 0.051413 | 0.018674 | -0.010564 | 0.16692 | 0.29758 | -0.17081 | -0.2603 | 121.291 | -0.45539 | 121.5837 | 120.5989 | -0.69207 | -0.52963 | -0.15477 | 117.7969 | -3.985 | 118.1087 | 118.0467 | 0.24974 | -3.8543 | -4.3227 | 121.7538 | 121.6795 | 122.0544 | 117.9579 | -0.91815 | 118.2242 | 118.3548 | 117.8864 | 118.0759 | -4.4122
1548.1562 | 122.1268 | -118.3411 | 3.7811 | 1.4211e-13 | -0.005517 | -0.0019935 | 4.418 | -0.014337 | 0.011593 | -0.0019839 | 0.0077016 | 0.0081403 | -0.0075247 | 0.039408 | 0.0033095 | 3.0457 | -0.07643 | 2.0747 | 3.2158 | 3.1278 | 3.5164 | 2.7621 | 0.060571 | 0.018674 | -0.001407 | 0.15776 | 0.30216 | -0.17081 | -0.2603 | 121.1032 | -0.56533 | 121.3867 | 120.4158 | -0.68743 | -0.65336 | -0.26473 | 118.0808 | -3.6234 | 118.4016 | 118.3397 | 0.2589 | -3.479 | -3.9519 | 121.5569 | 121.4688 | 121.8575 | 118.2646 | -1.019 | 118.4988 | 118.6432 | 118.1702 | 118.3597 | -4.0414
1549.8438 | 122.1634 | -118.4967 | 3.479 | 1.4211e-13 | -0.0057306 | -0.0024209 | 4.3195 | -0.014337 | 0.01138 | -0.0019839 | 0.0077016 | 0.0077131 | -0.0073111 | 0.039835 | 0.0030959 | 2.858 | -0.090166 | 1.9099 | 3.0418 | 2.9583 | 3.3333 | 2.5698 | 0.055992 | 0.018674 | -0.001407 | 0.1715 | 0.30216 | -0.17081 | -0.25572 | 121.0665 | -0.43719 | 121.3547 | 120.4066 | -0.65993 | -0.52066 | -0.14575 | 118.241 | -3.3075 | 118.5527 | 118.4953 | 0.25432 | -3.1768 | -3.6498 | 121.5385 | 121.455 | 121.83 | 118.4065 | -0.90918 | 118.6682 | 118.7989 | 118.3259 | 118.5154 | -3.7347
1551.5938 | 121.9757 | -118.6386 | 3.4287 | 1.4211e-13 | -0.0057306 | -0.0019935 | 4.2229 | -0.014337 | 0.01138 | -0.0019839 | 0.007488 | 0.0074993 | -0.0077383 | 0.039621 | 0.0033095 | 2.7618 | -0.090166 | 1.8275 | 2.9365 | 2.8485 | 3.2325 | 2.2768 | 0.069728 | 0.027831 | -0.005985 | 0.16234 | 0.29758 | -0.17539 | -0.25572 | 120.9154 | -0.49214 | 121.4004 | 120.4661 | -0.44929 | -0.5802 | -0.19613 | 118.3829 | -3.2663 | 118.7083 | 118.6326 | 0.24974 | -3.1311 | -3.604 | 121.5751 | 121.4871 | 121.8711 | 118.5484 | -1.1519 | 118.801 | 118.9362 | 118.4632 | 118.6664 | -3.6844
1553.3594 | 122.0078 | -118.515 | 3.4882 | 1.4211e-13 | -0.0059444 | -0.0022073 | 4.1265 | -0.01455 | 0.011593 | 0.013277 | 0.0077016 | 0.0079267 | -0.0073111 | 0.039621 | 0.0030959 | 2.7984 | -0.081008 | 1.8778 | 2.9686 | 2.8759 | 3.1959 | 2.1989 | 0.060571 | 0.023253 | 0.003172 | 0.16234 | 0.293 | -0.17539 | -0.25572 | 120.7139 | -0.5196 | 121.3135 | 120.3929 | -0.32109 | -0.61224 | -0.29226 | 118.2593 | -3.3258 | 118.5756 | 118.5182 | 0.2589 | -3.1952 | -3.6636 | 121.4836 | 121.3909 | 121.7109 | 118.434 | -1.2892 | 118.6774 | 118.808 | 118.3396 | 118.5383 | -3.7439
1555.1094 | 122.081 | -118.5837 | 3.3371 | 1.4211e-13 | -0.0059444 | -0.0019935 | 4.0513 | -0.014123 | 0.011166 | -0.0019839 | 0.0079152 | 0.0077131 | -0.0073111 | 0.039194 | 0.0033095 | 2.7435 | -0.085587 | 1.8458 | 2.9136 | 2.8256 | 3.1455 | 2.2127 | 0.051413 | 0.023253 | -0.005985 | 0.16234 | 0.30216 | -0.17539 | -0.2603 | 120.7963 | -0.42348 | 121.3272 | 120.4295 | -0.36687 | -0.51154 | -0.19157 | 118.3234 | -3.1748 | 118.6351 | 118.5777 | 0.25432 | -3.0349 | -3.5125 | 121.4973 | 121.4092 | 121.7292 | 118.4981 | -1.1244 | 118.746 | 118.8858 | 118.4083 | 118.6069 | -3.5974
1556.8125 | 122.0261 | -117.2745 | 4.5868 | 1.4211e-13 | -0.005517 | -0.0022073 | 4.656 | -0.014123 | 0.01138 | -0.0019839 | 0.0079152 | 0.0077131 | -0.0073111 | 0.039408 | 0.0033095 | 4.6161 | -0.07643 | 3.5993 | 4.777 | 4.8494 | 5.009 | 4.2823 | 0.060571 | 0.014095 | -0.001407 | 0.16692 | 0.29758 | -0.17081 | -0.2603 | 121.5568 | 0.19023 | 121.8905 | 120.8738 | -0.68307 | 0.26265 | 0.42223 | 117.0142 | -4.4199 | 117.335 | 117.2731 | 0.2589 | -4.2892 | -4.7576 | 122.0515 | 122.1239 | 122.2835 | 117.198 | -0.30445 | 117.4414 | 117.5721 | 117.1037 | 117.2886 | -4.8471
1558.5625 | 122.0078 | -118.1717 | 3.6896 | 1.4211e-13 | -0.006158 | -0.0019935 | 3.8955 | -0.013909 | 0.01138 | -0.0019839 | 0.0077016 | 0.0074993 | -0.0073111 | 0.039408 | 0.0030959 | 3.1281 | -0.090166 | 2.267 | 3.2936 | 3.2148 | 3.5301 | 2.579 | 0.060571 | 0.018674 | -0.010564 | 0.16692 | 0.30216 | -0.17081 | -0.26488 | 120.7507 | -0.39595 | 121.2998 | 120.4387 | -0.31199 | -0.47481 | -0.15944 | 117.9068 | -3.5227 | 118.2323 | 118.1611 | 0.25432 | -3.3874 | -3.8604 | 121.4653 | 121.3865 | 121.7018 | 118.0815 | -1.1106 | 118.3386 | 118.4738 | 118.0009 | 118.1904 | -3.9545
1560.3125 | 122.0123 | -118.0573 | 3.7399 | 1.4211e-13 | -0.0063718 | -0.0019935 | 3.8178 | -0.014337 | 0.011593 | -0.0019839 | 0.007488 | 0.0077131 | -0.0075247 | 0.039621 | 0.0033095 | 3.2059 | -0.094744 | 2.3586 | 3.376 | 3.288 | 3.608 | 2.4645 | 0.060571 | 0.027831 | 0.003172 | 0.16234 | 0.29758 | -0.17081 | -0.2603 | 120.5218 | -0.36389 | 121.2632 | 120.4158 | -0.10595 | -0.4519 | -0.13196 | 117.7969 | -3.5776 | 118.1178 | 118.0604 | 0.26348 | -3.4423 | -3.9107 | 121.4333 | 121.3453 | 121.6652 | 117.9625 | -1.2754 | 118.2196 | 118.3548 | 117.8864 | 118.0851 | -4.0002
1562.0156 | 121.875 | -118.0573 | 3.804 | 1.4211e-13 | -0.0059444 | -0.0017799 | 3.7558 | -0.013909 | 0.011166 | 0.013277 | 0.007488 | 0.0079267 | -0.0073111 | 0.039835 | 0.0028821 | 3.2425 | -0.090166 | 2.3586 | 3.4172 | 3.3247 | 3.6538 | 2.8858 | 0.060571 | 0.018674 | -0.001407 | 0.16692 | 0.29758 | -0.17539 | -0.25572 | 120.943 | -0.38677 | 121.2998 | 120.4158 | -0.52721 | -0.47936 | -0.15026 | 117.8015 | -3.6371 | 118.1178 | 118.0558 | 0.25432 | -3.5064 | -3.9794 | 121.4745 | 121.3819 | 121.711 | 117.9671 | -0.91825 | 118.2242 | 118.3548 | 117.8819 | 118.0759 | -4.0597
1563.7656 | 121.9162 | -118.2266 | 3.6072 | 1.4211e-13 | -0.006158 | -0.0024209 | 3.6947 | -0.014123 | 0.01138 | -0.0019839 | 0.0077016 | 0.0081403 | -0.0077383 | 0.039621 | 0.0033095 | 3.0457 | -0.094744 | 2.2258 | 3.2021 | 3.1186 | 3.4477 | 2.7484 | 0.055992 | 0.027831 | 0.003172 | 0.16692 | 0.30216 | -0.17081 | -0.2603 | 120.975 | -0.40512 | 121.2723 | 120.4524 | -0.52261 | -0.48857 | -0.15946 | 117.9663 | -3.4403 | 118.2826 | 118.2298 | 0.26348 | -3.305 | -3.778 | 121.4287 | 121.3452 | 121.6743 | 118.1319 | -0.85878 | 118.3935 | 118.5288 | 118.0558 | 118.2545 | -3.8675
1565.5312 | 121.9894 | -2.0096 | 119.989 | 1.4211e-13 | -0.0065854 | -0.0022073 | 1.2995 | -0.013909 | 0.011166 | -0.0019839 | 0.0070608 | 0.0077131 | -0.0070975 | 0.039408 | 0.0030959 | 2.0842 | -0.058115 | 1.7542 | 2.323 | 2.2303 | 2.6098 | 0.75199 | 0.001048 | -0.031692 | -0.074666 | 0.1074 | 0.23348 | -0.17081 | -0.32441 | 2.7616 | -117.666 | 4.0938 | 3.7638 | 1.0022 | -117.7587 | -117.3792 | 1.6852 | -119.8816 | 2.0106 | 1.9349 | 0.24974 | -119.7555 | -120.1598 | 4.3326 | 4.2399 | 4.6194 | 1.9515 | -119.237 | 2.117 | 2.2431 | 1.8388 | 1.9779 | -120.3134
1567.2344 | 122.0535 | -2.3392 | 119.8151 | 1.4211e-13 | -0.0070128 | -0.0019935 | 0.031287 | -0.013696 | 0.010525 | 0.013277 | 0.0077016 | 0.0077131 | -0.0073111 | 0.039621 | 0.0030959 | -0.003531 | -0.026065 | -0.045036 | 0.17574 | 0.23846 | 0.49452 | -0.28285 | -0.00811 | -0.040849 | -0.083823 | 0.089087 | 0.22432 | -0.17539 | -0.33814 | 2.0563 | -119.6393 | 2.3356 | 2.2941 | 0.23781 | -119.5766 | -119.3205 | 2.001 | -119.726 | 2.3311 | 2.2553 | 0.25432 | -119.5907 | -119.9905 | 2.5149 | 2.5776 | 2.8337 | 2.3131 | -120.0979 | 2.4283 | 2.5635 | 2.1638 | 2.2983 | -120.1532
1569 | 122.1863 | -2.4719 | 119.6594 | 1.4211e-13 | -0.0072264 | -0.0017799 | 0.030433 | -0.013482 | 0.010739 | 0.0056466 | 0.007488 | 0.0077131 | -0.0073111 | 0.039408 | 0.0033095 | -0.008109 | -0.039801 | -0.054192 | 0.16659 | -0.068325 | 0.49452 | -0.11342 | -0.003531 | -0.040849 | -0.083823 | 0.089087 | 0.2289 | -0.17539 | -0.33357 | 2.3585 | -119.4928 | 2.4638 | 2.4177 | 0.059233 | -119.7277 | -119.1649 | 2.1384 | -119.5703 | 2.4684 | 2.3881 | 0.24974 | -119.4305 | -119.8348 | 2.6385 | 2.4036 | 2.9664 | 2.4321 | -119.7728 | 2.561 | 2.7008 | 2.2965 | 2.4311 | -119.993
1570.6719 | 122.2092 | -2.4948 | 119.6594 | 1.4211e-13 | -0.0072264 | -0.0024209 | 0.030646 | -0.013909 | 0.010739 | -0.0019839 | 0.0072744 | 0.0077131 | -0.0070975 | 0.039621 | 0.0030959 | -0.008109 | -0.044379 | -0.045036 | 0.16659 | -0.072904 | 0.48536 | 0.15215 | -0.00811 | -0.045428 | -0.083823 | 0.084508 | 0.22432 | -0.17539 | -0.34272 | 2.647 | -119.4928 | 2.4867 | 2.4498 | -0.19719 | -119.7323 | -119.1741 | 2.1521 | -119.5749 | 2.4867 | 2.411 | 0.2589 | -119.4351 | -119.8348 | 2.6614 | 2.4219 | 2.9802 | 2.4504 | -119.5073 | 2.5793 | 2.7191 | 2.3194 | 2.4494 | -120.0021
1572.4219 | 122.1954 | -2.5223 | 119.6274 | 1.4211e-13 | -0.006799 | -0.0019935 | 0.030646 | -0.013482 | 0.010952 | -0.0096144 | 0.0077016 | 0.0077131 | -0.0073111 | 0.039621 | 0.0030959 | -0.003531 | -0.053537 | -0.045036 | 0.16659 | -0.059167 | 0.48078 | 0.16131 | -0.017267 | -0.040849 | -0.079245 | 0.089087 | 0.23806 | -0.17081 | -0.33357 | 2.6836 | -119.4608 | 2.5187 | 2.4772 | -0.20635 | -119.6865 | -119.1466 | 2.1887 | -119.5383 | 2.505 | 2.443 | 0.25432 | -119.3893 | -119.7982 | 2.6889 | 2.4631 | 3.0031 | 2.4687 | -119.4661 | 2.6114 | 2.7603 | 2.3515 | 2.4814 | -119.9609
1574.1562 | 122.2229 | -2.5177 | 119.6503 | 1.4211e-13 | -0.0070128 | -0.0022073 | 0.030219 | -0.013909 | 0.010739 | -0.0019839 | 0.0079152 | 0.0077131 | -0.0077383 | 0.039835 | 0.0028821 | 0.001048 | -0.044379 | -0.049614 | 0.16659 | -0.068325 | 0.41668 | 0.14757 | -0.003531 | -0.040849 | -0.083823 | 0.098244 | 0.22432 | -0.16624 | -0.32899 | 2.6653 | -119.4837 | 2.5187 | 2.4681 | -0.19719 | -119.7186 | -119.2336 | 2.1887 | -119.552 | 2.5142 | 2.4339 | 0.24516 | -119.4259 | -119.8165 | 2.6843 | 2.4494 | 2.9344 | 2.4733 | -119.5027 | 2.6159 | 2.742 | 2.3515 | 2.4769 | -119.9793
1575.8438 | 122.1863 | -2.449 | 119.7052 | 1.4211e-13 | -0.0072264 | -0.0024209 | 0.030219 | -0.013482 | 0.010739 | -0.0019839 | 0.0077016 | 0.0079267 | -0.0079521 | 0.039621 | 0.0033095 | 0.001048 | -0.048958 | -0.054192 | 0.16659 | -0.072904 | 0.41668 | 0.16131 | -0.00811 | -0.045428 | -0.074666 | 0.084508 | 0.22432 | -0.17539 | -0.32899 | 2.6103 | -119.5386 | 2.4501 | 2.3948 | -0.2155 | -119.7781 | -119.2885 | 2.12 | -119.6207 | 2.4409 | 2.3744 | 0.25432 | -119.4809 | -119.8806 | 2.6156 | 2.3761 | 2.8657 | 2.4001 | -119.5439 | 2.5335 | 2.6734 | 2.2736 | 2.4036 | -120.0342
1577.6094 | 122.168 | -2.4536 | 119.7601 | 1.4211e-13 | -0.00744 | -0.0022073 | 0.030005 | -0.013482 | 0.010952 | 0.020908 | 0.0077016 | 0.0077131 | -0.0073111 | 0.039408 | 0.0033095 | -0.017266 | -0.044379 | -0.054192 | 0.16659 | -0.077483 | 0.41668 | 0.15673 | -0.00811 | -0.040849 | -0.074666 | 0.093665 | 0.22432 | -0.17081 | -0.33357 | 2.6103 | -119.5935 | 2.4363 | 2.3994 | -0.21092 | -119.8376 | -119.3435 | 2.12 | -119.6665 | 2.4455 | 2.3789 | 0.2589 | -119.5358 | -119.9309 | 2.6202 | 2.3761 | 2.8703 | 2.4092 | -119.6034 | 2.5473 | 2.6779 | 2.2828 | 2.4128 | -120.0937
1579.2969 | 122.1725 | -2.4536 | 119.7693 | 1.4211e-13 | -0.0070128 | -0.0024209 | 0.030219 | -0.013696 | 0.010952 | -0.0019839 | 0.0077016 | 0.0077131 | -0.0075247 | 0.039621 | 0.0035231 | -0.003531 | -0.053537 | -0.045036 | 0.16659 | -0.068325 | 0.41668 | 0.15673 | -0.003531 | -0.036271 | -0.083823 | 0.089087 | 0.21516 | -0.16624 | -0.32899 | 2.6103 | -119.6027 | 2.4501 | 2.4086 | -0.20177 | -119.8376 | -119.3526 | 2.1246 | -119.6802 | 2.4501 | 2.3698 | 0.24516 | -119.5541 | -119.9355 | 2.6202 | 2.3853 | 2.8703 | 2.4001 | -119.6126 | 2.5427 | 2.6688 | 2.2874 | 2.4173 | -120.0983
1581.0312 | 122.2 | -2.4124 | 119.7739 | 1.4211e-13 | -0.0070128 | -0.0024209 | 0.030219 | -0.013268 | 0.010739 | 0.013277 | 0.0079152 | 0.0077131 | -0.0075247 | 0.039408 | 0.0028821 | -0.008109 | -0.048958 | -0.049614 | 0.16201 | -0.077483 | 0.4121 | 0.15215 | -0.012689 | -0.040849 | -0.083823 | 0.093665 | 0.22432 | -0.16624 | -0.33357 | 2.5646 | -119.6119 | 2.4043 | 2.3628 | -0.20177 | -119.8513 | -119.3618 | 2.0789 | -119.6802 | 2.3997 | 2.3286 | 0.24974 | -119.5495 | -119.9401 | 2.5744 | 2.3349 | 2.8245 | 2.3635 | -119.6217 | 2.5061 | 2.6367 | 2.2462 | 2.3716 | -120.1074
1582.7812 | 122.2504 | -2.3712 | 119.7739 | 1.4211e-13 | -0.006799 | -0.0019935 | 0.030219 | -0.013696 | 0.010739 | -0.0019839 | 0.0072744 | 0.0079267 | -0.0073111 | 0.039408 | 0.0030959 | -0.003531 | -0.044379 | -0.05877 | 0.16201 | -0.077483 | 0.41668 | 0.15673 | -0.003531 | -0.036271 | -0.083823 | 0.089087 | 0.21974 | -0.16624 | -0.32899 | 2.5279 | -119.6119 | 2.3677 | 2.3124 | -0.2155 | -119.8513 | -119.3572 | 2.0422 | -119.6848 | 2.3677 | 2.2874 | 0.24516 | -119.5541 | -119.9401 | 2.5332 | 2.2937 | 2.7879 | 2.3268 | -119.6171 | 2.4603 | 2.591 | 2.205 | 2.3349 | -120.1029
1584.4844 | 122.2092 | -2.3712 | 119.8013 | 1.4211e-13 | -0.0072264 | -0.0024209 | 0.030219 | -0.013696 | 0.010952 | -0.0019839 | 0.0077016 | 0.0081403 | -0.0075247 | 0.039621 | 0.0033095 | -0.003531 | -0.044379 | -0.054192 | 0.15743 | -0.072904 | 0.41668 | 0.16131 | -0.00811 | -0.040849 | -0.079245 | 0.089087 | 0.22432 | -0.17081 | -0.33814 | 2.5325 | -119.6439 | 2.3677 | 2.317 | -0.2155 | -119.8742 | -119.3846 | 2.0331 | -119.7122 | 2.3631 | 2.292 | 0.2589 | -119.577 | -119.9721 | 2.5286 | 2.2983 | 2.7879 | 2.3268 | -119.64 | 2.4603 | 2.5955 | 2.2004 | 2.3304 | -120.1395
1586.25 | 122.2046 | -2.3987 | 119.7693 | 1.4211e-13 | -0.0070128 | -0.0019935 | 0.030433 | -0.013696 | 0.010525 | 0.0056466 | 0.0077016 | 0.0074993 | -0.0077383 | 0.039408 | 0.0030959 | 0.001048 | -0.048958 | -0.049614 | 0.15743 | -0.077483 | 0.4121 | 0.15673 | -0.012689 | -0.040849 | -0.074666 | 0.093665 | 0.22432 | -0.17081 | -0.33814 | 2.5554 | -119.6119 | 2.3997 | 2.3491 | -0.20635 | -119.8468 | -119.3572 | 2.0605 | -119.6756 | 2.386 | 2.324 | 0.26348 | -119.545 | -119.9401 | 2.5561 | 2.3212 | 2.8108 | 2.3497 | -119.6126 | 2.4923 | 2.623 | 2.2279 | 2.3578 | -120.1074
1588 | 122.1268 | -2.4307 | 119.7922 | 1.4211e-13 | -0.0070128 | -0.0024209 | 0.029792 | -0.013909 | 0.010739 | -0.0019839 | 0.007488 | 0.0081403 | -0.0081657 | 0.039408 | 0.0030959 | -0.008109 | -0.048958 | -0.05877 | 0.15743 | -0.077483 | 0.4121 | 0.16131 | -0.012689 | -0.040849 | -0.074666 | 0.089087 | 0.21974 | -0.17539 | -0.33814 | 2.592 | -119.6347 | 2.4226 | 2.372 | -0.22008 | -119.8697 | -119.3801 | 2.0926 | -119.7031 | 2.418 | 2.3561 | 0.26348 | -119.5724 | -119.9676 | 2.5882 | 2.3532 | 2.8428 | 2.3818 | -119.6309 | 2.5198 | 2.6505 | 2.2553 | 2.3899 | -120.1303
1589.6875 | 122.2641 | -2.3712 | 119.7968 | 1.4211e-13 | -0.006799 | -0.0022073 | 0.030433 | -0.013696 | 0.010739 | 0.013277 | 0.0079152 | 0.0081403 | -0.0073111 | 0.039835 | 0.0028821 | -0.003531 | -0.048958 | -0.049614 | 0.15285 | -0.072904 | 0.42126 | 0.15215 | -0.012689 | -0.036271 | -0.079245 | 0.089087 | 0.21974 | -0.17997 | -0.34272 | 2.5234 | -119.6439 | 2.3677 | 2.3216 | -0.20177 | -119.8697 | -119.3755 | 2.0285 | -119.7077 | 2.3585 | 2.292 | 0.26348 | -119.577 | -119.9767 | 2.5241 | 2.2983 | 2.7925 | 2.3223 | -119.6446 | 2.4603 | 2.591 | 2.1912 | 2.3349 | -120.1395
1591.4375 | 122.1725 | -2.4765 | 119.7601 | 1.4211e-13 | -0.006799 | -0.0024209 | 0.030646 | -0.013909 | 0.010739 | 0.0056466 | 0.0077016 | 0.0079267 | -0.0077383 | 0.039835 | 0.0030959 | -0.003531 | -0.048958 | -0.054192 | 0.15743 | -0.082062 | 0.41668 | 0.15673 | -0.012689 | -0.040849 | -0.083823 | 0.098244 | 0.2289 | -0.16624 | -0.34272 | 2.6332 | -119.6027 | 2.473 | 2.4223 | -0.21092 | -119.8422 | -119.3435 | 2.1338 | -119.6619 | 2.4638 | 2.3927 | 0.2589 | -119.5312 | -119.9264 | 2.6339 | 2.3944 | 2.8932 | 2.4275 | -119.6034 | 2.5747 | 2.7054 | 2.3103 | 2.4357 | -120.1029
1593.1875 | 122.2366 | -2.4353 | 119.7372 | 1.4211e-13 | -0.0070128 | -0.0024209 | 0.030005 | -0.013696 | 0.010952 | 0.0056466 | 0.0077016 | 0.0074993 | -0.0073111 | 0.039194 | 0.0030959 | 0.001048 | -0.048958 | -0.054192 | 0.15743 | -0.086641 | 0.4121 | 0.15673 | -0.012689 | -0.040849 | -0.083823 | 0.089087 | 0.23348 | -0.17081 | -0.34272 | 2.592 | -119.5798 | 2.4364 | 2.3811 | -0.21092 | -119.8239 | -119.3251 | 2.0926 | -119.6482 | 2.4226 | 2.3515 | 0.2589 | -119.5038 | -119.9081 | 2.5927 | 2.3487 | 2.8474 | 2.3863 | -119.5805 | 2.5244 | 2.6688 | 2.2645 | 2.3945 | -120.08
1594.9219 | 122.1909 | -2.4445 | 119.7922 | 1.4211e-13 | -0.0072264 | -0.0028483 | 0.030433 | -0.013696 | 0.010952 | 0.0056466 | 0.0077016 | 0.0074993 | -0.0075247 | 0.040049 | 0.0028821 | 0.001048 | -0.048958 | -0.049614 | 0.15743 | -0.082062 | 0.40753 | 0.15215 | -0.012689 | -0.045428 | -0.070087 | 0.093665 | 0.23348 | -0.17081 | -0.33357 | 2.5966 | -119.6347 | 2.4455 | 2.3948 | -0.20177 | -119.8742 | -119.3846 | 2.1109 | -119.6985 | 2.4318 | 2.3744 | 0.26348 | -119.5587 | -119.963 | 2.6019 | 2.3624 | 2.852 | 2.3955 | -119.64 | 2.5381 | 2.6779 | 2.2736 | 2.399 | -120.1257
1596.6875 | 122.1771 | -2.4628 | 119.7601 | 1.4211e-13 | -0.0070128 | -0.0022073 | 0.030433 | -0.013268 | 0.010311 | 0.0056466 | 0.0077016 | 0.0079267 | -0.0075247 | 0.039835 | 0.0033095 | -0.008109 | -0.048958 | -0.049614 | 0.15743 | -0.086641 | 0.40753 | 0.14757 | -0.012689 | -0.040849 | -0.079245 | 0.093665 | 0.24264 | -0.16166 | -0.33814 | 2.6103 | -119.6027 | 2.4547 | 2.4132 | -0.19719 | -119.8468 | -119.3526 | 2.1246 | -119.6665 | 2.4501 | 2.3835 | 0.2589 | -119.5175 | -119.9218 | 2.6202 | 2.3761 | 2.8703 | 2.4138 | -119.6126 | 2.5564 | 2.7054 | 2.3011 | 2.4219 | -120.0983
1598.375 | 122.2458 | -2.4078 | 119.8105 | 1.4211e-13 | -0.00744 | -0.0024209 | 0.030646 | -0.014123 | 0.010739 | 0.013277 | 0.007488 | 0.0079267 | -0.0073111 | 0.040049 | 0.0030959 | -0.008109 | -0.048958 | -0.054192 | 0.16659 | -0.077483 | 0.40753 | 0.15673 | -0.012689 | -0.036271 | -0.079245 | 0.089087 | 0.21974 | -0.17081 | -0.34272 | 2.5646 | -119.6439 | 2.3997 | 2.3536 | -0.21092 | -119.888 | -119.403 | 2.0651 | -119.7214 | 2.3951 | 2.3286 | 0.26348 | -119.5907 | -119.9813 | 2.5744 | 2.3304 | 2.8154 | 2.3589 | -119.6538 | 2.4969 | 2.6276 | 2.237 | 2.3716 | -120.1532
1600.1094 | 122.1863 | -2.4399 | 119.8288 | 1.4211e-13 | -0.00744 | -0.0022073 | 0.030005 | -0.013909 | 0.010311 | -0.0019839 | 0.0077016 | 0.0074993 | -0.0079521 | 0.039835 | 0.0030959 | -0.003531 | -0.053537 | -0.049614 | 0.15285 | -0.082062 | 0.40753 | 0.15673 | -0.00811 | -0.036271 | -0.074666 | 0.089087 | 0.22432 | -0.16624 | -0.33357 | 2.5966 | -119.6759 | 2.4363 | 2.3903 | -0.20635 | -119.9109 | -119.4213 | 2.1063 | -119.7397 | 2.4318 | 2.3652 | 0.2589 | -119.6045 | -119.995 | 2.5927 | 2.3578 | 2.8474 | 2.3863 | -119.6721 | 2.529 | 2.6642 | 2.2736 | 2.4036 | -120.1624
1601.875 | 122.1405 | -2.4445 | 119.8151 | 1.4211e-13 | -0.0076538 | -0.0024209 | 0.030433 | -0.013482 | 0.010525 | 0.0056466 | 0.007488 | 0.0079267 | -0.0073111 | 0.039621 | 0.0030959 | -0.003531 | -0.048958 | -0.05877 | 0.16201 | -0.086641 | 0.40295 | 0.14757 | -0.012689 | -0.040849 | -0.074666 | 0.093665 | 0.2289 | -0.17539 | -0.33814 | 2.592 | -119.6531 | 2.4409 | 2.3857 | -0.20634 | -119.9017 | -119.4121 | 2.1063 | -119.7214 | 2.4318 | 2.3698 | 0.26348 | -119.5862 | -119.9905 | 2.6065 | 2.3578 | 2.8474 | 2.3955 | -119.6675 | 2.5381 | 2.6734 | 2.2691 | 2.4036 | -120.1532
1603.5625 | 122.0856 | -68.4998 | 53.7598 | 1.4211e-13 | -0.0072264 | -0.0024209 | 0.030219 | -0.013696 | 0.010952 | -0.0096144 | 0.0072744 | 0.0077131 | -0.0070975 | 0.039621 | 0.0030959 | 0.019361 | -0.026065 | -0.026723 | 0.1849 | -0.068325 | 0.43042 | 0.15215 | 0.010205 | -0.031692 | -0.051772 | 0.11656 | 0.25637 | -0.17539 | -0.31067 | 68.6519 | -53.5749 | 68.5191 | 68.473 | -0.17888 | -53.8281 | -53.3293 | 68.1891 | -53.6432 | 68.51 | 68.448 | 0.2589 | -53.5034 | -53.9352 | 68.6847 | 68.4314 | 68.9302 | 68.4737 | -53.6076 | 68.6163 | 68.7561 | 68.3244 | 68.4681 | -54.0704
1605.3125 | 121.9986 | -111.2823 | 10.4416 | 1.4211e-13 | -0.0070128 | -0.0024209 | 0.030005 | -0.013696 | 0.010739 | -0.0019839 | 0.0077016 | 0.0077131 | -0.0073111 | 0.039835 | 0.0026685 | 0.042253 | 0.001407 | -0.008409 | 0.19406 | -0.04543 | 0.45789 | -0.017268 | 0.033099 | 0.000359 | -0.028879 | 0.13945 | 0.27926 | -0.16624 | -0.29236 | 111.2651 | -10.2475 | 111.3246 | 111.2739 | 0.008859 | -10.487 | -9.9837 | 110.99 | -10.3021 | 111.3154 | 111.2535 | 0.26348 | -10.1623 | -10.6078 | 111.4764 | 111.2369 | 111.7402 | 111.2838 | -10.4589 | 111.4218 | 111.5616 | 111.1161 | 111.2827 | -10.7339
1607.0781 | 122.1039 | -0.74158 | 120.6894 | 1.4211e-13 | -0.0072264 | -0.0019935 | 0.030219 | -0.013696 | 0.010525 | -0.0019839 | 0.007488 | 0.0077131 | -0.0075247 | 0.039835 | 0.0026685 | -0.008109 | -0.044379 | -0.049614 | 0.16201 | -0.082062 | 0.4121 | 0.15215 | -0.00811 | -0.040849 | -0.079245 | 0.098244 | 0.22432 | -0.17997 | -0.33357 | 0.89373 | -120.5274 | 0.73347 | 0.69196 | -0.20177 | -120.7715 | -120.2773 | 0.40801 | -120.5911 | 0.73347 | 0.66233 | 0.25432 | -120.4651 | -120.8694 | 0.90359 | 0.65952 | 1.1537 | 0.6972 | -120.5372 | 0.83982 | 0.9659 | 0.56161 | 0.70073 | -121.023
1608.8281 | 122.1588 | -0.79651 | 121.2936 | 1.4211e-13 | -0.00744 | -0.0022073 | 0.030005 | -0.013482 | 0.010525 | -0.0019839 | 0.007488 | 0.0074993 | -0.0075247 | 0.039408 | 0.0030959 | -0.003531 | -0.044379 | -0.049614 | 0.15743 | -0.072904 | 0.40753 | 0.15673 | -0.003531 | -0.045428 | -0.079245 | 0.098244 | 0.23348 | -0.17997 | -0.33357 | 0.95324 | -121.1362 | 0.79298 | 0.74689 | -0.20635 | -121.3665 | -120.8861 | 0.46294 | -121.1954 | 0.79298 | 0.71726 | 0.25432 | -121.0602 | -121.4736 | 0.95394 | 0.72361 | 1.204 | 0.75213 | -121.1369 | 0.89475 | 1.03 | 0.61654 | 0.75108 | -121.6272
1610.5156 | 122.0261 | -0.88806 | 121.3074 | 1.4211e-13 | -0.0076538 | -0.0022073 | 0.030219 | -0.014123 | 0.010739 | 0.013277 | 0.0079152 | 0.0077131 | -0.0077383 | 0.039621 | 0.0030959 | 0.001048 | -0.039801 | -0.054192 | 0.16201 | -0.072904 | 0.40753 | 0.15215 | 0.005626 | -0.040849 | -0.074666 | 0.10282 | 0.23348 | -0.16624 | -0.33357 | 1.0402 | -121.1454 | 0.88911 | 0.83387 | -0.20634 | -121.3803 | -120.8998 | 0.5545 | -121.2046 | 0.89369 | 0.8134 | 0.2589 | -121.0739 | -121.4736 | 1.0501 | 0.81516 | 1.2956 | 0.84826 | -121.1552 | 0.99088 | 1.1215 | 0.72183 | 0.84721 | -121.6409
1612.2812 | 122.1268 | -0.83313 | 121.2845 | 1.4211e-13 | -0.0070128 | -0.0019935 | 0.030219 | -0.013696 | 0.010952 | 0.020908 | 0.007488 | 0.0074993 | -0.0079521 | 0.039621 | 0.0030959 | 0.001048 | -0.044379 | -0.045036 | 0.16201 | -0.072904 | 0.40753 | 0.15673 | -0.00811 | -0.036271 | -0.079245 | 0.1074 | 0.2289 | -0.17081 | -0.33357 | 0.98986 | -121.1225 | 0.83418 | 0.78809 | -0.20177 | -121.3574 | -120.877 | 0.49957 | -121.1771 | 0.82502 | 0.75389 | 0.25432 | -121.0556 | -121.4553 | 0.99514 | 0.76023 | 1.2407 | 0.78875 | -121.1278 | 0.94053 | 1.062 | 0.66231 | 0.79686 | -121.618
1614.0312 | 122.1359 | -0.87891 | 121.2799 | 1.4211e-13 | -0.0070128 | -0.0022073 | 0.030005 | -0.013696 | 0.010311 | 0.0056466 | 0.007488 | 0.0077131 | -0.0077383 | 0.039621 | 0.0030959 | -0.003531 | -0.048958 | -0.045036 | 0.16659 | -0.072904 | 0.40753 | 0.15215 | 0.001048 | -0.040849 | -0.070087 | 0.098244 | 0.23806 | -0.17539 | -0.32899 | 1.0311 | -121.1133 | 0.87538 | 0.83387 | -0.19719 | -121.3528 | -120.8724 | 0.54992 | -121.1817 | 0.87995 | 0.80882 | 0.2589 | -121.0418 | -121.4553 | 1.0455 | 0.806 | 1.2864 | 0.82995 | -121.1278 | 0.97715 | 1.117 | 0.70351 | 0.83806 | -121.6089
1615.7188 | 122.113 | -0.86517 | 121.3074 | 1.4211e-13 | -0.0072264 | -0.0022073 | 0.030005 | -0.013909 | 0.010525 | -0.0019839 | 0.007488 | 0.0074993 | -0.0077383 | 0.039621 | 0.0030959 | 0.010204 | -0.039801 | -0.040457 | 0.16201 | -0.077483 | 0.4121 | 0.15673 | -0.012689 | -0.040849 | -0.074666 | 0.098244 | 0.23806 | -0.17539 | -0.32441 | 1.0219 | -121.1454 | 0.87538 | 0.82472 | -0.19719 | -121.3849 | -120.8953 | 0.54077 | -121.2091 | 0.85248 | 0.79051 | 0.24974 | -121.0693 | -121.4828 | 1.0272 | 0.78769 | 1.2773 | 0.82537 | -121.1506 | 0.96342 | 1.1032 | 0.68978 | 0.82432 | -121.6318
1617.5 | 122.0947 | -0.85144 | 121.3486 | 1.4211e-13 | -0.0076538 | -0.0026347 | 0.030219 | -0.014123 | 0.010952 | 0.0056466 | 0.0077016 | 0.0079267 | -0.0075247 | 0.039835 | 0.0033095 | 0.001048 | -0.044379 | -0.054192 | 0.17574 | -0.077483 | 0.41668 | 0.15673 | -0.012689 | -0.045428 | -0.065509 | 0.098244 | 0.23348 | -0.17997 | -0.33357 | 1.0082 | -121.1728 | 0.85249 | 0.79725 | -0.21092 | -121.4261 | -120.9319 | 0.51787 | -121.2503 | 0.83875 | 0.78593 | 0.26806 | -121.1151 | -121.5285 | 1.0272 | 0.77396 | 1.2681 | 0.80706 | -121.1918 | 0.94968 | 1.0849 | 0.67147 | 0.80601 | -121.6821
1619.2031 | 122.0947 | -0.85144 | 121.3394 | 1.4211e-13 | -0.0072264 | -0.0022073 | 0.030433 | -0.013696 | 0.010525 | -0.0019839 | 0.0079152 | 0.0079267 | -0.0077383 | 0.039835 | 0.0028821 | -0.003531 | -0.039801 | -0.045036 | 0.15743 | -0.086641 | 0.40753 | 0.15215 | -0.003531 | -0.040849 | -0.074666 | 0.089087 | 0.2289 | -0.17081 | -0.33357 | 1.0036 | -121.182 | 0.84791 | 0.8064 | -0.19719 | -121.4261 | -120.9319 | 0.51787 | -121.2503 | 0.84791 | 0.77677 | 0.2589 | -121.1105 | -121.5102 | 1.0089 | 0.7648 | 1.259 | 0.81164 | -121.1873 | 0.94053 | 1.0803 | 0.68063 | 0.81059 | -121.673
1620.9375 | 122.1954 | -0.82855 | 121.2891 | 1.4211e-13 | -0.0070128 | -0.0022073 | 0.030433 | -0.013268 | 0.010739 | 0.013277 | 0.007488 | 0.0074993 | -0.0073111 | 0.039408 | 0.0030959 | -0.003531 | -0.044379 | -0.045036 | 0.16201 | -0.082062 | 0.40753 | 0.16131 | -0.00811 | -0.040849 | -0.070087 | 0.098244 | 0.23348 | -0.17081 | -0.33357 | 0.98986 | -121.1271 | 0.82502 | 0.78352 | -0.20635 | -121.3711 | -120.8815 | 0.49499 | -121.1908 | 0.82044 | 0.75846 | 0.26348 | -121.0556 | -121.4599 | 0.99056 | 0.74649 | 1.2361 | 0.78417 | -121.1278 | 0.9268 | 1.062 | 0.65774 | 0.7877 | -121.6226
1622.625 | 122.1497 | -0.84228 | 121.2936 | 1.4211e-13 | -0.00744 | -0.0022073 | 0.030219 | -0.014123 | 0.010739 | -0.0019839 | 0.0072744 | 0.0079267 | -0.0075247 | 0.040262 | 0.0030959 | 0.005626 | -0.039801 | -0.040457 | 0.15743 | -0.082062 | 0.40295 | 0.14757 | -0.00811 | -0.036271 | -0.074666 | 0.098244 | 0.22432 | -0.17081 | -0.33357 | 0.98986 | -121.1362 | 0.84791 | 0.80183 | -0.18803 | -121.3757 | -120.8907 | 0.50872 | -121.1954 | 0.83417 | 0.76762 | 0.2589 | -121.0693 | -121.4645 | 0.99972 | 0.76022 | 1.2452 | 0.80248 | -121.1461 | 0.94053 | 1.0666 | 0.67147 | 0.80601 | -121.6272
1624.3906 | 122.081 | -0.87891 | 121.3303 | 1.4211e-13 | -0.0072264 | -0.0017799 | 0.030219 | -0.013696 | 0.010952 | 0.013277 | 0.0077016 | 0.0074993 | -0.0073111 | 0.039621 | 0.0030959 | 0.001048 | -0.053537 | -0.049614 | 0.16201 | -0.082062 | 0.40295 | 0.15673 | -0.003531 | -0.040849 | -0.074666 | 0.098244 | 0.23806 | -0.17081 | -0.32899 | 1.0356 | -121.1683 | 0.87995 | 0.82929 | -0.20635 | -121.4123 | -120.9273 | 0.54992 | -121.232 | 0.87538 | 0.80424 | 0.25432 | -121.0922 | -121.5011 | 1.0409 | 0.79684 | 1.2819 | 0.82537 | -121.1735 | 0.97715 | 1.117 | 0.70809 | 0.83806 | -121.6592
1626.125 | 122.1405 | -0.82855 | 121.3028 | 1.4211e-13 | -0.00744 | -0.0022073 | 0.030219 | -0.013696 | 0.010952 | -0.0019839 | 0.007488 | 0.0077131 | -0.0075247 | 0.039835 | 0.0028821 | 0.001048 | -0.048958 | -0.049614 | 0.15743 | -0.082062 | 0.40295 | 0.15215 | -0.003531 | -0.045428 | -0.074666 | 0.10282 | 0.23348 | -0.17081 | -0.33357 | 0.9807 | -121.1454 | 0.8296 | 0.77894 | -0.20177 | -121.3849 | -120.8998 | 0.49499 | -121.2 | 0.82502 | 0.75389 | 0.2589 | -121.0693 | -121.4736 | 0.98598 | 0.74649 | 1.2315 | 0.77959 | -121.1506 | 0.93137 | 1.062 | 0.65774 | 0.78312 | -121.6364
1627.875 | 122.1405 | -0.83771 | 121.2799 | 1.4211e-13 | -0.00744 | -0.0026347 | 0.030433 | -0.013482 | 0.010525 | 0.013277 | 0.007488 | 0.0081403 | -0.0075247 | 0.039835 | 0.0028821 | -0.008109 | -0.044379 | -0.045036 | 0.15743 | -0.086641 | 0.40295 | 0.15673 | -0.00811 | -0.036271 | -0.074666 | 0.098244 | 0.23348 | -0.17081 | -0.32899 | 0.99444 | -121.1225 | 0.8296 | 0.79267 | -0.20177 | -121.3665 | -120.877 | 0.50872 | -121.1817 | 0.8296 | 0.76304 | 0.25432 | -121.0464 | -121.4507 | 0.99514 | 0.75107 | 1.2407 | 0.79333 | -121.1232 | 0.93595 | 1.0712 | 0.66689 | 0.80144 | -121.6089
1629.625 | 122.1405 | -0.88806 | 121.2662 | 1.4211e-13 | -0.0076538 | -0.0019935 | 0.030219 | -0.013909 | 0.010739 | -0.0019839 | 0.0077016 | 0.0079267 | -0.0073111 | 0.039835 | 0.0028821 | -0.003531 | -0.044379 | -0.045036 | 0.15743 | -0.082062 | 0.40753 | 0.15673 | -0.00811 | -0.036271 | -0.079245 | 0.098244 | 0.23806 | -0.17539 | -0.32441 | 1.0448 | -121.1087 | 0.88453 | 0.84303 | -0.20177 | -121.3482 | -120.8586 | 0.56366 | -121.1679 | 0.87995 | 0.80882 | 0.24516 | -121.0281 | -121.4416 | 1.0455 | 0.806 | 1.2956 | 0.84368 | -121.1094 | 0.98631 | 1.1261 | 0.71267 | 0.85179 | -121.5906
1631.3125 | 122.113 | -0.89722 | 121.2845 | 1.4211e-13 | -0.0072264 | -0.0024209 | 0.030433 | -0.013482 | 0.010739 | 0.013277 | 0.007488 | 0.0079267 | -0.0075247 | 0.040049 | 0.0033095 | -0.003531 | -0.044379 | -0.049614 | 0.16201 | -0.082062 | 0.39837 | 0.15673 | 0.001048 | -0.040849 | -0.065509 | 0.1074 | 0.21974 | -0.17539 | -0.33814 | 1.0539 | -121.1225 | 0.89369 | 0.8476 | -0.20635 | -121.3665 | -120.8861 | 0.55907 | -121.1771 | 0.89827 | 0.83171 | 0.27264 | -121.0647 | -121.4599 | 1.0592 | 0.81516 | 1.2956 | 0.85284 | -121.1278 | 1.0046 | 1.117 | 0.72182 | 0.85637 | -121.6226
1633.0781 | 122.1405 | -0.88348 | 121.2753 | 1.4211e-13 | -0.0072264 | -0.0022073 | 0.030433 | -0.013909 | 0.010952 | 0.020908 | 0.0079152 | 0.0077131 | -0.0075247 | 0.040049 | 0.0030959 | 0.001048 | -0.039801 | -0.035879 | 0.16659 | -0.082062 | 0.39837 | 0.16131 | -0.00811 | -0.031692 | -0.074666 | 0.093665 | 0.23348 | -0.16624 | -0.33357 | 1.0448 | -121.1087 | 0.88453 | 0.84761 | -0.19719 | -121.3574 | -120.877 | 0.54992 | -121.1817 | 0.87537 | 0.80882 | 0.2589 | -121.0419 | -121.4416 | 1.0501 | 0.80142 | 1.2819 | 0.84368 | -121.114 | 0.97715 | 1.117 | 0.71725 | 0.85179 | -121.6089
1634.7656 | 122.0673 | -0.92468 | 121.2708 | 1.4211e-13 | -0.0072264 | -0.0022073 | 0.029792 | -0.013909 | 0.010525 | 0.0056466 | 0.007488 | 0.0079267 | -0.0075247 | 0.039835 | 0.0026685 | -0.008109 | -0.039801 | -0.040457 | 0.15743 | -0.082062 | 0.40753 | 0.15673 | -0.003531 | -0.045428 | -0.070087 | 0.089087 | 0.23348 | -0.16624 | -0.33357 | 1.0814 | -121.1133 | 0.91657 | 0.88423 | -0.19719 | -121.3528 | -120.8632 | 0.59112 | -121.1817 | 0.92115 | 0.8546 | 0.26348 | -121.0373 | -121.437 | 1.0821 | 0.84262 | 1.3322 | 0.88488 | -121.114 | 1.0138 | 1.1582 | 0.75845 | 0.87926 | -121.6043
1636.5156 | 122.1405 | -0.88348 | 121.2341 | 1.4211e-13 | -0.0072264 | -0.0024209 | 0.030219 | -0.013909 | 0.010739 | -0.0096144 | 0.007488 | 0.0077131 | -0.0075247 | 0.040049 | 0.0030959 | -0.021844 | -0.044379 | -0.045036 | 0.16201 | -0.072904 | 0.40295 | 0.15673 | -0.003531 | -0.045428 | -0.074666 | 0.10282 | 0.23348 | -0.17539 | -0.33814 | 1.0402 | -121.0721 | 0.86164 | 0.83845 | -0.20177 | -121.307 | -120.8312 | 0.54534 | -121.1313 | 0.87995 | 0.80882 | 0.26348 | -121.0007 | -121.4095 | 1.0455 | 0.81058 | 1.2864 | 0.8391 | -121.0774 | 0.98631 | 1.117 | 0.70809 | 0.83806 | -121.5723
1638.2031 | 122.2183 | -0.89264 | 121.2387 | 1.4211e-13 | -0.00744 | -0.0026347 | 0.030433 | -0.013696 | 0.010739 | -0.0019839 | 0.0072744 | 0.0077131 | -0.0073111 | 0.039835 | 0.0028821 | -0.021844 | -0.039801 | -0.040457 | 0.16201 | -0.082062 | 0.40295 | 0.15673 | -0.012689 | -0.045428 | -0.065509 | 0.10282 | 0.23348 | -0.17539 | -0.31983 | 1.0494 | -121.0767 | 0.87079 | 0.85218 | -0.19719 | -121.3208 | -120.8358 | 0.57281 | -121.1359 | 0.87995 | 0.82713 | 0.25432 | -121.0052 | -121.4141 | 1.0546 | 0.81058 | 1.2956 | 0.85284 | -121.082 | 0.99546 | 1.1261 | 0.71725 | 0.84721 | -121.5585
1639.9531 | 122.1771 | -1.0483 | 121.1975 | 1.4211e-13 | -0.0072264 | -0.0024209 | 0.030219 | -0.013909 | 0.010952 | -0.0019839 | 0.007488 | 0.0077131 | -0.0075247 | 0.039621 | 0.0030959 | -0.008109 | -0.035222 | -0.040457 | 0.16659 | -0.077483 | 0.40753 | 0.15673 | -0.003531 | -0.036271 | -0.070087 | 0.10282 | 0.23806 | -0.17539 | -0.34272 | 1.205 | -121.0309 | 1.0402 | 1.0078 | -0.19719 | -121.275 | -120.79 | 0.70556 | -121.0947 | 1.0447 | 0.97819 | 0.27264 | -120.9595 | -121.3729 | 1.2149 | 0.9708 | 1.4558 | 1.0131 | -121.0408 | 1.1511 | 1.2863 | 0.87289 | 1.012 | -121.5402
1641.7031 | 122.168 | -0.93384 | 121.3211 | 1.4211e-13 | -0.0070128 | -0.0024209 | 0.030219 | -0.013909 | 0.010739 | 0.013277 | 0.007488 | 0.0077131 | -0.0075247 | 0.040049 | 0.0030959 | -0.008109 | -0.044379 | -0.045036 | 0.15743 | -0.077483 | 0.40295 | 0.15215 | -0.003531 | -0.031692 | -0.070087 | 0.093665 | 0.23348 | -0.17081 | -0.33814 | 1.086 | -121.1637 | 0.92573 | 0.8888 | -0.19719 | -121.3986 | -120.9182 | 0.59569 | -121.2274 | 0.93031 | 0.86375 | 0.26806 | -121.0876 | -121.4919 | 1.0913 | 0.85635 | 1.3368 | 0.88946 | -121.169 | 1.0275 | 1.1673 | 0.76302 | 0.90215 | -121.6593
1643.3906 | 122.1863 | -1.236 | 121.0373 | 1.4211e-13 | -0.0070128 | -0.0024209 | 0.030219 | -0.013909 | 0.010952 | -0.0019839 | 0.0077016 | 0.0074993 | -0.0077383 | 0.039835 | 0.0028821 | -0.008109 | -0.035222 | -0.045036 | 0.15743 | -0.072904 | 0.39837 | 0.15215 | -0.003531 | -0.045428 | -0.070087 | 0.098244 | 0.23806 | -0.17081 | -0.33357 | 1.3881 | -120.8799 | 1.2279 | 1.1909 | -0.19719 | -121.1102 | -120.6389 | 0.9024 | -120.939 | 1.2324 | 1.1659 | 0.26348 | -120.7992 | -121.2081 | 1.3934 | 1.1631 | 1.6343 | 1.2007 | -120.8851 | 1.3342 | 1.474 | 1.0651 | 1.1905 | -121.3709
1645.1406 | 122.1909 | -0.94299 | 121.3623 | 1.4211e-13 | -0.006799 | -0.0024209 | 0.030433 | -0.014123 | 0.010739 | -0.0019839 | 0.0079152 | 0.0079267 | -0.0073111 | 0.039621 | 0.0028821 | -0.008109 | -0.039801 | -0.040457 | 0.16201 | -0.072904 | 0.39837 | 0.15673 | -0.003531 | -0.040849 | -0.070087 | 0.093665 | 0.2289 | -0.17081 | -0.33814 | 1.0997 | -121.2003 | 0.93488 | 0.90254 | -0.19719 | -121.4352 | -120.9639 | 0.60485 | -121.2686 | 0.93946 | 0.87291 | 0.26806 | -121.1334 | -121.5331 | 1.105 | 0.87009 | 1.3414 | 0.90319 | -121.2056 | 1.0367 | 1.1719 | 0.77218 | 0.90214 | -121.7004
1646.8906 | 122.1634 | -1.2222 | 121.0876 | 1.4211e-13 | -0.0072264 | -0.0024209 | 0.030433 | -0.013482 | 0.010739 | 0.0056466 | 0.0077016 | 0.0079267 | -0.0073111 | 0.039621 | 0.0026685 | -0.012688 | -0.039801 | -0.040457 | 0.15743 | -0.077483 | 0.40295 | 0.14299 | -0.003531 | -0.036271 | -0.070087 | 0.098244 | 0.23348 | -0.17081 | -0.32899 | 1.3652 | -120.9302 | 1.2095 | 1.1818 | -0.18345 | -121.1651 | -120.6847 | 0.89324 | -120.9894 | 1.2187 | 1.1521 | 0.2589 | -120.8542 | -121.2585 | 1.3797 | 1.1447 | 1.6252 | 1.1824 | -120.9447 | 1.3205 | 1.4557 | 1.0514 | 1.186 | -121.4166
1648.5781 | 122.2046 | -0.95215 | 121.3898 | 1.4211e-13 | -0.0070128 | -0.0024209 | 0.030646 | -0.013909 | 0.010739 | -0.0096144 | 0.0077016 | 0.0081403 | -0.0075247 | 0.039835 | 0.0033095 | -0.017266 | -0.039801 | -0.049614 | 0.16201 | -0.072904 | 0.39837 | 0.15673 | -0.00811 | -0.040849 | -0.065509 | 0.10282 | 0.23806 | -0.17081 | -0.32899 | 1.1089 | -121.2278 | 0.93488 | 0.90253 | -0.20635 | -121.4627 | -120.9914 | 0.62316 | -121.2869 | 0.94404 | 0.88664 | 0.26348 | -121.1517 | -121.5606 | 1.1142 | 0.87924 | 1.3505 | 0.91235 | -121.233 | 1.055 | 1.1902 | 0.78133 | 0.9113 | -121.7188
1650.3125 | 122.3373 | -0.97046 | 121.2433 | 1.4211e-13 | -0.00744 | -0.0022073 | 0.030219 | -0.013482 | 0.010952 | 0.0056466 | 0.007488 | 0.0081403 | -0.0075247 | 0.039621 | 0.0028821 | -0.008109 | -0.048958 | -0.035879 | 0.16201 | -0.072904 | 0.39837 | 0.15673 | -0.00811 | -0.031692 | -0.070087 | 0.10282 | 0.23348 | -0.17081 | -0.32899 | 1.1272 | -121.0813 | 0.96235 | 0.93458 | -0.19261 | -121.3162 | -120.8449 | 0.64147 | -121.1405 | 0.96235 | 0.90037 | 0.2589 | -121.0098 | -121.4141 | 1.1325 | 0.89755 | 1.3688 | 0.9215 | -121.0866 | 1.0733 | 1.2039 | 0.79964 | 0.93877 | -121.5723
1652 | 122.3373 | -1.2863 | 121.0007 | 1.4211e-13 | -0.00744 | -0.0022073 | 0.030005 | -0.013909 | 0.010525 | -0.0096144 | 0.0077016 | 0.0079267 | -0.0077383 | 0.039835 | 0.0028821 | -0.012688 | -0.039801 | -0.045036 | 0.15743 | -0.086641 | 0.39837 | 0.14299 | 0.001048 | -0.031692 | -0.06093 | 0.1074 | 0.23806 | -0.17081 | -0.32899 | 1.4293 | -120.8432 | 1.2736 | 1.2413 | -0.18803 | -121.0873 | -120.6023 | 0.95733 | -120.8933 | 1.2874 | 1.2254 | 0.26806 | -120.7626 | -121.1715 | 1.4437 | 1.1997 | 1.6847 | 1.2465 | -120.8577 | 1.3937 | 1.5244 | 1.1155 | 1.2546 | -121.3297
1653.75 | 122.2229 | -2.1927 | 120.1263 | 1.4211e-13 | -0.0076538 | -0.0024209 | 0.030005 | -0.013696 | 0.010525 | 0.0056466 | 0.0077016 | 0.0079267 | -0.0077383 | 0.039835 | 0.0026685 | -0.003531 | -0.048958 | -0.040457 | 0.16201 | -0.082062 | 0.40753 | 0.15673 | 0.001048 | -0.040849 | -0.070087 | 0.10282 | 0.24264 | -0.16624 | -0.32899 | 2.3494 | -119.9643 | 2.1892 | 2.1522 | -0.19719 | -120.2084 | -119.7188 | 1.8637 | -120.0235 | 2.1937 | 2.1226 | 0.2589 | -119.8837 | -120.2926 | 2.3547 | 2.1106 | 2.6002 | 2.1437 | -119.9696 | 2.2955 | 2.4353 | 2.0265 | 2.1518 | -120.4553
1655.5 | 122.3099 | -1.1948 | 121.0419 | 1.4211e-13 | -0.006799 | -0.0022073 | 0.030646 | -0.013696 | 0.010952 | -0.0019839 | 0.0077016 | 0.0077131 | -0.0075247 | 0.039835 | 0.0030959 | -0.008109 | -0.039801 | -0.035879 | 0.15743 | -0.082062 | 0.39837 | 0.15673 | -0.00811 | -0.040849 | -0.079245 | 0.1074 | 0.23348 | -0.17081 | -0.32899 | 1.3515 | -120.8844 | 1.1867 | 1.1589 | -0.19261 | -121.1239 | -120.6435 | 0.86578 | -120.9345 | 1.1867 | 1.1155 | 0.24974 | -120.8084 | -121.2127 | 1.3522 | 1.1127 | 1.5931 | 1.155 | -120.8851 | 1.3022 | 1.4282 | 1.0239 | 1.1539 | -121.3709
1657.2031 | 122.2641 | -1.4603 | 120.8679 | 1.4211e-13 | -0.0072264 | -0.0019935 | 0.030005 | -0.013482 | 0.010739 | 0.0056466 | 0.007488 | 0.0077131 | -0.0077383 | 0.040049 | 0.0028821 | 0.001048 | -0.044379 | -0.040457 | 0.16201 | -0.077483 | 0.42126 | 0.15215 | -0.003531 | -0.036271 | -0.074666 | 0.093665 | 0.23806 | -0.16166 | -0.33357 | 1.6124 | -120.7059 | 1.4613 | 1.4198 | -0.19261 | -120.9454 | -120.4467 | 1.1267 | -120.7743 | 1.4567 | 1.3856 | 0.2589 | -120.6299 | -121.0296 | 1.6223 | 1.3828 | 1.8815 | 1.4159 | -120.7158 | 1.5539 | 1.6983 | 1.2986 | 1.424 | -121.2015
1658.9688 | 122.2412 | -2.0142 | 120.2591 | 1.4211e-13 | -0.0072264 | -0.0019935 | 0.030005 | -0.013696 | 0.010739 | -0.0019839 | 0.0077016 | 0.0079267 | -0.0077383 | 0.039835 | 0.0026685 | -0.003531 | -0.044379 | -0.045036 | 0.16201 | -0.086641 | 0.4121 | 0.15215 | -0.003531 | -0.040849 | -0.070087 | 0.098244 | 0.23806 | -0.17539 | -0.33357 | 2.1663 | -120.0971 | 2.0106 | 1.9691 | -0.19719 | -120.3457 | -119.847 | 1.6806 | -120.1609 | 2.0106 | 1.9441 | 0.26348 | -120.021 | -120.4345 | 2.1762 | 1.9275 | 2.4263 | 1.9698 | -120.1069 | 2.1124 | 2.2522 | 1.8388 | 1.9733 | -120.5927
1660.6562 | 122.3328 | -2.0462 | 120.2042 | 1.4211e-13 | -0.00744 | -0.0024209 | 0.030219 | -0.013909 | 0.010739 | 0.0056466 | 0.0077016 | 0.0077131 | -0.0075247 | 0.040049 | 0.0030959 | -0.008109 | -0.039801 | -0.035879 | 0.16201 | -0.077483 | 0.40753 | 0.15215 | 0.001048 | -0.040849 | -0.070087 | 0.098244 | 0.23348 | -0.17081 | -0.33814 | 2.1984 | -120.0422 | 2.0381 | 2.0103 | -0.18803 | -120.2816 | -119.7966 | 1.7081 | -120.1059 | 2.0473 | 1.9761 | 0.26806 | -119.9707 | -120.375 | 2.2082 | 1.9687 | 2.4537 | 2.0064 | -120.052 | 2.1444 | 2.2797 | 1.8754 | 2.0054 | -120.5423
1662.4219 | 122.3145 | -3.6392 | 118.5974 | 1.4211e-13 | -0.00744 | -0.0022073 | 0.030433 | -0.014123 | 0.010952 | -0.0019839 | 0.007488 | 0.0079267 | -0.0077383 | 0.039621 | 0.0028821 | -0.008109 | -0.044379 | -0.040457 | 0.16201 | -0.082062 | 0.40753 | 0.15673 | 0.001048 | -0.031692 | -0.070087 | 0.093665 | 0.23348 | -0.17081 | -0.33814 | 3.796 | -118.4354 | 3.6311 | 3.5988 | -0.19719 | -118.6795 | -118.1899 | 3.3011 | -118.5037 | 3.6403 | 3.5691 | 0.26806 | -118.3639 | -118.7682 | 3.8012 | 3.5572 | 4.0467 | 3.5948 | -118.4407 | 3.7329 | 3.8727 | 3.4684 | 3.6075 | -118.9356
1664.1719 | 122.2778 | -1.355 | 121.0327 | 1.4211e-13 | -0.0076538 | -0.0022073 | 0.030219 | -0.014123 | 0.010311 | 0.013277 | 0.0077016 | 0.0077131 | -0.0077383 | 0.039621 | 0.0028821 | -0.008109 | -0.044379 | -0.049614 | 0.16659 | -0.082062 | 0.40753 | 0.15215 | 0.005626 | -0.040849 | -0.065509 | 0.098244 | 0.2289 | -0.17081 | -0.32441 | 1.5071 | -120.8661 | 1.3469 | 1.3054 | -0.20177 | -121.1148 | -120.6252 | 1.0306 | -120.9345 | 1.3606 | 1.2895 | 0.2589 | -120.8038 | -121.2035 | 1.5216 | 1.2729 | 1.7625 | 1.3106 | -120.8806 | 1.4532 | 1.5839 | 1.1842 | 1.3141 | -121.3571
1665.9219 | 122.3557 | -0.86517 | 121.3852 | 1.4211e-13 | -0.0072264 | -0.0026347 | 0.030433 | -0.013909 | 0.011166 | 0.0056466 | 0.0077016 | 0.0077131 | -0.0077383 | 0.039835 | 0.0028821 | -0.026423 | -0.044379 | -0.045036 | 0.15743 | -0.072904 | 0.40753 | 0.15673 | -0.003531 | -0.031692 | -0.074666 | 0.098244 | 0.23806 | -0.17081 | -0.32899 | 1.0219 | -121.2278 | 0.83875 | 0.82014 | -0.20177 | -121.4581 | -120.9777 | 0.53619 | -121.2869 | 0.86164 | 0.79051 | 0.25432 | -121.1471 | -121.556 | 1.0226 | 0.79227 | 1.2727 | 0.82079 | -121.2285 | 0.96342 | 1.1032 | 0.69436 | 0.83348 | -121.7142
1667.6094 | 122.3282 | -0.94299 | 121.3669 | 1.4211e-13 | -0.00744 | -0.0026347 | 0.030219 | -0.013696 | 0.010739 | 0.0056466 | 0.0077016 | 0.0077131 | -0.0077383 | 0.039835 | 0.0030959 | -0.017266 | -0.039801 | -0.045036 | 0.16201 | -0.082062 | 0.40295 | 0.15215 | -0.012689 | -0.045428 | -0.074666 | 0.098244 | 0.23806 | -0.17081 | -0.32899 | 1.0951 | -121.2049 | 0.92573 | 0.89796 | -0.19719 | -121.4489 | -120.9639 | 0.61401 | -121.2686 | 0.9303 | 0.86833 | 0.25432 | -121.1288 | -121.5377 | 1.105 | 0.86093 | 1.3459 | 0.90319 | -121.2147 | 1.0412 | 1.1811 | 0.77218 | 0.89756 | -121.6959
1669.3594 | 122.2733 | -0.98877 | 121.4035 | 1.4211e-13 | -0.0072264 | -0.0022073 | 0.030219 | -0.013482 | 0.010739 | -0.0019839 | 0.0077016 | 0.0077131 | -0.0077383 | 0.040049 | 0.0026685 | -0.003531 | -0.039801 | -0.045036 | 0.15285 | -0.077483 | 0.40295 | 0.15215 | -0.003531 | -0.040849 | -0.070087 | 0.10282 | 0.2289 | -0.16166 | -0.32899 | 1.1409 | -121.2507 | 0.98524 | 0.94373 | -0.19719 | -121.481 | -121.0006 | 0.65978 | -121.3007 | 0.98524 | 0.91868 | 0.2589 | -121.1746 | -121.5652 | 1.1416 | 0.91129 | 1.3917 | 0.94897 | -121.2514 | 1.0916 | 1.2177 | 0.82711 | 0.94792 | -121.7325
1671.0938 | 122.3831 | -0.86517 | 121.431 | 1.4211e-13 | -0.0072264 | -0.0024209 | 0.030219 | -0.013696 | 0.010739 | 0.013277 | 0.007488 | 0.0079267 | -0.0077383 | 0.039194 | 0.0033095 | -0.012688 | -0.039801 | -0.035879 | 0.15743 | -0.086641 | 0.39837 | 0.15215 | -0.003531 | -0.040849 | -0.070087 | 0.098244 | 0.24264 | -0.17081 | -0.32899 | 1.0173 | -121.2735 | 0.85248 | 0.82929 | -0.18803 | -121.5176 | -121.0326 | 0.53619 | -121.3327 | 0.86164 | 0.79509 | 0.2589 | -121.1883 | -121.6018 | 1.0226 | 0.77853 | 1.2635 | 0.82537 | -121.2788 | 0.96342 | 1.1078 | 0.69436 | 0.82432 | -121.76
1672.7812 | 122.374 | -0.87433 | 121.4264 | 1.4211e-13 | -0.00744 | -0.0022073 | 0.030005 | -0.013696 | 0.010525 | -0.0019839 | 0.0072744 | 0.0074993 | -0.0075247 | 0.040049 | 0.0030959 | -0.008109 | -0.039801 | -0.040457 | 0.16201 | -0.086641 | 0.39837 | 0.15215 | 0.001048 | -0.031692 | -0.070087 | 0.10282 | 0.23806 | -0.17539 | -0.32899 | 1.0265 | -121.2644 | 0.86622 | 0.83387 | -0.19261 | -121.513 | -121.028 | 0.54534 | -121.3236 | 0.87538 | 0.80424 | 0.2589 | -121.1883 | -121.6018 | 1.0363 | 0.78769 | 1.2727 | 0.83453 | -121.2742 | 0.97715 | 1.1124 | 0.69894 | 0.84264 | -121.7554
1674.5469 | 122.4014 | -0.86517 | 121.4539 | 1.4211e-13 | -0.00744 | -0.0024209 | 0.030433 | -0.013696 | 0.010525 | -0.0019839 | 0.0077016 | 0.0077131 | -0.0077383 | 0.039835 | 0.0030959 | 0.005626 | -0.035222 | -0.035879 | 0.16201 | -0.072904 | 0.40753 | 0.15673 | 0.001048 | -0.031692 | -0.079245 | 0.1074 | 0.23348 | -0.17081 | -0.32899 | 1.0219 | -121.2918 | 0.8708 | 0.82929 | -0.19261 | -121.5268 | -121.0463 | 0.53619 | -121.3465 | 0.86622 | 0.78593 | 0.24974 | -121.2204 | -121.6247 | 1.0272 | 0.79227 | 1.2727 | 0.82995 | -121.2971 | 0.97257 | 1.0987 | 0.69436 | 0.83348 | -121.7828
1676.2969 | 122.2687 | -0.92926 | 121.5134 | 1.4211e-13 | -0.00744 | -0.0024209 | 0.030005 | -0.013696 | 0.010525 | -0.0019839 | 0.007488 | 0.0077131 | -0.0079521 | 0.039621 | 0.0028821 | 0.001048 | -0.039801 | -0.040457 | 0.16659 | -0.072904 | 0.4121 | 0.15673 | -0.00811 | -0.031692 | -0.070087 | 0.093665 | 0.23806 | -0.17539 | -0.32899 | 1.086 | -121.3468 | 0.93031 | 0.8888 | -0.19719 | -121.5863 | -121.1013 | 0.60027 | -121.4197 | 0.92115 | 0.85917 | 0.2589 | -121.2753 | -121.6888 | 1.0958 | 0.85636 | 1.3414 | 0.88946 | -121.3566 | 1.0229 | 1.1673 | 0.75387 | 0.89757 | -121.8424
1678.0625 | 122.319 | -0.91095 | 121.5134 | 1.4211e-13 | -0.00744 | -0.0026347 | 0.030219 | -0.013696 | 0.010739 | -0.0019839 | 0.0077016 | 0.0079267 | -0.0077383 | 0.040049 | 0.0030959 | -0.008109 | -0.030644 | -0.031301 | 0.17117 | -0.077483 | 0.4121 | 0.16131 | 0.001048 | -0.031692 | -0.065509 | 0.10282 | 0.23806 | -0.17997 | -0.33357 | 1.0723 | -121.3422 | 0.90284 | 0.87965 | -0.19261 | -121.5909 | -121.1013 | 0.57739 | -121.4105 | 0.912 | 0.84544 | 0.26806 | -121.2753 | -121.6933 | 1.0821 | 0.83347 | 1.3231 | 0.88031 | -121.3521 | 1.0138 | 1.149 | 0.73098 | 0.87926 | -121.8469
1679.75 | 122.406 | -0.89264 | 121.4493 | 1.4211e-13 | -0.0072264 | -0.0022073 | 0.029792 | -0.013482 | 0.010525 | 0.013277 | 0.0079152 | 0.0079267 | -0.0077383 | 0.040049 | 0.0028821 | -0.012688 | -0.039801 | -0.040457 | 0.16659 | -0.082062 | 0.40753 | 0.16131 | 0.005626 | -0.031692 | -0.074666 | 0.10282 | 0.24264 | -0.16624 | -0.33357 | 1.0539 | -121.2827 | 0.87995 | 0.85218 | -0.20177 | -121.5313 | -121.0418 | 0.55907 | -121.3465 | 0.89826 | 0.81797 | 0.2589 | -121.2066 | -121.6155 | 1.0592 | 0.81058 | 1.3002 | 0.85284 | -121.288 | 0.99546 | 1.1353 | 0.7264 | 0.86095 | -121.7828
1681.5 | 122.3007 | -0.91095 | 121.4905 | 1.4211e-13 | -0.00744 | -0.0026347 | 0.030219 | -0.013909 | 0.010525 | 0.020908 | 0.0079152 | 0.0074993 | -0.0073111 | 0.040049 | 0.0030959 | 0.001048 | -0.035222 | -0.035879 | 0.16201 | -0.082062 | 0.40295 | 0.15673 | -0.012689 | -0.040849 | -0.074666 | 0.1074 | 0.23348 | -0.17539 | -0.33357 | 1.0677 | -121.3285 | 0.912 | 0.87507 | -0.19261 | -121.5725 | -121.0875 | 0.57739 | -121.3831 | 0.89826 | 0.83628 | 0.2589 | -121.257 | -121.6659 | 1.073 | 0.82889 | 1.3139 | 0.87573 | -121.3337 | 1.0184 | 1.1444 | 0.73556 | 0.8701 | -121.824
1683.2031 | 122.3145 | -0.89264 | 121.5088 | 1.4211e-13 | -0.00744 | -0.0024209 | 0.029792 | -0.014123 | 0.010739 | -0.0019839 | 0.0072744 | 0.0077131 | -0.0075247 | 0.039835 | 0.0026685 | -0.008109 | -0.039801 | -0.045036 | 0.15285 | -0.086641 | 0.39837 | 0.16131 | -0.003531 | -0.036271 | -0.070087 | 0.098244 | 0.23806 | -0.16624 | -0.32441 | 1.0539 | -121.3559 | 0.88453 | 0.8476 | -0.20635 | -121.5954 | -121.1104 | 0.56823 | -121.4105 | 0.88911 | 0.82255 | 0.25432 | -121.2707 | -121.675 | 1.0455 | 0.806 | 1.291 | 0.85284 | -121.3475 | 0.99088 | 1.1307 | 0.7264 | 0.85637 | -121.8332
1684.9531 | 122.3969 | -0.83313 | 121.4905 | 1.4211e-13 | -0.00744 | -0.0026347 | 0.030005 | -0.013909 | 0.010739 | 0.0056466 | 0.007488 | 0.0079267 | -0.0077383 | 0.039835 | 0.0028821 | -0.012688 | -0.035222 | -0.040457 | 0.15285 | -0.086641 | 0.39837 | 0.15215 | 0.001048 | -0.031692 | -0.079245 | 0.10282 | 0.23348 | -0.17539 | -0.33357 | 0.98528 | -121.3376 | 0.82044 | 0.79267 | -0.19261 | -121.5771 | -121.0921 | 0.49957 | -121.3877 | 0.83418 | 0.75389 | 0.25432 | -121.257 | -121.6659 | 0.98598 | 0.74649 | 1.2315 | 0.79791 | -121.3383 | 0.93595 | 1.0666 | 0.65774 | 0.80144 | -121.824
1686.7031 | 122.4243 | -0.82855 | 121.4951 | 1.4211e-13 | -0.0072264 | -0.0026347 | 0.030433 | -0.013482 | 0.010739 | -0.0019839 | 0.007488 | 0.0077131 | -0.0073111 | 0.039835 | 0.0024549 | -0.008109 | -0.048958 | -0.040457 | 0.16201 | -0.077483 | 0.39837 | 0.15673 | 0.001048 | -0.031692 | -0.074666 | 0.1074 | 0.23348 | -0.17081 | -0.32899 | 0.98528 | -121.333 | 0.82044 | 0.78809 | -0.19719 | -121.5725 | -121.0967 | 0.49957 | -121.3877 | 0.8296 | 0.75389 | 0.25432 | -121.2616 | -121.6659 | 0.99056 | 0.75107 | 1.2269 | 0.77959 | -121.3383 | 0.93595 | 1.062 | 0.65774 | 0.79686 | -121.824
1688.4531 | 122.3511 | -0.87891 | 121.5271 | 1.4211e-13 | -0.0072264 | -0.0024209 | 0.030005 | -0.013909 | 0.010952 | 0.0056466 | 0.0077016 | 0.0077131 | -0.0075247 | 0.040049 | 0.0026685 | -0.012688 | -0.044379 | -0.035879 | 0.16201 | -0.077483 | 0.39837 | 0.15673 | 0.001048 | -0.027113 | -0.065509 | 0.098244 | 0.2289 | -0.17539 | -0.33357 | 1.0356 | -121.3651 | 0.86622 | 0.84303 | -0.19261 | -121.6046 | -121.1287 | 0.54534 | -121.4289 | 0.87995 | 0.8134 | 0.26806 | -121.2982 | -121.7025 | 1.0409 | 0.80142 | 1.2773 | 0.83453 | -121.3704 | 0.97715 | 1.1078 | 0.70351 | 0.85179 | -121.8607
1690.2031 | 122.4335 | -0.85602 | 121.4951 | 1.4211e-13 | -0.0072264 | -0.0024209 | 0.030005 | -0.014123 | 0.010739 | -0.0019839 | 0.0077016 | 0.0077131 | -0.0077383 | 0.040476 | 0.0030959 | -0.008109 | -0.039801 | -0.045036 | 0.16201 | -0.072904 | 0.39837 | 0.15673 | 0.001048 | -0.040849 | -0.070087 | 0.10282 | 0.24264 | -0.16624 | -0.33357 | 1.0127 | -121.333 | 0.84791 | 0.81098 | -0.20177 | -121.568 | -121.0967 | 0.52245 | -121.3922 | 0.85707 | 0.78593 | 0.26348 | -121.2524 | -121.6613 | 1.018 | 0.78311 | 1.2544 | 0.81622 | -121.3383 | 0.95884 | 1.0987 | 0.68978 | 0.81517 | -121.8286
1691.9531 | 122.3373 | -2.5452 | 119.8425 | 1.4211e-13 | -0.0076538 | -0.0022073 | 0.030219 | -0.013909 | 0.010739 | 0.0056466 | 0.0079152 | 0.0077131 | -0.0077383 | 0.040049 | 0.0028821 | -0.008109 | -0.039801 | -0.031301 | 0.15743 | -0.082062 | 0.39837 | 0.15215 | -0.003531 | -0.036271 | -0.070087 | 0.098244 | 0.23348 | -0.17081 | -0.33357 | 2.6973 | -119.6851 | 2.5371 | 2.5139 | -0.18345 | -119.9246 | -119.4442 | 2.2116 | -119.7443 | 2.5416 | 2.4751 | 0.26348 | -119.609 | -120.0133 | 2.7026 | 2.4631 | 2.9435 | 2.5054 | -119.6904 | 2.6434 | 2.7786 | 2.3744 | 2.5089 | -120.1761
1693.6406 | 122.3007 | -0.94299 | 121.4355 | 1.4211e-13 | -0.0072264 | -0.0024209 | 0.030219 | -0.013696 | 0.010525 | -0.0019839 | 0.0077016 | 0.0077131 | -0.0075247 | 0.040049 | 0.0030959 | -0.003531 | -0.048958 | -0.040457 | 0.16201 | -0.086641 | 0.40295 | 0.14757 | -0.003531 | -0.036271 | -0.079245 | 0.10282 | 0.23348 | -0.16624 | -0.32899 | 1.0906 | -121.2735 | 0.93946 | 0.90254 | -0.18803 | -121.5222 | -121.0326 | 0.61401 | -121.3327 | 0.93946 | 0.86375 | 0.24974 | -121.2021 | -121.6018 | 1.105 | 0.85635 | 1.3459 | 0.89403 | -121.288 | 1.0458 | 1.1765 | 0.77676 | 0.90672 | -121.7645
1695.3906 | 122.3145 | -1.1215 | 121.2524 | 1.4211e-13 | -0.00744 | -0.0022073 | 0.030219 | -0.013909 | 0.011166 | -0.0019839 | 0.007488 | 0.0079267 | -0.0077383 | 0.040049 | 0.0024549 | -0.012688 | -0.039801 | -0.035879 | 0.16201 | -0.077483 | 0.40753 | 0.15215 | 0.001048 | -0.036271 | -0.070087 | 0.098244 | 0.23348 | -0.17539 | -0.32899 | 1.2737 | -121.0904 | 1.1088 | 1.0856 | -0.18803 | -121.3299 | -120.8449 | 0.79253 | -121.1542 | 1.1226 | 1.0514 | 0.2589 | -121.019 | -121.4278 | 1.2835 | 1.044 | 1.529 | 1.0817 | -121.1003 | 1.2198 | 1.355 | 0.94613 | 1.0853 | -121.5814
1697.1406 | 122.2824 | -0.91095 | 121.5317 | 1.4211e-13 | -0.0072264 | -0.0026347 | 0.030219 | -0.013909 | 0.010739 | -0.0019839 | 0.007488 | 0.0074993 | -0.0075247 | 0.039621 | 0.0030959 | -0.012688 | -0.039801 | -0.040457 | 0.14827 | -0.086641 | 0.39837 | 0.16131 | 0.001048 | -0.031692 | -0.070087 | 0.10282 | 0.23348 | -0.17081 | -0.32899 | 1.0723 | -121.3834 | 0.89826 | 0.87049 | -0.20177 | -121.6183 | -121.1333 | 0.58196 | -121.4289 | 0.912 | 0.84086 | 0.2589 | -121.2982 | -121.7025 | 1.0592 | 0.82431 | 1.3093 | 0.87115 | -121.3704 | 1.0138 | 1.1444 | 0.74013 | 0.87926 | -121.8607
1698.8281 | 122.4243 | -0.88348 | 121.5088 | 1.4211e-13 | -0.0076538 | -0.0028483 | 0.030219 | -0.013909 | 0.010739 | 0.013277 | 0.0072744 | 0.0077131 | -0.0077383 | 0.039835 | 0.0028821 | -0.008109 | -0.048958 | -0.040457 | 0.15743 | -0.077483 | 0.40753 | 0.15673 | -0.00811 | -0.031692 | -0.065509 | 0.098244 | 0.23348 | -0.17081 | -0.32899 | 1.0402 | -121.3514 | 0.87538 | 0.84303 | -0.19719 | -121.5863 | -121.1013 | 0.5545 | -121.4105 | 0.87537 | 0.81798 | 0.26348 | -121.2753 | -121.6796 | 1.0409 | 0.806 | 1.291 | 0.83453 | -121.3521 | 0.98173 | 1.117 | 0.71267 | 0.85179 | -121.8378
1700.5781 | 122.2595 | -16.0584 | 106.1691 | 1.4211e-13 | -0.0078674 | -0.0028483 | 0.030005 | -0.013909 | 0.010525 | 0.013277 | 0.0072744 | 0.0077131 | -0.0075247 | 0.040049 | 0.0028821 | -0.003531 | -0.035222 | -0.035879 | 0.15285 | -0.077483 | 0.40753 | 0.12468 | 0.010205 | -0.031692 | -0.051772 | 0.11656 | 0.24721 | -0.17539 | -0.32441 | 16.183 | -106.0163 | 16.0548 | 16.0225 | -0.16056 | -106.2466 | -105.7616 | 15.7339 | -106.0526 | 16.0686 | 16.0066 | 0.27264 | -105.9219 | -106.3445 | 16.2112 | 15.9809 | 16.4659 | 16.0231 | -106.0444 | 16.1749 | 16.3056 | 15.883 | 16.0267 | -106.4935
1702.3281 | 122.3419 | -2.2476 | 120.1721 | 1.4211e-13 | -0.0070128 | -0.0022073 | 0.030219 | -0.013909 | 0.010952 | 0.013277 | 0.007488 | 0.0074993 | -0.0079521 | 0.040262 | 0.0028821 | -0.012688 | -0.044379 | -0.040457 | 0.16201 | -0.072904 | 0.40295 | 0.15215 | 0.001048 | -0.040849 | -0.074666 | 0.10282 | 0.24264 | -0.17997 | -0.33814 | 2.3998 | -120.0101 | 2.2349 | 2.2072 | -0.19261 | -120.245 | -119.7692 | 1.9095 | -120.0693 | 2.2487 | 2.173 | 0.26348 | -119.9295 | -120.3521 | 2.4096 | 2.1747 | 2.6506 | 2.2032 | -120.02 | 2.3504 | 2.4903 | 2.0676 | 2.2068 | -120.5103
1704.0781 | 122.406 | -2.3621 | 119.8929 | 1.4211e-13 | -0.0072264 | -0.0019935 | 0.030219 | -0.013909 | 0.010952 | -0.0019839 | 0.0072744 | 0.0077131 | -0.0077383 | 0.039835 | 0.0028821 | -0.003531 | -0.044379 | -0.045036 | 0.16659 | -0.082062 | 0.39837 | 0.15673 | -0.003531 | -0.040849 | -0.074666 | 0.10282 | 0.23348 | -0.17539 | -0.32899 | 2.5188 | -119.7263 | 2.3585 | 2.317 | -0.20177 | -119.9749 | -119.4945 | 2.0331 | -119.7901 | 2.3585 | 2.2874 | 0.25432 | -119.6594 | -120.0683 | 2.5286 | 2.28 | 2.7604 | 2.3177 | -119.7362 | 2.4649 | 2.5955 | 2.1867 | 2.3212 | -120.2219
1705.7656 | 122.4518 | -2.0691 | 120.3552 | 1.4211e-13 | -0.0072264 | -0.0024209 | 0.030219 | -0.013696 | 0.010739 | 0.0056466 | 0.0070608 | 0.0077131 | -0.0075247 | 0.039835 | 0.0028821 | -0.012688 | -0.044379 | -0.040457 | 0.15743 | -0.082062 | 0.39837 | 0.15215 | 0.001048 | -0.040849 | -0.070087 | 0.10282 | 0.24264 | -0.16624 | -0.32899 | 2.2212 | -120.1978 | 2.0564 | 2.0286 | -0.19261 | -120.4373 | -119.9569 | 1.7401 | -120.2524 | 2.0701 | 1.999 | 0.2589 | -120.1126 | -120.5215 | 2.2265 | 1.987 | 2.4675 | 2.0247 | -120.2031 | 2.1719 | 2.3117 | 1.9029 | 2.0282 | -120.6842
1707.5469 | 122.3419 | -1.9547 | 120.5383 | 1.4211e-13 | -0.0076538 | -0.0026347 | 0.030433 | -0.013909 | 0.010739 | -0.0096144 | 0.007488 | 0.0072857 | -0.0073111 | 0.040049 | 0.0028821 | -0.003531 | -0.044379 | -0.040457 | 0.15285 | -0.086641 | 0.39837 | 0.15215 | -0.003531 | -0.036271 | -0.065509 | 0.098244 | 0.23806 | -0.16624 | -0.32899 | 2.1068 | -120.3855 | 1.9511 | 1.9142 | -0.19261 | -120.625 | -120.14 | 1.6257 | -120.4401 | 1.9511 | 1.8891 | 0.26348 | -120.3003 | -120.7046 | 2.1075 | 1.868 | 2.353 | 1.9103 | -120.3862 | 2.0529 | 2.1927 | 1.7884 | 1.9184 | -120.8673
1709.25 | 122.4243 | -1.5747 | 120.7672 | 1.4211e-13 | -0.0070128 | -0.0022073 | 0.030005 | -0.013909 | 0.010739 | -0.0019839 | 0.007488 | 0.0077131 | -0.0079521 | 0.040262 | 0.0026685 | -0.003531 | -0.039801 | -0.040457 | 0.15285 | -0.077483 | 0.39837 | 0.15673 | 0.001048 | -0.040849 | -0.065509 | 0.1074 | 0.23348 | -0.17539 | -0.33814 | 1.7314 | -120.6144 | 1.5712 | 1.5343 | -0.19719 | -120.8447 | -120.3688 | 1.2366 | -120.6598 | 1.5758 | 1.5092 | 0.27264 | -120.5337 | -120.9426 | 1.7276 | 1.4972 | 1.9731 | 1.5349 | -120.6105 | 1.6821 | 1.8082 | 1.3993 | 1.5339 | -121.1054
1711 | 122.3969 | -1.7075 | 120.4742 | 1.4211e-13 | -0.0076538 | -0.0019935 | 0.030219 | -0.014123 | 0.010739 | 0.0056466 | 0.0072744 | 0.0077131 | -0.0077383 | 0.040262 | 0.0028821 | -0.003531 | -0.035222 | -0.049614 | 0.15285 | -0.072904 | 0.40295 | 0.1201 | 0.001048 | -0.040849 | -0.070087 | 0.1074 | 0.24264 | -0.16624 | -0.33357 | 1.8276 | -120.3214 | 1.7039 | 1.6578 | -0.16971 | -120.5471 | -120.0713 | 1.3739 | -120.3668 | 1.7085 | 1.6374 | 0.26348 | -120.2316 | -120.6405 | 1.8603 | 1.6346 | 2.1104 | 1.6722 | -120.3541 | 1.8149 | 1.9501 | 1.5412 | 1.6666 | -120.8078
1712.6875 | 122.4655 | -1.9775 | 120.5658 | 1.4211e-13 | -0.0076538 | -0.0022073 | 0.030433 | -0.013909 | 0.010739 | 0.013277 | 0.0077016 | 0.0079267 | -0.0075247 | 0.040262 | 0.0028821 | -0.008109 | -0.044379 | -0.040457 | 0.14827 | -0.086641 | 0.39837 | 0.16131 | -0.00811 | -0.031692 | -0.074666 | 0.093665 | 0.24264 | -0.17539 | -0.33357 | 2.1388 | -120.4175 | 1.9694 | 1.9371 | -0.20177 | -120.6524 | -120.1674 | 1.644 | -120.4721 | 1.9694 | 1.9029 | 0.2589 | -120.3232 | -120.7412 | 2.1258 | 1.8909 | 2.3759 | 1.9332 | -120.4045 | 2.0712 | 2.2202 | 1.8021 | 1.9458 | -120.8994
1714.4375 | 122.3373 | -2.298 | 120.1859 | 1.4211e-13 | -0.0076538 | -0.0026347 | 0.030219 | -0.013696 | 0.010739 | -0.0096144 | 0.007488 | 0.0079267 | -0.0073111 | 0.040262 | 0.0026685 | -0.003531 | -0.039801 | -0.040457 | 0.16201 | -0.077483 | 0.39837 | 0.14299 | 0.001048 | -0.036271 | -0.070087 | 0.1074 | 0.23348 | -0.17081 | -0.33814 | 2.441 | -120.0238 | 2.2944 | 2.2575 | -0.18345 | -120.2633 | -119.7875 | 1.9598 | -120.0785 | 2.299 | 2.2279 | 0.26806 | -119.9524 | -120.3567 | 2.46 | 2.2205 | 2.6963 | 2.2582 | -120.0429 | 2.4054 | 2.5315 | 2.1272 | 2.2617 | -120.524
1716.125 | 122.5113 | -1.9089 | 120.5429 | 1.4211e-13 | -0.00744 | -0.0024209 | 0.030219 | -0.014337 | 0.010952 | 0.013277 | 0.008129 | 0.0074993 | -0.0077383 | 0.040262 | 0.0024549 | -0.008109 | -0.048958 | -0.035879 | 0.15285 | -0.077483 | 0.39837 | 0.14757 | 0.005626 | -0.031692 | -0.065509 | 0.10282 | 0.24264 | -0.17081 | -0.33357 | 2.0564 | -120.3901 | 1.9008 | 1.873 | -0.18345 | -120.6204 | -120.1445 | 1.5753 | -120.4401 | 1.9145 | 1.8434 | 0.26806 | -120.3003 | -120.7137 | 2.0617 | 1.8314 | 2.3072 | 1.8599 | -120.3953 | 2.0117 | 2.1515 | 1.7381 | 1.8772 | -120.8765
1717.875 | 122.3236 | -3.7537 | 118.6478 | 1.4211e-13 | -0.0076538 | -0.0019935 | 0.030005 | -0.014123 | 0.010525 | 0.0056466 | 0.0070608 | 0.0081403 | -0.0079521 | 0.040476 | 0.0030959 | -0.008109 | -0.044379 | -0.026723 | 0.14827 | -0.082062 | 0.39837 | 0.15673 | 0.001048 | -0.031692 | -0.070087 | 0.1074 | 0.24264 | -0.17081 | -0.33357 | 3.9104 | -118.4995 | 3.7456 | 3.7269 | -0.18345 | -118.7298 | -118.2494 | 3.4201 | -118.5404 | 3.7547 | 3.6836 | 0.26348 | -118.4051 | -118.8186 | 3.9019 | 3.6716 | 4.152 | 3.7093 | -118.491 | 3.8611 | 3.9963 | 3.5828 | 3.722 | -118.9813
1719.6094 | 122.3465 | -3.6026 | 118.7805 | 1.4211e-13 | -0.00744 | -0.0026347 | 0.030005 | -0.014123 | 0.010739 | -0.0019839 | 0.0072744 | 0.0077131 | -0.0075247 | 0.040262 | 0.0028821 | 0.001048 | -0.035222 | -0.040457 | 0.15743 | -0.086641 | 0.39837 | 0.15215 | 0.001048 | -0.031692 | -0.070087 | 0.1074 | 0.24264 | -0.16624 | -0.33814 | 3.7548 | -118.6231 | 3.6036 | 3.5621 | -0.19261 | -118.8672 | -118.3821 | 3.2645 | -118.6731 | 3.6036 | 3.5325 | 0.26806 | -118.5379 | -118.9468 | 3.76 | 3.516 | 4.001 | 3.5674 | -118.6284 | 3.71 | 3.8452 | 3.4364 | 3.5709 | -119.1187
1721.3594 | 118.2999 | -26.1795 | 91.8503 | 1.4211e-13 | -0.0076538 | -0.0024209 | 0.029792 | -0.013909 | 0.010098 | -0.0019839 | 0.007488 | 0.0077131 | -0.0077383 | 0.040262 | 0.0030959 | 0.005626 | -0.030644 | -0.026723 | 0.17117 | -0.077483 | 0.39837 | 0.15215 | 0.010205 | -0.027113 | -0.06093 | 0.11656 | 0.24264 | -0.17539 | -0.31983 | 26.3317 | -91.6791 | 26.1851 | 26.1528 | -0.17888 | -91.9278 | -91.4519 | 25.8597 | -91.7337 | 26.1897 | 26.1186 | 0.2589 | -91.6076 | -92.0257 | 26.3507 | 26.102 | 26.5779 | 26.1489 | -91.6981 | 26.2961 | 26.4221 | 26.0041 | 26.1524 | -92.1701
1723.1094 | 117.659 | -26.7838 | 90.8203 | 1.4211e-13 | -0.0076538 | -0.0022073 | 0.029792 | -0.013696 | 0.010098 | -0.0096144 | 0.0077016 | 0.0079267 | -0.0077383 | 0.040262 | 0.0028821 | 0.001048 | -0.035222 | -0.031301 | 0.16659 | -0.077483 | 0.40295 | 0.10178 | 0.010205 | -0.022535 | -0.06093 | 0.11656 | 0.24264 | -0.17081 | -0.31983 | 26.8855 | -90.6537 | 26.7848 | 26.7525 | -0.13309 | -90.8978 | -90.4174 | 26.4639 | -90.7038 | 26.794 | 26.7228 | 0.2589 | -90.5777 | -90.9911 | 26.9503 | 26.7063 | 27.1867 | 26.7485 | -90.7185 | 26.9003 | 27.0264 | 26.6129 | 26.7612 | -91.1401
1724.8438 | 117.3157 | -29.6585 | 87.3825 | 1.4211e-13 | -0.008081 | -0.0024209 | 0.029792 | -0.013482 | 0.0098841 | 0.0056466 | 0.007488 | 0.0077131 | -0.0073111 | 0.040262 | 0.0028821 | 0.001048 | -0.035222 | -0.031301 | 0.17117 | -0.072904 | 0.41668 | 0.092626 | 0.005626 | -0.031692 | -0.06093 | 0.11198 | 0.25179 | -0.17081 | -0.31983 | 29.7511 | -87.2113 | 29.6596 | 29.6272 | -0.12393 | -87.4554 | -86.9658 | 29.3387 | -87.2705 | 29.6641 | 29.5976 | 0.2589 | -87.1307 | -87.5533 | 29.8297 | 29.5856 | 30.0752 | 29.6233 | -87.2899 | 29.7705 | 29.9103 | 29.4877 | 29.6268 | -87.7023
1726.5156 | 115.535 | -77.0828 | 38.3881 | 1.4211e-13 | -0.0076538 | -0.0026347 | 0.029364 | -0.013696 | 0.0098841 | -0.0096144 | 0.0072744 | 0.0081403 | -0.0081657 | 0.040049 | 0.0026685 | 0.028518 | -0.007751 | -0.008409 | 0.1849 | -0.068325 | 0.43042 | 0.15215 | 0.02852 | -0.00422 | -0.038036 | 0.13945 | 0.27926 | -0.17539 | -0.29236 | 77.235 | -38.2032 | 77.1113 | 77.0744 | -0.16056 | -38.4564 | -37.9576 | 76.7905 | -38.2486 | 77.1113 | 77.0448 | 0.25432 | -38.1088 | -38.5635 | 77.2677 | 77.0145 | 77.5132 | 77.0751 | -38.2359 | 77.2223 | 77.3621 | 76.9074 | 77.0786 | -38.6804
1728.2812 | 119.6594 | -119.1696 | 0.27466 | 1.4211e-13 | -0.0078674 | -0.0022073 | 0.030005 | -0.013696 | 0.010739 | 0.0056466 | 0.0077016 | 0.0079267 | -0.0075247 | 0.040476 | 0.0026685 | 0.037675 | 0.010564 | 0.000747 | 0.20321 | -0.050009 | 0.45331 | 0.15673 | 0.046835 | 0.004938 | -0.015143 | 0.15776 | 0.29758 | -0.17081 | -0.2832 | 119.3263 | -0.071444 | 119.2073 | 119.1704 | -0.15598 | -0.32467 | 0.17865 | 118.8864 | -0.11689 | 119.2165 | 119.1545 | 0.26805 | 0.022922 | -0.44547 | 119.3728 | 119.1196 | 119.6229 | 119.1802 | -0.11793 | 119.3274 | 119.4672 | 118.9988 | 119.1746 | -0.55786
1729.9531 | 120.0485 | -119.6045 | 0.21515 | 1.4211e-13 | -0.0076538 | -0.0022073 | 0.030005 | -0.013909 | 0.010952 | 0.0056466 | 0.0079152 | 0.0077131 | -0.0077383 | 0.040049 | 0.0028821 | 0.033096 | 0.001407 | 0.000747 | 0.20321 | -0.04543 | 0.45331 | 0.16131 | 0.042256 | 0.004938 | -0.0243 | 0.14861 | 0.293 | -0.17081 | -0.28778 | 119.7658 | -0.011935 | 119.6376 | 119.6052 | -0.16056 | -0.26058 | 0.23816 | 119.3167 | -0.066542 | 119.6467 | 119.5802 | 0.26348 | 0.077852 | -0.38596 | 119.8077 | 119.5591 | 120.0578 | 119.6059 | -0.053839 | 119.7531 | 119.8975 | 119.4337 | 119.6094 | -0.50293
1731.7031 | 120.1172 | -119.8059 | 0.25635 | 1.4211e-13 | -0.0072264 | -0.0024209 | 0.030005 | -0.014123 | 0.010525 | -0.0096144 | 0.0077016 | 0.0074993 | -0.0075247 | 0.040476 | 0.0028821 | 0.037675 | 0.005985 | 0.009904 | 0.20779 | -0.059167 | 0.44873 | 0.16589 | 0.051413 | 0.018674 | -0.010564 | 0.15776 | 0.29758 | -0.17539 | -0.27404 | 119.9718 | -0.048555 | 119.8436 | 119.8158 | -0.15599 | -0.31551 | 0.19238 | 119.5319 | -0.098584 | 119.8573 | 119.7953 | 0.26348 | 0.041232 | -0.43174 | 120.0137 | 119.7467 | 120.2546 | 119.8119 | -0.090459 | 119.9637 | 120.1035 | 119.6305 | 119.8246 | -0.53039
1733.3906 | 120.2545 | -119.8883 | 0.21973 | 1.4211e-13 | -0.0078674 | -0.0024209 | 0.030219 | -0.013909 | 0.010525 | 0.0056466 | 0.0077016 | 0.0077131 | -0.0077383 | 0.040476 | 0.0028821 | 0.033096 | 0.001407 | 0.009904 | 0.21237 | -0.063746 | 0.44873 | 0.15215 | 0.046835 | 0.004938 | -0.015143 | 0.15776 | 0.293 | -0.17081 | -0.2832 | 120.0405 | -0.007356 | 119.9214 | 119.8982 | -0.14225 | -0.28347 | 0.22901 | 119.6051 | -0.061963 | 119.9351 | 119.8732 | 0.26805 | 0.073274 | -0.39054 | 120.1007 | 119.8246 | 120.337 | 119.8897 | -0.067575 | 120.0461 | 120.1813 | 119.7175 | 119.8932 | -0.50293
1735.1406 | 120.2271 | -119.9982 | 0.22888 | 1.4211e-13 | -0.0076538 | -0.0024209 | 0.030219 | -0.013909 | 0.010739 | 0.0056466 | 0.007488 | 0.0077131 | -0.0073111 | 0.040476 | 0.0024549 | 0.037675 | 0.005985 | 0.005325 | 0.20779 | -0.068325 | 0.44873 | 0.15673 | 0.042256 | 0.009516 | -0.015143 | 0.15776 | 0.293 | -0.17081 | -0.27862 | 120.1549 | -0.021089 | 120.0358 | 120.0035 | -0.15141 | -0.29721 | 0.21985 | 119.7195 | -0.071118 | 120.0404 | 119.983 | 0.26348 | 0.064119 | -0.3997 | 120.206 | 119.9298 | 120.4469 | 120.0042 | -0.072151 | 120.1559 | 120.2912 | 119.8274 | 120.0077 | -0.5075
1736.8125 | 120.3873 | -120.0485 | 0.21515 | 1.4211e-13 | -0.00744 | -0.0024209 | 0.030005 | -0.013909 | 0.010739 | -0.0019839 | 0.0072744 | 0.0077131 | -0.0077383 | 0.040476 | 0.0028821 | 0.037675 | 0.001407 | 0.014482 | 0.20779 | -0.008799 | 0.45331 | 0.15215 | 0.046835 | 0.014095 | -0.015143 | 0.15776 | 0.293 | -0.17081 | -0.27862 | 120.2007 | -0.007356 | 120.0862 | 120.063 | -0.13767 | -0.22395 | 0.23816 | 119.7699 | -0.057385 | 120.0954 | 120.0334 | 0.26348 | 0.077852 | -0.38596 | 120.2563 | 120.0397 | 120.5018 | 120.0499 | -0.062997 | 120.2063 | 120.3415 | 119.8777 | 120.0626 | -0.49377
1738.5625 | 120.4102 | -120.1035 | 0.24261 | 1.4211e-13 | -0.0076538 | -0.0022073 | 0.030005 | -0.014123 | 0.010739 | -0.0019839 | 0.007488 | 0.0072857 | -0.0077383 | 0.040262 | 0.0030959 | 0.037675 | 0.001407 | 0.009904 | 0.20779 | -0.059167 | 0.44873 | 0.15215 | 0.055992 | 0.000359 | -0.010564 | 0.14861 | 0.29758 | -0.16624 | -0.2832 | 120.2556 | -0.034822 | 120.1411 | 120.1134 | -0.14225 | -0.30178 | 0.20612 | 119.8203 | -0.094008 | 120.1594 | 120.0929 | 0.27263 | 0.054965 | -0.40885 | 120.3112 | 120.0443 | 120.5522 | 120.1049 | -0.090463 | 120.2521 | 120.401 | 119.9372 | 120.1038 | -0.52581
1740.3281 | 120.4422 | -120.1813 | 0.23804 | 1.4211e-13 | -0.0076538 | -0.0026347 | 0.030219 | -0.013909 | 0.010739 | -0.0096144 | 0.0072744 | 0.0081403 | -0.0077383 | 0.04069 | 0.0026685 | 0.037675 | 0.001407 | 0.009904 | 0.20779 | -0.031693 | 0.45789 | 0.14757 | 0.051413 | 0.014095 | -0.019721 | 0.15776 | 0.293 | -0.17081 | -0.27862 | 120.3288 | -0.030244 | 120.2189 | 120.1912 | -0.13767 | -0.26973 | 0.21985 | 119.9027 | -0.080273 | 120.2327 | 120.1616 | 0.2589 | 0.054964 | -0.40885 | 120.3891 | 120.1496 | 120.6392 | 120.1827 | -0.090464 | 120.339 | 120.4743 | 120.0105 | 120.1954 | -0.51666
1742.0156 | 120.5383 | -120.195 | 0.22888 | 1.4211e-13 | -0.0078674 | -0.0024209 | 0.030005 | -0.014123 | 0.010952 | 0.0056466 | 0.0072744 | 0.0077131 | -0.0077383 | 0.040262 | 0.0026685 | 0.037675 | 0.005985 | 0.005325 | 0.20321 | -0.059167 | 0.45331 | 0.15673 | 0.042256 | 0.014095 | -0.019721 | 0.16234 | 0.28842 | -0.17539 | -0.27404 | 120.3517 | -0.025668 | 120.2327 | 120.2003 | -0.15141 | -0.28805 | 0.22443 | 119.921 | -0.06654 | 120.2373 | 120.1753 | 0.25432 | 0.059541 | -0.40427 | 120.3982 | 120.1358 | 120.6483 | 120.201 | -0.072151 | 120.3573 | 120.4834 | 120.0196 | 120.2091 | -0.50292
1743.7656 | 120.5795 | -120.2087 | 0.21515 | 1.4211e-13 | -0.0078674 | -0.0024209 | 0.029792 | -0.013909 | 0.010952 | -0.0019839 | 0.007488 | 0.0077131 | -0.0077383 | 0.040262 | 0.0028821 | 0.042253 | 0.005985 | 0.005325 | 0.19864 | -0.036272 | 0.44873 | 0.16131 | 0.046835 | 0.009516 | -0.019721 | 0.16692 | 0.293 | -0.16624 | -0.2832 | 120.3701 | -0.016513 | 120.251 | 120.2141 | -0.15599 | -0.25142 | 0.23358 | 119.9255 | -0.048228 | 120.2556 | 120.189 | 0.26348 | 0.077852 | -0.38138 | 120.4074 | 120.1725 | 120.6575 | 120.2147 | -0.053839 | 120.3757 | 120.5017 | 120.0425 | 120.2183 | -0.49835
1745.5312 | 120.6162 | -120.2454 | 0.22888 | 1.4211e-13 | -0.0076538 | -0.0024209 | 0.029792 | -0.013696 | 0.010739 | 0.0056466 | 0.0077016 | 0.0074993 | -0.0075247 | 0.040262 | 0.0026685 | 0.033096 | -0.003172 | 0.005325 | 0.20779 | -0.054588 | 0.44873 | 0.15673 | 0.051413 | 0.009516 | -0.019721 | 0.15318 | 0.28384 | -0.17997 | -0.27862 | 120.4021 | -0.021089 | 120.2785 | 120.2507 | -0.15141 | -0.28347 | 0.21985 | 119.9667 | -0.075697 | 120.2968 | 120.2256 | 0.2589 | 0.054962 | -0.40885 | 120.4532 | 120.1908 | 120.6941 | 120.2422 | -0.072151 | 120.3985 | 120.5292 | 120.0654 | 120.2549 | -0.5075
1747.2031 | 120.5887 | -120.3278 | 0.24261 | 1.4211e-13 | -0.0078674 | -0.0022073 | 0.030005 | -0.013696 | 0.010739 | -0.0019839 | 0.0079152 | 0.0074993 | -0.0075247 | 0.040049 | 0.0026685 | 0.042253 | 0.010564 | 0.009904 | 0.20321 | -0.036272 | 0.44873 | 0.15673 | 0.051413 | 0.009516 | -0.0243 | 0.15776 | 0.29758 | -0.17081 | -0.2832 | 120.4845 | -0.039401 | 120.37 | 120.3377 | -0.14683 | -0.27889 | 0.20612 | 120.0446 | -0.084851 | 120.3792 | 120.3035 | 0.2589 | 0.054965 | -0.41343 | 120.531 | 120.2915 | 120.7765 | 120.3383 | -0.085884 | 120.4855 | 120.6253 | 120.1569 | 120.3373 | -0.52581
1748.9531 | 120.7031 | -120.3003 | 0.22888 | 1.4211e-13 | -0.00744 | -0.0024209 | 0.030433 | -0.013909 | 0.010739 | 0.0056466 | 0.007488 | 0.0079267 | -0.0075247 | 0.040476 | 0.0033095 | 0.023939 | 0.001407 | 0.005325 | 0.20321 | -0.013378 | 0.44873 | 0.15673 | 0.042256 | 0.000359 | -0.0243 | 0.16234 | 0.293 | -0.17081 | -0.2832 | 120.457 | -0.025668 | 120.3242 | 120.3056 | -0.15141 | -0.24226 | 0.21985 | 120.0171 | -0.06654 | 120.3425 | 120.276 | 0.2589 | 0.064119 | -0.3997 | 120.5035 | 120.2869 | 120.749 | 120.3017 | -0.072151 | 120.4626 | 120.5933 | 120.1295 | 120.3007 | -0.51208
1750.6875 | 120.6802 | -120.3415 | 0.25635 | 1.4211e-13 | -0.0076538 | -0.0024209 | 0.030219 | -0.013696 | 0.010311 | 0.0056466 | 0.007488 | 0.0079267 | -0.0079521 | 0.040476 | 0.0030959 | 0.037675 | 0.005985 | 0.000747 | 0.20321 | -0.059167 | 0.44873 | 0.15673 | 0.046835 | 0.014095 | -0.019721 | 0.15776 | 0.293 | -0.17997 | -0.27862 | 120.4982 | -0.053134 | 120.3792 | 120.3422 | -0.15598 | -0.31551 | 0.19238 | 120.0629 | -0.098584 | 120.3883 | 120.3218 | 0.2589 | 0.036653 | -0.43632 | 120.5447 | 120.2823 | 120.7902 | 120.3475 | -0.099617 | 120.4993 | 120.6345 | 120.1615 | 120.3556 | -0.53497
1752.4375 | 120.6482 | -120.401 | 0.27466 | 1.4211e-13 | -0.0078674 | -0.0026347 | 0.030219 | -0.014123 | 0.010311 | 0.013277 | 0.0072744 | 0.0077131 | -0.0077383 | 0.040476 | 0.0028821 | 0.037675 | 0.005985 | 0.009904 | 0.20321 | -0.022536 | 0.45331 | 0.16589 | 0.051413 | 0.014095 | -0.005985 | 0.15318 | 0.293 | -0.17081 | -0.2832 | 120.5669 | -0.071444 | 120.4387 | 120.4109 | -0.15599 | -0.29719 | 0.17865 | 120.1178 | -0.12147 | 120.4524 | 120.395 | 0.27721 | 0.018343 | -0.44547 | 120.6042 | 120.3785 | 120.8543 | 120.407 | -0.10877 | 120.5542 | 120.694 | 120.2302 | 120.4151 | -0.55786
1754.1875 | 120.7809 | -120.3552 | 0.2655 | 1.4211e-13 | -0.0076538 | -0.0024209 | 0.030005 | -0.013696 | 0.010952 | 0.0056466 | 0.0079152 | 0.0074993 | -0.0077383 | 0.040049 | 0.0024549 | 0.042253 | 0.005985 | 0.000747 | 0.20321 | -0.063746 | 0.44415 | 0.15673 | 0.042256 | -0.00422 | -0.015143 | 0.15318 | 0.29758 | -0.16624 | -0.2832 | 120.512 | -0.062289 | 120.3975 | 120.356 | -0.15598 | -0.32925 | 0.17865 | 120.072 | -0.11232 | 120.3975 | 120.3401 | 0.26805 | 0.032077 | -0.43174 | 120.5584 | 120.2915 | 120.7994 | 120.3612 | -0.10877 | 120.5084 | 120.6528 | 120.189 | 120.351 | -0.5487
1755.9375 | 120.7489 | -120.4239 | 0.29297 | 1.4211e-13 | -0.008081 | -0.0022073 | 0.029792 | -0.014123 | 0.010739 | 0.0056466 | 0.0072744 | 0.0079267 | -0.0077383 | 0.040262 | 0.0030959 | 0.042253 | 0.005985 | 0.005325 | 0.20321 | -0.031693 | 0.45331 | 0.15215 | 0.046835 | 0.014095 | -0.005985 | 0.15776 | 0.29758 | -0.17539 | -0.2832 | 120.576 | -0.089755 | 120.4661 | 120.4292 | -0.14683 | -0.32466 | 0.16034 | 120.1407 | -0.1352 | 120.4707 | 120.4179 | 0.27721 | 0.004611 | -0.46836 | 120.6271 | 120.3922 | 120.8772 | 120.4299 | -0.14082 | 120.5817 | 120.7215 | 120.2485 | 120.438 | -0.57617
1757.625 | 120.8084 | -120.4239 | 0.27924 | 1.4211e-13 | -0.008081 | -0.0024209 | 0.030005 | -0.014123 | 0.010952 | 0.0056466 | 0.007488 | 0.0074993 | -0.0079521 | 0.040476 | 0.0028821 | 0.028518 | 0.001407 | 0.009904 | 0.20321 | -0.022536 | 0.43957 | 0.16131 | 0.051413 | 0.009516 | -0.015143 | 0.15776 | 0.28842 | -0.17081 | -0.2832 | 120.5852 | -0.076022 | 120.4524 | 120.4338 | -0.15141 | -0.30177 | 0.16034 | 120.1407 | -0.12147 | 120.4753 | 120.4087 | 0.26805 | 0.009187 | -0.45005 | 120.6271 | 120.4014 | 120.8635 | 120.4253 | -0.11793 | 120.5817 | 120.7123 | 120.2531 | 120.4334 | -0.56243
1759.3906 | 120.8588 | -120.4514 | 0.28381 | 1.4211e-13 | -0.008081 | -0.0024209 | 0.030219 | -0.013909 | 0.010525 | 0.0056466 | 0.007488 | 0.0077131 | -0.0073111 | 0.040476 | 0.0024549 | 0.033096 | 0.001407 | 0.005325 | 0.20321 | -0.040851 | 0.44873 | 0.16131 | 0.042256 | 0.009516 | -0.010564 | 0.16234 | 0.293 | -0.17539 | -0.2832 | 120.6127 | -0.080599 | 120.4845 | 120.4567 | -0.15599 | -0.32466 | 0.16492 | 120.1682 | -0.12147 | 120.4936 | 120.4408 | 0.27263 | 0.009188 | -0.45921 | 120.6546 | 120.4105 | 120.9001 | 120.4528 | -0.1225 | 120.6137 | 120.7444 | 120.276 | 120.4609 | -0.56701
1761.0781 | 120.7993 | -120.4926 | 0.29297 | 1.4211e-13 | -0.00744 | -0.0024209 | 0.030219 | -0.013909 | 0.010739 | -0.0096144 | 0.0077016 | 0.0077131 | -0.0075247 | 0.040262 | 0.0028821 | 0.037675 | 0.010564 | 0.009904 | 0.20321 | -0.063746 | 0.44873 | 0.15673 | 0.046835 | 0.009516 | -0.015143 | 0.16234 | 0.29758 | -0.17081 | -0.27862 | 120.6493 | -0.089755 | 120.5302 | 120.5025 | -0.14683 | -0.35672 | 0.15576 | 120.2139 | -0.13063 | 120.5394 | 120.4774 | 0.26348 | 0.004611 | -0.46378 | 120.6958 | 120.4288 | 120.9413 | 120.5031 | -0.13624 | 120.6549 | 120.7901 | 120.3217 | 120.5021 | -0.57159
1762.8281 | 120.813 | -120.5246 | 0.31586 | 1.4211e-13 | -0.0078674 | -0.0026347 | 0.030005 | -0.013909 | 0.010525 | -0.0019839 | 0.0077016 | 0.0074993 | -0.0075247 | 0.04069 | 0.0026685 | 0.028518 | -0.003172 | 0.000747 | 0.20779 | -0.036272 | 0.45331 | 0.15673 | 0.060571 | 0.009516 | -0.019721 | 0.15776 | 0.293 | -0.17539 | -0.27862 | 120.6813 | -0.10806 | 120.5531 | 120.5253 | -0.15598 | -0.35213 | 0.13745 | 120.246 | -0.15809 | 120.5852 | 120.5049 | 0.2589 | -0.022856 | -0.49125 | 120.7324 | 120.4883 | 120.9779 | 120.5214 | -0.15913 | 120.6824 | 120.8176 | 120.3492 | 120.5341 | -0.59448
1764.5781 | 120.932 | -120.5154 | 0.28381 | 1.4211e-13 | -0.008081 | -0.0026347 | 0.030219 | -0.013909 | 0.010311 | 0.0056466 | 0.0077016 | 0.0077131 | -0.0075247 | 0.040476 | 0.0022413 | 0.033096 | 0.005985 | 0.005325 | 0.20321 | -0.04543 | 0.44415 | 0.15215 | 0.046835 | 0.004938 | -0.015143 | 0.16692 | 0.29758 | -0.17539 | -0.27862 | 120.6676 | -0.080599 | 120.5485 | 120.5208 | -0.14683 | -0.32924 | 0.16034 | 120.2368 | -0.11689 | 120.5623 | 120.5003 | 0.26348 | 0.013767 | -0.45921 | 120.7187 | 120.47 | 120.9596 | 120.5214 | -0.13166 | 120.6824 | 120.813 | 120.34 | 120.5204 | -0.56243
1766.3281 | 120.9778 | -120.5383 | 0.30212 | 1.4211e-13 | -0.008081 | -0.0026347 | 0.030219 | -0.014123 | 0.010311 | -0.0096144 | 0.0077016 | 0.0077131 | -0.0081657 | 0.040903 | 0.0028821 | 0.042253 | 0.005985 | 0.000747 | 0.20321 | -0.040851 | 0.43957 | 0.15215 | 0.051413 | 0.009516 | -0.015143 | 0.15318 | 0.293 | -0.17539 | -0.2832 | 120.6905 | -0.09891 | 120.5806 | 120.5391 | -0.15141 | -0.34298 | 0.13745 | 120.2551 | -0.14894 | 120.5897 | 120.5232 | 0.26805 | -0.009123 | -0.47752 | 120.7415 | 120.4975 | 120.9779 | 120.5443 | -0.14997 | 120.6915 | 120.8313 | 120.3629 | 120.5478 | -0.58532
1768.0781 | 120.9869 | -120.5612 | 0.28839 | 1.4211e-13 | -0.0078674 | -0.0024209 | 0.029792 | -0.013909 | 0.010952 | -0.0096144 | 0.0077016 | 0.0077131 | -0.0075247 | 0.040476 | 0.0028821 | 0.028518 | 0.001407 | 0.014482 | 0.20321 | -0.022536 | 0.44415 | 0.15673 | 0.046835 | 0.009516 | -0.019721 | 0.15318 | 0.293 | -0.17539 | -0.27862 | 120.7179 | -0.085177 | 120.5897 | 120.5757 | -0.14225 | -0.31093 | 0.15576 | 120.2826 | -0.13521 | 120.6081 | 120.5415 | 0.2589 | 0.00461 | -0.46378 | 120.7644 | 120.5387 | 121.0054 | 120.5626 | -0.13166 | 120.7144 | 120.8542 | 120.3858 | 120.5707 | -0.56701
1769.7656 | 120.9595 | -120.6207 | 0.31128 | 1.4211e-13 | -0.0076538 | -0.0024209 | 0.030005 | -0.013696 | 0.010525 | 0.0056466 | 0.0077016 | 0.0074993 | -0.0075247 | 0.040476 | 0.0028821 | 0.037675 | 0.005985 | 0.005325 | 0.20321 | -0.063746 | 0.44415 | 0.14757 | 0.046835 | 0.009516 | -0.015143 | 0.15776 | 0.29758 | -0.17081 | -0.28778 | 120.7683 | -0.10806 | 120.6584 | 120.6261 | -0.14225 | -0.37502 | 0.13288 | 120.333 | -0.15351 | 120.6676 | 120.6056 | 0.27263 | -0.013699 | -0.48209 | 120.8239 | 120.557 | 121.0649 | 120.6267 | -0.16371 | 120.7785 | 120.9183 | 120.4499 | 120.6302 | -0.59906
1771.5312 | 121.0052 | -120.6024 | 0.3067 | 1.4211e-13 | -0.00744 | -0.0024209 | 0.030005 | -0.014123 | 0.010525 | 0.0056466 | 0.0072744 | 0.0077131 | -0.0079521 | 0.040476 | 0.0026685 | 0.033096 | 0.001407 | 0.005325 | 0.19406 | -0.022536 | 0.43957 | 0.15673 | 0.055992 | 0.004938 | -0.015143 | 0.15318 | 0.293 | -0.16624 | -0.27862 | 120.7591 | -0.11264 | 120.6355 | 120.6077 | -0.15141 | -0.32924 | 0.13287 | 120.3238 | -0.15352 | 120.6584 | 120.5873 | 0.26348 | -0.013701 | -0.47294 | 120.7965 | 120.5799 | 121.042 | 120.6038 | -0.14997 | 120.7556 | 120.8954 | 120.4362 | 120.6074 | -0.58532
1773.2812 | 120.9961 | -120.6528 | 0.32959 | 1.4211e-13 | -0.0076538 | -0.0024209 | 0.030005 | -0.014123 | 0.010952 | 0.0056466 | 0.007488 | 0.0074993 | -0.0073111 | 0.04069 | 0.0028821 | 0.033096 | -0.003172 | 0.005325 | 0.20779 | -0.04543 | 0.44415 | 0.15673 | 0.042256 | 0.009516 | -0.010564 | 0.16234 | 0.30216 | -0.16624 | -0.2832 | 120.8095 | -0.1218 | 120.6859 | 120.6581 | -0.15141 | -0.37502 | 0.11456 | 120.3696 | -0.16725 | 120.695 | 120.6422 | 0.27263 | -0.027432 | -0.49583 | 120.8606 | 120.6073 | 121.0969 | 120.6496 | -0.17286 | 120.8151 | 120.9549 | 120.4865 | 120.6623 | -0.61279
1774.9688 | 120.9915 | -120.6848 | 0.33875 | 1.4211e-13 | -0.0076538 | -0.0024209 | 0.030005 | -0.013909 | 0.010739 | 0.0056466 | 0.007488 | 0.0079267 | -0.0077383 | 0.04069 | 0.0026685 | 0.042253 | 0.010564 | 0.009904 | 0.20321 | -0.031693 | 0.44415 | 0.15215 | 0.042256 | 0.000359 | -0.015143 | 0.16234 | 0.29758 | -0.17539 | -0.27404 | 120.837 | -0.13553 | 120.7271 | 120.6947 | -0.14225 | -0.37044 | 0.10541 | 120.4108 | -0.1764 | 120.7271 | 120.6697 | 0.2589 | -0.041165 | -0.51414 | 120.888 | 120.6531 | 121.129 | 120.6954 | -0.18659 | 120.8472 | 120.9824 | 120.5094 | 120.6852 | -0.61279
1776.7031 | 121.0236 | -120.6757 | 0.32044 | 1.4211e-13 | -0.0078674 | -0.0024209 | 0.030005 | -0.013696 | 0.010739 | -0.0019839 | 0.0072744 | 0.0079267 | -0.0075247 | 0.040262 | 0.0028821 | 0.033096 | -0.003172 | 0.009904 | 0.19864 | -0.059167 | 0.44415 | 0.15673 | 0.042256 | 0.004938 | -0.019721 | 0.16234 | 0.28384 | -0.16624 | -0.2832 | 120.8324 | -0.1218 | 120.7088 | 120.6856 | -0.14683 | -0.3796 | 0.12372 | 120.3925 | -0.15809 | 120.7179 | 120.6559 | 0.26348 | -0.036591 | -0.48667 | 120.8743 | 120.6165 | 121.1198 | 120.6725 | -0.1637 | 120.838 | 120.9595 | 120.5094 | 120.6806 | -0.60363
1778.4531 | 121.0922 | -120.694 | 0.31128 | 1.4211e-13 | -0.00744 | -0.0028483 | 0.030219 | -0.014123 | 0.010739 | -0.0019839 | 0.0077016 | 0.0072857 | -0.0075247 | 0.040476 | 0.0026685 | 0.033096 | 0.001407 | 0.009904 | 0.19864 | -0.04543 | 0.44415 | 0.15673 | 0.051413 | 0.004938 | -0.015143 | 0.15318 | 0.29758 | -0.16166 | -0.2832 | 120.8507 | -0.11264 | 120.7271 | 120.7039 | -0.14683 | -0.35671 | 0.13288 | 120.4108 | -0.15809 | 120.7454 | 120.6788 | 0.26805 | -0.013699 | -0.47294 | 120.8926 | 120.6485 | 121.1381 | 120.6954 | -0.15455 | 120.8472 | 120.9915 | 120.5323 | 120.6989 | -0.59448
1780.2188 | 121.1243 | -120.7031 | 0.3067 | 1.4211e-13 | -0.008081 | -0.0026347 | 0.030219 | -0.013909 | 0.010525 | 0.013277 | 0.007488 | 0.0074993 | -0.0077383 | 0.04069 | 0.0024549 | 0.033096 | -0.007751 | 0.000747 | 0.20321 | 0.018675 | 0.44873 | 0.15673 | 0.046835 | 0.009516 | -0.019721 | 0.16234 | 0.29758 | -0.17081 | -0.27862 | 120.8599 | -0.10349 | 120.7362 | 120.7039 | -0.15598 | -0.28803 | 0.14203 | 120.4245 | -0.14436 | 120.75 | 120.6834 | 0.2589 | -0.009122 | -0.47752 | 120.9063 | 120.7218 | 121.1519 | 120.6954 | -0.14997 | 120.8655 | 121.0007 | 120.5323 | 120.7126 | -0.58532
1781.9688 | 121.0373 | -120.7718 | 0.33417 | 1.4211e-13 | -0.0078674 | -0.0024209 | 0.029792 | -0.013696 | 0.010525 | -0.0019839 | 0.0077016 | 0.0077131 | -0.0077383 | 0.04069 | 0.0030959 | 0.046831 | 0.001407 | 0.009904 | 0.19864 | -0.022536 | 0.44873 | 0.15215 | 0.046835 | 0.009516 | -0.015143 | 0.16234 | 0.29758 | -0.17081 | -0.27404 | 120.9239 | -0.13553 | 120.8186 | 120.7817 | -0.14225 | -0.3567 | 0.11457 | 120.4977 | -0.17183 | 120.8186 | 120.7566 | 0.2589 | -0.036587 | -0.50498 | 120.9704 | 120.7493 | 121.2205 | 120.7732 | -0.18201 | 120.9341 | 121.0694 | 120.601 | 120.7813 | -0.60821
1783.6562 | 121.2021 | -120.7443 | 0.3067 | 1.4211e-13 | -0.0076538 | -0.0026347 | 0.030219 | -0.013909 | 0.010098 | 0.0056466 | 0.0077016 | 0.0074993 | -0.0073111 | 0.04069 | 0.0026685 | 0.033096 | 0.005985 | 0.005325 | 0.20779 | -0.017957 | 0.44415 | 0.15215 | 0.046835 | 0.004938 | -0.019721 | 0.15776 | 0.293 | -0.16624 | -0.29236 | 120.8965 | -0.098909 | 120.7774 | 120.7496 | -0.14683 | -0.32466 | 0.13745 | 120.452 | -0.14894 | 120.7912 | 120.7246 | 0.27264 | -0.013701 | -0.47294 | 120.9521 | 120.7264 | 121.1885 | 120.7503 | -0.15455 | 120.9021 | 121.0373 | 120.5781 | 120.7493 | -0.59906
1785.4062 | 121.2341 | -120.7672 | 0.31128 | 1.4211e-13 | -0.008081 | -0.0028483 | 0.030005 | -0.013909 | 0.010311 | -0.0019839 | 0.007488 | 0.0077131 | -0.0075247 | 0.040476 | 0.0026685 | 0.037675 | 0.001407 | 0.009904 | 0.20779 | 0.018675 | 0.45331 | 0.16131 | 0.051413 | 0.009516 | -0.015143 | 0.15318 | 0.29758 | -0.17539 | -0.27404 | 120.9285 | -0.10349 | 120.8049 | 120.7771 | -0.15141 | -0.2926 | 0.14203 | 120.4932 | -0.15809 | 120.8186 | 120.7521 | 0.2589 | -0.013699 | -0.48667 | 120.975 | 120.7859 | 121.2205 | 120.7686 | -0.14997 | 120.9204 | 121.0648 | 120.5918 | 120.7767 | -0.58532
1787.0938 | 121.1151 | -120.7947 | 0.3479 | 1.4211e-13 | -0.0078674 | -0.0026347 | 0.029792 | -0.013696 | 0.010739 | -0.0019839 | 0.0079152 | 0.0077131 | -0.0075247 | 0.040903 | 0.0030959 | 0.028518 | 0.001407 | 0.000747 | 0.20779 | -0.013378 | 0.44873 | 0.15673 | 0.046835 | 0.000359 | -0.015143 | 0.15776 | 0.28842 | -0.16624 | -0.2832 | 120.9514 | -0.14011 | 120.8232 | 120.7954 | -0.15598 | -0.36128 | 0.10083 | 120.5115 | -0.19014 | 120.8415 | 120.7795 | 0.26805 | -0.059477 | -0.51414 | 121.0025 | 120.7813 | 121.2434 | 120.7961 | -0.19117 | 120.9524 | 121.0831 | 120.6284 | 120.795 | -0.6311
1788.8438 | 121.2021 | -120.813 | 0.32501 | 1.4211e-13 | -0.0076538 | -0.0026347 | 0.030005 | -0.013909 | 0.010525 | -0.0096144 | 0.0077016 | 0.0077131 | -0.0077383 | 0.04069 | 0.0024549 | 0.037675 | 0.001407 | 0.009904 | 0.19864 | -0.040851 | 0.44873 | 0.15673 | 0.046835 | 0.004938 | -0.019721 | 0.15776 | 0.30216 | -0.17081 | -0.27404 | 120.9697 | -0.12638 | 120.8507 | 120.8229 | -0.14683 | -0.36586 | 0.12372 | 120.5389 | -0.16725 | 120.8598 | 120.7933 | 0.25432 | -0.022854 | -0.49583 | 121.0116 | 120.7721 | 121.2617 | 120.8144 | -0.16828 | 120.9708 | 121.1151 | 120.6422 | 120.8179 | -0.59905
1790.5938 | 121.1334 | -120.8313 | 0.35248 | 1.4211e-13 | -0.0078674 | -0.0026347 | 0.030219 | -0.013909 | 0.010525 | 0.0056466 | 0.0079152 | 0.0081403 | -0.0075247 | 0.040903 | 0.0028821 | 0.042253 | 0.001407 | 0.005325 | 0.20321 | -0.017957 | 0.44873 | 0.15673 | 0.051413 | 0.004938 | -0.019721 | 0.15776 | 0.29758 | -0.17081 | -0.28778 | 120.988 | -0.14926 | 120.8736 | 120.8366 | -0.15141 | -0.37044 | 0.096254 | 120.5435 | -0.19471 | 120.8827 | 120.8116 | 0.26806 | -0.054898 | -0.52329 | 121.0345 | 120.8133 | 121.28 | 120.8327 | -0.19575 | 120.9891 | 121.1289 | 120.6605 | 120.8362 | -0.64026
1792.2812 | 121.2891 | -120.8359 | 0.32959 | 1.4211e-13 | -0.0076538 | -0.0024209 | 0.030005 | -0.014123 | 0.010739 | -0.0019839 | 0.0077016 | 0.0079267 | -0.0075247 | 0.040903 | 0.0028821 | 0.033096 | 0.005985 | 0.009904 | 0.20779 | -0.013378 | 0.43957 | 0.15673 | 0.046835 | 0.014095 | -0.015143 | 0.16234 | 0.29758 | -0.17081 | -0.2832 | 120.9926 | -0.1218 | 120.869 | 120.8458 | -0.14683 | -0.34297 | 0.10998 | 120.5527 | -0.16725 | 120.8827 | 120.8207 | 0.26805 | -0.03201 | -0.5004 | 121.0437 | 120.8225 | 121.2755 | 120.8419 | -0.17286 | 120.9982 | 121.1335 | 120.6651 | 120.85 | -0.61279
1794.0469 | 121.2799 | -120.8313 | 0.33875 | 1.4211e-13 | -0.0078674 | -0.0026347 | 0.030005 | -0.013909 | 0.010739 | 0.013277 | 0.0077016 | 0.0081403 | -0.0075247 | 0.04069 | 0.0026685 | 0.037675 | 0.005985 | 0.009904 | 0.20779 | 0.014096 | 0.44873 | 0.15215 | 0.046835 | 0.009516 | -0.015143 | 0.16234 | 0.293 | -0.17081 | -0.27862 | 120.9835 | -0.13095 | 120.869 | 120.8412 | -0.14225 | -0.32465 | 0.10999 | 120.5527 | -0.1764 | 120.8781 | 120.8162 | 0.26348 | -0.045744 | -0.50956 | 121.0391 | 120.8454 | 121.28 | 120.8373 | -0.18659 | 120.9936 | 121.1243 | 120.6605 | 120.8408 | -0.61736
1795.8125 | 121.2158 | -120.8954 | 0.37079 | 1.4211e-13 | -0.0082948 | -0.0028483 | 0.030219 | -0.014337 | 0.010525 | 0.0056466 | 0.007488 | 0.0077131 | -0.0077383 | 0.040903 | 0.0026685 | 0.037675 | 0.010564 | 0.005325 | 0.20779 | 0.046148 | 0.44415 | 0.15215 | 0.046835 | 0.004938 | -0.010564 | 0.15776 | 0.28842 | -0.17081 | -0.27862 | 121.0475 | -0.163 | 120.9331 | 120.9007 | -0.14683 | -0.32464 | 0.073365 | 120.6168 | -0.21302 | 120.9422 | 120.8848 | 0.26805 | -0.082366 | -0.5416 | 121.1032 | 120.9415 | 121.3395 | 120.906 | -0.21864 | 121.0532 | 121.1838 | 120.7246 | 120.9003 | -0.64941
1797.5625 | 121.2845 | -120.8633 | 0.33875 | 1.4211e-13 | -0.0078674 | -0.0026347 | 0.030433 | -0.013909 | 0.010525 | 0.0056466 | 0.007488 | 0.0079267 | -0.0073111 | 0.040476 | 0.0030959 | 0.033096 | 0.001407 | 0.000747 | 0.20321 | -0.013378 | 0.44415 | 0.15215 | 0.042256 | 0.000359 | -0.019721 | 0.15318 | 0.293 | -0.17081 | -0.28778 | 121.0155 | -0.13553 | 120.8964 | 120.8641 | -0.15141 | -0.35212 | 0.10541 | 120.5756 | -0.18556 | 120.9056 | 120.8436 | 0.26806 | -0.045744 | -0.50956 | 121.0666 | 120.85 | 121.3075 | 120.8647 | -0.18659 | 121.0165 | 121.1563 | 120.6925 | 120.8637 | -0.62652
1799.2656 | 121.3257 | -120.8679 | 0.37079 | 1.4211e-13 | -0.008081 | -0.0024209 | 0.030005 | -0.014337 | 0.010311 | 0.0056466 | 0.0077016 | 0.0077131 | -0.0077383 | 0.04069 | 0.0028821 | 0.042253 | 0.010564 | 0.005325 | 0.20779 | -0.008799 | 0.44415 | 0.15215 | 0.037677 | 0.000359 | -0.015143 | 0.16234 | 0.293 | -0.17539 | -0.29236 | 121.0201 | -0.163 | 120.9102 | 120.8732 | -0.14683 | -0.37959 | 0.073365 | 120.5756 | -0.20845 | 120.9056 | 120.8528 | 0.27721 | -0.077788 | -0.54618 | 121.0757 | 120.8591 | 121.3121 | 120.8785 | -0.21864 | 121.0303 | 121.1609 | 120.6925 | 120.8683 | -0.66314
1801.0312 | 121.376 | -120.8633 | 0.32044 | 1.4211e-13 | -0.0076538 | -0.0026347 | 0.030219 | -0.01455 | 0.010952 | 0.013277 | 0.007488 | 0.0074993 | -0.0077383 | 0.04069 | 0.0026685 | 0.033096 | 0.010564 | 0.014482 | 0.20321 | -0.036272 | 0.43957 | 0.16131 | 0.046835 | 0.014095 | -0.019721 | 0.14861 | 0.29758 | -0.16624 | -0.28778 | 121.0247 | -0.11722 | 120.8964 | 120.8778 | -0.14683 | -0.35671 | 0.11914 | 120.5756 | -0.17183 | 120.9102 | 120.8436 | 0.26806 | -0.022855 | -0.48667 | 121.0666 | 120.8271 | 121.3029 | 120.8739 | -0.15913 | 121.0119 | 121.1609 | 120.6971 | 120.8774 | -0.60821
1802.7656 | 121.376 | -120.8817 | 0.32959 | 1.4211e-13 | -0.0078674 | -0.0026347 | 0.030219 | -0.014123 | 0.010311 | -0.0096144 | 0.0070608 | 0.0074993 | -0.0077383 | 0.04069 | 0.0028821 | 0.028518 | 0.005985 | 0.009904 | 0.20321 | 0.03699 | 0.43957 | 0.15673 | 0.046835 | 0.014095 | -0.015143 | 0.15776 | 0.29758 | -0.17539 | -0.27404 | 121.0384 | -0.12638 | 120.9102 | 120.8916 | -0.14683 | -0.2926 | 0.10998 | 120.6076 | -0.17183 | 120.9285 | 120.8665 | 0.2589 | -0.03201 | -0.50498 | 121.0849 | 120.9186 | 121.3212 | 120.8876 | -0.17286 | 121.0394 | 121.1792 | 120.7063 | 120.8957 | -0.60363
1804.4531 | 121.3211 | -120.9366 | 0.36621 | 1.4211e-13 | -0.008081 | -0.0024209 | 0.029792 | -0.014337 | 0.010952 | 0.013277 | 0.0072744 | 0.0077131 | -0.0075247 | 0.040903 | 0.0026685 | 0.037675 | 0.005985 | 0.005325 | 0.19864 | -0.031693 | 0.44873 | 0.15673 | 0.037677 | 0.009516 | -0.010564 | 0.15318 | 0.28842 | -0.17081 | -0.27862 | 121.0933 | -0.16758 | 120.9743 | 120.9419 | -0.15141 | -0.3979 | 0.082521 | 120.658 | -0.21303 | 120.9743 | 120.926 | 0.26805 | -0.077788 | -0.53703 | 121.1352 | 120.9049 | 121.3853 | 120.9426 | -0.20948 | 121.0898 | 121.225 | 120.7658 | 120.9461 | -0.64483
1806.2031 | 121.3303 | -120.932 | 0.36163 | 1.4211e-13 | -0.0078674 | -0.0028483 | 0.030005 | -0.014123 | 0.010952 | 0.013277 | 0.0077016 | 0.0079267 | -0.0077383 | 0.040903 | 0.0028821 | 0.028518 | 0.005985 | 0.005325 | 0.20779 | 0.000359 | 0.44873 | 0.15215 | 0.042256 | 0.004938 | -0.019721 | 0.15776 | 0.293 | -0.17081 | -0.28778 | 121.0842 | -0.15384 | 120.9605 | 120.9373 | -0.14683 | -0.36127 | 0.087099 | 120.6442 | -0.20387 | 120.9743 | 120.9123 | 0.26806 | -0.068632 | -0.53245 | 121.1398 | 120.9324 | 121.3807 | 120.938 | -0.20948 | 121.0898 | 121.225 | 120.7612 | 120.9369 | -0.64941
1807.9688 | 121.431 | -120.9503 | 0.35706 | 1.4211e-13 | -0.0082948 | -0.0026347 | 0.029792 | -0.014123 | 0.010525 | 0.0056466 | 0.0072744 | 0.0077131 | -0.0079521 | 0.040903 | 0.0028821 | 0.037675 | 0.015142 | 0.005325 | 0.20321 | 0.000359 | 0.44873 | 0.14757 | 0.051413 | 0.009516 | -0.010564 | 0.16234 | 0.293 | -0.17539 | -0.28778 | 121.0979 | -0.15384 | 120.988 | 120.9556 | -0.14225 | -0.3567 | 0.091676 | 120.6625 | -0.19471 | 121.0017 | 120.9398 | 0.27721 | -0.064055 | -0.53245 | 121.1535 | 120.9507 | 121.399 | 120.9655 | -0.20948 | 121.1127 | 121.2433 | 120.7749 | 120.9598 | -0.64483
1809.7188 | 121.4035 | -120.9595 | 0.35706 | 1.4211e-13 | -0.0078674 | -0.0026347 | 0.030005 | -0.013909 | 0.010952 | 0.013277 | 0.007488 | 0.0079267 | -0.0077383 | 0.04069 | 0.0028821 | 0.042253 | 0.001407 | 0.014482 | 0.20321 | 0.000359 | 0.44415 | 0.14757 | 0.046835 | 0.009516 | -0.015143 | 0.15318 | 0.293 | -0.16624 | -0.2832 | 121.107 | -0.15384 | 121.0017 | 120.974 | -0.13309 | -0.3567 | 0.087098 | 120.6763 | -0.20387 | 121.0063 | 120.9443 | 0.26805 | -0.064055 | -0.52329 | 121.1627 | 120.9598 | 121.4036 | 120.9609 | -0.20948 | 121.1127 | 121.2525 | 120.7932 | 120.969 | -0.64025
1811.4688 | 121.4539 | -120.9778 | 0.35706 | 1.4211e-13 | -0.0082948 | -0.0026347 | 0.029792 | -0.014337 | 0.010739 | -0.0019839 | 0.0072744 | 0.0077131 | -0.0073111 | 0.040903 | 0.0030959 | 0.037675 | 0.010564 | 0.005325 | 0.20321 | -0.050009 | 0.44415 | 0.15673 | 0.055992 | 0.014095 | -0.019721 | 0.16234 | 0.293 | -0.17081 | -0.27862 | 121.1345 | -0.15384 | 121.0155 | 120.9831 | -0.15141 | -0.40707 | 0.087098 | 120.6992 | -0.19471 | 121.0338 | 120.9581 | 0.2589 | -0.064055 | -0.52787 | 121.181 | 120.9278 | 121.4219 | 120.9883 | -0.20032 | 121.1401 | 121.2708 | 120.807 | 120.9919 | -0.63567
1813.1562 | 121.3715 | -121.0144 | 0.39825 | 1.4211e-13 | -0.0082948 | -0.0026347 | 0.030005 | -0.014123 | 0.010739 | 0.013277 | 0.0072744 | 0.0077131 | -0.0075247 | 0.040476 | 0.0024549 | 0.037675 | 0.005985 | 0.009904 | 0.20779 | 0.055306 | 0.44873 | 0.15215 | 0.042256 | 0.014095 | -0.019721 | 0.15776 | 0.30216 | -0.17081 | -0.27862 | 121.1666 | -0.19046 | 121.0521 | 121.0243 | -0.14225 | -0.34295 | 0.050478 | 120.7358 | -0.24049 | 121.0567 | 120.9947 | 0.2589 | -0.096096 | -0.56907 | 121.2222 | 121.0697 | 121.4631 | 121.0204 | -0.2461 | 121.1722 | 121.3166 | 120.8436 | 121.0285 | -0.67687
1814.9062 | 121.4813 | -121.019 | 0.32959 | 1.4211e-13 | -0.008081 | -0.0028483 | 0.029792 | -0.014123 | 0.010739 | 0.013277 | 0.007488 | 0.0079267 | -0.0075247 | 0.040903 | 0.0026685 | 0.042253 | 0.005985 | 0.009904 | 0.20321 | 0.027833 | 0.44873 | 0.15215 | 0.046835 | 0.004938 | -0.010564 | 0.15776 | 0.30674 | -0.17539 | -0.2832 | 121.1711 | -0.12638 | 121.0612 | 121.0289 | -0.14225 | -0.30176 | 0.11914 | 120.7358 | -0.17183 | 121.0658 | 121.0084 | 0.27263 | -0.022853 | -0.50498 | 121.2222 | 121.0468 | 121.4677 | 121.025 | -0.17744 | 121.1767 | 121.3257 | 120.8436 | 121.0239 | -0.61279
1816.6406 | 121.3898 | -121.051 | 0.37537 | 1.4211e-13 | -0.008081 | -0.0026347 | 0.029792 | -0.014123 | 0.010311 | 0.013277 | 0.0072744 | 0.0074993 | -0.0079521 | 0.04069 | 0.0028821 | 0.033096 | -0.003172 | 0.014482 | 0.20779 | 0.069043 | 0.44873 | 0.15673 | 0.051413 | 0.009516 | -0.019721 | 0.16234 | 0.29758 | -0.17081 | -0.2832 | 121.2078 | -0.16757 | 121.0841 | 121.0655 | -0.14225 | -0.30632 | 0.073366 | 120.7678 | -0.21302 | 121.1024 | 121.0313 | 0.26348 | -0.077786 | -0.54618 | 121.2588 | 121.1201 | 121.4998 | 121.0479 | -0.21863 | 121.2134 | 121.3486 | 120.8802 | 121.0605 | -0.65856
1818.3906 | 121.4722 | -121.0464 | 0.34332 | 1.4211e-13 | -0.0087222 | -0.0028483 | 0.030219 | -0.014123 | 0.010525 | 0.013277 | 0.0077016 | 0.0079267 | -0.0075247 | 0.04069 | 0.0028821 | 0.033096 | 0.005985 | 0.005325 | 0.19864 | -0.013378 | 0.43957 | 0.15215 | 0.042256 | 0.014095 | -0.015143 | 0.16234 | 0.29758 | -0.17539 | -0.27404 | 121.1986 | -0.14469 | 121.0795 | 121.0518 | -0.14683 | -0.3567 | 0.096252 | 120.7724 | -0.18098 | 121.0887 | 121.0313 | 0.2589 | -0.045743 | -0.51872 | 121.2451 | 121.0331 | 121.486 | 121.0524 | -0.19117 | 121.2088 | 121.344 | 120.8711 | 121.0605 | -0.61736
1820.1406 | 121.4264 | -121.0693 | 0.39368 | 1.4211e-13 | -0.008081 | -0.0024209 | 0.029792 | -0.014123 | 0.010739 | 0.0056466 | 0.007488 | 0.0077131 | -0.0075247 | 0.040903 | 0.0030959 | 0.033096 | 0.005985 | 0.005325 | 0.20321 | 0.059885 | 0.44415 | 0.14757 | 0.051413 | 0.014095 | -0.019721 | 0.16234 | 0.29758 | -0.17539 | -0.28778 | 121.2169 | -0.19046 | 121.1024 | 121.0747 | -0.14225 | -0.33379 | 0.050477 | 120.7816 | -0.23134 | 121.1207 | 121.0496 | 0.26806 | -0.096097 | -0.56907 | 121.2726 | 121.1292 | 121.5135 | 121.0753 | -0.2461 | 121.2317 | 121.3669 | 120.8939 | 121.0834 | -0.68145
1821.8906 | 121.5134 | -121.0419 | 0.37994 | 1.4211e-13 | -0.0085084 | -0.0024209 | 0.030005 | -0.014337 | 0.010525 | 0.0056466 | 0.0072744 | 0.0077131 | -0.0075247 | 0.041117 | 0.0028821 | 0.042253 | -0.003172 | 0.009904 | 0.20321 | -0.017957 | 0.44415 | 0.15215 | 0.042256 | 0.014095 | -0.015143 | 0.16234 | 0.29758 | -0.17539 | -0.27862 | 121.194 | -0.17673 | 121.0841 | 121.0518 | -0.14225 | -0.3979 | 0.06421 | 120.7633 | -0.2176 | 121.0841 | 121.0267 | 0.26348 | -0.082364 | -0.55534 | 121.2451 | 121.0239 | 121.486 | 121.0387 | -0.22779 | 121.2042 | 121.3394 | 120.8665 | 121.056 | -0.65856
1823.5625 | 121.4813 | -121.0693 | 0.38452 | 1.4211e-13 | -0.0085084 | -0.0024209 | 0.030005 | -0.014123 | 0.010525 | 0.0056466 | 0.0072744 | 0.0077131 | -0.0077383 | 0.04069 | 0.0028821 | 0.028518 | 0.005985 | 0.014482 | 0.19864 | 0.087359 | 0.45331 | 0.16131 | 0.037677 | 0.009516 | -0.010564 | 0.15776 | 0.30216 | -0.16624 | -0.2832 | 121.2306 | -0.18588 | 121.0979 | 121.0838 | -0.14683 | -0.29716 | 0.06879 | 120.7861 | -0.22676 | 121.107 | 121.0588 | 0.27263 | -0.082363 | -0.55076 | 121.268 | 121.1567 | 121.5226 | 121.0753 | -0.22321 | 121.2271 | 121.3715 | 120.9031 | 121.0789 | -0.66772
1825.3281 | 121.582 | -121.0373 | 0.3479 | 1.4211e-13 | -0.008081 | -0.0026347 | 0.030005 | -0.014123 | 0.010311 | 0.0056466 | 0.007488 | 0.0074993 | -0.0077383 | 0.041117 | 0.0030959 | 0.028518 | 0.001407 | 0.005325 | 0.20321 | 0.027833 | 0.44415 | 0.15673 | 0.046835 | 0.014095 | -0.019721 | 0.15318 | 0.30216 | -0.16624 | -0.2832 | 121.194 | -0.14469 | 121.0658 | 121.0426 | -0.15141 | -0.32007 | 0.096254 | 120.7541 | -0.19471 | 121.0841 | 121.0176 | 0.26348 | -0.045742 | -0.51414 | 121.2405 | 121.0651 | 121.4814 | 121.0387 | -0.19117 | 121.1905 | 121.3394 | 120.8711 | 121.0514 | -0.6311
1827.0781 | 121.5866 | -121.0968 | 0.36163 | 1.4211e-13 | -0.0085084 | -0.0026347 | 0.030219 | -0.014123 | 0.010952 | 0.013277 | 0.0072744 | 0.0077131 | -0.0081657 | 0.041117 | 0.0028821 | 0.042253 | 0.005985 | 0.005325 | 0.20779 | -0.040851 | 0.44415 | 0.15215 | 0.046835 | 0.004938 | -0.015143 | 0.15318 | 0.30216 | -0.17081 | -0.2832 | 121.249 | -0.15384 | 121.1391 | 121.1021 | -0.14683 | -0.40248 | 0.082521 | 120.8136 | -0.20845 | 121.1436 | 121.0817 | 0.26805 | -0.059475 | -0.53245 | 121.3046 | 121.056 | 121.541 | 121.1028 | -0.20948 | 121.25 | 121.399 | 120.926 | 121.1017 | -0.64483
1828.75 | 121.5271 | -121.1334 | 0.37994 | 1.4211e-13 | -0.0085084 | -0.0028483 | 0.030005 | -0.013696 | 0.010525 | -0.0019839 | 0.007488 | 0.0074993 | -0.0073111 | 0.041117 | 0.0030959 | 0.033096 | 0.005985 | 0.005325 | 0.19864 | -0.013378 | 0.44873 | 0.15673 | 0.051413 | 0.004938 | -0.015143 | 0.15776 | 0.29758 | -0.17539 | -0.2832 | 121.2902 | -0.18131 | 121.1665 | 121.1387 | -0.15141 | -0.39332 | 0.068788 | 120.8502 | -0.22218 | 121.1848 | 121.1183 | 0.26805 | -0.082364 | -0.55534 | 121.3321 | 121.12 | 121.5822 | 121.1394 | -0.22321 | 121.2912 | 121.431 | 120.958 | 121.1384 | -0.66314
1830.5156 | 121.6507 | -121.1197 | 0.33417 | 1.4211e-13 | -0.0085084 | -0.0024209 | 0.030219 | -0.014123 | 0.010739 | 0.0056466 | 0.007488 | 0.0074993 | -0.0075247 | 0.040903 | 0.0024549 | 0.037675 | 0.001407 | 0.005325 | 0.20779 | -0.031693 | 0.44873 | 0.15673 | 0.046835 | 0.009516 | -0.0243 | 0.15776 | 0.29758 | -0.17081 | -0.27862 | 121.2764 | -0.12637 | 121.1574 | 121.125 | -0.15141 | -0.36586 | 0.11457 | 120.8411 | -0.1764 | 121.1665 | 121.0954 | 0.25432 | -0.036587 | -0.50498 | 121.3275 | 121.088 | 121.5684 | 121.1211 | -0.17744 | 121.2775 | 121.4173 | 120.9489 | 121.1292 | -0.61279
1832.2031 | 121.4996 | -121.17 | 0.36163 | 1.4211e-13 | -0.0085084 | -0.0024209 | 0.030219 | -0.013909 | 0.010525 | 0.013277 | 0.007488 | 0.0079267 | -0.0077383 | 0.041117 | 0.0030959 | 0.033096 | -0.003172 | 0.009904 | 0.20321 | 0.032411 | 0.45331 | 0.15215 | 0.046835 | 0.004938 | -0.015143 | 0.16234 | 0.30216 | -0.16624 | -0.27862 | 121.3222 | -0.15842 | 121.2031 | 121.1799 | -0.14225 | -0.32922 | 0.091678 | 120.8914 | -0.19929 | 121.2169 | 121.1549 | 0.26348 | -0.059475 | -0.52787 | 121.3733 | 121.2025 | 121.6234 | 121.1669 | -0.20948 | 121.3324 | 121.4722 | 121.0038 | 121.175 | -0.64025
1833.9531 | 121.6278 | -121.138 | 0.35706 | 1.4211e-13 | -0.0085084 | -0.0024209 | 0.030219 | -0.014337 | 0.010311 | -0.0019839 | 0.007488 | 0.0077131 | -0.0075247 | 0.041331 | 0.0028821 | 0.042253 | 0.005985 | 0.000747 | 0.20321 | 0.004938 | 0.45331 | 0.15673 | 0.046835 | 0.004938 | -0.010564 | 0.15318 | 0.293 | -0.17081 | -0.27862 | 121.2947 | -0.15384 | 121.1803 | 121.1387 | -0.15598 | -0.35212 | 0.096255 | 120.8594 | -0.20387 | 121.1848 | 121.1274 | 0.26805 | -0.064055 | -0.52787 | 121.3412 | 121.1429 | 121.5913 | 121.144 | -0.20032 | 121.2912 | 121.431 | 120.9672 | 121.1429 | -0.63567
1835.7031 | 121.5866 | -121.1655 | 0.37994 | 1.4211e-13 | -0.0089358 | -0.0026347 | 0.030219 | -0.014123 | 0.010098 | 0.0056466 | 0.0072744 | 0.0077131 | -0.0081657 | 0.041331 | 0.0028821 | 0.033096 | 0.005985 | 0.009904 | 0.20779 | -0.00422 | 0.44415 | 0.15673 | 0.042256 | 0.014095 | -0.0243 | 0.15318 | 0.28842 | -0.16624 | -0.2832 | 121.3222 | -0.17215 | 121.1986 | 121.1754 | -0.14683 | -0.38416 | 0.06421 | 120.8823 | -0.22676 | 121.2077 | 121.1412 | 0.2589 | -0.091521 | -0.54618 | 121.3733 | 121.1612 | 121.6096 | 121.1715 | -0.22321 | 121.3187 | 121.4539 | 120.9992 | 121.1796 | -0.66314
1837.4375 | 121.6736 | -121.1609 | 0.3479 | 1.4211e-13 | -0.0085084 | -0.0026347 | 0.030219 | -0.014337 | 0.010739 | 0.0056466 | 0.007488 | 0.0079267 | -0.0077383 | 0.040903 | 0.0026685 | 0.033096 | 0.001407 | 0.005325 | 0.20779 | -0.027115 | 0.44873 | 0.15673 | 0.046835 | 0.004938 | -0.015143 | 0.16234 | 0.30674 | -0.17081 | -0.27862 | 121.3176 | -0.14011 | 121.194 | 121.1662 | -0.15141 | -0.37501 | 0.10083 | 120.8823 | -0.18556 | 121.2077 | 121.1457 | 0.26348 | -0.041163 | -0.51872 | 121.3687 | 121.1338 | 121.6096 | 121.1623 | -0.19117 | 121.3232 | 121.4676 | 120.9901 | 121.1658 | -0.62652
1839.125 | 121.6187 | -121.1929 | 0.37994 | 1.4211e-13 | -0.0085084 | -0.0024209 | 0.029792 | -0.014123 | 0.010739 | 0.0056466 | 0.0077016 | 0.0077131 | -0.0077383 | 0.041331 | 0.0028821 | 0.037675 | 0.001407 | 0.009904 | 0.20321 | -0.017957 | 0.44873 | 0.15215 | 0.055992 | 0.014095 | -0.019721 | 0.16234 | 0.293 | -0.17081 | -0.29236 | 121.3451 | -0.17673 | 121.2306 | 121.2028 | -0.14225 | -0.3979 | 0.068788 | 120.9006 | -0.2176 | 121.2489 | 121.1732 | 0.27264 | -0.086943 | -0.55076 | 121.3961 | 121.175 | 121.6417 | 121.1943 | -0.22779 | 121.3553 | 121.4859 | 121.0221 | 121.207 | -0.6723
1840.8906 | 121.6415 | -121.2112 | 0.37079 | 1.4211e-13 | -0.0085084 | -0.0024209 | 0.030005 | -0.014337 | 0.010525 | 0.0056466 | 0.007488 | 0.0072857 | -0.0079521 | 0.041544 | 0.0028821 | 0.033096 | 0.001407 | 0.005325 | 0.19864 | -0.017957 | 0.44873 | 0.15673 | 0.042256 | 0.009516 | -0.015143 | 0.15776 | 0.30674 | -0.17081 | -0.28778 | 121.368 | -0.17215 | 121.2443 | 121.2166 | -0.15141 | -0.38875 | 0.077943 | 120.9235 | -0.21302 | 121.2535 | 121.1961 | 0.27263 | -0.064052 | -0.5416 | 121.4099 | 121.1933 | 121.66 | 121.2126 | -0.21406 | 121.369 | 121.518 | 121.0404 | 121.2208 | -0.65857
1842.6406 | 121.582 | -121.2341 | 0.37537 | 1.4211e-13 | -0.0087222 | -0.0028483 | 0.030433 | -0.014123 | 0.010525 | -0.0019839 | 0.0072744 | 0.0079267 | -0.0077383 | 0.041331 | 0.0028821 | 0.037675 | 0.005985 | 0.005325 | 0.20779 | 0.03699 | 0.44415 | 0.15215 | 0.051413 | 0.009516 | -0.015143 | 0.15776 | 0.30216 | -0.16624 | -0.27862 | 121.3863 | -0.16757 | 121.2718 | 121.2395 | -0.14683 | -0.33838 | 0.068788 | 120.9555 | -0.2176 | 121.2855 | 121.219 | 0.26348 | -0.073208 | -0.5416 | 121.4419 | 121.2711 | 121.6783 | 121.2401 | -0.22321 | 121.3919 | 121.5363 | 121.0679 | 121.2436 | -0.65399
1844.3281 | 121.6644 | -121.2158 | 0.3479 | 1.4211e-13 | -0.0087222 | -0.0026347 | 0.030005 | -0.014123 | 0.010525 | 0.020908 | 0.007488 | 0.0074993 | -0.0075247 | 0.041544 | 0.0026685 | 0.033096 | 0.015142 | 0.000747 | 0.20779 | -0.017957 | 0.44873 | 0.15673 | 0.046835 | 0.004938 | -0.019721 | 0.16234 | 0.29758 | -0.17539 | -0.2832 | 121.3726 | -0.14011 | 121.2489 | 121.2166 | -0.15598 | -0.36586 | 0.10083 | 120.9326 | -0.18556 | 121.2627 | 121.1961 | 0.26348 | -0.05032 | -0.52329 | 121.4236 | 121.1979 | 121.6646 | 121.231 | -0.19117 | 121.3782 | 121.5134 | 121.0404 | 121.2208 | -0.6311
1846.0781 | 121.6324 | -121.2616 | 0.37537 | 1.4211e-13 | -0.0085084 | -0.0024209 | 0.030219 | -0.013909 | 0.010739 | -0.0019839 | 0.007488 | 0.0077131 | -0.0077383 | 0.041117 | 0.0028821 | 0.042253 | 0.001407 | 0.009904 | 0.19406 | -0.04543 | 0.44873 | 0.14757 | 0.051413 | 0.014095 | -0.019721 | 0.15776 | 0.29758 | -0.16624 | -0.27862 | 121.4092 | -0.18131 | 121.3038 | 121.2715 | -0.13767 | -0.4208 | 0.073366 | 120.983 | -0.2176 | 121.313 | 121.2419 | 0.2589 | -0.077786 | -0.5416 | 121.4557 | 121.2162 | 121.7103 | 121.263 | -0.22779 | 121.4194 | 121.5592 | 121.0954 | 121.2757 | -0.65399
1847.8281 | 121.6827 | -121.2708 | 0.35706 | 1.4211e-13 | -0.0085084 | -0.0024209 | 0.030005 | -0.014123 | 0.010525 | -0.0019839 | 0.0070608 | 0.0074993 | -0.0079521 | 0.041331 | 0.0028821 | 0.037675 | -0.003172 | 0.000747 | 0.20779 | 0.041569 | 0.44873 | 0.15673 | 0.046835 | 0.009516 | -0.015143 | 0.14861 | 0.30674 | -0.17539 | -0.2832 | 121.4275 | -0.14926 | 121.3084 | 121.2715 | -0.15598 | -0.31549 | 0.091676 | 120.9876 | -0.20845 | 121.3176 | 121.2556 | 0.26805 | -0.050319 | -0.53245 | 121.4785 | 121.3123 | 121.7195 | 121.2676 | -0.20032 | 121.4194 | 121.5775 | 121.0954 | 121.2803 | -0.64025
1849.5156 | 121.7422 | -121.2616 | 0.31586 | 1.4211e-13 | -0.0082948 | -0.0024209 | 0.029792 | -0.013696 | 0.010739 | -0.0019839 | 0.007488 | 0.0081403 | -0.0075247 | 0.041331 | 0.0030959 | 0.033096 | 0.001407 | 0.005325 | 0.20321 | -0.036272 | 0.43957 | 0.15215 | 0.033099 | 0.014095 | -0.019721 | 0.15776 | 0.30216 | -0.17081 | -0.2832 | 121.4137 | -0.11264 | 121.2947 | 121.2669 | -0.14683 | -0.35213 | 0.12372 | 120.9784 | -0.15809 | 121.2947 | 121.2419 | 0.26348 | -0.013699 | -0.48667 | 121.4648 | 121.2253 | 121.7012 | 121.263 | -0.1637 | 121.4194 | 121.5638 | 121.0908 | 121.2757 | -0.59906
1851.2031 | 121.6324 | -121.312 | 0.34332 | 1.4211e-13 | -0.0087222 | -0.0026347 | 0.030005 | -0.014123 | 0.010311 | -0.0019839 | 0.0072744 | 0.0074993 | -0.0077383 | 0.041331 | 0.0028821 | 0.037675 | 0.001407 | 0.009904 | 0.19864 | -0.017957 | 0.44873 | 0.16131 | 0.051413 | 0.009516 | -0.015143 | 0.15776 | 0.293 | -0.16624 | -0.27862 | 121.4733 | -0.14469 | 121.3496 | 121.3219 | -0.15141 | -0.36128 | 0.10541 | 121.0333 | -0.18556 | 121.3634 | 121.2968 | 0.26348 | -0.050322 | -0.50956 | 121.5106 | 121.294 | 121.7607 | 121.3134 | -0.18201 | 121.4697 | 121.605 | 121.1457 | 121.3215 | -0.62194
1852.9531 | 121.7422 | -121.3211 | 0.33417 | 1.4211e-13 | -0.0087222 | -0.0022073 | 0.030005 | -0.014123 | 0.010311 | -0.0019839 | 0.0077016 | 0.0077131 | -0.0070975 | 0.041331 | 0.0026685 | 0.037675 | 0.005985 | 0.009904 | 0.20321 | -0.031693 | 0.45331 | 0.14757 | 0.042256 | 0.014095 | -0.0243 | 0.14861 | 0.28842 | -0.17539 | -0.27862 | 121.4687 | -0.13095 | 121.3588 | 121.331 | -0.13767 | -0.36586 | 0.11914 | 121.0425 | -0.18556 | 121.3634 | 121.2968 | 0.25432 | -0.045744 | -0.50956 | 121.5243 | 121.2894 | 121.7744 | 121.3271 | -0.18659 | 121.4697 | 121.6095 | 121.1457 | 121.3352 | -0.61279
1854.7031 | 121.6461 | -121.3577 | 0.36163 | 1.4211e-13 | -0.0085084 | -0.0026347 | 0.030005 | -0.01455 | 0.010525 | -0.0019839 | 0.007488 | 0.0077131 | -0.0075247 | 0.041544 | 0.0028821 | 0.033096 | 0.001407 | 0.014482 | 0.20321 | 0.000359 | 0.44415 | 0.15215 | 0.046835 | 0.014095 | -0.010564 | 0.16234 | 0.29758 | -0.16624 | -0.27862 | 121.5099 | -0.15842 | 121.3908 | 121.3722 | -0.13767 | -0.36127 | 0.082521 | 121.0791 | -0.19929 | 121.4046 | 121.3472 | 0.26805 | -0.064053 | -0.52787 | 121.5609 | 121.3581 | 121.8019 | 121.3591 | -0.20948 | 121.5201 | 121.6553 | 121.1915 | 121.3718 | -0.64025
1856.4531 | 121.7239 | -121.3531 | 0.32501 | 1.4211e-13 | -0.0087222 | -0.0026347 | 0.030005 | -0.014337 | 0.010525 | -0.0019839 | 0.0072744 | 0.0079267 | -0.0075247 | 0.041331 | 0.0028821 | 0.033096 | 0.010564 | 0.005325 | 0.20779 | -0.013378 | 0.44873 | 0.15673 | 0.046835 | 0.018674 | -0.015143 | 0.16234 | 0.293 | -0.17539 | -0.2832 | 121.5099 | -0.11722 | 121.3862 | 121.3585 | -0.15141 | -0.33839 | 0.12372 | 121.07 | -0.16267 | 121.4 | 121.338 | 0.26805 | -0.032011 | -0.5004 | 121.5609 | 121.3398 | 121.8019 | 121.3637 | -0.16828 | 121.5155 | 121.6462 | 121.1778 | 121.3718 | -0.60821
1858.1406 | 121.756 | -121.3348 | 0.32044 | 1.4211e-13 | -0.0089358 | -0.0028483 | 0.030005 | -0.013909 | 0.010525 | -0.0019839 | 0.007488 | 0.0079267 | -0.0077383 | 0.041758 | 0.0028821 | 0.042253 | -0.003172 | 0.005325 | 0.19864 | -0.00422 | 0.44873 | 0.15215 | 0.051413 | 0.014095 | -0.0243 | 0.15776 | 0.29758 | -0.17081 | -0.2832 | 121.487 | -0.1218 | 121.3771 | 121.3402 | -0.14683 | -0.32466 | 0.1283 | 121.0516 | -0.16267 | 121.3863 | 121.3105 | 0.2589 | -0.022855 | -0.49125 | 121.5335 | 121.3306 | 121.7836 | 121.3317 | -0.16828 | 121.4926 | 121.6324 | 121.164 | 121.3489 | -0.60363
1859.8906 | 121.7331 | -121.3852 | 0.35706 | 1.4211e-13 | -0.0087222 | -0.0026347 | 0.030005 | -0.013909 | 0.010739 | 0.0056466 | 0.0077016 | 0.0079267 | -0.0075247 | 0.041544 | 0.0026685 | 0.037675 | 0.005985 | 0.005325 | 0.20321 | -0.013378 | 0.44873 | 0.15673 | 0.042256 | 0.014095 | -0.010564 | 0.16692 | 0.30216 | -0.17081 | -0.27862 | 121.5419 | -0.15384 | 121.4229 | 121.3905 | -0.15141 | -0.37043 | 0.091676 | 121.1066 | -0.19013 | 121.4274 | 121.3746 | 0.26805 | -0.054898 | -0.52787 | 121.5884 | 121.3718 | 121.8339 | 121.3912 | -0.20032 | 121.5521 | 121.6874 | 121.2144 | 121.3993 | -0.63567
1861.6406 | 121.8018 | -121.3531 | 0.29297 | 1.4211e-13 | -0.0087222 | -0.0030619 | 0.030219 | -0.013696 | 0.010739 | 0.013277 | 0.0077016 | 0.0079267 | -0.0075247 | 0.041331 | 0.0024549 | 0.033096 | -0.003172 | -0.003831 | 0.20321 | 0.018675 | 0.43957 | 0.15673 | 0.046835 | 0.009516 | -0.015143 | 0.15776 | 0.28842 | -0.17539 | -0.27404 | 121.5099 | -0.089755 | 121.3862 | 121.3493 | -0.16056 | -0.27429 | 0.14661 | 121.0791 | -0.1352 | 121.4 | 121.338 | 0.2589 | -0.004546 | -0.46836 | 121.5564 | 121.3718 | 121.7927 | 121.35 | -0.13624 | 121.5109 | 121.6416 | 121.1778 | 121.3627 | -0.56701
1863.4062 | 121.7834 | -121.4035 | 0.32501 | 1.4211e-13 | -0.0089358 | -0.0024209 | 0.030005 | -0.014123 | 0.010952 | 0.0056466 | 0.0072744 | 0.0074993 | -0.0077383 | 0.041117 | 0.0028821 | 0.046831 | 0.015142 | 0.009904 | 0.19864 | 0.032411 | 0.44873 | 0.14757 | 0.042256 | 0.014095 | -0.015143 | 0.16234 | 0.293 | -0.17081 | -0.2832 | 121.5511 | -0.12638 | 121.4503 | 121.4134 | -0.13767 | -0.2926 | 0.12372 | 121.1203 | -0.16267 | 121.4458 | 121.3884 | 0.26805 | -0.032011 | -0.49583 | 121.6021 | 121.4359 | 121.8522 | 121.4186 | -0.17744 | 121.5658 | 121.6965 | 121.2327 | 121.4176 | -0.60821
1865.1094 | 121.7377 | -121.4447 | 0.33875 | 1.4211e-13 | -0.0091494 | -0.0026347 | 0.030219 | -0.014337 | 0.010311 | -0.0019839 | 0.007488 | 0.0077131 | -0.0075247 | 0.041117 | 0.0033095 | 0.042253 | 0.001407 | 0.000747 | 0.20321 | 0.000359 | 0.44415 | 0.15673 | 0.037677 | 0.004938 | -0.015143 | 0.16234 | 0.30674 | -0.17539 | -0.27862 | 121.6014 | -0.13553 | 121.487 | 121.4454 | -0.15598 | -0.33839 | 0.10541 | 121.1661 | -0.1764 | 121.4824 | 121.4296 | 0.26348 | -0.032008 | -0.51414 | 121.6479 | 121.4451 | 121.8889 | 121.4461 | -0.18201 | 121.607 | 121.7514 | 121.2693 | 121.4496 | -0.61736
1866.8594 | 121.7102 | -121.4447 | 0.3479 | 1.4211e-13 | -0.0087222 | -0.0028483 | 0.029792 | -0.014123 | 0.010525 | -0.0019839 | 0.007488 | 0.0077131 | -0.0077383 | 0.041544 | 0.0024549 | 0.042253 | 0.001407 | 0.005325 | 0.20779 | -0.00422 | 0.44415 | 0.15673 | 0.046835 | 0.014095 | -0.015143 | 0.16234 | 0.29758 | -0.17081 | -0.2832 | 121.6014 | -0.14011 | 121.487 | 121.45 | -0.15141 | -0.35212 | 0.096254 | 121.1615 | -0.18556 | 121.4915 | 121.4296 | 0.26805 | -0.05032 | -0.51872 | 121.6525 | 121.4405 | 121.8889 | 121.4461 | -0.19117 | 121.607 | 121.7423 | 121.2739 | 121.4588 | -0.6311
1868.5469 | 121.8475 | -121.3898 | 0.3067 | 1.4211e-13 | -0.0091494 | -0.0026347 | 0.029792 | -0.013909 | 0.010525 | 0.0056466 | 0.007488 | 0.0074993 | -0.0075247 | 0.041544 | 0.0026685 | 0.037675 | 0.001407 | 0.014482 | 0.20779 | -0.022536 | 0.44415 | 0.15673 | 0.051413 | 0.009516 | -0.019721 | 0.15776 | 0.30216 | -0.16624 | -0.28778 | 121.5465 | -0.098909 | 121.4274 | 121.4043 | -0.14225 | -0.32924 | 0.13745 | 121.102 | -0.14894 | 121.4412 | 121.37 | 0.26806 | -0.004544 | -0.47294 | 121.5976 | 121.3672 | 121.8339 | 121.3912 | -0.14997 | 121.5475 | 121.6919 | 121.2235 | 121.3993 | -0.59448
1870.3125 | 121.7239 | -121.4722 | 0.32959 | 1.4211e-13 | -0.0087222 | -0.0028483 | 0.030005 | -0.013909 | 0.010525 | 0.0056466 | 0.0077016 | 0.0079267 | -0.0077383 | 0.041544 | 0.0026685 | 0.037675 | 0.005985 | 0.005325 | 0.20779 | -0.040851 | 0.43957 | 0.15673 | 0.037677 | 0.004938 | -0.0243 | 0.15776 | 0.29758 | -0.17539 | -0.28778 | 121.6289 | -0.1218 | 121.5098 | 121.4775 | -0.15141 | -0.37044 | 0.10998 | 121.1844 | -0.17183 | 121.5098 | 121.4479 | 0.26348 | -0.03201 | -0.50498 | 121.68 | 121.4313 | 121.9117 | 121.4782 | -0.17286 | 121.6299 | 121.7697 | 121.2968 | 121.4771 | -0.61737
1872 | 121.8109 | -121.4539 | 0.31128 | 1.4211e-13 | -0.0089358 | -0.0026347 | 0.029792 | -0.014123 | 0.010525 | 0.013277 | 0.0072744 | 0.0077131 | -0.0077383 | 0.041331 | 0.0028821 | 0.037675 | 0.010564 | 0.014482 | 0.20321 | -0.054588 | 0.45331 | 0.15673 | 0.046835 | 0.014095 | -0.015143 | 0.16234 | 0.28384 | -0.17081 | -0.27862 | 121.6106 | -0.10806 | 121.4915 | 121.4683 | -0.14225 | -0.36587 | 0.14203 | 121.1752 | -0.14894 | 121.5007 | 121.4387 | 0.26348 | -0.027435 | -0.48209 | 121.6571 | 121.3993 | 121.9072 | 121.4644 | -0.15455 | 121.6162 | 121.7377 | 121.283 | 121.468 | -0.5899
1873.7344 | 121.7514 | -121.4813 | 0.31586 | 1.4211e-13 | -0.0089358 | -0.0026347 | 0.030005 | -0.014123 | 0.010311 | -0.0019839 | 0.0072744 | 0.0074993 | -0.0077383 | 0.041544 | 0.0033095 | 0.037675 | 0.010564 | 0.000747 | 0.20321 | -0.027115 | 0.435 | 0.16131 | 0.051413 | 0.004938 | -0.015143 | 0.16692 | 0.293 | -0.17081 | -0.27862 | 121.6426 | -0.11264 | 121.519 | 121.4821 | -0.16056 | -0.34297 | 0.11914 | 121.2027 | -0.14894 | 121.5327 | 121.4662 | 0.26348 | -0.022856 | -0.48667 | 121.6845 | 121.4542 | 121.9163 | 121.4919 | -0.15455 | 121.6482 | 121.7743 | 121.3105 | 121.4863 | -0.59448
1875.5 | 121.7697 | -121.4859 | 0.32501 | 1.4211e-13 | -0.0091494 | -0.0026347 | 0.030005 | -0.014337 | 0.010739 | 0.0056466 | 0.0077016 | 0.0077131 | -0.0073111 | 0.041331 | 0.0028821 | 0.033096 | 0.005985 | 0.005325 | 0.20779 | -0.013378 | 0.43957 | 0.15215 | 0.042256 | 0.014095 | -0.015143 | 0.16234 | 0.293 | -0.17081 | -0.27862 | 121.6381 | -0.11722 | 121.519 | 121.4912 | -0.14683 | -0.33839 | 0.11456 | 121.2073 | -0.16267 | 121.5282 | 121.4708 | 0.26348 | -0.032011 | -0.49583 | 121.6937 | 121.4725 | 121.9255 | 121.4919 | -0.17286 | 121.6482 | 121.7789 | 121.3151 | 121.5 | -0.60363
1877.1875 | 121.8475 | -121.4584 | 0.31128 | 1.4211e-13 | -0.0093632 | -0.0024209 | 0.030219 | -0.014123 | 0.010525 | -0.0019839 | 0.0077016 | 0.0077131 | -0.0073111 | 0.041758 | 0.0026685 | 0.037675 | 0.005985 | 0.009904 | 0.20779 | -0.04543 | 0.45331 | 0.15215 | 0.042256 | 0.014095 | -0.019721 | 0.15776 | 0.29758 | -0.17539 | -0.28778 | 121.6106 | -0.10349 | 121.4961 | 121.4683 | -0.14225 | -0.35671 | 0.14203 | 121.1707 | -0.15351 | 121.5007 | 121.4387 | 0.26806 | -0.013699 | -0.48667 | 121.6662 | 121.413 | 121.9117 | 121.4644 | -0.15913 | 121.6162 | 121.756 | 121.283 | 121.4725 | -0.59906
1878.9219 | 121.9254 | -121.4767 | 0.30212 | 1.4211e-13 | -0.0089358 | -0.0026347 | 0.030005 | -0.014123 | 0.010739 | -0.0019839 | 0.0072744 | 0.0079267 | -0.0077383 | 0.041544 | 0.0024549 | 0.042253 | 0.005985 | 0.005325 | 0.20321 | 0.014096 | 0.43957 | 0.15673 | 0.046835 | 0.014095 | -0.010564 | 0.15318 | 0.29758 | -0.16624 | -0.27862 | 121.6335 | -0.09891 | 121.519 | 121.4821 | -0.15141 | -0.28803 | 0.13745 | 121.1981 | -0.14894 | 121.5236 | 121.4662 | 0.26805 | -0.004544 | -0.46836 | 121.68 | 121.4908 | 121.9163 | 121.4827 | -0.14539 | 121.6299 | 121.7743 | 121.3105 | 121.4908 | -0.58074
1880.6719 | 121.8018 | -121.5225 | 0.32044 | 1.4211e-13 | -0.0089358 | -0.0026347 | 0.030005 | -0.014337 | 0.010525 | 0.0056466 | 0.0072744 | 0.0074993 | -0.0075247 | 0.041117 | 0.0022413 | 0.037675 | 0.010564 | 0.005325 | 0.20321 | 0.027833 | 0.44415 | 0.14757 | 0.042256 | 0.014095 | -0.019721 | 0.15318 | 0.30216 | -0.17539 | -0.28778 | 121.6701 | -0.11722 | 121.5602 | 121.5278 | -0.14225 | -0.2926 | 0.12372 | 121.2347 | -0.16725 | 121.5648 | 121.5028 | 0.26806 | -0.018277 | -0.49583 | 121.7257 | 121.5504 | 121.9667 | 121.5331 | -0.17286 | 121.6757 | 121.8247 | 121.3471 | 121.5366 | -0.60821
1882.3594 | 121.8155 | -121.5408 | 0.33875 | 1.4211e-13 | -0.0091494 | -0.0024209 | 0.030219 | -0.014337 | 0.010525 | 0.0056466 | 0.007488 | 0.0079267 | -0.0077383 | 0.041758 | 0.0028821 | 0.037675 | -0.003172 | 0.009904 | 0.20321 | 0.014096 | 0.44873 | 0.15673 | 0.051413 | 0.009516 | -0.019721 | 0.16234 | 0.30216 | -0.17539 | -0.2832 | 121.6976 | -0.13553 | 121.5785 | 121.5507 | -0.14683 | -0.32465 | 0.10999 | 121.2576 | -0.1764 | 121.5922 | 121.5211 | 0.26348 | -0.036587 | -0.51414 | 121.744 | 121.5549 | 121.9896 | 121.5377 | -0.18201 | 121.7032 | 121.843 | 121.3654 | 121.5503 | -0.62194
1884.1094 | 121.8109 | -121.5134 | 0.33875 | 1.4211e-13 | -0.0089358 | -0.0030619 | 0.030005 | -0.013909 | 0.010525 | 0.013277 | 0.007488 | 0.0077131 | -0.0075247 | 0.041758 | 0.0028821 | 0.033096 | 0.010564 | 0.005325 | 0.20779 | 0.004938 | 0.44873 | 0.15673 | 0.046835 | 0.014095 | -0.019721 | 0.16234 | 0.30216 | -0.16624 | -0.28778 | 121.6701 | -0.13095 | 121.5465 | 121.5187 | -0.15141 | -0.33381 | 0.10999 | 121.2256 | -0.1764 | 121.5602 | 121.4936 | 0.26806 | -0.036587 | -0.50498 | 121.7212 | 121.5183 | 121.9621 | 121.5239 | -0.18201 | 121.6757 | 121.8155 | 121.3471 | 121.5275 | -0.62652
1885.875 | 121.9528 | -121.4813 | 0.29297 | 1.4211e-13 | -0.0091494 | -0.0028483 | 0.030005 | -0.014123 | 0.010525 | -0.0019839 | 0.0072744 | 0.0074993 | -0.0077383 | 0.041972 | 0.0028821 | 0.037675 | 0.005985 | 0.000747 | 0.20321 | 0.000359 | 0.45331 | 0.15673 | 0.051413 | 0.009516 | -0.015143 | 0.16692 | 0.29758 | -0.16624 | -0.2832 | 121.6381 | -0.089755 | 121.519 | 121.4821 | -0.15598 | -0.29261 | 0.16034 | 121.1981 | -0.12605 | 121.5327 | 121.4662 | 0.26805 | 0.004611 | -0.4592 | 121.6845 | 121.4817 | 121.9346 | 121.4873 | -0.13624 | 121.6482 | 121.7789 | 121.3151 | 121.4908 | -0.57617
1888.9531 | 121.843 | -121.5729 | 0.33875 | 1.4211e-13 | -0.0093632 | -0.0026347 | 0.030005 | -0.013909 | 0.010525 | -0.0096144 | 0.0072744 | 0.0079267 | -0.0077383 | 0.041544 | 0.0022413 | 0.037675 | 0.005985 | 0.009904 | 0.20779 | -0.050009 | 0.44873 | 0.15673 | 0.051413 | 0.009516 | -0.010564 | 0.15776 | 0.29758 | -0.16624 | -0.2832 | 121.7296 | -0.13095 | 121.6106 | 121.5828 | -0.14683 | -0.38875 | 0.10999 | 121.2897 | -0.18098 | 121.6243 | 121.5623 | 0.27263 | -0.041165 | -0.50498 | 121.7807 | 121.5229 | 122.0216 | 121.5789 | -0.18201 | 121.7306 | 121.8705 | 121.4066 | 121.5824 | -0.62194
1892.9375 | 121.9803 | -121.55 | 0.3067 | 1.4211e-13 | -0.0091494 | -0.0028483 | 0.030219 | -0.014337 | 0.010525 | 0.0056466 | 0.0077016 | 0.0077131 | -0.0079521 | 0.042185 | 0.0026685 | 0.042253 | 0.001407 | 0.009904 | 0.20321 | 0.004938 | 0.45331 | 0.16131 | 0.046835 | 0.004938 | -0.015143 | 0.15776 | 0.29758 | -0.16624 | -0.28778 | 121.7113 | -0.10349 | 121.5922 | 121.5599 | -0.15141 | -0.30176 | 0.14661 | 121.2622 | -0.14894 | 121.5968 | 121.5348 | 0.27263 | -0.009122 | -0.47294 | 121.7532 | 121.5549 | 122.0033 | 121.5514 | -0.14539 | 121.7078 | 121.8476 | 121.3838 | 121.5549 | -0.59448
1899.2812 | 121.8933 | -121.5866 | 0.31586 | 1.4211e-13 | -0.0091494 | -0.0028483 | 0.029792 | -0.014123 | 0.010525 | 0.0056466 | 0.0072744 | 0.0077131 | -0.0077383 | 0.041544 | 0.0028821 | 0.042253 | 0.005985 | 0.000747 | 0.19864 | -0.017957 | 0.44415 | 0.15215 | 0.042256 | 0.014095 | -0.019721 | 0.16234 | 0.293 | -0.17081 | -0.28778 | 121.7388 | -0.11722 | 121.6289 | 121.5874 | -0.15141 | -0.33381 | 0.1283 | 121.2988 | -0.15352 | 121.6289 | 121.5669 | 0.26806 | -0.022856 | -0.48667 | 121.7852 | 121.5687 | 122.0308 | 121.5926 | -0.1637 | 121.749 | 121.8796 | 121.4158 | 121.6007 | -0.60363
1900.9844 | 121.9345 | -121.6049 | 0.32959 | 1.4211e-13 | -0.0095768 | -0.0030619 | 0.030005 | -0.014123 | 0.010098 | 0.020908 | 0.0072744 | 0.0077131 | -0.0077383 | 0.041972 | 0.0028821 | 0.042253 | 0.001407 | 0.000747 | 0.20321 | 0.041569 | 0.44415 | 0.14757 | 0.046835 | 0.014095 | -0.019721 | 0.15776 | 0.30216 | -0.17081 | -0.2832 | 121.7525 | -0.12638 | 121.6472 | 121.6057 | -0.14683 | -0.28802 | 0.11456 | 121.3217 | -0.17183 | 121.6518 | 121.5852 | 0.26348 | -0.027432 | -0.5004 | 121.8081 | 121.6465 | 122.0491 | 121.6063 | -0.18202 | 121.7627 | 121.9071 | 121.4341 | 121.619 | -0.61279
1902.75 | 122.0169 | -121.582 | 0.29297 | 1.4211e-13 | -0.0093632 | -0.0026347 | 0.029792 | -0.014123 | 0.010098 | 0.013277 | 0.0070608 | 0.0081403 | -0.0077383 | 0.041972 | 0.0024549 | 0.037675 | 0.001407 | -0.003831 | 0.19864 | 0.032411 | 0.44873 | 0.15673 | 0.046835 | 0.014095 | -0.019721 | 0.16692 | 0.28842 | -0.17081 | -0.27404 | 121.7388 | -0.094333 | 121.6197 | 121.5782 | -0.16056 | -0.26056 | 0.15576 | 121.308 | -0.12605 | 121.6289 | 121.5623 | 0.25432 | -0.004546 | -0.46378 | 121.7807 | 121.6144 | 122.0308 | 121.5834 | -0.13624 | 121.749 | 121.8705 | 121.4112 | 121.5961 | -0.56701
1904.4375 | 121.9208 | -121.6232 | 0.32044 | 1.4211e-13 | -0.0095768 | -0.0026347 | 0.029792 | -0.014337 | 0.010525 | -0.0019839 | 0.0072744 | 0.0077131 | -0.0079521 | 0.041758 | 0.0026685 | 0.033096 | 0.005985 | 0.005325 | 0.20779 | -0.050009 | 0.45331 | 0.15215 | 0.051413 | 0.018674 | -0.015143 | 0.15776 | 0.29758 | -0.17081 | -0.29236 | 121.7754 | -0.11264 | 121.6563 | 121.6286 | -0.14683 | -0.37044 | 0.13288 | 121.3309 | -0.16267 | 121.6746 | 121.6081 | 0.27721 | -0.022855 | -0.49125 | 121.831 | 121.5732 | 122.0765 | 121.6292 | -0.16828 | 121.781 | 121.9208 | 121.4524 | 121.6419 | -0.61279
1906.125 | 121.9162 | -121.637 | 0.33417 | 1.4211e-13 | -0.0097904 | -0.0026347 | 0.029792 | -0.014123 | 0.010098 | 0.0056466 | 0.007488 | 0.0077131 | -0.0079521 | 0.042185 | 0.0026685 | 0.042253 | 0.010564 | 0.009904 | 0.20779 | -0.00422 | 0.44415 | 0.15215 | 0.051413 | 0.018674 | -0.005985 | 0.15776 | 0.29758 | -0.17081 | -0.27862 | 121.7891 | -0.12637 | 121.6792 | 121.6469 | -0.14225 | -0.33839 | 0.10999 | 121.3583 | -0.1764 | 121.6884 | 121.631 | 0.27263 | -0.036587 | -0.50498 | 121.8448 | 121.6327 | 122.0811 | 121.6475 | -0.18201 | 121.7947 | 121.9345 | 121.4661 | 121.6556 | -0.61279
1907.8906 | 122.049 | -121.5958 | 0.29297 | 1.4211e-13 | -0.0093632 | -0.0026347 | 0.030005 | -0.013909 | 0.010311 | 0.0056466 | 0.007488 | 0.0077131 | -0.0077383 | 0.041758 | 0.0024549 | 0.033096 | 0.001407 | 0.005325 | 0.20321 | 0.050727 | 0.44873 | 0.15215 | 0.051413 | 0.023253 | -0.015143 | 0.15776 | 0.293 | -0.16166 | -0.27862 | 121.7479 | -0.089755 | 121.6289 | 121.6011 | -0.14683 | -0.24224 | 0.15576 | 121.3171 | -0.1352 | 121.6472 | 121.5806 | 0.26348 | 3.2e-05 | -0.45463 | 121.799 | 121.6465 | 122.0445 | 121.5972 | -0.14082 | 121.7535 | 121.8888 | 121.4341 | 121.619 | -0.57159
1909.6406 | 121.9299 | -121.6507 | 0.32959 | 1.4211e-13 | -0.0093632 | -0.0026347 | 0.029792 | -0.014123 | 0.010739 | -0.0019839 | 0.0072744 | 0.0074993 | -0.0075247 | 0.041972 | 0.0026685 | 0.033096 | 0.005985 | 0.000747 | 0.20321 | -0.022536 | 0.44415 | 0.14757 | 0.042256 | 0.014095 | -0.010564 | 0.16234 | 0.293 | -0.17081 | -0.28778 | 121.7983 | -0.12638 | 121.6838 | 121.6514 | -0.14683 | -0.35213 | 0.11456 | 121.3629 | -0.16725 | 121.693 | 121.6401 | 0.27721 | -0.036589 | -0.5004 | 121.8539 | 121.6282 | 122.0948 | 121.6567 | -0.18202 | 121.813 | 121.9437 | 121.4799 | 121.6648 | -0.61737
1911.3906 | 122.0764 | -121.6095 | 0.28381 | 1.4211e-13 | -0.0095768 | -0.0028483 | 0.030219 | -0.01455 | 0.010311 | -0.0096144 | 0.007488 | 0.0077131 | -0.0077383 | 0.042185 | 0.0024549 | 0.046831 | 0.005985 | 0.000747 | 0.20779 | -0.017957 | 0.44415 | 0.15215 | 0.051413 | 0.009516 | -0.015143 | 0.16234 | 0.293 | -0.17081 | -0.28778 | 121.7616 | -0.07602 | 121.6563 | 121.6102 | -0.15141 | -0.30177 | 0.16034 | 121.3217 | -0.12147 | 121.6609 | 121.5944 | 0.27263 | 0.009188 | -0.45463 | 121.8173 | 121.5915 | 122.0537 | 121.6155 | -0.13166 | 121.7718 | 121.9025 | 121.4387 | 121.619 | -0.57159
1913.0781 | 122.0947 | -121.582 | 0.28839 | 1.4211e-13 | -0.0093632 | -0.0024209 | 0.029792 | -0.014123 | 0.010311 | -0.0096144 | 0.0072744 | 0.0077131 | -0.0077383 | 0.042185 | 0.0024549 | 0.037675 | 0.001407 | 0.009904 | 0.20779 | 0.004938 | 0.43957 | 0.14757 | 0.051413 | 0.014095 | -0.015143 | 0.16234 | 0.28842 | -0.17081 | -0.2832 | 121.7296 | -0.080598 | 121.6197 | 121.5919 | -0.13767 | -0.28345 | 0.15118 | 121.2988 | -0.12605 | 121.6334 | 121.5669 | 0.26805 | 3.2e-05 | -0.45921 | 121.7898 | 121.587 | 122.0216 | 121.5834 | -0.14082 | 121.7444 | 121.8705 | 121.4112 | 121.5961 | -0.57159
1914.8125 | 122.0901 | -121.6141 | 0.27924 | 1.4211e-13 | -0.0091494 | -0.0026347 | 0.030005 | -0.013909 | 0.010525 | -0.0019839 | 0.007488 | 0.0081403 | -0.0077383 | 0.042185 | 0.0026685 | 0.037675 | 0.001407 | 0.009904 | 0.20321 | -0.013378 | 0.44415 | 0.15215 | 0.051413 | 0.018674 | -0.015143 | 0.15776 | 0.29758 | -0.16624 | -0.2832 | 121.7662 | -0.076022 | 121.6517 | 121.624 | -0.14225 | -0.29261 | 0.16492 | 121.3309 | -0.12147 | 121.6655 | 121.5989 | 0.26805 | 0.018344 | -0.44547 | 121.8173 | 121.6007 | 122.0582 | 121.6155 | -0.12708 | 121.7718 | 121.9117 | 121.4478 | 121.6327 | -0.56243
1916.5781 | 122.0718 | -121.6278 | 0.32044 | 1.4211e-13 | -0.0097904 | -0.0028483 | 0.030219 | -0.01455 | 0.010525 | 0.0056466 | 0.0072744 | 0.0077131 | -0.0081657 | 0.041972 | 0.0026685 | 0.037675 | 0.005985 | 0.000747 | 0.21237 | 0.000359 | 0.44415 | 0.16131 | 0.051413 | 0.009516 | -0.010564 | 0.16234 | 0.30216 | -0.17539 | -0.28778 | 121.7891 | -0.10806 | 121.6655 | 121.6286 | -0.16056 | -0.32008 | 0.12372 | 121.34 | -0.15809 | 121.6792 | 121.6172 | 0.27721 | -0.018277 | -0.49583 | 121.8402 | 121.6282 | 122.072 | 121.6338 | -0.15913 | 121.7901 | 121.93 | 121.4524 | 121.6373 | -0.60821
1918.2656 | 121.9482 | -121.6827 | 0.34332 | 1.4211e-13 | -0.010004 | -0.0028483 | 0.029792 | -0.014123 | 0.010739 | -0.0019839 | 0.007488 | 0.0074993 | -0.0077383 | 0.041544 | 0.0028821 | 0.037675 | 0.001407 | 0.005325 | 0.19864 | -0.027115 | 0.44415 | 0.14757 | 0.046835 | 0.014095 | -0.015143 | 0.15318 | 0.29758 | -0.17539 | -0.2832 | 121.8303 | -0.14469 | 121.7204 | 121.6881 | -0.14225 | -0.37044 | 0.10083 | 121.3995 | -0.19014 | 121.7296 | 121.6676 | 0.26805 | -0.045743 | -0.51872 | 121.8814 | 121.6556 | 122.1269 | 121.6841 | -0.19575 | 121.8359 | 121.9803 | 121.5073 | 121.6968 | -0.62652
1920.0156 | 122.0627 | -121.6827 | 0.31128 | 1.4211e-13 | -0.0095768 | -0.0028483 | 0.029792 | -0.014337 | 0.010311 | 0.0056466 | 0.0072744 | 0.0079267 | -0.0077383 | 0.041758 | 0.0026685 | 0.037675 | 0.005985 | 0.009904 | 0.20321 | 0.014096 | 0.45789 | 0.15673 | 0.042256 | 0.009516 | -0.015143 | 0.15776 | 0.293 | -0.17539 | -0.27862 | 121.8395 | -0.10806 | 121.7204 | 121.6926 | -0.14683 | -0.29718 | 0.14661 | 121.4041 | -0.15351 | 121.725 | 121.6676 | 0.26348 | -0.018278 | -0.48667 | 121.886 | 121.6968 | 122.1406 | 121.6887 | -0.15455 | 121.8405 | 121.9757 | 121.5073 | 121.6923 | -0.5899
1921.7656 | 122.1222 | -121.6553 | 0.29755 | 1.4211e-13 | -0.010004 | -0.0032757 | 0.029792 | -0.014123 | 0.010311 | -0.0019839 | 0.0072744 | 0.0079267 | -0.0073111 | 0.041972 | 0.0028821 | 0.037675 | 0.005985 | 0.005325 | 0.20779 | -0.00422 | 0.43957 | 0.15215 | 0.046835 | 0.023253 | -0.010564 | 0.16234 | 0.30674 | -0.17081 | -0.2832 | 121.8074 | -0.089753 | 121.6929 | 121.6606 | -0.14683 | -0.30177 | 0.14203 | 121.3721 | -0.1352 | 121.7021 | 121.6447 | 0.27263 | 0.009191 | -0.46836 | 121.8631 | 121.6511 | 122.0948 | 121.6613 | -0.14539 | 121.8176 | 121.962 | 121.4845 | 121.6785 | -0.58074
1923.5156 | 122.1176 | -121.6415 | 0.27466 | 1.4211e-13 | -0.0097904 | -0.0028483 | 0.029792 | -0.01455 | 0.010525 | 0.0056466 | 0.0077016 | 0.0074993 | -0.0073111 | 0.042185 | 0.0026685 | 0.037675 | 0.001407 | 0.005325 | 0.20779 | 0.014096 | 0.45331 | 0.15215 | 0.046835 | 0.014095 | -0.019721 | 0.16234 | 0.28842 | -0.16624 | -0.28778 | 121.7937 | -0.066865 | 121.6792 | 121.6469 | -0.14683 | -0.26056 | 0.17865 | 121.3538 | -0.11232 | 121.6884 | 121.6218 | 0.26806 | 0.013765 | -0.44089 | 121.8493 | 121.6556 | 122.0949 | 121.6429 | -0.12251 | 121.8039 | 121.93 | 121.4753 | 121.6556 | -0.56244
1925.2031 | 121.9894 | -121.7331 | 0.3479 | 1.4211e-13 | -0.0097904 | -0.0026347 | 0.029792 | -0.014123 | 0.010311 | -0.0019839 | 0.007488 | 0.0077131 | -0.0077383 | 0.042399 | 0.0026685 | 0.042253 | 0.010564 | 0.009904 | 0.20779 | -0.036272 | 0.44873 | 0.15215 | 0.051413 | 0.014095 | -0.005985 | 0.15318 | 0.30216 | -0.16166 | -0.2832 | 121.8852 | -0.14011 | 121.7753 | 121.743 | -0.14225 | -0.38417 | 0.10083 | 121.4499 | -0.19471 | 121.7845 | 121.7271 | 0.27721 | -0.045742 | -0.50956 | 121.9409 | 121.6968 | 122.1818 | 121.7437 | -0.19575 | 121.8863 | 122.0353 | 121.5714 | 121.7472 | -0.6311
1926.9375 | 122.0947 | -121.6873 | 0.28839 | 1.4211e-13 | -0.0097904 | -0.0032757 | 0.030005 | -0.014123 | 0.010098 | -0.0019839 | 0.007488 | 0.0074993 | -0.0075247 | 0.042185 | 0.0028821 | 0.042253 | 0.010564 | 0.005325 | 0.19864 | -0.017957 | 0.44415 | 0.16131 | 0.046835 | 0.014095 | -0.015143 | 0.16234 | 0.30216 | -0.17081 | -0.2832 | 121.8486 | -0.089755 | 121.7296 | 121.6926 | -0.15599 | -0.30635 | 0.15576 | 121.4041 | -0.12605 | 121.7342 | 121.6722 | 0.26805 | 0.013767 | -0.45921 | 121.886 | 121.6694 | 122.1315 | 121.6979 | -0.12708 | 121.8497 | 121.9895 | 121.5165 | 121.7014 | -0.57159
1928.6875 | 122.1222 | -121.669 | 0.3067 | 1.4211e-13 | -0.010004 | -0.0026347 | 0.030005 | -0.014337 | 0.010739 | -0.0019839 | 0.007488 | 0.0077131 | -0.0075247 | 0.041972 | 0.0030959 | 0.033096 | 0.010564 | 0.000747 | 0.20321 | -0.054588 | 0.43957 | 0.16131 | 0.055992 | 0.009516 | -0.019721 | 0.16692 | 0.30674 | -0.17081 | -0.28778 | 121.8303 | -0.10349 | 121.7021 | 121.6698 | -0.16056 | -0.36129 | 0.13287 | 121.3812 | -0.13978 | 121.725 | 121.6493 | 0.26806 | 3.5e-05 | -0.47752 | 121.8722 | 121.6144 | 122.1086 | 121.6796 | -0.14539 | 121.8359 | 121.9757 | 121.4982 | 121.6785 | -0.59448
1930.4375 | 122.168 | -121.6736 | 0.30212 | 1.4211e-13 | -0.0097904 | -0.0030619 | 0.029792 | -0.014337 | 0.010311 | -0.0019839 | 0.007488 | 0.0077131 | -0.0075247 | 0.042185 | 0.0026685 | 0.037675 | 0.005985 | 0.000747 | 0.20321 | -0.031693 | 0.44873 | 0.15673 | 0.046835 | 0.014095 | -0.0243 | 0.16692 | 0.30216 | -0.17081 | -0.28778 | 121.8303 | -0.09891 | 121.7113 | 121.6743 | -0.15598 | -0.33382 | 0.14661 | 121.3858 | -0.1352 | 121.7204 | 121.6493 | 0.26348 | 3.4e-05 | -0.47294 | 121.8768 | 121.6419 | 122.1223 | 121.6796 | -0.14539 | 121.8405 | 121.9757 | 121.5028 | 121.6877 | -0.5899
1932.1406 | 122.168 | -121.7056 | 0.27924 | 1.4211e-13 | -0.0095768 | -0.0026347 | 0.029792 | -0.014123 | 0.010525 | 0.013277 | 0.0077016 | 0.0077131 | -0.0079521 | 0.042185 | 0.0024549 | 0.05141 | 0.005985 | 0.005325 | 0.20779 | -0.027115 | 0.44873 | 0.15673 | 0.046835 | 0.009516 | -0.010564 | 0.16234 | 0.30216 | -0.17081 | -0.28778 | 121.8624 | -0.071443 | 121.757 | 121.711 | -0.15141 | -0.30635 | 0.1695 | 121.4179 | -0.11689 | 121.7525 | 121.6951 | 0.27721 | 0.022922 | -0.45005 | 121.9134 | 121.6785 | 122.1544 | 121.7116 | -0.1225 | 121.868 | 122.0078 | 121.5348 | 121.7151 | -0.56701
1933.8906 | 122.0627 | -121.7331 | 0.31128 | 1.4211e-13 | -0.0095768 | -0.0026347 | 0.029578 | -0.013909 | 0.010525 | -0.0019839 | 0.007488 | 0.0074993 | -0.0077383 | 0.042185 | 0.0026685 | 0.042253 | 0.001407 | 0.005325 | 0.20779 | -0.017957 | 0.43957 | 0.15673 | 0.046835 | 0.009516 | -0.019721 | 0.16234 | 0.30216 | -0.16624 | -0.2832 | 121.8898 | -0.10349 | 121.7753 | 121.7384 | -0.15141 | -0.32924 | 0.1283 | 121.4499 | -0.14894 | 121.7799 | 121.7134 | 0.26348 | -0.009121 | -0.47751 | 121.9409 | 121.7151 | 122.1727 | 121.7345 | -0.15455 | 121.8954 | 122.0353 | 121.5669 | 121.7426 | -0.59448
1935.625 | 122.1313 | -121.7056 | 0.28839 | 1.4211e-13 | -0.0097904 | -0.0028483 | 0.030005 | -0.014337 | 0.010739 | 0.013277 | 0.0070608 | 0.0079267 | -0.0079521 | 0.041972 | 0.0030959 | 0.042253 | 0.005985 | 0.000747 | 0.19864 | 0.000359 | 0.44873 | 0.16131 | 0.046835 | 0.004938 | -0.019721 | 0.15776 | 0.30674 | -0.17081 | -0.27862 | 121.8669 | -0.089755 | 121.7479 | 121.7064 | -0.16056 | -0.28803 | 0.16034 | 121.427 | -0.13063 | 121.7525 | 121.6859 | 0.2589 | 0.018346 | -0.45921 | 121.9043 | 121.706 | 122.1544 | 121.7116 | -0.12708 | 121.8634 | 122.0124 | 121.5348 | 121.7106 | -0.56701
1937.375 | 122.1451 | -121.7056 | 0.28381 | 1.4211e-13 | -0.0097904 | -0.0026347 | 0.029792 | -0.013909 | 0.010525 | 0.013277 | 0.0072744 | 0.0079267 | -0.0075247 | 0.042399 | 0.0026685 | 0.033096 | 0.015142 | -0.003831 | 0.20321 | 0.050727 | 0.44873 | 0.14757 | 0.046835 | 0.014095 | -0.015143 | 0.15776 | 0.30216 | -0.17081 | -0.2832 | 121.8532 | -0.080599 | 121.7387 | 121.7018 | -0.1514 | -0.23309 | 0.16492 | 121.4224 | -0.12605 | 121.7525 | 121.6905 | 0.26805 | 0.018345 | -0.45463 | 121.9088 | 121.7564 | 122.1544 | 121.7208 | -0.13624 | 121.8634 | 122.0078 | 121.5348 | 121.7197 | -0.56701
1939.0625 | 122.0673 | -121.7422 | 0.33417 | 1.4211e-13 | -0.010004 | -0.0030619 | 0.029792 | -0.01455 | 0.010525 | -0.0019839 | 0.007488 | 0.0079267 | -0.0075247 | 0.041972 | 0.0026685 | 0.033096 | 0.005985 | -0.003831 | 0.19406 | 0.027833 | 0.44415 | 0.15215 | 0.046835 | 0.014095 | -0.019721 | 0.16234 | 0.29758 | -0.16624 | -0.28778 | 121.8944 | -0.14011 | 121.7753 | 121.7384 | -0.15598 | -0.30633 | 0.10999 | 121.4545 | -0.17183 | 121.7891 | 121.7225 | 0.26806 | -0.036587 | -0.5004 | 121.9363 | 121.7701 | 122.1864 | 121.7482 | -0.18201 | 121.9046 | 122.0398 | 121.576 | 121.7563 | -0.62194
1940.8125 | 122.1176 | -121.7377 | 0.32044 | 1.4211e-13 | -0.0095768 | -0.0026347 | 0.029792 | -0.014337 | 0.010525 | -0.017245 | 0.0072744 | 0.0077131 | -0.0077383 | 0.042399 | 0.0026685 | 0.033096 | 0.005985 | -0.003831 | 0.19864 | -0.031693 | 0.44873 | 0.15215 | 0.055992 | 0.014095 | -0.015143 | 0.16234 | 0.30216 | -0.17081 | -0.29236 | 121.8898 | -0.1218 | 121.7708 | 121.7338 | -0.15598 | -0.35213 | 0.1283 | 121.4453 | -0.15809 | 121.7937 | 121.7225 | 0.27721 | -0.018277 | -0.49125 | 121.9363 | 121.706 | 122.1864 | 121.7437 | -0.16828 | 121.9 | 122.0398 | 121.5669 | 121.7518 | -0.61279
1942.5625 | 122.1909 | -121.7331 | 0.28839 | 1.4211e-13 | -0.0097904 | -0.0028483 | 0.029792 | -0.014123 | 0.010525 | 0.020908 | 0.007488 | 0.0074993 | -0.0075247 | 0.042185 | 0.0028821 | 0.042253 | 0.005985 | -0.003831 | 0.19864 | -0.022536 | 0.44415 | 0.14757 | 0.051413 | 0.018674 | -0.019721 | 0.16692 | 0.31132 | -0.16166 | -0.27862 | 121.8807 | -0.089755 | 121.7753 | 121.7293 | -0.1514 | -0.31093 | 0.15576 | 121.4545 | -0.12147 | 121.7845 | 121.7134 | 0.2589 | 0.022925 | -0.45005 | 121.9317 | 121.7106 | 122.1772 | 121.7391 | -0.14082 | 121.9 | 122.0444 | 121.5714 | 121.7518 | -0.56701
1944.25 | 122.1909 | -121.7102 | 0.29297 | 1.4211e-13 | -0.0097904 | -0.0028483 | 0.029792 | -0.014123 | 0.010525 | 0.0056466 | 0.0077016 | 0.0077131 | -0.0077383 | 0.042185 | 0.0026685 | 0.037675 | 0.005985 | -0.008409 | 0.20779 | -0.00422 | 0.44873 | 0.15673 | 0.046835 | 0.009516 | -0.0243 | 0.16692 | 0.30674 | -0.16624 | -0.27862 | 121.8669 | -0.085176 | 121.7479 | 121.7018 | -0.16514 | -0.29719 | 0.15576 | 121.4316 | -0.12605 | 121.757 | 121.6859 | 0.25432 | 0.013768 | -0.4592 | 121.918 | 121.706 | 122.1589 | 121.7162 | -0.13624 | 121.8771 | 122.0169 | 121.544 | 121.7197 | -0.57159
1946.0156 | 122.1588 | -121.7422 | 0.29755 | 1.4211e-13 | -0.0093632 | -0.0026347 | 0.029792 | -0.014337 | 0.010525 | 0.0056466 | 0.0072744 | 0.0074993 | -0.0075247 | 0.042399 | 0.0028821 | 0.037675 | -0.003172 | -0.008409 | 0.20779 | -0.00422 | 0.44873 | 0.15673 | 0.046835 | 0.014095 | -0.015143 | 0.15776 | 0.30674 | -0.16624 | -0.28778 | 121.899 | -0.089753 | 121.7799 | 121.7338 | -0.16514 | -0.30177 | 0.15119 | 121.4545 | -0.13978 | 121.7891 | 121.7271 | 0.27263 | 0.009191 | -0.46378 | 121.95 | 121.738 | 122.191 | 121.7391 | -0.14081 | 121.9 | 122.049 | 121.576 | 121.7563 | -0.58532
1947.7188 | 122.113 | -121.7743 | 0.32501 | 1.4211e-13 | -0.010218 | -0.0030619 | 0.030005 | -0.014123 | 0.010739 | -0.0019839 | 0.006847 | 0.0081403 | -0.0079521 | 0.041972 | 0.0028821 | 0.037675 | 0.005985 | -0.017566 | 0.20779 | -0.017957 | 0.44415 | 0.16131 | 0.046835 | 0.018674 | -0.010564 | 0.16692 | 0.31132 | -0.17081 | -0.2832 | 121.9356 | -0.11722 | 121.812 | 121.7567 | -0.17888 | -0.34297 | 0.11914 | 121.4911 | -0.15809 | 121.8211 | 121.7637 | 0.27263 | -0.013696 | -0.49583 | 121.9821 | 121.7563 | 122.2184 | 121.7803 | -0.1637 | 121.9412 | 122.0856 | 121.6035 | 121.793 | -0.60821
1949.4531 | 122.1863 | -121.7651 | 0.28839 | 1.4211e-13 | -0.0095768 | -0.0030619 | 0.030005 | -0.014123 | 0.010525 | -0.0019839 | 0.007488 | 0.0079267 | -0.0075247 | 0.042185 | 0.0028821 | 0.037675 | 0.005985 | -0.012988 | 0.19406 | -0.017957 | 0.435 | 0.15673 | 0.046835 | 0.014095 | -0.019721 | 0.15776 | 0.293 | -0.17081 | -0.28778 | 121.9219 | -0.094333 | 121.8028 | 121.7521 | -0.16972 | -0.30635 | 0.14661 | 121.4774 | -0.13063 | 121.812 | 121.7454 | 0.26806 | 0.00461 | -0.45921 | 121.9592 | 121.7472 | 122.2001 | 121.7711 | -0.13166 | 121.9229 | 122.0581 | 121.5943 | 121.7792 | -0.57617
1951.2031 | 122.0764 | -121.8338 | 0.32044 | 1.4211e-13 | -0.0097904 | -0.0028483 | 0.029792 | -0.01455 | 0.010739 | -0.0019839 | 0.0077016 | 0.0077131 | -0.0077383 | 0.041972 | 0.0026685 | 0.037675 | 0.005985 | -0.012988 | 0.19864 | 0.000359 | 0.44873 | 0.15215 | 0.042256 | 0.014095 | -0.019721 | 0.16234 | 0.30216 | -0.17539 | -0.2832 | 121.986 | -0.1218 | 121.8715 | 121.8208 | -0.16514 | -0.32008 | 0.1283 | 121.5506 | -0.15809 | 121.8761 | 121.8141 | 0.26348 | -0.018277 | -0.49583 | 122.0324 | 121.8342 | 122.2825 | 121.8398 | -0.16828 | 121.9961 | 122.136 | 121.6584 | 121.8479 | -0.60363
1952.9531 | 122.2046 | -121.788 | 0.28839 | 1.4211e-13 | -0.010004 | -0.0028483 | 0.029792 | -0.014337 | 0.010525 | 0.013277 | 0.007488 | 0.0077131 | -0.0079521 | 0.042399 | 0.0026685 | 0.037675 | 0.001407 | -0.017566 | 0.20321 | -0.008799 | 0.44873 | 0.15673 | 0.046835 | 0.009516 | -0.015143 | 0.15776 | 0.29758 | -0.16624 | -0.2832 | 121.9448 | -0.085177 | 121.8257 | 121.7705 | -0.1743 | -0.29719 | 0.16034 | 121.5048 | -0.13063 | 121.8349 | 121.7729 | 0.26805 | 0.009189 | -0.45463 | 121.9912 | 121.7792 | 122.2368 | 121.7894 | -0.13166 | 121.9458 | 122.0856 | 121.6218 | 121.7975 | -0.57159
1954.6406 | 122.168 | -121.8018 | 0.32044 | 1.4211e-13 | -0.0097904 | -0.0026347 | 0.030219 | -0.013909 | 0.010525 | 0.020908 | 0.0072744 | 0.0081403 | -0.0079521 | 0.042399 | 0.0028821 | 0.042253 | 0.010564 | -0.008409 | 0.21237 | 0.032411 | 0.44415 | 0.15673 | 0.051413 | 0.009516 | -0.005985 | 0.15318 | 0.30674 | -0.17539 | -0.2832 | 121.9585 | -0.10806 | 121.844 | 121.7933 | -0.16514 | -0.28802 | 0.12372 | 121.5186 | -0.16725 | 121.8532 | 121.7958 | 0.27721 | -0.013698 | -0.49583 | 122.0141 | 121.8342 | 122.2459 | 121.8123 | -0.1637 | 121.9549 | 122.1085 | 121.6264 | 121.8113 | -0.60363
1956.4062 | 122.2321 | -121.7651 | 0.29755 | 1.4211e-13 | -0.0097904 | -0.0028483 | 0.030219 | -0.014123 | 0.010311 | -0.0019839 | 0.007488 | 0.0077131 | -0.0077383 | 0.042185 | 0.0026685 | 0.042253 | 0.001407 | -0.012988 | 0.19864 | -0.00422 | 0.44415 | 0.15673 | 0.046835 | 0.009516 | -0.015143 | 0.16234 | 0.293 | -0.17539 | -0.2832 | 121.9219 | -0.09891 | 121.8074 | 121.7521 | -0.16972 | -0.30177 | 0.14661 | 121.4819 | -0.1352 | 121.812 | 121.75 | 0.26805 | -0.004545 | -0.47294 | 121.9638 | 121.7609 | 122.2093 | 121.7665 | -0.14081 | 121.9275 | 122.0581 | 121.5897 | 121.7747 | -0.58074
1958.0938 | 122.1725 | -121.8292 | 0.31586 | 1.4211e-13 | -0.010004 | -0.0024209 | 0.030005 | -0.01455 | 0.010311 | 0.0056466 | 0.0072744 | 0.0074993 | -0.0079521 | 0.042399 | 0.0028821 | 0.042253 | 0.001407 | -0.003831 | 0.20321 | 0.08278 | 0.44873 | 0.14757 | 0.051413 | 0.014095 | -0.019721 | 0.16234 | 0.29758 | -0.17081 | -0.28778 | 121.9768 | -0.11264 | 121.8715 | 121.8254 | -0.1514 | -0.23308 | 0.13288 | 121.5414 | -0.15352 | 121.8806 | 121.8095 | 0.26806 | -0.018277 | -0.48667 | 122.0324 | 121.912 | 122.278 | 121.8306 | -0.16828 | 121.9916 | 122.1268 | 121.6584 | 121.8433 | -0.60363
1959.8438 | 122.1497 | -121.8201 | 0.31128 | 1.4211e-13 | -0.010004 | -0.0026347 | 0.030005 | -0.01455 | 0.010098 | 0.013277 | 0.0072744 | 0.0079267 | -0.0073111 | 0.042399 | 0.0028821 | 0.037675 | 0.001407 | -0.012988 | 0.20321 | -0.04543 | 0.44415 | 0.14757 | 0.046835 | 0.009516 | -0.010564 | 0.15776 | 0.30674 | -0.16624 | -0.28778 | 121.9676 | -0.10806 | 121.8577 | 121.8071 | -0.16056 | -0.35671 | 0.13288 | 121.5323 | -0.15351 | 121.8669 | 121.8095 | 0.27721 | -0.004542 | -0.47751 | 122.0233 | 121.7746 | 122.2642 | 121.8215 | -0.16371 | 121.9778 | 122.1268 | 121.6538 | 121.8296 | -0.59906
1961.6094 | 122.2504 | -121.8475 | 0.3067 | 1.4211e-13 | -0.0095768 | -0.0028483 | 0.030005 | -0.01455 | 0.010525 | -0.0019839 | 0.0072744 | 0.0074993 | -0.0077383 | 0.042399 | 0.0026685 | 0.037675 | 0.010564 | -0.008409 | 0.20321 | -0.059167 | 0.44415 | 0.15673 | 0.042256 | 0.014095 | -0.019721 | 0.15776 | 0.30674 | -0.16624 | -0.29236 | 122.0043 | -0.10349 | 121.8852 | 121.8391 | -0.16514 | -0.36587 | 0.13745 | 121.5552 | -0.14894 | 121.8898 | 121.8278 | 0.27264 | 3.5e-05 | -0.47294 | 122.0507 | 121.7884 | 122.2917 | 121.8581 | -0.14997 | 122.0053 | 122.1543 | 121.6813 | 121.8616 | -0.59906
1963.3594 | 122.1268 | -121.8567 | 0.32501 | 1.4211e-13 | -0.010218 | -0.0028483 | 0.030005 | -0.014337 | 0.010311 | 0.0056466 | 0.0072744 | 0.0079267 | -0.0079521 | 0.042185 | 0.0024549 | 0.037675 | 0.005985 | -0.012988 | 0.19864 | -0.054588 | 0.44873 | 0.15673 | 0.051413 | 0.009516 | -0.010564 | 0.15776 | 0.30216 | -0.17081 | -0.28778 | 122.0134 | -0.12638 | 121.8944 | 121.8437 | -0.16972 | -0.3796 | 0.12372 | 121.5689 | -0.16725 | 121.9081 | 121.8461 | 0.27721 | -0.022854 | -0.49583 | 122.0553 | 121.8021 | 122.3054 | 121.8627 | -0.16828 | 122.0145 | 122.1588 | 121.6859 | 121.8662 | -0.61279
1965.0469 | 122.2137 | -121.8521 | 0.30212 | 1.4211e-13 | -0.010004 | -0.0030619 | 0.029578 | -0.014337 | 0.010311 | 0.013277 | 0.007488 | 0.0074993 | -0.0077383 | 0.042399 | 0.0026685 | 0.037675 | 0.010564 | -0.008409 | 0.19864 | -0.054588 | 0.44873 | 0.15215 | 0.046835 | 0.014095 | -0.015143 | 0.16234 | 0.30216 | -0.17081 | -0.28778 | 122.0043 | -0.10349 | 121.8898 | 121.8437 | -0.16056 | -0.35671 | 0.14661 | 121.5643 | -0.13978 | 121.8989 | 121.837 | 0.27263 | 3.4e-05 | -0.47294 | 122.0507 | 121.7975 | 122.3008 | 121.8627 | -0.14997 | 122.0145 | 122.1543 | 121.6813 | 121.8662 | -0.5899
1966.7969 | 122.1405 | -121.8658 | 0.34332 | 1.4211e-13 | -0.010004 | -0.0032757 | 0.029792 | -0.014764 | 0.010311 | 0.0056466 | 0.0072744 | 0.0074993 | -0.0079521 | 0.042613 | 0.0024549 | 0.028518 | 0.005985 | 0.000747 | 0.19864 | -0.022536 | 0.44415 | 0.15673 | 0.046835 | 0.014095 | -0.015143 | 0.16234 | 0.30216 | -0.17081 | -0.2832 | 122.0226 | -0.14469 | 121.8944 | 121.8666 | -0.15598 | -0.36586 | 0.10083 | 121.5826 | -0.18098 | 121.9127 | 121.8507 | 0.26805 | -0.041165 | -0.51414 | 122.0645 | 121.8433 | 122.31 | 121.8718 | -0.18659 | 122.0282 | 122.168 | 121.695 | 121.8799 | -0.62652
1968.5469 | 122.1451 | -121.8979 | 0.33875 | 1.4211e-13 | -0.010218 | -0.0030619 | 0.030005 | -0.01455 | 0.010311 | 0.0056466 | 0.0072744 | 0.0077131 | -0.0077383 | 0.042185 | 0.0026685 | 0.042253 | 0.010564 | -0.017566 | 0.20321 | 0.023254 | 0.44415 | 0.16131 | 0.042256 | 0.014095 | -0.015143 | 0.16234 | 0.29758 | -0.17081 | -0.28778 | 122.0592 | -0.13553 | 121.9401 | 121.8803 | -0.17888 | -0.31549 | 0.10541 | 121.6101 | -0.1764 | 121.9401 | 121.8827 | 0.27263 | -0.041165 | -0.50956 | 122.1011 | 121.9211 | 122.342 | 121.9085 | -0.17744 | 122.0602 | 122.1955 | 121.7271 | 121.912 | -0.62652
1970.2188 | 122.2458 | -121.8384 | 0.3067 | 1.4211e-13 | -0.010004 | -0.0028483 | 0.030005 | -0.014337 | 0.010952 | 0.013277 | 0.007488 | 0.0074993 | -0.0079521 | 0.041972 | 0.0026685 | 0.033096 | 0.001407 | 0.000747 | 0.20321 | -0.027115 | 0.45331 | 0.15215 | 0.051413 | 0.009516 | -0.028879 | 0.16234 | 0.29758 | -0.17081 | -0.28778 | 121.9905 | -0.10349 | 121.8715 | 121.8391 | -0.15141 | -0.33382 | 0.14661 | 121.5506 | -0.14436 | 121.8898 | 121.8095 | 0.2589 | -0.009122 | -0.47752 | 122.0416 | 121.8113 | 122.2917 | 121.8398 | -0.15455 | 122.0007 | 122.136 | 121.6676 | 121.8479 | -0.59448
1971.9688 | 122.2 | -121.875 | 0.32044 | 1.4211e-13 | -0.010004 | -0.0028483 | 0.029792 | -0.014123 | 0.010311 | 0.0056466 | 0.0070608 | 0.0077131 | -0.0077383 | 0.042399 | 0.0028821 | 0.033096 | 0.001407 | -0.008409 | 0.19864 | -0.00422 | 0.45331 | 0.15215 | 0.046835 | 0.014095 | -0.015143 | 0.16234 | 0.29758 | -0.17539 | -0.28778 | 122.0272 | -0.1218 | 121.9081 | 121.8666 | -0.16056 | -0.32466 | 0.13288 | 121.5872 | -0.15809 | 121.9218 | 121.8599 | 0.27263 | -0.022855 | -0.49583 | 122.0736 | 121.8708 | 122.3283 | 121.8764 | -0.16828 | 122.0373 | 122.1726 | 121.6996 | 121.8891 | -0.60821
1973.6719 | 122.2046 | -121.8796 | 0.32501 | 1.4211e-13 | -0.010004 | -0.0030619 | 0.029792 | -0.01455 | 0.010525 | -0.0019839 | 0.0072744 | 0.0074993 | -0.0075247 | 0.042399 | 0.0030959 | 0.037675 | 0.005985 | -0.008409 | 0.20779 | 0.023254 | 0.45331 | 0.15215 | 0.042256 | 0.018674 | -0.015143 | 0.15318 | 0.293 | -0.17081 | -0.29236 | 122.0317 | -0.11722 | 121.9173 | 121.8712 | -0.16056 | -0.30176 | 0.1283 | 121.5872 | -0.17183 | 121.9218 | 121.8644 | 0.27721 | -0.032011 | -0.49583 | 122.0874 | 121.9028 | 122.3329 | 121.8856 | -0.17286 | 122.0328 | 122.1726 | 121.7088 | 121.8983 | -0.61737
1975.4375 | 122.2229 | -121.875 | 0.33417 | 1.4211e-13 | -0.010218 | -0.0028483 | 0.030005 | -0.014337 | 0.010098 | -0.0019839 | 0.0070608 | 0.0074993 | -0.0079521 | 0.042399 | 0.0028821 | 0.042253 | 0.005985 | -0.008409 | 0.19864 | -0.040851 | 0.44873 | 0.15673 | 0.051413 | 0.014095 | -0.019721 | 0.16234 | 0.293 | -0.17539 | -0.27862 | 122.0317 | -0.13553 | 121.9173 | 121.8666 | -0.16514 | -0.37502 | 0.11457 | 121.5964 | -0.17183 | 121.9264 | 121.8553 | 0.2589 | -0.041166 | -0.50956 | 122.0736 | 121.8341 | 122.3237 | 121.881 | -0.17744 | 122.0373 | 122.168 | 121.6996 | 121.8891 | -0.61279
1977.125 | 122.3145 | -121.8521 | 0.3067 | 1.4211e-13 | -0.010431 | -0.0030619 | 0.029792 | -0.01455 | 0.010311 | 0.0056466 | 0.007488 | 0.0077131 | -0.0075247 | 0.042399 | 0.0028821 | 0.042253 | 0.001407 | -0.012988 | 0.20779 | 0.03699 | 0.44415 | 0.15673 | 0.046835 | 0.018674 | -0.015143 | 0.16692 | 0.30674 | -0.17081 | -0.29236 | 122.0088 | -0.098909 | 121.8944 | 121.8391 | -0.16972 | -0.26971 | 0.13745 | 121.5598 | -0.13978 | 121.8989 | 121.837 | 0.27721 | 3.5e-05 | -0.47752 | 122.0599 | 121.8891 | 122.2963 | 121.8535 | -0.14997 | 122.019 | 122.1588 | 121.6813 | 121.8708 | -0.59906
1978.875 | 122.2275 | -121.875 | 0.32501 | 1.4211e-13 | -0.010431 | -0.0026347 | 0.030005 | -0.014764 | 0.010525 | -0.0096144 | 0.0072744 | 0.0077131 | -0.0079521 | 0.042399 | 0.0026685 | 0.037675 | 0.005985 | -0.003831 | 0.19864 | -0.008799 | 0.435 | 0.16131 | 0.046835 | 0.018674 | -0.019721 | 0.16692 | 0.30216 | -0.17081 | -0.28778 | 122.0363 | -0.12638 | 121.9127 | 121.8712 | -0.16514 | -0.33381 | 0.10998 | 121.5872 | -0.15809 | 121.9218 | 121.8553 | 0.26806 | -0.022854 | -0.49583 | 122.0736 | 121.8662 | 122.31 | 121.881 | -0.1637 | 122.0419 | 122.1772 | 121.7042 | 121.8937 | -0.61279
1980.625 | 122.1909 | -121.907 | 0.32044 | 1.4211e-13 | -0.010004 | -0.0026347 | 0.030005 | -0.014764 | 0.010098 | 0.0056466 | 0.0072744 | 0.0077131 | -0.0073111 | 0.042399 | 0.0024549 | 0.037675 | -0.003172 | -0.008409 | 0.19406 | 0.000359 | 0.44873 | 0.15215 | 0.051413 | 0.014095 | -0.015143 | 0.16692 | 0.30216 | -0.17081 | -0.2832 | 122.0592 | -0.12638 | 121.9447 | 121.8986 | -0.16056 | -0.32008 | 0.1283 | 121.6238 | -0.15351 | 121.9585 | 121.8919 | 0.26805 | -0.018277 | -0.49125 | 122.1011 | 121.9074 | 122.3558 | 121.9039 | -0.16828 | 122.074 | 122.2092 | 121.7362 | 121.9211 | -0.60363
1982.3281 | 122.1817 | -121.907 | 0.33417 | 1.4211e-13 | -0.010218 | -0.0028483 | 0.029578 | -0.014337 | 0.010525 | -0.0019839 | 0.0070608 | 0.0074993 | -0.0077383 | 0.042399 | 0.0024549 | 0.033096 | 0.005985 | -0.012988 | 0.20321 | -0.008799 | 0.44415 | 0.15673 | 0.046835 | 0.014095 | -0.010564 | 0.16692 | 0.29758 | -0.17081 | -0.28778 | 122.0638 | -0.13095 | 121.9401 | 121.8941 | -0.16972 | -0.34297 | 0.10999 | 121.6193 | -0.16725 | 121.9539 | 121.8965 | 0.27721 | -0.036587 | -0.50498 | 122.1103 | 121.8982 | 122.3512 | 121.913 | -0.17744 | 122.074 | 122.2046 | 121.7362 | 121.9211 | -0.62194
1984.0781 | 122.3419 | -121.8796 | 0.30212 | 1.4211e-13 | -0.010004 | -0.0028483 | 0.029792 | -0.014123 | 0.010311 | 0.013277 | 0.0079152 | 0.0074993 | -0.0079521 | 0.042399 | 0.0026685 | 0.037675 | 0.001407 | -0.003831 | 0.19864 | 0.018675 | 0.44415 | 0.15673 | 0.042256 | 0.018674 | -0.019721 | 0.16234 | 0.29758 | -0.16624 | -0.2832 | 122.0363 | -0.10349 | 121.9173 | 121.8757 | -0.16056 | -0.28345 | 0.14203 | 121.5964 | -0.13978 | 121.9218 | 121.8599 | 0.26348 | -0.004544 | -0.46836 | 122.0782 | 121.8983 | 122.3237 | 121.881 | -0.14539 | 122.0419 | 122.1772 | 121.7133 | 121.8983 | -0.58532
1985.8125 | 122.2092 | -121.8887 | 0.33417 | 1.4211e-13 | -0.010218 | -0.0028483 | 0.029792 | -0.01455 | 0.010311 | -0.0019839 | 0.0072744 | 0.0079267 | -0.0077383 | 0.042185 | 0.0024549 | 0.037675 | 0.010564 | -0.008409 | 0.20321 | -0.040851 | 0.44415 | 0.15215 | 0.042256 | 0.009516 | -0.015143 | 0.15776 | 0.30674 | -0.17081 | -0.2832 | 122.0409 | -0.13095 | 121.9264 | 121.8803 | -0.16056 | -0.37502 | 0.10999 | 121.6055 | -0.1764 | 121.931 | 121.8736 | 0.26805 | -0.02743 | -0.50498 | 122.0919 | 121.8479 | 122.3329 | 121.8993 | -0.18201 | 122.0465 | 122.1955 | 121.7179 | 121.8982 | -0.61736
1987.5 | 122.2504 | -121.9299 | 0.32501 | 1.4211e-13 | -0.010004 | -0.0026347 | 0.029792 | -0.01455 | 0.010525 | 0.0056466 | 0.0072744 | 0.0074993 | -0.0075247 | 0.042399 | 0.0024549 | 0.037675 | 0.001407 | -0.017566 | 0.20321 | -0.050009 | 0.43957 | 0.15673 | 0.046835 | 0.014095 | -0.019721 | 0.16234 | 0.29758 | -0.17539 | -0.2832 | 122.0867 | -0.1218 | 121.9676 | 121.9124 | -0.1743 | -0.37502 | 0.11456 | 121.6467 | -0.16267 | 121.9768 | 121.9102 | 0.26348 | -0.027432 | -0.5004 | 122.1331 | 121.8799 | 122.3695 | 121.9313 | -0.16828 | 122.0923 | 122.2275 | 121.7545 | 121.944 | -0.60821
1989.25 | 122.2366 | -121.8979 | 0.32044 | 1.4211e-13 | -0.010218 | -0.0026347 | 0.029578 | -0.014337 | 0.010525 | 0.0056466 | 0.007488 | 0.0077131 | -0.0077383 | 0.042613 | 0.0026685 | 0.033096 | 0.005985 | -0.017566 | 0.20321 | -0.00422 | 0.44873 | 0.14757 | 0.046835 | 0.009516 | -0.005985 | 0.16692 | 0.30216 | -0.17081 | -0.2832 | 122.0455 | -0.11722 | 121.931 | 121.8803 | -0.16514 | -0.32466 | 0.1283 | 121.6147 | -0.15351 | 121.9447 | 121.8919 | 0.27721 | -0.018277 | -0.49125 | 122.1011 | 121.8937 | 122.3466 | 121.9039 | -0.17286 | 122.0648 | 122.2 | 121.7271 | 121.9074 | -0.60363
1990.9375 | 122.2687 | -121.9162 | 0.32501 | 1.4211e-13 | -0.010218 | -0.0028483 | 0.029364 | -0.014337 | 0.010311 | -0.0096144 | 0.0072744 | 0.0077131 | -0.0073111 | 0.042613 | 0.0026685 | 0.033096 | 0.005985 | -0.012988 | 0.19864 | -0.008799 | 0.44873 | 0.15215 | 0.042256 | 0.014095 | -0.015143 | 0.16692 | 0.29758 | -0.17081 | -0.28778 | 122.0684 | -0.12638 | 121.9493 | 121.9032 | -0.16514 | -0.33381 | 0.12372 | 121.6284 | -0.15809 | 121.9585 | 121.9011 | 0.27263 | -0.027432 | -0.49583 | 122.1148 | 121.9074 | 122.3649 | 121.9222 | -0.17286 | 122.0831 | 122.2138 | 121.7454 | 121.9303 | -0.61279
1992.6875 | 122.3145 | -121.9254 | 0.30212 | 1.4211e-13 | -0.010004 | -0.0024209 | 0.030219 | -0.01455 | 0.010525 | -0.0019839 | 0.0072744 | 0.0077131 | -0.0077383 | 0.042399 | 0.0024549 | 0.042253 | -0.003172 | -0.008409 | 0.19864 | -0.063746 | 0.44873 | 0.15673 | 0.042256 | 0.009516 | -0.015143 | 0.16234 | 0.30216 | -0.17081 | -0.28778 | 122.0821 | -0.10349 | 121.9676 | 121.9169 | -0.16514 | -0.36587 | 0.14661 | 121.6376 | -0.13978 | 121.9676 | 121.9102 | 0.27263 | 3.4e-05 | -0.47294 | 122.124 | 121.8616 | 122.3741 | 121.9222 | -0.14539 | 122.0877 | 122.2275 | 121.7545 | 121.9349 | -0.5899
1994.4375 | 122.2412 | -121.9391 | 0.35248 | 1.4211e-13 | -0.010431 | -0.0028483 | 0.030005 | -0.014337 | 0.010098 | -0.0019839 | 0.0072744 | 0.0074993 | -0.0081657 | 0.042613 | 0.0028821 | 0.042253 | 0.001407 | -0.012988 | 0.21237 | -0.027115 | 0.44415 | 0.15673 | 0.051413 | 0.014095 | -0.015143 | 0.15776 | 0.30216 | -0.17081 | -0.2832 | 122.0958 | -0.14011 | 121.9813 | 121.9261 | -0.16972 | -0.37959 | 0.091676 | 121.6559 | -0.19471 | 121.9905 | 121.9239 | 0.26805 | -0.05032 | -0.52329 | 122.1515 | 121.912 | 122.3832 | 121.9405 | -0.19575 | 122.0969 | 122.2412 | 121.7683 | 121.9532 | -0.63568
1996.1406 | 122.2412 | -121.9666 | 0.34332 | 1.4211e-13 | -0.010218 | -0.0028483 | 0.029792 | -0.014123 | 0.010098 | 0.0056466 | 0.0072744 | 0.0077131 | -0.0077383 | 0.042613 | 0.0026685 | 0.046831 | -0.003172 | -0.017566 | 0.20779 | 0.055306 | 0.44415 | 0.15215 | 0.055992 | 0.018674 | -0.015143 | 0.16234 | 0.29758 | -0.17081 | -0.29236 | 122.1187 | -0.13553 | 122.0134 | 121.949 | -0.16972 | -0.28802 | 0.10083 | 121.6742 | -0.18098 | 122.0225 | 121.9514 | 0.27721 | -0.045743 | -0.51414 | 122.1743 | 122.0219 | 122.4107 | 121.9634 | -0.19117 | 122.1289 | 122.2641 | 121.7957 | 121.9852 | -0.63568
1997.8906 | 122.3648 | -121.875 | 0.28381 | 1.4211e-13 | -0.010218 | -0.0028483 | 0.029792 | -0.01455 | 0.010311 | 0.0056466 | 0.007488 | 0.0074993 | -0.0081657 | 0.042185 | 0.0026685 | 0.033096 | 0.005985 | -0.008409 | 0.20321 | -0.054588 | 0.44415 | 0.15215 | 0.046835 | 0.018674 | -0.019721 | 0.16234 | 0.30674 | -0.16624 | -0.28778 | 122.0272 | -0.080599 | 121.9081 | 121.8666 | -0.16056 | -0.3384 | 0.16034 | 121.5872 | -0.12147 | 121.9218 | 121.8553 | 0.26806 | 0.022924 | -0.45005 | 122.0782 | 121.8204 | 122.3192 | 121.881 | -0.13166 | 122.0373 | 122.1817 | 121.7088 | 121.8937 | -0.57159
1999.6406 | 122.2824 | -121.9482 | 0.33875 | 1.4211e-13 | -0.010218 | -0.0024209 | 0.029792 | -0.01455 | 0.010525 | 0.013277 | 0.007488 | 0.0072857 | -0.0079521 | 0.042613 | 0.0024549 | 0.042253 | 0.001407 | -0.012988 | 0.20321 | -0.00422 | 0.44415 | 0.15215 | 0.055992 | 0.018674 | -0.019721 | 0.16234 | 0.30216 | -0.17081 | -0.28778 | 122.1004 | -0.13553 | 121.9905 | 121.9353 | -0.16514 | -0.34297 | 0.10541 | 121.6605 | -0.1764 | 122.0042 | 121.9285 | 0.26806 | -0.036587 | -0.50956 | 122.1515 | 121.944 | 122.3924 | 121.9496 | -0.18659 | 122.1106 | 122.2504 | 121.7774 | 121.9669 | -0.62652
2001.3906 | 122.3328 | -121.9299 | 0.31128 | 1.4211e-13 | -0.010218 | -0.0028483 | 0.029792 | -0.014337 | 0.010098 | 0.013277 | 0.007488 | 0.0072857 | -0.0075247 | 0.042399 | 0.0026685 | 0.042253 | 0.010564 | -0.022144 | 0.20321 | 0.000359 | 0.43957 | 0.15673 | 0.042256 | 0.014095 | -0.019721 | 0.16234 | 0.29758 | -0.17081 | -0.29236 | 122.0867 | -0.10806 | 121.9722 | 121.9078 | -0.17888 | -0.31092 | 0.1283 | 121.6376 | -0.14894 | 121.9722 | 121.9102 | 0.27264 | -0.013699 | -0.48209 | 122.1331 | 121.9303 | 122.3695 | 121.9405 | -0.15455 | 122.0923 | 122.2275 | 121.7591 | 121.944 | -0.60363
2003.0781 | 122.3053 | -121.962 | 0.33875 | 1.4211e-13 | -0.010004 | -0.0030619 | 0.029792 | -0.01455 | 0.010311 | 0.0056466 | 0.0072744 | 0.0077131 | -0.0075247 | 0.042827 | 0.0028821 | 0.042253 | 0.005985 | -0.012988 | 0.19864 | 0.014096 | 0.44873 | 0.14757 | 0.046835 | 0.014095 | -0.015143 | 0.15776 | 0.30216 | -0.16624 | -0.27862 | 122.1095 | -0.14011 | 122.0042 | 121.949 | -0.16056 | -0.32465 | 0.10999 | 121.6834 | -0.18098 | 122.0088 | 121.9468 | 0.26348 | -0.036587 | -0.50498 | 122.1606 | 121.9761 | 122.4107 | 121.968 | -0.19117 | 122.1197 | 122.2641 | 121.7957 | 121.9761 | -0.61736
2004.8281 | 122.2916 | -121.9757 | 0.33417 | 1.4211e-13 | -0.010218 | -0.0026347 | 0.030005 | -0.014337 | 0.010098 | 0.0056466 | 0.007488 | 0.0081403 | -0.0079521 | 0.042399 | 0.0026685 | 0.042253 | 0.005985 | -0.017566 | 0.19864 | -0.063746 | 0.44873 | 0.15215 | 0.042256 | 0.018674 | -0.019721 | 0.15776 | 0.30216 | -0.17081 | -0.2832 | 122.1279 | -0.13553 | 122.018 | 121.9581 | -0.16972 | -0.39791 | 0.11457 | 121.6925 | -0.1764 | 122.018 | 121.956 | 0.26348 | -0.032009 | -0.50498 | 122.1743 | 121.912 | 122.4244 | 121.9817 | -0.18201 | 122.1335 | 122.2779 | 121.8049 | 121.9944 | -0.61736
2006.5312 | 122.2687 | -121.9711 | 0.33417 | 1.4211e-13 | -0.010218 | -0.0030619 | 0.030005 | -0.014337 | 0.010311 | -0.0019839 | 0.007488 | 0.0072857 | -0.0081657 | 0.042185 | 0.0024549 | 0.037675 | 0.001407 | -0.026723 | 0.20321 | 0.014096 | 0.44415 | 0.15215 | 0.037677 | 0.009516 | -0.015143 | 0.15318 | 0.30674 | -0.17081 | -0.29236 | 122.1233 | -0.13095 | 122.0088 | 121.9444 | -0.17888 | -0.32007 | 0.10999 | 121.6788 | -0.18098 | 122.0088 | 121.956 | 0.27721 | -0.02743 | -0.50498 | 122.1743 | 121.9852 | 122.4153 | 121.9725 | -0.18201 | 122.1243 | 122.2779 | 121.8003 | 121.9806 | -0.62652
2008.2969 | 122.3145 | -121.9711 | 0.31128 | 1.4211e-13 | -0.010004 | -0.0032757 | 0.029792 | -0.014764 | 0.010311 | 0.0056466 | 0.0070608 | 0.0079267 | -0.0077383 | 0.042613 | 0.0022413 | 0.037675 | 0.001407 | -0.012988 | 0.19864 | -0.013378 | 0.44415 | 0.15673 | 0.051413 | 0.018674 | -0.015143 | 0.16692 | 0.30216 | -0.17539 | -0.28778 | 122.1279 | -0.11264 | 122.0088 | 121.9581 | -0.16972 | -0.32466 | 0.13288 | 121.6834 | -0.14436 | 122.0225 | 121.956 | 0.27263 | -0.009121 | -0.48667 | 122.1698 | 121.9578 | 122.4153 | 121.9725 | -0.15455 | 122.1381 | 122.2733 | 121.7957 | 121.9898 | -0.59906
2010.0469 | 122.3099 | -121.9849 | 0.32044 | 1.4211e-13 | -0.010004 | -0.0028483 | 0.029792 | -0.014337 | 0.010098 | 0.0056466 | 0.0072744 | 0.0077131 | -0.0077383 | 0.042399 | 0.0024549 | 0.042253 | 0.005985 | -0.026723 | 0.19864 | -0.027115 | 0.44873 | 0.15673 | 0.042256 | 0.018674 | -0.015143 | 0.16692 | 0.30216 | -0.16624 | -0.29236 | 122.1416 | -0.1218 | 122.0271 | 121.9581 | -0.18345 | -0.34755 | 0.1283 | 121.6925 | -0.15351 | 122.0271 | 121.9697 | 0.27721 | -0.018277 | -0.48667 | 122.1835 | 121.9577 | 122.4336 | 121.9908 | -0.1637 | 122.1518 | 122.287 | 121.8186 | 122.0035 | -0.61279
2011.7969 | 122.287 | -122.0215 | 0.33875 | 1.4211e-13 | -0.010431 | -0.0030619 | 0.029578 | -0.014337 | 0.0098841 | -0.0019839 | 0.0070608 | 0.0077131 | -0.0079521 | 0.042399 | 0.0022413 | 0.042253 | -0.003172 | -0.017566 | 0.20321 | -0.022536 | 0.45331 | 0.15673 | 0.046835 | 0.014095 | -0.019721 | 0.15776 | 0.31132 | -0.16624 | -0.2832 | 122.1782 | -0.13553 | 122.0637 | 122.0039 | -0.1743 | -0.36128 | 0.11457 | 121.7383 | -0.18098 | 122.0683 | 122.0018 | 0.26348 | -0.027429 | -0.50498 | 122.2247 | 121.9989 | 122.4748 | 122.0183 | -0.18201 | 122.1792 | 122.3328 | 121.8552 | 122.0356 | -0.62194
2013.4844 | 122.3557 | -121.9711 | 0.29755 | 1.4211e-13 | -0.010431 | -0.0028483 | 0.029792 | -0.014337 | 0.010525 | -0.0019839 | 0.007488 | 0.0074993 | -0.0079521 | 0.042399 | 0.0024549 | 0.046831 | -0.003172 | -0.017566 | 0.20321 | 0.041569 | 0.44873 | 0.14299 | 0.046835 | 0.014095 | -0.010564 | 0.1715 | 0.30674 | -0.16624 | -0.2832 | 122.1141 | -0.094332 | 122.018 | 121.9536 | -0.16056 | -0.25598 | 0.15119 | 121.6879 | -0.12605 | 122.018 | 121.9606 | 0.27263 | 0.009191 | -0.46378 | 122.1743 | 122.0127 | 122.4199 | 121.968 | -0.15455 | 122.1426 | 122.2779 | 121.8049 | 121.9852 | -0.58074
2015.2344 | 122.4197 | -121.9666 | 0.29297 | 1.4211e-13 | -0.010004 | -0.0028483 | 0.029578 | -0.01455 | 0.010525 | 0.0056466 | 0.0072744 | 0.0074993 | -0.0079521 | 0.042399 | 0.0026685 | 0.042253 | 0.005985 | -0.008409 | 0.20321 | 0.03699 | 0.45331 | 0.15673 | 0.051413 | 0.014095 | -0.005985 | 0.15318 | 0.30216 | -0.17081 | -0.2832 | 122.1233 | -0.089755 | 122.0088 | 121.9581 | -0.16514 | -0.25598 | 0.16034 | 121.6834 | -0.13978 | 122.018 | 121.9606 | 0.27721 | 0.009189 | -0.46378 | 122.1698 | 122.0035 | 122.4199 | 121.9725 | -0.13624 | 122.1197 | 122.2687 | 121.7957 | 121.9806 | -0.57617
2017 | 122.4152 | -121.9803 | 0.28839 | 1.4211e-13 | -0.010218 | -0.0030619 | 0.029578 | -0.014337 | 0.010525 | 0.0056466 | 0.007488 | 0.0079267 | -0.0079521 | 0.042613 | 0.0024549 | 0.042253 | 0.010564 | -0.012988 | 0.20321 | 0.055306 | 0.44873 | 0.16131 | 0.042256 | 0.014095 | -0.015143 | 0.16234 | 0.29758 | -0.17539 | -0.29236 | 122.1416 | -0.085177 | 122.0225 | 121.9673 | -0.1743 | -0.23309 | 0.16034 | 121.6879 | -0.12605 | 122.0225 | 121.9651 | 0.27721 | 0.009189 | -0.46378 | 122.1835 | 122.0356 | 122.429 | 121.9909 | -0.12708 | 122.1426 | 122.2779 | 121.8049 | 121.9944 | -0.58075
2018.7031 | 122.4197 | -121.9849 | 0.31128 | 1.4211e-13 | -0.010004 | -0.0030619 | 0.029578 | -0.01455 | 0.010525 | -0.0096144 | 0.0072744 | 0.0077131 | -0.0077383 | 0.042613 | 0.0022413 | 0.037675 | 0.005985 | -0.012988 | 0.21237 | -0.00422 | 0.44415 | 0.15673 | 0.046835 | 0.009516 | -0.015143 | 0.16692 | 0.293 | -0.17997 | -0.2832 | 122.1416 | -0.098908 | 122.0225 | 121.9719 | -0.16972 | -0.3155 | 0.13288 | 121.7017 | -0.14436 | 122.0317 | 121.9697 | 0.26805 | -0.018278 | -0.49125 | 122.1972 | 121.9806 | 122.429 | 121.9908 | -0.15455 | 122.1518 | 122.2779 | 121.8049 | 121.9944 | -0.59448
2020.4531 | 122.1817 | -122.113 | 0.25177 | 1.4211e-13 | -0.010218 | -0.0024209 | 0.029792 | -0.014337 | 0.010311 | -0.0019839 | 0.0072744 | 0.0077131 | -0.0077383 | 0.042827 | 0.0022413 | 0.023939 | -0.007751 | -0.022144 | 0.18948 | 0.018675 | 0.44415 | 0.16131 | 0.037677 | 0.009516 | -0.015143 | 0.15776 | 0.30216 | -0.17081 | -0.28778 | 122.2743 | -0.062291 | 122.137 | 122.0909 | -0.18345 | -0.23309 | 0.19238 | 121.8253 | -0.094006 | 122.1507 | 122.0979 | 0.27263 | 0.050388 | -0.42258 | 122.3025 | 122.1317 | 122.5572 | 122.1053 | -0.09046 | 122.2708 | 122.4152 | 121.9422 | 122.1226 | -0.53955
2022.1406 | 122.2916 | -122.0947 | 0.22888 | 1.4211e-13 | -0.010218 | -0.0032757 | 0.029792 | -0.014337 | 0.010098 | -0.0096144 | 0.007488 | 0.0077131 | -0.0079521 | 0.042613 | 0.0024549 | 0.028518 | -0.007751 | -0.026723 | 0.19406 | -0.068325 | 0.44873 | 0.15215 | 0.037677 | 0.014095 | -0.015143 | 0.16234 | 0.30216 | -0.16624 | -0.29236 | 122.2469 | -0.034824 | 122.1232 | 122.068 | -0.17888 | -0.29721 | 0.21985 | 121.8024 | -0.06654 | 122.1324 | 122.0796 | 0.27721 | 0.073276 | -0.39512 | 122.2888 | 122.0264 | 122.5435 | 122.087 | -0.07673 | 122.2571 | 122.3969 | 121.9285 | 122.1088 | -0.52124
2023.9062 | 122.4106 | -122.0581 | 0.19684 | 1.4211e-13 | -0.010004 | -0.0028483 | 0.029578 | -0.01455 | 0.010525 | 0.0056466 | 0.0077016 | 0.0074993 | -0.0079521 | 0.042399 | 0.0022413 | 0.037675 | 0.001407 | -0.017566 | 0.20779 | -0.022536 | 0.43957 | 0.15673 | 0.046835 | 0.014095 | -0.010564 | 0.15776 | 0.30216 | -0.17539 | -0.28778 | 122.2148 | 0.010955 | 122.0958 | 122.0405 | -0.1743 | -0.21937 | 0.24274 | 121.7703 | -0.039074 | 122.1049 | 122.0475 | 0.27721 | 0.10532 | -0.37223 | 122.2659 | 122.0356 | 122.4977 | 122.0595 | -0.040107 | 122.2159 | 122.3603 | 121.8827 | 122.0722 | -0.48462
2025.6562 | 122.4106 | -122.0856 | 0.20599 | 1.4211e-13 | -0.010004 | -0.0026347 | 0.030005 | -0.014337 | 0.0098841 | -0.0019839 | 0.007488 | 0.0077131 | -0.0077383 | 0.042613 | 0.0026685 | 0.037675 | 0.001407 | -0.008409 | 0.20321 | -0.054588 | 0.45331 | 0.16131 | 0.046835 | 0.009516 | -0.015143 | 0.15318 | 0.30674 | -0.17539 | -0.28778 | 122.2469 | -0.00278 | 122.1232 | 122.0772 | -0.16972 | -0.26058 | 0.24732 | 121.7978 | -0.052809 | 122.1324 | 122.0704 | 0.27263 | 0.10074 | -0.38139 | 122.2888 | 122.031 | 122.5389 | 122.087 | -0.044684 | 122.2388 | 122.3923 | 121.9102 | 122.0951 | -0.49377
2027.3438 | 122.4472 | -122.0535 | 0.21973 | 1.4211e-13 | -0.010218 | -0.0028483 | 0.029792 | -0.01455 | 0.010098 | 0.0056466 | 0.007488 | 0.0079267 | -0.0075247 | 0.042613 | 0.0026685 | 0.037675 | 0.005985 | -0.017566 | 0.20779 | -0.050009 | 0.44873 | 0.14757 | 0.042256 | 0.009516 | -0.010564 | 0.16692 | 0.30674 | -0.17081 | -0.29236 | 122.2011 | -0.011934 | 122.0912 | 122.036 | -0.16514 | -0.26974 | 0.22901 | 121.7612 | -0.052806 | 122.0958 | 122.043 | 0.28179 | 0.08701 | -0.39054 | 122.2613 | 122.0035 | 122.5023 | 122.0595 | -0.072154 | 122.2204 | 122.3603 | 121.8827 | 122.063 | -0.51208
2029.0781 | 122.3145 | -122.1542 | 0.22888 | 1.4211e-13 | -0.010431 | -0.0034893 | 0.029792 | -0.014337 | 0.010098 | -0.0019839 | 0.0072744 | 0.0077131 | -0.0081657 | 0.042613 | 0.0026685 | 0.033096 | 0.001407 | -0.012988 | 0.19864 | 0.009517 | 0.45331 | 0.15215 | 0.037677 | 0.014095 | -0.015143 | 0.15318 | 0.30216 | -0.17081 | -0.29693 | 122.3064 | -0.030246 | 122.1873 | 122.1412 | -0.16514 | -0.21937 | 0.22443 | 121.8573 | -0.075697 | 122.1919 | 122.1391 | 0.28179 | 0.073276 | -0.3997 | 122.3529 | 122.1638 | 122.6075 | 122.1556 | -0.07673 | 122.3074 | 122.4564 | 121.9834 | 122.1683 | -0.52582
2030.8281 | 122.3236 | -122.1222 | 0.22888 | 1.4211e-13 | -0.010218 | -0.0028483 | 0.030005 | -0.01455 | 0.010525 | 0.0056466 | 0.0079152 | 0.0074993 | -0.0077383 | 0.042613 | 0.0022413 | 0.028518 | 0.001407 | -0.012988 | 0.20321 | 0.004938 | 0.44415 | 0.15673 | 0.046835 | 0.004938 | -0.015143 | 0.15776 | 0.30674 | -0.17081 | -0.28778 | 122.2789 | -0.025668 | 122.1507 | 122.1092 | -0.16972 | -0.22394 | 0.21527 | 121.8344 | -0.071118 | 122.169 | 122.107 | 0.27263 | 0.077855 | -0.3997 | 122.3254 | 122.1271 | 122.5663 | 122.1236 | -0.072151 | 122.28 | 122.4289 | 121.9514 | 122.1271 | -0.51666
2032.5781 | 122.319 | -122.1405 | 0.23804 | 1.4211e-13 | -0.010431 | -0.0026347 | 0.029578 | -0.014764 | 0.010098 | 0.020908 | 0.0070608 | 0.0074993 | -0.0079521 | 0.042613 | 0.0026685 | 0.042253 | 0.010564 | -0.017566 | 0.20779 | -0.008799 | 0.43957 | 0.15215 | 0.051413 | 0.014095 | -0.010564 | 0.16234 | 0.29758 | -0.17081 | -0.28778 | 122.2927 | -0.030244 | 122.1828 | 122.1229 | -0.16972 | -0.24684 | 0.20154 | 121.8527 | -0.075695 | 122.1919 | 122.1299 | 0.27721 | 0.059543 | -0.40885 | 122.3483 | 122.1317 | 122.5801 | 122.1511 | -0.085885 | 122.3028 | 122.4381 | 121.9697 | 122.1546 | -0.52581
2034.3281 | 122.4518 | -122.1039 | 0.19684 | 1.4211e-13 | -0.010004 | -0.0026347 | 0.029792 | -0.01455 | 0.010525 | -0.0019839 | 0.0070608 | 0.0077131 | -0.0079521 | 0.042827 | 0.0026685 | 0.037675 | -0.007751 | -0.012988 | 0.20321 | 0.014096 | 0.44873 | 0.15215 | 0.037677 | 0.009516 | -0.019721 | 0.15776 | 0.29758 | -0.16624 | -0.28778 | 122.256 | 0.006376 | 122.1416 | 122.0909 | -0.16514 | -0.18274 | 0.25189 | 121.8161 | -0.039074 | 122.1416 | 122.0842 | 0.26806 | 0.10074 | -0.36307 | 122.3071 | 122.118 | 122.5526 | 122.0961 | -0.044686 | 122.2616 | 122.4015 | 121.9376 | 122.1134 | -0.48462
2036.0156 | 122.374 | -122.1359 | 0.21057 | 1.4211e-13 | -0.010218 | -0.0028483 | 0.030005 | -0.014337 | 0.010311 | 0.013277 | 0.007488 | 0.0079267 | -0.0075247 | 0.042613 | 0.0024549 | 0.028518 | 0.001407 | -0.026723 | 0.19864 | 0.000359 | 0.43957 | 0.15673 | 0.046835 | 0.004938 | -0.019721 | 0.16234 | 0.30216 | -0.17081 | -0.28778 | 122.2927 | -0.011935 | 122.1644 | 122.1092 | -0.18345 | -0.21021 | 0.229 | 121.8481 | -0.048229 | 122.1828 | 122.1162 | 0.26806 | 0.091587 | -0.38139 | 122.3346 | 122.1363 | 122.5755 | 122.1373 | -0.05384 | 122.2983 | 122.4381 | 121.9651 | 122.1409 | -0.49835
2037.7656 | 122.4472 | -122.1268 | 0.21973 | 1.4211e-13 | -0.010004 | -0.0028483 | 0.030005 | -0.014337 | 0.010311 | -0.0019839 | 0.0072744 | 0.0077131 | -0.0077383 | 0.042613 | 0.0028821 | 0.037675 | 0.001407 | -0.003831 | 0.20779 | -0.027115 | 0.44873 | 0.16131 | 0.046835 | 0.004938 | -0.019721 | 0.15776 | 0.30674 | -0.16624 | -0.28778 | 122.2881 | -0.011934 | 122.1644 | 122.1229 | -0.16514 | -0.24684 | 0.22901 | 121.839 | -0.061963 | 122.1736 | 122.107 | 0.26806 | 0.08701 | -0.38596 | 122.3346 | 122.0997 | 122.5755 | 122.1282 | -0.058417 | 122.2845 | 122.4335 | 121.9605 | 122.1317 | -0.5075
2039.4531 | 122.374 | -122.1222 | 0.2243 | 1.4211e-13 | -0.010431 | -0.0030619 | 0.029792 | -0.014123 | 0.010098 | 0.0056466 | 0.0070608 | 0.0074993 | -0.0079521 | 0.042613 | 0.0026685 | 0.033096 | -0.003172 | -0.008409 | 0.19864 | 0.014096 | 0.44873 | 0.15215 | 0.046835 | 0.004938 | -0.019721 | 0.15776 | 0.30216 | -0.17539 | -0.29693 | 122.2743 | -0.025668 | 122.1553 | 122.1138 | -0.16056 | -0.21021 | 0.22443 | 121.8253 | -0.06654 | 122.169 | 122.1025 | 0.27721 | 0.077854 | -0.3997 | 122.3208 | 122.1363 | 122.5709 | 122.119 | -0.072152 | 122.28 | 122.4244 | 121.9468 | 122.1271 | -0.52124
2041.2031 | 122.3785 | -122.1542 | 0.22888 | 1.4211e-13 | -0.010218 | -0.0028483 | 0.029792 | -0.01455 | 0.010311 | 0.013277 | 0.0066334 | 0.0079267 | -0.0075247 | 0.042827 | 0.0024549 | 0.037675 | 0.001407 | -0.012988 | 0.19406 | -0.017957 | 0.44415 | 0.15215 | 0.042256 | 0.014095 | -0.015143 | 0.15776 | 0.30216 | -0.17081 | -0.29236 | 122.3064 | -0.034824 | 122.1919 | 122.1412 | -0.16514 | -0.24684 | 0.21527 | 121.8619 | -0.071118 | 122.1965 | 122.1391 | 0.27721 | 0.073276 | -0.3997 | 122.3483 | 122.1363 | 122.5984 | 122.1556 | -0.07673 | 122.312 | 122.4564 | 121.9834 | 122.1683 | -0.52124
2042.9531 | 122.3831 | -122.1725 | 0.2243 | 1.4211e-13 | -0.010218 | -0.0028483 | 0.029792 | -0.01455 | 0.010311 | -0.0019839 | 0.0072744 | 0.0077131 | -0.0079521 | 0.042613 | 0.0022413 | 0.037675 | -0.003172 | -0.022144 | 0.19864 | -0.008799 | 0.44415 | 0.16131 | 0.037677 | 0.014095 | -0.019721 | 0.16234 | 0.293 | -0.17539 | -0.28778 | 122.3339 | -0.025668 | 122.2102 | 122.1504 | -0.18345 | -0.2331 | 0.21985 | 121.8848 | -0.061962 | 122.2102 | 122.1528 | 0.26806 | 0.068697 | -0.3997 | 122.3712 | 122.1637 | 122.6167 | 122.1694 | -0.062994 | 122.3349 | 122.4655 | 121.9972 | 122.1866 | -0.51208
2044.7031 | 122.3557 | -122.1863 | 0.24261 | 1.4211e-13 | -0.010004 | -0.0028483 | 0.030005 | -0.014764 | 0.010311 | -0.0019839 | 0.007488 | 0.0077131 | -0.0077383 | 0.042185 | 0.0026685 | 0.037675 | 0.001407 | -0.008409 | 0.20321 | 0.023254 | 0.44873 | 0.16131 | 0.046835 | 0.014095 | -0.019721 | 0.15776 | 0.29758 | -0.17081 | -0.2832 | 122.3476 | -0.039401 | 122.224 | 122.1779 | -0.16972 | -0.21936 | 0.20612 | 121.9031 | -0.084851 | 122.2331 | 122.1666 | 0.26348 | 0.054965 | -0.41343 | 122.3895 | 122.2095 | 122.635 | 122.1877 | -0.081305 | 122.344 | 122.4839 | 122.0155 | 122.2004 | -0.52581
2046.3906 | 122.3557 | -122.1909 | 0.21515 | 1.4211e-13 | -0.0095768 | -0.0028483 | 0.029792 | -0.014337 | 0.010098 | -0.0019839 | 0.0070608 | 0.0074993 | -0.0079521 | 0.042827 | 0.0024549 | 0.023939 | 0.005985 | -0.017566 | 0.19864 | -0.054588 | 0.45331 | 0.15673 | 0.046835 | 0.014095 | -0.019721 | 0.14861 | 0.30674 | -0.17081 | -0.29236 | 122.3476 | -0.016513 | 122.2148 | 122.1733 | -0.1743 | -0.26974 | 0.23816 | 121.8985 | -0.066542 | 122.2377 | 122.1711 | 0.27264 | 0.091588 | -0.38596 | 122.3895 | 122.1363 | 122.6442 | 122.1968 | -0.058418 | 122.3395 | 122.4976 | 122.02 | 122.205 | -0.5075
2048.1406 | 122.5067 | -122.1405 | 0.20142 | 1.4211e-13 | -0.010218 | -0.0028483 | 0.030005 | -0.01455 | 0.010311 | 0.0056466 | 0.0072744 | 0.0077131 | -0.0077383 | 0.042613 | 0.0024549 | 0.037675 | 0.001407 | -0.012988 | 0.19864 | -0.027115 | 0.44415 | 0.15673 | 0.051413 | 0.014095 | -0.0243 | 0.16234 | 0.29758 | -0.16166 | -0.29236 | 122.2972 | -0.00278 | 122.1782 | 122.1275 | -0.16972 | -0.22853 | 0.24274 | 121.8481 | -0.039074 | 122.1919 | 122.1162 | 0.26806 | 0.096164 | -0.36307 | 122.3391 | 122.1134 | 122.5847 | 122.1419 | -0.044685 | 122.3028 | 122.4381 | 121.9788 | 122.1546 | -0.49377
2049.8281 | 122.3694 | -122.1909 | 0.22888 | 1.4211e-13 | -0.010218 | -0.0026347 | 0.029578 | -0.014337 | 0.010311 | -0.0019839 | 0.0072744 | 0.0077131 | -0.0077383 | 0.042399 | 0.0024549 | 0.037675 | 0.001407 | -0.003831 | 0.19864 | -0.017957 | 0.44873 | 0.15673 | 0.042256 | 0.009516 | -0.028879 | 0.16234 | 0.30216 | -0.16624 | -0.28778 | 122.3476 | -0.030246 | 122.2285 | 122.187 | -0.16056 | -0.24684 | 0.21985 | 121.9031 | -0.06654 | 122.2331 | 122.162 | 0.2589 | 0.073276 | -0.39512 | 122.3895 | 122.1729 | 122.6396 | 122.1923 | -0.072151 | 122.3532 | 122.493 | 122.0246 | 122.2004 | -0.51666
2051.5781 | 122.4472 | -122.1451 | 0.21057 | 1.4211e-13 | -0.010004 | -0.0028483 | 0.029792 | -0.01455 | 0.010525 | -0.0019839 | 0.0072744 | 0.0074993 | -0.0081657 | 0.042613 | 0.0026685 | 0.042253 | -0.003172 | -0.012988 | 0.19406 | -0.036272 | 0.44415 | 0.15673 | 0.046835 | 0.014095 | -0.015143 | 0.15318 | 0.29758 | -0.17081 | -0.28778 | 122.3018 | -0.016513 | 122.1873 | 122.1321 | -0.16972 | -0.24684 | 0.23358 | 121.8573 | -0.057386 | 122.1919 | 122.1299 | 0.27263 | 0.087009 | -0.38139 | 122.3391 | 122.1088 | 122.5892 | 122.1419 | -0.05384 | 122.2983 | 122.4427 | 121.9743 | 122.1592 | -0.49835
2053.3281 | 122.4838 | -122.1771 | 0.20599 | 1.4211e-13 | -0.010004 | -0.0028483 | 0.029578 | -0.01455 | 0.010311 | 0.0056466 | 0.0070608 | 0.0077131 | -0.0079521 | 0.042399 | 0.0026685 | 0.037675 | -0.003172 | -0.012988 | 0.19864 | 0.046148 | 0.44415 | 0.15673 | 0.051413 | 0.009516 | -0.019721 | 0.15776 | 0.28842 | -0.17081 | -0.29236 | 122.3339 | -0.007358 | 122.2148 | 122.1641 | -0.16972 | -0.15985 | 0.23816 | 121.8848 | -0.04823 | 122.2285 | 122.1574 | 0.27264 | 0.082429 | -0.37681 | 122.3758 | 122.2233 | 122.6213 | 122.174 | -0.049263 | 122.3349 | 122.4655 | 122.0063 | 122.1866 | -0.49835
2055.0781 | 122.3877 | -122.1863 | 0.2243 | 1.4211e-13 | -0.010004 | -0.0028483 | 0.029578 | -0.01455 | 0.010098 | -0.0019839 | 0.0070608 | 0.0074993 | -0.0077383 | 0.042613 | 0.0026685 | 0.037675 | 0.005985 | -0.012988 | 0.19406 | -0.04543 | 0.44415 | 0.15215 | 0.046835 | 0.014095 | -0.015143 | 0.16234 | 0.29758 | -0.17081 | -0.28778 | 122.3384 | -0.030246 | 122.224 | 122.1733 | -0.16514 | -0.26973 | 0.21985 | 121.8985 | -0.061962 | 122.2331 | 122.1711 | 0.27263 | 0.073276 | -0.39512 | 122.3803 | 122.1408 | 122.6304 | 122.1923 | -0.072152 | 122.3486 | 122.4839 | 122.0155 | 122.2004 | -0.51208
2056.7656 | 122.3923 | -122.2366 | 0.23346 | 1.4211e-13 | -0.010218 | -0.0026347 | 0.030219 | -0.01455 | 0.010311 | -0.0019839 | 0.0072744 | 0.0081403 | -0.0081657 | 0.042613 | 0.0024549 | 0.033096 | 0.001407 | -0.017566 | 0.20779 | -0.04543 | 0.45331 | 0.15215 | 0.046835 | 0.009516 | -0.019721 | 0.15318 | 0.30216 | -0.17081 | -0.29693 | 122.3888 | -0.025666 | 122.2697 | 122.2191 | -0.16972 | -0.27889 | 0.21985 | 121.9397 | -0.080274 | 122.2835 | 122.2169 | 0.27721 | 0.068699 | -0.40427 | 122.4444 | 122.1912 | 122.6899 | 122.238 | -0.081307 | 122.3898 | 122.5388 | 122.0658 | 122.2461 | -0.53039
2058.5156 | 122.5113 | -122.1725 | 0.21515 | 1.4211e-13 | -0.010004 | -0.0030619 | 0.030005 | -0.014337 | 0.010098 | -0.0019839 | 0.0072744 | 0.0074993 | -0.0079521 | 0.042613 | 0.0024549 | 0.042253 | -0.003172 | -0.017566 | 0.20321 | 0.023254 | 0.44415 | 0.14757 | 0.042256 | 0.014095 | -0.019721 | 0.15776 | 0.29758 | -0.17539 | -0.29693 | 122.3201 | -0.011935 | 122.2148 | 122.155 | -0.16514 | -0.1919 | 0.229 | 121.8756 | -0.057385 | 122.2148 | 122.1528 | 0.27721 | 0.082431 | -0.39054 | 122.3758 | 122.1958 | 122.6167 | 122.1694 | -0.067576 | 122.3303 | 122.4701 | 121.9972 | 122.1866 | -0.51208
2060.25 | 122.3923 | -122.1954 | 0.22888 | 1.4211e-13 | -0.010218 | -0.0028483 | 0.030005 | -0.01455 | 0.010311 | 0.020908 | 0.007488 | 0.0077131 | -0.0075247 | 0.042185 | 0.0024549 | 0.033096 | -0.003172 | -0.008409 | 0.19864 | 0.014096 | 0.44415 | 0.15215 | 0.042256 | 0.009516 | -0.019721 | 0.15776 | 0.30216 | -0.16624 | -0.29236 | 122.3476 | -0.030246 | 122.2285 | 122.187 | -0.16056 | -0.21479 | 0.21527 | 121.9031 | -0.071118 | 122.2377 | 122.1757 | 0.27264 | 0.073276 | -0.39512 | 122.3941 | 122.2095 | 122.6396 | 122.1923 | -0.07673 | 122.3532 | 122.4976 | 122.0292 | 122.205 | -0.52124
2062 | 122.3969 | -122.2137 | 0.21973 | 1.4211e-13 | -0.010431 | -0.0030619 | 0.030005 | -0.014337 | 0.0098841 | 0.013277 | 0.0070608 | 0.0077131 | -0.0077383 | 0.042613 | 0.0026685 | 0.037675 | 0.005985 | -0.017566 | 0.19864 | 0.018675 | 0.44873 | 0.16131 | 0.042256 | 0.014095 | -0.019721 | 0.15318 | 0.30674 | -0.17081 | -0.29236 | 122.3751 | -0.021091 | 122.2514 | 122.1962 | -0.17888 | -0.20105 | 0.22901 | 121.9214 | -0.066542 | 122.256 | 122.194 | 0.27264 | 0.08701 | -0.39054 | 122.4124 | 122.2324 | 122.6625 | 122.2197 | -0.058417 | 122.3669 | 122.5205 | 122.0429 | 122.2278 | -0.51208
2063.6875 | 122.4884 | -122.2092 | 0.20142 | 1.4211e-13 | -0.010431 | -0.0026347 | 0.029792 | -0.014764 | 0.010098 | -0.0019839 | 0.007488 | 0.0079267 | -0.0081657 | 0.042613 | 0.0026685 | 0.033096 | 0.001407 | -0.012988 | 0.19864 | 0.014096 | 0.44415 | 0.15673 | 0.042256 | 0.009516 | -0.028879 | 0.16692 | 0.30216 | -0.16624 | -0.29236 | 122.3659 | -0.00278 | 122.2423 | 122.1962 | -0.16972 | -0.18732 | 0.24274 | 121.9168 | -0.034495 | 122.2514 | 122.1803 | 0.26348 | 0.10074 | -0.36765 | 122.4078 | 122.2233 | 122.6533 | 122.2106 | -0.044685 | 122.3761 | 122.5113 | 122.0429 | 122.2187 | -0.49377
2065.4375 | 122.5388 | -122.1725 | 0.19684 | 1.4211e-13 | -0.010431 | -0.0032757 | 0.029792 | -0.01455 | 0.010311 | 0.0056466 | 0.007488 | 0.0077131 | -0.0077383 | 0.042827 | 0.0024549 | 0.042253 | 0.005985 | -0.003831 | 0.19864 | -0.027115 | 0.44873 | 0.15215 | 0.037677 | 0.009516 | -0.015143 | 0.16692 | 0.30216 | -0.18455 | -0.29236 | 122.3247 | 0.001798 | 122.2148 | 122.1687 | -0.15598 | -0.22395 | 0.25189 | 121.8802 | -0.029917 | 122.2102 | 122.1574 | 0.27721 | 0.10532 | -0.38139 | 122.3712 | 122.1454 | 122.6213 | 122.1785 | -0.044686 | 122.3395 | 122.4747 | 121.988 | 122.1821 | -0.48919
2067.2031 | 122.5433 | -122.1954 | 0.20599 | 1.4211e-13 | -0.010218 | -0.0030619 | 0.029364 | -0.014337 | 0.0098841 | 0.0056466 | 0.0072744 | 0.0077131 | -0.0081657 | 0.042827 | 0.0028821 | 0.033096 | 0.005985 | -0.017566 | 0.19864 | -0.00422 | 0.44873 | 0.15673 | 0.042256 | 0.004938 | -0.019721 | 0.16692 | 0.29758 | -0.17081 | -0.29693 | 122.3522 | -0.007358 | 122.2285 | 122.1779 | -0.1743 | -0.21021 | 0.24274 | 121.8985 | -0.039073 | 122.2377 | 122.1757 | 0.27721 | 0.091586 | -0.37681 | 122.3941 | 122.1912 | 122.6442 | 122.2014 | -0.049263 | 122.3624 | 122.493 | 122.0246 | 122.2004 | -0.50293
2068.8906 | 122.5708 | -122.1909 | 0.19226 | 1.4211e-13 | -0.010431 | -0.0028483 | 0.029578 | -0.014337 | 0.010098 | 0.0056466 | 0.0072744 | 0.0074993 | -0.0077383 | 0.042613 | 0.0028821 | 0.046831 | 0.001407 | -0.008409 | 0.20321 | 0.014096 | 0.435 | 0.15215 | 0.042256 | 0.004938 | -0.0243 | 0.15776 | 0.29758 | -0.17081 | -0.29693 | 122.343 | 0.010953 | 122.2377 | 122.1824 | -0.16056 | -0.17816 | 0.24274 | 121.8939 | -0.034497 | 122.2331 | 122.1666 | 0.27263 | 0.10532 | -0.36308 | 122.3941 | 122.205 | 122.6259 | 122.1923 | -0.040109 | 122.3486 | 122.4884 | 122.02 | 122.1958 | -0.48919
2070.6406 | 122.4564 | -122.2412 | 0.22888 | 1.4211e-13 | -0.010431 | -0.0032757 | 0.029364 | -0.01455 | 0.0094567 | 0.0056466 | 0.0070608 | 0.0077131 | -0.0079521 | 0.042613 | 0.0022413 | 0.033096 | 0.001407 | -0.012988 | 0.19864 | -0.022536 | 0.44415 | 0.15215 | 0.046835 | 0.018674 | -0.015143 | 0.15776 | 0.29758 | -0.17539 | -0.29236 | 122.3934 | -0.030246 | 122.2743 | 122.2282 | -0.16514 | -0.25142 | 0.21527 | 121.9489 | -0.071118 | 122.288 | 122.2261 | 0.27721 | 0.068698 | -0.40427 | 122.4398 | 122.2187 | 122.6854 | 122.2426 | -0.07673 | 122.399 | 122.5388 | 122.0658 | 122.2599 | -0.52124
2072.3906 | 122.5113 | -122.1817 | 0.2243 | 1.4211e-13 | -0.010431 | -0.0030619 | 0.029364 | -0.01455 | 0.010098 | 0.0056466 | 0.0070608 | 0.0072857 | -0.0077383 | 0.042399 | 0.0026685 | 0.037675 | -0.003172 | -0.008409 | 0.20321 | -0.017957 | 0.44873 | 0.16131 | 0.051413 | 0.009516 | -0.019721 | 0.16234 | 0.29758 | -0.17081 | -0.29236 | 122.343 | -0.02109 | 122.2194 | 122.1733 | -0.16972 | -0.24226 | 0.22443 | 121.8893 | -0.061962 | 122.2331 | 122.162 | 0.27264 | 0.073276 | -0.39512 | 122.3849 | 122.1637 | 122.6304 | 122.1785 | -0.062994 | 122.344 | 122.4793 | 122.0109 | 122.1912 | -0.51666
2074.0781 | 122.5204 | -122.2137 | 0.19226 | 1.4211e-13 | -0.010218 | -0.0028483 | 0.029792 | -0.01455 | 0.010311 | -0.0019839 | 0.0070608 | 0.0074993 | -0.0077383 | 0.042399 | 0.0026685 | 0.037675 | 0.005985 | -0.012988 | 0.19864 | -0.027115 | 0.43957 | 0.15215 | 0.042256 | 0.009516 | -0.015143 | 0.16692 | 0.29758 | -0.17081 | -0.29236 | 122.3659 | 0.006375 | 122.2514 | 122.2008 | -0.16514 | -0.21938 | 0.24731 | 121.9214 | -0.02534 | 122.256 | 122.1986 | 0.27721 | 0.10532 | -0.36308 | 122.4124 | 122.1866 | 122.6533 | 122.2197 | -0.040109 | 122.3807 | 122.5113 | 122.0429 | 122.2233 | -0.48462
2075.8281 | 122.438 | -122.2412 | 0.23346 | 1.4211e-13 | -0.010004 | -0.0030619 | 0.029578 | -0.01455 | 0.0098841 | 0.0056466 | 0.007488 | 0.0074993 | -0.0079521 | 0.042399 | 0.0020275 | 0.037675 | 0.010564 | -0.012988 | 0.20321 | 0.018675 | 0.44873 | 0.15215 | 0.046835 | 0.009516 | -0.019721 | 0.15776 | 0.30216 | -0.16624 | -0.28778 | 122.3934 | -0.030245 | 122.2789 | 122.2282 | -0.16514 | -0.21478 | 0.21527 | 121.9534 | -0.075695 | 122.288 | 122.2215 | 0.26806 | 0.068699 | -0.3997 | 122.4444 | 122.2599 | 122.6899 | 122.2518 | -0.081307 | 122.399 | 122.5434 | 122.075 | 122.2507 | -0.52124
2077.5781 | 122.438 | -122.2366 | 0.2243 | 1.4211e-13 | -0.010218 | -0.0030619 | 0.029364 | -0.01455 | 0.0096705 | 0.0056466 | 0.007488 | 0.0079267 | -0.0079521 | 0.042399 | 0.0024549 | 0.037675 | 0.005985 | -0.012988 | 0.18948 | 0.000359 | 0.44415 | 0.15673 | 0.051413 | 0.018674 | -0.033458 | 0.15776 | 0.30216 | -0.17081 | -0.28778 | 122.3934 | -0.034825 | 122.2743 | 122.2236 | -0.16972 | -0.22395 | 0.21985 | 121.9489 | -0.06654 | 122.288 | 122.2032 | 0.25432 | 0.077854 | -0.39512 | 122.4261 | 122.237 | 122.6808 | 122.2426 | -0.067573 | 122.3944 | 122.5388 | 122.0658 | 122.2553 | -0.51208
2079.2656 | 122.4884 | -122.2321 | 0.21515 | 1.4211e-13 | -0.010218 | -0.0028483 | 0.029578 | -0.014123 | 0.010098 | -0.0019839 | 0.0072744 | 0.0077131 | -0.0077383 | 0.042399 | 0.0024549 | 0.037675 | -0.003172 | -0.022144 | 0.20321 | -0.008799 | 0.44415 | 0.15215 | 0.042256 | 0.009516 | -0.019721 | 0.16234 | 0.30674 | -0.16624 | -0.29236 | 122.3842 | -0.011935 | 122.2697 | 122.2099 | -0.1743 | -0.22395 | 0.229 | 121.9397 | -0.052807 | 122.2743 | 122.2123 | 0.27264 | 0.091588 | -0.38138 | 122.4353 | 122.2233 | 122.6762 | 122.2289 | -0.062997 | 122.3944 | 122.5388 | 122.0658 | 122.2416 | -0.5075
2081.0312 | 122.4426 | -122.2641 | 0.21973 | 1.4211e-13 | -0.010218 | -0.0030619 | 0.029792 | -0.014764 | 0.0098841 | 0.0056466 | 0.0072744 | 0.0079267 | -0.0079521 | 0.042827 | 0.0026685 | 0.037675 | 0.005985 | -0.012988 | 0.19406 | -0.027115 | 0.44415 | 0.15673 | 0.046835 | 0.014095 | -0.028879 | 0.16234 | 0.30216 | -0.17539 | -0.29236 | 122.4208 | -0.025669 | 122.3018 | 122.2511 | -0.16972 | -0.24684 | 0.22443 | 121.9717 | -0.057385 | 122.3109 | 122.2352 | 0.26348 | 0.082431 | -0.39512 | 122.4582 | 122.237 | 122.7083 | 122.2701 | -0.062996 | 122.4264 | 122.5663 | 122.0887 | 122.2782 | -0.51208
2082.7656 | 122.4472 | -122.2687 | 0.23346 | 1.4211e-13 | -0.010431 | -0.0028483 | 0.029364 | -0.014337 | 0.0098841 | -0.0019839 | 0.0072744 | 0.0074993 | -0.0077383 | 0.042613 | 0.0024549 | 0.033096 | -0.003172 | -0.017566 | 0.19406 | 0.023254 | 0.44873 | 0.15215 | 0.042256 | 0.009516 | -0.010564 | 0.15776 | 0.30674 | -0.17081 | -0.29693 | 122.4208 | -0.039401 | 122.3018 | 122.2511 | -0.16972 | -0.21021 | 0.21527 | 121.9717 | -0.075695 | 122.3109 | 122.2581 | 0.28637 | 0.073278 | -0.40427 | 122.4627 | 122.2919 | 122.7174 | 122.2655 | -0.081307 | 122.4264 | 122.5754 | 122.0979 | 122.2782 | -0.53039
2084.5156 | 122.4472 | -122.2687 | 0.22888 | 1.4211e-13 | -0.010218 | -0.0024209 | 0.029792 | -0.014764 | 0.0098841 | -0.0019839 | 0.0070608 | 0.0079267 | -0.0081657 | 0.042827 | 0.0024549 | 0.042253 | 0.001407 | -0.008409 | 0.19864 | 0.009517 | 0.45331 | 0.16131 | 0.046835 | 0.009516 | -0.010564 | 0.16234 | 0.30674 | -0.17081 | -0.29693 | 122.43 | -0.030246 | 122.3109 | 122.2603 | -0.16972 | -0.21937 | 0.22443 | 121.9717 | -0.06654 | 122.3155 | 122.2581 | 0.28637 | 0.077855 | -0.3997 | 122.4673 | 122.2782 | 122.722 | 122.2701 | -0.067572 | 122.431 | 122.5754 | 122.0979 | 122.2782 | -0.52582
2086.2031 | 122.493 | -122.2549 | 0.21973 | 1.4211e-13 | -0.010431 | -0.0030619 | 0.029578 | -0.014337 | 0.0096705 | -0.0019839 | 0.0070608 | 0.0079267 | -0.0079521 | 0.042613 | 0.0020275 | 0.042253 | 0.001407 | -0.012988 | 0.19864 | -0.04543 | 0.44415 | 0.15673 | 0.042256 | 0.009516 | -0.015143 | 0.16692 | 0.30216 | -0.17539 | -0.29236 | 122.4117 | -0.021091 | 122.2972 | 122.242 | -0.16972 | -0.26516 | 0.22443 | 121.9626 | -0.052806 | 122.2972 | 122.2398 | 0.27721 | 0.082431 | -0.39512 | 122.4536 | 122.2095 | 122.6991 | 122.2564 | -0.062996 | 122.4219 | 122.5571 | 122.0796 | 122.2645 | -0.51208
2087.9531 | 122.5891 | -122.2092 | 0.1831 | 1.4211e-13 | -0.010004 | -0.0026347 | 0.029792 | -0.014337 | 0.0098841 | 0.0056466 | 0.0070608 | 0.0074993 | -0.0079521 | 0.042399 | 0.0022413 | 0.028518 | 0.001407 | -0.012988 | 0.20321 | -0.054588 | 0.44415 | 0.15215 | 0.037677 | 0.009516 | -0.015143 | 0.15776 | 0.29758 | -0.16624 | -0.29236 | 122.3613 | 0.020109 | 122.2377 | 122.1962 | -0.16514 | -0.23769 | 0.26105 | 121.9168 | -0.025341 | 122.2468 | 122.194 | 0.27721 | 0.11448 | -0.34934 | 122.4124 | 122.1546 | 122.6533 | 122.2106 | -0.030953 | 122.3669 | 122.5067 | 122.0429 | 122.2187 | -0.47546
2089.7188 | 122.5891 | -122.2183 | 0.19684 | 1.4211e-13 | -0.010218 | -0.0028483 | 0.029578 | -0.014337 | 0.0098841 | -0.0019839 | 0.0070608 | 0.0077131 | -0.0077383 | 0.042399 | 0.0024549 | 0.033096 | 0.001407 | -0.008409 | 0.19864 | -0.050009 | 0.44415 | 0.15673 | 0.046835 | 0.018674 | -0.015143 | 0.15318 | 0.30216 | -0.17081 | -0.29693 | 122.3751 | 0.001798 | 122.2514 | 122.2099 | -0.16514 | -0.24685 | 0.24732 | 121.9214 | -0.043653 | 122.2652 | 122.2032 | 0.28179 | 0.10532 | -0.36765 | 122.417 | 122.1683 | 122.6625 | 122.2197 | -0.040107 | 122.3715 | 122.5205 | 122.0475 | 122.237 | -0.49377
2091.4062 | 122.5616 | -122.2366 | 0.18768 | 1.4211e-13 | -0.010218 | -0.0028483 | 0.029578 | -0.014764 | 0.0098841 | -0.0019839 | 0.0070608 | 0.0074993 | -0.0079521 | 0.042613 | 0.0028821 | 0.037675 | -0.003172 | -0.012988 | 0.19864 | -0.054588 | 0.44415 | 0.15673 | 0.042256 | 0.014095 | -0.015143 | 0.15776 | 0.30216 | -0.17081 | -0.29693 | 122.3934 | 0.010953 | 122.2743 | 122.2236 | -0.16972 | -0.24227 | 0.25647 | 121.9397 | -0.029919 | 122.2789 | 122.2215 | 0.28179 | 0.11447 | -0.3585 | 122.4353 | 122.182 | 122.6808 | 122.2335 | -0.030952 | 122.3944 | 122.5388 | 122.0658 | 122.2507 | -0.48462
2093.1562 | 122.5388 | -122.287 | 0.19684 | 1.4211e-13 | -0.010218 | -0.0028483 | 0.029792 | -0.01455 | 0.0096705 | 0.0056466 | 0.0077016 | 0.0074993 | -0.0079521 | 0.042399 | 0.0026685 | 0.037675 | 0.005985 | -0.012988 | 0.19864 | -0.063746 | 0.44415 | 0.16131 | 0.042256 | 0.014095 | -0.015143 | 0.15776 | 0.293 | -0.17539 | -0.28778 | 122.4483 | 0.001798 | 122.3247 | 122.274 | -0.1743 | -0.26058 | 0.24732 | 121.9992 | -0.039074 | 122.3292 | 122.2718 | 0.27263 | 0.096163 | -0.37223 | 122.4856 | 122.2232 | 122.7311 | 122.293 | -0.035528 | 122.4448 | 122.58 | 122.1116 | 122.3011 | -0.48462
2094.9062 | 122.4609 | -122.2824 | 0.2243 | 1.4211e-13 | -0.010004 | -0.0030619 | 0.029792 | -0.014337 | 0.010098 | 0.0056466 | 0.0072744 | 0.0077131 | -0.0079521 | 0.042613 | 0.0022413 | 0.037675 | 0.001407 | -0.017566 | 0.19864 | -0.059167 | 0.43957 | 0.15215 | 0.042256 | 0.000359 | -0.0243 | 0.15318 | 0.30216 | -0.16624 | -0.28778 | 122.4346 | -0.025668 | 122.3201 | 122.2648 | -0.16972 | -0.28347 | 0.21527 | 121.9946 | -0.071119 | 122.3247 | 122.2581 | 0.26348 | 0.077854 | -0.39054 | 122.481 | 122.2232 | 122.722 | 122.2838 | -0.072152 | 122.4356 | 122.5846 | 122.1162 | 122.2828 | -0.51208
2096.5938 | 122.4701 | -122.2778 | 0.21515 | 1.4211e-13 | -0.010218 | -0.0030619 | 0.029792 | -0.01455 | 0.010098 | -0.0019839 | 0.007488 | 0.0079267 | -0.0079521 | 0.042185 | 0.0026685 | 0.037675 | 0.001407 | -0.022144 | 0.20321 | -0.059167 | 0.44873 | 0.15673 | 0.046835 | 0.004938 | -0.0243 | 0.16234 | 0.30674 | -0.17081 | -0.29236 | 122.4346 | -0.011935 | 122.3155 | 122.2557 | -0.17888 | -0.27432 | 0.23358 | 121.9855 | -0.052807 | 122.3247 | 122.2535 | 0.26806 | 0.091588 | -0.38596 | 122.481 | 122.2187 | 122.7266 | 122.2792 | -0.058418 | 122.4402 | 122.5846 | 122.107 | 122.2828 | -0.5075
2098.2812 | 122.5021 | -122.2961 | 0.22888 | 1.4211e-13 | -0.010004 | -0.0028483 | 0.029792 | -0.014337 | 0.0098841 | 0.013277 | 0.0070608 | 0.0077131 | -0.0077383 | 0.042613 | 0.0024549 | 0.042253 | 0.001407 | -0.012988 | 0.19864 | -0.059167 | 0.44873 | 0.15673 | 0.051413 | 0.009516 | -0.019721 | 0.16692 | 0.29758 | -0.17081 | -0.29236 | 122.4529 | -0.030246 | 122.3384 | 122.2832 | -0.16972 | -0.28805 | 0.21985 | 122.0038 | -0.061961 | 122.3476 | 122.2764 | 0.27264 | 0.068698 | -0.3997 | 122.4948 | 122.237 | 122.7449 | 122.2976 | -0.072151 | 122.4631 | 122.5937 | 122.1253 | 122.3057 | -0.52124
2100.0469 | 122.5296 | -122.2916 | 0.23804 | 1.4211e-13 | -0.010645 | -0.0028483 | 0.029151 | -0.014978 | 0.0098841 | -0.0019839 | 0.007488 | 0.0074993 | -0.0077383 | 0.042613 | 0.0024549 | 0.042253 | 0.005985 | -0.012988 | 0.19864 | -0.013378 | 0.44873 | 0.15673 | 0.042256 | 0.014095 | -0.010564 | 0.16692 | 0.30674 | -0.17081 | -0.29236 | 122.4483 | -0.039401 | 122.3338 | 122.2786 | -0.16972 | -0.25141 | 0.2107 | 121.9992 | -0.071116 | 122.3338 | 122.281 | 0.28179 | 0.0687 | -0.40885 | 122.4902 | 122.2782 | 122.7403 | 122.2976 | -0.081306 | 122.4585 | 122.5983 | 122.1208 | 122.3057 | -0.53039
2101.7969 | 122.4884 | -122.3099 | 0.22888 | 1.4211e-13 | -0.010431 | -0.0030619 | 0.029578 | -0.01455 | 0.0096705 | -0.0019839 | 0.0072744 | 0.0074993 | -0.0081657 | 0.042185 | 0.0024549 | 0.037675 | 0.001407 | -0.012988 | 0.20321 | -0.063746 | 0.435 | 0.15673 | 0.046835 | 0.004938 | -0.0243 | 0.15776 | 0.293 | -0.17081 | -0.30151 | 122.4666 | -0.025668 | 122.3475 | 122.2969 | -0.16972 | -0.29263 | 0.20612 | 122.0084 | -0.071118 | 122.3567 | 122.2856 | 0.27721 | 0.064119 | -0.3997 | 122.5131 | 122.2461 | 122.7449 | 122.3113 | -0.072151 | 122.4676 | 122.6029 | 122.1391 | 122.3148 | -0.53039
2103.5469 | 122.4884 | -122.319 | 0.22888 | 1.4211e-13 | -0.010859 | -0.0028483 | 0.029792 | -0.014764 | 0.0094567 | -0.0019839 | 0.0070608 | 0.0074993 | -0.0081657 | 0.042613 | 0.0024549 | 0.037675 | 0.001407 | -0.012988 | 0.20321 | -0.017957 | 0.44415 | 0.16131 | 0.046835 | 0.014095 | -0.019721 | 0.16234 | 0.29758 | -0.16624 | -0.28778 | 122.4803 | -0.025668 | 122.3567 | 122.306 | -0.1743 | -0.24684 | 0.21527 | 122.0313 | -0.06654 | 122.3659 | 122.2993 | 0.26806 | 0.068698 | -0.39512 | 122.5222 | 122.3011 | 122.7632 | 122.3204 | -0.067572 | 122.4814 | 122.6166 | 122.1528 | 122.3331 | -0.51666
2105.2344 | 122.493 | -122.3328 | 0.2655 | 1.4211e-13 | -0.010431 | -0.0028483 | 0.029792 | -0.01455 | 0.010098 | -0.0019839 | 0.007488 | 0.0079267 | -0.0079521 | 0.042827 | 0.0026685 | 0.037675 | 0.005985 | -0.008409 | 0.19864 | -0.063746 | 0.44873 | 0.15673 | 0.051413 | 0.009516 | -0.0243 | 0.15776 | 0.30216 | -0.17081 | -0.29236 | 122.4895 | -0.066867 | 122.3704 | 122.3244 | -0.16514 | -0.32925 | 0.18323 | 122.0404 | -0.10774 | 122.3842 | 122.3085 | 0.26806 | 0.036655 | -0.43632 | 122.5314 | 122.269 | 122.7815 | 122.3387 | -0.10877 | 122.4905 | 122.6349 | 122.1619 | 122.3423 | -0.55786
2106.9844 | 122.5754 | -122.2916 | 0.19684 | 1.4211e-13 | -0.010218 | -0.0028483 | 0.030005 | -0.014337 | 0.010098 | 0.013277 | 0.0070608 | 0.0079267 | -0.0077383 | 0.042613 | 0.0024549 | 0.042253 | -0.003172 | -0.012988 | 0.19864 | -0.04543 | 0.43957 | 0.15673 | 0.046835 | 0.009516 | -0.019721 | 0.16692 | 0.30216 | -0.17081 | -0.29236 | 122.4483 | 0.001798 | 122.3338 | 122.2786 | -0.16972 | -0.24227 | 0.24274 | 121.9992 | -0.029917 | 122.3384 | 122.2718 | 0.27264 | 0.10532 | -0.36765 | 122.4902 | 122.2461 | 122.7311 | 122.2884 | -0.040107 | 122.4585 | 122.5937 | 122.1208 | 122.3011 | -0.48919
2108.7344 | 122.58 | -122.2824 | 0.21515 | 1.4211e-13 | -0.010645 | -0.0028483 | 0.029792 | -0.014337 | 0.010098 | 0.0056466 | 0.0072744 | 0.0079267 | -0.0079521 | 0.042827 | 0.0022413 | 0.037675 | -0.003172 | -0.008409 | 0.18948 | -0.059167 | 0.43957 | 0.15673 | 0.046835 | 0.000359 | -0.0243 | 0.15776 | 0.28842 | -0.17081 | -0.29236 | 122.4391 | -0.02567 | 122.3201 | 122.274 | -0.16514 | -0.27432 | 0.22443 | 121.9901 | -0.057385 | 122.3292 | 122.2581 | 0.26806 | 0.073274 | -0.38596 | 122.4719 | 122.2232 | 122.722 | 122.2792 | -0.058418 | 122.4402 | 122.5708 | 122.1116 | 122.2828 | -0.5075
2110.4375 | 122.5983 | -122.2916 | 0.20599 | 1.4211e-13 | -0.010431 | -0.0028483 | 0.029578 | -0.014764 | 0.0098841 | 0.0056466 | 0.0072744 | 0.0077131 | -0.0079521 | 0.042613 | 0.0024549 | 0.033096 | 0.001407 | -0.008409 | 0.19864 | -0.059167 | 0.44415 | 0.16131 | 0.046835 | 0.004938 | -0.0243 | 0.16692 | 0.30674 | -0.16624 | -0.30151 | 122.4529 | -0.007358 | 122.3247 | 122.2832 | -0.16972 | -0.26516 | 0.23816 | 121.9901 | -0.039073 | 122.3384 | 122.2673 | 0.27721 | 0.10074 | -0.37223 | 122.4902 | 122.2324 | 122.7357 | 122.293 | -0.044684 | 122.4585 | 122.5983 | 122.1253 | 122.2965 | -0.50751
2112.1875 | 122.5342 | -122.3007 | 0.20599 | 1.4211e-13 | -0.010004 | -0.0030619 | 0.029578 | -0.01455 | 0.0096705 | 0.0056466 | 0.007488 | 0.0074993 | -0.0077383 | 0.042399 | 0.0024549 | 0.042253 | -0.007751 | -0.012988 | 0.19406 | -0.063746 | 0.44415 | 0.15673 | 0.051413 | 0.009516 | -0.028879 | 0.16234 | 0.293 | -0.17081 | -0.29693 | 122.4575 | -0.011936 | 122.343 | 122.2877 | -0.16972 | -0.26974 | 0.23816 | 122.0038 | -0.043652 | 122.3521 | 122.2718 | 0.26805 | 0.087007 | -0.37681 | 122.4948 | 122.237 | 122.7449 | 122.293 | -0.049263 | 122.4631 | 122.5937 | 122.1299 | 122.3102 | -0.50293
2113.9531 | 122.5388 | -122.3511 | 0.21515 | 1.4211e-13 | -0.010431 | -0.0026347 | 0.029578 | -0.01455 | 0.010311 | 0.0056466 | 0.0072744 | 0.0074993 | -0.0081657 | 0.042399 | 0.0028821 | 0.033096 | 0.001407 | -0.012988 | 0.19406 | -0.059167 | 0.435 | 0.15673 | 0.042256 | 0.004938 | -0.019721 | 0.15776 | 0.30674 | -0.17081 | -0.30151 | 122.5078 | -0.021091 | 122.3842 | 122.3381 | -0.16972 | -0.27432 | 0.21985 | 122.0496 | -0.057385 | 122.3933 | 122.3314 | 0.28179 | 0.091588 | -0.38596 | 122.5451 | 122.2919 | 122.7861 | 122.3525 | -0.058418 | 122.5088 | 122.6578 | 122.1803 | 122.356 | -0.51666
2115.7031 | 122.6395 | -122.3099 | 0.1831 | 1.4211e-13 | -0.010431 | -0.0024209 | 0.029792 | -0.014764 | 0.0098841 | -0.0019839 | 0.0070608 | 0.0074993 | -0.0079521 | 0.042827 | 0.0024549 | 0.042253 | -0.003172 | -0.012988 | 0.19406 | -0.054588 | 0.44873 | 0.14757 | 0.051413 | 0.009516 | -0.015143 | 0.15776 | 0.30216 | -0.17081 | -0.30151 | 122.4574 | 0.010953 | 122.3521 | 122.2969 | -0.16056 | -0.23769 | 0.26563 | 122.0084 | -0.025341 | 122.3613 | 122.2947 | 0.28637 | 0.11905 | -0.35392 | 122.5039 | 122.2553 | 122.7586 | 122.3067 | -0.035532 | 122.4676 | 122.612 | 122.1391 | 122.3194 | -0.48462
2117.3906 | 122.5296 | -122.3328 | 0.20599 | 1.4211e-13 | -0.010218 | -0.0028483 | 0.029578 | -0.014123 | 0.0098841 | 0.0056466 | 0.007488 | 0.0074993 | -0.0079521 | 0.042613 | 0.0024549 | 0.033096 | 0.001407 | -0.012988 | 0.19864 | -0.027115 | 0.44415 | 0.15673 | 0.046835 | 0.009516 | -0.019721 | 0.16234 | 0.30674 | -0.17539 | -0.29693 | 122.4895 | -0.007358 | 122.3659 | 122.3198 | -0.16972 | -0.23311 | 0.23816 | 122.0358 | -0.043652 | 122.3796 | 122.313 | 0.27721 | 0.10074 | -0.38139 | 122.5314 | 122.3056 | 122.7769 | 122.3342 | -0.049263 | 122.4951 | 122.6395 | 122.1574 | 122.3423 | -0.50293
2119.1406 | 122.6212 | -122.2916 | 0.20142 | 1.4211e-13 | -0.010431 | -0.0030619 | 0.030005 | -0.01455 | 0.010098 | 0.0056466 | 0.0077016 | 0.0072857 | -0.0081657 | 0.042613 | 0.0024549 | 0.033096 | 0.001407 | -0.012988 | 0.19406 | -0.059167 | 0.43957 | 0.16131 | 0.051413 | 0.004938 | -0.019721 | 0.16692 | 0.293 | -0.17081 | -0.29693 | 122.4529 | -0.007358 | 122.3247 | 122.2786 | -0.1743 | -0.26058 | 0.23816 | 121.9946 | -0.034495 | 122.343 | 122.2718 | 0.27721 | 0.091585 | -0.37223 | 122.4856 | 122.2324 | 122.7311 | 122.293 | -0.040106 | 122.4585 | 122.5846 | 122.1208 | 122.2965 | -0.49835
2120.8906 | 122.6578 | -122.3007 | 0.20599 | 1.4211e-13 | -0.010431 | -0.0028483 | 0.029364 | -0.014978 | 0.0094567 | 0.0056466 | 0.0072744 | 0.0074993 | -0.0079521 | 0.042613 | 0.0026685 | 0.037675 | 0.001407 | -0.012988 | 0.19864 | -0.054588 | 0.435 | 0.15215 | 0.046835 | 0.009516 | -0.019721 | 0.16692 | 0.30216 | -0.17539 | -0.29693 | 122.4529 | -0.007358 | 122.3384 | 122.2877 | -0.16514 | -0.26058 | 0.229 | 122.0038 | -0.039073 | 122.3476 | 122.281 | 0.27721 | 0.096164 | -0.38139 | 122.4994 | 122.2461 | 122.7357 | 122.3021 | -0.053842 | 122.4676 | 122.6029 | 122.1253 | 122.3102 | -0.50293
2122.5781 | 122.6074 | -122.319 | 0.21057 | 1.4211e-13 | -0.010645 | -0.0028483 | 0.029578 | -0.01455 | 0.010311 | -0.0019839 | 0.0072744 | 0.0074993 | -0.0077383 | 0.042613 | 0.0024549 | 0.033096 | -0.003172 | -0.008409 | 0.19864 | -0.054588 | 0.43957 | 0.15215 | 0.033099 | 0.009516 | -0.019721 | 0.16692 | 0.30216 | -0.17081 | -0.29693 | 122.4712 | -0.011935 | 122.3521 | 122.3106 | -0.16056 | -0.26516 | 0.229 | 122.0221 | -0.04365 | 122.3521 | 122.2993 | 0.27721 | 0.091587 | -0.38139 | 122.5177 | 122.2644 | 122.7586 | 122.3159 | -0.058419 | 122.486 | 122.6212 | 122.1482 | 122.3285 | -0.5075
2124.3438 | 122.6624 | -122.3236 | 0.19684 | 1.4211e-13 | -0.010218 | -0.0026347 | 0.029578 | -0.01455 | 0.0098841 | -0.0019839 | 0.0072744 | 0.0072857 | -0.0081657 | 0.042613 | 0.0024549 | 0.033096 | -0.007751 | -0.012988 | 0.19406 | -0.054588 | 0.44415 | 0.15673 | 0.051413 | 0.014095 | -0.0243 | 0.16234 | 0.30216 | -0.17081 | -0.28778 | 122.4803 | -0.00278 | 122.3567 | 122.3106 | -0.16972 | -0.25143 | 0.24732 | 122.0358 | -0.034496 | 122.375 | 122.2993 | 0.26348 | 0.10532 | -0.36765 | 122.5177 | 122.269 | 122.7678 | 122.3159 | -0.040107 | 122.4859 | 122.6258 | 122.1528 | 122.3377 | -0.48462
2126.0938 | 122.6395 | -122.3145 | 0.19226 | 1.4211e-13 | -0.010218 | -0.0028483 | 0.029792 | -0.014764 | 0.0098841 | -0.0019839 | 0.0072744 | 0.0074993 | -0.0081657 | 0.042399 | 0.0024549 | 0.042253 | 0.005985 | -0.008409 | 0.19864 | -0.054588 | 0.435 | 0.16131 | 0.046835 | 0.009516 | -0.028879 | 0.15318 | 0.30674 | -0.17081 | -0.2832 | 122.4758 | 0.006375 | 122.3567 | 122.306 | -0.16972 | -0.24685 | 0.24274 | 122.0313 | -0.039076 | 122.3613 | 122.2856 | 0.25432 | 0.11448 | -0.36308 | 122.5131 | 122.2599 | 122.7494 | 122.3204 | -0.030951 | 122.4676 | 122.6212 | 122.1436 | 122.324 | -0.47546
2127.8438 | 122.5708 | -122.3419 | 0.20142 | 1.4211e-13 | -0.010431 | -0.0026347 | 0.029792 | -0.01455 | 0.010311 | 0.0056466 | 0.006847 | 0.0081403 | -0.0077383 | 0.042399 | 0.0024549 | 0.042253 | 0.001407 | -0.017566 | 0.19864 | -0.059167 | 0.44415 | 0.15673 | 0.042256 | 0.009516 | -0.005985 | 0.16234 | 0.30216 | -0.17081 | -0.29693 | 122.4986 | -0.00278 | 122.3842 | 122.3244 | -0.1743 | -0.26058 | 0.24274 | 122.045 | -0.039074 | 122.3842 | 122.3359 | 0.29095 | 0.10074 | -0.37223 | 122.5406 | 122.2828 | 122.7861 | 122.3433 | -0.044685 | 122.5043 | 122.6441 | 122.1711 | 122.3514 | -0.49835
2129.5469 | 122.5845 | -122.3419 | 0.22888 | 1.4211e-13 | -0.010431 | -0.0026347 | 0.029792 | -0.014764 | 0.0098841 | 0.0056466 | 0.007488 | 0.0074993 | -0.0079521 | 0.042613 | 0.0022413 | 0.042253 | 0.005985 | -0.008409 | 0.19864 | -0.063746 | 0.44415 | 0.15215 | 0.042256 | 0.009516 | -0.015143 | 0.16234 | 0.30216 | -0.17539 | -0.29236 | 122.4941 | -0.030246 | 122.3842 | 122.3335 | -0.16056 | -0.29263 | 0.21527 | 122.0496 | -0.06654 | 122.3842 | 122.3268 | 0.27721 | 0.073276 | -0.40427 | 122.5406 | 122.2782 | 122.7861 | 122.3479 | -0.07673 | 122.5043 | 122.6441 | 122.1665 | 122.3514 | -0.52124
2131.2969 | 122.644 | -122.3145 | 0.20142 | 1.4211e-13 | -0.010431 | -0.0028483 | 0.030005 | -0.014764 | 0.0096705 | 0.013277 | 0.0072744 | 0.0079267 | -0.0081657 | 0.042399 | 0.0026685 | 0.042253 | -0.003172 | -0.008409 | 0.20321 | -0.059167 | 0.44415 | 0.14757 | 0.042256 | 0.014095 | -0.019721 | 0.16692 | 0.30216 | -0.17081 | -0.28778 | 122.462 | 0.001798 | 122.3567 | 122.306 | -0.15598 | -0.26058 | 0.24274 | 122.0267 | -0.034495 | 122.3567 | 122.2947 | 0.26806 | 0.10074 | -0.37223 | 122.5177 | 122.2553 | 122.7586 | 122.3113 | -0.053843 | 122.4814 | 122.6166 | 122.1436 | 122.3285 | -0.48919
2133.0469 | 122.5296 | -122.3511 | 0.22888 | 1.4211e-13 | -0.010431 | -0.0026347 | 0.029792 | -0.01455 | 0.0094567 | 0.013277 | 0.0072744 | 0.0074993 | -0.0079521 | 0.042399 | 0.0024549 | 0.037675 | 0.001407 | -0.003831 | 0.20321 | -0.063746 | 0.44415 | 0.16131 | 0.051413 | 0.009516 | -0.015143 | 0.16692 | 0.30674 | -0.16624 | -0.29236 | 122.5124 | -0.025668 | 122.3887 | 122.3472 | -0.16514 | -0.29263 | 0.21527 | 122.0587 | -0.061961 | 122.4025 | 122.3359 | 0.27721 | 0.077855 | -0.39512 | 122.5543 | 122.2873 | 122.7952 | 122.3525 | -0.067572 | 122.518 | 122.6578 | 122.1848 | 122.3606 | -0.52124
2134.8125 | 122.5388 | -122.3831 | 0.23346 | 1.4211e-13 | -0.010218 | -0.0026347 | 0.029364 | -0.01455 | 0.0096705 | -0.0096144 | 0.0070608 | 0.0074993 | -0.0079521 | 0.042185 | 0.0022413 | 0.037675 | -0.003172 | -0.003831 | 0.20321 | -0.063746 | 0.44873 | 0.15215 | 0.042256 | 0.009516 | -0.0243 | 0.15776 | 0.29758 | -0.16624 | -0.29693 | 122.5353 | -0.030245 | 122.4208 | 122.3793 | -0.15598 | -0.2972 | 0.21527 | 122.0862 | -0.075695 | 122.4254 | 122.3588 | 0.27263 | 0.064121 | -0.3997 | 122.5863 | 122.3194 | 122.8319 | 122.3799 | -0.081307 | 122.5409 | 122.6807 | 122.2169 | 122.3926 | -0.53039
2136.5156 | 122.5479 | -122.374 | 0.20599 | 1.4211e-13 | -0.010431 | -0.0022073 | 0.029578 | -0.014978 | 0.0096705 | 0.0056466 | 0.0070608 | 0.0074993 | -0.0077383 | 0.042399 | 0.0022413 | 0.037675 | 0.001407 | 0.000747 | 0.19864 | -0.059167 | 0.44873 | 0.16131 | 0.046835 | 0.009516 | -0.015143 | 0.15776 | 0.29758 | -0.17539 | -0.29693 | 122.5353 | -0.007358 | 122.4116 | 122.3747 | -0.16056 | -0.26516 | 0.24274 | 122.077 | -0.04823 | 122.4208 | 122.3588 | 0.28179 | 0.091586 | -0.38139 | 122.5726 | 122.3148 | 122.8227 | 122.3754 | -0.044684 | 122.5317 | 122.6715 | 122.1986 | 122.3835 | -0.50293
2138.2656 | 122.5525 | -122.3831 | 0.22888 | 1.4211e-13 | -0.010431 | -0.0030619 | 0.029792 | -0.014764 | 0.0098841 | -0.0019839 | 0.0072744 | 0.0074993 | -0.0079521 | 0.042399 | 0.0024549 | 0.033096 | 0.001407 | -0.003831 | 0.19406 | -0.063746 | 0.435 | 0.15673 | 0.046835 | 0.004938 | -0.019721 | 0.16234 | 0.30674 | -0.16624 | -0.29693 | 122.5398 | -0.034824 | 122.4162 | 122.3793 | -0.16056 | -0.29263 | 0.20612 | 122.0862 | -0.06654 | 122.43 | 122.3634 | 0.27721 | 0.077855 | -0.39512 | 122.5772 | 122.3194 | 122.8181 | 122.3845 | -0.072151 | 122.5455 | 122.6899 | 122.2169 | 122.3881 | -0.52582
2140.0312 | 122.5983 | -122.3511 | 0.21057 | 1.4211e-13 | -0.010004 | -0.0028483 | 0.030005 | -0.01455 | 0.0096705 | 0.0056466 | 0.0072744 | 0.0077131 | -0.0081657 | 0.042613 | 0.0024549 | 0.037675 | 0.001407 | -0.003831 | 0.19406 | -0.054588 | 0.44415 | 0.16131 | 0.046835 | 0.014095 | -0.019721 | 0.15776 | 0.30216 | -0.17081 | -0.28778 | 122.5124 | -0.016513 | 122.3887 | 122.3472 | -0.16514 | -0.26516 | 0.23358 | 122.0633 | -0.052807 | 122.3979 | 122.3314 | 0.26806 | 0.091587 | -0.38139 | 122.5451 | 122.2965 | 122.7952 | 122.3525 | -0.049261 | 122.5088 | 122.6532 | 122.1803 | 122.3652 | -0.49835
2141.7188 | 122.6028 | -122.3694 | 0.20599 | 1.4211e-13 | -0.010645 | -0.0028483 | 0.029792 | -0.014764 | 0.0096705 | 0.0056466 | 0.0072744 | 0.0079267 | -0.0079521 | 0.042613 | 0.0024549 | 0.028518 | 0.001407 | -0.008409 | 0.19864 | -0.050009 | 0.43957 | 0.15215 | 0.042256 | 0.004938 | -0.015143 | 0.15776 | 0.29758 | -0.17539 | -0.29693 | 122.5215 | -0.007358 | 122.3979 | 122.361 | -0.16056 | -0.256 | 0.23358 | 122.0725 | -0.04823 | 122.4116 | 122.3542 | 0.28179 | 0.091586 | -0.38139 | 122.568 | 122.3194 | 122.809 | 122.3708 | -0.053842 | 122.5271 | 122.667 | 122.194 | 122.3743 | -0.50293
2143.4844 | 122.6715 | -122.3145 | 0.18768 | 1.4211e-13 | -0.010431 | -0.0026347 | 0.029578 | -0.014337 | 0.0098841 | -0.0019839 | 0.007488 | 0.0077131 | -0.0079521 | 0.042399 | 0.0026685 | 0.037675 | 0.001407 | 0.000747 | 0.19864 | -0.050009 | 0.44415 | 0.15673 | 0.046835 | 0.004938 | -0.015143 | 0.16234 | 0.30674 | -0.17539 | -0.29693 | 122.4712 | 0.010953 | 122.3521 | 122.3152 | -0.15598 | -0.23769 | 0.25647 | 122.0175 | -0.025341 | 122.3613 | 122.2993 | 0.28179 | 0.11905 | -0.36308 | 122.5131 | 122.2644 | 122.7586 | 122.3159 | -0.030952 | 122.4768 | 122.6212 | 122.1391 | 122.3194 | -0.48462
2145.1719 | 122.5754 | -122.3831 | 0.21515 | 1.4211e-13 | -0.010431 | -0.0026347 | 0.029792 | -0.01455 | 0.0096705 | 0.013277 | 0.0072744 | 0.0074993 | -0.0079521 | 0.042827 | 0.0024549 | 0.046831 | 0.005985 | 0.000747 | 0.19864 | 0.027833 | 0.44873 | 0.15673 | 0.046835 | 0.014095 | -0.019721 | 0.15318 | 0.30216 | -0.17081 | -0.30151 | 122.5398 | -0.016513 | 122.4299 | 122.3839 | -0.15598 | -0.18732 | 0.23358 | 122.0816 | -0.061964 | 122.43 | 122.3634 | 0.28179 | 0.087009 | -0.38596 | 122.5818 | 122.411 | 122.8319 | 122.3891 | -0.058418 | 122.5363 | 122.6853 | 122.2123 | 122.3972 | -0.51666
2146.9062 | 122.5891 | -122.3831 | 0.2243 | 1.4211e-13 | -0.010645 | -0.0026347 | 0.029364 | -0.01455 | 0.0096705 | -0.0096144 | 0.0072744 | 0.0072857 | -0.0081657 | 0.042827 | 0.0024549 | 0.033096 | 0.005985 | 0.000747 | 0.19864 | -0.059167 | 0.44873 | 0.15215 | 0.046835 | 0.014095 | -0.019721 | 0.16234 | 0.30674 | -0.17081 | -0.29236 | 122.5353 | -0.025668 | 122.4162 | 122.3839 | -0.15141 | -0.28347 | 0.22443 | 122.0908 | -0.061962 | 122.43 | 122.3634 | 0.27264 | 0.082433 | -0.39512 | 122.5818 | 122.324 | 122.8319 | 122.3891 | -0.072152 | 122.5455 | 122.6899 | 122.2123 | 122.3972 | -0.51666
2148.6562 | 122.7081 | -122.3511 | 0.18768 | 1.4211e-13 | -0.010218 | -0.0026347 | 0.029578 | -0.01455 | 0.0098841 | -0.0019839 | 0.007488 | 0.0072857 | -0.0081657 | 0.042613 | 0.0024549 | 0.046831 | 0.005985 | -0.003831 | 0.18948 | -0.054588 | 0.44415 | 0.15673 | 0.046835 | 0.004938 | -0.015143 | 0.15776 | 0.30216 | -0.17081 | -0.30151 | 122.5078 | 0.001796 | 122.3979 | 122.3472 | -0.16056 | -0.24227 | 0.25647 | 122.0496 | -0.029919 | 122.3979 | 122.3359 | 0.28637 | 0.11447 | -0.3585 | 122.5406 | 122.2965 | 122.7952 | 122.3571 | -0.030952 | 122.5088 | 122.6532 | 122.1803 | 122.356 | -0.4892
2150.4219 | 122.6624 | -122.3511 | 0.20599 | 1.4211e-13 | -0.010431 | -0.0026347 | 0.029578 | -0.014978 | 0.0098841 | 0.0056466 | 0.006847 | 0.0077131 | -0.0081657 | 0.042827 | 0.0024549 | 0.033096 | 0.001407 | 0.000747 | 0.20321 | -0.022536 | 0.44873 | 0.14757 | 0.046835 | 0.004938 | -0.019721 | 0.1715 | 0.29758 | -0.17081 | -0.29693 | 122.4986 | -0.00278 | 122.3842 | 122.3518 | -0.14683 | -0.22853 | 0.24274 | 122.0541 | -0.034495 | 122.3979 | 122.3314 | 0.27721 | 0.091586 | -0.37681 | 122.5543 | 122.3285 | 122.7998 | 122.3525 | -0.058421 | 122.5226 | 122.6487 | 122.1803 | 122.356 | -0.50293
2152.1094 | 122.5525 | -122.4152 | 0.2243 | 1.4211e-13 | -0.010004 | -0.0024209 | 0.030005 | -0.01455 | 0.0096705 | 0.0056466 | 0.0077016 | 0.0074993 | -0.0079521 | 0.042399 | 0.0024549 | 0.033096 | -0.007751 | 0.000747 | 0.19406 | -0.063746 | 0.43957 | 0.14757 | 0.042256 | 0.009516 | -0.019721 | 0.16234 | 0.30216 | -0.17081 | -0.30151 | 122.5627 | -0.030246 | 122.4483 | 122.4159 | -0.14683 | -0.28805 | 0.21527 | 122.1136 | -0.061962 | 122.4574 | 122.3954 | 0.28179 | 0.077854 | -0.39512 | 122.6092 | 122.3514 | 122.8547 | 122.4074 | -0.076731 | 122.5775 | 122.7173 | 122.2443 | 122.4247 | -0.52582
2153.8594 | 122.5937 | -122.374 | 0.22888 | 1.4211e-13 | -0.010645 | -0.0026347 | 0.029578 | -0.014764 | 0.0098841 | -0.0019839 | 0.0070608 | 0.0072857 | -0.0079521 | 0.042185 | 0.0024549 | 0.037675 | -0.003172 | -0.012988 | 0.18948 | -0.063746 | 0.44415 | 0.15215 | 0.042256 | 0.004938 | -0.0243 | 0.15776 | 0.29758 | -0.16624 | -0.28778 | 122.5261 | -0.039403 | 122.4116 | 122.361 | -0.16514 | -0.29263 | 0.21527 | 122.0862 | -0.071118 | 122.4162 | 122.3497 | 0.26348 | 0.068698 | -0.39512 | 122.5634 | 122.3102 | 122.8181 | 122.3708 | -0.07673 | 122.5317 | 122.6715 | 122.2077 | 122.3789 | -0.51666
2155.6094 | 122.6486 | -122.3831 | 0.21973 | 1.4211e-13 | -0.010218 | -0.0028483 | 0.029578 | -0.01455 | 0.0098841 | -0.0019839 | 0.0072744 | 0.0074993 | -0.0081657 | 0.042185 | 0.0022413 | 0.033096 | 0.001407 | -0.008409 | 0.18948 | -0.068325 | 0.44415 | 0.15215 | 0.042256 | 0.004938 | -0.0243 | 0.16234 | 0.30216 | -0.17081 | -0.29236 | 122.5353 | -0.030248 | 122.4162 | 122.3747 | -0.16056 | -0.28805 | 0.22443 | 122.0908 | -0.057385 | 122.4254 | 122.3588 | 0.26806 | 0.082431 | -0.39054 | 122.5726 | 122.3148 | 122.8273 | 122.3845 | -0.067575 | 122.5455 | 122.6853 | 122.2123 | 122.3881 | -0.51208
2157.3594 | 122.5845 | -122.4014 | 0.23804 | 1.4211e-13 | -0.010218 | -0.0030619 | 0.029792 | -0.014764 | 0.0098841 | 0.013277 | 0.0072744 | 0.0077131 | -0.0079521 | 0.042613 | 0.0024549 | 0.037675 | 0.001407 | -0.012988 | 0.20321 | -0.031693 | 0.43957 | 0.14299 | 0.02852 | 0.004938 | -0.015143 | 0.16234 | 0.30674 | -0.17539 | -0.28778 | 122.5444 | -0.034823 | 122.4391 | 122.3884 | -0.15598 | -0.26973 | 0.20154 | 122.1137 | -0.075695 | 122.4299 | 122.3863 | 0.27263 | 0.0687 | -0.41343 | 122.6046 | 122.3697 | 122.841 | 122.4028 | -0.095043 | 122.5638 | 122.7082 | 122.226 | 122.4064 | -0.52581
2159.0469 | 122.699 | -122.3785 | 0.21515 | 1.4211e-13 | -0.010431 | -0.0024209 | 0.029792 | -0.014764 | 0.0098841 | -0.0019839 | 0.0072744 | 0.0077131 | -0.0077383 | 0.042399 | 0.0024549 | 0.033096 | 0.001407 | 0.000747 | 0.19864 | -0.063746 | 0.44873 | 0.15215 | 0.037677 | 0.000359 | -0.015143 | 0.15318 | 0.28842 | -0.17539 | -0.28778 | 122.5307 | -0.016513 | 122.4116 | 122.3793 | -0.15141 | -0.2789 | 0.23358 | 122.0908 | -0.061964 | 122.4162 | 122.3634 | 0.27263 | 0.073274 | -0.39054 | 122.5772 | 122.3148 | 122.8273 | 122.3799 | -0.062997 | 122.5317 | 122.667 | 122.2031 | 122.3789 | -0.50293
2160.7969 | 122.6761 | -122.3831 | 0.21515 | 1.4211e-13 | -0.010004 | -0.0028483 | 0.029792 | -0.01455 | 0.0098841 | 0.0056466 | 0.0072744 | 0.0074993 | -0.0079521 | 0.042399 | 0.0022413 | 0.033096 | 0.001407 | -0.003831 | 0.19864 | -0.059167 | 0.43957 | 0.16131 | 0.046835 | 0.014095 | -0.019721 | 0.16692 | 0.30216 | -0.16624 | -0.29693 | 122.5444 | -0.016513 | 122.4162 | 122.3793 | -0.16514 | -0.27432 | 0.22443 | 122.0862 | -0.048228 | 122.43 | 122.3634 | 0.27721 | 0.087009 | -0.38138 | 122.5818 | 122.324 | 122.8227 | 122.3845 | -0.053839 | 122.55 | 122.6853 | 122.2169 | 122.3972 | -0.51208
2162.5312 | 122.6898 | -122.3969 | 0.21515 | 1.4211e-13 | -0.010218 | -0.0024209 | 0.029792 | -0.014764 | 0.0098841 | -0.0019839 | 0.0072744 | 0.0074993 | -0.0079521 | 0.042399 | 0.0024549 | 0.042253 | 0.001407 | -0.008409 | 0.20321 | -0.063746 | 0.435 | 0.14757 | 0.046835 | 0.009516 | -0.019721 | 0.16234 | 0.29758 | -0.17081 | -0.29236 | 122.5444 | -0.011935 | 122.4391 | 122.3884 | -0.15598 | -0.2789 | 0.21985 | 122.1045 | -0.052807 | 122.4437 | 122.3771 | 0.27264 | 0.082431 | -0.38596 | 122.6001 | 122.3331 | 122.8318 | 122.3983 | -0.067576 | 122.5592 | 122.6944 | 122.226 | 122.4064 | -0.5075
2164.2812 | 122.5983 | -122.3923 | 0.21057 | 1.4211e-13 | -0.010645 | -0.0026347 | 0.029578 | -0.014337 | 0.0098841 | 0.013277 | 0.006847 | 0.0072857 | -0.0083793 | 0.042613 | 0.0024549 | 0.033096 | 0.005985 | 0.000747 | 0.19864 | -0.063746 | 0.42584 | 0.15673 | 0.051413 | 0.004938 | -0.0243 | 0.16234 | 0.30216 | -0.17997 | -0.29236 | 122.549 | -0.011935 | 122.4254 | 122.393 | -0.15598 | -0.27432 | 0.21527 | 122.0999 | -0.048229 | 122.4437 | 122.368 | 0.26806 | 0.091587 | -0.39054 | 122.5909 | 122.3285 | 122.8181 | 122.3983 | -0.05384 | 122.5546 | 122.6944 | 122.2123 | 122.3972 | -0.50293
2166.0469 | 122.6166 | -122.4152 | 0.21973 | 1.4211e-13 | -0.010431 | -0.0028483 | 0.029364 | -0.014764 | 0.0096705 | 0.0056466 | 0.0072744 | 0.0077131 | -0.0081657 | 0.042399 | 0.0020275 | 0.037675 | -0.003172 | -0.003831 | 0.19864 | -0.059167 | 0.44415 | 0.15673 | 0.042256 | 0.009516 | -0.019721 | 0.15776 | 0.30216 | -0.17539 | -0.29693 | 122.5719 | -0.021091 | 122.4528 | 122.4113 | -0.16056 | -0.27889 | 0.22443 | 122.1182 | -0.061963 | 122.4574 | 122.3954 | 0.27721 | 0.082431 | -0.39512 | 122.6138 | 122.356 | 122.8593 | 122.412 | -0.062996 | 122.5729 | 122.7173 | 122.2398 | 122.4247 | -0.51666
2167.75 | 122.612 | -122.4243 | 0.25177 | 1.4211e-13 | -0.010645 | -0.0028483 | 0.030005 | -0.01455 | 0.0096705 | -0.0019839 | 0.0072744 | 0.0074993 | -0.0079521 | 0.042613 | 0.0022413 | 0.046831 | 0.001407 | -0.003831 | 0.19864 | -0.068325 | 0.44415 | 0.16131 | 0.037677 | 0.014095 | -0.015143 | 0.15776 | 0.29758 | -0.16624 | -0.29236 | 122.5856 | -0.053134 | 122.4711 | 122.4205 | -0.16514 | -0.3201 | 0.19238 | 122.132 | -0.094006 | 122.462 | 122.4092 | 0.27721 | 0.04581 | -0.41801 | 122.623 | 122.356 | 122.8685 | 122.4257 | -0.09046 | 122.5821 | 122.7219 | 122.2581 | 122.4384 | -0.54413
2169.5156 | 122.6624 | -122.4289 | 0.21515 | 1.4211e-13 | -0.010431 | -0.0024209 | 0.029578 | -0.01455 | 0.010098 | -0.0019839 | 0.0072744 | 0.0074993 | -0.0081657 | 0.042399 | 0.0022413 | 0.037675 | 0.001407 | -0.003831 | 0.19864 | -0.059167 | 0.44415 | 0.15673 | 0.042256 | 0.014095 | -0.019721 | 0.16692 | 0.30674 | -0.17081 | -0.29236 | 122.5856 | -0.016513 | 122.4666 | 122.4251 | -0.16056 | -0.27432 | 0.229 | 122.1365 | -0.048228 | 122.4711 | 122.4092 | 0.27264 | 0.091588 | -0.38596 | 122.6275 | 122.3697 | 122.873 | 122.4303 | -0.058418 | 122.5958 | 122.7356 | 122.2581 | 122.443 | -0.5075
2171.2031 | 122.7722 | -122.3785 | 0.20599 | 1.4211e-13 | -0.010218 | -0.0028483 | 0.029151 | -0.01455 | 0.0098841 | 0.0056466 | 0.0077016 | 0.0074993 | -0.0081657 | 0.042613 | 0.0026685 | 0.037675 | -0.007751 | -0.008409 | 0.20321 | -0.063746 | 0.43957 | 0.15673 | 0.051413 | 0.004938 | -0.015143 | 0.15776 | 0.30674 | -0.16624 | -0.29693 | 122.5353 | -0.00278 | 122.4162 | 122.3701 | -0.16514 | -0.26974 | 0.23358 | 122.0816 | -0.04823 | 122.43 | 122.3634 | 0.28179 | 0.10074 | -0.37223 | 122.5818 | 122.3148 | 122.8181 | 122.3708 | -0.049263 | 122.5363 | 122.6853 | 122.2123 | 122.3835 | -0.50293
2172.9531 | 122.6349 | -122.4243 | 0.2243 | 1.4211e-13 | -0.010218 | -0.0028483 | 0.030005 | -0.01455 | 0.0098841 | 0.013277 | 0.0070608 | 0.0074993 | -0.0079521 | 0.042185 | 0.0024549 | 0.046831 | 0.005985 | -0.003831 | 0.19406 | -0.059167 | 0.44873 | 0.15673 | 0.051413 | 0.009516 | -0.0243 | 0.16692 | 0.30674 | -0.17997 | -0.29236 | 122.581 | -0.030246 | 122.4711 | 122.4205 | -0.16056 | -0.28347 | 0.22443 | 122.132 | -0.057383 | 122.4757 | 122.4 | 0.26806 | 0.082433 | -0.40428 | 122.6184 | 122.3651 | 122.873 | 122.4303 | -0.067573 | 122.5912 | 122.7311 | 122.2443 | 122.4338 | -0.51666
2174.6406 | 122.6074 | -122.4518 | 0.21973 | 1.4211e-13 | -0.010645 | -0.0028483 | 0.029792 | -0.01455 | 0.010525 | -0.0096144 | 0.0072744 | 0.0074993 | -0.0081657 | 0.042613 | 0.0024549 | 0.033096 | -0.007751 | -0.017566 | 0.19406 | -0.063746 | 0.44415 | 0.16131 | 0.042256 | 0.000359 | -0.0243 | 0.16234 | 0.30674 | -0.17081 | -0.29693 | 122.6131 | -0.025669 | 122.4849 | 122.4342 | -0.17888 | -0.28347 | 0.22443 | 122.1548 | -0.057385 | 122.494 | 122.4275 | 0.27263 | 0.08701 | -0.39054 | 122.6458 | 122.388 | 122.8959 | 122.444 | -0.058417 | 122.6141 | 122.7585 | 122.281 | 122.4521 | -0.51666
2176.4062 | 122.6257 | -122.438 | 0.22888 | 1.4211e-13 | -0.010218 | -0.0032757 | 0.029578 | -0.01455 | 0.0098841 | -0.0019839 | 0.0070608 | 0.0074993 | -0.0081657 | 0.042399 | 0.0024549 | 0.037675 | 0.001407 | -0.017566 | 0.19864 | -0.063746 | 0.43957 | 0.15673 | 0.037677 | 0.014095 | -0.019721 | 0.16692 | 0.30674 | -0.17081 | -0.29693 | 122.5948 | -0.030246 | 122.4757 | 122.4205 | -0.1743 | -0.29263 | 0.21069 | 122.1411 | -0.061961 | 122.4757 | 122.4183 | 0.27721 | 0.077855 | -0.3997 | 122.6367 | 122.3743 | 122.8776 | 122.4395 | -0.072151 | 122.605 | 122.7448 | 122.2672 | 122.4521 | -0.52582
2178.1562 | 122.7448 | -122.3877 | 0.20599 | 1.4211e-13 | -0.010431 | -0.0030619 | 0.029364 | -0.014978 | 0.0098841 | 0.0056466 | 0.0072744 | 0.0074993 | -0.0081657 | 0.042399 | 0.0026685 | 0.028518 | 0.005985 | -0.008409 | 0.19864 | -0.059167 | 0.435 | 0.15673 | 0.042256 | 0.009516 | -0.019721 | 0.16234 | 0.30674 | -0.17081 | -0.30609 | 122.5444 | -0.007358 | 122.4162 | 122.3793 | -0.16514 | -0.26516 | 0.229 | 122.0816 | -0.043652 | 122.43 | 122.368 | 0.28637 | 0.10074 | -0.37681 | 122.5863 | 122.3285 | 122.8227 | 122.3937 | -0.049263 | 122.55 | 122.6944 | 122.2169 | 122.3972 | -0.51209
2179.9219 | 122.7631 | -122.3969 | 0.1831 | 1.4211e-13 | -0.010218 | -0.0028483 | 0.029792 | -0.014337 | 0.0098841 | 0.0056466 | 0.0072744 | 0.0077131 | -0.0083793 | 0.042613 | 0.0024549 | 0.033096 | 0.001407 | -0.012988 | 0.19406 | -0.063746 | 0.44415 | 0.15215 | 0.046835 | 0.004938 | -0.0243 | 0.15318 | 0.30216 | -0.17539 | -0.29236 | 122.549 | 0.010953 | 122.4299 | 122.3839 | -0.16514 | -0.24685 | 0.26105 | 122.1045 | -0.02992 | 122.4437 | 122.3726 | 0.26806 | 0.11905 | -0.3585 | 122.5909 | 122.3331 | 122.841 | 122.3983 | -0.030953 | 122.55 | 122.699 | 122.2215 | 122.4018 | -0.47546
2181.6094 | 122.7493 | -122.3831 | 0.20599 | 1.4211e-13 | -0.010645 | -0.0026347 | 0.029578 | -0.014764 | 0.010098 | 0.0056466 | 0.007488 | 0.0074993 | -0.0081657 | 0.042185 | 0.0024549 | 0.037675 | -0.003172 | -0.012988 | 0.19864 | -0.059167 | 0.44415 | 0.15215 | 0.042256 | 0.004938 | -0.019721 | 0.16234 | 0.30216 | -0.17081 | -0.29693 | 122.5353 | -0.007358 | 122.4208 | 122.3701 | -0.16514 | -0.26516 | 0.23816 | 122.0862 | -0.043652 | 122.4254 | 122.3634 | 0.27721 | 0.096164 | -0.37681 | 122.5818 | 122.324 | 122.8273 | 122.3799 | -0.053842 | 122.5455 | 122.6853 | 122.2123 | 122.3881 | -0.50293
2183.3594 | 122.7081 | -122.406 | 0.20599 | 1.4211e-13 | -0.010218 | -0.0026347 | 0.029792 | -0.01455 | 0.0098841 | -0.0019839 | 0.0072744 | 0.0077131 | -0.0079521 | 0.042399 | 0.0024549 | 0.037675 | 0.001407 | 0.005325 | 0.19864 | -0.063746 | 0.44415 | 0.16131 | 0.037677 | 0.009516 | -0.015143 | 0.16234 | 0.30216 | -0.16624 | -0.29693 | 122.5673 | -0.007358 | 122.4437 | 122.4113 | -0.15599 | -0.26974 | 0.23816 | 122.1091 | -0.043652 | 122.4437 | 122.3909 | 0.28179 | 0.096164 | -0.37223 | 122.6046 | 122.3423 | 122.8502 | 122.4074 | -0.044684 | 122.5683 | 122.7082 | 122.2398 | 122.4155 | -0.50293
2185.125 | 122.6532 | -122.4564 | 0.23346 | 1.4211e-13 | -0.010218 | -0.0030619 | 0.029578 | -0.014764 | 0.0098841 | 0.0056466 | 0.0072744 | 0.0072857 | -0.0079521 | 0.042185 | 0.0024549 | 0.042253 | 0.010564 | -0.003831 | 0.19406 | -0.054588 | 0.44415 | 0.15673 | 0.042256 | 0.009516 | -0.015143 | 0.16692 | 0.30674 | -0.16624 | -0.29693 | 122.6131 | -0.039401 | 122.4986 | 122.4525 | -0.16056 | -0.28805 | 0.21069 | 122.1594 | -0.066538 | 122.4986 | 122.4412 | 0.28179 | 0.073278 | -0.3997 | 122.6504 | 122.4018 | 122.9005 | 122.4669 | -0.076728 | 122.6233 | 122.7631 | 122.2901 | 122.4659 | -0.53039
2186.8125 | 122.7814 | -122.4152 | 0.19226 | 1.4211e-13 | -0.010218 | -0.0022073 | 0.029792 | -0.01455 | 0.0098841 | 0.0056466 | 0.007488 | 0.0074993 | -0.0079521 | 0.042613 | 0.0026685 | 0.042253 | 0.001407 | -0.008409 | 0.19864 | -0.054588 | 0.44415 | 0.14757 | 0.042256 | 0.000359 | -0.019721 | 0.16234 | 0.293 | -0.17081 | -0.28778 | 122.5627 | 0.006375 | 122.4574 | 122.4068 | -0.15598 | -0.24685 | 0.25189 | 122.1274 | -0.029919 | 122.4574 | 122.3954 | 0.26806 | 0.10074 | -0.36308 | 122.6138 | 122.3606 | 122.8593 | 122.4166 | -0.044688 | 122.5775 | 122.7082 | 122.2443 | 122.4155 | -0.48004
2188.5781 | 122.731 | -122.3969 | 0.19684 | 1.4211e-13 | -0.010431 | -0.0032757 | 0.029578 | -0.01455 | 0.0098841 | 0.013277 | 0.006847 | 0.0072857 | -0.0079521 | 0.042613 | 0.0022413 | 0.05141 | 0.001407 | -0.012988 | 0.19864 | -0.059167 | 0.44415 | 0.16131 | 0.042256 | 0.009516 | -0.015143 | 0.15318 | 0.30674 | -0.17539 | -0.29693 | 122.5582 | 0.001798 | 122.4483 | 122.3839 | -0.1743 | -0.25601 | 0.24732 | 122.0999 | -0.043653 | 122.4391 | 122.3817 | 0.28179 | 0.1099 | -0.37223 | 122.5955 | 122.3377 | 122.841 | 122.3983 | -0.035528 | 122.55 | 122.7036 | 122.2215 | 122.4064 | -0.49377
2190.3438 | 122.7448 | -122.4197 | 0.19226 | 1.4211e-13 | -0.010431 | -0.0024209 | 0.029578 | -0.01455 | 0.010098 | 0.0056466 | 0.0070608 | 0.0077131 | -0.0079521 | 0.042827 | 0.0026685 | 0.033096 | 0.001407 | -0.012988 | 0.19864 | -0.059167 | 0.435 | 0.15673 | 0.033099 | 0.000359 | -0.015143 | 0.16234 | 0.29758 | -0.17081 | -0.29236 | 122.5765 | 0.006375 | 122.4528 | 122.4068 | -0.16972 | -0.25143 | 0.24274 | 122.1274 | -0.029919 | 122.4528 | 122.4046 | 0.27721 | 0.10532 | -0.36308 | 122.6184 | 122.3606 | 122.8547 | 122.4211 | -0.03553 | 122.5821 | 122.7173 | 122.2489 | 122.4201 | -0.48462
2192.0938 | 122.7997 | -122.4197 | 0.18768 | 1.4211e-13 | -0.010431 | -0.0028483 | 0.029578 | -0.014764 | 0.0098841 | 0.0056466 | 0.007488 | 0.0077131 | -0.0079521 | 0.042613 | 0.0024549 | 0.037675 | 0.001407 | -0.008409 | 0.19864 | -0.063746 | 0.44415 | 0.14757 | 0.037677 | 0.009516 | -0.019721 | 0.16234 | 0.30216 | -0.17081 | -0.29236 | 122.5673 | 0.010953 | 122.4574 | 122.4113 | -0.15598 | -0.25143 | 0.25647 | 122.1274 | -0.025341 | 122.4574 | 122.4 | 0.27264 | 0.11447 | -0.3585 | 122.6184 | 122.356 | 122.8639 | 122.4211 | -0.04011 | 122.5821 | 122.7219 | 122.2489 | 122.4293 | -0.48004
2193.7969 | 122.7722 | -122.406 | 0.20142 | 1.4211e-13 | -0.010218 | -0.0028483 | 0.029578 | -0.01455 | 0.010098 | -0.0019839 | 0.0070608 | 0.0077131 | -0.0081657 | 0.042399 | 0.0024549 | 0.033096 | -0.003172 | -0.008409 | 0.19406 | -0.054588 | 0.44415 | 0.15673 | 0.042256 | 0.009516 | -0.015143 | 0.15776 | 0.30216 | -0.16624 | -0.28778 | 122.5627 | -0.007358 | 122.4391 | 122.3976 | -0.16514 | -0.256 | 0.24274 | 122.1182 | -0.043652 | 122.4483 | 122.3909 | 0.27263 | 0.10074 | -0.36765 | 122.6001 | 122.3514 | 122.8502 | 122.4028 | -0.044685 | 122.5638 | 122.7082 | 122.2398 | 122.4155 | -0.48919
2195.5469 | 122.7448 | -122.4152 | 0.20142 | 1.4211e-13 | -0.010431 | -0.0028483 | 0.030005 | -0.01455 | 0.0098841 | -0.0019839 | 0.0072744 | 0.0079267 | -0.0079521 | 0.042399 | 0.0024549 | 0.037675 | -0.007751 | -0.008409 | 0.19406 | -0.04543 | 0.43957 | 0.15673 | 0.042256 | 0.004938 | -0.0243 | 0.16692 | 0.30674 | -0.16624 | -0.29236 | 122.5719 | -0.007358 | 122.4528 | 122.4068 | -0.16514 | -0.24685 | 0.23816 | 122.1228 | -0.034495 | 122.4574 | 122.3909 | 0.26806 | 0.10532 | -0.36765 | 122.6092 | 122.3697 | 122.8547 | 122.4074 | -0.044685 | 122.5821 | 122.7219 | 122.2489 | 122.4201 | -0.49377
2197.2969 | 122.7676 | -122.4289 | 0.19684 | 1.4211e-13 | -0.010645 | -0.0032757 | 0.029792 | -0.014764 | 0.0098841 | 0.0056466 | 0.007488 | 0.0072857 | -0.0079521 | 0.042399 | 0.0022413 | 0.028518 | 0.001407 | -0.008409 | 0.20321 | -0.059167 | 0.44415 | 0.15215 | 0.042256 | 0.004938 | -0.0243 | 0.1715 | 0.29758 | -0.17081 | -0.30151 | 122.581 | 0.006376 | 122.4574 | 122.4205 | -0.16056 | -0.25601 | 0.24732 | 122.1274 | -0.025339 | 122.4711 | 122.4046 | 0.27721 | 0.10074 | -0.36765 | 122.6321 | 122.3697 | 122.873 | 122.4303 | -0.044686 | 122.6004 | 122.7265 | 122.2581 | 122.4338 | -0.49835
2199.0625 | 122.644 | -122.4884 | 0.24719 | 1.4211e-13 | -0.010431 | -0.0026347 | 0.029578 | -0.01455 | 0.010311 | 0.013277 | 0.007488 | 0.0079267 | -0.0081657 | 0.042613 | 0.0024549 | 0.033096 | -0.003172 | -0.022144 | 0.18948 | -0.068325 | 0.43957 | 0.14757 | 0.046835 | 0.009516 | -0.0243 | 0.16234 | 0.31132 | -0.17081 | -0.30151 | 122.636 | -0.057713 | 122.5215 | 122.4663 | -0.16972 | -0.31552 | 0.19238 | 122.1869 | -0.08485 | 122.5352 | 122.4641 | 0.27721 | 0.064124 | -0.41801 | 122.6779 | 122.4201 | 122.928 | 122.4852 | -0.099619 | 122.6507 | 122.7997 | 122.3176 | 122.4979 | -0.5487
2200.75 | 122.7768 | -122.438 | 0.20142 | 1.4211e-13 | -0.010431 | -0.0028483 | 0.029578 | -0.01455 | 0.0096705 | 0.0056466 | 0.0072744 | 0.0077131 | -0.0079521 | 0.042399 | 0.0022413 | 0.037675 | -0.003172 | -0.017566 | 0.19864 | -0.063746 | 0.43957 | 0.15215 | 0.042256 | 0.000359 | -0.0243 | 0.15776 | 0.30216 | -0.17081 | -0.30151 | 122.5902 | -0.00278 | 122.4757 | 122.4205 | -0.16972 | -0.26516 | 0.23816 | 122.1365 | -0.043652 | 122.4803 | 122.4137 | 0.27721 | 0.10074 | -0.37223 | 122.6367 | 122.3743 | 122.8776 | 122.4349 | -0.049264 | 122.5958 | 122.7402 | 122.2672 | 122.4384 | -0.50293
2202.5 | 122.6303 | -122.4701 | 0.23346 | 1.4211e-13 | -0.010645 | -0.0030619 | 0.029578 | -0.01455 | 0.010311 | 0.0056466 | 0.0070608 | 0.0070721 | -0.0081657 | 0.042185 | 0.0024549 | 0.033096 | 0.001407 | -0.017566 | 0.18948 | -0.063746 | 0.43957 | 0.15215 | 0.051413 | 0.009516 | -0.0243 | 0.16234 | 0.29758 | -0.17081 | -0.29693 | 122.6222 | -0.04398 | 122.5032 | 122.4525 | -0.16972 | -0.2972 | 0.20612 | 122.1732 | -0.071117 | 122.5215 | 122.4458 | 0.27263 | 0.064121 | -0.40427 | 122.6596 | 122.4063 | 122.9097 | 122.4715 | -0.081307 | 122.6324 | 122.7677 | 122.2993 | 122.4796 | -0.53039
2204.25 | 122.8043 | -122.4335 | 0.19684 | 1.4211e-13 | -0.010431 | -0.0028483 | 0.029578 | -0.01455 | 0.0096705 | -0.0019839 | 0.0072744 | 0.0077131 | -0.0081657 | 0.042613 | 0.0020275 | 0.033096 | 0.001407 | -0.017566 | 0.19406 | -0.068325 | 0.44415 | 0.15215 | 0.046835 | 0.000359 | -0.0243 | 0.16692 | 0.30216 | -0.17081 | -0.29693 | 122.5856 | -0.00278 | 122.4666 | 122.4159 | -0.16972 | -0.26516 | 0.24732 | 122.1365 | -0.029917 | 122.4803 | 122.4092 | 0.27263 | 0.10532 | -0.36765 | 122.6275 | 122.3651 | 122.8776 | 122.4349 | -0.044686 | 122.6004 | 122.7356 | 122.2627 | 122.4338 | -0.49377
2205.9531 | 122.7127 | -122.4518 | 0.20142 | 1.4211e-13 | -0.010431 | -0.0032757 | 0.029578 | -0.014978 | 0.0094567 | -0.0019839 | 0.0072744 | 0.0074993 | -0.0077383 | 0.042399 | 0.0022413 | 0.042253 | -0.007751 | -0.017566 | 0.19864 | -0.063746 | 0.44415 | 0.15673 | 0.042256 | 0.004938 | -0.0243 | 0.16234 | 0.28842 | -0.17081 | -0.29693 | 122.6085 | -0.00278 | 122.494 | 122.4342 | -0.1743 | -0.26516 | 0.24274 | 122.1548 | -0.039074 | 122.494 | 122.4275 | 0.27263 | 0.087007 | -0.37223 | 122.6504 | 122.388 | 122.8959 | 122.444 | -0.044685 | 122.6141 | 122.7402 | 122.281 | 122.4567 | -0.49835
2207.7031 | 122.6303 | -122.5021 | 0.22888 | 1.4211e-13 | -0.010431 | -0.0026347 | 0.029578 | -0.014764 | 0.0098841 | -0.0019839 | 0.0072744 | 0.0072857 | -0.0081657 | 0.042399 | 0.0024549 | 0.033096 | 0.001407 | -0.022144 | 0.18948 | -0.072904 | 0.435 | 0.14757 | 0.042256 | 0.004938 | -0.019721 | 0.16234 | 0.30216 | -0.16624 | -0.2832 | 122.6497 | -0.039403 | 122.5352 | 122.48 | -0.16972 | -0.30179 | 0.20612 | 122.2189 | -0.06654 | 122.5444 | 122.4824 | 0.26348 | 0.073276 | -0.39512 | 122.6916 | 122.4292 | 122.9371 | 122.5035 | -0.081309 | 122.6645 | 122.8043 | 122.3359 | 122.5071 | -0.51208
2209.3906 | 122.6624 | -122.5021 | 0.23346 | 1.4211e-13 | -0.010431 | -0.0030619 | 0.029792 | -0.014978 | 0.0096705 | 0.013277 | 0.0072744 | 0.0077131 | -0.0079521 | 0.042399 | 0.0022413 | 0.037675 | 0.005985 | -0.003831 | 0.19864 | -0.063746 | 0.44415 | 0.14299 | 0.042256 | 0.009516 | -0.010564 | 0.15776 | 0.28842 | -0.17081 | -0.29693 | 122.6451 | -0.034823 | 122.5398 | 122.4983 | -0.14683 | -0.2972 | 0.21069 | 122.2052 | -0.075695 | 122.5444 | 122.4916 | 0.28637 | 0.054964 | -0.40427 | 122.7008 | 122.4384 | 122.9463 | 122.5081 | -0.090465 | 122.6599 | 122.7906 | 122.3313 | 122.5117 | -0.53039
2211.1406 | 122.6669 | -122.5159 | 0.21973 | 1.4211e-13 | -0.010431 | -0.0030619 | 0.029364 | -0.01455 | 0.0096705 | 0.013277 | 0.0070608 | 0.0077131 | -0.0077383 | 0.042613 | 0.0022413 | 0.033096 | 0.005985 | -0.012988 | 0.19406 | -0.068325 | 0.44415 | 0.15215 | 0.042256 | 0.000359 | -0.0243 | 0.16234 | 0.29758 | -0.16624 | -0.29693 | 122.668 | -0.025669 | 122.549 | 122.5029 | -0.16514 | -0.28805 | 0.22443 | 122.2189 | -0.057385 | 122.5581 | 122.4916 | 0.27263 | 0.077853 | -0.38596 | 122.7099 | 122.4475 | 122.96 | 122.5219 | -0.067575 | 122.6782 | 122.8134 | 122.3496 | 122.5162 | -0.51666
2212.8125 | 122.8134 | -122.4609 | 0.20142 | 1.4211e-13 | -0.010645 | -0.0028483 | 0.029364 | -0.014764 | 0.0096705 | 0.0056466 | 0.0072744 | 0.0072857 | -0.0079521 | 0.042185 | 0.0020275 | 0.037675 | 0.001407 | -0.012988 | 0.19406 | -0.017957 | 0.43957 | 0.15215 | 0.037677 | 0.004938 | -0.028879 | 0.16234 | 0.30216 | -0.16624 | -0.28778 | 122.6131 | -0.007358 | 122.4986 | 122.4479 | -0.16514 | -0.21937 | 0.23816 | 122.1732 | -0.039074 | 122.4986 | 122.4321 | 0.2589 | 0.10074 | -0.36765 | 122.655 | 122.443 | 122.9005 | 122.4623 | -0.049264 | 122.6233 | 122.7631 | 122.2947 | 122.4659 | -0.48919
2214.5625 | 122.7448 | -122.4792 | 0.21515 | 1.4211e-13 | -0.010645 | -0.0030619 | 0.030005 | -0.014764 | 0.0098841 | -0.0019839 | 0.006847 | 0.0077131 | -0.0081657 | 0.042613 | 0.0022413 | 0.033096 | -0.003172 | -0.012988 | 0.19406 | -0.059167 | 0.44415 | 0.16131 | 0.046835 | 0.014095 | -0.019721 | 0.16234 | 0.30216 | -0.16624 | -0.29693 | 122.6406 | -0.021091 | 122.5123 | 122.4663 | -0.1743 | -0.27432 | 0.229 | 122.1823 | -0.052807 | 122.5261 | 122.4595 | 0.27721 | 0.087009 | -0.38138 | 122.6733 | 122.4201 | 122.9234 | 122.4761 | -0.053839 | 122.6416 | 122.7814 | 122.313 | 122.4933 | -0.51208
2216.3281 | 122.8226 | -122.4564 | 0.20142 | 1.4211e-13 | -0.010431 | -0.0032757 | 0.029578 | -0.014764 | 0.010098 | -0.0096144 | 0.0072744 | 0.0072857 | -0.0081657 | 0.042399 | 0.0022413 | 0.037675 | -0.003172 | -0.008409 | 0.18948 | -0.059167 | 0.44415 | 0.15673 | 0.042256 | 0.004938 | -0.019721 | 0.16234 | 0.30216 | -0.17081 | -0.29236 | 122.6131 | -0.011937 | 122.494 | 122.448 | -0.16514 | -0.26058 | 0.24274 | 122.164 | -0.039074 | 122.4986 | 122.4366 | 0.27264 | 0.10074 | -0.37223 | 122.6458 | 122.3972 | 122.9005 | 122.4532 | -0.044685 | 122.6187 | 122.7585 | 122.2855 | 122.4613 | -0.49377
2218.0781 | 122.7905 | -122.4472 | 0.18768 | 1.4211e-13 | -0.010431 | -0.0030619 | 0.029578 | -0.01455 | 0.0098841 | 0.0056466 | 0.0072744 | 0.0077131 | -0.0077383 | 0.042399 | 0.0022413 | 0.033096 | 0.001407 | -0.012988 | 0.19406 | -0.063746 | 0.43957 | 0.15215 | 0.037677 | 0.004938 | -0.019721 | 0.16234 | 0.30216 | -0.16624 | -0.28778 | 122.5994 | 0.006375 | 122.4803 | 122.4342 | -0.16514 | -0.25143 | 0.25189 | 122.1594 | -0.025341 | 122.4849 | 122.4275 | 0.26806 | 0.11447 | -0.35392 | 122.6413 | 122.3835 | 122.8868 | 122.4486 | -0.035531 | 122.6095 | 122.7494 | 122.281 | 122.4521 | -0.47546
2219.7656 | 122.7356 | -122.4838 | 0.22888 | 1.4211e-13 | -0.010218 | -0.0028483 | 0.029792 | -0.01455 | 0.0098841 | 0.013277 | 0.007488 | 0.0074993 | -0.0083793 | 0.042613 | 0.0018139 | 0.033096 | 0.005985 | -0.008409 | 0.18948 | -0.068325 | 0.44415 | 0.15215 | 0.042256 | 0.018674 | -0.0243 | 0.16234 | 0.29758 | -0.16166 | -0.29236 | 122.636 | -0.039403 | 122.5169 | 122.4754 | -0.16056 | -0.29721 | 0.21527 | 122.1915 | -0.06654 | 122.5261 | 122.4595 | 0.26806 | 0.068698 | -0.39054 | 122.6733 | 122.4155 | 122.928 | 122.4898 | -0.07673 | 122.6462 | 122.7814 | 122.3222 | 122.5025 | -0.52124
2221.5469 | 122.7036 | -122.4747 | 0.21973 | 1.4211e-13 | -0.010431 | -0.0028483 | 0.029578 | -0.01455 | 0.0098841 | -0.0019839 | 0.0070608 | 0.0079267 | -0.0081657 | 0.042613 | 0.0022413 | 0.037675 | 0.001407 | -0.012988 | 0.20321 | -0.059167 | 0.43957 | 0.15673 | 0.037677 | 0.009516 | -0.019721 | 0.16234 | 0.293 | -0.17081 | -0.29693 | 122.6314 | -0.016513 | 122.5123 | 122.4617 | -0.16972 | -0.27889 | 0.21985 | 122.1777 | -0.057385 | 122.5123 | 122.4549 | 0.27721 | 0.073274 | -0.39054 | 122.6779 | 122.4155 | 122.9142 | 122.4761 | -0.062996 | 122.637 | 122.7677 | 122.3039 | 122.4842 | -0.51666
2223.2969 | 122.8317 | -122.4564 | 0.21057 | 1.4211e-13 | -0.010859 | -0.0030619 | 0.029578 | -0.014764 | 0.0098841 | 0.0056466 | 0.0070608 | 0.0072857 | -0.0081657 | 0.042827 | 0.0020275 | 0.042253 | 0.001407 | -0.012988 | 0.19406 | -0.063746 | 0.44415 | 0.16589 | 0.037677 | 0.009516 | -0.019721 | 0.16234 | 0.30216 | -0.17081 | -0.29236 | 122.6222 | -0.016513 | 122.4986 | 122.4434 | -0.17888 | -0.27432 | 0.23358 | 122.164 | -0.048229 | 122.494 | 122.4366 | 0.27264 | 0.091587 | -0.38139 | 122.6504 | 122.3926 | 122.9005 | 122.4578 | -0.044682 | 122.6187 | 122.7585 | 122.2855 | 122.4659 | -0.50293
2225.0469 | 122.7768 | -122.4655 | 0.21057 | 1.4211e-13 | -0.010645 | -0.0028483 | 0.029364 | -0.014978 | 0.0098841 | -0.0019839 | 0.0072744 | 0.0074993 | -0.0077383 | 0.042399 | 0.0020275 | 0.028518 | -0.003172 | -0.008409 | 0.19406 | -0.059167 | 0.44415 | 0.15215 | 0.042256 | 0.014095 | -0.0243 | 0.15776 | 0.30674 | -0.16166 | -0.29236 | 122.6177 | -0.016513 | 122.494 | 122.4571 | -0.16056 | -0.26974 | 0.23358 | 122.1732 | -0.052807 | 122.5078 | 122.4412 | 0.26806 | 0.096166 | -0.37223 | 122.6596 | 122.4063 | 122.9097 | 122.4623 | -0.058419 | 122.6233 | 122.7723 | 122.3039 | 122.4796 | -0.50293
2226.7344 | 122.7539 | -122.4747 | 0.2243 | 1.4211e-13 | -0.010859 | -0.0030619 | 0.029578 | -0.014764 | 0.010098 | -0.0019839 | 0.0072744 | 0.0077131 | -0.0083793 | 0.042827 | 0.0020275 | 0.037675 | -0.003172 | -0.012988 | 0.18948 | -0.063746 | 0.44873 | 0.14757 | 0.037677 | 0.009516 | -0.0243 | 0.15776 | 0.30216 | -0.17081 | -0.29693 | 122.6222 | -0.034825 | 122.5123 | 122.4617 | -0.16056 | -0.28805 | 0.22443 | 122.1777 | -0.06654 | 122.5123 | 122.4504 | 0.27263 | 0.077854 | -0.39512 | 122.6641 | 122.4109 | 122.9234 | 122.4715 | -0.076731 | 122.6324 | 122.7768 | 122.3039 | 122.4842 | -0.52124
2228.4844 | 122.8226 | -122.493 | 0.19684 | 1.4211e-13 | -0.010218 | -0.0030619 | 0.029792 | -0.014764 | 0.0096705 | -0.0019839 | 0.007488 | 0.0074993 | -0.0079521 | 0.042399 | 0.0024549 | 0.033096 | -0.003172 | -0.017566 | 0.19864 | -0.04543 | 0.44415 | 0.15673 | 0.042256 | 0.004938 | -0.010564 | 0.15776 | 0.30674 | -0.17081 | -0.29236 | 122.6497 | 0.001798 | 122.5261 | 122.4754 | -0.1743 | -0.24227 | 0.24732 | 122.2006 | -0.039074 | 122.5352 | 122.4824 | 0.28179 | 0.1099 | -0.36765 | 122.6916 | 122.4476 | 122.9371 | 122.4898 | -0.040107 | 122.6507 | 122.7997 | 122.3222 | 122.4979 | -0.48919
2230.2344 | 122.699 | -122.5067 | 0.23346 | 1.4211e-13 | -0.010859 | -0.0030619 | 0.029364 | -0.014978 | 0.0096705 | 0.013277 | 0.0072744 | 0.0077131 | -0.0079521 | 0.042613 | 0.0024549 | 0.037675 | 0.001407 | -0.008409 | 0.19864 | -0.04543 | 0.44415 | 0.14757 | 0.042256 | 0.018674 | -0.015143 | 0.15776 | 0.30216 | -0.17997 | -0.29236 | 122.6543 | -0.034823 | 122.5444 | 122.4983 | -0.15598 | -0.27889 | 0.21069 | 122.2144 | -0.075695 | 122.549 | 122.4916 | 0.27721 | 0.068699 | -0.41343 | 122.7053 | 122.4613 | 122.9509 | 122.5081 | -0.085886 | 122.6645 | 122.8089 | 122.3267 | 122.5254 | -0.52582
2232 | 122.6944 | -122.5342 | 0.24261 | 1.4211e-13 | -0.010859 | -0.0030619 | 0.029792 | -0.014764 | 0.0098841 | 0.0056466 | 0.0072744 | 0.0077131 | -0.0079521 | 0.042613 | 0.0024549 | 0.037675 | -0.003172 | -0.017566 | 0.18948 | -0.059167 | 0.43957 | 0.15673 | 0.037677 | 0.009516 | -0.0243 | 0.16234 | 0.29758 | -0.16624 | -0.29693 | 122.6909 | -0.053136 | 122.5719 | 122.5166 | -0.1743 | -0.30178 | 0.19696 | 122.2372 | -0.080273 | 122.5719 | 122.5099 | 0.27263 | 0.054965 | -0.40885 | 122.7237 | 122.475 | 122.9738 | 122.531 | -0.085884 | 122.6965 | 122.8318 | 122.3679 | 122.5437 | -0.53955
2233.6875 | 122.8226 | -122.4609 | 0.19684 | 1.4211e-13 | -0.010431 | -0.0030619 | 0.029578 | -0.01455 | 0.010098 | -0.0019839 | 0.0072744 | 0.0077131 | -0.0079521 | 0.042613 | 0.0024549 | 0.037675 | 0.010564 | -0.017566 | 0.19406 | -0.054588 | 0.44415 | 0.15673 | 0.037677 | 0.009516 | -0.019721 | 0.16234 | 0.29758 | -0.17081 | -0.28778 | 122.6177 | -0.00278 | 122.4986 | 122.4434 | -0.1743 | -0.25143 | 0.24732 | 122.1732 | -0.034496 | 122.4986 | 122.4412 | 0.26806 | 0.10074 | -0.36765 | 122.655 | 122.4063 | 122.9051 | 122.4715 | -0.040107 | 122.6233 | 122.7585 | 122.2901 | 122.4705 | -0.48462
2235.4375 | 122.731 | -122.5021 | 0.2243 | 1.4211e-13 | -0.010645 | -0.0028483 | 0.029578 | -0.01455 | 0.0098841 | 0.0056466 | 0.0072744 | 0.0074993 | -0.0081657 | 0.042399 | 0.0022413 | 0.037675 | -0.003172 | -0.008409 | 0.19406 | -0.050009 | 0.43957 | 0.16131 | 0.037677 | 0.009516 | -0.019721 | 0.15776 | 0.30216 | -0.17997 | -0.29236 | 122.6634 | -0.030246 | 122.5398 | 122.4937 | -0.16972 | -0.27431 | 0.21527 | 122.2098 | -0.06654 | 122.5398 | 122.4824 | 0.27264 | 0.077854 | -0.40428 | 122.6962 | 122.4521 | 122.9417 | 122.499 | -0.062994 | 122.6599 | 122.8043 | 122.3222 | 122.5117 | -0.51666
2237.1875 | 122.7676 | -122.5067 | 0.22888 | 1.4211e-13 | -0.010859 | -0.0028483 | 0.029364 | -0.014764 | 0.010098 | 0.0056466 | 0.0066334 | 0.0074993 | -0.0081657 | 0.042613 | 0.0022413 | 0.033096 | 0.005985 | 0.000747 | 0.20321 | -0.050009 | 0.44415 | 0.16131 | 0.042256 | 0.009516 | -0.019721 | 0.15776 | 0.30674 | -0.17539 | -0.29693 | 122.668 | -0.025668 | 122.5398 | 122.5075 | -0.16056 | -0.27889 | 0.21527 | 122.2098 | -0.071118 | 122.549 | 122.487 | 0.27721 | 0.077855 | -0.40427 | 122.7099 | 122.4567 | 122.9509 | 122.5127 | -0.067572 | 122.6645 | 122.8135 | 122.3313 | 122.5162 | -0.52582
2238.9531 | 122.7676 | -122.4976 | 0.2243 | 1.4211e-13 | -0.010859 | -0.0028483 | 0.029578 | -0.014764 | 0.0098841 | -0.024875 | 0.0072744 | 0.0070721 | -0.0075247 | 0.042827 | 0.0022413 | 0.033096 | 0.001407 | -0.012988 | 0.19406 | -0.063746 | 0.43957 | 0.15673 | 0.046835 | 0.000359 | -0.0243 | 0.16692 | 0.30216 | -0.16624 | -0.29236 | 122.6543 | -0.030246 | 122.5307 | 122.4846 | -0.16972 | -0.28805 | 0.21527 | 122.2052 | -0.057383 | 122.5444 | 122.4733 | 0.26806 | 0.077854 | -0.39054 | 122.6916 | 122.4338 | 122.9371 | 122.499 | -0.067573 | 122.6645 | 122.7997 | 122.3313 | 122.4979 | -0.51666
2240.6406 | 122.8088 | -122.493 | 0.21515 | 1.4211e-13 | -0.010859 | -0.0028483 | 0.029578 | -0.014764 | 0.0098841 | 0.0056466 | 0.0072744 | 0.0070721 | -0.0081657 | 0.042613 | 0.0024549 | 0.033096 | 0.001407 | -0.003831 | 0.18948 | -0.063746 | 0.43957 | 0.15215 | 0.046835 | 0.014095 | -0.019721 | 0.16234 | 0.29758 | -0.17081 | -0.29236 | 122.6451 | -0.02567 | 122.5261 | 122.4891 | -0.15598 | -0.2789 | 0.22443 | 122.2006 | -0.052807 | 122.5398 | 122.4733 | 0.27264 | 0.082431 | -0.38596 | 122.6825 | 122.4292 | 122.9326 | 122.4944 | -0.062997 | 122.6553 | 122.7906 | 122.3222 | 122.5071 | -0.5075
2242.3906 | 122.7539 | -122.5388 | 0.21057 | 1.4211e-13 | -0.011073 | -0.0030619 | 0.030005 | -0.01455 | 0.010098 | -0.0019839 | 0.0070608 | 0.0074993 | -0.0083793 | 0.042399 | 0.0024549 | 0.046831 | 0.001407 | -0.003831 | 0.19864 | -0.040851 | 0.44873 | 0.14757 | 0.046835 | 0.009516 | -0.0243 | 0.16234 | 0.30674 | -0.17081 | -0.30151 | 122.6863 | -0.011935 | 122.5856 | 122.5349 | -0.1514 | -0.25142 | 0.23816 | 122.2372 | -0.048229 | 122.5856 | 122.5145 | 0.27721 | 0.096166 | -0.38139 | 122.7374 | 122.4979 | 122.9875 | 122.5402 | -0.062998 | 122.7011 | 122.8455 | 122.3679 | 122.5483 | -0.51208
2244.1406 | 122.699 | -122.5433 | 0.24719 | 1.4211e-13 | -0.010859 | -0.0028483 | 0.029364 | -0.014337 | 0.010098 | -0.0019839 | 0.0070608 | 0.0077131 | -0.0081657 | 0.042399 | 0.0020275 | 0.033096 | 0.005985 | -0.012988 | 0.19406 | -0.059167 | 0.44415 | 0.15673 | 0.046835 | 0.014095 | -0.015143 | 0.15318 | 0.30216 | -0.17539 | -0.29236 | 122.7001 | -0.053134 | 122.5764 | 122.5303 | -0.16972 | -0.30636 | 0.19696 | 122.251 | -0.094007 | 122.5902 | 122.5282 | 0.27721 | 0.054966 | -0.42258 | 122.7374 | 122.4842 | 122.9875 | 122.5493 | -0.090461 | 122.6965 | 122.8455 | 122.3679 | 122.5574 | -0.53955
2245.8281 | 122.7539 | -122.4976 | 0.23804 | 1.4211e-13 | -0.011073 | -0.0026347 | 0.029578 | -0.014978 | 0.010311 | 0.0056466 | 0.0072744 | 0.0074993 | -0.0079521 | 0.042613 | 0.0024549 | 0.033096 | -0.003172 | -0.017566 | 0.19406 | -0.068325 | 0.44415 | 0.15673 | 0.051413 | 0.009516 | -0.0243 | 0.15776 | 0.30216 | -0.16166 | -0.29236 | 122.6543 | -0.043979 | 122.5307 | 122.48 | -0.1743 | -0.30636 | 0.20612 | 122.2052 | -0.080273 | 122.549 | 122.4733 | 0.26806 | 0.064121 | -0.3997 | 122.6916 | 122.4292 | 122.9417 | 122.4944 | -0.081306 | 122.6553 | 122.7997 | 122.3359 | 122.5071 | -0.53039
2247.5781 | 122.7081 | -122.5433 | 0.2243 | 1.4211e-13 | -0.010859 | -0.0030619 | 0.029578 | -0.014764 | 0.010311 | 0.0056466 | 0.0070608 | 0.0074993 | -0.0079521 | 0.042399 | 0.0022413 | 0.028518 | 0.005985 | -0.012988 | 0.19406 | -0.063746 | 0.44415 | 0.15673 | 0.037677 | 0.009516 | -0.010564 | 0.16234 | 0.29758 | -0.17081 | -0.30609 | 122.7001 | -0.030246 | 122.5719 | 122.5303 | -0.16972 | -0.28805 | 0.21985 | 122.2372 | -0.061962 | 122.581 | 122.5328 | 0.29553 | 0.073276 | -0.39512 | 122.7374 | 122.4796 | 122.9875 | 122.5493 | -0.067573 | 122.7057 | 122.8409 | 122.3725 | 122.5529 | -0.5304
2249.3281 | 122.7905 | -122.525 | 0.21973 | 1.4211e-13 | -0.011073 | -0.0028483 | 0.029792 | -0.014764 | 0.0098841 | 0.013277 | 0.007488 | 0.0077131 | -0.0079521 | 0.042613 | 0.0024549 | 0.028518 | 0.005985 | -0.017566 | 0.19406 | -0.068325 | 0.435 | 0.15215 | 0.042256 | 0.009516 | -0.019721 | 0.16234 | 0.30674 | -0.17081 | -0.29693 | 122.6772 | -0.025669 | 122.5535 | 122.5075 | -0.16972 | -0.28805 | 0.21527 | 122.2281 | -0.057385 | 122.5673 | 122.5053 | 0.27721 | 0.08701 | -0.39054 | 122.7191 | 122.4567 | 122.96 | 122.531 | -0.067575 | 122.6874 | 122.8318 | 122.3542 | 122.5345 | -0.51666
2251.0781 | 122.7585 | -122.5525 | 0.24261 | 1.4211e-13 | -0.010645 | -0.0026347 | 0.029364 | -0.01455 | 0.010098 | 0.013277 | 0.0072744 | 0.0072857 | -0.0083793 | 0.042185 | 0.0022413 | 0.023939 | -0.003172 | -0.017566 | 0.19406 | -0.063746 | 0.43042 | 0.15215 | 0.042256 | 0.004938 | -0.015143 | 0.15318 | 0.29758 | -0.16624 | -0.29236 | 122.7046 | -0.048557 | 122.5764 | 122.5349 | -0.16972 | -0.30636 | 0.1878 | 122.2601 | -0.08943 | 122.5947 | 122.5373 | 0.27721 | 0.054965 | -0.40885 | 122.7465 | 122.4887 | 122.9829 | 122.5493 | -0.090463 | 122.7057 | 122.8501 | 122.3863 | 122.5574 | -0.53497
2252.75 | 122.7814 | -122.5296 | 0.20142 | 1.4211e-13 | -0.010859 | -0.0028483 | 0.029151 | -0.015191 | 0.0098841 | -0.0019839 | 0.0072744 | 0.0077131 | -0.0081657 | 0.042399 | 0.0020275 | 0.028518 | -0.007751 | -0.022144 | 0.19406 | -0.027115 | 0.44415 | 0.15673 | 0.042256 | 0.009516 | -0.019721 | 0.16692 | 0.30674 | -0.17539 | -0.29693 | 122.6863 | -0.007358 | 122.5581 | 122.5075 | -0.17888 | -0.22853 | 0.24274 | 122.2327 | -0.034495 | 122.5719 | 122.5099 | 0.27721 | 0.10532 | -0.37681 | 122.7237 | 122.5025 | 122.9738 | 122.5219 | -0.044685 | 122.6965 | 122.8363 | 122.3542 | 122.5391 | -0.49835
2254.5 | 122.8638 | -122.4976 | 0.19226 | 1.4211e-13 | -0.010859 | -0.0028483 | 0.029364 | -0.01455 | 0.010098 | -0.0096144 | 0.0070608 | 0.0074993 | -0.0081657 | 0.042399 | 0.0022413 | 0.037675 | -0.003172 | -0.008409 | 0.19864 | -0.040851 | 0.44415 | 0.15673 | 0.037677 | 0.000359 | -0.0243 | 0.16234 | 0.30674 | -0.17539 | -0.29236 | 122.6543 | 0.006375 | 122.5352 | 122.4891 | -0.16514 | -0.23311 | 0.25189 | 122.2052 | -0.029919 | 122.5352 | 122.4733 | 0.26806 | 0.11448 | -0.36765 | 122.6962 | 122.4567 | 122.9417 | 122.4944 | -0.03553 | 122.6599 | 122.8043 | 122.3222 | 122.4979 | -0.48462
2256.25 | 122.7585 | -122.5479 | 0.20599 | 1.4211e-13 | -0.010859 | -0.0032757 | 0.030005 | -0.014978 | 0.010098 | 0.013277 | 0.0072744 | 0.0074993 | -0.0081657 | 0.042613 | 0.0024549 | 0.037675 | 0.001407 | -0.012988 | 0.19864 | -0.063746 | 0.44415 | 0.15673 | 0.037677 | 0.004938 | -0.019721 | 0.15776 | 0.30216 | -0.17081 | -0.30151 | 122.7046 | -0.007358 | 122.5856 | 122.5349 | -0.16972 | -0.26974 | 0.23816 | 122.2464 | -0.04823 | 122.5856 | 122.5282 | 0.28179 | 0.096164 | -0.37681 | 122.7465 | 122.4842 | 122.9921 | 122.5493 | -0.049263 | 122.7057 | 122.8501 | 122.3771 | 122.5529 | -0.50751
2258 | 122.7768 | -122.5433 | 0.24261 | 1.4211e-13 | -0.010859 | -0.0026347 | 0.029364 | -0.015191 | 0.010098 | 0.0056466 | 0.007488 | 0.0074993 | -0.0081657 | 0.042399 | 0.0024549 | 0.046831 | 0.005985 | -0.008409 | 0.20321 | -0.050009 | 0.44415 | 0.15673 | 0.042256 | 0.014095 | -0.015143 | 0.16234 | 0.30216 | -0.17539 | -0.29693 | 122.7001 | -0.039401 | 122.5902 | 122.5349 | -0.16514 | -0.29262 | 0.20154 | 122.2464 | -0.080273 | 122.5856 | 122.5282 | 0.28179 | 0.059543 | -0.41801 | 122.7465 | 122.4933 | 122.9875 | 122.5493 | -0.085884 | 122.7057 | 122.8455 | 122.3679 | 122.5574 | -0.53955
2259.7031 | 122.8134 | -122.5159 | 0.23346 | 1.4211e-13 | -0.011286 | -0.0028483 | 0.029364 | -0.014978 | 0.010311 | 0.013277 | 0.0070608 | 0.0074993 | -0.0083793 | 0.042399 | 0.0022413 | 0.028518 | 0.005985 | -0.003831 | 0.19406 | -0.068325 | 0.44873 | 0.15673 | 0.046835 | 0.018674 | -0.0243 | 0.16234 | 0.30216 | -0.17081 | -0.29693 | 122.6726 | -0.039401 | 122.5444 | 122.512 | -0.16056 | -0.30178 | 0.21527 | 122.2189 | -0.071117 | 122.5627 | 122.4916 | 0.27263 | 0.068699 | -0.40427 | 122.7099 | 122.4475 | 122.9646 | 122.5219 | -0.076728 | 122.6782 | 122.818 | 122.3451 | 122.5345 | -0.53039
2261.4688 | 122.8592 | -122.5021 | 0.19226 | 1.4211e-13 | -0.010431 | -0.0026347 | 0.029578 | -0.014764 | 0.0098841 | 0.0056466 | 0.007488 | 0.0077131 | -0.0081657 | 0.042399 | 0.0020275 | 0.028518 | 0.010564 | -0.012988 | 0.19864 | -0.059167 | 0.44873 | 0.16131 | 0.037677 | 0.009516 | -0.015143 | 0.16234 | 0.30216 | -0.17081 | -0.29693 | 122.6634 | 0.006375 | 122.5307 | 122.4891 | -0.1743 | -0.25143 | 0.25647 | 122.2052 | -0.029919 | 122.5398 | 122.487 | 0.28179 | 0.1099 | -0.36308 | 122.7008 | 122.443 | 122.9509 | 122.5127 | -0.030951 | 122.6645 | 122.8043 | 122.3313 | 122.5117 | -0.48919
2263.2031 | 122.8867 | -122.5113 | 0.19684 | 1.4211e-13 | -0.010431 | -0.0028483 | 0.029151 | -0.01455 | 0.010098 | 0.013277 | 0.0070608 | 0.0074993 | -0.0081657 | 0.042613 | 0.0022413 | 0.033096 | 0.001407 | -0.003831 | 0.19864 | -0.054588 | 0.44873 | 0.15215 | 0.042256 | 0.000359 | -0.015143 | 0.15776 | 0.30216 | -0.17539 | -0.29693 | 122.6634 | 0.001798 | 122.5444 | 122.5075 | -0.15598 | -0.25143 | 0.25189 | 122.2144 | -0.039074 | 122.5535 | 122.4961 | 0.28179 | 0.10532 | -0.37223 | 122.7099 | 122.4567 | 122.96 | 122.5127 | -0.044686 | 122.6691 | 122.8135 | 122.3359 | 122.5117 | -0.49377
2264.9688 | 122.8821 | -122.5296 | 0.20142 | 1.4211e-13 | -0.011286 | -0.0030619 | 0.029792 | -0.014978 | 0.010098 | 0.0056466 | 0.006847 | 0.0077131 | -0.0077383 | 0.042399 | 0.0022413 | 0.037675 | 0.005985 | -0.012988 | 0.18948 | -0.059167 | 0.44873 | 0.14299 | 0.037677 | 0.009516 | -0.015143 | 0.16234 | 0.29758 | -0.17081 | -0.28778 | 122.6726 | -0.011937 | 122.5673 | 122.5166 | -0.15598 | -0.26058 | 0.24732 | 122.2418 | -0.039074 | 122.5673 | 122.5145 | 0.27263 | 0.096164 | -0.37223 | 122.7191 | 122.4704 | 122.9783 | 122.5356 | -0.058422 | 122.6919 | 122.8272 | 122.3588 | 122.5391 | -0.48919
2266.6562 | 122.8592 | -122.5388 | 0.21515 | 1.4211e-13 | -0.010859 | -0.0028483 | 0.029792 | -0.014764 | 0.0098841 | -0.0019839 | 0.0070608 | 0.0074993 | -0.0081657 | 0.042399 | 0.0024549 | 0.033096 | 0.005985 | -0.012988 | 0.18948 | -0.063746 | 0.44415 | 0.15673 | 0.037677 | 0.009516 | -0.015143 | 0.16692 | 0.30674 | -0.17081 | -0.29693 | 122.6955 | -0.02567 | 122.5719 | 122.5258 | -0.16972 | -0.2789 | 0.229 | 122.2418 | -0.048228 | 122.5764 | 122.5236 | 0.28179 | 0.091588 | -0.38596 | 122.7282 | 122.475 | 122.9829 | 122.5447 | -0.058418 | 122.7057 | 122.8455 | 122.3679 | 122.5483 | -0.51208
2268.4062 | 122.7905 | -122.58 | 0.2243 | 1.4211e-13 | -0.010645 | -0.0030619 | 0.029792 | -0.014978 | 0.010098 | -0.0019839 | 0.0070608 | 0.0077131 | -0.0083793 | 0.042399 | 0.0026685 | 0.037675 | 0.001407 | -0.003831 | 0.20321 | -0.063746 | 0.42584 | 0.14757 | 0.051413 | 0.014095 | -0.0243 | 0.16234 | 0.30674 | -0.17081 | -0.29693 | 122.7275 | -0.02109 | 122.6176 | 122.5761 | -0.1514 | -0.28805 | 0.20154 | 122.283 | -0.061962 | 122.6314 | 122.5557 | 0.27263 | 0.082433 | -0.39512 | 122.7832 | 122.5162 | 123.0058 | 122.5814 | -0.076731 | 122.7423 | 122.8867 | 122.4091 | 122.5941 | -0.52124
2270.1562 | 122.8317 | -122.5479 | 0.19226 | 1.4211e-13 | -0.010859 | -0.0032757 | 0.029364 | -0.014337 | 0.010311 | 0.0056466 | 0.0070608 | 0.0079267 | -0.0077383 | 0.042613 | 0.0022413 | 0.037675 | 0.010564 | -0.008409 | 0.19864 | -0.059167 | 0.435 | 0.15215 | 0.046835 | 0.009516 | -0.019721 | 0.16234 | 0.31132 | -0.17539 | -0.29693 | 122.7001 | 0.006375 | 122.5856 | 122.5395 | -0.16056 | -0.25143 | 0.24274 | 122.251 | -0.029919 | 122.5947 | 122.5282 | 0.27721 | 0.11905 | -0.36765 | 122.7465 | 122.4887 | 122.9829 | 122.5585 | -0.040109 | 122.7103 | 122.8592 | 122.3725 | 122.5574 | -0.48919
2271.8438 | 122.905 | -122.5342 | 0.18768 | 1.4211e-13 | -0.010859 | -0.0028483 | 0.029792 | -0.014978 | 0.010311 | -0.0019839 | 0.007488 | 0.0074993 | -0.0077383 | 0.042399 | 0.0020275 | 0.037675 | 0.005985 | -0.012988 | 0.19406 | -0.068325 | 0.435 | 0.15215 | 0.046835 | 0.014095 | -0.0243 | 0.15776 | 0.30216 | -0.17081 | -0.30151 | 122.6863 | 0.006375 | 122.5719 | 122.5212 | -0.16514 | -0.25601 | 0.24731 | 122.2327 | -0.029919 | 122.581 | 122.5099 | 0.27721 | 0.11447 | -0.3585 | 122.7282 | 122.4659 | 122.9692 | 122.5402 | -0.035531 | 122.6919 | 122.8363 | 122.3634 | 122.5483 | -0.4892
2273.5781 | 122.731 | -122.5616 | 0.24261 | 1.4211e-13 | -0.010645 | -0.0032757 | 0.029578 | -0.014978 | 0.010311 | 0.013277 | 0.0072744 | 0.0074993 | -0.0079521 | 0.042185 | 0.0022413 | 0.037675 | 0.010564 | -0.008409 | 0.19864 | -0.059167 | 0.435 | 0.15673 | 0.051413 | 0.004938 | -0.019721 | 0.16692 | 0.30674 | -0.17081 | -0.29693 | 122.7184 | -0.043979 | 122.5993 | 122.5532 | -0.16514 | -0.30178 | 0.19238 | 122.2647 | -0.075694 | 122.6131 | 122.5419 | 0.27721 | 0.064122 | -0.41343 | 122.7603 | 122.5025 | 122.9966 | 122.5722 | -0.085884 | 122.7286 | 122.8684 | 122.3908 | 122.5666 | -0.53955
2275.3281 | 122.8409 | -122.5571 | 0.21057 | 1.4211e-13 | -0.010859 | -0.0030619 | 0.029578 | -0.014764 | 0.010098 | -0.0019839 | 0.0070608 | 0.0077131 | -0.0081657 | 0.042613 | 0.0022413 | 0.037675 | 0.001407 | -0.012988 | 0.18948 | -0.059167 | 0.44415 | 0.15215 | 0.037677 | 0.000359 | -0.015143 | 0.16234 | 0.30674 | -0.16624 | -0.29693 | 122.7092 | -0.021092 | 122.5947 | 122.5441 | -0.16514 | -0.26974 | 0.23358 | 122.2601 | -0.048229 | 122.5947 | 122.5419 | 0.28179 | 0.096166 | -0.37681 | 122.7465 | 122.4979 | 123.0012 | 122.5585 | -0.058419 | 122.7194 | 122.8638 | 122.3908 | 122.5574 | -0.5075
2277.0938 | 122.905 | -122.525 | 0.20599 | 1.4211e-13 | -0.011286 | -0.0026347 | 0.030005 | -0.014764 | 0.010311 | 0.0056466 | 0.0070608 | 0.0077131 | -0.0079521 | 0.042185 | 0.0018139 | 0.042253 | 0.001407 | -0.008409 | 0.19406 | -0.059167 | 0.43957 | 0.15673 | 0.046835 | 0.009516 | -0.0243 | 0.16234 | 0.31132 | -0.17539 | -0.29236 | 122.6818 | -0.011936 | 122.5673 | 122.5166 | -0.16514 | -0.26516 | 0.23358 | 122.2327 | -0.043652 | 122.5719 | 122.5007 | 0.26806 | 0.10532 | -0.38139 | 122.7191 | 122.4659 | 122.9646 | 122.5264 | -0.049263 | 122.6874 | 122.8363 | 122.3496 | 122.5345 | -0.49835
2278.8438 | 122.8683 | -122.5296 | 0.1831 | 1.4211e-13 | -0.010859 | -0.0026347 | 0.029578 | -0.014764 | 0.010098 | -0.0019839 | 0.0070608 | 0.0072857 | -0.0077383 | 0.042399 | 0.0022413 | 0.037675 | 0.005985 | -0.012988 | 0.19864 | -0.068325 | 0.44415 | 0.15673 | 0.042256 | 0.009516 | -0.015143 | 0.16234 | 0.30216 | -0.17081 | -0.29236 | 122.6863 | 0.015531 | 122.5673 | 122.5166 | -0.16972 | -0.25143 | 0.26105 | 122.2372 | -0.020763 | 122.5719 | 122.5145 | 0.27721 | 0.11905 | -0.35392 | 122.7282 | 122.4613 | 122.9738 | 122.5356 | -0.026374 | 122.6919 | 122.8318 | 122.3588 | 122.5391 | -0.47546
2280.5312 | 122.8134 | -122.5616 | 0.21515 | 1.4211e-13 | -0.010859 | -0.0028483 | 0.029578 | -0.014978 | 0.010098 | 0.0056466 | 0.0072744 | 0.0072857 | -0.0081657 | 0.042399 | 0.0018139 | 0.037675 | 0.001407 | -0.012988 | 0.19864 | -0.059167 | 0.44415 | 0.15673 | 0.042256 | 0.000359 | -0.019721 | 0.1715 | 0.30216 | -0.16624 | -0.30151 | 122.7184 | -0.016513 | 122.5993 | 122.5487 | -0.16972 | -0.27432 | 0.229 | 122.2601 | -0.04365 | 122.6039 | 122.5419 | 0.28179 | 0.087009 | -0.38138 | 122.7603 | 122.5025 | 123.0058 | 122.5631 | -0.058418 | 122.7331 | 122.8638 | 122.3954 | 122.562 | -0.51666
2282.2812 | 122.8958 | -122.5616 | 0.23346 | 1.4211e-13 | -0.010645 | -0.0028483 | 0.029578 | -0.014764 | 0.010098 | -0.0019839 | 0.0072744 | 0.0072857 | -0.0081657 | 0.042185 | 0.0020275 | 0.042253 | -0.003172 | -0.012988 | 0.19864 | -0.054588 | 0.43957 | 0.14299 | 0.037677 | 0.004938 | -0.019721 | 0.16234 | 0.30216 | -0.17081 | -0.29236 | 122.7046 | -0.034823 | 122.6039 | 122.5487 | -0.15598 | -0.28805 | 0.20612 | 122.2693 | -0.071117 | 122.5993 | 122.5419 | 0.27264 | 0.068699 | -0.40427 | 122.7603 | 122.5071 | 123.0012 | 122.5585 | -0.090465 | 122.724 | 122.8638 | 122.3908 | 122.5666 | -0.52582
2284.0469 | 122.8546 | -122.5525 | 0.20599 | 1.4211e-13 | -0.011286 | -0.0028483 | 0.029578 | -0.014764 | 0.010311 | 0.013277 | 0.0072744 | 0.0077131 | -0.0081657 | 0.042613 | 0.0024549 | 0.033096 | 0.001407 | -0.012988 | 0.19406 | -0.063746 | 0.435 | 0.15673 | 0.037677 | 0.009516 | -0.019721 | 0.16692 | 0.29758 | -0.17081 | -0.29693 | 122.7092 | -0.011936 | 122.5856 | 122.5395 | -0.16972 | -0.26974 | 0.229 | 122.2556 | -0.039073 | 122.5902 | 122.5328 | 0.27721 | 0.091586 | -0.37681 | 122.7465 | 122.4887 | 122.9875 | 122.5539 | -0.049263 | 122.7194 | 122.8501 | 122.3817 | 122.562 | -0.50293
2285.7344 | 122.7814 | -122.5571 | 0.22888 | 1.4211e-13 | -0.010859 | -0.0028483 | 0.029578 | -0.014978 | 0.010098 | 0.0056466 | 0.0072744 | 0.0072857 | -0.0083793 | 0.042399 | 0.0022413 | 0.033096 | 0.005985 | -0.012988 | 0.19864 | -0.068325 | 0.44415 | 0.15215 | 0.046835 | 0.004938 | -0.019721 | 0.16692 | 0.29758 | -0.17539 | -0.29693 | 122.7092 | -0.030246 | 122.5902 | 122.5441 | -0.16514 | -0.29721 | 0.21527 | 122.2601 | -0.061961 | 122.6039 | 122.5373 | 0.27721 | 0.068698 | -0.40427 | 122.7557 | 122.4887 | 123.0012 | 122.5631 | -0.07673 | 122.724 | 122.8546 | 122.3817 | 122.562 | -0.52582
2287.4844 | 122.8912 | -122.5113 | 0.18768 | 1.4211e-13 | -0.011073 | -0.0028483 | 0.029578 | -0.01455 | 0.0098841 | -0.0019839 | 0.007488 | 0.0072857 | -0.0081657 | 0.042185 | 0.0022413 | 0.042253 | 0.010564 | -0.022144 | 0.19864 | -0.050009 | 0.44873 | 0.15673 | 0.042256 | 0.009516 | -0.028879 | 0.16692 | 0.30216 | -0.16624 | -0.29693 | 122.668 | 0.010953 | 122.5535 | 122.4891 | -0.17888 | -0.23769 | 0.26105 | 122.2144 | -0.020762 | 122.5535 | 122.4824 | 0.26805 | 0.11447 | -0.35392 | 122.7099 | 122.4613 | 122.96 | 122.5219 | -0.030952 | 122.6782 | 122.8135 | 122.3451 | 122.5208 | -0.48462
2289.2344 | 122.7722 | -122.5983 | 0.24719 | 1.4211e-13 | -0.011073 | -0.0030619 | 0.029364 | -0.014978 | 0.010311 | 0.013277 | 0.0072744 | 0.0072857 | -0.0081657 | 0.042399 | 0.0022413 | 0.033096 | 0.005985 | -0.012988 | 0.19864 | -0.063746 | 0.44415 | 0.15673 | 0.042256 | 0.009516 | -0.019721 | 0.16234 | 0.30216 | -0.17539 | -0.30151 | 122.755 | -0.048556 | 122.6314 | 122.5853 | -0.16972 | -0.31094 | 0.19696 | 122.2968 | -0.08485 | 122.6405 | 122.5785 | 0.28179 | 0.054966 | -0.42258 | 122.7969 | 122.5345 | 123.0424 | 122.6043 | -0.090461 | 122.7606 | 122.9004 | 122.4229 | 122.6078 | -0.5487
2290.9844 | 122.7722 | -122.5937 | 0.21515 | 1.4211e-13 | -0.011286 | -0.0028483 | 0.029578 | -0.014764 | 0.010098 | 0.013277 | 0.0072744 | 0.0074993 | -0.0081657 | 0.042399 | 0.0020275 | 0.042253 | 0.005985 | -0.012988 | 0.19406 | -0.063746 | 0.43957 | 0.15673 | 0.046835 | 0.004938 | -0.0243 | 0.16692 | 0.30674 | -0.17539 | -0.30151 | 122.7504 | -0.021091 | 122.6359 | 122.5807 | -0.16972 | -0.2789 | 0.22443 | 122.2922 | -0.048228 | 122.6405 | 122.5694 | 0.27721 | 0.091588 | -0.39054 | 122.7877 | 122.5299 | 123.0333 | 122.5997 | -0.058418 | 122.7606 | 122.9004 | 122.4183 | 122.5986 | -0.51666
2292.6719 | 122.8134 | -122.5616 | 0.20599 | 1.4211e-13 | -0.010859 | -0.0026347 | 0.029578 | -0.014978 | 0.010311 | 0.0056466 | 0.0072744 | 0.0072857 | -0.0079521 | 0.042399 | 0.0022413 | 0.037675 | 0.005985 | -0.012988 | 0.19864 | -0.050009 | 0.44415 | 0.15673 | 0.042256 | -0.00422 | -0.019721 | 0.1715 | 0.30674 | -0.16624 | -0.29693 | 122.7184 | -0.007358 | 122.5993 | 122.5487 | -0.16972 | -0.256 | 0.23816 | 122.2647 | -0.034495 | 122.6039 | 122.5419 | 0.27721 | 0.10074 | -0.37223 | 122.7603 | 122.5116 | 123.0058 | 122.5676 | -0.049263 | 122.7331 | 122.8684 | 122.3954 | 122.5574 | -0.50293
2294.4375 | 122.8088 | -122.6212 | 0.24261 | 1.4211e-13 | -0.011073 | -0.0028483 | 0.029578 | -0.014978 | 0.0098841 | -0.0019839 | 0.0070608 | 0.0074993 | -0.0081657 | 0.042613 | 0.0022413 | 0.033096 | 0.005985 | -0.017566 | 0.19406 | -0.059167 | 0.43957 | 0.15673 | 0.051413 | 0.004938 | -0.019721 | 0.16234 | 0.30674 | -0.17539 | -0.29236 | 122.7779 | -0.048557 | 122.6543 | 122.6036 | -0.1743 | -0.30178 | 0.19696 | 122.3288 | -0.080273 | 122.6726 | 122.6014 | 0.27264 | 0.064122 | -0.41801 | 122.8152 | 122.562 | 123.0607 | 122.6271 | -0.085884 | 122.7835 | 122.9279 | 122.4458 | 122.6261 | -0.53497
2296.125 | 122.8043 | -122.6028 | 0.23804 | 1.4211e-13 | -0.011073 | -0.0030619 | 0.029792 | -0.014764 | 0.0098841 | -0.0019839 | 0.0072744 | 0.0070721 | -0.0077383 | 0.042613 | 0.0022413 | 0.033096 | 0.001407 | -0.012988 | 0.18948 | -0.063746 | 0.44873 | 0.15673 | 0.037677 | 0.004938 | -0.019721 | 0.15776 | 0.30674 | -0.17081 | -0.29236 | 122.7596 | -0.048558 | 122.6359 | 122.5899 | -0.16972 | -0.30178 | 0.2107 | 122.3105 | -0.080273 | 122.6405 | 122.5831 | 0.27264 | 0.0687 | -0.40885 | 122.7923 | 122.5391 | 123.0516 | 122.6043 | -0.081306 | 122.7606 | 122.9096 | 122.432 | 122.6078 | -0.53039
2297.875 | 122.8455 | -122.6028 | 0.21515 | 1.4211e-13 | -0.011073 | -0.0030619 | 0.029792 | -0.014764 | 0.0098841 | 0.0056466 | 0.006847 | 0.0074993 | -0.0077383 | 0.042399 | 0.0020275 | 0.028518 | -0.003172 | -0.008409 | 0.19864 | -0.068325 | 0.43957 | 0.15673 | 0.042256 | 0.000359 | -0.015143 | 0.15776 | 0.31132 | -0.16624 | -0.29236 | 122.7596 | -0.016513 | 122.6314 | 122.5944 | -0.16514 | -0.28347 | 0.22443 | 122.3105 | -0.057385 | 122.6451 | 122.5877 | 0.27721 | 0.096167 | -0.38138 | 122.8015 | 122.5345 | 123.0424 | 122.5997 | -0.058418 | 122.7606 | 122.9142 | 122.4366 | 122.6032 | -0.5075
2299.625 | 122.8363 | -122.6028 | 0.2243 | 1.4211e-13 | -0.010859 | -0.0028483 | 0.029364 | -0.014764 | 0.010525 | -0.0019839 | 0.0072744 | 0.0072857 | -0.0077383 | 0.042827 | 0.0018139 | 0.037675 | 0.001407 | -0.008409 | 0.19864 | -0.063746 | 0.44873 | 0.15673 | 0.037677 | 0.000359 | -0.015143 | 0.16234 | 0.31132 | -0.17081 | -0.29693 | 122.7596 | -0.025668 | 122.6405 | 122.5944 | -0.16514 | -0.28805 | 0.22443 | 122.3059 | -0.061962 | 122.6405 | 122.5877 | 0.28179 | 0.087012 | -0.39512 | 122.8015 | 122.5391 | 123.0516 | 122.6043 | -0.067573 | 122.7652 | 122.9142 | 122.432 | 122.6032 | -0.52124
2301.375 | 122.8775 | -122.5479 | 0.19226 | 1.4211e-13 | -0.011073 | -0.0028483 | 0.029578 | -0.01455 | 0.010098 | -0.0019839 | 0.0070608 | 0.0074993 | -0.0083793 | 0.042613 | 0.0016003 | 0.037675 | 0.010564 | -0.012988 | 0.19864 | -0.054588 | 0.44415 | 0.15673 | 0.037677 | 0.000359 | -0.0243 | 0.15776 | 0.31132 | -0.17081 | -0.29693 | 122.7046 | 0.006375 | 122.5856 | 122.5349 | -0.16972 | -0.24685 | 0.25189 | 122.251 | -0.034497 | 122.5856 | 122.5236 | 0.27263 | 0.11905 | -0.36308 | 122.7465 | 122.4933 | 122.9921 | 122.5585 | -0.03553 | 122.7057 | 122.8592 | 122.3771 | 122.5483 | -0.48919
2303.1406 | 122.8775 | -122.5525 | 0.21515 | 1.4211e-13 | -0.011286 | -0.0028483 | 0.029151 | -0.014764 | 0.0098841 | 0.0056466 | 0.0072744 | 0.0072857 | -0.0083793 | 0.042613 | 0.0022413 | 0.037675 | 0.005985 | -0.008409 | 0.20321 | -0.059167 | 0.43957 | 0.15673 | 0.046835 | 0.014095 | -0.019721 | 0.16234 | 0.30674 | -0.17539 | -0.29693 | 122.7092 | -0.011935 | 122.5902 | 122.5441 | -0.16514 | -0.27432 | 0.22443 | 122.2556 | -0.052807 | 122.5993 | 122.5328 | 0.27721 | 0.091588 | -0.39054 | 122.7557 | 122.4933 | 122.9921 | 122.5585 | -0.058418 | 122.7148 | 122.8592 | 122.3771 | 122.5666 | -0.51208
2304.8438 | 122.818 | -122.58 | 0.2243 | 1.4211e-13 | -0.011073 | -0.0032757 | 0.029578 | -0.015191 | 0.010098 | -0.0019839 | 0.0070608 | 0.0074993 | -0.0083793 | 0.042613 | 0.0022413 | 0.046831 | -0.003172 | -0.017566 | 0.19864 | -0.068325 | 0.44415 | 0.15215 | 0.042256 | 0.009516 | -0.019721 | 0.16234 | 0.31132 | -0.17081 | -0.29693 | 122.7321 | -0.025668 | 122.6268 | 122.5624 | -0.16972 | -0.29263 | 0.21985 | 122.283 | -0.061962 | 122.6222 | 122.5602 | 0.27721 | 0.087012 | -0.39512 | 122.7786 | 122.5116 | 123.0241 | 122.5768 | -0.072152 | 122.7423 | 122.8913 | 122.4091 | 122.5895 | -0.52124
2306.5938 | 122.7814 | -122.6074 | 0.23804 | 1.4211e-13 | -0.011286 | -0.0028483 | 0.029578 | -0.014764 | 0.010098 | 0.020908 | 0.0072744 | 0.0074993 | -0.0079521 | 0.042399 | 0.0022413 | 0.033096 | 0.001407 | -0.017566 | 0.19406 | -0.068325 | 0.44415 | 0.16131 | 0.042256 | 0.004938 | -0.015143 | 0.16234 | 0.30216 | -0.17081 | -0.29236 | 122.7687 | -0.043979 | 122.6405 | 122.5899 | -0.17888 | -0.30636 | 0.20612 | 122.3151 | -0.075695 | 122.6497 | 122.5923 | 0.27721 | 0.064121 | -0.40885 | 122.8015 | 122.5391 | 123.0516 | 122.6088 | -0.076727 | 122.7698 | 122.9096 | 122.4366 | 122.6124 | -0.53039
2308.3438 | 122.9462 | -122.5571 | 0.20142 | 1.4211e-13 | -0.011286 | -0.0030619 | 0.029364 | -0.014978 | 0.010311 | 0.013277 | 0.0070608 | 0.0074993 | -0.0085929 | 0.042399 | 0.0022413 | 0.033096 | 0.005985 | -0.008409 | 0.20321 | -0.063746 | 0.44873 | 0.15215 | 0.042256 | 0.004938 | -0.010564 | 0.16692 | 0.31132 | -0.17539 | -0.29693 | 122.7092 | 0.001798 | 122.5902 | 122.5487 | -0.16056 | -0.26516 | 0.24732 | 122.2601 | -0.034495 | 122.5993 | 122.5465 | 0.28637 | 0.1099 | -0.37681 | 122.7603 | 122.4933 | 123.0058 | 122.5631 | -0.049264 | 122.724 | 122.8684 | 122.3817 | 122.562 | -0.49835
2310.0938 | 122.8088 | -122.6212 | 0.23346 | 1.4211e-13 | -0.011073 | -0.0028483 | 0.030005 | -0.014978 | 0.010311 | 0.0056466 | 0.0070608 | 0.0072857 | -0.0079521 | 0.042399 | 0.0022413 | 0.033096 | 0.001407 | -0.012988 | 0.19406 | -0.063746 | 0.42584 | 0.15215 | 0.033099 | 0.004938 | -0.019721 | 0.16234 | 0.30216 | -0.17539 | -0.29236 | 122.7733 | -0.039401 | 122.6543 | 122.6082 | -0.16514 | -0.2972 | 0.19238 | 122.3288 | -0.071117 | 122.6543 | 122.6014 | 0.27264 | 0.068699 | -0.40885 | 122.8152 | 122.5574 | 123.047 | 122.6226 | -0.081307 | 122.7835 | 122.9233 | 122.4458 | 122.6261 | -0.52582
2311.8438 | 122.8546 | -122.5845 | 0.20599 | 1.4211e-13 | -0.011073 | -0.0028483 | 0.029364 | -0.014764 | 0.010311 | 0.0056466 | 0.007488 | 0.0072857 | -0.0083793 | 0.042613 | 0.0020275 | 0.033096 | 0.005985 | -0.008409 | 0.19406 | -0.063746 | 0.42584 | 0.15673 | 0.037677 | 0.004938 | -0.019721 | 0.16234 | 0.30674 | -0.17081 | -0.29693 | 122.7413 | -0.011936 | 122.6176 | 122.5761 | -0.16514 | -0.26974 | 0.21985 | 122.2876 | -0.043652 | 122.6222 | 122.5648 | 0.27721 | 0.10074 | -0.37681 | 122.7786 | 122.5208 | 123.0104 | 122.5905 | -0.049263 | 122.7469 | 122.8913 | 122.4137 | 122.5895 | -0.50293
2313.5312 | 122.9141 | -122.6028 | 0.20599 | 1.4211e-13 | -0.010859 | -0.0030619 | 0.029578 | -0.014764 | 0.010525 | -0.0019839 | 0.0070608 | 0.0072857 | -0.0079521 | 0.042185 | 0.0022413 | 0.023939 | -0.003172 | -0.012988 | 0.19406 | -0.059167 | 0.42584 | 0.15673 | 0.042256 | 0.009516 | -0.019721 | 0.16234 | 0.30674 | -0.16624 | -0.29693 | 122.7596 | -0.011936 | 122.6268 | 122.5899 | -0.16972 | -0.26516 | 0.21985 | 122.3059 | -0.043652 | 122.6451 | 122.5831 | 0.27721 | 0.10074 | -0.37223 | 122.7969 | 122.5437 | 123.0287 | 122.5997 | -0.049263 | 122.7652 | 122.9096 | 122.4366 | 122.6124 | -0.50293
2315.2656 | 122.9279 | -122.5845 | 0.20599 | 1.4211e-13 | -0.0115 | -0.0028483 | 0.029364 | -0.014764 | 0.010311 | -0.0019839 | 0.0072744 | 0.0074993 | -0.0083793 | 0.042399 | 0.0022413 | 0.042253 | 0.001407 | -0.003831 | 0.19864 | -0.063746 | 0.43957 | 0.16131 | 0.042256 | 0.004938 | -0.015143 | 0.15776 | 0.30674 | -0.16624 | -0.29693 | 122.7458 | -0.007358 | 122.6268 | 122.5807 | -0.16514 | -0.26974 | 0.23358 | 122.2876 | -0.04823 | 122.6268 | 122.5694 | 0.28179 | 0.10074 | -0.37223 | 122.7832 | 122.5208 | 123.0241 | 122.5859 | -0.044684 | 122.7423 | 122.8913 | 122.4183 | 122.5895 | -0.50293
2317.0312 | 122.85 | -122.6257 | 0.23804 | 1.4211e-13 | -0.011073 | -0.0028483 | 0.029364 | -0.014978 | 0.0098841 | 0.0056466 | 0.0072744 | 0.0077131 | -0.0083793 | 0.042827 | 0.0022413 | 0.037675 | 0.005985 | -0.008409 | 0.19864 | -0.063746 | 0.44873 | 0.16131 | 0.046835 | 0.009516 | -0.0243 | 0.16234 | 0.30216 | -0.17539 | -0.29693 | 122.787 | -0.039401 | 122.6634 | 122.6173 | -0.16972 | -0.30178 | 0.2107 | 122.3288 | -0.075695 | 122.6726 | 122.6014 | 0.27263 | 0.064121 | -0.41343 | 122.8244 | 122.562 | 123.0745 | 122.6317 | -0.076727 | 122.7881 | 122.9279 | 122.4503 | 122.6352 | -0.53497
2318.7188 | 122.8134 | -122.6349 | 0.22888 | 1.4211e-13 | -0.011286 | -0.0030619 | 0.029364 | -0.014764 | 0.0098841 | -0.0019839 | 0.0072744 | 0.0077131 | -0.0083793 | 0.042613 | 0.0024549 | 0.033096 | 0.005985 | -0.003831 | 0.20321 | -0.059167 | 0.44415 | 0.15215 | 0.042256 | -0.00422 | -0.015143 | 0.15776 | 0.31132 | -0.17997 | -0.29236 | 122.787 | -0.025668 | 122.668 | 122.6311 | -0.15598 | -0.28805 | 0.21527 | 122.3425 | -0.071118 | 122.6771 | 122.6197 | 0.27721 | 0.082434 | -0.40885 | 122.8381 | 122.5757 | 123.079 | 122.6409 | -0.07673 | 122.7927 | 122.9462 | 122.4549 | 122.6307 | -0.52124
2320.4688 | 122.8363 | -122.6028 | 0.2243 | 1.4211e-13 | -0.011286 | -0.0028483 | 0.029578 | -0.014978 | 0.0098841 | -0.0019839 | 0.0070608 | 0.0074993 | -0.0081657 | 0.042399 | 0.0022413 | 0.037675 | 0.005985 | -0.008409 | 0.19406 | -0.068325 | 0.44415 | 0.14757 | 0.042256 | 0.004938 | -0.010564 | 0.16692 | 0.30674 | -0.17539 | -0.30151 | 122.7504 | -0.030246 | 122.6405 | 122.5944 | -0.15598 | -0.29263 | 0.21985 | 122.3013 | -0.057383 | 122.6451 | 122.5923 | 0.29095 | 0.082433 | -0.3997 | 122.7969 | 122.5345 | 123.047 | 122.6088 | -0.076731 | 122.7698 | 122.9096 | 122.4275 | 122.6078 | -0.52582
2322.2344 | 122.9462 | -122.5845 | 0.18768 | 1.4211e-13 | -0.011286 | -0.0028483 | 0.029792 | -0.014978 | 0.010311 | 0.0056466 | 0.0072744 | 0.0077131 | -0.0083793 | 0.042399 | 0.0022413 | 0.037675 | -0.003172 | -0.012988 | 0.19864 | -0.059167 | 0.44415 | 0.14757 | 0.042256 | 0.004938 | -0.0243 | 0.16234 | 0.30216 | -0.17081 | -0.30151 | 122.7321 | 0.010953 | 122.6222 | 122.5715 | -0.16056 | -0.24685 | 0.25647 | 122.283 | -0.025341 | 122.6268 | 122.5602 | 0.27721 | 0.11447 | -0.3585 | 122.7832 | 122.5254 | 123.0287 | 122.5814 | -0.04011 | 122.7469 | 122.8867 | 122.4137 | 122.5895 | -0.4892
2323.9219 | 122.9599 | -122.6074 | 0.18768 | 1.4211e-13 | -0.011286 | -0.0028483 | 0.029578 | -0.014978 | 0.0098841 | 0.013277 | 0.006847 | 0.0074993 | -0.0083793 | 0.042613 | 0.0018139 | 0.037675 | -0.003172 | -0.012988 | 0.19406 | -0.068325 | 0.44415 | 0.14757 | 0.042256 | 0.000359 | -0.015143 | 0.16234 | 0.31589 | -0.17539 | -0.30151 | 122.755 | 0.006375 | 122.6451 | 122.5944 | -0.16056 | -0.25601 | 0.25647 | 122.3059 | -0.025341 | 122.6497 | 122.5923 | 0.28637 | 0.12821 | -0.36308 | 122.8015 | 122.5391 | 123.0516 | 122.6042 | -0.04011 | 122.7698 | 122.9233 | 122.432 | 122.6078 | -0.4892
2325.6719 | 122.8775 | -122.6074 | 0.19684 | 1.4211e-13 | -0.011714 | -0.0028483 | 0.029578 | -0.014978 | 0.010311 | -0.0019839 | 0.0072744 | 0.0074993 | -0.0083793 | 0.042185 | 0.0024549 | 0.033096 | 0.001407 | -0.008409 | 0.20321 | -0.068325 | 0.435 | 0.15673 | 0.037677 | 0.004938 | -0.015143 | 0.16234 | 0.30674 | -0.17081 | -0.30151 | 122.7642 | 0.006376 | 122.6405 | 122.599 | -0.16514 | -0.26516 | 0.23816 | 122.3059 | -0.034496 | 122.6451 | 122.5923 | 0.28637 | 0.1099 | -0.36765 | 122.8106 | 122.5391 | 123.0424 | 122.6088 | -0.040107 | 122.7698 | 122.9142 | 122.4366 | 122.6124 | -0.49835
2327.4219 | 122.8088 | -122.6486 | 0.22888 | 1.4211e-13 | -0.011073 | -0.0030619 | 0.029792 | -0.014764 | 0.010098 | -0.0096144 | 0.0070608 | 0.0072857 | -0.0081657 | 0.042399 | 0.0020275 | 0.033096 | 0.001407 | -0.012988 | 0.20321 | -0.063746 | 0.44415 | 0.16131 | 0.051413 | 0.004938 | -0.0243 | 0.16234 | 0.30674 | -0.17081 | -0.28778 | 122.8099 | -0.025668 | 122.6817 | 122.6356 | -0.1743 | -0.29263 | 0.21527 | 122.3608 | -0.06654 | 122.7 | 122.6243 | 0.26348 | 0.077855 | -0.3997 | 122.8518 | 122.5849 | 123.0928 | 122.65 | -0.067572 | 122.811 | 122.9554 | 122.4778 | 122.6536 | -0.51666
2329.125 | 122.85 | -122.6257 | 0.20599 | 1.4211e-13 | -0.011286 | -0.0028483 | 0.029792 | -0.014764 | 0.010098 | 0.013277 | 0.0070608 | 0.0074993 | -0.0083793 | 0.042185 | 0.0018139 | 0.037675 | 0.001407 | -0.008409 | 0.18948 | -0.059167 | 0.44415 | 0.15673 | 0.046835 | 0.000359 | -0.0243 | 0.16234 | 0.30216 | -0.17539 | -0.29693 | 122.7825 | -0.016515 | 122.6634 | 122.6173 | -0.16514 | -0.26516 | 0.23816 | 122.3288 | -0.043652 | 122.6726 | 122.6014 | 0.27263 | 0.096164 | -0.38139 | 122.8152 | 122.5666 | 123.0699 | 122.6271 | -0.049263 | 122.7881 | 122.9279 | 122.4503 | 122.6261 | -0.50293
2330.875 | 122.905 | -122.612 | 0.17853 | 1.4211e-13 | -0.0115 | -0.0030619 | 0.029364 | -0.014978 | 0.010311 | -0.0019839 | 0.0070608 | 0.0072857 | -0.0083793 | 0.042185 | 0.0020275 | 0.033096 | 0.005985 | -0.008409 | 0.19864 | -0.059167 | 0.43957 | 0.14299 | 0.037677 | 0.004938 | -0.010564 | 0.16234 | 0.30674 | -0.17081 | -0.29693 | 122.755 | 0.020108 | 122.6451 | 122.6036 | -0.1514 | -0.23769 | 0.26105 | 122.3151 | -0.016186 | 122.6497 | 122.6014 | 0.28637 | 0.12821 | -0.34934 | 122.8106 | 122.5528 | 123.0516 | 122.618 | -0.035534 | 122.7743 | 122.9187 | 122.4412 | 122.6169 | -0.47546
2332.625 | 122.8592 | -122.6257 | 0.22888 | 1.4211e-13 | -0.011073 | -0.0028483 | 0.029364 | -0.014978 | 0.010098 | 0.0056466 | 0.0072744 | 0.0074993 | -0.0079521 | 0.042399 | 0.0020275 | 0.037675 | 0.001407 | -0.012988 | 0.19406 | -0.059167 | 0.44873 | 0.14757 | 0.046835 | 0.000359 | -0.0243 | 0.15776 | 0.30216 | -0.16624 | -0.28778 | 122.7733 | -0.034824 | 122.6634 | 122.6127 | -0.16056 | -0.28805 | 0.21985 | 122.338 | -0.071118 | 122.6726 | 122.6014 | 0.26348 | 0.073276 | -0.39512 | 122.8198 | 122.5666 | 123.0745 | 122.6271 | -0.081309 | 122.7835 | 122.9279 | 122.4595 | 122.6261 | -0.51666
2334.375 | 122.9691 | -122.6074 | 0.1831 | 1.4211e-13 | -0.011286 | -0.0030619 | 0.029364 | -0.01455 | 0.010098 | -0.0096144 | 0.0072744 | 0.0074993 | -0.0081657 | 0.042185 | 0.0018139 | 0.037675 | 0.010564 | -0.017566 | 0.19864 | -0.068325 | 0.44415 | 0.16131 | 0.042256 | 0.004938 | -0.015143 | 0.16234 | 0.30216 | -0.17081 | -0.29236 | 122.7687 | 0.015531 | 122.6451 | 122.5899 | -0.17888 | -0.25143 | 0.26105 | 122.3151 | -0.020763 | 122.6497 | 122.5923 | 0.27721 | 0.11905 | -0.35392 | 122.8061 | 122.5391 | 123.0516 | 122.618 | -0.021795 | 122.7698 | 122.9096 | 122.4366 | 122.6124 | -0.47546
2336.125 | 122.818 | -122.6532 | 0.2243 | 1.4211e-13 | -0.011286 | -0.0026347 | 0.029578 | -0.01455 | 0.0098841 | 0.013277 | 0.0070608 | 0.0074993 | -0.0079521 | 0.042185 | 0.0018139 | 0.042253 | 0.005985 | -0.012988 | 0.19406 | -0.072904 | 0.44415 | 0.15673 | 0.037677 | 0.009516 | -0.019721 | 0.16234 | 0.30216 | -0.17539 | -0.29236 | 122.8099 | -0.030246 | 122.6955 | 122.6402 | -0.16972 | -0.29721 | 0.21985 | 122.3608 | -0.061962 | 122.6909 | 122.6335 | 0.27264 | 0.077854 | -0.3997 | 122.8473 | 122.5803 | 123.0974 | 122.6592 | -0.067573 | 122.8155 | 122.9554 | 122.4778 | 122.6627 | -0.51666
2337.8281 | 122.8271 | -122.6395 | 0.2243 | 1.4211e-13 | -0.0115 | -0.0032757 | 0.029578 | -0.014978 | 0.0098841 | -0.0019839 | 0.0070608 | 0.0074993 | -0.0085929 | 0.042399 | 0.0022413 | 0.037675 | 0.001407 | -0.017566 | 0.19406 | -0.072904 | 0.45789 | 0.15673 | 0.042256 | 0.009516 | -0.015143 | 0.16234 | 0.30674 | -0.17081 | -0.29693 | 122.7962 | -0.030246 | 122.6771 | 122.6219 | -0.1743 | -0.29721 | 0.23359 | 122.3425 | -0.061962 | 122.6817 | 122.6243 | 0.28179 | 0.082433 | -0.39512 | 122.8335 | 122.5666 | 123.0974 | 122.6409 | -0.067573 | 122.8018 | 122.9462 | 122.4686 | 122.649 | -0.52124
2339.5625 | 122.9416 | -122.6074 | 0.20142 | 1.4211e-13 | -0.011073 | -0.0028483 | 0.029364 | -0.014764 | 0.010098 | 0.0056466 | 0.0070608 | 0.0077131 | -0.0083793 | 0.042399 | 0.0024549 | 0.037675 | 0.001407 | -0.012988 | 0.20321 | -0.059167 | 0.44415 | 0.15673 | 0.051413 | 0.009516 | -0.015143 | 0.16692 | 0.30216 | -0.17081 | -0.29236 | 122.7642 | 0.001798 | 122.6451 | 122.5944 | -0.16972 | -0.26058 | 0.24274 | 122.3151 | -0.034495 | 122.6588 | 122.5923 | 0.27721 | 0.10074 | -0.37223 | 122.8106 | 122.5483 | 123.0516 | 122.6088 | -0.044685 | 122.7743 | 122.9096 | 122.4366 | 122.6169 | -0.49377
2341.25 | 122.8867 | -122.644 | 0.20142 | 1.4211e-13 | -0.010859 | -0.0030619 | 0.029792 | -0.014764 | 0.010098 | -0.0019839 | 0.0072744 | 0.0074993 | -0.0081657 | 0.042399 | 0.0018139 | 0.033096 | 0.005985 | -0.012988 | 0.18948 | -0.054588 | 0.44415 | 0.15215 | 0.037677 | 0.004938 | -0.019721 | 0.15776 | 0.30674 | -0.18455 | -0.29236 | 122.7962 | -0.011937 | 122.6771 | 122.6311 | -0.16514 | -0.256 | 0.24274 | 122.3517 | -0.043652 | 122.6817 | 122.6243 | 0.27264 | 0.10532 | -0.38597 | 122.8335 | 122.5895 | 123.0882 | 122.65 | -0.049264 | 122.8018 | 122.9508 | 122.4595 | 122.649 | -0.49377
2343.0156 | 122.9507 | -122.6303 | 0.19226 | 1.4211e-13 | -0.011286 | -0.0030619 | 0.029578 | -0.014978 | 0.010311 | 0.0056466 | 0.0072744 | 0.0070721 | -0.0083793 | 0.042613 | 0.0020275 | 0.037675 | 0.005985 | -0.012988 | 0.19864 | -0.063746 | 0.44415 | 0.15215 | 0.037677 | 0.004938 | -0.015143 | 0.16234 | 0.30216 | -0.17081 | -0.29693 | 122.7825 | 0.006375 | 122.668 | 122.6173 | -0.16514 | -0.25601 | 0.25189 | 122.3334 | -0.029919 | 122.668 | 122.6152 | 0.28179 | 0.1099 | -0.36308 | 122.8289 | 122.5666 | 123.0745 | 122.6363 | -0.040109 | 122.7927 | 122.9325 | 122.4595 | 122.6352 | -0.48919
2344.7656 | 122.9736 | -122.6212 | 0.21057 | 1.4211e-13 | -0.011286 | -0.0030619 | 0.029364 | -0.014978 | 0.0096705 | -0.0019839 | 0.0072744 | 0.0074993 | -0.0083793 | 0.042613 | 0.0018139 | 0.037675 | -0.003172 | -0.012988 | 0.19864 | -0.063746 | 0.44415 | 0.15215 | 0.046835 | 0.000359 | -0.019721 | 0.16234 | 0.29758 | -0.17081 | -0.29236 | 122.7733 | -0.011935 | 122.6588 | 122.6082 | -0.16514 | -0.27432 | 0.23358 | 122.3288 | -0.048229 | 122.668 | 122.6014 | 0.27264 | 0.087009 | -0.38139 | 122.8198 | 122.5574 | 123.0653 | 122.618 | -0.058419 | 122.7835 | 122.9187 | 122.4503 | 122.6215 | -0.50293
2346.5312 | 122.9462 | -122.644 | 0.19226 | 1.4211e-13 | -0.011073 | -0.0030619 | 0.029578 | -0.014764 | 0.010098 | -0.0019839 | 0.0070608 | 0.0074993 | -0.0081657 | 0.042399 | 0.0018139 | 0.037675 | 0.010564 | -0.012988 | 0.19406 | -0.059167 | 0.44415 | 0.16131 | 0.042256 | 0.004938 | -0.015143 | 0.16692 | 0.30216 | -0.17539 | -0.29693 | 122.8054 | 0.001797 | 122.6817 | 122.6311 | -0.1743 | -0.25143 | 0.25189 | 122.3471 | -0.02534 | 122.6863 | 122.6289 | 0.28179 | 0.1099 | -0.36765 | 122.8381 | 122.5849 | 123.0882 | 122.6546 | -0.030951 | 122.811 | 122.9462 | 122.4686 | 122.649 | -0.48919
2348.2344 | 122.8592 | -122.6624 | 0.21973 | 1.4211e-13 | -0.011073 | -0.0028483 | 0.029578 | -0.014978 | 0.010098 | -0.0019839 | 0.0070608 | 0.0077131 | -0.0081657 | 0.042399 | 0.0022413 | 0.033096 | 0.001407 | -0.008409 | 0.19864 | -0.063746 | 0.44415 | 0.15673 | 0.037677 | 0.004938 | -0.015143 | 0.15776 | 0.30674 | -0.17081 | -0.29236 | 122.8191 | -0.021091 | 122.6954 | 122.6539 | -0.16514 | -0.28347 | 0.22443 | 122.37 | -0.061963 | 122.7 | 122.6472 | 0.27721 | 0.08701 | -0.39054 | 122.861 | 122.5986 | 123.1065 | 122.6638 | -0.062996 | 122.8201 | 122.9691 | 122.4915 | 122.6673 | -0.51208
2349.9844 | 122.9279 | -122.6166 | 0.20599 | 1.4211e-13 | -0.0115 | -0.0028483 | 0.029792 | -0.014978 | 0.010525 | -0.0019839 | 0.0072744 | 0.0077131 | -0.0083793 | 0.042399 | 0.0022413 | 0.033096 | 0.005985 | -0.012988 | 0.19406 | -0.063746 | 0.435 | 0.15215 | 0.042256 | 0.000359 | -0.019721 | 0.1715 | 0.30216 | -0.17081 | -0.29236 | 122.7687 | -0.011936 | 122.6497 | 122.6036 | -0.16514 | -0.26974 | 0.229 | 122.3242 | -0.034495 | 122.6588 | 122.5969 | 0.27264 | 0.096164 | -0.37681 | 122.8106 | 122.5528 | 123.0516 | 122.6226 | -0.053842 | 122.7881 | 122.9187 | 122.4458 | 122.6169 | -0.49835
2351.7344 | 122.9095 | -122.6578 | 0.21057 | 1.4211e-13 | -0.011073 | -0.0026347 | 0.029578 | -0.014978 | 0.010311 | 0.0056466 | 0.0070608 | 0.0070721 | -0.0081657 | 0.042613 | 0.0020275 | 0.037675 | 0.001407 | -0.003831 | 0.19864 | -0.059167 | 0.44873 | 0.15673 | 0.037677 | 0.004938 | -0.0243 | 0.1715 | 0.30216 | -0.16624 | -0.30609 | 122.8145 | -0.011935 | 122.6955 | 122.6539 | -0.16056 | -0.26974 | 0.23816 | 122.3517 | -0.039072 | 122.6955 | 122.6335 | 0.28179 | 0.091587 | -0.37681 | 122.8564 | 122.5986 | 123.1065 | 122.6592 | -0.05384 | 122.8293 | 122.9599 | 122.4915 | 122.6627 | -0.51666
2353.4219 | 122.9645 | -122.6349 | 0.18768 | 1.4211e-13 | -0.0115 | -0.0030619 | 0.029578 | -0.014978 | 0.010311 | 0.013277 | 0.0072744 | 0.0070721 | -0.0088065 | 0.042399 | 0.0020275 | 0.033096 | 0.005985 | -0.008409 | 0.18948 | -0.059167 | 0.44415 | 0.15215 | 0.037677 | 0.000359 | -0.019721 | 0.15776 | 0.30216 | -0.17539 | -0.29693 | 122.787 | 0.001796 | 122.668 | 122.6265 | -0.16056 | -0.24685 | 0.25647 | 122.338 | -0.029919 | 122.6726 | 122.6152 | 0.27721 | 0.11447 | -0.36308 | 122.8244 | 122.5757 | 123.079 | 122.6409 | -0.035531 | 122.7927 | 122.937 | 122.4595 | 122.6352 | -0.48462
2355.1562 | 122.9736 | -122.612 | 0.21515 | 1.4211e-13 | -0.011286 | -0.0030619 | 0.029578 | -0.01455 | 0.0098841 | 0.0056466 | 0.0072744 | 0.0074993 | -0.0077383 | 0.042613 | 0.0020275 | 0.042253 | 0.001407 | -0.017566 | 0.18948 | -0.063746 | 0.44415 | 0.14757 | 0.042256 | 0.000359 | -0.019721 | 0.15776 | 0.31132 | -0.17539 | -0.29236 | 122.7596 | -0.02567 | 122.6543 | 122.5944 | -0.16514 | -0.2789 | 0.229 | 122.3196 | -0.057385 | 122.6543 | 122.5923 | 0.27264 | 0.096167 | -0.39054 | 122.8015 | 122.5483 | 123.0562 | 122.6134 | -0.067576 | 122.7698 | 122.9233 | 122.4366 | 122.6124 | -0.5075
2356.9062 | 122.9233 | -122.6303 | 0.1831 | 1.4211e-13 | -0.011286 | -0.0030619 | 0.029364 | -0.014978 | 0.010098 | 0.0056466 | 0.0072744 | 0.0074993 | -0.0081657 | 0.042613 | 0.0018139 | 0.037675 | -0.003172 | -0.012988 | 0.19864 | -0.068325 | 0.44415 | 0.15215 | 0.037677 | 0.004938 | -0.019721 | 0.16692 | 0.30674 | -0.16624 | -0.29693 | 122.7825 | 0.015531 | 122.668 | 122.6173 | -0.16514 | -0.25143 | 0.26105 | 122.3334 | -0.016184 | 122.668 | 122.6106 | 0.27721 | 0.12363 | -0.34934 | 122.8289 | 122.562 | 123.0745 | 122.6271 | -0.030953 | 122.7972 | 122.937 | 122.4641 | 122.6352 | -0.48004
2358.6719 | 122.9004 | -122.6669 | 0.23346 | 1.4211e-13 | -0.011286 | -0.0028483 | 0.029364 | -0.014764 | 0.010098 | -0.0019839 | 0.006847 | 0.0074993 | -0.0079521 | 0.042185 | 0.0020275 | 0.037675 | 0.001407 | -0.012988 | 0.20321 | -0.068325 | 0.44415 | 0.16131 | 0.042256 | 0.004938 | -0.015143 | 0.15776 | 0.31132 | -0.16624 | -0.29236 | 122.8282 | -0.030245 | 122.7046 | 122.6539 | -0.1743 | -0.30178 | 0.21069 | 122.3746 | -0.075695 | 122.7092 | 122.6518 | 0.27721 | 0.077857 | -0.3997 | 122.8701 | 122.5986 | 123.1111 | 122.6683 | -0.072149 | 122.8247 | 122.9782 | 122.5007 | 122.6719 | -0.52582
2360.3594 | 122.8546 | -122.6807 | 0.21973 | 1.4211e-13 | -0.011714 | -0.0030619 | 0.029578 | -0.015191 | 0.010311 | -0.0019839 | 0.0072744 | 0.0079267 | -0.0083793 | 0.042399 | 0.0022413 | 0.033096 | 0.005985 | -0.008409 | 0.19864 | -0.063746 | 0.44415 | 0.15215 | 0.042256 | 0.000359 | -0.015143 | 0.15776 | 0.30674 | -0.16624 | -0.30151 | 122.8328 | -0.021091 | 122.7138 | 122.6723 | -0.16056 | -0.28347 | 0.22443 | 122.3792 | -0.061963 | 122.7229 | 122.6655 | 0.28637 | 0.08701 | -0.38596 | 122.8793 | 122.6169 | 123.1248 | 122.6866 | -0.067575 | 122.8384 | 122.9874 | 122.5144 | 122.681 | -0.52124
2362.1094 | 122.9782 | -122.612 | 0.18768 | 1.4211e-13 | -0.011286 | -0.0030619 | 0.029578 | -0.014764 | 0.010098 | 0.020908 | 0.0072744 | 0.0072857 | -0.0085929 | 0.042399 | 0.0022413 | 0.033096 | 0.005985 | -0.012988 | 0.19864 | -0.050009 | 0.43957 | 0.14757 | 0.046835 | 0.004938 | -0.0243 | 0.15776 | 0.30216 | -0.16624 | -0.29693 | 122.7596 | 0.010953 | 122.6451 | 122.599 | -0.16056 | -0.23769 | 0.25189 | 122.3151 | -0.029919 | 122.6588 | 122.5877 | 0.27263 | 0.11447 | -0.35392 | 122.8106 | 122.562 | 123.0516 | 122.618 | -0.04011 | 122.7698 | 122.9142 | 122.4458 | 122.6169 | -0.48462
2363.8125 | 122.937 | -122.6303 | 0.21515 | 1.4211e-13 | -0.0115 | -0.0030619 | 0.029792 | -0.014764 | 0.0098841 | 0.0056466 | 0.0072744 | 0.0074993 | -0.0083793 | 0.042399 | 0.0020275 | 0.037675 | 0.005985 | -0.008409 | 0.20779 | -0.059167 | 0.44415 | 0.12926 | 0.042256 | 0.014095 | -0.0243 | 0.16234 | 0.30216 | -0.16624 | -0.29693 | 122.7596 | -0.007356 | 122.668 | 122.6219 | -0.13767 | -0.27432 | 0.229 | 122.3334 | -0.052807 | 122.6726 | 122.606 | 0.27263 | 0.087009 | -0.38138 | 122.8381 | 122.5711 | 123.0745 | 122.6363 | -0.085891 | 122.7927 | 122.9325 | 122.4641 | 122.6444 | -0.51208
2365.5625 | 122.9782 | -122.644 | 0.20599 | 1.4211e-13 | -0.0115 | -0.0028483 | 0.029578 | -0.014764 | 0.0098841 | 0.0056466 | 0.0070608 | 0.0077131 | -0.0081657 | 0.042613 | 0.0020275 | 0.033096 | 0.010564 | -0.022144 | 0.19864 | -0.063746 | 0.44415 | 0.14757 | 0.046835 | 0.004938 | -0.015143 | 0.16234 | 0.30674 | -0.16624 | -0.29693 | 122.7916 | -0.007358 | 122.6771 | 122.6219 | -0.16972 | -0.26974 | 0.23816 | 122.3471 | -0.043652 | 122.6909 | 122.6289 | 0.28179 | 0.10074 | -0.37223 | 122.8427 | 122.5803 | 123.0882 | 122.6546 | -0.058421 | 122.8064 | 122.9508 | 122.4778 | 122.649 | -0.50293
2367.3281 | 122.9553 | -122.6486 | 0.20599 | 1.4211e-13 | -0.0115 | -0.0030619 | 0.029578 | -0.015191 | 0.0098841 | 0.0056466 | 0.006847 | 0.0072857 | -0.0081657 | 0.042399 | 0.0020275 | 0.033096 | 0.001407 | -0.012988 | 0.19864 | -0.068325 | 0.44415 | 0.15673 | 0.042256 | 0.009516 | -0.0243 | 0.1715 | 0.30216 | -0.16624 | -0.30151 | 122.8054 | -0.007358 | 122.6817 | 122.6356 | -0.16972 | -0.27432 | 0.23816 | 122.3471 | -0.034495 | 122.6909 | 122.6243 | 0.27721 | 0.096164 | -0.37223 | 122.8473 | 122.5803 | 123.0928 | 122.65 | -0.049263 | 122.8201 | 122.9508 | 122.4824 | 122.6581 | -0.50751
2369.0312 | 122.8363 | -122.6852 | 0.2243 | 1.4211e-13 | -0.011927 | -0.0028483 | 0.029151 | -0.014978 | 0.0098841 | -0.0019839 | 0.0070608 | 0.0074993 | -0.0083793 | 0.042399 | 0.0022413 | 0.037675 | 0.010564 | -0.017566 | 0.19864 | -0.059167 | 0.43957 | 0.15673 | 0.042256 | 0.000359 | -0.019721 | 0.16234 | 0.30216 | -0.17997 | -0.29693 | 122.842 | -0.025668 | 122.7229 | 122.6677 | -0.1743 | -0.28347 | 0.21527 | 122.3883 | -0.061962 | 122.7275 | 122.6655 | 0.27721 | 0.077854 | -0.40428 | 122.8839 | 122.6261 | 123.1248 | 122.6958 | -0.067573 | 122.8476 | 122.9874 | 122.5053 | 122.6856 | -0.52124
2370.7656 | 122.8775 | -122.6624 | 0.21973 | 1.4211e-13 | -0.0115 | -0.0032757 | 0.029364 | -0.014764 | 0.010098 | 0.013277 | 0.0072744 | 0.0074993 | -0.0085929 | 0.042185 | 0.0018139 | 0.037675 | 0.005985 | -0.012988 | 0.19864 | -0.068325 | 0.44415 | 0.16131 | 0.033099 | 0.004938 | -0.0243 | 0.15776 | 0.30216 | -0.17081 | -0.29693 | 122.8237 | -0.021091 | 122.7 | 122.6494 | -0.1743 | -0.28805 | 0.22443 | 122.3654 | -0.061963 | 122.6955 | 122.6381 | 0.27263 | 0.082431 | -0.39054 | 122.861 | 122.594 | 123.1065 | 122.6683 | -0.058417 | 122.8201 | 122.9645 | 122.4915 | 122.6673 | -0.51666
2372.4531 | 122.9279 | -122.6578 | 0.21057 | 1.4211e-13 | -0.011927 | -0.0030619 | 0.029151 | -0.014764 | 0.010098 | -0.0019839 | 0.006847 | 0.0074993 | -0.0081657 | 0.042613 | 0.0022413 | 0.028518 | 0.005985 | -0.012988 | 0.19864 | -0.068325 | 0.44873 | 0.15215 | 0.042256 | 0.000359 | -0.015143 | 0.16692 | 0.30216 | -0.17081 | -0.29693 | 122.8099 | -0.011935 | 122.6863 | 122.6448 | -0.16514 | -0.2789 | 0.23816 | 122.3608 | -0.04365 | 122.7 | 122.6426 | 0.28179 | 0.091587 | -0.38139 | 122.8564 | 122.5895 | 123.1065 | 122.6638 | -0.058419 | 122.8247 | 122.9599 | 122.487 | 122.6581 | -0.5075
2374.2031 | 122.905 | -122.6898 | 0.2243 | 1.4211e-13 | -0.011714 | -0.0028483 | 0.029578 | -0.015191 | 0.010098 | -0.0019839 | 0.006847 | 0.0074993 | -0.0083793 | 0.041972 | 0.0022413 | 0.042253 | 0.010564 | -0.012988 | 0.1849 | -0.031693 | 0.44873 | 0.1201 | 0.037677 | 0.000359 | -0.019721 | 0.16692 | 0.31132 | -0.17539 | -0.29236 | 122.8099 | -0.039403 | 122.7321 | 122.6768 | -0.13309 | -0.256 | 0.22443 | 122.3975 | -0.057383 | 122.7275 | 122.6701 | 0.27264 | 0.087012 | -0.3997 | 122.8747 | 122.6581 | 123.1386 | 122.7004 | -0.1042 | 122.8567 | 123.0011 | 122.5144 | 122.6902 | -0.51666
2375.9531 | 122.9919 | -122.6349 | 0.21057 | 1.4211e-13 | -0.011714 | -0.0030619 | 0.029578 | -0.015191 | 0.0098841 | -0.0019839 | 0.0072744 | 0.0074993 | -0.0081657 | 0.042399 | 0.0022413 | 0.037675 | 0.005985 | -0.012988 | 0.20321 | -0.063746 | 0.44873 | 0.16131 | 0.037677 | 0.009516 | -0.015143 | 0.16234 | 0.30674 | -0.16624 | -0.29236 | 122.7962 | -0.007357 | 122.6726 | 122.6219 | -0.1743 | -0.27432 | 0.23816 | 122.3425 | -0.048229 | 122.6726 | 122.6197 | 0.27721 | 0.096166 | -0.37681 | 122.8381 | 122.5711 | 123.0836 | 122.6409 | -0.049261 | 122.7972 | 122.9416 | 122.4687 | 122.6444 | -0.50293
2377.6406 | 122.905 | -122.6715 | 0.25177 | 1.4211e-13 | -0.011714 | -0.0032757 | 0.029364 | -0.014978 | 0.010098 | -0.0019839 | 0.0072744 | 0.0077131 | -0.0081657 | 0.042613 | 0.0013867 | 0.042253 | 0.001407 | -0.012988 | 0.19406 | -0.027115 | 0.44873 | 0.12926 | 0.037677 | 0.009516 | -0.015143 | 0.16234 | 0.30674 | -0.17081 | -0.29693 | 122.8008 | -0.057712 | 122.7138 | 122.6585 | -0.14225 | -0.27888 | 0.19696 | 122.3746 | -0.089428 | 122.7092 | 122.6564 | 0.28179 | 0.054967 | -0.42258 | 122.8656 | 122.6444 | 123.1202 | 122.6729 | -0.12251 | 122.8339 | 122.9782 | 122.5007 | 122.681 | -0.5487
2379.3906 | 123.0057 | -122.6578 | 0.19226 | 1.4211e-13 | -0.0115 | -0.0030619 | 0.029578 | -0.014978 | 0.010098 | 0.0056466 | 0.0072744 | 0.0077131 | -0.0079521 | 0.042613 | 0.0022413 | 0.037675 | -0.003172 | -0.017566 | 0.19406 | -0.063746 | 0.44415 | 0.15215 | 0.042256 | 0.000359 | -0.019721 | 0.15776 | 0.30674 | -0.16624 | -0.30151 | 122.8099 | 0.001797 | 122.6955 | 122.6402 | -0.16972 | -0.25601 | 0.25189 | 122.3563 | -0.034497 | 122.7 | 122.6381 | 0.28179 | 0.11448 | -0.3585 | 122.8518 | 122.594 | 123.1019 | 122.6546 | -0.040109 | 122.8155 | 122.9645 | 122.4915 | 122.6581 | -0.49377
2381.1406 | 122.9141 | -122.6624 | 0.23346 | 1.4211e-13 | -0.011714 | -0.0028483 | 0.029578 | -0.015191 | 0.010098 | -0.0019839 | 0.0072744 | 0.0077131 | -0.0083793 | 0.042399 | 0.0022413 | 0.042253 | 0.005985 | -0.017566 | 0.19406 | -0.054588 | 0.44415 | 0.15215 | 0.046835 | 0.004938 | -0.019721 | 0.16234 | 0.30674 | -0.17081 | -0.30151 | 122.8145 | -0.039401 | 122.7046 | 122.6448 | -0.16972 | -0.28805 | 0.21069 | 122.3608 | -0.071117 | 122.7092 | 122.6426 | 0.28179 | 0.073278 | -0.40427 | 122.8564 | 122.6078 | 123.1065 | 122.6683 | -0.081307 | 122.8247 | 122.9691 | 122.4915 | 122.6673 | -0.53497
2382.8281 | 122.9233 | -122.6807 | 0.22888 | 1.4211e-13 | -0.011286 | -0.0034893 | 0.029364 | -0.015405 | 0.010098 | 0.0056466 | 0.0072744 | 0.0077131 | -0.0081657 | 0.042613 | 0.0020275 | 0.033096 | 0.001407 | -0.003831 | 0.19406 | -0.063746 | 0.44415 | 0.16131 | 0.037677 | 0.004938 | -0.019721 | 0.15776 | 0.30216 | -0.16624 | -0.29693 | 122.842 | -0.034824 | 122.7138 | 122.6768 | -0.16514 | -0.29263 | 0.21527 | 122.3837 | -0.071118 | 122.7183 | 122.6609 | 0.27721 | 0.073276 | -0.39512 | 122.8747 | 122.6169 | 123.1248 | 122.6821 | -0.067572 | 122.8384 | 122.9828 | 122.5144 | 122.6856 | -0.52582
2384.5781 | 122.9507 | -122.6669 | 0.20142 | 1.4211e-13 | -0.011714 | -0.0028483 | 0.029578 | -0.015191 | 0.010098 | -0.0019839 | 0.0070608 | 0.0072857 | -0.0081657 | 0.042399 | 0.0020275 | 0.037675 | 0.001407 | -0.012988 | 0.19406 | -0.059167 | 0.44873 | 0.15215 | 0.046835 | 0.000359 | -0.019721 | 0.16234 | 0.30216 | -0.17081 | -0.29236 | 122.8191 | -0.007358 | 122.7046 | 122.6539 | -0.16514 | -0.26058 | 0.24732 | 122.3746 | -0.039074 | 122.7138 | 122.6472 | 0.27264 | 0.10074 | -0.37223 | 122.861 | 122.6078 | 123.1157 | 122.6683 | -0.049264 | 122.8293 | 122.9691 | 122.4961 | 122.6673 | -0.49377
2386.3438 | 122.8683 | -122.7081 | 0.2243 | 1.4211e-13 | -0.0115 | -0.0032757 | 0.029364 | -0.014978 | 0.0096705 | 0.0056466 | 0.0070608 | 0.0074993 | -0.0081657 | 0.042185 | 0.0020275 | 0.037675 | 0.005985 | -0.017566 | 0.19864 | -0.059167 | 0.44415 | 0.15215 | 0.046835 | 0.009516 | -0.019721 | 0.16234 | 0.31132 | -0.17081 | -0.30151 | 122.8603 | -0.025668 | 122.7458 | 122.6906 | -0.16972 | -0.28347 | 0.21985 | 122.4066 | -0.061962 | 122.755 | 122.6884 | 0.28179 | 0.087012 | -0.39512 | 122.9068 | 122.649 | 123.1523 | 122.7141 | -0.072152 | 122.8705 | 123.0194 | 122.5373 | 122.7176 | -0.52582
2388.0312 | 122.9187 | -122.6852 | 0.21515 | 1.4211e-13 | -0.011714 | -0.0030619 | 0.029792 | -0.014978 | 0.010098 | 0.0056466 | 0.0072744 | 0.0072857 | -0.0077383 | 0.042613 | 0.0020275 | 0.023939 | 0.001407 | -0.012988 | 0.19864 | -0.063746 | 0.43957 | 0.15215 | 0.033099 | 0.000359 | -0.015143 | 0.16234 | 0.31132 | -0.16624 | -0.30151 | 122.8374 | -0.016513 | 122.7092 | 122.6723 | -0.16514 | -0.2789 | 0.22443 | 122.3837 | -0.052807 | 122.7183 | 122.6701 | 0.28637 | 0.096167 | -0.38138 | 122.8839 | 122.6215 | 123.1248 | 122.6866 | -0.062997 | 122.8476 | 122.9966 | 122.519 | 122.6856 | -0.51666
2389.7812 | 123.0331 | -122.6761 | 0.18768 | 1.4211e-13 | -0.011927 | -0.0030619 | 0.029792 | -0.014978 | 0.010311 | 0.0056466 | 0.0070608 | 0.0074993 | -0.0085929 | 0.042399 | 0.0022413 | 0.033096 | 0.001407 | -0.017566 | 0.19406 | -0.054588 | 0.44415 | 0.14757 | 0.037677 | -0.00422 | -0.015143 | 0.16234 | 0.30674 | -0.16166 | -0.29693 | 122.8237 | 0.006375 | 122.7092 | 122.6585 | -0.16514 | -0.24227 | 0.25647 | 122.3792 | -0.025341 | 122.7138 | 122.6609 | 0.28179 | 0.11905 | -0.34934 | 122.8701 | 122.6215 | 123.1202 | 122.6775 | -0.04011 | 122.8384 | 122.9828 | 122.5144 | 122.6719 | -0.48462
2391.5312 | 122.9691 | -122.6715 | 0.21057 | 1.4211e-13 | -0.011714 | -0.0030619 | 0.029364 | -0.014764 | 0.010311 | -0.0096144 | 0.0072744 | 0.0074993 | -0.0081657 | 0.042399 | 0.0022413 | 0.033096 | 0.001407 | -0.008409 | 0.19406 | -0.059167 | 0.44873 | 0.14299 | 0.037677 | 0.004938 | -0.0243 | 0.1715 | 0.30216 | -0.16624 | -0.29693 | 122.8145 | -0.016513 | 122.7046 | 122.6631 | -0.1514 | -0.26974 | 0.23816 | 122.3746 | -0.039072 | 122.7092 | 122.6472 | 0.27263 | 0.091587 | -0.37681 | 122.8656 | 122.6123 | 123.1202 | 122.6729 | -0.067577 | 122.843 | 122.9737 | 122.5053 | 122.6764 | -0.5075
2393.2812 | 122.9324 | -122.6852 | 0.23804 | 1.4211e-13 | -0.0115 | -0.0030619 | 0.029151 | -0.015191 | 0.010311 | 0.0056466 | 0.0072744 | 0.0074993 | -0.0081657 | 0.042399 | 0.0020275 | 0.037675 | 0.001407 | -0.012988 | 0.19864 | -0.059167 | 0.44873 | 0.16131 | 0.042256 | 0.009516 | -0.019721 | 0.15776 | 0.30216 | -0.17539 | -0.29693 | 122.8466 | -0.039401 | 122.7229 | 122.6723 | -0.1743 | -0.2972 | 0.2107 | 122.3883 | -0.080273 | 122.7275 | 122.6655 | 0.27721 | 0.064121 | -0.41343 | 122.8839 | 122.6261 | 123.134 | 122.6866 | -0.076727 | 122.843 | 122.9874 | 122.5098 | 122.6948 | -0.53497
2395.0312 | 122.9645 | -122.7081 | 0.21057 | 1.4211e-13 | -0.011286 | -0.0032757 | 0.029578 | -0.014978 | 0.010311 | -0.0019839 | 0.0070608 | 0.0077131 | -0.0077383 | 0.042185 | 0.0020275 | 0.042253 | 0.001407 | -0.012988 | 0.19406 | -0.063746 | 0.43957 | 0.16131 | 0.042256 | 0.004938 | -0.0243 | 0.1715 | 0.30674 | -0.17081 | -0.30609 | 122.8694 | -0.016513 | 122.7504 | 122.6951 | -0.1743 | -0.27432 | 0.229 | 122.402 | -0.039072 | 122.7504 | 122.6838 | 0.28179 | 0.096166 | -0.38139 | 122.9022 | 122.6444 | 123.1477 | 122.7095 | -0.049261 | 122.8796 | 123.0149 | 122.5373 | 122.7131 | -0.51666
2396.7188 | 122.8958 | -122.731 | 0.23804 | 1.4211e-13 | -0.0115 | -0.0026347 | 0.029578 | -0.015191 | 0.0098841 | 0.013277 | 0.0070608 | 0.0074993 | -0.0081657 | 0.042613 | 0.0022413 | 0.037675 | 0.005985 | -0.012988 | 0.19864 | -0.050009 | 0.43957 | 0.15215 | 0.046835 | 0.014095 | -0.0243 | 0.16692 | 0.30674 | -0.17081 | -0.30151 | 122.8832 | -0.039401 | 122.7687 | 122.718 | -0.16514 | -0.28805 | 0.20154 | 122.4295 | -0.071116 | 122.7779 | 122.7067 | 0.27721 | 0.0687 | -0.40885 | 122.9297 | 122.681 | 123.1706 | 122.737 | -0.085885 | 122.8979 | 123.0378 | 122.5602 | 122.7451 | -0.53955
2398.4844 | 122.9645 | -122.6578 | 0.22888 | 1.4211e-13 | -0.011927 | -0.0032757 | 0.029364 | -0.014978 | 0.010098 | 0.0056466 | 0.0070608 | 0.0072857 | -0.0083793 | 0.042399 | 0.0018139 | 0.037675 | 0.015142 | -0.008409 | 0.19864 | -0.059167 | 0.44873 | 0.15215 | 0.046835 | 0.009516 | -0.010564 | 0.16234 | 0.30674 | -0.17539 | -0.29693 | 122.8099 | -0.030246 | 122.6955 | 122.6494 | -0.16056 | -0.28805 | 0.21985 | 122.3608 | -0.06654 | 122.7046 | 122.6472 | 0.28637 | 0.077855 | -0.40427 | 122.8564 | 122.5986 | 123.1065 | 122.6729 | -0.07673 | 122.8201 | 122.9645 | 122.4824 | 122.6673 | -0.52582
2400.2344 | 123.0103 | -122.6486 | 0.19684 | 1.4211e-13 | -0.0115 | -0.0032757 | 0.029578 | -0.014978 | 0.0098841 | 0.0056466 | 0.0072744 | 0.0070721 | -0.0083793 | 0.042613 | 0.0016003 | 0.042253 | 0.001407 | -0.017566 | 0.19864 | -0.040851 | 0.44873 | 0.15215 | 0.037677 | 0.009516 | -0.015143 | 0.16234 | 0.30216 | -0.17081 | -0.30151 | 122.8008 | 0.001798 | 122.6909 | 122.6311 | -0.16972 | -0.23769 | 0.25189 | 122.3471 | -0.034496 | 122.6863 | 122.6335 | 0.28637 | 0.10532 | -0.36765 | 122.8473 | 122.6078 | 123.0974 | 122.65 | -0.044686 | 122.811 | 122.9508 | 122.4778 | 122.6581 | -0.49835
2401.9844 | 122.9553 | -122.7036 | 0.2243 | 1.4211e-13 | -0.011714 | -0.0028483 | 0.029578 | -0.014764 | 0.010098 | -0.0019839 | 0.007488 | 0.0072857 | -0.0083793 | 0.042613 | 0.0022413 | 0.037675 | 0.005985 | -0.008409 | 0.19864 | -0.059167 | 0.44873 | 0.16131 | 0.046835 | 0.000359 | -0.0243 | 0.15776 | 0.30674 | -0.17539 | -0.29693 | 122.8649 | -0.025668 | 122.7412 | 122.6951 | -0.16972 | -0.28347 | 0.22443 | 122.4066 | -0.06654 | 122.7504 | 122.6793 | 0.27263 | 0.082433 | -0.3997 | 122.9022 | 122.6444 | 123.1523 | 122.7095 | -0.062994 | 122.8613 | 123.0103 | 122.5282 | 122.7039 | -0.52124
2403.6875 | 122.9279 | -122.7264 | 0.21973 | 1.4211e-13 | -0.0115 | -0.0032757 | 0.029364 | -0.014978 | 0.0098841 | -0.0019839 | 0.0070608 | 0.0074993 | -0.0081657 | 0.042399 | 0.0024549 | 0.037675 | 0.010564 | -0.008409 | 0.19406 | -0.027115 | 0.44415 | 0.15673 | 0.042256 | 0.009516 | -0.0243 | 0.16234 | 0.31132 | -0.17081 | -0.30151 | 122.8832 | -0.025669 | 122.7641 | 122.718 | -0.16514 | -0.24684 | 0.22443 | 122.4249 | -0.057385 | 122.7687 | 122.7021 | 0.27721 | 0.091589 | -0.39054 | 122.9205 | 122.6993 | 123.1706 | 122.737 | -0.062996 | 122.8888 | 123.0378 | 122.5556 | 122.736 | -0.52124
2405.4375 | 123.0057 | -122.6852 | 0.19226 | 1.4211e-13 | -0.011286 | -0.0032757 | 0.029364 | -0.015191 | 0.010311 | 0.0056466 | 0.0070608 | 0.0070721 | -0.0083793 | 0.042613 | 0.0018139 | 0.037675 | 0.001407 | -0.008409 | 0.19406 | -0.059167 | 0.44415 | 0.15673 | 0.037677 | 0.009516 | -0.019721 | 0.15776 | 0.30674 | -0.16624 | -0.29693 | 122.842 | 0.001797 | 122.7229 | 122.6768 | -0.16514 | -0.25143 | 0.25189 | 122.3883 | -0.034497 | 122.7229 | 122.6655 | 0.27721 | 0.11448 | -0.3585 | 122.8793 | 122.6261 | 123.1294 | 122.6866 | -0.03553 | 122.843 | 122.992 | 122.519 | 122.6948 | -0.48919
2407.125 | 123.0286 | -122.6944 | 0.19226 | 1.4211e-13 | -0.0115 | -0.0030619 | 0.029364 | -0.014978 | 0.0098841 | -0.0019839 | 0.0072744 | 0.0072857 | -0.0081657 | 0.042399 | 0.0020275 | 0.037675 | 0.010564 | -0.012988 | 0.18948 | -0.059167 | 0.43957 | 0.15215 | 0.046835 | -0.00422 | -0.015143 | 0.16692 | 0.31132 | -0.17081 | -0.30151 | 122.8465 | -0.002782 | 122.7321 | 122.6814 | -0.16514 | -0.25143 | 0.24731 | 122.3929 | -0.02534 | 122.7412 | 122.6793 | 0.28637 | 0.11905 | -0.36308 | 122.8839 | 122.6352 | 123.134 | 122.705 | -0.040109 | 122.8613 | 123.0057 | 122.5236 | 122.6902 | -0.49377
2408.875 | 122.9416 | -122.7081 | 0.23346 | 1.4211e-13 | -0.011927 | -0.0030619 | 0.029578 | -0.015191 | 0.010311 | -0.0019839 | 0.0072744 | 0.0074993 | -0.0081657 | 0.042399 | 0.0020275 | 0.033096 | 0.005985 | -0.008409 | 0.18948 | -0.063746 | 0.43957 | 0.15215 | 0.046835 | 0.004938 | -0.0243 | 0.16234 | 0.30216 | -0.17081 | -0.29236 | 122.8603 | -0.04398 | 122.7412 | 122.6997 | -0.16056 | -0.2972 | 0.20612 | 122.4158 | -0.071117 | 122.755 | 122.6838 | 0.26806 | 0.068699 | -0.40427 | 122.8976 | 122.6444 | 123.1477 | 122.7141 | -0.081307 | 122.8705 | 123.0103 | 122.5373 | 122.7131 | -0.52582
2410.5625 | 122.9187 | -122.731 | 0.23346 | 1.4211e-13 | -0.011714 | -0.0030619 | 0.029364 | -0.015191 | 0.0098841 | 0.0056466 | 0.0072744 | 0.0074993 | -0.0085929 | 0.042399 | 0.0020275 | 0.037675 | 0.001407 | -0.012988 | 0.19864 | -0.063746 | 0.45331 | 0.15673 | 0.037677 | 0.004938 | -0.019721 | 0.16692 | 0.30216 | -0.17081 | -0.30151 | 122.8877 | -0.034823 | 122.7687 | 122.718 | -0.16972 | -0.2972 | 0.21985 | 122.4295 | -0.066538 | 122.7687 | 122.7113 | 0.28179 | 0.068699 | -0.40427 | 122.9297 | 122.6673 | 123.1843 | 122.7324 | -0.076728 | 122.8979 | 123.0332 | 122.5602 | 122.736 | -0.53497
2412.2969 | 122.8867 | -122.7173 | 0.21515 | 1.4211e-13 | -0.011286 | -0.0032757 | 0.029792 | -0.014764 | 0.010525 | 0.0056466 | 0.0070608 | 0.0072857 | -0.0081657 | 0.042399 | 0.0020275 | 0.033096 | -0.003172 | -0.012988 | 0.19406 | -0.063746 | 0.435 | 0.15215 | 0.037677 | -0.00422 | -0.0243 | 0.16692 | 0.30216 | -0.17081 | -0.29693 | 122.8694 | -0.021091 | 122.7504 | 122.7043 | -0.16514 | -0.2789 | 0.21985 | 122.4204 | -0.048228 | 122.755 | 122.693 | 0.27263 | 0.087009 | -0.38596 | 122.9113 | 122.6535 | 123.1523 | 122.7141 | -0.062997 | 122.8842 | 123.0194 | 122.5465 | 122.7131 | -0.51208
2414.0469 | 122.9416 | -122.7173 | 0.22888 | 1.4211e-13 | -0.0115 | -0.0032757 | 0.029792 | -0.015191 | 0.010098 | 0.013277 | 0.007488 | 0.0072857 | -0.0083793 | 0.042613 | 0.0020275 | 0.037675 | 0.005985 | -0.008409 | 0.20321 | -0.068325 | 0.45331 | 0.15673 | 0.037677 | 0.004938 | -0.019721 | 0.16234 | 0.31132 | -0.17081 | -0.30151 | 122.874 | -0.025668 | 122.755 | 122.7089 | -0.16514 | -0.29721 | 0.22443 | 122.4158 | -0.06654 | 122.755 | 122.6976 | 0.28179 | 0.082434 | -0.3997 | 122.9205 | 122.649 | 123.1706 | 122.7233 | -0.072151 | 122.8796 | 123.0286 | 122.5465 | 122.7222 | -0.53039
2415.7344 | 122.9279 | -122.7127 | 0.21973 | 1.4211e-13 | -0.011927 | -0.0032757 | 0.029151 | -0.015191 | 0.0096705 | -0.0019839 | 0.0072744 | 0.0072857 | -0.0083793 | 0.042399 | 0.0020275 | 0.033096 | 0.001407 | -0.008409 | 0.19864 | -0.059167 | 0.44415 | 0.16131 | 0.042256 | 0.000359 | -0.015143 | 0.16692 | 0.31132 | -0.17081 | -0.29693 | 122.874 | -0.021091 | 122.7458 | 122.7043 | -0.16972 | -0.27889 | 0.22443 | 122.4158 | -0.052806 | 122.755 | 122.6976 | 0.28179 | 0.091589 | -0.39054 | 122.9113 | 122.6535 | 123.1569 | 122.7141 | -0.058417 | 122.8796 | 123.024 | 122.5419 | 122.7131 | -0.51666
2417.4844 | 123.0057 | -122.7036 | 0.21057 | 1.4211e-13 | -0.011714 | -0.0030619 | 0.029151 | -0.014764 | 0.0098841 | -0.0019839 | 0.0066334 | 0.0077131 | -0.0083793 | 0.042613 | 0.0018139 | 0.042253 | 0.001407 | -0.012988 | 0.19864 | -0.059167 | 0.44873 | 0.15673 | 0.042256 | 0.000359 | -0.0243 | 0.16692 | 0.31132 | -0.16624 | -0.30151 | 122.8603 | -0.011935 | 122.7458 | 122.6906 | -0.16972 | -0.26974 | 0.23816 | 122.402 | -0.04365 | 122.7458 | 122.6793 | 0.27721 | 0.10074 | -0.37681 | 122.9022 | 122.6444 | 123.1523 | 122.705 | -0.05384 | 122.8705 | 123.0149 | 122.5373 | 122.7039 | -0.51208
2419.2656 | 123.0103 | -122.7036 | 0.20599 | 1.4211e-13 | -0.012141 | -0.0028483 | 0.029364 | -0.015191 | 0.010098 | 0.013277 | 0.0070608 | 0.0079267 | -0.0083793 | 0.042613 | 0.0018139 | 0.037675 | 0.005985 | -0.012988 | 0.19406 | -0.059167 | 0.44415 | 0.15673 | 0.033099 | 0.004938 | -0.0243 | 0.16234 | 0.31132 | -0.17081 | -0.29693 | 122.8603 | -0.011936 | 122.7412 | 122.6906 | -0.16972 | -0.26516 | 0.23816 | 122.4066 | -0.043652 | 122.7367 | 122.6793 | 0.27263 | 0.10532 | -0.37681 | 122.8976 | 122.6444 | 123.1477 | 122.7095 | -0.049263 | 122.8659 | 123.0149 | 122.5327 | 122.7085 | -0.50293
2420.9531 | 123.0469 | -122.6944 | 0.19226 | 1.4211e-13 | -0.011714 | -0.0034893 | 0.029578 | -0.014764 | 0.010525 | -0.0019839 | 0.006847 | 0.0072857 | -0.0083793 | 0.042399 | 0.0018139 | 0.037675 | 0.001407 | -0.017566 | 0.18948 | -0.063746 | 0.44415 | 0.15215 | 0.046835 | 0.004938 | -0.019721 | 0.16692 | 0.30674 | -0.17081 | -0.30151 | 122.8465 | -0.002782 | 122.7321 | 122.6768 | -0.16972 | -0.25601 | 0.25189 | 122.3929 | -0.02534 | 122.7412 | 122.6747 | 0.28179 | 0.11448 | -0.36308 | 122.8839 | 122.6307 | 123.1386 | 122.6958 | -0.040109 | 122.8613 | 123.0011 | 122.5236 | 122.6993 | -0.49377
2422.7031 | 123.0377 | -122.7036 | 0.21515 | 1.4211e-13 | -0.011927 | -0.0037031 | 0.029364 | -0.014764 | 0.010311 | -0.0019839 | 0.0072744 | 0.0072857 | -0.0083793 | 0.042613 | 0.0020275 | 0.037675 | 0.010564 | -0.012988 | 0.19864 | -0.068325 | 0.45331 | 0.15215 | 0.042256 | 0.004938 | -0.019721 | 0.16234 | 0.30216 | -0.17081 | -0.30151 | 122.8557 | -0.016513 | 122.7412 | 122.6906 | -0.16514 | -0.28347 | 0.23816 | 122.402 | -0.052807 | 122.7458 | 122.6838 | 0.28179 | 0.087009 | -0.38596 | 122.9022 | 122.6352 | 123.1569 | 122.7141 | -0.062997 | 122.8659 | 123.0057 | 122.5327 | 122.7085 | -0.51666
2424.4062 | 122.9599 | -122.7173 | 0.21057 | 1.4211e-13 | -0.011714 | -0.0032757 | 0.029364 | -0.014978 | 0.010098 | -0.0019839 | 0.006847 | 0.0070721 | -0.0081657 | 0.042827 | 0.0020275 | 0.033096 | 0.005985 | -0.003831 | 0.19406 | -0.063746 | 0.44873 | 0.15673 | 0.046835 | 0.000359 | -0.019721 | 0.16692 | 0.30674 | -0.17539 | -0.29693 | 122.874 | -0.016513 | 122.7504 | 122.7135 | -0.16056 | -0.27432 | 0.23816 | 122.4204 | -0.04365 | 122.7641 | 122.6976 | 0.27721 | 0.096166 | -0.38596 | 122.9113 | 122.6535 | 123.166 | 122.7233 | -0.05384 | 122.8842 | 123.024 | 122.5419 | 122.7176 | -0.5075
2426.1719 | 122.937 | -122.7493 | 0.2243 | 1.4211e-13 | -0.012141 | -0.0032757 | 0.029578 | -0.014978 | 0.0098841 | 0.0056466 | 0.006847 | 0.0070721 | -0.0081657 | 0.042399 | 0.0020275 | 0.037675 | 0.001407 | -0.003831 | 0.19864 | -0.054588 | 0.44873 | 0.14757 | 0.042256 | 0.004938 | -0.019721 | 0.16692 | 0.30216 | -0.17539 | -0.29693 | 122.8969 | -0.025668 | 122.787 | 122.7455 | -0.1514 | -0.27889 | 0.22443 | 122.4524 | -0.057383 | 122.7916 | 122.7296 | 0.27721 | 0.077854 | -0.3997 | 122.948 | 122.6947 | 123.1981 | 122.7507 | -0.076731 | 122.9163 | 123.0515 | 122.5739 | 122.7543 | -0.52124
2427.875 | 122.9645 | -122.7448 | 0.2243 | 1.4211e-13 | -0.012141 | -0.0030619 | 0.029364 | -0.014764 | 0.010098 | 0.0056466 | 0.0070608 | 0.0072857 | -0.0079521 | 0.042399 | 0.0020275 | 0.042253 | 0.010564 | -0.012988 | 0.18948 | -0.063746 | 0.45331 | 0.15673 | 0.042256 | 0.009516 | -0.0243 | 0.16234 | 0.31132 | -0.16624 | -0.29693 | 122.9015 | -0.034825 | 122.787 | 122.7318 | -0.16972 | -0.28805 | 0.22901 | 122.4478 | -0.061962 | 122.787 | 122.7205 | 0.27263 | 0.087012 | -0.39054 | 122.9342 | 122.681 | 123.1981 | 122.7553 | -0.067573 | 122.9071 | 123.0561 | 122.5785 | 122.7543 | -0.52124
2429.6406 | 122.9782 | -122.7264 | 0.23346 | 1.4211e-13 | -0.011714 | -0.0030619 | 0.029364 | -0.015405 | 0.010098 | 0.0056466 | 0.0072744 | 0.0070721 | -0.0081657 | 0.042399 | 0.0022413 | 0.037675 | 0.001407 | -0.008409 | 0.19406 | -0.063746 | 0.44873 | 0.15673 | 0.046835 | 0.009516 | -0.015143 | 0.16234 | 0.30216 | -0.17081 | -0.30151 | 122.8832 | -0.039401 | 122.7641 | 122.718 | -0.16514 | -0.2972 | 0.21527 | 122.4249 | -0.071117 | 122.7733 | 122.7113 | 0.28637 | 0.068699 | -0.40427 | 122.9205 | 122.6627 | 123.1752 | 122.7278 | -0.076728 | 122.8888 | 123.0286 | 122.5556 | 122.736 | -0.53497
2431.4062 | 123.0057 | -122.7173 | 0.20142 | 1.4211e-13 | -0.011714 | -0.0028483 | 0.029578 | -0.015191 | 0.010098 | 0.0056466 | 0.006847 | 0.0072857 | -0.0083793 | 0.042613 | 0.0016003 | 0.037675 | 0.001407 | -0.008409 | 0.19864 | -0.063746 | 0.44415 | 0.15673 | 0.046835 | 0.018674 | -0.019721 | 0.16234 | 0.30216 | -0.17081 | -0.29693 | 122.874 | -0.00278 | 122.755 | 122.7089 | -0.16514 | -0.26516 | 0.24274 | 122.4204 | -0.039074 | 122.7641 | 122.6976 | 0.27721 | 0.10074 | -0.37223 | 122.9159 | 122.6535 | 123.1614 | 122.7187 | -0.044685 | 122.8796 | 123.0194 | 122.5465 | 122.736 | -0.49835
2433.1562 | 122.9874 | -122.7264 | 0.20599 | 1.4211e-13 | -0.011714 | -0.0030619 | 0.029151 | -0.015191 | 0.0098841 | -0.0019839 | 0.0072744 | 0.0074993 | -0.0085929 | 0.042399 | 0.0018139 | 0.042253 | 0.010564 | -0.017566 | 0.19406 | -0.054588 | 0.43957 | 0.15673 | 0.046835 | 0.000359 | -0.010564 | 0.16692 | 0.30216 | -0.17081 | -0.30609 | 122.8832 | -0.011936 | 122.7687 | 122.7089 | -0.1743 | -0.26058 | 0.23358 | 122.4203 | -0.039073 | 122.7733 | 122.7159 | 0.29553 | 0.096164 | -0.37681 | 122.9205 | 122.6719 | 123.166 | 122.737 | -0.049263 | 122.8934 | 123.0286 | 122.5556 | 122.7268 | -0.51209
2434.8594 | 122.9691 | -122.7402 | 0.2243 | 1.4211e-13 | -0.012141 | -0.0028483 | 0.029578 | -0.014764 | 0.0098841 | -0.0019839 | 0.0072744 | 0.0074993 | -0.0081657 | 0.042613 | 0.0018139 | 0.037675 | 0.001407 | -0.012988 | 0.19406 | -0.063746 | 0.45331 | 0.15215 | 0.051413 | 0.009516 | -0.019721 | 0.16692 | 0.30674 | -0.17081 | -0.30151 | 122.8923 | -0.030246 | 122.7778 | 122.7272 | -0.16514 | -0.28805 | 0.22901 | 122.4387 | -0.057383 | 122.7916 | 122.7205 | 0.28179 | 0.082433 | -0.39512 | 122.9342 | 122.6764 | 123.1935 | 122.7416 | -0.072152 | 122.9071 | 123.0469 | 122.5694 | 122.7497 | -0.52582
2436.625 | 122.9324 | -122.7493 | 0.22888 | 1.4211e-13 | -0.011714 | -0.0028483 | 0.029792 | -0.015191 | 0.010098 | 0.013277 | 0.0070608 | 0.0072857 | -0.0083793 | 0.042399 | 0.0018139 | 0.037675 | 0.005985 | -0.012988 | 0.20321 | -0.059167 | 0.45331 | 0.15215 | 0.046835 | 0.009516 | -0.0243 | 0.16692 | 0.31132 | -0.16624 | -0.30151 | 122.9015 | -0.025668 | 122.787 | 122.7363 | -0.16514 | -0.28805 | 0.22443 | 122.4478 | -0.061961 | 122.7962 | 122.725 | 0.27721 | 0.082434 | -0.39512 | 122.9525 | 122.6902 | 123.2026 | 122.7553 | -0.07673 | 122.9163 | 123.0606 | 122.5831 | 122.7588 | -0.53039
2438.3125 | 122.9736 | -122.7631 | 0.23804 | 1.4211e-13 | -0.011927 | -0.0030619 | 0.029364 | -0.015191 | 0.0098841 | -0.0019839 | 0.0070608 | 0.0077131 | -0.0083793 | 0.042613 | 0.0020275 | 0.033096 | 0.005985 | -0.012988 | 0.20321 | -0.063746 | 0.45331 | 0.16131 | 0.042256 | 0.009516 | -0.019721 | 0.16234 | 0.31132 | -0.17081 | -0.29693 | 122.9244 | -0.034823 | 122.7962 | 122.7501 | -0.1743 | -0.30178 | 0.21527 | 122.4661 | -0.075695 | 122.8053 | 122.7433 | 0.27721 | 0.073279 | -0.40885 | 122.9663 | 122.6993 | 123.2164 | 122.769 | -0.076727 | 122.9254 | 123.0744 | 122.5922 | 122.7726 | -0.53497
2440.0625 | 122.937 | -122.7493 | 0.23804 | 1.4211e-13 | -0.011927 | -0.0032757 | 0.029578 | -0.014764 | 0.010098 | -0.0019839 | 0.007488 | 0.0074993 | -0.0081657 | 0.042613 | 0.0022413 | 0.042253 | 0.010564 | -0.008409 | 0.19864 | -0.054588 | 0.44873 | 0.15673 | 0.046835 | 0.000359 | -0.019721 | 0.16234 | 0.30674 | -0.17539 | -0.28778 | 122.9061 | -0.039401 | 122.7916 | 122.7409 | -0.16514 | -0.29263 | 0.2107 | 122.4616 | -0.075695 | 122.7962 | 122.7296 | 0.26806 | 0.0687 | -0.41343 | 122.948 | 122.6947 | 123.1981 | 122.7599 | -0.081306 | 122.9117 | 123.0561 | 122.5739 | 122.7497 | -0.52581
2441.8125 | 123.0194 | -122.7036 | 0.21057 | 1.4211e-13 | -0.011927 | -0.0032757 | 0.029578 | -0.015191 | 0.010525 | -0.0019839 | 0.0072744 | 0.0072857 | -0.0083793 | 0.042399 | 0.0018139 | 0.033096 | 0.005985 | -0.012988 | 0.19864 | -0.054588 | 0.44873 | 0.15673 | 0.042256 | 0.004938 | -0.0243 | 0.1715 | 0.31589 | -0.17539 | -0.29693 | 122.8603 | -0.011935 | 122.7366 | 122.6906 | -0.16972 | -0.26516 | 0.23816 | 122.4066 | -0.039072 | 122.7458 | 122.6793 | 0.27263 | 0.10532 | -0.38596 | 122.9022 | 122.649 | 123.1523 | 122.7095 | -0.05384 | 122.8751 | 123.0194 | 122.5282 | 122.7085 | -0.5075
2443.5156 | 123.0011 | -122.731 | 0.20599 | 1.4211e-13 | -0.012141 | -0.0030619 | 0.029792 | -0.014978 | 0.010311 | -0.0019839 | 0.0070608 | 0.0074993 | -0.0081657 | 0.042399 | 0.0018139 | 0.037675 | 0.005985 | -0.012988 | 0.19406 | -0.04543 | 0.44415 | 0.15215 | 0.046835 | 0.004938 | -0.028879 | 0.16234 | 0.30674 | -0.17539 | -0.30151 | 122.8832 | -0.011936 | 122.7687 | 122.718 | -0.16514 | -0.25142 | 0.23816 | 122.4295 | -0.043652 | 122.7779 | 122.7021 | 0.27263 | 0.10074 | -0.38139 | 122.9251 | 122.6856 | 123.1752 | 122.737 | -0.053842 | 122.8934 | 123.0378 | 122.5556 | 122.736 | -0.50751
2445.2812 | 123.0743 | -122.7081 | 0.18768 | 1.4211e-13 | -0.011927 | -0.0032757 | 0.029578 | -0.014978 | 0.0098841 | 0.0056466 | 0.0070608 | 0.0074993 | -0.0083793 | 0.042613 | 0.0020275 | 0.033096 | 0.001407 | -0.012988 | 0.19864 | -0.059167 | 0.45331 | 0.14757 | 0.037677 | 0.004938 | -0.028879 | 0.16692 | 0.30216 | -0.17081 | -0.29693 | 122.8557 | 0.010953 | 122.7412 | 122.6951 | -0.16056 | -0.24685 | 0.26563 | 122.4112 | -0.020762 | 122.7458 | 122.6793 | 0.26805 | 0.11447 | -0.3585 | 122.9068 | 122.649 | 123.1614 | 122.7095 | -0.04011 | 122.8751 | 123.0103 | 122.5373 | 122.7131 | -0.48462
2447.0469 | 123.024 | -122.7264 | 0.20599 | 1.4211e-13 | -0.011927 | -0.0032757 | 0.029792 | -0.014764 | 0.010311 | 0.020908 | 0.0070608 | 0.0077131 | -0.0085929 | 0.042613 | 0.0020275 | 0.037675 | -0.003172 | -0.012988 | 0.19406 | -0.063746 | 0.44873 | 0.15673 | 0.037677 | 0.004938 | -0.0243 | 0.15776 | 0.30674 | -0.17081 | -0.30151 | 122.8832 | -0.011936 | 122.7641 | 122.7135 | -0.16972 | -0.26974 | 0.24274 | 122.4249 | -0.04823 | 122.7641 | 122.7021 | 0.27721 | 0.10074 | -0.37681 | 122.9205 | 122.6627 | 123.1752 | 122.7233 | -0.049263 | 122.8842 | 123.0332 | 122.5556 | 122.7314 | -0.50751
2448.75 | 123.0469 | -122.7219 | 0.19226 | 1.4211e-13 | -0.012355 | -0.0028483 | 0.029364 | -0.014978 | 0.010311 | -0.0019839 | 0.0072744 | 0.0074993 | -0.0081657 | 0.042613 | 0.0018139 | 0.037675 | -0.003172 | -0.008409 | 0.20321 | -0.059167 | 0.44873 | 0.15215 | 0.046835 | 0.000359 | -0.019721 | 0.16234 | 0.31132 | -0.17539 | -0.29693 | 122.874 | 0.010953 | 122.7595 | 122.7135 | -0.16056 | -0.25143 | 0.25647 | 122.4249 | -0.029919 | 122.7687 | 122.7021 | 0.27721 | 0.11905 | -0.36765 | 122.9251 | 122.6627 | 123.1706 | 122.7187 | -0.040109 | 122.8842 | 123.0332 | 122.5465 | 122.7222 | -0.48919
2450.5 | 122.9462 | -122.7539 | 0.2243 | 1.4211e-13 | -0.012141 | -0.0032757 | 0.029364 | -0.014764 | 0.0098841 | -0.0019839 | 0.0072744 | 0.0072857 | -0.0081657 | 0.042613 | 0.0020275 | 0.037675 | 0.005985 | -0.008409 | 0.19406 | -0.059167 | 0.45331 | 0.15215 | 0.037677 | 0.004938 | -0.019721 | 0.16234 | 0.30216 | -0.17539 | -0.30151 | 122.9061 | -0.030246 | 122.7916 | 122.7455 | -0.16056 | -0.28347 | 0.22901 | 122.4524 | -0.061962 | 122.7916 | 122.7342 | 0.28179 | 0.077854 | -0.3997 | 122.948 | 122.6947 | 123.2072 | 122.7599 | -0.072152 | 122.9162 | 123.0561 | 122.5785 | 122.7588 | -0.52582
2452.25 | 122.9599 | -122.7631 | 0.21515 | 1.4211e-13 | -0.011927 | -0.0028483 | 0.029792 | -0.015191 | 0.010098 | -0.0019839 | 0.0072744 | 0.0077131 | -0.0081657 | 0.042613 | 0.0020275 | 0.042253 | -0.003172 | -0.008409 | 0.19406 | -0.068325 | 0.41668 | 0.16131 | 0.037677 | 0.004938 | -0.0243 | 0.1715 | 0.30216 | -0.17539 | -0.29693 | 122.9244 | -0.021091 | 122.8053 | 122.7547 | -0.16972 | -0.28347 | 0.20153 | 122.4661 | -0.04365 | 122.8007 | 122.7388 | 0.27263 | 0.087009 | -0.39054 | 122.9571 | 122.6947 | 123.1797 | 122.7599 | -0.053839 | 122.9346 | 123.0652 | 122.5877 | 122.768 | -0.51208
2454.0156 | 123.0148 | -122.7219 | 0.20142 | 1.4211e-13 | -0.012141 | -0.0030619 | 0.029578 | -0.014978 | 0.010311 | 0.0056466 | 0.0070608 | 0.0070721 | -0.0079521 | 0.042613 | 0.0018139 | 0.028518 | -0.003172 | -0.017566 | 0.20321 | -0.054588 | 0.44415 | 0.15215 | 0.037677 | 0.009516 | -0.019721 | 0.16234 | 0.30674 | -0.17539 | -0.29693 | 122.874 | 0.001798 | 122.7504 | 122.7043 | -0.16972 | -0.256 | 0.24274 | 122.4249 | -0.039074 | 122.7595 | 122.7021 | 0.27721 | 0.10532 | -0.37681 | 122.9251 | 122.6673 | 123.166 | 122.7187 | -0.049264 | 122.8842 | 123.0286 | 122.5465 | 122.7314 | -0.49835
2455.7031 | 123.0148 | -122.731 | 0.19684 | 1.4211e-13 | -0.012141 | -0.0030619 | 0.029578 | -0.015191 | 0.0098841 | -0.0096144 | 0.0072744 | 0.0074993 | -0.0079521 | 0.042399 | 0.0018139 | 0.033096 | 0.001407 | -0.008409 | 0.19864 | -0.063746 | 0.44873 | 0.16131 | 0.037677 | 0.000359 | -0.015143 | 0.16692 | 0.30674 | -0.17539 | -0.29693 | 122.8923 | 0.001798 | 122.7641 | 122.7226 | -0.16972 | -0.26058 | 0.25189 | 122.4341 | -0.029917 | 122.7687 | 122.7159 | 0.28179 | 0.1099 | -0.37223 | 122.9297 | 122.6673 | 123.1798 | 122.7324 | -0.035528 | 122.8979 | 123.0378 | 122.5556 | 122.7314 | -0.49377
2457.4531 | 122.9462 | -122.7768 | 0.21973 | 1.4211e-13 | -0.011927 | -0.0032757 | 0.029151 | -0.014978 | 0.010098 | -0.0019839 | 0.006847 | 0.0074993 | -0.0083793 | 0.042613 | 0.0013867 | 0.037675 | 0.001407 | -0.008409 | 0.20321 | -0.040851 | 0.45789 | 0.15673 | 0.037677 | 0.004938 | -0.010564 | 0.16234 | 0.30216 | -0.17081 | -0.30151 | 122.9335 | -0.016513 | 122.8145 | 122.7684 | -0.16514 | -0.26058 | 0.23816 | 122.4753 | -0.057385 | 122.8145 | 122.7662 | 0.29095 | 0.082431 | -0.39054 | 122.98 | 122.7359 | 123.2347 | 122.7782 | -0.062996 | 122.9391 | 123.079 | 122.606 | 122.7817 | -0.52124
2459.2344 | 122.9782 | -122.7676 | 0.22888 | 1.4211e-13 | -0.011927 | -0.0032757 | 0.029364 | -0.014978 | 0.010098 | -0.0019839 | 0.006847 | 0.0074993 | -0.0083793 | 0.042613 | 0.0018139 | 0.042253 | 0.005985 | -0.003831 | 0.19864 | -0.063746 | 0.45789 | 0.15673 | 0.037677 | 0.009516 | -0.015143 | 0.16692 | 0.31132 | -0.16624 | -0.29693 | 122.9244 | -0.030246 | 122.8099 | 122.7638 | -0.16056 | -0.29263 | 0.22901 | 122.4707 | -0.061961 | 122.8053 | 122.7525 | 0.28179 | 0.082434 | -0.39512 | 122.9663 | 122.7039 | 123.2255 | 122.7736 | -0.072151 | 122.9346 | 123.079 | 122.6014 | 122.7772 | -0.52582
2460.9219 | 123.0377 | -122.7493 | 0.20599 | 1.4211e-13 | -0.012141 | -0.0032757 | 0.029364 | -0.015405 | 0.0098841 | -0.0019839 | 0.0070608 | 0.0072857 | -0.0081657 | 0.042185 | 0.0020275 | 0.033096 | 0.005985 | -0.012988 | 0.19406 | -0.031693 | 0.45789 | 0.16131 | 0.046835 | 0.000359 | -0.0243 | 0.16692 | 0.30216 | -0.17081 | -0.29693 | 122.9106 | -0.011936 | 122.7824 | 122.7363 | -0.1743 | -0.23769 | 0.2519 | 122.4524 | -0.039073 | 122.7962 | 122.725 | 0.27263 | 0.096164 | -0.37681 | 122.9434 | 122.7176 | 123.2072 | 122.7553 | -0.044684 | 122.9163 | 123.0515 | 122.5785 | 122.7497 | -0.50293

## Thermal Data
Fire Time | A Position - Middle | C Position - 3' | C Position - Middle | C Position - 7'
-0.5271 | 12.7138 | 12.186 | 12.2066 | 12.1332
0.4729 | 12.7071 | 12.1848 | 12.2114 | 12.1324
1.4729 | 12.6282 | 12.1923 | 12.2163 | 12.1333
2.4729 | 12.7377 | 12.1834 | 12.22 | 12.1301
3.4729 | 12.6267 | 12.1896 | 12.2169 | 12.131
4.4729 | 12.7336 | 12.1867 | 12.2252 | 12.1346
5.4729 | 12.7715 | 12.1965 | 12.2284 | 12.1404
6.4729 | 12.6475 | 12.1991 | 12.2343 | 12.1463
7.4729 | 12.7115 | 12.2074 | 12.2406 | 12.1453
8.4729 | 13.1029 | 12.2173 | 12.2596 | 12.1561
9.4729 | 13.4656 | 12.28 | 12.3095 | 12.1573
10.4729 | 17.2731 | 12.3515 | 12.4105 | 12.1762
11.4729 | 24.0907 | 12.6484 | 12.6386 | 12.4285
12.4729 | 30.8708 | 13.2223 | 13.0231 | 12.7121
13.4729 | 40.5472 | 13.8423 | 13.2978 | 13.1979
14.4729 | 47.1629 | 14.684 | 13.9267 | 14.0629
15.4729 | 52.4953 | 15.7879 | 14.8901 | 14.8611
16.4729 | 56.537 | 16.5889 | 16.1999 | 15.5548
17.4729 | 62.016 | 17.8187 | 17.0878 | 16.2512
18.4729 | 65.4405 | 18.6441 | 17.9926 | 17.6522
19.4729 | 70.906 | 19.7085 | 19.0439 | 18.518
20.4885 | 75.0478 | 20.8014 | 20.3043 | 20.0951
21.4885 | 80.1671 | 22.6137 | 21.2824 | 21.8405
22.4729 | 89.3533 | 24.4548 | 22.8356 | 24.1429
23.4729 | 91.9658 | 26.4534 | 24.5636 | 25.5281
24.4729 | 97.208 | 28.4783 | 26.3315 | 26.9187
25.4729 | 104.455 | 30.4069 | 28.4617 | 28.6681
26.4729 | 107.9484 | 33.1135 | 30.8499 | 31.2463
27.4729 | 113.5725 | 35.1715 | 32.7684 | 33.4937
28.4729 | 116.946 | 36.7454 | 34.1197 | 35.4249
29.4729 | 123.9411 | 38.2788 | 35.5168 | 36.6958
30.4729 | 127.8746 | 40.5705 | 37.1951 | 38.8075
31.4729 | 132.2836 | 42.2286 | 39.465 | 41.3434
32.4729 | 137.1631 | 44.1573 | 42.1356 | 43.9276
33.4729 | 144.7636 | 46.1515 | 43.7026 | 46.5755
34.4729 | 148.681 | 48.1545 | 45.0768 | 49.2528
35.4729 | 159.6487 | 50.1984 | 46.561 | 51.6688
36.4729 | 162.9732 | 52.06 | 48.105 | 53.9229
37.4729 | 166.5165 | 54.3979 | 50.0023 | 55.4543
38.4729 | 169.7673 | 56.5502 | 52.374 | 57.3226
39.4729 | 174.8321 | 58.1495 | 54.503 | 59.2008
40.4729 | 177.1349 | 60.5451 | 57.1463 | 61.0513
41.4729 | 181.1846 | 62.3082 | 59.163 | 63.1967
42.4729 | 186.1471 | 64.4036 | 60.7054 | 65.1255
43.4729 | 192.5958 | 66.9255 | 62.6088 | 66.9148
44.4729 | 193.0769 | 68.2489 | 64.1484 | 68.7999
45.4729 | 195.2774 | 69.8109 | 66.1619 | 71.4564
46.4729 | 199.5001 | 71.4041 | 68.278 | 72.6818
47.4729 | 201.2946 | 73.4749 | 70.1165 | 74.27
48.4729 | 203.4076 | 75.6441 | 72.5254 | 75.706
49.4729 | 206.2602 | 77.534 | 73.4768 | 78.2741
50.4729 | 206.3612 | 78.7966 | 74.828 | 80.5642
51.4729 | 208.3152 | 81.7578 | 77.5745 | 82.8645
52.4729 | 212.4378 | 85.1395 | 78.9183 | 84.3149
53.4729 | 216.1684 | 86.8718 | 80.6811 | 85.9261
54.4729 | 218.5647 | 88.6568 | 82.6312 | 88.4077
55.4729 | 223.5841 | 90.5069 | 84.8508 | 89.8415
56.4729 | 230.0168 | 92.0902 | 86.2952 | 91.4491
57.4729 | 234.505 | 93.9432 | 88.1331 | 92.9169
58.4729 | 237.7046 | 94.8221 | 89.6898 | 93.899
59.4729 | 243.1268 | 96.7252 | 91.5673 | 95.8459
60.4729 | 250.7594 | 97.5579 | 93.5056 | 96.8572
61.4729 | 249.8655 | 98.6543 | 94.6776 | 98.4248
62.4729 | 253.7957 | 100.3117 | 96.2738 | 99.3842
63.4729 | 254.041 | 101.4769 | 97.5126 | 100.2072
64.4729 | 254.8303 | 103.6834 | 98.2468 | 101.2191
65.4729 | 258.0611 | 104.536 | 99.5498 | 102.327
66.4729 | 260.4526 | 106.0161 | 100.64 | 103.6619
67.4729 | 265.1907 | 107.2706 | 101.8933 | 104.8909
68.4729 | 264.0602 | 108.448 | 102.9012 | 107.2642
69.4729 | 264.2976 | 110.3032 | 103.9355 | 109.9787
70.4729 | 261.7176 | 111.5025 | 105.6819 | 111.4873
71.4729 | 261.0273 | 112.6688 | 107.0692 | 112.5087
72.4729 | 263.0459 | 113.2681 | 108.1949 | 113.4935
73.4729 | 260.2992 | 114.3751 | 109.7803 | 114.4214
74.4729 | 259.4617 | 115.3577 | 110.9273 | 115.0956
75.4729 | 257.7189 | 116.3151 | 111.8771 | 115.8948
76.4729 | 256.2628 | 118.0397 | 113.1663 | 117.4147
77.4729 | 253.633 | 118.4535 | 114.2664 | 117.8419
78.4729 | 251.8573 | 119.1474 | 114.9677 | 118.8799
79.4729 | 251.7385 | 119.7256 | 116.2678 | 120.2384
80.4729 | 253.3152 | 119.8271 | 117.0946 | 121.064
81.4729 | 253.0427 | 120.0261 | 118.1831 | 121.4847
82.4729 | 252.8035 | 120.7647 | 118.8149 | 122.0617
83.4729 | 253.3573 | 121.9187 | 119.5018 | 122.4821
84.4729 | 251.0755 | 122.5667 | 120.2352 | 123.1345
85.4729 | 250.031 | 123.9083 | 121.1934 | 123.4072
86.4729 | 247.9447 | 124.9105 | 122.4978 | 123.9039
87.4729 | 245.8236 | 126.5321 | 122.9755 | 124.8079
88.4729 | 243.2541 | 127.4138 | 123.1824 | 126.3745
89.4729 | 240.4367 | 127.9791 | 123.4047 | 127.4417
90.4729 | 238.7647 | 127.9713 | 124.232 | 128.5443
91.4729 | 237.0478 | 128.4071 | 125.1235 | 129.1573
92.4729 | 238.1805 | 128.5002 | 125.9188 | 129.5941
93.4729 | 237.3367 | 128.9768 | 126.7433 | 129.5659
94.4729 | 234.9084 | 129.5212 | 127.2728 | 130.0045
95.4729 | 232.4845 | 130.1249 | 127.6417 | 129.857
96.4729 | 231.5642 | 130.6223 | 128.3245 | 130.0563
97.4729 | 231.3073 | 130.651 | 128.5887 | 130.8066
98.4729 | 230.8492 | 131.6289 | 128.9341 | 132.0906
99.4729 | 233.8029 | 131.9289 | 129.5688 | 132.4145
100.4729 | 236.166 | 132.5096 | 130.4505 | 132.8847
101.4729 | 237.1092 | 133.4469 | 130.4407 | 133.0576
102.4729 | 236.5993 | 133.4368 | 130.72 | 133.1416
103.4729 | 238.6551 | 134.0049 | 131.2058 | 133.3307
104.4729 | 240.666 | 134.3249 | 131.8161 | 133.7403
105.4729 | 241.6565 | 134.8961 | 132.2302 | 134.0716
106.4729 | 246.0266 | 134.8392 | 132.4895 | 134.3247
107.4729 | 248.1959 | 135.2407 | 132.9876 | 134.6312
108.4729 | 251.1222 | 135.6212 | 133.3249 | 135.2541
109.4729 | 253.0351 | 135.8416 | 133.0151 | 135.1011
110.4885 | 257.1862 | 135.4571 | 133.0996 | 134.93
111.4729 | 258.8456 | 135.7358 | 133.2761 | 135.0123
112.4729 | 260.3881 | 135.8664 | 133.2906 | 134.9398
113.4729 | 262.1443 | 136.1012 | 133.5523 | 135.5052
114.4729 | 265.9913 | 136.377 | 134.0951 | 135.7831
115.4729 | 271.5923 | 136.1975 | 134.4502 | 136.4287
116.4729 | 273.8465 | 136.7566 | 134.8798 | 137.0759
117.4729 | 278.1198 | 136.7948 | 134.7237 | 137.1509
118.4729 | 280.3669 | 137.0223 | 135.3062 | 136.9867
119.4729 | 280.4501 | 137.2968 | 135.6187 | 137.1912
120.4729 | 282.0152 | 137.1175 | 135.978 | 137.392
121.4729 | 282.0512 | 137.1153 | 136.2357 | 137.3666
122.4729 | 283.3971 | 136.7495 | 136.4587 | 137.3426
123.4729 | 286.2829 | 136.984 | 136.7896 | 137.5985
124.4729 | 287.5599 | 137.2517 | 137.7693 | 137.6163
125.4729 | 289.6891 | 137.495 | 138.2138 | 137.8446
126.4729 | 293.0718 | 137.568 | 138.455 | 138.0275
127.4729 | 295.4587 | 137.6997 | 139.133 | 138.1658
128.4729 | 296.8958 | 137.9925 | 139.4484 | 138.4546
129.4729 | 296.6707 | 138.7476 | 139.7114 | 139.0177
130.4729 | 295.5892 | 138.4704 | 140.1691 | 139.3865
131.4729 | 297.5868 | 138.446 | 139.8768 | 139.4609
132.4729 | 296.7139 | 138.4998 | 139.7889 | 139.7328
133.4729 | 297.4883 | 138.8442 | 139.8003 | 139.5581
134.4729 | 300.8002 | 139.5394 | 140.0649 | 140.0099
135.4729 | 303.2409 | 139.7607 | 140.2919 | 139.9979
136.4729 | 305.1399 | 139.7349 | 140.7192 | 140.5702
137.4729 | 306.3609 | 139.9292 | 141.153 | 141.2991
138.4729 | 307.5222 | 140.1927 | 141.1528 | 141.46
139.4729 | 312.2537 | 140.3676 | 141.99 | 141.5781
140.4729 | 317.5032 | 140.0406 | 142.5826 | 141.7673
141.4729 | 318.0546 | 140.4006 | 143.2011 | 142.4418
142.4729 | 320.171 | 140.6076 | 142.8394 | 142.3409
143.4729 | 319.971 | 140.448 | 143.2646 | 142.3365
144.4729 | 322.4692 | 140.869 | 143.6745 | 142.596
145.4729 | 321.727 | 141.7543 | 143.8558 | 143.0318
146.4729 | 322.1013 | 142.6709 | 143.7471 | 143.502
147.4729 | 323.625 | 144.107 | 144.3158 | 144.0601
148.4729 | 327.5429 | 144.2796 | 144.7342 | 144.2105
149.4729 | 331.6404 | 145.1272 | 145.1899 | 144.8105
150.4729 | 331.8748 | 145.1829 | 145.7147 | 145.2202
151.4729 | 335.8879 | 145.3336 | 145.7101 | 145.3324
152.4729 | 337.2706 | 146.5211 | 146.5915 | 145.7468
153.4729 | 359.1949 | 147.3705 | 147.2256 | 145.9627
154.4729 | 359.5468 | 148.093 | 148.1793 | 146.9321
155.4729 | 358.2652 | 148.589 | 149.1319 | 147.6918
156.4729 | 365.7749 | 148.6051 | 148.9633 | 147.6766
157.4729 | 367.1494 | 149.5195 | 149.2986 | 148.4418
158.4729 | 365.2439 | 149.1983 | 149.6109 | 149.5706
159.4729 | 362.564 | 149.1419 | 149.6734 | 150.3295
160.4729 | 363.6173 | 150.0398 | 150.1912 | 150.3944
161.4729 | 362.7387 | 150.4807 | 150.4805 | 151.0915
162.4729 | 363.8547 | 151.1787 | 151.2265 | 151.7169
163.4729 | 380.7564 | 152.0348 | 151.7798 | 151.7504
164.4729 | 378.0008 | 152.6703 | 152.5507 | 152.732
165.4729 | 373.567 | 153.0834 | 153.1166 | 153.4061
166.4729 | 373.3802 | 153.2556 | 153.5805 | 153.5813
167.4729 | 386.4905 | 154.1306 | 153.6911 | 154.0481
168.4729 | 385.4613 | 154.6485 | 153.7416 | 154.2458
169.4729 | 394.1164 | 155.6082 | 154.4674 | 155.2399
170.4885 | 45.212 | 125.8561 | 161.4877 | 28.5835
171.4729 | 26.0543 | 125.8186 | 161.1238 | 26.0471
172.4729 | 383.7022 | 152.632 | 157.1917 | 28.6768
173.4729 | 382.9477 | 158.0488 | 156.2223 | 158.1229
174.4729 | 385.1805 | 158.4749 | 157.7846 | 158.7389
175.4729 | 381.8388 | 158.8048 | 158.2667 | 159.729
176.4729 | 384.7623 | 159.6976 | 159.2021 | 161.065
177.4729 | 391.7747 | 160.1255 | 160.0821 | 161.0148
178.4729 | 393.0261 | 161.4153 | 161.3066 | 162.4869
179.4729 | 404.5358 | 161.9389 | 161.5344 | 163.8723
180.4729 | 405.4264 | 162.5769 | 162.281 | 164.3238
181.4729 | 407.7945 | 163.4306 | 163.2748 | 166.0692
182.4729 | 411.877 | 163.9485 | 163.9149 | 167.0942
183.4729 | 411.5939 | 164.8543 | 164.3178 | 168.0656
184.4729 | 413.0875 | 165.9657 | 164.9592 | 167.4051
185.4729 | 414.4348 | 166.7003 | 165.0116 | 168.2838
186.4729 | 412.0424 | 166.5234 | 165.4002 | 168.2131
187.4729 | 413.8122 | 167.03 | 165.4863 | 168.6793
188.4729 | 415.5818 | 167.4841 | 165.7359 | 168.7959
189.4729 | 414.3434 | 168.0616 | 165.7451 | 168.7102
190.4729 | 411.7053 | 169.0097 | 165.3084 | 169.1805
191.4729 | 409.468 | 169.5864 | 165.2792 | 169.2414
192.4729 | 412.0143 | 169.6359 | 165.6053 | 168.7057
193.4729 | 412.2185 | 170.1907 | 166.1411 | 168.9268
194.4729 | 408.8564 | 170.7792 | 166.0513 | 168.9662
195.4729 | 408.9647 | 170.941 | 165.9593 | 168.7483
196.4729 | 408.3527 | 172.6152 | 166.2459 | 169.3988
197.4729 | 409.0545 | 172.9474 | 166.3251 | 169.5165
198.4729 | 415.0043 | 173.7291 | 167.1092 | 170.3947
199.4729 | 414.9512 | 174.2195 | 167.5195 | 171.3389
200.4729 | 416.2528 | 174.4531 | 167.4895 | 171.1594
201.4729 | 415.2731 | 175.349 | 168.7584 | 172.2824
202.4729 | 412.6833 | 175.3138 | 169.401 | 172.8355
203.4729 | 417.5798 | 175.5575 | 169.3562 | 173.1331
204.4729 | 417.0182 | 174.9195 | 169.1658 | 172.8081
205.4729 | 423.8579 | 175.2818 | 170.3605 | 173.4263
206.4729 | 421.7777 | 175.3329 | 170.7507 | 172.8333
207.4729 | 421.4072 | 174.9682 | 171.1245 | 172.8751
208.4729 | 422.0933 | 175.4748 | 171.1203 | 172.8414
209.4729 | 425.2179 | 175.4504 | 171.4419 | 173.4868
210.4729 | 428.5098 | 175.3134 | 171.4142 | 173.5377
211.4729 | 426.4834 | 175.884 | 171.8603 | 174.6634
212.4729 | 435.3906 | 176.4079 | 171.8723 | 175.0222
213.4729 | 432.3988 | 176.0902 | 172.5772 | 175.2315
214.4729 | 431.9013 | 176.0537 | 172.9225 | 175.6959
215.4729 | 430.3662 | 175.7632 | 172.9229 | 176.7411
216.4729 | 437.9336 | 175.6212 | 173.2958 | 176.5349
217.4729 | 440.3401 | 175.5374 | 173.5605 | 177.1659
218.4729 | 444.439 | 176.23 | 174.0294 | 177.4534
219.4729 | 447.1629 | 176.4148 | 174.8011 | 177.6375
220.4729 | 455.1877 | 176.3167 | 175.2736 | 177.4225
221.4729 | 458.6005 | 176.4955 | 175.2327 | 177.3837
222.4729 | 455.0676 | 176.59 | 175.36 | 178.025
223.4729 | 457.7737 | 177.0165 | 175.2217 | 177.9282
224.4729 | 454.0506 | 177.6088 | 175.4178 | 178.0739
225.4729 | 464.0163 | 177.992 | 175.3596 | 178.2283
226.4729 | 462.8534 | 177.9885 | 175.0783 | 177.9742
227.4729 | 463.2473 | 178.2106 | 175.0555 | 178.9129
228.4729 | 474.3359 | 178.8845 | 176.0031 | 179.0845
229.4729 | 475.4686 | 179.4049 | 176.1169 | 179.6741
230.4729 | 485.3487 | 180.24 | 176.533 | 180.2177
231.4729 | 499.4431 | 179.5279 | 176.6174 | 180.6546
232.4729 | 508.8787 | 179.9616 | 177.3226 | 180.1881
233.4729 | 512.7938 | 180.7316 | 177.4977 | 180.4658
234.4729 | 529.458 | 180.7247 | 177.4819 | 179.7831
235.4729 | 534.394 | 182.0649 | 177.9213 | 179.8899
236.4729 | 552.3829 | 182.6605 | 178.3558 | 180.2564
237.4729 | 562.9403 | 184.0058 | 179.536 | 180.9176
238.4729 | 567.8045 | 183.5975 | 179.5628 | 180.9805
239.4729 | 589.4885 | 184.7171 | 180.349 | 181.5583
240.4729 | 585.2442 | 184.3713 | 180.6821 | 181.6903
241.4729 | 600.3373 | 184.2477 | 180.5516 | 181.7499
242.4729 | 612.4282 | 184.2681 | 180.179 | 182.5068
243.4729 | 628.996 | 184.6936 | 180.764 | 182.8806
244.4729 | 644.5468 | 185.5242 | 180.6767 | 183.1557
245.4729 | 655.7866 | 185.685 | 180.5029 | 182.6677
246.4729 | 643.6532 | 187.1962 | 181.2857 | 183.2057
247.4729 | 638.8461 | 186.93 | 182.053 | 182.9816
248.4729 | 642.1766 | 186.9643 | 182.1164 | 182.9357
249.4729 | 654.2033 | 186.9144 | 182.3879 | 183.4976
250.4729 | 670.5386 | 186.9684 | 183.3345 | 184.8809
251.4729 | 690.3177 | 187.1748 | 183.5807 | 184.9015
252.4729 | 694.2604 | 187.6051 | 183.5449 | 185.2409
253.4729 | 690.8749 | 188.2872 | 183.2122 | 185.0061
254.4729 | 695.3035 | 188.2366 | 183.1658 | 184.9444
255.4729 | 691.1042 | 188.0598 | 182.7917 | 184.5494
256.4729 | 694.8372 | 188.4127 | 182.8738 | 184.9067
257.4729 | 709.2557 | 188.9593 | 183.3169 | 186.3099
258.4729 | 702.6301 | 189.1457 | 183.5006 | 186.264
259.4729 | 716.3119 | 189.2038 | 184.4423 | 186.533
260.4729 | 712.2514 | 189.8616 | 185.6761 | 187.4586
261.4729 | 705.2572 | 190.5235 | 186.5976 | 189.095
262.4729 | 695.2059 | 190.1395 | 186.5457 | 189.2591
263.4729 | 695.0189 | 190.377 | 187.7472 | 189.7545
264.4729 | 697.9185 | 190.3976 | 189.0372 | 191.0328
265.4729 | 717.1279 | 190.6792 | 189.3148 | 191.6791
266.4729 | 723.7521 | 191.3705 | 190.3671 | 191.7477
267.4729 | 721.6389 | 191.4736 | 190.5742 | 193.0331
268.4729 | 726.1059 | 191.512 | 190.6472 | 193.4723
269.4729 | 712.1645 | 192.1094 | 190.8743 | 193.2513
270.4729 | 704.4965 | 192.847 | 190.813 | 194.4507
271.4729 | 692.8387 | 192.5262 | 190.3824 | 194.2832
272.4729 | 681.3262 | 193.4483 | 190.6693 | 194.8157
273.4729 | 673.7753 | 194.091 | 190.988 | 195.5901
274.4729 | 678.8144 | 193.717 | 191.3807 | 194.9578
275.4729 | 687.7671 | 193.4085 | 191.6669 | 195.0001
276.4729 | 697.5693 | 194.1698 | 191.9439 | 195.1954
277.4729 | 707.8358 | 194.0522 | 191.8724 | 194.7341
278.4729 | 723.5791 | 194.9199 | 192.8167 | 195.1851
279.4729 | 724.9902 | 194.9589 | 192.6288 | 195.5907
280.4729 | 726.0857 | 195.5381 | 193.2197 | 195.8217
281.4729 | 722.1619 | 195.2607 | 192.9598 | 195.3326
282.4729 | 731.9677 | 195.6441 | 193.0956 | 195.5185
283.4729 | 727.6152 | 195.8639 | 193.55 | 195.5904
284.4729 | 719.5387 | 195.1768 | 193.5972 | 195.5538
285.4729 | 721.5261 | 194.8372 | 193.1896 | 195.4047
286.4729 | 713.8807 | 194.6063 | 194.8172 | 196.7174
287.4729 | 722.9764 | 194.9139 | 194.9869 | 196.2979
288.4729 | 707.5902 | 195.3305 | 195.2605 | 195.9257
289.4729 | 713.8908 | 195.3015 | 195.9944 | 196.1266
290.4885 | 718.2017 | 195.3722 | 195.8294 | 196.2717
291.4729 | 730.5667 | 196.5556 | 196.2087 | 196.5871
292.4729 | 748.1562 | 196.4967 | 196.5842 | 196.7574
293.4729 | 751.9174 | 196.591 | 196.7688 | 197.9854
294.4729 | 742.1589 | 196.7857 | 196.8672 | 197.789
295.4729 | 735.9862 | 196.6896 | 197.2483 | 197.7811
296.4729 | 738.2652 | 197.8222 | 197.5303 | 197.7676
297.4729 | 735.3599 | 198.2442 | 197.0696 | 197.4997
298.4729 | 744.9786 | 198.0676 | 196.8008 | 197.3919
299.4729 | 745.6745 | 198.6144 | 196.8699 | 197.76
300.4729 | 735.3479 | 198.277 | 196.9307 | 197.5019
301.4729 | 739.2534 | 198.0645 | 196.8415 | 197.9417
302.4729 | 748.3084 | 197.8969 | 197.3402 | 198.6282
303.4729 | 757.4529 | 198.6139 | 196.8644 | 198.6681
304.4729 | 751.4601 | 199.656 | 198.3689 | 198.9452
305.4729 | 763.2174 | 199.953 | 198.296 | 198.8999
306.4729 | 771.0962 | 200.7136 | 199.3195 | 199.2643
307.4729 | 783.4243 | 200.6275 | 199.0348 | 199.2423
308.4729 | 781.8862 | 201.1188 | 199.098 | 198.8694
309.4729 | 786.7069 | 201.2634 | 198.6736 | 198.4415
310.4729 | 791.4818 | 200.9251 | 198.517 | 198.0943
311.4729 | 797.1506 | 200.7759 | 198.2018 | 198.3324
312.4729 | 799.8887 | 201.0324 | 197.9859 | 197.9534
313.4729 | 779.6677 | 200.7794 | 198.1787 | 198.1586
314.4729 | 780.9448 | 200.4511 | 198.4129 | 197.9614
315.4729 | 773.5653 | 200.2509 | 198.0822 | 198.4208
316.4729 | 764.9578 | 200.2027 | 198.0172 | 198.6746
317.4729 | 777.3914 | 200.105 | 198.2729 | 198.5414
318.4729 | 784.2129 | 200.2548 | 197.8252 | 199.2001
319.4729 | 793.1097 | 200.2215 | 197.8702 | 199.1044
320.4729 | 800.5696 | 200.965 | 198.8522 | 199.1069
321.4729 | 805.8373 | 200.8962 | 198.3351 | 199.4206
322.4729 | 813.9341 | 200.4648 | 198.1571 | 199.7301
323.4729 | 796.6409 | 200.4686 | 198.1807 | 199.3903
324.4729 | 789.628 | 201.819 | 198.422 | 199.7653
325.4729 | 780.3313 | 203.0589 | 198.0201 | 199.7896
326.4729 | 775.7917 | 202.8964 | 198.8222 | 199.3648
327.4729 | 774.6488 | 202.6293 | 200.0821 | 199.9366
328.4729 | 772.4667 | 203.1968 | 199.8512 | 200.1692
329.4729 | 790.5081 | 202.9996 | 199.5445 | 200.373
330.4729 | 786.8114 | 203.3006 | 200.2089 | 200.0587
331.4729 | 785.9291 | 203.4196 | 201.3132 | 200.5195
332.4729 | 795.716 | 203.9123 | 202.0081 | 200.7654
333.4729 | 795.2127 | 204.8497 | 202.3638 | 200.9831
334.4729 | 787.2515 | 205.7291 | 201.9497 | 200.7698
335.4729 | 788.0835 | 205.9271 | 201.6036 | 200.4018
336.4729 | 787.8497 | 205.3896 | 201.1225 | 201.4528
337.4729 | 787.1986 | 205.204 | 200.82 | 201.8523
338.4729 | 779.542 | 204.9566 | 200.5051 | 201.1627
339.4729 | 781.8778 | 205.5215 | 200.6843 | 201.323
340.4729 | 788.6663 | 205.6453 | 201.5485 | 202.3425
341.4729 | 791.8152 | 205.9247 | 201.599 | 202.5395
342.4729 | 776.0762 | 205.5876 | 201.5981 | 202.9895
343.4729 | 769.1268 | 205.8588 | 201.5641 | 202.8285
344.4729 | 769.8746 | 206.87 | 202.0948 | 203.9261
345.4729 | 771.677 | 206.023 | 202.0492 | 203.6011
346.4729 | 764.0694 | 205.3519 | 202.2448 | 203.4963
347.4729 | 763.7831 | 206.5927 | 202.899 | 203.0974
348.4729 | 761.6089 | 206.3363 | 203.0748 | 202.9594
349.4729 | 756.784 | 206.4935 | 203.7956 | 202.9622
350.4885 | 757.323 | 206.4472 | 204.0192 | 203.0033
351.4729 | 751.1622 | 206.3268 | 204.5946 | 203.0771
352.4729 | 745.1621 | 206.8849 | 204.5835 | 203.392
353.4729 | 736.6855 | 206.8338 | 204.195 | 203.8013
354.4729 | 734.8056 | 206.7683 | 205.0079 | 204.7764
355.4729 | 727.705 | 206.7333 | 204.2663 | 204.74
356.4729 | 723.888 | 207.3665 | 203.8036 | 205.8285
357.4729 | 725.8421 | 207.4441 | 204.3021 | 205.8564
358.4729 | 735.508 | 207.4609 | 203.8595 | 206.0596
359.4729 | 731.8894 | 207.3135 | 203.3655 | 205.9527
360.4729 | 732.034 | 206.8022 | 202.5964 | 205.6356
361.4729 | 739.63 | 206.755 | 202.3437 | 206.2538
362.4729 | 747.893 | 206.8766 | 203.2099 | 205.8703
363.4729 | 751.9451 | 206.959 | 203.0283 | 206.2203
364.4729 | 756.3156 | 206.7937 | 204.3476 | 206.3677
365.4729 | 767.9851 | 207.5071 | 204.0213 | 206.189
366.4729 | 764.5356 | 208.0758 | 204.3255 | 205.6607
367.4729 | 761.4332 | 208.5249 | 204.2409 | 205.5677
368.4729 | 762.8387 | 208.413 | 204.4386 | 206.5368
369.4729 | 767.0498 | 208.8716 | 204.5196 | 206.788
370.4729 | 763.3692 | 209.0888 | 204.8314 | 208.2171
371.4729 | 770.4009 | 209.3088 | 204.7744 | 208.2746
372.4729 | 774.1546 | 209.3496 | 204.7785 | 208.2366
373.4729 | 783.5827 | 209.6639 | 205.7898 | 208.746
374.4729 | 789.6691 | 209.6035 | 205.8885 | 208.1234
375.4729 | 786.1238 | 209.4973 | 205.5395 | 207.454
376.4729 | 770.7224 | 209.2192 | 205.4845 | 207.7304
377.4729 | 784.1891 | 208.578 | 205.6212 | 207.5673
378.4729 | 782.0701 | 208.4444 | 205.4001 | 207.6859
379.4729 | 779.7986 | 208.3312 | 205.7924 | 207.8324
380.4729 | 782.486 | 208.6731 | 205.8635 | 208.5903
381.4729 | 787.6551 | 208.7144 | 206.3817 | 208.5971
382.4729 | 796.0782 | 209.3017 | 206.563 | 208.998
383.4729 | 791.1888 | 209.2144 | 206.9134 | 209.5105
384.4729 | 790.1667 | 209.1023 | 207.4228 | 210.4209
385.4729 | 778.9363 | 208.8897 | 207.3242 | 210.5168
386.4729 | 775.8445 | 208.6461 | 207.7325 | 210.581
387.4729 | 776.0434 | 208.8911 | 207.6619 | 210.2068
388.4729 | 773.5092 | 209.2432 | 207.4404 | 210.4734
389.4729 | 774.3968 | 209.5079 | 207.4681 | 211.241
390.4729 | 773.7146 | 209.7758 | 207.8547 | 211.0882
391.4729 | 773.2766 | 209.6769 | 208.4288 | 210.9637
392.4729 | 771.7603 | 209.5534 | 208.4862 | 210.6131
393.4729 | 773.8039 | 209.5711 | 208.1704 | 210.507
394.4729 | 765.8365 | 209.7735 | 208.5549 | 210.9372
395.4729 | 766.4433 | 210.2951 | 208.8837 | 210.7289
396.4729 | 763.731 | 210.2038 | 208.4989 | 210.329
397.4729 | 761.3347 | 210.3321 | 208.4853 | 211.2502
398.4729 | 765.5873 | 210.6 | 209.251 | 211.1766
399.4729 | 767.6625 | 210.9845 | 209.1043 | 211.7307
400.4729 | 769.1446 | 211.3139 | 208.9912 | 211.2471
401.4729 | 767.6715 | 211.8865 | 208.7574 | 210.8239
402.4729 | 757.8339 | 212.6303 | 208.8199 | 210.8261
403.4729 | 754.0656 | 213.7753 | 209.0398 | 210.6527
404.4729 | 754.2335 | 214.3994 | 210.1618 | 210.7594
405.4729 | 758.5412 | 214.2646 | 210.055 | 210.9034
406.4729 | 759.5157 | 214.388 | 210.5657 | 211.5873
407.4729 | 761.3064 | 214.8369 | 210.8859 | 211.5806
408.4729 | 756.8542 | 215.6009 | 211.3112 | 212.1145
409.4729 | 758.2498 | 216.0874 | 211.163 | 212.2831
410.4885 | 765.8242 | 216.6393 | 210.9579 | 212.0978
411.4729 | 763.986 | 216.8365 | 210.9492 | 212.7096
412.4729 | 762.0532 | 217.2032 | 210.9732 | 212.7238
413.4729 | 760.6928 | 217.8034 | 210.6754 | 212.8713
414.4729 | 761.1129 | 217.8366 | 210.3706 | 213.2942
415.4729 | 764.3117 | 218.1369 | 210.3547 | 213.5786
416.4729 | 754.1748 | 218.8477 | 210.1508 | 213.3311
417.4729 | 743.4796 | 218.2177 | 209.7913 | 212.8131
418.4729 | 740.2398 | 217.7352 | 209.6812 | 212.5498
419.4729 | 739.5555 | 217.6621 | 209.6865 | 212.2074
420.4729 | 739.6413 | 217.7893 | 209.6845 | 213.3179
421.4729 | 736.8662 | 217.4274 | 209.632 | 213.0425
422.4729 | 731.474 | 217.6107 | 210.1828 | 213.4943
423.4729 | 732.9952 | 217.8414 | 209.7415 | 212.7041
424.4729 | 731.177 | 218.4508 | 209.745 | 213.3486
425.4729 | 733.5443 | 218.0161 | 209.3996 | 213.1027
426.4729 | 738.3708 | 217.4584 | 208.9317 | 213.0704
427.4729 | 737.537 | 217.1395 | 209.7496 | 213.6066
428.4729 | 736.5765 | 217.4212 | 209.6153 | 213.8883
429.4729 | 740.0869 | 217.6008 | 209.4611 | 213.4335
430.4729 | 744.1139 | 217.6201 | 209.2546 | 213.5523
431.4729 | 746.4614 | 217.4479 | 208.9678 | 213.8288
432.4729 | 747.9759 | 217.5389 | 208.8617 | 214.0503
433.4729 | 744.3701 | 217.996 | 209.7653 | 213.778
434.4729 | 742.5973 | 217.929 | 210.1778 | 214.6812
435.4729 | 740.8813 | 218.234 | 210.1524 | 213.9929
436.4729 | 742.9511 | 218.2603 | 210.3815 | 214.1093
437.4729 | 751.3893 | 218.8824 | 210.386 | 214.7286
438.4729 | 745.9194 | 219.4095 | 210.3138 | 214.4645
439.4729 | 741.9009 | 218.9837 | 210.4224 | 214.4896
440.4729 | 739.5587 | 219.2258 | 210.8683 | 214.7555
441.4729 | 735.0523 | 219.6164 | 211.5432 | 215.5358
442.4729 | 735.1962 | 220.5077 | 211.948 | 216.5339
443.4729 | 735.2162 | 221.6985 | 213.588 | 216.9629
444.4729 | 730.2289 | 222.0114 | 214.6166 | 218.0768
445.4729 | 730.1962 | 221.7 | 214.9028 | 217.8542
446.4729 | 730.6236 | 221.2342 | 215.1839 | 218.3705
447.4729 | 727.3448 | 221.8317 | 215.3938 | 218.618
448.4729 | 724.5585 | 221.7841 | 216.4607 | 218.8654
449.4729 | 723.5243 | 222.3224 | 216.025 | 218.6185
450.4729 | 720.8548 | 222.9726 | 216.171 | 218.6229
451.4729 | 717.2589 | 223.2751 | 216.1847 | 218.418
452.4729 | 716.9259 | 223.44 | 216.101 | 217.8951
453.4729 | 716.7206 | 224.4818 | 216.7114 | 218.302
454.4729 | 712.7041 | 224.1525 | 216.4676 | 217.8861
455.4729 | 714.2737 | 223.6196 | 217.0899 | 218.0695
456.4729 | 716.9787 | 223.984 | 217.697 | 218.319
457.4729 | 718.6812 | 223.7479 | 217.7889 | 218.231
458.4729 | 715.834 | 223.7533 | 217.9359 | 218.3886
459.4729 | 714.07 | 223.9356 | 218.2336 | 218.3959
460.4729 | 717.3178 | 224.0286 | 218.7123 | 219.0725
461.4729 | 715.6322 | 223.9423 | 218.2094 | 219.2172
462.4729 | 714.5778 | 224.3263 | 218.1548 | 219.0979
463.4729 | 712.7742 | 224.914 | 218.0049 | 219.557
464.4729 | 710.3885 | 225.0529 | 218.509 | 219.6002
465.4729 | 709.0319 | 225.8156 | 218.1049 | 219.9455
466.4729 | 709.9679 | 225.7183 | 218.256 | 220.0494
467.4729 | 712.7084 | 226.7665 | 219.1544 | 219.8305
468.4729 | 713.2693 | 226.449 | 218.8276 | 219.4317
469.4729 | 715.9182 | 226.0828 | 218.7526 | 219.0639
470.4729 | 715.2347 | 225.864 | 218.8616 | 218.8861
471.4729 | 712.5863 | 225.7528 | 218.6433 | 218.8663
472.4729 | 710.6268 | 226.1833 | 218.745 | 219.5027
473.4729 | 705.5911 | 226.0295 | 218.8544 | 220.2214
474.4729 | 703.4776 | 227.1521 | 219.006 | 220.399
475.4729 | 702.6011 | 227.2889 | 218.9621 | 220.4994
476.4729 | 700.7864 | 226.7688 | 218.9755 | 221.0171
477.4729 | 698.8952 | 226.7839 | 219.2869 | 220.952
478.4729 | 702.8421 | 227.3932 | 219.0936 | 220.5098
479.4729 | 703.2359 | 227.8906 | 220.1301 | 220.4088
480.4729 | 703.9087 | 228.3425 | 219.8342 | 220.5571
481.4729 | 701.9037 | 228.7658 | 220.0854 | 221.9694
482.4729 | 698.5601 | 228.9336 | 220.2955 | 222.3027
483.4729 | 700.5692 | 229.7821 | 220.1981 | 222.3182
484.4729 | 704.273 | 230.0493 | 220.4065 | 221.9373
485.4729 | 701.6732 | 230.03 | 220.4679 | 222.1966
486.4729 | 701.3684 | 229.6982 | 221.1817 | 222.9496
487.4729 | 700.949 | 229.3816 | 221.4826 | 222.9451
488.4729 | 699.7134 | 229.1806 | 222.2118 | 222.7299
489.4729 | 698.8 | 229.9424 | 222.5056 | 222.6457
490.4729 | 698.8475 | 229.6825 | 222.887 | 223.2664
491.4729 | 697.4706 | 229.1277 | 223.2675 | 223.206
492.4729 | 698.998 | 229.0202 | 223.6656 | 223.0706
493.4729 | 700.8002 | 229.2436 | 223.8536 | 223.1077
494.4729 | 700.258 | 229.1692 | 223.5973 | 222.8101
495.4729 | 698.2905 | 229.2791 | 224.1574 | 222.6164
496.4729 | 697.2589 | 229.6749 | 224.2101 | 222.8877
497.4729 | 695.1813 | 229.5749 | 224.2859 | 223.6852
498.4729 | 694.8558 | 229.6424 | 224.1611 | 223.6171
499.4729 | 697.8376 | 230.2309 | 224.0155 | 224.1756
500.4729 | 696.1898 | 229.8968 | 223.7164 | 224.1387
501.4729 | 696.2453 | 230.4725 | 223.5042 | 224.2318
502.4729 | 696.1322 | 230.8013 | 223.6685 | 223.9291
503.4729 | 703.4078 | 230.8258 | 224.059 | 224.0522
504.4729 | 701.0641 | 231.0675 | 223.8813 | 224.6773
505.4729 | 697.3589 | 231.3296 | 224.0585 | 225.0458
506.4729 | 697.316 | 231.1377 | 224.4996 | 224.7325
507.4885 | 700.8928 | 230.9861 | 225.2045 | 225.0373
508.4729 | 699.5241 | 231.5213 | 226.073 | 225.6976
509.4729 | 699.767 | 231.4558 | 226.7883 | 225.7915
510.4729 | 698.1631 | 231.4847 | 227.503 | 225.8996
511.4729 | 697.6309 | 231.9332 | 227.6784 | 225.6209
512.4729 | 696.6986 | 232.17 | 227.1702 | 225.5493
513.4729 | 695.6782 | 232.3665 | 227.1476 | 225.8592
514.4729 | 694.7893 | 232.8742 | 227.3359 | 225.6261
515.4729 | 693.4555 | 233.6054 | 227.8693 | 226.5495
516.4729 | 693.529 | 233.9444 | 227.5984 | 226.6192
517.4729 | 692.248 | 234.3786 | 228.8484 | 227.7479
518.4729 | 691.2336 | 234.1543 | 229.1735 | 228.1494
519.4729 | 689.3031 | 234.7575 | 229.5133 | 228.613
520.4729 | 687.4717 | 234.9945 | 230.1142 | 229.3184
521.4729 | 689.3702 | 235.929 | 230.8472 | 229.6208
522.4729 | 690.1968 | 236.0473 | 231.3331 | 229.8375
523.4729 | 688.5178 | 235.9684 | 231.5873 | 230.3427
524.4729 | 687.6181 | 235.9058 | 232.1126 | 230.8653
525.4729 | 685.7897 | 236.287 | 231.9787 | 231.5617
526.4729 | 687.8432 | 236.8972 | 231.9199 | 231.9492
527.4729 | 687.0064 | 237.3572 | 231.8542 | 232.8072
528.4729 | 687.4076 | 237.8088 | 232.2924 | 234.0559
529.4729 | 687.5962 | 237.9152 | 232.0208 | 234.0048
530.4885 | 686.7784 | 237.8148 | 231.6451 | 233.985
531.4729 | 684.8345 | 238.4108 | 231.9078 | 234.0059
532.4729 | 683.0257 | 238.8042 | 231.8113 | 234.1859
533.4729 | 681.8314 | 238.5134 | 231.4888 | 234.1967
534.4729 | 679.4987 | 238.404 | 231.351 | 234.0314
535.4729 | 682.1064 | 238.3523 | 231.5424 | 233.8462
536.4729 | 681.9768 | 238.5902 | 232.0195 | 234.2873
537.4729 | 682.1 | 238.3843 | 231.4897 | 233.8908
538.4729 | 680.8995 | 238.0803 | 231.5467 | 233.3139
539.4729 | 679.5852 | 237.8219 | 231.8266 | 233.3895
540.4729 | 678.7486 | 237.7255 | 231.6017 | 233.7379
541.4729 | 678.5804 | 237.4389 | 231.5638 | 233.8974
542.4729 | 676.9647 | 237.6714 | 231.1996 | 234.327
543.4729 | 681.1032 | 237.7974 | 231.4081 | 234.0485
544.4729 | 679.7311 | 237.5752 | 231.8987 | 234.9186
545.4729 | 678.8191 | 237.5516 | 232.7147 | 235.9115
546.4729 | 679.0824 | 237.3893 | 232.5651 | 235.968
547.4729 | 676.9923 | 237.3859 | 232.2173 | 235.8304
548.4729 | 678.6637 | 237.5917 | 232.1631 | 235.1916
549.4729 | 679.886 | 237.3475 | 231.9863 | 234.2675
550.4729 | 678.1667 | 237.0404 | 231.7011 | 233.8999
551.4729 | 677.822 | 236.9855 | 231.1992 | 234.0067
552.4729 | 675.8013 | 237.1383 | 230.6965 | 233.6752
553.4729 | 676.3162 | 237.4482 | 230.9643 | 234.1108
554.4729 | 686.1473 | 237.703 | 231.4591 | 234.5964
555.4729 | 686.2702 | 238.4939 | 231.8092 | 234.5936
556.4729 | 687.7937 | 238.6012 | 232.0109 | 234.5173
557.4729 | 686.7043 | 238.8784 | 232.1002 | 234.3119
558.4729 | 691.4109 | 238.8473 | 231.7833 | 234.1795
559.4729 | 689.2591 | 238.6543 | 232.2137 | 234.6416
560.4729 | 686.619 | 239.0263 | 232.8719 | 234.2478
561.4729 | 684.3993 | 238.996 | 233.0414 | 235.0771
562.4729 | 683.0283 | 239.246 | 232.6504 | 235.0912
563.4729 | 681.1403 | 239.0691 | 232.7556 | 234.9468
564.4729 | 680.862 | 239.1993 | 232.5511 | 234.4638
565.4729 | 680.9177 | 239.1447 | 233.0253 | 234.3976
566.4729 | 679.3209 | 238.8059 | 232.7335 | 234.2539
567.4729 | 684.9263 | 238.5259 | 232.6469 | 234.1995
568.4729 | 684.3353 | 238.3575 | 232.2695 | 234.2551
569.4729 | 685.4666 | 238.4069 | 232.7133 | 234.2149
570.4729 | 684.4932 | 238.4662 | 232.3761 | 234.6409
571.4729 | 681.0784 | 238.6235 | 232.255 | 234.4226
572.4729 | 680.4395 | 238.3572 | 232.2553 | 234.5028
573.4729 | 678.0875 | 239.2926 | 232.8301 | 234.9328
574.4729 | 678.4295 | 239.3122 | 232.7841 | 235.115
575.4729 | 679.355 | 239.2957 | 232.8748 | 235.3661
576.4729 | 676.0274 | 239.2919 | 233.1166 | 235.3811
577.4729 | 674.3892 | 239.5146 | 233.1539 | 235.6183
578.4729 | 676.1601 | 239.1573 | 233.5507 | 235.8445
579.4729 | 675.2109 | 239.0459 | 233.095 | 235.5084
580.4729 | 679.4044 | 238.8721 | 232.7963 | 235.8648
581.4729 | 680.2998 | 238.9301 | 232.7975 | 235.7809
582.4729 | 681.816 | 238.7514 | 232.1822 | 235.2331
583.4729 | 679.954 | 238.3946 | 231.6561 | 234.6877
584.4729 | 679.4007 | 238.2107 | 231.0566 | 234.8919
585.4729 | 678.0512 | 238.4492 | 231.5427 | 235.3239
586.4729 | 678.134 | 238.3621 | 231.3934 | 235.0018
587.4729 | 677.7497 | 238.5003 | 231.5003 | 235.3936
588.4729 | 678.319 | 238.5121 | 231.8318 | 235.5897
589.4729 | 677.3824 | 238.8161 | 231.5054 | 235.5554
590.4729 | 678.1226 | 239.2342 | 231.4231 | 235.2937
591.4729 | 679.4721 | 239.247 | 232.1838 | 235.3232
592.4729 | 679.79 | 239.5001 | 232.7265 | 235.5976
593.4729 | 685.2566 | 239.9362 | 232.8181 | 235.7163
594.4729 | 682.6255 | 240.0983 | 232.7566 | 236.3857
595.4729 | 678.4929 | 240.4217 | 232.8829 | 236.5774
596.4729 | 677.6266 | 240.346 | 233.2752 | 236.2522
597.4729 | 677.293 | 240.1438 | 233.1887 | 236.8003
598.4729 | 679.0956 | 240.4177 | 233.1411 | 237.1851
599.4729 | 682.245 | 239.8282 | 232.6883 | 236.7302
600.4729 | 680.4874 | 239.7243 | 232.4876 | 236.8925
601.4729 | 680.502 | 239.7042 | 232.6003 | 237.1508
602.4729 | 680.9568 | 239.8548 | 232.5605 | 236.9858
603.4729 | 685.0912 | 240.0052 | 232.7091 | 236.8356
604.4729 | 687.658 | 240.4381 | 232.7501 | 237.1737
605.4729 | 686.4379 | 240.769 | 233.3521 | 237.1083
606.4729 | 694.2351 | 241.1535 | 234.14 | 237.0398
607.4729 | 693.1059 | 240.7257 | 234.1727 | 236.9303
608.4729 | 691.0873 | 240.5882 | 234.5062 | 237.4404
609.4729 | 688.5013 | 240.8521 | 234.7713 | 236.9752
610.4729 | 686.621 | 241.4458 | 234.352 | 236.7514
611.4729 | 692.2369 | 241.8492 | 234.2272 | 236.9675
612.4729 | 688.0974 | 241.9806 | 234.7426 | 237.1046
613.4729 | 682.2162 | 242.6019 | 234.4642 | 237.3232
614.4885 | 681.3642 | 242.4965 | 234.7142 | 236.8814
615.4729 | 677.8464 | 242.9793 | 234.6352 | 236.7105
616.4729 | 675.2026 | 243.5208 | 234.7585 | 236.298
617.4729 | 673.7216 | 243.6822 | 234.687 | 236.874
618.4729 | 671.9683 | 243.7228 | 234.7714 | 236.6824
619.4729 | 671.4292 | 243.9562 | 235.368 | 237.2687
620.4729 | 668.9208 | 243.7358 | 235.3209 | 238.0806
621.4729 | 669.9634 | 243.7823 | 235.1438 | 238.0577
622.4729 | 668.4273 | 243.8556 | 235.8082 | 238.3897
623.4729 | 667.4765 | 243.5863 | 235.6958 | 238.4103
624.4729 | 666.7141 | 243.8359 | 235.823 | 238.489
625.4729 | 665.4724 | 243.8324 | 236.0699 | 238.4286
626.4729 | 666.1675 | 244.015 | 236.0337 | 238.2444
627.4729 | 666.0065 | 244.3673 | 235.8338 | 237.676
628.4729 | 665.1228 | 244.1759 | 235.6146 | 237.4165
629.4729 | 671.763 | 243.953 | 235.8627 | 237.555
630.4729 | 672.4167 | 244.4618 | 236.2271 | 238.3127
631.4729 | 671.2716 | 244.6915 | 236.5042 | 238.3744
632.4729 | 670.5025 | 244.7845 | 236.602 | 238.7259
633.4729 | 667.1184 | 245.2278 | 236.7265 | 238.4606
634.4729 | 667.609 | 244.9024 | 237.2656 | 238.786
635.4729 | 667.6475 | 244.9259 | 237.1105 | 238.9481
636.4729 | 666.655 | 244.7831 | 237.7138 | 238.7287
637.4729 | 668.018 | 245.1186 | 238.3972 | 240.0665
638.4729 | 666.1235 | 245.6708 | 238.1662 | 240.2436
639.4729 | 666.3293 | 245.7689 | 238.1349 | 239.6236
640.4729 | 664.3793 | 245.7376 | 238.0064 | 239.6866
641.4729 | 663.376 | 245.1672 | 238.4873 | 239.5986
642.4729 | 664.2621 | 244.7505 | 237.8579 | 239.5348
643.4729 | 664.3583 | 244.7609 | 237.5911 | 239.2505
644.5042 | 664.8356 | 244.4844 | 237.1834 | 239.3601
645.4729 | 664.0941 | 243.83 | 237.6767 | 239.638
646.4729 | 662.5704 | 243.5324 | 237.244 | 239.3942
647.4729 | 660.9268 | 242.9028 | 237.391 | 239.8042
648.4729 | 663.6627 | 243.2033 | 237.4054 | 240.0821
649.4729 | 664.2763 | 243.0287 | 237.4835 | 239.586
650.4729 | 663.4852 | 243.0537 | 237.1456 | 239.4551
651.4729 | 663.0732 | 243.5737 | 236.9314 | 239.3637
652.4729 | 661.649 | 243.5102 | 237.4821 | 240.098
653.4729 | 659.5086 | 243.1056 | 237.3419 | 239.8919
654.4729 | 655.9785 | 243.2018 | 237.6421 | 240.0467
655.4729 | 658.6496 | 243.1075 | 237.5174 | 239.4866
656.4729 | 657.2908 | 243.1515 | 237.5737 | 239.099
657.4729 | 655.5623 | 243.0992 | 237.8733 | 239.6441
658.4729 | 656.2388 | 243.845 | 238.0803 | 239.3332
659.4729 | 657.2508 | 244.2455 | 238.0408 | 239.9827
660.4729 | 657.5056 | 243.894 | 237.7873 | 240.0497
661.4729 | 657.3709 | 243.8283 | 237.8374 | 240.9183
662.4729 | 655.8071 | 244.0363 | 237.9677 | 241.2737
663.4729 | 655.6916 | 243.6477 | 238.4863 | 241.9699
664.4729 | 654.895 | 243.9143 | 238.4009 | 242.7737
665.4729 | 653.2472 | 244.0892 | 238.5188 | 242.9985
666.4729 | 652.295 | 243.6681 | 239.5331 | 243.3552
667.4729 | 652.1774 | 243.7507 | 239.9044 | 244.2444
668.4729 | 652.085 | 243.9638 | 240.6519 | 244.7331
669.4729 | 650.2032 | 244.4891 | 240.6235 | 245.2249
670.4729 | 652.2469 | 244.7836 | 240.7623 | 245.0833
671.4729 | 651.0029 | 244.4543 | 240.9251 | 245.34
672.4729 | 653.2947 | 244.6641 | 240.8646 | 245.7113
673.4729 | 650.8789 | 245.2128 | 241.9267 | 246.1334
674.4729 | 651.0549 | 245.7133 | 242.0508 | 246.514
675.4729 | 652.9178 | 245.896 | 242.6862 | 246.848
676.4729 | 654.521 | 246.0862 | 243.3357 | 247.702
677.4729 | 653.3591 | 245.6692 | 243.1805 | 248.0159
678.4729 | 652.8807 | 245.6184 | 243.6962 | 248.3902
679.4729 | 655.6875 | 245.3457 | 243.6485 | 248.5969
680.4729 | 656.9614 | 244.833 | 243.6716 | 248.7918
681.4729 | 658.9596 | 245.5811 | 244.1173 | 249.1827
682.4729 | 658.0144 | 245.6066 | 245.5736 | 249.3205
683.4729 | 659.4977 | 246.5837 | 245.7627 | 249.5168
684.4729 | 659.5385 | 246.6678 | 245.6177 | 249.3354
685.4729 | 658.5121 | 247.5312 | 245.8125 | 249.7884
686.4729 | 664.2396 | 247.7924 | 246.2444 | 249.8371
687.4729 | 663.6479 | 248.0638 | 247.1069 | 250.3932
688.4729 | 663.7931 | 248.6143 | 247.1862 | 250.3428
689.4729 | 665.1929 | 248.3247 | 246.9672 | 250.4623
690.4729 | 664.0897 | 248.2857 | 247.0979 | 250.3409
691.4729 | 662.4231 | 248.6032 | 247.8058 | 250.2576
692.4729 | 659.9403 | 249.1503 | 248.0568 | 250.188
693.4729 | 659.7251 | 249.1456 | 248.5563 | 250.0633
694.4729 | 659.5812 | 249.5428 | 248.4651 | 249.9566
695.4729 | 659.5686 | 249.8779 | 248.3812 | 250.1648
696.4729 | 660.0637 | 249.765 | 247.744 | 250.5514
697.4729 | 658.5172 | 249.4652 | 247.436 | 250.4589
698.4729 | 659.0802 | 249.1438 | 247.2636 | 250.4913
699.4729 | 657.9176 | 250.0011 | 247.383 | 250.4966
700.4729 | 658.3005 | 249.4766 | 246.578 | 250.5307
701.4729 | 657.792 | 249.3275 | 246.3856 | 250.854
702.4729 | 660.8966 | 249.1625 | 246.4767 | 250.8137
703.4729 | 660.4727 | 249.0656 | 246.6276 | 251.2425
704.4885 | 660.2966 | 248.7247 | 246.4191 | 251.8013
705.4729 | 658.5454 | 248.6979 | 246.4007 | 252.1858
706.4729 | 658.4107 | 248.9645 | 246.6272 | 252.1315
707.4729 | 659.246 | 249.5055 | 247.2653 | 252.1943
708.4729 | 659.1649 | 249.2493 | 247.0561 | 252.0231
709.4729 | 657.5229 | 249.1955 | 246.7453 | 251.6459
710.4729 | 657.155 | 249.4082 | 247.4633 | 252.0444
711.4729 | 656.7448 | 249.4312 | 247.861 | 252.3871
712.4729 | 655.6589 | 249.5849 | 247.7802 | 252.7898
713.4729 | 655.7795 | 250.0098 | 247.9234 | 253.3114
714.4729 | 656.0439 | 249.8559 | 247.9925 | 253.5667
715.4729 | 655.6038 | 250.2998 | 248.1847 | 253.6524
716.4729 | 657.3798 | 250.3227 | 248.0576 | 253.6793
717.4729 | 657.8213 | 250.8199 | 248.3934 | 254.0666
718.4729 | 659.9888 | 250.9837 | 248.8786 | 254.3065
719.4729 | 661.2724 | 251.8256 | 248.9663 | 253.5228
720.4729 | 663.6537 | 251.4333 | 248.7327 | 253.0519
721.4729 | 663.2149 | 251.9234 | 249.1073 | 253.378
722.4729 | 663.4843 | 252.3472 | 249.3197 | 254.1371
723.4729 | 664.6302 | 252.3788 | 249.7531 | 254.399
724.4729 | 666.4899 | 252.5856 | 250.6438 | 254.776
725.4729 | 666.0538 | 252.198 | 250.811 | 254.842
726.4729 | 665.1254 | 252.4728 | 250.9153 | 255.0961
727.4729 | 665.3691 | 253.3473 | 251.4284 | 255.4229
728.4729 | 663.3998 | 253.6808 | 251.8089 | 255.8578
729.4729 | 662.6407 | 253.5213 | 252.1324 | 255.6037
730.4729 | 661.7014 | 253.6466 | 252.0832 | 255.5177
731.4729 | 660.5201 | 253.9262 | 252.1711 | 256.3538
732.4729 | 660.6812 | 254.283 | 252.201 | 256.4383
733.4729 | 659.8118 | 254.2556 | 251.4864 | 256.6617
734.4885 | 659.4792 | 254.6726 | 251.7698 | 256.7603
735.4729 | 659.5261 | 254.961 | 251.9124 | 256.6842
736.4729 | 659.5244 | 254.4593 | 251.5928 | 256.8847
737.4729 | 662.6801 | 254.2784 | 251.6384 | 257.0754
738.4729 | 663.8625 | 254.3861 | 251.6301 | 256.6343
739.4729 | 664.7646 | 254.8357 | 251.5036 | 256.9078
740.4729 | 665.047 | 254.6023 | 251.9712 | 257.5519
741.4729 | 664.9848 | 254.5733 | 251.8904 | 257.7974
742.4729 | 663.2034 | 254.8021 | 252.4794 | 258.2976
743.4729 | 661.8008 | 255.1584 | 252.7525 | 258.775
744.4729 | 665.2823 | 255.1802 | 252.5681 | 259.0675
745.4729 | 664.3698 | 255.3044 | 252.3557 | 258.9407
746.4729 | 662.4843 | 255.4694 | 253.0358 | 258.9341
747.4885 | 660.9636 | 255.1303 | 253.0861 | 258.6663
748.4885 | 659.9413 | 255.043 | 253.1608 | 258.9254
749.4729 | 660.2619 | 255.6832 | 254.0678 | 258.9866
750.4729 | 658.1514 | 255.5616 | 253.9899 | 258.9171
751.4729 | 657.9266 | 255.5448 | 253.5818 | 259.4701
752.4729 | 657.844 | 255.3094 | 254.0908 | 259.2425
753.4729 | 658.1359 | 255.0796 | 253.686 | 259.2002
754.4729 | 657.8041 | 255.0293 | 254.5076 | 259.5586
755.4729 | 657.7605 | 255.3871 | 254.1169 | 259.8695
756.4729 | 657.6452 | 255.3032 | 254.7536 | 259.4028
757.4729 | 656.6933 | 255.4879 | 254.7229 | 259.3084
758.4729 | 658.5506 | 255.5082 | 254.6239 | 259.3967
759.4729 | 658.4579 | 255.4331 | 254.2317 | 258.9923
760.4729 | 658.3739 | 255.3898 | 253.8766 | 259.0716
761.4729 | 659.4118 | 255.9077 | 254.9887 | 260.1832
762.4729 | 660.636 | 256.1682 | 254.2418 | 259.3943
763.4729 | 660.8637 | 256.537 | 255.141 | 259.5397
764.4885 | 660.2157 | 256.5054 | 255.1721 | 260.0962
765.4729 | 659.4034 | 257.1341 | 255.3002 | 259.54
766.4729 | 657.7623 | 257.301 | 255.5865 | 259.7524
767.4729 | 660.4298 | 257.1022 | 256.1167 | 259.7606
768.4729 | 659.5292 | 257.3276 | 255.7657 | 259.8127
769.4729 | 659.0294 | 257.522 | 255.1002 | 259.8424
770.4729 | 658.2901 | 257.997 | 254.8391 | 259.5932
771.4729 | 657.4475 | 258.2224 | 254.4463 | 259.7817
772.4729 | 656.933 | 257.9463 | 254.2003 | 259.7827
773.4729 | 657.4325 | 257.72 | 254.4375 | 260.0966
774.4729 | 656.5942 | 257.3388 | 254.223 | 259.7829
775.4729 | 656.8467 | 257.1822 | 254.3231 | 259.364
776.4729 | 657.6886 | 257.2077 | 253.8111 | 259.1192
777.4729 | 656.9941 | 257.0681 | 254.554 | 258.9129
778.4729 | 656.1658 | 256.9772 | 254.2481 | 258.7801
779.4729 | 654.6209 | 256.8082 | 253.613 | 258.6796
780.4729 | 655.7718 | 256.7002 | 254.5332 | 259.2763
781.4729 | 656.0935 | 256.3922 | 254.1207 | 259.2693
782.4729 | 657.2911 | 256.5964 | 254.221 | 259.8111
783.4729 | 657.0166 | 256.2591 | 253.9671 | 260.2794
784.4729 | 656.2068 | 256.1795 | 253.4378 | 259.4867
785.4729 | 656.6632 | 256.145 | 253.9175 | 259.8491
786.4729 | 656.8612 | 255.9216 | 254.48 | 259.8248
787.4729 | 656.9305 | 255.8841 | 254.7168 | 259.5914
788.4729 | 657.4921 | 255.9295 | 255.074 | 260.1828
789.4729 | 656.5352 | 256.0742 | 255.4518 | 260.6165
790.4729 | 655.8978 | 256.3881 | 255.2335 | 261.1256
791.4729 | 654.3935 | 256.4401 | 254.9284 | 261.6065
792.4729 | 653.7814 | 256.0542 | 255.4301 | 261.945
793.4729 | 652.5828 | 256.4459 | 255.8524 | 261.9986
794.4729 | 651.9694 | 256.6201 | 255.9866 | 261.7134
795.4729 | 651.6999 | 256.4487 | 255.6926 | 261.9247
796.4729 | 652.3912 | 256.3742 | 255.6876 | 262.1857
797.4729 | 653.0692 | 256.1035 | 255.5724 | 262.2212
798.4729 | 653.1457 | 256.2928 | 255.2739 | 262.4194
799.4729 | 656.0457 | 256.2455 | 255.2898 | 262.4901
800.4729 | 655.8976 | 256.5448 | 255.7057 | 262.7864
801.4729 | 655.4253 | 256.84 | 255.4754 | 262.856
802.4729 | 655.6679 | 257.1861 | 255.6728 | 262.9593
803.4729 | 656.5467 | 257.2171 | 256.2456 | 262.9573
804.4729 | 657.3588 | 257.1073 | 256.5826 | 263.4649
805.4729 | 656.3381 | 257.1604 | 256.7215 | 263.5251
806.4729 | 654.8127 | 257.5404 | 256.9134 | 263.435
807.4729 | 654.1231 | 257.8984 | 256.937 | 262.8844
808.4729 | 654.2735 | 257.6028 | 257.13 | 263.1043
809.4729 | 652.6532 | 257.6196 | 256.948 | 263.0635
810.4729 | 652.9805 | 257.6707 | 257.0444 | 262.4704
811.4729 | 652.3118 | 258.221 | 257.7944 | 261.9977
812.4729 | 652.0397 | 258.0217 | 258.0161 | 262.0703
813.4729 | 656.6227 | 258.0214 | 257.7993 | 262.2394
814.4729 | 655.5701 | 258.3058 | 257.2692 | 261.8609
815.4729 | 655.6035 | 258.5157 | 257.1623 | 261.8872
816.4729 | 655.9367 | 258.3845 | 257.1087 | 261.482
817.4729 | 655.3208 | 258.4662 | 257.1164 | 261.5872
818.4729 | 655.1162 | 258.6015 | 257.2557 | 261.7794
819.4729 | 655.1367 | 258.7125 | 257.365 | 262.4312
820.4729 | 655.8862 | 259.2377 | 257.3685 | 262.9075
821.4729 | 656.8709 | 260.5548 | 257.2336 | 263.3863
822.4729 | 655.9696 | 260.8349 | 257.5512 | 263.4335
823.4729 | 656.0415 | 260.7077 | 257.4739 | 263.915
824.4729 | 655.6401 | 260.7758 | 257.6054 | 264.1636
825.4729 | 655.9468 | 260.9354 | 257.6258 | 263.9492
826.4729 | 656.6381 | 260.9878 | 257.8992 | 263.5989
827.4729 | 658.4473 | 260.5285 | 257.8649 | 264.1478
828.4729 | 659.2227 | 260.0481 | 257.7006 | 264.5569
829.4729 | 661.4834 | 260.0219 | 258.0856 | 265.1118
830.4729 | 661.3168 | 260.1409 | 257.8379 | 265.4599
831.4729 | 662.2062 | 260.4699 | 257.5759 | 265.4824
832.4729 | 663.0796 | 260.3029 | 257.1846 | 265.9892
833.4729 | 661.958 | 260.5246 | 256.8444 | 265.91
834.4729 | 661.8099 | 260.8393 | 256.9037 | 265.4088
835.4729 | 662.1714 | 261.0428 | 257.2258 | 265.9153
836.4729 | 663.3746 | 261.1416 | 257.7783 | 265.9703
837.4729 | 664.3198 | 261.7344 | 258.4142 | 266.3331
838.4729 | 664.7605 | 261.3903 | 258.3757 | 266.1283
839.4729 | 665.0423 | 262.0066 | 258.4855 | 266.1012
840.4729 | 666.3285 | 262.1809 | 258.4224 | 266.4084
841.4729 | 666.9154 | 262.6101 | 259.4031 | 266.1159
842.4729 | 666.9296 | 262.5057 | 259.2149 | 266.205
843.4729 | 665.2905 | 262.5648 | 259.2247 | 266.4512
844.4729 | 665.5514 | 262.7735 | 259.3391 | 265.9529
845.4729 | 664.5801 | 262.9485 | 259.7563 | 266.2929
846.4729 | 663.0921 | 262.7667 | 260.1442 | 265.8983
847.4729 | 663.0839 | 262.77 | 260.2761 | 266.1723
848.4729 | 663.904 | 262.4887 | 260.3956 | 266.0553
849.4729 | 666.7416 | 262.9881 | 260.6973 | 266.5006
850.4729 | 668.5289 | 263.1322 | 260.7862 | 266.4035
851.4729 | 669.7025 | 263.7261 | 260.816 | 266.3649
852.4729 | 669.501 | 264.4059 | 261.1422 | 266.1044
853.4729 | 671.0154 | 264.4363 | 261.0608 | 265.8734
854.4885 | 669.0918 | 265.0462 | 261.7211 | 265.4888
855.4729 | 670.496 | 265.5667 | 262.6201 | 265.8788
856.4729 | 674.7022 | 265.5574 | 261.9704 | 265.9957
857.4729 | 674.4831 | 265.2921 | 262.6254 | 266.4051
858.4729 | 674.3755 | 265.3987 | 262.6778 | 266.5689
859.4729 | 674.1477 | 265.697 | 262.4407 | 266.3828
860.4729 | 673.3239 | 265.2695 | 262.5417 | 266.4605
861.4729 | 675.8869 | 265.2475 | 262.8863 | 266.0228
862.4729 | 676.988 | 265.6554 | 263.0655 | 266.6705
863.4729 | 676.2602 | 265.1585 | 263.2664 | 266.6375
864.4729 | 675.6007 | 265.2774 | 262.9084 | 266.008
865.4729 | 674.0455 | 265.2028 | 262.9495 | 265.9775
866.4729 | 675.5906 | 265.1911 | 263.0188 | 266.3221
867.4729 | 675.1482 | 265.0717 | 263.3423 | 266.5782
868.4729 | 673.6353 | 264.9572 | 263.1594 | 266.7987
869.4729 | 673.7045 | 264.9673 | 263.233 | 266.2304
870.4729 | 676.0604 | 264.7868 | 263.3433 | 266.3638
871.4729 | 678.9012 | 264.5723 | 262.9786 | 266.5763
872.4729 | 679.1975 | 264.5951 | 262.5718 | 266.0994
873.4729 | 680.3067 | 264.3583 | 262.4566 | 266.1413
874.4729 | 682.1825 | 264.586 | 262.2974 | 265.9227
875.4729 | 684.1298 | 264.2743 | 262.2308 | 266.0009
876.4729 | 685.5518 | 263.7736 | 261.7125 | 266.2848
877.4729 | 686.2085 | 263.3776 | 261.9839 | 266.2338
878.4729 | 686.4584 | 263.3493 | 261.7359 | 265.7419
879.4729 | 685.7011 | 263.2458 | 261.5943 | 265.3496
880.4729 | 684.6215 | 263.4084 | 262.5741 | 265.9435
881.4729 | 685.4823 | 263.7489 | 262.4795 | 265.9499
882.4729 | 685.5747 | 263.8283 | 262.9737 | 266.1098
883.4729 | 685.6021 | 263.6409 | 262.9727 | 266.2716
884.4729 | 686.9716 | 264.5197 | 263.6567 | 266.6412
885.4729 | 687.6723 | 264.4612 | 264.1785 | 266.9902
886.4729 | 688.9885 | 264.6261 | 263.9373 | 267.3402
887.4729 | 688.8131 | 264.6021 | 263.7216 | 267.092
888.4729 | 688.4675 | 264.1027 | 263.5769 | 267.094
889.4729 | 687.2353 | 264.3674 | 263.5079 | 267.5489
890.4729 | 684.9892 | 264.3692 | 263.4807 | 267.2846
891.4729 | 684.7624 | 264.9024 | 263.2289 | 266.9819
892.4729 | 685.3427 | 265.1428 | 263.5713 | 267.0325
893.4729 | 685.9105 | 264.9415 | 263.5958 | 266.9846
894.4729 | 684.8419 | 264.8488 | 263.558 | 267.1324
895.4729 | 684.8362 | 264.607 | 263.3588 | 267.2425
896.4729 | 685.2447 | 264.7921 | 263.5154 | 267.832
897.4729 | 688.5222 | 264.6237 | 263.5742 | 267.6335
898.4729 | 689.3859 | 264.5765 | 263.42 | 267.754
899.4729 | 691.1273 | 264.4717 | 263.2213 | 267.7987
900.4729 | 691.2709 | 264.1544 | 262.9966 | 267.8919
901.4729 | 692.5516 | 264.1871 | 263.0701 | 268.1033
902.4729 | 693.6181 | 263.712 | 264.0973 | 268.631
903.4729 | 695.1993 | 263.7632 | 264.0051 | 268.9652
904.4729 | 695.7605 | 263.8941 | 263.7768 | 269.1064
905.4729 | 695.8463 | 263.9216 | 263.8771 | 269.4749
906.4729 | 693.5272 | 264.5015 | 263.9281 | 269.6676
907.4729 | 693.2223 | 264.1855 | 263.7935 | 269.8676
908.4729 | 693.9467 | 264.0345 | 263.7452 | 270.0695
909.4729 | 693.308 | 263.9131 | 263.8191 | 270.1549
910.4729 | 694.7491 | 263.698 | 263.5955 | 269.9631
911.4729 | 694.0114 | 263.7298 | 263.3612 | 270.0117
912.4729 | 695.0058 | 264.2447 | 263.5193 | 270.2761
913.4729 | 695.1888 | 264.4336 | 264.1001 | 270.7718
914.4729 | 695.4437 | 264.7284 | 263.8848 | 271.1642
915.4729 | 695.1045 | 265.018 | 264.2058 | 271.3253
916.4729 | 694.4719 | 264.8557 | 263.9146 | 271.3083
917.4729 | 694.1194 | 265.3563 | 264.5646 | 270.8475
918.4729 | 694.2539 | 265.4661 | 265.0425 | 271.6306
919.4729 | 692.2626 | 265.8665 | 265.0786 | 271.9506
920.4729 | 691.8658 | 266.1809 | 264.9882 | 272.0314
921.4729 | 691.2449 | 266.0032 | 265.2286 | 272.3651
922.4729 | 692.2476 | 265.9173 | 265.225 | 271.9977
923.4729 | 694.7958 | 265.8835 | 265.0678 | 272.2899
924.4729 | 696.7372 | 265.3857 | 264.7789 | 272.0286
925.4729 | 695.5586 | 265.1793 | 264.9091 | 271.8356
926.4729 | 695.349 | 265.0144 | 264.6428 | 271.5851
927.4729 | 696.6272 | 265.1218 | 264.3918 | 271.0423
928.4729 | 698.6544 | 264.7644 | 264.4113 | 270.9921
929.4729 | 701.3482 | 264.4205 | 264.2926 | 271.456
930.4729 | 701.9967 | 264.2875 | 264.4137 | 271.8291
931.4729 | 704.5175 | 264.4172 | 265.1447 | 272.1023
932.4729 | 704.1841 | 264.4736 | 265.5457 | 272.351
933.4729 | 706.5912 | 264.4617 | 265.6652 | 272.6838
934.4729 | 705.4651 | 264.5748 | 265.346 | 273.0183
935.4729 | 704.9376 | 264.6568 | 265.005 | 272.1269
936.4729 | 704.8894 | 264.893 | 265.2822 | 272.295
937.4729 | 706.7839 | 264.9245 | 265.5186 | 272.0484
938.4729 | 708.9852 | 265.1183 | 265.774 | 271.1152
939.4729 | 708.5894 | 265.1067 | 265.6972 | 271.453
940.4729 | 708.4069 | 265.3381 | 265.792 | 271.1736
941.4729 | 708.4866 | 265.5137 | 266.1383 | 272.0349
942.4729 | 707.7876 | 265.6211 | 266.1124 | 271.9071
943.4729 | 707.5051 | 265.8836 | 266.6789 | 271.5976
944.4729 | 709.0366 | 266.5598 | 267.2599 | 271.6363
945.4729 | 708.9297 | 266.3805 | 267.5196 | 271.6008
946.4729 | 710.8235 | 266.4325 | 267.8052 | 271.75
947.4729 | 710.5147 | 266.5453 | 267.7662 | 271.3822
948.4729 | 710.2621 | 266.6496 | 268.4157 | 271.2625
949.4729 | 709.5262 | 267.0136 | 268.4221 | 271.5071
950.4729 | 709.2478 | 267.0459 | 267.7159 | 271.5693
951.4729 | 709.0753 | 267.1785 | 267.647 | 271.4199
952.4729 | 710.8068 | 267.1993 | 267.6409 | 271.3487
953.4729 | 708.9765 | 267.4914 | 267.538 | 271.3027
954.4729 | 708.7192 | 267.8836 | 267.3213 | 271.1531
955.4729 | 709.7575 | 268.0979 | 266.9872 | 271.7396
956.4729 | 710.7843 | 268.4676 | 266.8919 | 272.3016
957.4729 | 711.2022 | 268.5063 | 267.3534 | 272.7307
958.4729 | 711.3646 | 268.2634 | 267.6688 | 273.108
959.4729 | 711.6433 | 267.8418 | 266.9559 | 272.8388
960.4729 | 711.0031 | 267.5856 | 266.8399 | 272.7267
961.4729 | 713.0367 | 267.0848 | 266.9891 | 272.7284
962.4729 | 714.8985 | 267.1662 | 266.9535 | 272.7631
963.4729 | 716.5672 | 267.0236 | 266.8904 | 272.4559
964.4729 | 716.2793 | 266.481 | 266.3256 | 272.222
965.4729 | 714.6164 | 266.5496 | 266.131 | 271.9263
966.4729 | 714.5689 | 266.4149 | 266.6647 | 271.9834
967.4729 | 713.2704 | 266.839 | 266.5647 | 272.2995
968.4729 | 712.6391 | 266.8437 | 266.865 | 272.2264
969.4729 | 712.7633 | 267.1102 | 266.8694 | 272.4389
970.4729 | 713.095 | 268.0269 | 267.3908 | 273.01
971.4729 | 713.4067 | 268.0268 | 267.2485 | 272.8704
972.4729 | 714.5821 | 268.1113 | 267.2135 | 273.1198
973.4729 | 716.2973 | 268.0863 | 267.5261 | 273.2414
974.4729 | 716.7165 | 267.9574 | 267.1679 | 273.0673
975.4729 | 719.304 | 267.984 | 266.9505 | 272.9352
976.4729 | 720.6025 | 267.6756 | 266.8933 | 272.9634
977.4729 | 723.5978 | 267.4307 | 267.1725 | 273.4249
978.4729 | 723.2277 | 267.2901 | 267.0723 | 273.242
979.4729 | 722.7237 | 267.5056 | 267.2219 | 273.3471
980.4729 | 724.7681 | 267.1825 | 267.0884 | 272.9838
981.4729 | 725.2703 | 267.9383 | 267.4694 | 272.8991
982.4729 | 728.3426 | 267.8495 | 267.6553 | 273.0892
983.4729 | 732.0459 | 267.46 | 267.9666 | 273.489
984.4729 | 734.2214 | 267.754 | 267.716 | 273.5525
985.4729 | 734.4631 | 267.7756 | 267.3978 | 273.4046
986.4729 | 736.077 | 268.0646 | 267.643 | 273.7989
987.4729 | 738.0909 | 268.0302 | 267.7762 | 273.7927
988.4729 | 739.6147 | 268.4922 | 268.2253 | 274.7343
989.4729 | 740.6886 | 269.1987 | 268.442 | 274.8537
990.4729 | 740.6037 | 269.8318 | 268.487 | 274.7579
991.4729 | 738.7263 | 270.3543 | 268.5826 | 274.773
992.4729 | 736.8766 | 270.509 | 269.1953 | 274.8109
993.4729 | 736.3017 | 270.382 | 269.2325 | 275.1327
994.4729 | 737.9676 | 270.4738 | 269.4871 | 275.6124
995.4729 | 735.714 | 270.4826 | 270.0848 | 276.0503
996.4729 | 736.0848 | 270.4411 | 270.1047 | 275.6242
997.4729 | 735.8865 | 270.549 | 270.5051 | 275.9675
998.4729 | 736.3674 | 270.6642 | 270.3721 | 275.8091
999.4729 | 735.7473 | 270.4479 | 270.1954 | 275.9817
1000.4729 | 737.5018 | 270.3516 | 270.2368 | 276.3069
1001.4729 | 739.7858 | 270.5572 | 270.6946 | 276.2208
1002.4729 | 739.6747 | 270.4735 | 271.2816 | 276.5434
1003.4729 | 739.2596 | 270.3547 | 270.7899 | 276.326
1004.4729 | 739.5018 | 270.2477 | 270.8693 | 276.8162
1005.4729 | 739.927 | 269.9966 | 271.1551 | 276.2618
1006.4729 | 738.9281 | 269.9767 | 270.8144 | 276.1077
1007.4729 | 737.3001 | 269.8622 | 270.6049 | 275.7543
1008.4729 | 736.7508 | 269.9042 | 270.3477 | 275.8775
1009.4729 | 736.6861 | 270.3473 | 270.841 | 276.3669
1010.4729 | 737.8481 | 270.001 | 270.7043 | 276.2936
1011.4729 | 738.5158 | 269.8595 | 270.5818 | 276.1602
1012.4729 | 739.3806 | 269.8818 | 270.9663 | 276.2325
1013.4729 | 739.5423 | 269.7437 | 270.9222 | 276.1961
1014.4729 | 742.3561 | 270.0133 | 271.0923 | 276.6493
1015.4729 | 744.7436 | 270.1081 | 270.9555 | 276.9395
1016.4729 | 742.757 | 270.3379 | 270.7795 | 276.6119
1017.4729 | 740.8282 | 270.7033 | 271.2514 | 276.2739
1018.4729 | 741.5636 | 270.9101 | 271.2429 | 276.4355
1019.4729 | 741.2948 | 270.414 | 271.0346 | 276.1286
1020.4729 | 740.7492 | 270.4712 | 271.4007 | 276.2965
1021.4729 | 740.5136 | 270.263 | 271.2537 | 276.8241
1022.4729 | 742.6682 | 270.2955 | 271.3213 | 276.7229
1023.4729 | 744.0751 | 270.5083 | 272.1676 | 276.3636
1024.4729 | 747.5634 | 270.5568 | 272.2431 | 277.0279
1025.4729 | 752.4343 | 270.3783 | 272.2782 | 276.932
1026.4729 | 752.5163 | 270.325 | 271.8542 | 276.6127
1027.4729 | 751.1524 | 270.755 | 271.797 | 276.5614
1028.4729 | 753.3893 | 270.5315 | 271.8834 | 276.6405
1029.4729 | 755.2757 | 270.7186 | 271.7485 | 276.7419
1030.4729 | 756.7109 | 271.1765 | 272.2962 | 277.2366
1031.4729 | 759.6331 | 270.9228 | 272.0929 | 277.7064
1032.4729 | 759.865 | 271.077 | 272.3688 | 277.1026
1033.4729 | 757.1036 | 270.996 | 272.5966 | 276.9887
1034.4729 | 760.6821 | 270.6009 | 273.1101 | 277.2741
1035.4729 | 761.0512 | 270.3255 | 272.8377 | 276.6304
1036.4729 | 759.6587 | 270.8158 | 273.0098 | 276.2702
1037.4729 | 762.0242 | 270.8691 | 272.8422 | 275.5711
1038.4729 | 763.9842 | 271.1173 | 272.9747 | 275.3051
1039.4729 | 766.0448 | 271.2722 | 272.7663 | 275.8313
1040.4729 | 762.8901 | 271.4597 | 273.3053 | 275.8152
1041.4729 | 762.3505 | 271.8028 | 273.0315 | 275.4808
1042.4729 | 761.0458 | 271.8696 | 273.3237 | 276.1597
1043.4729 | 761.8496 | 271.9512 | 273.0613 | 275.7403
1044.4729 | 763.7691 | 271.6412 | 273.1791 | 275.9345
1045.4729 | 765.3979 | 271.5702 | 272.8989 | 275.9906
1046.4729 | 764.0374 | 271.9871 | 272.9197 | 276.2524
1047.4729 | 768.4863 | 272.0913 | 273.4276 | 276.8957
1048.4729 | 763.8091 | 272.4124 | 273.2209 | 276.52
1049.4729 | 761.5366 | 272.1754 | 273.053 | 276.4548
1050.4729 | 762.0338 | 272.4396 | 273.0446 | 276.5835
1051.4729 | 763.4131 | 272.5434 | 273.5578 | 276.864
1052.4729 | 762.812 | 272.3608 | 272.892 | 276.9685
1053.4729 | 763.7425 | 271.8866 | 272.9525 | 276.7335
1054.4729 | 763.7517 | 271.4988 | 273.0975 | 276.9449
1055.4729 | 764.2966 | 271.2963 | 272.5955 | 276.9997
1056.4729 | 766.3482 | 271.8096 | 272.9862 | 277.0476
1057.4729 | 764.3721 | 271.4609 | 273.0023 | 277.2023
1058.4729 | 763.5841 | 271.3395 | 272.7492 | 277.3344
1059.4729 | 768.3964 | 271.7191 | 273.1534 | 277.3277
1060.4729 | 774.6278 | 271.4063 | 272.9981 | 276.9804
1061.4729 | 770.4641 | 271.3644 | 272.5225 | 276.8568
1062.4729 | 771.4153 | 271.087 | 272.6554 | 276.7685
1063.4729 | 772.4262 | 270.7555 | 272.166 | 277.0197
1064.4729 | 770.9043 | 271.0868 | 272.3862 | 276.9324
1065.4729 | 775.4888 | 271.4697 | 271.9419 | 277.3462
1066.4729 | 777.7974 | 271.6928 | 271.8691 | 277.7588
1067.4729 | 784.3395 | 271.3844 | 271.9889 | 278.0178
1068.4729 | 788.3351 | 271.5989 | 272.0075 | 278.1704
1069.4729 | 787.2065 | 271.4751 | 271.8019 | 277.7335
1070.4729 | 785.0025 | 271.9913 | 272.0189 | 277.9148
1071.4729 | 786.1393 | 272.3784 | 271.9529 | 277.0381
1072.4729 | 782.7692 | 272.9103 | 272.5337 | 276.6182
1073.4729 | 782.9222 | 272.8193 | 272.2959 | 276.9049
1074.4729 | 777.6316 | 273.7445 | 272.468 | 277.3597
1075.4729 | 776.4996 | 273.7939 | 272.9294 | 277.9507
1076.4729 | 778.3891 | 274.2169 | 272.9474 | 278.5748
1077.4729 | 782.1149 | 274.8679 | 273.9255 | 279.4662
1078.4729 | 781.0676 | 275.3866 | 274.3867 | 279.7454
1079.4729 | 781.422 | 275.8136 | 275.2454 | 280.568
1080.4729 | 778.4239 | 276.2109 | 275.1182 | 280.8088
1081.4729 | 781.5132 | 275.9422 | 275.4704 | 281.3251
1082.4729 | 781.3896 | 276.2333 | 275.603 | 281.939
1083.4885 | 785.3319 | 276.0489 | 275.9732 | 282.6299
1084.4729 | 786.4818 | 276.3699 | 276.267 | 282.6758
1085.4729 | 791.5788 | 276.505 | 276.7648 | 282.708
1086.4729 | 793.7757 | 276.9873 | 277.2944 | 283.43
1087.4729 | 797.4076 | 278.0198 | 277.5243 | 282.9834
1088.4729 | 800.4391 | 278.4329 | 277.5247 | 283.1569
1089.4729 | 799.5588 | 278.1909 | 277.9329 | 283.3615
1090.4729 | 799.5871 | 278.607 | 278.7217 | 283.8036
1091.4729 | 807.3377 | 278.3558 | 279.0095 | 284.3707
1092.4729 | 807.5859 | 278.512 | 279.7345 | 285.0686
1093.4729 | 809.9364 | 278.7736 | 279.4725 | 284.6113
1094.4729 | 809.9892 | 279.0866 | 279.523 | 285.0866
1095.4729 | 810.5132 | 279.4353 | 279.6947 | 285.0067
1096.4729 | 814.8595 | 279.6738 | 279.6063 | 284.6581
1097.4729 | 812.3079 | 280.0932 | 279.8871 | 284.9622
1098.4729 | 811.0367 | 280.8452 | 280.163 | 285.6214
1099.4729 | 815.4888 | 281.2262 | 280.6915 | 286.5915
1100.4729 | 813.9423 | 282.2707 | 280.8457 | 286.9551
1101.4729 | 813.4676 | 282.7691 | 281.303 | 286.8482
1102.4729 | 810.3064 | 282.6991 | 281.2349 | 286.9949
1103.4729 | 807.8034 | 282.8092 | 281.2688 | 287.6915
1104.4729 | 808.0967 | 283.44 | 281.9854 | 288.3932
1105.4729 | 808.4112 | 283.4168 | 282.1726 | 288.4495
1106.4729 | 807.3846 | 283.9198 | 281.827 | 288.1367
1107.4729 | 808.8533 | 283.5418 | 281.6121 | 287.9017
1108.4729 | 809.7938 | 283.7721 | 282.5409 | 288.0897
1109.4729 | 811.6996 | 284.2774 | 283.2343 | 288.386
1110.4729 | 809.3099 | 284.7468 | 283.565 | 288.8725
1111.4729 | 811.2683 | 284.8239 | 284.1098 | 289.767
1112.4729 | 810.0588 | 285.0284 | 283.8996 | 289.581
1113.4729 | 811.6457 | 284.864 | 284.3213 | 290.3294
1114.4729 | 811.8992 | 284.8796 | 284.4467 | 290.1463
1115.4729 | 815.1198 | 285.6323 | 284.7734 | 290.5665
1116.4729 | 813.7373 | 285.8094 | 284.3218 | 290.6641
1117.4729 | 815.1665 | 285.602 | 283.999 | 290.8578
1118.4729 | 812.5904 | 285.6672 | 284.2779 | 291.276
1119.4729 | 812.1361 | 285.7536 | 284.1453 | 291.3717
1120.4729 | 824.7406 | 285.7954 | 284.3173 | 291.8718
1121.4729 | 834.2485 | 285.6448 | 285.5677 | 292.493
1122.4729 | 841.3598 | 285.9989 | 286.8814 | 293.3334
1123.4729 | 830.0088 | 286.2159 | 286.7092 | 293.5852
1124.4729 | 821.7268 | 286.6795 | 287.0902 | 294.4577
1125.4729 | 817.9071 | 287.8729 | 287.2635 | 294.8032
1126.4729 | 815.2463 | 288.2735 | 286.9512 | 294.4214
1127.4729 | 814.045 | 288.2508 | 286.9214 | 295.3947
1128.4729 | 812.4572 | 288.8425 | 287.4931 | 295.5762
1129.4729 | 810.7618 | 289.0321 | 287.8755 | 295.9166
1130.4729 | 809.7588 | 290.1053 | 288.9437 | 295.9311
1131.4729 | 808.5981 | 290.8331 | 289.074 | 296.3192
1132.4729 | 808.8385 | 291.1197 | 289.5188 | 297.2687
1133.4729 | 807.275 | 291.4896 | 290.0554 | 297.5283
1134.4729 | 805.6445 | 291.9327 | 291.0572 | 297.9994
1135.4729 | 805.9175 | 292.0313 | 291.073 | 298.0872
1136.4729 | 807.061 | 291.7729 | 291.648 | 298.4781
1137.4729 | 807.7259 | 291.4101 | 291.7676 | 298.609
1138.4729 | 808.0903 | 291.4577 | 291.6313 | 298.5331
1139.4729 | 807.7834 | 291.0044 | 291.8591 | 297.7215
1140.4729 | 809.6215 | 290.6316 | 292.3615 | 298.6297
1141.4729 | 809.7076 | 291.243 | 291.7193 | 298.4885
1142.4729 | 807.4447 | 292.0533 | 291.5508 | 299.2606
1143.4729 | 806.9056 | 292.1059 | 290.9485 | 299.9203
1144.4729 | 805.6345 | 292.0991 | 290.7384 | 299.8022
1145.4729 | 807.4826 | 292.1247 | 291.3726 | 299.8894
1146.4729 | 806.8285 | 292.2967 | 291.3845 | 300.0811
1147.4729 | 807.8238 | 292.195 | 291.7346 | 300.1105
1148.4729 | 808.1301 | 292.0602 | 292.5892 | 300.7189
1149.4729 | 808.9846 | 291.9881 | 293.1223 | 300.4638
1150.4729 | 808.9451 | 292.3012 | 292.8803 | 301.3147
1151.4729 | 808.0492 | 292.4803 | 292.9009 | 301.0552
1152.4729 | 808.2493 | 292.7672 | 293.1329 | 301.6992
1153.4729 | 808.2967 | 292.5102 | 293.0179 | 301.5717
1154.4729 | 808.3128 | 292.8858 | 293.5112 | 302.6244
1155.4729 | 807.7023 | 293.0954 | 294.3547 | 303.0263
1156.4729 | 808.5819 | 293.2412 | 294.9347 | 304.4853
1157.4729 | 809.4849 | 293.3454 | 295.6175 | 305.0967
1158.4729 | 809.1791 | 293.8759 | 296.3027 | 305.0532
1159.4729 | 810.5736 | 294.4137 | 296.1578 | 305.1299
1160.4729 | 812.5262 | 294.2634 | 295.8855 | 304.9963
1161.4729 | 813.2237 | 294.7073 | 295.824 | 305.12
1162.4729 | 815.2769 | 294.4327 | 295.9034 | 306.1766
1163.4729 | 823.1355 | 294.8493 | 296.5967 | 306.7489
1164.4729 | 824.7152 | 295.5968 | 297.7673 | 307.4158
1165.4729 | 822.9638 | 296.1299 | 299.0947 | 308.0384
1166.4729 | 819.7143 | 295.9268 | 299.5154 | 308.5369
1167.4729 | 818.4497 | 296.8806 | 299.1476 | 309.1884
1168.4729 | 817.2442 | 297.1664 | 299.3393 | 309.5245
1169.4729 | 816.1223 | 297.992 | 299.6377 | 310.0642
1170.4729 | 815.236 | 298.1237 | 299.7139 | 310.4272
1171.4729 | 815.1619 | 297.9871 | 300.1377 | 310.6436
1172.4729 | 813.5234 | 298.2077 | 301.4491 | 311.5538
1173.4729 | 813.9788 | 298.9141 | 301.6895 | 312.1832
1174.4729 | 814.3821 | 300.2811 | 303.2126 | 313.5543
1175.4729 | 816.0591 | 300.0809 | 304.2332 | 313.7272
1176.4729 | 818.8968 | 300.8861 | 304.765 | 313.7181
1177.4729 | 818.3417 | 301.2894 | 305.238 | 314.2556
1178.4729 | 819.7454 | 301.5402 | 304.9521 | 314.2583
1179.4729 | 819.7074 | 302.1368 | 305.4029 | 314.9683
1180.4729 | 822.1951 | 302.0713 | 305.5 | 315.0785
1181.4729 | 823.5512 | 301.8423 | 305.2472 | 315.0627
1182.4729 | 821.3112 | 302.0974 | 305.7438 | 315.1656
1183.4729 | 818.4258 | 302.6323 | 306.6458 | 315.7462
1184.4729 | 819.4796 | 303.102 | 306.8832 | 316.0993
1185.4729 | 818.1136 | 303.5496 | 307.0205 | 316.0806
1186.4729 | 819.1697 | 304.1424 | 307.6236 | 316.5144
1187.4729 | 819.7572 | 304.2587 | 308.2536 | 316.2783
1188.4729 | 819.8935 | 304.1955 | 307.6761 | 315.8797
1189.4729 | 820.334 | 304.377 | 307.9935 | 316.3283
1190.4729 | 823.214 | 304.1719 | 308.2593 | 316.9705
1191.4729 | 825.2528 | 304.448 | 307.8312 | 316.7966
1192.4729 | 826.1427 | 304.6014 | 308.5924 | 317.6801
1193.4729 | 831.6878 | 305.7051 | 309.1718 | 318.8361
1194.4729 | 833.3356 | 305.8475 | 309.8241 | 319.6989
1195.4729 | 834.3196 | 306.5558 | 310.1224 | 320.507
1196.4729 | 833.5485 | 307.186 | 310.6009 | 321.0696
1197.4729 | 832.3653 | 307.4388 | 310.817 | 321.3695
1198.4729 | 831.7601 | 307.8244 | 311.4325 | 321.5221
1199.4729 | 832.3206 | 307.8035 | 311.4559 | 322.2284
1200.4729 | 833.4887 | 308.1953 | 311.1727 | 322.0168
1201.4729 | 833.2216 | 308.0048 | 311.3013 | 322.8056
1202.4729 | 830.4797 | 308.5806 | 311.2359 | 322.4373
1203.4729 | 829.8976 | 308.794 | 311.8955 | 322.3119
1204.4729 | 830.0351 | 308.9576 | 311.6771 | 322.0596
1205.4729 | 830.7997 | 308.8524 | 311.1455 | 321.6663
1206.4729 | 829.0392 | 308.4128 | 311.8201 | 321.4026
1207.4729 | 830.7465 | 308.0279 | 311.4769 | 321.248
1208.4729 | 830.5106 | 308.0639 | 311.3767 | 321.8049
1209.4729 | 830.9744 | 308.3799 | 312.1066 | 321.6006
1210.4729 | 829.5854 | 308.9944 | 312.3815 | 321.792
1211.4729 | 828.5634 | 309.5806 | 312.1716 | 321.8877
1212.4729 | 828.1157 | 309.6548 | 312.3055 | 322.1609
1213.4729 | 826.0751 | 309.339 | 312.5336 | 321.9724
1214.4729 | 824.2469 | 309.6497 | 312.8833 | 321.4589
1215.4729 | 823.0761 | 310.1515 | 312.8976 | 321.4129
1216.4729 | 822.8698 | 310.5083 | 313.0553 | 321.8523
1217.4729 | 823.5695 | 310.6839 | 312.892 | 322.203
1218.4729 | 824.0554 | 310.5935 | 313.1661 | 322.5598
1219.4729 | 825.6214 | 310.8552 | 314.1322 | 322.9569
1220.4729 | 825.6707 | 310.6964 | 314.1592 | 323.5497
1221.4729 | 826.5559 | 311.3274 | 314.7056 | 323.7553
1222.4729 | 824.6951 | 311.362 | 315.3191 | 324.1102
1223.4729 | 824.8375 | 311.9162 | 315.0245 | 323.9759
1224.4729 | 824.0088 | 312.1186 | 315.2632 | 324.3487
1225.4729 | 825.7848 | 312.4948 | 315.6726 | 325.8297
1226.4729 | 827.7077 | 313.0101 | 316.8458 | 326.2678
1227.4729 | 830.4635 | 313.4729 | 317.5873 | 326.6331
1228.4885 | 830.9546 | 314.1537 | 317.7595 | 326.7046
1229.4729 | 832.1306 | 314.8398 | 318.3548 | 326.7372
1230.4885 | 831.3984 | 315.3307 | 318.8983 | 327.4261
1231.4885 | 829.9755 | 315.6621 | 318.7974 | 327.3041
1232.4729 | 830.84 | 316.168 | 319.1726 | 327.1666
1233.4729 | 830.5605 | 316.6318 | 319.5986 | 327.4957
1234.4729 | 830.8723 | 316.3009 | 319.7975 | 328.2168
1235.4729 | 831.7268 | 316.0801 | 319.6013 | 328.552
1236.4729 | 832.2434 | 316.4286 | 319.9311 | 328.128
1237.4729 | 831.2285 | 316.7678 | 320.1233 | 327.7173
1238.4729 | 833.6865 | 316.7254 | 320.3399 | 327.7851
1239.4729 | 833.8308 | 317.2454 | 320.5766 | 328.9551
1240.4729 | 836.6627 | 318.0563 | 320.8023 | 328.6035
1241.4729 | 838.6838 | 318.5606 | 320.6672 | 328.2194
1242.4729 | 841.0896 | 318.6368 | 320.6689 | 328.3356
1243.4729 | 840.4394 | 318.7265 | 320.6151 | 328.9721
1244.4729 | 839.6327 | 319.0442 | 320.8721 | 329.5804
1245.4729 | 842.5667 | 319.4757 | 320.7097 | 329.1837
1246.4729 | 840.8367 | 319.8249 | 320.7297 | 329.0283
1247.4729 | 839.0964 | 319.733 | 320.6614 | 329.1039
1248.4729 | 836.8233 | 319.2568 | 320.5614 | 329.0783
1249.4729 | 833.234 | 318.9043 | 320.3583 | 329.4448
1250.4729 | 830.9521 | 318.7692 | 321.0703 | 329.3869
1251.4729 | 831.2125 | 319.0455 | 321.113 | 329.1596
1252.4729 | 830.0736 | 319.693 | 321.3961 | 330.1771
1253.4729 | 827.3768 | 320.0043 | 321.4784 | 330.3542
1254.4729 | 823.8652 | 320.0536 | 320.9819 | 329.9904
1255.4729 | 823.7827 | 320.303 | 321.3265 | 329.7921
1256.4729 | 820.6714 | 320.1735 | 321.1337 | 330.6324
1257.4729 | 815.8044 | 320.5672 | 321.1575 | 330.8082
1258.4729 | 816.0377 | 321.0267 | 321.7883 | 331.3753
1259.4729 | 816.2962 | 321.5502 | 322.2693 | 331.9619
1260.4729 | 817.6924 | 321.8996 | 322.7516 | 332.6386
1261.4729 | 817.3891 | 321.6454 | 322.8246 | 332.4431
1262.4729 | 817.8741 | 322.188 | 323.1979 | 333.5979
1263.4885 | 818.9011 | 322.5524 | 323.5518 | 332.7336
1264.4729 | 819.0495 | 323.0079 | 323.625 | 332.5369
1265.4729 | 817.7838 | 323.0992 | 323.8555 | 332.4719
1266.4729 | 817.5178 | 323.4511 | 324.5216 | 332.3668
1267.4729 | 817.3846 | 323.3878 | 324.7338 | 333.19
1268.4729 | 819.325 | 323.5394 | 324.6828 | 334.1559
1269.4729 | 819.5041 | 323.7507 | 324.646 | 334.2265
1270.4729 | 820.3623 | 323.9854 | 325.015 | 335.9599
1271.4729 | 818.5866 | 324.3587 | 324.8271 | 337.0009
1272.4729 | 820.8312 | 324.4124 | 324.5758 | 336.8163
1273.4729 | 822.6675 | 324.4661 | 324.2496 | 336.6177
1274.4729 | 823.1077 | 324.4506 | 324.6877 | 337.4463
1275.4729 | 824.4938 | 324.9815 | 325.0718 | 337.3075
1276.4729 | 828.198 | 325.3558 | 325.4286 | 337.7671
1277.4729 | 829.1293 | 326.0435 | 325.7529 | 337.2653
1278.4729 | 829.5602 | 326.0077 | 326.1806 | 338.0378
1279.4729 | 827.6382 | 325.8397 | 326.0997 | 338.228
1280.4729 | 822.5447 | 325.7858 | 326.2536 | 338.4262
1281.4729 | 818.074 | 326.1709 | 326.1891 | 338.2966
1282.4729 | 816.4885 | 326.1744 | 326.1201 | 338.1263
1283.4729 | 815.1353 | 326.1426 | 326.3683 | 338.3922
1284.4729 | 817.9734 | 326.7816 | 326.776 | 338.6011
1285.4729 | 821.9507 | 326.9137 | 327.6513 | 338.4132
1286.4729 | 821.2091 | 327.1636 | 328.5516 | 339.9764
1287.4729 | 823.5168 | 327.0032 | 329.1125 | 340.9141
1288.4729 | 825.0671 | 327.3748 | 329.0593 | 340.5262
1289.4729 | 824.8851 | 328.1198 | 329.0705 | 341.0568
1290.4729 | 826.223 | 328.4973 | 329.483 | 341.1472
1291.4729 | 826.2464 | 329.3334 | 329.6312 | 340.9779
1292.4729 | 826.0706 | 329.1553 | 329.3278 | 340.919
1293.4729 | 826.2366 | 329.3608 | 329.5035 | 340.5838
1294.4729 | 826.9915 | 328.9535 | 329.5297 | 340.7738
1295.4729 | 827.4946 | 328.8018 | 329.3063 | 340.9694
1296.4729 | 827.4344 | 328.9289 | 329.1805 | 340.7412
1297.4729 | 832.3283 | 329.0425 | 329.5415 | 340.7796
1298.4729 | 833.1236 | 329.1219 | 329.7695 | 340.8105
1299.4729 | 830.4094 | 329.1161 | 329.2125 | 340.3643
1300.4729 | 829.483 | 328.8703 | 329.9617 | 340.3822
1301.4729 | 829.055 | 329.4665 | 329.8372 | 340.2309
1302.4729 | 826.8878 | 329.2447 | 330.2821 | 340.9355
1303.4729 | 825.1126 | 329.3481 | 330.1223 | 340.6186
1304.4729 | 822.8303 | 329.9262 | 329.7447 | 340.7322
1305.4729 | 821.1248 | 330.1795 | 329.7686 | 340.92
1306.4729 | 820.1931 | 330.2398 | 330.4417 | 340.9984
1307.4729 | 817.8589 | 330.6709 | 330.378 | 340.9349
1308.4729 | 818.9356 | 330.7861 | 331.0133 | 341.4213
1309.4729 | 818.7283 | 330.7601 | 331.285 | 341.744
1310.4729 | 818.3994 | 331.2518 | 331.6652 | 341.8087
1311.4729 | 819.3176 | 332.1271 | 332.5018 | 342.0678
1312.4729 | 816.4914 | 332.2145 | 332.7363 | 342.3343
1313.4729 | 816.5412 | 332.1353 | 333.6975 | 343.082
1314.4729 | 816.1534 | 332.4244 | 333.964 | 343.1968
1315.4729 | 815.5113 | 332.7893 | 334.0113 | 343.3051
1316.4729 | 814.4268 | 332.6671 | 333.7146 | 343.6053
1317.4729 | 816.1822 | 332.5304 | 333.2286 | 343.1621
1318.4729 | 814.602 | 332.3007 | 332.9313 | 342.0685
1319.4729 | 813.7365 | 332.2135 | 332.4158 | 342.2135
1320.4729 | 812.3337 | 332.7066 | 332.5115 | 342.9534
1321.4729 | 810.295 | 332.5194 | 333.0276 | 343.7602
1322.4729 | 809.7079 | 332.3457 | 332.8497 | 344.3488
1323.4729 | 808.4153 | 332.0445 | 332.9149 | 344.5421
1324.4729 | 809.2787 | 332.462 | 332.8602 | 344.9233
1325.4729 | 809.7477 | 332.2839 | 333.2045 | 344.7202
1326.4729 | 809.2384 | 331.8899 | 332.8602 | 344.3144
1327.4729 | 808.103 | 331.8129 | 332.2559 | 344.6505
1328.4729 | 810.3858 | 332.0954 | 332.1651 | 344.7631
1329.4729 | 809.3555 | 331.6374 | 332.4439 | 344.8599
1330.4729 | 807.5927 | 331.7301 | 332.9011 | 345.5683
1331.4729 | 807.8454 | 331.7067 | 332.8433 | 345.9158
1332.4729 | 807.9062 | 331.911 | 333.2339 | 346.4038
1333.4729 | 806.2584 | 331.9364 | 334.5562 | 346.4773
1334.4729 | 806.2325 | 332.042 | 334.824 | 345.8715
1335.4729 | 808.8598 | 332.5081 | 334.8021 | 346.2859
1336.4729 | 807.2725 | 332.6664 | 334.8042 | 346.4029
1337.4729 | 806.7433 | 332.3993 | 334.9396 | 345.9912
1338.4729 | 807.913 | 332.516 | 334.533 | 345.4323
1339.4729 | 808.0503 | 332.6299 | 335.3949 | 345.5939
1340.4729 | 808.3128 | 332.8381 | 335.4282 | 345.1044
1341.4729 | 805.5204 | 332.3068 | 335.2951 | 344.5701
1342.4729 | 805.4949 | 332.617 | 335.1172 | 345.0165
1343.4729 | 806.2666 | 332.8441 | 335.4342 | 345.9383
1344.4729 | 806.1451 | 333.1344 | 335.7761 | 347.0235
1345.4729 | 804.4972 | 333.2505 | 336.5655 | 346.9802
1346.4729 | 805.6992 | 333.5863 | 337.0904 | 347.4017
1347.4729 | 804.2994 | 333.7486 | 337.2262 | 347.9656
1348.4729 | 802.8397 | 333.9439 | 337.1573 | 348.1911
1349.4729 | 804.2691 | 334.3645 | 337.4569 | 348.7611
1350.4729 | 806.3105 | 334.187 | 337.6971 | 348.6992
1351.4729 | 805.9155 | 334.0498 | 338.0207 | 348.8914
1352.4729 | 806.4736 | 333.5214 | 337.5909 | 348.2577
1353.4729 | 808.0758 | 333.9653 | 337.2838 | 347.8664
1354.4729 | 808.7986 | 334.5566 | 338.0057 | 348.3692
1355.4729 | 811.4082 | 334.4239 | 337.981 | 348.0618
1356.4885 | 813.0427 | 334.4457 | 338.1889 | 348.2672
1357.4885 | 816.8189 | 334.4737 | 338.0435 | 348.0796
1358.4729 | 817.318 | 334.4677 | 337.9381 | 347.952
1359.4729 | 812.5602 | 334.5567 | 337.4669 | 347.1505
1360.4729 | 814.5516 | 334.4885 | 337.2245 | 347.148
1361.4885 | 814.2029 | 334.5266 | 337.7314 | 346.7046
1362.4729 | 814.6796 | 334.3263 | 338.1211 | 347.1592
1363.4729 | 814.104 | 333.7645 | 338.0721 | 347.2861
1364.4729 | 811.3599 | 333.8208 | 338.3014 | 347.6043
1365.4729 | 809.1442 | 334.4286 | 338.8561 | 347.992
1366.4729 | 808.9101 | 334.0586 | 338.7282 | 347.332
1367.4729 | 807.692 | 334.121 | 338.7823 | 346.9315
1368.4729 | 807.4348 | 333.9496 | 338.8904 | 347.282
1369.4729 | 805.3811 | 333.8243 | 339.1791 | 347.3615
1370.4729 | 803.8373 | 333.6565 | 339.6283 | 348.1196
1371.4729 | 804.7346 | 334.4564 | 340.0761 | 348.198
1372.4729 | 805.965 | 334.4457 | 340.8204 | 349.1979
1373.4729 | 806.1228 | 334.8964 | 340.6933 | 349.9719
1374.4729 | 804.0755 | 334.8356 | 341.0299 | 349.899
1375.4729 | 804.9796 | 334.8288 | 340.8928 | 349.6999
1376.4729 | 803.844 | 334.3704 | 340.6021 | 350.3206
1377.4729 | 805.3332 | 334.5939 | 340.6082 | 349.5833
1378.4729 | 809.4915 | 334.2651 | 340.1672 | 348.9791
1379.4729 | 811.4136 | 333.9968 | 339.9734 | 348.5763
1380.4729 | 808.8076 | 333.8499 | 340.1497 | 348.6822
1381.4729 | 809.7998 | 334.0274 | 339.7873 | 348.5811
1382.4729 | 810.9695 | 334.1645 | 339.6512 | 348.7374
1383.4729 | 810.601 | 334.308 | 339.9728 | 348.9121
1384.4729 | 808.9047 | 335.0757 | 340.4523 | 348.9603
1385.4729 | 806.1656 | 335.2564 | 340.5723 | 348.9727
1386.4729 | 804.4133 | 335.3219 | 340.3221 | 348.2226
1387.4729 | 801.0916 | 335.5641 | 339.7971 | 347.8525
1388.4729 | 799.7187 | 335.1849 | 339.6898 | 347.8162
1389.4729 | 796.8153 | 335.2412 | 339.6375 | 347.7723
1390.4729 | 798.2587 | 334.9799 | 339.7721 | 347.8552
1391.4729 | 798.0854 | 335.4304 | 340.1115 | 347.9891
1392.4729 | 795.405 | 335.4779 | 340.0855 | 348.4483
1393.4729 | 796.1055 | 335.6905 | 339.9425 | 347.9838
1394.4729 | 792.7822 | 335.8933 | 339.2776 | 348.1114
1395.4729 | 794.8327 | 336.2291 | 339.8735 | 348.6751
1396.4729 | 792.8205 | 336.4909 | 339.6155 | 349.8477
1397.4729 | 790.9175 | 336.4102 | 339.6575 | 349.8238
1398.4729 | 791.8723 | 336.519 | 339.755 | 349.8046
1399.4729 | 792.014 | 336.2663 | 339.8961 | 349.5488
1400.4729 | 792.2276 | 336.7097 | 340.3126 | 350.3022
1401.4729 | 792.1156 | 336.5854 | 340.0749 | 350.7891
1402.4729 | 789.6693 | 336.9921 | 339.7872 | 350.559
1403.4729 | 789.8697 | 337.1951 | 339.9042 | 349.6643
1404.4729 | 789.906 | 337.4496 | 339.8078 | 348.9662
1405.4729 | 790.0696 | 337.0605 | 340.0931 | 348.7266
1406.4729 | 791.5497 | 336.7273 | 339.7139 | 348.7329
1407.4729 | 793.8091 | 336.1651 | 338.9892 | 348.2665
1408.4729 | 792.9192 | 335.9416 | 339.3263 | 347.6077
1409.4729 | 794.0377 | 335.3103 | 338.645 | 346.9667
1410.4729 | 793.439 | 335.2496 | 338.2737 | 346.6338
1411.4729 | 793.9843 | 334.9786 | 338.1044 | 345.6997
1412.4729 | 794.3108 | 334.7055 | 337.5314 | 345.4015
1413.4729 | 792.9706 | 334.6472 | 337.4001 | 344.7394
1414.4729 | 791.3403 | 334.322 | 337.1749 | 344.483
1415.4729 | 790.0535 | 333.6409 | 336.555 | 344.0901
1416.4729 | 790.2524 | 333.4595 | 336.2499 | 343.5387
1417.4729 | 790.1181 | 333.1948 | 335.526 | 343.2923
1418.4729 | 789.4235 | 332.66 | 334.9386 | 342.291
1419.4729 | 791.1312 | 332.383 | 334.9917 | 342.4161
1420.4729 | 790.9489 | 331.9727 | 334.6944 | 342.276
1421.4729 | 790.7246 | 331.9403 | 334.8216 | 342.5912
1422.4729 | 792.8466 | 331.6514 | 335.0239 | 342.1604
1423.4729 | 794.4202 | 331.3149 | 334.8101 | 342.1693
1424.4729 | 799.8261 | 331.0544 | 334.5446 | 342.1598
1425.4729 | 798.2572 | 330.8444 | 334.4952 | 342.108
1426.4729 | 799.2386 | 331.253 | 334.5993 | 341.9451
1427.4729 | 799.8103 | 331.4071 | 334.7687 | 341.888
1428.4729 | 798.8169 | 332.1317 | 335.0678 | 342.591
1429.4729 | 799.4766 | 332.4306 | 335.2424 | 342.5612
1430.4729 | 798.2004 | 332.1096 | 334.4824 | 342.3817
1431.4729 | 796.1728 | 332.3943 | 334.1108 | 341.9019
1432.4729 | 794.5213 | 332.3524 | 334.2191 | 341.793
1433.4729 | 792.9881 | 332.2179 | 334.0995 | 341.5178
1434.4729 | 791.9115 | 332.0273 | 333.6021 | 341.7959
1435.4729 | 791.9765 | 331.5266 | 333.1168 | 341.3831
1436.4729 | 793.2312 | 331.7279 | 333.0045 | 341.1712
1437.4729 | 791.3559 | 331.9261 | 332.9272 | 341.1498
1438.4729 | 792.4822 | 331.5969 | 333.6022 | 341.2558
1439.4729 | 793.1186 | 331.3337 | 333.4595 | 340.9978
1440.4729 | 792.511 | 331.0897 | 333.4678 | 341.1357
1441.4729 | 794.8993 | 330.7674 | 333.0357 | 341.2584
1442.4729 | 796.0719 | 330.4466 | 332.4785 | 341.0301
1443.4729 | 798.9959 | 330.712 | 332.3973 | 341.4344
1444.4729 | 799.5378 | 330.5878 | 332.5767 | 341.293
1445.4729 | 799.4126 | 330.588 | 331.9859 | 341.1888
1446.4729 | 800.6041 | 330.6652 | 332.3622 | 341.4045
1447.4729 | 798.2444 | 330.4388 | 331.8371 | 340.7809
1448.4729 | 795.9602 | 330.2419 | 331.8993 | 340.8813
1449.4729 | 795.5135 | 330.0924 | 331.6341 | 340.9053
1450.4729 | 797.7353 | 330.1545 | 331.9133 | 340.8449
1451.4729 | 798.212 | 329.9608 | 332.1656 | 340.8221
1452.4729 | 800.4847 | 330.0265 | 332.144 | 340.5494
1453.4729 | 799.4254 | 329.8598 | 332.1196 | 340.5029
1454.4729 | 799.831 | 329.5189 | 331.7505 | 340.3037
1455.4729 | 799.0641 | 329.3571 | 331.5182 | 339.9268
1456.4729 | 797.6085 | 329.1114 | 331.2918 | 339.2307
1457.4729 | 796.2572 | 329.0862 | 331.0578 | 339.295
1458.4729 | 793.7829 | 328.9045 | 330.7312 | 339.5694
1459.4729 | 793.2017 | 328.7774 | 330.317 | 338.7906
1460.4729 | 792.43 | 328.5489 | 330.2523 | 338.4684
1461.4729 | 791.6817 | 328.2264 | 330.611 | 338.9959
1462.4729 | 790.0376 | 328.2187 | 330.4475 | 338.9023
1463.4729 | 788.615 | 328.2017 | 330.2054 | 338.9581
1464.4729 | 788.5003 | 328.6368 | 330.8457 | 339.414
1465.4729 | 787.2837 | 329.2191 | 330.8996 | 339.5762
1466.4729 | 785.4411 | 328.6966 | 330.4494 | 339.3633
1467.4729 | 784.2772 | 328.7205 | 330.3993 | 339.668
1468.4729 | 781.5521 | 328.6122 | 330.2256 | 339.2534
1469.4729 | 782.4095 | 328.644 | 329.9473 | 339.0343
1470.4729 | 783.3924 | 328.5325 | 329.7379 | 338.9618
1471.4729 | 783.8709 | 328.0767 | 329.5347 | 339.1614
1472.4729 | 782.2504 | 328.1927 | 329.5981 | 339.1333
1473.4729 | 782.8918 | 327.6835 | 329.6768 | 339.643
1474.4729 | 782.5619 | 327.1 | 329.339 | 339.1061
1475.4729 | 779.212 | 326.7778 | 328.7725 | 338.8666
1476.4729 | 777.0146 | 326.7971 | 328.9326 | 338.856
1477.4729 | 771.354 | 327.2299 | 329.0123 | 339.2467
1478.4729 | 769.3263 | 327.1273 | 329.3412 | 339.4397
1479.4729 | 772.092 | 327.2406 | 329.3392 | 339.3325
1480.4729 | 777.2034 | 327.0922 | 329.4594 | 339.5555
1481.4729 | 781.7028 | 327.243 | 329.3981 | 339.6422
1482.4729 | 786.0081 | 328.0035 | 329.3625 | 339.3478
1483.4729 | 785.1349 | 328.266 | 329.1764 | 339.2436
1484.4729 | 786.1802 | 328.3777 | 329.5069 | 339.7011
1485.4729 | 789.6431 | 327.9244 | 329.3804 | 339.783
1486.4729 | 791.2669 | 327.8865 | 329.0899 | 339.8074
1487.4729 | 792.3333 | 327.4898 | 329.1368 | 339.6409
1488.4729 | 792.7123 | 327.3983 | 329.8107 | 340.3208
1489.4729 | 795.9573 | 327.9956 | 329.9967 | 340.7858
1490.4729 | 792.6719 | 328.1307 | 330.0831 | 340.893
1491.4729 | 789.8731 | 328.0607 | 330.2832 | 341.2209
1492.4729 | 790.9544 | 328.0928 | 330.2431 | 341.0209
1493.4729 | 792.8045 | 328.0969 | 330.1513 | 340.9676
1494.4729 | 785.9089 | 328.5534 | 330.4452 | 340.5506
1495.4729 | 783.3826 | 328.3846 | 330.8058 | 341.032
1496.4729 | 781.2575 | 328.6607 | 330.9988 | 340.8735
1497.4729 | 781.162 | 328.8569 | 331.4045 | 341.5041
1498.4729 | 781.8513 | 328.4971 | 330.9835 | 341.1999
1499.4729 | 778.7749 | 328.9521 | 330.7189 | 341.0096
1500.4729 | 783.6365 | 328.7207 | 330.6729 | 340.7558
1501.4729 | 785.5962 | 328.6341 | 330.6888 | 340.7031
1502.4729 | 784.0238 | 328.4567 | 330.9794 | 340.8067
1503.4729 | 784.9735 | 328.7765 | 330.609 | 340.2804
1504.4729 | 782.0434 | 329.2751 | 330.427 | 340.4602
1505.4729 | 777.7291 | 327.0067 | 330.7911 | 339.0803
1506.4729 | 773.4322 | 328.8542 | 329.8787 | 339.9164
1507.4729 | 773.5909 | 328.8083 | 329.9418 | 339.8578
1508.4729 | 776.7369 | 328.9434 | 329.7598 | 339.9292
1509.4729 | 781.2766 | 328.7332 | 329.9448 | 339.6381
1510.4729 | 785.1583 | 328.4817 | 329.5585 | 339.3673
1511.4729 | 787.908 | 328.8454 | 329.3492 | 339.4975
1512.4729 | 790.5869 | 328.831 | 329.2142 | 339.7361
1513.4729 | 789.4744 | 328.5248 | 329.8114 | 339.8316
1514.4729 | 788.2723 | 328.7037 | 330.0368 | 339.3467
1515.4729 | 787.1791 | 328.2875 | 329.8109 | 339.3384
1516.4729 | 787.542 | 328.2363 | 329.6003 | 339.319
1517.4729 | 784.0087 | 328.2082 | 329.1522 | 339.9172
1518.4729 | 776.8599 | 328.3189 | 329.2318 | 340.3028
1519.4729 | 770.0732 | 328.5105 | 328.9879 | 340.1632
1520.4729 | 765.5925 | 328.5447 | 329.7726 | 340.453
1521.4729 | 760.8864 | 328.7177 | 330.5301 | 340.7154
1522.4729 | 761.0091 | 328.8902 | 330.8498 | 341.0783
1523.4729 | 766.1399 | 329.4793 | 331.6396 | 341.652
1524.4729 | 772.8108 | 330.0305 | 332.1548 | 342.3399
1525.4729 | 775.5282 | 330.4699 | 332.4182 | 343.0562
1526.4729 | 780.2804 | 330.9923 | 332.4784 | 343.1583
1527.4729 | 780.5567 | 331.6467 | 332.7956 | 343.2268
1528.4729 | 775.0427 | 332.3041 | 333.1674 | 343.8663
1529.4729 | 776.3724 | 332.1808 | 333.2406 | 343.8186
1530.4729 | 771.0219 | 332.0995 | 333.0544 | 343.784
1531.4729 | 763.4601 | 332.0746 | 332.8613 | 343.6714
1532.4729 | 761.8891 | 332.4245 | 333.2313 | 343.7656
1533.4729 | 762.8459 | 332.8351 | 334.317 | 344.7514
1534.4729 | 766.5264 | 332.8484 | 334.8127 | 345.1188
1535.4729 | 773.9909 | 332.8852 | 335.2761 | 345.5969
1536.4729 | 775.0293 | 333.6526 | 335.7854 | 346.1169
1537.4729 | 777.5742 | 333.89 | 336.1823 | 346.328
1538.4729 | 785.8666 | 334.0098 | 336.0155 | 346.1724
1539.4729 | 794.2124 | 334.4724 | 335.692 | 346.5661
1540.4729 | 793.5909 | 334.7525 | 335.5258 | 347.0716
1541.4729 | 788.6768 | 334.3137 | 336.2223 | 347.6331
1542.4729 | 785.4362 | 333.9937 | 336.4308 | 347.9163
1543.4729 | 780.5312 | 334.1952 | 336.4832 | 347.7467
1544.4729 | 779.2195 | 334.8802 | 336.4166 | 348.3887
1545.4729 | 779.6784 | 334.6661 | 336.819 | 348.3362
1546.4729 | 780.2572 | 334.8586 | 336.7497 | 347.8465
1547.4729 | 777.8812 | 335.1191 | 337.1893 | 347.9945
1548.4729 | 776.7182 | 335.2635 | 337.4044 | 347.6227
1549.4729 | 776.6563 | 335.7297 | 337.8575 | 347.8112
1550.4729 | 775.5157 | 335.6813 | 338.0941 | 348.3175
1551.4729 | 769.7946 | 335.9327 | 338.1244 | 348.2887
1552.4729 | 770.6439 | 336.4012 | 338.336 | 348.0497
1553.4729 | 776.6503 | 337.0736 | 339.2497 | 348.9676
1554.4729 | 784.1115 | 337.2792 | 339.1907 | 348.9778
1555.4729 | 787.2727 | 337.6186 | 339.4009 | 348.8824
1556.4729 | 788.8528 | 337.776 | 339.438 | 348.6167
1557.4729 | 784.3901 | 337.3339 | 339.3304 | 348.2038
1558.4729 | 785.1213 | 337.2529 | 339.2681 | 348.1302
1559.4729 | 788.0116 | 338.2905 | 339.1357 | 348.1703
1560.4729 | 790.6978 | 338.5184 | 338.9301 | 348.1026
1561.4729 | 788.56 | 338.5586 | 339.1973 | 348.4322
1562.4729 | 789.0065 | 338.9145 | 339.5743 | 348.5759
1563.4729 | 791.486 | 339.0459 | 339.7524 | 349.2483
1564.4729 | 794.2291 | 338.9638 | 340.1402 | 349.3968
1565.4729 | 792.8379 | 338.6048 | 340.0563 | 349.4602
1566.4729 | 790.1175 | 338.2795 | 339.7811 | 349.2098
1567.4729 | 790.4848 | 338.0317 | 340.1659 | 349.7184
1568.4729 | 792.3714 | 338.0939 | 339.8934 | 350.0557
1569.4729 | 790.7115 | 338.1147 | 339.9381 | 349.8638
1570.4729 | 780.8049 | 338.0339 | 340.0277 | 349.5099
1571.4729 | 778.6014 | 338.1157 | 340.0413 | 349.4365
1572.4729 | 773.2739 | 338.0995 | 340.4192 | 349.7631
1573.4729 | 776.1002 | 338.2369 | 340.4822 | 349.7958
1574.4729 | 788.2317 | 338.3088 | 340.6536 | 350.3638
1575.4729 | 804.2814 | 338.417 | 341.0876 | 351.1039
1576.4729 | 809.1158 | 338.735 | 341.3896 | 351.2839
1577.4729 | 806.6519 | 339.1556 | 341.778 | 351.186
1578.4729 | 807.2885 | 338.94 | 342.0788 | 351.3437
1579.4729 | 809.4158 | 339.1942 | 341.8004 | 351.5416
1580.4729 | 812.3944 | 339.4762 | 341.5463 | 351.5082
1581.4729 | 814.2961 | 339.2565 | 341.0341 | 351.2103
1582.4729 | 814.0018 | 339.4074 | 341.4192 | 351.1441
1583.4729 | 818.2912 | 339.5823 | 341.3157 | 351.0242
1584.4729 | 817.4584 | 339.6239 | 341.4457 | 351.0658
1585.4729 | 816.8981 | 339.7624 | 340.9731 | 350.8137
1586.4729 | 817.4996 | 339.792 | 341.1638 | 350.6038
1587.4729 | 818.7113 | 339.819 | 341.3871 | 350.9691
1588.4729 | 819.8422 | 339.9388 | 341.4225 | 351.1665
1589.4729 | 818.7015 | 339.8024 | 341.7456 | 351.2268
1590.4729 | 818.3378 | 340.1151 | 341.7713 | 351.3938
1591.4729 | 815.9133 | 340.1477 | 341.5517 | 351.1183
1592.4729 | 816.046 | 340.0151 | 341.3776 | 350.7984
1593.4729 | 819.6465 | 340.15 | 341.8623 | 351.314
1594.4729 | 823.4777 | 340.1016 | 342.0195 | 351.3737
1595.4729 | 820.0288 | 340.4325 | 342.5301 | 351.7434
1596.4729 | 823.0949 | 340.4384 | 342.8498 | 351.6462
1597.4729 | 829.3 | 340.8954 | 342.7957 | 352.2355
1598.4729 | 831.2428 | 341.2259 | 342.8761 | 352.7208
1599.4729 | 834.0821 | 341.0532 | 343.3987 | 353.3504
1600.4729 | 837.9813 | 341.0791 | 343.5766 | 353.2206
1601.4885 | 841.0568 | 340.8381 | 343.5121 | 353.3433
1602.4729 | 843.7269 | 340.6137 | 343.4735 | 352.9437
1603.4729 | 847.3119 | 340.3901 | 343.459 | 352.9176
1604.4729 | 845.6215 | 340.5451 | 343.5937 | 352.9155
1605.4729 | 845.7088 | 340.6015 | 343.589 | 352.9609
1606.4729 | 846.9022 | 340.6397 | 343.6593 | 353.1281
1607.4729 | 842.2809 | 341.1169 | 343.9957 | 353.3691
1608.4729 | 842.7404 | 341.0896 | 344.8282 | 353.77
1609.4729 | 843.173 | 340.829 | 344.3751 | 353.551
1610.4729 | 839.9451 | 340.7831 | 344.2837 | 353.28
1611.4729 | 833.1848 | 341.2506 | 344.2187 | 353.074
1612.4729 | 827.2405 | 341.0504 | 344.6226 | 353.2814
1613.4729 | 826.9627 | 341.2206 | 344.866 | 353.5027
1614.4729 | 830.4117 | 341.4839 | 344.8603 | 353.6412
1615.4729 | 839.8645 | 341.8116 | 345.3774 | 353.9476
1616.4729 | 843.9015 | 342.2951 | 345.3414 | 353.8611
1617.4729 | 847.6011 | 342.4986 | 344.8023 | 353.4336
1618.4729 | 848.4758 | 343.0435 | 344.9902 | 353.1187
1619.4729 | 847.9356 | 343.0623 | 344.7247 | 354.1384
1620.4729 | 849.8136 | 343.1429 | 344.8803 | 354.1847
1621.4729 | 853.5705 | 343.0634 | 344.6237 | 353.8465
1622.4729 | 853.1955 | 343.1347 | 344.4407 | 353.9916
1623.4729 | 851.4973 | 342.8574 | 344.546 | 353.9619
1624.4729 | 852.1381 | 342.6593 | 344.3041 | 354.0014
1625.4729 | 851.7792 | 342.6945 | 344.2352 | 353.6187
1626.4729 | 849.7045 | 342.4264 | 343.8886 | 353.9947
1627.4729 | 852.1926 | 342.0687 | 343.3493 | 353.9121
1628.4729 | 856.5191 | 341.9945 | 343.086 | 354.0448
1629.4729 | 856.5526 | 341.6051 | 342.7421 | 353.6408
1630.4729 | 854.643 | 341.4858 | 342.3009 | 353.5432
1631.4729 | 846.5061 | 341.0515 | 342.0865 | 352.982
1632.4729 | 848.4587 | 340.9805 | 342.2865 | 352.9289
1633.4729 | 845.3022 | 340.864 | 342.3104 | 352.5585
1634.4729 | 843.8162 | 340.8729 | 342.1548 | 352.402
1635.4729 | 850.6404 | 340.5477 | 342.3396 | 352.098
1636.4729 | 857.46 | 340.1245 | 342.0486 | 351.966
1637.4729 | 852.6743 | 339.9958 | 341.6383 | 352.0556
1638.4729 | 849.6463 | 339.4697 | 341.6994 | 352.0724
1639.4729 | 864.8161 | 339.3296 | 341.3579 | 352.0473
1640.4729 | 864.3811 | 339.0957 | 341.1872 | 352.0051
1641.4729 | 861.8966 | 339.1329 | 341.4676 | 352.0067
1642.4729 | 855.0015 | 338.9889 | 341.4411 | 352.1004
1643.4729 | 854.9006 | 338.8594 | 341.1683 | 351.9735
1644.4729 | 859.4959 | 339.036 | 340.9803 | 351.5525
1645.4729 | 859.2124 | 339.2353 | 341.0558 | 351.3471
1646.4729 | 855.3735 | 339.4974 | 341.4043 | 351.4029
1647.4729 | 845.6576 | 339.3779 | 341.7117 | 351.3791
1648.4729 | 843.3418 | 339.6005 | 341.7456 | 351.1685
1649.4729 | 841.0179 | 339.9201 | 342.1709 | 351.0735
1650.4729 | 840.5333 | 340.5379 | 342.7691 | 351.4712
1651.4729 | 842.4702 | 340.5755 | 342.9355 | 352.1371
1652.4729 | 845.9274 | 340.9964 | 342.9931 | 352.4476
1653.4729 | 854.2496 | 341.5014 | 343.0509 | 352.3986
1654.4729 | 858.2468 | 341.3689 | 342.6526 | 352.3856
1655.4729 | 853.362 | 341.5658 | 342.348 | 352.3878
1656.4729 | 855.2854 | 342.0361 | 342.6297 | 352.7964
1657.4729 | 848.2063 | 341.8657 | 342.6259 | 352.5941
1658.4729 | 836.7212 | 341.9457 | 342.5803 | 353.0957
1659.4729 | 834.0015 | 342.1621 | 343.1049 | 353.0468
1660.4729 | 833.7763 | 341.8251 | 343.1773 | 353.4292
1661.4729 | 825.9744 | 341.5595 | 342.908 | 353.5013
1662.4729 | 823.6311 | 341.688 | 342.8599 | 353.9301
1663.4729 | 828.271 | 341.6753 | 342.9016 | 354.0123
1664.4729 | 833.4835 | 342.0945 | 343.8465 | 354.5266
1665.4885 | 834.4124 | 342.0798 | 344.78 | 355.8361
1666.4729 | 838.3412 | 341.8457 | 344.5588 | 355.7529
1667.4729 | 829.0631 | 341.6754 | 344.452 | 355.623
1668.4729 | 839.5816 | 341.3072 | 344.418 | 355.2536
1669.4729 | 845.4393 | 341.3082 | 344.3703 | 355.2128
1670.4729 | 843.3336 | 341.2388 | 344.4251 | 355.235
1671.4729 | 837.8379 | 341.5222 | 344.4087 | 355.3892
1672.4729 | 841.5292 | 341.7231 | 344.2481 | 355.3667
1673.4729 | 841.0788 | 341.8992 | 344.4583 | 355.5551
1674.4729 | 835.734 | 341.98 | 344.3032 | 355.323
1675.4729 | 838.6398 | 342.1666 | 344.1667 | 355.2581
1676.4729 | 823.6026 | 342.1347 | 344.1739 | 355.334
1677.4729 | 809.8138 | 342.3036 | 344.9248 | 356.2153
1678.4729 | 812.6325 | 342.7163 | 345.4085 | 356.6495
1679.4729 | 818.2212 | 343.22 | 345.7254 | 356.5552
1680.4729 | 822.6241 | 344.1114 | 346.4712 | 357.6413
1681.4729 | 823.5133 | 344.8359 | 347.6523 | 357.8271
1682.4729 | 831.7499 | 345.7416 | 348.0546 | 357.6899
1683.4729 | 831.0197 | 345.774 | 348.0032 | 357.4117
1684.4729 | 830.9497 | 346.0302 | 348.2369 | 357.8843
1685.4729 | 832.9026 | 346.6033 | 348.8593 | 357.9854
1686.4729 | 837.9344 | 347.3698 | 349.1074 | 358.9893
1687.4729 | 843.1397 | 347.464 | 349.5034 | 359.1207
1688.4729 | 843.3238 | 347.5103 | 349.9328 | 359.5593
1689.4729 | 848.9448 | 347.765 | 350.03 | 359.1574
1690.4729 | 845.4671 | 347.7529 | 349.5487 | 359.249
1691.4729 | 846.4331 | 347.739 | 349.3671 | 359.1453
1692.4729 | 843.2678 | 347.5457 | 349.4619 | 359.1471
1693.4729 | 835.9728 | 347.3103 | 349.5567 | 358.9503
1694.4729 | 839.5617 | 347.2822 | 349.126 | 359.4788
1695.4885 | 847.3517 | 347.3698 | 348.9005 | 359.615
1696.4729 | 856.4266 | 346.9773 | 348.9666 | 360.0998
1697.4729 | 864.376 | 347.5356 | 349.0584 | 359.9298
1698.4729 | 869.9726 | 347.5977 | 348.9584 | 359.964
1699.4729 | 869.0943 | 348.206 | 348.8408 | 360.0744
1700.4729 | 863.3391 | 348.1974 | 349.0196 | 360.4945
1701.4729 | 860.0327 | 348.1754 | 349.2332 | 360.6326
1702.4729 | 849.2392 | 348.2405 | 349.2851 | 360.7829
1703.4729 | 845.0101 | 348.4003 | 349.109 | 360.8299
1704.4729 | 840.294 | 348.4897 | 349.7691 | 361.0896
1705.4729 | 841.8945 | 348.6329 | 349.6798 | 361.3858
1706.4729 | 839.4921 | 349.6051 | 349.9954 | 361.3209
1707.4729 | 833.4936 | 349.7719 | 350.2795 | 361.6068
1708.4729 | 833.8966 | 349.624 | 350.3862 | 361.3779
1709.4729 | 832.7632 | 349.7277 | 350.719 | 361.6107
1710.4729 | 826.2118 | 349.7585 | 350.7009 | 361.7557
1711.4729 | 830.3172 | 349.9822 | 350.6471 | 361.2395
1712.4729 | 830.6518 | 350.0825 | 351.3372 | 361.3723
1713.4729 | 832.9766 | 350.1669 | 351.5406 | 362.3328
1714.4729 | 837.3045 | 350.2431 | 351.305 | 362.1175
1715.4729 | 839.8438 | 350.6937 | 351.3883 | 362.7197
1716.4729 | 845.4308 | 350.918 | 351.8947 | 362.7004
1717.4729 | 849.9594 | 351.0317 | 352.0133 | 363.148
1718.4729 | 841.8943 | 351.647 | 351.9286 | 363.1591
1719.4729 | 833.4233 | 351.8524 | 352.2425 | 363.7003
1720.4729 | 837.3491 | 351.9033 | 352.2467 | 363.8349
1721.4729 | 840.131 | 351.8884 | 352.5022 | 363.6792
1722.4729 | 827.689 | 351.4955 | 352.2262 | 363.6063
1723.4729 | 827.8002 | 352.0655 | 352.3902 | 363.3878
1724.4729 | 828.6267 | 352.0172 | 352.1785 | 363.0592
1725.4729 | 832.9494 | 352.0661 | 351.9336 | 362.7667
1726.4729 | 833.6945 | 352.1662 | 351.9966 | 363.4064
1727.4729 | 836.388 | 352.1489 | 352.2067 | 363.2352
1728.4729 | 841.6027 | 351.7516 | 352.2309 | 363.7076
1729.4729 | 848.8405 | 351.8171 | 352.5221 | 363.439
1730.4729 | 846.8729 | 352.1002 | 352.4319 | 362.9739
1731.4729 | 843.0658 | 352.8453 | 352.4441 | 364.0292
1732.4729 | 845.8312 | 352.5932 | 352.7655 | 364.2767
1733.4729 | 849.0235 | 352.3551 | 352.7391 | 364.4273
1734.4729 | 851.6916 | 352.287 | 353.094 | 364.5781
1735.4729 | 850.4899 | 352.2586 | 353.7224 | 365.083
1736.4729 | 847.653 | 352.4446 | 354.0667 | 365.0043
1737.4729 | 848.0054 | 352.665 | 354.0647 | 365.0261
1738.4729 | 853.3052 | 353.1293 | 353.7223 | 364.9591
1739.4729 | 852.9307 | 353.0986 | 353.7469 | 364.9314
1740.4729 | 854.5515 | 353.4437 | 353.9915 | 365.4339
1741.4729 | 853.0298 | 353.5388 | 354.2477 | 365.7117
1742.4729 | 852.8132 | 353.5254 | 354.4875 | 365.4961
1743.4729 | 856.2782 | 353.5384 | 354.4477 | 365.8618
1744.4729 | 853.7974 | 353.6712 | 354.5352 | 365.435
1745.4729 | 849.7414 | 353.4114 | 354.1693 | 365.6672
1746.4729 | 847.8743 | 353.4151 | 353.8993 | 365.5201
1747.4729 | 834.8497 | 353.753 | 353.905 | 365.7818
1748.4729 | 840.6305 | 353.788 | 354.2699 | 366.4476
1749.4729 | 844.1231 | 354.133 | 354.8011 | 367.2399
1750.4729 | 858.8426 | 354.3243 | 355.4262 | 367.8584
1751.4729 | 857.0824 | 355.0309 | 355.8458 | 368.5388
1752.4729 | 852.7381 | 355.5284 | 356.7425 | 369.0004
1753.4729 | 844.7107 | 355.9725 | 357.0583 | 369.1055
1754.4729 | 837.8864 | 356.5514 | 357.7802 | 369.09
1755.4885 | 838.4914 | 356.6479 | 358.0297 | 369.2151
1756.4729 | 835.9629 | 357.2165 | 358.3408 | 369.3986
1757.4729 | 837.9281 | 357.9102 | 358.6075 | 369.8276
1758.4729 | 834.8647 | 357.7479 | 358.7863 | 369.7011
1759.4729 | 833.0331 | 357.6635 | 358.8663 | 370.3829
1760.4729 | 830.9353 | 357.708 | 358.9158 | 370.4606
1761.4729 | 832.9361 | 357.5903 | 359.3549 | 371.0864
1762.4729 | 842.4808 | 357.3344 | 359.5112 | 371.7368
1763.4729 | 847.522 | 357.1499 | 360.1826 | 372.232
1764.4729 | 851.8495 | 356.8775 | 360.3874 | 372.3364
1765.4729 | 855.4869 | 357.0141 | 360.3521 | 371.8895
1766.4729 | 861.195 | 357.2379 | 360.656 | 373.0215
1767.4729 | 863.1111 | 357.6425 | 360.7614 | 373.0629
1768.4729 | 861.8931 | 357.9922 | 360.9352 | 373.841
1769.4729 | 851.7843 | 358.5297 | 361.3146 | 373.9604
1770.4729 | 848.353 | 358.3924 | 361.1171 | 373.7871
1771.4729 | 850.775 | 358.4307 | 361.0306 | 373.7922
1772.4729 | 857.8797 | 358.5299 | 361.7463 | 374.7549
1773.4729 | 864.3412 | 358.4607 | 361.8123 | 374.4554
1774.4729 | 866.6277 | 358.5664 | 361.4398 | 374.0209
1775.4729 | 865.7986 | 358.764 | 361.2614 | 373.7531
1776.4729 | 865.7721 | 358.9207 | 361.7069 | 373.6347
1777.4729 | 867.8784 | 359.1017 | 361.8812 | 374.0961
1778.4729 | 874.9746 | 358.734 | 361.6339 | 373.8102
1779.4729 | 873.4953 | 358.906 | 361.8171 | 373.6104
1780.4729 | 866.1674 | 359.1022 | 362.1173 | 373.6903
1781.4729 | 859.4476 | 359.5401 | 362.4011 | 373.577
1782.4729 | 860.3521 | 359.6933 | 362.6161 | 373.389
1783.4729 | 864.1063 | 359.9026 | 362.9669 | 373.6576
1784.4729 | 862.3437 | 359.8568 | 363.251 | 373.9065
1785.4729 | 866.099 | 359.9404 | 363.1307 | 373.8898
1786.4729 | 866.5579 | 359.9799 | 363.3222 | 373.944
1787.4729 | 858.0547 | 360.1001 | 363.2628 | 373.9737
1788.4729 | 857.823 | 360.5513 | 363.6798 | 373.9537
1789.4729 | 856.3982 | 360.6547 | 363.3367 | 373.6382
1790.4729 | 849.3423 | 360.918 | 363.633 | 374.0672
1791.4729 | 845.3863 | 361.1663 | 363.8834 | 374.3428
1792.4729 | 842.8115 | 360.9653 | 363.8788 | 374.0627
1793.4729 | 843.6877 | 361.018 | 363.7827 | 373.8244
1794.4729 | 844.6006 | 360.659 | 363.5739 | 373.9637
1795.4729 | 842.631 | 360.8147 | 363.2087 | 373.9888
1796.4729 | 837.3862 | 360.7416 | 362.9275 | 373.8769
1797.4729 | 832.6118 | 360.8389 | 362.5531 | 373.6841
1798.4729 | 831.5986 | 361.1139 | 362.5581 | 373.5791
1799.4729 | 831.0745 | 361.0146 | 362.6923 | 373.4764
1800.4729 | 835.0982 | 361.2515 | 362.5968 | 373.5687
1801.4729 | 840.9764 | 361.2822 | 362.7048 | 373.5504
1802.4729 | 842.4988 | 360.9296 | 362.5919 | 373.1995
1803.4729 | 841.1709 | 361.3989 | 362.5667 | 373.2401
1804.4729 | 845.9826 | 361.2958 | 363.1297 | 373.6475
1805.4729 | 846.0816 | 361.4267 | 362.8992 | 373.6431
1806.4729 | 847.2573 | 361.5607 | 362.7489 | 374.4217
1807.4729 | 837.4422 | 361.9055 | 362.9329 | 374.7209
1808.4729 | 830.8335 | 362.5177 | 363.5639 | 375.3546
1809.4729 | 816.437 | 362.8885 | 363.7616 | 375.4699
1810.4729 | 819.7217 | 363.1514 | 363.8166 | 375.2462
1811.4729 | 823.1232 | 363.1648 | 363.9602 | 374.9573
1812.4729 | 831.9252 | 363.5313 | 364.4273 | 375.0102
1813.4729 | 827.6963 | 363.8806 | 364.7935 | 375.5498
1814.4729 | 837.1024 | 363.9383 | 364.8378 | 375.2722
1815.4729 | 841.1341 | 364.0134 | 364.5974 | 375.2684
1816.4729 | 849.7946 | 363.9763 | 364.3629 | 375.089
1817.4729 | 848.1343 | 363.7218 | 363.9865 | 374.9486
1818.4729 | 846.4514 | 363.7108 | 363.9247 | 375.2639
1819.4729 | 843.2227 | 363.614 | 364.1038 | 375.8033
1820.4729 | 848.0461 | 363.7328 | 364.2553 | 375.9557
1821.4729 | 851.0252 | 363.8202 | 364.6546 | 376.2638
1822.4729 | 851.4807 | 364.1152 | 365.0384 | 376.0215
1823.4729 | 850.8871 | 363.9386 | 365.2554 | 376.0648
1824.4729 | 847.2307 | 364.1127 | 365.3354 | 376.6008
1825.4729 | 844.032 | 364.2839 | 365.6157 | 376.4659
1826.4729 | 843.293 | 364.3108 | 365.8658 | 376.5979
1827.4729 | 848.9017 | 364.6103 | 365.9963 | 376.8363
1828.4729 | 853.5429 | 364.7629 | 366.0747 | 377.113
1829.4729 | 854.1956 | 365.0894 | 365.9293 | 377.2753
1830.4729 | 853.156 | 365.6532 | 366.7711 | 377.6904
1831.4729 | 842.4959 | 365.6681 | 366.8973 | 377.9115
1832.4729 | 844.0966 | 365.7301 | 368.0485 | 378.77
1833.4729 | 843.1857 | 366.0232 | 368.0497 | 378.1827
1834.4729 | 840.8225 | 366.1441 | 368.2681 | 378.1711
1835.4729 | 837.3691 | 366.2383 | 368.197 | 378.2975
1836.4729 | 835.9603 | 365.9864 | 368.8732 | 378.4806
1837.4729 | 841.3303 | 365.9414 | 368.8179 | 378.2908
1838.4729 | 843.7706 | 366.1878 | 368.839 | 378.3555
1839.4729 | 839.379 | 366.3067 | 369.4875 | 380.2109
1840.4729 | 841.2508 | 366.3741 | 369.6531 | 380.2315
1841.4729 | 840.0773 | 366.574 | 369.7043 | 380.2781
1842.4729 | 844.9417 | 366.6296 | 369.8807 | 380.1534
1843.4729 | 846.6756 | 366.4874 | 369.4382 | 379.9474
1844.4729 | 846.1003 | 366.4331 | 369.8021 | 380.2119
1845.4729 | 849.1836 | 366.4651 | 369.8116 | 380.0337
1846.4729 | 852.4764 | 366.5627 | 369.9414 | 380.0429
1847.4729 | 843.72 | 366.7162 | 369.8322 | 379.9733
1848.4729 | 838.9573 | 366.8148 | 369.8694 | 380.4762
1849.4729 | 842.8915 | 367.2223 | 370.2746 | 380.973
1850.4729 | 849.5865 | 367.6766 | 370.1622 | 380.8358
1851.4729 | 848.0113 | 368.2354 | 370.2587 | 380.917
1852.4729 | 851.3015 | 367.7814 | 370.22 | 380.7848
1853.4729 | 842.9449 | 367.6461 | 370.7804 | 380.9914
1854.4729 | 839.376 | 367.6114 | 370.3739 | 381.1721
1855.4729 | 837.2042 | 367.8306 | 370.6018 | 381.7191
1856.4729 | 838.3989 | 368.04 | 370.8644 | 381.7579
1857.4729 | 836.5817 | 367.8209 | 370.6798 | 381.7586
1858.4729 | 840.1246 | 367.4773 | 370.3051 | 381.1233
1859.4729 | 843.5611 | 367.3523 | 369.9603 | 380.7732
1860.4729 | 844.9435 | 367.4217 | 369.9061 | 381.1052
1861.4729 | 846.8093 | 367.4881 | 369.5384 | 380.8234
1862.4885 | 843.0588 | 367.6175 | 369.6923 | 380.9487
1863.4729 | 848.3389 | 367.7995 | 369.7924 | 380.6389
1864.4729 | 853.1102 | 367.8605 | 370.9039 | 381.1161
1865.4729 | 856.2808 | 367.9203 | 370.6627 | 381.2691
1866.4729 | 857.1037 | 368.469 | 370.5301 | 381.8188
1867.4729 | 859.5117 | 368.5945 | 370.8603 | 382.1661
1868.4729 | 857.2496 | 368.6528 | 371.3888 | 382.6107
1869.4729 | 859.7214 | 369.6756 | 371.8219 | 383.9325
1870.4729 | 867.6428 | 369.9342 | 372.5016 | 384.981
1871.4729 | 878.0943 | 369.8317 | 372.5201 | 385.3983
1872.4729 | 882.844 | 370.1186 | 372.628 | 385.8146
1873.4729 | 883.8057 | 370.7827 | 372.7579 | 386.5271
1874.4729 | 877.7457 | 371.7334 | 373.1722 | 386.4593
1875.4729 | 860.6937 | 371.5995 | 373.2106 | 386.6901
1876.4729 | 864.509 | 371.3688 | 373.1052 | 386.8827
1877.4729 | 866.0504 | 370.9804 | 373.1606 | 386.7508
1878.4729 | 866.4131 | 371.0079 | 373.1555 | 386.9231
1879.4729 | 864.327 | 370.9905 | 373.3693 | 387.4514
1880.4729 | 863.0888 | 371.4215 | 373.8565 | 387.6181
1881.4729 | 863.6728 | 371.9307 | 375.0307 | 388.4276
1882.4729 | 864.9804 | 371.9662 | 375.3985 | 388.1697
1883.4729 | 872.2939 | 372.0416 | 376.1678 | 389.0398
1884.4729 | 875.864 | 372.7377 | 376.8257 | 389.5607
1885.4729 | 881.2036 | 373.2392 | 376.8237 | 389.6493
1886.4729 | 885.8642 | 373.9101 | 377.1553 | 390.0995
1887.4729 | 880.6642 | 374.3704 | 377.9663 | 390.7483
1888.4729 | 873.9667 | 374.6437 | 378.182 | 390.6908
1889.4729 | 876.7072 | 374.4615 | 377.8728 | 390.393
1890.4729 | 877.0393 | 374.4969 | 378.0197 | 390.546
1891.4729 | 881.556 | 374.4442 | 378.6615 | 391.2023
1892.4729 | 878.1465 | 374.915 | 378.7648 | 391.1384
1893.4729 | 885.6533 | 375.1822 | 379.1637 | 391.911
1894.4729 | 883.9109 | 375.2964 | 379.0969 | 391.628
1895.4729 | 873.3872 | 375.6812 | 379.3719 | 392.0977
1896.4729 | 872.76 | 375.8413 | 379.5452 | 392.9746
1897.4729 | 870.1509 | 376.2978 | 379.6386 | 392.9815
1898.4729 | 869.2635 | 376.4588 | 379.5758 | 393.3241
1899.4729 | 873.7903 | 376.4376 | 379.7302 | 392.71
1900.4729 | 871.6787 | 377.4764 | 380.9713 | 392.8884
1901.4729 | 872.3037 | 377.7089 | 380.8771 | 393.1133
1902.4729 | 877.62 | 377.8599 | 381.1791 | 393.7761
1903.4729 | 882.6558 | 378.4816 | 381.5521 | 394.0521
1904.4729 | 888.3847 | 378.8369 | 382.603 | 394.4767
1905.4885 | 880.8773 | 379.1674 | 383.3136 | 394.5919
1906.4729 | 878.7989 | 379.6286 | 384.0501 | 395.3084
1907.4729 | 882.6941 | 379.9391 | 384.6908 | 395.3504
1908.4729 | 888.8808 | 380.1208 | 385.1917 | 395.2924
1909.4729 | 894.097 | 380.5258 | 385.5407 | 396.7954
1910.4729 | 905.5767 | 380.8358 | 385.5659 | 396.9639
1911.4729 | 894.7113 | 381.1155 | 385.2523 | 396.9178
1912.4729 | 883.0059 | 381.8272 | 385.1253 | 397.1577
1913.4729 | 871.6551 | 382.3443 | 385.1033 | 397.8399
1914.4729 | 873.0284 | 382.7033 | 385.4009 | 398.5514
1915.4729 | 864.8742 | 383.1247 | 385.2828 | 398.7888
1916.4729 | 853.7775 | 383.1754 | 385.752 | 399.3649
1917.4729 | 845.3007 | 383.5176 | 386 | 400.0089
1918.4729 | 854.3016 | 384.2028 | 386.3369 | 400.8031
1919.4729 | 864.3716 | 384.2776 | 386.6812 | 400.8816
1920.4729 | 872.8276 | 384.7271 | 387.3276 | 400.6484
1921.4729 | 870.265 | 384.8157 | 387.7263 | 400.3929
1922.4729 | 861.9379 | 385.564 | 387.7477 | 400.6149
1923.4729 | 868.7869 | 386.0894 | 387.8994 | 400.7964
1924.4729 | 876.3056 | 385.9478 | 388.2044 | 401.248
1925.4729 | 875.1666 | 385.8948 | 388.7051 | 402.0351
1926.4729 | 870.7983 | 386.246 | 388.5789 | 401.8468
1927.4729 | 874.5672 | 386.8495 | 388.7926 | 402.1749
1928.4729 | 880.659 | 386.9178 | 389.0452 | 402.0872
1929.4729 | 890.9017 | 387.0534 | 388.9048 | 401.6783
1930.4729 | 888.5296 | 387.098 | 388.938 | 401.6527
1931.4729 | 893.0718 | 387.2967 | 388.9792 | 401.922
1932.4729 | 890.4243 | 387.4148 | 389.2917 | 401.9261
1933.4729 | 886.9162 | 387.4413 | 389.7654 | 402.412
1934.4729 | 884.6971 | 387.115 | 389.4892 | 401.8917
1935.4885 | 879.7362 | 387.128 | 389.8768 | 402.2658
1936.4729 | 878.1126 | 386.9723 | 390.4248 | 402.9647
1937.4729 | 875.0153 | 386.692 | 390.5847 | 403.173
1938.4729 | 879.1163 | 386.6708 | 390.1405 | 402.8145
1939.4729 | 874.7691 | 387.1006 | 390.2117 | 402.7591
1940.4885 | 877.6408 | 387.159 | 390.4891 | 402.8713
1941.4885 | 875.2298 | 387.0792 | 390.4705 | 402.482
1942.4729 | 876.3156 | 386.5486 | 390.1746 | 402.1671
1943.4729 | 875.0135 | 385.8349 | 389.4715 | 402.3081
1944.4729 | 880.6195 | 385.5862 | 389.7262 | 403.0932
1945.4729 | 877.554 | 384.9433 | 389.3113 | 402.4087
1946.4729 | 870.0782 | 384.5173 | 389.2882 | 402.9825
1947.4885 | 869.217 | 384.5232 | 389.4272 | 402.7513
1948.4729 | 872.2886 | 384.4033 | 389.4088 | 402.7407
1949.4729 | 873.1501 | 384.741 | 389.2256 | 402.3561
1950.4729 | 877.0037 | 385.3718 | 389.5602 | 402.1003
1951.4729 | 882.7219 | 385.813 | 389.6341 | 402.2088
1952.4729 | 881.0363 | 386.2035 | 390.2265 | 402.4292
1953.4729 | 877.999 | 386.3973 | 390.3312 | 402.7021
1954.4729 | 886.6395 | 386.0844 | 390.8537 | 402.7513
1955.4729 | 880.971 | 386.1254 | 390.7519 | 402.3521
1956.4729 | 868.7353 | 386.6926 | 391.0334 | 403.0454
1957.4729 | 864.5575 | 387.5984 | 392.0527 | 403.3098
1958.4729 | 852.9265 | 388.0164 | 392.4622 | 404.0613
1959.4729 | 853.7357 | 388.0219 | 392.2041 | 404.0765
1960.4729 | 866.4956 | 388.0877 | 392.2807 | 404.9641
1961.4729 | 876.2931 | 387.9262 | 392.2609 | 405.3674
1962.4729 | 882.4814 | 388.3069 | 392.9309 | 405.4512
1963.4729 | 882.2689 | 388.5535 | 392.9817 | 405.9844
1964.4729 | 873.0069 | 388.6195 | 392.7681 | 406.336
1965.4885 | 872.5075 | 388.9259 | 392.9442 | 406.2949
1966.4729 | 865.1521 | 388.8545 | 392.8662 | 407.1513
1967.4729 | 875.4913 | 389.5318 | 393.739 | 408.0414
1968.4729 | 885.5804 | 390.0359 | 393.9192 | 408.4353
1969.4729 | 887.7494 | 389.9761 | 393.9055 | 408.8783
1970.4729 | 892.8735 | 390.6827 | 394.2897 | 408.6754
1971.4729 | 899.7297 | 391.2866 | 394.5902 | 408.3671
1972.4729 | 896.9243 | 391.7236 | 394.8365 | 408.2132
1973.4729 | 890.5605 | 392.0198 | 395.2303 | 408.3345
1974.4729 | 883.0043 | 392.7597 | 396.0698 | 408.6137
1975.4729 | 883.1559 | 392.873 | 396.452 | 409.1429
1976.4729 | 888.778 | 392.798 | 397.1778 | 409.6075
1977.4729 | 888.2717 | 392.7794 | 397.2373 | 410.1607
1978.4729 | 884.8083 | 392.8903 | 397.3784 | 411.0453
1979.4729 | 881.6892 | 393.0711 | 397.6125 | 411.7588
1980.4729 | 881.2726 | 393.1581 | 397.6269 | 412.062
1981.4729 | 888.4564 | 392.9426 | 397.7982 | 411.7428
1982.4729 | 881.9043 | 393.2986 | 397.6935 | 411.9213
1983.4885 | 868.4631 | 393.9268 | 397.4732 | 411.7245
1984.4729 | 866.9637 | 393.4864 | 397.3122 | 412.0796
1985.4729 | 872.0115 | 393.0548 | 397.2467 | 412.1345
1986.4729 | 872.8461 | 393.0049 | 397.522 | 412.818
1987.4729 | 874.0262 | 393.0295 | 398.1689 | 413.2313
1988.4729 | 875.6506 | 393.1262 | 398.4293 | 413.6448
1989.4729 | 877.7829 | 394.4198 | 398.7591 | 413.4125
1990.4729 | 877.8889 | 395.167 | 398.854 | 413.2846
1991.4729 | 882.5114 | 395.5148 | 398.6797 | 413.2721
1992.4729 | 875.8219 | 395.219 | 398.7986 | 413.5398
1993.4729 | 872.1432 | 395.3222 | 398.8166 | 412.9834
1994.4729 | 867.0019 | 395.0314 | 398.4815 | 412.5995
1995.4885 | 863.411 | 394.7816 | 398.5074 | 412.6054
1996.4729 | 864.6634 | 394.7149 | 398.9393 | 412.2218
1997.4729 | 862.3847 | 394.8323 | 398.6571 | 412.7303
1998.4729 | 867.778 | 395.5014 | 399.1622 | 412.7465
1999.4729 | 870.6235 | 395.1451 | 398.9945 | 413.0985
2000.4729 | 870.0737 | 394.8026 | 398.9269 | 412.9726
2001.4729 | 852.9961 | 394.6661 | 399.1215 | 413.3021
2002.4729 | 850.2373 | 394.7246 | 398.9339 | 413.2426
2003.4729 | 851.1108 | 394.6154 | 399.8531 | 413.297
2004.4729 | 850.6595 | 395.6018 | 399.808 | 415.0387
2005.4729 | 845.9316 | 396.2153 | 400.7939 | 415.2114
2006.4729 | 843.0092 | 395.9439 | 401.2537 | 416.2788
2007.4729 | 839.1611 | 396.0147 | 402.1914 | 416.8413
2008.4729 | 852.8188 | 395.9588 | 402.5909 | 416.923
2009.4729 | 857.4772 | 395.4999 | 402.151 | 416.9442
2010.4729 | 867.5334 | 395.3265 | 402.2353 | 416.7837
2011.4729 | 873.9261 | 395.5178 | 402.1379 | 416.7679
2012.4729 | 865.2962 | 395.739 | 402.1613 | 416.729
2013.4729 | 869.7377 | 395.963 | 401.9073 | 416.874
2014.4729 | 873.4827 | 396.3847 | 402.8665 | 416.9672
2015.4729 | 879.8825 | 396.5706 | 403.1641 | 416.9728
2016.4729 | 885.0649 | 396.477 | 403.7762 | 416.7441
2017.4729 | 885.8653 | 396.6586 | 403.8758 | 417.0929
2018.4729 | 876.5474 | 397.2973 | 403.8176 | 417.1617
2019.4729 | 865.5206 | 397.6381 | 403.4461 | 417.0031
2020.4729 | 865.6985 | 398.2392 | 403.4505 | 416.722
2021.4729 | 868.1295 | 398.3945 | 403.121 | 416.4813
2022.4729 | 867.7599 | 398.5001 | 403.0354 | 416.2428
2023.4729 | 863.459 | 398.8712 | 403.3027 | 416.6111
2024.4729 | 859.6831 | 399.2646 | 403.3366 | 417.1183
2025.4885 | 855.7995 | 399.3281 | 403.3189 | 417.5499
2026.4729 | 857.3332 | 400.0562 | 403.6309 | 418.0346
2027.4729 | 842.7923 | 400.3616 | 403.4764 | 417.8321
2028.4729 | 828.949 | 401.2084 | 404.0283 | 419.0258
2029.4729 | 817.1324 | 401.9299 | 404.484 | 420.1513
2030.4729 | 825.2824 | 403.4797 | 405.2583 | 421.1473
2031.4729 | 833.7774 | 403.8999 | 406.1042 | 421.2514
2032.4729 | 837.1625 | 404.2087 | 406.3049 | 421.8492
2033.4729 | 819.6075 | 404.7038 | 407.1197 | 421.4373
2034.4729 | 809.2813 | 404.6494 | 407.2656 | 422.1338
2035.4729 | 802.5822 | 404.734 | 407.7276 | 422.4192
2036.4729 | 819.8737 | 404.711 | 408.0763 | 422.4886
2037.4729 | 836.5355 | 404.9047 | 408.1517 | 422.0605
2038.4729 | 838.652 | 405.3448 | 408.1343 | 421.7896
2039.4729 | 846.7749 | 405.4782 | 409.5883 | 423.4323
2040.4729 | 847.1662 | 405.5777 | 409.8265 | 423.4417
2041.4729 | 839.9003 | 405.6947 | 409.5777 | 422.9739
2042.4729 | 838.2461 | 405.7996 | 409.2527 | 423.4089
2043.4729 | 841.788 | 405.6533 | 409.2953 | 423.517
2044.4729 | 840.7934 | 405.4465 | 409.115 | 422.7238
2045.4729 | 849.0669 | 405.6302 | 410.1118 | 423.3961
2046.4729 | 852.9212 | 405.4375 | 410.0986 | 423.1275
2047.4729 | 848.3991 | 404.9732 | 409.8309 | 423.0725
2048.4729 | 852.7196 | 404.6522 | 409.2252 | 422.4042
2049.4729 | 852.2759 | 404.6765 | 408.6591 | 422.2178
2050.4729 | 848.6957 | 404.0878 | 408.4286 | 422.1729
2051.4729 | 851.5979 | 404.5857 | 408.9648 | 422.2785
2052.4729 | 857.62 | 404.611 | 408.854 | 422.7237
2053.4729 | 869.4713 | 404.5113 | 408.5969 | 422.5058
2054.4729 | 878.2891 | 405.0299 | 408.1174 | 422.288
2055.4729 | 875.5598 | 405.7464 | 408.3595 | 422.586
2056.4729 | 869.0498 | 405.852 | 408.3149 | 422.3873
2057.4729 | 854.9044 | 405.6585 | 408.3956 | 422.9259
2058.4729 | 854.9807 | 405.6457 | 408.4119 | 422.7661
2059.4729 | 865.2245 | 405.7949 | 408.1187 | 423.4009
2060.4729 | 862.1027 | 406.0807 | 408.397 | 423.6912
2061.4729 | 859.0151 | 406.9383 | 408.6144 | 424.3987
2062.4729 | 844.2595 | 406.8385 | 408.7793 | 423.8785
2063.4729 | 824.2028 | 407.0656 | 409.4986 | 424.3302
2064.4729 | 831.3687 | 407.8218 | 410.303 | 425.2768
2065.4729 | 842.4907 | 408.3152 | 410.3541 | 425.8848
2066.4729 | 854.0124 | 408.3288 | 410.7494 | 425.4238
2067.4729 | 864.3085 | 408.0074 | 410.6024 | 425.6056
2068.4729 | 862.0977 | 407.9232 | 410.4061 | 425.3441
2069.4729 | 873.4297 | 407.7086 | 410.5161 | 425.1327
2070.4729 | 868.5105 | 407.791 | 410.5873 | 425.3892
2071.4729 | 873.928 | 407.514 | 410.3564 | 425.5661
2072.4729 | 882.9113 | 407.9091 | 411.2776 | 425.826
2073.4729 | 883.4512 | 408.0148 | 411.5221 | 425.746
2074.4729 | 880.2342 | 408.361 | 411.4381 | 426.0625
2075.4729 | 880.8865 | 408.3769 | 411.5185 | 426.7314
2076.4729 | 880.0382 | 408.681 | 411.4525 | 426.8334
2077.4729 | 883.5672 | 408.8944 | 411.6635 | 427.1449
2078.4729 | 887.6762 | 408.8824 | 411.5064 | 426.6608
2079.4729 | 889.3263 | 408.7432 | 411.5045 | 426.6054
2080.4729 | 891.5814 | 409.242 | 411.6054 | 426.7121
2081.4729 | 896.8519 | 409.1458 | 411.6937 | 426.2835
2082.4729 | 886.5221 | 409.3844 | 411.2849 | 426.5694
2083.4729 | 886.4344 | 409.5369 | 411.5399 | 426.95
2084.4729 | 890.8613 | 409.2154 | 411.3631 | 427.3593
2085.4729 | 879.4027 | 408.8298 | 410.9105 | 426.8438
2086.4729 | 887.4615 | 409.6031 | 410.8762 | 426.5901
2087.4729 | 883.8776 | 409.9227 | 411.0038 | 427.0588
2088.4729 | 863.7049 | 410.3558 | 411.9043 | 427.6565
2089.4729 | 860.5929 | 410.0621 | 412.1213 | 427.7244
2090.4729 | 855.8886 | 410.1753 | 412.2471 | 427.7172
2091.4729 | 864.5164 | 410.2899 | 411.9723 | 427.2575
2092.4729 | 861.5727 | 410.2901 | 412.0407 | 427.233
2093.4729 | 844.4555 | 410.2624 | 412.4741 | 427.0924
2094.4729 | 842.753 | 410.5054 | 412.8109 | 427.6727
2095.4729 | 855.4433 | 411.0318 | 413.289 | 429.0734
2096.4729 | 871.0886 | 411.0288 | 413.85 | 429.2862
2097.4729 | 881.3949 | 411.1413 | 414.2424 | 429.1788
2098.4729 | 878.1139 | 411.1158 | 414.5014 | 429.4017
2099.4729 | 886.7554 | 411.5768 | 414.4627 | 430.1321
2100.4729 | 889.5223 | 411.3062 | 414.5631 | 430.2004
2101.4729 | 883.575 | 410.9853 | 414.2779 | 430.1007
2102.4729 | 891.3513 | 411.1545 | 414.4379 | 430.3237
2103.4729 | 892.222 | 411.4958 | 414.5743 | 430.3941
2104.4729 | 894.9724 | 411.5133 | 414.7953 | 430.0576
2105.4729 | 891.2237 | 411.5689 | 415.0972 | 430.581
2106.4729 | 892.1103 | 411.9602 | 415.0502 | 430.6164
2107.4729 | 898.9256 | 411.8185 | 415.4645 | 430.4706
2108.4729 | 893.444 | 412.1819 | 415.5589 | 430.2867
2109.4729 | 892.8007 | 412.6425 | 415.8824 | 430.1962
2110.4729 | 888.5611 | 412.5892 | 415.5202 | 430.5411
2111.4729 | 870.0509 | 412.1788 | 415.3165 | 430.2307
2112.4729 | 857.9508 | 411.8897 | 414.7341 | 429.8997
2113.4729 | 860.0413 | 411.5997 | 414.0631 | 429.3249
2114.4729 | 861.2717 | 411.3838 | 413.667 | 429.1801
2115.4729 | 859.9824 | 411.5048 | 413.9171 | 428.8799
2116.4729 | 863.9396 | 411.451 | 414.2057 | 429.0259
2117.4729 | 860.6531 | 411.6535 | 414.2986 | 428.4676
2118.4729 | 866.3684 | 411.4976 | 414.2742 | 428.4572
2119.4729 | 871.5506 | 411.8319 | 414.4204 | 428.2342
2120.4729 | 875.3747 | 411.6177 | 414.504 | 428.2557
2121.4729 | 882.3452 | 411.8641 | 414.2662 | 428.1023
2122.4729 | 871.3834 | 411.9812 | 414.2294 | 427.7902
2123.4729 | 879.6696 | 411.8447 | 414.1785 | 427.9527
2124.4729 | 892.2454 | 411.6021 | 414.4431 | 427.4059
2125.4729 | 894.3876 | 411.7006 | 414.8032 | 427.4911
2126.4729 | 880.3532 | 411.6854 | 414.7509 | 427.2269
2127.4729 | 892.1607 | 411.617 | 414.5703 | 427.2764
2128.4729 | 899.2985 | 412.1568 | 414.4489 | 428.0397
2129.4729 | 905.7187 | 411.9167 | 414.647 | 428.0769
2130.4729 | 901.4753 | 412.2792 | 414.7245 | 427.9829
2131.4729 | 908.4705 | 412.3444 | 414.6168 | 427.872
2132.4729 | 900.5206 | 412.6412 | 415.0897 | 427.6204
2133.4729 | 900.7245 | 412.3334 | 415.264 | 428.0198
2134.4729 | 889.9485 | 412.5072 | 415.6121 | 428.315
2135.4729 | 894.0811 | 412.8611 | 416.5602 | 428.4158
2136.4729 | 899.1201 | 413.082 | 416.5313 | 428.8879
2137.4729 | 900.7867 | 413.3502 | 417.5305 | 428.7489
2138.4729 | 891.8336 | 413.5358 | 417.4994 | 429.2737
2139.4729 | 891.9449 | 413.3057 | 417.2438 | 429.3927
2140.4729 | 885.4641 | 413.681 | 417.02 | 430.27
2141.4729 | 888.468 | 413.5692 | 417.0533 | 430.6455
2142.4729 | 884.3929 | 413.6746 | 416.6299 | 430.3532
2143.4729 | 873.7824 | 413.7515 | 416.4798 | 430.8783
2144.4729 | 875.1373 | 413.7444 | 416.4799 | 430.9225
2145.4729 | 885.6502 | 413.9912 | 415.9406 | 430.5753
2146.4729 | 896.5186 | 414.1091 | 415.6627 | 430.6432
2147.4729 | 891.8834 | 414.0199 | 415.5305 | 429.886
2148.4729 | 883.904 | 413.7036 | 415.3293 | 430.3236
2149.4729 | 882.4714 | 414.1664 | 415.9176 | 430.5701
2150.4729 | 886.5305 | 413.893 | 416.1907 | 430.6793
2151.4729 | 883.877 | 413.6272 | 415.7914 | 430.4496
2152.4729 | 883.6724 | 413.2386 | 415.3808 | 430.7908
2153.4729 | 876.8034 | 413.7763 | 416.1852 | 431.4715
2154.4729 | 878.9281 | 413.9192 | 416.2522 | 430.7819
2155.4729 | 870.9858 | 413.9003 | 416.452 | 430.6509
2156.4729 | 875.806 | 413.845 | 416.4287 | 430.7313
2157.4729 | 882.9024 | 413.7705 | 416.4501 | 430.1364
2158.4729 | 889.4539 | 413.6247 | 415.9997 | 429.2879
2159.4729 | 884.7327 | 413.6952 | 416.0633 | 428.9465
2160.4729 | 899.038 | 413.9182 | 415.6682 | 428.9116
2161.4729 | 895.7459 | 414.6103 | 416.2479 | 428.8858
2162.4729 | 900.826 | 414.5326 | 416.1387 | 428.2934
2163.4729 | 905.4087 | 414.3332 | 416.5528 | 428.5342
2164.4729 | 917.7042 | 414.1848 | 416.4194 | 428.0703
2165.4729 | 905.9152 | 413.7522 | 415.837 | 428.01
2166.4729 | 901.0234 | 413.9893 | 415.5808 | 428.0125
2167.4729 | 901.1396 | 414.1955 | 415.2889 | 427.6805
2168.4729 | 888.4083 | 414.5728 | 415.1419 | 427.8102
2169.4729 | 900.8149 | 414.5859 | 415.4629 | 428.1155
2170.4729 | 896.1284 | 414.3866 | 415.3547 | 427.9353
2171.4729 | 887.4089 | 414.5706 | 415.365 | 427.2209
2172.4729 | 884.8288 | 414.1003 | 414.7315 | 426.412
2173.4729 | 884.2148 | 413.9198 | 415.0108 | 425.9486
2174.4729 | 887.7983 | 413.6617 | 414.4862 | 425.3644
2175.4729 | 887.9417 | 414.585 | 414.6417 | 425.2344
2176.4729 | 888.7906 | 414.5784 | 414.8781 | 425.2785
2177.4729 | 888.191 | 415.0129 | 415.169 | 425.6468
2178.4729 | 890.8426 | 415.3451 | 415.5897 | 426.1557
2179.4729 | 890.0178 | 415.4298 | 416.3825 | 427.221
2180.4729 | 888.4335 | 415.9435 | 416.6488 | 427.1242
2181.4729 | 888.3419 | 415.8361 | 416.758 | 427.4384
2182.4729 | 892.8805 | 416.1164 | 416.9928 | 427.6333
2183.4729 | 888.7821 | 416.4452 | 416.6484 | 428.1722
2184.4729 | 886.9145 | 416.7676 | 417.1614 | 428.2668
2185.4729 | 891.1944 | 417.3584 | 417.2195 | 428.3925
2186.4729 | 897.4131 | 417.3803 | 417.1269 | 428.7523
2187.4729 | 890.751 | 417.2079 | 417.0598 | 428.8715
2188.4729 | 906.5193 | 416.7091 | 416.8629 | 428.9404
2189.4729 | 896.5888 | 416.9252 | 416.5571 | 428.4944
2190.4729 | 894.2652 | 417.4542 | 417.2481 | 428.6685
2191.4729 | 889.6927 | 417.1115 | 417.278 | 428.4998
2192.4729 | 894.9705 | 417.2375 | 417.3239 | 428.9528
2193.4729 | 907.3966 | 416.8173 | 417.0772 | 428.7787
2194.4729 | 906.5489 | 416.7591 | 417.054 | 428.4747
2195.4729 | 907.1712 | 417.0989 | 417.3756 | 428.2298
2196.4729 | 906.8088 | 417.3931 | 417.251 | 428.2112
2197.4729 | 901.6338 | 417.499 | 417.2101 | 428.7224
2198.4729 | 895.018 | 417.6079 | 417.8616 | 428.8143
2199.4729 | 892.3706 | 417.3262 | 418.126 | 428.7912
2200.4729 | 895.9801 | 418.153 | 418.1947 | 428.7467
2201.4729 | 897.4097 | 417.8838 | 417.9216 | 428.3158
2202.4729 | 902.7848 | 418.1937 | 417.5965 | 428.1846
2203.4729 | 898.5458 | 418.3795 | 417.7621 | 428.5718
2204.4729 | 892.5146 | 418.5918 | 418.3818 | 428.8131
2205.4729 | 900.8198 | 418.6745 | 418.5665 | 428.7721
2206.4729 | 894.2809 | 418.2458 | 419.9448 | 429.649
2207.4729 | 898.4363 | 417.7859 | 419.4377 | 429.7284
2208.4729 | 905.1658 | 417.3364 | 419.0837 | 430.1948
2209.4729 | 895.1376 | 417.1678 | 418.7384 | 429.7818
2210.4729 | 889.232 | 417.422 | 418.6766 | 429.5708
2211.4729 | 890.5563 | 417.301 | 418.4275 | 428.7622
2212.4729 | 895.9216 | 417.2213 | 418.4825 | 428.718
2213.4729 | 903.6112 | 417.912 | 418.6288 | 428.8476
2214.4729 | 898.1701 | 418.108 | 418.3798 | 428.6586
2215.4729 | 903.7488 | 418.1333 | 418.3783 | 428.6613
2216.4729 | 911.4799 | 418.2735 | 418.5157 | 428.4872
2217.4729 | 903.9476 | 418.4125 | 419.2522 | 428.9517
2218.4729 | 902.0201 | 418.2896 | 419.1426 | 429.0758
2219.4729 | 902.2573 | 418.0817 | 419.0104 | 429.1128
2220.4729 | 899.9013 | 417.7361 | 418.5332 | 429.3493
2221.4729 | 904.8631 | 417.7919 | 418.1974 | 429.2514
2222.4729 | 903.4748 | 418.547 | 418.8567 | 429.8887
2223.4729 | 898.9725 | 418.3692 | 418.8304 | 429.6076
2224.4729 | 903.0108 | 418.5864 | 418.4419 | 429.5765
2225.4729 | 905.2907 | 418.5835 | 418.1118 | 429.4865
2226.4729 | 908.6285 | 418.6552 | 417.833 | 429.2349
2227.4729 | 905.5195 | 419.4065 | 418.075 | 428.8237
2228.4729 | 913.6777 | 419.7714 | 418.5723 | 429.1729
2229.4729 | 901.2173 | 420.1957 | 418.4693 | 428.5471
2230.4729 | 892.9123 | 420.1473 | 418.4226 | 428.3263
2231.4729 | 885.6567 | 420.1008 | 418.8399 | 428.4026
2232.4729 | 891.2254 | 420.3194 | 418.879 | 428.6702
2233.4729 | 897.1848 | 420.2006 | 419.115 | 429.0516
2234.4729 | 906.5742 | 420.5051 | 419.6796 | 429.7877
2235.4729 | 892.6013 | 421.6386 | 420.6899 | 429.9812
2236.4729 | 893.4224 | 421.6997 | 421.1059 | 430.0852
2237.4729 | 887.1378 | 421.7546 | 420.9903 | 430.026
2238.4729 | 880.7039 | 422.12 | 421.621 | 430.6239
2239.4729 | 871.8587 | 422.1378 | 421.3018 | 430.8761
2240.4729 | 871.3944 | 421.7931 | 420.9874 | 430.6085
2241.4729 | 875.4424 | 421.9737 | 421.095 | 430.9995
2242.4729 | 872.8366 | 421.9517 | 421.1894 | 430.8404
2243.4729 | 888.9442 | 421.595 | 421.0567 | 430.6075
2244.4729 | 893.3617 | 421.2901 | 421.175 | 429.7109
2245.4729 | 897.3095 | 421.2371 | 421.0146 | 429.2232
2246.4729 | 894.5071 | 421.2755 | 420.9755 | 429.8539
2247.4729 | 903.4078 | 420.9305 | 420.7786 | 429.4022
2248.4729 | 902.8752 | 420.8306 | 420.4704 | 429.1354
2249.4729 | 897.2653 | 420.8285 | 420.4629 | 429.3715
2250.4729 | 895.3744 | 420.8244 | 420.318 | 429.3101
2251.4729 | 898.7481 | 420.4397 | 419.9199 | 428.8135
2252.4729 | 909.1767 | 420.4733 | 420.0257 | 428.9336
2253.4729 | 903.7762 | 420.4337 | 420.1308 | 429.063
2254.4729 | 907.4665 | 420.8856 | 420.4519 | 429.5746
2255.4729 | 906.092 | 421.115 | 420.9764 | 429.9796
2256.4729 | 913.2009 | 420.9409 | 420.9581 | 430.0368
2257.4729 | 915.5464 | 422.2298 | 421.4947 | 430.2171
2258.4729 | 894.098 | 421.9043 | 421.3974 | 429.8952
2259.4729 | 884.3215 | 422.0353 | 421.3638 | 429.9745
2260.4729 | 891.599 | 422.4682 | 421.6718 | 429.8576
2261.4729 | 894.1059 | 422.3498 | 421.8787 | 430.1507
2262.4729 | 890.3636 | 422.1434 | 421.4928 | 429.5858
2263.4729 | 892.0436 | 421.8814 | 421.4671 | 429.3372
2264.4729 | 887.2517 | 421.7903 | 421.4732 | 429.0436
2265.4729 | 878.5976 | 421.8328 | 421.053 | 429.04
2266.4729 | 878.4334 | 421.4947 | 420.8136 | 429.0471
2267.4729 | 879.1334 | 421.1684 | 420.5446 | 428.7517
2268.4729 | 879.5785 | 421.5283 | 420.6085 | 428.5732
2269.4729 | 885.4887 | 421.9535 | 420.4489 | 428.3987
2270.4729 | 888.7686 | 422.334 | 420.7593 | 428.862
2271.4729 | 898.5179 | 422.2575 | 420.7925 | 429.0436
2272.4729 | 895.8146 | 422.3164 | 420.5161 | 429.2561
2273.4729 | 900.8035 | 422.2497 | 420.9065 | 429.2817
2274.4729 | 908.1936 | 421.9997 | 421.1363 | 429.5535
2275.4729 | 910.4392 | 422.057 | 420.8693 | 429.5326
2276.4729 | 918.5175 | 422.0977 | 420.5248 | 429.2637
2277.4729 | 906.6379 | 422.0449 | 420.2947 | 428.9748
2278.4729 | 895.009 | 422.3308 | 420.4235 | 429.1553
2279.4729 | 894.6591 | 422.6695 | 420.3662 | 428.8932
2280.4729 | 902.5032 | 422.6814 | 420.243 | 428.7013
2281.4729 | 894.3213 | 422.61 | 420.031 | 428.665
2282.4729 | 897.998 | 422.7029 | 419.8642 | 428.5334
2283.4729 | 904.7234 | 423.0742 | 420.7705 | 428.6354
2284.4729 | 901.5338 | 423.3473 | 420.7337 | 428.528
2285.4729 | 899.3394 | 423.7666 | 421.0201 | 429.0111
2286.4729 | 894.233 | 424.0304 | 422.2685 | 428.935
2287.4729 | 889.6652 | 424.4113 | 422.3816 | 429.3654
2288.4729 | 899.9487 | 424.0542 | 422.3321 | 429.6514
2289.4729 | 896.6679 | 424.2275 | 422.8839 | 429.8475
2290.4729 | 901.3807 | 424.7205 | 423.0452 | 429.9897
2291.4729 | 894.6885 | 424.76 | 423.4076 | 429.9617
2292.4729 | 892.7876 | 425.7028 | 423.8717 | 430.0605
2293.4729 | 889.7163 | 425.4204 | 424.35 | 430.3515
2294.4729 | 886.6959 | 425.3182 | 424.2513 | 430.9053
2295.4729 | 883.7294 | 425.1389 | 424.4934 | 432.1952
2296.4729 | 889.6931 | 425.543 | 425.0922 | 432.1437
2297.4729 | 891.1175 | 425.9816 | 425.5304 | 432.537
2298.4729 | 889.9734 | 426.8281 | 425.5873 | 432.2533
2299.4729 | 883.1629 | 426.7332 | 425.4568 | 432.0773
2300.4729 | 889.496 | 426.5899 | 425.6142 | 432.148
2301.4729 | 899.6726 | 426.7315 | 425.6797 | 432.5984
2302.4729 | 901.8305 | 426.8745 | 425.6273 | 432.8802
2303.4729 | 898.8988 | 426.9 | 425.9376 | 432.8556
2304.4729 | 899.0154 | 426.8084 | 425.6774 | 432.6928
2305.4729 | 905.9147 | 426.2287 | 425.6172 | 432.4035
2306.4729 | 911.5197 | 427.128 | 425.5621 | 432.5826
2307.4729 | 909.4929 | 427.114 | 426.1254 | 433.1073
2308.4729 | 912.2968 | 427.4665 | 426.3437 | 433.0158
2309.4729 | 908.6663 | 427.2447 | 426.4498 | 433.103
2310.4729 | 897.3536 | 427.1488 | 426.5205 | 433.3707
2311.4729 | 884.8925 | 427.2687 | 426.9236 | 433.6685
2312.4729 | 882.5532 | 426.9143 | 426.7775 | 434.0085
2313.4729 | 882.6008 | 426.7357 | 426.4052 | 434.427
2314.4729 | 887.6141 | 426.739 | 425.9919 | 434.723
2315.4729 | 896.3211 | 426.0481 | 425.5294 | 434.2138
2316.4729 | 891.1675 | 425.6178 | 425.1872 | 433.5067
2317.4729 | 877.8391 | 425.2379 | 424.4673 | 433.1426
2318.4729 | 873.6692 | 425.722 | 423.8906 | 432.897
2319.4729 | 875.38 | 425.8723 | 424.5679 | 433.0688
2320.4729 | 877.3786 | 425.3488 | 424.9963 | 432.9451
2321.4729 | 885.0229 | 424.8254 | 424.4254 | 432.2657
2322.4729 | 891.9397 | 424.3755 | 424.935 | 432.1879
2323.4729 | 888.4886 | 424.5013 | 424.6799 | 431.9913
2324.4729 | 881.0616 | 424.6454 | 424.8654 | 431.8417
2325.4729 | 875.7517 | 424.6983 | 424.9479 | 431.8673
2326.4729 | 878.1816 | 425.1695 | 424.2511 | 432.2022
2327.4729 | 887.5329 | 425.2736 | 424.9357 | 432.9319
2328.4729 | 884.3548 | 425.3948 | 424.9438 | 432.9891
2329.4729 | 891.4654 | 425.611 | 425.4588 | 432.9601
2330.4729 | 893.1313 | 425.9657 | 425.7673 | 432.6553
2331.4729 | 903.673 | 425.8849 | 425.687 | 432.3882
2332.4729 | 910.4841 | 426.6149 | 426.1368 | 432.542
2333.4729 | 903.1333 | 426.6664 | 426.4366 | 432.8064
2334.4729 | 910.9481 | 426.6557 | 426.7823 | 433.1626
2335.4729 | 907.48 | 426.7958 | 427.3197 | 433.3014
2336.4729 | 893.107 | 426.4256 | 427.6879 | 433.7543
2337.4729 | 891.0689 | 426.3681 | 426.9338 | 433.5784
2338.4729 | 891.1144 | 426.4711 | 427.0005 | 433.6981
2339.4729 | 883.2195 | 427.0502 | 427.3353 | 433.7066
2340.4729 | 879.2009 | 427.0879 | 427.3226 | 433.7991
2341.4729 | 883.3556 | 427.1302 | 427.0007 | 433.5486
2342.4729 | 873.3429 | 427.1556 | 426.7802 | 432.9352
2343.4729 | 860.3201 | 426.9823 | 426.9567 | 432.6646
2344.4729 | 850.6285 | 426.7927 | 427.1847 | 432.4421
2345.4729 | 852.4539 | 426.6779 | 426.8979 | 432.072
2346.4729 | 848.5404 | 426.2323 | 426.5122 | 431.2884
2347.4729 | 842.3682 | 426.0406 | 426.5004 | 431.819
2348.4729 | 849.2931 | 425.6825 | 426.5043 | 431.4146
2349.4729 | 863.395 | 425.043 | 425.8366 | 430.7832
2350.4729 | 858.9918 | 425.0502 | 425.7755 | 430.3455
2351.4729 | 863.8085 | 425.8695 | 425.8667 | 429.802
2352.4729 | 880.8652 | 425.7383 | 425.2312 | 429.6003
2353.4729 | 893.684 | 426.0015 | 425.398 | 429.5735
2354.4729 | 873.1453 | 425.9131 | 425.0523 | 429.4193
2355.4729 | 843.2017 | 425.5645 | 425.1807 | 429.3047
2356.4729 | 851.5339 | 425.3786 | 425.5112 | 429.8821
2357.4729 | 848.153 | 425.2102 | 425.6552 | 430.1023
2358.4729 | 837.5539 | 425.7549 | 425.559 | 429.7056
2359.4729 | 838.1213 | 425.7792 | 425.1665 | 429.1501
2360.4729 | 854.1513 | 426.1424 | 425.4549 | 429.6493
2361.4729 | 881.1681 | 426.0725 | 425.5628 | 429.6134
2362.4729 | 884.9941 | 425.6964 | 425.4241 | 429.4547
2363.4729 | 875.994 | 425.5743 | 425.0253 | 429.1881
2364.4729 | 875.6178 | 426.0458 | 424.6351 | 429.0113
2365.4729 | 867.8901 | 426.1932 | 424.9153 | 429.0342
2366.4729 | 872.4151 | 425.9258 | 425.2003 | 428.9196
2367.4729 | 867.6052 | 425.5764 | 425.0578 | 428.5983
2368.4729 | 877.5495 | 425.4454 | 424.882 | 428.5045
2369.4729 | 879.1065 | 424.9093 | 424.6936 | 428.5221
2370.4729 | 871.7641 | 425.3437 | 424.4083 | 428.2688
2371.4729 | 877.4727 | 425.0448 | 424.1236 | 428.0359
2372.4729 | 869.4725 | 425.3146 | 424.6767 | 428.0955
2373.4729 | 862.0826 | 425.6051 | 424.7068 | 428.328
2374.4729 | 863.6675 | 425.7606 | 424.818 | 428.2272
2375.4729 | 874.2268 | 425.9093 | 424.9083 | 427.9394
2376.4729 | 877.987 | 426.0398 | 425.0084 | 427.9242
2377.4729 | 883.3967 | 425.9851 | 424.8326 | 427.579
2378.4729 | 880.9236 | 425.9925 | 425.1441 | 427.1155
2379.4729 | 890.1242 | 425.5304 | 425.0094 | 426.7507
2380.4729 | 904.2221 | 425.6539 | 424.4742 | 426.8289
2381.4729 | 900.6684 | 425.2173 | 424.3925 | 427.5968
2382.4729 | 894.7524 | 425.0576 | 424.4108 | 428.5807
2383.4729 | 907.0166 | 425.0305 | 424.6685 | 429.3459
2384.4729 | 902.9051 | 424.9775 | 424.102 | 430.0082
2385.4729 | 911.6862 | 425.0504 | 424.2738 | 429.936
2386.4729 | 922.1765 | 425.1391 | 424.8455 | 430.8882
2387.4729 | 919.3802 | 425.4658 | 424.652 | 430.9971
2388.4729 | 910.0154 | 425.8376 | 424.806 | 431.1051
2389.4729 | 910.3673 | 426.3359 | 424.7971 | 430.9512
2390.4729 | 911.2885 | 426.1729 | 425.3424 | 431.1014
2391.4729 | 902.4714 | 426.6555 | 426.3284 | 431.1276
2392.4729 | 910.6578 | 426.1638 | 426.2001 | 431.3064
2393.4729 | 908.7734 | 426.2117 | 426.4526 | 432.2416
2394.4729 | 903.8908 | 426.4065 | 426.6272 | 432.6427
2395.4729 | 895.9433 | 426.781 | 428.1068 | 432.9534
2396.4729 | 898.7427 | 426.9042 | 428.6896 | 433.5469
2397.4729 | 903.0017 | 427.1413 | 428.3659 | 434.3454
2398.4729 | 900.8212 | 427.1736 | 428.5392 | 434.2437
2399.4729 | 895.6613 | 427.017 | 428.7113 | 434.2879
2400.4729 | 900.0897 | 426.6141 | 428.644 | 434.3291
2401.4885 | 898.635 | 426.0466 | 428.0429 | 433.8412
2402.4729 | 900.1512 | 425.6851 | 427.975 | 433.4786
2403.4729 | 908.2051 | 425.3747 | 427.7397 | 432.6745
2404.4729 | 911.1812 | 425.6913 | 427.3595 | 432.1499
2405.4729 | 901.7017 | 425.6889 | 427.085 | 431.7254
2406.4729 | 895.2269 | 425.6193 | 426.8017 | 431.3449
2407.4729 | 903.1813 | 425.4718 | 426.8885 | 430.9977
2408.4729 | 906.4508 | 425.3017 | 426.7351 | 431.0308
2409.4729 | 913.6957 | 425.5887 | 427.1098 | 431.5638
2410.4729 | 913.4721 | 425.602 | 427.038 | 431.3857
2411.4729 | 900.7245 | 425.6253 | 427.0769 | 431.7524
2412.4729 | 877.7924 | 426.196 | 426.9952 | 431.8344
2413.4729 | 861.2775 | 427.2228 | 427.7833 | 431.7779
2414.4729 | 854.2023 | 427.8489 | 428.2559 | 432.0717
2415.4729 | 862.8551 | 427.9448 | 428.6078 | 432.1225
2416.4729 | 854.8828 | 427.851 | 428.4961 | 431.6974
2417.4729 | 862.4732 | 427.7262 | 428.009 | 431.569
2418.4729 | 876.7568 | 427.1389 | 428.2913 | 431.278
2419.4729 | 875.6178 | 427.2996 | 427.7727 | 430.7378
2420.4729 | 867.8355 | 427.7039 | 427.7781 | 430.4871
2421.4729 | 868.635 | 427.6964 | 427.7662 | 430.6663
2422.4729 | 877.1518 | 427.4701 | 427.2177 | 430.8803
2423.4729 | 885.0995 | 427.335 | 427.4847 | 430.5681
2424.4729 | 878.5266 | 427.8542 | 427.946 | 430.6551
2425.4729 | 874.7151 | 427.5065 | 427.822 | 430.5615
2426.4729 | 875.882 | 426.81 | 427.8071 | 430.3903
2427.4729 | 887.1393 | 426.6523 | 427.766 | 430.1978
2428.4729 | 892.3308 | 426.5892 | 428.0263 | 430.0982
2429.4729 | 891.4797 | 426.4354 | 427.7104 | 430.1006
2430.4729 | 892.5346 | 426.7188 | 427.3683 | 429.5808
2431.4729 | 893.6902 | 427.3751 | 427.5212 | 429.1302
2432.4729 | 894.0031 | 427.0966 | 427.6249 | 429.0163
2433.4729 | 894.4958 | 426.8863 | 427.3643 | 428.7708
2434.4729 | 890.6287 | 426.4737 | 427.3173 | 428.9123
2435.4729 | 874.325 | 426.0555 | 426.9924 | 428.5835
2436.4729 | 864.9354 | 426.3535 | 426.7769 | 428.4984
2437.4729 | 861.6517 | 427.1161 | 427.0544 | 428.3447
2438.4729 | 861.8274 | 427.673 | 426.9244 | 427.9033
2439.4729 | 853.0594 | 427.6775 | 427.1082 | 427.6318
2440.4729 | 849.5737 | 427.1671 | 427.4226 | 427.3725
2441.4729 | 838.3075 | 427.4448 | 427.0963 | 427.115
2442.4729 | 833.3451 | 427.6473 | 427.248 | 426.958
2443.4729 | 841.9466 | 427.4979 | 427.3992 | 427.0153
2444.4729 | 854.3823 | 427.2433 | 427.1573 | 426.8196
2445.4729 | 858.9904 | 427.3616 | 426.9933 | 427.1648
2446.4729 | 865.4984 | 427.4201 | 426.5431 | 427.1952
2447.4729 | 873.9857 | 427.8706 | 426.7228 | 427.4134
2448.4729 | 890.8113 | 427.7897 | 426.4283 | 427.506
2449.4729 | 904.6631 | 427.3845 | 426.3283 | 427.6507
2450.4729 | 890.4672 | 427.5829 | 426.8121 | 427.7753
2451.4729 | 894.0658 | 427.4017 | 426.3712 | 427.5766
2452.4729 | 888.0283 | 427.6624 | 426.9106 | 427.5825
2453.4729 | 892.965 | 427.3177 | 427.1129 | 427.6756
2454.4729 | 899.2576 | 428.0469 | 427.2906 | 427.8897
2455.4729 | 896.1989 | 427.8371 | 427.3083 | 427.9666
2456.4729 | 892.1898 | 427.969 | 427.2982 | 428.4719
2457.4729 | 892.3142 | 428.053 | 427.598 | 429.2996
2458.4729 | 891.5408 | 427.965 | 428.1755 | 429.9588
2459.4729 | 888.1734 | 428.1458 | 428.3256 | 430.5771
2460.4729 | 886.4836 | 428.3873 | 428.757 | 431.3249