## Test Conditions
DESIREE-FIRE Intermediate Scale Test 10 - Circuit Data Only
Test Date: | 2010-03-25
DCSim DAQ Start Time | 10:11
DCSim Time for Synchronization | 10:40
Heat Source Synchronization | 0:00 | hours:minutes:seconds
Heat Source DAQ Start Time | 10:40
Fire Time | 11:27
Offset | 1:16 | hours:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 4560 | seconds
Heat Source Offset | 0:47 | hours:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 2811 | seconds
Heat Source Stop Time | 12:33
Test Duration | 1:06 | hours:minutes:seconds
| 3960 | seconds
CT500 turns | 2 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 turns | 5 | 1 or 5
Pre-Test Baseline: | Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
1" Solenoid Valve | Kerite, 7c, 12AWG, with zinc wrap |  | There are two cable TCs monitoring internal temperatures of the Kerite cable in D Position. Channels 15 and 16 are represented as "D Position - Kerite 7c w - 3'" and "D Position - Kerite 7c w - 5'" in the raw temperature files. | There are three TCs monitoring air temperatures along the middle of the tray in D Position. Channels 12, 13, and 14 are represented as "D Position - 3'", "D Position - Middle", and "D Position - 7'" in the raw temperature files.
Large Coil | Kerite, 9c, 12AWG, without zinc wrap |  | There are two cable TCs monitoring internal temperatures of the Kerite cable in D Position. Channels 17 and 18 are represented as "D Position - Kerite 9c wo - 3'" and "D Position - Kerite 9c wo - 5'" in the raw temperature files. | There are three TCs monitoring air temperatures along the middle of the tray in D Position. Channels 12, 13, and 14 are represented as "D Position - 3'", "D Position - Middle", and "D Position - 7'" in the raw temperature files.
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | 1"Coil_CT500 | 1"Coil_CT35_1_P | 1"Coil_CT35_2_G | 1"Coil_CT35_3_R | 1"Coil_CT35_4_N2 | 1"Coil_CT35_5_S | 1"Coil_CT35_6_N1 | LgCoil_CT500 | LgCoil_CT35_1_P | LgCoil_CT35_2_G | LgCoil_CT35_3_N2 | LgCoil_CT35_4_S | LgCoil_CT35_5_N1 | 1"Coil_VT7_1_G | 1"Coil_VT7_2_R | 1"Coil_VT7_3_SP | 1"Coil_VT7_4_S | 1"Coil_VTU_1_P | 1"Coil_VTU_2_N2 | 1"Coil_VTU_3_N1 | LgCoil_VT7_1_R | LgCoil_VT7_2_SP | LgCoil_VT7_3_S | LgCoil_VTU_1_P | LgCoil_VTU_2_G | LgCoil_VTU_3_N2 | LgCoil_VTU_4_N1 | {1"Valve} V(N2) - V(Batt -) | {1"Valve} V(N1) - V(Batt -) | {1"Valve} V(P) - V(Batt +) | {1"Valve} V(R) - V(Batt -) | {1"Valve} V(S) - V(Batt -) | {1"Valve} V(S) - V(N1) | {1"Valve} V(G) - V(Batt +) | {LgCoil} V(N2) - V(Batt -) | {LgCoil} V(N1) - V(Batt -) | {LgCoil} V(P) - V(Batt +) | {LgCoil} V(R) - V(Batt -) | {LgCoil} V(S) - V(Batt -) | {LgCoil} V(S) - V(N1) | {LgCoil} V(G) - V(Batt +) | {1"Valve} V(P) - V(Batt -) | {1"Valve} V(G) - V(Batt -) | {1"Valve} V(SP) - V(Batt -) | {1"Valve} V(N1) - V(Batt +) | {LgCoil} V(P) - V(Batt -) | {LgCoil} V(G) - V(Batt -) | {LgCoil} V(SP) - V(Batt -) | {LgCoil} V(N1) - V(Batt +)
-1.2812 | 121.9574 | -61.0931 | 60.498 | -0.020218 | 0.0029459 | 0.066042 | 0.0012476 | 0.067543 | -0.0033495 | 0.0011067 | -0.013123 | -0.0046975 | 0.065262 | 0.066328 | -0.19635 | -6.2012e-05 | 60.6354 | -61.0336 | 0.064087 | -61.1435 | 60.3516 | -61.1984 | -61.0565 | -61.5005 | 0.07782 | -61.4319 | 60.3012 | 60.3378 | -60.9009 | -61.116 | -0.10529 | 0.036621 | -0.14648 | 0.05951 | -0.050354 | -0.086975 | 0.13733 | 0.19226 | -0.022888 | -0.19684 | -0.40741 | -0.33875 | -0.31586 | -0.16022 | 121.4447 | 121.7285 | 61.1572 | -121.5546 | 121.3943 | 121.431 | 61.171 | -121.6141
0.46875 | 121.8567 | -61.1664 | 60.5072 | -0.0049592 | -0.0011131 | 0.064119 | 0.0014612 | 0.066048 | 0.0034863 | 0.0015339 | 0.0021363 | 0.0017111 | 0.067398 | 0.06825 | -0.19336 | -0.0043344 | 60.6628 | -61.0382 | 0.073242 | -61.1572 | 60.3973 | -61.2213 | -61.1023 | -61.4777 | 0.10529 | -61.4914 | 60.3287 | 60.3516 | -60.9421 | -61.1572 | -0.054931 | 0.064087 | -0.10986 | 0.12817 | 0.009155 | -0.054932 | 0.15564 | 0.2243 | 0.009155 | -0.17853 | -0.31128 | -0.32501 | -0.33417 | -0.15564 | 121.5637 | 121.8292 | 61.2396 | -121.6095 | 121.4951 | 121.5179 | 61.2717 | -121.6644
2.2188 | 121.907 | -61.0977 | 60.5301 | -0.0049592 | 0.0018777 | 0.069032 | -0.00046138 | 0.068184 | -0.0029223 | -0.00081594 | 0.0021363 | -0.0023477 | 0.065048 | 0.066755 | -0.19464 | 0.0012198 | 60.7224 | -60.9192 | 0.17395 | -61.0886 | 60.3516 | -61.171 | -61.0245 | -61.409 | 0.17395 | -61.3678 | 60.3104 | 60.3928 | -60.8643 | -61.0886 | -0.073242 | 0.073242 | -0.17853 | 0.17853 | 0.009155 | -0.064087 | 0.19226 | 0.23346 | 0.009155 | -0.21973 | -0.31128 | -0.27008 | -0.27924 | -0.13733 | 121.4493 | 121.8201 | 61.2717 | -121.5546 | 121.4081 | 121.4905 | 61.2717 | -121.6187
3.9844 | 121.9666 | -61.0794 | 60.4935 | 0.0026703 | 0.0061501 | 0.0701 | -0.00088858 | 0.068611 | -0.0022815 | -0.0012433 | 0.0097658 | -0.0057657 | 0.065262 | 0.066755 | -0.19677 | -0.00113 | 60.6537 | -60.9924 | 0.09613 | -61.1389 | 60.3333 | -61.1893 | -61.0611 | -61.4456 | 0.12817 | -61.3907 | 60.3378 | 60.3745 | -60.8688 | -61.1069 | -0.10986 | 0.018311 | -0.16022 | 0.086975 | -0.059509 | -0.07782 | 0.16022 | 0.21057 | -0.027466 | -0.15564 | -0.36621 | -0.31128 | -0.28381 | -0.11902 | 121.4127 | 121.7331 | 61.1755 | -121.5546 | 121.4172 | 121.4539 | 61.2076 | -121.6003
5.6719 | 121.9666 | -61.0748 | 60.5118 | 0.0026703 | 0.0048685 | 0.065401 | 0.0023156 | 0.066475 | -0.0035633 | -0.00060234 | -0.0054932 | -0.0032021 | 0.066544 | 0.068037 | -0.19571 | -0.0015572 | 60.7132 | -60.9421 | 0.14648 | -61.0931 | 60.3516 | -61.1618 | -61.0336 | -61.4227 | 0.14648 | -61.3495 | 60.3241 | 60.3607 | -60.8688 | -61.0931 | -0.086975 | 0.041199 | -0.16022 | 0.13275 | -0.018311 | -0.05951 | 0.20142 | 0.20599 | -0.018311 | -0.18768 | -0.3479 | -0.27466 | -0.25635 | -0.15106 | 121.4264 | 121.788 | 61.2213 | -121.5454 | 121.3989 | 121.4355 | 61.2213 | -121.6049
7.3438 | 121.8338 | -61.1114 | 60.5713 | 0.0103 | -0.00047207 | 0.067537 | 0.0057336 | 0.067543 | 0.0015637 | 0.00067926 | -0.0054932 | -0.0019205 | 0.066971 | 0.068464 | -0.19464 | -0.0013436 | 60.6766 | -60.9924 | 0.10986 | -61.1298 | 60.3745 | -61.1526 | -61.0474 | -61.496 | 0.07782 | -61.4822 | 60.3973 | 60.4019 | -60.9009 | -61.1069 | -0.041199 | 0.064087 | -0.19684 | 0.11902 | -0.018311 | -0.082398 | 0.10529 | 0.21057 | 0.004577 | -0.17395 | -0.38452 | -0.37079 | -0.37537 | -0.16937 | 121.4859 | 121.788 | 61.2213 | -121.6187 | 121.5088 | 121.5134 | 61.1893 | -121.6782
9.0312 | 121.8018 | -61.1664 | 60.5072 | 0.0026703 | 0.00059593 | 0.065828 | -0.0019568 | 0.069039 | 0.0036999 | 0.00046566 | -0.013123 | 0.0025657 | 0.066116 | 0.070173 | -0.19122 | -0.0024118 | 60.6674 | -61.0519 | 0.041199 | -61.1755 | 60.3653 | -61.2305 | -61.0886 | -61.5143 | 0.036621 | -61.5463 | 60.2783 | 60.3516 | -60.9512 | -61.1664 | -0.064087 | 0.07782 | -0.14191 | 0.11444 | -0.009155 | -0.086975 | 0.16022 | 0.21515 | 0 | -0.22888 | -0.3479 | -0.37994 | -0.37994 | -0.15564 | 121.5317 | 121.8338 | 61.2076 | -121.5958 | 121.4447 | 121.5179 | 61.203 | -121.6736
10.7188 | 121.9162 | -61.1343 | 60.4202 | -0.0049592 | 0.0059365 | 0.064119 | -0.0045202 | 0.068184 | -0.00057253 | 0.0021747 | 0.0021363 | -0.0010659 | 0.066116 | 0.068464 | -0.19314 | -0.00027561 | 60.6674 | -61.0199 | 0.059509 | -61.1526 | 60.2829 | -61.2396 | -61.0794 | -61.4594 | 0.082397 | -61.4594 | 60.2005 | 60.3058 | -60.9329 | -61.1435 | -0.10529 | 0.054931 | -0.13733 | 0.11444 | -0.018311 | -0.073242 | 0.24719 | 0.20142 | -0.009156 | -0.21973 | -0.32501 | -0.32501 | -0.31586 | -0.11444 | 121.4172 | 121.8018 | 61.1938 | -121.4996 | 121.3348 | 121.4401 | 61.2167 | -121.5637
12.4531 | 121.9299 | -61.1664 | 60.4248 | 0.0026703 | 0.0044411 | 0.06476 | 0.0014612 | 0.065621 | 0.00049567 | 0.0034565 | -0.0054932 | -0.00085232 | 0.064621 | 0.066328 | -0.19357 | -6.2012e-05 | 60.5942 | -61.116 | -0.009155 | -61.2305 | 60.3241 | -61.2579 | -61.1023 | -61.5189 | 0.032043 | -61.5097 | 60.2554 | 60.3012 | -60.9283 | -61.1618 | -0.091553 | 0.064087 | -0.10071 | 0.050354 | -0.064087 | -0.12817 | 0.16937 | 0.23804 | 0.004578 | -0.16937 | -0.35248 | -0.34332 | -0.3479 | -0.1236 | 121.4905 | 121.7606 | 61.1572 | -121.5271 | 121.4218 | 121.4676 | 61.1984 | -121.5866
14.1406 | 121.9482 | -61.1206 | 60.4477 | -0.012589 | 0.0035867 | 0.065401 | -0.00067498 | 0.069893 | 0.00070927 | 0.0034565 | 0.0097658 | -0.00063872 | 0.066757 | 0.068678 | -0.19421 | -0.00048921 | 60.6491 | -61.0245 | 0.045776 | -61.1526 | 60.2875 | -61.2122 | -61.1069 | -61.4731 | 0.082397 | -61.4731 | 60.2554 | 60.3058 | -60.9421 | -61.1389 | -0.091553 | 0.013732 | -0.16022 | 0.09613 | -0.032044 | -0.045776 | 0.20142 | 0.17853 | -0.018311 | -0.19226 | -0.35248 | -0.35248 | -0.33417 | -0.14191 | 121.4081 | 121.7697 | 61.1664 | -121.5546 | 121.376 | 121.4264 | 61.203 | -121.5866
15.8125 | 121.8018 | -61.116 | 60.5576 | -0.0049592 | -0.00025847 | 0.06711 | 0.00060662 | 0.068398 | -0.0020679 | 0.00025206 | 0.0021363 | -0.0014933 | 0.067184 | 0.067182 | -0.19421 | 0.00079259 | 60.6995 | -60.9512 | 0.16022 | -61.0931 | 60.3745 | -61.1618 | -61.0336 | -61.4639 | 0.13733 | -61.4227 | 60.347 | 60.4294 | -60.9009 | -61.0931 | -0.045776 | 0.082398 | -0.1831 | 0.16479 | 0.022888 | -0.05951 | 0.14191 | 0.21515 | 0.022888 | -0.21057 | -0.3479 | -0.3067 | -0.32959 | -0.12817 | 121.4905 | 121.8155 | 61.2762 | -121.5912 | 121.463 | 121.5454 | 61.2534 | -121.6507
17.4844 | 121.8887 | -61.1389 | 60.4797 | 0.0026703 | 0.0063639 | 0.069887 | -0.0017432 | 0.066048 | -0.0027087 | 0.00046566 | -0.0054932 | -0.0032021 | 0.063553 | 0.06825 | -0.19378 | -0.00048921 | 60.6491 | -61.0153 | 0.050354 | -61.1847 | 60.2921 | -61.2122 | -61.0519 | -61.4868 | 0.059509 | -61.4594 | 60.2554 | 60.3287 | -60.8917 | -61.116 | -0.073242 | 0.086975 | -0.18768 | 0.1236 | -0.045776 | -0.13275 | 0.16937 | 0.24719 | 0.022888 | -0.2243 | -0.3479 | -0.32043 | -0.34332 | -0.15106 | 121.431 | 121.788 | 61.1893 | -121.5317 | 121.3943 | 121.4676 | 61.1984 | -121.5958
19.1719 | 121.9254 | -61.0886 | 60.5164 | -0.0049592 | 0.00059593 | 0.068605 | 0.00039302 | 0.066689 | -0.0020679 | 0.0015339 | 0.0097658 | -0.0032021 | 0.065048 | 0.066328 | -0.19507 | 0.0018606 | 60.7361 | -60.8963 | 0.16022 | -61.0657 | 60.3699 | -61.1572 | -61.0291 | -61.4136 | 0.19684 | -61.3403 | 60.3149 | 60.3699 | -60.878 | -61.0748 | -0.068665 | 0.059509 | -0.14648 | 0.19226 | 0.022888 | -0.036621 | 0.21973 | 0.21057 | 0.013733 | -0.20142 | -0.32501 | -0.25177 | -0.2655 | -0.14648 | 121.4584 | 121.8246 | 61.2488 | -121.5454 | 121.4035 | 121.4584 | 61.2854 | -121.5912
20.9219 | 121.9025 | -61.1481 | 60.4706 | 0.0026703 | 0.0027323 | 0.066683 | 0.003811 | 0.068398 | -0.0016405 | -0.0010297 | -0.0054932 | -0.0029885 | 0.065262 | 0.067823 | -0.19528 | -0.00048921 | 60.6537 | -61.0428 | 0.045776 | -61.1618 | 60.3378 | -61.1755 | -61.0519 | -61.5234 | 0.059509 | -61.4594 | 60.2966 | 60.3287 | -60.9238 | -61.116 | -0.027466 | 0.09613 | -0.13275 | 0.10529 | -0.013733 | -0.10986 | 0.18311 | 0.2243 | 0.032043 | -0.17395 | -0.37537 | -0.31128 | -0.34332 | -0.14191 | 121.4859 | 121.8018 | 61.1938 | -121.5225 | 121.4447 | 121.4767 | 61.2076 | -121.5866
22.6094 | 121.8842 | -61.1298 | 60.4385 | -0.0049592 | 0.0038003 | 0.065187 | 0.00017942 | 0.067543 | 0.0024183 | 3.8456e-05 | 0.0097658 | -0.00063872 | 0.067184 | 0.068464 | -0.19421 | -0.002839 | 60.6628 | -60.9924 | 0.054932 | -61.1343 | 60.2692 | -61.2122 | -61.0931 | -61.4594 | 0.086975 | -61.4456 | 60.2371 | 60.26 | -60.9558 | -61.1343 | -0.082397 | 0.036621 | -0.16937 | 0.13733 | -0.004577 | -0.041198 | 0.2243 | 0.17395 | -0.004577 | -0.20142 | -0.32959 | -0.31586 | -0.31128 | -0.17853 | 121.3989 | 121.7926 | 61.1847 | -121.5317 | 121.3669 | 121.3898 | 61.2167 | -121.5729
24.3594 | 121.8613 | -61.0886 | 60.5392 | -0.0049592 | 0.0016641 | 0.066896 | 0.0031702 | 0.066902 | 0.00070927 | 0.0026019 | 0.0021363 | -0.0023477 | 0.066116 | 0.066969 | -0.19507 | -0.0019846 | 60.7452 | -60.91 | 0.16937 | -61.0657 | 60.3378 | -61.1526 | -61.0107 | -61.4182 | 0.16479 | -61.3678 | 60.3195 | 60.3378 | -60.8871 | -61.0886 | -0.064087 | 0.07782 | -0.20142 | 0.17853 | 0.022888 | -0.054932 | 0.20599 | 0.20142 | 0 | -0.21973 | -0.32959 | -0.27924 | -0.27924 | -0.20142 | 121.4264 | 121.8338 | 61.2579 | -121.55 | 121.4081 | 121.4264 | 61.2534 | -121.6278
26.0312 | 121.9391 | -61.1435 | 60.4294 | 0.0026703 | 0.0029459 | 0.065828 | -0.00024778 | 0.067971 | 0.0022047 | 0.0028155 | 0.0021363 | 0.0010703 | 0.063766 | 0.066969 | -0.19421 | -0.0024118 | 60.6033 | -61.0748 | 0 | -61.1938 | 60.2921 | -61.2167 | -61.1069 | -61.4822 | 0.027466 | -61.496 | 60.2463 | 60.3012 | -60.9558 | -61.1343 | -0.073242 | 0.036621 | -0.13733 | 0.068665 | -0.050354 | -0.086975 | 0.17395 | 0.18768 | 0.009156 | -0.1831 | -0.33875 | -0.35248 | -0.36163 | -0.12817 | 121.4355 | 121.7468 | 61.1435 | -121.5363 | 121.3898 | 121.4447 | 61.171 | -121.5637
27.7188 | 121.9116 | -61.1252 | 60.4706 | 0.0026703 | 0.0070047 | 0.069673 | -0.00067498 | 0.069252 | -0.0022815 | 0.0013203 | 0.0021363 | -0.0036295 | 0.06398 | 0.06825 | -0.194 | 0.0014334 | 60.6216 | -61.0107 | 0.036621 | -61.1435 | 60.3424 | -61.1664 | -61.0474 | -61.5005 | 0.041199 | -61.4639 | 60.2829 | 60.3333 | -60.9009 | -61.1114 | -0.041199 | 0.07782 | -0.12817 | 0.11444 | -0.018311 | -0.096131 | 0.15106 | 0.2243 | 0.013733 | -0.18768 | -0.37537 | -0.33875 | -0.35248 | -0.13733 | 121.4676 | 121.7468 | 61.1618 | -121.5179 | 121.4081 | 121.4584 | 61.1664 | -121.582
29.4688 | 121.8475 | -61.116 | 60.5118 | -0.0049592 | -0.0023947 | 0.064974 | 0.00060662 | 0.06733 | 0.00028207 | 0.0019611 | -0.0054932 | 2.078e-06 | 0.068253 | 0.068678 | -0.19485 | -0.00027561 | 60.6445 | -61.0245 | 0.068665 | -61.1481 | 60.3973 | -61.1801 | -61.0245 | -61.5051 | 0.059509 | -61.496 | 60.3882 | 60.4111 | -60.8734 | -61.1252 | -0.064087 | 0.091553 | -0.11444 | 0.091553 | -0.032043 | -0.1236 | 0.13275 | 0.24262 | -0.009155 | -0.1236 | -0.3891 | -0.37994 | -0.37079 | -0.10071 | 121.5134 | 121.7606 | 61.1847 | -121.5363 | 121.5042 | 121.5271 | 61.1755 | -121.637
31.1562 | 121.9482 | -61.1389 | 60.3836 | -0.012589 | 0.0038003 | 0.066469 | -0.0021704 | 0.063912 | 0.0015637 | 0.0026019 | 0.0021363 | 0.00042948 | 0.065903 | 0.065473 | -0.19421 | -0.00048921 | 60.5804 | -61.1069 | -0.027466 | -61.2259 | 60.3149 | -61.2579 | -61.1069 | -61.5189 | 0.018311 | -61.5005 | 60.2875 | 60.3195 | -60.9192 | -61.1755 | -0.11902 | 0.032043 | -0.068665 | 0.032043 | -0.086975 | -0.11902 | 0.19684 | 0.21973 | -0.036621 | -0.09613 | -0.37994 | -0.36163 | -0.32501 | -0.064087 | 121.4539 | 121.7194 | 61.1115 | -121.4905 | 121.4264 | 121.4584 | 61.1572 | -121.5591
32.8438 | 121.788 | -61.1664 | 60.4843 | -0.0049592 | 0.00080973 | 0.065401 | -0.0011024 | 0.068184 | 0.0032727 | 0.0011067 | -0.013123 | 0.00064308 | 0.064407 | 0.06761 | -0.19314 | -0.00048921 | 60.6537 | -61.0565 | 0.054932 | -61.171 | 60.3287 | -61.203 | -61.0977 | -61.5189 | 0.022888 | -61.5417 | 60.3058 | 60.3699 | -60.9467 | -61.1572 | -0.036621 | 0.068665 | -0.15564 | 0.10986 | -0.004577 | -0.073242 | 0.16937 | 0.21973 | 0.009155 | -0.17853 | -0.35248 | -0.37537 | -0.38452 | -0.11444 | 121.4951 | 121.8201 | 61.2213 | -121.582 | 121.4722 | 121.5363 | 61.1893 | -121.6415
34.5312 | 121.788 | -61.1664 | 60.4752 | 0.0026703 | 0.00059593 | 0.063051 | -0.00088858 | 0.067543 | 0.0030591 | 0.0015339 | -0.0054932 | -0.00021152 | 0.06633 | 0.067823 | -0.19592 | -0.00113 | 60.6628 | -61.0336 | 0.091553 | -61.1664 | 60.3287 | -61.1984 | -61.0794 | -61.5051 | 0.054932 | -61.5143 | 60.3149 | 60.3699 | -60.9329 | -61.1572 | -0.032043 | 0.086975 | -0.14648 | 0.13275 | 0 | -0.086975 | 0.18768 | 0.23346 | 0.009155 | -0.16022 | -0.33875 | -0.3479 | -0.35706 | -0.10529 | 121.4951 | 121.8292 | 61.2579 | -121.5546 | 121.4813 | 121.5363 | 61.2213 | -121.6324
36.2188 | 121.7789 | -61.1114 | 60.5759 | 0.0103 | 0.0027323 | 0.066469 | 0.0014612 | 0.068611 | -0.0048449 | 0.0021747 | -0.0054932 | -0.0038431 | 0.066757 | 0.068037 | -0.19912 | 0.00057899 | 60.6995 | -60.9375 | 0.16022 | -61.0794 | 60.3607 | -61.1435 | -60.9924 | -61.4685 | 0.13275 | -61.4273 | 60.3195 | 60.4294 | -60.8963 | -61.0748 | -0.032044 | 0.11902 | -0.21515 | 0.17395 | 0.032043 | -0.086975 | 0.1236 | 0.21515 | 0.036621 | -0.25635 | -0.35706 | -0.31586 | -0.35248 | -0.14649 | 121.4722 | 121.8109 | 61.2717 | -121.5683 | 121.431 | 121.5408 | 61.2442 | -121.6507
37.9844 | 121.8613 | -61.1114 | 60.4889 | 0.0026703 | -0.00068567 | 0.064333 | -0.00088858 | 0.066902 | 0.0030591 | 0.0026019 | -0.013123 | 0.00021568 | 0.066971 | 0.071241 | -0.19442 | -0.0026254 | 60.6354 | -61.0245 | 0.086975 | -61.1343 | 60.3516 | -61.2076 | -61.0657 | -61.4822 | 0.10529 | -61.4685 | 60.3378 | 60.3745 | -60.9329 | -61.1298 | -0.096131 | 0.045776 | -0.13733 | 0.086975 | -0.022888 | -0.068664 | 0.14648 | 0.17853 | -0.018311 | -0.15106 | -0.37079 | -0.35706 | -0.33874 | -0.11444 | 121.463 | 121.7468 | 61.1984 | -121.5546 | 121.4493 | 121.4859 | 61.2167 | -121.6187
39.7344 | 121.9299 | -61.0886 | 60.5072 | -0.012589 | 0.0050821 | 0.067964 | -0.00067498 | 0.067116 | -0.0056995 | -0.00081594 | 0.0021363 | -0.0029885 | 0.06633 | 0.06761 | -0.19912 | 0.001647 | 60.6812 | -60.9375 | 0.11444 | -61.084 | 60.3424 | -61.1435 | -61.0245 | -61.4227 | 0.15564 | -61.3449 | 60.3012 | 60.3699 | -60.8826 | -61.0794 | -0.054932 | 0.064087 | -0.16479 | 0.15106 | 0.004578 | -0.059509 | 0.17395 | 0.20599 | 0.009155 | -0.20599 | -0.33417 | -0.25635 | -0.2655 | -0.13733 | 121.431 | 121.7697 | 61.203 | -121.5317 | 121.3898 | 121.4584 | 61.2442 | -121.5866
41.4062 | 121.843 | -61.1343 | 60.4935 | 0.0103 | 0.00038233 | 0.063478 | -0.00067498 | 0.066475 | 0.0039135 | 0.0011067 | -0.0054932 | 0.0010703 | 0.066757 | 0.069532 | -0.19378 | -0.0024118 | 60.6628 | -61.0199 | 0.07782 | -61.1481 | 60.3836 | -61.1938 | -61.0703 | -61.4685 | 0.10071 | -61.4777 | 60.3378 | 60.3424 | -60.9421 | -61.1069 | -0.05951 | 0.064087 | -0.10986 | 0.11444 | -0.013733 | -0.07782 | 0.16937 | 0.19226 | 0.027465 | -0.15564 | -0.33417 | -0.34332 | -0.37079 | -0.15106 | 121.5179 | 121.7972 | 61.2122 | -121.5637 | 121.4722 | 121.4767 | 61.235 | -121.6003
43.1719 | 121.9482 | -61.0474 | 60.498 | -0.012589 | 0.0025185 | 0.067323 | 0.002102 | 0.066048 | -0.0065539 | -0.00017514 | 0.0021363 | -0.0059793 | 0.066544 | 0.066328 | -0.19977 | -0.0019846 | 60.6628 | -60.9467 | 0.12817 | -61.0977 | 60.3287 | -61.1664 | -60.997 | -61.4319 | 0.13733 | -61.3541 | 60.3104 | 60.3561 | -60.8871 | -61.0931 | -0.11902 | 0.050354 | -0.16937 | 0.10071 | -0.050354 | -0.10071 | 0.16479 | 0.16022 | -0.045777 | -0.18768 | -0.38452 | -0.3067 | -0.26093 | -0.14191 | 121.376 | 121.7102 | 61.1755 | -121.4951 | 121.3577 | 121.4035 | 61.1847 | -121.5912
44.9375 | 121.843 | -61.1343 | 60.4889 | 0.0026703 | 0.00059593 | 0.066042 | -3.4178e-05 | 0.065407 | 0.0043409 | 0.0015339 | 0.0021363 | 0.0034201 | 0.068253 | 0.068678 | -0.19272 | -0.00091641 | 60.6445 | -61.0153 | 0.086975 | -61.1389 | 60.379 | -61.1984 | -61.0382 | -61.4777 | 0.091553 | -61.4731 | 60.3333 | 60.3378 | -60.9192 | -61.1343 | -0.064087 | 0.09613 | -0.10986 | 0.11902 | -0.004578 | -0.10071 | 0.15564 | 0.21515 | 0 | -0.15564 | -0.34332 | -0.33875 | -0.33875 | -0.15106 | 121.5134 | 121.7789 | 61.2213 | -121.5271 | 121.4676 | 121.4722 | 61.2259 | -121.6232
46.625 | 121.8109 | -61.1389 | 60.4706 | -0.012589 | 0.0018777 | 0.062196 | -0.00067498 | 0.068398 | 0.0030591 | 0.0026019 | -0.0054932 | -0.00042512 | 0.067825 | 0.068037 | -0.19656 | -0.0013436 | 60.6628 | -61.0199 | 0.07782 | -61.1298 | 60.3561 | -61.203 | -61.0748 | -61.4548 | 0.10529 | -61.4685 | 60.3378 | 60.3836 | -60.9283 | -61.1343 | -0.064087 | 0.064087 | -0.11444 | 0.11902 | 0.009155 | -0.054932 | 0.19226 | 0.21057 | 0.004578 | -0.13275 | -0.31586 | -0.32959 | -0.33417 | -0.086975 | 121.4951 | 121.8018 | 61.2167 | -121.5454 | 121.4767 | 121.5225 | 61.2442 | -121.6049
48.3594 | 121.9254 | -61.084 | 60.5026 | 0.0026703 | 0.0033731 | 0.066683 | 0.002102 | 0.068398 | -0.0061267 | 3.8456e-05 | -0.0054932 | -0.0040567 | 0.067825 | 0.067823 | -0.19998 | -0.00091641 | 60.6995 | -60.878 | 0.17395 | -61.0794 | 60.3195 | -61.1389 | -61.0062 | -61.3998 | 0.16937 | -61.3312 | 60.2966 | 60.3287 | -60.8688 | -61.0977 | -0.054932 | 0.077819 | -0.18311 | 0.20599 | 0.004577 | -0.073242 | 0.19684 | 0.21515 | -0.013733 | -0.20599 | -0.31586 | -0.24719 | -0.23346 | -0.17395 | 121.4035 | 121.7834 | 61.2579 | -121.5088 | 121.3806 | 121.4127 | 61.2534 | -121.6003
50.0625 | 121.7697 | -61.1664 | 60.4843 | -0.0049592 | -4.4874e-05 | 0.064119 | -0.00046138 | 0.066048 | 0.0034863 | 0.0013203 | 0.0021363 | 0.0012839 | 0.067398 | 0.066542 | -0.19357 | -0.00027561 | 60.5896 | -61.084 | 0.027466 | -61.1938 | 60.3516 | -61.2076 | -61.0931 | -61.5463 | 0.009155 | -61.5463 | 60.3012 | 60.3241 | -60.9604 | -61.1664 | -0.041199 | 0.073242 | -0.13275 | 0.082398 | -0.027466 | -0.10071 | 0.10529 | 0.20599 | 0 | -0.18311 | -0.37994 | -0.37994 | -0.37994 | -0.16022 | 121.5179 | 121.756 | 61.1938 | -121.5775 | 121.4676 | 121.4905 | 61.1755 | -121.6507
51.7969 | 121.8796 | -61.1343 | 60.4385 | 0.0026703 | 0.0046549 | 0.068605 | -0.0011024 | 0.067116 | -0.0033495 | 0.00025206 | -0.0054932 | -0.0032021 | 0.065048 | 0.066755 | -0.19742 | 0.00036539 | 60.64 | -60.9924 | 0.050354 | -61.1526 | 60.2829 | -61.2167 | -61.0886 | -61.5097 | 0.064087 | -61.4456 | 60.2188 | 60.3241 | -60.9238 | -61.1481 | -0.082398 | 0.045776 | -0.15564 | 0.14191 | -0.018311 | -0.064087 | 0.20142 | 0.21057 | -0.013733 | -0.21973 | -0.37537 | -0.31128 | -0.29755 | -0.11444 | 121.4172 | 121.7743 | 61.1847 | -121.5271 | 121.3531 | 121.4584 | 61.1984 | -121.5866
53.4688 | 121.8063 | -61.1755 | 60.4752 | 0.0026703 | -0.0021811 | 0.063905 | 0.0012476 | 0.064553 | 0.0060499 | 0.0021747 | -0.013123 | 0.00085668 | 0.067398 | 0.070387 | -0.19571 | -0.0032662 | 60.5347 | -61.1526 | -0.022888 | -61.1984 | 60.3516 | -61.2259 | -61.1114 | -61.5875 | -0.054932 | -61.6013 | 60.2966 | 60.3195 | -60.9558 | -61.1938 | -0.050354 | 0.064087 | -0.1236 | 0.022888 | -0.022888 | -0.086975 | 0.059509 | 0.21973 | -0.018311 | -0.17853 | -0.41199 | -0.42572 | -0.40741 | -0.15564 | 121.5271 | 121.7102 | 61.1526 | -121.5866 | 121.4722 | 121.4951 | 61.1206 | -121.669
55.25 | 121.9162 | -61.1069 | 60.4752 | -0.0049592 | 0.0046549 | 0.066469 | 0.00017942 | 0.066902 | -0.0042041 | -0.0018841 | 0.0097658 | -0.0029885 | 0.064621 | 0.065901 | -0.19742 | -0.00070281 | 60.6308 | -61.0107 | 0.032043 | -61.1572 | 60.3149 | -61.171 | -61.0519 | -61.5189 | 0.041199 | -61.4548 | 60.2692 | 60.3287 | -60.8917 | -61.1252 | -0.064086 | 0.054932 | -0.16022 | 0.096131 | -0.050354 | -0.10529 | 0.15564 | 0.21515 | -0.01831 | -0.20599 | -0.41199 | -0.3479 | -0.32959 | -0.14648 | 121.4218 | 121.7377 | 61.1389 | -121.5271 | 121.376 | 121.4355 | 61.1481 | -121.6003
57 | 121.9162 | -61.1618 | 60.4156 | 0.0026703 | 0.0016641 | 0.063478 | -0.003025 | 0.06498 | 0.0022047 | 0.0015339 | -0.013123 | 0.0019247 | 0.064621 | 0.069959 | -0.19293 | -0.0019846 | 60.5896 | -61.1023 | -0.032043 | -61.2167 | 60.3378 | -61.235 | -61.0931 | -61.5234 | -0.018311 | -61.5189 | 60.2646 | 60.3149 | -60.9421 | -61.1526 | -0.073242 | 0.068664 | -0.077819 | 0.059509 | -0.054932 | -0.1236 | 0.17395 | 0.21973 | 0.009155 | -0.15106 | -0.36163 | -0.35706 | -0.36621 | -0.10071 | 121.4996 | 121.7514 | 61.1298 | -121.5088 | 121.4264 | 121.4767 | 61.1435 | -121.5683
58.6875 | 121.8887 | -61.1389 | 60.4156 | -0.0049592 | 0.00038233 | 0.064974 | -0.0019568 | 0.067971 | 0.0013501 | 0.0017475 | 0.0021363 | 0.00042948 | 0.066971 | 0.068464 | -0.19357 | -0.00070281 | 60.5713 | -61.1343 | -0.041199 | -61.2167 | 60.3241 | -61.2396 | -61.1206 | -61.5646 | -0.009155 | -61.5463 | 60.2875 | 60.3333 | -60.9512 | -61.1572 | -0.10071 | 0.018311 | -0.091552 | 0.004578 | -0.07782 | -0.096131 | 0.15564 | 0.18768 | -0.018311 | -0.12817 | -0.42572 | -0.40741 | -0.3891 | -0.082397 | 121.463 | 121.7102 | 61.0977 | -121.5363 | 121.4264 | 121.4722 | 61.1298 | -121.5729
60.4375 | 121.8292 | -61.0931 | 60.5347 | 0.0026703 | -0.00068567 | 0.067751 | 0.0027428 | 0.067116 | -0.0050585 | -0.00017514 | -0.0054932 | -0.0036295 | 0.065475 | 0.066969 | -0.19507 | -0.00091641 | 60.704 | -60.9055 | 0.16937 | -61.0657 | 60.3241 | -61.1298 | -61.0199 | -61.4136 | 0.16479 | -61.3586 | 60.3058 | 60.3836 | -60.8688 | -61.0611 | -0.036621 | 0.073243 | -0.21057 | 0.18768 | 0.027466 | -0.045777 | 0.16937 | 0.22431 | 0.032044 | -0.22888 | -0.32043 | -0.2655 | -0.29755 | -0.15106 | 121.4172 | 121.7972 | 61.2625 | -121.5546 | 121.3989 | 121.4767 | 61.2579 | -121.5958
62.1875 | 121.9208 | -61.0657 | 60.4706 | -0.0049592 | 0.0023049 | 0.069032 | -0.00046138 | 0.065621 | -0.0039905 | -0.00081594 | 0.0021363 | -0.0034159 | 0.064194 | 0.066755 | -0.19613 | -0.00027561 | 60.6216 | -60.997 | 0.059509 | -61.1298 | 60.3333 | -61.1572 | -61.0245 | -61.4777 | 0.10071 | -61.3815 | 60.2692 | 60.3424 | -60.8643 | -61.0931 | -0.091553 | 0.041199 | -0.13733 | 0.068665 | -0.064087 | -0.10529 | 0.15106 | 0.20142 | -0.027466 | -0.20142 | -0.41199 | -0.31586 | -0.28839 | -0.12817 | 121.3989 | 121.6873 | 61.1252 | -121.4951 | 121.3348 | 121.4081 | 61.1664 | -121.5637
63.875 | 121.9208 | -61.1481 | 60.3928 | 0.0026703 | 0.0012369 | 0.067323 | 0.00017942 | 0.067971 | 0.0028455 | 0.0015339 | -0.0054932 | -0.00021152 | 0.068466 | 0.06761 | -0.19464 | -0.0013436 | 60.6079 | -61.0245 | 0.027466 | -61.1618 | 60.2829 | -61.2122 | -61.0977 | -61.4685 | 0.059509 | -61.4594 | 60.2417 | 60.2829 | -60.9512 | -61.1389 | -0.064087 | 0.050354 | -0.10986 | 0.1236 | -0.013733 | -0.064087 | 0.21515 | 0.19684 | 0.009155 | -0.15106 | -0.32043 | -0.31128 | -0.32043 | -0.10986 | 121.431 | 121.756 | 61.1755 | -121.4905 | 121.3898 | 121.431 | 61.2076 | -121.5317
65.5625 | 121.8979 | -61.1572 | 60.4156 | 0.0026703 | 0.0050821 | 0.067323 | -0.00046138 | 0.065407 | 0.0034863 | 0.00025206 | -0.0054932 | -0.00063872 | 0.067398 | 0.066969 | -0.1925 | -0.0030526 | 60.5713 | -61.0931 | -0.036621 | -61.2122 | 60.3333 | -61.2213 | -61.1069 | -61.528 | 0.004578 | -61.5189 | 60.2692 | 60.2737 | -60.9375 | -61.1526 | -0.064086 | 0.050354 | -0.082397 | 0.064087 | -0.054931 | -0.10529 | 0.15564 | 0.21973 | 0.004578 | -0.14648 | -0.37079 | -0.36163 | -0.36621 | -0.14191 | 121.4905 | 121.7285 | 61.1206 | -121.5225 | 121.4264 | 121.431 | 61.1618 | -121.5683
67.2344 | 121.9254 | -61.0703 | 60.4706 | 0.0026703 | 0.0048685 | 0.067323 | 0.0018884 | 0.066689 | -0.0046313 | -0.00017514 | -0.0054932 | -0.0044839 | 0.065262 | 0.067182 | -0.19549 | 0.00015159 | 60.6171 | -61.0107 | 0.059509 | -61.1343 | 60.3241 | -61.1847 | -61.0611 | -61.4777 | 0.082397 | -61.409 | 60.2966 | 60.3424 | -60.8826 | -61.116 | -0.11444 | 0.009155 | -0.14648 | 0.059509 | -0.064087 | -0.073242 | 0.14648 | 0.18768 | -0.045777 | -0.17395 | -0.40741 | -0.33875 | -0.29297 | -0.12817 | 121.3943 | 121.6873 | 61.1298 | -121.5317 | 121.3669 | 121.4127 | 61.1526 | -121.5866
68.9219 | 121.9299 | -61.0703 | 60.4752 | -0.0049592 | 0.0031595 | 0.067751 | 0.0031702 | 0.068611 | -0.0027087 | -0.00081594 | 0.0021363 | -0.0034159 | 0.067398 | 0.068037 | -0.1972 | -0.00113 | 60.64 | -60.9695 | 0.086975 | -61.1252 | 60.3241 | -61.1526 | -61.0336 | -61.441 | 0.1236 | -61.377 | 60.2875 | 60.3424 | -60.8734 | -61.0794 | -0.082398 | 0.036621 | -0.15106 | 0.10071 | -0.054932 | -0.091553 | 0.1648 | 0.19684 | -0.009156 | -0.18768 | -0.37079 | -0.3067 | -0.29755 | -0.13275 | 121.3943 | 121.7102 | 61.1572 | -121.5088 | 121.3577 | 121.4127 | 61.1938 | -121.5546
70.6719 | 121.9116 | -61.0519 | 60.4843 | -0.0049592 | 0.0055093 | 0.067537 | 0.0016748 | 0.06968 | -0.0014269 | 0.00067926 | -0.0054932 | -0.0021341 | 0.065903 | 0.066969 | -0.19784 | -0.0034798 | 60.6995 | -60.8963 | 0.15106 | -61.0794 | 60.3287 | -61.1343 | -60.9879 | -61.3998 | 0.16937 | -61.322 | 60.2966 | 60.3699 | -60.8551 | -61.0657 | -0.082397 | 0.064087 | -0.15564 | 0.15564 | -0.027466 | -0.091553 | 0.21515 | 0.19684 | -0.013733 | -0.18768 | -0.3479 | -0.27008 | -0.25635 | -0.11444 | 121.3806 | 121.7514 | 61.203 | -121.4722 | 121.3486 | 121.4218 | 61.2213 | -121.55
72.3438 | 121.8292 | -61.1435 | 60.498 | -0.0049592 | -0.0021811 | 0.061342 | 0.0031702 | 0.06733 | 0.0056225 | 0.0019611 | -0.0054932 | 0.0019247 | 0.068039 | 0.068891 | -0.19314 | -0.0021982 | 60.6583 | -61.0107 | 0.082397 | -61.1206 | 60.3561 | -61.1801 | -61.0611 | -61.4548 | 0.091553 | -61.4594 | 60.3241 | 60.3653 | -60.8963 | -61.1114 | -0.036621 | 0.082398 | -0.14191 | 0.13275 | 0.022889 | -0.059509 | 0.16022 | 0.24719 | 0.032044 | -0.17395 | -0.31128 | -0.31586 | -0.3479 | -0.13275 | 121.4996 | 121.8018 | 61.2259 | -121.5591 | 121.4676 | 121.5088 | 61.235 | -121.6095
74.0938 | 121.7834 | -61.1023 | 60.5484 | -0.0049592 | -0.00025847 | 0.066042 | -0.001316 | 0.065621 | -0.00099973 | -0.00017514 | -0.0054932 | -0.00063872 | 0.066757 | 0.068037 | -0.19699 | -6.2012e-05 | 60.6445 | -60.9833 | 0.09613 | -61.116 | 60.3607 | -61.1618 | -61.0474 | -61.4868 | 0.07782 | -61.4639 | 60.3699 | 60.4111 | -60.8963 | -61.0886 | -0.059509 | 0.054932 | -0.18768 | 0.11902 | -0.013733 | -0.068665 | 0.09613 | 0.20599 | 0.013733 | -0.17853 | -0.38452 | -0.36163 | -0.37537 | -0.13733 | 121.463 | 121.7468 | 61.1984 | -121.5958 | 121.4722 | 121.5134 | 61.1801 | -121.637
75.7812 | 121.9299 | -61.0611 | 60.4797 | 0.0026703 | 0.0048685 | 0.066896 | -0.0028112 | 0.066048 | -0.0039905 | -0.0014569 | -0.0054932 | -0.0029885 | 0.064621 | 0.069105 | -0.19763 | -0.00027561 | 60.6262 | -61.0016 | 0.054932 | -61.1252 | 60.3241 | -61.1801 | -61.0428 | -61.4685 | 0.07782 | -61.4136 | 60.2829 | 60.3561 | -60.878 | -61.084 | -0.11902 | 0.01831 | -0.15564 | 0.059509 | -0.064087 | -0.082397 | 0.14648 | 0.1831 | -0.022888 | -0.19684 | -0.40741 | -0.35248 | -0.32959 | -0.1236 | 121.3852 | 121.6873 | 61.116 | -121.5225 | 121.344 | 121.4172 | 61.1389 | -121.5637
77.4688 | 121.7972 | -61.0703 | 60.5576 | -0.012589 | -0.0019675 | 0.066255 | 0.0035974 | 0.069039 | -0.00078613 | 0.00025206 | 0.0097658 | -0.00063872 | 0.067398 | 0.068678 | -0.19549 | -0.0024118 | 60.6949 | -60.9283 | 0.14648 | -61.0794 | 60.3516 | -61.1298 | -61.0153 | -61.4502 | 0.10071 | -61.4273 | 60.3241 | 60.3745 | -60.8688 | -61.0565 | -0.05951 | 0.054931 | -0.20599 | 0.14191 | -0.009156 | -0.064087 | 0.13733 | 0.20142 | 0.013732 | -0.23346 | -0.37994 | -0.35706 | -0.37079 | -0.1831 | 121.4218 | 121.7651 | 61.2167 | -121.5729 | 121.3943 | 121.4447 | 61.171 | -121.6141
79.2344 | 121.7972 | -61.1206 | 60.5484 | 0.0026703 | 0.00016873 | 0.067537 | -0.00088858 | 0.064766 | 0.0013501 | 0.0019611 | -0.0054932 | 0.00085668 | 0.065262 | 0.06761 | -0.19464 | -0.0013436 | 60.6262 | -61.0153 | 0.068665 | -61.1252 | 60.4156 | -61.1526 | -61.0245 | -61.4822 | 0.068665 | -61.4777 | 60.3653 | 60.4294 | -60.8734 | -61.0886 | -0.032044 | 0.09613 | -0.13275 | 0.10528 | -0.004578 | -0.10071 | 0.07782 | 0.24719 | 0.032043 | -0.18311 | -0.36163 | -0.35706 | -0.3891 | -0.11902 | 121.5363 | 121.7468 | 61.1893 | -121.5729 | 121.4859 | 121.55 | 61.1893 | -121.637
80.9375 | 121.7789 | -61.1938 | 60.4614 | -0.0049592 | 0.00059593 | 0.064333 | 0.00060662 | 0.065834 | 0.0049817 | 0.0028155 | 0.0021363 | -0.00042512 | 0.065262 | 0.070387 | -0.1925 | -0.00048921 | 60.553 | -61.1298 | -0.032043 | -61.2167 | 60.3378 | -61.2396 | -61.0886 | -61.5738 | -0.018311 | -61.5601 | 60.2829 | 60.3333 | -60.9421 | -61.171 | -0.045776 | 0.10529 | -0.1236 | 0.064087 | -0.022888 | -0.12817 | 0.091553 | 0.25177 | 0.022889 | -0.17853 | -0.37994 | -0.36621 | -0.3891 | -0.12817 | 121.5317 | 121.7468 | 61.1618 | -121.55 | 121.4767 | 121.5271 | 61.1755 | -121.6324
82.6875 | 121.7743 | -61.1755 | 60.4385 | 0.0026703 | -0.0036765 | 0.062837 | -3.4178e-05 | 0.068398 | 0.0032727 | 0.0034565 | -0.0054932 | 2.078e-06 | 0.064835 | 0.067396 | -0.19314 | -0.0021982 | 60.6491 | -61.0016 | 0.086975 | -61.1343 | 60.3287 | -61.1938 | -61.0794 | -61.4639 | 0.091553 | -61.4731 | 60.3058 | 60.3516 | -60.9238 | -61.1206 | -0.018311 | 0.09613 | -0.10986 | 0.17395 | 0.041199 | -0.054931 | 0.21057 | 0.25177 | 0.054932 | -0.13275 | -0.28839 | -0.29755 | -0.35248 | -0.086976 | 121.5042 | 121.8246 | 61.2625 | -121.5179 | 121.4813 | 121.5271 | 61.2671 | -121.5591
84.3594 | 121.7926 | -61.1664 | 60.4202 | 0.0026703 | -4.4874e-05 | 0.063692 | -0.002384 | 0.065407 | 0.0017773 | 0.0021747 | -0.0054932 | 0.00021568 | 0.067612 | 0.0706 | -0.19378 | 0.0010062 | 60.5072 | -61.1389 | -0.032043 | -61.2122 | 60.3378 | -61.2213 | -61.0931 | -61.5646 | -0.036621 | -61.5738 | 60.2829 | 60.347 | -60.965 | -61.1664 | -0.054931 | 0.073242 | -0.082397 | 0.027466 | -0.045776 | -0.11902 | 0.086975 | 0.20142 | 0 | -0.13733 | -0.39825 | -0.40741 | -0.40741 | -0.073242 | 121.5042 | 121.6736 | 61.1343 | -121.5134 | 121.4493 | 121.5134 | 61.1298 | -121.5866
86.0469 | 121.8567 | -61.116 | 60.4431 | -0.0049592 | 0.0042275 | 0.069032 | 0.00039302 | 0.067757 | -0.0035633 | 0.0011067 | -0.013123 | -0.0044839 | 0.064407 | 0.068891 | -0.19763 | 0.0025016 | 60.5988 | -61.0062 | 0.050354 | -61.1572 | 60.2829 | -61.1893 | -61.0565 | -61.496 | 0.064087 | -61.441 | 60.2463 | 60.2921 | -60.8826 | -61.1389 | -0.073242 | 0.059509 | -0.16022 | 0.10986 | -0.041199 | -0.10071 | 0.15564 | 0.23346 | -0.022888 | -0.19684 | -0.37994 | -0.32501 | -0.30212 | -0.15106 | 121.3989 | 121.7148 | 61.1664 | -121.4996 | 121.3623 | 121.4081 | 61.1801 | -121.582
87.7344 | 121.9254 | -61.0977 | 60.4843 | -0.0049592 | 0.0052957 | 0.067537 | 0.0035974 | 0.066689 | -0.0046313 | 0.0013203 | -0.0054932 | -0.0061929 | 0.065048 | 0.070173 | -0.19806 | -0.00048921 | 60.6033 | -60.9924 | 0.073242 | -61.0977 | 60.3058 | -61.1572 | -61.0245 | -61.4639 | 0.10071 | -61.3953 | 60.3012 | 60.3104 | -60.8917 | -61.0703 | -0.05951 | 0.073242 | -0.17853 | 0.10529 | 0 | -0.073242 | 0.11902 | 0.20599 | 0.027466 | -0.18311 | -0.36621 | -0.29755 | -0.32501 | -0.17395 | 121.4035 | 121.7011 | 61.171 | -121.5088 | 121.3989 | 121.4081 | 61.1984 | -121.5546
89.4688 | 121.8567 | -61.1618 | 60.4111 | 0.0103 | 0.0042275 | 0.06476 | -0.002384 | 0.066689 | 0.0039135 | 0.0019611 | -0.0054932 | 0.00064308 | 0.066757 | 0.067823 | -0.19186 | -0.00070281 | 60.5484 | -61.1298 | -0.059509 | -61.2076 | 60.347 | -61.2305 | -61.0748 | -61.5601 | -0.022888 | -61.5463 | 60.2875 | 60.3287 | -60.9512 | -61.1664 | -0.068665 | 0.086975 | -0.064087 | 0.032043 | -0.045777 | -0.13275 | 0.13733 | 0.21057 | -0.004578 | -0.1236 | -0.39826 | -0.38452 | -0.37994 | -0.082398 | 121.5088 | 121.7102 | 61.1023 | -121.4859 | 121.4493 | 121.4905 | 61.1389 | -121.5775
91.25 | 121.8246 | -61.1298 | 60.4248 | 0.0103 | 0.0010233 | 0.066683 | -0.00067498 | 0.066048 | 0.00092287 | 0.00046566 | 0.0021363 | 0.00064308 | 0.06633 | 0.067396 | -0.19058 | -0.00070281 | 60.5301 | -61.1206 | -0.045776 | -61.2076 | 60.3149 | -61.235 | -61.1252 | -61.5692 | -0.022888 | -61.5555 | 60.3149 | 60.3195 | -60.9467 | -61.1755 | -0.10528 | 0.004578 | -0.10986 | 0.009156 | -0.07782 | -0.082398 | 0.10529 | 0.18311 | -0.045776 | -0.10986 | -0.43945 | -0.42572 | -0.37994 | -0.10529 | 121.4447 | 121.6599 | 61.084 | -121.55 | 121.4447 | 121.4493 | 61.1069 | -121.6003
93.0156 | 121.8018 | -61.1114 | 60.466 | 0.0026703 | -0.0043173 | 0.065401 | 0.0018884 | 0.067543 | 0.0017773 | 0.0021747 | -0.013123 | -0.0010659 | 0.065262 | 0.069105 | -0.194 | -0.00113 | 60.6354 | -60.997 | 0.09613 | -61.116 | 60.3745 | -61.1618 | -61.0474 | -61.4548 | 0.10071 | -61.4456 | 60.2966 | 60.3378 | -60.9009 | -61.1252 | -0.050354 | 0.064087 | -0.091552 | 0.11444 | -0.004578 | -0.068665 | 0.16937 | 0.21057 | -0.013733 | -0.16937 | -0.34332 | -0.33417 | -0.32044 | -0.12817 | 121.4859 | 121.7468 | 61.2076 | -121.5134 | 121.4081 | 121.4493 | 61.2122 | -121.5912
94.7188 | 121.7651 | -61.1801 | 60.4568 | -0.0049592 | -0.0011131 | 0.064333 | -0.00024778 | 0.067971 | 0.0019909 | 0.0038837 | 0.0021363 | 0.0029929 | 0.066757 | 0.06761 | -0.194 | 0.00079259 | 60.5484 | -61.0886 | -0.013733 | -61.1893 | 60.3241 | -61.2167 | -61.0886 | -61.5509 | 0 | -61.5509 | 60.2692 | 60.347 | -60.9375 | -61.1618 | -0.036621 | 0.091553 | -0.13275 | 0.091553 | -0.009155 | -0.10071 | 0.091553 | 0.24262 | 0.018311 | -0.18768 | -0.37079 | -0.37079 | -0.3891 | -0.10986 | 121.5042 | 121.7285 | 61.1664 | -121.5454 | 121.4493 | 121.5271 | 61.1801 | -121.6187
96.4688 | 121.8155 | -61.1526 | 60.4202 | -0.0049592 | -0.00068567 | 0.065828 | -0.0015296 | 0.065407 | 0.0015637 | 0.0023883 | -0.013123 | 0.00064308 | 0.065475 | 0.069105 | -0.19507 | -0.0013436 | 60.5209 | -61.1389 | -0.045776 | -61.2122 | 60.3195 | -61.2167 | -61.0977 | -61.5829 | -0.032043 | -61.5555 | 60.2783 | 60.3378 | -60.9604 | -61.171 | -0.064087 | 0.054932 | -0.10071 | 0.013733 | -0.059509 | -0.11444 | 0.10071 | 0.19226 | -0.01831 | -0.14191 | -0.4303 | -0.40283 | -0.38452 | -0.082397 | 121.4722 | 121.6736 | 61.1069 | -121.5179 | 121.431 | 121.4905 | 61.1206 | -121.5912
98.25 | 121.9162 | -61.116 | 60.3928 | -0.0049592 | 0.0050821 | 0.065401 | 0.0018884 | 0.066689 | -0.00057253 | 0.0047383 | 0.0021363 | -0.0014933 | 0.067184 | 0.068037 | -0.194 | -6.2012e-05 | 60.5804 | -61.0382 | 0.018311 | -61.1435 | 60.2966 | -61.1984 | -61.0703 | -61.4822 | 0.064087 | -61.441 | 60.2234 | 60.3012 | -60.9558 | -61.1389 | -0.082397 | 0.045777 | -0.09613 | 0.07782 | -0.027466 | -0.073243 | 0.18768 | 0.16022 | -0.022888 | -0.16937 | -0.36621 | -0.32501 | -0.30212 | -0.091553 | 121.4127 | 121.6965 | 61.1343 | -121.463 | 121.3394 | 121.4172 | 61.1801 | -121.5317
99.9844 | 121.8475 | -61.0657 | 60.5118 | 0.0026703 | 0.0042275 | 0.069887 | -0.00024778 | 0.069039 | -0.0061267 | 0.0023883 | -0.0054932 | -0.0044839 | 0.066116 | 0.066114 | -0.19806 | 0.00015159 | 60.6903 | -60.8734 | 0.16479 | -61.0474 | 60.3149 | -61.0931 | -60.9787 | -61.3998 | 0.1831 | -61.3312 | 60.2875 | 60.3516 | -60.8597 | -61.0703 | -0.027466 | 0.086975 | -0.19684 | 0.19226 | 0.018311 | -0.068664 | 0.17853 | 0.20599 | -0.004577 | -0.2243 | -0.33417 | -0.2655 | -0.26093 | -0.16022 | 121.3806 | 121.756 | 61.2305 | -121.4905 | 121.3531 | 121.4172 | 61.2488 | -121.582
101.7344 | 121.756 | -61.0748 | 60.5392 | 0.0026703 | 0.0010233 | 0.06711 | 0.0029566 | 0.065621 | -0.0035633 | -0.00060234 | 0.0021363 | -0.0019205 | 0.069107 | 0.066328 | -0.19592 | -0.0015572 | 60.6949 | -60.9192 | 0.16479 | -61.0565 | 60.347 | -61.1206 | -61.0016 | -61.4548 | 0.11444 | -61.3907 | 60.3333 | 60.4019 | -60.8688 | -61.084 | -0.045776 | 0.073242 | -0.19226 | 0.15564 | 0.01831 | -0.054932 | 0.15564 | 0.20599 | -0.009155 | -0.20599 | -0.37994 | -0.31586 | -0.3067 | -0.13733 | 121.4218 | 121.7697 | 61.2396 | -121.5408 | 121.4081 | 121.4767 | 61.1893 | -121.6232
103.4062 | 121.9025 | -61.1343 | 60.379 | 0.0026703 | -0.00047207 | 0.063692 | -0.0015296 | 0.066262 | 0.0024183 | 3.8456e-05 | -0.0054932 | -0.0017069 | 0.065048 | 0.068678 | -0.19336 | -0.0015572 | 60.5942 | -61.0565 | 0.004578 | -61.1755 | 60.2875 | -61.2213 | -61.1069 | -61.4914 | 0.041199 | -61.4685 | 60.2325 | 60.3058 | -60.9146 | -61.1389 | -0.086975 | 0.027465 | -0.091552 | 0.077819 | -0.041199 | -0.068664 | 0.21515 | 0.21973 | -0.004578 | -0.14648 | -0.35706 | -0.33417 | -0.32959 | -0.073242 | 121.4218 | 121.7285 | 61.1389 | -121.4859 | 121.3669 | 121.4401 | 61.1755 | -121.5179
105.1875 | 121.8109 | -61.1206 | 60.4614 | -0.0049592 | 0.0029459 | 0.064333 | 0.002102 | 0.069252 | 0.0015637 | -0.0023113 | -0.013123 | 0.00021568 | 0.064621 | 0.068891 | -0.19677 | -0.0030526 | 60.6216 | -61.0336 | 0.064087 | -61.116 | 60.3928 | -61.1572 | -61.0428 | -61.4822 | 0.068665 | -61.4548 | 60.3333 | 60.3882 | -60.9009 | -61.1069 | -0.036622 | 0.077819 | -0.068665 | 0.086975 | 0.004577 | -0.073242 | 0.16022 | 0.21973 | 0.013732 | -0.12817 | -0.36163 | -0.33417 | -0.3479 | -0.073242 | 121.5134 | 121.7422 | 61.1847 | -121.5042 | 121.4539 | 121.5088 | 61.1893 | -121.5683
107.0469 | 121.8155 | -61.1298 | 60.4752 | 0.0026703 | -0.0015403 | 0.064546 | 0.001034 | 0.066689 | 0.0019909 | 0.0030293 | -0.0054932 | 2.078e-06 | 0.068253 | 0.06825 | -0.194 | -0.0013436 | 60.6308 | -61.0107 | 0.082397 | -61.1069 | 60.3699 | -61.171 | -61.0611 | -61.4822 | 0.086975 | -61.4502 | 60.3149 | 60.3607 | -60.8963 | -61.0977 | -0.041198 | 0.068665 | -0.10529 | 0.11902 | 0.022888 | -0.045777 | 0.15564 | 0.23346 | 0.032044 | -0.16022 | -0.35248 | -0.32043 | -0.35248 | -0.11444 | 121.4996 | 121.7606 | 61.2122 | -121.5363 | 121.4447 | 121.4905 | 61.2167 | -121.5729
109.0156 | 121.843 | -61.0565 | 60.4889 | 0.0026703 | 0.0014505 | 0.068391 | 0.0012476 | 0.066689 | -0.0039905 | -0.0016705 | -0.013123 | -0.0032021 | 0.068253 | 0.067182 | -0.19592 | -0.0013436 | 60.6949 | -60.8734 | 0.19226 | -61.0519 | 60.3195 | -61.1252 | -61.0062 | -61.3953 | 0.17395 | -61.3312 | 60.2875 | 60.379 | -60.8414 | -61.0611 | -0.068664 | 0.050354 | -0.16937 | 0.18311 | 0.004578 | -0.045776 | 0.20599 | 0.21515 | -0.004577 | -0.20142 | -0.33874 | -0.27466 | -0.27008 | -0.10986 | 121.376 | 121.7514 | 61.2488 | -121.4951 | 121.344 | 121.4355 | 61.2305 | -121.55
110.7031 | 121.8887 | -61.1206 | 60.4065 | -0.012589 | 0.0050821 | 0.065187 | -0.0015296 | 0.066902 | 0.0013501 | 0.0013203 | -0.0054932 | 2.078e-06 | 0.064194 | 0.069319 | -0.19592 | -0.0013436 | 60.6262 | -60.9879 | 0.054932 | -61.1389 | 60.2737 | -61.2076 | -61.0657 | -61.4456 | 0.054932 | -61.441 | 60.2051 | 60.2371 | -60.9604 | -61.116 | -0.086976 | 0.054931 | -0.13275 | 0.13275 | -0.018311 | -0.073242 | 0.21973 | 0.16022 | 0.004577 | -0.20142 | -0.32501 | -0.32044 | -0.32501 | -0.16937 | 121.3943 | 121.7468 | 61.1755 | -121.4722 | 121.3257 | 121.3577 | 61.1755 | -121.5225
112.4062 | 121.8567 | -61.1023 | 60.4385 | 0.0026703 | 0.0067911 | 0.067751 | -0.0034522 | 0.069893 | -0.00099973 | -0.00081594 | 0.0021363 | -0.0027749 | 0.064194 | 0.0706 | -0.19485 | -6.2012e-05 | 60.64 | -60.9741 | 0.059509 | -61.1298 | 60.2692 | -61.171 | -61.0611 | -61.4685 | 0.059509 | -61.4273 | 60.2417 | 60.2829 | -60.9192 | -61.1069 | -0.068664 | 0.041199 | -0.16937 | 0.12817 | -0.027466 | -0.068665 | 0.20142 | 0.18311 | -0.004578 | -0.19684 | -0.36621 | -0.32501 | -0.32043 | -0.15564 | 121.3715 | 121.7422 | 61.1618 | -121.4996 | 121.344 | 121.3852 | 61.1618 | -121.5454
114.1094 | 121.8796 | -61.0428 | 60.4843 | 0.0103 | 0.0048685 | 0.071809 | -0.0017432 | 0.066262 | -0.0024951 | -0.0014569 | 0.0021363 | -0.0051247 | 0.061417 | 0.063337 | -0.19528 | -0.0039072 | 60.7178 | -60.8551 | 0.16937 | -61.0519 | 60.3287 | -61.1252 | -61.0016 | -61.3907 | 0.17853 | -61.3174 | 60.2783 | 60.3836 | -60.8551 | -61.0703 | -0.082397 | 0.041199 | -0.15564 | 0.18768 | -0.009155 | -0.050354 | 0.23346 | 0.18768 | -0.027465 | -0.20599 | -0.3479 | -0.27466 | -0.24719 | -0.10071 | 121.3715 | 121.7606 | 61.2122 | -121.4859 | 121.3211 | 121.4264 | 61.2213 | -121.5546
115.7812 | 121.8796 | -61.1114 | 60.3882 | 0.0026703 | 0.0031595 | 0.066042 | -0.00088858 | 0.066689 | 0.0011365 | -0.0010297 | -0.0054932 | -0.0023477 | 0.065048 | 0.06825 | -0.19314 | -0.0036936 | 60.6445 | -61.0016 | 0.068665 | -61.1343 | 60.2737 | -61.1984 | -61.0382 | -61.4548 | 0.059509 | -61.441 | 60.228 | 60.2783 | -60.9375 | -61.1389 | -0.086975 | 0.073242 | -0.11444 | 0.10986 | -0.022888 | -0.09613 | 0.25635 | 0.17395 | -0.027466 | -0.16022 | -0.34332 | -0.32959 | -0.30212 | -0.10986 | 121.3852 | 121.756 | 61.1801 | -121.4264 | 121.3394 | 121.3898 | 61.171 | -121.5271
117.4688 | 121.7926 | -61.1206 | 60.4294 | -0.012589 | -0.0021811 | 0.063692 | -0.0011024 | 0.068184 | 0.0036999 | 0.00025206 | -0.0054932 | 0.0021383 | 0.066544 | 0.06825 | -0.19421 | -0.0026254 | 60.6537 | -60.997 | 0.082397 | -61.1069 | 60.347 | -61.1755 | -61.0382 | -61.4502 | 0.086975 | -61.4594 | 60.2829 | 60.3607 | -60.9009 | -61.116 | -0.054932 | 0.082397 | -0.082397 | 0.1236 | 0.013732 | -0.068665 | 0.22431 | 0.21973 | 0.004577 | -0.14648 | -0.32959 | -0.33875 | -0.34332 | -0.068664 | 121.4676 | 121.7743 | 61.203 | -121.4676 | 121.4035 | 121.4813 | 61.2076 | -121.5454
119.1406 | 121.788 | -61.1298 | 60.4706 | -0.0049592 | -4.4874e-05 | 0.065187 | -3.4178e-05 | 0.066902 | 0.0047681 | 0.0028155 | -0.0054932 | 0.00064308 | 0.065903 | 0.071028 | -0.19592 | -0.002839 | 60.64 | -60.9741 | 0.086975 | -61.1114 | 60.3424 | -61.1938 | -61.0519 | -61.4594 | 0.10071 | -61.4548 | 60.2921 | 60.3333 | -60.8963 | -61.1343 | -0.064087 | 0.07782 | -0.12817 | 0.15564 | 0.018311 | -0.059509 | 0.16937 | 0.23346 | -0.004577 | -0.17853 | -0.32959 | -0.32501 | -0.32044 | -0.13733 | 121.4722 | 121.7697 | 61.2167 | -121.5225 | 121.4218 | 121.463 | 61.2305 | -121.6049
120.8281 | 121.7972 | -61.0977 | 60.4752 | 0.0026703 | -0.00068567 | 0.066469 | 0.0027428 | 0.067116 | 0.00049567 | 0.0011067 | 0.0021363 | -0.00063872 | 0.06868 | 0.069319 | -0.19742 | -0.0026254 | 60.5896 | -61.0245 | 0.059509 | -61.1252 | 60.3607 | -61.1343 | -61.0519 | -61.4822 | 0.091553 | -61.4548 | 60.347 | 60.379 | -60.9146 | -61.084 | -0.036621 | 0.045776 | -0.11444 | 0.073242 | -0.027466 | -0.073242 | 0.11444 | 0.18311 | 0.013733 | -0.12817 | -0.38452 | -0.35706 | -0.37079 | -0.096131 | 121.4584 | 121.6873 | 61.1572 | -121.5271 | 121.4447 | 121.4767 | 61.1893 | -121.5591
122.5 | 121.907 | -61.0565 | 60.4752 | 0.0026703 | 0.0042275 | 0.065187 | 0.0027428 | 0.066475 | -0.0052721 | 0.0015339 | 0.0021363 | -0.0053385 | 0.065262 | 0.067396 | -0.20062 | 0.0014334 | 60.6033 | -60.9604 | 0.068665 | -61.1023 | 60.3058 | -61.1664 | -61.0199 | -61.441 | 0.11902 | -61.3541 | 60.2737 | 60.3195 | -60.8688 | -61.0977 | -0.10986 | 0.036622 | -0.16937 | 0.096131 | -0.045776 | -0.082398 | 0.12817 | 0.18768 | -0.041198 | -0.20142 | -0.38452 | -0.29755 | -0.25635 | -0.15564 | 121.3623 | 121.6599 | 61.1252 | -121.4951 | 121.3303 | 121.376 | 61.1755 | -121.5729
124.1875 | 121.7606 | -61.1618 | 60.4477 | -0.0049592 | -0.0017539 | 0.065187 | -0.00088858 | 0.069252 | 0.0047681 | 0.0019611 | -0.0054932 | -0.0012795 | 0.065048 | 0.069319 | -0.19464 | 0.00057899 | 60.5392 | -61.1114 | -0.013733 | -61.1938 | 60.3333 | -61.1984 | -61.0886 | -61.5555 | -0.027466 | -61.5646 | 60.3058 | 60.3333 | -60.9421 | -61.1389 | -0.036621 | 0.073242 | -0.11444 | 0.050354 | -0.032044 | -0.10529 | 0.091553 | 0.21973 | 0.022888 | -0.14191 | -0.39368 | -0.40283 | -0.42572 | -0.11444 | 121.4951 | 121.701 | 61.1481 | -121.5363 | 121.4676 | 121.4951 | 61.1343 | -121.5866
125.8438 | 121.7743 | -61.0886 | 60.5164 | 0.0026703 | -0.0023947 | 0.066683 | 0.003811 | 0.067971 | -0.00035893 | 0.00046566 | 0.0021363 | -0.0025613 | 0.069321 | 0.068678 | -0.19592 | 0.0012198 | 60.5942 | -61.0062 | 0.07782 | -61.1252 | 60.3653 | -61.1526 | -61.0107 | -61.5005 | 0.068665 | -61.4456 | 60.3699 | 60.4065 | -60.9009 | -61.0657 | -0.064087 | 0.07782 | -0.15106 | 0.082397 | -0.036621 | -0.11444 | 0.07782 | 0.18768 | 0.022888 | -0.14648 | -0.41199 | -0.35706 | -0.37994 | -0.10986 | 121.4539 | 121.6827 | 61.1664 | -121.5271 | 121.4584 | 121.4951 | 61.1572 | -121.582
127.5312 | 121.8704 | -61.1252 | 60.4202 | 0.025558 | 0.0065775 | 0.064974 | -3.4178e-05 | 0.065193 | -0.00014533 | 0.0015339 | -0.0054932 | -0.0036295 | 0.065048 | 0.069105 | -0.19549 | -0.001771 | 60.6216 | -60.9741 | 0.054932 | -61.116 | 60.26 | -61.1893 | -61.0657 | -61.4548 | 0.059509 | -61.4227 | 60.1959 | 60.2554 | -60.9329 | -61.1481 | -0.064087 | 0.059509 | -0.16022 | 0.15106 | 0.009155 | -0.050354 | 0.20142 | 0.19226 | -0.022888 | -0.2243 | -0.32959 | -0.29755 | -0.27466 | -0.16479 | 121.3852 | 121.7468 | 61.1801 | -121.4859 | 121.3211 | 121.3806 | 61.1847 | -121.5683
129.2812 | 121.7606 | -61.1343 | 60.4706 | -0.0049592 | -0.0013267 | 0.064546 | -0.0017432 | 0.069252 | 0.0017773 | 0.0019611 | -0.0054932 | 0.00042948 | 0.06633 | 0.070387 | -0.1925 | 0.00057899 | 60.5392 | -61.1023 | -0.032043 | -61.1801 | 60.3378 | -61.2167 | -61.084 | -61.5646 | -0.041199 | -61.5646 | 60.26 | 60.3012 | -60.9512 | -61.1526 | -0.082398 | 0.050354 | -0.13275 | 0.032043 | -0.045777 | -0.096131 | 0.068665 | 0.1831 | -0.018311 | -0.21057 | -0.4303 | -0.4303 | -0.41199 | -0.16937 | 121.4722 | 121.6736 | 61.1023 | -121.5546 | 121.3943 | 121.4355 | 61.0931 | -121.6232
130.9531 | 121.8155 | -61.1206 | 60.4294 | -0.0049592 | 0.00059593 | 0.064119 | -3.4178e-05 | 0.066475 | -0.00057253 | 0.0017475 | 0.0097658 | 0.00021568 | 0.066971 | 0.068037 | -0.19742 | -0.0026254 | 60.5301 | -61.1206 | -0.041199 | -61.2076 | 60.2966 | -61.2122 | -61.0748 | -61.5463 | -0.022888 | -61.528 | 60.2692 | 60.3287 | -60.9467 | -61.1572 | -0.091553 | 0.045776 | -0.13275 | 0 | -0.086976 | -0.13275 | 0.10071 | 0.17395 | -0.036622 | -0.16022 | -0.42572 | -0.40741 | -0.37079 | -0.10071 | 121.4172 | 121.6507 | 61.0794 | -121.5042 | 121.3898 | 121.4493 | 61.0977 | -121.5866
132.6406 | 121.8796 | -61.0794 | 60.4614 | -0.012589 | 0.0082865 | 0.067964 | 0.0018884 | 0.067116 | -0.0052721 | 0.00046566 | -0.0054932 | -0.0040567 | 0.067184 | 0.066542 | -0.1987 | -0.00091641 | 60.5713 | -61.0153 | 0.050354 | -61.1298 | 60.2966 | -61.171 | -61.0245 | -61.5005 | 0.054932 | -61.4136 | 60.2554 | 60.3333 | -60.8963 | -61.0931 | -0.091552 | 0.054932 | -0.1648 | 0.064087 | -0.050354 | -0.10529 | 0.10986 | 0.18311 | -0.013733 | -0.20599 | -0.42114 | -0.33417 | -0.32043 | -0.12817 | 121.376 | 121.6507 | 61.1298 | -121.4859 | 121.3348 | 121.4127 | 61.1343 | -121.5546
134.3125 | 121.7972 | -61.1069 | 60.4156 | 0.0026703 | 0.0018777 | 0.065401 | -0.0015296 | 0.06968 | 0.0011365 | 0.00067926 | 0.0021363 | 0.00064308 | 0.062271 | 0.069319 | -0.19421 | -0.0034798 | 60.5255 | -61.1298 | -0.059509 | -61.2076 | 60.3241 | -61.2396 | -61.1252 | -61.5738 | -0.045776 | -61.5463 | 60.2966 | 60.3241 | -60.9512 | -61.1389 | -0.13275 | -0.01831 | -0.091552 | -0.022888 | -0.10071 | -0.082398 | 0.10986 | 0.15564 | -0.032043 | -0.11902 | -0.46692 | -0.43945 | -0.40741 | -0.091552 | 121.431 | 121.6324 | 61.0474 | -121.5408 | 121.4035 | 121.431 | 61.0611 | -121.5546
135.9844 | 121.7514 | -61.1298 | 60.466 | -0.0049592 | -0.0011131 | 0.064546 | -0.00024778 | 0.066048 | 0.0036999 | 3.8456e-05 | 0.0021363 | -0.00021152 | 0.067612 | 0.068678 | -0.19507 | -0.0030526 | 60.6079 | -61.0336 | 0.059509 | -61.1252 | 60.3333 | -61.1847 | -61.0382 | -61.5051 | 0.041199 | -61.496 | 60.2966 | 60.347 | -60.9375 | -61.1343 | -0.054931 | 0.091553 | -0.13275 | 0.096131 | 0.004578 | -0.086975 | 0.14191 | 0.19226 | -0.004577 | -0.16937 | -0.37537 | -0.36621 | -0.36163 | -0.11902 | 121.463 | 121.7377 | 61.1893 | -121.5042 | 121.4264 | 121.4767 | 61.171 | -121.6003
137.6719 | 121.8246 | -61.0794 | 60.4431 | -0.0049592 | 0.0040139 | 0.064546 | 0.0025292 | 0.066262 | -0.0048449 | -0.00017514 | 0.0097658 | -0.0053385 | 0.065475 | 0.069105 | -0.1972 | -0.00113 | 60.5896 | -60.9879 | 0.036621 | -61.1298 | 60.2783 | -61.1481 | -61.0474 | -61.4731 | 0.073242 | -61.4227 | 60.2554 | 60.3104 | -60.8963 | -61.0931 | -0.068664 | 0.032044 | -0.16479 | 0.091553 | -0.050354 | -0.082398 | 0.14648 | 0.18311 | -0.013733 | -0.18768 | -0.39368 | -0.34332 | -0.32959 | -0.13275 | 121.3577 | 121.669 | 61.116 | -121.4905 | 121.3348 | 121.3898 | 61.1526 | -121.5363
139.3438 | 121.7468 | -61.1618 | 60.4385 | -0.012589 | 0.00059593 | 0.064333 | -0.0017432 | 0.069252 | 0.0043409 | 0.0026019 | 0.0021363 | 0.0012839 | 0.064835 | 0.070387 | -0.19229 | -0.001771 | 60.553 | -61.084 | 0.004578 | -61.171 | 60.3287 | -61.1938 | -61.0748 | -61.5189 | 0 | -61.5509 | 60.2921 | 60.3745 | -60.9375 | -61.1389 | -0.032044 | 0.086975 | -0.10986 | 0.07782 | -0.009155 | -0.09613 | 0.11444 | 0.2243 | 0.022888 | -0.14648 | -0.35706 | -0.3891 | -0.41199 | -0.064087 | 121.4905 | 121.7148 | 61.1664 | -121.5134 | 121.4539 | 121.5363 | 61.1618 | -121.5775
141.0156 | 121.7514 | -61.171 | 60.4523 | -0.0049592 | -0.0013267 | 0.062837 | -0.0028112 | 0.067971 | 0.0019909 | 0.0030293 | 0.0021363 | 0.00021568 | 0.068466 | 0.069319 | -0.19442 | -0.0030526 | 60.5621 | -61.0703 | 0.013733 | -61.1664 | 60.3195 | -61.2167 | -61.0565 | -61.5372 | -0.018311 | -61.5463 | 60.2966 | 60.3378 | -60.9421 | -61.1526 | -0.045777 | 0.11444 | -0.13275 | 0.10071 | 0.004577 | -0.10986 | 0.10986 | 0.22888 | 0.01831 | -0.15564 | -0.36621 | -0.37537 | -0.39368 | -0.11444 | 121.4905 | 121.7331 | 61.1847 | -121.5088 | 121.4676 | 121.5088 | 61.1526 | -121.6049
142.6875 | 121.7606 | -61.1389 | 60.4111 | -0.0049592 | -4.4874e-05 | 0.065187 | 0.0016748 | 0.067116 | 0.0028455 | 0.0034565 | 0.0021363 | -0.00063872 | 0.06633 | 0.068464 | -0.19571 | -0.0024118 | 60.5164 | -61.1435 | -0.036621 | -61.2076 | 60.3104 | -61.1938 | -61.084 | -61.5601 | -0.054932 | -61.5646 | 60.2921 | 60.3333 | -60.965 | -61.1572 | -0.054932 | 0.054932 | -0.10071 | -0.004578 | -0.068665 | -0.1236 | 0.10529 | 0.17395 | -0.018311 | -0.11902 | -0.42114 | -0.42572 | -0.40741 | -0.07782 | 121.4493 | 121.6553 | 61.1023 | -121.4951 | 121.431 | 121.4722 | 61.084 | -121.5683
144.375 | 121.8979 | -61.1023 | 60.3836 | 0.0103 | 0.0014505 | 0.063478 | -0.0021704 | 0.067116 | -0.00099973 | 0.00089286 | 0.0021363 | -0.0012795 | 0.06633 | 0.068464 | -0.19677 | 0.0018606 | 60.5392 | -61.0931 | -0.036621 | -61.1938 | 60.3012 | -61.1938 | -61.0977 | -61.5143 | 0.009155 | -61.4868 | 60.2554 | 60.3287 | -60.9329 | -61.1481 | -0.091553 | 0.004578 | -0.082398 | 0.009155 | -0.091553 | -0.096131 | 0.15564 | 0.16937 | -0.045776 | -0.12817 | -0.41199 | -0.38452 | -0.33874 | -0.054932 | 121.4035 | 121.6415 | 61.0657 | -121.4813 | 121.3577 | 121.431 | 61.1114 | -121.5317
146.0781 | 121.756 | -61.0931 | 60.5484 | -0.0049592 | -0.00047207 | 0.067964 | 0.0031702 | 0.068398 | -0.0035633 | 0.00046566 | 0.0021363 | -0.0025613 | 0.06398 | 0.068464 | -0.19699 | -0.0013436 | 60.6537 | -60.9467 | 0.14191 | -61.0611 | 60.3287 | -61.1114 | -61.0016 | -61.4868 | 0.11444 | -61.4182 | 60.3195 | 60.4156 | -60.8826 | -61.0703 | -0.01831 | 0.091553 | -0.21973 | 0.14648 | 0.032044 | -0.059509 | 0.10529 | 0.21057 | 0.022889 | -0.22888 | -0.39368 | -0.32501 | -0.3479 | -0.13275 | 121.4218 | 121.7468 | 61.235 | -121.55 | 121.4127 | 121.5088 | 61.2076 | -121.6187
147.75 | 121.7697 | -61.0886 | 60.5026 | 0.0026703 | 0.0014505 | 0.067537 | 0.0048792 | 0.065621 | -0.0039905 | -0.00060234 | 0.0021363 | -0.0040567 | 0.067612 | 0.068464 | -0.20041 | -0.0013436 | 60.672 | -60.9009 | 0.16937 | -61.0428 | 60.3287 | -61.1023 | -60.9833 | -61.3998 | 0.14648 | -61.3403 | 60.3012 | 60.3516 | -60.8459 | -61.0748 | -0.013733 | 0.10529 | -0.17395 | 0.18768 | 0.045776 | -0.05951 | 0.16937 | 0.24262 | 0.013733 | -0.20142 | -0.31128 | -0.25177 | -0.2655 | -0.15106 | 121.4172 | 121.7606 | 61.2579 | -121.4859 | 121.3898 | 121.4401 | 61.235 | -121.5775
149.4219 | 121.8613 | -61.0519 | 60.4431 | 0.0026703 | 0.0025185 | 0.069032 | 0.003811 | 0.067116 | -0.0046313 | -0.0012433 | -0.0054932 | -0.0032021 | 0.066971 | 0.066755 | -0.19699 | -0.0015572 | 60.5804 | -60.997 | 0.045776 | -61.1252 | 60.2875 | -61.1664 | -61.0107 | -61.496 | 0.032043 | -61.4273 | 60.2829 | 60.347 | -60.9238 | -61.1023 | -0.11444 | 0.041199 | -0.15564 | 0.054932 | -0.073242 | -0.11444 | 0.13733 | 0.12817 | -0.050354 | -0.16022 | -0.44403 | -0.37537 | -0.32501 | -0.09613 | 121.3394 | 121.6324 | 61.0977 | -121.4539 | 121.3348 | 121.3989 | 61.084 | -121.5454
151.0938 | 121.8887 | -61.0519 | 60.4477 | 0.0026703 | 0.0050821 | 0.066896 | 0.00060662 | 0.06733 | -0.0024951 | -0.0027387 | 0.0097658 | -0.0029885 | 0.065903 | 0.065901 | -0.19763 | -0.0013436 | 60.6216 | -60.9695 | 0.073242 | -61.0886 | 60.3287 | -61.1435 | -61.0245 | -61.4273 | 0.12817 | -61.3586 | 60.2829 | 60.3424 | -60.878 | -61.0611 | -0.091553 | 0.027466 | -0.11902 | 0.082398 | -0.036621 | -0.064087 | 0.17395 | 0.17395 | -0.009155 | -0.16479 | -0.37537 | -0.3067 | -0.29755 | -0.10529 | 121.3806 | 121.6736 | 61.1252 | -121.4722 | 121.3348 | 121.3943 | 61.1801 | -121.5088
152.7969 | 121.8109 | -61.0931 | 60.4111 | -0.0049592 | 0.0023049 | 0.065614 | -0.0038794 | 0.066475 | 0.0022047 | 0.0019611 | -0.0054932 | -0.0042703 | 0.066757 | 0.065687 | -0.194 | -0.0019846 | 60.6262 | -60.965 | 0.045776 | -61.1206 | 60.2325 | -61.1801 | -61.0474 | -61.4548 | 0.064087 | -61.4136 | 60.2234 | 60.2921 | -60.8963 | -61.1389 | -0.086975 | 0.045777 | -0.17853 | 0.12817 | -0.027465 | -0.073242 | 0.21515 | 0.19684 | -0.045776 | -0.18768 | -0.36163 | -0.32043 | -0.27466 | -0.11902 | 121.3257 | 121.7194 | 61.1389 | -121.4584 | 121.3165 | 121.3852 | 61.1572 | -121.55
154.4688 | 121.8796 | -61.0977 | 60.3607 | 0.0026703 | 0.0059365 | 0.065828 | -0.0021704 | 0.063912 | 0.0034863 | 0.0019611 | 0.0021363 | 0.00021568 | 0.063126 | 0.068464 | -0.19229 | -0.0024118 | 60.5804 | -61.0519 | -0.004578 | -61.1664 | 60.2875 | -61.2076 | -61.0519 | -61.4502 | 0.045776 | -61.4502 | 60.2554 | 60.2783 | -60.9512 | -61.1298 | -0.10986 | 0.045776 | -0.073242 | 0.045776 | -0.068665 | -0.11444 | 0.21973 | 0.14648 | -0.032044 | -0.10529 | -0.35248 | -0.35248 | -0.32043 | -0.082398 | 121.3852 | 121.6782 | 61.0931 | -121.4127 | 121.3531 | 121.376 | 61.1435 | -121.4905
156.1719 | 121.7834 | -61.1069 | 60.498 | 0.0026703 | -0.0047445 | 0.067751 | 0.0012476 | 0.067757 | 0.00070927 | 0.0011067 | -0.0054932 | -0.00021152 | 0.068253 | 0.067396 | -0.19699 | -0.00048921 | 60.6216 | -61.0062 | 0.073242 | -61.1114 | 60.3836 | -61.1252 | -60.997 | -61.4731 | 0.054932 | -61.4639 | 60.3607 | 60.3882 | -60.8597 | -61.0794 | -0.01831 | 0.10986 | -0.11444 | 0.10071 | -0.004577 | -0.11444 | 0.1236 | 0.24719 | 0.027466 | -0.13733 | -0.36621 | -0.35706 | -0.38452 | -0.10986 | 121.4905 | 121.7285 | 61.1801 | -121.4951 | 121.4676 | 121.4951 | 61.1618 | -121.5775
157.8438 | 121.7468 | -61.0703 | 60.498 | 0.0026703 | -0.0026083 | 0.066255 | 0.0044518 | 0.067543 | 0.0011365 | 0.0034565 | -0.0054932 | -0.0027749 | 0.067398 | 0.069105 | -0.19656 | -0.00070281 | 60.6079 | -60.9833 | 0.091553 | -61.1069 | 60.3745 | -61.1389 | -61.0291 | -61.4731 | 0.073242 | -61.4365 | 60.3561 | 60.3836 | -60.878 | -61.084 | -0.068665 | 0.041198 | -0.1236 | 0.086975 | -0.036622 | -0.07782 | 0.10986 | 0.19226 | -0.013733 | -0.14191 | -0.40283 | -0.36621 | -0.35248 | -0.11444 | 121.4447 | 121.6782 | 61.1618 | -121.5271 | 121.4264 | 121.4539 | 61.1435 | -121.582
159.5156 | 121.7422 | -61.1526 | 60.4523 | 0.0026703 | -0.0036765 | 0.062624 | -0.00067498 | 0.066475 | 0.0030591 | 0.0021747 | -0.0054932 | -0.00042512 | 0.067825 | 0.068891 | -0.19507 | -0.001771 | 60.6262 | -61.0107 | 0.068665 | -61.1343 | 60.3287 | -61.1801 | -61.0428 | -61.4868 | 0.050354 | -61.4822 | 60.2921 | 60.3378 | -60.9055 | -61.1572 | -0.027466 | 0.10986 | -0.1236 | 0.14191 | 0.018311 | -0.091552 | 0.17395 | 0.24719 | -0.004578 | -0.16022 | -0.33417 | -0.32959 | -0.32501 | -0.11444 | 121.4813 | 121.7789 | 61.2213 | -121.4951 | 121.4447 | 121.4905 | 61.203 | -121.6095
161.1875 | 121.7651 | -61.116 | 60.4614 | -0.0049592 | 0.00016873 | 0.064546 | -0.00067498 | 0.065621 | 0.0039135 | 0.0028155 | 0.0021363 | 0.00085668 | 0.066971 | 0.068464 | -0.194 | -0.001771 | 60.6125 | -60.9879 | 0.086975 | -61.1069 | 60.3333 | -61.1618 | -61.0611 | -61.4365 | 0.10986 | -61.4548 | 60.2829 | 60.3607 | -60.8963 | -61.1069 | -0.045776 | 0.054932 | -0.12817 | 0.12817 | 0.009155 | -0.045777 | 0.15106 | 0.21973 | 0.009155 | -0.17853 | -0.32043 | -0.33875 | -0.3479 | -0.10071 | 121.4493 | 121.7285 | 61.203 | -121.5225 | 121.3989 | 121.4767 | 61.2259 | -121.5683
162.8594 | 121.7377 | -61.0886 | 60.5164 | 0.0026703 | -0.0019675 | 0.066469 | 0.0040246 | 0.065621 | -0.0031359 | 0.00067926 | 0.0021363 | -0.0021341 | 0.065689 | 0.069105 | -0.19806 | -6.2012e-05 | 60.6171 | -60.9375 | 0.11444 | -61.0703 | 60.3561 | -61.1206 | -60.9879 | -61.4731 | 0.082397 | -61.4182 | 60.347 | 60.4065 | -60.8734 | -61.084 | -0.032043 | 0.10071 | -0.16022 | 0.15106 | 0.018311 | -0.082397 | 0.10071 | 0.21515 | 0.004578 | -0.16937 | -0.38452 | -0.32959 | -0.33417 | -0.10986 | 121.4447 | 121.7056 | 61.203 | -121.5042 | 121.4355 | 121.4951 | 61.171 | -121.6003
164.5312 | 121.8338 | -61.0703 | 60.4889 | -0.0049592 | -4.4874e-05 | 0.068605 | 0.0023156 | 0.063698 | -0.0039905 | 0.0013203 | -0.0054932 | -0.0057657 | 0.067398 | 0.066114 | -0.19677 | 0.00015159 | 60.6812 | -60.8688 | 0.16937 | -61.0199 | 60.3424 | -61.116 | -60.9787 | -61.3815 | 0.19226 | -61.3174 | 60.2829 | 60.347 | -60.8414 | -61.0565 | -0.045777 | 0.091552 | -0.14648 | 0.20142 | 0.050354 | -0.041198 | 0.19226 | 0.22888 | 0.013732 | -0.20599 | -0.31128 | -0.24719 | -0.26093 | -0.14191 | 121.4127 | 121.7514 | 61.2396 | -121.4676 | 121.3531 | 121.4172 | 61.2625 | -121.5454
166.2344 | 121.8704 | -61.0977 | 60.3836 | 0.0026703 | 0.0038003 | 0.065828 | -0.0017432 | 0.067757 | 0.0011365 | 0.0013203 | 0.0097658 | -0.00021152 | 0.066757 | 0.068678 | -0.19378 | -0.0030526 | 60.5576 | -61.0748 | -0.032043 | -61.1755 | 60.2966 | -61.2167 | -61.0794 | -61.4914 | 0.022888 | -61.4777 | 60.2554 | 60.2966 | -60.9055 | -61.1435 | -0.11902 | 0.01831 | -0.086975 | 0.022888 | -0.07782 | -0.09613 | 0.17395 | 0.19226 | -0.045777 | -0.12817 | -0.39368 | -0.37994 | -0.33417 | -0.086975 | 121.3943 | 121.6553 | 61.0657 | -121.463 | 121.3531 | 121.3943 | 61.1206 | -121.5271
167.9688 | 121.8201 | -61.0931 | 60.4385 | -0.0049592 | -0.00025847 | 0.068178 | -0.00067498 | 0.066262 | -0.0022815 | 0.00025206 | -0.0054932 | -0.0027749 | 0.063766 | 0.066969 | -0.19464 | -0.00113 | 60.6171 | -60.965 | 0.068665 | -61.1206 | 60.228 | -61.1664 | -61.0474 | -61.4685 | 0.050354 | -61.4227 | 60.2325 | 60.2737 | -60.9375 | -61.1206 | -0.073242 | 0.045777 | -0.21057 | 0.12817 | -0.027465 | -0.073242 | 0.17853 | 0.15564 | -0.027465 | -0.20599 | -0.37537 | -0.32959 | -0.30212 | -0.16479 | 121.3211 | 121.7102 | 61.1618 | -121.4859 | 121.3257 | 121.3669 | 61.1435 | -121.5591
169.6562 | 121.843 | -61.084 | 60.4477 | 0.0026703 | 0.0059365 | 0.068178 | 0.00082022 | 0.065407 | -0.0022815 | -0.0025249 | 0.0021363 | -0.00042512 | 0.067184 | 0.066969 | -0.19592 | -0.00027561 | 60.5804 | -60.997 | 0.027466 | -61.1252 | 60.2829 | -61.1526 | -61.0107 | -61.4777 | 0.045776 | -61.4136 | 60.2737 | 60.3058 | -60.9009 | -61.1069 | -0.068665 | 0.073242 | -0.16479 | 0.086975 | -0.041199 | -0.11444 | 0.13275 | 0.1831 | -0.022889 | -0.17395 | -0.39368 | -0.32959 | -0.3067 | -0.14191 | 121.3669 | 121.6644 | 61.1114 | -121.4584 | 121.3577 | 121.3898 | 61.1298 | -121.5546
171.3281 | 121.8155 | -61.0336 | 60.5026 | 0.0026703 | 0.0023049 | 0.066683 | 0.0029566 | 0.069039 | -0.0022815 | -0.00081594 | -0.0054932 | -0.0040567 | 0.06633 | 0.06761 | -0.19507 | -0.0026254 | 60.6857 | -60.8597 | 0.18768 | -61.0382 | 60.3333 | -61.0931 | -60.9833 | -61.3815 | 0.17395 | -61.3266 | 60.3012 | 60.3195 | -60.8643 | -61.0565 | -0.05951 | 0.050354 | -0.16937 | 0.17395 | -0.004578 | -0.054932 | 0.1831 | 0.16937 | -0.022889 | -0.20142 | -0.3479 | -0.29297 | -0.27008 | -0.18311 | 121.3669 | 121.7194 | 61.2213 | -121.4859 | 121.3348 | 121.3531 | 61.2076 | -121.5591
173 | 121.8704 | -61.0474 | 60.4431 | 0.0103 | 0.0040139 | 0.067751 | 0.0027428 | 0.06733 | -0.0029223 | -0.00038874 | -0.0054932 | -0.0064065 | 0.066544 | 0.068891 | -0.19742 | -0.00091641 | 60.5804 | -60.965 | 0.050354 | -61.0977 | 60.3012 | -61.1298 | -61.0245 | -61.441 | 0.064087 | -61.3724 | 60.2737 | 60.3241 | -60.91 | -61.0886 | -0.082398 | 0.022888 | -0.14191 | 0.082397 | -0.050354 | -0.073242 | 0.13733 | 0.13733 | -0.041199 | -0.16937 | -0.39368 | -0.32501 | -0.28381 | -0.11902 | 121.3486 | 121.6278 | 61.0977 | -121.4676 | 121.3211 | 121.3715 | 61.1114 | -121.5317
174.6719 | 121.8842 | -61.0336 | 60.4431 | -0.012589 | 0.0061501 | 0.069032 | 0.00060662 | 0.066689 | -0.0012133 | 3.8456e-05 | 0.0021363 | -0.0014933 | 0.065475 | 0.067823 | -0.19656 | -0.00113 | 60.6216 | -60.9695 | 0.068665 | -61.1023 | 60.2921 | -61.1389 | -61.0107 | -61.4227 | 0.09613 | -61.3632 | 60.3012 | 60.3241 | -60.8917 | -61.0748 | -0.10529 | 0.022888 | -0.15106 | 0.064087 | -0.068665 | -0.091553 | 0.17853 | 0.14191 | -0.041199 | -0.14191 | -0.3891 | -0.32959 | -0.28839 | -0.11902 | 121.3257 | 121.6553 | 61.1023 | -121.4539 | 121.3348 | 121.3577 | 61.1298 | -121.5179
176.375 | 121.7422 | -61.084 | 60.5164 | 0.0026703 | 0.0020913 | 0.06476 | 0.0027428 | 0.067116 | -0.00014533 | -0.00081594 | 0.0021363 | -0.00085232 | 0.066544 | 0.068891 | -0.19656 | -0.0026254 | 60.6812 | -60.878 | 0.16022 | -61.0336 | 60.3241 | -61.1114 | -61.0016 | -61.3815 | 0.15564 | -61.3632 | 60.3149 | 60.3653 | -60.8505 | -61.0474 | -0.027466 | 0.082397 | -0.19226 | 0.20599 | 0.050354 | -0.032043 | 0.16479 | 0.23346 | 0.036621 | -0.20142 | -0.29755 | -0.27924 | -0.31586 | -0.15106 | 121.4081 | 121.7651 | 61.2442 | -121.5179 | 121.3989 | 121.4493 | 61.2396 | -121.5637
178.1094 | 121.756 | -61.0794 | 60.4889 | 0.0103 | -0.00025847 | 0.065614 | 0.0033838 | 0.068611 | 0.00049567 | 0.00067926 | -0.0054932 | 0.0010703 | 0.067612 | 0.066328 | -0.19827 | -0.001771 | 60.6079 | -60.9924 | 0.07782 | -61.1114 | 60.3882 | -61.1343 | -61.0107 | -61.4456 | 0.073242 | -61.4548 | 60.3607 | 60.379 | -60.8963 | -61.084 | -0.054931 | 0.068665 | -0.10071 | 0.086975 | -0.032043 | -0.10071 | 0.11902 | 0.18311 | -0.004577 | -0.12817 | -0.36621 | -0.37537 | -0.37079 | -0.10986 | 121.4676 | 121.6873 | 61.1572 | -121.4996 | 121.4401 | 121.4584 | 61.1526 | -121.5729
179.8438 | 121.8155 | -61.0931 | 60.4431 | 0.0026703 | 0.0052957 | 0.064333 | 0.00039302 | 0.06498 | -0.0020679 | 0.00067926 | 0.0097658 | -0.0023477 | 0.065048 | 0.069105 | -0.19549 | -0.0013436 | 60.5942 | -60.9695 | 0.050354 | -61.1114 | 60.2783 | -61.1481 | -61.0107 | -61.4685 | 0.050354 | -61.4182 | 60.2371 | 60.2737 | -60.9192 | -61.1252 | -0.054931 | 0.082398 | -0.16479 | 0.1236 | -0.01831 | -0.10071 | 0.15106 | 0.17395 | -0.032043 | -0.20599 | -0.37537 | -0.32501 | -0.29297 | -0.16937 | 121.3715 | 121.6873 | 61.1435 | -121.4539 | 121.3303 | 121.3669 | 61.1435 | -121.5683
181.5156 | 121.7422 | -61.0657 | 60.4935 | -0.0049592 | -0.0030357 | 0.065614 | 0.00017942 | 0.066902 | 0.0013501 | 0.00046566 | -0.013123 | 0.00021568 | 0.06633 | 0.071028 | -0.19485 | -0.001771 | 60.6033 | -60.9787 | 0.086975 | -61.1069 | 60.4111 | -61.1389 | -61.0107 | -61.4594 | 0.068665 | -61.4273 | 60.3699 | 60.4202 | -60.878 | -61.1023 | -0.073242 | 0.054932 | -0.082397 | 0.086975 | -0.041199 | -0.096131 | 0.10986 | 0.18768 | -0.036621 | -0.1236 | -0.39368 | -0.36163 | -0.32501 | -0.073242 | 121.4767 | 121.669 | 61.1526 | -121.5042 | 121.4355 | 121.4859 | 61.1343 | -121.5958
183.1875 | 121.8246 | -61.0703 | 60.4431 | 0.0026703 | 0.0046549 | 0.067751 | 0.0014612 | 0.065834 | -0.0020679 | -0.00017514 | -0.013123 | -0.0019205 | 0.06398 | 0.069105 | -0.19592 | 0.00079259 | 60.5804 | -60.9787 | 0.050354 | -61.1206 | 60.2783 | -61.1526 | -61.0199 | -61.4594 | 0.032043 | -61.409 | 60.2737 | 60.3241 | -60.8734 | -61.0977 | -0.082398 | 0.050354 | -0.16479 | 0.091552 | -0.050354 | -0.10071 | 0.13733 | 0.19684 | -0.027466 | -0.16937 | -0.3891 | -0.33875 | -0.31128 | -0.11902 | 121.3486 | 121.6507 | 61.1206 | -121.463 | 121.344 | 121.3943 | 61.1023 | -121.5408
184.8906 | 121.8613 | -61.0474 | 60.4523 | -0.0049592 | 0.0052957 | 0.06711 | 0.00082022 | 0.066048 | -0.0016405 | 0.0015339 | 0.0021363 | -0.0040567 | 0.065262 | 0.06761 | -0.19613 | -0.0013436 | 60.6583 | -60.9192 | 0.11444 | -61.0565 | 60.3195 | -61.1069 | -60.9741 | -61.3953 | 0.13275 | -61.3266 | 60.2829 | 60.3241 | -60.8643 | -61.0565 | -0.05951 | 0.073242 | -0.13275 | 0.12817 | -0.009156 | -0.082398 | 0.20599 | 0.1831 | -0.009156 | -0.16937 | -0.3479 | -0.27924 | -0.27008 | -0.12817 | 121.3669 | 121.7056 | 61.1618 | -121.4264 | 121.3303 | 121.3715 | 61.1801 | -121.5088
186.5781 | 121.875 | -61.0611 | 60.4385 | 0.0026703 | 0.0076455 | 0.069887 | 0.0012476 | 0.068184 | -0.0020679 | 0.0015339 | -0.0054932 | -0.0046975 | 0.064835 | 0.068678 | -0.19549 | 0.00079259 | 60.6125 | -60.9421 | 0.054932 | -61.0977 | 60.3058 | -61.1526 | -61.0291 | -61.4319 | 0.09613 | -61.3632 | 60.2554 | 60.3333 | -60.878 | -61.0794 | -0.091553 | 0.032043 | -0.13275 | 0.11902 | -0.036621 | -0.068664 | 0.17395 | 0.1831 | -0.018311 | -0.18311 | -0.37079 | -0.30212 | -0.28381 | -0.10529 | 121.3669 | 121.6736 | 61.116 | -121.4676 | 121.3165 | 121.3943 | 61.1572 | -121.5179
188.3281 | 121.8613 | -61.0474 | 60.4431 | -0.012589 | 0.0050821 | 0.066896 | 0.00082022 | 0.068398 | -0.0014269 | -0.00038874 | -0.0054932 | -0.0029885 | 0.062485 | 0.065473 | -0.19442 | -0.0036936 | 60.5942 | -60.9741 | 0.032043 | -61.0977 | 60.3104 | -61.1618 | -61.0153 | -61.4456 | 0.064087 | -61.3861 | 60.2737 | 60.3149 | -60.878 | -61.0931 | -0.11444 | 0.032043 | -0.13275 | 0.073242 | -0.050354 | -0.082397 | 0.15106 | 0.16937 | -0.045777 | -0.16937 | -0.39826 | -0.33875 | -0.29297 | -0.12817 | 121.3577 | 121.6415 | 61.0794 | -121.4584 | 121.3211 | 121.3623 | 61.1114 | -121.5363
190.0312 | 121.8155 | -61.0977 | 60.4111 | -0.0049592 | 0.0042275 | 0.065187 | -0.0017432 | 0.062416 | 0.00092287 | 0.0023883 | -0.0054932 | -0.0023477 | 0.065689 | 0.068037 | -0.19421 | -0.0021982 | 60.6079 | -60.9558 | 0.059509 | -61.116 | 60.26 | -61.1984 | -61.0474 | -61.4227 | 0.07782 | -61.4044 | 60.2142 | 60.2371 | -60.9238 | -61.116 | -0.10071 | 0.050354 | -0.15106 | 0.14191 | -0.018311 | -0.068665 | 0.19684 | 0.17395 | -0.018311 | -0.19684 | -0.32501 | -0.3067 | -0.28839 | -0.17395 | 121.3577 | 121.7056 | 61.1572 | -121.4584 | 121.3119 | 121.3348 | 61.1755 | -121.5271
191.7344 | 121.8201 | -61.1023 | 60.3973 | -0.020218 | 0.0012369 | 0.066255 | -0.0025976 | 0.068611 | 0.0017773 | 0.0011067 | 0.0021363 | -0.0012795 | 0.062912 | 0.066755 | -0.19336 | -6.2012e-05 | 60.6125 | -60.965 | 0.054932 | -61.1252 | 60.228 | -61.1801 | -61.0565 | -61.3998 | 0.073242 | -61.3953 | 60.1913 | 60.2509 | -60.9192 | -61.1206 | -0.07782 | 0.045776 | -0.16937 | 0.13733 | -0.022888 | -0.068664 | 0.21515 | 0.18311 | -0.01831 | -0.20599 | -0.29755 | -0.29297 | -0.27466 | -0.14649 | 121.3303 | 121.7148 | 61.1572 | -121.4539 | 121.2936 | 121.3531 | 61.1755 | -121.5179
193.4531 | 121.8613 | -61.1023 | 60.379 | -0.0049592 | 0.0040139 | 0.067323 | -0.0032386 | 0.066475 | 0.0039135 | 0.00089286 | 0.0021363 | 0.0012839 | 0.064621 | 0.068464 | -0.19336 | -6.2012e-05 | 60.5621 | -61.0657 | -0.036621 | -61.1801 | 60.2966 | -61.1938 | -61.0748 | -61.5005 | -0.009155 | -61.5005 | 60.2554 | 60.3104 | -60.9375 | -61.1298 | -0.091553 | 0.027466 | -0.082397 | 0.036621 | -0.07782 | -0.10529 | 0.18311 | 0.16479 | -0.027466 | -0.1236 | -0.39825 | -0.39825 | -0.37079 | -0.068664 | 121.3989 | 121.6644 | 61.0657 | -121.4539 | 121.3577 | 121.4127 | 61.0931 | -121.5088
195.1562 | 121.7285 | -61.0428 | 60.5118 | 0.017929 | 0.00080973 | 0.066255 | -3.4178e-05 | 0.068398 | -0.0014269 | 0.00089286 | -0.0054932 | -0.0012795 | 0.065048 | 0.068891 | -0.19677 | 0.0010062 | 60.6491 | -60.9192 | 0.13275 | -61.0565 | 60.3287 | -61.1252 | -60.965 | -61.4273 | 0.11902 | -61.3953 | 60.3333 | 60.3836 | -60.8551 | -61.0611 | -0.082397 | 0.07782 | -0.18311 | 0.1236 | -0.013733 | -0.091553 | 0.13733 | 0.18768 | -0.01831 | -0.17853 | -0.38452 | -0.35248 | -0.33417 | -0.12817 | 121.3715 | 121.6919 | 61.1755 | -121.4767 | 121.376 | 121.4264 | 61.1618 | -121.5729
196.8438 | 121.7789 | -61.1023 | 60.4523 | 0.0026703 | -0.0021811 | 0.066255 | 0.0025292 | 0.069893 | 0.0041273 | 0.0015339 | -0.0054932 | 0.0019247 | 0.068893 | 0.068678 | -0.19549 | -0.0026254 | 60.6171 | -60.9833 | 0.059509 | -61.0931 | 60.3836 | -61.1435 | -61.0245 | -61.441 | 0.086975 | -61.441 | 60.347 | 60.3516 | -60.9055 | -61.1069 | -0.041199 | 0.07782 | -0.068665 | 0.11902 | 0.009155 | -0.068665 | 0.16479 | 0.19684 | -0.004578 | -0.10529 | -0.33875 | -0.33875 | -0.33417 | -0.10071 | 121.4859 | 121.7194 | 61.1618 | -121.4767 | 121.4493 | 121.4539 | 61.1893 | -121.5591
198.5156 | 121.8292 | -61.1069 | 60.3653 | 0.0103 | 0.0033731 | 0.064546 | -0.0017432 | 0.066689 | 0.0013501 | 0.0015339 | 0.0021363 | -0.00021152 | 0.066116 | 0.071241 | -0.19357 | 0.00036539 | 60.5209 | -61.0611 | -0.041199 | -61.1755 | 60.3012 | -61.1847 | -61.0886 | -61.5097 | -0.022888 | -61.5005 | 60.2554 | 60.2921 | -60.965 | -61.1481 | -0.077819 | 0.018311 | -0.064087 | 0.045777 | -0.068664 | -0.086975 | 0.15564 | 0.14191 | -0.041198 | -0.10986 | -0.40283 | -0.39368 | -0.35248 | -0.073242 | 121.4081 | 121.6278 | 61.0657 | -121.4539 | 121.3623 | 121.3989 | 61.084 | -121.5134
200.2656 | 121.8109 | -61.0794 | 60.4156 | -0.0049592 | 0.0055093 | 0.066255 | -0.00067498 | 0.069466 | -0.0020679 | 0.0038837 | -0.0054932 | -0.0034159 | 0.065475 | 0.067182 | -0.19763 | 0.00057899 | 60.5942 | -60.9375 | 0.059509 | -61.1114 | 60.2554 | -61.171 | -61.0519 | -61.441 | 0.059509 | -61.3953 | 60.2097 | 60.2692 | -60.8917 | -61.1206 | -0.091552 | 0.027466 | -0.16022 | 0.14191 | -0.032043 | -0.059509 | 0.17853 | 0.18768 | -0.041198 | -0.20599 | -0.36163 | -0.31586 | -0.27466 | -0.14648 | 121.3348 | 121.6736 | 61.1389 | -121.4676 | 121.2891 | 121.3486 | 61.1389 | -121.5363
201.9531 | 121.8063 | -61.0977 | 60.4248 | 0.0026703 | 0.0063639 | 0.066683 | -0.00067498 | 0.067757 | -0.0029223 | 0.0013203 | -0.0054932 | -0.0014933 | 0.065048 | 0.06761 | -0.1972 | -6.2012e-05 | 60.5804 | -60.9604 | 0.059509 | -61.1206 | 60.2509 | -61.1389 | -61.0474 | -61.4639 | 0.059509 | -61.3953 | 60.2188 | 60.2966 | -60.8734 | -61.116 | -0.041199 | 0.050354 | -0.17395 | 0.13733 | -0.022888 | -0.073242 | 0.15564 | 0.2243 | -0.018311 | -0.20599 | -0.36621 | -0.29755 | -0.27924 | -0.12817 | 121.3486 | 121.6782 | 61.1572 | -121.4722 | 121.3165 | 121.3943 | 61.1572 | -121.5408
203.625 | 121.8109 | -61.1023 | 60.3973 | 0.0103 | 0.0042275 | 0.068605 | -0.0015296 | 0.065621 | -0.0016405 | 0.0019611 | -0.0054932 | -0.0029885 | 0.063766 | 0.068464 | -0.19528 | -0.0026254 | 60.6171 | -60.9558 | 0.059509 | -61.116 | 60.2554 | -61.1664 | -61.0428 | -61.4273 | 0.086975 | -61.3907 | 60.2234 | 60.2783 | -60.9283 | -61.1298 | -0.064087 | 0.059509 | -0.14191 | 0.14648 | -0.013733 | -0.073242 | 0.21973 | 0.17395 | -0.027466 | -0.17395 | -0.32501 | -0.28839 | -0.26093 | -0.11902 | 121.3577 | 121.7194 | 61.1618 | -121.4401 | 121.3257 | 121.3806 | 61.1893 | -121.5271
205.375 | 121.7697 | -61.084 | 60.4477 | 0.0103 | -0.0032493 | 0.064119 | 0.00082022 | 0.069252 | 0.0058363 | 0.0021747 | 0.0021363 | 0.00021568 | 0.065689 | 0.067396 | -0.19528 | -0.002839 | 60.6262 | -60.9833 | 0.07782 | -61.0794 | 60.347 | -61.1664 | -61.0291 | -61.4227 | 0.086975 | -61.4319 | 60.3195 | 60.3287 | -60.8917 | -61.1252 | -0.082398 | 0.054931 | -0.10071 | 0.10071 | 0.004577 | -0.050354 | 0.17853 | 0.19226 | -0.041199 | -0.12817 | -0.33874 | -0.3479 | -0.3067 | -0.11902 | 121.431 | 121.7102 | 61.1618 | -121.4767 | 121.4035 | 121.4127 | 61.171 | -121.5729
207.0625 | 121.8521 | -61.1069 | 60.3928 | 0.0103 | 0.0027323 | 0.063265 | -0.003025 | 0.06968 | 0.00092287 | 0.0026019 | 0.0021363 | -0.00085232 | 0.065048 | 0.068678 | -0.19378 | -0.0026254 | 60.5896 | -60.997 | 0.027466 | -61.1114 | 60.2783 | -61.1938 | -61.0748 | -61.4273 | 0.073242 | -61.4227 | 60.1913 | 60.2921 | -60.9238 | -61.1298 | -0.086975 | 0.032044 | -0.11444 | 0.10986 | -0.004577 | -0.036621 | 0.19684 | 0.18311 | -0.022888 | -0.20142 | -0.32043 | -0.31586 | -0.29297 | -0.10071 | 121.3852 | 121.6965 | 61.1343 | -121.4676 | 121.2982 | 121.3989 | 61.1801 | -121.5225
208.7344 | 121.8246 | -61.0886 | 60.3836 | -0.0049592 | 0.0052957 | 0.067751 | -0.0015296 | 0.068825 | -0.00035893 | 0.0019611 | 0.0021363 | -0.0023477 | 0.064194 | 0.068037 | -0.19848 | -0.0021982 | 60.6033 | -60.9741 | 0.059509 | -61.1023 | 60.2509 | -61.1664 | -61.0519 | -61.4319 | 0.068665 | -61.4182 | 60.1959 | 60.2829 | -60.9192 | -61.1252 | -0.07782 | 0.036621 | -0.13275 | 0.11444 | -0.013733 | -0.050354 | 0.21973 | 0.16937 | -0.036621 | -0.18768 | -0.34332 | -0.32959 | -0.29297 | -0.10071 | 121.3394 | 121.6919 | 61.1481 | -121.4355 | 121.2845 | 121.3715 | 61.1572 | -121.5088
210.4219 | 121.8567 | -61.0291 | 60.4614 | -0.0049592 | 0.0044411 | 0.067323 | 0.00039302 | 0.067757 | -0.0063403 | 0.00067926 | 0.0021363 | -0.0029885 | 0.064621 | 0.066969 | -0.19998 | -0.00048921 | 60.6308 | -60.91 | 0.11902 | -61.0611 | 60.2875 | -61.1069 | -60.9604 | -61.3907 | 0.13275 | -61.3129 | 60.2646 | 60.3516 | -60.8551 | -61.0886 | -0.07782 | 0.068665 | -0.17395 | 0.11902 | -0.032043 | -0.10071 | 0.16937 | 0.17395 | -0.059509 | -0.19684 | -0.36163 | -0.28381 | -0.2243 | -0.10986 | 121.3165 | 121.6599 | 61.1481 | -121.4218 | 121.2936 | 121.3806 | 61.1618 | -121.55
212.1094 | 121.8018 | -61.0703 | 60.4202 | -0.0049592 | 0.0061501 | 0.071169 | -0.00067498 | 0.067543 | -0.00057253 | -0.0018841 | -0.0054932 | -0.0038431 | 0.062057 | 0.066969 | -0.19742 | -0.00048921 | 60.6216 | -60.9558 | 0.036621 | -61.0977 | 60.2737 | -61.1481 | -61.0199 | -61.4639 | 0.041199 | -61.409 | 60.2509 | 60.3058 | -60.8643 | -61.1252 | -0.07782 | 0.050354 | -0.14648 | 0.11444 | -0.027466 | -0.07782 | 0.20142 | 0.20599 | -0.054932 | -0.16937 | -0.39368 | -0.33875 | -0.28381 | -0.11444 | 121.344 | 121.6919 | 61.1069 | -121.4401 | 121.3211 | 121.376 | 61.1114 | -121.5454
213.9062 | 121.7651 | -61.0886 | 60.4523 | 0.0026703 | -0.00025847 | 0.066683 | -0.0015296 | 0.068398 | 0.0026319 | 0.00089286 | -0.0054932 | 0.0014975 | 0.064835 | 0.067396 | -0.19442 | -0.0019846 | 60.64 | -60.9741 | 0.091553 | -61.0977 | 60.3378 | -61.1572 | -61.0428 | -61.4319 | 0.10529 | -61.4182 | 60.2921 | 60.3378 | -60.9009 | -61.1069 | -0.068665 | 0.045776 | -0.11444 | 0.11444 | -0.009155 | -0.054931 | 0.18768 | 0.18768 | -0.018311 | -0.16022 | -0.34332 | -0.32959 | -0.31128 | -0.11444 | 121.4264 | 121.7285 | 61.1801 | -121.4951 | 121.3806 | 121.4264 | 61.1938 | -121.5591
215.5938 | 121.7651 | -61.084 | 60.4568 | -0.0049592 | -0.0041037 | 0.063478 | 0.001034 | 0.067543 | 0.0043409 | 0.0019611 | 0.0021363 | 0.00064308 | 0.067612 | 0.068464 | -0.19635 | -6.2012e-05 | 60.6033 | -60.9787 | 0.09613 | -61.0931 | 60.347 | -61.1572 | -61.0382 | -61.4365 | 0.091553 | -61.4273 | 60.3058 | 60.3333 | -60.8826 | -61.116 | -0.073243 | 0.045776 | -0.10986 | 0.10529 | -0.009156 | -0.054932 | 0.14648 | 0.20142 | -0.032044 | -0.15106 | -0.35248 | -0.34332 | -0.31128 | -0.1236 | 121.431 | 121.6873 | 61.1801 | -121.4951 | 121.3898 | 121.4172 | 61.1755 | -121.5729
217.3438 | 121.788 | -61.1069 | 60.4111 | 0.0026703 | 0.0033731 | 0.065187 | 0.002102 | 0.065834 | -0.0020679 | 0.0030293 | 0.0097658 | -0.0021341 | 0.067398 | 0.067396 | -0.19806 | -0.00027561 | 60.6079 | -60.9512 | 0.059509 | -61.1114 | 60.2417 | -61.1664 | -61.0428 | -61.4456 | 0.073242 | -61.3861 | 60.1822 | 60.2783 | -60.91 | -61.1206 | -0.059509 | 0.064087 | -0.16937 | 0.15564 | -0.004577 | -0.068664 | 0.19684 | 0.19684 | -0.013732 | -0.22888 | -0.33875 | -0.27923 | -0.2655 | -0.13275 | 121.3486 | 121.7148 | 61.1664 | -121.4539 | 121.2891 | 121.3852 | 61.1801 | -121.5317
219.0469 | 121.7056 | -61.0565 | 60.5164 | -0.0049592 | -0.0013267 | 0.065828 | 0.0035974 | 0.067543 | -0.00014533 | 0.0017475 | 0.0097658 | -0.0021341 | 0.067184 | 0.067396 | -0.19827 | -0.0019846 | 60.6308 | -60.9512 | 0.11444 | -61.0703 | 60.3653 | -61.116 | -60.9879 | -61.4594 | 0.068665 | -61.4136 | 60.3287 | 60.4111 | -60.8597 | -61.0794 | -0.059509 | 0.068665 | -0.15106 | 0.10529 | -0.013732 | -0.082397 | 0.11444 | 0.19684 | -0.022888 | -0.18768 | -0.40283 | -0.35705 | -0.33417 | -0.10529 | 121.4218 | 121.6873 | 61.171 | -121.5042 | 121.3852 | 121.4676 | 61.1252 | -121.5958
220.7344 | 121.8063 | -61.0703 | 60.4156 | -0.0049592 | 0.0020913 | 0.065187 | 0.00017942 | 0.066475 | -0.0039905 | 0.0028155 | 0.0021363 | -0.0044839 | 0.065475 | 0.068464 | -0.19742 | -0.00048921 | 60.5804 | -60.9741 | 0.027466 | -61.1069 | 60.2783 | -61.1618 | -61.0199 | -61.4594 | 0.050354 | -61.4136 | 60.2463 | 60.3287 | -60.8826 | -61.0794 | -0.091553 | 0.050354 | -0.13733 | 0.09613 | -0.036622 | -0.086976 | 0.16479 | 0.18768 | -0.009156 | -0.16937 | -0.3891 | -0.34332 | -0.33417 | -0.086975 | 121.3486 | 121.6507 | 61.0977 | -121.4355 | 121.3165 | 121.3989 | 61.1206 | -121.4951
222.4375 | 121.8704 | -61.0291 | 60.4706 | -0.0049592 | 0.0042275 | 0.064974 | -0.0021704 | 0.068184 | -0.0050585 | 0.00089286 | 0.0097658 | -0.0053385 | 0.063126 | 0.065901 | -0.19784 | -0.00113 | 60.6216 | -60.91 | 0.10071 | -61.0519 | 60.3195 | -61.1252 | -60.9879 | -61.3998 | 0.12817 | -61.322 | 60.2829 | 60.3241 | -60.8551 | -61.0748 | -0.09613 | 0.041199 | -0.15106 | 0.11902 | -0.022888 | -0.064087 | 0.15106 | 0.17395 | -0.045776 | -0.18768 | -0.37079 | -0.29297 | -0.24719 | -0.14648 | 121.3486 | 121.6507 | 61.1298 | -121.4584 | 121.312 | 121.3531 | 61.1572 | -121.5454
224.25 | 121.7422 | -61.1343 | 60.3836 | 0.0026703 | 0.0027323 | 0.064119 | -0.001316 | 0.065193 | 0.0060499 | -0.00017514 | -0.013123 | 0.0017111 | 0.064621 | 0.06825 | -0.19229 | -0.0049752 | 60.5255 | -61.0748 | -0.045776 | -61.1618 | 60.3287 | -61.2305 | -61.0703 | -61.5372 | -0.045776 | -61.528 | 60.2737 | 60.2921 | -60.9467 | -61.1755 | -0.096131 | 0.064087 | -0.054932 | 0.059509 | -0.027466 | -0.091553 | 0.14191 | 0.18768 | -0.041199 | -0.10986 | -0.40283 | -0.39368 | -0.35248 | -0.091553 | 121.463 | 121.6599 | 61.0886 | -121.4539 | 121.4081 | 121.4264 | 61.0886 | -121.5591
226.0156 | 121.8475 | -61.0886 | 60.379 | -0.0049592 | 0.0048685 | 0.064333 | -0.00088858 | 0.066048 | 6.8274e-05 | 0.0017475 | 0.0021363 | -0.0012795 | 0.06398 | 0.068891 | -0.19549 | -0.0013436 | 60.585 | -60.9879 | 0.009155 | -61.1252 | 60.2783 | -61.1893 | -61.0794 | -61.441 | 0.07782 | -61.4273 | 60.2188 | 60.2554 | -60.9055 | -61.1206 | -0.10071 | 0.009155 | -0.10071 | 0.10071 | -0.036621 | -0.045776 | 0.20599 | 0.18311 | -0.032043 | -0.16022 | -0.35248 | -0.33874 | -0.3067 | -0.1236 | 121.3669 | 121.6736 | 61.0977 | -121.4584 | 121.3074 | 121.344 | 61.1664 | -121.4996
227.7969 | 121.7377 | -61.1206 | 60.4568 | -0.0049592 | -0.0023947 | 0.063051 | 0.002102 | 0.067116 | 0.0034863 | 0.0011067 | -0.0054932 | 0.0014975 | 0.067184 | 0.070173 | -0.19507 | -0.0032662 | 60.6125 | -60.9604 | 0.091553 | -61.0931 | 60.3241 | -61.1435 | -61.0428 | -61.4182 | 0.10529 | -61.4182 | 60.2966 | 60.3241 | -60.878 | -61.1298 | -0.022889 | 0.077819 | -0.13275 | 0.16022 | 0.027465 | -0.050354 | 0.15564 | 0.24261 | -0.009156 | -0.16022 | -0.29755 | -0.29755 | -0.28839 | -0.13275 | 121.4447 | 121.7331 | 61.2122 | -121.4996 | 121.4172 | 121.4447 | 61.2259 | -121.5866
229.4844 | 121.7468 | -61.0794 | 60.4614 | 0.0026703 | -0.00047207 | 0.066042 | 0.0027428 | 0.066262 | 0.00070927 | 0.0026019 | 0.0097658 | 0.00021568 | 0.06868 | 0.069746 | -0.19656 | 0.00015159 | 60.5896 | -60.9879 | 0.073242 | -61.0977 | 60.3561 | -61.1389 | -61.0016 | -61.4685 | 0.064087 | -61.4319 | 60.3561 | 60.4019 | -60.8688 | -61.1069 | -0.059509 | 0.07782 | -0.10529 | 0.091553 | -0.01831 | -0.09613 | 0.12817 | 0.21057 | -0.027466 | -0.10529 | -0.3891 | -0.35248 | -0.32501 | -0.059509 | 121.4355 | 121.669 | 61.1526 | -121.463 | 121.4355 | 121.4813 | 61.1435 | -121.5683
231.25 | 121.7789 | -61.0748 | 60.4111 | -0.0049592 | 0.0067911 | 0.067537 | -0.0021704 | 0.066262 | -0.0014269 | 0.0036701 | -0.013123 | -0.0034159 | 0.065048 | 0.067182 | -0.19464 | 0.00036539 | 60.6079 | -60.9329 | 0.073242 | -61.1114 | 60.2692 | -61.1801 | -61.0291 | -61.4273 | 0.082397 | -61.3907 | 60.2142 | 60.2829 | -60.9009 | -61.1298 | -0.10529 | 0.045776 | -0.14191 | 0.14191 | -0.036621 | -0.082397 | 0.19684 | 0.17395 | -0.054932 | -0.19684 | -0.35248 | -0.31586 | -0.26093 | -0.12817 | 121.344 | 121.6827 | 61.1481 | -121.4401 | 121.2891 | 121.3577 | 61.1572 | -121.5408
233.0156 | 121.7972 | -61.0977 | 60.3973 | -0.0049592 | 0.0018777 | 0.064119 | -0.0017432 | 0.066262 | 0.0047681 | 0.0034565 | -0.0054932 | 0.00042948 | 0.064835 | 0.068037 | -0.19357 | -0.00027561 | 60.5164 | -61.0886 | -0.045776 | -61.1664 | 60.3149 | -61.1938 | -61.0565 | -61.528 | -0.032043 | -61.4914 | 60.2554 | 60.3516 | -60.9329 | -61.1298 | -0.096131 | 0.041198 | -0.082398 | 0.009155 | -0.068665 | -0.10986 | 0.11902 | 0.1648 | -0.032044 | -0.14191 | -0.4303 | -0.39368 | -0.36163 | -0.045777 | 121.4127 | 121.6141 | 61.0519 | -121.4539 | 121.3531 | 121.4493 | 61.0657 | -121.5271
234.7031 | 121.8201 | -61.0977 | 60.3745 | 0.0103 | 0.0046549 | 0.065401 | -0.001316 | 0.066048 | 0.0011365 | 0.0017475 | 0.0021363 | -0.0027749 | 0.061844 | 0.068037 | -0.19635 | -0.00048921 | 60.5942 | -60.9467 | 0.054932 | -61.0977 | 60.2325 | -61.1664 | -61.0519 | -61.4319 | 0.09613 | -61.377 | 60.2005 | 60.2875 | -60.91 | -61.1206 | -0.068665 | 0.045776 | -0.14191 | 0.15106 | 0 | -0.045776 | 0.21973 | 0.18768 | -0.022888 | -0.17395 | -0.33417 | -0.27924 | -0.25635 | -0.086975 | 121.3303 | 121.6919 | 61.1526 | -121.4264 | 121.2982 | 121.3852 | 61.1938 | -121.4951
236.4531 | 121.7972 | -61.0291 | 60.4706 | 0.0026703 | 0.0057229 | 0.067537 | 0.0033838 | 0.069252 | -0.0044177 | 0.00025206 | -0.0054932 | -0.0049111 | 0.067825 | 0.066755 | -0.19977 | -0.00027561 | 60.6812 | -60.8459 | 0.17395 | -61.0153 | 60.3149 | -61.084 | -60.9787 | -61.377 | 0.1831 | -61.3083 | 60.2737 | 60.3516 | -60.8414 | -61.0565 | -0.054931 | 0.050354 | -0.15564 | 0.18311 | 0.013733 | -0.036621 | 0.21057 | 0.18768 | -0.027466 | -0.19684 | -0.3479 | -0.27924 | -0.25177 | -0.11902 | 121.344 | 121.7102 | 61.203 | -121.4493 | 121.3028 | 121.3806 | 61.2122 | -121.5271
238.2344 | 121.8018 | -61.0703 | 60.4202 | 0.0026703 | 0.0027323 | 0.066683 | 0.001034 | 0.067543 | 0.00092287 | -0.00060234 | -0.0054932 | -0.0010659 | 0.06398 | 0.068037 | -0.19635 | 0.00036539 | 60.5896 | -60.9695 | 0.045776 | -61.1206 | 60.2783 | -61.1389 | -61.0245 | -61.4639 | 0.045776 | -61.4044 | 60.2554 | 60.3241 | -60.8688 | -61.1023 | -0.068665 | 0.045776 | -0.14191 | 0.10071 | -0.050354 | -0.09613 | 0.16937 | 0.20142 | -0.032044 | -0.16479 | -0.39368 | -0.33417 | -0.30212 | -0.09613 | 121.3486 | 121.6599 | 61.116 | -121.4447 | 121.3257 | 121.3943 | 61.116 | -121.5225
239.9844 | 121.7972 | -61.0794 | 60.4111 | -0.020218 | 0.0093545 | 0.069673 | 0.00060662 | 0.066262 | -0.0031359 | -0.0014569 | 0.0021363 | -0.0029885 | 0.064194 | 0.066969 | -0.19656 | 0.00015159 | 60.5942 | -60.9558 | 0.054932 | -61.116 | 60.2692 | -61.116 | -61.0153 | -61.441 | 0.041199 | -61.4044 | 60.2554 | 60.2829 | -60.9009 | -61.1252 | -0.036621 | 0.064087 | -0.14191 | 0.1236 | -0.036621 | -0.10071 | 0.18311 | 0.17853 | -0.045776 | -0.15564 | -0.36163 | -0.32501 | -0.27924 | -0.12817 | 121.3486 | 121.6736 | 61.1343 | -121.4264 | 121.3348 | 121.3623 | 61.1206 | -121.5363
241.6719 | 121.8475 | -61.0382 | 60.4477 | -0.0049592 | 0.0080727 | 0.070955 | -0.00088858 | 0.064125 | -0.0033495 | -0.0014569 | -0.0054932 | -0.0049111 | 0.066544 | 0.065901 | -0.19656 | -0.0013436 | 60.5759 | -60.9558 | 0.045776 | -61.0886 | 60.3012 | -61.1343 | -61.0245 | -61.441 | 0.064087 | -61.377 | 60.2737 | 60.3058 | -60.8688 | -61.0886 | -0.09613 | 0.013733 | -0.14648 | 0.082397 | -0.050354 | -0.064087 | 0.12817 | 0.16937 | -0.050354 | -0.17395 | -0.40283 | -0.33875 | -0.28839 | -0.14191 | 121.3394 | 121.6141 | 61.084 | -121.4722 | 121.312 | 121.344 | 61.1023 | -121.5363
243.4375 | 121.7514 | -61.1206 | 60.3882 | 0.0026703 | 0.0025185 | 0.065187 | -0.0025976 | 0.067971 | 0.0064771 | 0.0019611 | 0.0097658 | 0.00064308 | 0.06633 | 0.069319 | -0.19421 | -0.0030526 | 60.5209 | -61.1023 | -0.050354 | -61.1801 | 60.3104 | -61.1801 | -61.0748 | -61.5234 | -0.027466 | -61.5143 | 60.2829 | 60.2966 | -60.9283 | -61.1526 | -0.05951 | 0.045776 | -0.07782 | 0.01831 | -0.05951 | -0.10529 | 0.13275 | 0.19226 | -0.032044 | -0.10529 | -0.40283 | -0.39368 | -0.36163 | -0.091553 | 121.431 | 121.6415 | 61.0703 | -121.463 | 121.4035 | 121.4172 | 61.0931 | -121.5408
245.1875 | 121.788 | -61.0977 | 60.4248 | -0.0049592 | 0.0040139 | 0.066683 | -0.00088858 | 0.067116 | -0.00099973 | 0.00067926 | 0.0021363 | -0.0029885 | 0.064194 | 0.067823 | -0.19699 | -0.0021982 | 60.5988 | -60.9329 | 0.050354 | -61.1206 | 60.2417 | -61.1572 | -61.0245 | -61.4365 | 0.050354 | -61.409 | 60.2234 | 60.2966 | -60.8826 | -61.1023 | -0.05951 | 0.073242 | -0.18311 | 0.1648 | -0.022888 | -0.09613 | 0.17395 | 0.21515 | -0.004578 | -0.20142 | -0.33874 | -0.31128 | -0.3067 | -0.12817 | 121.3394 | 121.6965 | 61.1481 | -121.4493 | 121.3211 | 121.3943 | 61.1481 | -121.5271
246.8906 | 121.7468 | -61.0519 | 60.4797 | -0.0049592 | 0.00038233 | 0.067751 | 0.003811 | 0.066262 | -0.00099973 | 0.0023883 | 0.0021363 | -0.0046975 | 0.065048 | 0.067182 | -0.19699 | -0.0026254 | 60.6812 | -60.8505 | 0.16937 | -61.0245 | 60.2966 | -61.0977 | -60.9467 | -61.3632 | 0.16022 | -61.322 | 60.2692 | 60.3149 | -60.8459 | -61.0657 | -0.045776 | 0.10529 | -0.18311 | 0.20142 | 0.027466 | -0.07782 | 0.20142 | 0.20599 | -0.013733 | -0.21057 | -0.31128 | -0.27008 | -0.25635 | -0.1648 | 121.3486 | 121.7331 | 61.2213 | -121.4264 | 121.3211 | 121.3669 | 61.2122 | -121.5454
248.6406 | 121.8613 | -61.0245 | 60.466 | 0.0026703 | 0.0020913 | 0.070314 | 0.0025292 | 0.068398 | -0.0042041 | 0.00046566 | -0.0054932 | -0.0034159 | 0.065048 | 0.064405 | -0.19763 | 0.00036539 | 60.6079 | -60.8963 | 0.086975 | -61.0565 | 60.3287 | -61.116 | -61.0016 | -61.4044 | 0.1236 | -61.3312 | 60.2692 | 60.3058 | -60.8734 | -61.0794 | -0.091553 | 0.022888 | -0.13733 | 0.12817 | -0.032044 | -0.054932 | 0.14191 | 0.15106 | -0.054932 | -0.19684 | -0.37994 | -0.3067 | -0.25177 | -0.16022 | 121.3531 | 121.6324 | 61.1115 | -121.4676 | 121.2936 | 121.3303 | 61.1481 | -121.5454
250.3438 | 121.6965 | -61.0931 | 60.4385 | 0.0026703 | -4.4874e-05 | 0.065614 | 0.00060662 | 0.067757 | 0.0058363 | 0.0017475 | -0.0054932 | 0.0014975 | 0.067184 | 0.070387 | -0.19314 | -0.0026254 | 60.6079 | -60.9741 | 0.068665 | -61.1023 | 60.3149 | -61.171 | -61.0245 | -61.4456 | 0.045776 | -61.4685 | 60.3058 | 60.3012 | -60.9192 | -61.1343 | -0.077819 | 0.068665 | -0.1236 | 0.11902 | -0.009155 | -0.07782 | 0.16937 | 0.17395 | -0.041198 | -0.13275 | -0.35248 | -0.37537 | -0.33417 | -0.13733 | 121.4081 | 121.701 | 61.1618 | -121.463 | 121.3989 | 121.3943 | 61.1389 | -121.5729
252.1094 | 121.701 | -61.0657 | 60.5072 | -0.0049592 | -0.00089927 | 0.068391 | 0.001034 | 0.066048 | -0.0014269 | 0.0017475 | -0.0054932 | -0.0021341 | 0.065689 | 0.068464 | -0.19571 | -0.001771 | 60.64 | -60.8963 | 0.13733 | -61.0336 | 60.3333 | -61.084 | -60.9741 | -61.409 | 0.10071 | -61.3953 | 60.3149 | 60.3653 | -60.8505 | -61.0519 | -0.01831 | 0.091553 | -0.17395 | 0.16937 | 0.032044 | -0.059509 | 0.13275 | 0.21515 | 0.013733 | -0.19226 | -0.34332 | -0.32959 | -0.34332 | -0.14191 | 121.3989 | 121.7056 | 61.203 | -121.4813 | 121.3806 | 121.431 | 61.1664 | -121.5591
253.8594 | 121.7239 | -61.1114 | 60.4385 | -0.0049592 | -0.0015403 | 0.064974 | 0.0025292 | 0.066048 | 0.0024183 | 0.0034565 | -0.0054932 | 0.0012839 | 0.068253 | 0.068678 | -0.19507 | -0.0013436 | 60.6079 | -60.9467 | 0.086975 | -61.0886 | 60.3424 | -61.171 | -61.0062 | -61.4182 | 0.086975 | -61.4365 | 60.3012 | 60.3241 | -60.8871 | -61.0931 | -0.059509 | 0.10528 | -0.096131 | 0.16479 | 0.022888 | -0.082397 | 0.16937 | 0.2243 | 0.01831 | -0.13733 | -0.3067 | -0.32501 | -0.34332 | -0.11444 | 121.4539 | 121.7194 | 61.1984 | -121.4447 | 121.4127 | 121.4355 | 61.1984 | -121.5317
255.5469 | 121.7102 | -61.1389 | 60.4156 | -0.0049592 | -0.0015403 | 0.059419 | 0.0012476 | 0.068611 | 0.0051953 | 0.0032429 | 0.0021363 | 0.0019247 | 0.067612 | 0.069746 | -0.19528 | -0.00070281 | 60.5118 | -61.0703 | -0.018311 | -61.1618 | 60.2966 | -61.1847 | -61.0703 | -61.528 | -0.036621 | -61.5417 | 60.2692 | 60.3333 | -60.9329 | -61.1435 | -0.045776 | 0.068665 | -0.11902 | 0.068665 | -0.022888 | -0.091553 | 0.096131 | 0.20599 | -0.004578 | -0.14648 | -0.3891 | -0.40283 | -0.39825 | -0.082397 | 121.4355 | 121.6507 | 61.1206 | -121.4859 | 121.4081 | 121.4722 | 61.1023 | -121.5591
257.2969 | 121.7285 | -61.1343 | 60.4248 | -0.0049592 | -0.00068567 | 0.064333 | -3.4178e-05 | 0.067757 | 0.0028455 | 0.0017475 | -0.0054932 | 0.0010703 | 0.068466 | 0.070387 | -0.19442 | -0.00048921 | 60.4935 | -61.0977 | -0.036621 | -61.1618 | 60.3104 | -61.1938 | -61.084 | -61.528 | -0.018311 | -61.5097 | 60.2646 | 60.3104 | -60.9375 | -61.1572 | -0.05951 | 0.050354 | -0.11444 | 0.036621 | -0.027466 | -0.07782 | 0.068664 | 0.19684 | -0.022889 | -0.16022 | -0.39368 | -0.37537 | -0.35248 | -0.11444 | 121.4447 | 121.6278 | 61.0977 | -121.5088 | 121.3989 | 121.4447 | 61.116 | -121.582
259 | 121.756 | -61.0565 | 60.4568 | 0.0026703 | -0.0034629 | 0.066469 | 0.0025292 | 0.068825 | -0.00014533 | 0.0017475 | -0.0054932 | -0.0021341 | 0.066971 | 0.068678 | -0.194 | 0.0014334 | 60.5576 | -60.9741 | 0.054932 | -61.0931 | 60.3745 | -61.1252 | -60.997 | -61.4685 | 0.073242 | -61.4365 | 60.3516 | 60.3699 | -60.8551 | -61.0703 | -0.068664 | 0.05951 | -0.082397 | 0.082398 | -0.036621 | -0.096131 | 0.10071 | 0.20142 | -0.013732 | -0.10529 | -0.41199 | -0.37994 | -0.36621 | -0.086975 | 121.431 | 121.6141 | 61.1115 | -121.4539 | 121.4081 | 121.4264 | 61.1298 | -121.5271
260.7031 | 121.701 | -61.1252 | 60.4248 | 0.0026703 | -0.00089927 | 0.064546 | -0.0015296 | 0.066689 | 0.0011365 | 0.0034565 | -0.0054932 | 0.00042948 | 0.067612 | 0.069959 | -0.19613 | -6.2012e-05 | 60.5026 | -61.0794 | -0.041199 | -61.1618 | 60.3058 | -61.1801 | -61.0565 | -61.5372 | -0.041199 | -61.5417 | 60.2646 | 60.3195 | -60.9421 | -61.1572 | -0.054932 | 0.068664 | -0.11902 | 0.045776 | -0.036621 | -0.10528 | 0.07782 | 0.1831 | -0.032044 | -0.16022 | -0.41199 | -0.41656 | -0.38452 | -0.10529 | 121.431 | 121.6278 | 61.084 | -121.4813 | 121.3898 | 121.4447 | 61.084 | -121.582
262.4688 | 121.7789 | -61.084 | 60.3882 | 0.0026703 | 0.0055093 | 0.066469 | -0.0019568 | 0.067757 | -0.0050585 | 0.0015339 | 0.0021363 | -0.0027749 | 0.066116 | 0.06761 | -0.19592 | 0.00057899 | 60.5759 | -60.9421 | 0.054932 | -61.0977 | 60.228 | -61.1481 | -61.0291 | -61.4319 | 0.082397 | -61.3953 | 60.1822 | 60.2783 | -60.9009 | -61.1298 | -0.064087 | 0.054931 | -0.16022 | 0.14191 | -0.013733 | -0.068664 | 0.18768 | 0.1831 | -0.045777 | -0.20599 | -0.3479 | -0.31128 | -0.2655 | -0.10986 | 121.3119 | 121.6599 | 61.1389 | -121.4172 | 121.2662 | 121.3623 | 61.1664 | -121.5179
264.1719 | 121.7606 | -61.0931 | 60.4477 | -0.0049592 | -0.0038901 | 0.066469 | 0.00039302 | 0.067971 | 6.8274e-05 | 0.00067926 | 0.0021363 | 0.0017111 | 0.063766 | 0.069746 | -0.19613 | -0.0034798 | 60.5713 | -60.9924 | 0.059509 | -61.0748 | 60.3745 | -61.1206 | -61.0016 | -61.4456 | 0.086975 | -61.4136 | 60.3058 | 60.4065 | -60.8734 | -61.084 | -0.027465 | 0.091553 | -0.073242 | 0.10071 | 0.018311 | -0.073242 | 0.1236 | 0.21973 | 0.009156 | -0.14191 | -0.35248 | -0.32043 | -0.32959 | -0.041199 | 121.4676 | 121.6644 | 61.1526 | -121.4493 | 121.3989 | 121.4996 | 61.1801 | -121.5317
265.875 | 121.8201 | -61.084 | 60.3561 | -0.0049592 | 0.0023049 | 0.064333 | -0.0025976 | 0.07032 | 6.8274e-05 | 0.0011067 | -0.0054932 | -0.0012795 | 0.068466 | 0.069532 | -0.19613 | -0.00113 | 60.5209 | -61.0382 | -0.009155 | -61.1618 | 60.2646 | -61.1801 | -61.0565 | -61.4594 | 0.032043 | -61.4227 | 60.2097 | 60.2783 | -60.8963 | -61.1114 | -0.096131 | 0.027465 | -0.091553 | 0.045776 | -0.07782 | -0.10528 | 0.16479 | 0.18768 | -0.027466 | -0.14648 | -0.37537 | -0.33874 | -0.31128 | -0.07782 | 121.3486 | 121.6049 | 61.0748 | -121.4127 | 121.2936 | 121.3623 | 61.116 | -121.4676
267.5781 | 121.7468 | -61.0794 | 60.466 | -0.0049592 | -0.0011131 | 0.06711 | 0.0014612 | 0.065621 | 0.00049567 | 0.0015339 | -0.0054932 | -0.00063872 | 0.067398 | 0.06825 | -0.19549 | -0.00048921 | 60.5713 | -60.9787 | 0.064087 | -61.1023 | 60.347 | -61.1252 | -61.0245 | -61.4594 | 0.07782 | -61.4182 | 60.3104 | 60.4065 | -60.8826 | -61.0794 | -0.045776 | 0.054932 | -0.11902 | 0.10071 | -0.022888 | -0.07782 | 0.10529 | 0.19684 | 0 | -0.15564 | -0.37994 | -0.33874 | -0.33874 | -0.059509 | 121.4264 | 121.6507 | 61.1435 | -121.4905 | 121.3898 | 121.4859 | 61.1572 | -121.5454
269.3281 | 121.8292 | -61.0611 | 60.379 | 0.0026703 | 0.0027323 | 0.063051 | -0.001316 | 0.068611 | 0.00028207 | 0.00067926 | 0.0021363 | -0.0027749 | 0.064835 | 0.070814 | -0.1972 | -0.00027561 | 60.5118 | -61.0519 | -0.045776 | -61.1801 | 60.2737 | -61.171 | -61.0794 | -61.496 | 0.009155 | -61.4639 | 60.2371 | 60.3058 | -60.9283 | -61.1298 | -0.10986 | -0.018311 | -0.10528 | 0.009155 | -0.11902 | -0.10071 | 0.13275 | 0.13275 | -0.068665 | -0.14191 | -0.43488 | -0.40283 | -0.33417 | -0.073242 | 121.3348 | 121.5729 | 61.0153 | -121.4584 | 121.2982 | 121.3669 | 61.0703 | -121.5088
271.0938 | 121.8155 | -61.084 | 60.4019 | -0.0049592 | 0.0059365 | 0.067537 | -0.0017432 | 0.064553 | -0.0020679 | 0.0026019 | 0.0021363 | -0.0049111 | 0.066971 | 0.066969 | -0.19613 | 0.00036539 | 60.5896 | -60.9512 | 0.032043 | -61.0931 | 60.2371 | -61.1481 | -61.0291 | -61.4227 | 0.082397 | -61.3907 | 60.1822 | 60.2783 | -60.9146 | -61.1206 | -0.064087 | 0.054931 | -0.16479 | 0.13275 | -0.009156 | -0.064087 | 0.18768 | 0.16937 | -0.036621 | -0.21973 | -0.33874 | -0.3067 | -0.27008 | -0.1236 | 121.3211 | 121.6736 | 61.116 | -121.431 | 121.2662 | 121.3623 | 61.1664 | -121.5225
272.7969 | 121.7743 | -61.1069 | 60.4019 | -0.0049592 | 0.0023049 | 0.063478 | -3.4178e-05 | 0.066475 | 0.0024183 | 0.00089286 | -0.0054932 | -0.00042512 | 0.066544 | 0.068678 | -0.19699 | -0.00027561 | 60.4935 | -61.0794 | -0.045776 | -61.1664 | 60.3012 | -61.1893 | -61.0794 | -61.5372 | -0.041199 | -61.4914 | 60.2554 | 60.3195 | -60.9238 | -61.1481 | -0.082397 | 0.027466 | -0.10071 | 0.027466 | -0.059509 | -0.086975 | 0.091552 | 0.18311 | -0.041198 | -0.14648 | -0.4303 | -0.38452 | -0.34332 | -0.082398 | 121.4081 | 121.6003 | 61.0611 | -121.4813 | 121.3623 | 121.4264 | 61.0657 | -121.55
274.4844 | 121.6782 | -61.116 | 60.434 | 0.0026703 | -0.0013267 | 0.062837 | -0.001316 | 0.065621 | 0.0011365 | 0.0011067 | -0.028381 | -0.0012795 | 0.065689 | 0.066328 | -0.19549 | -0.00091641 | 60.5759 | -60.9879 | 0.054932 | -61.1069 | 60.3058 | -61.1343 | -61.0336 | -61.4731 | 0.041199 | -61.4685 | 60.2875 | 60.3516 | -60.9055 | -61.1252 | -0.01831 | 0.082398 | -0.12817 | 0.12817 | 0.009155 | -0.073243 | 0.14191 | 0.21057 | -0.009155 | -0.14648 | -0.35706 | -0.35248 | -0.34332 | -0.082398 | 121.4218 | 121.6919 | 61.171 | -121.4676 | 121.4035 | 121.4676 | 61.1572 | -121.5591
276.2656 | 121.8063 | -61.0199 | 60.4706 | -0.0049592 | 0.00016873 | 0.06711 | 0.0016748 | 0.067971 | -0.0063403 | -0.00017514 | 0.0021363 | -0.0055521 | 0.065048 | 0.067396 | -0.1987 | -0.00048921 | 60.6537 | -60.8459 | 0.17395 | -61.0153 | 60.3378 | -61.084 | -60.9512 | -61.3724 | 0.18768 | -61.2991 | 60.2737 | 60.3561 | -60.8047 | -61.0382 | -0.064087 | 0.068664 | -0.13275 | 0.17395 | 0.004577 | -0.064087 | 0.18311 | 0.21515 | -0.018311 | -0.19684 | -0.35248 | -0.27924 | -0.26093 | -0.11444 | 121.3577 | 121.6736 | 61.1938 | -121.4218 | 121.2936 | 121.376 | 61.2076 | -121.5088
278.0469 | 121.7972 | -61.0703 | 60.4065 | -0.0049592 | 0.0023049 | 0.064333 | 0.0029566 | 0.063698 | -0.0035633 | 0.00025206 | 0.0097658 | -0.0034159 | 0.067612 | 0.068464 | -0.19848 | -0.001771 | 60.5713 | -60.9741 | 0.041199 | -61.1114 | 60.2737 | -61.1252 | -60.9833 | -61.4777 | 0.041199 | -61.3953 | 60.2371 | 60.3333 | -60.8688 | -61.0794 | -0.054932 | 0.086975 | -0.13275 | 0.09613 | -0.041199 | -0.12817 | 0.16479 | 0.20142 | -0.009156 | -0.16937 | -0.40741 | -0.32501 | -0.31586 | -0.073242 | 121.344 | 121.6415 | 61.1114 | -121.3898 | 121.3074 | 121.4035 | 61.1114 | -121.4859
279.75 | 121.6873 | -61.116 | 60.4431 | -0.0049592 | -0.00068567 | 0.062196 | 0.0023156 | 0.067971 | 0.0032727 | 0.00025206 | -0.0054932 | 0.0017111 | 0.066757 | 0.070173 | -0.19592 | -0.002839 | 60.5804 | -61.0153 | 0.059509 | -61.1252 | 60.3104 | -61.171 | -61.0336 | -61.4777 | 0.018311 | -61.5005 | 60.2646 | 60.3241 | -60.9238 | -61.1206 | -0.054931 | 0.082398 | -0.13275 | 0.10071 | -0.009155 | -0.091553 | 0.13733 | 0.19226 | -0.004577 | -0.17853 | -0.36163 | -0.38452 | -0.37994 | -0.11902 | 121.4264 | 121.6965 | 61.1755 | -121.4767 | 121.3806 | 121.4401 | 61.1343 | -121.5637
281.5 | 121.6873 | -61.116 | 60.4202 | 0.0026703 | -0.00068567 | 0.064974 | -0.0019568 | 0.067543 | 0.0028455 | 0.0026019 | -0.0054932 | -0.0014933 | 0.065262 | 0.068678 | -0.1925 | -0.001771 | 60.5759 | -60.9833 | 0.032043 | -61.1206 | 60.2829 | -61.1526 | -61.0336 | -61.4914 | 0.013733 | -61.496 | 60.2829 | 60.3287 | -60.91 | -61.1252 | -0.036621 | 0.082398 | -0.13733 | 0.13275 | -0.004577 | -0.086975 | 0.15564 | 0.20599 | -0.009155 | -0.13733 | -0.37537 | -0.37994 | -0.37079 | -0.091553 | 121.3989 | 121.6919 | 61.1481 | -121.4539 | 121.3989 | 121.4447 | 61.1298 | -121.5454
283.2812 | 121.8246 | -61.0062 | 60.4477 | 0.0026703 | 0.0020913 | 0.068178 | 0.0050928 | 0.066475 | -0.0065539 | -0.0012433 | -0.0054932 | -0.0070475 | 0.066757 | 0.066542 | -0.19977 | 0.00057899 | 60.6537 | -60.8231 | 0.16479 | -61.0291 | 60.2692 | -61.0794 | -60.9924 | -61.3449 | 0.18768 | -61.2488 | 60.2554 | 60.3424 | -60.8231 | -61.0748 | -0.073242 | 0.013733 | -0.17853 | 0.18311 | -0.022888 | -0.036621 | 0.20599 | 0.18311 | -0.068664 | -0.19226 | -0.33874 | -0.24261 | -0.17395 | -0.10529 | 121.2753 | 121.6599 | 61.171 | -121.4401 | 121.2616 | 121.3486 | 61.1938 | -121.5225
285.0469 | 121.7331 | -61.0657 | 60.5026 | -0.0049592 | 0.0010233 | 0.067323 | 0.003811 | 0.06733 | -0.0018543 | 3.8456e-05 | 0.0021363 | -0.0012795 | 0.066116 | 0.067396 | -0.19571 | -0.001771 | 60.5713 | -60.9695 | 0.050354 | -61.0794 | 60.3836 | -61.116 | -61.0016 | -61.4639 | 0.054932 | -61.409 | 60.3561 | 60.3973 | -60.8734 | -61.0703 | -0.050354 | 0.064087 | -0.11902 | 0.096131 | -0.013733 | -0.07782 | 0.068664 | 0.19226 | -0.004577 | -0.14648 | -0.39825 | -0.34332 | -0.33875 | -0.10529 | 121.4493 | 121.637 | 61.116 | -121.5042 | 121.4218 | 121.463 | 61.1206 | -121.5729
286.75 | 121.7972 | -61.0748 | 60.434 | 0.0103 | 0.0059365 | 0.0701 | 0.0012476 | 0.066262 | -0.0042041 | -0.0023113 | -0.0054932 | -0.0040567 | 0.063766 | 0.068678 | -0.19912 | -6.2012e-05 | 60.5804 | -60.9421 | 0.027466 | -61.0794 | 60.2921 | -61.1298 | -61.0062 | -61.4639 | 0.036621 | -61.3998 | 60.2417 | 60.347 | -60.8551 | -61.0931 | -0.054932 | 0.068664 | -0.14191 | 0.13275 | -0.004578 | -0.073242 | 0.14648 | 0.21973 | -0.018311 | -0.19226 | -0.3891 | -0.32501 | -0.3067 | -0.086975 | 121.3669 | 121.6553 | 61.1023 | -121.4401 | 121.3165 | 121.4218 | 61.1114 | -121.5271
288.5 | 121.7102 | -61.0977 | 60.4065 | -0.0049592 | 0.0010233 | 0.065401 | -0.003025 | 0.067543 | 0.0036999 | 0.00089286 | 0.0021363 | 0.0014975 | 0.064621 | 0.070173 | -0.19507 | -0.00027561 | 60.4752 | -61.0977 | -0.050354 | -61.1526 | 60.3195 | -61.1847 | -61.0519 | -61.528 | -0.041199 | -61.5189 | 60.2646 | 60.3104 | -60.9283 | -61.1435 | -0.086975 | 0.045776 | -0.086975 | 0 | -0.054932 | -0.10071 | 0.068665 | 0.16937 | -0.045777 | -0.14191 | -0.4303 | -0.42114 | -0.37537 | -0.09613 | 121.4172 | 121.5729 | 61.0474 | -121.4584 | 121.3623 | 121.4081 | 61.0565 | -121.55
290.2969 | 121.7468 | -61.0886 | 60.4431 | -0.012589 | -0.00089927 | 0.066255 | 0.00082022 | 0.066048 | -0.00078613 | 0.0011067 | 0.0021363 | -0.0017069 | 0.065903 | 0.06825 | -0.19549 | -0.001771 | 60.5759 | -60.9741 | 0.064087 | -61.0794 | 60.3653 | -61.1343 | -61.0153 | -61.4456 | 0.082397 | -61.4227 | 60.3104 | 60.3653 | -60.8505 | -61.0931 | -0.045776 | 0.073242 | -0.07782 | 0.11444 | 0.009155 | -0.064087 | 0.13275 | 0.23804 | -0.004578 | -0.13275 | -0.35706 | -0.33417 | -0.32959 | -0.07782 | 121.4539 | 121.6644 | 61.1526 | -121.4584 | 121.3989 | 121.4539 | 61.171 | -121.5363
292.0625 | 121.8155 | -61.0977 | 60.3561 | -0.0049592 | 0.0052957 | 0.063478 | -0.0019568 | 0.065834 | 0.00070927 | 0.0019611 | -0.013123 | -0.0029885 | 0.065689 | 0.068678 | -0.19699 | -0.0019846 | 60.5209 | -61.0657 | -0.054932 | -61.1618 | 60.3012 | -61.1755 | -61.0474 | -61.5097 | -0.027466 | -61.4914 | 60.2371 | 60.3058 | -60.9283 | -61.1435 | -0.07782 | 0.050354 | -0.054932 | 0.032043 | -0.064087 | -0.11444 | 0.16479 | 0.16937 | -0.045777 | -0.11902 | -0.41199 | -0.39368 | -0.3479 | -0.050354 | 121.3989 | 121.6187 | 61.0428 | -121.4035 | 121.3348 | 121.4035 | 61.0703 | -121.4996
293.8281 | 121.7194 | -61.0931 | 60.434 | -0.0049592 | 0.0010233 | 0.063692 | -0.0017432 | 0.064339 | 0.0039135 | 0.0032429 | 0.0021363 | 0.0021383 | 0.065475 | 0.071241 | -0.19571 | -0.0032662 | 60.5164 | -61.0794 | -0.045776 | -61.1618 | 60.3195 | -61.1938 | -61.0657 | -61.5463 | -0.041199 | -61.528 | 60.2554 | 60.3287 | -60.9146 | -61.1343 | -0.10071 | 0.027466 | -0.11444 | 0.013733 | -0.068664 | -0.09613 | 0.082397 | 0.17853 | -0.041198 | -0.17853 | -0.45319 | -0.43488 | -0.39368 | -0.10529 | 121.4127 | 121.6095 | 61.0474 | -121.4996 | 121.3486 | 121.4218 | 61.0519 | -121.5683
295.5156 | 121.7697 | -61.0931 | 60.3699 | 0.0103 | 0.0010233 | 0.064974 | 0.0014612 | 0.067116 | 0.0011365 | 0.0040973 | -0.0054932 | 2.078e-06 | 0.065689 | 0.069319 | -0.19378 | -6.2012e-05 | 60.4797 | -61.0748 | -0.041199 | -61.1664 | 60.2921 | -61.1801 | -61.0565 | -61.5234 | -0.036621 | -61.5005 | 60.2509 | 60.3287 | -60.9192 | -61.1343 | -0.086975 | 0.036621 | -0.07782 | 0.018311 | -0.073242 | -0.10986 | 0.10986 | 0.17395 | -0.041198 | -0.11902 | -0.4303 | -0.40741 | -0.36621 | -0.041199 | 121.3852 | 121.5729 | 61.0519 | -121.4264 | 121.344 | 121.4218 | 61.0565 | -121.5042
297.2812 | 121.8613 | -61.0245 | 60.4294 | 0.0103 | 0.0012369 | 0.066683 | 0.0033838 | 0.06733 | -0.0071947 | 0.00089286 | 0.0021363 | -0.0057657 | 0.065262 | 0.06825 | -0.20126 | 0.0012198 | 60.5804 | -60.9283 | 0.07782 | -61.0519 | 60.3012 | -61.1298 | -60.965 | -61.3998 | 0.1236 | -61.3266 | 60.2554 | 60.3699 | -60.8414 | -61.0474 | -0.10529 | 0.059509 | -0.12817 | 0.09613 | -0.027466 | -0.086975 | 0.15106 | 0.18311 | -0.022888 | -0.17395 | -0.37537 | -0.30212 | -0.27924 | -0.059509 | 121.3257 | 121.6049 | 61.1023 | -121.3943 | 121.2799 | 121.3943 | 61.1481 | -121.4767
299.0469 | 121.669 | -61.116 | 60.4111 | 0.0026703 | -0.00047207 | 0.061983 | 0.0012476 | 0.067757 | 0.0049817 | 0.00046566 | -0.0054932 | 2.078e-06 | 0.066116 | 0.071241 | -0.19549 | -0.0015572 | 60.5667 | -61.0153 | 0.041199 | -61.1206 | 60.3012 | -61.1618 | -61.0245 | -61.4914 | 0.013733 | -61.5097 | 60.2921 | 60.3561 | -60.8963 | -61.1435 | -0.045776 | 0.091553 | -0.10986 | 0.10071 | -0.004577 | -0.09613 | 0.15564 | 0.21973 | -0.027466 | -0.11902 | -0.37537 | -0.39368 | -0.36621 | -0.054932 | 121.4172 | 121.6827 | 61.1572 | -121.4355 | 121.4081 | 121.4722 | 61.1298 | -121.5546
300.75 | 121.8201 | -61.0153 | 60.4202 | -0.0049592 | 0.0042275 | 0.066683 | 0.001034 | 0.067116 | -0.0054859 | -0.00038874 | 0.0097658 | -0.0053385 | 0.064835 | 0.066328 | -0.19806 | -0.00048921 | 60.64 | -60.878 | 0.13275 | -61.0336 | 60.3241 | -61.0931 | -60.9787 | -61.3724 | 0.15106 | -61.29 | 60.2554 | 60.379 | -60.8322 | -61.0519 | -0.07782 | 0.036621 | -0.09613 | 0.13733 | -0.01831 | -0.054931 | 0.21973 | 0.18311 | -0.036621 | -0.16479 | -0.35705 | -0.27466 | -0.23804 | -0.041199 | 121.3394 | 121.6553 | 61.1481 | -121.3989 | 121.2708 | 121.3943 | 61.1664 | -121.4722
302.4531 | 121.6919 | -61.1114 | 60.4202 | 0.0026703 | -0.0030357 | 0.060701 | 0.00060662 | 0.069039 | 0.0024183 | 0.0015339 | 0.0021363 | -0.00021152 | 0.069534 | 0.068037 | -0.19592 | -0.0039072 | 60.5392 | -61.0336 | 0.013733 | -61.1343 | 60.3104 | -61.1801 | -61.0428 | -61.5051 | 0.004578 | -61.5051 | 60.2509 | 60.3333 | -60.9238 | -61.1252 | -0.068665 | 0.068664 | -0.10986 | 0.07782 | -0.022888 | -0.091552 | 0.11902 | 0.18768 | -0.013733 | -0.16937 | -0.39368 | -0.39368 | -0.37994 | -0.086975 | 121.4218 | 121.6507 | 61.1252 | -121.463 | 121.3623 | 121.4447 | 61.116 | -121.5454
304.1562 | 121.8109 | -61.0886 | 60.379 | 0.0026703 | 0.0052957 | 0.061983 | -0.00067498 | 0.065193 | -0.00014533 | 0.0013203 | -0.0054932 | -0.0038431 | 0.067184 | 0.069746 | -0.1972 | -0.0015572 | 60.5804 | -60.9421 | 0.059509 | -61.0794 | 60.2142 | -61.1618 | -61.0382 | -61.409 | 0.064087 | -61.3953 | 60.1913 | 60.2737 | -60.91 | -61.1023 | -0.073242 | 0.050354 | -0.16479 | 0.14648 | 0.009155 | -0.041199 | 0.20142 | 0.17853 | -0.013733 | -0.18768 | -0.32043 | -0.3067 | -0.29297 | -0.10528 | 121.3028 | 121.669 | 61.1481 | -121.4172 | 121.2799 | 121.3623 | 61.1526 | -121.4813
305.9062 | 121.8155 | -61.0886 | 60.3561 | -0.0049592 | 0.0020913 | 0.065401 | -0.002384 | 0.065193 | 6.8274e-05 | 3.8456e-05 | 0.0021363 | -0.0012795 | 0.066971 | 0.069105 | -0.194 | -0.0019846 | 60.5164 | -61.0199 | -0.009155 | -61.1252 | 60.2737 | -61.171 | -61.0565 | -61.4594 | 0.027466 | -61.4273 | 60.228 | 60.3104 | -60.8963 | -61.1206 | -0.082397 | 0.032043 | -0.082397 | 0.068665 | -0.036621 | -0.068664 | 0.16022 | 0.19226 | -0.032043 | -0.12817 | -0.37079 | -0.33874 | -0.3067 | -0.045776 | 121.3623 | 121.6049 | 61.0794 | -121.4127 | 121.3165 | 121.3989 | 61.116 | -121.4767
307.6094 | 121.6873 | -61.0428 | 60.4477 | 0.0026703 | 0.0010233 | 0.068391 | 0.0029566 | 0.06498 | -0.0027087 | -0.0031659 | -0.013123 | -0.0032021 | 0.065048 | 0.066755 | -0.1972 | -0.0021982 | 60.6354 | -60.8551 | 0.17853 | -61.0153 | 60.3012 | -61.0748 | -60.965 | -61.3815 | 0.16022 | -61.3129 | 60.2875 | 60.3882 | -60.8368 | -61.0519 | -0.032043 | 0.07782 | -0.14648 | 0.18768 | 0.027466 | -0.050354 | 0.18768 | 0.20599 | -0.009155 | -0.16022 | -0.33875 | -0.27008 | -0.26093 | -0.059509 | 121.344 | 121.6782 | 61.2213 | -121.4127 | 121.3303 | 121.431 | 61.203 | -121.4996
309.375 | 121.6827 | -61.0336 | 60.4614 | -0.0049592 | 0.00016873 | 0.068178 | 0.002102 | 0.06733 | -0.00078613 | -0.00060234 | -0.0054932 | -0.0038431 | 0.062698 | 0.065901 | -0.1987 | -0.0013436 | 60.6308 | -60.8597 | 0.16022 | -61.0107 | 60.3378 | -61.1069 | -60.9604 | -61.4044 | 0.13275 | -61.3358 | 60.3012 | 60.3516 | -60.8551 | -61.0703 | -0.073243 | 0.073242 | -0.1236 | 0.17395 | 0.022888 | -0.050354 | 0.16937 | 0.17853 | -0.036621 | -0.16022 | -0.37079 | -0.30212 | -0.2655 | -0.10986 | 121.3715 | 121.6644 | 61.1938 | -121.4218 | 121.3348 | 121.3852 | 61.1664 | -121.5317
311.1406 | 121.8155 | -61.0748 | 60.3607 | 0.0026703 | 0.0052957 | 0.063051 | -0.0028112 | 0.067757 | 0.0017773 | 0.00046566 | -0.013123 | -0.0021341 | 0.064194 | 0.065901 | -0.19378 | -0.00048921 | 60.5347 | -61.0016 | 0.009155 | -61.1298 | 60.2692 | -61.1664 | -61.0428 | -61.441 | 0.041199 | -61.409 | 60.2188 | 60.2829 | -60.91 | -61.1023 | -0.091553 | 0.032043 | -0.091553 | 0.073242 | -0.054932 | -0.086975 | 0.17395 | 0.16479 | -0.027466 | -0.14191 | -0.36621 | -0.33417 | -0.3067 | -0.07782 | 121.344 | 121.6095 | 61.084 | -121.4035 | 121.2936 | 121.3577 | 61.116 | -121.463
312.9062 | 121.7926 | -61.0794 | 60.3561 | 0.0026703 | 0.0010233 | 0.067964 | -0.0011024 | 0.069252 | 0.0030591 | 0.0019611 | -0.013123 | -0.00085232 | 0.06633 | 0.067396 | -0.19421 | -6.2012e-05 | 60.5255 | -61.0565 | -0.041199 | -61.1526 | 60.3104 | -61.1893 | -61.0611 | -61.5097 | -0.036621 | -61.4868 | 60.2554 | 60.2966 | -60.9283 | -61.1435 | -0.10986 | 0.018311 | -0.045776 | 0.022888 | -0.073242 | -0.091553 | 0.16937 | 0.15106 | -0.064087 | -0.10071 | -0.4303 | -0.40741 | -0.34332 | -0.059509 | 121.3898 | 121.6049 | 61.0382 | -121.4172 | 121.3348 | 121.376 | 61.0428 | -121.4996
314.5938 | 121.7743 | -61.0748 | 60.4065 | 0.0103 | 0.0044411 | 0.068391 | 0.0042382 | 0.066048 | -0.0048449 | 3.8456e-05 | -0.0054932 | -0.0036295 | 0.063126 | 0.068037 | -0.19592 | 0.0012198 | 60.5759 | -60.9329 | 0.054932 | -61.1023 | 60.2142 | -61.1389 | -61.0153 | -61.441 | 0.059509 | -61.3861 | 60.2371 | 60.2921 | -60.8734 | -61.0977 | -0.064087 | 0.059509 | -0.19226 | 0.14191 | -0.027466 | -0.086975 | 0.16937 | 0.20142 | -0.022888 | -0.16937 | -0.36621 | -0.31128 | -0.28839 | -0.11444 | 121.2891 | 121.6507 | 61.1298 | -121.4218 | 121.312 | 121.3669 | 61.1343 | -121.5042
316.3438 | 121.8338 | -61.0016 | 60.4477 | -0.0049592 | 0.0035867 | 0.065401 | -3.4178e-05 | 0.06733 | -0.0042041 | -0.0016705 | -0.0054932 | -0.0029885 | 0.063339 | 0.069105 | -0.19806 | -0.00027561 | 60.6445 | -60.8734 | 0.12817 | -61.0153 | 60.3104 | -61.116 | -60.9787 | -61.3724 | 0.13275 | -61.29 | 60.2737 | 60.3607 | -60.8368 | -61.0336 | -0.11444 | 0.022888 | -0.13733 | 0.12817 | -0.013733 | -0.036621 | 0.19684 | 0.16479 | -0.032043 | -0.17395 | -0.37079 | -0.28839 | -0.25635 | -0.086975 | 121.312 | 121.6461 | 61.1298 | -121.4264 | 121.2753 | 121.3623 | 61.1343 | -121.4813
318.1094 | 121.8155 | -61.0336 | 60.4523 | 0.0026703 | 0.0067911 | 0.066255 | 0.0014612 | 0.066902 | -0.0020679 | 0.00046566 | 0.0021363 | -0.0036295 | 0.064194 | 0.067396 | -0.19955 | -0.00070281 | 60.5804 | -60.9375 | 0.045776 | -61.0703 | 60.3012 | -61.1114 | -61.0107 | -61.4365 | 0.045776 | -61.3541 | 60.2554 | 60.3149 | -60.8688 | -61.0657 | -0.07782 | 0.022888 | -0.15106 | 0.09613 | -0.036621 | -0.059509 | 0.12817 | 0.1648 | -0.032044 | -0.19684 | -0.40283 | -0.32043 | -0.28839 | -0.13733 | 121.3348 | 121.6141 | 61.0794 | -121.463 | 121.2891 | 121.3486 | 61.0794 | -121.5179
319.875 | 121.7194 | -61.0657 | 60.4523 | -0.0049592 | -0.0017539 | 0.066042 | 0.0014612 | 0.067116 | 0.0045545 | 0.0026019 | -0.013123 | -0.0014933 | 0.066544 | 0.065901 | -0.19592 | -0.0036936 | 60.5896 | -60.965 | 0.073242 | -61.0657 | 60.3882 | -61.116 | -61.0153 | -61.4365 | 0.059509 | -61.4136 | 60.3287 | 60.3745 | -60.8551 | -61.084 | -0.050354 | 0.050354 | -0.064087 | 0.10071 | 0 | -0.050354 | 0.13733 | 0.21057 | -0.01831 | -0.1236 | -0.37079 | -0.3479 | -0.32959 | -0.07782 | 121.4539 | 121.6553 | 61.1389 | -121.4676 | 121.3943 | 121.4401 | 61.1252 | -121.5363
321.5781 | 121.7331 | -61.0291 | 60.4523 | -0.0049592 | -0.00089927 | 0.064546 | 0.0014612 | 0.066262 | 0.0039135 | 0.0015339 | -0.0054932 | 0.0017111 | 0.066757 | 0.071455 | -0.1972 | -0.0015572 | 60.6171 | -60.9604 | 0.07782 | -61.0611 | 60.3561 | -61.1252 | -61.0107 | -61.4136 | 0.082397 | -61.4044 | 60.3149 | 60.3607 | -60.878 | -61.116 | -0.09613 | 0.018311 | -0.096131 | 0.068665 | -0.032043 | -0.050354 | 0.16479 | 0.15106 | -0.086975 | -0.13733 | -0.38452 | -0.37537 | -0.28839 | -0.091553 | 121.3852 | 121.6461 | 61.1069 | -121.463 | 121.344 | 121.3898 | 61.1114 | -121.5683
323.3594 | 121.6736 | -61.0291 | 60.4843 | -0.0049592 | 0.00038233 | 0.06946 | 0.0014612 | 0.068611 | -0.0022815 | 0.0013203 | 0.0021363 | -0.0027749 | 0.064835 | 0.067396 | -0.19998 | -0.0015572 | 60.6079 | -60.9055 | 0.12817 | -61.0336 | 60.3287 | -61.084 | -60.965 | -61.4227 | 0.086975 | -61.3861 | 60.3378 | 60.4019 | -60.8368 | -61.0565 | -0.054931 | 0.064087 | -0.15564 | 0.1236 | -0.004577 | -0.068664 | 0.1236 | 0.19226 | -0.027466 | -0.14648 | -0.39368 | -0.35706 | -0.32959 | -0.082397 | 121.3577 | 121.637 | 61.1572 | -121.4493 | 121.3669 | 121.431 | 61.116 | -121.5408
325.1406 | 121.7743 | -61.0291 | 60.4614 | 0.0026703 | 0.0040139 | 0.067964 | 0.0025292 | 0.067757 | -0.0035633 | -0.0025249 | -0.0054932 | -0.0038431 | 0.06633 | 0.068037 | -0.19934 | -0.00070281 | 60.6674 | -60.8185 | 0.16479 | -61.0062 | 60.3378 | -61.0657 | -60.965 | -61.3495 | 0.16937 | -61.2946 | 60.2554 | 60.3516 | -60.8139 | -61.0336 | -0.036621 | 0.064087 | -0.1236 | 0.21057 | 0.022888 | -0.041199 | 0.20599 | 0.21515 | -0.004577 | -0.20599 | -0.32043 | -0.2655 | -0.26093 | -0.10986 | 121.3669 | 121.6965 | 61.1938 | -121.4264 | 121.2845 | 121.3806 | 61.1984 | -121.4951
326.8438 | 121.8018 | -61.0748 | 60.3836 | -0.012589 | 0.0014505 | 0.066255 | -0.00046138 | 0.067971 | 0.0024183 | 0.0026019 | -0.0054932 | 0.00064308 | 0.064835 | 0.068464 | -0.19528 | -0.0024118 | 60.5347 | -61.0428 | -0.036621 | -61.1526 | 60.3104 | -61.1801 | -61.0382 | -61.4868 | -0.036621 | -61.4594 | 60.2325 | 60.2921 | -60.9329 | -61.1343 | -0.10529 | 0.036621 | -0.073242 | 0.032043 | -0.07782 | -0.11444 | 0.15106 | 0.14191 | -0.059509 | -0.15106 | -0.41199 | -0.38452 | -0.32501 | -0.091553 | 121.3852 | 121.6095 | 61.0382 | -121.4218 | 121.3074 | 121.3669 | 61.0382 | -121.5179
328.6094 | 121.7926 | -61.0062 | 60.4568 | -0.0049592 | 0.0031595 | 0.065828 | 0.0040246 | 0.067543 | -0.0054859 | 0.00067926 | -0.0054932 | -0.0046975 | 0.066971 | 0.064833 | -0.20126 | -0.0021982 | 60.6857 | -60.7956 | 0.1831 | -61.0062 | 60.3149 | -61.084 | -60.9329 | -61.3449 | 0.18768 | -61.2854 | 60.2646 | 60.3561 | -60.8322 | -61.0291 | -0.077819 | 0.073243 | -0.14191 | 0.21057 | 0 | -0.073243 | 0.22888 | 0.17395 | -0.022888 | -0.19226 | -0.33874 | -0.27923 | -0.25635 | -0.10071 | 121.3211 | 121.6919 | 61.1893 | -121.3898 | 121.2708 | 121.3623 | 61.1938 | -121.4859
330.375 | 121.6919 | -61.0931 | 60.4248 | -0.0049592 | -0.00089927 | 0.066683 | 0.0027428 | 0.067971 | 0.0034863 | 0.0034565 | 0.0021363 | 0.00085668 | 0.065048 | 0.06761 | -0.19442 | -0.0032662 | 60.6079 | -60.9512 | 0.073242 | -61.0794 | 60.3333 | -61.1069 | -61.0016 | -61.4365 | 0.064087 | -61.4319 | 60.2829 | 60.3378 | -60.8688 | -61.1023 | -0.013733 | 0.091553 | -0.091553 | 0.14191 | 0.013733 | -0.07782 | 0.1831 | 0.22431 | -0.009155 | -0.14191 | -0.34332 | -0.33875 | -0.32959 | -0.086975 | 121.4264 | 121.701 | 61.1664 | -121.4264 | 121.376 | 121.431 | 61.1572 | -121.5271
332.125 | 121.701 | -61.0977 | 60.434 | -0.0049592 | 0.0033731 | 0.062624 | -3.4178e-05 | 0.067757 | 0.0039135 | 0.0036701 | -0.013123 | -0.0014933 | 0.064835 | 0.071028 | -0.19507 | -0.0036936 | 60.4935 | -61.0931 | -0.054932 | -61.171 | 60.3012 | -61.171 | -61.0382 | -61.5097 | -0.032043 | -61.5051 | 60.26 | 60.3333 | -60.9329 | -61.1389 | -0.073242 | 0.059509 | -0.13275 | 0.004577 | -0.073242 | -0.13275 | 0.059509 | 0.1648 | -0.041199 | -0.17395 | -0.41199 | -0.40741 | -0.36621 | -0.10071 | 121.3989 | 121.5912 | 61.0428 | -121.4722 | 121.3577 | 121.431 | 61.0657 | -121.5729
333.8281 | 121.7422 | -61.0474 | 60.4477 | 0.0026703 | 0.0016641 | 0.063905 | 0.0018884 | 0.065834 | -0.00014533 | 0.0019611 | -0.0054932 | -0.0025613 | 0.066971 | 0.066328 | -0.19742 | -6.2012e-05 | 60.5438 | -60.9558 | 0.059509 | -61.0703 | 60.3516 | -61.1114 | -61.0016 | -61.4273 | 0.082397 | -61.3861 | 60.3241 | 60.3973 | -60.8459 | -61.084 | -0.064087 | 0.045776 | -0.096131 | 0.091552 | -0.022888 | -0.068664 | 0.09613 | 0.20142 | -0.036621 | -0.1236 | -0.37994 | -0.33875 | -0.30212 | -0.050354 | 121.3989 | 121.5912 | 61.1069 | -121.4493 | 121.3715 | 121.4447 | 61.1298 | -121.5317
335.5938 | 121.6873 | -61.0886 | 60.4111 | 0.0026703 | 0.0012369 | 0.064974 | -0.0032386 | 0.06733 | 0.0017773 | 0.0043109 | 0.0021363 | 0.00085668 | 0.06633 | 0.071668 | -0.19507 | 0.00079259 | 60.4935 | -61.0657 | -0.036621 | -61.1389 | 60.3149 | -61.171 | -61.0382 | -61.528 | -0.059509 | -61.5143 | 60.2646 | 60.3378 | -60.9238 | -61.1252 | -0.082397 | 0.050354 | -0.096131 | 0.022888 | -0.050354 | -0.10071 | 0.082397 | 0.1648 | -0.036621 | -0.14648 | -0.43945 | -0.42572 | -0.3891 | -0.073242 | 121.4035 | 121.582 | 61.0519 | -121.4493 | 121.3531 | 121.4264 | 61.0291 | -121.5363
337.3594 | 121.7285 | -61.0474 | 60.466 | -0.0049592 | -0.0019675 | 0.068605 | -3.4178e-05 | 0.067543 | -0.0031359 | 0.00067926 | -0.013123 | -0.00063872 | 0.066544 | 0.068891 | -0.19806 | 0.00079259 | 60.5667 | -60.9604 | 0.073242 | -61.0657 | 60.4065 | -61.0977 | -60.9741 | -61.4502 | 0.054932 | -61.4044 | 60.3287 | 60.3882 | -60.8505 | -61.0382 | -0.050354 | 0.073242 | -0.059509 | 0.086975 | -0.018311 | -0.091553 | 0.10071 | 0.19684 | 0.009155 | -0.13733 | -0.40283 | -0.35706 | -0.36621 | -0.077819 | 121.4539 | 121.6141 | 61.1206 | -121.4401 | 121.376 | 121.4355 | 61.1023 | -121.5042
339.0781 | 121.8246 | -61.0199 | 60.4706 | 0.0026703 | 0.0038003 | 0.067964 | 0.0027428 | 0.063484 | -0.0059131 | -0.0010297 | -0.013123 | -0.0042703 | 0.064835 | 0.067823 | -0.19934 | 0.0012198 | 60.5759 | -60.91 | 0.086975 | -61.0382 | 60.3195 | -61.1069 | -60.9833 | -61.3907 | 0.1236 | -61.3083 | 60.2554 | 60.3607 | -60.8368 | -61.0611 | -0.086976 | 0.036621 | -0.15106 | 0.10986 | -0.018311 | -0.054932 | 0.10529 | 0.1831 | -0.041199 | -0.21515 | -0.37079 | -0.28839 | -0.24719 | -0.10986 | 121.3394 | 121.5958 | 61.1069 | -121.4539 | 121.2753 | 121.3806 | 61.1435 | -121.5317
340.8438 | 121.7972 | -61.0611 | 60.3745 | -0.0049592 | 0.0044411 | 0.064974 | -0.00088858 | 0.066262 | -0.00014533 | 0.0011067 | -0.0054932 | -0.0032021 | 0.063126 | 0.068037 | -0.1972 | -0.0026254 | 60.5713 | -60.9238 | 0.064087 | -61.0748 | 60.2371 | -61.1481 | -61.0016 | -61.4044 | 0.064087 | -61.377 | 60.1913 | 60.2509 | -60.9055 | -61.1069 | -0.086975 | 0.059509 | -0.13733 | 0.13733 | -0.013733 | -0.073242 | 0.19684 | 0.15564 | -0.045777 | -0.18311 | -0.34332 | -0.31586 | -0.27008 | -0.1236 | 121.2982 | 121.6324 | 61.1252 | -121.376 | 121.2524 | 121.3119 | 61.1252 | -121.4813
342.5312 | 121.7697 | -61.0519 | 60.4065 | -0.020218 | 0.0050821 | 0.067537 | -0.00024778 | 0.069039 | -0.0029223 | 0.0011067 | -0.0054932 | -0.0040567 | 0.062057 | 0.067823 | -0.19763 | -0.00113 | 60.5804 | -60.9375 | 0.045776 | -61.0931 | 60.2463 | -61.1343 | -61.0107 | -61.4365 | 0.045776 | -61.3678 | 60.2371 | 60.2829 | -60.8551 | -61.0794 | -0.082397 | 0.041199 | -0.16022 | 0.11444 | -0.041199 | -0.082398 | 0.17395 | 0.19684 | -0.027466 | -0.16937 | -0.38452 | -0.31586 | -0.28839 | -0.1236 | 121.2982 | 121.6324 | 61.0977 | -121.4172 | 121.2891 | 121.3348 | 61.0977 | -121.4859
344.2969 | 121.7972 | -61.0474 | 60.3745 | 0.0026703 | 0.0035867 | 0.066042 | 0.00017942 | 0.068611 | 0.00049567 | -0.00060234 | 0.0097658 | -0.0029885 | 0.063126 | 0.070387 | -0.1972 | -0.002839 | 60.5713 | -60.9146 | 0.041199 | -61.0703 | 60.2509 | -61.1481 | -61.0153 | -61.3953 | 0.059509 | -61.3724 | 60.1959 | 60.2463 | -60.9009 | -61.1114 | -0.10071 | 0.032043 | -0.1236 | 0.13275 | -0.022888 | -0.054931 | 0.19684 | 0.14648 | -0.064087 | -0.17853 | -0.3479 | -0.32501 | -0.26093 | -0.12817 | 121.2982 | 121.6187 | 61.0886 | -121.3898 | 121.2433 | 121.2936 | 61.1069 | -121.4859
346.0469 | 121.7606 | -61.0519 | 60.3836 | 0.0026703 | 0.0061501 | 0.067323 | 0.002102 | 0.068611 | -0.0037769 | -0.00060234 | -0.0054932 | -0.0012795 | 0.063339 | 0.066328 | -0.19613 | -0.00113 | 60.5804 | -60.9055 | 0.059509 | -61.0611 | 60.2234 | -61.1481 | -61.0245 | -61.4044 | 0.073242 | -61.3541 | 60.2005 | 60.2554 | -60.8963 | -61.1023 | -0.09613 | 0.027466 | -0.16022 | 0.14648 | -0.009155 | -0.036621 | 0.19684 | 0.15564 | -0.050354 | -0.18311 | -0.35248 | -0.30212 | -0.25177 | -0.12817 | 121.2753 | 121.6324 | 61.1114 | -121.4081 | 121.2524 | 121.3074 | 61.1252 | -121.4859
347.7344 | 121.8292 | -61.0016 | 60.4431 | -0.0049592 | 0.0035867 | 0.067323 | 0.0029566 | 0.069252 | -0.0035633 | 0.00046566 | -0.0054932 | -0.0032021 | 0.063766 | 0.065901 | -0.19742 | -0.0013436 | 60.5942 | -60.9009 | 0.068665 | -61.0519 | 60.3104 | -61.0748 | -60.9604 | -61.3953 | 0.086975 | -61.2946 | 60.2692 | 60.3333 | -60.8414 | -61.0519 | -0.073242 | 0.041199 | -0.13275 | 0.10071 | -0.050354 | -0.091553 | 0.15106 | 0.16022 | -0.050354 | -0.17395 | -0.39368 | -0.29297 | -0.24262 | -0.10986 | 121.312 | 121.5958 | 61.0703 | -121.4035 | 121.2708 | 121.3348 | 61.0886 | -121.4951
349.5 | 121.7194 | -61.0657 | 60.4523 | -0.0049592 | -0.0019675 | 0.061556 | 0.0014612 | 0.06733 | 0.0041273 | 0.00025206 | 0.0097658 | 2.078e-06 | 0.06633 | 0.069105 | -0.19442 | -0.0047616 | 60.6125 | -60.9329 | 0.086975 | -61.0519 | 60.347 | -61.1298 | -61.0107 | -61.3998 | 0.073242 | -61.3998 | 60.3012 | 60.3333 | -60.8826 | -61.084 | -0.064087 | 0.054932 | -0.10529 | 0.13275 | 0.013733 | -0.041199 | 0.16022 | 0.18311 | -0.01831 | -0.15106 | -0.33417 | -0.33417 | -0.31586 | -0.11902 | 121.4127 | 121.6782 | 61.1526 | -121.463 | 121.3669 | 121.3989 | 61.1389 | -121.5363
351.2656 | 121.8155 | -60.9924 | 60.4614 | -0.0049592 | 0.0050821 | 0.066896 | 0.0027428 | 0.067971 | -0.0042041 | 0.00046566 | -0.0054932 | -0.0053385 | 0.064407 | 0.066114 | -0.20062 | -0.0015572 | 60.6674 | -60.8231 | 0.16022 | -60.9833 | 60.3012 | -61.0611 | -60.9512 | -61.3266 | 0.17395 | -61.2534 | 60.2737 | 60.3516 | -60.8047 | -61.0382 | -0.068664 | 0.041199 | -0.16022 | 0.16937 | 0.009156 | -0.032043 | 0.20599 | 0.18768 | -0.045776 | -0.18768 | -0.33417 | -0.26093 | -0.21515 | -0.10986 | 121.2936 | 121.6599 | 61.1526 | -121.4127 | 121.2662 | 121.344 | 61.1664 | -121.4996
353.0312 | 121.701 | -61.0794 | 60.4385 | 0.0026703 | -0.00089927 | 0.063905 | 0.0027428 | 0.064766 | 0.0054089 | 0.00046566 | 0.0021363 | -0.0010659 | 0.06633 | 0.068678 | -0.19507 | -0.004548 | 60.6033 | -60.9192 | 0.07782 | -61.0428 | 60.3333 | -61.1343 | -60.9924 | -61.3953 | 0.086975 | -61.3861 | 60.3058 | 60.3561 | -60.8551 | -61.0748 | -0.054931 | 0.086975 | -0.10529 | 0.16022 | 0.036621 | -0.050354 | 0.16479 | 0.2243 | 0.004578 | -0.13275 | -0.31586 | -0.3067 | -0.31128 | -0.082398 | 121.4127 | 121.6827 | 61.1572 | -121.431 | 121.3852 | 121.4355 | 61.1664 | -121.5134
354.7344 | 121.7056 | -61.0245 | 60.4797 | -0.0049592 | 0.00038233 | 0.066683 | 0.0016748 | 0.06733 | 0.00049567 | 0.00025206 | 0.0021363 | -0.0021341 | 0.067184 | 0.068037 | -0.19912 | -0.00070281 | 60.5804 | -60.9421 | 0.068665 | -61.0611 | 60.3699 | -61.0977 | -60.9879 | -61.4365 | 0.050354 | -61.3998 | 60.3653 | 60.3973 | -60.8459 | -61.0657 | -0.073242 | 0.036621 | -0.10986 | 0.082397 | -0.036621 | -0.073242 | 0.10071 | 0.17853 | -0.041199 | -0.11444 | -0.41199 | -0.37537 | -0.33417 | -0.082397 | 121.3943 | 121.6049 | 61.0931 | -121.4676 | 121.3898 | 121.4218 | 61.0748 | -121.5454
356.4844 | 121.701 | -61.0245 | 60.4889 | 0.0026703 | 0.0014505 | 0.067964 | 0.0018884 | 0.066048 | -0.0014269 | 3.8456e-05 | -0.0054932 | -0.0010659 | 0.067825 | 0.068891 | -0.19635 | -6.2012e-05 | 60.553 | -60.9238 | 0.073242 | -61.0611 | 60.3882 | -61.0977 | -60.9512 | -61.4182 | 0.064087 | -61.4044 | 60.347 | 60.4248 | -60.8368 | -61.0519 | -0.073242 | 0.073242 | -0.10071 | 0.10071 | -0.036621 | -0.10986 | 0.064087 | 0.18768 | -0.027466 | -0.14191 | -0.39368 | -0.37994 | -0.35248 | -0.064087 | 121.4127 | 121.5775 | 61.0977 | -121.4401 | 121.3715 | 121.4493 | 61.0886 | -121.5408
358.1875 | 121.8155 | -61.0016 | 60.4523 | -0.012589 | 0.0044411 | 0.068819 | 0.0018884 | 0.064125 | -0.0042041 | 0.0015339 | -0.0054932 | -0.0066201 | 0.06398 | 0.066755 | -0.1987 | -0.0013436 | 60.5621 | -60.91 | 0.07782 | -61.0474 | 60.3058 | -61.1114 | -60.997 | -61.4182 | 0.082397 | -61.3174 | 60.2554 | 60.3287 | -60.8322 | -61.0611 | -0.10986 | 0.004578 | -0.14649 | 0.091553 | -0.045776 | -0.050354 | 0.10986 | 0.16937 | -0.059509 | -0.19684 | -0.41656 | -0.31586 | -0.25635 | -0.1236 | 121.3074 | 121.5637 | 61.0794 | -121.4493 | 121.257 | 121.3303 | 61.084 | -121.5134
359.9531 | 121.7194 | -61.0565 | 60.4385 | 0.0026703 | -0.00025847 | 0.064119 | -0.00088858 | 0.066689 | 0.0036999 | 0.0038837 | 0.0097658 | -0.0010659 | 0.065048 | 0.067396 | -0.19528 | -0.002839 | 60.6171 | -60.9146 | 0.082397 | -61.0291 | 60.3424 | -61.1023 | -60.9741 | -61.3861 | 0.086975 | -61.3815 | 60.3149 | 60.347 | -60.8368 | -61.084 | -0.045776 | 0.082398 | -0.096131 | 0.14191 | 0.027466 | -0.054932 | 0.17853 | 0.21973 | -0.027465 | -0.1236 | -0.32959 | -0.32501 | -0.29755 | -0.091553 | 121.3989 | 121.6736 | 61.1389 | -121.4127 | 121.3715 | 121.4035 | 61.1435 | -121.5225
361.6562 | 121.756 | -61.0519 | 60.4294 | 0.0026703 | 0.0035867 | 0.06476 | -0.00088858 | 0.064766 | -0.0024951 | 3.8456e-05 | 0.0021363 | -0.0042703 | 0.06398 | 0.065687 | -0.19699 | 0.0010062 | 60.6033 | -60.8688 | 0.068665 | -61.0657 | 60.2417 | -61.1298 | -60.9879 | -61.4227 | 0.054932 | -61.3586 | 60.2142 | 60.2921 | -60.8688 | -61.0931 | -0.07782 | 0.064087 | -0.18768 | 0.18311 | -0.013733 | -0.07782 | 0.17395 | 0.18311 | -0.041199 | -0.21515 | -0.37079 | -0.3067 | -0.2655 | -0.13733 | 121.2936 | 121.6553 | 61.1206 | -121.4172 | 121.2662 | 121.344 | 61.1069 | -121.5225
363.4219 | 121.7926 | -61.0428 | 60.3653 | 0.0103 | 0.0029459 | 0.06476 | -0.0038794 | 0.066902 | 0.0017773 | 0.0015339 | 0.0021363 | -0.0017069 | 0.064835 | 0.0706 | -0.19613 | -0.0015572 | 60.5392 | -61.0107 | -0.018311 | -61.116 | 60.2966 | -61.1435 | -61.0474 | -61.4456 | 0.009155 | -61.4182 | 60.2463 | 60.3333 | -60.878 | -61.0703 | -0.10071 | -0.004577 | -0.068664 | 0.032044 | -0.073242 | -0.068665 | 0.17395 | 0.16479 | -0.027465 | -0.11902 | -0.40283 | -0.37537 | -0.3479 | -0.032043 | 121.3394 | 121.582 | 61.0245 | -121.4127 | 121.2891 | 121.376 | 61.0519 | -121.4355
365.125 | 121.7377 | -61.0382 | 60.466 | -0.0049592 | -0.00047207 | 0.06711 | -0.00024778 | 0.068825 | 0.0013501 | 0.0019611 | 0.0097658 | 2.078e-06 | 0.064835 | 0.066755 | -0.19613 | -0.00091641 | 60.585 | -60.9283 | 0.073242 | -61.0382 | 60.3836 | -61.1023 | -60.9879 | -61.3953 | 0.064087 | -61.3815 | 60.3287 | 60.3516 | -60.8597 | -61.0931 | -0.064087 | 0.050354 | -0.082397 | 0.10986 | 0 | -0.050354 | 0.11902 | 0.17853 | -0.054932 | -0.13733 | -0.35706 | -0.34332 | -0.28839 | -0.11444 | 121.4218 | 121.6232 | 61.1114 | -121.4539 | 121.3669 | 121.3898 | 61.1023 | -121.5591
366.9062 | 121.6644 | -61.0428 | 60.5255 | -0.0049592 | 0.0010233 | 0.06476 | 0.0016748 | 0.066048 | 0.00028207 | 0.00089286 | -0.0054932 | -0.0019205 | 0.06633 | 0.06825 | -0.20019 | -0.0021982 | 60.6033 | -60.8963 | 0.086975 | -61.0382 | 60.3745 | -61.0886 | -60.9604 | -61.4182 | 0.064087 | -61.3632 | 60.3241 | 60.4019 | -60.8276 | -61.0199 | -0.045776 | 0.082398 | -0.15106 | 0.14648 | 0.004578 | -0.07782 | 0.07782 | 0.21515 | 0.022889 | -0.20142 | -0.37537 | -0.32043 | -0.34332 | -0.1236 | 121.4172 | 121.6461 | 61.1298 | -121.4859 | 121.3669 | 121.4447 | 61.1069 | -121.5454
368.6094 | 121.7468 | -61.0336 | 60.4568 | -0.0049592 | 0.0091409 | 0.064974 | -3.4178e-05 | 0.066475 | -0.0059131 | -0.00017514 | 0.0021363 | -0.0053385 | 0.065689 | 0.068037 | -0.19934 | 0.0018606 | 60.585 | -60.91 | 0.045776 | -61.0519 | 60.2737 | -61.1114 | -60.9924 | -61.4273 | 0.045776 | -61.3678 | 60.2188 | 60.3287 | -60.8414 | -61.0703 | -0.07782 | 0.041198 | -0.1831 | 0.1236 | -0.018311 | -0.059509 | 0.12817 | 0.19226 | -0.036621 | -0.23804 | -0.39368 | -0.33417 | -0.29755 | -0.12817 | 121.3074 | 121.6187 | 61.0794 | -121.4493 | 121.2524 | 121.3623 | 61.0794 | -121.5271
370.3594 | 121.7468 | -61.0016 | 60.4843 | 0.0026703 | 0.00059593 | 0.068391 | 0.0029566 | 0.068184 | -0.0039905 | -0.0010297 | -0.0054932 | -0.0049111 | 0.063553 | 0.066755 | -0.19784 | -0.0019846 | 60.6766 | -60.7864 | 0.17853 | -60.965 | 60.3287 | -61.0016 | -60.9009 | -61.322 | 0.15564 | -61.2534 | 60.2875 | 60.3378 | -60.7819 | -61.0199 | 0 | 0.10071 | -0.15564 | 0.21515 | 0.036621 | -0.064087 | 0.19226 | 0.21973 | -0.01831 | -0.19684 | -0.32043 | -0.25177 | -0.23346 | -0.14648 | 121.3303 | 121.6782 | 61.1801 | -121.3852 | 121.2891 | 121.3394 | 61.1572 | -121.5042
372.125 | 121.7331 | -61.0519 | 60.4477 | -0.012589 | -0.00025847 | 0.067537 | -0.00024778 | 0.065621 | 0.0019909 | 0.00089286 | 0.0021363 | -0.0032021 | 0.065048 | 0.068037 | -0.19485 | -0.0021982 | 60.5988 | -60.9421 | 0.07782 | -61.0382 | 60.3653 | -61.116 | -60.9741 | -61.3907 | 0.064087 | -61.3724 | 60.347 | 60.379 | -60.8414 | -61.084 | -0.064087 | 0.07782 | -0.082398 | 0.10986 | 0.013733 | -0.064087 | 0.15106 | 0.21057 | -0.032043 | -0.10071 | -0.33875 | -0.32043 | -0.28839 | -0.068665 | 121.4172 | 121.6507 | 61.1298 | -121.4218 | 121.3989 | 121.431 | 61.116 | -121.5317
373.8906 | 121.7972 | -60.965 | 60.4568 | -0.0049592 | 0.0016641 | 0.069032 | 0.0018884 | 0.068611 | -0.0048449 | -0.00081594 | 0.0021363 | -0.0042703 | 0.066116 | 0.068464 | -0.19998 | 0.00015159 | 60.6674 | -60.7956 | 0.16022 | -60.9741 | 60.3012 | -61.0519 | -60.9375 | -61.3129 | 0.16937 | -61.235 | 60.2829 | 60.3699 | -60.7956 | -61.0199 | -0.086975 | 0.027466 | -0.15564 | 0.16937 | -0.009155 | -0.036621 | 0.21057 | 0.16937 | -0.054931 | -0.17395 | -0.3479 | -0.27008 | -0.21515 | -0.086975 | 121.2662 | 121.6324 | 61.1252 | -121.3943 | 121.2479 | 121.3348 | 61.1343 | -121.4767
375.5781 | 121.7194 | -61.0199 | 60.4797 | 0.0026703 | 0.00016873 | 0.062196 | 0.0046656 | 0.06498 | 0.00070927 | 3.8456e-05 | 0.0021363 | 2.078e-06 | 0.068039 | 0.069105 | -0.1972 | -0.002839 | 60.6033 | -60.9283 | 0.082397 | -61.0336 | 60.4111 | -61.0748 | -60.9695 | -61.4182 | 0.036621 | -61.3861 | 60.3653 | 60.4019 | -60.8322 | -61.0199 | -0.054932 | 0.050354 | -0.068664 | 0.091552 | -0.013733 | -0.064087 | 0.1236 | 0.18768 | 0 | -0.11444 | -0.39825 | -0.36621 | -0.36621 | -0.077819 | 121.431 | 121.6232 | 61.1023 | -121.4493 | 121.3852 | 121.4218 | 61.0565 | -121.4996
377.3438 | 121.7514 | -61.0153 | 60.4797 | -0.012589 | -0.0015403 | 0.066683 | 0.0042382 | 0.066689 | 0.0034863 | 0.0021747 | 0.0021363 | 0.0017111 | 0.065262 | 0.068464 | -0.19528 | -0.0026254 | 60.6125 | -60.91 | 0.073242 | -61.0199 | 60.4019 | -61.084 | -60.9787 | -61.3907 | 0.07782 | -61.3678 | 60.3241 | 60.3836 | -60.8368 | -61.0703 | -0.068664 | 0.036621 | -0.077819 | 0.10529 | -0.004577 | -0.041198 | 0.13275 | 0.17853 | -0.054931 | -0.15564 | -0.37537 | -0.35248 | -0.29755 | -0.09613 | 121.4172 | 121.6278 | 61.0886 | -121.4584 | 121.3394 | 121.3989 | 61.0931 | -121.55
379.1094 | 121.7651 | -61.0153 | 60.4706 | -0.012589 | 0.0018777 | 0.067537 | 0.0018884 | 0.066475 | -0.0044177 | 0.0026019 | 0.0021363 | -0.0057657 | 0.066544 | 0.066328 | -0.19848 | -0.00048921 | 60.585 | -60.8963 | 0.045776 | -61.0336 | 60.2921 | -61.1023 | -60.965 | -61.4044 | 0.032043 | -61.3495 | 60.2692 | 60.3607 | -60.8505 | -61.0336 | -0.086975 | 0.050354 | -0.17853 | 0.11902 | -0.01831 | -0.068664 | 0.11444 | 0.1648 | -0.01831 | -0.20142 | -0.3891 | -0.33417 | -0.31586 | -0.10986 | 121.3074 | 121.6003 | 61.0611 | -121.4355 | 121.2845 | 121.376 | 61.0474 | -121.5042
380.7969 | 121.7148 | -61.0016 | 60.5026 | 0.0026703 | 0.00038233 | 0.067751 | 0.003811 | 0.067757 | -0.0018543 | -0.0014569 | -0.0054932 | -0.0040567 | 0.065262 | 0.066755 | -0.19806 | -6.2012e-05 | 60.672 | -60.7956 | 0.17395 | -60.965 | 60.3333 | -61.0291 | -60.9146 | -61.322 | 0.15106 | -61.2671 | 60.2875 | 60.347 | -60.7956 | -61.0199 | -0.027466 | 0.086975 | -0.16937 | 0.20599 | 0.036621 | -0.050354 | 0.16937 | 0.20599 | -0.01831 | -0.21515 | -0.32043 | -0.2655 | -0.24719 | -0.15564 | 121.3348 | 121.6736 | 61.1755 | -121.4172 | 121.2891 | 121.3486 | 61.1526 | -121.5225
382.5 | 121.6599 | -61.084 | 60.4431 | -0.0049592 | 0.00080973 | 0.063051 | -0.00067498 | 0.065621 | 0.0051953 | 0.00089286 | -0.013123 | 0.00021568 | 0.065903 | 0.066969 | -0.19186 | -0.00113 | 60.5942 | -60.9604 | 0.032043 | -61.0611 | 60.3378 | -61.1114 | -60.9695 | -61.4273 | 0.009155 | -61.4456 | 60.2966 | 60.3424 | -60.8688 | -61.0977 | -0.027466 | 0.11444 | -0.10529 | 0.1236 | 0.022888 | -0.091553 | 0.15106 | 0.21515 | -0.013733 | -0.14648 | -0.34332 | -0.36163 | -0.3479 | -0.10071 | 121.4218 | 121.6782 | 61.116 | -121.4127 | 121.3806 | 121.4264 | 61.0931 | -121.5408
384.2031 | 121.8063 | -61.0428 | 60.3745 | -0.0049592 | 0.0038003 | 0.06476 | -0.00046138 | 0.066262 | 0.00092287 | 0.0036701 | 0.0021363 | -0.00063872 | 0.063339 | 0.070173 | -0.19742 | -0.0015572 | 60.5484 | -60.9879 | -0.004578 | -61.0977 | 60.2829 | -61.1526 | -61.0291 | -61.4365 | 0.022888 | -61.3907 | 60.2463 | 60.3149 | -60.8734 | -61.0611 | -0.10986 | 0.013733 | -0.091553 | 0.054932 | -0.054931 | -0.068664 | 0.17395 | 0.16937 | -0.01831 | -0.12817 | -0.39368 | -0.3479 | -0.32959 | -0.05951 | 121.3257 | 121.5912 | 61.0382 | -121.4035 | 121.2891 | 121.3577 | 61.0657 | -121.4355
385.8906 | 121.788 | -60.9558 | 60.4706 | -0.0049592 | 0.0023049 | 0.067323 | 0.0029566 | 0.067757 | -0.0048449 | 0.0021747 | 0.0021363 | -0.0061929 | 0.064407 | 0.066755 | -0.19848 | -0.0013436 | 60.704 | -60.7636 | 0.16937 | -60.9558 | 60.3333 | -61.0291 | -60.9146 | -61.3083 | 0.19226 | -61.2213 | 60.2921 | 60.4065 | -60.759 | -60.965 | -0.073242 | 0.041199 | -0.13733 | 0.19226 | 0 | -0.041199 | 0.23346 | 0.19684 | -0.009155 | -0.17853 | -0.35248 | -0.2655 | -0.25635 | -0.064087 | 121.2891 | 121.6599 | 61.1252 | -121.3852 | 121.2479 | 121.3623 | 61.1481 | -121.4355
387.5938 | 121.7468 | -61.0565 | 60.4019 | -0.012589 | 0.0016641 | 0.063905 | -0.0019568 | 0.066262 | 0.0017773 | 0.0011067 | 0.0021363 | 0.0021383 | 0.065903 | 0.069746 | -0.19421 | -0.0026254 | 60.5255 | -61.0291 | -0.054932 | -61.1114 | 60.3287 | -61.1389 | -61.0107 | -61.4685 | -0.050354 | -61.4548 | 60.2829 | 60.3699 | -60.8871 | -61.1114 | -0.082397 | 0.045777 | -0.073243 | 0.027466 | -0.054931 | -0.10071 | 0.1236 | 0.16937 | -0.054931 | -0.11902 | -0.41199 | -0.39825 | -0.34332 | -0.032044 | 121.3852 | 121.582 | 61.0016 | -121.4127 | 121.3394 | 121.4264 | 61.0062 | -121.5134
389.2969 | 121.6873 | -61.0062 | 60.4935 | -0.0049592 | -0.00089927 | 0.067323 | 0.0023156 | 0.066902 | -0.00014533 | 0.00025206 | -0.0054932 | -0.0032021 | 0.067612 | 0.065901 | -0.19635 | -0.0013436 | 60.5804 | -60.9192 | 0.073242 | -61.0336 | 60.3882 | -61.0519 | -60.9329 | -61.4319 | 0.059509 | -61.3541 | 60.3836 | 60.4111 | -60.8322 | -61.0016 | -0.045776 | 0.073243 | -0.10528 | 0.086976 | -0.027465 | -0.10071 | 0.086975 | 0.17395 | 0.004578 | -0.10986 | -0.42572 | -0.3479 | -0.35248 | -0.082397 | 121.3943 | 121.5866 | 61.0794 | -121.4264 | 121.3898 | 121.4172 | 61.0657 | -121.4951
391.0469 | 121.6644 | -61.0565 | 60.4614 | 0.0026703 | -0.0021811 | 0.064333 | -0.00088858 | 0.07032 | 0.00092287 | 0.0011067 | -0.0054932 | 0.00042948 | 0.064835 | 0.068678 | -0.19378 | -0.0015572 | 60.6125 | -60.8917 | 0.064087 | -61.0474 | 60.3607 | -61.1069 | -60.965 | -61.409 | 0.041199 | -61.3998 | 60.3012 | 60.3745 | -60.8643 | -61.084 | -0.050354 | 0.091553 | -0.10071 | 0.16479 | 0.009156 | -0.082397 | 0.15106 | 0.19226 | -0.027465 | -0.16022 | -0.35248 | -0.34332 | -0.31586 | -0.086975 | 121.4172 | 121.669 | 61.1206 | -121.4264 | 121.3577 | 121.431 | 61.0977 | -121.5454
392.7969 | 121.7102 | -61.0428 | 60.4523 | -0.012589 | 0.00038233 | 0.066469 | 0.0018884 | 0.06498 | 0.0032727 | 0.0023883 | 0.0021363 | -0.0010659 | 0.066971 | 0.066969 | -0.19549 | -0.0013436 | 60.6079 | -60.9009 | 0.09613 | -61.0291 | 60.3424 | -61.0748 | -60.9512 | -61.3815 | 0.068665 | -61.3541 | 60.3149 | 60.3516 | -60.8185 | -61.0703 | -0.032043 | 0.091553 | -0.10986 | 0.14191 | 0.013733 | -0.07782 | 0.15564 | 0.22431 | -0.027465 | -0.13733 | -0.33875 | -0.31128 | -0.28381 | -0.10071 | 121.3852 | 121.6507 | 61.1389 | -121.4035 | 121.3577 | 121.3943 | 61.1115 | -121.5225
394.5 | 121.6644 | -61.1069 | 60.434 | -0.012589 | 0.0020913 | 0.061556 | -0.00067498 | 0.064339 | 0.0024183 | 0.00089286 | -0.0054932 | -0.0019205 | 0.066116 | 0.06825 | -0.19742 | 0.00036539 | 60.5438 | -60.9741 | 0.013733 | -61.084 | 60.3516 | -61.1298 | -61.0016 | -61.4731 | -0.013733 | -61.4502 | 60.3058 | 60.347 | -60.878 | -61.0794 | -0.022888 | 0.10529 | -0.082398 | 0.13275 | 0.022889 | -0.082397 | 0.10986 | 0.22888 | 0.027466 | -0.12817 | -0.36621 | -0.34332 | -0.37079 | -0.086975 | 121.4584 | 121.6507 | 61.1206 | -121.4355 | 121.4127 | 121.4539 | 61.0931 | -121.5134
396.25 | 121.7972 | -61.0245 | 60.3928 | 0.0026703 | 0.0052957 | 0.065401 | -0.0034522 | 0.065834 | -0.0018543 | 0.0013203 | -0.0054932 | -0.0038431 | 0.064835 | 0.068037 | -0.19592 | -0.00091641 | 60.6033 | -60.8917 | 0.068665 | -61.0474 | 60.2417 | -61.1069 | -60.9787 | -61.3815 | 0.064087 | -61.3312 | 60.1913 | 60.2875 | -60.8459 | -61.0611 | -0.082398 | 0.045776 | -0.15106 | 0.13275 | -0.022888 | -0.068664 | 0.21057 | 0.17853 | -0.036621 | -0.20142 | -0.35706 | -0.3067 | -0.27008 | -0.10529 | 121.2662 | 121.6278 | 61.0931 | -121.3715 | 121.2158 | 121.312 | 61.0886 | -121.4539
398.0156 | 121.7056 | -60.9924 | 60.498 | 0.0026703 | 0.0014505 | 0.066042 | 0.0025292 | 0.06733 | -0.0056995 | 0.00025206 | -0.0054932 | -0.0034159 | 0.064194 | 0.06761 | -0.19827 | -0.00070281 | 60.672 | -60.7819 | 0.17853 | -60.9558 | 60.3516 | -61.0245 | -60.9329 | -61.3312 | 0.15106 | -61.2488 | 60.3012 | 60.3516 | -60.7773 | -61.0199 | -0.032043 | 0.05951 | -0.14648 | 0.21057 | 0.036621 | -0.022889 | 0.17395 | 0.21515 | -0.027465 | -0.19684 | -0.33874 | -0.25635 | -0.22888 | -0.14648 | 121.344 | 121.6644 | 61.171 | -121.431 | 121.2936 | 121.344 | 61.1435 | -121.5179
399.7344 | 121.8018 | -60.965 | 60.434 | 0.0026703 | 0.0040139 | 0.066896 | -0.00024778 | 0.066475 | -0.0061267 | -0.00081594 | 0.0021363 | -0.0049111 | 0.064194 | 0.06761 | -0.19891 | -0.00048921 | 60.5713 | -60.8963 | 0.054932 | -61.0291 | 60.3195 | -61.0748 | -60.9512 | -61.4044 | 0.068665 | -61.3037 | 60.2875 | 60.3424 | -60.8047 | -61.0428 | -0.10986 | 0.013733 | -0.11444 | 0.068665 | -0.064087 | -0.07782 | 0.13733 | 0.16022 | -0.07782 | -0.14648 | -0.43945 | -0.33875 | -0.26093 | -0.091553 | 121.2845 | 121.5363 | 61.0199 | -121.3852 | 121.2524 | 121.3074 | 61.0336 | -121.4767
401.5 | 121.8018 | -60.9512 | 60.498 | -0.012589 | 0.0016641 | 0.064974 | 0.0016748 | 0.069252 | -0.0016405 | -0.0010297 | 0.0021363 | -0.0046975 | 0.064835 | 0.067823 | -0.20041 | -0.0036936 | 60.6903 | -60.7956 | 0.14191 | -60.9512 | 60.3333 | -61.0245 | -60.878 | -61.3129 | 0.14191 | -61.2259 | 60.3104 | 60.3699 | -60.7681 | -60.9604 | -0.073242 | 0.073242 | -0.16479 | 0.15564 | 0 | -0.073242 | 0.19226 | 0.18311 | -0.009155 | -0.18768 | -0.36163 | -0.27466 | -0.2655 | -0.12817 | 121.2845 | 121.6415 | 61.0931 | -121.376 | 121.2616 | 121.3211 | 61.0931 | -121.4584
403.2031 | 121.7514 | -61.0107 | 60.4385 | 0.0026703 | -0.0023947 | 0.066255 | -0.004093 | 0.068825 | -0.0014269 | 0.00067926 | 0.0021363 | -0.0027749 | 0.064194 | 0.066328 | -0.19635 | -0.0030526 | 60.6354 | -60.8688 | 0.07782 | -61.0107 | 60.2829 | -61.0977 | -60.965 | -61.3541 | 0.054932 | -61.2946 | 60.2509 | 60.3149 | -60.8459 | -61.0657 | -0.086975 | 0.045776 | -0.15564 | 0.14191 | 0 | -0.045776 | 0.19684 | 0.16479 | -0.054932 | -0.18768 | -0.34332 | -0.28381 | -0.22888 | -0.1236 | 121.2936 | 121.6461 | 61.0886 | -121.4035 | 121.2616 | 121.3257 | 61.0657 | -121.5042
404.9688 | 121.8018 | -61.0062 | 60.3882 | 0.0026703 | 0.0010233 | 0.065614 | -0.0019568 | 0.066689 | 0.0028455 | 0.0019611 | -0.013123 | -0.0014933 | 0.064621 | 0.069319 | -0.19442 | -0.0021982 | 60.5942 | -60.9467 | -0.009155 | -61.0657 | 60.3287 | -61.0931 | -60.9879 | -61.3724 | 0.022888 | -61.3541 | 60.3012 | 60.347 | -60.8551 | -61.0611 | -0.086975 | 0.018311 | -0.05951 | 0.05951 | -0.059509 | -0.07782 | 0.20599 | 0.15106 | -0.054931 | -0.086976 | -0.36621 | -0.3479 | -0.29297 | -0.041199 | 121.3348 | 121.6003 | 60.997 | -121.376 | 121.3074 | 121.3531 | 61.0291 | -121.4493
406.6562 | 121.6599 | -60.9741 | 60.5347 | -0.0049592 | 0.0046549 | 0.066896 | 0.0016748 | 0.068398 | -0.0031359 | 0.00025206 | -0.0054932 | -0.0040567 | 0.064835 | 0.064192 | -0.19742 | 0.00057899 | 60.704 | -60.7727 | 0.16479 | -60.9421 | 60.3607 | -60.9924 | -60.91 | -61.2946 | 0.14648 | -61.2259 | 60.347 | 60.4156 | -60.7498 | -60.9558 | -0.018311 | 0.064087 | -0.17395 | 0.20142 | 0.032043 | -0.032044 | 0.16937 | 0.2243 | 0.01831 | -0.18768 | -0.32044 | -0.25177 | -0.27008 | -0.11902 | 121.3348 | 121.6782 | 61.1389 | -121.4447 | 121.3211 | 121.3898 | 61.1206 | -121.4905
408.4219 | 121.6553 | -60.9833 | 60.5072 | -0.012589 | 0.0052957 | 0.066896 | 0.00060662 | 0.063271 | 0.0017773 | 0.0015339 | 0.0097658 | -0.0021341 | 0.06633 | 0.066542 | -0.19784 | -0.0015572 | 60.6445 | -60.8643 | 0.10071 | -60.9924 | 60.4019 | -61.0199 | -60.9467 | -61.3907 | 0.054932 | -61.3403 | 60.3745 | 60.4431 | -60.7864 | -61.0016 | -0.036621 | 0.036621 | -0.10529 | 0.11902 | -0.009156 | -0.045777 | 0.13733 | 0.19684 | -0.018311 | -0.13275 | -0.40741 | -0.35706 | -0.33874 | -0.064087 | 121.3852 | 121.6278 | 61.084 | -121.4539 | 121.3577 | 121.4264 | 61.0382 | -121.5088
410.125 | 121.6827 | -61.0062 | 60.5164 | -0.0049592 | 0.0027323 | 0.065614 | 0.0014612 | 0.067757 | -0.00035893 | 0.00067926 | -0.0054932 | -0.0034159 | 0.065689 | 0.06825 | -0.19912 | -0.0024118 | 60.6949 | -60.7681 | 0.16937 | -60.9375 | 60.3516 | -61.0107 | -60.8826 | -61.2854 | 0.13733 | -61.2534 | 60.3378 | 60.4156 | -60.7819 | -61.0016 | -0.004577 | 0.1236 | -0.16479 | 0.23804 | 0.068665 | -0.054932 | 0.17853 | 0.22431 | 0.004578 | -0.17853 | -0.27923 | -0.24719 | -0.25177 | -0.10071 | 121.3577 | 121.7011 | 61.1755 | -121.3989 | 121.344 | 121.4218 | 61.1435 | -121.5179
411.875 | 121.6736 | -61.0199 | 60.4568 | -0.0049592 | 0.0067911 | 0.061769 | 0.0027428 | 0.067116 | 0.0047681 | 0.0036701 | -0.013123 | 0.0010703 | 0.067398 | 0.071668 | -0.19613 | -0.0015572 | 60.5392 | -61.0199 | -0.022888 | -61.084 | 60.3745 | -61.1114 | -61.0016 | -61.4594 | -0.064087 | -61.4548 | 60.3287 | 60.3607 | -60.8551 | -61.0611 | -0.091553 | 0.01831 | -0.082397 | 0 | -0.064087 | -0.082397 | 0.082398 | 0.16479 | -0.041199 | -0.12817 | -0.43945 | -0.43488 | -0.39368 | -0.09613 | 121.3943 | 121.5591 | 60.997 | -121.4584 | 121.3486 | 121.3806 | 60.9558 | -121.5179
413.5781 | 121.6827 | -60.9879 | 60.4843 | -0.0049592 | 0.0091409 | 0.063692 | -3.4178e-05 | 0.065621 | 0.0036999 | 0.0045245 | 0.0097658 | 2.078e-06 | 0.065689 | 0.069532 | -0.19464 | -0.0030526 | 60.6445 | -60.8688 | 0.086975 | -60.9924 | 60.3882 | -61.0611 | -60.9375 | -61.322 | 0.073242 | -61.3266 | 60.3378 | 60.3973 | -60.8002 | -61.0245 | -0.073242 | 0.050354 | -0.09613 | 0.11902 | -0.004578 | -0.054932 | 0.16022 | 0.18768 | -0.036621 | -0.14648 | -0.33417 | -0.33875 | -0.30212 | -0.086975 | 121.376 | 121.6324 | 61.0748 | -121.4218 | 121.3257 | 121.3852 | 61.0611 | -121.5088
415.3438 | 121.6553 | -61.0611 | 60.4752 | 0.0026703 | 0.0035867 | 0.061983 | -0.0032386 | 0.066689 | 0.0032727 | 0.0013203 | -0.0054932 | 2.078e-06 | 0.065262 | 0.069746 | -0.19485 | -0.001771 | 60.6125 | -60.8963 | 0.041199 | -61.0153 | 60.3699 | -61.0565 | -60.9604 | -61.3953 | 0.009155 | -61.4044 | 60.3104 | 60.3928 | -60.8414 | -61.0382 | 0.004577 | 0.10071 | -0.10529 | 0.16479 | 0.045776 | -0.054932 | 0.13733 | 0.21973 | 0.022888 | -0.16479 | -0.33417 | -0.34332 | -0.36621 | -0.082398 | 121.431 | 121.6736 | 61.1023 | -121.4355 | 121.3715 | 121.4539 | 61.0703 | -121.5134
417.1094 | 121.6644 | -60.9787 | 60.5804 | -0.0049592 | 0.0040139 | 0.065614 | 0.0023156 | 0.067971 | -0.0035633 | 0.0021747 | -0.013123 | -0.0029885 | 0.064621 | 0.06761 | -0.19784 | -0.00070281 | 60.6583 | -60.8322 | 0.13733 | -60.9558 | 60.379 | -61.0245 | -60.9055 | -61.3541 | 0.073242 | -61.2991 | 60.3745 | 60.4568 | -60.7864 | -60.9695 | -0.045776 | 0.073242 | -0.20142 | 0.14648 | 0.022888 | -0.050354 | 0.07782 | 0.19226 | 0.009156 | -0.20599 | -0.37537 | -0.32043 | -0.32959 | -0.1236 | 121.3577 | 121.637 | 61.116 | -121.4859 | 121.3531 | 121.4355 | 61.0519 | -121.55
418.8594 | 121.7926 | -60.9924 | 60.3973 | -0.0049592 | 0.0074319 | 0.064974 | 0.00039302 | 0.067971 | 0.00092287 | 3.8456e-05 | -0.0054932 | 0.00042948 | 0.067398 | 0.071668 | -0.19742 | -0.00091641 | 60.5438 | -60.9924 | -0.018311 | -61.0886 | 60.3287 | -61.1298 | -60.9879 | -61.4319 | -0.032043 | -61.3907 | 60.2829 | 60.3836 | -60.8414 | -61.0519 | -0.13733 | 0.004578 | -0.068665 | 0 | -0.09613 | -0.10071 | 0.14648 | 0.15106 | -0.059509 | -0.11444 | -0.43945 | -0.39825 | -0.33875 | -0.013733 | 121.3211 | 121.5363 | 60.9741 | -121.3852 | 121.2753 | 121.376 | 60.9604 | -121.4493
420.5625 | 121.6644 | -60.9329 | 60.553 | -0.0049592 | -4.4874e-05 | 0.065187 | -0.0021704 | 0.067757 | -0.0024951 | 0.0013203 | -0.0054932 | -0.0034159 | 0.064621 | 0.067182 | -0.19934 | -0.0013436 | 60.6537 | -60.8414 | 0.086975 | -60.9604 | 60.4248 | -60.997 | -60.8826 | -61.3449 | 0.050354 | -61.2946 | 60.4156 | 60.4935 | -60.7407 | -60.9604 | -0.064087 | 0.050354 | -0.12817 | 0.091552 | -0.027466 | -0.07782 | 0.10071 | 0.19226 | -0.027466 | -0.13733 | -0.41199 | -0.36163 | -0.33417 | -0.05951 | 121.3577 | 121.5866 | 61.0199 | -121.4355 | 121.3486 | 121.4264 | 60.9833 | -121.5134
422.3125 | 121.6965 | -60.9833 | 60.5164 | -0.0049592 | 0.0042275 | 0.067964 | 0.0012476 | 0.06498 | -0.00078613 | 0.00067926 | 0.0021363 | -0.00085232 | 0.06398 | 0.067396 | -0.19742 | -0.00027561 | 60.6216 | -60.878 | 0.068665 | -60.9924 | 60.434 | -61.0199 | -60.9146 | -61.377 | 0.041199 | -61.3403 | 60.3882 | 60.4752 | -60.8002 | -61.0062 | -0.036621 | 0.068664 | -0.082397 | 0.10528 | -0.009156 | -0.07782 | 0.10529 | 0.1831 | -0.022889 | -0.12817 | -0.39368 | -0.35706 | -0.33417 | -0.041198 | 121.4172 | 121.6049 | 61.0519 | -121.431 | 121.3715 | 121.4584 | 61.0245 | -121.5225
424.0781 | 121.6599 | -61.0382 | 60.5026 | -0.0049592 | 0.0078591 | 0.063265 | 0.0018884 | 0.063271 | 0.0017773 | 0.00025206 | 0.0021363 | -0.00021152 | 0.067825 | 0.070387 | -0.19528 | -0.0021982 | 60.6537 | -60.8688 | 0.09613 | -60.997 | 60.3699 | -61.0519 | -60.9375 | -61.3632 | 0.059509 | -61.3449 | 60.3195 | 60.3973 | -60.8139 | -61.0474 | -0.013733 | 0.10071 | -0.13275 | 0.16937 | 0.041199 | -0.059509 | 0.15106 | 0.2243 | -0.009155 | -0.18311 | -0.32501 | -0.3067 | -0.29755 | -0.10529 | 121.4081 | 121.6919 | 61.1343 | -121.4401 | 121.3577 | 121.4355 | 61.0977 | -121.55
425.7656 | 121.8018 | -60.997 | 60.4385 | -0.012589 | -4.4874e-05 | 0.066042 | -0.0034522 | 0.063912 | 0.0015637 | 0.0043109 | -0.0054932 | -0.0021341 | 0.063553 | 0.06825 | -0.19635 | -0.00070281 | 60.5713 | -60.9512 | -0.032043 | -61.0611 | 60.3653 | -61.0931 | -60.9741 | -61.4273 | -0.041199 | -61.377 | 60.2966 | 60.4065 | -60.8276 | -61.0382 | -0.096131 | 0.022888 | -0.073243 | 0.045776 | -0.064087 | -0.086975 | 0.13275 | 0.16937 | -0.041199 | -0.14191 | -0.4303 | -0.37994 | -0.33875 | -0.032044 | 121.3623 | 121.5683 | 60.965 | -121.4127 | 121.2936 | 121.4035 | 60.9558 | -121.4767
427.4688 | 121.8246 | -60.9512 | 60.498 | 0.0026703 | 0.0023049 | 0.06711 | -3.4178e-05 | 0.068398 | -0.0054859 | 0.00067926 | -0.0054932 | -0.0066201 | 0.064194 | 0.06761 | -0.19891 | 0.0014334 | 60.64 | -60.8093 | 0.09613 | -60.9604 | 60.3653 | -61.0291 | -60.8917 | -61.322 | 0.10071 | -61.2167 | 60.3241 | 60.3973 | -60.7636 | -60.9833 | -0.07782 | 0.059509 | -0.13275 | 0.14191 | -0.009155 | -0.068664 | 0.14191 | 0.18768 | -0.032043 | -0.17395 | -0.37079 | -0.2655 | -0.23346 | -0.10071 | 121.3165 | 121.5912 | 61.0474 | -121.3898 | 121.2753 | 121.3486 | 61.0519 | -121.4813
429.25 | 121.7651 | -60.9787 | 60.4935 | -0.0049592 | 0.00016873 | 0.068819 | -0.0011024 | 0.067116 | -0.0039905 | -0.00017514 | 0.0021363 | -0.0049111 | 0.063339 | 0.065901 | -0.19784 | 0.00057899 | 60.6216 | -60.8597 | 0.045776 | -61.0016 | 60.3333 | -61.0428 | -60.9146 | -61.3678 | 0.009155 | -61.2991 | 60.2966 | 60.3973 | -60.8139 | -61.0199 | -0.064087 | 0.064087 | -0.16022 | 0.11902 | -0.022888 | -0.086975 | 0.12817 | 0.16479 | -0.041198 | -0.19684 | -0.3891 | -0.32043 | -0.27924 | -0.09613 | 121.312 | 121.6003 | 61.0245 | -121.4081 | 121.2753 | 121.376 | 60.9879 | -121.5134
430.9531 | 121.7102 | -60.9558 | 60.5164 | 0.0026703 | 0.0052957 | 0.066255 | -3.4178e-05 | 0.065407 | 6.8274e-05 | -0.0010297 | -0.0054932 | 0.00021568 | 0.065048 | 0.066328 | -0.19677 | -0.00091641 | 60.6308 | -60.8643 | 0.068665 | -60.9833 | 60.4568 | -61.0199 | -60.8826 | -61.3632 | 0.032043 | -61.322 | 60.3973 | 60.4431 | -60.7681 | -61.0016 | -0.064086 | 0.073243 | -0.059509 | 0.091553 | -0.027465 | -0.10071 | 0.11444 | 0.18768 | -0.045776 | -0.11902 | -0.40741 | -0.36621 | -0.32043 | -0.073242 | 121.4127 | 121.5866 | 61.0245 | -121.3989 | 121.3531 | 121.3989 | 60.9879 | -121.5179
432.6562 | 121.6736 | -61.0474 | 60.4889 | 0.0026703 | 0.0020913 | 0.063692 | 0.00039302 | 0.067971 | 0.0024183 | 0.0026019 | -0.013123 | 0.00021568 | 0.065689 | 0.0706 | -0.19635 | -0.0024118 | 60.5942 | -60.9283 | 0.027466 | -61.0428 | 60.3973 | -61.0474 | -60.9787 | -61.4044 | -0.050354 | -61.4182 | 60.3378 | 60.3928 | -60.8185 | -61.0565 | 0 | 0.068664 | -0.091553 | 0.11902 | 0.004577 | -0.064087 | 0.10529 | 0.22888 | -0.009156 | -0.15106 | -0.35706 | -0.37079 | -0.36163 | -0.096131 | 121.4447 | 121.6415 | 61.0748 | -121.4676 | 121.3852 | 121.4401 | 60.997 | -121.5454
434.4375 | 121.6827 | -60.9467 | 60.5896 | 0.0103 | 0.0052957 | 0.066469 | 0.0046656 | 0.066689 | -0.0033495 | 0.00067926 | -0.0054932 | -0.0053385 | 0.067398 | 0.067823 | -0.20041 | -0.0030526 | 60.6766 | -60.7636 | 0.17395 | -60.91 | 60.4019 | -61.0153 | -60.8597 | -61.3174 | 0.10071 | -61.2534 | 60.3836 | 60.4385 | -60.759 | -60.9604 | -0.068665 | 0.086975 | -0.18768 | 0.1831 | 0.036621 | -0.050354 | 0.086975 | 0.18768 | -0.013733 | -0.20599 | -0.37079 | -0.3067 | -0.29297 | -0.15106 | 121.3486 | 121.6232 | 61.1206 | -121.4493 | 121.3303 | 121.3852 | 61.0474 | -121.55
436.2031 | 121.6873 | -61.0245 | 60.498 | 0.0026703 | 0.0016641 | 0.064333 | -0.001316 | 0.065407 | 0.0054089 | 0.0017475 | -0.0054932 | -0.00063872 | 0.067825 | 0.068678 | -0.19571 | -0.001771 | 60.5484 | -60.9879 | -0.027466 | -61.0703 | 60.3973 | -61.0931 | -60.9924 | -61.4456 | -0.068665 | -61.4273 | 60.3287 | 60.3882 | -60.8505 | -61.0565 | -0.068665 | 0.032043 | -0.10071 | 0.036621 | -0.045776 | -0.077819 | 0.050354 | 0.17395 | -0.032044 | -0.16937 | -0.42114 | -0.40283 | -0.37079 | -0.10986 | 121.4218 | 121.5729 | 60.997 | -121.4905 | 121.3531 | 121.4127 | 60.9558 | -121.5546
437.8906 | 121.8063 | -60.9421 | 60.4843 | -0.0049592 | -0.0023947 | 0.068391 | -0.0011024 | 0.064766 | -0.0078357 | -0.00081594 | -0.0054932 | -0.0049111 | 0.064407 | 0.066328 | -0.19784 | -0.00027561 | 60.6445 | -60.8047 | 0.082397 | -60.9741 | 60.3424 | -61.0565 | -60.9055 | -61.3174 | 0.09613 | -61.2213 | 60.3058 | 60.3928 | -60.7636 | -61.0062 | -0.11444 | 0.036621 | -0.14191 | 0.13733 | -0.032043 | -0.068664 | 0.16022 | 0.17853 | -0.064087 | -0.17853 | -0.37537 | -0.27923 | -0.21515 | -0.091553 | 121.2845 | 121.5866 | 61.0245 | -121.3898 | 121.2479 | 121.3348 | 61.0382 | -121.4905
439.5938 | 121.8018 | -60.9421 | 60.498 | -0.0049592 | -0.0030357 | 0.067323 | 0.0023156 | 0.067543 | -0.0050585 | 0.00089286 | -0.0054932 | -0.0059793 | 0.06398 | 0.068037 | -0.19806 | -0.0026254 | 60.6125 | -60.8505 | 0.068665 | -60.9924 | 60.3516 | -61.0474 | -60.9283 | -61.3586 | 0.041199 | -61.2579 | 60.3195 | 60.3699 | -60.7819 | -60.9879 | -0.10528 | 0.013733 | -0.14648 | 0.091553 | -0.050354 | -0.064087 | 0.11444 | 0.16022 | -0.045776 | -0.17853 | -0.41656 | -0.31586 | -0.27008 | -0.12817 | 121.2936 | 121.5546 | 61.0107 | -121.4264 | 121.2616 | 121.312 | 60.9833 | -121.4859
441.3438 | 121.7834 | -61.0016 | 60.4385 | -0.0049592 | 0.0046549 | 0.064333 | -0.00024778 | 0.066902 | 0.0045545 | 0.0011067 | -0.0054932 | -0.0017069 | 0.065689 | 0.06825 | -0.19571 | -0.001771 | 60.5988 | -60.9558 | -0.027466 | -61.0565 | 60.3653 | -61.1069 | -60.9787 | -61.3998 | -0.050354 | -61.3724 | 60.2966 | 60.347 | -60.8459 | -61.0291 | -0.10529 | 0.022888 | -0.073243 | 0.045776 | -0.054932 | -0.07782 | 0.16022 | 0.15564 | -0.027466 | -0.14191 | -0.39825 | -0.37079 | -0.34332 | -0.091553 | 121.3669 | 121.6003 | 60.9741 | -121.4172 | 121.2982 | 121.3486 | 60.9512 | -121.4676
443.1094 | 121.7743 | -60.9375 | 60.5026 | 0.0026703 | -0.00025847 | 0.066255 | -0.0011024 | 0.068398 | -0.0027087 | 0.00046566 | 0.0021363 | -0.0055521 | 0.064194 | 0.06825 | -0.19827 | 0.00057899 | 60.6171 | -60.8414 | 0.050354 | -60.9787 | 60.3424 | -61.0107 | -60.8963 | -61.3632 | -0.009155 | -61.2854 | 60.3104 | 60.3699 | -60.7681 | -60.9833 | -0.073242 | 0.041199 | -0.16022 | 0.09613 | -0.041199 | -0.082398 | 0.11444 | 0.16937 | -0.045776 | -0.19226 | -0.42572 | -0.3479 | -0.30212 | -0.13275 | 121.2799 | 121.5546 | 60.9879 | -121.3989 | 121.2479 | 121.3074 | 60.9283 | -121.4859
444.8125 | 121.756 | -60.9283 | 60.5072 | -0.0049592 | 0.00038233 | 0.067751 | 0.0031702 | 0.068611 | -0.0012133 | -0.0010297 | -0.0054932 | -0.0053385 | 0.065048 | 0.066542 | -0.20041 | -0.00113 | 60.6537 | -60.8093 | 0.07782 | -60.9833 | 60.3287 | -61.0062 | -60.9238 | -61.3174 | 0.018311 | -61.2625 | 60.3195 | 60.3973 | -60.7636 | -60.997 | -0.07782 | 0.004578 | -0.17853 | 0.11902 | -0.054931 | -0.059509 | 0.14648 | 0.16479 | -0.068664 | -0.18768 | -0.3891 | -0.33417 | -0.2655 | -0.10986 | 121.257 | 121.582 | 61.0062 | -121.431 | 121.2479 | 121.3257 | 60.9467 | -121.5042
446.5781 | 121.8292 | -60.9146 | 60.5072 | 0.0103 | 0.00080973 | 0.066042 | 0.0027428 | 0.064553 | -0.0014269 | -0.0016705 | -0.013123 | -0.0042703 | 0.066116 | 0.06761 | -0.19763 | -0.001771 | 60.6903 | -60.7819 | 0.11444 | -60.9375 | 60.3973 | -60.9879 | -60.8597 | -61.2854 | 0.086975 | -61.203 | 60.3333 | 60.4202 | -60.7407 | -60.9467 | -0.073242 | 0.054932 | -0.10986 | 0.13275 | -0.022888 | -0.07782 | 0.18311 | 0.17395 | -0.032043 | -0.17395 | -0.37079 | -0.28839 | -0.25635 | -0.086975 | 121.312 | 121.6049 | 61.0291 | -121.3669 | 121.2479 | 121.3348 | 61.0016 | -121.4539
448.3438 | 121.7056 | -60.9558 | 60.5438 | 0.0103 | 0.0012369 | 0.066896 | 0.00017942 | 0.067116 | 0.0024183 | -0.00017514 | 0.0021363 | -0.0014933 | 0.066757 | 0.068891 | -0.19592 | -0.0024118 | 60.6537 | -60.8597 | 0.073242 | -60.9604 | 60.4523 | -60.997 | -60.8688 | -61.3266 | 0.013733 | -61.3312 | 60.4065 | 60.4568 | -60.7636 | -60.9879 | -0.041198 | 0.086976 | -0.091552 | 0.096131 | -0.004577 | -0.091553 | 0.10986 | 0.19226 | -0.032043 | -0.13733 | -0.37079 | -0.37537 | -0.34332 | -0.086975 | 121.4081 | 121.6095 | 61.0291 | -121.4127 | 121.3623 | 121.4127 | 60.9695 | -121.5317
450.1094 | 121.788 | -60.8734 | 60.5804 | -0.0049592 | -0.0017539 | 0.065614 | -0.00067498 | 0.065407 | -0.0046313 | -0.00060234 | 0.0021363 | -0.0046975 | 0.063553 | 0.066969 | -0.20062 | 0.00015159 | 60.7544 | -60.704 | 0.16479 | -60.8688 | 60.4385 | -60.9467 | -60.8276 | -61.2122 | 0.14191 | -61.1343 | 60.3745 | 60.4477 | -60.7132 | -60.9192 | -0.073242 | 0.045776 | -0.14191 | 0.16937 | 0.004578 | -0.041198 | 0.17395 | 0.16022 | -0.045776 | -0.20599 | -0.33875 | -0.26093 | -0.21515 | -0.13275 | 121.312 | 121.6278 | 61.0382 | -121.4081 | 121.2479 | 121.3211 | 61.0153 | -121.4996
451.8594 | 121.8201 | -60.8505 | 60.5988 | 0.0026703 | 0.00016873 | 0.066683 | 0.00082022 | 0.067757 | -0.0033495 | 0.0013203 | -0.0054932 | -0.0040567 | 0.063553 | 0.065687 | -0.19955 | -0.0013436 | 60.759 | -60.7224 | 0.11902 | -60.8643 | 60.4477 | -60.9329 | -60.8139 | -61.2076 | 0.07782 | -61.1298 | 60.4111 | 60.4752 | -60.6812 | -60.8917 | -0.082397 | 0.036621 | -0.15106 | 0.12817 | -0.013733 | -0.050354 | 0.16022 | 0.16937 | -0.041199 | -0.18768 | -0.35706 | -0.27924 | -0.23804 | -0.1236 | 121.2982 | 121.6095 | 60.9695 | -121.4127 | 121.2616 | 121.3257 | 60.9283 | -121.4905
453.5625 | 121.8018 | -60.7956 | 60.6079 | 0.0026703 | -0.0032493 | 0.065828 | -0.00067498 | 0.066048 | -0.0033495 | -0.0023113 | 0.0021363 | -0.0044839 | 0.061417 | 0.064405 | -0.19784 | -0.0019846 | 60.759 | -60.7224 | 0.082397 | -60.8688 | 60.5026 | -60.9192 | -60.8002 | -61.203 | 0.036621 | -61.1572 | 60.4248 | 60.4935 | -60.6491 | -60.8688 | -0.1236 | -0.004578 | -0.10528 | 0.073242 | -0.073242 | -0.068664 | 0.15106 | 0.14648 | -0.073242 | -0.1831 | -0.40741 | -0.36163 | -0.28839 | -0.11444 | 121.2982 | 121.5546 | 60.878 | -121.4081 | 121.2204 | 121.2891 | 60.8322 | -121.4767
455.3125 | 121.8109 | -60.7498 | 60.6949 | -0.0049592 | -4.4874e-05 | 0.067323 | 0.002102 | 0.066689 | -0.0014269 | -0.0012433 | 0.0021363 | -0.0032021 | 0.06398 | 0.064833 | -0.19699 | -0.0021982 | 60.8551 | -60.6216 | 0.11902 | -60.759 | 60.5484 | -60.8322 | -60.7224 | -61.0931 | 0.091553 | -61.0519 | 60.5072 | 60.5621 | -60.585 | -60.791 | -0.082397 | 0.027466 | -0.14648 | 0.12817 | -0.009155 | -0.036621 | 0.16022 | 0.16479 | -0.041199 | -0.18768 | -0.34332 | -0.30212 | -0.26093 | -0.13275 | 121.2982 | 121.6049 | 60.8688 | -121.4172 | 121.257 | 121.312 | 60.8414 | -121.4859
457.0625 | 121.7926 | -60.6583 | 60.7681 | -0.0049592 | -4.4874e-05 | 0.066042 | 0.00039302 | 0.066902 | -0.0014269 | -0.00017514 | -0.013123 | -0.0027749 | 0.064194 | 0.066114 | -0.19763 | -0.0049752 | 60.9879 | -60.4889 | 0.15106 | -60.6537 | 60.6537 | -60.7361 | -60.6033 | -60.9879 | 0.11444 | -60.9283 | 60.5988 | 60.6812 | -60.4614 | -60.6812 | -0.07782 | 0.054931 | -0.11444 | 0.16937 | 0.004577 | -0.050354 | 0.21973 | 0.19684 | -0.022888 | -0.16937 | -0.32959 | -0.27008 | -0.24719 | -0.086975 | 121.312 | 121.6461 | 60.8093 | -121.3715 | 121.257 | 121.3394 | 60.7727 | -121.4493
458.75 | 121.6644 | -60.6079 | 60.8826 | -0.0049592 | 0.0052957 | 0.065401 | 0.002102 | 0.067543 | 0.0011365 | 0.00089286 | 0.0021363 | -0.0017069 | 0.068893 | 0.067396 | -0.19827 | -0.0024118 | 60.997 | -60.5118 | 0.12817 | -60.6537 | 60.7452 | -60.6903 | -60.5713 | -61.0107 | 0.050354 | -60.9924 | 60.7498 | 60.791 | -60.4385 | -60.6445 | -0.082398 | 0.036621 | -0.13733 | 0.09613 | -0.045777 | -0.082398 | 0.11444 | 0.16937 | -0.036621 | -0.13275 | -0.40283 | -0.38452 | -0.3479 | -0.091552 | 121.3531 | 121.6049 | 60.7361 | -121.4539 | 121.3577 | 121.3989 | 60.6583 | -121.5271
460.5 | 121.6736 | -60.6125 | 60.8826 | -0.012589 | 0.0046549 | 0.066255 | 0.0018884 | 0.06733 | 0.0017773 | 0.00025206 | -0.0054932 | -0.0012795 | 0.065689 | 0.067823 | -0.19677 | -0.0030526 | 60.9879 | -60.5026 | 0.09613 | -60.6491 | 60.7956 | -60.6766 | -60.5164 | -60.9924 | 0.032043 | -60.9787 | 60.7727 | 60.8093 | -60.4248 | -60.6033 | -0.064087 | 0.096131 | -0.086975 | 0.10986 | -0.036621 | -0.13275 | 0.10529 | 0.18768 | 0.009155 | -0.10986 | -0.37994 | -0.36621 | -0.37537 | -0.073242 | 121.4081 | 121.6003 | 60.7086 | -121.3989 | 121.3852 | 121.4218 | 60.6445 | -121.4859
462.2656 | 121.6736 | -60.5667 | 60.9787 | -0.012589 | 0.0010233 | 0.067964 | 0.002102 | 0.06498 | 0.0011365 | 0.0021747 | -0.0054932 | -0.0012795 | 0.06633 | 0.065901 | -0.19763 | -0.0013436 | 61.0291 | -60.4477 | 0.091553 | -60.5804 | 60.8414 | -60.5988 | -60.4889 | -60.9375 | 0.041199 | -60.9055 | 60.8231 | 60.8505 | -60.3607 | -60.5621 | -0.032044 | 0.077819 | -0.13733 | 0.11902 | -0.013733 | -0.091552 | 0.050354 | 0.20599 | 0.004577 | -0.15564 | -0.37079 | -0.33875 | -0.34332 | -0.12817 | 121.4081 | 121.5958 | 60.6583 | -121.4676 | 121.3898 | 121.4172 | 60.6079 | -121.5408
464.0156 | 121.6644 | -60.5438 | 60.9787 | -0.0049592 | 0.0023049 | 0.06711 | 0.0012476 | 0.068398 | 0.0017773 | 0.00089286 | 0.0021363 | -0.0034159 | 0.06633 | 0.06761 | -0.19806 | -0.0030526 | 61.0611 | -60.3836 | 0.13275 | -60.5347 | 60.8597 | -60.585 | -60.4523 | -60.9146 | 0.050354 | -60.878 | 60.8139 | 60.8734 | -60.3287 | -60.5667 | -0.041199 | 0.091552 | -0.11902 | 0.16022 | 0.009155 | -0.082397 | 0.082397 | 0.21515 | -0.022888 | -0.16479 | -0.37079 | -0.33417 | -0.31128 | -0.10529 | 121.4035 | 121.6049 | 60.6766 | -121.431 | 121.3577 | 121.4172 | 60.5942 | -121.5454
465.7031 | 121.6736 | -60.553 | 60.9238 | 0.0026703 | 0.0023049 | 0.064546 | -0.0015296 | 0.066262 | 0.0022047 | 0.0028155 | 0.0021363 | -0.00042512 | 0.066116 | 0.069532 | -0.19613 | -0.0032662 | 61.0107 | -60.498 | -0.032043 | -60.5988 | 60.8643 | -60.6033 | -60.4843 | -60.9467 | -0.068665 | -60.9375 | 60.7819 | 60.8459 | -60.379 | -60.5713 | -0.050354 | 0.068665 | -0.059509 | 0.054932 | -0.045776 | -0.11444 | 0.086975 | 0.17395 | -0.01831 | -0.14191 | -0.39368 | -0.38452 | -0.36621 | -0.07782 | 121.4172 | 121.5637 | 60.5209 | -121.4081 | 121.3348 | 121.3989 | 60.4843 | -121.4951
467.4531 | 121.6782 | -60.5164 | 61.0062 | -0.0049592 | 0.0014505 | 0.064546 | 0.002102 | 0.066262 | 0.0024183 | 0.0040973 | 0.0097658 | 0.0012839 | 0.066116 | 0.066969 | -0.19742 | -0.00027561 | 61.0611 | -60.4523 | -0.009155 | -60.5347 | 60.9238 | -60.5621 | -60.4523 | -60.9055 | -0.09613 | -60.9146 | 60.8231 | 60.8826 | -60.3195 | -60.5347 | -0.045777 | 0.064086 | -0.082398 | 0.064086 | -0.018311 | -0.082397 | 0.054931 | 0.19684 | -0.018311 | -0.18311 | -0.3891 | -0.39825 | -0.37994 | -0.1236 | 121.4401 | 121.5775 | 60.5072 | -121.4584 | 121.3394 | 121.3989 | 60.4202 | -121.5408
469.2031 | 121.7056 | -60.4202 | 61.084 | -0.0049592 | 0.0063639 | 0.066469 | 0.003811 | 0.068611 | -0.0012133 | 0.0013203 | -0.0054932 | -0.0017069 | 0.065689 | 0.070173 | -0.19891 | -6.2012e-05 | 61.1664 | -60.3012 | 0.073242 | -60.4431 | 60.9924 | -60.4889 | -60.379 | -60.8139 | 0.013733 | -60.7727 | 60.9512 | 61.0062 | -60.2142 | -60.4248 | -0.068665 | 0.041199 | -0.091552 | 0.11902 | -0.022888 | -0.064087 | 0.082398 | 0.20599 | -0.004578 | -0.13275 | -0.39368 | -0.35248 | -0.3479 | -0.077819 | 121.4127 | 121.5866 | 60.4935 | -121.463 | 121.3715 | 121.4264 | 60.434 | -121.5088
470.9062 | 121.8018 | -60.4019 | 61.0382 | -0.0049592 | 0.00016873 | 0.06946 | 0.0023156 | 0.068398 | -0.0069811 | 0.00089286 | 0.0021363 | -0.0038431 | 0.065689 | 0.067396 | -0.19955 | -0.00048921 | 61.1389 | -60.2966 | 0.082397 | -60.4385 | 60.8871 | -60.5118 | -60.3653 | -60.7956 | 0.073242 | -60.7086 | 60.8643 | 60.8963 | -60.2325 | -60.4431 | -0.10986 | 0.036622 | -0.15106 | 0.10529 | -0.036621 | -0.073243 | 0.10071 | 0.16937 | -0.041198 | -0.17395 | -0.39368 | -0.3067 | -0.2655 | -0.14191 | 121.2891 | 121.5408 | 60.4843 | -121.4035 | 121.2662 | 121.2982 | 60.4752 | -121.4813
472.6719 | 121.7239 | -60.6766 | 60.7544 | -0.0049592 | 0.0020913 | 0.063478 | -0.0011024 | 0.064125 | 0.0024183 | -0.00038874 | 0.0021363 | 0.0010703 | 0.063766 | 0.068891 | -0.19784 | -0.0036936 | 60.9009 | -60.6308 | -0.009155 | -60.7315 | 60.6903 | -60.759 | -60.6262 | -61.0977 | -0.050354 | -61.0611 | 60.6628 | 60.7269 | -60.4935 | -60.7498 | -0.082397 | 0.050354 | -0.064087 | 0.045777 | -0.054931 | -0.10529 | 0.14648 | 0.18311 | -0.073242 | -0.091553 | -0.42114 | -0.38452 | -0.31128 | -0.027466 | 121.3669 | 121.5775 | 60.6674 | -121.3806 | 121.3394 | 121.4035 | 60.6262 | -121.5042
474.4219 | 121.669 | -60.672 | 60.8093 | -0.0049592 | 0.0050821 | 0.063051 | -0.00024778 | 0.068398 | 0.0049817 | 0.0028155 | -0.0054932 | 2.078e-06 | 0.06398 | 0.071028 | -0.19485 | -0.00070281 | 60.9238 | -60.6033 | -0.018311 | -60.704 | 60.7269 | -60.7269 | -60.6033 | -61.084 | -0.09613 | -61.0703 | 60.6857 | 60.7498 | -60.4797 | -60.6949 | -0.054932 | 0.068664 | -0.082397 | 0.068664 | -0.032044 | -0.10071 | 0.11444 | 0.19226 | -0.022888 | -0.1236 | -0.41199 | -0.39825 | -0.37537 | -0.059509 | 121.3989 | 121.5958 | 60.6537 | -121.4127 | 121.3577 | 121.4218 | 60.5759 | -121.5042
476.125 | 121.701 | -60.5896 | 60.8963 | -0.0049592 | 0.0044411 | 0.064974 | -0.0017432 | 0.066902 | -0.0018543 | 0.00089286 | -0.0054932 | -0.0027749 | 0.065903 | 0.068037 | -0.19699 | -0.0019846 | 60.9787 | -60.4889 | 0.082397 | -60.6079 | 60.7819 | -60.6674 | -60.5347 | -60.997 | 0.022888 | -60.9421 | 60.7544 | 60.8139 | -60.4156 | -60.6171 | -0.077819 | 0.054932 | -0.11444 | 0.10071 | -0.01831 | -0.073242 | 0.082398 | 0.17395 | -0.027465 | -0.14191 | -0.40741 | -0.35248 | -0.32501 | -0.082397 | 121.3715 | 121.5683 | 60.672 | -121.431 | 121.344 | 121.4035 | 60.6125 | -121.5134
477.8281 | 121.6461 | -60.5759 | 60.9146 | -0.012589 | 0.0038003 | 0.06476 | 0.0029566 | 0.068184 | 0.0039135 | 0.0023883 | -0.013123 | 0.00064308 | 0.064835 | 0.068037 | -0.19806 | -0.0013436 | 61.0657 | -60.4431 | 0.064087 | -60.585 | 60.8093 | -60.6125 | -60.5072 | -60.9375 | -0.018311 | -60.9375 | 60.7864 | 60.8185 | -60.3561 | -60.5804 | -0.036621 | 0.068665 | -0.10529 | 0.13275 | -0.009155 | -0.07782 | 0.15106 | 0.21973 | -0.004577 | -0.12817 | -0.36163 | -0.36163 | -0.35706 | -0.096131 | 121.3852 | 121.6415 | 60.64 | -121.4218 | 121.3623 | 121.3943 | 60.5576 | -121.4951
479.5938 | 121.7514 | -60.3516 | 61.0794 | -0.0049592 | -0.0011131 | 0.066683 | 0.00060662 | 0.067116 | -0.0056995 | 0.0015339 | 0.0021363 | -0.0049111 | 0.062698 | 0.066542 | -0.20083 | 0.0018606 | 61.171 | -60.2554 | 0.050354 | -60.4111 | 60.9375 | -60.4202 | -60.3195 | -60.7727 | -0.018311 | -60.7086 | 60.8963 | 60.9741 | -60.2005 | -60.4202 | -0.068665 | 0.032043 | -0.14191 | 0.09613 | -0.05951 | -0.091553 | 0.091552 | 0.15106 | -0.068665 | -0.18311 | -0.42114 | -0.35706 | -0.28839 | -0.10529 | 121.2891 | 121.5225 | 60.4019 | -121.3989 | 121.2479 | 121.3257 | 60.3333 | -121.4996
481.3594 | 121.7102 | -60.2966 | 61.1755 | -0.0049592 | 0.0040139 | 0.066255 | 0.0033838 | 0.067757 | 0.0017773 | -0.00060234 | -0.0054932 | -0.0021341 | 0.06633 | 0.067182 | -0.19827 | -0.0024118 | 61.2854 | -60.2097 | 0.086975 | -60.3104 | 61.1069 | -60.3561 | -60.228 | -60.672 | 0.036621 | -60.6445 | 61.0611 | 61.1435 | -60.1364 | -60.3195 | -0.059509 | 0.068665 | -0.068664 | 0.086975 | -0.013733 | -0.082398 | 0.10986 | 0.16022 | -0.022888 | -0.11444 | -0.37537 | -0.3479 | -0.32501 | -0.032043 | 121.4035 | 121.582 | 60.3836 | -121.4035 | 121.3577 | 121.4401 | 60.3333 | -121.4951
483.0625 | 121.8063 | -60.26 | 61.1572 | -0.0049592 | 0.0018777 | 0.066469 | 0.0018884 | 0.065621 | -0.0071947 | -0.00017514 | -0.0054932 | -0.0034159 | 0.063339 | 0.065687 | -0.20083 | 0.00057899 | 61.2579 | -60.1868 | 0.082397 | -60.3241 | 61.0199 | -60.3607 | -60.2463 | -60.6903 | 0.022888 | -60.5988 | 60.9924 | 61.0611 | -60.0677 | -60.3012 | -0.10071 | 0.013733 | -0.13733 | 0.073242 | -0.064087 | -0.07782 | 0.10071 | 0.19226 | -0.041198 | -0.16479 | -0.4303 | -0.33874 | -0.29755 | -0.096131 | 121.2799 | 121.5179 | 60.3424 | -121.4035 | 121.2524 | 121.3211 | 60.2829 | -121.4584
484.8125 | 121.6507 | -60.4889 | 61.0245 | -0.012589 | 0.0050821 | 0.064546 | 0.0018884 | 0.065193 | -0.0014269 | 3.8456e-05 | -0.0054932 | -0.0038431 | 0.065903 | 0.068891 | -0.19934 | -0.0024118 | 61.1252 | -60.3378 | 0.14648 | -60.4935 | 60.8368 | -60.5667 | -60.4156 | -60.8871 | 0.032043 | -60.8322 | 60.8322 | 60.9055 | -60.3287 | -60.498 | -0.077819 | 0.073243 | -0.18768 | 0.15106 | -0.004577 | -0.07782 | 0.10071 | 0.16022 | -0.009155 | -0.19226 | -0.39825 | -0.34332 | -0.33417 | -0.11902 | 121.3257 | 121.6141 | 60.6354 | -121.4401 | 121.3211 | 121.3943 | 60.5209 | -121.5225
486.5 | 121.6599 | -60.5621 | 60.9787 | -0.0049592 | 0.0044411 | 0.064333 | 0.00082022 | 0.064553 | 0.0047681 | 0.00046566 | -0.0054932 | 0.00064308 | 0.067398 | 0.06825 | -0.19827 | -0.0015572 | 61.116 | -60.3745 | 0.09613 | -60.5301 | 60.8505 | -60.553 | -60.4752 | -60.8688 | -0.004578 | -60.8734 | 60.8047 | 60.878 | -60.3516 | -60.5621 | 0.009155 | 0.086975 | -0.12817 | 0.18768 | 0.032044 | -0.054931 | 0.13733 | 0.21057 | 0 | -0.17395 | -0.3067 | -0.31128 | -0.31128 | -0.10071 | 121.4127 | 121.6782 | 60.6583 | -121.4539 | 121.3669 | 121.4401 | 60.5576 | -121.5408
488.25 | 121.6736 | -60.5392 | 60.9421 | -0.0049592 | 0.0042275 | 0.063905 | 0.001034 | 0.06498 | 0.0024183 | 0.0023883 | -0.0054932 | -0.00042512 | 0.066116 | 0.068464 | -0.19528 | -0.0013436 | 60.9924 | -60.5072 | -0.027466 | -60.5988 | 60.8551 | -60.5942 | -60.4935 | -60.9512 | -0.091553 | -60.9512 | 60.8047 | 60.8597 | -60.3882 | -60.5759 | -0.054931 | 0.045777 | -0.086975 | 0.032044 | -0.059509 | -0.10529 | 0.050354 | 0.15106 | -0.036621 | -0.13733 | -0.41199 | -0.41199 | -0.37537 | -0.082398 | 121.3943 | 121.5317 | 60.5118 | -121.4355 | 121.344 | 121.3989 | 60.4477 | -121.5179
490.0156 | 121.7285 | -60.5026 | 60.9421 | -0.0049592 | 0.0025185 | 0.063478 | 0.002102 | 0.065407 | -0.0052721 | 0.00025206 | 0.0021363 | -0.0049111 | 0.064621 | 0.066542 | -0.20147 | -0.00091641 | 61.1023 | -60.3333 | 0.10986 | -60.5072 | 60.8002 | -60.5713 | -60.4431 | -60.8688 | -0.013733 | -60.8139 | 60.7407 | 60.8414 | -60.3195 | -60.5118 | -0.068664 | 0.05951 | -0.14191 | 0.16937 | -0.004577 | -0.064087 | 0.16022 | 0.18311 | -0.009155 | -0.20142 | -0.36621 | -0.31128 | -0.30212 | -0.10071 | 121.3028 | 121.6049 | 60.6125 | -121.3852 | 121.2433 | 121.344 | 60.4889 | -121.4539
491.7188 | 121.701 | -60.4477 | 61.0748 | 0.0026703 | 0.0061501 | 0.065187 | 0.0044518 | 0.066689 | -0.0020679 | 0.00067926 | 0.0021363 | -0.0021341 | 0.068893 | 0.067823 | -0.19827 | -0.0034798 | 61.1298 | -60.3333 | 0.10529 | -60.4797 | 60.965 | -60.4935 | -60.3928 | -60.8597 | 0 | -60.8002 | 60.9375 | 60.9924 | -60.2646 | -60.4568 | -0.045776 | 0.054932 | -0.10986 | 0.11444 | -0.032043 | -0.086975 | 0.054932 | 0.18311 | -0.009155 | -0.13733 | -0.41199 | -0.35248 | -0.34332 | -0.082397 | 121.4127 | 121.5775 | 60.553 | -121.4676 | 121.3852 | 121.4401 | 60.4477 | -121.5317
493.4688 | 121.6782 | -60.4477 | 61.0382 | -0.0049592 | 0.0050821 | 0.06711 | 0.0027428 | 0.065834 | -0.00078613 | -0.00038874 | -0.0054932 | -0.0025613 | 0.065262 | 0.066755 | -0.19742 | 0.00015159 | 61.1023 | -60.3561 | 0.10071 | -60.4843 | 60.9375 | -60.4843 | -60.3745 | -60.878 | 0 | -60.8093 | 60.9055 | 60.9695 | -60.2692 | -60.4797 | -0.036621 | 0.073242 | -0.10071 | 0.091553 | -0.036621 | -0.10986 | 0.064087 | 0.17853 | -0.032043 | -0.13275 | -0.4303 | -0.36163 | -0.32959 | -0.068665 | 121.3852 | 121.55 | 60.5484 | -121.4127 | 121.3531 | 121.4172 | 60.4477 | -121.5179
495.25 | 121.7834 | -60.4202 | 61.0016 | -0.0049592 | 0.0012369 | 0.066683 | 0.00017942 | 0.066475 | -0.0050585 | 0.00025206 | -0.0054932 | -0.0049111 | 0.064835 | 0.06825 | -0.20083 | -0.0024118 | 61.0931 | -60.347 | 0.073242 | -60.4889 | 60.8459 | -60.5209 | -60.4111 | -60.8459 | -0.013733 | -60.7727 | 60.8093 | 60.9009 | -60.2554 | -60.4889 | -0.10071 | 0.009155 | -0.15564 | 0.073242 | -0.068665 | -0.07782 | 0.091553 | 0.16479 | -0.068665 | -0.19226 | -0.42572 | -0.35248 | -0.28381 | -0.10071 | 121.2662 | 121.5134 | 60.4935 | -121.4127 | 121.2296 | 121.3211 | 60.4065 | -121.4905
497.0156 | 121.6553 | -60.4294 | 61.0474 | -0.0049592 | 0.00016873 | 0.067751 | -0.00088858 | 0.065621 | -0.0016405 | 0.0011067 | 0.0021363 | -0.0038431 | 0.063553 | 0.067182 | -0.19806 | -0.0030526 | 61.1893 | -60.2463 | 0.1831 | -60.4202 | 60.9055 | -60.4614 | -60.3561 | -60.8139 | 0.054932 | -60.7544 | 60.8917 | 60.9238 | -60.2417 | -60.4614 | -0.032044 | 0.073242 | -0.14191 | 0.1831 | 0.009155 | -0.064087 | 0.14191 | 0.18768 | -0.032044 | -0.15564 | -0.38452 | -0.32501 | -0.29297 | -0.1236 | 121.3348 | 121.6187 | 60.6125 | -121.4035 | 121.3211 | 121.3531 | 60.4843 | -121.5088
498.7031 | 121.6599 | -60.4477 | 61.0474 | -0.0049592 | 0.0042275 | 0.063265 | 0.00039302 | 0.066902 | 0.0034863 | 0.0013203 | -0.0054932 | 0.00085668 | 0.064407 | 0.06825 | -0.19507 | -0.00070281 | 61.116 | -60.4156 | -0.027466 | -60.5072 | 60.9375 | -60.5209 | -60.4202 | -60.8597 | -0.10529 | -60.8734 | 60.878 | 60.9375 | -60.2692 | -60.4889 | -0.073242 | 0.027466 | -0.10986 | 0.032044 | -0.059509 | -0.086975 | 0.068665 | 0.17853 | -0.041199 | -0.16937 | -0.41199 | -0.42572 | -0.38452 | -0.10986 | 121.3852 | 121.5637 | 60.4202 | -121.4676 | 121.3257 | 121.3852 | 60.3424 | -121.5363
500.4531 | 121.7377 | -60.4065 | 61.0336 | 0.0026703 | 0.0042275 | 0.064974 | -0.0021704 | 0.066475 | 0.0017773 | 0.0017475 | -0.0054932 | -0.0012795 | 0.063339 | 0.067396 | -0.19571 | -0.00070281 | 61.1114 | -60.3561 | -0.027466 | -60.4752 | 60.9512 | -60.498 | -60.3928 | -60.8276 | -0.10986 | -60.8139 | 60.9192 | 60.9604 | -60.2509 | -60.4568 | -0.091553 | 0.013733 | -0.082397 | 0.050354 | -0.068665 | -0.082398 | 0.07782 | 0.15564 | -0.050354 | -0.11444 | -0.42114 | -0.40741 | -0.35706 | -0.073242 | 121.3577 | 121.5179 | 60.379 | -121.4264 | 121.3257 | 121.3669 | 60.2966 | -121.4905
502.2188 | 121.8109 | -60.3607 | 61.0611 | 0.0026703 | 0.0027323 | 0.064974 | 0.00039302 | 0.064766 | -0.0056995 | -0.00017514 | 0.0021363 | -0.0057657 | 0.062912 | 0.066328 | -0.20062 | -0.00070281 | 61.2076 | -60.228 | 0.1236 | -60.3836 | 60.9375 | -60.4614 | -60.3287 | -60.7361 | 0.045776 | -60.6491 | 60.8688 | 60.9879 | -60.1822 | -60.379 | -0.10071 | 0.032044 | -0.1236 | 0.13275 | -0.022888 | -0.054932 | 0.14648 | 0.17853 | -0.01831 | -0.19226 | -0.37537 | -0.28839 | -0.27008 | -0.073242 | 121.2982 | 121.5683 | 60.4843 | -121.3898 | 121.2296 | 121.3486 | 60.4065 | -121.4401
503.9219 | 121.7194 | -60.3928 | 61.0565 | 0.0026703 | 0.0040139 | 0.065187 | 0.0044518 | 0.067543 | -0.0035633 | -0.0033795 | -0.0054932 | -0.0017069 | 0.066544 | 0.067823 | -0.19912 | -0.0026254 | 61.235 | -60.1913 | 0.21057 | -60.3745 | 60.91 | -60.4477 | -60.3378 | -60.7315 | 0.09613 | -60.6628 | 60.878 | 60.9604 | -60.2142 | -60.4019 | -0.054932 | 0.054931 | -0.14648 | 0.20142 | 0.01831 | -0.036621 | 0.17853 | 0.17853 | -0.009156 | -0.17853 | -0.33875 | -0.27008 | -0.26093 | -0.096131 | 121.3028 | 121.6278 | 60.6033 | -121.3943 | 121.2708 | 121.3531 | 60.4889 | -121.4584
505.6875 | 121.7377 | -60.3653 | 61.0611 | 0.0026703 | -0.0036765 | 0.065187 | -0.00024778 | 0.066475 | 0.00049567 | 0.0015339 | -0.0054932 | -0.0036295 | 0.06398 | 0.06761 | -0.19891 | -0.0047616 | 61.2305 | -60.2325 | 0.091553 | -60.4111 | 60.878 | -60.4477 | -60.3424 | -60.7544 | -0.032043 | -60.7086 | 60.8505 | 60.9467 | -60.2005 | -60.3973 | -0.082398 | 0.022888 | -0.1831 | 0.13275 | -0.045777 | -0.068665 | 0.16937 | 0.1648 | -0.032044 | -0.21057 | -0.3891 | -0.34332 | -0.31128 | -0.11444 | 121.2433 | 121.5958 | 60.4568 | -121.4035 | 121.2158 | 121.3119 | 60.3333 | -121.4584
507.4531 | 121.7606 | -60.3745 | 61.0519 | 0.0026703 | 0.00059593 | 0.06711 | -0.0015296 | 0.064125 | -0.0014269 | -0.00060234 | -0.020752 | -0.0042703 | 0.065262 | 0.065687 | -0.19891 | -0.00070281 | 61.2534 | -60.1822 | 0.20599 | -60.3607 | 60.9192 | -60.4614 | -60.3287 | -60.704 | 0.10071 | -60.6537 | 60.8734 | 60.9467 | -60.1776 | -60.4111 | -0.086975 | 0.045777 | -0.13275 | 0.19226 | 0.013733 | -0.032044 | 0.20142 | 0.19684 | -0.036621 | -0.17853 | -0.32959 | -0.27924 | -0.24262 | -0.10529 | 121.2936 | 121.6278 | 60.5804 | -121.3806 | 121.2479 | 121.3211 | 60.4752 | -121.463
509.1719 | 121.669 | -60.3882 | 61.0931 | -0.012589 | 0.0010233 | 0.064333 | 0.00039302 | 0.065834 | -0.0018543 | 0.0017475 | -0.0054932 | -0.0034159 | 0.063766 | 0.067396 | -0.19784 | -0.004548 | 61.2579 | -60.1822 | 0.19226 | -60.3745 | 60.9467 | -60.4294 | -60.3241 | -60.7269 | 0.068665 | -60.6628 | 60.9192 | 61.0107 | -60.2051 | -60.4065 | -0.041198 | 0.064087 | -0.14648 | 0.20599 | 0.013733 | -0.050354 | 0.1648 | 0.18311 | -0.01831 | -0.17395 | -0.33874 | -0.27466 | -0.25635 | -0.082398 | 121.3348 | 121.6461 | 60.5804 | -121.4172 | 121.3074 | 121.3989 | 60.4568 | -121.4996
510.9375 | 121.7239 | -60.3882 | 61.0291 | 0.0026703 | -0.0013267 | 0.066896 | -0.002384 | 0.067116 | -0.0022815 | 0.00046566 | 0.0021363 | -0.0038431 | 0.061203 | 0.068464 | -0.19635 | -0.00070281 | 61.1984 | -60.2371 | 0.07782 | -60.4294 | 60.9238 | -60.4523 | -60.379 | -60.7681 | -0.054932 | -60.7132 | 60.8734 | 60.9375 | -60.2142 | -60.4156 | -0.064087 | 0.009156 | -0.10529 | 0.15106 | -0.041198 | -0.050354 | 0.16937 | 0.17395 | -0.027465 | -0.15564 | -0.37994 | -0.32501 | -0.29755 | -0.091553 | 121.312 | 121.5866 | 60.466 | -121.4081 | 121.2616 | 121.3257 | 60.3333 | -121.4447
512.6562 | 121.6736 | -60.3928 | 61.0794 | -0.0049592 | 0.0025185 | 0.066042 | 0.0012476 | 0.064766 | 0.0056225 | -0.00017514 | 0.0097658 | -0.0012795 | 0.064407 | 0.068891 | -0.19507 | -0.0032662 | 61.2442 | -60.2325 | 0.11444 | -60.3928 | 60.997 | -60.466 | -60.3378 | -60.7132 | 0.004578 | -60.7132 | 60.9558 | 60.9833 | -60.2097 | -60.3973 | -0.073242 | 0.054931 | -0.082398 | 0.16022 | 0 | -0.054931 | 0.16479 | 0.1831 | -0.004578 | -0.1236 | -0.32044 | -0.32044 | -0.31586 | -0.096131 | 121.3898 | 121.637 | 60.5072 | -121.4172 | 121.3486 | 121.376 | 60.3973 | -121.4767
514.4219 | 121.6965 | -60.3287 | 61.1435 | -0.012589 | 0.0035867 | 0.062837 | 0.0012476 | 0.069039 | 0.0032727 | 0.0045245 | 0.0021363 | -0.0021341 | 0.067398 | 0.067823 | -0.1972 | -0.0024118 | 61.2717 | -60.1868 | 0.10986 | -60.3195 | 61.0519 | -60.4065 | -60.26 | -60.6628 | 0.009155 | -60.6583 | 61.0107 | 61.0703 | -60.1227 | -60.3561 | -0.07782 | 0.068664 | -0.091553 | 0.14191 | 0.009155 | -0.059509 | 0.12817 | 0.20599 | -0.027466 | -0.13275 | -0.33417 | -0.32959 | -0.30212 | -0.073243 | 121.3806 | 121.6003 | 60.4385 | -121.4035 | 121.3394 | 121.3989 | 60.3378 | -121.4996
516.1406 | 121.6919 | -60.2966 | 61.2076 | 0.0026703 | 0.0018777 | 0.066255 | 0.00082022 | 0.065407 | -0.0054859 | 0.0023883 | -0.0054932 | -0.0055521 | 0.064194 | 0.066969 | -0.19912 | -0.00113 | 61.3266 | -60.0677 | 0.20599 | -60.26 | 61.0199 | -60.3516 | -60.1959 | -60.5988 | 0.073242 | -60.553 | 60.9833 | 61.0336 | -60.0815 | -60.3012 | -0.054931 | 0.10071 | -0.18768 | 0.22888 | 0.036621 | -0.064087 | 0.11902 | 0.21515 | -0.004577 | -0.22431 | -0.30212 | -0.25635 | -0.25177 | -0.17395 | 121.3165 | 121.6232 | 60.5026 | -121.4035 | 121.2799 | 121.3303 | 60.3699 | -121.5088
517.8438 | 121.6232 | -60.2829 | 61.1984 | -0.0049592 | 0.0033731 | 0.063905 | 0.00060662 | 0.069466 | 0.0015637 | 0.0017475 | -0.0054932 | -0.00063872 | 0.06633 | 0.067396 | -0.1972 | -0.0041208 | 61.3083 | -60.173 | 0.1236 | -60.2921 | 61.0703 | -60.3699 | -60.2325 | -60.64 | 0.004578 | -60.6171 | 61.0199 | 61.0886 | -60.1135 | -60.3195 | -0.086975 | 0.050354 | -0.12817 | 0.10986 | -0.009155 | -0.059509 | 0.10986 | 0.16937 | -0.036621 | -0.17853 | -0.35706 | -0.33417 | -0.29755 | -0.10986 | 121.3531 | 121.5912 | 60.4065 | -121.431 | 121.3028 | 121.3715 | 60.2875 | -121.5179
519.6094 | 121.7148 | -60.2783 | 61.1801 | -0.0049592 | 0.0027323 | 0.068819 | 0.0016748 | 0.065193 | -0.0037769 | 0.0013203 | -0.0054932 | -0.0051247 | 0.065475 | 0.064833 | -0.20105 | -0.00048921 | 61.3495 | -60.0632 | 0.21515 | -60.26 | 61.0199 | -60.3333 | -60.1959 | -60.6079 | 0.082397 | -60.5301 | 60.9924 | 61.0703 | -60.0632 | -60.2875 | -0.054932 | 0.082397 | -0.16022 | 0.21515 | 0.01831 | -0.064087 | 0.16937 | 0.21515 | -0.009156 | -0.18768 | -0.32959 | -0.25177 | -0.24261 | -0.10986 | 121.2982 | 121.6278 | 60.4935 | -121.376 | 121.2708 | 121.3486 | 60.3607 | -121.4676
521.375 | 121.7422 | -60.3333 | 61.0611 | 0.0026703 | -0.0013267 | 0.06711 | -0.00088858 | 0.069252 | 0.0022047 | -0.00017514 | -0.0054932 | -0.00085232 | 0.063126 | 0.068891 | -0.19806 | -0.0019846 | 61.2808 | -60.1822 | 0.10986 | -60.3424 | 60.9467 | -60.4065 | -60.2921 | -60.6766 | -0.027466 | -60.6308 | 60.9192 | 60.9604 | -60.1868 | -60.3561 | -0.073242 | 0.041199 | -0.11444 | 0.15106 | -0.009155 | -0.050354 | 0.21973 | 0.14648 | -0.022888 | -0.14191 | -0.34332 | -0.29755 | -0.27466 | -0.10071 | 121.2799 | 121.6141 | 60.4431 | -121.3531 | 121.2524 | 121.2936 | 60.3058 | -121.4172
523.0625 | 121.7377 | -60.26 | 61.171 | -0.0049592 | 0.0014505 | 0.06476 | 0.00060662 | 0.066262 | -0.0016405 | 0.0013203 | -0.0054932 | -0.0029885 | 0.061417 | 0.06825 | -0.19699 | -0.00113 | 61.3541 | -60.1089 | 0.10529 | -60.2783 | 61.0245 | -60.3241 | -60.2097 | -60.6079 | -0.032043 | -60.5759 | 60.9695 | 61.0474 | -60.1089 | -60.3058 | -0.064087 | 0.050354 | -0.14648 | 0.15106 | -0.01831 | -0.068664 | 0.18311 | 0.15106 | -0.045776 | -0.20142 | -0.3479 | -0.31586 | -0.27008 | -0.1236 | 121.2845 | 121.6141 | 60.3653 | -121.3806 | 121.2296 | 121.3074 | 60.228 | -121.4767
524.8281 | 121.7377 | -60.1868 | 61.2671 | 0.0026703 | 0.0038003 | 0.06711 | 0.0018884 | 0.067543 | -0.0035633 | 0.00025206 | 0.0021363 | -0.0049111 | 0.066757 | 0.066755 | -0.20062 | -0.0026254 | 61.4594 | -59.967 | 0.21973 | -60.1547 | 61.1023 | -60.228 | -60.0998 | -60.5026 | 0.073242 | -60.4568 | 61.0977 | 61.1572 | -59.9945 | -60.1822 | -0.041198 | 0.086976 | -0.1648 | 0.21973 | 0.032044 | -0.054932 | 0.19226 | 0.19226 | 0.004578 | -0.16937 | -0.31586 | -0.27008 | -0.27466 | -0.10986 | 121.2891 | 121.6461 | 60.4065 | -121.3669 | 121.2845 | 121.344 | 60.26 | -121.4493
526.5312 | 121.6644 | -60.1868 | 61.3403 | -0.0049592 | 0.0010233 | 0.067537 | -3.4178e-05 | 0.066902 | 0.0011365 | -0.00081594 | 0.0021363 | -0.0014933 | 0.064835 | 0.066755 | -0.19934 | -0.0021982 | 61.5005 | -59.9625 | 0.19684 | -60.1181 | 61.171 | -60.1959 | -60.0586 | -60.4797 | 0.032043 | -60.4385 | 61.1526 | 61.2442 | -59.9533 | -60.1685 | -0.009155 | 0.12817 | -0.16937 | 0.22431 | 0.068665 | -0.059509 | 0.16022 | 0.23346 | 0.018311 | -0.18768 | -0.29297 | -0.25177 | -0.27008 | -0.09613 | 121.3577 | 121.6873 | 60.3836 | -121.3989 | 121.3394 | 121.431 | 60.2188 | -121.5088
528.2812 | 121.7514 | -60.1273 | 61.2625 | -0.0049592 | 0.0023049 | 0.065187 | -0.00067498 | 0.067971 | 0.00049567 | 0.0019611 | -0.0054932 | -0.0025613 | 0.063553 | 0.069532 | -0.19656 | -0.0019846 | 61.4914 | -59.9854 | 0.10071 | -60.1456 | 61.1389 | -60.2188 | -60.1089 | -60.4843 | -0.045776 | -60.4568 | 61.1069 | 61.171 | -59.9991 | -60.1868 | -0.091553 | 0.01831 | -0.1236 | 0.14191 | -0.018311 | -0.036621 | 0.22888 | 0.12817 | -0.05951 | -0.15564 | -0.35706 | -0.32959 | -0.27008 | -0.091553 | 121.2662 | 121.6187 | 60.228 | -121.3715 | 121.2341 | 121.2982 | 60.0815 | -121.4493
529.9844 | 121.7285 | -60.0815 | 61.3541 | 0.0026703 | 0.00016873 | 0.063905 | 0.00060662 | 0.068184 | -0.00057253 | 0.00067926 | -0.0054932 | -0.0025613 | 0.062057 | 0.068891 | -0.19827 | -0.002839 | 61.5463 | -59.935 | 0.10529 | -60.0906 | 61.1847 | -60.141 | -60.0037 | -60.4111 | -0.041199 | -60.3745 | 61.1572 | 61.2534 | -59.9121 | -60.1273 | -0.059509 | 0.07782 | -0.16937 | 0.14648 | -0.009155 | -0.086975 | 0.19226 | 0.16937 | -0.045776 | -0.19684 | -0.32959 | -0.29297 | -0.24719 | -0.10071 | 121.2662 | 121.6278 | 60.1868 | -121.3577 | 121.2387 | 121.3348 | 60.0403 | -121.4813
531.75 | 121.6873 | -60.0632 | 61.4136 | -0.0049592 | 0.0061501 | 0.066042 | 0.00082022 | 0.06733 | 0.0056225 | 0.0015339 | -0.013123 | 0.0017111 | 0.064194 | 0.069532 | -0.19549 | -0.0024118 | 61.5784 | -59.9258 | 0.11444 | -60.0586 | 61.3312 | -60.1089 | -60.022 | -60.3882 | 0 | -60.3973 | 61.2717 | 61.3449 | -59.8663 | -60.0861 | -0.045777 | 0.041198 | -0.082397 | 0.13733 | 0.004577 | -0.036621 | 0.1648 | 0.19684 | -0.022889 | -0.14191 | -0.32501 | -0.33417 | -0.31128 | -0.068664 | 121.3943 | 121.6415 | 60.1776 | -121.4355 | 121.3348 | 121.4081 | 60.0632 | -121.4996
533.4375 | 121.7743 | -60.0403 | 61.3632 | 0.0026703 | 0.0027323 | 0.063051 | -0.0017432 | 0.065193 | 0.00028207 | 0.0026019 | 0.0021363 | -0.0034159 | 0.065903 | 0.069532 | -0.19699 | -0.00070281 | 61.5143 | -59.9945 | 0.027466 | -60.1089 | 61.2762 | -60.1227 | -60.0037 | -60.4065 | -0.07782 | -60.3882 | 61.235 | 61.3129 | -59.8801 | -60.0906 | -0.082398 | 0.036621 | -0.086975 | 0.045776 | -0.068665 | -0.10529 | 0.15106 | 0.16022 | -0.050354 | -0.12817 | -0.36621 | -0.3479 | -0.29755 | -0.050354 | 121.3165 | 121.5546 | 60.0677 | -121.3669 | 121.2753 | 121.3531 | 59.9625 | -121.4539
535.2031 | 121.7377 | -59.9762 | 61.441 | -0.0049592 | -0.0026083 | 0.067537 | -0.0017432 | 0.066475 | 0.00028207 | 0.0013203 | -0.0054932 | -0.0044839 | 0.062485 | 0.066542 | -0.19806 | -0.001771 | 61.6516 | -59.8343 | 0.10529 | -59.9991 | 61.2808 | -60.0266 | -59.9487 | -60.3058 | -0.036621 | -60.2737 | 61.2579 | 61.3403 | -59.8114 | -60.0082 | -0.050354 | 0.027466 | -0.16022 | 0.14191 | -0.022888 | -0.050354 | 0.21057 | 0.1648 | -0.032044 | -0.1831 | -0.32959 | -0.29755 | -0.2655 | -0.10071 | 121.257 | 121.6278 | 60.0815 | -121.3898 | 121.2341 | 121.3165 | 59.9396 | -121.4493
536.9062 | 121.6461 | -59.9167 | 61.5921 | -0.0049592 | -0.00047207 | 0.065614 | 0.0031702 | 0.067116 | -0.0020679 | -0.00017514 | -0.0054932 | -0.0027749 | 0.067398 | 0.069319 | -0.20105 | -0.00048921 | 61.7111 | -59.7565 | 0.19226 | -59.903 | 61.3907 | -59.9625 | -59.848 | -60.2875 | -0.013733 | -60.2417 | 61.3541 | 61.4822 | -59.7565 | -59.9258 | -0.045776 | 0.068665 | -0.20142 | 0.16022 | 0.013733 | -0.054932 | 0.11902 | 0.16022 | -0.009155 | -0.23804 | -0.37079 | -0.32501 | -0.31586 | -0.10986 | 121.3074 | 121.6278 | 60.1089 | -121.4401 | 121.2708 | 121.3989 | 59.903 | -121.5179
538.6094 | 121.7743 | -59.9625 | 61.4548 | -0.012589 | 0.00016873 | 0.063692 | 0.0014612 | 0.064766 | 0.00092287 | 0.0032429 | 0.0021363 | -0.00063872 | 0.065048 | 0.069959 | -0.19699 | -0.0024118 | 61.6379 | -59.8572 | 0.07782 | -59.9945 | 61.3174 | -60.0403 | -59.9121 | -60.3012 | -0.054932 | -60.2737 | 61.2671 | 61.3541 | -59.8068 | -60.0082 | -0.07782 | 0.050354 | -0.13733 | 0.10529 | -0.032044 | -0.082398 | 0.1831 | 0.15564 | -0.045777 | -0.18768 | -0.33875 | -0.31128 | -0.2655 | -0.10071 | 121.2799 | 121.6003 | 60.0403 | -121.3669 | 121.2296 | 121.3165 | 59.9075 | -121.463
540.3906 | 121.7697 | -59.8572 | 61.5509 | -0.0049592 | -0.0051719 | 0.067323 | -0.0011024 | 0.066689 | -0.0050585 | 3.8456e-05 | 0.0021363 | -0.0049111 | 0.064194 | 0.068037 | -0.20083 | -0.00091641 | 61.7432 | -59.697 | 0.19684 | -59.8755 | 61.377 | -59.9442 | -59.8022 | -60.2097 | 0.050354 | -60.1273 | 61.3632 | 61.4548 | -59.6649 | -59.903 | -0.086975 | 0.054932 | -0.17395 | 0.16022 | -0.01831 | -0.073242 | 0.19226 | 0.19226 | -0.045776 | -0.18768 | -0.35248 | -0.27008 | -0.2243 | -0.09613 | 121.2341 | 121.6003 | 60.054 | -121.3531 | 121.2204 | 121.312 | 59.9075 | -121.4539
542.1719 | 121.669 | -59.7977 | 61.6974 | -0.0049592 | 0.0031595 | 0.066255 | -3.4178e-05 | 0.065621 | 0.00092287 | 0.00025206 | -0.0054932 | -0.0025613 | 0.063126 | 0.066114 | -0.19912 | -0.0032662 | 61.7706 | -59.7107 | 0.11444 | -59.8343 | 61.5875 | -59.8526 | -59.7656 | -60.2051 | -0.045776 | -60.1685 | 61.5189 | 61.6058 | -59.6375 | -59.8206 | -0.054932 | 0.032043 | -0.10986 | 0.086975 | -0.036622 | -0.068665 | 0.073242 | 0.16022 | -0.022889 | -0.17853 | -0.40741 | -0.37079 | -0.3479 | -0.091553 | 121.3852 | 121.5683 | 59.9121 | -121.463 | 121.3165 | 121.4035 | 59.7519 | -121.5179
543.875 | 121.7697 | -59.935 | 61.5051 | 0.0026703 | 0.00038233 | 0.068605 | 0.0012476 | 0.068398 | -0.0052721 | -0.0020977 | -0.013123 | -0.0029885 | 0.064194 | 0.06761 | -0.1987 | -0.0026254 | 61.734 | -59.6924 | 0.2243 | -59.903 | 61.3907 | -59.9579 | -59.848 | -60.2188 | 0.054932 | -60.1639 | 61.3266 | 61.4182 | -59.7382 | -59.9396 | -0.022888 | 0.086976 | -0.11444 | 0.24262 | 0.032044 | -0.054932 | 0.22888 | 0.19684 | -0.004577 | -0.17853 | -0.28381 | -0.22888 | -0.2243 | -0.086975 | 121.3257 | 121.669 | 60.1593 | -121.3531 | 121.2616 | 121.3531 | 59.9899 | -121.4447
545.5781 | 121.6919 | -60.0082 | 61.4639 | 0.0026703 | 0.0063639 | 0.065614 | 0.0029566 | 0.064339 | 0.0032727 | 3.8456e-05 | -0.013123 | -0.0012795 | 0.065262 | 0.069746 | -0.19891 | -0.0049752 | 61.6058 | -59.9258 | 0.13275 | -60.0174 | 61.3586 | -60.0952 | -59.967 | -60.3561 | -0.054932 | -60.3241 | 61.2991 | 61.3861 | -59.8297 | -60.0632 | -0.086975 | 0.041199 | -0.10529 | 0.082398 | -0.009155 | -0.050354 | 0.14191 | 0.17853 | -0.054931 | -0.1648 | -0.3479 | -0.31586 | -0.26093 | -0.07782 | 121.3669 | 121.6141 | 60.141 | -121.431 | 121.3074 | 121.3943 | 59.9533 | -121.5271
547.3438 | 121.7789 | -59.9579 | 61.4365 | -0.0049592 | 0.0031595 | 0.063478 | -0.00067498 | 0.066262 | 0.0022047 | 0.0032429 | 0.0021363 | -0.0025613 | 0.065475 | 0.068037 | -0.19571 | -0.00113 | 61.5829 | -59.8938 | 0.036621 | -60.0449 | 61.3861 | -60.0586 | -59.9487 | -60.3287 | -0.10529 | -60.3058 | 61.3266 | 61.3815 | -59.816 | -59.9899 | -0.10071 | 0.009156 | -0.050354 | 0.064087 | -0.086975 | -0.096131 | 0.14648 | 0.14191 | -0.032043 | -0.10986 | -0.37079 | -0.3479 | -0.31586 | -0.054931 | 121.344 | 121.5408 | 59.9945 | -121.3852 | 121.2845 | 121.3394 | 59.8526 | -121.4264
549.125 | 121.637 | -59.9625 | 61.5326 | 0.0026703 | 0.0025185 | 0.065187 | -0.003025 | 0.065834 | 0.0047681 | 0.0023883 | -0.0054932 | -0.0010659 | 0.065903 | 0.069105 | -0.19357 | -0.0024118 | 61.6837 | -59.8022 | 0.13733 | -59.9442 | 61.4319 | -59.9899 | -59.8663 | -60.2829 | -0.064087 | -60.2966 | 61.377 | 61.4639 | -59.7748 | -59.9533 | -0.027466 | 0.09613 | -0.10071 | 0.16022 | 0.01831 | -0.07782 | 0.15106 | 0.18768 | 0.009155 | -0.15564 | -0.32044 | -0.33417 | -0.34332 | -0.068665 | 121.3943 | 121.6461 | 60.0998 | -121.3989 | 121.3394 | 121.4264 | 59.8984 | -121.4859
550.8906 | 121.7743 | -60.0952 | 61.3083 | -0.012589 | -0.0023947 | 0.069032 | 0.0016748 | 0.067971 | -0.0035633 | 0.0013203 | 0.0021363 | -0.0059793 | 0.063339 | 0.066755 | -0.19934 | -0.0013436 | 61.4868 | -59.903 | 0.20599 | -60.1181 | 61.1618 | -60.1547 | -60.0632 | -60.4477 | 0.045776 | -60.3378 | 61.1252 | 61.235 | -59.9487 | -60.1273 | -0.059509 | 0.032044 | -0.14649 | 0.19226 | -0.022888 | -0.054932 | 0.17853 | 0.14649 | -0.032043 | -0.18311 | -0.35248 | -0.24261 | -0.21057 | -0.073243 | 121.257 | 121.582 | 60.3012 | -121.3715 | 121.2204 | 121.3303 | 60.141 | -121.4355
552.5938 | 121.7789 | -59.9854 | 61.3953 | 0.0026703 | 0.0020913 | 0.066683 | 0.0025292 | 0.066048 | -0.0037769 | 0.00067926 | 0.0021363 | -0.0068337 | 0.065903 | 0.068037 | -0.20019 | -0.00048921 | 61.5784 | -59.8434 | 0.20599 | -59.9991 | 61.2854 | -60.0723 | -59.967 | -60.3607 | 0.018311 | -60.2737 | 61.2305 | 61.29 | -59.8434 | -60.0403 | -0.086975 | 0.018311 | -0.10986 | 0.14191 | -0.013732 | -0.032043 | 0.18311 | 0.14191 | -0.054931 | -0.16479 | -0.37537 | -0.28839 | -0.23346 | -0.10529 | 121.2708 | 121.5637 | 60.1913 | -121.3623 | 121.2158 | 121.2753 | 60.0037 | -121.4355
554.3438 | 121.756 | -60.0128 | 61.4136 | -0.012589 | 0.0025185 | 0.061983 | -0.00088858 | 0.066048 | 0.0019909 | 0.0015339 | -0.0054932 | -0.0017069 | 0.064194 | 0.068678 | -0.19742 | -0.0041208 | 61.6058 | -59.8709 | 0.10529 | -60.0128 | 61.2762 | -60.0632 | -59.9487 | -60.3378 | -0.073242 | -60.3104 | 61.2305 | 61.2946 | -59.8434 | -60.0586 | -0.050354 | 0.064087 | -0.13733 | 0.14191 | 0 | -0.064087 | 0.19226 | 0.16937 | -0.045777 | -0.1831 | -0.32501 | -0.29755 | -0.25177 | -0.11902 | 121.2891 | 121.6187 | 60.1181 | -121.3623 | 121.2433 | 121.3074 | 59.9396 | -121.4722
556.0625 | 121.7239 | -59.9075 | 61.5051 | 0.0026703 | 0.00059593 | 0.066683 | -0.0036658 | 0.066475 | -0.0022815 | 0.0021747 | 0.0021363 | -0.0044839 | 0.063339 | 0.065473 | -0.19549 | -0.001771 | 61.6699 | -59.7748 | 0.13733 | -59.9533 | 61.3129 | -60.0128 | -59.8663 | -60.2646 | -0.07782 | -60.2463 | 61.2991 | 61.3724 | -59.7565 | -59.9854 | -0.10528 | 0.041199 | -0.19226 | 0.13275 | -0.045776 | -0.086975 | 0.16479 | 0.15106 | -0.07782 | -0.20599 | -0.35705 | -0.33874 | -0.26093 | -0.13275 | 121.2204 | 121.5775 | 60.0449 | -121.3715 | 121.2067 | 121.2799 | 59.8297 | -121.4905
557.8281 | 121.6415 | -59.9396 | 61.5097 | -0.0049592 | 0.0042275 | 0.063905 | 0.001034 | 0.065193 | 0.0062635 | 0.0032429 | 0.0021363 | -0.00042512 | 0.065475 | 0.06761 | -0.19635 | -0.0041208 | 61.6928 | -59.7702 | 0.16022 | -59.9258 | 61.4365 | -59.9762 | -59.8755 | -60.2417 | -0.050354 | -60.2646 | 61.3998 | 61.4502 | -59.7565 | -59.9304 | -0.036621 | 0.064087 | -0.073243 | 0.16937 | 0.013733 | -0.050354 | 0.18311 | 0.1831 | 0.009155 | -0.10986 | -0.30212 | -0.32501 | -0.33417 | -0.05951 | 121.376 | 121.6324 | 60.0998 | -121.3852 | 121.3394 | 121.3898 | 59.8892 | -121.4401
559.5312 | 121.6782 | -59.8938 | 61.5509 | -0.012589 | 0.0038003 | 0.068819 | 0.002102 | 0.067971 | -0.00035893 | 3.8456e-05 | -0.020752 | -0.0021341 | 0.067612 | 0.069105 | -0.19912 | -0.00048921 | 61.6699 | -59.8114 | 0.13275 | -59.9213 | 61.4868 | -59.9533 | -59.848 | -60.2875 | -0.09613 | -60.2646 | 61.4456 | 61.5097 | -59.7107 | -59.9121 | -0.059509 | 0.045777 | -0.064087 | 0.082398 | -0.027466 | -0.073243 | 0.11902 | 0.18311 | -0.01831 | -0.10528 | -0.39368 | -0.37079 | -0.35248 | -0.041198 | 121.3806 | 121.5637 | 60.0266 | -121.3989 | 121.3394 | 121.4035 | 59.7977 | -121.463
561.2969 | 121.7606 | -59.8114 | 61.5967 | -0.0049592 | 0.0023049 | 0.069246 | 0.00082022 | 0.068184 | -0.0059131 | 0.0013203 | -0.013123 | -0.0053385 | 0.065262 | 0.067823 | -0.19934 | -0.00070281 | 61.7203 | -59.7107 | 0.11902 | -59.8572 | 61.4822 | -59.8938 | -59.7977 | -60.2051 | -0.09613 | -60.1364 | 61.4273 | 61.5189 | -59.6237 | -59.8389 | -0.082398 | 0.013733 | -0.11444 | 0.10071 | -0.045777 | -0.05951 | 0.1236 | 0.18768 | -0.027466 | -0.16937 | -0.39368 | -0.32501 | -0.29755 | -0.07782 | 121.2936 | 121.5317 | 59.9304 | -121.3943 | 121.2387 | 121.3303 | 59.7153 | -121.4355
563 | 121.6965 | -59.7931 | 61.6745 | -0.012589 | 0.0055093 | 0.066042 | 0.0029566 | 0.066262 | -0.0022815 | 0.0015339 | -0.0054932 | -0.0044839 | 0.065475 | 0.066542 | -0.19934 | -0.0021982 | 61.8301 | -59.6008 | 0.24261 | -59.7702 | 61.4914 | -59.8343 | -59.7244 | -60.0906 | 0.009155 | -60.0632 | 61.4456 | 61.5372 | -59.6146 | -59.7885 | -0.041199 | 0.068665 | -0.18311 | 0.19226 | 0.022888 | -0.045777 | 0.15564 | 0.17853 | 0.004578 | -0.22888 | -0.29755 | -0.27008 | -0.27466 | -0.13733 | 121.2845 | 121.6232 | 60.0357 | -121.3989 | 121.2387 | 121.3303 | 59.8022 | -121.463
564.7969 | 121.6461 | -60.1868 | 61.3358 | 0.0026703 | 0.0048685 | 0.066469 | 0.0014612 | 0.067543 | -0.00035893 | -0.00038874 | -0.0054932 | -0.0019205 | 0.066757 | 0.067823 | -0.19998 | -0.0026254 | 61.4182 | -60.0266 | 0.18768 | -60.1776 | 61.171 | -60.2509 | -60.1181 | -60.5713 | -0.064087 | -60.5392 | 61.1252 | 61.2076 | -60.0174 | -60.2097 | -0.064086 | 0.068665 | -0.16479 | 0.16022 | 0.009156 | -0.059509 | 0.082398 | 0.16937 | -0.022888 | -0.21057 | -0.38452 | -0.35248 | -0.32959 | -0.12817 | 121.3577 | 121.6049 | 60.3745 | -121.4539 | 121.312 | 121.3943 | 60.1227 | -121.5454
566.4844 | 121.7194 | -60.2188 | 61.2167 | 0.0026703 | -0.00025847 | 0.065187 | -0.0045202 | 0.065621 | -0.00057253 | 3.8456e-05 | -0.013123 | -0.0023477 | 0.064194 | 0.068037 | -0.19763 | -0.0026254 | 61.377 | -60.0769 | 0.19684 | -60.2554 | 61.0336 | -60.3287 | -60.2005 | -60.5804 | -0.054932 | -60.5576 | 61.0107 | 61.0931 | -60.054 | -60.2875 | -0.10986 | 0.018311 | -0.18311 | 0.14191 | -0.036621 | -0.054932 | 0.16022 | 0.1648 | -0.068665 | -0.20599 | -0.36163 | -0.33874 | -0.27008 | -0.1236 | 121.2524 | 121.5958 | 60.4156 | -121.4172 | 121.2296 | 121.312 | 60.1639 | -121.5042
568.25 | 121.6415 | -60.1547 | 61.3495 | 0.0026703 | 0.0025185 | 0.063905 | -0.001316 | 0.065834 | 0.0041273 | 0.0015339 | 0.0021363 | -0.00085232 | 0.065689 | 0.068678 | -0.19592 | -0.00048921 | 61.4319 | -60.0494 | 0.086975 | -60.1776 | 61.2305 | -60.2097 | -60.0952 | -60.5301 | -0.17853 | -60.5484 | 61.1847 | 61.2625 | -59.9854 | -60.1959 | -0.054932 | 0.059509 | -0.11902 | 0.10529 | -0.022888 | -0.082397 | 0.082398 | 0.16937 | -0.041199 | -0.1648 | -0.37537 | -0.39368 | -0.35248 | -0.086975 | 121.3852 | 121.5866 | 60.2417 | -121.4447 | 121.3394 | 121.4172 | 59.9762 | -121.5454
569.9375 | 121.756 | -60.1685 | 61.2396 | -0.0049592 | -0.0015403 | 0.064546 | -0.0025976 | 0.067971 | -0.00099973 | 0.0026019 | 0.0021363 | -0.0012795 | 0.062912 | 0.070173 | -0.19592 | -0.0024118 | 61.4319 | -60.0266 | 0.13733 | -60.1868 | 61.1298 | -60.2463 | -60.1273 | -60.5072 | -0.10986 | -60.4843 | 61.0565 | 61.1572 | -60.0128 | -60.2051 | -0.07782 | 0.041199 | -0.10986 | 0.14191 | -0.018311 | -0.05951 | 0.19226 | 0.15564 | -0.036621 | -0.1831 | -0.33875 | -0.31586 | -0.27924 | -0.082397 | 121.2982 | 121.6003 | 60.3058 | -121.3669 | 121.225 | 121.3257 | 60.0586 | -121.4447
571.6406 | 121.7148 | -60.2051 | 61.2122 | 0.0026703 | -0.0017539 | 0.066255 | 0.00060662 | 0.068611 | -0.00057253 | 0.0011067 | 0.0021363 | -0.0042703 | 0.064407 | 0.068464 | -0.19763 | -0.0021982 | 61.3815 | -60.0449 | 0.13275 | -60.228 | 61.0382 | -60.2646 | -60.1685 | -60.5667 | -0.13733 | -60.5209 | 61.0291 | 61.1023 | -60.0494 | -60.2554 | -0.059509 | 0.036621 | -0.17395 | 0.16022 | -0.022888 | -0.059509 | 0.16937 | 0.15564 | -0.050354 | -0.18311 | -0.36163 | -0.31586 | -0.2655 | -0.10986 | 121.2433 | 121.5866 | 60.3378 | -121.3806 | 121.2341 | 121.3074 | 60.0677 | -121.4676
573.3906 | 121.756 | -59.9213 | 61.4685 | 0.0026703 | 0.0048685 | 0.063905 | -0.00088858 | 0.065834 | 0.0034863 | 0.0021747 | 0.0021363 | -0.0021341 | 0.065689 | 0.068891 | -0.19528 | -0.0015572 | 61.6196 | -59.8892 | 0.036621 | -59.9945 | 61.4044 | -60.0311 | -59.8892 | -60.3333 | -0.19226 | -60.3058 | 61.3403 | 61.4182 | -59.7656 | -59.9716 | -0.10986 | 0.032044 | -0.064087 | 0.032044 | -0.073242 | -0.10529 | 0.15106 | 0.15564 | -0.050354 | -0.12817 | -0.41199 | -0.38452 | -0.33417 | -0.050354 | 121.3257 | 121.5408 | 59.9579 | -121.3577 | 121.2616 | 121.3394 | 59.729 | -121.4401
575.1719 | 121.6461 | -59.8846 | 61.5921 | -0.0049592 | 0.0018777 | 0.067537 | 0.00039302 | 0.066689 | -0.0012133 | 0.0013203 | -0.0054932 | -0.0027749 | 0.063339 | 0.068891 | -0.1987 | -0.00027561 | 61.6837 | -59.7519 | 0.17853 | -59.903 | 61.4502 | -59.9167 | -59.8114 | -60.2966 | -0.1236 | -60.2417 | 61.441 | 61.528 | -59.7244 | -59.903 | -0.032043 | 0.073243 | -0.14191 | 0.13275 | -0.01831 | -0.091553 | 0.091553 | 0.16022 | -0.01831 | -0.15106 | -0.41199 | -0.35705 | -0.33874 | -0.064087 | 121.3348 | 121.5683 | 60.0632 | -121.4035 | 121.3257 | 121.4127 | 59.761 | -121.4951
576.9375 | 121.7056 | -60.1318 | 61.2991 | 0.0026703 | -0.0028219 | 0.066896 | -0.00067498 | 0.064125 | -0.0020679 | -0.00038874 | -0.0054932 | -0.0055521 | 0.062271 | 0.066328 | -0.19827 | -6.2012e-05 | 61.4365 | -59.9945 | 0.12817 | -60.1868 | 61.1526 | -60.1776 | -60.0677 | -60.5072 | -0.15564 | -60.4568 | 61.1206 | 61.1984 | -59.9625 | -60.1318 | -0.045776 | 0.064087 | -0.14648 | 0.13733 | -0.054932 | -0.11902 | 0.13733 | 0.16937 | 0 | -0.17853 | -0.37537 | -0.32501 | -0.32501 | -0.10071 | 121.2845 | 121.5683 | 60.26 | -121.3669 | 121.2524 | 121.3303 | 59.9762 | -121.431
578.6406 | 121.7102 | -60.0815 | 61.3358 | -0.0049592 | 0.0031595 | 0.067751 | 0.003811 | 0.067757 | -0.0014269 | -0.0010297 | -0.0054932 | -0.0044839 | 0.063766 | 0.066114 | -0.20126 | -0.0043344 | 61.5234 | -59.8709 | 0.24719 | -60.0632 | 61.1938 | -60.1181 | -60.0082 | -60.4111 | -0.022888 | -60.347 | 61.1893 | 61.2305 | -59.9258 | -60.0952 | -0.036621 | 0.073242 | -0.14191 | 0.21057 | 0.018311 | -0.054931 | 0.18768 | 0.15564 | -0.013733 | -0.14648 | -0.32959 | -0.2655 | -0.25177 | -0.10529 | 121.2753 | 121.6049 | 60.3287 | -121.344 | 121.2708 | 121.312 | 60.0586 | -121.431
580.3906 | 121.637 | -60.26 | 61.2167 | 0.0026703 | 0.0029459 | 0.06711 | 0.0029566 | 0.068611 | -0.0022815 | 0.0019611 | -0.0054932 | -0.0036295 | 0.065903 | 0.066542 | -0.19891 | -0.0026254 | 61.3403 | -60.0632 | 0.24261 | -60.2371 | 61.0336 | -60.3241 | -60.1959 | -60.6125 | -0.054932 | -60.553 | 60.997 | 61.0931 | -60.0998 | -60.2646 | -0.064087 | 0.064087 | -0.18311 | 0.19684 | 0.022888 | -0.041199 | 0.1236 | 0.16022 | -0.004577 | -0.21973 | -0.35248 | -0.29297 | -0.28839 | -0.1236 | 121.2936 | 121.6003 | 60.5026 | -121.4127 | 121.257 | 121.3531 | 60.2051 | -121.4813
582.0781 | 121.7148 | -60.5759 | 60.8368 | 0.0103 | 0.00080973 | 0.065401 | -0.0032386 | 0.067971 | 6.8274e-05 | -0.00017514 | 0.0021363 | -0.0029885 | 0.063766 | 0.066755 | -0.19848 | -0.0019846 | 61.0199 | -60.4111 | 0.14191 | -60.6033 | 60.6812 | -60.64 | -60.5484 | -60.9192 | -0.14648 | -60.8871 | 60.64 | 60.7544 | -60.4156 | -60.5942 | -0.064087 | 0.027466 | -0.15564 | 0.1648 | -0.027466 | -0.054932 | 0.1831 | 0.16022 | -0.01831 | -0.19684 | -0.34332 | -0.31128 | -0.29297 | -0.082397 | 121.257 | 121.5958 | 60.7178 | -121.3852 | 121.2158 | 121.3303 | 60.4294 | -121.431
583.8438 | 121.6782 | -60.6491 | 60.8139 | -0.0049592 | 0.0067911 | 0.063265 | 0.0029566 | 0.067757 | 0.00070927 | 0.0026019 | -0.020752 | -0.00085232 | 0.065475 | 0.0706 | -0.19848 | -0.0036936 | 60.9512 | -60.5438 | 0.14191 | -60.6491 | 60.7773 | -60.6766 | -60.5804 | -61.0199 | -0.17395 | -61.0016 | 60.7132 | 60.791 | -60.4614 | -60.6354 | -0.027466 | 0.068665 | -0.036621 | 0.10529 | 0 | -0.068665 | 0.13733 | 0.18768 | 0.013733 | -0.10071 | -0.37079 | -0.35248 | -0.36621 | -0.022888 | 121.4264 | 121.6003 | 60.791 | -121.3943 | 121.3623 | 121.4401 | 60.4752 | -121.4493
585.5469 | 121.7514 | -61.4319 | 59.9533 | 0.0026703 | -0.0011131 | 0.067751 | 0.001034 | 0.064339 | -0.0035633 | -0.00060234 | -0.0054932 | -0.0049111 | 0.062912 | 0.065901 | -0.19955 | -0.002839 | 60.1822 | -61.235 | 0.23804 | -61.4182 | 59.8297 | -61.5234 | -61.377 | -61.7523 | -0.064087 | -61.6882 | 59.7794 | 59.8618 | -61.2717 | -61.4548 | -0.091552 | 0.054932 | -0.1236 | 0.19684 | 0.013733 | -0.041199 | 0.22888 | 0.16022 | -0.022888 | -0.17395 | -0.32043 | -0.25635 | -0.23346 | -0.091553 | 121.2616 | 121.6141 | 61.6699 | -121.3303 | 121.2112 | 121.2936 | 61.3678 | -121.4081
587.3281 | 121.7651 | -60.7773 | 60.6171 | 0.0026703 | 0.0023049 | 0.063265 | -0.001316 | 0.066689 | 0.0026319 | 0.0019611 | -0.0054932 | -0.00085232 | 0.06398 | 0.069746 | -0.19742 | -0.0024118 | 60.7407 | -60.7544 | 0.050354 | -60.878 | 60.5026 | -60.9055 | -60.7864 | -61.1847 | -0.21515 | -61.1664 | 60.4752 | 60.5301 | -60.6583 | -60.8597 | -0.12817 | -0.009155 | -0.11444 | 0.022888 | -0.10071 | -0.091553 | 0.1236 | 0.11902 | -0.082397 | -0.14191 | -0.40741 | -0.3891 | -0.3067 | -0.086975 | 121.2799 | 121.5179 | 60.8276 | -121.4035 | 121.2524 | 121.3074 | 60.5621 | -121.4767
589.0312 | 121.7789 | -60.4843 | 60.9009 | -0.012589 | 0.0018777 | 0.06711 | -0.0028112 | 0.062844 | -0.0044177 | -0.00060234 | -0.0054932 | -0.0053385 | 0.065475 | 0.064833 | -0.19912 | -0.00070281 | 61.084 | -60.3378 | 0.15106 | -60.4797 | 60.8047 | -60.5484 | -60.4294 | -60.8414 | -0.14191 | -60.7544 | 60.791 | 60.8734 | -60.2737 | -60.4706 | -0.064087 | 0.054932 | -0.09613 | 0.14648 | 0.004578 | -0.050354 | 0.1831 | 0.21057 | 0.013733 | -0.10986 | -0.35706 | -0.27008 | -0.28381 | -0.027466 | 121.2891 | 121.5683 | 60.6354 | -121.3303 | 121.2753 | 121.3577 | 60.3424 | -121.3715
590.7969 | 121.6599 | -62.4481 | 59.0332 | -0.0049592 | 0.0033731 | 0.065614 | 0.00039302 | 0.067971 | 0.0011365 | 0.00025206 | -0.0054932 | -0.0021341 | 0.065689 | 0.066328 | -0.20105 | -0.0034798 | 59.1705 | -62.2284 | 0.24719 | -62.3978 | 58.8409 | -62.5122 | -62.4023 | -62.7869 | -0.10071 | -62.7274 | 58.8638 | 58.9096 | -62.2879 | -62.4756 | -0.064087 | 0.045776 | -0.19226 | 0.21973 | 0.050354 | 0.004578 | 0.13733 | 0.16022 | -0.027466 | -0.16937 | -0.33874 | -0.27924 | -0.25177 | -0.1236 | 121.2891 | 121.6187 | 62.6953 | -121.4355 | 121.312 | 121.3577 | 62.3474 | -121.5088
592.5781 | 121.7285 | -62.6266 | 58.754 | -0.0049592 | -0.00089927 | 0.06476 | -0.001316 | 0.066262 | 0.0019909 | 0.0036701 | -0.0054932 | -0.0032021 | 0.064194 | 0.069105 | -0.19912 | -0.0015572 | 58.9462 | -62.4939 | 0.11902 | -62.6541 | 58.5983 | -62.764 | -62.6312 | -62.9562 | -0.20599 | -62.9425 | 58.5754 | 58.6258 | -62.4802 | -62.7045 | -0.13733 | -0.004578 | -0.15564 | 0.13275 | -0.027466 | -0.022888 | 0.19226 | 0.14648 | -0.07782 | -0.17853 | -0.32959 | -0.31586 | -0.23804 | -0.12817 | 121.225 | 121.5729 | 62.7457 | -121.3852 | 121.2021 | 121.2524 | 62.4207 | -121.4584
594.3438 | 121.6461 | -63.4964 | 57.9483 | -0.0049592 | 0.0033731 | 0.064119 | -0.0032386 | 0.066048 | 0.0041273 | 0.0021747 | 0.0097658 | 0.00021568 | 0.062485 | 0.06825 | -0.19442 | -0.0019846 | 58.0765 | -63.3728 | 0.07782 | -63.5056 | 57.8979 | -63.5559 | -63.4186 | -63.8672 | -0.28839 | -63.8947 | 57.8522 | 57.9071 | -63.3224 | -63.5239 | -0.059509 | 0.07782 | -0.050354 | 0.1236 | -0.009155 | -0.086975 | 0.12817 | 0.17395 | -0.027466 | -0.09613 | -0.37079 | -0.39825 | -0.37079 | -0.041199 | 121.3943 | 121.5729 | 63.5742 | -121.3669 | 121.3486 | 121.4035 | 63.208 | -121.4722
596.0938 | 121.7926 | -64.2883 | 57.1381 | -0.0049592 | -0.0028219 | 0.067751 | -0.00088858 | 0.068611 | -0.0046313 | 0.0023883 | -0.013123 | -0.0042703 | 0.062057 | 0.066328 | -0.19977 | -0.00027561 | 57.2525 | -64.1418 | 0.17853 | -64.3112 | 56.9229 | -64.4028 | -64.2609 | -64.6545 | -0.14191 | -64.563 | 56.955 | 57.0236 | -64.1281 | -64.3341 | -0.11444 | 0.027466 | -0.21515 | 0.14648 | -0.022888 | -0.050354 | 0.11444 | 0.16022 | -0.045776 | -0.18311 | -0.36621 | -0.27466 | -0.22888 | -0.11444 | 121.2112 | 121.5408 | 64.4669 | -121.3989 | 121.2433 | 121.312 | 64.1464 | -121.4722
597.8594 | 121.6461 | -63.0432 | 58.4427 | -0.0049592 | 0.0055093 | 0.063051 | 0.0046656 | 0.064553 | 0.0011365 | -0.0016705 | 0.0097658 | -0.0012795 | 0.065903 | 0.06761 | -0.19998 | -0.0019846 | 58.4976 | -62.9379 | 0.1831 | -63.0981 | 58.2916 | -63.121 | -63.0203 | -63.4781 | -0.20142 | -63.4232 | 58.2825 | 58.3008 | -62.915 | -63.0981 | -0.07782 | 0.022888 | -0.15106 | 0.10529 | -0.054932 | -0.07782 | 0.054932 | 0.12817 | -0.054932 | -0.16022 | -0.43487 | -0.37994 | -0.32501 | -0.14191 | 121.3348 | 121.5408 | 63.2263 | -121.463 | 121.3257 | 121.344 | 62.8418 | -121.5408
599.5625 | 121.6782 | -63.7848 | 57.6691 | -0.012589 | 0.0065775 | 0.064974 | 0.0033838 | 0.065193 | 0.0024183 | 0.00089286 | -0.0054932 | -0.00021152 | 0.065903 | 0.066755 | -0.19891 | -0.0021982 | 57.7652 | -63.6887 | 0.16479 | -63.8077 | 57.5867 | -63.858 | -63.7436 | -64.1968 | -0.25177 | -64.151 | 57.5455 | 57.5912 | -63.6292 | -63.8306 | -0.073242 | 0.041199 | -0.082397 | 0.09613 | -0.022888 | -0.064087 | 0.096131 | 0.15564 | -0.045776 | -0.1236 | -0.41199 | -0.36621 | -0.32043 | -0.077819 | 121.3715 | 121.55 | 63.9496 | -121.4127 | 121.3303 | 121.376 | 63.533 | -121.4996
601.3125 | 121.7606 | -64.325 | 57.1106 | 0.0026703 | 0.0033731 | 0.064333 | 0.00039302 | 0.064766 | 0.0015637 | 0.00089286 | -0.0054932 | -0.00085232 | 0.066116 | 0.068464 | -0.1972 | -0.002839 | 57.3807 | -64.0594 | 0.073242 | -64.1876 | 57.1564 | -64.27 | -64.1418 | -64.5447 | -0.29297 | -64.5172 | 57.0923 | 57.1381 | -64.0228 | -64.238 | 0.054931 | 0.1831 | 0.045776 | 0.2655 | 0.13733 | -0.045776 | 0.27008 | 0.30212 | 0.086975 | -0.018311 | -0.21973 | -0.19226 | -0.27924 | 0.027466 | 121.4813 | 121.7056 | 64.3982 | -121.2524 | 121.4172 | 121.463 | 64.032 | -121.3486
603.0781 | 121.7651 | -64.769 | 56.6437 | -0.020218 | 0.0010233 | 0.066896 | 0.002102 | 0.065407 | -0.0048449 | 0.00025206 | 0.0021363 | -0.0049111 | 0.065262 | 0.063764 | -0.20041 | 0.00015159 | 56.8314 | -64.5126 | 0.25177 | -64.7461 | 56.5292 | -64.8239 | -64.7003 | -65.0803 | -0.11444 | -64.9796 | 56.4651 | 56.5613 | -64.5905 | -64.7781 | -0.054932 | 0.068665 | -0.11444 | 0.25635 | 0.022888 | -0.045777 | 0.18768 | 0.17853 | -0.009155 | -0.17853 | -0.31128 | -0.21057 | -0.20142 | -0.082398 | 121.2982 | 121.6003 | 65.0208 | -121.344 | 121.2341 | 121.3303 | 64.6545 | -121.4218
604.8594 | 121.6873 | -63.8351 | 57.6141 | 0.0026703 | 0.0063639 | 0.065614 | 0.0012476 | 0.069039 | 0.0032727 | 0.0017475 | 0.0021363 | -0.00042512 | 0.067398 | 0.069319 | -0.19742 | -0.0032662 | 57.7194 | -63.7024 | 0.16479 | -63.8351 | 57.5226 | -63.9221 | -63.7894 | -64.2014 | -0.24261 | -64.1785 | 57.4722 | 57.5043 | -63.6612 | -63.8901 | -0.086975 | 0.045776 | -0.091553 | 0.13275 | 0 | -0.045776 | 0.10528 | 0.17395 | -0.054932 | -0.14191 | -0.36621 | -0.34332 | -0.28839 | -0.10986 | 121.3577 | 121.5546 | 63.9999 | -121.4035 | 121.3074 | 121.3394 | 63.5925 | -121.5042
606.5625 | 121.7239 | -65.3 | 56.0898 | -0.012589 | 0.0020913 | 0.064974 | -0.0011024 | 0.067116 | -0.00099973 | 0.0015339 | -0.0054932 | -0.0049111 | 0.063126 | 0.068037 | -0.20169 | 0.00057899 | 56.3049 | -65.0665 | 0.082397 | -65.2817 | 55.9753 | -65.3778 | -65.2313 | -65.6525 | -0.37079 | -65.6021 | 55.9433 | 56.0257 | -65.1352 | -65.3503 | -0.07782 | 0.068665 | -0.11444 | 0.23346 | 0.018311 | -0.050354 | 0.21515 | 0.16479 | -0.050354 | -0.14648 | -0.35248 | -0.30212 | -0.25177 | -0.064087 | 121.2753 | 121.6049 | 65.3824 | -121.3211 | 121.2433 | 121.3257 | 64.9292 | -121.4401
608.3438 | 121.7285 | -66.9388 | 54.4785 | 0.0026703 | 0.0027323 | 0.063692 | -0.00067498 | 0.064553 | -0.00078613 | 0.0017475 | 0.0021363 | -0.0042703 | 0.064621 | 0.066755 | -0.19742 | -0.0021982 | 54.6616 | -66.7191 | 0.11902 | -66.9113 | 54.3182 | -67.0166 | -66.9022 | -67.2592 | -0.29755 | -67.2134 | 54.3137 | 54.364 | -66.7603 | -66.9571 | -0.07782 | 0.036621 | -0.16022 | 0.21973 | 0.027466 | -0.009155 | 0.18311 | 0.17853 | -0.01831 | -0.16479 | -0.32043 | -0.27466 | -0.25635 | -0.11444 | 121.257 | 121.6003 | 67.0578 | -121.3806 | 121.2524 | 121.3028 | 66.6412 | -121.4355
610.1094 | 121.7468 | -67.3737 | 54.0756 | 0.0103 | -0.0047445 | 0.066255 | -0.001316 | 0.066689 | -0.0029223 | 0.00025206 | -0.0054932 | -0.0038431 | 0.063553 | 0.066328 | -0.1987 | -0.001771 | 54.2908 | -67.0349 | 0.23804 | -67.2729 | 53.9429 | -67.4194 | -67.2638 | -67.6804 | -0.23346 | -67.598 | 53.9017 | 53.9337 | -67.1722 | -67.3782 | -0.045777 | 0.10986 | -0.13275 | 0.33874 | 0.10071 | -0.009155 | 0.21515 | 0.20142 | -0.004578 | -0.17395 | -0.3067 | -0.2243 | -0.21973 | -0.14191 | 121.3165 | 121.6644 | 67.6117 | -121.3394 | 121.2753 | 121.3074 | 67.1402 | -121.4539
611.8125 | 121.7102 | -68.7469 | 52.6428 | 0.0103 | 0.0035867 | 0.066896 | 0.0012476 | 0.065834 | -0.0018543 | -0.00081594 | -0.0054932 | -0.0040567 | 0.064194 | 0.069532 | -0.19827 | -0.00113 | 52.8214 | -68.5547 | 0.091553 | -68.7515 | 52.5238 | -68.8568 | -68.6737 | -69.1452 | -0.38452 | -69.0811 | 52.4689 | 52.565 | -68.5593 | -68.811 | -0.10986 | 0.073242 | -0.11902 | 0.19226 | -0.004578 | -0.07782 | 0.17853 | 0.18768 | -0.064087 | -0.17395 | -0.39825 | -0.33417 | -0.27008 | -0.07782 | 121.2708 | 121.5683 | 68.8385 | -121.3165 | 121.2158 | 121.3119 | 68.3624 | -121.4539
613.5312 | 121.6324 | -69.6899 | 51.7319 | 0.0026703 | 0.0074319 | 0.063905 | -0.00024778 | 0.067116 | 0.0036999 | 0.0015339 | -0.0054932 | 0.0021383 | 0.066544 | 0.068037 | -0.19677 | -0.0019846 | 51.8738 | -69.5343 | 0.07782 | -69.6854 | 51.6678 | -69.7906 | -69.635 | -70.0928 | -0.43488 | -70.0699 | 51.622 | 51.6861 | -69.5023 | -69.7266 | -0.10071 | 0.054931 | -0.064087 | 0.15564 | 0.004577 | -0.050354 | 0.14191 | 0.18768 | -0.036621 | -0.10986 | -0.40283 | -0.37994 | -0.34332 | -0.045777 | 121.3577 | 121.5637 | 69.7678 | -121.3669 | 121.3119 | 121.376 | 69.2551 | -121.4584
615.2969 | 121.6278 | -69.3878 | 52.0981 | -0.0049592 | 0.0048685 | 0.063692 | 0.0014612 | 0.06733 | 0.0054089 | 0.0040973 | 0.0021363 | 0.0036337 | 0.066971 | 0.069319 | -0.19742 | -0.0039072 | 52.2263 | -69.1589 | 0.10529 | -69.3466 | 51.9745 | -69.4519 | -69.2963 | -69.7266 | -0.45776 | -69.7083 | 51.9287 | 51.9928 | -69.1818 | -69.4199 | -0.064087 | 0.091552 | -0.1236 | 0.22888 | 0.041198 | -0.050354 | 0.12817 | 0.20599 | -0.032044 | -0.16937 | -0.33875 | -0.32044 | -0.28839 | -0.10529 | 121.3623 | 121.6141 | 69.4931 | -121.3943 | 121.3165 | 121.3806 | 68.9301 | -121.5179
617.0625 | 121.7056 | -69.6075 | 51.8097 | -0.012589 | 0.0027323 | 0.066896 | 0.0018884 | 0.06733 | -0.0065539 | 3.8456e-05 | 0.0097658 | -0.0029885 | 0.065262 | 0.065473 | -0.19891 | -6.2012e-05 | 52.0065 | -69.3054 | 0.24719 | -69.5435 | 51.6907 | -69.6625 | -69.5297 | -69.9142 | -0.27466 | -69.8502 | 51.6541 | 51.7273 | -69.4153 | -69.5984 | -0.054932 | 0.07782 | -0.11902 | 0.30212 | 0.064087 | -0.013733 | 0.19684 | 0.19226 | 0.009155 | -0.15564 | -0.3067 | -0.24262 | -0.25177 | -0.082397 | 121.2982 | 121.6141 | 69.8547 | -121.3394 | 121.2616 | 121.3348 | 69.3329 | -121.4081
618.8438 | 121.7194 | -69.0445 | 52.3636 | 0.0026703 | -4.4874e-05 | 0.067751 | -3.4178e-05 | 0.067543 | -0.0052721 | -0.00038874 | -0.013123 | -0.0051247 | 0.064407 | 0.066755 | -0.20041 | 0.0012198 | 52.4963 | -68.8522 | 0.11444 | -69.0353 | 52.2446 | -69.136 | -68.985 | -69.4473 | -0.42572 | -69.3558 | 52.2034 | 52.2812 | -68.9026 | -69.0948 | -0.091552 | 0.05951 | -0.11902 | 0.19226 | 0.009156 | -0.050354 | 0.13275 | 0.14191 | -0.050354 | -0.16022 | -0.40283 | -0.31128 | -0.26093 | -0.082397 | 121.2891 | 121.5408 | 69.1589 | -121.3486 | 121.2479 | 121.3257 | 68.6188 | -121.4584
620.5469 | 121.7194 | -70.1431 | 51.2741 | 0.0026703 | -0.0026083 | 0.065401 | -3.4178e-05 | 0.067543 | -0.0029223 | 0.0026019 | 0.0097658 | -0.0061929 | 0.06398 | 0.068678 | -0.1987 | -0.00070281 | 51.4526 | -69.8639 | 0.082397 | -70.0836 | 51.1734 | -70.1981 | -70.0562 | -70.4956 | -0.4715 | -70.4132 | 51.1276 | 51.1826 | -69.9417 | -70.1569 | -0.054932 | 0.086975 | -0.10071 | 0.27923 | 0.059509 | -0.027466 | 0.17853 | 0.20142 | -0.013733 | -0.14648 | -0.35248 | -0.27008 | -0.25635 | -0.091553 | 121.3165 | 121.5958 | 70.2255 | -121.3303 | 121.2708 | 121.3257 | 69.6716 | -121.431
622.2812 | 121.6461 | -69.5389 | 51.915 | -0.0049592 | 0.0038003 | 0.064974 | 0.0018884 | 0.067757 | -0.00057253 | 0.0015339 | -0.0054932 | -0.0044839 | 0.062912 | 0.065687 | -0.19912 | -0.0015572 | 52.1027 | -69.2276 | 0.17853 | -69.4565 | 51.7822 | -69.5755 | -69.4336 | -69.8685 | -0.37079 | -69.7723 | 51.741 | 51.8005 | -69.3466 | -69.5389 | -0.036621 | 0.10528 | -0.13275 | 0.31128 | 0.082397 | -0.022888 | 0.18768 | 0.19226 | 0 | -0.17395 | -0.32959 | -0.23346 | -0.23346 | -0.11444 | 121.3211 | 121.6415 | 69.7174 | -121.3486 | 121.2799 | 121.3394 | 69.1681 | -121.4539
624.0469 | 121.6278 | -67.9047 | 53.5629 | -0.0049592 | 0.0025185 | 0.063265 | -0.0032386 | 0.063912 | 0.0049817 | 0.0019611 | 0.0097658 | 0.0017111 | 0.065689 | 0.069746 | -0.19784 | -0.0030526 | 53.6774 | -67.7353 | 0.054932 | -67.8772 | 53.4943 | -67.9367 | -67.8085 | -68.2983 | -0.48523 | -68.2709 | 53.4622 | 53.5172 | -67.6987 | -67.9138 | -0.032044 | 0.09613 | -0.068664 | 0.16937 | 0.027466 | -0.068664 | 0.11444 | 0.20599 | -0.009155 | -0.10071 | -0.39368 | -0.36621 | -0.35706 | -0.045776 | 121.3989 | 121.582 | 67.9596 | -121.3715 | 121.3669 | 121.4218 | 67.4194 | -121.4767
625.75 | 121.6415 | -75.0275 | 46.4539 | 0.0026703 | 0.0035867 | 0.065187 | 0.00017942 | 0.066262 | -0.00078613 | 0.00089286 | 0.0097658 | -0.0032021 | 0.065262 | 0.068464 | -0.19763 | -0.00070281 | 46.5546 | -74.7528 | 0.082397 | -74.9588 | 46.3074 | -75.1144 | -74.9496 | -75.4166 | -0.58136 | -75.3433 | 46.312 | 46.3715 | -74.8672 | -75.0687 | -0.086975 | 0.07782 | -0.14648 | 0.27466 | 0.068665 | -0.009155 | 0.10071 | 0.16022 | -0.041199 | -0.14191 | -0.3891 | -0.31586 | -0.27466 | -0.082397 | 121.3348 | 121.582 | 75.1099 | -121.4035 | 121.3394 | 121.3989 | 74.4461 | -121.5225
627.5312 | 121.7606 | -79.1428 | 42.1967 | -0.0049592 | 0.0044411 | 0.066469 | -0.00046138 | 0.065621 | 0.0019909 | 0.0034565 | -0.0054932 | 0.0012839 | 0.067184 | 0.071028 | -0.1987 | -0.0041208 | 42.3477 | -78.9963 | 1.0483 | -79.1656 | 42.1646 | -79.335 | -79.1702 | -79.5868 | 0.55389 | -79.4998 | 42.1188 | 42.1738 | -79.0283 | -79.2389 | -0.19226 | -0.027466 | -0.032043 | 0.14648 | -0.022888 | 0.004578 | 0.15106 | 0.11444 | -0.096131 | -0.07782 | -0.44403 | -0.35706 | -0.26092 | -0.022888 | 121.3074 | 121.4905 | 80.191 | -121.3669 | 121.2616 | 121.3165 | 79.6967 | -121.4355
629.2969 | 121.6827 | -74.4278 | 47.0306 | -0.012589 | 0.0012369 | 0.06711 | 0.00017942 | 0.066689 | -0.00035893 | 0.0023883 | 0.0021363 | -0.0010659 | 0.065262 | 0.06761 | -0.19827 | 0.00057899 | 47.1405 | -74.2172 | 0.064087 | -74.3774 | 46.9391 | -74.5056 | -74.35 | -74.8169 | -0.59509 | -74.7528 | 46.9345 | 46.9894 | -74.231 | -74.4507 | -0.07782 | 0.077819 | -0.091553 | 0.21057 | 0.050354 | -0.027465 | 0.10986 | 0.19684 | -0.022889 | -0.096131 | -0.3891 | -0.32501 | -0.30212 | -0.041199 | 121.3669 | 121.5683 | 74.4919 | -121.3806 | 121.3623 | 121.4172 | 73.8327 | -121.4813
631.0625 | 121.6644 | -81.0287 | 40.3976 | -0.0049592 | 0.0029459 | 0.066042 | -3.4178e-05 | 0.065621 | -0.0020679 | 0.00046566 | -0.0054932 | -0.0032021 | 0.065689 | 0.069319 | -0.20169 | 0.0014334 | 40.4526 | -80.8319 | -0.036621 | -81.0287 | 40.2832 | -81.1935 | -81.0425 | -81.4819 | -0.86975 | -81.3812 | 40.2786 | 40.3427 | -80.9006 | -81.134 | -0.16479 | -0.013732 | -0.11444 | 0.19684 | 0 | 0.013732 | 0.054932 | 0.12817 | -0.10529 | -0.11902 | -0.45319 | -0.35248 | -0.24719 | -0.054932 | 121.312 | 121.4813 | 80.9921 | -121.4401 | 121.3074 | 121.3715 | 80.159 | -121.5317
632.7969 | 121.6782 | -79.3488 | 42.1005 | -0.012589 | 0.0029459 | 0.063478 | 0.0027428 | 0.064125 | 0.00070927 | -0.00017514 | -0.0054932 | -0.0014933 | 0.065262 | 0.069105 | -0.19677 | -0.0015572 | 42.2195 | -79.0878 | 0.009155 | -79.2435 | 42.0456 | -79.4266 | -79.248 | -79.7287 | -0.74616 | -79.628 | 42.0136 | 42.0868 | -79.129 | -79.3533 | -0.07782 | 0.10071 | -0.054932 | 0.26093 | 0.10529 | 0.004578 | 0.11902 | 0.21973 | -0.004578 | -0.086975 | -0.37994 | -0.27924 | -0.27466 | -0.013733 | 121.3943 | 121.5683 | 79.3579 | -121.3486 | 121.3623 | 121.4355 | 78.6026 | -121.4539
634.5781 | 121.7789 | -86.5585 | 34.758 | -0.0049592 | 0.0016641 | 0.065401 | -0.0019568 | 0.066689 | -0.00014533 | 0.00067926 | 0.0097658 | -0.0038431 | 0.064194 | 0.06825 | -0.19742 | -0.00113 | 34.996 | -86.2518 | -0.12817 | -86.4853 | 34.6848 | -86.7142 | -86.5311 | -86.9385 | -1.0208 | -86.8378 | 34.639 | 34.7214 | -86.4258 | -86.6592 | -0.15564 | 0.027466 | -0.073243 | 0.3067 | 0.073242 | 0.045776 | 0.23804 | 0.13275 | -0.10071 | -0.11902 | -0.37994 | -0.27924 | -0.17853 | -0.036621 | 121.2433 | 121.5546 | 86.4304 | -121.2891 | 121.1975 | 121.2799 | 85.5377 | -121.4172
636.3594 | 121.7285 | -87.6663 | 33.7234 | -0.0049592 | 0.0016641 | 0.06711 | 0.0012476 | 0.066689 | -0.0039905 | 0.00046566 | -0.0054932 | -0.0057657 | 0.063766 | 0.06761 | -0.19998 | 0.00015159 | 33.8196 | -87.4008 | -0.10071 | -87.6297 | 33.5724 | -87.8586 | -87.6297 | -88.1424 | -1.1261 | -88.0005 | 33.5449 | 33.6227 | -87.5519 | -87.7625 | -0.19226 | 0.036621 | -0.15106 | 0.2655 | 0.036621 | 0 | 0.09613 | 0.11444 | -0.09613 | -0.17853 | -0.47607 | -0.33417 | -0.23804 | -0.10071 | 121.2387 | 121.4859 | 87.5656 | -121.3531 | 121.2112 | 121.2891 | 86.5402 | -121.4859
638.125 | 121.6141 | -81.1066 | 40.3519 | -0.0049592 | 0.0067911 | 0.063265 | 0.0025292 | 0.067116 | 0.0024183 | 0.0023883 | 0.0021363 | -0.0014933 | 0.066116 | 0.070173 | -0.19784 | -0.004548 | 40.7272 | -80.603 | 0.88806 | -80.8136 | 40.4526 | -80.9875 | -80.8182 | -81.2851 | 0.14191 | -81.1935 | 40.3931 | 40.4572 | -80.722 | -80.9509 | 0.11902 | 0.28839 | 0.10071 | 0.50354 | 0.29297 | 0.004577 | 0.37537 | 0.38452 | 0.15564 | 0.041198 | -0.17853 | -0.086975 | -0.24261 | 0.10528 | 121.5591 | 121.8338 | 81.9946 | -121.17 | 121.4996 | 121.5637 | 81.2485 | -121.3028
639.8281 | 121.756 | -82.7133 | 38.6673 | 0.0026703 | 0.0014505 | 0.06476 | -0.0021704 | 0.065621 | -0.0014269 | -0.00017514 | 0.0021363 | -0.0034159 | 0.063766 | 0.071028 | -0.19763 | -0.00113 | 38.8779 | -82.3929 | -0.041199 | -82.6172 | 38.5574 | -82.8323 | -82.6447 | -83.0566 | -0.94757 | -82.9651 | 38.5025 | 38.5849 | -82.5439 | -82.7682 | -0.11902 | 0.068665 | -0.10986 | 0.32044 | 0.096131 | 0.027466 | 0.21057 | 0.16937 | -0.054932 | -0.16479 | -0.34332 | -0.25177 | -0.19684 | -0.082397 | 121.2708 | 121.5912 | 82.6721 | -121.3119 | 121.2158 | 121.2982 | 81.7657 | -121.4355
641.5312 | 121.6782 | -84.8282 | 37.2299 | -0.012589 | 0.00016873 | 0.066896 | 0.001034 | 0.065193 | -0.0033495 | 0.00046566 | -0.0054932 | -0.0061929 | 0.064621 | 0.065687 | -0.19848 | -0.00048921 | 34.7031 | -86.4899 | 0.082397 | -86.7142 | 34.4467 | -86.9476 | -86.7737 | -87.1857 | -0.83771 | -87.0163 | 34.5108 | 34.5795 | -86.5631 | -86.7966 | -2.1194 | -1.9455 | -2.7832 | -1.6617 | -1.886 | 0.05951 | -2.5269 | -1.7349 | -1.9684 | -2.7191 | -2.3575 | -2.1881 | -0.21973 | -2.6505 | 119.2749 | 119.5312 | 84.9106 | -124.0036 | 119.339 | 119.4077 | 83.9905 | -124.0265
643.3125 | 121.7743 | -89.0854 | 32.2678 | -0.0049592 | 0.0029459 | 0.065614 | 0.002102 | 0.066689 | -0.0052721 | -0.0023113 | 0.0021363 | -0.0068337 | 0.064835 | 0.068891 | -0.20105 | -0.00027561 | 32.5012 | -88.678 | -0.032043 | -88.9709 | 32.1899 | -89.2273 | -89.035 | -89.4516 | -1.1719 | -89.2822 | 32.1304 | 32.2174 | -88.9114 | -89.1586 | -0.14191 | 0.050354 | -0.07782 | 0.40741 | 0.11444 | 0.064087 | 0.23346 | 0.17395 | -0.073242 | -0.13733 | -0.36621 | -0.19684 | -0.1236 | -0.050354 | 121.2753 | 121.5866 | 89.0533 | -121.3028 | 121.2158 | 121.3028 | 87.9135 | -121.4264
645.0781 | 121.7651 | -89.5111 | 31.8375 | -0.0049592 | 0.0031595 | 0.066255 | 0.001034 | 0.066689 | -0.0035633 | -0.0010297 | -0.0054932 | -0.0040567 | 0.067184 | 0.06761 | -0.20233 | -0.00091641 | 32.0663 | -89.1312 | -0.073242 | -89.4241 | 31.7734 | -89.6484 | -89.4608 | -89.8911 | -1.236 | -89.7263 | 31.7047 | 31.7551 | -89.3555 | -89.5935 | -0.13733 | 0.050354 | -0.064087 | 0.37994 | 0.086975 | 0.036621 | 0.22888 | 0.15564 | -0.082398 | -0.13275 | -0.37994 | -0.21515 | -0.13275 | -0.082397 | 121.2845 | 121.5775 | 89.4379 | -121.2982 | 121.2158 | 121.2662 | 88.2751 | -121.431
646.7969 | 121.6278 | -90.9256 | 30.5008 | -0.0049592 | 0.0093545 | 0.063905 | 0.0023156 | 0.067543 | 0.0060499 | 0.0030293 | -0.0054932 | 0.0014975 | 0.066971 | 0.069959 | -0.194 | -0.0030526 | 30.6885 | -90.5548 | -0.14648 | -90.8112 | 30.4367 | -91.0675 | -90.8432 | -91.2689 | -1.4053 | -91.2003 | 30.4001 | 30.4459 | -90.7516 | -90.976 | -0.14191 | 0.082397 | -0.064086 | 0.37079 | 0.11444 | 0.032044 | 0.18768 | 0.17395 | -0.050354 | -0.10071 | -0.34332 | -0.27466 | -0.2243 | -0.054931 | 121.3623 | 121.6141 | 90.7791 | -121.344 | 121.3257 | 121.3715 | 89.5203 | -121.4767
648.5156 | 121.7606 | -87.5702 | 33.8242 | -0.0049592 | 0.00038233 | 0.067751 | 0.00082022 | 0.066262 | -0.0044177 | 0.0017475 | -0.0054932 | -0.0036295 | 0.065475 | 0.067396 | -0.19912 | -0.0026254 | 34.0576 | -87.1262 | 0 | -87.4237 | 33.728 | -87.6801 | -87.4741 | -87.8906 | -1.1719 | -87.7441 | 33.696 | 33.7372 | -87.3734 | -87.616 | -0.10986 | 0.09613 | -0.096131 | 0.44403 | 0.14648 | 0.050354 | 0.23346 | 0.19684 | -0.045777 | -0.12817 | -0.32044 | -0.17395 | -0.12817 | -0.086975 | 121.2982 | 121.6278 | 87.5702 | -121.2982 | 121.2662 | 121.3074 | 86.3983 | -121.4401
650.2969 | 121.7239 | -97.6044 | 23.7488 | -0.0049592 | 0.0025185 | 0.063692 | 0.00082022 | 0.070107 | 0.00028207 | 0.0017475 | 0.0021363 | -0.0029885 | 0.064835 | 0.066969 | -0.19977 | 0.0010062 | 24.0372 | -97.1146 | -0.21973 | -97.403 | 23.7259 | -97.7234 | -97.4991 | -97.9706 | -1.799 | -97.8241 | 23.6755 | 23.7213 | -97.4075 | -97.6639 | -0.11902 | 0.10529 | -0.022888 | 0.48981 | 0.20142 | 0.09613 | 0.28839 | 0.19684 | -0.059509 | -0.073242 | -0.36621 | -0.21973 | -0.16022 | -0.027466 | 121.3303 | 121.6415 | 97.3846 | -121.2479 | 121.2799 | 121.3257 | 95.8054 | -121.4127
652.0625 | 121.6599 | -90.4449 | 30.9769 | -0.012589 | 0.0048685 | 0.064974 | 0.0016748 | 0.070107 | 0.0032727 | 0.0019611 | -0.013123 | 0.00021568 | 0.063553 | 0.0706 | -0.19571 | -0.0026254 | 31.1462 | -90.065 | -0.14648 | -90.3168 | 30.9357 | -90.5548 | -90.3763 | -90.7883 | -1.4648 | -90.6876 | 30.8762 | 30.9357 | -90.2435 | -90.4816 | -0.10986 | 0.068664 | -0.041199 | 0.37994 | 0.12817 | 0.05951 | 0.16937 | 0.20142 | -0.036621 | -0.10071 | -0.34332 | -0.24262 | -0.20599 | -0.041199 | 121.3806 | 121.5912 | 90.2985 | -121.3531 | 121.3211 | 121.3806 | 88.9801 | -121.4584
653.8281 | 121.6278 | -91.8594 | 29.5807 | -0.020218 | 0.0046549 | 0.065614 | -0.003025 | 0.067971 | 0.0043409 | 0.0028155 | 0.0021363 | 2.078e-06 | 0.063766 | 0.069959 | -0.19485 | -0.00070281 | 29.7226 | -91.5024 | -0.21973 | -91.7313 | 29.5898 | -91.9647 | -91.7725 | -92.2806 | -1.5976 | -92.1799 | 29.4846 | 29.5441 | -91.6397 | -91.8961 | -0.10529 | 0.086975 | 0.009156 | 0.35706 | 0.12817 | 0.041199 | 0.14191 | 0.21973 | -0.036621 | -0.09613 | -0.42114 | -0.32044 | -0.28381 | -0.036621 | 121.4493 | 121.582 | 91.6397 | -121.3531 | 121.344 | 121.4035 | 90.2618 | -121.4767
655.5312 | 121.5546 | -92.926 | 28.5004 | -0.0049592 | 0.01085 | 0.062624 | 0.001034 | 0.067971 | 0.0024183 | 0.0028155 | 0.0021363 | -0.0019205 | 0.066116 | 0.069105 | -0.19763 | -0.00113 | 28.6285 | -92.5598 | -0.1831 | -92.7933 | 28.3768 | -93.0679 | -92.8711 | -93.306 | -1.6205 | -93.2007 | 28.3447 | 28.418 | -92.7246 | -92.9626 | -0.14191 | 0.054931 | -0.1236 | 0.36621 | 0.13275 | 0.07782 | 0.12817 | 0.20142 | -0.036621 | -0.15564 | -0.37994 | -0.27466 | -0.23804 | -0.082397 | 121.3028 | 121.5546 | 92.7429 | -121.3715 | 121.2708 | 121.344 | 91.3055 | -121.463
657.2812 | 121.6827 | -43.5699 | 77.8702 | 0.0026703 | 0.0040139 | 0.063905 | -0.0019568 | 0.066902 | -0.0016405 | 0.00089286 | -0.013123 | -0.0038431 | 0.065048 | 0.06825 | -0.19784 | 0.001647 | 78.0167 | -43.4921 | 0.3067 | -43.5883 | 77.8336 | -43.4143 | -43.3868 | -43.8263 | 0.018311 | -43.8538 | 77.7557 | 77.861 | -43.2678 | -43.4418 | 0.15564 | 0.18311 | -0.036621 | 0.07782 | -0.018311 | -0.20142 | 0.14648 | 0.30212 | 0.12817 | -0.11444 | -0.25635 | -0.28381 | -0.41199 | -0.009155 | 121.4035 | 121.5866 | 43.8766 | -121.257 | 121.3257 | 121.431 | 43.5883 | -121.3119
659.0469 | 121.6415 | -43.6798 | 77.7466 | -0.0049592 | -0.00089927 | 0.068819 | 0.0025292 | 0.064553 | -0.0069811 | -0.0010297 | -0.0054932 | -0.0064065 | 0.064194 | 0.067823 | -0.20105 | 0.00079259 | 77.8061 | -43.6844 | 0.35248 | -43.7988 | 77.5681 | -43.6432 | -43.5928 | -44.0826 | 0.004578 | -44.0506 | 77.5269 | 77.6459 | -43.4967 | -43.6844 | 0.036622 | 0.086976 | -0.17853 | -0.004577 | -0.11902 | -0.20599 | 0.059509 | 0.18311 | -0.004577 | -0.21973 | -0.40283 | -0.37079 | -0.36621 | -0.10071 | 121.2479 | 121.4859 | 44.0323 | -121.3394 | 121.2067 | 121.3257 | 43.6844 | -121.431
660.75 | 121.5729 | -43.4784 | 78.0304 | 0.0026703 | 0.0012369 | 0.067537 | 0.0012476 | 0.06733 | -0.0039905 | 0.0019611 | -0.013123 | -0.0038431 | 0.065048 | 0.065901 | -0.19998 | -0.00091641 | 78.0121 | -43.4738 | 0.39368 | -43.5928 | 77.7603 | -43.5059 | -43.3868 | -43.8492 | 0.009155 | -43.84 | 77.7924 | 77.8748 | -43.3136 | -43.4372 | -0.027465 | 0.091553 | -0.27008 | 0.004578 | -0.11444 | -0.20599 | -0.018311 | 0.16479 | 0.041199 | -0.23804 | -0.37079 | -0.36163 | -0.40283 | -0.15564 | 121.2387 | 121.4905 | 43.8721 | -121.4172 | 121.2708 | 121.3531 | 43.4875 | -121.4676
662.5156 | 121.6644 | -41.5924 | 79.834 | -0.0049592 | 0.0033731 | 0.065187 | 0.00039302 | 0.067116 | 0.0043409 | 0.0019611 | 0.0021363 | -0.0029885 | 0.064194 | 0.06825 | -0.19656 | -0.0024118 | 79.8935 | -41.684 | 0.29755 | -41.7343 | 79.7653 | -41.6016 | -41.5466 | -41.9998 | -0.036621 | -42.0364 | 79.6967 | 79.7607 | -41.423 | -41.6107 | -0.009155 | 0.045776 | -0.068664 | -0.091553 | -0.14191 | -0.18768 | 0.05951 | 0.16937 | -0.018311 | -0.13733 | -0.40741 | -0.44403 | -0.42572 | -0.073242 | 121.3577 | 121.4859 | 41.89 | -121.3806 | 121.2891 | 121.3531 | 41.5558 | -121.4447
664.2969 | 121.7102 | -41.4276 | 79.9713 | -0.0049592 | 0.00080973 | 0.063265 | 0.0014612 | 0.063912 | 0.0030591 | 0.0034565 | -0.013123 | -0.0038431 | 0.065475 | 0.067823 | -0.19998 | -0.0019846 | 80.0583 | -41.5054 | 0.31128 | -41.5787 | 79.8798 | -41.4871 | -41.3956 | -41.7984 | 0.009155 | -41.8213 | 79.8203 | 79.9118 | -41.2628 | -41.4185 | -0.05951 | 0.032043 | -0.091552 | -0.07782 | -0.15106 | -0.1831 | 0.086976 | 0.1648 | 0.009155 | -0.15106 | -0.37079 | -0.39368 | -0.40283 | -0.059509 | 121.3074 | 121.4859 | 41.7389 | -121.3669 | 121.2479 | 121.3394 | 41.4368 | -121.3898
666 | 121.7239 | -42.2699 | 79.1336 | 0.0026703 | 0.0040139 | 0.067751 | 0.001034 | 0.065621 | -0.0054859 | -0.00038874 | -0.0054932 | -0.0040567 | 0.062057 | 0.06526 | -0.19955 | 0.00057899 | 79.2023 | -42.334 | 0.35706 | -42.4118 | 78.9734 | -42.3203 | -42.2195 | -42.659 | -0.036621 | -42.6498 | 78.9505 | 79.0649 | -42.1097 | -42.2745 | -0.050354 | 0.050354 | -0.16022 | -0.064087 | -0.14191 | -0.19226 | 0.068665 | 0.16022 | -0.004578 | -0.18311 | -0.3891 | -0.37994 | -0.37537 | -0.068665 | 121.2433 | 121.4722 | 42.627 | -121.3531 | 121.2204 | 121.3348 | 42.2333 | -121.4081
667.7812 | 121.6599 | -37.7884 | 83.6517 | 0.0026703 | 0.00016873 | 0.067537 | -0.00024778 | 0.066902 | -0.0029223 | -0.0014569 | 0.0021363 | -0.0051247 | 0.063766 | 0.065901 | -0.19998 | -0.002839 | 83.7799 | -37.7655 | 0.47607 | -37.8845 | 83.4961 | -37.8067 | -37.738 | -38.118 | 0.12817 | -38.118 | 83.4274 | 83.5373 | -37.6373 | -37.7701 | -0.018311 | 0.050354 | -0.15564 | 0.022888 | -0.09613 | -0.14648 | 0.12817 | 0.15106 | 0.01831 | -0.2243 | -0.32959 | -0.32959 | -0.3479 | -0.11444 | 121.2845 | 121.5683 | 38.2645 | -121.3898 | 121.2158 | 121.3257 | 37.9166 | -121.4218
669.4688 | 121.6919 | -44.1376 | 77.2705 | -0.0049592 | 0.0010233 | 0.063905 | 0.001034 | 0.065834 | -0.0016405 | 0.0013203 | 0.0021363 | -0.00085232 | 0.064621 | 0.068891 | -0.19784 | -0.0015572 | 77.4078 | -44.1284 | 0.39825 | -44.2566 | 77.1057 | -44.1742 | -44.101 | -44.5084 | -0.045776 | -44.4809 | 77.0599 | 77.1561 | -44.014 | -44.165 | -0.036621 | 0.036621 | -0.1648 | 0.009155 | -0.11902 | -0.15564 | 0.13733 | 0.1236 | -0.027466 | -0.21057 | -0.37079 | -0.34332 | -0.31586 | -0.11444 | 121.2433 | 121.5454 | 44.5358 | -121.3715 | 121.1975 | 121.2936 | 44.0918 | -121.4355
671.2344 | 121.6553 | -45.4102 | 76.0437 | -0.0049592 | 0.0040139 | 0.065401 | 0.0033838 | 0.066902 | 0.0013501 | -0.00081594 | -0.0054932 | -0.00042512 | 0.065689 | 0.068678 | -0.19784 | -0.0030526 | 76.149 | -45.401 | 0.39825 | -45.4971 | 75.9888 | -45.4239 | -45.3415 | -45.7809 | -0.086975 | -45.8038 | 75.9338 | 76.0117 | -45.2362 | -45.3918 | -0.013733 | 0.068664 | -0.054931 | 0.009155 | -0.086975 | -0.15564 | 0.10529 | 0.17395 | 0.01831 | -0.10986 | -0.37079 | -0.39368 | -0.41199 | -0.032043 | 121.3989 | 121.5591 | 45.8084 | -121.3852 | 121.344 | 121.4218 | 45.3232 | -121.4355
672.9375 | 121.7422 | -42.2379 | 79.1565 | 0.0026703 | 0.0016641 | 0.066683 | 0.0014612 | 0.067543 | -0.0042041 | -0.00017514 | -0.0054932 | -0.0036295 | 0.065475 | 0.067396 | -0.20147 | -0.0026254 | 79.303 | -42.2241 | 0.35248 | -42.3386 | 79.097 | -42.2058 | -42.16 | -42.5812 | -0.054932 | -42.5629 | 79.0146 | 79.1061 | -42.0685 | -42.215 | 0.032043 | 0.07782 | -0.059509 | 0.013733 | -0.10071 | -0.17853 | 0.14648 | 0.16937 | 0.022888 | -0.14191 | -0.34332 | -0.32501 | -0.3479 | -0.050354 | 121.3348 | 121.5408 | 42.5903 | -121.3165 | 121.2524 | 121.344 | 42.1829 | -121.3715
674.7031 | 121.7239 | -42.7368 | 78.6438 | -0.0049592 | 0.00080973 | 0.06476 | -0.002384 | 0.066475 | 0.0047681 | 0.00089286 | -0.013123 | -0.0014933 | 0.064407 | 0.068891 | -0.19592 | -0.0024118 | 78.7537 | -42.8329 | 0.32501 | -42.9016 | 78.5751 | -42.8101 | -42.7277 | -43.1488 | -0.10529 | -43.1854 | 78.511 | 78.5889 | -42.627 | -42.7734 | -0.073243 | 0.009155 | -0.068665 | -0.096131 | -0.1648 | -0.17395 | 0.10986 | 0.10986 | -0.036621 | -0.13275 | -0.41199 | -0.44861 | -0.41199 | -0.054932 | 121.3119 | 121.4905 | 43.0618 | -121.3715 | 121.2479 | 121.3257 | 42.6315 | -121.4172
676.3906 | 121.7194 | -42.3294 | 79.0787 | -0.0049592 | -0.0015403 | 0.067964 | 0.00039302 | 0.066262 | -0.0020679 | 0.0015339 | 0.0021363 | -0.0034159 | 0.06163 | 0.067182 | -0.20105 | -0.00113 | 79.1931 | -42.3614 | 0.39368 | -42.4667 | 78.9276 | -42.366 | -42.3019 | -42.7505 | -0.059509 | -42.7231 | 78.8773 | 79.0237 | -42.215 | -42.3477 | -0.036621 | 0.027466 | -0.15106 | -0.032043 | -0.13733 | -0.16479 | 0.11444 | 0.11444 | -0.01831 | -0.20142 | -0.42114 | -0.39368 | -0.37537 | -0.054931 | 121.257 | 121.5225 | 42.7231 | -121.3806 | 121.2067 | 121.3531 | 42.2699 | -121.4264
678.1562 | 121.6461 | -42.2836 | 79.1977 | -0.0049592 | 0.0042275 | 0.065401 | 0.0029566 | 0.064766 | 0.0024183 | -0.00038874 | 0.0021363 | -0.0019205 | 0.065903 | 0.067823 | -0.19934 | -0.004548 | 79.3076 | -42.2928 | 0.41199 | -42.3569 | 79.1107 | -42.2699 | -42.1921 | -42.6361 | -0.068665 | -42.6682 | 79.097 | 79.2068 | -42.1005 | -42.2287 | 0.013733 | 0.091552 | -0.086975 | -0.009156 | -0.073243 | -0.16479 | 0.10986 | 0.18311 | 0.054931 | -0.10071 | -0.35248 | -0.38452 | -0.43945 | 0.009155 | 121.3943 | 121.5912 | 42.6956 | -121.3898 | 121.3806 | 121.4905 | 42.215 | -121.4264
679.9531 | 121.669 | -41.5466 | 79.9164 | -0.012589 | 0.0057229 | 0.064119 | 0.001034 | 0.067116 | 0.0017773 | 0.0028155 | -0.0054932 | -0.00021152 | 0.06868 | 0.068678 | -0.19656 | -0.0026254 | 79.9942 | -41.5924 | 0.48981 | -41.6336 | 79.7974 | -41.5512 | -41.478 | -41.89 | 0.027466 | -41.9403 | 79.7516 | 79.8248 | -41.3864 | -41.5512 | -0.004577 | 0.068665 | -0.11902 | -0.045776 | -0.086975 | -0.15564 | 0.07782 | 0.16022 | -0.004577 | -0.16479 | -0.34332 | -0.39368 | -0.3891 | -0.091553 | 121.344 | 121.5408 | 42.0364 | -121.3943 | 121.2982 | 121.3715 | 41.5741 | -121.4676
681.6562 | 121.7285 | -41.4642 | 79.9576 | -0.012589 | 0.0027323 | 0.063478 | 0.002102 | 0.066475 | -0.0039905 | 0.00067926 | 0.0021363 | -0.0034159 | 0.061844 | 0.066755 | -0.19977 | -0.00048921 | 80.127 | -41.3864 | 0.55389 | -41.5329 | 79.7882 | -41.4917 | -41.4185 | -41.7755 | 0.10529 | -41.7801 | 79.7562 | 79.8889 | -41.3177 | -41.4551 | -0.027466 | 0.045776 | -0.16937 | 0.077819 | -0.068665 | -0.11444 | 0.16937 | 0.14648 | 0.009155 | -0.20142 | -0.31128 | -0.31586 | -0.32501 | -0.068665 | 121.2524 | 121.5912 | 42.0181 | -121.376 | 121.2204 | 121.3531 | 41.5695 | -121.4127
683.4219 | 121.6415 | -40.3427 | 81.1478 | 0.0026703 | 0.00059593 | 0.065187 | 0.0016748 | 0.066475 | 0.0030591 | -0.00038874 | -0.0054932 | -0.0012795 | 0.066116 | 0.068464 | -0.20019 | -0.0026254 | 81.1935 | -40.3839 | 0.44861 | -40.448 | 81.0654 | -40.3473 | -40.2832 | -40.7318 | 0.009155 | -40.7455 | 81.015 | 81.1111 | -40.1688 | -40.3198 | -0.004578 | 0.059509 | -0.082397 | -0.041199 | -0.10529 | -0.16479 | 0.045776 | 0.17395 | 0.022888 | -0.13275 | -0.3891 | -0.40283 | -0.42572 | -0.036621 | 121.4081 | 121.5363 | 40.7913 | -121.431 | 121.3577 | 121.4539 | 40.3519 | -121.4676
685.1875 | 121.756 | -47.0764 | 74.2676 | 0.0026703 | 0.0025185 | 0.064119 | -0.00088858 | 0.067757 | 0.0013501 | 0.0021747 | -0.0054932 | -0.0040567 | 0.065262 | 0.066328 | -0.1972 | -0.0015572 | 74.4781 | -47.0673 | 0.37994 | -47.168 | 74.1623 | -47.1634 | -47.0489 | -47.4152 | -0.17853 | -47.4289 | 74.1119 | 74.2264 | -46.962 | -47.1085 | -0.086975 | 0.027466 | -0.10529 | 0.009155 | -0.091553 | -0.11902 | 0.21057 | 0.11444 | -0.032043 | -0.15564 | -0.33874 | -0.35248 | -0.32043 | -0.041199 | 121.2387 | 121.5546 | 47.4564 | -121.3165 | 121.1884 | 121.3028 | 46.8979 | -121.376
686.9531 | 121.6278 | -46.6095 | 74.8672 | -0.0049592 | 0.0016641 | 0.066042 | 0.0027428 | 0.066475 | -0.00014533 | -0.0016705 | -0.013123 | -0.0012795 | 0.06633 | 0.066969 | -0.20169 | -0.0015572 | 74.9176 | -46.6187 | 0.40283 | -46.7285 | 74.7208 | -46.6461 | -46.5729 | -47.0261 | -0.18768 | -47.0215 | 74.6841 | 74.8169 | -46.4584 | -46.6278 | -0.036621 | 0.036621 | -0.14648 | -0.009155 | -0.11902 | -0.15564 | 0.050354 | 0.15106 | -0.018311 | -0.18311 | -0.41657 | -0.41199 | -0.39368 | -0.050354 | 121.3303 | 121.5271 | 47.0123 | -121.4401 | 121.2936 | 121.4264 | 46.4218 | -121.4951
688.6719 | 121.6644 | -46.7056 | 74.762 | -0.012589 | 0.0023049 | 0.068391 | 0.00082022 | 0.067971 | 6.8274e-05 | 0.0013203 | -0.020752 | -0.00021152 | 0.063553 | 0.06761 | -0.19848 | -0.0019846 | 74.8444 | -46.7148 | 0.42572 | -46.7972 | 74.6841 | -46.7239 | -46.6644 | -47.081 | -0.15564 | -47.113 | 74.6384 | 74.7208 | -46.5317 | -46.6965 | -0.018311 | 0.041198 | -0.07782 | -0.009156 | -0.091553 | -0.13275 | 0.082397 | 0.17395 | 0.009155 | -0.1236 | -0.37537 | -0.40741 | -0.41656 | -0.041199 | 121.3898 | 121.55 | 47.1313 | -121.4264 | 121.344 | 121.4264 | 46.55 | -121.4584
690.4375 | 121.6141 | -45.5795 | 75.8972 | -0.012589 | 0.0046549 | 0.062624 | 0.00060662 | 0.067543 | 0.0054089 | 0.0030293 | -0.0054932 | -0.0019205 | 0.065689 | 0.068464 | -0.19699 | -0.0013436 | 75.9888 | -45.5887 | 0.35706 | -45.6757 | 75.7965 | -45.5933 | -45.52 | -45.9274 | -0.22888 | -46.0052 | 75.7416 | 75.8698 | -45.3918 | -45.5841 | -0.013733 | 0.059509 | -0.10071 | -0.009155 | -0.09613 | -0.15564 | 0.091553 | 0.18768 | -0.004577 | -0.15564 | -0.3479 | -0.42572 | -0.42114 | -0.027466 | 121.376 | 121.5683 | 45.9366 | -121.4172 | 121.3211 | 121.4493 | 45.3506 | -121.4813
692.1875 | 121.6003 | -44.1696 | 77.3254 | -0.012589 | -0.0032493 | 0.063692 | -3.4178e-05 | 0.067543 | -0.0048449 | -0.0014569 | -0.020752 | -0.0051247 | 0.062271 | 0.069532 | -0.19977 | -0.00027561 | 77.4353 | -44.0781 | 0.52185 | -44.1971 | 77.1606 | -44.1605 | -44.0826 | -44.4809 | -0.064087 | -44.4901 | 77.1286 | 77.243 | -43.9636 | -44.1422 | 0.009156 | 0.086975 | -0.16479 | 0.091553 | -0.027466 | -0.11444 | 0.10986 | 0.20599 | 0.027466 | -0.19684 | -0.31128 | -0.32043 | -0.3479 | -0.082397 | 121.3303 | 121.6049 | 44.6915 | -121.4081 | 121.2982 | 121.4127 | 44.1055 | -121.4676
693.8906 | 121.756 | -42.9199 | 78.5019 | -0.0049592 | 0.00038233 | 0.06946 | -0.0011024 | 0.066262 | -0.0039905 | 0.00089286 | 0.0021363 | -0.0036295 | 0.063766 | 0.064619 | -0.19848 | -0.00070281 | 78.598 | -42.9245 | 0.43488 | -43.0115 | 78.4012 | -42.9337 | -42.8513 | -43.2861 | -0.073242 | -43.2312 | 78.3463 | 78.4287 | -42.7597 | -42.8833 | -0.013733 | 0.068665 | -0.10071 | -0.004578 | -0.091553 | -0.16022 | 0.09613 | 0.16022 | 0.036621 | -0.15564 | -0.36621 | -0.31128 | -0.3479 | -0.073242 | 121.3211 | 121.5179 | 43.3548 | -121.3531 | 121.2662 | 121.3486 | 42.8467 | -121.3852
695.6562 | 121.6187 | -41.2354 | 80.278 | -0.0049592 | 0.0023049 | 0.065828 | 0.00060662 | 0.06498 | 6.8274e-05 | -0.0014569 | -0.0054932 | -0.0046975 | 0.064621 | 0.067182 | -0.19891 | -0.00070281 | 80.3284 | -41.2582 | 0.4715 | -41.3406 | 80.1498 | -41.217 | -41.185 | -41.6061 | -0.054932 | -41.6199 | 80.0949 | 80.2048 | -41.0568 | -41.2216 | 0.018311 | 0.050354 | -0.12817 | -0.022888 | -0.10529 | -0.15564 | 0.050354 | 0.17853 | 0.013733 | -0.1831 | -0.37079 | -0.38452 | -0.39825 | -0.073242 | 121.3852 | 121.5637 | 41.7068 | -121.463 | 121.3303 | 121.4401 | 41.1804 | -121.4996
697.4219 | 121.6873 | -38.4979 | 82.9834 | -0.0049592 | -0.0017539 | 0.066042 | -0.0036658 | 0.067971 | -0.0035633 | -0.00017514 | -0.0054932 | -0.0038431 | 0.062698 | 0.067182 | -0.20062 | -0.0013436 | 83.0704 | -38.5208 | 0.49896 | -38.5986 | 82.8186 | -38.4933 | -38.4338 | -38.8596 | 0.027466 | -38.8641 | 82.7774 | 82.869 | -38.324 | -38.4842 | 0.004578 | 0.064087 | -0.16479 | -0.022888 | -0.10071 | -0.16479 | 0.086976 | 0.17395 | 0.013733 | -0.20599 | -0.36163 | -0.36621 | -0.37994 | -0.11444 | 121.3165 | 121.5683 | 38.9969 | -121.4172 | 121.2753 | 121.3669 | 38.5254 | -121.4676
699.1875 | 121.6827 | -35.5728 | 85.8948 | -0.0049592 | 0.0042275 | 0.067323 | 0.002102 | 0.067543 | -0.00057253 | 0.0023883 | 0.0021363 | -0.0040567 | 0.06633 | 0.067182 | -0.20318 | -0.0021982 | 85.9818 | -35.6094 | 0.56763 | -35.6873 | 85.7712 | -35.5362 | -35.5087 | -35.9299 | 0.15106 | -35.9299 | 85.7025 | 85.7895 | -35.3989 | -35.5453 | 0.036621 | 0.064087 | -0.1236 | -0.036621 | -0.11444 | -0.17853 | 0.086975 | 0.17395 | 0.027466 | -0.19226 | -0.35706 | -0.35706 | -0.38452 | -0.10528 | 121.344 | 121.5546 | 36.1404 | -121.4035 | 121.2753 | 121.3623 | 35.7239 | -121.4401
700.9531 | 121.7056 | -33.7692 | 87.7075 | -0.0049592 | 0.00016873 | 0.066042 | -0.0025976 | 0.063057 | 0.00070927 | 0.0011067 | 0.0021363 | -0.0023477 | 0.063766 | 0.066328 | -0.19763 | -0.0036936 | 87.8403 | -33.7738 | 0.59052 | -33.8654 | 87.5381 | -33.7555 | -33.7097 | -34.0485 | 0.26093 | -34.0897 | 87.4924 | 87.5748 | -33.577 | -33.7418 | 0.013733 | 0.059509 | -0.16937 | -0.004578 | -0.09613 | -0.15564 | 0.13275 | 0.19226 | 0.027466 | -0.21515 | -0.27924 | -0.32043 | -0.3479 | -0.13275 | 121.3074 | 121.6095 | 34.3597 | -121.4172 | 121.2616 | 121.344 | 34.0302 | -121.4493
702.6562 | 121.6141 | -32.4783 | 89.0396 | 0.0103 | 0.0061501 | 0.06476 | 0.00060662 | 0.065834 | 0.0047681 | 0.0036701 | -0.0054932 | 0.00085668 | 0.065262 | 0.067396 | -0.19485 | -0.0047616 | 89.122 | -32.5378 | 0.65002 | -32.5836 | 88.8931 | -32.4417 | -32.4097 | -32.7805 | 0.33875 | -32.8537 | 88.8428 | 88.9435 | -32.2952 | -32.46 | 0.036622 | 0.068665 | -0.14648 | -0.059509 | -0.10529 | -0.17395 | 0.082397 | 0.18311 | 0.018311 | -0.19684 | -0.30212 | -0.37537 | -0.39368 | -0.096131 | 121.3715 | 121.6003 | 33.1284 | -121.4493 | 121.3211 | 121.4218 | 32.8171 | -121.4996
704.4219 | 121.7285 | -32.4005 | 89.0533 | -0.0049592 | -0.0013267 | 0.066469 | 0.0040246 | 0.062844 | -0.0048449 | -0.0012433 | -0.0054932 | -0.0051247 | 0.064407 | 0.065901 | -0.20126 | 0.00057899 | 89.09 | -32.5104 | 0.60883 | -32.5653 | 88.8794 | -32.4005 | -32.3868 | -32.7805 | 0.27924 | -32.7759 | 88.829 | 88.9389 | -32.2769 | -32.4142 | 0 | 0.013733 | -0.17395 | -0.10986 | -0.1648 | -0.17853 | 0.036621 | 0.1236 | -0.013733 | -0.2243 | -0.37994 | -0.37537 | -0.36163 | -0.11444 | 121.2799 | 121.4905 | 33.0093 | -121.4401 | 121.2296 | 121.3394 | 32.6797 | -121.4676
706.125 | 121.6553 | -31.7322 | 89.7995 | -0.0049592 | 0.0033731 | 0.066896 | 0.002102 | 0.068398 | 0.00092287 | 0.00067926 | -0.0054932 | -0.00042512 | 0.06633 | 0.066328 | -0.19955 | -0.0030526 | 89.8087 | -31.8512 | 0.6134 | -31.8604 | 89.653 | -31.7001 | -31.6635 | -32.0938 | 0.29755 | -32.1259 | 89.6393 | 89.6896 | -31.5857 | -31.6956 | 0.032044 | 0.068665 | -0.14648 | -0.11902 | -0.12817 | -0.19684 | 0.009155 | 0.14649 | 0.036621 | -0.16022 | -0.36163 | -0.39368 | -0.4303 | -0.10986 | 121.3852 | 121.5408 | 32.3456 | -121.463 | 121.3715 | 121.4218 | 32.0297 | -121.4951
707.8906 | 121.6782 | -30.8716 | 90.5914 | -0.0049592 | -0.0011131 | 0.065187 | 0.00039302 | 0.065193 | -0.0035633 | 3.8456e-05 | 0.0097658 | -0.0036295 | 0.066971 | 0.06825 | -0.1987 | -0.002839 | 90.6921 | -30.9128 | 0.6546 | -30.9998 | 90.4175 | -30.8441 | -30.8304 | -31.1966 | 0.35706 | -31.2241 | 90.3625 | 90.477 | -30.7297 | -30.8578 | 0.027466 | 0.041199 | -0.17395 | -0.041199 | -0.12817 | -0.16937 | 0.10071 | 0.14191 | 0.013733 | -0.22888 | -0.32501 | -0.35248 | -0.36621 | -0.11444 | 121.2891 | 121.5637 | 31.5262 | -121.4218 | 121.2341 | 121.3486 | 31.2286 | -121.4493
709.6562 | 121.637 | -28.9444 | 92.5827 | -0.0049592 | -0.0015403 | 0.066683 | 0.00082022 | 0.065407 | -0.00057253 | -0.0010297 | 0.017395 | -0.0042703 | 0.063766 | 0.065473 | -0.19891 | -0.001771 | 92.688 | -28.9215 | 0.78278 | -28.9993 | 92.4362 | -28.8849 | -28.8574 | -29.2145 | 0.53558 | -29.2465 | 92.3676 | 92.4683 | -28.775 | -28.8712 | 0.059509 | 0.086975 | -0.14648 | 0.022888 | -0.054932 | -0.14191 | 0.10529 | 0.16937 | 0.073242 | -0.21515 | -0.27008 | -0.30212 | -0.37537 | -0.11444 | 121.3806 | 121.6324 | 29.7272 | -121.4401 | 121.312 | 121.4127 | 29.48 | -121.4539
711.3594 | 121.6507 | -28.0014 | 93.4982 | 0.0026703 | 0.0048685 | 0.063905 | 0.0012476 | 0.065407 | 0.0041273 | 0.0019611 | -0.0054932 | -0.0012795 | 0.064835 | 0.069319 | -0.1987 | -0.0054026 | 93.5852 | -28.1067 | 0.74616 | -28.125 | 93.4067 | -27.9602 | -27.9602 | -28.3081 | 0.54474 | -28.3997 | 93.3197 | 93.4113 | -27.8549 | -27.9694 | 0.041199 | 0.041199 | -0.091553 | -0.10528 | -0.1236 | -0.1648 | 0.086975 | 0.14649 | 0.032044 | -0.17853 | -0.3067 | -0.39825 | -0.4303 | -0.086975 | 121.4081 | 121.5866 | 28.7476 | -121.4584 | 121.3211 | 121.4127 | 28.5461 | -121.4676
713.125 | 121.6232 | -27.1408 | 94.3726 | -0.0049592 | 0.0033731 | 0.064546 | 0.0012476 | 0.069039 | 0.0019909 | 0.0021747 | 0.0021363 | -0.00021152 | 0.064835 | 0.066755 | -0.19592 | -0.0015572 | 94.4641 | -27.2003 | 0.7782 | -27.2507 | 94.2352 | -27.1225 | -27.0905 | -27.4246 | 0.59967 | -27.5208 | 94.194 | 94.281 | -26.9714 | -27.1042 | 0.01831 | 0.050354 | -0.13733 | -0.059509 | -0.10986 | -0.16022 | 0.091552 | 0.16937 | 0.036621 | -0.17853 | -0.28381 | -0.37994 | -0.41657 | -0.091553 | 121.376 | 121.6049 | 27.919 | -121.463 | 121.3348 | 121.4218 | 27.7405 | -121.4767
714.9062 | 121.6827 | -25.8591 | 95.6131 | -0.012589 | 0.0059365 | 0.064974 | -3.4178e-05 | 0.065834 | 0.0013501 | 0.0023883 | 0.0021363 | -0.0017069 | 0.062912 | 0.06761 | -0.19656 | -0.00113 | 95.6268 | -26.0605 | 0.67749 | -26.0559 | 95.5032 | -25.8865 | -25.8499 | -26.2573 | 0.54932 | -26.3351 | 95.4529 | 95.5536 | -25.7309 | -25.8545 | -0.027466 | 0.009155 | -0.10986 | -0.20142 | -0.19684 | -0.20599 | 0.013733 | 0.12817 | 0.004578 | -0.16022 | -0.39825 | -0.47607 | -0.48065 | -0.059509 | 121.3623 | 121.4859 | 26.5366 | -121.463 | 121.312 | 121.4127 | 26.4084 | -121.4676
716.5938 | 121.7422 | -24.646 | 96.7987 | 0.0026703 | -0.0047445 | 0.06711 | 0.0012476 | 0.064766 | -0.0061267 | 0.00046566 | 0.0021363 | -0.0066201 | 0.062912 | 0.068678 | -0.20233 | 0.0018606 | 96.904 | -24.7238 | 0.83313 | -24.7742 | 96.6797 | -24.6185 | -24.6094 | -24.9527 | 0.74616 | -24.9664 | 96.6019 | 96.7529 | -24.4812 | -24.6094 | 0.027466 | 0.036621 | -0.11902 | -0.07782 | -0.12817 | -0.1648 | 0.10529 | 0.1648 | 0.036621 | -0.19684 | -0.3067 | -0.32043 | -0.35706 | -0.045776 | 121.3257 | 121.55 | 25.4791 | -121.4081 | 121.2479 | 121.3989 | 25.3922 | -121.4081
718.3438 | 121.669 | -25.1633 | 96.3364 | -0.012589 | 0.0063639 | 0.064119 | 0.0033838 | 0.065621 | 0.0036999 | 0.0011067 | -0.013123 | -0.0010659 | 0.064407 | 0.06825 | -0.19955 | -0.0030526 | 96.3867 | -25.3098 | 0.80566 | -25.296 | 96.2311 | -25.145 | -25.145 | -25.4745 | 0.70496 | -25.5569 | 96.1533 | 96.2906 | -25.0351 | -25.1221 | 0.018311 | 0.018311 | -0.10529 | -0.14648 | -0.13275 | -0.15106 | 0.050354 | 0.12817 | 0.041199 | -0.18311 | -0.31128 | -0.39368 | -0.43488 | -0.045777 | 121.3943 | 121.55 | 25.9689 | -121.4813 | 121.3165 | 121.4539 | 25.8682 | -121.4584
720.0938 | 121.6049 | -24.614 | 96.936 | -0.012589 | 0.0057229 | 0.067537 | 0.0016748 | 0.065621 | 6.8274e-05 | -0.00017514 | -0.0054932 | -0.0019205 | 0.065475 | 0.065901 | -0.19998 | -0.0015572 | 96.9269 | -24.733 | 0.83771 | -24.7513 | 96.7987 | -24.5499 | -24.5499 | -24.9573 | 0.70496 | -25.0122 | 96.7438 | 96.8628 | -24.4675 | -24.5911 | 0.064087 | 0.064087 | -0.13733 | -0.11902 | -0.13733 | -0.20142 | -0.009155 | 0.14648 | 0.022889 | -0.19226 | -0.34332 | -0.39825 | -0.42114 | -0.073242 | 121.4127 | 121.5408 | 25.4517 | -121.4859 | 121.3577 | 121.4767 | 25.3189 | -121.5271
721.7969 | 121.701 | -24.1013 | 97.3892 | -0.0049592 | 0.0033731 | 0.06711 | 0.0023156 | 0.067116 | -0.0046313 | -0.00081594 | -0.0054932 | -0.0029885 | 0.066757 | 0.065473 | -0.20062 | -0.001771 | 97.4487 | -24.1699 | 0.85144 | -24.2294 | 97.229 | -24.0829 | -24.0509 | -24.3988 | 0.72784 | -24.4446 | 97.1512 | 97.2931 | -23.9594 | -24.0692 | 0.01831 | 0.050354 | -0.16022 | -0.068665 | -0.12817 | -0.17853 | 0.059509 | 0.14191 | 0.032043 | -0.23804 | -0.29755 | -0.34332 | -0.37537 | -0.09613 | 121.3303 | 121.55 | 24.9527 | -121.4401 | 121.2524 | 121.3943 | 24.8291 | -121.4584
723.5625 | 121.6827 | -29.1504 | 92.3767 | 0.0026703 | 0.0070047 | 0.063265 | 0.0033838 | 0.069252 | 0.0024183 | -0.00060234 | -0.0054932 | 0.0010703 | 0.065689 | 0.066969 | -0.19827 | -0.0032662 | 92.4179 | -29.2831 | 0.78278 | -29.2831 | 92.2165 | -29.1641 | -29.1321 | -29.4571 | 0.53558 | -29.5349 | 92.1799 | 92.276 | -29.0039 | -29.1229 | -0.013733 | 0.018311 | -0.16022 | -0.13275 | -0.13275 | -0.15106 | 0.041199 | 0.14648 | 0.027466 | -0.19684 | -0.3067 | -0.38452 | -0.41199 | -0.10071 | 121.3669 | 121.5683 | 29.9332 | -121.5088 | 121.3303 | 121.4264 | 29.686 | -121.4996
725.25 | 121.7194 | -27.5665 | 93.8828 | -0.0049592 | 0.0012369 | 0.06476 | -0.0011024 | 0.063484 | -0.00057253 | 0.0023883 | -0.0054932 | -0.0014933 | 0.065262 | 0.069105 | -0.19763 | -0.001771 | 93.9194 | -27.7771 | 0.69122 | -27.7771 | 93.7912 | -27.594 | -27.6169 | -27.951 | 0.47607 | -28.0151 | 93.718 | 93.8187 | -27.4429 | -27.594 | -0.027466 | -0.050354 | -0.091552 | -0.21057 | -0.21057 | -0.16022 | 0.036622 | 0.1236 | -0.027466 | -0.16479 | -0.38452 | -0.44861 | -0.42114 | -0.064086 | 121.3577 | 121.4859 | 28.2578 | -121.4996 | 121.2845 | 121.3852 | 28.0426 | -121.4767
727 | 121.6278 | -28.9124 | 92.6147 | -0.012589 | 0.0025185 | 0.063692 | -0.0019568 | 0.066902 | 0.0041273 | 0.0013203 | -0.013123 | -0.0017069 | 0.065048 | 0.068464 | -0.19763 | 0.001647 | 92.5873 | -29.0543 | 0.68207 | -29.0726 | 92.4866 | -28.9032 | -28.8574 | -29.2648 | 0.42572 | -29.3701 | 92.4637 | 92.5507 | -28.7567 | -28.8803 | 0.009156 | 0.054932 | -0.12817 | -0.14191 | -0.16022 | -0.21515 | -0.027466 | 0.15564 | 0.032044 | -0.15106 | -0.35248 | -0.45776 | -0.48981 | -0.064087 | 121.3989 | 121.4996 | 29.5944 | -121.4722 | 121.376 | 121.463 | 29.3381 | -121.4951
728.7656 | 121.6873 | -24.0692 | 97.4304 | 0.0026703 | 0.0038003 | 0.066896 | 0.0027428 | 0.066262 | -0.0071947 | 0.00046566 | 0.0021363 | -0.0051247 | 0.06633 | 0.067182 | -0.19955 | -0.00070281 | 97.467 | -24.1196 | 0.88348 | -24.1791 | 97.2153 | -24.0784 | -24.0326 | -24.3347 | 0.76904 | -24.3896 | 97.1787 | 97.3068 | -23.9182 | -24.0372 | -0.009155 | 0.036621 | -0.21515 | -0.050354 | -0.10986 | -0.14648 | 0.036621 | 0.15106 | 0.032044 | -0.25177 | -0.2655 | -0.32043 | -0.35248 | -0.1236 | 121.2845 | 121.5363 | 24.9527 | -121.463 | 121.2479 | 121.376 | 24.8383 | -121.4676
730.4688 | 121.7377 | -18.837 | 102.6627 | -0.0049592 | 0.0038003 | 0.06476 | 0.0012476 | 0.067116 | 0.00092287 | 0.00046566 | 0.0021363 | -0.0036295 | 0.065262 | 0.067823 | -0.19806 | -0.00070281 | 102.7039 | -18.9651 | 0.95215 | -18.9423 | 102.5391 | -18.7866 | -18.7866 | -19.0521 | 1.0803 | -19.1528 | 102.4704 | 102.5436 | -18.6768 | -18.7592 | 0.050354 | 0.050354 | -0.1236 | -0.12817 | -0.10529 | -0.15564 | 0.041198 | 0.16022 | 0.07782 | -0.19226 | -0.21515 | -0.31586 | -0.39368 | -0.11902 | 121.376 | 121.5408 | 19.7891 | -121.4493 | 121.3074 | 121.3806 | 19.9173 | -121.4218
732.25 | 121.6827 | -17.0975 | 104.4205 | -0.012589 | 0.0023049 | 0.066469 | 0.0050928 | 0.065834 | -0.0042041 | 0.00067926 | 0.0097658 | -0.0046975 | 0.066116 | 0.068037 | -0.20041 | -0.0015572 | 104.4983 | -17.0883 | 1.1169 | -17.1341 | 104.2511 | -17.0288 | -17.038 | -17.276 | 1.2863 | -17.3264 | 104.2191 | 104.3152 | -16.9373 | -17.0151 | 0.068664 | 0.059509 | -0.16937 | 0.009155 | -0.036621 | -0.09613 | 0.07782 | 0.16022 | 0.082397 | -0.20142 | -0.17853 | -0.22888 | -0.31128 | -0.10529 | 121.3486 | 121.5958 | 18.2144 | -121.4584 | 121.3165 | 121.4127 | 18.3838 | -121.4355
733.9531 | 121.6553 | -17.9626 | 103.5919 | -0.012589 | 0.0048685 | 0.063478 | 0.00039302 | 0.06498 | 0.0045545 | 0.00089286 | -0.0054932 | 0.00064308 | 0.065903 | 0.070173 | -0.19592 | -0.0066842 | 103.624 | -18.0634 | 1.0574 | -18.0496 | 103.4592 | -17.9306 | -17.9169 | -18.187 | 1.2268 | -18.3014 | 103.3813 | 103.4866 | -17.8207 | -17.9077 | 0.032043 | 0.045776 | -0.13275 | -0.10071 | -0.086976 | -0.13275 | 0.032043 | 0.14191 | 0.054931 | -0.21057 | -0.22431 | -0.33875 | -0.39368 | -0.10529 | 121.4218 | 121.5866 | 19.0201 | -121.5088 | 121.344 | 121.4493 | 19.1895 | -121.4996
735.7188 | 121.7102 | -24.7787 | 96.698 | -0.012589 | -0.00047207 | 0.066255 | -0.00046138 | 0.066262 | -0.0027087 | 0.0013203 | 0.0021363 | -0.0027749 | 0.064621 | 0.069959 | -0.20147 | -0.00070281 | 96.7484 | -24.8886 | 0.85144 | -24.9252 | 96.5286 | -24.7604 | -24.733 | -25.1175 | 0.78278 | -25.1495 | 96.4645 | 96.6248 | -24.6231 | -24.733 | 0.018311 | 0.045777 | -0.16937 | -0.10986 | -0.14648 | -0.19226 | 0.050354 | 0.15564 | 0.045777 | -0.23346 | -0.33874 | -0.37079 | -0.41657 | -0.073242 | 121.3074 | 121.5271 | 25.6302 | -121.431 | 121.2433 | 121.4035 | 25.5615 | -121.431
737.4062 | 121.6507 | -23.2727 | 98.259 | -0.0049592 | 0.0055093 | 0.066255 | 0.0031702 | 0.064766 | 0.00092287 | -0.0012433 | -0.0054932 | -0.0027749 | 0.06633 | 0.067182 | -0.20041 | -0.0032662 | 98.2407 | -23.4329 | 0.94299 | -23.4238 | 98.1354 | -23.2452 | -23.259 | -23.6298 | 0.88806 | -23.6984 | 98.0804 | 98.172 | -23.1583 | -23.2635 | 0.027466 | 0.013733 | -0.1236 | -0.16022 | -0.15106 | -0.1648 | -0.01831 | 0.11444 | 0.009155 | -0.17853 | -0.35706 | -0.42572 | -0.43488 | -0.086975 | 121.4081 | 121.5134 | 24.2157 | -121.5179 | 121.3531 | 121.4447 | 24.1608 | -121.5225
739.1719 | 121.701 | -18.7042 | 102.7954 | -0.012589 | -4.4874e-05 | 0.066683 | -0.0019568 | 0.067543 | -0.0020679 | 0.00025206 | -0.0054932 | -0.0023477 | 0.06398 | 0.065473 | -0.19891 | -0.00091641 | 102.8824 | -18.7637 | 1.03 | -18.7775 | 102.6077 | -18.6493 | -18.663 | -18.9056 | 1.1719 | -18.988 | 102.594 | 102.681 | -18.5669 | -18.6356 | 0.054932 | 0.041199 | -0.18768 | -0.059509 | -0.073242 | -0.11444 | 0.086975 | 0.13733 | 0.068665 | -0.20142 | -0.20142 | -0.28381 | -0.35248 | -0.11444 | 121.312 | 121.5866 | 19.7342 | -121.4584 | 121.2982 | 121.3852 | 19.8761 | -121.431
740.9375 | 121.7331 | -17.6147 | 103.8712 | -0.0049592 | -0.0026083 | 0.065187 | 0.00039302 | 0.065621 | -0.0027087 | -0.0016705 | 0.0021363 | -0.0059793 | 0.064407 | 0.066328 | -0.20083 | -0.0021982 | 103.9032 | -17.7338 | 1.0345 | -17.7246 | 103.7292 | -17.5644 | -17.5919 | -17.9031 | 1.2085 | -17.9581 | 103.6743 | 103.8071 | -17.482 | -17.5644 | 0.050354 | 0.022888 | -0.14191 | -0.11902 | -0.10986 | -0.13275 | 0.032043 | 0.13275 | 0.050354 | -0.19684 | -0.28839 | -0.34332 | -0.39368 | -0.064087 | 121.344 | 121.5179 | 18.6493 | -121.463 | 121.2891 | 121.4218 | 18.8232 | -121.4355
742.6406 | 121.7514 | -16.2506 | 105.2399 | -0.0049592 | 0.0048685 | 0.064974 | 0.0014612 | 0.068611 | 0.0017773 | 0.0015339 | -0.0054932 | 0.00064308 | 0.065689 | 0.06761 | -0.1972 | -0.002839 | 105.2994 | -16.3788 | 1.0666 | -16.3559 | 105.1071 | -16.2277 | -16.2186 | -16.4291 | 1.355 | -16.5482 | 105.0522 | 105.162 | -16.1041 | -16.1865 | 0.022888 | 0.032043 | -0.13275 | -0.12817 | -0.10529 | -0.13733 | 0.059509 | 0.14648 | 0.064087 | -0.18768 | -0.17853 | -0.29755 | -0.36163 | -0.07782 | 121.3577 | 121.55 | 17.3172 | -121.4584 | 121.3028 | 121.4127 | 17.6056 | -121.4264
744.4062 | 121.6736 | -16.5894 | 104.9469 | -0.0049592 | 0.0031595 | 0.066896 | 0.0053064 | 0.066262 | -0.0048449 | -0.00081594 | 0.0021363 | -0.0044839 | 0.064407 | 0.065687 | -0.20019 | -0.0015572 | 105.0339 | -16.6077 | 1.2085 | -16.6168 | 104.7821 | -16.5161 | -16.5344 | -16.745 | 1.4282 | -16.8274 | 104.7043 | 104.837 | -16.4108 | -16.5161 | 0.073242 | 0.054931 | -0.16479 | -0.018311 | -0.027466 | -0.082397 | 0.086976 | 0.17853 | 0.073242 | -0.24261 | -0.15564 | -0.23804 | -0.31128 | -0.10986 | 121.3715 | 121.6232 | 17.7979 | -121.4813 | 121.2936 | 121.4264 | 18.0176 | -121.463
746.1562 | 121.6736 | -14.7354 | 106.7825 | -0.0049592 | 0.0010233 | 0.066042 | 0.0018884 | 0.068398 | -0.0020679 | -0.0010297 | 0.0021363 | -0.0070475 | 0.064194 | 0.06825 | -0.20212 | -0.0034798 | 106.8695 | -14.7354 | 1.3733 | -14.7491 | 106.6177 | -14.6851 | -14.6805 | -14.8819 | 1.7578 | -14.9551 | 106.5811 | 106.6727 | -14.6027 | -14.6667 | 0.050354 | 0.054932 | -0.16479 | 0 | -0.013733 | -0.068665 | 0.086975 | 0.13275 | 0.068665 | -0.20142 | -0.14648 | -0.21973 | -0.28839 | -0.10986 | 121.3531 | 121.6049 | 16.1087 | -121.463 | 121.3165 | 121.4081 | 16.4932 | -121.4493
747.8594 | 121.6461 | -13.3759 | 108.2291 | -0.0049592 | 0.0057229 | 0.064546 | 0.0029566 | 0.065193 | 0.0017773 | 0.00046566 | 0.0021363 | -0.00021152 | 0.065689 | 0.06825 | -0.19912 | -0.0026254 | 108.1924 | -13.4766 | 1.1765 | -13.4125 | 108.0688 | -13.3118 | -13.3301 | -13.5681 | 1.5564 | -13.6963 | 108.0093 | 108.1146 | -13.2477 | -13.3255 | 0.064086 | 0.045776 | -0.16022 | -0.10071 | -0.036622 | -0.082398 | -0.036621 | 0.12817 | 0.050354 | -0.21973 | -0.19226 | -0.32043 | -0.37079 | -0.11444 | 121.4447 | 121.5683 | 14.5523 | -121.5591 | 121.3852 | 121.4905 | 14.9322 | -121.5546
749.625 | 121.7331 | -12.204 | 109.2865 | -0.0049592 | 0.0029459 | 0.063478 | 0.00082022 | 0.066689 | 0.0015637 | 0.0013203 | 0.017395 | -0.0040567 | 0.06633 | 0.069105 | -0.1987 | -0.0021982 | 109.3918 | -12.2589 | 1.2314 | -12.2086 | 109.1583 | -12.1582 | -12.1857 | -12.3047 | 1.7166 | -12.4374 | 109.0622 | 109.1583 | -12.0712 | -12.1445 | 0.045776 | 0.01831 | -0.12817 | -0.054932 | -0.004578 | -0.022888 | 0.10529 | 0.13275 | 0.059509 | -0.2243 | -0.10071 | -0.23346 | -0.29297 | -0.12817 | 121.3623 | 121.5958 | 13.4354 | -121.4722 | 121.2662 | 121.3623 | 13.9206 | -121.431
751.3906 | 121.6461 | -10.1578 | 111.4426 | -0.0049592 | 0.0063639 | 0.065828 | -0.00024778 | 0.068398 | 0.0024183 | 0.0019611 | -0.0054932 | -0.00085232 | 0.066971 | 0.066542 | -0.1987 | -0.0032662 | 111.3922 | -10.2219 | 1.2909 | -10.1486 | 111.2961 | -10.0754 | -10.1166 | -10.2448 | 1.8539 | -10.3958 | 111.2412 | 111.351 | -10.0113 | -10.0754 | 0.082398 | 0.041199 | -0.14648 | -0.064087 | 0.009155 | -0.032044 | -0.050354 | 0.14648 | 0.082398 | -0.20142 | -0.086975 | -0.23804 | -0.32043 | -0.091553 | 121.4539 | 121.55 | 11.4487 | -121.5591 | 121.3989 | 121.5088 | 12.0117 | -121.5179
753.1562 | 121.7056 | -10.3821 | 111.1267 | -0.0049592 | 0.0025185 | 0.064119 | -0.0021704 | 0.065621 | -0.0018543 | 0.0017475 | -0.0054932 | -0.0021341 | 0.06398 | 0.065473 | -0.19677 | -0.001771 | 111.2183 | -10.3546 | 1.3184 | -10.3409 | 110.9619 | -10.3271 | -10.3546 | -10.4187 | 1.8906 | -10.556 | 110.9207 | 111.0718 | -10.2356 | -10.3043 | 0.054932 | 0.027466 | -0.1648 | 0.027466 | 0.041199 | 0.013733 | 0.091553 | 0.14648 | 0.07782 | -0.20599 | -0.036621 | -0.17395 | -0.25177 | -0.054932 | 121.344 | 121.6003 | 11.7004 | -121.4813 | 121.3028 | 121.4539 | 12.2726 | -121.431
754.8906 | 121.5912 | -10.0937 | 111.4929 | 0.0026703 | 0.0044411 | 0.064119 | -0.0025976 | 0.067543 | 0.0049817 | 0.0023883 | -0.0054932 | 0.00064308 | 0.065689 | 0.067823 | -0.19528 | -0.0024118 | 111.4838 | -10.1395 | 1.3229 | -10.0845 | 111.3556 | -10.0159 | -10.0479 | -10.1761 | 1.8585 | -10.3592 | 111.2915 | 111.4197 | -9.938 | -9.9976 | 0.07782 | 0.045776 | -0.13733 | -0.045776 | 0.009155 | -0.036621 | -0.009155 | 0.15564 | 0.09613 | -0.20142 | -0.082397 | -0.2655 | -0.36163 | -0.073242 | 121.4493 | 121.5775 | 11.4166 | -121.5408 | 121.3852 | 121.5134 | 11.9522 | -121.4905
756.6562 | 121.7377 | -9.3384 | 112.1933 | -0.0049592 | 0.0010233 | 0.066683 | 0.0042382 | 0.065193 | -0.0084765 | -0.00038874 | 0.0021363 | -0.0044839 | 0.065689 | 0.063764 | -0.20276 | -0.00070281 | 112.1658 | -9.3842 | 1.3641 | -9.3201 | 112.0148 | -9.2926 | -9.3521 | -9.4345 | 1.973 | -9.5215 | 111.969 | 112.0789 | -9.2285 | -9.2651 | 0.045776 | -0.013733 | -0.17853 | -0.045776 | 0.018311 | 0.032044 | -0.027465 | 0.10986 | 0.073242 | -0.2243 | -0.09613 | -0.1831 | -0.25635 | -0.11444 | 121.3531 | 121.5042 | 10.7025 | -121.5454 | 121.3074 | 121.4172 | 11.3113 | -121.4584
758.4219 | 121.6599 | -8.4778 | 113.0905 | 0.0026703 | 0.00080973 | 0.066042 | -0.00067498 | 0.064125 | 0.0030591 | 0.00089286 | -0.0054932 | -0.0017069 | 0.065262 | 0.066755 | -0.1987 | -0.0041208 | 113.0859 | -8.5144 | 1.3962 | -8.4229 | 112.999 | -8.4 | -8.4503 | -8.5419 | 2.0645 | -8.6792 | 112.9166 | 113.031 | -8.3542 | -8.4 | 0.07782 | 0.027466 | -0.091553 | -0.036621 | 0.054931 | 0.027465 | -0.004578 | 0.1236 | 0.07782 | -0.17395 | -0.064087 | -0.20142 | -0.27924 | -0.059509 | 121.4767 | 121.5637 | 9.874 | -121.5408 | 121.3943 | 121.5088 | 10.5423 | -121.4905
760.125 | 121.7239 | -8.107 | 113.4064 | -0.0049592 | 0.00080973 | 0.066255 | 0.00060662 | 0.065621 | 0.00070927 | 0.0028155 | -0.0054932 | -0.00085232 | 0.06398 | 0.067182 | -0.1987 | -0.00091641 | 113.4476 | -8.1482 | 1.387 | -8.0704 | 113.269 | -8.0612 | -8.107 | -8.1345 | 2.1057 | -8.2672 | 113.2095 | 113.3469 | -7.9514 | -8.0521 | 0.045777 | 0 | -0.13733 | -0.041198 | 0.036621 | 0.036621 | 0.041199 | 0.15564 | 0.054932 | -0.19684 | -0.027465 | -0.16022 | -0.21515 | -0.059509 | 121.376 | 121.5546 | 9.494 | -121.5134 | 121.3165 | 121.4539 | 10.2127 | -121.4584
761.8906 | 121.6827 | -7.8964 | 113.6993 | -0.012589 | 0.0040139 | 0.066896 | 0.0018884 | 0.065834 | -0.0059131 | -0.0018841 | -0.0054932 | -0.0059793 | 0.063766 | 0.067396 | -0.19934 | -0.0013436 | 113.7222 | -7.7866 | 1.5427 | -7.782 | 113.4979 | -7.8094 | -7.8323 | -7.8873 | 2.243 | -7.9926 | 113.4247 | 113.5574 | -7.7408 | -7.8003 | 0.086975 | 0.064087 | -0.20142 | 0.10986 | 0.11444 | 0.050354 | 0.022888 | 0.15564 | 0.09613 | -0.27466 | 0.009155 | -0.096131 | -0.19226 | -0.14191 | 121.3943 | 121.6187 | 9.4391 | -121.5317 | 121.3211 | 121.4539 | 10.1395 | -121.4996
763.6406 | 121.6049 | -7.6492 | 113.9465 | 0.0103 | 0.0072183 | 0.06476 | 0.001034 | 0.067116 | 0.0024183 | 0.0013203 | 0.0021363 | 0.00085668 | 0.065475 | 0.068464 | -0.19656 | -0.0034798 | 113.9923 | -7.608 | 1.5015 | -7.5439 | 113.8092 | -7.5439 | -7.5851 | -7.6447 | 2.211 | -7.8003 | 113.7497 | 113.8962 | -7.4799 | -7.5439 | 0.10529 | 0.064087 | -0.13733 | 0.041199 | 0.10529 | 0.041199 | 0.045777 | 0.16937 | 0.10529 | -0.19684 | 0.004578 | -0.15106 | -0.25635 | -0.050354 | 121.4584 | 121.6415 | 9.1507 | -121.5317 | 121.3989 | 121.5454 | 9.8602 | -121.4905
765.3906 | 121.6095 | -7.2372 | 114.386 | -0.012589 | 0.0067911 | 0.063051 | 0.0014612 | 0.066689 | 0.0022047 | 0.0036701 | -0.0054932 | 0.00042948 | 0.067184 | 0.067396 | -0.19891 | -0.0032662 | 114.3814 | -7.2098 | 1.5244 | -7.1365 | 114.2029 | -7.1457 | -7.2189 | -7.2327 | 2.2751 | -7.3792 | 114.1296 | 114.299 | -7.0862 | -7.1365 | 0.091553 | 0.018311 | -0.1831 | 0.027466 | 0.10071 | 0.082397 | -0.004577 | 0.15106 | 0.10071 | -0.25635 | 0.004578 | -0.14191 | -0.24261 | -0.086975 | 121.4401 | 121.6187 | 8.7616 | -121.6049 | 121.3669 | 121.5363 | 9.5123 | -121.5225
767.0938 | 121.7056 | -7.0129 | 114.5416 | -0.0049592 | 0.0031595 | 0.063692 | -0.00088858 | 0.065621 | -0.0037769 | 0.0013203 | 0.0021363 | -0.0066201 | 0.065689 | 0.068037 | -0.20105 | 0.00036539 | 114.5737 | -6.9305 | 1.5244 | -6.8985 | 114.3539 | -6.9305 | -6.958 | -7.0038 | 2.3026 | -7.0999 | 114.3127 | 114.4638 | -6.8573 | -6.926 | 0.082397 | 0.054931 | -0.18768 | 0.082397 | 0.11444 | 0.059509 | 0.032043 | 0.15564 | 0.086975 | -0.22888 | 0.009155 | -0.086976 | -0.17395 | -0.07782 | 121.3669 | 121.5866 | 8.5373 | -121.4996 | 121.3257 | 121.4767 | 9.3155 | -121.4676
768.875 | 121.6324 | -6.4133 | 115.2054 | 0.0026703 | 0.0035867 | 0.062624 | -0.00067498 | 0.067757 | 0.0036999 | 0.0015339 | -0.013123 | 0.00021568 | 0.065048 | 0.068891 | -0.19656 | -0.0036936 | 115.1413 | -6.4865 | 1.4328 | -6.3629 | 115.0635 | -6.3263 | -6.3538 | -6.4407 | 2.2522 | -6.6055 | 115.0269 | 115.1825 | -6.2576 | -6.3354 | 0.086975 | 0.059509 | -0.14191 | -0.073242 | 0.050354 | -0.009155 | -0.064087 | 0.15564 | 0.07782 | -0.17853 | -0.027466 | -0.19226 | -0.27008 | -0.022888 | 121.4767 | 121.5546 | 7.8461 | -121.5591 | 121.4401 | 121.5958 | 8.6655 | -121.5408
770.6406 | 121.701 | -6.0928 | 115.4617 | 0.0026703 | 0.0027323 | 0.065614 | -0.00067498 | 0.066689 | 0.00028207 | 0.0011067 | 0.0097658 | -0.0027749 | 0.06633 | 0.067396 | -0.19806 | -0.001771 | 115.4297 | -6.1386 | 1.4694 | -6.0471 | 115.329 | -6.0242 | -6.1111 | -6.1523 | 2.3254 | -6.2714 | 115.2924 | 115.4251 | -5.9921 | -6.0425 | 0.068664 | -0.018311 | -0.13275 | -0.045777 | 0.045776 | 0.064087 | -0.032044 | 0.10071 | 0.050354 | -0.16937 | -0.05951 | -0.17853 | -0.22888 | -0.036621 | 121.4218 | 121.5225 | 7.5623 | -121.5729 | 121.3852 | 121.5179 | 8.4183 | -121.5042
772.3906 | 121.6049 | -5.8914 | 115.7089 | -0.0049592 | 0.0067911 | 0.063905 | 0.0029566 | 0.066262 | 0.0032727 | 0.0028155 | 0.0021363 | -0.00085232 | 0.068253 | 0.069319 | -0.19934 | -0.001771 | 115.7135 | -5.8319 | 1.6159 | -5.7816 | 115.5899 | -5.7953 | -5.8548 | -5.8685 | 2.4673 | -6.0287 | 115.5258 | 115.6357 | -5.7404 | -5.7999 | 0.09613 | 0.036621 | -0.11902 | 0.059509 | 0.10986 | 0.073242 | 0.004578 | 0.15106 | 0.091552 | -0.1831 | 0.022888 | -0.13733 | -0.22888 | -0.073242 | 121.4813 | 121.6049 | 7.5073 | -121.5637 | 121.4172 | 121.5271 | 8.3588 | -121.5088
774.0938 | 121.6324 | -5.6076 | 116.011 | 0.0026703 | 0.0061501 | 0.065614 | 0.0025292 | 0.065834 | -0.0029223 | -0.00017514 | 0.0021363 | -0.0021341 | 0.064835 | 0.06526 | -0.19998 | -0.00091641 | 115.9241 | -5.5939 | 1.5793 | -5.5161 | 115.8737 | -5.5161 | -5.5573 | -5.6442 | 2.4582 | -5.7495 | 115.8279 | 115.979 | -5.4703 | -5.5069 | 0.091553 | 0.050354 | -0.13733 | 0.013733 | 0.091553 | 0.041199 | -0.086975 | 0.13733 | 0.10071 | -0.18311 | -0.036621 | -0.14191 | -0.24261 | -0.032043 | 121.4813 | 121.5317 | 7.1869 | -121.5683 | 121.4355 | 121.5866 | 8.0658 | -121.5179
775.8438 | 121.669 | -5.4016 | 116.1758 | -0.0049592 | 0.0063639 | 0.065828 | 0.00039302 | 0.069039 | -0.00014533 | 0.0017475 | 0.0021363 | -0.0019205 | 0.065262 | 0.06761 | -0.19806 | -0.0019846 | 116.153 | -5.4108 | 1.6342 | -5.3055 | 116.0477 | -5.3513 | -5.3925 | -5.397 | 2.5589 | -5.5344 | 115.9836 | 116.1209 | -5.2734 | -5.3329 | 0.050354 | 0.009155 | -0.12817 | -0.009156 | 0.09613 | 0.086975 | -0.022888 | 0.12817 | 0.068664 | -0.19226 | 0.004577 | -0.13275 | -0.20142 | -0.054931 | 121.4493 | 121.5546 | 7.0358 | -121.5683 | 121.3852 | 121.5225 | 7.9605 | -121.5088
777.5312 | 121.6507 | -5.2551 | 116.3361 | 0.0026703 | 0.0035867 | 0.06711 | 0.0012476 | 0.066689 | -0.0027087 | 0.00046566 | -0.013123 | -0.0010659 | 0.066757 | 0.068678 | -0.19977 | -0.00091641 | 116.2674 | -5.2597 | 1.6205 | -5.1682 | 116.2033 | -5.1819 | -5.246 | -5.2963 | 2.5497 | -5.4016 | 116.1621 | 116.3086 | -5.1041 | -5.1727 | 0.073242 | 0.009155 | -0.13275 | -0.004578 | 0.086975 | 0.07782 | -0.068665 | 0.15106 | 0.082398 | -0.17395 | -0.041199 | -0.14648 | -0.22888 | -0.027466 | 121.4584 | 121.5225 | 6.8756 | -121.582 | 121.4172 | 121.5637 | 7.8049 | -121.5088
779.2969 | 121.5912 | -5.0262 | 116.5787 | -0.020218 | 0.011491 | 0.06241 | 0.0046656 | 0.066689 | 0.0030591 | 0.0015339 | 0.0021363 | 0.00064308 | 0.067398 | 0.068891 | -0.19827 | -0.0013436 | 116.5421 | -5.0308 | 1.6296 | -4.9301 | 116.4413 | -4.9301 | -5.0125 | -5.0354 | 2.5635 | -5.2048 | 116.391 | 116.5283 | -4.8798 | -4.9622 | 0.09613 | 0.013733 | -0.13733 | -0.004578 | 0.09613 | 0.082397 | -0.036621 | 0.14648 | 0.064087 | -0.18768 | -0.009155 | -0.17853 | -0.24262 | -0.050354 | 121.4676 | 121.5683 | 6.6559 | -121.5912 | 121.4172 | 121.5546 | 7.5897 | -121.5408
781.0625 | 121.6827 | -4.7836 | 116.7664 | 0.0026703 | 0.0048685 | 0.06711 | -0.00067498 | 0.064766 | -0.0052721 | -0.00081594 | -0.0054932 | -0.0061929 | 0.065903 | 0.068037 | -0.19998 | -0.0013436 | 116.8167 | -4.6875 | 1.68 | -4.6646 | 116.6061 | -4.6875 | -4.7424 | -4.7333 | 2.655 | -4.8614 | 116.5054 | 116.7023 | -4.6509 | -4.6921 | 0.09613 | 0.041198 | -0.16022 | 0.09613 | 0.11902 | 0.07782 | 0.050354 | 0.13275 | 0.091552 | -0.26093 | 0.050354 | -0.07782 | -0.16937 | -0.064086 | 121.3898 | 121.6003 | 6.4636 | -121.5088 | 121.2891 | 121.4859 | 7.4387 | -121.4584
782.8281 | 121.6553 | -4.541 | 117.0776 | -0.0049592 | 0.0035867 | 0.064974 | 0.001034 | 0.065407 | -0.0029223 | -0.0010297 | -0.013123 | -0.0049111 | 0.064835 | 0.066328 | -0.20105 | -0.00113 | 117.0868 | -4.4128 | 1.799 | -4.3671 | 116.8671 | -4.4449 | -4.4724 | -4.454 | 2.7603 | -4.5593 | 116.8213 | 116.9815 | -4.3716 | -4.422 | 0.096131 | 0.068665 | -0.21057 | 0.12817 | 0.17395 | 0.10529 | 0.009155 | 0.16937 | 0.11902 | -0.25635 | 0.086975 | -0.01831 | -0.13733 | -0.096131 | 121.4081 | 121.6278 | 6.34 | -121.55 | 121.3623 | 121.5225 | 7.3013 | -121.4996
784.6094 | 121.6782 | -4.5776 | 116.9907 | 0.0026703 | 0.0016641 | 0.064333 | -0.0019568 | 0.06733 | -0.0061267 | 0.00046566 | -0.020752 | -0.0042703 | 0.063766 | 0.066755 | -0.20019 | -0.0024118 | 116.9998 | -4.5181 | 1.6891 | -4.4861 | 116.803 | -4.4907 | -4.5319 | -4.5731 | 2.6642 | -4.6555 | 116.7755 | 116.922 | -4.4357 | -4.4769 | 0.086975 | 0.045777 | -0.18768 | 0.05951 | 0.091553 | 0.045776 | 0.009155 | 0.14191 | 0.10071 | -0.21515 | 0.004578 | -0.07782 | -0.17853 | -0.068665 | 121.3806 | 121.5775 | 6.2668 | -121.5225 | 121.3531 | 121.4996 | 7.2418 | -121.4676
786.3125 | 121.7377 | -4.303 | 117.2607 | -0.0049592 | 0.00016873 | 0.067751 | -0.00067498 | 0.063912 | -0.0014269 | -0.00060234 | -0.0054932 | -0.0044839 | 0.06163 | 0.066542 | -0.20169 | -0.00113 | 117.3157 | -4.1977 | 1.7807 | -4.1656 | 117.1051 | -4.2252 | -4.2664 | -4.2252 | 2.774 | -4.303 | 117.0273 | 117.1692 | -4.1656 | -4.2023 | 0.07782 | 0.036622 | -0.15564 | 0.10529 | 0.13733 | 0.10071 | 0.054932 | 0.13733 | 0.10071 | -0.23346 | 0.07782 | 0 | -0.10071 | -0.091553 | 121.4081 | 121.6187 | 6.0837 | -121.5271 | 121.3303 | 121.4722 | 7.077 | -121.463
788.0781 | 121.6003 | -4.0924 | 117.5629 | -0.0049592 | 0.0050821 | 0.064333 | 0.00060662 | 0.065193 | 0.0045545 | 0.0011067 | -0.0054932 | 0.00021568 | 0.065903 | 0.069105 | -0.1972 | -0.0054026 | 117.5171 | -4.0833 | 1.7166 | -3.9688 | 117.4118 | -3.9963 | -4.0329 | -4.0512 | 2.7191 | -4.2343 | 117.3615 | 117.4942 | -3.9322 | -3.978 | 0.09613 | 0.059509 | -0.15106 | 0.009155 | 0.1236 | 0.064087 | -0.045776 | 0.16022 | 0.11444 | -0.20142 | 0.041199 | -0.14191 | -0.25635 | -0.068664 | 121.5042 | 121.6095 | 5.809 | -121.5958 | 121.4539 | 121.5866 | 6.8115 | -121.5408
789.7812 | 121.6736 | -3.7811 | 117.778 | 0.0026703 | 0.0014505 | 0.067323 | -0.001316 | 0.066048 | -0.0020679 | 0.0011067 | -0.013123 | -0.0057657 | 0.066116 | 0.067396 | -0.19763 | -0.0019846 | 117.8238 | -3.6804 | 1.7899 | -3.6621 | 117.5995 | -3.6987 | -3.7445 | -3.717 | 2.8198 | -3.8315 | 117.5217 | 117.6819 | -3.6575 | -3.7079 | 0.082398 | 0.036621 | -0.17853 | 0.10071 | 0.11902 | 0.082398 | 0.045777 | 0.1236 | 0.073242 | -0.25635 | 0.064087 | -0.050354 | -0.1236 | -0.09613 | 121.3806 | 121.6049 | 5.571 | -121.5225 | 121.3028 | 121.463 | 6.601 | -121.4859
791.4844 | 121.5958 | -3.5019 | 118.1213 | -0.012589 | 0.0057229 | 0.064333 | -0.00046138 | 0.06498 | 0.0026319 | 0.0019611 | 0.0021363 | -0.0012795 | 0.063766 | 0.069105 | -0.1972 | -0.0034798 | 118.0664 | -3.4744 | 1.7578 | -3.3783 | 118.0069 | -3.3966 | -3.4744 | -3.479 | 2.7786 | -3.6346 | 117.9428 | 118.0801 | -3.3691 | -3.3966 | 0.10529 | 0.027466 | -0.11444 | 0.027466 | 0.1236 | 0.09613 | -0.054932 | 0.13275 | 0.10529 | -0.17853 | 0.022888 | -0.13275 | -0.23804 | -0.041199 | 121.5088 | 121.5683 | 5.2597 | -121.5958 | 121.4447 | 121.582 | 6.2805 | -121.5179
793.25 | 121.6049 | -3.3646 | 118.2404 | -0.012589 | 0.0018777 | 0.065187 | 0.0042382 | 0.065834 | -0.0031359 | 0.00025206 | -0.0054932 | -0.0023477 | 0.066544 | 0.065901 | -0.20105 | -0.0013436 | 118.2404 | -3.2776 | 1.8448 | -3.2135 | 118.0984 | -3.2547 | -3.3234 | -3.3417 | 2.8931 | -3.4287 | 118.0573 | 118.1854 | -3.2135 | -3.2684 | 0.10986 | 0.041199 | -0.14191 | 0.086975 | 0.15106 | 0.10986 | 0 | 0.15106 | 0.09613 | -0.18311 | 0.022888 | -0.064087 | -0.16022 | -0.054931 | 121.463 | 121.6049 | 5.2094 | -121.5637 | 121.4218 | 121.55 | 6.2576 | -121.5088
795.0156 | 121.701 | -3.1586 | 118.4418 | -0.0049592 | -0.0011131 | 0.066896 | -0.0015296 | 0.067543 | -0.0046313 | -0.0012433 | -0.013123 | -0.0044839 | 0.061417 | 0.067182 | -0.19977 | -0.0021982 | 118.4143 | -3.0808 | 1.8082 | -3.0212 | 118.2861 | -3.0579 | -3.1128 | -3.1128 | 2.9022 | -3.2181 | 118.2358 | 118.3731 | -3.0121 | -3.0487 | 0.10071 | 0.045776 | -0.15564 | 0.077819 | 0.13733 | 0.091553 | -0.027465 | 0.14648 | 0.10986 | -0.20599 | 0.045776 | -0.05951 | -0.16937 | -0.068664 | 121.4447 | 121.5729 | 4.9667 | -121.5546 | 121.3943 | 121.5317 | 6.0608 | -121.4905
796.7812 | 121.6415 | -3.0808 | 118.5196 | -0.012589 | 0.0010233 | 0.065614 | 0.00039302 | 0.064553 | -0.0029223 | -0.0023113 | -0.013123 | -0.0029885 | 0.06398 | 0.067396 | -0.19827 | -0.0030526 | 118.5699 | -2.9343 | 1.9409 | -2.8976 | 118.3594 | -2.9663 | -3.0121 | -2.9617 | 3.0396 | -3.0579 | 118.3044 | 118.4738 | -2.9022 | -2.9572 | 0.11444 | 0.068665 | -0.16022 | 0.14649 | 0.18311 | 0.11444 | 0.050354 | 0.17853 | 0.1236 | -0.21515 | 0.11902 | 0.022889 | -0.10071 | -0.045776 | 121.4401 | 121.6507 | 5.0217 | -121.5317 | 121.3852 | 121.5546 | 6.1203 | -121.4767
798.5312 | 121.7239 | -2.9984 | 118.5654 | -0.012589 | -0.00047207 | 0.066896 | 0.0012476 | 0.066902 | -0.0029223 | 3.8456e-05 | -0.020752 | -0.0051247 | 0.063553 | 0.066755 | -0.19912 | -0.0015572 | 118.6523 | -2.8381 | 1.9455 | -2.8244 | 118.4326 | -2.9022 | -2.9617 | -2.8839 | 3.0441 | -2.98 | 118.3502 | 118.5379 | -2.8473 | -2.8839 | 0.09613 | 0.036621 | -0.13275 | 0.16022 | 0.17395 | 0.13733 | 0.086975 | 0.15106 | 0.11444 | -0.21515 | 0.11444 | 0.01831 | -0.096131 | -0.027466 | 121.431 | 121.6507 | 4.9438 | -121.5271 | 121.3486 | 121.5363 | 6.0425 | -121.4493
800.2969 | 121.6141 | -2.9572 | 118.6661 | -0.0049592 | -0.00068567 | 0.067323 | -0.002384 | 0.067116 | -0.0018543 | -0.00081594 | -0.013123 | -0.0032021 | 0.062271 | 0.066328 | -0.19848 | -0.0030526 | 118.7027 | -2.8061 | 1.9547 | -2.7695 | 118.4921 | -2.8336 | -2.8885 | -2.8381 | 3.0716 | -2.9617 | 118.4418 | 118.5928 | -2.8015 | -2.8381 | 0.1236 | 0.068664 | -0.17395 | 0.15106 | 0.18768 | 0.11902 | 0.036621 | 0.15564 | 0.11902 | -0.22431 | 0.11902 | -0.004578 | -0.1236 | -0.073243 | 121.4493 | 121.6599 | 4.9118 | -121.5546 | 121.3989 | 121.55 | 6.0287 | -121.5042
802 | 121.7331 | -2.7878 | 118.7531 | -0.0049592 | 0.0031595 | 0.068178 | 0.00017942 | 0.066048 | -0.0022815 | -0.0031659 | -0.0054932 | -0.0049111 | 0.063553 | 0.066969 | -0.19934 | -0.0032662 | 118.8354 | -2.6733 | 1.9547 | -2.6413 | 118.6203 | -2.7008 | -2.7924 | -2.6917 | 3.0945 | -2.7786 | 118.5242 | 118.6798 | -2.6505 | -2.7145 | 0.086975 | -0.004577 | -0.13275 | 0.11444 | 0.14648 | 0.15106 | 0.082397 | 0.13733 | 0.073242 | -0.22888 | 0.096131 | 0.009156 | -0.064086 | -0.073242 | 121.4081 | 121.6232 | 4.7424 | -121.5454 | 121.312 | 121.4676 | 5.8823 | -121.4676
803.7656 | 121.5866 | -2.7466 | 118.8858 | 0.0026703 | 0.0042275 | 0.066469 | -0.0011024 | 0.065621 | 0.0045545 | 0.0026019 | -0.0054932 | 0.0027793 | 0.063553 | 0.066328 | -0.19571 | -0.0051888 | 118.9087 | -2.6367 | 1.9226 | -2.5772 | 118.7576 | -2.6093 | -2.6733 | -2.6505 | 3.0441 | -2.8336 | 118.7164 | 118.8538 | -2.5543 | -2.6184 | 0.13733 | 0.073242 | -0.12817 | 0.10986 | 0.16937 | 0.096131 | 0.022888 | 0.19226 | 0.12817 | -0.16937 | 0.09613 | -0.086975 | -0.21515 | -0.032043 | 121.5042 | 121.6553 | 4.6692 | -121.5591 | 121.463 | 121.6003 | 5.7907 | -121.5042
805.5469 | 121.6919 | -2.623 | 118.895 | -0.012589 | 0.0089273 | 0.063265 | 0.0042382 | 0.066475 | 0.0036999 | 0.00089286 | -0.013123 | -0.0010659 | 0.066116 | 0.066969 | -0.19827 | -0.0030526 | 118.9041 | -2.6596 | 1.8539 | -2.5406 | 118.8309 | -2.5635 | -2.6321 | -2.6047 | 2.9984 | -2.7512 | 118.7531 | 118.8995 | -2.5177 | -2.5681 | 0.059509 | -0.009155 | -0.064086 | -0.036621 | 0.082398 | 0.091553 | 0.009156 | 0.10529 | 0.054932 | -0.14191 | 0.018311 | -0.12817 | -0.18311 | 0.004578 | 121.4539 | 121.5271 | 4.4769 | -121.5271 | 121.376 | 121.5225 | 5.6213 | -121.463
807.3125 | 121.7239 | -2.5772 | 118.9774 | -0.020218 | 0.0070047 | 0.062837 | 0.0033838 | 0.065834 | 0.0022047 | 0.0017475 | -0.0054932 | 0.00021568 | 0.067825 | 0.068891 | -0.19998 | -0.0015572 | 118.9362 | -2.6093 | 1.8723 | -2.504 | 118.8446 | -2.5177 | -2.6047 | -2.5406 | 3.0487 | -2.6917 | 118.8034 | 118.9499 | -2.4857 | -2.504 | 0.059509 | -0.027466 | -0.13275 | -0.032044 | 0.073242 | 0.10071 | -0.041199 | 0.091552 | 0.073242 | -0.17395 | 0.036621 | -0.11444 | -0.18768 | -0.027466 | 121.4218 | 121.5134 | 4.4495 | -121.582 | 121.3806 | 121.5271 | 5.6259 | -121.4813
809.0156 | 121.5912 | -2.4811 | 119.1147 | 0.0026703 | 0.0040139 | 0.062624 | 0.00017942 | 0.064339 | 0.0026319 | 0.0017475 | -0.0054932 | -0.00042512 | 0.065048 | 0.069105 | -0.19549 | -0.0034798 | 119.0781 | -2.4765 | 1.9409 | -2.3666 | 118.9636 | -2.4124 | -2.4673 | -2.4399 | 3.1082 | -2.623 | 118.9087 | 119.0552 | -2.3666 | -2.3987 | 0.068664 | 0.013733 | -0.15106 | 0.004578 | 0.11444 | 0.10071 | -0.036621 | 0.11444 | 0.082397 | -0.20599 | 0.041199 | -0.14191 | -0.2243 | -0.059509 | 121.4447 | 121.5591 | 4.422 | -121.582 | 121.3898 | 121.5363 | 5.5893 | -121.5134
810.7812 | 121.6095 | -2.4033 | 119.2154 | 0.0026703 | 0.0046549 | 0.062624 | 0.001034 | 0.068398 | 0.00070927 | 0.0023883 | 0.0021363 | -0.00042512 | 0.064407 | 0.069746 | -0.19848 | -0.001771 | 119.1559 | -2.4033 | 1.9455 | -2.2934 | 119.0826 | -2.3163 | -2.3895 | -2.3804 | 3.1128 | -2.5406 | 119.0277 | 119.165 | -2.2614 | -2.3163 | 0.086975 | 0.013733 | -0.13275 | 0 | 0.10986 | 0.09613 | -0.059509 | 0.14191 | 0.086975 | -0.18768 | 0.022888 | -0.13733 | -0.2243 | -0.050354 | 121.4859 | 121.5591 | 4.3488 | -121.6049 | 121.431 | 121.5683 | 5.5161 | -121.5317
812.5469 | 121.6187 | -2.2202 | 119.4168 | -0.012589 | 0.0033731 | 0.06711 | -0.00024778 | 0.064766 | -0.0044177 | -0.00038874 | -0.0054932 | -0.0032021 | 0.063766 | 0.069532 | -0.20083 | -0.00070281 | 119.4031 | -2.0599 | 2.0966 | -2.0233 | 119.1879 | -2.1103 | -2.1652 | -2.1149 | 3.2776 | -2.2064 | 119.1788 | 119.3253 | -2.0462 | -2.1011 | 0.10986 | 0.054932 | -0.22888 | 0.16022 | 0.19684 | 0.14191 | -0.013733 | 0.17395 | 0.11902 | -0.23804 | 0.10529 | 0.013733 | -0.10529 | -0.091553 | 121.4081 | 121.6232 | 4.3167 | -121.582 | 121.3989 | 121.5454 | 5.4977 | -121.5179
814.3125 | 121.5912 | -2.1744 | 119.4305 | -0.0049592 | 0.0080727 | 0.064119 | 0.00060662 | 0.067116 | 0.0028455 | -0.00081594 | 0.0021363 | -0.0010659 | 0.066757 | 0.068891 | -0.19955 | -0.0034798 | 119.4214 | -2.0966 | 2.0279 | -2.0325 | 119.2749 | -2.1011 | -2.1561 | -2.1057 | 3.2547 | -2.2476 | 119.2291 | 119.3665 | -2.0279 | -2.0737 | 0.073242 | 0.01831 | -0.15564 | 0.077819 | 0.14191 | 0.1236 | -0.009155 | 0.14648 | 0.10071 | -0.20142 | 0.068664 | -0.073243 | -0.17395 | -0.064087 | 121.4493 | 121.5958 | 4.2023 | -121.5866 | 121.4035 | 121.5408 | 5.4291 | -121.5042
816.0156 | 121.7239 | -2.1149 | 119.4626 | -0.0049592 | 0.0010233 | 0.067323 | 0.00060662 | 0.067116 | -0.0071947 | 0.00025206 | -0.0054932 | -0.0053385 | 0.063126 | 0.066328 | -0.19891 | 0.00036539 | 119.4214 | -2.0416 | 1.9958 | -1.9775 | 119.3115 | -2.0279 | -2.0874 | -2.0782 | 3.2135 | -2.1469 | 119.2383 | 119.3802 | -1.9592 | -2.0096 | 0.086975 | 0.027466 | -0.15106 | 0.073242 | 0.13733 | 0.10986 | -0.041198 | 0.15564 | 0.10528 | -0.2243 | 0.036621 | -0.032044 | -0.13733 | -0.082397 | 121.4264 | 121.5363 | 4.1107 | -121.55 | 121.3531 | 121.4951 | 5.3284 | -121.4722
817.7812 | 121.6187 | -2.1881 | 119.4031 | -0.0049592 | 0.0018777 | 0.065401 | 0.0012476 | 0.063271 | 0.0030591 | 0.0011067 | -0.0054932 | -0.00042512 | 0.065903 | 0.066542 | -0.19806 | -0.0019846 | 119.371 | -2.1057 | 2.0691 | -2.0416 | 119.2429 | -2.0966 | -2.179 | -2.1103 | 3.3005 | -2.243 | 119.2154 | 119.3024 | -2.0462 | -2.0966 | 0.091552 | 0.009155 | -0.16022 | 0.082397 | 0.14648 | 0.13733 | -0.032043 | 0.14191 | 0.091552 | -0.18768 | 0.077819 | -0.054932 | -0.14648 | -0.10071 | 121.431 | 121.5591 | 4.2572 | -121.582 | 121.4035 | 121.4905 | 5.4886 | -121.4996
819.5 | 121.6324 | -2.2018 | 119.2291 | -0.0049592 | 0.0027323 | 0.06711 | 0.002102 | 0.063271 | -0.0071947 | -0.00060234 | 0.0021363 | -0.0057657 | 0.064407 | 0.062483 | -0.20297 | -0.00091641 | 119.2749 | -2.0462 | 2.1286 | -2.0554 | 119.0918 | -2.1149 | -2.1606 | -2.1103 | 3.3737 | -2.1698 | 119.0094 | 119.1147 | -2.0691 | -2.1149 | 0.086975 | 0.041198 | -0.13733 | 0.15564 | 0.14648 | 0.10529 | 0.045776 | 0.13275 | 0.086975 | -0.21973 | 0.091552 | 0.032043 | -0.054932 | -0.11444 | 121.2936 | 121.4767 | 4.3304 | -121.3898 | 121.2112 | 121.3165 | 5.5756 | -121.344
821.25 | 121.5225 | -2.2751 | 119.0918 | -0.0049592 | 0.0016641 | 0.065614 | 0.0016748 | 0.064553 | -0.0046313 | 3.8456e-05 | -0.013123 | -0.0044839 | 0.06398 | 0.06825 | -0.20169 | -0.0030526 | 119.133 | -2.1835 | 2.0554 | -2.124 | 118.9774 | -2.1561 | -2.2247 | -2.2293 | 3.2684 | -2.2934 | 118.9362 | 119.0323 | -2.1194 | -2.1561 | 0.11902 | 0.050354 | -0.11444 | 0.091552 | 0.15106 | 0.10071 | 0.041199 | 0.15564 | 0.11902 | -0.15564 | 0.045776 | -0.018311 | -0.13733 | -0.059509 | 121.2524 | 121.4081 | 4.3304 | -121.3165 | 121.2112 | 121.3074 | 5.5435 | -121.2479
823.0156 | 121.3394 | -1.9226 | 119.3436 | -0.0049592 | 0.0050821 | 0.063478 | 0.00017942 | 0.064125 | 0.0017773 | 0.0015339 | 0.0021363 | -0.00021152 | 0.067825 | 0.065901 | -0.19827 | -0.0043344 | 119.2978 | -1.9089 | 2.0737 | -1.8082 | 119.22 | -1.8448 | -1.9089 | -1.8768 | 3.3188 | -2.005 | 119.2291 | 119.2795 | -1.7853 | -1.8402 | 0.077819 | 0.013732 | -0.1236 | 0.013732 | 0.11444 | 0.10071 | -0.045776 | 0.13733 | 0.082397 | -0.11444 | 0.045776 | -0.082398 | -0.1648 | -0.064087 | 121.1426 | 121.2204 | 3.9963 | -121.2524 | 121.1517 | 121.2021 | 5.2414 | -121.1838
824.7812 | 121.5546 | -1.7487 | 119.5908 | 0.0026703 | 0.0055093 | 0.067751 | 0.0046656 | 0.064553 | -0.0046313 | -0.0018841 | 0.0097658 | -0.0061929 | 0.065475 | 0.066969 | -0.20062 | -0.0015572 | 119.6411 | -1.6251 | 2.1606 | -1.6113 | 119.4672 | -1.6754 | -1.7349 | -1.6663 | 3.4332 | -1.7349 | 119.3939 | 119.5267 | -1.6434 | -1.6663 | 0.073242 | 0.013733 | -0.1236 | 0.1236 | 0.13733 | 0.1236 | 0.050354 | 0.10528 | 0.082397 | -0.19684 | 0.082397 | 0.013733 | -0.068664 | -0.064087 | 121.2158 | 121.3898 | 3.9093 | -121.3257 | 121.1426 | 121.2753 | 5.1819 | -121.257
826.5312 | 121.6049 | -1.767 | 119.6457 | 0.0026703 | 0.0012369 | 0.064546 | -0.00088858 | 0.065621 | 0.0030591 | -0.00081594 | -0.0054932 | -0.0025613 | 0.066757 | 0.06825 | -0.20019 | -0.0036936 | 119.664 | -1.7395 | 2.0645 | -1.6617 | 119.5267 | -1.7075 | -1.7761 | -1.6891 | 3.3737 | -1.8082 | 119.4763 | 119.5953 | -1.6251 | -1.6754 | 0.05951 | -0.009155 | -0.11902 | 0.027466 | 0.10529 | 0.11444 | 0.01831 | 0.14191 | 0.091553 | -0.16937 | 0.07782 | -0.041199 | -0.13275 | -0.050354 | 121.2936 | 121.431 | 3.8315 | -121.4218 | 121.2433 | 121.3623 | 5.1407 | -121.3211
828.2969 | 121.6232 | -1.7853 | 119.6686 | -0.0049592 | 0.0010233 | 0.066896 | 0.002102 | 0.068398 | -0.0067675 | -0.00038874 | 0.0021363 | -0.0042703 | 0.063766 | 0.067396 | -0.20297 | -0.0026254 | 119.7281 | -1.6388 | 2.1973 | -1.6113 | 119.5267 | -1.6846 | -1.767 | -1.6571 | 3.4698 | -1.7258 | 119.4534 | 119.5862 | -1.6342 | -1.6663 | 0.10071 | 0.01831 | -0.14191 | 0.14648 | 0.17395 | 0.15564 | 0.059509 | 0.15106 | 0.11902 | -0.21515 | 0.12817 | 0.059509 | -0.059509 | -0.082397 | 121.312 | 121.5134 | 3.9825 | -121.4355 | 121.2387 | 121.3715 | 5.2551 | -121.3348
830.0156 | 121.5912 | -1.799 | 119.7006 | -0.0049592 | 0.0031595 | 0.063692 | -0.00024778 | 0.065193 | -0.00099973 | 0.00067926 | -0.0054932 | -0.0046975 | 0.064407 | 0.066969 | -0.19998 | -0.0026254 | 119.7235 | -1.6525 | 2.1606 | -1.6342 | 119.5404 | -1.6846 | -1.7532 | -1.7029 | 3.4103 | -1.7899 | 119.4626 | 119.6091 | -1.6617 | -1.68 | 0.11444 | 0.045776 | -0.16022 | 0.14648 | 0.1648 | 0.11902 | 0.022888 | 0.13733 | 0.11902 | -0.23804 | 0.09613 | 0.009155 | -0.10986 | -0.091553 | 121.3394 | 121.5225 | 3.9597 | -121.4539 | 121.2616 | 121.4081 | 5.2093 | -121.3806
831.7969 | 121.5729 | -1.8402 | 119.6594 | 0.0026703 | 0.0052957 | 0.066683 | 0.00060662 | 0.065407 | 0.0036999 | 0.0032429 | 0.0097658 | 0.00021568 | 0.064835 | 0.06825 | -0.19421 | -0.0043344 | 119.6869 | -1.7761 | 2.1881 | -1.7029 | 119.5724 | -1.7532 | -1.8265 | -1.7532 | 3.447 | -1.9043 | 119.4901 | 119.5999 | -1.7075 | -1.7487 | 0.086975 | 0.013733 | -0.086975 | 0.064087 | 0.13733 | 0.1236 | 0.027466 | 0.13275 | 0.091553 | -0.16937 | 0.086975 | -0.064087 | -0.15564 | -0.059509 | 121.4127 | 121.5271 | 4.0283 | -121.4859 | 121.3303 | 121.4401 | 5.2872 | -121.4081
833.5 | 121.5958 | -1.8539 | 119.6777 | -0.0049592 | 0.0046549 | 0.063265 | -0.001316 | 0.064339 | 0.0034863 | 3.8456e-05 | 0.0021363 | 0.0012839 | 0.062912 | 0.066542 | -0.19699 | -0.0021982 | 119.6457 | -1.8494 | 2.0691 | -1.7303 | 119.5862 | -1.7441 | -1.8036 | -1.8036 | 3.36 | -1.9409 | 119.5267 | 119.664 | -1.7303 | -1.7487 | 0.10986 | 0.050354 | -0.091552 | 0.004578 | 0.1236 | 0.073242 | -0.032043 | 0.1236 | 0.10529 | -0.15106 | 0.050354 | -0.086975 | -0.19226 | -0.013733 | 121.4401 | 121.4996 | 3.923 | -121.4813 | 121.3806 | 121.5179 | 5.2139 | -121.4264
835.2656 | 121.6324 | -1.8265 | 119.7189 | -0.012589 | 0.0012369 | 0.065614 | -0.0011024 | 0.063698 | 0.00049567 | 0.0045245 | -0.0054932 | -0.0017069 | 0.063553 | 0.06825 | -0.19677 | -0.0019846 | 119.6777 | -1.8082 | 2.0874 | -1.7303 | 119.6228 | -1.7303 | -1.7853 | -1.7899 | 3.4012 | -1.9089 | 119.5312 | 119.6503 | -1.6663 | -1.7349 | 0.09613 | 0.041199 | -0.09613 | 0.01831 | 0.09613 | 0.054931 | -0.041199 | 0.16022 | 0.091553 | -0.18768 | 0.036621 | -0.082398 | -0.17395 | -0.068664 | 121.4493 | 121.5042 | 3.9139 | -121.5042 | 121.3577 | 121.4767 | 5.2277 | -121.4539
837.0312 | 121.582 | -1.7899 | 119.8242 | -0.012589 | 0.0044411 | 0.065401 | 0.0053064 | 0.065621 | 0.00070927 | 0.00046566 | -0.0054932 | -0.0027749 | 0.065689 | 0.065473 | -0.19912 | -0.00113 | 119.7281 | -1.7349 | 2.1973 | -1.6479 | 119.6457 | -1.6983 | -1.7441 | -1.7578 | 3.4698 | -1.8539 | 119.6365 | 119.7556 | -1.6251 | -1.6708 | 0.091553 | 0.045776 | -0.17853 | 0.054932 | 0.14191 | 0.096131 | -0.096131 | 0.16479 | 0.11902 | -0.18768 | 0.032044 | -0.064087 | -0.18311 | -0.068665 | 121.4355 | 121.5179 | 3.9871 | -121.5683 | 121.4264 | 121.5454 | 5.2597 | -121.4951
838.7969 | 121.55 | -1.7349 | 119.8608 | -0.012589 | 0.0038003 | 0.066255 | -0.00088858 | 0.06733 | 0.0011365 | 0.0032429 | 0.0021363 | -0.00063872 | 0.066544 | 0.069319 | -0.19699 | -0.00091641 | 119.8334 | -1.6388 | 2.2476 | -1.5793 | 119.696 | -1.6205 | -1.712 | -1.6434 | 3.5431 | -1.7853 | 119.6548 | 119.7601 | -1.5839 | -1.6251 | 0.11444 | 0.022888 | -0.16479 | 0.09613 | 0.15564 | 0.13275 | -0.027466 | 0.15106 | 0.10986 | -0.20599 | 0.091552 | -0.050354 | -0.16022 | -0.10071 | 121.431 | 121.5683 | 3.9825 | -121.5729 | 121.3898 | 121.4951 | 5.278 | -121.4859
840.5625 | 121.7102 | -1.6891 | 119.8151 | 0.0026703 | -0.0051719 | 0.069032 | 0.00017942 | 0.066262 | -0.0086901 | -0.0014569 | -0.013123 | -0.0059793 | 0.061844 | 0.065473 | -0.20382 | 0.00015159 | 119.8288 | -1.5839 | 2.2202 | -1.5518 | 119.696 | -1.6022 | -1.6617 | -1.6251 | 3.5706 | -1.6708 | 119.632 | 119.783 | -1.5198 | -1.5884 | 0.086975 | 0.027466 | -0.11902 | 0.10529 | 0.13733 | 0.10986 | 0.013733 | 0.16937 | 0.10071 | -0.1831 | 0.064087 | 0.018311 | -0.082397 | -0.032043 | 121.3852 | 121.5179 | 3.9093 | -121.4767 | 121.3211 | 121.4722 | 5.2597 | -121.4035
842.3281 | 121.6782 | -1.6067 | 119.9066 | 0.0026703 | -0.0017539 | 0.066042 | 0.00017942 | 0.063912 | 0.0011365 | 0.0015339 | 0.0021363 | -0.0014933 | 0.062057 | 0.070173 | -0.19763 | -0.0041208 | 119.8746 | -1.6251 | 2.1561 | -1.5289 | 119.8105 | -1.5289 | -1.6022 | -1.5793 | 3.4836 | -1.6891 | 119.7372 | 119.8975 | -1.4923 | -1.5106 | 0.077819 | 0.004577 | -0.09613 | -0.018311 | 0.077819 | 0.073242 | -0.032043 | 0.11444 | 0.09613 | -0.16937 | 0.027465 | -0.082398 | -0.17853 | -0.009155 | 121.4172 | 121.4813 | 3.7628 | -121.5088 | 121.344 | 121.5042 | 5.0903 | -121.4172
844.0938 | 121.6232 | -1.6251 | 119.9707 | -0.012589 | 0.0065775 | 0.063905 | 0.0057336 | 0.065407 | 0.00092287 | 0.00046566 | -0.013123 | -0.0012795 | 0.068466 | 0.06825 | -0.2019 | -0.0041208 | 119.9066 | -1.6022 | 2.2705 | -1.4832 | 119.8425 | -1.5244 | -1.5884 | -1.5793 | 3.5706 | -1.6891 | 119.8196 | 119.9112 | -1.4877 | -1.5106 | 0.10071 | 0.036621 | -0.12817 | 0.022888 | 0.14191 | 0.10529 | -0.064087 | 0.13733 | 0.11444 | -0.15106 | 0.045776 | -0.064087 | -0.17853 | -0.059509 | 121.4676 | 121.5317 | 3.8956 | -121.5591 | 121.4447 | 121.5363 | 5.1956 | -121.4813
845.8125 | 121.6965 | -1.5427 | 119.9799 | -0.0049592 | 0.0029459 | 0.06476 | 0.0016748 | 0.065621 | 0.0028455 | 0.0043109 | -0.0054932 | -0.0038431 | 0.065903 | 0.069959 | -0.20019 | -0.002839 | 119.9524 | -1.5381 | 2.1881 | -1.4511 | 119.8654 | -1.474 | -1.5564 | -1.506 | 3.5339 | -1.6159 | 119.8196 | 119.9249 | -1.4328 | -1.4465 | 0.068665 | -0.013732 | -0.11444 | 0.004578 | 0.091553 | 0.10528 | -0.027465 | 0.10986 | 0.096131 | -0.16022 | 0.036622 | -0.073242 | -0.16937 | -0.054931 | 121.4081 | 121.4951 | 3.7308 | -121.5363 | 121.3623 | 121.4676 | 5.0766 | -121.4264
847.5781 | 121.5683 | -1.5747 | 120.0577 | 0.0026703 | 0.0044411 | 0.065614 | 0.0027428 | 0.06733 | -0.0022815 | 0.0028155 | -0.0054932 | -0.0025613 | 0.064194 | 0.066114 | -0.20212 | -0.0030526 | 120.0165 | -1.4328 | 2.3666 | -1.3916 | 119.8471 | -1.4511 | -1.5289 | -1.4969 | 3.6118 | -1.593 | 119.8288 | 119.9707 | -1.3916 | -1.4603 | 0.1236 | 0.045776 | -0.21057 | 0.14191 | 0.18311 | 0.13733 | -0.041199 | 0.18311 | 0.11444 | -0.22888 | 0.07782 | -0.018311 | -0.13275 | -0.086975 | 121.4218 | 121.5912 | 3.9413 | -121.5866 | 121.4035 | 121.5454 | 5.1865 | -121.5179
849.3438 | 121.5546 | -1.4236 | 120.2179 | 0.0026703 | 0.011491 | 0.063692 | 0.002102 | 0.066475 | 0.0041273 | 0.0021747 | -0.013123 | 0.00064308 | 0.068253 | 0.068678 | -0.20019 | -0.0021982 | 120.1538 | -1.3412 | 2.3254 | -1.2726 | 120.0577 | -1.3 | -1.3687 | -1.3275 | 3.6118 | -1.4832 | 119.9753 | 120.1218 | -1.268 | -1.3 | 0.1236 | 0.054932 | -0.16022 | 0.082397 | 0.15106 | 0.09613 | -0.064087 | 0.15564 | 0.1236 | -0.24262 | 0.09613 | -0.059509 | -0.18311 | -0.096131 | 121.4813 | 121.5775 | 3.7491 | -121.5866 | 121.3989 | 121.5454 | 5.0354 | -121.5179
851.0469 | 121.701 | -1.2863 | 120.2545 | -0.0049592 | 0.0027323 | 0.065187 | -0.0043066 | 0.066262 | 0.0017773 | 0.0015339 | -0.0054932 | -0.0019205 | 0.063126 | 0.066542 | -0.19635 | -0.0024118 | 120.2087 | -1.3 | 2.2385 | -1.2039 | 120.1401 | -1.236 | -1.2863 | -1.2817 | 3.5889 | -1.3962 | 120.0806 | 120.2042 | -1.181 | -1.1993 | 0.050354 | 0 | -0.11444 | -0.013733 | 0.082398 | 0.082398 | -0.045777 | 0.10529 | 0.086975 | -0.17395 | 0.004578 | -0.10986 | -0.19684 | -0.050354 | 121.4264 | 121.4951 | 3.5248 | -121.5408 | 121.3669 | 121.4905 | 4.8752 | -121.4539
852.8125 | 121.6599 | -1.2726 | 120.3049 | 0.0026703 | 0.0038003 | 0.068178 | 0.0029566 | 0.067543 | -0.0061267 | 0.00046566 | 0.0021363 | -0.0040567 | 0.065262 | 0.067396 | -0.20233 | -0.0036936 | 120.3232 | -1.1261 | 2.4307 | -1.0895 | 120.1126 | -1.181 | -1.2405 | -1.1398 | 3.7765 | -1.2314 | 120.0668 | 120.2362 | -1.1169 | -1.1536 | 0.091553 | 0.032043 | -0.19226 | 0.14648 | 0.18311 | 0.15106 | 0.01831 | 0.15564 | 0.11902 | -0.23804 | 0.13275 | 0.041199 | -0.07782 | -0.068665 | 121.3852 | 121.5958 | 3.7033 | -121.5454 | 121.3394 | 121.5088 | 5.0491 | -121.4584
854.5781 | 121.6553 | -1.2589 | 120.3278 | -0.012589 | 0.0018777 | 0.063692 | 0.0040246 | 0.065193 | -0.0046313 | -0.0014569 | -0.013123 | -0.0053385 | 0.065262 | 0.066542 | -0.20212 | -0.0021982 | 120.3323 | -1.0986 | 2.4445 | -1.0895 | 120.1584 | -1.1673 | -1.2131 | -1.1444 | 3.7903 | -1.2222 | 120.0851 | 120.2316 | -1.1078 | -1.1536 | 0.091553 | 0.045776 | -0.16937 | 0.16022 | 0.16937 | 0.1236 | 0.004577 | 0.15106 | 0.10529 | -0.24262 | 0.11444 | 0.036621 | -0.068665 | -0.096131 | 121.4172 | 121.5912 | 3.7033 | -121.5408 | 121.344 | 121.4905 | 5.0491 | -121.4813
856.2656 | 121.6278 | -1.2543 | 120.3598 | 0.0026703 | 0.0035867 | 0.066683 | 0.0040246 | 0.069039 | -0.0018543 | -0.00060234 | 0.0021363 | -0.0049111 | 0.063126 | 0.068678 | -0.20041 | -0.0036936 | 120.3735 | -1.0757 | 2.4628 | -1.0483 | 120.195 | -1.1261 | -1.1856 | -1.1032 | 3.7949 | -1.1902 | 120.1309 | 120.2316 | -1.062 | -1.1215 | 0.12817 | 0.068664 | -0.16479 | 0.17853 | 0.20599 | 0.13733 | 0.013733 | 0.19226 | 0.13275 | -0.22888 | 0.15106 | 0.064086 | -0.068665 | -0.12817 | 121.4493 | 121.6278 | 3.717 | -121.5454 | 121.3852 | 121.4859 | 5.0491 | -121.4813
858.0312 | 121.6507 | -1.2268 | 120.369 | -0.012589 | 0.0042275 | 0.06241 | -0.001316 | 0.066902 | 0.0043409 | 0.00067926 | -0.0054932 | -0.00063872 | 0.063553 | 0.0706 | -0.19656 | -0.0036936 | 120.3232 | -1.1765 | 2.3941 | -1.0941 | 120.2591 | -1.1398 | -1.2039 | -1.149 | 3.7399 | -1.2817 | 120.1859 | 120.3094 | -1.0941 | -1.1261 | 0.086975 | 0.022889 | -0.10986 | 0.050354 | 0.13275 | 0.10986 | -0.045777 | 0.13275 | 0.10071 | -0.18311 | 0.07782 | -0.054931 | -0.15564 | -0.05951 | 121.4859 | 121.55 | 3.6209 | -121.5729 | 121.4127 | 121.5363 | 4.9667 | -121.4951
859.7969 | 121.7056 | -1.1856 | 120.3506 | -0.012589 | -0.00068567 | 0.066896 | -0.0011024 | 0.066262 | -0.0056995 | 3.8456e-05 | -0.0054932 | -0.0066201 | 0.063766 | 0.064619 | -0.19891 | -0.0026254 | 120.4102 | -1.0391 | 2.4673 | -1.0162 | 120.2225 | -1.1169 | -1.1581 | -1.0757 | 3.8177 | -1.1261 | 120.1538 | 120.2911 | -1.0437 | -1.1032 | 0.068665 | 0.027466 | -0.12817 | 0.14648 | 0.16937 | 0.14191 | 0.059509 | 0.14191 | 0.082398 | -0.19684 | 0.10986 | 0.059509 | -0.022889 | -0.059509 | 121.4081 | 121.5958 | 3.653 | -121.5088 | 121.3394 | 121.4767 | 5.0034 | -121.4539
861.5469 | 121.6919 | -1.1536 | 120.4102 | 0.0026703 | -0.0032493 | 0.064546 | -0.00088858 | 0.068611 | -0.0033495 | 0.00046566 | 0.0021363 | -0.0036295 | 0.061844 | 0.065687 | -0.2019 | -0.00113 | 120.4514 | -0.97961 | 2.4994 | -0.97504 | 120.2545 | -1.0666 | -1.1032 | -1.0391 | 3.8406 | -1.1307 | 120.2042 | 120.3415 | -1.0162 | -1.0712 | 0.086975 | 0.050354 | -0.15564 | 0.17395 | 0.17853 | 0.12817 | 0.041199 | 0.13733 | 0.082397 | -0.20599 | 0.11444 | 0.022888 | -0.059509 | -0.068664 | 121.4081 | 121.6049 | 3.653 | -121.5134 | 121.3577 | 121.4951 | 4.9942 | -121.4813
863.2969 | 121.5912 | -1.181 | 120.4514 | -0.0049592 | 0.0061501 | 0.065187 | 0.0027428 | 0.066689 | 0.0015637 | -0.0014569 | -0.0054932 | 0.00085668 | 0.064621 | 0.06825 | -0.19955 | -0.0039072 | 120.3827 | -1.1353 | 2.4078 | -1.0712 | 120.2957 | -1.0849 | -1.1536 | -1.1536 | 3.7628 | -1.2543 | 120.2774 | 120.3918 | -1.0437 | -1.0849 | 0.09613 | 0.027466 | -0.15564 | 0.045776 | 0.10986 | 0.082397 | -0.068665 | 0.13733 | 0.09613 | -0.17395 | 0.027466 | -0.073242 | -0.16937 | -0.059509 | 121.4767 | 121.5637 | 3.5889 | -121.6049 | 121.4584 | 121.5729 | 4.9438 | -121.5363
865.0156 | 121.6278 | -1.1581 | 120.4651 | 0.0026703 | 0.0065775 | 0.065828 | -0.00046138 | 0.06733 | 0.00070927 | -0.00081594 | -0.013123 | -0.00063872 | 0.06633 | 0.066114 | -0.19592 | -0.0024118 | 120.3918 | -1.1215 | 2.4216 | -1.0391 | 120.3094 | -1.0895 | -1.1261 | -1.0986 | 3.7949 | -1.2177 | 120.2866 | 120.4056 | -1.0071 | -1.062 | 0.068664 | 0.032043 | -0.15564 | 0.036621 | 0.11902 | 0.086975 | -0.073242 | 0.15106 | 0.09613 | -0.17853 | 0.059509 | -0.059509 | -0.15564 | -0.059509 | 121.4676 | 121.55 | 3.5797 | -121.5912 | 121.4447 | 121.5637 | 4.953 | -121.5271
866.7812 | 121.5775 | -1.1673 | 120.4788 | -0.0049592 | 0.0046549 | 0.065828 | -0.003025 | 0.065834 | 0.0034863 | 0.0015339 | -0.0054932 | 0.00064308 | 0.065689 | 0.066969 | -0.19635 | -0.0036936 | 120.4193 | -1.1261 | 2.417 | -1.0391 | 120.3369 | -1.0666 | -1.1215 | -1.0986 | 3.7491 | -1.2634 | 120.2774 | 120.401 | -1.03 | -1.0483 | 0.10071 | 0.045776 | -0.14191 | 0.041198 | 0.12817 | 0.082397 | -0.059509 | 0.13733 | 0.11902 | -0.20142 | 0.068664 | -0.096131 | -0.21515 | -0.07782 | 121.5042 | 121.5866 | 3.5843 | -121.6003 | 121.4447 | 121.5683 | 4.9164 | -121.5271
868.5469 | 121.6873 | -1.0666 | 120.5109 | -0.0049592 | -0.0019675 | 0.067323 | -0.00024778 | 0.066048 | -0.0048449 | 0.00046566 | -0.0054932 | -0.0057657 | 0.064621 | 0.067182 | -0.20126 | 0.001647 | 120.4651 | -0.96588 | 2.449 | -0.93384 | 120.3552 | -0.9613 | -1.0391 | -1.0254 | 3.8223 | -1.0941 | 120.3003 | 120.4102 | -0.93842 | -0.97046 | 0.10528 | 0.027465 | -0.15564 | 0.10071 | 0.13275 | 0.10529 | -0.045776 | 0.12817 | 0.09613 | -0.21057 | 0.041198 | -0.027466 | -0.1236 | -0.10071 | 121.4218 | 121.5317 | 3.5156 | -121.55 | 121.3669 | 121.4767 | 4.8889 | -121.4813
870.2969 | 121.6003 | -1.0529 | 120.5612 | -0.0049592 | 0.0063639 | 0.067537 | 0.0046656 | 0.066902 | -0.0024951 | -0.00017514 | -0.013123 | -0.0036295 | 0.066544 | 0.067823 | -0.20382 | 0.00015159 | 120.575 | -0.90179 | 2.5589 | -0.85144 | 120.4102 | -0.92926 | -1.0025 | -0.95673 | 3.9276 | -1.0529 | 120.3552 | 120.4926 | -0.90179 | -0.93384 | 0.1236 | 0.050354 | -0.15106 | 0.15106 | 0.20142 | 0.15106 | 0.013733 | 0.15106 | 0.11902 | -0.20599 | 0.09613 | 0 | -0.11902 | -0.068664 | 121.463 | 121.6278 | 3.6118 | -121.5637 | 121.4081 | 121.5454 | 4.9805 | -121.4951
872 | 121.6141 | -1.0712 | 120.5795 | 0.0026703 | 0.0055093 | 0.061983 | 0.0040246 | 0.066262 | 0.00070927 | -0.00060234 | 0.0021363 | -0.0023477 | 0.066971 | 0.067396 | -0.20126 | -0.0036936 | 120.4697 | -1.0162 | 2.4902 | -0.94299 | 120.4651 | -0.9613 | -1.03 | -1.0162 | 3.8727 | -1.1353 | 120.433 | 120.4697 | -0.9201 | -0.95673 | 0.10986 | 0.041199 | -0.11444 | 0.054932 | 0.12817 | 0.086975 | -0.10986 | 0.15106 | 0.11444 | -0.14648 | 0.054932 | -0.064087 | -0.17853 | -0.10986 | 121.5363 | 121.5408 | 3.5614 | -121.6095 | 121.5042 | 121.5408 | 4.9438 | -121.5363
873.7656 | 121.7056 | -0.96588 | 120.6024 | -0.0049592 | 0.0025185 | 0.063478 | -3.4178e-05 | 0.067543 | 0.0011365 | 0.0017475 | -0.013123 | 0.00064308 | 0.064407 | 0.067823 | -0.19955 | -0.0032662 | 120.5475 | -0.97504 | 2.4216 | -0.87891 | 120.4926 | -0.88806 | -0.97504 | -0.92926 | 3.8452 | -1.0483 | 120.4605 | 120.5566 | -0.84228 | -0.89722 | 0.077819 | -0.009156 | -0.10986 | -0.009156 | 0.086975 | 0.096131 | -0.054932 | 0.1236 | 0.068664 | -0.14191 | 0.036621 | -0.082398 | -0.15106 | -0.045776 | 121.4584 | 121.5134 | 3.3875 | -121.5775 | 121.4264 | 121.5225 | 4.8111 | -121.4996
875.4844 | 121.6461 | -0.94299 | 120.6757 | -0.0049592 | 0.0052957 | 0.06476 | -0.00024778 | 0.067971 | 0.0028455 | 0.0015339 | -0.013123 | -0.00063872 | 0.06633 | 0.069746 | -0.1987 | -0.0034798 | 120.6116 | -0.88348 | 2.5635 | -0.80566 | 120.5383 | -0.85144 | -0.95673 | -0.8606 | 3.9734 | -0.98419 | 120.4559 | 120.607 | -0.82398 | -0.86975 | 0.091553 | -0.013733 | -0.13733 | 0.059509 | 0.13733 | 0.15106 | -0.064087 | 0.11902 | 0.073242 | -0.21973 | 0.082397 | -0.041199 | -0.11444 | -0.068664 | 121.4813 | 121.5546 | 3.5065 | -121.6324 | 121.3989 | 121.55 | 4.9164 | -121.5454
877.25 | 121.669 | -0.91095 | 120.6757 | 0.0103 | -0.00025847 | 0.066683 | -0.0015296 | 0.066262 | -0.0054859 | -0.00060234 | -0.0054932 | -0.0061929 | 0.063553 | 0.066114 | -0.20083 | 0.00015159 | 120.6299 | -0.80109 | 2.536 | -0.75989 | 120.5109 | -0.80109 | -0.86975 | -0.83771 | 3.9185 | -0.92926 | 120.4559 | 120.5841 | -0.75989 | -0.81024 | 0.10986 | 0.041199 | -0.16479 | 0.10986 | 0.15106 | 0.10986 | -0.045776 | 0.15106 | 0.10071 | -0.21973 | 0.073242 | -0.01831 | -0.11902 | -0.091553 | 121.4218 | 121.5408 | 3.447 | -121.5454 | 121.3669 | 121.4951 | 4.8294 | -121.4859
879.0312 | 121.6003 | -0.89722 | 120.7031 | 0.0026703 | 0.0044411 | 0.066469 | 0.0016748 | 0.062844 | 6.8274e-05 | 0.00025206 | -0.013123 | -0.0029885 | 0.064407 | 0.066969 | -0.20062 | -0.0030526 | 120.639 | -0.83313 | 2.5589 | -0.78735 | 120.5978 | -0.82398 | -0.88806 | -0.87433 | 3.9459 | -0.95673 | 120.5383 | 120.6619 | -0.7782 | -0.79193 | 0.073242 | 0.009155 | -0.10529 | 0.064087 | 0.10986 | 0.10071 | -0.064087 | 0.11902 | 0.10529 | -0.16479 | 0.022888 | -0.059509 | -0.16479 | -0.041199 | 121.4951 | 121.5363 | 3.4561 | -121.5912 | 121.4355 | 121.5591 | 4.8431 | -121.4951
880.8125 | 121.6324 | -0.89722 | 120.7214 | 0.0026703 | 0.0046549 | 0.066469 | 0.001034 | 0.064553 | -0.00014533 | 0.00025206 | -0.013123 | -0.0032021 | 0.065475 | 0.066542 | -0.20019 | -0.0036936 | 120.639 | -0.8606 | 2.5635 | -0.77362 | 120.6207 | -0.82855 | -0.87891 | -0.87433 | 3.9642 | -0.97961 | 120.5429 | 120.6482 | -0.75073 | -0.80566 | 0.068665 | 0.018311 | -0.10071 | 0.036621 | 0.1236 | 0.10528 | -0.082398 | 0.14649 | 0.091553 | -0.17853 | 0.022888 | -0.082397 | -0.17395 | -0.073243 | 121.5179 | 121.5363 | 3.4607 | -121.6003 | 121.4401 | 121.5454 | 4.8615 | -121.5271
882.5156 | 121.7239 | -0.82398 | 120.694 | 0.0026703 | 0.0025185 | 0.06476 | -0.00088858 | 0.065193 | 0.00049567 | 0.0030293 | -0.0054932 | -0.0034159 | 0.06633 | 0.068464 | -0.20019 | -0.0021982 | 120.7031 | -0.79193 | 2.5681 | -0.71411 | 120.575 | -0.75531 | -0.85144 | -0.737 | 4.0146 | -0.8606 | 120.5063 | 120.6162 | -0.72784 | -0.74158 | 0.068665 | -0.027465 | -0.11902 | 0.032044 | 0.10986 | 0.13733 | 0.009155 | 0.096131 | 0.082398 | -0.18768 | 0.086975 | -0.036621 | -0.11902 | -0.07782 | 121.3989 | 121.5271 | 3.392 | -121.5454 | 121.3303 | 121.4401 | 4.8386 | -121.4355
884.2812 | 121.6141 | -0.87433 | 120.726 | -0.0049592 | 0.0035867 | 0.06241 | -0.00046138 | 0.065407 | 0.0026319 | 0.0023883 | 0.0021363 | -0.00063872 | 0.06633 | 0.068678 | -0.19827 | -0.0024118 | 120.6482 | -0.88348 | 2.5177 | -0.76904 | 120.6345 | -0.78735 | -0.84228 | -0.83771 | 3.9505 | -0.95215 | 120.5521 | 120.6757 | -0.74158 | -0.7782 | 0.086975 | 0.032044 | -0.091553 | -0.009155 | 0.10529 | 0.073242 | -0.07782 | 0.13275 | 0.096131 | -0.17395 | 0.036621 | -0.077819 | -0.17395 | -0.050354 | 121.5088 | 121.5225 | 3.392 | -121.5683 | 121.4264 | 121.55 | 4.8248 | -121.5042
886.0469 | 121.6736 | -0.84228 | 120.7443 | 0.0026703 | 0.0035867 | 0.066683 | 0.0044518 | 0.064553 | -0.0052721 | 0.00046566 | 0.0021363 | -0.0046975 | 0.065689 | 0.067396 | -0.20489 | -0.0021982 | 120.7626 | -0.67749 | 2.7237 | -0.65918 | 120.5658 | -0.737 | -0.80109 | -0.71411 | 4.1336 | -0.80109 | 120.5246 | 120.6528 | -0.6958 | -0.72784 | 0.10528 | 0.041199 | -0.17853 | 0.16479 | 0.1831 | 0.14191 | 0.01831 | 0.14648 | 0.11444 | -0.21973 | 0.12817 | 0.041199 | -0.073242 | -0.091553 | 121.4081 | 121.6049 | 3.566 | -121.5454 | 121.3669 | 121.4951 | 4.9759 | -121.4722
887.75 | 121.6827 | -0.81482 | 120.7352 | 0.0026703 | 0.00059593 | 0.064974 | 0.00039302 | 0.069466 | -0.00014533 | 0.0013203 | 0.0021363 | -0.0046975 | 0.065689 | 0.06761 | -0.19827 | -0.0026254 | 120.7901 | -0.68207 | 2.655 | -0.64545 | 120.5933 | -0.71411 | -0.7782 | -0.66834 | 4.097 | -0.78735 | 120.5338 | 120.6757 | -0.68207 | -0.71411 | 0.10071 | 0.036621 | -0.14191 | 0.13275 | 0.16937 | 0.13275 | 0.054932 | 0.13275 | 0.10071 | -0.20142 | 0.14648 | 0.027465 | -0.073243 | -0.059509 | 121.4081 | 121.6049 | 3.4698 | -121.5134 | 121.3486 | 121.4905 | 4.9118 | -121.4493
889.5 | 121.6278 | -0.80566 | 120.8221 | -0.0049592 | 0.0046549 | 0.064333 | -0.00024778 | 0.067543 | 0.0054089 | 0.0026019 | -0.0054932 | -0.0017069 | 0.064407 | 0.068037 | -0.20019 | -0.0019846 | 120.7718 | -0.737 | 2.6917 | -0.66376 | 120.6757 | -0.72784 | -0.79651 | -0.70496 | 4.1107 | -0.85144 | 120.5933 | 120.6894 | -0.68665 | -0.71411 | 0.07782 | 0.009155 | -0.14648 | 0.068664 | 0.14191 | 0.13275 | -0.050354 | 0.11902 | 0.091553 | -0.22888 | 0.10071 | -0.045776 | -0.13733 | -0.13275 | 121.4813 | 121.5775 | 3.4973 | -121.6187 | 121.3989 | 121.4951 | 4.9164 | -121.5363
891.2812 | 121.582 | -0.82398 | 120.8176 | 0.0026703 | 0.0070047 | 0.064333 | 0.00017942 | 0.064339 | 0.0034863 | 0.0028155 | -0.0054932 | -0.0014933 | 0.066757 | 0.069746 | -0.19635 | -0.002839 | 120.7169 | -0.76904 | 2.6413 | -0.6958 | 120.6711 | -0.71411 | -0.78735 | -0.77362 | 4.0375 | -0.91095 | 120.6482 | 120.7169 | -0.68665 | -0.70953 | 0.10986 | 0.036621 | -0.14648 | 0.054932 | 0.12817 | 0.091553 | -0.10071 | 0.13733 | 0.11444 | -0.16937 | 0.050354 | -0.086975 | -0.20142 | -0.10071 | 121.4951 | 121.5408 | 3.4653 | -121.6049 | 121.4722 | 121.5408 | 4.8615 | -121.5271
893.0469 | 121.7239 | -0.76446 | 120.8038 | 0.0026703 | 0.00059593 | 0.06711 | 0.0014612 | 0.064339 | -0.0052721 | 0.0015339 | 0.0021363 | -0.0049111 | 0.062271 | 0.065687 | -0.20254 | -0.00113 | 120.7489 | -0.6958 | 2.6596 | -0.62714 | 120.6711 | -0.65918 | -0.72784 | -0.71869 | 4.0924 | -0.77362 | 120.5978 | 120.7535 | -0.63629 | -0.66376 | 0.10528 | 0.036621 | -0.13275 | 0.068664 | 0.13733 | 0.10071 | -0.054932 | 0.12817 | 0.10071 | -0.20599 | 0.045776 | -0.009156 | -0.10986 | -0.050354 | 121.4355 | 121.5134 | 3.4241 | -121.5317 | 121.3623 | 121.5179 | 4.8569 | -121.4676
894.7656 | 121.7422 | -0.75531 | 120.8176 | -0.0049592 | 0.0040139 | 0.066255 | 0.0033838 | 0.066689 | -0.0037769 | 0.00089286 | -0.0054932 | -0.0061929 | 0.066544 | 0.067182 | -0.20297 | -0.0024118 | 120.7993 | -0.63171 | 2.71 | -0.59052 | 120.694 | -0.6546 | -0.72327 | -0.66376 | 4.1656 | -0.71869 | 120.6345 | 120.7352 | -0.6134 | -0.64087 | 0.10071 | 0.032043 | -0.1236 | 0.1236 | 0.1648 | 0.13275 | -0.018311 | 0.14191 | 0.11444 | -0.18311 | 0.091553 | 0.036621 | -0.07782 | -0.082398 | 121.4493 | 121.5546 | 3.4653 | -121.5408 | 121.3898 | 121.4905 | 4.921 | -121.4584
896.5156 | 121.7377 | -0.73242 | 120.8359 | -0.012589 | 0.0016641 | 0.066469 | 0.00082022 | 0.069252 | -0.0039905 | -0.0016705 | -0.0054932 | -0.0053385 | 0.063339 | 0.06761 | -0.20233 | -0.0036936 | 120.8725 | -0.5722 | 2.7695 | -0.56305 | 120.7077 | -0.62714 | -0.71411 | -0.60425 | 4.2389 | -0.67291 | 120.6207 | 120.7581 | -0.5722 | -0.6134 | 0.10529 | 0.018311 | -0.12817 | 0.16022 | 0.16937 | 0.15106 | 0.036622 | 0.16022 | 0.11902 | -0.21515 | 0.12817 | 0.059509 | -0.05951 | -0.077819 | 121.4401 | 121.6049 | 3.5019 | -121.55 | 121.3531 | 121.4905 | 4.9713 | -121.4493
898.2812 | 121.7148 | -0.71411 | 120.8359 | -0.012589 | 0.0018777 | 0.063051 | -0.0017432 | 0.065621 | 0.0032727 | 0.0011067 | 0.0021363 | -0.00085232 | 0.06633 | 0.068037 | -0.19763 | -0.0058298 | 120.7993 | -0.70496 | 2.6733 | -0.63629 | 120.7031 | -0.65918 | -0.72327 | -0.65002 | 4.1611 | -0.76446 | 120.6482 | 120.7306 | -0.6134 | -0.65002 | 0.054931 | -0.009156 | -0.13275 | 0.009155 | 0.077819 | 0.086975 | -0.036621 | 0.10071 | 0.064087 | -0.18768 | 0.064087 | -0.050354 | -0.11444 | -0.10528 | 121.4172 | 121.5134 | 3.3875 | -121.5591 | 121.3623 | 121.4447 | 4.8752 | -121.4859
899.9844 | 121.6415 | -0.7782 | 120.8221 | -0.0049592 | 0.0046549 | 0.064333 | -0.00046138 | 0.068611 | 0.0043409 | 0.0017475 | -0.0054932 | -0.00085232 | 0.066757 | 0.069532 | -0.19806 | -0.0047616 | 120.8313 | -0.67749 | 2.7695 | -0.59967 | 120.7306 | -0.66376 | -0.74158 | -0.65918 | 4.2252 | -0.80109 | 120.6757 | 120.8038 | -0.62714 | -0.65918 | 0.11444 | 0.036621 | -0.091553 | 0.10071 | 0.17853 | 0.14191 | 0.009155 | 0.15106 | 0.11902 | -0.14648 | 0.11902 | -0.022888 | -0.14191 | -0.018311 | 121.5088 | 121.6095 | 3.5477 | -121.5637 | 121.4539 | 121.582 | 5.0034 | -121.4813
901.7656 | 121.6599 | -0.74158 | 120.8405 | -0.0049592 | 0.0016641 | 0.066255 | 0.002102 | 0.067971 | -0.0029223 | -0.00017514 | 0.0021363 | -0.0061929 | 0.065475 | 0.065901 | -0.19998 | -0.00091641 | 120.8725 | -0.54932 | 2.861 | -0.54474 | 120.694 | -0.60883 | -0.67749 | -0.59052 | 4.2847 | -0.69122 | 120.6436 | 120.7535 | -0.5722 | -0.61798 | 0.13275 | 0.064087 | -0.14648 | 0.19226 | 0.19684 | 0.13275 | 0.032044 | 0.16937 | 0.1236 | -0.19684 | 0.15106 | 0.050354 | -0.073242 | -0.086975 | 121.4355 | 121.6141 | 3.6026 | -121.5179 | 121.3852 | 121.4951 | 5.0262 | -121.4584
903.5156 | 121.6919 | -0.73242 | 120.8405 | -0.012589 | 0.0010233 | 0.068178 | 0.00039302 | 0.065834 | -0.0029223 | -0.00017514 | -0.0054932 | -0.0061929 | 0.063339 | 0.065901 | -0.19998 | -0.0013436 | 120.8313 | -0.64545 | 2.7374 | -0.58594 | 120.726 | -0.62256 | -0.69122 | -0.65918 | 4.1931 | -0.737 | 120.6345 | 120.7718 | -0.60425 | -0.63171 | 0.10986 | 0.041199 | -0.11444 | 0.086975 | 0.14648 | 0.10529 | -0.009155 | 0.12817 | 0.10071 | -0.20599 | 0.073242 | -0.004578 | -0.10529 | -0.068664 | 121.4584 | 121.5637 | 3.4698 | -121.5317 | 121.3669 | 121.5042 | 4.9255 | -121.4722
905.2188 | 121.6049 | -0.74158 | 120.8771 | -0.0049592 | 0.0055093 | 0.064119 | 0.0012476 | 0.06733 | 0.0043409 | 0.0017475 | 0.0021363 | 0.00042948 | 0.066971 | 0.067182 | -0.1987 | -0.0047616 | 120.8725 | -0.66376 | 2.8107 | -0.59509 | 120.7764 | -0.65002 | -0.75073 | -0.63629 | 4.2572 | -0.76446 | 120.6757 | 120.7764 | -0.60425 | -0.63629 | 0.091553 | -0.009155 | -0.10071 | 0.07782 | 0.14648 | 0.15564 | -0.004577 | 0.13733 | 0.10529 | -0.20142 | 0.10529 | -0.022888 | -0.12817 | -0.10071 | 121.5179 | 121.6141 | 3.5522 | -121.6278 | 121.4172 | 121.5179 | 4.9988 | -121.5134
906.9844 | 121.5958 | -0.75989 | 120.8862 | -0.012589 | 0.0038003 | 0.064333 | -0.0011024 | 0.065193 | 0.0034863 | 0.0030293 | -0.0054932 | -0.0027749 | 0.065903 | 0.067823 | -0.19677 | -0.0021982 | 120.8084 | -0.71869 | 2.7512 | -0.6134 | 120.7718 | -0.64087 | -0.737 | -0.70038 | 4.1656 | -0.83771 | 120.726 | 120.8221 | -0.60425 | -0.64087 | 0.11902 | 0.022888 | -0.11444 | 0.041199 | 0.14648 | 0.1236 | -0.077819 | 0.15564 | 0.11902 | -0.16022 | 0.05951 | -0.07782 | -0.19684 | -0.064086 | 121.5317 | 121.5683 | 3.511 | -121.6232 | 121.4859 | 121.582 | 4.9255 | -121.5271
908.7656 | 121.6965 | -0.70953 | 120.8313 | -0.0049592 | 0.0042275 | 0.066255 | 0.0040246 | 0.065193 | -0.0037769 | 0.00046566 | -0.0054932 | -0.0055521 | 0.065048 | 0.064833 | -0.20041 | -0.00070281 | 120.9 | -0.52185 | 2.9022 | -0.52643 | 120.7123 | -0.6134 | -0.6958 | -0.58594 | 4.3533 | -0.6546 | 120.6436 | 120.7581 | -0.55847 | -0.6134 | 0.096131 | 0.013733 | -0.11902 | 0.18768 | 0.18311 | 0.16937 | 0.068664 | 0.15106 | 0.096131 | -0.18768 | 0.1236 | 0.054932 | -0.041199 | -0.073242 | 121.4218 | 121.6095 | 3.6118 | -121.5271 | 121.3531 | 121.4676 | 5.0629 | -121.4447
910.4844 | 121.7102 | -0.70953 | 120.8817 | 0.0026703 | 0.00080973 | 0.064333 | 0.00082022 | 0.063698 | 0.0028455 | 0.0015339 | 0.0021363 | 0.00021568 | 0.065048 | 0.068891 | -0.19848 | -0.0030526 | 120.8176 | -0.70953 | 2.7466 | -0.59967 | 120.7855 | -0.64545 | -0.70953 | -0.68207 | 4.2023 | -0.79193 | 120.7169 | 120.813 | -0.58594 | -0.62256 | 0.064087 | 0 | -0.096131 | 0 | 0.10986 | 0.10986 | -0.064087 | 0.1236 | 0.086975 | -0.16479 | 0.027466 | -0.082397 | -0.16937 | -0.068665 | 121.4951 | 121.5271 | 3.4561 | -121.5912 | 121.4264 | 121.5225 | 4.9118 | -121.5042
912.2344 | 121.7377 | -0.70038 | 120.845 | -0.0049592 | 0.0012369 | 0.065828 | 0.0044518 | 0.068825 | -0.0046313 | -0.00060234 | -0.013123 | -0.0070475 | 0.066116 | 0.063764 | -0.20126 | -0.0024118 | 120.9045 | -0.53558 | 2.9068 | -0.52185 | 120.7169 | -0.59967 | -0.66834 | -0.57678 | 4.3945 | -0.63171 | 120.6619 | 120.7718 | -0.55847 | -0.59052 | 0.10071 | 0.032043 | -0.12817 | 0.16479 | 0.17853 | 0.14648 | 0.059509 | 0.14191 | 0.10986 | -0.18311 | 0.1236 | 0.068664 | -0.041199 | -0.073242 | 121.4172 | 121.6049 | 3.6072 | -121.5134 | 121.3623 | 121.4722 | 5.0949 | -121.4355
914 | 121.7377 | -0.69122 | 120.8588 | 0.0026703 | 0.0023049 | 0.069246 | 0.0035974 | 0.067543 | -0.0044177 | -0.0027387 | -0.0054932 | -0.0046975 | 0.06398 | 0.066328 | -0.20169 | -0.0047616 | 120.9183 | -0.54932 | 2.916 | -0.50354 | 120.7489 | -0.59967 | -0.65918 | -0.55389 | 4.39 | -0.64087 | 120.6802 | 120.7947 | -0.55847 | -0.58136 | 0.091553 | 0.032043 | -0.10986 | 0.14191 | 0.18768 | 0.15564 | 0.059509 | 0.13275 | 0.10986 | -0.17853 | 0.13733 | 0.050354 | -0.059509 | -0.064087 | 121.4401 | 121.6095 | 3.6072 | -121.5179 | 121.3715 | 121.4859 | 5.0812 | -121.4401
915.7031 | 121.7239 | -0.69122 | 120.8771 | -0.0049592 | 0.0052957 | 0.065401 | 0.0035974 | 0.067757 | -0.0024951 | -0.0010297 | 0.0021363 | -0.0038431 | 0.067612 | 0.067823 | -0.20126 | -0.0032662 | 120.9183 | -0.56305 | 2.9205 | -0.52185 | 120.7397 | -0.60425 | -0.66834 | -0.5722 | 4.3854 | -0.6546 | 120.7031 | 120.7855 | -0.53101 | -0.5722 | 0.086975 | 0.022888 | -0.13733 | 0.12817 | 0.16937 | 0.14648 | 0.041199 | 0.16022 | 0.11902 | -0.17395 | 0.11902 | 0.036621 | -0.082397 | -0.091553 | 121.431 | 121.6095 | 3.6118 | -121.5454 | 121.3943 | 121.4767 | 5.0766 | -121.4493
917.4531 | 121.5912 | -0.70953 | 120.9229 | 0.0026703 | 0.0076455 | 0.063265 | 0.0025292 | 0.068398 | 0.0045545 | 0.0032429 | -0.0054932 | 0.00021568 | 0.066971 | 0.069746 | -0.1972 | -0.006257 | 120.8725 | -0.67749 | 2.8473 | -0.58136 | 120.7993 | -0.6134 | -0.67291 | -0.64545 | 4.2847 | -0.81482 | 120.7535 | 120.8588 | -0.5722 | -0.62256 | 0.096131 | 0.036621 | -0.1236 | 0.032044 | 0.12817 | 0.091553 | -0.050354 | 0.13733 | 0.086975 | -0.16937 | 0.064087 | -0.10528 | -0.19226 | -0.064087 | 121.5088 | 121.582 | 3.5568 | -121.5958 | 121.463 | 121.5683 | 4.9942 | -121.5454
919.2188 | 121.7422 | -0.68207 | 120.845 | 0.0026703 | 0.0018777 | 0.067323 | 0.001034 | 0.063912 | -0.0056995 | -0.00060234 | 0.0021363 | -0.0046975 | 0.064407 | 0.067823 | -0.2034 | -0.0024118 | 120.8817 | -0.59052 | 2.9022 | -0.53558 | 120.7443 | -0.59967 | -0.64545 | -0.58594 | 4.3945 | -0.66376 | 120.6619 | 120.8267 | -0.54932 | -0.56763 | 0.082398 | 0.036621 | -0.10071 | 0.091553 | 0.14648 | 0.10986 | 0.036621 | 0.13275 | 0.11444 | -0.18311 | 0.096131 | 0.018311 | -0.09613 | -0.018311 | 121.4264 | 121.5637 | 3.5843 | -121.4905 | 121.344 | 121.5088 | 5.0766 | -121.4127
920.9375 | 121.6461 | -0.68665 | 120.9274 | -0.0049592 | 0.0027323 | 0.064974 | -0.0017432 | 0.067971 | 0.0043409 | 0.0030293 | 0.0021363 | 0.0017111 | 0.065475 | 0.068891 | -0.1972 | -0.0060434 | 120.9 | -0.64545 | 2.9434 | -0.55847 | 120.8176 | -0.59967 | -0.66376 | -0.59509 | 4.4449 | -0.75073 | 120.7489 | 120.8817 | -0.57678 | -0.58136 | 0.086976 | 0.022889 | -0.10986 | 0.041199 | 0.12817 | 0.10529 | -0.027466 | 0.10986 | 0.10529 | -0.17853 | 0.091553 | -0.064086 | -0.16937 | -0.045776 | 121.5042 | 121.5866 | 3.6301 | -121.5912 | 121.4355 | 121.5683 | 5.1315 | -121.5088
922.7031 | 121.5912 | -0.6958 | 120.9732 | -0.0049592 | 0.0033731 | 0.066042 | -0.00024778 | 0.065834 | 0.0034863 | 0.0028155 | -0.0054932 | 0.00085668 | 0.065475 | 0.066969 | -0.19699 | -0.0039072 | 120.932 | -0.59509 | 2.9526 | -0.53101 | 120.813 | -0.56763 | -0.65002 | -0.5722 | 4.3945 | -0.75073 | 120.7581 | 120.8908 | -0.53101 | -0.5722 | 0.12817 | 0.045777 | -0.16022 | 0.10071 | 0.1648 | 0.11902 | -0.041199 | 0.1648 | 0.1236 | -0.21515 | 0.1236 | -0.054931 | -0.17853 | -0.082398 | 121.5088 | 121.6278 | 3.6484 | -121.6232 | 121.4539 | 121.5866 | 5.0903 | -121.5454
924.3906 | 121.5912 | -0.68665 | 120.9641 | -0.012589 | 0.0040139 | 0.065614 | 0.0046656 | 0.067971 | -0.0052721 | 0.0013203 | 0.0021363 | -0.0034159 | 0.064621 | 0.067396 | -0.20254 | -0.00027561 | 120.9091 | -0.55847 | 2.9984 | -0.49896 | 120.7901 | -0.58594 | -0.64087 | -0.62256 | 4.4174 | -0.70953 | 120.7718 | 120.8908 | -0.54016 | -0.57678 | 0.10071 | 0.045777 | -0.17395 | 0.12817 | 0.18768 | 0.14191 | -0.054931 | 0.14648 | 0.10986 | -0.19226 | 0.064087 | -0.022888 | -0.13275 | -0.073242 | 121.4767 | 121.5958 | 3.685 | -121.6049 | 121.4584 | 121.5775 | 5.1041 | -121.5408
926.1562 | 121.7377 | -0.61798 | 120.9366 | -0.0049592 | 0.0014505 | 0.066896 | 0.0012476 | 0.067116 | -0.0056995 | -0.00038874 | -0.0054932 | -0.0046975 | 0.064621 | 0.067823 | -0.20105 | -0.00113 | 120.9045 | -0.56305 | 2.948 | -0.50354 | 120.8176 | -0.55847 | -0.6134 | -0.56763 | 4.4403 | -0.62714 | 120.7352 | 120.8954 | -0.51727 | -0.54474 | 0.059509 | 0.004578 | -0.11902 | 0.054932 | 0.11444 | 0.10986 | -0.032043 | 0.10071 | 0.073242 | -0.20142 | 0.050354 | -0.009155 | -0.082397 | -0.041198 | 121.4355 | 121.5225 | 3.566 | -121.55 | 121.3531 | 121.5134 | 5.0583 | -121.4813
927.9062 | 121.5958 | -0.66376 | 120.9732 | -0.012589 | 0.0055093 | 0.065401 | 0.00082022 | 0.068825 | -0.0016405 | -0.00081594 | 0.0021363 | -0.0017069 | 0.064407 | 0.068464 | -0.20041 | -0.0041208 | 120.8908 | -0.63629 | 2.98 | -0.54474 | 120.8405 | -0.55847 | -0.63171 | -0.6134 | 4.4037 | -0.71411 | 120.7901 | 120.9183 | -0.51727 | -0.55847 | 0.10529 | 0.032043 | -0.13275 | 0.027465 | 0.11902 | 0.086975 | -0.082398 | 0.14648 | 0.10529 | -0.18311 | 0.050354 | -0.050354 | -0.15564 | -0.054932 | 121.5042 | 121.5546 | 3.6438 | -121.6049 | 121.4539 | 121.582 | 5.0674 | -121.5317
929.6094 | 121.5912 | -0.66376 | 120.9641 | 0.0026703 | 0.0076455 | 0.063905 | -0.00088858 | 0.063057 | 0.0054089 | 0.0021747 | -0.0054932 | 2.078e-06 | 0.063766 | 0.069959 | -0.19848 | -0.0036936 | 120.9503 | -0.5722 | 3.0258 | -0.50812 | 120.8542 | -0.55389 | -0.63171 | -0.55389 | 4.4724 | -0.70038 | 120.7901 | 120.932 | -0.52185 | -0.54474 | 0.10986 | 0.032043 | -0.10986 | 0.091552 | 0.15564 | 0.1236 | -0.013733 | 0.14191 | 0.11902 | -0.17395 | 0.10986 | -0.036621 | -0.15564 | -0.032043 | 121.5179 | 121.6141 | 3.6896 | -121.5958 | 121.4539 | 121.5958 | 5.1361 | -121.5088
931.375 | 121.6644 | -0.65918 | 120.9641 | 0.0026703 | 0.0059365 | 0.065187 | -0.004093 | 0.067116 | -0.00035893 | -0.00060234 | -0.0054932 | -0.00042512 | 0.063339 | 0.068037 | -0.19742 | -0.00113 | 120.8954 | -0.6546 | 2.9343 | -0.53558 | 120.8679 | -0.56305 | -0.62714 | -0.60883 | 4.39 | -0.73242 | 120.8038 | 120.9183 | -0.50812 | -0.53558 | 0.096131 | 0.032044 | -0.09613 | 0.004578 | 0.1236 | 0.091553 | -0.068664 | 0.15106 | 0.1236 | -0.16022 | 0.050354 | -0.073242 | -0.19684 | -0.045776 | 121.5271 | 121.5546 | 3.5934 | -121.5912 | 121.463 | 121.5775 | 5.0491 | -121.4996
933.0938 | 121.6919 | -0.63171 | 120.9595 | 0.0103 | 0.0020913 | 0.064546 | 0.00039302 | 0.065834 | -0.0024951 | 0.0034565 | 0.0021363 | -0.0044839 | 0.06398 | 0.065473 | -0.20083 | 0.0014334 | 120.9778 | -0.48065 | 3.0579 | -0.44861 | 120.7901 | -0.52185 | -0.57678 | -0.51727 | 4.5136 | -0.58594 | 120.7397 | 120.8771 | -0.48523 | -0.50354 | 0.10986 | 0.054932 | -0.16937 | 0.15106 | 0.18311 | 0.12817 | 0.01831 | 0.14648 | 0.12817 | -0.21973 | 0.11444 | 0.045777 | -0.082397 | -0.082398 | 121.4218 | 121.6095 | 3.6896 | -121.5363 | 121.3715 | 121.5088 | 5.1453 | -121.463
934.8594 | 121.6415 | -0.64545 | 120.9732 | -0.0049592 | 0.0065775 | 0.063692 | 0.0027428 | 0.065834 | 0.0030591 | 0.0011067 | 0.0021363 | 0.0012839 | 0.067612 | 0.069746 | -0.19912 | -0.0030526 | 120.9595 | -0.5722 | 3.0716 | -0.48065 | 120.8679 | -0.54932 | -0.62714 | -0.55847 | 4.5502 | -0.65918 | 120.8084 | 120.9183 | -0.49896 | -0.54016 | 0.096131 | 0.018311 | -0.10529 | 0.073242 | 0.16479 | 0.14648 | -0.013733 | 0.14648 | 0.10529 | -0.16479 | 0.086975 | -0.013733 | -0.11902 | -0.054932 | 121.5134 | 121.6049 | 3.717 | -121.6003 | 121.4539 | 121.5637 | 5.1956 | -121.5134
936.625 | 121.6782 | -0.60883 | 120.9732 | 0.017929 | 0.0033731 | 0.064333 | 0.0031702 | 0.063271 | -0.0054859 | -0.0014569 | -0.0054932 | -0.0053385 | 0.065475 | 0.067182 | -0.2034 | -0.001771 | 120.9412 | -0.53101 | 3.0579 | -0.4715 | 120.813 | -0.52185 | -0.58136 | -0.55389 | 4.5044 | -0.63171 | 120.7809 | 120.9 | -0.47607 | -0.5127 | 0.086975 | 0.027466 | -0.16022 | 0.07782 | 0.13733 | 0.10986 | -0.032044 | 0.13275 | 0.096131 | -0.19226 | 0.054932 | -0.022888 | -0.11902 | -0.073243 | 121.4218 | 121.55 | 3.6667 | -121.5546 | 121.3898 | 121.5088 | 5.1132 | -121.4859
938.3906 | 121.6736 | -0.60425 | 121.0007 | -0.012589 | 0.0040139 | 0.066255 | 0.0027428 | 0.06498 | -0.0039905 | 0.0017475 | -0.020752 | -0.0053385 | 0.062271 | 0.066542 | -0.20169 | -0.0026254 | 121.019 | -0.4303 | 3.1769 | -0.41657 | 120.8267 | -0.49896 | -0.56305 | -0.48065 | 4.6417 | -0.55847 | 120.7581 | 120.9 | -0.44861 | -0.49896 | 0.10529 | 0.041199 | -0.17395 | 0.17395 | 0.18768 | 0.14648 | 0.018311 | 0.15564 | 0.10529 | -0.24261 | 0.1236 | 0.045776 | -0.05951 | -0.10071 | 121.431 | 121.6232 | 3.7811 | -121.5637 | 121.3623 | 121.5042 | 5.246 | -121.4996
940.1094 | 121.6095 | -0.63629 | 121.0007 | 0.0026703 | 0.0055093 | 0.063265 | -0.00024778 | 0.069252 | 0.0036999 | -0.00038874 | 0.0097658 | -0.0014933 | 0.068253 | 0.068037 | -0.19891 | -0.004548 | 120.9274 | -0.62714 | 3.0396 | -0.52185 | 120.8862 | -0.54016 | -0.59967 | -0.58136 | 4.4907 | -0.72784 | 120.8176 | 120.9503 | -0.50354 | -0.52643 | 0.096131 | 0.036622 | -0.11444 | 0.009156 | 0.11444 | 0.077819 | -0.073242 | 0.13275 | 0.10986 | -0.1831 | 0.054932 | -0.091552 | -0.20142 | -0.050354 | 121.5225 | 121.5637 | 3.6758 | -121.6003 | 121.4539 | 121.5866 | 5.127 | -121.5271
941.8906 | 121.6644 | -0.59967 | 120.9686 | -0.0049592 | 0.0059365 | 0.06711 | 0.0023156 | 0.065407 | -0.0024951 | -0.00017514 | -0.0054932 | -0.0044839 | 0.066757 | 0.066969 | -0.20083 | -0.00113 | 120.9595 | -0.49439 | 3.1174 | -0.4715 | 120.8405 | -0.49896 | -0.56305 | -0.52643 | 4.5456 | -0.60425 | 120.7672 | 120.9137 | -0.46692 | -0.49439 | 0.10071 | 0.036621 | -0.12817 | 0.10529 | 0.12817 | 0.091552 | -0.009155 | 0.13275 | 0.10529 | -0.20142 | 0.073242 | -0.004578 | -0.10986 | -0.054932 | 121.4401 | 121.5591 | 3.717 | -121.5317 | 121.3669 | 121.5134 | 5.1453 | -121.463
943.6562 | 121.6278 | -0.62256 | 121.0007 | -0.0049592 | -4.4874e-05 | 0.066255 | 0.0014612 | 0.067543 | 0.00092287 | 0.0019611 | 0.0021363 | -0.0023477 | 0.065262 | 0.068037 | -0.19891 | -0.0032662 | 120.9183 | -0.5722 | 3.1265 | -0.48981 | 120.8954 | -0.52185 | -0.6134 | -0.56763 | 4.5593 | -0.69122 | 120.845 | 120.932 | -0.49439 | -0.52643 | 0.10071 | 0.009156 | -0.10528 | 0.050354 | 0.13275 | 0.1236 | -0.082397 | 0.12817 | 0.096131 | -0.15564 | 0.054932 | -0.068664 | -0.1648 | -0.068664 | 121.5179 | 121.5408 | 3.7491 | -121.6141 | 121.4676 | 121.5546 | 5.1819 | -121.5271
945.3594 | 121.6919 | -0.59052 | 120.9732 | 0.0026703 | 0.0010233 | 0.065614 | 0.00060662 | 0.063698 | -0.0031359 | 3.8456e-05 | 0.0021363 | -0.0068337 | 0.06398 | 0.06825 | -0.20147 | -0.0030526 | 121.019 | -0.43488 | 3.1769 | -0.41657 | 120.8725 | -0.48981 | -0.53101 | -0.46692 | 4.5868 | -0.54474 | 120.8176 | 120.8862 | -0.44403 | -0.48523 | 0.10071 | 0.059509 | -0.10071 | 0.15564 | 0.17395 | 0.11444 | 0.045776 | 0.14648 | 0.10529 | -0.15564 | 0.1236 | 0.045776 | -0.05951 | -0.086976 | 121.463 | 121.6095 | 3.7674 | -121.5042 | 121.4081 | 121.4767 | 5.1773 | -121.4584
947.1406 | 121.6782 | -0.57678 | 121.0327 | -0.0049592 | 0.0027323 | 0.068178 | 0.0044518 | 0.06498 | -0.0024951 | -0.0012433 | -0.0054932 | -0.0029885 | 0.065475 | 0.066542 | -0.20126 | -0.0013436 | 121.0281 | -0.44403 | 3.1769 | -0.42572 | 120.8679 | -0.4715 | -0.53101 | -0.48523 | 4.6143 | -0.5722 | 120.7947 | 120.9457 | -0.43945 | -0.46234 | 0.10529 | 0.045776 | -0.16479 | 0.13275 | 0.15106 | 0.10529 | -0.004578 | 0.13733 | 0.11444 | -0.23804 | 0.091553 | 0.004577 | -0.10986 | -0.086975 | 121.4447 | 121.6049 | 3.7537 | -121.5637 | 121.3715 | 121.5225 | 5.191 | -121.4951
948.8438 | 121.5775 | -0.59967 | 121.0373 | -0.0049592 | 0.0046549 | 0.066469 | 0.00060662 | 0.066048 | 0.0047681 | 0.0023883 | -0.0054932 | -0.0019205 | 0.065689 | 0.068891 | -0.19848 | -0.0051888 | 121.0144 | -0.51727 | 3.1952 | -0.46234 | 120.9412 | -0.49896 | -0.56763 | -0.50812 | 4.6143 | -0.6546 | 120.8679 | 120.9366 | -0.45319 | -0.49439 | 0.10071 | 0.032043 | -0.09613 | 0.082397 | 0.13733 | 0.10529 | -0.022888 | 0.14648 | 0.10529 | -0.16937 | 0.091552 | -0.054932 | -0.16022 | -0.10071 | 121.5408 | 121.6141 | 3.7949 | -121.6049 | 121.4676 | 121.5363 | 5.2139 | -121.5317
950.5938 | 121.7239 | -0.55847 | 120.9961 | 0.0026703 | 0.0016641 | 0.064333 | 0.00017942 | 0.068398 | 0.0011365 | 0.0028155 | -0.013123 | -0.0025613 | 0.065475 | 0.069319 | -0.20105 | -0.00048921 | 121.0464 | -0.43488 | 3.2181 | -0.38452 | 120.9 | -0.45776 | -0.53101 | -0.4303 | 4.6921 | -0.54932 | 120.813 | 120.9183 | -0.42572 | -0.44861 | 0.10071 | 0.027466 | -0.096131 | 0.1236 | 0.17395 | 0.14648 | 0.050354 | 0.13275 | 0.10986 | -0.18311 | 0.12817 | 0.009156 | -0.10071 | -0.07782 | 121.4584 | 121.6049 | 3.7766 | -121.5271 | 121.3715 | 121.4767 | 5.2506 | -121.4447
952.3594 | 121.6095 | -0.58136 | 121.0556 | -0.0049592 | 0.0067911 | 0.062196 | 0.002102 | 0.065834 | 0.0024183 | 0.0017475 | -0.0054932 | -0.00085232 | 0.065689 | 0.067823 | -0.19699 | -0.0030526 | 121.0281 | -0.46234 | 3.2547 | -0.4303 | 120.9366 | -0.4715 | -0.54474 | -0.4715 | 4.7012 | -0.60883 | 120.8954 | 120.9549 | -0.42572 | -0.48065 | 0.10986 | 0.036621 | -0.11902 | 0.11902 | 0.15106 | 0.11444 | -0.027466 | 0.15564 | 0.10071 | -0.16022 | 0.10986 | -0.027466 | -0.12817 | -0.10071 | 121.5179 | 121.6095 | 3.8361 | -121.6003 | 121.4767 | 121.5363 | 5.2826 | -121.5363
954.0625 | 121.6415 | -0.56305 | 121.051 | -0.012589 | 0.0031595 | 0.066469 | 0.0033838 | 0.067971 | -0.0050585 | 0.0017475 | -0.013123 | -0.0055521 | 0.065903 | 0.066969 | -0.2034 | -0.0021982 | 121.0281 | -0.3891 | 3.3417 | -0.37994 | 120.8817 | -0.46692 | -0.50354 | -0.42572 | 4.7882 | -0.5127 | 120.8496 | 120.9503 | -0.39368 | -0.43488 | 0.09613 | 0.059509 | -0.16937 | 0.17395 | 0.18311 | 0.1236 | -0.022888 | 0.16937 | 0.12817 | -0.20142 | 0.13733 | 0.050354 | -0.07782 | -0.10071 | 121.4447 | 121.5912 | 3.9047 | -121.5546 | 121.4127 | 121.5134 | 5.3513 | -121.4859
955.8438 | 121.7194 | -0.53101 | 121.0373 | -0.012589 | 0.0046549 | 0.067751 | 0.0031702 | 0.064125 | -0.0050585 | -0.0010297 | -0.020752 | -0.0049111 | 0.066116 | 0.067182 | -0.20297 | -0.0039072 | 121.0876 | -0.36163 | 3.3508 | -0.35706 | 120.9 | -0.43945 | -0.50354 | -0.42114 | 4.8019 | -0.48065 | 120.8542 | 120.9595 | -0.37994 | -0.4303 | 0.091553 | 0.027466 | -0.13733 | 0.16937 | 0.17395 | 0.14648 | 0.050354 | 0.15106 | 0.10071 | -0.1831 | 0.10986 | 0.050354 | -0.050354 | -0.077819 | 121.431 | 121.6187 | 3.8818 | -121.5408 | 121.3852 | 121.4905 | 5.3329 | -121.4676
957.6094 | 121.6873 | -0.52185 | 121.051 | -0.0049592 | 0.0029459 | 0.066683 | -0.00046138 | 0.067757 | -0.0024951 | 0.0013203 | -0.013123 | -0.0040567 | 0.062271 | 0.065687 | -0.20276 | -0.0056162 | 121.0876 | -0.36621 | 3.36 | -0.33875 | 120.9366 | -0.42114 | -0.50812 | -0.39825 | 4.8111 | -0.4715 | 120.8542 | 120.9686 | -0.38452 | -0.41657 | 0.10071 | 0.013733 | -0.11444 | 0.15564 | 0.18311 | 0.16937 | 0.036621 | 0.13733 | 0.10529 | -0.19684 | 0.1236 | 0.050354 | -0.054932 | -0.082397 | 121.4584 | 121.6095 | 3.8818 | -121.5591 | 121.376 | 121.4905 | 5.3329 | -121.4676
959.375 | 121.6827 | -0.53558 | 121.0464 | -0.012589 | 0.0027323 | 0.067964 | -0.00067498 | 0.065621 | -0.0018543 | -0.00017514 | -0.0054932 | -0.0046975 | 0.065903 | 0.06761 | -0.20169 | -0.0026254 | 121.0602 | -0.4303 | 3.273 | -0.38452 | 120.9274 | -0.44403 | -0.48523 | -0.44861 | 4.6967 | -0.52185 | 120.8908 | 120.9961 | -0.38452 | -0.41657 | 0.091552 | 0.050354 | -0.11902 | 0.10529 | 0.15106 | 0.10071 | 0.013733 | 0.15106 | 0.11902 | -0.15564 | 0.086975 | 0.013732 | -0.10529 | -0.050354 | 121.463 | 121.5958 | 3.8086 | -121.5317 | 121.4264 | 121.5317 | 5.2322 | -121.463
961.0938 | 121.6782 | -0.52643 | 121.0602 | -0.0049592 | 0.0038003 | 0.066469 | 0.00082022 | 0.066475 | -0.00078613 | -0.00038874 | -0.0054932 | -0.0034159 | 0.065475 | 0.068037 | -0.20041 | -0.0043344 | 121.106 | -0.3479 | 3.3966 | -0.33875 | 120.9412 | -0.44403 | -0.48065 | -0.37994 | 4.8477 | -0.47607 | 120.8817 | 120.9732 | -0.36621 | -0.40283 | 0.082397 | 0.045776 | -0.11902 | 0.17853 | 0.18768 | 0.14191 | 0.045776 | 0.16022 | 0.1236 | -0.17853 | 0.14648 | 0.050354 | -0.073242 | -0.086975 | 121.4676 | 121.6324 | 3.923 | -121.5408 | 121.4081 | 121.4996 | 5.3741 | -121.463
962.875 | 121.6736 | -0.5127 | 121.0419 | -0.012589 | 0.0033731 | 0.06711 | -0.001316 | 0.065834 | -0.00014533 | -0.00081594 | -0.013123 | -0.0053385 | 0.064194 | 0.068037 | -0.19912 | -0.0043344 | 121.0876 | -0.37537 | 3.3188 | -0.37079 | 120.932 | -0.39825 | -0.49439 | -0.40283 | 4.7745 | -0.5127 | 120.8771 | 120.9961 | -0.35706 | -0.40283 | 0.11444 | 0.01831 | -0.10986 | 0.13733 | 0.14191 | 0.1236 | 0.045776 | 0.15564 | 0.10986 | -0.16479 | 0.10986 | 0 | -0.10986 | -0.045776 | 121.4447 | 121.6003 | 3.8315 | -121.5363 | 121.3898 | 121.5088 | 5.2872 | -121.4447
964.5781 | 121.6736 | -0.52185 | 121.0831 | -0.012589 | 0.0023049 | 0.065187 | -0.002384 | 0.06733 | 0.00092287 | 0.00067926 | -0.013123 | -0.0036295 | 0.064407 | 0.068464 | -0.19891 | -0.0021982 | 121.1105 | -0.35706 | 3.3737 | -0.34332 | 120.9366 | -0.39368 | -0.47607 | -0.37079 | 4.8203 | -0.48523 | 120.8588 | 120.9732 | -0.37079 | -0.39368 | 0.12817 | 0.045777 | -0.14648 | 0.16479 | 0.17853 | 0.13275 | 0.027466 | 0.15106 | 0.12817 | -0.2243 | 0.15106 | 0.036622 | -0.091552 | -0.10986 | 121.4584 | 121.6324 | 3.8956 | -121.5591 | 121.3806 | 121.4951 | 5.3421 | -121.4767
966.3438 | 121.7148 | -0.50812 | 121.0693 | 0.0103 | 0.0027323 | 0.067323 | 0.0012476 | 0.065193 | -0.0018543 | -0.00017514 | -0.0054932 | -0.0053385 | 0.063766 | 0.06526 | -0.1987 | -0.0034798 | 121.1197 | -0.33417 | 3.4515 | -0.31128 | 120.9366 | -0.42114 | -0.46692 | -0.37079 | 4.8935 | -0.45776 | 120.8771 | 120.9732 | -0.35706 | -0.39368 | 0.086975 | 0.041199 | -0.13275 | 0.17395 | 0.19684 | 0.15564 | 0.050354 | 0.15106 | 0.11444 | -0.19226 | 0.13733 | 0.050354 | -0.064087 | -0.09613 | 121.4447 | 121.6278 | 3.9597 | -121.5363 | 121.3852 | 121.4813 | 5.4016 | -121.463
968.0469 | 121.7377 | -0.49896 | 121.0785 | -0.0049592 | 0.0033731 | 0.065614 | 0.0014612 | 0.063484 | -0.0022815 | -0.0029523 | 0.0021363 | -0.0066201 | 0.063553 | 0.066328 | -0.20105 | -0.002839 | 121.0464 | -0.41657 | 3.3691 | -0.37079 | 120.9641 | -0.42114 | -0.48981 | -0.42572 | 4.7928 | -0.5127 | 120.9137 | 120.9732 | -0.37994 | -0.39825 | 0.077819 | 0.009155 | -0.11444 | 0.082397 | 0.12817 | 0.11902 | -0.032043 | 0.11902 | 0.10071 | -0.16479 | 0.073242 | -0.013733 | -0.11444 | -0.10528 | 121.463 | 121.5454 | 3.8681 | -121.5683 | 121.4127 | 121.4722 | 5.2917 | -121.4767
969.8125 | 121.6873 | -0.5127 | 121.0922 | -0.012589 | 0.0016641 | 0.065828 | -0.004093 | 0.066902 | 0.0019909 | -0.00081594 | 0.0021363 | -0.0038431 | 0.064621 | 0.065901 | -0.19677 | -0.0036936 | 121.1243 | -0.34332 | 3.4241 | -0.32044 | 120.9274 | -0.39368 | -0.45776 | -0.36163 | 4.8477 | -0.48523 | 120.9137 | 120.9824 | -0.36621 | -0.39825 | 0.11902 | 0.054931 | -0.16479 | 0.16937 | 0.19226 | 0.13733 | 0.032044 | 0.14648 | 0.11444 | -0.17853 | 0.15106 | 0.027466 | -0.086975 | -0.10986 | 121.4401 | 121.637 | 3.9368 | -121.55 | 121.4264 | 121.4951 | 5.3604 | -121.4905
971.5 | 121.6873 | -0.52185 | 121.0693 | -0.020218 | 0.0099953 | 0.063478 | 0.0042382 | 0.064339 | 0.0051953 | 0.00025206 | -0.0054932 | 0.00064308 | 0.067825 | 0.0706 | -0.19934 | -0.0047616 | 121.0373 | -0.49896 | 3.3417 | -0.40283 | 121.0052 | -0.42572 | -0.52185 | -0.45776 | 4.7791 | -0.5722 | 120.9366 | 121.0373 | -0.37994 | -0.39825 | 0.096131 | 0 | -0.064087 | 0.022889 | 0.11902 | 0.11902 | -0.032044 | 0.14191 | 0.1236 | -0.13275 | 0.064087 | -0.050354 | -0.17395 | -0.032044 | 121.5271 | 121.5591 | 3.8635 | -121.5912 | 121.4584 | 121.5591 | 5.3009 | -121.4676
973.2656 | 121.7102 | -0.48981 | 121.0693 | -0.012589 | 0.00080973 | 0.064546 | -0.0015296 | 0.067757 | 0.0034863 | 0.0032429 | -0.013123 | 2.078e-06 | 0.06398 | 0.067823 | -0.19742 | -0.0026254 | 121.0556 | -0.46692 | 3.3737 | -0.39368 | 120.9869 | -0.4303 | -0.49439 | -0.41199 | 4.834 | -0.54016 | 120.9412 | 121.0373 | -0.36621 | -0.3891 | 0.059509 | -0.004578 | -0.082398 | 0.022888 | 0.09613 | 0.10071 | -0.013733 | 0.1236 | 0.10071 | -0.12817 | 0.07782 | -0.050354 | -0.15106 | -0.032044 | 121.4767 | 121.5454 | 3.8635 | -121.5637 | 121.431 | 121.5271 | 5.3238 | -121.4584
975.0469 | 121.6324 | -0.52185 | 121.0876 | -0.0049592 | 0.0040139 | 0.064119 | 0.00039302 | 0.06498 | 0.0022047 | -0.00060234 | 0.0021363 | 0.0010703 | 0.064194 | 0.067823 | -0.19656 | -0.0026254 | 121.0236 | -0.49439 | 3.3829 | -0.39368 | 121.0098 | -0.41657 | -0.49439 | -0.45319 | 4.8065 | -0.60425 | 120.9732 | 121.0648 | -0.37994 | -0.41199 | 0.10529 | 0.027466 | -0.077819 | 0.027466 | 0.12817 | 0.10071 | -0.064086 | 0.14191 | 0.10986 | -0.11444 | 0.068665 | -0.082397 | -0.19226 | -0.022888 | 121.5317 | 121.5454 | 3.9047 | -121.582 | 121.4951 | 121.5866 | 5.3284 | -121.4996
976.7656 | 121.7377 | -0.4715 | 121.0785 | -0.0049592 | 0.0029459 | 0.06711 | 0.00082022 | 0.065621 | -0.0059131 | 0.00067926 | -0.020752 | -0.0066201 | 0.062271 | 0.064619 | -0.20212 | -0.00070281 | 121.0602 | -0.38452 | 3.4698 | -0.34332 | 120.9641 | -0.37994 | -0.43945 | -0.38452 | 4.9072 | -0.46692 | 120.932 | 121.0327 | -0.33417 | -0.38452 | 0.091553 | 0.032044 | -0.11444 | 0.086976 | 0.12817 | 0.09613 | -0.01831 | 0.13733 | 0.086976 | -0.14648 | 0.086976 | 0.004578 | -0.082398 | -0.045776 | 121.4355 | 121.5317 | 3.9413 | -121.5179 | 121.4035 | 121.5042 | 5.3787 | -121.463
978.5156 | 121.6095 | -0.49896 | 121.1426 | 0.0026703 | 0.00016873 | 0.065401 | -0.00024778 | 0.06968 | -0.0024951 | 0.00089286 | -0.013123 | -0.0032021 | 0.064194 | 0.067182 | -0.19998 | -0.002839 | 121.1288 | -0.33875 | 3.5843 | -0.29755 | 120.9824 | -0.37994 | -0.42572 | -0.38452 | 5.0034 | -0.46692 | 120.9183 | 121.0281 | -0.33875 | -0.38452 | 0.11902 | 0.073242 | -0.16022 | 0.16022 | 0.20142 | 0.12817 | -0.013733 | 0.16022 | 0.11444 | -0.2243 | 0.11444 | 0.032043 | -0.082398 | -0.11444 | 121.4813 | 121.6278 | 4.0833 | -121.5683 | 121.4172 | 121.5271 | 5.5023 | -121.5271
980.2969 | 121.6873 | -0.48981 | 121.0968 | -0.012589 | 0.0018777 | 0.067964 | -0.00067498 | 0.065834 | -0.0014269 | -0.00038874 | -0.0054932 | -0.0059793 | 0.062057 | 0.06526 | -0.20019 | -0.0019846 | 121.0968 | -0.37994 | 3.4927 | -0.33417 | 120.9961 | -0.37537 | -0.44861 | -0.40283 | 4.9255 | -0.48523 | 120.9091 | 121.0419 | -0.34332 | -0.35248 | 0.11444 | 0.041199 | -0.10071 | 0.10986 | 0.15564 | 0.11444 | 0 | 0.14648 | 0.13733 | -0.18768 | 0.086975 | 0.004578 | -0.13275 | -0.054932 | 121.4859 | 121.5866 | 3.9825 | -121.5454 | 121.3989 | 121.5317 | 5.4153 | -121.4493
982 | 121.7102 | -0.48065 | 121.0831 | -0.012589 | 0.0035867 | 0.065614 | 0.0046656 | 0.065834 | -0.0016405 | -0.00038874 | -0.0054932 | -0.0055521 | 0.065048 | 0.06526 | -0.20297 | -0.0041208 | 121.0739 | -0.40741 | 3.5202 | -0.33417 | 121.0007 | -0.36163 | -0.43488 | -0.40283 | 4.953 | -0.45776 | 120.9229 | 121.0327 | -0.33417 | -0.35248 | 0.11902 | 0.045777 | -0.082398 | 0.073242 | 0.14649 | 0.10071 | -0.009155 | 0.14649 | 0.12817 | -0.16022 | 0.07782 | 0.022888 | -0.10529 | -0.050354 | 121.4813 | 121.5546 | 4.0009 | -121.5179 | 121.4035 | 121.5134 | 5.4337 | -121.4355
983.7656 | 121.6095 | -0.50354 | 121.1288 | -0.0049592 | 0.0029459 | 0.063692 | -0.00088858 | 0.063484 | 0.0013501 | 0.0017475 | -0.0054932 | 0.0025657 | 0.064194 | 0.068678 | -0.19699 | -0.0047616 | 121.0464 | -0.51727 | 3.4698 | -0.38452 | 121.051 | -0.40283 | -0.48065 | -0.43945 | 4.8935 | -0.57678 | 120.9915 | 121.0831 | -0.3479 | -0.38452 | 0.10071 | 0.022888 | -0.07782 | -0.013733 | 0.11902 | 0.096131 | -0.082397 | 0.15564 | 0.11902 | -0.13733 | 0.064087 | -0.073242 | -0.19226 | -0.045776 | 121.5546 | 121.55 | 3.9734 | -121.6095 | 121.4951 | 121.5866 | 5.397 | -121.5134
985.4688 | 121.7422 | -0.46234 | 121.1105 | 0.0103 | 0.0020913 | 0.064974 | -0.00046138 | 0.063698 | -0.0024951 | -0.0016705 | -0.0054932 | -0.0040567 | 0.066757 | 0.064405 | -0.2019 | -0.0019846 | 121.0739 | -0.37994 | 3.5614 | -0.32959 | 121.0098 | -0.37079 | -0.43945 | -0.37537 | 4.9667 | -0.4715 | 120.932 | 121.0602 | -0.33417 | -0.37537 | 0.091552 | 0.022888 | -0.10071 | 0.082397 | 0.13275 | 0.10986 | -0.036621 | 0.12817 | 0.086975 | -0.17853 | 0.086975 | -0.009156 | -0.096131 | -0.050354 | 121.4722 | 121.5363 | 4.0237 | -121.55 | 121.3943 | 121.5225 | 5.4291 | -121.4859
987.25 | 121.7148 | -0.45319 | 121.1105 | -0.012589 | 0.0033731 | 0.064546 | 0.0053064 | 0.065621 | -0.0033495 | -0.0018841 | -0.0054932 | -0.0066201 | 0.067612 | 0.067396 | -0.20147 | -0.0036936 | 121.1792 | -0.27008 | 3.6987 | -0.27008 | 120.9869 | -0.37079 | -0.4303 | -0.32501 | 5.0858 | -0.40741 | 120.9274 | 121.0373 | -0.32501 | -0.35248 | 0.082397 | 0.022888 | -0.1236 | 0.1831 | 0.1831 | 0.16022 | 0.068664 | 0.12817 | 0.10071 | -0.18311 | 0.12817 | 0.045776 | -0.054932 | -0.073243 | 121.4401 | 121.6324 | 4.1519 | -121.5408 | 121.3806 | 121.4905 | 5.5389 | -121.463
989.0156 | 121.7422 | -0.46234 | 121.0922 | 0.0026703 | 0.0033731 | 0.067751 | -0.00067498 | 0.066262 | -0.0018543 | 0.00046566 | 0.0021363 | -0.0038431 | 0.063553 | 0.068037 | -0.20062 | -0.0026254 | 121.1197 | -0.37079 | 3.6301 | -0.31128 | 121.0281 | -0.36163 | -0.42572 | -0.35706 | 5.0491 | -0.4303 | 120.9457 | 121.019 | -0.32959 | -0.35706 | 0.10071 | 0.036621 | -0.064087 | 0.091552 | 0.15106 | 0.11444 | 0.027466 | 0.13275 | 0.10529 | -0.14648 | 0.10529 | 0.032043 | -0.073242 | -0.073242 | 121.4905 | 121.582 | 4.0924 | -121.5179 | 121.4081 | 121.4813 | 5.5115 | -121.4493
990.7969 | 121.7148 | -0.44861 | 121.1472 | -0.0049592 | 0.0020913 | 0.063478 | -0.00067498 | 0.066902 | 0.0032727 | 0.0011067 | 0.0021363 | 0.00021568 | 0.065475 | 0.068678 | -0.19763 | -0.0060434 | 121.1151 | -0.42114 | 3.5934 | -0.35706 | 121.0419 | -0.37537 | -0.43945 | -0.35706 | 5.0262 | -0.48981 | 120.9915 | 121.0281 | -0.33417 | -0.34332 | 0.073242 | 0.009155 | -0.10529 | 0.027465 | 0.091552 | 0.082397 | -0.032044 | 0.11444 | 0.10529 | -0.15564 | 0.091552 | -0.041199 | -0.14648 | -0.11902 | 121.4905 | 121.5637 | 4.0421 | -121.5866 | 121.4401 | 121.4767 | 5.4749 | -121.4905
992.5 | 121.669 | -0.44403 | 121.1334 | 0.0026703 | -0.0032493 | 0.068391 | -0.00024778 | 0.06498 | -0.0031359 | -0.0020977 | -0.0054932 | -0.0019205 | 0.062271 | 0.066328 | -0.20105 | -0.0026254 | 121.1243 | -0.33417 | 3.653 | -0.3067 | 120.9915 | -0.35248 | -0.39368 | -0.35248 | 5.04 | -0.45776 | 120.9183 | 121.0556 | -0.30212 | -0.33417 | 0.091553 | 0.050354 | -0.14191 | 0.10986 | 0.13733 | 0.086975 | -0.009155 | 0.14191 | 0.10986 | -0.21515 | 0.091553 | -0.013733 | -0.1236 | -0.07782 | 121.4355 | 121.5683 | 4.097 | -121.5271 | 121.3623 | 121.4996 | 5.484 | -121.4676
994.2656 | 121.6003 | -0.47607 | 121.1655 | -0.012589 | 0.0055093 | 0.065187 | 0.0012476 | 0.06498 | 0.0039135 | 0.0011067 | 0.0021363 | 0.00064308 | 0.064621 | 0.069959 | -0.19742 | -0.0039072 | 121.1426 | -0.37537 | 3.7079 | -0.33417 | 121.0464 | -0.37994 | -0.44861 | -0.36621 | 5.0995 | -0.52185 | 120.9961 | 121.0693 | -0.32501 | -0.36163 | 0.09613 | 0.027466 | -0.11902 | 0.10071 | 0.14191 | 0.11444 | -0.022888 | 0.15106 | 0.11444 | -0.16937 | 0.10986 | -0.045777 | -0.16022 | -0.09613 | 121.5225 | 121.6187 | 4.184 | -121.6141 | 121.4722 | 121.5454 | 5.5756 | -121.5271
996.0469 | 121.6232 | -0.48523 | 121.1517 | -0.0049592 | 0.0020913 | 0.06476 | -0.0028112 | 0.066475 | 0.0032727 | 0.0013203 | 0.0021363 | -0.00085232 | 0.065475 | 0.068891 | -0.19827 | -0.00070281 | 121.0602 | -0.48065 | 3.6301 | -0.36621 | 121.0602 | -0.37079 | -0.44861 | -0.39368 | 5.0217 | -0.54932 | 121.0098 | 121.0876 | -0.34332 | -0.37537 | 0.11444 | 0.036621 | -0.091552 | 0.004577 | 0.11902 | 0.082397 | -0.091552 | 0.14191 | 0.10986 | -0.14191 | 0.091552 | -0.064087 | -0.17395 | -0.064087 | 121.5454 | 121.5454 | 4.1153 | -121.6003 | 121.4951 | 121.5729 | 5.5069 | -121.5271
997.8281 | 121.637 | -0.46234 | 121.1609 | -0.0049592 | 0.0042275 | 0.062624 | 0.00060662 | 0.065834 | 0.0019909 | 0.00089286 | -0.0054932 | -0.0012795 | 0.065048 | 0.070387 | -0.20041 | -0.00113 | 121.0693 | -0.43945 | 3.6575 | -0.35248 | 121.0693 | -0.37994 | -0.43945 | -0.41199 | 5.0217 | -0.53558 | 121.0007 | 121.0968 | -0.30212 | -0.36621 | 0.082397 | 0.022888 | -0.091553 | 0.022888 | 0.10986 | 0.086975 | -0.091553 | 0.16022 | 0.09613 | -0.16022 | 0.050354 | -0.073242 | -0.16937 | -0.064087 | 121.5317 | 121.5317 | 4.1199 | -121.6003 | 121.463 | 121.5591 | 5.484 | -121.5271
999.5312 | 121.6644 | -0.43945 | 121.1472 | -0.0049592 | 0.0035867 | 0.065614 | 0.0027428 | 0.066262 | -0.0054859 | -0.00060234 | 0.0021363 | -0.0046975 | 0.065903 | 0.066755 | -0.20147 | -0.0019846 | 121.1105 | -0.33875 | 3.7491 | -0.29297 | 121.019 | -0.33875 | -0.39825 | -0.36621 | 5.0903 | -0.44403 | 120.9503 | 121.051 | -0.30212 | -0.32501 | 0.10071 | 0.041199 | -0.12817 | 0.10071 | 0.14648 | 0.10529 | -0.036621 | 0.13733 | 0.11444 | -0.19684 | 0.073242 | -0.004578 | -0.11902 | -0.096131 | 121.4584 | 121.55 | 4.1885 | -121.5454 | 121.3898 | 121.4905 | 5.5298 | -121.4722
1001.2969 | 121.7377 | -0.41657 | 121.1426 | -0.0049592 | 0.0025185 | 0.065187 | 0.00060662 | 0.062203 | -0.0061267 | 0.00025206 | 0.0021363 | -0.0053385 | 0.064194 | 0.06825 | -0.20233 | 0.00015159 | 121.106 | -0.35248 | 3.7491 | -0.28839 | 121.0373 | -0.34332 | -0.39368 | -0.35706 | 5.1086 | -0.42114 | 120.9778 | 121.0602 | -0.29297 | -0.32501 | 0.073242 | 0.022888 | -0.10529 | 0.064087 | 0.12817 | 0.10529 | -0.036621 | 0.1236 | 0.091553 | -0.16479 | 0.059509 | -0.004578 | -0.096131 | -0.082397 | 121.4539 | 121.5225 | 4.1656 | -121.5363 | 121.3943 | 121.4767 | 5.5252 | -121.4676
1003.0781 | 121.6782 | -0.4303 | 121.1563 | 0.0026703 | 0.0031595 | 0.065614 | -0.002384 | 0.066475 | 0.0032727 | 0.0017475 | 0.0021363 | 0.00021568 | 0.066544 | 0.070173 | -0.19827 | -0.0047616 | 121.0968 | -0.44403 | 3.7079 | -0.3479 | 121.0693 | -0.36621 | -0.42114 | -0.39825 | 5.0903 | -0.52185 | 121.0236 | 121.106 | -0.31586 | -0.3479 | 0.064087 | 0.009155 | -0.086975 | -0.013733 | 0.082398 | 0.073243 | -0.059509 | 0.11444 | 0.082398 | -0.13275 | 0.032044 | -0.091553 | -0.17395 | -0.050354 | 121.4996 | 121.5271 | 4.1382 | -121.5775 | 121.4539 | 121.5363 | 5.5206 | -121.5042
1004.7812 | 121.7102 | -0.4303 | 121.1426 | 0.0026703 | 0.0012369 | 0.063265 | -3.4178e-05 | 0.064553 | 0.0032727 | 0.0026019 | -0.0054932 | -0.0032021 | 0.064621 | 0.069105 | -0.20041 | -0.00091641 | 121.1197 | -0.41657 | 3.7399 | -0.32959 | 121.0602 | -0.36163 | -0.4303 | -0.36163 | 5.1361 | -0.48065 | 121.0098 | 121.0785 | -0.29297 | -0.32501 | 0.068665 | 0 | -0.082397 | 0.013733 | 0.10071 | 0.10071 | -0.022888 | 0.13733 | 0.10529 | -0.13275 | 0.068665 | -0.050354 | -0.15564 | -0.064087 | 121.4905 | 121.55 | 4.1702 | -121.5729 | 121.4401 | 121.5088 | 5.5664 | -121.4676
1006.5469 | 121.6599 | -0.46234 | 121.1609 | -0.012589 | 0.0093545 | 0.064546 | 0.0035974 | 0.06498 | 0.0041273 | 0.0015339 | 0.0021363 | -0.00042512 | 0.06633 | 0.06761 | -0.20126 | -0.0034798 | 121.1243 | -0.39825 | 3.8681 | -0.29755 | 121.0602 | -0.35706 | -0.43945 | -0.3479 | 5.246 | -0.48981 | 121.0007 | 121.1243 | -0.30212 | -0.34332 | 0.10529 | 0.022888 | -0.10071 | 0.064087 | 0.1648 | 0.14191 | -0.036621 | 0.16022 | 0.11902 | -0.16022 | 0.11444 | -0.027466 | -0.14648 | -0.036621 | 121.5225 | 121.5866 | 4.3304 | -121.6003 | 121.463 | 121.5866 | 5.7083 | -121.5042
1008.3125 | 121.6049 | -0.46692 | 121.1929 | 0.0026703 | 0.0052957 | 0.064333 | 0.0046656 | 0.068611 | -0.0042041 | 0.0021747 | -0.0054932 | -0.0034159 | 0.06633 | 0.06761 | -0.20169 | -0.00113 | 121.1426 | -0.32501 | 3.923 | -0.28381 | 121.0098 | -0.35706 | -0.41199 | -0.3891 | 5.2414 | -0.46692 | 120.9915 | 121.1197 | -0.31128 | -0.35706 | 0.10986 | 0.054932 | -0.1831 | 0.14191 | 0.18311 | 0.12817 | -0.050354 | 0.15564 | 0.10986 | -0.20142 | 0.07782 | 0 | -0.10986 | -0.073242 | 121.4767 | 121.6095 | 4.39 | -121.6049 | 121.4584 | 121.5866 | 5.7083 | -121.55
1010.0781 | 121.6553 | -0.45776 | 121.1746 | 0.0026703 | 0.0038003 | 0.063478 | -0.0011024 | 0.065834 | 6.8274e-05 | 0.0023883 | -0.0054932 | -0.0021341 | 0.065262 | 0.06825 | -0.19998 | -0.0030526 | 121.0831 | -0.43488 | 3.8086 | -0.32501 | 121.0876 | -0.35706 | -0.42114 | -0.39825 | 5.1407 | -0.51727 | 121.0464 | 121.1426 | -0.32044 | -0.33875 | 0.10071 | 0.036621 | -0.086976 | 0.022889 | 0.13275 | 0.096131 | -0.091553 | 0.13733 | 0.11902 | -0.12817 | 0.05951 | -0.059509 | -0.17853 | -0.032044 | 121.5454 | 121.5408 | 4.2664 | -121.5958 | 121.5042 | 121.6003 | 5.5984 | -121.5134
1011.7969 | 121.6782 | -0.41657 | 121.138 | -0.0049592 | -0.00025847 | 0.065614 | -0.001316 | 0.063698 | -0.0022815 | 0.0015339 | -0.013123 | -0.0044839 | 0.063766 | 0.064619 | -0.20126 | -0.0026254 | 121.1838 | -0.27466 | 3.9322 | -0.26093 | 121.0419 | -0.3067 | -0.38452 | -0.29297 | 5.278 | -0.3891 | 120.9595 | 121.0831 | -0.27924 | -0.29755 | 0.10986 | 0.032044 | -0.09613 | 0.14191 | 0.15564 | 0.1236 | 0.045777 | 0.13733 | 0.11902 | -0.17853 | 0.1236 | 0.027466 | -0.091553 | -0.054931 | 121.4584 | 121.6003 | 4.3488 | -121.5225 | 121.376 | 121.4996 | 5.6946 | -121.4355
1013.4844 | 121.6827 | -0.41657 | 121.1792 | -0.012589 | -0.00068567 | 0.06476 | 0.00060662 | 0.066475 | -0.0027087 | 0.0011067 | 0.0097658 | -0.0038431 | 0.061844 | 0.066542 | -0.20062 | 0.00036539 | 121.1792 | -0.27008 | 3.9368 | -0.27466 | 121.0327 | -0.32959 | -0.38452 | -0.31586 | 5.2551 | -0.39825 | 120.9641 | 121.0876 | -0.27924 | -0.31128 | 0.086975 | 0.032044 | -0.14648 | 0.14648 | 0.14191 | 0.10986 | 0 | 0.13733 | 0.10529 | -0.21515 | 0.10071 | 0.018311 | -0.086975 | -0.091553 | 121.4493 | 121.5958 | 4.3533 | -121.5637 | 121.3806 | 121.5042 | 5.6717 | -121.4905
1015.25 | 121.6324 | -0.45319 | 121.1975 | 0.0026703 | 0.0029459 | 0.066469 | -0.00067498 | 0.067116 | 0.0049817 | 0.00067926 | 0.0021363 | 0.00064308 | 0.064194 | 0.067396 | -0.19827 | -0.002839 | 121.0693 | -0.43945 | 3.8864 | -0.32501 | 121.0922 | -0.34332 | -0.4303 | -0.39368 | 5.1727 | -0.52643 | 121.0373 | 121.1243 | -0.32959 | -0.3479 | 0.10986 | 0.022888 | -0.10529 | 0.013733 | 0.12817 | 0.10529 | -0.12817 | 0.1236 | 0.10529 | -0.16022 | 0.059509 | -0.073242 | -0.17853 | -0.073242 | 121.5454 | 121.5225 | 4.3396 | -121.6278 | 121.4905 | 121.5775 | 5.6259 | -121.5454
1016.9688 | 121.7422 | -0.42114 | 121.1517 | 0.0026703 | 0.0029459 | 0.066683 | 0.0031702 | 0.068184 | -0.0061267 | 0.0030293 | -0.0054932 | -0.0053385 | 0.068039 | 0.065473 | -0.20425 | -0.0030526 | 121.1609 | -0.27466 | 4.0192 | -0.23804 | 121.0419 | -0.32044 | -0.38452 | -0.3067 | 5.3604 | -0.36163 | 120.9641 | 121.0785 | -0.27466 | -0.31586 | 0.10071 | 0.036622 | -0.10986 | 0.14648 | 0.18311 | 0.14648 | 0.009156 | 0.14648 | 0.10529 | -0.18768 | 0.11444 | 0.05951 | -0.045776 | -0.073242 | 121.463 | 121.582 | 4.4403 | -121.5363 | 121.3852 | 121.4996 | 5.7816 | -121.4676
1018.6719 | 121.6873 | -0.41199 | 121.1746 | 0.0026703 | 0.00038233 | 0.066469 | 0.0029566 | 0.06498 | -0.0016405 | 0.00046566 | -0.0054932 | -0.0055521 | 0.064194 | 0.068037 | -0.20169 | 0.00015159 | 121.1334 | -0.32044 | 3.9871 | -0.28381 | 121.0373 | -0.31586 | -0.37537 | -0.33875 | 5.2872 | -0.43945 | 121.0007 | 121.106 | -0.29297 | -0.3067 | 0.09613 | 0.036621 | -0.13733 | 0.091552 | 0.12817 | 0.091553 | -0.041199 | 0.11902 | 0.10529 | -0.17395 | 0.073242 | -0.027466 | -0.13275 | -0.068665 | 121.4493 | 121.5454 | 4.3991 | -121.55 | 121.4127 | 121.5179 | 5.6992 | -121.4813
1020.4219 | 121.6415 | -0.4303 | 121.1975 | 0.0026703 | 0.0055093 | 0.063265 | 0.0018884 | 0.066475 | 0.0047681 | -0.0012433 | -0.0054932 | 0.00021568 | 0.065689 | 0.068037 | -0.19848 | -0.0047616 | 121.138 | -0.37537 | 4.0466 | -0.29297 | 121.0922 | -0.33875 | -0.41657 | -0.32959 | 5.3696 | -0.46692 | 121.0419 | 121.138 | -0.31128 | -0.33417 | 0.091553 | 0.013733 | -0.10529 | 0.054932 | 0.13733 | 0.1236 | -0.05951 | 0.11902 | 0.096131 | -0.15564 | 0.10071 | -0.036621 | -0.13275 | -0.05951 | 121.5225 | 121.5683 | 4.4769 | -121.6141 | 121.4722 | 121.5683 | 5.7999 | -121.5317
1022.2188 | 121.6553 | -0.43488 | 121.2158 | -0.012589 | 0.0057229 | 0.066255 | 0.0018884 | 0.068611 | 0.0032727 | 0.0030293 | -0.0054932 | -0.0014933 | 0.065262 | 0.068464 | -0.20083 | -0.00113 | 121.1426 | -0.38452 | 4.0558 | -0.28381 | 121.1014 | -0.34332 | -0.42114 | -0.3479 | 5.3696 | -0.47607 | 121.0464 | 121.1197 | -0.29297 | -0.3479 | 0.091552 | 0.013732 | -0.11444 | 0.050354 | 0.15106 | 0.13733 | -0.073242 | 0.14191 | 0.086975 | -0.16937 | 0.086975 | -0.041199 | -0.12817 | -0.09613 | 121.5363 | 121.5775 | 4.4907 | -121.637 | 121.4813 | 121.5546 | 5.8044 | -121.5637
1023.9219 | 121.7422 | -0.38452 | 121.1655 | -0.0049592 | 0.0016641 | 0.06711 | 0.001034 | 0.066262 | -0.0067675 | -0.0014569 | -0.0054932 | -0.0057657 | 0.063766 | 0.067396 | -0.20361 | -0.0026254 | 121.1929 | -0.24719 | 4.129 | -0.22888 | 121.0693 | -0.32044 | -0.35706 | -0.2655 | 5.4337 | -0.32044 | 120.9869 | 121.1609 | -0.25635 | -0.27466 | 0.064086 | 0.027465 | -0.09613 | 0.13733 | 0.15564 | 0.12817 | 0.027466 | 0.12817 | 0.10986 | -0.17853 | 0.11902 | 0.064086 | -0.045777 | -0.004577 | 121.4539 | 121.5775 | 4.5135 | -121.5225 | 121.3715 | 121.5454 | 5.8182 | -121.4401
1025.625 | 121.7239 | -0.38452 | 121.1884 | -0.0049592 | 0.0040139 | 0.063905 | -0.0015296 | 0.065621 | 0.0022047 | 0.0021747 | -0.0054932 | -0.0051247 | 0.065048 | 0.06761 | -0.20019 | -0.0015572 | 121.2112 | -0.27466 | 4.1016 | -0.22888 | 121.0602 | -0.3067 | -0.36163 | -0.24719 | 5.3925 | -0.37537 | 121.0007 | 121.1151 | -0.24719 | -0.28381 | 0.077819 | 0.022888 | -0.12817 | 0.10986 | 0.15564 | 0.13275 | 0.022889 | 0.13733 | 0.10071 | -0.18768 | 0.13733 | 0.009155 | -0.091553 | -0.073242 | 121.4447 | 121.5958 | 4.4861 | -121.55 | 121.3852 | 121.4996 | 5.777 | -121.4722
1027.3906 | 121.6965 | -0.41657 | 121.1975 | 0.0026703 | 0.0035867 | 0.066469 | -0.0036658 | 0.065621 | 0.0017773 | 0.0032429 | 0.0021363 | -0.0017069 | 0.064407 | 0.06825 | -0.19998 | -0.0019846 | 121.1288 | -0.39825 | 4.0192 | -0.32501 | 121.1288 | -0.32959 | -0.42114 | -0.36621 | 5.3284 | -0.48065 | 121.0602 | 121.1655 | -0.29297 | -0.32044 | 0.086975 | -0.004578 | -0.068665 | 0.018311 | 0.091553 | 0.096131 | -0.068665 | 0.1236 | 0.09613 | -0.13733 | 0.050354 | -0.064087 | -0.16022 | -0.032044 | 121.5454 | 121.5454 | 4.4357 | -121.6187 | 121.4767 | 121.582 | 5.7449 | -121.5179
1029.1719 | 121.6553 | -0.42572 | 121.225 | -0.012589 | 0.0014505 | 0.064333 | -0.0011024 | 0.069893 | 0.0034863 | 0.0026019 | -0.020752 | -0.00042512 | 0.064194 | 0.066114 | -0.19806 | -0.0030526 | 121.1563 | -0.35706 | 4.1611 | -0.27924 | 121.1243 | -0.32959 | -0.3891 | -0.3067 | 5.452 | -0.43945 | 121.051 | 121.1655 | -0.27924 | -0.31128 | 0.09613 | 0.036621 | -0.10071 | 0.068664 | 0.14648 | 0.10986 | -0.068665 | 0.14648 | 0.11444 | -0.17395 | 0.11902 | -0.013733 | -0.12817 | -0.05951 | 121.55 | 121.582 | 4.5868 | -121.6141 | 121.4767 | 121.5912 | 5.8777 | -121.5363
1030.8906 | 121.6599 | -0.4303 | 121.225 | 0.0026703 | 0.0050821 | 0.065401 | -0.0021704 | 0.067116 | -0.00014533 | 0.00046566 | -0.0054932 | -0.0012795 | 0.063766 | 0.06761 | -0.20041 | -0.001771 | 121.1655 | -0.34332 | 4.184 | -0.2655 | 121.0876 | -0.32044 | -0.41199 | -0.31128 | 5.4657 | -0.44403 | 121.051 | 121.1929 | -0.29297 | -0.31586 | 0.10986 | 0.018311 | -0.13733 | 0.086975 | 0.1648 | 0.14648 | -0.05951 | 0.13733 | 0.11444 | -0.17395 | 0.11902 | -0.013733 | -0.12817 | -0.032044 | 121.5179 | 121.5958 | 4.6143 | -121.637 | 121.4813 | 121.6232 | 5.896 | -121.5408
1032.6094 | 121.7194 | -0.38452 | 121.17 | -0.012589 | 0.00038233 | 0.066469 | 0.0031702 | 0.067116 | -0.0046313 | -0.00060234 | -0.0054932 | -0.0051247 | 0.062912 | 0.068037 | -0.20382 | -0.00113 | 121.2067 | -0.24261 | 4.2389 | -0.2243 | 121.0648 | -0.28381 | -0.3479 | -0.27008 | 5.5298 | -0.32959 | 120.9824 | 121.17 | -0.23346 | -0.29297 | 0.10071 | 0.036621 | -0.10529 | 0.14191 | 0.16022 | 0.1236 | 0.036621 | 0.15106 | 0.091552 | -0.18768 | 0.11444 | 0.054931 | -0.036621 | 0 | 121.4493 | 121.5912 | 4.6234 | -121.5179 | 121.3669 | 121.5546 | 5.9143 | -121.463
1034.3594 | 121.7194 | -0.37994 | 121.1655 | -0.012589 | 0.0023049 | 0.065187 | -0.0021704 | 0.064766 | 0.00070927 | 0.0017475 | -0.020752 | -0.0032021 | 0.063339 | 0.064619 | -0.20041 | -0.0034798 | 121.2433 | -0.27008 | 4.2297 | -0.2243 | 121.1014 | -0.27924 | -0.33875 | -0.24261 | 5.5069 | -0.35706 | 121.019 | 121.1655 | -0.22888 | -0.2655 | 0.10071 | 0.041199 | -0.064087 | 0.10986 | 0.15564 | 0.11444 | 0.07782 | 0.15106 | 0.11444 | -0.14648 | 0.13733 | 0.022888 | -0.091553 | 0 | 121.4813 | 121.6232 | 4.6097 | -121.5042 | 121.3989 | 121.5454 | 5.8868 | -121.431
1036.0625 | 121.6415 | -0.41657 | 121.2067 | -0.012589 | 0.0072183 | 0.066469 | -0.00046138 | 0.067543 | 0.0028455 | 0.0045245 | 0.0021363 | 0.00085668 | 0.065475 | 0.069532 | -0.1987 | -0.0039072 | 121.2158 | -0.31128 | 4.2755 | -0.24719 | 121.1105 | -0.30212 | -0.38452 | -0.27924 | 5.5389 | -0.41657 | 121.0831 | 121.2387 | -0.24719 | -0.28839 | 0.11444 | 0.032044 | -0.09613 | 0.10529 | 0.16937 | 0.13733 | 0.009155 | 0.16937 | 0.12817 | -0.1236 | 0.13733 | 0 | -0.12817 | 0.032043 | 121.5271 | 121.6324 | 4.6921 | -121.5912 | 121.4996 | 121.6553 | 5.9555 | -121.4951
1037.8281 | 121.6187 | -0.39825 | 121.2112 | 0.0026703 | 0.0067911 | 0.06476 | 0.0029566 | 0.066475 | 0.0022047 | 0.0017475 | -0.0054932 | -0.0036295 | 0.065903 | 0.069532 | -0.1987 | -0.002839 | 121.1929 | -0.28839 | 4.2984 | -0.23346 | 121.1151 | -0.30212 | -0.36163 | -0.27924 | 5.5618 | -0.41199 | 121.0693 | 121.2158 | -0.24261 | -0.28381 | 0.09613 | 0.036621 | -0.096131 | 0.10986 | 0.16479 | 0.12817 | -0.018311 | 0.15564 | 0.11444 | -0.14191 | 0.11902 | -0.013733 | -0.12817 | 0.004577 | 121.5134 | 121.5912 | 4.6967 | -121.5729 | 121.4676 | 121.6141 | 5.9601 | -121.4951
1039.5156 | 121.582 | -0.41199 | 121.257 | -0.0049592 | 0.0061501 | 0.063692 | 0.002102 | 0.065621 | 0.0034863 | 0.0028155 | -0.0054932 | -0.0019205 | 0.065689 | 0.068464 | -0.19955 | -0.0032662 | 121.1746 | -0.33875 | 4.2618 | -0.2655 | 121.1472 | -0.29297 | -0.37079 | -0.33417 | 5.5069 | -0.46692 | 121.0922 | 121.2296 | -0.27008 | -0.30212 | 0.11902 | 0.041198 | -0.10986 | 0.073242 | 0.14648 | 0.10529 | -0.082397 | 0.14191 | 0.10986 | -0.16479 | 0.07782 | -0.054932 | -0.16479 | -0.027466 | 121.5591 | 121.5866 | 4.6738 | -121.6278 | 121.5042 | 121.6415 | 5.9189 | -121.5591
1041.2656 | 121.6827 | -0.35706 | 121.2204 | -0.0049592 | -4.4874e-05 | 0.066255 | -0.00067498 | 0.064125 | -0.0044177 | 0.0023883 | -0.0054932 | -0.0046975 | 0.060776 | 0.064833 | -0.20062 | -0.0034798 | 121.2479 | -0.23346 | 4.3167 | -0.1831 | 121.0739 | -0.2655 | -0.32501 | -0.23804 | 5.5984 | -0.33875 | 121.0419 | 121.2021 | -0.22888 | -0.24261 | 0.091553 | 0.032044 | -0.14648 | 0.1236 | 0.17395 | 0.14191 | 0.027466 | 0.12817 | 0.11444 | -0.17853 | 0.11902 | 0.018311 | -0.09613 | -0.018311 | 121.431 | 121.6049 | 4.6738 | -121.5454 | 121.3989 | 121.5591 | 5.9555 | -121.463
1042.9844 | 121.6141 | -0.3891 | 121.2616 | -0.0049592 | 0.0046549 | 0.064333 | -0.0025976 | 0.064339 | 0.0011365 | -0.00017514 | -0.0054932 | -0.00085232 | 0.063553 | 0.068891 | -0.20062 | -0.0021982 | 121.1563 | -0.39825 | 4.2572 | -0.27466 | 121.17 | -0.29297 | -0.37994 | -0.36163 | 5.4657 | -0.50354 | 121.1243 | 121.2341 | -0.25177 | -0.29297 | 0.09613 | 0.009155 | -0.091553 | -0.009155 | 0.11444 | 0.10529 | -0.10529 | 0.13733 | 0.09613 | -0.13733 | 0.027466 | -0.11444 | -0.21057 | -0.027466 | 121.5591 | 121.5454 | 4.6463 | -121.6415 | 121.5134 | 121.6232 | 5.8548 | -121.5546
1044.7344 | 121.7194 | -0.34332 | 121.2296 | 0.0026703 | 0.0035867 | 0.064974 | 0.0018884 | 0.066475 | 6.8274e-05 | 0.0015339 | 0.0021363 | -0.0040567 | 0.065262 | 0.068678 | -0.20019 | -0.0015572 | 121.17 | -0.35706 | 4.2801 | -0.27466 | 121.1517 | -0.29755 | -0.36163 | -0.3067 | 5.5206 | -0.43488 | 121.0648 | 121.1929 | -0.24719 | -0.26093 | 0.045777 | -0.01831 | -0.07782 | -0.013733 | 0.068665 | 0.086975 | -0.059509 | 0.096131 | 0.082398 | -0.16479 | 0.036621 | -0.091552 | -0.17395 | -0.036621 | 121.4951 | 121.5134 | 4.6234 | -121.5912 | 121.4081 | 121.5363 | 5.864 | -121.4905
1046.4844 | 121.7331 | -0.33417 | 121.2341 | -0.0049592 | 0.0035867 | 0.065828 | 0.00060662 | 0.066475 | -0.0027087 | 0.00025206 | -0.013123 | -0.0032021 | 0.064194 | 0.06825 | -0.19977 | -0.00027561 | 121.2112 | -0.31128 | 4.335 | -0.22888 | 121.1334 | -0.27008 | -0.33417 | -0.25635 | 5.5984 | -0.3479 | 121.0693 | 121.2112 | -0.21515 | -0.23804 | 0.064086 | 0 | -0.10071 | 0.022888 | 0.10528 | 0.10528 | -0.022888 | 0.11902 | 0.09613 | -0.16479 | 0.077819 | -0.013733 | -0.10986 | -0.022888 | 121.4676 | 121.5454 | 4.6692 | -121.5683 | 121.4035 | 121.5454 | 5.9326 | -121.4722
1048.25 | 121.6827 | -0.35248 | 121.2158 | 0.0026703 | -0.0017539 | 0.065828 | 0.00039302 | 0.064766 | -0.0046313 | -0.00038874 | -0.0054932 | -0.0061929 | 0.063339 | 0.065901 | -0.2019 | 0.00015159 | 121.2021 | -0.25177 | 4.39 | -0.21057 | 121.1105 | -0.23346 | -0.32044 | -0.28381 | 5.5939 | -0.36163 | 121.0602 | 121.2067 | -0.2243 | -0.25177 | 0.11902 | 0.032043 | -0.10528 | 0.10071 | 0.14191 | 0.10986 | -0.013733 | 0.12817 | 0.10071 | -0.15564 | 0.068665 | -0.009155 | -0.10986 | -0.009155 | 121.463 | 121.5546 | 4.7424 | -121.5363 | 121.4127 | 121.5591 | 5.9463 | -121.4676
1050.0156 | 121.637 | -0.3891 | 121.2524 | -0.0049592 | 0.0048685 | 0.064974 | -0.00046138 | 0.066475 | 0.0019909 | 0.00067926 | 0.0021363 | -0.0017069 | 0.064407 | 0.06825 | -0.1987 | -0.0051888 | 121.225 | -0.28381 | 4.4495 | -0.2243 | 121.17 | -0.29755 | -0.35248 | -0.25177 | 5.6671 | -0.40283 | 121.0922 | 121.225 | -0.25177 | -0.2655 | 0.091553 | 0.036621 | -0.082397 | 0.10529 | 0.16479 | 0.12817 | -0.027465 | 0.13733 | 0.1236 | -0.16022 | 0.13733 | -0.013733 | -0.13733 | -0.027465 | 121.5591 | 121.6141 | 4.8386 | -121.6049 | 121.4813 | 121.6141 | 6.0562 | -121.5179
1051.7656 | 121.7422 | -0.34332 | 121.2341 | 0.0026703 | 0.0029459 | 0.065187 | 0.00017942 | 0.064339 | -0.0012133 | 0.00025206 | -0.0054932 | -0.0021341 | 0.064621 | 0.068464 | -0.19955 | -0.0019846 | 121.1884 | -0.35706 | 4.3762 | -0.2655 | 121.1792 | -0.27924 | -0.33875 | -0.3067 | 5.5664 | -0.42114 | 121.0876 | 121.257 | -0.21515 | -0.25635 | 0.064087 | 0.004578 | -0.054932 | -0.013733 | 0.07782 | 0.073242 | -0.045777 | 0.12817 | 0.086975 | -0.14648 | 0.036621 | -0.07782 | -0.16479 | 0.022888 | 121.5225 | 121.5317 | 4.7195 | -121.5729 | 121.431 | 121.6003 | 5.9097 | -121.4905
1053.4531 | 121.6736 | -0.36163 | 121.2387 | 0.0026703 | 0.0065775 | 0.066042 | 0.0061608 | 0.065834 | -0.0044177 | -0.00060234 | -0.0054932 | -0.0051247 | 0.065048 | 0.065901 | -0.20297 | -0.0030526 | 121.2753 | -0.20599 | 4.5914 | -0.17395 | 121.1334 | -0.23346 | -0.32044 | -0.21515 | 5.7495 | -0.31128 | 121.0419 | 121.2204 | -0.20599 | -0.23346 | 0.12817 | 0.041198 | -0.10529 | 0.15564 | 0.18768 | 0.14649 | 0.036622 | 0.15564 | 0.12817 | -0.19684 | 0.14648 | 0.050354 | -0.07782 | -0.01831 | 121.4951 | 121.637 | 4.953 | -121.5591 | 121.4035 | 121.582 | 6.1111 | -121.4722
1055.2344 | 121.6507 | -0.37079 | 121.2662 | -0.0049592 | 0.0042275 | 0.063692 | 0.0027428 | 0.067543 | -0.00014533 | -0.0014569 | -0.013123 | -0.0021341 | 0.066971 | 0.066755 | -0.20041 | -0.0049752 | 121.1975 | -0.32959 | 4.5181 | -0.22888 | 121.1655 | -0.29297 | -0.36163 | -0.31586 | 5.6808 | -0.42114 | 121.1197 | 121.2524 | -0.24719 | -0.27924 | 0.07782 | 0.009156 | -0.10071 | 0.041199 | 0.14191 | 0.13275 | -0.068664 | 0.1236 | 0.091553 | -0.14648 | 0.054932 | -0.050354 | -0.14191 | -0.013733 | 121.5363 | 121.5683 | 4.8889 | -121.6278 | 121.4905 | 121.6232 | 6.0516 | -121.5454
1057.0156 | 121.6095 | -0.39368 | 121.2753 | -0.0049592 | 0.0044411 | 0.063905 | 0.0029566 | 0.067116 | -0.0016405 | 0.00046566 | -0.0054932 | -0.0021341 | 0.067825 | 0.069746 | -0.20276 | -0.0047616 | 121.1609 | -0.32044 | 4.5319 | -0.24261 | 121.1563 | -0.28839 | -0.36163 | -0.33417 | 5.6946 | -0.42572 | 121.1105 | 121.2387 | -0.23346 | -0.28381 | 0.10529 | 0.032044 | -0.11902 | 0.073242 | 0.15106 | 0.11902 | -0.11444 | 0.16022 | 0.10986 | -0.16479 | 0.05951 | -0.032043 | -0.14191 | -0.036622 | 121.55 | 121.5546 | 4.9255 | -121.637 | 121.5042 | 121.6324 | 6.0883 | -121.5591
1058.7969 | 121.6553 | -0.37079 | 121.2799 | 0.0026703 | 0.0059365 | 0.066042 | 0.0035974 | 0.066902 | 0.00049567 | 0.00089286 | -0.013123 | 0.0019247 | 0.066757 | 0.068464 | -0.20062 | -0.0043344 | 121.1746 | -0.32044 | 4.5547 | -0.23804 | 121.1792 | -0.28839 | -0.35248 | -0.29755 | 5.7541 | -0.42572 | 121.106 | 121.2387 | -0.23346 | -0.27008 | 0.082398 | 0.018311 | -0.10071 | 0.050354 | 0.13275 | 0.11444 | -0.10528 | 0.13733 | 0.10071 | -0.17395 | 0.073243 | -0.054931 | -0.15564 | -0.041199 | 121.55 | 121.5454 | 4.9255 | -121.6324 | 121.4767 | 121.6095 | 6.1249 | -121.55
1060.4844 | 121.6095 | -0.38452 | 121.2891 | -0.0049592 | 0.0063639 | 0.063905 | 0.0027428 | 0.066689 | -0.0024951 | -0.0012433 | 0.0021363 | -0.0023477 | 0.065048 | 0.068891 | -0.20425 | -0.0024118 | 121.225 | -0.23346 | 4.6417 | -0.19684 | 121.1197 | -0.27466 | -0.31586 | -0.29297 | 5.7358 | -0.38452 | 121.0968 | 121.2524 | -0.2243 | -0.24719 | 0.10986 | 0.068664 | -0.16937 | 0.15106 | 0.18768 | 0.11902 | -0.064086 | 0.16022 | 0.13733 | -0.19226 | 0.091552 | 0 | -0.13733 | -0.036621 | 121.5042 | 121.6095 | 5.0262 | -121.6049 | 121.4813 | 121.637 | 6.1203 | -121.5363
1062.2812 | 121.7697 | -0.34332 | 121.2433 | -0.012589 | 0.0016641 | 0.067964 | 0.0033838 | 0.065193 | -0.0042041 | -0.00081594 | 0.0097658 | -0.0059793 | 0.062698 | 0.066542 | -0.20254 | -0.0015572 | 121.2112 | -0.21057 | 4.6463 | -0.1831 | 121.138 | -0.25177 | -0.32501 | -0.22888 | 5.8319 | -0.29297 | 121.0648 | 121.1929 | -0.20599 | -0.23346 | 0.091553 | 0.018311 | -0.10529 | 0.13275 | 0.16022 | 0.14191 | -0.032043 | 0.13733 | 0.10986 | -0.17853 | 0.11444 | 0.050354 | -0.05951 | -0.050354 | 121.4813 | 121.5546 | 4.9896 | -121.5683 | 121.4081 | 121.5363 | 6.1752 | -121.4767
1064.0625 | 121.6919 | -0.33875 | 121.2616 | 0.0026703 | 0.0031595 | 0.064333 | 0.00017942 | 0.065407 | -0.00057253 | -0.0012433 | 0.0021363 | -0.0036295 | 0.065048 | 0.067396 | -0.19955 | -0.0060434 | 121.2708 | -0.18768 | 4.6783 | -0.17395 | 121.1243 | -0.23804 | -0.32044 | -0.19684 | 5.8136 | -0.29297 | 121.0693 | 121.2112 | -0.19684 | -0.23804 | 0.10071 | 0.01831 | -0.13733 | 0.15106 | 0.1648 | 0.14649 | 0.009155 | 0.14191 | 0.10071 | -0.19226 | 0.14191 | 0.045776 | -0.054932 | -0.050354 | 121.463 | 121.6095 | 5.0171 | -121.582 | 121.4081 | 121.55 | 6.1523 | -121.4996
1065.8438 | 121.6095 | -0.39368 | 121.3028 | -0.0049592 | 0.0048685 | 0.066042 | 0.0031702 | 0.065834 | 0.00049567 | -0.0010297 | -0.013123 | -0.0044839 | 0.066971 | 0.066114 | -0.19998 | -0.002839 | 121.17 | -0.31586 | 4.6692 | -0.26093 | 121.1609 | -0.27008 | -0.36163 | -0.31128 | 5.7816 | -0.42572 | 121.1243 | 121.2204 | -0.21973 | -0.25177 | 0.1236 | 0.032044 | -0.14191 | 0.07782 | 0.13275 | 0.10071 | -0.13275 | 0.17395 | 0.14191 | -0.17853 | 0.082398 | -0.032043 | -0.17395 | -0.082397 | 121.5546 | 121.5637 | 5.0629 | -121.6644 | 121.5179 | 121.6141 | 6.1752 | -121.5546
1067.5312 | 121.6141 | -0.37994 | 121.2936 | 0.0026703 | 0.00016873 | 0.066255 | -0.00088858 | 0.065621 | -0.00099973 | 0.0017475 | -0.0054932 | -0.0021341 | 0.062698 | 0.066542 | -0.2019 | -0.0030526 | 121.2662 | -0.17853 | 4.7699 | -0.15564 | 121.1472 | -0.24719 | -0.32044 | -0.26093 | 5.8456 | -0.35248 | 121.0876 | 121.2296 | -0.20599 | -0.24719 | 0.13275 | 0.059509 | -0.14648 | 0.20142 | 0.2243 | 0.1648 | -0.027466 | 0.17395 | 0.13275 | -0.20599 | 0.11902 | 0.027466 | -0.10529 | -0.064087 | 121.5271 | 121.6461 | 5.1498 | -121.6141 | 121.4676 | 121.6095 | 6.2256 | -121.5408
1069.2969 | 121.7468 | -0.3067 | 121.2479 | -0.0049592 | 0.0020913 | 0.065828 | -0.0021704 | 0.067116 | 0.00092287 | 0.0045245 | -0.0054932 | -0.00085232 | 0.06163 | 0.066542 | -0.19784 | -0.0024118 | 121.2708 | -0.24261 | 4.715 | -0.17395 | 121.17 | -0.23804 | -0.3067 | -0.1831 | 5.8548 | -0.31128 | 121.0739 | 121.2296 | -0.19226 | -0.22888 | 0.068665 | 0 | -0.07782 | 0.064087 | 0.13275 | 0.13275 | 0.022888 | 0.11444 | 0.07782 | -0.17395 | 0.1236 | -0.004577 | -0.082397 | -0.018311 | 121.4767 | 121.5775 | 5.0217 | -121.5546 | 121.3806 | 121.5363 | 6.1615 | -121.4767
1071.0781 | 121.7606 | -0.33417 | 121.257 | -0.020218 | 0.0038003 | 0.067323 | 0.0033838 | 0.067116 | -0.0048449 | 0.00089286 | 0.0021363 | -0.0059793 | 0.064621 | 0.065901 | -0.20276 | -0.00048921 | 121.225 | -0.21973 | 4.7745 | -0.16479 | 121.1609 | -0.25177 | -0.30212 | -0.23346 | 5.8731 | -0.30212 | 121.0831 | 121.2296 | -0.18768 | -0.23346 | 0.082397 | 0.032043 | -0.09613 | 0.11444 | 0.16937 | 0.13733 | -0.032043 | 0.14648 | 0.10071 | -0.17395 | 0.10071 | 0.032043 | -0.068665 | -0.027466 | 121.4951 | 121.5591 | 5.1086 | -121.5591 | 121.4172 | 121.5637 | 6.2073 | -121.4905
1072.7969 | 121.7514 | -0.31586 | 121.2524 | -0.012589 | 0.0012369 | 0.066255 | 0.0042382 | 0.06498 | -0.0024951 | -0.00017514 | -0.013123 | -0.0064065 | 0.064407 | 0.067823 | -0.20468 | -0.0015572 | 121.2753 | -0.19226 | 4.8248 | -0.16022 | 121.1655 | -0.22888 | -0.29297 | -0.20599 | 5.9235 | -0.28381 | 121.0968 | 121.2021 | -0.1831 | -0.2243 | 0.086975 | 0.022888 | -0.086975 | 0.1236 | 0.15564 | 0.13275 | 0.022889 | 0.13275 | 0.091553 | -0.15564 | 0.10986 | 0.032044 | -0.059509 | -0.050354 | 121.4813 | 121.5912 | 5.1407 | -121.5454 | 121.4127 | 121.5179 | 6.2393 | -121.4767
1074.5 | 121.6461 | -0.35706 | 121.2662 | -0.0049592 | 0.0025185 | 0.061983 | 0.002102 | 0.066048 | -0.0020679 | 0.00046566 | -0.0054932 | -0.0042703 | 0.067398 | 0.067396 | -0.20297 | -0.0041208 | 121.2799 | -0.16479 | 4.9255 | -0.14191 | 121.1426 | -0.22888 | -0.29755 | -0.19226 | 5.9647 | -0.29297 | 121.0556 | 121.2112 | -0.19226 | -0.20599 | 0.12817 | 0.05951 | -0.1236 | 0.19226 | 0.21515 | 0.15564 | 0.013733 | 0.16479 | 0.15106 | -0.21057 | 0.16479 | 0.064087 | -0.086975 | -0.054931 | 121.4996 | 121.637 | 5.2826 | -121.5637 | 121.4127 | 121.5683 | 6.3217 | -121.4722
1076.2812 | 121.7148 | -0.33417 | 121.2616 | 0.0026703 | 0.0010233 | 0.066255 | -0.0032386 | 0.064553 | 0.0028455 | 0.00089286 | -0.013123 | -0.00085232 | 0.063766 | 0.068891 | -0.19827 | -0.0051888 | 121.2067 | -0.30212 | 4.7424 | -0.23804 | 121.2067 | -0.25635 | -0.33417 | -0.25635 | 5.8411 | -0.42114 | 121.1334 | 121.2387 | -0.21515 | -0.25177 | 0.077819 | 0 | -0.054932 | 0.032043 | 0.09613 | 0.09613 | -0.054932 | 0.11902 | 0.082397 | -0.12817 | 0.077819 | -0.086976 | -0.16937 | -0.022889 | 121.5408 | 121.5408 | 5.0766 | -121.5958 | 121.4676 | 121.5729 | 6.1752 | -121.5134
1078.0469 | 121.7285 | -0.31128 | 121.2479 | 0.0026703 | -4.4874e-05 | 0.063265 | 0.00060662 | 0.066262 | 0.0032727 | 0.0021747 | -0.013123 | -0.0012795 | 0.063766 | 0.068464 | -0.19891 | -0.0036936 | 121.2067 | -0.27466 | 4.7882 | -0.22888 | 121.2112 | -0.25177 | -0.32044 | -0.24261 | 5.8731 | -0.3891 | 121.1151 | 121.2479 | -0.20142 | -0.23346 | 0.059509 | -0.009156 | -0.036621 | 0.036621 | 0.082397 | 0.091553 | -0.041199 | 0.10986 | 0.07782 | -0.13275 | 0.068664 | -0.07782 | -0.15564 | 0 | 121.5225 | 121.5179 | 5.0995 | -121.5683 | 121.4264 | 121.5591 | 6.1844 | -121.4813
1079.8281 | 121.6919 | -0.32501 | 121.2708 | -0.0049592 | 0.0027323 | 0.066469 | 0.00017942 | 0.063271 | -0.0069811 | -0.00038874 | -0.0054932 | -0.0061929 | 0.063126 | 0.065473 | -0.20233 | -0.00048921 | 121.2479 | -0.19684 | 4.8843 | -0.18768 | 121.1472 | -0.2243 | -0.29755 | -0.23804 | 5.9052 | -0.33417 | 121.0785 | 121.2296 | -0.18768 | -0.21057 | 0.10071 | 0.027466 | -0.1236 | 0.12817 | 0.13733 | 0.10986 | -0.022888 | 0.13733 | 0.11444 | -0.19226 | 0.086975 | -0.009155 | -0.1236 | -0.041199 | 121.4722 | 121.5729 | 5.2093 | -121.5683 | 121.4035 | 121.5546 | 6.2302 | -121.4813
1081.5156 | 121.7239 | -0.32044 | 121.2616 | -0.012589 | -0.00089927 | 0.066683 | -0.00067498 | 0.067116 | -0.0035633 | -0.00038874 | 0.0021363 | -0.0061929 | 0.063766 | 0.067823 | -0.20382 | -0.0021982 | 121.2341 | -0.2243 | 4.8981 | -0.18768 | 121.1472 | -0.20142 | -0.29297 | -0.23346 | 5.9143 | -0.3479 | 121.1197 | 121.2067 | -0.18768 | -0.22888 | 0.11902 | 0.027466 | -0.11444 | 0.096131 | 0.13275 | 0.10529 | -0.027466 | 0.13275 | 0.091553 | -0.14191 | 0.086976 | -0.027465 | -0.11902 | -0.054932 | 121.4676 | 121.5546 | 5.2185 | -121.5546 | 121.4401 | 121.5271 | 6.2347 | -121.4905
1083.2969 | 121.6324 | -0.36621 | 121.2936 | -0.0049592 | 0.0033731 | 0.066469 | 0.002102 | 0.064125 | 0.0011365 | -0.00060234 | -0.0054932 | -0.0019205 | 0.063553 | 0.066114 | -0.20041 | -0.0030526 | 121.1975 | -0.28381 | 4.9438 | -0.23346 | 121.1884 | -0.27466 | -0.32959 | -0.30212 | 5.9372 | -0.42114 | 121.1517 | 121.2479 | -0.21973 | -0.25177 | 0.091553 | 0.036621 | -0.10529 | 0.082398 | 0.13275 | 0.096131 | -0.09613 | 0.14648 | 0.11444 | -0.14191 | 0.064087 | -0.054932 | -0.16937 | -0.045776 | 121.5546 | 121.5637 | 5.3101 | -121.6232 | 121.5179 | 121.6141 | 6.3034 | -121.5454
1085.0781 | 121.6965 | -0.31586 | 121.2799 | -0.012589 | 0.0010233 | 0.067537 | 0.0012476 | 0.067116 | -0.0024951 | 0.00089286 | -0.0054932 | -0.0046975 | 0.066544 | 0.067823 | -0.20297 | -0.0019846 | 121.2433 | -0.19226 | 4.9759 | -0.1831 | 121.1563 | -0.21057 | -0.29297 | -0.21973 | 5.9601 | -0.32959 | 121.0831 | 121.2341 | -0.16479 | -0.20599 | 0.10529 | 0.022888 | -0.1236 | 0.1236 | 0.13275 | 0.10986 | -0.036621 | 0.15106 | 0.10986 | -0.19684 | 0.09613 | -0.013733 | -0.1236 | -0.045776 | 121.4722 | 121.5591 | 5.2917 | -121.5729 | 121.3989 | 121.55 | 6.2759 | -121.4859
1086.8594 | 121.7285 | -0.31128 | 121.2799 | -0.012589 | 0.0023049 | 0.065187 | 0.0016748 | 0.062844 | -0.0027087 | -0.00081594 | -0.013123 | -0.0036295 | 0.065903 | 0.066755 | -0.20361 | -0.0030526 | 121.312 | -0.14191 | 5.0812 | -0.14191 | 121.1609 | -0.21057 | -0.28381 | -0.17395 | 6.0928 | -0.25177 | 121.0922 | 121.2158 | -0.16479 | -0.21057 | 0.10071 | 0.027466 | -0.11902 | 0.16937 | 0.16937 | 0.14191 | 0.032044 | 0.14648 | 0.10071 | -0.18768 | 0.13733 | 0.059509 | -0.041199 | -0.064087 | 121.4722 | 121.6232 | 5.3925 | -121.5637 | 121.4035 | 121.5271 | 6.4041 | -121.4905
1088.5625 | 121.7285 | -0.30212 | 121.2799 | -0.0049592 | 0.00016873 | 0.065187 | -0.003025 | 0.065621 | 0.0017773 | 0.00046566 | -0.013123 | -0.0025613 | 0.063766 | 0.06761 | -0.19955 | -0.0034798 | 121.3165 | -0.1831 | 5.0446 | -0.13275 | 121.1746 | -0.21973 | -0.27008 | -0.16022 | 6.0562 | -0.28381 | 121.0968 | 121.225 | -0.16479 | -0.19684 | 0.082397 | 0.032043 | -0.10528 | 0.11902 | 0.16937 | 0.13733 | 0.036621 | 0.13733 | 0.10529 | -0.1831 | 0.14191 | 0.018311 | -0.086975 | -0.054931 | 121.4767 | 121.6187 | 5.3467 | -121.55 | 121.3989 | 121.5271 | 6.3583 | -121.4767
1090.3438 | 121.7148 | -0.31128 | 121.2845 | -0.0049592 | 0.0027323 | 0.068178 | -0.00088858 | 0.068184 | -0.0016405 | 0.00046566 | -0.013123 | -0.0042703 | 0.063766 | 0.065473 | -0.20297 | -0.001771 | 121.3394 | -0.1236 | 5.1819 | -0.13275 | 121.1426 | -0.22888 | -0.27924 | -0.16022 | 6.1386 | -0.26093 | 121.0968 | 121.2616 | -0.16479 | -0.21057 | 0.082397 | 0.032043 | -0.14191 | 0.18768 | 0.17853 | 0.14648 | 0.054932 | 0.14648 | 0.10071 | -0.18768 | 0.15106 | 0.050354 | -0.050354 | -0.022888 | 121.4539 | 121.6507 | 5.4932 | -121.5637 | 121.4081 | 121.5729 | 6.4499 | -121.4951
1092.0469 | 121.7377 | -0.32044 | 121.2708 | 0.0026703 | -0.00025847 | 0.065614 | -0.00046138 | 0.066475 | -0.0039905 | -0.0018841 | -0.0054932 | -0.0038431 | 0.064194 | 0.065687 | -0.20105 | -0.0030526 | 121.2433 | -0.23346 | 5.0766 | -0.17395 | 121.1884 | -0.23804 | -0.29755 | -0.23346 | 6.0425 | -0.32044 | 121.1151 | 121.2387 | -0.20599 | -0.20599 | 0.082398 | 0.022889 | -0.082398 | 0.086976 | 0.14649 | 0.1236 | -0.027466 | 0.11444 | 0.11444 | -0.15564 | 0.086976 | 0 | -0.11444 | -0.032044 | 121.5088 | 121.5637 | 5.397 | -121.5683 | 121.4355 | 121.5591 | 6.3629 | -121.4767
1093.8281 | 121.7331 | -0.28381 | 121.2524 | 0.0026703 | 0.0025185 | 0.067964 | -3.4178e-05 | 0.066902 | -0.0029223 | 0.00067926 | -0.0054932 | -0.0021341 | 0.062057 | 0.067182 | -0.19891 | -0.0058298 | 121.3348 | -0.14191 | 5.191 | -0.14191 | 121.1746 | -0.21057 | -0.28381 | -0.16022 | 6.1615 | -0.24261 | 121.1014 | 121.2479 | -0.13733 | -0.19684 | 0.073242 | 0 | -0.077819 | 0.14191 | 0.14191 | 0.14191 | 0.082398 | 0.14648 | 0.086975 | -0.15106 | 0.1236 | 0.041198 | -0.045777 | -0.004577 | 121.4584 | 121.6187 | 5.4749 | -121.5363 | 121.3852 | 121.5317 | 6.4453 | -121.4493
1095.5938 | 121.6049 | -0.34332 | 121.3303 | -0.020218 | 0.0048685 | 0.066469 | 0.002102 | 0.063698 | 0.0026319 | 0.00067926 | -0.0054932 | -0.0014933 | 0.065262 | 0.067396 | -0.20041 | -0.0039072 | 121.2341 | -0.24719 | 5.1773 | -0.20142 | 121.1975 | -0.25635 | -0.31128 | -0.27008 | 6.0471 | -0.39368 | 121.1609 | 121.2708 | -0.19226 | -0.22888 | 0.086975 | 0.032044 | -0.13275 | 0.096131 | 0.14191 | 0.10986 | -0.09613 | 0.15106 | 0.11444 | -0.16937 | 0.073242 | -0.050354 | -0.16479 | -0.059509 | 121.5408 | 121.5775 | 5.5206 | -121.6415 | 121.5042 | 121.6141 | 6.3904 | -121.5591
1097.3125 | 121.7377 | -0.29297 | 121.2799 | 0.0026703 | 0.0016641 | 0.063692 | 0.00017942 | 0.06498 | 0.0034863 | 0.0021747 | -0.013123 | -0.00085232 | 0.062912 | 0.068678 | -0.19806 | -0.0047616 | 121.2708 | -0.25635 | 5.1407 | -0.1831 | 121.2112 | -0.23346 | -0.29755 | -0.16937 | 6.1386 | -0.32501 | 121.1197 | 121.2433 | -0.17395 | -0.21057 | 0.05951 | -0.004577 | -0.068664 | 0.036621 | 0.10986 | 0.11444 | -0.009155 | 0.11902 | 0.082398 | -0.16022 | 0.1236 | -0.032043 | -0.11444 | -0.036621 | 121.5042 | 121.5637 | 5.4337 | -121.5775 | 121.4127 | 121.5363 | 6.4316 | -121.4905
1099.0938 | 121.6003 | -0.33875 | 121.3074 | 0.0026703 | 0.0074319 | 0.063265 | -3.4178e-05 | 0.066262 | 0.0036999 | 0.00067926 | 0.0097658 | -0.00042512 | 0.065689 | 0.068891 | -0.19977 | -0.004548 | 121.2753 | -0.22888 | 5.2368 | -0.17395 | 121.2158 | -0.24261 | -0.3067 | -0.21515 | 6.1661 | -0.37994 | 121.138 | 121.2845 | -0.20142 | -0.23346 | 0.09613 | 0.032043 | -0.091553 | 0.10986 | 0.1648 | 0.13275 | -0.032043 | 0.13733 | 0.10529 | -0.16937 | 0.1236 | -0.041199 | -0.14649 | -0.022888 | 121.5546 | 121.6141 | 5.5756 | -121.6141 | 121.4767 | 121.6232 | 6.5048 | -121.5408
1100.8594 | 121.7285 | -0.31128 | 121.2982 | -0.0049592 | 0.0050821 | 0.066683 | 0.002102 | 0.066048 | -0.0042041 | -0.00081594 | -0.0054932 | -0.0068337 | 0.062912 | 0.067823 | -0.20062 | -0.00091641 | 121.2296 | -0.20142 | 5.2231 | -0.16022 | 121.1838 | -0.21515 | -0.27466 | -0.23346 | 6.1523 | -0.32044 | 121.1014 | 121.2662 | -0.16022 | -0.21057 | 0.09613 | 0.036621 | -0.11444 | 0.10986 | 0.15106 | 0.11444 | -0.068665 | 0.15106 | 0.10071 | -0.19684 | 0.07782 | -0.009156 | -0.10986 | -0.032044 | 121.4951 | 121.5408 | 5.5344 | -121.5729 | 121.4127 | 121.5775 | 6.4636 | -121.5088
1102.5781 | 121.6873 | -0.31586 | 121.312 | 0.0026703 | 0.0029459 | 0.065187 | 0.0027428 | 0.066048 | -0.0018543 | 0.0028155 | -0.013123 | -0.0042703 | 0.063553 | 0.067823 | -0.20404 | -0.0026254 | 121.2708 | -0.1831 | 5.2689 | -0.16022 | 121.1517 | -0.19226 | -0.25635 | -0.2243 | 6.1569 | -0.32044 | 121.1197 | 121.2479 | -0.16937 | -0.18768 | 0.1236 | 0.059509 | -0.16022 | 0.13275 | 0.15564 | 0.096131 | -0.041199 | 0.14648 | 0.12817 | -0.19226 | 0.091553 | -0.004578 | -0.13275 | -0.064087 | 121.4676 | 121.5866 | 5.5847 | -121.5683 | 121.4355 | 121.5637 | 6.4728 | -121.4996
1104.3594 | 121.7239 | -0.28381 | 121.2799 | 0.0026703 | 0.0033731 | 0.064974 | -0.001316 | 0.063698 | 0.00092287 | 0.0023883 | -0.013123 | -0.0025613 | 0.064407 | 0.068037 | -0.20083 | -0.004548 | 121.3348 | -0.15106 | 5.3284 | -0.11902 | 121.1884 | -0.19684 | -0.27466 | -0.14191 | 6.2347 | -0.27008 | 121.1243 | 121.2296 | -0.13733 | -0.1831 | 0.086975 | 0.009155 | -0.091553 | 0.13275 | 0.16479 | 0.15564 | 0.054932 | 0.14648 | 0.10071 | -0.15564 | 0.14191 | 0.013732 | -0.086976 | -0.050354 | 121.4722 | 121.6187 | 5.6122 | -121.5546 | 121.4081 | 121.5134 | 6.5186 | -121.463
1106.125 | 121.6141 | -0.32959 | 121.3074 | 0.0026703 | 0.0061501 | 0.064333 | -0.002384 | 0.066902 | 0.0032727 | 0.0030293 | -0.013123 | -0.00042512 | 0.063339 | 0.067396 | -0.19656 | -0.0043344 | 121.225 | -0.31128 | 5.278 | -0.20599 | 121.2387 | -0.24261 | -0.3067 | -0.27008 | 6.1478 | -0.43488 | 121.1563 | 121.3257 | -0.17853 | -0.23346 | 0.086975 | 0.022888 | -0.068665 | 0.018311 | 0.1236 | 0.10071 | -0.082397 | 0.15106 | 0.096131 | -0.15106 | 0.059509 | -0.10529 | -0.20142 | 0.018311 | 121.5683 | 121.5546 | 5.6076 | -121.6141 | 121.4859 | 121.6553 | 6.4774 | -121.5408
1107.8281 | 121.6003 | -0.33875 | 121.2982 | -0.0049592 | 0.0059365 | 0.064974 | -0.001316 | 0.066475 | 0.0034863 | 0.0034565 | -0.0054932 | -0.00042512 | 0.064835 | 0.066969 | -0.19742 | -0.0039072 | 121.2433 | -0.27466 | 5.3238 | -0.20142 | 121.2296 | -0.21973 | -0.27008 | -0.25635 | 6.1844 | -0.41657 | 121.1517 | 121.312 | -0.1831 | -0.21973 | 0.11902 | 0.068664 | -0.068665 | 0.064087 | 0.13733 | 0.068665 | -0.054932 | 0.15564 | 0.11902 | -0.14649 | 0.082397 | -0.07782 | -0.19684 | 0.013733 | 121.5683 | 121.582 | 5.6625 | -121.5683 | 121.4905 | 121.6507 | 6.5231 | -121.5179
1109.5781 | 121.6507 | -0.32501 | 121.2753 | -0.0049592 | 0.0059365 | 0.068178 | -0.002384 | 0.066048 | 0.0028455 | 0.0030293 | 0.0021363 | -0.0014933 | 0.066544 | 0.068037 | -0.19977 | -0.00113 | 121.225 | -0.3067 | 5.3055 | -0.2243 | 121.2296 | -0.22888 | -0.29297 | -0.27008 | 6.189 | -0.39368 | 121.1838 | 121.3165 | -0.17395 | -0.23804 | 0.09613 | 0.032043 | -0.045777 | 0.01831 | 0.10071 | 0.068665 | -0.050354 | 0.15106 | 0.086975 | -0.091553 | 0.054931 | -0.068665 | -0.15564 | 0.041198 | 121.5546 | 121.55 | 5.6305 | -121.5683 | 121.5088 | 121.6415 | 6.514 | -121.5134
1111.3594 | 121.6919 | -0.32044 | 121.2845 | -0.0049592 | 0.00080973 | 0.066042 | 0.0025292 | 0.063698 | -0.0044177 | 0.0015339 | 0.0021363 | -0.0042703 | 0.062271 | 0.069532 | -0.20318 | -0.0019846 | 121.2708 | -0.16937 | 5.4291 | -0.16479 | 121.1655 | -0.21057 | -0.27466 | -0.20599 | 6.2485 | -0.28381 | 121.1197 | 121.2708 | -0.15564 | -0.17853 | 0.10986 | 0.045777 | -0.11902 | 0.15106 | 0.15564 | 0.10986 | -0.013733 | 0.1648 | 0.14191 | -0.16479 | 0.11444 | 0.036622 | -0.10528 | -0.013733 | 121.4859 | 121.5912 | 5.7495 | -121.5591 | 121.4401 | 121.5912 | 6.5689 | -121.463
1113.0781 | 121.7102 | -0.3067 | 121.2982 | -0.012589 | 0.0048685 | 0.064333 | 0.00552 | 0.068611 | -0.0035633 | -0.00060234 | -0.0054932 | -0.0068337 | 0.066544 | 0.066755 | -0.20276 | -0.001771 | 121.3303 | -0.13733 | 5.5618 | -0.11444 | 121.1609 | -0.21973 | -0.2655 | -0.16937 | 6.3858 | -0.22888 | 121.1288 | 121.225 | -0.16022 | -0.18768 | 0.086975 | 0.041199 | -0.13733 | 0.16937 | 0.19226 | 0.15106 | 0.032043 | 0.14648 | 0.11902 | -0.16937 | 0.13733 | 0.07782 | -0.041199 | -0.073242 | 121.4676 | 121.637 | 5.8685 | -121.5637 | 121.4355 | 121.5317 | 6.6925 | -121.4859
1114.8594 | 121.6461 | -0.31586 | 121.3165 | 0.0026703 | 0.0080727 | 0.065614 | 0.003811 | 0.069252 | 0.0045545 | 0.0011067 | -0.0054932 | -0.0023477 | 0.064194 | 0.06825 | -0.20041 | -0.0034798 | 121.2296 | -0.27466 | 5.4977 | -0.18768 | 121.2524 | -0.23804 | -0.3067 | -0.25635 | 6.3126 | -0.37537 | 121.1838 | 121.2616 | -0.19226 | -0.20599 | 0.07782 | 0.009155 | -0.064087 | 0.041199 | 0.12817 | 0.11902 | -0.086975 | 0.1236 | 0.10986 | -0.13275 | 0.059509 | -0.059509 | -0.16937 | -0.054931 | 121.5683 | 121.5454 | 5.8136 | -121.6232 | 121.4996 | 121.5775 | 6.6284 | -121.5225
1116.5469 | 121.5866 | -0.34332 | 121.3531 | -0.012589 | 0.0099953 | 0.063051 | 0.0046656 | 0.067757 | 0.0039135 | 0.0011067 | 0.0097658 | -0.00063872 | 0.067612 | 0.068037 | -0.19934 | -0.0024118 | 121.2753 | -0.21973 | 5.5298 | -0.17853 | 121.2296 | -0.2243 | -0.29755 | -0.21057 | 6.3309 | -0.36621 | 121.1563 | 121.2708 | -0.21057 | -0.21057 | 0.11902 | 0.045777 | -0.1236 | 0.1236 | 0.16479 | 0.11902 | -0.077819 | 0.13275 | 0.13275 | -0.19684 | 0.13275 | -0.022888 | -0.15564 | -0.082397 | 121.5729 | 121.6187 | 5.8731 | -121.6507 | 121.4996 | 121.6141 | 6.6742 | -121.5637
1118.3125 | 121.701 | -0.31586 | 121.312 | -0.0049592 | 0.00038233 | 0.066896 | -0.00046138 | 0.067116 | -0.0046313 | 0.0019611 | 0.0021363 | -0.0042703 | 0.063766 | 0.066328 | -0.20083 | -0.0015572 | 121.2708 | -0.14191 | 5.5527 | -0.14191 | 121.1609 | -0.20142 | -0.26093 | -0.20142 | 6.34 | -0.27466 | 121.1105 | 121.2524 | -0.16022 | -0.19226 | 0.11444 | 0.054932 | -0.15106 | 0.17395 | 0.17395 | 0.11902 | -0.041199 | 0.15564 | 0.1236 | -0.20142 | 0.11444 | 0.041199 | -0.082397 | -0.05951 | 121.4767 | 121.5866 | 5.8685 | -121.5729 | 121.4264 | 121.5683 | 6.6559 | -121.5042
1120.0938 | 121.7377 | -0.27466 | 121.3028 | 0.0026703 | 0.0052957 | 0.063478 | 0.00017942 | 0.064553 | -0.00057253 | 0.0026019 | -0.0054932 | -0.0027749 | 0.065903 | 0.068464 | -0.19912 | -0.0026254 | 121.2616 | -0.23804 | 5.5252 | -0.17853 | 121.2158 | -0.21973 | -0.28839 | -0.18768 | 6.3766 | -0.3067 | 121.1334 | 121.2753 | -0.16022 | -0.19684 | 0.054931 | -0.013733 | -0.086975 | 0.036621 | 0.09613 | 0.10986 | -0.041198 | 0.11444 | 0.07782 | -0.16937 | 0.086975 | -0.032044 | -0.10986 | -0.027465 | 121.4905 | 121.5363 | 5.7999 | -121.5912 | 121.4081 | 121.55 | 6.6513 | -121.4996
1121.7969 | 121.6095 | -0.3479 | 121.3165 | -0.0049592 | 0.0055093 | 0.067751 | -0.001316 | 0.064125 | -0.0039905 | -0.00017514 | -0.0054932 | -0.0051247 | 0.063339 | 0.065901 | -0.20212 | -0.00113 | 121.2296 | -0.21973 | 5.6168 | -0.17395 | 121.2112 | -0.22888 | -0.29755 | -0.28381 | 6.3583 | -0.35248 | 121.1838 | 121.3211 | -0.18768 | -0.21057 | 0.11902 | 0.050354 | -0.10529 | 0.12817 | 0.17395 | 0.1236 | -0.086975 | 0.16022 | 0.13733 | -0.13275 | 0.064087 | -0.004578 | -0.14191 | 0.004578 | 121.5591 | 121.5775 | 5.9647 | -121.6141 | 121.5317 | 121.669 | 6.7062 | -121.5271
1123.5625 | 121.6141 | -0.32044 | 121.3531 | -0.0049592 | 0.0050821 | 0.066469 | -0.0017432 | 0.064339 | 0.0028455 | 0.0013203 | -0.013123 | 0.00021568 | 0.062057 | 0.06825 | -0.1987 | -6.2012e-05 | 121.2158 | -0.32044 | 5.5618 | -0.20142 | 121.2204 | -0.20599 | -0.30212 | -0.25177 | 6.3126 | -0.39825 | 121.1655 | 121.344 | -0.1831 | -0.23346 | 0.11444 | 0.018311 | -0.13275 | 0 | 0.11902 | 0.10071 | -0.13733 | 0.13733 | 0.086976 | -0.18768 | 0.068665 | -0.077819 | -0.16479 | -0.009155 | 121.5408 | 121.5363 | 5.8823 | -121.6553 | 121.4859 | 121.6644 | 6.633 | -121.5866
1125.3438 | 121.7056 | -0.29297 | 121.3028 | -0.012589 | 0.0048685 | 0.064119 | -0.0011024 | 0.066902 | -0.0024951 | 0.00025206 | -0.013123 | -0.0027749 | 0.063339 | 0.066328 | -0.20083 | -0.00048921 | 121.3211 | -0.13275 | 5.6946 | -0.11902 | 121.2067 | -0.19684 | -0.24719 | -0.13733 | 6.4407 | -0.24261 | 121.1151 | 121.2799 | -0.16479 | -0.1831 | 0.096131 | 0.045777 | -0.09613 | 0.16022 | 0.17395 | 0.12817 | 0.018311 | 0.12817 | 0.10986 | -0.18768 | 0.15564 | 0.050354 | -0.05951 | -0.022888 | 121.4996 | 121.6141 | 5.9875 | -121.55 | 121.4081 | 121.5729 | 6.7337 | -121.4859
1127.0469 | 121.6873 | -0.29297 | 121.3028 | -0.0049592 | -0.0019675 | 0.066896 | 0.0023156 | 0.066262 | -0.0042041 | -0.0016705 | 0.0021363 | -0.0064065 | 0.066116 | 0.066755 | -0.20147 | -0.002839 | 121.2662 | -0.1831 | 5.6671 | -0.15564 | 121.2204 | -0.19226 | -0.25635 | -0.20599 | 6.3858 | -0.29755 | 121.1609 | 121.2891 | -0.14648 | -0.19684 | 0.10071 | 0.036621 | -0.082397 | 0.10986 | 0.13733 | 0.10071 | -0.036621 | 0.14648 | 0.096131 | -0.14191 | 0.086975 | -0.004577 | -0.10071 | -0.013733 | 121.5134 | 121.5591 | 5.9601 | -121.5591 | 121.4539 | 121.582 | 6.6788 | -121.4996
1128.8281 | 121.7239 | -0.28381 | 121.3165 | -0.020218 | 0.0040139 | 0.066683 | 0.0029566 | 0.066048 | -0.0042041 | -0.0012433 | 0.0021363 | -0.0064065 | 0.06398 | 0.066755 | -0.20212 | -0.00113 | 121.2616 | -0.19684 | 5.7037 | -0.15106 | 121.1929 | -0.20142 | -0.2655 | -0.21973 | 6.395 | -0.29755 | 121.1563 | 121.3028 | -0.15106 | -0.17853 | 0.082397 | 0.01831 | -0.1236 | 0.086975 | 0.13275 | 0.11444 | -0.054931 | 0.13275 | 0.10528 | -0.16022 | 0.064086 | -0.013733 | -0.11902 | -0.013733 | 121.4767 | 121.5454 | 5.9875 | -121.582 | 121.4401 | 121.5866 | 6.6788 | -121.4951
1130.5938 | 121.6324 | -0.31586 | 121.3394 | -0.0049592 | 0.0052957 | 0.064333 | 0.00017942 | 0.067757 | 0.0047681 | -0.00017514 | 0.0097658 | -0.0010659 | 0.06633 | 0.069532 | -0.19784 | -0.0054026 | 121.225 | -0.31128 | 5.6671 | -0.18768 | 121.257 | -0.23346 | -0.3067 | -0.24261 | 6.3766 | -0.37994 | 121.2158 | 121.2936 | -0.1831 | -0.21973 | 0.082398 | 0.009155 | -0.082398 | 0.004578 | 0.12817 | 0.11902 | -0.11444 | 0.13275 | 0.09613 | -0.1236 | 0.073242 | -0.064087 | -0.16022 | -0.045777 | 121.5729 | 121.5408 | 5.983 | -121.6461 | 121.5317 | 121.6095 | 6.6925 | -121.5591
1132.375 | 121.6324 | -0.34332 | 121.3303 | -0.012589 | 0.0048685 | 0.064546 | -0.0021704 | 0.066902 | 0.00092287 | 0.0038837 | 0.0021363 | -0.0010659 | 0.064621 | 0.067182 | -0.19891 | -0.0032662 | 121.2296 | -0.31586 | 5.6946 | -0.21057 | 121.2387 | -0.21057 | -0.28381 | -0.25635 | 6.4087 | -0.39825 | 121.1975 | 121.3257 | -0.15564 | -0.20142 | 0.13275 | 0.05951 | -0.091553 | 0.027466 | 0.13275 | 0.073242 | -0.10071 | 0.18768 | 0.14191 | -0.13275 | 0.086975 | -0.054931 | -0.19684 | -0.004577 | 121.582 | 121.5729 | 6.0379 | -121.6141 | 121.5408 | 121.669 | 6.752 | -121.5317
1134.0781 | 121.7102 | -0.27924 | 121.2936 | -0.0049592 | 0.0050821 | 0.065187 | 0.0023156 | 0.067116 | 0.00070927 | 0.0017475 | -0.013123 | -0.0036295 | 0.066971 | 0.070173 | -0.1987 | -0.0024118 | 121.2387 | -0.26093 | 5.7358 | -0.19226 | 121.257 | -0.21057 | -0.29297 | -0.21057 | 6.4178 | -0.35706 | 121.1884 | 121.2799 | -0.16937 | -0.20142 | 0.068665 | -0.013733 | -0.036621 | 0.018311 | 0.086975 | 0.10071 | -0.054932 | 0.10986 | 0.07782 | -0.10529 | 0.068665 | -0.07782 | -0.15564 | -0.013733 | 121.5363 | 121.5179 | 6.015 | -121.5866 | 121.4676 | 121.5591 | 6.6971 | -121.4951
1135.8438 | 121.6187 | -0.33417 | 121.3348 | -0.012589 | 0.0031595 | 0.063478 | -0.0015296 | 0.065407 | 0.0028455 | 0.0032429 | 0.0021363 | -0.00042512 | 0.066971 | 0.069105 | -0.20083 | -0.0019846 | 121.2296 | -0.27924 | 5.777 | -0.20142 | 121.257 | -0.21973 | -0.29297 | -0.2655 | 6.4316 | -0.43488 | 121.1975 | 121.3211 | -0.17853 | -0.20599 | 0.11444 | 0.041198 | -0.07782 | 0.054931 | 0.13275 | 0.091553 | -0.10529 | 0.15564 | 0.12817 | -0.13733 | 0.068664 | -0.10071 | -0.22888 | -0.013733 | 121.5912 | 121.5637 | 6.1111 | -121.6278 | 121.5317 | 121.6553 | 6.7657 | -121.5408
1137.6094 | 121.7422 | -0.27924 | 121.3165 | -0.0049592 | 0.0018777 | 0.067751 | 0.0029566 | 0.06733 | -0.0063403 | -0.0010297 | -0.020752 | -0.0053385 | 0.065262 | 0.064619 | -0.2034 | -0.001771 | 121.2341 | -0.17853 | 5.8411 | -0.15106 | 121.2204 | -0.18768 | -0.23346 | -0.21973 | 6.5094 | -0.27924 | 121.1472 | 121.2753 | -0.13733 | -0.18768 | 0.091553 | 0.045777 | -0.09613 | 0.10071 | 0.12817 | 0.082397 | -0.082397 | 0.14191 | 0.091553 | -0.16937 | 0.059509 | 0 | -0.091553 | -0.041198 | 121.4996 | 121.5134 | 6.1203 | -121.55 | 121.4264 | 121.5546 | 6.7886 | -121.5042
1139.3906 | 121.6873 | -0.29297 | 121.3348 | -0.0049592 | 0.0035867 | 0.066469 | 0.0035974 | 0.066048 | -0.0037769 | 0.00067926 | -0.013123 | -0.0036295 | 0.065048 | 0.070173 | -0.20276 | -0.0026254 | 121.2936 | -0.15564 | 5.8823 | -0.14191 | 121.2204 | -0.17395 | -0.24719 | -0.19226 | 6.5002 | -0.29297 | 121.1472 | 121.2799 | -0.13733 | -0.16022 | 0.11902 | 0.045777 | -0.11444 | 0.13733 | 0.15106 | 0.10528 | -0.041199 | 0.15564 | 0.13275 | -0.18768 | 0.10071 | 0 | -0.13275 | -0.054932 | 121.5134 | 121.5866 | 6.1752 | -121.582 | 121.4401 | 121.5729 | 6.7932 | -121.4951
1141.1719 | 121.7377 | -0.2655 | 121.3165 | -0.0049592 | 0.00080973 | 0.062624 | -0.001316 | 0.064766 | 0.00070927 | -0.00017514 | 0.0021363 | -0.0044839 | 0.065475 | 0.069746 | -0.19955 | -0.0051888 | 121.3303 | -0.12817 | 5.9784 | -0.086975 | 121.2204 | -0.17395 | -0.23346 | -0.11444 | 6.5826 | -0.23346 | 121.1288 | 121.2433 | -0.14648 | -0.15564 | 0.091553 | 0.032044 | -0.09613 | 0.13733 | 0.17853 | 0.14648 | 0.013733 | 0.11902 | 0.10986 | -0.18768 | 0.15106 | 0.032044 | -0.077819 | -0.073242 | 121.4859 | 121.5958 | 6.2439 | -121.55 | 121.3943 | 121.5088 | 6.8481 | -121.4722
1142.9531 | 121.6507 | -0.31128 | 121.3577 | -0.0049592 | 0.0042275 | 0.06241 | 0.001034 | 0.066689 | 0.0019909 | 0.0017475 | -0.013123 | -0.00063872 | 0.064835 | 0.066328 | -0.19806 | -0.0056162 | 121.2845 | -0.20599 | 5.9921 | -0.13733 | 121.2524 | -0.20142 | -0.26093 | -0.1831 | 6.6513 | -0.32501 | 121.1838 | 121.3074 | -0.16479 | -0.19684 | 0.10986 | 0.050354 | -0.10529 | 0.10528 | 0.17395 | 0.1236 | -0.073242 | 0.14648 | 0.11444 | -0.17395 | 0.12817 | -0.013733 | -0.12817 | -0.050354 | 121.5637 | 121.5958 | 6.3034 | -121.6187 | 121.4951 | 121.6187 | 6.9626 | -121.5546
1144.6562 | 121.6644 | -0.30212 | 121.3394 | 0.0026703 | 0.0065775 | 0.065187 | 0.0012476 | 0.06733 | 0.00028207 | 0.0011067 | -0.0054932 | -0.0010659 | 0.067398 | 0.066328 | -0.19912 | -0.0030526 | 121.225 | -0.24261 | 5.9921 | -0.17395 | 121.2616 | -0.20599 | -0.28839 | -0.21973 | 6.6238 | -0.3479 | 121.1884 | 121.3165 | -0.16479 | -0.21057 | 0.09613 | 0.013733 | -0.07782 | 0.059509 | 0.12817 | 0.11444 | -0.11444 | 0.13733 | 0.091553 | -0.15106 | 0.082397 | -0.045776 | -0.13733 | -0.022889 | 121.5637 | 121.5271 | 6.2942 | -121.6278 | 121.4905 | 121.6187 | 6.926 | -121.55
1146.4219 | 121.7148 | -0.29755 | 121.3165 | -0.0049592 | -4.4874e-05 | 0.066255 | 0.001034 | 0.065621 | -0.0033495 | -0.0025249 | -0.0054932 | -0.0055521 | 0.064407 | 0.066542 | -0.20318 | -0.0013436 | 121.2708 | -0.16937 | 6.0196 | -0.13733 | 121.1975 | -0.16937 | -0.25177 | -0.20599 | 6.6193 | -0.27466 | 121.1426 | 121.3074 | -0.13275 | -0.16022 | 0.12817 | 0.045776 | -0.11902 | 0.12817 | 0.16022 | 0.11444 | -0.045776 | 0.16479 | 0.13733 | -0.17395 | 0.091552 | 0.022888 | -0.11444 | -0.009155 | 121.4951 | 121.5683 | 6.3171 | -121.5683 | 121.4401 | 121.6049 | 6.9168 | -121.4767
1148.2031 | 121.6049 | -0.31128 | 121.3303 | 0.0026703 | 0.0059365 | 0.066042 | 0.003811 | 0.065621 | -0.00099973 | 0.00025206 | -0.0054932 | -0.0040567 | 0.065048 | 0.067182 | -0.20254 | -0.0019846 | 121.2936 | -0.15106 | 6.1203 | -0.12817 | 121.2158 | -0.18768 | -0.25635 | -0.21973 | 6.6696 | -0.32044 | 121.1838 | 121.312 | -0.16022 | -0.18768 | 0.1236 | 0.054931 | -0.11444 | 0.16022 | 0.1831 | 0.12817 | -0.036621 | 0.15106 | 0.1236 | -0.14648 | 0.091552 | -0.009156 | -0.13275 | -0.01831 | 121.5271 | 121.6049 | 6.4316 | -121.5866 | 121.4951 | 121.6232 | 6.9809 | -121.5179
1149.9688 | 121.7422 | -0.27008 | 121.344 | -0.012589 | 0.0023049 | 0.066255 | 0.0014612 | 0.06498 | -0.0044177 | -0.0010297 | 0.0021363 | -0.0040567 | 0.066544 | 0.06825 | -0.20318 | -0.0039072 | 121.2708 | -0.17395 | 6.0791 | -0.13275 | 121.2158 | -0.1831 | -0.24261 | -0.18768 | 6.6925 | -0.25635 | 121.1563 | 121.2936 | -0.11902 | -0.16022 | 0.086976 | 0.027466 | -0.12817 | 0.096131 | 0.13733 | 0.10986 | -0.073242 | 0.15106 | 0.10986 | -0.18768 | 0.082398 | 0.013733 | -0.096131 | -0.050354 | 121.4859 | 121.5408 | 6.3492 | -121.5866 | 121.4264 | 121.5637 | 6.9626 | -121.5042
1151.6719 | 121.6919 | -0.27466 | 121.3348 | -0.0049592 | 0.0035867 | 0.064119 | -0.00046138 | 0.06498 | 0.0041273 | 0.00046566 | 0.0021363 | -0.00085232 | 0.065262 | 0.068037 | -0.19977 | -0.0047616 | 121.2662 | -0.25177 | 6.0242 | -0.17853 | 121.2662 | -0.21515 | -0.27008 | -0.21515 | 6.6147 | -0.35706 | 121.225 | 121.312 | -0.16022 | -0.19226 | 0.059509 | 0.004577 | -0.068665 | 0.022888 | 0.09613 | 0.091553 | -0.068665 | 0.11444 | 0.082397 | -0.10986 | 0.059509 | -0.082398 | -0.16479 | -0.022888 | 121.5408 | 121.5408 | 6.2988 | -121.6049 | 121.4996 | 121.5866 | 6.8893 | -121.5271
1153.4375 | 121.6919 | -0.25177 | 121.3028 | 0.0026703 | 0.0035867 | 0.066255 | 0.00082022 | 0.066902 | -0.0027087 | 0.0011067 | -0.020752 | -0.0051247 | 0.065262 | 0.065687 | -0.20212 | -0.0032662 | 121.3531 | -0.10986 | 6.1844 | -0.086975 | 121.2112 | -0.14648 | -0.24719 | -0.1236 | 6.752 | -0.25177 | 121.1517 | 121.2845 | -0.11902 | -0.15106 | 0.10529 | 0.004578 | -0.091552 | 0.14191 | 0.16479 | 0.16022 | 0.050354 | 0.13275 | 0.10071 | -0.15106 | 0.12817 | 0 | -0.10071 | -0.01831 | 121.463 | 121.6049 | 6.4362 | -121.55 | 121.4035 | 121.5363 | 7.0038 | -121.4539
1155.1719 | 121.756 | -0.27008 | 121.3211 | -0.0049592 | 0.0029459 | 0.069032 | 0.001034 | 0.065834 | -0.0042041 | -0.00081594 | 0.0021363 | -0.0057657 | 0.064835 | 0.065687 | -0.20062 | -0.0047616 | 121.312 | -0.15564 | 6.1981 | -0.10986 | 121.2204 | -0.16937 | -0.23804 | -0.14648 | 6.7474 | -0.23346 | 121.1426 | 121.2936 | -0.1236 | -0.16022 | 0.10071 | 0.032044 | -0.10071 | 0.11444 | 0.16022 | 0.12817 | -0.009155 | 0.14649 | 0.10986 | -0.17853 | 0.1236 | 0.036622 | -0.073242 | -0.027466 | 121.4905 | 121.582 | 6.4682 | -121.5591 | 121.4127 | 121.5637 | 7.0175 | -121.4813
1156.9531 | 121.6919 | -0.27008 | 121.3348 | 0.0103 | 0.0025185 | 0.065187 | 0.0023156 | 0.064339 | -0.0020679 | -0.0014569 | -0.0054932 | -0.0032021 | 0.064407 | 0.06761 | -0.2019 | -0.0024118 | 121.3074 | -0.14648 | 6.221 | -0.13275 | 121.2296 | -0.16937 | -0.25177 | -0.16937 | 6.7154 | -0.27924 | 121.1655 | 121.2799 | -0.13733 | -0.16479 | 0.10071 | 0.018311 | -0.10529 | 0.1236 | 0.13733 | 0.11902 | -0.027466 | 0.13275 | 0.10529 | -0.16937 | 0.10071 | -0.009155 | -0.11444 | -0.054932 | 121.4996 | 121.5775 | 6.4911 | -121.5866 | 121.4355 | 121.55 | 6.9855 | -121.4996
1158.7188 | 121.7331 | -0.23346 | 121.312 | 0.0026703 | 0.0018777 | 0.065614 | -0.001316 | 0.06733 | 0.0041273 | 0.0013203 | -0.013123 | -0.0014933 | 0.065048 | 0.068037 | -0.20041 | -0.0041208 | 121.3028 | -0.18768 | 6.1981 | -0.14648 | 121.2708 | -0.1831 | -0.23804 | -0.13733 | 6.7749 | -0.28381 | 121.1929 | 121.2616 | -0.14648 | -0.15564 | 0.050354 | -0.004578 | -0.041199 | 0.045776 | 0.086975 | 0.091553 | -0.009156 | 0.086975 | 0.077819 | -0.11902 | 0.09613 | -0.050354 | -0.12817 | -0.050354 | 121.5042 | 121.5363 | 6.4316 | -121.55 | 121.4264 | 121.4951 | 7.0084 | -121.4676
1160.4219 | 121.7239 | -0.25177 | 121.3165 | -0.0049592 | 0.0038003 | 0.064974 | 0.0042382 | 0.067116 | -0.0042041 | 0.0017475 | 0.0021363 | -0.0044839 | 0.065903 | 0.067396 | -0.20147 | -0.0034798 | 121.3715 | -0.059509 | 6.3629 | -0.09613 | 121.2204 | -0.17853 | -0.22888 | -0.11902 | 6.9077 | -0.20142 | 121.1472 | 121.2616 | -0.10071 | -0.16937 | 0.073242 | 0.022888 | -0.09613 | 0.19226 | 0.15564 | 0.13275 | 0.054932 | 0.15106 | 0.082397 | -0.16937 | 0.13275 | 0.050354 | -0.032043 | -0.054931 | 121.4722 | 121.6232 | 6.6147 | -121.5454 | 121.3989 | 121.5134 | 7.1594 | -121.4859
1162.2031 | 121.7422 | -0.26093 | 121.344 | -0.0049592 | 0.0029459 | 0.06711 | 0.0018884 | 0.062844 | -0.0039905 | -0.0012433 | -0.013123 | -0.0053385 | 0.062912 | 0.066542 | -0.20233 | -0.0036936 | 121.3394 | -0.091553 | 6.3492 | -0.086975 | 121.225 | -0.16022 | -0.22888 | -0.11444 | 6.8893 | -0.1831 | 121.1426 | 121.2662 | -0.12817 | -0.15564 | 0.10071 | 0.032043 | -0.11902 | 0.16937 | 0.17395 | 0.14191 | -0.004577 | 0.13275 | 0.10529 | -0.20142 | 0.14648 | 0.07782 | -0.027465 | -0.07782 | 121.4859 | 121.6003 | 6.6101 | -121.5729 | 121.4035 | 121.5271 | 7.1503 | -121.4996
1163.9688 | 121.6049 | -0.30212 | 121.3806 | -0.0049592 | 0.0025185 | 0.067323 | -0.0011024 | 0.066902 | 6.8274e-05 | 3.8456e-05 | -0.013123 | -0.0034159 | 0.063553 | 0.06526 | -0.20169 | -0.0036936 | 121.3257 | -0.13733 | 6.3904 | -0.11444 | 121.2479 | -0.16937 | -0.25635 | -0.18768 | 6.8527 | -0.31128 | 121.2067 | 121.312 | -0.14191 | -0.1831 | 0.13275 | 0.045776 | -0.13275 | 0.16479 | 0.18768 | 0.14191 | -0.054931 | 0.16022 | 0.11902 | -0.17395 | 0.11444 | -0.009155 | -0.12817 | -0.068664 | 121.55 | 121.6278 | 6.6925 | -121.637 | 121.5088 | 121.6141 | 7.1548 | -121.5637
1165.7344 | 121.7239 | -0.25635 | 121.3211 | -0.0049592 | 0.0035867 | 0.065187 | -0.0019568 | 0.064339 | 0.00092287 | 0.0013203 | 0.0021363 | -0.0044839 | 0.06398 | 0.067396 | -0.19742 | -0.0019846 | 121.3669 | -0.09613 | 6.3995 | -0.073242 | 121.2387 | -0.15564 | -0.22888 | -0.086975 | 6.8802 | -0.23804 | 121.1884 | 121.2936 | -0.11444 | -0.14648 | 0.10071 | 0.027466 | -0.082398 | 0.16022 | 0.18311 | 0.15564 | 0.045776 | 0.14191 | 0.10986 | -0.13275 | 0.16937 | 0.018311 | -0.091553 | -0.027466 | 121.4951 | 121.6232 | 6.6559 | -121.55 | 121.4447 | 121.55 | 7.1365 | -121.4676
1167.4844 | 121.637 | -0.28381 | 121.3715 | -0.0049592 | 0.0063639 | 0.063905 | -0.0034522 | 0.065621 | 0.0017773 | 0.00046566 | -0.013123 | -0.0023477 | 0.062912 | 0.069959 | -0.19891 | -0.0043344 | 121.2524 | -0.26093 | 6.3263 | -0.16022 | 121.2891 | -0.17853 | -0.27008 | -0.21515 | 6.8115 | -0.37994 | 121.2067 | 121.3486 | -0.15106 | -0.17853 | 0.10528 | 0.013732 | -0.082398 | 0.022888 | 0.1236 | 0.10986 | -0.11902 | 0.13275 | 0.10528 | -0.16479 | 0.068664 | -0.096131 | -0.20142 | -0.022888 | 121.5729 | 121.5363 | 6.6101 | -121.6415 | 121.4905 | 121.6324 | 7.0953 | -121.55
1169.1875 | 121.6232 | -0.30212 | 121.3669 | -0.012589 | 0.0046549 | 0.06476 | -0.002384 | 0.066902 | 0.0026319 | 0.0036701 | -0.0054932 | 0.0023521 | 0.064407 | 0.068037 | -0.19934 | -0.00027561 | 121.2662 | -0.2655 | 6.3583 | -0.16479 | 121.2708 | -0.19226 | -0.28381 | -0.21973 | 6.7978 | -0.3891 | 121.2158 | 121.3211 | -0.14191 | -0.17395 | 0.10986 | 0.018311 | -0.09613 | 0.036621 | 0.13733 | 0.11902 | -0.10071 | 0.16022 | 0.12817 | -0.15106 | 0.082397 | -0.086975 | -0.21515 | -0.045776 | 121.5729 | 121.5683 | 6.6605 | -121.6507 | 121.5179 | 121.6232 | 7.0999 | -121.5408
1170.9531 | 121.701 | -0.2655 | 121.3577 | -0.0049592 | 0.0033731 | 0.067964 | 0.0029566 | 0.065834 | -0.0050585 | 0.0017475 | -0.013123 | -0.0049111 | 0.065903 | 0.066328 | -0.20425 | -0.0032662 | 121.3669 | -0.068665 | 6.5689 | -0.086975 | 121.225 | -0.16022 | -0.21515 | -0.11444 | 7.0175 | -0.20142 | 121.1746 | 121.3165 | -0.11902 | -0.14648 | 0.10529 | 0.050354 | -0.13275 | 0.19684 | 0.17853 | 0.12817 | 0.009155 | 0.14648 | 0.11902 | -0.1831 | 0.15106 | 0.064087 | -0.054932 | -0.041199 | 121.4905 | 121.6324 | 6.8344 | -121.5729 | 121.4401 | 121.582 | 7.283 | -121.5042
1172.7188 | 121.7285 | -0.25177 | 121.3257 | -0.012589 | 0.0059365 | 0.065187 | 0.0046656 | 0.065834 | 0.0030591 | 0.0028155 | 0.0097658 | -0.0025613 | 0.06633 | 0.069105 | -0.19998 | -0.006257 | 121.3303 | -0.16479 | 6.4865 | -0.10986 | 121.2387 | -0.17853 | -0.23346 | -0.11902 | 6.9717 | -0.24719 | 121.17 | 121.3028 | -0.1236 | -0.11444 | 0.073242 | 0.018311 | -0.086976 | 0.086975 | 0.14191 | 0.1236 | 0.004577 | 0.12817 | 0.13733 | -0.15564 | 0.13275 | 0.004578 | -0.13275 | -0.022889 | 121.4905 | 121.582 | 6.7383 | -121.5591 | 121.4218 | 121.5546 | 7.2235 | -121.4401
1174.4688 | 121.756 | -0.25635 | 121.3394 | -0.012589 | 0.0012369 | 0.06711 | 0.001034 | 0.065621 | -0.0035633 | 0.00067926 | 0.0021363 | -0.0049111 | 0.062912 | 0.068464 | -0.20083 | -0.0032662 | 121.3394 | -0.11444 | 6.5735 | -0.091553 | 121.2387 | -0.16022 | -0.22888 | -0.12817 | 7.0175 | -0.20599 | 121.1838 | 121.3028 | -0.10986 | -0.15106 | 0.096131 | 0.027466 | -0.10071 | 0.14191 | 0.1648 | 0.13733 | 0 | 0.14649 | 0.10529 | -0.15564 | 0.12817 | 0.050354 | -0.054932 | -0.036622 | 121.4951 | 121.5958 | 6.8298 | -121.5683 | 121.4401 | 121.5591 | 7.2739 | -121.4905
1176.1719 | 121.6415 | -0.29755 | 121.3623 | 0.0026703 | 0.0012369 | 0.065614 | 0.0018884 | 0.067757 | -0.00078613 | 0.0013203 | -0.0054932 | -0.0032021 | 0.065262 | 0.06526 | -0.2019 | -0.0039072 | 121.3531 | -0.091553 | 6.6559 | -0.064087 | 121.2387 | -0.16479 | -0.21057 | -0.12817 | 7.0724 | -0.23346 | 121.1838 | 121.2891 | -0.11444 | -0.16022 | 0.13275 | 0.086975 | -0.1236 | 0.20599 | 0.23346 | 0.14648 | -0.009156 | 0.1831 | 0.13733 | -0.17853 | 0.16937 | 0.064087 | -0.073242 | -0.073243 | 121.5363 | 121.6507 | 6.9534 | -121.5729 | 121.4813 | 121.5866 | 7.37 | -121.5225
1177.9375 | 121.6461 | -0.28839 | 121.3531 | -0.0049592 | 0.0050821 | 0.063905 | -0.00088858 | 0.066689 | 0.0030591 | 0.0015339 | -0.0054932 | 2.078e-06 | 0.062698 | 0.066542 | -0.19827 | -0.0060434 | 121.3257 | -0.16937 | 6.6147 | -0.12817 | 121.2708 | -0.17853 | -0.26093 | -0.14648 | 7.0541 | -0.3067 | 121.2112 | 121.3486 | -0.14648 | -0.16479 | 0.10986 | 0.027466 | -0.082397 | 0.11902 | 0.16022 | 0.13275 | -0.027465 | 0.14191 | 0.1236 | -0.14191 | 0.14191 | -0.018311 | -0.14191 | -0.004577 | 121.5591 | 121.6141 | 6.9031 | -121.6141 | 121.4996 | 121.637 | 7.3425 | -121.5179
1179.7188 | 121.6461 | -0.28839 | 121.3577 | -0.0049592 | -0.0026083 | 0.06476 | 0.0012476 | 0.068398 | -0.0027087 | 3.8456e-05 | 0.0021363 | -0.0061929 | 0.062057 | 0.066969 | -0.19891 | -0.0015572 | 121.3486 | -0.073242 | 6.7245 | -0.064087 | 121.2296 | -0.15564 | -0.23804 | -0.12817 | 7.1091 | -0.2243 | 121.1838 | 121.3074 | -0.10071 | -0.15106 | 0.13275 | 0.050354 | -0.12817 | 0.21515 | 0.2243 | 0.17395 | -0.009155 | 0.18768 | 0.13733 | -0.17395 | 0.16022 | 0.064087 | -0.073242 | -0.050354 | 121.5179 | 121.637 | 7.0129 | -121.5958 | 121.4722 | 121.5958 | 7.3975 | -121.5088
1181.4062 | 121.6782 | -0.29755 | 121.3486 | -0.0049592 | 0.0055093 | 0.063478 | 0.0035974 | 0.068611 | 0.0056225 | 0.00046566 | -0.0054932 | -0.0025613 | 0.067398 | 0.067396 | -0.20062 | -0.0041208 | 121.3074 | -0.20599 | 6.6513 | -0.14648 | 121.312 | -0.19226 | -0.26093 | -0.1831 | 7.0816 | -0.31128 | 121.2296 | 121.312 | -0.14191 | -0.18768 | 0.10528 | 0.036621 | -0.036621 | 0.091552 | 0.15106 | 0.11444 | -0.041199 | 0.15564 | 0.10986 | -0.11902 | 0.11444 | -0.013733 | -0.1236 | -0.036621 | 121.6095 | 121.6049 | 6.9489 | -121.6095 | 121.5271 | 121.6095 | 7.3791 | -121.5363
1183.1875 | 121.6507 | -0.27466 | 121.3989 | -0.0049592 | 0.0040139 | 0.066042 | 0.0031702 | 0.065834 | -0.0037769 | 0.00046566 | -0.0054932 | -0.0051247 | 0.067184 | 0.066542 | -0.20233 | -0.0021982 | 121.3486 | -0.07782 | 6.8069 | -0.073242 | 121.225 | -0.16022 | -0.22888 | -0.11444 | 7.164 | -0.21057 | 121.1792 | 121.3303 | -0.10529 | -0.13733 | 0.11444 | 0.045776 | -0.17395 | 0.19684 | 0.20142 | 0.15564 | -0.050354 | 0.16937 | 0.13733 | -0.21973 | 0.16022 | 0.064087 | -0.073242 | -0.068665 | 121.4996 | 121.6232 | 7.0816 | -121.6278 | 121.4539 | 121.6049 | 7.4387 | -121.5363
1184.9531 | 121.5912 | -0.28381 | 121.4035 | -0.012589 | 0.0046549 | 0.062837 | -0.0019568 | 0.065193 | 0.0066907 | 0.00067926 | -0.013123 | -0.00042512 | 0.064835 | 0.070387 | -0.19699 | -0.0036936 | 121.3211 | -0.19684 | 6.7062 | -0.13733 | 121.2662 | -0.1831 | -0.25635 | -0.18768 | 7.0496 | -0.34332 | 121.2204 | 121.3394 | -0.13275 | -0.17395 | 0.10071 | 0.027465 | -0.13733 | 0.086975 | 0.14648 | 0.11902 | -0.082397 | 0.15106 | 0.10986 | -0.1831 | 0.09613 | -0.05951 | -0.16937 | -0.064086 | 121.55 | 121.6049 | 6.9901 | -121.6599 | 121.5042 | 121.6232 | 7.3334 | -121.5775
1186.6562 | 121.7377 | -0.2655 | 121.344 | -0.0049592 | 0.0010233 | 0.067323 | -3.4178e-05 | 0.064125 | -0.0056995 | -0.00017514 | -0.0054932 | -0.0072611 | 0.062271 | 0.066542 | -0.20083 | -0.0030526 | 121.2982 | -0.17853 | 6.7291 | -0.11902 | 121.257 | -0.17395 | -0.23346 | -0.17395 | 7.1045 | -0.25177 | 121.1884 | 121.3715 | -0.11444 | -0.14191 | 0.091553 | 0.032044 | -0.086975 | 0.086975 | 0.14648 | 0.11444 | -0.045776 | 0.15106 | 0.1236 | -0.15564 | 0.091553 | 0.013733 | -0.10986 | 0.027466 | 121.5225 | 121.5637 | 6.9946 | -121.5775 | 121.4539 | 121.637 | 7.37 | -121.4859
1188.4219 | 121.7468 | -0.25635 | 121.3577 | -0.0049592 | -0.0015403 | 0.065187 | 0.0027428 | 0.06498 | -0.0027087 | 0.0011067 | -0.013123 | -0.0051247 | 0.061417 | 0.064833 | -0.19998 | -0.0024118 | 121.312 | -0.16937 | 6.7657 | -0.1236 | 121.2662 | -0.16937 | -0.23346 | -0.17853 | 7.1136 | -0.25177 | 121.1884 | 121.3303 | -0.11902 | -0.16022 | 0.086975 | 0.022889 | -0.091553 | 0.086975 | 0.13275 | 0.10986 | -0.045776 | 0.13733 | 0.096131 | -0.16937 | 0.07782 | 0.004578 | -0.091553 | -0.027466 | 121.5225 | 121.5683 | 7.0221 | -121.5912 | 121.4447 | 121.5866 | 7.37 | -121.5179
1190.125 | 121.6827 | -0.2655 | 121.3806 | -0.0049592 | 0.0023049 | 0.067323 | 0.0027428 | 0.066048 | -0.0014269 | -0.0031659 | -0.0054932 | -0.0055521 | 0.067612 | 0.065901 | -0.20254 | -0.0041208 | 121.376 | -0.068665 | 6.9168 | -0.073242 | 121.2204 | -0.14648 | -0.23346 | -0.10529 | 7.2418 | -0.20599 | 121.1838 | 121.2982 | -0.1236 | -0.14191 | 0.11902 | 0.032044 | -0.16022 | 0.19684 | 0.19226 | 0.16022 | -0.004577 | 0.14191 | 0.1236 | -0.19684 | 0.16022 | 0.059509 | -0.064087 | -0.082397 | 121.4859 | 121.6415 | 7.1823 | -121.6141 | 121.4493 | 121.5637 | 7.5073 | -121.5225
1191.8906 | 121.6187 | -0.29297 | 121.3852 | -0.0049592 | 0.0044411 | 0.065187 | -0.0011024 | 0.068184 | 0.0058363 | 0.00046566 | -0.013123 | 0.0012839 | 0.063766 | 0.071455 | -0.19677 | -0.0049752 | 121.3577 | -0.16937 | 6.8619 | -0.1236 | 121.2891 | -0.16937 | -0.23804 | -0.14648 | 7.1411 | -0.32044 | 121.2341 | 121.3074 | -0.13275 | -0.16479 | 0.1236 | 0.054932 | -0.096131 | 0.1236 | 0.16937 | 0.11444 | -0.027466 | 0.16022 | 0.12817 | -0.15106 | 0.14648 | -0.027466 | -0.15564 | -0.07782 | 121.582 | 121.6507 | 7.1548 | -121.6232 | 121.5271 | 121.6003 | 7.4341 | -121.55
1193.6562 | 121.6278 | -0.27924 | 121.3531 | -0.0049592 | 0.0055093 | 0.067964 | 0.001034 | 0.064766 | -0.0018543 | 0.00046566 | -0.013123 | -0.0053385 | 0.065262 | 0.06526 | -0.20297 | -0.0021982 | 121.3486 | -0.10529 | 6.9672 | -0.10071 | 121.2616 | -0.1831 | -0.23346 | -0.15106 | 7.2052 | -0.27008 | 121.2021 | 121.344 | -0.12817 | -0.16022 | 0.096131 | 0.045777 | -0.091552 | 0.17395 | 0.17853 | 0.13275 | -0.004577 | 0.15106 | 0.11902 | -0.15106 | 0.12817 | 0.009155 | -0.10986 | -0.009155 | 121.5408 | 121.6278 | 7.2464 | -121.5866 | 121.4813 | 121.6232 | 7.4844 | -121.5134
1195.3594 | 121.6461 | -0.27466 | 121.3669 | 0.0026703 | 0.0072183 | 0.065187 | 0.0016748 | 0.069039 | 0.0028455 | 0.0019611 | -0.0054932 | 0.00042948 | 0.065903 | 0.067396 | -0.2019 | -0.0047616 | 121.3486 | -0.16022 | 6.9534 | -0.11444 | 121.2799 | -0.16479 | -0.24261 | -0.15564 | 7.2601 | -0.28839 | 121.2158 | 121.3486 | -0.14191 | -0.16479 | 0.10986 | 0.032043 | -0.086975 | 0.11444 | 0.16022 | 0.12817 | -0.01831 | 0.13275 | 0.10986 | -0.15106 | 0.11902 | -0.013733 | -0.1236 | -0.01831 | 121.5546 | 121.6232 | 7.2281 | -121.6095 | 121.4905 | 121.6232 | 7.5348 | -121.5317
1197.125 | 121.7194 | -0.24719 | 121.3348 | -0.0049592 | 0.00080973 | 0.064546 | -3.4178e-05 | 0.065407 | -0.0014269 | 0.00067926 | -0.020752 | -0.0064065 | 0.064835 | 0.067396 | -0.1987 | -0.0039072 | 121.3623 | -0.07782 | 6.9855 | -0.086975 | 121.2433 | -0.13733 | -0.19684 | -0.086975 | 7.2739 | -0.21057 | 121.1884 | 121.2845 | -0.10529 | -0.13733 | 0.10986 | 0.050354 | -0.091553 | 0.16937 | 0.16022 | 0.10986 | 0.027466 | 0.14191 | 0.10986 | -0.14648 | 0.16022 | 0.036621 | -0.073242 | -0.050354 | 121.4905 | 121.6095 | 7.2327 | -121.5317 | 121.4355 | 121.5317 | 7.5211 | -121.4722
1198.8438 | 121.7285 | -0.23346 | 121.3394 | -0.0049592 | 0.0033731 | 0.067537 | 0.0046656 | 0.067116 | -0.0059131 | -0.00038874 | 0.0021363 | -0.0057657 | 0.065262 | 0.067823 | -0.20404 | -0.002839 | 121.3669 | -0.068665 | 7.0633 | -0.07782 | 121.2662 | -0.14648 | -0.21515 | -0.09613 | 7.338 | -0.17395 | 121.1884 | 121.3074 | -0.11444 | -0.13275 | 0.086975 | 0.01831 | -0.073243 | 0.16479 | 0.15564 | 0.13733 | 0.027465 | 0.11902 | 0.10071 | -0.15106 | 0.13733 | 0.059509 | -0.041199 | -0.032044 | 121.4996 | 121.6003 | 7.2968 | -121.5546 | 121.4218 | 121.5408 | 7.5714 | -121.4722
1200.5625 | 121.7239 | -0.2243 | 121.3348 | -0.0049592 | 0.00059593 | 0.066042 | -0.0015296 | 0.067543 | -0.00099973 | 0.0013203 | 0.0021363 | -0.0042703 | 0.063126 | 0.066328 | -0.19934 | -0.0054026 | 121.3852 | -0.086975 | 7.0496 | -0.068665 | 121.2479 | -0.14191 | -0.21515 | -0.07782 | 7.2968 | -0.21973 | 121.1838 | 121.3074 | -0.10071 | -0.11902 | 0.082397 | 0.009155 | -0.086975 | 0.13733 | 0.15564 | 0.14648 | 0.050354 | 0.1236 | 0.10529 | -0.15106 | 0.14648 | 0.004577 | -0.10071 | -0.027466 | 121.4722 | 121.6095 | 7.2739 | -121.55 | 121.4081 | 121.5317 | 7.5211 | -121.4539
1202.3281 | 121.7239 | -0.25177 | 121.376 | -0.0049592 | 0.0033731 | 0.064974 | 0.0012476 | 0.064125 | -0.0029223 | -0.0010297 | -0.013123 | -0.0051247 | 0.064621 | 0.066114 | -0.20105 | -0.002839 | 121.312 | -0.12817 | 7.0312 | -0.11902 | 121.2616 | -0.13733 | -0.20599 | -0.16022 | 7.2922 | -0.24719 | 121.1884 | 121.2891 | -0.10529 | -0.14648 | 0.11444 | 0.045776 | -0.11444 | 0.1236 | 0.13275 | 0.086975 | -0.064087 | 0.14648 | 0.10529 | -0.18768 | 0.091553 | 0.004578 | -0.10071 | -0.086976 | 121.5134 | 121.5637 | 7.283 | -121.582 | 121.4401 | 121.5408 | 7.5439 | -121.5225
1204.0938 | 121.6919 | -0.23804 | 121.3623 | 0.017929 | 0.00016873 | 0.064546 | -0.0015296 | 0.066048 | 0.0024183 | 0.00067926 | 0.0021363 | -0.0040567 | 0.062271 | 0.066542 | -0.19934 | -0.0021982 | 121.376 | -0.086975 | 7.0953 | -0.073242 | 121.2387 | -0.13275 | -0.20142 | -0.10071 | 7.3334 | -0.20142 | 121.1792 | 121.2753 | -0.10071 | -0.12817 | 0.10529 | 0.036621 | -0.1236 | 0.15106 | 0.16479 | 0.12817 | 0.013733 | 0.13733 | 0.10986 | -0.18311 | 0.13733 | 0.036621 | -0.073242 | -0.086975 | 121.4767 | 121.6141 | 7.3334 | -121.5637 | 121.4172 | 121.5134 | 7.5714 | -121.4905
1205.7969 | 121.6049 | -0.27924 | 121.3852 | 0.0026703 | 0.0063639 | 0.063905 | 0.0014612 | 0.064553 | 0.0056225 | 0.0021747 | 0.0021363 | 0.00085668 | 0.064835 | 0.068891 | -0.19699 | -0.0051888 | 121.3303 | -0.17853 | 7.1136 | -0.13275 | 121.2845 | -0.15564 | -0.24719 | -0.15564 | 7.3242 | -0.32501 | 121.2753 | 121.3577 | -0.13275 | -0.15564 | 0.1236 | 0.032044 | -0.10071 | 0.10071 | 0.14648 | 0.11444 | -0.054932 | 0.14648 | 0.1236 | -0.10986 | 0.1236 | -0.045776 | -0.16937 | -0.027466 | 121.5637 | 121.6095 | 7.3929 | -121.6324 | 121.5546 | 121.637 | 7.6035 | -121.5408
1207.5469 | 121.669 | -0.27008 | 121.3989 | -0.012589 | 0.0091409 | 0.06711 | 0.0050928 | 0.063271 | 0.0011365 | 0.00046566 | -0.0054932 | -0.0040567 | 0.068253 | 0.06825 | -0.2019 | -0.0032662 | 121.2891 | -0.19684 | 7.1503 | -0.1236 | 121.2982 | -0.16937 | -0.24261 | -0.17853 | 7.3425 | -0.32501 | 121.2616 | 121.344 | -0.12817 | -0.16937 | 0.10071 | 0.027466 | -0.10071 | 0.073243 | 0.14649 | 0.11902 | -0.10986 | 0.14191 | 0.10071 | -0.13733 | 0.091553 | -0.054931 | -0.15564 | -0.054932 | 121.5683 | 121.5591 | 7.4204 | -121.6415 | 121.5317 | 121.6141 | 7.6126 | -121.5683
1209.3281 | 121.7789 | -0.2243 | 121.3486 | -0.0049592 | 0.0029459 | 0.069887 | 0.0033838 | 0.064125 | -0.0042041 | 0.00067926 | -0.0054932 | -0.0055521 | 0.064835 | 0.065687 | -0.20404 | -0.0013436 | 121.3165 | -0.12817 | 7.1777 | -0.10071 | 121.2616 | -0.12817 | -0.22888 | -0.1236 | 7.402 | -0.19684 | 121.1792 | 121.3257 | -0.091553 | -0.1236 | 0.09613 | -0.004578 | -0.086975 | 0.09613 | 0.1236 | 0.12817 | -0.032044 | 0.13275 | 0.10071 | -0.16937 | 0.10071 | 0.027466 | -0.073242 | -0.022888 | 121.4859 | 121.5408 | 7.402 | -121.5775 | 121.4035 | 121.55 | 7.6263 | -121.4722
1211.0312 | 121.6782 | -0.24719 | 121.3715 | -0.0049592 | -0.0011131 | 0.064546 | -0.001316 | 0.066262 | -0.0016405 | 0.0019611 | -0.0054932 | -0.0046975 | 0.06398 | 0.064833 | -0.20233 | -0.0019846 | 121.3486 | -0.10071 | 7.2144 | -0.11902 | 121.2387 | -0.13275 | -0.21057 | -0.13275 | 7.3792 | -0.23346 | 121.2067 | 121.3348 | -0.10986 | -0.14191 | 0.11444 | 0.036621 | -0.13275 | 0.14648 | 0.12817 | 0.091552 | -0.022888 | 0.13733 | 0.10528 | -0.16479 | 0.11444 | 0.013733 | -0.091552 | -0.036621 | 121.4859 | 121.5958 | 7.4615 | -121.582 | 121.4539 | 121.582 | 7.6263 | -121.5134
1212.7969 | 121.7285 | -0.2243 | 121.344 | 0.0026703 | 0.0016641 | 0.066896 | 0.0031702 | 0.063912 | -0.0033495 | -0.0023113 | -0.013123 | -0.0057657 | 0.063339 | 0.065901 | -0.20126 | -0.0047616 | 121.3806 | -0.036621 | 7.3425 | -0.059509 | 121.2616 | -0.1236 | -0.18768 | -0.064087 | 7.5531 | -0.17853 | 121.2067 | 121.2982 | -0.09613 | -0.13275 | 0.10071 | 0.036621 | -0.082397 | 0.18768 | 0.16479 | 0.12817 | 0.036621 | 0.12817 | 0.091553 | -0.13733 | 0.16022 | 0.045776 | -0.045777 | -0.045776 | 121.4859 | 121.6049 | 7.5668 | -121.5317 | 121.431 | 121.5225 | 7.7774 | -121.4767
1214.5 | 121.7422 | -0.21973 | 121.3623 | -0.0049592 | 0.0018777 | 0.06476 | -0.0011024 | 0.06733 | 0.0019909 | -0.00060234 | -0.0054932 | -0.0019205 | 0.063553 | 0.069319 | -0.19891 | -0.0047616 | 121.3394 | -0.16937 | 7.2327 | -0.12817 | 121.3028 | -0.15564 | -0.24261 | -0.11444 | 7.457 | -0.25177 | 121.2021 | 121.3211 | -0.11902 | -0.12817 | 0.064087 | -0.022888 | -0.05951 | 0.050354 | 0.091553 | 0.11444 | -0.022888 | 0.10071 | 0.091553 | -0.16022 | 0.10529 | -0.032043 | -0.1236 | -0.041199 | 121.5225 | 121.5591 | 7.4524 | -121.6049 | 121.4218 | 121.5408 | 7.6767 | -121.4905
1216.2656 | 121.6736 | -0.27924 | 121.3669 | 0.0026703 | 0.0040139 | 0.068605 | 0.00017942 | 0.066902 | -0.0027087 | 0.0030293 | -0.0054932 | -0.0038431 | 0.06398 | 0.065046 | -0.19977 | -0.0047616 | 121.3852 | -0.068665 | 7.4295 | -0.068665 | 121.2479 | -0.14648 | -0.23346 | -0.09613 | 7.5851 | -0.19684 | 121.1975 | 121.3348 | -0.091553 | -0.14191 | 0.13275 | 0.045777 | -0.11902 | 0.21057 | 0.21057 | 0.16479 | 0.018311 | 0.18768 | 0.13733 | -0.16937 | 0.18311 | 0.082398 | -0.054931 | -0.032043 | 121.5271 | 121.6644 | 7.7087 | -121.6003 | 121.4767 | 121.6141 | 7.8644 | -121.5088
1217.9688 | 121.7056 | -0.26093 | 121.3623 | 0.0026703 | -0.0017539 | 0.066683 | 0.00039302 | 0.066475 | -0.0020679 | 0.00025206 | -0.013123 | -0.0049111 | 0.066757 | 0.068037 | -0.20318 | -0.0039072 | 121.3303 | -0.10529 | 7.3517 | -0.09613 | 121.2753 | -0.14191 | -0.20599 | -0.15106 | 7.4615 | -0.24719 | 121.2067 | 121.3257 | -0.086975 | -0.15564 | 0.11902 | 0.054931 | -0.086975 | 0.15564 | 0.1648 | 0.10986 | -0.032044 | 0.17395 | 0.10529 | -0.15564 | 0.10986 | 0.013733 | -0.091552 | -0.036621 | 121.5363 | 121.5912 | 7.6126 | -121.5683 | 121.4676 | 121.5866 | 7.7225 | -121.5179
1219.7344 | 121.7056 | -0.2655 | 121.3623 | 0.0026703 | -0.00068567 | 0.065187 | 0.002102 | 0.065621 | 6.8274e-05 | 0.0019611 | 0.0021363 | -0.0032021 | 0.060989 | 0.066328 | -0.20062 | -0.0032662 | 121.376 | -0.091553 | 7.4249 | -0.086975 | 121.257 | -0.13733 | -0.21057 | -0.11902 | 7.5211 | -0.23804 | 121.2112 | 121.344 | -0.10071 | -0.14648 | 0.12817 | 0.054932 | -0.10529 | 0.17395 | 0.17853 | 0.1236 | 0.013733 | 0.16479 | 0.11902 | -0.15106 | 0.14648 | 0.027466 | -0.091553 | -0.018311 | 121.5225 | 121.6415 | 7.6904 | -121.5729 | 121.4767 | 121.6095 | 7.7866 | -121.5088
1221.4844 | 121.701 | -0.25635 | 121.3394 | -0.0049592 | 0.0010233 | 0.065401 | -0.00024778 | 0.066902 | -0.0016405 | 0.00067926 | -0.0054932 | -0.0046975 | 0.063339 | 0.065687 | -0.20019 | -0.0030526 | 121.3715 | -0.082397 | 7.4478 | -0.086975 | 121.2479 | -0.14191 | -0.21973 | -0.10986 | 7.5348 | -0.21515 | 121.1975 | 121.3165 | -0.13733 | -0.13275 | 0.11444 | 0.036621 | -0.091553 | 0.17395 | 0.16937 | 0.13275 | 0.032043 | 0.11902 | 0.1236 | -0.14191 | 0.14649 | 0.041199 | -0.082398 | -0.022889 | 121.5042 | 121.6278 | 7.7042 | -121.5591 | 121.4539 | 121.5729 | 7.7911 | -121.4722
1223.1875 | 121.6827 | -0.24719 | 121.3623 | 0.0026703 | 0.0042275 | 0.065187 | -0.0017432 | 0.068184 | 0.0036999 | 3.8456e-05 | 0.0021363 | -0.0012795 | 0.06398 | 0.069319 | -0.19848 | -0.0036936 | 121.2936 | -0.21515 | 7.3746 | -0.14648 | 121.3165 | -0.17395 | -0.25177 | -0.17853 | 7.5027 | -0.34332 | 121.2524 | 121.3348 | -0.14648 | -0.16022 | 0.073242 | -0.004578 | -0.045777 | 0.032043 | 0.10071 | 0.10529 | -0.068665 | 0.10071 | 0.086975 | -0.10986 | 0.068664 | -0.096131 | -0.18311 | -0.027466 | 121.5637 | 121.5408 | 7.6218 | -121.6141 | 121.4996 | 121.582 | 7.7499 | -121.5225
1224.9688 | 121.6736 | -0.25177 | 121.3531 | -0.0049592 | -0.00089927 | 0.068391 | -0.0015296 | 0.066689 | -0.0039905 | 0.0019611 | -0.0054932 | -0.0044839 | 0.061844 | 0.065687 | -0.20254 | -0.0019846 | 121.3394 | -0.10529 | 7.4936 | -0.10529 | 121.257 | -0.14648 | -0.20599 | -0.15564 | 7.5485 | -0.25177 | 121.1792 | 121.3165 | -0.11444 | -0.12817 | 0.10529 | 0.045776 | -0.09613 | 0.14648 | 0.14648 | 0.10071 | -0.013732 | 0.13733 | 0.1236 | -0.17395 | 0.09613 | 0 | -0.1236 | -0.036621 | 121.5088 | 121.5912 | 7.7454 | -121.5591 | 121.431 | 121.5683 | 7.8003 | -121.4813
1226.7188 | 121.7606 | -0.24719 | 121.3303 | -0.0049592 | 0.0029459 | 0.068605 | 0.0023156 | 0.066689 | -0.0052721 | -0.0018841 | -0.0054932 | -0.0044839 | 0.064194 | 0.068464 | -0.20126 | -0.0030526 | 121.3852 | -0.054932 | 7.5989 | -0.054932 | 121.2662 | -0.13275 | -0.20142 | -0.086975 | 7.6584 | -0.16022 | 121.1792 | 121.3074 | -0.09613 | -0.12817 | 0.11444 | 0.045776 | -0.064087 | 0.19226 | 0.19226 | 0.14648 | 0.054932 | 0.15106 | 0.11902 | -0.15106 | 0.16022 | 0.086975 | -0.032043 | -0.022888 | 121.5134 | 121.6324 | 7.8461 | -121.5317 | 121.4264 | 121.5546 | 7.9056 | -121.4584
1228.4688 | 121.701 | -0.24719 | 121.3623 | -0.012589 | 0.0033731 | 0.064974 | 0.0035974 | 0.066048 | -0.00078613 | -0.0010297 | -0.0054932 | -0.0057657 | 0.06398 | 0.066114 | -0.20254 | -0.0030526 | 121.3943 | -0.050354 | 7.6767 | -0.082397 | 121.2936 | -0.13275 | -0.21057 | -0.082397 | 7.7271 | -0.18768 | 121.1929 | 121.3348 | -0.10529 | -0.12817 | 0.11444 | 0.036621 | -0.068665 | 0.19684 | 0.16479 | 0.12817 | 0.032043 | 0.14191 | 0.11902 | -0.16937 | 0.16479 | 0.059509 | -0.059509 | -0.027466 | 121.5408 | 121.6415 | 7.9239 | -121.5729 | 121.4401 | 121.582 | 7.9742 | -121.4905
1230.25 | 121.6965 | -0.2243 | 121.3394 | -0.0049592 | 0.0016641 | 0.062624 | -0.00088858 | 0.065407 | 0.00049567 | 0.00025206 | -0.013123 | -0.0012795 | 0.065048 | 0.06825 | -0.20019 | -0.0024118 | 121.4172 | -0.086975 | 7.6309 | -0.068665 | 121.2479 | -0.14191 | -0.20142 | -0.064087 | 7.6721 | -0.21057 | 121.225 | 121.3348 | -0.11444 | -0.1236 | 0.082397 | 0.022888 | -0.091553 | 0.13733 | 0.15564 | 0.13275 | 0.077819 | 0.10986 | 0.10071 | -0.11444 | 0.16022 | 0.013733 | -0.086975 | -0.004578 | 121.4722 | 121.6415 | 7.8552 | -121.5408 | 121.4493 | 121.5591 | 7.8964 | -121.463
1232 | 121.6049 | -0.28839 | 121.3898 | -0.0049592 | 0.0059365 | 0.065187 | -0.002384 | 0.066262 | 0.0054089 | 0.0034565 | -0.0054932 | -0.00085232 | 0.064194 | 0.069105 | -0.19742 | -0.0054026 | 121.3486 | -0.16937 | 7.6401 | -0.12817 | 121.2936 | -0.16479 | -0.24261 | -0.14191 | 7.6355 | -0.32959 | 121.2387 | 121.3943 | -0.11444 | -0.16479 | 0.1236 | 0.045776 | -0.096131 | 0.11902 | 0.16022 | 0.11444 | -0.041199 | 0.17395 | 0.1236 | -0.15106 | 0.14648 | -0.041199 | -0.16479 | 0.004577 | 121.582 | 121.637 | 7.9285 | -121.6324 | 121.5271 | 121.6827 | 7.9239 | -121.5546
1233.7031 | 121.7743 | -0.24261 | 121.3303 | 0.0103 | -4.4874e-05 | 0.067751 | -3.4178e-05 | 0.067971 | -0.0046313 | 0.0019611 | -0.0054932 | -0.0038431 | 0.063766 | 0.064405 | -0.20147 | -0.00113 | 121.3577 | -0.10529 | 7.7133 | -0.091553 | 121.2753 | -0.15106 | -0.21515 | -0.10529 | 7.7087 | -0.18768 | 121.1975 | 121.3348 | -0.10071 | -0.11444 | 0.091553 | 0.027466 | -0.054931 | 0.13733 | 0.15106 | 0.1236 | 0.027466 | 0.14191 | 0.12817 | -0.13275 | 0.13733 | 0.054932 | -0.073242 | 0.004578 | 121.5179 | 121.6003 | 7.9559 | -121.5454 | 121.4401 | 121.5775 | 7.9514 | -121.4447
1235.4688 | 121.7606 | -0.22888 | 121.3531 | 0.0026703 | 0.0014505 | 0.066896 | 0.0031702 | 0.065834 | -0.0046313 | -0.0027387 | -0.0054932 | -0.0076883 | 0.064835 | 0.064192 | -0.20318 | -0.0041208 | 121.3806 | -0.082397 | 7.7499 | -0.073242 | 121.2662 | -0.14648 | -0.20599 | -0.09613 | 7.7454 | -0.18768 | 121.1884 | 121.3531 | -0.10071 | -0.13733 | 0.082398 | 0.022888 | -0.086975 | 0.14649 | 0.15564 | 0.13275 | 0.027466 | 0.12817 | 0.091553 | -0.16479 | 0.13275 | 0.041199 | -0.050354 | 0 | 121.4951 | 121.6095 | 7.9788 | -121.5591 | 121.4172 | 121.582 | 7.9742 | -121.4905
1237.1719 | 121.6095 | -0.27008 | 121.4172 | 0.0026703 | 0.0027323 | 0.066255 | 0.0014612 | 0.068825 | -0.00078613 | 0.00025206 | -0.013123 | -0.0049111 | 0.062912 | 0.065046 | -0.19977 | -0.0043344 | 121.376 | -0.10529 | 7.8049 | -0.091553 | 121.2708 | -0.16022 | -0.22888 | -0.15564 | 7.7316 | -0.28381 | 121.2204 | 121.3715 | -0.12817 | -0.16022 | 0.10986 | 0.041199 | -0.14648 | 0.1648 | 0.17853 | 0.13733 | -0.041198 | 0.14191 | 0.10986 | -0.19684 | 0.11444 | -0.013732 | -0.1236 | -0.045776 | 121.5408 | 121.6461 | 8.075 | -121.6461 | 121.4905 | 121.6415 | 8.0017 | -121.5775
1238.9375 | 121.701 | -0.24261 | 121.3623 | -0.0049592 | 0.0038003 | 0.065401 | -0.0021704 | 0.065407 | -0.00035893 | -0.0016705 | -0.0054932 | -0.0034159 | 0.062698 | 0.067396 | -0.20147 | -0.0032662 | 121.3989 | -0.073242 | 7.814 | -0.073242 | 121.2662 | -0.13275 | -0.21973 | -0.068665 | 7.7683 | -0.21057 | 121.2021 | 121.3211 | -0.09613 | -0.12817 | 0.10986 | 0.022888 | -0.096131 | 0.16937 | 0.16937 | 0.14649 | 0.036621 | 0.14649 | 0.11444 | -0.16022 | 0.17395 | 0.032044 | -0.082397 | -0.041199 | 121.5088 | 121.6415 | 8.0566 | -121.582 | 121.4447 | 121.5637 | 8.0109 | -121.4905
1240.7188 | 121.5958 | -0.28839 | 121.3943 | -0.0049592 | 0.0042275 | 0.063692 | 0.00039302 | 0.065407 | 0.0049817 | 0.0015339 | -0.0054932 | -0.00085232 | 0.063339 | 0.069105 | -0.19677 | -0.0058298 | 121.3898 | -0.14648 | 7.8278 | -0.11902 | 121.312 | -0.1831 | -0.23346 | -0.14648 | 7.7499 | -0.32501 | 121.2616 | 121.3531 | -0.12817 | -0.16479 | 0.10529 | 0.054932 | -0.082397 | 0.14191 | 0.16937 | 0.11444 | -0.004577 | 0.16022 | 0.1236 | -0.13275 | 0.14191 | -0.036621 | -0.16022 | -0.041199 | 121.6003 | 121.6782 | 8.1162 | -121.6278 | 121.55 | 121.6415 | 8.0383 | -121.5591
1242.4375 | 121.7239 | -0.25177 | 121.3531 | -0.0049592 | 0.0020913 | 0.063265 | 0.0033838 | 0.064125 | -0.0039905 | -0.00081594 | -0.0054932 | -0.0079019 | 0.066116 | 0.066542 | -0.20147 | -0.0024118 | 121.3348 | -0.12817 | 7.8415 | -0.10986 | 121.2936 | -0.12817 | -0.21973 | -0.15106 | 7.7545 | -0.26093 | 121.2112 | 121.3486 | -0.091553 | -0.14191 | 0.1236 | 0.032043 | -0.059509 | 0.1236 | 0.14191 | 0.10986 | -0.01831 | 0.16022 | 0.10986 | -0.14191 | 0.10071 | -0.009155 | -0.11902 | -0.004577 | 121.5454 | 121.5866 | 8.0933 | -121.5729 | 121.463 | 121.6003 | 8.0063 | -121.4951
1244.2031 | 121.6507 | -0.27008 | 121.3943 | -0.020218 | 0.0040139 | 0.065401 | 0.00039302 | 0.065621 | 0.0032727 | 0.00067926 | 0.0021363 | 0.00064308 | 0.06398 | 0.06825 | -0.19998 | -0.0039072 | 121.3531 | -0.15106 | 7.9056 | -0.10986 | 121.2982 | -0.16937 | -0.24261 | -0.11444 | 7.8598 | -0.27924 | 121.2433 | 121.3943 | -0.11444 | -0.15564 | 0.10071 | 0.027466 | -0.09613 | 0.11902 | 0.16022 | 0.13275 | -0.041199 | 0.15564 | 0.11444 | -0.15106 | 0.15564 | -0.009155 | -0.1236 | 0 | 121.5683 | 121.6232 | 8.1757 | -121.637 | 121.5134 | 121.6644 | 8.1299 | -121.55
1245.9688 | 121.5912 | -0.25635 | 121.4081 | 0.0026703 | 0.0044411 | 0.06241 | -0.002384 | 0.068611 | 0.0043409 | 0.0017475 | -0.013123 | 0.00042948 | 0.063126 | 0.066328 | -0.19742 | -0.0043344 | 121.3531 | -0.16022 | 7.901 | -0.13733 | 121.3165 | -0.1831 | -0.24261 | -0.14191 | 7.8369 | -0.33417 | 121.225 | 121.376 | -0.1236 | -0.16937 | 0.073243 | 0.013733 | -0.091553 | 0.096131 | 0.11902 | 0.10529 | -0.054932 | 0.13275 | 0.086975 | -0.1831 | 0.11444 | -0.077819 | -0.16479 | -0.032043 | 121.5729 | 121.6095 | 8.1573 | -121.6507 | 121.4813 | 121.6324 | 8.0933 | -121.5775
1247.7188 | 121.6232 | -0.2655 | 121.4035 | -0.0049592 | 0.0050821 | 0.065614 | -0.0015296 | 0.066048 | 0.0045545 | 0.0017475 | 0.0021363 | -0.0023477 | 0.064835 | 0.068678 | -0.1987 | -0.00048921 | 121.3669 | -0.13733 | 7.988 | -0.10986 | 121.3028 | -0.15564 | -0.2243 | -0.11902 | 7.8964 | -0.27466 | 121.225 | 121.3989 | -0.11444 | -0.15564 | 0.10986 | 0.041199 | -0.10071 | 0.12817 | 0.15564 | 0.11444 | -0.036621 | 0.15106 | 0.10986 | -0.17853 | 0.14648 | -0.009155 | -0.11902 | -0.004577 | 121.5683 | 121.6324 | 8.2535 | -121.6278 | 121.4905 | 121.6644 | 8.1619 | -121.5591
1249.4219 | 121.7697 | -0.22888 | 121.3531 | 0.0103 | 0.0031595 | 0.067751 | 0.003811 | 0.065193 | -0.0061267 | -0.00060234 | -0.013123 | -0.0051247 | 0.066116 | 0.066542 | -0.20468 | -0.00070281 | 121.3257 | -0.1236 | 8.0063 | -0.086975 | 121.2616 | -0.14191 | -0.21515 | -0.1236 | 7.9056 | -0.20599 | 121.2021 | 121.3806 | -0.10529 | -0.15106 | 0.086975 | 0.013733 | -0.091552 | 0.10529 | 0.14191 | 0.12817 | -0.027465 | 0.1236 | 0.07782 | -0.15106 | 0.10529 | 0.022888 | -0.054932 | 0.027466 | 121.4905 | 121.5546 | 8.2352 | -121.5683 | 121.431 | 121.6095 | 8.1345 | -121.5042
1251.2031 | 121.6736 | -0.2655 | 121.4081 | 0.0026703 | 0.0059365 | 0.065614 | 0.0014612 | 0.067971 | 6.8274e-05 | 0.00089286 | 0.0021363 | -0.00021152 | 0.067184 | 0.068678 | -0.20233 | -0.0030526 | 121.3074 | -0.21515 | 8.0246 | -0.1236 | 121.3211 | -0.17853 | -0.23804 | -0.1831 | 7.8735 | -0.32501 | 121.257 | 121.4081 | -0.13733 | -0.16022 | 0.086975 | 0.027466 | -0.086975 | 0.050354 | 0.14191 | 0.11444 | -0.10071 | 0.12817 | 0.10529 | -0.15106 | 0.082398 | -0.059509 | -0.1648 | 0 | 121.5866 | 121.5729 | 8.2901 | -121.6461 | 121.5225 | 121.6736 | 8.139 | -121.5683
1252.9688 | 121.7285 | -0.23346 | 121.3806 | 0.0026703 | 0.0057229 | 0.063692 | 0.00082022 | 0.06498 | 0.00028207 | 0.00067926 | -0.0054932 | -0.0017069 | 0.066971 | 0.06761 | -0.20083 | -0.0015572 | 121.2936 | -0.21973 | 7.9788 | -0.14191 | 121.312 | -0.1831 | -0.24261 | -0.17853 | 7.8461 | -0.32501 | 121.2524 | 121.3898 | -0.11444 | -0.14648 | 0.050354 | -0.009156 | -0.068664 | 0.013732 | 0.091552 | 0.10071 | -0.086975 | 0.11902 | 0.086975 | -0.12817 | 0.054931 | -0.091553 | -0.17853 | 0.009156 | 121.5454 | 121.5271 | 8.2123 | -121.6232 | 121.4859 | 121.6232 | 8.0795 | -121.5271
1254.75 | 121.5912 | -0.27466 | 121.4172 | -0.0049592 | 0.0035867 | 0.063265 | -0.00067498 | 0.063271 | 0.0041273 | 0.0043109 | 0.0097658 | -0.00063872 | 0.065262 | 0.068678 | -0.19656 | -0.0030526 | 121.3303 | -0.14648 | 8.107 | -0.1236 | 121.2799 | -0.15106 | -0.23346 | -0.17853 | 7.9147 | -0.32959 | 121.2524 | 121.4081 | -0.13733 | -0.16937 | 0.1236 | 0.041199 | -0.13733 | 0.12817 | 0.15106 | 0.10986 | -0.086975 | 0.13733 | 0.10529 | -0.16479 | 0.09613 | -0.054932 | -0.16022 | -0.009155 | 121.5546 | 121.6049 | 8.3817 | -121.6507 | 121.5271 | 121.6827 | 8.1894 | -121.5866
1256.5156 | 121.7194 | -0.25177 | 121.376 | -0.0049592 | -0.0017539 | 0.06711 | -0.00046138 | 0.063698 | -0.0052721 | -0.00081594 | -0.0054932 | -0.0061929 | 0.061417 | 0.066328 | -0.20318 | 0.00057899 | 121.3257 | -0.091553 | 8.139 | -0.091553 | 121.2708 | -0.14191 | -0.21057 | -0.15564 | 7.9468 | -0.23346 | 121.1929 | 121.3669 | -0.086975 | -0.10986 | 0.10986 | 0.041199 | -0.10529 | 0.16022 | 0.16022 | 0.11902 | -0.050354 | 0.16479 | 0.14191 | -0.18311 | 0.09613 | 0.018311 | -0.1236 | -0.009156 | 121.5225 | 121.5775 | 8.3908 | -121.5866 | 121.4447 | 121.6187 | 8.1985 | -121.4859
1258.2188 | 121.6919 | -0.25177 | 121.376 | -0.012589 | 0.0055093 | 0.064546 | -0.00024778 | 0.066048 | 0.0039135 | 0.00046566 | -0.0054932 | -0.00063872 | 0.065903 | 0.068891 | -0.20083 | -0.0030526 | 121.2982 | -0.22888 | 8.107 | -0.13275 | 121.3211 | -0.17395 | -0.25177 | -0.19684 | 7.9056 | -0.32044 | 121.2662 | 121.4035 | -0.13275 | -0.16022 | 0.07782 | 0 | -0.054932 | 0.022888 | 0.11902 | 0.11902 | -0.07782 | 0.11902 | 0.091553 | -0.10986 | 0.054932 | -0.068665 | -0.16022 | 0.027465 | 121.5729 | 121.55 | 8.3588 | -121.6278 | 121.5179 | 121.6553 | 8.1573 | -121.5363
1259.9844 | 121.6644 | -0.25177 | 121.4081 | 0.0026703 | 0.0067911 | 0.065614 | 0.0035974 | 0.065193 | 0.00049567 | 0.0036701 | 0.0021363 | -0.00085232 | 0.064835 | 0.06825 | -0.20297 | -0.00113 | 121.2936 | -0.17853 | 8.226 | -0.1236 | 121.3074 | -0.17395 | -0.22888 | -0.16479 | 8.0109 | -0.28839 | 121.2387 | 121.3715 | -0.12817 | -0.16022 | 0.07782 | 0.022888 | -0.10071 | 0.073242 | 0.12817 | 0.10529 | -0.11444 | 0.1236 | 0.091553 | -0.16937 | 0.086975 | -0.036621 | -0.12817 | -0.036621 | 121.5591 | 121.5454 | 8.4778 | -121.637 | 121.4905 | 121.6232 | 8.2626 | -121.5683
1261.6719 | 121.7056 | -0.23804 | 121.3806 | 0.017929 | -0.00025847 | 0.064333 | -0.00067498 | 0.065834 | -0.0029223 | 0.0011067 | -0.0054932 | -0.0049111 | 0.062698 | 0.067823 | -0.20105 | -0.0015572 | 121.3715 | -0.059509 | 8.2901 | -0.050354 | 121.2433 | -0.14648 | -0.19226 | -0.091553 | 8.0429 | -0.19684 | 121.1792 | 121.3394 | -0.10986 | -0.11902 | 0.091553 | 0.045776 | -0.13733 | 0.17853 | 0.18768 | 0.14191 | -0.009155 | 0.12817 | 0.11902 | -0.20142 | 0.14648 | 0.041199 | -0.077819 | -0.041198 | 121.4813 | 121.6095 | 8.5281 | -121.5729 | 121.4172 | 121.5775 | 8.2809 | -121.4996
1263.4375 | 121.6965 | -0.22888 | 121.3898 | -0.0049592 | 0.0029459 | 0.066255 | -3.4178e-05 | 0.066262 | -0.0037769 | 0.0011067 | -0.013123 | -0.0049111 | 0.062912 | 0.065473 | -0.20019 | -0.002839 | 121.3989 | -0.064087 | 8.3313 | -0.054932 | 121.2479 | -0.1236 | -0.20599 | -0.10529 | 8.0429 | -0.19684 | 121.1929 | 121.3715 | -0.10529 | -0.13275 | 0.10529 | 0.022888 | -0.14191 | 0.16479 | 0.17395 | 0.15106 | 0.009155 | 0.1236 | 0.096131 | -0.19684 | 0.1236 | 0.032044 | -0.064087 | -0.018311 | 121.4767 | 121.6278 | 8.5602 | -121.5958 | 121.4218 | 121.6003 | 8.2718 | -121.5225
1265.2188 | 121.6415 | -0.27008 | 121.4035 | -0.012589 | 0.0072183 | 0.066255 | 0.002102 | 0.065621 | 0.0043409 | -0.0012433 | 0.0097658 | -0.0012795 | 0.06633 | 0.066755 | -0.20083 | -0.0036936 | 121.3715 | -0.13275 | 8.3633 | -0.086975 | 121.3211 | -0.14648 | -0.22888 | -0.11444 | 8.0887 | -0.27008 | 121.2433 | 121.3989 | -0.1236 | -0.13275 | 0.1236 | 0.041199 | -0.082397 | 0.13733 | 0.18311 | 0.14191 | -0.032043 | 0.14649 | 0.13733 | -0.16022 | 0.15564 | 0 | -0.13733 | -0.004577 | 121.5912 | 121.6415 | 8.6334 | -121.6324 | 121.5134 | 121.669 | 8.3588 | -121.5363
1266.9844 | 121.7377 | -0.23804 | 121.3898 | -0.012589 | 0.0031595 | 0.065828 | -0.00024778 | 0.065834 | 0.00070927 | 0.0015339 | -0.0054932 | -0.0027749 | 0.063339 | 0.069105 | -0.19977 | -0.0021982 | 121.3028 | -0.19684 | 8.2855 | -0.14191 | 121.3211 | -0.16479 | -0.25177 | -0.1831 | 8.0246 | -0.32044 | 121.2616 | 121.4172 | -0.1236 | -0.16022 | 0.073242 | -0.013733 | -0.068665 | 0.041199 | 0.09613 | 0.10986 | -0.086976 | 0.11444 | 0.07782 | -0.12817 | 0.054932 | -0.082398 | -0.16022 | 0.027465 | 121.5591 | 121.5408 | 8.5236 | -121.6415 | 121.4996 | 121.6553 | 8.2626 | -121.55
1268.6875 | 121.7514 | -0.24719 | 121.3486 | 0.0103 | 0.0025185 | 0.066683 | 0.00039302 | 0.064553 | -0.0052721 | 0.00025206 | -0.0054932 | -0.0076883 | 0.062485 | 0.066755 | -0.20212 | -0.00113 | 121.4035 | -0.027466 | 8.5007 | -0.041199 | 121.2753 | -0.12817 | -0.20142 | -0.086975 | 8.2031 | -0.17395 | 121.225 | 121.3943 | -0.091553 | -0.12817 | 0.11902 | 0.045776 | -0.073242 | 0.21973 | 0.20599 | 0.16022 | 0.054931 | 0.15564 | 0.11902 | -0.1236 | 0.16022 | 0.073242 | -0.045776 | 0.045776 | 121.5225 | 121.6507 | 8.7479 | -121.55 | 121.4722 | 121.6415 | 8.4503 | -121.4767
1270.4688 | 121.7285 | -0.22888 | 121.3577 | 0.0026703 | 0.00080973 | 0.06476 | -0.00067498 | 0.068184 | -0.00035893 | 0.0019611 | 0.0021363 | -0.0023477 | 0.062698 | 0.068891 | -0.19827 | -0.0036936 | 121.4081 | -0.068665 | 8.4686 | -0.050354 | 121.2662 | -0.14191 | -0.20599 | -0.064087 | 8.1619 | -0.18768 | 121.2067 | 121.3852 | -0.086975 | -0.10986 | 0.086975 | 0.022888 | -0.091553 | 0.16022 | 0.17853 | 0.15564 | 0.050354 | 0.14191 | 0.11902 | -0.15106 | 0.16479 | 0.041199 | -0.07782 | 0.027466 | 121.4951 | 121.637 | 8.6975 | -121.5637 | 121.4355 | 121.6141 | 8.3908 | -121.4676
1272.1719 | 121.7239 | -0.23804 | 121.376 | 0.0026703 | 0.0020913 | 0.064119 | 0.0016748 | 0.063057 | 0.0026319 | -0.00017514 | -0.013123 | -0.0023477 | 0.063553 | 0.069319 | -0.19784 | -0.002839 | 121.3211 | -0.21973 | 8.4 | -0.14648 | 121.3257 | -0.17395 | -0.24261 | -0.17853 | 8.0887 | -0.32044 | 121.2753 | 121.4172 | -0.12817 | -0.15106 | 0.064087 | -0.004578 | -0.050354 | 0.01831 | 0.091553 | 0.096131 | -0.054932 | 0.10986 | 0.086975 | -0.10071 | 0.059509 | -0.082398 | -0.16937 | 0.041198 | 121.5637 | 121.5591 | 8.638 | -121.6187 | 121.5134 | 121.6553 | 8.3267 | -121.5271
1273.9375 | 121.6553 | -0.27466 | 121.3989 | -0.012589 | 0.0035867 | 0.066255 | 0.0048792 | 0.065621 | -0.0016405 | 0.00089286 | -0.013123 | -0.0025613 | 0.066116 | 0.067823 | -0.2019 | -0.0030526 | 121.2936 | -0.17395 | 8.5236 | -0.13275 | 121.2891 | -0.1831 | -0.24261 | -0.20599 | 8.1665 | -0.32501 | 121.2753 | 121.4172 | -0.1236 | -0.16022 | 0.091553 | 0.032043 | -0.10986 | 0.10071 | 0.14191 | 0.10986 | -0.10529 | 0.15106 | 0.11444 | -0.1236 | 0.068664 | -0.050354 | -0.1648 | 0.01831 | 121.5637 | 121.5683 | 8.7982 | -121.6415 | 121.55 | 121.6919 | 8.4412 | -121.5591
1275.7031 | 121.6873 | -0.2243 | 121.344 | 0.0103 | 0.00016873 | 0.065828 | 0.00082022 | 0.066689 | -0.0044177 | -0.00060234 | -0.0054932 | -0.0066201 | 0.063553 | 0.065901 | -0.20169 | -0.0019846 | 121.3623 | -0.086975 | 8.5648 | -0.091553 | 121.2616 | -0.14191 | -0.1831 | -0.13275 | 8.194 | -0.2243 | 121.2021 | 121.3715 | -0.10071 | -0.1236 | 0.082397 | 0.041199 | -0.082397 | 0.13733 | 0.13275 | 0.091552 | 0.018311 | 0.1236 | 0.10071 | -0.14191 | 0.091553 | 0 | -0.10071 | 0.027466 | 121.4859 | 121.5866 | 8.7891 | -121.5271 | 121.4264 | 121.5958 | 8.4183 | -121.4676
1277.4062 | 121.7194 | -0.21057 | 121.3577 | 0.0026703 | 0.0035867 | 0.066469 | -0.00046138 | 0.066048 | -0.0014269 | 0.0019611 | -0.013123 | -0.0046975 | 0.065475 | 0.066755 | -0.19998 | -0.0043344 | 121.3989 | -0.059509 | 8.6243 | -0.036621 | 121.312 | -0.11444 | -0.17853 | -0.059509 | 8.2672 | -0.20142 | 121.2158 | 121.344 | -0.082397 | -0.10529 | 0.09613 | 0.032043 | -0.045776 | 0.15106 | 0.17395 | 0.14191 | 0.041199 | 0.12817 | 0.10529 | -0.14191 | 0.15106 | 0.009155 | -0.09613 | -0.013733 | 121.5225 | 121.6095 | 8.8348 | -121.5363 | 121.4264 | 121.5546 | 8.4778 | -121.463
1279.1719 | 121.6049 | -0.27008 | 121.3989 | 0.0026703 | 0.0042275 | 0.064546 | 0.00082022 | 0.064125 | 0.0041273 | 0.0030293 | -0.013123 | -0.0019205 | 0.065048 | 0.068464 | -0.1972 | -0.0047616 | 121.3257 | -0.17853 | 8.6288 | -0.13733 | 121.3074 | -0.16937 | -0.25177 | -0.16022 | 8.1985 | -0.3479 | 121.2708 | 121.4218 | -0.1236 | -0.16937 | 0.10071 | 0.018311 | -0.091553 | 0.091553 | 0.13275 | 0.11444 | -0.073242 | 0.14649 | 0.10071 | -0.12817 | 0.10986 | -0.077819 | -0.17853 | 0.022888 | 121.5775 | 121.5958 | 8.8989 | -121.6507 | 121.5408 | 121.6919 | 8.4686 | -121.5683
1280.875 | 121.6644 | -0.27466 | 121.3715 | -0.012589 | 0.0061501 | 0.064974 | 0.00039302 | 0.06498 | 0.0026319 | 0.00089286 | 0.0021363 | -0.0025613 | 0.064194 | 0.06761 | -0.19977 | -0.0032662 | 121.2891 | -0.21515 | 8.6105 | -0.13733 | 121.3257 | -0.15564 | -0.23346 | -0.19226 | 8.1711 | -0.33875 | 121.2662 | 121.4081 | -0.11902 | -0.16479 | 0.11902 | 0.041199 | -0.045776 | 0.059509 | 0.13733 | 0.09613 | -0.082398 | 0.15564 | 0.10986 | -0.10529 | 0.082397 | -0.064087 | -0.17395 | 0.036621 | 121.6003 | 121.5637 | 8.8852 | -121.6049 | 121.5408 | 121.6827 | 8.4457 | -121.5363
1282.6406 | 121.7514 | -0.21973 | 121.3669 | -0.0049592 | 0.00038233 | 0.065828 | 0.001034 | 0.06498 | -0.0046313 | 0.0013203 | -0.0054932 | -0.0068337 | 0.063339 | 0.065901 | -0.2034 | -0.0013436 | 121.312 | -0.13275 | 8.7204 | -0.091553 | 121.2799 | -0.13733 | -0.19226 | -0.15106 | 8.2809 | -0.22888 | 121.2296 | 121.376 | -0.09613 | -0.11902 | 0.082398 | 0.027466 | -0.086975 | 0.086976 | 0.12817 | 0.10071 | -0.054931 | 0.1236 | 0.10071 | -0.13733 | 0.068665 | -0.009155 | -0.10986 | 0.009156 | 121.4996 | 121.5317 | 8.9401 | -121.5591 | 121.4493 | 121.5958 | 8.5007 | -121.4859
1284.3906 | 121.7834 | -0.24261 | 121.3715 | 0.0026703 | 0.00038233 | 0.067751 | 0.00082022 | 0.066902 | -0.0056995 | -0.00081594 | -0.0054932 | -0.0068337 | 0.062485 | 0.066114 | -0.20147 | -0.0041208 | 121.3577 | -0.091553 | 8.7982 | -0.073242 | 121.2982 | -0.13733 | -0.19684 | -0.10071 | 8.3633 | -0.18768 | 121.2067 | 121.3806 | -0.091553 | -0.1236 | 0.10529 | 0.045777 | -0.073242 | 0.15106 | 0.16937 | 0.1236 | -0.013733 | 0.15106 | 0.11902 | -0.16479 | 0.14191 | 0.054932 | -0.064087 | 0.009155 | 121.5408 | 121.6003 | 9.0408 | -121.5683 | 121.4493 | 121.6232 | 8.606 | -121.4951
1286.0938 | 121.6232 | -0.25635 | 121.4218 | -0.012589 | 0.012559 | 0.063265 | 0.0029566 | 0.06733 | 0.0071179 | -0.00038874 | -0.0054932 | 0.00085668 | 0.067398 | 0.068464 | -0.19742 | -0.0051888 | 121.3806 | -0.15564 | 8.8211 | -0.11444 | 121.3165 | -0.15564 | -0.23346 | -0.12817 | 8.3176 | -0.3067 | 121.2204 | 121.4127 | -0.10986 | -0.15106 | 0.10071 | 0.022889 | -0.10529 | 0.10071 | 0.14191 | 0.11902 | -0.041199 | 0.14649 | 0.10529 | -0.20142 | 0.12817 | -0.050354 | -0.15564 | -0.009155 | 121.5729 | 121.637 | 9.0775 | -121.6553 | 121.4767 | 121.669 | 8.5739 | -121.5729
1287.8594 | 121.7422 | -0.21057 | 121.376 | -0.012589 | 0.0040139 | 0.065187 | 0.0035974 | 0.066475 | -0.0048449 | 0.0019611 | -0.0054932 | -0.0068337 | 0.064835 | 0.066328 | -0.20361 | -0.001771 | 121.4218 | -0.032043 | 8.9539 | -0.036621 | 121.2616 | -0.1236 | -0.1831 | -0.068665 | 8.432 | -0.17395 | 121.2204 | 121.3898 | -0.073242 | -0.12817 | 0.086975 | 0.027466 | -0.11444 | 0.17853 | 0.17395 | 0.14648 | 0.045776 | 0.13733 | 0.082397 | -0.15564 | 0.14191 | 0.036621 | -0.045776 | 0.013733 | 121.4722 | 121.6324 | 9.1644 | -121.5591 | 121.431 | 121.6003 | 8.6426 | -121.5042
1289.6094 | 121.6324 | -0.27008 | 121.4127 | -0.0049592 | 0.0046549 | 0.06476 | 0.0025292 | 0.064766 | -0.0029223 | 3.8456e-05 | 0.0097658 | -0.0046975 | 0.066544 | 0.065687 | -0.19977 | -0.0051888 | 121.3806 | -0.059509 | 8.9905 | -0.059509 | 121.2891 | -0.14648 | -0.20599 | -0.10071 | 8.4366 | -0.21057 | 121.2204 | 121.3898 | -0.10071 | -0.12817 | 0.1236 | 0.064087 | -0.1236 | 0.21057 | 0.21057 | 0.14649 | -0.032044 | 0.16937 | 0.14191 | -0.19226 | 0.16937 | 0.05951 | -0.082397 | -0.022888 | 121.5591 | 121.6507 | 9.2606 | -121.6187 | 121.4905 | 121.6599 | 8.7067 | -121.5408
1291.3125 | 121.7377 | -0.23804 | 121.3852 | 0.0026703 | 0.0027323 | 0.064974 | -0.0025976 | 0.06498 | 0.00028207 | -0.0010297 | -0.0054932 | -0.0014933 | 0.061203 | 0.067396 | -0.19934 | -0.0024118 | 121.4172 | -0.059509 | 8.9493 | -0.041199 | 121.2753 | -0.1236 | -0.1831 | -0.064087 | 8.4091 | -0.18768 | 121.2158 | 121.376 | -0.09613 | -0.09613 | 0.11444 | 0.054932 | -0.10986 | 0.17853 | 0.19684 | 0.14191 | 0.032043 | 0.14191 | 0.14191 | -0.16937 | 0.17395 | 0.050354 | -0.091553 | -0.009155 | 121.5134 | 121.6553 | 9.1873 | -121.5683 | 121.4539 | 121.6141 | 8.6472 | -121.4813
1293.0781 | 121.6644 | -0.25635 | 121.4127 | -0.0049592 | 0.0050821 | 0.063905 | 0.00017942 | 0.069039 | -0.00057253 | 0.00067926 | -0.0054932 | -0.0019205 | 0.065048 | 0.065901 | -0.20083 | -0.0024118 | 121.2982 | -0.19226 | 8.9401 | -0.13275 | 121.344 | -0.17395 | -0.21973 | -0.17395 | 8.3862 | -0.31586 | 121.2799 | 121.431 | -0.12817 | -0.16022 | 0.082398 | 0.036621 | -0.068665 | 0.064087 | 0.1236 | 0.086976 | -0.11444 | 0.12817 | 0.096131 | -0.13275 | 0.082398 | -0.059509 | -0.15564 | 0.01831 | 121.6003 | 121.5546 | 9.1965 | -121.6324 | 121.5363 | 121.6873 | 8.6426 | -121.5729
1294.8281 | 121.6644 | -0.2655 | 121.4035 | -0.012589 | 0.0097817 | 0.064333 | 0.0033838 | 0.065193 | 0.0030591 | 0.0049519 | -0.0054932 | -0.0014933 | 0.066757 | 0.0706 | -0.20169 | -0.0047616 | 121.3486 | -0.15106 | 9.0317 | -0.10529 | 121.3211 | -0.14648 | -0.24261 | -0.11444 | 8.4595 | -0.29755 | 121.2433 | 121.3989 | -0.11444 | -0.15564 | 0.11902 | 0.022888 | -0.082397 | 0.11444 | 0.16022 | 0.13733 | -0.054931 | 0.15106 | 0.10986 | -0.16022 | 0.15106 | -0.032043 | -0.14191 | -0.004577 | 121.5866 | 121.6141 | 9.2972 | -121.6461 | 121.5088 | 121.6644 | 8.725 | -121.5591
1296.5938 | 121.6919 | -0.23346 | 121.3989 | 0.0026703 | 0.0014505 | 0.06711 | 0.0014612 | 0.066689 | -0.0054859 | 0.0019611 | 0.0021363 | -0.0079019 | 0.065262 | 0.065901 | -0.20083 | -0.00091641 | 121.344 | -0.10071 | 9.05 | -0.086975 | 121.2708 | -0.13275 | -0.19684 | -0.1236 | 8.4412 | -0.23346 | 121.2112 | 121.3943 | -0.086975 | -0.14191 | 0.10071 | 0.036621 | -0.12817 | 0.13275 | 0.14648 | 0.10986 | -0.054932 | 0.14648 | 0.091552 | -0.18768 | 0.10986 | 0 | -0.091552 | -0.004578 | 121.5042 | 121.5775 | 9.2834 | -121.5958 | 121.4447 | 121.6278 | 8.6746 | -121.5408
1298.375 | 121.6278 | -0.2655 | 121.3943 | -0.012589 | 0.0046549 | 0.06241 | 0.00082022 | 0.066902 | 0.0043409 | 0.0028155 | -0.0054932 | -0.0027749 | 0.066544 | 0.069532 | -0.19827 | -0.0026254 | 121.3669 | -0.11444 | 9.1187 | -0.10529 | 121.3394 | -0.15564 | -0.23346 | -0.10071 | 8.5098 | -0.28381 | 121.2341 | 121.3943 | -0.10529 | -0.14191 | 0.10986 | 0.032044 | -0.054931 | 0.15106 | 0.16022 | 0.12817 | -0.027466 | 0.16022 | 0.1236 | -0.16022 | 0.16479 | -0.01831 | -0.14191 | 0 | 121.6049 | 121.6324 | 9.3842 | -121.6278 | 121.4996 | 121.6599 | 8.7753 | -121.5363
1300.0781 | 121.7377 | -0.23804 | 121.3806 | 0.0026703 | 0.0044411 | 0.065401 | -0.001316 | 0.06498 | 0.0015637 | 0.0030293 | -0.0054932 | -0.0027749 | 0.06398 | 0.066114 | -0.19977 | -0.0024118 | 121.3074 | -0.18768 | 9.0454 | -0.14191 | 121.3028 | -0.16479 | -0.2243 | -0.16022 | 8.4641 | -0.30212 | 121.2479 | 121.4264 | -0.10071 | -0.16479 | 0.073242 | 0.013733 | -0.07782 | 0.050354 | 0.09613 | 0.082397 | -0.073242 | 0.13733 | 0.073242 | -0.13275 | 0.07782 | -0.064087 | -0.13733 | 0.045777 | 121.5408 | 121.5454 | 9.2834 | -121.6049 | 121.4859 | 121.6644 | 8.7021 | -121.5454
1301.8438 | 121.637 | -0.27008 | 121.3989 | -0.0049592 | 0.0091409 | 0.064119 | 0.0027428 | 0.065834 | 0.0015637 | 0.0019611 | -0.0054932 | -0.00021152 | 0.066971 | 0.067182 | -0.20041 | -0.0041208 | 121.3669 | -0.11902 | 9.2011 | -0.082397 | 121.312 | -0.14648 | -0.23804 | -0.11444 | 8.5922 | -0.25635 | 121.2616 | 121.431 | -0.10986 | -0.14648 | 0.1236 | 0.032044 | -0.086975 | 0.15106 | 0.18768 | 0.15564 | -0.032044 | 0.16022 | 0.1236 | -0.13733 | 0.15564 | 0.013733 | -0.10986 | 0.032043 | 121.582 | 121.637 | 9.4711 | -121.637 | 121.5317 | 121.7011 | 8.8623 | -121.5454
1303.6094 | 121.6232 | -0.25635 | 121.4172 | 0.0026703 | 0.0052957 | 0.066255 | 0.00082022 | 0.067971 | -0.0048449 | -0.00060234 | -0.0054932 | -0.0038431 | 0.066971 | 0.065901 | -0.20276 | -0.00091641 | 121.312 | -0.14648 | 9.2377 | -0.11444 | 121.3074 | -0.14648 | -0.22888 | -0.1831 | 8.5419 | -0.29755 | 121.257 | 121.4493 | -0.11902 | -0.14648 | 0.10986 | 0.027466 | -0.10986 | 0.10986 | 0.14191 | 0.11444 | -0.10529 | 0.13733 | 0.10986 | -0.16022 | 0.073243 | -0.041198 | -0.15106 | 0.032044 | 121.5637 | 121.5683 | 9.494 | -121.6461 | 121.5134 | 121.7056 | 8.7982 | -121.5637
1305.3125 | 121.7834 | -0.23346 | 121.3669 | -0.012589 | 0.0033731 | 0.065401 | 0.0040246 | 0.066902 | -0.0056995 | 0.00067926 | -0.0054932 | -0.0064065 | 0.062912 | 0.065473 | -0.20382 | -0.0036936 | 121.3394 | -0.09613 | 9.2697 | -0.064087 | 121.3074 | -0.13733 | -0.21057 | -0.10529 | 8.638 | -0.1831 | 121.2112 | 121.4035 | -0.082397 | -0.1236 | 0.09613 | 0.022888 | -0.059509 | 0.13733 | 0.16937 | 0.14648 | -0.027465 | 0.15106 | 0.10986 | -0.15564 | 0.12817 | 0.050354 | -0.059509 | 0.036621 | 121.5408 | 121.5729 | 9.5032 | -121.5775 | 121.4447 | 121.637 | 8.8715 | -121.4905
1307.0781 | 121.7377 | -0.21515 | 121.3806 | 0.0026703 | 0.0018777 | 0.064974 | -0.0036658 | 0.065407 | 0.00070927 | 0.00067926 | -0.013123 | -0.00063872 | 0.063126 | 0.066755 | -0.19784 | -0.0043344 | 121.3348 | -0.16937 | 9.2239 | -0.13275 | 121.3257 | -0.16479 | -0.23346 | -0.14648 | 8.5648 | -0.30212 | 121.2616 | 121.4127 | -0.10071 | -0.13275 | 0.050354 | -0.01831 | -0.054931 | 0.045776 | 0.082398 | 0.10071 | -0.045776 | 0.11444 | 0.082398 | -0.11902 | 0.068665 | -0.086975 | -0.16937 | 0.032044 | 121.5408 | 121.55 | 9.4391 | -121.6141 | 121.4767 | 121.6278 | 8.7799 | -121.5134
1308.8438 | 121.756 | -0.22888 | 121.3669 | -0.0049592 | -0.0043173 | 0.067323 | 0.00039302 | 0.066902 | -0.0059131 | -0.00038874 | -0.0054932 | -0.0066201 | 0.061844 | 0.065473 | -0.20425 | -0.00091641 | 121.3348 | -0.10986 | 9.3384 | -0.068665 | 121.2982 | -0.13733 | -0.19684 | -0.1236 | 8.6472 | -0.18768 | 121.2112 | 121.4035 | -0.086975 | -0.11902 | 0.091553 | 0.032044 | -0.068664 | 0.11902 | 0.16022 | 0.12817 | -0.032043 | 0.14191 | 0.10986 | -0.15564 | 0.10529 | 0.041199 | -0.068664 | 0.036621 | 121.5271 | 121.5637 | 9.5673 | -121.5637 | 121.4401 | 121.6324 | 8.876 | -121.4859
1310.6094 | 121.6232 | -0.25177 | 121.4218 | -0.0049592 | 0.0031595 | 0.063692 | -0.0015296 | 0.066048 | 0.0056225 | 0.0021747 | -0.013123 | -0.0010659 | 0.063766 | 0.065473 | -0.19806 | -0.0043344 | 121.3165 | -0.19684 | 9.3475 | -0.12817 | 121.3211 | -0.16022 | -0.2243 | -0.16937 | 8.5739 | -0.34332 | 121.2845 | 121.4493 | -0.10986 | -0.16479 | 0.091553 | 0.027466 | -0.10071 | 0.054932 | 0.1236 | 0.09613 | -0.10529 | 0.14191 | 0.086975 | -0.13733 | 0.082397 | -0.091553 | -0.17853 | 0.027466 | 121.5729 | 121.5683 | 9.5993 | -121.6461 | 121.5363 | 121.701 | 8.8257 | -121.5866
1312.375 | 121.6324 | -0.2655 | 121.4127 | 0.0026703 | 0.0052957 | 0.064333 | -0.001316 | 0.066048 | 0.0026319 | 0.0034565 | -0.013123 | 0.0010703 | 0.063553 | 0.068464 | -0.19998 | -0.0036936 | 121.2982 | -0.2243 | 9.3384 | -0.14648 | 121.3028 | -0.16479 | -0.21973 | -0.17853 | 8.5922 | -0.33417 | 121.2799 | 121.4676 | -0.11444 | -0.14648 | 0.10071 | 0.045776 | -0.10986 | 0.041199 | 0.11902 | 0.073243 | -0.11444 | 0.15106 | 0.11902 | -0.13275 | 0.086975 | -0.068664 | -0.18768 | 0.054931 | 121.5683 | 121.5637 | 9.6039 | -121.6324 | 121.5454 | 121.7331 | 8.8577 | -121.5591
1314.1406 | 121.669 | -0.25177 | 121.3989 | -0.020218 | 0.0061501 | 0.065187 | 0.0012476 | 0.06733 | -0.00057253 | 0.0011067 | -0.0054932 | -0.0023477 | 0.06633 | 0.06761 | -0.20041 | -0.0034798 | 121.3257 | -0.16022 | 9.462 | -0.11902 | 121.3577 | -0.14648 | -0.23804 | -0.15106 | 8.7112 | -0.28839 | 121.2662 | 121.4355 | -0.10071 | -0.1236 | 0.10529 | 0.013733 | -0.041199 | 0.091553 | 0.13275 | 0.11902 | -0.073242 | 0.15106 | 0.12817 | -0.13275 | 0.10071 | -0.036621 | -0.1648 | 0.036621 | 121.6095 | 121.5775 | 9.7137 | -121.637 | 121.5179 | 121.6873 | 8.963 | -121.5225
1315.8438 | 121.6507 | -0.26093 | 121.4355 | -0.012589 | 0.0042275 | 0.065828 | 0.0035974 | 0.06498 | -0.0042041 | 3.8456e-05 | 0.0021363 | -0.0053385 | 0.065689 | 0.066328 | -0.20297 | -0.00027561 | 121.376 | -0.045776 | 9.6085 | -0.041199 | 121.2433 | -0.13733 | -0.1831 | -0.10071 | 8.7936 | -0.1831 | 121.2296 | 121.4355 | -0.068665 | -0.10986 | 0.1236 | 0.07782 | -0.19226 | 0.21515 | 0.21973 | 0.14191 | -0.059509 | 0.19226 | 0.15106 | -0.20599 | 0.16022 | 0.07782 | -0.073242 | 0 | 121.5042 | 121.637 | 9.8694 | -121.6187 | 121.4905 | 121.6965 | 9.0546 | -121.5454
1317.6094 | 121.6415 | -0.25177 | 121.431 | -0.012589 | 0.0057229 | 0.064119 | -0.001316 | 0.065834 | 0.0019909 | 0.0036701 | -0.0054932 | 2.078e-06 | 0.06633 | 0.068891 | -0.19912 | -0.002839 | 121.3074 | -0.21515 | 9.4437 | -0.15106 | 121.344 | -0.16022 | -0.22888 | -0.16022 | 8.67 | -0.33875 | 121.257 | 121.4493 | -0.10529 | -0.14191 | 0.091553 | 0.022888 | -0.086975 | 0.036621 | 0.10071 | 0.07782 | -0.1236 | 0.14648 | 0.10986 | -0.17395 | 0.091553 | -0.086975 | -0.19684 | 0.018311 | 121.5958 | 121.5591 | 9.6954 | -121.6599 | 121.5088 | 121.701 | 8.9218 | -121.5729
1319.375 | 121.6324 | -0.26093 | 121.4355 | -0.0049592 | 0.0042275 | 0.066683 | 0.0014612 | 0.06968 | -0.0020679 | 0.00046566 | -0.020752 | -0.0025613 | 0.065689 | 0.06825 | -0.20212 | -0.0019846 | 121.3028 | -0.16479 | 9.5947 | -0.14648 | 121.312 | -0.15106 | -0.24261 | -0.19226 | 8.7616 | -0.30212 | 121.2616 | 121.4355 | -0.13733 | -0.15564 | 0.10986 | 0.01831 | -0.1236 | 0.09613 | 0.11444 | 0.096131 | -0.13275 | 0.1236 | 0.10529 | -0.17395 | 0.068664 | -0.041199 | -0.14648 | 0 | 121.5729 | 121.5637 | 9.8557 | -121.6782 | 121.5225 | 121.6965 | 9.0225 | -121.5912
1321.0781 | 121.7377 | -0.22888 | 121.4035 | -0.0049592 | 0.0048685 | 0.066896 | 0.0033838 | 0.066262 | -0.0046313 | -0.0018841 | -0.0054932 | -0.0053385 | 0.063339 | 0.068037 | -0.20254 | -0.001771 | 121.4172 | -0.009155 | 9.7229 | -0.036621 | 121.2936 | -0.11902 | -0.20599 | -0.086975 | 8.8852 | -0.15564 | 121.2112 | 121.4127 | -0.068665 | -0.10529 | 0.10986 | 0.022888 | -0.10986 | 0.21973 | 0.19226 | 0.16937 | 0.013733 | 0.16022 | 0.1236 | -0.19226 | 0.14191 | 0.073242 | -0.050354 | 0.009156 | 121.5225 | 121.6461 | 9.9518 | -121.6095 | 121.4401 | 121.6415 | 9.1141 | -121.5088
1322.8438 | 121.7102 | -0.23804 | 121.3989 | -0.0049592 | 0.0027323 | 0.065828 | 0.00039302 | 0.066689 | -0.0029223 | 3.8456e-05 | -0.013123 | -0.0059793 | 0.065903 | 0.067182 | -0.20276 | -0.0034798 | 121.4127 | -0.032043 | 9.7733 | -0.050354 | 121.2982 | -0.14191 | -0.18768 | -0.059509 | 8.9127 | -0.16937 | 121.2433 | 121.3989 | -0.07782 | -0.11902 | 0.09613 | 0.050354 | -0.10071 | 0.20599 | 0.18768 | 0.13733 | 0.013733 | 0.16022 | 0.11902 | -0.15564 | 0.17853 | 0.068664 | -0.050354 | 0 | 121.5363 | 121.6507 | 10.0113 | -121.5866 | 121.4813 | 121.637 | 9.1507 | -121.5179
1324.6094 | 121.6187 | -0.25635 | 121.4035 | -0.0049592 | 0.0059365 | 0.064333 | -0.0011024 | 0.067543 | 0.0058363 | -0.00017514 | -0.013123 | 0.0010703 | 0.066544 | 0.06761 | -0.1972 | -0.0041208 | 121.344 | -0.16937 | 9.6634 | -0.11902 | 121.344 | -0.14648 | -0.21515 | -0.15106 | 8.8074 | -0.33875 | 121.2662 | 121.4264 | -0.11444 | -0.16022 | 0.10986 | 0.041199 | -0.059509 | 0.086975 | 0.13733 | 0.09613 | -0.059509 | 0.14191 | 0.096131 | -0.13733 | 0.10529 | -0.082397 | -0.17853 | 0.022889 | 121.6003 | 121.6003 | 9.9197 | -121.6187 | 121.5225 | 121.6827 | 9.0637 | -121.5637
1326.3125 | 121.6095 | -0.2655 | 121.4127 | 0.0026703 | 0.0042275 | 0.063265 | -0.0011024 | 0.067543 | 0.0034863 | 0.0030293 | -0.0054932 | 0.00021568 | 0.064194 | 0.069746 | -0.19848 | -0.0043344 | 121.3257 | -0.16479 | 9.7229 | -0.13275 | 121.3303 | -0.16479 | -0.21057 | -0.16479 | 8.8486 | -0.32959 | 121.2662 | 121.4355 | -0.10986 | -0.14648 | 0.10071 | 0.054932 | -0.082398 | 0.10071 | 0.13275 | 0.07782 | -0.086975 | 0.15564 | 0.11902 | -0.14648 | 0.10071 | -0.064087 | -0.18311 | 0.022888 | 121.5958 | 121.5912 | 9.9884 | -121.6232 | 121.5317 | 121.701 | 9.1141 | -121.5591
1328.0625 | 121.7056 | -0.23346 | 121.3852 | -0.0049592 | -0.00068567 | 0.064546 | 0.0012476 | 0.067543 | -0.0042041 | 0.0026019 | 0.0021363 | -0.0059793 | 0.064835 | 0.067823 | -0.20361 | -0.00091641 | 121.3852 | -0.041199 | 9.8328 | -0.059509 | 121.257 | -0.13275 | -0.17853 | -0.073242 | 8.9493 | -0.19226 | 121.225 | 121.3943 | -0.09613 | -0.09613 | 0.10071 | 0.054931 | -0.12817 | 0.19226 | 0.17395 | 0.11902 | 0 | 0.13733 | 0.13733 | -0.16022 | 0.16022 | 0.041198 | -0.096131 | 0.009155 | 121.4905 | 121.6187 | 10.0662 | -121.5637 | 121.4584 | 121.6278 | 9.1827 | -121.4813
1329.7656 | 121.6141 | -0.27924 | 121.4447 | -0.012589 | 0.0046549 | 0.065828 | 0.00082022 | 0.065621 | 0.0030591 | 0.00089286 | 0.0021363 | -0.0032021 | 0.067825 | 0.067823 | -0.19891 | -0.0043344 | 121.3074 | -0.1831 | 9.8053 | -0.10986 | 121.3486 | -0.15564 | -0.23804 | -0.17853 | 8.8623 | -0.35248 | 121.2982 | 121.4401 | -0.11902 | -0.14191 | 0.1236 | 0.041199 | -0.09613 | 0.096131 | 0.16937 | 0.12817 | -0.13733 | 0.16022 | 0.13733 | -0.14648 | 0.10071 | -0.073242 | -0.21057 | -0.004577 | 121.6278 | 121.5866 | 10.0845 | -121.6827 | 121.5775 | 121.7194 | 9.1415 | -121.5866
1331.5469 | 121.7514 | -0.22888 | 121.3715 | 0.0026703 | 0.0027323 | 0.063692 | 0.0014612 | 0.064766 | -0.0031359 | 0.0023883 | -0.013123 | -0.0057657 | 0.064621 | 0.067182 | -0.20019 | -0.0024118 | 121.3898 | -0.032043 | 9.906 | -0.032043 | 121.2891 | -0.11902 | -0.19684 | -0.054932 | 9.0042 | -0.19684 | 121.2433 | 121.3486 | -0.064087 | -0.10529 | 0.10986 | 0.032044 | -0.082398 | 0.19684 | 0.19684 | 0.1648 | 0.018311 | 0.16479 | 0.1236 | -0.12817 | 0.17395 | 0.032044 | -0.091552 | -0.022888 | 121.5179 | 121.6187 | 10.1349 | -121.5683 | 121.4722 | 121.5775 | 9.2331 | -121.4767
1333.25 | 121.7697 | -0.20599 | 121.3806 | 0.0026703 | 0.00080973 | 0.068178 | 0.0031702 | 0.065834 | -0.0054859 | -0.0012433 | -0.013123 | -0.0042703 | 0.064194 | 0.066969 | -0.20254 | -0.00091641 | 121.3715 | -0.036621 | 9.993 | -0.050354 | 121.2753 | -0.13733 | -0.21057 | -0.059509 | 9.05 | -0.16937 | 121.225 | 121.3989 | -0.086975 | -0.10071 | 0.068665 | -0.004577 | -0.10529 | 0.16937 | 0.15564 | 0.16022 | -0.009155 | 0.11902 | 0.10529 | -0.15564 | 0.14649 | 0.036621 | -0.068665 | 0.018311 | 121.4813 | 121.5775 | 10.199 | -121.5912 | 121.431 | 121.6049 | 9.256 | -121.4813
1335.0156 | 121.7148 | -0.24261 | 121.4035 | -0.0049592 | -0.0015403 | 0.064333 | 0.0012476 | 0.065193 | -0.0018543 | 0.0013203 | 0.0097658 | -0.0055521 | 0.063553 | 0.066969 | -0.20254 | -0.00113 | 121.3577 | -0.07782 | 9.9655 | -0.07782 | 121.2982 | -0.10986 | -0.20142 | -0.12817 | 8.9905 | -0.21057 | 121.2112 | 121.4127 | -0.082397 | -0.10071 | 0.13275 | 0.041199 | -0.10528 | 0.16479 | 0.16479 | 0.1236 | -0.045776 | 0.16022 | 0.14191 | -0.19226 | 0.11444 | 0.032044 | -0.10986 | 0.009156 | 121.5408 | 121.6003 | 10.2081 | -121.6049 | 121.4539 | 121.6553 | 9.2331 | -121.5042
1336.9531 | 121.5958 | -0.27008 | 121.4355 | -0.0049592 | 0.0052957 | 0.065187 | -0.0025976 | 0.064553 | 0.0030591 | 3.8456e-05 | -0.013123 | 0.00085668 | 0.062057 | 0.068037 | -0.19784 | -0.0039072 | 121.3531 | -0.14648 | 9.993 | -0.10986 | 121.3165 | -0.14191 | -0.21973 | -0.14648 | 8.9996 | -0.33417 | 121.2936 | 121.4081 | -0.14191 | -0.15106 | 0.12817 | 0.050354 | -0.11902 | 0.1236 | 0.16022 | 0.10986 | -0.082398 | 0.12817 | 0.11902 | -0.14191 | 0.1236 | -0.064086 | -0.1831 | -0.027466 | 121.5866 | 121.6232 | 10.2631 | -121.6553 | 121.5637 | 121.6782 | 9.2697 | -121.5866
1338.7188 | 121.7651 | -0.21057 | 121.3943 | 0.0026703 | 0.0010233 | 0.066896 | 0.0014612 | 0.064553 | -0.0063403 | -0.0014569 | -0.0054932 | -0.0061929 | 0.062698 | 0.066755 | -0.20318 | -0.00070281 | 121.4081 | -0.032043 | 10.1395 | -0.059509 | 121.2799 | -0.12817 | -0.19226 | -0.068665 | 9.1278 | -0.16022 | 121.225 | 121.3943 | -0.064087 | -0.10529 | 0.082397 | 0.01831 | -0.11444 | 0.17853 | 0.15106 | 0.13275 | 0.013733 | 0.14648 | 0.10529 | -0.16937 | 0.14191 | 0.050354 | -0.054931 | 0 | 121.4905 | 121.6187 | 10.35 | -121.5866 | 121.4355 | 121.6049 | 9.3384 | -121.4996
1340.4844 | 121.7651 | -0.22888 | 121.3577 | 0.0026703 | -4.4874e-05 | 0.064546 | 0.0027428 | 0.066902 | -0.0035633 | -0.00081594 | -0.0054932 | -0.0042703 | 0.063766 | 0.06761 | -0.20361 | -0.00070281 | 121.376 | -0.082397 | 10.1303 | -0.073242 | 121.3257 | -0.12817 | -0.20599 | -0.10529 | 9.1141 | -0.19226 | 121.2524 | 121.4127 | -0.086975 | -0.11444 | 0.10071 | 0.022888 | -0.032043 | 0.14649 | 0.15564 | 0.13275 | 0.018311 | 0.14191 | 0.11444 | -0.10529 | 0.1236 | 0.036621 | -0.07782 | 0.054932 | 121.5546 | 121.6049 | 10.3592 | -121.5637 | 121.4813 | 121.6415 | 9.343 | -121.4722
1342.2031 | 121.6873 | -0.23804 | 121.4264 | -0.012589 | 0.0035867 | 0.066042 | -0.00024778 | 0.06733 | 0.0028455 | 0.00067926 | -0.013123 | -0.0014933 | 0.065689 | 0.068891 | -0.1987 | -0.0030526 | 121.3257 | -0.21057 | 10.0662 | -0.12817 | 121.3623 | -0.16022 | -0.24719 | -0.16022 | 9.0042 | -0.32044 | 121.2845 | 121.4172 | -0.10986 | -0.15564 | 0.07782 | -0.009155 | -0.064087 | 0.027466 | 0.10986 | 0.11902 | -0.10071 | 0.12817 | 0.082397 | -0.14191 | 0.07782 | -0.082398 | -0.1648 | -0.009156 | 121.6003 | 121.5637 | 10.3043 | -121.6736 | 121.5225 | 121.6553 | 9.2422 | -121.582
1343.9688 | 121.7148 | -0.2243 | 121.4081 | 0.0026703 | 0.0025185 | 0.063905 | 0.0016748 | 0.06733 | -0.0042041 | 0.0011067 | 0.0021363 | -0.0046975 | 0.065262 | 0.066542 | -0.20361 | -0.0019846 | 121.3623 | -0.064087 | 10.1944 | -0.068665 | 121.2845 | -0.12817 | -0.20599 | -0.11902 | 9.1141 | -0.21973 | 121.2387 | 121.3806 | -0.091553 | -0.13275 | 0.09613 | 0.01831 | -0.1236 | 0.16022 | 0.15564 | 0.13733 | -0.045776 | 0.13275 | 0.091553 | -0.16937 | 0.10529 | 0.004577 | -0.086976 | -0.027466 | 121.5088 | 121.5866 | 10.4187 | -121.6141 | 121.463 | 121.6049 | 9.3384 | -121.5408
1345.6719 | 121.6278 | -0.27466 | 121.4447 | 0.0103 | 0.0057229 | 0.064119 | 0.00017942 | 0.066048 | 0.0071179 | 0.0032429 | -0.0054932 | 0.00085668 | 0.066971 | 0.068037 | -0.19912 | -0.0039072 | 121.3303 | -0.16022 | 10.2219 | -0.11444 | 121.3623 | -0.17395 | -0.23346 | -0.13733 | 9.1141 | -0.33875 | 121.2753 | 121.4035 | -0.1236 | -0.14648 | 0.10071 | 0.041199 | -0.082397 | 0.11444 | 0.16022 | 0.11902 | -0.11444 | 0.15106 | 0.12817 | -0.16937 | 0.13733 | -0.064087 | -0.19226 | -0.041199 | 121.637 | 121.6049 | 10.4965 | -121.6782 | 121.55 | 121.6782 | 9.3887 | -121.5912
1347.4375 | 121.637 | -0.28381 | 121.4493 | -0.012589 | 0.0042275 | 0.067323 | 0.0023156 | 0.068184 | -0.00099973 | 0.00067926 | -0.013123 | -0.0036295 | 0.063766 | 0.067823 | -0.20212 | -0.0034798 | 121.3028 | -0.16022 | 10.2859 | -0.13733 | 121.344 | -0.15106 | -0.21973 | -0.17853 | 9.1553 | -0.29297 | 121.2799 | 121.4539 | -0.11902 | -0.15106 | 0.13275 | 0.064086 | -0.10529 | 0.1236 | 0.14648 | 0.082398 | -0.14648 | 0.16479 | 0.13275 | -0.16937 | 0.10528 | -0.009156 | -0.14191 | 0.004577 | 121.6278 | 121.5866 | 10.5698 | -121.669 | 121.5637 | 121.7377 | 9.4391 | -121.6003
1349.1406 | 121.7697 | -0.21515 | 121.3989 | -0.012589 | 0.0038003 | 0.066042 | 0.0033838 | 0.064339 | -0.0044177 | -0.00038874 | -0.013123 | -0.0057657 | 0.064194 | 0.066328 | -0.20425 | -0.0015572 | 121.3715 | -0.054932 | 10.3912 | -0.059509 | 121.3165 | -0.12817 | -0.20142 | -0.091553 | 9.3063 | -0.16937 | 121.2067 | 121.4035 | -0.082397 | -0.11444 | 0.086975 | 0.013733 | -0.082398 | 0.16022 | 0.15564 | 0.14191 | -0.027466 | 0.13275 | 0.10071 | -0.19226 | 0.1236 | 0.045776 | -0.054932 | 0.004577 | 121.5317 | 121.5866 | 10.6064 | -121.6003 | 121.4218 | 121.6187 | 9.5215 | -121.5134
1350.9062 | 121.7468 | -0.21515 | 121.4035 | 0.0026703 | 0.0010233 | 0.065828 | -0.004093 | 0.066048 | 0.0022047 | 0.0015339 | 0.0021363 | -0.0036295 | 0.064194 | 0.066969 | -0.19912 | -0.0026254 | 121.4081 | -0.041199 | 10.3912 | -0.036621 | 121.2936 | -0.1236 | -0.1831 | -0.036621 | 9.288 | -0.17853 | 121.2341 | 121.3852 | -0.064087 | -0.09613 | 0.091553 | 0.032044 | -0.10986 | 0.17395 | 0.17853 | 0.14648 | 0.004578 | 0.15106 | 0.11902 | -0.16937 | 0.17853 | 0.036621 | -0.082398 | -0.01831 | 121.5088 | 121.6232 | 10.6064 | -121.5866 | 121.4493 | 121.6003 | 9.5032 | -121.4996
1352.6719 | 121.7468 | -0.20599 | 121.3852 | 0.0026703 | 0.0055093 | 0.063692 | 0.0012476 | 0.066902 | -0.00078613 | 0.0043109 | 0.0021363 | -0.0036295 | 0.065475 | 0.068037 | -0.19848 | -0.0056162 | 121.3943 | -0.086975 | 10.4187 | -0.045776 | 121.3028 | -0.12817 | -0.20599 | -0.045776 | 9.3018 | -0.19684 | 121.2479 | 121.4035 | -0.068665 | -0.10529 | 0.07782 | 0 | -0.082398 | 0.11902 | 0.16022 | 0.16022 | 0.009155 | 0.13733 | 0.10071 | -0.13733 | 0.16022 | 0.009156 | -0.091552 | 0.01831 | 121.5088 | 121.6003 | 10.6247 | -121.5912 | 121.4539 | 121.6095 | 9.5078 | -121.4905
1354.375 | 121.6461 | -0.27466 | 121.4172 | -0.012589 | 0.0061501 | 0.063051 | -0.0034522 | 0.066475 | 0.0066907 | 0.0017475 | 0.0021363 | -0.0014933 | 0.065903 | 0.06825 | -0.19891 | -0.0039072 | 121.3257 | -0.19226 | 10.3867 | -0.13733 | 121.3348 | -0.16022 | -0.21973 | -0.16479 | 9.2331 | -0.3479 | 121.3028 | 121.4355 | -0.10986 | -0.16022 | 0.11444 | 0.054931 | -0.082397 | 0.082397 | 0.13733 | 0.082398 | -0.091552 | 0.1648 | 0.11444 | -0.11444 | 0.10986 | -0.073242 | -0.18768 | 0.018311 | 121.6095 | 121.6003 | 10.6613 | -121.637 | 121.5775 | 121.7102 | 9.5078 | -121.5775
1356.1406 | 121.6232 | -0.2655 | 121.4447 | -0.012589 | 0.0038003 | 0.064119 | 0.0023156 | 0.066048 | -0.0016405 | 3.8456e-05 | -0.013123 | -0.0038431 | 0.065475 | 0.068678 | -0.20276 | -0.0021982 | 121.312 | -0.13275 | 10.5011 | -0.12817 | 121.3257 | -0.15564 | -0.21973 | -0.16937 | 9.3018 | -0.28839 | 121.2753 | 121.4218 | -0.11444 | -0.15564 | 0.10986 | 0.045776 | -0.11902 | 0.13275 | 0.13733 | 0.091553 | -0.13275 | 0.15106 | 0.10986 | -0.16937 | 0.09613 | -0.022888 | -0.13275 | -0.022888 | 121.5912 | 121.5775 | 10.7666 | -121.6644 | 121.5408 | 121.6873 | 9.5673 | -121.6003
1357.8438 | 121.7789 | -0.2243 | 121.3943 | 0.0103 | 0.0010233 | 0.068819 | 0.00082022 | 0.067971 | -0.0042041 | 0.00025206 | -0.013123 | -0.0053385 | 0.063553 | 0.064619 | -0.20468 | -0.0024118 | 121.3531 | -0.073242 | 10.5698 | -0.068665 | 121.3165 | -0.13275 | -0.1831 | -0.086975 | 9.3842 | -0.1831 | 121.225 | 121.4218 | -0.086975 | -0.10529 | 0.091553 | 0.041199 | -0.07782 | 0.15106 | 0.15564 | 0.11444 | -0.041199 | 0.13733 | 0.11902 | -0.16937 | 0.13733 | 0.041199 | -0.077819 | 0.027466 | 121.5408 | 121.5775 | 10.7941 | -121.5775 | 121.4493 | 121.6461 | 9.6085 | -121.4996
1359.5469 | 121.6599 | -0.24261 | 121.4172 | -0.012589 | 0.0087137 | 0.063692 | -0.00024778 | 0.066689 | 0.0039135 | 0.00046566 | -0.0054932 | -0.0025613 | 0.066544 | 0.066969 | -0.20083 | -0.006257 | 121.3806 | -0.11444 | 10.6155 | -0.073242 | 121.3303 | -0.16022 | -0.21973 | -0.091553 | 9.4208 | -0.26093 | 121.3028 | 121.4218 | -0.10529 | -0.13275 | 0.082398 | 0.022888 | -0.086975 | 0.12817 | 0.16937 | 0.14649 | -0.036621 | 0.13733 | 0.10986 | -0.11444 | 0.15106 | -0.01831 | -0.12817 | 0.004578 | 121.5729 | 121.6232 | 10.8582 | -121.637 | 121.5454 | 121.6644 | 9.6634 | -121.55
1361.3125 | 121.6965 | -0.25177 | 121.4081 | -0.0049592 | 0.0031595 | 0.064546 | 0.0012476 | 0.065834 | 0.0013501 | 0.0026019 | -0.0054932 | -0.0027749 | 0.064835 | 0.069319 | -0.1987 | -0.0041208 | 121.3165 | -0.16479 | 10.5515 | -0.12817 | 121.3577 | -0.15106 | -0.20599 | -0.15564 | 9.2972 | -0.32044 | 121.2982 | 121.4081 | -0.11902 | -0.15106 | 0.10071 | 0.045776 | -0.050354 | 0.086975 | 0.1236 | 0.07782 | -0.091553 | 0.13275 | 0.10071 | -0.10986 | 0.09613 | -0.068665 | -0.16937 | 0 | 121.6095 | 121.5683 | 10.8032 | -121.6141 | 121.55 | 121.6599 | 9.549 | -121.5591
1363.0938 | 121.6461 | -0.2655 | 121.4355 | -0.012589 | 0.0035867 | 0.065187 | 0.0035974 | 0.065621 | -0.0024951 | 3.8456e-05 | -0.0054932 | -0.0036295 | 0.066544 | 0.067823 | -0.20169 | -0.0036936 | 121.3074 | -0.13733 | 10.675 | -0.1236 | 121.3303 | -0.16022 | -0.2243 | -0.15564 | 9.3933 | -0.28839 | 121.2753 | 121.4401 | -0.11902 | -0.15564 | 0.10529 | 0.041199 | -0.10529 | 0.12817 | 0.14191 | 0.10071 | -0.12817 | 0.14648 | 0.10986 | -0.16022 | 0.10986 | -0.022888 | -0.13275 | 0.004578 | 121.5958 | 121.5729 | 10.9406 | -121.6599 | 121.5408 | 121.7056 | 9.6588 | -121.5912
1364.8594 | 121.6187 | -0.25635 | 121.431 | 0.0026703 | 0.0033731 | 0.067323 | 0.00082022 | 0.065834 | 0.0026319 | 0.0028155 | -0.0054932 | 0.00064308 | 0.063766 | 0.068678 | -0.19763 | -0.0036936 | 121.3669 | -0.10071 | 10.7483 | -0.086975 | 121.3577 | -0.13275 | -0.2243 | -0.12817 | 9.462 | -0.29755 | 121.2662 | 121.4218 | -0.10529 | -0.13275 | 0.1236 | 0.032044 | -0.073242 | 0.15564 | 0.16937 | 0.13733 | -0.064087 | 0.15106 | 0.1236 | -0.16479 | 0.12817 | -0.041198 | -0.16479 | -0.009155 | 121.6141 | 121.6232 | 11.0046 | -121.6553 | 121.5225 | 121.6782 | 9.7183 | -121.5637
1366.5781 | 121.6873 | -0.23804 | 121.4081 | -0.012589 | 0.0031595 | 0.066896 | 0.0031702 | 0.068184 | -0.0042041 | -0.0016705 | -0.013123 | -0.0066201 | 0.065903 | 0.066328 | -0.20404 | -0.0024118 | 121.3898 | -0.013733 | 10.8856 | -0.050354 | 121.2708 | -0.14191 | -0.18768 | -0.068665 | 9.5856 | -0.1831 | 121.2387 | 121.4081 | -0.068665 | -0.10071 | 0.09613 | 0.050354 | -0.13733 | 0.2243 | 0.18768 | 0.13733 | -0.01831 | 0.16937 | 0.13733 | -0.16937 | 0.16937 | 0.054932 | -0.082397 | 0 | 121.5088 | 121.6278 | 11.1237 | -121.5958 | 121.4767 | 121.6461 | 9.8236 | -121.5088
1368.3438 | 121.7422 | -0.20599 | 121.3898 | -0.0049592 | 0.0018777 | 0.064333 | -0.00067498 | 0.066902 | 0.00092287 | 0.0017475 | -0.0054932 | -0.0023477 | 0.064194 | 0.067823 | -0.19934 | -0.0024118 | 121.3577 | -0.09613 | 10.8032 | -0.07782 | 121.3074 | -0.1236 | -0.18768 | -0.082397 | 9.5078 | -0.21057 | 121.2524 | 121.376 | -0.073242 | -0.11444 | 0.082398 | 0.018311 | -0.082398 | 0.10986 | 0.12817 | 0.10986 | -0.032044 | 0.13275 | 0.091553 | -0.13733 | 0.1236 | -0.004577 | -0.09613 | -0.013733 | 121.5134 | 121.5637 | 11.0092 | -121.5775 | 121.4584 | 121.582 | 9.7137 | -121.5042
1370.1094 | 121.6736 | -0.24261 | 121.4401 | -0.012589 | 0.0070047 | 0.065828 | 0.0025292 | 0.063484 | 0.00070927 | -0.00038874 | -0.0054932 | -0.0012795 | 0.066757 | 0.066755 | -0.19934 | -0.0021982 | 121.3165 | -0.16022 | 10.8444 | -0.13733 | 121.3669 | -0.16937 | -0.21515 | -0.15564 | 9.5352 | -0.3067 | 121.2845 | 121.4493 | -0.10529 | -0.14191 | 0.073242 | 0.027466 | -0.073243 | 0.082398 | 0.10529 | 0.07782 | -0.1236 | 0.13733 | 0.10071 | -0.15564 | 0.086975 | -0.064087 | -0.16479 | 0.009155 | 121.6095 | 121.5591 | 11.087 | -121.6553 | 121.5271 | 121.6919 | 9.7778 | -121.582
1371.875 | 121.7148 | -0.23804 | 121.3989 | 0.0026703 | -0.0019675 | 0.068178 | 0.00082022 | 0.066048 | -0.0033495 | 0.0013203 | -0.0054932 | -0.0068337 | 0.06398 | 0.065901 | -0.20062 | -0.00113 | 121.3669 | -0.059509 | 10.9177 | -0.082397 | 121.2982 | -0.10986 | -0.1831 | -0.10986 | 9.5444 | -0.23346 | 121.2479 | 121.4172 | -0.064087 | -0.11444 | 0.12817 | 0.054932 | -0.10071 | 0.17853 | 0.15564 | 0.10071 | -0.032044 | 0.17395 | 0.1236 | -0.15106 | 0.12817 | 0.004578 | -0.11902 | 0.01831 | 121.5363 | 121.6049 | 11.1557 | -121.582 | 121.4859 | 121.6553 | 9.7824 | -121.5134
1373.5781 | 121.7514 | -0.21515 | 121.3989 | 0.0026703 | 0.00080973 | 0.066896 | 0.0027428 | 0.066902 | -0.0059131 | -0.00017514 | -0.0054932 | -0.0068337 | 0.062271 | 0.064619 | -0.20169 | -0.0034798 | 121.4035 | -0.018311 | 11.0321 | -0.041199 | 121.3028 | -0.11444 | -0.19226 | -0.059509 | 9.6817 | -0.14191 | 121.2387 | 121.3989 | -0.064087 | -0.11444 | 0.10071 | 0.022888 | -0.096131 | 0.19684 | 0.17395 | 0.15106 | 0.004577 | 0.15106 | 0.10071 | -0.16022 | 0.15564 | 0.073242 | -0.027466 | 0 | 121.5179 | 121.6187 | 11.2473 | -121.5912 | 121.4539 | 121.6141 | 9.8969 | -121.5134
1375.2812 | 121.6873 | -0.24719 | 121.4264 | 0.0026703 | 0.0020913 | 0.064546 | 0.00039302 | 0.066048 | 0.0034863 | -0.00038874 | -0.013123 | -0.0019205 | 0.064407 | 0.068678 | -0.20169 | -0.0039072 | 121.3348 | -0.19684 | 10.9131 | -0.12817 | 121.344 | -0.16479 | -0.2243 | -0.14648 | 9.5352 | -0.31128 | 121.2845 | 121.463 | -0.10071 | -0.13275 | 0.082397 | 0.022888 | -0.082398 | 0.050354 | 0.11902 | 0.09613 | -0.091553 | 0.14648 | 0.11444 | -0.14191 | 0.10071 | -0.064087 | -0.17853 | 0.036621 | 121.5912 | 121.582 | 11.1603 | -121.6507 | 121.5317 | 121.7102 | 9.7824 | -121.5591
1377 | 121.7056 | -0.20142 | 121.431 | 0.0103 | 0.0040139 | 0.06476 | 0.00082022 | 0.065834 | -0.0035633 | 0.0019611 | -0.013123 | -0.0046975 | 0.06398 | 0.067823 | -0.20105 | -0.0036936 | 121.4218 | -0.013733 | 11.0825 | -0.045776 | 121.3028 | -0.10986 | -0.1831 | -0.036621 | 9.6725 | -0.17395 | 121.2479 | 121.3852 | -0.064087 | -0.091553 | 0.091553 | 0.018311 | -0.12817 | 0.18768 | 0.15564 | 0.13733 | -0.009155 | 0.13733 | 0.10986 | -0.1831 | 0.1648 | 0.027466 | -0.082397 | -0.045776 | 121.5042 | 121.6232 | 11.2839 | -121.6141 | 121.4493 | 121.5866 | 9.874 | -121.5225
1378.7656 | 121.7239 | -0.2243 | 121.4218 | 0.0026703 | 0.0025185 | 0.066683 | -0.0011024 | 0.068611 | 0.0041273 | 0.0030293 | -0.013123 | -0.0017069 | 0.064835 | 0.067396 | -0.19827 | -0.0036936 | 121.3394 | -0.16937 | 11.0138 | -0.13275 | 121.3486 | -0.14648 | -0.2243 | -0.14648 | 9.5947 | -0.31128 | 121.2936 | 121.431 | -0.11902 | -0.14648 | 0.07782 | 0 | -0.073242 | 0.054931 | 0.091553 | 0.091553 | -0.082397 | 0.10529 | 0.07782 | -0.12817 | 0.07782 | -0.086975 | -0.16479 | 0.009155 | 121.5729 | 121.5637 | 11.2381 | -121.6461 | 121.5179 | 121.6553 | 9.819 | -121.5683
1380.4688 | 121.6095 | -0.25635 | 121.4539 | -0.0049592 | 0.0046549 | 0.065187 | -0.00024778 | 0.065407 | 0.0015637 | 0.0043109 | -0.0054932 | -0.0019205 | 0.065048 | 0.068678 | -0.19763 | -0.0043344 | 121.3898 | -0.10986 | 11.1511 | -0.10071 | 121.3623 | -0.13275 | -0.21515 | -0.11444 | 9.6771 | -0.3067 | 121.2982 | 121.4539 | -0.10986 | -0.14191 | 0.1236 | 0.041199 | -0.091552 | 0.14649 | 0.15564 | 0.11444 | -0.064086 | 0.14649 | 0.11444 | -0.15564 | 0.14191 | -0.050354 | -0.16479 | 0 | 121.6187 | 121.6461 | 11.4075 | -121.669 | 121.5546 | 121.7102 | 9.9335 | -121.5958
1382.2344 | 121.6324 | -0.24719 | 121.4081 | -0.0049592 | 0.0052957 | 0.063905 | 0.00082022 | 0.066475 | 0.0022047 | 0.0045245 | -0.013123 | -0.00042512 | 0.065262 | 0.069105 | -0.19763 | -0.002839 | 121.3898 | -0.07782 | 11.2335 | -0.082397 | 121.3303 | -0.13275 | -0.20142 | -0.082397 | 9.7778 | -0.27008 | 121.2662 | 121.4447 | -0.086975 | -0.12817 | 0.11444 | 0.045776 | -0.07782 | 0.16937 | 0.16479 | 0.11902 | -0.01831 | 0.16022 | 0.11902 | -0.14191 | 0.16479 | -0.022889 | -0.14191 | 0.036621 | 121.5775 | 121.637 | 11.4807 | -121.6095 | 121.5134 | 121.6919 | 10.025 | -121.5363
1383.9844 | 121.637 | -0.2655 | 121.4401 | 0.0026703 | 0.0038003 | 0.064974 | 0.00082022 | 0.068825 | 0.0011365 | 0.00025206 | -0.0054932 | -0.0017069 | 0.067398 | 0.068464 | -0.19912 | -0.00091641 | 121.2982 | -0.18768 | 11.1832 | -0.13275 | 121.3806 | -0.14648 | -0.2243 | -0.16937 | 9.6954 | -0.32501 | 121.2982 | 121.4447 | -0.10529 | -0.13733 | 0.11902 | 0.041199 | -0.05951 | 0.07782 | 0.13275 | 0.091553 | -0.14191 | 0.16022 | 0.12817 | -0.14191 | 0.09613 | -0.059509 | -0.18768 | 0.004577 | 121.6461 | 121.5637 | 11.4487 | -121.6644 | 121.5637 | 121.7102 | 9.9609 | -121.5775
1385.75 | 121.6644 | -0.25635 | 121.4401 | 0.0026703 | 0.0033731 | 0.064546 | 0.00060662 | 0.065193 | -0.0022815 | 0.0030293 | 0.0021363 | -0.0032021 | 0.06398 | 0.068464 | -0.19998 | -0.0013436 | 121.2799 | -0.1831 | 11.2244 | -0.12817 | 121.3623 | -0.15106 | -0.2243 | -0.16022 | 9.7 | -0.31586 | 121.312 | 121.4539 | -0.10071 | -0.14191 | 0.10529 | 0.032044 | -0.07782 | 0.073243 | 0.12817 | 0.09613 | -0.16022 | 0.15564 | 0.11444 | -0.12817 | 0.096131 | -0.059509 | -0.17395 | 0.013732 | 121.6187 | 121.5363 | 11.4807 | -121.6644 | 121.5683 | 121.7102 | 9.9564 | -121.582
1387.5156 | 121.7651 | -0.19684 | 121.3852 | -0.012589 | 0.0050821 | 0.066042 | 0.00082022 | 0.066475 | -0.0018543 | 0.0023883 | 0.0021363 | -0.0038431 | 0.064194 | 0.066328 | -0.20212 | -6.2012e-05 | 121.4172 | -0.050354 | 11.3525 | -0.041199 | 121.3028 | -0.10986 | -0.1831 | -0.041199 | 9.8099 | -0.16479 | 121.2433 | 121.4172 | -0.068665 | -0.10529 | 0.086975 | 0.013733 | -0.082398 | 0.14648 | 0.15564 | 0.14191 | 0.032043 | 0.12817 | 0.091552 | -0.14191 | 0.15564 | 0.032043 | -0.059509 | 0.032043 | 121.4996 | 121.6141 | 11.5494 | -121.5683 | 121.4401 | 121.6141 | 10.0067 | -121.4905
1389.2812 | 121.6644 | -0.22888 | 121.4447 | 0.0026703 | 0.0076455 | 0.06476 | 0.0027428 | 0.06733 | 0.0017773 | 0.0026019 | 0.0097658 | -0.0021341 | 0.064407 | 0.069959 | -0.20105 | -0.0034798 | 121.3715 | -0.11444 | 11.4166 | -0.082397 | 121.3486 | -0.13275 | -0.21057 | -0.09613 | 9.8557 | -0.25177 | 121.2936 | 121.4539 | -0.10071 | -0.13733 | 0.096131 | 0.018311 | -0.09613 | 0.11444 | 0.14649 | 0.12817 | -0.073242 | 0.12817 | 0.091553 | -0.15106 | 0.13275 | -0.022888 | -0.11444 | 0.009155 | 121.5775 | 121.6003 | 11.6455 | -121.6553 | 121.5225 | 121.6827 | 10.0845 | -121.582
1391.0625 | 121.701 | -0.23346 | 121.4172 | -0.012589 | 0.0061501 | 0.066896 | -0.0015296 | 0.064125 | -0.00099973 | 0.0017475 | -0.0054932 | -0.0017069 | 0.064194 | 0.068678 | -0.19891 | -0.0032662 | 121.3257 | -0.1831 | 11.3709 | -0.12817 | 121.344 | -0.14191 | -0.20599 | -0.15106 | 9.7733 | -0.29755 | 121.3074 | 121.4813 | -0.091553 | -0.13275 | 0.091552 | 0.027465 | -0.073242 | 0.050354 | 0.10528 | 0.07782 | -0.091552 | 0.14191 | 0.10071 | -0.10986 | 0.082397 | -0.064087 | -0.16479 | 0.064087 | 121.5775 | 121.5591 | 11.6043 | -121.6232 | 121.5408 | 121.7148 | 10.0067 | -121.55
1392.8438 | 121.6324 | -0.24261 | 121.431 | -0.012589 | 0.0038003 | 0.063905 | 0.00039302 | 0.065834 | 0.0017773 | 0.0023883 | -0.0054932 | -0.0027749 | 0.065262 | 0.068464 | -0.19912 | -0.0039072 | 121.3577 | -0.091553 | 11.5128 | -0.07782 | 121.3577 | -0.15106 | -0.21973 | -0.082397 | 9.9289 | -0.24719 | 121.2708 | 121.4493 | -0.10071 | -0.14191 | 0.091553 | 0.022888 | -0.073242 | 0.15106 | 0.16479 | 0.14191 | -0.073242 | 0.14191 | 0.10071 | -0.16022 | 0.16022 | -0.004577 | -0.10528 | 0.018311 | 121.6003 | 121.6003 | 11.7554 | -121.6507 | 121.5134 | 121.6919 | 10.1715 | -121.5729
1394.5469 | 121.6415 | -0.2655 | 121.4539 | 0.0026703 | 0.0065775 | 0.065187 | 0.0061608 | 0.068825 | -0.0039905 | -0.0014569 | -0.013123 | -0.0038431 | 0.066971 | 0.06761 | -0.20489 | -0.00091641 | 121.3028 | -0.14648 | 11.5448 | -0.13275 | 121.3531 | -0.14191 | -0.23804 | -0.18768 | 9.8969 | -0.31128 | 121.2936 | 121.4859 | -0.11902 | -0.13275 | 0.1236 | 0.027466 | -0.10071 | 0.11902 | 0.13275 | 0.10529 | -0.15106 | 0.14648 | 0.13275 | -0.16022 | 0.07782 | -0.045776 | -0.17853 | 0.032044 | 121.6187 | 121.5683 | 11.8103 | -121.6919 | 121.5591 | 121.7514 | 10.1624 | -121.5866
1396.3125 | 121.7606 | -0.19684 | 121.3989 | 0.0026703 | 0.0020913 | 0.065401 | 0.00039302 | 0.065193 | -0.0082629 | -0.00038874 | -0.020752 | -0.0070475 | 0.064835 | 0.066755 | -0.20404 | -6.2012e-05 | 121.3989 | 0 | 11.6821 | -0.036621 | 121.2982 | -0.10986 | -0.19226 | -0.054932 | 10.0388 | -0.15106 | 121.2158 | 121.431 | -0.068665 | -0.11902 | 0.086975 | 0.004577 | -0.10071 | 0.19684 | 0.16022 | 0.15564 | 0 | 0.12817 | 0.077819 | -0.18311 | 0.14191 | 0.045776 | -0.032043 | 0.032043 | 121.4951 | 121.5958 | 11.879 | -121.5912 | 121.4127 | 121.6278 | 10.2356 | -121.5179
1398.0781 | 121.6965 | -0.23804 | 121.431 | -0.0049592 | 0.010423 | 0.064974 | 0.0012476 | 0.068611 | 0.0034863 | -0.00017514 | -0.0054932 | -0.0014933 | 0.065262 | 0.069319 | -0.19977 | -0.0036936 | 121.3715 | -0.12817 | 11.6501 | -0.082397 | 121.3715 | -0.14648 | -0.22888 | -0.11444 | 9.9838 | -0.25635 | 121.3074 | 121.4676 | -0.10986 | -0.13275 | 0.091553 | 0.009155 | -0.059509 | 0.10986 | 0.15564 | 0.14649 | -0.059509 | 0.12817 | 0.10529 | -0.1236 | 0.1236 | -0.018311 | -0.1236 | 0.036621 | 121.6095 | 121.6095 | 11.8881 | -121.6599 | 121.5454 | 121.7056 | 10.2219 | -121.5637
1399.8438 | 121.7422 | -0.20142 | 121.4035 | -0.0049592 | 0.0027323 | 0.063478 | -0.001316 | 0.063698 | -0.0044177 | 0.00025206 | -0.0054932 | -0.0061929 | 0.063553 | 0.066328 | -0.20019 | -0.001771 | 121.4264 | -0.022888 | 11.7279 | -0.027466 | 121.3028 | -0.10529 | -0.1831 | -0.045776 | 10.0296 | -0.17853 | 121.257 | 121.4218 | -0.059509 | -0.10529 | 0.09613 | 0.018311 | -0.10071 | 0.17853 | 0.17395 | 0.15564 | 0.022889 | 0.14191 | 0.09613 | -0.14648 | 0.15564 | 0.022888 | -0.073242 | 0.018311 | 121.5042 | 121.6278 | 11.9293 | -121.5866 | 121.4584 | 121.6232 | 10.231 | -121.5088
1401.5469 | 121.6736 | -0.24261 | 121.4127 | -0.0049592 | 0.0093545 | 0.063905 | 0.0027428 | 0.066689 | 0.0011365 | -0.00017514 | -0.0054932 | -0.0017069 | 0.066116 | 0.069746 | -0.20019 | -0.0039072 | 121.3669 | -0.10986 | 11.7828 | -0.073242 | 121.3577 | -0.13733 | -0.21057 | -0.09613 | 10.0754 | -0.24719 | 121.2936 | 121.4676 | -0.10071 | -0.1236 | 0.10529 | 0.032044 | -0.054932 | 0.13275 | 0.16937 | 0.13733 | -0.045777 | 0.14191 | 0.11902 | -0.11902 | 0.14649 | -0.004577 | -0.1236 | 0.054931 | 121.6003 | 121.6095 | 12.0255 | -121.6232 | 121.5363 | 121.7102 | 10.318 | -121.5363
1403.3125 | 121.6324 | -0.25177 | 121.4127 | -0.012589 | 0.0052957 | 0.066255 | 0.0016748 | 0.064553 | -0.0052721 | -0.00017514 | -0.0054932 | -0.0059793 | 0.065689 | 0.067823 | -0.2019 | -0.0032662 | 121.3715 | -0.032043 | 11.8881 | -0.045776 | 121.3074 | -0.13733 | -0.19684 | -0.10071 | 10.1074 | -0.23804 | 121.2845 | 121.4401 | -0.082397 | -0.1236 | 0.11444 | 0.054932 | -0.10529 | 0.21973 | 0.20599 | 0.15106 | -0.041199 | 0.16937 | 0.12817 | -0.12817 | 0.15106 | 0.013733 | -0.11444 | 0.027466 | 121.5591 | 121.6232 | 12.1399 | -121.6095 | 121.5363 | 121.6919 | 10.3592 | -121.5363
1405.0156 | 121.6873 | -0.24261 | 121.4584 | 0.0026703 | 0.0057229 | 0.066042 | 0.0023156 | 0.064766 | -0.0018543 | 0.00046566 | -0.0054932 | -0.00085232 | 0.065262 | 0.068678 | -0.2019 | -0.0030526 | 121.3211 | -0.16022 | 11.8378 | -0.11444 | 121.3486 | -0.16022 | -0.21057 | -0.15564 | 10.0616 | -0.30212 | 121.3074 | 121.4767 | -0.1236 | -0.15564 | 0.082398 | 0.032044 | -0.10986 | 0.082398 | 0.12817 | 0.09613 | -0.13733 | 0.11902 | 0.086975 | -0.15106 | 0.086975 | -0.059509 | -0.14648 | 0.018311 | 121.5912 | 121.5637 | 12.0804 | -121.669 | 121.55 | 121.7194 | 10.3043 | -121.6141
1406.7812 | 121.6232 | -0.2655 | 121.4539 | -0.012589 | 0.0061501 | 0.063905 | -0.00067498 | 0.065834 | 0.0022047 | 0.0043109 | -0.0054932 | 0.00021568 | 0.065048 | 0.068891 | -0.19827 | -0.0049752 | 121.3806 | -0.10529 | 11.9019 | -0.09613 | 121.3486 | -0.13733 | -0.21973 | -0.12817 | 10.0891 | -0.30212 | 121.2936 | 121.4859 | -0.11444 | -0.1236 | 0.12817 | 0.045776 | -0.10528 | 0.16022 | 0.16937 | 0.1236 | -0.073242 | 0.15106 | 0.14191 | -0.16022 | 0.13733 | -0.036621 | -0.17853 | 0.032044 | 121.6141 | 121.6461 | 12.1674 | -121.6736 | 121.5591 | 121.7514 | 10.3546 | -121.5775
1408.5469 | 121.7148 | -0.21973 | 121.4127 | 0.0026703 | -0.0015403 | 0.066896 | 0.0016748 | 0.066262 | -0.0048449 | -0.0012433 | -0.0054932 | -0.0072611 | 0.062271 | 0.066755 | -0.2019 | -0.001771 | 121.3531 | -0.059509 | 11.9568 | -0.073242 | 121.3074 | -0.11444 | -0.17853 | -0.10986 | 10.1349 | -0.21973 | 121.257 | 121.4218 | -0.07782 | -0.10986 | 0.10529 | 0.041199 | -0.10529 | 0.16022 | 0.14649 | 0.10529 | -0.05951 | 0.14191 | 0.10986 | -0.15564 | 0.10986 | 0 | -0.10986 | 0.009155 | 121.5271 | 121.5729 | 12.1765 | -121.5912 | 121.4767 | 121.6415 | 10.3546 | -121.5225
1410.2656 | 121.7651 | -0.21973 | 121.4218 | -0.0049592 | 0.0023049 | 0.066896 | 0.00082022 | 0.06498 | -0.0056995 | -0.00060234 | -0.0054932 | -0.0070475 | 0.06163 | 0.06526 | -0.20318 | -0.0024118 | 121.3943 | -0.027466 | 12.0758 | -0.050354 | 121.2982 | -0.12817 | -0.17853 | -0.059509 | 10.2951 | -0.15106 | 121.2433 | 121.4127 | -0.064087 | -0.09613 | 0.091553 | 0.041199 | -0.1236 | 0.19226 | 0.16937 | 0.12817 | -0.027466 | 0.15564 | 0.1236 | -0.17853 | 0.16022 | 0.068665 | -0.054932 | -0.009155 | 121.5179 | 121.6141 | 12.2955 | -121.6003 | 121.463 | 121.6324 | 10.5148 | -121.5179
1412.0312 | 121.7697 | -0.19684 | 121.3852 | -0.012589 | 0.0010233 | 0.065187 | -0.0011024 | 0.067757 | 0.0032727 | -0.00017514 | -0.0054932 | -0.0023477 | 0.063553 | 0.068037 | -0.19613 | -0.0051888 | 121.3623 | -0.10529 | 12.0392 | -0.09613 | 121.3394 | -0.13733 | -0.18768 | -0.07782 | 10.2219 | -0.22888 | 121.2753 | 121.4355 | -0.073242 | -0.11902 | 0.059509 | 0.009155 | -0.045776 | 0.091552 | 0.10071 | 0.091553 | -0.022888 | 0.1236 | 0.077819 | -0.10986 | 0.11902 | -0.032044 | -0.10986 | 0.050354 | 121.5363 | 121.5591 | 12.236 | -121.5729 | 121.4722 | 121.6324 | 10.4187 | -121.5042
1413.7344 | 121.6736 | -0.26093 | 121.4081 | -0.020218 | 0.0046549 | 0.065187 | 0.0031702 | 0.063484 | 0.00092287 | -0.0018841 | -0.0054932 | -0.0025613 | 0.066116 | 0.067823 | -0.20169 | -0.0024118 | 121.3165 | -0.15564 | 12.1124 | -0.11902 | 121.3669 | -0.15564 | -0.23804 | -0.15106 | 10.2631 | -0.3067 | 121.3028 | 121.431 | -0.10071 | -0.16937 | 0.10529 | 0.022888 | -0.041199 | 0.10529 | 0.14191 | 0.11902 | -0.091553 | 0.16022 | 0.091552 | -0.10529 | 0.10986 | -0.045777 | -0.13733 | 0.022888 | 121.6278 | 121.5775 | 12.3734 | -121.6461 | 121.5637 | 121.6919 | 10.524 | -121.5775
1415.5 | 121.7697 | -0.20142 | 121.376 | -0.012589 | 0.0033731 | 0.066469 | 0.0027428 | 0.066689 | -0.0063403 | 0.0017475 | -0.0054932 | -0.0068337 | 0.065048 | 0.068678 | -0.20425 | -0.0030526 | 121.3898 | -0.032043 | 12.2406 | -0.050354 | 121.3028 | -0.1236 | -0.19226 | -0.064087 | 10.3683 | -0.15564 | 121.2341 | 121.431 | -0.064087 | -0.1236 | 0.07782 | 0.009155 | -0.073243 | 0.16937 | 0.15106 | 0.14191 | 0.013733 | 0.13733 | 0.07782 | -0.14191 | 0.13733 | 0.045776 | -0.032044 | 0.054931 | 121.5042 | 121.5912 | 12.442 | -121.5683 | 121.4355 | 121.6324 | 10.5698 | -121.4996
1417.2188 | 121.7514 | -0.21515 | 121.4035 | -0.0049592 | -0.00089927 | 0.065614 | -0.0025976 | 0.067757 | 0.0022047 | 0.0021747 | -0.0054932 | -0.0044839 | 0.065048 | 0.066969 | -0.19763 | -0.0039072 | 121.431 | -0.032043 | 12.2498 | -0.036621 | 121.3257 | -0.12817 | -0.1831 | -0.027466 | 10.3683 | -0.18768 | 121.2524 | 121.4081 | -0.059509 | -0.091553 | 0.086975 | 0.032044 | -0.077819 | 0.18311 | 0.17853 | 0.14648 | 0.027466 | 0.15564 | 0.1236 | -0.15106 | 0.18768 | 0.027466 | -0.09613 | 0.004578 | 121.5408 | 121.6461 | 12.4649 | -121.5866 | 121.4676 | 121.6232 | 10.5835 | -121.4951
1418.9844 | 121.7285 | -0.21973 | 121.4355 | 0.0026703 | 0.0025185 | 0.065401 | 0.0014612 | 0.065834 | 0.0041273 | 0.00025206 | 0.0021363 | -0.0017069 | 0.065262 | 0.069319 | -0.19955 | -0.0032662 | 121.3348 | -0.15564 | 12.2177 | -0.12817 | 121.3669 | -0.15564 | -0.21515 | -0.13275 | 10.2859 | -0.31586 | 121.2982 | 121.4355 | -0.11902 | -0.11902 | 0.064087 | 0.004578 | -0.068665 | 0.064087 | 0.091553 | 0.086975 | -0.10071 | 0.10071 | 0.10071 | -0.13733 | 0.086976 | -0.09613 | -0.19684 | 0 | 121.5866 | 121.5546 | 12.4374 | -121.6507 | 121.5179 | 121.6553 | 10.5057 | -121.5546
1420.6875 | 121.6553 | -0.24719 | 121.4172 | -0.012589 | 0.0040139 | 0.063265 | -0.00067498 | 0.067757 | 0.0039135 | 0.0013203 | -0.020752 | -0.0040567 | 0.064621 | 0.06761 | -0.19934 | -0.0036936 | 121.376 | -0.07782 | 12.3688 | -0.091553 | 121.3577 | -0.16022 | -0.21057 | -0.07782 | 10.4691 | -0.26093 | 121.2936 | 121.463 | -0.10071 | -0.13275 | 0.086975 | 0.036621 | -0.059509 | 0.16937 | 0.15564 | 0.11902 | -0.041198 | 0.14648 | 0.11444 | -0.1236 | 0.16937 | -0.013733 | -0.12817 | 0.045777 | 121.6049 | 121.6232 | 12.616 | -121.6278 | 121.5408 | 121.7102 | 10.7162 | -121.55
1422.7344 | 121.7926 | -0.19684 | 121.3852 | 0.0026703 | 0.0012369 | 0.065401 | 0.0053064 | 0.066262 | -0.0052721 | 0.00025206 | -0.013123 | -0.0066201 | 0.06633 | 0.066328 | -0.20404 | -0.0030526 | 121.3669 | -0.036621 | 12.4558 | -0.073242 | 121.3074 | -0.12817 | -0.19226 | -0.068665 | 10.5057 | -0.16937 | 121.2433 | 121.431 | -0.086975 | -0.11444 | 0.068664 | 0.004577 | -0.07782 | 0.16022 | 0.1236 | 0.11902 | -0.018311 | 0.10986 | 0.082397 | -0.14191 | 0.12817 | 0.027465 | -0.054932 | 0.045776 | 121.5042 | 121.5637 | 12.6526 | -121.5775 | 121.4401 | 121.6278 | 10.7025 | -121.4996
1426.4531 | 121.6736 | -0.23804 | 121.431 | -0.0049592 | 0.0033731 | 0.065187 | -0.00088858 | 0.067971 | 0.0022047 | 0.0011067 | -0.013123 | -0.0021341 | 0.062485 | 0.06825 | -0.20105 | -0.0041208 | 121.3531 | -0.13275 | 12.5244 | -0.10986 | 121.3486 | -0.15106 | -0.24719 | -0.10986 | 10.5148 | -0.27466 | 121.312 | 121.4539 | -0.10529 | -0.15106 | 0.086975 | -0.009155 | -0.082397 | 0.10529 | 0.12817 | 0.13733 | -0.07782 | 0.13275 | 0.086975 | -0.11902 | 0.12817 | -0.036621 | -0.1236 | 0.022888 | 121.5866 | 121.5912 | 12.7625 | -121.6782 | 121.55 | 121.6919 | 10.7529 | -121.582
1430.0938 | 121.7194 | -0.21515 | 121.3989 | -0.0049592 | 0.00038233 | 0.064974 | 0.00039302 | 0.066475 | -0.00099973 | 0.00046566 | -0.013123 | -0.0059793 | 0.062485 | 0.067823 | -0.20019 | -0.0034798 | 121.4218 | -0.013733 | 12.6984 | -0.041199 | 121.3165 | -0.10071 | -0.16022 | -0.027466 | 10.6155 | -0.16479 | 121.2204 | 121.3943 | -0.064087 | -0.082397 | 0.11444 | 0.054932 | -0.082398 | 0.20142 | 0.17395 | 0.11902 | 0.022888 | 0.15106 | 0.13275 | -0.17853 | 0.18768 | 0.050354 | -0.082398 | -0.004578 | 121.5317 | 121.637 | 12.9135 | -121.5591 | 121.4355 | 121.6095 | 10.8307 | -121.4813
1435.9375 | 121.7697 | -0.21515 | 121.4081 | -0.012589 | 0.0020913 | 0.064546 | 0.0014612 | 0.06498 | -0.0050585 | -0.0012433 | -0.0054932 | -0.0061929 | 0.063553 | 0.066542 | -0.20382 | -0.0026254 | 121.4035 | -0.009155 | 12.9272 | -0.045776 | 121.344 | -0.09613 | -0.17395 | -0.064087 | 10.73 | -0.15564 | 121.2708 | 121.4493 | -0.073242 | -0.09613 | 0.11902 | 0.041199 | -0.064087 | 0.20599 | 0.16937 | 0.12817 | -0.004578 | 0.14191 | 0.11902 | -0.13733 | 0.15106 | 0.059509 | -0.05951 | 0.041199 | 121.5591 | 121.6187 | 13.1424 | -121.582 | 121.4859 | 121.6644 | 10.9451 | -121.5042
1437.7031 | 121.6736 | -0.23346 | 121.4355 | -0.012589 | 0.0063639 | 0.064974 | 0.0025292 | 0.065621 | 0.0017773 | -0.00038874 | -0.0054932 | -0.0032021 | 0.066544 | 0.068037 | -0.20212 | -0.0047616 | 121.3257 | -0.13733 | 12.9135 | -0.10986 | 121.3394 | -0.15564 | -0.23804 | -0.14191 | 10.6888 | -0.29755 | 121.3074 | 121.431 | -0.09613 | -0.1236 | 0.077819 | -0.004578 | -0.09613 | 0.09613 | 0.1236 | 0.12817 | -0.10986 | 0.13733 | 0.10986 | -0.12817 | 0.091552 | -0.064087 | -0.17395 | -0.004578 | 121.5729 | 121.5591 | 13.147 | -121.6736 | 121.5408 | 121.6644 | 10.9222 | -121.5591
1439.4688 | 121.6644 | -0.24719 | 121.4355 | -0.0049592 | 0.0076455 | 0.066469 | 0.003811 | 0.068398 | -0.00099973 | 0.00089286 | -0.0054932 | -0.0042703 | 0.06398 | 0.067823 | -0.20212 | -0.00113 | 121.344 | -0.09613 | 12.9959 | -0.11444 | 121.3394 | -0.15106 | -0.22888 | -0.15106 | 10.7254 | -0.28381 | 121.2891 | 121.4584 | -0.10986 | -0.14648 | 0.09613 | 0.01831 | -0.09613 | 0.15106 | 0.13275 | 0.11444 | -0.091553 | 0.13733 | 0.10071 | -0.14648 | 0.09613 | -0.036621 | -0.13733 | 0.022888 | 121.5866 | 121.5912 | 13.2431 | -121.6644 | 121.5363 | 121.7056 | 10.9726 | -121.582
1441.1719 | 121.637 | -0.25177 | 121.4722 | -0.012589 | 0.0050821 | 0.066683 | 0.002102 | 0.067543 | -0.0016405 | -0.0016705 | 0.0021363 | -0.0053385 | 0.066757 | 0.065473 | -0.2034 | -0.0039072 | 121.376 | -0.022888 | 13.1195 | -0.054932 | 121.3348 | -0.12817 | -0.20142 | -0.10529 | 10.762 | -0.24261 | 121.2845 | 121.431 | -0.086975 | -0.15564 | 0.1236 | 0.050354 | -0.13733 | 0.22888 | 0.19684 | 0.14648 | -0.09613 | 0.16479 | 0.09613 | -0.18768 | 0.14648 | 0.009155 | -0.086975 | -0.041199 | 121.5866 | 121.6278 | 13.3713 | -121.6736 | 121.5363 | 121.6827 | 11.0138 | -121.6278
1442.9375 | 121.7651 | -0.2243 | 121.4218 | -0.0049592 | 0.00080973 | 0.066255 | 0.00082022 | 0.064766 | -0.0039905 | -0.00060234 | -0.0054932 | -0.0068337 | 0.064835 | 0.064619 | -0.2034 | -0.0021982 | 121.3531 | -0.064087 | 13.1104 | -0.07782 | 121.3394 | -0.11902 | -0.20142 | -0.10529 | 10.7666 | -0.21057 | 121.2662 | 121.4035 | -0.07782 | -0.10071 | 0.10529 | 0.022888 | -0.082397 | 0.16022 | 0.14648 | 0.1236 | -0.068665 | 0.14648 | 0.1236 | -0.15564 | 0.11902 | 0.013733 | -0.10986 | -0.018311 | 121.5637 | 121.5775 | 13.3347 | -121.6232 | 121.4905 | 121.6278 | 10.9909 | -121.5225
1444.6562 | 121.7514 | -0.20142 | 121.4127 | -0.0049592 | 0.0014505 | 0.064974 | -0.0011024 | 0.065834 | 0.0034863 | 0.0015339 | -0.0054932 | -0.0012795 | 0.062698 | 0.068678 | -0.19848 | -0.0036936 | 121.3669 | -0.10071 | 13.1287 | -0.09613 | 121.3715 | -0.11444 | -0.20599 | -0.073242 | 10.817 | -0.24719 | 121.2799 | 121.4127 | -0.091553 | -0.10529 | 0.086975 | -0.004578 | -0.041199 | 0.10071 | 0.10529 | 0.10986 | -0.045777 | 0.10986 | 0.09613 | -0.13275 | 0.12817 | -0.045776 | -0.14191 | 0 | 121.5729 | 121.5683 | 13.3301 | -121.6187 | 121.4813 | 121.6141 | 11.0184 | -121.5179
1446.4062 | 121.7285 | -0.21515 | 121.431 | 0.0026703 | 0.0016641 | 0.064546 | 0.00039302 | 0.06733 | -0.0012133 | 0.00089286 | 0.0097658 | -0.0046975 | 0.063553 | 0.06761 | -0.20169 | -0.0015572 | 121.4218 | 0.004578 | 13.2935 | -0.041199 | 121.3211 | -0.10529 | -0.1831 | -0.045776 | 10.8902 | -0.19226 | 121.2753 | 121.3989 | -0.068665 | -0.10529 | 0.10986 | 0.032044 | -0.10986 | 0.21973 | 0.17395 | 0.14191 | -0.009155 | 0.14648 | 0.10986 | -0.15564 | 0.16937 | 0.022888 | -0.086975 | -0.032043 | 121.5363 | 121.637 | 13.5086 | -121.6141 | 121.4905 | 121.6141 | 11.1053 | -121.5363
1448.1719 | 121.7697 | -0.18768 | 121.4035 | 0.0026703 | 0.00038233 | 0.064333 | -3.4178e-05 | 0.065834 | 0.0011365 | 0.0028155 | -0.0054932 | -0.0034159 | 0.065689 | 0.067182 | -0.1987 | -0.0043344 | 121.3852 | -0.022888 | 13.3301 | -0.045776 | 121.3394 | -0.1236 | -0.19226 | -0.036621 | 10.9039 | -0.19226 | 121.2662 | 121.3852 | -0.059509 | -0.091553 | 0.064087 | -0.004578 | -0.064086 | 0.16479 | 0.14191 | 0.14648 | -0.01831 | 0.12817 | 0.09613 | -0.13733 | 0.15106 | -0.004578 | -0.10071 | -0.01831 | 121.5271 | 121.5729 | 13.5178 | -121.5958 | 121.4539 | 121.5729 | 11.0916 | -121.4951
1449.875 | 121.7697 | -0.20142 | 121.4493 | 0.0026703 | -0.00047207 | 0.069246 | -0.00024778 | 0.067543 | -0.0029223 | -0.00017514 | -0.0054932 | -0.0051247 | 0.064835 | 0.066542 | -0.20361 | -0.001771 | 121.3623 | -0.032043 | 13.385 | -0.07782 | 121.3531 | -0.10071 | -0.17395 | -0.086975 | 10.9543 | -0.20142 | 121.2524 | 121.4264 | -0.082397 | -0.10986 | 0.10071 | 0.027466 | -0.096131 | 0.16937 | 0.1236 | 0.09613 | -0.086975 | 0.11902 | 0.091553 | -0.19684 | 0.11444 | 0 | -0.091553 | -0.022888 | 121.5546 | 121.5637 | 13.5864 | -121.6232 | 121.4539 | 121.6278 | 11.1557 | -121.5591
1451.5781 | 121.7148 | -0.2243 | 121.3943 | -0.012589 | 0.0014505 | 0.062624 | 0.0025292 | 0.065193 | 0.00028207 | 0.00067926 | -0.013123 | -0.0053385 | 0.064835 | 0.068678 | -0.20083 | -0.0047616 | 121.4264 | 0.009155 | 13.4857 | -0.027466 | 121.3211 | -0.10529 | -0.17853 | -0.004578 | 11.0275 | -0.17853 | 121.2479 | 121.3989 | -0.07782 | -0.09613 | 0.11902 | 0.045776 | -0.073242 | 0.23346 | 0.19684 | 0.15106 | 0.032044 | 0.14648 | 0.12817 | -0.14648 | 0.21973 | 0.045776 | -0.082398 | 0.004578 | 121.5454 | 121.6507 | 13.71 | -121.5729 | 121.4722 | 121.6232 | 11.2518 | -121.4905
1453.3281 | 121.6507 | -0.26093 | 121.4401 | -0.0049592 | 0.0033731 | 0.063692 | 0.00060662 | 0.063057 | 0.0041273 | 0.0011067 | -0.0054932 | -0.00063872 | 0.065262 | 0.067823 | -0.19677 | -0.0013436 | 121.3211 | -0.15564 | 13.4216 | -0.13733 | 121.3852 | -0.12817 | -0.21515 | -0.13275 | 10.9314 | -0.34332 | 121.2845 | 121.4218 | -0.09613 | -0.13275 | 0.13275 | 0.045776 | -0.054932 | 0.10529 | 0.1236 | 0.07782 | -0.11902 | 0.1648 | 0.12817 | -0.15564 | 0.12817 | -0.082398 | -0.21057 | -0.018311 | 121.6461 | 121.582 | 13.6826 | -121.6553 | 121.5454 | 121.6827 | 11.1923 | -121.5729
1455.0469 | 121.7926 | -0.19226 | 121.3989 | -0.012589 | 0.0012369 | 0.068178 | 0.002102 | 0.067543 | -0.0059131 | -0.00017514 | -0.0054932 | -0.0034159 | 0.06398 | 0.066114 | -0.20361 | -0.00091641 | 121.3715 | -0.018311 | 13.6002 | -0.064087 | 121.312 | -0.13275 | -0.18768 | -0.050354 | 11.087 | -0.16937 | 121.2753 | 121.4264 | -0.07782 | -0.086975 | 0.05951 | 0.004578 | -0.086975 | 0.17395 | 0.12817 | 0.1236 | -0.027466 | 0.11444 | 0.10529 | -0.1236 | 0.14191 | 0.022888 | -0.082398 | 0.027466 | 121.5042 | 121.5637 | 13.7924 | -121.5866 | 121.4676 | 121.6187 | 11.2793 | -121.4859
1456.8125 | 121.6415 | -0.27008 | 121.431 | -0.0049592 | 0.0044411 | 0.064546 | -3.4178e-05 | 0.069252 | 0.0045545 | 0.0015339 | -0.013123 | -0.0017069 | 0.065048 | 0.068678 | -0.1987 | -0.0043344 | 121.344 | -0.1236 | 13.5773 | -0.1236 | 121.3577 | -0.13733 | -0.21515 | -0.13733 | 11.0275 | -0.34332 | 121.312 | 121.4539 | -0.10071 | -0.13275 | 0.13275 | 0.054932 | -0.073242 | 0.14649 | 0.14649 | 0.091553 | -0.086975 | 0.16937 | 0.13733 | -0.11902 | 0.13275 | -0.073242 | -0.21057 | 0.022888 | 121.6278 | 121.6141 | 13.8474 | -121.6461 | 121.582 | 121.7239 | 11.2976 | -121.5637
1458.5781 | 121.756 | -0.19684 | 121.4081 | 0.0026703 | 0.0033731 | 0.067751 | 0.003811 | 0.068398 | -0.0056995 | 3.8456e-05 | -0.0054932 | -0.0053385 | 0.064407 | 0.066328 | -0.20276 | -0.0036936 | 121.4081 | 0.064087 | 13.829 | -0.018311 | 121.312 | -0.11902 | -0.16937 | -0.022888 | 11.2701 | -0.14191 | 121.2524 | 121.3989 | -0.068665 | -0.11444 | 0.077819 | 0.027465 | -0.09613 | 0.26093 | 0.17853 | 0.15106 | 0 | 0.12817 | 0.082397 | -0.15564 | 0.17395 | 0.054931 | -0.027466 | -0.009155 | 121.5088 | 121.6049 | 14.0259 | -121.5775 | 121.4493 | 121.5958 | 11.467 | -121.5225
1460.2656 | 121.6324 | -0.24261 | 121.4493 | -0.0049592 | 0.0074319 | 0.064333 | -0.0015296 | 0.065407 | 0.0039135 | 0.00046566 | -0.0054932 | -0.00085232 | 0.065689 | 0.068891 | -0.19955 | -0.0043344 | 121.3898 | -0.045776 | 13.8153 | -0.082397 | 121.3623 | -0.14191 | -0.21057 | -0.073242 | 11.2106 | -0.25635 | 121.3074 | 121.4127 | -0.10529 | -0.13733 | 0.10071 | 0.032044 | -0.086975 | 0.19684 | 0.16022 | 0.12817 | -0.059509 | 0.13733 | 0.10529 | -0.14191 | 0.16937 | -0.013733 | -0.11902 | -0.036621 | 121.6049 | 121.6324 | 14.0579 | -121.6599 | 121.55 | 121.6553 | 11.4532 | -121.5866
1462.0312 | 121.7834 | -0.20142 | 121.4081 | 0.0026703 | 0.00059593 | 0.066042 | 0.0042382 | 0.065621 | -0.0048449 | -0.00060234 | 0.0021363 | -0.0083291 | 0.064194 | 0.066542 | -0.2034 | -0.0024118 | 121.3394 | -0.027466 | 13.8702 | -0.064087 | 121.3486 | -0.13275 | -0.19684 | -0.068665 | 11.2198 | -0.1831 | 121.257 | 121.4035 | -0.07782 | -0.10529 | 0.068665 | 0.004578 | -0.059509 | 0.17395 | 0.13733 | 0.13275 | -0.068664 | 0.1236 | 0.09613 | -0.15106 | 0.13275 | 0.018311 | -0.077819 | -0.004578 | 121.55 | 121.5408 | 14.0717 | -121.6049 | 121.4584 | 121.6049 | 11.4212 | -121.5134
1463.7344 | 121.701 | -0.21973 | 121.4081 | -0.012589 | 0.0042275 | 0.067964 | 0.0023156 | 0.064766 | -0.0027087 | 0.00067926 | -0.0054932 | -0.0055521 | 0.064621 | 0.066542 | -0.20169 | -0.0030526 | 121.3806 | -0.018311 | 13.9252 | -0.073242 | 121.3074 | -0.11444 | -0.17853 | -0.07782 | 11.2152 | -0.21057 | 121.2616 | 121.4127 | -0.054932 | -0.10529 | 0.10529 | 0.041199 | -0.10071 | 0.20142 | 0.14649 | 0.10529 | -0.027466 | 0.16479 | 0.11444 | -0.14648 | 0.14191 | 0.009156 | -0.10529 | 0.004578 | 121.5271 | 121.6003 | 14.1449 | -121.5866 | 121.4813 | 121.6324 | 11.4349 | -121.5134
1465.5 | 121.6782 | -0.25177 | 121.4493 | -0.0049592 | 0.0055093 | 0.066042 | 0.0031702 | 0.066475 | 0.0017773 | -0.0018841 | -0.013123 | -0.0021341 | 0.065475 | 0.066542 | -0.20169 | -0.0032662 | 121.3211 | -0.10986 | 13.9709 | -0.10071 | 121.3715 | -0.15564 | -0.2243 | -0.1236 | 11.2473 | -0.3067 | 121.312 | 121.4401 | -0.10986 | -0.15564 | 0.09613 | 0.027466 | -0.07782 | 0.14191 | 0.15106 | 0.1236 | -0.12817 | 0.14191 | 0.09613 | -0.13733 | 0.12817 | -0.054932 | -0.15106 | -0.009155 | 121.6232 | 121.5729 | 14.2227 | -121.6736 | 121.5637 | 121.6919 | 11.499 | -121.6049
1467.2812 | 121.6278 | -0.25635 | 121.4584 | -0.012589 | 0.0040139 | 0.065187 | 0.002102 | 0.07032 | -0.00099973 | -0.0014569 | -0.013123 | -0.0036295 | 0.064835 | 0.066328 | -0.20276 | -0.0043344 | 121.3852 | -0.032043 | 14.1083 | -0.07782 | 121.3486 | -0.11444 | -0.21057 | -0.10071 | 11.3068 | -0.25635 | 121.2845 | 121.4539 | -0.09613 | -0.15106 | 0.14191 | 0.045777 | -0.10986 | 0.22431 | 0.17853 | 0.13275 | -0.073242 | 0.16022 | 0.10529 | -0.17395 | 0.15564 | 0 | -0.10529 | -0.004578 | 121.6049 | 121.6415 | 14.3646 | -121.669 | 121.5408 | 121.7102 | 11.5631 | -121.6095
1468.9844 | 121.7239 | -0.2243 | 121.4172 | -0.0049592 | 0.0016641 | 0.066469 | 0.0014612 | 0.06498 | -0.0018543 | 3.8456e-05 | 0.0097658 | -0.0036295 | 0.063126 | 0.06526 | -0.20254 | -0.0019846 | 121.3531 | -0.036621 | 14.122 | -0.073242 | 121.3394 | -0.11902 | -0.19226 | -0.09613 | 11.3022 | -0.21973 | 121.2708 | 121.431 | -0.068665 | -0.10529 | 0.10529 | 0.032043 | -0.077819 | 0.18768 | 0.15106 | 0.11902 | -0.064087 | 0.15564 | 0.11902 | -0.14648 | 0.12817 | 0.004577 | -0.11444 | 0.013733 | 121.5637 | 121.5775 | 14.3463 | -121.6095 | 121.4951 | 121.6553 | 11.5265 | -121.5225
1470.7656 | 121.6324 | -0.24719 | 121.463 | -0.0049592 | 0.0059365 | 0.064546 | 0.0014612 | 0.065834 | 0.00070927 | 0.00067926 | -0.013123 | -0.0029885 | 0.065262 | 0.067182 | -0.19977 | -0.0030526 | 121.344 | -0.07782 | 14.2273 | -0.086975 | 121.3531 | -0.13275 | -0.20142 | -0.1236 | 11.3342 | -0.28381 | 121.3028 | 121.4584 | -0.11444 | -0.12817 | 0.11444 | 0.045776 | -0.10986 | 0.16937 | 0.16022 | 0.11444 | -0.11902 | 0.13275 | 0.11902 | -0.16022 | 0.1236 | -0.036621 | -0.15564 | -0.004578 | 121.6003 | 121.5912 | 14.4745 | -121.6644 | 121.55 | 121.7056 | 11.5814 | -121.5912
1472.4531 | 121.7697 | -0.1831 | 121.4127 | -0.012589 | -0.00089927 | 0.066683 | -0.0021704 | 0.065407 | 0.0017773 | 3.8456e-05 | -0.013123 | -0.0042703 | 0.06398 | 0.068464 | -0.19827 | -0.0034798 | 121.4401 | 0 | 14.296 | -0.032043 | 121.3623 | -0.10529 | -0.1831 | -0.004578 | 11.4166 | -0.18768 | 121.257 | 121.3898 | -0.054932 | -0.10071 | 0.077819 | 0 | -0.050354 | 0.1831 | 0.15106 | 0.15106 | 0.027466 | 0.12817 | 0.082397 | -0.15564 | 0.17853 | -0.004578 | -0.086975 | -0.022888 | 121.5454 | 121.6232 | 14.4791 | -121.5958 | 121.4401 | 121.5729 | 11.5997 | -121.5134
1474.2344 | 121.756 | -0.21973 | 121.4127 | -0.012589 | 0.0029459 | 0.066255 | 0.0033838 | 0.064553 | -0.0044177 | 0.00046566 | -0.013123 | -0.0072611 | 0.065048 | 0.065687 | -0.2034 | -0.0032662 | 121.4447 | 0.068665 | 14.4608 | -0.022888 | 121.3257 | -0.09613 | -0.17853 | -0.027466 | 11.4395 | -0.15106 | 121.257 | 121.4035 | -0.068665 | -0.09613 | 0.1236 | 0.041199 | -0.086975 | 0.28839 | 0.19684 | 0.15564 | 0.032043 | 0.15106 | 0.1236 | -0.15564 | 0.19226 | 0.068665 | -0.054932 | -0.009156 | 121.5454 | 121.6644 | 14.6805 | -121.5912 | 121.4767 | 121.6232 | 11.6592 | -121.5088
1476 | 121.756 | -0.19226 | 121.4081 | -0.0049592 | 0.0040139 | 0.064119 | -0.00067498 | 0.065834 | 0.0030591 | 0.00089286 | 0.0097658 | -0.0023477 | 0.065689 | 0.068464 | -0.1987 | -0.0043344 | 121.3623 | -0.11902 | 14.3555 | -0.10529 | 121.3852 | -0.15106 | -0.21057 | -0.086975 | 11.3113 | -0.28839 | 121.3165 | 121.4493 | -0.086975 | -0.1236 | 0.041199 | -0.01831 | -0.022888 | 0.073242 | 0.086975 | 0.10529 | -0.045776 | 0.10529 | 0.068665 | -0.091553 | 0.10529 | -0.09613 | -0.1648 | 0.041199 | 121.5775 | 121.5546 | 14.5477 | -121.6187 | 121.5088 | 121.6415 | 11.5036 | -121.5317
1477.7031 | 121.7789 | -0.19226 | 121.4127 | -0.012589 | 0.0025185 | 0.063692 | -0.001316 | 0.065621 | 6.8274e-05 | 0.0013203 | -0.0054932 | -0.0044839 | 0.06398 | 0.069959 | -0.1987 | -0.0051888 | 121.3715 | -0.054932 | 14.4653 | -0.082397 | 121.3348 | -0.1236 | -0.21057 | -0.022888 | 11.412 | -0.20142 | 121.2799 | 121.4081 | -0.064087 | -0.10986 | 0.068665 | -0.01831 | -0.07782 | 0.13733 | 0.10986 | 0.12817 | -0.041199 | 0.12817 | 0.082398 | -0.13275 | 0.16937 | -0.009155 | -0.091553 | -0.004578 | 121.5271 | 121.5637 | 14.6576 | -121.6232 | 121.4722 | 121.6003 | 11.6043 | -121.5225
1479.4688 | 121.7606 | -0.18768 | 121.4035 | -0.012589 | 0.0016641 | 0.063692 | -0.0019568 | 0.067116 | 0.0019909 | 0.00025206 | -0.013123 | -0.0032021 | 0.062912 | 0.070173 | -0.19998 | -0.0032662 | 121.376 | -0.045776 | 14.5386 | -0.068665 | 121.3577 | -0.11902 | -0.19226 | -0.018311 | 11.4761 | -0.21515 | 121.2662 | 121.4264 | -0.068665 | -0.10071 | 0.068664 | -0.004578 | -0.045776 | 0.14191 | 0.11902 | 0.1236 | -0.027465 | 0.11902 | 0.086975 | -0.13733 | 0.16937 | -0.027466 | -0.11444 | 0.022889 | 121.5454 | 121.5637 | 14.7263 | -121.5958 | 121.4539 | 121.6141 | 11.6638 | -121.5042
1481.1719 | 121.6873 | -0.20142 | 121.4172 | 0.0026703 | 0.0044411 | 0.063692 | -0.00024778 | 0.064339 | 0.00028207 | 0.0026019 | -0.0054932 | -0.0021341 | 0.065048 | 0.069319 | -0.20062 | -0.0015572 | 121.3348 | -0.11444 | 14.5432 | -0.11902 | 121.3989 | -0.13733 | -0.21057 | -0.1236 | 11.4212 | -0.3067 | 121.312 | 121.4722 | -0.09613 | -0.13275 | 0.064087 | -0.009155 | -0.01831 | 0.086975 | 0.082397 | 0.091552 | -0.082397 | 0.10529 | 0.068665 | -0.10529 | 0.07782 | -0.10529 | -0.17395 | 0.054932 | 121.6003 | 121.5363 | 14.7446 | -121.6278 | 121.5134 | 121.6736 | 11.6226 | -121.55
1482.9375 | 121.7194 | -0.21057 | 121.4355 | -0.0049592 | 0.0048685 | 0.063051 | 0.0068018 | 0.066475 | -0.0050585 | 3.8456e-05 | -0.013123 | -0.0070475 | 0.06398 | 0.066328 | -0.20382 | -0.0021982 | 121.4264 | 0.068665 | 14.8361 | -0.027466 | 121.2936 | -0.11902 | -0.16479 | -0.022888 | 11.6272 | -0.15106 | 121.2616 | 121.4264 | -0.059509 | -0.10071 | 0.091552 | 0.045776 | -0.14191 | 0.27924 | 0.18311 | 0.13733 | -0.009155 | 0.15106 | 0.10986 | -0.17395 | 0.18768 | 0.059509 | -0.050354 | -0.009155 | 121.5042 | 121.637 | 15.0467 | -121.6003 | 121.4722 | 121.637 | 11.8378 | -121.5363
1484.6719 | 121.6827 | -0.23804 | 121.463 | -0.0049592 | 0.0040139 | 0.064546 | 0.003811 | 0.068825 | -0.0037769 | -0.00017514 | 0.0021363 | -0.0057657 | 0.065475 | 0.069746 | -0.20254 | -0.0026254 | 121.4127 | 0.045776 | 14.9139 | -0.032043 | 121.3165 | -0.10529 | -0.1831 | -0.027466 | 11.6592 | -0.17395 | 121.2616 | 121.431 | -0.064087 | -0.091553 | 0.13275 | 0.054932 | -0.14648 | 0.28381 | 0.20599 | 0.15106 | -0.050354 | 0.17395 | 0.14648 | -0.20142 | 0.21057 | 0.064087 | -0.082397 | -0.032044 | 121.5546 | 121.6507 | 15.152 | -121.6461 | 121.4996 | 121.669 | 11.8973 | -121.5546
1486.4375 | 121.6232 | -0.25635 | 121.463 | -0.0049592 | 0.0080727 | 0.062624 | -0.0025976 | 0.068825 | 0.0051953 | 0.0011067 | 0.0021363 | 2.078e-06 | 0.064407 | 0.068678 | -0.19934 | -0.002839 | 121.3898 | -0.059509 | 14.8773 | -0.07782 | 121.376 | -0.13275 | -0.18768 | -0.07782 | 11.6409 | -0.29755 | 121.3211 | 121.4493 | -0.09613 | -0.11902 | 0.1236 | 0.068665 | -0.086975 | 0.19684 | 0.17853 | 0.10986 | -0.073242 | 0.16022 | 0.13733 | -0.14191 | 0.17853 | -0.041198 | -0.17853 | -0.013733 | 121.6324 | 121.6461 | 15.1337 | -121.6507 | 121.5775 | 121.7056 | 11.8973 | -121.582
1488.1406 | 121.6461 | -0.23804 | 121.4584 | -0.012589 | 0.0050821 | 0.067323 | 0.00039302 | 0.067116 | -0.0035633 | -0.00017514 | 0.0021363 | -0.0038431 | 0.063766 | 0.067823 | -0.20212 | -0.0024118 | 121.3165 | -0.10529 | 14.9277 | -0.1236 | 121.3531 | -0.15106 | -0.20142 | -0.13733 | 11.6501 | -0.27924 | 121.344 | 121.4767 | -0.10529 | -0.12817 | 0.086975 | 0.036621 | -0.10529 | 0.13275 | 0.11444 | 0.07782 | -0.14191 | 0.13275 | 0.10986 | -0.11444 | 0.10071 | -0.041199 | -0.15106 | 0.018311 | 121.5912 | 121.5546 | 15.1657 | -121.6599 | 121.582 | 121.7148 | 11.8881 | -121.5866
1489.9062 | 121.7285 | -0.20599 | 121.4081 | -0.020218 | 0.00080973 | 0.068391 | -0.001316 | 0.066048 | -0.0059131 | 0.00025206 | -0.0054932 | -0.0034159 | 0.063126 | 0.063551 | -0.20276 | -0.004548 | 121.3806 | -0.032043 | 15.0192 | -0.068665 | 121.3348 | -0.10986 | -0.17853 | -0.091553 | 11.673 | -0.21057 | 121.2708 | 121.4676 | -0.068665 | -0.10529 | 0.096131 | 0.027466 | -0.073242 | 0.17395 | 0.13733 | 0.10986 | -0.027466 | 0.13733 | 0.10071 | -0.13733 | 0.11444 | -0.004577 | -0.10529 | 0.059509 | 121.5408 | 121.5866 | 15.2252 | -121.5866 | 121.4767 | 121.6736 | 11.879 | -121.5134
1491.6094 | 121.7651 | -0.20599 | 121.4447 | 0.0026703 | 0.0012369 | 0.066683 | 0.001034 | 0.068611 | -0.0044177 | -0.0010297 | -0.013123 | -0.0051247 | 0.064407 | 0.065473 | -0.20361 | -0.001771 | 121.4127 | 0.009155 | 15.1657 | -0.041199 | 121.344 | -0.10529 | -0.1831 | -0.018311 | 11.8103 | -0.16022 | 121.2753 | 121.3989 | -0.073242 | -0.086975 | 0.10071 | 0.022889 | -0.10071 | 0.21515 | 0.1648 | 0.14191 | -0.032043 | 0.13275 | 0.11902 | -0.16937 | 0.18768 | 0.045777 | -0.073242 | -0.045776 | 121.55 | 121.6187 | 15.3717 | -121.6278 | 121.4813 | 121.6049 | 12.0163 | -121.5317
1493.375 | 121.756 | -0.19226 | 121.4081 | -0.012589 | 0.0025185 | 0.06476 | -0.00046138 | 0.066262 | 0.0026319 | 0.00025206 | 0.0021363 | 2.078e-06 | 0.06398 | 0.068037 | -0.19827 | -0.0047616 | 121.3623 | -0.086975 | 15.1291 | -0.09613 | 121.3623 | -0.15106 | -0.20142 | -0.068665 | 11.7783 | -0.24719 | 121.3028 | 121.4081 | -0.07782 | -0.10529 | 0.041199 | -0.009155 | -0.045776 | 0.10529 | 0.096131 | 0.10529 | -0.045776 | 0.11444 | 0.086975 | -0.10529 | 0.1236 | -0.054931 | -0.14191 | 0 | 121.5546 | 121.5546 | 15.3214 | -121.6095 | 121.4951 | 121.6003 | 11.9705 | -121.5134
1495.0781 | 121.6782 | -0.24261 | 121.4218 | -0.012589 | 0.0044411 | 0.064974 | -3.4178e-05 | 0.066902 | 0.0026319 | 0.0017475 | 0.0021363 | -0.0032021 | 0.061417 | 0.067182 | -0.19848 | -0.0047616 | 121.3486 | -0.073242 | 15.2527 | -0.07782 | 121.3623 | -0.14648 | -0.21973 | -0.082397 | 11.8652 | -0.27924 | 121.3257 | 121.4493 | -0.086975 | -0.13733 | 0.096131 | 0.022888 | -0.059509 | 0.16937 | 0.16479 | 0.14191 | -0.073242 | 0.15564 | 0.10529 | -0.09613 | 0.16022 | -0.036621 | -0.14191 | 0.027466 | 121.6049 | 121.5912 | 15.4953 | -121.6415 | 121.5683 | 121.6919 | 12.1078 | -121.5591
1496.8438 | 121.6782 | -0.24261 | 121.463 | -0.0049592 | 0.0072183 | 0.067537 | 0.00082022 | 0.064553 | -0.0012133 | 0.0011067 | -0.0054932 | -0.00085232 | 0.064621 | 0.06761 | -0.20126 | -0.0030526 | 121.3257 | -0.091553 | 15.3259 | -0.10529 | 121.3715 | -0.13733 | -0.23346 | -0.13275 | 11.8835 | -0.3067 | 121.3257 | 121.4676 | -0.10529 | -0.13733 | 0.10529 | 0.009156 | -0.091553 | 0.15106 | 0.13733 | 0.12817 | -0.13733 | 0.13733 | 0.10529 | -0.13733 | 0.10986 | -0.064087 | -0.16937 | 0.004577 | 121.6141 | 121.5683 | 15.5685 | -121.6965 | 121.5683 | 121.7102 | 12.1262 | -121.6003
1498.5469 | 121.7056 | -0.2243 | 121.4539 | 0.0026703 | 0.0067911 | 0.064333 | -0.00024778 | 0.069252 | 0.0034863 | 0.00067926 | 0.0021363 | -0.0027749 | 0.064835 | 0.068678 | -0.19848 | -0.0039072 | 121.3715 | -0.059509 | 15.4312 | -0.073242 | 121.3669 | -0.13733 | -0.21057 | -0.068665 | 11.9568 | -0.2655 | 121.3028 | 121.4813 | -0.091553 | -0.11444 | 0.086975 | 0.013733 | -0.086975 | 0.16479 | 0.15106 | 0.13733 | -0.082397 | 0.13275 | 0.10986 | -0.15106 | 0.15564 | -0.041199 | -0.15106 | 0.027466 | 121.5912 | 121.5958 | 15.6555 | -121.6644 | 121.5271 | 121.7056 | 12.1811 | -121.5683
1500.3125 | 121.669 | -0.23346 | 121.4447 | 0.0026703 | 0.0061501 | 0.06711 | 0.0035974 | 0.065407 | -0.00014533 | 0.0019611 | 0.0021363 | -0.0014933 | 0.065262 | 0.068037 | -0.20147 | -0.00091641 | 121.3348 | -0.10529 | 15.4953 | -0.086975 | 121.3989 | -0.14648 | -0.2243 | -0.1236 | 11.9659 | -0.2655 | 121.3394 | 121.463 | -0.10071 | -0.12817 | 0.086975 | 0.009155 | -0.045776 | 0.12817 | 0.14648 | 0.13733 | -0.10986 | 0.13275 | 0.10528 | -0.10529 | 0.10986 | -0.032044 | -0.13733 | 0.018311 | 121.6324 | 121.5683 | 15.7288 | -121.669 | 121.5729 | 121.6965 | 12.1994 | -121.5729
1502.0781 | 121.6919 | -0.23804 | 121.431 | -0.0049592 | 0.0040139 | 0.065401 | -0.0021704 | 0.064766 | -0.00014533 | 0.0032429 | -0.0054932 | -0.0055521 | 0.064835 | 0.06825 | -0.20083 | -0.002839 | 121.3074 | -0.1236 | 15.509 | -0.11902 | 121.3898 | -0.15106 | -0.21057 | -0.15106 | 11.9385 | -0.31586 | 121.3257 | 121.4676 | -0.10986 | -0.13275 | 0.086975 | 0.027466 | -0.041198 | 0.11444 | 0.11902 | 0.091552 | -0.1236 | 0.12817 | 0.10529 | -0.10529 | 0.086975 | -0.07782 | -0.18311 | 0.036621 | 121.6278 | 121.5454 | 15.7471 | -121.6415 | 121.5637 | 121.7056 | 12.1765 | -121.5637
1503.7812 | 121.7239 | -0.21057 | 121.4127 | -0.012589 | -4.4874e-05 | 0.067323 | 0.0012476 | 0.065193 | -0.0056995 | 0.00046566 | -0.0054932 | -0.0059793 | 0.062912 | 0.066114 | -0.20361 | -0.0024118 | 121.3715 | -0.009155 | 15.6601 | -0.064087 | 121.3531 | -0.10071 | -0.17395 | -0.073242 | 12.03 | -0.20142 | 121.2753 | 121.4813 | -0.082397 | -0.09613 | 0.10986 | 0.036621 | -0.05951 | 0.20142 | 0.14648 | 0.10986 | -0.041199 | 0.12817 | 0.11444 | -0.13733 | 0.13733 | 0.009155 | -0.10529 | 0.068664 | 121.5637 | 121.582 | 15.8707 | -121.5866 | 121.4859 | 121.6919 | 12.2406 | -121.5088
1505.5625 | 121.756 | -0.20142 | 121.4172 | -0.012589 | 0.0052957 | 0.065187 | -0.00024778 | 0.065193 | 0.0030591 | 0.0011067 | -0.0054932 | -0.0010659 | 0.063766 | 0.068891 | -0.19977 | -0.0041208 | 121.3577 | -0.10071 | 15.6647 | -0.10986 | 121.3943 | -0.14191 | -0.21057 | -0.10529 | 12.0209 | -0.27924 | 121.3165 | 121.4905 | -0.07782 | -0.10986 | 0.059509 | -0.009155 | -0.022888 | 0.10071 | 0.091553 | 0.10071 | -0.059509 | 0.1236 | 0.091553 | -0.10071 | 0.09613 | -0.07782 | -0.16937 | 0.073243 | 121.5958 | 121.5591 | 15.8661 | -121.6278 | 121.5179 | 121.6919 | 12.2223 | -121.5271
1507.3281 | 121.6599 | -0.25177 | 121.4539 | -0.0049592 | 0.0048685 | 0.06711 | 0.0059472 | 0.064766 | -0.0024951 | -0.0012433 | -0.020752 | -0.0025613 | 0.065903 | 0.06761 | -0.20254 | -0.0019846 | 121.3211 | -0.086975 | 15.8386 | -0.11444 | 121.4035 | -0.14648 | -0.2243 | -0.15106 | 12.117 | -0.27008 | 121.3486 | 121.4905 | -0.13733 | -0.13275 | 0.10529 | 0.027466 | -0.050354 | 0.16479 | 0.13733 | 0.10986 | -0.13275 | 0.11444 | 0.11902 | -0.10528 | 0.10071 | -0.018311 | -0.13733 | 0.036622 | 121.6553 | 121.5729 | 16.0904 | -121.6782 | 121.6003 | 121.7422 | 12.3688 | -121.5866
1509.0156 | 121.7651 | -0.20142 | 121.431 | 0.0026703 | 0.0035867 | 0.063478 | -3.4178e-05 | 0.067757 | -0.00014533 | -0.0010297 | -0.013123 | -0.0049111 | 0.063126 | 0.067396 | -0.19934 | -0.0034798 | 121.4218 | -0.013733 | 15.9348 | -0.045776 | 121.3394 | -0.11444 | -0.17853 | -0.013733 | 12.2177 | -0.18768 | 121.2753 | 121.4539 | -0.073242 | -0.10529 | 0.086975 | 0.022888 | -0.091552 | 0.18768 | 0.15564 | 0.13275 | -0.009155 | 0.12817 | 0.09613 | -0.15564 | 0.18768 | 0.013733 | -0.082397 | 0.022888 | 121.5408 | 121.6232 | 16.1362 | -121.6095 | 121.4767 | 121.6553 | 12.4191 | -121.5363
1510.7969 | 121.7239 | -0.23346 | 121.4493 | -0.0049592 | 0.0033731 | 0.067751 | 0.0035974 | 0.064339 | -0.0067675 | -0.00060234 | -0.013123 | -0.0057657 | 0.065689 | 0.066114 | -0.20212 | -0.002839 | 121.3715 | 0.009155 | 16.0172 | -0.054932 | 121.3669 | -0.10986 | -0.18768 | -0.082397 | 12.1902 | -0.20599 | 121.2753 | 121.4218 | -0.073242 | -0.091553 | 0.1236 | 0.045776 | -0.082398 | 0.24261 | 0.17853 | 0.13275 | -0.07782 | 0.16022 | 0.14191 | -0.17395 | 0.15106 | 0.027465 | -0.11444 | -0.027466 | 121.6003 | 121.6049 | 16.2506 | -121.637 | 121.5088 | 121.6553 | 12.4237 | -121.5408
1512.5 | 121.6599 | -0.22888 | 121.4539 | -0.0049592 | 0.0027323 | 0.06476 | 0.001034 | 0.065621 | 0.0043409 | 0.0015339 | -0.0054932 | -0.0025613 | 0.066116 | 0.06825 | -0.1987 | -0.0056162 | 121.312 | -0.11444 | 16.0263 | -0.10071 | 121.4127 | -0.12817 | -0.20599 | -0.11902 | 12.1536 | -0.32501 | 121.3257 | 121.4859 | -0.10071 | -0.15106 | 0.10071 | 0.022888 | -0.041198 | 0.11444 | 0.12817 | 0.10529 | -0.14191 | 0.12817 | 0.07782 | -0.12817 | 0.10986 | -0.09613 | -0.17395 | 0.032044 | 121.6415 | 121.5408 | 16.2552 | -121.6599 | 121.5546 | 121.7148 | 12.3825 | -121.6049
1514.2656 | 121.6461 | -0.23804 | 121.4539 | -0.0049592 | 0.0040139 | 0.06241 | -0.00067498 | 0.065621 | 0.0028455 | 0.0032429 | 0.0021363 | 0.00021568 | 0.065903 | 0.071028 | -0.1987 | -0.0060434 | 121.3531 | -0.10071 | 16.1224 | -0.10071 | 121.3577 | -0.13733 | -0.21515 | -0.12817 | 12.2223 | -0.32959 | 121.344 | 121.4676 | -0.086975 | -0.12817 | 0.10071 | 0.022888 | -0.09613 | 0.13733 | 0.13733 | 0.11444 | -0.10071 | 0.15106 | 0.10986 | -0.10986 | 0.10986 | -0.091553 | -0.20142 | 0.013733 | 121.5958 | 121.5912 | 16.3605 | -121.669 | 121.582 | 121.7056 | 12.4603 | -121.582
1516.0156 | 121.637 | -0.23804 | 121.463 | -0.0049592 | 0.0091409 | 0.064546 | 0.00039302 | 0.064339 | 0.00049567 | 0.0028155 | -0.0054932 | -0.0012795 | 0.067398 | 0.068678 | -0.1987 | -0.0039072 | 121.3715 | -0.036621 | 16.2689 | -0.068665 | 121.344 | -0.11444 | -0.21057 | -0.07782 | 12.3367 | -0.29755 | 121.3165 | 121.4493 | -0.086975 | -0.12817 | 0.1236 | 0.027466 | -0.11902 | 0.20142 | 0.16937 | 0.14191 | -0.091553 | 0.15106 | 0.10986 | -0.14648 | 0.16022 | -0.059509 | -0.16937 | -0.013733 | 121.582 | 121.6095 | 16.507 | -121.6736 | 121.5546 | 121.6873 | 12.5748 | -121.5912
1517.7188 | 121.7697 | -0.18768 | 121.4035 | -0.012589 | 0.0033731 | 0.064974 | -0.00024778 | 0.067116 | 6.8274e-05 | 0.0011067 | 0.0021363 | -0.0044839 | 0.065262 | 0.068891 | -0.19891 | -0.0021982 | 121.3348 | -0.068665 | 16.2918 | -0.10986 | 121.376 | -0.14191 | -0.20142 | -0.07782 | 12.3322 | -0.26093 | 121.3028 | 121.4722 | -0.086975 | -0.1236 | 0.045776 | -0.013733 | -0.027465 | 0.11902 | 0.07782 | 0.091553 | -0.068664 | 0.10071 | 0.064087 | -0.10071 | 0.10986 | -0.073242 | -0.13733 | 0.068665 | 121.5637 | 121.5225 | 16.4795 | -121.6049 | 121.4905 | 121.6599 | 12.5198 | -121.5271
1519.4844 | 121.6278 | -0.25635 | 121.463 | 0.0026703 | 0.0063639 | 0.062624 | 0.00060662 | 0.06498 | 0.00092287 | 0.0019611 | 0.0021363 | -0.0023477 | 0.062912 | 0.068678 | -0.20019 | -0.0041208 | 121.3715 | -0.036621 | 16.4383 | -0.07782 | 121.3486 | -0.12817 | -0.21057 | -0.086975 | 12.41 | -0.29755 | 121.3165 | 121.4905 | -0.086975 | -0.11902 | 0.12817 | 0.045777 | -0.11444 | 0.21973 | 0.17853 | 0.13275 | -0.091553 | 0.16937 | 0.13733 | -0.14648 | 0.16937 | -0.041198 | -0.17853 | 0.027466 | 121.6049 | 121.6278 | 16.6946 | -121.6736 | 121.5729 | 121.7468 | 12.6663 | -121.582
1521.25 | 121.7789 | -0.18768 | 121.4218 | -0.020218 | 0.0040139 | 0.066255 | 0.00017942 | 0.063912 | 0.00028207 | 0.0021747 | -0.0054932 | -0.0032021 | 0.064407 | 0.067182 | -0.20019 | -0.0015572 | 121.3348 | -0.059509 | 16.4932 | -0.086975 | 121.3669 | -0.1236 | -0.19684 | -0.068665 | 12.4741 | -0.2243 | 121.312 | 121.4539 | -0.073242 | -0.10071 | 0.064087 | -0.009155 | -0.054932 | 0.12817 | 0.10071 | 0.10986 | -0.086975 | 0.11444 | 0.086975 | -0.10986 | 0.11902 | -0.036621 | -0.1236 | 0.032043 | 121.5546 | 121.5225 | 16.6809 | -121.6187 | 121.4996 | 121.6415 | 12.6617 | -121.5225
1522.9531 | 121.6461 | -0.22888 | 121.4493 | -0.0049592 | 0.0040139 | 0.066042 | 0.00552 | 0.066902 | -0.0056995 | -0.00060234 | -0.0054932 | -0.0059793 | 0.064835 | 0.066114 | -0.20468 | -0.0030526 | 121.3898 | 0.068665 | 16.7267 | -0.036621 | 121.3623 | -0.12817 | -0.17853 | -0.059509 | 12.6068 | -0.17853 | 121.2753 | 121.4539 | -0.07782 | -0.10071 | 0.10071 | 0.050354 | -0.086975 | 0.29755 | 0.19226 | 0.14191 | -0.059509 | 0.15106 | 0.12817 | -0.17395 | 0.16937 | 0.050354 | -0.07782 | 0.004577 | 121.5912 | 121.6187 | 16.9556 | -121.6278 | 121.5042 | 121.6827 | 12.8357 | -121.55
1524.7344 | 121.6461 | -0.24261 | 121.4813 | -0.012589 | 0.0067911 | 0.064974 | 0.00060662 | 0.066689 | 0.0024183 | 0.0011067 | 0.0021363 | -0.0017069 | 0.065262 | 0.069746 | -0.20041 | -0.0032662 | 121.3394 | -0.082397 | 16.6626 | -0.091553 | 121.3943 | -0.13275 | -0.20599 | -0.12817 | 12.5153 | -0.31128 | 121.3348 | 121.4951 | -0.086975 | -0.1236 | 0.10986 | 0.036621 | -0.086975 | 0.16022 | 0.15106 | 0.11444 | -0.14191 | 0.15564 | 0.11902 | -0.14648 | 0.11444 | -0.068664 | -0.18768 | 0.013733 | 121.637 | 121.582 | 16.9052 | -121.6873 | 121.5775 | 121.7377 | 12.7579 | -121.6049
1526.4844 | 121.669 | -0.22888 | 121.4584 | -0.0049592 | 0.0046549 | 0.06241 | 0.0033838 | 0.06733 | 0.0011365 | 0.0021747 | 0.0021363 | -0.0019205 | 0.065689 | 0.06825 | -0.19955 | -0.0026254 | 121.3074 | -0.10071 | 16.7267 | -0.09613 | 121.3989 | -0.1236 | -0.21057 | -0.11444 | 12.5107 | -0.3067 | 121.3303 | 121.4676 | -0.082397 | -0.14648 | 0.10529 | 0.018311 | -0.059509 | 0.12817 | 0.13275 | 0.11444 | -0.15106 | 0.14649 | 0.082398 | -0.12817 | 0.11444 | -0.07782 | -0.16022 | 0.009155 | 121.6278 | 121.5363 | 16.9556 | -121.669 | 121.5591 | 121.6965 | 12.7396 | -121.6049
1528.1875 | 121.7194 | -0.21515 | 121.4218 | 0.0103 | -0.00025847 | 0.06711 | -0.001316 | 0.065193 | -0.0054859 | -0.00038874 | 0.0021363 | -0.0068337 | 0.062698 | 0.06761 | -0.20511 | -0.00070281 | 121.3669 | 0.013733 | 16.8823 | -0.068665 | 121.3531 | -0.10071 | -0.17395 | -0.07782 | 12.6434 | -0.21057 | 121.2662 | 121.4859 | -0.059509 | -0.10071 | 0.11444 | 0.041199 | -0.068665 | 0.22888 | 0.14648 | 0.10528 | -0.054932 | 0.15564 | 0.11444 | -0.15564 | 0.13733 | 0.004578 | -0.10986 | 0.064087 | 121.5683 | 121.582 | 17.0975 | -121.5958 | 121.4813 | 121.701 | 12.8586 | -121.5225
1529.9531 | 121.6599 | -0.25635 | 121.4584 | -0.012589 | 0.0042275 | 0.066469 | 0.002102 | 0.06498 | -0.0024951 | -0.0020977 | -0.013123 | -0.0061929 | 0.063553 | 0.066114 | -0.20297 | -0.0041208 | 121.4081 | 0.059509 | 17.0746 | -0.013733 | 121.3531 | -0.1236 | -0.18768 | -0.032043 | 12.7716 | -0.16937 | 121.2982 | 121.4539 | -0.073242 | -0.11444 | 0.13275 | 0.068665 | -0.10529 | 0.31586 | 0.24262 | 0.17395 | -0.050354 | 0.18311 | 0.14191 | -0.16022 | 0.22431 | 0.086975 | -0.054932 | -0.004578 | 121.6095 | 121.6644 | 17.3309 | -121.6461 | 121.5546 | 121.7102 | 13.028 | -121.5729
1531.7188 | 121.7606 | -0.17853 | 121.4172 | -0.0049592 | 0.00016873 | 0.066683 | -0.0028112 | 0.063484 | -0.00014533 | 0.00089286 | 0.0021363 | -0.0029885 | 0.062271 | 0.06825 | -0.1987 | -0.0056162 | 121.4264 | 0.045776 | 17.1112 | -0.018311 | 121.3394 | -0.11444 | -0.1831 | -0.004578 | 12.7808 | -0.17853 | 121.2799 | 121.4355 | -0.068665 | -0.073242 | 0.064087 | -0.004577 | -0.077819 | 0.2243 | 0.16022 | 0.16479 | 0.009156 | 0.10986 | 0.10529 | -0.13733 | 0.17395 | 0 | -0.10529 | 0.018311 | 121.5179 | 121.6049 | 17.2897 | -121.6003 | 121.4584 | 121.6141 | 12.9593 | -121.4905
1533.4688 | 121.7926 | -0.19226 | 121.4035 | -0.012589 | 0.00059593 | 0.068391 | -0.0011024 | 0.063057 | -0.0033495 | -0.0010297 | -0.013123 | -0.0072611 | 0.062057 | 0.066542 | -0.20382 | -0.0041208 | 121.3669 | 0.009155 | 17.1844 | -0.041199 | 121.3394 | -0.10986 | -0.17853 | -0.054932 | 12.8311 | -0.17395 | 121.2845 | 121.4539 | -0.07782 | -0.11444 | 0.082398 | 0.013733 | -0.064086 | 0.20142 | 0.15106 | 0.13733 | -0.036621 | 0.11444 | 0.07782 | -0.11902 | 0.13733 | 0.018311 | -0.059509 | 0.050354 | 121.5317 | 121.5591 | 17.3767 | -121.582 | 121.4767 | 121.6461 | 13.0234 | -121.5179
1535.25 | 121.7056 | -0.19684 | 121.4447 | -0.0049592 | 0.0050821 | 0.066469 | 0.00060662 | 0.067757 | 0.0041273 | 0.00089286 | 0.0021363 | -0.0032021 | 0.065475 | 0.069105 | -0.19998 | -0.0019846 | 121.3531 | -0.091553 | 17.1616 | -0.11444 | 121.4081 | -0.14648 | -0.21057 | -0.091553 | 12.7304 | -0.30212 | 121.344 | 121.4813 | -0.091553 | -0.14191 | 0.050354 | -0.013733 | -0.036621 | 0.10529 | 0.082397 | 0.09613 | -0.091553 | 0.10529 | 0.054931 | -0.10071 | 0.10529 | -0.10529 | -0.16022 | 0.036621 | 121.6049 | 121.55 | 17.3584 | -121.6553 | 121.5408 | 121.6782 | 12.9272 | -121.5866
1536.9375 | 121.6324 | -0.25177 | 121.4539 | -0.0049592 | 0.0061501 | 0.066469 | 0.003811 | 0.069252 | -0.00014533 | -0.0018841 | -0.0054932 | -0.0046975 | 0.066544 | 0.066755 | -0.20361 | -0.0015572 | 121.3852 | 0.009155 | 17.395 | -0.064087 | 121.3577 | -0.1236 | -0.18768 | -0.09613 | 12.8677 | -0.27008 | 121.3257 | 121.4859 | -0.09613 | -0.13275 | 0.12817 | 0.064087 | -0.09613 | 0.26093 | 0.18768 | 0.1236 | -0.068664 | 0.15564 | 0.11902 | -0.12817 | 0.15564 | -0.018311 | -0.13733 | 0.032044 | 121.6095 | 121.637 | 17.6468 | -121.6415 | 121.5775 | 121.7377 | 13.1195 | -121.5866
1538.7031 | 121.7789 | -0.19226 | 121.4172 | -0.0049592 | 0.0023049 | 0.066042 | 0.002102 | 0.067543 | -0.0039905 | -0.0016705 | -0.0054932 | -0.0070475 | 0.066116 | 0.068037 | -0.20404 | -0.0039072 | 121.4218 | 0.09613 | 17.514 | -0.022888 | 121.3303 | -0.10986 | -0.18768 | 0.018311 | 13.0508 | -0.12817 | 121.2616 | 121.4127 | -0.050354 | -0.10071 | 0.082398 | 0.004578 | -0.086975 | 0.28839 | 0.16937 | 0.16479 | 0.004578 | 0.14191 | 0.091553 | -0.15564 | 0.21057 | 0.064087 | -0.027466 | -0.004577 | 121.5225 | 121.6141 | 17.7063 | -121.6049 | 121.4539 | 121.6049 | 13.2431 | -121.5179
1540.4688 | 121.6324 | -0.25635 | 121.4584 | -0.020218 | 0.0040139 | 0.065187 | 0.0018884 | 0.06733 | -0.00014533 | -0.0027387 | -0.013123 | -0.0021341 | 0.063766 | 0.067823 | -0.20233 | -0.0049752 | 121.3898 | 0 | 17.5598 | -0.068665 | 121.3623 | -0.12817 | -0.21057 | -0.10529 | 12.9593 | -0.27008 | 121.3577 | 121.4767 | -0.10986 | -0.1236 | 0.12817 | 0.045777 | -0.09613 | 0.25635 | 0.18768 | 0.14191 | -0.068664 | 0.14649 | 0.13275 | -0.10071 | 0.15106 | -0.013733 | -0.14649 | 0.018311 | 121.6187 | 121.6461 | 17.8162 | -121.669 | 121.6141 | 121.7331 | 13.2156 | -121.582
1542.1875 | 121.756 | -0.17853 | 121.431 | 0.0103 | 0.0042275 | 0.066042 | -0.00024778 | 0.068398 | 0.0030591 | 0.0015339 | 0.0021363 | -0.00085232 | 0.063553 | 0.065687 | -0.19977 | -0.0034798 | 121.3531 | -0.050354 | 17.5186 | -0.09613 | 121.3989 | -0.14191 | -0.20599 | -0.054932 | 12.9501 | -0.27008 | 121.312 | 121.4722 | -0.082397 | -0.11902 | 0.036621 | -0.027466 | -0.032043 | 0.12817 | 0.082398 | 0.10986 | -0.07782 | 0.096131 | 0.059509 | -0.11902 | 0.1236 | -0.091553 | -0.15106 | 0.041199 | 121.5775 | 121.5317 | 17.6971 | -121.637 | 121.4905 | 121.6507 | 13.1287 | -121.55
1543.9375 | 121.6415 | -0.22888 | 121.4401 | -0.0049592 | 0.0074319 | 0.063692 | 0.0023156 | 0.064766 | 0.0028455 | 0.0011067 | -0.013123 | -0.0019205 | 0.066757 | 0.066542 | -0.19912 | -0.0056162 | 121.4081 | 0.013733 | 17.7017 | -0.059509 | 121.3806 | -0.14191 | -0.19226 | -0.022888 | 13.092 | -0.25177 | 121.3074 | 121.4401 | -0.091553 | -0.1236 | 0.086975 | 0.036621 | -0.05951 | 0.24261 | 0.16937 | 0.13275 | -0.032044 | 0.13733 | 0.10529 | -0.13275 | 0.20599 | -0.022888 | -0.12817 | 0 | 121.6095 | 121.637 | 17.9306 | -121.6324 | 121.5363 | 121.669 | 13.3209 | -121.5637
1545.6562 | 121.7148 | -0.21973 | 121.4218 | -0.012589 | 0.0016641 | 0.065614 | 0.0033838 | 0.065407 | -0.0027087 | 0.0043109 | -0.0054932 | -0.0081155 | 0.066757 | 0.06761 | -0.20254 | -0.0024118 | 121.3943 | 0.082397 | 17.8162 | -0.045776 | 121.3394 | -0.10071 | -0.16937 | -0.032043 | 13.0966 | -0.20142 | 121.2616 | 121.4401 | -0.073242 | -0.10986 | 0.11902 | 0.050354 | -0.082397 | 0.30212 | 0.17395 | 0.1236 | -0.027466 | 0.14649 | 0.10986 | -0.16022 | 0.18768 | 0.018311 | -0.091553 | 0.018311 | 121.5591 | 121.6141 | 18.0359 | -121.5912 | 121.4813 | 121.6599 | 13.3163 | -121.5317
1547.4219 | 121.7468 | -0.17853 | 121.431 | 0.0026703 | 0.0033731 | 0.065828 | -0.00024778 | 0.067971 | -0.00035893 | 0.0019611 | -0.0054932 | -0.0036295 | 0.063766 | 0.06761 | -0.1987 | -0.0047616 | 121.4447 | 0.073242 | 17.894 | -0.022888 | 121.3623 | -0.086975 | -0.16022 | 0.013733 | 13.1927 | -0.15564 | 121.2616 | 121.4264 | -0.054932 | -0.09613 | 0.091553 | 0.018311 | -0.068664 | 0.25177 | 0.15564 | 0.13733 | 0.013733 | 0.1236 | 0.082398 | -0.16937 | 0.19226 | 0.022888 | -0.05951 | -0.004577 | 121.5408 | 121.6232 | 18.0725 | -121.5912 | 121.4401 | 121.6049 | 13.3713 | -121.5271
1549.125 | 121.7834 | -0.19226 | 121.4264 | -0.0049592 | 0.0061501 | 0.065828 | 0.002102 | 0.065834 | -0.00099973 | 0.00025206 | 0.0021363 | -0.0029885 | 0.064194 | 0.069319 | -0.19934 | -0.004548 | 121.3989 | 0.032043 | 17.9718 | -0.041199 | 121.3577 | -0.10529 | -0.18768 | 0.018311 | 13.2111 | -0.19684 | 121.2845 | 121.4447 | -0.050354 | -0.07782 | 0.086975 | 0.004578 | -0.068665 | 0.2243 | 0.15106 | 0.14648 | -0.027466 | 0.14191 | 0.11444 | -0.14191 | 0.21057 | -0.004577 | -0.11902 | 0.01831 | 121.55 | 121.5912 | 18.1641 | -121.6141 | 121.4767 | 121.637 | 13.4033 | -121.5042
1550.8906 | 121.6873 | -0.20599 | 121.4676 | 0.0026703 | 0.0082865 | 0.063692 | 0.003811 | 0.06498 | 0.0039135 | 0.00089286 | 0.0021363 | -0.0027749 | 0.06633 | 0.069105 | -0.20147 | -0.0036936 | 121.3486 | -0.045776 | 18.0359 | -0.086975 | 121.3852 | -0.13275 | -0.21515 | -0.073242 | 13.2523 | -0.25635 | 121.3165 | 121.4584 | -0.10071 | -0.1236 | 0.073243 | -0.009155 | -0.082397 | 0.16022 | 0.11902 | 0.12817 | -0.11902 | 0.10529 | 0.082398 | -0.15106 | 0.13275 | -0.050354 | -0.13275 | -0.009155 | 121.5912 | 121.5546 | 18.2419 | -121.6827 | 121.5225 | 121.6644 | 13.4583 | -121.5912
1552.5938 | 121.7834 | -0.19226 | 121.4447 | 0.0026703 | 0.0014505 | 0.068178 | 0.0012476 | 0.06498 | -0.0046313 | 3.8456e-05 | -0.0054932 | -0.0055521 | 0.064835 | 0.068037 | -0.20297 | -0.0047616 | 121.3989 | 0.082397 | 18.1915 | -0.027466 | 121.344 | -0.11444 | -0.17395 | -0.022888 | 13.3575 | -0.14191 | 121.2845 | 121.4539 | -0.059509 | -0.07782 | 0.07782 | 0.018311 | -0.10071 | 0.27466 | 0.16479 | 0.14648 | -0.045776 | 0.13275 | 0.11444 | -0.16022 | 0.16937 | 0.050354 | -0.064087 | 0.009155 | 121.5363 | 121.5912 | 18.3838 | -121.6187 | 121.4767 | 121.6461 | 13.5498 | -121.5225
1554.3594 | 121.7697 | -0.1831 | 121.431 | -0.012589 | 0.0040139 | 0.064974 | -0.002384 | 0.068184 | 0.0011365 | 3.8456e-05 | 0.0097658 | -0.0029885 | 0.06163 | 0.068678 | -0.19955 | -0.004548 | 121.3898 | 0.004578 | 18.1915 | -0.073242 | 121.4035 | -0.11902 | -0.19226 | -0.009155 | 13.3209 | -0.21057 | 121.3303 | 121.4493 | -0.050354 | -0.09613 | 0.064086 | -0.009156 | -0.027466 | 0.18768 | 0.10986 | 0.11902 | -0.041198 | 0.13275 | 0.086975 | -0.10071 | 0.17395 | -0.027466 | -0.11444 | 0.018311 | 121.5866 | 121.5729 | 18.3746 | -121.6232 | 121.5134 | 121.6324 | 13.504 | -121.5271
1556.125 | 121.6507 | -0.24719 | 121.4676 | 0.0026703 | 0.0059365 | 0.063692 | 0.00039302 | 0.065193 | 0.0045545 | 0.0013203 | -0.013123 | -0.00021152 | 0.065475 | 0.069746 | -0.19806 | -0.0036936 | 121.3394 | -0.068665 | 18.2739 | -0.10529 | 121.4081 | -0.12817 | -0.20599 | -0.10529 | 13.3255 | -0.33417 | 121.3486 | 121.4859 | -0.10529 | -0.13275 | 0.11902 | 0.041198 | -0.059509 | 0.17853 | 0.14191 | 0.10071 | -0.12817 | 0.14191 | 0.11444 | -0.11902 | 0.14191 | -0.086975 | -0.20142 | 0.018311 | 121.6553 | 121.5866 | 18.5211 | -121.6736 | 121.5958 | 121.7331 | 13.5727 | -121.6003
1557.875 | 121.6507 | -0.24261 | 121.463 | -0.0049592 | 0.0057229 | 0.063478 | -3.4178e-05 | 0.06498 | 0.00070927 | 0.0021747 | 0.0021363 | -0.00063872 | 0.063126 | 0.067182 | -0.19827 | -0.0021982 | 121.3257 | -0.068665 | 18.3243 | -0.09613 | 121.3989 | -0.14191 | -0.20599 | -0.11902 | 13.3392 | -0.32044 | 121.312 | 121.4859 | -0.091553 | -0.11902 | 0.10071 | 0.036621 | -0.064087 | 0.17395 | 0.14649 | 0.10986 | -0.13733 | 0.15106 | 0.1236 | -0.15106 | 0.1236 | -0.07782 | -0.20142 | 0.022888 | 121.6415 | 121.5683 | 18.5669 | -121.669 | 121.5546 | 121.7285 | 13.5818 | -121.582
1559.5781 | 121.7606 | -0.17395 | 121.4264 | -0.0049592 | 0.00059593 | 0.06711 | 0.002102 | 0.066475 | 0.00028207 | 0.00025206 | -0.0054932 | -0.0025613 | 0.062485 | 0.066328 | -0.20126 | -0.0032662 | 121.4264 | 0.086975 | 18.5486 | -0.022888 | 121.3348 | -0.10529 | -0.16022 | 0.013733 | 13.5406 | -0.16479 | 121.2616 | 121.4676 | -0.07782 | -0.082397 | 0.068664 | 0.013733 | -0.091553 | 0.26092 | 0.15106 | 0.13733 | 0 | 0.09613 | 0.091553 | -0.1648 | 0.18768 | 0.009155 | -0.082398 | 0.041198 | 121.5088 | 121.6003 | 18.7225 | -121.5866 | 121.4355 | 121.6415 | 13.7146 | -121.5088
1561.3438 | 121.7056 | -0.21515 | 121.4493 | 0.0026703 | 0.0048685 | 0.064546 | 0.002102 | 0.067971 | 0.0015637 | 3.8456e-05 | -0.0054932 | -0.0010659 | 0.065475 | 0.069959 | -0.19998 | -0.0039072 | 121.3715 | -0.009155 | 18.6172 | -0.064087 | 121.3898 | -0.14191 | -0.21057 | -0.050354 | 13.5773 | -0.25177 | 121.3211 | 121.4676 | -0.086975 | -0.12817 | 0.073242 | 0.004578 | -0.059509 | 0.20599 | 0.15106 | 0.14648 | -0.07782 | 0.12817 | 0.086975 | -0.12817 | 0.16479 | -0.036621 | -0.1236 | 0.01831 | 121.6049 | 121.5866 | 18.8324 | -121.6599 | 121.5363 | 121.6827 | 13.7924 | -121.5775
1563.1094 | 121.7285 | -0.21057 | 121.4172 | -0.0049592 | 0.0020913 | 0.066896 | -0.00046138 | 0.066048 | -0.0067675 | 0.0013203 | -0.0054932 | -0.0029885 | 0.064621 | 0.067396 | -0.20297 | -0.0024118 | 121.4264 | 0.1236 | 18.7912 | -0.022888 | 121.3394 | -0.09613 | -0.17395 | 0.004578 | 13.7054 | -0.14648 | 121.2799 | 121.4264 | -0.054932 | -0.10529 | 0.11444 | 0.036621 | -0.077819 | 0.33417 | 0.18768 | 0.15106 | 0.009156 | 0.15564 | 0.10529 | -0.13733 | 0.21515 | 0.064087 | -0.041198 | 0.009156 | 121.55 | 121.637 | 19.0018 | -121.5912 | 121.4905 | 121.637 | 13.916 | -121.5225
1564.8906 | 121.6827 | -0.2243 | 121.4584 | -0.012589 | 0.0042275 | 0.065614 | 0.0031702 | 0.067971 | 0.0011365 | -0.0014569 | -0.0054932 | -0.0038431 | 0.066116 | 0.067823 | -0.20254 | -0.002839 | 121.3303 | -0.032043 | 18.7592 | -0.082397 | 121.4035 | -0.14191 | -0.21515 | -0.10529 | 13.6414 | -0.28839 | 121.3531 | 121.4676 | -0.10071 | -0.1236 | 0.082397 | 0.009155 | -0.054932 | 0.19226 | 0.14191 | 0.13275 | -0.12817 | 0.1236 | 0.10071 | -0.10529 | 0.11902 | -0.064087 | -0.1648 | 0.009155 | 121.6278 | 121.5546 | 18.9835 | -121.6736 | 121.5775 | 121.6919 | 13.8657 | -121.582
1566.6562 | 121.6553 | -0.24719 | 121.463 | -0.0049592 | 0.011704 | 0.061128 | 0.0053064 | 0.065407 | 0.0028455 | 0.0013203 | -0.013123 | -0.0042703 | 0.068253 | 0.06825 | -0.2019 | -0.0024118 | 121.3165 | -0.07782 | 18.8049 | -0.11902 | 121.4035 | -0.13275 | -0.20599 | -0.091553 | 13.6093 | -0.30212 | 121.344 | 121.4722 | -0.082397 | -0.12817 | 0.11444 | 0.041198 | -0.05951 | 0.16937 | 0.12817 | 0.086975 | -0.14648 | 0.16479 | 0.11902 | -0.11902 | 0.15564 | -0.054932 | -0.17395 | 0.009155 | 121.6507 | 121.5637 | 19.0521 | -121.669 | 121.5912 | 121.7194 | 13.8565 | -121.5912
1568.3594 | 121.7743 | -0.1831 | 121.3989 | 0.0026703 | 0.0016641 | 0.066042 | -0.0021704 | 0.066689 | -0.00078613 | 0.0013203 | 0.0021363 | -0.0040567 | 0.064407 | 0.068464 | -0.20254 | -0.002839 | 121.4218 | 0.091553 | 19.0201 | -0.009155 | 121.3486 | -0.091553 | -0.15564 | 0.022888 | 13.7787 | -0.16479 | 121.3028 | 121.4447 | -0.050354 | -0.082397 | 0.091552 | 0.027465 | -0.050354 | 0.27466 | 0.17395 | 0.14649 | 0.022888 | 0.13275 | 0.10071 | -0.096131 | 0.20599 | 0.01831 | -0.082398 | 0.045776 | 121.5317 | 121.6049 | 19.2032 | -121.5546 | 121.4859 | 121.6278 | 13.9618 | -121.4813
1570.1406 | 121.6782 | -0.23804 | 121.4401 | -0.0049592 | 0.00080973 | 0.063051 | 0.00060662 | 0.066689 | 0.0030591 | 0.00067926 | 0.0021363 | -0.0012795 | 0.066116 | 0.068678 | -0.20019 | -0.0041208 | 121.3165 | -0.036621 | 18.988 | -0.10071 | 121.4127 | -0.12817 | -0.2243 | -0.10529 | 13.71 | -0.30212 | 121.3211 | 121.4722 | -0.10071 | -0.1236 | 0.10986 | 0.013733 | -0.027466 | 0.20142 | 0.13733 | 0.1236 | -0.1236 | 0.13733 | 0.11444 | -0.11902 | 0.13275 | -0.064087 | -0.17853 | 0.032043 | 121.6507 | 121.5546 | 19.2261 | -121.6644 | 121.5591 | 121.7102 | 13.9481 | -121.5637
1571.9062 | 121.7789 | -0.19684 | 121.4355 | -0.0049592 | 0.0023049 | 0.067751 | 0.0023156 | 0.066475 | -0.0067675 | -0.00017514 | -0.020752 | -0.0066201 | 0.062271 | 0.066755 | -0.2034 | -0.002839 | 121.4218 | 0.13275 | 19.2581 | -0.013733 | 121.3577 | -0.10071 | -0.15564 | 0.013733 | 13.9252 | -0.11902 | 121.2662 | 121.463 | -0.054932 | -0.10071 | 0.09613 | 0.041198 | -0.07782 | 0.32959 | 0.18311 | 0.14191 | -0.013733 | 0.14191 | 0.09613 | -0.16937 | 0.21057 | 0.077819 | -0.018311 | 0.027466 | 121.5546 | 121.6187 | 19.455 | -121.5912 | 121.463 | 121.6599 | 14.122 | -121.5363
1573.6094 | 121.7194 | -0.21057 | 121.463 | 0.0026703 | 0.00080973 | 0.065614 | 0.0014612 | 0.065193 | -0.0014269 | -0.0027387 | -0.013123 | -0.0042703 | 0.06398 | 0.066969 | -0.20361 | -0.0032662 | 121.3898 | 0.07782 | 19.2764 | -0.041199 | 121.3531 | -0.091553 | -0.15564 | -0.059509 | 13.8657 | -0.19684 | 121.2662 | 121.4218 | -0.064087 | -0.086975 | 0.11902 | 0.054931 | -0.10986 | 0.28839 | 0.16937 | 0.11444 | -0.073242 | 0.14648 | 0.1236 | -0.19684 | 0.15106 | 0.013733 | -0.10986 | -0.041199 | 121.5637 | 121.6003 | 19.487 | -121.6187 | 121.4767 | 121.6324 | 14.0762 | -121.55
1575.3906 | 121.7468 | -0.17853 | 121.4447 | -0.0049592 | 0.0031595 | 0.064974 | 0.0033838 | 0.06733 | -0.0033495 | -0.0012433 | -0.0054932 | -0.0053385 | 0.064621 | 0.06825 | -0.20297 | -0.0060434 | 121.4539 | 0.15564 | 19.4824 | 0 | 121.344 | -0.082397 | -0.18768 | 0.022888 | 14.0259 | -0.13275 | 121.2891 | 121.4035 | -0.036621 | -0.10071 | 0.096131 | -0.009155 | -0.10071 | 0.33417 | 0.17853 | 0.18768 | 0.009155 | 0.14191 | 0.07782 | -0.15564 | 0.20142 | 0.045777 | -0.032043 | -0.041199 | 121.5225 | 121.6324 | 19.6609 | -121.6324 | 121.4676 | 121.582 | 14.2044 | -121.5454
1577.0938 | 121.7239 | -0.20142 | 121.4722 | -0.012589 | 0.0014505 | 0.06711 | -0.00046138 | 0.06498 | -0.0014269 | -0.0010297 | -0.013123 | -0.0034159 | 0.063766 | 0.068037 | -0.20041 | -0.0030526 | 121.4264 | 0.09613 | 19.487 | -0.041199 | 121.344 | -0.10529 | -0.18768 | -0.004578 | 13.9664 | -0.17853 | 121.2936 | 121.4493 | -0.054932 | -0.10071 | 0.09613 | 0.013733 | -0.12817 | 0.29755 | 0.16022 | 0.14648 | -0.045776 | 0.14648 | 0.10071 | -0.17853 | 0.19684 | 0.022888 | -0.07782 | -0.022888 | 121.5454 | 121.6278 | 19.6884 | -121.6599 | 121.4951 | 121.6507 | 14.1678 | -121.5729
1578.8594 | 121.7239 | -0.21973 | 121.4722 | 0.0026703 | -4.4874e-05 | 0.06711 | -0.0021704 | 0.064553 | -0.0020679 | -0.0010297 | -0.013123 | -0.0059793 | 0.065262 | 0.066755 | -0.20276 | -0.0026254 | 121.4127 | 0.10071 | 19.5557 | -0.059509 | 121.3669 | -0.09613 | -0.17395 | -0.027466 | 14.0259 | -0.20142 | 121.3028 | 121.4264 | -0.059509 | -0.091553 | 0.1236 | 0.045777 | -0.10529 | 0.32044 | 0.16022 | 0.11444 | -0.059509 | 0.16022 | 0.12817 | -0.16937 | 0.19226 | 0.018311 | -0.10986 | -0.045776 | 121.5866 | 121.6324 | 19.7754 | -121.6461 | 121.5225 | 121.6461 | 14.2456 | -121.5637
1580.5781 | 121.7834 | -0.1831 | 121.4355 | 0.0026703 | 0.0033731 | 0.065187 | 0.00039302 | 0.068398 | 0.0011365 | -0.0023113 | 0.0097658 | -0.0027749 | 0.065048 | 0.067182 | -0.19998 | -0.0060434 | 121.4447 | 0.086975 | 19.6609 | -0.018311 | 121.3715 | -0.11444 | -0.17853 | 0.036621 | 14.1083 | -0.16937 | 121.2799 | 121.4127 | -0.045776 | -0.091553 | 0.068664 | 0.004577 | -0.064087 | 0.27008 | 0.16479 | 0.16022 | 0.009155 | 0.13733 | 0.091552 | -0.15564 | 0.21973 | 0.013732 | -0.07782 | -0.022888 | 121.5546 | 121.6278 | 19.8441 | -121.6141 | 121.463 | 121.5958 | 14.2914 | -121.5271
1582.3438 | 121.7514 | -0.19226 | 121.4447 | 0.0026703 | -4.4874e-05 | 0.066255 | 0.00039302 | 0.06498 | -0.0020679 | 0.00067926 | -0.0054932 | -0.0046975 | 0.063126 | 0.068891 | -0.20254 | -0.0019846 | 121.3989 | 0.068665 | 19.7296 | -0.050354 | 121.376 | -0.10529 | -0.1831 | -0.032043 | 14.1174 | -0.2243 | 121.2753 | 121.4401 | -0.09613 | -0.10529 | 0.086975 | 0.009156 | -0.068664 | 0.26093 | 0.14191 | 0.13275 | -0.045776 | 0.096131 | 0.086975 | -0.16937 | 0.16022 | -0.032043 | -0.11902 | -0.004577 | 121.5683 | 121.5912 | 19.9219 | -121.6278 | 121.4676 | 121.6324 | 14.3097 | -121.55
1584.0938 | 121.7926 | -0.20142 | 121.4401 | 0.0026703 | -0.0032493 | 0.068178 | -3.4178e-05 | 0.068611 | -0.0031359 | -0.00060234 | -0.013123 | -0.0064065 | 0.061417 | 0.06825 | -0.20083 | -0.0034798 | 121.3989 | 0.07782 | 19.8441 | -0.041199 | 121.3623 | -0.11902 | -0.1831 | -0.009155 | 14.2319 | -0.17853 | 121.2891 | 121.463 | -0.068665 | -0.073242 | 0.082397 | 0.018311 | -0.07782 | 0.27924 | 0.16022 | 0.14191 | -0.041199 | 0.13275 | 0.12817 | -0.15106 | 0.19226 | 0.022888 | -0.10529 | 0.022888 | 121.5637 | 121.6003 | 20.0455 | -121.6232 | 121.4905 | 121.6644 | 14.4333 | -121.5134
1585.875 | 121.7194 | -0.20599 | 121.4264 | 0.0103 | -0.0013267 | 0.06711 | -0.0015296 | 0.064553 | -0.00035893 | -0.00017514 | -0.013123 | -0.0042703 | 0.062057 | 0.068891 | -0.20254 | -0.001771 | 121.4127 | 0.11444 | 19.9448 | -0.050354 | 121.3577 | -0.10986 | -0.16937 | -0.004578 | 14.241 | -0.19684 | 121.2891 | 121.431 | -0.041199 | -0.082397 | 0.096131 | 0.036621 | -0.068665 | 0.32044 | 0.15564 | 0.11902 | -0.013733 | 0.1648 | 0.1236 | -0.13733 | 0.20142 | 0.009156 | -0.11444 | 0.004577 | 121.5637 | 121.6187 | 20.1508 | -121.5958 | 121.4951 | 121.637 | 14.447 | -121.5088
1587.5781 | 121.6507 | -0.24719 | 121.4905 | -0.0049592 | 0.0046549 | 0.061983 | 0.00082022 | 0.065193 | 0.0075451 | 0.0019611 | -0.0054932 | 2.078e-06 | 0.066116 | 0.070387 | -0.19763 | -0.0054026 | 121.3943 | 0.004578 | 19.9722 | -0.10071 | 121.4264 | -0.11444 | -0.20142 | -0.054932 | 14.241 | -0.31586 | 121.3531 | 121.4676 | -0.091553 | -0.11902 | 0.13275 | 0.045776 | -0.064087 | 0.25177 | 0.14648 | 0.10071 | -0.096131 | 0.15564 | 0.12817 | -0.13733 | 0.19226 | -0.068665 | -0.19684 | -0.022889 | 121.6736 | 121.6415 | 20.2194 | -121.6919 | 121.6003 | 121.7148 | 14.4882 | -121.6095
1589.3438 | 121.6644 | -0.23804 | 121.4813 | -0.0049592 | 0.0063639 | 0.065614 | 0.0042382 | 0.06733 | 6.8274e-05 | 0.0011067 | -0.0054932 | -0.0051247 | 0.064835 | 0.06761 | -0.2019 | -0.0032662 | 121.3531 | 0.009155 | 20.1096 | -0.11444 | 121.3898 | -0.13275 | -0.2243 | -0.086975 | 14.3326 | -0.3067 | 121.3486 | 121.4905 | -0.091553 | -0.13733 | 0.10529 | 0.013733 | -0.091552 | 0.24719 | 0.1236 | 0.10986 | -0.12817 | 0.14648 | 0.10071 | -0.13275 | 0.15106 | -0.068665 | -0.16937 | 0.009156 | 121.6278 | 121.5912 | 20.3476 | -121.7056 | 121.5866 | 121.7285 | 14.5706 | -121.6187
1591.1094 | 121.637 | -0.22888 | 121.463 | -0.0049592 | 0.0042275 | 0.066896 | -0.00024778 | 0.063698 | -0.0018543 | 0.0013203 | -0.0054932 | -0.0029885 | 0.063553 | 0.068037 | -0.2034 | -0.0039072 | 121.3577 | 0.041199 | 20.1965 | -0.091553 | 121.3989 | -0.13733 | -0.21973 | -0.09613 | 14.4012 | -0.27924 | 121.3486 | 121.5042 | -0.07782 | -0.13275 | 0.091553 | 0.009155 | -0.064087 | 0.27008 | 0.13733 | 0.12817 | -0.10529 | 0.15106 | 0.096131 | -0.11444 | 0.13275 | -0.050354 | -0.14648 | 0.041198 | 121.6278 | 121.5866 | 20.4254 | -121.6827 | 121.5775 | 121.7331 | 14.6301 | -121.5958
1592.875 | 121.6507 | -0.23804 | 121.4722 | -0.012589 | 0.0063639 | 0.06711 | 0.002102 | 0.066902 | -0.0029223 | 0.0011067 | 0.0021363 | -0.0029885 | 0.065262 | 0.067182 | -0.20382 | -0.0041208 | 121.4035 | 0.07782 | 20.3705 | -0.032043 | 121.3623 | -0.11444 | -0.19684 | -0.068665 | 14.4836 | -0.2655 | 121.2982 | 121.5042 | -0.07782 | -0.12817 | 0.1236 | 0.041199 | -0.10986 | 0.31586 | 0.20599 | 0.1648 | -0.068665 | 0.16022 | 0.10986 | -0.17395 | 0.16937 | -0.027466 | -0.13733 | 0.032043 | 121.6003 | 121.6415 | 20.6085 | -121.669 | 121.5363 | 121.7422 | 14.7217 | -121.6003
1594.6406 | 121.6507 | -0.24719 | 121.4767 | -0.012589 | 0.0087137 | 0.065187 | 0.0035974 | 0.066048 | 6.8274e-05 | 0.00046566 | -0.0054932 | -0.0053385 | 0.065048 | 0.068891 | -0.20212 | -0.0043344 | 121.3623 | 0.054932 | 20.4163 | -0.073242 | 121.4172 | -0.12817 | -0.19684 | -0.073242 | 14.502 | -0.2655 | 121.344 | 121.4722 | -0.11902 | -0.12817 | 0.11902 | 0.050354 | -0.05951 | 0.30212 | 0.17395 | 0.1236 | -0.11444 | 0.12817 | 0.11902 | -0.13275 | 0.17395 | -0.018311 | -0.13733 | -0.004578 | 121.6644 | 121.6095 | 20.6635 | -121.6736 | 121.5912 | 121.7194 | 14.7491 | -121.6049
1596.4062 | 121.637 | -0.23346 | 121.5134 | -0.012589 | 0.0063639 | 0.064974 | -3.4178e-05 | 0.06498 | 0.0060499 | 0.0036701 | 0.0021363 | -0.0029885 | 0.066544 | 0.069746 | -0.19998 | -0.002839 | 121.3989 | 0.059509 | 20.5032 | -0.073242 | 121.4264 | -0.13275 | -0.20599 | -0.027466 | 14.5752 | -0.27924 | 121.3486 | 121.4493 | -0.10529 | -0.1236 | 0.10071 | 0.027465 | -0.086975 | 0.29297 | 0.16022 | 0.13275 | -0.11444 | 0.12817 | 0.10986 | -0.16479 | 0.20599 | -0.045777 | -0.15564 | -0.064087 | 121.6599 | 121.6324 | 20.7367 | -121.7194 | 121.582 | 121.6827 | 14.8087 | -121.637
1598.1094 | 121.669 | -0.23346 | 121.4905 | -0.012589 | 0.0057229 | 0.065614 | 0.0025292 | 0.066262 | -0.0018543 | 3.8456e-05 | -0.020752 | -0.0034159 | 0.064621 | 0.06761 | -0.20212 | -0.001771 | 121.3394 | 0.018311 | 20.5856 | -0.10071 | 121.3989 | -0.14191 | -0.22888 | -0.10071 | 14.6255 | -0.2655 | 121.3257 | 121.4905 | -0.10071 | -0.13733 | 0.091552 | 0.004577 | -0.091553 | 0.25177 | 0.13275 | 0.12817 | -0.15106 | 0.13275 | 0.09613 | -0.16479 | 0.13275 | -0.032044 | -0.12817 | 0 | 121.6324 | 121.5729 | 20.8191 | -121.7194 | 121.5591 | 121.7239 | 14.859 | -121.6278
1599.875 | 121.669 | -0.24719 | 121.4767 | -0.0049592 | 0.0070047 | 0.066255 | 0.0014612 | 0.064339 | -0.0016405 | 0.0013203 | 0.0021363 | -0.0049111 | 0.064835 | 0.065901 | -0.20083 | -0.0030526 | 121.3074 | 0.036621 | 20.6818 | -0.10529 | 121.4035 | -0.13733 | -0.2243 | -0.091553 | 14.6851 | -0.29755 | 121.3211 | 121.4905 | -0.10986 | -0.13733 | 0.10986 | 0.022888 | -0.073243 | 0.28381 | 0.14191 | 0.11902 | -0.16937 | 0.13733 | 0.10986 | -0.15564 | 0.15564 | -0.050354 | -0.16022 | 0.013733 | 121.6507 | 121.5546 | 20.929 | -121.7011 | 121.5683 | 121.7377 | 14.9323 | -121.6141
1601.6406 | 121.7285 | -0.21057 | 121.431 | -0.0049592 | 0.0010233 | 0.064974 | 0.002102 | 0.063271 | -0.0016405 | -0.00081594 | 0.0021363 | -0.0051247 | 0.066544 | 0.066969 | -0.20511 | -0.0024118 | 121.3989 | 0.14191 | 20.8374 | -0.036621 | 121.376 | -0.10071 | -0.16479 | -0.009155 | 14.7766 | -0.19684 | 121.2845 | 121.4355 | -0.050354 | -0.091553 | 0.10986 | 0.045776 | -0.054931 | 0.35248 | 0.17395 | 0.12817 | -0.032043 | 0.16022 | 0.11902 | -0.14648 | 0.20142 | 0.013733 | -0.10529 | 0.004578 | 121.5866 | 121.6095 | 21.048 | -121.5958 | 121.4951 | 121.6461 | 14.9872 | -121.5225
1603.3594 | 121.669 | -0.23346 | 121.4584 | 0.0026703 | 0.0029459 | 0.065187 | 0.00017942 | 0.065407 | 0.0034863 | 0.00025206 | -0.0054932 | -0.0019205 | 0.06398 | 0.068037 | -0.19934 | -0.0049752 | 121.3211 | -0.004578 | 20.8191 | -0.09613 | 121.4264 | -0.12817 | -0.19226 | -0.064087 | 14.7446 | -0.3067 | 121.3577 | 121.4905 | -0.086975 | -0.13275 | 0.10528 | 0.041198 | -0.032043 | 0.22888 | 0.13733 | 0.096131 | -0.13733 | 0.14648 | 0.10071 | -0.10071 | 0.16937 | -0.073243 | -0.17395 | 0.032044 | 121.6599 | 121.5546 | 21.0526 | -121.6507 | 121.5912 | 121.7239 | 14.978 | -121.5912
1605.125 | 121.7285 | -0.21057 | 121.4447 | -0.0049592 | 0.0016641 | 0.069673 | -3.4178e-05 | 0.067543 | -0.0035633 | 0.0017475 | -0.0054932 | -0.0053385 | 0.062057 | 0.066114 | -0.19998 | -0.0030526 | 121.4264 | 0.15564 | 21.0297 | -0.032043 | 121.3486 | -0.091553 | -0.16022 | -0.004578 | 14.9094 | -0.18768 | 121.312 | 121.4676 | -0.054932 | -0.086975 | 0.11902 | 0.050354 | -0.09613 | 0.36621 | 0.17853 | 0.12817 | -0.01831 | 0.15564 | 0.1236 | -0.13275 | 0.20599 | 0.022888 | -0.10071 | 0.022888 | 121.5591 | 121.637 | 21.2402 | -121.6049 | 121.5225 | 121.6782 | 15.1199 | -121.5317
1606.9062 | 121.7651 | -0.18768 | 121.4264 | -0.0049592 | 0.0057229 | 0.063478 | 0.0016748 | 0.066262 | 0.0019909 | 0.0013203 | -0.013123 | -0.0046975 | 0.065689 | 0.069105 | -0.20126 | -0.0030526 | 121.3989 | 0.064087 | 21.0571 | -0.068665 | 121.4127 | -0.10986 | -0.1831 | 0.013733 | 14.9597 | -0.20142 | 121.3211 | 121.4401 | -0.054932 | -0.082397 | 0.07782 | 0.004578 | -0.013733 | 0.25177 | 0.11902 | 0.11444 | -0.027466 | 0.13275 | 0.10529 | -0.10529 | 0.20142 | -0.013733 | -0.11902 | 0.013733 | 121.6003 | 121.5866 | 21.2448 | -121.6095 | 121.5088 | 121.6278 | 15.1474 | -121.5088
1608.6719 | 121.6965 | -0.2243 | 121.4813 | -0.012589 | 0.0038003 | 0.066469 | 0.002102 | 0.067757 | -0.00099973 | -0.00038874 | -0.0054932 | -0.0032021 | 0.068466 | 0.068464 | -0.2034 | -0.0043344 | 121.344 | 0.036621 | 21.1578 | -0.086975 | 121.3943 | -0.13275 | -0.21973 | -0.064087 | 15.0101 | -0.27924 | 121.344 | 121.4859 | -0.10529 | -0.1236 | 0.091553 | 0.004577 | -0.086975 | 0.26093 | 0.13733 | 0.13275 | -0.13733 | 0.11902 | 0.10071 | -0.13733 | 0.16022 | -0.054932 | -0.15564 | 0.004578 | 121.6187 | 121.5683 | 21.3821 | -121.7011 | 121.5683 | 121.7102 | 15.2344 | -121.6049
1610.4375 | 121.6873 | -0.21057 | 121.4676 | -0.020218 | 0.0033731 | 0.064974 | 0.0044518 | 0.067757 | -0.0031359 | 0.00025206 | -0.013123 | -0.0055521 | 0.064835 | 0.070173 | -0.20297 | -0.0030526 | 121.4401 | 0.18768 | 21.405 | 0 | 121.3623 | -0.086975 | -0.15564 | 0.013733 | 15.1978 | -0.15564 | 121.2799 | 121.4401 | -0.050354 | -0.091553 | 0.1236 | 0.054931 | -0.10528 | 0.39825 | 0.21057 | 0.15564 | -0.027465 | 0.16022 | 0.11902 | -0.18768 | 0.2243 | 0.054931 | -0.064087 | -0.027465 | 121.5729 | 121.6507 | 21.6156 | -121.6232 | 121.4905 | 121.6507 | 15.4083 | -121.5591
1612.2188 | 121.7422 | -0.21973 | 121.4539 | -0.012589 | -0.00068567 | 0.066042 | -3.4178e-05 | 0.067543 | -0.0044177 | -0.00081594 | -0.0054932 | -0.0053385 | 0.063339 | 0.06761 | -0.20169 | -0.0034798 | 121.3898 | 0.13275 | 21.4096 | -0.050354 | 121.3577 | -0.086975 | -0.16937 | -0.027466 | 15.1428 | -0.20599 | 121.3028 | 121.4447 | -0.064087 | -0.091553 | 0.13275 | 0.050354 | -0.09613 | 0.35248 | 0.16937 | 0.11902 | -0.064086 | 0.15564 | 0.12817 | -0.15106 | 0.19226 | 0.013733 | -0.11444 | -0.009155 | 121.5775 | 121.6095 | 21.6293 | -121.6232 | 121.5225 | 121.6644 | 15.3625 | -121.5454
1613.9844 | 121.6919 | -0.21057 | 121.4722 | 0.0026703 | 0.0057229 | 0.065614 | 0.001034 | 0.067971 | 0.0019909 | 0.00089286 | 0.0021363 | -0.0042703 | 0.066544 | 0.06825 | -0.20041 | -0.0041208 | 121.3486 | 0.054932 | 21.4828 | -0.082397 | 121.4081 | -0.13733 | -0.21057 | -0.041199 | 15.2206 | -0.27008 | 121.3394 | 121.4767 | -0.09613 | -0.1236 | 0.073242 | 0 | -0.064087 | 0.2655 | 0.12817 | 0.12817 | -0.1236 | 0.11444 | 0.086975 | -0.13275 | 0.16937 | -0.05951 | -0.14649 | 0.004578 | 121.6187 | 121.5591 | 21.6934 | -121.6827 | 121.55 | 121.6873 | 15.4312 | -121.5958
1615.7031 | 121.6507 | -0.23346 | 121.4676 | -0.012589 | 0.0063639 | 0.064546 | -0.00067498 | 0.066475 | 0.0017773 | 0.0032429 | -0.0054932 | -0.00063872 | 0.065903 | 0.068891 | -0.1987 | -0.0024118 | 121.3623 | 0.054932 | 21.5561 | -0.091553 | 121.4081 | -0.13275 | -0.21515 | -0.068665 | 15.2206 | -0.31128 | 121.3257 | 121.4859 | -0.10529 | -0.12817 | 0.10071 | 0.01831 | -0.059509 | 0.28839 | 0.14191 | 0.1236 | -0.10528 | 0.12817 | 0.10528 | -0.14191 | 0.16479 | -0.07782 | -0.1831 | 0.018311 | 121.6415 | 121.5958 | 21.7895 | -121.6827 | 121.5591 | 121.7194 | 15.4541 | -121.5958
1617.4688 | 121.7377 | -0.1831 | 121.4493 | -0.012589 | -0.0011131 | 0.067751 | -0.0017432 | 0.065621 | -0.0052721 | 0.0011067 | -0.0054932 | -0.0049111 | 0.060562 | 0.067823 | -0.2019 | -0.0013436 | 121.4355 | 0.1831 | 21.7484 | -0.027466 | 121.3486 | -0.073242 | -0.16022 | 0.018311 | 15.3671 | -0.16479 | 121.2936 | 121.4584 | -0.054932 | -0.10071 | 0.10986 | 0.022888 | -0.10071 | 0.36621 | 0.15564 | 0.13275 | -0.013733 | 0.12817 | 0.082397 | -0.15564 | 0.20142 | 0.01831 | -0.064087 | 0.009155 | 121.5317 | 121.6187 | 21.9315 | -121.6095 | 121.4767 | 121.6415 | 15.5502 | -121.55
1619.1719 | 121.7834 | -0.17853 | 121.4447 | -0.012589 | -0.0021811 | 0.062837 | -3.4178e-05 | 0.066262 | -0.0046313 | -0.00038874 | -0.0054932 | -0.0083291 | 0.061203 | 0.066542 | -0.20297 | -0.00048921 | 121.3852 | 0.19226 | 21.8491 | -0.018311 | 121.3852 | -0.086975 | -0.16937 | 0 | 15.4861 | -0.14648 | 121.3028 | 121.4493 | -0.041199 | -0.086975 | 0.091553 | 0.009155 | -0.059509 | 0.37079 | 0.16022 | 0.15106 | -0.059509 | 0.13733 | 0.091553 | -0.14191 | 0.17853 | 0.032044 | -0.059509 | 0.004578 | 121.5637 | 121.5637 | 22.0276 | -121.6141 | 121.4813 | 121.6278 | 15.6647 | -121.5317
1620.9375 | 121.7697 | -0.17395 | 121.4584 | -0.012589 | 0.0046549 | 0.066042 | 0.0029566 | 0.066048 | -0.0035633 | 3.8456e-05 | -0.0054932 | -0.0081155 | 0.064194 | 0.066755 | -0.20404 | -0.0049752 | 121.4264 | 0.19226 | 21.9864 | -0.013733 | 121.3943 | -0.10529 | -0.17853 | 0.032043 | 15.5228 | -0.1236 | 121.3028 | 121.4127 | -0.064087 | -0.091553 | 0.068664 | -0.004578 | -0.064087 | 0.36621 | 0.16022 | 0.16479 | -0.032043 | 0.10986 | 0.082397 | -0.15564 | 0.20599 | 0.050354 | -0.032043 | -0.045776 | 121.5683 | 121.6003 | 22.1603 | -121.637 | 121.4767 | 121.5866 | 15.6967 | -121.55
1622.7031 | 121.7148 | -0.20599 | 121.4447 | 0.0026703 | 0.0014505 | 0.065828 | -0.00024778 | 0.066689 | -0.0027087 | -0.0016705 | -0.013123 | -0.0059793 | 0.062485 | 0.066328 | -0.20318 | -0.0013436 | 121.4264 | 0.15564 | 22.0184 | -0.064087 | 121.3715 | -0.07782 | -0.17853 | -0.004578 | 15.5182 | -0.21515 | 121.3074 | 121.4539 | -0.064087 | -0.086975 | 0.12817 | 0.027466 | -0.073242 | 0.36163 | 0.14191 | 0.11444 | -0.01831 | 0.14191 | 0.11902 | -0.13733 | 0.20142 | -0.009155 | -0.12817 | 0.009155 | 121.5775 | 121.6324 | 22.2244 | -121.6232 | 121.5134 | 121.6599 | 15.7242 | -121.5317
1624.4844 | 121.6919 | -0.21973 | 121.4584 | -0.0049592 | 0.0067911 | 0.06476 | 0.0014612 | 0.069466 | 0.0049817 | 0.0028155 | 0.0021363 | -0.00063872 | 0.065903 | 0.068037 | -0.20041 | -0.0058298 | 121.4081 | 0.10986 | 22.1283 | -0.036621 | 121.4127 | -0.12817 | -0.21973 | 0.009155 | 15.6006 | -0.23346 | 121.3394 | 121.4996 | -0.082397 | -0.11444 | 0.091553 | 0 | -0.045776 | 0.32959 | 0.18311 | 0.18311 | -0.050354 | 0.13733 | 0.10529 | -0.11902 | 0.22888 | -0.013732 | -0.11902 | 0.041199 | 121.6324 | 121.6278 | 22.348 | -121.6782 | 121.5591 | 121.7194 | 15.8203 | -121.5729
1626.2656 | 121.7331 | -0.18768 | 121.463 | -0.012589 | 0.00038233 | 0.064546 | -0.00088858 | 0.063698 | -0.0012133 | 0.0038837 | 0.0021363 | -0.0057657 | 0.062271 | 0.068464 | -0.20105 | -0.002839 | 121.463 | 0.20142 | 22.2565 | -0.004578 | 121.344 | -0.10529 | -0.16479 | 0.073242 | 15.683 | -0.16022 | 121.3074 | 121.4355 | -0.059509 | -0.086975 | 0.082397 | 0.022888 | -0.11902 | 0.3891 | 0.1831 | 0.16022 | 0 | 0.12817 | 0.10071 | -0.15564 | 0.26092 | 0.027466 | -0.073242 | -0.027466 | 121.5317 | 121.6507 | 22.4442 | -121.6278 | 121.4951 | 121.6232 | 15.8707 | -121.55
1627.9531 | 121.7056 | -0.22888 | 121.4722 | 0.0026703 | 0.0046549 | 0.063905 | 0.0012476 | 0.065621 | 0.0011365 | -0.00060234 | -0.013123 | -0.0017069 | 0.064621 | 0.068464 | -0.2019 | -0.0034798 | 121.3669 | 0.07782 | 22.2656 | -0.082397 | 121.4447 | -0.1236 | -0.21515 | -0.064087 | 15.6647 | -0.28839 | 121.3623 | 121.5088 | -0.086975 | -0.11902 | 0.10529 | 0.013733 | -0.027466 | 0.3067 | 0.14649 | 0.13275 | -0.10529 | 0.14191 | 0.10986 | -0.10986 | 0.16479 | -0.059509 | -0.16937 | 0.036621 | 121.6736 | 121.5958 | 22.4945 | -121.6873 | 121.5912 | 121.7377 | 15.8936 | -121.5912
1629.7344 | 121.7834 | -0.18768 | 121.431 | -0.0049592 | 0.0020913 | 0.066896 | 0.0014612 | 0.06263 | -0.0054859 | 0.00067926 | -0.0054932 | -0.0076883 | 0.062485 | 0.06526 | -0.20318 | -0.0024118 | 121.4447 | 0.23804 | 22.4991 | -0.018311 | 121.3531 | -0.091553 | -0.19684 | 0.027466 | 15.8478 | -0.11902 | 121.2891 | 121.4584 | -0.050354 | -0.064087 | 0.09613 | -0.009155 | -0.07782 | 0.42572 | 0.16937 | 0.17853 | 0.013733 | 0.13733 | 0.1236 | -0.14191 | 0.21515 | 0.068664 | -0.054932 | 0.027466 | 121.5408 | 121.6324 | 22.6868 | -121.6278 | 121.4767 | 121.6461 | 16.0355 | -121.4951
1631.4375 | 121.7056 | -0.23346 | 121.4676 | 0.0026703 | 0.0080727 | 0.06476 | 0.0025292 | 0.066689 | 0.0028455 | 0.0017475 | 0.0021363 | -0.0034159 | 0.066757 | 0.067823 | -0.20083 | -0.0060434 | 121.3898 | 0.082397 | 22.4716 | -0.073242 | 121.4355 | -0.11902 | -0.19684 | -0.009155 | 15.7791 | -0.26093 | 121.3669 | 121.5042 | -0.07782 | -0.1236 | 0.11444 | 0.036621 | -0.032043 | 0.31586 | 0.16022 | 0.1236 | -0.077819 | 0.15564 | 0.10986 | -0.10071 | 0.2243 | -0.027466 | -0.13733 | 0.036621 | 121.669 | 121.6232 | 22.7051 | -121.6644 | 121.6003 | 121.7377 | 16.0126 | -121.5912
1633.2031 | 121.6461 | -0.21057 | 121.4813 | -0.012589 | 0.0031595 | 0.066469 | -0.00024778 | 0.067971 | -0.0024951 | -0.00038874 | -0.0054932 | -0.0051247 | 0.063553 | 0.068464 | -0.20233 | -0.0034798 | 121.4127 | 0.1831 | 22.6776 | -0.022888 | 121.3852 | -0.10986 | -0.18768 | -0.027466 | 15.8844 | -0.2243 | 121.3348 | 121.463 | -0.054932 | -0.10529 | 0.10071 | 0.022888 | -0.09613 | 0.39368 | 0.18768 | 0.16479 | -0.068664 | 0.15564 | 0.10529 | -0.14648 | 0.18311 | -0.013733 | -0.11902 | -0.01831 | 121.5958 | 121.6232 | 22.8882 | -121.669 | 121.5454 | 121.6736 | 16.095 | -121.5866
1634.9844 | 121.6782 | -0.23346 | 121.4722 | -0.012589 | 0.0040139 | 0.06476 | 0.0025292 | 0.066902 | 0.0015637 | 0.00067926 | -0.013123 | -0.0032021 | 0.064407 | 0.070814 | -0.20382 | -0.0015572 | 121.3577 | 0.09613 | 22.6822 | -0.082397 | 121.4218 | -0.14191 | -0.20599 | -0.059509 | 15.8386 | -0.28381 | 121.3577 | 121.5179 | -0.07782 | -0.13275 | 0.091552 | 0.027465 | -0.050354 | 0.32959 | 0.15106 | 0.1236 | -0.11444 | 0.15564 | 0.10071 | -0.11444 | 0.17395 | -0.050354 | -0.15106 | 0.045776 | 121.6553 | 121.5912 | 22.9156 | -121.6782 | 121.5912 | 121.7514 | 16.0721 | -121.6049
1636.7031 | 121.6461 | -0.24261 | 121.463 | -0.0049592 | 0.0070047 | 0.065401 | 0.0018884 | 0.066475 | -0.0012133 | -0.0023113 | 0.0097658 | -0.0036295 | 0.064194 | 0.069746 | -0.20532 | -0.0036936 | 121.376 | 0.13733 | 22.8149 | -0.068665 | 121.3852 | -0.11444 | -0.20142 | -0.050354 | 15.921 | -0.2655 | 121.3257 | 121.5088 | -0.086975 | -0.10986 | 0.12817 | 0.041199 | -0.07782 | 0.37994 | 0.17395 | 0.13275 | -0.086975 | 0.15564 | 0.13275 | -0.13733 | 0.19226 | -0.022888 | -0.15564 | 0.045776 | 121.6278 | 121.6187 | 23.0576 | -121.6644 | 121.5683 | 121.7514 | 16.1636 | -121.5729
1638.4688 | 121.756 | -0.20599 | 121.4676 | -0.0049592 | 0.0044411 | 0.065401 | 0.00017942 | 0.06263 | 0.00092287 | 0.0015339 | -0.013123 | -0.0032021 | 0.06398 | 0.070173 | -0.19891 | -0.0047616 | 121.3577 | 0.10071 | 22.8424 | -0.11444 | 121.4218 | -0.13275 | -0.20599 | -0.036621 | 15.9714 | -0.27466 | 121.3211 | 121.4722 | -0.091553 | -0.10529 | 0.073243 | 0 | -0.045776 | 0.3067 | 0.091553 | 0.091553 | -0.10986 | 0.11444 | 0.10071 | -0.14648 | 0.16937 | -0.068664 | -0.16937 | 0.004578 | 121.6278 | 121.5637 | 23.0484 | -121.6736 | 121.5271 | 121.6782 | 16.1774 | -121.5729
1640.1719 | 121.7148 | -0.20599 | 121.4539 | -0.012589 | 0.0072183 | 0.06241 | 0.0031702 | 0.067116 | 0.00049567 | 0.0026019 | -0.0054932 | 0.0010703 | 0.065903 | 0.069746 | -0.20041 | -0.0054026 | 121.3486 | 0.068665 | 22.9385 | -0.09613 | 121.4218 | -0.1236 | -0.21057 | -0.059509 | 16.04 | -0.27924 | 121.3623 | 121.4905 | -0.086975 | -0.11902 | 0.082398 | -0.004577 | -0.032043 | 0.27466 | 0.10986 | 0.11444 | -0.10528 | 0.11902 | 0.086975 | -0.091552 | 0.14649 | -0.073242 | -0.16022 | 0.036622 | 121.6278 | 121.5546 | 23.1445 | -121.6644 | 121.5683 | 121.6965 | 16.246 | -121.5729
1641.9375 | 121.7743 | -0.19226 | 121.4401 | -0.012589 | 0.00080973 | 0.069673 | 0.0027428 | 0.065834 | -0.0065539 | 0.00025206 | -0.0054932 | -0.0070475 | 0.063766 | 0.066328 | -0.20575 | -0.00048921 | 121.4264 | 0.22888 | 23.1766 | -0.018311 | 121.3806 | -0.073242 | -0.16937 | 0.050354 | 16.2643 | -0.11902 | 121.3074 | 121.4676 | -0.068665 | -0.086975 | 0.11902 | 0.022888 | -0.05951 | 0.42114 | 0.17395 | 0.15106 | -0.013733 | 0.1236 | 0.10529 | -0.13275 | 0.24261 | 0.073242 | -0.032044 | 0.027465 | 121.5729 | 121.6187 | 23.3688 | -121.6095 | 121.4996 | 121.6599 | 16.4566 | -121.5271
1643.7031 | 121.6965 | -0.21515 | 121.4722 | -0.0049592 | 0.0044411 | 0.064974 | -3.4178e-05 | 0.066689 | 0.0017773 | 0.00025206 | -0.0054932 | 0.00064308 | 0.060776 | 0.068037 | -0.20019 | -0.0056162 | 121.3806 | 0.10986 | 23.1903 | -0.07782 | 121.4218 | -0.12817 | -0.20599 | -0.018311 | 16.2231 | -0.24261 | 121.3531 | 121.5134 | -0.086975 | -0.10986 | 0.086975 | 0.009155 | -0.050354 | 0.32501 | 0.13733 | 0.12817 | -0.091553 | 0.12817 | 0.10529 | -0.11902 | 0.19684 | -0.027466 | -0.13275 | 0.041199 | 121.637 | 121.5958 | 23.4055 | -121.6782 | 121.5683 | 121.7285 | 16.4383 | -121.582
1645.4688 | 121.7743 | -0.19226 | 121.4264 | -0.012589 | 0.0018777 | 0.069032 | 0.0014612 | 0.066048 | -0.0059131 | 0.0021747 | -0.0054932 | -0.0066201 | 0.064407 | 0.065046 | -0.20447 | -0.0015572 | 121.4539 | 0.27924 | 23.4329 | -0.004578 | 121.3577 | -0.091553 | -0.15564 | 0.068665 | 16.4383 | -0.10529 | 121.2845 | 121.4676 | -0.064087 | -0.073242 | 0.10071 | 0.036621 | -0.068665 | 0.4715 | 0.18768 | 0.15106 | 0.027465 | 0.12817 | 0.11902 | -0.14191 | 0.26093 | 0.086975 | -0.032044 | 0.041198 | 121.55 | 121.6461 | 23.6252 | -121.582 | 121.4767 | 121.6599 | 16.6306 | -121.4996
1647.1875 | 121.6644 | -0.23804 | 121.4951 | -0.0049592 | 0.0059365 | 0.066042 | 0.001034 | 0.066902 | 0.0019909 | -0.0010297 | -0.0054932 | -0.0010659 | 0.066544 | 0.066755 | -0.20062 | -0.0030526 | 121.3531 | 0.1236 | 23.4009 | -0.091553 | 121.4035 | -0.15106 | -0.20599 | -0.068665 | 16.3605 | -0.27924 | 121.344 | 121.5042 | -0.086975 | -0.12817 | 0.086975 | 0.032043 | -0.091553 | 0.36163 | 0.14648 | 0.11444 | -0.14191 | 0.15106 | 0.10986 | -0.15106 | 0.16937 | -0.041199 | -0.15106 | 0.009155 | 121.6415 | 121.5912 | 23.6389 | -121.7011 | 121.582 | 121.7422 | 16.5985 | -121.6232
1648.9531 | 121.6827 | -0.20142 | 121.463 | -0.0049592 | 0.0082865 | 0.062837 | 0.0012476 | 0.065834 | 0.0030591 | 0.00067926 | -0.0054932 | -0.0012795 | 0.065475 | 0.069532 | -0.19934 | -0.0041208 | 121.4172 | 0.1831 | 23.5336 | -0.041199 | 121.3852 | -0.11902 | -0.19226 | 0.018311 | 16.4795 | -0.23804 | 121.3531 | 121.5088 | -0.091553 | -0.11444 | 0.082397 | 0.009155 | -0.07782 | 0.38452 | 0.16022 | 0.15106 | -0.045777 | 0.10986 | 0.086975 | -0.10986 | 0.21973 | -0.036621 | -0.1236 | 0.045776 | 121.5866 | 121.6187 | 23.735 | -121.6553 | 121.5546 | 121.7102 | 16.6809 | -121.5775
1650.7188 | 121.7789 | -0.19684 | 121.4401 | -0.0049592 | 0.0020913 | 0.066896 | 0.0035974 | 0.066048 | -0.0052721 | -0.00017514 | -0.0054932 | -0.0076883 | 0.065262 | 0.067823 | -0.20404 | -0.0013436 | 121.3577 | 0.20142 | 23.6298 | -0.045776 | 121.3715 | -0.11444 | -0.16937 | -0.009155 | 16.5207 | -0.18768 | 121.3074 | 121.4996 | -0.073242 | -0.11444 | 0.082397 | 0.027465 | -0.068665 | 0.39825 | 0.15106 | 0.1236 | -0.082398 | 0.1236 | 0.082397 | -0.13275 | 0.18768 | 0.009155 | -0.073242 | 0.059509 | 121.5683 | 121.5546 | 23.8266 | -121.6095 | 121.5042 | 121.6965 | 16.7175 | -121.5546
1652.4688 | 121.6599 | -0.21973 | 121.4722 | -0.012589 | 0.0067911 | 0.064546 | -0.0017432 | 0.064339 | 0.0045545 | -0.00060234 | -0.020752 | 0.00064308 | 0.065689 | 0.068464 | -0.20212 | -0.0041208 | 121.4264 | 0.19684 | 23.7213 | -0.045776 | 121.3852 | -0.13275 | -0.20599 | 0.032043 | 16.6122 | -0.24719 | 121.3394 | 121.4767 | -0.082397 | -0.11902 | 0.086976 | 0.013733 | -0.086975 | 0.41657 | 0.17395 | 0.16022 | -0.045776 | 0.13733 | 0.10071 | -0.13275 | 0.25177 | -0.027465 | -0.12817 | 0.004578 | 121.6049 | 121.6461 | 23.941 | -121.6782 | 121.5591 | 121.6965 | 16.832 | -121.5912
1654.25 | 121.6736 | -0.21515 | 121.4493 | -0.012589 | 0.0093545 | 0.06476 | 0.0033838 | 0.065193 | 0.0030591 | 0.0032429 | -0.020752 | -0.0032021 | 0.065475 | 0.069105 | -0.20105 | -0.0041208 | 121.4081 | 0.20599 | 23.8449 | -0.041199 | 121.4081 | -0.12817 | -0.20142 | 0.013733 | 16.7084 | -0.24261 | 121.3303 | 121.5179 | -0.068665 | -0.11444 | 0.086975 | 0.013733 | -0.041199 | 0.42114 | 0.17395 | 0.16022 | -0.041199 | 0.14648 | 0.10071 | -0.11902 | 0.22888 | -0.027466 | -0.12817 | 0.068664 | 121.6232 | 121.6232 | 24.0601 | -121.6507 | 121.5454 | 121.7331 | 16.9235 | -121.5637
1655.9531 | 121.7377 | -0.21515 | 121.4584 | -0.0049592 | 0.0023049 | 0.066469 | -0.00046138 | 0.066689 | -0.0042041 | 0.0023883 | 0.0021363 | -0.0064065 | 0.063126 | 0.068464 | -0.20147 | -0.0021982 | 121.4264 | 0.28839 | 23.9822 | -0.013733 | 121.3531 | -0.091553 | -0.16022 | 0.050354 | 16.7725 | -0.16022 | 121.2891 | 121.4859 | -0.050354 | -0.09613 | 0.1236 | 0.054932 | -0.10529 | 0.50354 | 0.20142 | 0.14648 | -0.032043 | 0.16479 | 0.11902 | -0.16937 | 0.2655 | 0.054932 | -0.064087 | 0.027466 | 121.5683 | 121.6415 | 24.1974 | -121.6187 | 121.5042 | 121.701 | 16.9876 | -121.5546
1657.6719 | 121.669 | -0.2243 | 121.4859 | -0.0049592 | 0.0057229 | 0.065187 | 0.00060662 | 0.066262 | 0.0034863 | 0.0017475 | -0.013123 | -0.00042512 | 0.064407 | 0.067396 | -0.19998 | -0.0030526 | 121.4127 | 0.21057 | 24.0326 | -0.050354 | 121.3943 | -0.11902 | -0.18768 | 0.018311 | 16.864 | -0.22888 | 121.3211 | 121.5134 | -0.07782 | -0.10529 | 0.10529 | 0.036621 | -0.091553 | 0.43488 | 0.17395 | 0.13733 | -0.073242 | 0.14648 | 0.11902 | -0.16479 | 0.24261 | -0.004578 | -0.1236 | 0.027466 | 121.6187 | 121.637 | 24.2569 | -121.6736 | 121.5454 | 121.7377 | 17.0883 | -121.5912
1659.4375 | 121.7148 | -0.23346 | 121.4722 | 0.0026703 | 0.0048685 | 0.064333 | -0.00067498 | 0.065834 | -0.0012133 | 0.0019611 | 0.0097658 | -0.0019205 | 0.064621 | 0.066542 | -0.19891 | -0.0015572 | 121.3394 | 0.12817 | 24.0463 | -0.086975 | 121.431 | -0.13733 | -0.21973 | -0.059509 | 16.7862 | -0.28381 | 121.3486 | 121.5179 | -0.091553 | -0.10529 | 0.09613 | 0.013732 | -0.041199 | 0.36163 | 0.14648 | 0.13275 | -0.13275 | 0.14191 | 0.12817 | -0.1236 | 0.17395 | -0.050354 | -0.17853 | 0.045776 | 121.6644 | 121.5729 | 24.2798 | -121.6919 | 121.582 | 121.7514 | 17.0197 | -121.5775
1661.1406 | 121.7377 | -0.21515 | 121.4584 | -0.012589 | 0.00059593 | 0.067323 | 0.0023156 | 0.066902 | -0.0056995 | -0.00060234 | -0.013123 | -0.0087563 | 0.063766 | 0.066328 | -0.20276 | -0.0019846 | 121.3898 | 0.25635 | 24.2706 | -0.059509 | 121.3577 | -0.10529 | -0.16937 | 0 | 16.9601 | -0.19684 | 121.2982 | 121.4676 | -0.064087 | -0.082397 | 0.10986 | 0.045776 | -0.10071 | 0.4715 | 0.15564 | 0.10986 | -0.068664 | 0.15106 | 0.13275 | -0.16022 | 0.21515 | 0.018311 | -0.11444 | 0.009155 | 121.5729 | 121.6049 | 24.4858 | -121.6278 | 121.5134 | 121.6827 | 17.1753 | -121.5408
1662.9062 | 121.7697 | -0.17395 | 121.4355 | -0.020218 | 0.0025185 | 0.062196 | 0.00060662 | 0.068398 | -0.0018543 | 0.0015339 | -0.0054932 | -0.0038431 | 0.065475 | 0.067823 | -0.20041 | -0.002839 | 121.4447 | 0.29755 | 24.3988 | -0.009155 | 121.3577 | -0.073242 | -0.17853 | 0.082397 | 17.0792 | -0.15106 | 121.312 | 121.4676 | -0.050354 | -0.07782 | 0.10071 | -0.004578 | -0.07782 | 0.4715 | 0.16479 | 0.16937 | 0.009155 | 0.1236 | 0.09613 | -0.1236 | 0.25635 | 0.022888 | -0.073242 | 0.032043 | 121.5317 | 121.6187 | 24.5728 | -121.6141 | 121.4859 | 121.6415 | 17.2531 | -121.5134
1664.6719 | 121.7651 | -0.1831 | 121.4401 | -0.0049592 | 0.0033731 | 0.066896 | -0.0011024 | 0.065407 | -0.00078613 | -0.0016705 | -0.020752 | -0.0049111 | 0.063339 | 0.066969 | -0.20105 | -0.0021982 | 121.4493 | 0.29755 | 24.5132 | -0.009155 | 121.3943 | -0.10986 | -0.15564 | 0.073242 | 17.1799 | -0.15564 | 121.2891 | 121.4767 | -0.036621 | -0.073242 | 0.073242 | 0.027465 | -0.045777 | 0.48065 | 0.17395 | 0.14649 | 0.009155 | 0.14648 | 0.10986 | -0.15106 | 0.25635 | 0.027465 | -0.082398 | 0.036621 | 121.5775 | 121.6324 | 24.6964 | -121.5958 | 121.4722 | 121.6599 | 17.363 | -121.5134
1666.4375 | 121.7697 | -0.17853 | 121.4493 | -0.012589 | 0.00016873 | 0.065614 | -0.0015296 | 0.065407 | 0.00092287 | 0.0011067 | -0.013123 | -0.0044839 | 0.06163 | 0.067823 | -0.1987 | -0.0036936 | 121.4584 | 0.30212 | 24.6094 | 0.004578 | 121.3715 | -0.09613 | -0.16022 | 0.09613 | 17.2165 | -0.15106 | 121.2936 | 121.4676 | -0.064087 | -0.082397 | 0.082398 | 0.018311 | -0.07782 | 0.48065 | 0.18311 | 0.16479 | 0.009155 | 0.11444 | 0.096131 | -0.15564 | 0.27466 | 0.027466 | -0.068665 | 0.01831 | 121.55 | 121.637 | 24.7879 | -121.6095 | 121.4722 | 121.6461 | 17.395 | -121.5317
1668.1406 | 121.8063 | -0.19226 | 121.4355 | -0.012589 | -0.00025847 | 0.065187 | 0.003811 | 0.065407 | -0.0046313 | -0.0014569 | -0.013123 | -0.0076883 | 0.066544 | 0.064405 | -0.20447 | -0.0034798 | 121.3943 | 0.25177 | 24.7055 | -0.027466 | 121.3715 | -0.10071 | -0.16937 | 0.022888 | 17.2577 | -0.16479 | 121.3394 | 121.4584 | -0.054932 | -0.086975 | 0.091553 | 0.022888 | -0.064087 | 0.44403 | 0.16479 | 0.14191 | -0.041199 | 0.13733 | 0.10529 | -0.09613 | 0.21515 | 0.027466 | -0.07782 | 0.022888 | 121.5637 | 121.5866 | 24.8978 | -121.6049 | 121.5317 | 121.6507 | 17.45 | -121.5225
1669.9219 | 121.7056 | -0.20142 | 121.4539 | -0.012589 | 0.0040139 | 0.062624 | 0.0023156 | 0.065407 | 0.0043409 | 0.00089286 | -0.0054932 | -0.0025613 | 0.064194 | 0.06825 | -0.20105 | -0.0058298 | 121.376 | 0.16479 | 24.6918 | -0.091553 | 121.4264 | -0.13733 | -0.20599 | -0.018311 | 17.2211 | -0.30212 | 121.3623 | 121.5317 | -0.068665 | -0.1236 | 0.064087 | -0.004578 | -0.027465 | 0.36621 | 0.10986 | 0.11444 | -0.077819 | 0.13275 | 0.07782 | -0.091552 | 0.18311 | -0.10071 | -0.17853 | 0.07782 | 121.6278 | 121.5775 | 24.8932 | -121.6599 | 121.5637 | 121.7331 | 17.4225 | -121.5775
1671.625 | 121.7102 | -0.22888 | 121.4401 | -0.0049592 | 0.0050821 | 0.068605 | 0.00552 | 0.066689 | 6.8274e-05 | 0.0028155 | -0.0054932 | -0.0032021 | 0.066971 | 0.06761 | -0.20254 | -0.0049752 | 121.344 | 0.18768 | 24.8383 | -0.10071 | 121.4355 | -0.15106 | -0.2243 | -0.032043 | 17.3538 | -0.28381 | 121.3898 | 121.5088 | -0.10071 | -0.1236 | 0.07782 | 0.004578 | -0.004578 | 0.41656 | 0.12817 | 0.1236 | -0.096131 | 0.12817 | 0.10529 | -0.050354 | 0.19684 | -0.054931 | -0.16022 | 0.068664 | 121.6644 | 121.5729 | 25.0671 | -121.6644 | 121.6187 | 121.7377 | 17.5827 | -121.5637
1673.3906 | 121.701 | -0.21515 | 121.4676 | 0.0026703 | 0.0067911 | 0.06476 | 0.0014612 | 0.06733 | 0.0019909 | 0.0011067 | -0.0054932 | -0.0023477 | 0.065689 | 0.070814 | -0.2019 | -0.0032662 | 121.3531 | 0.21973 | 24.939 | -0.086975 | 121.4035 | -0.13275 | -0.19226 | -0.009155 | 17.4728 | -0.28381 | 121.3623 | 121.5134 | -0.091553 | -0.10986 | 0.082398 | 0.022888 | -0.064087 | 0.43488 | 0.12817 | 0.10529 | -0.11444 | 0.1236 | 0.10529 | -0.10528 | 0.20599 | -0.068664 | -0.17395 | 0.045777 | 121.6187 | 121.5683 | 25.1541 | -121.6599 | 121.5775 | 121.7285 | 17.688 | -121.5775
1675.0938 | 121.6599 | -0.24261 | 121.4722 | 0.0026703 | 0.0055093 | 0.067323 | 0.001034 | 0.066475 | -0.0039905 | 0.00067926 | -0.013123 | -0.0029885 | 0.063553 | 0.066328 | -0.20297 | -0.00091641 | 121.4081 | 0.3067 | 25.1221 | -0.036621 | 121.3898 | -0.12817 | -0.17853 | 0 | 17.5735 | -0.24719 | 121.3257 | 121.5088 | -0.086975 | -0.11902 | 0.11444 | 0.064087 | -0.082397 | 0.54932 | 0.20599 | 0.14191 | -0.064087 | 0.15564 | 0.1236 | -0.14648 | 0.24261 | -0.004577 | -0.12817 | 0.036621 | 121.6324 | 121.6507 | 25.3647 | -121.6507 | 121.5683 | 121.7514 | 17.8162 | -121.5912
1676.875 | 121.7148 | -0.2243 | 121.4539 | 0.0026703 | 0.0055093 | 0.064333 | 0.0023156 | 0.066902 | 0.0032727 | 0.0019611 | -0.013123 | -0.0019205 | 0.063553 | 0.06761 | -0.20019 | -0.0034798 | 121.376 | 0.2243 | 25.1541 | -0.064087 | 121.431 | -0.1236 | -0.19684 | 0.009155 | 17.6697 | -0.26093 | 121.3531 | 121.5134 | -0.073242 | -0.11444 | 0.10071 | 0.027466 | -0.022888 | 0.44861 | 0.16022 | 0.13275 | -0.077819 | 0.15106 | 0.10986 | -0.10071 | 0.23346 | -0.036621 | -0.14648 | 0.05951 | 121.6553 | 121.6003 | 25.3784 | -121.6507 | 121.5775 | 121.7377 | 17.894 | -121.5683
1678.6406 | 121.7377 | -0.21515 | 121.4218 | -0.0049592 | 0.00038233 | 0.067323 | 0.0014612 | 0.066048 | -0.0050585 | 0.0013203 | 0.0021363 | -0.0068337 | 0.062485 | 0.068891 | -0.20361 | -0.0024118 | 121.376 | 0.32959 | 25.3143 | -0.050354 | 121.3852 | -0.09613 | -0.16937 | 0.018311 | 17.72 | -0.20599 | 121.3211 | 121.4951 | -0.054932 | -0.11444 | 0.11902 | 0.045776 | -0.036621 | 0.54474 | 0.16479 | 0.11902 | -0.045776 | 0.16022 | 0.10071 | -0.10071 | 0.23346 | 0.009155 | -0.091553 | 0.073242 | 121.6003 | 121.5912 | 25.5295 | -121.5912 | 121.5363 | 121.7102 | 17.9352 | -121.5363
1680.4062 | 121.7102 | -0.23346 | 121.4493 | -0.0049592 | 0.0033731 | 0.065401 | 0.0012476 | 0.066048 | 0.0039135 | 0.00089286 | 0.0021363 | -0.0029885 | 0.064835 | 0.067823 | -0.20019 | -0.0068978 | 121.3486 | 0.21057 | 25.3281 | -0.091553 | 121.4035 | -0.11902 | -0.21057 | -0.022888 | 17.7063 | -0.29755 | 121.3623 | 121.5134 | -0.091553 | -0.11902 | 0.11444 | 0.022888 | -0.045777 | 0.44403 | 0.14191 | 0.11902 | -0.10071 | 0.14191 | 0.11444 | -0.086975 | 0.21057 | -0.064087 | -0.17853 | 0.064087 | 121.637 | 121.582 | 25.5615 | -121.6599 | 121.5958 | 121.7468 | 17.9398 | -121.5683
1682.125 | 121.7789 | -0.20142 | 121.4539 | 0.0026703 | 0.0031595 | 0.065828 | 0.0042382 | 0.06733 | -0.0063403 | -0.0010297 | -0.0054932 | -0.0070475 | 0.065475 | 0.066114 | -0.20425 | -0.0024118 | 121.4127 | 0.36621 | 25.5798 | -0.022888 | 121.376 | -0.10986 | -0.16937 | 0.07782 | 17.9352 | -0.13733 | 121.312 | 121.4447 | -0.050354 | -0.086975 | 0.091553 | 0.032043 | -0.077819 | 0.56763 | 0.17853 | 0.14649 | -0.041198 | 0.15106 | 0.11444 | -0.14191 | 0.27924 | 0.064087 | -0.050354 | -0.009155 | 121.5775 | 121.6141 | 25.7812 | -121.6232 | 121.5134 | 121.6461 | 18.1366 | -121.5408
1683.8906 | 121.7194 | -0.21515 | 121.4355 | -0.012589 | 0.0042275 | 0.064119 | -0.0017432 | 0.064125 | 0.0030591 | 0.0019611 | 0.0021363 | 2.078e-06 | 0.064407 | 0.069319 | -0.19998 | -0.002839 | 121.3577 | 0.22888 | 25.5386 | -0.091553 | 121.4355 | -0.11902 | -0.21515 | -0.013733 | 17.8665 | -0.28839 | 121.3715 | 121.4767 | -0.068665 | -0.10986 | 0.09613 | 0 | 0 | 0.44403 | 0.1236 | 0.1236 | -0.07782 | 0.14648 | 0.10529 | -0.064087 | 0.20142 | -0.073242 | -0.17853 | 0.041199 | 121.6507 | 121.5729 | 25.7538 | -121.6507 | 121.5866 | 121.6919 | 18.0817 | -121.5454
1685.6562 | 121.6736 | -0.23346 | 121.4905 | -0.020218 | 0.0042275 | 0.066469 | 0.0035974 | 0.067757 | -0.0027087 | -0.00060234 | -0.0054932 | -0.0064065 | 0.063126 | 0.065901 | -0.20468 | -0.0019846 | 121.4401 | 0.40283 | 25.8316 | -0.004578 | 121.3531 | -0.10071 | -0.16479 | 0.064087 | 18.1183 | -0.16022 | 121.3028 | 121.4813 | -0.059509 | -0.086975 | 0.13275 | 0.068664 | -0.13733 | 0.63629 | 0.22888 | 0.16022 | -0.050354 | 0.17395 | 0.14648 | -0.18768 | 0.29755 | 0.073242 | -0.073242 | -0.009156 | 121.5866 | 121.6736 | 26.0651 | -121.6553 | 121.5363 | 121.7148 | 18.3517 | -121.5775
1687.4219 | 121.6278 | -0.21515 | 121.4767 | -0.012589 | 0.0061501 | 0.065187 | -0.00046138 | 0.065193 | 0.0039135 | 0.0030293 | -0.013123 | -0.0012795 | 0.065903 | 0.069532 | -0.19912 | -0.0030526 | 121.3806 | 0.30212 | 25.795 | -0.082397 | 121.4172 | -0.1236 | -0.21515 | 0.004578 | 18.0725 | -0.29755 | 121.3531 | 121.5042 | -0.07782 | -0.13275 | 0.091553 | 0 | -0.05951 | 0.51727 | 0.13275 | 0.13275 | -0.096131 | 0.13733 | 0.082398 | -0.1236 | 0.21973 | -0.082397 | -0.16479 | 0.027465 | 121.6324 | 121.5958 | 26.0101 | -121.6919 | 121.5683 | 121.7194 | 18.2877 | -121.6095
1689.125 | 121.7148 | -0.23346 | 121.4447 | 0.0026703 | 0.0080727 | 0.064546 | 0.00017942 | 0.06498 | 0.0022047 | 0.0023883 | -0.0054932 | -0.0038431 | 0.066544 | 0.068037 | -0.20147 | -0.0024118 | 121.3943 | 0.32959 | 25.9369 | -0.045776 | 121.4035 | -0.14191 | -0.2243 | 0.032043 | 18.1366 | -0.24261 | 121.3486 | 121.4996 | -0.091553 | -0.1236 | 0.091552 | 0.009155 | -0.041199 | 0.56305 | 0.18768 | 0.17853 | -0.050354 | 0.14191 | 0.10986 | -0.09613 | 0.2655 | -0.009156 | -0.11902 | 0.054932 | 121.637 | 121.6278 | 26.1703 | -121.669 | 121.582 | 121.7331 | 18.3701 | -121.5683
1690.9062 | 121.669 | -0.22888 | 121.4813 | 0.0103 | 0.0052957 | 0.066042 | 0.0046656 | 0.066689 | -0.0042041 | -0.0010297 | -0.013123 | -0.0046975 | 0.064621 | 0.067396 | -0.20425 | -0.001771 | 121.3623 | 0.32501 | 26.033 | -0.045776 | 121.4127 | -0.14191 | -0.21515 | -0.027466 | 18.1549 | -0.27466 | 121.3486 | 121.5317 | -0.09613 | -0.11902 | 0.086975 | 0.013733 | -0.068664 | 0.55389 | 0.18311 | 0.16937 | -0.11902 | 0.13275 | 0.10986 | -0.13275 | 0.20142 | -0.045776 | -0.15564 | 0.050354 | 121.6415 | 121.5912 | 26.2619 | -121.6965 | 121.5775 | 121.7606 | 18.3838 | -121.6003
1692.6875 | 121.637 | -0.23804 | 121.4859 | -0.0049592 | 0.0048685 | 0.064546 | -0.0015296 | 0.066689 | 0.0043409 | 0.0015339 | 0.0021363 | -0.0034159 | 0.065689 | 0.068037 | -0.19656 | -0.0034798 | 121.3898 | 0.35248 | 26.1383 | -0.064087 | 121.4081 | -0.1236 | -0.21515 | 0.022888 | 18.2602 | -0.27466 | 121.3211 | 121.4905 | -0.09613 | -0.11902 | 0.11444 | 0.022888 | -0.07782 | 0.59052 | 0.17395 | 0.15106 | -0.09613 | 0.14191 | 0.11902 | -0.16479 | 0.26093 | -0.036621 | -0.15564 | 0.004578 | 121.6461 | 121.6278 | 26.3763 | -121.701 | 121.5591 | 121.7285 | 18.4982 | -121.6049
1694.3906 | 121.6827 | -0.24261 | 121.4905 | 0.0026703 | 0.0061501 | 0.068178 | 0.00082022 | 0.066262 | -0.0029223 | -0.00017514 | 0.0021363 | -0.0034159 | 0.066971 | 0.06761 | -0.20361 | -0.0034798 | 121.344 | 0.30212 | 26.2024 | -0.091553 | 121.4264 | -0.14191 | -0.21515 | -0.041199 | 18.306 | -0.28839 | 121.3486 | 121.5408 | -0.10529 | -0.1236 | 0.10071 | 0.027466 | -0.064087 | 0.54474 | 0.15106 | 0.1236 | -0.14648 | 0.13733 | 0.11902 | -0.14191 | 0.20142 | -0.045776 | -0.1648 | 0.050354 | 121.669 | 121.5866 | 26.445 | -121.7056 | 121.5912 | 121.7834 | 18.5486 | -121.6141
1696.1562 | 121.7239 | -0.20599 | 121.4447 | -0.0049592 | 0.0020913 | 0.064974 | -0.0038794 | 0.067116 | -0.0044177 | 0.0015339 | 0.0021363 | -0.0053385 | 0.062698 | 0.066114 | -0.20254 | -0.00091641 | 121.4401 | 0.4303 | 26.4221 | -0.018311 | 121.3531 | -0.091553 | -0.15564 | 0.086975 | 18.4708 | -0.16479 | 121.3074 | 121.463 | -0.054932 | -0.091553 | 0.11444 | 0.050354 | -0.091553 | 0.63629 | 0.18768 | 0.13733 | -0.004577 | 0.15106 | 0.11444 | -0.13733 | 0.29297 | 0.041199 | -0.073242 | 0.018311 | 121.5591 | 121.6461 | 26.6281 | -121.6003 | 121.5134 | 121.669 | 18.6768 | -121.5363
1697.8594 | 121.7102 | -0.19226 | 121.4859 | -0.012589 | 0.0031595 | 0.066469 | 0.0012476 | 0.064125 | 0.0019909 | 0.00025206 | -0.013123 | -0.0023477 | 0.065262 | 0.06761 | -0.19955 | -0.0024118 | 121.3486 | 0.30212 | 26.3809 | -0.086975 | 121.4401 | -0.12817 | -0.20599 | -0.032043 | 18.4204 | -0.28381 | 121.3623 | 121.4996 | -0.091553 | -0.12817 | 0.064087 | -0.013733 | -0.045776 | 0.49438 | 0.10529 | 0.11902 | -0.13733 | 0.10071 | 0.064087 | -0.1236 | 0.16022 | -0.091552 | -0.15564 | 0.013733 | 121.6324 | 121.5408 | 26.5732 | -121.6919 | 121.5546 | 121.6919 | 18.6127 | -121.6141
1699.625 | 121.7194 | -0.22888 | 121.4767 | -0.012589 | 0.0072183 | 0.066896 | 0.0025292 | 0.065193 | -0.00057253 | -0.00017514 | 0.0021363 | -0.0021341 | 0.066971 | 0.068037 | -0.20105 | -0.0034798 | 121.3577 | 0.33417 | 26.5091 | -0.07782 | 121.4218 | -0.15106 | -0.20599 | -0.013733 | 18.6081 | -0.27008 | 121.3577 | 121.5042 | -0.09613 | -0.11444 | 0.07782 | 0.022888 | -0.054932 | 0.56305 | 0.15106 | 0.12817 | -0.11902 | 0.13275 | 0.11444 | -0.11902 | 0.21515 | -0.041199 | -0.15564 | 0.027465 | 121.6507 | 121.5866 | 26.738 | -121.6827 | 121.5866 | 121.7331 | 18.837 | -121.5912
1701.3281 | 121.7377 | -0.21057 | 121.4447 | -0.0049592 | 0.0042275 | 0.068178 | 0.0025292 | 0.066048 | -0.0046313 | -0.0020977 | -0.013123 | -0.0040567 | 0.064194 | 0.069319 | -0.20425 | -0.00070281 | 121.3989 | 0.45776 | 26.7151 | -0.032043 | 121.3623 | -0.09613 | -0.1831 | 0.041199 | 18.6722 | -0.18768 | 121.2936 | 121.4767 | -0.045776 | -0.082397 | 0.11444 | 0.027466 | -0.082397 | 0.66834 | 0.17853 | 0.15106 | -0.045776 | 0.1648 | 0.12817 | -0.15106 | 0.25177 | 0.022888 | -0.10529 | 0.032044 | 121.5729 | 121.6095 | 26.9257 | -121.6278 | 121.5042 | 121.6873 | 18.8828 | -121.5271
1703.1094 | 121.6736 | -0.23804 | 121.463 | 0.0103 | 0.0059365 | 0.066896 | 0.0033838 | 0.066262 | -0.0035633 | 3.8456e-05 | -0.013123 | -0.0053385 | 0.064194 | 0.065901 | -0.20511 | -0.004548 | 121.4264 | 0.47607 | 26.8433 | -0.009155 | 121.3715 | -0.09613 | -0.17853 | 0.073242 | 18.8553 | -0.18768 | 121.3211 | 121.5088 | -0.059509 | -0.11902 | 0.14191 | 0.059509 | -0.091553 | 0.71411 | 0.22888 | 0.16937 | -0.036621 | 0.17853 | 0.11902 | -0.14191 | 0.31128 | 0.050354 | -0.068664 | 0.045776 | 121.6095 | 121.6644 | 27.0813 | -121.6415 | 121.5591 | 121.7468 | 19.0933 | -121.582
1704.8125 | 121.6644 | -0.21973 | 121.4905 | 0.0026703 | 0.0055093 | 0.066683 | -0.0025976 | 0.065193 | 0.0034863 | 0.0019611 | -0.0054932 | -0.0017069 | 0.062912 | 0.068891 | -0.19848 | -0.0043344 | 121.376 | 0.31128 | 26.8112 | -0.091553 | 121.431 | -0.13733 | -0.21515 | -0.027466 | 18.782 | -0.3067 | 121.3623 | 121.5408 | -0.082397 | -0.11902 | 0.082398 | 0.004578 | -0.05951 | 0.53101 | 0.12817 | 0.1236 | -0.11444 | 0.13733 | 0.10071 | -0.12817 | 0.19226 | -0.086975 | -0.18768 | 0.050354 | 121.6507 | 121.5958 | 27.0309 | -121.7056 | 121.582 | 121.7606 | 19.0018 | -121.6095
1706.5781 | 121.6827 | -0.23346 | 121.4905 | -0.0049592 | 0.0014505 | 0.067964 | 0.00039302 | 0.066689 | -0.0050585 | -0.0016705 | -0.013123 | -0.0055521 | 0.064194 | 0.066969 | -0.20404 | -0.001771 | 121.4401 | 0.49439 | 27.0813 | 0 | 121.3577 | -0.10529 | -0.16479 | 0.091553 | 19.0338 | -0.15564 | 121.2982 | 121.4813 | -0.064087 | -0.082397 | 0.12817 | 0.068664 | -0.13275 | 0.72784 | 0.23346 | 0.16479 | -0.050354 | 0.16937 | 0.15106 | -0.19226 | 0.32501 | 0.077819 | -0.073243 | -0.009156 | 121.5912 | 121.6736 | 27.3148 | -121.6553 | 121.5317 | 121.7148 | 19.2673 | -121.5729
1708.3438 | 121.7789 | -0.17853 | 121.4493 | -0.012589 | 0.0023049 | 0.065401 | 0.00082022 | 0.067116 | -0.00014533 | 0.00089286 | -0.0054932 | -0.0057657 | 0.064835 | 0.069105 | -0.20297 | -0.0036936 | 121.4539 | 0.48065 | 27.1317 | 0.009155 | 121.376 | -0.10529 | -0.16022 | 0.10986 | 19.0704 | -0.16479 | 121.3074 | 121.4584 | -0.059509 | -0.10071 | 0.073242 | 0.018311 | -0.073242 | 0.65918 | 0.18768 | 0.16937 | 0.004577 | 0.11902 | 0.07782 | -0.14191 | 0.28839 | 0.013733 | -0.064087 | 0.009155 | 121.5546 | 121.6324 | 27.3102 | -121.6095 | 121.4859 | 121.637 | 19.249 | -121.55
1710.0469 | 121.6827 | -0.22888 | 121.4767 | 0.0103 | 0.0095681 | 0.065401 | 0.002102 | 0.067971 | 0.0026319 | 0.0015339 | 0.0021363 | 0.0014975 | 0.068039 | 0.069319 | -0.19998 | -0.0047616 | 121.4172 | 0.43488 | 27.182 | -0.050354 | 121.3989 | -0.12817 | -0.20142 | 0.064087 | 19.1483 | -0.23804 | 121.3577 | 121.4996 | -0.068665 | -0.13275 | 0.10071 | 0.027466 | -0.07782 | 0.66376 | 0.17853 | 0.15106 | -0.05951 | 0.16022 | 0.096131 | -0.11902 | 0.29297 | -0.009155 | -0.10529 | 0.022888 | 121.6278 | 121.6461 | 27.4109 | -121.6782 | 121.5866 | 121.7285 | 19.3771 | -121.6095
1711.8125 | 121.6599 | -0.23346 | 121.463 | -0.0049592 | 0.0082865 | 0.066042 | -0.001316 | 0.065193 | 0.0024183 | 0.0034565 | -0.013123 | -0.0019205 | 0.062698 | 0.070387 | -0.20019 | -0.0034798 | 121.4127 | 0.44403 | 27.2736 | -0.036621 | 121.3989 | -0.1236 | -0.21515 | 0.054932 | 19.1986 | -0.27924 | 121.344 | 121.5454 | -0.10071 | -0.12817 | 0.10986 | 0.01831 | -0.064087 | 0.67749 | 0.19684 | 0.17853 | -0.050354 | 0.13275 | 0.10528 | -0.11902 | 0.28839 | -0.045777 | -0.15106 | 0.082397 | 121.6324 | 121.6461 | 27.507 | -121.6782 | 121.5775 | 121.7789 | 19.4321 | -121.5912
1713.5938 | 121.7239 | -0.21057 | 121.4584 | -0.012589 | 0.0055093 | 0.064546 | 0.0016748 | 0.064339 | 6.8274e-05 | 0.0017475 | -0.0054932 | -0.0044839 | 0.065262 | 0.070387 | -0.20147 | -0.0024118 | 121.344 | 0.37537 | 27.3148 | -0.091553 | 121.4218 | -0.11444 | -0.2243 | 0 | 19.2444 | -0.29297 | 121.3531 | 121.5179 | -0.10529 | -0.10986 | 0.09613 | -0.013733 | -0.036621 | 0.58594 | 0.11902 | 0.13275 | -0.11444 | 0.10529 | 0.10071 | -0.10529 | 0.21057 | -0.082398 | -0.18311 | 0.059509 | 121.6324 | 121.5546 | 27.5253 | -121.6827 | 121.5637 | 121.7285 | 19.455 | -121.5683
1715.2969 | 121.701 | -0.2243 | 121.463 | -0.0049592 | 0.0042275 | 0.063051 | 0.00039302 | 0.065834 | 0.00049567 | 0.0015339 | -0.0054932 | -0.0023477 | 0.066544 | 0.067823 | -0.20062 | -0.0030526 | 121.3394 | 0.3891 | 27.4109 | -0.091553 | 121.4172 | -0.14191 | -0.20599 | -0.009155 | 19.3451 | -0.30212 | 121.3486 | 121.5225 | -0.09613 | -0.13275 | 0.082397 | 0.01831 | -0.045777 | 0.6134 | 0.13275 | 0.11444 | -0.1236 | 0.12817 | 0.091553 | -0.11444 | 0.21515 | -0.07782 | -0.16937 | 0.059509 | 121.6415 | 121.5637 | 27.6352 | -121.669 | 121.5729 | 121.7468 | 19.5694 | -121.5958
1717.0625 | 121.6965 | -0.22888 | 121.4767 | -0.0049592 | 0.0080727 | 0.066469 | 0.003811 | 0.065621 | -0.0042041 | 0.00067926 | 0.0021363 | -0.0066201 | 0.067184 | 0.065473 | -0.20361 | -0.0021982 | 121.3348 | 0.42572 | 27.5482 | -0.073242 | 121.4081 | -0.15564 | -0.21515 | 0.009155 | 19.5007 | -0.27008 | 121.3623 | 121.5225 | -0.091553 | -0.12817 | 0.073242 | 0.013733 | -0.068665 | 0.6546 | 0.15564 | 0.14191 | -0.14191 | 0.13733 | 0.10071 | -0.11444 | 0.23804 | -0.041199 | -0.14191 | 0.045776 | 121.637 | 121.5637 | 27.7771 | -121.6919 | 121.5912 | 121.7514 | 19.7296 | -121.6049
1718.7656 | 121.701 | -0.22888 | 121.463 | 0.0026703 | 0.0038003 | 0.067751 | 0.0031702 | 0.067116 | -0.0056995 | 0.00046566 | 0.0021363 | -0.0053385 | 0.063766 | 0.065901 | -0.20382 | -0.0032662 | 121.4035 | 0.57678 | 27.7771 | -0.004578 | 121.344 | -0.10071 | -0.16937 | 0.091553 | 19.7113 | -0.15564 | 121.2891 | 121.4859 | -0.059509 | -0.09613 | 0.12817 | 0.059509 | -0.11902 | 0.80566 | 0.2243 | 0.16479 | -0.05951 | 0.16937 | 0.13275 | -0.17395 | 0.32044 | 0.073242 | -0.05951 | 0.022888 | 121.5729 | 121.6324 | 28.006 | -121.6324 | 121.5179 | 121.7148 | 19.9402 | -121.5591
1720.5469 | 121.6599 | -0.24261 | 121.5042 | -0.012589 | 0.0025185 | 0.066683 | 0.0023156 | 0.066262 | -0.0035633 | -0.0025249 | -0.013123 | -0.0029885 | 0.062485 | 0.066114 | -0.20297 | -0.00091641 | 121.3715 | 0.5127 | 27.8229 | -0.041199 | 121.3989 | -0.11444 | -0.19684 | 0.018311 | 19.725 | -0.26093 | 121.3348 | 121.4905 | -0.086975 | -0.12817 | 0.12817 | 0.045777 | -0.10528 | 0.75531 | 0.20142 | 0.15564 | -0.13275 | 0.15564 | 0.11444 | -0.16937 | 0.26093 | -0.01831 | -0.13275 | -0.013732 | 121.6415 | 121.6141 | 28.0655 | -121.701 | 121.5775 | 121.7331 | 19.9677 | -121.6324
1722.3281 | 121.7468 | -0.21973 | 121.4767 | -0.012589 | 0.0040139 | 0.067964 | 0.0040246 | 0.065407 | -0.0046313 | -0.00081594 | -0.013123 | -0.0061929 | 0.064407 | 0.065046 | -0.20297 | -0.0015572 | 121.3669 | 0.54016 | 27.9236 | -0.036621 | 121.3989 | -0.10986 | -0.17853 | 0.050354 | 19.7525 | -0.19226 | 121.3074 | 121.463 | -0.068665 | -0.10529 | 0.10986 | 0.041199 | -0.07782 | 0.75989 | 0.18311 | 0.14191 | -0.10986 | 0.15106 | 0.11444 | -0.16937 | 0.27008 | 0.027466 | -0.086975 | -0.013733 | 121.6187 | 121.5866 | 28.1433 | -121.6553 | 121.5271 | 121.6827 | 19.9722 | -121.582
1724.0938 | 121.669 | -0.26093 | 121.4767 | -0.012589 | 0.0027323 | 0.066683 | 0.00082022 | 0.065621 | -0.0020679 | -0.00081594 | 0.0097658 | -0.0049111 | 0.066116 | 0.066114 | -0.2034 | -0.0049752 | 121.4081 | 0.59967 | 28.0472 | -0.027466 | 121.3623 | -0.12817 | -0.18768 | 0.045776 | 19.8578 | -0.2243 | 121.3211 | 121.4905 | -0.082397 | -0.10529 | 0.13275 | 0.073242 | -0.11444 | 0.86059 | 0.23346 | 0.16022 | -0.068665 | 0.17853 | 0.15564 | -0.15564 | 0.3067 | 0.036621 | -0.11902 | 0.013733 | 121.6232 | 121.669 | 28.3081 | -121.6644 | 121.582 | 121.7514 | 20.1187 | -121.582
1725.7969 | 121.8201 | -0.19684 | 121.4539 | -0.0049592 | 0.0048685 | 0.068391 | 0.0014612 | 0.062844 | -0.0042041 | -0.0010297 | -0.0054932 | -0.0055521 | 0.064407 | 0.067823 | -0.20404 | -0.0047616 | 121.4172 | 0.58594 | 28.1708 | -0.004578 | 121.3989 | -0.11444 | -0.17853 | 0.091553 | 19.9219 | -0.15564 | 121.2891 | 121.4859 | -0.059509 | -0.091553 | 0.082397 | 0.01831 | -0.054931 | 0.78277 | 0.19226 | 0.17395 | -0.036621 | 0.13733 | 0.10529 | -0.16479 | 0.28839 | 0.041198 | -0.064087 | 0.032044 | 121.5958 | 121.6141 | 28.3676 | -121.6324 | 121.4859 | 121.6827 | 20.1187 | -121.5454
1727.5781 | 121.7606 | -0.18768 | 121.4539 | -0.012589 | 0.0031595 | 0.065401 | -0.0011024 | 0.067116 | -0.00014533 | 0.0019611 | 0.0021363 | -0.0049111 | 0.065903 | 0.069105 | -0.20212 | -0.0054026 | 121.463 | 0.6134 | 28.2806 | -0.009155 | 121.3806 | -0.09613 | -0.16479 | 0.15106 | 19.9173 | -0.16937 | 121.3074 | 121.4401 | -0.059509 | -0.082397 | 0.091553 | 0.022888 | -0.073242 | 0.80109 | 0.17853 | 0.15564 | 0.009156 | 0.12817 | 0.10529 | -0.14648 | 0.33874 | 0.01831 | -0.086976 | -0.013732 | 121.5683 | 121.6507 | 28.4683 | -121.6187 | 121.4951 | 121.6278 | 20.105 | -121.5363
1729.3594 | 121.7422 | -0.21515 | 121.4767 | -0.0049592 | 0.0031595 | 0.06711 | 0.0027428 | 0.066902 | -0.0016405 | 0.0017475 | -0.013123 | -0.0046975 | 0.062057 | 0.064192 | -0.20169 | -0.0034798 | 121.4767 | 0.66834 | 28.4088 | -0.009155 | 121.376 | -0.10529 | -0.17395 | 0.11902 | 19.986 | -0.15564 | 121.3165 | 121.4493 | -0.068665 | -0.10986 | 0.10986 | 0.041199 | -0.10071 | 0.88348 | 0.20599 | 0.16479 | 0 | 0.14648 | 0.10529 | -0.16022 | 0.33417 | 0.059509 | -0.045777 | -0.027466 | 121.5912 | 121.6919 | 28.624 | -121.6507 | 121.5317 | 121.6644 | 20.2011 | -121.5866
1731.0469 | 121.7789 | -0.19226 | 121.4493 | -0.012589 | 0.0040139 | 0.066042 | -0.0036658 | 0.066048 | 0.0013501 | 3.8456e-05 | -0.0054932 | -0.0019205 | 0.062485 | 0.068037 | -0.20062 | -0.0049752 | 121.3898 | 0.53558 | 28.363 | -0.068665 | 121.4355 | -0.1236 | -0.20599 | 0.086975 | 19.9493 | -0.24719 | 121.3211 | 121.4951 | -0.082397 | -0.10071 | 0.068665 | -0.013733 | -0.013733 | 0.72784 | 0.1236 | 0.13733 | -0.059509 | 0.10986 | 0.091553 | -0.12817 | 0.27924 | -0.054931 | -0.14648 | 0.045776 | 121.6278 | 121.582 | 28.5553 | -121.6553 | 121.5134 | 121.6873 | 20.1416 | -121.55
1732.8281 | 121.7422 | -0.21515 | 121.4676 | -0.0049592 | 0.0044411 | 0.066042 | 0.0012476 | 0.065621 | -0.0020679 | 0.00046566 | -0.0054932 | -0.0032021 | 0.063126 | 0.067396 | -0.20233 | -0.002839 | 121.431 | 0.66376 | 28.5782 | -0.009155 | 121.3623 | -0.10986 | -0.15564 | 0.10986 | 19.9814 | -0.17853 | 121.3028 | 121.463 | -0.068665 | -0.11902 | 0.10529 | 0.059509 | -0.10528 | 0.87891 | 0.20599 | 0.14649 | -0.036621 | 0.14648 | 0.09613 | -0.16479 | 0.32501 | 0.036621 | -0.059509 | -0.004577 | 121.5775 | 121.6461 | 28.7933 | -121.6232 | 121.5179 | 121.6782 | 20.1965 | -121.5866
1734.5312 | 121.7697 | -0.19684 | 121.4447 | -0.012589 | -0.0043173 | 0.06946 | -0.003025 | 0.066902 | -0.0031359 | 0.0013203 | 0.0021363 | -0.0040567 | 0.061203 | 0.065046 | -0.20212 | -0.0047616 | 121.4676 | 0.70953 | 28.7109 | 0.004578 | 121.3669 | -0.11444 | -0.16937 | 0.14191 | 20.1874 | -0.14191 | 121.3028 | 121.4493 | -0.073242 | -0.091553 | 0.082397 | 0.027465 | -0.07782 | 0.90637 | 0.20142 | 0.17395 | 0.022888 | 0.1236 | 0.10529 | -0.14191 | 0.33875 | 0.054931 | -0.050354 | 0.004578 | 121.5637 | 121.6644 | 28.9078 | -121.6141 | 121.4996 | 121.6461 | 20.3842 | -121.5363
1736.2969 | 121.6553 | -0.24261 | 121.463 | 0.0026703 | 0.012345 | 0.063905 | 0.0029566 | 0.066262 | 0.0056225 | 0.00046566 | -0.013123 | 0.00042948 | 0.065475 | 0.069319 | -0.19934 | -0.0064706 | 121.4401 | 0.59509 | 28.7155 | -0.045776 | 121.4218 | -0.12817 | -0.20599 | 0.09613 | 20.0409 | -0.27466 | 121.344 | 121.5088 | -0.091553 | -0.12817 | 0.11444 | 0.036621 | -0.041199 | 0.83771 | 0.19684 | 0.16022 | -0.022888 | 0.15106 | 0.11444 | -0.11902 | 0.33874 | -0.032043 | -0.14648 | 0.045776 | 121.6644 | 121.6827 | 28.9581 | -121.669 | 121.5866 | 121.7514 | 20.2835 | -121.5912
1738 | 121.6919 | -0.24261 | 121.4584 | -0.0049592 | 0.0057229 | 0.064974 | -0.0011024 | 0.065834 | 0.0026319 | 0.0030293 | 0.0021363 | -0.0012795 | 0.06633 | 0.068037 | -0.19891 | -0.004548 | 121.3348 | 0.51727 | 28.7247 | -0.10529 | 121.4355 | -0.15106 | -0.21057 | 0.032043 | 20.0317 | -0.31586 | 121.3577 | 121.4905 | -0.09613 | -0.13733 | 0.091553 | 0.032044 | -0.022888 | 0.75989 | 0.13733 | 0.10529 | -0.1236 | 0.14649 | 0.10529 | -0.10071 | 0.27466 | -0.073242 | -0.17853 | 0.032044 | 121.6782 | 121.5775 | 28.9673 | -121.669 | 121.6003 | 121.7331 | 20.2744 | -121.5958
1739.7656 | 121.7148 | -0.22888 | 121.4813 | -0.012589 | 0.0061501 | 0.065614 | 0.0046656 | 0.06733 | -0.0022815 | 0.00089286 | -0.013123 | -0.0068337 | 0.064835 | 0.068678 | -0.20447 | -0.0036936 | 121.4218 | 0.72327 | 29.0222 | 0 | 121.3577 | -0.10529 | -0.16937 | 0.1236 | 20.2789 | -0.16479 | 121.3028 | 121.4447 | -0.086975 | -0.09613 | 0.1236 | 0.059509 | -0.1236 | 0.95215 | 0.22888 | 0.16937 | -0.059509 | 0.14191 | 0.13275 | -0.17853 | 0.35248 | 0.064087 | -0.068665 | -0.036621 | 121.5866 | 121.6507 | 29.2511 | -121.6507 | 121.5317 | 121.6736 | 20.5078 | -121.5775
1741.4688 | 121.756 | -0.21057 | 121.463 | -0.012589 | 0.00038233 | 0.068605 | -0.002384 | 0.066262 | -0.0014269 | 0.0017475 | -0.013123 | -0.0057657 | 0.063553 | 0.067182 | -0.20212 | -0.0021982 | 121.4218 | 0.70953 | 29.068 | -0.013733 | 121.3669 | -0.11444 | -0.17395 | 0.12817 | 20.2835 | -0.17395 | 121.312 | 121.4539 | -0.068665 | -0.10071 | 0.09613 | 0.036621 | -0.096131 | 0.9201 | 0.19684 | 0.16022 | -0.041199 | 0.14191 | 0.10986 | -0.15106 | 0.33875 | 0.036621 | -0.073242 | -0.009156 | 121.5775 | 121.6324 | 29.2786 | -121.637 | 121.5225 | 121.6644 | 20.4941 | -121.5637
1743.2344 | 121.7102 | -0.22888 | 121.4951 | 0.0026703 | 0.0057229 | 0.066255 | -3.4178e-05 | 0.066048 | 0.0030591 | 0.0011067 | 0.0021363 | -0.0029885 | 0.064407 | 0.069105 | -0.20019 | -0.0041208 | 121.3577 | 0.59967 | 29.0497 | -0.082397 | 121.3943 | -0.14191 | -0.23346 | 0.032043 | 20.3201 | -0.29755 | 121.3531 | 121.4767 | -0.10986 | -0.15106 | 0.086975 | -0.004577 | -0.10071 | 0.82855 | 0.14649 | 0.15106 | -0.13733 | 0.11902 | 0.07782 | -0.14191 | 0.26093 | -0.068664 | -0.14648 | -0.01831 | 121.6232 | 121.5866 | 29.2786 | -121.7285 | 121.582 | 121.7056 | 20.549 | -121.6461
1745.0156 | 121.7194 | -0.2243 | 121.4539 | 0.0026703 | 0.0059365 | 0.065401 | 0.0014612 | 0.063698 | 0.0028455 | 0.0023883 | 0.0021363 | -0.0036295 | 0.065475 | 0.068678 | -0.20041 | -0.0066842 | 121.344 | 0.59967 | 29.1183 | -0.086975 | 121.4127 | -0.15106 | -0.21515 | 0.027466 | 20.3659 | -0.31128 | 121.3348 | 121.4951 | -0.10071 | -0.14191 | 0.073242 | 0.009155 | -0.041198 | 0.82397 | 0.13733 | 0.12817 | -0.10986 | 0.1236 | 0.082397 | -0.11902 | 0.25177 | -0.086975 | -0.16937 | 0.041199 | 121.637 | 121.5683 | 29.3427 | -121.669 | 121.5591 | 121.7194 | 20.5902 | -121.5958
1746.7969 | 121.7834 | -0.19226 | 121.4355 | -0.0049592 | 0.0067911 | 0.065828 | 0.00039302 | 0.068184 | 0.0015637 | 0.0017475 | -0.013123 | -0.0034159 | 0.06398 | 0.066969 | -0.20147 | -0.0013436 | 121.3898 | 0.67749 | 29.2923 | -0.041199 | 121.4035 | -0.1236 | -0.20142 | 0.14191 | 20.5811 | -0.19226 | 121.2891 | 121.4539 | -0.082397 | -0.091553 | 0.068665 | -0.009155 | -0.032044 | 0.86975 | 0.15106 | 0.16022 | -0.045776 | 0.10986 | 0.10071 | -0.14648 | 0.33417 | 0 | -0.10071 | 0.01831 | 121.5958 | 121.582 | 29.4846 | -121.637 | 121.4813 | 121.6461 | 20.7733 | -121.5271
1748.5 | 121.6599 | -0.24719 | 121.4447 | -0.020218 | 0.0095681 | 0.064333 | 0.0027428 | 0.068398 | 0.0022047 | 0.0017475 | -0.0054932 | -0.0017069 | 0.065048 | 0.068678 | -0.20126 | -0.004548 | 121.4081 | 0.68665 | 29.393 | -0.050354 | 121.3898 | -0.13275 | -0.20599 | 0.09613 | 20.6406 | -0.28381 | 121.3303 | 121.4905 | -0.10071 | -0.11902 | 0.11444 | 0.041198 | -0.054931 | 0.93384 | 0.19684 | 0.15564 | -0.036621 | 0.14648 | 0.12817 | -0.11444 | 0.34332 | -0.036621 | -0.16479 | 0.045777 | 121.637 | 121.6553 | 29.6402 | -121.6507 | 121.5775 | 121.7377 | 20.8878 | -121.5637
1750.25 | 121.7422 | -0.23346 | 121.4447 | -0.0049592 | 0.00016873 | 0.06711 | -0.00067498 | 0.065193 | -0.0056995 | 0.0017475 | -0.028381 | -0.0074747 | 0.060989 | 0.065046 | -0.20147 | 0.00036539 | 121.3852 | 0.737 | 29.5029 | -0.041199 | 121.3623 | -0.12817 | -0.19226 | 0.068665 | 20.6772 | -0.21515 | 121.3211 | 121.4859 | -0.068665 | -0.10529 | 0.10528 | 0.041198 | -0.082397 | 0.97046 | 0.19226 | 0.15106 | -0.059509 | 0.16479 | 0.12817 | -0.1236 | 0.30212 | 0.01831 | -0.10986 | 0.041199 | 121.5958 | 121.6187 | 29.7363 | -121.637 | 121.5546 | 121.7194 | 20.9106 | -121.55
1752.0312 | 121.7972 | -0.17853 | 121.431 | -0.0049592 | 0.0057229 | 0.067323 | 0.0012476 | 0.067757 | -0.0069811 | 0.0015339 | -0.0054932 | -0.0059793 | 0.063553 | 0.064619 | -0.20425 | -0.00113 | 121.4172 | 0.78735 | 29.6448 | -0.013733 | 121.3577 | -0.10529 | -0.1831 | 0.11444 | 20.7962 | -0.13275 | 121.2845 | 121.4584 | -0.07782 | -0.10071 | 0.073242 | -0.004577 | -0.073242 | 0.96588 | 0.16479 | 0.16937 | -0.013733 | 0.10071 | 0.07782 | -0.14648 | 0.29297 | 0.045777 | -0.032043 | 0.027466 | 121.5363 | 121.5958 | 29.8233 | -121.6141 | 121.463 | 121.637 | 20.9747 | -121.5317
1753.75 | 121.6461 | -0.23804 | 121.4951 | -0.0049592 | 0.0055093 | 0.069032 | 0.00017942 | 0.06733 | 0.0013501 | -0.00017514 | -0.0054932 | -0.0010659 | 0.06398 | 0.067396 | -0.20382 | -0.0030526 | 121.3394 | 0.68665 | 29.631 | -0.09613 | 121.3898 | -0.16479 | -0.21973 | 0.013733 | 20.7962 | -0.29297 | 121.3715 | 121.5225 | -0.10986 | -0.14191 | 0.073242 | 0.01831 | -0.10529 | 0.92468 | 0.14191 | 0.1236 | -0.15564 | 0.12817 | 0.09613 | -0.1236 | 0.25177 | -0.054932 | -0.15106 | 0.027466 | 121.6278 | 121.5775 | 29.8691 | -121.7148 | 121.6095 | 121.7606 | 21.0342 | -121.637
1755.5156 | 121.7606 | -0.21057 | 121.4355 | 0.0026703 | 0.0029459 | 0.064333 | -0.001316 | 0.068184 | -0.00014533 | 0.00067926 | -0.013123 | -0.0055521 | 0.063339 | 0.06825 | -0.20233 | -0.0047616 | 121.4218 | 0.80566 | 29.8187 | 0 | 121.3486 | -0.091553 | -0.1831 | 0.15564 | 21.0297 | -0.17395 | 121.2982 | 121.4584 | -0.082397 | -0.10986 | 0.11902 | 0.027466 | -0.086975 | 1.0162 | 0.21057 | 0.1831 | -0.013733 | 0.12817 | 0.10071 | -0.13733 | 0.36621 | 0.036621 | -0.064087 | 0.022888 | 121.5591 | 121.6324 | 30.0293 | -121.6187 | 121.5088 | 121.669 | 21.2402 | -121.5454
1757.2969 | 121.7422 | -0.2243 | 121.431 | -0.012589 | -0.0021811 | 0.070314 | -0.0032386 | 0.066689 | -0.0052721 | -0.0016705 | -0.013123 | -0.0055521 | 0.06163 | 0.065901 | -0.20276 | -0.0021982 | 121.3715 | 0.79651 | 29.8553 | -0.050354 | 121.3623 | -0.10986 | -0.19226 | 0.07782 | 21.0342 | -0.2243 | 121.312 | 121.4584 | -0.07782 | -0.10071 | 0.11444 | 0.032043 | -0.068664 | 1.0208 | 0.17395 | 0.14191 | -0.059509 | 0.14648 | 0.1236 | -0.11902 | 0.30212 | 0 | -0.1236 | 0.027466 | 121.5866 | 121.5958 | 30.0797 | -121.6232 | 121.5363 | 121.6827 | 21.2585 | -121.5317
1759 | 121.7422 | -0.21057 | 121.4584 | -0.012589 | 0.0040139 | 0.06946 | -0.0019568 | 0.068825 | -0.00057253 | 0.00067926 | -0.0054932 | -0.0044839 | 0.062912 | 0.066328 | -0.20105 | -0.0030526 | 121.4172 | 0.82855 | 29.9927 | -0.027466 | 121.3531 | -0.11902 | -0.1831 | 0.10529 | 21.0846 | -0.19226 | 121.2982 | 121.4493 | -0.082397 | -0.1236 | 0.091552 | 0.027466 | -0.10529 | 1.0391 | 0.18311 | 0.15564 | -0.041199 | 0.12817 | 0.086975 | -0.16022 | 0.31586 | 0.01831 | -0.068665 | -0.009155 | 121.5637 | 121.6278 | 30.2032 | -121.6415 | 121.5088 | 121.6599 | 21.2952 | -121.582
1760.7656 | 121.6553 | -0.27466 | 121.4813 | -0.0049592 | 0.0052957 | 0.069032 | 0.0044518 | 0.069252 | 0.00049567 | -0.0014569 | -0.0054932 | -0.0044839 | 0.066116 | 0.066328 | -0.2019 | -0.0056162 | 121.3669 | 0.737 | 30.0018 | -0.091553 | 121.3852 | -0.15564 | -0.23346 | 0.022888 | 21.2173 | -0.29755 | 121.3669 | 121.4905 | -0.1236 | -0.15564 | 0.11902 | 0.041199 | -0.09613 | 1.0117 | 0.18311 | 0.14191 | -0.11444 | 0.15106 | 0.11902 | -0.11444 | 0.29755 | -0.022888 | -0.14191 | 0.009156 | 121.6599 | 121.6415 | 30.2765 | -121.7148 | 121.6415 | 121.7651 | 21.492 | -121.637
1762.5312 | 121.7422 | -0.2243 | 121.4447 | -0.0049592 | 0.0025185 | 0.067537 | 0.0012476 | 0.066689 | -0.0018543 | -0.00060234 | 0.0097658 | -0.0061929 | 0.06398 | 0.068678 | -0.20318 | -0.0032662 | 121.4218 | 0.8606 | 30.1437 | -0.032043 | 121.376 | -0.10986 | -0.17853 | 0.13275 | 21.3226 | -0.19684 | 121.2708 | 121.431 | -0.082397 | -0.11902 | 0.11444 | 0.045776 | -0.068664 | 1.0849 | 0.19226 | 0.14648 | -0.022888 | 0.14191 | 0.10529 | -0.17395 | 0.35706 | 0.027466 | -0.077819 | -0.013733 | 121.6003 | 121.6461 | 30.368 | -121.6232 | 121.4951 | 121.6553 | 21.5469 | -121.5637
1764.2969 | 121.7789 | -0.19684 | 121.4355 | -0.0049592 | 0.0038003 | 0.06476 | -0.0011024 | 0.067971 | 0.0013501 | 0.0026019 | -0.013123 | -0.0038431 | 0.062698 | 0.068037 | -0.19977 | -0.0041208 | 121.4401 | 0.85602 | 30.2124 | -0.004578 | 121.376 | -0.11902 | -0.20142 | 0.16479 | 21.4416 | -0.17853 | 121.2936 | 121.4493 | -0.073242 | -0.1236 | 0.077819 | -0.004578 | -0.059509 | 1.0529 | 0.19226 | 0.19684 | 0.004578 | 0.1236 | 0.073242 | -0.14191 | 0.36163 | 0.01831 | -0.054932 | 0.013733 | 121.5729 | 121.637 | 30.4092 | -121.637 | 121.4905 | 121.6461 | 21.6385 | -121.5591
1766.0625 | 121.6553 | -0.27008 | 121.463 | -0.0049592 | 0.0078591 | 0.068178 | 0.0027428 | 0.067543 | -0.00099973 | -0.00017514 | -0.013123 | -0.0032021 | 0.063766 | 0.066969 | -0.2034 | -0.0039072 | 121.4127 | 0.84686 | 30.2765 | -0.027466 | 121.3669 | -0.1236 | -0.2243 | 0.07782 | 21.492 | -0.25177 | 121.3303 | 121.463 | -0.09613 | -0.14191 | 0.14649 | 0.045777 | -0.096131 | 1.1169 | 0.24262 | 0.19684 | -0.050354 | 0.17395 | 0.12817 | -0.13275 | 0.3479 | 0.018311 | -0.10986 | 0 | 121.637 | 121.6827 | 30.5466 | -121.6873 | 121.6003 | 121.7331 | 21.7621 | -121.6049
1767.7812 | 121.7834 | -0.21973 | 121.4218 | -0.0049592 | 0.0050821 | 0.064546 | -0.0015296 | 0.068184 | 0.0022047 | 0.00067926 | -0.020752 | -0.0032021 | 0.063339 | 0.067823 | -0.19977 | -0.0039072 | 121.376 | 0.78735 | 30.2673 | -0.07782 | 121.3989 | -0.15564 | -0.20599 | 0.10529 | 21.6156 | -0.25635 | 121.312 | 121.4767 | -0.086975 | -0.11444 | 0.064087 | 0.013733 | -0.022888 | 1.0071 | 0.14191 | 0.12817 | -0.045776 | 0.13275 | 0.10529 | -0.10986 | 0.32501 | -0.036621 | -0.14191 | 0.054932 | 121.6187 | 121.5958 | 30.4871 | -121.6278 | 121.5317 | 121.6965 | 21.8353 | -121.5363
1769.5312 | 121.7972 | -0.20142 | 121.4172 | 0.0026703 | -0.0017539 | 0.070741 | -0.0025976 | 0.066048 | -0.0037769 | 0.00025206 | 0.0021363 | -0.0055521 | 0.062057 | 0.067182 | -0.20425 | -0.0026254 | 121.376 | 0.87433 | 30.4138 | -0.036621 | 121.3989 | -0.12817 | -0.19684 | 0.1236 | 21.7667 | -0.18768 | 121.2936 | 121.4767 | -0.10071 | -0.10986 | 0.073242 | 0.004578 | -0.01831 | 1.0757 | 0.1648 | 0.16022 | -0.041198 | 0.10071 | 0.091553 | -0.1236 | 0.32501 | 0.013733 | -0.07782 | 0.05951 | 121.6003 | 121.5775 | 30.6152 | -121.6141 | 121.4951 | 121.6782 | 21.9681 | -121.5271
1771.3125 | 121.7148 | -0.23346 | 121.4355 | -0.012589 | 0.0057229 | 0.06476 | 0.0014612 | 0.066902 | 0.0051953 | 0.00025206 | 0.0021363 | -0.0023477 | 0.063126 | 0.069319 | -0.20019 | -0.0043344 | 121.3486 | 0.76904 | 30.3818 | -0.091553 | 121.3898 | -0.16479 | -0.21973 | 0.054932 | 21.8353 | -0.31128 | 121.3348 | 121.5042 | -0.11902 | -0.13733 | 0.068664 | 0.013732 | -0.045776 | 1.0025 | 0.14191 | 0.12817 | -0.086975 | 0.11444 | 0.09613 | -0.10071 | 0.28839 | -0.07782 | -0.17395 | 0.068664 | 121.6232 | 121.582 | 30.6152 | -121.6553 | 121.5683 | 121.7377 | 22.0688 | -121.5729
1773.0938 | 121.7697 | -0.20599 | 121.4401 | -0.020218 | 0.0057229 | 0.069887 | 0.002102 | 0.069893 | -0.0048449 | -0.00060234 | 0.017395 | -0.0057657 | 0.063126 | 0.066328 | -0.20382 | -0.0021982 | 121.463 | 0.99335 | 30.6564 | 0.009155 | 121.344 | -0.1236 | -0.20599 | 0.15106 | 22.2061 | -0.14648 | 121.2708 | 121.463 | -0.068665 | -0.10529 | 0.082398 | 0 | -0.096131 | 1.1993 | 0.21515 | 0.21515 | 0.022888 | 0.13733 | 0.10071 | -0.16937 | 0.35706 | 0.05951 | -0.041198 | 0.022888 | 121.55 | 121.669 | 30.8624 | -121.6461 | 121.4767 | 121.669 | 22.4121 | -121.5454
1774.875 | 121.7056 | -0.24261 | 121.4676 | -0.0049592 | 0.0091409 | 0.066255 | 0.001034 | 0.069252 | 0.0036999 | 0.0026019 | -0.013123 | 2.078e-06 | 0.065262 | 0.069746 | -0.19806 | -0.0051888 | 121.3989 | 0.88806 | 30.5786 | -0.050354 | 121.4081 | -0.14191 | -0.21515 | 0.1236 | 22.1878 | -0.26093 | 121.3257 | 121.4951 | -0.10529 | -0.11444 | 0.10071 | 0.027466 | -0.059509 | 1.1307 | 0.19226 | 0.16479 | -0.068664 | 0.13733 | 0.12817 | -0.14191 | 0.36621 | -0.01831 | -0.14648 | 0.027466 | 121.6507 | 121.6415 | 30.8212 | -121.6827 | 121.5683 | 121.7377 | 22.4304 | -121.582
1776.5625 | 121.6599 | -0.27008 | 121.4859 | -0.0049592 | 0.0042275 | 0.06711 | 0.0023156 | 0.066475 | 0.00049567 | 0.0013203 | -0.0054932 | -0.0034159 | 0.065048 | 0.068891 | -0.20447 | -0.0041208 | 121.3303 | 0.87433 | 30.6152 | -0.07782 | 121.4035 | -0.16022 | -0.23346 | 0.036621 | 21.9772 | -0.29297 | 121.3486 | 121.5225 | -0.1236 | -0.16479 | 0.10986 | 0.036622 | -0.082398 | 1.1444 | 0.19226 | 0.15564 | -0.15564 | 0.14649 | 0.10529 | -0.13733 | 0.3067 | -0.022888 | -0.12817 | 0.036621 | 121.6736 | 121.6003 | 30.8853 | -121.7194 | 121.6187 | 121.7926 | 22.2473 | -121.6507
1778.3438 | 121.6553 | -0.26093 | 121.4996 | -0.0049592 | 0.0063639 | 0.066683 | 0.0033838 | 0.067116 | -0.00057253 | 0.00089286 | -0.0054932 | -0.0061929 | 0.065262 | 0.067396 | -0.20147 | -0.001771 | 121.3577 | 0.89264 | 30.6976 | -0.082397 | 121.376 | -0.15106 | -0.23346 | 0.045776 | 22.0825 | -0.29755 | 121.3348 | 121.4859 | -0.13275 | -0.16479 | 0.10986 | 0.027466 | -0.1236 | 1.1536 | 0.17853 | 0.15106 | -0.14191 | 0.12817 | 0.09613 | -0.16479 | 0.3067 | -0.036621 | -0.13275 | -0.013733 | 121.637 | 121.6187 | 30.9586 | -121.7331 | 121.5958 | 121.7468 | 22.3434 | -121.6644
1780.0625 | 121.6827 | -0.2655 | 121.4676 | -0.0049592 | 0.0052957 | 0.065614 | -0.0028112 | 0.067757 | 0.0036999 | 0.0043109 | -0.020752 | -0.0019205 | 0.064407 | 0.066542 | -0.19806 | -0.0049752 | 121.4081 | 0.94299 | 30.7571 | -0.032043 | 121.4172 | -0.16022 | -0.21973 | 0.1236 | 22.1649 | -0.26093 | 121.3348 | 121.4813 | -0.10071 | -0.14648 | 0.10529 | 0.045776 | -0.050354 | 1.2085 | 0.23346 | 0.18768 | -0.059509 | 0.16479 | 0.11902 | -0.13275 | 0.3891 | 0.004578 | -0.11444 | 0.013733 | 121.6827 | 121.6736 | 31.0226 | -121.6873 | 121.6003 | 121.7468 | 22.4304 | -121.6141
1781.8438 | 121.756 | -0.2243 | 121.4447 | -0.0049592 | 0.0063639 | 0.068391 | -0.00046138 | 0.069466 | 0.0022047 | 0.0040973 | -0.0054932 | -0.0029885 | 0.06398 | 0.06825 | -0.19955 | -0.0024118 | 121.3348 | 0.88348 | 30.7343 | -0.086975 | 121.4035 | -0.16022 | -0.23804 | 0.068665 | 22.11 | -0.29297 | 121.3394 | 121.4767 | -0.11444 | -0.15106 | 0.064087 | -0.013733 | -0.041199 | 1.1078 | 0.13733 | 0.15106 | -0.10986 | 0.10986 | 0.073242 | -0.10529 | 0.29297 | -0.068665 | -0.14191 | 0.032044 | 121.6278 | 121.5591 | 30.9586 | -121.6827 | 121.5637 | 121.7011 | 22.3343 | -121.5958
1783.6094 | 121.7651 | -0.2243 | 121.431 | -0.0049592 | 0.00080973 | 0.066469 | 0.0029566 | 0.065407 | -0.0052721 | 0.0028155 | 0.0021363 | -0.0072611 | 0.06398 | 0.065901 | -0.20468 | -0.0013436 | 121.3577 | 0.98877 | 30.8807 | -0.059509 | 121.376 | -0.12817 | -0.19226 | 0.091553 | 22.2656 | -0.21973 | 121.2936 | 121.4447 | -0.10071 | -0.10986 | 0.09613 | 0.032043 | -0.054931 | 1.2131 | 0.16479 | 0.13275 | -0.073242 | 0.1236 | 0.11444 | -0.13733 | 0.31586 | 0.004577 | -0.10986 | 0.013733 | 121.6003 | 121.582 | 31.105 | -121.6232 | 121.5179 | 121.669 | 22.4899 | -121.5408
1785.375 | 121.7102 | -0.22888 | 121.4355 | -0.012589 | 0.0093545 | 0.064546 | 0.0033838 | 0.069039 | 0.0019909 | 0.00067926 | -0.0054932 | -0.0027749 | 0.065262 | 0.06761 | -0.20126 | -0.004548 | 121.3852 | 0.97961 | 30.9082 | -0.050354 | 121.3943 | -0.13275 | -0.21973 | 0.11444 | 22.3389 | -0.2655 | 121.3303 | 121.4584 | -0.10986 | -0.14648 | 0.096131 | 0.009155 | -0.041199 | 1.2085 | 0.17853 | 0.16937 | -0.050354 | 0.11902 | 0.082398 | -0.10529 | 0.34332 | -0.036621 | -0.11902 | 0.022888 | 121.6232 | 121.6141 | 31.1371 | -121.6553 | 121.5591 | 121.6873 | 22.5677 | -121.582
1787.0781 | 121.6507 | -0.27008 | 121.4539 | -0.0049592 | 0.0059365 | 0.066683 | -0.0025976 | 0.067757 | 0.0028455 | 0.0045245 | -0.020752 | -0.0014933 | 0.064194 | 0.069746 | -0.19998 | -0.0041208 | 121.376 | 0.97961 | 30.9219 | -0.054932 | 121.4035 | -0.16479 | -0.2243 | 0.10071 | 22.403 | -0.29755 | 121.3394 | 121.4813 | -0.11902 | -0.14191 | 0.10529 | 0.045777 | -0.050354 | 1.2497 | 0.21515 | 0.16937 | -0.077819 | 0.15106 | 0.12817 | -0.11444 | 0.37079 | -0.027465 | -0.15564 | 0.027466 | 121.6736 | 121.6461 | 31.192 | -121.6782 | 121.6095 | 121.7514 | 22.673 | -121.5958
1788.8594 | 121.7239 | -0.21515 | 121.4447 | -0.0049592 | 0.0018777 | 0.06946 | 0.00017942 | 0.065193 | -0.0063403 | 0.00046566 | -0.0054932 | -0.0074747 | 0.065048 | 0.06825 | -0.20382 | -0.0019846 | 121.3715 | 1.0483 | 30.9998 | -0.027466 | 121.3531 | -0.1236 | -0.20142 | 0.11444 | 22.4899 | -0.21515 | 121.2799 | 121.4676 | -0.091553 | -0.11444 | 0.091553 | 0.013733 | -0.091553 | 1.2634 | 0.18768 | 0.17395 | -0.073242 | 0.1236 | 0.10071 | -0.1648 | 0.32959 | 0 | -0.10071 | 0.022888 | 121.5683 | 121.5866 | 31.2149 | -121.6461 | 121.4951 | 121.6827 | 22.7051 | -121.5591
1790.625 | 121.788 | -0.20142 | 121.4401 | 0.0026703 | 0.0050821 | 0.067323 | -0.00067498 | 0.069252 | 0.00028207 | 0.0026019 | 0.0021363 | -0.0019205 | 0.06398 | 0.068037 | -0.19934 | -0.0024118 | 121.4127 | 1.03 | 31.0272 | -0.027466 | 121.3898 | -0.12817 | -0.21057 | 0.16022 | 22.6273 | -0.21057 | 121.3028 | 121.4539 | -0.086975 | -0.10071 | 0.073242 | -0.009155 | -0.050354 | 1.2314 | 0.17395 | 0.18311 | -0.027466 | 0.11444 | 0.10071 | -0.13733 | 0.36163 | -0.009155 | -0.10986 | 0.013732 | 121.5912 | 121.6141 | 31.2286 | -121.6507 | 121.5042 | 121.6553 | 22.8287 | -121.5408
1792.3906 | 121.7606 | -0.21973 | 121.4401 | -0.012589 | 0.0033731 | 0.068178 | -0.00046138 | 0.064125 | -0.0044177 | 0.00046566 | -0.013123 | -0.0079019 | 0.063126 | 0.066114 | -0.20425 | -0.00113 | 121.3623 | 1.0483 | 31.0638 | -0.045776 | 121.344 | -0.1236 | -0.19684 | 0.09613 | 22.6639 | -0.22888 | 121.3074 | 121.4722 | -0.091553 | -0.13733 | 0.096131 | 0.022889 | -0.096131 | 1.268 | 0.17395 | 0.15106 | -0.07782 | 0.12817 | 0.082398 | -0.13275 | 0.31586 | -0.009155 | -0.091553 | 0.032043 | 121.5637 | 121.582 | 31.2836 | -121.637 | 121.5271 | 121.6919 | 22.8836 | -121.5775
1794.0938 | 121.6873 | -0.24261 | 121.4493 | 0.0026703 | 0.011918 | 0.066683 | 0.0033838 | 0.066475 | 0.0054089 | 0.00025206 | -0.0054932 | 0.0010703 | 0.067184 | 0.066755 | -0.20083 | -0.0064706 | 121.3806 | 1.0162 | 31.0455 | -0.068665 | 121.3669 | -0.17853 | -0.26093 | 0.11902 | 22.8012 | -0.27466 | 121.3348 | 121.463 | -0.12817 | -0.17395 | 0.064087 | -0.01831 | -0.082398 | 1.2589 | 0.17395 | 0.19226 | -0.068665 | 0.11444 | 0.068665 | -0.11444 | 0.36163 | -0.032043 | -0.10071 | 0.013733 | 121.6095 | 121.6232 | 31.2881 | -121.7102 | 121.5775 | 121.7056 | 23.0438 | -121.6232
1795.875 | 121.7651 | -0.23346 | 121.4035 | 0.0026703 | 0.0059365 | 0.068178 | 0.003811 | 0.064553 | -0.0033495 | 0.00067926 | -0.0054932 | -0.0066201 | 0.062912 | 0.066114 | -0.20489 | -0.0021982 | 121.4264 | 1.1856 | 31.1966 | 0.013733 | 121.3165 | -0.16022 | -0.20599 | 0.15564 | 23.0164 | -0.16022 | 121.2524 | 121.431 | -0.07782 | -0.13275 | 0.073242 | 0.027465 | -0.086975 | 1.4191 | 0.24719 | 0.21973 | 0.022889 | 0.15564 | 0.10071 | -0.15106 | 0.3891 | 0.073242 | -0.027466 | 0.027466 | 121.55 | 121.6599 | 31.4301 | -121.6095 | 121.4859 | 121.6644 | 23.2498 | -121.5363
1797.6562 | 121.6919 | -0.24261 | 121.4401 | 0.0026703 | 0.0055093 | 0.065614 | -0.0028112 | 0.065834 | 0.0034863 | 0.0013203 | -0.0054932 | -0.00063872 | 0.063553 | 0.066328 | -0.19998 | -0.0056162 | 121.3852 | 1.0712 | 31.0959 | -0.068665 | 121.3943 | -0.16022 | -0.24261 | 0.10986 | 23.0255 | -0.28839 | 121.312 | 121.4767 | -0.09613 | -0.16479 | 0.082398 | 0 | -0.045777 | 1.3138 | 0.17395 | 0.17395 | -0.054932 | 0.14649 | 0.07782 | -0.12817 | 0.35248 | -0.045776 | -0.1236 | 0.036621 | 121.637 | 121.6278 | 31.3385 | -121.6827 | 121.5546 | 121.7194 | 23.2681 | -121.6049
1799.3594 | 121.6827 | -0.26093 | 121.4401 | -0.0049592 | 0.01085 | 0.065828 | 0.0027428 | 0.068398 | 0.0039135 | 0.0021747 | -0.0054932 | -0.0023477 | 0.067184 | 0.067182 | -0.20212 | -0.0032662 | 121.376 | 1.0803 | 31.1325 | -0.059509 | 121.3989 | -0.16022 | -0.23346 | 0.13275 | 23.1445 | -0.28381 | 121.312 | 121.4813 | -0.13275 | -0.14648 | 0.10071 | 0.027466 | -0.041199 | 1.3412 | 0.20142 | 0.17395 | -0.064087 | 0.12817 | 0.11444 | -0.12817 | 0.39368 | -0.022888 | -0.13733 | 0.041198 | 121.6599 | 121.637 | 31.3934 | -121.6736 | 121.5729 | 121.7422 | 23.4055 | -121.5866
1801.125 | 121.7422 | -0.23804 | 121.4264 | -0.0049592 | 0.0012369 | 0.069887 | -0.00024778 | 0.067971 | -0.0052721 | 0.0013203 | -0.0054932 | -0.0074747 | 0.06398 | 0.066755 | -0.2019 | -0.001771 | 121.376 | 1.181 | 31.1966 | -0.036621 | 121.3211 | -0.1236 | -0.17395 | 0.13733 | 23.2224 | -0.21973 | 121.2891 | 121.4355 | -0.11902 | -0.13733 | 0.11444 | 0.064087 | -0.10529 | 1.4191 | 0.20142 | 0.13733 | -0.050354 | 0.11902 | 0.10071 | -0.13733 | 0.37537 | 0.01831 | -0.082398 | 0.009155 | 121.5591 | 121.6141 | 31.4346 | -121.6003 | 121.5271 | 121.6736 | 23.4604 | -121.5637
1802.8906 | 121.7926 | -0.21973 | 121.4081 | -0.020218 | 0.0029459 | 0.067323 | 0.00082022 | 0.067757 | 0.0011365 | 0.0026019 | -0.013123 | -0.0057657 | 0.06398 | 0.066542 | -0.20169 | -0.0036936 | 121.4035 | 1.1765 | 31.2012 | -0.004578 | 121.3531 | -0.13733 | -0.21973 | 0.20142 | 23.3734 | -0.21973 | 121.2662 | 121.431 | -0.09613 | -0.10986 | 0.082398 | 0 | -0.054932 | 1.3962 | 0.21515 | 0.21515 | -0.004578 | 0.1236 | 0.10986 | -0.14191 | 0.42114 | 0 | -0.10986 | 0.022888 | 121.5729 | 121.6232 | 31.4209 | -121.6278 | 121.4859 | 121.6507 | 23.5931 | -121.5179
1804.6562 | 121.7514 | -0.24261 | 121.4127 | -0.0049592 | 0.0085001 | 0.066469 | 0.0033838 | 0.068611 | 0.0036999 | 0.0026019 | -0.0054932 | -0.0021341 | 0.067825 | 0.069532 | -0.20254 | -0.0024118 | 121.3211 | 1.0574 | 31.0867 | -0.09613 | 121.3943 | -0.16022 | -0.24261 | 0.091553 | 23.4787 | -0.3067 | 121.3165 | 121.463 | -0.1236 | -0.16022 | 0.082398 | 0 | -0.018311 | 1.3 | 0.14649 | 0.14649 | -0.091553 | 0.11902 | 0.082398 | -0.096131 | 0.33417 | -0.064087 | -0.14648 | 0.050354 | 121.637 | 121.5637 | 31.3293 | -121.6553 | 121.5591 | 121.7056 | 23.7213 | -121.5729
1806.3594 | 121.7972 | -0.2243 | 121.3852 | -0.012589 | 0.0095681 | 0.065828 | 0.002102 | 0.068184 | -0.00099973 | 0.0028155 | 0.0021363 | -0.0036295 | 0.066116 | 0.066542 | -0.20382 | -0.0047616 | 121.4035 | 1.2085 | 31.2195 | -0.004578 | 121.344 | -0.12817 | -0.20599 | 0.21057 | 23.7442 | -0.19684 | 121.2982 | 121.4172 | -0.10071 | -0.10529 | 0.09613 | 0.01831 | -0.041199 | 1.4328 | 0.21973 | 0.20142 | 0.01831 | 0.1236 | 0.11902 | -0.086975 | 0.43488 | 0.027466 | -0.091552 | 0.032043 | 121.5683 | 121.6278 | 31.4438 | -121.5912 | 121.5225 | 121.6415 | 23.9685 | -121.4905
1808.1094 | 121.7239 | -0.23346 | 121.4355 | 0.0103 | 0.00016873 | 0.06711 | -0.00024778 | 0.066262 | -0.0037769 | -0.00081594 | -0.013123 | -0.0061929 | 0.062057 | 0.067182 | -0.2019 | -0.0015572 | 121.3623 | 1.2131 | 31.1966 | -0.041199 | 121.3531 | -0.13733 | -0.21515 | 0.13733 | 23.7717 | -0.21973 | 121.2982 | 121.4447 | -0.091553 | -0.13733 | 0.09613 | 0.01831 | -0.082398 | 1.4465 | 0.19226 | 0.17395 | -0.073242 | 0.14191 | 0.09613 | -0.13733 | 0.37079 | 0.013732 | -0.082398 | 0.009155 | 121.5866 | 121.5958 | 31.4301 | -121.6507 | 121.5317 | 121.6782 | 24.0051 | -121.5729
1809.8906 | 121.7239 | -0.25635 | 121.4539 | -0.0049592 | 0.0048685 | 0.06711 | 0.00017942 | 0.067543 | 0.0032727 | 0.0028155 | 0.0021363 | -0.0032021 | 0.062485 | 0.067823 | -0.19912 | -0.0056162 | 121.376 | 1.1673 | 31.1417 | -0.041199 | 121.3989 | -0.15564 | -0.23804 | 0.13275 | 23.6755 | -0.27466 | 121.3257 | 121.4905 | -0.11902 | -0.16937 | 0.10071 | 0.018311 | -0.054931 | 1.4236 | 0.21515 | 0.19684 | -0.077819 | 0.13733 | 0.086975 | -0.12817 | 0.3891 | -0.01831 | -0.10529 | 0.036622 | 121.6553 | 121.6324 | 31.398 | -121.6919 | 121.582 | 121.7468 | 23.9319 | -121.6232
1811.5938 | 121.7926 | -0.22888 | 121.4401 | -0.0049592 | 0.0031595 | 0.069246 | 0.001034 | 0.06733 | -0.0048449 | 0.00046566 | -0.013123 | -0.0051247 | 0.063553 | 0.064833 | -0.20297 | -0.0019846 | 121.4218 | 1.3138 | 31.2698 | 0.013733 | 121.3623 | -0.13733 | -0.21515 | 0.1831 | 23.7808 | -0.16937 | 121.2799 | 121.4355 | -0.091553 | -0.10986 | 0.091553 | 0.013733 | -0.07782 | 1.5427 | 0.24261 | 0.22888 | -0.018311 | 0.13733 | 0.11902 | -0.16022 | 0.41199 | 0.059509 | -0.05951 | -0.004578 | 121.5912 | 121.6507 | 31.4987 | -121.6553 | 121.5088 | 121.6644 | 24.0097 | -121.55
1813.3594 | 121.7834 | -0.21973 | 121.3989 | -0.0049592 | 0.0048685 | 0.064546 | 0.0025292 | 0.06498 | 0.0041273 | 0.0026019 | -0.013123 | -0.0017069 | 0.064835 | 0.065687 | -0.19955 | -0.0041208 | 121.4035 | 1.236 | 31.1829 | -0.022888 | 121.3806 | -0.14648 | -0.21515 | 0.19684 | 23.8449 | -0.20599 | 121.2936 | 121.4493 | -0.09613 | -0.11902 | 0.073243 | 0.004578 | -0.018311 | 1.4557 | 0.19684 | 0.19226 | 0.004577 | 0.1236 | 0.10071 | -0.10529 | 0.41657 | 0.013733 | -0.086975 | 0.050354 | 121.6003 | 121.6232 | 31.4026 | -121.6141 | 121.5134 | 121.669 | 24.0646 | -121.5179
1815.125 | 121.7651 | -0.23346 | 121.4172 | -0.0049592 | 0.0035867 | 0.068605 | 0.0040246 | 0.067757 | -0.0042041 | 0.00067926 | -0.013123 | -0.0066201 | 0.062912 | 0.067396 | -0.2019 | -0.0036936 | 121.4355 | 1.3367 | 31.2698 | -0.004578 | 121.3303 | -0.14191 | -0.20599 | 0.19684 | 24.0234 | -0.16937 | 121.2799 | 121.4447 | -0.086975 | -0.13275 | 0.091552 | 0.027465 | -0.086975 | 1.5701 | 0.22888 | 0.20142 | 0.018311 | 0.14648 | 0.10071 | -0.13733 | 0.4303 | 0.064086 | -0.036622 | 0.027466 | 121.5637 | 121.669 | 31.5033 | -121.6232 | 121.5134 | 121.6782 | 24.2569 | -121.55
1816.8906 | 121.7606 | -0.2243 | 121.4401 | -0.0049592 | 0.0025185 | 0.067751 | 0.0023156 | 0.06733 | -0.0024951 | 0.00089286 | -0.0054932 | -0.0059793 | 0.063766 | 0.069746 | -0.20297 | -0.0041208 | 121.3623 | 1.2543 | 31.16 | -0.054932 | 121.3623 | -0.13275 | -0.21973 | 0.13733 | 23.9594 | -0.25177 | 121.2708 | 121.4676 | -0.11902 | -0.12817 | 0.091553 | 0.004577 | -0.07782 | 1.4786 | 0.16937 | 0.16479 | -0.07782 | 0.10529 | 0.09613 | -0.16937 | 0.36163 | -0.027466 | -0.1236 | 0.027465 | 121.5866 | 121.5866 | 31.3843 | -121.6599 | 121.4951 | 121.6919 | 24.1837 | -121.5683
1818.5938 | 121.7834 | -0.22888 | 121.4218 | 0.0026703 | 0.0044411 | 0.068391 | 0.0040246 | 0.070107 | -0.0012133 | -0.00060234 | -0.0054932 | -0.0051247 | 0.068253 | 0.06825 | -0.20169 | -0.0054026 | 121.4355 | 1.4008 | 31.2241 | 0.013733 | 121.3394 | -0.13275 | -0.21057 | 0.21057 | 24.2432 | -0.16479 | 121.2891 | 121.431 | -0.10071 | -0.14648 | 0.096131 | 0.018311 | -0.082397 | 1.6296 | 0.24261 | 0.2243 | 0.013733 | 0.12817 | 0.082398 | -0.13275 | 0.43945 | 0.064087 | -0.018311 | 0.009155 | 121.5683 | 121.6644 | 31.4529 | -121.6324 | 121.5179 | 121.6599 | 24.472 | -121.5683
1820.3594 | 121.7377 | -0.25177 | 121.431 | -0.012589 | -0.0011131 | 0.068819 | -0.002384 | 0.06733 | -0.0014269 | 0.00025206 | -0.0054932 | -0.0061929 | 0.061844 | 0.068678 | -0.20276 | -0.0030526 | 121.3577 | 1.3321 | 31.1279 | -0.054932 | 121.3531 | -0.15106 | -0.20599 | 0.15564 | 24.1699 | -0.24261 | 121.2891 | 121.4172 | -0.10071 | -0.15564 | 0.10071 | 0.045776 | -0.07782 | 1.5839 | 0.19684 | 0.15106 | -0.073242 | 0.15106 | 0.09613 | -0.14191 | 0.40741 | 0.009155 | -0.086975 | -0.013733 | 121.6049 | 121.6095 | 31.3797 | -121.637 | 121.5408 | 121.669 | 24.4217 | -121.5866
1822.0625 | 121.7285 | -0.25635 | 121.4493 | 0.0026703 | 0.0063639 | 0.067751 | 0.00017942 | 0.069039 | 0.0039135 | 0.0036701 | 0.0021363 | -0.00063872 | 0.06398 | 0.070173 | -0.19977 | -0.0054026 | 121.3669 | 1.2955 | 31.073 | -0.041199 | 121.3943 | -0.16022 | -0.25177 | 0.17395 | 24.3027 | -0.28381 | 121.3257 | 121.4722 | -0.11444 | -0.16937 | 0.096131 | 0.004578 | -0.054932 | 1.5518 | 0.21515 | 0.21057 | -0.082398 | 0.14191 | 0.086975 | -0.1236 | 0.4303 | -0.027465 | -0.11444 | 0.022888 | 121.6507 | 121.6232 | 31.3293 | -121.701 | 121.582 | 121.7285 | 24.559 | -121.6187
1823.8438 | 121.7972 | -0.23346 | 121.3989 | -0.012589 | 0.0040139 | 0.067964 | 0.0029566 | 0.065407 | -0.0044177 | 0.00046566 | 0.0021363 | -0.0072611 | 0.065262 | 0.067396 | -0.20447 | -0.0036936 | 121.3577 | 1.3504 | 31.0776 | -0.041199 | 121.376 | -0.13275 | -0.22888 | 0.16479 | 24.4904 | -0.23804 | 121.2982 | 121.4172 | -0.10071 | -0.14191 | 0.10071 | 0.004577 | -0.022888 | 1.5839 | 0.19226 | 0.18768 | -0.041199 | 0.13275 | 0.091552 | -0.10071 | 0.39825 | -0.004578 | -0.09613 | 0.01831 | 121.6095 | 121.5912 | 31.311 | -121.6278 | 121.5317 | 121.6507 | 24.7238 | -121.5408
1825.5469 | 121.7697 | -0.22888 | 121.4264 | 0.0026703 | -0.0021811 | 0.068178 | -0.0021704 | 0.067757 | -0.0029223 | 0.0026019 | -0.0054932 | -0.0057657 | 0.063339 | 0.065473 | -0.2034 | -0.0049752 | 121.4264 | 1.4832 | 31.1554 | 0.009155 | 121.3531 | -0.15106 | -0.20599 | 0.21515 | 24.6002 | -0.1831 | 121.2936 | 121.4539 | -0.091553 | -0.13733 | 0.07782 | 0.022888 | -0.073243 | 1.712 | 0.23804 | 0.21515 | 0 | 0.13733 | 0.091553 | -0.13275 | 0.44403 | 0.045777 | -0.045776 | 0.027465 | 121.582 | 121.6553 | 31.3843 | -121.6324 | 121.5225 | 121.6827 | 24.8291 | -121.5637
1827.3125 | 121.6919 | -0.26093 | 121.4401 | 0.0103 | 0.0072183 | 0.069887 | 0.0044518 | 0.067971 | -0.0018543 | 0.0019611 | -0.0054932 | -0.0059793 | 0.064407 | 0.06761 | -0.20233 | -0.0051888 | 121.4127 | 1.4648 | 31.1096 | -0.004578 | 121.3394 | -0.15564 | -0.20599 | 0.2243 | 24.6918 | -0.19684 | 121.2845 | 121.4447 | -0.09613 | -0.13733 | 0.10529 | 0.054931 | -0.10071 | 1.7258 | 0.25635 | 0.20142 | -0.027466 | 0.1648 | 0.1236 | -0.15564 | 0.48523 | 0.064087 | -0.059509 | 0.004577 | 121.6003 | 121.6736 | 31.3705 | -121.6461 | 121.5454 | 121.7056 | 24.9527 | -121.5775
1829.0938 | 121.7468 | -0.23346 | 121.4264 | -0.020218 | 0.0038003 | 0.065828 | -0.0011024 | 0.066902 | 0.0026319 | 0.0023883 | 0.0021363 | -0.0051247 | 0.06398 | 0.067396 | -0.19998 | -0.0051888 | 121.4218 | 1.4786 | 31.073 | -0.009155 | 121.3486 | -0.13275 | -0.17853 | 0.23346 | 24.7559 | -0.20599 | 121.2936 | 121.3943 | -0.10071 | -0.11444 | 0.10071 | 0.054931 | -0.07782 | 1.712 | 0.2243 | 0.16937 | -0.004578 | 0.13275 | 0.11902 | -0.13275 | 0.46692 | 0.027465 | -0.091553 | -0.032044 | 121.582 | 121.6553 | 31.3065 | -121.6049 | 121.5271 | 121.6278 | 24.9893 | -121.5408
1830.8594 | 121.8063 | -0.23346 | 121.3898 | -0.0049592 | 0.0031595 | 0.066896 | 0.0014612 | 0.06733 | -0.00078613 | 0.0011067 | -0.013123 | -0.0064065 | 0.062912 | 0.065687 | -0.20062 | -0.0026254 | 121.3531 | 1.442 | 30.9906 | -0.041199 | 121.3669 | -0.15564 | -0.22888 | 0.19226 | 24.8199 | -0.23346 | 121.2936 | 121.4355 | -0.10986 | -0.14191 | 0.077819 | 0.004577 | -0.022889 | 1.6754 | 0.19226 | 0.18768 | -0.036622 | 0.1236 | 0.091552 | -0.096131 | 0.42572 | 0 | -0.091552 | 0.045776 | 121.6003 | 121.5866 | 31.2241 | -121.6187 | 121.5271 | 121.669 | 25.0534 | -121.5317
1832.5625 | 121.6782 | -0.27924 | 121.4447 | 0.0026703 | 0.0080727 | 0.067964 | 0.0029566 | 0.067757 | 0.0013501 | 0.0019611 | -0.0054932 | -0.0055521 | 0.066971 | 0.068037 | -0.20297 | -0.0036936 | 121.3943 | 1.5152 | 31.0043 | 0.004578 | 121.3531 | -0.15106 | -0.21973 | 0.2243 | 24.9756 | -0.2243 | 121.312 | 121.4264 | -0.10529 | -0.14191 | 0.12817 | 0.059509 | -0.091553 | 1.7944 | 0.28381 | 0.22431 | -0.050354 | 0.17395 | 0.13733 | -0.13275 | 0.50354 | 0.054932 | -0.082397 | -0.01831 | 121.6324 | 121.6736 | 31.2836 | -121.6644 | 121.5912 | 121.7056 | 25.2548 | -121.5866
1834.3281 | 121.8018 | -0.23346 | 121.4081 | -0.012589 | 0.0027323 | 0.071382 | -0.00024778 | 0.067116 | -0.0035633 | 0.0013203 | -0.0054932 | -0.0066201 | 0.064621 | 0.068891 | -0.2019 | -0.0039072 | 121.3989 | 1.5427 | 30.9586 | -0.009155 | 121.376 | -0.14191 | -0.21057 | 0.22888 | 25.0122 | -0.16937 | 121.2845 | 121.4218 | -0.091553 | -0.12817 | 0.091552 | 0.022888 | -0.032043 | 1.7761 | 0.2243 | 0.20142 | -0.009155 | 0.14191 | 0.10528 | -0.1236 | 0.46234 | 0.064086 | -0.041199 | 0.013733 | 121.6095 | 121.6324 | 31.192 | -121.6187 | 121.5179 | 121.6553 | 25.2457 | -121.5363
1836.0938 | 121.7056 | -0.26093 | 121.4264 | -0.012589 | 0.011491 | 0.067964 | 0.002102 | 0.066902 | 0.0041273 | 0.0017475 | -0.013123 | -0.00063872 | 0.066116 | 0.068678 | -0.2034 | -0.0071114 | 121.3394 | 1.4191 | 30.8029 | -0.073242 | 121.3898 | -0.19226 | -0.25635 | 0.15564 | 24.9527 | -0.32044 | 121.3486 | 121.463 | -0.1236 | -0.16937 | 0.068664 | 0.004577 | -0.036621 | 1.68 | 0.18768 | 0.18311 | -0.086975 | 0.13733 | 0.091552 | -0.07782 | 0.41657 | -0.05951 | -0.15106 | 0.036621 | 121.6507 | 121.6003 | 31.0638 | -121.6827 | 121.6095 | 121.7239 | 25.2136 | -121.5958
1837.8125 | 121.7056 | -0.27008 | 121.4264 | 0.0026703 | 0.0065775 | 0.067537 | -0.00024778 | 0.066475 | 0.0030591 | 0.00025206 | -0.0054932 | -0.0038431 | 0.063339 | 0.066114 | -0.20019 | -0.0051888 | 121.3257 | 1.4511 | 30.7434 | -0.086975 | 121.3806 | -0.19226 | -0.27008 | 0.14191 | 24.9756 | -0.31128 | 121.3303 | 121.5088 | -0.13275 | -0.16479 | 0.07782 | 0 | -0.045777 | 1.7212 | 0.18311 | 0.18311 | -0.10071 | 0.13733 | 0.10529 | -0.096131 | 0.41199 | -0.041198 | -0.14648 | 0.082397 | 121.6507 | 121.5958 | 31.0135 | -121.6965 | 121.6003 | 121.7789 | 25.2457 | -121.5912
1839.5312 | 121.788 | -0.23346 | 121.3943 | -0.012589 | 0.0057229 | 0.067537 | -0.00067498 | 0.067971 | 0.00049567 | 0.0040973 | 0.0021363 | -0.0042703 | 0.065689 | 0.06825 | -0.20062 | -0.0030526 | 121.4218 | 1.5747 | 30.8121 | 0.004578 | 121.3348 | -0.14191 | -0.21515 | 0.25635 | 25.1404 | -0.20142 | 121.2616 | 121.4493 | -0.086975 | -0.11902 | 0.091552 | 0.01831 | -0.059509 | 1.8082 | 0.23804 | 0.21973 | 0.027466 | 0.14648 | 0.11444 | -0.13275 | 0.48981 | 0.032043 | -0.082397 | 0.054932 | 121.5683 | 121.6553 | 31.0455 | -121.6095 | 121.4951 | 121.6827 | 25.3738 | -121.5134
1841.2969 | 121.701 | -0.30212 | 121.4081 | 0.0026703 | 0.0078591 | 0.066042 | 0.0046656 | 0.067757 | -0.00057253 | -0.00017514 | 0.0021363 | -0.0034159 | 0.064835 | 0.067396 | -0.20297 | -0.0039072 | 121.2982 | 1.4786 | 30.6656 | -0.086975 | 121.3852 | -0.20599 | -0.26093 | 0.13733 | 25.2136 | -0.31128 | 121.3348 | 121.4722 | -0.15106 | -0.17395 | 0.09613 | 0.041199 | -0.022888 | 1.7807 | 0.21515 | 0.17395 | -0.10986 | 0.15106 | 0.12817 | -0.073242 | 0.43945 | -0.009155 | -0.13733 | 0.064087 | 121.6873 | 121.6003 | 30.9677 | -121.669 | 121.637 | 121.7743 | 25.5157 | -121.582
1843.0625 | 121.7468 | -0.23804 | 121.3989 | 0.0026703 | 0.0059365 | 0.070314 | 0.00017942 | 0.071175 | -0.0050585 | 0.0019611 | -0.0054932 | -0.0081155 | 0.063339 | 0.064833 | -0.20212 | -0.00113 | 121.4172 | 1.6434 | 30.7526 | -0.009155 | 121.3486 | -0.14648 | -0.20599 | 0.23346 | 25.4883 | -0.20142 | 121.2616 | 121.4172 | -0.1236 | -0.14648 | 0.091553 | 0.032043 | -0.050354 | 1.8814 | 0.22888 | 0.19684 | 0.01831 | 0.11444 | 0.091553 | -0.13733 | 0.4715 | 0.036621 | -0.054932 | 0.01831 | 121.5866 | 121.6553 | 30.9906 | -121.6049 | 121.4996 | 121.6553 | 25.7263 | -121.5454
1844.8438 | 121.7834 | -0.25177 | 121.4218 | -0.0049592 | 0.0070047 | 0.068178 | 0.0031702 | 0.066048 | -0.0027087 | -0.00017514 | -0.013123 | -0.0066201 | 0.064621 | 0.068037 | -0.20447 | -0.0026254 | 121.4081 | 1.6846 | 30.7022 | 0.004578 | 121.3394 | -0.15106 | -0.22888 | 0.27008 | 25.5386 | -0.15106 | 121.2708 | 121.4447 | -0.10071 | -0.14648 | 0.10071 | 0.022888 | -0.082397 | 1.9363 | 0.25635 | 0.23346 | -0.013733 | 0.15106 | 0.10529 | -0.15106 | 0.52185 | 0.10071 | -0.004578 | 0.022888 | 121.5912 | 121.6599 | 30.954 | -121.6507 | 121.5225 | 121.6965 | 25.7904 | -121.5683
1846.5469 | 121.7926 | -0.24719 | 121.4127 | -0.0049592 | 0.0048685 | 0.0701 | -0.00024778 | 0.067543 | -0.0027087 | -0.00017514 | -0.0054932 | -0.0061929 | 0.062485 | 0.067823 | -0.20297 | -0.0047616 | 121.3852 | 1.6983 | 30.6381 | -0.004578 | 121.3577 | -0.15106 | -0.21973 | 0.25635 | 25.6302 | -0.17853 | 121.2662 | 121.4035 | -0.11902 | -0.13733 | 0.09613 | 0.027465 | -0.054932 | 1.9455 | 0.24261 | 0.21515 | -0.027466 | 0.12817 | 0.10986 | -0.14648 | 0.50354 | 0.068664 | -0.041199 | -0.009156 | 121.6049 | 121.6324 | 30.8853 | -121.6324 | 121.5134 | 121.6507 | 25.8774 | -121.55
1848.3125 | 121.6461 | -0.28381 | 121.4218 | -0.012589 | 0.0095681 | 0.068178 | -0.0025976 | 0.064339 | 0.0047681 | 0.0017475 | -0.013123 | 0.00085668 | 0.06398 | 0.06825 | -0.19891 | -0.0056162 | 121.3348 | 1.5793 | 30.4642 | -0.068665 | 121.3806 | -0.20142 | -0.24719 | 0.16937 | 25.4791 | -0.35706 | 121.3211 | 121.4584 | -0.13733 | -0.17853 | 0.082397 | 0.036621 | -0.041199 | 1.8631 | 0.21515 | 0.17853 | -0.086975 | 0.14648 | 0.10528 | -0.10071 | 0.45319 | -0.073243 | -0.17853 | 0.036621 | 121.6644 | 121.6187 | 30.748 | -121.669 | 121.6049 | 121.7422 | 25.7629 | -121.6003
1850.0469 | 121.6415 | -0.29755 | 121.4264 | -0.0049592 | 0.0076455 | 0.067964 | -0.001316 | 0.068611 | 0.0039135 | 0.0028155 | 0.0021363 | -0.00042512 | 0.064621 | 0.065687 | -0.19763 | -0.0015572 | 121.2936 | 1.5884 | 30.3909 | -0.082397 | 121.3806 | -0.1831 | -0.27008 | 0.13275 | 25.5295 | -0.37994 | 121.3394 | 121.4447 | -0.14191 | -0.16022 | 0.11444 | 0.027465 | -0.045777 | 1.886 | 0.21515 | 0.18768 | -0.13275 | 0.15564 | 0.13733 | -0.086975 | 0.4303 | -0.082398 | -0.21973 | 0.01831 | 121.6782 | 121.5912 | 30.6885 | -121.6965 | 121.637 | 121.7422 | 25.827 | -121.5866
1851.8281 | 121.7056 | -0.28381 | 121.4539 | -0.0049592 | 0.0055093 | 0.069246 | 0.0027428 | 0.065834 | -0.0020679 | 0.0021747 | 0.0021363 | -0.0042703 | 0.064407 | 0.066328 | -0.20212 | -0.0019846 | 121.2845 | 1.6251 | 30.3497 | -0.091553 | 121.3806 | -0.17853 | -0.28381 | 0.1236 | 25.6531 | -0.32044 | 121.3165 | 121.4951 | -0.14648 | -0.17853 | 0.10528 | 0 | -0.073242 | 1.9089 | 0.19226 | 0.19226 | -0.16937 | 0.13733 | 0.10528 | -0.13733 | 0.40741 | -0.036622 | -0.14191 | 0.041199 | 121.6644 | 121.5683 | 30.6335 | -121.7377 | 121.6003 | 121.7789 | 25.9369 | -121.6324
1853.5938 | 121.7697 | -0.24719 | 121.4172 | 0.0026703 | 0.0035867 | 0.068819 | 0.0033838 | 0.06968 | -0.0039905 | 0.00067926 | -0.013123 | -0.0061929 | 0.066544 | 0.067396 | -0.20404 | -0.001771 | 121.3165 | 1.7166 | 30.3818 | -0.041199 | 121.3394 | -0.14648 | -0.2243 | 0.16479 | 25.795 | -0.25177 | 121.2845 | 121.4218 | -0.11444 | -0.14648 | 0.10071 | 0.022888 | -0.077819 | 1.9638 | 0.20599 | 0.18311 | -0.10071 | 0.13275 | 0.10071 | -0.13275 | 0.41199 | -0.004578 | -0.10529 | 0.004578 | 121.5866 | 121.5637 | 30.629 | -121.6415 | 121.5317 | 121.669 | 26.0422 | -121.5637
1855.375 | 121.701 | -0.28381 | 121.4035 | -0.0049592 | 0.0091409 | 0.069673 | 0.0023156 | 0.064766 | -0.0027087 | -0.00038874 | 0.0021363 | -0.0051247 | 0.066116 | 0.066114 | -0.20425 | -0.004548 | 121.3898 | 1.799 | 30.4138 | 0.004578 | 121.3303 | -0.15564 | -0.2243 | 0.24261 | 26.0559 | -0.19226 | 121.2799 | 121.4218 | -0.10529 | -0.15106 | 0.12817 | 0.059509 | -0.073242 | 2.0828 | 0.28839 | 0.22888 | -0.013732 | 0.17853 | 0.13275 | -0.1236 | 0.52643 | 0.091552 | -0.041199 | 0.018311 | 121.6141 | 121.6736 | 30.6976 | -121.6278 | 121.5637 | 121.7056 | 26.3397 | -121.5546
1857.0938 | 121.6599 | -0.3067 | 121.431 | -0.012589 | 0.0080727 | 0.06946 | 0.001034 | 0.065834 | -0.00057253 | 0.00089286 | -0.020752 | -0.0044839 | 0.063339 | 0.065473 | -0.2019 | -0.0039072 | 121.3531 | 1.7899 | 30.2719 | -0.032043 | 121.3577 | -0.17853 | -0.26093 | 0.16479 | 26.1383 | -0.28381 | 121.3211 | 121.4493 | -0.14191 | -0.19226 | 0.12817 | 0.045777 | -0.073242 | 2.0966 | 0.27466 | 0.22888 | -0.07782 | 0.16479 | 0.11444 | -0.10986 | 0.4715 | 0.022889 | -0.091552 | 0.018311 | 121.6644 | 121.6599 | 30.5786 | -121.6919 | 121.6278 | 121.756 | 26.445 | -121.6232
1858.875 | 121.756 | -0.22888 | 121.3852 | -0.0049592 | 0.0027323 | 0.0701 | -0.0021704 | 0.067757 | -0.0024951 | 0.0015339 | -0.013123 | -0.0044839 | 0.062485 | 0.066755 | -0.19955 | -0.0032662 | 121.3852 | 1.8539 | 30.2673 | -0.022888 | 121.3394 | -0.15564 | -0.21057 | 0.25635 | 26.3031 | -0.21057 | 121.2433 | 121.4172 | -0.12817 | -0.14191 | 0.073242 | 0.018311 | -0.045776 | 2.0828 | 0.20599 | 0.18768 | 0 | 0.10071 | 0.086975 | -0.14191 | 0.48523 | 0.018311 | -0.068664 | 0.032043 | 121.5683 | 121.6141 | 30.4962 | -121.5958 | 121.4722 | 121.6461 | 26.532 | -121.5271
1860.5781 | 121.7606 | -0.25635 | 121.4401 | -0.0049592 | 0.0074319 | 0.06946 | 0.0042382 | 0.066689 | -0.0018543 | 0.0011067 | -0.013123 | -0.0059793 | 0.064194 | 0.06526 | -0.20212 | -0.0047616 | 121.3898 | 1.9135 | 30.2353 | 0.009155 | 121.3394 | -0.16937 | -0.25177 | 0.27466 | 26.5182 | -0.19226 | 121.2799 | 121.4081 | -0.12817 | -0.13733 | 0.086975 | 0.004578 | -0.10071 | 2.1698 | 0.2655 | 0.26093 | -0.050354 | 0.12817 | 0.11902 | -0.16022 | 0.53101 | 0.064087 | -0.054932 | -0.032044 | 121.5958 | 121.6461 | 30.4916 | -121.6919 | 121.5363 | 121.6644 | 26.7746 | -121.5775
1862.3438 | 121.6599 | -0.28839 | 121.4584 | 0.0026703 | 0.0067911 | 0.066896 | -0.0019568 | 0.068184 | 0.0054089 | 0.0023883 | 0.0021363 | -0.0019205 | 0.064621 | 0.069959 | -0.19934 | -0.0049752 | 121.3577 | 1.8219 | 30.0751 | -0.050354 | 121.3989 | -0.18768 | -0.2655 | 0.21973 | 26.5732 | -0.3067 | 121.3165 | 121.4218 | -0.14648 | -0.18768 | 0.10071 | 0.022888 | -0.059509 | 2.1103 | 0.23804 | 0.21515 | -0.10071 | 0.14191 | 0.10071 | -0.14191 | 0.50812 | -0.018311 | -0.11902 | -0.036621 | 121.6873 | 121.6461 | 30.3635 | -121.7239 | 121.6049 | 121.7102 | 26.8616 | -121.6461
1864.125 | 121.7926 | -0.22888 | 121.4127 | -0.012589 | 0.0055093 | 0.065401 | -0.0017432 | 0.067543 | 0.0011365 | 0.0030293 | -0.0054932 | -0.0019205 | 0.065475 | 0.068891 | -0.20212 | -0.0032662 | 121.3257 | 1.8173 | 30.0247 | -0.07782 | 121.3852 | -0.17853 | -0.24261 | 0.21973 | 26.5411 | -0.29755 | 121.2936 | 121.4584 | -0.12817 | -0.16022 | 0.050354 | -0.013733 | -0.027466 | 2.0462 | 0.15106 | 0.16479 | -0.086975 | 0.10071 | 0.068665 | -0.11902 | 0.44861 | -0.068664 | -0.13733 | 0.045776 | 121.6141 | 121.5546 | 30.2536 | -121.6553 | 121.5225 | 121.6873 | 26.77 | -121.5729
1865.8281 | 121.6736 | -0.3067 | 121.4035 | -0.0049592 | 0.0063639 | 0.068605 | -0.0021704 | 0.068398 | 0.0028455 | 0.0015339 | -0.0054932 | -0.0025613 | 0.063339 | 0.069532 | -0.20062 | -0.0043344 | 121.2799 | 1.7807 | 29.9377 | -0.10071 | 121.3806 | -0.21057 | -0.2655 | 0.15564 | 26.532 | -0.35248 | 121.2982 | 121.4767 | -0.13275 | -0.1831 | 0.096131 | 0.041199 | -0.022888 | 2.0874 | 0.20599 | 0.16479 | -0.1236 | 0.17395 | 0.1236 | -0.10528 | 0.46234 | -0.045776 | -0.16937 | 0.073243 | 121.6873 | 121.5866 | 30.2444 | -121.669 | 121.6049 | 121.7834 | 26.8387 | -121.5866
1867.5938 | 121.8018 | -0.25177 | 121.3715 | 0.0026703 | 0.0029459 | 0.070741 | 0.003811 | 0.066689 | -0.0037769 | -0.00060234 | 0.0021363 | -0.0081155 | 0.065475 | 0.066755 | -0.20532 | -0.0021982 | 121.3715 | 1.9958 | 30.0659 | -0.013733 | 121.3348 | -0.16022 | -0.24261 | 0.27008 | 26.7975 | -0.18768 | 121.2387 | 121.4081 | -0.13275 | -0.14191 | 0.091553 | 0.009155 | -0.036621 | 2.2476 | 0.23804 | 0.22888 | 0 | 0.11902 | 0.10986 | -0.13275 | 0.52185 | 0.064087 | -0.045776 | 0.036621 | 121.5866 | 121.6232 | 30.3177 | -121.6141 | 121.4905 | 121.6599 | 27.0493 | -121.5134
1869.3594 | 121.7194 | -0.29755 | 121.4355 | 0.0026703 | 0.0091409 | 0.066896 | 0.00082022 | 0.066689 | 0.0015637 | 0.0013203 | 0.0021363 | -0.0017069 | 0.063553 | 0.069105 | -0.20276 | -0.0054026 | 121.3165 | 1.8906 | 29.924 | -0.064087 | 121.3852 | -0.20599 | -0.27466 | 0.20599 | 26.9577 | -0.31586 | 121.2936 | 121.4355 | -0.14648 | -0.18768 | 0.091552 | 0.022888 | -0.050354 | 2.1881 | 0.23346 | 0.21057 | -0.11902 | 0.15106 | 0.10986 | -0.14191 | 0.50354 | -0.018311 | -0.12817 | 0 | 121.6827 | 121.6141 | 30.2216 | -121.7102 | 121.5912 | 121.7331 | 27.2552 | -121.6232
1871.1406 | 121.7056 | -0.28839 | 121.4355 | -0.0049592 | 0.0078591 | 0.070528 | 0.0029566 | 0.069039 | 0.0015637 | 0.0017475 | -0.0054932 | -0.0027749 | 0.064407 | 0.070173 | -0.20041 | -0.0036936 | 121.2936 | 1.9135 | 29.8645 | -0.07782 | 121.3577 | -0.19226 | -0.28381 | 0.18768 | 27.0493 | -0.32959 | 121.3028 | 121.4722 | -0.16022 | -0.18768 | 0.09613 | 0.004578 | -0.07782 | 2.2018 | 0.21057 | 0.20599 | -0.14191 | 0.12817 | 0.10071 | -0.13275 | 0.47607 | -0.041199 | -0.14191 | 0.036621 | 121.6461 | 121.582 | 30.1529 | -121.7194 | 121.5912 | 121.7606 | 27.3376 | -121.6232
1872.9062 | 121.7468 | -0.2655 | 121.3943 | -0.0049592 | 0.0027323 | 0.070528 | 0.001034 | 0.068825 | -0.0031359 | 0.00025206 | 0.0021363 | -0.0061929 | 0.063126 | 0.06526 | -0.20724 | -0.00091641 | 121.3348 | 2.0599 | 29.9332 | -0.032043 | 121.312 | -0.16479 | -0.24261 | 0.2243 | 27.2049 | -0.24719 | 121.257 | 121.3898 | -0.11902 | -0.16022 | 0.10071 | 0.022888 | -0.082397 | 2.3254 | 0.23346 | 0.21057 | -0.059509 | 0.14648 | 0.10529 | -0.13733 | 0.48981 | 0.018311 | -0.086975 | -0.004577 | 121.5775 | 121.6003 | 30.1987 | -121.637 | 121.5225 | 121.6553 | 27.4704 | -121.5546
1874.625 | 121.8613 | -0.29755 | 121.4035 | -0.0049592 | 0.0059365 | 0.070741 | 0.00017942 | 0.068825 | 0.0039135 | 0.0028155 | 0.0021363 | -0.0027749 | 0.064621 | 0.068464 | -0.20019 | -0.004548 | 121.344 | 2.0279 | 29.8691 | -0.041199 | 121.3394 | -0.20142 | -0.27924 | 0.23346 | 27.3651 | -0.29755 | 121.2982 | 121.4264 | -0.15106 | -0.1831 | 0.09613 | 0.01831 | -0.064086 | 2.3254 | 0.25635 | 0.23804 | -0.059509 | 0.14648 | 0.11444 | -0.10528 | 0.531 | 0 | -0.11444 | 0.022889 | 121.637 | 121.6415 | 30.1666 | -121.6827 | 121.5958 | 121.7239 | 27.6627 | -121.5866
1876.3906 | 121.788 | -0.27466 | 121.3943 | -0.012589 | 0.0035867 | 0.070528 | 0.0031702 | 0.073097 | -0.0059131 | 3.8456e-05 | -0.0054932 | -0.0089701 | 0.063553 | 0.065046 | -0.20468 | -0.0026254 | 121.2936 | 2.0599 | 29.8599 | -0.050354 | 121.344 | -0.17853 | -0.26093 | 0.21057 | 27.3834 | -0.28381 | 121.2524 | 121.4264 | -0.14191 | -0.17395 | 0.09613 | 0.013733 | -0.050354 | 2.3346 | 0.2243 | 0.21057 | -0.10071 | 0.13275 | 0.10071 | -0.14191 | 0.48523 | -0.009155 | -0.10986 | 0.032044 | 121.6187 | 121.5683 | 30.1346 | -121.6553 | 121.5271 | 121.7011 | 27.6581 | -121.5683
1878.1719 | 121.6782 | -0.28839 | 121.3852 | 0.0026703 | 0.0089273 | 0.071169 | 0.0048792 | 0.070107 | 0.00070927 | 0.00046566 | -0.013123 | -0.0059793 | 0.064621 | 0.066328 | -0.20425 | -0.0021982 | 121.344 | 2.1561 | 29.9057 | -0.018311 | 121.312 | -0.17853 | -0.26093 | 0.23346 | 27.4979 | -0.26093 | 121.225 | 121.3852 | -0.15564 | -0.17853 | 0.10986 | 0.027466 | -0.073242 | 2.4445 | 0.27008 | 0.24261 | -0.041199 | 0.13275 | 0.10986 | -0.16022 | 0.52185 | 0.027466 | -0.082397 | 0 | 121.6003 | 121.6324 | 30.1941 | -121.6461 | 121.5134 | 121.6736 | 27.7863 | -121.5637
1879.8906 | 121.6553 | -0.28381 | 121.4218 | 0.0026703 | 0.0085001 | 0.06711 | -0.0025976 | 0.065834 | 0.0047681 | 0.0017475 | -0.013123 | -0.0027749 | 0.062485 | 0.069959 | -0.20041 | -0.0041208 | 121.3577 | 2.1469 | 29.8187 | -0.041199 | 121.344 | -0.21057 | -0.28839 | 0.24719 | 27.5116 | -0.3479 | 121.312 | 121.4355 | -0.15106 | -0.20142 | 0.073242 | -0.004578 | -0.07782 | 2.4307 | 0.24261 | 0.24719 | -0.064087 | 0.13275 | 0.082397 | -0.10986 | 0.531 | -0.064087 | -0.14648 | 0.013733 | 121.6278 | 121.6415 | 30.1025 | -121.7102 | 121.5958 | 121.7194 | 27.7954 | -121.6232
1881.6719 | 121.7056 | -0.31128 | 121.4172 | -0.0049592 | 0.0085001 | 0.072237 | 0.0018884 | 0.065834 | -0.0024951 | 0.0028155 | 0.0021363 | -0.0066201 | 0.064407 | 0.066114 | -0.20425 | -0.0024118 | 121.3577 | 2.2476 | 29.8782 | 0.004578 | 121.312 | -0.17395 | -0.25177 | 0.27466 | 27.6077 | -0.25177 | 121.2616 | 121.4127 | -0.1236 | -0.17395 | 0.13733 | 0.059509 | -0.10529 | 2.5589 | 0.31586 | 0.25635 | -0.059509 | 0.18768 | 0.13733 | -0.15564 | 0.58594 | 0.059509 | -0.07782 | -0.004577 | 121.6232 | 121.669 | 30.1895 | -121.669 | 121.5729 | 121.7239 | 27.919 | -121.5912
1883.375 | 121.7148 | -0.27924 | 121.3806 | -0.012589 | 0.0080727 | 0.066255 | 0.00082022 | 0.066902 | 0.0028455 | 0.0015339 | -0.0054932 | -0.0021341 | 0.065689 | 0.067823 | -0.1987 | -0.0056162 | 121.3303 | 2.179 | 29.7638 | -0.054932 | 121.3715 | -0.2243 | -0.28381 | 0.24719 | 27.5757 | -0.31586 | 121.312 | 121.4355 | -0.15564 | -0.20142 | 0.054932 | -0.004577 | -0.009155 | 2.4582 | 0.2243 | 0.22888 | -0.050354 | 0.1236 | 0.07782 | -0.068664 | 0.52643 | -0.036621 | -0.11444 | 0.054932 | 121.6507 | 121.6095 | 30.043 | -121.6644 | 121.5912 | 121.7148 | 27.8549 | -121.582
1885.1719 | 121.7789 | -0.25635 | 121.3852 | -0.0049592 | 0.0059365 | 0.069246 | 0.001034 | 0.068184 | 0.0019909 | 0.0028155 | -0.0054932 | -0.0034159 | 0.064407 | 0.069532 | -0.20254 | -0.0013436 | 121.2799 | 2.179 | 29.7089 | -0.082397 | 121.3486 | -0.21515 | -0.2655 | 0.19226 | 27.562 | -0.33875 | 121.2936 | 121.4584 | -0.16479 | -0.19684 | 0.041199 | -0.009155 | -0.036621 | 2.4353 | 0.17395 | 0.18311 | -0.10529 | 0.091553 | 0.05951 | -0.091553 | 0.44861 | -0.082397 | -0.14191 | 0.073242 | 121.6049 | 121.5363 | 29.9652 | -121.6507 | 121.55 | 121.7148 | 27.8183 | -121.582
1886.9375 | 121.7926 | -0.25635 | 121.3577 | -0.012589 | 0.0072183 | 0.069032 | -0.0011024 | 0.068398 | 0.00049567 | 0.00067926 | -0.020752 | -0.0036295 | 0.063126 | 0.068464 | -0.20041 | -0.0024118 | 121.3394 | 2.2888 | 29.8004 | -0.036621 | 121.3394 | -0.16937 | -0.24719 | 0.28381 | 27.6215 | -0.2655 | 121.2387 | 121.4035 | -0.14648 | -0.16479 | 0.086975 | 0.009156 | -0.01831 | 2.5452 | 0.21973 | 0.21057 | -0.01831 | 0.10986 | 0.091553 | -0.11902 | 0.54016 | -0.009155 | -0.10071 | 0.045776 | 121.5958 | 121.5958 | 30.0568 | -121.6049 | 121.4951 | 121.6599 | 27.8778 | -121.5225
1888.6406 | 121.7743 | -0.27466 | 121.3669 | -0.020218 | 0.0031595 | 0.069673 | 0.0016748 | 0.064125 | -0.0048449 | 0.00067926 | -0.0054932 | -0.0066201 | 0.063553 | 0.06825 | -0.20511 | -0.0036936 | 121.2982 | 2.3163 | 29.8096 | -0.045776 | 121.3211 | -0.19684 | -0.23804 | 0.23346 | 27.7542 | -0.29297 | 121.2616 | 121.4401 | -0.14648 | -0.18768 | 0.07782 | 0.036621 | -0.045776 | 2.5909 | 0.22888 | 0.19226 | -0.068664 | 0.12817 | 0.086975 | -0.10529 | 0.50812 | -0.018311 | -0.10529 | 0.073243 | 121.5958 | 121.5729 | 30.0842 | -121.6049 | 121.5363 | 121.7148 | 28.0289 | -121.5546
1890.4062 | 121.6873 | -0.31586 | 121.376 | -0.0049592 | 0.0082865 | 0.066255 | 0.002102 | 0.067116 | 0.0047681 | 0.0019611 | -0.0054932 | -0.0034159 | 0.064621 | 0.070173 | -0.20019 | -0.0041208 | 121.3394 | 2.3529 | 29.805 | -0.045776 | 121.3348 | -0.21515 | -0.28839 | 0.2655 | 27.8458 | -0.31586 | 121.2708 | 121.4218 | -0.16022 | -0.20599 | 0.10071 | 0.027466 | -0.041199 | 2.6688 | 0.27008 | 0.24262 | -0.036621 | 0.15564 | 0.10986 | -0.10529 | 0.58136 | 0 | -0.10986 | 0.045776 | 121.6507 | 121.6553 | 30.1209 | -121.6644 | 121.5866 | 121.7377 | 28.1616 | -121.582
1892.1875 | 121.7331 | -0.29755 | 121.3669 | 0.0026703 | 0.0067911 | 0.067964 | -3.4178e-05 | 0.065621 | 0.0024183 | 0.0011067 | -0.0054932 | -0.0025613 | 0.064194 | 0.070814 | -0.20062 | -0.0039072 | 121.2708 | 2.3209 | 29.7409 | -0.09613 | 121.3486 | -0.20142 | -0.31128 | 0.19684 | 27.8961 | -0.37079 | 121.2662 | 121.4539 | -0.17395 | -0.21057 | 0.09613 | -0.013733 | -0.01831 | 2.6184 | 0.20142 | 0.21515 | -0.09613 | 0.1236 | 0.086975 | -0.10071 | 0.49438 | -0.073243 | -0.16022 | 0.086975 | 121.6461 | 121.5683 | 30.0385 | -121.6782 | 121.5637 | 121.7514 | 28.1937 | -121.5775
1893.9531 | 121.7926 | -0.28839 | 121.3577 | -0.012589 | 0.0063639 | 0.074373 | 0.0012476 | 0.068611 | -0.0048449 | 3.8456e-05 | -0.013123 | -0.0085427 | 0.062271 | 0.066542 | -0.20532 | -0.0030526 | 121.3486 | 2.5223 | 29.9332 | -0.009155 | 121.3211 | -0.20142 | -0.25177 | 0.30212 | 28.2303 | -0.20599 | 121.1838 | 121.4172 | -0.13733 | -0.17853 | 0.086975 | 0.036621 | -0.036621 | 2.8107 | 0.27924 | 0.24261 | -0.009155 | 0.15106 | 0.10986 | -0.17395 | 0.59052 | 0.082397 | -0.027466 | 0.059509 | 121.6095 | 121.637 | 30.2216 | -121.6095 | 121.4722 | 121.7056 | 28.5187 | -121.5363
1895.6719 | 121.669 | -0.32959 | 121.4127 | -0.012589 | 0.0074319 | 0.071809 | -0.00046138 | 0.070107 | -0.00057253 | -0.00017514 | -0.013123 | -0.0021341 | 0.063339 | 0.069319 | -0.20425 | -0.0064706 | 121.2708 | 2.4261 | 29.8187 | -0.09613 | 121.3623 | -0.23804 | -0.31586 | 0.17395 | 28.2532 | -0.37079 | 121.2936 | 121.4264 | -0.18768 | -0.21515 | 0.091553 | 0.013733 | -0.050354 | 2.7557 | 0.23346 | 0.21973 | -0.14191 | 0.14191 | 0.11444 | -0.11902 | 0.50354 | -0.041199 | -0.15564 | 0.013733 | 121.6919 | 121.6003 | 30.1483 | -121.7285 | 121.6232 | 121.756 | 28.5828 | -121.6278
1897.4375 | 121.6782 | -0.33417 | 121.4035 | -0.0049592 | 0.0097817 | 0.069246 | -0.00024778 | 0.067757 | 0.0034863 | 0.0043109 | 0.0021363 | -0.0029885 | 0.06633 | 0.067823 | -0.19912 | -0.0041208 | 121.2753 | 2.449 | 29.8141 | -0.086975 | 121.3531 | -0.23346 | -0.29297 | 0.21057 | 28.3859 | -0.40741 | 121.2845 | 121.4493 | -0.19226 | -0.23346 | 0.10071 | 0.041198 | -0.050354 | 2.7832 | 0.24719 | 0.20599 | -0.12817 | 0.14191 | 0.10071 | -0.11902 | 0.54474 | -0.073243 | -0.17395 | 0.045777 | 121.6873 | 121.6095 | 30.1483 | -121.6965 | 121.6187 | 121.7834 | 28.7201 | -121.637
1899.1406 | 121.7514 | -0.28381 | 121.3577 | -0.020218 | 0.0063639 | 0.072023 | -0.00046138 | 0.06968 | -0.0031359 | 0.0028155 | -0.0054932 | -0.0064065 | 0.062271 | 0.06825 | -0.20361 | -0.001771 | 121.2982 | 2.5818 | 29.9332 | -0.064087 | 121.3074 | -0.19684 | -0.2655 | 0.25177 | 28.4637 | -0.31128 | 121.2296 | 121.4172 | -0.16479 | -0.1831 | 0.086975 | 0.01831 | -0.050354 | 2.8656 | 0.21973 | 0.20142 | -0.059509 | 0.11902 | 0.10071 | -0.12817 | 0.53558 | -0.027466 | -0.12817 | 0.059509 | 121.5912 | 121.582 | 30.217 | -121.6232 | 121.5134 | 121.701 | 28.7476 | -121.5408
1900.9219 | 121.7651 | -0.29755 | 121.3852 | -0.012589 | 0.0067911 | 0.069032 | 0.00552 | 0.068398 | -0.0020679 | -0.00060234 | -0.013123 | -0.0051247 | 0.065475 | 0.064833 | -0.20468 | -0.0058298 | 121.3531 | 2.6825 | 30.0018 | 0 | 121.3211 | -0.18768 | -0.2655 | 0.31586 | 28.7201 | -0.24261 | 121.2341 | 121.3715 | -0.15106 | -0.18768 | 0.10986 | 0.032043 | -0.064087 | 2.98 | 0.29755 | 0.2655 | -0.032044 | 0.14648 | 0.10986 | -0.15106 | 0.6134 | 0.054931 | -0.054932 | -0.013733 | 121.6187 | 121.6507 | 30.2994 | -121.6507 | 121.5317 | 121.669 | 29.0176 | -121.5729
1902.6875 | 121.756 | -0.27466 | 121.376 | 0.0026703 | 0.0040139 | 0.072878 | 0.0014612 | 0.068184 | -0.00035893 | 0.0028155 | -0.0054932 | -0.0049111 | 0.065903 | 0.068464 | -0.20382 | -0.0058298 | 121.3623 | 2.7008 | 30.0201 | -0.018311 | 121.2845 | -0.18768 | -0.24719 | 0.31128 | 28.7292 | -0.25635 | 121.2112 | 121.3623 | -0.14648 | -0.19684 | 0.086975 | 0.027466 | -0.091553 | 2.9755 | 0.25635 | 0.22888 | -0.013733 | 0.12817 | 0.07782 | -0.16479 | 0.58594 | 0.01831 | -0.05951 | -0.013733 | 121.5591 | 121.637 | 30.2948 | -121.6232 | 121.4859 | 121.637 | 29.0039 | -121.5729
1904.4688 | 121.8063 | -0.29297 | 121.3531 | -0.0049592 | 0.0033731 | 0.073305 | 0.0018884 | 0.069039 | -0.0050585 | 0.0013203 | -0.013123 | -0.0066201 | 0.063553 | 0.066755 | -0.20212 | -0.0043344 | 121.3348 | 2.7695 | 30.043 | -0.009155 | 121.3303 | -0.19684 | -0.27466 | 0.3067 | 28.9078 | -0.23346 | 121.2387 | 121.3669 | -0.15106 | -0.19684 | 0.096131 | 0.018311 | -0.022888 | 3.0624 | 0.28381 | 0.2655 | -0.01831 | 0.14191 | 0.096131 | -0.11444 | 0.59967 | 0.05951 | -0.036621 | 0.013733 | 121.6232 | 121.6278 | 30.336 | -121.6278 | 121.5317 | 121.6599 | 29.2007 | -121.55
1906.1875 | 121.669 | -0.32959 | 121.376 | -0.0049592 | 0.0093545 | 0.070955 | 0.0042382 | 0.068398 | 0.00092287 | -0.00081594 | -0.0054932 | -0.0055521 | 0.065475 | 0.069319 | -0.20361 | -0.0058298 | 121.2799 | 2.7054 | 29.9744 | -0.073242 | 121.312 | -0.23346 | -0.32044 | 0.21515 | 28.9902 | -0.36621 | 121.2753 | 121.3806 | -0.20599 | -0.22888 | 0.096131 | 0.009155 | -0.064087 | 3.035 | 0.25635 | 0.24719 | -0.096131 | 0.1236 | 0.10071 | -0.10071 | 0.54474 | -0.036621 | -0.13733 | 0.004577 | 121.6415 | 121.6095 | 30.304 | -121.6965 | 121.6049 | 121.7102 | 29.3198 | -121.6049
1907.9688 | 121.7972 | -0.28381 | 121.3623 | -0.0049592 | 0.0078591 | 0.072878 | 0.0014612 | 0.070107 | -0.0027087 | -0.00017514 | 0.0021363 | -0.0072611 | 0.062912 | 0.067823 | -0.20361 | -0.0058298 | 121.3257 | 2.8336 | 30.0888 | -0.013733 | 121.3074 | -0.20142 | -0.29297 | 0.32501 | 29.1504 | -0.24261 | 121.225 | 121.3531 | -0.14648 | -0.19226 | 0.082397 | -0.009156 | -0.054932 | 3.1174 | 0.27008 | 0.27924 | -0.036621 | 0.13733 | 0.091552 | -0.13733 | 0.60882 | 0.041198 | -0.050354 | -0.009156 | 121.5912 | 121.6095 | 30.3726 | -121.6553 | 121.5088 | 121.637 | 29.4342 | -121.5546
1909.75 | 121.7468 | -0.30212 | 121.3715 | -0.0049592 | 0.0072183 | 0.072237 | 0.0012476 | 0.07032 | 6.8274e-05 | -0.00017514 | 0.0021363 | -0.0066201 | 0.065048 | 0.066542 | -0.20468 | -0.0054026 | 121.3486 | 2.9297 | 30.1392 | 0 | 121.3028 | -0.21057 | -0.27008 | 0.32044 | 29.3381 | -0.26093 | 121.2341 | 121.3348 | -0.16937 | -0.21057 | 0.091553 | 0.032043 | -0.068665 | 3.2318 | 0.30212 | 0.27008 | -0.022888 | 0.13275 | 0.091553 | -0.13733 | 0.62256 | 0.041199 | -0.050354 | -0.036621 | 121.6049 | 121.6507 | 30.4413 | -121.6415 | 121.5363 | 121.637 | 29.6402 | -121.582
1911.4531 | 121.8201 | -0.29755 | 121.3577 | 0.0103 | 0.0012369 | 0.072023 | -0.0011024 | 0.066902 | -0.0012133 | -0.00038874 | -0.013123 | -0.0066201 | 0.063126 | 0.065687 | -0.20019 | -0.0034798 | 121.3165 | 2.9068 | 30.1163 | -0.036621 | 121.3028 | -0.23346 | -0.28381 | 0.29755 | 29.3243 | -0.27924 | 121.2204 | 121.376 | -0.17395 | -0.21515 | 0.064087 | 0.013733 | -0.054932 | 3.2043 | 0.26092 | 0.24719 | -0.041199 | 0.1236 | 0.082397 | -0.13733 | 0.59509 | 0.01831 | -0.064087 | 0.018311 | 121.6003 | 121.6141 | 30.4138 | -121.6415 | 121.5179 | 121.6736 | 29.6219 | -121.5729
1913.2188 | 121.6919 | -0.32501 | 121.3623 | 0.0026703 | 0.0099953 | 0.070741 | -0.0019568 | 0.068825 | 0.0069043 | 0.0030293 | -0.013123 | -0.00085232 | 0.061203 | 0.068678 | -0.19806 | -0.0043344 | 121.2524 | 2.8152 | 29.9927 | -0.10986 | 121.3486 | -0.23804 | -0.31128 | 0.24719 | 29.0588 | -0.41657 | 121.2662 | 121.3943 | -0.19684 | -0.23346 | 0.086975 | 0.013733 | -0.013733 | 3.1403 | 0.21515 | 0.20142 | -0.10986 | 0.12817 | 0.091553 | -0.096131 | 0.5722 | -0.091553 | -0.18311 | 0.032043 | 121.6736 | 121.5775 | 30.3177 | -121.6736 | 121.5912 | 121.7194 | 29.3839 | -121.5958
1915 | 121.6415 | -0.34332 | 121.3623 | -0.0049592 | 0.011064 | 0.071596 | 0.0027428 | 0.070534 | 0.0051953 | 0.0055927 | -0.0054932 | -0.0025613 | 0.065262 | 0.069105 | -0.20147 | -0.0056162 | 121.2982 | 2.9663 | 30.0842 | -0.073242 | 121.3165 | -0.23804 | -0.32044 | 0.27008 | 29.1 | -0.39825 | 121.2616 | 121.3806 | -0.20599 | -0.2243 | 0.10529 | 0.022888 | -0.045777 | 3.3096 | 0.27008 | 0.24719 | -0.064087 | 0.13733 | 0.11902 | -0.10071 | 0.6134 | -0.054931 | -0.17395 | 0.01831 | 121.6599 | 121.6415 | 30.4276 | -121.6827 | 121.6049 | 121.7239 | 29.4434 | -121.5866
1916.7031 | 121.788 | -0.30212 | 121.3394 | 0.0103 | 0.0087137 | 0.069887 | -0.0021704 | 0.065407 | -0.0016405 | 0.0047383 | -0.0054932 | -0.0066201 | 0.064194 | 0.068037 | -0.20276 | -0.0019846 | 121.3257 | 3.0762 | 30.1987 | -0.022888 | 121.2708 | -0.22888 | -0.27008 | 0.35248 | 29.5029 | -0.27924 | 121.1929 | 121.344 | -0.13733 | -0.21057 | 0.073242 | 0.032043 | -0.068665 | 3.3783 | 0.27924 | 0.24719 | -0.013733 | 0.16479 | 0.091553 | -0.14648 | 0.6546 | 0.022888 | -0.068665 | 0.004577 | 121.5729 | 121.6278 | 30.5008 | -121.6095 | 121.4951 | 121.6461 | 29.805 | -121.55
1918.4531 | 121.8109 | -0.31586 | 121.3303 | -0.012589 | 0.0052957 | 0.074373 | 0.002102 | 0.067757 | -0.0039905 | 0.0019611 | -0.0054932 | -0.0068337 | 0.063126 | 0.063551 | -0.20511 | -0.0032662 | 121.257 | 3.0991 | 30.1758 | -0.050354 | 121.2799 | -0.22888 | -0.29755 | 0.29755 | 29.6127 | -0.29297 | 121.1929 | 121.344 | -0.19226 | -0.21515 | 0.086975 | 0.018311 | -0.050354 | 3.4149 | 0.2655 | 0.24719 | -0.073242 | 0.1236 | 0.10071 | -0.13733 | 0.6134 | 0.022888 | -0.07782 | 0.013733 | 121.5958 | 121.5729 | 30.4916 | -121.6278 | 121.5088 | 121.6599 | 29.9286 | -121.5454
1920.25 | 121.7056 | -0.33875 | 121.3669 | -0.0049592 | 0.0085001 | 0.073305 | 0.0033838 | 0.06733 | 0.0013501 | 0.00089286 | -0.013123 | -0.0040567 | 0.067825 | 0.06825 | -0.20126 | -0.0054026 | 121.2341 | 3.067 | 30.1025 | -0.086975 | 121.3257 | -0.24719 | -0.33875 | 0.22888 | 29.6631 | -0.41657 | 121.2433 | 121.3989 | -0.2243 | -0.27008 | 0.091553 | 0 | -0.041198 | 3.4058 | 0.25177 | 0.25177 | -0.13275 | 0.11444 | 0.068664 | -0.1236 | 0.56763 | -0.07782 | -0.14648 | 0.032044 | 121.6644 | 121.5729 | 30.4413 | -121.7056 | 121.582 | 121.7377 | 30.0018 | -121.637
1922.0312 | 121.7606 | -0.31586 | 121.3577 | -0.012589 | 0.0099953 | 0.07245 | 0.0029566 | 0.067543 | -0.0039905 | 0.0013203 | -0.0054932 | -0.0042703 | 0.063553 | 0.06526 | -0.2034 | -0.0019846 | 121.3531 | 3.2913 | 30.2719 | 0.009155 | 121.2708 | -0.22888 | -0.28839 | 0.36621 | 29.9744 | -0.25177 | 121.2067 | 121.3486 | -0.18768 | -0.20599 | 0.086975 | 0.027466 | -0.086975 | 3.6072 | 0.32501 | 0.29755 | -0.004578 | 0.12817 | 0.10986 | -0.15106 | 0.68207 | 0.064087 | -0.045776 | -0.009155 | 121.5866 | 121.669 | 30.5878 | -121.6461 | 121.5225 | 121.6644 | 30.2902 | -121.5637
1923.8125 | 121.7377 | -0.31586 | 121.3623 | -0.0049592 | 0.0065775 | 0.073946 | -0.00067498 | 0.067971 | -0.0024951 | 0.0011067 | -0.013123 | -0.0076883 | 0.063126 | 0.067396 | -0.20318 | -0.0026254 | 121.3211 | 3.3005 | 30.2261 | -0.027466 | 121.2662 | -0.21057 | -0.29755 | 0.32959 | 29.9286 | -0.30212 | 121.2021 | 121.3577 | -0.17395 | -0.21515 | 0.10529 | 0.018311 | -0.096131 | 3.6163 | 0.28839 | 0.27008 | -0.041199 | 0.14191 | 0.10071 | -0.16022 | 0.64545 | 0.013733 | -0.086975 | -0.004578 | 121.582 | 121.637 | 30.542 | -121.6599 | 121.5179 | 121.6736 | 30.2444 | -121.5775
1925.5312 | 121.6507 | -0.35248 | 121.3989 | -0.0049592 | 0.017686 | 0.071596 | 0.001034 | 0.070107 | 0.0051953 | 0.0030293 | -0.0054932 | 0.00021568 | 0.067184 | 0.067823 | -0.20041 | -0.0039072 | 121.3394 | 3.2959 | 30.1804 | -0.036621 | 121.2982 | -0.25635 | -0.32501 | 0.33417 | 29.9194 | -0.35706 | 121.257 | 121.3989 | -0.20599 | -0.21973 | 0.09613 | 0.027466 | -0.10071 | 3.6484 | 0.31586 | 0.28839 | -0.059509 | 0.14648 | 0.13275 | -0.14191 | 0.68664 | -0.004578 | -0.13733 | 0 | 121.6507 | 121.6919 | 30.5328 | -121.7239 | 121.6095 | 121.7514 | 30.2719 | -121.6187
1927.2812 | 121.7697 | -0.30212 | 121.3257 | -0.012589 | 0.0074319 | 0.072878 | -0.0032386 | 0.067543 | 0.0019909 | 0.0040973 | 0.0021363 | -0.0029885 | 0.063553 | 0.06825 | -0.1987 | -0.0021982 | 121.257 | 3.3005 | 30.1392 | -0.082397 | 121.3211 | -0.24719 | -0.32044 | 0.29755 | 29.9332 | -0.37079 | 121.2616 | 121.3989 | -0.16937 | -0.23804 | 0.054932 | -0.018311 | -0.004578 | 3.6026 | 0.21973 | 0.23804 | -0.068665 | 0.13275 | 0.064087 | -0.064087 | 0.59967 | -0.068665 | -0.13275 | 0.073242 | 121.6232 | 121.5591 | 30.4413 | -121.6461 | 121.5637 | 121.7011 | 30.2353 | -121.5637
1929.0469 | 121.6736 | -0.3479 | 121.3852 | -0.0049592 | 0.0095681 | 0.073518 | 0.0035974 | 0.069252 | -0.0031359 | 0.0028155 | -0.0054932 | -0.0061929 | 0.066971 | 0.066969 | -0.2066 | -0.0024118 | 121.257 | 3.4012 | 30.1712 | -0.059509 | 121.3165 | -0.25177 | -0.32959 | 0.27924 | 30.0797 | -0.37537 | 121.2524 | 121.3852 | -0.19226 | -0.24719 | 0.09613 | 0.01831 | -0.068665 | 3.7491 | 0.28839 | 0.27008 | -0.12817 | 0.15564 | 0.10071 | -0.13275 | 0.62714 | -0.027466 | -0.12817 | 0 | 121.6644 | 121.6049 | 30.5191 | -121.7148 | 121.6003 | 121.7331 | 30.4276 | -121.6324
1930.7656 | 121.6782 | -0.34332 | 121.3989 | -0.0049592 | 0.010423 | 0.071809 | 0.0018884 | 0.066475 | -0.00035893 | 3.8456e-05 | -0.013123 | -0.0053385 | 0.063766 | 0.066542 | -0.20276 | -0.0015572 | 121.2341 | 3.4149 | 30.1392 | -0.07782 | 121.3303 | -0.26093 | -0.32501 | 0.26093 | 30.1941 | -0.39368 | 121.2753 | 121.3943 | -0.20142 | -0.25177 | 0.082398 | 0.018311 | -0.068665 | 3.7582 | 0.2655 | 0.24719 | -0.16479 | 0.14191 | 0.091553 | -0.1236 | 0.60425 | -0.050354 | -0.14191 | -0.004578 | 121.6736 | 121.5775 | 30.4825 | -121.7239 | 121.6187 | 121.7377 | 30.5374 | -121.6507
1932.5312 | 121.7789 | -0.29755 | 121.3577 | -0.012589 | 0.011704 | 0.070955 | 0.0029566 | 0.069252 | 0.0030591 | 0.0013203 | -0.013123 | -0.0049111 | 0.068253 | 0.069746 | -0.20169 | -0.0043344 | 121.344 | 3.598 | 30.2673 | 0.022888 | 121.3028 | -0.19226 | -0.27008 | 0.41657 | 30.2856 | -0.27466 | 121.2204 | 121.3531 | -0.17395 | -0.20142 | 0.10528 | 0.027465 | -0.054932 | 3.8956 | 0.32043 | 0.29297 | -0.013733 | 0.1236 | 0.09613 | -0.13733 | 0.71411 | 0.022888 | -0.073242 | -0.004578 | 121.6003 | 121.6415 | 30.5649 | -121.6278 | 121.5179 | 121.6507 | 30.5832 | -121.5591
1934.2969 | 121.7606 | -0.31586 | 121.3211 | -0.0049592 | 0.0055093 | 0.074159 | -0.00088858 | 0.067543 | -0.0016405 | 0.00067926 | -0.013123 | -0.0068337 | 0.062912 | 0.06761 | -0.2034 | -0.001771 | 121.2936 | 3.6163 | 30.2078 | -0.032043 | 121.3028 | -0.21515 | -0.27008 | 0.33417 | 30.4321 | -0.31128 | 121.2204 | 121.3852 | -0.17395 | -0.20142 | 0.10071 | 0.045776 | -0.018311 | 3.9322 | 0.28381 | 0.23804 | -0.027466 | 0.14191 | 0.11444 | -0.10071 | 0.65002 | 0.004578 | -0.10986 | 0.064087 | 121.6187 | 121.6095 | 30.5237 | -121.5912 | 121.5363 | 121.701 | 30.748 | -121.5225
1936 | 121.7926 | -0.32959 | 121.3531 | 0.0026703 | 0.0067911 | 0.075227 | 0.0048792 | 0.06968 | -0.0031359 | 3.8456e-05 | -0.013123 | -0.0072611 | 0.064194 | 0.068464 | -0.20404 | -0.0021982 | 121.3303 | 3.7262 | 30.2628 | 0.009155 | 121.312 | -0.20142 | -0.30212 | 0.40741 | 30.7159 | -0.22888 | 121.2296 | 121.3394 | -0.17853 | -0.20142 | 0.12817 | 0.027466 | -0.041198 | 4.0558 | 0.33875 | 0.31128 | -0.022888 | 0.15106 | 0.12817 | -0.1236 | 0.737 | 0.10071 | -0.027466 | -0.013732 | 121.6415 | 121.6599 | 30.5923 | -121.6553 | 121.5591 | 121.669 | 31.0455 | -121.5546
1937.7656 | 121.7697 | -0.29755 | 121.3577 | -0.0049592 | 0.0057229 | 0.076296 | 0.001034 | 0.067543 | -0.0020679 | 0.0021747 | 0.0021363 | -0.0064065 | 0.063553 | 0.065473 | -0.20447 | -0.0049752 | 121.2845 | 3.7216 | 30.1941 | -0.013733 | 121.3074 | -0.21515 | -0.28839 | 0.36163 | 30.6976 | -0.3067 | 121.225 | 121.3669 | -0.16022 | -0.20599 | 0.082397 | 0.009155 | -0.050354 | 4.0192 | 0.28381 | 0.27466 | -0.073242 | 0.13733 | 0.091552 | -0.13275 | 0.65918 | -0.009156 | -0.10071 | 0.009155 | 121.6049 | 121.582 | 30.4916 | -121.6461 | 121.5225 | 121.6644 | 30.9952 | -121.5637
1939.4688 | 121.6553 | -0.34332 | 121.3989 | -0.0049592 | 0.010423 | 0.072878 | -0.0021704 | 0.071602 | 0.0056225 | 0.0023883 | -0.0054932 | 0.00042948 | 0.065689 | 0.067823 | -0.19891 | -0.0030526 | 121.3303 | 3.772 | 30.1483 | -0.041199 | 121.3165 | -0.24719 | -0.31586 | 0.35248 | 30.7709 | -0.37994 | 121.257 | 121.3623 | -0.17853 | -0.21973 | 0.096131 | 0.027466 | -0.082398 | 4.1153 | 0.30212 | 0.27466 | -0.068665 | 0.16479 | 0.1236 | -0.14191 | 0.6958 | -0.036621 | -0.16022 | -0.036621 | 121.6599 | 121.6736 | 30.4916 | -121.7148 | 121.6003 | 121.7056 | 31.1142 | -121.6187
1941.25 | 121.6873 | -0.32959 | 121.3852 | -0.0049592 | 0.011064 | 0.07245 | -0.00088858 | 0.071602 | 0.0045545 | 0.0051655 | -0.0054932 | -0.0025613 | 0.065262 | 0.068678 | -0.20019 | -0.0066842 | 121.3211 | 3.8681 | 30.1712 | -0.018311 | 121.3486 | -0.24719 | -0.32044 | 0.39825 | 30.9723 | -0.32959 | 121.2479 | 121.3898 | -0.19684 | -0.23346 | 0.082398 | 0.009155 | -0.036621 | 4.1977 | 0.31128 | 0.30212 | -0.064087 | 0.13275 | 0.096131 | -0.13733 | 0.72784 | 0 | -0.096131 | 0.004578 | 121.6782 | 121.6507 | 30.5008 | -121.7056 | 121.5775 | 121.7194 | 31.3019 | -121.6187
1942.9688 | 121.7102 | -0.33417 | 121.3577 | -0.020218 | 0.0097817 | 0.075441 | -0.00046138 | 0.070748 | 0.0028455 | 0.0023883 | -0.013123 | -0.0051247 | 0.064194 | 0.068891 | -0.20425 | -0.0030526 | 121.2433 | 3.8635 | 30.1392 | -0.059509 | 121.312 | -0.26093 | -0.32501 | 0.33417 | 31.0913 | -0.3891 | 121.2753 | 121.4172 | -0.21057 | -0.2243 | 0.073242 | 0.009155 | -0.045776 | 4.1977 | 0.27466 | 0.2655 | -0.11444 | 0.1236 | 0.10986 | -0.082397 | 0.66833 | -0.054932 | -0.16479 | 0.059509 | 121.6461 | 121.5775 | 30.4733 | -121.6827 | 121.6095 | 121.7514 | 31.4255 | -121.582
1944.6719 | 121.7239 | -0.33417 | 121.3806 | -0.0049592 | 0.01085 | 0.075014 | 0.0027428 | 0.070961 | 0.00070927 | 0.0034565 | 0.0021363 | -0.0029885 | 0.066544 | 0.068678 | -0.20404 | -0.0039072 | 121.2479 | 3.9276 | 30.1209 | -0.036621 | 121.3211 | -0.25177 | -0.32959 | 0.32044 | 31.1188 | -0.37994 | 121.2479 | 121.4127 | -0.21515 | -0.21973 | 0.082397 | 0.004577 | -0.059509 | 4.2618 | 0.29755 | 0.29297 | -0.13275 | 0.11902 | 0.11444 | -0.13275 | 0.6546 | -0.045777 | -0.16022 | 0.032044 | 121.6553 | 121.582 | 30.455 | -121.7102 | 121.582 | 121.7468 | 31.4529 | -121.6003
1946.4375 | 121.7697 | -0.29755 | 121.3303 | -0.012589 | 0.010636 | 0.0748 | -0.00088858 | 0.069466 | -0.00057253 | 0.0040973 | -0.0054932 | -0.0032021 | 0.065689 | 0.066114 | -0.20083 | -0.0015572 | 121.3348 | 4.1245 | 30.249 | 0.032043 | 121.2708 | -0.21973 | -0.28381 | 0.44403 | 31.4209 | -0.2655 | 121.2112 | 121.3623 | -0.1831 | -0.19684 | 0.077819 | 0.013733 | -0.059509 | 4.422 | 0.32959 | 0.31586 | 0.004578 | 0.11444 | 0.10071 | -0.11902 | 0.74158 | 0.032043 | -0.068665 | 0.032044 | 121.5683 | 121.6324 | 30.5466 | -121.6141 | 121.5088 | 121.6599 | 31.7184 | -121.5271
1948.2188 | 121.7194 | -0.32044 | 121.3715 | -0.012589 | 0.013413 | 0.072664 | 0.00060662 | 0.06968 | 0.0036999 | 0.0023883 | -0.0054932 | -0.00085232 | 0.067184 | 0.068678 | -0.20212 | -0.0041208 | 121.2708 | 4.1153 | 30.1758 | -0.004578 | 121.3257 | -0.23804 | -0.32959 | 0.39825 | 31.4529 | -0.35706 | 121.2662 | 121.3806 | -0.19226 | -0.24261 | 0.082398 | -0.009155 | -0.045776 | 4.4357 | 0.31586 | 0.32501 | -0.10071 | 0.12817 | 0.07782 | -0.10529 | 0.71869 | -0.036621 | -0.11444 | 0.009155 | 121.6461 | 121.5912 | 30.4962 | -121.701 | 121.5866 | 121.7011 | 31.7734 | -121.6141
1949.9219 | 121.7148 | -0.33417 | 121.344 | -0.0049592 | 0.011277 | 0.075655 | -0.00088858 | 0.070107 | 0.0024183 | 0.0021747 | -0.013123 | -0.0021341 | 0.065689 | 0.069532 | -0.20147 | -0.002839 | 121.2341 | 4.1107 | 30.1209 | -0.068665 | 121.3303 | -0.24261 | -0.32501 | 0.33875 | 31.4255 | -0.41657 | 121.257 | 121.4081 | -0.21057 | -0.25635 | 0.091552 | 0.009155 | -0.013733 | 4.4449 | 0.2655 | 0.25635 | -0.10986 | 0.1236 | 0.077819 | -0.086975 | 0.67291 | -0.082398 | -0.16022 | 0.064087 | 121.6644 | 121.5683 | 30.455 | -121.669 | 121.5912 | 121.7422 | 31.7596 | -121.6003
1951.6406 | 121.788 | -0.32501 | 121.3303 | -0.012589 | 0.0089273 | 0.075014 | 0.002102 | 0.069039 | -0.0067675 | 0.0015339 | -0.013123 | -0.0068337 | 0.063766 | 0.066114 | -0.20425 | -0.0015572 | 121.257 | 4.2755 | 30.2399 | 0.004578 | 121.2845 | -0.21973 | -0.29297 | 0.38452 | 31.7184 | -0.32501 | 121.1929 | 121.3852 | -0.1831 | -0.21515 | 0.10529 | 0.032043 | -0.045776 | 4.6005 | 0.32959 | 0.29755 | -0.073242 | 0.14191 | 0.10986 | -0.13733 | 0.70953 | 0 | -0.10986 | 0.054932 | 121.6095 | 121.582 | 30.5649 | -121.6232 | 121.5179 | 121.7102 | 32.0435 | -121.5454
1953.4062 | 121.8018 | -0.32501 | 121.344 | -0.012589 | 0.0097817 | 0.073946 | 0.0033838 | 0.07032 | -0.0046313 | -0.0016705 | 0.0021363 | -0.0068337 | 0.066971 | 0.068891 | -0.20788 | -0.0034798 | 121.312 | 4.3991 | 30.3177 | 0.027466 | 121.2753 | -0.21515 | -0.30212 | 0.43945 | 31.8375 | -0.25635 | 121.1884 | 121.3669 | -0.1831 | -0.19684 | 0.10986 | 0.022888 | -0.068664 | 4.7241 | 0.35248 | 0.32959 | -0.032043 | 0.14191 | 0.12817 | -0.15564 | 0.76446 | 0.068664 | -0.05951 | 0.022888 | 121.6003 | 121.637 | 30.6427 | -121.6461 | 121.5134 | 121.6919 | 32.1625 | -121.5408
1955.1875 | 121.7743 | -0.30212 | 121.344 | -0.012589 | 0.0091409 | 0.076509 | -0.00046138 | 0.071388 | -0.00099973 | 0.0015339 | 0.0021363 | -0.0040567 | 0.063126 | 0.068037 | -0.20169 | -0.0043344 | 121.344 | 4.4861 | 30.3406 | 0.036621 | 121.2799 | -0.20599 | -0.29297 | 0.47607 | 32.0709 | -0.27924 | 121.1884 | 121.3394 | -0.17853 | -0.20599 | 0.09613 | 0.009155 | -0.064087 | 4.7882 | 0.33875 | 0.32959 | 0 | 0.1236 | 0.09613 | -0.15564 | 0.7782 | 0.022888 | -0.073242 | -0.004577 | 121.582 | 121.6461 | 30.6427 | -121.637 | 121.4905 | 121.6415 | 32.373 | -121.55
1956.9062 | 121.8018 | -0.31128 | 121.3348 | 0.0026703 | 0.0093545 | 0.074373 | 0.0057336 | 0.069466 | -0.0033495 | 0.00046566 | -0.0054932 | -0.0087563 | 0.065903 | 0.06761 | -0.20553 | -0.0043344 | 121.3257 | 4.6326 | 30.4367 | 0.045776 | 121.2708 | -0.23346 | -0.28839 | 0.45319 | 32.1762 | -0.25635 | 121.2021 | 121.3257 | -0.20599 | -0.22888 | 0.07782 | 0.022888 | -0.064087 | 4.9438 | 0.35705 | 0.33417 | -0.009155 | 0.10528 | 0.082397 | -0.13275 | 0.76446 | 0.054931 | -0.027466 | -0.009155 | 121.582 | 121.637 | 30.748 | -121.6232 | 121.5134 | 121.637 | 32.4875 | -121.5637
1958.6875 | 121.6873 | -0.35248 | 121.3486 | -0.020218 | 0.014909 | 0.074373 | 0.0044518 | 0.068398 | 0.0034863 | 0.00025206 | -0.0054932 | -0.0034159 | 0.069534 | 0.068464 | -0.20361 | -0.0060434 | 121.225 | 4.5639 | 30.3452 | -0.050354 | 121.3394 | -0.27466 | -0.33417 | 0.35706 | 32.0663 | -0.42114 | 121.2616 | 121.3715 | -0.23804 | -0.2655 | 0.07782 | 0.018311 | -0.009155 | 4.9164 | 0.30212 | 0.28381 | -0.1236 | 0.11444 | 0.086975 | -0.086975 | 0.70953 | -0.068665 | -0.15564 | 0.022888 | 121.6919 | 121.5775 | 30.6976 | -121.6827 | 121.6141 | 121.7239 | 32.4188 | -121.6141
1960.4531 | 121.7377 | -0.33875 | 121.3211 | -0.0049592 | 0.0093545 | 0.076723 | 0.0035974 | 0.070748 | -0.0022815 | 0.0023883 | -0.013123 | -0.0079019 | 0.065262 | 0.068464 | -0.20233 | -0.0054026 | 121.2662 | 4.7424 | 30.5145 | 0 | 121.2662 | -0.25177 | -0.29297 | 0.43488 | 32.222 | -0.32501 | 121.1975 | 121.344 | -0.20599 | -0.21515 | 0.086975 | 0.045776 | -0.054932 | 5.0812 | 0.33875 | 0.29297 | -0.054932 | 0.13275 | 0.1236 | -0.1236 | 0.77362 | 0.013733 | -0.10986 | 0.022888 | 121.6049 | 121.6049 | 30.8533 | -121.6141 | 121.5363 | 121.6827 | 32.5607 | -121.5363
1962.25 | 121.6782 | -0.35706 | 121.3623 | -0.020218 | 0.012986 | 0.075441 | 0.0035974 | 0.071602 | 0.0022047 | 0.0026019 | 0.0021363 | -0.0057657 | 0.065048 | 0.06825 | -0.20318 | -0.0066842 | 121.2982 | 4.8981 | 30.6427 | 0.054932 | 121.2616 | -0.22888 | -0.30212 | 0.47607 | 32.4509 | -0.29755 | 121.2067 | 121.3257 | -0.20599 | -0.23346 | 0.12817 | 0.054932 | -0.10071 | 5.2551 | 0.41199 | 0.35706 | -0.064087 | 0.15106 | 0.1236 | -0.15564 | 0.83313 | 0.05951 | -0.064087 | -0.036621 | 121.6187 | 121.6553 | 30.9998 | -121.6644 | 121.5637 | 121.6827 | 32.8079 | -121.5958
1964.0156 | 121.7468 | -0.33875 | 121.3303 | -0.0049592 | 0.0067911 | 0.076723 | 0.00017942 | 0.068611 | -0.00057253 | 0.0023883 | -0.013123 | -0.0064065 | 0.062912 | 0.06761 | -0.20212 | -0.0030526 | 121.2708 | 4.9622 | 30.6885 | 0.013733 | 121.2662 | -0.24719 | -0.29755 | 0.45319 | 32.4509 | -0.33417 | 121.1929 | 121.2982 | -0.20142 | -0.24261 | 0.091553 | 0.041199 | -0.064087 | 5.3009 | 0.35248 | 0.31128 | -0.059509 | 0.13733 | 0.09613 | -0.13733 | 0.79193 | 0.004578 | -0.091552 | -0.032043 | 121.6049 | 121.6095 | 31.0272 | -121.6278 | 121.5317 | 121.637 | 32.7896 | -121.5729
1965.7188 | 121.6507 | -0.37079 | 121.3623 | -0.0049592 | 0.01085 | 0.074159 | -0.0011024 | 0.071388 | 0.0056225 | 0.0026019 | -0.013123 | -0.0017069 | 0.06633 | 0.069319 | -0.19848 | -0.0032662 | 121.2616 | 4.9988 | 30.7068 | -0.013733 | 121.2845 | -0.26093 | -0.35706 | 0.42114 | 32.3456 | -0.43945 | 121.2296 | 121.312 | -0.24261 | -0.27466 | 0.10986 | 0.013733 | -0.07782 | 5.3696 | 0.35706 | 0.34332 | -0.10071 | 0.12817 | 0.096131 | -0.13275 | 0.79193 | -0.068664 | -0.16479 | -0.050354 | 121.6553 | 121.6324 | 31.0776 | -121.7194 | 121.6003 | 121.6827 | 32.7164 | -121.637
1967.4844 | 121.6919 | -0.38452 | 121.344 | -0.0049592 | 0.012345 | 0.076509 | -0.0021704 | 0.072029 | 0.0032727 | 0.0045245 | -0.0054932 | -0.0010659 | 0.066116 | 0.068037 | -0.19827 | -0.0026254 | 121.1884 | 5.0079 | 30.7663 | -0.045776 | 121.2982 | -0.27924 | -0.3479 | 0.40283 | 32.3044 | -0.46234 | 121.2296 | 121.3486 | -0.23346 | -0.27008 | 0.10529 | 0.036621 | -0.045776 | 5.3925 | 0.33875 | 0.30212 | -0.15564 | 0.15106 | 0.11444 | -0.11444 | 0.78735 | -0.07782 | -0.19226 | 0.004578 | 121.6827 | 121.5729 | 31.1508 | -121.6919 | 121.6141 | 121.7331 | 32.6889 | -121.6141
1969.2812 | 121.7606 | -0.33417 | 121.2936 | -0.012589 | 0.0097817 | 0.077364 | 0.001034 | 0.068825 | -0.0039905 | 0.0015339 | 0.0021363 | -0.0079019 | 0.062271 | 0.065901 | -0.20254 | -0.0024118 | 121.2387 | 5.2643 | 30.9952 | 0.013733 | 121.2341 | -0.25177 | -0.31128 | 0.43488 | 32.4646 | -0.32959 | 121.1746 | 121.3394 | -0.20142 | -0.24719 | 0.082397 | 0.022888 | -0.059509 | 5.5984 | 0.3479 | 0.32501 | -0.054932 | 0.13275 | 0.086975 | -0.11902 | 0.76904 | 0.004577 | -0.082398 | 0.045777 | 121.5683 | 121.5729 | 31.3293 | -121.6049 | 121.5088 | 121.6736 | 32.7988 | -121.5408
1971.0625 | 121.701 | -0.35706 | 121.3715 | 0.0103 | 0.011704 | 0.075655 | -0.0017432 | 0.071602 | 0.0047681 | 0.0034565 | -0.0054932 | -0.0029885 | 0.063553 | 0.069319 | -0.19848 | -0.0036936 | 121.2753 | 5.3696 | 31.1142 | 0.004578 | 121.2845 | -0.28839 | -0.33417 | 0.48981 | 32.6202 | -0.37994 | 121.2296 | 121.3715 | -0.22888 | -0.24719 | 0.068665 | 0.022889 | -0.086975 | 5.7266 | 0.36163 | 0.33875 | -0.09613 | 0.12817 | 0.10986 | -0.14191 | 0.84686 | -0.022888 | -0.13275 | 0 | 121.6415 | 121.6324 | 31.4713 | -121.7056 | 121.5866 | 121.7285 | 32.9773 | -121.6187
1972.7812 | 121.6873 | -0.35248 | 121.344 | -0.012589 | 0.012773 | 0.076296 | -3.4178e-05 | 0.069466 | 0.0043409 | 0.0026019 | -0.0054932 | -0.0014933 | 0.062698 | 0.071455 | -0.20083 | -0.002839 | 121.2799 | 5.4932 | 31.2515 | 0.013733 | 121.2982 | -0.27008 | -0.3479 | 0.49439 | 32.7255 | -0.38452 | 121.2296 | 121.3806 | -0.21057 | -0.24261 | 0.082397 | 0.004578 | -0.045776 | 5.8456 | 0.36621 | 0.36163 | -0.064087 | 0.14191 | 0.10986 | -0.11444 | 0.84686 | -0.032043 | -0.14191 | 0.036621 | 121.6507 | 121.6324 | 31.604 | -121.6919 | 121.582 | 121.7331 | 33.078 | -121.5866
1974.5469 | 121.6827 | -0.36163 | 121.3394 | 0.0103 | 0.0080727 | 0.078859 | 0.0025292 | 0.071602 | 0.00049567 | 0.0034565 | -0.0054932 | -0.0066201 | 0.063766 | 0.068037 | -0.20382 | -0.0015572 | 121.1884 | 5.5801 | 31.3385 | -0.032043 | 121.2799 | -0.28381 | -0.35248 | 0.39825 | 32.3776 | -0.41657 | 121.225 | 121.3669 | -0.23804 | -0.27466 | 0.07782 | 0.009155 | -0.05951 | 5.9418 | 0.32959 | 0.32044 | -0.15106 | 0.1236 | 0.086975 | -0.11444 | 0.75989 | -0.054932 | -0.14191 | 0.027465 | 121.6415 | 121.55 | 31.7001 | -121.6919 | 121.5866 | 121.7285 | 32.7393 | -121.6141
1976.3281 | 121.7285 | -0.33875 | 121.3211 | -0.012589 | 0.012345 | 0.077364 | 0.0053064 | 0.071388 | -0.0035633 | 0.0026019 | -0.0054932 | -0.0081155 | 0.066971 | 0.069105 | -0.20489 | -0.0024118 | 121.2982 | 5.8411 | 31.6269 | 0.082397 | 121.2662 | -0.22888 | -0.3067 | 0.52643 | 32.5928 | -0.27924 | 121.17 | 121.3486 | -0.18768 | -0.23804 | 0.10986 | 0.032043 | -0.054932 | 6.1798 | 0.42114 | 0.3891 | -0.022888 | 0.15106 | 0.10071 | -0.15106 | 0.86517 | 0.059509 | -0.041199 | 0.027466 | 121.6049 | 121.637 | 31.9656 | -121.6278 | 121.5088 | 121.6873 | 32.9315 | -121.5591
1978.0938 | 121.6919 | -0.37994 | 121.3623 | -0.012589 | 0.011277 | 0.079073 | 0.0016748 | 0.072029 | 0.0015637 | 0.0028155 | 0.0021363 | -0.0023477 | 0.065262 | 0.067396 | -0.20212 | -0.0034798 | 121.2158 | 5.8411 | 31.636 | -0.018311 | 121.2799 | -0.28381 | -0.35248 | 0.41657 | 32.5653 | -0.40741 | 121.257 | 121.3577 | -0.23804 | -0.27466 | 0.096131 | 0.027466 | -0.082398 | 6.221 | 0.36163 | 0.33417 | -0.14649 | 0.14191 | 0.10529 | -0.10529 | 0.79651 | -0.027466 | -0.13275 | -0.004578 | 121.6599 | 121.5958 | 32.016 | -121.7148 | 121.637 | 121.7377 | 32.9453 | -121.637
1979.8125 | 121.6919 | -0.36621 | 121.3486 | -0.0049592 | 0.0132 | 0.075868 | -0.0025976 | 0.070961 | 0.0041273 | 0.0036701 | -0.0054932 | -0.0036295 | 0.063339 | 0.068037 | -0.19998 | -0.0047616 | 121.2845 | 6.0196 | 31.7917 | 0.045776 | 121.2936 | -0.2655 | -0.34332 | 0.50812 | 32.5928 | -0.36621 | 121.2387 | 121.3669 | -0.21515 | -0.25177 | 0.10071 | 0.022888 | -0.054932 | 6.3858 | 0.41199 | 0.3891 | -0.064087 | 0.15106 | 0.11444 | -0.10986 | 0.87433 | 0 | -0.11444 | 0.01831 | 121.6599 | 121.6507 | 32.1579 | -121.6919 | 121.6049 | 121.7331 | 32.959 | -121.6003
1981.5312 | 121.7148 | -0.34332 | 121.3531 | -0.020218 | 0.012345 | 0.075868 | -0.0025976 | 0.072457 | 0.0024183 | 0.0034565 | -0.0054932 | -0.0019205 | 0.066757 | 0.067182 | -0.20147 | -0.001771 | 121.2067 | 6.102 | 31.8695 | 0 | 121.3074 | -0.28381 | -0.32959 | 0.43488 | 32.6614 | -0.43488 | 121.2112 | 121.344 | -0.23346 | -0.27466 | 0.05951 | 0.013733 | -0.045776 | 6.4453 | 0.34332 | 0.32959 | -0.14648 | 0.10986 | 0.068665 | -0.14191 | 0.7782 | -0.091552 | -0.16022 | -0.009155 | 121.6507 | 121.55 | 32.2128 | -121.6827 | 121.5546 | 121.6873 | 33.0048 | -121.6278
1983.2969 | 121.7194 | -0.35706 | 121.3394 | -0.012589 | 0.016831 | 0.077364 | 0.0044518 | 0.071816 | 0.0036999 | 0.0038837 | -0.013123 | -0.0032021 | 0.069107 | 0.066542 | -0.20468 | -0.0039072 | 121.225 | 6.2942 | 32.048 | 0.036621 | 121.3074 | -0.2655 | -0.3479 | 0.49439 | 32.8995 | -0.3891 | 121.2387 | 121.3623 | -0.22888 | -0.2655 | 0.091553 | 0.009156 | -0.032044 | 6.6513 | 0.39368 | 0.38452 | -0.11444 | 0.12817 | 0.091553 | -0.10071 | 0.85144 | -0.032043 | -0.1236 | 0.022888 | 121.6644 | 121.582 | 32.4051 | -121.6873 | 121.5958 | 121.7194 | 33.2565 | -121.6049
1985.0625 | 121.8018 | -0.32044 | 121.2982 | -0.012589 | 0.010423 | 0.079286 | 0.0029566 | 0.070534 | -0.0050585 | 0.0026019 | -0.013123 | -0.0072611 | 0.066757 | 0.068891 | -0.2066 | -0.0024118 | 121.2524 | 6.5598 | 32.2815 | 0.10071 | 121.2616 | -0.23346 | -0.28381 | 0.54932 | 33.0688 | -0.27008 | 121.1884 | 121.3303 | -0.20599 | -0.24261 | 0.086976 | 0.036622 | -0.036621 | 6.8802 | 0.42114 | 0.38452 | -0.045777 | 0.11444 | 0.07782 | -0.10986 | 0.86975 | 0.050354 | -0.027466 | 0.032043 | 121.582 | 121.5729 | 32.6019 | -121.582 | 121.5088 | 121.6507 | 33.3893 | -121.5408
1986.8438 | 121.8109 | -0.32044 | 121.3074 | -0.0049592 | 0.010423 | 0.081636 | 0.0029566 | 0.071175 | -0.0020679 | -0.00017514 | -0.013123 | -0.0066201 | 0.063339 | 0.066969 | -0.20681 | -0.0041208 | 121.2799 | 6.7062 | 32.3914 | 0.10986 | 121.2479 | -0.23346 | -0.31586 | 0.55389 | 33.165 | -0.27466 | 121.1838 | 121.3531 | -0.19226 | -0.21057 | 0.086976 | 0.004578 | -0.059509 | 7.0267 | 0.4303 | 0.42572 | -0.027466 | 0.12817 | 0.10986 | -0.1236 | 0.87433 | 0.045777 | -0.064087 | 0.045776 | 121.5683 | 121.6003 | 32.7118 | -121.6232 | 121.5042 | 121.6736 | 33.4854 | -121.5179
1988.5312 | 121.6736 | -0.39368 | 121.312 | -0.0049592 | 0.012986 | 0.076936 | 0.0029566 | 0.070107 | 0.0056225 | 0.0034565 | -0.0054932 | -0.0029885 | 0.067612 | 0.06825 | -0.20126 | -0.0071114 | 121.2112 | 6.7062 | 32.3776 | 0.027466 | 121.3211 | -0.27466 | -0.34332 | 0.49439 | 32.991 | -0.45319 | 121.2296 | 121.3577 | -0.23346 | -0.26093 | 0.11902 | 0.050354 | 0.009155 | 7.0999 | 0.42114 | 0.37079 | -0.10071 | 0.16022 | 0.13275 | -0.082398 | 0.88806 | -0.059509 | -0.19226 | 0.045776 | 121.7148 | 121.6049 | 32.7713 | -121.6553 | 121.6232 | 121.7514 | 33.3847 | -121.5729
1990.3125 | 121.6827 | -0.36163 | 121.344 | -0.0049592 | 0.0132 | 0.080995 | 0.0050928 | 0.073738 | 0.0011365 | 0.0030293 | -0.013123 | -0.0046975 | 0.068253 | 0.066969 | -0.20361 | -0.0041208 | 121.1838 | 6.926 | 32.4966 | 0.032043 | 121.2845 | -0.29297 | -0.36163 | 0.48981 | 33.1009 | -0.40741 | 121.225 | 121.3623 | -0.24719 | -0.27924 | 0.068664 | 0 | -0.059509 | 7.2876 | 0.39368 | 0.39368 | -0.16022 | 0.11444 | 0.082397 | -0.11902 | 0.85144 | -0.045777 | -0.12817 | 0.018311 | 121.6461 | 121.5454 | 32.8583 | -121.7056 | 121.5866 | 121.7239 | 33.4625 | -121.6232
1992.0312 | 121.7468 | -0.33875 | 121.3257 | 0.0026703 | 0.0132 | 0.079286 | 0.0023156 | 0.070961 | -0.00078613 | 0.0023883 | -0.0054932 | -0.0061929 | 0.063766 | 0.069105 | -0.2034 | -0.0019846 | 121.2845 | 7.1915 | 32.7072 | 0.11902 | 121.2616 | -0.23804 | -0.3067 | 0.60883 | 33.1604 | -0.30212 | 121.1792 | 121.3303 | -0.19226 | -0.24261 | 0.10071 | 0.032043 | -0.064087 | 7.5302 | 0.45776 | 0.42572 | -0.041199 | 0.14648 | 0.09613 | -0.14648 | 0.94757 | 0.036621 | -0.059509 | 0.004577 | 121.6003 | 121.6232 | 33.046 | -121.6324 | 121.5179 | 121.669 | 33.4991 | -121.5683
1993.8125 | 121.669 | -0.36621 | 121.3348 | 0.0026703 | 0.012132 | 0.077577 | 0.00017942 | 0.071388 | 0.0073315 | 0.0032429 | -0.013123 | -0.0021341 | 0.065048 | 0.071241 | -0.20041 | -0.0073252 | 121.2158 | 7.2372 | 32.6752 | 0.068665 | 121.3165 | -0.26093 | -0.3479 | 0.52643 | 33.1055 | -0.45319 | 121.2341 | 121.3577 | -0.22888 | -0.27466 | 0.10529 | 0.018311 | -0.018311 | 7.6035 | 0.43488 | 0.41656 | -0.11902 | 0.13733 | 0.091553 | -0.10071 | 0.89264 | -0.086975 | -0.17853 | 0.022888 | 121.6827 | 121.582 | 33.0414 | -121.6827 | 121.6003 | 121.7239 | 33.4717 | -121.6095
1995.5156 | 121.7194 | -0.3479 | 121.3074 | -0.0049592 | 0.018754 | 0.080354 | 0.0033838 | 0.072884 | 0.0024183 | 0.0053791 | -0.0054932 | -0.0038431 | 0.068466 | 0.0706 | -0.20254 | -0.0047616 | 121.2341 | 7.4295 | 32.7896 | 0.10986 | 121.3028 | -0.27008 | -0.33875 | 0.56763 | 33.0963 | -0.38452 | 121.2204 | 121.3669 | -0.23804 | -0.26093 | 0.077819 | 0.009155 | -0.004578 | 7.7774 | 0.45776 | 0.44861 | -0.073242 | 0.10986 | 0.086975 | -0.086975 | 0.91553 | -0.036621 | -0.1236 | 0.059509 | 121.6507 | 121.582 | 33.1375 | -121.6461 | 121.5683 | 121.7148 | 33.4442 | -121.5683
1997.2812 | 121.7743 | -0.33417 | 121.3028 | -0.0049592 | 0.016404 | 0.080995 | 0.0035974 | 0.072243 | -0.0037769 | 0.0019611 | -0.013123 | -0.0087563 | 0.067184 | 0.067182 | -0.20681 | -0.0030526 | 121.2845 | 7.7316 | 33.0139 | 0.15564 | 121.2479 | -0.23346 | -0.31586 | 0.64087 | 33.2245 | -0.24261 | 121.17 | 121.3165 | -0.20142 | -0.22888 | 0.10071 | 0.01831 | -0.054931 | 8.0658 | 0.48981 | 0.4715 | -0.01831 | 0.13275 | 0.10528 | -0.13275 | 0.97504 | 0.091552 | -0.013733 | 0.013733 | 121.582 | 121.6187 | 33.3481 | -121.6187 | 121.5042 | 121.6507 | 33.5587 | -121.5317
1999.0625 | 121.7468 | -0.33417 | 121.2936 | -0.0049592 | 0.014268 | 0.079714 | 0.00060662 | 0.072029 | 6.8274e-05 | 0.0049519 | -0.0054932 | -0.0070475 | 0.064194 | 0.067396 | -0.20297 | -0.0047616 | 121.2891 | 7.901 | 33.0917 | 0.16937 | 121.2479 | -0.2243 | -0.3067 | 0.65002 | 33.2108 | -0.28839 | 121.1975 | 121.3211 | -0.18768 | -0.2243 | 0.10986 | 0.027465 | -0.045776 | 8.2352 | 0.50354 | 0.47607 | -0.004578 | 0.14648 | 0.10986 | -0.09613 | 0.98419 | 0.045776 | -0.064087 | 0.027466 | 121.582 | 121.6232 | 33.4259 | -121.6003 | 121.5317 | 121.6553 | 33.5449 | -121.5179
2000.8438 | 121.756 | -0.33875 | 121.3531 | -0.0049592 | 0.015122 | 0.082918 | 0.0018884 | 0.073311 | -0.0012133 | 0.0028155 | -0.013123 | -0.0066201 | 0.064835 | 0.066755 | -0.20297 | -0.0041208 | 121.3028 | 8.075 | 33.197 | 0.19226 | 121.2524 | -0.23346 | -0.32044 | 0.6546 | 33.3023 | -0.27924 | 121.1746 | 121.3257 | -0.19226 | -0.2243 | 0.10529 | 0.01831 | -0.10071 | 8.4137 | 0.53101 | 0.5127 | -0.050354 | 0.14648 | 0.11444 | -0.17853 | 0.99335 | 0.059509 | -0.054932 | -0.027465 | 121.5912 | 121.6415 | 33.5358 | -121.6736 | 121.5134 | 121.6644 | 33.6411 | -121.5775
2002.6094 | 121.7789 | -0.35248 | 121.3257 | 0.0026703 | 0.0080727 | 0.083772 | -0.00067498 | 0.073311 | -0.00035893 | 0.0028155 | -0.0054932 | -0.0068337 | 0.06163 | 0.067182 | -0.2034 | -0.002839 | 121.2341 | 8.1711 | 33.2336 | 0.15106 | 121.2662 | -0.24261 | -0.32501 | 0.59509 | 33.1924 | -0.3479 | 121.2112 | 121.3257 | -0.21973 | -0.23804 | 0.10986 | 0.027466 | -0.05951 | 8.5236 | 0.50354 | 0.47607 | -0.091553 | 0.13275 | 0.11444 | -0.11444 | 0.94757 | 0.004578 | -0.10986 | 0 | 121.6187 | 121.5866 | 33.5861 | -121.6507 | 121.5637 | 121.6782 | 33.5449 | -121.5637
2004.375 | 121.6644 | -0.36621 | 121.3303 | -0.0049592 | 0.017045 | 0.081636 | -0.001316 | 0.073738 | 0.0069043 | 0.0038837 | -0.0054932 | -0.0021341 | 0.065262 | 0.06761 | -0.20062 | -0.0060434 | 121.2296 | 8.2581 | 33.2428 | 0.12817 | 121.312 | -0.27466 | -0.36621 | 0.58594 | 33.2291 | -0.46692 | 121.2433 | 121.3486 | -0.24261 | -0.26093 | 0.091553 | 0 | -0.01831 | 8.6243 | 0.49439 | 0.49439 | -0.10071 | 0.1236 | 0.10529 | -0.086975 | 0.95215 | -0.10071 | -0.20599 | 0.018311 | 121.6782 | 121.5958 | 33.609 | -121.6965 | 121.6095 | 121.7148 | 33.5953 | -121.5912
2006.1719 | 121.6644 | -0.37994 | 121.3394 | -0.012589 | 0.0179 | 0.083345 | 0.0018884 | 0.074166 | -0.00099973 | 0.0017475 | 0.0021363 | -0.0036295 | 0.065689 | 0.066114 | -0.20404 | -0.0032662 | 121.2845 | 8.5648 | 33.4991 | 0.23346 | 121.2433 | -0.25177 | -0.31586 | 0.6546 | 33.4213 | -0.32501 | 121.1563 | 121.3531 | -0.21973 | -0.25177 | 0.12817 | 0.064087 | -0.096131 | 8.9447 | 0.6134 | 0.54932 | -0.054932 | 0.16022 | 0.12817 | -0.18311 | 1.0345 | 0.054932 | -0.073242 | 0.013732 | 121.6232 | 121.6644 | 33.8791 | -121.6553 | 121.5363 | 121.7331 | 33.8013 | -121.5912
2007.8906 | 121.7789 | -0.33875 | 121.3211 | -0.012589 | 0.016404 | 0.082063 | -0.00088858 | 0.071175 | 0.0032727 | 0.0055927 | -0.0054932 | -0.0019205 | 0.065262 | 0.070814 | -0.19827 | -0.0043344 | 121.2021 | 8.6243 | 33.4625 | 0.14191 | 121.3211 | -0.26093 | -0.3479 | 0.60883 | 33.3023 | -0.41657 | 121.2479 | 121.3577 | -0.2243 | -0.24261 | 0.07782 | -0.009155 | 0 | 8.963 | 0.48065 | 0.48981 | -0.11902 | 0.11444 | 0.09613 | -0.073242 | 0.94757 | -0.07782 | -0.17395 | 0.036621 | 121.6599 | 121.5408 | 33.8013 | -121.669 | 121.5866 | 121.6965 | 33.6411 | -121.5637
2009.6562 | 121.7651 | -0.34332 | 121.312 | -0.012589 | 0.014695 | 0.085909 | 0.00082022 | 0.071816 | -0.0016405 | 0.0023883 | -0.013123 | -0.0076883 | 0.063553 | 0.066328 | -0.20575 | -0.004548 | 121.3028 | 8.9813 | 33.7189 | 0.25635 | 121.2387 | -0.25635 | -0.32044 | 0.71411 | 33.4351 | -0.25177 | 121.1792 | 121.3303 | -0.20599 | -0.23346 | 0.086975 | 0.022888 | -0.073243 | 9.3246 | 0.59967 | 0.57678 | -0.009156 | 0.13733 | 0.10986 | -0.13275 | 1.0574 | 0.091553 | -0.018311 | 0.01831 | 121.582 | 121.6461 | 34.0622 | -121.6324 | 121.5225 | 121.6736 | 33.7784 | -121.5454
2011.4219 | 121.6644 | -0.38452 | 121.3257 | -0.0049592 | 0.016831 | 0.083345 | 0.003811 | 0.073525 | 0.0034863 | 0.0019611 | -0.013123 | -0.0046975 | 0.065903 | 0.068891 | -0.20489 | -0.0051888 | 121.1975 | 9.0271 | 33.7006 | 0.15564 | 121.2799 | -0.28839 | -0.37079 | 0.59052 | 33.4579 | -0.42114 | 121.2112 | 121.3531 | -0.24261 | -0.28839 | 0.09613 | 0.013732 | -0.045777 | 9.4116 | 0.54016 | 0.52643 | -0.12817 | 0.14191 | 0.09613 | -0.11444 | 0.97504 | -0.036622 | -0.13275 | 0.027465 | 121.6644 | 121.582 | 34.0851 | -121.6965 | 121.5958 | 121.7377 | 33.8425 | -121.6141
2013.2188 | 121.7422 | -0.35248 | 121.2891 | -0.0049592 | 0.014054 | 0.08484 | 0.001034 | 0.073952 | 0.00028207 | 0.0034565 | -0.0054932 | -0.0066201 | 0.062057 | 0.069532 | -0.20382 | -0.0032662 | 121.2799 | 9.3109 | 33.902 | 0.23804 | 121.257 | -0.2655 | -0.32044 | 0.65918 | 33.7051 | -0.32959 | 121.1929 | 121.3348 | -0.20142 | -0.24261 | 0.086975 | 0.032043 | -0.032043 | 9.6634 | 0.59052 | 0.55847 | -0.009155 | 0.15106 | 0.10986 | -0.09613 | 1.0117 | 0.022888 | -0.086975 | 0.045777 | 121.6095 | 121.6324 | 34.2545 | -121.6095 | 121.5454 | 121.6873 | 34.0576 | -121.5317
2014.9219 | 121.7331 | -0.32959 | 121.3165 | -0.012589 | 0.013841 | 0.085481 | 0.0014612 | 0.071175 | -0.00099973 | 0.0043109 | -0.013123 | -0.0046975 | 0.063766 | 0.070814 | -0.20447 | -0.002839 | 121.2341 | 9.4711 | 33.9798 | 0.23804 | 121.2753 | -0.23804 | -0.32044 | 0.67749 | 33.7784 | -0.33875 | 121.1792 | 121.3028 | -0.2243 | -0.26093 | 0.091553 | 0.009155 | -0.041198 | 9.8007 | 0.56763 | 0.55847 | -0.082397 | 0.10529 | 0.068665 | -0.13733 | 1.0071 | -0.009155 | -0.07782 | -0.013733 | 121.6049 | 121.5637 | 34.3094 | -121.637 | 121.5088 | 121.6324 | 34.108 | -121.5775
2016.6875 | 121.788 | -0.32501 | 121.2891 | 0.0103 | 0.01555 | 0.086122 | 0.0014612 | 0.071175 | 0.00028207 | 0.0036701 | -0.013123 | -0.0072611 | 0.065689 | 0.065901 | -0.20447 | -0.0021982 | 121.2296 | 9.6817 | 34.0576 | 0.27008 | 121.2708 | -0.2655 | -0.33417 | 0.70496 | 33.9066 | -0.31128 | 121.17 | 121.3028 | -0.21515 | -0.25177 | 0.059509 | -0.009155 | -0.01831 | 10.0067 | 0.59509 | 0.60425 | -0.059509 | 0.10986 | 0.073242 | -0.11902 | 1.03 | 0.013733 | -0.059509 | 0.013733 | 121.5958 | 121.5546 | 34.3826 | -121.6232 | 121.4951 | 121.6278 | 34.2316 | -121.5408
2018.4531 | 121.6553 | -0.37537 | 121.3074 | -0.0049592 | 0.019395 | 0.0842 | -0.0011024 | 0.074379 | 0.0062635 | 0.0047383 | 0.0021363 | -0.0021341 | 0.066116 | 0.069319 | -0.19998 | -0.004548 | 121.1838 | 9.7595 | 34.0439 | 0.21515 | 121.3074 | -0.28381 | -0.35706 | 0.67291 | 33.8837 | -0.45319 | 121.2204 | 121.3165 | -0.24719 | -0.26093 | 0.091553 | 0.01831 | 0 | 10.1349 | 0.59052 | 0.5722 | -0.1236 | 0.12817 | 0.11444 | -0.086975 | 1.0483 | -0.07782 | -0.19226 | 0.009155 | 121.6827 | 121.5591 | 34.4192 | -121.6644 | 121.5958 | 121.6919 | 34.259 | -121.5683
2020.2344 | 121.6324 | -0.37994 | 121.3074 | -0.0049592 | 0.021745 | 0.085054 | -0.0011024 | 0.074593 | 0.0066907 | 0.0047383 | -0.0054932 | -0.0017069 | 0.067184 | 0.068891 | -0.19806 | -0.0039072 | 121.2341 | 10.0571 | 34.227 | 0.26093 | 121.2753 | -0.2655 | -0.35706 | 0.71869 | 34.0851 | -0.42114 | 121.2158 | 121.3257 | -0.22888 | -0.25635 | 0.11444 | 0.022888 | -0.032043 | 10.437 | 0.64087 | 0.61798 | -0.073242 | 0.15106 | 0.1236 | -0.091553 | 1.0986 | -0.041199 | -0.16479 | 0.018311 | 121.6553 | 121.6141 | 34.6069 | -121.6644 | 121.5958 | 121.7056 | 34.465 | -121.5637
2021.9375 | 121.7194 | -0.33875 | 121.3303 | 0.0026703 | 0.016618 | 0.087404 | 0.0018884 | 0.07502 | -0.00035893 | 0.0051655 | 0.0021363 | -0.0070475 | 0.064621 | 0.066969 | -0.20489 | -0.00070281 | 121.2341 | 10.3409 | 34.4055 | 0.3067 | 121.2204 | -0.25635 | -0.32044 | 0.74158 | 34.4055 | -0.33417 | 121.1746 | 121.2891 | -0.20142 | -0.23346 | 0.082397 | 0.01831 | -0.10986 | 10.6796 | 0.64545 | 0.62714 | -0.09613 | 0.13733 | 0.10529 | -0.15564 | 1.0803 | 0.004578 | -0.10071 | -0.041199 | 121.5591 | 121.5729 | 34.7443 | -121.6507 | 121.5134 | 121.6278 | 34.7443 | -121.5637
2023.7188 | 121.7743 | -0.32501 | 121.3303 | -0.0049592 | 0.018968 | 0.090395 | 0.0025292 | 0.075875 | -0.00057253 | 0.0045245 | -0.013123 | -0.0074747 | 0.067398 | 0.06761 | -0.2066 | -0.0047616 | 121.2708 | 10.5835 | 34.5612 | 0.35706 | 121.2433 | -0.24719 | -0.31128 | 0.76904 | 35.1105 | -0.27008 | 121.1609 | 121.2891 | -0.20142 | -0.23346 | 0.07782 | 0.013733 | -0.086975 | 10.9085 | 0.68207 | 0.66833 | -0.059509 | 0.1236 | 0.091553 | -0.16937 | 1.0941 | 0.054931 | -0.036622 | -0.041199 | 121.5683 | 121.5958 | 34.8862 | -121.6415 | 121.4859 | 121.6141 | 35.4355 | -121.5637
2025.4844 | 121.788 | -0.32501 | 121.2845 | 0.0026703 | 0.020249 | 0.088899 | 0.0029566 | 0.07502 | -0.00078613 | 0.0036701 | -0.0054932 | -0.0079019 | 0.06633 | 0.067823 | -0.20511 | -0.0047616 | 121.2799 | 10.8124 | 34.6619 | 0.38452 | 121.2662 | -0.24261 | -0.32501 | 0.79651 | 35.2432 | -0.25635 | 121.1609 | 121.2936 | -0.19684 | -0.2243 | 0.082397 | 0 | -0.018311 | 11.1374 | 0.70953 | 0.70953 | -0.004578 | 0.12817 | 0.10071 | -0.1236 | 1.1215 | 0.068664 | -0.032044 | 0.009155 | 121.5912 | 121.6049 | 34.9869 | -121.6095 | 121.4859 | 121.6187 | 35.5682 | -121.5088
2027.2812 | 121.7331 | -0.34332 | 121.3074 | -0.012589 | 0.020463 | 0.087831 | -0.001316 | 0.076088 | 0.0058363 | 0.0058063 | 0.0021363 | -0.0025613 | 0.06398 | 0.071241 | -0.2019 | -0.004548 | 121.2067 | 10.8398 | 34.5657 | 0.28381 | 121.2891 | -0.27924 | -0.35248 | 0.70953 | 35.1151 | -0.43488 | 121.2341 | 121.3303 | -0.21973 | -0.27466 | 0.064087 | -0.009155 | -0.018311 | 11.1832 | 0.62714 | 0.63629 | -0.10071 | 0.1236 | 0.068665 | -0.073242 | 1.0529 | -0.091552 | -0.16022 | 0.022888 | 121.6324 | 121.55 | 34.9091 | -121.6599 | 121.5775 | 121.6736 | 35.4584 | -121.582
2028.9844 | 121.7789 | -0.3479 | 121.2799 | -0.020218 | 0.01854 | 0.090181 | 0.0018884 | 0.073738 | 6.8274e-05 | 0.0068745 | -0.0054932 | -0.0055521 | 0.06633 | 0.067396 | -0.20447 | -0.0032662 | 121.2067 | 11.1237 | 34.6939 | 0.33417 | 121.257 | -0.25635 | -0.33417 | 0.75073 | 35.3256 | -0.37994 | 121.1746 | 121.2982 | -0.21515 | -0.2655 | 0.091552 | 0.013733 | -0.022888 | 11.4716 | 0.68207 | 0.66833 | -0.073242 | 0.13275 | 0.082397 | -0.10528 | 1.0986 | -0.032044 | -0.11444 | 0.018311 | 121.6049 | 121.5546 | 35.0418 | -121.6141 | 121.5225 | 121.6461 | 35.6735 | -121.5454
2030.7656 | 121.6415 | -0.40283 | 121.3257 | -0.012589 | 0.02324 | 0.088258 | 0.0014612 | 0.076729 | 0.0022047 | 0.0066609 | -0.020752 | -0.0040567 | 0.066757 | 0.070173 | -0.20425 | -0.0049752 | 121.2021 | 11.3022 | 34.6848 | 0.32959 | 121.2524 | -0.28381 | -0.36163 | 0.71869 | 35.3806 | -0.42572 | 121.2067 | 121.3211 | -0.26093 | -0.27924 | 0.11902 | 0.041199 | -0.073243 | 11.705 | 0.73242 | 0.69122 | -0.1236 | 0.14191 | 0.1236 | -0.11902 | 1.1215 | -0.022888 | -0.14648 | -0.004578 | 121.6553 | 121.6049 | 35.0876 | -121.6873 | 121.6095 | 121.7239 | 35.7834 | -121.6049
2032.4844 | 121.7651 | -0.33875 | 121.2753 | -0.012589 | 0.023027 | 0.089327 | 0.0033838 | 0.077584 | -0.0014269 | 0.0040973 | 0.0021363 | -0.0055521 | 0.063126 | 0.065901 | -0.20404 | -0.0047616 | 121.2891 | 11.5997 | 34.8175 | 0.39825 | 121.2387 | -0.25635 | -0.33417 | 0.83771 | 35.6186 | -0.27008 | 121.138 | 121.2616 | -0.20599 | -0.26093 | 0.082397 | 0.004578 | -0.036622 | 11.9385 | 0.737 | 0.73242 | 0.013732 | 0.13275 | 0.07782 | -0.13733 | 1.1765 | 0.068664 | -0.009156 | -0.013733 | 121.5775 | 121.6278 | 35.1562 | -121.6095 | 121.4767 | 121.6003 | 35.9573 | -121.5363
2034.2656 | 121.6965 | -0.39825 | 121.3165 | -0.012589 | 0.023454 | 0.090395 | -0.00046138 | 0.076943 | 0.0056225 | 0.0058063 | -0.013123 | -0.0010659 | 0.06633 | 0.069746 | -0.2034 | -0.0036936 | 121.1609 | 11.6501 | 34.6848 | 0.31128 | 121.2662 | -0.33417 | -0.3891 | 0.71869 | 35.5408 | -0.45319 | 121.225 | 121.344 | -0.27466 | -0.29755 | 0.064087 | 0.009155 | -0.050354 | 12.0483 | 0.70953 | 0.70038 | -0.15564 | 0.1236 | 0.10071 | -0.091552 | 1.1169 | -0.054932 | -0.15564 | 0.027466 | 121.6644 | 121.5591 | 35.083 | -121.7056 | 121.6232 | 121.7422 | 35.939 | -121.6141
2036.0469 | 121.6324 | -0.43488 | 121.312 | 0.0026703 | 0.026231 | 0.090181 | -0.00067498 | 0.078865 | 0.0094677 | 0.0083697 | -0.0054932 | -0.0012795 | 0.064835 | 0.069319 | -0.20019 | -0.0047616 | 121.225 | 11.911 | 34.7443 | 0.35706 | 121.2524 | -0.31586 | -0.39368 | 0.7782 | 35.7513 | -0.44861 | 121.2112 | 121.3211 | -0.26093 | -0.30212 | 0.11902 | 0.041198 | -0.05951 | 12.3459 | 0.79193 | 0.75073 | -0.086975 | 0.17395 | 0.13275 | -0.10071 | 1.2131 | -0.013733 | -0.14648 | 0.009155 | 121.6873 | 121.6599 | 35.1791 | -121.7056 | 121.6461 | 121.756 | 36.1862 | -121.6141
2037.8281 | 121.7148 | -0.41199 | 121.2433 | -0.020218 | 0.021958 | 0.092317 | 0.003811 | 0.077584 | 0.00028207 | 0.0053791 | 0.0021363 | -0.0091837 | 0.064835 | 0.066328 | -0.20511 | -0.0015572 | 121.2112 | 12.2498 | 34.8267 | 0.40283 | 121.1884 | -0.29297 | -0.35706 | 0.82855 | 35.9756 | -0.34332 | 121.0922 | 121.2479 | -0.24719 | -0.29297 | 0.11902 | 0.054931 | -0.054932 | 12.6617 | 0.81482 | 0.75989 | -0.032043 | 0.16479 | 0.11902 | -0.15106 | 1.2405 | 0.068664 | -0.050354 | 0.004578 | 121.6003 | 121.6232 | 35.2386 | -121.6003 | 121.5042 | 121.6599 | 36.3876 | -121.5363
2039.5312 | 121.7285 | -0.3891 | 121.2753 | -0.0049592 | 0.018113 | 0.093385 | -0.0021704 | 0.076729 | 0.00028207 | 0.0055927 | -0.020752 | -0.0079019 | 0.062698 | 0.06526 | -0.20254 | -0.0021982 | 121.2112 | 12.4374 | 34.8267 | 0.38452 | 121.225 | -0.27008 | -0.32959 | 0.82398 | 36.1313 | -0.36621 | 121.1472 | 121.3074 | -0.21515 | -0.27924 | 0.11902 | 0.059509 | -0.050354 | 12.8265 | 0.77362 | 0.71411 | -0.064087 | 0.17395 | 0.10986 | -0.12817 | 1.2131 | 0.022888 | -0.086975 | 0.032043 | 121.6141 | 121.6003 | 35.2158 | -121.6049 | 121.5363 | 121.6965 | 36.5204 | -121.5546
2041.2969 | 121.7331 | -0.31128 | 121.3028 | -0.0049592 | 0.020249 | 0.094026 | 0.00017942 | 0.076088 | 0.0034863 | 0.0090107 | -0.013123 | -0.0061929 | 0.064194 | 0.064192 | -0.20169 | -0.0021982 | 121.2799 | 12.7487 | 34.8495 | 0.45776 | 121.2387 | -0.21973 | -0.3067 | 0.89722 | 36.3602 | -0.31128 | 121.1929 | 121.2845 | -0.21515 | -0.24261 | 0.091552 | 0.004577 | -0.064087 | 13.06 | 0.76904 | 0.76447 | -0.022888 | 0.09613 | 0.068664 | -0.10986 | 1.2085 | 0 | -0.068664 | -0.01831 | 121.55 | 121.5912 | 35.1608 | -121.6095 | 121.5042 | 121.5958 | 36.6714 | -121.5454
2043.0938 | 121.6507 | -0.37537 | 121.3577 | -0.012589 | 0.025163 | 0.092958 | 0.0046656 | 0.079933 | 0.0058363 | 0.0058063 | 0.0097658 | -0.0019205 | 0.06633 | 0.068037 | -0.20489 | -0.0030526 | 121.2067 | 12.8769 | 34.7305 | 0.41657 | 121.2936 | -0.28839 | -0.36163 | 0.81482 | 36.6119 | -0.41657 | 121.2296 | 121.3623 | -0.24719 | -0.27008 | 0.086975 | 0.013733 | -0.064087 | 13.2523 | 0.79193 | 0.7782 | -0.15106 | 0.12817 | 0.10528 | -0.12817 | 1.1902 | -0.041199 | -0.14648 | 0.004578 | 121.669 | 121.582 | 35.1059 | -121.7194 | 121.6049 | 121.7377 | 36.9873 | -121.6278
2044.8594 | 121.6553 | -0.37537 | 121.3348 | -0.0049592 | 0.026017 | 0.092958 | 0.0014612 | 0.075234 | 0.0079725 | 0.0060199 | -0.013123 | -0.00063872 | 0.064194 | 0.065046 | -0.19977 | -0.0051888 | 121.2708 | 13.1836 | 34.7946 | 0.47607 | 121.257 | -0.27008 | -0.35706 | 0.90179 | 36.5433 | -0.36163 | 121.2021 | 121.3531 | -0.21515 | -0.26093 | 0.10528 | 0.01831 | -0.07782 | 13.559 | 0.85144 | 0.83313 | -0.064087 | 0.16022 | 0.11444 | -0.13275 | 1.2772 | 0.013733 | -0.10071 | 0.01831 | 121.6324 | 121.6461 | 35.17 | -121.6919 | 121.5775 | 121.7285 | 36.9186 | -121.5958
2046.625 | 121.756 | -0.32501 | 121.3074 | -0.0049592 | 0.022172 | 0.095308 | -0.00088858 | 0.078011 | 0.0039135 | 0.0068745 | 0.0021363 | -0.0064065 | 0.06398 | 0.067823 | -0.20062 | -0.0026254 | 121.2891 | 13.5269 | 34.9777 | 0.54016 | 121.2204 | -0.23804 | -0.3067 | 0.95673 | 36.4059 | -0.30212 | 121.1334 | 121.312 | -0.20599 | -0.23804 | 0.086975 | 0.01831 | -0.086975 | 13.8519 | 0.86517 | 0.84686 | -0.018311 | 0.11902 | 0.086975 | -0.17395 | 1.2817 | 0.022888 | -0.064087 | 0.004578 | 121.5454 | 121.6141 | 35.3027 | -121.6141 | 121.4584 | 121.637 | 36.731 | -121.5454
2048.3438 | 121.6507 | -0.38452 | 121.3074 | -0.012589 | 0.027085 | 0.095308 | 0.0053064 | 0.081429 | 0.0011365 | 0.0068745 | 0.0021363 | -0.0042703 | 0.065048 | 0.066542 | -0.20553 | -0.0026254 | 121.2708 | 13.7741 | 35.0372 | 0.56305 | 121.2112 | -0.23804 | -0.32501 | 0.9201 | 35.8521 | -0.32501 | 121.1609 | 121.3303 | -0.21973 | -0.23346 | 0.14648 | 0.059509 | -0.09613 | 14.1586 | 0.94757 | 0.88806 | -0.036621 | 0.16479 | 0.15106 | -0.14648 | 1.3046 | 0.059509 | -0.091553 | 0.022888 | 121.5958 | 121.6553 | 35.4218 | -121.6324 | 121.5454 | 121.7148 | 36.2366 | -121.5408
2050.125 | 121.669 | -0.37994 | 121.312 | -0.0049592 | 0.031358 | 0.094667 | 0.0027428 | 0.077584 | 0.0081861 | 0.0077289 | -0.013123 | -0.0029885 | 0.066544 | 0.069319 | -0.20318 | -0.0054026 | 121.2433 | 13.9709 | 35.0006 | 0.53101 | 121.2524 | -0.29755 | -0.35706 | 0.93842 | 36.232 | -0.3891 | 121.1792 | 121.3394 | -0.25635 | -0.27924 | 0.082398 | 0.022888 | -0.05951 | 14.3509 | 0.91095 | 0.88806 | -0.068665 | 0.1236 | 0.10071 | -0.13275 | 1.3184 | -0.009155 | -0.10986 | 0.027466 | 121.6324 | 121.6232 | 35.3806 | -121.669 | 121.5591 | 121.7194 | 36.6119 | -121.5912
2051.9062 | 121.7468 | -0.37079 | 121.2982 | -0.0049592 | 0.029862 | 0.097658 | -0.0017432 | 0.078865 | 0.0054089 | 0.0094379 | -0.013123 | -0.0042703 | 0.065689 | 0.070387 | -0.2019 | -0.0019846 | 121.1792 | 14.1769 | 35.0235 | 0.50812 | 121.2479 | -0.28381 | -0.35248 | 0.87891 | 36.4197 | -0.44403 | 121.1884 | 121.3348 | -0.2655 | -0.29297 | 0.086976 | 0.018311 | -0.050354 | 14.5477 | 0.87891 | 0.8606 | -0.11902 | 0.10529 | 0.07782 | -0.10986 | 1.2497 | -0.073242 | -0.15106 | 0.036621 | 121.6187 | 121.55 | 35.3943 | -121.6507 | 121.5591 | 121.7056 | 36.7905 | -121.5912
2053.6875 | 121.701 | -0.40283 | 121.2479 | 0.0026703 | 0.028794 | 0.095308 | -3.4178e-05 | 0.080361 | 0.0066907 | 0.0090107 | -0.013123 | -0.0036295 | 0.066116 | 0.069746 | -0.20062 | -0.0039072 | 121.1563 | 14.4287 | 35.1242 | 0.50812 | 121.2524 | -0.31586 | -0.39368 | 0.8606 | 36.5799 | -0.46692 | 121.1975 | 121.2982 | -0.27924 | -0.30212 | 0.086975 | 0.009155 | 0.004577 | 14.8315 | 0.91095 | 0.90179 | -0.091553 | 0.1236 | 0.10071 | -0.050354 | 1.2634 | -0.064087 | -0.16479 | 0.050354 | 121.6553 | 121.5591 | 35.527 | -121.6415 | 121.6003 | 121.7011 | 36.9827 | -121.55
2055.4531 | 121.756 | -0.37537 | 121.2753 | -0.0049592 | 0.027085 | 0.099367 | 0.0029566 | 0.078652 | -0.00099973 | 0.0092243 | -0.0054932 | -0.0068337 | 0.065689 | 0.068037 | -0.20639 | -0.0021982 | 121.2341 | 14.8956 | 35.4813 | 0.63629 | 121.1975 | -0.2655 | -0.35706 | 0.97046 | 36.8958 | -0.31586 | 121.1243 | 121.2753 | -0.24261 | -0.27008 | 0.10986 | 0.01831 | -0.07782 | 15.271 | 1.0117 | 0.99335 | -0.041199 | 0.13275 | 0.10528 | -0.15106 | 1.3458 | 0.059509 | -0.045776 | 0 | 121.5729 | 121.6095 | 35.8566 | -121.6324 | 121.4996 | 121.6507 | 37.2711 | -121.5454
2057.1719 | 121.7651 | -0.37994 | 121.2204 | -0.0049592 | 0.029008 | 0.097658 | 0.00082022 | 0.080361 | 0.0058363 | 0.0094379 | -0.0054932 | -0.0029885 | 0.064835 | 0.068678 | -0.2034 | -0.0064706 | 121.1884 | 15.0604 | 35.6094 | 0.60425 | 121.225 | -0.30212 | -0.38452 | 0.9613 | 36.5936 | -0.37994 | 121.1243 | 121.2662 | -0.25635 | -0.27924 | 0.07782 | -0.004577 | 0.004578 | 15.4404 | 0.98419 | 0.98877 | -0.032044 | 0.1236 | 0.10071 | -0.09613 | 1.3412 | 0 | -0.10071 | 0.045776 | 121.6049 | 121.5683 | 35.9894 | -121.6049 | 121.5042 | 121.6461 | 36.9736 | -121.4996
2058.9375 | 121.6278 | -0.44861 | 121.2845 | -0.012589 | 0.034349 | 0.10043 | -0.0011024 | 0.07972 | 0.0081861 | 0.010933 | -0.0054932 | -0.0023477 | 0.064194 | 0.069959 | -0.2019 | -0.0039072 | 121.1929 | 15.3397 | 35.8109 | 0.60425 | 121.1792 | -0.35248 | -0.42572 | 0.91553 | 36.8546 | -0.44861 | 121.1426 | 121.2982 | -0.28839 | -0.32959 | 0.09613 | 0.022888 | -0.10529 | 15.7883 | 1.0529 | 1.03 | -0.091553 | 0.16022 | 0.11902 | -0.14191 | 1.3641 | 0 | -0.11902 | 0.013733 | 121.6278 | 121.6415 | 36.2595 | -121.7102 | 121.5912 | 121.7468 | 37.3032 | -121.6141
2060.6406 | 121.6736 | -0.4715 | 121.2479 | -0.0049592 | 0.037553 | 0.10108 | 0.0031702 | 0.08207 | 0.0066907 | 0.012215 | 0.0021363 | -0.0023477 | 0.066544 | 0.067182 | -0.20212 | -0.0043344 | 121.0693 | 15.4999 | 35.9894 | 0.57678 | 121.1975 | -0.36621 | -0.43945 | 0.8606 | 36.9186 | -0.53101 | 121.1105 | 121.2799 | -0.32044 | -0.35706 | 0.10529 | 0.032044 | -0.050354 | 15.9714 | 1.0483 | 1.0162 | -0.17853 | 0.15106 | 0.11444 | -0.13733 | 1.3321 | -0.059509 | -0.17395 | 0.032043 | 121.669 | 121.5408 | 36.4609 | -121.6873 | 121.582 | 121.7514 | 37.3901 | -121.6049
2062.4062 | 121.6324 | -0.4715 | 121.2296 | -0.012589 | 0.035417 | 0.10129 | 0.0012476 | 0.07972 | 0.0083997 | 0.011574 | -0.0054932 | 2.078e-06 | 0.067398 | 0.071455 | -0.20062 | -0.0030526 | 121.0876 | 15.8569 | 36.3281 | 0.61798 | 121.1517 | -0.36621 | -0.45776 | 0.86517 | 37.1567 | -0.54016 | 121.106 | 121.2662 | -0.32501 | -0.36163 | 0.10529 | 0.013733 | -0.07782 | 16.3284 | 1.0895 | 1.0757 | -0.14191 | 0.14648 | 0.10986 | -0.1236 | 1.3367 | -0.068664 | -0.17853 | 0.036621 | 121.6232 | 121.5591 | 36.7996 | -121.6873 | 121.5775 | 121.7377 | 37.6282 | -121.5912
2064.125 | 121.7697 | -0.42572 | 121.1838 | -0.0049592 | 0.032426 | 0.1015 | 0.001034 | 0.081429 | 0.0028455 | 0.012429 | -0.013123 | -0.0042703 | 0.066116 | 0.069959 | -0.20297 | -0.0013436 | 121.1563 | 16.2643 | 36.7493 | 0.72327 | 121.1609 | -0.32501 | -0.39825 | 1.0117 | 37.3352 | -0.39368 | 121.0739 | 121.2387 | -0.29297 | -0.30212 | 0.10071 | 0.027466 | -0.022888 | 16.6901 | 1.149 | 1.1215 | -0.027466 | 0.13275 | 0.1236 | -0.10986 | 1.4374 | 0.032043 | -0.091553 | 0.054931 | 121.5866 | 121.582 | 37.175 | -121.582 | 121.4996 | 121.6644 | 37.7609 | -121.4859
2065.9062 | 121.7468 | -0.4303 | 121.1975 | -0.0049592 | 0.033067 | 0.10236 | 0.0031702 | 0.08207 | -0.00099973 | 0.0087971 | -0.0054932 | -0.0083291 | 0.06633 | 0.06825 | -0.20575 | -0.0030526 | 121.0922 | 16.5527 | 37.0377 | 0.72784 | 121.1288 | -0.32044 | -0.41199 | 0.94757 | 37.381 | -0.43488 | 121.0739 | 121.2433 | -0.29755 | -0.30212 | 0.10986 | 0.018311 | -0.068665 | 16.983 | 1.1581 | 1.1398 | -0.10529 | 0.13275 | 0.12817 | -0.1236 | 1.3779 | -0.004577 | -0.13275 | 0.045776 | 121.5591 | 121.5225 | 37.468 | -121.6095 | 121.5042 | 121.6736 | 37.8113 | -121.4996
2067.6875 | 121.6599 | -0.4303 | 121.2112 | -0.012589 | 0.042039 | 0.10449 | 0.00039302 | 0.081002 | 0.010536 | 0.01072 | -0.0054932 | -0.00063872 | 0.067398 | 0.06825 | -0.2019 | -0.004548 | 121.1426 | 16.8365 | 37.3215 | 0.75989 | 121.1746 | -0.36163 | -0.4303 | 0.99792 | 37.5641 | -0.46234 | 121.0968 | 121.2524 | -0.3067 | -0.35706 | 0.068665 | 0 | -0.036621 | 17.2668 | 1.1902 | 1.1902 | -0.068665 | 0.1236 | 0.073242 | -0.11444 | 1.4282 | -0.032043 | -0.10529 | 0.041198 | 121.6049 | 121.5729 | 37.7518 | -121.6415 | 121.5271 | 121.6827 | 37.9944 | -121.5683
2069.4531 | 121.7468 | -0.4303 | 121.1792 | -0.012589 | 0.031785 | 0.10941 | 0.00082022 | 0.081642 | 0.00092287 | 0.010079 | -0.0054932 | -0.0079019 | 0.063766 | 0.067182 | -0.2019 | -0.0032662 | 121.0876 | 17.157 | 37.6694 | 0.78278 | 121.1288 | -0.33417 | -0.42114 | 0.97961 | 37.7014 | -0.4303 | 121.0648 | 121.2479 | -0.29755 | -0.32501 | 0.096131 | 0.009155 | -0.050354 | 17.5873 | 1.2131 | 1.2039 | -0.091553 | 0.13275 | 0.10529 | -0.11444 | 1.4099 | 0 | -0.10529 | 0.068665 | 121.5591 | 121.5179 | 38.0997 | -121.6003 | 121.4951 | 121.6782 | 38.1317 | -121.5042
2071.2344 | 121.7697 | -0.43488 | 121.1746 | -0.020218 | 0.032853 | 0.10727 | 0.0018884 | 0.080574 | 0.0024183 | 0.010292 | -0.013123 | -0.0079019 | 0.064194 | 0.069105 | -0.20596 | -0.00091641 | 121.0876 | 17.4637 | 37.9623 | 0.80109 | 121.1563 | -0.33417 | -0.42114 | 1.0025 | 37.7747 | -0.41657 | 121.0693 | 121.1884 | -0.31586 | -0.33875 | 0.10071 | 0.013732 | -0.018311 | 17.8986 | 1.236 | 1.2222 | -0.086976 | 0.11902 | 0.09613 | -0.10529 | 1.4374 | 0.01831 | -0.07782 | 0.013732 | 121.5912 | 121.5225 | 38.3972 | -121.5958 | 121.5042 | 121.6232 | 38.2095 | -121.5134
2072.9375 | 121.6827 | -0.46692 | 121.2021 | 0.0026703 | 0.041184 | 0.10706 | 0.00017942 | 0.083565 | 0.010322 | 0.010292 | -0.013123 | -0.0042703 | 0.06633 | 0.070387 | -0.20019 | -0.0075388 | 121.1426 | 17.688 | 38.1958 | 0.8194 | 121.1746 | -0.37537 | -0.44861 | 1.0162 | 37.9395 | -0.48065 | 121.0831 | 121.2433 | -0.32959 | -0.36621 | 0.091553 | 0.018311 | -0.027465 | 18.1549 | 1.2863 | 1.268 | -0.059509 | 0.13733 | 0.10071 | -0.11902 | 1.4832 | -0.013733 | -0.11444 | 0.041199 | 121.6415 | 121.6095 | 38.6627 | -121.6507 | 121.55 | 121.7102 | 38.4064 | -121.5683
2074.7188 | 121.6324 | -0.46692 | 121.2296 | -0.0049592 | 0.04033 | 0.10983 | -0.001316 | 0.08207 | 0.01139 | 0.012856 | -0.013123 | -0.0023477 | 0.06398 | 0.068037 | -0.19848 | -0.0049752 | 121.1426 | 17.9764 | 38.324 | 0.8194 | 121.1563 | -0.36621 | -0.43945 | 1.0529 | 37.944 | -0.49896 | 121.0922 | 121.225 | -0.33417 | -0.3479 | 0.10071 | 0.027466 | -0.073242 | 18.4433 | 1.2863 | 1.2589 | -0.086975 | 0.13275 | 0.11902 | -0.13733 | 1.5198 | -0.032043 | -0.15106 | -0.004577 | 121.6232 | 121.6095 | 38.7909 | -121.669 | 121.5591 | 121.6919 | 38.4109 | -121.5775
2076.4844 | 121.7972 | -0.43488 | 121.1929 | -0.0049592 | 0.037553 | 0.11261 | 0.001034 | 0.083138 | 0.0013501 | 0.010506 | 0.0021363 | -0.0096109 | 0.066757 | 0.065687 | -0.20447 | -0.00091641 | 121.1014 | 18.1732 | 38.3331 | 0.86517 | 121.1426 | -0.35248 | -0.44861 | 1.062 | 38.1638 | -0.3891 | 121.0281 | 121.2112 | -0.3067 | -0.33875 | 0.082397 | -0.013733 | -0.050354 | 18.6081 | 1.3 | 1.3138 | -0.091553 | 0.12817 | 0.09613 | -0.16479 | 1.4969 | 0.045776 | -0.050354 | 0.018311 | 121.5775 | 121.5363 | 38.768 | -121.6415 | 121.463 | 121.6461 | 38.5986 | -121.5317
2078.2812 | 121.6782 | -0.4715 | 121.2296 | 0.0026703 | 0.040971 | 0.11069 | 0.0023156 | 0.082497 | 0.0081861 | 0.010933 | 0.0021363 | -0.0029885 | 0.067398 | 0.069105 | -0.20553 | -0.0034798 | 121.0739 | 18.2465 | 38.1088 | 0.82855 | 121.1655 | -0.38452 | -0.47607 | 0.98419 | 38.0859 | -0.52643 | 121.1105 | 121.2387 | -0.3479 | -0.36163 | 0.086976 | -0.004577 | -0.064087 | 18.718 | 1.3 | 1.3046 | -0.15564 | 0.1236 | 0.10986 | -0.11902 | 1.4557 | -0.054931 | -0.1648 | 0.009155 | 121.637 | 121.5454 | 38.5803 | -121.7056 | 121.582 | 121.7102 | 38.5574 | -121.5912
2079.9844 | 121.7148 | -0.43488 | 121.2021 | 0.0026703 | 0.039689 | 0.11389 | 0.0035974 | 0.082497 | 0.0026319 | 0.012642 | 0.0021363 | -0.0070475 | 0.064621 | 0.067182 | -0.20596 | -0.0056162 | 121.1609 | 18.6127 | 38.15 | 0.95215 | 121.1151 | -0.32959 | -0.41199 | 1.1169 | 38.2919 | -0.37079 | 121.051 | 121.2387 | -0.28381 | -0.31128 | 0.10529 | 0.022888 | -0.086975 | 19.0475 | 1.387 | 1.3641 | -0.041198 | 0.15106 | 0.1236 | -0.15106 | 1.5518 | 0.064086 | -0.05951 | 0.036621 | 121.55 | 121.5958 | 38.5849 | -121.6141 | 121.4859 | 121.6736 | 38.7268 | -121.5134
2081.7656 | 121.6919 | -0.45776 | 121.2158 | -0.0049592 | 0.041612 | 0.11347 | -3.4178e-05 | 0.082711 | 0.0081861 | 0.012429 | -0.0054932 | -0.0021341 | 0.065475 | 0.069105 | -0.20126 | -0.0032662 | 121.0831 | 18.6401 | 38.118 | 0.87433 | 121.1609 | -0.38452 | -0.44403 | 1.0483 | 38.1042 | -0.5127 | 121.1197 | 121.2479 | -0.34332 | -0.36621 | 0.073243 | 0.013733 | -0.054931 | 19.0979 | 1.3321 | 1.3184 | -0.13275 | 0.11444 | 0.091553 | -0.09613 | 1.506 | -0.054931 | -0.14648 | 0.032044 | 121.6187 | 121.5408 | 38.5757 | -121.6599 | 121.5775 | 121.7056 | 38.562 | -121.582
2083.5469 | 121.7239 | -0.43488 | 121.1746 | -0.0049592 | 0.046952 | 0.11176 | 0.0025292 | 0.084206 | 0.011818 | 0.012856 | -0.020752 | -0.0044839 | 0.068466 | 0.072096 | -0.20382 | -0.0041208 | 121.0785 | 18.8873 | 38.0585 | 0.88806 | 121.17 | -0.37079 | -0.45319 | 1.062 | 37.9807 | -0.52185 | 121.1197 | 121.2387 | -0.33417 | -0.34332 | 0.064086 | -0.018311 | -0.004578 | 19.3222 | 1.3229 | 1.3412 | -0.096131 | 0.10071 | 0.091552 | -0.054932 | 1.4969 | -0.086976 | -0.17853 | 0.064086 | 121.6049 | 121.5134 | 38.4933 | -121.6278 | 121.5546 | 121.6736 | 38.4155 | -121.5179
2085.25 | 121.6553 | -0.46234 | 121.1792 | -0.0049592 | 0.041825 | 0.11475 | 0.00039302 | 0.082924 | 0.011818 | 0.014138 | -0.0054932 | -0.0034159 | 0.067612 | 0.071668 | -0.19955 | -0.0015572 | 121.0373 | 19.075 | 38.0539 | 0.9201 | 121.1655 | -0.37994 | -0.46234 | 1.0757 | 37.8937 | -0.54474 | 121.106 | 121.2387 | -0.33417 | -0.3891 | 0.082397 | 0 | -0.013733 | 19.5374 | 1.3824 | 1.3824 | -0.14191 | 0.12817 | 0.073242 | -0.073242 | 1.5381 | -0.082398 | -0.15564 | 0.059509 | 121.6278 | 121.4996 | 38.5162 | -121.6415 | 121.5683 | 121.701 | 38.356 | -121.5683
2087.0312 | 121.7422 | -0.4303 | 121.1517 | -0.012589 | 0.039048 | 0.11325 | 0.0012476 | 0.085701 | 0.0086133 | 0.012856 | -0.0054932 | -0.0051247 | 0.064194 | 0.068037 | -0.2019 | -0.0041208 | 121.138 | 19.4321 | 38.1821 | 1.0208 | 121.1105 | -0.34332 | -0.42114 | 1.1856 | 38.0997 | -0.41657 | 120.9915 | 121.1838 | -0.31586 | -0.34332 | 0.086975 | 0.009155 | -0.041198 | 19.8624 | 1.4511 | 1.442 | -0.013733 | 0.11444 | 0.086975 | -0.16022 | 1.6159 | 0.013733 | -0.073242 | 0.032044 | 121.5408 | 121.5683 | 38.6124 | -121.5729 | 121.4218 | 121.6141 | 38.53 | -121.4951
2088.7969 | 121.7422 | -0.43488 | 121.17 | -0.0049592 | 0.040116 | 0.11987 | 0.0029566 | 0.083565 | 0.0034863 | 0.010933 | -0.0054932 | -0.0098245 | 0.065262 | 0.067396 | -0.20532 | -0.0024118 | 121.1288 | 19.7021 | 38.2462 | 1.0437 | 121.1151 | -0.36621 | -0.4303 | 1.2268 | 38.2233 | -0.39368 | 121.0236 | 121.1884 | -0.32501 | -0.35706 | 0.068664 | 0.004577 | -0.054932 | 20.137 | 1.4786 | 1.474 | -0.041199 | 0.10986 | 0.077819 | -0.14648 | 1.6617 | 0.041198 | -0.036621 | 0.01831 | 121.55 | 121.5637 | 38.681 | -121.6003 | 121.4584 | 121.6232 | 38.6581 | -121.5271
2090.5 | 121.756 | -0.45776 | 121.1884 | -0.012589 | 0.040971 | 0.11667 | -0.00046138 | 0.083992 | 0.0088269 | 0.014565 | -0.0054932 | -0.0034159 | 0.06398 | 0.067182 | -0.19977 | -0.0030526 | 121.0464 | 19.7708 | 38.2416 | 0.98419 | 121.1197 | -0.38452 | -0.47607 | 1.1261 | 38.1683 | -0.52185 | 121.051 | 121.1975 | -0.3479 | -0.38452 | 0.073243 | -0.01831 | -0.068664 | 20.2286 | 1.442 | 1.4603 | -0.14191 | 0.10986 | 0.073243 | -0.13733 | 1.5839 | -0.064087 | -0.13733 | 0.009156 | 121.5775 | 121.5042 | 38.6993 | -121.6644 | 121.5088 | 121.6553 | 38.6261 | -121.5729
2092.2812 | 121.7606 | -0.42572 | 121.17 | 0.0026703 | 0.040971 | 0.11817 | 0.0035974 | 0.085488 | 0.0024183 | 0.010933 | 0.0021363 | -0.0089701 | 0.066971 | 0.068037 | -0.20489 | -0.004548 | 121.1243 | 20.0684 | 38.7222 | 1.0986 | 121.1105 | -0.33875 | -0.40283 | 1.2634 | 38.736 | -0.36163 | 121.0602 | 121.1655 | -0.29755 | -0.34332 | 0.086975 | 0.022888 | -0.059509 | 20.4941 | 1.5244 | 1.5015 | -0.045776 | 0.12817 | 0.082397 | -0.10986 | 1.6891 | 0.064087 | -0.01831 | -0.004578 | 121.5363 | 121.55 | 39.1479 | -121.5729 | 121.4859 | 121.5912 | 39.1617 | -121.5134
2094.0625 | 121.6415 | -0.46234 | 121.1929 | -0.0049592 | 0.045671 | 0.11902 | -0.00088858 | 0.085488 | 0.01374 | 0.014565 | 0.0021363 | -0.0017069 | 0.065262 | 0.069746 | -0.19977 | -0.0043344 | 121.1105 | 20.2606 | 38.6673 | 1.0757 | 121.1426 | -0.36621 | -0.44861 | 1.2451 | 38.7085 | -0.48065 | 121.0785 | 121.225 | -0.32501 | -0.36621 | 0.09613 | 0.013733 | -0.050354 | 20.723 | 1.5381 | 1.5244 | -0.082397 | 0.13733 | 0.09613 | -0.11444 | 1.7075 | -0.018311 | -0.11444 | 0.032044 | 121.6049 | 121.5729 | 39.1296 | -121.6415 | 121.5408 | 121.6873 | 39.1708 | -121.5591
2095.8438 | 121.7056 | -0.45319 | 121.1563 | -0.012589 | 0.04268 | 0.1203 | -0.0036658 | 0.083992 | 0.0064771 | 0.014778 | 0.0021363 | -0.0074747 | 0.060776 | 0.068037 | -0.2034 | -0.0024118 | 121.1334 | 20.5627 | 38.6902 | 1.1536 | 121.1151 | -0.35248 | -0.42114 | 1.2955 | 38.9191 | -0.41199 | 121.0373 | 121.1838 | -0.31586 | -0.33875 | 0.10071 | 0.032043 | -0.041199 | 21.0159 | 1.6067 | 1.5747 | -0.022888 | 0.13733 | 0.11444 | -0.11902 | 1.7487 | 0.041199 | -0.073242 | 0.027466 | 121.5683 | 121.5866 | 39.1434 | -121.5775 | 121.4905 | 121.637 | 39.3723 | -121.4951
2097.5469 | 121.6324 | -0.50354 | 121.2021 | -0.012589 | 0.042253 | 0.12094 | 0.0025292 | 0.086769 | 0.0075451 | 0.014351 | -0.0054932 | -0.0053385 | 0.065903 | 0.066542 | -0.20254 | -0.0039072 | 121.1014 | 20.7916 | 38.6719 | 1.1536 | 121.0922 | -0.37079 | -0.43945 | 1.2405 | 39.0244 | -0.48065 | 121.0464 | 121.2067 | -0.32959 | -0.38452 | 0.13275 | 0.064087 | -0.10986 | 21.2952 | 1.6571 | 1.593 | -0.10071 | 0.17395 | 0.11902 | -0.15564 | 1.7441 | 0.022888 | -0.096131 | 0.004578 | 121.5958 | 121.6049 | 39.1754 | -121.6415 | 121.55 | 121.7102 | 39.5279 | -121.5866
2099.3281 | 121.6141 | -0.50812 | 121.1929 | -0.020218 | 0.04738 | 0.12116 | 0.0059472 | 0.089974 | 0.0079725 | 0.014138 | 0.0021363 | -0.0066201 | 0.066544 | 0.068678 | -0.20553 | -0.0047616 | 121.0922 | 20.9885 | 38.6673 | 1.1581 | 121.1151 | -0.37994 | -0.43488 | 1.2451 | 39.1296 | -0.48065 | 121.0373 | 121.1884 | -0.33417 | -0.39368 | 0.12817 | 0.073243 | -0.07782 | 21.4966 | 1.6663 | 1.593 | -0.10071 | 0.17395 | 0.11444 | -0.15564 | 1.7532 | 0.027466 | -0.086975 | -0.004578 | 121.6232 | 121.6003 | 39.1754 | -121.6278 | 121.5454 | 121.6965 | 39.6378 | -121.5866
2101.1094 | 121.6461 | -0.48523 | 121.1929 | 0.0026703 | 0.049943 | 0.12158 | 0.0014612 | 0.087624 | 0.015663 | 0.01606 | -0.013123 | -0.0023477 | 0.065903 | 0.067823 | -0.20041 | -0.0039072 | 121.0968 | 21.1258 | 38.6627 | 1.1765 | 121.1243 | -0.39368 | -0.45319 | 1.3138 | 39.3036 | -0.48523 | 121.0648 | 121.1929 | -0.35706 | -0.39368 | 0.091552 | 0.032043 | -0.068664 | 21.611 | 1.6617 | 1.6296 | -0.09613 | 0.12817 | 0.091552 | -0.12817 | 1.799 | 0 | -0.091552 | 0 | 121.6095 | 121.582 | 39.1479 | -121.6461 | 121.55 | 121.6782 | 39.7888 | -121.5866
2102.8906 | 121.6003 | -0.53558 | 121.1792 | -0.012589 | 0.052079 | 0.11881 | 0.00017942 | 0.086769 | 0.013527 | 0.017342 | -0.013123 | -0.0036295 | 0.065048 | 0.069532 | -0.20041 | -0.0047616 | 121.0739 | 21.2906 | 38.7268 | 1.2085 | 121.1243 | -0.40741 | -0.48065 | 1.2955 | 39.4638 | -0.54932 | 121.051 | 121.2158 | -0.36163 | -0.39368 | 0.12817 | 0.054931 | -0.054931 | 21.8262 | 1.7441 | 1.6891 | -0.10528 | 0.17395 | 0.14191 | -0.12817 | 1.8311 | -0.013733 | -0.15564 | 0.036621 | 121.6599 | 121.6095 | 39.2624 | -121.6599 | 121.5866 | 121.7514 | 39.9994 | -121.5729
2104.5938 | 121.637 | -0.50354 | 121.1563 | -0.012589 | 0.051866 | 0.12393 | 0.0025292 | 0.090187 | 0.0064771 | 0.015419 | -0.0054932 | -0.0061929 | 0.065689 | 0.069105 | -0.20553 | -0.0015572 | 121.019 | 21.4691 | 38.7543 | 1.2085 | 121.0876 | -0.41657 | -0.48523 | 1.2497 | 39.6973 | -0.54932 | 121.0648 | 121.2067 | -0.37537 | -0.40741 | 0.086975 | 0.018311 | -0.068665 | 21.9727 | 1.712 | 1.6937 | -0.13733 | 0.12817 | 0.09613 | -0.091553 | 1.7532 | -0.045776 | -0.14191 | 0.050354 | 121.5912 | 121.5225 | 39.2578 | -121.6415 | 121.5683 | 121.7102 | 40.2008 | -121.5637
2106.3125 | 121.7194 | -0.48065 | 121.1563 | -0.0049592 | 0.051866 | 0.12415 | -0.00067498 | 0.08741 | 0.010536 | 0.016274 | -0.013123 | -0.0040567 | 0.067184 | 0.071028 | -0.20297 | -0.0021982 | 121.0098 | 21.7209 | 38.9236 | 1.2589 | 121.1197 | -0.39825 | -0.50812 | 1.2817 | 39.83 | -0.56305 | 121.0464 | 121.2158 | -0.36621 | -0.39825 | 0.082398 | -0.027466 | -0.036621 | 22.2015 | 1.7395 | 1.767 | -0.14648 | 0.11444 | 0.082398 | -0.10986 | 1.7624 | -0.082397 | -0.1648 | 0.059509 | 121.6003 | 121.4905 | 39.4043 | -121.6644 | 121.5271 | 121.6965 | 40.3107 | -121.5546
2108.0938 | 121.6644 | -0.46692 | 121.2158 | -0.0049592 | 0.057847 | 0.12522 | 0.0057336 | 0.089333 | 0.011818 | 0.016487 | -0.0054932 | -0.0027749 | 0.068893 | 0.071028 | -0.20404 | -0.0021982 | 121.0236 | 21.9864 | 39.0884 | 1.3458 | 121.1197 | -0.36621 | -0.46692 | 1.355 | 40.1871 | -0.53101 | 121.0922 | 121.2204 | -0.35706 | -0.38452 | 0.10071 | 0 | -0.09613 | 22.4533 | 1.8127 | 1.8127 | -0.19226 | 0.10986 | 0.082398 | -0.1236 | 1.8219 | -0.064087 | -0.14648 | 0.004578 | 121.5866 | 121.4905 | 39.5554 | -121.6827 | 121.5591 | 121.6873 | 40.654 | -121.6003
2109.875 | 121.7514 | -0.4715 | 121.138 | -0.012589 | 0.049516 | 0.12885 | 0.0025292 | 0.08976 | 0.0045545 | 0.015206 | -0.013123 | -0.0074747 | 0.063126 | 0.068891 | -0.20468 | -0.00091641 | 121.0419 | 22.1008 | 39.006 | 1.3779 | 121.0739 | -0.3891 | -0.45776 | 1.4053 | 40.4572 | -0.44403 | 120.9915 | 121.1472 | -0.33417 | -0.39368 | 0.082398 | 0.013733 | -0.064086 | 22.5723 | 1.8494 | 1.8356 | -0.09613 | 0.13733 | 0.07782 | -0.14648 | 1.8768 | 0.027466 | -0.050354 | 0.009156 | 121.5454 | 121.5134 | 39.4775 | -121.5958 | 121.463 | 121.6187 | 40.9286 | -121.5317
2111.5781 | 121.7377 | -0.49439 | 121.1243 | -0.012589 | 0.051652 | 0.12906 | 0.001034 | 0.090615 | 0.0066907 | 0.016915 | -0.013123 | -0.0087563 | 0.06398 | 0.066755 | -0.20361 | -0.0030526 | 121.0373 | 22.1695 | 39.0152 | 1.387 | 121.051 | -0.3891 | -0.43945 | 1.4099 | 40.7135 | -0.48981 | 121.0052 | 121.1426 | -0.36163 | -0.37537 | 0.10529 | 0.054932 | -0.073243 | 22.6639 | 1.8814 | 1.8265 | -0.086976 | 0.13275 | 0.11902 | -0.11902 | 1.9043 | 0.004578 | -0.11444 | 0.01831 | 121.5454 | 121.5317 | 39.5096 | -121.5637 | 121.4996 | 121.637 | 41.2079 | -121.4996
2113.3594 | 121.701 | -0.49439 | 121.1334 | 0.0026703 | 0.050797 | 0.13141 | 0.0029566 | 0.087837 | 0.0088269 | 0.014778 | 0.0097658 | -0.0064065 | 0.066544 | 0.068678 | -0.20233 | -0.0039072 | 121.0464 | 22.3755 | 39.1754 | 1.4145 | 121.0693 | -0.38452 | -0.45776 | 1.4557 | 41.1804 | -0.48981 | 121.0007 | 121.1288 | -0.36621 | -0.39825 | 0.10986 | 0.036621 | -0.064087 | 22.8699 | 1.9089 | 1.8723 | -0.086975 | 0.12817 | 0.096131 | -0.13275 | 1.9501 | 0.004578 | -0.091553 | -0.004578 | 121.5637 | 121.5408 | 39.6698 | -121.5912 | 121.4951 | 121.6232 | 41.6748 | -121.5317
2115.125 | 121.7468 | -0.48065 | 121.1014 | -0.0049592 | 0.054215 | 0.12927 | -0.00024778 | 0.092751 | 0.014167 | 0.020119 | -0.013123 | -0.0036295 | 0.065903 | 0.069105 | -0.20212 | -0.0056162 | 121.0831 | 22.6364 | 39.1205 | 1.4786 | 121.0419 | -0.3891 | -0.48065 | 1.5472 | 41.5466 | -0.4715 | 121.0007 | 121.1151 | -0.36163 | -0.39825 | 0.091553 | 0 | -0.059509 | 23.1171 | 1.9592 | 1.9592 | -0.01831 | 0.11902 | 0.082398 | -0.10071 | 2.0279 | 0.009155 | -0.073243 | 0.013733 | 121.5225 | 121.5637 | 39.6011 | -121.582 | 121.4813 | 121.5958 | 42.0273 | -121.4996
2116.8906 | 121.6141 | -0.53101 | 121.1197 | -0.012589 | 0.058702 | 0.12949 | -0.00046138 | 0.091683 | 0.016731 | 0.019692 | -0.0054932 | -0.0025613 | 0.065262 | 0.070173 | -0.19998 | -0.0064706 | 120.9961 | 22.7554 | 39.0381 | 1.442 | 121.0922 | -0.44403 | -0.50354 | 1.4603 | 41.6748 | -0.62256 | 121.0052 | 121.1426 | -0.39368 | -0.43945 | 0.086975 | 0.027466 | -0.027466 | 23.2864 | 1.973 | 1.9455 | -0.1236 | 0.13733 | 0.091553 | -0.11444 | 1.9913 | -0.091553 | -0.18311 | 0.022888 | 121.6232 | 121.5271 | 39.5691 | -121.6232 | 121.5363 | 121.6736 | 42.2058 | -121.5591
2118.6562 | 121.701 | -0.53101 | 121.0922 | -0.020218 | 0.059342 | 0.13269 | 0.0029566 | 0.091042 | 0.0069043 | 0.016701 | 0.0021363 | -0.0074747 | 0.06398 | 0.064405 | -0.20447 | -0.0034798 | 121.0556 | 23.2178 | 39.2075 | 1.5793 | 121.0007 | -0.43488 | -0.48523 | 1.561 | 42.0364 | -0.4715 | 120.9183 | 121.1014 | -0.38452 | -0.4303 | 0.096131 | 0.045777 | -0.091553 | 23.7488 | 2.1103 | 2.0645 | -0.036621 | 0.14648 | 0.10071 | -0.17395 | 2.092 | 0.059509 | -0.041199 | 0.009155 | 121.5317 | 121.5866 | 39.7385 | -121.5775 | 121.4493 | 121.6324 | 42.5674 | -121.5225
2120.4219 | 121.6919 | -0.54474 | 121.0739 | -0.012589 | 0.061051 | 0.13184 | 0.00082022 | 0.091896 | 0.016731 | 0.019478 | -0.0054932 | -0.0023477 | 0.065048 | 0.070173 | -0.19977 | -0.0039072 | 120.9595 | 23.2956 | 39.1251 | 1.5564 | 121.0602 | -0.46234 | -0.55389 | 1.4969 | 41.954 | -0.60883 | 120.9915 | 121.1197 | -0.42114 | -0.43945 | 0.082398 | -0.009155 | -0.013733 | 23.8403 | 2.1011 | 2.1103 | -0.11444 | 0.1236 | 0.10529 | -0.082398 | 2.0416 | -0.064087 | -0.16937 | 0.045776 | 121.6049 | 121.5042 | 39.6698 | -121.6278 | 121.5363 | 121.6644 | 42.4988 | -121.5134
2122.125 | 121.6827 | -0.50812 | 121.0922 | -0.0049592 | 0.061265 | 0.13333 | 0.001034 | 0.091469 | 0.016517 | 0.020973 | -0.013123 | -0.0023477 | 0.064621 | 0.069105 | -0.2019 | -0.0041208 | 120.9824 | 23.5336 | 39.2349 | 1.6205 | 121.0602 | -0.43945 | -0.50812 | 1.5564 | 42.2928 | -0.59967 | 120.9915 | 121.1609 | -0.40741 | -0.44403 | 0.068665 | 0 | -0.032043 | 24.0417 | 2.1286 | 2.1286 | -0.10986 | 0.10071 | 0.064087 | -0.10071 | 2.0645 | -0.091552 | -0.15564 | 0.068665 | 121.5683 | 121.4905 | 39.743 | -121.6003 | 121.4996 | 121.669 | 42.8009 | -121.5363
2123.8906 | 121.7331 | -0.4715 | 121.0968 | -0.012589 | 0.062333 | 0.1344 | -0.00088858 | 0.093392 | 0.015663 | 0.021614 | -0.0054932 | -0.0046975 | 0.066116 | 0.0706 | -0.20382 | -0.0036936 | 121.0144 | 23.8449 | 39.6652 | 1.7349 | 121.051 | -0.41657 | -0.48523 | 1.6983 | 42.7826 | -0.48523 | 120.9595 | 121.1288 | -0.37537 | -0.37994 | 0.054932 | -0.013732 | -0.045777 | 24.3164 | 2.2064 | 2.2202 | -0.082398 | 0.096131 | 0.091553 | -0.13733 | 2.1698 | -0.013732 | -0.10529 | 0.032043 | 121.5225 | 121.4859 | 40.1367 | -121.582 | 121.431 | 121.6003 | 43.2541 | -121.4767
2125.6562 | 121.6324 | -0.50812 | 121.1243 | 0.0026703 | 0.060838 | 0.13269 | 0.0025292 | 0.092537 | 0.016945 | 0.020973 | -0.013123 | -0.0032021 | 0.067398 | 0.0706 | -0.20169 | -0.0039072 | 120.9732 | 23.9731 | 39.9811 | 1.7395 | 121.0831 | -0.44403 | -0.49896 | 1.6342 | 43.0161 | -0.59052 | 121.0144 | 121.1655 | -0.38452 | -0.4303 | 0.064087 | 0.009156 | -0.041199 | 24.4812 | 2.2476 | 2.2385 | -0.15106 | 0.1236 | 0.07782 | -0.10986 | 2.1423 | -0.082397 | -0.16022 | 0.041198 | 121.5912 | 121.4813 | 40.4892 | -121.6232 | 121.5225 | 121.6736 | 43.5242 | -121.5546
2127.3594 | 121.7377 | -0.48981 | 121.0968 | -0.0049592 | 0.062333 | 0.13483 | -0.00067498 | 0.090615 | 0.014381 | 0.022896 | 0.0021363 | -0.0057657 | 0.062912 | 0.069746 | -0.2034 | -0.00048921 | 121.051 | 24.1699 | 40.4022 | 1.8448 | 121.0739 | -0.39368 | -0.45776 | 1.7899 | 43.3319 | -0.45319 | 120.9824 | 121.1151 | -0.35248 | -0.36163 | 0.09613 | 0.032043 | -0.022888 | 24.6597 | 2.3346 | 2.3026 | -0.045777 | 0.13733 | 0.12817 | -0.11444 | 2.2797 | 0.036621 | -0.091553 | 0.01831 | 121.5637 | 121.5408 | 40.892 | -121.5546 | 121.4722 | 121.6049 | 43.8217 | -121.4584
2129.1406 | 121.637 | -0.48065 | 121.1609 | -0.012589 | 0.066819 | 0.13312 | 0.0016748 | 0.094673 | 0.017372 | 0.021614 | 0.0021363 | -0.0034159 | 0.066544 | 0.069319 | -0.2034 | -0.0047616 | 121.0419 | 24.353 | 40.48 | 1.8768 | 121.0876 | -0.40741 | -0.46234 | 1.8082 | 43.483 | -0.50354 | 121.0419 | 121.17 | -0.3479 | -0.39825 | 0.073242 | 0.018311 | -0.073243 | 24.8337 | 2.3575 | 2.3392 | -0.11902 | 0.13275 | 0.082398 | -0.11902 | 2.2888 | -0.022888 | -0.10529 | 0.009155 | 121.5683 | 121.5225 | 40.9607 | -121.6232 | 121.5225 | 121.6507 | 43.9636 | -121.5591
2130.9219 | 121.6827 | -0.46234 | 121.106 | -0.0049592 | 0.064256 | 0.13718 | 0.0027428 | 0.093178 | 0.0075451 | 0.02076 | -0.0054932 | -0.0070475 | 0.067398 | 0.070173 | -0.20617 | -0.0021982 | 121.0464 | 24.6185 | 40.6906 | 1.9455 | 121.0373 | -0.35706 | -0.45319 | 1.8082 | 43.6569 | -0.44861 | 120.9732 | 121.1334 | -0.33417 | -0.36621 | 0.10529 | 0.009155 | -0.068665 | 25.0809 | 2.4078 | 2.3987 | -0.059509 | 0.12817 | 0.09613 | -0.13275 | 2.2705 | 0.013733 | -0.082397 | 0.027466 | 121.4996 | 121.5088 | 41.153 | -121.5591 | 121.4355 | 121.5958 | 44.1193 | -121.4722
2132.7031 | 121.7148 | -0.45319 | 121.0922 | -0.020218 | 0.064897 | 0.13803 | 0.0018884 | 0.094246 | 0.014808 | 0.021614 | -0.013123 | -0.0051247 | 0.065048 | 0.071668 | -0.20297 | -0.0049752 | 121.0876 | 24.939 | 40.8463 | 2.0233 | 121.0693 | -0.36621 | -0.43488 | 1.9592 | 43.8858 | -0.42572 | 120.9778 | 121.1151 | -0.32959 | -0.35248 | 0.086975 | 0.018311 | -0.022888 | 25.3922 | 2.4765 | 2.4582 | -0.004578 | 0.1236 | 0.10071 | -0.11444 | 2.4124 | 0.027466 | -0.073242 | 0.022888 | 121.5225 | 121.5408 | 41.2994 | -121.5271 | 121.431 | 121.5683 | 44.339 | -121.4447
2134.4219 | 121.6965 | -0.46692 | 121.106 | -0.012589 | 0.067033 | 0.13825 | 0.0016748 | 0.094033 | 0.013099 | 0.020973 | -0.0054932 | -0.0061929 | 0.063766 | 0.06761 | -0.20511 | -0.0024118 | 121.0464 | 25.1495 | 40.9698 | 2.0554 | 121.0464 | -0.37537 | -0.4303 | 1.9318 | 44.133 | -0.48523 | 121.0236 | 121.1426 | -0.34332 | -0.38452 | 0.091553 | 0.036621 | -0.059509 | 25.6165 | 2.5223 | 2.4857 | -0.059509 | 0.1236 | 0.082398 | -0.082397 | 2.3987 | -0.01831 | -0.10071 | 0.036621 | 121.5134 | 121.5134 | 41.4368 | -121.5363 | 121.4905 | 121.6095 | 44.5999 | -121.4905
2136.2031 | 121.756 | -0.45319 | 121.1472 | -0.0049592 | 0.067246 | 0.13974 | 0.0023156 | 0.095528 | 0.013099 | 0.020119 | 0.0021363 | -0.0074747 | 0.066116 | 0.068037 | -0.20404 | -0.0047616 | 121.0831 | 25.4608 | 41.2079 | 2.1469 | 121.0876 | -0.37079 | -0.4303 | 2.0325 | 44.6503 | -0.40741 | 121.0098 | 121.1334 | -0.32044 | -0.35248 | 0.082397 | 0.022888 | -0.05951 | 25.914 | 2.6001 | 2.5772 | -0.064087 | 0.13275 | 0.10071 | -0.13733 | 2.4857 | 0.045776 | -0.054932 | -0.013733 | 121.5408 | 121.5363 | 41.6611 | -121.5775 | 121.463 | 121.5866 | 45.1035 | -121.4996
2138 | 121.5866 | -0.48523 | 121.17 | 0.0026703 | 0.070451 | 0.13654 | 0.00039302 | 0.095314 | 0.022926 | 0.024605 | -0.0054932 | -0.0019205 | 0.067612 | 0.06825 | -0.20105 | -0.0056162 | 121.0693 | 25.6531 | 41.2582 | 2.1835 | 121.0831 | -0.3891 | -0.46692 | 2.0554 | 44.8929 | -0.54932 | 121.0373 | 121.138 | -0.36621 | -0.39825 | 0.09613 | 0.01831 | -0.086975 | 26.1383 | 2.6688 | 2.6505 | -0.10071 | 0.11902 | 0.086975 | -0.13275 | 2.5406 | -0.064087 | -0.15106 | -0.032044 | 121.5683 | 121.5546 | 41.7435 | -121.637 | 121.5225 | 121.6232 | 45.3781 | -121.5683
2139.7656 | 121.5729 | -0.50354 | 121.1334 | -0.0049592 | 0.075151 | 0.14017 | 0.00017942 | 0.098946 | 0.02079 | 0.027169 | -0.020752 | -0.0040567 | 0.068253 | 0.071455 | -0.20019 | -0.0039072 | 121.0373 | 25.8453 | 41.3361 | 2.179 | 121.0876 | -0.40283 | -0.4715 | 2.0645 | 45.1492 | -0.58136 | 121.0098 | 121.1609 | -0.38452 | -0.39825 | 0.10071 | 0.032043 | -0.045777 | 26.3489 | 2.6825 | 2.6505 | -0.096131 | 0.11902 | 0.10529 | -0.1236 | 2.5681 | -0.07782 | -0.18311 | 0.027466 | 121.5912 | 121.5408 | 41.8396 | -121.6049 | 121.5134 | 121.6644 | 45.6528 | -121.5317
2141.4688 | 121.582 | -0.54016 | 121.1426 | -0.012589 | 0.074937 | 0.13996 | 0.00039302 | 0.096596 | 0.020362 | 0.024605 | -0.013123 | -0.0025613 | 0.068893 | 0.068464 | -0.20212 | -0.004548 | 120.9641 | 26.1063 | 41.4459 | 2.2293 | 121.0785 | -0.42114 | -0.48981 | 2.1103 | 45.4468 | -0.58594 | 121.0098 | 121.138 | -0.3479 | -0.40283 | 0.11902 | 0.050354 | -0.064087 | 26.6464 | 2.7695 | 2.7191 | -0.17853 | 0.19226 | 0.13733 | -0.13275 | 2.6505 | -0.045776 | -0.18311 | -0.004578 | 121.6187 | 121.5042 | 41.9861 | -121.6324 | 121.55 | 121.6782 | 45.9869 | -121.5454
2143.25 | 121.5912 | -0.52185 | 121.106 | -0.020218 | 0.076005 | 0.14209 | 0.0033838 | 0.098091 | 0.012031 | 0.024391 | -0.0054932 | -0.0070475 | 0.067825 | 0.071241 | -0.20447 | -0.002839 | 120.9778 | 26.4038 | 41.5329 | 2.3163 | 121.0144 | -0.42572 | -0.49896 | 2.1378 | 45.7626 | -0.54932 | 121.0007 | 121.1517 | -0.42572 | -0.4303 | 0.096131 | 0.022889 | -0.091553 | 26.9257 | 2.8381 | 2.8152 | -0.12817 | 0.096131 | 0.091553 | -0.10529 | 2.6596 | -0.027465 | -0.11902 | 0.045776 | 121.5363 | 121.4996 | 42.0547 | -121.6049 | 121.5225 | 121.6736 | 46.2845 | -121.5363
2145.0156 | 121.669 | -0.48065 | 121.1426 | -0.0049592 | 0.074296 | 0.14423 | 0.0042382 | 0.095528 | 0.015449 | 0.025887 | -0.013123 | -0.0066201 | 0.065689 | 0.069959 | -0.20382 | -0.0015572 | 121.0464 | 26.7014 | 41.7847 | 2.4536 | 121.0419 | -0.36163 | -0.43488 | 2.2842 | 46.1151 | -0.44403 | 120.9869 | 121.1105 | -0.33875 | -0.37994 | 0.11902 | 0.045777 | -0.10071 | 27.182 | 2.9343 | 2.8885 | -0.09613 | 0.14191 | 0.10071 | -0.15564 | 2.7649 | 0.036621 | -0.064087 | -0.032043 | 121.5225 | 121.5271 | 42.2653 | -121.5775 | 121.4676 | 121.5912 | 46.5958 | -121.5225
2146.7969 | 121.582 | -0.48523 | 121.1426 | 0.0103 | 0.078355 | 0.14401 | 0.00039302 | 0.099159 | 0.022712 | 0.02546 | -0.0054932 | -0.0019205 | 0.064407 | 0.071668 | -0.19806 | -0.0036936 | 121.051 | 26.8753 | 41.8076 | 2.4857 | 121.0922 | -0.3891 | -0.45319 | 2.3392 | 46.3531 | -0.52643 | 121.0236 | 121.1243 | -0.35706 | -0.38452 | 0.09613 | 0.032043 | -0.050354 | 27.3605 | 2.9709 | 2.9388 | -0.091553 | 0.12817 | 0.10071 | -0.11902 | 2.8244 | -0.041199 | -0.14191 | -0.01831 | 121.5775 | 121.5363 | 42.2928 | -121.5958 | 121.5088 | 121.6095 | 46.8384 | -121.5271
2148.5625 | 121.637 | -0.48065 | 121.1151 | -0.020218 | 0.083055 | 0.14487 | 0.002102 | 0.097451 | 0.019935 | 0.027169 | -0.013123 | -0.0019205 | 0.067612 | 0.06825 | -0.20212 | -0.004548 | 120.9961 | 27.1042 | 41.8625 | 2.5497 | 121.0831 | -0.4303 | -0.46692 | 2.3987 | 46.843 | -0.5127 | 121.0052 | 121.1472 | -0.38452 | -0.40283 | 0.050354 | 0.013733 | -0.032043 | 27.5848 | 3.0304 | 3.0167 | -0.11902 | 0.096131 | 0.07782 | -0.10986 | 2.8793 | -0.032043 | -0.10986 | 0.032044 | 121.5637 | 121.4767 | 42.3431 | -121.582 | 121.4859 | 121.6278 | 47.3236 | -121.5179
2150.3281 | 121.5958 | -0.51727 | 121.1426 | -0.0049592 | 0.081773 | 0.14722 | 0.0025292 | 0.099159 | 0.014381 | 0.026741 | 0.0021363 | -0.0059793 | 0.067184 | 0.068891 | -0.20382 | -0.0032662 | 121.0327 | 27.4017 | 42.041 | 2.6459 | 121.0098 | -0.38452 | -0.46234 | 2.4582 | 47.2549 | -0.47607 | 120.9869 | 121.1517 | -0.36621 | -0.39368 | 0.13275 | 0.054932 | -0.13275 | 27.919 | 3.1631 | 3.1082 | -0.10986 | 0.15106 | 0.1236 | -0.15564 | 2.9755 | 0.041199 | -0.082397 | 0.009155 | 121.5271 | 121.55 | 42.5583 | -121.6049 | 121.5042 | 121.669 | 47.7722 | -121.5363
2152.0938 | 121.6095 | -0.49896 | 121.1243 | -0.0049592 | 0.079209 | 0.15021 | 0.0014612 | 0.099587 | 0.016945 | 0.025887 | -0.013123 | -0.0079019 | 0.06633 | 0.068037 | -0.20404 | -0.0039072 | 121.0281 | 27.6306 | 42.1646 | 2.6825 | 121.019 | -0.38452 | -0.44861 | 2.5635 | 47.5525 | -0.43945 | 120.9686 | 121.0922 | -0.34332 | -0.3891 | 0.11444 | 0.050354 | -0.10529 | 28.1296 | 3.1815 | 3.1311 | -0.096131 | 0.15564 | 0.10986 | -0.15564 | 3.0624 | 0.059509 | -0.050354 | -0.032044 | 121.5179 | 121.5271 | 42.6636 | -121.5729 | 121.4676 | 121.5912 | 48.0515 | -121.5134
2153.7969 | 121.582 | -0.52643 | 121.106 | -0.012589 | 0.086259 | 0.14765 | 0.00082022 | 0.10108 | 0.024421 | 0.02845 | -0.0054932 | -0.0014933 | 0.065689 | 0.070173 | -0.20019 | -0.0060434 | 120.9915 | 27.6718 | 42.1234 | 2.6733 | 121.0693 | -0.42114 | -0.48981 | 2.5406 | 47.6624 | -0.58136 | 121.0052 | 121.1334 | -0.38452 | -0.42572 | 0.10529 | 0.036621 | -0.036621 | 28.1982 | 3.1998 | 3.1631 | -0.11444 | 0.14191 | 0.10071 | -0.10071 | 3.067 | -0.054932 | -0.15564 | 0.027466 | 121.5958 | 121.5179 | 42.6498 | -121.5958 | 121.5317 | 121.6599 | 48.1888 | -121.5317
2155.5625 | 121.6278 | -0.53101 | 121.1014 | -0.0049592 | 0.087327 | 0.14978 | 0.00552 | 0.097664 | 0.02079 | 0.029732 | -0.0054932 | -0.0027749 | 0.06868 | 0.070387 | -0.2066 | -0.0030526 | 120.9366 | 27.8961 | 42.334 | 2.71 | 121.051 | -0.44403 | -0.52185 | 2.5818 | 47.9416 | -0.5722 | 120.9869 | 121.1426 | -0.38452 | -0.42114 | 0.086975 | 0.009155 | -0.050354 | 28.4271 | 3.241 | 3.2318 | -0.16479 | 0.14648 | 0.10986 | -0.11444 | 3.1128 | -0.041199 | -0.15106 | 0.041199 | 121.582 | 121.4676 | 42.865 | -121.6232 | 121.5179 | 121.6736 | 48.4726 | -121.5225
2157.2656 | 121.5958 | -0.48065 | 121.138 | -0.0049592 | 0.087541 | 0.14893 | 0.00017942 | 0.10215 | 0.022071 | 0.029946 | -0.0054932 | -0.0025613 | 0.067825 | 0.071241 | -0.2019 | -0.0026254 | 121.0007 | 28.0838 | 42.4255 | 2.8061 | 121.0968 | -0.38452 | -0.48065 | 2.7008 | 48.3627 | -0.56763 | 121.019 | 121.1838 | -0.37537 | -0.3891 | 0.096131 | 0 | -0.041198 | 28.5645 | 3.2867 | 3.2867 | -0.13733 | 0.10529 | 0.091553 | -0.11902 | 3.1815 | -0.086975 | -0.17853 | 0.045777 | 121.5775 | 121.4813 | 42.9062 | -121.6187 | 121.4996 | 121.6644 | 48.8434 | -121.5271
2159.0469 | 121.6049 | -0.4715 | 121.138 | -0.012589 | 0.088182 | 0.15192 | 0.0035974 | 0.10151 | 0.015236 | 0.029091 | 0.0021363 | -0.0066201 | 0.067184 | 0.069959 | -0.2066 | -0.0039072 | 121.0693 | 28.4088 | 42.6086 | 2.9251 | 121.0281 | -0.35248 | -0.42572 | 2.861 | 48.8754 | -0.39825 | 120.9915 | 121.138 | -0.3067 | -0.33875 | 0.11902 | 0.045777 | -0.10986 | 28.8803 | 3.3966 | 3.3508 | -0.068664 | 0.1648 | 0.13275 | -0.14648 | 3.3325 | 0.073243 | -0.059509 | 0 | 121.4996 | 121.5408 | 43.0801 | -121.5637 | 121.463 | 121.6095 | 49.3469 | -121.4767
2160.8281 | 121.6965 | -0.4303 | 121.1151 | -0.012589 | 0.085618 | 0.15555 | 0.0048792 | 0.10065 | 0.017799 | 0.027169 | -0.0054932 | -0.0068337 | 0.065689 | 0.071028 | -0.20468 | -0.0026254 | 121.0785 | 28.6194 | 42.7048 | 3.0075 | 121.0648 | -0.33875 | -0.41199 | 2.9663 | 49.1501 | -0.36621 | 120.9961 | 121.1426 | -0.30212 | -0.32959 | 0.091553 | 0.018311 | -0.050354 | 29.0497 | 3.4378 | 3.4195 | -0.036621 | 0.12817 | 0.10071 | -0.11902 | 3.3966 | 0.064087 | -0.036621 | 0.027466 | 121.4951 | 121.5088 | 43.1351 | -121.5271 | 121.4264 | 121.5729 | 49.5804 | -121.4447
2162.5938 | 121.7148 | -0.4303 | 121.1243 | -0.020218 | 0.087754 | 0.15427 | -0.001316 | 0.10258 | 0.025489 | 0.030159 | -0.013123 | -0.0044839 | 0.069107 | 0.071668 | -0.20126 | -0.0041208 | 121.0052 | 28.656 | 42.6865 | 2.9755 | 121.106 | -0.37079 | -0.45776 | 2.9572 | 49.2004 | -0.48981 | 121.0236 | 121.138 | -0.32044 | -0.37079 | 0.059509 | -0.027466 | -0.018311 | 29.0863 | 3.4058 | 3.4332 | -0.11902 | 0.10986 | 0.059509 | -0.10071 | 3.3875 | -0.059509 | -0.11902 | 0.013732 | 121.5363 | 121.4355 | 43.1168 | -121.582 | 121.4539 | 121.5683 | 49.6307 | -121.4951
2164.3906 | 121.6187 | -0.49896 | 121.1334 | 0.0026703 | 0.093522 | 0.15619 | 0.00039302 | 0.10407 | 0.025489 | 0.031655 | 0.0021363 | -0.0029885 | 0.066971 | 0.0706 | -0.20276 | -0.006257 | 120.9915 | 28.8483 | 42.8055 | 3.0396 | 121.0922 | -0.39368 | -0.46234 | 3.0441 | 49.1547 | -0.50354 | 121.0419 | 121.1609 | -0.34332 | -0.36621 | 0.10529 | 0.036621 | -0.041199 | 29.3472 | 3.5385 | 3.5019 | -0.14191 | 0.15564 | 0.13275 | -0.091553 | 3.5431 | -0.004578 | -0.13733 | 0.027466 | 121.5912 | 121.4905 | 43.3044 | -121.5958 | 121.5408 | 121.6599 | 49.6536 | -121.4996
2166.1719 | 121.6827 | -0.42572 | 121.1609 | -0.012589 | 0.09224 | 0.1564 | -0.004093 | 0.10065 | 0.023353 | 0.031655 | -0.0054932 | -0.0036295 | 0.066971 | 0.069959 | -0.20083 | -0.0019846 | 121.0144 | 28.9902 | 42.8925 | 3.1174 | 121.1334 | -0.34332 | -0.42572 | 3.1219 | 49.205 | -0.49439 | 121.0648 | 121.1746 | -0.30212 | -0.35248 | 0.082397 | 0 | -0.027466 | 29.4159 | 3.5431 | 3.5431 | -0.14648 | 0.1236 | 0.073242 | -0.096131 | 3.5477 | -0.068665 | -0.14191 | 0.013733 | 121.5591 | 121.4401 | 43.3182 | -121.5866 | 121.4905 | 121.6003 | 49.6307 | -121.5134
2167.9375 | 121.6873 | -0.43488 | 121.106 | -0.0049592 | 0.096299 | 0.15769 | -3.4178e-05 | 0.10343 | 0.022926 | 0.031868 | -0.013123 | -0.0034159 | 0.065475 | 0.0706 | -0.20297 | -0.0019846 | 120.9778 | 29.0863 | 43.1259 | 3.1219 | 121.0785 | -0.37537 | -0.45319 | 3.186 | 49.4659 | -0.5127 | 121.0236 | 121.1517 | -0.35248 | -0.37537 | 0.059509 | -0.018311 | -0.027466 | 29.5212 | 3.5568 | 3.5751 | -0.12817 | 0.082397 | 0.059509 | -0.082397 | 3.6209 | -0.07782 | -0.13733 | 0.045776 | 121.5134 | 121.4127 | 43.5608 | -121.5591 | 121.4584 | 121.5866 | 49.9008 | -121.4813
2169.7031 | 121.5912 | -0.50812 | 121.17 | -0.012589 | 0.097367 | 0.15854 | 0.0018884 | 0.10258 | 0.021644 | 0.030159 | -0.0054932 | -0.0034159 | 0.066971 | 0.070387 | -0.20447 | -0.001771 | 120.9412 | 29.2374 | 43.3136 | 3.1815 | 121.051 | -0.38452 | -0.44861 | 3.2272 | 50.2579 | -0.54016 | 121.0098 | 121.1838 | -0.3479 | -0.40741 | 0.1236 | 0.05951 | -0.11902 | 29.7455 | 3.6896 | 3.6301 | -0.22888 | 0.16022 | 0.10071 | -0.16022 | 3.7354 | -0.032043 | -0.13275 | 0.013733 | 121.5591 | 121.4493 | 43.8217 | -121.6187 | 121.5179 | 121.6919 | 50.766 | -121.5775
2171.4219 | 121.6599 | -0.44861 | 121.0739 | -0.012589 | 0.096299 | 0.16153 | -0.0011024 | 0.10493 | 0.021431 | 0.033364 | -0.0054932 | -0.0057657 | 0.064835 | 0.069105 | -0.20276 | -0.002839 | 121.0419 | 29.5624 | 43.5883 | 3.3188 | 121.0052 | -0.35248 | -0.44403 | 3.4012 | 50.6195 | -0.40741 | 120.9457 | 121.1014 | -0.33875 | -0.36621 | 0.09613 | 0.004577 | -0.068665 | 30.011 | 3.7674 | 3.7628 | -0.032044 | 0.10986 | 0.082397 | -0.12817 | 3.8498 | 0.041198 | -0.041199 | 0.027465 | 121.4539 | 121.4905 | 44.0369 | -121.5179 | 121.3943 | 121.55 | 51.0681 | -121.4401
2173.1875 | 121.7148 | -0.45319 | 121.0739 | -0.012589 | 0.098008 | 0.16474 | 0.0018884 | 0.10386 | 0.019294 | 0.032509 | -0.0054932 | -0.0057657 | 0.067612 | 0.068678 | -0.20788 | -0.0036936 | 121.0281 | 29.7638 | 43.7119 | 3.3737 | 121.0327 | -0.37079 | -0.45319 | 3.4378 | 50.798 | -0.38452 | 120.9549 | 121.1014 | -0.33875 | -0.36163 | 0.082397 | 0 | -0.041199 | 30.217 | 3.8269 | 3.8269 | -0.045777 | 0.11444 | 0.091553 | -0.11902 | 3.891 | 0.068665 | -0.022888 | 0.027465 | 121.4859 | 121.4813 | 44.165 | -121.5271 | 121.4081 | 121.5546 | 51.2512 | -121.4355
2174.9688 | 121.6827 | -0.45319 | 121.0831 | 0.0026703 | 0.10292 | 0.16644 | 0.002102 | 0.10493 | 0.022712 | 0.031014 | -0.013123 | -0.0072611 | 0.065048 | 0.068464 | -0.20575 | -0.0032662 | 121.0556 | 30.011 | 43.8583 | 3.4424 | 121.019 | -0.3891 | -0.44403 | 3.5065 | 50.9308 | -0.40741 | 120.9274 | 121.0831 | -0.32044 | -0.37994 | 0.064087 | 0.009155 | -0.064087 | 30.4642 | 3.8956 | 3.8864 | -0.027466 | 0.13275 | 0.073242 | -0.15564 | 3.9597 | 0.045776 | -0.027466 | 0 | 121.4722 | 121.5088 | 44.3115 | -121.5271 | 121.3806 | 121.5363 | 51.384 | -121.463
2176.6719 | 121.6827 | -0.48065 | 121.0831 | 0.0026703 | 0.099504 | 0.1658 | 0.0023156 | 0.10621 | 0.02314 | 0.033577 | -0.013123 | -0.0076883 | 0.067184 | 0.06825 | -0.20489 | -0.0036936 | 120.9732 | 30.0659 | 43.8995 | 3.4561 | 121.0281 | -0.37079 | -0.43945 | 3.4927 | 51.1093 | -0.49439 | 120.9686 | 121.1014 | -0.3479 | -0.39825 | 0.10986 | 0.041199 | -0.054932 | 30.5466 | 3.9368 | 3.8956 | -0.10986 | 0.13275 | 0.082398 | -0.11444 | 3.9734 | -0.013733 | -0.096131 | 0.01831 | 121.5088 | 121.4539 | 44.3802 | -121.5225 | 121.4493 | 121.582 | 51.59 | -121.4813
2178.4531 | 121.5958 | -0.52643 | 121.0785 | 0.0026703 | 0.10719 | 0.16666 | 0.0016748 | 0.10706 | 0.031044 | 0.034432 | -0.0054932 | -0.0019205 | 0.06868 | 0.072523 | -0.19912 | -0.0030526 | 120.9869 | 30.2216 | 43.9407 | 3.4927 | 121.0373 | -0.41199 | -0.49439 | 3.5751 | 51.3107 | -0.52643 | 120.9595 | 121.0922 | -0.38452 | -0.4303 | 0.11444 | 0.032043 | -0.041199 | 30.748 | 4.0192 | 3.9871 | -0.091553 | 0.14191 | 0.09613 | -0.11902 | 4.1016 | 0 | -0.09613 | 0.013733 | 121.5637 | 121.5134 | 44.4672 | -121.5729 | 121.4859 | 121.6187 | 51.8372 | -121.5088
2180.2344 | 121.6599 | -0.50354 | 121.0556 | -0.0049592 | 0.10634 | 0.16538 | -0.0011024 | 0.106 | 0.023567 | 0.036141 | -0.013123 | -0.0051247 | 0.065262 | 0.070173 | -0.20297 | -0.0026254 | 121.019 | 30.4596 | 44.0506 | 3.5843 | 120.9824 | -0.39825 | -0.46234 | 3.6987 | 51.5762 | -0.44861 | 120.9183 | 121.0648 | -0.36621 | -0.40283 | 0.10529 | 0.041199 | -0.073242 | 30.9631 | 4.0878 | 4.0466 | -0.036621 | 0.13733 | 0.10071 | -0.13733 | 4.2023 | 0.054932 | -0.045776 | 0.009155 | 121.4859 | 121.5225 | 44.5541 | -121.5179 | 121.4218 | 121.5683 | 52.0798 | -121.4584
2182 | 121.669 | -0.50812 | 121.051 | -0.012589 | 0.10613 | 0.1658 | -0.0021704 | 0.1045 | 0.026558 | 0.038277 | -0.013123 | -0.0053385 | 0.067184 | 0.071028 | -0.20147 | -0.0056162 | 121.0052 | 30.5786 | 44.1055 | 3.6484 | 120.9595 | -0.3891 | -0.48065 | 3.8452 | 51.503 | -0.46692 | 120.9091 | 121.0236 | -0.38452 | -0.39368 | 0.11902 | 0.027466 | -0.091552 | 31.0867 | 4.1565 | 4.129 | -0.045776 | 0.1236 | 0.11444 | -0.14191 | 4.3533 | 0.041199 | -0.073242 | -0.027465 | 121.4676 | 121.5134 | 44.6136 | -121.5317 | 121.4172 | 121.5317 | 52.0111 | -121.4447
2183.7188 | 121.6827 | -0.50812 | 121.019 | -0.020218 | 0.11061 | 0.16922 | 0.0025292 | 0.10899 | 0.02378 | 0.036782 | -0.0054932 | -0.0081155 | 0.066544 | 0.068037 | -0.20425 | -0.0026254 | 121.0098 | 30.8441 | 44.165 | 3.6987 | 120.9641 | -0.42114 | -0.47607 | 3.9413 | 51.8463 | -0.43488 | 120.8862 | 121.019 | -0.37537 | -0.39825 | 0.086975 | 0.032044 | -0.054932 | 31.3522 | 4.2068 | 4.1748 | -0.009155 | 0.13275 | 0.10986 | -0.13275 | 4.4495 | 0.073243 | -0.036621 | 0 | 121.4722 | 121.5179 | 44.6732 | -121.4951 | 121.3943 | 121.5271 | 52.3544 | -121.4172
2185.4844 | 121.6782 | -0.50354 | 121.0007 | -0.0049592 | 0.11232 | 0.16944 | -0.0019568 | 0.10963 | 0.029548 | 0.037636 | -0.013123 | -0.0017069 | 0.066757 | 0.071882 | -0.19912 | -0.0039072 | 120.9183 | 30.8304 | 44.0186 | 3.6713 | 121.0098 | -0.45319 | -0.51727 | 3.978 | 52.0065 | -0.5722 | 120.9412 | 121.0373 | -0.40283 | -0.44403 | 0.050354 | -0.013733 | 0.009156 | 31.3339 | 4.1748 | 4.1885 | -0.082397 | 0.10071 | 0.059509 | -0.059509 | 4.4815 | -0.068665 | -0.12817 | 0.036621 | 121.5134 | 121.4218 | 44.5221 | -121.5179 | 121.4447 | 121.5408 | 52.5101 | -121.4447
2187.2656 | 121.6553 | -0.51727 | 121.0236 | -0.012589 | 0.11382 | 0.17178 | 0.0014612 | 0.10856 | 0.024208 | 0.037209 | -0.013123 | -0.0061929 | 0.066971 | 0.069319 | -0.20318 | -0.00113 | 120.9229 | 31.0501 | 44.1422 | 3.7674 | 120.9641 | -0.41199 | -0.48523 | 4.0558 | 52.2263 | -0.52185 | 120.9091 | 121.0052 | -0.37079 | -0.42572 | 0.10529 | 0.032044 | -0.05951 | 31.5674 | 4.2847 | 4.2526 | -0.10071 | 0.14648 | 0.091553 | -0.11444 | 4.5731 | -0.004578 | -0.096131 | -0.018311 | 121.4813 | 121.4401 | 44.6594 | -121.5088 | 121.4264 | 121.5225 | 52.7435 | -121.4493
2189.0469 | 121.637 | -0.52643 | 121.0373 | -0.012589 | 0.11424 | 0.17029 | 0.00060662 | 0.10835 | 0.031257 | 0.039986 | -0.0054932 | -0.0017069 | 0.069748 | 0.069532 | -0.20254 | -0.0036936 | 120.9091 | 31.0822 | 44.1101 | 3.7582 | 120.9915 | -0.44403 | -0.52185 | 4.1519 | 52.4689 | -0.60883 | 120.9457 | 121.051 | -0.41199 | -0.43488 | 0.082397 | 0.004577 | -0.045776 | 31.6086 | 4.2847 | 4.2801 | -0.12817 | 0.11444 | 0.091553 | -0.091552 | 4.6783 | -0.082398 | -0.17395 | 0.013733 | 121.5179 | 121.4355 | 44.6365 | -121.5591 | 121.4722 | 121.5775 | 52.9953 | -121.4722
2190.8125 | 121.5408 | -0.56763 | 121.0419 | -0.0049592 | 0.12343 | 0.17072 | 0.0046656 | 0.10728 | 0.032753 | 0.041054 | -0.013123 | -0.00042512 | 0.071884 | 0.071882 | -0.20105 | -0.0047616 | 120.9412 | 31.2424 | 44.2017 | 3.8223 | 120.9824 | -0.45319 | -0.53558 | 4.2847 | 52.7618 | -0.59509 | 120.9229 | 121.0419 | -0.41199 | -0.46234 | 0.11444 | 0.032044 | -0.059509 | 31.81 | 4.39 | 4.3579 | -0.10071 | 0.15564 | 0.10529 | -0.11902 | 4.8523 | -0.027466 | -0.13275 | 0 | 121.55 | 121.5088 | 44.7693 | -121.5775 | 121.4905 | 121.6095 | 53.3295 | -121.5042
2192.5156 | 121.6003 | -0.56305 | 121.0464 | -0.0049592 | 0.12108 | 0.17413 | 0.0042382 | 0.11112 | 0.028907 | 0.04084 | -0.0054932 | -0.0029885 | 0.069107 | 0.071241 | -0.20297 | -0.0030526 | 120.8817 | 31.4026 | 44.2108 | 3.8635 | 120.9778 | -0.45319 | -0.54932 | 4.335 | 52.8122 | -0.60883 | 120.9366 | 121.051 | -0.4303 | -0.46692 | 0.10986 | 0.013733 | -0.068665 | 31.9656 | 4.4266 | 4.4128 | -0.16479 | 0.13275 | 0.09613 | -0.10986 | 4.8981 | -0.045777 | -0.14191 | 0.004577 | 121.5408 | 121.4447 | 44.7739 | -121.5958 | 121.4996 | 121.6141 | 53.3752 | -121.5134
2194.2969 | 121.6644 | -0.52185 | 121.0464 | -0.0049592 | 0.11745 | 0.17307 | 0.0031702 | 0.1092 | 0.022071 | 0.039986 | -0.0054932 | -0.0066201 | 0.067612 | 0.069105 | -0.20468 | -0.00027561 | 120.8954 | 31.6727 | 44.3298 | 3.9505 | 120.9824 | -0.41199 | -0.48523 | 4.4907 | 52.9861 | -0.52185 | 120.9045 | 121.0236 | -0.37537 | -0.44403 | 0.10986 | 0.036622 | -0.064087 | 32.1945 | 4.4724 | 4.4357 | -0.15106 | 0.14648 | 0.07782 | -0.14191 | 5.0125 | 0 | -0.07782 | -0.022888 | 121.5042 | 121.4172 | 44.8517 | -121.5317 | 121.4264 | 121.5454 | 53.508 | -121.4905
2196.0625 | 121.669 | -0.48981 | 120.9824 | 0.0026703 | 0.12022 | 0.17456 | -3.4178e-05 | 0.11027 | 0.031044 | 0.040413 | -0.0054932 | -0.0064065 | 0.067825 | 0.072309 | -0.20105 | -0.0039072 | 120.9641 | 31.7551 | 44.3665 | 4.0695 | 120.9778 | -0.40741 | -0.48523 | 4.6692 | 53.064 | -0.48065 | 120.8817 | 121.0373 | -0.36621 | -0.40741 | 0.082397 | 0.004578 | -0.004578 | 32.2449 | 4.5593 | 4.5547 | -0.018311 | 0.1236 | 0.082397 | -0.10071 | 5.159 | 0.009155 | -0.073242 | 0.054931 | 121.4676 | 121.4539 | 44.8563 | -121.4676 | 121.3715 | 121.5271 | 53.5538 | -121.3898
2197.8281 | 121.6507 | -0.53558 | 120.9778 | -0.0049592 | 0.11574 | 0.17841 | -0.00046138 | 0.11048 | 0.025489 | 0.0402 | -0.013123 | -0.0081155 | 0.06398 | 0.067182 | -0.20318 | -0.0015572 | 120.8817 | 31.9244 | 44.3573 | 4.0649 | 120.9457 | -0.42572 | -0.49439 | 4.6646 | 53.2791 | -0.52185 | 120.8725 | 120.9915 | -0.3891 | -0.43488 | 0.10986 | 0.041198 | -0.032043 | 32.46 | 4.6005 | 4.5593 | -0.09613 | 0.14648 | 0.10071 | -0.10529 | 5.2002 | 0.013732 | -0.086976 | 0.013733 | 121.4813 | 121.4172 | 44.8929 | -121.4722 | 121.4081 | 121.5271 | 53.8147 | -121.4127
2199.5469 | 121.6553 | -0.51727 | 120.9915 | -0.0049592 | 0.12621 | 0.17798 | 0.00082022 | 0.11048 | 0.031471 | 0.042122 | 0.0097658 | -0.0019205 | 0.070816 | 0.071882 | -0.20169 | -0.0049752 | 120.8817 | 32.0114 | 44.2749 | 4.0787 | 121.0007 | -0.43945 | -0.52643 | 4.7791 | 53.9383 | -0.58136 | 120.9412 | 121.0007 | -0.39368 | -0.43945 | 0.07782 | -0.009155 | 0.009155 | 32.5287 | 4.5959 | 4.6051 | -0.10986 | 0.1236 | 0.07782 | -0.050354 | 5.2963 | -0.064087 | -0.14191 | 0.009155 | 121.5179 | 121.3989 | 44.7922 | -121.5179 | 121.4584 | 121.5179 | 54.4556 | -121.431
2201.3125 | 121.5454 | -0.58136 | 121.0419 | -0.0049592 | 0.12621 | 0.17734 | 0.0018884 | 0.1139 | 0.027412 | 0.038491 | -0.013123 | -0.0064065 | 0.068039 | 0.069959 | -0.20596 | -0.0034798 | 120.9229 | 32.2403 | 44.4031 | 4.1748 | 120.9457 | -0.42572 | -0.50354 | 4.953 | 54.5242 | -0.52643 | 120.8725 | 121.0373 | -0.40741 | -0.43945 | 0.15564 | 0.07782 | -0.09613 | 32.8217 | 4.7562 | 4.6783 | -0.11902 | 0.17395 | 0.14191 | -0.16937 | 5.5344 | 0.054932 | -0.086975 | -0.004578 | 121.5271 | 121.5042 | 44.9844 | -121.5454 | 121.4539 | 121.6187 | 55.1056 | -121.4813
2203.0938 | 121.5134 | -0.55847 | 121.0236 | -0.0049592 | 0.12642 | 0.17648 | 0.0029566 | 0.11155 | 0.035957 | 0.04319 | -0.020752 | -0.0021341 | 0.068466 | 0.071241 | -0.20062 | -0.0054026 | 120.9229 | 32.2952 | 44.3161 | 4.184 | 120.9732 | -0.43945 | -0.52643 | 5.0629 | 54.863 | -0.59052 | 120.9274 | 121.0327 | -0.43488 | -0.45319 | 0.11902 | 0.032044 | -0.050354 | 32.8537 | 4.7424 | 4.7104 | -0.10071 | 0.1236 | 0.10529 | -0.096131 | 5.6213 | -0.032043 | -0.13733 | 0.009155 | 121.5317 | 121.4813 | 44.8746 | -121.55 | 121.4859 | 121.5912 | 55.4214 | -121.4767
2204.875 | 121.669 | -0.52643 | 120.9824 | -0.012589 | 0.12599 | 0.17926 | -0.00088858 | 0.11539 | 0.031257 | 0.042763 | -0.0054932 | -0.0055521 | 0.065903 | 0.071028 | -0.20169 | -0.002839 | 120.8954 | 32.4463 | 44.3253 | 4.2343 | 120.9641 | -0.43945 | -0.52185 | 5.2597 | 55.2017 | -0.51727 | 120.845 | 120.9824 | -0.39825 | -0.4303 | 0.086975 | 0.004577 | -0.018311 | 32.9727 | 4.7607 | 4.7562 | -0.086975 | 0.12817 | 0.09613 | -0.13733 | 5.7861 | 0.009155 | -0.086975 | 0 | 121.4905 | 121.4218 | 44.8517 | -121.5042 | 121.3715 | 121.5088 | 55.7281 | -121.4127
2206.5781 | 121.637 | -0.53558 | 120.9595 | -0.0049592 | 0.1245 | 0.17948 | 0.00039302 | 0.11582 | 0.029548 | 0.044472 | 0.0021363 | -0.0051247 | 0.067184 | 0.071668 | -0.20382 | -0.0021982 | 120.9366 | 32.6248 | 44.3573 | 4.303 | 120.9045 | -0.42572 | -0.50812 | 5.397 | 55.6686 | -0.49439 | 120.8496 | 120.9824 | -0.40741 | -0.43945 | 0.10986 | 0.027465 | -0.054932 | 33.1604 | 4.8386 | 4.8111 | -0.022889 | 0.12817 | 0.09613 | -0.10986 | 5.9326 | 0.041198 | -0.054932 | 0.022888 | 121.4401 | 121.4722 | 44.8929 | -121.4676 | 121.3852 | 121.5179 | 56.2042 | -121.3989
2208.3594 | 121.5683 | -0.58136 | 121.019 | -0.0049592 | 0.1324 | 0.18289 | 0.003811 | 0.11582 | 0.03083 | 0.043831 | -0.013123 | -0.0040567 | 0.07103 | 0.069746 | -0.20468 | -0.004548 | 120.8267 | 32.6431 | 44.3344 | 4.2709 | 120.9595 | -0.47607 | -0.56763 | 5.3421 | 56.0486 | -0.63629 | 120.9 | 121.0052 | -0.44403 | -0.48523 | 0.10529 | 0.013733 | -0.059509 | 33.2245 | 4.8523 | 4.8386 | -0.19226 | 0.13733 | 0.096131 | -0.11902 | 5.9235 | -0.054932 | -0.15106 | -0.013733 | 121.5408 | 121.4081 | 44.9158 | -121.5866 | 121.4813 | 121.5866 | 56.6299 | -121.5042
2210.0625 | 121.6141 | -0.53558 | 120.9732 | -0.0049592 | 0.12621 | 0.18076 | 0.00017942 | 0.11561 | 0.028267 | 0.045967 | -0.0054932 | -0.0059793 | 0.068039 | 0.071455 | -0.2034 | -0.0013436 | 120.9229 | 32.8354 | 44.4168 | 4.3579 | 120.9045 | -0.4303 | -0.49896 | 5.5801 | 56.2958 | -0.48523 | 120.8359 | 120.9732 | -0.39368 | -0.42572 | 0.10529 | 0.036621 | -0.068665 | 33.371 | 4.8935 | 4.8569 | -0.050354 | 0.14191 | 0.10986 | -0.13733 | 6.1157 | 0.050354 | -0.059509 | 0 | 121.4401 | 121.4584 | 44.9524 | -121.4722 | 121.3715 | 121.5088 | 56.8314 | -121.3989
2211.8281 | 121.6507 | -0.50354 | 120.9869 | -0.0049592 | 0.12749 | 0.18375 | 0.0029566 | 0.11475 | 0.027412 | 0.042763 | -0.013123 | -0.0072611 | 0.067398 | 0.068037 | -0.20532 | -0.0024118 | 120.9412 | 32.9361 | 44.4443 | 4.454 | 120.932 | -0.39825 | -0.49896 | 5.7404 | 56.4972 | -0.45319 | 120.8771 | 121.0052 | -0.37537 | -0.40283 | 0.10529 | 0.004578 | -0.054931 | 33.4396 | 4.9576 | 4.953 | -0.045776 | 0.12817 | 0.10071 | -0.10986 | 6.2439 | 0.050354 | -0.050354 | 0.018311 | 121.4355 | 121.4447 | 44.9478 | -121.4859 | 121.3806 | 121.5088 | 57.0007 | -121.3898
2213.5938 | 121.5225 | -0.5722 | 121.0098 | -0.012589 | 0.13518 | 0.18076 | -0.00046138 | 0.11347 | 0.03788 | 0.04554 | -0.0054932 | -0.0019205 | 0.070602 | 0.071668 | -0.20019 | -0.004548 | 120.8725 | 32.8766 | 44.4855 | 4.4128 | 120.9641 | -0.45319 | -0.54016 | 5.7724 | 56.3599 | -0.63171 | 120.9183 | 121.0281 | -0.43488 | -0.46692 | 0.11902 | 0.032044 | -0.045777 | 33.4488 | 4.985 | 4.953 | -0.13733 | 0.13733 | 0.10529 | -0.091553 | 6.3446 | -0.059509 | -0.1648 | 0.01831 | 121.5363 | 121.4447 | 45.0577 | -121.55 | 121.4905 | 121.6003 | 56.9321 | -121.4767
2215.3594 | 121.6461 | -0.51727 | 120.9686 | -0.012589 | 0.1324 | 0.18311 | 0.00060662 | 0.11518 | 0.032966 | 0.046608 | 0.0021363 | -0.0046975 | 0.06868 | 0.072523 | -0.19955 | -0.0041208 | 120.932 | 33.1284 | 44.6869 | 4.5227 | 120.9091 | -0.41657 | -0.49896 | 5.9601 | 56.5475 | -0.50354 | 120.8725 | 120.9915 | -0.40283 | -0.42114 | 0.10071 | 0.018311 | -0.059509 | 33.6456 | 5.04 | 5.0217 | -0.036621 | 0.11444 | 0.09613 | -0.09613 | 6.4774 | 0.013733 | -0.082397 | 0.022888 | 121.4264 | 121.4493 | 45.2042 | -121.4676 | 121.3898 | 121.5088 | 57.0648 | -121.3898
2217.0781 | 121.5729 | -0.55847 | 121.0144 | -0.012589 | 0.13667 | 0.18759 | 0.0035974 | 0.11454 | 0.026985 | 0.043831 | 0.0021363 | -0.0057657 | 0.070816 | 0.070814 | -0.20404 | -0.002839 | 120.9183 | 33.2245 | 44.7968 | 4.5593 | 120.8817 | -0.43945 | -0.50354 | 6.0791 | 57.3257 | -0.48981 | 120.8542 | 120.9503 | -0.41199 | -0.44861 | 0.11902 | 0.054932 | -0.13275 | 33.783 | 5.1178 | 5.0629 | -0.09613 | 0.14648 | 0.10986 | -0.16022 | 6.6376 | 0.068665 | -0.041199 | -0.064087 | 121.4401 | 121.4767 | 45.3552 | -121.5179 | 121.4127 | 121.5088 | 57.8842 | -121.463
2218.8594 | 121.637 | -0.52643 | 120.9686 | 0.0026703 | 0.13667 | 0.18738 | 0.0044518 | 0.11475 | 0.029548 | 0.044258 | -0.0054932 | -0.0093973 | 0.06868 | 0.070387 | -0.20596 | -0.0026254 | 120.9229 | 33.3298 | 44.8013 | 4.6234 | 120.8771 | -0.44403 | -0.49896 | 6.2073 | 57.3212 | -0.47607 | 120.8588 | 120.9457 | -0.40283 | -0.43488 | 0.082397 | 0.027466 | -0.091553 | 33.8562 | 5.1498 | 5.1224 | -0.045776 | 0.1236 | 0.091553 | -0.10986 | 6.7337 | 0.050354 | -0.041199 | -0.022888 | 121.4035 | 121.4493 | 45.3278 | -121.4676 | 121.3852 | 121.4722 | 57.8476 | -121.4035
2220.5625 | 121.5683 | -0.56305 | 121.0052 | -0.012589 | 0.13902 | 0.18738 | 0.0012476 | 0.11518 | 0.035957 | 0.045113 | -0.013123 | -0.0025613 | 0.070602 | 0.071668 | -0.20169 | -0.0054026 | 120.8313 | 33.2291 | 44.6274 | 4.5547 | 120.9457 | -0.4715 | -0.56305 | 6.2073 | 57.5729 | -0.6134 | 120.9 | 120.9824 | -0.44403 | -0.46692 | 0.091552 | 0 | -0.059509 | 33.7921 | 5.1178 | 5.1178 | -0.17395 | 0.11902 | 0.09613 | -0.10529 | 6.7703 | -0.050354 | -0.14648 | -0.022888 | 121.5088 | 121.3943 | 45.1904 | -121.5683 | 121.463 | 121.5454 | 58.136 | -121.4722
2222.3281 | 121.6003 | -0.55389 | 120.9549 | -0.012589 | 0.13582 | 0.19016 | 0.002102 | 0.11582 | 0.029976 | 0.045967 | -0.0054932 | -0.0072611 | 0.070816 | 0.070814 | -0.20404 | 0.00015159 | 120.8359 | 33.4579 | 44.7144 | 4.6417 | 120.9091 | -0.45319 | -0.5127 | 6.3492 | 58.0261 | -0.55847 | 120.8313 | 120.932 | -0.42114 | -0.45776 | 0.10071 | 0.041199 | -0.045776 | 34.0118 | 5.1956 | 5.1544 | -0.11902 | 0.13275 | 0.09613 | -0.1236 | 6.9031 | -0.004578 | -0.10071 | -0.022888 | 121.463 | 121.3898 | 45.2682 | -121.4676 | 121.3852 | 121.4859 | 58.58 | -121.4127
2224.0938 | 121.5042 | -0.58594 | 121.0236 | -0.020218 | 0.13817 | 0.18781 | 0.0023156 | 0.11625 | 0.034034 | 0.04554 | -0.0054932 | -0.0053385 | 0.066971 | 0.069746 | -0.20233 | -0.0015572 | 120.8862 | 33.5953 | 44.7189 | 4.7516 | 120.9137 | -0.48065 | -0.54932 | 6.4774 | 58.2825 | -0.58594 | 120.8679 | 121.0007 | -0.4303 | -0.4715 | 0.10529 | 0.036621 | -0.10986 | 34.1812 | 5.3375 | 5.3009 | -0.13733 | 0.15564 | 0.11444 | -0.15564 | 7.0633 | 0 | -0.11444 | -0.022889 | 121.4996 | 121.4722 | 45.3049 | -121.5729 | 121.4539 | 121.5866 | 58.8684 | -121.4951
2225.8594 | 121.6049 | -0.54932 | 120.9595 | -0.012589 | 0.13945 | 0.18973 | 0.0018884 | 0.11732 | 0.029335 | 0.044899 | -0.013123 | -0.0059793 | 0.068893 | 0.07295 | -0.20318 | -0.0013436 | 120.8633 | 33.6731 | 44.7739 | 4.7699 | 120.8862 | -0.44403 | -0.52643 | 6.5964 | 58.6441 | -0.54474 | 120.8588 | 120.9412 | -0.41657 | -0.4303 | 0.10529 | 0.022888 | -0.073243 | 34.2224 | 5.3192 | 5.2963 | -0.096131 | 0.13275 | 0.11902 | -0.10071 | 7.1457 | 0.004577 | -0.11444 | -0.018311 | 121.4355 | 121.4127 | 45.3232 | -121.4859 | 121.4081 | 121.4905 | 59.1934 | -121.3898
2227.625 | 121.5042 | -0.58594 | 120.9595 | -0.012589 | 0.14137 | 0.1893 | 0.0027428 | 0.12031 | 0.034675 | 0.04789 | -0.0054932 | -0.0051247 | 0.069962 | 0.073164 | -0.20318 | -0.001771 | 120.845 | 33.6823 | 44.7556 | 4.7562 | 120.9091 | -0.46692 | -0.54016 | 6.665 | 58.8043 | -0.6134 | 120.8725 | 121.0098 | -0.44403 | -0.49439 | 0.11902 | 0.045776 | -0.050354 | 34.2682 | 5.3421 | 5.2963 | -0.11444 | 0.14191 | 0.091552 | -0.086975 | 7.251 | -0.027466 | -0.11902 | 0.050354 | 121.4951 | 121.431 | 45.3415 | -121.4996 | 121.4584 | 121.5958 | 59.3903 | -121.4539
2229.4062 | 121.582 | -0.55847 | 120.9686 | -0.0049592 | 0.14565 | 0.19357 | -0.0015296 | 0.11945 | 0.038734 | 0.049385 | 0.0021363 | 2.078e-06 | 0.070175 | 0.071668 | -0.1987 | -0.0024118 | 120.8176 | 33.7601 | 44.8105 | 4.8065 | 120.9549 | -0.48523 | -0.54932 | 6.7795 | 59.0332 | -0.64087 | 120.8633 | 120.9869 | -0.45776 | -0.48523 | 0.073243 | 0.009156 | -0.013733 | 34.3185 | 5.365 | 5.3558 | -0.15106 | 0.10071 | 0.073243 | -0.10529 | 7.338 | -0.082397 | -0.15564 | 0.01831 | 121.5134 | 121.376 | 45.369 | -121.5179 | 121.4218 | 121.5454 | 59.5917 | -121.4539
2231.1094 | 121.6507 | -0.54932 | 120.932 | -0.012589 | 0.14266 | 0.19122 | 0.001034 | 0.11967 | 0.032539 | 0.047463 | -0.013123 | -0.0081155 | 0.069962 | 0.069746 | -0.20489 | -6.2012e-05 | 120.8221 | 33.934 | 44.9661 | 4.8843 | 120.8908 | -0.46692 | -0.54016 | 6.9122 | 59.6008 | -0.54474 | 120.8176 | 120.9274 | -0.44403 | -0.44403 | 0.082397 | 0.009155 | -0.041199 | 34.4833 | 5.4337 | 5.4245 | -0.10986 | 0.10529 | 0.10529 | -0.11444 | 7.4615 | 0.004577 | -0.10071 | -0.004578 | 121.4401 | 121.3715 | 45.5154 | -121.4722 | 121.3669 | 121.4767 | 60.1501 | -121.376
2232.875 | 121.5958 | -0.55847 | 120.9412 | -0.0049592 | 0.14095 | 0.19229 | 0.00017942 | 0.11732 | 0.033607 | 0.046822 | -0.0054932 | -0.0053385 | 0.06868 | 0.070814 | -0.2034 | -0.00048921 | 120.8588 | 34.0576 | 44.989 | 4.921 | 120.8771 | -0.44861 | -0.51727 | 7.0312 | 60.4294 | -0.55389 | 120.8084 | 120.8954 | -0.43488 | -0.46234 | 0.10986 | 0.041199 | -0.064087 | 34.6161 | 5.4794 | 5.4382 | -0.082397 | 0.1236 | 0.096131 | -0.13275 | 7.5897 | 0.004578 | -0.091553 | -0.045776 | 121.4355 | 121.4172 | 45.5475 | -121.4584 | 121.3669 | 121.4539 | 60.9879 | -121.4035
2234.5781 | 121.637 | -0.56763 | 120.9137 | -0.012589 | 0.14522 | 0.19357 | 0.00552 | 0.11774 | 0.034034 | 0.049385 | -0.0054932 | -0.0079019 | 0.069962 | 0.072309 | -0.20425 | -0.0026254 | 120.8817 | 34.1858 | 45.0485 | 4.9942 | 120.8633 | -0.46692 | -0.50812 | 7.1594 | 59.6146 | -0.48523 | 120.8176 | 120.932 | -0.42114 | -0.45776 | 0.10071 | 0.059509 | -0.050354 | 34.7534 | 5.5618 | 5.5023 | -0.032043 | 0.14648 | 0.10986 | -0.09613 | 7.7271 | 0.082398 | -0.027465 | 0.018311 | 121.431 | 121.4493 | 45.6162 | -121.4218 | 121.3852 | 121.4996 | 60.1822 | -121.3715
2236.3438 | 121.5042 | -0.58594 | 120.9503 | -0.012589 | 0.1497 | 0.19251 | -0.0021704 | 0.11967 | 0.041725 | 0.049813 | -0.013123 | -0.0014933 | 0.069534 | 0.072737 | -0.20019 | -0.0026254 | 120.8679 | 34.1537 | 44.8883 | 4.9667 | 120.8954 | -0.5127 | -0.5722 | 7.2189 | 59.3948 | -0.61798 | 120.8405 | 120.9366 | -0.44861 | -0.50354 | 0.073242 | 0.013732 | -0.054931 | 34.7397 | 5.5527 | 5.5389 | -0.082397 | 0.13733 | 0.082397 | -0.10986 | 7.8049 | -0.032044 | -0.11444 | -0.013733 | 121.4813 | 121.4539 | 45.4742 | -121.5225 | 121.4264 | 121.5225 | 59.9808 | -121.4539
2238.125 | 121.5546 | -0.59052 | 120.9457 | -0.020218 | 0.15013 | 0.19422 | 0.0014612 | 0.11903 | 0.038307 | 0.051735 | -0.013123 | 0.00042948 | 0.069321 | 0.073164 | -0.20147 | -0.0034798 | 120.8359 | 34.1904 | 44.9844 | 4.9805 | 120.8862 | -0.50354 | -0.56305 | 7.3288 | 59.4406 | -0.6134 | 120.8359 | 120.9503 | -0.45776 | -0.50354 | 0.086975 | 0.027466 | -0.05951 | 34.7809 | 5.571 | 5.5435 | -0.10986 | 0.13275 | 0.086975 | -0.10986 | 7.9193 | -0.022888 | -0.10986 | 0.004577 | 121.4767 | 121.4264 | 45.575 | -121.5088 | 121.4264 | 121.5408 | 60.0311 | -121.4493
2239.9062 | 121.6278 | -0.5722 | 120.9137 | -0.012589 | 0.14928 | 0.19721 | 0.00082022 | 0.11796 | 0.032753 | 0.051522 | 0.0021363 | -0.0051247 | 0.070602 | 0.069746 | -0.20447 | -0.0015572 | 120.8862 | 34.3781 | 45.076 | 5.0674 | 120.8267 | -0.48981 | -0.54016 | 7.4707 | 59.6649 | -0.49439 | 120.7855 | 120.9229 | -0.42572 | -0.4715 | 0.082398 | 0.032044 | -0.086975 | 34.9503 | 5.6396 | 5.6076 | -0.027466 | 0.14648 | 0.10071 | -0.12817 | 8.0429 | 0.07782 | -0.022888 | 0.009156 | 121.3989 | 121.4584 | 45.6482 | -121.4539 | 121.3577 | 121.4951 | 60.2371 | -121.3852
2241.6719 | 121.6232 | -0.57678 | 120.8954 | -0.012589 | 0.1465 | 0.19721 | -0.0021704 | 0.11881 | 0.036384 | 0.051522 | -0.0054932 | -0.0027749 | 0.069321 | 0.071668 | -0.19977 | -0.0051888 | 120.8588 | 34.3277 | 45.0943 | 5.0446 | 120.8588 | -0.48523 | -0.54474 | 7.608 | 59.3857 | -0.53558 | 120.7993 | 120.9091 | -0.44403 | -0.46234 | 0.091553 | 0.032043 | -0.036621 | 34.9045 | 5.6213 | 5.5893 | -0.036621 | 0.13275 | 0.11444 | -0.096131 | 8.1848 | 0.041199 | -0.073242 | 0.013733 | 121.4355 | 121.4355 | 45.6711 | -121.4401 | 121.376 | 121.4859 | 59.9625 | -121.3577
2243.4375 | 121.6278 | -0.55847 | 120.9 | -0.012589 | 0.15013 | 0.19678 | 0.00017942 | 0.12202 | 0.037025 | 0.052162 | 0.0021363 | -0.0042703 | 0.068466 | 0.073164 | -0.20105 | -0.0019846 | 120.8588 | 34.3506 | 45.2179 | 5.0995 | 120.8771 | -0.46692 | -0.54016 | 7.6721 | 59.198 | -0.53101 | 120.8038 | 120.932 | -0.44861 | -0.46692 | 0.091553 | 0.018311 | -0.022888 | 34.9091 | 5.658 | 5.6396 | -0.041198 | 0.10986 | 0.091553 | -0.09613 | 8.2306 | 0.027466 | -0.064087 | 0.032044 | 121.4355 | 121.4172 | 45.7764 | -121.4401 | 121.3623 | 121.4905 | 59.7565 | -121.3669
2245.1562 | 121.5134 | -0.61798 | 120.9686 | 0.0026703 | 0.1512 | 0.19956 | 0.0033838 | 0.11881 | 0.035957 | 0.053444 | -0.0054932 | -0.0081155 | 0.069534 | 0.071241 | -0.2034 | -0.0021982 | 120.8313 | 34.4513 | 45.2454 | 5.1315 | 120.8588 | -0.4715 | -0.54932 | 7.7316 | 59.1248 | -0.55389 | 120.8038 | 120.8817 | -0.44861 | -0.48523 | 0.14648 | 0.068665 | -0.10986 | 35.0693 | 5.7495 | 5.6808 | -0.13733 | 0.16937 | 0.13275 | -0.16479 | 8.3496 | 0.064087 | -0.068665 | -0.086975 | 121.4767 | 121.4493 | 45.8633 | -121.5179 | 121.4218 | 121.4996 | 59.7427 | -121.4539
2246.9219 | 121.5729 | -0.59052 | 120.9366 | -0.020218 | 0.15205 | 0.19977 | 0.0031702 | 0.11881 | 0.03553 | 0.050453 | -0.0054932 | -0.0085427 | 0.071884 | 0.069746 | -0.20361 | -0.0034798 | 120.8359 | 34.4925 | 45.3873 | 5.127 | 120.8405 | -0.48981 | -0.54932 | 7.8506 | 59.0927 | -0.53101 | 120.7718 | 120.8908 | -0.43945 | -0.49439 | 0.10071 | 0.041199 | -0.09613 | 35.083 | 5.7175 | 5.6763 | -0.10071 | 0.15106 | 0.09613 | -0.16479 | 8.4412 | 0.059509 | -0.036621 | -0.045776 | 121.431 | 121.4264 | 45.9778 | -121.4859 | 121.3623 | 121.4813 | 59.6832 | -121.431
2248.625 | 121.5042 | -0.61798 | 120.9412 | -0.012589 | 0.15569 | 0.2002 | 0.0018884 | 0.11988 | 0.035102 | 0.051522 | -0.0054932 | -0.0057657 | 0.071671 | 0.072309 | -0.20126 | -0.0034798 | 120.8313 | 34.4833 | 45.3781 | 5.1315 | 120.8496 | -0.50812 | -0.56305 | 7.9147 | 59.2209 | -0.59509 | 120.7901 | 120.8954 | -0.4715 | -0.50812 | 0.10986 | 0.054932 | -0.091553 | 35.1013 | 5.7495 | 5.6946 | -0.10986 | 0.14648 | 0.10986 | -0.15106 | 8.5327 | 0.022888 | -0.086975 | -0.045776 | 121.4676 | 121.4493 | 45.9961 | -121.5042 | 121.4081 | 121.5134 | 59.8389 | -121.4493
2250.4062 | 121.5271 | -0.61798 | 120.9366 | -0.0049592 | 0.15569 | 0.19849 | 0.001034 | 0.12095 | 0.039375 | 0.052376 | -0.013123 | -0.0014933 | 0.071671 | 0.073377 | -0.20233 | -0.0026254 | 120.7764 | 34.433 | 45.3049 | 5.0949 | 120.8588 | -0.52185 | -0.61798 | 7.9514 | 59.2117 | -0.67291 | 120.845 | 120.9686 | -0.49896 | -0.52185 | 0.09613 | 0 | -0.077819 | 35.051 | 5.7129 | 5.7129 | -0.16022 | 0.11902 | 0.09613 | -0.091552 | 8.5693 | -0.054932 | -0.15106 | 0.032044 | 121.4767 | 121.3943 | 45.9229 | -121.5546 | 121.463 | 121.5866 | 59.8297 | -121.4584
2252.125 | 121.4905 | -0.63171 | 120.9366 | -0.012589 | 0.15825 | 0.1987 | 0.00017942 | 0.12031 | 0.041938 | 0.054085 | -0.0054932 | -0.0010659 | 0.070816 | 0.072309 | -0.1987 | -0.0015572 | 120.7718 | 34.4742 | 45.4056 | 5.1224 | 120.8633 | -0.51727 | -0.59052 | 8.0658 | 58.8272 | -0.70038 | 120.8313 | 120.9274 | -0.48065 | -0.52643 | 0.11444 | 0.041199 | -0.073242 | 35.1059 | 5.7541 | 5.7129 | -0.16479 | 0.15106 | 0.10529 | -0.10528 | 8.6975 | -0.068664 | -0.17395 | -0.009155 | 121.4951 | 121.4035 | 46.0373 | -121.5271 | 121.463 | 121.5591 | 59.4589 | -121.463
2253.9062 | 121.5408 | -0.6134 | 120.8771 | -0.012589 | 0.15697 | 0.1987 | 0.003811 | 0.12095 | 0.041084 | 0.054512 | -0.0054932 | -0.0036295 | 0.073166 | 0.072096 | -0.20276 | -0.0015572 | 120.7352 | 34.5154 | 45.5063 | 5.1453 | 120.8588 | -0.52643 | -0.59967 | 8.2077 | 59.2712 | -0.65918 | 120.8221 | 120.9641 | -0.49896 | -0.53101 | 0.086975 | 0.013733 | -0.01831 | 35.1288 | 5.7587 | 5.7449 | -0.14191 | 0.11444 | 0.082397 | -0.054931 | 8.8211 | -0.045777 | -0.12817 | 0.086975 | 121.4722 | 121.3486 | 46.1197 | -121.4767 | 121.4355 | 121.5775 | 59.8846 | -121.4081
2255.625 | 121.4859 | -0.62714 | 120.9183 | -0.0049592 | 0.15889 | 0.19956 | 0.0012476 | 0.12095 | 0.040229 | 0.054512 | -0.013123 | -0.0025613 | 0.072311 | 0.073377 | -0.20105 | -0.001771 | 120.7443 | 34.552 | 45.5612 | 5.1407 | 120.8405 | -0.50812 | -0.6134 | 8.2626 | 59.0973 | -0.70953 | 120.7947 | 120.9137 | -0.50354 | -0.52643 | 0.11902 | 0.013733 | -0.07782 | 35.1791 | 5.7678 | 5.7541 | -0.17395 | 0.1236 | 0.10071 | -0.1236 | 8.8898 | -0.082398 | -0.18311 | -0.004578 | 121.4676 | 121.3715 | 46.1884 | -121.5317 | 121.4218 | 121.5408 | 59.7244 | -121.4447
2257.3906 | 121.4996 | -0.63629 | 120.9091 | -0.0049592 | 0.15718 | 0.20084 | 0.0048792 | 0.12031 | 0.035316 | 0.050667 | -0.0054932 | -0.0044839 | 0.071884 | 0.072523 | -0.20553 | -0.00070281 | 120.7169 | 34.5978 | 45.6757 | 5.1178 | 120.8359 | -0.54016 | -0.60883 | 8.3588 | 59.3765 | -0.67291 | 120.7993 | 120.9183 | -0.50354 | -0.54016 | 0.096131 | 0.027466 | -0.073243 | 35.2341 | 5.7541 | 5.7266 | -0.19226 | 0.13275 | 0.096131 | -0.10986 | 8.9951 | -0.036621 | -0.13275 | 0.009155 | 121.4722 | 121.3531 | 46.312 | -121.5179 | 121.4355 | 121.5546 | 60.0128 | -121.4493
2259.1094 | 121.5271 | -0.63171 | 120.8862 | -0.012589 | 0.1574 | 0.20062 | 0.0016748 | 0.12244 | 0.039375 | 0.054726 | 0.0021363 | -0.0017069 | 0.072952 | 0.073377 | -0.20019 | -0.00091641 | 120.726 | 34.6161 | 45.6985 | 5.1407 | 120.8496 | -0.53101 | -0.59052 | 8.519 | 59.1568 | -0.68665 | 120.8084 | 120.9091 | -0.50812 | -0.53558 | 0.10071 | 0.041199 | -0.036621 | 35.2478 | 5.7724 | 5.7312 | -0.16022 | 0.1236 | 0.096131 | -0.077819 | 9.1507 | -0.054932 | -0.15106 | 0.022889 | 121.4813 | 121.3577 | 46.3303 | -121.4767 | 121.4401 | 121.5408 | 59.7885 | -121.4218
2260.8906 | 121.4951 | -0.65918 | 120.8725 | -0.012589 | 0.1591 | 0.19849 | 0.0040246 | 0.12095 | 0.032753 | 0.054085 | 0.0021363 | -0.0074747 | 0.07338 | 0.072309 | -0.20746 | -0.0013436 | 120.7947 | 34.8587 | 45.9732 | 5.2414 | 120.7855 | -0.51727 | -0.59052 | 8.6884 | 59.2392 | -0.55847 | 120.7489 | 120.8679 | -0.47607 | -0.5127 | 0.14191 | 0.068665 | -0.086976 | 35.5179 | 5.9006 | 5.8319 | -0.07782 | 0.18311 | 0.14648 | -0.1236 | 9.3475 | 0.10071 | -0.045777 | -0.004578 | 121.4447 | 121.4539 | 46.6324 | -121.463 | 121.4081 | 121.5271 | 59.8984 | -121.3852
2262.6562 | 121.5454 | -0.62714 | 120.8954 | -0.012589 | 0.16167 | 0.19998 | 0.0023156 | 0.12159 | 0.039802 | 0.053871 | -0.013123 | -0.0038431 | 0.072311 | 0.074873 | -0.20276 | -0.002839 | 120.7169 | 34.79 | 45.7901 | 5.1956 | 120.8221 | -0.5722 | -0.63629 | 8.7662 | 59.1202 | -0.67749 | 120.7626 | 120.932 | -0.53558 | -0.56763 | 0.054931 | -0.009156 | -0.073242 | 35.4172 | 5.8228 | 5.8319 | -0.17853 | 0.091553 | 0.059509 | -0.13275 | 9.3933 | -0.050354 | -0.10986 | 0.036621 | 121.4493 | 121.344 | 46.4172 | -121.5317 | 121.3898 | 121.5591 | 59.7473 | -121.463
2264.4219 | 121.5775 | -0.63171 | 120.8359 | -0.0049592 | 0.15633 | 0.20105 | 0.0027428 | 0.12095 | 0.032325 | 0.051949 | -0.013123 | -0.0087563 | 0.071457 | 0.074446 | -0.20489 | 0.0020744 | 120.726 | 34.8633 | 45.9412 | 5.2277 | 120.7718 | -0.51727 | -0.57678 | 8.8715 | 58.7723 | -0.60883 | 120.7581 | 120.8359 | -0.49439 | -0.54474 | 0.11444 | 0.054932 | -0.064086 | 35.495 | 5.8594 | 5.8044 | -0.10986 | 0.13733 | 0.086975 | -0.077819 | 9.5032 | 0.022888 | -0.064087 | 0 | 121.4035 | 121.3577 | 46.5729 | -121.4127 | 121.3898 | 121.4676 | 59.404 | -121.3806
2266.2031 | 121.4905 | -0.68207 | 120.8725 | -0.020218 | 0.1574 | 0.20319 | 0.00060662 | 0.1233 | 0.039375 | 0.05494 | 0.0021363 | -0.0049111 | 0.072311 | 0.072737 | -0.20425 | -6.2012e-05 | 120.6711 | 34.8175 | 45.8862 | 5.1727 | 120.7901 | -0.56763 | -0.65002 | 8.9355 | 58.9233 | -0.69122 | 120.7626 | 120.8817 | -0.53101 | -0.56305 | 0.11444 | 0.032044 | -0.082398 | 35.4996 | 5.8548 | 5.8228 | -0.20142 | 0.15106 | 0.11902 | -0.10986 | 9.6176 | -0.009155 | -0.12817 | 0.009155 | 121.4722 | 121.3531 | 46.5683 | -121.5225 | 121.4447 | 121.5637 | 59.6054 | -121.4355
2267.9062 | 121.5271 | -0.6546 | 120.8496 | -0.0049592 | 0.16402 | 0.20062 | 0.0023156 | 0.12437 | 0.042366 | 0.052803 | -0.013123 | -0.0019205 | 0.073807 | 0.071882 | -0.19891 | -0.0032662 | 120.7031 | 34.8267 | 45.8633 | 5.2322 | 120.8176 | -0.55389 | -0.64545 | 9.0958 | 59.0378 | -0.67749 | 120.7306 | 120.8588 | -0.53558 | -0.5722 | 0.10071 | 0.009155 | -0.032043 | 35.4813 | 5.8868 | 5.8777 | -0.14648 | 0.11902 | 0.082397 | -0.11902 | 9.7504 | -0.022888 | -0.10529 | 0.009156 | 121.4722 | 121.3577 | 46.5179 | -121.4951 | 121.3852 | 121.5134 | 59.6924 | -121.4218
2269.6875 | 121.4767 | -0.67291 | 120.9045 | 0.0026703 | 0.16338 | 0.20361 | 0.002102 | 0.12394 | 0.036598 | 0.055367 | -0.0054932 | -0.0055521 | 0.073166 | 0.072096 | -0.20297 | -0.0013436 | 120.7306 | 34.9045 | 45.9549 | 5.2551 | 120.7809 | -0.55389 | -0.64545 | 9.1965 | 59.0927 | -0.69122 | 120.7352 | 120.8862 | -0.52643 | -0.57678 | 0.11902 | 0.027466 | -0.1236 | 35.5774 | 5.928 | 5.9006 | -0.17395 | 0.14648 | 0.096131 | -0.16937 | 9.8694 | -0.01831 | -0.11444 | -0.018311 | 121.4539 | 121.4035 | 46.6278 | -121.55 | 121.4081 | 121.5591 | 59.7656 | -121.4813
2271.4531 | 121.5637 | -0.67749 | 120.8359 | 0.0026703 | 0.15761 | 0.20233 | -0.001316 | 0.12266 | 0.032966 | 0.054512 | -0.020752 | -0.0079019 | 0.072311 | 0.071882 | -0.20361 | -0.00048921 | 120.7352 | 34.9869 | 46.0693 | 5.3055 | 120.7443 | -0.53101 | -0.6134 | 9.3155 | 58.9508 | -0.60883 | 120.6894 | 120.813 | -0.50354 | -0.55389 | 0.14648 | 0.064087 | -0.091552 | 35.6644 | 5.983 | 5.9189 | -0.10071 | 0.17395 | 0.1236 | -0.14648 | 9.993 | 0.068664 | -0.054932 | -0.022888 | 121.4218 | 121.4127 | 46.7468 | -121.4493 | 121.3669 | 121.4905 | 59.6283 | -121.3898
2273.1562 | 121.6049 | -0.63629 | 120.7993 | -0.012589 | 0.16145 | 0.20789 | 0.002102 | 0.12244 | 0.033821 | 0.05259 | 0.0021363 | -0.0085427 | 0.071671 | 0.071241 | -0.2034 | -0.0024118 | 120.6894 | 34.9594 | 46.0693 | 5.3009 | 120.7535 | -0.55847 | -0.62256 | 9.4116 | 59.1248 | -0.62714 | 120.6802 | 120.813 | -0.51727 | -0.54932 | 0.07782 | 0.013733 | -0.045776 | 35.5957 | 5.9372 | 5.9235 | -0.10986 | 0.11902 | 0.086976 | -0.11902 | 10.0479 | 0.009156 | -0.07782 | 0.013733 | 121.3898 | 121.3257 | 46.7056 | -121.4218 | 121.3165 | 121.4493 | 59.761 | -121.3486
2274.9219 | 121.6187 | -0.65002 | 120.7993 | -0.012589 | 0.16295 | 0.20511 | 0.0023156 | 0.12373 | 0.036811 | 0.055367 | -0.013123 | -0.0076883 | 0.072525 | 0.072309 | -0.20361 | -0.0026254 | 120.7489 | 35.1059 | 46.0648 | 5.3879 | 120.7489 | -0.55389 | -0.60883 | 9.5718 | 59.2392 | -0.56305 | 120.6894 | 120.7993 | -0.52643 | -0.54474 | 0.09613 | 0.041198 | -0.050354 | 35.7559 | 6.0379 | 5.9967 | -0.050354 | 0.1236 | 0.10529 | -0.10986 | 10.2219 | 0.086975 | -0.01831 | 0 | 121.3989 | 121.3989 | 46.7148 | -121.4081 | 121.3394 | 121.4493 | 59.8892 | -121.344
2276.6875 | 121.4676 | -0.69122 | 120.8176 | -0.0049592 | 0.16444 | 0.20233 | -0.00067498 | 0.12608 | 0.045356 | 0.058357 | -0.0054932 | -0.0027749 | 0.071884 | 0.074232 | -0.19998 | -0.0034798 | 120.7031 | 34.9823 | 45.9229 | 5.3192 | 120.7901 | -0.56763 | -0.63171 | 9.613 | 59.0881 | -0.76446 | 120.7855 | 120.8771 | -0.55389 | -0.58136 | 0.1236 | 0.059509 | -0.027466 | 35.6735 | 6.0104 | 5.9509 | -0.11444 | 0.13733 | 0.10986 | -0.032044 | 10.3043 | -0.073242 | -0.1831 | 0.059509 | 121.4813 | 121.3943 | 46.6141 | -121.4493 | 121.4767 | 121.5683 | 59.7794 | -121.3989
2278.4688 | 121.5134 | -0.68207 | 120.8542 | -0.020218 | 0.16829 | 0.2049 | 0.001034 | 0.12458 | 0.039589 | 0.056435 | -0.0054932 | -0.0038431 | 0.073593 | 0.071668 | -0.20169 | -0.0015572 | 120.6665 | 35.1059 | 45.9045 | 5.3513 | 120.7718 | -0.59052 | -0.63629 | 9.7 | 59.0652 | -0.71411 | 120.7535 | 120.8542 | -0.54932 | -0.59052 | 0.091553 | 0.045776 | -0.082397 | 35.788 | 6.0333 | 5.9875 | -0.18768 | 0.13275 | 0.091553 | -0.10071 | 10.3821 | -0.032043 | -0.1236 | 0 | 121.4539 | 121.3486 | 46.5866 | -121.4905 | 121.4355 | 121.5363 | 59.7473 | -121.4447
2280.25 | 121.5912 | -0.62714 | 120.813 | -0.0049592 | 0.16487 | 0.20874 | 0.0033838 | 0.12394 | 0.035102 | 0.056649 | -0.013123 | -0.0076883 | 0.071671 | 0.072523 | -0.20553 | -0.001771 | 120.6894 | 35.202 | 46.0327 | 5.4062 | 120.7764 | -0.5722 | -0.60883 | 9.8785 | 59.1339 | -0.61798 | 120.6848 | 120.8542 | -0.50812 | -0.54016 | 0.054931 | 0.01831 | -0.036621 | 35.8292 | 6.0333 | 6.015 | -0.1236 | 0.11902 | 0.086975 | -0.12817 | 10.5057 | 0.009155 | -0.07782 | 0.041199 | 121.4035 | 121.3165 | 46.6599 | -121.4218 | 121.3119 | 121.4813 | 59.761 | -121.3531
2281.9531 | 121.4584 | -0.67749 | 120.8633 | -0.012589 | 0.17021 | 0.2049 | 0.0014612 | 0.12394 | 0.045784 | 0.060066 | -0.013123 | -0.0014933 | 0.07338 | 0.074018 | -0.20105 | -0.002839 | 120.7077 | 35.2203 | 45.9869 | 5.4108 | 120.8176 | -0.5722 | -0.65918 | 10.025 | 58.9279 | -0.71411 | 120.7672 | 120.8313 | -0.53558 | -0.58594 | 0.10529 | 0.01831 | -0.045776 | 35.8978 | 6.0883 | 6.0699 | -0.15564 | 0.14191 | 0.091553 | -0.09613 | 10.7025 | -0.036621 | -0.12817 | -0.032043 | 121.4951 | 121.3852 | 46.6644 | -121.5225 | 121.4447 | 121.5088 | 59.6054 | -121.4493
2283.7344 | 121.463 | -0.69122 | 120.8588 | -0.0049592 | 0.17128 | 0.20853 | 0.0044518 | 0.12565 | 0.037452 | 0.058357 | -0.020752 | -0.0023477 | 0.073593 | 0.073377 | -0.20447 | -0.00027561 | 120.6482 | 35.2615 | 45.9595 | 5.4337 | 120.7443 | -0.59052 | -0.66376 | 10.0983 | 58.9371 | -0.72784 | 120.7306 | 120.8908 | -0.55847 | -0.59509 | 0.10071 | 0.027466 | -0.11444 | 35.9528 | 6.1249 | 6.0974 | -0.21057 | 0.13275 | 0.09613 | -0.12817 | 10.7895 | -0.036621 | -0.13275 | 0.032043 | 121.4355 | 121.3394 | 46.6507 | -121.5225 | 121.4218 | 121.582 | 59.6283 | -121.4539
2285.5156 | 121.4401 | -0.68207 | 120.8267 | -0.012589 | 0.17128 | 0.20703 | 0.00060662 | 0.12629 | 0.043007 | 0.058785 | -0.0054932 | -0.0023477 | 0.072525 | 0.073805 | -0.20083 | -0.0032662 | 120.7031 | 35.3485 | 45.9915 | 5.4703 | 120.7809 | -0.58136 | -0.64087 | 10.2676 | 58.9325 | -0.737 | 120.7123 | 120.8679 | -0.54474 | -0.58594 | 0.10071 | 0.041199 | -0.045776 | 36.0306 | 6.1523 | 6.1111 | -0.1236 | 0.13733 | 0.096131 | -0.11444 | 10.9497 | -0.054932 | -0.15106 | 0.041199 | 121.463 | 121.3852 | 46.6736 | -121.4676 | 121.3943 | 121.55 | 59.6146 | -121.4127
2287.2969 | 121.5912 | -0.63629 | 120.7581 | 0.0026703 | 0.17085 | 0.2128 | 0.0050928 | 0.12544 | 0.034675 | 0.056221 | -0.0054932 | -0.0087563 | 0.072739 | 0.071882 | -0.20617 | -0.00070281 | 120.694 | 35.4584 | 46.051 | 5.5344 | 120.7397 | -0.55389 | -0.62256 | 10.4507 | 59.1156 | -0.5722 | 120.6757 | 120.7993 | -0.53101 | -0.52643 | 0.082398 | 0.013733 | -0.018311 | 36.0947 | 6.1707 | 6.1569 | -0.064087 | 0.10529 | 0.10986 | -0.082398 | 11.087 | 0.064087 | -0.045777 | 0.041198 | 121.376 | 121.3303 | 46.6873 | -121.3806 | 121.312 | 121.4355 | 59.7519 | -121.2845
2289.0781 | 121.4813 | -0.68665 | 120.8313 | -0.020218 | 0.1747 | 0.21024 | -0.0028112 | 0.12373 | 0.042152 | 0.05793 | -0.0054932 | -0.0023477 | 0.07338 | 0.074446 | -0.1987 | -0.002839 | 120.6345 | 35.3439 | 45.9045 | 5.5023 | 120.7901 | -0.58594 | -0.64545 | 10.4462 | 59.0012 | -0.75531 | 120.7352 | 120.8633 | -0.56305 | -0.56305 | 0.10071 | 0.041199 | -0.041199 | 36.0306 | 6.189 | 6.1478 | -0.19684 | 0.1236 | 0.1236 | -0.096131 | 11.1328 | -0.068664 | -0.19226 | 0.032043 | 121.4767 | 121.3211 | 46.5912 | -121.4767 | 121.4218 | 121.55 | 59.6878 | -121.3943
2290.7969 | 121.5637 | -0.6546 | 120.7947 | -0.012589 | 0.17491 | 0.21366 | 0.00082022 | 0.12501 | 0.036598 | 0.05793 | -0.0054932 | -0.0085427 | 0.073166 | 0.071455 | -0.20318 | -0.00048921 | 120.7214 | 35.582 | 46.0785 | 5.6259 | 120.7031 | -0.55847 | -0.63629 | 10.6018 | 59.3124 | -0.59052 | 120.6528 | 120.7947 | -0.53558 | -0.55389 | 0.09613 | 0.01831 | -0.091553 | 36.2366 | 6.2805 | 6.2622 | -0.073242 | 0.11902 | 0.10071 | -0.14191 | 11.2564 | 0.064087 | -0.036621 | 0 | 121.3577 | 121.376 | 46.7331 | -121.431 | 121.3074 | 121.4493 | 59.967 | -121.3486
2292.5781 | 121.5454 | -0.67291 | 120.7764 | -0.0049592 | 0.1732 | 0.21131 | 0.0029566 | 0.12821 | 0.038307 | 0.058357 | -0.0054932 | -0.0051247 | 0.072952 | 0.073591 | -0.20404 | -0.0019846 | 120.6802 | 35.495 | 45.9503 | 5.6076 | 120.7031 | -0.56305 | -0.63171 | 10.6796 | 59.3399 | -0.65002 | 120.6482 | 120.8038 | -0.53101 | -0.5722 | 0.10986 | 0.041199 | -0.073242 | 36.1679 | 6.2805 | 6.2393 | -0.09613 | 0.14191 | 0.10071 | -0.12817 | 11.3525 | 0.022889 | -0.077819 | 0.027466 | 121.376 | 121.3531 | 46.6232 | -121.4081 | 121.3211 | 121.4767 | 60.0128 | -121.3486
2294.3594 | 121.6049 | -0.6546 | 120.7901 | 0.0026703 | 0.17342 | 0.21216 | 0.0023156 | 0.12672 | 0.037666 | 0.056435 | -0.013123 | -0.0085427 | 0.071671 | 0.072523 | -0.20447 | -0.0024118 | 120.6619 | 35.5042 | 45.9503 | 5.6305 | 120.7123 | -0.5722 | -0.64545 | 10.7758 | 59.6329 | -0.62714 | 120.6619 | 120.8038 | -0.54474 | -0.5722 | 0.082397 | 0.009155 | -0.07782 | 36.1588 | 6.2851 | 6.2759 | -0.12817 | 0.10986 | 0.082397 | -0.12817 | 11.4304 | 0.027466 | -0.054931 | 0.013733 | 121.3669 | 121.3165 | 46.6049 | -121.4355 | 121.3165 | 121.4584 | 60.2875 | -121.3623
2296.1562 | 121.5729 | -0.66376 | 120.7489 | -0.0049592 | 0.17427 | 0.21024 | -0.0028112 | 0.12757 | 0.044929 | 0.06028 | -0.013123 | -0.0042703 | 0.071243 | 0.074873 | -0.20019 | -0.0039072 | 120.7352 | 35.5957 | 45.9457 | 5.7037 | 120.7077 | -0.5722 | -0.64087 | 10.9314 | 59.7977 | -0.63629 | 120.6299 | 120.7489 | -0.54932 | -0.5722 | 0.091552 | 0.022888 | -0.041198 | 36.2595 | 6.3675 | 6.3446 | -0.013733 | 0.11444 | 0.091552 | -0.11902 | 11.5952 | 0.027465 | -0.064087 | 0 | 121.3715 | 121.3989 | 46.6095 | -121.3898 | 121.2936 | 121.4127 | 60.4614 | -121.3211
2297.9375 | 121.4447 | -0.70953 | 120.7855 | -0.0049592 | 0.17983 | 0.21002 | 0.0012476 | 0.12714 | 0.045997 | 0.060494 | -0.0054932 | -0.0017069 | 0.076157 | 0.074018 | -0.19848 | -0.001771 | 120.6848 | 35.6369 | 45.813 | 5.6534 | 120.726 | -0.59967 | -0.65918 | 10.9772 | 59.935 | -0.737 | 120.6619 | 120.8084 | -0.58594 | -0.59967 | 0.10986 | 0.050354 | -0.059509 | 36.3464 | 6.3629 | 6.3126 | -0.10071 | 0.1236 | 0.10986 | -0.1236 | 11.6867 | -0.027466 | -0.13733 | 0.022889 | 121.4355 | 121.3943 | 46.5225 | -121.4447 | 121.3715 | 121.5179 | 60.6445 | -121.3852
2299.6406 | 121.4767 | -0.71869 | 120.7855 | -0.0049592 | 0.18175 | 0.21002 | 0.0033838 | 0.1265 | 0.046424 | 0.061775 | -0.0054932 | -0.0010659 | 0.075088 | 0.076795 | -0.20468 | -0.00113 | 120.6482 | 35.6461 | 45.8862 | 5.6946 | 120.7123 | -0.6134 | -0.68207 | 11.1237 | 60.1639 | -0.71869 | 120.6528 | 120.7718 | -0.57678 | -0.60425 | 0.10529 | 0.036621 | -0.073242 | 36.3647 | 6.4133 | 6.3766 | -0.13733 | 0.14191 | 0.11444 | -0.13275 | 11.8423 | 0 | -0.11444 | -0.013732 | 121.431 | 121.3669 | 46.6049 | -121.4676 | 121.3715 | 121.4905 | 60.8826 | -121.3898
2301.3438 | 121.55 | -0.6546 | 120.7443 | -0.0049592 | 0.17491 | 0.21301 | 0.00039302 | 0.12672 | 0.038734 | 0.061775 | -0.013123 | -0.0064065 | 0.073593 | 0.073591 | -0.20212 | -0.0030526 | 120.6802 | 35.7559 | 45.9412 | 5.7587 | 120.6711 | -0.55389 | -0.64087 | 11.3342 | 60.7544 | -0.62256 | 120.6253 | 120.7626 | -0.54474 | -0.56305 | 0.10071 | 0.013733 | -0.073242 | 36.4105 | 6.4133 | 6.3995 | -0.064087 | 0.10986 | 0.091553 | -0.11902 | 11.9888 | 0.032043 | -0.05951 | 0.01831 | 121.3257 | 121.3348 | 46.5958 | -121.3852 | 121.2799 | 121.4172 | 61.409 | -121.3074
2303.125 | 121.5729 | -0.66376 | 120.7901 | -0.020218 | 0.17384 | 0.21408 | 0.0016748 | 0.12693 | 0.037239 | 0.060066 | -0.0054932 | -0.0066201 | 0.075088 | 0.071668 | -0.20468 | 0.0027152 | 120.6299 | 35.7056 | 45.8633 | 5.7175 | 120.7031 | -0.5722 | -0.65002 | 11.4212 | 60.3836 | -0.67291 | 120.6573 | 120.7626 | -0.56763 | -0.5722 | 0.091552 | 0.013733 | -0.086975 | 36.3693 | 6.3812 | 6.3675 | -0.16022 | 0.09613 | 0.091552 | -0.13275 | 12.085 | -0.009156 | -0.10071 | -0.027466 | 121.3669 | 121.2936 | 46.5271 | -121.4401 | 121.3211 | 121.4264 | 61.0474 | -121.3623
2304.9062 | 121.5271 | -0.68665 | 120.7352 | -0.0049592 | 0.17683 | 0.21408 | 0.0014612 | 0.12821 | 0.038307 | 0.05793 | -0.0054932 | -0.0057657 | 0.074448 | 0.072737 | -0.20382 | -0.00070281 | 120.6665 | 35.7971 | 45.9183 | 5.7632 | 120.694 | -0.56763 | -0.63171 | 11.5494 | 60.4248 | -0.68207 | 120.6299 | 120.7489 | -0.54932 | -0.5722 | 0.11902 | 0.054932 | -0.041198 | 36.4838 | 6.4499 | 6.395 | -0.068664 | 0.13733 | 0.11444 | -0.10528 | 12.236 | 0.004578 | -0.10986 | 0.013733 | 121.3806 | 121.3531 | 46.6049 | -121.3669 | 121.3165 | 121.4355 | 61.1115 | -121.3074
2306.6875 | 121.4859 | -0.70496 | 120.7764 | -0.012589 | 0.17769 | 0.2175 | 0.0044518 | 0.12821 | 0.043861 | 0.058144 | 0.0021363 | -0.0025613 | 0.072952 | 0.074018 | -0.20126 | -0.0019846 | 120.5933 | 35.733 | 45.8176 | 5.7358 | 120.726 | -0.61798 | -0.69122 | 11.6547 | 60.347 | -0.78278 | 120.6985 | 120.8038 | -0.59052 | -0.61798 | 0.086975 | 0.013733 | -0.050354 | 36.438 | 6.4407 | 6.427 | -0.1831 | 0.11444 | 0.086975 | -0.07782 | 12.3596 | -0.07782 | -0.1648 | 0.027466 | 121.431 | 121.2982 | 46.5225 | -121.4676 | 121.4035 | 121.5088 | 61.0519 | -121.3943
2308.4062 | 121.4447 | -0.71411 | 120.7855 | -0.012589 | 0.18132 | 0.21665 | 0.0012476 | 0.13035 | 0.047065 | 0.062416 | -0.0054932 | -0.0046975 | 0.075302 | 0.075514 | -0.20126 | -0.0019846 | 120.6436 | 35.8521 | 45.8633 | 5.7953 | 120.6848 | -0.60883 | -0.66376 | 11.8332 | 60.5255 | -0.71869 | 120.6619 | 120.7855 | -0.5722 | -0.61798 | 0.10529 | 0.050354 | -0.10071 | 36.5662 | 6.5094 | 6.459 | -0.14191 | 0.14191 | 0.09613 | -0.1236 | 12.5473 | -0.004578 | -0.10071 | 0 | 121.3989 | 121.3577 | 46.5775 | -121.4493 | 121.376 | 121.4996 | 61.2396 | -121.4035
2310.1875 | 121.5225 | -0.67291 | 120.726 | -0.012589 | 0.17641 | 0.21729 | -0.0017432 | 0.12928 | 0.040016 | 0.062416 | -0.0054932 | -0.0076883 | 0.074448 | 0.074018 | -0.2034 | 0.001647 | 120.6757 | 35.9482 | 45.8954 | 5.8365 | 120.6482 | -0.56763 | -0.63171 | 11.9843 | 60.7224 | -0.64087 | 120.6207 | 120.726 | -0.54474 | -0.59509 | 0.10529 | 0.041199 | -0.07782 | 36.6211 | 6.5094 | 6.4682 | -0.050354 | 0.12817 | 0.07782 | -0.10528 | 12.6572 | 0.032044 | -0.045776 | 0 | 121.3211 | 121.3486 | 46.5683 | -121.3577 | 121.2936 | 121.3989 | 61.3953 | -121.3211
2311.9688 | 121.5637 | -0.67291 | 120.7169 | 0.0026703 | 0.1747 | 0.21835 | 0.00082022 | 0.13078 | 0.037025 | 0.059426 | 0.0021363 | -0.0072611 | 0.073166 | 0.072737 | -0.20361 | 0.00036539 | 120.6711 | 36.026 | 45.8862 | 5.8685 | 120.6665 | -0.57678 | -0.64087 | 12.1033 | 60.9375 | -0.62256 | 120.5933 | 120.726 | -0.54474 | -0.59967 | 0.096131 | 0.032044 | -0.050354 | 36.6989 | 6.5414 | 6.5094 | -0.045776 | 0.12817 | 0.073243 | -0.1236 | 12.7762 | 0.050354 | -0.022889 | 0.009155 | 121.3394 | 121.344 | 46.5591 | -121.3577 | 121.2662 | 121.3989 | 61.6104 | -121.3165
2313.6875 | 121.5134 | -0.70038 | 120.7535 | -0.0049592 | 0.17961 | 0.21964 | 0.002102 | 0.12907 | 0.04087 | 0.060066 | 0.0021363 | -0.0072611 | 0.074875 | 0.073805 | -0.20233 | 0.0010062 | 120.6253 | 35.8978 | 45.7489 | 5.8228 | 120.6894 | -0.59052 | -0.65002 | 12.1902 | 60.8643 | -0.69122 | 120.639 | 120.7443 | -0.56763 | -0.60883 | 0.10986 | 0.050354 | -0.064087 | 36.5982 | 6.5231 | 6.4728 | -0.12817 | 0.13275 | 0.091552 | -0.11444 | 12.8906 | 0.009155 | -0.082397 | -0.009155 | 121.3898 | 121.3257 | 46.4493 | -121.4035 | 121.3394 | 121.4447 | 61.5646 | -121.3623
2315.4688 | 121.5546 | -0.68207 | 120.7123 | -0.0049592 | 0.18218 | 0.21771 | -0.00067498 | 0.12949 | 0.044929 | 0.061562 | -0.013123 | -0.0049111 | 0.077225 | 0.075727 | -0.20361 | -0.0030526 | 120.6802 | 35.9711 | 45.7489 | 5.9143 | 120.6711 | -0.60425 | -0.64545 | 12.4008 | 60.965 | -0.64545 | 120.6162 | 120.7077 | -0.54932 | -0.59052 | 0.07782 | 0.036621 | -0.041198 | 36.6531 | 6.5964 | 6.5598 | -0.032043 | 0.13275 | 0.091553 | -0.09613 | 13.0829 | 0.036621 | -0.054932 | -0.004577 | 121.3531 | 121.3623 | 46.431 | -121.3577 | 121.2982 | 121.3898 | 61.647 | -121.3028
2317.1875 | 121.4905 | -0.71869 | 120.7443 | -0.0049592 | 0.18388 | 0.21835 | 0.0023156 | 0.13099 | 0.040016 | 0.058998 | -0.0054932 | -0.0064065 | 0.075516 | 0.074232 | -0.20468 | -0.0021982 | 120.6573 | 36.0489 | 45.6665 | 5.9189 | 120.6482 | -0.56763 | -0.64545 | 12.4512 | 61.1252 | -0.62714 | 120.5978 | 120.726 | -0.54932 | -0.57678 | 0.15106 | 0.073242 | -0.096131 | 36.7676 | 6.6376 | 6.5643 | -0.086975 | 0.16937 | 0.14191 | -0.14649 | 13.1699 | 0.091553 | -0.050354 | -0.018311 | 121.3669 | 121.376 | 46.3852 | -121.3898 | 121.3165 | 121.4447 | 61.8439 | -121.3211
2318.9531 | 121.5134 | -0.69122 | 120.7397 | -0.0049592 | 0.18004 | 0.22049 | 0.00039302 | 0.13035 | 0.041725 | 0.059853 | -0.020752 | -0.0074747 | 0.073166 | 0.07295 | -0.20169 | -0.0019846 | 120.6299 | 36.058 | 45.639 | 5.8914 | 120.6757 | -0.59052 | -0.6546 | 12.5153 | 61.1023 | -0.67749 | 120.6299 | 120.7169 | -0.5722 | -0.60425 | 0.10071 | 0.036621 | -0.064087 | 36.7493 | 6.5826 | 6.546 | -0.10986 | 0.11902 | 0.086975 | -0.10986 | 13.2065 | 0.013733 | -0.073242 | -0.022888 | 121.3669 | 121.3211 | 46.3303 | -121.3943 | 121.3211 | 121.4081 | 61.7935 | -121.344
2320.7344 | 121.5271 | -0.71869 | 120.7214 | -0.012589 | 0.1841 | 0.21942 | 0.0050928 | 0.13078 | 0.039161 | 0.061775 | -0.020752 | -0.0059793 | 0.076797 | 0.075086 | -0.20404 | -0.0021982 | 120.6985 | 36.1176 | 45.6848 | 5.9326 | 120.6802 | -0.59509 | -0.67291 | 12.6617 | 61.1801 | -0.62256 | 120.5887 | 120.7169 | -0.54016 | -0.58136 | 0.1236 | 0.045776 | -0.041199 | 36.8362 | 6.6513 | 6.6055 | -0.022889 | 0.17853 | 0.13733 | -0.13275 | 13.3804 | 0.09613 | -0.041199 | -0.004578 | 121.3989 | 121.4172 | 46.4035 | -121.3943 | 121.3074 | 121.4355 | 61.8988 | -121.3028
2322.5 | 121.4905 | -0.72327 | 120.726 | -0.0049592 | 0.18602 | 0.22177 | 0.0014612 | 0.13078 | 0.047493 | 0.064339 | -0.020752 | -0.0025613 | 0.074875 | 0.076368 | -0.20169 | -0.0039072 | 120.5887 | 36.026 | 45.4926 | 5.8823 | 120.7169 | -0.63629 | -0.72327 | 12.6434 | 60.9329 | -0.78278 | 120.6345 | 120.7626 | -0.58594 | -0.62256 | 0.086975 | 0 | -0.009155 | 36.7493 | 6.6055 | 6.6055 | -0.13733 | 0.13733 | 0.10071 | -0.091553 | 13.3667 | -0.059509 | -0.16022 | 0.036621 | 121.4401 | 121.312 | 46.2158 | -121.4493 | 121.3577 | 121.4859 | 61.6562 | -121.3486
2324.2188 | 121.5271 | -0.63629 | 120.7718 | -0.020218 | 0.18367 | 0.22113 | 0.00039302 | 0.12907 | 0.044929 | 0.063271 | -0.0054932 | -0.0021341 | 0.077225 | 0.077436 | -0.20297 | -0.0032662 | 120.6436 | 36.1496 | 45.52 | 5.9555 | 120.7397 | -0.55847 | -0.64545 | 12.7945 | 61.0886 | -0.70038 | 120.7077 | 120.8038 | -0.53558 | -0.55389 | 0.07782 | -0.009155 | -0.032044 | 36.7859 | 6.5918 | 6.601 | -0.12817 | 0.10071 | 0.082398 | -0.064087 | 13.4308 | -0.064086 | -0.14648 | 0.032043 | 121.376 | 121.2799 | 46.1563 | -121.4172 | 121.344 | 121.4401 | 61.7249 | -121.3257
2326 | 121.55 | -0.51727 | 120.8542 | 0.0026703 | 0.18388 | 0.22241 | 0.0014612 | 0.13163 | 0.044075 | 0.063271 | -0.013123 | -0.0053385 | 0.076157 | 0.075727 | -0.20062 | 0.001647 | 120.7855 | 36.3419 | 45.7489 | 6.1203 | 120.8267 | -0.44861 | -0.50812 | 13.0829 | 61.2808 | -0.50812 | 120.7535 | 120.8725 | -0.41199 | -0.43945 | 0.068665 | 0.009155 | -0.027466 | 36.8591 | 6.6376 | 6.6284 | -0.068665 | 0.10529 | 0.07782 | -0.10071 | 13.6002 | 0.009155 | -0.068665 | 0.018311 | 121.344 | 121.3028 | 46.2662 | -121.3623 | 121.2708 | 121.3898 | 61.7981 | -121.2936
2327.7656 | 121.4172 | -0.75531 | 120.7443 | -0.012589 | 0.19029 | 0.22434 | 0.00552 | 0.13056 | 0.042152 | 0.066262 | -0.020752 | -0.0049111 | 0.074661 | 0.077009 | -0.20532 | -0.00027561 | 120.5704 | 36.2778 | 45.6757 | 5.9875 | 120.6482 | -0.62256 | -0.69122 | 12.886 | 60.672 | -0.75989 | 120.5933 | 120.7443 | -0.6134 | -0.64545 | 0.13275 | 0.064087 | -0.096131 | 37.0331 | 6.7429 | 6.6788 | -0.17395 | 0.14191 | 0.10986 | -0.15106 | 13.6414 | -0.004578 | -0.11444 | 0 | 121.4035 | 121.3257 | 46.431 | -121.4355 | 121.3486 | 121.4996 | 61.4273 | -121.3898
2329.5312 | 121.4172 | -0.75531 | 120.7352 | -0.0049592 | 0.19328 | 0.22049 | 0.0040246 | 0.12992 | 0.04792 | 0.066048 | -0.0054932 | -0.0025613 | 0.080643 | 0.077864 | -0.2019 | -0.00091641 | 120.5475 | 36.2457 | 45.6528 | 5.9875 | 120.6665 | -0.64545 | -0.71411 | 12.9501 | 60.5209 | -0.82398 | 120.6207 | 120.7535 | -0.63171 | -0.64545 | 0.10986 | 0.041199 | -0.068664 | 37.001 | 6.7429 | 6.7017 | -0.18768 | 0.1236 | 0.10986 | -0.11444 | 13.7054 | -0.068665 | -0.17853 | 0.018311 | 121.4218 | 121.3028 | 46.4081 | -121.4493 | 121.376 | 121.5088 | 61.2762 | -121.3806
2331.2656 | 121.5088 | -0.6958 | 120.7031 | -0.0049592 | 0.18858 | 0.22135 | 0.00082022 | 0.12971 | 0.04322 | 0.06733 | -0.0054932 | -0.0051247 | 0.077866 | 0.077223 | -0.20083 | 0.0010062 | 120.5383 | 36.3419 | 45.5292 | 6.015 | 120.6619 | -0.64087 | -0.70953 | 13.0463 | 60.2234 | -0.78278 | 120.6345 | 120.726 | -0.60883 | -0.64545 | 0.054932 | -0.013733 | -0.041199 | 37.0377 | 6.7108 | 6.7245 | -0.16479 | 0.086975 | 0.050354 | -0.068665 | 13.7421 | -0.086975 | -0.13733 | 0.022888 | 121.3577 | 121.2341 | 46.225 | -121.4127 | 121.3303 | 121.4218 | 60.9192 | -121.3486
2333.0469 | 121.5454 | -0.70496 | 120.6619 | -0.012589 | 0.18773 | 0.2254 | -0.0019568 | 0.13056 | 0.045143 | 0.065621 | -0.0054932 | -0.0019205 | 0.077438 | 0.077223 | -0.20169 | -6.2012e-05 | 120.5429 | 36.4151 | 45.5109 | 6.0333 | 120.6482 | -0.63629 | -0.70496 | 13.1332 | 60.0037 | -0.72784 | 120.6024 | 120.7077 | -0.58136 | -0.63171 | 0.068664 | 0 | -0.013733 | 37.1201 | 6.7383 | 6.7383 | -0.11902 | 0.1236 | 0.073242 | -0.059509 | 13.8382 | -0.022888 | -0.09613 | 0.045777 | 121.3531 | 121.2479 | 46.2158 | -121.3669 | 121.3074 | 121.4127 | 60.7086 | -121.2936
2334.75 | 121.463 | -0.74158 | 120.6848 | -0.0049592 | 0.19371 | 0.22476 | 0.0031702 | 0.13163 | 0.044075 | 0.064125 | -0.0054932 | -0.0036295 | 0.07872 | 0.075727 | -0.20062 | -6.2012e-05 | 120.5246 | 36.4426 | 45.3827 | 6.0654 | 120.6436 | -0.66834 | -0.737 | 13.1378 | 59.7656 | -0.76904 | 120.6024 | 120.7352 | -0.60883 | -0.65002 | 0.073242 | 0.004577 | -0.041198 | 37.1841 | 6.8069 | 6.8024 | -0.16022 | 0.13275 | 0.091553 | -0.082397 | 13.8794 | -0.027466 | -0.11902 | 0.050354 | 121.3852 | 121.2662 | 46.1243 | -121.4218 | 121.344 | 121.4767 | 60.5072 | -121.3348
2336.5312 | 121.3943 | -0.75989 | 120.7077 | -0.020218 | 0.19243 | 0.2237 | 0.001034 | 0.1327 | 0.046424 | 0.066475 | -0.0054932 | -0.0029885 | 0.075088 | 0.078718 | -0.20105 | -0.0015572 | 120.5383 | 36.4883 | 45.0348 | 6.1066 | 120.6436 | -0.64087 | -0.73242 | 13.2294 | 59.5734 | -0.81024 | 120.5795 | 120.7718 | -0.6134 | -0.65918 | 0.11902 | 0.027466 | -0.064087 | 37.2482 | 6.8665 | 6.839 | -0.16937 | 0.14648 | 0.10071 | -0.12817 | 13.9893 | -0.050354 | -0.15106 | 0.064087 | 121.4035 | 121.2982 | 45.7947 | -121.4401 | 121.3394 | 121.5317 | 60.3333 | -121.3669
2338.3125 | 121.4539 | -0.76446 | 120.7031 | -0.0049592 | 0.192 | 0.22669 | 0.0040246 | 0.13483 | 0.039802 | 0.065193 | -0.013123 | -0.0087563 | 0.077225 | 0.074232 | -0.20596 | 0.0014334 | 120.5795 | 36.6806 | 45.0027 | 6.2027 | 120.5658 | -0.6134 | -0.6958 | 13.3667 | 59.5367 | -0.66376 | 120.5429 | 120.726 | -0.57678 | -0.62256 | 0.15106 | 0.068664 | -0.13733 | 37.4451 | 6.9672 | 6.8985 | -0.1236 | 0.18768 | 0.14191 | -0.16022 | 14.1312 | 0.10071 | -0.041198 | 0.022888 | 121.3303 | 121.344 | 45.7672 | -121.3989 | 121.3074 | 121.4905 | 60.3012 | -121.3257
2340.0156 | 121.431 | -0.75531 | 120.7169 | 0.0026703 | 0.19328 | 0.22775 | 0.0042382 | 0.13313 | 0.044502 | 0.064339 | -0.0054932 | -0.0040567 | 0.078934 | 0.073805 | -0.20532 | -0.00048921 | 120.5154 | 36.5982 | 44.9249 | 6.1432 | 120.6573 | -0.6546 | -0.71411 | 13.3118 | 59.2758 | -0.76904 | 120.6024 | 120.7443 | -0.61798 | -0.65002 | 0.10071 | 0.041199 | -0.059509 | 37.3535 | 6.8985 | 6.8573 | -0.20142 | 0.13733 | 0.10529 | -0.11444 | 14.0671 | -0.013733 | -0.11902 | 0.027466 | 121.4127 | 121.2708 | 45.6802 | -121.431 | 121.3577 | 121.4996 | 60.0311 | -121.3669
2341.7812 | 121.4081 | -0.74158 | 120.7077 | -0.012589 | 0.1982 | 0.22583 | -0.00024778 | 0.13355 | 0.049202 | 0.067116 | -0.0054932 | -0.0025613 | 0.076797 | 0.077009 | -0.20147 | -0.00113 | 120.6162 | 36.7126 | 45.0119 | 6.2347 | 120.6436 | -0.6134 | -0.70953 | 13.4171 | 59.0927 | -0.737 | 120.5978 | 120.7443 | -0.60425 | -0.63629 | 0.12817 | 0.032043 | -0.064087 | 37.4542 | 6.9763 | 6.9443 | -0.091553 | 0.13733 | 0.10529 | -0.10986 | 14.1586 | 0.004577 | -0.10071 | 0.036621 | 121.3852 | 121.3577 | 45.7535 | -121.4172 | 121.3394 | 121.4859 | 59.8343 | -121.344
2343.5469 | 121.431 | -0.75073 | 120.726 | -0.012589 | 0.19692 | 0.22882 | 0.003811 | 0.13227 | 0.045997 | 0.065621 | 0.0097658 | -0.0059793 | 0.078506 | 0.076582 | -0.20425 | 0.00057899 | 120.4926 | 36.6714 | 44.0643 | 6.1935 | 120.6711 | -0.6546 | -0.71869 | 13.3713 | 58.7219 | -0.77362 | 120.607 | 120.7535 | -0.62714 | -0.6546 | 0.09613 | 0.032043 | -0.054931 | 37.4222 | 6.9443 | 6.9122 | -0.23346 | 0.1236 | 0.09613 | -0.11902 | 14.122 | -0.022889 | -0.11902 | 0.027466 | 121.4218 | 121.2433 | 44.8151 | -121.4447 | 121.3577 | 121.5042 | 59.4727 | -121.3806
2345.3125 | 121.5363 | -0.70038 | 120.6573 | -0.0049592 | 0.19328 | 0.22989 | 0.0016748 | 0.13078 | 0.039802 | 0.066475 | -0.0054932 | -0.0091837 | 0.074875 | 0.073164 | -0.20254 | 0.00057899 | 120.5841 | 36.9003 | 44.632 | 6.2851 | 120.5795 | -0.60425 | -0.68665 | 13.504 | 58.5388 | -0.63171 | 120.5475 | 120.6894 | -0.58136 | -0.62256 | 0.09613 | 0.013732 | -0.07782 | 37.6007 | 6.9855 | 6.9717 | -0.073243 | 0.11902 | 0.077819 | -0.10986 | 14.2044 | 0.068664 | -0.009155 | 0.032043 | 121.2799 | 121.2845 | 45.3323 | -121.344 | 121.2479 | 121.3898 | 59.2392 | -121.2799
2347.0781 | 121.4447 | -0.74158 | 120.6848 | -0.012589 | 0.1982 | 0.2269 | 0.0018884 | 0.13398 | 0.047706 | 0.064766 | -0.013123 | -0.0010659 | 0.077652 | 0.075514 | -0.20254 | 0.00079259 | 120.5063 | 36.7538 | 44.7281 | 6.2302 | 120.6345 | -0.65918 | -0.72784 | 13.4308 | 58.2504 | -0.77362 | 120.5933 | 120.7123 | -0.62256 | -0.6546 | 0.082397 | 0.013733 | -0.050354 | 37.4954 | 6.9717 | 6.958 | -0.17853 | 0.11902 | 0.086975 | -0.091552 | 14.1724 | -0.032044 | -0.11902 | 0.027466 | 121.376 | 121.2479 | 45.4697 | -121.4127 | 121.3348 | 121.4539 | 58.992 | -121.3394
2348.7812 | 121.4584 | -0.737 | 120.6985 | -0.012589 | 0.20268 | 0.22775 | 0.0018884 | 0.13548 | 0.048347 | 0.066689 | -0.0054932 | -0.0025613 | 0.07872 | 0.076368 | -0.20212 | -0.0013436 | 120.5292 | 36.8042 | 45.3003 | 6.2622 | 120.6436 | -0.65002 | -0.72327 | 13.4995 | 58.0994 | -0.74158 | 120.6024 | 120.7397 | -0.62256 | -0.6546 | 0.086976 | 0.013733 | -0.054931 | 37.5412 | 6.9992 | 6.9855 | -0.16937 | 0.11444 | 0.082398 | -0.09613 | 14.2365 | -0.004577 | -0.086975 | 0.041199 | 121.3806 | 121.2662 | 46.0373 | -121.4218 | 121.3394 | 121.4767 | 58.8364 | -121.3531
2350.5469 | 121.4218 | -0.7782 | 120.6802 | 0.0026703 | 0.19884 | 0.22904 | 0.0044518 | 0.13526 | 0.045997 | 0.066902 | -0.013123 | -0.0059793 | 0.079788 | 0.075514 | -0.20468 | -0.00048921 | 120.4742 | 36.8088 | 44.7922 | 6.2485 | 120.6116 | -0.6546 | -0.71869 | 13.4491 | 57.8064 | -0.78278 | 120.5841 | 120.6894 | -0.63629 | -0.68207 | 0.1236 | 0.059509 | -0.068665 | 37.587 | 7.0267 | 6.9672 | -0.20599 | 0.14191 | 0.09613 | -0.096131 | 14.2273 | -0.004578 | -0.10071 | 0.009155 | 121.3898 | 121.2524 | 45.5704 | -121.3989 | 121.3623 | 121.4676 | 58.5846 | -121.3623
2352.3281 | 121.4264 | -0.74616 | 120.6619 | -0.012589 | 0.19606 | 0.22605 | 0.0029566 | 0.13462 | 0.048561 | 0.066475 | 0.0021363 | -0.0055521 | 0.076584 | 0.076795 | -0.20083 | -0.00070281 | 120.4788 | 36.8317 | 44.9295 | 6.2714 | 120.6528 | -0.61798 | -0.72327 | 13.5315 | 57.5958 | -0.80109 | 120.575 | 120.7169 | -0.61798 | -0.64087 | 0.12817 | 0.022888 | -0.009155 | 37.5778 | 7.0175 | 6.9946 | -0.1831 | 0.12817 | 0.10529 | -0.086975 | 14.2776 | -0.054931 | -0.16022 | 0.054932 | 121.3989 | 121.225 | 45.6757 | -121.3852 | 121.3211 | 121.463 | 58.342 | -121.3028
2354.0469 | 121.5317 | -0.68665 | 120.639 | -0.012589 | 0.1967 | 0.22861 | -3.4178e-05 | 0.13633 | 0.042579 | 0.069252 | -0.013123 | -0.0066201 | 0.076797 | 0.077436 | -0.20276 | 0.00079259 | 120.5704 | 36.9781 | 45.2637 | 6.3583 | 120.5841 | -0.59967 | -0.66834 | 13.7192 | 57.6233 | -0.65918 | 120.5475 | 120.6711 | -0.5722 | -0.60883 | 0.086976 | 0.018311 | -0.054932 | 37.6648 | 7.045 | 7.0267 | -0.068664 | 0.11444 | 0.07782 | -0.091553 | 14.4058 | 0.027466 | -0.050354 | 0.032044 | 121.2708 | 121.257 | 45.9503 | -121.3074 | 121.2341 | 121.3577 | 58.3099 | -121.2479
2355.8281 | 121.4035 | -0.74158 | 120.694 | -0.012589 | 0.20119 | 0.23053 | -0.00046138 | 0.13313 | 0.047706 | 0.066475 | -0.013123 | -0.0036295 | 0.077011 | 0.076368 | -0.20147 | -0.00048921 | 120.4605 | 36.8134 | 45.3552 | 6.2485 | 120.6436 | -0.65002 | -0.737 | 13.6826 | 57.193 | -0.81024 | 120.5841 | 120.7214 | -0.63171 | -0.6546 | 0.091553 | 0.004577 | -0.050354 | 37.5549 | 6.9901 | 6.9855 | -0.23346 | 0.10986 | 0.086975 | -0.10986 | 14.4241 | -0.068665 | -0.15564 | 0.027466 | 121.3852 | 121.2021 | 46.0968 | -121.431 | 121.3257 | 121.463 | 57.9346 | -121.3486
2357.5469 | 121.4859 | -0.71411 | 120.6253 | -0.012589 | 0.19649 | 0.23224 | -3.4178e-05 | 0.13633 | 0.045143 | 0.065621 | -0.013123 | -0.0076883 | 0.077866 | 0.077009 | -0.20382 | 0.00079259 | 120.5795 | 37.001 | 45.5841 | 6.3858 | 120.5704 | -0.60883 | -0.68207 | 13.8748 | 57.2205 | -0.65002 | 120.5383 | 120.6665 | -0.57678 | -0.60425 | 0.10529 | 0.032043 | -0.054931 | 37.7151 | 7.0999 | 7.0679 | -0.045776 | 0.13733 | 0.10986 | -0.086975 | 14.5889 | 0.064087 | -0.045776 | 0.041199 | 121.2845 | 121.2936 | 46.2982 | -121.3074 | 121.2524 | 121.3806 | 57.9346 | -121.2296
2359.3125 | 121.4401 | -0.71869 | 120.7077 | -0.012589 | 0.20076 | 0.22968 | 0.0033838 | 0.13462 | 0.047279 | 0.064766 | 0.0021363 | -0.00063872 | 0.077225 | 0.077223 | -0.20212 | -6.2012e-05 | 120.5017 | 36.9186 | 45.694 | 6.2851 | 120.6253 | -0.64087 | -0.71411 | 13.8199 | 56.8817 | -0.77362 | 120.5795 | 120.7535 | -0.59967 | -0.65002 | 0.07782 | 0.004578 | -0.082398 | 37.6373 | 7.0038 | 6.9992 | -0.20599 | 0.11902 | 0.068665 | -0.12817 | 14.5386 | -0.054932 | -0.1236 | 0.045776 | 121.344 | 121.2204 | 46.4127 | -121.4218 | 121.2982 | 121.4722 | 57.6004 | -121.3577
2361.0938 | 121.4722 | -0.74158 | 120.6116 | -0.0049592 | 0.19521 | 0.23032 | 0.0012476 | 0.13526 | 0.041511 | 0.064339 | -0.0054932 | -0.0079019 | 0.077652 | 0.0753 | -0.20639 | 0.00057899 | 120.4834 | 36.937 | 45.8038 | 6.2668 | 120.5704 | -0.64545 | -0.71869 | 13.8748 | 56.6483 | -0.74158 | 120.5063 | 120.6665 | -0.62256 | -0.64087 | 0.09613 | 0.022888 | -0.041198 | 37.6785 | 7.0084 | 6.9855 | -0.12817 | 0.11902 | 0.10071 | -0.10528 | 14.6164 | 0 | -0.10071 | 0.054932 | 121.312 | 121.225 | 46.5454 | -121.3303 | 121.2479 | 121.4081 | 57.3898 | -121.2524
2362.8594 | 121.3989 | -0.7782 | 120.6665 | -0.020218 | 0.19948 | 0.22946 | 0.002102 | 0.1374 | 0.044288 | 0.064125 | -0.013123 | -0.0072611 | 0.076584 | 0.074873 | -0.20404 | -0.00091641 | 120.5383 | 37.0651 | 45.9366 | 6.3309 | 120.5521 | -0.63629 | -0.71411 | 13.9984 | 56.5979 | -0.73242 | 120.5246 | 120.6665 | -0.62714 | -0.66834 | 0.14191 | 0.064087 | -0.11444 | 37.8433 | 7.1091 | 7.045 | -0.12817 | 0.15106 | 0.10986 | -0.14191 | 14.7766 | 0.045776 | -0.064087 | 0 | 121.3303 | 121.3165 | 46.7148 | -121.3806 | 121.3028 | 121.4447 | 57.3761 | -121.3348
2364.5781 | 121.3898 | -0.75531 | 120.6573 | -0.0049592 | 0.20097 | 0.2284 | -3.4178e-05 | 0.13505 | 0.051979 | 0.067543 | -0.0054932 | -0.0021341 | 0.077652 | 0.076368 | -0.19977 | 0.00057899 | 120.5475 | 37.0056 | 45.9641 | 6.2759 | 120.5887 | -0.64545 | -0.74158 | 14.0717 | 56.3782 | -0.76904 | 120.5383 | 120.6802 | -0.62714 | -0.67291 | 0.10986 | 0.013733 | -0.068665 | 37.7609 | 7.0312 | 7.0175 | -0.10986 | 0.12817 | 0.082397 | -0.11902 | 14.827 | -0.013733 | -0.09613 | 0.022888 | 121.344 | 121.3028 | 46.7194 | -121.3989 | 121.2936 | 121.4355 | 57.1335 | -121.3303
2366.3594 | 121.4722 | -0.737 | 120.607 | -0.012589 | 0.19756 | 0.23117 | 0.0048792 | 0.13419 | 0.042152 | 0.066048 | -0.0054932 | -0.0083291 | 0.078506 | 0.076582 | -0.20575 | -0.0015572 | 120.5704 | 37.1109 | 46.0876 | 6.3446 | 120.5704 | -0.62256 | -0.70038 | 14.1678 | 56.2546 | -0.67291 | 120.5154 | 120.6482 | -0.60425 | -0.62714 | 0.11444 | 0.036622 | -0.036621 | 37.8479 | 7.0816 | 7.045 | -0.036621 | 0.13275 | 0.10986 | -0.091553 | 14.9048 | 0.064087 | -0.045777 | 0.041198 | 121.3074 | 121.3074 | 46.8246 | -121.3074 | 121.2524 | 121.3852 | 56.9916 | -121.2341
2368.0625 | 121.4081 | -0.75989 | 120.6573 | -0.0049592 | 0.20076 | 0.23032 | 0.0016748 | 0.13847 | 0.044929 | 0.066902 | -0.013123 | -0.0068337 | 0.077225 | 0.0753 | -0.20233 | -0.00091641 | 120.4651 | 37.0285 | 46.0007 | 6.2851 | 120.5978 | -0.66376 | -0.75073 | 14.1129 | 55.957 | -0.81024 | 120.5704 | 120.6711 | -0.65002 | -0.68665 | 0.096131 | 0.009156 | -0.05951 | 37.7884 | 7.045 | 7.0358 | -0.19226 | 0.10986 | 0.073242 | -0.086975 | 14.8727 | -0.050354 | -0.1236 | 0.013733 | 121.3577 | 121.225 | 46.7606 | -121.4081 | 121.3303 | 121.431 | 56.7169 | -121.344
2369.8281 | 121.431 | -0.76446 | 120.6528 | -0.027847 | 0.20226 | 0.22946 | 0.0029566 | 0.13569 | 0.04792 | 0.066048 | -0.013123 | -0.0025613 | 0.080643 | 0.077009 | -0.20233 | -0.00091641 | 120.4834 | 37.0468 | 46.0419 | 6.2942 | 120.5978 | -0.66834 | -0.76446 | 14.2136 | 55.8014 | -0.80109 | 120.5429 | 120.6985 | -0.62714 | -0.6546 | 0.09613 | 0 | -0.054932 | 37.8113 | 7.0587 | 7.0587 | -0.16937 | 0.13733 | 0.10986 | -0.10986 | 14.978 | -0.036621 | -0.14648 | 0.045776 | 121.3623 | 121.2479 | 46.8063 | -121.4172 | 121.3074 | 121.463 | 56.5659 | -121.3074
2371.5469 | 121.4172 | -0.76446 | 120.6573 | -0.020218 | 0.20439 | 0.2284 | 0.0029566 | 0.13654 | 0.048133 | 0.067757 | -0.0054932 | -0.0038431 | 0.078506 | 0.078504 | -0.20276 | -0.0021982 | 120.488 | 37.1475 | 46.0693 | 6.3263 | 120.6116 | -0.65918 | -0.75073 | 14.2914 | 55.6183 | -0.7782 | 120.5521 | 120.6802 | -0.6134 | -0.65918 | 0.10528 | 0.013733 | -0.045777 | 37.912 | 7.0908 | 7.077 | -0.16937 | 0.15106 | 0.10528 | -0.10529 | 15.0558 | -0.013733 | -0.11902 | 0.022888 | 121.376 | 121.2524 | 46.8338 | -121.4081 | 121.3165 | 121.4447 | 56.3828 | -121.3165
2373.3125 | 121.3623 | -0.76904 | 120.6436 | 0.0026703 | 0.20247 | 0.23224 | 0.002102 | 0.1359 | 0.043007 | 0.067543 | -0.0054932 | -0.0072611 | 0.075516 | 0.076582 | -0.20233 | 0.00079259 | 120.5063 | 37.2757 | 46.1975 | 6.3995 | 120.5383 | -0.64545 | -0.70496 | 14.3372 | 55.4077 | -0.75989 | 120.4926 | 120.6573 | -0.6134 | -0.66376 | 0.1236 | 0.064087 | -0.10529 | 38.0447 | 7.1686 | 7.1045 | -0.13733 | 0.15564 | 0.10529 | -0.15106 | 15.1062 | 0.009155 | -0.096131 | 0.013733 | 121.3074 | 121.2753 | 46.9666 | -121.3486 | 121.2616 | 121.4264 | 56.1768 | -121.3074
2375.0156 | 121.4996 | -0.72784 | 120.5887 | -0.012589 | 0.19948 | 0.23224 | 0.0016748 | 0.13548 | 0.04087 | 0.065621 | -0.013123 | -0.0079019 | 0.077652 | 0.074873 | -0.20596 | -6.2012e-05 | 120.52 | 37.3261 | 46.2524 | 6.4224 | 120.5429 | -0.62714 | -0.71411 | 14.4058 | 55.2292 | -0.66834 | 120.4926 | 120.6253 | -0.58594 | -0.63629 | 0.10071 | 0.013733 | -0.045776 | 38.0539 | 7.1503 | 7.1365 | -0.068664 | 0.14191 | 0.091552 | -0.09613 | 15.1337 | 0.059509 | -0.032043 | 0.036621 | 121.2708 | 121.2479 | 46.9803 | -121.3028 | 121.2204 | 121.3531 | 55.957 | -121.225
2376.7969 | 121.4584 | -0.75073 | 120.6436 | 0.0026703 | 0.20183 | 0.23074 | 0.0014612 | 0.1359 | 0.050697 | 0.07032 | 0.0021363 | -0.0040567 | 0.076797 | 0.077436 | -0.20019 | -0.00091641 | 120.4605 | 37.2162 | 46.1792 | 6.3629 | 120.5841 | -0.66376 | -0.74158 | 14.3875 | 54.7302 | -0.81024 | 120.5475 | 120.6711 | -0.63171 | -0.66376 | 0.086975 | 0.009155 | -0.05951 | 37.9669 | 7.1136 | 7.1045 | -0.18311 | 0.11902 | 0.086975 | -0.096131 | 15.1382 | -0.05951 | -0.14648 | 0.027466 | 121.3348 | 121.2112 | 46.9299 | -121.3852 | 121.2982 | 121.4218 | 55.481 | -121.3074
2378.5781 | 121.4493 | -0.737 | 120.5933 | -0.0049592 | 0.20204 | 0.23074 | -0.0017432 | 0.13633 | 0.048561 | 0.069893 | -0.0054932 | -0.0061929 | 0.078506 | 0.074232 | -0.20318 | -6.2012e-05 | 120.5566 | 37.4268 | 46.3852 | 6.4819 | 120.5246 | -0.6134 | -0.68665 | 14.5523 | 54.7394 | -0.67291 | 120.4834 | 120.6345 | -0.6134 | -0.63629 | 0.1236 | 0.050354 | -0.068665 | 38.1638 | 7.2189 | 7.1686 | -0.036621 | 0.1236 | 0.10071 | -0.10986 | 15.2893 | 0.064087 | -0.036621 | 0.041198 | 121.2616 | 121.2936 | 47.1222 | -121.2799 | 121.2204 | 121.3715 | 55.4764 | -121.2296
2380.3594 | 121.3806 | -0.76904 | 120.6253 | -0.0049592 | 0.20311 | 0.23438 | 0.0035974 | 0.13441 | 0.04557 | 0.068825 | -0.0054932 | -0.0057657 | 0.07872 | 0.074446 | -0.20575 | 0.0010062 | 120.5338 | 37.5046 | 46.4355 | 6.5002 | 120.5475 | -0.64545 | -0.70953 | 14.5798 | 54.8218 | -0.6958 | 120.4971 | 120.6436 | -0.6134 | -0.6546 | 0.1236 | 0.059509 | -0.07782 | 38.2736 | 7.2693 | 7.2098 | -0.091553 | 0.15564 | 0.11444 | -0.12817 | 15.3488 | 0.073242 | -0.041199 | 0.018311 | 121.3165 | 121.3028 | 47.2046 | -121.3348 | 121.2662 | 121.4127 | 55.5908 | -121.2799
2382.1406 | 121.4035 | -0.76904 | 120.6207 | -0.012589 | 0.20802 | 0.23288 | 0.00082022 | 0.13654 | 0.049629 | 0.067971 | 0.0097658 | -0.0019205 | 0.079147 | 0.076795 | -0.2019 | -0.00091641 | 120.4788 | 37.468 | 46.3257 | 6.4865 | 120.575 | -0.66834 | -0.737 | 14.5615 | 54.4601 | -0.7782 | 120.5154 | 120.6757 | -0.61798 | -0.67291 | 0.10071 | 0.032043 | -0.045777 | 38.237 | 7.2556 | 7.2235 | -0.14191 | 0.15106 | 0.09613 | -0.10529 | 15.3305 | -0.009155 | -0.10528 | 0.054931 | 121.344 | 121.2479 | 47.0947 | -121.3577 | 121.2845 | 121.4447 | 55.2292 | -121.2936
2383.9062 | 121.4355 | -0.74616 | 120.6162 | -0.0049592 | 0.20033 | 0.23566 | -0.00067498 | 0.13483 | 0.044075 | 0.068825 | -0.0054932 | -0.0072611 | 0.077438 | 0.076155 | -0.20276 | 0.0020744 | 120.4971 | 37.6053 | 46.4172 | 6.5186 | 120.5154 | -0.62714 | -0.70953 | 14.6439 | 54.2908 | -0.71411 | 120.4468 | 120.607 | -0.60883 | -0.64087 | 0.11902 | 0.036621 | -0.10071 | 38.3514 | 7.2647 | 7.2281 | -0.11902 | 0.13733 | 0.10529 | -0.16937 | 15.39 | 0.032044 | -0.073242 | -0.009155 | 121.2616 | 121.2433 | 47.1634 | -121.3257 | 121.1929 | 121.3531 | 55.0369 | -121.257
2385.6719 | 121.344 | -0.79193 | 120.6665 | 0.0026703 | 0.20781 | 0.23609 | 0.0014612 | 0.13441 | 0.047279 | 0.067543 | 0.0097658 | -0.0042703 | 0.078506 | 0.074873 | -0.20254 | 0.0014334 | 120.4239 | 37.5504 | 46.2845 | 6.4636 | 120.5429 | -0.67749 | -0.75073 | 14.5569 | 54.0939 | -0.78735 | 120.5429 | 120.6528 | -0.65002 | -0.67749 | 0.11444 | 0.041199 | -0.1236 | 38.3423 | 7.2556 | 7.2144 | -0.24262 | 0.14191 | 0.11444 | -0.1236 | 15.3488 | 0.004577 | -0.10986 | -0.013733 | 121.3348 | 121.2158 | 47.0764 | -121.4172 | 121.3348 | 121.4447 | 54.8859 | -121.344
2387.3906 | 121.3669 | -0.76446 | 120.6207 | -0.012589 | 0.20781 | 0.23309 | 0.0029566 | 0.13718 | 0.051979 | 0.067971 | -0.0054932 | -0.0032021 | 0.080429 | 0.079359 | -0.20041 | -0.00027561 | 120.4926 | 37.6053 | 46.3577 | 6.5277 | 120.5566 | -0.66834 | -0.73242 | 14.6942 | 54.0436 | -0.7782 | 120.5154 | 120.6345 | -0.64545 | -0.67291 | 0.09613 | 0.032043 | -0.064087 | 38.3698 | 7.2922 | 7.2601 | -0.12817 | 0.11902 | 0.091552 | -0.10529 | 15.4587 | -0.013733 | -0.10528 | 0.013732 | 121.3211 | 121.257 | 47.1222 | -121.3531 | 121.2799 | 121.3989 | 54.808 | -121.2936
2389.1719 | 121.4127 | -0.78735 | 120.607 | 0.0026703 | 0.20909 | 0.23331 | 0.0016748 | 0.13697 | 0.046424 | 0.071602 | -0.020752 | -0.0027749 | 0.080215 | 0.076155 | -0.20147 | 0.00015159 | 120.4559 | 37.6144 | 46.2936 | 6.5323 | 120.5704 | -0.65918 | -0.74616 | 14.7217 | 53.8467 | -0.78278 | 120.5017 | 120.6253 | -0.65002 | -0.68665 | 0.12817 | 0.041199 | -0.036621 | 38.4018 | 7.3196 | 7.2784 | -0.15106 | 0.13733 | 0.10071 | -0.10529 | 15.509 | 0.004578 | -0.09613 | 0.01831 | 121.3577 | 121.2433 | 47.081 | -121.3531 | 121.2891 | 121.4127 | 54.6341 | -121.2936
2390.9375 | 121.431 | -0.75531 | 120.5933 | 0.0026703 | 0.20461 | 0.23587 | -0.00046138 | 0.13783 | 0.044502 | 0.069466 | -0.0054932 | -0.0055521 | 0.077438 | 0.074659 | -0.20233 | -0.00048921 | 120.5017 | 37.7106 | 46.3486 | 6.6101 | 120.4926 | -0.64545 | -0.70953 | 14.8087 | 53.7918 | -0.70038 | 120.4559 | 120.5933 | -0.62256 | -0.64087 | 0.10986 | 0.045776 | -0.10071 | 38.4659 | 7.3654 | 7.3196 | -0.091553 | 0.13275 | 0.11444 | -0.13733 | 15.564 | 0.054932 | -0.059509 | 0 | 121.2479 | 121.257 | 47.1039 | -121.3028 | 121.2112 | 121.3486 | 54.5471 | -121.2341
2392.7188 | 121.4539 | -0.72784 | 120.575 | -0.012589 | 0.20802 | 0.23694 | -3.4178e-05 | 0.13676 | 0.049629 | 0.070534 | -0.013123 | -0.0049111 | 0.078934 | 0.077436 | -0.20041 | 0.001647 | 120.4239 | 37.5824 | 46.2021 | 6.5277 | 120.5429 | -0.67749 | -0.75531 | 14.8041 | 53.54 | -0.79651 | 120.4926 | 120.6345 | -0.64545 | -0.66376 | 0.050354 | -0.027466 | -0.032043 | 38.3102 | 7.2556 | 7.283 | -0.15106 | 0.082397 | 0.064087 | -0.082397 | 15.5319 | -0.068665 | -0.13275 | 0.059509 | 121.2708 | 121.1517 | 46.9299 | -121.3303 | 121.2204 | 121.3623 | 54.2679 | -121.2387
2394.4219 | 121.3531 | -0.79651 | 120.6253 | -0.020218 | 0.20995 | 0.23609 | 0.002102 | 0.1359 | 0.050056 | 0.071602 | -0.0054932 | -0.0046975 | 0.080643 | 0.07765 | -0.20276 | 0.00057899 | 120.3873 | 37.6007 | 46.051 | 6.5323 | 120.5383 | -0.68207 | -0.74616 | 14.8224 | 53.4805 | -0.84686 | 120.4926 | 120.6345 | -0.65002 | -0.70038 | 0.11444 | 0.050354 | -0.086975 | 38.3972 | 7.3288 | 7.2784 | -0.23804 | 0.14648 | 0.096131 | -0.13275 | 15.6189 | -0.050354 | -0.14649 | 0.009155 | 121.3348 | 121.1838 | 46.8475 | -121.3715 | 121.2891 | 121.431 | 54.277 | -121.3257
2396.2188 | 121.3486 | -0.80109 | 120.6162 | 0.0026703 | 0.20866 | 0.23566 | 0.0057336 | 0.13847 | 0.044716 | 0.06968 | -0.013123 | -0.0059793 | 0.080429 | 0.077864 | -0.20425 | 0.00079259 | 120.3964 | 37.7151 | 46.106 | 6.5689 | 120.5017 | -0.66834 | -0.75531 | 14.8636 | 53.4027 | -0.81482 | 120.4834 | 120.6573 | -0.65002 | -0.69122 | 0.13275 | 0.045776 | -0.11444 | 38.5162 | 7.37 | 7.3242 | -0.21973 | 0.15106 | 0.10986 | -0.13275 | 15.6647 | -0.013733 | -0.1236 | 0.041199 | 121.3028 | 121.1975 | 46.907 | -121.3715 | 121.2845 | 121.4584 | 54.2038 | -121.3074
2397.9844 | 121.4493 | -0.75073 | 120.575 | -0.012589 | 0.20781 | 0.23865 | 0.002102 | 0.13569 | 0.041725 | 0.069039 | 0.0021363 | -0.0087563 | 0.080429 | 0.0753 | -0.20681 | 0.00057899 | 120.5109 | 37.8937 | 46.225 | 6.6696 | 120.4971 | -0.65918 | -0.72327 | 14.9963 | 53.5355 | -0.68665 | 120.4193 | 120.5841 | -0.60883 | -0.63171 | 0.091552 | 0.027465 | -0.07782 | 38.6444 | 7.4203 | 7.3929 | -0.064087 | 0.14191 | 0.11902 | -0.15564 | 15.7471 | 0.064086 | -0.054932 | 0.009155 | 121.2479 | 121.2616 | 46.9757 | -121.2982 | 121.17 | 121.3348 | 54.2862 | -121.2067
2399.7031 | 121.4447 | -0.74616 | 120.5521 | -0.0049592 | 0.20503 | 0.24036 | 0.00082022 | 0.1374 | 0.045356 | 0.068611 | -0.013123 | -0.0064065 | 0.077652 | 0.076368 | -0.20447 | 0.0014334 | 120.433 | 37.7975 | 46.1288 | 6.6467 | 120.4971 | -0.66376 | -0.737 | 14.9872 | 53.421 | -0.76446 | 120.4514 | 120.607 | -0.63171 | -0.68207 | 0.082398 | 0.009155 | -0.054932 | 38.5437 | 7.3929 | 7.3837 | -0.11902 | 0.11444 | 0.064087 | -0.10071 | 15.7333 | -0.01831 | -0.082397 | 0.054932 | 121.2433 | 121.1792 | 46.875 | -121.2891 | 121.1975 | 121.3531 | 54.1672 | -121.2341
2401.4844 | 121.3348 | -0.80109 | 120.607 | -0.020218 | 0.21101 | 0.23929 | -3.4178e-05 | 0.13783 | 0.047065 | 0.069466 | -0.013123 | -0.0053385 | 0.079575 | 0.076368 | -0.20083 | -0.0021982 | 120.3873 | 37.7426 | 46.1105 | 6.5872 | 120.5017 | -0.70038 | -0.7782 | 14.9826 | 53.3157 | -0.83313 | 120.4605 | 120.5887 | -0.67749 | -0.70496 | 0.10071 | 0.022888 | -0.10529 | 38.5437 | 7.3883 | 7.3654 | -0.21973 | 0.1236 | 0.09613 | -0.14648 | 15.7837 | -0.032044 | -0.12817 | -0.018311 | 121.3028 | 121.1884 | 46.9116 | -121.3852 | 121.2616 | 121.3898 | 54.1168 | -121.312
2403.2656 | 121.4584 | -0.76446 | 120.5566 | 0.0026703 | 0.21037 | 0.24079 | 0.00017942 | 0.13804 | 0.049415 | 0.073097 | -0.0054932 | -0.0044839 | 0.081711 | 0.076795 | -0.20019 | -0.0013436 | 120.3964 | 37.7747 | 46.0785 | 6.6193 | 120.5246 | -0.70038 | -0.76446 | 15.0787 | 53.2745 | -0.82855 | 120.4605 | 120.5933 | -0.6546 | -0.69122 | 0.064087 | 0 | -0.032044 | 38.5391 | 7.3837 | 7.3837 | -0.16022 | 0.10986 | 0.073242 | -0.096131 | 15.8432 | -0.064087 | -0.13733 | 0.036621 | 121.2891 | 121.1609 | 46.843 | -121.3211 | 121.225 | 121.3577 | 54.039 | -121.2479
2404.9688 | 121.4355 | -0.77362 | 120.5566 | -0.0049592 | 0.2108 | 0.23822 | 0.00060662 | 0.13783 | 0.051979 | 0.072243 | -0.0054932 | -0.0044839 | 0.082779 | 0.077223 | -0.20254 | 0.0020744 | 120.3781 | 37.7975 | 46.0327 | 6.633 | 120.5063 | -0.68665 | -0.76904 | 15.1062 | 53.0457 | -0.84686 | 120.4651 | 120.575 | -0.66834 | -0.67749 | 0.086975 | 0.004578 | -0.050354 | 38.5712 | 7.4066 | 7.402 | -0.17853 | 0.10529 | 0.096131 | -0.091553 | 15.8798 | -0.073242 | -0.16937 | 0.01831 | 121.2799 | 121.1517 | 46.8063 | -121.3257 | 121.2387 | 121.3486 | 53.8193 | -121.2341
2406.7656 | 121.3806 | -0.80566 | 120.5566 | -0.012589 | 0.21315 | 0.23908 | 0.001034 | 0.13804 | 0.050911 | 0.07032 | -0.013123 | -0.0023477 | 0.080215 | 0.075086 | -0.20212 | 0.0012198 | 120.3598 | 37.8662 | 46.0831 | 6.6422 | 120.4788 | -0.71411 | -0.7782 | 15.1154 | 53.064 | -0.85144 | 120.4514 | 120.6207 | -0.68207 | -0.71411 | 0.091553 | 0.027466 | -0.07782 | 38.6719 | 7.4478 | 7.4203 | -0.19684 | 0.1236 | 0.091553 | -0.10529 | 15.921 | -0.045776 | -0.13733 | 0.064087 | 121.2845 | 121.1655 | 46.8887 | -121.3348 | 121.257 | 121.4264 | 53.8696 | -121.2708
2408.4688 | 121.3394 | -0.80109 | 120.5612 | -0.0049592 | 0.21401 | 0.241 | 0.0033838 | 0.13761 | 0.044502 | 0.070748 | -0.013123 | -0.0070475 | 0.079788 | 0.074446 | -0.20318 | -0.0024118 | 120.4468 | 38.0402 | 46.2158 | 6.7429 | 120.4239 | -0.67749 | -0.74158 | 15.2573 | 53.1509 | -0.72784 | 120.3827 | 120.5521 | -0.65002 | -0.69122 | 0.1236 | 0.059509 | -0.13733 | 38.8412 | 7.5439 | 7.4844 | -0.11444 | 0.15106 | 0.10986 | -0.17853 | 16.0583 | 0.073242 | -0.036621 | -0.009155 | 121.225 | 121.2479 | 47.0169 | -121.3028 | 121.1838 | 121.3531 | 53.952 | -121.2524
2410.2344 | 121.376 | -0.81024 | 120.5475 | 0.0026703 | 0.21465 | 0.23993 | 0.0035974 | 0.13953 | 0.051338 | 0.071602 | -0.0054932 | -0.0053385 | 0.080856 | 0.077223 | -0.20276 | -0.00048921 | 120.3781 | 37.9211 | 46.0602 | 6.6833 | 120.4926 | -0.72327 | -0.79193 | 15.1932 | 53.1692 | -0.85144 | 120.4605 | 120.6116 | -0.67749 | -0.71869 | 0.086975 | 0.018311 | -0.054931 | 38.7314 | 7.4936 | 7.4753 | -0.16937 | 0.13275 | 0.091553 | -0.086975 | 16.0034 | -0.041198 | -0.13275 | 0.064087 | 121.3028 | 121.1884 | 46.8704 | -121.3394 | 121.2708 | 121.4218 | 53.9795 | -121.2662
2412.0156 | 121.3715 | -0.8194 | 120.5338 | -0.012589 | 0.2123 | 0.24143 | 0.00082022 | 0.13868 | 0.051765 | 0.07032 | -0.0054932 | -0.0025613 | 0.078934 | 0.075941 | -0.2019 | -6.2012e-05 | 120.3461 | 37.9761 | 46.0007 | 6.6925 | 120.4834 | -0.70038 | -0.80566 | 15.2481 | 53.3798 | -0.85602 | 120.4376 | 120.575 | -0.68207 | -0.71869 | 0.11902 | 0.013733 | -0.050354 | 38.7955 | 7.5119 | 7.4982 | -0.18768 | 0.13733 | 0.10071 | -0.09613 | 16.0675 | -0.036621 | -0.13733 | 0.041199 | 121.3028 | 121.1655 | 46.8201 | -121.3394 | 121.257 | 121.3943 | 54.1992 | -121.2524
2413.75 | 121.3165 | -0.8194 | 120.5612 | -0.012589 | 0.21465 | 0.24121 | -0.004093 | 0.13996 | 0.051765 | 0.072029 | -0.0054932 | -0.0038431 | 0.078506 | 0.07765 | -0.20147 | 0.0020744 | 120.3369 | 37.9715 | 45.9549 | 6.6971 | 120.4605 | -0.72327 | -0.79193 | 15.2893 | 53.3066 | -0.89264 | 120.4514 | 120.5978 | -0.68665 | -0.72784 | 0.09613 | 0.027466 | -0.10071 | 38.7909 | 7.5165 | 7.489 | -0.2243 | 0.13275 | 0.091553 | -0.10986 | 16.1087 | -0.073242 | -0.16479 | 0.036621 | 121.2799 | 121.1563 | 46.7743 | -121.3531 | 121.2708 | 121.4172 | 54.126 | -121.2891
2415.5156 | 121.4401 | -0.78735 | 120.5063 | -0.012589 | 0.21208 | 0.24399 | 0.001034 | 0.13825 | 0.041938 | 0.068184 | -0.013123 | -0.0083291 | 0.078293 | 0.073377 | -0.20617 | 0.003356 | 120.4147 | 38.1592 | 46.0876 | 6.8069 | 120.433 | -0.68665 | -0.75531 | 15.4541 | 53.5812 | -0.69122 | 120.3369 | 120.5383 | -0.66376 | -0.70953 | 0.10071 | 0.032044 | -0.073243 | 38.9465 | 7.5943 | 7.5623 | -0.091553 | 0.1236 | 0.07782 | -0.16937 | 16.2415 | 0.096131 | 0.018311 | 0.032043 | 121.2204 | 121.2021 | 46.875 | -121.2616 | 121.1243 | 121.3257 | 54.3686 | -121.2158
2417.25 | 121.3348 | -0.8194 | 120.5154 | -0.0049592 | 0.21358 | 0.24314 | 0.001034 | 0.13804 | 0.052406 | 0.071602 | -0.0054932 | -0.0027749 | 0.080643 | 0.079786 | -0.20254 | -0.00113 | 120.4056 | 38.0905 | 45.9869 | 6.7749 | 120.4742 | -0.72327 | -0.7782 | 15.4724 | 53.5904 | -0.82398 | 120.4056 | 120.5475 | -0.69122 | -0.72327 | 0.09613 | 0.041199 | -0.041199 | 38.9099 | 7.5943 | 7.5531 | -0.10986 | 0.12817 | 0.09613 | -0.10986 | 16.2918 | -0.004578 | -0.10071 | 0.032043 | 121.2936 | 121.225 | 46.8063 | -121.2936 | 121.225 | 121.3669 | 54.4098 | -121.2387
2419.0156 | 121.3257 | -0.8194 | 120.5429 | -0.020218 | 0.21828 | 0.24634 | 0.003811 | 0.13975 | 0.045997 | 0.071816 | -0.0054932 | -0.0081155 | 0.08107 | 0.075514 | -0.20852 | 0.0010062 | 120.3964 | 38.1638 | 46.0648 | 6.8436 | 120.4285 | -0.68207 | -0.75989 | 15.5045 | 53.7369 | -0.75073 | 120.3552 | 120.5429 | -0.64545 | -0.70496 | 0.13733 | 0.059509 | -0.11444 | 38.9832 | 7.663 | 7.6035 | -0.14648 | 0.17395 | 0.11444 | -0.18768 | 16.3239 | 0.068665 | -0.045776 | 0 | 121.2479 | 121.2158 | 46.8842 | -121.3028 | 121.1746 | 121.3623 | 54.5563 | -121.2479
2420.7969 | 121.3531 | -0.81024 | 120.5338 | -0.020218 | 0.21892 | 0.24228 | 0.0027428 | 0.13847 | 0.052833 | 0.072029 | -0.013123 | -0.0012795 | 0.079147 | 0.078077 | -0.20276 | 0.00015159 | 120.3781 | 38.1042 | 46.0464 | 6.7932 | 120.4697 | -0.70038 | -0.80109 | 15.5136 | 53.6728 | -0.8194 | 120.433 | 120.5475 | -0.68207 | -0.71869 | 0.10986 | 0.009156 | -0.064086 | 38.9145 | 7.6035 | 7.5943 | -0.15564 | 0.12817 | 0.091553 | -0.10071 | 16.3239 | -0.009155 | -0.10071 | 0.013733 | 121.2799 | 121.1884 | 46.8567 | -121.3348 | 121.2433 | 121.3577 | 54.483 | -121.2524
2422.5156 | 121.4035 | -0.80109 | 120.488 | 0.0026703 | 0.21272 | 0.24527 | 0.0029566 | 0.1374 | 0.045143 | 0.07032 | -0.0054932 | -0.0081155 | 0.080643 | 0.07765 | -0.20617 | 0.002288 | 120.3506 | 38.1454 | 46.0922 | 6.8161 | 120.4193 | -0.70038 | -0.7782 | 15.5273 | 53.7323 | -0.7782 | 120.3461 | 120.5063 | -0.67291 | -0.6958 | 0.10071 | 0.022888 | -0.068664 | 38.9465 | 7.6172 | 7.5943 | -0.13733 | 0.12817 | 0.10528 | -0.14191 | 16.3284 | 0.022888 | -0.082397 | 0.018311 | 121.2204 | 121.1517 | 46.8933 | -121.2662 | 121.1472 | 121.3074 | 54.5334 | -121.1838
2424.3125 | 121.4218 | -0.79193 | 120.4697 | -0.0049592 | 0.2155 | 0.24527 | 0.0023156 | 0.13953 | 0.050911 | 0.07267 | -0.0054932 | -0.0055521 | 0.079361 | 0.078291 | -0.20041 | -0.0024118 | 120.3461 | 38.0997 | 46.0556 | 6.8024 | 120.4285 | -0.71411 | -0.80566 | 15.6143 | 53.9108 | -0.79193 | 120.3827 | 120.5063 | -0.67749 | -0.72327 | 0.07782 | -0.013733 | -0.041199 | 38.8916 | 7.5943 | 7.608 | -0.1236 | 0.11444 | 0.068664 | -0.086976 | 16.4062 | 0 | -0.068664 | 0.036621 | 121.2204 | 121.138 | 46.8475 | -121.2753 | 121.1746 | 121.2982 | 54.7028 | -121.1929
2426.0938 | 121.2845 | -0.86517 | 120.5109 | -0.020218 | 0.21379 | 0.24698 | 0.002102 | 0.13932 | 0.047706 | 0.074379 | 0.0021363 | -0.0059793 | 0.080429 | 0.078504 | -0.20233 | 0.0010062 | 120.3415 | 38.1821 | 46.1197 | 6.8527 | 120.3964 | -0.72327 | -0.81482 | 15.6006 | 53.9062 | -0.85144 | 120.3735 | 120.5338 | -0.70496 | -0.75989 | 0.14191 | 0.050354 | -0.11444 | 39.0472 | 7.7179 | 7.6675 | -0.16937 | 0.16022 | 0.10528 | -0.13733 | 16.4658 | 0.013733 | -0.091552 | 0.022888 | 121.2616 | 121.2067 | 46.9849 | -121.3257 | 121.2387 | 121.3989 | 54.7714 | -121.2708
2427.875 | 121.3028 | -0.85602 | 120.4788 | 0.0026703 | 0.21977 | 0.24591 | 0.0050928 | 0.14039 | 0.05262 | 0.071175 | -0.020752 | -0.0049111 | 0.08107 | 0.077009 | -0.20425 | 0.00079259 | 120.2774 | 38.1226 | 46.0098 | 6.7932 | 120.4102 | -0.75989 | -0.84228 | 15.6006 | 53.9108 | -0.89264 | 120.3918 | 120.5292 | -0.74158 | -0.75531 | 0.09613 | 0.013733 | -0.068665 | 38.9786 | 7.6492 | 7.6355 | -0.20142 | 0.11444 | 0.10071 | -0.086975 | 16.4566 | -0.036621 | -0.13733 | 0.050354 | 121.2662 | 121.1334 | 46.8658 | -121.3211 | 121.2479 | 121.3852 | 54.7668 | -121.2341
2429.5938 | 121.3943 | -0.83313 | 120.4376 | -0.0049592 | 0.21956 | 0.24591 | -0.0015296 | 0.13975 | 0.052192 | 0.073738 | -0.013123 | -0.0036295 | 0.081284 | 0.078718 | -0.20062 | -0.00070281 | 120.3049 | 38.1546 | 45.9732 | 6.8481 | 120.4376 | -0.75989 | -0.82398 | 15.6738 | 53.952 | -0.88806 | 120.3598 | 120.5109 | -0.70953 | -0.75531 | 0.073242 | 0.009155 | 0 | 38.9877 | 7.6813 | 7.6721 | -0.13275 | 0.1236 | 0.07782 | -0.07782 | 16.507 | -0.054932 | -0.13275 | 0.073242 | 121.2708 | 121.138 | 46.8063 | -121.2616 | 121.1929 | 121.344 | 54.7852 | -121.1929
2431.375 | 121.3715 | -0.82855 | 120.4468 | -0.0049592 | 0.21764 | 0.24783 | 0.0023156 | 0.14295 | 0.045143 | 0.070961 | -0.013123 | -0.0072611 | 0.081924 | 0.075727 | -0.20468 | 0.00079259 | 120.3735 | 38.3423 | 46.0876 | 6.9351 | 120.3552 | -0.72784 | -0.79651 | 15.7928 | 54.1534 | -0.75073 | 120.2866 | 120.4788 | -0.69122 | -0.75531 | 0.10071 | 0.032043 | -0.091552 | 39.1708 | 7.7637 | 7.7316 | -0.073242 | 0.13733 | 0.073242 | -0.16022 | 16.6214 | 0.07782 | 0.004578 | 0.032044 | 121.1838 | 121.2021 | 46.9162 | -121.2433 | 121.1151 | 121.3074 | 54.982 | -121.2021
2433.1094 | 121.4264 | -0.83771 | 120.4193 | -0.012589 | 0.21465 | 0.24912 | -0.00024778 | 0.14317 | 0.047493 | 0.072029 | 0.0021363 | -0.0064065 | 0.078934 | 0.076368 | -0.20361 | 0.0012198 | 120.3049 | 38.2736 | 45.9915 | 6.8985 | 120.3461 | -0.75073 | -0.80109 | 15.77 | 54.1718 | -0.80566 | 120.314 | 120.4468 | -0.70038 | -0.72327 | 0.086976 | 0.036622 | -0.073243 | 39.1113 | 7.7362 | 7.6996 | -0.11444 | 0.13733 | 0.11444 | -0.10529 | 16.6077 | 0.032044 | -0.082397 | 0.027465 | 121.1838 | 121.1426 | 46.8292 | -121.2204 | 121.1517 | 121.2845 | 55.0095 | -121.1426
2434.875 | 121.2936 | -0.89264 | 120.4697 | -0.0049592 | 0.22298 | 0.24933 | 0.001034 | 0.14039 | 0.051979 | 0.072884 | -0.013123 | -0.0042703 | 0.082565 | 0.075941 | -0.20297 | 0.00015159 | 120.2728 | 38.2278 | 45.9045 | 6.8665 | 120.3918 | -0.7782 | -0.85602 | 15.7471 | 54.2358 | -0.91095 | 120.3369 | 120.4926 | -0.75531 | -0.79651 | 0.11444 | 0.036621 | -0.07782 | 39.1205 | 7.7591 | 7.7225 | -0.19684 | 0.13733 | 0.09613 | -0.13275 | 16.6397 | -0.018311 | -0.11444 | 0.022888 | 121.2845 | 121.1655 | 46.7972 | -121.3257 | 121.2296 | 121.3852 | 55.1285 | -121.2662
2436.6562 | 121.2845 | -0.91095 | 120.4376 | 0.0026703 | 0.22276 | 0.24976 | 0.0018884 | 0.13889 | 0.048774 | 0.072029 | -0.0054932 | -0.0051247 | 0.080643 | 0.075941 | -0.2034 | 0.001647 | 120.3049 | 38.2965 | 45.9229 | 6.9626 | 120.3094 | -0.78735 | -0.82855 | 15.7974 | 54.4189 | -0.85602 | 120.2682 | 120.4422 | -0.7782 | -0.78278 | 0.1236 | 0.082398 | -0.12817 | 39.2075 | 7.8735 | 7.7911 | -0.13275 | 0.13275 | 0.12817 | -0.16937 | 16.7084 | 0.054932 | -0.073242 | 0.004578 | 121.2204 | 121.2158 | 46.8338 | -121.2662 | 121.1792 | 121.3531 | 55.3299 | -121.2204
2438.4375 | 121.3211 | -1.4923 | 119.7144 | -0.0049592 | 0.21806 | 0.24954 | 0.00039302 | 0.14317 | 0.048774 | 0.073097 | -0.013123 | -0.0064065 | 0.080002 | 0.077223 | -0.20147 | 0.0027152 | 119.6182 | 37.8204 | 45.4056 | 6.3812 | 119.6228 | -1.4145 | -1.4786 | 15.1932 | 53.9062 | -1.506 | 119.5541 | 119.7372 | -1.387 | -1.4282 | 0.07782 | 0.013733 | -0.091552 | 39.3127 | 7.8735 | 7.8598 | -0.09613 | 0.10529 | 0.064087 | -0.16022 | 16.6855 | -0.013732 | -0.077819 | 0.022889 | 121.1151 | 121.1105 | 46.8979 | -121.1929 | 121.0464 | 121.2296 | 55.3986 | -121.1426
2440.2188 | 121.3257 | -1.4603 | 119.7372 | 0.0026703 | 0.22298 | 0.24912 | 0.0050928 | 0.13996 | 0.050483 | 0.072029 | -0.013123 | -0.0051247 | 0.08342 | 0.077223 | -0.20553 | -0.0013436 | 119.6869 | 37.8891 | 45.369 | 6.4682 | 119.632 | -1.3779 | -1.4648 | 15.358 | 54.071 | -1.4053 | 119.5999 | 119.7098 | -1.3275 | -1.3779 | 0.082397 | -0.004578 | -0.10529 | 39.3494 | 7.9285 | 7.933 | -0.050354 | 0.13275 | 0.082397 | -0.13733 | 16.8182 | 0.054932 | -0.027465 | -0.027466 | 121.0922 | 121.1472 | 46.8292 | -121.2021 | 121.0602 | 121.17 | 55.5313 | -121.1151
2441.9219 | 121.1929 | -1.506 | 119.7189 | 0.0026703 | 0.22853 | 0.2504 | -3.4178e-05 | 0.1406 | 0.05796 | 0.074593 | -0.0054932 | -0.0017069 | 0.085129 | 0.077009 | -0.20019 | -0.00048921 | 119.632 | 37.8296 | 45.1492 | 6.4178 | 119.6777 | -1.4053 | -1.4832 | 15.3122 | 53.9566 | -1.5152 | 119.6365 | 119.7372 | -1.4053 | -1.4099 | 0.10071 | 0.022888 | -0.041199 | 39.3356 | 7.9239 | 7.901 | -0.086975 | 0.10071 | 0.09613 | -0.082397 | 16.8182 | -0.009156 | -0.10529 | 0.018311 | 121.1838 | 121.138 | 46.6553 | -121.2021 | 121.1426 | 121.2433 | 55.4626 | -121.1288
2443.7031 | 121.2753 | -1.506 | 119.6411 | -0.020218 | 0.22105 | 0.24954 | -0.0038794 | 0.14188 | 0.049842 | 0.075447 | -0.013123 | -0.0085427 | 0.082779 | 0.0753 | -0.19934 | 0.0010062 | 119.577 | 37.8754 | 45.0302 | 6.4316 | 119.5404 | -1.4236 | -1.4832 | 15.39 | 54.1122 | -1.474 | 119.5084 | 119.6274 | -1.387 | -1.4145 | 0.082397 | 0.022888 | -0.10071 | 39.3814 | 7.9376 | 7.9147 | -0.064087 | 0.11902 | 0.091552 | -0.13275 | 16.8961 | 0.032043 | -0.059509 | -0.013733 | 121.0464 | 121.0831 | 46.5363 | -121.1243 | 121.0144 | 121.1334 | 55.6183 | -121.0556
2445.4688 | 121.2204 | -1.5976 | 119.5541 | -0.012589 | 0.2249 | 0.25318 | 0.0035974 | 0.14253 | 0.051338 | 0.073738 | -0.028381 | -0.0083291 | 0.081497 | 0.074659 | -0.20147 | 0.0010062 | 119.4946 | 37.7975 | 45.0943 | 6.3904 | 119.4992 | -1.474 | -1.561 | 15.3625 | 54.126 | -1.5335 | 119.4534 | 119.5587 | -1.442 | -1.5015 | 0.1236 | 0.036621 | -0.054931 | 39.3951 | 7.988 | 7.9514 | -0.059509 | 0.15564 | 0.09613 | -0.10071 | 16.9601 | 0.064087 | -0.032043 | 0.004578 | 121.0968 | 121.0922 | 46.6919 | -121.1151 | 121.051 | 121.1563 | 55.7236 | -121.0556
2447.1875 | 121.2479 | -1.6708 | 119.4717 | 0.0026703 | 0.21977 | 0.2489 | 0.00017942 | 0.14103 | 0.049842 | 0.07502 | -0.013123 | -0.0036295 | 0.078934 | 0.077864 | -0.20532 | 0.00057899 | 119.4168 | 37.7518 | 45.0714 | 6.3354 | 119.4077 | -1.5518 | -1.6022 | 15.3397 | 54.1077 | -1.6296 | 119.3756 | 119.4992 | -1.5289 | -1.5656 | 0.11902 | 0.068664 | -0.064087 | 39.4226 | 8.0063 | 7.9376 | -0.054932 | 0.14191 | 0.10528 | -0.096131 | 17.0105 | 0.041198 | -0.064087 | 0.027466 | 121.0785 | 121.0876 | 46.7422 | -121.0739 | 121.0464 | 121.17 | 55.7785 | -121.0373
2448.9531 | 121.2433 | -1.712 | 119.371 | -0.012589 | 0.22533 | 0.2489 | -0.0015296 | 0.14359 | 0.055397 | 0.073311 | 0.0021363 | -0.0032021 | 0.079147 | 0.076368 | -0.20041 | -0.00113 | 119.3161 | 37.738 | 44.9753 | 6.3034 | 119.3161 | -1.6342 | -1.7029 | 15.3946 | 54.071 | -1.6983 | 119.252 | 119.3802 | -1.5976 | -1.6342 | 0.07782 | 0.009155 | -0.054932 | 39.4501 | 8.0154 | 8.0063 | -0.054932 | 0.11444 | 0.07782 | -0.11902 | 17.1066 | 0.013733 | -0.064087 | 0.009155 | 121.0281 | 121.0281 | 46.6873 | -121.0739 | 120.9641 | 121.0922 | 55.7831 | -121.0052
2450.7188 | 121.2341 | -1.8494 | 119.252 | -0.012589 | 0.22554 | 0.25018 | 0.00060662 | 0.14573 | 0.057106 | 0.076088 | -0.013123 | -0.0023477 | 0.081497 | 0.078504 | -0.20041 | 0.0037832 | 119.1193 | 37.5275 | 44.7189 | 6.1432 | 119.2337 | -1.7853 | -1.8494 | 15.2435 | 53.9154 | -1.9089 | 119.1605 | 119.2932 | -1.7303 | -1.7624 | 0.064087 | 0 | -0.01831 | 39.3768 | 7.9926 | 7.9926 | -0.13275 | 0.11902 | 0.086975 | -0.091553 | 17.0929 | -0.05951 | -0.14649 | 0.041199 | 121.0831 | 120.9686 | 46.5683 | -121.1014 | 121.0098 | 121.1426 | 55.7648 | -121.0144
2452.4219 | 121.1151 | -1.973 | 119.1467 | -0.012589 | 0.22939 | 0.25211 | 0.0050928 | 0.14466 | 0.053047 | 0.076943 | -0.028381 | -0.0049111 | 0.084702 | 0.07765 | -0.20468 | 0.002288 | 118.9728 | 37.4725 | 44.5679 | 6.0471 | 119.0872 | -1.886 | -1.9592 | 15.1566 | 53.92 | -2.0187 | 119.0506 | 119.1925 | -1.8356 | -1.8906 | 0.086975 | 0.013732 | -0.05951 | 39.4455 | 8.02 | 8.0063 | -0.17395 | 0.13733 | 0.082397 | -0.096131 | 17.1295 | -0.045777 | -0.12817 | 0.045776 | 121.0602 | 120.9457 | 46.5408 | -121.106 | 121.0236 | 121.1655 | 55.8929 | -121.0373
2454.1875 | 121.1563 | -2.3804 | 118.6752 | -0.0049592 | 0.2264 | 0.25467 | 0.0018884 | 0.14552 | 0.048133 | 0.076943 | -0.0054932 | -0.0049111 | 0.081924 | 0.075941 | -0.20468 | 0.00079259 | 118.6386 | 37.3718 | 44.3069 | 5.7861 | 118.602 | -2.2476 | -2.3254 | 14.9506 | 53.6224 | -2.3071 | 118.5425 | 118.7027 | -2.2247 | -2.2842 | 0.13275 | 0.054932 | -0.073242 | 39.7522 | 8.1665 | 8.1116 | -0.036621 | 0.15564 | 0.09613 | -0.13275 | 17.3309 | 0.073242 | -0.022888 | 0.027466 | 120.9824 | 121.019 | 46.6873 | -121.0007 | 120.9229 | 121.0831 | 56.0028 | -120.9595
2455.9688 | 121.0785 | -2.8427 | 118.2037 | -0.012589 | 0.22789 | 0.25339 | 0.0012476 | 0.14744 | 0.056465 | 0.075447 | -0.013123 | -0.0021341 | 0.079361 | 0.07765 | -0.20041 | -0.00091641 | 118.0298 | 36.8637 | 43.8629 | 5.3284 | 118.1488 | -2.7649 | -2.8244 | 14.4516 | 52.9907 | -2.9205 | 118.103 | 118.2266 | -2.7054 | -2.7695 | 0.077819 | 0.01831 | -0.054931 | 39.7064 | 8.1711 | 8.1528 | -0.17395 | 0.13733 | 0.073242 | -0.10071 | 17.2943 | -0.07782 | -0.15106 | 0.022889 | 120.9915 | 120.8725 | 46.7056 | -121.0281 | 120.9457 | 121.0693 | 55.8334 | -120.9732
2457.6875 | 121.0602 | -4.8523 | 116.0294 | 0.0026703 | 0.22298 | 0.24997 | 0.003811 | 0.15043 | 0.050697 | 0.077797 | 0.0021363 | -0.0093973 | 0.082993 | 0.077009 | -0.20831 | 0.00057899 | 115.979 | 35.7101 | 42.6865 | 3.6896 | 115.9744 | -4.747 | -4.7836 | 12.6617 | 51.2192 | -4.8019 | 115.9287 | 116.066 | -4.6921 | -4.747 | 0.10529 | 0.068665 | -0.054932 | 40.5624 | 8.5419 | 8.4732 | -0.050354 | 0.16022 | 0.10529 | -0.10071 | 17.514 | 0.050354 | -0.054932 | 0.036621 | 120.8267 | 120.8313 | 47.5388 | -120.813 | 120.7809 | 120.9183 | 56.0715 | -120.7764
2459.4531 | 120.9274 | -4.4357 | 116.3589 | -0.012589 | 0.22554 | 0.24997 | -0.0011024 | 0.14658 | 0.053474 | 0.079506 | -0.0054932 | -0.0055521 | 0.079361 | 0.076582 | -0.20147 | 0.0014334 | 116.3498 | 35.9482 | 42.8421 | 4.0741 | 116.3406 | -4.2801 | -4.3396 | 13.1332 | 51.5305 | -4.3808 | 116.2811 | 116.423 | -4.2618 | -4.2984 | 0.15564 | 0.09613 | -0.018311 | 40.3839 | 8.5098 | 8.4137 | -0.009156 | 0.17395 | 0.13733 | -0.07782 | 17.569 | 0.054932 | -0.082397 | 0.064087 | 120.7764 | 120.7855 | 47.2778 | -120.6985 | 120.7169 | 120.8588 | 55.9662 | -120.6573
2461.1719 | 120.7855 | -6.5048 | 114.1525 | -0.012589 | 0.22383 | 0.24976 | 0.0018884 | 0.15171 | 0.055183 | 0.080574 | 0.0021363 | -0.0087563 | 0.080429 | 0.077864 | -0.2034 | 0.00036539 | 113.6993 | 34.4925 | 41.5787 | 2.2751 | 113.9008 | -6.5369 | -6.5643 | 11.0184 | 49.4339 | -6.6513 | 113.855 | 113.974 | -6.4178 | -6.5048 | -0.032043 | -0.059509 | -0.25177 | 40.9973 | 8.7799 | 8.8394 | -0.45319 | 0.086975 | 0 | -0.29755 | 17.5232 | -0.14648 | -0.14648 | -0.17853 | 120.4056 | 120.2042 | 48.0835 | -120.7169 | 120.3598 | 120.4788 | 55.9387 | -120.6573
2462.9375 | 120.694 | -7.9926 | 112.5092 | 0.0026703 | 0.22234 | 0.24741 | 0.002102 | 0.15171 | 0.05796 | 0.082283 | 0.0021363 | -0.0070475 | 0.081284 | 0.075727 | -0.20126 | 0.00079259 | 112.5229 | 33.4854 | 40.5212 | 0.99792 | 112.4817 | -7.901 | -7.9422 | 9.6359 | 48.111 | -8.1711 | 112.4176 | 112.5046 | -7.901 | -7.9468 | 0.091553 | 0.050354 | -0.027466 | 41.478 | 8.9905 | 8.9401 | 0.013733 | 0.091553 | 0.045777 | -0.091552 | 17.6285 | -0.17853 | -0.22431 | -0.004577 | 120.4742 | 120.5154 | 48.5138 | -120.4514 | 120.4102 | 120.4971 | 56.1035 | -120.4559
2464.7188 | 121.1014 | -0.40741 | 120.607 | -0.012589 | 0.22554 | 0.25894 | 0.00082022 | 0.14381 | 0.048561 | 0.072243 | -0.013123 | -0.0064065 | 0.079575 | 0.075727 | -0.20276 | 0.0018606 | 120.4788 | 38.5025 | 45.0394 | 7.5302 | 120.5658 | -0.29755 | -0.36163 | 17.1936 | 55.4901 | -0.37079 | 120.5017 | 120.6162 | -0.26093 | -0.31128 | 0.10986 | 0.045777 | -0.041199 | 38.9099 | 7.9376 | 7.8918 | -0.12817 | 0.14648 | 0.096131 | -0.10529 | 17.601 | 0.036621 | -0.05951 | 0.009155 | 120.9732 | 120.8862 | 45.4468 | -120.9686 | 120.9091 | 121.0236 | 55.8975 | -120.9183
2466.4219 | 121.17 | -0.40741 | 120.6711 | -0.012589 | 0.22768 | 0.26065 | 0.0025292 | 0.14445 | 0.048561 | 0.073738 | -0.0054932 | -0.0068337 | 0.081284 | 0.075941 | -0.2034 | 0.0035696 | 120.6116 | 38.6032 | 45.0989 | 7.6035 | 120.5658 | -0.29297 | -0.36163 | 17.3355 | 55.719 | -0.3067 | 120.5521 | 120.639 | -0.24719 | -0.31128 | 0.11444 | 0.045777 | -0.10529 | 39.0106 | 8.0109 | 7.9651 | -0.05951 | 0.16022 | 0.096131 | -0.11902 | 17.7429 | 0.10071 | 0.004577 | -0.032044 | 120.9732 | 121.019 | 45.5063 | -121.0327 | 120.9595 | 121.0464 | 56.1264 | -120.9824
2468.2031 | 121.2341 | -0.39368 | 120.7169 | 0.0103 | 0.2281 | 0.26022 | -0.0011024 | 0.14359 | 0.050911 | 0.073097 | -0.0054932 | -0.0068337 | 0.081497 | 0.076795 | -0.2034 | 0.00079259 | 120.5704 | 38.4705 | 44.9387 | 7.5577 | 120.6436 | -0.28381 | -0.37079 | 17.2943 | 55.5725 | -0.37079 | 120.5933 | 120.7123 | -0.29297 | -0.31586 | 0.10986 | 0.022888 | -0.073242 | 38.8641 | 7.9514 | 7.9285 | -0.14648 | 0.10071 | 0.07782 | -0.1236 | 17.688 | 0.022888 | -0.054932 | -0.004578 | 121.0373 | 120.9641 | 45.3323 | -121.0876 | 120.9869 | 121.106 | 55.9662 | -121.0327
2469.9688 | 121.1105 | -0.43488 | 120.7764 | -0.012589 | 0.23622 | 0.25958 | -0.0011024 | 0.14167 | 0.059242 | 0.075447 | -0.013123 | -0.0019205 | 0.082138 | 0.077009 | -0.19827 | -0.0015572 | 120.6116 | 38.4567 | 44.8105 | 7.5485 | 120.7031 | -0.33875 | -0.42114 | 17.3355 | 55.5359 | -0.46692 | 120.6482 | 120.7397 | -0.31586 | -0.34332 | 0.09613 | 0.013732 | -0.073242 | 38.8916 | 7.9834 | 7.9697 | -0.16479 | 0.11902 | 0.091552 | -0.12817 | 17.7704 | -0.032044 | -0.1236 | -0.036621 | 121.138 | 121.0464 | 45.2454 | -121.1975 | 121.0831 | 121.1746 | 55.9708 | -121.1197
2471.6875 | 121.2891 | -0.41199 | 120.7214 | -0.012589 | 0.22832 | 0.26535 | 0.0016748 | 0.14253 | 0.047706 | 0.073738 | -0.013123 | -0.0068337 | 0.081924 | 0.076795 | -0.20276 | 0.0029288 | 120.5841 | 38.475 | 44.7693 | 7.5806 | 120.6665 | -0.29297 | -0.37537 | 17.4866 | 55.7098 | -0.35248 | 120.607 | 120.7581 | -0.28839 | -0.3067 | 0.11902 | 0.036621 | -0.054932 | 38.887 | 7.9926 | 7.9559 | -0.13733 | 0.1236 | 0.10529 | -0.11444 | 17.8986 | 0.059509 | -0.045776 | 0.036621 | 121.0785 | 120.9961 | 45.1813 | -121.0968 | 121.019 | 121.17 | 56.1218 | -121.0281
2473.4531 | 121.2158 | -0.41657 | 120.7535 | -0.012589 | 0.23302 | 0.26578 | 0.0031702 | 0.14381 | 0.05262 | 0.074593 | -0.020752 | -0.0040567 | 0.081711 | 0.074446 | -0.20233 | 0.00036539 | 120.6711 | 38.5254 | 44.7784 | 7.6355 | 120.6802 | -0.30212 | -0.39368 | 17.6285 | 55.9433 | -0.32501 | 120.6345 | 120.7306 | -0.2655 | -0.31586 | 0.11444 | 0.022888 | -0.073242 | 38.942 | 8.0521 | 8.0292 | -0.082397 | 0.15106 | 0.10071 | -0.11902 | 18.045 | 0.091553 | -0.009155 | -0.022888 | 121.0968 | 121.0876 | 45.195 | -121.1472 | 121.051 | 121.1472 | 56.3599 | -121.0693
2475.2344 | 121.1517 | -0.44861 | 120.7809 | -0.0049592 | 0.23473 | 0.26535 | -0.0011024 | 0.14658 | 0.054756 | 0.07267 | -0.013123 | -0.0040567 | 0.082138 | 0.0753 | -0.2034 | 0.001647 | 120.6207 | 38.3926 | 44.5221 | 7.5714 | 120.7031 | -0.32501 | -0.40283 | 17.6743 | 55.9021 | -0.43945 | 120.6573 | 120.7809 | -0.31128 | -0.3479 | 0.1236 | 0.045776 | -0.07782 | 38.8412 | 8.02 | 7.9742 | -0.16022 | 0.13733 | 0.10071 | -0.1236 | 18.1229 | 0.009155 | -0.091553 | 0 | 121.1517 | 121.0693 | 44.9707 | -121.1838 | 121.106 | 121.2296 | 56.3507 | -121.1288
2476.9375 | 121.2021 | -0.43945 | 120.7672 | -0.020218 | 0.23665 | 0.26621 | 0.0029566 | 0.1421 | 0.05027 | 0.072029 | -0.0054932 | -0.0053385 | 0.081284 | 0.077223 | -0.20297 | 0.00015159 | 120.6711 | 38.4338 | 42.7048 | 7.6447 | 120.6619 | -0.32959 | -0.3891 | 17.8711 | 56.012 | -0.36163 | 120.6162 | 120.7535 | -0.27466 | -0.31128 | 0.10986 | 0.050354 | -0.10529 | 38.8733 | 8.0841 | 8.0338 | -0.09613 | 0.16479 | 0.12817 | -0.15106 | 18.3105 | 0.07782 | -0.050354 | -0.013733 | 121.1014 | 121.1105 | 43.1442 | -121.1563 | 121.0556 | 121.1929 | 56.4514 | -121.0785
2478.7031 | 121.2296 | -0.42572 | 120.7581 | -0.0049592 | 0.24007 | 0.26407 | 0.0061608 | 0.14082 | 0.054756 | 0.073525 | 0.0097658 | -0.0034159 | 0.086624 | 0.077436 | -0.20254 | -0.00027561 | 120.607 | 38.2645 | 41.748 | 7.5577 | 120.7123 | -0.34332 | -0.40741 | 17.9489 | 55.8655 | -0.46234 | 120.6848 | 120.7855 | -0.31586 | -0.37537 | 0.082397 | 0.01831 | -0.045777 | 38.6902 | 7.9834 | 7.9651 | -0.15106 | 0.10986 | 0.050354 | -0.073243 | 18.3746 | -0.036621 | -0.086975 | 0.027465 | 121.138 | 121.0327 | 42.1738 | -121.1655 | 121.1105 | 121.2112 | 56.2912 | -121.1334
2480.4688 | 121.3028 | -0.41657 | 120.7672 | -0.020218 | 0.23537 | 0.26621 | 0.0023156 | 0.14381 | 0.047279 | 0.075447 | -0.0054932 | -0.0059793 | 0.081711 | 0.077009 | -0.20297 | 0.001647 | 120.6711 | 38.4247 | 44.5816 | 7.6584 | 120.6573 | -0.3067 | -0.39368 | 18.1412 | 56.0852 | -0.31128 | 120.6116 | 120.7352 | -0.29755 | -0.32501 | 0.10986 | 0.022888 | -0.10986 | 38.8412 | 8.075 | 8.0521 | -0.09613 | 0.11902 | 0.091553 | -0.15564 | 18.5577 | 0.10529 | 0.013733 | -0.032044 | 121.0739 | 121.0876 | 44.9982 | -121.1609 | 121.0281 | 121.1517 | 56.5018 | -121.0922
2482.1875 | 121.225 | -0.44403 | 120.7718 | -0.0049592 | 0.23644 | 0.30551 | 0.00017942 | 0.14573 | 0.056251 | 0.076943 | -0.013123 | -0.0025613 | 0.084488 | 0.080427 | -0.19977 | 0.0014334 | 120.575 | 38.1866 | 44.4031 | 7.5668 | 120.7123 | -0.39368 | -0.45319 | 18.1366 | 55.8563 | -0.47607 | 120.694 | 120.7626 | -0.33417 | -0.38452 | 0.050354 | -0.009155 | -0.05951 | 38.6307 | 8.0109 | 8.02 | -0.19684 | 0.10986 | 0.05951 | -0.07782 | 18.5806 | -0.032043 | -0.091553 | -0.009156 | 121.1563 | 121.019 | 44.8471 | -121.225 | 121.138 | 121.2067 | 56.3004 | -121.1563
2483.9688 | 121.1975 | -8.876 | 112.2345 | -0.012589 | 0.22939 | 0.28394 | 0.0018884 | 0.15577 | 0.056038 | 0.085488 | -0.013123 | -0.0093973 | 0.083206 | 0.076368 | -0.20212 | 0.0042106 | 112.0651 | 32.8445 | 39.592 | 0.3891 | 112.1796 | -8.7982 | -8.8211 | 10.08 | 47.9874 | -8.9813 | 112.0834 | 112.1887 | -8.7341 | -8.7891 | 0.07782 | 0.054932 | -0.054932 | 41.7206 | 9.2651 | 9.2102 | -0.16937 | 0.14191 | 0.086976 | -0.15106 | 18.956 | -0.10529 | -0.19226 | -0.045776 | 121.0556 | 120.9412 | 48.468 | -121.0556 | 120.9595 | 121.0648 | 56.8634 | -121.0236
2485.6719 | 121.1288 | -8.9264 | 112.2391 | -0.012589 | 0.23323 | 0.28607 | 0.0014612 | 0.15897 | 0.065651 | 0.085701 | -0.013123 | -0.0021341 | 0.083206 | 0.078932 | -0.19891 | 0.00015159 | 112.056 | 32.7072 | 39.4363 | 0.33875 | 112.1796 | -8.8211 | -8.8715 | 10.1074 | 47.8043 | -9.1324 | 112.1292 | 112.2299 | -8.7616 | -8.8486 | 0.10529 | 0.054932 | -0.05951 | 41.6336 | 9.2651 | 9.2102 | -0.18311 | 0.16479 | 0.07782 | -0.10986 | 19.0338 | -0.20599 | -0.28381 | -0.009156 | 121.106 | 120.9824 | 48.3627 | -121.1105 | 121.0556 | 121.1563 | 56.7307 | -121.0876
2487.4375 | 121.138 | -8.8257 | 112.3764 | -0.0049592 | 0.23366 | 0.28821 | 0.003811 | 0.1547 | 0.059455 | 0.083992 | 0.0021363 | -0.0070475 | 0.086411 | 0.075086 | -0.20276 | 0.0018606 | 112.2253 | 32.8629 | 39.5782 | 0.47607 | 112.2025 | -8.7112 | -8.7708 | 10.3683 | 48.2254 | -8.9035 | 112.1658 | 112.2986 | -8.6884 | -8.7296 | 0.11444 | 0.054932 | -0.17395 | 41.6885 | 9.3018 | 9.2468 | -0.15106 | 0.13733 | 0.096131 | -0.21057 | 19.194 | -0.077819 | -0.17395 | -0.07782 | 121.0281 | 121.051 | 48.4039 | -121.1472 | 120.9915 | 121.1243 | 57.0511 | -121.106
2489.1406 | 121.2341 | -10.0937 | 111.0626 | 0.0026703 | 0.22875 | 0.28693 | -0.00024778 | 0.1547 | 0.055824 | 0.089333 | 0.0021363 | -0.0070475 | 0.081924 | 0.078077 | -0.20404 | 0.0027152 | 112.0102 | 32.4188 | 39.2441 | 0.2655 | 111.9415 | -9.05 | -9.082 | 10.2814 | 47.8958 | -9.256 | 111.9553 | 112.0789 | -8.876 | -8.9264 | 1.0437 | 1.0117 | 0.87891 | 42.5125 | 10.3592 | 9.3475 | 0.94757 | 1.2177 | 1.1673 | 0.89264 | 20.3751 | 0.83771 | -0.32959 | 1.0162 | 122.0352 | 122.1039 | 49.3378 | -120.1447 | 122.0489 | 122.1725 | 57.9895 | -119.989
2490.9219 | 121.1838 | -18.4433 | 103.7384 | -0.012589 | 0.22704 | 0.72272 | 0.001034 | 0.17521 | 0.072914 | 0.10172 | -0.0054932 | -0.0044839 | 0.08342 | 0.080854 | -0.20083 | 0.00079259 | 101.8845 | 26.4908 | 33.8974 | -7.7362 | 102.3102 | -18.3929 | -18.4296 | 1.5289 | 40.2878 | -16.8503 | 103.2028 | 103.7842 | -17.189 | -16.9098 | 0.050354 | 0.013733 | -1.4282 | 44.9341 | 10.7071 | 10.6934 | -1.8539 | 1.2543 | 1.5335 | -0.53558 | 19.9722 | 1.593 | 0.059509 | 0.045777 | 120.7535 | 120.3278 | 52.3407 | -122.168 | 121.6461 | 122.2275 | 58.7311 | -120.6482
2492.7031 | 121.0236 | -70.9305 | 49.6674 | -0.0049592 | 0.20162 | 3.6064 | 0.0018884 | 0.24656 | 0.12012 | 0.16944 | 0.0021363 | -0.0070475 | 0.080429 | 0.080427 | -0.19955 | 0.003356 | 49.3607 | -6.4682 | 3.9185 | -52.4963 | 49.5529 | -70.9396 | -70.7703 | -49.324 | -9.8511 | -71.022 | 49.855 | 49.8505 | -70.8389 | -71.1365 | -0.009155 | 0.16022 | -0.11444 | 64.4623 | 18.4341 | 18.2739 | -0.3067 | 0.091553 | -0.20599 | 0.18768 | 21.6064 | -0.091553 | 0.11444 | 0.18311 | 120.4834 | 120.2911 | 74.8489 | -120.4376 | 120.7855 | 120.7809 | 61.0794 | -120.8038
2494.4844 | 120.8542 | -80.8319 | 39.6194 | -0.020218 | 0.1967 | 6.2152 | 0.001034 | 0.26215 | 0.13615 | 0.18354 | -0.0054932 | -0.0053385 | 0.080429 | 0.085127 | -0.1987 | 0.00057899 | 39.1205 | -12.4603 | -1.4236 | -60.8688 | 39.5645 | -80.452 | -80.3284 | -59.23 | -19.4229 | -80.9555 | 39.418 | 39.4913 | -80.7083 | -80.8594 | 0.37994 | 0.50354 | -0.054932 | 68.3716 | 19.9631 | 19.4595 | -0.49896 | 0.1236 | -0.027466 | -0.20142 | 21.6019 | -0.1236 | -0.09613 | -0.12817 | 120.3964 | 119.9524 | 79.4083 | -119.9478 | 120.2499 | 120.3232 | 61.409 | -120.4788
2496.2188 | 120.6894 | -86.2564 | 34.1721 | -0.012589 | 0.19798 | 5.7546 | -0.002384 | 0.26856 | 0.14469 | 0.19166 | -0.013123 | 0.00042948 | 0.08107 | 0.08534 | -0.19549 | 0.003356 | 33.8516 | -15.7379 | -4.5502 | -65.1352 | 34.2957 | -85.8032 | -85.611 | -63.2675 | -23.5336 | -85.4691 | 35.0784 | 35.1562 | -85.1349 | -85.3729 | 0.45319 | 0.64545 | 0.1236 | 70.5185 | 21.1212 | 20.4758 | -0.32043 | 1.1215 | 0.88348 | 0.90637 | 22.9889 | 0.78735 | -0.09613 | 0.98419 | 120.5521 | 120.108 | 81.7062 | -119.783 | 121.3348 | 121.4127 | 62.7228 | -119.545
2498 | 120.4514 | -85.4782 | 34.7763 | -0.027847 | 0.19948 | 6.8932 | 0.0029566 | 0.26856 | 0.13807 | 0.18653 | -0.0054932 | -0.0036295 | 0.082138 | 0.084059 | -0.19742 | 0.0044242 | 36.1313 | -14.1907 | -3.717 | -62.265 | 36.3464 | -83.4274 | -83.2123 | -60.3882 | -20.8282 | -82.8644 | 37.3672 | 37.413 | -82.9193 | -83.2123 | 2.0508 | 2.2659 | 1.5701 | 71.2875 | 23.2132 | 20.9473 | 1.355 | 2.5589 | 2.2659 | 2.5909 | 25.09 | 2.6138 | 0.3479 | 2.6367 | 121.8246 | 121.6095 | 81.7612 | -117.9886 | 122.8455 | 122.8912 | 64.65 | -117.9886
2499.7812 | 120.2316 | -87.7579 | 32.4142 | -0.0049592 | 0.19734 | 6.8932 | 0.003811 | 0.27305 | 0.14747 | 0.197 | 0.0021363 | -0.0034159 | 0.082565 | 0.085127 | -0.19934 | 0.0029288 | 30.1666 | -17.3538 | -6.0791 | -67.6895 | 31.4941 | -87.6755 | -87.5336 | -64.6362 | -25.4242 | -87.8952 | 32.3181 | 32.1991 | -87.8448 | -88.0371 | 0.082398 | 0.22431 | -0.9201 | 70.4041 | 20.0684 | 19.8441 | -2.2476 | -0.086975 | -0.27923 | -0.096131 | 23.1216 | -0.13733 | 0.14191 | -0.21515 | 119.252 | 117.9245 | 81.6788 | -119.9478 | 120.076 | 119.957 | 62.3337 | -120.4514
2501.5 | 120.9183 | -119.5312 | 1.149 | -0.012589 | 0.17683 | 0.74408 | 0.00060662 | 0.32603 | 0.17182 | 0.23844 | -0.013123 | -0.0057657 | 0.082565 | 0.084059 | -0.19742 | 0.0052786 | 1.0208 | -35.5637 | -22.8561 | -93.0817 | 1.0757 | -119.6823 | -119.4351 | -95.4803 | -54.9728 | -119.5129 | 1.0574 | 1.1124 | -119.3573 | -119.6091 | -0.15106 | 0.09613 | -0.073242 | 83.9676 | 26.4496 | 26.3535 | -0.12817 | 0.17395 | -0.07782 | -0.091553 | 24.0509 | 0.018311 | 0.096131 | -0.036621 | 120.607 | 120.5521 | 96.6751 | -120.5841 | 120.5887 | 120.6436 | 64.5584 | -120.7581
2503.2969 | 121.0648 | -119.014 | 1.7349 | -0.0049592 | 0.17833 | 0.74451 | 0.0033838 | 0.32645 | 0.16883 | 0.23801 | -0.020752 | -0.0076883 | 0.079575 | 0.084059 | -0.20062 | 0.0057058 | 1.5701 | -35.1379 | -22.5494 | -92.569 | 1.6708 | -119.133 | -118.9178 | -94.8303 | -54.3732 | -118.9728 | 1.6525 | 1.6983 | -118.8354 | -119.1055 | -0.11902 | 0.09613 | -0.064087 | 83.876 | 26.445 | 26.3489 | -0.16479 | 0.17853 | -0.091553 | -0.082397 | 24.1837 | 0.041199 | 0.13275 | -0.036621 | 120.6848 | 120.5841 | 96.4645 | -120.6528 | 120.6665 | 120.7123 | 64.6408 | -120.8405
2505 | 121.0052 | -118.5608 | 2.2202 | -0.0049592 | 0.17705 | 0.74259 | 0.0027428 | 0.32539 | 0.17353 | 0.23652 | -0.013123 | -0.0083291 | 0.081284 | 0.083418 | -0.19613 | 0.006774 | 2.0737 | -34.7717 | -22.2748 | -92.1204 | 2.1606 | -118.6798 | -118.4418 | -94.2352 | -53.8834 | -118.5745 | 2.1378 | 2.1835 | -118.3823 | -118.6478 | -0.11902 | 0.11902 | -0.059509 | 83.7891 | 26.4404 | 26.3214 | -0.14648 | 0.17853 | -0.086975 | -0.082398 | 24.3256 | -0.013733 | 0.073242 | -0.036621 | 120.7214 | 120.6345 | 96.286 | -120.6619 | 120.6985 | 120.7443 | 64.6774 | -120.8679
2506.7969 | 121.0876 | -117.9337 | 2.8519 | 0.0026703 | 0.18047 | 0.7396 | -0.00088858 | 0.32624 | 0.17823 | 0.23951 | -0.013123 | -0.0038431 | 0.080215 | 0.085127 | -0.19485 | 0.0025016 | 2.71 | -34.3369 | -21.9131 | -91.5848 | 2.8336 | -118.0344 | -117.8329 | -93.4113 | -53.3203 | -117.9382 | 2.7832 | 2.8381 | -117.7597 | -118.0161 | -0.10071 | 0.10071 | -0.018311 | 83.5968 | 26.3489 | 26.2482 | -0.14191 | 0.17395 | -0.082397 | -0.068665 | 24.5224 | -0.004577 | 0.07782 | -0.013733 | 120.7672 | 120.6436 | 96.0205 | -120.6848 | 120.7169 | 120.7718 | 64.6133 | -120.8679
2508.5156 | 121.0144 | -117.7826 | 3.0441 | -0.0049592 | 0.18089 | 0.73853 | 0.0050928 | 0.32816 | 0.17759 | 0.23908 | -0.0054932 | -0.0029885 | 0.082565 | 0.084272 | -0.19827 | 0.003997 | 2.8427 | -34.1858 | -21.8124 | -91.3742 | 3.0167 | -117.9062 | -117.6636 | -93.187 | -53.2471 | -117.865 | 2.9984 | 3.0396 | -117.5812 | -117.8696 | -0.1236 | 0.11902 | -0.027465 | 83.5968 | 26.4084 | 26.2894 | -0.20142 | 0.20142 | -0.086975 | -0.045776 | 24.5956 | -0.082397 | 0.004578 | -0.004577 | 120.7993 | 120.6253 | 95.9702 | -120.7077 | 120.7809 | 120.8221 | 64.5355 | -120.9137
2510.2812 | 121.0144 | -117.897 | 2.9892 | -0.020218 | 0.18282 | 0.74088 | 0.0044518 | 0.32688 | 0.17631 | 0.23737 | -0.013123 | -0.0049111 | 0.083206 | 0.084272 | -0.19934 | 0.0057058 | 2.742 | -34.1583 | -21.7484 | -91.4108 | 2.9205 | -117.9886 | -117.7689 | -93.1503 | -53.3432 | -117.9611 | 2.9114 | 2.9617 | -117.7002 | -117.9474 | -0.091552 | 0.12817 | -0.068665 | 83.7387 | 26.4862 | 26.358 | -0.24719 | 0.19684 | -0.050354 | -0.07782 | 24.7467 | -0.064087 | -0.013733 | -0.027466 | 120.8176 | 120.639 | 96.1487 | -120.7581 | 120.8084 | 120.8588 | 64.5538 | -120.9366
2512.0469 | 121.0007 | -117.9474 | 2.9663 | 0.0026703 | 0.18153 | 0.74259 | 0.0033838 | 0.32902 | 0.17588 | 0.23994 | -0.020752 | -0.0042703 | 0.082565 | 0.083845 | -0.19891 | 0.0069876 | 2.7328 | -34.053 | -21.7255 | -91.3834 | 2.9022 | -118.0069 | -117.7826 | -92.9764 | -53.3203 | -117.9794 | 2.8931 | 2.9388 | -117.7231 | -117.9932 | -0.059509 | 0.16479 | -0.064087 | 83.8943 | 26.564 | 26.3992 | -0.23346 | 0.22431 | -0.045776 | -0.073243 | 24.971 | -0.032043 | 0.013733 | -0.027466 | 120.8496 | 120.6802 | 96.2219 | -120.7489 | 120.8405 | 120.8862 | 64.6271 | -120.9595
2513.7656 | 120.9824 | -117.8833 | 3.0167 | -0.012589 | 0.18346 | 0.7428 | 0.00039302 | 0.32923 | 0.18143 | 0.24122 | -0.0054932 | -0.0036295 | 0.083206 | 0.087477 | -0.19528 | 0.0046378 | 2.8107 | -33.9294 | -21.6339 | -91.2689 | 2.9572 | -117.9657 | -117.7414 | -92.6971 | -53.2654 | -117.9611 | 2.9388 | 2.98 | -117.6956 | -117.9474 | -0.082397 | 0.14191 | -0.05951 | 83.9539 | 26.6144 | 26.4725 | -0.20599 | 0.18768 | -0.064087 | -0.07782 | 25.1862 | -0.07782 | -0.013733 | -0.036621 | 120.8405 | 120.694 | 96.2494 | -120.7581 | 120.8221 | 120.8633 | 64.6179 | -120.9641
2515.5312 | 121.1426 | -117.8146 | 3.0121 | 0.0026703 | 0.17748 | 0.74686 | 0.0031702 | 0.3303 | 0.17289 | 0.24143 | -0.013123 | -0.0091837 | 0.081924 | 0.083631 | -0.20147 | 0.0048514 | 2.8656 | -33.7006 | -21.4371 | -91.127 | 2.9251 | -117.8879 | -117.6865 | -92.4088 | -53.0502 | -117.7643 | 2.9251 | 2.9617 | -117.6224 | -117.8833 | -0.073242 | 0.12817 | -0.086975 | 84.1141 | 26.6876 | 26.5594 | -0.14648 | 0.19226 | -0.068665 | -0.086975 | 25.4059 | 0.050354 | 0.11902 | -0.050354 | 120.7397 | 120.6802 | 96.3776 | -120.6985 | 120.7397 | 120.7764 | 64.7644 | -120.8954
2517.25 | 121.0922 | -117.8513 | 3.0396 | -0.012589 | 0.18047 | 0.75049 | 0.00082022 | 0.33222 | 0.17567 | 0.23972 | -0.013123 | -0.0079019 | 0.081497 | 0.084486 | -0.1987 | 0.0057058 | 2.9068 | -33.5724 | -21.3364 | -91.0492 | 2.9343 | -117.9153 | -117.6865 | -92.244 | -52.8946 | -117.778 | 2.9205 | 2.9572 | -117.5812 | -117.8833 | -0.064087 | 0.16479 | -0.10529 | 84.2789 | 26.8021 | 26.6373 | -0.13275 | 0.27008 | -0.032044 | -0.11902 | 25.6073 | 0.073242 | 0.10529 | -0.082398 | 120.7855 | 120.7581 | 96.5149 | -120.726 | 120.7718 | 120.8084 | 64.9567 | -120.9229
2519.0312 | 121.0556 | -117.6636 | 3.1952 | -0.0049592 | 0.18346 | 0.74472 | 0.002102 | 0.33308 | 0.18143 | 0.23994 | -0.0054932 | -0.0040567 | 0.082352 | 0.087904 | -0.19549 | 0.002288 | 3.0304 | -33.5083 | -21.2814 | -90.8936 | 3.1448 | -117.7597 | -117.5537 | -91.9373 | -52.7893 | -117.7048 | 3.1219 | 3.1906 | -117.4942 | -117.7551 | -0.096131 | 0.10986 | -0.050354 | 84.1553 | 26.77 | 26.6602 | -0.16479 | 0.16937 | -0.091553 | -0.073242 | 25.7263 | -0.041199 | 0.050354 | -0.004577 | 120.8084 | 120.694 | 96.3821 | -120.7489 | 120.7855 | 120.8542 | 64.8743 | -120.9503
2520.7344 | 121.1472 | -117.7094 | 3.1219 | -0.0049592 | 0.18068 | 0.75006 | -0.0021704 | 0.3335 | 0.17716 | 0.2425 | -0.013123 | -0.0057657 | 0.079147 | 0.087477 | -0.19613 | 0.0054922 | 3.0258 | -33.3664 | -21.1761 | -90.8432 | 3.0579 | -117.7917 | -117.5537 | -91.7541 | -52.5375 | -117.6956 | 3.0075 | 3.0762 | -117.54 | -117.7597 | -0.082397 | 0.15564 | -0.064087 | 84.343 | 26.8662 | 26.7105 | -0.09613 | 0.16937 | -0.050354 | -0.11444 | 25.9552 | 0.013733 | 0.064087 | -0.045776 | 120.7672 | 120.7352 | 96.5332 | -120.6757 | 120.7169 | 120.7855 | 65.1718 | -120.8817
2522.5 | 121.0693 | -117.7505 | 3.1357 | -0.0049592 | 0.18495 | 0.74793 | 0.0014612 | 0.3335 | 0.18122 | 0.24207 | -0.013123 | -0.0021341 | 0.082352 | 0.084699 | -0.19677 | 0.0035696 | 2.916 | -33.3984 | -21.2036 | -90.8661 | 3.0579 | -117.8375 | -117.6453 | -91.6672 | -52.5009 | -117.8009 | 3.067 | 3.1082 | -117.5629 | -117.8375 | -0.086975 | 0.10529 | -0.07782 | 84.3521 | 26.8845 | 26.7792 | -0.21973 | 0.18768 | -0.086975 | -0.068664 | 26.0834 | -0.050354 | 0.036621 | -0.027466 | 120.8084 | 120.6665 | 96.5469 | -120.7809 | 120.8176 | 120.8588 | 65.2496 | -120.9732
2524.2188 | 121.0098 | -117.7505 | 3.154 | -0.0049592 | 0.18474 | 0.75113 | 0.00039302 | 0.3318 | 0.18229 | 0.24421 | -0.020752 | -0.0044839 | 0.083847 | 0.086622 | -0.19357 | 0.0037832 | 2.9205 | -33.3389 | -21.1029 | -90.8203 | 3.0853 | -117.8558 | -117.6178 | -91.5024 | -52.5879 | -117.8329 | 3.0899 | 3.1311 | -117.572 | -117.8329 | -0.10529 | 0.13275 | -0.068665 | 84.4116 | 26.9302 | 26.7975 | -0.23346 | 0.17853 | -0.082398 | -0.064087 | 26.2482 | -0.082398 | 0 | -0.022888 | 120.8359 | 120.6711 | 96.6476 | -120.7718 | 120.8405 | 120.8817 | 65.1627 | -120.9869
2525.9844 | 121.0373 | -117.8787 | 3.035 | -0.0049592 | 0.18453 | 0.75668 | 0.0025292 | 0.335 | 0.17438 | 0.24271 | -0.013123 | -0.0096109 | 0.082352 | 0.084059 | -0.19998 | 0.0065604 | 2.8885 | -33.1558 | -20.9015 | -90.7562 | 2.9388 | -117.9153 | -117.7139 | -91.3696 | -52.5192 | -117.8055 | 2.9388 | 2.98 | -117.6453 | -117.8879 | -0.036621 | 0.16479 | -0.09613 | 84.7229 | 27.1225 | 26.9577 | -0.14648 | 0.23346 | -0.009155 | -0.09613 | 26.5091 | 0.073242 | 0.082397 | -0.054931 | 120.8176 | 120.7672 | 96.9772 | -120.7489 | 120.8176 | 120.8588 | 65.3595 | -120.9229
2527.7656 | 121.0922 | -117.7734 | 3.1036 | -0.0049592 | 0.18089 | 0.75562 | 0.0029566 | 0.33372 | 0.17567 | 0.24336 | -0.013123 | -0.0091837 | 0.081924 | 0.085981 | -0.19806 | 0.0072012 | 2.948 | -33.0597 | -20.7687 | -90.7013 | 3.0167 | -117.8146 | -117.6132 | -91.1453 | -52.5009 | -117.7551 | 3.0441 | 3.0579 | -117.5674 | -117.8329 | -0.041199 | 0.16022 | -0.086975 | 84.7137 | 27.0721 | 26.9119 | -0.15564 | 0.20599 | -0.05951 | -0.05951 | 26.6281 | 0.01831 | 0.07782 | -0.045777 | 120.7901 | 120.7214 | 97.0047 | -120.7169 | 120.8176 | 120.8313 | 65.2725 | -120.9366
2529.5469 | 121.1105 | -117.8421 | 3.0075 | -0.012589 | 0.17769 | 0.75797 | -0.00067498 | 0.33671 | 0.1793 | 0.24186 | 0.0021363 | -0.0070475 | 0.080429 | 0.083204 | -0.19613 | 0.005065 | 2.8839 | -33.0185 | -20.723 | -90.7059 | 2.9297 | -117.9153 | -117.6865 | -91.0584 | -52.5055 | -117.8421 | 2.9068 | 2.9663 | -117.6636 | -117.9199 | -0.073242 | 0.15564 | -0.07782 | 84.8236 | 27.1362 | 26.9806 | -0.1236 | 0.17853 | -0.07782 | -0.10071 | 26.7838 | 0 | 0.07782 | -0.041198 | 120.7718 | 120.726 | 97.1191 | -120.694 | 120.7489 | 120.8084 | 65.3366 | -120.9274
2531.3281 | 121.0236 | -117.9199 | 3.0167 | -0.012589 | 0.18282 | 0.75946 | 0.0029566 | 0.33863 | 0.18015 | 0.24613 | -0.013123 | -0.0042703 | 0.081924 | 0.085768 | -0.1987 | 0.0052786 | 2.7924 | -33.0597 | -20.7367 | -90.715 | 2.9663 | -117.984 | -117.7689 | -91.0172 | -52.5787 | -117.9382 | 2.9114 | 2.9709 | -117.7231 | -117.9657 | -0.064087 | 0.15106 | -0.050354 | 84.8602 | 27.2049 | 27.0538 | -0.2243 | 0.19684 | -0.045776 | -0.10529 | 26.9028 | -0.01831 | 0.027466 | -0.045777 | 120.8862 | 120.7123 | 97.1832 | -120.7855 | 120.8313 | 120.8908 | 65.3412 | -120.9824
2533.0312 | 121.0556 | -117.9153 | 2.9709 | -0.0049592 | 0.18239 | 0.7616 | 0.00552 | 0.34077 | 0.17823 | 0.24635 | -0.013123 | -0.0072611 | 0.083847 | 0.086408 | -0.20126 | 0.003997 | 2.8702 | -32.9132 | -20.549 | -90.5914 | 2.8885 | -117.9794 | -117.7597 | -90.7196 | -52.6199 | -117.8513 | 2.861 | 2.9343 | -117.6956 | -117.9565 | -0.064087 | 0.15564 | -0.082397 | 85.0021 | 27.3239 | 27.1683 | -0.10071 | 0.21973 | -0.041199 | -0.10986 | 27.1957 | 0.064087 | 0.10529 | -0.036621 | 120.8038 | 120.7855 | 97.3663 | -120.7306 | 120.7764 | 120.8496 | 65.2954 | -120.9274
2534.8281 | 121.1151 | -115.0085 | 5.7953 | -0.012589 | 0.18367 | 0.74558 | 0.00039302 | 0.33436 | 0.18037 | 0.2425 | 0.0021363 | -0.0064065 | 0.081924 | 0.085127 | -0.19421 | 0.0025016 | 5.7587 | -31.1966 | -18.9468 | -88.179 | 5.6992 | -115.1093 | -114.8758 | -87.7121 | -49.9969 | -114.9994 | 5.7175 | 5.7449 | -114.8529 | -115.0726 | -0.10071 | 0.13275 | -0.09613 | 83.812 | 26.8295 | 26.6968 | -0.036621 | 0.15564 | -0.064087 | -0.07782 | 27.2964 | 0.009155 | 0.073242 | -0.050354 | 120.7077 | 120.7672 | 96.0617 | -120.6711 | 120.726 | 120.7535 | 65.0116 | -120.8679
2536.6094 | 121.138 | -115.0589 | 5.7632 | -0.0049592 | 0.1841 | 0.74686 | 0.0016748 | 0.33479 | 0.18165 | 0.24378 | -0.013123 | -0.0046975 | 0.082993 | 0.086836 | -0.19549 | 0.0035696 | 5.6992 | -31.1691 | -18.8965 | -88.1332 | 5.69 | -115.1459 | -114.9353 | -87.561 | -50.0473 | -115.0497 | 5.6808 | 5.7266 | -114.8895 | -115.1047 | -0.086975 | 0.1236 | -0.073243 | 83.8898 | 26.9257 | 26.8021 | -0.064087 | 0.16937 | -0.045776 | -0.082398 | 27.4979 | 0.009155 | 0.054931 | -0.036621 | 120.7489 | 120.7581 | 96.1624 | -120.6985 | 120.7397 | 120.7855 | 65.0116 | -120.8679
2538.3906 | 121.1517 | -115.3336 | 5.4703 | -0.0049592 | 0.18816 | 0.71311 | 0.0033838 | 0.32175 | 0.16691 | 0.23203 | 0.0021363 | -0.0066201 | 0.083847 | 0.084699 | -0.19912 | 0.006774 | 5.4199 | -34.6527 | -22.8836 | -89.621 | 5.4291 | -115.4434 | -115.2054 | -87.8037 | -50.3632 | -115.3107 | 5.397 | 5.4337 | -115.1733 | -115.4251 | -0.10986 | 0.12817 | -0.041199 | 80.6808 | 25.7126 | 25.5844 | -0.050354 | 0.16022 | -0.091553 | -0.073242 | 27.5299 | 0.022888 | 0.11444 | -0.036621 | 120.7626 | 120.7535 | 92.45 | -120.6757 | 120.7306 | 120.7672 | 64.9704 | -120.8954
2540.0938 | 121.1792 | -115.6403 | 5.159 | -0.012589 | 0.18538 | 0.70926 | -3.4178e-05 | 0.32453 | 0.16563 | 0.2299 | -0.0054932 | -0.0091837 | 0.084274 | 0.085768 | -0.19677 | 0.0052786 | 5.072 | -35.2066 | -23.5107 | -90.0284 | 5.1041 | -115.741 | -115.5167 | -87.9822 | -50.8118 | -115.6219 | 5.1178 | 5.1361 | -115.4617 | -115.7181 | -0.10071 | 0.1236 | -0.054932 | 80.4337 | 25.6119 | 25.4883 | -0.086976 | 0.17853 | -0.07782 | -0.041199 | 27.6581 | 0.018311 | 0.096131 | -0.022889 | 120.7443 | 120.7123 | 92.1295 | -120.6757 | 120.7581 | 120.7764 | 64.8285 | -120.8771
2541.8594 | 121.138 | -115.4572 | 5.3833 | -0.0049592 | 0.18666 | 0.71695 | 0.0016748 | 0.3256 | 0.17118 | 0.23481 | -0.0054932 | -0.0061929 | 0.081497 | 0.085554 | -0.19827 | 0.0061332 | 5.2551 | -34.4284 | -22.6318 | -89.6118 | 5.3238 | -115.5487 | -115.329 | -87.6663 | -50.6241 | -115.4617 | 5.3009 | 5.3558 | -115.2832 | -115.535 | -0.091553 | 0.12817 | -0.059509 | 81.0287 | 25.8453 | 25.7172 | -0.12817 | 0.17395 | -0.07782 | -0.082398 | 27.7908 | -0.004578 | 0.073242 | -0.027466 | 120.7809 | 120.7123 | 92.8253 | -120.7123 | 120.7581 | 120.813 | 64.8331 | -120.9183
2543.5781 | 121.0007 | -115.7272 | 5.1819 | -0.012589 | 0.19286 | 0.71973 | -0.0011024 | 0.32517 | 0.17823 | 0.23887 | -0.0054932 | -0.0027749 | 0.083847 | 0.087049 | -0.19442 | 0.0020744 | 5.072 | -34.3414 | -22.4991 | -89.6988 | 5.0949 | -115.773 | -115.6082 | -87.7396 | -50.972 | -115.7593 | 5.1086 | 5.127 | -115.5487 | -115.7776 | -0.045776 | 0.11902 | -0.086975 | 81.3858 | 26.0284 | 25.9094 | -0.10986 | 0.17853 | -0.050354 | -0.073242 | 27.9877 | -0.032043 | 0.018311 | -0.054932 | 120.8221 | 120.7993 | 93.2281 | -120.7901 | 120.8359 | 120.8542 | 64.7552 | -120.9595
2545.3438 | 121.1655 | -116.1484 | 4.6783 | -0.0049592 | 0.19093 | 0.68448 | 0.0025292 | 0.31471 | 0.16071 | 0.22327 | 0.0021363 | -0.010893 | 0.084915 | 0.084913 | -0.1987 | 0.0063468 | 4.5547 | -38.1134 | -26.8707 | -91.4932 | 4.6051 | -116.2628 | -116.0339 | -88.092 | -51.5717 | -116.1438 | 4.5822 | 4.6463 | -115.9882 | -116.2399 | -0.11444 | 0.11444 | -0.073242 | 78.035 | 24.6552 | 24.5407 | -0.1236 | 0.16022 | -0.091553 | -0.096131 | 28.0563 | 0.004577 | 0.09613 | -0.032044 | 120.7535 | 120.7031 | 89.2776 | -120.7123 | 120.7306 | 120.7947 | 64.5767 | -120.9183
2547.0938 | 121.0144 | -116.3132 | 4.6051 | -0.012589 | 0.19969 | 0.67508 | -0.0011024 | 0.31236 | 0.16712 | 0.22498 | -0.0054932 | -0.0012795 | 0.085556 | 0.088972 | -0.19528 | 0.0042106 | 4.4815 | -38.8138 | -27.681 | -91.7725 | 4.5181 | -116.3773 | -116.1896 | -88.0646 | -51.7319 | -116.3361 | 4.5227 | 4.541 | -116.1163 | -116.3818 | -0.064087 | 0.1236 | -0.086976 | 77.4994 | 24.5407 | 24.4171 | -0.1236 | 0.19684 | -0.068665 | -0.082398 | 28.2486 | -0.022889 | 0.045776 | -0.064087 | 120.8313 | 120.7947 | 88.6322 | -120.7947 | 120.8359 | 120.8542 | 64.5813 | -120.9869
2548.8281 | 121.1517 | -116.7664 | 4.0878 | -0.0049592 | 0.20247 | 0.63428 | 0.00552 | 0.29697 | 0.1496 | 0.2096 | 0.0021363 | -0.0091837 | 0.08342 | 0.087263 | -0.20318 | 0.006774 | 4.0237 | -43.2358 | -32.7484 | -94.3039 | 4.0054 | -116.8671 | -116.6473 | -88.4949 | -52.3087 | -116.6931 | 3.9642 | 4.0237 | -116.5787 | -116.8396 | -0.10071 | 0.11902 | -0.082398 | 73.5306 | 22.4625 | 22.3434 | -0.064087 | 0.18768 | -0.073243 | -0.1236 | 28.2715 | 0.073242 | 0.14648 | -0.064087 | 120.7718 | 120.7901 | 84.0179 | -120.7352 | 120.7306 | 120.7901 | 64.4577 | -120.9274
2550.5938 | 121.051 | -115.6082 | 5.3238 | -0.012589 | 0.20546 | 0.63043 | 0.0025292 | 0.29633 | 0.15302 | 0.21003 | -0.013123 | -0.0046975 | 0.088333 | 0.086195 | -0.19656 | 0.0054922 | 5.127 | -42.3111 | -31.9748 | -92.6743 | 5.2551 | -115.6952 | -115.4846 | -87.2452 | -51.329 | -115.6357 | 5.2277 | 5.2643 | -115.448 | -115.6631 | -0.086975 | 0.1236 | -0.068665 | 73.2971 | 22.934 | 22.8104 | -0.19684 | 0.16022 | -0.054932 | -0.096131 | 28.363 | -0.027466 | 0.027466 | -0.05951 | 120.8633 | 120.7352 | 83.6334 | -120.8084 | 120.8359 | 120.8725 | 64.2792 | -120.9869
2552.2969 | 121.0739 | -115.8142 | 5.1086 | -0.012589 | 0.20631 | 0.63065 | 0.00082022 | 0.29612 | 0.15345 | 0.21046 | -0.013123 | -0.0032021 | 0.08577 | 0.08534 | -0.19613 | 0.0046378 | 4.921 | -42.5629 | -32.2998 | -92.8802 | 5.0491 | -115.8966 | -115.6815 | -87.3047 | -51.5579 | -115.8508 | 5.0171 | 5.0629 | -115.654 | -115.8829 | -0.082397 | 0.13275 | -0.05951 | 73.2513 | 22.934 | 22.8012 | -0.18768 | 0.16022 | -0.068665 | -0.091553 | 28.5095 | -0.036621 | 0.032044 | -0.045777 | 120.8633 | 120.7352 | 83.5144 | -120.7901 | 120.8313 | 120.8771 | 64.2563 | -120.9915
2554.0625 | 121.0464 | -116.0019 | 4.9255 | -0.012589 | 0.20311 | 0.63684 | 0.0033838 | 0.29804 | 0.14896 | 0.21323 | -0.013123 | -0.0098245 | 0.085556 | 0.085768 | -0.19934 | 0.0080558 | 4.7882 | -42.2607 | -31.9656 | -92.8253 | 4.7928 | -116.0477 | -115.8691 | -87.2726 | -51.6403 | -115.9515 | 4.8019 | 4.8477 | -115.8005 | -116.0568 | -0.045776 | 0.13275 | -0.13275 | 73.7412 | 23.1766 | 23.0438 | -0.13733 | 0.20142 | -0.054932 | -0.1236 | 28.7292 | 0.050354 | 0.10529 | -0.07782 | 120.7947 | 120.7901 | 84.0363 | -120.7947 | 120.8038 | 120.8496 | 64.3616 | -120.9824
2555.8438 | 121.0785 | -116.1484 | 4.7424 | -0.012589 | 0.20717 | 0.63278 | 0.0040246 | 0.29655 | 0.15644 | 0.21024 | -0.0054932 | -0.0040567 | 0.087692 | 0.087904 | -0.19806 | 0.0063468 | 4.5639 | -42.8192 | -32.6111 | -93.132 | 4.6829 | -116.2537 | -116.0431 | -87.41 | -51.9882 | -116.185 | 4.6646 | 4.7104 | -115.9973 | -116.2399 | -0.10529 | 0.10528 | -0.05951 | 73.3292 | 23.0164 | 22.9111 | -0.17853 | 0.15106 | -0.091553 | -0.07782 | 28.7384 | -0.036622 | 0.054931 | -0.032044 | 120.8313 | 120.7123 | 83.5373 | -120.7855 | 120.813 | 120.8588 | 64.1602 | -120.9824
2557.5469 | 121.051 | -116.3498 | 4.5685 | -0.027847 | 0.21016 | 0.63129 | 0.0029566 | 0.29462 | 0.1558 | 0.21323 | -0.0054932 | -0.0036295 | 0.087906 | 0.089399 | -0.19635 | 0.005065 | 4.3488 | -42.9565 | -32.7026 | -93.2785 | 4.509 | -116.4413 | -116.2125 | -87.5198 | -52.3407 | -116.4093 | 4.4769 | 4.541 | -116.1392 | -116.4047 | -0.091553 | 0.13733 | -0.059509 | 73.3932 | 23.0713 | 22.934 | -0.21973 | 0.21057 | -0.054932 | -0.091552 | 28.83 | -0.05951 | -0.004578 | -0.027465 | 120.8588 | 120.6985 | 83.6472 | -120.7809 | 120.8267 | 120.8908 | 64.0091 | -120.9732
2559.3125 | 121.0281 | -116.5009 | 4.39 | -0.012589 | 0.19457 | 0.72614 | 0.00082022 | 0.33051 | 0.17844 | 0.24079 | -0.0054932 | -0.0032021 | 0.085983 | 0.088972 | -0.194 | 0.0057058 | 4.1794 | -35.2386 | -23.7717 | -90.2527 | 4.3488 | -116.6199 | -116.3727 | -87.3276 | -52.2629 | -116.6016 | 4.3259 | 4.3716 | -116.3406 | -116.5741 | -0.11902 | 0.12817 | -0.041199 | 81.2622 | 26.2482 | 26.12 | -0.21057 | 0.16022 | -0.073243 | -0.064087 | 29.1733 | -0.10071 | -0.027465 | -0.018311 | 120.8496 | 120.6802 | 92.7292 | -120.7626 | 120.8267 | 120.8725 | 64.238 | -120.9641
2561.0312 | 121.0327 | -116.6702 | 4.2252 | -0.012589 | 0.19948 | 0.72507 | -0.00067498 | 0.32752 | 0.17524 | 0.24101 | 0.0021363 | -0.0025613 | 0.086197 | 0.087049 | -0.19336 | 0.0059196 | 4.0787 | -35.5225 | -24.1562 | -90.4587 | 4.1519 | -116.7572 | -116.5283 | -87.3596 | -52.4368 | -116.6702 | 4.1336 | 4.1794 | -116.4917 | -116.7526 | -0.086975 | 0.14191 | -0.073242 | 81.1478 | 26.2115 | 26.0696 | -0.14648 | 0.17853 | -0.082398 | -0.091553 | 29.3106 | 0 | 0.082398 | -0.045777 | 120.8221 | 120.7489 | 92.514 | -120.7535 | 120.8038 | 120.8496 | 64.2334 | -120.9778
2562.7969 | 121.1288 | -116.272 | 4.5593 | 0.0026703 | 0.19563 | 0.73938 | -3.4178e-05 | 0.33286 | 0.17802 | 0.24378 | -0.0054932 | -0.0057657 | 0.084061 | 0.089399 | -0.19763 | 0.0078422 | 4.4037 | -33.8425 | -22.3022 | -89.566 | 4.5456 | -116.3818 | -116.1621 | -86.8332 | -52.1027 | -116.2674 | 4.5456 | 4.6188 | -116.0843 | -116.3406 | -0.10986 | 0.10986 | -0.013733 | 82.4295 | 26.7059 | 26.5961 | -0.15564 | 0.18768 | -0.068664 | -0.013733 | 29.4388 | 0.004578 | 0.073242 | 0.059509 | 120.8176 | 120.6757 | 93.9697 | -120.7214 | 120.8176 | 120.8908 | 64.1693 | -120.9
2564.5781 | 121.1746 | -117.1417 | 3.6987 | -0.0049592 | 0.20482 | 0.63834 | 0.0040246 | 0.29655 | 0.1496 | 0.21452 | -0.0054932 | -0.010679 | 0.085983 | 0.085981 | -0.20083 | 0.0080558 | 3.5339 | -43.5745 | -33.5312 | -93.8736 | 3.6072 | -117.2699 | -117.0639 | -87.854 | -53.302 | -117.1234 | 3.5843 | 3.6255 | -116.9907 | -117.2653 | -0.12817 | 0.07782 | -0.091552 | 73.5672 | 23.2681 | 23.1903 | -0.16479 | 0.15106 | -0.1236 | -0.11444 | 29.2877 | 0.018311 | 0.14191 | -0.073242 | 120.7489 | 120.6757 | 83.6105 | -120.7626 | 120.726 | 120.7672 | 63.8397 | -120.9641
2566.2969 | 121.0831 | -116.629 | 4.2755 | -0.0049592 | 0.20995 | 0.64111 | 0.0044518 | 0.29997 | 0.15623 | 0.21409 | -0.020752 | -0.0061929 | 0.089828 | 0.087049 | -0.19571 | 0.0061332 | 4.0649 | -42.9794 | -32.9498 | -93.2648 | 4.1977 | -116.7114 | -116.51 | -87.1948 | -52.9587 | -116.6473 | 4.1794 | 4.2389 | -116.4688 | -116.716 | -0.082398 | 0.11902 | -0.07782 | 73.6496 | 23.3643 | 23.2452 | -0.21057 | 0.16022 | -0.086975 | -0.096131 | 29.4342 | -0.018311 | 0.068664 | -0.036621 | 120.8267 | 120.694 | 83.6792 | -120.7855 | 120.8084 | 120.8679 | 63.6703 | -120.9915
2568.0469 | 121.1609 | -116.2811 | 4.5364 | -0.012589 | 0.2076 | 0.64133 | 0.00082022 | 0.30082 | 0.15708 | 0.21687 | 0.0021363 | -0.0066201 | 0.086411 | 0.088972 | -0.19507 | 0.0078422 | 4.3945 | -42.5949 | -32.515 | -92.894 | 4.5136 | -116.4276 | -116.1896 | -86.7096 | -52.7435 | -116.3132 | 4.4724 | 4.5364 | -116.1301 | -116.3818 | -0.14648 | 0.091553 | -0.022888 | 73.6862 | 23.3871 | 23.2956 | -0.14191 | 0.15106 | -0.10071 | -0.064087 | 29.5715 | -0.032043 | 0.068665 | 0 | 120.7947 | 120.6757 | 83.7662 | -120.726 | 120.7535 | 120.8176 | 63.5376 | -120.9183
2569.8281 | 121.1243 | -116.2994 | 4.5547 | -0.0049592 | 0.20888 | 0.64261 | 0.0012476 | 0.29826 | 0.15772 | 0.2158 | -0.0054932 | -0.0046975 | 0.084915 | 0.089613 | -0.19464 | 0.0078422 | 4.4083 | -42.3843 | -32.4051 | -92.7979 | 4.541 | -116.4047 | -116.1667 | -86.5814 | -52.7664 | -116.3269 | 4.509 | 4.5547 | -116.1392 | -116.3773 | -0.10529 | 0.13275 | -0.013733 | 73.9151 | 23.5016 | 23.3688 | -0.14649 | 0.16022 | -0.07782 | -0.045777 | 29.718 | -0.027466 | 0.050354 | 0 | 120.8405 | 120.7077 | 83.8943 | -120.7214 | 120.8084 | 120.8542 | 63.533 | -120.932
2571.5938 | 121.019 | -116.185 | 4.7195 | -0.0049592 | 0.20973 | 0.64646 | 0.003811 | 0.30146 | 0.15623 | 0.21601 | -0.0054932 | -0.0059793 | 0.087051 | 0.086622 | -0.19955 | 0.0078422 | 4.5547 | -42.1783 | -32.222 | -92.5873 | 4.6783 | -116.2766 | -116.0339 | -86.2839 | -52.739 | -116.185 | 4.66 | 4.6921 | -116.0019 | -116.2491 | -0.091552 | 0.15106 | -0.041198 | 74.0067 | 23.5977 | 23.4467 | -0.16479 | 0.18311 | -0.064086 | -0.059509 | 29.9011 | 0 | 0.064086 | -0.027465 | 120.8633 | 120.7397 | 83.963 | -120.7535 | 120.845 | 120.8771 | 63.446 | -120.9686
2573.3594 | 121.0739 | -116.4322 | 4.4861 | -0.0049592 | 0.20973 | 0.64838 | 0.0044518 | 0.30125 | 0.15772 | 0.21558 | -0.020752 | -0.0036295 | 0.08812 | 0.088758 | -0.19848 | 0.0063468 | 4.2755 | -42.3065 | -32.3273 | -92.7521 | 4.4083 | -116.5329 | -116.2857 | -86.4029 | -53.096 | -116.4642 | 4.4128 | 4.4632 | -116.2674 | -116.51 | -0.10071 | 0.14648 | -0.07782 | 74.1257 | 23.6801 | 23.5336 | -0.21057 | 0.1648 | -0.07782 | -0.073242 | 30.0293 | -0.032043 | 0.045777 | -0.022888 | 120.8405 | 120.7077 | 84.1049 | -120.7718 | 120.845 | 120.8954 | 63.3362 | -120.9961
2575.1406 | 121.051 | -116.5375 | 4.3945 | -0.012589 | 0.21272 | 0.64966 | -0.001316 | 0.30466 | 0.15922 | 0.21751 | -0.013123 | -0.0036295 | 0.086624 | 0.088545 | -0.19442 | 0.0052786 | 4.2618 | -42.1967 | -32.1579 | -92.7383 | 4.3121 | -116.597 | -116.3773 | -86.2564 | -53.1647 | -116.4825 | 4.303 | 4.3579 | -116.3452 | -116.597 | -0.059509 | 0.16022 | -0.082397 | 74.3408 | 23.7991 | 23.6389 | -0.13275 | 0.19226 | -0.059509 | -0.091552 | 30.2811 | 0.054932 | 0.11444 | -0.036621 | 120.8496 | 120.7993 | 84.3796 | -120.7718 | 120.8405 | 120.8954 | 63.3728 | -120.9915
2576.8594 | 121.0419 | -116.4368 | 4.5044 | -0.0049592 | 0.21251 | 0.65415 | 0.003811 | 0.30296 | 0.15708 | 0.21793 | -0.0054932 | -0.0053385 | 0.08812 | 0.087049 | -0.19827 | 0.0080558 | 4.2801 | -41.954 | -31.8787 | -92.5735 | 4.422 | -116.5146 | -116.3177 | -86.055 | -53.096 | -116.4459 | 4.4037 | 4.4678 | -116.2628 | -116.4963 | -0.077819 | 0.11902 | -0.082398 | 74.4827 | 23.8632 | 23.7442 | -0.2243 | 0.17395 | -0.059509 | -0.10071 | 30.3818 | -0.009155 | 0.050354 | -0.036622 | 120.8588 | 120.7169 | 84.5581 | -120.8221 | 120.8405 | 120.9045 | 63.3408 | -121.0007
2578.625 | 121.0327 | -116.4093 | 4.4952 | -0.0049592 | 0.2123 | 0.6535 | 0.0053064 | 0.30253 | 0.15452 | 0.21751 | -0.0054932 | -0.0059793 | 0.087479 | 0.089613 | -0.19763 | 0.0078422 | 4.3488 | -41.8167 | -31.7917 | -92.482 | 4.3991 | -116.4734 | -116.2628 | -85.9085 | -53.2288 | -116.391 | 4.4128 | 4.4632 | -116.2308 | -116.4734 | -0.064087 | 0.14648 | -0.09613 | 74.5926 | 23.9273 | 23.7808 | -0.14648 | 0.17853 | -0.064087 | -0.082397 | 30.5008 | 0.018311 | 0.082398 | -0.032043 | 120.8084 | 120.7581 | 84.6176 | -120.7581 | 120.8221 | 120.8725 | 63.1805 | -120.9686
2580.4062 | 121.0693 | -116.3681 | 4.5456 | -0.0049592 | 0.21294 | 0.65393 | -0.00067498 | 0.30274 | 0.16285 | 0.22028 | -0.0054932 | -0.0019205 | 0.088333 | 0.092176 | -0.19507 | 0.005065 | 4.4174 | -41.8259 | -31.842 | -92.395 | 4.4769 | -116.4551 | -116.2262 | -85.6293 | -53.2104 | -116.3406 | 4.454 | 4.4998 | -116.1484 | -116.4001 | -0.086975 | 0.14191 | -0.068664 | 74.5422 | 23.9731 | 23.8312 | -0.12817 | 0.21973 | -0.032043 | -0.091552 | 30.7388 | 0.027466 | 0.059509 | -0.045776 | 120.845 | 120.7855 | 84.5261 | -120.7718 | 120.8221 | 120.8679 | 63.1577 | -120.9457
2582.1094 | 121.0693 | -116.3361 | 4.5639 | 0.0026703 | 0.21187 | 0.65607 | 0.0035974 | 0.30402 | 0.16071 | 0.219 | -0.013123 | -0.0049111 | 0.090042 | 0.088545 | -0.19763 | 0.0074148 | 4.3625 | -41.8945 | -31.8878 | -92.3996 | 4.4815 | -116.4505 | -116.2216 | -85.5148 | -53.2425 | -116.3498 | 4.4724 | 4.5273 | -116.1896 | -116.423 | -0.11444 | 0.11444 | -0.082398 | 74.4415 | 23.9365 | 23.822 | -0.20142 | 0.14648 | -0.086975 | -0.091553 | 30.8212 | -0.013732 | 0.073243 | -0.036621 | 120.8176 | 120.6985 | 84.4482 | -120.7855 | 120.8084 | 120.8633 | 63.0936 | -120.9869
2583.8906 | 121.0968 | -116.423 | 4.4724 | -0.0049592 | 0.21208 | 0.65799 | 0.0027428 | 0.30274 | 0.15495 | 0.21879 | -0.020752 | -0.0070475 | 0.088547 | 0.088758 | -0.20019 | 0.0082694 | 4.3716 | -41.7114 | -31.7413 | -92.3264 | 4.3625 | -116.4871 | -116.2399 | -85.4874 | -53.3615 | -116.3269 | 4.3762 | 4.4083 | -116.2399 | -116.4459 | -0.064087 | 0.18311 | -0.10986 | 74.7116 | 24.0967 | 23.9136 | -0.10071 | 0.18311 | -0.022888 | -0.09613 | 30.9357 | 0.096131 | 0.11902 | -0.064087 | 120.7855 | 120.7947 | 84.6817 | -120.7123 | 120.7993 | 120.8313 | 63.0615 | -120.9183
2585.6719 | 121.0922 | -116.4871 | 4.4128 | -0.020218 | 0.2123 | 0.65906 | -3.4178e-05 | 0.30445 | 0.16093 | 0.22114 | -0.0054932 | -0.0042703 | 0.089615 | 0.08769 | -0.19571 | 0.0063468 | 4.2343 | -41.7435 | -31.7596 | -92.3767 | 4.3671 | -116.5787 | -116.3452 | -85.437 | -53.5995 | -116.4871 | 4.3442 | 4.39 | -116.3223 | -116.5695 | -0.091552 | 0.14191 | -0.045777 | 74.7437 | 24.1104 | 23.9685 | -0.17853 | 0.16479 | -0.082397 | -0.068665 | 31.0501 | 0 | 0.082397 | -0.022888 | 120.8542 | 120.7214 | 84.7275 | -120.7581 | 120.8313 | 120.8771 | 62.8876 | -120.9824
2587.4375 | 121.1563 | -116.3315 | 4.4815 | 0.0026703 | 0.20824 | 0.66098 | 0.0035974 | 0.30723 | 0.15537 | 0.21943 | -0.020752 | -0.0089701 | 0.087051 | 0.086408 | -0.19827 | 0.0093374 | 4.422 | -41.3635 | -31.4163 | -92.1066 | 4.4174 | -116.4322 | -116.1804 | -85.1395 | -53.389 | -116.2582 | 4.422 | 4.4632 | -116.1896 | -116.4047 | -0.10071 | 0.15106 | -0.064087 | 74.968 | 24.2249 | 24.0738 | -0.059509 | 0.14191 | -0.073242 | -0.059509 | 31.192 | 0.073242 | 0.14648 | -0.01831 | 120.7489 | 120.7535 | 84.9152 | -120.6619 | 120.7535 | 120.7947 | 62.9425 | -120.8862
2589.1562 | 121.1197 | -116.4597 | 4.3762 | -0.0049592 | 0.21529 | 0.65799 | 0.001034 | 0.30317 | 0.16605 | 0.22114 | 0.0021363 | -0.0034159 | 0.089828 | 0.089826 | -0.19442 | 0.0074148 | 4.2252 | -41.6931 | -31.778 | -92.3126 | 4.3488 | -116.597 | -116.3498 | -85.2081 | -53.8101 | -116.51 | 4.3259 | 4.3716 | -116.3177 | -116.5695 | -0.13733 | 0.10986 | -0.027466 | 74.7665 | 24.147 | 24.0372 | -0.15106 | 0.14191 | -0.10986 | -0.050354 | 31.2515 | -0.050354 | 0.059509 | -0.004578 | 120.8084 | 120.6848 | 84.6817 | -120.726 | 120.7855 | 120.8313 | 62.6495 | -120.9457
2590.9375 | 121.0144 | -116.1667 | 4.7379 | -0.012589 | 0.217 | 0.65457 | 0.00082022 | 0.30531 | 0.1637 | 0.2205 | -0.0054932 | -0.0038431 | 0.089188 | 0.09004 | -0.19421 | 0.0059196 | 4.5227 | -41.748 | -31.8466 | -92.157 | 4.6463 | -116.272 | -116.0614 | -84.787 | -53.4576 | -116.2491 | 4.6326 | 4.6875 | -116.0294 | -116.2857 | -0.10529 | 0.10529 | -0.091553 | 74.4186 | 24.0097 | 23.9044 | -0.21515 | 0.13733 | -0.11902 | -0.10529 | 31.3797 | -0.082397 | 0.036622 | -0.050354 | 120.813 | 120.6894 | 84.3201 | -120.7993 | 120.7993 | 120.8542 | 62.709 | -121.0236
2592.7188 | 121.0098 | -116.3864 | 4.5181 | -0.012589 | 0.21678 | 0.65906 | -0.0011024 | 0.30787 | 0.16328 | 0.22199 | -0.0054932 | -0.0049111 | 0.08876 | 0.090681 | -0.19528 | 0.0080558 | 4.3533 | -41.5878 | -31.691 | -92.1936 | 4.4449 | -116.478 | -116.2308 | -84.8373 | -53.7277 | -116.4093 | 4.4357 | 4.4861 | -116.2079 | -116.4368 | -0.091552 | 0.15564 | -0.073242 | 74.7986 | 24.1928 | 24.0372 | -0.16479 | 0.17853 | -0.050354 | -0.082397 | 31.5491 | -0.022888 | 0.027466 | -0.032043 | 120.8313 | 120.7397 | 84.6954 | -120.7489 | 120.8221 | 120.8725 | 62.6587 | -120.9549
2594.5 | 121.0785 | -116.4368 | 4.454 | -0.0049592 | 0.21742 | 0.6612 | -0.00046138 | 0.30851 | 0.16157 | 0.22349 | -0.0054932 | -0.0055521 | 0.086838 | 0.089826 | -0.19635 | 0.008483 | 4.2892 | -41.4551 | -31.517 | -92.1249 | 4.3808 | -116.5695 | -116.2994 | -84.7137 | -53.8651 | -116.4139 | 4.3854 | 4.4128 | -116.2766 | -116.5054 | -0.13275 | 0.13733 | -0.073243 | 74.9817 | 24.3118 | 24.1745 | -0.16479 | 0.16022 | -0.068664 | -0.068665 | 31.723 | 0.022889 | 0.091553 | -0.041199 | 120.8176 | 120.726 | 84.9197 | -120.7535 | 120.8221 | 120.8496 | 62.5717 | -120.9595
2596.2344 | 121.0556 | -111.1816 | 9.7412 | -0.0049592 | 0.21977 | 0.63556 | 0.0040246 | 0.30274 | 0.15623 | 0.2158 | 0.0021363 | -0.0068337 | 0.090042 | 0.09004 | -0.19699 | 0.0095512 | 9.5901 | -37.7014 | -27.9694 | -87.4374 | 9.6725 | -111.2366 | -111.0443 | -79.6371 | -49.0356 | -111.1816 | 9.6588 | 9.7183 | -111.0123 | -111.2137 | -0.054931 | 0.13733 | -0.068665 | 73.4802 | 23.7442 | 23.6069 | -0.15106 | 0.16937 | -0.032043 | -0.082398 | 31.5445 | 0 | 0.032043 | -0.022888 | 120.8542 | 120.7718 | 83.2123 | -120.7855 | 120.8405 | 120.9 | 62.146 | -120.9549
2598 | 121.1334 | -112.6831 | 8.139 | -0.012589 | 0.21657 | 0.64026 | 0.00017942 | 0.30274 | 0.15751 | 0.219 | 0.0021363 | -0.0079019 | 0.088974 | 0.090254 | -0.19656 | 0.0097648 | 8.107 | -38.8184 | -28.9673 | -88.7741 | 8.0429 | -112.7838 | -112.5366 | -80.9006 | -50.4684 | -112.619 | 8.0338 | 8.0841 | -112.5458 | -112.7701 | -0.10071 | 0.14648 | -0.09613 | 73.8647 | 23.909 | 23.7625 | -0.032043 | 0.13733 | -0.086976 | -0.10529 | 31.7825 | 0.064086 | 0.15106 | -0.054932 | 120.726 | 120.7901 | 83.7158 | -120.6757 | 120.7169 | 120.7672 | 62.2147 | -120.9091
2599.7812 | 121.0236 | -114.2029 | 6.6879 | 0.0103 | 0.21892 | 0.64774 | 0.0059472 | 0.30466 | 0.15751 | 0.2205 | -0.013123 | -0.0070475 | 0.089401 | 0.088758 | -0.19784 | 0.0082694 | 6.5918 | -39.8712 | -30.043 | -90.0421 | 6.5964 | -114.267 | -114.0289 | -82.2601 | -51.9287 | -114.1479 | 6.601 | 6.6605 | -114.0106 | -114.2487 | -0.064087 | 0.17395 | -0.091552 | 74.3317 | 24.1608 | 23.9868 | -0.09613 | 0.19226 | -0.045776 | -0.086975 | 31.9427 | 0.054932 | 0.10071 | -0.027466 | 120.7993 | 120.7947 | 84.1599 | -120.7169 | 120.8038 | 120.8633 | 62.2742 | -120.9366
2601.5625 | 121.0464 | -114.8712 | 6.0516 | 0.0026703 | 0.21977 | 0.6535 | 0.0029566 | 0.30573 | 0.15623 | 0.22263 | 0.0021363 | -0.0070475 | 0.087692 | 0.086836 | -0.20041 | 0.0080558 | 5.9326 | -40.3656 | -30.5786 | -90.6189 | 5.9189 | -114.9216 | -114.6973 | -82.7087 | -52.652 | -114.7659 | 5.9509 | 5.9875 | -114.6881 | -114.8987 | -0.050354 | 0.17395 | -0.13275 | 74.5056 | 24.2523 | 24.0784 | -0.11902 | 0.18311 | -0.027466 | -0.10071 | 32.1625 | 0.10529 | 0.13275 | -0.064087 | 120.7901 | 120.8038 | 84.2926 | -120.7489 | 120.8221 | 120.8588 | 62.2192 | -120.9503
2603.3438 | 121.0693 | -111.5204 | 9.343 | -0.012589 | 0.22597 | 0.63278 | 0.0035974 | 0.3036 | 0.16135 | 0.21793 | -0.013123 | -0.0036295 | 0.091965 | 0.089613 | -0.19528 | 0.0065604 | 9.288 | -38.0768 | -28.4363 | -87.5381 | 9.3201 | -111.5524 | -111.3556 | -79.3167 | -49.6033 | -111.4655 | 9.3155 | 9.3796 | -111.3373 | -111.5524 | -0.032043 | 0.16479 | -0.022889 | 73.4436 | 23.9822 | 23.8174 | -0.054932 | 0.18311 | -0.032043 | -0.027466 | 32.2037 | 0.054932 | 0.086975 | 0.036621 | 120.8405 | 120.8084 | 83.0841 | -120.6985 | 120.8359 | 120.9 | 61.9171 | -120.8954
2605.0469 | 121.1014 | -111.3968 | 9.4025 | -0.012589 | 0.21785 | 0.6565 | -0.002384 | 0.31193 | 0.16071 | 0.22669 | -0.013123 | -0.0079019 | 0.089828 | 0.088545 | -0.19378 | 0.0082694 | 9.3704 | -35.9756 | -26.0513 | -86.7737 | 9.2972 | -111.4929 | -111.2778 | -79.0695 | -49.5209 | -111.351 | 9.3063 | 9.3475 | -111.3007 | -111.4975 | -0.09613 | 0.11902 | -0.10529 | 75.4211 | 24.6231 | 24.5041 | -0.032044 | 0.096131 | -0.10071 | -0.096131 | 32.3273 | 0.045777 | 0.14648 | -0.054932 | 120.694 | 120.7672 | 85.3455 | -120.6802 | 120.7031 | 120.7443 | 61.8759 | -120.9
2606.8125 | 121.1288 | -111.9324 | 8.8715 | -0.012589 | 0.2202 | 0.66226 | 0.0023156 | 0.30979 | 0.16584 | 0.22904 | -0.0054932 | -0.0061929 | 0.090042 | 0.090681 | -0.19592 | 0.0089102 | 8.8715 | -36.058 | -26.0513 | -87.0987 | 8.7799 | -112.0422 | -111.8134 | -79.4037 | -49.91 | -111.8591 | 8.7799 | 8.8165 | -111.7722 | -112.0102 | -0.10986 | 0.11902 | -0.091553 | 75.8743 | 24.8337 | 24.7147 | 0 | 0.16022 | -0.07782 | -0.091553 | 32.5287 | 0.073242 | 0.15106 | -0.054932 | 120.7123 | 120.8038 | 85.881 | -120.6848 | 120.7123 | 120.7489 | 62.0224 | -120.8817
2608.5781 | 121.1655 | -112.294 | 8.5007 | -0.0049592 | 0.22063 | 0.67316 | -0.0011024 | 0.31321 | 0.16862 | 0.22904 | -0.0054932 | -0.0057657 | 0.088547 | 0.088972 | -0.19592 | 0.0089102 | 8.4366 | -35.6918 | -25.5615 | -87.1857 | 8.4412 | -112.413 | -112.1979 | -79.6143 | -50.148 | -112.2711 | 8.4137 | 8.4641 | -112.175 | -112.3718 | -0.11902 | 0.09613 | -0.059509 | 76.6022 | 25.1083 | 25.0122 | -0.064087 | 0.11902 | -0.07782 | -0.086975 | 32.6797 | 0.022888 | 0.10071 | -0.036621 | 120.7352 | 120.7306 | 86.7325 | -120.6985 | 120.7077 | 120.7581 | 62.146 | -120.8725
2610.3594 | 121.0739 | -112.532 | 8.3084 | -0.0049592 | 0.22298 | 0.67807 | 0.0044518 | 0.31577 | 0.16605 | 0.22968 | -0.013123 | -0.0068337 | 0.089828 | 0.089186 | -0.19763 | 0.010833 | 8.2764 | -35.4858 | -25.3372 | -87.1902 | 8.2214 | -112.6007 | -112.3535 | -79.5639 | -50.1846 | -112.4084 | 8.2214 | 8.2809 | -112.381 | -112.587 | -0.068665 | 0.17853 | -0.086975 | 77.0462 | 25.3418 | 25.1633 | -0.032044 | 0.15106 | -0.054932 | -0.086975 | 32.9681 | 0.1236 | 0.17853 | -0.027466 | 120.7535 | 120.8084 | 87.1948 | -120.6619 | 120.7535 | 120.813 | 62.3474 | -120.8954
2612.0469 | 121.0922 | -112.5229 | 8.2901 | -0.0049592 | 0.22063 | 0.68234 | 0.00060662 | 0.31641 | 0.1684 | 0.23374 | -0.013123 | -0.0076883 | 0.089401 | 0.088117 | -0.19635 | 0.0091238 | 8.2031 | -35.2066 | -25.0031 | -87.149 | 8.1894 | -112.6144 | -112.4039 | -79.5364 | -50.1526 | -112.4817 | 8.194 | 8.2489 | -112.4222 | -112.619 | -0.091553 | 0.11902 | -0.10071 | 77.3163 | 25.3738 | 25.2548 | -0.086975 | 0.10071 | -0.096131 | -0.09613 | 32.9864 | 0.041199 | 0.13733 | -0.041199 | 120.7123 | 120.726 | 87.5198 | -120.694 | 120.7169 | 120.7718 | 62.3703 | -120.9091
2613.8281 | 121.1517 | -111.232 | 9.5673 | -0.012589 | 0.2217 | 0.67359 | 0.00082022 | 0.31727 | 0.17097 | 0.2346 | -0.013123 | -0.0040567 | 0.09111 | 0.089186 | -0.19464 | 0.0082694 | 9.5535 | -34.1766 | -24.0875 | -85.9039 | 9.5078 | -111.3281 | -111.1038 | -78.1631 | -48.9349 | -111.1725 | 9.4757 | 9.5123 | -111.1221 | -111.3052 | -0.09613 | 0.12817 | -0.05951 | 77.0554 | 25.3281 | 25.1999 | -0.013733 | 0.10986 | -0.073242 | -0.091553 | 33.0688 | 0.05951 | 0.13275 | -0.054932 | 120.7397 | 120.7855 | 87.1445 | -120.6711 | 120.7077 | 120.7443 | 62.2971 | -120.8725
2615.6094 | 121.0876 | -111.8408 | 8.9859 | -0.012589 | 0.22704 | 0.677 | 0.00082022 | 0.31599 | 0.1731 | 0.23417 | -0.013123 | -0.0027749 | 0.092178 | 0.093458 | -0.19421 | 0.0099784 | 8.8898 | -34.6893 | -24.5728 | -86.4532 | 8.9401 | -111.9598 | -111.731 | -78.7125 | -49.6124 | -111.8729 | 8.9355 | 8.9813 | -111.7172 | -111.9278 | -0.11902 | 0.10986 | -0.045776 | 77.1515 | 25.3876 | 25.2777 | -0.09613 | 0.1236 | -0.086975 | -0.050354 | 33.1284 | -0.032044 | 0.054931 | -0.004578 | 120.7809 | 120.7306 | 87.2681 | -120.7169 | 120.7764 | 120.8221 | 62.2284 | -120.9137
2617.3125 | 121.1334 | -112.0834 | 8.7112 | -0.020218 | 0.2249 | 0.68234 | 0.0016748 | 0.31834 | 0.16969 | 0.23652 | 0.0021363 | -0.0057657 | 0.089401 | 0.089186 | -0.19421 | 0.011046 | 8.6151 | -34.6344 | -24.5224 | -86.5723 | 8.6655 | -112.1979 | -112.0102 | -78.8681 | -49.8917 | -112.0834 | 8.6334 | 8.6884 | -111.9736 | -112.1796 | -0.11444 | 0.073242 | -0.045777 | 77.449 | 25.5112 | 25.4379 | -0.096131 | 0.10986 | -0.09613 | -0.07782 | 33.2153 | 0 | 0.09613 | -0.022889 | 120.7489 | 120.6985 | 87.561 | -120.7214 | 120.7169 | 120.7718 | 62.1918 | -120.8908
2619.0781 | 121.0144 | -87.4832 | 33.4671 | -0.020218 | 0.23558 | 0.57959 | 0.00552 | 0.3021 | 0.15922 | 0.219 | -0.013123 | -0.0038431 | 0.09346 | 0.089613 | -0.19848 | 0.008483 | 33.3939 | -14.3646 | -4.6143 | -63.7115 | 33.3389 | -87.4466 | -87.3093 | -55.2246 | -26.4908 | -87.4466 | 33.3572 | 33.403 | -87.2498 | -87.442 | 0.036621 | 0.17395 | -0.12817 | 73.1186 | 23.7717 | 23.5977 | -0.073242 | 0.23346 | 0.041198 | -0.10986 | 32.2586 | 0.036621 | -0.004577 | -0.064087 | 120.8221 | 120.8771 | 82.869 | -120.7764 | 120.8405 | 120.8862 | 60.9924 | -120.9091
2620.8594 | 121.0144 | -89.4196 | 31.4941 | -0.012589 | 0.23451 | 0.58493 | 0.003811 | 0.30381 | 0.16093 | 0.2205 | -0.0054932 | -0.0029885 | 0.092178 | 0.089186 | -0.19571 | 0.0074148 | 31.5079 | -16.1133 | -6.4819 | -65.5884 | 31.4026 | -89.4104 | -89.241 | -56.8817 | -28.3493 | -89.3829 | 31.3889 | 31.4255 | -89.1998 | -89.4196 | 0.009156 | 0.17853 | -0.091553 | 73.3063 | 23.8312 | 23.6526 | 0.013733 | 0.21973 | 0 | -0.10529 | 32.5378 | 0.036621 | 0.036621 | -0.068665 | 120.8221 | 120.9274 | 82.9376 | -120.7352 | 120.8084 | 120.845 | 61.0703 | -120.9137
2622.5781 | 121.1243 | -91.7404 | 29.0451 | -0.012589 | 0.23195 | 0.59326 | 0.0059472 | 0.30466 | 0.15473 | 0.21857 | -0.013123 | -0.0089701 | 0.091324 | 0.089186 | -0.20126 | 0.0091238 | 29.2557 | -17.9718 | -8.3679 | -67.6117 | 29.1275 | -91.6214 | -91.4474 | -59.0149 | -30.4733 | -91.6534 | 28.9673 | 29.0314 | -91.5802 | -91.7358 | 0.11902 | 0.29297 | 0.082397 | 73.7686 | 24.1287 | 23.8358 | 0.21057 | 0.16022 | 0.004577 | -0.07782 | 32.7255 | 0.086975 | 0.082398 | -0.013733 | 120.8679 | 120.9961 | 83.3725 | -120.4926 | 120.7077 | 120.7718 | 61.2671 | -120.7809
2624.3594 | 121.0876 | -94.4275 | 26.3992 | -0.020218 | 0.23366 | 0.60544 | 0.0029566 | 0.30466 | 0.15729 | 0.22007 | 0.0021363 | -0.0089701 | 0.091751 | 0.088117 | -0.19763 | 0.010406 | 26.3947 | -20.4391 | -10.8261 | -70.3033 | 26.3031 | -94.4641 | -94.2764 | -61.4914 | -33.2199 | -94.3909 | 26.2756 | 26.3123 | -94.313 | -94.4824 | -0.036621 | 0.15106 | -0.09613 | 73.9883 | 24.1241 | 23.9731 | -0.004578 | 0.11444 | -0.054932 | -0.1236 | 32.9361 | 0.036621 | 0.091553 | -0.086975 | 120.7306 | 120.8221 | 83.6014 | -120.6757 | 120.7031 | 120.7397 | 61.2076 | -120.8817
2626.0781 | 121.106 | -92.0837 | 28.7338 | -0.012589 | 0.22704 | 0.5986 | 0.0016748 | 0.30424 | 0.15708 | 0.21943 | -0.0054932 | -0.0074747 | 0.091965 | 0.088758 | -0.19763 | 0.011046 | 28.7476 | -18.3746 | -8.812 | -68.1015 | 28.6331 | -92.1295 | -91.9281 | -59.1248 | -30.9906 | -92.07 | 28.6377 | 28.688 | -91.9144 | -92.1432 | -0.045777 | 0.15564 | -0.10071 | 73.7091 | 23.9822 | 23.8266 | 0.013733 | 0.16937 | -0.05951 | -0.096131 | 32.959 | 0.013733 | 0.073243 | -0.045777 | 120.7169 | 120.8313 | 83.2718 | -120.6619 | 120.7214 | 120.7718 | 61.0931 | -120.8771
2627.8594 | 121.0464 | -89.7675 | 31.0776 | -0.0049592 | 0.23814 | 0.58856 | 0.0033838 | 0.30253 | 0.16306 | 0.21836 | 0.0021363 | -0.0040567 | 0.093246 | 0.088972 | -0.19549 | 0.0072012 | 31.0501 | -16.4566 | -6.871 | -65.9454 | 30.9998 | -89.827 | -89.6667 | -56.7856 | -28.8162 | -89.8041 | 30.9998 | 31.0181 | -89.6622 | -89.8361 | -0.059509 | 0.10071 | -0.07782 | 73.3109 | 23.822 | 23.7213 | -0.027466 | 0.10529 | -0.068665 | -0.07782 | 32.9819 | -0.036621 | 0.032044 | -0.05951 | 120.7672 | 120.8176 | 82.8964 | -120.7443 | 120.7672 | 120.7855 | 60.9512 | -120.9137
2629.5781 | 121.1426 | -87.8311 | 32.9773 | -0.012589 | 0.23387 | 0.57895 | 0.0025292 | 0.29847 | 0.15516 | 0.21836 | -0.013123 | -0.0089701 | 0.092819 | 0.089399 | -0.19848 | 0.01126 | 32.991 | -14.9002 | -5.3833 | -64.151 | 32.872 | -87.8632 | -87.7029 | -54.8172 | -27.0218 | -87.8265 | 32.8812 | 32.9544 | -87.6846 | -87.8815 | -0.032043 | 0.12817 | -0.10529 | 72.9309 | 23.6801 | 23.5519 | 0.013733 | 0.14648 | -0.050354 | -0.09613 | 33.0139 | 0.004578 | 0.054932 | -0.022888 | 120.7031 | 120.8221 | 82.4478 | -120.6802 | 120.7123 | 120.7855 | 60.8093 | -120.8588
2631.3594 | 121.1197 | -87.6755 | 33.1055 | -0.020218 | 0.23686 | 0.57916 | -0.0011024 | 0.29569 | 0.15794 | 0.21815 | -0.0054932 | -0.0061929 | 0.093246 | 0.091963 | -0.19442 | 0.0080558 | 33.1696 | -14.8407 | -5.3467 | -64.0366 | 33.0048 | -87.7579 | -87.5931 | -54.4693 | -26.8799 | -87.6755 | 33.0048 | 33.0551 | -87.5931 | -87.7716 | -0.082398 | 0.082397 | -0.10071 | 72.8348 | 23.6389 | 23.5565 | 0.064087 | 0.082397 | -0.09613 | -0.10071 | 33.2062 | 0 | 0.09613 | -0.050354 | 120.6802 | 120.845 | 82.3288 | -120.6985 | 120.6802 | 120.7306 | 60.7956 | -120.8771
2633.125 | 121.0007 | -87.7716 | 33.0963 | -0.012589 | 0.23836 | 0.57489 | 0.00017942 | 0.29911 | 0.16199 | 0.21879 | 0.0021363 | -0.0019205 | 0.094528 | 0.088972 | -0.19442 | 0.0095512 | 33.0734 | -15.1794 | -5.7404 | -64.2151 | 33.0093 | -87.822 | -87.6755 | -54.4876 | -27.0905 | -87.8586 | 33.0139 | 33.0414 | -87.6343 | -87.8265 | -0.050354 | 0.09613 | -0.086975 | 72.5922 | 23.5565 | 23.4604 | -0.022888 | 0.13733 | -0.054932 | -0.082397 | 33.284 | -0.086976 | -0.032044 | -0.054931 | 120.7809 | 120.845 | 82.0312 | -120.7718 | 120.7855 | 120.813 | 60.6812 | -120.9229
2634.9062 | 121.019 | -92.0151 | 28.775 | 0.0026703 | 0.99394 | 0.47406 | -0.00067498 | 0.37132 | 0.71314 | 0.23545 | 0.0021363 | -0.0023477 | 0.092606 | 0.091108 | -0.19571 | 0.0082694 | 28.624 | -2.9526 | -5.9326 | 14.3005 | 28.5324 | -92.1432 | -91.9556 | -58.3374 | -31.1554 | -92.1021 | 28.6148 | 28.624 | -91.9968 | -92.1982 | -0.12817 | 0.05951 | -0.24261 | 89.0625 | 106.3156 | 106.2561 | -0.15106 | 0.018311 | -0.18311 | -0.16022 | 33.6777 | -0.086975 | 0.09613 | -0.15106 | 120.5475 | 120.639 | 86.0825 | -120.7306 | 120.6299 | 120.639 | 60.8597 | -120.9732
2636.6875 | 120.9869 | -92.6102 | 28.1616 | -0.0049592 | 1.1228 | 0.45868 | 0.00082022 | 0.38435 | 0.80628 | 0.23737 | -0.0054932 | -0.0036295 | 0.092819 | 0.090467 | -0.19442 | 0.010192 | 28.0792 | -0.71411 | -5.8273 | 27.8366 | 28.0426 | -92.6376 | -92.45 | -58.6807 | -31.6818 | -92.6285 | 28.0701 | 28.1204 | -92.5003 | -92.6834 | -0.027466 | 0.16022 | -0.11902 | 91.8961 | 120.4468 | 120.2866 | -0.082397 | 0.10986 | -0.073243 | -0.091553 | 33.9294 | -0.018311 | 0.054932 | -0.041199 | 120.6528 | 120.6894 | 86.7828 | -120.6116 | 120.6802 | 120.7306 | 60.9283 | -120.845
2638.4688 | 120.9412 | -91.8549 | 28.9215 | -0.0049592 | 1.1245 | 0.45612 | 0.0018884 | 0.38242 | 0.80735 | 0.23908 | -0.020752 | -0.0034159 | 0.092819 | 0.090467 | -0.19336 | 0.010192 | 28.8071 | -0.036621 | -5.2048 | 28.5828 | 28.743 | -91.8732 | -91.6626 | -57.8064 | -31.0684 | -91.9235 | 28.8025 | 28.8712 | -91.7267 | -91.9327 | -0.018311 | 0.19226 | -0.17853 | 91.8182 | 120.4376 | 120.2454 | -0.11444 | 0.12817 | -0.07782 | -0.11902 | 34.0485 | -0.068665 | 0.009155 | -0.050354 | 120.5978 | 120.6619 | 86.6501 | -120.5841 | 120.6573 | 120.726 | 60.7864 | -120.8542
2640.1875 | 120.9366 | -91.8869 | 28.8986 | -0.0049592 | 1.1225 | 0.45676 | 0.0042382 | 0.38371 | 0.79945 | 0.23588 | -0.0054932 | -0.0089701 | 0.093674 | 0.089826 | -0.19827 | 0.010619 | 28.862 | 0.10986 | -5.0858 | 28.6377 | 28.7109 | -91.8182 | -91.6351 | -57.6462 | -30.9219 | -91.777 | 28.7704 | 28.8528 | -91.6992 | -91.8869 | 0.068665 | 0.25177 | -0.18768 | 91.9968 | 120.5246 | 120.2728 | -0.036621 | 0.18768 | 0 | -0.12817 | 34.2407 | 0.10986 | 0.10986 | -0.045777 | 120.5978 | 120.7489 | 86.8011 | -120.5338 | 120.6573 | 120.7397 | 60.965 | -120.7855
2641.9688 | 121.0327 | -91.6901 | 28.981 | -0.020218 | 1.1208 | 0.45697 | 0.001034 | 0.38691 | 0.79902 | 0.23566 | -0.013123 | -0.0079019 | 0.091965 | 0.089399 | -0.1987 | 0.011046 | 29.0222 | 0.3479 | -4.9622 | 28.775 | 28.8437 | -91.6672 | -91.507 | -57.3715 | -30.8304 | -91.5756 | 28.9078 | 28.9536 | -91.5436 | -91.7358 | 0.022888 | 0.1831 | -0.13733 | 92.038 | 120.4651 | 120.282 | 0.041199 | 0.14648 | -0.045777 | -0.073242 | 34.3185 | 0.11444 | 0.16022 | -0.027466 | 120.5338 | 120.7123 | 86.7279 | -120.488 | 120.5978 | 120.6436 | 60.8597 | -120.7169
2643.75 | 120.9045 | -91.9373 | 28.8162 | -0.020218 | 1.1215 | 0.45612 | 0.003811 | 0.38477 | 0.80094 | 0.23866 | -0.013123 | -0.0070475 | 0.093674 | 0.091535 | -0.19827 | 0.0097648 | 28.7292 | 0.07782 | -5.2231 | 28.5095 | 28.6743 | -91.9235 | -91.7267 | -57.55 | -31.1874 | -91.9235 | 28.7247 | 28.775 | -91.8137 | -91.9693 | 0.013733 | 0.21057 | -0.14191 | 92.0151 | 120.4468 | 120.2362 | -0.086975 | 0.1236 | -0.032043 | -0.091553 | 34.3872 | 0.013733 | 0.045776 | -0.041199 | 120.6116 | 120.6665 | 86.7142 | -120.5429 | 120.6619 | 120.7123 | 60.7498 | -120.7855
2645.5312 | 120.9824 | -40.8417 | 80.0812 | -0.0049592 | 0.0132 | 0.020754 | 0.0012476 | 0.032082 | -0.0012133 | -0.048027 | -0.0054932 | -0.0076883 | 0.096237 | 0.086195 | -0.19998 | 0.0078422 | 0.11902 | 0.15564 | 0.23346 | 0.20142 | 0.09613 | 0.036621 | -0.059509 | -9.0454 | 17.4866 | -40.892 | 79.9026 | 79.9805 | -40.6265 | -40.7318 | 40.8783 | 40.7822 | -79.985 | 40.9973 | 41.0431 | 0.26093 | -79.9622 | 0.21515 | 0.10986 | -0.17853 | 31.7963 | -0.050354 | -0.16022 | -0.10071 | 40.9378 | 40.9607 | 41.0751 | -80.1407 | 120.7443 | 120.8221 | 58.3282 | -120.813
2647.25 | 121.1014 | -40.5945 | 80.3055 | -0.012589 | 0.0132 | 0.017763 | 0.0048792 | 0.033364 | -0.00078613 | -0.049736 | 0.0021363 | -0.0072611 | 0.09816 | 0.086622 | -0.20019 | 0.008483 | 0.059509 | 0.073242 | 0.17853 | 0.13275 | 0.09613 | 0.032043 | -0.09613 | -8.757 | 17.6651 | -40.6998 | 80.159 | 80.2597 | -40.4114 | -40.535 | 40.6265 | 40.4984 | -80.2094 | 40.6677 | 40.7272 | 0.22888 | -80.246 | 0.1831 | 0.059509 | -0.14648 | 31.8375 | -0.10529 | -0.16479 | -0.045776 | 40.6906 | 40.654 | 40.773 | -80.4016 | 120.7535 | 120.8542 | 58.2596 | -120.8405
2649.0469 | 121.0968 | -40.4434 | 80.4474 | -0.0049592 | 0.011918 | 0.01819 | 0.00060662 | 0.033364 | 0.0015637 | -0.047386 | -0.013123 | -0.0083291 | 0.098373 | 0.087263 | -0.19806 | 0.0069876 | 0.091553 | 0.09613 | 0.20142 | 0.14648 | 0.036621 | 0.045776 | -0.064087 | -8.5098 | 17.7383 | -40.6036 | 80.3009 | 80.365 | -40.3152 | -40.4343 | 40.4892 | 40.3793 | -80.4108 | 40.5396 | 40.5899 | 0.21057 | -80.3558 | 0.12817 | 0.009155 | -0.14648 | 31.9336 | -0.16022 | -0.16937 | -0.082398 | 40.48 | 40.535 | 40.6448 | -80.5115 | 120.7443 | 120.8084 | 58.1818 | -120.8817
2650.7656 | 121.0556 | -40.3656 | 80.5801 | -0.012589 | 0.016191 | 0.016695 | -0.0021704 | 0.030373 | 0.0060499 | -0.049949 | -0.0054932 | -0.0034159 | 0.098587 | 0.088117 | -0.19592 | 0.0089102 | 0.036621 | 0.041199 | 0.11902 | 0.10071 | 0.091553 | 0.013733 | -0.11444 | -8.3588 | 17.8116 | -40.5762 | 80.452 | 80.5115 | -40.2603 | -40.3885 | 40.3793 | 40.2512 | -80.4886 | 40.4068 | 40.4663 | 0.21515 | -80.5435 | 0.10529 | -0.022888 | -0.12817 | 32.0068 | -0.21057 | -0.18768 | -0.068664 | 40.4572 | 40.4022 | 40.4846 | -80.6946 | 120.8176 | 120.8771 | 58.1772 | -120.9686
2652.5312 | 121.1609 | -40.2466 | 80.6717 | -0.012589 | 0.011918 | 0.019258 | 0.0025292 | 0.031227 | -0.0024951 | -0.046318 | -0.013123 | -0.0076883 | 0.097946 | 0.086622 | -0.19891 | 0.0095512 | 0.054932 | 0.10071 | 0.1831 | 0.10986 | 0.041199 | 0.041199 | -0.064087 | -8.1299 | 17.9169 | -40.4068 | 80.5389 | 80.6213 | -40.155 | -40.2512 | 40.2878 | 40.1825 | -80.6305 | 40.3473 | 40.3564 | 0.17395 | -80.6168 | 0.091553 | -0.004578 | -0.13275 | 32.1167 | -0.16022 | -0.15564 | -0.050354 | 40.2878 | 40.3015 | 40.4297 | -80.7358 | 120.7855 | 120.8679 | 58.1635 | -120.9229
2654.2969 | 121.1746 | -40.1184 | 80.8182 | -0.012589 | 0.0089273 | 0.019685 | -0.002384 | 0.034645 | -0.0014269 | -0.047813 | -0.0054932 | -0.0053385 | 0.094528 | 0.084272 | -0.19977 | 0.0074148 | 0.054932 | 0.15564 | 0.20599 | 0.12817 | 0.050354 | 0.032043 | -0.073242 | -7.9147 | 18.0588 | -40.2649 | 80.6854 | 80.7312 | -40.0177 | -40.1184 | 40.1505 | 40.0452 | -80.7678 | 40.274 | 40.2466 | 0.20142 | -80.7632 | 0.10071 | 0 | -0.13275 | 32.2037 | -0.14648 | -0.14648 | -0.086975 | 40.1688 | 40.1733 | 40.3244 | -80.8914 | 120.8038 | 120.8496 | 58.1772 | -120.9366
2656.0312 | 121.1655 | -40.0314 | 80.928 | -0.020218 | 0.013413 | 0.019045 | -0.00046138 | 0.03315 | -0.00078613 | -0.047172 | 0.0021363 | -0.0083291 | 0.097305 | 0.087904 | -0.20062 | 0.0097648 | 0.073242 | 0.10529 | 0.17853 | 0.11444 | 0.036621 | 0.036621 | -0.064087 | -7.6996 | 18.0954 | -40.2008 | 80.777 | 80.8456 | -39.9078 | -40.0406 | 40.0681 | 39.9673 | -80.8914 | 40.1367 | 40.1459 | 0.17853 | -80.8548 | 0.1236 | -0.009155 | -0.15106 | 32.3318 | -0.16937 | -0.16022 | -0.082398 | 40.0681 | 40.1047 | 40.21 | -80.9921 | 120.8084 | 120.8771 | 58.1268 | -120.9686
2657.7969 | 121.1151 | -39.9536 | 81.0745 | -0.012589 | 0.014268 | 0.016054 | -0.001316 | 0.032295 | 0.0071179 | -0.045463 | 0.0021363 | -0.0032021 | 0.097733 | 0.08769 | -0.19635 | 0.0057058 | -0.013733 | -0.054932 | 0.054932 | 0.045776 | 0.082397 | 0.004578 | -0.09613 | -7.5806 | 18.0267 | -40.2237 | 80.9372 | 81.0333 | -39.8392 | -39.9582 | 39.9582 | 39.8575 | -80.9921 | 39.8987 | 39.9994 | 0.14191 | -81.0883 | 0.11444 | -0.004578 | -0.13733 | 32.373 | -0.27008 | -0.2655 | -0.041199 | 40.036 | 39.9399 | 40.0085 | -81.1707 | 120.8908 | 120.9869 | 57.9803 | -121.0327
2659.5625 | 121.2708 | -39.7888 | 81.134 | -0.012589 | 0.014695 | 0.018617 | 0.001034 | 0.032082 | 0.0036999 | -0.04525 | 0.0021363 | -0.0040567 | 0.096237 | 0.083418 | -0.19784 | 0.010192 | 0.009155 | 0.018311 | 0.11902 | 0.07782 | 0.054932 | 0.027466 | -0.086975 | -7.2876 | 18.1686 | -40.0223 | 81.0242 | 81.0928 | -39.7247 | -39.8254 | 39.8163 | 39.7018 | -81.0791 | 39.8071 | 39.8666 | 0.16479 | -81.1249 | 0.064087 | -0.036621 | -0.10986 | 32.5012 | -0.23346 | -0.19684 | -0.041199 | 39.8438 | 39.798 | 39.9078 | -81.221 | 120.813 | 120.8817 | 57.9575 | -120.9595
2661.2656 | 121.2067 | -39.7202 | 81.2439 | -0.012589 | 0.010636 | 0.02054 | -3.4178e-05 | 0.031868 | -0.0024951 | -0.047386 | -0.013123 | -0.0085427 | 0.09581 | 0.086408 | -0.19955 | 0.011687 | 0.009155 | 0.082397 | 0.16022 | 0.09613 | 0.041199 | 0.054932 | -0.041199 | -7.164 | 18.2465 | -39.9353 | 81.0883 | 81.1523 | -39.6469 | -39.7568 | 39.7751 | 39.679 | -81.2027 | 39.8026 | 39.8163 | 0.13733 | -81.2347 | 0.073242 | -0.036621 | -0.15564 | 32.5562 | -0.21515 | -0.17853 | -0.091552 | 39.7614 | 39.7293 | 39.8804 | -81.2851 | 120.8084 | 120.8725 | 57.9666 | -121.0007
2663.0469 | 121.2799 | -39.6057 | 81.3721 | -0.012589 | 0.012986 | 0.022463 | 0.0042382 | 0.032723 | -0.0014269 | -0.0476 | -0.0054932 | -0.0068337 | 0.10008 | 0.08534 | -0.20212 | 0.0089102 | 0.082397 | 0.16937 | 0.21057 | 0.14191 | 0.064087 | 0.045776 | -0.032043 | -6.8573 | 18.3426 | -39.7156 | 81.2164 | 81.2943 | -39.4913 | -39.6149 | 39.6515 | 39.5737 | -81.308 | 39.7751 | 39.7476 | 0.17395 | -81.2897 | 0.11444 | -0.009155 | -0.15564 | 32.7484 | -0.10986 | -0.10071 | -0.07782 | 39.6698 | 39.6881 | 39.8163 | -81.4041 | 120.8221 | 120.9 | 57.9483 | -120.9869
2664.8281 | 121.225 | -39.5279 | 81.4865 | -0.012589 | 0.012345 | 0.018404 | -0.001316 | 0.029732 | -0.0022815 | -0.047172 | -0.013123 | -0.0064065 | 0.098587 | 0.086195 | -0.20041 | 0.008483 | 0.041199 | 0.082397 | 0.15564 | 0.091553 | 0.027466 | 0.045776 | -0.064087 | -6.7291 | 18.3105 | -39.679 | 81.3446 | 81.395 | -39.3951 | -39.5279 | 39.5737 | 39.4638 | -81.459 | 39.6103 | 39.6194 | 0.15564 | -81.4453 | 0.13275 | 0 | -0.14191 | 32.7988 | -0.15106 | -0.15106 | -0.091553 | 39.5554 | 39.5691 | 39.6835 | -81.5506 | 120.8725 | 120.9229 | 57.8384 | -121.0144
2666.6094 | 121.2204 | -39.2303 | 81.7657 | -0.012589 | 0.017259 | 0.017549 | -3.4178e-05 | 0.034218 | 0.0047681 | -0.047172 | 0.0021363 | -0.0046975 | 0.10051 | 0.088331 | -0.19656 | 0.0054922 | 0.036621 | 0.018311 | 0.10071 | 0.10986 | 0.086975 | 0.032043 | -0.07782 | -6.4545 | 18.4113 | -39.6744 | 81.5689 | 81.6193 | -39.2532 | -39.3768 | 39.2624 | 39.1525 | -81.6788 | 39.2487 | 39.3402 | 0.18768 | -81.7291 | -0.022888 | -0.14648 | -0.19684 | 32.7759 | -0.44403 | -0.29755 | -0.14648 | 39.3173 | 39.267 | 39.3311 | -81.8436 | 120.7993 | 120.8496 | 57.6416 | -121.1426
2668.3125 | 121.225 | -32.1213 | 88.9526 | -0.012589 | 0.013627 | 0.018831 | 0.002102 | 0.032295 | -0.0031359 | -0.046745 | -0.013123 | -0.0098245 | 0.09816 | 0.083631 | -0.18289 | 0.0086966 | 0.11444 | 0.19226 | 0.26093 | 0.19684 | 0.09613 | 0.10529 | 0.004578 | 0.57678 | 25.3326 | -31.6772 | 88.7604 | 88.8382 | -31.9839 | -32.1121 | 32.2266 | 32.1259 | -88.8565 | 32.3135 | 32.3181 | 0.19226 | -88.8382 | 0.13733 | 0.009155 | -0.19226 | 32.6981 | 0.44403 | 0.43488 | -0.11444 | 32.2174 | 32.2357 | 32.3822 | -88.9481 | 120.8817 | 120.9595 | 57.4539 | -121.0648
2670.0938 | 121.2982 | -31.929 | 89.0762 | 0.0026703 | 0.0061501 | 0.021822 | -0.00046138 | 0.033791 | -0.0012133 | -0.048454 | -0.0054932 | -0.0070475 | 0.098373 | 0.086408 | -0.18396 | 0.008483 | 0.073242 | 0.13275 | 0.21057 | 0.17395 | 0.13275 | 0.11444 | 0.013733 | 0.82398 | 25.4334 | -31.5537 | 88.9709 | 89.0533 | -31.8146 | -31.9107 | 32.0435 | 31.9427 | -88.9435 | 32.0618 | 32.103 | 0.16022 | -89.003 | 0.11444 | 0.01831 | -0.10529 | 32.753 | 0.37537 | 0.35706 | -0.022888 | 32.0618 | 32.0023 | 32.1396 | -89.0625 | 120.9 | 120.9824 | 57.3624 | -120.9869
2671.875 | 121.2753 | -35.9299 | 85.0891 | -0.0049592 | 0.012345 | 0.018831 | 0.001034 | 0.032295 | -0.0018543 | -0.048881 | -0.013123 | -0.0070475 | 0.099442 | 0.087477 | -0.19357 | 0.011046 | 0.068665 | 0.10529 | 0.18768 | 0.15564 | 0.091553 | 0.10071 | -0.013733 | -2.8152 | 21.8216 | -35.6049 | 85.025 | 85.0937 | -35.7834 | -35.8841 | 36.0306 | 35.9161 | -84.9976 | 36.0352 | 36.0855 | 0.16937 | -85.0204 | 0.14648 | 0.045777 | -0.064087 | 33.1146 | 0.32501 | 0.27924 | 0.004578 | 36.0214 | 35.9985 | 36.1176 | -85.1028 | 120.9549 | 121.0236 | 57.7515 | -120.9732
2673.6719 | 121.2708 | -29.892 | 91.1499 | -0.012589 | 0.014268 | 0.018617 | 0.0029566 | 0.030586 | -0.00078613 | -0.048881 | -0.0054932 | -0.0068337 | 0.099655 | 0.085768 | -0.18118 | 0.0074148 | 0.1831 | 0.24261 | 0.28839 | 0.24719 | 0.13733 | 0.12817 | 0.032043 | 3.0304 | 27.4109 | -29.3335 | 91.008 | 91.1041 | -29.7684 | -29.8828 | 30.0201 | 29.924 | -91.0126 | 30.1346 | 30.1392 | 0.21515 | -90.9668 | 0.1236 | 0.009156 | -0.14191 | 32.9224 | 0.55847 | 0.54932 | -0.045776 | 30.0293 | 30.0751 | 30.1804 | -91.1179 | 120.9 | 120.9961 | 57.3029 | -121.0327
2675.4375 | 121.2799 | -29.1275 | 91.9235 | -0.012589 | 0.012132 | 0.017122 | 0.001034 | 0.032723 | 0.0019909 | -0.047172 | -0.013123 | -0.0059793 | 0.10051 | 0.088117 | -0.18054 | 0.0076286 | 0.17853 | 0.19684 | 0.27924 | 0.21973 | 0.15106 | 0.15106 | 0.064087 | 3.8635 | 27.9739 | -28.6102 | 91.7953 | 91.8869 | -28.9856 | -29.0817 | 29.2786 | 29.1916 | -91.7725 | 29.3243 | 29.3472 | 0.15564 | -91.745 | 0.14191 | 0.045776 | -0.12817 | 32.991 | 0.51727 | 0.4715 | -0.036621 | 29.2786 | 29.306 | 29.4067 | -91.8594 | 120.9229 | 121.0144 | 57.1014 | -121.0052
2677.1562 | 121.2021 | -29.0085 | 92.1295 | -0.012589 | 0.015122 | 0.016908 | 0.0029566 | 0.031441 | 0.00028207 | -0.048027 | -0.013123 | -0.0046975 | 0.10179 | 0.086836 | -0.17712 | 0.0089102 | 0.068665 | 0.082397 | 0.16479 | 0.15564 | 0.17395 | 0.10529 | 0.009155 | 3.9688 | 27.9877 | -28.5965 | 91.983 | 92.0609 | -28.9032 | -28.9993 | 29.1138 | 29.0176 | -91.9556 | 29.0909 | 29.1641 | 0.14649 | -92.0609 | 0.10529 | 0.009155 | -0.14649 | 32.9773 | 0.41199 | 0.40283 | -0.068665 | 29.1824 | 29.0771 | 29.1733 | -92.1204 | 120.9915 | 121.0693 | 56.9962 | -121.1288
2678.9375 | 121.2158 | -28.3905 | 92.7292 | -0.0049592 | 0.015336 | 0.01819 | -0.0011024 | 0.031227 | 0.0064771 | -0.046104 | -0.013123 | -0.0025613 | 0.10136 | 0.088545 | -0.17264 | 0.0069876 | 0.082397 | 0.050354 | 0.13275 | 0.14191 | 0.16022 | 0.12817 | 0.013733 | 4.6875 | 28.569 | -27.9144 | 92.6285 | 92.6605 | -28.2669 | -28.3722 | 28.5187 | 28.4042 | -92.569 | 28.4409 | 28.5324 | 0.12817 | -92.6468 | 0.1236 | 0.018311 | -0.10071 | 33.078 | 0.47607 | 0.45776 | -0.068665 | 28.5507 | 28.4729 | 28.5233 | -92.7155 | 121.019 | 121.051 | 56.9595 | -121.1014
2680.7188 | 121.2433 | -27.3331 | 93.7958 | -0.012589 | 0.015977 | 0.020754 | 0.0018884 | 0.035286 | 0.00092287 | -0.043754 | -0.013123 | -0.0053385 | 0.10329 | 0.085768 | -0.18097 | 0.0093374 | 0.064087 | 0.10529 | 0.16022 | 0.15564 | 0.17395 | 0.09613 | 0.004578 | 5.7358 | 29.5303 | -26.9577 | 93.6813 | 93.7866 | -27.2232 | -27.3331 | 27.4292 | 27.3376 | -93.6218 | 27.4384 | 27.4887 | 0.15106 | -93.7317 | 0.10986 | 0 | -0.11444 | 33.0688 | 0.37537 | 0.37537 | -0.009155 | 27.507 | 27.3972 | 27.4933 | -93.7912 | 121.0144 | 121.1197 | 56.8634 | -121.1288
2682.4844 | 121.3394 | -28.1021 | 92.9443 | -0.020218 | 0.012773 | 0.016908 | 0.00060662 | 0.031441 | 0.0015637 | -0.046531 | -0.0054932 | -0.0038431 | 0.10115 | 0.08769 | -0.18054 | 0.0080558 | 0.11902 | 0.16022 | 0.23804 | 0.20599 | 0.15106 | 0.16479 | 0.032043 | 5.159 | 28.8025 | -27.6901 | 92.8162 | 92.8986 | -28.0106 | -28.1021 | 28.2669 | 28.1342 | -92.7933 | 28.2623 | 28.3081 | 0.17395 | -92.8253 | 0.091553 | 0 | -0.12817 | 33.2611 | 0.41199 | 0.41199 | -0.045776 | 28.2532 | 28.2211 | 28.3401 | -92.9123 | 120.9183 | 121.0007 | 56.9046 | -121.0464
2684.2031 | 121.3531 | -27.7634 | 93.2785 | -0.0049592 | 0.0091409 | 0.021608 | -0.00024778 | 0.033364 | -0.0037769 | -0.049736 | -0.013123 | -0.0089701 | 0.1003 | 0.087477 | -0.18353 | 0.010833 | 0.1236 | 0.18768 | 0.24719 | 0.21973 | 0.14191 | 0.16937 | 0.036621 | 5.4794 | 29.155 | -27.3285 | 93.1458 | 93.2648 | -27.6672 | -27.7908 | 27.9327 | 27.8 | -93.1366 | 27.951 | 27.9831 | 0.18311 | -93.1549 | 0.096131 | -0.027466 | -0.13275 | 33.2428 | 0.43488 | 0.46234 | -0.013732 | 27.9053 | 27.887 | 28.0106 | -93.2419 | 120.9091 | 121.0281 | 56.9183 | -121.0693
2685.9844 | 121.3211 | -24.1425 | 96.9635 | -0.012589 | 0.0087137 | 0.019685 | 0.00060662 | 0.034859 | -0.0024951 | -0.04824 | -0.013123 | -0.0066201 | 0.099228 | 0.082777 | -0.17733 | 0.010833 | 0.10986 | 0.17853 | 0.23804 | 0.2243 | 0.16022 | 0.16479 | 0.054932 | 8.8852 | 32.4692 | -23.6115 | 96.7987 | 96.8903 | -24.0417 | -24.147 | 24.3073 | 24.1974 | -96.8033 | 24.321 | 24.3668 | 0.16937 | -96.8536 | 0.10071 | -0.004578 | -0.16479 | 33.0276 | 0.53101 | 0.53558 | -0.073242 | 24.3027 | 24.2523 | 24.3805 | -96.9086 | 120.9412 | 121.0327 | 56.6116 | -121.1105
2687.75 | 121.3257 | -24.3622 | 96.7667 | -0.012589 | 0.011918 | 0.020967 | 0.001034 | 0.035713 | -0.0018543 | -0.046104 | -0.013123 | -0.0057657 | 0.10008 | 0.088117 | -0.17883 | 0.0086966 | 0.13733 | 0.16022 | 0.23346 | 0.21057 | 0.16479 | 0.17853 | 0.068665 | 8.7753 | 32.2678 | -23.7808 | 96.6248 | 96.7026 | -24.2386 | -24.3256 | 24.5407 | 24.4308 | -96.6019 | 24.5224 | 24.5728 | 0.14191 | -96.6293 | 0.1236 | 0.036621 | -0.14191 | 33.1375 | 0.58136 | 0.54474 | -0.064087 | 24.527 | 24.4995 | 24.5956 | -96.698 | 120.9869 | 121.0648 | 56.6299 | -121.0922
2689.4531 | 121.3348 | -24.0875 | 96.9589 | 0.0026703 | 0.013627 | 0.017336 | -0.00024778 | 0.031441 | 0.0030591 | -0.04824 | -0.020752 | -0.0032021 | 0.1003 | 0.088331 | -0.17392 | 0.0082694 | 0.11902 | 0.09613 | 0.16479 | 0.16479 | 0.19684 | 0.12817 | 0.041199 | 9.0225 | 32.3318 | -23.6206 | 96.8719 | 96.936 | -24.0372 | -24.1379 | 24.2157 | 24.1287 | -96.7621 | 24.1837 | 24.2523 | 0.1236 | -96.8399 | 0.050354 | -0.050354 | -0.086975 | 33.11 | 0.46692 | 0.51727 | -0.022888 | 24.2844 | 24.2065 | 24.2523 | -96.9177 | 120.9595 | 121.0236 | 56.4194 | -121.0968
2691.2969 | 121.2067 | -23.9868 | 97.1832 | -0.0049592 | 0.015763 | 0.017122 | -0.0015296 | 0.034645 | 0.0047681 | -0.046531 | 0.0021363 | -0.0025613 | 0.10222 | 0.088545 | -0.17199 | 0.0078422 | 0.11444 | 0.10071 | 0.15564 | 0.16937 | 0.19684 | 0.14191 | 0.050354 | 9.2056 | 32.4921 | -23.4741 | 97.0459 | 97.1558 | -23.8678 | -23.9594 | 24.1287 | 24.0372 | -96.9864 | 24.0875 | 24.1562 | 0.11902 | -97.0688 | 0.11902 | 0.027465 | -0.13733 | 33.1924 | 0.5127 | 0.48523 | -0.027466 | 24.1837 | 24.1013 | 24.1425 | -97.1329 | 121.0327 | 121.1426 | 56.4789 | -121.1426
2693.0781 | 121.257 | -23.8724 | 97.261 | -0.0049592 | 0.014482 | 0.018404 | 0.0027428 | 0.033577 | -0.00099973 | -0.046959 | -0.013123 | -0.0044839 | 0.10521 | 0.087477 | -0.17798 | 0.0097648 | 0.09613 | 0.086975 | 0.17853 | 0.16479 | 0.19226 | 0.12817 | 0.022888 | 9.343 | 32.6065 | -23.3688 | 97.1466 | 97.2336 | -23.79 | -23.8678 | 24.0005 | 23.8953 | -97.0688 | 23.9594 | 24.0372 | 0.14191 | -97.1649 | 0.082397 | 0.004577 | -0.11444 | 33.2153 | 0.50354 | 0.49896 | -0.027465 | 24.0646 | 23.9685 | 24.0509 | -97.2382 | 121.019 | 121.106 | 56.4789 | -121.1288
2694.8594 | 121.3257 | -24.7101 | 96.3913 | -0.0049592 | 0.0085001 | 0.019045 | -0.0017432 | 0.032509 | -0.0016405 | -0.043754 | 0.0021363 | -0.0053385 | 0.10094 | 0.088758 | -0.17691 | 0.010833 | 0.19226 | 0.21515 | 0.27924 | 0.23804 | 0.13733 | 0.17395 | 0.068665 | 8.6426 | 31.8741 | -24.4217 | 96.1945 | 96.2997 | -24.646 | -24.733 | 24.884 | 24.7787 | -96.254 | 24.9252 | 24.9481 | 0.16937 | -96.199 | 0.064087 | -0.022888 | -0.19684 | 33.3527 | 0.28839 | 0.31128 | -0.091552 | 24.8474 | 24.9023 | 24.9893 | -96.3226 | 120.9045 | 121.0098 | 56.5842 | -121.1243
2696.5781 | 121.3303 | -24.1287 | 97.0001 | -0.012589 | 0.011064 | 0.01584 | 0.00082022 | 0.029518 | -0.0020679 | -0.046745 | -0.0054932 | -0.0061929 | 0.10265 | 0.089826 | -0.17669 | 0.0093374 | 0.19684 | 0.21515 | 0.29755 | 0.23804 | 0.13275 | 0.17395 | 0.073242 | 9.2651 | 32.4326 | -23.5062 | 96.8262 | 96.9681 | -24.028 | -24.1287 | 24.3027 | 24.202 | -96.8674 | 24.3439 | 24.3668 | 0.16479 | -96.8033 | 0.10071 | 0 | -0.17395 | 33.3939 | 0.62256 | 0.62256 | -0.032043 | 24.2615 | 24.3256 | 24.4263 | -96.9269 | 120.9549 | 121.0968 | 56.5613 | -121.1288
2698.3438 | 121.344 | -24.3027 | 96.7575 | -0.0049592 | 0.011704 | 0.016695 | -0.003025 | 0.034645 | 0.0011365 | -0.047172 | -0.0054932 | -0.0081155 | 0.10158 | 0.089613 | -0.17477 | 0.0082694 | 0.19684 | 0.19684 | 0.28381 | 0.23804 | 0.14191 | 0.17853 | 0.073242 | 9.1461 | 32.2174 | -23.6984 | 96.6339 | 96.7667 | -24.202 | -24.2844 | 24.4812 | 24.3759 | -96.6156 | 24.4995 | 24.5407 | 0.16479 | -96.5607 | 0.10071 | 0.01831 | -0.1236 | 33.4488 | 0.60425 | 0.58594 | 0.009156 | 24.4446 | 24.4995 | 24.5865 | -96.6843 | 120.9366 | 121.0693 | 56.5201 | -121.0419
2700.0469 | 121.2845 | -24.5453 | 96.611 | -0.0049592 | 0.012773 | 0.019258 | 0.0016748 | 0.034004 | -0.0016405 | -0.04824 | -0.0054932 | -0.0083291 | 0.10222 | 0.086836 | -0.17691 | 0.0082694 | 0.16022 | 0.19684 | 0.28839 | 0.21057 | 0.1236 | 0.15564 | 0.054932 | 8.9722 | 32.0572 | -23.8586 | 96.46 | 96.5744 | -24.4034 | -24.5087 | 24.7009 | 24.6002 | -96.4874 | 24.7421 | 24.7559 | 0.15564 | -96.4508 | 0.14191 | 0.036621 | -0.15106 | 33.5175 | 0.68664 | 0.65002 | -0.036621 | 24.6689 | 24.7055 | 24.8337 | -96.5561 | 121.0052 | 121.1197 | 56.6025 | -121.1197
2701.8281 | 121.3303 | -23.2773 | 97.8653 | -0.0049592 | 0.0063639 | 0.018831 | -0.00088858 | 0.032295 | -0.0018543 | -0.049736 | -0.013123 | -0.0066201 | 0.102 | 0.086836 | -0.17819 | 0.0080558 | 0.14648 | 0.16937 | 0.25177 | 0.19226 | 0.13733 | 0.15106 | 0.050354 | 10.1303 | 33.0826 | -22.6181 | 97.728 | 97.8333 | -23.1583 | -23.2407 | 23.4283 | 23.3276 | -97.728 | 23.4467 | 23.4695 | 0.14191 | -97.7188 | 0.11902 | 0.036621 | -0.13733 | 33.4076 | 0.65918 | 0.62256 | -0.032043 | 23.4146 | 23.4238 | 23.5291 | -97.8149 | 121.0052 | 121.1105 | 56.3599 | -121.106
2703.5469 | 121.2936 | -24.0784 | 97.0779 | -0.012589 | 0.020036 | 0.018617 | 0.0012476 | 0.032723 | 0.0064771 | -0.044822 | -0.020752 | -0.0027749 | 0.10564 | 0.088972 | -0.17306 | 0.0063468 | 0.14648 | 0.12817 | 0.19226 | 0.19226 | 0.15564 | 0.12817 | 0.036621 | 9.4528 | 32.3227 | -23.4467 | 96.9681 | 97.0459 | -23.9594 | -24.0601 | 24.2065 | 24.115 | -96.9223 | 24.2065 | 24.2706 | 0.15564 | -96.9315 | 0.11902 | 0.01831 | -0.10986 | 33.5312 | 0.63171 | 0.6134 | -0.032044 | 24.234 | 24.2249 | 24.2706 | -97.0413 | 121.0464 | 121.1243 | 56.4011 | -121.138
2705.3125 | 121.2662 | -24.0326 | 97.1512 | -0.020218 | 0.012773 | 0.020326 | 0.0012476 | 0.03315 | -0.0012133 | -0.044822 | -0.0054932 | -0.0059793 | 0.10307 | 0.087049 | -0.17584 | 0.0097648 | 0.1236 | 0.17395 | 0.2243 | 0.20599 | 0.14191 | 0.15106 | 0.036621 | 9.4849 | 32.3914 | -23.4009 | 97.023 | 97.1008 | -23.9182 | -24.0143 | 24.1837 | 24.0692 | -97.0093 | 24.2065 | 24.2386 | 0.16937 | -97.0276 | 0.11444 | 0.018311 | -0.12817 | 33.5175 | 0.63171 | 0.6134 | -0.050354 | 24.1745 | 24.1562 | 24.2569 | -97.1146 | 121.0556 | 121.1334 | 56.4239 | -121.1655
2707.0938 | 121.4081 | -23.7808 | 97.3251 | -0.0049592 | 0.0097817 | 0.020754 | 0.0031702 | 0.031441 | -0.0018543 | -0.047172 | -0.0054932 | -0.0079019 | 0.10435 | 0.08769 | -0.17669 | 0.0089102 | 0.10071 | 0.16022 | 0.23346 | 0.20142 | 0.13733 | 0.15564 | 0.059509 | 9.7321 | 32.6157 | -23.0942 | 97.2015 | 97.2931 | -23.6664 | -23.7671 | 23.9365 | 23.8403 | -97.1878 | 23.941 | 23.9822 | 0.14191 | -97.2244 | 0.11444 | 0.013733 | -0.1236 | 33.5129 | 0.68665 | 0.67291 | -0.032043 | 23.9182 | 23.8815 | 24.0143 | -97.2656 | 120.9824 | 121.0739 | 56.3965 | -121.0922
2708.8125 | 121.3257 | -23.5519 | 97.6135 | -0.012589 | 0.015336 | 0.016908 | -0.001316 | 0.03315 | 0.0058363 | -0.048027 | -0.013123 | -0.0038431 | 0.10136 | 0.087477 | -0.17135 | 0.0078422 | 0.086975 | 0.10986 | 0.15564 | 0.17395 | 0.1831 | 0.13275 | 0.027466 | 9.9609 | 32.7209 | -22.9385 | 97.4991 | 97.5815 | -23.465 | -23.5703 | 23.6847 | 23.5794 | -97.4304 | 23.6618 | 23.7259 | 0.14648 | -97.5266 | 0.086975 | -0.01831 | -0.11444 | 33.5129 | 0.6134 | 0.63171 | -0.032043 | 23.735 | 23.6389 | 23.7076 | -97.5861 | 121.051 | 121.1334 | 56.2729 | -121.1838
2710.5938 | 121.3577 | -23.2864 | 97.847 | -0.0049592 | 0.011064 | 0.019472 | 0.002102 | 0.031227 | -0.0024951 | -0.048027 | 0.0021363 | -0.0074747 | 0.10222 | 0.08769 | -0.17733 | 0.0086966 | 0.11902 | 0.17395 | 0.20599 | 0.18768 | 0.12817 | 0.17853 | 0.059509 | 10.2539 | 32.9498 | -22.5861 | 97.6959 | 97.8607 | -23.1628 | -23.2773 | 23.465 | 23.3459 | -97.7188 | 23.4604 | 23.4741 | 0.12817 | -97.728 | 0.1236 | 0.009155 | -0.15106 | 33.5403 | 0.70038 | 0.69122 | 0.013733 | 23.4146 | 23.4055 | 23.4924 | -97.7875 | 120.9824 | 121.1472 | 56.2363 | -121.1243
2712.375 | 121.4035 | -23.2452 | 97.8745 | -0.012589 | 0.015122 | 0.01584 | 0.0012476 | 0.031441 | 0.0049817 | -0.044395 | -0.0054932 | -0.0025613 | 0.10606 | 0.088758 | -0.17135 | 0.0074148 | 0.09613 | 0.073242 | 0.11444 | 0.15106 | 0.15106 | 0.16937 | 0.054932 | 10.318 | 32.9681 | -22.6044 | 97.7509 | 97.8973 | -23.1491 | -23.2407 | 23.4146 | 23.3002 | -97.7234 | 23.3185 | 23.3963 | 0.09613 | -97.7783 | 0.09613 | 0.004577 | -0.1236 | 33.5632 | 0.64087 | 0.63629 | 0.022888 | 23.3963 | 23.3414 | 23.3597 | -97.8195 | 120.9961 | 121.1426 | 56.2134 | -121.1151
2714.0938 | 121.312 | -22.7783 | 98.4009 | 0.0026703 | 0.017259 | 0.01819 | 0.00552 | 0.032295 | 0.0032727 | -0.04525 | -0.013123 | -0.0038431 | 0.1082 | 0.089186 | -0.17221 | 0.0099784 | 0.082397 | 0.082397 | 0.10529 | 0.17853 | 0.18768 | 0.13733 | 0.032043 | 10.7803 | 33.4213 | -22.0688 | 98.3276 | 98.4329 | -22.6685 | -22.7554 | 22.9156 | 22.8104 | -98.2132 | 22.8607 | 22.9568 | 0.14648 | -98.3185 | 0.10986 | 0.022888 | -0.073242 | 33.5587 | 0.70953 | 0.68664 | 0.032043 | 22.966 | 22.8607 | 22.8836 | -98.3688 | 121.106 | 121.2112 | 56.1996 | -121.1563
2715.875 | 121.3074 | -24.0234 | 97.1512 | -0.012589 | 0.014695 | 0.01819 | 0.0018884 | 0.031441 | 0.0032727 | -0.046104 | -0.0054932 | -0.0034159 | 0.10692 | 0.090254 | -0.17199 | 0.0097648 | 0.11902 | 0.10529 | 0.12817 | 0.1831 | 0.12817 | 0.14648 | 0.027466 | 9.6863 | 32.1899 | -23.3093 | 97.023 | 97.1466 | -23.9365 | -24.0097 | 24.1699 | 24.0509 | -97.023 | 24.1287 | 24.2065 | 0.15564 | -97.0322 | 0.086975 | 0.013732 | -0.12817 | 33.7097 | 0.71411 | 0.70038 | -0.004578 | 24.1516 | 24.1425 | 24.1516 | -97.1237 | 121.0464 | 121.17 | 56.2134 | -121.1609
2717.6562 | 121.3806 | -22.7325 | 98.3871 | -0.012589 | 0.011064 | 0.019899 | 0.0027428 | 0.035073 | -0.0061267 | -0.046104 | -0.013123 | -0.01132 | 0.10393 | 0.086408 | -0.1752 | 0.012969 | 0.15564 | 0.24261 | 0.24261 | 0.24261 | 0.11444 | 0.16937 | 0.050354 | 10.8948 | 33.4717 | -21.9681 | 98.2407 | 98.3597 | -22.6135 | -22.7371 | 22.9019 | 22.7829 | -98.2727 | 22.9752 | 22.9752 | 0.19226 | -98.2315 | 0.11902 | -0.004578 | -0.14648 | 33.6273 | 0.76447 | 0.76904 | -0.027466 | 22.847 | 22.8882 | 22.9752 | -98.3368 | 120.9732 | 121.0922 | 56.2042 | -121.1243
2719.375 | 121.2936 | -21.8719 | 99.3942 | -0.0049592 | 0.013413 | 0.019472 | 0.0016748 | 0.034859 | 0.00070927 | -0.045677 | -0.013123 | -0.0038431 | 0.10265 | 0.087263 | -0.17349 | 0.0097648 | -0.027466 | 0.009155 | 0.022888 | 0.068665 | 0.082397 | 0.054932 | -0.059509 | 11.6409 | 34.1812 | -21.1578 | 99.2386 | 99.353 | -21.7484 | -21.8445 | 21.9269 | 21.8124 | -99.3118 | 21.8811 | 21.9406 | 0.12817 | -99.4217 | 0.1236 | 0.027466 | -0.15564 | 33.5129 | 0.71411 | 0.68664 | -0.041199 | 21.9543 | 21.8445 | 21.8948 | -99.4537 | 121.1105 | 121.225 | 56.0532 | -121.2387
2721.1562 | 121.344 | -21.2402 | 99.9664 | -0.012589 | 0.017686 | 0.014131 | 0.0023156 | 0.0355 | 0.0056225 | -0.044609 | -0.0054932 | -0.0029885 | 0.10329 | 0.088331 | -0.17071 | 0.0080558 | 0.009155 | 0.018311 | 0.032043 | 0.07782 | 0.041199 | 0.022888 | -0.082397 | 12.3322 | 34.7672 | -20.4758 | 99.8749 | 100.0031 | -21.0846 | -21.1899 | 21.2631 | 21.1578 | -99.9252 | 21.2585 | 21.3181 | 0.16022 | -99.9573 | 0.15564 | 0.050354 | -0.091553 | 33.5724 | 0.76447 | 0.71411 | 0.036621 | 21.2814 | 21.2494 | 21.2723 | -100.0488 | 121.1151 | 121.2433 | 56.0074 | -121.1563
2722.9375 | 121.3394 | -21.0205 | 100.1862 | -0.0049592 | 0.01555 | 0.015627 | -0.0011024 | 0.029518 | 0.0032727 | -0.045463 | -0.0054932 | -0.0027749 | 0.10414 | 0.089399 | -0.16836 | 0.011687 | -0.054932 | -0.07782 | -0.050354 | 0.027466 | 0.054932 | 0.036621 | -0.07782 | 12.442 | 34.7992 | -20.2835 | 100.1083 | 100.1999 | -20.9015 | -21.0022 | 21.0571 | 20.9427 | -100.1312 | 20.9427 | 21.048 | 0.10529 | -100.2411 | 0.11902 | 0.018311 | -0.07782 | 33.4625 | 0.737 | 0.71869 | 0.013733 | 21.0754 | 20.9656 | 20.9702 | -100.264 | 121.1288 | 121.2204 | 55.8197 | -121.1884
2724.6562 | 121.4172 | -21.904 | 99.2477 | -0.012589 | 0.012132 | 0.017976 | 0.0042382 | 0.032295 | -0.0071947 | -0.045891 | -0.013123 | -0.010679 | 0.10585 | 0.086408 | -0.17669 | 0.010833 | 0.018311 | 0.082397 | 0.086975 | 0.091553 | 0.013733 | 0.064087 | -0.059509 | 11.6959 | 34.0576 | -21.0938 | 99.0921 | 99.234 | -21.7987 | -21.8948 | 21.9681 | 21.8445 | -99.234 | 21.9864 | 21.9955 | 0.15106 | -99.2294 | 0.10529 | 0.009156 | -0.15564 | 33.5999 | 0.81024 | 0.80109 | -0.013733 | 21.9177 | 21.9223 | 21.991 | -99.3073 | 120.9961 | 121.138 | 55.9616 | -121.1426
2726.4375 | 121.3715 | -18.8049 | 102.42 | -0.0049592 | 0.013413 | 0.016481 | 0.003811 | 0.033577 | -0.0029223 | -0.04824 | -0.013123 | -0.0068337 | 0.10414 | 0.09004 | -0.16879 | 0.011901 | -0.018311 | 0.009155 | 0.059509 | 0.054932 | 0.009155 | 0.064087 | -0.036621 | 14.5706 | 36.9415 | -17.8024 | 102.2781 | 102.42 | -18.6356 | -18.7454 | 18.869 | 18.7683 | -102.4109 | 18.8141 | 18.8599 | 0.091553 | -102.4384 | 0.16937 | 0.05951 | -0.14191 | 33.3756 | 1.0025 | 0.94299 | 0 | 18.8141 | 18.7866 | 18.8644 | -102.4567 | 121.0831 | 121.225 | 55.7465 | -121.1655
2728.1562 | 121.376 | -17.4728 | 103.7109 | -0.020218 | 0.013627 | 0.01819 | -0.00067498 | 0.031227 | -0.00099973 | -0.04824 | -0.013123 | -0.0072611 | 0.10521 | 0.08769 | -0.16516 | 0.011046 | 0.022888 | 0.086975 | 0.10071 | 0.082397 | -0.004578 | 0.07782 | -0.054932 | 15.8432 | 38.15 | -16.4566 | 103.6057 | 103.6972 | -17.3309 | -17.4362 | 17.5507 | 17.4179 | -103.7155 | 17.5598 | 17.5552 | 0.13733 | -103.688 | 0.14191 | 0.036621 | -0.10528 | 33.316 | 1.0162 | 0.97961 | -0.013732 | 17.4683 | 17.4957 | 17.5735 | -103.7659 | 121.0785 | 121.17 | 55.6229 | -121.1472
2729.9375 | 121.4355 | -16.8365 | 104.3655 | -0.012589 | 0.014054 | 0.013918 | -0.0017432 | 0.032936 | 0.0045545 | -0.047172 | 0.0021363 | -0.0027749 | 0.10585 | 0.090254 | -0.16238 | 0.0076286 | -0.027466 | -0.022888 | 0.018311 | 0.022888 | 0.036621 | 0.045776 | -0.059509 | 16.4658 | 38.6307 | -15.7928 | 104.2465 | 104.3472 | -16.7404 | -16.8365 | 16.8823 | 16.777 | -104.3289 | 16.8137 | 16.8594 | 0.082397 | -104.393 | 0.096131 | 0 | -0.11902 | 33.3023 | 1.0437 | 1.0437 | -0.018311 | 16.8732 | 16.8091 | 16.8549 | -104.425 | 121.0831 | 121.1838 | 55.4672 | -121.2021
2731.6562 | 121.3531 | -16.6534 | 104.5761 | -0.012589 | 0.016618 | 0.017549 | 0.00060662 | 0.033577 | 0.0043409 | -0.044395 | 0.0021363 | -0.0049111 | 0.10649 | 0.085554 | -0.15875 | 0.010192 | -0.009155 | -0.004578 | 0.018311 | 0.054932 | 0.041199 | 0.018311 | -0.086975 | 16.6672 | 38.7909 | -15.4724 | 104.4708 | 104.5807 | -16.5253 | -16.6077 | 16.6718 | 16.5665 | -104.5349 | 16.6489 | 16.7084 | 0.14191 | -104.5853 | 0.12817 | 0.045776 | -0.10529 | 33.3206 | 1.181 | 1.1353 | 0.004577 | 16.6946 | 16.6443 | 16.6718 | -104.6631 | 121.1243 | 121.2341 | 55.4443 | -121.1838
2733.4219 | 121.3211 | -14.7446 | 106.5353 | -0.012589 | 0.012986 | 0.019258 | -0.00046138 | 0.031441 | 0.00070927 | -0.047813 | -0.028381 | -0.0057657 | 0.10564 | 0.085768 | -0.16195 | 0.01126 | 0.11444 | 0.12817 | 0.14648 | 0.20142 | 0.23346 | 0.17395 | 0.054932 | 18.3197 | 40.4526 | -13.5635 | 106.3843 | 106.517 | -14.6439 | -14.7034 | 14.9185 | 14.7995 | -106.3019 | 14.8727 | 14.946 | 0.14648 | -106.4209 | 0.10071 | 0.041199 | -0.15106 | 33.0643 | 1.181 | 1.1398 | -0.01831 | 14.978 | 14.859 | 14.8911 | -106.4804 | 121.1288 | 121.2616 | 55.1971 | -121.2387
2735.125 | 121.344 | -10.8627 | 110.4309 | 0.0026703 | 0.014054 | 0.017336 | 0.0018884 | 0.032509 | 0.0045545 | -0.045036 | -0.0054932 | -0.0032021 | 0.10542 | 0.088972 | 2.6585 | 0.0095512 | -0.041199 | -0.036621 | -0.013733 | 0.027466 | 0.054932 | 0.068665 | -0.050354 | 21.9681 | 44.0552 | -10.0937 | 110.3348 | 110.4767 | -10.7071 | -10.762 | 10.9314 | 10.8124 | -110.376 | 10.8261 | 10.8902 | 0.07782 | -110.4721 | 0.15564 | 0.10071 | -0.09613 | 32.8308 | 0.76904 | 0.66834 | 0.045777 | 10.9177 | 10.8215 | 10.849 | -110.4813 | 121.1975 | 121.3394 | 54.9179 | -121.1929
2736.9062 | 121.3257 | -12.5931 | 108.7372 | 0.0103 | 0.01555 | 0.019045 | 0.0040246 | 0.033577 | -0.0018543 | -0.045677 | 0.0021363 | -0.0051247 | 0.10628 | 0.089826 | 2.6267 | 0.0097648 | 0.13275 | 0.15564 | 0.17395 | 0.2243 | 0.26093 | 0.21973 | 0.09613 | 20.4117 | 42.4942 | -10.8856 | 108.5999 | 108.7326 | -12.4374 | -12.5153 | 12.8128 | 12.6892 | -108.4763 | 12.7487 | 12.8174 | 0.12817 | -108.6044 | 0.15564 | 0.07782 | -0.13733 | 33.0048 | 1.7075 | 1.6296 | -0.004578 | 12.854 | 12.7258 | 12.767 | -108.6411 | 121.1929 | 121.3257 | 55.0873 | -121.2524
2738.6719 | 121.4218 | -11.3388 | 107.6431 | -0.012589 | 0.015336 | 0.015627 | 0.00039302 | 0.030159 | 0.0017773 | -0.045677 | -0.013123 | -0.0023477 | 0.10585 | 0.088758 | 2.6807 | 0.011046 | -0.064087 | -0.054932 | -0.036621 | 0.009155 | 0.032043 | 0.009155 | -0.073242 | 18.4021 | 39.5554 | -10.0845 | 105.5878 | 105.4596 | -15.6281 | -15.9851 | 11.348 | 11.2656 | -107.6111 | 11.2839 | 11.348 | 0.082397 | -107.7072 | -4.2892 | -4.6463 | -2.0554 | 29.7409 | 1.2543 | 5.9006 | -2.1835 | 11.3708 | 11.2747 | 11.3022 | -107.7164 | 116.9266 | 116.7984 | 50.8942 | -123.6282
2740.375 | 121.3623 | -10.1028 | 111.1588 | -0.012589 | 0.018754 | 0.015199 | 0.0040246 | 0.032723 | 0.0041273 | -0.045677 | -0.013123 | -0.0038431 | 0.10777 | 0.088972 | 2.619 | 0.0080558 | -0.032043 | -0.009155 | 0.018311 | 0.032043 | 0.036621 | 0.032043 | -0.086975 | 22.7692 | 44.8837 | -9.169 | 111.1862 | 111.3327 | -9.8648 | -9.9197 | 10.1349 | 10.0159 | -111.1221 | 10.0937 | 10.1349 | 0.11902 | -111.1908 | 0.23804 | 0.1831 | 0.027466 | 32.872 | 0.93384 | 0.75073 | 0.17395 | 10.1395 | 10.0708 | 10.1212 | -111.2457 | 121.2891 | 121.4355 | 54.9866 | -121.0785
2742.1562 | 121.344 | -9.6634 | 111.6623 | -0.020218 | 0.016618 | 0.017336 | 0.0031702 | 0.033791 | -0.0024951 | -0.047813 | -0.013123 | -0.0046975 | 0.10841 | 0.086408 | 2.6502 | 0.010619 | -0.082397 | -0.036621 | -0.027466 | 0.013733 | 0.045776 | 0.022888 | -0.073242 | 23.085 | 45.0989 | -8.0338 | 111.5387 | 111.6943 | -9.5352 | -9.5856 | 9.6863 | 9.5901 | -111.6165 | 9.6268 | 9.6771 | 0.086975 | -111.7447 | 0.12817 | 0.07782 | -0.1236 | 32.7484 | 1.6296 | 1.5518 | 0.032044 | 9.7092 | 9.581 | 9.6359 | -111.7355 | 121.2021 | 121.3577 | 54.7623 | -121.2479
2743.875 | 121.3898 | -9.4116 | 111.8958 | -0.012589 | 0.011277 | 0.018831 | -3.4178e-05 | 0.032295 | -0.00035893 | -0.04525 | -0.013123 | -0.010038 | 0.10371 | 0.085768 | 2.6045 | 0.0093374 | 0.022888 | 0.068665 | 0.10986 | 0.09613 | 0 | 0.068665 | -0.041199 | 23.4329 | 45.3278 | -7.663 | 111.7126 | 111.8546 | -9.2789 | -9.3292 | 9.4803 | 9.3704 | -111.8958 | 9.4803 | 9.5078 | 0.13733 | -111.8729 | 0.13275 | 0.082397 | -0.18311 | 32.8445 | 1.7487 | 1.6663 | -0.041199 | 9.4116 | 9.4345 | 9.5215 | -111.937 | 121.1243 | 121.2662 | 54.7394 | -121.225
2745.6562 | 121.431 | -13.3301 | 107.8766 | -0.0049592 | 0.0132 | 0.016054 | 0.0016748 | 0.030586 | 0.00028207 | -0.043968 | -0.013123 | -0.0066201 | 0.10692 | 0.08769 | 2.6519 | 0.0086966 | 0.036621 | 0.036621 | 0.11444 | 0.10529 | -0.018311 | 0.064087 | -0.027466 | 19.7937 | 41.5741 | -11.8469 | 107.7805 | 107.8857 | -13.1836 | -13.2843 | 13.3942 | 13.3026 | -107.8949 | 13.3667 | 13.4354 | 0.13275 | -107.84 | 0.14648 | 0.045776 | -0.09613 | 33.1238 | 1.4832 | 1.4374 | 0.009155 | 13.3118 | 13.3667 | 13.4445 | -107.9041 | 121.1105 | 121.2158 | 54.9042 | -121.1609
2747.4375 | 121.4081 | -11.9888 | 109.2133 | -0.0049592 | 0.012773 | 0.016695 | -0.0017432 | 0.034004 | -0.00099973 | -0.045677 | -0.013123 | -0.0061929 | 0.105 | 0.088117 | 2.6222 | 0.0086966 | 0.022888 | 0.059509 | 0.11444 | 0.091553 | -0.013733 | 0.064087 | -0.027466 | 21.0983 | 42.746 | -9.6222 | 109.0942 | 109.227 | -11.8698 | -11.9431 | 12.0529 | 11.9614 | -109.227 | 12.0483 | 12.0804 | 0.11902 | -109.1904 | 0.11902 | 0.045777 | -0.11902 | 33.0872 | 2.3666 | 2.3209 | 0.013733 | 11.9751 | 12.0117 | 12.1033 | -109.2407 | 121.0831 | 121.2158 | 54.7348 | -121.1563
2749.1562 | 121.3257 | -10.9726 | 110.3806 | -0.0049592 | 0.016831 | 0.016267 | 0.0018884 | 0.032295 | 0.0028455 | -0.046745 | -0.0054932 | -0.0038431 | 0.1082 | 0.089613 | 2.5017 | 0.006774 | -0.004578 | -0.009155 | 0.036621 | 0.054932 | 0.009155 | 0.032043 | -0.054932 | 22.0688 | 43.6249 | -8.345 | 110.2249 | 110.3302 | -10.817 | -10.8948 | 11.0046 | 10.9177 | -110.3714 | 10.9634 | 11.0275 | 0.10986 | -110.3851 | 0.15564 | 0.07782 | -0.15564 | 33.0414 | 2.6276 | 2.5497 | -0.050354 | 10.9817 | 10.968 | 11.0092 | -110.4355 | 121.1975 | 121.3028 | 54.5975 | -121.2753
2750.9219 | 121.3531 | -11.6318 | 109.6802 | -0.0049592 | 0.016191 | 0.015413 | -0.00046138 | 0.033577 | 0.0034863 | -0.043968 | -0.0054932 | -0.0049111 | 0.10905 | 0.088972 | 2.6134 | 0.010192 | 0.10071 | 0.064087 | 0.15564 | 0.19684 | 0.23804 | 0.19684 | 0.068665 | 21.4188 | 42.9657 | -9.0637 | 109.5566 | 109.6664 | -11.4944 | -11.586 | 11.8286 | 11.7004 | -109.4421 | 11.6959 | 11.8286 | 0.12817 | -109.5795 | 0.13733 | 0.045776 | -0.1236 | 33.0505 | 2.5681 | 2.5223 | -0.013733 | 11.8698 | 11.7325 | 11.7874 | -109.6115 | 121.1884 | 121.2982 | 54.5975 | -121.2662
2752.6406 | 121.4767 | -9.1782 | 112.0377 | 0.0103 | 0.013627 | 0.02054 | 0.003811 | 0.032936 | -0.0061267 | -0.049095 | -0.013123 | -0.0093973 | 0.10628 | 0.087263 | 2.6495 | 0.012755 | 0.17395 | 0.22888 | 0.3067 | 0.2655 | 0.20599 | 0.2243 | 0.10071 | 23.6023 | 45.282 | -7.6126 | 111.9232 | 112.0651 | -9.0134 | -9.0317 | 9.4025 | 9.2789 | -111.8317 | 9.407 | 9.4437 | 0.16479 | -111.8637 | 0.16479 | 0.14649 | -0.11444 | 32.7805 | 1.5656 | 1.4191 | 0.027466 | 9.3842 | 9.3521 | 9.4849 | -111.937 | 121.1014 | 121.2433 | 54.4601 | -121.0693
2754.4219 | 121.4264 | -11.3937 | 109.8358 | -0.0049592 | 0.0065775 | 0.017976 | -0.0017432 | 0.031655 | -0.0020679 | -0.048454 | -0.013123 | -0.0072611 | 0.10521 | 0.087049 | 2.5782 | 0.010833 | 0.14191 | 0.17395 | 0.27008 | 0.24719 | 0.17853 | 0.22888 | 0.11902 | 21.6476 | 43.1625 | -8.5098 | 109.7031 | 109.8495 | -11.2747 | -11.3388 | 11.6226 | 11.5128 | -109.6573 | 11.5677 | 11.6409 | 0.12817 | -109.6939 | 0.11902 | 0.054932 | -0.13275 | 33.0414 | 2.8839 | 2.829 | 0.013733 | 11.5723 | 11.5356 | 11.6638 | -109.7168 | 121.0968 | 121.2433 | 54.5563 | -121.1746
2756.1406 | 121.4676 | -12.735 | 108.4534 | -0.0049592 | 0.012345 | 0.017763 | 0.001034 | 0.0355 | 0.00028207 | -0.04525 | -0.013123 | -0.0059793 | 0.10414 | 0.086622 | 2.5818 | 0.0091238 | 0.20599 | 0.19684 | 0.27466 | 0.2655 | 0.16479 | 0.21057 | 0.10986 | 20.6268 | 41.954 | -8.0887 | 108.3252 | 108.4167 | -12.6434 | -12.6938 | 12.9456 | 12.8448 | -108.2886 | 12.9318 | 13.0005 | 0.15564 | -108.2474 | 0.091552 | 0.041198 | -0.12817 | 33.3618 | 4.6463 | 4.6051 | -0.036621 | 12.8998 | 12.941 | 13.0096 | -108.3435 | 121.0602 | 121.1517 | 54.689 | -121.1472
2757.9375 | 121.3623 | -12.5885 | 108.6777 | -0.0049592 | 0.012559 | 0.02054 | 0.0050928 | 0.032509 | -0.0020679 | -0.049736 | -0.013123 | -0.0085427 | 0.10905 | 0.089399 | 2.557 | 0.0093374 | 0.1831 | 0.22888 | 0.29755 | 0.2655 | 0.16937 | 0.20142 | 0.09613 | 20.9152 | 42.2333 | -6.7429 | 108.5587 | 108.6731 | -12.4237 | -12.4649 | 12.7899 | 12.6846 | -108.5083 | 12.8174 | 12.854 | 0.16937 | -108.4946 | 0.1648 | 0.1236 | -0.11902 | 33.5037 | 5.8456 | 5.722 | -0.004577 | 12.7579 | 12.7716 | 12.886 | -108.5815 | 121.1472 | 121.2616 | 54.8218 | -121.1426
2759.6562 | 121.4447 | -12.5015 | 108.6731 | -0.020218 | 0.013627 | 0.014131 | 0.0012476 | 0.031868 | 0.0024183 | -0.045463 | -0.013123 | -0.0012795 | 0.10606 | 0.091108 | 2.5805 | 0.010192 | 0.21057 | 0.1831 | 0.26093 | 0.27466 | 0.16479 | 0.19226 | 0.10071 | 20.9564 | 42.1005 | -5.8502 | 108.4991 | 108.5999 | -12.4649 | -12.5198 | 12.6938 | 12.6022 | -108.5083 | 12.6846 | 12.7762 | 0.17395 | -108.4625 | 0.036621 | -0.01831 | -0.17395 | 33.4579 | 6.6513 | 6.6696 | -0.073242 | 12.6663 | 12.7121 | 12.7625 | -108.5724 | 121.0007 | 121.1014 | 54.6021 | -121.1929
2761.4219 | 121.4767 | -8.9676 | 111.7813 | -0.012589 | 0.014054 | 0.017549 | 0.0023156 | 0.033364 | 0.00092287 | -0.048454 | -0.013123 | -0.0055521 | 0.1067 | 0.087904 | 2.579 | 0.0082694 | 0.18768 | 0.20599 | 0.27466 | 0.25635 | 0.17853 | 0.19684 | 0.082397 | 23.7167 | 45.7169 | -6.2714 | 112.619 | 111.5707 | -9.2606 | -10.112 | 9.1644 | 9.05 | -111.6028 | 9.1736 | 9.2239 | 0.17395 | -111.5936 | -0.29297 | -1.1444 | 0.83771 | 32.6843 | 2.6962 | 3.8406 | -0.21057 | 9.1461 | 9.1553 | 9.2422 | -111.6989 | 121.5866 | 120.5383 | 54.6844 | -121.8933
2763.1875 | 121.3303 | -6.3171 | 115.1459 | -0.012589 | 0.016618 | 0.018831 | 0.003811 | 0.034004 | 0.00070927 | -0.046959 | 0.0021363 | -0.0061929 | 0.10457 | 0.086195 | 2.544 | 0.0086966 | 0.027466 | 0.054932 | 0.15564 | 0.091553 | 0.027466 | 0.050354 | -0.068665 | 26.1429 | 46.7011 | -5.3192 | 112.825 | 111.9553 | -8.3359 | -9.5032 | 6.3675 | 6.2485 | -115.1184 | 6.3721 | 6.4087 | 0.16022 | -115.1184 | -2.0187 | -3.186 | -2.3209 | 32.46 | 0.99793 | 4.184 | -3.1906 | 6.3446 | 6.3446 | 6.4728 | -115.2145 | 119.1422 | 118.2724 | 53.0182 | -124.649
2764.8906 | 121.5225 | -4.8614 | 113.3881 | -0.012589 | 0.011064 | 0.014986 | -0.0015296 | 0.033577 | 0.0034863 | -0.04525 | -0.0054932 | -0.0036295 | 0.10542 | 0.089613 | 2.5656 | 0.0089102 | 0.022888 | -0.004578 | 0.1236 | 0.091553 | 0.059509 | 0.073242 | -0.013733 | 25.7217 | 47.7448 | -5.5389 | 114.5782 | 114.7476 | -6.34 | -6.2897 | 4.9347 | 4.8477 | -113.3286 | 4.8569 | 4.953 | 0.10529 | -113.3652 | -1.4786 | -1.4282 | 1.1902 | 30.5832 | -0.67749 | 0.75073 | 1.3596 | 4.921 | 4.8843 | 4.985 | -113.4018 | 119.4397 | 119.6091 | 52.6062 | -119.6777
2766.6719 | 121.3806 | -18.1274 | 103.1525 | -0.0049592 | 0.013841 | 0.017336 | 0.00017942 | 0.035286 | -0.00057253 | -0.046318 | -0.0054932 | -0.0083291 | 0.10713 | 0.091749 | 2.5951 | 0.010833 | 0.1831 | 0.15564 | 0.24719 | 0.21057 | 0.12817 | 0.16937 | 0.059509 | 13.8062 | 36.5662 | -5.2963 | 102.9144 | 103.9719 | -17.2623 | -16.5619 | 18.2968 | 18.1869 | -103.0243 | 18.2831 | 18.338 | 0.15106 | -102.9694 | 0.86517 | 1.5656 | -0.23804 | 31.9336 | 12.8311 | 11.2656 | 0.8194 | 18.2556 | 18.3105 | 18.3746 | -103.093 | 121.0419 | 122.0993 | 54.6936 | -119.7144
2768.4375 | 121.3028 | -15.5228 | 105.8624 | -0.0049592 | 0.018327 | 0.012636 | 0.0023156 | 0.034218 | 0.0092541 | -0.046318 | -0.0054932 | -0.0019205 | 0.1082 | 0.091322 | 2.5585 | 0.008483 | 0.10986 | 0.054932 | 0.14191 | 0.16479 | 0.16937 | 0.15564 | 0.041199 | 17.8299 | 39.5233 | -5.7495 | 105.7205 | 105.8624 | -15.2618 | -15.3122 | 15.6784 | 15.564 | -105.6931 | 15.5777 | 15.6876 | 0.1236 | -105.7526 | 0.26093 | 0.21057 | -0.14191 | 33.3527 | 9.7733 | 9.5627 | 0 | 15.6921 | 15.6326 | 15.6647 | -105.8212 | 121.2433 | 121.3852 | 55.0461 | -121.1746
2770.1562 | 121.3898 | -9.6039 | 111.5662 | -0.0049592 | 0.014268 | 0.016695 | -0.0017432 | 0.030586 | 0.0024183 | -0.045463 | -0.020752 | -0.0059793 | 0.10564 | 0.088331 | 2.6632 | 0.010619 | 0.17395 | 0.17395 | 0.24261 | 0.25635 | 0.16022 | 0.19226 | 0.082397 | 22.3068 | 44.4672 | -6.1523 | 110.7925 | 111.2274 | -9.787 | -9.5078 | 9.7961 | 9.6863 | -111.4059 | 9.7778 | 9.8602 | 0.17395 | -111.3922 | -0.1831 | 0.096131 | -0.77362 | 31.9107 | 3.4515 | 3.3554 | -0.33875 | 9.7641 | 9.7778 | 9.8465 | -111.4838 | 120.3964 | 120.8313 | 54.071 | -121.0739
2771.9375 | 121.4081 | -20.5765 | 100.5615 | -0.0049592 | 0.010636 | 0.01584 | -0.00024778 | 0.032509 | 0.00092287 | -0.043968 | 0.0021363 | -0.0083291 | 0.10564 | 0.093458 | 2.6256 | 0.011474 | 0.050354 | 0.059509 | 0.16022 | 0.11444 | -0.004578 | 0.073242 | -0.036621 | 13.7192 | 34.9091 | -5.5893 | 100.4745 | 100.5936 | -20.4163 | -20.4803 | 20.6497 | 20.5399 | -100.5661 | 20.636 | 20.6909 | 0.15106 | -100.5112 | 0.16022 | 0.09613 | -0.086975 | 34.2957 | 14.9872 | 14.8911 | 0.032044 | 20.5719 | 20.6268 | 20.7367 | -100.5981 | 121.051 | 121.17 | 55.4855 | -121.0419
2773.6562 | 121.3394 | -25.4288 | 95.7504 | 0.0026703 | 0.017259 | 0.01819 | 0.0016748 | 0.032936 | 0.0032727 | -0.046318 | -0.013123 | -0.0032021 | 0.10777 | 0.094526 | 2.6025 | 0.0097648 | -0.064087 | -0.054932 | 0.032043 | 0.059509 | 0.032043 | 0.022888 | -0.09613 | 10.0845 | 30.7617 | -4.454 | 95.9976 | 96.0571 | -24.9252 | -25.058 | 25.4517 | 25.3326 | -95.7184 | 25.3738 | 25.4883 | 0.15564 | -95.8145 | 0.50354 | 0.37079 | 0.24719 | 35.5133 | 20.9747 | 20.6039 | 0.3067 | 25.4608 | 25.3647 | 25.4608 | -95.8466 | 121.4264 | 121.4859 | 56.1905 | -120.8084
2775.4062 | 121.3898 | -29.6631 | 91.2323 | 0.0026703 | 0.015336 | 0.016908 | -0.001316 | 0.032082 | 0.0028455 | -0.043968 | -0.0054932 | -0.0051247 | 0.10521 | 0.096449 | 2.6553 | 0.013824 | -0.064087 | -0.036621 | 0.018311 | 0.027466 | 0.027466 | 0.027466 | -0.082397 | 5.9967 | 26.2939 | -3.6346 | 90.9027 | 91.0492 | -29.8645 | -29.9881 | 29.6906 | 29.5807 | -91.2048 | 29.6265 | 29.6906 | 0.10986 | -91.2964 | -0.20142 | -0.32501 | -0.32959 | 35.6598 | 26.0284 | 26.3535 | -0.18311 | 29.6906 | 29.599 | 29.6814 | -91.3147 | 120.5658 | 120.7123 | 55.957 | -121.2204
2777.1406 | 121.3303 | -36.026 | 84.9792 | -0.012589 | 0.012773 | 0.01819 | -0.002384 | 0.032723 | 0.0024183 | -0.044395 | -0.013123 | -0.0053385 | 0.10478 | 0.10008 | 2.6515 | 0.014678 | 0.009155 | 0.018311 | 0.073242 | 0.091553 | 0.10986 | 0.073242 | -0.027466 | 1.2039 | 20.7413 | -3.5431 | 84.9197 | 84.9609 | -35.8933 | -36.0352 | 36.0992 | 35.9985 | -84.8694 | 36.0443 | 36.1176 | 0.11902 | -84.9701 | 0.13275 | -0.009155 | -0.059509 | 37.2299 | 32.4829 | 32.4921 | -0.018311 | 36.1359 | 36.0352 | 36.0992 | -85.0067 | 120.9457 | 120.9869 | 56.7673 | -121.0144
2778.9062 | 121.3531 | -34.8907 | 86.1099 | -0.0049592 | 0.012345 | 0.017976 | 0.001034 | 0.032509 | 0.00049567 | -0.044395 | -0.0054932 | -0.0057657 | 0.10542 | 0.089399 | 2.6017 | 0.011474 | 0.050354 | 0.032043 | 0.10529 | 0.1236 | 0.12817 | 0.11444 | 0 | 12.5198 | 33.6548 | -14.1586 | 98.6984 | 98.3368 | -22.5357 | -23.0484 | 35.0052 | 34.8907 | -85.9818 | 34.9228 | 35.0143 | 0.1236 | -86.0596 | 12.355 | 11.8423 | 12.5885 | 47.4106 | 20.7321 | 8.8898 | 12.2269 | 35.0189 | 34.9411 | 34.996 | -86.1099 | 133.5892 | 133.2275 | 68.5455 | -109.1583
2780.6719 | 121.2341 | -32.515 | 88.5635 | -0.020218 | 0.015122 | 0.020113 | 0.0016748 | 0.033577 | -0.0022815 | -0.0476 | -0.0054932 | -0.0053385 | 0.10457 | 0.091322 | 2.5983 | 0.012755 | 0.022888 | 0.059509 | 0.12817 | 0.12817 | 0.091553 | 0.07782 | -0.045776 | 3.2959 | 24.3668 | -13.5818 | 88.8199 | 88.8748 | -32.0755 | -32.2128 | 32.5928 | 32.4692 | -88.472 | 32.5745 | 32.6431 | 0.17395 | -88.5406 | 0.43945 | 0.30212 | 0.25635 | 35.8109 | 18.9331 | 18.631 | 0.31128 | 32.6065 | 32.5378 | 32.6431 | -88.6093 | 121.3348 | 121.3898 | 56.8817 | -120.7764
2782.4375 | 121.1334 | -29.7913 | 91.3239 | -0.012589 | 0.012773 | 0.019045 | -0.00046138 | 0.032723 | -0.00078613 | -0.046959 | -0.020752 | -0.0072611 | 0.10243 | 0.095594 | 2.6412 | 0.011687 | -0.027466 | 0.022888 | 0.082397 | 0.073242 | 0.018311 | 0.022888 | -0.082397 | 6.2393 | 26.825 | -1.6067 | 91.2964 | 91.3879 | -29.4525 | -29.567 | 29.8141 | 29.7089 | -91.3055 | 29.8141 | 29.8645 | 0.15564 | -91.3513 | 0.33875 | 0.2243 | -0.027466 | 36.0306 | 28.1845 | 27.9602 | 0.064086 | 29.8096 | 29.7638 | 29.8737 | -91.4062 | 121.0876 | 121.1792 | 56.6162 | -120.8908
2784.1562 | 121.2524 | -45.1538 | 75.769 | 0.0026703 | 0.012986 | 0.017549 | -0.00024778 | 0.031655 | 0.0026319 | -0.045036 | -0.013123 | -0.0034159 | 0.10478 | 0.10243 | 2.6739 | 0.012542 | -0.045776 | -0.041199 | 0 | 0.045776 | 0.054932 | 0.032043 | -0.064087 | -6.221 | 12.4741 | -2.2156 | 75.499 | 75.6042 | -45.1859 | -45.3186 | 45.1859 | 45.0897 | -75.7141 | 45.1126 | 45.1996 | 0.10986 | -75.8148 | -0.032043 | -0.16479 | -0.27008 | 38.9328 | 42.9382 | 43.103 | -0.16479 | 45.2087 | 45.108 | 45.1538 | -75.8331 | 120.6528 | 120.7581 | 57.6279 | -121.0876
2785.9375 | 121.1334 | -45.3873 | 75.531 | -0.012589 | 0.016191 | 0.017122 | 0.001034 | 0.0308 | 0.0051953 | -0.04525 | -0.013123 | -0.0042703 | 0.10307 | 0.10286 | 2.6741 | 0.011474 | 0.022888 | 0.013733 | 0.068665 | 0.082397 | 0.059509 | 0.054932 | -0.068665 | -6.1478 | 12.561 | -1.4282 | 75.5173 | 75.5814 | -45.1447 | -45.2957 | 45.4422 | 45.3186 | -75.4715 | 45.401 | 45.4697 | 0.15106 | -75.5081 | 0.24262 | 0.091553 | -0.013733 | 39.2395 | 43.959 | 43.8675 | 0.050354 | 45.4468 | 45.4102 | 45.4559 | -75.5997 | 120.9045 | 120.9686 | 57.9483 | -120.8267
2787.7188 | 120.8908 | -20.4941 | 102.0905 | -0.020218 | 0.017045 | 0.019258 | 0.0033838 | 0.03315 | 0.00028207 | -0.046104 | -0.0054932 | -0.0036295 | 0.10863 | 0.093244 | 2.5927 | 0.0093374 | -0.004578 | 0.027466 | 0.10071 | 0.09613 | 0.13733 | 0.07782 | -0.004578 | 13.3987 | 36.2961 | -0.99792 | 100.4425 | 100.6485 | -19.8761 | -19.6335 | 20.5719 | 20.4895 | -101.9531 | 20.5215 | 20.5902 | 0.10071 | -102.095 | 0.61798 | 0.8606 | -1.6479 | 33.8928 | 19.4962 | 18.6356 | -1.442 | 20.6314 | 20.4895 | 20.5948 | -102.095 | 120.9366 | 121.1426 | 56.7902 | -121.7239
2789.4844 | 121.2067 | -13.5086 | 108.2565 | -0.012589 | 0.011704 | 0.019685 | -0.00024778 | 0.035073 | -0.0039905 | -0.047172 | -0.028381 | -0.0091837 | 0.10435 | 0.090467 | 2.5357 | 0.01126 | 0.16479 | 0.22888 | 0.28381 | 0.25177 | 0.12817 | 0.19226 | 0.073242 | 15.4999 | 38.4293 | -0.80109 | 103.1342 | 103.3493 | -17.6468 | -17.6239 | 13.7009 | 13.5818 | -108.1284 | 13.7375 | 13.7604 | 0.17853 | -108.0917 | -4.1382 | -4.1153 | -5.1224 | 29.0085 | 12.7075 | 16.8228 | -4.9072 | 13.6368 | 13.6734 | 13.7924 | -108.1833 | 116.6428 | 116.8579 | 51.9379 | -125.8804
2791.2031 | 121.1655 | -37.2757 | 83.7616 | -0.0049592 | 0.015122 | 0.01819 | 0.0033838 | 0.031441 | -0.00099973 | -0.048454 | -0.020752 | -0.0044839 | 0.10735 | 0.10093 | 2.6025 | 0.011046 | 0.013733 | -0.004578 | 0.041199 | 0.086975 | 0.091553 | 0.036621 | -0.041199 | 0.46692 | 20.1187 | -1.4282 | 83.5922 | 83.6792 | -37.1155 | -37.2574 | 37.3123 | 37.2345 | -83.67 | 37.2711 | 37.3627 | 0.12817 | -83.7479 | 0.16022 | 0.018311 | -0.16937 | 37.7426 | 35.8475 | 35.8292 | -0.082398 | 37.3672 | 37.2894 | 37.3169 | -83.8028 | 120.8679 | 120.9549 | 57.3944 | -121.019
2792.9844 | 121.1746 | -44.87 | 75.9384 | -0.0049592 | 0.012559 | 0.018831 | 0.001034 | 0.032295 | 0.0030591 | -0.047172 | -0.013123 | -0.0053385 | 0.10307 | 0.10307 | 2.6758 | 0.012115 | -0.022888 | -0.045776 | 0.018311 | 0.07782 | 0.082397 | 0.036621 | -0.054932 | -6.0287 | 12.8952 | -1.5381 | 75.5997 | 75.6866 | -44.957 | -45.0439 | 44.9066 | 44.8151 | -75.856 | 44.8242 | 44.9478 | 0.13275 | -75.9613 | -0.086975 | -0.17395 | -0.33875 | 38.8412 | 43.3319 | 43.5059 | -0.25177 | 44.9524 | 44.8471 | 44.8883 | -75.9933 | 120.4697 | 120.5566 | 57.7652 | -120.9824
2794.75 | 121.138 | -48.4955 | 72.2809 | -0.012589 | 0.016831 | 0.019472 | 0.0016748 | 0.032295 | 0.0036999 | -0.047172 | 0.0021363 | -0.0053385 | 0.1003 | 0.10328 | 2.6784 | 0.011901 | -0.041199 | -0.045776 | 0.009155 | 0.059509 | 0.07782 | 0.022888 | -0.09613 | -9.2514 | 9.343 | -1.5198 | 71.6675 | 71.7636 | -48.8708 | -48.999 | 48.5184 | 48.3994 | -72.2031 | 48.4497 | 48.555 | 0.15564 | -72.3221 | -0.37537 | -0.50354 | -0.6134 | 39.2441 | 46.9757 | 47.4792 | -0.51727 | 48.5733 | 48.4543 | 48.5046 | -72.377 | 120.163 | 120.2591 | 57.8384 | -121.2799
2796.5156 | 121.2112 | -110.1791 | 10.8124 | -0.012589 | 0.0132 | 0.018617 | 0.0014612 | 0.030159 | -0.0012133 | -0.046745 | -0.013123 | -0.010252 | 0.094101 | 0.09709 | 2.4338 | 0.016173 | 0.073242 | -0.041199 | -0.009155 | 0.16022 | 0.045776 | -0.004578 | -0.10071 | -66.8747 | -46.669 | -110.1608 | 10.6888 | 10.762 | -110.0784 | -110.2798 | 110.1746 | 110.0784 | -10.7666 | 110.1379 | 110.3394 | 0.26093 | -10.7391 | 0.10071 | -0.10071 | -0.1236 | 43.3044 | 0.01831 | 0.11902 | -0.050354 | 110.2249 | 110.2524 | 110.17 | -10.9131 | 120.8679 | 120.9412 | 63.5101 | -121.0922
2798.25 | 121.1655 | -91.7084 | 29.3243 | -0.0049592 | 0.012345 | 0.019899 | 0.003811 | 0.030586 | 0.0015637 | -0.046959 | -0.013123 | -0.0049111 | 0.098587 | 0.098371 | 2.572 | 0.014464 | -0.018311 | -0.15106 | -0.12817 | 0.064087 | 0.10071 | -0.013733 | -0.13275 | -49.3835 | -29.7409 | -91.3376 | 29.3015 | 29.3472 | -91.4886 | -91.7358 | 91.6946 | 91.5756 | -29.2236 | 91.5573 | 91.7725 | 0.19684 | -29.3427 | 0.21973 | -0.027466 | -0.022888 | 42.3248 | 0.37079 | 0.39825 | 0.022888 | 91.8091 | 91.6901 | 91.5802 | -29.4571 | 121.0098 | 121.0556 | 61.9675 | -121.0602
2800.0312 | 121.1517 | -89.7217 | 31.3293 | 0.0026703 | 0.013627 | 0.019258 | 0.0016748 | 0.031655 | 0.0017773 | -0.045677 | 0.0021363 | -0.0076883 | 0.098373 | 0.096876 | 2.6066 | 0.01596 | -0.027466 | -0.11902 | -0.10986 | 0.073242 | 0.082397 | -0.013733 | -0.11444 | -48.0377 | -27.9282 | -89.4104 | 31.2424 | 31.2607 | -89.5248 | -89.7125 | 89.7079 | 89.6072 | -31.2469 | 89.6027 | 89.7949 | 0.18768 | -31.3568 | 0.19684 | 0.009156 | -0.086975 | 41.684 | 0.31128 | 0.30212 | -0.068665 | 89.8041 | 89.6942 | 89.6118 | -31.4438 | 120.9641 | 120.9824 | 61.7935 | -121.0419
2801.75 | 121.106 | -85.9085 | 35.1013 | -0.012589 | 0.013413 | 0.017976 | 0.0044518 | 0.032082 | -0.00035893 | -0.047813 | -0.020752 | -0.0055521 | 0.098587 | 0.096449 | 2.6094 | 0.012542 | 0.054932 | -0.004578 | 0.032043 | 0.13733 | 0.059509 | 0.032043 | -0.082397 | -43.1396 | -24.2752 | -85.611 | 35.0052 | 35.0784 | -85.6888 | -85.9085 | 85.9406 | 85.8261 | -35.0418 | 85.9039 | 86.0458 | 0.21973 | -35.0464 | 0.21973 | 0 | -0.09613 | 42.7689 | 0.29755 | 0.29755 | -0.022888 | 85.968 | 85.9634 | 85.9406 | -35.1837 | 120.9137 | 120.9869 | 61.6333 | -121.0098
2803.5156 | 121.138 | -98.6938 | 22.2336 | -0.0049592 | 0.019822 | 0.015413 | 0.0035974 | 0.032723 | 0.0045545 | -0.045891 | -0.013123 | -0.0025613 | 0.097092 | 0.10136 | 2.6132 | 0.013824 | 0.027466 | -0.11444 | -0.082397 | 0.11444 | 0.073242 | -0.032043 | -0.12817 | -50.9628 | -36.0443 | -98.6526 | 22.1146 | 22.1832 | -98.5977 | -98.8449 | 98.6618 | 98.5657 | -22.1603 | 98.5794 | 98.8083 | 0.24262 | -22.2061 | 0.096131 | -0.15106 | -0.11902 | 47.731 | 0.041199 | 0.19226 | -0.050354 | 98.7671 | 98.7213 | 98.6115 | -22.3618 | 120.8084 | 120.8771 | 62.6495 | -121.0785
2805.2344 | 121.1609 | -98.1216 | 22.8287 | 0.0026703 | 0.012345 | 0.021181 | -0.0011024 | 0.031868 | 0.0051953 | -0.044822 | -0.013123 | -0.0040567 | 0.097733 | 0.099867 | 2.5863 | 0.015533 | 0.018311 | -0.1236 | -0.10071 | 0.09613 | 0.091553 | -0.004578 | -0.11444 | -53.5217 | -35.4355 | -97.6456 | 22.8653 | 22.8973 | -97.8973 | -98.1354 | 98.1171 | 98.0072 | -22.7371 | 97.998 | 98.2178 | 0.21057 | -22.8104 | 0.2243 | -0.013733 | 0.036621 | 44.5999 | 0.47607 | 0.48981 | 0.068665 | 98.2132 | 98.14 | 98.0209 | -22.9431 | 120.9869 | 121.019 | 62.6862 | -120.964
2807.0156 | 121.2433 | -96.0114 | 24.9252 | -0.012589 | 0.0089273 | 0.020326 | -0.00046138 | 0.032295 | -0.0061267 | -0.048454 | 0.0021363 | -0.0091837 | 0.094742 | 0.10072 | 2.5897 | 0.017669 | 0.004578 | -0.068665 | -0.018311 | 0.10986 | 0.054932 | 0.013733 | -0.09613 | -48.9716 | -33.3115 | -96.3684 | 24.8978 | 24.9344 | -95.8191 | -96.0846 | 96.0251 | 95.9152 | -24.8703 | 95.9427 | 96.1212 | 0.20599 | -24.9207 | 0.19226 | -0.073242 | -0.027466 | 47.0398 | -0.35706 | -0.28381 | 0.009155 | 96.0663 | 96.0159 | 95.993 | -25.0214 | 120.9091 | 120.9457 | 62.6999 | -121.0098
2808.7969 | 121.2524 | -99.9252 | 20.9427 | 0.0026703 | 0.01085 | 0.01819 | -0.00088858 | 0.034432 | -0.00099973 | -0.045463 | -0.0054932 | -0.0089701 | 0.091537 | 0.10115 | 2.6198 | 0.015746 | 0.10071 | -0.009155 | 0.018311 | 0.17395 | 0.036621 | 0.022888 | -0.10071 | -49.379 | -36.8042 | -99.4492 | 20.9061 | 20.9518 | -99.7467 | -99.9847 | 99.9481 | 99.8245 | -20.9061 | 99.9161 | 100.0992 | 0.27466 | -20.842 | 0.17853 | -0.059509 | -0.036621 | 50.5463 | 0.47607 | 0.53558 | 0.009155 | 99.9619 | 100.0259 | 99.9435 | -21.0434 | 120.8313 | 120.8771 | 63.121 | -120.9274
2810.5625 | 121.1609 | -98.4558 | 22.5174 | -0.0049592 | 0.017045 | 0.016267 | 0.0025292 | 0.032936 | 0.0045545 | -0.045677 | -0.0054932 | -0.0036295 | 0.096878 | 0.10307 | 2.6305 | 0.012542 | 0.032043 | -0.11444 | -0.082397 | 0.086975 | 0.091553 | 0.018311 | -0.11444 | -47.1176 | -35.9482 | -98.4009 | 22.4167 | 22.3572 | -98.4055 | -98.4695 | 98.4741 | 98.3414 | -22.4258 | 98.3414 | 98.5428 | 0.20142 | -22.4854 | 0.050354 | -0.013732 | -0.10071 | 51.3382 | 0.054932 | 0.068664 | -0.16022 | 98.5474 | 98.4879 | 98.3734 | -22.6318 | 120.8725 | 120.813 | 62.5076 | -120.9869
2812.3438 | 121.2387 | -100.296 | 20.5627 | -0.0049592 | 0.012345 | 0.019472 | 0.00060662 | 0.032723 | 0.0019909 | -0.046104 | 0.0021363 | -0.0044839 | 0.09581 | 0.10628 | 2.6087 | 0.014892 | 0.004578 | -0.10529 | -0.086975 | 0.07782 | 0.10986 | -0.013733 | -0.1236 | -45.6848 | -37.1063 | -99.8428 | 20.5353 | 20.5719 | -100.1724 | -100.4059 | 100.2823 | 100.1724 | -20.4529 | 100.1907 | 100.3738 | 0.20142 | -20.5582 | 0.1236 | -0.10986 | -0.027466 | 54.6112 | 0.45319 | 0.56305 | 0.009155 | 100.4059 | 100.3006 | 100.209 | -20.6863 | 120.8313 | 120.8679 | 63.1897 | -120.9686
2814.0625 | 121.1288 | -100.8545 | 20.0729 | 0.0026703 | 0.012986 | 0.017763 | -0.00046138 | 0.032936 | 0.0045545 | -0.046318 | -0.0054932 | -0.0055521 | 0.096237 | 0.10606 | 2.6357 | 0.016173 | -0.027466 | -0.17853 | -0.11444 | 0.068665 | 0.082397 | -0.022888 | -0.11902 | -44.9615 | -37.6282 | -100.4974 | 19.9493 | 20.018 | -100.7263 | -100.9827 | 100.8316 | 100.7355 | -19.9905 | 100.676 | 100.9232 | 0.18768 | -20.1004 | 0.12817 | -0.12817 | -0.1236 | 55.8929 | 0.35705 | 0.48523 | -0.054932 | 100.9369 | 100.827 | 100.7401 | -20.192 | 120.8038 | 120.8725 | 63.2263 | -121.0556
2815.8438 | 121.1563 | -86.6501 | 34.2773 | -0.020218 | 0.010423 | 0.019258 | 0.0042382 | 0.034859 | -0.0052721 | -0.047172 | -0.013123 | -0.0093973 | 0.096237 | 0.10051 | 2.5677 | 0.014892 | 0.10071 | 0.07782 | 0.086975 | 0.16479 | 0.022888 | 0.050354 | -0.064087 | -34.2957 | -24.4308 | -86.0367 | 34.227 | 34.2178 | -86.4807 | -86.7371 | 86.7004 | 86.586 | -34.2545 | 86.7279 | 86.8149 | 0.22888 | -34.1766 | 0.16937 | -0.086976 | -0.050354 | 52.3544 | 0.6134 | 0.70038 | -0.05951 | 86.673 | 86.7508 | 86.7371 | -34.3414 | 120.8771 | 120.8679 | 62.2192 | -121.0144
2817.625 | 121.1334 | -93.3426 | 27.5757 | -0.0049592 | 0.014054 | 0.018404 | -0.0021704 | 0.031227 | 0.0041273 | -0.045677 | 0.0021363 | -0.0042703 | 0.094101 | 0.10478 | 2.6613 | 0.014464 | -0.018311 | -0.14648 | -0.10071 | 0.07782 | 0.068665 | 0.018311 | -0.10529 | -37.8662 | -30.6702 | -91.7679 | 27.5391 | 27.5848 | -93.1595 | -93.4204 | 93.3609 | 93.2373 | -27.507 | 93.1961 | 93.4204 | 0.18311 | -27.594 | 0.1831 | -0.07782 | -0.036622 | 55.4764 | 1.5747 | 1.6525 | 0.009155 | 93.4113 | 93.3243 | 93.2419 | -27.681 | 120.8817 | 120.9274 | 62.6724 | -120.9961
2819.3281 | 121.1014 | -90.4266 | 30.5374 | -0.012589 | 0.014054 | 0.019685 | 0.001034 | 0.032509 | 0.0047681 | -0.045677 | -0.020752 | -0.0059793 | 0.094315 | 0.10307 | 2.6463 | 0.015105 | 0.036621 | -0.041199 | -0.018311 | 0.11902 | 0.059509 | 0.018311 | -0.09613 | -35.6918 | -27.8366 | -89.9139 | 30.4596 | 30.4688 | -90.2252 | -90.4633 | 90.4449 | 90.3305 | -30.4779 | 90.3854 | 90.5457 | 0.21515 | -30.5008 | 0.20142 | -0.036621 | -0.07782 | 54.7348 | 0.5127 | 0.54932 | -0.068665 | 90.4861 | 90.4633 | 90.4083 | -30.6335 | 120.8862 | 120.8954 | 62.59 | -121.0007
2821.1094 | 121.2112 | -88.8748 | 32.0114 | -0.0049592 | 0.0093545 | 0.021181 | 0.002102 | 0.031868 | -0.0063403 | -0.0476 | -0.020752 | -0.010679 | 0.091537 | 0.10414 | 2.6209 | 0.017882 | 0 | -0.041199 | 0 | 0.10986 | 0.036621 | 0.032043 | -0.064087 | -33.4946 | -26.3855 | -88.2202 | 31.8649 | 31.9244 | -88.7466 | -88.9572 | 88.9069 | 88.8107 | -31.9748 | 88.8336 | 88.9847 | 0.17395 | -32.0114 | 0.12817 | -0.082397 | -0.14649 | 55.3802 | 0.6546 | 0.737 | -0.086976 | 88.9114 | 88.8748 | 88.8748 | -32.0755 | 120.7397 | 120.7993 | 62.4893 | -120.9686
2822.9062 | 121.2387 | -101.1566 | 19.6747 | -0.0049592 | 0.0132 | 0.019472 | 0.0012476 | 0.032295 | -0.0059131 | -0.048881 | -0.0054932 | -0.0089701 | 0.089615 | 0.10798 | 2.6444 | 0.014892 | 0.022888 | -0.054932 | 0.004578 | 0.11902 | 0.059509 | 0.036621 | -0.082397 | -38.7451 | -37.3718 | -100.5112 | 19.5602 | 19.6289 | -101.0696 | -101.3123 | 101.1932 | 101.0742 | -19.6152 | 101.1017 | 101.2756 | 0.20142 | -19.6518 | 0.086975 | -0.15564 | -0.11444 | 62.4115 | 0.64545 | 0.80109 | -0.045777 | 101.2161 | 101.1795 | 101.1612 | -19.7571 | 120.7169 | 120.7855 | 63.7848 | -120.9869
2824.6719 | 121.106 | -103.2028 | 17.6697 | -0.020218 | 0.010209 | 0.019045 | 0.0016748 | 0.032295 | -0.0018543 | -0.048027 | -0.020752 | -0.0083291 | 0.088974 | 0.10777 | 2.6553 | 0.014251 | 0.091553 | 0.018311 | 0.054932 | 0.17395 | 0.059509 | 0.041199 | -0.073242 | -37.5137 | -39.0015 | -102.2736 | 17.5461 | 17.6193 | -103.0334 | -103.2669 | 103.244 | 103.1296 | -17.6102 | 103.2211 | 103.3768 | 0.24719 | -17.5781 | 0.16937 | -0.064087 | -0.1236 | 65.6891 | 0.92926 | 0.99335 | -0.050354 | 103.2623 | 103.2944 | 103.2578 | -17.7429 | 120.7489 | 120.8221 | 64.2014 | -120.9366
2826.3906 | 121.138 | -98.1995 | 22.6959 | 0.0026703 | 0.013841 | 0.018831 | 0.0025292 | 0.034004 | 0.0043409 | -0.049095 | -0.0054932 | -0.0081155 | 0.092392 | 0.10969 | 2.6288 | 0.011901 | -0.004578 | -0.11444 | -0.082397 | 0.068665 | 0.082397 | -0.009155 | -0.12817 | -34.8999 | -34.4742 | -97.6135 | 22.6959 | 22.7234 | -98.0804 | -98.2727 | 98.1903 | 98.0713 | -22.6135 | 98.085 | 98.2681 | 0.19684 | -22.7005 | 0.11902 | -0.073242 | 0 | 63.2996 | 0.58594 | 0.65918 | 0.027466 | 98.2819 | 98.1949 | 98.1171 | -22.8241 | 120.8954 | 120.9229 | 63.7253 | -120.9686
2828.1719 | 121.1609 | -102.7405 | 18.1 | -0.020218 | 0.0080727 | 0.020326 | 0.0029566 | 0.032509 | -0.00099973 | -0.047386 | -0.013123 | -0.0096109 | 0.090042 | 0.10948 | 2.5137 | 0.014892 | 0.032043 | -0.045776 | 0.009155 | 0.11902 | 0.068665 | 0.022888 | -0.064087 | -36.3235 | -38.6444 | -101.6876 | 18.0313 | 18.0817 | -102.5482 | -102.7954 | 102.7634 | 102.6764 | -18.0313 | 102.6947 | 102.8595 | 0.18311 | -18.0679 | 0.19226 | -0.054931 | -0.068665 | 66.4169 | 1.0529 | 1.1078 | -0.018311 | 102.8091 | 102.7725 | 102.7496 | -18.1641 | 120.7718 | 120.8221 | 64.0961 | -120.8954
2829.9531 | 121.225 | -101.1154 | 19.6701 | -0.0049592 | 0.014695 | 0.020326 | 0.001034 | 0.032509 | -0.0033495 | -0.046959 | -0.0054932 | -0.0089701 | 0.090042 | 0.10884 | 2.5259 | 0.015319 | 0.018311 | -0.045776 | 0.004578 | 0.12817 | 0.091553 | 0.032043 | -0.073242 | -33.6044 | -37.1292 | -102.7679 | 19.5007 | 19.5923 | -100.9827 | -101.2711 | 101.1475 | 101.0422 | -19.5786 | 101.0696 | 101.2436 | 0.20142 | -19.6518 | 0.13275 | -0.15564 | -0.16937 | 67.511 | -1.6525 | -1.4969 | -0.07782 | 101.207 | 101.1337 | 101.12 | -19.7433 | 120.6161 | 120.7077 | 63.9862 | -120.9412
2831.6719 | 121.1517 | -100.3601 | 20.3979 | -0.0049592 | 0.011064 | 0.019258 | -0.00088858 | 0.034004 | 0.0028455 | -0.046318 | -0.0054932 | -0.0076883 | 0.087479 | 0.11268 | 2.5194 | 0.014037 | 0.11902 | 0.004578 | 0.054932 | 0.16937 | 0.032043 | 0.041199 | -0.064087 | -32.5928 | -36.4197 | -99.202 | 20.2377 | 20.2927 | -100.2731 | -100.4929 | 100.4013 | 100.296 | -20.3659 | 100.3647 | 100.5295 | 0.23346 | -20.2789 | 0.086975 | -0.13275 | -0.16022 | 67.7673 | 1.1581 | 1.2909 | -0.10529 | 100.3922 | 100.4791 | 100.415 | -20.462 | 120.5978 | 120.6528 | 63.9404 | -120.8908
2833.4375 | 121.1609 | -100.3098 | 20.4758 | -0.012589 | 0.0085001 | 0.02054 | 0.0014612 | 0.032509 | -0.0018543 | -0.048454 | -0.0054932 | -0.0074747 | 0.088974 | 0.10905 | 2.6062 | 0.014892 | 0.041199 | -0.036621 | 0.013733 | 0.12817 | 0.07782 | 0.036621 | -0.07782 | -32.3776 | -36.3007 | -99.1104 | 20.3934 | 20.4163 | -100.1907 | -100.4105 | 100.3464 | 100.2319 | -20.3979 | 100.2731 | 100.4379 | 0.20599 | -20.4346 | 0.11902 | -0.10071 | -0.082397 | 67.9321 | 1.1993 | 1.3 | -0.059509 | 100.3876 | 100.351 | 100.3235 | -20.5536 | 120.7031 | 120.726 | 64.0091 | -120.8862
2835.1562 | 121.1472 | -98.5062 | 22.2977 | -0.012589 | 0.011918 | 0.019258 | 0.001034 | 0.035286 | -0.0029223 | -0.047813 | -0.013123 | -0.0085427 | 0.089615 | 0.11226 | 2.5835 | 0.012969 | 0.068665 | -0.027466 | 0.032043 | 0.12817 | 0.073242 | 0.032043 | -0.064087 | -30.4596 | -34.552 | -97.348 | 22.229 | 22.261 | -98.3276 | -98.5794 | 98.5382 | 98.4421 | -22.2244 | 98.4787 | 98.6343 | 0.19226 | -22.229 | 0.17853 | -0.073242 | -0.068664 | 68.0466 | 1.1581 | 1.2314 | -0.036621 | 98.5794 | 98.5748 | 98.5382 | -22.3618 | 120.7352 | 120.7672 | 63.9542 | -120.8771
2836.9219 | 120.9595 | -29.4754 | 91.42 | -0.012589 | 0.011491 | 0.017976 | 0.00082022 | 0.031441 | -0.00099973 | -0.049309 | -0.020752 | -0.0064065 | 0.105 | 0.087477 | 2.5786 | 0.0097648 | 0.018311 | 0.018311 | 0.09613 | 0.050354 | 0.009155 | 0.059509 | -0.059509 | 2.037 | 27.1774 | -28.6148 | 90.9851 | 91.095 | -29.5258 | -29.6219 | 29.5349 | 29.4159 | -91.4108 | 29.4937 | 29.5258 | 0.10986 | -91.4017 | -0.050354 | -0.14648 | -0.43488 | 31.5125 | 0.8606 | 1.0071 | -0.32501 | 29.4846 | 29.4937 | 29.5715 | -91.4795 | 120.4605 | 120.5704 | 56.6528 | -121.0419
2838.7188 | 121.1609 | -5.4291 | 115.654 | -0.012589 | 0.012559 | 0.019045 | 0.0033838 | 0.031655 | -0.00035893 | -0.048881 | -0.0054932 | -0.0055521 | 0.1114 | 0.079359 | 2.5575 | 0.0061332 | 0.022888 | 0.059509 | 0.14191 | 0.086975 | -0.009155 | 0.045776 | -0.064087 | 14.0076 | 49.0128 | -3.4515 | 115.448 | 115.5762 | -5.3192 | -5.3513 | 5.4749 | 5.365 | -115.6631 | 5.4886 | 5.5161 | 0.15106 | -115.6311 | 0.10986 | 0.07782 | -0.20599 | 19.4366 | 1.9775 | 1.8997 | -0.07782 | 5.4199 | 5.452 | 5.571 | -115.7181 | 120.8771 | 121.0052 | 54.4418 | -121.0052
2840.4219 | 121.1884 | -5.3513 | 115.7639 | -0.012589 | 0.0132 | 0.018617 | 0.00039302 | 0.031868 | 6.8274e-05 | -0.047386 | -0.020752 | -0.0068337 | 0.11162 | 0.079359 | 2.5801 | 0.0072012 | 0.068665 | 0.11902 | 0.18768 | 0.09613 | -0.009155 | 0.054932 | -0.07782 | 13.7878 | 49.2371 | -3.3142 | 115.6311 | 115.7547 | -5.1865 | -5.2277 | 5.4062 | 5.2734 | -115.773 | 5.4703 | 5.4474 | 0.17395 | -115.6952 | 0.1648 | 0.1236 | -0.13275 | 19.1391 | 2.037 | 1.9135 | -0.009155 | 5.3421 | 5.4199 | 5.5389 | -115.8417 | 120.9824 | 121.106 | 54.5883 | -120.9915
2842.2188 | 121.1563 | -5.1132 | 116.0934 | -0.012589 | 0.013841 | 0.016908 | 0.002102 | 0.033577 | 6.8274e-05 | -0.047172 | -0.013123 | -0.0040567 | 0.11119 | 0.077009 | 2.5897 | 0.0052786 | 0.036621 | 0.082397 | 0.15564 | 0.09613 | -0.032043 | 0.036621 | -0.064087 | 13.6917 | 49.4293 | -3.0579 | 115.9012 | 116.0477 | -4.9576 | -4.9942 | 5.1498 | 5.0491 | -116.1255 | 5.1956 | 5.2093 | 0.16022 | -116.0568 | 0.15564 | 0.11902 | -0.19226 | 18.8049 | 2.0554 | 1.9363 | -0.045777 | 5.0812 | 5.1498 | 5.2689 | -116.1575 | 121.0144 | 121.1609 | 54.5425 | -121.0876
2844 | 121.1609 | -5.0858 | 116.1255 | -0.0049592 | 0.014054 | 0.014345 | 0.00039302 | 0.029732 | 0.0060499 | -0.042686 | -0.013123 | -0.0034159 | 0.11397 | 0.080854 | 2.5124 | 0.0063468 | -0.050354 | -0.09613 | -0.018311 | -0.018311 | 0.013733 | 0.013733 | -0.11902 | 13.5361 | 49.2874 | -3.1815 | 115.9836 | 116.1255 | -4.9667 | -5.0217 | 5.0995 | 4.9667 | -116.1118 | 4.9896 | 5.0674 | 0.10071 | -116.1758 | 0.11902 | 0.064087 | -0.14191 | 18.6218 | 1.9043 | 1.8402 | 0 | 5.0995 | 5.0354 | 5.0674 | -116.2445 | 121.0693 | 121.2112 | 54.3732 | -121.1472
2845.7188 | 121.3348 | -5.1132 | 116.0339 | -0.012589 | 0.013413 | 0.017122 | 0.00039302 | 0.033364 | -0.0029223 | -0.045891 | -0.0054932 | -0.0096109 | 0.11183 | 0.081282 | 2.5526 | 0.0078422 | 0 | 0.073242 | 0.1236 | 0.09613 | -0.009155 | 0.032043 | -0.073242 | 17.9764 | 49.4431 | -3.2089 | 115.8966 | 116.0202 | -5.0262 | -5.0583 | 5.1453 | 5.04 | -116.0431 | 5.1865 | 5.2093 | 0.16937 | -116.0339 | 0.086975 | 0.054931 | -0.13733 | 23.0896 | 1.9043 | 1.8494 | -0.013733 | 5.1041 | 5.1132 | 5.2368 | -116.1072 | 121.0098 | 121.1334 | 54.5563 | -121.0922
2847.4844 | 121.2616 | -4.834 | 116.3727 | -0.012589 | 0.014482 | 0.017976 | -0.003025 | 0.032295 | 0.0043409 | -0.045036 | -0.013123 | -0.0021341 | 0.1114 | 0.08299 | 2.5714 | 0.0052786 | -0.059509 | -0.068665 | 0 | 0.018311 | 0.027466 | -0.004578 | -0.10071 | 19.8578 | 49.6353 | -3.0396 | 116.2766 | 116.3773 | -4.7516 | -4.7882 | 4.8294 | 4.7333 | -116.3452 | 4.7653 | 4.8523 | 0.11902 | -116.4322 | 0.082397 | 0.045776 | -0.096131 | 24.6918 | 1.7944 | 1.7487 | 0.004577 | 4.8615 | 4.7745 | 4.834 | -116.4734 | 121.1105 | 121.2112 | 54.4693 | -121.1609
2849.2031 | 121.2982 | -4.8569 | 116.3132 | -0.0049592 | 0.011277 | 0.018617 | -0.0021704 | 0.032295 | -0.0014269 | -0.045677 | -0.013123 | -0.0051247 | 0.10948 | 0.080641 | 2.5827 | 0.0078422 | 0.032043 | 0.10071 | 0.14191 | 0.064087 | -0.018311 | 0.032043 | -0.059509 | 19.4275 | 49.6902 | -2.948 | 116.185 | 116.2994 | -4.7516 | -4.7974 | 4.8889 | 4.7974 | -116.3315 | 4.9576 | 4.921 | 0.1236 | -116.2811 | 0.10529 | 0.05951 | -0.12817 | 24.2844 | 1.9089 | 1.8494 | -0.013733 | 4.8386 | 4.8889 | 4.9988 | -116.3727 | 121.0419 | 121.1563 | 54.5471 | -121.1105
2850.9844 | 121.2708 | -4.6051 | 116.6428 | 0.0026703 | 0.014268 | 0.017122 | 0.00082022 | 0.033364 | 0.0041273 | -0.045891 | -0.013123 | -0.0017069 | 0.10735 | 0.083845 | 2.6386 | 0.0057058 | -0.064087 | -0.036621 | 0.013733 | 0.041199 | 0.041199 | 0.004578 | -0.10986 | 19.0704 | 49.8917 | -2.7191 | 116.5329 | 116.6611 | -4.4861 | -4.5227 | 4.6097 | 4.4952 | -116.6016 | 4.5685 | 4.6463 | 0.15106 | -116.7068 | 0.11902 | 0.082398 | -0.10986 | 23.6755 | 1.886 | 1.8036 | 0.018311 | 4.6463 | 4.541 | 4.6188 | -116.7526 | 121.138 | 121.2662 | 54.4968 | -121.1655
2852.7812 | 121.3165 | -4.6875 | 116.5649 | 0.0026703 | 0.012986 | 0.017976 | -0.00024778 | 0.032082 | -0.0022815 | -0.044822 | -0.013123 | -0.0072611 | 0.11162 | 0.079786 | 2.5536 | 0.008483 | 0.013733 | 0.073242 | 0.13275 | 0.073242 | -0.036621 | 0.050354 | -0.054932 | 18.8461 | 49.8779 | -2.7374 | 116.3727 | 116.4871 | -4.5593 | -4.5914 | 4.7379 | 4.6326 | -116.6016 | 4.7607 | 4.7607 | 0.12817 | -116.5512 | 0.12817 | 0.09613 | -0.19226 | 23.5336 | 1.9501 | 1.8539 | -0.077819 | 4.6509 | 4.7012 | 4.8203 | -116.6199 | 121.0602 | 121.1746 | 54.5654 | -121.1563
2854.5625 | 121.3715 | -5.04 | 116.1896 | -0.0049592 | 0.015977 | 0.017336 | 0.0023156 | 0.032723 | 0.0011365 | -0.044822 | -0.013123 | -0.0061929 | 0.11247 | 0.081068 | 2.6017 | 0.0063468 | 0.018311 | 0.073242 | 0.13275 | 0.10071 | -0.027466 | 0.050354 | -0.068665 | 16.4246 | 49.3057 | -3.7949 | 115.8463 | 115.9195 | -5.1361 | -5.2231 | 5.0903 | 4.9713 | -116.217 | 5.1132 | 5.1407 | 0.16937 | -116.1713 | -0.09613 | -0.18311 | -0.34332 | 21.4645 | 1.2451 | 1.4282 | -0.27008 | 5.0125 | 5.0583 | 5.1727 | -116.2582 | 120.8862 | 120.9595 | 54.3457 | -121.4127
2856.3438 | 121.3028 | -4.7607 | 116.5283 | -0.012589 | 0.016191 | 0.015627 | 0.0027428 | 0.032295 | -0.00057253 | -0.0476 | -0.013123 | -0.0051247 | 0.11119 | 0.081709 | 2.5895 | 0.0072012 | 0.022888 | 0.091553 | 0.14648 | 0.10071 | -0.013733 | 0.022888 | -0.064087 | 18.5989 | 49.8322 | -2.7374 | 116.3406 | 116.4597 | -4.6417 | -4.7058 | 4.7836 | 4.6967 | -116.5421 | 4.8523 | 4.8614 | 0.1648 | -116.5054 | 0.11902 | 0.054931 | -0.18768 | 23.3597 | 2.0233 | 1.9684 | -0.068664 | 4.747 | 4.7836 | 4.9072 | -116.5924 | 121.1014 | 121.2204 | 54.5929 | -121.2341
2858.0469 | 121.3074 | -4.7562 | 116.5466 | -0.0049592 | 0.015763 | 0.01584 | -0.0011024 | 0.032936 | 0.0039135 | -0.044395 | -0.013123 | -0.00042512 | 0.11205 | 0.084059 | 2.61 | 0.0063468 | -0.004578 | -0.009155 | 0.050354 | 0.054932 | 0.022888 | 0.022888 | -0.10986 | 21.4096 | 49.823 | -2.8198 | 116.4139 | 116.5329 | -4.6371 | -4.6829 | 4.7791 | 4.6463 | -116.5237 | 4.747 | 4.8111 | 0.16479 | -116.5512 | 0.11902 | 0.073243 | -0.13275 | 26.1658 | 1.9363 | 1.8631 | -0.013733 | 4.7791 | 4.7516 | 4.8065 | -116.6565 | 121.17 | 121.2891 | 54.5792 | -121.2296
2859.8281 | 121.376 | -4.6509 | 116.5878 | -0.020218 | 0.014054 | 0.018404 | 0.00017942 | 0.031655 | -0.00078613 | -0.046318 | -0.013123 | -0.0053385 | 0.11055 | 0.084486 | 2.6028 | 0.0074148 | 0.018311 | 0.064087 | 0.15106 | 0.10071 | -0.022888 | 0.059509 | -0.054932 | 20.6635 | 49.9558 | -2.655 | 116.4368 | 116.5924 | -4.5456 | -4.5868 | 4.7104 | 4.5959 | -116.6107 | 4.715 | 4.7516 | 0.15564 | -116.5695 | 0.10529 | 0.064087 | -0.15106 | 25.3143 | 1.9958 | 1.9318 | 0.004577 | 4.628 | 4.6692 | 4.8019 | -116.6428 | 121.0876 | 121.2433 | 54.6066 | -121.1746
2861.6094 | 121.3989 | -4.866 | 116.3864 | -0.012589 | 0.014909 | 0.015199 | 0.00017942 | 0.033364 | 0.0028455 | -0.045677 | -0.0054932 | -0.00063872 | 0.11226 | 0.085768 | 2.5778 | 0.0080558 | -0.041199 | -0.082397 | -0.013733 | 0 | 0.018311 | 0 | -0.10071 | 19.7617 | 49.6857 | -2.9709 | 116.272 | 116.4047 | -4.7836 | -4.8248 | 4.866 | 4.7653 | -116.3681 | 4.7836 | 4.866 | 0.10071 | -116.4276 | 0.082398 | 0.041199 | -0.11444 | 24.6277 | 1.8951 | 1.8539 | 0.01831 | 4.8843 | 4.8248 | 4.8523 | -116.4871 | 121.138 | 121.2708 | 54.5517 | -121.2112
2863.3906 | 121.4218 | -5.0812 | 116.1438 | -0.012589 | 0.014054 | 0.01584 | -0.00024778 | 0.031655 | 6.8274e-05 | -0.046959 | 0.0021363 | -0.0057657 | 0.11183 | 0.084486 | 2.5602 | 0.008483 | 0.036621 | 0.054932 | 0.13275 | 0.11444 | -0.032043 | 0.050354 | -0.07782 | 18.9011 | 49.617 | -3.0396 | 116.0248 | 116.1667 | -4.9759 | -5.0262 | 5.1315 | 5.0034 | -116.1758 | 5.1361 | 5.1956 | 0.19226 | -116.1072 | 0.10529 | 0.054932 | -0.11902 | 23.9822 | 2.0416 | 1.9867 | 0.022888 | 5.0491 | 5.1178 | 5.2139 | -116.2216 | 121.106 | 121.2479 | 54.6982 | -121.17
2865.1094 | 121.3623 | -5.2597 | 116.066 | -0.0049592 | 0.017472 | 0.016054 | 0.00082022 | 0.033577 | 0.0011365 | -0.045036 | -0.013123 | -0.0027749 | 0.11333 | 0.082563 | 2.5577 | 0.0076286 | -0.027466 | -0.027466 | 0.022888 | 0.050354 | 0.018311 | 0.009155 | -0.10071 | 17.9764 | 49.4843 | -3.2501 | 115.9241 | 116.0202 | -5.1498 | -5.2048 | 5.2689 | 5.159 | -116.0477 | 5.2322 | 5.3101 | 0.15106 | -116.0934 | 0.10986 | 0.054932 | -0.14191 | 23.2361 | 2.0096 | 1.9547 | -0.045776 | 5.278 | 5.2322 | 5.2826 | -116.1667 | 121.1838 | 121.2799 | 54.744 | -121.2708
2866.8906 | 121.3943 | -5.1178 | 116.1987 | 0.0026703 | 0.016191 | 0.015413 | -0.00046138 | 0.029946 | 0.0024183 | -0.044822 | 0.0021363 | -0.0012795 | 0.11482 | 0.085981 | 2.5758 | 0.0076286 | -0.054932 | -0.082397 | -0.022888 | 0.009155 | 0.027466 | 0.004578 | -0.09613 | 18.0542 | 49.5071 | -3.1723 | 116.098 | 116.2079 | -5.0217 | -5.0766 | 5.1224 | 5.0217 | -116.1713 | 5.0354 | 5.127 | 0.10528 | -116.2537 | 0.096131 | 0.041199 | -0.10071 | 23.172 | 1.9455 | 1.9043 | 0.009156 | 5.1453 | 5.0629 | 5.0949 | -116.2949 | 121.2158 | 121.3257 | 54.6249 | -121.2753
2868.6875 | 121.3715 | -4.9576 | 116.4047 | -0.0049592 | 0.015336 | 0.014986 | 0.00039302 | 0.034218 | 0.0013501 | -0.0429 | 0.0021363 | -0.0017069 | 0.11311 | 0.087904 | 2.5393 | 0.0095512 | -0.068665 | -0.054932 | 0.004578 | 0.032043 | 0.013733 | 0.018311 | -0.10529 | 21.0983 | 49.7635 | -3.0029 | 116.272 | 116.3773 | -4.8569 | -4.8981 | 4.9759 | 4.8523 | -116.391 | 4.9026 | 4.9896 | 0.13733 | -116.4734 | 0.10071 | 0.05951 | -0.13275 | 26.0559 | 1.9547 | 1.8951 | -0.027466 | 4.9713 | 4.8889 | 4.9622 | -116.51 | 121.2296 | 121.3348 | 54.7211 | -121.3028
2870.4531 | 121.4264 | -5.3192 | 115.9836 | -0.012589 | 0.0132 | 0.018831 | 0.0014612 | 0.032723 | -0.0052721 | -0.044182 | -0.020752 | -0.0051247 | 0.10927 | 0.086195 | 2.5506 | 0.008483 | 0.022888 | 0.10071 | 0.13733 | 0.09613 | -0.004578 | 0.027466 | -0.086975 | 20.2972 | 49.617 | -3.3142 | 115.8234 | 115.9378 | -5.2277 | -5.2368 | 5.3467 | 5.2322 | -115.9882 | 5.4199 | 5.4153 | 0.1831 | -115.9607 | 0.091553 | 0.082398 | -0.16022 | 25.6165 | 2.005 | 1.9226 | -0.045777 | 5.3146 | 5.3421 | 5.4565 | -116.0706 | 121.1426 | 121.257 | 54.9362 | -121.2204
2872.2344 | 121.4996 | -5.9784 | 115.2924 | 0.0026703 | 0.010209 | 0.01819 | 0.00082022 | 0.032509 | -0.0035633 | -0.048454 | -0.013123 | -0.0046975 | 0.11012 | 0.085768 | 2.5963 | 0.0095512 | -0.032043 | 0.013733 | 0.091553 | 0.073242 | -0.013733 | 0.045776 | -0.07782 | 18.8141 | 49.0402 | -4.0466 | 115.1825 | 115.2969 | -5.864 | -5.928 | 6.0242 | 5.9006 | -115.3061 | 5.9921 | 6.0516 | 0.15106 | -115.3244 | 0.11444 | 0.050354 | -0.10986 | 24.7925 | 1.9318 | 1.8814 | 0.004578 | 5.9647 | 5.9464 | 6.0699 | -115.3702 | 121.1609 | 121.2753 | 55.0186 | -121.2204
2873.9531 | 121.431 | -6.221 | 115.1001 | -0.012589 | 0.012345 | 0.01819 | 0.0012476 | 0.031441 | -0.0012133 | -0.045677 | -0.013123 | -0.0066201 | 0.1097 | 0.084486 | 2.5741 | 0.0074148 | 0.032043 | 0.059509 | 0.13733 | 0.082397 | -0.013733 | 0.041199 | -0.059509 | 18.1137 | 48.8022 | -4.3213 | 114.9353 | 115.0452 | -6.1249 | -6.1661 | 6.2622 | 6.1615 | -115.1138 | 6.2805 | 6.3034 | 0.14191 | -115.0681 | 0.09613 | 0.054931 | -0.16479 | 24.3347 | 1.8997 | 1.8448 | -0.054932 | 6.2073 | 6.2531 | 6.3583 | -115.1596 | 121.1563 | 121.2662 | 55.0232 | -121.2662
2875.7344 | 121.3623 | -6.2942 | 115.0772 | 0.0026703 | 0.014482 | 0.014558 | -0.0015296 | 0.034004 | 0.0056225 | -0.044182 | -0.013123 | 0.0010703 | 0.1114 | 0.08769 | 2.5976 | 0.0069876 | 0.018311 | -0.004578 | 0.041199 | 0.050354 | -0.018311 | 0.009155 | -0.091553 | 17.6559 | 48.7244 | -4.4312 | 114.9261 | 115.0543 | -6.189 | -6.2256 | 6.3034 | 6.2027 | -115.0955 | 6.2897 | 6.3446 | 0.14191 | -115.0589 | 0.10529 | 0.068664 | -0.15106 | 23.9502 | 1.8631 | 1.7944 | -0.022888 | 6.2759 | 6.3126 | 6.3354 | -115.1688 | 121.2204 | 121.3486 | 55.0186 | -121.3028
2877.5 | 121.5179 | -6.4133 | 114.8483 | -0.020218 | 0.011277 | 0.019258 | 0.0033838 | 0.030586 | -0.0056995 | -0.046745 | -0.013123 | -0.0068337 | 0.11119 | 0.084913 | 2.5799 | 0.0093374 | -0.027466 | 0.018311 | 0.091553 | 0.068665 | 0 | 0.018311 | -0.064087 | 16.4291 | 48.642 | -4.4815 | 114.711 | 114.8392 | -6.3309 | -6.3583 | 6.4316 | 6.3492 | -114.8483 | 6.4316 | 6.4819 | 0.13275 | -114.8758 | 0.082397 | 0.054932 | -0.13733 | 22.8424 | 1.9318 | 1.8768 | -0.009156 | 6.4133 | 6.3858 | 6.5048 | -114.9124 | 121.1243 | 121.2524 | 55.0552 | -121.2067
2879.2188 | 121.3898 | -6.7612 | 114.6103 | -0.012589 | 0.012986 | 0.020326 | 0.0027428 | 0.035073 | -0.0016405 | -0.046318 | -0.020752 | -0.0064065 | 0.11226 | 0.087904 | 2.5812 | 0.0078422 | 0.027466 | 0.068665 | 0.13733 | 0.10071 | -0.018311 | 0.036621 | -0.068665 | 15.5411 | 48.3902 | -4.7424 | 114.4501 | 114.5554 | -6.6055 | -6.6742 | 6.7978 | 6.6925 | -114.6286 | 6.8298 | 6.8619 | 0.16937 | -114.5828 | 0.15564 | 0.086975 | -0.16022 | 22.3022 | 2.0187 | 1.9318 | -0.054932 | 6.7429 | 6.7886 | 6.8985 | -114.679 | 121.2112 | 121.3165 | 55.1514 | -121.2845
2881.0156 | 121.4035 | -7.4432 | 113.9053 | -0.012589 | 0.014268 | 0.014772 | -0.001316 | 0.032936 | 0.0045545 | -0.047386 | -0.028381 | -0.00021152 | 0.11162 | 0.089399 | 2.5869 | 0.0082694 | -0.059509 | -0.091553 | -0.018311 | 0.027466 | 0.045776 | 0.013733 | -0.10529 | 14.3051 | 47.6212 | -5.6168 | 113.8229 | 113.9236 | -7.3196 | -7.3792 | 7.457 | 7.338 | -113.8596 | 7.3517 | 7.4707 | 0.13275 | -113.9648 | 0.1236 | 0.064087 | -0.082397 | 21.7484 | 1.8265 | 1.7624 | 0.018311 | 7.489 | 7.3837 | 7.4249 | -114.0106 | 121.2662 | 121.3669 | 55.0644 | -121.2845
2882.7344 | 121.4218 | -7.489 | 113.8733 | -0.0049592 | 0.015763 | 0.018404 | 0.0014612 | 0.032723 | 0.00049567 | -0.045036 | -0.013123 | -0.0023477 | 0.11269 | 0.089186 | 2.6282 | 0.0091238 | -0.073242 | -0.068665 | -0.004578 | 0.009155 | 0.032043 | -0.009155 | -0.1236 | 11.8652 | 47.612 | -5.5756 | 113.7909 | 113.8916 | -7.3654 | -7.4203 | 7.4799 | 7.3654 | -113.8412 | 7.4203 | 7.4982 | 0.13275 | -113.9465 | 0.1236 | 0.068665 | -0.082397 | 19.3542 | 1.9135 | 1.8448 | 0.018311 | 7.5211 | 7.4158 | 7.4844 | -113.9969 | 121.2799 | 121.3806 | 55.101 | -121.2936
2884.5 | 121.4264 | -6.9122 | 114.4455 | 0.0026703 | 0.016404 | 0.016481 | 0.0031702 | 0.033577 | 0.0026319 | -0.046959 | -0.013123 | -0.0021341 | 0.11354 | 0.089826 | 2.5827 | 0.0078422 | -0.059509 | -0.059509 | -0.004578 | 0.027466 | 0.018311 | 0.013733 | -0.10529 | 13.1882 | 48.1705 | -5.0217 | 114.3311 | 114.4318 | -6.7841 | -6.8344 | 6.926 | 6.8069 | -114.4272 | 6.8527 | 6.9397 | 0.13275 | -114.505 | 0.12817 | 0.077819 | -0.11444 | 20.1004 | 1.8906 | 1.8127 | -0.013733 | 6.9305 | 6.8527 | 6.9077 | -114.5508 | 121.2433 | 121.344 | 55.0827 | -121.2799
2886.2344 | 121.4401 | -7.0038 | 114.3036 | -0.012589 | 0.012986 | 0.017122 | 0.00039302 | 0.034432 | 0.0017773 | -0.046531 | -0.0054932 | -0.0023477 | 0.11653 | 0.091749 | 2.5483 | 0.0089102 | -0.086975 | -0.086975 | -0.032043 | 0.009155 | 0.013733 | 0.004578 | -0.09613 | 13.3209 | 47.9965 | -5.0995 | 114.18 | 114.3173 | -6.9443 | -6.9809 | 7.0084 | 6.9077 | -114.2899 | 6.9168 | 7.0129 | 0.10528 | -114.3906 | 0.059509 | 0.022888 | -0.1236 | 20.3247 | 1.9043 | 1.8814 | 0.013733 | 7.0175 | 6.9168 | 6.9717 | -114.3997 | 121.1838 | 121.3211 | 55.0003 | -121.2845
2888 | 121.4035 | -6.752 | 114.7202 | 0.0026703 | 0.016618 | 0.014986 | 0.001034 | 0.034645 | 0.0045545 | -0.044182 | -0.0054932 | -0.0014933 | 0.12807 | 0.094313 | 2.5555 | 0.0099784 | -0.018311 | -0.027466 | 0.036621 | 0.054932 | 0.009155 | 0.004578 | -0.086975 | 11.0916 | 48.23 | -3.5385 | 114.4363 | 114.4913 | -6.7108 | -6.7612 | 6.7566 | 6.665 | -114.711 | 6.7245 | 6.8069 | 0.14191 | -114.7385 | 0.041199 | -0.009155 | -0.28381 | 17.8436 | 3.2135 | 3.2227 | -0.22888 | 6.7612 | 6.7337 | 6.7886 | -114.8071 | 121.1884 | 121.2433 | 54.982 | -121.4813
2889.7969 | 121.4767 | -43.9499 | 77.0966 | -0.012589 | 0.011277 | 0.019685 | -0.00024778 | 0.031655 | -0.0020679 | -0.0429 | -0.013123 | 0.0085471 | -0.01442 | -0.0020315 | 2.5543 | 0.030913 | 0.036621 | 0.091553 | 0.13275 | 0.11902 | 0.013733 | 0.07782 | -0.022888 | 0.041199 | 0.32044 | -0.004578 | 0.29755 | 0.32501 | 0.073242 | 0.032043 | 44.0277 | 43.927 | -77.0828 | 44.0414 | 44.0689 | 0.14191 | -77.0599 | 44.0231 | 43.9819 | -76.799 | 43.9911 | 43.9453 | -0.036621 | -76.7715 | 43.9636 | 43.9865 | 44.0826 | -77.1194 | 44.2474 | 44.2749 | 44.2703 | -77.0645
2891.5312 | 121.463 | -44.1238 | 77.0554 | -0.012589 | 0.0099953 | 0.019472 | 0.0023156 | 0.032509 | -0.0039905 | -0.048454 | -0.0054932 | 0.010042 | -0.014206 | -0.0016043 | 2.5615 | 0.029632 | 0.036621 | 0.086975 | 0.15106 | 0.12817 | 0.013733 | 0.068665 | -0.050354 | 0.018311 | 0.25177 | -0.018311 | 0.11902 | 0.13733 | 0.09613 | 0.027466 | 44.1925 | 44.0735 | -77.0416 | 44.2108 | 44.252 | 0.17853 | -77.0187 | 44.22 | 44.1513 | -76.9363 | 44.1422 | 44.1055 | -0.045777 | -76.918 | 44.1376 | 44.1605 | 44.2749 | -77.1057 | 44.2429 | 44.2612 | 44.3756 | -77.0279
2893.2969 | 121.4539 | -44.1788 | 77.092 | -0.012589 | 0.017686 | 0.018404 | 0.0053064 | 0.034218 | 0.00070927 | -0.046959 | -0.020752 | 0.0091879 | -0.012711 | -0.00053629 | 2.5432 | 0.029204 | -0.054932 | -0.036621 | 0.018311 | 0.041199 | 0.059509 | 0.027466 | -0.091553 | -0.07782 | 0.091553 | -0.10986 | 0.16022 | 0.16022 | 0.036621 | -0.009155 | 44.2062 | 44.0872 | -77.0325 | 44.1422 | 44.22 | 0.13275 | -77.1469 | 44.2154 | 44.1696 | -76.9318 | 44.101 | 44.0689 | -0.10071 | -76.9318 | 44.2383 | 44.1238 | 44.1971 | -77.1835 | 44.339 | 44.339 | 44.2703 | -77.1011
2895.0781 | 121.5546 | -44.1101 | 77.1011 | -0.020218 | 0.012132 | 0.018617 | 0.0042382 | 0.033577 | -0.0056995 | -0.047386 | -0.0054932 | 0.0079063 | -0.015915 | -0.00032249 | 2.5673 | 0.028991 | 0.059509 | 0.09613 | 0.15106 | 0.12817 | 0.009155 | 0.064087 | -0.041199 | 0.054932 | 0.23346 | 0.036621 | 0.09613 | 0.09613 | 0.09613 | 0.027466 | 44.1742 | 44.0689 | -77.092 | 44.2062 | 44.2383 | 0.16937 | -77.0416 | 44.2062 | 44.1376 | -77.005 | 44.165 | 44.1467 | 0.009155 | -77.005 | 44.1193 | 44.1696 | 44.2612 | -77.1423 | 44.2062 | 44.2062 | 44.3436 | -77.0737
2896.8594 | 121.463 | -43.9957 | 77.2797 | -0.012589 | 0.014054 | 0.016481 | 0.00060662 | 0.033791 | 0.0045545 | -0.044395 | -0.0054932 | 0.011751 | -0.013992 | 0.0022409 | 2.6224 | 0.026214 | -0.022888 | -0.091553 | -0.027466 | 0.036621 | 0.050354 | 0.036621 | -0.07782 | -0.068665 | 0.018311 | -0.15106 | 0.09613 | 0.13275 | 0.064087 | -0.004578 | 44.0323 | 43.9178 | -77.2293 | 43.9041 | 44.0323 | 0.11444 | -77.3026 | 44.0598 | 43.9911 | -77.1835 | 43.927 | 43.8446 | -0.14648 | -77.1469 | 44.046 | 43.9728 | 43.9682 | -77.3575 | 44.0918 | 44.1284 | 44.014 | -77.2842
2898.6406 | 121.4355 | -43.9178 | 77.3849 | -0.012589 | 0.013841 | 0.015627 | -0.0021704 | 0.031441 | 0.0032727 | -0.046318 | -0.013123 | 0.013247 | -0.01442 | -0.00010889 | 2.5884 | 0.028777 | 0.032043 | 0.009155 | 0.064087 | 0.07782 | 0.032043 | 0.032043 | -0.07782 | 0.004578 | 0.10986 | -0.091553 | 0.10529 | 0.12817 | 0.091553 | 0.013733 | 43.9499 | 43.84 | -77.3529 | 43.927 | 43.9957 | 0.15564 | -77.3529 | 44.0094 | 43.9316 | -77.2797 | 43.9224 | 43.8263 | -0.10529 | -77.2568 | 43.9499 | 43.9499 | 43.9819 | -77.4628 | 44.0231 | 44.046 | 44.0277 | -77.3712
2900.3594 | 121.5225 | -43.7393 | 77.5131 | -0.012589 | 0.0082865 | 0.017763 | 0.0018884 | 0.031441 | -0.0044177 | -0.04525 | 0.0021363 | 0.0072653 | -0.015488 | -0.0016043 | 2.6023 | 0.031554 | 0.004578 | 0.041199 | 0.082397 | 0.082397 | 0.009155 | 0.050354 | -0.059509 | -0.022888 | 0.11444 | -0.036621 | 0.032043 | 0.041199 | 0.10071 | 0.032043 | 43.7897 | 43.6798 | -77.504 | 43.7805 | 43.8217 | 0.14191 | -77.5085 | 43.84 | 43.7714 | -77.4811 | 43.7164 | 43.7027 | -0.068664 | -77.4719 | 43.7485 | 43.7439 | 43.8217 | -77.5726 | 43.7714 | 43.7805 | 43.8538 | -77.4811
2902.1406 | 121.4859 | -43.959 | 77.3209 | 0.0026703 | 0.014482 | 0.016908 | 0.0016748 | 0.032936 | 0.0045545 | -0.042686 | -0.020752 | 0.012606 | -0.015488 | 0.0018137 | 2.6318 | 0.028777 | -0.041199 | -0.091553 | -0.004578 | 0.045776 | 0.054932 | 0.032043 | -0.09613 | -0.068665 | -0.004578 | -0.14191 | 0.045776 | 0.059509 | 0.059509 | 0.018311 | 43.9911 | 43.8629 | -77.2659 | 43.8675 | 44.0048 | 0.14191 | -77.3621 | 44.0186 | 43.9774 | -77.2751 | 43.8904 | 43.8171 | -0.16022 | -77.2614 | 44.014 | 43.9178 | 43.9545 | -77.417 | 44.0048 | 44.0186 | 43.9545 | -77.3026
2903.9219 | 121.5134 | -43.8766 | 77.3804 | -0.012589 | 0.013627 | 0.018617 | 0.0031702 | 0.034004 | -0.0061267 | -0.046959 | -0.013123 | 0.0083335 | -0.013138 | -0.00074989 | 2.6203 | 0.028777 | 0.045776 | 0.10071 | 0.14191 | 0.12817 | 0.009155 | 0.036621 | -0.041199 | 0.041199 | 0.21057 | 0.013733 | 0.022888 | 0.054932 | 0.10071 | 0.036621 | 43.9133 | 43.8354 | -77.3712 | 43.9774 | 44.0048 | 0.16937 | -77.3346 | 43.9774 | 43.9133 | -77.3575 | 43.9178 | 43.8904 | -0.022888 | -77.3254 | 43.8858 | 43.9224 | 44.0186 | -77.4216 | 43.8995 | 43.9316 | 44.0872 | -77.3438
2905.6406 | 121.5546 | -43.6203 | 77.6276 | -0.0049592 | 0.0074319 | 0.020754 | 0.00017942 | 0.032509 | -0.0024951 | -0.045891 | -0.013123 | 0.0061973 | -0.015915 | -0.00032249 | 2.6128 | 0.028991 | 0.073242 | 0.10986 | 0.15106 | 0.12817 | 0.013733 | 0.041199 | -0.064087 | 0.050354 | 0.21973 | 0.027466 | 0.027466 | 0.064087 | 0.09613 | 0.041199 | 43.6615 | 43.5562 | -77.6138 | 43.7302 | 43.7485 | 0.19226 | -77.5543 | 43.7164 | 43.6615 | -77.6001 | 43.6707 | 43.6478 | -0.013733 | -77.5635 | 43.634 | 43.6935 | 43.7714 | -77.6916 | 43.6478 | 43.6844 | 43.84 | -77.5864
2907.4062 | 121.5683 | -43.4921 | 77.774 | -0.020218 | 0.0087137 | 0.018617 | 0.0040246 | 0.030373 | -0.0022815 | -0.048881 | -0.013123 | 0.0083335 | -0.014847 | -0.0028861 | 2.6344 | 0.028564 | -0.004578 | 0.018311 | 0.073242 | 0.091553 | 0.013733 | 0.054932 | -0.068665 | -0.022888 | 0.10071 | -0.041199 | 0.068665 | 0.059509 | 0.07782 | 0.045776 | 43.5471 | 43.4235 | -77.7603 | 43.5104 | 43.5837 | 0.16022 | -77.7786 | 43.5699 | 43.5379 | -77.7054 | 43.4692 | 43.4509 | -0.086975 | -77.7145 | 43.5059 | 43.4875 | 43.5654 | -77.8427 | 43.5608 | 43.5516 | 43.5928 | -77.7283
2909.2031 | 121.4676 | -44.2886 | 77.0508 | -0.012589 | 0.014909 | 0.019899 | 0.0029566 | 0.033364 | 0.0026319 | -0.047172 | -0.013123 | 0.011324 | -0.013351 | -0.00074989 | 2.5419 | 0.029632 | -0.009155 | -0.004578 | 0.045776 | 0.064087 | 0.050354 | 0.018311 | -0.082397 | -0.064087 | 0.07782 | -0.09613 | 0.082397 | 0.082397 | 0.045776 | 0 | 44.3069 | 44.2062 | -77.0004 | 44.2841 | 44.3527 | 0.14648 | -77.0599 | 44.3344 | 44.2886 | -76.9684 | 44.2245 | 44.1925 | -0.09613 | -76.9684 | 44.339 | 44.2795 | 44.3344 | -77.1332 | 44.371 | 44.371 | 44.3665 | -77.0508
2910.9219 | 121.5546 | -44.1788 | 77.0828 | -0.020218 | 0.014695 | 0.017763 | 0.00060662 | 0.031655 | -0.00014533 | -0.046745 | -0.0054932 | 0.01111 | -0.013138 | -0.0011771 | 2.5852 | 0.026855 | 0.064087 | 0.09613 | 0.13733 | 0.1236 | 0 | 0.045776 | -0.059509 | 0.041199 | 0.19226 | 0.018311 | 0.036621 | 0.045776 | 0.086975 | 0.041199 | 44.2245 | 44.1193 | -77.0828 | 44.2749 | 44.3024 | 0.1831 | -77.0187 | 44.2657 | 44.22 | -77.0462 | 44.22 | 44.1971 | -0.022888 | -77.037 | 44.1788 | 44.2429 | 44.3161 | -77.1423 | 44.2154 | 44.2245 | 44.371 | -77.0416
2912.7031 | 121.4767 | -44.1376 | 77.179 | -0.012589 | 0.012132 | 0.015627 | -0.00046138 | 0.032936 | 0.0034863 | -0.0476 | -0.020752 | 0.01581 | -0.013779 | 0.00074551 | 2.5812 | 0.026427 | 0.045776 | -0.004578 | 0.036621 | 0.082397 | 0.050354 | 0.009155 | -0.082397 | 0.018311 | 0.10529 | -0.07782 | 0.073242 | 0.068665 | 0.082397 | 0.004578 | 44.1467 | 44.0552 | -77.1286 | 44.133 | 44.22 | 0.16479 | -77.1332 | 44.22 | 44.1422 | -77.1057 | 44.1559 | 44.0598 | -0.082398 | -77.1103 | 44.1879 | 44.1833 | 44.1742 | -77.2614 | 44.2108 | 44.2062 | 44.2429 | -77.1744
2914.4219 | 121.5363 | -44.0277 | 77.2476 | -0.012589 | 0.010209 | 0.018831 | -0.00067498 | 0.031655 | -0.0029223 | -0.044609 | 0.0021363 | 0.0072653 | -0.015488 | 0.00053191 | 2.5201 | 0.030486 | 0.041199 | 0.041199 | 0.11444 | 0.10529 | -0.004578 | 0.045776 | -0.073242 | 0.013733 | 0.12817 | -0.013733 | 0.018311 | 0.032043 | 0.10071 | 0.041199 | 44.0735 | 43.9545 | -77.2522 | 44.0689 | 44.133 | 0.17853 | -77.2064 | 44.1284 | 44.0689 | -77.2293 | 44.0414 | 44.014 | -0.054932 | -77.2156 | 44.0231 | 44.0689 | 44.1422 | -77.3209 | 44.046 | 44.0598 | 44.1559 | -77.2064
2916.2031 | 121.6187 | -44.0094 | 77.2751 | -0.0049592 | 0.011918 | 0.017549 | 0.00082022 | 0.031655 | -0.0016405 | -0.048668 | 0.0021363 | 0.0076925 | -0.015701 | -0.0020315 | 2.557 | 0.02835 | 0.009155 | 0.041199 | 0.09613 | 0.11444 | 0.022888 | 0.036621 | -0.068665 | 0.022888 | 0.16937 | 0.004578 | 0.018311 | 0.032043 | 0.1236 | 0.041199 | 44.046 | 43.9407 | -77.2522 | 44.0506 | 44.1238 | 0.18311 | -77.2659 | 44.133 | 44.0506 | -77.2568 | 44.0323 | 44.014 | -0.036621 | -77.243 | 44.0323 | 44.0186 | 44.1055 | -77.3438 | 44.0277 | 44.0414 | 44.1788 | -77.2339
2917.9688 | 121.6095 | -44.1559 | 77.0966 | -0.012589 | 0.012773 | 0.020113 | 0.00039302 | 0.032509 | -0.0027087 | -0.046318 | -0.0054932 | 0.0096151 | -0.01442 | -0.0020315 | 2.5177 | 0.028136 | 0.041199 | 0.07782 | 0.11902 | 0.11902 | 0.013733 | 0.032043 | -0.059509 | 0.045776 | 0.17395 | 0.022888 | 0 | 0.013733 | 0.082397 | 0.032043 | 44.1879 | 44.0964 | -77.0828 | 44.2337 | 44.2749 | 0.17853 | -77.0554 | 44.2383 | 44.1879 | -77.0966 | 44.2017 | 44.1788 | -0.009155 | -77.0828 | 44.1696 | 44.1971 | 44.2749 | -77.1561 | 44.1559 | 44.1696 | 44.3298 | -77.0645
2919.75 | 121.6049 | -44.0186 | 77.2476 | -0.0049592 | 0.011277 | 0.019472 | -0.00088858 | 0.032509 | 0.0043409 | -0.045036 | -0.0054932 | 0.013674 | -0.01506 | 0.0018137 | 2.5323 | 0.027495 | 0.009155 | -0.009155 | 0.022888 | 0.07782 | 0.045776 | 0.032043 | -0.091553 | 0.022888 | 0.09613 | -0.064087 | -0.009155 | 0.004578 | 0.09613 | 0.045776 | 44.0506 | 43.927 | -77.2018 | 44.0094 | 44.0964 | 0.16937 | -77.2385 | 44.1147 | 44.0643 | -77.2568 | 44.0414 | 43.9545 | -0.10986 | -77.243 | 44.0643 | 44.0277 | 44.0414 | -77.3392 | 44.0094 | 44.0231 | 44.1147 | -77.2018
2921.5312 | 121.4767 | -43.9224 | 77.4307 | -0.012589 | 0.021318 | 0.014558 | 0.0057336 | 0.034218 | 0.0064771 | -0.043968 | -0.0054932 | 0.014742 | -0.012283 | 0.00010471 | 2.6075 | 0.026855 | 0.009155 | 0.004578 | 0.041199 | 0.073242 | 0.041199 | 0.032043 | -0.10529 | 0.004578 | 0.050354 | -0.11902 | 0.032043 | 0.036621 | 0.068665 | 0.009155 | 43.9545 | 43.8171 | -77.3895 | 43.927 | 43.9957 | 0.17853 | -77.4216 | 43.9911 | 43.9316 | -77.3987 | 43.927 | 43.8034 | -0.12817 | -77.3941 | 43.9636 | 43.9316 | 43.9636 | -77.536 | 43.9545 | 43.959 | 43.9728 | -77.4216
2923.2344 | 121.6049 | -43.5928 | 77.7054 | -0.012589 | 0.011704 | 0.019685 | 0.0014612 | 0.033364 | -0.0039905 | -0.047386 | -0.013123 | 0.0074789 | -0.014633 | -0.0030997 | 2.5756 | 0.030486 | -0.018311 | 0.009155 | 0.07782 | 0.086975 | 0.018311 | 0.045776 | -0.068665 | -0.004578 | 0.10986 | -0.045776 | -0.018311 | 0.022888 | 0.091553 | 0.032043 | 43.6386 | 43.5242 | -77.6871 | 43.602 | 43.6798 | 0.15564 | -77.7237 | 43.6844 | 43.6249 | -77.7237 | 43.5883 | 43.5471 | -0.077819 | -77.6825 | 43.6111 | 43.5745 | 43.6707 | -77.774 | 43.5745 | 43.6157 | 43.7027 | -77.6733
2925.0156 | 121.6049 | -43.5196 | 77.774 | -0.012589 | 0.012132 | 0.019899 | 0.0025292 | 0.032509 | -0.0033495 | -0.047172 | -0.013123 | 0.0091879 | -0.014847 | -0.0022453 | 2.569 | 0.028564 | 0.064087 | 0.11902 | 0.13275 | 0.11902 | 0.009155 | 0.050354 | -0.059509 | 0.064087 | 0.21515 | 0.036621 | -0.013733 | 0.004578 | 0.11444 | 0.032043 | 43.5699 | 43.4601 | -77.7649 | 43.6386 | 43.6386 | 0.17853 | -77.71 | 43.634 | 43.5516 | -77.7878 | 43.5837 | 43.5562 | 0.004578 | -77.7695 | 43.5287 | 43.5837 | 43.6523 | -77.8336 | 43.5059 | 43.5242 | 43.7347 | -77.742
2926.7344 | 121.5454 | -43.4967 | 77.8427 | -0.012589 | 0.015122 | 0.020326 | 0.0016748 | 0.030586 | -0.00014533 | -0.046959 | -0.020752 | 0.0081199 | -0.01506 | -0.0033133 | 2.5365 | 0.027495 | 0.045776 | 0.10071 | 0.1236 | 0.1236 | 0.013733 | 0.050354 | -0.059509 | 0.027466 | 0.16937 | -0.013733 | -0.004578 | 0 | 0.09613 | 0.032043 | 43.5471 | 43.4372 | -77.829 | 43.5974 | 43.6203 | 0.1831 | -77.7969 | 43.5928 | 43.5287 | -77.8473 | 43.5242 | 43.483 | -0.045776 | -77.8427 | 43.5104 | 43.5425 | 43.6203 | -77.9022 | 43.4921 | 43.4967 | 43.6661 | -77.8107
2928.5156 | 121.6187 | -43.4738 | 77.7924 | -0.0049592 | 0.011064 | 0.018404 | -3.4178e-05 | 0.033577 | -0.0024951 | -0.048668 | -0.013123 | 0.0072653 | -0.014633 | -0.0037405 | 2.5899 | 0.02835 | -0.009155 | 0.027466 | 0.073242 | 0.091553 | 0.022888 | 0.050354 | -0.059509 | 0.018311 | 0.12817 | -0.013733 | 0.009155 | 0.009155 | 0.10529 | 0.041199 | 43.5242 | 43.4143 | -77.7695 | 43.5013 | 43.5654 | 0.15106 | -77.8015 | 43.5791 | 43.515 | -77.7832 | 43.4921 | 43.4601 | -0.054932 | -77.7832 | 43.4967 | 43.4647 | 43.5471 | -77.8519 | 43.483 | 43.483 | 43.602 | -77.7512
2930.25 | 121.55 | -43.5059 | 77.8473 | -0.012589 | 0.014909 | 0.016908 | 0.001034 | 0.034859 | 0.0064771 | -0.046318 | -0.013123 | 0.013674 | -0.01442 | -0.0013907 | 2.528 | 0.026214 | 0.004578 | -0.022888 | 0.022888 | 0.082397 | 0.041199 | 0.036621 | -0.10071 | 0 | 0.091553 | -0.07782 | 0.022888 | 0.045776 | 0.073242 | 0.009155 | 43.5425 | 43.4052 | -77.8061 | 43.483 | 43.5883 | 0.18311 | -77.8427 | 43.5791 | 43.515 | -77.8244 | 43.5059 | 43.428 | -0.086975 | -77.8015 | 43.5471 | 43.5104 | 43.5287 | -77.948 | 43.5287 | 43.5516 | 43.5974 | -77.8381
2932.0312 | 121.5866 | -43.4509 | 77.8198 | -0.0049592 | 0.011277 | 0.017976 | 0.00082022 | 0.032936 | -0.00099973 | -0.044822 | -0.0054932 | 0.011751 | -0.015701 | -0.0020315 | 2.5434 | 0.030273 | 0.059509 | 0.073242 | 0.11444 | 0.11902 | -0.013733 | 0.054932 | -0.036621 | 0.054932 | 0.14648 | -0.004578 | 0 | 0.009155 | 0.09613 | 0.050354 | 43.5059 | 43.4143 | -77.8336 | 43.5242 | 43.5699 | 0.15564 | -77.7603 | 43.5471 | 43.5013 | -77.8198 | 43.5059 | 43.4463 | -0.054932 | -77.8107 | 43.4372 | 43.5104 | 43.5654 | -77.8564 | 43.4509 | 43.4601 | 43.5974 | -77.7695
2933.75 | 121.5729 | -43.3456 | 77.9755 | -0.0049592 | 0.0097817 | 0.020113 | 0.00082022 | 0.036141 | -0.0018543 | -0.045677 | -0.0054932 | 0.010683 | -0.014847 | -0.0035269 | 2.5737 | 0.029204 | 0.009155 | 0.045776 | 0.07782 | 0.086975 | -0.004578 | 0.054932 | -0.050354 | -0.009155 | 0.10071 | -0.041199 | -0.009155 | 0.009155 | 0.09613 | 0.045776 | 43.4006 | 43.2953 | -77.98 | 43.3914 | 43.4326 | 0.13733 | -77.9663 | 43.4418 | 43.3914 | -77.9846 | 43.3365 | 43.3044 | -0.086975 | -77.9663 | 43.3411 | 43.3548 | 43.4235 | -78.0258 | 43.3365 | 43.3548 | 43.4463 | -77.9297
2935.5156 | 121.4813 | -43.3456 | 78.0121 | -0.012589 | 0.017045 | 0.014986 | -0.0017432 | 0.032509 | 0.0064771 | -0.047172 | -0.0054932 | 0.014528 | -0.01442 | 0.00095911 | 2.5596 | 0.027495 | -0.004578 | -0.027466 | -0.009155 | 0.059509 | 0.036621 | 0.022888 | -0.082397 | -0.054932 | 0.013733 | -0.16022 | 0.036621 | 0.041199 | 0.059509 | -0.004578 | 43.3685 | 43.2632 | -77.9755 | 43.3182 | 43.4052 | 0.14191 | -78.0167 | 43.4052 | 43.3411 | -77.9755 | 43.2907 | 43.1854 | -0.15564 | -77.9709 | 43.3823 | 43.3411 | 43.3365 | -78.0945 | 43.3823 | 43.3868 | 43.3594 | -78.0167
2937.2344 | 121.5454 | -43.1671 | 78.186 | -0.0049592 | 0.014695 | 0.019685 | 0.001034 | 0.02845 | -0.0033495 | -0.046318 | -0.013123 | 0.0074789 | -0.015488 | -0.0016043 | 2.5756 | 0.027923 | 0.050354 | 0.10071 | 0.11444 | 0.12817 | -0.004578 | 0.059509 | -0.041199 | 0.050354 | 0.16479 | 0.018311 | -0.009155 | 0 | 0.10529 | 0.027466 | 43.2266 | 43.1259 | -78.1906 | 43.2678 | 43.2953 | 0.16937 | -78.1357 | 43.2724 | 43.1946 | -78.1952 | 43.2175 | 43.1854 | -0.009155 | -78.186 | 43.1625 | 43.2175 | 43.2816 | -78.2272 | 43.158 | 43.1671 | 43.3319 | -78.1586
2939.0156 | 121.4767 | -43.1717 | 78.2181 | -0.012589 | 0.015763 | 0.017122 | -0.001316 | 0.032723 | 0.0047681 | -0.043968 | 0.0021363 | 0.013888 | -0.013351 | -0.00010889 | 2.5684 | 0.026855 | 0 | -0.022888 | 0 | 0.064087 | 0.027466 | 0.032043 | -0.068665 | -0.032043 | 0.032043 | -0.11902 | 0.018311 | 0.027466 | 0.059509 | 0.004578 | 43.2037 | 43.103 | -78.1906 | 43.1488 | 43.2358 | 0.13275 | -78.2181 | 43.2312 | 43.1763 | -78.1998 | 43.1396 | 43.0527 | -0.1236 | -78.1906 | 43.1992 | 43.1717 | 43.1717 | -78.2867 | 43.19 | 43.1992 | 43.2037 | -78.2135
2940.7969 | 121.5775 | -43.0115 | 78.3646 | -0.0049592 | 0.012345 | 0.019045 | 0.00017942 | 0.031655 | -0.0056995 | -0.043754 | -0.013123 | 0.0087607 | -0.014206 | -0.0039541 | 2.5916 | 0.030059 | 0.036621 | 0.11444 | 0.13275 | 0.11444 | -0.004578 | 0.036621 | -0.050354 | 0.036621 | 0.1831 | 0.009155 | -0.004578 | -0.004578 | 0.09613 | 0.041199 | 43.0481 | 42.9611 | -78.3691 | 43.1259 | 43.1259 | 0.16479 | -78.3279 | 43.1076 | 43.0527 | -78.3691 | 43.0481 | 43.0206 | -0.032044 | -78.3691 | 43.0069 | 43.0481 | 43.1442 | -78.4149 | 43.0069 | 43.0069 | 43.1946 | -78.3234
2942.5156 | 121.5042 | -42.9932 | 78.4378 | -0.0049592 | 0.014482 | 0.019472 | 0.0031702 | 0.032509 | -0.00057253 | -0.046745 | -0.0054932 | 0.0061973 | -0.014847 | -0.0018179 | 2.6028 | 0.027068 | 0.018311 | 0.054932 | 0.073242 | 0.10986 | 0.004578 | 0.032043 | -0.073242 | -0.032043 | 0.10071 | -0.073242 | 0.004578 | 0.032043 | 0.073242 | 0.013733 | 43.0252 | 42.9199 | -78.4332 | 43.0481 | 43.103 | 0.18311 | -78.4195 | 43.0664 | 43.0069 | -78.4332 | 42.9611 | 42.9199 | -0.086975 | -78.4058 | 42.9977 | 43.0115 | 43.0664 | -78.511 | 42.9977 | 43.0252 | 43.0939 | -78.4241
2944.2969 | 121.6232 | -43.0115 | 78.2547 | -0.0049592 | 0.0097817 | 0.016054 | -0.00088858 | 0.032509 | 0.00070927 | -0.044395 | -0.020752 | 0.01111 | -0.012711 | -0.00096349 | 2.5884 | 0.027495 | 0.041199 | 0.064087 | 0.086975 | 0.13733 | 0.009155 | 0.07782 | -0.036621 | 0.064087 | 0.13733 | -0.018311 | -0.032043 | 0 | 0.10986 | 0.045776 | 43.0893 | 42.9749 | -78.2455 | 43.0756 | 43.1488 | 0.17395 | -78.2135 | 43.1213 | 43.0573 | -78.2867 | 43.0756 | 42.9932 | -0.064087 | -78.2547 | 43.0206 | 43.0527 | 43.0984 | -78.2913 | 42.9794 | 43.0115 | 43.1488 | -78.2089
2946.0781 | 121.6095 | -43.0527 | 78.2639 | -0.012589 | 0.010636 | 0.019685 | -0.0032386 | 0.029946 | 0.00028207 | -0.046745 | -0.013123 | 0.011324 | -0.016342 | -0.0011771 | 2.6008 | 0.030059 | 0.045776 | 0.086975 | 0.10529 | 0.1236 | 0.013733 | 0.059509 | -0.054932 | 0.032043 | 0.11902 | 0.009155 | -0.018311 | -0.018311 | 0.091553 | 0.045776 | 43.1122 | 42.9977 | -78.2501 | 43.1396 | 43.1763 | 0.17853 | -78.2181 | 43.1442 | 43.0984 | -78.2822 | 43.0847 | 43.0618 | -0.036621 | -78.2822 | 43.0664 | 43.0984 | 43.158 | -78.3188 | 43.0344 | 43.0344 | 43.1717 | -78.2181
2947.8594 | 121.6187 | -43.0252 | 78.2593 | -0.012589 | 0.012132 | 0.016054 | 0.00060662 | 0.02845 | 0.0026319 | -0.045677 | -0.020752 | 0.012392 | -0.013779 | -0.0011771 | 2.5865 | 0.027923 | -0.027466 | -0.068665 | -0.013733 | 0.032043 | 0.054932 | 0.022888 | -0.086975 | -0.041199 | 0.013733 | -0.10529 | 0 | 0.013733 | 0.07782 | 0.009155 | 43.0481 | 42.9382 | -78.2043 | 42.9565 | 43.0573 | 0.11902 | -78.2867 | 43.103 | 43.0344 | -78.2593 | 42.984 | 42.9199 | -0.11444 | -78.2455 | 43.0801 | 42.9977 | 43.0115 | -78.3463 | 43.0252 | 43.0389 | 43.0389 | -78.2501
2949.5781 | 121.6599 | -43.1671 | 78.1311 | -0.020218 | 0.011064 | 0.019045 | 0.0012476 | 0.030586 | -0.0029223 | -0.045891 | -0.020752 | 0.0074789 | -0.013779 | -0.0022453 | 2.6126 | 0.02835 | 0.004578 | 0.059509 | 0.10071 | 0.11444 | 0.036621 | 0.050354 | -0.050354 | 0.018311 | 0.15564 | 0.027466 | -0.013733 | -0.004578 | 0.09613 | 0.036621 | 43.2175 | 43.1168 | -78.0945 | 43.2266 | 43.2816 | 0.16479 | -78.1265 | 43.2632 | 43.2037 | -78.1448 | 43.1854 | 43.1946 | -0.009155 | -78.1357 | 43.2037 | 43.1717 | 43.2678 | -78.1815 | 43.1534 | 43.1625 | 43.3228 | -78.0945
2951.3906 | 121.55 | -43.2678 | 78.1265 | -0.012589 | 0.01555 | 0.016267 | -0.0028112 | 0.032509 | 0.0062635 | -0.046104 | -0.020752 | 0.013674 | -0.015915 | 0.0011727 | 2.5414 | 0.02835 | -0.059509 | -0.073242 | -0.032043 | 0.050354 | 0.054932 | 0.009155 | -0.086975 | -0.068665 | -0.013733 | -0.14191 | 0.022888 | 0.036621 | 0.059509 | 0.004578 | 43.277 | 43.1808 | -78.0716 | 43.1946 | 43.3182 | 0.13733 | -78.186 | 43.3273 | 43.2724 | -78.1036 | 43.1992 | 43.1259 | -0.14649 | -78.0899 | 43.3228 | 43.2083 | 43.2358 | -78.2135 | 43.2907 | 43.3044 | 43.2541 | -78.1219
2953.1094 | 121.6553 | -43.2678 | 78.0304 | -0.020218 | 0.012345 | 0.018831 | 0.003811 | 0.031868 | -0.0037769 | -0.046104 | -0.013123 | 0.0087607 | -0.011429 | -0.0020315 | 2.5782 | 0.028564 | -0.022888 | 0.018311 | 0.064087 | 0.059509 | 0.027466 | 0.054932 | -0.054932 | -0.009155 | 0.09613 | -0.032043 | -0.027466 | 0.022888 | 0.086975 | 0.036621 | 43.3228 | 43.2129 | -78.0029 | 43.2861 | 43.3273 | 0.11444 | -78.0533 | 43.3548 | 43.3044 | -78.0579 | 43.2587 | 43.2358 | -0.068664 | -78.0075 | 43.2953 | 43.2449 | 43.3319 | -78.0853 | 43.2404 | 43.2907 | 43.364 | -77.9938
2954.9062 | 121.5408 | -43.3411 | 78.0533 | -0.012589 | 0.016191 | 0.016695 | -0.00046138 | 0.032295 | 0.0051953 | -0.043754 | -0.0054932 | 0.014101 | -0.01506 | -0.0022453 | 2.5378 | 0.027709 | -0.064087 | -0.09613 | -0.054932 | 0.027466 | 0.045776 | 0.027466 | -0.073242 | -0.054932 | -0.018311 | -0.15564 | 0.018311 | 0.013733 | 0.059509 | 0.013733 | 43.3685 | 43.2678 | -78.0075 | 43.2449 | 43.3685 | 0.10071 | -78.1174 | 43.4006 | 43.3548 | -78.035 | 43.2861 | 43.1854 | -0.16937 | -78.0396 | 43.3868 | 43.277 | 43.2861 | -78.1265 | 43.3594 | 43.3548 | 43.3228 | -78.0396
2956.6875 | 121.5363 | -43.3548 | 78.0579 | -0.0049592 | 0.015122 | 0.018617 | 0.0057336 | 0.033577 | -0.00057253 | -0.044182 | -0.013123 | 0.011324 | -0.01442 | -0.0018179 | 2.5205 | 0.028777 | 0.013733 | 0.064087 | 0.086975 | 0.10529 | 0.018311 | 0.041199 | -0.07782 | -0.032043 | 0.10529 | -0.054932 | 0 | 0.032043 | 0.064087 | 0.013733 | 43.396 | 43.277 | -78.0396 | 43.4189 | 43.4601 | 0.18311 | -78.0441 | 43.4189 | 43.3685 | -78.0579 | 43.3228 | 43.2999 | -0.068665 | -78.0258 | 43.3731 | 43.3685 | 43.4418 | -78.1357 | 43.3548 | 43.3868 | 43.4601 | -78.0441
2958.4531 | 121.6507 | -43.2724 | 78.0807 | -0.012589 | 0.012345 | 0.018617 | 0.0023156 | 0.033364 | -0.0031359 | -0.04525 | -0.0054932 | 0.0087607 | -0.013351 | -0.0033133 | 2.4483 | 0.028991 | 0.050354 | 0.11902 | 0.11902 | 0.13275 | 0.004578 | 0.064087 | -0.054932 | 0.054932 | 0.1831 | 0.013733 | -0.022888 | -0.022888 | 0.082397 | 0.032043 | 43.3365 | 43.2175 | -78.0762 | 43.3914 | 43.4052 | 0.18768 | -78.0304 | 43.3548 | 43.3044 | -78.1036 | 43.3273 | 43.2861 | -0.01831 | -78.1036 | 43.277 | 43.3228 | 43.3914 | -78.1357 | 43.2495 | 43.2495 | 43.4555 | -78.0487
2960.1875 | 121.5454 | -43.3228 | 78.0899 | -0.020218 | 0.016831 | 0.016908 | 0.0033838 | 0.034218 | 0.0022047 | -0.047813 | -0.013123 | 0.010897 | -0.012924 | -0.00010889 | 2.4652 | 0.027282 | -0.054932 | -0.045776 | -0.022888 | 0.036621 | 0.054932 | 0.022888 | -0.10071 | -0.068665 | 0.032043 | -0.12817 | 0.022888 | 0.045776 | 0.045776 | -0.004578 | 43.3456 | 43.222 | -78.035 | 43.277 | 43.3594 | 0.13733 | -78.1448 | 43.3685 | 43.3182 | -78.067 | 43.2541 | 43.1946 | -0.1236 | -78.0441 | 43.3777 | 43.2678 | 43.2999 | -78.1906 | 43.3456 | 43.3685 | 43.3548 | -78.0945
2961.9688 | 121.5271 | -43.364 | 78.0029 | -0.0049592 | 0.012986 | 0.014772 | -0.00088858 | 0.032082 | 0.0058363 | -0.045677 | -0.013123 | 0.012179 | -0.016342 | 0.0020273 | 2.4816 | 0.026641 | 0.036621 | 0.013733 | 0.032043 | 0.091553 | 0.022888 | 0.036621 | -0.054932 | -0.013733 | 0.073242 | -0.10529 | 0.004578 | 0.022888 | 0.073242 | 0 | 43.4006 | 43.309 | -77.98 | 43.3777 | 43.4555 | 0.14649 | -77.9663 | 43.4372 | 43.364 | -77.9984 | 43.3502 | 43.2587 | -0.10529 | -77.98 | 43.3868 | 43.4006 | 43.396 | -78.0579 | 43.3685 | 43.3868 | 43.4372 | -78.0029
2963.7656 | 121.669 | -43.2724 | 78.0029 | -0.012589 | 0.012132 | 0.017549 | 0.0029566 | 0.031227 | -0.0039905 | -0.046104 | -0.013123 | 0.0068381 | -0.015701 | -0.0018179 | 2.4769 | 0.028777 | 0.013733 | 0.07782 | 0.11444 | 0.11902 | 0 | 0.064087 | -0.050354 | 0.041199 | 0.18768 | 0.032043 | -0.036621 | -0.009155 | 0.091553 | 0.041199 | 43.3365 | 43.222 | -78.0029 | 43.3502 | 43.3914 | 0.16937 | -77.9892 | 43.364 | 43.3136 | -78.0396 | 43.3136 | 43.3044 | -0.009156 | -78.0121 | 43.2724 | 43.2861 | 43.3868 | -78.0533 | 43.2358 | 43.2632 | 43.4601 | -77.9617
2965.4844 | 121.5591 | -43.4143 | 77.9984 | -0.0049592 | 0.013627 | 0.017763 | 0.0018884 | 0.035073 | 0.00049567 | -0.046318 | -0.0054932 | 0.011965 | -0.016129 | -0.0013907 | 2.5598 | 0.027282 | 0.050354 | 0.073242 | 0.10529 | 0.11444 | 0.009155 | 0.073242 | -0.032043 | 0.027466 | 0.16479 | -0.022888 | -0.027466 | 0 | 0.091553 | 0.032043 | 43.4875 | 43.3823 | -77.9892 | 43.4875 | 43.5287 | 0.14648 | -77.948 | 43.5059 | 43.4464 | -78.0258 | 43.4418 | 43.3914 | -0.054931 | -77.9984 | 43.4235 | 43.4647 | 43.5196 | -78.0304 | 43.3868 | 43.4143 | 43.5791 | -77.9663
2967.2812 | 121.5363 | -43.3548 | 78.0487 | -0.0049592 | 0.014054 | 0.017122 | 0.00039302 | 0.032509 | 0.00049567 | -0.045036 | -0.020752 | 0.011324 | -0.014206 | -0.00010889 | 2.5184 | 0.027282 | 0.009155 | 0.013733 | 0.059509 | 0.091553 | 0.032043 | 0.054932 | -0.064087 | -0.050354 | 0.073242 | -0.091553 | 0.004578 | 0.018311 | 0.064087 | -0.004578 | 43.4097 | 43.2907 | -78.0167 | 43.3685 | 43.4463 | 0.15564 | -78.0396 | 43.4189 | 43.3502 | -78.0441 | 43.3044 | 43.2632 | -0.086975 | -78.0304 | 43.3868 | 43.364 | 43.4143 | -78.1128 | 43.3594 | 43.3731 | 43.428 | -78.0533
2969.0625 | 121.669 | -43.2861 | 77.98 | -0.0049592 | 0.011491 | 0.018404 | -0.0011024 | 0.031868 | 0.0030591 | -0.043754 | -0.0054932 | 0.013674 | -0.013992 | 0.0011727 | 2.5615 | 0.027709 | 0.013733 | -0.027466 | 0.018311 | 0.054932 | 0.045776 | 0.045776 | -0.064087 | 0.009155 | 0.07782 | -0.073242 | 0 | 0.018311 | 0.068665 | 0.022888 | 43.3319 | 43.222 | -77.9343 | 43.2587 | 43.3411 | 0.11902 | -77.9663 | 43.3548 | 43.309 | -77.98 | 43.2953 | 43.2129 | -0.09613 | -77.9617 | 43.3319 | 43.2999 | 43.3044 | -78.0441 | 43.2861 | 43.3044 | 43.364 | -77.9572
2970.8594 | 121.5363 | -43.2632 | 78.1311 | -0.012589 | 0.014909 | 0.017336 | -0.00024778 | 0.032936 | 0.0058363 | -0.044609 | -0.013123 | 0.012179 | -0.012283 | -0.00032249 | 2.5605 | 0.027495 | 0.022888 | -0.009155 | 0.004578 | 0.073242 | 0.027466 | 0.036621 | -0.068665 | -0.018311 | 0.027466 | -0.13275 | -0.013733 | 0.027466 | 0.091553 | 0.009155 | 43.2999 | 43.1946 | -78.1036 | 43.2541 | 43.3365 | 0.14191 | -78.1082 | 43.3548 | 43.2724 | -78.1448 | 43.2449 | 43.1305 | -0.14191 | -78.1036 | 43.2907 | 43.2861 | 43.2678 | -78.1998 | 43.2495 | 43.2907 | 43.2907 | -78.1219
2972.5625 | 121.5363 | -43.309 | 78.1036 | -0.012589 | 0.014482 | 0.014986 | -0.00046138 | 0.033577 | 0.0056225 | -0.043968 | -0.0054932 | 0.012179 | -0.014206 | -0.00053629 | 2.5284 | 0.02835 | -0.027466 | -0.059509 | -0.013733 | 0.050354 | 0.041199 | 0.032043 | -0.064087 | -0.054932 | 0.018311 | -0.15564 | 0.004578 | 0.032043 | 0.045776 | -0.004578 | 43.3411 | 43.2449 | -78.0624 | 43.2495 | 43.3594 | 0.11444 | -78.1311 | 43.3548 | 43.3044 | -78.0991 | 43.2541 | 43.1534 | -0.15106 | -78.0716 | 43.3502 | 43.2816 | 43.2953 | -78.1677 | 43.3136 | 43.3411 | 43.3273 | -78.1082
2974.3438 | 121.637 | -43.2175 | 78.1494 | -0.0049592 | 0.012345 | 0.019685 | 0.0012476 | 0.032295 | -0.0054859 | -0.044609 | -0.013123 | 0.0089743 | -0.01442 | -0.00096349 | 2.5374 | 0.032409 | 0.004578 | 0.022888 | 0.064087 | 0.091553 | 0.009155 | 0.054932 | -0.036621 | -0.036621 | 0.082397 | -0.045776 | -0.022888 | 0.022888 | 0.091553 | 0.027466 | 43.2724 | 43.1808 | -78.1403 | 43.2404 | 43.309 | 0.12817 | -78.1448 | 43.309 | 43.2449 | -78.1723 | 43.1808 | 43.1717 | -0.073242 | -78.1265 | 43.2266 | 43.222 | 43.2816 | -78.186 | 43.1946 | 43.2404 | 43.2999 | -78.1219
2976.1406 | 121.6736 | -43.1946 | 78.1631 | -0.020218 | 0.01555 | 0.020326 | 0.00017942 | 0.030159 | 0.0011365 | -0.043754 | 0.0021363 | 0.010042 | -0.015701 | -0.0022453 | 2.5109 | 0.027068 | 0.064087 | 0.068665 | 0.11444 | 0.13275 | 0.004578 | 0.07782 | -0.036621 | 0.064087 | 0.13733 | -0.013733 | -0.045776 | -0.027466 | 0.091553 | 0.032043 | 43.2724 | 43.158 | -78.1586 | 43.2632 | 43.3273 | 0.16937 | -78.0991 | 43.2861 | 43.2266 | -78.2089 | 43.2587 | 43.1808 | -0.045776 | -78.1906 | 43.1992 | 43.2587 | 43.309 | -78.1998 | 43.1488 | 43.1671 | 43.3319 | -78.1311
2977.9219 | 121.5591 | -43.1717 | 78.2639 | -0.012589 | 0.015336 | 0.016481 | 0.0046656 | 0.032082 | 6.8274e-05 | -0.044395 | -0.0054932 | 0.011324 | -0.011002 | 0.00095911 | 2.585 | 0.029632 | -0.036621 | -0.022888 | 0.009155 | 0.068665 | 0.032043 | 0.045776 | -0.082397 | -0.073242 | 0.036621 | -0.11902 | 0.018311 | 0.027466 | 0.041199 | 0.004578 | 43.2175 | 43.0893 | -78.2318 | 43.1488 | 43.2404 | 0.15106 | -78.3005 | 43.2129 | 43.1763 | -78.2455 | 43.0984 | 43.0527 | -0.1236 | -78.2364 | 43.2037 | 43.1351 | 43.1808 | -78.3463 | 43.19 | 43.1992 | 43.2083 | -78.2593
2979.6875 | 121.5363 | -43.1763 | 78.2501 | -0.0049592 | 0.018754 | 0.014558 | 0.003811 | 0.031014 | 0.0043409 | -0.043968 | -0.020752 | 0.011965 | -0.011429 | 0.0024545 | 2.5551 | 0.026 | 0.004578 | -0.022888 | 0 | 0.068665 | 0.045776 | 0.036621 | -0.082397 | -0.027466 | 0.013733 | -0.13733 | 0 | 0.022888 | 0.073242 | -0.009155 | 43.2129 | 43.0939 | -78.2043 | 43.1534 | 43.2449 | 0.15106 | -78.2455 | 43.2495 | 43.1671 | -78.2501 | 43.1488 | 43.0389 | -0.12817 | -78.2272 | 43.222 | 43.1808 | 43.1763 | -78.3325 | 43.1763 | 43.1992 | 43.19 | -78.2593
2981.4219 | 121.6599 | -43.071 | 78.3279 | -0.012589 | 0.0078591 | 0.019472 | -0.00046138 | 0.032295 | -0.0046313 | -0.04525 | -0.0054932 | 0.0081199 | -0.014847 | 0.00031831 | 2.5547 | 0.030486 | 0.018311 | 0.032043 | 0.068665 | 0.11444 | 0.018311 | 0.054932 | -0.045776 | -0.022888 | 0.082397 | -0.036621 | -0.027466 | 0 | 0.068665 | 0.032043 | 43.1259 | 43.0252 | -78.3096 | 43.103 | 43.1854 | 0.16022 | -78.3096 | 43.1396 | 43.103 | -78.3554 | 43.0481 | 43.0344 | -0.068664 | -78.3279 | 43.0893 | 43.0893 | 43.1396 | -78.3737 | 43.0435 | 43.071 | 43.1534 | -78.2959
2983.2031 | 121.6049 | -43.0252 | 78.3966 | -0.0049592 | 0.013841 | 0.016908 | 0.00017942 | 0.034432 | 0.0051953 | -0.045463 | -0.0054932 | 0.013033 | -0.013779 | -0.0011771 | 2.5837 | 0.026427 | 0.022888 | 0.004578 | 0.018311 | 0.10986 | 0.068665 | 0.036621 | -0.091553 | -0.022888 | 0.07782 | -0.091553 | 0.013733 | 0.009155 | 0.073242 | 0.004578 | 43.0618 | 42.9337 | -78.3279 | 43.0298 | 43.1351 | 0.20142 | -78.3737 | 43.0984 | 43.0298 | -78.3829 | 43.0023 | 42.9337 | -0.096131 | -78.3875 | 43.0939 | 43.0481 | 43.0435 | -78.4882 | 43.0389 | 43.0344 | 43.103 | -78.392
2984.9219 | 121.5546 | -43.1671 | 78.2867 | -0.0049592 | 0.013841 | 0.017763 | -0.0019568 | 0.030586 | 0.0051953 | -0.043541 | -0.0054932 | 0.012606 | -0.013992 | 0.0022409 | 2.531 | 0.028991 | -0.018311 | -0.059509 | -0.018311 | 0.059509 | 0.050354 | 0.036621 | -0.073242 | -0.050354 | -0.004578 | -0.15564 | 0 | 0.027466 | 0.054932 | -0.004578 | 43.2037 | 43.0939 | -78.2364 | 43.1076 | 43.2266 | 0.13275 | -78.3051 | 43.222 | 43.1625 | -78.2867 | 43.1168 | 43.0115 | -0.15106 | -78.2593 | 43.2175 | 43.1488 | 43.1488 | -78.36 | 43.1671 | 43.1946 | 43.1625 | -78.2913
2986.7188 | 121.7148 | -43.0298 | 78.3325 | -0.012589 | 0.0091409 | -0.08499 | -3.4178e-05 | 0.029305 | -0.0042041 | -0.046959 | -0.0054932 | 0.0061973 | -0.015701 | -0.0018179 | 2.4889 | 0.031127 | 0.004578 | 0.068665 | 0.082397 | 0.11444 | 0.041199 | 0.064087 | -0.032043 | -0.013733 | 0.15564 | 0 | -0.032043 | -0.013733 | 0.10986 | 0.027466 | 43.0939 | 42.9977 | -78.2913 | 43.0984 | 43.1442 | 0.14648 | -78.3279 | 43.1396 | 43.0573 | -78.3646 | 43.0161 | 43.0298 | -0.027466 | -78.3463 | 43.071 | 43.0344 | 43.1122 | -78.3646 | 42.9977 | 43.0161 | 43.1854 | -78.3051
2988.4219 | 121.6873 | -42.952 | 78.4012 | -0.020218 | 0.0091409 | 0.020113 | 0.001034 | 0.032723 | -0.0042041 | -0.048668 | -0.020752 | 0.0098289 | -0.016983 | -0.0013907 | 2.623 | 0.029204 | -0.013733 | 0.018311 | 0.064087 | 0.09613 | 0.027466 | 0.073242 | -0.054932 | -0.036621 | 0.09613 | -0.032043 | -0.032043 | -0.009155 | 0.09613 | 0.004578 | 43.0252 | 42.897 | -78.3737 | 42.9703 | 43.0481 | 0.15106 | -78.4149 | 43.0481 | 42.9565 | -78.4332 | 42.9153 | 42.9199 | -0.036621 | -78.4103 | 42.9794 | 42.9382 | 43.0161 | -78.4561 | 42.9199 | 42.9428 | 43.0481 | -78.3966
2990.2031 | 121.6873 | -42.9382 | 78.4058 | -0.012589 | 0.012986 | 0.020326 | 0.0031702 | 0.029091 | -0.0014269 | -0.04824 | -0.013123 | 0.0094015 | -0.015915 | -0.0026725 | 2.4921 | 0.027923 | 0.064087 | 0.064087 | 0.09613 | 0.11902 | 0.032043 | 0.068665 | -0.054932 | 0.022888 | 0.15564 | 0.032043 | -0.032043 | -0.013733 | 0.09613 | 0.036621 | 43.0069 | 42.8833 | -78.3737 | 43.0023 | 43.0573 | 0.17395 | -78.3417 | 43.0344 | 42.9749 | -78.4378 | 42.9611 | 42.9703 | -0.004578 | -78.4195 | 42.9703 | 43.0023 | 43.0344 | -78.4607 | 42.9062 | 42.9245 | 43.0939 | -78.3691
2991.9844 | 121.5591 | -42.9153 | 78.511 | -0.0049592 | 0.014909 | 0.014986 | -0.003025 | 0.034859 | 0.0069043 | -0.044182 | -0.020752 | 0.01346 | -0.013565 | 0.0033089 | 2.5201 | 0.024932 | -0.009155 | -0.091553 | -0.027466 | 0.041199 | 0.050354 | 0.036621 | -0.086975 | -0.07782 | -0.027466 | -0.16937 | 0 | 0.027466 | 0.064087 | -0.009155 | 42.952 | 42.8284 | -78.4607 | 42.8238 | 42.9565 | 0.12817 | -78.5202 | 42.9794 | 42.9062 | -78.511 | 42.8375 | 42.746 | -0.16022 | -78.4836 | 42.9657 | 42.9062 | 42.8879 | -78.598 | 42.9153 | 42.9428 | 42.8879 | -78.5202
2993.7031 | 121.6873 | -42.8925 | 78.4744 | -0.020218 | 0.011277 | 0.019472 | 0.00082022 | 0.029732 | -0.0027087 | -0.046959 | -0.0054932 | 0.0070517 | -0.014847 | -0.0020315 | 2.5273 | 0.028564 | 0.054932 | 0.068665 | 0.09613 | 0.13275 | 0.009155 | 0.068665 | -0.041199 | 0.027466 | 0.14191 | 0.022888 | -0.027466 | -0.032043 | 0.068665 | 0.009155 | 42.9611 | 42.8513 | -78.4653 | 42.9611 | 43.0252 | 0.17395 | -78.4195 | 42.9611 | 42.9016 | -78.5019 | 42.9199 | 42.9153 | 0.013733 | -78.5065 | 42.9016 | 42.9474 | 42.9886 | -78.5156 | 42.865 | 42.8604 | 43.0344 | -78.4653
2995.4688 | 121.6507 | -42.8421 | 78.5385 | -0.012589 | 0.012345 | 0.017549 | 0.00039302 | 0.034432 | 0.0030591 | -0.046104 | -0.0054932 | 0.01047 | -0.013565 | -0.0016043 | 2.5626 | 0.027282 | 0.07782 | 0.064087 | 0.11902 | 0.12817 | 0.004578 | 0.082397 | -0.041199 | 0.054932 | 0.11902 | -0.004578 | -0.059509 | -0.045776 | 0.10071 | 0.036621 | 42.9245 | 42.8009 | -78.5339 | 42.9062 | 42.9703 | 0.16937 | -78.4607 | 42.9428 | 42.8787 | -78.598 | 42.897 | 42.8375 | -0.041199 | -78.5843 | 42.8467 | 42.9199 | 42.9611 | -78.5797 | 42.7826 | 42.7963 | 42.9611 | -78.5019
2997.25 | 121.6599 | -42.8284 | 78.5385 | -0.012589 | 0.012345 | 0.017549 | 0.0025292 | 0.032936 | -0.00099973 | -0.046531 | -0.0054932 | 0.0094015 | -0.014633 | -0.00053629 | 2.5765 | 0.027923 | 0.073242 | 0.10071 | 0.12817 | 0.13275 | 0.004578 | 0.054932 | -0.041199 | 0.041199 | 0.16479 | -0.004578 | -0.018311 | -0.013733 | 0.10071 | 0.022888 | 42.8833 | 42.7872 | -78.5339 | 42.9291 | 42.9611 | 0.17395 | -78.4653 | 42.9291 | 42.8513 | -78.5568 | 42.8696 | 42.8238 | -0.027466 | -78.5522 | 42.8329 | 42.9016 | 42.9565 | -78.5797 | 42.8101 | 42.8146 | 42.9932 | -78.5156
2999.0312 | 121.5912 | -42.9062 | 78.4836 | -0.012589 | 0.012986 | 0.018404 | 0.00017942 | 0.0308 | 0.0066907 | -0.046104 | -0.020752 | 0.012819 | -0.01442 | 0.00031831 | 2.6357 | 0.026641 | -0.022888 | -0.082397 | -0.022888 | 0.041199 | 0.068665 | 0.036621 | -0.07782 | -0.050354 | -0.041199 | -0.17853 | -0.022888 | 0.027466 | 0.073242 | -0.013733 | 42.9428 | 42.8284 | -78.4149 | 42.8238 | 42.9474 | 0.11902 | -78.5065 | 42.9794 | 42.8925 | -78.5065 | 42.8558 | 42.7277 | -0.16479 | -78.4561 | 42.9749 | 42.8833 | 42.8833 | -78.5614 | 42.8833 | 42.9337 | 42.865 | -78.4973
3000.75 | 121.6919 | -42.9016 | 78.4424 | -0.0049592 | 0.014268 | 0.017549 | 0.00039302 | 0.0308 | 0.0026319 | -0.045036 | -0.0054932 | 0.014528 | -0.014847 | 0.0018137 | 2.5829 | 0.029845 | -0.013733 | -0.054932 | -0.013733 | 0.064087 | 0.045776 | 0.036621 | -0.07782 | -0.027466 | 0 | -0.10986 | -0.009155 | 0.009155 | 0.082397 | 0.018311 | 42.9382 | 42.8238 | -78.3966 | 42.8467 | 42.9657 | 0.14191 | -78.4561 | 42.984 | 42.9199 | -78.4515 | 42.8741 | 42.7917 | -0.12817 | -78.4332 | 42.9474 | 42.8879 | 42.8879 | -78.5202 | 42.8925 | 42.9108 | 42.9016 | -78.4241
3002.5312 | 121.5683 | -42.8558 | 78.5934 | -0.0049592 | 0.0132 | 0.020113 | 0.003811 | 0.032082 | -0.00078613 | -0.044395 | -0.013123 | 0.011324 | -0.014206 | -0.0024589 | 2.5194 | 0.027709 | 0 | 0.027466 | 0.045776 | 0.086975 | 0.027466 | 0.032043 | -0.073242 | -0.050354 | 0.041199 | -0.11444 | 0.004578 | 0.018311 | 0.064087 | -0.018311 | 42.8879 | 42.7826 | -78.566 | 42.8833 | 42.9428 | 0.16022 | -78.5934 | 42.9199 | 42.8375 | -78.5889 | 42.8055 | 42.7414 | -0.09613 | -78.5751 | 42.8833 | 42.8558 | 42.9016 | -78.6667 | 42.8604 | 42.8741 | 42.897 | -78.6118
3004.2656 | 121.7377 | -42.746 | 78.6026 | -0.0049592 | 0.011491 | 0.019472 | 0.00082022 | 0.03315 | -0.0042041 | -0.046959 | -0.013123 | 0.0070517 | -0.015274 | -0.00032249 | 2.4573 | 0.028991 | 0.013733 | 0.059509 | 0.11902 | 0.12817 | 0.027466 | 0.059509 | -0.045776 | 0.009155 | 0.14648 | 0.018311 | -0.018311 | -0.022888 | 0.10071 | 0.027466 | 42.8055 | 42.7002 | -78.5751 | 42.8055 | 42.8741 | 0.17395 | -78.5889 | 42.8467 | 42.7734 | -78.6209 | 42.7551 | 42.7643 | -0.009155 | -78.6255 | 42.7734 | 42.7597 | 42.865 | -78.6484 | 42.7277 | 42.7231 | 42.8925 | -78.5751
3006.0469 | 121.5866 | -42.8192 | 78.6346 | -0.0049592 | 0.015336 | 0.017122 | 0.0035974 | 0.032936 | 0.0017773 | -0.04525 | -0.0054932 | 0.01111 | -0.011215 | 0.00010471 | 2.6021 | 0.026214 | -0.045776 | -0.050354 | -0.013733 | 0.050354 | 0.036621 | 0.036621 | -0.07782 | -0.07782 | 0.013733 | -0.13275 | 0.013733 | 0.032043 | 0.041199 | -0.009155 | 42.8558 | 42.7414 | -78.598 | 42.7689 | 42.8696 | 0.12817 | -78.6804 | 42.8604 | 42.8101 | -78.6209 | 42.7414 | 42.6865 | -0.1236 | -78.6026 | 42.8558 | 42.7734 | 42.8055 | -78.7125 | 42.8329 | 42.8513 | 42.8329 | -78.6438
3007.7656 | 121.7148 | -42.7414 | 78.5934 | -0.012589 | 0.011704 | 0.018831 | 0.0048792 | 0.0308 | -0.0039905 | -0.046959 | -0.013123 | 0.0085471 | -0.01442 | -0.0013907 | 2.5925 | 0.028564 | -0.004578 | 0.018311 | 0.059509 | 0.1236 | 0 | 0.041199 | -0.041199 | 0.004578 | 0.11444 | -0.022888 | -0.041199 | -0.022888 | 0.086975 | 0.027466 | 42.7826 | 42.7002 | -78.5934 | 42.7597 | 42.865 | 0.16479 | -78.598 | 42.8284 | 42.7689 | -78.6346 | 42.746 | 42.7185 | -0.050354 | -78.6163 | 42.7414 | 42.7368 | 42.8009 | -78.6346 | 42.7002 | 42.7185 | 42.8558 | -78.566
3009.5312 | 121.669 | -42.8467 | 78.5339 | -0.020218 | 0.012345 | 0.017549 | -0.0021704 | 0.0308 | 0.0030591 | -0.044822 | -0.0054932 | 0.010042 | -0.014847 | 0.00053191 | 2.6186 | 0.027495 | 0.07782 | 0.064087 | 0.10986 | 0.13733 | 0.004578 | 0.082397 | -0.036621 | 0.07782 | 0.1236 | 0 | -0.027466 | -0.009155 | 0.086975 | 0.032043 | 42.9291 | 42.8101 | -78.5294 | 42.9108 | 42.984 | 0.17395 | -78.4561 | 42.9337 | 42.8787 | -78.5614 | 42.9245 | 42.8467 | -0.032043 | -78.5431 | 42.8513 | 42.9245 | 42.9565 | -78.5706 | 42.8192 | 42.8375 | 42.9703 | -78.5019
3011.3281 | 121.6003 | -42.9291 | 78.511 | -0.0049592 | 0.017045 | 0.019258 | 0.0018884 | 0.03315 | 0.0013501 | -0.046318 | -0.0054932 | 0.011751 | -0.014633 | -0.00096349 | 2.6483 | 0.027068 | -0.041199 | -0.036621 | -0.022888 | 0.036621 | 0.059509 | -0.004578 | -0.10529 | -0.059509 | 0.009155 | -0.14191 | 0.022888 | 0.041199 | 0.045776 | -0.009155 | 42.9245 | 42.8238 | -78.4515 | 42.8925 | 42.9657 | 0.14191 | -78.5522 | 42.9749 | 42.9199 | -78.4882 | 42.8696 | 42.7872 | -0.13275 | -78.4698 | 42.9886 | 42.8879 | 42.9062 | -78.6163 | 42.952 | 42.9703 | 42.9382 | -78.5202
3013.0625 | 121.5866 | -42.5354 | 78.8818 | -0.012589 | 0.017686 | 0.016695 | -0.00046138 | 0.028023 | 0.0054089 | -0.044609 | -0.0054932 | 0.012819 | -0.01442 | -0.00010889 | 2.5867 | 0.026641 | 0.022888 | 0.022888 | 0.041199 | 0.091553 | 0.054932 | 0.027466 | -0.07782 | 0.013733 | 0.10071 | -0.091553 | -0.022888 | 0.004578 | 0.082397 | -0.013733 | 42.5629 | 42.4576 | -78.8269 | 42.5583 | 42.627 | 0.16937 | -78.8589 | 42.6178 | 42.5217 | -78.9047 | 42.5491 | 42.4438 | -0.07782 | -78.8773 | 42.5903 | 42.5583 | 42.5766 | -78.9597 | 42.5125 | 42.54 | 42.6361 | -78.8956
3014.8438 | 121.5683 | -42.3065 | 79.1245 | -0.012589 | 0.015122 | 0.015627 | 0.00060662 | 0.034218 | 0.0043409 | -0.044395 | 0.0021363 | 0.01111 | -0.01207 | -0.00053629 | 2.5598 | 0.027068 | -0.036621 | -0.050354 | -0.013733 | 0.054932 | 0.036621 | 0.022888 | -0.073242 | -0.050354 | 0 | -0.16479 | -0.004578 | 0.013733 | 0.050354 | -0.009155 | 42.3294 | 42.2333 | -79.0878 | 42.2562 | 42.3615 | 0.12817 | -79.1611 | 42.3569 | 42.2974 | -79.129 | 42.2562 | 42.1417 | -0.15564 | -79.1107 | 42.3431 | 42.2699 | 42.2928 | -79.1977 | 42.3019 | 42.3203 | 42.3065 | -79.1336
3016.625 | 121.6873 | -42.2699 | 79.1336 | -0.0049592 | 0.012132 | 0.019472 | 0.0025292 | 0.032936 | -0.0031359 | -0.045463 | -0.0054932 | 0.0044883 | -0.015274 | -0.0024589 | 2.4885 | 0.028777 | 0.041199 | 0.13733 | 0.14648 | 0.14648 | -0.004578 | 0.059509 | -0.045776 | 0.027466 | 0.17853 | 0.022888 | -0.041199 | -0.027466 | 0.10071 | 0.032043 | 42.3294 | 42.2241 | -79.1382 | 42.4072 | 42.4164 | 0.19226 | -79.0924 | 42.3706 | 42.3019 | -79.1748 | 42.2974 | 42.2928 | -0.009155 | -79.1611 | 42.2653 | 42.3111 | 42.4164 | -79.1794 | 42.2287 | 42.2424 | 42.4484 | -79.1016
3018.3281 | 121.6095 | -42.1921 | 79.2618 | -0.020218 | 0.015763 | 0.017976 | -0.00067498 | 0.031655 | 0.0047681 | -0.045463 | -0.0054932 | 0.012392 | -0.013565 | -0.0016043 | 2.4863 | 0.026427 | -0.050354 | -0.041199 | -0.018311 | 0.054932 | 0.041199 | 0.027466 | -0.064087 | -0.073242 | 0.032043 | -0.13275 | 0.004578 | 0.009155 | 0.045776 | -0.027466 | 42.2195 | 42.128 | -79.2206 | 42.1509 | 42.247 | 0.11902 | -79.3121 | 42.2379 | 42.1646 | -79.2572 | 42.1188 | 42.0593 | -0.10529 | -79.2526 | 42.2333 | 42.1417 | 42.1738 | -79.3259 | 42.1967 | 42.2012 | 42.2241 | -79.2892
3020.0938 | 121.7056 | -42.1371 | 79.2114 | -0.0049592 | 0.012986 | 0.016267 | -0.0015296 | 0.031227 | 0.0024183 | -0.0429 | -0.013123 | 0.0094015 | -0.016129 | -0.0018179 | 2.5607 | 0.028564 | -0.018311 | -0.022888 | 0.009155 | 0.064087 | 0.032043 | 0.045776 | -0.059509 | -0.004578 | 0.054932 | -0.045776 | -0.032043 | -0.022888 | 0.091553 | 0.022888 | 42.1829 | 42.0776 | -79.1794 | 42.1143 | 42.2012 | 0.1236 | -79.2297 | 42.2287 | 42.16 | -79.2435 | 42.1326 | 42.0914 | -0.068664 | -79.2343 | 42.1692 | 42.1188 | 42.1463 | -79.2709 | 42.1051 | 42.1143 | 42.1921 | -79.1885
3021.875 | 121.5729 | -42.247 | 79.2206 | -0.012589 | 0.0179 | 0.017549 | 0.0012476 | 0.033364 | -0.0014269 | -0.043968 | -0.013123 | 0.011751 | -0.012497 | -0.0030997 | 2.5517 | 0.028564 | -0.073242 | -0.032043 | -0.013733 | 0.041199 | 0.032043 | 0.027466 | -0.082397 | -0.091553 | 0.022888 | -0.13275 | 0.022888 | 0.018311 | 0.054932 | -0.013733 | 42.2745 | 42.1646 | -79.1885 | 42.215 | 42.2882 | 0.1236 | -79.2938 | 42.3019 | 42.2333 | -79.1977 | 42.1555 | 42.1143 | -0.11902 | -79.2023 | 42.2791 | 42.1738 | 42.2333 | -79.303 | 42.2699 | 42.2653 | 42.2699 | -79.2343
3023.5781 | 121.5683 | -42.2195 | 79.2435 | -0.0049592 | 0.020463 | 0.015199 | 0.003811 | 0.032295 | 0.0056225 | -0.043754 | -0.013123 | 0.01346 | -0.010361 | -0.00032249 | 2.5814 | 0.026 | 0.009155 | -0.004578 | 0.022888 | 0.073242 | 0.045776 | 0.054932 | -0.07782 | -0.009155 | 0.050354 | -0.1236 | -0.004578 | -0.013733 | 0.059509 | 0 | 42.2745 | 42.1417 | -79.1977 | 42.215 | 42.2928 | 0.15106 | -79.2343 | 42.2791 | 42.2195 | -79.248 | 42.2104 | 42.0959 | -0.1236 | -79.2572 | 42.2653 | 42.2287 | 42.2424 | -79.3213 | 42.215 | 42.2058 | 42.2699 | -79.2435
3025.3594 | 121.582 | -42.0868 | 79.3716 | -0.0049592 | 0.014054 | 0.015199 | -0.0017432 | 0.032723 | 0.0030591 | -0.045891 | -0.013123 | 0.013247 | -0.013992 | 0.00095911 | 2.6077 | 0.027709 | 0.018311 | 0.027466 | 0.032043 | 0.07782 | 0.041199 | 0.032043 | -0.064087 | -0.018311 | 0.050354 | -0.10529 | -0.013733 | 0.004578 | 0.064087 | 0.009155 | 42.1188 | 42.0227 | -79.3304 | 42.1143 | 42.1646 | 0.14191 | -79.3533 | 42.1509 | 42.0959 | -79.3854 | 42.0685 | 41.9815 | -0.11444 | -79.3671 | 42.128 | 42.1051 | 42.1188 | -79.4357 | 42.0731 | 42.0914 | 42.1371 | -79.3625
3027.1406 | 121.5591 | -42.0273 | 79.4449 | -0.012589 | 0.016618 | 0.020113 | 0.0029566 | 0.034859 | -0.0016405 | -0.044609 | -0.013123 | 0.0085471 | -0.012497 | -0.0020315 | 2.6169 | 0.029845 | -0.022888 | 0.050354 | 0.064087 | 0.09613 | 0.018311 | 0.064087 | -0.059509 | -0.059509 | 0.054932 | -0.082397 | -0.018311 | 0.013733 | 0.064087 | 0.004578 | 42.0914 | 41.9678 | -79.4266 | 42.0776 | 42.1234 | 0.15564 | -79.4678 | 42.0914 | 42.0319 | -79.4632 | 41.9678 | 41.9449 | -0.086975 | -79.4312 | 42.0456 | 42.0044 | 42.0914 | -79.5044 | 42.009 | 42.041 | 42.0822 | -79.4403
3028.9219 | 121.5591 | -41.8488 | 79.5822 | -0.012589 | 0.016831 | 0.017763 | -0.0015296 | 0.031227 | 0.0060499 | -0.0429 | 0.0021363 | 0.013033 | -0.012711 | 0.00010471 | 2.6747 | 0.027923 | 0.013733 | 0.022888 | 0.036621 | 0.07782 | 0.027466 | 0.041199 | -0.073242 | -0.009155 | 0.059509 | -0.11444 | -0.009155 | 0.004578 | 0.059509 | 0 | 41.89 | 41.7755 | -79.5547 | 41.8716 | 41.9266 | 0.15106 | -79.5685 | 41.9083 | 41.8488 | -79.5914 | 41.8396 | 41.7343 | -0.11444 | -79.5776 | 41.8762 | 41.8625 | 41.8854 | -79.6555 | 41.8396 | 41.8533 | 41.9083 | -79.5822
3030.6875 | 121.6278 | -41.9357 | 79.5044 | -0.020218 | 0.0091409 | 0.018404 | 0.0014612 | 0.032295 | -0.0046313 | -0.045677 | -0.013123 | 0.0068381 | -0.016129 | -0.00096349 | 2.6288 | 0.030486 | 0.022888 | 0.09613 | 0.1236 | 0.14191 | 0 | 0.064087 | -0.041199 | 0.022888 | 0.16022 | -0.004578 | -0.032043 | -0.027466 | 0.091553 | 0.041199 | 41.9998 | 41.8945 | -79.5044 | 42.0319 | 42.0776 | 0.18311 | -79.4815 | 42.0273 | 41.9769 | -79.5364 | 41.9586 | 41.9312 | -0.045777 | -79.5319 | 41.9357 | 41.9586 | 42.0593 | -79.5456 | 41.9037 | 41.9083 | 42.0959 | -79.4632
3032.4062 | 121.5683 | -41.7572 | 79.7241 | -0.012589 | 0.016831 | 0.018404 | 0.0023156 | 0.035713 | -0.0012133 | -0.045036 | -0.0054932 | 0.010256 | -0.016342 | -0.00096349 | 2.654 | 0.026214 | 0.004578 | 0.013733 | 0.041199 | 0.086975 | 0.032043 | 0.036621 | -0.068665 | -0.068665 | 0.059509 | -0.091553 | 0 | 0.009155 | 0.059509 | 0.027466 | 41.7938 | 41.6885 | -79.6921 | 41.7709 | 41.8442 | 0.15564 | -79.7195 | 41.8167 | 41.7847 | -79.7241 | 41.6885 | 41.6656 | -0.11902 | -79.715 | 41.7892 | 41.7618 | 41.7984 | -79.7928 | 41.7572 | 41.7664 | 41.8167 | -79.6967
3034.2031 | 121.6873 | -40.3931 | 80.983 | -0.020218 | 0.014054 | 0.01819 | 0.0014612 | 0.034645 | -0.0056995 | -0.045891 | -0.0054932 | 0.0079063 | -0.012497 | -0.0028861 | 2.6124 | 0.027709 | 0.050354 | 0.11902 | 0.13733 | 0.11902 | 0.009155 | 0.059509 | -0.054932 | 0.022888 | 0.15106 | 0.009155 | -0.027466 | -0.013733 | 0.10071 | 0.032043 | 40.4526 | 40.3381 | -80.9738 | 40.5121 | 40.5121 | 0.17395 | -80.9326 | 40.4938 | 40.4251 | -81.0104 | 40.416 | 40.4022 | -0.022888 | -80.9967 | 40.4022 | 40.4434 | 40.5304 | -81.0379 | 40.3656 | 40.3793 | 40.5441 | -80.9509
3035.9844 | 121.6919 | -39.8026 | 81.5918 | -0.0049592 | 0.011064 | 0.016908 | -0.002384 | 0.030373 | 0.0036999 | -0.04525 | -0.013123 | 0.010256 | -0.015488 | -0.00096349 | 2.534 | 0.029418 | -0.009155 | -0.045776 | 0.009155 | 0.059509 | 0.032043 | 0.036621 | -0.059509 | -0.013733 | 0.054932 | -0.073242 | -0.027466 | -0.022888 | 0.082397 | 0.022888 | 39.8392 | 39.743 | -81.5598 | 39.7568 | 39.8621 | 0.11902 | -81.601 | 39.8849 | 39.8254 | -81.6193 | 39.7888 | 39.7293 | -0.09613 | -81.6147 | 39.8346 | 39.7934 | 39.8117 | -81.6513 | 39.7751 | 39.7797 | 39.8575 | -81.5689
3037.7031 | 121.5637 | -39.8392 | 81.6284 | -0.0049592 | 0.015336 | 0.019045 | 0.0035974 | 0.033577 | 0.00028207 | -0.044609 | -0.013123 | 0.01047 | -0.014847 | -0.00053629 | 2.538 | 0.025786 | -0.050354 | -0.036621 | 0.009155 | 0.045776 | 0.036621 | 0.041199 | -0.073242 | -0.09613 | 0.022888 | -0.13275 | 0.009155 | 0.027466 | 0.045776 | -0.027466 | 39.8804 | 39.7659 | -81.5918 | 39.8026 | 39.8849 | 0.11902 | -81.6788 | 39.8849 | 39.8117 | -81.6193 | 39.743 | 39.7064 | -0.10529 | -81.601 | 39.8758 | 39.7888 | 39.8483 | -81.7017 | 39.8483 | 39.8666 | 39.8621 | -81.6559
3039.4688 | 121.7102 | -39.1022 | 82.283 | -0.012589 | 0.0093545 | 0.018831 | 0.002102 | 0.030586 | -0.0039905 | -0.046104 | -0.013123 | 0.0089743 | -0.016983 | 0.00031831 | 2.5261 | 0.029418 | 0.009155 | 0.036621 | 0.07782 | 0.091553 | 0.022888 | 0.064087 | -0.059509 | -0.004578 | 0.12817 | -0.004578 | -0.036621 | -0.027466 | 0.10529 | 0.032043 | 39.1663 | 39.0427 | -82.2601 | 39.1388 | 39.1937 | 0.15106 | -82.2739 | 39.2075 | 39.1342 | -82.3196 | 39.0976 | 39.0976 | -0.036621 | -82.3105 | 39.1251 | 39.1113 | 39.18 | -82.3425 | 39.0656 | 39.0747 | 39.2303 | -82.251
3041.2656 | 121.5683 | -38.8458 | 82.6355 | -0.020218 | 0.014054 | 0.016908 | 0.0027428 | 0.032082 | -0.00014533 | -0.047172 | -0.013123 | 0.0096151 | -0.01442 | -0.00053629 | 2.4872 | 0.026214 | 0.054932 | 0.073242 | 0.091553 | 0.11444 | 0 | 0.073242 | -0.045776 | -0.009155 | 0.1236 | -0.064087 | -0.022888 | -0.027466 | 0.07782 | 0.022888 | 38.9191 | 38.8 | -82.6355 | 38.9191 | 38.9603 | 0.16022 | -82.5806 | 38.9236 | 38.8687 | -82.6584 | 38.8367 | 38.7817 | -0.086975 | -82.663 | 38.8458 | 38.9008 | 38.9374 | -82.6813 | 38.8229 | 38.8184 | 38.9694 | -82.6126
3042.9844 | 121.6873 | -38.0402 | 83.3496 | -0.012589 | 0.011491 | 0.015199 | -0.0017432 | 0.031868 | 0.0019909 | -0.046104 | -0.013123 | 0.013033 | -0.01442 | 0.00053191 | 2.4778 | 0.025786 | 0.027466 | -0.032043 | 0.009155 | 0.059509 | 0.027466 | 0.054932 | -0.064087 | 0.032043 | 0.064087 | -0.059509 | -0.050354 | -0.013733 | 0.086975 | 0.013733 | 38.0951 | 37.9761 | -83.3221 | 38.0081 | 38.0997 | 0.1236 | -83.3221 | 38.1271 | 38.0539 | -83.4 | 38.0722 | 37.9807 | -0.073242 | -83.3633 | 38.0676 | 38.0676 | 38.0493 | -83.4137 | 37.9898 | 38.0264 | 38.1042 | -83.3359
3044.6875 | 121.6827 | -37.1658 | 84.1919 | -0.020218 | 0.0089273 | 0.016267 | -3.4178e-05 | 0.0308 | -0.0024951 | -0.045891 | -0.0054932 | 0.0074789 | -0.015488 | 0.00010471 | 2.5511 | 0.028777 | 0.004578 | 0.022888 | 0.059509 | 0.082397 | 0.018311 | 0.059509 | -0.050354 | -0.036621 | 0.064087 | -0.068665 | -0.032043 | -0.027466 | 0.082397 | 0.022888 | 37.2253 | 37.1155 | -84.1736 | 37.1887 | 37.2482 | 0.13275 | -84.1873 | 37.2482 | 37.1887 | -84.2239 | 37.1292 | 37.0972 | -0.091553 | -84.2194 | 37.1841 | 37.1704 | 37.2253 | -84.2422 | 37.1338 | 37.1384 | 37.2299 | -84.169
3046.4688 | 121.6553 | -36.7996 | 84.5856 | -0.012589 | 0.0099953 | 0.016908 | -0.0011024 | 0.031868 | -0.0035633 | -0.048668 | -0.0054932 | 0.01047 | -0.014206 | -0.00096349 | 2.5649 | 0.029418 | 0.004578 | 0.027466 | 0.050354 | 0.09613 | 0 | 0.059509 | -0.036621 | -0.018311 | 0.068665 | -0.064087 | -0.045776 | -0.022888 | 0.086975 | 0.027466 | 36.8591 | 36.763 | -84.5856 | 36.8271 | 36.8958 | 0.13275 | -84.581 | 36.8866 | 36.8271 | -84.6313 | 36.7813 | 36.7355 | -0.091553 | -84.6085 | 36.7996 | 36.8042 | 36.85 | -84.6222 | 36.7538 | 36.7767 | 36.8683 | -84.5581
3048.25 | 121.5958 | -35.8154 | 85.6567 | -0.012589 | 0.014695 | 0.016908 | 0.002102 | 0.035713 | 0.0049817 | -0.048027 | -0.020752 | 0.01346 | -0.014633 | 0.00031831 | 2.5284 | 0.026214 | -0.027466 | -0.059509 | -0.027466 | 0.041199 | 0.032043 | 0.027466 | -0.10071 | -0.073242 | 0.013733 | -0.13733 | 0.013733 | 0.013733 | 0.045776 | -0.009155 | 35.8429 | 35.7147 | -85.6247 | 35.7559 | 35.8566 | 0.14191 | -85.6842 | 35.8612 | 35.8063 | -85.643 | 35.7422 | 35.6781 | -0.12817 | -85.643 | 35.8475 | 35.788 | 35.788 | -85.7574 | 35.8292 | 35.8292 | 35.8292 | -85.6659
3049.9688 | 121.637 | -35.8429 | 85.524 | -0.0049592 | 0.0082865 | 0.014772 | 0.00060662 | 0.031227 | 0.00070927 | -0.042686 | -0.0054932 | 0.01111 | -0.01442 | 0.0018137 | 2.4274 | 0.028777 | 0.068665 | 0.073242 | 0.10071 | 0.12817 | -0.009155 | 0.073242 | -0.041199 | 0.045776 | 0.12817 | -0.018311 | -0.059509 | -0.036621 | 0.07782 | 0.032043 | 35.9161 | 35.8017 | -85.5331 | 35.9161 | 35.9711 | 0.16937 | -85.4553 | 35.9207 | 35.8749 | -85.5835 | 35.8887 | 35.8246 | -0.050354 | -85.5606 | 35.8337 | 35.9116 | 35.9436 | -85.5652 | 35.7834 | 35.8063 | 35.9711 | -85.4919
3051.75 | 121.5637 | -35.4721 | 85.9726 | -0.012589 | 0.019822 | 0.019258 | 0.0023156 | 0.031441 | 0.0056225 | -0.045463 | 0.0021363 | 0.011965 | -0.011642 | -0.0011771 | 2.5218 | 0.028136 | -0.050354 | -0.09613 | -0.041199 | 0.027466 | 0.045776 | 0.009155 | -0.068665 | -0.045776 | -0.027466 | -0.16937 | -0.004578 | 0.004578 | 0.054932 | -0.009155 | 35.4813 | 35.4034 | -85.9268 | 35.376 | 35.4996 | 0.096131 | -86.0229 | 35.527 | 35.463 | -85.9772 | 35.4263 | 35.3027 | -0.16022 | -85.968 | 35.5179 | 35.4218 | 35.4309 | -86.0413 | 35.4675 | 35.4767 | 35.4446 | -85.9818
3053.5 | 121.637 | -34.9823 | 86.3892 | -0.012589 | 0.011918 | 0.016481 | -3.4178e-05 | 0.031441 | 0.00028207 | -0.045463 | -0.013123 | 0.0096151 | -0.015701 | -0.0011771 | 2.5068 | 0.02835 | 0.041199 | 0.07782 | 0.10529 | 0.11444 | -0.004578 | 0.068665 | -0.036621 | 0.022888 | 0.12817 | -0.018311 | -0.050354 | -0.041199 | 0.091553 | 0.022888 | 35.051 | 34.9457 | -86.3937 | 35.0601 | 35.0967 | 0.15106 | -86.348 | 35.0739 | 35.0052 | -86.4395 | 35.0052 | 34.964 | -0.041199 | -86.4304 | 34.9777 | 35.0235 | 35.0876 | -86.4258 | 34.9319 | 34.9411 | 35.1105 | -86.3663
3055.2969 | 121.6782 | -34.5428 | 86.8469 | -0.012589 | 0.015336 | 0.014986 | -0.00024778 | 0.031441 | -0.00099973 | -0.043327 | -0.013123 | 0.01047 | -0.012497 | 0.00053191 | 2.5073 | 0.02835 | 0.045776 | 0.068665 | 0.07782 | 0.12817 | 0.018311 | 0.064087 | -0.050354 | 0.059509 | 0.1236 | -0.027466 | -0.059509 | -0.036621 | 0.10071 | 0.013733 | 34.6069 | 34.4925 | -86.8286 | 34.6115 | 34.671 | 0.17853 | -86.8011 | 34.6436 | 34.5566 | -86.9064 | 34.6024 | 34.5154 | -0.041199 | -86.8835 | 34.5612 | 34.5886 | 34.6207 | -86.8973 | 34.4833 | 34.5062 | 34.6664 | -86.8332
3057.0781 | 121.5591 | -34.5062 | 86.9568 | -0.012589 | 0.014909 | 0.016054 | 0.00082022 | 0.032936 | 0.0056225 | -0.044182 | -0.0054932 | 0.010042 | -0.012497 | 0.00031831 | 2.5464 | 0.026214 | -0.027466 | -0.054932 | -0.013733 | 0.036621 | 0.022888 | 0.032043 | -0.073242 | -0.054932 | -0.022888 | -0.17853 | -0.018311 | -0.009155 | 0.045776 | -0.013733 | 34.5383 | 34.433 | -86.9339 | 34.4513 | 34.5428 | 0.10986 | -86.9843 | 34.552 | 34.4925 | -86.9751 | 34.4513 | 34.3277 | -0.16479 | -86.9659 | 34.5291 | 34.4788 | 34.4925 | -87.03 | 34.4879 | 34.4971 | 34.4833 | -86.9705
3058.8594 | 121.5683 | -34.3735 | 87.0895 | -0.0049592 | 0.015336 | 0.018617 | 0.0053064 | 0.031227 | 0.00049567 | -0.046959 | -0.013123 | 0.0098289 | -0.011856 | -0.00032249 | 2.534 | 0.028564 | -0.064087 | -0.022888 | -0.022888 | 0.036621 | 0.054932 | 0.027466 | -0.09613 | -0.10529 | 0 | -0.13733 | 0 | 0.018311 | 0.041199 | -0.004578 | 34.4009 | 34.2773 | -87.0346 | 34.3506 | 34.4101 | 0.13275 | -87.1536 | 34.4147 | 34.3689 | -87.0895 | 34.2682 | 34.2361 | -0.13275 | -87.0712 | 34.4284 | 34.3094 | 34.3506 | -87.1857 | 34.3735 | 34.3918 | 34.3735 | -87.0941
3060.5625 | 121.5683 | -34.4604 | 86.9934 | -0.0049592 | 0.018327 | 0.017336 | 0.0012476 | 0.033577 | 0.0043409 | -0.041618 | -0.013123 | 0.012819 | -0.012711 | -0.00096349 | 2.4509 | 0.028777 | 0 | 0.018311 | 0.018311 | 0.082397 | 0.022888 | 0.036621 | -0.073242 | 0 | 0.064087 | -0.091553 | -0.013733 | -0.013733 | 0.064087 | -0.004578 | 34.4971 | 34.3872 | -86.9705 | 34.4788 | 34.5428 | 0.15564 | -86.9934 | 34.5245 | 34.4559 | -87.0071 | 34.4604 | 34.3689 | -0.086975 | -87.0071 | 34.4833 | 34.4604 | 34.4788 | -87.0666 | 34.4467 | 34.4467 | 34.5245 | -86.998
3062.3438 | 121.6736 | -33.7784 | 87.5839 | -0.012589 | 0.012559 | 0.016267 | -3.4178e-05 | 0.0308 | 0.00028207 | -0.044609 | 0.0021363 | 0.0098289 | -0.01506 | 0.0022409 | 2.497 | 0.02835 | -0.032043 | -0.036621 | 0.004578 | 0.050354 | 0.036621 | 0.041199 | -0.068665 | 0 | 0.064087 | -0.073242 | -0.036621 | -0.013733 | 0.082397 | 0.022888 | 33.8196 | 33.7097 | -87.5473 | 33.7418 | 33.8287 | 0.11902 | -87.616 | 33.8608 | 33.8013 | -87.6205 | 33.7784 | 33.7051 | -0.09613 | -87.5977 | 33.815 | 33.7463 | 33.783 | -87.6526 | 33.7418 | 33.7646 | 33.8425 | -87.561
3064.125 | 121.669 | -33.2611 | 88.0829 | -0.0049592 | 0.01085 | 0.017336 | -0.00067498 | 0.029305 | -0.0018543 | -0.04525 | -0.013123 | 0.0094015 | -0.012283 | 0.00031831 | 2.4887 | 0.02835 | 0.004578 | 0.018311 | 0.032043 | 0.091553 | 0.013733 | 0.050354 | -0.050354 | 0.018311 | 0.091553 | -0.045776 | -0.045776 | -0.036621 | 0.07782 | 0.041199 | 33.3115 | 33.2108 | -88.0692 | 33.2794 | 33.3527 | 0.14191 | -88.0783 | 33.3389 | 33.3023 | -88.1287 | 33.2794 | 33.2153 | -0.086975 | -88.1195 | 33.2748 | 33.2657 | 33.2932 | -88.1332 | 33.2153 | 33.2245 | 33.3527 | -88.0417
3065.9062 | 121.5866 | -32.2632 | 89.1403 | -0.012589 | 0.015763 | 0.017336 | 0.0031702 | 0.033364 | 0.00049567 | -0.04525 | -0.013123 | 0.011751 | -0.014633 | -0.00010889 | 2.5021 | 0.027068 | -0.050354 | -0.068665 | -0.018311 | 0.064087 | 0.041199 | 0.009155 | -0.07782 | -0.073242 | 0.018311 | -0.13733 | -0.018311 | 0.009155 | 0.041199 | 0.004578 | 32.2723 | 32.1854 | -89.0991 | 32.1945 | 32.3273 | 0.14191 | -89.1907 | 32.3044 | 32.2678 | -89.1586 | 32.1899 | 32.1259 | -0.14191 | -89.1312 | 32.3044 | 32.2128 | 32.2449 | -89.2181 | 32.2449 | 32.2723 | 32.2815 | -89.1357
3067.6719 | 121.5454 | -31.5399 | 89.9094 | -0.012589 | 0.01555 | 0.016695 | 0.0016748 | 0.031655 | 0.0028455 | -0.04525 | -0.013123 | 0.011538 | -0.015274 | -0.00074989 | 2.5004 | 0.027068 | 0.009155 | 0.018311 | 0.027466 | 0.082397 | 0.027466 | 0.036621 | -0.07782 | -0.027466 | 0.054932 | -0.10986 | -0.013733 | -0.018311 | 0.082397 | -0.009155 | 31.5765 | 31.4621 | -89.8819 | 31.5582 | 31.6223 | 0.16022 | -89.9002 | 31.6223 | 31.5308 | -89.9231 | 31.5125 | 31.4301 | -0.10071 | -89.9277 | 31.5674 | 31.5491 | 31.5674 | -89.9872 | 31.5262 | 31.5216 | 31.5948 | -89.9185
3069.3906 | 121.6507 | -30.9769 | 90.3854 | -0.012589 | 0.016831 | 0.016908 | -0.00067498 | 0.032936 | -0.00014533 | -0.043327 | -0.0054932 | 0.0096151 | -0.015915 | -0.0016043 | 2.4203 | 0.028564 | -0.054932 | -0.068665 | -0.027466 | 0.032043 | 0.036621 | 0.032043 | -0.07782 | -0.068665 | -0.004578 | -0.11902 | -0.032043 | -0.013733 | 0.045776 | 0.004578 | 31.0089 | 30.899 | -90.3488 | 30.9082 | 31.0089 | 0.10986 | -90.4404 | 31.0226 | 30.9814 | -90.4175 | 30.9082 | 30.8578 | -0.1236 | -90.3992 | 31.0135 | 30.9219 | 30.9494 | -90.4633 | 30.9448 | 30.9631 | 30.9723 | -90.3809
3071.1875 | 121.5225 | -30.5969 | 90.8478 | -0.012589 | 0.01555 | 0.016908 | -0.00024778 | 0.031441 | 0.0032727 | -0.045891 | -0.013123 | 0.013888 | -0.013565 | 0.00074551 | 2.4205 | 0.027709 | -0.045776 | -0.068665 | -0.032043 | 0.059509 | 0.027466 | 0.018311 | -0.086975 | -0.073242 | -0.018311 | -0.17853 | -0.027466 | -0.004578 | 0.054932 | -0.018311 | 30.6152 | 30.5099 | -90.8203 | 30.5283 | 30.6564 | 0.14648 | -90.8936 | 30.6519 | 30.5786 | -90.8752 | 30.5237 | 30.4184 | -0.16022 | -90.8524 | 30.6244 | 30.5511 | 30.5649 | -90.9348 | 30.5695 | 30.5923 | 30.5786 | -90.8661
3072.9219 | 121.6553 | -30.2216 | 91.1179 | -0.020218 | 0.01085 | 0.019685 | 0.0044518 | 0.032723 | -0.0059131 | -0.046318 | -0.0054932 | 0.0059837 | -0.013992 | -0.0018179 | 2.541 | 0.028564 | -0.045776 | 0.009155 | 0.068665 | 0.082397 | 0.013733 | 0.059509 | -0.082397 | -0.050354 | 0.068665 | -0.041199 | -0.050354 | -0.013733 | 0.07782 | 0.004578 | 30.2811 | 30.1392 | -91.1041 | 30.2307 | 30.304 | 0.16479 | -91.1636 | 30.2994 | 30.2261 | -91.1682 | 30.1712 | 30.1804 | -0.045777 | -91.1316 | 30.2353 | 30.1758 | 30.2902 | -91.2003 | 30.1712 | 30.2078 | 30.2902 | -91.1133
3074.6875 | 121.5317 | -30.1987 | 91.2781 | -0.012589 | 0.011064 | 0.016267 | 0.0016748 | 0.0308 | -0.0018543 | -0.046318 | -0.013123 | 0.0096151 | -0.016342 | -0.00010889 | 2.4793 | 0.028991 | 0.004578 | 0.054932 | 0.10071 | 0.11444 | -0.013733 | 0.045776 | -0.050354 | -0.032043 | 0.11444 | -0.064087 | -0.041199 | -0.022888 | 0.073242 | 0.004578 | 30.2444 | 30.1483 | -91.2918 | 30.2536 | 30.3131 | 0.16479 | -91.2735 | 30.2719 | 30.2032 | -91.3193 | 30.1666 | 30.1346 | -0.068665 | -91.301 | 30.1849 | 30.2032 | 30.2994 | -91.3284 | 30.1575 | 30.1758 | 30.3131 | -91.2735
3076.4219 | 121.5179 | -30.1437 | 91.2964 | -0.020218 | 0.013841 | 0.016908 | -0.00046138 | 0.034004 | 0.0030591 | -0.04525 | -0.020752 | 0.011965 | -0.012924 | 0.00053191 | 2.5088 | 0.026427 | -0.009155 | -0.032043 | -0.004578 | 0.064087 | 0.032043 | 0.027466 | -0.064087 | -0.07782 | -0.009155 | -0.14648 | -0.027466 | -0.009155 | 0.064087 | -0.013733 | 30.1712 | 30.0797 | -91.2643 | 30.1117 | 30.2078 | 0.12817 | -91.3055 | 30.2078 | 30.13 | -91.3239 | 30.0659 | 29.9973 | -0.13275 | -91.3055 | 30.1758 | 30.1346 | 30.1392 | -91.3605 | 30.1163 | 30.1346 | 30.1346 | -91.3101
3078.2188 | 121.5271 | -29.2877 | 92.1524 | -0.012589 | 0.017259 | 0.017336 | -0.002384 | 0.033791 | 0.0024183 | -0.044395 | -0.0054932 | 0.010256 | -0.016129 | -0.00053629 | 2.5026 | 0.026855 | 0.018311 | 0 | 0.022888 | 0.064087 | 0.022888 | 0.022888 | -0.068665 | -0.018311 | 0.064087 | -0.10071 | -0.032043 | -0.013733 | 0.059509 | -0.004578 | 29.3106 | 29.2191 | -92.1295 | 29.2877 | 29.3518 | 0.13275 | -92.1341 | 29.3472 | 29.2831 | -92.1844 | 29.2694 | 29.187 | -0.09613 | -92.1661 | 29.3106 | 29.306 | 29.3106 | -92.2211 | 29.2557 | 29.274 | 29.3518 | -92.157
3080 | 121.6187 | -28.8437 | 92.5095 | -0.012589 | 0.011918 | 0.019045 | 0.0018884 | 0.035073 | -0.0018543 | -0.04525 | -0.0054932 | 0.011751 | -0.017197 | 0.00010471 | 2.5579 | 0.026855 | 0.050354 | 0.064087 | 0.10986 | 0.11902 | -0.032043 | 0.064087 | -0.032043 | 0.032043 | 0.11444 | -0.022888 | -0.050354 | -0.054932 | 0.082397 | 0.027466 | 28.9078 | 28.8116 | -92.5415 | 28.9078 | 28.9627 | 0.15106 | -92.4591 | 28.9261 | 28.8712 | -92.5598 | 28.8757 | 28.8208 | -0.050354 | -92.5644 | 28.8116 | 28.894 | 28.9536 | -92.5415 | 28.7933 | 28.7888 | 28.9581 | -92.482
3081.7812 | 121.5546 | -27.4612 | 93.956 | -0.012589 | 0.019395 | 0.016695 | 0.002102 | 0.031441 | 0.0039135 | -0.045036 | -0.0054932 | 0.013674 | -0.013138 | 0.00053191 | 2.4763 | 0.026427 | 0 | -0.018311 | 0.013733 | 0.073242 | 0.022888 | 0.032043 | -0.09613 | -0.041199 | 0.054932 | -0.10071 | -0.022888 | 0 | 0.059509 | -0.004578 | 27.4933 | 27.3651 | -93.9331 | 27.4429 | 27.5345 | 0.16937 | -93.956 | 27.5208 | 27.4567 | -93.9789 | 27.42 | 27.3605 | -0.09613 | -93.956 | 27.4841 | 27.4612 | 27.475 | -94.0521 | 27.4384 | 27.4612 | 27.5162 | -93.9606
3083.4844 | 121.6415 | -27.0538 | 94.3588 | -0.0049592 | 0.012345 | 0.017976 | 0.0048792 | 0.033364 | -0.0056995 | -0.046959 | -0.020752 | 0.0053427 | -0.013565 | -0.00053629 | 2.5353 | 0.02835 | 0.041199 | 0.091553 | 0.11444 | 0.11902 | 0 | 0.054932 | -0.050354 | 0.032043 | 0.17395 | 0 | -0.050354 | -0.032043 | 0.064087 | 0.027466 | 27.1088 | 27.0035 | -94.3588 | 27.1454 | 27.1729 | 0.16937 | -94.3176 | 27.1179 | 27.0813 | -94.4092 | 27.0859 | 27.0538 | -0.027466 | -94.3909 | 27.0538 | 27.095 | 27.1683 | -94.4092 | 27.0035 | 27.0218 | 27.2278 | -94.3314
3085.2656 | 121.5179 | -26.6556 | 94.812 | -0.020218 | 0.012986 | 0.019045 | 0.0014612 | 0.034004 | -0.0024951 | -0.046959 | 0.0021363 | 0.010042 | -0.013351 | -0.0022453 | 2.5432 | 0.024505 | 0.022888 | 0.068665 | 0.07782 | 0.11444 | -0.004578 | 0.073242 | -0.050354 | -0.013733 | 0.10986 | -0.059509 | -0.045776 | -0.022888 | 0.064087 | 0.013733 | 26.7288 | 26.6052 | -94.8166 | 26.7242 | 26.77 | 0.16479 | -94.7891 | 26.7197 | 26.6693 | -94.8578 | 26.6418 | 26.5961 | -0.073242 | -94.8349 | 26.651 | 26.6785 | 26.7334 | -94.8624 | 26.6098 | 26.6327 | 26.7654 | -94.7983
3087.0469 | 121.6141 | -26.5686 | 94.7891 | -0.0049592 | 0.0085001 | 0.018831 | 0.00017942 | 0.031868 | -0.0042041 | -0.047172 | -0.013123 | 0.0074789 | -0.016342 | -0.0028861 | 2.5353 | 0.029418 | -0.022888 | -0.004578 | 0.050354 | 0.07782 | 0 | 0.054932 | -0.054932 | -0.036621 | 0.054932 | -0.059509 | -0.064087 | -0.050354 | 0.068665 | 0.013733 | 26.6235 | 26.5137 | -94.7891 | 26.564 | 26.6464 | 0.13275 | -94.812 | 26.6373 | 26.5823 | -94.8532 | 26.532 | 26.5091 | -0.073242 | -94.8395 | 26.5686 | 26.5457 | 26.619 | -94.8441 | 26.5045 | 26.5183 | 26.6235 | -94.7754
3088.8281 | 121.6415 | -26.8982 | 94.455 | 0.0026703 | 0.01555 | 0.018404 | 0.00060662 | 0.031868 | -0.0027087 | -0.045463 | -0.0054932 | 0.0087607 | -0.015488 | -0.0020315 | 2.5021 | 0.029632 | -0.022888 | 0.004578 | 0.050354 | 0.068665 | -0.009155 | 0.045776 | -0.045776 | -0.036621 | 0.045776 | -0.068665 | -0.041199 | -0.013733 | 0.054932 | 0.009155 | 26.944 | 26.8524 | -94.4641 | 26.9028 | 26.9669 | 0.11444 | -94.4778 | 26.9531 | 26.9073 | -94.4962 | 26.8616 | 26.8295 | -0.07782 | -94.4687 | 26.889 | 26.8753 | 26.9485 | -94.5007 | 26.857 | 26.8845 | 26.944 | -94.4458
3090.5312 | 121.5408 | -26.6052 | 94.812 | -0.027847 | 0.018754 | 0.017122 | 0.001034 | 0.032723 | 0.0073315 | -0.045463 | -0.0054932 | 0.013247 | -0.010788 | -0.00032249 | 2.4853 | 0.025146 | 0.027466 | 0 | 0.027466 | 0.064087 | 0.018311 | 0.041199 | -0.064087 | 0 | 0.045776 | -0.11444 | -0.022888 | 0 | 0.027466 | -0.004578 | 26.6464 | 26.5411 | -94.7937 | 26.6052 | 26.6693 | 0.12817 | -94.7845 | 26.6327 | 26.6006 | -94.8349 | 26.6052 | 26.4908 | -0.10986 | -94.812 | 26.6235 | 26.6327 | 26.6327 | -94.8761 | 26.5823 | 26.6052 | 26.651 | -94.8166
3092.3281 | 121.463 | -47.3465 | 73.8007 | 0.0026703 | 0.0132 | 0.016054 | -0.00067498 | 0.032509 | 0.0022047 | -0.043754 | -0.013123 | 0.011538 | -0.013138 | 0.0013863 | 2.5346 | 0.027495 | -0.013733 | -0.045776 | 0.009155 | 0.059509 | 0.041199 | 0.041199 | -0.068665 | -0.027466 | 0.004578 | -0.082397 | -0.018311 | 0 | 0.073242 | 0.013733 | 47.3877 | 47.2778 | -73.7595 | 47.3007 | 47.406 | 0.12817 | -73.8144 | 47.4197 | 47.3602 | -73.819 | 47.319 | 47.2641 | -0.09613 | -73.8007 | 47.3877 | 47.3328 | 47.3557 | -73.8693 | 47.3282 | 47.3465 | 47.3511 | -73.7869
3094.0938 | 121.257 | -45.7809 | 75.3204 | -0.012589 | 0.0070047 | 0.016908 | -3.4178e-05 | 0.032936 | -0.0022815 | -0.045677 | -0.020752 | 0.0066245 | -0.01506 | -0.0030997 | 2.444 | 0.027495 | 0.064087 | 0.11444 | 0.1236 | 0.1236 | 0.009155 | 0.091553 | -0.036621 | 0.050354 | 0.16022 | -0.013733 | -0.032043 | -0.041199 | 0.10071 | 0.022888 | 45.8725 | 45.7443 | -75.3113 | 45.8954 | 45.9045 | 0.16022 | -75.2563 | 45.8817 | 45.8038 | -75.3525 | 45.8313 | 45.7672 | -0.036621 | -75.3616 | 45.7901 | 45.845 | 45.9045 | -75.3571 | 45.7489 | 45.7397 | 45.9412 | -75.2975
3095.7969 | 121.1609 | -49.7726 | 71.2509 | -0.012589 | 0.017259 | 0.01584 | 0.0044518 | 0.031868 | -0.00057253 | -0.047813 | -0.020752 | 0.011538 | -0.012283 | -0.0018179 | 2.5438 | 0.02835 | -0.032043 | -0.082397 | -0.022888 | 0.045776 | 0.045776 | 0.041199 | -0.091553 | -0.07782 | 0.022888 | -0.13275 | 0.009155 | 0.022888 | 0.041199 | -0.004578 | 49.8138 | 49.6811 | -71.2051 | 49.6902 | 49.8184 | 0.13733 | -71.283 | 49.8138 | 49.7681 | -71.2418 | 49.6948 | 49.6399 | -0.12817 | -71.228 | 49.8184 | 49.7406 | 49.7498 | -71.3425 | 49.7818 | 49.7955 | 49.7955 | -71.2555
3097.5781 | 121.2524 | -29.9789 | 91.9693 | -0.0049592 | 0.011277 | 0.015413 | -0.00088858 | 0.030586 | 0.0015637 | -0.043541 | -0.020752 | 0.0087607 | -0.014633 | -0.00096349 | 2.5361 | 0.02835 | 0.064087 | 0.073242 | 0.10071 | 0.13275 | 0.013733 | 0.068665 | -0.073242 | 0.041199 | 0.09613 | -0.027466 | -0.064087 | -0.041199 | 0.10071 | 0.022888 | 30.0476 | 29.9057 | -91.9556 | 30.0522 | 30.1117 | 0.20599 | -91.9052 | 30.0797 | 30.0018 | -92.0334 | 30.0201 | 29.9515 | -0.050354 | -92.0105 | 29.9927 | 30.043 | 30.0797 | -92.0425 | 29.9149 | 29.9377 | 30.0751 | -91.9464
3099.3438 | 121.0693 | -53.7186 | 67.1951 | -0.020218 | 0.011064 | 0.021181 | 0.0014612 | 0.034218 | -0.0042041 | -0.046745 | -0.028381 | 0.0072653 | -0.016129 | -0.0013907 | 2.5421 | 0.027923 | -0.027466 | 0.018311 | 0.059509 | 0.082397 | 0.018311 | 0.073242 | -0.054932 | -0.018311 | 0.082397 | -0.041199 | -0.022888 | -0.013733 | 0.091553 | 0.045776 | 53.7918 | 53.6636 | -67.1768 | 53.7369 | 53.801 | 0.13733 | -67.2226 | 53.8101 | 53.7643 | -67.218 | 53.7003 | 53.6774 | -0.086975 | -67.2089 | 53.7369 | 53.6911 | 53.7781 | -67.2501 | 53.6957 | 53.7048 | 53.801 | -67.1494
3101.0625 | 120.6299 | -79.6783 | 40.5991 | -0.012589 | 0.015336 | 0.017976 | 0.002102 | 0.031441 | 0.0041273 | -0.044822 | -0.0054932 | 0.01111 | -0.015274 | -0.00074989 | 2.5684 | 0.026855 | 0 | -0.009155 | 0.013733 | 0.086975 | 0.059509 | 0.064087 | -0.073242 | -0.013733 | 0.073242 | -0.10071 | 0.032043 | 0.009155 | 0.073242 | 0.022888 | 79.7424 | 79.6051 | -40.5396 | 79.6692 | 79.7653 | 0.16022 | -40.5991 | 79.7516 | 79.7012 | -40.567 | 79.6646 | 79.5776 | -0.1236 | -40.5899 | 79.7379 | 79.6783 | 79.6921 | -40.6723 | 79.7104 | 79.6875 | 79.7516 | -40.5762
3102.8594 | 120.2774 | -73.2651 | 46.8338 | -0.020218 | 0.015977 | 0.015413 | 0.00082022 | 0.032295 | 0.0024183 | -0.045677 | -0.0054932 | 0.010042 | -0.011215 | -0.00096349 | 2.581 | 0.027709 | -0.022888 | -0.027466 | -0.004578 | 0.082397 | 0.050354 | 0.054932 | -0.068665 | -0.018311 | 0.064087 | -0.09613 | 0.004578 | 0.004578 | 0.09613 | 0.013733 | 73.32 | 73.1964 | -46.7834 | 73.2376 | 73.3475 | 0.15106 | -46.8567 | 73.3612 | 73.2788 | -46.8292 | 73.2468 | 73.1689 | -0.10986 | -46.8292 | 73.3154 | 73.2422 | 73.2605 | -46.9025 | 73.2697 | 73.2697 | 73.3292 | -46.8201
3104.5781 | 120.0531 | -63.0341 | 57.2159 | 0.0026703 | 0.014695 | 0.014986 | 0.0029566 | 0.034859 | 0.0064771 | -0.0429 | -0.013123 | 0.012819 | -0.013351 | 0.0033089 | 2.6023 | 0.028136 | 0.018311 | -0.027466 | 0.027466 | 0.068665 | 0.050354 | 0.054932 | -0.059509 | -0.018311 | 0.027466 | -0.14191 | -0.009155 | 0 | 0.064087 | 0.009155 | 63.089 | 62.9745 | -57.1655 | 63.0066 | 63.1027 | 0.12817 | -57.1976 | 63.0981 | 63.0432 | -57.225 | 63.0157 | 62.8922 | -0.15106 | -57.2159 | 63.0844 | 63.0524 | 63.0615 | -57.2754 | 63.0249 | 63.0341 | 63.0615 | -57.2067
3106.375 | 119.1513 | -59.7702 | 59.3033 | -0.012589 | 0.013627 | 0.017763 | 0.0033838 | 0.03315 | -0.0018543 | -0.046318 | -0.0054932 | 0.0098289 | -0.012711 | -0.00074989 | 2.5848 | 0.028777 | -0.045776 | -0.027466 | -0.009155 | 0.045776 | 0.054932 | 0.022888 | -0.086975 | -0.07782 | 0.041199 | -0.13733 | 0 | 0.027466 | 0.064087 | 0 | 59.7931 | 59.6832 | -59.2484 | 59.7427 | 59.816 | 0.13275 | -59.3491 | 59.8343 | 59.7702 | -59.3033 | 59.6924 | 59.6329 | -0.13733 | -59.2758 | 59.8251 | 59.7244 | 59.761 | -59.3903 | 59.7702 | 59.7977 | 59.8114 | -59.3033
3108.0938 | 118.9041 | -68.7195 | 49.8825 | -0.012589 | 0.0072183 | 0.016908 | 0.00060662 | 0.032082 | -0.0056995 | -0.045463 | -0.0054932 | 0.0087607 | -0.017624 | -0.0024589 | 2.5938 | 0.0307 | 0.073242 | 0.09613 | 0.13275 | 0.14191 | 0.022888 | 0.073242 | -0.027466 | 0.045776 | 0.16479 | 0.036621 | -0.036621 | -0.009155 | 0.10986 | 0.036621 | 68.7927 | 68.692 | -49.8596 | 68.8156 | 68.8614 | 0.16937 | -49.8093 | 68.8293 | 68.7561 | -49.9191 | 68.7653 | 68.7561 | 0 | -49.8917 | 68.7424 | 68.7927 | 68.8522 | -49.91 | 68.6829 | 68.7103 | 68.8843 | -49.8459
3109.875 | 119.0094 | -61.9583 | 56.7947 | -0.012589 | 0.0132 | 0.016481 | 0.0033838 | 0.033577 | -0.0044177 | -0.046531 | -0.0054932 | 0.0055563 | -0.013565 | -0.0013907 | 2.3979 | 0.027495 | 0.082397 | 0.1236 | 0.16479 | 0.15106 | 0.004578 | 0.07782 | -0.027466 | 0.036621 | 0.19226 | 0.022888 | -0.041199 | -0.004578 | 0.11902 | 0.041199 | 62.0361 | 61.9308 | -56.7902 | 62.0819 | 62.1094 | 0.17853 | -56.7123 | 62.0773 | 61.9995 | -56.8359 | 61.9949 | 61.9812 | -0.018311 | -56.7993 | 61.9629 | 62.0407 | 62.1231 | -56.8222 | 61.9171 | 61.9537 | 62.1506 | -56.7535
3111.5938 | 117.8879 | -48.4863 | 69.5206 | -0.0049592 | 0.012559 | 0.017336 | 0.0023156 | 0.03315 | 0.00092287 | -0.045677 | -0.0054932 | 0.010256 | -0.014633 | 0.00010471 | 2.4833 | 0.027068 | 0 | -0.027466 | 0.022888 | 0.064087 | 0.041199 | 0.041199 | -0.073242 | -0.07782 | 0.027466 | -0.11902 | 0.004578 | 0.027466 | 0.064087 | 0 | 48.5275 | 48.4131 | -69.4794 | 48.4589 | 48.5504 | 0.13733 | -69.5206 | 48.5504 | 48.4863 | -69.516 | 48.4085 | 48.3673 | -0.11902 | -69.4931 | 48.5275 | 48.4863 | 48.5092 | -69.5938 | 48.4909 | 48.5138 | 48.5138 | -69.5206
3113.3906 | 118.4143 | -42.4713 | 75.7462 | -0.020218 | 0.012559 | 0.020326 | 0.0023156 | 0.033791 | -0.0031359 | -0.045677 | -0.013123 | 0.0066245 | -0.012924 | -0.00010889 | 2.3964 | 0.027495 | 0.054932 | 0.091553 | 0.11444 | 0.1236 | 0.018311 | 0.059509 | -0.045776 | 0.036621 | 0.16022 | 0.018311 | -0.041199 | -0.032043 | 0.07782 | 0.022888 | 42.5308 | 42.4255 | -75.7278 | 42.5629 | 42.5949 | 0.16937 | -75.6912 | 42.5491 | 42.4942 | -75.7874 | 42.5079 | 42.4896 | -0.004577 | -75.7782 | 42.4896 | 42.5262 | 42.5858 | -75.7919 | 42.4301 | 42.4393 | 42.6315 | -75.7233
3115.1094 | 117.4072 | -60.9375 | 56.0303 | -0.0049592 | 0.0093545 | 0.016481 | 0.00060662 | 0.029946 | -0.0018543 | -0.04525 | -0.0054932 | 0.0085471 | -0.01506 | -0.00096349 | 2.5831 | 0.028136 | 0.027466 | 0.032043 | 0.082397 | 0.10986 | 0.022888 | 0.068665 | -0.054932 | 0.018311 | 0.13733 | -0.013733 | -0.032043 | -0.013733 | 0.10986 | 0.018311 | 61.0062 | 60.8826 | -56.0074 | 60.9695 | 61.0474 | 0.16479 | -56.0028 | 61.0474 | 60.9558 | -56.0623 | 60.9558 | 60.9238 | -0.032044 | -56.044 | 60.9604 | 60.965 | 61.0199 | -56.0852 | 60.9055 | 60.9238 | 61.0748 | -56.012
3116.8906 | 116.9952 | -60.6125 | 56.0852 | -0.012589 | 0.015122 | 0.016695 | -0.0015296 | 0.032936 | 0.0066907 | -0.0429 | -0.013123 | 0.013247 | -0.014206 | 0.0018137 | 2.5331 | 0.024932 | 0.004578 | -0.07782 | -0.027466 | 0.059509 | 0.054932 | 0.045776 | -0.064087 | -0.032043 | -0.018311 | -0.16937 | 0.009155 | 0.018311 | 0.068665 | 0.009155 | 60.6583 | 60.5484 | -56.0303 | 60.5347 | 60.672 | 0.1236 | -56.0806 | 60.6812 | 60.6216 | -56.0761 | 60.5804 | 60.4431 | -0.17853 | -56.0669 | 60.6674 | 60.6171 | 60.585 | -56.1493 | 60.6216 | 60.6308 | 60.5942 | -56.0761
3118.5938 | 118.6569 | -67.9047 | 50.2029 | -0.012589 | 0.011704 | 0.017976 | -0.00024778 | 0.032295 | -0.0061267 | -0.047172 | -0.013123 | 0.0074789 | -0.012924 | -0.00032249 | 2.563 | 0.029204 | 0.032043 | 0.059509 | 0.10071 | 0.1236 | 0.027466 | 0.10071 | -0.036621 | 0.032043 | 0.14191 | 0.027466 | -0.032043 | -0.013733 | 0.1236 | 0.027466 | 68.0054 | 67.868 | -50.1755 | 67.9642 | 68.0283 | 0.16022 | -50.1709 | 68.0283 | 67.9321 | -50.235 | 67.9367 | 67.9321 | 0 | -50.2167 | 67.9321 | 67.9367 | 68.0054 | -50.2396 | 67.8726 | 67.8909 | 68.0466 | -50.1755
3120.375 | 117.778 | -64.7186 | 52.8122 | -0.012589 | 0.015336 | 0.019472 | -0.00046138 | 0.031227 | 0.00070927 | -0.047813 | -0.0054932 | 0.010256 | -0.014206 | -0.0011771 | 2.5374 | 0.026214 | -0.009155 | -0.036621 | -0.004578 | 0.059509 | 0.068665 | 0.036621 | -0.064087 | -0.064087 | 0.032043 | -0.1236 | 0.004578 | 0.032043 | 0.064087 | -0.004578 | 64.7552 | 64.6545 | -52.7435 | 64.682 | 64.7781 | 0.1236 | -52.8214 | 64.7827 | 64.7141 | -52.8076 | 64.6545 | 64.595 | -0.11902 | -52.7802 | 64.7873 | 64.7095 | 64.7141 | -52.8763 | 64.7232 | 64.7507 | 64.7507 | -52.8168
3122.1562 | 117.4255 | -41.5421 | 75.3296 | -0.012589 | 0.012986 | 0.017549 | -0.00067498 | 0.035073 | 0.0017773 | -0.045891 | -0.0054932 | 0.0094015 | -0.015488 | -0.00032249 | 2.4701 | 0.027495 | 0.091553 | 0.068665 | 0.10071 | 0.13275 | -0.004578 | 0.068665 | -0.027466 | 0.059509 | 0.11444 | -0.018311 | -0.054932 | -0.032043 | 0.10986 | 0.036621 | 41.6107 | 41.5146 | -75.3342 | 41.6107 | 41.6748 | 0.16022 | -75.238 | 41.6519 | 41.5787 | -75.3845 | 41.6016 | 41.5237 | -0.054932 | -75.3616 | 41.5375 | 41.6336 | 41.6428 | -75.3571 | 41.4871 | 41.51 | 41.6565 | -75.293
3123.875 | 118.158 | -4.9072 | 113.3835 | -0.0049592 | 0.015977 | 0.01584 | -0.00046138 | 0.031868 | 0.0056225 | -0.044182 | -0.013123 | 0.012606 | -0.013351 | -0.0011771 | 2.5252 | 0.027495 | -0.054932 | -0.10986 | -0.059509 | 0.013733 | 0.032043 | 0.009155 | -0.10529 | -0.086975 | -0.036621 | -0.19226 | -0.027466 | 0 | 0.050354 | -0.041199 | 4.9164 | 4.8019 | -113.3514 | 4.7974 | 4.921 | 0.11902 | -113.4384 | 4.9576 | 4.866 | -113.4109 | 4.8203 | 4.715 | -0.15106 | -113.3835 | 4.9393 | 4.8523 | 4.8477 | -113.4888 | 4.8798 | 4.9072 | 4.8706 | -113.4247
3125.6406 | 118.634 | -9.3704 | 109.2453 | 0.0026703 | 0.014909 | 0.018831 | -0.00024778 | 0.032509 | 0.00092287 | -0.043968 | -0.020752 | 0.0096151 | -0.013779 | -0.00010889 | 2.5425 | 0.028564 | -0.041199 | -0.050354 | -0.013733 | 0.036621 | 0.018311 | 0.041199 | -0.073242 | -0.022888 | 0.050354 | -0.086975 | -0.045776 | -0.045776 | 0.050354 | 0.009155 | 9.4116 | 9.2972 | -109.227 | 9.3201 | 9.407 | 0.10986 | -109.2865 | 9.4208 | 9.3796 | -109.2911 | 9.3475 | 9.2834 | -0.09613 | -109.2911 | 9.3887 | 9.3292 | 9.3567 | -109.3185 | 9.3246 | 9.3246 | 9.4208 | -109.2361
3127.3438 | 117.3706 | -24.0189 | 93.1183 | -0.0049592 | 0.0074319 | 0.019258 | 0.0014612 | 0.031014 | -0.0029223 | -0.044609 | -0.0054932 | 0.0076925 | -0.015488 | -0.0013907 | 2.5303 | 0.030486 | 0.022888 | 0.064087 | 0.091553 | 0.10986 | -0.013733 | 0.045776 | -0.054932 | -0.013733 | 0.091553 | -0.041199 | -0.050354 | -0.032043 | 0.091553 | 0.013733 | 24.0646 | 23.9639 | -93.132 | 24.0829 | 24.1287 | 0.16479 | -93.0954 | 24.1104 | 24.0326 | -93.1686 | 24.0051 | 23.9777 | -0.054932 | -93.1503 | 24.0051 | 24.0417 | 24.1104 | -93.1732 | 23.9685 | 23.9868 | 24.1104 | -93.1046
3129.1406 | 117.7185 | -20.8511 | 97.1924 | -0.012589 | 0.014695 | 0.017763 | 0.0027428 | 0.034432 | 0.00028207 | -0.043968 | 0.0021363 | 0.010042 | -0.012711 | -0.0011771 | 2.4827 | 0.027923 | -0.064087 | -0.059509 | -0.027466 | 0.032043 | 0.036621 | 0.022888 | -0.086975 | -0.09613 | 0.013733 | -0.14648 | -0.013733 | -0.013733 | 0.027466 | -0.032043 | 20.874 | 20.7642 | -97.1558 | 20.7916 | 20.8832 | 0.11902 | -97.2565 | 20.8786 | 20.8191 | -97.2061 | 20.755 | 20.7047 | -0.11444 | -97.2061 | 20.8878 | 20.787 | 20.8237 | -97.2794 | 20.8374 | 20.8374 | 20.8649 | -97.2244
3130.9375 | 117.6361 | -12.973 | 104.3976 | -0.012589 | 0.011277 | 0.014772 | 0.0031702 | 0.029732 | -0.00078613 | -0.045891 | -0.0054932 | 0.0076925 | -0.013351 | -0.00053629 | 2.4387 | 0.028564 | 0.041199 | 0.059509 | 0.082397 | 0.11444 | -0.027466 | 0.050354 | -0.054932 | 0.013733 | 0.086975 | -0.032043 | -0.073242 | -0.050354 | 0.091553 | 0.004578 | 13.0234 | 12.9181 | -104.425 | 13.0325 | 13.0875 | 0.16937 | -104.3564 | 13.0646 | 12.9776 | -104.4708 | 12.9868 | 12.941 | -0.036621 | -104.4479 | 12.9456 | 13.0142 | 13.0554 | -104.4525 | 12.8998 | 12.9227 | 13.06 | -104.393
3132.6562 | 116.7389 | -21.9818 | 94.4778 | -0.012589 | 0.0179 | 0.013277 | 0.00039302 | 0.034645 | 0.0049817 | -0.044822 | -0.013123 | 0.012179 | -0.013351 | 0.00095911 | 2.4742 | 0.024505 | 0.018311 | -0.004578 | 0.009155 | 0.091553 | 0.022888 | 0.013733 | -0.09613 | -0.013733 | 0.054932 | -0.10071 | -0.041199 | -0.009155 | 0.054932 | 0 | 21.9955 | 21.8857 | -94.455 | 21.9772 | 22.0734 | 0.18768 | -94.4595 | 22.0367 | 21.9818 | -94.519 | 21.9681 | 21.8811 | -0.10071 | -94.487 | 22.0047 | 22.0001 | 21.991 | -94.574 | 21.9406 | 21.9727 | 22.0367 | -94.4778
3134.4219 | 118.4326 | -6.4316 | 111.9965 | -0.0049592 | 0.016831 | 0.014131 | -0.0011024 | 0.031868 | 0.0028455 | -0.045036 | -0.0054932 | 0.011324 | -0.011642 | 0.00095911 | 2.4566 | 0.026214 | -0.054932 | -0.10071 | -0.045776 | 0.032043 | 0.022888 | 0.018311 | -0.10529 | -0.10071 | -0.045776 | -0.19684 | -0.018311 | -0.013733 | 0.032043 | -0.018311 | 6.4499 | 6.3263 | -111.9736 | 6.3309 | 6.4636 | 0.13733 | -112.0514 | 6.4636 | 6.4133 | -112.0148 | 6.3309 | 6.2347 | -0.17853 | -112.0102 | 6.4545 | 6.3766 | 6.3858 | -112.1017 | 6.4133 | 6.4178 | 6.3858 | -112.0148
3136.2031 | 117.6636 | -13.3026 | 103.894 | -0.020218 | 0.012773 | 0.017976 | 0.003811 | 0.035286 | -0.0067675 | -0.043968 | -0.013123 | 0.0064109 | -0.013565 | 0.00031831 | 2.512 | 0.029632 | -0.032043 | -0.018311 | 0.045776 | 0.059509 | 0.004578 | 0.041199 | -0.064087 | -0.045776 | 0.068665 | -0.073242 | -0.045776 | -0.036621 | 0.073242 | 0.004578 | 13.3438 | 13.2385 | -103.8895 | 13.2843 | 13.3621 | 0.1236 | -103.9261 | 13.3759 | 13.3072 | -103.9398 | 13.2568 | 13.2294 | -0.07782 | -103.9307 | 13.3072 | 13.2706 | 13.3484 | -103.9581 | 13.2568 | 13.266 | 13.3713 | -103.8895
3137.9844 | 118.5974 | -5.5252 | 112.8983 | 0.0103 | 0.013627 | 0.016908 | 0.00017942 | 0.034004 | -0.00099973 | -0.045677 | 0.0097658 | 0.0098289 | -0.015701 | -0.0022453 | 2.5466 | 0.028136 | 0.032043 | 0.027466 | 0.068665 | 0.10986 | -0.013733 | 0.059509 | -0.045776 | 0.022888 | 0.10071 | -0.050354 | -0.07782 | -0.045776 | 0.073242 | 0.018311 | 5.5847 | 5.4794 | -112.912 | 5.5527 | 5.6351 | 0.15564 | -112.8662 | 5.5984 | 5.5435 | -112.9761 | 5.5481 | 5.4749 | -0.068665 | -112.944 | 5.5115 | 5.5573 | 5.5939 | -112.944 | 5.4474 | 5.4794 | 5.6259 | -112.8799
3139.7031 | 119.1834 | -0.58594 | 118.5791 | -0.012589 | 0.0132 | 0.018617 | 0.0027428 | 0.031441 | -0.0024951 | -0.044609 | -0.020752 | 0.0059837 | -0.015488 | -0.0022453 | 2.5276 | 0.025146 | 0.013733 | 0.073242 | 0.09613 | 0.09613 | -0.027466 | 0.041199 | -0.064087 | 0.018311 | 0.15564 | -0.018311 | -0.073242 | -0.050354 | 0.059509 | 0.013733 | 0.62714 | 0.52185 | -118.6066 | 0.65918 | 0.68207 | 0.16022 | -118.5654 | 0.64545 | 0.59967 | -118.6523 | 0.60425 | 0.56763 | -0.032044 | -118.6295 | 0.55847 | 0.59967 | 0.68207 | -118.6432 | 0.5127 | 0.53558 | 0.74158 | -118.5654
3141.5 | 119.2383 | -0.54474 | 118.7988 | -0.0049592 | 0.019609 | 0.017549 | 0.0040246 | 0.033791 | 0.00070927 | -0.045463 | -0.0054932 | 0.01047 | -0.012497 | 0.00053191 | 2.5098 | 0.027923 | -0.064087 | -0.050354 | -0.022888 | 0.022888 | 0.022888 | 0.009155 | -0.09613 | -0.091553 | 0.022888 | -0.13275 | -0.022888 | 0 | 0.018311 | -0.032043 | 0.55389 | 0.44861 | -118.7759 | 0.49438 | 0.56763 | 0.11902 | -118.8629 | 0.56305 | 0.5127 | -118.8217 | 0.45319 | 0.41199 | -0.10071 | -118.7988 | 0.56763 | 0.48065 | 0.52185 | -118.895 | 0.52185 | 0.54474 | 0.56763 | -118.8309
3143.2188 | 119.3619 | -0.73242 | 118.5104 | -0.020218 | 0.0132 | 0.014345 | -0.0017432 | 0.030159 | 0.0019909 | -0.044822 | -0.013123 | 0.01111 | -0.013779 | 0.0016001 | 2.4432 | 0.026214 | -0.036621 | -0.07782 | -0.045776 | 0.018311 | 0.018311 | 0.013733 | -0.10986 | -0.073242 | -0.032043 | -0.15106 | -0.045776 | -0.018311 | 0.045776 | -0.018311 | 0.74616 | 0.62256 | -118.4921 | 0.6546 | 0.75073 | 0.12817 | -118.5471 | 0.7782 | 0.71411 | -118.5562 | 0.65918 | 0.58136 | -0.13275 | -118.5287 | 0.75073 | 0.6958 | 0.68665 | -118.6203 | 0.68665 | 0.71411 | 0.70038 | -118.5287
3145 | 119.5129 | -0.48523 | 118.8995 | -0.0049592 | 0.012773 | 0.015627 | 0.0018884 | 0.032723 | 0.0026319 | -0.044609 | -0.0054932 | 0.011965 | -0.012711 | 0.0016001 | 2.5229 | 0.027068 | -0.032043 | -0.073242 | -0.032043 | 0.036621 | 0.022888 | 0.022888 | -0.10529 | -0.032043 | 0.018311 | -0.10986 | -0.036621 | -0.036621 | 0.045776 | 0.009155 | 0.50812 | 0.37994 | -118.8766 | 0.41199 | 0.52185 | 0.14191 | -118.9316 | 0.53101 | 0.49438 | -118.9362 | 0.45319 | 0.37537 | -0.11902 | -118.9362 | 0.50812 | 0.45319 | 0.45319 | -119.0048 | 0.44861 | 0.44861 | 0.50354 | -118.8904
3146.7812 | 119.5541 | -0.48981 | 118.9407 | -0.012589 | 0.012986 | 0.018617 | 0.0050928 | 0.03315 | -0.0048449 | -0.046318 | -0.0054932 | 0.0061973 | -0.01442 | -0.0022453 | 2.4257 | 0.029204 | 0.032043 | 0.073242 | 0.10071 | 0.10071 | -0.018311 | 0.036621 | -0.064087 | 0.009155 | 0.14648 | 0.004578 | -0.068665 | -0.054932 | 0.086975 | 0 | 0.52643 | 0.42572 | -118.959 | 0.56305 | 0.59052 | 0.1648 | -118.9087 | 0.57678 | 0.48981 | -119.0094 | 0.49896 | 0.49439 | 0.004578 | -118.9957 | 0.4715 | 0.52185 | 0.59052 | -119.0048 | 0.42114 | 0.43488 | 0.63629 | -118.9407
3148.5 | 119.2932 | -2.742 | 116.4688 | -0.0049592 | 0.014054 | 0.019045 | -0.00046138 | 0.032509 | -0.00057253 | -0.045891 | -0.0054932 | 0.0087607 | -0.01506 | -0.0011771 | 2.5182 | 0.030059 | 0 | 0.013733 | 0.064087 | 0.068665 | -0.018311 | 0.054932 | -0.064087 | -0.041199 | 0.041199 | -0.07782 | -0.054932 | -0.045776 | 0.068665 | 0.004578 | 2.7969 | 2.6779 | -116.4871 | 2.7557 | 2.8107 | 0.13275 | -116.4688 | 2.8107 | 2.7466 | -116.5237 | 2.7008 | 2.6642 | -0.082398 | -116.5146 | 2.7237 | 2.742 | 2.8061 | -116.5329 | 2.6871 | 2.6962 | 2.7832 | -116.4642
3150.2812 | 119.5999 | -0.72784 | 118.8263 | -0.012589 | 0.014695 | 0.017336 | 0.0018884 | 0.032936 | -0.0024951 | -0.046318 | -0.020752 | 0.0098289 | -0.01506 | -0.0011771 | 2.6062 | 0.026427 | 0.045776 | 0.050354 | 0.10529 | 0.10071 | -0.022888 | 0.045776 | -0.07782 | 0.018311 | 0.14191 | -0.022888 | -0.059509 | -0.054932 | 0.064087 | 0.022888 | 0.77362 | 0.65002 | -118.8492 | 0.7782 | 0.82855 | 0.17853 | -118.7805 | 0.79193 | 0.75073 | -118.8858 | 0.74616 | 0.70496 | -0.045776 | -118.8812 | 0.70496 | 0.77362 | 0.83313 | -118.9041 | 0.66834 | 0.67291 | 0.86975 | -118.8034
3152.0469 | 119.6365 | -0.5127 | 119.0552 | -0.012589 | 0.013627 | 0.016695 | 0.0029566 | 0.032723 | -0.0012133 | -0.046959 | 0.0021363 | 0.0083335 | -0.01506 | -0.00053629 | 2.6337 | 0.026855 | 0.059509 | 0.059509 | 0.091553 | 0.09613 | -0.022888 | 0.032043 | -0.086975 | 0.009155 | 0.14191 | -0.036621 | -0.059509 | -0.059509 | 0.054932 | 0.013733 | 0.54474 | 0.42572 | -119.0781 | 0.5722 | 0.60882 | 0.1831 | -118.9957 | 0.56763 | 0.52643 | -119.1147 | 0.52185 | 0.47607 | -0.050354 | -119.1147 | 0.48981 | 0.5722 | 0.60425 | -119.1422 | 0.45319 | 0.45319 | 0.6546 | -119.0414
3153.8281 | 119.6136 | -0.59967 | 119.0826 | -0.012589 | 0.016618 | 0.014558 | -0.0021704 | 0.033791 | 0.0071179 | -0.043754 | -0.013123 | 0.012179 | -0.013992 | 0.0016001 | 2.6149 | 0.024932 | -0.045776 | -0.1236 | -0.064087 | 0.018311 | 0.022888 | 0.013733 | -0.09613 | -0.091553 | -0.050354 | -0.21057 | -0.027466 | -0.009155 | 0.036621 | -0.018311 | 0.6134 | 0.50354 | -119.0598 | 0.47607 | 0.61798 | 0.11444 | -119.1284 | 0.63629 | 0.58136 | -119.1101 | 0.50812 | 0.3891 | -0.19226 | -119.0918 | 0.62256 | 0.55389 | 0.53558 | -119.1788 | 0.5722 | 0.59052 | 0.54932 | -119.101
3155.6094 | 119.7739 | -0.60425 | 118.9957 | -0.012589 | 0.014909 | 0.016908 | -0.0019568 | 0.032509 | 0.0013501 | -0.044822 | -0.0054932 | 0.0091879 | -0.016342 | 0.0011727 | 2.4665 | 0.026 | 0.022888 | 0.013733 | 0.054932 | 0.09613 | -0.013733 | 0.054932 | -0.068665 | 0.018311 | 0.09613 | -0.041199 | -0.068665 | -0.059509 | 0.064087 | 0.018311 | 0.65918 | 0.53558 | -119.0094 | 0.61798 | 0.70038 | 0.16479 | -118.9728 | 0.66834 | 0.62256 | -119.0643 | 0.62256 | 0.56305 | -0.05951 | -119.0552 | 0.59052 | 0.62714 | 0.65918 | -119.0643 | 0.53558 | 0.54474 | 0.70038 | -118.9774
3157.3906 | 119.7876 | -0.64545 | 119.0277 | -0.012589 | 0.01085 | 0.020113 | 0.0014612 | 0.032509 | -0.0039905 | -0.043113 | -0.013123 | 0.0066245 | -0.014206 | -0.0018179 | 2.5782 | 0.02835 | -0.013733 | -0.004578 | 0.036621 | 0.054932 | -0.013733 | 0.054932 | -0.082397 | -0.054932 | 0.041199 | -0.082397 | -0.059509 | -0.036621 | 0.068665 | -0.004578 | 0.70038 | 0.56305 | -119.0414 | 0.64087 | 0.70038 | 0.13733 | -119.0414 | 0.71411 | 0.64087 | -119.0872 | 0.59052 | 0.56305 | -0.077819 | -119.0643 | 0.63171 | 0.63171 | 0.68207 | -119.1101 | 0.58594 | 0.60883 | 0.68665 | -119.0323
3159.125 | 119.8059 | -1.0757 | 118.5837 | -0.012589 | 0.016191 | 0.017763 | -0.0021704 | 0.032936 | 0.0013501 | -0.043113 | -0.013123 | 0.0091879 | -0.015488 | -0.0022453 | 2.6532 | 0.028136 | 0.009155 | -0.027466 | 0.004578 | 0.064087 | -0.009155 | 0.045776 | -0.073242 | 0.018311 | 0.064087 | -0.068665 | -0.082397 | -0.041199 | 0.064087 | 0.009155 | 1.1215 | 1.0025 | -118.5928 | 1.0483 | 1.1398 | 0.13733 | -118.5745 | 1.1398 | 1.0849 | -118.6661 | 1.0941 | 1.0071 | -0.07782 | -118.6249 | 1.0666 | 1.0849 | 1.0803 | -118.6569 | 0.99335 | 1.0345 | 1.1398 | -118.5745
3160.8906 | 119.6091 | -1.7807 | 117.9153 | -0.0049592 | 0.0132 | 0.019899 | 0.0012476 | 0.032509 | 0.0011365 | -0.04525 | -0.013123 | 0.010256 | -0.01442 | -0.00053629 | 2.4782 | 0.028777 | -0.073242 | -0.050354 | -0.032043 | 0.004578 | 0.018311 | 0 | -0.09613 | -0.10986 | 0 | -0.15564 | -0.027466 | -0.009155 | 0.013733 | -0.032043 | 1.7807 | 1.6846 | -117.897 | 1.7303 | 1.7853 | 0.10071 | -117.9886 | 1.7944 | 1.7487 | -117.9428 | 1.6708 | 1.6251 | -0.1236 | -117.9245 | 1.799 | 1.7075 | 1.7487 | -118.0115 | 1.7532 | 1.7715 | 1.7807 | -117.9474
3162.6094 | 119.7876 | -1.1627 | 118.5013 | -0.0049592 | 0.010636 | 0.016908 | 0.0016748 | 0.030586 | 6.8274e-05 | -0.04525 | -0.020752 | 0.0087607 | -0.016129 | -0.00010889 | 2.4771 | 0.027923 | 0.050354 | 0.054932 | 0.07782 | 0.086975 | -0.027466 | 0.054932 | -0.064087 | 0.018311 | 0.086975 | -0.045776 | -0.064087 | -0.045776 | 0.07782 | 0.009155 | 1.2177 | 1.0986 | -118.5287 | 1.2177 | 1.2497 | 0.15106 | -118.4509 | 1.2405 | 1.1719 | -118.5654 | 1.181 | 1.1169 | -0.054931 | -118.5471 | 1.1353 | 1.2131 | 1.2405 | -118.5654 | 1.0986 | 1.1169 | 1.2497 | -118.4921
3164.3906 | 119.7464 | -0.70038 | 119.0414 | -0.012589 | 0.013627 | 0.01819 | 0.0027428 | 0.030586 | 0.0015637 | -0.046318 | -0.013123 | 0.012819 | -0.01207 | -0.00010889 | 2.4643 | 0.028136 | -0.050354 | -0.07782 | -0.045776 | 0.009155 | 0.009155 | 0.009155 | -0.10986 | -0.11444 | -0.013733 | -0.16479 | -0.013733 | -0.022888 | 0.045776 | -0.036621 | 0.70953 | 0.59051 | -119.0323 | 0.62256 | 0.70953 | 0.11902 | -119.0918 | 0.74615 | 0.66376 | -119.0552 | 0.58594 | 0.53558 | -0.12817 | -119.0643 | 0.70953 | 0.65002 | 0.6546 | -119.1513 | 0.68664 | 0.67749 | 0.68664 | -119.0781
3166.1875 | 119.7281 | -2.4811 | 116.9907 | 0.0026703 | 0.010636 | 0.018404 | 0.0033838 | 0.030159 | -0.0033495 | -0.04525 | -0.013123 | 0.0064109 | -0.012283 | -0.00032249 | 2.5983 | 0.029418 | -0.027466 | -0.022888 | 0.045776 | 0.064087 | 0.004578 | 0.041199 | -0.082397 | -0.050354 | 0.064087 | -0.064087 | -0.064087 | -0.032043 | 0.073242 | 0 | 2.5223 | 2.3987 | -116.9861 | 2.4582 | 2.5452 | 0.14648 | -117.0181 | 2.5543 | 2.4811 | -117.0547 | 2.4307 | 2.417 | -0.064087 | -117.0227 | 2.4857 | 2.4536 | 2.5269 | -117.0731 | 2.417 | 2.449 | 2.5452 | -116.9907
3167.9062 | 119.5908 | -1.6846 | 117.9245 | -0.012589 | 0.021318 | 0.01584 | 0.001034 | 0.034645 | 0.0066907 | -0.043968 | -0.0054932 | 0.012179 | -0.0099334 | 0.00010471 | 2.6397 | 0.025573 | 0.018311 | -0.022888 | 0.013733 | 0.045776 | 0.018311 | 0.022888 | -0.11902 | -0.013733 | 0.041199 | -0.11444 | -0.041199 | -0.036621 | 0.045776 | -0.009155 | 1.7075 | 1.5656 | -117.9062 | 1.6617 | 1.7303 | 0.16479 | -117.9062 | 1.7303 | 1.6754 | -117.9657 | 1.6708 | 1.5701 | -0.10529 | -117.9611 | 1.7029 | 1.7029 | 1.6983 | -118.0435 | 1.6434 | 1.6479 | 1.7258 | -117.9337
3169.6719 | 119.4809 | -4.4678 | 114.7842 | -0.012589 | 0.011064 | 0.016695 | 0.0033838 | 0.032723 | -0.0044177 | -0.045036 | -0.013123 | 0.0072653 | -0.013565 | -0.00010889 | 2.5156 | 0.028777 | 0.022888 | 0.059509 | 0.07782 | 0.10529 | -0.013733 | 0.032043 | -0.059509 | 0 | 0.1236 | -0.009155 | -0.064087 | -0.054932 | 0.082397 | 0.009155 | 4.4998 | 4.4083 | -114.798 | 4.5273 | 4.5731 | 0.16479 | -114.7614 | 4.5502 | 4.4769 | -114.8483 | 4.4678 | 4.4586 | -0.01831 | -114.8392 | 4.454 | 4.4907 | 4.5456 | -114.8438 | 4.4037 | 4.4128 | 4.5914 | -114.7751
3171.3906 | 119.3527 | -5.127 | 114.1937 | -0.027847 | 0.014268 | 0.015413 | -0.00067498 | 0.034645 | 0.0056225 | -0.044822 | -0.013123 | 0.011751 | -0.013992 | -0.00032249 | 2.5498 | 0.025359 | -0.045776 | -0.10529 | -0.064087 | 0.022888 | 0.032043 | 0.018311 | -0.11444 | -0.073242 | -0.045776 | -0.16937 | -0.036621 | -0.013733 | 0.022888 | -0.022888 | 5.1453 | 5.0125 | -114.1617 | 5.0217 | 5.1498 | 0.13733 | -114.2395 | 5.1498 | 5.1041 | -114.2303 | 5.0537 | 4.9576 | -0.14649 | -114.2075 | 5.159 | 5.0812 | 5.0629 | -114.3082 | 5.0903 | 5.1132 | 5.0812 | -114.2166
3173.1719 | 119.1879 | -6.2622 | 112.912 | -0.012589 | 0.01555 | 0.017976 | 0.0018884 | 0.03315 | 0.0030591 | -0.044395 | -0.013123 | 0.010897 | -0.010574 | -0.00032249 | 2.5201 | 0.025146 | -0.050354 | -0.073242 | -0.027466 | 0.045776 | 0.032043 | 0.004578 | -0.10986 | -0.050354 | 0.036621 | -0.14648 | -0.022888 | -0.009155 | 0.045776 | -0.013733 | 6.2668 | 6.1523 | -112.8799 | 6.189 | 6.308 | 0.15564 | -112.9623 | 6.308 | 6.2485 | -112.9349 | 6.2119 | 6.1157 | -0.13275 | -112.9211 | 6.2942 | 6.2119 | 6.2347 | -113.0219 | 6.2393 | 6.2531 | 6.2988 | -112.9257
3174.9375 | 118.7851 | -11.0275 | 107.5607 | -0.0049592 | 0.015122 | 0.017336 | 0.003811 | 0.031014 | -0.0061267 | -0.045891 | -0.013123 | 0.0068381 | -0.013138 | -0.0028861 | 2.547 | 0.027282 | 0.045776 | 0.10071 | 0.12817 | 0.1236 | -0.004578 | 0.036621 | -0.073242 | 0.013733 | 0.16022 | 0.009155 | -0.073242 | -0.054932 | 0.064087 | 0.013733 | 11.0641 | 10.9543 | -107.5653 | 11.1282 | 11.1511 | 0.19684 | -107.515 | 11.0916 | 11.0413 | -107.634 | 11.0413 | 11.0367 | -0.004578 | -107.6157 | 11.0229 | 11.0733 | 11.1557 | -107.634 | 10.9543 | 10.9726 | 11.1877 | -107.547
3176.7188 | 118.8263 | -6.4957 | 112.4039 | -0.012589 | 0.015977 | 0.018404 | 0.0023156 | 0.032082 | -0.0027087 | -0.046959 | -0.013123 | 0.0091879 | -0.013351 | -0.0016043 | 2.5733 | 0.026214 | 0.022888 | 0.054932 | 0.091553 | 0.10986 | -0.027466 | 0.036621 | -0.073242 | -0.018311 | 0.11444 | -0.059509 | -0.059509 | -0.041199 | 0.068665 | 0.013733 | 6.5323 | 6.4224 | -112.4313 | 6.5506 | 6.6055 | 0.18311 | -112.381 | 6.5643 | 6.5094 | -112.4634 | 6.4774 | 6.4362 | -0.073242 | -112.4451 | 6.4682 | 6.5186 | 6.5872 | -112.4771 | 6.4362 | 6.4545 | 6.6101 | -112.3901
3178.5 | 118.8538 | -5.9509 | 112.7838 | -0.020218 | 0.012986 | 0.015199 | -3.4178e-05 | 0.0355 | 6.8274e-05 | -0.045463 | -0.020752 | 0.0079063 | -0.014847 | 0.00031831 | 2.5703 | 0.027282 | 0.036621 | 0.068665 | 0.10071 | 0.086975 | -0.018311 | 0.064087 | -0.059509 | 0.022888 | 0.10529 | -0.027466 | -0.068665 | -0.059509 | 0.059509 | -0.009155 | 6.015 | 5.8914 | -112.8021 | 6.0196 | 6.0379 | 0.14648 | -112.7472 | 6.0104 | 5.9418 | -112.8525 | 5.9738 | 5.9235 | -0.018311 | -112.8433 | 5.9326 | 5.9875 | 6.0516 | -112.8433 | 5.8823 | 5.8914 | 6.0562 | -112.793
3180.2969 | 118.4555 | -8.0704 | 110.2432 | -0.012589 | 0.014482 | 0.015413 | -0.0011024 | 0.034218 | 0.0047681 | -0.043113 | -0.020752 | 0.014101 | -0.012711 | 0.0013863 | 2.4769 | 0.027068 | -0.068665 | -0.11902 | -0.068665 | 0.027466 | 0.022888 | 0.027466 | -0.091553 | -0.068665 | -0.045776 | -0.19226 | -0.032043 | -0.004578 | 0.036621 | -0.032043 | 8.0978 | 7.9788 | -110.2203 | 7.9514 | 8.0978 | 0.11902 | -110.3119 | 8.107 | 8.0383 | -110.2753 | 8.0017 | 7.8781 | -0.16022 | -110.2478 | 8.0933 | 8.0017 | 8.0017 | -110.3348 | 8.0383 | 8.0658 | 8.0246 | -110.2753
3182.0781 | 118.2541 | -11.7966 | 106.2744 | -0.035477 | 0.014268 | 0.015199 | 0.0046656 | 0.034432 | 0.0015637 | -0.043968 | -0.013123 | 0.010897 | -0.010788 | 0.00095911 | 2.5096 | 0.026641 | -0.045776 | -0.068665 | -0.045776 | 0.036621 | 0.036621 | 0.013733 | -0.10529 | -0.068665 | 0.018311 | -0.15564 | -0.018311 | -0.004578 | 0.041199 | -0.036621 | 11.8103 | 11.6913 | -106.2378 | 11.7279 | 11.8332 | 0.14191 | -106.3202 | 11.8378 | 11.7599 | -106.2927 | 11.7279 | 11.6409 | -0.11902 | -106.279 | 11.8332 | 11.7508 | 11.7508 | -106.3797 | 11.7783 | 11.792 | 11.8149 | -106.311
3183.8594 | 117.6865 | -16.1499 | 101.4038 | -0.0049592 | 0.016831 | 0.014986 | 0.00039302 | 0.031868 | 0.0047681 | -0.043968 | -0.020752 | 0.010897 | -0.013138 | 0.0013863 | 2.5316 | 0.026427 | -0.004578 | -0.009155 | 0.018311 | 0.064087 | 0.022888 | 0.027466 | -0.082397 | -0.018311 | 0.068665 | -0.09613 | -0.036621 | -0.013733 | 0.045776 | -0.013733 | 16.1774 | 16.0675 | -101.3809 | 16.1407 | 16.214 | 0.14648 | -101.4084 | 16.1957 | 16.1362 | -101.4404 | 16.1316 | 16.0538 | -0.082397 | -101.4175 | 16.1728 | 16.1453 | 16.1682 | -101.4862 | 16.1133 | 16.1362 | 16.2186 | -101.4175
3185.5938 | 117.8192 | -12.2635 | 105.368 | -0.012589 | 0.012345 | 0.016267 | -0.0032386 | 0.032509 | -0.0018543 | -0.0429 | -0.0054932 | 0.0087607 | -0.015488 | 0.0016001 | 2.5575 | 0.029845 | 0.032043 | 0.064087 | 0.091553 | 0.10986 | -0.032043 | 0.068665 | -0.054932 | 0.045776 | 0.11902 | -0.018311 | -0.064087 | -0.059509 | 0.086975 | 0.013733 | 12.3322 | 12.2086 | -105.4001 | 12.3276 | 12.3734 | 0.16479 | -105.336 | 12.3505 | 12.2772 | -105.4321 | 12.3093 | 12.2452 | -0.032044 | -105.4276 | 12.2314 | 12.2955 | 12.355 | -105.423 | 12.1994 | 12.204 | 12.3825 | -105.3543
3187.3594 | 119.0094 | -0.55389 | 118.4052 | -0.0049592 | 0.011918 | 0.017763 | 0.002102 | 0.031014 | -0.0052721 | -0.045463 | -0.013123 | 0.0076925 | -0.013565 | -0.0035269 | 2.5248 | 0.030486 | 0.041199 | 0.10071 | 0.10986 | 0.10529 | -0.041199 | 0.032043 | -0.068665 | 0.018311 | 0.15106 | -0.013733 | -0.082397 | -0.045776 | 0.068665 | 0.022888 | 0.58594 | 0.48523 | -118.4464 | 0.6546 | 0.65918 | 0.17395 | -118.364 | 0.62256 | 0.57678 | -118.4875 | 0.5722 | 0.54016 | -0.036621 | -118.4509 | 0.5127 | 0.59509 | 0.66376 | -118.4738 | 0.4715 | 0.50812 | 0.70496 | -118.3823
3189.0781 | 119.3893 | -0.59967 | 118.8263 | -0.0049592 | 0.016404 | 0.016267 | 0.0033838 | 0.032723 | 0.0032727 | -0.044395 | -0.013123 | 0.011751 | -0.011429 | 0.00031831 | 2.494 | 0.026427 | -0.054932 | -0.086975 | -0.045776 | 0.036621 | 0.013733 | -0.004578 | -0.10986 | -0.068665 | 0.022888 | -0.13275 | -0.041199 | -0.018311 | 0.036621 | -0.022888 | 0.59509 | 0.48981 | -118.8126 | 0.5127 | 0.63629 | 0.14648 | -118.8812 | 0.63629 | 0.57678 | -118.8675 | 0.53101 | 0.46692 | -0.10986 | -118.8446 | 0.6134 | 0.54474 | 0.55389 | -118.9362 | 0.55847 | 0.58136 | 0.62256 | -118.8492
3190.8594 | 119.5129 | -0.60425 | 118.9865 | -0.012589 | 0.014268 | 0.01584 | -0.002384 | 0.032936 | 0.0015637 | -0.044822 | -0.013123 | 0.011751 | -0.014206 | -0.00053629 | 2.5714 | 0.026855 | -0.022888 | -0.036621 | -0.004578 | 0.059509 | 0.013733 | 0.004578 | -0.11444 | -0.041199 | 0.050354 | -0.10986 | -0.022888 | -0.022888 | 0.036621 | -0.018311 | 0.60883 | 0.48981 | -118.9728 | 0.56763 | 0.66376 | 0.17395 | -119.0094 | 0.64087 | 0.58594 | -119.0094 | 0.56305 | 0.49439 | -0.091552 | -119.0094 | 0.61798 | 0.58136 | 0.59967 | -119.101 | 0.58136 | 0.58136 | 0.6546 | -119.0048
3192.5781 | 119.5999 | -0.60883 | 118.9957 | -0.0049592 | 0.015122 | 0.017336 | -0.00024778 | 0.031441 | 0.00092287 | -0.045891 | 0.0021363 | 0.011538 | -0.013779 | -0.0011771 | 2.5829 | 0.026855 | -0.050354 | -0.082397 | -0.041199 | 0.036621 | 0.013733 | 0.013733 | -0.11902 | -0.091553 | 0.018311 | -0.14191 | -0.018311 | 0 | 0.036621 | -0.022888 | 0.62256 | 0.48981 | -118.9819 | 0.52643 | 0.64545 | 0.15564 | -119.046 | 0.64545 | 0.58594 | -119.014 | 0.51727 | 0.46692 | -0.11902 | -118.9957 | 0.62256 | 0.55847 | 0.56763 | -119.1147 | 0.59052 | 0.60883 | 0.62714 | -119.0186
3194.3594 | 118.4784 | -5.5527 | 112.9578 | -0.012589 | 0.015763 | 0.015413 | 0.0014612 | 0.032723 | 0.0034863 | -0.0429 | -0.013123 | 0.01346 | -0.012497 | 0.0013863 | 2.5876 | 0.026214 | -0.068665 | -0.09613 | -0.045776 | 0.013733 | 0.027466 | 0.009155 | -0.10986 | -0.10071 | -0.041199 | -0.20142 | -0.027466 | -0.013733 | 0.036621 | -0.027466 | 5.5618 | 5.4428 | -112.9303 | 5.4565 | 5.5664 | 0.1236 | -113.0264 | 5.5893 | 5.5252 | -112.9852 | 5.452 | 5.3513 | -0.17395 | -112.9715 | 5.5801 | 5.484 | 5.5069 | -113.0676 | 5.5252 | 5.5389 | 5.5115 | -112.9852
3196.1406 | 119.6274 | -0.63171 | 118.9224 | 0.0026703 | 0.014482 | 0.017549 | 0.0053064 | 0.034218 | -0.0052721 | -0.045036 | -0.013123 | 0.0079063 | -0.01442 | -0.0011771 | 2.5083 | 0.028564 | 0.022888 | 0.068665 | 0.086975 | 0.10986 | -0.032043 | 0.041199 | -0.086975 | -0.009155 | 0.16022 | 0 | -0.091553 | -0.045776 | 0.068665 | 0.013733 | 0.67291 | 0.54474 | -118.9545 | 0.70038 | 0.74158 | 0.19684 | -118.8995 | 0.70038 | 0.64545 | -119.014 | 0.62256 | 0.63171 | -0.013733 | -118.9682 | 0.59967 | 0.6546 | 0.71869 | -119.0094 | 0.54016 | 0.58594 | 0.79193 | -118.9087
3197.9062 | 119.5221 | -0.72327 | 118.7851 | -0.0049592 | 0.010636 | 0.019472 | 0.00039302 | 0.034004 | -0.0050585 | -0.046959 | -0.013123 | 0.0074789 | -0.015701 | 0.00053191 | 2.6376 | 0.028777 | 0.013733 | 0.064087 | 0.073242 | 0.10071 | 0 | 0.041199 | -0.082397 | 0 | 0.14648 | 0.018311 | -0.073242 | -0.045776 | 0.064087 | 0.013733 | 0.76447 | 0.64087 | -118.7851 | 0.78735 | 0.82398 | 0.18311 | -118.7714 | 0.78735 | 0.737 | -118.8583 | 0.72327 | 0.74158 | 0.004578 | -118.8309 | 0.72327 | 0.737 | 0.79651 | -118.8675 | 0.65002 | 0.67749 | 0.86975 | -118.7714
3199.625 | 119.632 | -0.73242 | 118.9728 | -0.012589 | 0.017686 | 0.01819 | 0.0016748 | 0.034218 | -0.00099973 | -0.047386 | -0.0054932 | 0.0096151 | -0.01506 | -0.0018179 | 2.6109 | 0.027495 | 0.022888 | 0.045776 | 0.073242 | 0.10071 | -0.022888 | 0.050354 | -0.068665 | -0.045776 | 0.10071 | -0.064087 | -0.068665 | -0.050354 | 0.041199 | -0.013733 | 0.78278 | 0.66376 | -118.9957 | 0.7782 | 0.83313 | 0.16937 | -118.9499 | 0.77362 | 0.71869 | -119.0414 | 0.68665 | 0.66834 | -0.050354 | -119.0231 | 0.70953 | 0.75531 | 0.80566 | -119.0414 | 0.66376 | 0.68207 | 0.83313 | -118.9865
3201.4062 | 119.6228 | -0.71869 | 118.9911 | -0.0049592 | 0.013841 | 0.020113 | 0.00060662 | 0.032295 | -0.0022815 | -0.044822 | -0.013123 | 0.0085471 | -0.015915 | -0.00096349 | 2.6846 | 0.026427 | 0.009155 | 0.027466 | 0.036621 | 0.07782 | -0.013733 | 0.027466 | -0.10071 | -0.050354 | 0.059509 | -0.11902 | -0.041199 | -0.041199 | 0.041199 | -0.036621 | 0.74616 | 0.61798 | -119.0048 | 0.74616 | 0.79651 | 0.17853 | -118.9819 | 0.75989 | 0.68207 | -119.0323 | 0.66834 | 0.59967 | -0.082398 | -119.0323 | 0.70496 | 0.72784 | 0.75531 | -119.0918 | 0.67749 | 0.67749 | 0.7782 | -119.0277
3203.125 | 119.8242 | -0.70496 | 119.0277 | -0.012589 | 0.011491 | 0.016054 | 0.001034 | 0.03315 | 0.00049567 | -0.046531 | -0.013123 | 0.0083335 | -0.014206 | -0.00010889 | 2.6679 | 0.027495 | 0.027466 | 0.032043 | 0.086975 | 0.073242 | 0 | 0.045776 | -0.050354 | 0.018311 | 0.086975 | -0.054932 | -0.064087 | -0.045776 | 0.082397 | 0.009155 | 0.75073 | 0.6546 | -119.0277 | 0.737 | 0.7782 | 0.1236 | -119.0002 | 0.78735 | 0.71411 | -119.0918 | 0.72327 | 0.65002 | -0.064087 | -119.0735 | 0.70496 | 0.73242 | 0.79193 | -119.0781 | 0.64087 | 0.65918 | 0.79193 | -119.0186
3204.9062 | 119.7784 | -0.72327 | 119.1376 | 0.0026703 | 0.01555 | 0.017976 | -0.00046138 | 0.031655 | 0.0054089 | -0.043541 | -0.013123 | 0.012606 | -0.01506 | 0.0016001 | 2.6664 | 0.026427 | 0.027466 | -0.027466 | 0 | 0.068665 | 0.004578 | 0.018311 | -0.09613 | -0.022888 | 0.022888 | -0.14191 | -0.050354 | -0.022888 | 0.027466 | -0.009155 | 0.74158 | 0.62714 | -119.133 | 0.6958 | 0.79193 | 0.16479 | -119.1101 | 0.75073 | 0.71411 | -119.1879 | 0.70038 | 0.58136 | -0.13275 | -119.1605 | 0.72784 | 0.75073 | 0.72327 | -119.2337 | 0.67291 | 0.70038 | 0.74616 | -119.1467
3206.6875 | 119.9707 | -0.6958 | 119.1193 | -0.0049592 | 0.0132 | 0.016054 | 0.001034 | 0.032082 | -0.00014533 | -0.044182 | -0.0054932 | 0.0096151 | -0.011856 | 0.00053191 | 2.6025 | 0.028991 | 0.041199 | 0.054932 | 0.068665 | 0.11444 | -0.018311 | 0.064087 | -0.054932 | 0.045776 | 0.10071 | -0.041199 | -0.07782 | -0.036621 | 0.064087 | 0.004578 | 0.75989 | 0.64087 | -119.1376 | 0.75073 | 0.81024 | 0.16937 | -119.0781 | 0.75989 | 0.70038 | -119.1971 | 0.74158 | 0.6546 | -0.045777 | -119.1559 | 0.67749 | 0.737 | 0.76447 | -119.1742 | 0.61798 | 0.65918 | 0.79651 | -119.1147
3208.3906 | 119.1147 | -7.6218 | 111.2457 | -0.0049592 | 0.012132 | 0.018831 | 0.00082022 | 0.035073 | -0.0031359 | -0.045677 | -0.0054932 | 0.0076925 | -0.013992 | -0.0020315 | 2.6333 | 0.02835 | 0.018311 | 0.045776 | 0.086975 | 0.086975 | -0.013733 | 0.032043 | -0.050354 | 0.009155 | 0.13733 | -0.013733 | -0.059509 | -0.041199 | 0.086975 | 0.018311 | 7.6538 | 7.5714 | -111.2595 | 7.6675 | 7.7087 | 0.13733 | -111.2274 | 7.7087 | 7.6401 | -111.3052 | 7.6309 | 7.608 | -0.032044 | -111.2869 | 7.608 | 7.6401 | 7.7087 | -111.2961 | 7.5623 | 7.5806 | 7.7591 | -111.2274
3210.1719 | 119.0277 | -3.9825 | 114.9994 | -0.012589 | 0.014054 | 0.01819 | 0.003811 | 0.031868 | 0.00092287 | -0.047386 | -0.020752 | 0.010683 | -0.015701 | 0.0011727 | 2.4419 | 0.026 | -0.054932 | -0.09613 | -0.045776 | 0.032043 | 0.022888 | 0 | -0.11444 | -0.10071 | -0.013733 | -0.16937 | -0.022888 | -0.004578 | 0.041199 | -0.018311 | 3.9825 | 3.8681 | -114.9765 | 3.8864 | 4.0146 | 0.14648 | -115.0543 | 4.0237 | 3.9642 | -115.0223 | 3.8818 | 3.8132 | -0.15106 | -115.004 | 4.0054 | 3.9276 | 3.9368 | -115.1138 | 3.9597 | 3.978 | 3.9688 | -115.0177
3211.9531 | 118.1946 | -10.936 | 107.1945 | -0.0049592 | 0.020463 | 0.012636 | 0.0053064 | 0.031441 | 0.0051953 | -0.043541 | -0.0054932 | 0.013888 | -0.010788 | 0.0018137 | 2.5442 | 0.025573 | -0.022888 | -0.082397 | -0.022888 | 0.022888 | 0.009155 | 0.013733 | -0.09613 | -0.059509 | -0.013733 | -0.19684 | -0.036621 | -0.018311 | 0.036621 | -0.018311 | 10.9497 | 10.8398 | -107.1854 | 10.8536 | 10.9589 | 0.11902 | -107.2174 | 10.9726 | 10.9177 | -107.2311 | 10.8765 | 10.7391 | -0.17853 | -107.2128 | 10.9451 | 10.9131 | 10.9131 | -107.2906 | 10.8994 | 10.9177 | 10.9222 | -107.2128
3213.7188 | 118.6752 | -5.4428 | 113.0585 | 0.0026703 | 0.015763 | 0.014131 | -0.00088858 | 0.0308 | 0.0017773 | -0.043541 | -0.013123 | 0.01111 | -0.011642 | 0.0020273 | 2.553 | 0.024932 | -0.054932 | -0.086975 | -0.059509 | 0.027466 | 0.018311 | 0.027466 | -0.10071 | -0.07782 | -0.022888 | -0.15564 | -0.045776 | -0.018311 | 0.036621 | -0.013733 | 5.4703 | 5.3421 | -113.0402 | 5.3558 | 5.4703 | 0.12817 | -113.1134 | 5.4794 | 5.4291 | -113.1042 | 5.365 | 5.2872 | -0.14191 | -113.0768 | 5.4611 | 5.3879 | 5.3833 | -113.1592 | 5.397 | 5.4245 | 5.4199 | -113.0722
3215.4375 | 118.5287 | -6.3492 | 112.1017 | -0.012589 | 0.01555 | 0.019045 | -0.00088858 | 0.031441 | -0.0042041 | -0.0429 | -0.0054932 | 0.0087607 | -0.013351 | -0.00074989 | 2.4231 | 0.027709 | -0.004578 | 0.022888 | 0.059509 | 0.064087 | -0.022888 | 0.036621 | -0.068665 | -0.036621 | 0.064087 | -0.064087 | -0.059509 | -0.032043 | 0.073242 | 0.022888 | 6.3858 | 6.2805 | -112.1246 | 6.3721 | 6.4133 | 0.13275 | -112.1063 | 6.4224 | 6.3721 | -112.1613 | 6.3126 | 6.2851 | -0.086975 | -112.1338 | 6.3263 | 6.3446 | 6.4087 | -112.1704 | 6.2897 | 6.3171 | 6.4133 | -112.0789
3217.2188 | 119.4901 | -0.67291 | 118.7897 | -0.012589 | 0.011277 | 0.016481 | -0.0011024 | 0.032295 | -0.0027087 | -0.0429 | -0.020752 | 0.010256 | -0.013992 | 0.00095911 | 2.5921 | 0.029632 | 0.032043 | 0.045776 | 0.07782 | 0.082397 | -0.032043 | 0.036621 | -0.059509 | 0.004578 | 0.082397 | -0.036621 | -0.073242 | -0.054932 | 0.073242 | 0.018311 | 0.70953 | 0.6134 | -118.8217 | 0.71869 | 0.75531 | 0.14191 | -118.7576 | 0.74616 | 0.69122 | -118.8629 | 0.67749 | 0.63629 | -0.054932 | -118.8446 | 0.64087 | 0.70496 | 0.75073 | -118.8492 | 0.59967 | 0.61798 | 0.75531 | -118.7714
3219.0156 | 118.1076 | -11.2335 | 106.8604 | -0.020218 | 0.016191 | 0.019258 | 0.00060662 | 0.032509 | 0.0045545 | -0.045036 | -0.020752 | 0.013674 | -0.014633 | 0.00010471 | 2.4925 | 0.026427 | -0.054932 | -0.10071 | -0.064087 | 0.018311 | 0.009155 | 0.009155 | -0.10071 | -0.073242 | -0.041199 | -0.17395 | -0.022888 | -0.018311 | 0.050354 | -0.032043 | 11.2427 | 11.1328 | -106.8512 | 11.1328 | 11.2518 | 0.11902 | -106.9153 | 11.2839 | 11.2015 | -106.8832 | 11.1603 | 11.0596 | -0.14191 | -106.8787 | 11.2427 | 11.1786 | 11.1694 | -106.9611 | 11.2106 | 11.2152 | 11.1923 | -106.8924
3220.7344 | 119.1055 | -2.4307 | 116.5878 | -0.012589 | 0.01085 | 0.016481 | -0.0011024 | 0.032723 | -0.0016405 | -0.045891 | -0.0054932 | 0.0083335 | -0.015274 | -0.0016043 | 2.6412 | 0.026 | 0.022888 | 0.045776 | 0.07782 | 0.086975 | -0.022888 | 0.036621 | -0.054932 | -0.004578 | 0.073242 | -0.054932 | -0.07782 | -0.068665 | 0.050354 | -0.022888 | 2.4673 | 2.3758 | -116.6107 | 2.4765 | 2.5177 | 0.14191 | -116.5649 | 2.4811 | 2.4078 | -116.6656 | 2.4261 | 2.3758 | -0.032044 | -116.6565 | 2.4078 | 2.4536 | 2.5085 | -116.6428 | 2.3529 | 2.3621 | 2.504 | -116.6107
3222.5312 | 119.5404 | -1.355 | 118.0939 | -0.012589 | 0.014695 | 0.016908 | -0.0011024 | 0.029946 | 0.0043409 | -0.045036 | -0.0054932 | 0.01111 | -0.01506 | -0.00096349 | 2.6562 | 0.027923 | -0.068665 | -0.10529 | -0.050354 | 0.009155 | 0.018311 | 0.009155 | -0.07782 | -0.091553 | -0.041199 | -0.16937 | -0.022888 | -0.013733 | 0.032043 | -0.032043 | 1.3641 | 1.2772 | -118.0756 | 1.2497 | 1.3641 | 0.086975 | -118.1625 | 1.387 | 1.3229 | -118.1168 | 1.2634 | 1.1856 | -0.13733 | -118.1076 | 1.3733 | 1.2863 | 1.3046 | -118.1717 | 1.3321 | 1.3412 | 1.3138 | -118.1259
3224.2656 | 118.9774 | -6.5872 | 112.3581 | -0.012589 | 0.014482 | 0.017976 | 0.0059472 | 0.034004 | 0.0028455 | -0.045463 | -0.013123 | 0.011324 | -0.01442 | 0.0013863 | 2.6442 | 0.027068 | -0.054932 | -0.07782 | -0.036621 | 0.013733 | 0.018311 | 0.004578 | -0.10529 | -0.10529 | -0.013733 | -0.16937 | -0.027466 | -0.018311 | 0.041199 | -0.009155 | 6.5918 | 6.4819 | -112.3398 | 6.5094 | 6.601 | 0.11902 | -112.413 | 6.6284 | 6.5781 | -112.3856 | 6.4819 | 6.4178 | -0.16022 | -112.3764 | 6.6055 | 6.5323 | 6.5506 | -112.4634 | 6.5598 | 6.5689 | 6.5735 | -112.3672
3226.0312 | 118.8766 | -2.6413 | 116.1758 | -0.020218 | 0.015122 | 0.017549 | 0.00060662 | 0.034645 | 0.0028455 | -0.043541 | -0.0054932 | 0.010897 | -0.012711 | 0.00010471 | 2.6641 | 0.027068 | -0.064087 | -0.073242 | -0.041199 | 0.036621 | 0.022888 | 0.009155 | -0.11444 | -0.082397 | 0.018311 | -0.14648 | -0.027466 | -0.018311 | 0.041199 | -0.018311 | 2.6505 | 2.5269 | -116.153 | 2.5681 | 2.6779 | 0.15106 | -116.2399 | 2.6825 | 2.623 | -116.2033 | 2.5589 | 2.4948 | -0.12817 | -116.1942 | 2.6642 | 2.5772 | 2.6001 | -116.2903 | 2.6138 | 2.623 | 2.6596 | -116.1942
3227.8125 | 118.6523 | -7.3883 | 111.4105 | -0.012589 | 0.014482 | 0.016908 | 0.0031702 | 0.033364 | -0.0024951 | -0.044822 | -0.013123 | 0.0096151 | -0.011429 | -0.0011771 | 2.6416 | 0.029418 | -0.050354 | -0.036621 | -0.018311 | 0.022888 | 0.013733 | 0.018311 | -0.091553 | -0.10071 | 0.009155 | -0.14191 | -0.018311 | -0.009155 | 0.050354 | -0.032043 | 7.4066 | 7.2968 | -111.3968 | 7.3517 | 7.4112 | 0.11444 | -111.4609 | 7.4387 | 7.3563 | -111.4288 | 7.2876 | 7.2464 | -0.10986 | -111.4197 | 7.402 | 7.338 | 7.37 | -111.5021 | 7.37 | 7.3792 | 7.3975 | -111.4426
3229.5938 | 119.1422 | -4.5181 | 114.4363 | -0.0049592 | 0.0099953 | 0.016695 | 0.001034 | 0.031441 | -0.0050585 | -0.046104 | -0.013123 | 0.0074789 | -0.016342 | -0.00096349 | 2.5658 | 0.029632 | -0.045776 | -0.009155 | 0.027466 | 0.064087 | 0.009155 | 0.054932 | -0.064087 | -0.059509 | 0.054932 | -0.07782 | -0.068665 | -0.032043 | 0.064087 | -0.004578 | 4.5731 | 4.454 | -114.4272 | 4.509 | 4.5822 | 0.12817 | -114.4821 | 4.5822 | 4.5135 | -114.505 | 4.4586 | 4.4403 | -0.073242 | -114.4684 | 4.5273 | 4.4724 | 4.5456 | -114.5004 | 4.4495 | 4.4861 | 4.5731 | -114.4409
3231.3594 | 119.0964 | -1.7212 | 117.0456 | -0.020218 | 0.0093545 | 0.019685 | 0.00039302 | 0.030373 | -0.0035633 | -0.046959 | -0.013123 | 0.0083335 | -0.014847 | -0.0013907 | 2.5852 | 0.028564 | -0.050354 | -0.009155 | 0.018311 | 0.064087 | -0.009155 | 0.036621 | -0.082397 | -0.064087 | 0.041199 | -0.09613 | -0.064087 | -0.041199 | 0.050354 | -0.004578 | 1.7578 | 1.6388 | -117.0547 | 1.712 | 1.7853 | 0.14648 | -117.0959 | 1.7715 | 1.7166 | -117.1097 | 1.6571 | 1.6251 | -0.091552 | -117.0868 | 1.712 | 1.6708 | 1.7395 | -117.128 | 1.6571 | 1.68 | 1.7624 | -117.0502
3233.0781 | 119.1376 | -1.0208 | 118.0527 | -0.020218 | 0.011277 | 0.016267 | -0.0017432 | 0.034432 | 0.0013501 | -0.043541 | -0.020752 | 0.0079063 | -0.014633 | -0.0030997 | 2.5624 | 0.026641 | 0.045776 | 0.068665 | 0.091553 | 0.10529 | -0.022888 | 0.036621 | -0.059509 | 0.027466 | 0.09613 | -0.050354 | -0.07782 | -0.059509 | 0.07782 | 0.009155 | 1.0574 | 0.9613 | -118.0756 | 1.0895 | 1.1261 | 0.16479 | -118.0069 | 1.0986 | 1.03 | -118.1305 | 1.0483 | 0.97046 | -0.059509 | -118.1122 | 0.99792 | 1.0666 | 1.1124 | -118.1122 | 0.94299 | 0.9613 | 1.1169 | -118.0435
3234.8438 | 118.3823 | -11.3205 | 107.3547 | -0.020218 | 0.014482 | 0.019899 | 0.0029566 | 0.032936 | -0.0016405 | -0.04525 | -0.013123 | 0.0083335 | -0.014633 | -0.00096349 | 2.5846 | 0.024291 | 0.027466 | 0.068665 | 0.11902 | 0.09613 | -0.004578 | 0.045776 | -0.073242 | 0.004578 | 0.13275 | -0.041199 | -0.082397 | -0.054932 | 0.068665 | 0.009155 | 11.3663 | 11.2473 | -107.3593 | 11.3892 | 11.4166 | 0.16937 | -107.3273 | 11.3892 | 11.3297 | -107.4371 | 11.3251 | 11.2793 | -0.050354 | -107.4097 | 11.3159 | 11.348 | 11.4395 | -107.428 | 11.2381 | 11.2656 | 11.4532 | -107.3456
3236.5625 | 119.3298 | -12.9089 | 106.5857 | -0.0049592 | 0.010423 | 0.017763 | 0.002102 | 0.030159 | -0.00078613 | -0.045891 | -0.0054932 | 0.0066245 | -0.01442 | -0.0011771 | 2.6175 | 0.027923 | 0.027466 | 0.064087 | 0.09613 | 0.09613 | -0.022888 | 0.045776 | -0.082397 | 0.032043 | 0.13275 | -0.009155 | -0.059509 | -0.054932 | 0.10071 | 0.013733 | 12.9547 | 12.8265 | -106.6086 | 12.973 | 13.0051 | 0.17853 | -106.5582 | 13.0096 | 12.9227 | -106.6452 | 12.941 | 12.8998 | -0.022888 | -106.6406 | 12.886 | 12.9364 | 13.0051 | -106.6681 | 12.8494 | 12.854 | 13.0417 | -106.572
3238.3281 | 118.2587 | -14.328 | 103.5049 | 0.0026703 | 0.0093545 | 0.020326 | 0.00060662 | 0.033364 | -0.0016405 | -0.044822 | -0.0054932 | 0.0085471 | -0.01506 | -0.00053629 | 2.6248 | 0.025786 | 0 | 0.022888 | 0.050354 | 0.082397 | -0.009155 | 0.050354 | -0.054932 | -0.004578 | 0.10986 | -0.018311 | -0.054932 | -0.045776 | 0.086975 | 0.004578 | 14.3784 | 14.2731 | -103.5141 | 14.3509 | 14.4104 | 0.13733 | -103.5049 | 14.415 | 14.3326 | -103.5599 | 14.3234 | 14.3097 | -0.022889 | -103.5507 | 14.3188 | 14.328 | 14.3784 | -103.5599 | 14.2731 | 14.2822 | 14.4379 | -103.5004
3240.0469 | 119.0369 | -7.0496 | 111.9507 | -0.0049592 | 0.014482 | 0.01584 | 0.00039302 | 0.031868 | 0.0062635 | -0.043754 | -0.013123 | 0.014956 | -0.014847 | 0.0026681 | 2.5949 | 0.024505 | -0.036621 | -0.10529 | -0.045776 | 0.027466 | 0.027466 | 0.022888 | -0.11902 | -0.073242 | -0.045776 | -0.19684 | -0.004578 | 0.004578 | 0.022888 | -0.018311 | 7.0724 | 6.9305 | -111.9232 | 6.9443 | 7.077 | 0.14649 | -111.9873 | 7.0724 | 7.0312 | -111.9553 | 6.9763 | 6.8527 | -0.17853 | -111.9461 | 7.077 | 7.0129 | 7.0038 | -112.0697 | 7.045 | 7.0541 | 7.0038 | -111.969
3241.7812 | 119.3115 | -2.3987 | 116.7572 | -0.0049592 | 0.012773 | 0.017336 | -0.00046138 | 0.030159 | 0.0013501 | -0.044609 | -0.013123 | 0.0096151 | -0.016129 | -0.0013907 | 2.5534 | 0.027282 | 0 | -0.013733 | 0.009155 | 0.068665 | 0.004578 | 0.027466 | -0.073242 | 0.018311 | 0.073242 | -0.064087 | -0.073242 | -0.045776 | 0.059509 | 0.018311 | 2.4261 | 2.3254 | -116.7526 | 2.3849 | 2.4673 | 0.14191 | -116.7572 | 2.4582 | 2.417 | -116.8304 | 2.417 | 2.3346 | -0.082398 | -116.803 | 2.4033 | 2.3987 | 2.4078 | -116.8304 | 2.3254 | 2.3529 | 2.4719 | -116.7389
3243.5 | 119.0598 | -2.5497 | 116.6107 | -0.020218 | 0.011491 | 0.017976 | -0.00067498 | 0.031655 | -0.00078613 | -0.042686 | -0.0054932 | 0.0079063 | -0.014206 | -0.0026725 | 2.5848 | 0.027709 | 0.050354 | 0.068665 | 0.09613 | 0.10529 | -0.032043 | 0.059509 | -0.054932 | 0.036621 | 0.10986 | -0.027466 | -0.091553 | -0.045776 | 0.059509 | 0.013733 | 2.6093 | 2.4948 | -116.6428 | 2.6184 | 2.655 | 0.16022 | -116.5604 | 2.6093 | 2.5635 | -116.7023 | 2.5864 | 2.5223 | -0.041199 | -116.6565 | 2.5177 | 2.6001 | 2.6459 | -116.6656 | 2.4582 | 2.504 | 2.6596 | -116.597
3245.2812 | 119.1376 | -4.509 | 114.4684 | -0.0049592 | 0.010423 | 0.020326 | 0.0029566 | 0.031441 | -0.0029223 | -0.04525 | -0.013123 | 0.0059837 | -0.012924 | -0.0028861 | 2.5959 | 0.028564 | 0.032043 | 0.086975 | 0.10986 | 0.10071 | -0.013733 | 0.050354 | -0.073242 | 0.036621 | 0.16022 | -0.022888 | -0.086975 | -0.059509 | 0.07782 | 0.009155 | 4.5593 | 4.4357 | -114.4821 | 4.5959 | 4.6097 | 0.17395 | -114.4363 | 4.5868 | 4.5181 | -114.5554 | 4.5456 | 4.4861 | -0.032043 | -114.5279 | 4.4952 | 4.541 | 4.6188 | -114.5416 | 4.422 | 4.4495 | 4.6692 | -114.4592
3247.0625 | 118.959 | -3.5339 | 115.5075 | -0.012589 | 0.014482 | 0.016695 | 0.0014612 | 0.033577 | 0.0036999 | -0.044609 | -0.028381 | 0.01111 | -0.012283 | 0.00074551 | 2.6739 | 0.026214 | 0 | -0.013733 | 0.004578 | 0.068665 | 0 | 0.013733 | -0.09613 | -0.013733 | 0.054932 | -0.12817 | -0.041199 | -0.036621 | 0.059509 | -0.009155 | 3.5477 | 3.4378 | -115.5075 | 3.5202 | 3.6026 | 0.16479 | -115.5075 | 3.5934 | 3.5248 | -115.5487 | 3.5202 | 3.4058 | -0.11902 | -115.5441 | 3.5339 | 3.5339 | 3.5385 | -115.6036 | 3.4927 | 3.4973 | 3.5889 | -115.5167
3248.7812 | 119.2108 | -2.8381 | 116.3361 | -0.0049592 | 0.012986 | 0.019045 | 0.0031702 | 0.032082 | -0.0039905 | -0.044182 | -0.013123 | 0.0068381 | -0.013779 | -0.00053629 | 2.5957 | 0.028777 | 0.027466 | 0.091553 | 0.09613 | 0.1236 | -0.022888 | 0.032043 | -0.064087 | 0.004578 | 0.14648 | -0.009155 | -0.059509 | -0.059509 | 0.082397 | 0.022888 | 2.8702 | 2.774 | -116.3589 | 2.9297 | 2.9617 | 0.18768 | -116.3086 | 2.9205 | 2.861 | -116.3956 | 2.8427 | 2.829 | -0.032043 | -116.3956 | 2.8152 | 2.8656 | 2.9343 | -116.4001 | 2.7786 | 2.7786 | 2.9846 | -116.3132
3250.5 | 119.0186 | -4.8157 | 114.0335 | 0.0026703 | 0.011704 | 0.014131 | 0.00060662 | 0.029946 | 0.00092287 | -0.04525 | -0.0054932 | 0.0087607 | -0.01442 | 0.0013863 | 2.6363 | 0.026855 | 0.045776 | 0.050354 | 0.086975 | 0.10071 | -0.027466 | 0.050354 | -0.059509 | 0.027466 | 0.11444 | -0.045776 | -0.07782 | -0.045776 | 0.086975 | 0.022888 | 4.866 | 4.7562 | -114.061 | 4.866 | 4.9164 | 0.16022 | -113.9877 | 4.9026 | 4.8386 | -114.1113 | 4.8431 | 4.7699 | -0.068664 | -114.0793 | 4.7882 | 4.8614 | 4.9026 | -114.093 | 4.7379 | 4.7699 | 4.9301 | -114.0106
3252.2969 | 119.0186 | -4.454 | 114.6011 | -0.0049592 | 0.012773 | 0.017336 | 0.0023156 | 0.031014 | 0.0015637 | -0.0429 | 0.0021363 | 0.0083335 | -0.01442 | 0.0018137 | 2.5831 | 0.027923 | 0.022888 | -0.004578 | 0.054932 | 0.082397 | -0.004578 | 0.036621 | -0.073242 | 0.032043 | 0.082397 | -0.045776 | -0.064087 | -0.054932 | 0.068665 | 0.018311 | 4.4907 | 4.3808 | -114.6057 | 4.4495 | 4.5364 | 0.15564 | -114.5782 | 4.5227 | 4.4724 | -114.6652 | 4.4861 | 4.4083 | -0.064087 | -114.6561 | 4.4495 | 4.4769 | 4.509 | -114.6744 | 4.39 | 4.3991 | 4.5364 | -114.5828
3254.0781 | 118.8904 | -5.6534 | 113.3148 | -0.0049592 | 0.01854 | 0.016481 | 0.0053064 | 0.032723 | 0.0045545 | -0.043327 | -0.013123 | 0.014528 | -0.012924 | 0.00031831 | 2.6085 | 0.024291 | 0.032043 | -0.041199 | 0.009155 | 0.073242 | 0.018311 | 0.013733 | -0.10529 | -0.018311 | 0.022888 | -0.12817 | -0.036621 | -0.009155 | 0.054932 | -0.009155 | 5.6671 | 5.5481 | -113.2965 | 5.6122 | 5.7266 | 0.17853 | -113.2828 | 5.7083 | 5.6442 | -113.3514 | 5.6351 | 5.5252 | -0.11902 | -113.324 | 5.6717 | 5.6854 | 5.6625 | -113.4201 | 5.6168 | 5.6442 | 5.6763 | -113.324
3255.8594 | 118.2358 | -9.8557 | 108.3069 | -0.020218 | 0.014268 | 0.019685 | 0.0014612 | 0.034645 | -0.0044177 | -0.045677 | -0.020752 | 0.0066245 | -0.013565 | -0.0016043 | 2.5748 | 0.025786 | 0.018311 | 0.054932 | 0.082397 | 0.10529 | -0.013733 | 0.041199 | -0.054932 | 0 | 0.14191 | -0.036621 | -0.064087 | -0.041199 | 0.068665 | 0.013733 | 9.8969 | 9.8007 | -108.3206 | 9.9106 | 9.9609 | 0.16022 | -108.2886 | 9.9243 | 9.8694 | -108.371 | 9.8557 | 9.819 | -0.050354 | -108.3481 | 9.8419 | 9.874 | 9.938 | -108.3618 | 9.7916 | 9.8145 | 9.9976 | -108.2932
3257.5781 | 118.2266 | -9.787 | 108.3252 | -0.012589 | 0.012559 | 0.016908 | -0.0011024 | 0.029732 | 0.0039135 | -0.043327 | -0.0054932 | 0.012179 | -0.013779 | 0.0013863 | 2.5667 | 0.026214 | -0.027466 | -0.082397 | -0.041199 | 0.018311 | 0.032043 | 0.013733 | -0.11444 | -0.050354 | -0.004578 | -0.14648 | -0.045776 | -0.013733 | 0.068665 | -0.018311 | 9.8007 | 9.6725 | -108.2932 | 9.7046 | 9.8053 | 0.13275 | -108.3527 | 9.8557 | 9.7687 | -108.371 | 9.7366 | 9.6405 | -0.12817 | -108.3389 | 9.819 | 9.7595 | 9.7458 | -108.4396 | 9.7412 | 9.7733 | 9.7824 | -108.3435
3259.375 | 117.5858 | -14.3646 | 102.9739 | -0.012589 | 0.011064 | 0.01584 | -0.00024778 | 0.032723 | 0.00028207 | -0.044182 | -0.013123 | 0.0074789 | -0.015915 | -0.0018179 | 2.5508 | 0.027709 | 0.013733 | 0.041199 | 0.064087 | 0.086975 | 0 | 0.041199 | -0.068665 | -0.032043 | 0.082397 | -0.091553 | -0.032043 | -0.036621 | 0.050354 | -0.004578 | 14.4058 | 14.296 | -102.9739 | 14.4058 | 14.4516 | 0.15564 | -102.9602 | 14.415 | 14.36 | -103.006 | 14.3326 | 14.2731 | -0.086975 | -103.0106 | 14.3646 | 14.3784 | 14.4287 | -103.0426 | 14.3326 | 14.328 | 14.447 | -102.9785
3261.1562 | 117.7917 | -14.5569 | 103.1387 | -0.0049592 | 0.010423 | 0.016908 | 0.002102 | 0.033577 | -0.0014269 | -0.0476 | -0.013123 | 0.0096151 | -0.013779 | -0.00074989 | 2.635 | 0.027282 | 0.045776 | 0.054932 | 0.082397 | 0.11444 | -0.027466 | 0.064087 | -0.045776 | 0.009155 | 0.10986 | -0.018311 | -0.064087 | -0.054932 | 0.086975 | 0.022888 | 14.621 | 14.5111 | -103.1662 | 14.6118 | 14.6713 | 0.16022 | -103.093 | 14.6439 | 14.5798 | -103.2028 | 14.566 | 14.5386 | -0.041199 | -103.1937 | 14.5294 | 14.6027 | 14.6393 | -103.1845 | 14.4928 | 14.502 | 14.6667 | -103.1158
3262.8594 | 117.7963 | -9.2422 | 108.7372 | -0.012589 | 0.016191 | 0.01819 | 0.0018884 | 0.032082 | 0.0032727 | -0.044609 | 0.0021363 | 0.010897 | -0.014633 | -0.00074989 | 2.6745 | 0.027068 | -0.054932 | -0.054932 | -0.018311 | 0.050354 | 0.022888 | 0.018311 | -0.10529 | -0.036621 | 0.022888 | -0.1236 | -0.027466 | -0.032043 | 0.045776 | -0.027466 | 9.2606 | 9.137 | -108.7143 | 9.1873 | 9.2926 | 0.15564 | -108.7921 | 9.288 | 9.2148 | -108.7646 | 9.2056 | 9.1187 | -0.09613 | -108.7692 | 9.2651 | 9.1873 | 9.2239 | -108.8425 | 9.2148 | 9.2102 | 9.2651 | -108.7646
3264.6562 | 117.8833 | -10.6476 | 107.0938 | -0.020218 | 0.014695 | 0.016695 | 0.0029566 | 0.032295 | -0.0018543 | -0.044395 | -0.013123 | 0.0083335 | -0.013351 | 0.00053191 | 2.6301 | 0.028991 | 0.009155 | 0.041199 | 0.059509 | 0.091553 | -0.018311 | 0.045776 | -0.082397 | -0.045776 | 0.073242 | -0.073242 | -0.032043 | -0.018311 | 0.068665 | -0.009155 | 10.6934 | 10.5652 | -107.1121 | 10.6888 | 10.7391 | 0.17395 | -107.0847 | 10.7162 | 10.6384 | -107.1259 | 10.6018 | 10.5743 | -0.064087 | -107.1121 | 10.6293 | 10.6567 | 10.7071 | -107.1762 | 10.6155 | 10.6293 | 10.7208 | -107.103
3266.375 | 118.1076 | -8.8257 | 109.0118 | -0.0049592 | 0.013841 | 0.016481 | -3.4178e-05 | 0.030159 | 0.0032727 | -0.044395 | -0.0054932 | 0.012179 | -0.012497 | 0.00053191 | 2.5852 | 0.026427 | -0.073242 | -0.10071 | -0.07782 | 0.013733 | 0.022888 | 0.018311 | -0.10986 | -0.068665 | -0.032043 | -0.17853 | -0.022888 | -0.004578 | 0.041199 | -0.022888 | 8.844 | 8.7158 | -108.989 | 8.725 | 8.8394 | 0.1236 | -109.0851 | 8.8669 | 8.8028 | -109.0347 | 8.757 | 8.6472 | -0.15564 | -109.0164 | 8.8486 | 8.7524 | 8.7479 | -109.1217 | 8.8028 | 8.8211 | 8.7936 | -109.0347
3268.1562 | 117.1188 | -8.7799 | 108.2932 | -0.0049592 | 0.010636 | 0.017763 | 0.0025292 | 0.032082 | -0.0050585 | -0.044182 | -0.0054932 | 0.0059837 | -0.013779 | -0.0016043 | 2.6043 | 0.030486 | -0.050354 | -0.013733 | 0.032043 | 0.073242 | 0.004578 | 0.036621 | -0.064087 | -0.036621 | 0.07782 | -0.064087 | -0.045776 | -0.041199 | 0.068665 | -0.009155 | 8.8165 | 8.7158 | -108.2886 | 8.7662 | 8.8531 | 0.13733 | -108.3435 | 8.8486 | 8.7708 | -108.3389 | 8.7433 | 8.7158 | -0.054932 | -108.3344 | 8.7845 | 8.7296 | 8.8119 | -108.3572 | 8.7341 | 8.7387 | 8.8577 | -108.3023
3269.875 | 118.5928 | -7.9514 | 111.0947 | -0.0049592 | 0.013841 | 0.016054 | -0.00046138 | 0.035713 | 0.00092287 | -0.044609 | 0.0021363 | 0.0091879 | -0.014847 | -0.00032249 | 2.6162 | 0.025786 | -0.018311 | -0.036621 | 0.018311 | 0.054932 | 0.018311 | 0.032043 | -0.082397 | 0 | 0.068665 | -0.064087 | -0.059509 | -0.054932 | 0.073242 | 0.009155 | 7.9834 | 7.869 | -111.0764 | 7.9147 | 8.0063 | 0.13733 | -111.113 | 8.0246 | 7.9605 | -111.1542 | 7.9514 | 7.8873 | -0.073242 | -111.1496 | 7.9697 | 7.933 | 7.9697 | -111.1771 | 7.8918 | 7.8964 | 8.02 | -111.0855
3271.6562 | 117.8101 | -10.3775 | 107.3639 | -0.012589 | 0.0061501 | 0.019685 | -0.0011024 | 0.031014 | -0.0020679 | -0.046104 | -0.0054932 | 0.0079063 | -0.017624 | -0.0022453 | 2.6617 | 0.029845 | 0.022888 | 0.082397 | 0.07782 | 0.10986 | -0.018311 | 0.036621 | -0.050354 | 0.004578 | 0.13733 | -0.022888 | -0.064087 | -0.041199 | 0.068665 | 0.013733 | 10.4141 | 10.3271 | -107.3822 | 10.4599 | 10.4874 | 0.16022 | -107.341 | 10.4462 | 10.3912 | -107.428 | 10.3821 | 10.3546 | -0.036621 | -107.4051 | 10.3592 | 10.4004 | 10.4553 | -107.4142 | 10.3134 | 10.3363 | 10.5148 | -107.3502
3273.375 | 117.8284 | -8.6197 | 109.0256 | -0.0049592 | 0.016191 | 0.016695 | 0.00039302 | 0.03315 | 0.0064771 | -0.042473 | -0.013123 | 0.012606 | -0.014847 | -0.00053629 | 2.6624 | 0.024505 | 0.004578 | -0.009155 | 0 | 0.068665 | 0.013733 | 0.022888 | -0.086975 | 0.054932 | 0.018311 | -0.12817 | -0.050354 | -0.022888 | 0.045776 | -0.013733 | 8.6426 | 8.5327 | -109.0118 | 8.6105 | 8.6884 | 0.15564 | -109.021 | 8.6655 | 8.606 | -109.0759 | 8.6746 | 8.4915 | -0.11444 | -109.0485 | 8.6334 | 8.6243 | 8.6197 | -109.1125 | 8.5693 | 8.5968 | 8.638 | -109.0393
3275.1562 | 117.2333 | -15.9897 | 101.0788 | -0.012589 | 0.016404 | 0.014558 | 0.0046656 | 0.032936 | 0.0015637 | -0.046959 | 0.0021363 | 0.010256 | -0.010361 | 0.0013863 | 2.5111 | 0.027282 | -0.064087 | -0.054932 | -0.036621 | 0.027466 | 0.018311 | 0.013733 | -0.10986 | -0.086975 | 0.018311 | -0.15564 | -0.018311 | 0.018311 | 0.032043 | -0.022888 | 16.0034 | 15.8798 | -101.0605 | 15.9348 | 16.0172 | 0.13733 | -101.1429 | 16.0217 | 15.9668 | -101.0971 | 15.9027 | 15.834 | -0.13275 | -101.0605 | 16.008 | 15.9256 | 15.9531 | -101.1887 | 15.9714 | 16.008 | 16.008 | -101.1017
3276.9375 | 118.0115 | -11.3022 | 106.8832 | -0.012589 | 0.014054 | 0.019685 | 0.0044518 | 0.034432 | -0.0012133 | -0.043968 | -0.0054932 | 0.0098289 | -0.012924 | -0.00032249 | 2.601 | 0.027923 | -0.064087 | -0.073242 | -0.027466 | 0.032043 | 0.022888 | -0.004578 | -0.10071 | -0.10529 | 0.004578 | -0.14648 | -0.018311 | 0 | 0.032043 | -0.018311 | 11.2976 | 11.2015 | -106.8604 | 11.2289 | 11.3342 | 0.13275 | -106.9473 | 11.3342 | 11.2839 | -106.9016 | 11.1969 | 11.1557 | -0.12817 | -106.8832 | 11.3251 | 11.2381 | 11.2747 | -106.9839 | 11.2839 | 11.3022 | 11.3068 | -106.9016
3278.7188 | 117.5491 | -14.4424 | 102.8687 | -0.012589 | 0.012773 | 0.016481 | -0.001316 | 0.031227 | -0.0014269 | -0.043113 | -0.020752 | 0.0094015 | -0.015274 | 0.00010471 | 2.6318 | 0.026855 | 0.036621 | 0.059509 | 0.059509 | 0.13275 | -0.027466 | 0.054932 | -0.07782 | 0.045776 | 0.10071 | -0.009155 | -0.082397 | -0.050354 | 0.073242 | 0.032043 | 14.4974 | 14.3646 | -102.8961 | 14.502 | 14.5752 | 0.21057 | -102.832 | 14.5157 | 14.4745 | -102.951 | 14.4882 | 14.4333 | -0.041198 | -102.919 | 14.415 | 14.4791 | 14.502 | -102.9465 | 14.36 | 14.3921 | 14.5432 | -102.8366
3280.4375 | 116.7618 | -7.814 | 107.785 | -0.012589 | 0.012986 | 0.016908 | 0.001034 | 0.032936 | 0.0043409 | -0.043113 | -0.0054932 | 0.01111 | -0.01442 | 0.00095911 | 2.5395 | 0.028777 | -0.068665 | -0.10986 | -0.068665 | 0.022888 | 0.027466 | 0.022888 | -0.10071 | -0.091553 | -0.041199 | -0.17395 | -0.032043 | 0 | 0.022888 | -0.013733 | 7.8369 | 7.7133 | -107.7576 | 7.7042 | 7.8369 | 0.1236 | -107.8537 | 7.8369 | 7.8003 | -107.8171 | 7.7225 | 7.6401 | -0.16022 | -107.785 | 7.8415 | 7.7454 | 7.7454 | -107.8857 | 7.782 | 7.814 | 7.7728 | -107.7988
3282.2188 | 118.0206 | -9.5718 | 108.2108 | -0.012589 | 0.011491 | 0.019899 | 0.0042382 | 0.033577 | -0.0065539 | -0.044182 | -0.013123 | 0.0079063 | -0.013992 | -0.0013907 | 2.5423 | 0.027282 | -0.041199 | 0.018311 | 0.041199 | 0.07782 | -0.009155 | 0.059509 | -0.073242 | -0.032043 | 0.082397 | -0.027466 | -0.068665 | -0.059509 | 0.07782 | 0 | 9.6313 | 9.4986 | -108.2199 | 9.5901 | 9.6497 | 0.15106 | -108.252 | 9.6497 | 9.5718 | -108.2794 | 9.5398 | 9.5444 | -0.027466 | -108.2703 | 9.5627 | 9.5306 | 9.613 | -108.284 | 9.5032 | 9.5123 | 9.6542 | -108.2108
3283.9844 | 118.5837 | -2.504 | 115.9653 | -0.012589 | 0.0095681 | 0.019045 | 0.0023156 | 0.034432 | -0.0033495 | -0.043541 | -0.0054932 | 0.0083335 | -0.01442 | 0.00031831 | 2.6263 | 0.029418 | 0.009155 | 0.022888 | 0.054932 | 0.068665 | -0.013733 | 0.036621 | -0.059509 | -0.032043 | 0.045776 | -0.07782 | -0.064087 | -0.036621 | 0.068665 | -0.004578 | 2.5406 | 2.4445 | -115.979 | 2.5269 | 2.5726 | 0.12817 | -115.9561 | 2.5726 | 2.4994 | -116.0294 | 2.4719 | 2.4261 | -0.073242 | -116.0019 | 2.4902 | 2.5131 | 2.5589 | -116.0248 | 2.4399 | 2.4673 | 2.5497 | -115.9698
3285.7656 | 118.7576 | -5.8319 | 112.9486 | -0.012589 | 0.014054 | 0.016267 | -0.00067498 | 0.033791 | 0.0039135 | -0.045463 | -0.0054932 | 0.012392 | -0.014206 | 0.0022409 | 2.5122 | 0.025573 | -0.041199 | -0.11444 | -0.059509 | 0.022888 | 0.022888 | 0.009155 | -0.09613 | -0.082397 | -0.045776 | -0.17853 | -0.018311 | 0.004578 | 0.041199 | -0.018311 | 5.8411 | 5.7358 | -112.9257 | 5.7175 | 5.8548 | 0.11902 | -112.9898 | 5.8731 | 5.8136 | -112.9669 | 5.7495 | 5.6534 | -0.16022 | -112.944 | 5.8548 | 5.7907 | 5.7724 | -113.0447 | 5.8136 | 5.8365 | 5.7861 | -112.9669
3287.5469 | 119.371 | -0.90179 | 118.5287 | -0.012589 | 0.020677 | 0.016908 | 0.0025292 | 0.035073 | 0.0024183 | -0.04525 | -0.0054932 | 0.013674 | -0.013992 | -0.00096349 | 2.5451 | 0.026214 | -0.013733 | -0.032043 | -0.022888 | 0.064087 | 0.013733 | 0.022888 | -0.10986 | -0.041199 | 0.036621 | -0.1236 | -0.032043 | -0.022888 | 0.059509 | -0.018311 | 0.92468 | 0.79193 | -118.515 | 0.86975 | 0.96588 | 0.17395 | -118.5425 | 0.9613 | 0.88348 | -118.5608 | 0.86059 | 0.7782 | -0.10528 | -118.5516 | 0.91553 | 0.88806 | 0.87891 | -118.6386 | 0.86975 | 0.87891 | 0.93841 | -118.5471
3289.2656 | 119.5679 | -0.76904 | 118.6615 | -0.0049592 | 0.012132 | 0.019258 | 0.001034 | 0.032723 | -0.0050585 | -0.04525 | -0.020752 | 0.0068381 | -0.013565 | -0.00053629 | 2.5827 | 0.029204 | -0.050354 | -0.022888 | 0.032043 | 0.064087 | -0.018311 | 0.041199 | -0.082397 | -0.045776 | 0.068665 | -0.050354 | -0.068665 | -0.054932 | 0.07782 | 0 | 0.81024 | 0.68665 | -118.6798 | 0.74616 | 0.83313 | 0.14648 | -118.7119 | 0.84686 | 0.76904 | -118.7302 | 0.72327 | 0.71869 | -0.050354 | -118.7164 | 0.75073 | 0.71869 | 0.80109 | -118.7439 | 0.70038 | 0.71411 | 0.83771 | -118.6615
3291.0469 | 119.3344 | -1.3275 | 118.0618 | -0.0049592 | 0.0132 | 0.018831 | 0.00082022 | 0.0355 | -0.0016405 | -0.04525 | -0.0054932 | 0.0083335 | -0.013351 | -0.0018179 | 2.5573 | 0.02835 | 0.027466 | 0.054932 | 0.07782 | 0.10529 | -0.013733 | 0.041199 | -0.07782 | -0.004578 | 0.1236 | -0.041199 | -0.073242 | -0.050354 | 0.068665 | -0.004578 | 1.3687 | 1.2497 | -118.0756 | 1.3824 | 1.4328 | 0.18311 | -118.0344 | 1.3962 | 1.3229 | -118.1351 | 1.3229 | 1.2863 | -0.036621 | -118.1122 | 1.3138 | 1.355 | 1.4053 | -118.1396 | 1.2543 | 1.2772 | 1.4511 | -118.0664
3292.8281 | 119.6869 | -0.84686 | 118.7439 | -0.0049592 | 0.012132 | 0.018831 | 0.0029566 | 0.034004 | -0.0016405 | -0.046104 | -0.013123 | 0.0066245 | -0.016129 | -0.00096349 | 2.5359 | 0.027282 | -0.013733 | 0.022888 | 0.054932 | 0.073242 | -0.018311 | 0.036621 | -0.068665 | -0.022888 | 0.050354 | -0.073242 | -0.059509 | -0.027466 | 0.059509 | -0.009155 | 0.88348 | 0.7782 | -118.7622 | 0.86975 | 0.92011 | 0.14191 | -118.7576 | 0.90637 | 0.83771 | -118.8034 | 0.82398 | 0.77362 | -0.064087 | -118.7714 | 0.82855 | 0.83313 | 0.9018 | -118.8126 | 0.78735 | 0.8194 | 0.89722 | -118.7531
3294.6094 | 119.7647 | -0.99792 | 118.602 | -0.012589 | 0.011704 | 0.017549 | 0.0029566 | 0.032082 | -0.0018543 | -0.048668 | -0.013123 | 0.0064109 | -0.015488 | -0.0018179 | 2.5906 | 0.026427 | 0.041199 | 0.054932 | 0.073242 | 0.09613 | -0.018311 | 0.036621 | -0.054932 | 0.032043 | 0.12817 | 0.004578 | -0.059509 | -0.064087 | 0.086975 | 0.018311 | 1.0345 | 0.94299 | -118.6203 | 1.0529 | 1.0941 | 0.15106 | -118.5608 | 1.0849 | 1.0162 | -118.6615 | 1.03 | 1.0025 | -0.013733 | -118.6661 | 0.97961 | 1.0391 | 1.0712 | -118.6569 | 0.93842 | 0.93384 | 1.1261 | -118.5837
3296.3906 | 119.8425 | -0.81024 | 118.9178 | -0.012589 | 0.011918 | 0.01819 | 0.0023156 | 0.032723 | -0.0035633 | -0.046959 | -0.013123 | 0.0085471 | -0.015701 | -0.0013907 | 2.6183 | 0.024077 | 0.045776 | 0.091553 | 0.09613 | 0.10529 | -0.013733 | 0.036621 | -0.059509 | 0.027466 | 0.1236 | 0.004578 | -0.07782 | -0.059509 | 0.068665 | 0 | 0.84686 | 0.75073 | -118.9316 | 0.9018 | 0.91553 | 0.16479 | -118.8721 | 0.87891 | 0.81024 | -118.9957 | 0.83771 | 0.81482 | 0.004578 | -118.9774 | 0.79651 | 0.85602 | 0.90637 | -118.9774 | 0.73242 | 0.75073 | 0.93384 | -118.9178
3298.0938 | 119.9066 | -0.78735 | 118.9316 | -0.012589 | 0.012132 | 0.014772 | -0.0019568 | 0.0308 | 0.0051953 | -0.045677 | -0.0054932 | 0.011751 | -0.014206 | -0.00032249 | 2.6166 | 0.022796 | -0.018311 | -0.064087 | -0.013733 | 0.022888 | 0 | 0.018311 | -0.086975 | -0.009155 | 0.027466 | -0.09613 | -0.054932 | -0.050354 | 0.068665 | 0.004578 | 0.80566 | 0.70038 | -118.9316 | 0.72327 | 0.81024 | 0.10986 | -118.9499 | 0.85602 | 0.79193 | -118.9865 | 0.7782 | 0.69122 | -0.10071 | -118.9819 | 0.78735 | 0.76904 | 0.77362 | -119.0186 | 0.73242 | 0.737 | 0.81482 | -118.927
3299.875 | 119.8013 | -0.85602 | 119.0277 | -0.0049592 | 0.017686 | 0.017549 | -0.0019568 | 0.03315 | 0.0045545 | -0.043113 | -0.013123 | 0.013674 | -0.014206 | 0.00074551 | 2.5951 | 0.026214 | -0.027466 | -0.059509 | -0.036621 | 0.032043 | 0 | 0.013733 | -0.10071 | -0.054932 | -0.032043 | -0.1831 | -0.036621 | -0.013733 | 0.036621 | -0.041199 | 0.86975 | 0.75531 | -119.0277 | 0.79651 | 0.88806 | 0.13275 | -119.0552 | 0.89264 | 0.81482 | -119.0643 | 0.80109 | 0.67291 | -0.14191 | -119.0414 | 0.85602 | 0.82855 | 0.8194 | -119.1284 | 0.8194 | 0.84228 | 0.82397 | -119.0689
3301.6094 | 119.8563 | -0.86517 | 119.0781 | -0.012589 | 0.017472 | 0.016908 | -0.0019568 | 0.034004 | 0.0041273 | -0.041832 | -0.0054932 | 0.01111 | -0.013779 | -0.0013907 | 2.5585 | 0.027282 | -0.045776 | -0.054932 | -0.036621 | 0.018311 | 0 | 0.018311 | -0.10986 | -0.068665 | -0.036621 | -0.19684 | -0.022888 | -0.022888 | 0.032043 | -0.027466 | 0.88348 | 0.75531 | -119.0781 | 0.81024 | 0.88348 | 0.12817 | -119.1238 | 0.89722 | 0.83771 | -119.101 | 0.79651 | 0.66833 | -0.16937 | -119.101 | 0.86517 | 0.8194 | 0.82855 | -119.1879 | 0.84228 | 0.84228 | 0.82855 | -119.1055
3303.3906 | 119.9158 | -0.86975 | 119.1284 | -0.020218 | 0.01555 | 0.018617 | 0.0027428 | 0.032936 | 0.0041273 | -0.043541 | -0.0054932 | 0.01047 | -0.014206 | 0.0011727 | 2.5667 | 0.029204 | -0.068665 | -0.086975 | -0.045776 | 0.018311 | 0.013733 | 0.009155 | -0.10986 | -0.086975 | -0.036621 | -0.19226 | -0.054932 | -0.036621 | 0.032043 | -0.032043 | 0.87891 | 0.75989 | -119.1147 | 0.78278 | 0.88806 | 0.12817 | -119.1971 | 0.90179 | 0.83771 | -119.1833 | 0.78278 | 0.67749 | -0.16022 | -119.165 | 0.88348 | 0.80109 | 0.82398 | -119.2383 | 0.81482 | 0.83313 | 0.83313 | -119.1605
3305.125 | 119.9707 | -0.90637 | 119.1147 | -0.0049592 | 0.016404 | 0.017976 | -0.00024778 | 0.035286 | 0.00092287 | -0.045036 | -0.013123 | 0.012179 | -0.015274 | -0.00010889 | 2.5728 | 0.030059 | -0.086975 | -0.10071 | -0.082397 | 0.032043 | 0.027466 | 0.009155 | -0.10529 | -0.10071 | -0.036621 | -0.20142 | -0.032043 | -0.027466 | 0.022888 | -0.009155 | 0.91553 | 0.80109 | -119.0872 | 0.80566 | 0.93841 | 0.13733 | -119.2017 | 0.92926 | 0.89722 | -119.1467 | 0.80566 | 0.70496 | -0.19226 | -119.1422 | 0.93384 | 0.8194 | 0.82397 | -119.22 | 0.87433 | 0.87891 | 0.86975 | -119.1238
3306.9062 | 120.0943 | -0.83771 | 119.1238 | -0.0049592 | 0.011704 | 0.015627 | -0.00067498 | 0.031655 | -0.0016405 | -0.041832 | -0.0054932 | 0.0081199 | -0.016769 | -0.0016043 | 2.5085 | 0.027923 | 0.009155 | 0.059509 | 0.09613 | 0.10529 | -0.027466 | 0.050354 | -0.054932 | 0.013733 | 0.11444 | -0.022888 | -0.086975 | -0.054932 | 0.073242 | 0.009155 | 0.88806 | 0.78278 | -119.1513 | 0.89722 | 0.94299 | 0.16022 | -119.1147 | 0.91095 | 0.84686 | -119.2108 | 0.85144 | 0.81482 | -0.032043 | -119.1788 | 0.81024 | 0.84686 | 0.93384 | -119.1788 | 0.75073 | 0.78278 | 0.95215 | -119.1147
3308.625 | 120.0394 | -0.89264 | 119.1696 | 0.0026703 | 0.013841 | 0.017763 | 0.00060662 | 0.03315 | 0.0013501 | -0.042045 | -0.013123 | 0.01047 | -0.012497 | 0.00053191 | 2.5728 | 0.027709 | 0.004578 | -0.022888 | 0.018311 | 0.064087 | 0.013733 | 0.022888 | -0.091553 | -0.041199 | 0.054932 | -0.1236 | -0.050354 | -0.036621 | 0.041199 | -0.018311 | 0.91553 | 0.80109 | -119.1559 | 0.86975 | 0.95673 | 0.15564 | -119.165 | 0.93384 | 0.87433 | -119.22 | 0.85144 | 0.76904 | -0.10528 | -119.2062 | 0.90637 | 0.89722 | 0.91095 | -119.2612 | 0.84228 | 0.85602 | 0.94757 | -119.1879
3310.4062 | 120.1859 | -0.86975 | 119.1925 | -0.0049592 | 0.0074319 | 0.017976 | 0.0031702 | 0.030586 | -0.0056995 | -0.045036 | -0.0054932 | 0.0087607 | -0.013779 | 0.00031831 | 2.6485 | 0.029418 | -0.041199 | -0.018311 | 0.036621 | 0.064087 | -0.018311 | 0.032043 | -0.068665 | -0.068665 | 0.054932 | -0.073242 | -0.07782 | -0.045776 | 0.054932 | 0.004578 | 0.90179 | 0.80109 | -119.2108 | 0.85144 | 0.93384 | 0.13275 | -119.2337 | 0.92468 | 0.87433 | -119.2703 | 0.80109 | 0.79651 | -0.07782 | -119.2383 | 0.85144 | 0.82855 | 0.90637 | -119.2612 | 0.79193 | 0.82398 | 0.92468 | -119.1879
3312.125 | 120.1172 | -0.90179 | 119.2657 | -0.012589 | 0.016191 | 0.017336 | 0.0027428 | 0.034432 | 0.0024183 | -0.043327 | -0.013123 | 0.011324 | -0.013138 | 0.0016001 | 2.6162 | 0.026 | -0.091553 | -0.14191 | -0.073242 | 0.009155 | 0.018311 | 0.018311 | -0.11902 | -0.091553 | -0.054932 | -0.17853 | -0.041199 | -0.027466 | 0.041199 | -0.022888 | 0.9201 | 0.78277 | -119.2474 | 0.75989 | 0.91095 | 0.12817 | -119.3573 | 0.94299 | 0.87891 | -119.3069 | 0.81024 | 0.72327 | -0.15564 | -119.2932 | 0.9201 | 0.81024 | 0.82855 | -119.3848 | 0.86059 | 0.87433 | 0.84686 | -119.2886
3313.9062 | 120.1813 | -0.92926 | 119.2657 | -0.012589 | 0.0132 | 0.017122 | 0.00060662 | 0.033577 | 0.00092287 | -0.043968 | -0.020752 | 0.012606 | -0.012711 | 0.00074551 | 2.625 | 0.026214 | -0.032043 | -0.036621 | 0.022888 | 0.073242 | 0.032043 | 0.004578 | -0.10071 | -0.036621 | 0.050354 | -0.11444 | -0.045776 | -0.027466 | 0.054932 | -0.018311 | 0.93384 | 0.82855 | -119.2337 | 0.89264 | 1.0025 | 0.17395 | -119.2978 | 0.98419 | 0.91095 | -119.3115 | 0.89264 | 0.81482 | -0.09613 | -119.2932 | 0.9613 | 0.89722 | 0.95215 | -119.3665 | 0.88348 | 0.90179 | 0.97961 | -119.2841
3315.7031 | 120.3186 | -0.90637 | 119.2566 | -0.012589 | 0.010423 | 0.016695 | -0.00024778 | 0.032936 | 6.8274e-05 | -0.044609 | 0.0021363 | 0.0066245 | -0.014847 | 0.0022409 | 2.6455 | 0.028991 | 0.013733 | 0.004578 | 0.059509 | 0.09613 | 0 | 0.027466 | -0.07782 | 0.018311 | 0.10071 | -0.036621 | -0.09613 | -0.059509 | 0.068665 | 0.032043 | 0.93384 | 0.82855 | -119.2566 | 0.91095 | 1.0025 | 0.17395 | -119.2429 | 0.97504 | 0.93841 | -119.3527 | 0.92468 | 0.86975 | -0.068664 | -119.3161 | 0.90637 | 0.9201 | 0.96588 | -119.3344 | 0.81024 | 0.84686 | 1.0071 | -119.2245
3317.4688 | 120.3003 | -0.93384 | 119.2612 | -0.012589 | 0.011704 | 0.015413 | -0.00067498 | 0.0308 | -0.0018543 | -0.043541 | -0.0054932 | 0.0074789 | -0.013565 | 0.0016001 | 2.5961 | 0.025573 | 0.032043 | 0.050354 | 0.09613 | 0.10529 | -0.041199 | 0.054932 | -0.073242 | 0.004578 | 0.10071 | -0.018311 | -0.073242 | -0.041199 | 0.07782 | 0.022888 | 0.98877 | 0.8606 | -119.3024 | 0.98419 | 1.0391 | 0.17853 | -119.2291 | 1.0117 | 0.95673 | -119.3344 | 0.93842 | 0.91553 | -0.041199 | -119.3024 | 0.89264 | 0.96588 | 1.03 | -119.3344 | 0.8606 | 0.89264 | 1.0345 | -119.2383
3319.2031 | 120.3781 | -0.95673 | 119.2886 | -0.020218 | 0.011064 | 0.017122 | 0.0053064 | 0.03315 | -0.0046313 | -0.047172 | -0.0054932 | 0.0076925 | -0.01442 | -0.00096349 | 2.6365 | 0.028777 | -0.054932 | -0.018311 | 0.032043 | 0.068665 | -0.009155 | 0.036621 | -0.082397 | -0.041199 | 0.068665 | -0.059509 | -0.064087 | -0.036621 | 0.050354 | -0.013733 | 0.99335 | 0.87433 | -119.2978 | 0.93841 | 1.0254 | 0.15106 | -119.3436 | 1.0071 | 0.94299 | -119.3527 | 0.91553 | 0.89722 | -0.045776 | -119.3253 | 0.94757 | 0.90179 | 0.98877 | -119.371 | 0.89264 | 0.9201 | 1.0254 | -119.3024
3320.9844 | 120.2957 | -1.0071 | 119.339 | -0.0049592 | 0.015122 | 0.019899 | 0.0031702 | 0.032295 | -0.0012133 | -0.0476 | -0.013123 | 0.0059837 | -0.014847 | 0.00074551 | 2.6216 | 0.026855 | 0.018311 | 0.041199 | 0.082397 | 0.10986 | -0.009155 | 0.059509 | -0.068665 | -0.018311 | 0.10986 | -0.064087 | -0.064087 | -0.045776 | 0.054932 | -0.018311 | 1.0666 | 0.93841 | -119.3481 | 1.0483 | 1.1169 | 0.17853 | -119.3207 | 1.062 | 0.98877 | -119.4031 | 0.98877 | 0.94299 | -0.045776 | -119.3848 | 0.99792 | 1.0254 | 1.0895 | -119.4077 | 0.94299 | 0.9613 | 1.1169 | -119.3573
3322.7656 | 120.4605 | -0.97961 | 119.2932 | -0.012589 | 0.011704 | 0.017336 | -0.0011024 | 0.030159 | 0.0030591 | -0.043754 | -0.013123 | 0.0091879 | -0.014206 | 0.00031831 | 2.6457 | 0.024505 | -0.009155 | -0.022888 | 0 | 0.054932 | 0.018311 | 0.036621 | -0.086975 | 0.004578 | 0.059509 | -0.073242 | -0.082397 | -0.073242 | 0.073242 | 0.009155 | 1.0162 | 0.89264 | -119.2749 | 0.95673 | 1.0345 | 0.14191 | -119.3024 | 1.0529 | 0.98877 | -119.3756 | 0.98419 | 0.90637 | -0.082397 | -119.3665 | 0.99792 | 0.97046 | 0.97961 | -119.3802 | 0.89722 | 0.90637 | 1.0391 | -119.2841
3324.5469 | 120.4788 | -0.97961 | 119.3527 | -0.012589 | 0.0063639 | 0.019472 | 0.00039302 | 0.030159 | -0.0033495 | -0.044395 | -0.028381 | 0.0087607 | -0.015274 | -0.0016043 | 2.5808 | 0.028777 | -0.041199 | -0.013733 | 0.027466 | 0.064087 | -0.004578 | 0.036621 | -0.073242 | -0.036621 | 0.064087 | -0.059509 | -0.064087 | -0.045776 | 0.059509 | 0.004578 | 1.0162 | 0.90637 | -119.3573 | 0.96588 | 1.0437 | 0.13733 | -119.3939 | 1.0391 | 0.98419 | -119.4168 | 0.94299 | 0.9201 | -0.064087 | -119.3985 | 0.97504 | 0.93841 | 1.0071 | -119.426 | 0.91553 | 0.93384 | 1.0437 | -119.3481
3326.3438 | 120.369 | -1.0208 | 119.3939 | 0.0103 | 0.013841 | 0.017549 | -0.00046138 | 0.032295 | 0.0051953 | -0.043754 | -0.013123 | 0.011965 | -0.014633 | 0.0016001 | 2.6391 | 0.026855 | -0.073242 | -0.1236 | -0.073242 | 0.004578 | 0.027466 | 0.004578 | -0.11444 | -0.07782 | -0.054932 | -0.17395 | -0.036621 | -0.036621 | 0.032043 | -0.027466 | 1.0254 | 0.90637 | -119.3665 | 0.89722 | 1.0254 | 0.11902 | -119.4672 | 1.0529 | 0.99335 | -119.4305 | 0.94299 | 0.84686 | -0.14648 | -119.4305 | 1.0483 | 0.94757 | 0.94757 | -119.5084 | 0.98419 | 0.98419 | 0.96588 | -119.4214
3328.0469 | 120.3918 | -1.0254 | 119.4077 | -0.0049592 | 0.013841 | 0.016481 | 0.001034 | 0.031655 | 0.0041273 | -0.043541 | -0.020752 | 0.013247 | -0.013565 | -0.0013907 | 2.6333 | 0.027068 | -0.068665 | -0.11902 | -0.073242 | 0.009155 | 0.013733 | 0 | -0.10071 | -0.073242 | -0.050354 | -0.1831 | -0.027466 | -0.004578 | 0.054932 | -0.027466 | 1.0254 | 0.92468 | -119.3939 | 0.90637 | 1.0345 | 0.10986 | -119.4763 | 1.0803 | 0.99792 | -119.4351 | 0.95215 | 0.84229 | -0.15564 | -119.4122 | 1.0391 | 0.95673 | 0.95215 | -119.5084 | 0.99792 | 1.0208 | 0.97504 | -119.4351
3329.8281 | 120.4651 | -3.3463 | 117.0547 | -0.012589 | 0.017472 | 0.016908 | 0.00552 | 0.03315 | -0.00035893 | -0.045677 | 0.0021363 | 0.0087607 | -0.011215 | 0.00053191 | 2.5596 | 0.026427 | -0.068665 | -0.073242 | -0.050354 | 0.036621 | 0.032043 | -0.004578 | -0.10986 | -0.091553 | -0.009155 | -0.16937 | -0.013733 | -0.018311 | 0.027466 | -0.032043 | 3.3417 | 3.2364 | -117.0227 | 3.273 | 3.3829 | 0.14648 | -117.1234 | 3.3737 | 3.3142 | -117.0685 | 3.2547 | 3.1769 | -0.13733 | -117.0731 | 3.3783 | 3.2776 | 3.2959 | -117.1646 | 3.3325 | 3.3279 | 3.3371 | -117.0868
3331.5469 | 120.4056 | -5.2917 | 115.1093 | -0.020218 | 0.01555 | 0.017976 | 0.0027428 | 0.033791 | 0.00028207 | -0.045677 | -0.013123 | 0.0087607 | -0.013351 | 0.00010471 | 2.515 | 0.027495 | -0.064087 | -0.054932 | -0.009155 | 0.041199 | 0.022888 | 0.022888 | -0.10986 | -0.10986 | 0 | -0.13733 | -0.022888 | 0 | 0.036621 | -0.022888 | 5.3146 | 5.1819 | -115.0864 | 5.2368 | 5.3329 | 0.15106 | -115.1733 | 5.3284 | 5.2689 | -115.1321 | 5.1819 | 5.1544 | -0.11444 | -115.1093 | 5.3146 | 5.2277 | 5.2826 | -115.2191 | 5.2689 | 5.2917 | 5.2917 | -115.1321
3333.3125 | 120.433 | -6.459 | 113.9648 | 0.0026703 | 0.013627 | 0.01819 | 0.0029566 | 0.033791 | -0.0024951 | -0.046745 | -0.013123 | 0.0094015 | -0.014633 | -0.00032249 | 2.5417 | 0.02835 | -0.068665 | -0.050354 | -0.009155 | 0.032043 | 0.036621 | 0.004578 | -0.11444 | -0.091553 | 0.018311 | -0.15106 | -0.027466 | -0.018311 | 0.032043 | -0.032043 | 6.4636 | 6.3446 | -113.9282 | 6.4087 | 6.4911 | 0.14648 | -114.0335 | 6.4911 | 6.427 | -113.9923 | 6.3675 | 6.308 | -0.11902 | -113.9832 | 6.4957 | 6.3904 | 6.4499 | -114.0793 | 6.4316 | 6.4407 | 6.4774 | -113.9969
3335.0156 | 120.5292 | -7.6355 | 112.7151 | -0.020218 | 0.0132 | 0.016481 | 0.00082022 | 0.03315 | 0.0039135 | -0.042686 | -0.0054932 | 0.013247 | -0.015701 | -0.00010889 | 2.538 | 0.029204 | -0.045776 | -0.086975 | -0.064087 | 0.018311 | 0.018311 | 0.013733 | -0.10071 | -0.07782 | -0.032043 | -0.14648 | -0.013733 | -0.013733 | 0.054932 | -0.018311 | 7.6492 | 7.5348 | -112.6968 | 7.5485 | 7.6538 | 0.11902 | -112.7609 | 7.6904 | 7.6172 | -112.7289 | 7.5577 | 7.489 | -0.12817 | -112.7289 | 7.6538 | 7.5897 | 7.5714 | -112.8159 | 7.6218 | 7.6218 | 7.6035 | -112.7335
3336.8125 | 120.4285 | -6.9855 | 113.443 | -0.012589 | 0.015336 | 0.01584 | -0.0036658 | 0.031868 | 0.0028455 | -0.041618 | -0.013123 | 0.010256 | -0.015915 | -0.00074989 | 2.5421 | 0.02835 | -0.018311 | -0.059509 | -0.013733 | 0.045776 | 0.009155 | 0.009155 | -0.09613 | -0.059509 | -0.004578 | -0.16479 | -0.041199 | -0.022888 | 0.045776 | -0.036621 | 6.9946 | 6.8893 | -113.4338 | 6.926 | 7.0312 | 0.14191 | -113.4613 | 7.0312 | 6.9489 | -113.4842 | 6.926 | 6.8207 | -0.12817 | -113.4659 | 6.9946 | 6.9672 | 6.9717 | -113.5391 | 6.9443 | 6.9626 | 6.9809 | -113.4796
3338.5938 | 120.4788 | -6.5186 | 113.9648 | -0.020218 | 0.015763 | 0.01819 | 0.0029566 | 0.03315 | -0.0024951 | -0.046318 | -0.013123 | 0.0085471 | -0.013351 | 0.0011727 | 2.4891 | 0.028564 | 0.018311 | 0.050354 | 0.086975 | 0.10986 | -0.013733 | 0.041199 | -0.07782 | -0.036621 | 0.10529 | -0.073242 | -0.054932 | -0.009155 | 0.054932 | 0.009155 | 6.5598 | 6.4407 | -113.9786 | 6.5689 | 6.6284 | 0.18768 | -113.9465 | 6.5735 | 6.5277 | -114.0198 | 6.4819 | 6.4453 | -0.082397 | -113.974 | 6.5048 | 6.5369 | 6.6055 | -114.0427 | 6.4636 | 6.5094 | 6.6238 | -113.9557
3340.375 | 120.4788 | -10.08 | 110.408 | -0.012589 | 0.013841 | 0.018831 | 0.0025292 | 0.031655 | -0.0018543 | -0.047172 | 0.0021363 | 0.0091879 | -0.012924 | 0.00031831 | 2.5214 | 0.026855 | -0.068665 | -0.068665 | -0.022888 | 0.032043 | 0.036621 | 0.009155 | -0.091553 | -0.10529 | 0.009155 | -0.14191 | -0.013733 | 0.009155 | 0.018311 | -0.013733 | 10.0891 | 9.9884 | -110.3714 | 10.0113 | 10.112 | 0.1236 | -110.4767 | 10.0983 | 10.0662 | -110.4218 | 9.9747 | 9.938 | -0.12817 | -110.3989 | 10.1166 | 10.0113 | 10.0571 | -110.4996 | 10.0662 | 10.0891 | 10.0891 | -110.4218
3342.1094 | 120.6116 | -11.618 | 108.6823 | -0.012589 | 0.0076455 | 0.018831 | 0.001034 | 0.0308 | -0.0044177 | -0.045463 | -0.020752 | 0.0042747 | -0.014847 | -0.0020315 | 2.4387 | 0.028991 | -0.036621 | 0.009155 | 0.045776 | 0.07782 | 0 | 0.050354 | -0.064087 | -0.022888 | 0.10071 | -0.027466 | -0.050354 | -0.032043 | 0.068665 | 0.004578 | 11.6684 | 11.554 | -108.6823 | 11.6272 | 11.6959 | 0.14191 | -108.7189 | 11.6867 | 11.6226 | -108.7326 | 11.5952 | 11.5906 | -0.032044 | -108.7143 | 11.618 | 11.5814 | 11.6638 | -108.7463 | 11.5677 | 11.586 | 11.7188 | -108.6777
3343.875 | 120.4468 | -16.4795 | 103.8757 | -0.012589 | 0.012986 | 0.017549 | 0.0014612 | 0.032723 | -0.0022815 | -0.04824 | -0.013123 | 0.010256 | -0.014206 | -0.0013907 | 2.497 | 0.026214 | 0.027466 | 0.059509 | 0.082397 | 0.10986 | -0.004578 | 0.054932 | -0.073242 | -0.027466 | 0.11444 | -0.068665 | -0.054932 | -0.009155 | 0.073242 | 0.004578 | 16.5344 | 16.4062 | -103.8803 | 16.539 | 16.5894 | 0.18311 | -103.8483 | 16.5527 | 16.4841 | -103.9307 | 16.452 | 16.4108 | -0.073243 | -103.8849 | 16.4749 | 16.507 | 16.5619 | -103.949 | 16.4246 | 16.4703 | 16.5939 | -103.8712
3345.6562 | 120.5154 | -11.7828 | 108.5449 | -0.0049592 | 0.011918 | 0.017336 | -0.0017432 | 0.031441 | 0.0013501 | -0.045036 | -0.020752 | 0.0074789 | -0.014847 | -0.0018179 | 2.6224 | 0.026641 | 0.045776 | 0.054932 | 0.091553 | 0.10986 | -0.013733 | 0.064087 | -0.050354 | 0.041199 | 0.10529 | -0.022888 | -0.068665 | -0.068665 | 0.073242 | 0.018311 | 11.8469 | 11.7325 | -108.5587 | 11.8378 | 11.8927 | 0.16022 | -108.4991 | 11.8561 | 11.8011 | -108.6136 | 11.824 | 11.7599 | -0.041199 | -108.6136 | 11.7691 | 11.8286 | 11.8744 | -108.5953 | 11.7142 | 11.7142 | 11.8881 | -108.5266
3347.3594 | 120.4697 | -16.0629 | 104.2282 | -0.012589 | 0.010636 | 0.019899 | 0.002102 | 0.03315 | -0.0035633 | -0.046531 | -0.013123 | 0.0081199 | -0.01741 | -0.0016043 | 2.601 | 0.027709 | 0.013733 | 0.045776 | 0.059509 | 0.086975 | 0.004578 | 0.059509 | -0.059509 | -0.032043 | 0.059509 | -0.064087 | -0.059509 | -0.045776 | 0.082397 | 0.009155 | 16.1224 | 16.0034 | -104.2236 | 16.1087 | 16.1499 | 0.14648 | -104.2145 | 16.1453 | 16.0721 | -104.2877 | 16.0309 | 15.9988 | -0.073242 | -104.274 | 16.0675 | 16.0767 | 16.1224 | -104.2877 | 16.0034 | 16.0172 | 16.1224 | -104.2191
3349.1406 | 120.575 | -6.5048 | 113.9465 | -0.020218 | 0.0091409 | 0.016054 | -0.0015296 | 0.029732 | 0.0011365 | -0.043968 | -0.013123 | 0.0070517 | -0.018478 | -0.0033133 | 2.6077 | 0.026427 | 0.054932 | 0.073242 | 0.10071 | 0.10986 | -0.027466 | 0.054932 | -0.045776 | 0.027466 | 0.11902 | -0.022888 | -0.073242 | -0.064087 | 0.086975 | 0.013733 | 6.5598 | 6.459 | -113.974 | 6.5781 | 6.6147 | 0.15564 | -113.8916 | 6.5918 | 6.5186 | -114.0198 | 6.5323 | 6.4819 | -0.036621 | -114.0106 | 6.4774 | 6.5598 | 6.6055 | -113.9923 | 6.4316 | 6.4407 | 6.6238 | -113.9328
3350.9062 | 120.5292 | -5.6946 | 114.8529 | -0.012589 | 0.012773 | 0.018831 | 0.0046656 | 0.032723 | -0.00099973 | -0.044609 | -0.0054932 | 0.0070517 | -0.014206 | -0.0024589 | 2.5773 | 0.027495 | 0.022888 | 0.073242 | 0.09613 | 0.091553 | -0.036621 | 0.041199 | -0.082397 | 0.013733 | 0.13275 | -0.041199 | -0.082397 | -0.045776 | 0.082397 | -0.013733 | 5.7358 | 5.6122 | -114.8895 | 5.7678 | 5.7861 | 0.17395 | -114.83 | 5.777 | 5.6808 | -114.9353 | 5.7083 | 5.6534 | -0.027466 | -114.8987 | 5.658 | 5.7175 | 5.7907 | -114.9353 | 5.6122 | 5.6488 | 5.8273 | -114.8666
3352.625 | 120.5704 | -7.1503 | 113.3835 | 0.0026703 | 0.014268 | 0.016054 | 0.0029566 | 0.032723 | 0.0060499 | -0.045677 | -0.0054932 | 0.01047 | -0.013138 | -0.00032249 | 2.691 | 0.02365 | -0.009155 | -0.013733 | -0.004578 | 0.07782 | 0.022888 | 0.013733 | -0.10986 | -0.013733 | 0.032043 | -0.11902 | -0.032043 | -0.013733 | 0.041199 | -0.004578 | 7.164 | 7.0404 | -113.3606 | 7.1365 | 7.2281 | 0.18768 | -113.3926 | 7.1915 | 7.1457 | -113.4155 | 7.1365 | 7.0312 | -0.11444 | -113.3972 | 7.1732 | 7.1411 | 7.1457 | -113.4933 | 7.1182 | 7.1365 | 7.1823 | -113.3881
3354.4062 | 120.4926 | -15.3946 | 105.0613 | -0.0049592 | 0.012559 | 0.016267 | 0.0027428 | 0.032509 | 0.0054089 | -0.043754 | -0.013123 | 0.010256 | -0.014206 | -0.00010889 | 2.5908 | 0.026427 | -0.013733 | 0 | 0.018311 | 0.059509 | 0.013733 | 0.018311 | -0.082397 | -0.027466 | 0.004578 | -0.13275 | -0.032043 | -0.004578 | 0.064087 | -0.004578 | 15.4129 | 15.3122 | -105.0476 | 15.3946 | 15.4541 | 0.14191 | -105.0751 | 15.4587 | 15.39 | -105.0934 | 15.3671 | 15.2618 | -0.12817 | -105.0659 | 15.4083 | 15.3809 | 15.4129 | -105.1437 | 15.3625 | 15.39 | 15.3992 | -105.0659
3356.1406 | 120.5109 | -8.9172 | 111.5845 | -0.0049592 | 0.012559 | 0.014986 | -0.00024778 | 0.0308 | 0.0013501 | -0.042686 | -0.020752 | 0.012392 | -0.013138 | 0.0016001 | 2.534 | 0.02835 | -0.068665 | -0.09613 | -0.045776 | 0.013733 | 0.041199 | 0.018311 | -0.086975 | -0.068665 | -0.032043 | -0.16937 | -0.013733 | -0.013733 | 0.041199 | -0.018311 | 8.9355 | 8.8303 | -111.5433 | 8.8211 | 8.931 | 0.10071 | -111.6531 | 8.9584 | 8.8989 | -111.5982 | 8.8486 | 8.7479 | -0.15106 | -111.5982 | 8.9584 | 8.8486 | 8.8715 | -111.6714 | 8.9035 | 8.9035 | 8.8852 | -111.6028
3357.9062 | 120.4468 | -28.1708 | 91.9235 | -0.012589 | 0.0099953 | 0.01819 | 0.0042382 | 0.03315 | -0.0067675 | -0.044822 | -0.013123 | 0.0061973 | -0.015488 | -0.0033133 | 2.5996 | 0.029418 | 0.032043 | 0.086975 | 0.10986 | 0.13733 | 0.013733 | 0.059509 | -0.050354 | 0.022888 | 0.16937 | 0.036621 | -0.036621 | -0.018311 | 0.11902 | 0.032043 | 28.2303 | 28.1204 | -91.9098 | 28.2578 | 28.3081 | 0.18768 | -91.8915 | 28.2898 | 28.2028 | -91.9601 | 28.1937 | 28.2074 | 0.004578 | -91.9418 | 28.1845 | 28.2028 | 28.2806 | -91.9739 | 28.1342 | 28.1525 | 28.3401 | -91.8915
3359.6875 | 120.3232 | -33.4671 | 86.5173 | -0.012589 | 0.014054 | 0.017549 | 0.0044518 | 0.034218 | -0.0024951 | -0.045891 | -0.0054932 | 0.0072653 | -0.015274 | -0.0018179 | 2.4957 | 0.026855 | 0.059509 | 0.11902 | 0.11902 | 0.14191 | 0.018311 | 0.07782 | -0.041199 | 0.045776 | 0.16937 | 0 | -0.032043 | -0.013733 | 0.10529 | 0.045776 | 33.5449 | 33.4259 | -86.499 | 33.5861 | 33.609 | 0.18311 | -86.4578 | 33.5724 | 33.5129 | -86.5494 | 33.5129 | 33.4671 | -0.045776 | -86.5311 | 33.4854 | 33.5266 | 33.5861 | -86.5585 | 33.4351 | 33.4534 | 33.6365 | -86.4716
3361.4688 | 120.4239 | -31.3477 | 88.6597 | -0.012589 | 0.013841 | 0.016054 | -0.00024778 | 0.030586 | 0.00070927 | -0.043754 | 0.0021363 | 0.011324 | -0.015488 | 0.00031831 | 2.5141 | 0.025573 | 0.027466 | 0.004578 | 0.045776 | 0.086975 | 0.032043 | 0.068665 | -0.059509 | 0.027466 | 0.10071 | -0.036621 | -0.041199 | -0.013733 | 0.091553 | 0.041199 | 31.4163 | 31.2881 | -88.6276 | 31.3522 | 31.4346 | 0.14648 | -88.6322 | 31.4392 | 31.3889 | -88.7009 | 31.3751 | 31.311 | -0.07782 | -88.6734 | 31.3797 | 31.3751 | 31.3934 | -88.7192 | 31.3065 | 31.3339 | 31.4484 | -88.6185
3363.1875 | 120.4559 | -14.5981 | 105.5603 | -0.012589 | 0.0132 | 0.014986 | -3.4178e-05 | 0.033577 | 0.0039135 | -0.043968 | -0.0054932 | 0.0098289 | -0.014847 | 0.00074551 | 2.5256 | 0.024505 | -0.036621 | -0.068665 | -0.032043 | 0.032043 | 0.032043 | 0.022888 | -0.082397 | -0.050354 | 0 | -0.14648 | 0 | -0.013733 | 0.050354 | -0.013733 | 14.621 | 14.5157 | -105.5283 | 14.5294 | 14.6301 | 0.11444 | -105.5969 | 14.6484 | 14.5844 | -105.5603 | 14.5477 | 14.4516 | -0.13275 | -105.574 | 14.6301 | 14.5615 | 14.566 | -105.6427 | 14.5981 | 14.5844 | 14.5981 | -105.574
3364.9531 | 120.4147 | -21.2997 | 98.9365 | -0.0049592 | 0.0067911 | 0.019258 | 0.002102 | 0.031014 | -0.0033495 | -0.043754 | -0.0054932 | 0.0055563 | -0.01741 | -0.0026725 | 2.5919 | 0.028564 | 0.013733 | 0.050354 | 0.068665 | 0.082397 | 0.004578 | 0.059509 | -0.027466 | -0.004578 | 0.082397 | -0.059509 | -0.045776 | -0.013733 | 0.09613 | 0.036621 | 21.3593 | 21.2723 | -98.9319 | 21.3501 | 21.3821 | 0.10986 | -98.9227 | 21.3959 | 21.3364 | -98.9822 | 21.2952 | 21.2402 | -0.09613 | -98.9502 | 21.3043 | 21.3135 | 21.3684 | -98.9639 | 21.254 | 21.286 | 21.3821 | -98.8998
3366.75 | 120.575 | -11.8103 | 108.5266 | -0.012589 | 0.012773 | 0.016267 | 0.0044518 | 0.0308 | -0.00057253 | -0.047172 | -0.020752 | 0.0074789 | -0.015488 | -0.0026725 | 2.5797 | 0.026855 | -0.018311 | 0.018311 | 0.050354 | 0.086975 | 0.009155 | 0.050354 | -0.064087 | -0.013733 | 0.091553 | -0.032043 | -0.054932 | -0.036621 | 0.073242 | 0.004578 | 11.8607 | 11.7462 | -108.5175 | 11.8286 | 11.8973 | 0.15106 | -108.5449 | 11.8835 | 11.8149 | -108.5815 | 11.7966 | 11.7783 | -0.036621 | -108.5632 | 11.8195 | 11.792 | 11.8607 | -108.5907 | 11.7554 | 11.7737 | 11.9019 | -108.522
3368.4688 | 120.3964 | -15.5731 | 104.8462 | -0.020218 | 0.015122 | 0.017549 | 0.00039302 | 0.03315 | -0.0012133 | -0.043968 | -0.013123 | 0.0087607 | -0.015274 | -0.0026725 | 2.5951 | 0.026214 | 0.041199 | 0.082397 | 0.091553 | 0.1236 | -0.009155 | 0.041199 | -0.045776 | 0.018311 | 0.1236 | -0.041199 | -0.045776 | -0.032043 | 0.07782 | 0.009155 | 15.6143 | 15.5273 | -104.8553 | 15.6555 | 15.6967 | 0.16937 | -104.805 | 15.6509 | 15.5823 | -104.892 | 15.5914 | 15.5319 | -0.050354 | -104.8782 | 15.564 | 15.6143 | 15.6647 | -104.892 | 15.5273 | 15.5411 | 15.6967 | -104.837
3370.25 | 120.0714 | -44.7372 | 75.0458 | -0.0049592 | 0.014695 | 0.019258 | 0.001034 | 0.032295 | 0.0043409 | -0.042259 | -0.0054932 | 0.012179 | -0.014206 | -0.0016043 | 2.5485 | 0.025573 | -0.004578 | -0.050354 | -0.018311 | 0.073242 | 0.064087 | 0.068665 | -0.045776 | -0.036621 | -0.004578 | -0.14648 | 0.032043 | 0.018311 | 0.082397 | 0.032043 | 44.8059 | 44.6915 | -74.9817 | 44.6869 | 44.8105 | 0.11902 | -75.0504 | 44.8196 | 44.7693 | -75.0137 | 44.7006 | 44.5908 | -0.17853 | -75.0275 | 44.8013 | 44.7327 | 44.7189 | -75.0916 | 44.7693 | 44.7556 | 44.7327 | -75.0137
3372.0312 | 120.5017 | -0.27466 | 120.2362 | -0.0049592 | 0.016618 | 0.016908 | 0.0046656 | 0.031868 | 0.0011365 | -0.043754 | -0.0054932 | 0.010683 | -0.01207 | 0.00053191 | 2.5192 | 0.025573 | -0.022888 | -0.022888 | -0.009155 | 0.064087 | 0.022888 | 0.018311 | -0.10071 | -0.022888 | 0.041199 | -0.11902 | -0.032043 | -0.013733 | 0.050354 | 0.004578 | 0.29297 | 0.17395 | -120.2133 | 0.25177 | 0.33875 | 0.1648 | -120.2591 | 0.32501 | 0.27924 | -120.2682 | 0.25177 | 0.15564 | -0.1236 | -120.2499 | 0.29755 | 0.25177 | 0.2655 | -120.3369 | 0.24262 | 0.26093 | 0.31586 | -120.2316
3373.8125 | 120.607 | -0.28839 | 120.4285 | -0.020218 | 0.0132 | 0.016267 | 0.00082022 | 0.033577 | 0.0022047 | -0.041618 | -0.013123 | 0.012179 | -0.014206 | -0.00074989 | 2.5624 | 0.027068 | 0.022888 | -0.018311 | 0.013733 | 0.059509 | 0.022888 | 0.022888 | -0.082397 | -0.036621 | 0.032043 | -0.12817 | -0.041199 | -0.018311 | 0.045776 | -0.013733 | 0.31128 | 0.20599 | -120.4056 | 0.27008 | 0.3479 | 0.14191 | -120.4056 | 0.33417 | 0.27466 | -120.4697 | 0.25177 | 0.16022 | -0.11444 | -120.4468 | 0.31128 | 0.31128 | 0.30212 | -120.5109 | 0.24719 | 0.27008 | 0.32043 | -120.4422
3375.5312 | 120.7306 | -0.24719 | 120.433 | -0.012589 | 0.0091409 | 0.016054 | 0.0014612 | 0.034432 | -0.0035633 | -0.043541 | -0.0054932 | 0.0074789 | -0.014206 | -0.00053629 | 2.5201 | 0.028136 | 0.022888 | 0.045776 | 0.07782 | 0.086975 | -0.022888 | 0.054932 | -0.073242 | -0.013733 | 0.082397 | -0.059509 | -0.07782 | -0.041199 | 0.07782 | 0.018311 | 0.30212 | 0.17395 | -120.4559 | 0.29297 | 0.33417 | 0.16022 | -120.4102 | 0.32501 | 0.2655 | -120.5109 | 0.23346 | 0.18768 | -0.07782 | -120.4742 | 0.2243 | 0.27008 | 0.32501 | -120.5063 | 0.16937 | 0.20599 | 0.32959 | -120.4147
3377.3281 | 120.6802 | -0.28381 | 120.5292 | -0.0049592 | 0.014268 | 0.016267 | 0.0014612 | 0.031227 | 0.0045545 | -0.043754 | -0.0054932 | 0.013033 | -0.012924 | 0.00095911 | 2.5485 | 0.026641 | 0.004578 | -0.032043 | 0 | 0.073242 | 0.004578 | 0.032043 | -0.091553 | -0.045776 | 0.004578 | -0.15106 | -0.041199 | -0.018311 | 0.054932 | -0.004578 | 0.31586 | 0.19226 | -120.5246 | 0.25177 | 0.35706 | 0.16479 | -120.5246 | 0.33874 | 0.27923 | -120.5704 | 0.23804 | 0.13275 | -0.14648 | -120.5475 | 0.28839 | 0.28839 | 0.28381 | -120.6207 | 0.24261 | 0.2655 | 0.28839 | -120.5338
3379.0938 | 120.7855 | -0.26093 | 120.5612 | -0.0049592 | 0.016618 | 0.014131 | 0.0029566 | 0.032509 | 0.0026319 | -0.042473 | -0.013123 | 0.01111 | -0.01207 | 0.00074551 | 2.5611 | 0.027495 | -0.022888 | -0.041199 | 0.004578 | 0.07782 | 0.018311 | 0.009155 | -0.10071 | -0.027466 | 0.059509 | -0.11444 | -0.045776 | -0.013733 | 0.050354 | -0.041199 | 0.27008 | 0.16022 | -120.5429 | 0.21973 | 0.33875 | 0.17853 | -120.5841 | 0.31128 | 0.21973 | -120.607 | 0.23346 | 0.14648 | -0.073242 | -120.575 | 0.27924 | 0.23804 | 0.2655 | -120.6619 | 0.21515 | 0.24719 | 0.32043 | -120.6024
3380.875 | 120.8954 | -0.23804 | 120.5154 | -0.0049592 | 0.012559 | 0.017122 | -3.4178e-05 | 0.032295 | -0.00014533 | -0.0429 | 0.0021363 | 0.010897 | -0.016129 | 0.00053191 | 2.5654 | 0.030273 | -0.054932 | -0.064087 | -0.041199 | 0.027466 | 0.022888 | 0.018311 | -0.091553 | -0.050354 | 0.022888 | -0.10986 | -0.054932 | -0.036621 | 0.068665 | 0.004578 | 0.25635 | 0.14648 | -120.4926 | 0.17395 | 0.2655 | 0.11902 | -120.5704 | 0.3067 | 0.24261 | -120.5704 | 0.18768 | 0.12817 | -0.11444 | -120.5521 | 0.26093 | 0.1831 | 0.19684 | -120.607 | 0.1831 | 0.20142 | 0.26093 | -120.5109
3382.6562 | 120.8817 | -0.24719 | 120.5933 | -0.0049592 | 0.011491 | 0.017549 | 0.0059472 | 0.033577 | -0.0039905 | -0.046318 | -0.028381 | 0.0064109 | -0.015274 | -0.0026725 | 2.522 | 0.026427 | 0.027466 | 0.068665 | 0.10071 | 0.10529 | -0.036621 | 0.041199 | -0.068665 | 0.009155 | 0.16022 | 0 | -0.07782 | -0.050354 | 0.091553 | 0.013733 | 0.28839 | 0.17853 | -120.6299 | 0.31586 | 0.35248 | 0.17395 | -120.5658 | 0.33874 | 0.26093 | -120.6711 | 0.25635 | 0.24719 | -0.013733 | -120.6436 | 0.21057 | 0.27466 | 0.3479 | -120.6619 | 0.16937 | 0.19684 | 0.40741 | -120.5795
3384.4375 | 120.8359 | -0.27466 | 120.5887 | -0.012589 | 0.012986 | 0.020326 | -3.4178e-05 | 0.032723 | -0.0037769 | -0.046318 | -0.0054932 | 0.0076925 | -0.014206 | -0.00074989 | 2.5135 | 0.02835 | 0.032043 | 0.045776 | 0.082397 | 0.1236 | -0.018311 | 0.032043 | -0.059509 | 0.022888 | 0.14648 | -0.027466 | -0.068665 | -0.041199 | 0.073242 | 0.009155 | 0.3067 | 0.21515 | -120.607 | 0.32043 | 0.39825 | 0.1831 | -120.5566 | 0.3479 | 0.28381 | -120.6573 | 0.29755 | 0.24719 | -0.036621 | -120.6299 | 0.25635 | 0.3067 | 0.35706 | -120.6482 | 0.20599 | 0.23346 | 0.42114 | -120.5795
3386.2344 | 120.9824 | -0.24719 | 120.5566 | -0.020218 | 0.014482 | 0.02054 | 0.0033838 | 0.033791 | -0.0056995 | -0.04824 | 0.0021363 | 0.0064109 | -0.013351 | -0.0026725 | 2.5568 | 0.026641 | -0.036621 | -0.009155 | 0.032043 | 0.068665 | 0 | 0.027466 | -0.073242 | -0.036621 | 0.064087 | -0.054932 | -0.059509 | -0.050354 | 0.054932 | -0.004578 | 0.27466 | 0.17395 | -120.5566 | 0.23804 | 0.31586 | 0.14191 | -120.5933 | 0.30212 | 0.24261 | -120.6162 | 0.21057 | 0.19226 | -0.050354 | -120.607 | 0.24719 | 0.21057 | 0.27924 | -120.6299 | 0.18768 | 0.19684 | 0.31128 | -120.5612
3387.9375 | 120.9366 | -0.24719 | 120.5978 | -0.012589 | 0.0080727 | 0.019258 | -0.001316 | 0.031014 | -0.0044177 | -0.046959 | -0.020752 | 0.0066245 | -0.01442 | -0.0024589 | 2.5385 | 0.027495 | -0.009155 | -0.004578 | 0.050354 | 0.064087 | 0 | 0.050354 | -0.068665 | -0.032043 | 0.045776 | -0.073242 | -0.082397 | -0.045776 | 0.050354 | 0.013733 | 0.29755 | 0.17853 | -120.5978 | 0.24261 | 0.31128 | 0.13275 | -120.607 | 0.29755 | 0.26093 | -120.6802 | 0.21515 | 0.17395 | -0.086975 | -120.6436 | 0.24719 | 0.23804 | 0.29755 | -120.6665 | 0.16479 | 0.20142 | 0.29297 | -120.5841
3389.7188 | 121.019 | -0.23346 | 120.5933 | -0.012589 | 0.012986 | 0.016481 | 0.0042382 | 0.032082 | -0.0016405 | -0.049095 | -0.013123 | 0.0059837 | -0.013779 | -0.0022453 | 2.5423 | 0.026427 | 0.013733 | 0.022888 | 0.059509 | 0.091553 | 0 | 0.036621 | -0.086975 | -0.004578 | 0.10071 | -0.022888 | -0.073242 | -0.054932 | 0.091553 | 0.013733 | 0.27008 | 0.14648 | -120.5933 | 0.25635 | 0.32501 | 0.17853 | -120.5795 | 0.32501 | 0.24719 | -120.6665 | 0.22888 | 0.21057 | -0.036621 | -120.6482 | 0.23346 | 0.24719 | 0.29297 | -120.6802 | 0.16022 | 0.17853 | 0.33417 | -120.5795
3391.4375 | 120.9686 | -0.25635 | 120.6436 | -0.012589 | 0.0080727 | 0.015413 | 0.00039302 | 0.032723 | -0.00078613 | -0.045463 | -0.013123 | 0.0079063 | -0.012924 | -0.0016043 | 2.5615 | 0.024718 | 0.045776 | 0.054932 | 0.07782 | 0.086975 | -0.022888 | 0.059509 | -0.073242 | -0.013733 | 0.064087 | -0.054932 | -0.064087 | -0.050354 | 0.064087 | 0.009155 | 0.31586 | 0.18311 | -120.6665 | 0.31128 | 0.34332 | 0.16022 | -120.5978 | 0.32044 | 0.2655 | -120.7077 | 0.24262 | 0.20142 | -0.064087 | -120.694 | 0.23346 | 0.30212 | 0.33417 | -120.7169 | 0.19226 | 0.20599 | 0.32044 | -120.6345
3393.2031 | 121.0098 | -0.24719 | 120.6619 | -0.0049592 | 0.012559 | 0.017763 | -0.00046138 | 0.035286 | 0.0015637 | -0.04525 | -0.013123 | 0.0098289 | -0.016129 | -0.0013907 | 2.5496 | 0.026214 | 0.054932 | 0.073242 | 0.10529 | 0.10986 | -0.022888 | 0.045776 | -0.045776 | 0.041199 | 0.14191 | -0.018311 | -0.073242 | -0.045776 | 0.082397 | 0.041199 | 0.29297 | 0.20142 | -120.6848 | 0.32043 | 0.35706 | 0.15564 | -120.607 | 0.32959 | 0.28839 | -120.7352 | 0.28839 | 0.22888 | -0.05951 | -120.7077 | 0.2243 | 0.30212 | 0.35248 | -120.7077 | 0.17395 | 0.20142 | 0.3891 | -120.6207
3394.9688 | 121.0419 | -0.23804 | 120.6619 | -0.020218 | 0.011918 | 0.019472 | 0.0029566 | 0.034645 | -0.0018543 | -0.046745 | -0.020752 | 0.0064109 | -0.016129 | -0.0018179 | 2.5575 | 0.026 | 0.059509 | 0.091553 | 0.10071 | 0.10071 | -0.009155 | 0.041199 | -0.059509 | 0.041199 | 0.16479 | 0.004578 | -0.054932 | -0.064087 | 0.073242 | 0 | 0.27924 | 0.17853 | -120.6711 | 0.32959 | 0.33875 | 0.16022 | -120.6024 | 0.31128 | 0.23804 | -120.7169 | 0.27924 | 0.24261 | 0.004578 | -120.726 | 0.22888 | 0.29755 | 0.33875 | -120.7214 | 0.1831 | 0.17395 | 0.40283 | -120.6619
3396.7656 | 121.019 | -0.27008 | 120.7169 | -0.020218 | 0.012345 | 0.019899 | 0.0035974 | 0.032082 | -0.00057253 | -0.045463 | -0.013123 | 0.010042 | -0.013992 | -0.0026725 | 2.5897 | 0.026641 | 0.059509 | 0.091553 | 0.10986 | 0.10529 | -0.022888 | 0.041199 | -0.068665 | 0.018311 | 0.14648 | -0.018311 | -0.082397 | -0.054932 | 0.064087 | 0.022888 | 0.31128 | 0.20142 | -120.7397 | 0.36163 | 0.37537 | 0.17395 | -120.6573 | 0.33417 | 0.29297 | -120.7993 | 0.28839 | 0.25177 | -0.041199 | -120.7718 | 0.24719 | 0.32959 | 0.37994 | -120.7855 | 0.18768 | 0.21515 | 0.41657 | -120.694
3398.5469 | 120.9778 | -0.28381 | 120.7214 | -0.012589 | 0.012986 | 0.018404 | 0.00039302 | 0.031014 | 0.0013501 | -0.047386 | -0.013123 | 0.011538 | -0.015701 | -0.0013907 | 2.5959 | 0.026 | 0.064087 | 0.064087 | 0.09613 | 0.09613 | -0.032043 | 0.050354 | -0.068665 | 0.018311 | 0.11902 | -0.032043 | -0.064087 | -0.045776 | 0.073242 | 0 | 0.33417 | 0.21515 | -120.7535 | 0.3479 | 0.37994 | 0.16479 | -120.6573 | 0.35706 | 0.28381 | -120.7855 | 0.30212 | 0.25177 | -0.032043 | -120.7672 | 0.25177 | 0.3479 | 0.37994 | -120.7901 | 0.21973 | 0.23804 | 0.40283 | -120.7214
3400.2656 | 121.0419 | -0.25177 | 120.7397 | -0.0049592 | 0.0132 | 0.016481 | -0.00088858 | 0.0308 | 0.0064771 | -0.042686 | -0.0054932 | 0.011965 | -0.013779 | -0.00032249 | 2.5998 | 0.025573 | -0.036621 | -0.091553 | -0.045776 | 0.022888 | 0.045776 | 0.004578 | -0.09613 | -0.064087 | -0.041199 | -0.16937 | -0.036621 | -0.018311 | 0.027466 | -0.032043 | 0.25635 | 0.15564 | -120.694 | 0.16022 | 0.27466 | 0.11902 | -120.7764 | 0.27924 | 0.21973 | -120.7764 | 0.18768 | 0.082397 | -0.13733 | -120.7581 | 0.29755 | 0.21515 | 0.20599 | -120.8359 | 0.21515 | 0.23346 | 0.21057 | -120.7718
3402.0469 | 121.0464 | -0.26093 | 120.7672 | -0.020218 | 0.017472 | 0.016267 | 0.0016748 | 0.031655 | 0.0036999 | -0.044395 | -0.020752 | 0.010897 | -0.013138 | -0.00053629 | 2.5701 | 0.026 | -0.022888 | -0.036621 | -0.022888 | 0.054932 | 0.018311 | 0.009155 | -0.086975 | -0.032043 | 0.050354 | -0.10986 | -0.032043 | -0.022888 | 0.059509 | -0.013733 | 0.27008 | 0.17395 | -120.7489 | 0.2243 | 0.31586 | 0.14191 | -120.7901 | 0.32043 | 0.24719 | -120.7993 | 0.22888 | 0.15106 | -0.09613 | -120.7901 | 0.27924 | 0.23804 | 0.23804 | -120.8542 | 0.22888 | 0.23804 | 0.31128 | -120.7809
3403.8281 | 121.0236 | -0.27466 | 120.7718 | -0.0049592 | 0.014695 | 0.016054 | -0.00067498 | 0.033577 | 0.0036999 | -0.041404 | -0.013123 | 0.01111 | -0.014633 | -0.00096349 | 2.5848 | 0.027068 | -0.059509 | -0.11444 | -0.068665 | 0.004578 | 0.018311 | 0.022888 | -0.10071 | -0.07782 | -0.036621 | -0.17395 | -0.041199 | 0.004578 | 0.064087 | -0.041199 | 0.29755 | 0.17395 | -120.7535 | 0.16022 | 0.27924 | 0.10529 | -120.8313 | 0.33875 | 0.23346 | -120.813 | 0.19684 | 0.10071 | -0.13275 | -120.7672 | 0.29297 | 0.21515 | 0.20599 | -120.8725 | 0.23346 | 0.27924 | 0.23804 | -120.813
3405.5469 | 121.0236 | -0.28381 | 120.8038 | -0.0049592 | 0.022813 | 0.01819 | 0.0029566 | 0.033791 | 0.0036999 | -0.041191 | -0.013123 | 0.010897 | -0.010361 | 0.0011727 | 2.5782 | 0.027495 | -0.059509 | -0.059509 | -0.022888 | 0.045776 | 0.027466 | 0.032043 | -0.091553 | -0.073242 | -0.022888 | -0.1831 | -0.027466 | -0.018311 | 0.059509 | -0.013733 | 0.31586 | 0.19226 | -120.7764 | 0.2243 | 0.32959 | 0.13733 | -120.8633 | 0.34332 | 0.27008 | -120.8313 | 0.21057 | 0.10071 | -0.16937 | -120.8221 | 0.31128 | 0.2243 | 0.26092 | -120.8954 | 0.25635 | 0.2655 | 0.26092 | -120.8176
3407.3281 | 121.0648 | -0.27008 | 120.8405 | -0.012589 | 0.014695 | 0.013063 | 0.002102 | 0.033577 | 0.0028455 | -0.041832 | -0.0054932 | 0.01047 | -0.012283 | -0.00053629 | 2.5538 | 0.027923 | -0.013733 | -0.009155 | 0 | 0.068665 | -0.004578 | 0.032043 | -0.086975 | -0.027466 | 0.059509 | -0.10529 | -0.050354 | -0.036621 | 0.064087 | -0.022888 | 0.30212 | 0.18311 | -120.845 | 0.26093 | 0.33875 | 0.15564 | -120.8542 | 0.33417 | 0.24719 | -120.8908 | 0.24262 | 0.1648 | -0.082398 | -120.8771 | 0.2655 | 0.25635 | 0.27008 | -120.9274 | 0.21973 | 0.23346 | 0.32959 | -120.8633
3409.0469 | 121.1929 | -0.25177 | 120.7947 | -0.012589 | 0.011277 | 0.017336 | -0.00046138 | 0.032936 | 6.8274e-05 | -0.045036 | 0.0021363 | 0.0096151 | -0.014847 | 0.00074551 | 2.5664 | 0.028777 | 0.004578 | 0.045776 | 0.064087 | 0.10071 | -0.022888 | 0.032043 | -0.054932 | 0.018311 | 0.091553 | -0.036621 | -0.07782 | -0.050354 | 0.086975 | 0.022888 | 0.28381 | 0.19684 | -120.8176 | 0.29755 | 0.35248 | 0.15564 | -120.7901 | 0.33874 | 0.27466 | -120.8725 | 0.27008 | 0.21515 | -0.059509 | -120.845 | 0.22888 | 0.25635 | 0.31586 | -120.8496 | 0.17395 | 0.20142 | 0.34332 | -120.7718
3410.8281 | 121.2067 | -0.25177 | 120.8038 | -0.012589 | 0.0097817 | 0.017336 | 0.0025292 | 0.029305 | -0.0054859 | -0.044182 | -0.028381 | 0.0057699 | -0.015701 | -0.0037405 | 2.5923 | 0.029204 | -0.027466 | 0.018311 | 0.059509 | 0.07782 | 0.009155 | 0.045776 | -0.059509 | -0.041199 | 0.10071 | -0.022888 | -0.054932 | -0.054932 | 0.073242 | 0.009155 | 0.29755 | 0.19226 | -120.7947 | 0.27008 | 0.32959 | 0.13733 | -120.8313 | 0.32501 | 0.26093 | -120.8588 | 0.21057 | 0.22888 | -0.032043 | -120.8588 | 0.26093 | 0.2243 | 0.31128 | -120.8633 | 0.19684 | 0.19684 | 0.35248 | -120.7947
3412.625 | 121.2021 | -0.25635 | 120.8221 | -0.012589 | 0.012773 | 0.017336 | -0.0011024 | 0.032509 | 0.0017773 | -0.043541 | -0.013123 | 0.012179 | -0.015274 | 0.00010471 | 2.5555 | 0.02835 | -0.054932 | -0.09613 | -0.036621 | 0.018311 | 0.027466 | 0.013733 | -0.10071 | -0.064087 | 0 | -0.1236 | -0.027466 | -0.032043 | 0.054932 | -0.009155 | 0.27008 | 0.15564 | -120.7947 | 0.16022 | 0.27466 | 0.11902 | -120.8771 | 0.31128 | 0.24719 | -120.8496 | 0.19226 | 0.13275 | -0.11444 | -120.8542 | 0.28381 | 0.20142 | 0.21973 | -120.9229 | 0.22888 | 0.22431 | 0.25635 | -120.8313
3414.4062 | 121.1426 | -0.29755 | 120.8633 | -0.0049592 | 0.014268 | 0.017336 | 0.0033838 | 0.032082 | 0.0019909 | -0.046531 | -0.013123 | 0.01047 | -0.011642 | 0.00010471 | 2.5714 | 0.027923 | -0.07782 | -0.073242 | -0.041199 | 0.041199 | 0.036621 | -0.004578 | -0.10529 | -0.10071 | 0.004578 | -0.15106 | -0.018311 | -0.018311 | 0.050354 | -0.022888 | 0.29297 | 0.19226 | -120.8267 | 0.2243 | 0.33874 | 0.14649 | -120.9412 | 0.3479 | 0.27466 | -120.8817 | 0.19684 | 0.14648 | -0.12817 | -120.8817 | 0.33417 | 0.21973 | 0.25635 | -120.9686 | 0.27923 | 0.27923 | 0.30212 | -120.8862
3416.125 | 121.106 | -0.28381 | 120.8954 | -0.012589 | 0.013627 | 0.014345 | 0.0012476 | 0.033364 | 0.0051953 | -0.04525 | 0.0021363 | 0.01111 | -0.01442 | 0.0011727 | 2.5459 | 0.029204 | -0.059509 | -0.10529 | -0.045776 | 0.027466 | 0.032043 | 0.004578 | -0.10529 | -0.086975 | -0.036621 | -0.18768 | -0.032043 | -0.018311 | 0.041199 | -0.036621 | 0.28839 | 0.17853 | -120.8633 | 0.17853 | 0.31128 | 0.13275 | -120.9549 | 0.32501 | 0.24719 | -120.9274 | 0.19684 | 0.09613 | -0.15106 | -120.9137 | 0.31586 | 0.2243 | 0.23804 | -121.0007 | 0.25177 | 0.2655 | 0.24719 | -120.932
3417.9219 | 121.1517 | -0.28839 | 120.9229 | -0.012589 | 0.013413 | 0.018617 | 0.0031702 | 0.030373 | -0.00014533 | -0.046745 | -0.020752 | 0.0096151 | -0.012711 | -0.0028861 | 2.578 | 0.027282 | -0.091553 | -0.054932 | -0.041199 | 0.013733 | 0.018311 | -0.004578 | -0.11902 | -0.10529 | -0.004578 | -0.15564 | -0.018311 | -0.018311 | 0.032043 | -0.027466 | 0.28381 | 0.16937 | -120.9045 | 0.23346 | 0.30212 | 0.13275 | -121.0144 | 0.32043 | 0.26093 | -120.9412 | 0.18311 | 0.13275 | -0.12817 | -120.9412 | 0.3067 | 0.19684 | 0.24719 | -121.0419 | 0.27008 | 0.27008 | 0.28381 | -120.9503
3419.7031 | 121.1517 | -0.28839 | 120.9137 | -0.0049592 | 0.013627 | 0.017976 | 0.001034 | 0.031014 | -0.0056995 | -0.044609 | -0.013123 | 0.0051291 | -0.013138 | -0.0016043 | 2.5769 | 0.029418 | -0.009155 | 0.064087 | 0.07782 | 0.10071 | 0 | 0.036621 | -0.073242 | -0.013733 | 0.11444 | -0.045776 | -0.059509 | -0.041199 | 0.064087 | -0.013733 | 0.32501 | 0.21515 | -120.9137 | 0.35248 | 0.3891 | 0.17395 | -120.9229 | 0.35248 | 0.27466 | -120.9732 | 0.27466 | 0.24262 | -0.032043 | -120.9549 | 0.28839 | 0.27924 | 0.36621 | -120.9869 | 0.22888 | 0.24719 | 0.40283 | -120.9274
3421.4688 | 121.2387 | -0.24261 | 120.8496 | -0.0049592 | 0.0093545 | 0.016054 | -0.0019568 | 0.03315 | -0.00078613 | -0.044395 | -0.013123 | 0.0074789 | -0.016342 | -0.0028861 | 2.5895 | 0.028564 | 0.041199 | 0.068665 | 0.091553 | 0.11444 | -0.032043 | 0.050354 | -0.059509 | 0.022888 | 0.10529 | -0.045776 | -0.091553 | -0.059509 | 0.073242 | 0.018311 | 0.29297 | 0.18311 | -120.8817 | 0.31128 | 0.35706 | 0.17395 | -120.8084 | 0.31586 | 0.26093 | -120.9412 | 0.2655 | 0.19684 | -0.064087 | -120.9091 | 0.21057 | 0.28381 | 0.33417 | -120.9091 | 0.15106 | 0.18311 | 0.3479 | -120.8313
3423.1875 | 121.1655 | -0.28381 | 120.9641 | -0.0049592 | 0.011918 | 0.020967 | 0.0014612 | 0.032723 | -0.00099973 | -0.045036 | -0.013123 | 0.0079063 | -0.015488 | -0.0018179 | 2.557 | 0.025786 | -0.050354 | -0.036621 | -0.004578 | 0.041199 | 0.027466 | 0.018311 | -0.10529 | -0.10529 | 0.009155 | -0.14191 | -0.032043 | 0 | 0.022888 | -0.018311 | 0.30212 | 0.17853 | -120.9366 | 0.24719 | 0.32501 | 0.14649 | -121.0144 | 0.3067 | 0.2655 | -120.9961 | 0.17853 | 0.14191 | -0.1236 | -120.9641 | 0.31128 | 0.23346 | 0.27923 | -121.0693 | 0.25177 | 0.28381 | 0.29297 | -120.9824
3424.9531 | 121.2891 | -0.25635 | 120.9229 | -0.020218 | 0.0093545 | 0.02054 | -0.0017432 | 0.032936 | -0.0046313 | -0.046104 | -0.013123 | 0.0074789 | -0.017197 | -0.0018179 | 2.5767 | 0.027923 | -0.013733 | -0.009155 | 0.032043 | 0.068665 | -0.013733 | 0.050354 | -0.07782 | -0.045776 | 0.045776 | -0.064087 | -0.064087 | -0.050354 | 0.059509 | -0.013733 | 0.3067 | 0.17853 | -120.9366 | 0.24719 | 0.32501 | 0.14649 | -120.9366 | 0.31586 | 0.24262 | -120.9869 | 0.21057 | 0.19226 | -0.050354 | -120.9732 | 0.24262 | 0.24262 | 0.28839 | -121.0007 | 0.19226 | 0.20599 | 0.30212 | -120.9366
3426.7344 | 121.2936 | -0.23346 | 120.9091 | -0.0049592 | 0.011704 | 0.01819 | -0.0015296 | 0.031868 | -0.00035893 | -0.045677 | -0.0054932 | 0.0053427 | -0.015701 | -0.0016043 | 2.563 | 0.027282 | 0.059509 | 0.064087 | 0.09613 | 0.10529 | -0.004578 | 0.041199 | -0.073242 | 0.022888 | 0.10529 | -0.032043 | -0.068665 | -0.059509 | 0.07782 | 0.032043 | 0.27466 | 0.16022 | -120.9137 | 0.29755 | 0.33875 | 0.17853 | -120.8496 | 0.31128 | 0.2655 | -120.9778 | 0.25635 | 0.20142 | -0.064086 | -120.9686 | 0.22888 | 0.29297 | 0.32959 | -120.9824 | 0.16479 | 0.17395 | 0.33875 | -120.8771
3428.4531 | 121.2433 | -0.28381 | 120.9549 | 0.0026703 | 0.014695 | 0.018617 | -0.00024778 | 0.03315 | 0.0051953 | -0.046531 | -0.013123 | 0.011965 | -0.013779 | -0.00053629 | 2.5282 | 0.025786 | -0.022888 | -0.032043 | -0.013733 | 0.064087 | 0.022888 | 0.032043 | -0.082397 | -0.027466 | 0.041199 | -0.11902 | -0.041199 | -0.027466 | 0.027466 | -0.013733 | 0.31586 | 0.20142 | -120.932 | 0.25177 | 0.3479 | 0.14648 | -120.9778 | 0.31128 | 0.27008 | -120.9961 | 0.25635 | 0.16479 | -0.10529 | -120.9824 | 0.3067 | 0.26092 | 0.27008 | -121.0373 | 0.24261 | 0.25635 | 0.32501 | -120.9686
3430.25 | 121.2891 | -0.24719 | 120.9595 | -0.0049592 | 0.010423 | 0.019685 | 0.0029566 | 0.032723 | -0.0033495 | -0.047172 | -0.020752 | 0.0072653 | -0.014633 | -0.0013907 | 2.6002 | 0.026641 | 0.036621 | 0.086975 | 0.10529 | 0.10986 | 0.009155 | 0.045776 | -0.059509 | 0 | 0.14648 | -0.027466 | -0.073242 | -0.064087 | 0.064087 | 0 | 0.29297 | 0.18768 | -120.9503 | 0.33417 | 0.35706 | 0.16937 | -120.9229 | 0.31128 | 0.24719 | -121.0327 | 0.24719 | 0.21973 | -0.027466 | -121.0236 | 0.25635 | 0.28381 | 0.35248 | -121.019 | 0.17395 | 0.1831 | 0.39368 | -120.9595
3432.0312 | 121.2433 | -0.27008 | 120.9732 | -0.020218 | 0.01555 | 0.018831 | 0.0035974 | 0.034004 | -0.00099973 | -0.04525 | -0.0054932 | 0.0072653 | -0.01506 | -0.0026725 | 2.5724 | 0.025359 | 0.041199 | 0.073242 | 0.10071 | 0.10529 | -0.018311 | 0.045776 | -0.068665 | -0.004578 | 0.12817 | -0.022888 | -0.059509 | -0.050354 | 0.082397 | 0.013733 | 0.31586 | 0.20142 | -120.9915 | 0.34332 | 0.37537 | 0.17395 | -120.932 | 0.35248 | 0.28381 | -121.0327 | 0.2655 | 0.24719 | -0.036621 | -121.0236 | 0.25177 | 0.31128 | 0.37079 | -121.0419 | 0.21057 | 0.21973 | 0.39826 | -120.9595
3433.8281 | 121.3486 | -0.25177 | 120.9595 | -0.012589 | 0.012345 | 0.016695 | 0.0025292 | 0.0355 | 0.0051953 | -0.046318 | -0.020752 | 0.011324 | -0.012924 | 0.0013863 | 2.6211 | 0.024505 | -0.027466 | -0.086975 | -0.045776 | 0.027466 | 0.036621 | 0.009155 | -0.091553 | -0.054932 | -0.027466 | -0.15106 | -0.050354 | -0.036621 | 0.054932 | 0.004578 | 0.26093 | 0.16022 | -120.9229 | 0.16479 | 0.27924 | 0.11902 | -120.9869 | 0.3067 | 0.25635 | -121.0098 | 0.19684 | 0.10071 | -0.15564 | -120.9961 | 0.28839 | 0.2243 | 0.20599 | -121.051 | 0.20142 | 0.21515 | 0.2243 | -120.9549
3435.6094 | 121.2479 | -0.29755 | 121.0052 | 0.0026703 | 0.013627 | 0.017122 | 0.0014612 | 0.032723 | 0.0032727 | -0.043968 | 0.0021363 | 0.01047 | -0.013138 | 0.0026681 | 2.5803 | 0.025359 | -0.068665 | -0.11902 | -0.054932 | 0.018311 | 0.032043 | 0.013733 | -0.10986 | -0.082397 | -0.064087 | -0.18768 | -0.018311 | -0.032043 | 0.041199 | -0.013733 | 0.31128 | 0.18768 | -120.9732 | 0.17853 | 0.31586 | 0.12817 | -121.0739 | 0.33874 | 0.28381 | -121.0236 | 0.21515 | 0.10986 | -0.17395 | -121.0373 | 0.32959 | 0.22888 | 0.24261 | -121.1151 | 0.27923 | 0.2655 | 0.23346 | -121.019
3437.3906 | 121.2616 | -0.29755 | 121.0281 | -0.012589 | 0.016618 | 0.017976 | 0.0040246 | 0.031655 | -0.0014269 | -0.044182 | -0.013123 | 0.010683 | -0.013565 | -0.0016043 | 2.5504 | 0.027282 | -0.064087 | -0.032043 | -0.004578 | 0.018311 | 0.018311 | 0.013733 | -0.091553 | -0.10986 | 0 | -0.14191 | -0.013733 | -0.018311 | 0.018311 | -0.027466 | 0.31128 | 0.20599 | -121.0098 | 0.2655 | 0.31586 | 0.10986 | -121.0922 | 0.31586 | 0.27008 | -121.0419 | 0.18768 | 0.15564 | -0.11444 | -121.0464 | 0.31586 | 0.23346 | 0.29297 | -121.1197 | 0.28381 | 0.27923 | 0.29755 | -121.0556
3439.1094 | 121.2982 | -0.28381 | 121.0144 | -0.0049592 | 0.014054 | 0.01584 | 0.0014612 | 0.031655 | 0.0026319 | -0.042259 | -0.0054932 | 0.012392 | -0.013779 | 0.0030953 | 2.6361 | 0.025359 | -0.054932 | -0.09613 | -0.064087 | 0.032043 | 0.027466 | 0.022888 | -0.10071 | -0.091553 | -0.045776 | -0.17395 | -0.036621 | -0.027466 | 0.045776 | -0.027466 | 0.3067 | 0.1831 | -120.9869 | 0.18768 | 0.31586 | 0.13275 | -121.0693 | 0.32959 | 0.25635 | -121.051 | 0.19226 | 0.10986 | -0.14648 | -121.0419 | 0.31128 | 0.22888 | 0.21973 | -121.1151 | 0.24719 | 0.25635 | 0.23804 | -121.0419
3440.9062 | 121.2799 | -0.28839 | 121.0464 | -0.012589 | 0.013627 | 0.018617 | 0.0033838 | 0.033364 | -0.00035893 | -0.043754 | -0.020752 | 0.0085471 | -0.014847 | -0.00010889 | 2.5735 | 0.028136 | -0.064087 | -0.041199 | -0.022888 | 0.013733 | 0.027466 | 0.009155 | -0.10529 | -0.09613 | 0.013733 | -0.15106 | -0.032043 | -0.004578 | 0.041199 | -0.013733 | 0.29755 | 0.18311 | -121.019 | 0.24719 | 0.30212 | 0.11902 | -121.1105 | 0.32959 | 0.27466 | -121.0785 | 0.19226 | 0.13733 | -0.13733 | -121.051 | 0.31586 | 0.2243 | 0.2655 | -121.1517 | 0.25635 | 0.28381 | 0.30212 | -121.0602
3442.6406 | 121.4264 | -0.24261 | 121.0236 | -0.020218 | 0.012773 | 0.020113 | 0.0012476 | 0.032723 | -0.0046313 | -0.046959 | -0.013123 | 0.0057699 | -0.016556 | -0.0018179 | 2.5564 | 0.027923 | 0.018311 | 0.041199 | 0.09613 | 0.10529 | -0.013733 | 0.036621 | -0.059509 | 0.013733 | 0.14191 | 0.009155 | -0.059509 | -0.050354 | 0.086975 | 0.018311 | 0.27924 | 0.18311 | -121.0373 | 0.28381 | 0.3479 | 0.16479 | -121.0052 | 0.32959 | 0.26093 | -121.0831 | 0.25635 | 0.25177 | -0.009156 | -121.0739 | 0.22888 | 0.26093 | 0.33874 | -121.0831 | 0.18311 | 0.19226 | 0.38452 | -121.0052
3444.4219 | 121.3211 | -0.28839 | 121.0373 | -0.012589 | 0.015763 | 0.014986 | 0.0012476 | 0.030159 | 0.0028455 | -0.043327 | -0.013123 | 0.012179 | -0.01442 | 0.00053191 | 2.5583 | 0.026214 | -0.064087 | -0.11444 | -0.054932 | 0.018311 | 0.036621 | 0.004578 | -0.09613 | -0.07782 | -0.054932 | -0.16022 | -0.032043 | -0.013733 | 0.045776 | -0.018311 | 0.29297 | 0.19226 | -121.0007 | 0.17395 | 0.3067 | 0.11444 | -121.1014 | 0.33417 | 0.27008 | -121.0693 | 0.21057 | 0.12817 | -0.14191 | -121.051 | 0.32501 | 0.2243 | 0.23346 | -121.1334 | 0.25635 | 0.27466 | 0.23346 | -121.0556
3446.1406 | 121.3165 | -0.32044 | 121.0464 | -0.020218 | 0.015763 | 0.016908 | 0.0050928 | 0.034218 | -0.0033495 | -0.045891 | -0.013123 | 0.0070517 | -0.013138 | 0.0011727 | 2.575 | 0.025573 | 0.009155 | 0.022888 | 0.050354 | 0.082397 | -0.013733 | 0.032043 | -0.086975 | -0.050354 | 0.07782 | -0.10986 | -0.050354 | -0.013733 | 0.041199 | -0.013733 | 0.35248 | 0.23346 | -121.0602 | 0.34332 | 0.40283 | 0.16937 | -121.0373 | 0.36163 | 0.3067 | -121.0968 | 0.27008 | 0.21057 | -0.09613 | -121.0602 | 0.3067 | 0.32959 | 0.37079 | -121.1334 | 0.27008 | 0.3067 | 0.39826 | -121.0602
3447.9219 | 121.3348 | -0.30212 | 121.0648 | -0.0049592 | 0.015122 | 0.019045 | 0.0018884 | 0.032509 | -0.0035633 | -0.045463 | -0.028381 | 0.0083335 | -0.015274 | -0.0033133 | 2.5485 | 0.027068 | 0.036621 | 0.07782 | 0.091553 | 0.10986 | -0.018311 | 0.032043 | -0.068665 | 0 | 0.12817 | -0.045776 | -0.064087 | -0.050354 | 0.064087 | 0.013733 | 0.33417 | 0.23346 | -121.0831 | 0.37994 | 0.41199 | 0.17853 | -121.0281 | 0.36621 | 0.31586 | -121.1288 | 0.30212 | 0.25635 | -0.059509 | -121.1151 | 0.28381 | 0.33875 | 0.39368 | -121.1334 | 0.23804 | 0.25177 | 0.4303 | -121.051
3449.6875 | 121.4584 | -0.24261 | 121.0373 | -0.0049592 | 0.01085 | 0.019045 | 0.0025292 | 0.033364 | -0.0018543 | -0.046318 | 0.0021363 | 0.0074789 | -0.013351 | -0.0024589 | 2.5688 | 0.027709 | 0.027466 | 0.054932 | 0.082397 | 0.10529 | -0.013733 | 0.041199 | -0.07782 | 0.027466 | 0.15106 | 0 | -0.082397 | -0.050354 | 0.082397 | 0.022888 | 0.28381 | 0.16479 | -121.051 | 0.29755 | 0.3479 | 0.18311 | -121.0098 | 0.32501 | 0.2655 | -121.1197 | 0.27008 | 0.24261 | -0.022888 | -121.0876 | 0.22888 | 0.27008 | 0.32501 | -121.1151 | 0.16022 | 0.19226 | 0.39368 | -121.0144
3451.3906 | 121.344 | -0.29297 | 121.106 | -0.020218 | 0.014909 | 0.017549 | 0.0042382 | 0.032082 | 0.00070927 | -0.046745 | -0.020752 | 0.01111 | -0.011856 | -0.0016043 | 2.5628 | 0.027068 | -0.059509 | -0.064087 | -0.041199 | 0.022888 | 0.013733 | 0.004578 | -0.091553 | -0.10071 | -0.009155 | -0.16022 | -0.018311 | 0.013733 | 0.032043 | -0.022888 | 0.29755 | 0.20142 | -121.0922 | 0.22888 | 0.31586 | 0.11444 | -121.1655 | 0.32501 | 0.27008 | -121.1243 | 0.19226 | 0.13275 | -0.13733 | -121.0922 | 0.3067 | 0.23346 | 0.25177 | -121.1975 | 0.27466 | 0.3067 | 0.28381 | -121.1288
3453.1719 | 121.4401 | -0.27466 | 121.0739 | -0.012589 | 0.01085 | 0.020113 | 0.00060662 | 0.032295 | -0.0022815 | -0.046318 | -0.020752 | 0.0076925 | -0.016556 | -0.00032249 | 2.5493 | 0.025573 | -0.013733 | -0.004578 | 0.041199 | 0.050354 | -0.027466 | 0.027466 | -0.073242 | -0.036621 | 0.059509 | -0.073242 | -0.059509 | -0.059509 | 0.059509 | 0 | 0.30212 | 0.20142 | -121.1014 | 0.27008 | 0.32501 | 0.1236 | -121.0876 | 0.33417 | 0.27466 | -121.1334 | 0.23804 | 0.20142 | -0.073242 | -121.1334 | 0.24719 | 0.26093 | 0.31586 | -121.1472 | 0.21515 | 0.21515 | 0.33417 | -121.0739
3454.9531 | 121.4859 | -0.25177 | 121.051 | 0.0026703 | 0.011918 | 0.017976 | -0.00046138 | 0.032723 | 0.0030591 | -0.044822 | -0.0054932 | 0.011324 | -0.015488 | -0.0022453 | 2.5515 | 0.026427 | -0.013733 | -0.027466 | 0.009155 | 0.050354 | 0.022888 | 0.032043 | -0.091553 | 0 | 0.054932 | -0.073242 | -0.068665 | -0.027466 | 0.068665 | 0.013733 | 0.28381 | 0.16022 | -121.0281 | 0.2243 | 0.30212 | 0.14191 | -121.0648 | 0.32044 | 0.2655 | -121.1197 | 0.25177 | 0.17853 | -0.086975 | -121.0785 | 0.27466 | 0.23804 | 0.26093 | -121.1426 | 0.1831 | 0.2243 | 0.3067 | -121.0373
3456.6719 | 121.3806 | -0.31128 | 121.0968 | 0.0026703 | 0.011491 | 0.01819 | 0.0027428 | 0.031227 | 0.00049567 | -0.045891 | -0.020752 | 0.0091879 | -0.015488 | -0.0011771 | 2.5278 | 0.025573 | -0.064087 | -0.059509 | -0.027466 | 0.013733 | 0.041199 | -0.009155 | -0.10986 | -0.086975 | 0.004578 | -0.15564 | -0.013733 | -0.009155 | 0.036621 | -0.027466 | 0.30212 | 0.20142 | -121.0556 | 0.25177 | 0.32501 | 0.1236 | -121.1609 | 0.3479 | 0.28381 | -121.1105 | 0.2243 | 0.15564 | -0.12817 | -121.106 | 0.35248 | 0.24719 | 0.28381 | -121.2067 | 0.29755 | 0.30212 | 0.31586 | -121.1243
3458.4531 | 121.5088 | -0.2655 | 121.0922 | -0.012589 | 0.0093545 | 0.019472 | 0.0035974 | 0.030159 | -0.0042041 | -0.04525 | -0.0054932 | 0.0064109 | -0.01442 | -0.00053629 | 2.6055 | 0.029204 | -0.036621 | -0.013733 | 0.045776 | 0.068665 | -0.013733 | 0.036621 | -0.073242 | -0.050354 | 0.073242 | -0.059509 | -0.064087 | -0.045776 | 0.07782 | -0.004578 | 0.30212 | 0.19226 | -121.106 | 0.25177 | 0.33417 | 0.14191 | -121.1288 | 0.34332 | 0.26092 | -121.1563 | 0.21515 | 0.20599 | -0.054931 | -121.138 | 0.25177 | 0.22888 | 0.31128 | -121.1655 | 0.20142 | 0.21973 | 0.33874 | -121.0968
3460.2344 | 121.5088 | -0.24719 | 121.106 | -0.0049592 | 0.016404 | 0.01584 | 0.0018884 | 0.031441 | 0.0041273 | -0.044182 | -0.020752 | 0.011324 | -0.012283 | 0.00031831 | 2.5929 | 0.025786 | -0.013733 | -0.059509 | -0.009155 | 0.036621 | 0.018311 | 0.013733 | -0.086975 | -0.022888 | 0.027466 | -0.10529 | -0.045776 | -0.059509 | 0.064087 | 0 | 0.26093 | 0.16022 | -121.0876 | 0.18768 | 0.28381 | 0.1236 | -121.1197 | 0.31128 | 0.24719 | -121.1517 | 0.2243 | 0.14191 | -0.10529 | -121.1655 | 0.2655 | 0.23346 | 0.23804 | -121.1929 | 0.20142 | 0.18768 | 0.27466 | -121.106
3462.0156 | 121.4951 | -0.24719 | 121.1014 | -0.012589 | 0.011491 | 0.014986 | 0.00060662 | 0.032936 | 0.00092287 | -0.043113 | -0.013123 | 0.010042 | -0.014633 | 0.00031831 | 2.6418 | 0.025146 | 0.059509 | 0.054932 | 0.07782 | 0.11902 | -0.022888 | 0.068665 | -0.054932 | 0.059509 | 0.10071 | -0.036621 | -0.068665 | -0.059509 | 0.059509 | 0.027466 | 0.31586 | 0.19226 | -121.1243 | 0.30212 | 0.36621 | 0.17395 | -121.0419 | 0.3067 | 0.27466 | -121.17 | 0.3067 | 0.21057 | -0.064087 | -121.1609 | 0.2243 | 0.3067 | 0.32501 | -121.1563 | 0.17853 | 0.18768 | 0.3479 | -121.0739
3463.75 | 121.5134 | -0.2655 | 121.1105 | -0.012589 | 0.012559 | 0.017122 | 0.0042382 | 0.030159 | -0.0037769 | -0.044822 | -0.0054932 | 0.0074789 | -0.013138 | -0.00096349 | 2.6258 | 0.02835 | -0.036621 | -0.004578 | 0.036621 | 0.064087 | 0 | 0.022888 | -0.059509 | -0.045776 | 0.064087 | -0.07782 | -0.059509 | -0.032043 | 0.073242 | -0.009155 | 0.28839 | 0.20599 | -121.1105 | 0.26092 | 0.32959 | 0.1236 | -121.1472 | 0.33874 | 0.25635 | -121.17 | 0.21973 | 0.18768 | -0.068665 | -121.1426 | 0.2655 | 0.22888 | 0.30212 | -121.17 | 0.20599 | 0.23346 | 0.32959 | -121.1197
3465.5312 | 121.5179 | -0.26093 | 121.1243 | -0.0049592 | 0.013627 | 0.018404 | -0.00088858 | 0.031868 | -0.0024951 | -0.045036 | -0.020752 | 0.010897 | -0.016983 | -0.0018179 | 2.5876 | 0.025359 | 0.064087 | 0.10071 | 0.12817 | 0.11902 | -0.022888 | 0.045776 | -0.059509 | 0.013733 | 0.16022 | 0 | -0.064087 | -0.054932 | 0.068665 | 0.018311 | 0.3067 | 0.20142 | -121.1472 | 0.36163 | 0.37994 | 0.17853 | -121.0602 | 0.32959 | 0.27924 | -121.1884 | 0.27466 | 0.26093 | -0.018311 | -121.1792 | 0.23804 | 0.32501 | 0.3891 | -121.1838 | 0.19684 | 0.20599 | 0.42114 | -121.106
3467.3125 | 121.5546 | -0.26093 | 121.138 | -0.0049592 | 0.011704 | 0.01819 | 0.0016748 | 0.031868 | -0.0027087 | -0.046745 | -0.013123 | 0.0070517 | -0.014633 | 0.00053191 | 2.5479 | 0.024932 | -0.018311 | 0.013733 | 0.041199 | 0.064087 | 0 | 0.032043 | -0.064087 | -0.004578 | 0.082397 | -0.064087 | -0.059509 | -0.050354 | 0.064087 | 0.004578 | 0.29297 | 0.19684 | -121.138 | 0.27466 | 0.32501 | 0.12817 | -121.1563 | 0.32501 | 0.2655 | -121.1975 | 0.25635 | 0.19684 | -0.068665 | -121.1884 | 0.26093 | 0.24261 | 0.30212 | -121.2021 | 0.20142 | 0.21057 | 0.34332 | -121.1334
3469.1094 | 121.4218 | -0.28381 | 121.1838 | -0.012589 | 0.014909 | 0.014131 | 0.00060662 | 0.032509 | 0.0069043 | -0.043968 | -0.013123 | 0.014742 | -0.01506 | 0.00010471 | 2.5573 | 0.024077 | -0.022888 | -0.086975 | -0.041199 | 0.032043 | 0.022888 | 0.036621 | -0.09613 | -0.064087 | -0.032043 | -0.19684 | -0.041199 | -0.027466 | 0.054932 | -0.027466 | 0.32043 | 0.18768 | -121.1609 | 0.19684 | 0.31586 | 0.12817 | -121.2067 | 0.33874 | 0.25635 | -121.225 | 0.21973 | 0.086975 | -0.16937 | -121.2112 | 0.3067 | 0.26092 | 0.24261 | -121.2799 | 0.24261 | 0.25635 | 0.25177 | -121.2112
3470.8281 | 121.4813 | -0.30212 | 121.1884 | -0.012589 | 0.014695 | 0.01819 | 0.0025292 | 0.032723 | 0.0019909 | -0.044182 | -0.013123 | 0.0089743 | -0.013992 | -0.0030997 | 2.5863 | 0.027923 | -0.068665 | -0.059509 | -0.054932 | 0.027466 | 0.027466 | 0.022888 | -0.09613 | -0.091553 | 0.004578 | -0.16022 | -0.027466 | -0.022888 | 0.032043 | -0.036621 | 0.32501 | 0.20599 | -121.1609 | 0.24261 | 0.32959 | 0.1236 | -121.257 | 0.33417 | 0.2655 | -121.2158 | 0.21057 | 0.14191 | -0.1236 | -121.2112 | 0.32959 | 0.23346 | 0.24719 | -121.2845 | 0.27466 | 0.27924 | 0.3067 | -121.225
3472.6094 | 121.55 | -0.25635 | 121.1472 | -0.027847 | 0.0091409 | 0.019472 | 0.00017942 | 0.032082 | -0.0056995 | -0.045463 | 0.0021363 | 0.0066245 | -0.015915 | -0.0018179 | 2.4962 | 0.027282 | 0.041199 | 0.13275 | 0.11902 | 0.11902 | -0.022888 | 0.045776 | -0.054932 | 0.018311 | 0.15564 | -0.009155 | -0.068665 | -0.054932 | 0.073242 | 0.013733 | 0.30212 | 0.20142 | -121.17 | 0.3891 | 0.37537 | 0.17395 | -121.106 | 0.32959 | 0.27008 | -121.2158 | 0.27466 | 0.24719 | -0.022888 | -121.2021 | 0.23346 | 0.29755 | 0.37537 | -121.2021 | 0.18768 | 0.20142 | 0.41199 | -121.1334
3474.3906 | 121.4447 | -0.29755 | 121.2067 | -0.0049592 | 0.016404 | 0.017763 | 0.00039302 | 0.031868 | 0.0066907 | -0.045036 | -0.020752 | 0.011965 | -0.013351 | 0.0016001 | 2.6111 | 0.027068 | -0.036621 | -0.059509 | -0.036621 | 0.027466 | 0.022888 | 0 | -0.07782 | -0.064087 | -0.027466 | -0.16479 | -0.027466 | -0.022888 | 0.041199 | -0.022888 | 0.29755 | 0.21973 | -121.1838 | 0.23804 | 0.32501 | 0.10529 | -121.2433 | 0.33874 | 0.27466 | -121.2341 | 0.23346 | 0.13275 | -0.14191 | -121.2296 | 0.32043 | 0.26092 | 0.26092 | -121.2845 | 0.27008 | 0.27466 | 0.27008 | -121.2296
3476.1094 | 121.5775 | -0.25177 | 121.1609 | -0.0049592 | 0.011704 | 0.019258 | 0.001034 | 0.030373 | 0.0022047 | -0.042045 | -0.0054932 | 0.010256 | -0.015915 | 0.00095911 | 2.4878 | 0.027923 | -0.004578 | 0.009155 | 0.050354 | 0.086975 | -0.004578 | 0.036621 | -0.054932 | 0.032043 | 0.086975 | -0.059509 | -0.086975 | -0.050354 | 0.086975 | 0.022888 | 0.28839 | 0.19684 | -121.1655 | 0.26093 | 0.33874 | 0.14191 | -121.1655 | 0.33874 | 0.27466 | -121.2479 | 0.28381 | 0.19226 | -0.082397 | -121.2112 | 0.24719 | 0.24719 | 0.30212 | -121.2158 | 0.16479 | 0.20142 | 0.33874 | -121.138
3477.9062 | 121.5179 | -0.31128 | 121.2112 | -0.0049592 | 0.015336 | 0.016267 | 0.0023156 | 0.031227 | 0.0022047 | -0.042686 | -0.0054932 | 0.011324 | -0.016556 | -0.0013907 | 2.5656 | 0.026427 | -0.050354 | -0.054932 | -0.032043 | 0.041199 | 0.009155 | 0.004578 | -0.10529 | -0.059509 | 0.027466 | -0.13275 | -0.013733 | -0.009155 | 0.045776 | 0.004578 | 0.31586 | 0.20599 | -121.2021 | 0.25635 | 0.35248 | 0.14649 | -121.2616 | 0.35705 | 0.31586 | -121.225 | 0.25177 | 0.17853 | -0.13733 | -121.2204 | 0.32043 | 0.26092 | 0.27924 | -121.3165 | 0.29755 | 0.30212 | 0.33874 | -121.2067
3479.6875 | 121.5775 | -0.27466 | 121.2021 | -0.020218 | 0.012773 | 0.017549 | -0.00067498 | 0.0308 | 6.8274e-05 | -0.043968 | -0.020752 | 0.0091879 | -0.013779 | -0.0018179 | 2.5812 | 0.027923 | -0.059509 | -0.064087 | -0.036621 | 0.022888 | 0.013733 | 0.032043 | -0.10071 | -0.054932 | -0.018311 | -0.13733 | -0.027466 | -0.027466 | 0.041199 | -0.013733 | 0.3067 | 0.17395 | -121.1884 | 0.21057 | 0.29755 | 0.1236 | -121.2616 | 0.31586 | 0.26093 | -121.2296 | 0.21973 | 0.13733 | -0.1236 | -121.2296 | 0.28839 | 0.21515 | 0.23804 | -121.3028 | 0.24719 | 0.24719 | 0.25635 | -121.2158
3481.4688 | 121.5408 | -0.27466 | 121.1975 | -0.0049592 | 0.012345 | 0.019472 | 0.0027428 | 0.031441 | -0.0037769 | -0.046531 | -0.0054932 | 0.0079063 | -0.015488 | -0.0039541 | 2.463 | 0.029204 | 0.018311 | 0.091553 | 0.10529 | 0.10529 | -0.018311 | 0.045776 | -0.054932 | 0.004578 | 0.14648 | -0.018311 | -0.086975 | -0.045776 | 0.082397 | 0.018311 | 0.32043 | 0.21973 | -121.2158 | 0.36621 | 0.37994 | 0.16022 | -121.1792 | 0.35706 | 0.29297 | -121.2845 | 0.27924 | 0.25635 | -0.036622 | -121.2433 | 0.25635 | 0.29297 | 0.37994 | -121.2524 | 0.18768 | 0.22888 | 0.42114 | -121.1792
3483.1875 | 121.582 | -0.26093 | 121.2112 | -0.012589 | 0.011704 | 0.015627 | -0.00088858 | 0.03315 | 0.0019909 | -0.04525 | -0.013123 | 0.0066245 | -0.017197 | -0.0013907 | 2.4577 | 0.027068 | 0.036621 | 0.059509 | 0.10071 | 0.10986 | -0.032043 | 0.064087 | -0.059509 | 0.022888 | 0.10529 | -0.009155 | -0.082397 | -0.054932 | 0.082397 | 0.022888 | 0.32501 | 0.20142 | -121.2433 | 0.32043 | 0.37079 | 0.16937 | -121.1746 | 0.34332 | 0.28381 | -121.2936 | 0.28381 | 0.25177 | -0.032043 | -121.2662 | 0.22888 | 0.29755 | 0.36163 | -121.2708 | 0.17853 | 0.20599 | 0.36621 | -121.1884
3484.9688 | 121.6095 | -0.26093 | 121.2112 | -0.020218 | 0.011918 | 0.018831 | 0.00552 | 0.031441 | -0.0037769 | -0.045036 | 0.0021363 | 0.0061973 | -0.01506 | -0.0026725 | 2.4355 | 0.025573 | 0.045776 | 0.091553 | 0.13275 | 0.10986 | -0.013733 | 0.050354 | -0.064087 | 0 | 0.15564 | -0.009155 | -0.064087 | -0.050354 | 0.07782 | 0.004578 | 0.31128 | 0.19684 | -121.225 | 0.35248 | 0.37079 | 0.17395 | -121.1655 | 0.33875 | 0.2655 | -121.2753 | 0.26093 | 0.25177 | -0.013733 | -121.2616 | 0.24719 | 0.3067 | 0.39368 | -121.2753 | 0.19684 | 0.21057 | 0.41657 | -121.2067
3486.75 | 121.5088 | -0.31128 | 121.2112 | -0.012589 | 0.017259 | 0.017549 | 0.00039302 | 0.035927 | 0.0058363 | -0.044822 | -0.0054932 | 0.012606 | -0.01506 | -0.00096349 | 2.4925 | 0.025786 | -0.050354 | -0.073242 | -0.045776 | 0.027466 | 0.018311 | 0.022888 | -0.10529 | -0.07782 | -0.045776 | -0.17853 | -0.032043 | -0.018311 | 0.045776 | -0.022888 | 0.33417 | 0.20599 | -121.1929 | 0.23804 | 0.33874 | 0.13275 | -121.2616 | 0.35705 | 0.28839 | -121.2433 | 0.23346 | 0.13275 | -0.15564 | -121.2296 | 0.32959 | 0.26092 | 0.2655 | -121.3165 | 0.27924 | 0.29297 | 0.2655 | -121.2341
3488.4688 | 121.6278 | -0.29297 | 121.2204 | -0.012589 | 0.011064 | 0.016908 | 0.00017942 | 0.032295 | -0.0056995 | -0.04525 | -0.013123 | 0.0061973 | -0.016129 | -0.00032249 | 2.5577 | 0.028136 | -0.027466 | 0 | 0.045776 | 0.073242 | -0.004578 | 0.041199 | -0.07782 | -0.050354 | 0.059509 | -0.07782 | -0.064087 | -0.032043 | 0.07782 | 0.009155 | 0.33417 | 0.21515 | -121.225 | 0.29297 | 0.36621 | 0.15106 | -121.2479 | 0.37079 | 0.30212 | -121.2845 | 0.24261 | 0.21515 | -0.086975 | -121.2524 | 0.28839 | 0.2655 | 0.33874 | -121.2982 | 0.22888 | 0.26093 | 0.35248 | -121.2112
3490.25 | 121.5729 | -0.29297 | 121.2753 | -0.0049592 | 0.012986 | 0.017976 | 0.0040246 | 0.032509 | -0.0018543 | -0.043968 | -0.013123 | 0.0079063 | -0.013565 | -0.0016043 | 2.525 | 0.025786 | 0.050354 | 0.086975 | 0.09613 | 0.10986 | -0.009155 | 0.036621 | -0.064087 | 0.009155 | 0.15106 | -0.027466 | -0.073242 | -0.054932 | 0.073242 | 0.009155 | 0.32959 | 0.22888 | -121.2845 | 0.37994 | 0.40283 | 0.17395 | -121.225 | 0.36621 | 0.30212 | -121.3486 | 0.30212 | 0.2655 | -0.036621 | -121.3303 | 0.28381 | 0.34332 | 0.3891 | -121.3394 | 0.21973 | 0.23804 | 0.44403 | -121.2662
3492.0312 | 121.637 | -0.2655 | 121.2158 | -0.0049592 | 0.013413 | 0.017976 | 0.0018884 | 0.033364 | -0.0022815 | -0.043754 | 0.0021363 | 0.0068381 | -0.014206 | -0.00032249 | 2.5199 | 0.025359 | 0.059509 | 0.10071 | 0.14191 | 0.13275 | -0.018311 | 0.054932 | -0.082397 | 0.027466 | 0.14648 | -0.013733 | -0.073242 | -0.045776 | 0.082397 | 0.027466 | 0.32043 | 0.18311 | -121.2341 | 0.36621 | 0.39825 | 0.21515 | -121.1563 | 0.3479 | 0.29297 | -121.2891 | 0.29297 | 0.25177 | -0.041199 | -121.2616 | 0.24719 | 0.32501 | 0.40741 | -121.2982 | 0.19226 | 0.21973 | 0.41199 | -121.1884
3493.8125 | 121.6049 | -0.29755 | 121.2387 | -0.0049592 | 0.0087137 | 0.017336 | -3.4178e-05 | 0.030586 | 6.8274e-05 | -0.044182 | -0.013123 | 0.0085471 | -0.017624 | -0.00074989 | 2.5081 | 0.024932 | 0.054932 | 0.045776 | 0.086975 | 0.086975 | -0.022888 | 0.059509 | -0.050354 | -0.009155 | 0.064087 | -0.068665 | -0.068665 | -0.059509 | 0.086975 | 0.013733 | 0.35705 | 0.24719 | -121.2616 | 0.34332 | 0.38452 | 0.13733 | -121.1838 | 0.38452 | 0.31128 | -121.3074 | 0.28839 | 0.22888 | -0.082398 | -121.2982 | 0.27466 | 0.35248 | 0.38452 | -121.2891 | 0.22888 | 0.23804 | 0.36163 | -121.225
3495.5938 | 121.4996 | -0.31586 | 121.2708 | -0.0049592 | 0.016191 | 0.015413 | -0.0021704 | 0.033791 | 0.0064771 | -0.041404 | -0.0054932 | 0.012819 | -0.015488 | 0.00095911 | 2.6357 | 0.022582 | 0.022888 | -0.045776 | -0.018311 | 0.036621 | 0.022888 | 0.032043 | -0.10071 | -0.041199 | 0.009155 | -0.14191 | -0.041199 | -0.018311 | 0.059509 | -0.009155 | 0.3479 | 0.21515 | -121.2479 | 0.27008 | 0.35248 | 0.13733 | -121.2479 | 0.37537 | 0.3067 | -121.312 | 0.27466 | 0.17395 | -0.13275 | -121.2891 | 0.33875 | 0.33875 | 0.29755 | -121.3715 | 0.27466 | 0.29755 | 0.32501 | -121.2799
3497.3594 | 121.6187 | -0.27924 | 121.2387 | -0.012589 | 0.010636 | 0.017122 | 0.00017942 | 0.031441 | -0.00078613 | -0.042259 | -0.013123 | 0.0087607 | -0.016983 | 0.00010471 | 2.6098 | 0.025359 | 0.059509 | 0.045776 | 0.091553 | 0.10986 | -0.027466 | 0.059509 | -0.045776 | 0.041199 | 0.10986 | -0.032043 | -0.073242 | -0.064087 | 0.073242 | 0.018311 | 0.33874 | 0.23346 | -121.2662 | 0.32501 | 0.3891 | 0.15564 | -121.1792 | 0.35248 | 0.29755 | -121.3119 | 0.32043 | 0.24719 | -0.050354 | -121.3028 | 0.25177 | 0.33874 | 0.37079 | -121.2845 | 0.20599 | 0.21515 | 0.3891 | -121.2204
3499.0938 | 121.6278 | -0.29297 | 121.2479 | -0.0049592 | 0.0061501 | 0.017549 | 0.00039302 | 0.031227 | -0.0012133 | -0.044395 | -0.0054932 | 0.0087607 | -0.015915 | -0.00010889 | 2.4827 | 0.028991 | 0.036621 | 0.027466 | 0.086975 | 0.086975 | -0.027466 | 0.036621 | -0.050354 | -0.004578 | 0.059509 | -0.050354 | -0.059509 | -0.059509 | 0.073242 | 0.022888 | 0.32959 | 0.24261 | -121.2753 | 0.32043 | 0.37994 | 0.13733 | -121.2112 | 0.36621 | 0.31586 | -121.3074 | 0.28839 | 0.24261 | -0.073242 | -121.3074 | 0.2655 | 0.32959 | 0.37994 | -121.2982 | 0.23346 | 0.23346 | 0.35248 | -121.225
3500.875 | 121.6003 | -0.30212 | 121.2708 | -0.0049592 | 0.018754 | 0.015413 | 0.001034 | 0.032295 | 0.0036999 | -0.043754 | -0.013123 | 0.012392 | -0.013992 | -0.00096349 | 2.5308 | 0.023437 | 0.009155 | -0.041199 | -0.004578 | 0.054932 | 0.041199 | 0.009155 | -0.10071 | -0.036621 | 0.032043 | -0.11444 | -0.036621 | -0.018311 | 0.022888 | -0.018311 | 0.31128 | 0.20142 | -121.2296 | 0.26093 | 0.35706 | 0.15564 | -121.2616 | 0.32501 | 0.28381 | -121.3074 | 0.2655 | 0.18768 | -0.09613 | -121.2891 | 0.34332 | 0.31128 | 0.29755 | -121.3715 | 0.2655 | 0.28381 | 0.33417 | -121.2891
3502.6406 | 121.6003 | -0.32044 | 121.2662 | -0.012589 | 0.017259 | 0.016054 | -3.4178e-05 | 0.032295 | 0.0028455 | -0.043968 | -0.013123 | 0.010897 | -0.014633 | -0.00010889 | 2.5314 | 0.025359 | -0.013733 | -0.013733 | 0.013733 | 0.059509 | 0.022888 | 0.009155 | -0.10071 | -0.032043 | 0.050354 | -0.11444 | -0.050354 | -0.032043 | 0.050354 | -0.018311 | 0.32959 | 0.21973 | -121.2433 | 0.3067 | 0.37994 | 0.16022 | -121.2799 | 0.37079 | 0.30212 | -121.3165 | 0.28839 | 0.20599 | -0.09613 | -121.2982 | 0.34332 | 0.3067 | 0.33417 | -121.3669 | 0.27008 | 0.28839 | 0.37079 | -121.2845
3504.4219 | 121.5683 | -0.34332 | 121.2982 | -0.0049592 | 0.015122 | 0.017122 | 0.0053064 | 0.033791 | 0.00028207 | -0.044822 | -0.020752 | 0.010256 | -0.013779 | -0.00032249 | 2.6068 | 0.026214 | -0.032043 | 0.004578 | 0.018311 | 0.073242 | 0.009155 | 0.009155 | -0.086975 | -0.07782 | 0.036621 | -0.10986 | -0.027466 | -0.013733 | 0.041199 | -0.013733 | 0.35248 | 0.25635 | -121.2891 | 0.3479 | 0.41656 | 0.16022 | -121.3303 | 0.38452 | 0.32959 | -121.3257 | 0.2655 | 0.23346 | -0.09613 | -121.312 | 0.35248 | 0.31128 | 0.36163 | -121.3852 | 0.31586 | 0.32959 | 0.37994 | -121.312
3506.1406 | 121.6461 | -0.29755 | 121.2753 | -0.0049592 | 0.014054 | 0.019045 | 0.0027428 | 0.030586 | -0.0022815 | -0.043113 | -0.0054932 | 0.0068381 | -0.013351 | -0.00074989 | 2.4583 | 0.026214 | 0 | 0.004578 | 0.054932 | 0.068665 | 0 | 0.050354 | -0.059509 | -0.032043 | 0.064087 | -0.059509 | -0.068665 | -0.045776 | 0.068665 | 0.018311 | 0.3479 | 0.23804 | -121.2753 | 0.30212 | 0.36621 | 0.12817 | -121.2753 | 0.36621 | 0.31586 | -121.344 | 0.2655 | 0.23804 | -0.07782 | -121.3211 | 0.29755 | 0.29755 | 0.35248 | -121.3348 | 0.22888 | 0.25177 | 0.36163 | -121.257
3507.9219 | 121.5912 | -0.31128 | 121.312 | -0.0049592 | 0.0132 | 0.017549 | 0.0044518 | 0.028664 | -0.0018543 | -0.046745 | -0.013123 | 0.01047 | -0.012497 | 0.00053191 | 2.5041 | 0.027282 | -0.050354 | -0.064087 | -0.032043 | 0.027466 | 0.032043 | 0.009155 | -0.10071 | -0.091553 | 0.004578 | -0.16479 | -0.022888 | -0.004578 | 0.032043 | -0.032043 | 0.32043 | 0.21057 | -121.2799 | 0.24719 | 0.33874 | 0.12817 | -121.3623 | 0.34332 | 0.27924 | -121.3348 | 0.21973 | 0.14648 | -0.13275 | -121.3165 | 0.34332 | 0.26092 | 0.27924 | -121.4127 | 0.28839 | 0.3067 | 0.31586 | -121.344
3509.7031 | 121.6095 | -0.32044 | 121.2845 | -0.0049592 | 0.014909 | 0.016695 | -0.0032386 | 0.031868 | 0.0041273 | -0.042686 | -0.013123 | 0.01047 | -0.01506 | -0.00053629 | 2.4703 | 0.027923 | -0.059509 | -0.09613 | -0.068665 | 0.022888 | 0.027466 | 0.009155 | -0.091553 | -0.082397 | -0.050354 | -0.16937 | -0.045776 | -0.013733 | 0.041199 | -0.013733 | 0.32959 | 0.22888 | -121.257 | 0.22431 | 0.34332 | 0.11444 | -121.344 | 0.36163 | 0.3067 | -121.3303 | 0.23804 | 0.15106 | -0.15564 | -121.2982 | 0.3479 | 0.26093 | 0.25177 | -121.376 | 0.27466 | 0.3067 | 0.27008 | -121.2982
3511.4219 | 121.6782 | -0.29297 | 121.2753 | -0.0049592 | 0.0132 | 0.016695 | 0.00039302 | 0.033577 | -0.0012133 | -0.043113 | -0.020752 | 0.0064109 | -0.016556 | -0.0020315 | 2.5436 | 0.027282 | 0.036621 | 0.064087 | 0.09613 | 0.10529 | -0.022888 | 0.059509 | -0.059509 | 0.045776 | 0.10529 | -0.018311 | -0.073242 | -0.036621 | 0.068665 | 0.022888 | 0.35248 | 0.23346 | -121.2982 | 0.35706 | 0.39825 | 0.16479 | -121.2387 | 0.36163 | 0.31586 | -121.3486 | 0.33874 | 0.27466 | -0.041199 | -121.312 | 0.27008 | 0.32959 | 0.3891 | -121.3348 | 0.21973 | 0.25635 | 0.39825 | -121.2524
3513.2031 | 121.6507 | -0.33417 | 121.3348 | -0.0049592 | 0.017686 | 0.015413 | 0.0033838 | 0.032509 | 0.0019909 | -0.045463 | -0.013123 | 0.0096151 | -0.013992 | 0.00095911 | 2.5549 | 0.024505 | -0.041199 | -0.07782 | -0.022888 | 0.032043 | 0.018311 | 0.004578 | -0.10529 | -0.059509 | 0.022888 | -0.13275 | -0.041199 | -0.004578 | 0.045776 | -0.022888 | 0.33875 | 0.22888 | -121.3165 | 0.25635 | 0.36621 | 0.13733 | -121.376 | 0.37994 | 0.31128 | -121.376 | 0.27466 | 0.20142 | -0.10986 | -121.3394 | 0.35248 | 0.29297 | 0.31128 | -121.4401 | 0.29297 | 0.32959 | 0.35706 | -121.3577
3514.9844 | 121.6553 | -0.32044 | 121.3257 | -0.0049592 | 0.016404 | 0.014558 | 0.0031702 | 0.032936 | 0.0015637 | -0.043754 | -0.020752 | 0.010042 | -0.012283 | 0.0018137 | 2.4468 | 0.025359 | -0.018311 | -0.054932 | -0.004578 | 0.073242 | 0.018311 | 0.045776 | -0.10071 | -0.036621 | 0.045776 | -0.10071 | -0.041199 | -0.018311 | 0.041199 | -0.022888 | 0.36621 | 0.21973 | -121.3074 | 0.2655 | 0.39368 | 0.17395 | -121.344 | 0.36163 | 0.29755 | -121.3669 | 0.28381 | 0.21973 | -0.07782 | -121.344 | 0.33875 | 0.30212 | 0.31586 | -121.4264 | 0.27924 | 0.30212 | 0.36621 | -121.3486
3516.7031 | 121.7422 | -0.29297 | 121.2982 | -0.012589 | 0.012773 | 0.016908 | 0.0065882 | 0.0308 | -0.0063403 | -0.045036 | 0.0021363 | 0.0047019 | -0.013351 | -0.0013907 | 2.4432 | 0.029632 | -0.036621 | 0 | 0.050354 | 0.073242 | -0.018311 | 0.041199 | -0.091553 | -0.022888 | 0.09613 | -0.027466 | -0.068665 | -0.032043 | 0.068665 | 0.013733 | 0.33417 | 0.20142 | -121.3165 | 0.29297 | 0.36621 | 0.16479 | -121.3348 | 0.36163 | 0.3067 | -121.3669 | 0.27008 | 0.2655 | -0.041199 | -121.3303 | 0.27466 | 0.25635 | 0.34332 | -121.3898 | 0.2243 | 0.26093 | 0.3891 | -121.2845
3518.5 | 121.5958 | -0.34332 | 121.3394 | -0.0049592 | 0.0132 | 0.016695 | -0.002384 | 0.0308 | 0.0058363 | -0.045677 | -0.013123 | 0.013033 | -0.013992 | 0.0022409 | 2.5775 | 0.024077 | -0.059509 | -0.11444 | -0.059509 | 0.004578 | 0.022888 | 0.009155 | -0.10986 | -0.10071 | -0.054932 | -0.19684 | -0.027466 | -0.013733 | 0.045776 | -0.032043 | 0.35248 | 0.23346 | -121.3165 | 0.22888 | 0.3479 | 0.11444 | -121.3989 | 0.3891 | 0.31128 | -121.3669 | 0.24261 | 0.14648 | -0.1648 | -121.3531 | 0.36621 | 0.28381 | 0.28381 | -121.4493 | 0.31586 | 0.32959 | 0.28839 | -121.3715
3520.2812 | 121.6278 | -0.33417 | 121.3394 | -0.0049592 | 0.021745 | 0.01584 | 0.0023156 | 0.029732 | 0.0024183 | -0.044395 | -0.0054932 | 0.012819 | -0.01442 | 0.00010471 | 2.522 | 0.023864 | -0.050354 | -0.11902 | -0.050354 | 0.018311 | 0.022888 | 0.022888 | -0.091553 | -0.086975 | -0.045776 | -0.16937 | -0.027466 | -0.009155 | 0.050354 | -0.018311 | 0.35706 | 0.24261 | -121.3165 | 0.21515 | 0.35248 | 0.10986 | -121.3898 | 0.38452 | 0.31586 | -121.3669 | 0.24719 | 0.16479 | -0.15106 | -121.3486 | 0.35706 | 0.28381 | 0.28381 | -121.431 | 0.3067 | 0.32501 | 0.28839 | -121.3577
3522.0156 | 121.7422 | -0.31586 | 121.3348 | -0.0049592 | 0.011704 | 0.01819 | 0.0025292 | 0.0308 | -0.0067675 | -0.045463 | -0.0054932 | 0.0055563 | -0.013565 | 0.00074551 | 2.4748 | 0.028136 | 0.050354 | 0.10986 | 0.11902 | 0.10986 | -0.018311 | 0.059509 | -0.064087 | 0.018311 | 0.15106 | -0.004578 | -0.07782 | -0.045776 | 0.068665 | -0.004578 | 0.37537 | 0.25177 | -121.3531 | 0.42572 | 0.42572 | 0.17395 | -121.2845 | 0.38452 | 0.31128 | -121.4127 | 0.33417 | 0.31128 | 0 | -121.3806 | 0.29755 | 0.36621 | 0.43488 | -121.3989 | 0.23804 | 0.27008 | 0.46692 | -121.3394
3523.7969 | 121.7606 | -0.31128 | 121.3211 | 0.0026703 | 0.015336 | 0.017549 | -0.00046138 | 0.033577 | 0.0015637 | -0.045891 | -0.0054932 | 0.01111 | -0.015701 | 0.00053191 | 2.5256 | 0.026214 | -0.045776 | -0.091553 | -0.054932 | 0.032043 | 0.036621 | 0.009155 | -0.10986 | -0.068665 | -0.018311 | -0.13275 | -0.027466 | -0.022888 | 0.036621 | -0.018311 | 0.32043 | 0.20142 | -121.2845 | 0.21973 | 0.34332 | 0.14191 | -121.3669 | 0.3479 | 0.29297 | -121.3486 | 0.24261 | 0.17853 | -0.11444 | -121.344 | 0.3479 | 0.2655 | 0.25635 | -121.431 | 0.28381 | 0.28839 | 0.29297 | -121.3394
3525.5781 | 121.7651 | -0.32044 | 121.2753 | -0.012589 | 0.0085001 | 0.019258 | 0.0033838 | 0.033364 | -0.0056995 | -0.045677 | -0.013123 | 0.0068381 | -0.016556 | -0.0030997 | 2.5165 | 0.028136 | -0.009155 | 0.045776 | 0.07782 | 0.10071 | 0 | 0.032043 | -0.050354 | 0 | 0.12817 | -0.009155 | -0.064087 | -0.050354 | 0.073242 | 0.009155 | 0.35248 | 0.27008 | -121.2753 | 0.36621 | 0.42114 | 0.15106 | -121.2845 | 0.39368 | 0.32959 | -121.3394 | 0.32044 | 0.31128 | -0.01831 | -121.3257 | 0.32044 | 0.31128 | 0.39826 | -121.3257 | 0.25635 | 0.27008 | 0.44861 | -121.2662
3527.2812 | 121.6461 | -0.34332 | 121.3394 | -0.012589 | 0.019181 | 0.013277 | 0.0044518 | 0.031441 | 0.0049817 | -0.044609 | -0.013123 | 0.01111 | -0.012711 | 0.0016001 | 2.5566 | 0.025359 | -0.050354 | -0.09613 | -0.041199 | 0.027466 | 0.022888 | 0.004578 | -0.10071 | -0.082397 | -0.059509 | -0.19684 | -0.032043 | -0.013733 | 0.045776 | -0.022888 | 0.3479 | 0.24261 | -121.3165 | 0.24719 | 0.37079 | 0.12817 | -121.3898 | 0.3891 | 0.32043 | -121.3715 | 0.26093 | 0.14648 | -0.17395 | -121.3531 | 0.36621 | 0.29297 | 0.30212 | -121.4401 | 0.31128 | 0.32959 | 0.28381 | -121.3623
3529.0781 | 121.6553 | -0.36163 | 121.3623 | -0.012589 | 0.012559 | 0.016054 | 0.00082022 | 0.032509 | -0.0037769 | -0.04525 | -0.0054932 | 0.0087607 | -0.012497 | -0.0013907 | 2.5256 | 0.028991 | 0.009155 | 0.050354 | 0.073242 | 0.091553 | -0.013733 | 0.027466 | -0.07782 | -0.045776 | 0.082397 | -0.09613 | -0.054932 | -0.027466 | 0.064087 | -0.004578 | 0.3891 | 0.28381 | -121.376 | 0.41199 | 0.45319 | 0.16937 | -121.3531 | 0.42572 | 0.35705 | -121.4172 | 0.31586 | 0.2655 | -0.091552 | -121.3898 | 0.3479 | 0.37079 | 0.43488 | -121.4401 | 0.3067 | 0.33417 | 0.44403 | -121.3669
3530.8594 | 121.7926 | -0.31586 | 121.3348 | -0.0049592 | 0.013413 | 0.019045 | 0.0053064 | 0.030373 | -0.0037769 | -0.046745 | -0.0054932 | 0.0066245 | -0.015701 | -0.00053629 | 2.4541 | 0.026641 | 0.036621 | 0.073242 | 0.073242 | 0.1236 | -0.004578 | 0.036621 | -0.054932 | 0.013733 | 0.15106 | 0.004578 | -0.07782 | -0.045776 | 0.064087 | 0.018311 | 0.35248 | 0.26093 | -121.3394 | 0.3891 | 0.43945 | 0.17853 | -121.2982 | 0.37994 | 0.33417 | -121.4127 | 0.32959 | 0.32044 | -0.013733 | -121.3806 | 0.31128 | 0.35248 | 0.3891 | -121.3898 | 0.23804 | 0.27008 | 0.46692 | -121.3165
3532.5781 | 121.6736 | -0.35706 | 121.3348 | -0.012589 | 0.015122 | 0.016481 | -0.0017432 | 0.029946 | 0.0045545 | -0.044609 | -0.013123 | 0.011538 | -0.012924 | -0.00032249 | 2.5436 | 0.026427 | -0.050354 | -0.11444 | -0.054932 | 0.027466 | 0.009155 | 0.004578 | -0.09613 | -0.064087 | -0.041199 | -0.16937 | -0.009155 | -0.013733 | 0.054932 | 0 | 0.36163 | 0.26093 | -121.3257 | 0.24261 | 0.38452 | 0.1236 | -121.3852 | 0.41199 | 0.35706 | -121.344 | 0.29297 | 0.18768 | -0.16937 | -121.3486 | 0.36621 | 0.3067 | 0.30212 | -121.431 | 0.3479 | 0.34332 | 0.31586 | -121.3348
3534.375 | 121.669 | -0.37079 | 121.3531 | -0.0049592 | 0.01555 | 0.01349 | -0.00088858 | 0.032509 | 0.0060499 | -0.043541 | -0.0054932 | 0.011751 | -0.014847 | 0.00010471 | 2.4481 | 0.026 | -0.068665 | -0.10529 | -0.064087 | 0.022888 | 0.027466 | 0.009155 | -0.091553 | -0.07782 | -0.036621 | -0.18768 | -0.022888 | -0.022888 | 0.041199 | -0.018311 | 0.37994 | 0.27924 | -121.3257 | 0.2655 | 0.39368 | 0.11444 | -121.4218 | 0.41199 | 0.35248 | -121.376 | 0.29297 | 0.18311 | -0.16937 | -121.376 | 0.39825 | 0.30212 | 0.3067 | -121.4447 | 0.3479 | 0.3479 | 0.33417 | -121.3715
3536.1406 | 121.7834 | -0.32501 | 121.3165 | -0.0049592 | 0.0085001 | 0.019899 | 0.0014612 | 0.032936 | -0.0052721 | -0.043541 | -0.020752 | 0.0055563 | -0.016769 | -0.00053629 | 2.4964 | 0.028564 | -0.041199 | -0.013733 | 0.022888 | 0.068665 | 0.009155 | 0.036621 | -0.054932 | -0.041199 | 0.064087 | -0.059509 | -0.073242 | -0.050354 | 0.073242 | 0.009155 | 0.36163 | 0.27008 | -121.3074 | 0.31128 | 0.39368 | 0.1236 | -121.3577 | 0.39825 | 0.33417 | -121.3898 | 0.28381 | 0.2655 | -0.068664 | -121.3669 | 0.33417 | 0.28381 | 0.3479 | -121.3715 | 0.25177 | 0.27466 | 0.3891 | -121.3074
3537.8594 | 121.7972 | -0.31128 | 121.312 | -0.012589 | 0.014482 | 0.01584 | 0.0016748 | 0.030159 | 0.0019909 | -0.043968 | -0.013123 | 0.011538 | -0.015701 | -0.00010889 | 2.444 | 0.026 | -0.041199 | -0.073242 | -0.027466 | 0.018311 | 0.022888 | 0.027466 | -0.10986 | -0.036621 | 0.018311 | -0.09613 | -0.054932 | -0.022888 | 0.064087 | 0.004578 | 0.33874 | 0.20142 | -121.2891 | 0.23804 | 0.32959 | 0.12817 | -121.3531 | 0.37537 | 0.31586 | -121.3669 | 0.27466 | 0.21515 | -0.10071 | -121.3348 | 0.33417 | 0.27008 | 0.28381 | -121.4218 | 0.25635 | 0.28839 | 0.32959 | -121.3074
3539.6406 | 121.7239 | -0.37079 | 121.3394 | -0.0049592 | 0.014909 | 0.015627 | 0.0031702 | 0.03315 | 0.0032727 | -0.043541 | -0.020752 | 0.01111 | -0.013351 | -0.00032249 | 2.4323 | 0.025359 | -0.041199 | -0.032043 | 0 | 0.059509 | 0.004578 | 0.018311 | -0.10071 | -0.032043 | 0.041199 | -0.13733 | -0.045776 | -0.009155 | 0.027466 | -0.009155 | 0.3891 | 0.27008 | -121.3348 | 0.33875 | 0.4303 | 0.16022 | -121.3806 | 0.39825 | 0.36163 | -121.3852 | 0.33875 | 0.23346 | -0.12817 | -121.3486 | 0.37537 | 0.32959 | 0.37079 | -121.4401 | 0.32501 | 0.36163 | 0.41199 | -121.3486
3541.4219 | 121.756 | -0.93842 | 120.726 | -0.020218 | 0.012773 | 0.017763 | 0.0053064 | 0.03315 | -0.0039905 | -0.043327 | -0.013123 | 0.0042747 | -0.014206 | -0.0039541 | 2.4141 | 0.026855 | 0.018311 | 0.091553 | 0.10529 | 0.1236 | -0.022888 | 0.041199 | -0.073242 | 0.022888 | 0.16022 | -0.004578 | -0.059509 | -0.050354 | 0.073242 | 0.013733 | 0.97962 | 0.86517 | -120.7489 | 1.03 | 1.062 | 0.19684 | -120.7077 | 1.0117 | 0.95215 | -120.7855 | 0.9613 | 0.93384 | -0.018311 | -120.7764 | 0.91553 | 0.95673 | 1.0437 | -120.7993 | 0.87891 | 0.88806 | 1.0986 | -120.7123
3543.2031 | 121.8018 | -0.98419 | 120.6573 | -0.0049592 | 0.014909 | 0.017976 | -0.00046138 | 0.030159 | 0.0039135 | -0.045036 | -0.0054932 | 0.010683 | -0.016342 | 0.00053191 | 2.4293 | 0.026 | -0.045776 | -0.082397 | -0.041199 | 0.018311 | 0.022888 | 0.022888 | -0.086975 | -0.050354 | -0.018311 | -0.13275 | -0.009155 | -0.032043 | 0.054932 | 0.004578 | 1.0071 | 0.89722 | -120.6345 | 0.90179 | 1.0025 | 0.10529 | -120.7031 | 1.0391 | 0.98877 | -120.6665 | 0.93384 | 0.85144 | -0.13733 | -120.6894 | 1.0071 | 0.93842 | 0.94299 | -120.7443 | 0.97504 | 0.95215 | 0.96588 | -120.6528
3544.9219 | 121.7514 | -1.0574 | 120.5887 | -0.0049592 | 0.0089273 | 0.018617 | -3.4178e-05 | 0.030159 | -0.0042041 | -0.044822 | -0.020752 | 0.0068381 | -0.01741 | -0.0018179 | 2.4304 | 0.027068 | -0.013733 | 0.009155 | 0.036621 | 0.073242 | -0.004578 | 0.054932 | -0.064087 | -0.045776 | 0.054932 | -0.059509 | -0.064087 | -0.045776 | 0.054932 | 0.009155 | 1.1124 | 0.99335 | -120.5933 | 1.0666 | 1.1307 | 0.13733 | -120.6024 | 1.1124 | 1.0666 | -120.6528 | 1.0117 | 0.99792 | -0.068664 | -120.6345 | 1.0529 | 1.0437 | 1.0941 | -120.6528 | 0.99335 | 1.0117 | 1.1124 | -120.5795
3546.7031 | 121.8063 | -1.0895 | 120.52 | -0.012589 | 0.012986 | 0.016695 | 0.00082022 | 0.032936 | 0.00092287 | -0.0429 | -0.013123 | 0.010897 | -0.01506 | -0.00096349 | 2.4699 | 0.027709 | -0.013733 | -0.054932 | -0.009155 | 0.045776 | 0.009155 | 0.036621 | -0.07782 | -0.018311 | 0.041199 | -0.073242 | -0.064087 | -0.022888 | 0.068665 | 0.009155 | 1.1261 | 1.0117 | -120.5109 | 1.0345 | 1.1353 | 0.1236 | -120.5338 | 1.1581 | 1.0986 | -120.5841 | 1.0712 | 1.0162 | -0.082397 | -120.5429 | 1.0986 | 1.0757 | 1.0803 | -120.5978 | 1.0254 | 1.0666 | 1.1307 | -120.5109
3548.4688 | 121.7697 | -1.1765 | 120.5246 | -0.012589 | 0.014695 | 0.019258 | -0.00046138 | 0.029732 | 0.0030591 | -0.043968 | -0.0054932 | 0.011965 | -0.015488 | 0.0020273 | 2.5004 | 0.027068 | -0.054932 | -0.082397 | -0.054932 | 0.027466 | 0.050354 | -0.004578 | -0.10071 | -0.082397 | -0.022888 | -0.15106 | -0.041199 | -0.022888 | 0.022888 | -0.018311 | 1.1719 | 1.0757 | -120.4742 | 1.0941 | 1.2039 | 0.12817 | -120.5795 | 1.1993 | 1.1581 | -120.5658 | 1.0941 | 1.0254 | -0.13275 | -120.5475 | 1.2268 | 1.1215 | 1.1215 | -120.6253 | 1.1353 | 1.1536 | 1.1536 | -120.5429
3550.1875 | 121.8109 | -0.94757 | 120.7123 | -0.012589 | 0.014482 | 0.015627 | 0.0023156 | 0.032936 | -0.00057253 | -0.042259 | -0.013123 | 0.0094015 | -0.014633 | 0.00074551 | 2.4398 | 0.027709 | -0.013733 | -0.032043 | 0.009155 | 0.068665 | 0.009155 | 0.032043 | -0.064087 | 0.009155 | 0.054932 | -0.073242 | -0.073242 | -0.050354 | 0.082397 | 0.004578 | 0.97961 | 0.88348 | -120.7031 | 0.91553 | 1.0162 | 0.13275 | -120.726 | 1.03 | 0.95215 | -120.7855 | 0.95673 | 0.87433 | -0.07782 | -120.7626 | 0.95673 | 0.93384 | 0.95673 | -120.7764 | 0.87433 | 0.89722 | 1.0025 | -120.7077
3551.9688 | 121.7285 | -0.96588 | 120.7352 | -0.012589 | 0.017045 | 0.016054 | 0.0033838 | 0.031227 | 0.0045545 | -0.043113 | -0.013123 | 0.0091879 | -0.013351 | 0.00010471 | 2.5075 | 0.024291 | -0.045776 | -0.032043 | -0.009155 | 0.054932 | 0.013733 | 0.004578 | -0.091553 | -0.036621 | 0.036621 | -0.12817 | -0.032043 | -0.027466 | 0.041199 | -0.009155 | 0.97046 | 0.87433 | -120.7214 | 0.93384 | 1.0208 | 0.14649 | -120.7809 | 1.0071 | 0.95673 | -120.7672 | 0.92926 | 0.83771 | -0.11902 | -120.7626 | 0.97961 | 0.9201 | 0.95673 | -120.8267 | 0.93384 | 0.93841 | 1.0025 | -120.7443
3553.75 | 121.8018 | -0.99335 | 120.6573 | -0.0049592 | 0.011277 | 0.017549 | 0.00017942 | 0.031868 | -0.0016405 | -0.045036 | -0.0054932 | 0.0059837 | -0.012711 | 0.00074551 | 2.5179 | 0.026641 | 0.027466 | 0.050354 | 0.082397 | 0.10529 | -0.009155 | 0.050354 | -0.068665 | 0.027466 | 0.10529 | -0.041199 | -0.073242 | -0.054932 | 0.086975 | 0.032043 | 1.0437 | 0.92468 | -120.6665 | 1.0437 | 1.0986 | 0.17395 | -120.6299 | 1.0803 | 1.0254 | -120.7306 | 1.0208 | 0.95215 | -0.073242 | -120.7123 | 0.98419 | 1.0208 | 1.0757 | -120.726 | 0.9201 | 0.93841 | 1.0986 | -120.6253
3555.5312 | 121.6873 | -1.2085 | 120.52 | -0.012589 | 0.02089 | 0.017549 | 0.0059472 | 0.030586 | 0.0036999 | -0.043541 | -0.0054932 | 0.01111 | -0.012711 | 0.00010471 | 2.4639 | 0.024932 | -0.059509 | -0.059509 | -0.036621 | 0.027466 | 0.013733 | 0.013733 | -0.082397 | -0.07782 | -0.018311 | -0.16479 | -0.036621 | -0.009155 | 0.041199 | -0.013733 | 1.2222 | 1.1261 | -120.5063 | 1.149 | 1.236 | 0.10986 | -120.5795 | 1.2497 | 1.1948 | -120.5566 | 1.1307 | 1.0437 | -0.15106 | -120.5292 | 1.2222 | 1.149 | 1.1719 | -120.6024 | 1.1719 | 1.1993 | 1.1902 | -120.5338
3557.2344 | 121.7743 | -0.81482 | 120.8679 | -0.020218 | 0.014482 | 0.014131 | -0.00024778 | 0.032509 | 0.0017773 | -0.043327 | -0.0054932 | 0.011324 | -0.015915 | -0.00053629 | 2.4857 | 0.028136 | -0.064087 | -0.086975 | -0.054932 | 0.022888 | 0.027466 | 0.018311 | -0.10986 | -0.091553 | -0.032043 | -0.16479 | -0.036621 | -0.022888 | 0.045776 | -0.022888 | 0.83313 | 0.70496 | -120.8405 | 0.72784 | 0.83771 | 0.13275 | -120.932 | 0.86059 | 0.79193 | -120.9045 | 0.72327 | 0.65002 | -0.14191 | -120.8908 | 0.84228 | 0.75073 | 0.75989 | -120.9778 | 0.7782 | 0.79193 | 0.78278 | -120.8908
3559.0312 | 121.7102 | -1.1078 | 120.6436 | -0.020218 | 0.016404 | 0.015413 | 0.00017942 | 0.031014 | 0.0022047 | -0.044182 | -0.0054932 | 0.010683 | -0.014206 | 0.0013863 | 2.4737 | 0.027923 | -0.054932 | -0.11444 | -0.050354 | 0.018311 | 0.018311 | -0.004578 | -0.11902 | -0.10529 | -0.036621 | -0.16937 | -0.054932 | -0.032043 | 0.032043 | -0.018311 | 1.1032 | 0.98877 | -120.6253 | 0.99335 | 1.1261 | 0.13733 | -120.6985 | 1.1398 | 1.0895 | -120.6985 | 1.0025 | 0.93841 | -0.15106 | -120.6757 | 1.1261 | 1.0529 | 1.0574 | -120.7626 | 1.0529 | 1.0757 | 1.0712 | -120.6619
3560.8125 | 121.8201 | -1.1765 | 120.5109 | -0.0049592 | 0.01555 | 0.013918 | 0.00017942 | 0.031014 | -0.00099973 | -0.04525 | -0.020752 | 0.010256 | -0.013565 | -0.00010889 | 2.5062 | 0.027068 | -0.054932 | -0.054932 | -0.036621 | 0.027466 | 0.013733 | 0.018311 | -0.10071 | -0.045776 | 0.022888 | -0.10529 | -0.045776 | -0.027466 | 0.054932 | -0.004578 | 1.1948 | 1.0757 | -120.4971 | 1.1215 | 1.2039 | 0.12817 | -120.5658 | 1.2314 | 1.1719 | -120.5566 | 1.1307 | 1.0712 | -0.10071 | -120.5383 | 1.1902 | 1.1215 | 1.1398 | -120.6116 | 1.1307 | 1.149 | 1.1993 | -120.5154
3562.5938 | 121.8338 | -1.7395 | 119.9295 | -0.012589 | 0.012345 | 0.017763 | 0.0031702 | 0.030586 | -0.0039905 | -0.045463 | 0.0021363 | 0.0038473 | -0.016556 | -0.00074989 | 2.431 | 0.027282 | -0.045776 | -0.004578 | 0.041199 | 0.068665 | 0.004578 | 0.045776 | -0.073242 | -0.041199 | 0.073242 | -0.064087 | -0.059509 | -0.041199 | 0.07782 | 0.018311 | 1.7853 | 1.6663 | -119.9249 | 1.7349 | 1.8082 | 0.14191 | -119.9753 | 1.8173 | 1.7578 | -119.989 | 1.6983 | 1.6754 | -0.082398 | -119.9707 | 1.7441 | 1.6937 | 1.7807 | -120.0027 | 1.68 | 1.6983 | 1.8127 | -119.9112
3564.375 | 121.7651 | -1.8585 | 119.8013 | -0.012589 | 0.010636 | 0.017336 | 0.001034 | 0.0308 | -0.0042041 | -0.047813 | -0.013123 | 0.0059837 | -0.012924 | -0.00010889 | 2.4246 | 0.027068 | 0.004578 | 0.036621 | 0.068665 | 0.073242 | -0.018311 | 0.054932 | -0.068665 | -0.027466 | 0.073242 | -0.050354 | -0.068665 | -0.050354 | 0.082397 | 0.013733 | 1.9135 | 1.7899 | -119.8196 | 1.8951 | 1.9318 | 0.14191 | -119.7968 | 1.9409 | 1.8723 | -119.87 | 1.8311 | 1.8082 | -0.064087 | -119.8517 | 1.8402 | 1.8631 | 1.9272 | -119.87 | 1.7899 | 1.8082 | 1.9318 | -119.7876
3566.1406 | 121.8155 | -1.8082 | 119.8288 | -0.0049592 | 0.010423 | 0.019472 | 0.00060662 | 0.034859 | -0.0046313 | -0.045677 | 0.0021363 | 0.0068381 | -0.016983 | -0.0020315 | 2.462 | 0.027068 | -0.036621 | 0 | 0.050354 | 0.064087 | 0 | 0.045776 | -0.054932 | -0.027466 | 0.082397 | -0.059509 | -0.07782 | -0.045776 | 0.07782 | 0.004578 | 1.8539 | 1.7532 | -119.8288 | 1.8082 | 1.8723 | 0.11902 | -119.8654 | 1.886 | 1.8127 | -119.9066 | 1.7807 | 1.7487 | -0.064087 | -119.8746 | 1.8082 | 1.7715 | 1.8585 | -119.8837 | 1.7303 | 1.7624 | 1.8906 | -119.8242
3567.9219 | 121.7606 | -1.8448 | 119.8471 | -0.012589 | 0.014268 | 0.018617 | 0.0040246 | 0.029732 | -0.00078613 | -0.045036 | -0.013123 | 0.0070517 | -0.016983 | -0.0013907 | 2.4889 | 0.025786 | 0.045776 | 0.07782 | 0.10986 | 0.11902 | -0.013733 | 0.054932 | -0.073242 | 0.022888 | 0.12817 | -0.013733 | -0.086975 | -0.045776 | 0.091553 | 0.004578 | 1.8997 | 1.7715 | -119.8608 | 1.9226 | 1.9638 | 0.19226 | -119.8013 | 1.9363 | 1.8494 | -119.9341 | 1.8677 | 1.8311 | -0.018311 | -119.8929 | 1.8311 | 1.8906 | 1.9547 | -119.9203 | 1.7578 | 1.799 | 1.973 | -119.8425
3569.6562 | 121.7651 | -2.2614 | 119.4168 | -0.012589 | 0.013413 | 0.013918 | 0.0016748 | 0.029946 | 6.8274e-05 | -0.045036 | -0.0054932 | 0.0072653 | -0.013992 | 0.00053191 | 2.4586 | 0.025786 | 0.045776 | 0.041199 | 0.09613 | 0.091553 | -0.009155 | 0.054932 | -0.064087 | -0.004578 | 0.068665 | -0.045776 | -0.064087 | -0.041199 | 0.073242 | 0.022888 | 2.3163 | 2.1973 | -119.426 | 2.3026 | 2.3529 | 0.15564 | -119.371 | 2.3346 | 2.2842 | -119.4809 | 2.2568 | 2.2156 | -0.068664 | -119.458 | 2.2522 | 2.3071 | 2.3575 | -119.4809 | 2.1973 | 2.2202 | 2.33 | -119.3939
3571.4375 | 121.7697 | -2.0325 | 119.6182 | -0.012589 | 0.012132 | 0.018617 | -0.0021704 | 0.0308 | 0.00092287 | -0.044395 | -0.0054932 | 0.0085471 | -0.017197 | 0.00053191 | 2.4902 | 0.024077 | 0.073242 | 0.045776 | 0.086975 | 0.10986 | 0.009155 | 0.054932 | -0.054932 | 0.036621 | 0.10986 | -0.036621 | -0.07782 | -0.050354 | 0.073242 | 0.022888 | 2.0874 | 1.9775 | -119.6091 | 2.0782 | 2.1423 | 0.16479 | -119.545 | 2.1057 | 2.0554 | -119.696 | 2.0691 | 1.9959 | -0.059509 | -119.6686 | 2.0416 | 2.1057 | 2.1194 | -119.6732 | 1.9547 | 1.9821 | 2.1423 | -119.5953
3573.2188 | 121.7148 | -2.0462 | 119.6915 | -0.012589 | 0.016831 | 0.016695 | 0.0016748 | 0.031441 | 0.0056225 | -0.044395 | -0.0054932 | 0.01346 | -0.011642 | 0.00031831 | 2.4977 | 0.024077 | 0.009155 | -0.032043 | 0.013733 | 0.07782 | 0.018311 | 0.022888 | -0.091553 | -0.013733 | 0.041199 | -0.11444 | -0.041199 | -0.013733 | 0.059509 | -0.013733 | 2.0691 | 1.9547 | -119.6732 | 2.0142 | 2.124 | 0.16937 | -119.6823 | 2.1057 | 2.0325 | -119.7327 | 2.0325 | 1.9318 | -0.10071 | -119.7052 | 2.0645 | 2.0554 | 2.0599 | -119.783 | 2.005 | 2.0325 | 2.0874 | -119.7052
3574.9531 | 121.8201 | -2.2614 | 119.4214 | -0.012589 | 0.011704 | 0.017549 | 0.0035974 | 0.028878 | -0.0050585 | -0.044182 | -0.0054932 | 0.0042747 | -0.015701 | -0.00053629 | 2.6111 | 0.027282 | 0.054932 | 0.10071 | 0.12817 | 0.13275 | -0.009155 | 0.045776 | -0.068665 | 0.032043 | 0.16479 | -0.018311 | -0.073242 | -0.050354 | 0.07782 | 0.013733 | 2.3071 | 2.1927 | -119.4305 | 2.3621 | 2.3941 | 0.20142 | -119.3665 | 2.3392 | 2.2751 | -119.4946 | 2.2934 | 2.243 | -0.032044 | -119.4717 | 2.2522 | 2.3163 | 2.3895 | -119.4901 | 2.1881 | 2.211 | 2.4261 | -119.4077
3576.7344 | 121.7468 | -2.655 | 119.046 | -0.0049592 | 0.016404 | 0.015413 | 0.0016748 | 0.030586 | 0.0036999 | -0.043113 | -0.020752 | 0.012606 | -0.015488 | 0.00010471 | 2.6025 | 0.024077 | 0.004578 | -0.036621 | 0 | 0.064087 | 0.027466 | 0.027466 | -0.10529 | -0.009155 | 0.050354 | -0.11444 | -0.050354 | -0.013733 | 0.054932 | -0.004578 | 2.6825 | 2.5497 | -119.0186 | 2.6184 | 2.7191 | 0.16937 | -119.0414 | 2.71 | 2.6505 | -119.0964 | 2.6459 | 2.5406 | -0.10986 | -119.0598 | 2.6825 | 2.6596 | 2.655 | -119.1513 | 2.6047 | 2.6413 | 2.7054 | -119.0506
3578.5 | 121.6873 | -2.6688 | 119.0186 | -0.012589 | 0.015977 | 0.01584 | 0.00017942 | 0.031868 | 0.0024183 | -0.043113 | -0.013123 | 0.01111 | -0.014633 | 0.0024545 | 2.4891 | 0.024291 | -0.018311 | -0.054932 | 0 | 0.068665 | 0.013733 | 0.013733 | -0.10529 | -0.022888 | 0.050354 | -0.12817 | -0.045776 | -0.018311 | 0.054932 | 0 | 2.6825 | 2.5635 | -119.0048 | 2.6138 | 2.7374 | 0.17395 | -119.0369 | 2.7237 | 2.6688 | -119.0643 | 2.6459 | 2.5406 | -0.12817 | -119.0369 | 2.6825 | 2.6505 | 2.6688 | -119.1238 | 2.623 | 2.6505 | 2.7191 | -119.0186
3580.2344 | 121.6827 | -2.7969 | 118.7988 | -0.012589 | 0.011704 | 0.018617 | 0.00082022 | 0.034645 | -0.0042041 | -0.043754 | -0.0054932 | 0.0064109 | -0.016129 | -0.0018179 | 2.556 | 0.027923 | 0.004578 | 0.036621 | 0.064087 | 0.07782 | -0.027466 | 0.050354 | -0.041199 | -0.032043 | 0.082397 | -0.068665 | -0.073242 | -0.045776 | 0.073242 | 0.004578 | 2.8473 | 2.7557 | -118.8263 | 2.8336 | 2.8748 | 0.11902 | -118.7943 | 2.8702 | 2.8015 | -118.8721 | 2.7649 | 2.7283 | -0.073243 | -118.8446 | 2.7695 | 2.8015 | 2.861 | -118.84 | 2.7237 | 2.7512 | 2.8793 | -118.7943
3582.0469 | 121.6232 | -2.9114 | 118.7439 | -0.0049592 | 0.015122 | 0.018617 | 0.0033838 | 0.032936 | 0.00092287 | -0.044395 | -0.013123 | 0.010042 | -0.013565 | 0.00010471 | 2.4447 | 0.025573 | -0.054932 | -0.059509 | -0.032043 | 0.032043 | 0.036621 | 0.018311 | -0.10986 | -0.086975 | 0.004578 | -0.14191 | -0.013733 | -0.009155 | 0.027466 | -0.018311 | 2.9297 | 2.8015 | -118.7073 | 2.8519 | 2.9434 | 0.14191 | -118.7988 | 2.9388 | 2.8931 | -118.7576 | 2.8244 | 2.7695 | -0.1236 | -118.7531 | 2.948 | 2.8564 | 2.8793 | -118.8538 | 2.8976 | 2.9022 | 2.916 | -118.7622
3583.8281 | 121.6736 | -2.9572 | 118.6111 | -0.0049592 | 0.011918 | 0.017549 | 0.0031702 | 0.032936 | -0.0067675 | -0.044609 | -0.0054932 | 0.0094015 | -0.016129 | -0.00096349 | 2.4417 | 0.026214 | 0.036621 | 0.086975 | 0.10529 | 0.11444 | -0.018311 | 0.041199 | -0.068665 | 0.027466 | 0.15564 | -0.004578 | -0.07782 | -0.059509 | 0.073242 | 0.018311 | 2.9984 | 2.8885 | -118.6295 | 3.0441 | 3.0716 | 0.18311 | -118.5745 | 3.0304 | 2.9755 | -118.689 | 2.9846 | 2.9526 | -0.022889 | -118.6707 | 2.9388 | 2.9938 | 3.0624 | -118.6798 | 2.8793 | 2.8976 | 3.1128 | -118.5928
3585.5469 | 121.6644 | -3.0396 | 118.5196 | -0.012589 | 0.01085 | 0.017763 | -0.00088858 | 0.03315 | -0.00099973 | -0.046531 | -0.013123 | 0.0083335 | -0.016129 | -0.0037405 | 2.4921 | 0.027068 | 0.054932 | 0.086975 | 0.10529 | 0.10986 | -0.013733 | 0.045776 | -0.054932 | 0.018311 | 0.15564 | -0.013733 | -0.086975 | -0.041199 | 0.07782 | 0.027466 | 3.0853 | 2.9846 | -118.5333 | 3.1265 | 3.1494 | 0.16479 | -118.4647 | 3.1174 | 3.067 | -118.6066 | 3.0579 | 3.0258 | -0.041199 | -118.5608 | 3.0258 | 3.0945 | 3.1448 | -118.5745 | 2.9526 | 2.9984 | 3.1952 | -118.4921
3587.3125 | 121.7056 | -3.0808 | 118.428 | -0.020218 | 0.014695 | 0.01819 | -0.00046138 | 0.028237 | 0.0019909 | -0.044609 | -0.013123 | 0.010042 | -0.015488 | -0.0020315 | 2.4575 | 0.027709 | 0.045776 | 0.045776 | 0.082397 | 0.11444 | -0.032043 | 0.050354 | -0.064087 | 0.054932 | 0.11444 | -0.045776 | -0.082397 | -0.064087 | 0.086975 | 0.032043 | 3.1311 | 3.0167 | -118.4601 | 3.1265 | 3.1952 | 0.17853 | -118.3823 | 3.1677 | 3.1128 | -118.5104 | 3.1357 | 3.035 | -0.077819 | -118.4921 | 3.0487 | 3.1265 | 3.1631 | -118.4921 | 2.9984 | 3.0167 | 3.1952 | -118.396
3589.0781 | 121.6461 | -3.1586 | 118.3777 | -0.020218 | 0.014268 | 0.019045 | 0.0050928 | 0.030373 | -0.0029223 | -0.045891 | -0.013123 | 0.0087607 | -0.016342 | -0.0016043 | 2.5079 | 0.026214 | 0.073242 | 0.082397 | 0.11444 | 0.11444 | -0.018311 | 0.041199 | -0.073242 | 0.018311 | 0.15106 | -0.013733 | -0.073242 | -0.045776 | 0.082397 | 0.022888 | 3.1998 | 3.0853 | -118.396 | 3.241 | 3.273 | 0.18768 | -118.3044 | 3.241 | 3.1815 | -118.4509 | 3.1769 | 3.1448 | -0.036621 | -118.4235 | 3.1403 | 3.2318 | 3.273 | -118.4509 | 3.0853 | 3.1128 | 3.3096 | -118.3548
3590.875 | 121.6187 | -3.186 | 118.3868 | -0.012589 | 0.013841 | 0.016695 | 0.00017942 | 0.032936 | 0.0032727 | -0.044182 | -0.013123 | 0.012606 | -0.013565 | -0.0024589 | 2.5966 | 0.023437 | -0.009155 | -0.073242 | -0.032043 | 0.036621 | 0.022888 | 0.013733 | -0.11444 | -0.059509 | 0.032043 | -0.13275 | -0.018311 | -0.004578 | 0.036621 | -0.022888 | 3.1998 | 3.0716 | -118.364 | 3.1128 | 3.2227 | 0.15106 | -118.396 | 3.2227 | 3.1631 | -118.4052 | 3.1265 | 3.0533 | -0.10986 | -118.3914 | 3.2089 | 3.1769 | 3.154 | -118.5013 | 3.1677 | 3.1815 | 3.2181 | -118.4097
3592.5938 | 121.6599 | -3.9139 | 117.572 | -0.020218 | 0.0099953 | 0.018831 | 0.0033838 | 0.032723 | -0.0035633 | -0.046745 | -0.013123 | 0.0064109 | -0.015701 | -0.0026725 | 2.528 | 0.027282 | -0.009155 | -0.013733 | 0.050354 | 0.064087 | -0.009155 | 0.032043 | -0.059509 | -0.045776 | 0.059509 | -0.068665 | -0.059509 | -0.036621 | 0.073242 | 0.018311 | 3.9459 | 3.8544 | -117.5812 | 3.9001 | 3.978 | 0.1236 | -117.5812 | 3.9871 | 3.9322 | -117.6315 | 3.8681 | 3.8452 | -0.086976 | -117.6086 | 3.9047 | 3.9047 | 3.9642 | -117.6315 | 3.8544 | 3.8773 | 3.9734 | -117.5537
3594.375 | 121.6324 | -3.5751 | 118.0435 | -0.0049592 | 0.017472 | 0.016267 | 0.001034 | 0.032936 | 0.0045545 | -0.043541 | -0.013123 | 0.011538 | -0.013138 | -0.0013907 | 2.5566 | 0.024291 | -0.032043 | -0.059509 | -0.032043 | 0.045776 | 0.032043 | 0.009155 | -0.10986 | -0.086975 | 0.027466 | -0.14648 | -0.041199 | -0.009155 | 0.036621 | -0.018311 | 3.5843 | 3.4653 | -118.0115 | 3.5156 | 3.6209 | 0.15564 | -118.0756 | 3.6118 | 3.5568 | -118.0847 | 3.4882 | 3.4286 | -0.12817 | -118.0527 | 3.6072 | 3.5431 | 3.5431 | -118.1534 | 3.5339 | 3.566 | 3.6026 | -118.0618
3596.1094 | 121.6553 | -7.7133 | 113.7268 | -0.0049592 | 0.016831 | 0.014558 | 0.00060662 | 0.033791 | 0.0026319 | -0.043541 | -0.013123 | 0.0085471 | -0.013138 | 0.00095911 | 2.4368 | 0.023437 | 0.018311 | -0.027466 | 0.013733 | 0.059509 | 0.013733 | 0.059509 | -0.068665 | 0.009155 | 0.086975 | -0.054932 | -0.045776 | -0.036621 | 0.073242 | 0.018311 | 7.7728 | 7.6447 | -113.7131 | 7.6859 | 7.7728 | 0.12817 | -113.7085 | 7.7866 | 7.7316 | -113.7726 | 7.7225 | 7.6584 | -0.073243 | -113.7634 | 7.7271 | 7.7316 | 7.7271 | -113.7955 | 7.6675 | 7.6767 | 7.8003 | -113.7085
3597.8906 | 121.6003 | -3.8727 | 117.7048 | -0.020218 | 0.015122 | 0.019045 | 0.0031702 | 0.031014 | -0.00099973 | -0.045036 | -0.020752 | 0.011751 | -0.014847 | -0.0016043 | 2.4613 | 0.026855 | -0.054932 | -0.064087 | -0.041199 | 0.032043 | 0.041199 | 0.018311 | -0.09613 | -0.09613 | 0.004578 | -0.16022 | -0.032043 | 0 | 0.022888 | -0.013733 | 3.891 | 3.7766 | -117.6636 | 3.8086 | 3.9047 | 0.12817 | -117.7597 | 3.8956 | 3.8589 | -117.7368 | 3.7766 | 3.7125 | -0.14648 | -117.7048 | 3.9139 | 3.8177 | 3.8315 | -117.8009 | 3.8406 | 3.8727 | 3.8773 | -117.7185
3599.6719 | 121.6141 | -4.1885 | 117.3615 | -0.012589 | 0.017259 | 0.016695 | 0.00017942 | 0.034432 | 0.0015637 | -0.045463 | -0.0054932 | 0.011751 | -0.01442 | -0.0018179 | 2.4731 | 0.026641 | -0.032043 | -0.050354 | -0.018311 | 0.068665 | 0.018311 | 0.022888 | -0.10071 | -0.032043 | 0.050354 | -0.10529 | -0.041199 | -0.022888 | 0.036621 | -0.009155 | 4.2114 | 4.0878 | -117.3431 | 4.1382 | 4.2572 | 0.16937 | -117.3935 | 4.2252 | 4.1794 | -117.4026 | 4.1565 | 4.0833 | -0.096131 | -117.3843 | 4.2068 | 4.1565 | 4.1702 | -117.4622 | 4.1473 | 4.1657 | 4.2389 | -117.3706
3601.4375 | 121.7102 | -4.3121 | 117.2379 | -0.0049592 | 0.011277 | 0.02054 | 0.0014612 | 0.031868 | -0.0063403 | -0.045891 | -0.013123 | 0.0055563 | -0.013565 | -0.0026725 | 2.4927 | 0.029418 | -0.041199 | 0.018311 | 0.064087 | 0.068665 | 0.004578 | 0.050354 | -0.086975 | -0.036621 | 0.10986 | -0.041199 | -0.054932 | -0.045776 | 0.07782 | 0 | 4.3625 | 4.2252 | -117.2333 | 4.3304 | 4.3808 | 0.15564 | -117.2791 | 4.39 | 4.3121 | -117.2928 | 4.2755 | 4.2709 | -0.041199 | -117.2836 | 4.3167 | 4.2709 | 4.3762 | -117.3248 | 4.2572 | 4.2664 | 4.422 | -117.2379
3603.1562 | 121.6827 | -4.3808 | 117.1143 | -0.020218 | 0.011918 | 0.018831 | 0.00082022 | 0.031227 | 0.00092287 | -0.043968 | -0.013123 | 0.0096151 | -0.018051 | -0.00074989 | 2.5314 | 0.02835 | 0.054932 | 0.059509 | 0.091553 | 0.10986 | -0.004578 | 0.054932 | -0.045776 | 0.041199 | 0.10071 | -0.027466 | -0.11444 | -0.064087 | 0.09613 | 0.027466 | 4.4357 | 4.335 | -117.1188 | 4.4403 | 4.4907 | 0.15564 | -117.0593 | 4.4769 | 4.4083 | -117.2287 | 4.422 | 4.3533 | -0.054932 | -117.1783 | 4.3762 | 4.4357 | 4.4724 | -117.16 | 4.2664 | 4.3167 | 4.4815 | -117.0868
3604.9375 | 121.6919 | -4.5181 | 116.9724 | -0.0049592 | 0.012345 | 0.016267 | 0.0044518 | 0.03315 | -0.0042041 | -0.04824 | -0.0054932 | 0.0083335 | -0.01442 | -0.00096349 | 2.5246 | 0.026427 | -0.027466 | 0 | 0.059509 | 0.073242 | 0 | 0.041199 | -0.059509 | -0.027466 | 0.07782 | -0.045776 | -0.082397 | -0.032043 | 0.073242 | -0.009155 | 4.5593 | 4.4586 | -116.9724 | 4.5181 | 4.5914 | 0.13275 | -116.9998 | 4.5914 | 4.509 | -117.0547 | 4.4907 | 4.4724 | -0.036621 | -117.0044 | 4.5181 | 4.4907 | 4.5776 | -117.0319 | 4.4357 | 4.4861 | 4.5959 | -116.9815
3606.6562 | 121.6095 | -6.3858 | 115.0635 | 0.0026703 | 0.0093545 | 0.017336 | 0.001034 | 0.030586 | 0.0013501 | -0.043541 | -0.013123 | 0.0091879 | -0.017197 | -0.0016043 | 2.4733 | 0.025573 | 0.041199 | 0.073242 | 0.10529 | 0.11902 | -0.009155 | 0.064087 | -0.045776 | 0.045776 | 0.10071 | -0.027466 | -0.073242 | -0.041199 | 0.10071 | 0.027466 | 6.4499 | 6.34 | -115.0726 | 6.459 | 6.5048 | 0.16479 | -115.0223 | 6.4865 | 6.4133 | -115.1367 | 6.4316 | 6.3583 | -0.054932 | -115.1047 | 6.3766 | 6.427 | 6.4911 | -115.1093 | 6.3126 | 6.3446 | 6.4865 | -115.036
3608.4219 | 121.6095 | -8.2214 | 113.1454 | -0.0049592 | 0.01085 | 0.015413 | -0.0019568 | 0.031441 | 0.00049567 | -0.044182 | -0.013123 | 0.0089743 | -0.015274 | -0.0022453 | 2.5139 | 0.024505 | 0.064087 | 0.059509 | 0.091553 | 0.1236 | 0.009155 | 0.073242 | -0.036621 | 0.050354 | 0.09613 | -0.027466 | -0.073242 | -0.073242 | 0.082397 | 0.027466 | 8.2947 | 8.1848 | -113.1363 | 8.2809 | 8.345 | 0.16022 | -113.0814 | 8.3038 | 8.2489 | -113.2187 | 8.2718 | 8.194 | -0.054932 | -113.2187 | 8.2306 | 8.2855 | 8.313 | -113.1821 | 8.1482 | 8.1482 | 8.3176 | -113.118
3610.1562 | 121.5179 | -8.3496 | 113.0219 | -0.012589 | 0.012986 | 0.016054 | 0.0033838 | 0.028237 | -0.0018543 | -0.047172 | -0.020752 | 0.0072653 | -0.015274 | -0.0028861 | 2.5075 | 0.02835 | 0.004578 | 0.013733 | 0.054932 | 0.082397 | -0.004578 | 0.064087 | -0.059509 | -0.022888 | 0.059509 | -0.07782 | -0.041199 | -0.045776 | 0.073242 | 0.018311 | 8.4137 | 8.2901 | -113.0264 | 8.3633 | 8.432 | 0.14191 | -113.0173 | 8.4229 | 8.3679 | -113.0631 | 8.3267 | 8.2718 | -0.096131 | -113.0676 | 8.345 | 8.3542 | 8.4045 | -113.0814 | 8.3084 | 8.3038 | 8.4091 | -113.0035
3611.9375 | 121.4355 | -10.8261 | 110.5499 | -0.012589 | 0.019609 | 0.015627 | 0.00082022 | 0.034004 | 0.0045545 | -0.044609 | -0.0054932 | 0.014956 | -0.015488 | -0.00074989 | 2.5109 | 0.024718 | 0.045776 | 0.004578 | 0.022888 | 0.07782 | 0.018311 | 0.027466 | -0.07782 | -0.004578 | 0.054932 | -0.11444 | -0.027466 | -0.027466 | 0.059509 | 0.004578 | 10.8536 | 10.7483 | -110.5316 | 10.8307 | 10.9039 | 0.15564 | -110.5042 | 10.8856 | 10.8307 | -110.5774 | 10.8215 | 10.7117 | -0.11902 | -110.5774 | 10.8444 | 10.8719 | 10.849 | -110.6277 | 10.7986 | 10.7986 | 10.881 | -110.5453
3613.7188 | 121.4905 | -9.169 | 112.1613 | -0.012589 | 0.01085 | 0.019258 | 0.0012476 | 0.031441 | -0.0039905 | -0.04525 | -0.013123 | 0.0068381 | -0.016129 | -0.0043815 | 2.491 | 0.028777 | -0.013733 | 0.018311 | 0.054932 | 0.082397 | -0.009155 | 0.032043 | -0.041199 | -0.032043 | 0.068665 | -0.082397 | -0.082397 | -0.050354 | 0.07782 | 0.013733 | 9.201 | 9.1278 | -112.1704 | 9.1873 | 9.2514 | 0.1236 | -112.175 | 9.2468 | 9.1827 | -112.2437 | 9.137 | 9.0866 | -0.09613 | -112.2116 | 9.1599 | 9.1553 | 9.2239 | -112.2025 | 9.0866 | 9.1187 | 9.2377 | -112.1475
3615.4531 | 121.4218 | -9.9976 | 111.3419 | -0.020218 | 0.012773 | 0.015199 | -3.4178e-05 | 0.031868 | 0.00049567 | -0.045036 | -0.0054932 | 0.010683 | -0.015915 | -0.0026725 | 2.45 | 0.026214 | 0.041199 | 0.073242 | 0.11444 | 0.10529 | -0.013733 | 0.064087 | -0.050354 | 0.041199 | 0.086975 | -0.027466 | -0.073242 | -0.041199 | 0.082397 | 0.027466 | 10.0616 | 9.9472 | -111.3556 | 10.0708 | 10.1028 | 0.15564 | -111.3007 | 10.08 | 10.025 | -111.4151 | 10.0388 | 9.9701 | -0.054932 | -111.3831 | 9.9838 | 10.0388 | 10.112 | -111.3922 | 9.9243 | 9.9564 | 10.0845 | -111.3144
3617.2344 | 121.3348 | -11.4532 | 109.8404 | -0.012589 | 0.017686 | 0.016054 | 0.0018884 | 0.030586 | 0.0045545 | -0.041832 | -0.013123 | 0.011965 | -0.01506 | 0.0013863 | 2.4996 | 0.023437 | 0.022888 | 0.009155 | 0.032043 | 0.086975 | 0.045776 | 0.027466 | -0.086975 | 0.004578 | 0.07782 | -0.09613 | -0.036621 | -0.018311 | 0.068665 | 0 | 11.4807 | 11.3663 | -109.7946 | 11.4624 | 11.5402 | 0.17395 | -109.8175 | 11.5219 | 11.4532 | -109.877 | 11.4578 | 11.3571 | -0.09613 | -109.8587 | 11.499 | 11.4761 | 11.4853 | -109.9274 | 11.4166 | 11.4349 | 11.5311 | -109.8404
3619.0156 | 121.4401 | -12.9227 | 108.2153 | -0.012589 | 0.015122 | 0.016695 | -0.00024778 | 0.031014 | 0.0028455 | -0.043113 | -0.013123 | 0.010897 | -0.015274 | -0.00010889 | 2.4752 | 0.027923 | -0.027466 | -0.045776 | -0.022888 | 0.045776 | 0.022888 | 0.036621 | -0.091553 | -0.032043 | 0.009155 | -0.11444 | -0.050354 | -0.022888 | 0.059509 | 0.022888 | 12.9593 | 12.8311 | -108.1924 | 12.8769 | 12.9684 | 0.13733 | -108.2428 | 12.9822 | 12.9456 | -108.2657 | 12.8906 | 12.8082 | -0.13733 | -108.2382 | 12.9456 | 12.8952 | 12.8998 | -108.3069 | 12.8723 | 12.8998 | 12.9318 | -108.1924
3620.7344 | 121.3211 | -13.8519 | 107.3135 | -0.0049592 | 0.013627 | 0.016054 | 0.0035974 | 0.031868 | 0.0036999 | -0.045036 | -0.013123 | 0.013247 | -0.015488 | 0.00095911 | 2.4699 | 0.02835 | -0.032043 | -0.068665 | -0.022888 | 0.032043 | 0.036621 | 0.022888 | -0.10071 | -0.068665 | -0.013733 | -0.13733 | -0.009155 | 0 | 0.059509 | -0.009155 | 13.8748 | 13.7512 | -107.2769 | 13.7833 | 13.884 | 0.13275 | -107.3456 | 13.9114 | 13.8428 | -107.3227 | 13.7833 | 13.7146 | -0.12817 | -107.3135 | 13.8886 | 13.8199 | 13.829 | -107.4142 | 13.8428 | 13.8519 | 13.8382 | -107.3227
3622.5156 | 121.3211 | -16.246 | 104.7775 | -0.012589 | 0.012559 | 0.019045 | 0.0023156 | 0.032723 | -0.0042041 | -0.044395 | -0.013123 | 0.0087607 | -0.015701 | -0.0028861 | 2.5231 | 0.02835 | 0.027466 | 0.091553 | 0.10986 | 0.13275 | 0.004578 | 0.041199 | -0.050354 | 0.022888 | 0.17395 | 0.013733 | -0.068665 | -0.045776 | 0.09613 | 0.036621 | 16.2872 | 16.1957 | -104.7729 | 16.3376 | 16.3788 | 0.18311 | -104.7501 | 16.3422 | 16.2827 | -104.8462 | 16.2689 | 16.2598 | -0.022888 | -104.8233 | 16.2506 | 16.2735 | 16.3559 | -104.8279 | 16.1774 | 16.2003 | 16.42 | -104.7409
3624.3125 | 121.2479 | -11.499 | 109.7351 | -0.012589 | 0.014909 | 0.01819 | 0.0023156 | 0.034859 | -0.00035893 | -0.047813 | -0.020752 | 0.011324 | -0.01506 | -0.00074989 | 2.4278 | 0.027495 | 0 | 0.032043 | 0.050354 | 0.091553 | 0.022888 | 0.013733 | -0.07782 | -0.064087 | 0.045776 | -0.10986 | -0.018311 | -0.018311 | 0.045776 | -0.004578 | 11.5128 | 11.4212 | -109.7122 | 11.5311 | 11.5906 | 0.16937 | -109.7351 | 11.5448 | 11.4944 | -109.7534 | 11.4349 | 11.3892 | -0.10529 | -109.7534 | 11.5219 | 11.499 | 11.5494 | -109.8129 | 11.4807 | 11.4807 | 11.5448 | -109.7397
3626.0312 | 121.3989 | -9.3704 | 111.795 | -0.012589 | 0.011918 | 0.017976 | 0.0014612 | 0.031868 | -0.0052721 | -0.045677 | -0.013123 | 0.0079063 | -0.014633 | -0.0013907 | 2.4692 | 0.024932 | -0.027466 | 0.009155 | 0.050354 | 0.082397 | 0.009155 | 0.045776 | -0.050354 | -0.032043 | 0.073242 | -0.059509 | -0.054932 | -0.041199 | 0.091553 | 0.032043 | 9.4162 | 9.3201 | -111.7859 | 9.3796 | 9.4528 | 0.13275 | -111.8225 | 9.462 | 9.4025 | -111.85 | 9.3384 | 9.3109 | -0.091552 | -111.8362 | 9.3796 | 9.343 | 9.4208 | -111.8454 | 9.3155 | 9.3292 | 9.4437 | -111.763
3627.8125 | 121.1929 | -15.6143 | 105.4871 | -0.0049592 | 0.014695 | 0.01819 | 0.0029566 | 0.033791 | 6.8274e-05 | -0.045891 | -0.013123 | 0.011965 | -0.017838 | -0.0011771 | 2.447 | 0.025573 | -0.004578 | 0 | 0.022888 | 0.073242 | 0.022888 | 0.045776 | -0.082397 | -0.068665 | 0.027466 | -0.10986 | -0.009155 | -0.013733 | 0.045776 | 0.009155 | 15.6601 | 15.5319 | -105.4642 | 15.6143 | 15.6876 | 0.15564 | -105.4916 | 15.6601 | 15.6235 | -105.4962 | 15.5457 | 15.5045 | -0.11902 | -105.5008 | 15.6372 | 15.6097 | 15.6372 | -105.5695 | 15.6052 | 15.6006 | 15.6418 | -105.4779
3629.5938 | 121.051 | -17.514 | 103.3997 | -0.012589 | 0.016404 | 0.016481 | 0.002102 | 0.031868 | 0.0047681 | -0.04055 | -0.013123 | 0.013888 | -0.01506 | -0.0011771 | 2.446 | 0.024718 | 0.004578 | -0.013733 | 0.004578 | 0.068665 | 0.027466 | 0.027466 | -0.086975 | -0.027466 | 0.018311 | -0.15106 | -0.032043 | 0.013733 | 0.036621 | -0.004578 | 17.5415 | 17.4271 | -103.3722 | 17.5003 | 17.5827 | 0.15564 | -103.3951 | 17.5507 | 17.5095 | -103.4317 | 17.4866 | 17.363 | -0.14648 | -103.3859 | 17.5415 | 17.5186 | 17.5186 | -103.4866 | 17.482 | 17.5278 | 17.5323 | -103.4042
3631.375 | 121.0098 | -23.6252 | 97.2107 | -0.020218 | 0.018968 | 0.015627 | 0.0050928 | 0.032295 | 0.0011365 | -0.04525 | -0.0054932 | 0.012392 | -0.012711 | -0.00032249 | 2.424 | 0.025573 | -0.041199 | -0.041199 | -0.004578 | 0.041199 | 0.068665 | 0.041199 | -0.091553 | -0.045776 | 0.036621 | -0.1236 | 0 | 0.004578 | 0.086975 | 0 | 23.6664 | 23.5336 | -97.142 | 23.584 | 23.6664 | 0.13275 | -97.2519 | 23.7122 | 23.6252 | -97.2107 | 23.5794 | 23.5016 | -0.1236 | -97.2061 | 23.6938 | 23.584 | 23.6206 | -97.3022 | 23.6252 | 23.6298 | 23.6618 | -97.2107
3633.1094 | 120.9549 | -21.7667 | 99.0555 | -0.020218 | 0.014054 | 0.015199 | 0.00017942 | 0.02845 | 0.0056225 | -0.042045 | -0.020752 | 0.014315 | -0.015701 | 0.0037363 | 2.5265 | 0.024932 | -0.022888 | -0.068665 | -0.045776 | 0.050354 | 0.032043 | 0.050354 | -0.064087 | -0.068665 | 0.009155 | -0.16022 | -0.018311 | 0.018311 | 0.050354 | -0.004578 | 21.817 | 21.7026 | -99.0234 | 21.698 | 21.817 | 0.11444 | -99.0784 | 21.817 | 21.7621 | -99.0738 | 21.698 | 21.6064 | -0.15564 | -99.0372 | 21.7987 | 21.7438 | 21.7209 | -99.1196 | 21.7484 | 21.785 | 21.7758 | -99.0601
3634.8906 | 120.9366 | -23.1583 | 97.5128 | -0.020218 | 0.012132 | 0.02054 | 0.0016748 | 0.031014 | -0.0063403 | -0.045463 | -0.013123 | 0.0094015 | -0.021255 | -0.00096349 | 2.5177 | 0.025146 | 0.073242 | 0.10529 | 0.14191 | 0.13733 | 0.013733 | 0.086975 | -0.022888 | 0.050354 | 0.19226 | 0.022888 | -0.059509 | -0.018311 | 0.10986 | 0.022888 | 23.2452 | 23.1354 | -97.4991 | 23.2635 | 23.2956 | 0.16022 | -97.4396 | 23.2681 | 23.1812 | -97.5723 | 23.2086 | 23.1812 | 0 | -97.5311 | 23.172 | 23.2315 | 23.3002 | -97.5357 | 23.0988 | 23.14 | 23.3505 | -97.4899
3636.6719 | 120.7535 | -22.2839 | 98.2361 | -0.0049592 | 0.013413 | 0.017549 | 0.0033838 | 0.033364 | -0.0039905 | -0.045891 | -0.0054932 | 0.012179 | -0.020401 | 0.0041635 | 2.5192 | 0.024077 | 0.068665 | 0.09613 | 0.13275 | 0.15106 | 0.032043 | 0.091553 | -0.022888 | 0.036621 | 0.1831 | 0.018311 | -0.050354 | -0.041199 | 0.082397 | 0.045776 | 22.3755 | 22.261 | -98.204 | 22.3801 | 22.435 | 0.17395 | -98.1674 | 22.3663 | 22.3297 | -98.2864 | 22.3206 | 22.3022 | -0.027465 | -98.2773 | 22.316 | 22.3526 | 22.4167 | -98.259 | 22.2336 | 22.2427 | 22.467 | -98.1903
3638.375 | 120.7443 | -20.7825 | 99.678 | -0.012589 | 0.012345 | 0.019899 | 0.0027428 | 0.030586 | -0.0022815 | -0.046745 | -0.013123 | 0.013033 | -0.01976 | 0.0013863 | 2.4626 | 0.022368 | 0.082397 | 0.11902 | 0.13275 | 0.13275 | 0.018311 | 0.073242 | -0.027466 | 0.050354 | 0.19226 | 0.018311 | -0.050354 | -0.041199 | 0.091553 | 0.022888 | 20.8557 | 20.755 | -99.6597 | 20.9015 | 20.9152 | 0.16022 | -99.5956 | 20.874 | 20.8054 | -99.7284 | 20.8328 | 20.8008 | -0.004577 | -99.7192 | 20.8008 | 20.8649 | 20.9152 | -99.7055 | 20.7321 | 20.7413 | 20.9747 | -99.6552
3640.1562 | 120.5658 | -24.559 | 95.9427 | -0.012589 | 0.015122 | 0.015627 | 0.00060662 | 0.031655 | 0.0083997 | -0.044609 | -0.0054932 | 0.020083 | -0.021255 | 0.0062997 | 2.491 | 0.020232 | 0.045776 | 0.036621 | 0.054932 | 0.09613 | 0.036621 | 0.045776 | -0.045776 | 0.013733 | 0.064087 | -0.12817 | -0.041199 | -0.013733 | 0.059509 | -0.009155 | 24.6048 | 24.5132 | -95.9061 | 24.5956 | 24.6552 | 0.14191 | -95.8969 | 24.6185 | 24.5499 | -95.9839 | 24.5728 | 24.4308 | -0.11902 | -95.9564 | 24.5956 | 24.6048 | 24.614 | -95.9885 | 24.5178 | 24.5453 | 24.6231 | -95.9518
3641.9375 | 120.4056 | -21.048 | 99.1974 | -0.020218 | 0.011064 | 0.014131 | 0.00017942 | 0.031014 | -0.00035893 | -0.043541 | -0.0054932 | 0.014101 | -0.020187 | 0.0043771 | 2.559 | 0.02365 | 0.059509 | 0.09613 | 0.1236 | 0.14648 | 0.009155 | 0.091553 | -0.036621 | 0.041199 | 0.1236 | -0.032043 | -0.059509 | -0.022888 | 0.073242 | 0.013733 | 21.1395 | 21.0114 | -99.1882 | 21.1441 | 21.1945 | 0.18311 | -99.1379 | 21.1212 | 21.0617 | -99.2569 | 21.0892 | 21.0159 | -0.045776 | -99.2203 | 21.0571 | 21.1075 | 21.1716 | -99.234 | 20.9885 | 21.0251 | 21.1716 | -99.1837
3643.7188 | 120.0119 | -24.4171 | 95.5307 | -0.012589 | 0.014054 | 0.016695 | -0.00046138 | 0.031014 | 0.0036999 | -0.043113 | -0.020752 | 0.020296 | -0.024033 | 0.0058725 | 2.5299 | 0.021087 | 0.018311 | 0.036621 | 0.032043 | 0.11444 | 0.068665 | 0.059509 | -0.059509 | 0.009155 | 0.07782 | -0.11902 | -0.022888 | 0 | 0.068665 | -0.004578 | 24.4766 | 24.3576 | -95.462 | 24.4537 | 24.5316 | 0.17395 | -95.5124 | 24.4858 | 24.4125 | -95.5536 | 24.4263 | 24.2981 | -0.11444 | -95.5307 | 24.4858 | 24.4354 | 24.4492 | -95.5902 | 24.3942 | 24.4171 | 24.4949 | -95.5353
3645.5 | 121.0602 | -0.11444 | 120.8954 | -0.0049592 | 0.0089273 | 0.016267 | -0.0019568 | 0.029305 | 0.00028207 | -0.043968 | -0.013123 | 0.0068381 | -0.015701 | -0.00074989 | 2.516 | 0.026214 | 0.041199 | 0.073242 | 0.10529 | 0.10986 | -0.045776 | 0.050354 | -0.041199 | 0.027466 | 0.12817 | -0.027466 | -0.091553 | -0.064087 | 0.082397 | 0.022888 | 0.16479 | 0.073242 | -120.9412 | 0.18768 | 0.2243 | 0.15106 | -120.8542 | 0.19684 | 0.13733 | -120.9869 | 0.14191 | 0.086975 | -0.050354 | -120.9595 | 0.068665 | 0.15564 | 0.21973 | -120.9366 | 0.022888 | 0.050354 | 0.24262 | -120.8725
3647.2188 | 121.0693 | -0.15106 | 121.0602 | -0.020218 | 0.013841 | 0.016481 | 0.0050928 | 0.032723 | 0.00028207 | -0.045463 | -0.0054932 | 0.0085471 | -0.013992 | 0.0020273 | 2.5051 | 0.025146 | -0.073242 | -0.050354 | -0.027466 | 0.022888 | 0.027466 | 0.009155 | -0.10986 | -0.091553 | 0.018311 | -0.14191 | -0.013733 | -0.022888 | 0.027466 | -0.022888 | 0.16022 | 0.041199 | -121.0327 | 0.10071 | 0.17395 | 0.13275 | -121.1334 | 0.17853 | 0.12817 | -121.0739 | 0.059509 | 0.009155 | -0.11902 | -121.0831 | 0.17853 | 0.07782 | 0.1236 | -121.17 | 0.13733 | 0.12817 | 0.16937 | -121.0831
3649 | 121.2753 | -0.11902 | 121.0373 | -0.012589 | 0.011704 | 0.017763 | 0.0033838 | 0.030586 | -0.0044177 | -0.046959 | 0.0021363 | 0.0061973 | -0.013565 | -0.0011771 | 2.4853 | 0.027282 | -0.013733 | 0.022888 | 0.068665 | 0.07782 | -0.018311 | 0.041199 | -0.050354 | -0.004578 | 0.11444 | -0.018311 | -0.064087 | -0.045776 | 0.07782 | 0 | 0.16022 | 0.068665 | -121.0556 | 0.14191 | 0.19684 | 0.12817 | -121.051 | 0.19684 | 0.11902 | -121.1014 | 0.11444 | 0.10071 | -0.018311 | -121.0831 | 0.10071 | 0.10529 | 0.18768 | -121.0876 | 0.054932 | 0.073243 | 0.23346 | -121.0373
3650.7812 | 121.257 | -0.12817 | 121.1105 | -0.012589 | 0.013413 | 0.019685 | 0.001034 | 0.031227 | -0.0022815 | -0.04525 | -0.013123 | 0.0081199 | -0.016556 | -0.00096349 | 2.5545 | 0.024932 | 0.045776 | 0.082397 | 0.10529 | 0.10529 | -0.013733 | 0.045776 | -0.073242 | 0.027466 | 0.16022 | -0.013733 | -0.07782 | -0.050354 | 0.082397 | 0.013733 | 0.17395 | 0.054932 | -121.1243 | 0.21057 | 0.23346 | 0.17853 | -121.0648 | 0.21057 | 0.14191 | -121.1884 | 0.15564 | 0.11444 | -0.027466 | -121.1609 | 0.11444 | 0.17395 | 0.23346 | -121.1838 | 0.050354 | 0.07782 | 0.28839 | -121.0968
3652.5625 | 121.2112 | -0.14648 | 121.138 | -0.020218 | 0.013413 | 0.016054 | -3.4178e-05 | 0.032295 | -0.0014269 | -0.044609 | -0.0054932 | 0.0098289 | -0.015488 | -0.00074989 | 2.4756 | 0.024077 | 0.041199 | 0.064087 | 0.068665 | 0.10071 | -0.022888 | 0.050354 | -0.068665 | -0.022888 | 0.10071 | -0.059509 | -0.068665 | -0.041199 | 0.073242 | -0.018311 | 0.19684 | 0.077819 | -121.1609 | 0.21057 | 0.24719 | 0.16937 | -121.0968 | 0.21973 | 0.12817 | -121.2067 | 0.1236 | 0.086975 | -0.041198 | -121.1792 | 0.1236 | 0.18768 | 0.21515 | -121.2067 | 0.077819 | 0.10529 | 0.24719 | -121.1563
3654.3438 | 121.3165 | -0.11902 | 121.1609 | -0.0049592 | 0.01085 | 0.016481 | 0.00082022 | 0.031014 | -0.00014533 | -0.045677 | -0.013123 | 0.0070517 | -0.013565 | -0.0018179 | 2.5329 | 0.026 | 0.054932 | 0.082397 | 0.11902 | 0.12817 | -0.004578 | 0.041199 | -0.073242 | 0.036621 | 0.14648 | -0.013733 | -0.086975 | -0.045776 | 0.082397 | 0.022888 | 0.16022 | 0.045777 | -121.1655 | 0.20142 | 0.24719 | 0.20142 | -121.106 | 0.20142 | 0.14191 | -121.2479 | 0.15564 | 0.10529 | -0.036621 | -121.2067 | 0.11444 | 0.17395 | 0.23804 | -121.2341 | 0.032044 | 0.073243 | 0.2655 | -121.138
3656.0781 | 121.3394 | -0.1236 | 121.1838 | -0.020218 | 0.01555 | 0.018404 | 0.00039302 | 0.032936 | -0.00035893 | -0.045036 | -0.013123 | 0.0083335 | -0.015915 | -0.00074989 | 2.5137 | 0.026 | 0.054932 | 0.09613 | 0.10986 | 0.1236 | -0.009155 | 0.041199 | -0.068665 | 0.022888 | 0.14648 | -0.022888 | -0.064087 | -0.045776 | 0.082397 | 0.032043 | 0.16479 | 0.054931 | -121.1929 | 0.21973 | 0.24719 | 0.19226 | -121.1288 | 0.20599 | 0.15564 | -121.2479 | 0.14648 | 0.10071 | -0.054931 | -121.2296 | 0.11444 | 0.17853 | 0.23346 | -121.2524 | 0.059509 | 0.07782 | 0.27008 | -121.1517
3657.875 | 121.3715 | -0.1236 | 121.1838 | -0.012589 | 0.013627 | 0.017549 | -0.00088858 | 0.029518 | 0.0017773 | -0.044182 | -0.013123 | 0.0074789 | -0.016342 | 0.00031831 | 2.4586 | 0.024932 | 0.064087 | 0.054932 | 0.086975 | 0.10071 | -0.022888 | 0.036621 | -0.054932 | 0.013733 | 0.082397 | -0.050354 | -0.073242 | -0.045776 | 0.07782 | 0.009155 | 0.16022 | 0.068664 | -121.2067 | 0.17853 | 0.2243 | 0.15564 | -121.1197 | 0.20142 | 0.13275 | -121.257 | 0.13733 | 0.073242 | -0.059509 | -121.2296 | 0.10071 | 0.18768 | 0.21057 | -121.2387 | 0.050354 | 0.07782 | 0.20599 | -121.1746
3659.5938 | 121.4355 | -0.10986 | 121.2112 | -0.0049592 | 0.012986 | 0.012636 | -0.002384 | 0.032936 | 0.0051953 | -0.043541 | -0.013123 | 0.010897 | -0.013992 | 0.0024545 | 2.5154 | 0.026 | -0.018311 | -0.064087 | -0.041199 | 0.027466 | 0.022888 | -0.004578 | -0.09613 | -0.027466 | -0.013733 | -0.12817 | -0.022888 | -0.032043 | 0.041199 | 0.009155 | 0.10529 | 0.013733 | -121.1884 | 0.045776 | 0.13733 | 0.1236 | -121.2296 | 0.15106 | 0.11902 | -121.2341 | 0.082397 | -0.018311 | -0.13733 | -121.2433 | 0.13275 | 0.091552 | 0.068664 | -121.3074 | 0.086975 | 0.07782 | 0.09613 | -121.2021
3661.3594 | 121.4264 | -0.10986 | 121.1838 | -0.0049592 | 0.011491 | 0.016908 | -0.002384 | 0.0308 | 0.00049567 | -0.043327 | -0.013123 | 0.0068381 | -0.016556 | -0.0011771 | 2.4701 | 0.026427 | 0.073242 | 0.073242 | 0.09613 | 0.11902 | -0.018311 | 0.073242 | -0.050354 | 0.054932 | 0.10986 | -0.013733 | -0.091553 | -0.064087 | 0.086975 | 0.018311 | 0.18311 | 0.059509 | -121.2021 | 0.18311 | 0.22888 | 0.16937 | -121.1105 | 0.19684 | 0.12817 | -121.2753 | 0.16479 | 0.09613 | -0.032044 | -121.2479 | 0.091552 | 0.18311 | 0.20599 | -121.2341 | 0.01831 | 0.045776 | 0.21973 | -121.1655
3663.1406 | 121.3348 | -0.17395 | 121.2524 | -0.0049592 | 0.016191 | 0.01584 | 0.00082022 | 0.033577 | 0.0041273 | -0.043113 | -0.0054932 | 0.0096151 | -0.013351 | -0.0016043 | 2.5147 | 0.027709 | -0.004578 | -0.036621 | -0.004578 | 0.054932 | 0.018311 | 0.009155 | -0.086975 | -0.036621 | 0.018311 | -0.14648 | -0.041199 | -0.032043 | 0.068665 | -0.027466 | 0.1831 | 0.086975 | -121.2341 | 0.13733 | 0.22888 | 0.14191 | -121.257 | 0.24261 | 0.14648 | -121.2936 | 0.13733 | 0.027466 | -0.11902 | -121.2845 | 0.19226 | 0.16937 | 0.16937 | -121.3394 | 0.13275 | 0.14191 | 0.19226 | -121.2799
3664.8594 | 121.3806 | -0.16937 | 121.2616 | -0.020218 | 0.013627 | 0.016908 | 0.0023156 | 0.03315 | 0.00070927 | -0.044395 | -0.013123 | 0.0079063 | -0.015488 | -0.00010889 | 2.5846 | 0.027495 | -0.059509 | -0.059509 | -0.032043 | 0.013733 | 0.036621 | 0 | -0.10529 | -0.086975 | -0.013733 | -0.15564 | -0.032043 | -0.022888 | 0.027466 | -0.013733 | 0.16937 | 0.064087 | -121.225 | 0.10986 | 0.18311 | 0.11902 | -121.3211 | 0.19684 | 0.15564 | -121.2936 | 0.082398 | 0.013733 | -0.14191 | -121.2845 | 0.20599 | 0.10986 | 0.13733 | -121.3669 | 0.13733 | 0.14649 | 0.15564 | -121.2753
3666.6406 | 121.463 | -0.10986 | 121.2616 | -0.012589 | 0.010423 | 0.016481 | 0.001034 | 0.032295 | -0.0048449 | -0.044609 | -0.020752 | 0.0061973 | -0.013138 | -0.0018179 | 2.5216 | 0.028136 | 0.022888 | 0.054932 | 0.054932 | 0.073242 | -0.013733 | 0.054932 | -0.064087 | -0.013733 | 0.07782 | -0.050354 | -0.073242 | -0.050354 | 0.073242 | 0.018311 | 0.16479 | 0.045776 | -121.2753 | 0.16479 | 0.18311 | 0.13733 | -121.2387 | 0.18311 | 0.12817 | -121.3348 | 0.09613 | 0.059509 | -0.068665 | -121.312 | 0.09613 | 0.13275 | 0.16479 | -121.3257 | 0.036621 | 0.059509 | 0.18768 | -121.2433
3668.4062 | 121.4401 | -0.14648 | 121.2799 | -0.012589 | 0.014268 | 0.017976 | 0.0025292 | 0.034004 | 0.0036999 | -0.042045 | -0.013123 | 0.011538 | -0.013565 | -0.0011771 | 2.5526 | 0.027495 | -0.032043 | -0.10986 | -0.054932 | 0.032043 | 0.004578 | 0.018311 | -0.10986 | -0.082397 | -0.041199 | -0.16479 | -0.027466 | -0.013733 | 0.054932 | -0.018311 | 0.16479 | 0.036621 | -121.2753 | 0.036621 | 0.17853 | 0.14191 | -121.3119 | 0.20142 | 0.12817 | -121.3074 | 0.064087 | -0.018311 | -0.14648 | -121.2936 | 0.15106 | 0.11444 | 0.091552 | -121.3898 | 0.11902 | 0.13275 | 0.10529 | -121.2982
3670.1875 | 121.4996 | -0.12817 | 121.2753 | -0.012589 | 0.012345 | 0.017763 | 0.0027428 | 0.029518 | -0.0024951 | -0.044182 | -0.013123 | 0.0081199 | -0.017838 | -0.0013907 | 2.4874 | 0.027282 | 0.054932 | 0.054932 | 0.10529 | 0.09613 | -0.013733 | 0.068665 | -0.050354 | 0.022888 | 0.10529 | -0.027466 | -0.07782 | -0.054932 | 0.068665 | 0.018311 | 0.19684 | 0.07782 | -121.2891 | 0.18311 | 0.2243 | 0.14648 | -121.2204 | 0.19684 | 0.14649 | -121.3531 | 0.15106 | 0.10071 | -0.045777 | -121.3303 | 0.11444 | 0.18311 | 0.23346 | -121.3257 | 0.050354 | 0.073242 | 0.23346 | -121.257
3671.9844 | 121.5408 | -0.10529 | 121.2982 | -0.0049592 | 0.015122 | 0.015413 | 0.002102 | 0.032082 | 0.0030591 | -0.043541 | -0.013123 | 0.0096151 | -0.01442 | -0.00053629 | 2.569 | 0.024932 | -0.036621 | -0.07782 | -0.027466 | 0.032043 | 0.018311 | 0.027466 | -0.10986 | -0.032043 | -0.009155 | -0.11444 | -0.050354 | -0.032043 | 0.059509 | -0.004578 | 0.13275 | -0.004577 | -121.2799 | 0.027466 | 0.13733 | 0.14191 | -121.3348 | 0.16479 | 0.10071 | -121.3486 | 0.073243 | -0.009155 | -0.10986 | -121.3303 | 0.1236 | 0.068665 | 0.07782 | -121.4081 | 0.054932 | 0.073243 | 0.096131 | -121.3028
3673.7031 | 121.4127 | -0.16022 | 121.3486 | -0.020218 | 0.015122 | 0.016054 | 0.00017942 | 0.032295 | 0.0051953 | -0.042686 | 0.0021363 | 0.010897 | -0.013992 | -0.00053629 | 2.5342 | 0.027282 | -0.004578 | 0 | 0.013733 | 0.054932 | 0.009155 | 0.013733 | -0.091553 | -0.032043 | 0.027466 | -0.1236 | -0.054932 | -0.041199 | 0.045776 | -0.013733 | 0.17395 | 0.068664 | -121.3394 | 0.16022 | 0.21515 | 0.14649 | -121.3531 | 0.20599 | 0.14648 | -121.4035 | 0.12817 | 0.036621 | -0.10986 | -121.3898 | 0.16937 | 0.15564 | 0.17395 | -121.4401 | 0.10528 | 0.11902 | 0.18768 | -121.3623
3675.4688 | 121.4813 | -0.14191 | 121.3669 | -0.012589 | 0.016831 | 0.015199 | 0.0053064 | 0.030373 | 0.0041273 | -0.045036 | 0.0021363 | 0.011538 | -0.012711 | -0.00074989 | 2.4942 | 0.026427 | -0.004578 | -0.013733 | 0.018311 | 0.073242 | 0.032043 | 0.004578 | -0.086975 | -0.027466 | 0.07782 | -0.10529 | -0.036621 | -0.013733 | 0.054932 | -0.009155 | 0.14649 | 0.054932 | -121.3348 | 0.12817 | 0.21515 | 0.16022 | -121.3715 | 0.19684 | 0.13275 | -121.4035 | 0.11444 | 0.036621 | -0.096131 | -121.3806 | 0.17395 | 0.13733 | 0.16022 | -121.4539 | 0.10529 | 0.12817 | 0.21973 | -121.376
3677.25 | 121.5958 | -0.09613 | 121.3303 | -0.012589 | 0.01555 | 0.015627 | -0.00046138 | 0.033577 | -0.00035893 | -0.042259 | -0.013123 | 0.0083335 | -0.017838 | -0.00032249 | 2.5013 | 0.027495 | 0.004578 | 0.004578 | 0.041199 | 0.082397 | -0.013733 | 0.036621 | -0.082397 | 0.009155 | 0.091553 | -0.041199 | -0.082397 | -0.041199 | 0.064087 | 0.045776 | 0.13275 | 0.013733 | -121.344 | 0.10071 | 0.17853 | 0.16479 | -121.3257 | 0.16022 | 0.14191 | -121.4127 | 0.10528 | 0.054931 | -0.086975 | -121.3715 | 0.082397 | 0.10071 | 0.13733 | -121.4127 | 0.013733 | 0.054931 | 0.18768 | -121.2845
3678.9688 | 121.582 | -0.10986 | 121.3165 | -0.0049592 | 0.014268 | 0.017549 | -0.00088858 | 0.032082 | -0.0016405 | -0.042045 | -0.028381 | 0.0059837 | -0.016983 | -0.0028861 | 2.5141 | 0.02835 | 0.032043 | 0.041199 | 0.091553 | 0.11444 | -0.013733 | 0.054932 | -0.045776 | 0.032043 | 0.11444 | -0.027466 | -0.091553 | -0.064087 | 0.086975 | 0.022888 | 0.16479 | 0.064087 | -121.3303 | 0.15106 | 0.2243 | 0.16022 | -121.2845 | 0.19684 | 0.13275 | -121.4081 | 0.14191 | 0.082397 | -0.050354 | -121.3806 | 0.09613 | 0.14191 | 0.20142 | -121.3623 | 0.01831 | 0.045776 | 0.2243 | -121.2936
3680.75 | 121.5866 | -0.13733 | 121.3531 | -0.012589 | 0.014268 | 0.01584 | 0.0033838 | 0.0308 | -0.0022815 | -0.044822 | -0.013123 | 0.0081199 | -0.013351 | -0.0011771 | 2.5261 | 0.026641 | 0.027466 | 0.050354 | 0.091553 | 0.09613 | -0.022888 | 0.045776 | -0.054932 | -0.004578 | 0.09613 | -0.032043 | -0.068665 | -0.036621 | 0.07782 | 0.004578 | 0.18311 | 0.082397 | -121.376 | 0.18768 | 0.23346 | 0.15106 | -121.3257 | 0.21515 | 0.14191 | -121.4218 | 0.13275 | 0.10529 | -0.036621 | -121.3898 | 0.11444 | 0.16479 | 0.22888 | -121.4081 | 0.068664 | 0.10071 | 0.23346 | -121.3486
3682.5312 | 121.6141 | -0.10529 | 121.3577 | -0.012589 | 0.017472 | 0.015627 | 0.0031702 | 0.029518 | -0.0012133 | -0.043754 | -0.013123 | 0.0070517 | -0.011856 | -0.0033133 | 2.5041 | 0.024718 | 0.050354 | 0.064087 | 0.09613 | 0.1236 | -0.013733 | 0.064087 | -0.050354 | 0.041199 | 0.10529 | -0.022888 | -0.082397 | -0.068665 | 0.068665 | 0.018311 | 0.16937 | 0.054932 | -121.3715 | 0.16937 | 0.22888 | 0.17395 | -121.3074 | 0.17395 | 0.1236 | -121.4401 | 0.14649 | 0.082398 | -0.041199 | -121.4264 | 0.091553 | 0.15564 | 0.20142 | -121.4081 | 0.022889 | 0.036621 | 0.21057 | -121.3394
3684.25 | 121.6003 | -0.13733 | 121.3623 | -0.0049592 | 0.010209 | 0.014772 | 0.00060662 | 0.031014 | 0.00028207 | -0.045463 | -0.020752 | 0.0079063 | -0.016769 | -0.0035269 | 2.4517 | 0.026 | 0.054932 | 0.064087 | 0.09613 | 0.10529 | -0.022888 | 0.054932 | -0.054932 | 0.022888 | 0.11902 | -0.032043 | -0.073242 | -0.054932 | 0.086975 | 0.022888 | 0.19226 | 0.082397 | -121.3852 | 0.20142 | 0.24262 | 0.16022 | -121.3074 | 0.2243 | 0.16022 | -121.4355 | 0.16022 | 0.10529 | -0.054931 | -121.4172 | 0.11444 | 0.19226 | 0.23346 | -121.4172 | 0.064087 | 0.082397 | 0.25635 | -121.3394
3686.0156 | 121.5912 | -0.14191 | 121.3989 | -0.012589 | 0.010209 | 0.017549 | 0.0023156 | 0.030373 | -0.00099973 | -0.043541 | -0.013123 | 0.0059837 | -0.01506 | 0.00031831 | 2.5105 | 0.026 | 0.045776 | 0.041199 | 0.091553 | 0.09613 | -0.032043 | 0.073242 | -0.073242 | 0.004578 | 0.07782 | -0.045776 | -0.073242 | -0.045776 | 0.07782 | 0.018311 | 0.21515 | 0.068665 | -121.431 | 0.18311 | 0.23804 | 0.16937 | -121.3531 | 0.21973 | 0.16022 | -121.4722 | 0.14649 | 0.096131 | -0.064087 | -121.4447 | 0.10986 | 0.18768 | 0.23346 | -121.4722 | 0.068665 | 0.096131 | 0.21973 | -121.3806
3687.7969 | 121.5179 | -0.17853 | 121.4172 | -0.012589 | 0.015122 | 0.015413 | 0.001034 | 0.031441 | 0.0069043 | -0.043327 | -0.013123 | 0.011751 | -0.015274 | 0.00095911 | 2.5728 | 0.024077 | -0.018311 | -0.059509 | -0.022888 | 0.041199 | 0.009155 | 0.022888 | -0.091553 | -0.073242 | -0.032043 | -0.17395 | -0.032043 | -0.027466 | 0.036621 | -0.013733 | 0.20142 | 0.086975 | -121.4081 | 0.11902 | 0.21973 | 0.13275 | -121.4355 | 0.21515 | 0.16479 | -121.4493 | 0.10529 | 0.004578 | -0.16022 | -121.4447 | 0.18768 | 0.16022 | 0.15564 | -121.5088 | 0.14648 | 0.15106 | 0.14648 | -121.431
3689.5 | 121.6507 | -0.10986 | 121.376 | -0.0049592 | 0.010209 | 0.018617 | 0.001034 | 0.029946 | -0.0054859 | -0.045463 | -0.013123 | 0.0066245 | -0.015274 | -0.00096349 | 2.4985 | 0.026855 | -0.022888 | -0.009155 | 0.032043 | 0.059509 | 0.004578 | 0.050354 | -0.064087 | -0.041199 | 0.068665 | -0.064087 | -0.054932 | -0.036621 | 0.068665 | 0 | 0.16022 | 0.045776 | -121.3715 | 0.10071 | 0.16937 | 0.1236 | -121.3989 | 0.17853 | 0.10986 | -121.431 | 0.068664 | 0.045776 | -0.064087 | -121.4127 | 0.11444 | 0.086975 | 0.14191 | -121.4401 | 0.054931 | 0.073242 | 0.17853 | -121.376
3691.2812 | 121.5546 | -0.15564 | 121.4401 | -0.020218 | 0.019181 | 0.011995 | 0.003811 | 0.031441 | 0.0030591 | -0.044182 | -0.013123 | 0.012179 | -0.012711 | -0.0011771 | 2.5128 | 0.023864 | 0.009155 | 0 | 0.013733 | 0.07782 | 0.004578 | 0.018311 | -0.082397 | -0.022888 | 0.032043 | -0.13733 | -0.027466 | -0.027466 | 0.050354 | -0.022888 | 0.17395 | 0.073243 | -121.4355 | 0.15564 | 0.23346 | 0.16022 | -121.431 | 0.20599 | 0.13275 | -121.4676 | 0.13275 | 0.018311 | -0.11444 | -121.4676 | 0.16022 | 0.16479 | 0.16937 | -121.5225 | 0.12817 | 0.12817 | 0.18768 | -121.463
3693.0469 | 121.5225 | -0.17853 | 121.4539 | -0.020218 | 0.016404 | 0.016481 | 0.0018884 | 0.032295 | 0.0041273 | -0.041404 | -0.013123 | 0.0096151 | -0.01442 | 0.0018137 | 2.4648 | 0.024718 | -0.009155 | -0.032043 | -0.004578 | 0.045776 | 0.013733 | 0.009155 | -0.09613 | -0.064087 | 0.018311 | -0.15564 | -0.045776 | -0.018311 | 0.041199 | -0.027466 | 0.18768 | 0.082398 | -121.4401 | 0.14648 | 0.2243 | 0.14191 | -121.463 | 0.21973 | 0.15106 | -121.4996 | 0.11444 | 0.022888 | -0.12817 | -121.4722 | 0.19226 | 0.16937 | 0.17395 | -121.55 | 0.13275 | 0.16022 | 0.19684 | -121.4813
3694.8281 | 121.5775 | -0.17395 | 121.4905 | -0.012589 | 0.013841 | 0.016054 | 0.003811 | 0.031655 | -0.0056995 | -0.043754 | -0.020752 | 0.0070517 | -0.01442 | -0.00032249 | 2.5256 | 0.027068 | 0.009155 | 0.068665 | 0.082397 | 0.10529 | -0.018311 | 0.054932 | -0.073242 | -0.009155 | 0.11444 | -0.050354 | -0.064087 | -0.036621 | 0.064087 | 0.027466 | 0.22888 | 0.10071 | -121.5088 | 0.24261 | 0.27924 | 0.17853 | -121.4813 | 0.23804 | 0.20142 | -121.5546 | 0.16479 | 0.1236 | -0.07782 | -121.5271 | 0.15564 | 0.1831 | 0.25635 | -121.5637 | 0.10986 | 0.13733 | 0.28839 | -121.463
3696.5625 | 121.6278 | -0.15564 | 121.4813 | -0.012589 | 0.015763 | 0.016481 | 0.0035974 | 0.035286 | 0.0011365 | -0.045036 | -0.013123 | 0.0096151 | -0.013138 | -0.00074989 | 2.554 | 0.027068 | -0.059509 | -0.064087 | -0.050354 | 0.027466 | 0.036621 | 0 | -0.10529 | -0.091553 | -0.004578 | -0.14648 | -0.032043 | -0.004578 | 0.032043 | -0.004578 | 0.15564 | 0.050354 | -121.4447 | 0.091553 | 0.18311 | 0.13275 | -121.5408 | 0.18768 | 0.15106 | -121.5134 | 0.064087 | 0.009156 | -0.14191 | -121.4859 | 0.19226 | 0.096131 | 0.10529 | -121.5866 | 0.1236 | 0.15106 | 0.15106 | -121.4859
3698.3438 | 121.6782 | -0.13733 | 121.4447 | -0.012589 | 0.011277 | 0.015413 | -0.0017432 | 0.030159 | -0.0020679 | -0.044822 | -0.0054932 | 0.0066245 | -0.016983 | -0.00074989 | 2.434 | 0.024505 | 0.032043 | 0.064087 | 0.10071 | 0.10529 | -0.027466 | 0.054932 | -0.059509 | 0.018311 | 0.10529 | -0.013733 | -0.073242 | -0.059509 | 0.082397 | 0.018311 | 0.19226 | 0.07782 | -121.4722 | 0.20142 | 0.24262 | 0.16479 | -121.4127 | 0.21973 | 0.15564 | -121.5179 | 0.15564 | 0.1236 | -0.032044 | -121.5042 | 0.10986 | 0.16937 | 0.23804 | -121.5042 | 0.064087 | 0.07782 | 0.24262 | -121.4264
3700.125 | 121.6049 | -0.15564 | 121.4676 | -0.012589 | 0.016191 | 0.013063 | -3.4178e-05 | 0.032723 | 0.0051953 | -0.042686 | -0.013123 | 0.011324 | -0.014847 | 0.0016001 | 2.4801 | 0.025786 | -0.073242 | -0.09613 | -0.07782 | 0.022888 | 0.027466 | 0.013733 | -0.11444 | -0.07782 | -0.041199 | -0.17853 | -0.027466 | -0.004578 | 0.036621 | -0.013733 | 0.16937 | 0.041199 | -121.4401 | 0.05951 | 0.17853 | 0.13733 | -121.5408 | 0.19226 | 0.14191 | -121.4951 | 0.07782 | -0.022888 | -0.16479 | -121.4722 | 0.18311 | 0.082398 | 0.07782 | -121.582 | 0.12817 | 0.15106 | 0.11444 | -121.4813
3701.8438 | 121.7148 | -0.11902 | 121.4401 | -0.012589 | 0.013413 | 0.016054 | 0.00082022 | 0.031868 | 0.0019909 | -0.043968 | -0.013123 | 0.0089743 | -0.015274 | -0.00010889 | 2.5652 | 0.02835 | -0.027466 | -0.059509 | -0.027466 | 0.041199 | 0.027466 | 0.027466 | -0.086975 | -0.018311 | 0.032043 | -0.10071 | -0.068665 | -0.036621 | 0.064087 | 0.018311 | 0.14649 | 0.032044 | -121.4127 | 0.05951 | 0.16022 | 0.12817 | -121.4676 | 0.18311 | 0.13733 | -121.5088 | 0.10071 | 0.018311 | -0.11902 | -121.4767 | 0.14649 | 0.091553 | 0.091553 | -121.5271 | 0.050354 | 0.082398 | 0.15106 | -121.4218
3703.5469 | 121.6553 | -0.13733 | 121.4859 | -0.012589 | 0.014695 | 0.019472 | 0.00017942 | 0.031868 | 0.0015637 | -0.043754 | -0.0054932 | 0.01047 | -0.013565 | -0.00096349 | 2.5771 | 0.026 | -0.036621 | -0.059509 | -0.022888 | 0.059509 | 0.018311 | -0.004578 | -0.10071 | -0.054932 | 0.041199 | -0.1236 | -0.032043 | -0.027466 | 0.059509 | -0.027466 | 0.13275 | 0.036621 | -121.4676 | 0.07782 | 0.19684 | 0.16022 | -121.5225 | 0.19684 | 0.10986 | -121.5179 | 0.082397 | 0.013733 | -0.09613 | -121.5134 | 0.15564 | 0.10071 | 0.11444 | -121.5866 | 0.10529 | 0.10986 | 0.17853 | -121.5134
3705.3281 | 121.6507 | -0.15564 | 121.4859 | -0.012589 | 0.014268 | 0.015627 | 0.0029566 | 0.032509 | -0.00099973 | -0.045036 | -0.0054932 | 0.0096151 | -0.013779 | 0.00010471 | 2.5931 | 0.026641 | -0.045776 | -0.073242 | -0.036621 | 0.027466 | 0.022888 | -0.004578 | -0.11444 | -0.10986 | 0.004578 | -0.16022 | -0.022888 | 0.018311 | 0.027466 | -0.027466 | 0.15106 | 0.041199 | -121.463 | 0.082398 | 0.18311 | 0.14191 | -121.5317 | 0.18311 | 0.12817 | -121.5088 | 0.045777 | -0.004577 | -0.13275 | -121.4676 | 0.17853 | 0.10986 | 0.11902 | -121.6003 | 0.13275 | 0.17395 | 0.16022 | -121.5134
3707.0625 | 121.6232 | -0.15106 | 121.5179 | -0.012589 | 0.012773 | 0.014345 | 0.0014612 | 0.0308 | 0.0030591 | -0.043541 | -0.013123 | 0.011538 | -0.01442 | 0.0013863 | 2.6263 | 0.026641 | 0.018311 | -0.022888 | 0.018311 | 0.07782 | 0.013733 | 0.004578 | -0.082397 | -0.027466 | 0.036621 | -0.11444 | -0.036621 | -0.036621 | 0.059509 | -0.018311 | 0.15564 | 0.068665 | -121.5042 | 0.12817 | 0.22888 | 0.16022 | -121.4996 | 0.21057 | 0.13275 | -121.5546 | 0.1236 | 0.036621 | -0.09613 | -121.5546 | 0.16479 | 0.16937 | 0.16937 | -121.6003 | 0.11444 | 0.11444 | 0.18768 | -121.5363
3708.8594 | 121.7194 | -0.13733 | 121.5042 | 0.0026703 | 0.016618 | 0.017549 | 0.0023156 | 0.031655 | -0.0067675 | -0.045891 | -0.020752 | 0.0057699 | -0.013779 | -0.0016043 | 2.5184 | 0.02835 | 0.050354 | 0.07782 | 0.10071 | 0.11444 | -0.032043 | 0.027466 | -0.068665 | 0.018311 | 0.16022 | -0.009155 | -0.064087 | -0.041199 | 0.07782 | 0.018311 | 0.16479 | 0.068664 | -121.5363 | 0.21515 | 0.25177 | 0.18311 | -121.4539 | 0.21515 | 0.15564 | -121.5683 | 0.15564 | 0.12817 | -0.027466 | -121.5454 | 0.10529 | 0.18768 | 0.23804 | -121.5729 | 0.073242 | 0.09613 | 0.29755 | -121.4859
3710.5781 | 121.7514 | -0.14191 | 121.5042 | -0.0049592 | 0.014909 | 0.016267 | -0.00088858 | 0.029305 | 6.8274e-05 | -0.044822 | -0.0054932 | 0.01047 | -0.01442 | -0.00010889 | 2.4754 | 0.02835 | -0.027466 | -0.10529 | -0.041199 | 0.027466 | 0.036621 | 0.013733 | -0.10986 | -0.082397 | -0.018311 | -0.13733 | -0.027466 | -0.004578 | 0.045776 | -0.009155 | 0.15564 | 0.032044 | -121.4676 | 0.036621 | 0.16937 | 0.13733 | -121.5317 | 0.18768 | 0.13275 | -121.5317 | 0.05951 | 0.004578 | -0.12817 | -121.5088 | 0.17853 | 0.11444 | 0.10071 | -121.6141 | 0.11444 | 0.13733 | 0.1236 | -121.5134
3712.3438 | 121.7651 | -0.15564 | 121.4996 | -0.0049592 | 0.014054 | 0.017976 | 0.001034 | 0.034432 | 0.0013501 | -0.042045 | -0.013123 | 0.0096151 | -0.015274 | 0.0018137 | 2.5718 | 0.025573 | -0.018311 | -0.082397 | -0.027466 | 0.022888 | 0.009155 | 0.009155 | -0.086975 | -0.059509 | 0.009155 | -0.13275 | -0.050354 | -0.022888 | 0.041199 | 0.004578 | 0.16479 | 0.068665 | -121.4905 | 0.073243 | 0.17853 | 0.10986 | -121.5179 | 0.19684 | 0.16022 | -121.55 | 0.096131 | 0.022889 | -0.13733 | -121.5225 | 0.16479 | 0.13733 | 0.12817 | -121.5866 | 0.10529 | 0.13275 | 0.16479 | -121.4951
3714.125 | 121.669 | -0.16479 | 121.5363 | -0.012589 | 0.015122 | 0.016267 | 0.0035974 | 0.032082 | -0.0031359 | -0.043968 | -0.020752 | 0.0081199 | -0.01506 | -0.0011771 | 2.4628 | 0.02835 | 0.018311 | 0.018311 | 0.068665 | 0.091553 | -0.009155 | 0.027466 | -0.068665 | -0.054932 | 0.068665 | -0.082397 | -0.050354 | -0.018311 | 0.059509 | -0.009155 | 0.19226 | 0.09613 | -121.5454 | 0.18311 | 0.25635 | 0.16022 | -121.5179 | 0.2243 | 0.15564 | -121.5866 | 0.10986 | 0.082398 | -0.073242 | -121.5546 | 0.15564 | 0.18311 | 0.23346 | -121.6049 | 0.11444 | 0.14648 | 0.23346 | -121.5454
3715.9062 | 121.7056 | -0.14648 | 121.5683 | -0.020218 | 0.018113 | 0.011995 | 0.003811 | 0.031655 | 0.0058363 | -0.044182 | -0.0054932 | 0.012606 | -0.0086518 | 0.0020273 | 2.485 | 0.024932 | -0.009155 | -0.045776 | 0.004578 | 0.064087 | 0.022888 | -0.009155 | -0.09613 | -0.027466 | 0.050354 | -0.10071 | -0.045776 | 0.009155 | 0.036621 | -0.036621 | 0.13733 | 0.050354 | -121.5454 | 0.10071 | 0.21057 | 0.16022 | -121.5775 | 0.18311 | 0.10986 | -121.6141 | 0.11902 | 0.045776 | -0.064087 | -121.5591 | 0.16937 | 0.13733 | 0.15106 | -121.6644 | 0.10071 | 0.15564 | 0.19684 | -121.6049
3717.6719 | 121.7331 | -0.1236 | 121.5454 | -0.027847 | 0.012559 | 0.017122 | 0.0035974 | 0.031227 | -0.0048449 | -0.044395 | -0.020752 | 0.0053427 | -0.013779 | -0.0033133 | 2.4265 | 0.02835 | -0.009155 | 0.027466 | 0.064087 | 0.082397 | -0.022888 | 0.054932 | -0.064087 | -0.045776 | 0.064087 | -0.064087 | -0.073242 | -0.045776 | 0.059509 | 0.009155 | 0.17853 | 0.059509 | -121.5683 | 0.15106 | 0.20599 | 0.14648 | -121.5546 | 0.1831 | 0.13275 | -121.6187 | 0.07782 | 0.059509 | -0.073242 | -121.5912 | 0.10071 | 0.11444 | 0.18768 | -121.6095 | 0.050354 | 0.07782 | 0.18768 | -121.5363
3719.3906 | 121.8338 | -0.14191 | 121.5271 | -0.0049592 | 0.014909 | 0.016054 | 0.003811 | 0.031655 | -0.0046313 | -0.043968 | -0.0054932 | 0.0038473 | -0.011215 | -0.0022453 | 2.4917 | 0.027923 | -0.009155 | 0.018311 | 0.073242 | 0.09613 | 0 | 0.022888 | -0.07782 | 0.009155 | 0.11902 | -0.013733 | -0.064087 | -0.045776 | 0.073242 | 0.013733 | 0.16479 | 0.064087 | -121.5271 | 0.16022 | 0.23804 | 0.17395 | -121.5363 | 0.21515 | 0.15564 | -121.5912 | 0.15106 | 0.12817 | -0.027466 | -121.5729 | 0.14191 | 0.13275 | 0.21515 | -121.6049 | 0.07782 | 0.096131 | 0.26093 | -121.5134
3721.1719 | 121.6736 | -0.16022 | 121.5775 | -0.020218 | 0.016618 | 0.015413 | 0.00082022 | 0.031655 | 0.0056225 | -0.0429 | -0.013123 | 0.0098289 | -0.013779 | 0.0035227 | 2.4308 | 0.024077 | 0 | -0.036621 | -0.013733 | 0.041199 | 0.022888 | 0.018311 | -0.09613 | -0.036621 | 0.013733 | -0.15564 | -0.045776 | -0.022888 | 0.059509 | -0.009155 | 0.17853 | 0.064087 | -121.5546 | 0.1236 | 0.20142 | 0.13733 | -121.5775 | 0.21973 | 0.15106 | -121.6232 | 0.1236 | 0.004577 | -0.14649 | -121.6003 | 0.1831 | 0.16022 | 0.14648 | -121.6736 | 0.11444 | 0.13733 | 0.17395 | -121.5866
3722.9531 | 121.7331 | -0.16937 | 121.5958 | -0.0049592 | 0.017472 | 0.016908 | 0.0048792 | 0.031014 | 0.00092287 | -0.045463 | -0.013123 | 0.0089743 | -0.013138 | -0.0016043 | 2.4496 | 0.026214 | -0.064087 | -0.059509 | -0.032043 | 0.027466 | 0.022888 | -0.009155 | -0.11902 | -0.10071 | -0.004578 | -0.15564 | -0.022888 | -0.022888 | 0.022888 | -0.013733 | 0.16022 | 0.050354 | -121.5729 | 0.10986 | 0.19684 | 0.14649 | -121.6599 | 0.19226 | 0.15564 | -121.6187 | 0.068665 | 0.013733 | -0.14191 | -121.6187 | 0.19226 | 0.10529 | 0.13733 | -121.7148 | 0.14649 | 0.14649 | 0.16479 | -121.6095
3724.6719 | 121.7697 | -0.13733 | 121.5546 | -0.0049592 | 0.013627 | 0.016695 | 0.0035974 | 0.029946 | -0.0012133 | -0.043968 | 0.0021363 | 0.0079063 | -0.015274 | -0.00096349 | 2.4927 | 0.027068 | 0.045776 | 0.064087 | 0.10529 | 0.09613 | -0.018311 | 0.050354 | -0.050354 | 0.027466 | 0.10986 | -0.036621 | -0.07782 | -0.050354 | 0.064087 | 0.027466 | 0.18768 | 0.086975 | -121.5729 | 0.20142 | 0.23346 | 0.14648 | -121.5088 | 0.20142 | 0.16479 | -121.6324 | 0.16479 | 0.10071 | -0.064087 | -121.6049 | 0.11902 | 0.18311 | 0.24262 | -121.6049 | 0.059509 | 0.086975 | 0.24719 | -121.5271
3726.4375 | 121.6965 | -0.16937 | 121.6049 | 0.0026703 | 0.0179 | 0.014558 | 0.00039302 | 0.031014 | 0.0051953 | -0.043754 | -0.013123 | 0.012179 | -0.01442 | 0.0016001 | 2.5397 | 0.023864 | 0.032043 | -0.004578 | 0.013733 | 0.082397 | 0.018311 | 0.032043 | -0.082397 | -0.018311 | 0.050354 | -0.1236 | -0.050354 | -0.013733 | 0.050354 | -0.009155 | 0.20142 | 0.086976 | -121.5866 | 0.16479 | 0.25177 | 0.16479 | -121.5729 | 0.21973 | 0.16022 | -121.6553 | 0.15106 | 0.045777 | -0.11444 | -121.6187 | 0.18768 | 0.20142 | 0.18311 | -121.6873 | 0.11902 | 0.15564 | 0.21973 | -121.6141
3728.2188 | 121.6965 | -0.17853 | 121.5866 | -0.012589 | 0.015336 | 0.014772 | -0.00067498 | 0.031441 | 0.0034863 | -0.042686 | -0.0054932 | 0.013033 | -0.01442 | -0.0018179 | 2.5583 | 0.027282 | -0.054932 | -0.068665 | -0.054932 | 0.032043 | 0.022888 | 0.018311 | -0.10986 | -0.09613 | -0.032043 | -0.18768 | -0.036621 | -0.018311 | 0.009155 | -0.013733 | 0.19684 | 0.068665 | -121.5637 | 0.10986 | 0.21057 | 0.14191 | -121.6415 | 0.18768 | 0.16479 | -121.6232 | 0.082398 | -0.009155 | -0.17395 | -121.6049 | 0.20142 | 0.1236 | 0.1236 | -121.6965 | 0.14191 | 0.16022 | 0.14648 | -121.6003
3730 | 121.6873 | -0.19226 | 121.6003 | -0.020218 | 0.015763 | 0.015627 | -0.002384 | 0.030586 | 0.0034863 | -0.043327 | -0.013123 | 0.011751 | -0.01442 | 0.00074551 | 2.6094 | 0.026641 | -0.041199 | -0.036621 | -0.009155 | 0.032043 | 0.027466 | 0.013733 | -0.091553 | -0.064087 | 0 | -0.15106 | -0.050354 | -0.013733 | 0.054932 | -0.022888 | 0.20599 | 0.10071 | -121.5729 | 0.15564 | 0.2243 | 0.1236 | -121.6415 | 0.24719 | 0.16937 | -121.6507 | 0.12817 | 0.041199 | -0.12817 | -121.6141 | 0.21973 | 0.15106 | 0.18311 | -121.6919 | 0.14191 | 0.17853 | 0.19226 | -121.6232
3731.7344 | 121.7148 | -0.18768 | 121.6095 | -0.012589 | 0.016618 | 0.016267 | 0.0023156 | 0.029732 | 0.0015637 | -0.043327 | -0.0054932 | 0.010042 | -0.014847 | 0.00053191 | 2.5184 | 0.028777 | -0.009155 | -0.009155 | 0.013733 | 0.064087 | 0.022888 | 0.022888 | -0.086975 | -0.045776 | 0.027466 | -0.11902 | -0.054932 | -0.032043 | 0.064087 | -0.009155 | 0.21057 | 0.10071 | -121.5866 | 0.17853 | 0.25177 | 0.15106 | -121.6187 | 0.25177 | 0.17853 | -121.6644 | 0.14191 | 0.068664 | -0.10986 | -121.6415 | 0.21057 | 0.17853 | 0.20142 | -121.6965 | 0.13275 | 0.15564 | 0.21515 | -121.6187
3733.5 | 121.7789 | -0.16022 | 121.6049 | -0.0049592 | 0.014482 | 0.014772 | 0.00039302 | 0.031868 | 0.0019909 | -0.043968 | -0.013123 | 0.010256 | -0.012711 | 0.00074551 | 2.5573 | 0.028136 | -0.068665 | -0.10529 | -0.045776 | 0.032043 | 0.032043 | 0.013733 | -0.091553 | -0.10071 | -0.032043 | -0.16937 | -0.032043 | -0.018311 | 0.036621 | -0.013733 | 0.17395 | 0.068664 | -121.5729 | 0.054931 | 0.19226 | 0.1236 | -121.6736 | 0.19684 | 0.14648 | -121.637 | 0.059509 | -0.009156 | -0.15564 | -121.6232 | 0.19226 | 0.091552 | 0.11444 | -121.6965 | 0.12817 | 0.14191 | 0.12817 | -121.6187
3735.2812 | 121.756 | -0.1831 | 121.6141 | -0.020218 | 0.014054 | 0.015413 | 0.0048792 | 0.032082 | -0.0056995 | -0.043754 | -0.013123 | 0.0068381 | -0.01442 | -0.00096349 | 2.5 | 0.027923 | 0.004578 | 0.041199 | 0.09613 | 0.11902 | -0.009155 | 0.041199 | -0.07782 | -0.018311 | 0.1236 | -0.036621 | -0.059509 | -0.032043 | 0.073242 | -0.004578 | 0.2243 | 0.10528 | -121.6232 | 0.2243 | 0.30212 | 0.19684 | -121.6095 | 0.25635 | 0.17853 | -121.6736 | 0.16479 | 0.14648 | -0.032043 | -121.6461 | 0.17395 | 0.18768 | 0.27924 | -121.6919 | 0.1236 | 0.15106 | 0.3067 | -121.6187
3737.0156 | 121.7651 | -0.17853 | 121.6187 | 0.0026703 | 0.014695 | 0.013063 | -3.4178e-05 | 0.031227 | 0.0030591 | -0.042045 | -0.013123 | 0.011751 | -0.014206 | 0.0011727 | 2.5152 | 0.025573 | 0.018311 | -0.022888 | 0.009155 | 0.064087 | 0.018311 | 0.027466 | -0.086975 | -0.022888 | 0.054932 | -0.10071 | -0.045776 | -0.013733 | 0.045776 | -0.009155 | 0.20599 | 0.091553 | -121.6003 | 0.15564 | 0.24261 | 0.15106 | -121.6003 | 0.2243 | 0.16937 | -121.6644 | 0.15564 | 0.07782 | -0.091553 | -121.6324 | 0.19684 | 0.19684 | 0.18768 | -121.7056 | 0.13275 | 0.16479 | 0.23346 | -121.6278
3738.7969 | 121.7926 | -0.16022 | 121.6232 | -0.020218 | 0.015122 | 0.014345 | -0.0021704 | 0.031227 | 0.0028455 | -0.045036 | -0.020752 | 0.011751 | -0.01506 | 0.00031831 | 2.5831 | 0.024505 | -0.009155 | -0.036621 | -0.004578 | 0.068665 | 0.018311 | 0.009155 | -0.091553 | -0.027466 | 0.041199 | -0.10529 | -0.041199 | -0.009155 | 0.036621 | -0.027466 | 0.16937 | 0.068664 | -121.6049 | 0.1236 | 0.22888 | 0.16022 | -121.6324 | 0.19684 | 0.13275 | -121.6644 | 0.13275 | 0.054931 | -0.07782 | -121.6324 | 0.17853 | 0.15106 | 0.15564 | -121.7148 | 0.11902 | 0.15106 | 0.20142 | -121.6507
3740.5 | 121.8796 | -0.13733 | 121.5912 | -0.020218 | 0.016404 | 0.013918 | 0.002102 | 0.031014 | 0.00092287 | -0.046104 | -0.020752 | 0.0087607 | -0.0097198 | 0.00010471 | 2.4797 | 0.027282 | -0.036621 | -0.050354 | 0 | 0.054932 | 0.018311 | 0.027466 | -0.064087 | -0.022888 | 0.050354 | -0.054932 | -0.07782 | -0.032043 | 0.064087 | -0.009155 | 0.16479 | 0.073242 | -121.5729 | 0.086975 | 0.19226 | 0.11902 | -121.6278 | 0.20142 | 0.12817 | -121.669 | 0.11444 | 0.082397 | -0.045777 | -121.6232 | 0.15564 | 0.10071 | 0.13733 | -121.6553 | 0.059509 | 0.10529 | 0.18768 | -121.6003
3742.2812 | 121.7651 | -0.1831 | 121.6599 | -0.012589 | 0.01555 | 0.018617 | 0.0040246 | 0.032082 | -0.0039905 | -0.043968 | -0.013123 | 0.010683 | -0.012924 | 0.00095911 | 2.5109 | 0.028136 | 0.013733 | 0.032043 | 0.068665 | 0.10071 | -0.009155 | 0.032043 | -0.082397 | -0.054932 | 0.091553 | -0.086975 | -0.045776 | -0.018311 | 0.054932 | -0.013733 | 0.21515 | 0.10071 | -121.669 | 0.21515 | 0.28381 | 0.18311 | -121.6461 | 0.23804 | 0.16937 | -121.7056 | 0.12817 | 0.09613 | -0.073242 | -121.6782 | 0.17395 | 0.19684 | 0.25177 | -121.7422 | 0.13733 | 0.16479 | 0.27466 | -121.6736
3744.0469 | 121.7697 | -0.1831 | 121.6599 | -0.012589 | 0.014054 | 0.016695 | 0.0031702 | 0.031227 | -0.0024951 | -0.045677 | -0.020752 | 0.0074789 | -0.013992 | 0.00010471 | 2.5162 | 0.026855 | 0 | 0.009155 | 0.027466 | 0.07782 | 0.004578 | 0.032043 | -0.091553 | -0.068665 | 0.041199 | -0.11444 | -0.064087 | -0.018311 | 0.050354 | -0.004578 | 0.21515 | 0.091552 | -121.6553 | 0.19226 | 0.26092 | 0.16937 | -121.6599 | 0.23346 | 0.17853 | -121.7239 | 0.11444 | 0.068664 | -0.10986 | -121.6782 | 0.18768 | 0.1831 | 0.21057 | -121.7514 | 0.11902 | 0.16479 | 0.2243 | -121.6644
3745.7812 | 121.7926 | -0.19226 | 121.6232 | -0.0049592 | 0.015122 | 0.014772 | 0.001034 | 0.0308 | 0.0015637 | -0.042686 | -0.0054932 | 0.013247 | -0.013138 | 0.0045907 | 2.4799 | 0.027709 | -0.041199 | -0.11902 | -0.059509 | 0.027466 | 0.027466 | 0.018311 | -0.09613 | -0.082397 | -0.041199 | -0.16479 | -0.022888 | -0.009155 | 0.050354 | -0.036621 | 0.21057 | 0.096131 | -121.5958 | 0.073242 | 0.21973 | 0.1236 | -121.6644 | 0.24261 | 0.15564 | -121.6461 | 0.10986 | 0.027466 | -0.12817 | -121.6324 | 0.21973 | 0.15106 | 0.13275 | -121.7194 | 0.16937 | 0.18311 | 0.15106 | -121.6599
3747.5625 | 121.7834 | -0.20142 | 121.6644 | -0.027847 | 0.01555 | 0.014986 | 0.0046656 | 0.034645 | -0.0037769 | -0.045463 | -0.020752 | 0.0064109 | -0.012924 | -0.00096349 | 2.5419 | 0.026641 | 0.041199 | 0.054932 | 0.10071 | 0.11444 | -0.022888 | 0.041199 | -0.059509 | -0.009155 | 0.11902 | -0.041199 | -0.068665 | -0.022888 | 0.073242 | 0.004578 | 0.24262 | 0.14191 | -121.6873 | 0.25635 | 0.31586 | 0.17395 | -121.6232 | 0.27466 | 0.20599 | -121.7331 | 0.19226 | 0.16022 | -0.045777 | -121.6873 | 0.17853 | 0.24262 | 0.30212 | -121.7239 | 0.13275 | 0.17853 | 0.32044 | -121.6599
3749.3438 | 121.8338 | -0.16022 | 121.6644 | -0.012589 | 0.012345 | 0.015627 | -0.00024778 | 0.029946 | 0.00070927 | -0.044395 | -0.013123 | 0.010042 | -0.013992 | 0.0011727 | 2.4682 | 0.025146 | -0.022888 | -0.050354 | 0 | 0.068665 | 0.027466 | 0.009155 | -0.10529 | -0.041199 | 0.041199 | -0.10529 | -0.036621 | -0.013733 | 0.041199 | -0.018311 | 0.16937 | 0.054931 | -121.637 | 0.10986 | 0.22888 | 0.17395 | -121.6873 | 0.20142 | 0.14191 | -121.701 | 0.11902 | 0.054931 | -0.086975 | -121.6782 | 0.18768 | 0.13733 | 0.16022 | -121.7697 | 0.1236 | 0.14648 | 0.20142 | -121.6827
3751.0781 | 121.8338 | -0.16937 | 121.6599 | -0.020218 | 0.014268 | 0.016908 | 0.00039302 | 0.032936 | 6.8274e-05 | -0.045463 | -0.013123 | 0.0089743 | -0.012283 | -0.00053629 | 2.5107 | 0.026427 | -0.059509 | -0.073242 | -0.036621 | 0.022888 | 0.036621 | 0 | -0.11902 | -0.086975 | -0.004578 | -0.15106 | -0.018311 | -0.013733 | 0.050354 | -0.032043 | 0.16937 | 0.050354 | -121.6232 | 0.096131 | 0.19226 | 0.14191 | -121.7194 | 0.21973 | 0.13733 | -121.6782 | 0.082398 | 0.018311 | -0.11902 | -121.6736 | 0.20599 | 0.10986 | 0.13275 | -121.7789 | 0.15106 | 0.15564 | 0.16479 | -121.6919
3752.8594 | 121.7926 | -0.20142 | 121.6827 | -0.0049592 | 0.014909 | 0.015627 | 0.002102 | 0.033577 | -0.0048449 | -0.045036 | -0.0054932 | 0.0051291 | -0.013351 | 0.00010471 | 2.5669 | 0.026641 | 0.009155 | 0.036621 | 0.073242 | 0.10529 | -0.013733 | 0.022888 | -0.07782 | -0.036621 | 0.073242 | -0.082397 | -0.054932 | -0.018311 | 0.082397 | -0.009155 | 0.2243 | 0.1236 | -121.6965 | 0.23804 | 0.3067 | 0.18311 | -121.6736 | 0.28381 | 0.19226 | -121.7377 | 0.1648 | 0.11902 | -0.073242 | -121.701 | 0.18768 | 0.21057 | 0.27466 | -121.7606 | 0.14648 | 0.18311 | 0.27466 | -121.6919
3754.5781 | 121.8979 | -0.15106 | 121.6415 | -0.012589 | 0.0093545 | 0.016908 | 0.0033838 | 0.030373 | -0.0050585 | -0.045463 | -0.020752 | 0.0066245 | -0.015274 | -0.00032249 | 2.5284 | 0.026 | -0.027466 | 0.022888 | 0.041199 | 0.07782 | -0.004578 | 0.032043 | -0.073242 | -0.050354 | 0.041199 | -0.064087 | -0.064087 | -0.036621 | 0.064087 | 0 | 0.18311 | 0.07782 | -121.6461 | 0.17395 | 0.22888 | 0.15106 | -121.669 | 0.21515 | 0.15106 | -121.7056 | 0.10071 | 0.086975 | -0.064087 | -121.6782 | 0.14648 | 0.1236 | 0.19226 | -121.7148 | 0.086975 | 0.11444 | 0.19226 | -121.6415
3756.3438 | 121.9162 | -0.14191 | 121.6599 | -0.012589 | 0.011064 | 0.016481 | -0.00067498 | 0.031868 | -0.0029223 | -0.045463 | -0.013123 | 0.0083335 | -0.015274 | -0.00096349 | 2.5752 | 0.027068 | -0.027466 | 0 | 0.045776 | 0.07782 | -0.009155 | 0.059509 | -0.068665 | -0.059509 | 0.045776 | -0.068665 | -0.068665 | -0.050354 | 0.068665 | 0.009155 | 0.20142 | 0.073242 | -121.669 | 0.14191 | 0.21973 | 0.14649 | -121.6873 | 0.21057 | 0.15106 | -121.7285 | 0.082398 | 0.073242 | -0.07782 | -121.7102 | 0.13275 | 0.11444 | 0.18768 | -121.7285 | 0.073242 | 0.091553 | 0.18768 | -121.6507
3758.125 | 121.9574 | -0.15106 | 121.6461 | -0.0049592 | 0.012559 | 0.017336 | 0.002102 | 0.0308 | -0.0029223 | -0.042473 | -0.013123 | 0.0083335 | -0.016769 | -0.0016043 | 2.6145 | 0.025146 | -0.004578 | 0.018311 | 0.059509 | 0.064087 | -0.013733 | 0.032043 | -0.068665 | -0.022888 | 0.10071 | -0.032043 | -0.068665 | -0.045776 | 0.073242 | 0.009155 | 0.18311 | 0.082397 | -121.6599 | 0.16937 | 0.21515 | 0.13275 | -121.6507 | 0.2243 | 0.16022 | -121.7148 | 0.12817 | 0.11902 | -0.041198 | -121.6919 | 0.13733 | 0.14648 | 0.21057 | -121.7148 | 0.082397 | 0.10529 | 0.25177 | -121.637
3759.8438 | 121.8109 | -0.17395 | 121.6782 | -0.012589 | 0.016191 | 0.01584 | -0.0021704 | 0.034004 | 0.0069043 | -0.043541 | -0.020752 | 0.012819 | -0.013565 | 0.00074551 | 2.5429 | 0.024932 | 0.009155 | -0.018311 | 0 | 0.059509 | 0.018311 | 0.027466 | -0.091553 | -0.027466 | -0.018311 | -0.15106 | -0.041199 | -0.022888 | 0.059509 | -0.036621 | 0.20142 | 0.082397 | -121.6599 | 0.15564 | 0.23346 | 0.15106 | -121.669 | 0.23346 | 0.13733 | -121.7194 | 0.14648 | 0.022888 | -0.11444 | -121.701 | 0.19226 | 0.1831 | 0.17395 | -121.7697 | 0.13275 | 0.15106 | 0.15564 | -121.7148
3761.625 | 121.9254 | -0.15106 | 121.6782 | -0.012589 | 0.012559 | 0.019899 | 0.0018884 | 0.029518 | -0.0031359 | -0.043968 | -0.013123 | 0.0074789 | -0.014633 | -0.0041679 | 2.5564 | 0.026 | 0.068665 | 0.091553 | 0.10529 | 0.11444 | -0.027466 | 0.059509 | -0.050354 | 0.022888 | 0.15564 | 0 | -0.082397 | -0.050354 | 0.07782 | 0.009155 | 0.21057 | 0.10071 | -121.7056 | 0.24261 | 0.2655 | 0.16479 | -121.6095 | 0.22888 | 0.16022 | -121.7606 | 0.17395 | 0.15106 | -0.009155 | -121.7285 | 0.1236 | 0.21973 | 0.25635 | -121.7285 | 0.068665 | 0.10071 | 0.3067 | -121.669
3763.4062 | 121.9528 | -0.12817 | 121.6553 | -0.0049592 | 0.010636 | 0.017549 | -3.4178e-05 | 0.029732 | -0.0031359 | -0.045036 | -0.013123 | 0.0070517 | -0.013779 | -0.0011771 | 2.5186 | 0.026427 | -0.013733 | -0.009155 | 0.054932 | 0.068665 | -0.004578 | 0.032043 | -0.059509 | -0.032043 | 0.054932 | -0.07782 | -0.068665 | -0.036621 | 0.068665 | -0.009155 | 0.16022 | 0.068665 | -121.6599 | 0.11902 | 0.19684 | 0.12817 | -121.669 | 0.19684 | 0.11902 | -121.7239 | 0.096131 | 0.050354 | -0.068665 | -121.6919 | 0.1236 | 0.11444 | 0.18311 | -121.7148 | 0.059509 | 0.091553 | 0.18311 | -121.6644
3765.125 | 121.9711 | -0.14191 | 121.6873 | -0.0049592 | 0.010209 | 0.017976 | 0.0044518 | 0.031014 | -0.0016405 | -0.043113 | -0.020752 | 0.0053427 | -0.013992 | -0.0026725 | 2.497 | 0.026641 | 0.041199 | 0.07782 | 0.10529 | 0.11902 | -0.018311 | 0.054932 | -0.07782 | 0.027466 | 0.13733 | 0 | -0.07782 | -0.064087 | 0.09613 | 0.004578 | 0.19684 | 0.064087 | -121.7056 | 0.21973 | 0.26093 | 0.19684 | -121.6461 | 0.23804 | 0.14649 | -121.7651 | 0.16937 | 0.14191 | -0.004578 | -121.7514 | 0.1236 | 0.18311 | 0.24719 | -121.7651 | 0.064087 | 0.07782 | 0.27924 | -121.6827
3766.9062 | 121.8567 | -0.19226 | 121.6965 | -0.0049592 | 0.013413 | 0.017122 | 0.00082022 | 0.031655 | 6.8274e-05 | -0.043754 | -0.013123 | 0.0081199 | -0.015701 | -0.00096349 | 2.5034 | 0.025359 | 0.054932 | 0.073242 | 0.10071 | 0.11902 | -0.018311 | 0.041199 | -0.073242 | 0.004578 | 0.12817 | -0.045776 | -0.054932 | -0.036621 | 0.082397 | 0.022888 | 0.23346 | 0.11902 | -121.7148 | 0.2655 | 0.31128 | 0.19226 | -121.6415 | 0.27466 | 0.21515 | -121.7514 | 0.19684 | 0.14648 | -0.068664 | -121.7331 | 0.17395 | 0.24719 | 0.29297 | -121.7697 | 0.13733 | 0.15564 | 0.32044 | -121.6736
3768.6875 | 121.9803 | -0.16022 | 121.6873 | -0.012589 | 0.012773 | 0.016481 | 0.0046656 | 0.029305 | -0.0037769 | -0.046104 | -0.0054932 | 0.0057699 | -0.01442 | -0.00053629 | 2.5107 | 0.026214 | -0.022888 | 0.018311 | 0.045776 | 0.073242 | -0.018311 | 0.050354 | -0.073242 | -0.027466 | 0.073242 | -0.059509 | -0.059509 | -0.050354 | 0.068665 | 0.004578 | 0.21057 | 0.086975 | -121.7056 | 0.17853 | 0.23346 | 0.14648 | -121.7102 | 0.22888 | 0.16479 | -121.7468 | 0.13275 | 0.10071 | -0.064087 | -121.7377 | 0.14191 | 0.13733 | 0.20599 | -121.7606 | 0.10071 | 0.10986 | 0.23346 | -121.6827
3770.4531 | 121.9208 | -0.15564 | 121.6919 | -0.0049592 | 0.011064 | 0.015413 | -0.0015296 | 0.029946 | -0.0014269 | -0.044395 | -0.013123 | 0.01111 | -0.015701 | -0.0020315 | 2.4906 | 0.024932 | 0.022888 | 0.004578 | 0.054932 | 0.091553 | -0.004578 | 0.064087 | -0.059509 | -0.009155 | 0.059509 | -0.082397 | -0.086975 | -0.027466 | 0.064087 | 0.009155 | 0.21973 | 0.096131 | -121.6965 | 0.16022 | 0.24719 | 0.15106 | -121.669 | 0.21973 | 0.16479 | -121.7789 | 0.14649 | 0.073243 | -0.091552 | -121.7194 | 0.15106 | 0.17853 | 0.21057 | -121.7514 | 0.068665 | 0.12817 | 0.21515 | -121.6827
3772.1875 | 121.8979 | -0.17395 | 121.7194 | -0.012589 | 0.015763 | 0.016054 | 0.00060662 | 0.029518 | 0.0058363 | -0.044395 | -0.013123 | 0.010897 | -0.014633 | 0.00053191 | 2.5508 | 0.021514 | -0.013733 | -0.036621 | -0.018311 | 0.064087 | 0.027466 | 0.027466 | -0.09613 | -0.013733 | 0.032043 | -0.13275 | -0.036621 | -0.018311 | 0.050354 | -0.004578 | 0.20142 | 0.07782 | -121.6919 | 0.13733 | 0.23804 | 0.16022 | -121.7331 | 0.2243 | 0.16937 | -121.756 | 0.16022 | 0.041199 | -0.12817 | -121.7377 | 0.20142 | 0.16022 | 0.15564 | -121.8155 | 0.13733 | 0.15564 | 0.20599 | -121.7239
3773.9844 | 121.9894 | -0.14191 | 121.7056 | -0.0049592 | 0.014268 | 0.016267 | 0.0035974 | 0.033577 | -0.0027087 | -0.044395 | -0.020752 | 0.0064109 | -0.013565 | -0.0013907 | 2.5297 | 0.026 | 0.004578 | 0.027466 | 0.082397 | 0.09613 | -0.036621 | 0.027466 | -0.068665 | 0.018311 | 0.11902 | -0.018311 | -0.082397 | -0.054932 | 0.073242 | 0.022888 | 0.16937 | 0.073242 | -121.7422 | 0.16937 | 0.23804 | 0.16479 | -121.701 | 0.21515 | 0.16479 | -121.788 | 0.16022 | 0.1236 | -0.041199 | -121.7606 | 0.10529 | 0.14649 | 0.2243 | -121.7743 | 0.05951 | 0.086975 | 0.26093 | -121.6827
3775.7656 | 121.9986 | -0.12817 | 121.701 | -0.012589 | 0.011491 | 0.014345 | 0.00082022 | 0.032082 | 0.0041273 | -0.043113 | -0.0054932 | 0.0098289 | -0.016129 | 0.0022409 | 2.5643 | 0.025786 | 0.018311 | -0.018311 | 0.013733 | 0.064087 | 0.018311 | 0.036621 | -0.068665 | 0.027466 | 0.07782 | -0.068665 | -0.064087 | -0.036621 | 0.073242 | 0.027466 | 0.1648 | 0.059509 | -121.6827 | 0.10986 | 0.19226 | 0.13275 | -121.6827 | 0.20142 | 0.15564 | -121.7651 | 0.15564 | 0.059509 | -0.096131 | -121.7377 | 0.14649 | 0.14649 | 0.14191 | -121.7697 | 0.064087 | 0.091553 | 0.20599 | -121.6736
3777.4688 | 121.9711 | -0.13275 | 121.7285 | -0.0049592 | 0.0132 | 0.017549 | 0.0025292 | 0.03315 | -0.0039905 | -0.043113 | -0.013123 | 0.0074789 | -0.013992 | -0.0011771 | 2.581 | 0.027282 | 0.041199 | 0.11444 | 0.11444 | 0.1236 | -0.018311 | 0.041199 | -0.059509 | 0.032043 | 0.15564 | -0.013733 | -0.054932 | -0.059509 | 0.091553 | 0.018311 | 0.17395 | 0.073242 | -121.7468 | 0.24719 | 0.25635 | 0.1831 | -121.6873 | 0.2243 | 0.15106 | -121.7834 | 0.16479 | 0.11902 | -0.032044 | -121.788 | 0.11444 | 0.17395 | 0.24719 | -121.788 | 0.077819 | 0.073242 | 0.28839 | -121.7102
3779.2656 | 121.9528 | -0.15106 | 121.7331 | -0.020218 | 0.011277 | 0.017976 | -0.00067498 | 0.032295 | -0.0037769 | -0.043113 | -0.013123 | 0.0066245 | -0.015701 | -0.0020315 | 2.532 | 0.026427 | 0.013733 | -0.004578 | 0.036621 | 0.073242 | -0.018311 | 0.041199 | -0.073242 | -0.022888 | 0.068665 | -0.068665 | -0.068665 | -0.041199 | 0.068665 | -0.004578 | 0.19226 | 0.07782 | -121.7514 | 0.14648 | 0.2243 | 0.14648 | -121.7194 | 0.21973 | 0.14648 | -121.8018 | 0.12817 | 0.082397 | -0.064087 | -121.7743 | 0.13275 | 0.16479 | 0.18768 | -121.8063 | 0.082397 | 0.10986 | 0.21973 | -121.7377
3781.0469 | 121.8475 | -0.19226 | 121.7514 | -0.012589 | 0.017686 | 0.016054 | -0.00046138 | 0.033791 | 0.0064771 | -0.043754 | -0.028381 | 0.011965 | -0.014633 | -0.00010889 | 2.5158 | 0.02365 | 0.036621 | 0 | 0.009155 | 0.073242 | 0.022888 | 0.022888 | -0.10071 | 0 | 0.018311 | -0.13275 | -0.054932 | -0.018311 | 0.059509 | -0.013733 | 0.21515 | 0.091553 | -121.7285 | 0.19226 | 0.2655 | 0.17395 | -121.7148 | 0.25177 | 0.17853 | -121.8063 | 0.19226 | 0.05951 | -0.11902 | -121.7697 | 0.21515 | 0.22888 | 0.20142 | -121.8521 | 0.13733 | 0.17395 | 0.21057 | -121.7651
3782.8281 | 121.962 | -0.14191 | 121.7194 | -0.012589 | 0.012773 | 0.014772 | 0.0016748 | 0.031227 | 0.00049567 | -0.041832 | -0.0054932 | 0.0070517 | -0.01442 | -0.0013907 | 2.4915 | 0.026 | 0.045776 | 0.059509 | 0.086975 | 0.10529 | -0.018311 | 0.045776 | -0.082397 | 0.041199 | 0.10529 | -0.036621 | -0.073242 | -0.050354 | 0.07782 | 0.022888 | 0.18768 | 0.05951 | -121.7377 | 0.20142 | 0.24719 | 0.18768 | -121.6736 | 0.21973 | 0.16479 | -121.7926 | 0.18311 | 0.10529 | -0.059509 | -121.7697 | 0.1236 | 0.18768 | 0.22888 | -121.8018 | 0.068665 | 0.091553 | 0.24719 | -121.6965
3784.6094 | 121.8842 | -0.18768 | 121.7789 | -0.0049592 | 0.017472 | 0.014345 | 0.00060662 | 0.031655 | 0.0032727 | -0.043968 | -0.020752 | 0.01047 | -0.013138 | -0.0020315 | 2.5549 | 0.023864 | 0.036621 | -0.004578 | 0.013733 | 0.073242 | 0.013733 | 0.027466 | -0.09613 | -0.004578 | 0.064087 | -0.11902 | -0.041199 | -0.032043 | 0.041199 | -0.013733 | 0.21515 | 0.091553 | -121.7651 | 0.1831 | 0.26092 | 0.16937 | -121.7422 | 0.22888 | 0.17395 | -121.8201 | 0.1831 | 0.068664 | -0.10529 | -121.8109 | 0.20142 | 0.2243 | 0.20142 | -121.875 | 0.14648 | 0.15564 | 0.25177 | -121.7926
3786.3906 | 121.994 | -0.13275 | 121.7285 | -0.012589 | 0.014695 | 0.017763 | -0.00067498 | 0.029732 | 0.0024183 | -0.041618 | -0.020752 | 0.0089743 | -0.014847 | -0.00053629 | 2.5523 | 0.027282 | -0.027466 | -0.068665 | -0.018311 | 0.032043 | 0.022888 | 0.013733 | -0.091553 | -0.027466 | 0.013733 | -0.11902 | -0.045776 | -0.027466 | 0.064087 | -0.009155 | 0.14648 | 0.041198 | -121.7056 | 0.064086 | 0.16479 | 0.1236 | -121.756 | 0.19684 | 0.1236 | -121.7743 | 0.10529 | 0.013732 | -0.10986 | -121.756 | 0.15564 | 0.10529 | 0.11444 | -121.8201 | 0.086975 | 0.10529 | 0.14648 | -121.7377
3788.1875 | 122.0123 | -0.13275 | 121.7285 | -0.0049592 | 0.015122 | 0.014558 | -0.001316 | 0.031014 | 0.00049567 | -0.043541 | -0.0054932 | 0.013888 | -0.016129 | -0.00032249 | 2.6128 | 0.027709 | -0.022888 | -0.064087 | -0.022888 | 0.036621 | 0.022888 | 0.022888 | -0.091553 | -0.027466 | 0.027466 | -0.10071 | -0.045776 | -0.036621 | 0.064087 | 0 | 0.15564 | 0.041198 | -121.7056 | 0.068664 | 0.16937 | 0.12817 | -121.7514 | 0.19684 | 0.13275 | -121.7743 | 0.10529 | 0.032043 | -0.10071 | -121.7651 | 0.15564 | 0.10986 | 0.10986 | -121.8201 | 0.086975 | 0.09613 | 0.16022 | -121.7285
3789.9062 | 121.875 | -0.17853 | 121.7651 | -0.012589 | 0.015977 | 0.015413 | 0.00017942 | 0.033364 | 0.0024183 | -0.043327 | -0.013123 | 0.013033 | -0.013351 | 0.0016001 | 2.5667 | 0.025573 | -0.004578 | -0.064087 | -0.032043 | 0.032043 | 0.022888 | 0.027466 | -0.091553 | -0.059509 | -0.004578 | -0.17853 | -0.032043 | -0.022888 | 0.045776 | -0.004578 | 0.20599 | 0.086975 | -121.7422 | 0.11444 | 0.21057 | 0.1236 | -121.7697 | 0.2243 | 0.17395 | -121.7972 | 0.11902 | 0 | -0.17395 | -121.788 | 0.20142 | 0.17395 | 0.14648 | -121.8567 | 0.14648 | 0.15564 | 0.17395 | -121.7697
3791.6875 | 122.0261 | -0.11444 | 121.7468 | -0.020218 | 0.011918 | 0.016267 | 0.0025292 | 0.031441 | -0.0054859 | -0.044182 | -0.013123 | 0.0042747 | -0.015488 | -0.0024589 | 2.5949 | 0.027282 | 0.013733 | 0.041199 | 0.082397 | 0.10529 | 0.004578 | 0.032043 | -0.059509 | -0.009155 | 0.13733 | -0.018311 | -0.064087 | -0.050354 | 0.091553 | 0.022888 | 0.14648 | 0.054932 | -121.7422 | 0.15564 | 0.21973 | 0.16479 | -121.7331 | 0.20599 | 0.13733 | -121.8109 | 0.10529 | 0.09613 | -0.041199 | -121.7972 | 0.11902 | 0.12817 | 0.19684 | -121.8063 | 0.050354 | 0.064087 | 0.25177 | -121.7239
3793.4062 | 121.9162 | -0.17395 | 121.7834 | -0.0049592 | 0.012986 | 0.01349 | 0.0012476 | 0.028878 | 0.0024183 | -0.043327 | -0.013123 | 0.011751 | -0.015488 | 0.00053191 | 2.6064 | 0.025573 | -0.054932 | -0.1236 | -0.073242 | 0.004578 | 0.013733 | 0.004578 | -0.091553 | -0.07782 | -0.045776 | -0.16479 | -0.045776 | -0.004578 | 0.050354 | -0.022888 | 0.17853 | 0.082397 | -121.7697 | 0.050354 | 0.17853 | 0.096131 | -121.8384 | 0.2243 | 0.15106 | -121.8292 | 0.09613 | 0.009155 | -0.14191 | -121.788 | 0.18768 | 0.11902 | 0.10071 | -121.875 | 0.12817 | 0.16937 | 0.12817 | -121.8063
3795.2031 | 121.9162 | -0.1831 | 121.7926 | -0.012589 | 0.015977 | 0.016908 | 0.00017942 | 0.033577 | 0.0026319 | -0.043541 | -0.013123 | 0.0091879 | -0.015274 | 0.0011727 | 2.5799 | 0.027282 | -0.07782 | -0.1236 | -0.059509 | 0.004578 | 0.013733 | 0.022888 | -0.10529 | -0.07782 | -0.045776 | -0.1831 | -0.041199 | -0.032043 | 0.054932 | -0.027466 | 0.20599 | 0.077819 | -121.7789 | 0.059509 | 0.18768 | 0.10986 | -121.8704 | 0.23804 | 0.15564 | -121.8338 | 0.10528 | 0 | -0.15564 | -121.8246 | 0.19684 | 0.10528 | 0.1236 | -121.8979 | 0.14191 | 0.15106 | 0.13733 | -121.8201
3796.9844 | 121.9894 | -0.14648 | 121.7834 | -0.012589 | 0.011064 | 0.018404 | 0.0040246 | 0.031014 | -0.0061267 | -0.043968 | -0.0054932 | 0.0068381 | -0.013992 | -0.00074989 | 2.626 | 0.027709 | -0.009155 | 0.004578 | 0.045776 | 0.059509 | -0.013733 | 0.027466 | -0.064087 | -0.050354 | 0.068665 | -0.068665 | -0.068665 | -0.041199 | 0.064087 | 0.013733 | 0.17395 | 0.082397 | -121.7972 | 0.15106 | 0.20599 | 0.1236 | -121.7926 | 0.21057 | 0.16022 | -121.8521 | 0.09613 | 0.077819 | -0.082398 | -121.8246 | 0.13275 | 0.13733 | 0.19226 | -121.8475 | 0.077819 | 0.10529 | 0.21515 | -121.7697
3798.7031 | 121.9208 | -0.18768 | 121.8338 | -0.012589 | 0.015336 | 0.019045 | 0.0027428 | 0.032723 | -0.0020679 | -0.042259 | -0.013123 | 0.0068381 | -0.014206 | -0.0020315 | 2.5797 | 0.026641 | -0.032043 | -0.013733 | 0.018311 | 0.054932 | 0.013733 | 0.013733 | -0.10071 | -0.09613 | 0.036621 | -0.13275 | -0.032043 | -0.018311 | 0.032043 | -0.041199 | 0.20142 | 0.086975 | -121.8201 | 0.17395 | 0.24261 | 0.15564 | -121.8658 | 0.21973 | 0.14648 | -121.8658 | 0.091553 | 0.054932 | -0.091552 | -121.8521 | 0.20142 | 0.15564 | 0.20599 | -121.9345 | 0.15564 | 0.16937 | 0.2243 | -121.875
3800.4688 | 121.9254 | -0.17853 | 121.8201 | 0.0026703 | 0.014268 | 0.020326 | 0.0035974 | 0.029305 | -0.0024951 | -0.046531 | -0.013123 | 0.0068381 | -0.011642 | -0.00053629 | 2.54 | 0.025359 | 0.018311 | 0.064087 | 0.064087 | 0.10529 | -0.013733 | 0.013733 | -0.068665 | -0.027466 | 0.10529 | -0.073242 | -0.059509 | -0.045776 | 0.036621 | -0.018311 | 0.19226 | 0.10986 | -121.8338 | 0.24261 | 0.28381 | 0.17395 | -121.8018 | 0.21515 | 0.16022 | -121.8796 | 0.15106 | 0.10529 | -0.054931 | -121.8658 | 0.16479 | 0.19684 | 0.24261 | -121.8887 | 0.11902 | 0.13275 | 0.28381 | -121.8384
3802.25 | 121.9345 | -0.20599 | 121.8018 | 0.0026703 | 0.015763 | 0.015627 | 0.003811 | 0.030159 | -0.0029223 | -0.041404 | -0.028381 | 0.0094015 | -0.01207 | -0.0013907 | 2.5491 | 0.025786 | 0.032043 | 0.045776 | 0.086975 | 0.11444 | 0 | 0.041199 | -0.082397 | 0 | 0.1236 | -0.045776 | -0.059509 | -0.045776 | 0.054932 | -0.009155 | 0.24719 | 0.1236 | -121.8018 | 0.25177 | 0.32044 | 0.19684 | -121.7697 | 0.26093 | 0.19684 | -121.8613 | 0.20599 | 0.16022 | -0.036621 | -121.8475 | 0.20599 | 0.23804 | 0.29297 | -121.8842 | 0.14649 | 0.16022 | 0.32959 | -121.8109
3803.9844 | 121.9482 | -0.14648 | 121.8201 | -0.012589 | 0.017259 | 0.013918 | -0.001316 | 0.0308 | 0.0028455 | -0.043754 | -0.0054932 | 0.01047 | -0.015488 | -0.00032249 | 2.6013 | 0.023009 | 0.022888 | 0.004578 | 0.018311 | 0.068665 | 0.027466 | 0.022888 | -0.07782 | 0 | 0.064087 | -0.10986 | -0.041199 | -0.041199 | 0.045776 | -0.004578 | 0.16937 | 0.068664 | -121.7926 | 0.15106 | 0.21515 | 0.14649 | -121.7972 | 0.19226 | 0.14191 | -121.8613 | 0.14648 | 0.036621 | -0.10529 | -121.8613 | 0.17395 | 0.16937 | 0.16479 | -121.8979 | 0.10529 | 0.10529 | 0.21057 | -121.8246
3805.7812 | 121.9345 | -0.20599 | 121.8063 | -0.020218 | 0.016191 | 0.015413 | 0.0029566 | 0.031655 | -0.0022815 | -0.045891 | -0.0054932 | 0.0072653 | -0.015915 | -0.0026725 | 2.5474 | 0.026641 | -0.009155 | 0.013733 | 0.045776 | 0.073242 | -0.004578 | 0.009155 | -0.091553 | -0.064087 | 0.045776 | -0.10986 | -0.041199 | -0.018311 | 0.050354 | 0 | 0.21515 | 0.11444 | -121.8109 | 0.21973 | 0.27924 | 0.16479 | -121.8155 | 0.25635 | 0.20599 | -121.8475 | 0.14191 | 0.096131 | -0.10986 | -121.8246 | 0.20142 | 0.19684 | 0.25177 | -121.8979 | 0.1648 | 0.18768 | 0.25177 | -121.8063
3807.5 | 121.9437 | -0.1831 | 121.8155 | -0.0049592 | 0.016404 | 0.015627 | -0.0021704 | 0.033577 | 0.0032727 | -0.043968 | -0.013123 | 0.012819 | -0.016129 | 0.0020273 | 2.5231 | 0.024505 | 0.032043 | -0.004578 | 0.022888 | 0.07782 | 0.013733 | 0.018311 | -0.07782 | -0.022888 | 0.032043 | -0.11444 | -0.045776 | -0.004578 | 0.059509 | -0.009155 | 0.20142 | 0.10528 | -121.8018 | 0.17853 | 0.26092 | 0.15564 | -121.7834 | 0.24261 | 0.17395 | -121.8613 | 0.16022 | 0.068664 | -0.10529 | -121.8201 | 0.19684 | 0.21515 | 0.20599 | -121.8933 | 0.13733 | 0.17853 | 0.21515 | -121.8246
3809.2812 | 122.0673 | -0.12817 | 121.7972 | -0.0049592 | 0.010209 | 0.017122 | 0.0016748 | 0.033577 | -0.0059131 | -0.045036 | -0.013123 | 0.0061973 | -0.017624 | -0.0026725 | 2.5378 | 0.027282 | -0.036621 | -0.013733 | 0.036621 | 0.07782 | 0.018311 | 0.027466 | -0.068665 | -0.032043 | 0.073242 | -0.054932 | -0.068665 | -0.036621 | 0.068665 | 0.013733 | 0.15564 | 0.059509 | -121.7789 | 0.11444 | 0.20599 | 0.14649 | -121.8338 | 0.19684 | 0.14191 | -121.8658 | 0.096131 | 0.073242 | -0.068665 | -121.8338 | 0.14649 | 0.091553 | 0.1648 | -121.8658 | 0.059509 | 0.091553 | 0.20142 | -121.7834
3811.0625 | 121.9849 | -0.16022 | 121.7926 | -0.012589 | 0.014054 | 0.014345 | 0.00060662 | 0.031014 | 0.0049817 | -0.046745 | -0.013123 | 0.010897 | -0.013992 | -0.00032249 | 2.5602 | 0.025573 | -0.018311 | -0.050354 | -0.013733 | 0.050354 | 0.022888 | 0.032043 | -0.091553 | -0.027466 | 0.036621 | -0.11902 | -0.045776 | -0.013733 | 0.036621 | -0.013733 | 0.19226 | 0.068664 | -121.7697 | 0.10986 | 0.21057 | 0.14191 | -121.8109 | 0.19684 | 0.14648 | -121.8384 | 0.13275 | 0.041198 | -0.10529 | -121.8063 | 0.1831 | 0.14191 | 0.14648 | -121.8842 | 0.11444 | 0.14648 | 0.19684 | -121.8063
3812.8594 | 121.9437 | -0.19226 | 121.8384 | -0.012589 | 0.018113 | 0.016267 | 0.0023156 | 0.034859 | 0.0045545 | -0.043968 | -0.013123 | 0.012819 | -0.013992 | 0.00074551 | 2.597 | 0.025146 | 0.022888 | -0.027466 | 0.004578 | 0.064087 | 0.018311 | 0.018311 | -0.091553 | -0.054932 | 0.022888 | -0.11902 | -0.041199 | -0.041199 | 0.036621 | -0.018311 | 0.21057 | 0.10071 | -121.8201 | 0.16479 | 0.25635 | 0.15564 | -121.8155 | 0.22888 | 0.17395 | -121.8796 | 0.13733 | 0.073242 | -0.10071 | -121.8796 | 0.21057 | 0.21515 | 0.19684 | -121.9299 | 0.15106 | 0.15106 | 0.21515 | -121.8567
3814.5625 | 121.9803 | -0.16937 | 121.8063 | -0.020218 | 0.014268 | 0.018617 | 0.0033838 | 0.031655 | -0.0014269 | -0.042473 | -0.0054932 | 0.0059837 | -0.015915 | -0.0011771 | 2.6064 | 0.027923 | 0.022888 | 0.073242 | 0.10071 | 0.12817 | 0 | 0.059509 | -0.059509 | -0.004578 | 0.14648 | -0.013733 | -0.07782 | -0.045776 | 0.054932 | 0 | 0.22888 | 0.10986 | -121.8063 | 0.24261 | 0.29755 | 0.18768 | -121.7834 | 0.22431 | 0.16937 | -121.8842 | 0.16479 | 0.15564 | -0.013733 | -121.8521 | 0.16937 | 0.19226 | 0.27008 | -121.8658 | 0.091553 | 0.1236 | 0.31586 | -121.8063
3816.3438 | 122.0535 | -0.14191 | 121.8109 | -0.0049592 | 0.01555 | 0.014558 | 0.0014612 | 0.030159 | 0.0013501 | -0.043968 | -0.013123 | 0.011324 | -0.013779 | -0.00010889 | 2.6094 | 0.026427 | -0.050354 | -0.07782 | -0.054932 | 0.013733 | 0.032043 | 0.018311 | -0.10071 | -0.068665 | -0.013733 | -0.15106 | -0.036621 | -0.018311 | 0.045776 | -0.004578 | 0.16022 | 0.041199 | -121.7789 | 0.064087 | 0.15564 | 0.11444 | -121.8613 | 0.18768 | 0.13733 | -121.8475 | 0.073242 | -0.009155 | -0.14648 | -121.8292 | 0.17395 | 0.091553 | 0.086975 | -121.9116 | 0.10529 | 0.1236 | 0.12817 | -121.8155
3818.0469 | 121.9666 | -0.17853 | 121.8338 | -0.012589 | 0.016191 | 0.017763 | 0.003811 | 0.031227 | -0.0014269 | -0.043968 | -0.020752 | 0.0087607 | -0.012711 | -0.00096349 | 2.54 | 0.027282 | -0.064087 | -0.059509 | -0.018311 | 0.018311 | 0.013733 | 0.004578 | -0.11902 | -0.10529 | 0.009155 | -0.14648 | -0.027466 | 0 | 0.018311 | -0.027466 | 0.18311 | 0.059509 | -121.8201 | 0.11902 | 0.19684 | 0.13733 | -121.8979 | 0.19684 | 0.15106 | -121.8613 | 0.073242 | 0.032044 | -0.11902 | -121.8338 | 0.19226 | 0.11444 | 0.16022 | -121.9528 | 0.15106 | 0.17853 | 0.18768 | -121.8613
3819.8438 | 121.994 | -0.17395 | 121.8384 | -0.012589 | 0.014909 | 0.015199 | 0.003811 | 0.032723 | 0.00028207 | -0.044395 | 0.0021363 | 0.0096151 | -0.013351 | 0.0013863 | 2.5391 | 0.025573 | -0.036621 | -0.082397 | -0.032043 | 0.041199 | 0.054932 | 0.004578 | -0.10986 | -0.07782 | 0.018311 | -0.13733 | -0.041199 | -0.018311 | 0.036621 | -0.041199 | 0.17853 | 0.064087 | -121.7834 | 0.091553 | 0.21515 | 0.15106 | -121.875 | 0.21057 | 0.13275 | -121.8796 | 0.09613 | 0.036621 | -0.09613 | -121.8567 | 0.22888 | 0.13733 | 0.14191 | -121.9482 | 0.13275 | 0.15564 | 0.19226 | -121.8796
3821.625 | 121.994 | -0.16937 | 121.8567 | -0.020218 | 0.016831 | 0.014345 | 0.0012476 | 0.032509 | 0.0028455 | -0.043754 | -0.013123 | 0.010683 | -0.014206 | 0.0024545 | 2.5921 | 0.026 | -0.068665 | -0.09613 | -0.054932 | 0.045776 | 0.018311 | 0.027466 | -0.091553 | -0.10071 | -0.041199 | -0.16937 | -0.022888 | -0.018311 | 0.036621 | -0.027466 | 0.19684 | 0.07782 | -121.8384 | 0.073243 | 0.21515 | 0.13733 | -121.9254 | 0.20599 | 0.14191 | -121.8796 | 0.068665 | 0 | -0.14191 | -121.875 | 0.18768 | 0.10071 | 0.11444 | -121.9482 | 0.14649 | 0.15106 | 0.12817 | -121.8842
3823.3906 | 122.0581 | -0.15106 | 121.8155 | -0.012589 | 0.010209 | 0.016481 | -0.0019568 | 0.032509 | -0.0042041 | -0.042473 | -0.013123 | 0.0070517 | -0.017624 | -0.0022453 | 2.5113 | 0.029204 | 0.027466 | 0.064087 | 0.10071 | 0.11444 | -0.018311 | 0.036621 | -0.050354 | 0.009155 | 0.11444 | -0.013733 | -0.10529 | -0.059509 | 0.07782 | 0.009155 | 0.18768 | 0.10071 | -121.8338 | 0.21515 | 0.2655 | 0.16479 | -121.788 | 0.22888 | 0.16022 | -121.9208 | 0.16022 | 0.13733 | -0.022888 | -121.875 | 0.13275 | 0.17853 | 0.25177 | -121.8658 | 0.045776 | 0.091553 | 0.2655 | -121.8063
3825.1875 | 122.0215 | -0.16937 | 121.8521 | -0.012589 | 0.017259 | 0.014986 | 0.0016748 | 0.032723 | 0.0015637 | -0.045036 | -0.0054932 | 0.0094015 | -0.013779 | -0.00053629 | 2.5299 | 0.025146 | -0.054932 | -0.091553 | -0.027466 | 0.045776 | 0.041199 | 0.009155 | -0.10986 | -0.068665 | 0.027466 | -0.12817 | -0.032043 | -0.013733 | 0.045776 | -0.009155 | 0.17853 | 0.05951 | -121.8109 | 0.07782 | 0.21515 | 0.15564 | -121.907 | 0.21515 | 0.16022 | -121.8842 | 0.10071 | 0.041199 | -0.11902 | -121.8658 | 0.21057 | 0.11444 | 0.14191 | -121.962 | 0.13733 | 0.15564 | 0.19684 | -121.8613
3826.9062 | 122.113 | -0.13275 | 121.8246 | -0.012589 | 0.011918 | 0.016054 | 0.0035974 | 0.029946 | -0.0052721 | -0.04525 | -0.020752 | 0.0055563 | -0.016769 | 0.00010471 | 2.6399 | 0.027923 | -0.018311 | -0.013733 | 0.045776 | 0.07782 | 0 | 0.050354 | -0.064087 | 0 | 0.082397 | -0.041199 | -0.068665 | -0.022888 | 0.068665 | 0.009155 | 0.18311 | 0.068664 | -121.8246 | 0.11902 | 0.21057 | 0.14191 | -121.843 | 0.20142 | 0.14191 | -121.8933 | 0.13275 | 0.091552 | -0.050354 | -121.8475 | 0.13275 | 0.11444 | 0.17853 | -121.8887 | 0.064086 | 0.10986 | 0.21515 | -121.8155
3828.7031 | 122.1176 | -0.14648 | 121.8201 | -0.012589 | 0.012132 | 0.015199 | 0.002102 | 0.031868 | -0.0037769 | -0.046959 | -0.013123 | 0.0055563 | -0.013565 | -0.0011771 | 2.537 | 0.026214 | -0.013733 | -0.004578 | 0.059509 | 0.07782 | -0.009155 | 0.027466 | -0.064087 | -0.027466 | 0.10529 | -0.018311 | -0.068665 | -0.054932 | 0.059509 | 0 | 0.17395 | 0.082397 | -121.8292 | 0.14191 | 0.2243 | 0.14191 | -121.8338 | 0.20599 | 0.14648 | -121.8887 | 0.11902 | 0.12817 | -0.018311 | -121.875 | 0.13733 | 0.13275 | 0.20599 | -121.8842 | 0.077819 | 0.091552 | 0.25177 | -121.8201
3830.4062 | 122.1313 | -0.15106 | 121.8109 | -0.012589 | 0.011277 | 0.017976 | -0.00024778 | 0.033791 | -0.0069811 | -0.045677 | -0.013123 | 0.0057699 | -0.01506 | 0.00010471 | 2.5699 | 0.025786 | 0.022888 | 0.018311 | 0.054932 | 0.10071 | 0.004578 | 0.059509 | -0.054932 | -0.009155 | 0.11444 | -0.032043 | -0.059509 | -0.041199 | 0.073242 | 0.036621 | 0.21057 | 0.09613 | -121.8063 | 0.16937 | 0.25177 | 0.15564 | -121.788 | 0.2243 | 0.18768 | -121.8704 | 0.14191 | 0.11902 | -0.068664 | -121.8521 | 0.15564 | 0.17395 | 0.20599 | -121.8658 | 0.091553 | 0.10986 | 0.2655 | -121.7743
3832.1875 | 121.962 | -0.1831 | 121.875 | -0.0049592 | 0.018968 | 0.013918 | 0.00017942 | 0.032936 | 0.0058363 | -0.044822 | -0.028381 | 0.011751 | -0.014847 | 0.00095911 | 2.5455 | 0.022155 | 0 | -0.068665 | -0.013733 | 0.050354 | 0.027466 | 0.009155 | -0.082397 | -0.045776 | -0.018311 | -0.17395 | -0.036621 | -0.027466 | 0.036621 | -0.022888 | 0.19226 | 0.10071 | -121.8475 | 0.11444 | 0.23346 | 0.13275 | -121.875 | 0.21973 | 0.16022 | -121.9116 | 0.13733 | 0.009155 | -0.15106 | -121.9025 | 0.21057 | 0.1831 | 0.16937 | -121.9574 | 0.14648 | 0.15564 | 0.16479 | -121.8979
3833.9688 | 122.0856 | -0.15106 | 121.843 | -0.020218 | 0.014482 | 0.016054 | 0.003811 | 0.032082 | -0.0054859 | -0.04525 | -0.020752 | 0.0081199 | -0.01506 | -0.0026725 | 2.5214 | 0.025786 | 0.036621 | 0.082397 | 0.10986 | 0.11444 | -0.013733 | 0.032043 | -0.082397 | 0.032043 | 0.14191 | -0.013733 | -0.073242 | -0.064087 | 0.073242 | 0.013733 | 0.18311 | 0.068665 | -121.8567 | 0.23346 | 0.2655 | 0.19684 | -121.8063 | 0.2243 | 0.16479 | -121.9162 | 0.18311 | 0.13733 | -0.027466 | -121.907 | 0.13733 | 0.18768 | 0.26093 | -121.9254 | 0.07782 | 0.086975 | 0.29297 | -121.8292
3835.7656 | 122.1451 | -0.13733 | 121.8201 | -0.012589 | 0.014268 | 0.016267 | 0.0025292 | 0.031868 | -0.0029223 | -0.043968 | -0.0054932 | 0.0079063 | -0.015274 | -0.0022453 | 2.5269 | 0.025786 | 0.009155 | 0.022888 | 0.045776 | 0.091553 | 0 | 0.045776 | -0.068665 | -0.013733 | 0.10986 | -0.013733 | -0.064087 | -0.041199 | 0.073242 | 0.013733 | 0.18311 | 0.068664 | -121.8201 | 0.16022 | 0.22888 | 0.16022 | -121.8109 | 0.21057 | 0.15106 | -121.8842 | 0.1236 | 0.1236 | -0.027466 | -121.8613 | 0.13733 | 0.14648 | 0.18311 | -121.8887 | 0.073242 | 0.09613 | 0.24719 | -121.8063
3837.5469 | 122.1039 | -0.14191 | 121.8246 | -0.012589 | 0.0099953 | 0.017976 | 0.00082022 | 0.027809 | -0.0035633 | -0.043754 | -0.013123 | 0.0068381 | -0.014847 | -0.00010889 | 2.547 | 0.025359 | -0.013733 | 0.009155 | 0.050354 | 0.059509 | -0.009155 | 0.041199 | -0.059509 | -0.036621 | 0.041199 | -0.091553 | -0.054932 | -0.036621 | 0.050354 | -0.004578 | 0.18311 | 0.082398 | -121.8338 | 0.15106 | 0.20142 | 0.11902 | -121.8384 | 0.19226 | 0.13733 | -121.8796 | 0.10529 | 0.050354 | -0.086975 | -121.8613 | 0.13275 | 0.12817 | 0.19226 | -121.8842 | 0.086975 | 0.10529 | 0.18311 | -121.8292
3839.2812 | 122.0627 | -0.16022 | 121.875 | -0.027847 | 0.011491 | 0.016054 | -3.4178e-05 | 0.030159 | -0.0022815 | -0.046531 | 0.0021363 | 0.0085471 | -0.016129 | -0.0030997 | 2.4592 | 0.026214 | 0.036621 | 0.032043 | 0.073242 | 0.086975 | -0.027466 | 0.045776 | -0.068665 | -0.013733 | 0.068665 | -0.064087 | -0.07782 | -0.036621 | 0.068665 | 0.018311 | 0.20599 | 0.091552 | -121.9025 | 0.19226 | 0.24719 | 0.15564 | -121.8384 | 0.22888 | 0.17853 | -121.9528 | 0.14648 | 0.09613 | -0.082398 | -121.9116 | 0.13275 | 0.19684 | 0.23346 | -121.9437 | 0.082397 | 0.1236 | 0.22888 | -121.8567
3841.0781 | 122.0215 | -0.19226 | 121.9025 | -0.0049592 | 0.014482 | 0.016908 | 0.003811 | 0.030159 | -0.00035893 | -0.044609 | -0.0054932 | 0.0091879 | -0.01442 | -0.0024589 | 2.5949 | 0.023864 | 0.054932 | 0.050354 | 0.09613 | 0.1236 | -0.018311 | 0.045776 | -0.068665 | 0.009155 | 0.11444 | -0.032043 | -0.045776 | -0.022888 | 0.068665 | 0.009155 | 0.23804 | 0.1236 | -121.9208 | 0.24261 | 0.31586 | 0.19226 | -121.8475 | 0.26093 | 0.20142 | -121.9482 | 0.20142 | 0.16022 | -0.041198 | -121.9254 | 0.17395 | 0.24719 | 0.28839 | -121.9711 | 0.14648 | 0.16937 | 0.3067 | -121.8933
3842.875 | 122.1359 | -0.14191 | 121.8475 | -0.012589 | 0.0132 | 0.014345 | 0.00082022 | 0.031227 | 0.0032727 | -0.043113 | -0.0054932 | 0.01047 | -0.015488 | -0.00010889 | 2.5613 | 0.025146 | 0.009155 | -0.013733 | 0.036621 | 0.073242 | 0 | 0.027466 | -0.073242 | 0.045776 | 0.07782 | -0.059509 | -0.064087 | -0.045776 | 0.091553 | 0.013733 | 0.16937 | 0.068665 | -121.8475 | 0.12817 | 0.21515 | 0.14648 | -121.8384 | 0.23346 | 0.15564 | -121.9116 | 0.18768 | 0.082398 | -0.073242 | -121.8933 | 0.14191 | 0.15106 | 0.17853 | -121.9208 | 0.07782 | 0.096131 | 0.21973 | -121.8338
3844.5938 | 122.0352 | -0.18768 | 121.9162 | -0.012589 | 0.01555 | 0.018617 | 0.0012476 | 0.031227 | -0.00014533 | -0.045463 | -0.013123 | 0.011965 | -0.013992 | -0.0011771 | 2.447 | 0.024932 | -0.050354 | -0.050354 | -0.018311 | 0.027466 | 0.032043 | 0.018311 | -0.09613 | -0.07782 | 0.009155 | -0.15564 | -0.032043 | -0.027466 | 0.027466 | -0.009155 | 0.20599 | 0.091553 | -121.8842 | 0.13733 | 0.21515 | 0.1236 | -121.9666 | 0.21515 | 0.17853 | -121.9482 | 0.10986 | 0.032043 | -0.14649 | -121.9437 | 0.21973 | 0.13733 | 0.16937 | -122.0123 | 0.15564 | 0.16022 | 0.19684 | -121.9254
3846.375 | 122.0306 | -0.19684 | 121.9162 | 0.0026703 | 0.015336 | 0.015627 | 0.0040246 | 0.032723 | -0.00035893 | -0.043968 | -0.028381 | 0.010897 | -0.011002 | -0.0024589 | 2.5278 | 0.025573 | -0.041199 | -0.041199 | -0.018311 | 0.027466 | 0.027466 | 0.009155 | -0.086975 | -0.082397 | 0.027466 | -0.15106 | -0.022888 | -0.027466 | 0.018311 | -0.018311 | 0.20599 | 0.10986 | -121.8887 | 0.15564 | 0.2243 | 0.11444 | -121.9574 | 0.21515 | 0.17853 | -121.9391 | 0.11444 | 0.045776 | -0.13275 | -121.9437 | 0.2243 | 0.15564 | 0.17853 | -122.0032 | 0.17395 | 0.16937 | 0.2243 | -121.9345
3848.1719 | 122.1405 | -0.14648 | 121.8475 | -0.012589 | 0.0132 | 0.017122 | 0.0018884 | 0.029305 | -0.0014269 | -0.045677 | -0.0054932 | 0.0072653 | -0.015915 | 0.00031831 | 2.5041 | 0.028564 | -0.009155 | -0.009155 | 0.045776 | 0.068665 | -0.009155 | 0.036621 | -0.086975 | -0.041199 | 0.054932 | -0.073242 | -0.059509 | -0.041199 | 0.073242 | 0 | 0.18311 | 0.059509 | -121.8567 | 0.13733 | 0.21515 | 0.15564 | -121.8567 | 0.21973 | 0.14648 | -121.907 | 0.10529 | 0.073242 | -0.073242 | -121.8887 | 0.13733 | 0.13733 | 0.19226 | -121.9345 | 0.086975 | 0.10529 | 0.20142 | -121.8475
3849.9531 | 122.1634 | -0.14648 | 121.8704 | -0.012589 | 0.012132 | 0.017122 | 0.0025292 | 0.032936 | -0.0048449 | -0.043968 | -0.013123 | 0.0066245 | -0.015274 | -0.0011771 | 2.5323 | 0.024077 | 0.050354 | 0.082397 | 0.09613 | 0.11444 | 0 | 0.059509 | -0.059509 | 0.041199 | 0.16022 | 0.009155 | -0.064087 | -0.050354 | 0.091553 | 0.018311 | 0.20599 | 0.086975 | -121.8704 | 0.22888 | 0.26093 | 0.17395 | -121.8201 | 0.23804 | 0.16479 | -121.9345 | 0.18768 | 0.15564 | -0.009156 | -121.9208 | 0.14648 | 0.19684 | 0.24261 | -121.9299 | 0.082397 | 0.09613 | 0.3067 | -121.8521
3851.6719 | 122.0673 | -0.16937 | 121.8887 | -0.012589 | 0.014695 | 0.014558 | -0.0025976 | 0.032723 | 0.0054089 | -0.043327 | -0.020752 | 0.011324 | -0.016129 | 0.00095911 | 2.5419 | 0.024077 | 0.018311 | 0 | 0.004578 | 0.068665 | 0.036621 | 0.022888 | -0.09613 | 0.009155 | 0.068665 | -0.10529 | -0.041199 | -0.041199 | 0.054932 | -0.004578 | 0.19226 | 0.073243 | -121.8521 | 0.16937 | 0.23804 | 0.16479 | -121.8704 | 0.22431 | 0.16479 | -121.9299 | 0.17853 | 0.064087 | -0.10071 | -121.9299 | 0.20599 | 0.18768 | 0.17395 | -121.9849 | 0.12817 | 0.12817 | 0.23804 | -121.8933
3853.4531 | 122.1039 | -0.15106 | 121.8658 | -0.020218 | 0.0095681 | 0.016908 | -0.00046138 | 0.031868 | -0.0024951 | -0.042473 | -0.0054932 | 0.0061973 | -0.015488 | -0.0026725 | 2.4171 | 0.029418 | 0.009155 | 0.041199 | 0.054932 | 0.07782 | -0.004578 | 0.059509 | -0.073242 | -0.013733 | 0.064087 | -0.068665 | -0.059509 | -0.059509 | 0.059509 | 0.004578 | 0.21057 | 0.07782 | -121.8704 | 0.19226 | 0.22888 | 0.15106 | -121.8567 | 0.21057 | 0.15564 | -121.9254 | 0.13733 | 0.082397 | -0.073243 | -121.9254 | 0.14648 | 0.16022 | 0.20599 | -121.9391 | 0.091553 | 0.091553 | 0.21515 | -121.8613
3855.1875 | 122.0352 | -0.19684 | 121.8933 | -0.020218 | 0.016404 | 0.014558 | 0.001034 | 0.032509 | 0.0047681 | -0.041191 | -0.0054932 | 0.011751 | -0.01506 | -0.00010889 | 2.5293 | 0.025146 | -0.050354 | -0.10529 | -0.054932 | 0.032043 | 0.022888 | -0.004578 | -0.10986 | -0.059509 | -0.032043 | -0.1831 | -0.050354 | -0.022888 | 0.041199 | -0.018311 | 0.19226 | 0.086975 | -121.8704 | 0.091552 | 0.22888 | 0.14191 | -121.9437 | 0.23804 | 0.17853 | -121.9437 | 0.13733 | 0.013733 | -0.16479 | -121.9162 | 0.21973 | 0.14648 | 0.14191 | -122.0032 | 0.14648 | 0.17395 | 0.1648 | -121.9116
3856.9844 | 122.0398 | -0.16479 | 121.8842 | -0.0049592 | 0.017259 | 0.017549 | -0.00024778 | 0.032509 | 0.0047681 | -0.0429 | -0.020752 | 0.012179 | -0.016129 | -0.00074989 | 2.6418 | 0.025146 | 0.013733 | 0.009155 | 0.013733 | 0.073242 | 0.018311 | 0.027466 | -0.09613 | -0.013733 | 0.045776 | -0.11902 | -0.032043 | -0.004578 | 0.059509 | -0.018311 | 0.19226 | 0.068665 | -121.8658 | 0.17395 | 0.23804 | 0.16937 | -121.8704 | 0.2243 | 0.14648 | -121.9162 | 0.15106 | 0.045776 | -0.10071 | -121.8887 | 0.18311 | 0.17853 | 0.17853 | -121.9803 | 0.13275 | 0.16022 | 0.21057 | -121.9025
3858.7812 | 122.168 | -0.14648 | 121.8887 | -0.012589 | 0.014054 | 0.017336 | 0.0023156 | 0.028023 | -0.0063403 | -0.044395 | -0.013123 | 0.0083335 | -0.015488 | -0.00074989 | 2.5878 | 0.026427 | 0.027466 | 0.082397 | 0.086975 | 0.10986 | -0.009155 | 0.036621 | -0.068665 | 0.013733 | 0.15564 | 0.013733 | -0.082397 | -0.050354 | 0.082397 | 0.013733 | 0.18311 | 0.077819 | -121.8979 | 0.22888 | 0.25635 | 0.17853 | -121.8613 | 0.22888 | 0.16022 | -121.9711 | 0.16022 | 0.16022 | 0 | -121.9391 | 0.13733 | 0.17395 | 0.23346 | -121.9574 | 0.064087 | 0.09613 | 0.30212 | -121.875
3860.5781 | 122.113 | -0.16022 | 121.8887 | -0.012589 | 0.013627 | 0.016267 | 0.0025292 | 0.033577 | -0.0024951 | -0.04525 | -0.013123 | 0.0089743 | -0.015915 | -0.0013907 | 2.5391 | 0.025359 | 0.054932 | 0.036621 | 0.086975 | 0.09613 | -0.018311 | 0.059509 | -0.059509 | -0.009155 | 0.07782 | -0.032043 | -0.082397 | -0.045776 | 0.073242 | 0.004578 | 0.21973 | 0.10071 | -121.907 | 0.19684 | 0.25635 | 0.15564 | -121.8338 | 0.23346 | 0.16479 | -121.9711 | 0.15106 | 0.12817 | -0.036621 | -121.9345 | 0.14191 | 0.21515 | 0.24719 | -121.9482 | 0.07782 | 0.11444 | 0.23804 | -121.8842
3862.375 | 122.0947 | -0.17853 | 121.907 | -0.012589 | 0.014695 | 0.018617 | 0.0018884 | 0.032295 | -0.00057253 | -0.045036 | -0.028381 | 0.0064109 | -0.015488 | -0.0024589 | 2.5468 | 0.025786 | 0.054932 | 0.073242 | 0.091553 | 0.1236 | -0.004578 | 0.027466 | -0.064087 | 0.018311 | 0.14648 | -0.022888 | -0.068665 | -0.059509 | 0.064087 | 0.004578 | 0.20599 | 0.11444 | -121.9116 | 0.25177 | 0.30212 | 0.18768 | -121.8521 | 0.24261 | 0.18311 | -121.9757 | 0.19684 | 0.15564 | -0.027466 | -121.9666 | 0.17395 | 0.23346 | 0.27008 | -121.9711 | 0.10986 | 0.11902 | 0.32501 | -121.9025
3864.0938 | 122.1863 | -0.13275 | 121.9116 | -0.0049592 | 0.0078591 | 0.016908 | -3.4178e-05 | 0.032082 | -0.0031359 | -0.044609 | -0.0054932 | 0.0049155 | -0.016983 | -0.00053629 | 2.6087 | 0.026427 | 0.004578 | 0.013733 | 0.050354 | 0.086975 | 0.004578 | 0.041199 | -0.064087 | -0.022888 | 0.09613 | -0.036621 | -0.073242 | -0.050354 | 0.07782 | 0.027466 | 0.17395 | 0.068664 | -121.907 | 0.14648 | 0.21973 | 0.15106 | -121.907 | 0.21057 | 0.16022 | -121.9849 | 0.10986 | 0.09613 | -0.064087 | -121.962 | 0.13733 | 0.13733 | 0.18311 | -121.9757 | 0.059509 | 0.082397 | 0.22888 | -121.8842
3865.8906 | 122.1039 | -0.16937 | 121.9208 | -0.012589 | 0.015122 | 0.013918 | -0.0025976 | 0.030159 | 0.0086133 | -0.045036 | -0.0054932 | 0.010683 | -0.015274 | 0.00031831 | 2.5169 | 0.02365 | -0.041199 | -0.091553 | -0.054932 | 0.032043 | 0.041199 | 0.013733 | -0.10986 | -0.073242 | -0.036621 | -0.16479 | -0.041199 | -0.027466 | 0.041199 | -0.027466 | 0.18311 | 0.05951 | -121.8796 | 0.07782 | 0.20142 | 0.14191 | -121.962 | 0.21057 | 0.14191 | -121.962 | 0.096131 | 0.004578 | -0.13733 | -121.9482 | 0.21057 | 0.12817 | 0.11444 | -122.0306 | 0.12817 | 0.14191 | 0.13275 | -121.9482
3867.6719 | 122.1542 | -0.15106 | 121.9162 | -0.0049592 | 0.013841 | 0.016695 | 0.0014612 | 0.030586 | -0.0016405 | -0.044182 | -0.020752 | 0.0066245 | -0.014847 | -0.0020315 | 2.5335 | 0.024932 | 0.054932 | 0.09613 | 0.10529 | 0.11444 | -0.022888 | 0.041199 | -0.064087 | 0.036621 | 0.15106 | 0 | -0.073242 | -0.054932 | 0.086975 | 0.009155 | 0.19226 | 0.086975 | -121.9391 | 0.24719 | 0.2655 | 0.17853 | -121.8613 | 0.23804 | 0.16022 | -121.9894 | 0.18768 | 0.15106 | -0.009155 | -121.9711 | 0.12817 | 0.20599 | 0.25635 | -121.9803 | 0.07782 | 0.09613 | 0.30212 | -121.907
3869.4531 | 122.0673 | -0.20599 | 121.9666 | -0.0049592 | 0.017045 | 0.015627 | 0.0029566 | 0.031014 | 0.00092287 | -0.046104 | -0.013123 | 0.0087607 | -0.013565 | -0.00074989 | 2.4951 | 0.026427 | -0.054932 | -0.082397 | -0.022888 | 0.027466 | 0.018311 | 0.004578 | -0.11444 | -0.082397 | 0.009155 | -0.14648 | -0.027466 | -0.009155 | 0.045776 | -0.032043 | 0.21057 | 0.091553 | -121.9482 | 0.1236 | 0.23346 | 0.14191 | -122.0215 | 0.25177 | 0.17395 | -121.994 | 0.1236 | 0.05951 | -0.11444 | -121.9757 | 0.22431 | 0.15106 | 0.18311 | -122.081 | 0.17853 | 0.19684 | 0.21515 | -121.9986
3871.1719 | 122.1039 | -0.17853 | 121.9208 | -0.012589 | 0.015977 | 0.01349 | 0.0057336 | 0.031227 | 0.0034863 | -0.044182 | -0.020752 | 0.010897 | -0.01207 | -0.0013907 | 2.5756 | 0.023009 | -0.032043 | -0.064087 | -0.041199 | 0.041199 | 0.036621 | 0 | -0.10529 | -0.064087 | 0.032043 | -0.13733 | -0.032043 | 0.013733 | 0.032043 | -0.013733 | 0.17853 | 0.073242 | -121.8842 | 0.11444 | 0.21973 | 0.14649 | -121.9528 | 0.21057 | 0.16479 | -121.9528 | 0.11444 | 0.041199 | -0.1236 | -121.907 | 0.21515 | 0.14648 | 0.13733 | -122.0261 | 0.14648 | 0.19226 | 0.21057 | -121.9345
3872.9531 | 122.2046 | -0.14648 | 121.9025 | -0.020218 | 0.010209 | 0.015413 | 0.0018884 | 0.035073 | -0.0065539 | -0.046104 | -0.013123 | 0.0057699 | -0.014847 | 0.0018137 | 2.5594 | 0.025573 | -0.013733 | 0.013733 | 0.059509 | 0.09613 | 0 | 0.036621 | -0.086975 | -0.004578 | 0.11902 | -0.027466 | -0.07782 | -0.059509 | 0.068665 | 0.022888 | 0.18311 | 0.059509 | -121.9025 | 0.16022 | 0.24261 | 0.1831 | -121.9162 | 0.21515 | 0.16937 | -121.9803 | 0.14191 | 0.11902 | -0.050354 | -121.962 | 0.14648 | 0.13275 | 0.20599 | -121.9894 | 0.068664 | 0.086975 | 0.2655 | -121.8796
3874.75 | 122.113 | -0.1831 | 121.9574 | -0.012589 | 0.018113 | 0.014772 | 0.0018884 | 0.032509 | 0.0024183 | -0.0429 | 0.0021363 | 0.010683 | -0.013565 | 0.00031831 | 2.6322 | 0.024932 | -0.041199 | -0.059509 | -0.032043 | 0.041199 | 0.036621 | 0.009155 | -0.11444 | -0.045776 | 0.022888 | -0.13275 | -0.041199 | -0.027466 | 0.041199 | -0.032043 | 0.19226 | 0.068664 | -121.9208 | 0.1236 | 0.2243 | 0.15564 | -121.9986 | 0.2243 | 0.15106 | -121.9986 | 0.13733 | 0.050354 | -0.10071 | -121.9849 | 0.21973 | 0.14191 | 0.15106 | -122.0718 | 0.14191 | 0.15564 | 0.20599 | -121.9894
3876.4688 | 122.113 | -0.20142 | 121.9666 | -0.012589 | 0.01555 | 0.016054 | 0.0033838 | 0.030586 | 0.0013501 | -0.043968 | -0.013123 | 0.01047 | -0.013351 | 0.00031831 | 2.607 | 0.025573 | -0.073242 | -0.059509 | -0.041199 | 0.032043 | 0.032043 | 0.009155 | -0.12817 | -0.068665 | 0 | -0.16022 | -0.018311 | -0.009155 | 0.036621 | -0.027466 | 0.21057 | 0.073242 | -121.9345 | 0.14191 | 0.23346 | 0.16022 | -122.0398 | 0.23804 | 0.17395 | -121.9849 | 0.13275 | 0.041199 | -0.13275 | -121.9757 | 0.23346 | 0.12817 | 0.16022 | -122.0947 | 0.18311 | 0.19226 | 0.20142 | -121.994
3878.2656 | 122.1268 | -0.1831 | 121.9666 | -0.020218 | 0.015336 | 0.013918 | 0.001034 | 0.032509 | 0.0030591 | -0.044609 | -0.013123 | 0.010256 | -0.014633 | 0.00010471 | 2.4156 | 0.024718 | -0.054932 | -0.059509 | -0.032043 | 0.036621 | 0.027466 | 0.004578 | -0.10529 | -0.068665 | 0.027466 | -0.14191 | -0.032043 | -0.018311 | 0.041199 | -0.018311 | 0.18768 | 0.077819 | -121.9391 | 0.1236 | 0.21973 | 0.14191 | -122.0215 | 0.2243 | 0.16479 | -121.9986 | 0.11444 | 0.041198 | -0.1236 | -121.9849 | 0.21057 | 0.12817 | 0.15106 | -122.0718 | 0.15106 | 0.16479 | 0.21057 | -121.9849
3880 | 122.0718 | -0.17853 | 121.9666 | -0.012589 | 0.017686 | 0.014558 | 0.00060662 | 0.032082 | 0.0024183 | -0.042686 | -0.013123 | 0.01047 | -0.015488 | -0.00010889 | 2.6357 | 0.025786 | 0.018311 | -0.004578 | 0.013733 | 0.073242 | 0.018311 | 0.009155 | -0.07782 | -0.027466 | 0.036621 | -0.13275 | -0.054932 | -0.013733 | 0.045776 | -0.009155 | 0.18768 | 0.10071 | -121.9482 | 0.17395 | 0.25177 | 0.15106 | -121.9482 | 0.2243 | 0.16937 | -122.0215 | 0.15106 | 0.045777 | -0.1236 | -121.9803 | 0.19684 | 0.19684 | 0.19226 | -122.0444 | 0.1236 | 0.16479 | 0.21515 | -121.9757
3881.7812 | 122.2092 | -0.14191 | 121.9437 | -0.0049592 | 0.012559 | 0.015413 | 0.00082022 | 0.029732 | -0.00099973 | -0.043968 | -0.013123 | 0.0072653 | -0.016769 | -0.0016043 | 2.4829 | 0.025573 | 0.004578 | 0.004578 | 0.045776 | 0.082397 | 0 | 0.050354 | -0.082397 | 0.027466 | 0.10986 | -0.045776 | -0.082397 | -0.050354 | 0.068665 | 0.018311 | 0.19226 | 0.05951 | -121.9437 | 0.14649 | 0.2243 | 0.16479 | -121.9391 | 0.21057 | 0.16022 | -122.0261 | 0.16937 | 0.096131 | -0.064087 | -121.994 | 0.14191 | 0.14649 | 0.18768 | -122.0261 | 0.05951 | 0.091553 | 0.25177 | -121.9254
3883.5625 | 122.168 | -0.15564 | 121.9574 | -0.020218 | 0.016618 | 0.016908 | 0.0044518 | 0.033577 | -0.0048449 | -0.043754 | -0.0054932 | 0.0068381 | -0.015274 | -0.00053629 | 2.5523 | 0.026641 | 0.022888 | 0.091553 | 0.11444 | 0.09613 | -0.004578 | 0.054932 | -0.07782 | 0.018311 | 0.16022 | -0.004578 | -0.07782 | -0.054932 | 0.064087 | 0.004578 | 0.21057 | 0.07782 | -121.962 | 0.24719 | 0.25177 | 0.17395 | -121.9345 | 0.21973 | 0.16022 | -122.0352 | 0.17395 | 0.15106 | -0.009156 | -122.0123 | 0.15106 | 0.17853 | 0.27008 | -122.0352 | 0.07782 | 0.10071 | 0.31586 | -121.9528
3885.375 | 122.1039 | -0.17853 | 121.962 | -0.012589 | 0.015977 | 0.013277 | 0.0031702 | 0.030586 | 0.0043409 | -0.044395 | 0.0021363 | 0.012819 | -0.013779 | 0.0013863 | 2.6299 | 0.025146 | -0.068665 | -0.10986 | -0.068665 | 0.013733 | 0.032043 | 0.013733 | -0.11902 | -0.086975 | -0.027466 | -0.17395 | -0.022888 | -0.009155 | 0.050354 | -0.027466 | 0.19226 | 0.059509 | -121.9299 | 0.068665 | 0.19226 | 0.13275 | -122.0306 | 0.22888 | 0.15106 | -121.9849 | 0.091553 | 0.004578 | -0.14648 | -121.9711 | 0.21057 | 0.10986 | 0.10986 | -122.081 | 0.15564 | 0.16937 | 0.15106 | -121.9894
3887.0938 | 122.1313 | -0.16479 | 121.9666 | -0.012589 | 0.018968 | 0.015199 | 0.0014612 | 0.032295 | 0.0022047 | -0.043968 | -0.013123 | 0.0094015 | -0.014206 | -0.00096349 | 2.641 | 0.024505 | -0.036621 | -0.041199 | 0 | 0.059509 | 0.027466 | 0.013733 | -0.086975 | -0.050354 | 0.054932 | -0.10986 | -0.041199 | -0.041199 | 0.054932 | -0.013733 | 0.17853 | 0.07782 | -121.9391 | 0.1236 | 0.2243 | 0.14648 | -122.0032 | 0.21973 | 0.15106 | -122.0078 | 0.11444 | 0.054932 | -0.09613 | -122.0078 | 0.19226 | 0.12817 | 0.16479 | -122.0535 | 0.1236 | 0.1236 | 0.21973 | -121.9803
3888.875 | 122.0947 | -0.18768 | 121.9574 | -0.012589 | 0.017259 | 0.018617 | 0.0023156 | 0.032082 | -0.00099973 | -0.044395 | -0.0054932 | 0.0081199 | -0.014847 | -0.0018179 | 2.6151 | 0.027068 | -0.036621 | -0.018311 | 0.004578 | 0.059509 | 0.018311 | 0.027466 | -0.091553 | -0.10071 | 0.027466 | -0.11902 | -0.050354 | -0.018311 | 0.045776 | -0.018311 | 0.21515 | 0.09613 | -121.9391 | 0.16937 | 0.24719 | 0.15106 | -121.994 | 0.23346 | 0.16937 | -122.0078 | 0.086975 | 0.068664 | -0.10071 | -121.9757 | 0.20599 | 0.15106 | 0.19226 | -122.049 | 0.13733 | 0.16937 | 0.21515 | -121.9757
3890.6562 | 122.1542 | -0.15564 | 121.9528 | -0.0049592 | 0.0097817 | 0.018617 | -0.0015296 | 0.029732 | -0.0033495 | -0.044395 | -0.020752 | 0.0066245 | -0.015915 | -0.00096349 | 2.6367 | 0.028991 | 0.022888 | 0.086975 | 0.09613 | 0.10986 | -0.022888 | 0.032043 | -0.064087 | 0.009155 | 0.14648 | -0.013733 | -0.068665 | -0.068665 | 0.068665 | -0.004578 | 0.18768 | 0.091553 | -121.9757 | 0.24261 | 0.2655 | 0.17395 | -121.9299 | 0.22431 | 0.15106 | -122.0215 | 0.16479 | 0.14191 | -0.009155 | -122.0215 | 0.13275 | 0.17853 | 0.25177 | -122.0169 | 0.086975 | 0.086975 | 0.30212 | -121.9574
3892.375 | 122.2321 | -0.16022 | 121.9345 | -0.020218 | 0.013413 | 0.017549 | -0.00046138 | 0.031014 | -0.0035633 | -0.044609 | -0.020752 | 0.0051291 | -0.014633 | -0.0028861 | 2.5412 | 0.027495 | -0.004578 | 0.009155 | 0.054932 | 0.073242 | 0.009155 | 0.054932 | -0.073242 | -0.027466 | 0.09613 | -0.032043 | -0.059509 | -0.022888 | 0.064087 | 0.004578 | 0.21515 | 0.086975 | -121.9254 | 0.16937 | 0.23346 | 0.14648 | -121.9391 | 0.2243 | 0.16479 | -121.994 | 0.13275 | 0.12817 | -0.036621 | -121.9574 | 0.16937 | 0.15564 | 0.21515 | -122.0078 | 0.10071 | 0.13733 | 0.25635 | -121.9299
3894.1719 | 122.1725 | -0.15106 | 121.9437 | -0.012589 | 0.014482 | 0.013704 | 0.0014612 | 0.031227 | 0.0034863 | -0.043113 | -0.0054932 | 0.0087607 | -0.015701 | 0.0018137 | 2.6342 | 0.022368 | -0.018311 | -0.09613 | -0.032043 | 0.032043 | 0.036621 | 0.004578 | -0.10529 | -0.086975 | -0.041199 | -0.16022 | -0.036621 | -0.018311 | 0.059509 | -0.018311 | 0.15564 | 0.045776 | -121.907 | 0.054932 | 0.18311 | 0.13733 | -121.962 | 0.21057 | 0.13275 | -121.9803 | 0.064087 | -0.009155 | -0.14191 | -121.962 | 0.18768 | 0.13275 | 0.11902 | -122.049 | 0.11444 | 0.13275 | 0.10986 | -121.962
3895.9062 | 122.1771 | -0.17395 | 121.9757 | -0.0049592 | 0.013413 | 0.017549 | 0.0044518 | 0.032936 | -0.0031359 | -0.046104 | -0.0054932 | 0.0074789 | -0.016983 | -0.0018179 | 2.6222 | 0.027282 | 0.045776 | 0.07782 | 0.10071 | 0.11902 | -0.004578 | 0.050354 | -0.059509 | 0.004578 | 0.16022 | -0.018311 | -0.091553 | -0.054932 | 0.07782 | 0.013733 | 0.2243 | 0.11444 | -121.9803 | 0.25177 | 0.29297 | 0.17853 | -121.9299 | 0.25177 | 0.18768 | -122.0673 | 0.17853 | 0.15564 | -0.032044 | -122.0306 | 0.16937 | 0.21973 | 0.27466 | -122.0352 | 0.082397 | 0.11902 | 0.33417 | -121.962
3897.6719 | 122.2366 | -0.11902 | 121.9482 | -0.0049592 | 0.010636 | 0.01584 | -0.00046138 | 0.032082 | 0.00070927 | -0.041832 | -0.013123 | 0.0083335 | -0.016769 | 0.00010471 | 2.5662 | 0.024077 | 0.032043 | 0.013733 | 0.073242 | 0.10071 | -0.009155 | 0.045776 | -0.073242 | 0.018311 | 0.091553 | -0.041199 | -0.068665 | -0.045776 | 0.09613 | 0.013733 | 0.16479 | 0.045777 | -121.9574 | 0.13275 | 0.21973 | 0.17395 | -121.9162 | 0.21515 | 0.13275 | -122.0169 | 0.13733 | 0.07782 | -0.054932 | -121.994 | 0.10986 | 0.15106 | 0.19226 | -122.0215 | 0.050354 | 0.073243 | 0.21057 | -121.9345
3899.3906 | 122.1497 | -0.18768 | 121.9986 | -0.0049592 | 0.016191 | 0.014558 | 0.0046656 | 0.032509 | -0.00057253 | -0.044395 | -0.020752 | 0.0047019 | -0.014206 | 0.00031831 | 2.591 | 0.025359 | 0.045776 | 0.07782 | 0.11902 | 0.11902 | -0.018311 | 0.073242 | -0.045776 | 0.018311 | 0.13275 | -0.036621 | -0.068665 | -0.050354 | 0.068665 | 0.022888 | 0.26092 | 0.14191 | -122.0169 | 0.2655 | 0.3067 | 0.16479 | -121.9528 | 0.25635 | 0.21057 | -122.0673 | 0.20599 | 0.15106 | -0.059509 | -122.049 | 0.16937 | 0.23346 | 0.3067 | -122.0444 | 0.11902 | 0.13733 | 0.32043 | -121.9757
3901.1719 | 122.1725 | -0.1831 | 121.9894 | -0.020218 | 0.017472 | 0.015413 | 0.0027428 | 0.0308 | 0.00049567 | -0.045036 | -0.0054932 | 0.011751 | -0.014847 | 0.0020273 | 2.6183 | 0.024291 | -0.027466 | -0.064087 | -0.032043 | 0.059509 | 0.032043 | -0.004578 | -0.10529 | -0.045776 | 0.027466 | -0.13275 | -0.041199 | -0.013733 | 0.036621 | -0.032043 | 0.17853 | 0.077819 | -121.9574 | 0.11902 | 0.24261 | 0.16479 | -122.0169 | 0.21973 | 0.15106 | -122.0306 | 0.13733 | 0.050354 | -0.10071 | -122.0032 | 0.21515 | 0.15564 | 0.15106 | -122.0947 | 0.14191 | 0.16937 | 0.21057 | -122.0215
3902.9531 | 122.2412 | -0.15106 | 121.9711 | -0.0049592 | 0.012132 | 0.019045 | 0.00039302 | 0.029946 | -0.0042041 | -0.043113 | -0.0054932 | 0.0059837 | -0.017838 | -0.0016043 | 2.6286 | 0.026855 | -0.022888 | 0.004578 | 0.036621 | 0.064087 | 0.004578 | 0.050354 | -0.068665 | -0.041199 | 0.068665 | -0.073242 | -0.082397 | -0.036621 | 0.059509 | 0.009155 | 0.20142 | 0.082397 | -121.9666 | 0.15564 | 0.21515 | 0.13275 | -121.994 | 0.21057 | 0.16022 | -122.0535 | 0.10986 | 0.07782 | -0.082397 | -122.0078 | 0.15564 | 0.12817 | 0.18768 | -122.0398 | 0.068665 | 0.11444 | 0.21973 | -121.962
3904.7344 | 122.1268 | -0.16479 | 121.9803 | -0.012589 | 0.020036 | 0.014772 | 0.0025292 | 0.033577 | 0.0039135 | -0.042473 | -0.013123 | 0.013033 | -0.011429 | -0.00074989 | 2.6756 | 0.023009 | 0.041199 | -0.004578 | 0.018311 | 0.07782 | 0.041199 | 0 | -0.086975 | -0.032043 | 0.050354 | -0.13733 | -0.027466 | -0.018311 | 0.041199 | -0.009155 | 0.16479 | 0.07782 | -121.9391 | 0.16022 | 0.24261 | 0.16479 | -121.9391 | 0.20599 | 0.15564 | -122.0078 | 0.13275 | 0.027466 | -0.12817 | -121.9986 | 0.20599 | 0.20599 | 0.18311 | -122.0673 | 0.13733 | 0.14648 | 0.21515 | -121.9894
3906.4531 | 122.2137 | -0.11444 | 121.9254 | -0.020218 | 0.010423 | 0.015627 | -0.0011024 | 0.0308 | 0.0011365 | -0.040336 | 0.0021363 | 0.0070517 | -0.017624 | -0.00074989 | 2.6498 | 0.027068 | 0.041199 | 0.059509 | 0.07782 | 0.11902 | -0.022888 | 0.073242 | -0.068665 | 0.045776 | 0.10529 | -0.027466 | -0.091553 | -0.054932 | 0.064087 | 0.022888 | 0.18768 | 0.045776 | -121.9482 | 0.17395 | 0.23346 | 0.18768 | -121.8842 | 0.17853 | 0.13733 | -122.0169 | 0.16022 | 0.086975 | -0.050354 | -121.9803 | 0.091553 | 0.15564 | 0.19226 | -121.994 | 0.022888 | 0.059509 | 0.21973 | -121.9025
3908.2656 | 122.1268 | -0.19684 | 122.0032 | -0.012589 | 0.013627 | 0.019685 | 0.0014612 | 0.0308 | -0.0014269 | -0.043968 | -0.013123 | 0.0068381 | -0.013565 | -0.0020315 | 2.4846 | 0.026855 | -0.032043 | -0.009155 | 0 | 0.041199 | 0.022888 | 0.013733 | -0.091553 | -0.091553 | 0.022888 | -0.12817 | -0.022888 | 0 | 0.036621 | -0.041199 | 0.21057 | 0.10529 | -121.9803 | 0.18768 | 0.23804 | 0.13275 | -122.0352 | 0.23346 | 0.15564 | -122.0261 | 0.10529 | 0.068664 | -0.086975 | -122.0032 | 0.21973 | 0.1648 | 0.19684 | -122.0947 | 0.17395 | 0.19684 | 0.21973 | -122.0444
3909.9844 | 122.2549 | -0.13275 | 121.9757 | -0.012589 | 0.014482 | 0.017549 | 0.0046656 | 0.032723 | -0.0044177 | -0.047386 | -0.013123 | 0.0064109 | -0.014633 | -0.00074989 | 2.51 | 0.026214 | 0.045776 | 0.073242 | 0.10071 | 0.11902 | 0.004578 | 0.064087 | -0.068665 | 0.018311 | 0.16022 | 0.004578 | -0.07782 | -0.059509 | 0.07782 | 0.009155 | 0.19684 | 0.064086 | -121.9711 | 0.20599 | 0.25177 | 0.18768 | -121.9299 | 0.21057 | 0.14191 | -122.0535 | 0.15106 | 0.13733 | -0.004577 | -122.0352 | 0.13733 | 0.17853 | 0.23346 | -122.0444 | 0.054931 | 0.073242 | 0.29297 | -121.9666
3911.7656 | 122.2458 | -0.15106 | 121.9894 | -0.012589 | 0.011704 | 0.016695 | 0.0025292 | 0.029946 | -0.0029223 | -0.043968 | -0.013123 | 0.0085471 | -0.016983 | 0.00053191 | 2.5656 | 0.025786 | -0.009155 | -0.018311 | 0.045776 | 0.064087 | 0.009155 | 0.045776 | -0.073242 | -0.041199 | 0.064087 | -0.064087 | -0.064087 | -0.036621 | 0.068665 | 0 | 0.19684 | 0.07782 | -121.9803 | 0.13275 | 0.21515 | 0.13733 | -121.9986 | 0.21973 | 0.15106 | -122.0535 | 0.10986 | 0.086975 | -0.064087 | -122.0261 | 0.16022 | 0.14191 | 0.19684 | -122.0627 | 0.086975 | 0.11444 | 0.21515 | -121.9894
3913.5469 | 122.2687 | -0.12817 | 121.9711 | -0.012589 | 0.020036 | 0.014131 | 0.0025292 | 0.027809 | 0.0045545 | -0.041191 | -0.013123 | 0.012606 | -0.012711 | 0.0013863 | 2.6222 | 0.024718 | -0.004578 | -0.068665 | 0 | 0.041199 | 0.013733 | 0.009155 | -0.07782 | -0.018311 | 0.018311 | -0.10529 | -0.041199 | -0.018311 | 0.059509 | 0.013733 | 0.13733 | 0.050354 | -121.9574 | 0.059509 | 0.16937 | 0.11902 | -121.9757 | 0.18768 | 0.14191 | -122.0123 | 0.10986 | 0.022888 | -0.11902 | -121.9894 | 0.14191 | 0.1236 | 0.12817 | -122.049 | 0.086975 | 0.10986 | 0.14649 | -121.9574
3915.3594 | 122.2549 | -0.1236 | 122.0032 | -0.020218 | 0.014054 | 0.017336 | 0.0018884 | 0.030586 | -0.0031359 | -0.044822 | -0.020752 | 0.0051291 | -0.013779 | -0.0016043 | 2.5934 | 0.024291 | 0.045776 | 0.082397 | 0.10071 | 0.10986 | -0.018311 | 0.032043 | -0.059509 | 0.041199 | 0.14191 | 0 | -0.082397 | -0.054932 | 0.068665 | 0.018311 | 0.15564 | 0.064087 | -122.0215 | 0.20599 | 0.23346 | 0.16937 | -121.9574 | 0.19226 | 0.14191 | -122.0856 | 0.16479 | 0.1236 | -0.018311 | -122.0581 | 0.10528 | 0.16937 | 0.2243 | -122.0627 | 0.041199 | 0.068664 | 0.2655 | -121.9849
3917.1562 | 122.2046 | -0.15106 | 122.0215 | -0.0049592 | 0.014695 | 0.018617 | 0.0031702 | 0.031441 | 0.00028207 | -0.0429 | -0.0054932 | 0.0074789 | -0.013565 | -0.0016043 | 2.5872 | 0.022796 | 0.054932 | 0.086975 | 0.10986 | 0.11444 | -0.022888 | 0.059509 | -0.054932 | 0.022888 | 0.15106 | -0.022888 | -0.059509 | -0.041199 | 0.086975 | 0.013733 | 0.21057 | 0.09613 | -122.0444 | 0.23804 | 0.2655 | 0.16937 | -121.9666 | 0.23804 | 0.16479 | -122.081 | 0.17395 | 0.12817 | -0.036621 | -122.0627 | 0.12817 | 0.20599 | 0.26093 | -122.0764 | 0.091553 | 0.10986 | 0.30212 | -122.0078
3918.9375 | 122.2641 | -0.14191 | 121.9986 | -0.012589 | 0.016618 | 0.014345 | 0.00082022 | 0.029946 | 0.0043409 | -0.042473 | -0.013123 | 0.0096151 | -0.014633 | 0.0016001 | 2.5532 | 0.024077 | 0.054932 | 0.050354 | 0.073242 | 0.10986 | -0.009155 | 0.059509 | -0.041199 | 0.059509 | 0.10071 | -0.041199 | -0.07782 | -0.050354 | 0.086975 | 0.027466 | 0.20142 | 0.10071 | -122.0078 | 0.19226 | 0.25177 | 0.15106 | -121.9437 | 0.22888 | 0.16937 | -122.0764 | 0.20142 | 0.10071 | -0.068665 | -122.049 | 0.13275 | 0.19684 | 0.21515 | -122.0398 | 0.064087 | 0.091553 | 0.24262 | -121.9711
3920.6562 | 122.1497 | -0.16937 | 122.0215 | -0.012589 | 0.018754 | 0.016267 | -0.00067498 | 0.033791 | 0.0062635 | -0.042045 | -0.013123 | 0.011324 | -0.015701 | -0.00074989 | 2.6542 | 0.024291 | 0.027466 | 0.018311 | 0.009155 | 0.086975 | 0.018311 | 0.022888 | -0.10529 | 0.009155 | 0.064087 | -0.11444 | -0.022888 | -0.022888 | 0.054932 | 0.004578 | 0.19226 | 0.064087 | -122.0032 | 0.18768 | 0.25635 | 0.19226 | -121.994 | 0.22431 | 0.17395 | -122.0444 | 0.17853 | 0.054932 | -0.11902 | -122.0444 | 0.18768 | 0.19684 | 0.17853 | -122.1268 | 0.14649 | 0.14649 | 0.23346 | -122.0169
3922.4375 | 122.1313 | -0.18768 | 122.0169 | -0.0049592 | 0.014268 | 0.015627 | -0.0021704 | 0.030586 | 0.0039135 | -0.041191 | -0.013123 | 0.011324 | -0.013992 | -0.0022453 | 2.6681 | 0.025146 | 0.045776 | 0.004578 | 0.018311 | 0.068665 | 0.041199 | 0.013733 | -0.086975 | -0.004578 | 0.045776 | -0.1236 | -0.036621 | -0.027466 | 0.041199 | -0.004578 | 0.20142 | 0.10071 | -121.9757 | 0.19226 | 0.25635 | 0.15564 | -121.9711 | 0.22888 | 0.1831 | -122.0535 | 0.1831 | 0.064087 | -0.11902 | -122.0444 | 0.22888 | 0.23346 | 0.20599 | -122.1039 | 0.15106 | 0.16022 | 0.23346 | -122.0215
3924.1562 | 122.2321 | -0.16022 | 122.0123 | -0.012589 | 0.013627 | 0.018831 | 0.0014612 | 0.032082 | -0.0059131 | -0.042045 | -0.013123 | 0.0059837 | -0.01506 | -0.0020315 | 2.6579 | 0.027709 | 0.032043 | 0.091553 | 0.091553 | 0.10986 | -0.022888 | 0.059509 | -0.064087 | 0.022888 | 0.15106 | -0.004578 | -0.091553 | -0.045776 | 0.07782 | 0.004578 | 0.21973 | 0.09613 | -122.0352 | 0.25177 | 0.27008 | 0.17395 | -121.9803 | 0.23804 | 0.16479 | -122.1039 | 0.1831 | 0.15564 | -0.009156 | -122.0581 | 0.13733 | 0.19226 | 0.25177 | -122.0764 | 0.068664 | 0.11444 | 0.31128 | -122.0078
3925.9375 | 122.1542 | -0.18768 | 122.0123 | -0.020218 | 0.015763 | 0.015627 | -0.0011024 | 0.032509 | 0.0056225 | -0.043754 | 0.0021363 | 0.010683 | -0.013779 | -0.0011771 | 2.5201 | 0.025786 | 0.018311 | -0.013733 | 0.009155 | 0.07782 | 0.009155 | 0.027466 | -0.091553 | -0.027466 | 0.036621 | -0.1236 | -0.036621 | -0.013733 | 0.041199 | -0.004578 | 0.21515 | 0.09613 | -122.0032 | 0.17395 | 0.2655 | 0.16937 | -121.994 | 0.22888 | 0.1831 | -122.0489 | 0.16022 | 0.064087 | -0.11902 | -122.0261 | 0.19684 | 0.20599 | 0.19684 | -122.1039 | 0.15106 | 0.17395 | 0.2243 | -122.0169
3927.7188 | 122.2092 | -0.16022 | 122.0123 | -0.020218 | 0.018113 | 0.01584 | 0.0053064 | 0.0308 | 0.0026319 | -0.044182 | -0.020752 | 0.010256 | -0.012497 | -0.00074989 | 2.6119 | 0.025786 | -0.027466 | -0.050354 | -0.004578 | 0.068665 | 0.022888 | 0.013733 | -0.10071 | -0.027466 | 0.041199 | -0.10986 | -0.027466 | -0.009155 | 0.045776 | -0.004578 | 0.17395 | 0.059509 | -121.9894 | 0.10986 | 0.22888 | 0.16937 | -122.0398 | 0.20599 | 0.15564 | -122.0398 | 0.13275 | 0.050354 | -0.10529 | -122.0215 | 0.1831 | 0.13275 | 0.15564 | -122.113 | 0.13275 | 0.15106 | 0.20142 | -122.0169
3929.4375 | 122.1909 | -0.1831 | 122.0032 | -0.020218 | 0.016191 | 0.01584 | -0.0015296 | 0.032082 | 0.0034863 | -0.04055 | -0.0054932 | 0.0091879 | -0.015274 | -0.0011771 | 2.5976 | 0.025146 | 0.013733 | -0.004578 | 0.013733 | 0.082397 | 0.018311 | 0.013733 | -0.09613 | -0.018311 | 0.059509 | -0.086975 | -0.045776 | -0.009155 | 0.064087 | -0.018311 | 0.19684 | 0.086975 | -121.9849 | 0.17853 | 0.2655 | 0.17853 | -121.9894 | 0.24719 | 0.16479 | -122.049 | 0.16479 | 0.09613 | -0.068664 | -122.0123 | 0.20142 | 0.19684 | 0.19684 | -122.0993 | 0.13733 | 0.17395 | 0.24261 | -122.0215
3931.2344 | 122.1863 | -0.17853 | 122.0352 | -0.012589 | 0.014909 | 0.016695 | 0.00552 | 0.034218 | -0.0014269 | -0.045036 | -0.0054932 | 0.0064109 | -0.012283 | -0.0011771 | 2.5299 | 0.027282 | -0.068665 | -0.045776 | -0.022888 | 0.032043 | 0.022888 | 0.009155 | -0.082397 | -0.11444 | 0.027466 | -0.15106 | -0.027466 | -0.009155 | 0.036621 | -0.022888 | 0.18768 | 0.096131 | -122.0123 | 0.13275 | 0.21057 | 0.11444 | -122.1039 | 0.21515 | 0.15564 | -122.0627 | 0.064087 | 0.027466 | -0.12817 | -122.0444 | 0.20142 | 0.10986 | 0.15564 | -122.1176 | 0.15106 | 0.16937 | 0.20599 | -122.0581
3933.0156 | 122.2504 | -0.14191 | 121.9986 | -0.020218 | 0.012132 | 0.014772 | 0.001034 | 0.034004 | -0.0020679 | -0.043541 | -0.020752 | 0.0059837 | -0.015701 | -0.0011771 | 2.4756 | 0.028564 | 0.045776 | 0.059509 | 0.10986 | 0.11444 | -0.018311 | 0.050354 | -0.041199 | 0.022888 | 0.11444 | -0.032043 | -0.07782 | -0.054932 | 0.073242 | 0.018311 | 0.19226 | 0.10071 | -122.0169 | 0.20142 | 0.25635 | 0.15564 | -121.9528 | 0.21515 | 0.16022 | -122.0764 | 0.16479 | 0.10986 | -0.050354 | -122.0535 | 0.1236 | 0.18768 | 0.25177 | -122.0398 | 0.064087 | 0.086975 | 0.25635 | -121.9803
3934.7969 | 122.2092 | -0.16937 | 122.0398 | -0.020218 | 0.016191 | 0.015413 | 0.0033838 | 0.031441 | 0.0041273 | -0.043113 | -0.0054932 | 0.010256 | -0.013351 | -0.0016043 | 2.4848 | 0.024932 | 0.004578 | -0.013733 | 0.009155 | 0.064087 | 0.045776 | 0.009155 | -0.10529 | -0.027466 | 0.050354 | -0.1236 | -0.050354 | -0.018311 | 0.068665 | -0.022888 | 0.17853 | 0.064087 | -121.994 | 0.15564 | 0.23346 | 0.16937 | -122.0352 | 0.23804 | 0.14649 | -122.0901 | 0.14191 | 0.045777 | -0.10071 | -122.0581 | 0.21515 | 0.17395 | 0.17853 | -122.1451 | 0.11902 | 0.15106 | 0.21973 | -122.0627
3936.5 | 122.2549 | -0.14191 | 122.0169 | -0.012589 | 0.012132 | 0.018831 | 0.0014612 | 0.028878 | -0.0069811 | -0.044182 | -0.0054932 | 0.0047019 | -0.016129 | -0.0020315 | 2.5124 | 0.027495 | -0.022888 | 0.018311 | 0.041199 | 0.068665 | 0 | 0.045776 | -0.073242 | -0.041199 | 0.050354 | -0.068665 | -0.073242 | -0.032043 | 0.064087 | -0.009155 | 0.18768 | 0.068665 | -122.0169 | 0.16022 | 0.21057 | 0.14191 | -122.0398 | 0.20599 | 0.13275 | -122.0901 | 0.10071 | 0.073242 | -0.05951 | -122.049 | 0.14191 | 0.11902 | 0.18311 | -122.0901 | 0.068665 | 0.10986 | 0.19226 | -122.0261
3938.2812 | 122.2641 | -0.16022 | 122.0078 | -0.012589 | 0.014909 | 0.016267 | 0.0031702 | 0.031655 | -0.0069811 | -0.044395 | 0.0021363 | 0.0066245 | -0.015915 | -0.0020315 | 2.6081 | 0.026855 | -0.004578 | 0 | 0.045776 | 0.064087 | -0.004578 | 0.036621 | -0.054932 | -0.054932 | 0.059509 | -0.064087 | -0.059509 | -0.036621 | 0.082397 | 0.009155 | 0.19684 | 0.10528 | -122.0123 | 0.16022 | 0.2243 | 0.11902 | -122.0123 | 0.24261 | 0.16937 | -122.0673 | 0.10528 | 0.09613 | -0.073242 | -122.0444 | 0.15564 | 0.15564 | 0.20599 | -122.0627 | 0.10071 | 0.1236 | 0.21973 | -121.9986
3940.0625 | 122.1497 | -0.17853 | 122.0718 | -0.012589 | 0.018327 | 0.015413 | 0.001034 | 0.033791 | 0.0058363 | -0.043327 | -0.013123 | 0.011965 | -0.012924 | 0.00095911 | 2.6329 | 0.023437 | -0.004578 | -0.032043 | -0.013733 | 0.054932 | 0.022888 | 0.022888 | -0.082397 | -0.045776 | 0 | -0.13733 | -0.045776 | -0.018311 | 0.045776 | -0.018311 | 0.20142 | 0.096131 | -122.049 | 0.14648 | 0.23346 | 0.13733 | -122.0764 | 0.2243 | 0.16022 | -122.1176 | 0.13275 | 0.041199 | -0.11902 | -122.0901 | 0.20142 | 0.17395 | 0.16479 | -122.1542 | 0.13275 | 0.16022 | 0.17853 | -122.0901
3941.7812 | 122.2595 | -0.13733 | 122.0306 | -0.012589 | 0.0093545 | 0.012636 | 0.0018884 | 0.030159 | -0.0018543 | -0.045036 | -0.0054932 | 0.0072653 | -0.015274 | -0.0018179 | 2.5893 | 0.026 | 0.045776 | 0.050354 | 0.086975 | 0.11444 | -0.009155 | 0.059509 | -0.068665 | 0.032043 | 0.11444 | -0.018311 | -0.073242 | -0.059509 | 0.064087 | 0.018311 | 0.19684 | 0.068664 | -122.0398 | 0.18768 | 0.25177 | 0.18311 | -121.9849 | 0.20142 | 0.15564 | -122.1039 | 0.16937 | 0.11902 | -0.036622 | -122.0901 | 0.12817 | 0.18311 | 0.2243 | -122.0993 | 0.064087 | 0.07782 | 0.25177 | -122.0123
3943.5 | 122.2183 | -0.17395 | 122.0169 | -0.012589 | 0.013627 | 0.01584 | 0.0016748 | 0.032295 | 0.00092287 | -0.044395 | -0.0054932 | 0.0089743 | -0.013138 | 0.0013863 | 2.6331 | 0.023437 | -0.045776 | -0.082397 | -0.036621 | 0.045776 | 0.032043 | -0.004578 | -0.10986 | -0.068665 | 0.009155 | -0.14648 | -0.027466 | -0.018311 | 0.045776 | -0.032043 | 0.16937 | 0.064087 | -121.9849 | 0.091553 | 0.21973 | 0.15564 | -122.0627 | 0.21973 | 0.14191 | -122.0444 | 0.10528 | 0.027466 | -0.11444 | -122.0352 | 0.20599 | 0.12817 | 0.13733 | -122.1268 | 0.14648 | 0.15564 | 0.1831 | -122.049
3945.2812 | 122.3007 | -0.13275 | 122.0032 | -0.020218 | 0.017259 | 0.01285 | 0.001034 | 0.031014 | 0.0026319 | -0.042473 | -0.0054932 | 0.0081199 | -0.013992 | 0.0016001 | 2.6201 | 0.026 | -0.022888 | -0.050354 | -0.022888 | 0.045776 | 0.018311 | 0.013733 | -0.10071 | -0.022888 | 0.013733 | -0.10529 | -0.064087 | -0.022888 | 0.059509 | -0.013733 | 0.14648 | 0.032043 | -121.9849 | 0.082397 | 0.17853 | 0.14648 | -122.0261 | 0.19226 | 0.11902 | -122.0673 | 0.10986 | 0.027465 | -0.091553 | -122.0261 | 0.15106 | 0.10986 | 0.10986 | -122.1039 | 0.068664 | 0.10986 | 0.14648 | -122.0169
3947.0625 | 122.1954 | -0.16937 | 122.0856 | -0.012589 | 0.016191 | 0.014131 | 0.00060662 | 0.033577 | 0.0030591 | -0.043327 | -0.0054932 | 0.0096151 | -0.015701 | 0.00010471 | 2.6038 | 0.026427 | -0.059509 | -0.10986 | -0.050354 | 0.022888 | 0.032043 | 0.009155 | -0.091553 | -0.068665 | -0.041199 | -0.1831 | -0.013733 | -0.013733 | 0.036621 | -0.027466 | 0.17853 | 0.07782 | -122.0535 | 0.05951 | 0.19226 | 0.11444 | -122.1451 | 0.20599 | 0.14191 | -122.0993 | 0.10071 | -0.013732 | -0.15564 | -122.0993 | 0.20142 | 0.10986 | 0.11902 | -122.1771 | 0.15564 | 0.15564 | 0.12817 | -122.113
3948.8438 | 122.2137 | -0.18768 | 122.0215 | -0.0049592 | 0.018968 | 0.016267 | 0.0027428 | 0.032509 | -0.00099973 | -0.043541 | 0.0021363 | 0.0089743 | -0.013351 | -0.00053629 | 2.6055 | 0.025786 | -0.07782 | -0.064087 | -0.036621 | 0.036621 | 0.036621 | -0.009155 | -0.10986 | -0.086975 | -0.004578 | -0.15564 | -0.018311 | 0.004578 | 0.032043 | -0.027466 | 0.17853 | 0.07782 | -121.9849 | 0.1236 | 0.2243 | 0.14648 | -122.0993 | 0.21973 | 0.16022 | -122.0398 | 0.10071 | 0.032043 | -0.12817 | -122.0169 | 0.2243 | 0.10986 | 0.15106 | -122.1313 | 0.16937 | 0.19226 | 0.1831 | -122.049
3950.5469 | 122.2687 | -0.15564 | 122.0444 | -0.012589 | 0.020677 | 0.014558 | 0.00552 | 0.031014 | 0.0017773 | -0.043327 | -0.020752 | 0.010897 | -0.010147 | 0.00074551 | 2.672 | 0.025573 | -0.064087 | -0.086975 | -0.036621 | 0.027466 | 0.022888 | 0.004578 | -0.10071 | -0.073242 | -0.022888 | -0.14191 | -0.027466 | -0.018311 | 0.041199 | -0.022888 | 0.16022 | 0.054932 | -122.0215 | 0.068665 | 0.18311 | 0.12817 | -122.1085 | 0.19684 | 0.13275 | -122.0718 | 0.082398 | 0.013733 | -0.11902 | -122.0627 | 0.17853 | 0.091553 | 0.11902 | -122.1451 | 0.12817 | 0.13733 | 0.13275 | -122.0673
3952.3281 | 122.168 | -0.17853 | 122.0535 | -0.012589 | 0.017045 | 0.013918 | 0.0040246 | 0.0355 | 0.0028455 | -0.043113 | -0.013123 | 0.012819 | -0.013138 | 0.0022409 | 2.6814 | 0.025359 | 0 | -0.022888 | 0.004578 | 0.073242 | 0.013733 | 0.018311 | -0.10071 | -0.032043 | 0.027466 | -0.13733 | -0.045776 | -0.027466 | 0.054932 | -0.027466 | 0.19684 | 0.07782 | -122.0398 | 0.15564 | 0.25177 | 0.17395 | -122.0535 | 0.23346 | 0.15106 | -122.0993 | 0.14648 | 0.041199 | -0.10986 | -122.081 | 0.19226 | 0.17853 | 0.18311 | -122.1542 | 0.13275 | 0.15106 | 0.20599 | -122.081
3954.1094 | 122.2778 | -0.14648 | 122.0261 | -0.012589 | 0.014054 | 0.017549 | -0.00088858 | 0.032509 | -0.0065539 | -0.044395 | -0.013123 | 0.0085471 | -0.018265 | -0.0013907 | 2.6965 | 0.026427 | 0.041199 | 0.073242 | 0.10529 | 0.10986 | -0.009155 | 0.07782 | -0.045776 | 0.013733 | 0.10529 | -0.018311 | -0.07782 | -0.054932 | 0.073242 | -0.009155 | 0.2243 | 0.10071 | -122.0352 | 0.21973 | 0.25635 | 0.15564 | -121.9849 | 0.21973 | 0.13733 | -122.1039 | 0.16022 | 0.12817 | -0.009156 | -122.081 | 0.13733 | 0.18768 | 0.25177 | -122.0718 | 0.068664 | 0.091552 | 0.25177 | -122.0352
3955.9062 | 122.3099 | -0.14191 | 122.0261 | -0.012589 | 0.011704 | 0.017763 | 0.0029566 | 0.0308 | -0.0065539 | -0.043968 | -0.013123 | 0.0085471 | -0.016342 | -0.0020315 | 2.6882 | 0.027495 | 0.050354 | 0.091553 | 0.10986 | 0.11902 | -0.009155 | 0.045776 | -0.073242 | 0.009155 | 0.15106 | 0 | -0.086975 | -0.059509 | 0.050354 | 0.027466 | 0.18768 | 0.068665 | -122.0352 | 0.23346 | 0.26093 | 0.19226 | -121.9757 | 0.19226 | 0.16937 | -122.113 | 0.15106 | 0.14191 | -0.027466 | -122.0856 | 0.13275 | 0.19226 | 0.25177 | -122.0993 | 0.054932 | 0.082398 | 0.29297 | -121.9986
3957.625 | 122.2458 | -0.17395 | 122.049 | -0.0049592 | 0.017259 | 0.016054 | 0.0065882 | 0.032936 | 0.0015637 | -0.044609 | 0.0021363 | 0.0098289 | -0.012497 | 0.00053191 | 2.695 | 0.023009 | -0.027466 | -0.068665 | -0.022888 | 0.045776 | 0.036621 | 0.018311 | -0.11444 | -0.07782 | 0.013733 | -0.14648 | -0.032043 | 0 | 0.036621 | -0.027466 | 0.19226 | 0.059509 | -122.0123 | 0.10528 | 0.21973 | 0.16022 | -122.0764 | 0.21057 | 0.14648 | -122.081 | 0.09613 | 0.027466 | -0.11902 | -122.049 | 0.21057 | 0.14648 | 0.15106 | -122.1634 | 0.14191 | 0.17395 | 0.18768 | -122.0764
3959.4062 | 122.3145 | -0.13275 | 122.0352 | -0.012589 | 0.013841 | 0.016695 | 0.0029566 | 0.032723 | -0.0054859 | -0.046318 | -0.0054932 | 0.0034201 | -0.014206 | -0.0011771 | 2.6733 | 0.025786 | 0.045776 | 0.07782 | 0.10986 | 0.11902 | -0.013733 | 0.041199 | -0.059509 | 0.018311 | 0.14648 | 0.018311 | -0.064087 | -0.050354 | 0.068665 | 0.022888 | 0.17395 | 0.073242 | -122.049 | 0.21057 | 0.25177 | 0.17853 | -121.9894 | 0.20142 | 0.15564 | -122.0993 | 0.15106 | 0.15106 | -0.004577 | -122.0856 | 0.11902 | 0.17853 | 0.24261 | -122.0947 | 0.068664 | 0.082397 | 0.27924 | -122.0123
3961.2031 | 122.2092 | -0.17395 | 122.1039 | 0.0026703 | 0.017472 | 0.016481 | 0.0012476 | 0.033577 | -0.00099973 | -0.045036 | -0.020752 | 0.0083335 | -0.015488 | -0.0013907 | 2.6835 | 0.025146 | 0.045776 | 0.041199 | 0.091553 | 0.11902 | -0.018311 | 0.045776 | -0.073242 | -0.009155 | 0.11444 | -0.045776 | -0.050354 | -0.036621 | 0.045776 | 0.009155 | 0.21973 | 0.10071 | -122.1222 | 0.21515 | 0.29297 | 0.19226 | -122.0581 | 0.21973 | 0.1831 | -122.1542 | 0.16479 | 0.12817 | -0.054931 | -122.1405 | 0.15564 | 0.21973 | 0.2655 | -122.1771 | 0.1236 | 0.13733 | 0.28839 | -122.0947

## Thermal Data
Fire Time | D Position - 3' | D Position - Middle | D Position - 7' | D Position - Kerite 7c w - 3' | D Position - Kerite 7c w - 5' | D Position - Kerite 9c wo - 3' | D Position - Kerite 9c wo - 5'
-0.7458 | 6.9757 | 7.0904 | 7.101 | 7.2646 | 6.5402 | 6.6059 | 6.6547
0.2542 | 6.9741 | 7.107 | 7.0944 | 7.2695 | 6.5341 | 6.5995 | 6.656
1.2542 | 6.9752 | 7.0985 | 7.0938 | 7.2598 | 6.5323 | 6.6049 | 6.6575
2.2542 | 6.9768 | 7.0934 | 7.0995 | 7.2679 | 6.5474 | 6.6056 | 6.6594
3.2542 | 6.9733 | 7.1084 | 7.0922 | 7.2669 | 6.536 | 6.5997 | 6.6624
4.2542 | 6.979 | 7.0927 | 7.1014 | 7.2689 | 6.5371 | 6.6104 | 6.6618
5.2542 | 6.9764 | 7.0873 | 7.102 | 7.2783 | 6.5369 | 6.5983 | 6.6523
6.2542 | 6.9775 | 7.3257 | 7.1265 | 7.2688 | 6.5423 | 6.6015 | 6.6529
7.2542 | 6.9854 | 7.38 | 7.1734 | 7.271 | 6.5421 | 6.6151 | 6.6479
8.2542 | 7.3389 | 8.5434 | 7.6471 | 7.2777 | 6.5397 | 6.6051 | 6.6469
9.2542 | 8.6169 | 9.551 | 9.3537 | 7.286 | 6.5418 | 6.6072 | 6.639
10.2542 | 10.0682 | 10.6103 | 10.3876 | 7.2709 | 6.5348 | 6.6054 | 6.627
11.2542 | 10.9654 | 11.8177 | 11.7958 | 7.2764 | 6.5338 | 6.6013 | 6.6286
12.2542 | 12.9053 | 14.4701 | 13.0492 | 7.2786 | 6.5331 | 6.6084 | 6.605
13.2542 | 14.5595 | 16.8932 | 14.8178 | 7.2738 | 6.5383 | 6.603 | 6.6028
14.2542 | 17.1136 | 20.4163 | 17.694 | 7.2714 | 6.5419 | 6.6064 | 6.5848
15.2542 | 19.2959 | 24.9538 | 21.3718 | 7.2774 | 6.536 | 6.6275 | 6.5698
16.2542 | 23.316 | 30.065 | 23.4645 | 7.2873 | 6.5387 | 6.6211 | 6.5737
17.2542 | 27.1115 | 33.8572 | 26.6903 | 7.28 | 6.5283 | 6.6339 | 6.5583
18.2542 | 30.851 | 38.0256 | 31.2619 | 7.2817 | 6.519 | 6.6526 | 6.56
19.2542 | 34.4139 | 43.5991 | 34.1935 | 7.274 | 6.5156 | 6.6746 | 6.5439
20.2542 | 37.9535 | 47.1422 | 37.8375 | 7.2764 | 6.5338 | 6.6707 | 6.5389
21.2542 | 41.0535 | 50.9429 | 42.2338 | 7.2651 | 6.5615 | 6.709 | 6.5434
22.2542 | 44.1157 | 55.3377 | 45.5387 | 7.272 | 6.5553 | 6.7295 | 6.5436
23.2542 | 46.2852 | 59.4085 | 49.2471 | 7.2799 | 6.5454 | 6.7644 | 6.5051
24.2542 | 48.892 | 63.4208 | 53.3751 | 7.2804 | 6.5421 | 6.8089 | 6.5477
25.2542 | 51.8505 | 68.093 | 58.9782 | 7.2824 | 6.5319 | 6.8453 | 6.5339
26.2542 | 54.6448 | 70.4252 | 62.0004 | 7.2755 | 6.5557 | 6.8897 | 6.5412
27.2542 | 57.2331 | 73.5275 | 63.7228 | 7.2858 | 6.5527 | 6.9343 | 6.5676
28.2542 | 62.436 | 77.2802 | 67.1706 | 7.286 | 6.5685 | 6.979 | 6.5473
29.2542 | 67.8871 | 80.663 | 70.3262 | 7.2755 | 6.5731 | 7.0359 | 6.5925
30.2542 | 70.5353 | 84.0569 | 72.8574 | 7.2649 | 6.6043 | 7.0942 | 6.5707
31.2542 | 73.0518 | 87.7708 | 75.9973 | 7.2801 | 6.633 | 7.1372 | 6.5761
32.2542 | 75.8076 | 92.5174 | 78.7837 | 7.2683 | 6.6454 | 7.2096 | 6.5978
33.2542 | 79.1592 | 95.7597 | 81.4638 | 7.2678 | 6.6724 | 7.2756 | 6.6019
34.2542 | 83.0153 | 98.44 | 83.7518 | 7.2609 | 6.6702 | 7.325 | 6.6033
35.2542 | 85.3232 | 101.7598 | 85.4247 | 7.257 | 6.6791 | 7.3736 | 6.6339
36.2542 | 91.2229 | 105.1601 | 89.088 | 7.262 | 6.7073 | 7.4692 | 6.6415
37.2542 | 95.8662 | 107.8811 | 92.8258 | 7.2513 | 6.7069 | 7.5125 | 6.6287
38.2542 | 98.5298 | 112.2663 | 98.1989 | 7.252 | 6.7422 | 7.5859 | 6.6721
39.2542 | 99.7127 | 113.8481 | 99.1958 | 7.228 | 6.7512 | 7.6527 | 6.6684
40.2542 | 101.8054 | 115.3058 | 100.4747 | 7.2265 | 6.777 | 7.7069 | 6.7169
41.2542 | 104.1474 | 117.0203 | 102.5309 | 7.2206 | 6.8 | 7.7863 | 6.7175
42.2542 | 107.0845 | 118.9503 | 104.5334 | 7.2276 | 6.8155 | 7.8568 | 6.7406
43.2542 | 110.9769 | 122.2821 | 108.499 | 7.1928 | 6.8222 | 7.9486 | 6.7406
44.2542 | 111.2036 | 124.4182 | 110.3162 | 7.2125 | 6.8235 | 8.0044 | 6.7431
45.2542 | 113.891 | 125.5249 | 112.1894 | 7.1917 | 6.8626 | 8.0867 | 6.7745
46.2542 | 114.6927 | 127.4924 | 113.4934 | 7.1764 | 6.8638 | 8.1579 | 6.7783
47.2542 | 114.3837 | 127.9906 | 114.6868 | 7.2004 | 6.906 | 8.1884 | 6.8267
48.2542 | 114.7376 | 128.4633 | 116.3572 | 7.1783 | 6.9253 | 8.2856 | 6.8594
49.2542 | 114.9022 | 131.6958 | 118.6119 | 7.187 | 6.9234 | 8.3966 | 6.8655
50.2542 | 114.886 | 132.8155 | 119.659 | 7.1823 | 6.9512 | 8.464 | 6.9167
51.2542 | 114.6675 | 133.7323 | 122.4135 | 7.171 | 6.9792 | 8.5558 | 6.9442
52.2542 | 114.8348 | 133.5039 | 124.9821 | 7.167 | 6.9948 | 8.6316 | 6.9701
53.2542 | 114.5182 | 134.0282 | 126.5172 | 7.1613 | 7.0365 | 8.7174 | 6.9926
54.2542 | 115.0266 | 135.3358 | 128.8176 | 7.1711 | 7.0518 | 8.8312 | 7.0165
55.2542 | 119.7514 | 136.829 | 131.3504 | 7.1675 | 7.0547 | 8.9474 | 7.0833
56.2542 | 119.5598 | 136.7578 | 132.5651 | 7.1545 | 7.0769 | 9.0546 | 7.1234
57.2542 | 121.5909 | 137.9569 | 133.7598 | 7.1507 | 7.1084 | 9.1475 | 7.1592
58.2542 | 122.0083 | 139.5241 | 134.428 | 7.1077 | 7.109 | 9.2587 | 7.1689
59.2542 | 123.1989 | 139.9569 | 134.9002 | 7.1242 | 7.1693 | 9.3638 | 7.2299
60.2542 | 123.2552 | 141.175 | 135.5581 | 7.1223 | 7.1992 | 9.4804 | 7.2846
61.2542 | 123.3336 | 142.0226 | 136.8702 | 7.119 | 7.217 | 9.5935 | 7.3072
62.2542 | 123.3805 | 143.414 | 138.2551 | 7.1232 | 7.2577 | 9.6985 | 7.3374
63.2542 | 123.2744 | 142.5418 | 139.5061 | 7.1202 | 7.2583 | 9.825 | 7.3385
64.2542 | 123.3934 | 143.8931 | 140.7884 | 7.1304 | 7.2717 | 9.908 | 7.4162
65.2542 | 124.4087 | 143.8082 | 141.9252 | 7.1399 | 7.3225 | 10.0169 | 7.4723
66.2542 | 124.4643 | 144.8609 | 143.6526 | 7.1477 | 7.3505 | 10.1412 | 7.4754
67.2542 | 127.4938 | 146.8789 | 146.6409 | 7.1606 | 7.3564 | 10.2467 | 7.5425
68.2542 | 127.2149 | 148.2784 | 147.1949 | 7.1601 | 7.3992 | 10.3496 | 7.5628
69.2542 | 127.9841 | 148.1454 | 146.455 | 7.1506 | 7.4261 | 10.4104 | 7.5997
70.2542 | 130.3817 | 149.2759 | 146.624 | 7.151 | 7.4444 | 10.5101 | 7.6458
71.2542 | 130.1441 | 149.3794 | 146.4717 | 7.1753 | 7.4551 | 10.6342 | 7.6711
72.2542 | 130.103 | 150.4336 | 147.7566 | 7.1891 | 7.4654 | 10.7436 | 7.7299
73.2542 | 129.6294 | 150.7439 | 148.9002 | 7.1775 | 7.4927 | 10.843 | 7.7926
74.2542 | 129.4803 | 149.6745 | 148.8817 | 7.1857 | 7.534 | 10.9575 | 7.8408
75.2542 | 128.8109 | 150.0699 | 149.0258 | 7.1778 | 7.553 | 11.0412 | 7.8627
76.2542 | 130.9832 | 150.9071 | 150.2028 | 7.2011 | 7.5606 | 11.1363 | 7.937
77.2542 | 133.8335 | 151.2569 | 151.1381 | 7.1964 | 7.6095 | 11.2393 | 7.9727
78.2542 | 133.9558 | 152.0597 | 151.6571 | 7.1899 | 7.6467 | 11.3533 | 8.0039
79.2542 | 135.2484 | 153.6356 | 153.3414 | 7.1947 | 7.6511 | 11.445 | 8.0652
80.2542 | 136.5203 | 155.172 | 156.4397 | 7.1867 | 7.6567 | 11.5602 | 8.0718
81.2542 | 136.8613 | 157.2938 | 157.409 | 7.1951 | 7.6759 | 11.6479 | 8.1682
82.2542 | 137.2256 | 157.931 | 159.0329 | 7.1957 | 7.7042 | 11.7372 | 8.2059
83.2542 | 137.5202 | 159.4103 | 160.56 | 7.1866 | 7.7432 | 11.8198 | 8.2687
84.2542 | 138.464 | 160.3908 | 160.8683 | 7.185 | 7.7744 | 11.9544 | 8.3116
85.2542 | 138.6167 | 161.4186 | 161.1669 | 7.1938 | 7.8088 | 12.0419 | 8.3548
86.2542 | 142.2466 | 162.1532 | 161.7076 | 7.1996 | 7.8124 | 12.146 | 8.379
87.2542 | 141.0613 | 162.7406 | 161.735 | 7.1925 | 7.8573 | 12.2628 | 8.4473
88.2542 | 140.7085 | 162.2752 | 161.7139 | 7.2029 | 7.8557 | 12.3471 | 8.5179
89.2542 | 140.162 | 162.5671 | 161.5361 | 7.1999 | 7.8883 | 12.4875 | 8.5402
90.2542 | 139.8559 | 162.4657 | 161.377 | 7.2002 | 7.94 | 12.5514 | 8.6043
91.2542 | 139.9209 | 163.2356 | 161.761 | 7.1955 | 7.9459 | 12.6827 | 8.6711
92.2542 | 142.0828 | 164.0475 | 163.3802 | 7.1851 | 7.9707 | 12.7792 | 8.6957
93.2542 | 144.2248 | 164.5511 | 165.6104 | 7.1942 | 7.9683 | 12.908 | 8.7416
94.2542 | 143.1093 | 164.7048 | 165.7488 | 7.1745 | 7.9813 | 12.9902 | 8.7917
95.2542 | 142.3476 | 165.5108 | 167.7593 | 7.1808 | 8.0491 | 13.0804 | 8.8324
96.2542 | 141.387 | 164.9071 | 168.7964 | 7.1717 | 8.0886 | 13.1598 | 8.8764
97.2542 | 141.1534 | 165.2898 | 169.1707 | 7.187 | 8.1068 | 13.2979 | 8.9362
98.2542 | 142.36 | 165.0422 | 169.5374 | 7.1769 | 8.0957 | 13.4032 | 8.9695
99.2542 | 144.2861 | 166.4189 | 172.5444 | 7.2063 | 8.1605 | 13.5025 | 9.0262
100.2542 | 146.7574 | 169.6971 | 173.8406 | 7.1898 | 8.1828 | 13.6184 | 9.0991
101.2542 | 145.8411 | 170.8938 | 174.0981 | 7.194 | 8.1901 | 13.6889 | 9.1669
102.2542 | 146.0159 | 171.1279 | 175.3454 | 7.1831 | 8.2053 | 13.7998 | 9.1852
103.2542 | 145.212 | 171.0638 | 177.1771 | 7.1943 | 8.2358 | 13.9149 | 9.2577
104.2542 | 145.0505 | 171.3256 | 177.8846 | 7.1982 | 8.3168 | 14.0172 | 9.3193
105.2542 | 144.8537 | 170.3636 | 178.3105 | 7.202 | 8.3157 | 14.1265 | 9.3601
106.2542 | 144.2585 | 169.7413 | 178.386 | 7.2002 | 8.3374 | 14.2515 | 9.434
107.2542 | 143.7804 | 170.903 | 179.7205 | 7.2102 | 8.3624 | 14.333 | 9.5083
108.2542 | 143.2711 | 171.8892 | 181.6994 | 7.2108 | 8.4207 | 14.4577 | 9.5316
109.2542 | 142.7728 | 173.4086 | 182.3034 | 7.2262 | 8.4447 | 14.5972 | 9.5908
110.2542 | 142.2237 | 171.3821 | 182.3745 | 7.23 | 8.4985 | 14.7225 | 9.6433
111.2542 | 141.9588 | 171.5868 | 182.5228 | 7.2387 | 8.5264 | 14.8217 | 9.7311
112.2542 | 141.6952 | 170.9646 | 182.3865 | 7.232 | 8.5223 | 14.9631 | 9.7512
113.2542 | 143.5624 | 173.13 | 183.612 | 7.2489 | 8.5566 | 15.0773 | 9.8311
114.2542 | 144.5832 | 173.3755 | 182.8523 | 7.2456 | 8.6038 | 15.206 | 9.8591
115.2542 | 144.4734 | 174.4041 | 183.4745 | 7.2515 | 8.6355 | 15.3243 | 9.9348
116.2542 | 144.2982 | 174.775 | 184.0815 | 7.2565 | 8.642 | 15.4452 | 10.0022
117.2542 | 144.5306 | 173.6307 | 184.0273 | 7.2688 | 8.6886 | 15.5595 | 10.0608
118.2542 | 144.7789 | 173.7253 | 185.2691 | 7.2806 | 8.7278 | 15.6873 | 10.1097
119.2542 | 145.0537 | 174.0533 | 184.8454 | 7.2897 | 8.7732 | 15.7653 | 10.1873
120.2542 | 145.1237 | 174.3602 | 184.372 | 7.3013 | 8.8028 | 15.9049 | 10.2431
121.2542 | 144.6834 | 173.6027 | 184.8406 | 7.3048 | 8.8443 | 16.0119 | 10.3161
122.2542 | 144.2665 | 173.1544 | 185.0561 | 7.3028 | 8.8561 | 16.1513 | 10.3759
123.2542 | 144.7049 | 173.684 | 184.8645 | 7.3249 | 8.85 | 16.247 | 10.4233
124.2542 | 143.503 | 174.2945 | 185.0194 | 7.3347 | 8.8782 | 16.3651 | 10.4757
125.2542 | 143.4109 | 174.8744 | 185.9401 | 7.3413 | 8.8716 | 16.4834 | 10.5269
126.2542 | 143.2954 | 174.8598 | 185.4866 | 7.3606 | 8.9596 | 16.6233 | 10.5919
127.2542 | 143.2507 | 176.1042 | 187.2632 | 7.3714 | 8.9917 | 16.7568 | 10.6664
128.2542 | 143.4505 | 176.1734 | 186.7054 | 7.3841 | 9.0209 | 16.8562 | 10.7252
129.2542 | 142.9908 | 177.6012 | 186.5897 | 7.3894 | 9.0448 | 16.9725 | 10.8038
130.2542 | 142.683 | 177.3582 | 187.1798 | 7.3812 | 9.0852 | 17.1008 | 10.8577
131.2542 | 143.2921 | 177.6685 | 186.8429 | 7.4018 | 9.1151 | 17.2164 | 10.9043
132.2542 | 142.7074 | 177.5715 | 186.9032 | 7.4089 | 9.1344 | 17.3398 | 10.9522
133.2542 | 142.8164 | 178.5867 | 188.0025 | 7.4327 | 9.1872 | 17.4888 | 11.0209
134.2542 | 143.175 | 179.088 | 188.1273 | 7.4442 | 9.1836 | 17.6198 | 11.0897
135.2542 | 143.3006 | 179.2072 | 187.5916 | 7.4431 | 9.2249 | 17.7318 | 11.1467
136.2542 | 143.0248 | 179.0015 | 187.9609 | 7.4556 | 9.278 | 17.8683 | 11.2112
137.2542 | 143.2525 | 178.2868 | 187.1633 | 7.4619 | 9.2683 | 18.0081 | 11.2552
138.2542 | 144.1129 | 178.5539 | 186.4173 | 7.4759 | 9.3224 | 18.1311 | 11.3229
139.2542 | 144.1608 | 178.2276 | 186.4037 | 7.4955 | 9.3647 | 18.2795 | 11.3723
140.2542 | 144.0451 | 177.2375 | 186.5178 | 7.5087 | 9.3956 | 18.4093 | 11.4672
141.2542 | 143.8925 | 177.8816 | 186.8679 | 7.5185 | 9.4324 | 18.5394 | 11.522
142.2542 | 143.7297 | 178.9912 | 186.8391 | 7.5257 | 9.4786 | 18.6359 | 11.5846
143.2542 | 144.3789 | 179.4762 | 186.6867 | 7.517 | 9.5034 | 18.762 | 11.6598
144.2542 | 143.9032 | 179.2968 | 186.763 | 7.5365 | 9.5379 | 18.8924 | 11.69
145.2542 | 143.7473 | 178.852 | 186.5704 | 7.5385 | 9.5506 | 19.0392 | 11.7559
146.2542 | 144.319 | 178.6064 | 187.05 | 7.5538 | 9.5667 | 19.1461 | 11.7953
147.2542 | 145.0362 | 178.7392 | 187.5026 | 7.5883 | 9.596 | 19.297 | 11.8444
148.2542 | 145.136 | 178.5453 | 187.71 | 7.5828 | 9.6566 | 19.4054 | 11.9252
149.2542 | 144.9585 | 178.3954 | 188.7504 | 7.6071 | 9.6934 | 19.4982 | 11.9935
150.2542 | 146.0727 | 179.0642 | 189.4107 | 7.6215 | 9.7163 | 19.6358 | 12.0731
151.2542 | 147.1489 | 180.9764 | 190.7951 | 7.6335 | 9.7256 | 19.7489 | 12.1425
152.2542 | 146.8232 | 181.6676 | 192.1965 | 7.6295 | 9.7715 | 19.8533 | 12.2099
153.2542 | 147.0834 | 181.7373 | 192.448 | 7.6274 | 9.8098 | 19.9812 | 12.2638
154.2542 | 147.2734 | 181.5292 | 192.6975 | 7.6421 | 9.8486 | 20.1156 | 12.3422
155.2542 | 147.6205 | 183.4443 | 193.0425 | 7.6645 | 9.8541 | 20.233 | 12.3796
156.2542 | 150.5744 | 185.1049 | 195.9475 | 7.6813 | 9.8613 | 20.3575 | 12.4462
157.2542 | 152.1559 | 185.2091 | 196.4903 | 7.664 | 9.9168 | 20.4973 | 12.4928
158.2542 | 152.2431 | 185.6641 | 197.0567 | 7.6727 | 9.944 | 20.5845 | 12.5288
159.2542 | 152.486 | 186.3884 | 197.2801 | 7.7042 | 9.9977 | 20.7094 | 12.6046
160.2542 | 153.4376 | 187.344 | 197.8607 | 7.7133 | 10.0314 | 20.8144 | 12.6753
161.2542 | 153.5281 | 188.0653 | 197.9143 | 7.7283 | 10.0481 | 20.9532 | 12.757
162.2542 | 154.6809 | 188.853 | 197.9641 | 7.7235 | 10.1085 | 21.0843 | 12.814
163.2542 | 154.7592 | 188.1915 | 198.4619 | 7.726 | 10.1602 | 21.1818 | 12.8962
164.2542 | 154.7466 | 187.635 | 197.9068 | 7.7636 | 10.1754 | 21.2819 | 12.9468
165.2542 | 154.6174 | 188.1005 | 198.2959 | 7.763 | 10.2226 | 21.3868 | 13.0001
166.2542 | 154.5591 | 188.0687 | 198.7743 | 7.7551 | 10.2935 | 21.4946 | 13.0542
167.2542 | 155.613 | 186.9499 | 198.412 | 7.7832 | 10.2777 | 21.6049 | 13.1052
168.2542 | 156.6393 | 187.2479 | 199.2784 | 7.7938 | 10.3526 | 21.7324 | 13.1692
169.2542 | 157.4805 | 188.6019 | 200.5621 | 7.8139 | 10.3567 | 21.8104 | 13.2549
170.2542 | 158.4776 | 189.6738 | 201.7332 | 7.8325 | 10.4273 | 21.9283 | 13.3082
171.2542 | 160.564 | 190.2125 | 201.6468 | 7.8551 | 10.4853 | 21.9964 | 13.3735
172.2542 | 161.2533 | 190.0362 | 201.8348 | 7.8574 | 10.5373 | 22.1029 | 13.4335
173.2542 | 161.305 | 188.8285 | 202.5222 | 7.8687 | 10.6016 | 22.226 | 13.4719
174.2542 | 160.8724 | 189.9439 | 203.4705 | 7.901 | 10.6506 | 22.307 | 13.5566
175.2542 | 161.3406 | 190.1187 | 204.9496 | 7.8951 | 10.6815 | 22.429 | 13.6308
176.2542 | 160.4012 | 190.0917 | 204.972 | 7.9043 | 10.7204 | 22.5139 | 13.6591
177.2542 | 160.1396 | 190.1778 | 204.7394 | 7.937 | 10.8018 | 22.6109 | 13.7477
178.2542 | 159.0563 | 190.5426 | 205.43 | 7.9607 | 10.8329 | 22.7198 | 13.8438
179.2542 | 159.9768 | 192.1278 | 207.0479 | 7.9766 | 10.8724 | 22.8373 | 13.8828
180.2542 | 160.3929 | 192.9684 | 207.3217 | 7.9801 | 10.9311 | 22.9586 | 13.9416
181.2542 | 160.2963 | 192.8706 | 207.021 | 7.9874 | 10.9921 | 23.0725 | 14.023
182.2542 | 159.6459 | 191.0293 | 206.3193 | 7.9932 | 11.0588 | 23.185 | 14.0607
183.2542 | 158.7391 | 190.106 | 205.3953 | 8.0028 | 11.1175 | 23.2738 | 14.1264
184.2542 | 158.4763 | 188.4701 | 203.7289 | 8.0276 | 11.147 | 23.4072 | 14.2012
185.2542 | 157.9499 | 186.9369 | 202.8319 | 8.0423 | 11.1789 | 23.5177 | 14.2802
186.2542 | 157.6759 | 186.8381 | 201.6557 | 8.063 | 11.2463 | 23.6391 | 14.3389
187.2542 | 157.4218 | 186.5778 | 201.3689 | 8.0882 | 11.2739 | 23.7404 | 14.4114
188.2542 | 156.5912 | 186.6834 | 200.104 | 8.0961 | 11.3507 | 23.8526 | 14.447
189.2542 | 156.5308 | 187.0398 | 200.8266 | 8.1155 | 11.3901 | 23.9786 | 14.502
190.2542 | 156.6112 | 187.2327 | 199.9972 | 8.1272 | 11.4634 | 24.0717 | 14.5647
191.2542 | 156.1528 | 186.6577 | 199.5383 | 8.1526 | 11.5003 | 24.1522 | 14.6573
192.2542 | 155.3143 | 187.9184 | 200.1953 | 8.1551 | 11.5245 | 24.2854 | 14.7039
193.2542 | 154.3379 | 187.0856 | 200.3159 | 8.1864 | 11.5634 | 24.3709 | 14.7665
194.2542 | 154.7718 | 187.6672 | 200.602 | 8.1955 | 11.5983 | 24.4905 | 14.8406
195.2542 | 154.2364 | 187.5993 | 202.3856 | 8.2169 | 11.6421 | 24.5677 | 14.8886
196.2542 | 153.486 | 187.5949 | 202.482 | 8.2208 | 11.7107 | 24.6861 | 14.9525
197.2542 | 153.5976 | 187.3626 | 202.2659 | 8.2434 | 11.7457 | 24.8008 | 14.9867
198.2542 | 154.7445 | 187.4648 | 202.7085 | 8.2417 | 11.7734 | 24.912 | 15.0308
199.2542 | 153.8866 | 187.7184 | 203.311 | 8.2757 | 11.8205 | 25.0009 | 15.1104
200.2542 | 154.4755 | 188.5299 | 203.7465 | 8.2936 | 11.8692 | 25.1293 | 15.1354
201.2542 | 154.1361 | 188.8364 | 203.7875 | 8.301 | 11.9126 | 25.22 | 15.2027
202.2542 | 154.295 | 188.7849 | 204.3279 | 8.3154 | 11.9365 | 25.3471 | 15.2566
203.2542 | 155.0144 | 190.5934 | 205.5821 | 8.335 | 11.9623 | 25.437 | 15.3352
204.2542 | 154.3194 | 190.3964 | 206.6279 | 8.3644 | 12.0237 | 25.5024 | 15.41
205.2542 | 154.4179 | 190.8368 | 206.3106 | 8.376 | 12.0238 | 25.63 | 15.4618
206.2542 | 154.6329 | 191.0613 | 206.5127 | 8.372 | 12.1247 | 25.7534 | 15.5405
207.2542 | 153.9039 | 190.5122 | 206.4671 | 8.3969 | 12.1411 | 25.8503 | 15.56
208.2542 | 153.8185 | 189.7714 | 206.3702 | 8.4055 | 12.1736 | 25.9655 | 15.6429
209.2542 | 153.6688 | 189.7004 | 206.6237 | 8.4257 | 12.2344 | 26.0735 | 15.7209
210.2542 | 153.1392 | 189.1728 | 206.7752 | 8.4563 | 12.2578 | 26.1551 | 15.7745
211.2542 | 153.2457 | 188.6978 | 207.5852 | 8.4517 | 12.3021 | 26.2872 | 15.8275
212.2542 | 153.0431 | 189.7241 | 207.8075 | 8.4709 | 12.3347 | 26.3928 | 15.8976
213.2542 | 153.7792 | 190.191 | 208.9389 | 8.4891 | 12.4001 | 26.4861 | 15.9292
214.2542 | 153.6799 | 189.9944 | 208.9797 | 8.5093 | 12.4181 | 26.5903 | 15.9922
215.2542 | 153.525 | 190.3247 | 209.289 | 8.5359 | 12.4755 | 26.7003 | 16.0631
216.2542 | 156.8705 | 192.769 | 210.101 | 8.5647 | 12.5224 | 26.8142 | 16.1045
217.2542 | 158.8407 | 195.4031 | 211.2667 | 8.55 | 12.5822 | 26.9231 | 16.1606
218.2542 | 158.77 | 194.9008 | 210.9768 | 8.5734 | 12.6192 | 27.024 | 16.2199
219.2542 | 159.6778 | 194.9104 | 211.7029 | 8.57 | 12.668 | 27.1184 | 16.295
220.2542 | 159.2775 | 194.0548 | 212.1243 | 8.6118 | 12.7036 | 27.2205 | 16.3597
221.2542 | 159.3812 | 195.088 | 212.1003 | 8.6121 | 12.733 | 27.3398 | 16.4069
222.2542 | 160.5831 | 196.2133 | 212.6572 | 8.6469 | 12.7833 | 27.4443 | 16.4668
223.2542 | 161.2778 | 196.231 | 212.3945 | 8.6409 | 12.8038 | 27.5697 | 16.5356
224.2542 | 161.656 | 198.4684 | 213.3567 | 8.6808 | 12.8438 | 27.6828 | 16.59
225.2542 | 161.4291 | 198.7391 | 213.922 | 8.6839 | 12.9073 | 27.7744 | 16.6207
226.2542 | 161.127 | 198.3204 | 214.2709 | 8.6977 | 12.9611 | 27.9185 | 16.6794
227.2542 | 162.9626 | 199.5367 | 215.3596 | 8.7186 | 13.0064 | 28.0041 | 16.7669
228.2542 | 165.394 | 200.2674 | 215.7311 | 8.7188 | 13.0226 | 28.1348 | 16.8225
229.2542 | 169.4269 | 202.7222 | 215.9825 | 8.7341 | 13.1056 | 28.2462 | 16.8758
230.2542 | 169.1458 | 204.4172 | 216.6164 | 8.7318 | 13.1465 | 28.3513 | 16.9296
231.2542 | 169.4221 | 205.9493 | 217.2193 | 8.7706 | 13.149 | 28.4409 | 17.0001
232.2542 | 170.8317 | 207.8668 | 217.467 | 8.8082 | 13.2089 | 28.5527 | 17.081
233.2542 | 174.1105 | 209.2358 | 218.9653 | 8.8111 | 13.2873 | 28.6729 | 17.1254
234.2542 | 173.8483 | 210.4361 | 219.2884 | 8.832 | 13.3158 | 28.7869 | 17.1878
235.2542 | 173.1363 | 211.2573 | 220.8579 | 8.8599 | 13.3364 | 28.8981 | 17.232
236.2542 | 172.0316 | 209.975 | 220.645 | 8.8623 | 13.415 | 28.984 | 17.3305
237.2542 | 171.9473 | 209.9438 | 220.8406 | 8.8795 | 13.465 | 29.1073 | 17.3692
238.2542 | 173.5708 | 212.1621 | 221.8564 | 8.9052 | 13.5165 | 29.2246 | 17.4221
239.2542 | 173.2487 | 211.8514 | 222.2003 | 8.9127 | 13.5513 | 29.3185 | 17.4973
240.2542 | 172.3793 | 210.229 | 222.6461 | 8.9407 | 13.5619 | 29.4327 | 17.5714
241.2542 | 173.5394 | 211.9673 | 223.9974 | 8.954 | 13.6563 | 29.5504 | 17.6283
242.2542 | 174.5473 | 212.4931 | 225.9024 | 8.9687 | 13.7105 | 29.6834 | 17.6641
243.2542 | 174.9303 | 213.2305 | 225.0614 | 9.0024 | 13.7144 | 29.7615 | 17.7314
244.2542 | 174.9001 | 213.1593 | 226.9851 | 9.0279 | 13.795 | 29.8661 | 17.8029
245.2542 | 176.014 | 215.5672 | 229.3685 | 9.0292 | 13.8448 | 30.0203 | 17.8638
246.2542 | 175.4443 | 214.1939 | 229.7326 | 9.0795 | 13.8733 | 30.0905 | 17.9248
247.2542 | 175.0448 | 213.7335 | 230.3505 | 9.0984 | 13.9383 | 30.2305 | 17.9793
248.2542 | 175.7691 | 217.4249 | 231.6984 | 9.1095 | 14.0023 | 30.3685 | 18.0286
249.2542 | 177.3435 | 218.4312 | 231.942 | 9.092 | 14.0304 | 30.4934 | 18.0922
250.2542 | 178.4005 | 218.5499 | 232.8693 | 9.15 | 14.0914 | 30.6255 | 18.1587
251.2542 | 178.13 | 219.5832 | 233.2403 | 9.1735 | 14.1331 | 30.7392 | 18.2414
252.2542 | 178.0752 | 220.2459 | 233.0619 | 9.1803 | 14.1614 | 30.8702 | 18.302
253.2542 | 177.5344 | 220.9294 | 233.7461 | 9.2188 | 14.2335 | 30.9865 | 18.3607
254.2542 | 177.2452 | 221.1412 | 234.1646 | 9.2412 | 14.2775 | 31.1028 | 18.4209
255.2542 | 177.0081 | 220.7345 | 233.8844 | 9.2555 | 14.3201 | 31.2306 | 18.4533
256.2542 | 177.8595 | 222.2166 | 235.3837 | 9.2605 | 14.3676 | 31.3761 | 18.5072
257.2542 | 178.3642 | 221.1084 | 236.1307 | 9.3061 | 14.4023 | 31.4857 | 18.5843
258.2542 | 178.1358 | 222.8881 | 237.6821 | 9.3303 | 14.4773 | 31.6197 | 18.6386
259.2542 | 178.8315 | 224.029 | 239.4328 | 9.3362 | 14.5346 | 31.7434 | 18.6979
260.2542 | 182.0052 | 223.5469 | 239.6402 | 9.3702 | 14.5607 | 31.8554 | 18.7388
261.2542 | 182.0248 | 223.7764 | 239.8006 | 9.3983 | 14.6243 | 31.9821 | 18.8176
262.2542 | 182.5229 | 222.9453 | 240.799 | 9.4083 | 14.6869 | 32.1043 | 18.8838
263.2542 | 182.2724 | 223.176 | 240.5405 | 9.4427 | 14.7492 | 32.2479 | 18.9608
264.2542 | 182.166 | 222.5425 | 241.2456 | 9.4524 | 14.7738 | 32.3421 | 19.0163
265.2542 | 181.9656 | 222.2033 | 241.3663 | 9.4851 | 14.8283 | 32.4893 | 19.0592
266.2542 | 181.072 | 222.7276 | 242.1165 | 9.5143 | 14.8761 | 32.621 | 19.1527
267.2542 | 180.9111 | 222.8434 | 242.5258 | 9.5274 | 14.9535 | 32.7229 | 19.2478
268.2542 | 180.7694 | 223.4503 | 245.1938 | 9.5421 | 14.9848 | 32.8628 | 19.2835
269.2542 | 181.3049 | 225.534 | 247.1887 | 9.5785 | 15.05 | 32.985 | 19.3439
270.2542 | 182.8805 | 226.2169 | 247.7618 | 9.5971 | 15.1229 | 33.1296 | 19.4135
271.2542 | 184.2444 | 226.868 | 247.245 | 9.6162 | 15.1372 | 33.2653 | 19.4847
272.2542 | 183.6194 | 226.7025 | 246.8402 | 9.6268 | 15.1851 | 33.395 | 19.5565
273.2542 | 184.2315 | 228.0828 | 248.1351 | 9.6559 | 15.2191 | 33.5205 | 19.6286
274.2542 | 184.1281 | 228.6047 | 247.9924 | 9.6805 | 15.2797 | 33.6208 | 19.6813
275.2542 | 184.8516 | 228.9846 | 247.4611 | 9.7063 | 15.3719 | 33.7508 | 19.7722
276.2542 | 185.1891 | 231.8834 | 249.3111 | 9.7304 | 15.4188 | 33.9059 | 19.8337
277.2542 | 185.6165 | 231.5173 | 251.0133 | 9.7467 | 15.4768 | 34.0266 | 19.8776
278.2542 | 184.7919 | 232.1706 | 252.065 | 9.7593 | 15.5194 | 34.1766 | 19.963
279.2542 | 185.0284 | 232.8642 | 252.445 | 9.8014 | 15.5654 | 34.2724 | 20.0252
280.2542 | 185.1431 | 234.512 | 252.8671 | 9.8132 | 15.6031 | 34.4167 | 20.0934
281.2542 | 184.9899 | 235.8969 | 253.693 | 9.8305 | 15.658 | 34.5468 | 20.1436
282.2542 | 185.1801 | 236.8075 | 255.2584 | 9.864 | 15.7097 | 34.6629 | 20.2046
283.2542 | 186.1702 | 237.7586 | 256.9054 | 9.8973 | 15.7698 | 34.8233 | 20.2981
284.2542 | 186.0521 | 236.6218 | 256.5687 | 9.9177 | 15.8702 | 34.9673 | 20.378
285.2542 | 186.3376 | 236.6577 | 256.6832 | 9.9342 | 15.9174 | 35.1171 | 20.44
286.2542 | 186.1351 | 235.9688 | 256.7878 | 9.9634 | 16.0109 | 35.2234 | 20.5332
287.2542 | 185.6459 | 235.5781 | 256.2037 | 9.9899 | 16.0641 | 35.3609 | 20.6003
288.2542 | 185.6956 | 238.5603 | 257.8537 | 9.995 | 16.088 | 35.4996 | 20.6471
289.2542 | 186.2409 | 238.5047 | 258.6572 | 10.0294 | 16.1535 | 35.6168 | 20.7182
290.2542 | 186.9085 | 239.4871 | 259.5582 | 10.051 | 16.2125 | 35.7631 | 20.7787
291.2542 | 188.2659 | 240.2763 | 259.7303 | 10.0694 | 16.2891 | 35.8928 | 20.8448
292.2542 | 189.2613 | 239.7518 | 260.4224 | 10.0931 | 16.3837 | 36.0575 | 20.9061
293.2542 | 191.4552 | 240.5547 | 259.8614 | 10.1316 | 16.4209 | 36.1795 | 20.9691
294.2542 | 195.0539 | 241.4041 | 259.6135 | 10.1559 | 16.4763 | 36.3131 | 21.0359
295.2542 | 194.2831 | 241.7007 | 260.0121 | 10.1804 | 16.5723 | 36.4602 | 21.147
296.2542 | 194.3057 | 241.54 | 262.3737 | 10.2192 | 16.6369 | 36.626 | 21.2175
297.2542 | 193.8516 | 240.8623 | 262.8802 | 10.2515 | 16.6497 | 36.6992 | 21.2975
298.2542 | 193.715 | 241.5379 | 264.265 | 10.2665 | 16.7334 | 36.8393 | 21.3679
299.2542 | 195.3336 | 245.0811 | 266.3474 | 10.3054 | 16.8208 | 37.0045 | 21.415
300.2542 | 195.979 | 247.1298 | 268.9832 | 10.3232 | 16.8968 | 37.134 | 21.4837
301.2542 | 197.3091 | 247.8879 | 268.0706 | 10.3299 | 16.9182 | 37.2535 | 21.5611
302.2542 | 197.8979 | 246.1628 | 267.6476 | 10.3561 | 16.9917 | 37.3762 | 21.6383
303.2542 | 197.5858 | 246.7718 | 267.415 | 10.3904 | 17.0591 | 37.5204 | 21.7141
304.2542 | 198.6162 | 246.2582 | 268.2423 | 10.4265 | 17.1296 | 37.6654 | 21.8134
305.2542 | 199.1569 | 247.5686 | 268.3076 | 10.431 | 17.1962 | 37.7697 | 21.8811
306.2542 | 199.5531 | 247.8601 | 268.2986 | 10.4669 | 17.2541 | 37.9275 | 21.9612
307.2542 | 200.0157 | 249.6943 | 269.2025 | 10.4986 | 17.3173 | 38.061 | 22.0076
308.2542 | 201.3041 | 250.4097 | 270.443 | 10.5292 | 17.4037 | 38.2119 | 22.0839
309.2542 | 202.0788 | 250.6392 | 270.8316 | 10.557 | 17.4576 | 38.3539 | 22.1466
310.2542 | 203.8973 | 251.6035 | 270.8 | 10.6077 | 17.5242 | 38.4755 | 22.2418
311.2542 | 203.2562 | 253.9648 | 272.106 | 10.6319 | 17.6076 | 38.63 | 22.3419
312.2542 | 203.7435 | 255.6331 | 272.4547 | 10.6473 | 17.6629 | 38.7703 | 22.4148
313.2542 | 204.285 | 255.8232 | 272.6896 | 10.681 | 17.7707 | 38.9181 | 22.4967
314.2542 | 207.6363 | 256.8984 | 273.1054 | 10.6979 | 17.8177 | 39.0432 | 22.5586
315.2542 | 213.0084 | 260.5512 | 275.2901 | 10.7623 | 17.8326 | 39.1695 | 22.6419
316.2542 | 215.826 | 262.8334 | 276.8533 | 10.7669 | 17.934 | 39.3183 | 22.7138
317.2542 | 215.6341 | 265.1287 | 279.5672 | 10.7884 | 17.9996 | 39.4287 | 22.7926
318.2542 | 213.8815 | 265.0334 | 280.4199 | 10.8157 | 18.067 | 39.5924 | 22.8419
319.2542 | 212.7162 | 264.1638 | 281.0343 | 10.8497 | 18.1558 | 39.6822 | 22.9286
320.2542 | 212.4598 | 264.9513 | 281.7814 | 10.894 | 18.2058 | 39.8368 | 23.0192
321.2542 | 212.3666 | 264.9414 | 282.549 | 10.9182 | 18.3003 | 40.0158 | 23.1052
322.2542 | 214.0063 | 265.3412 | 282.4646 | 10.9371 | 18.4439 | 40.1479 | 23.1833
323.2542 | 215.5028 | 265.4752 | 282.9296 | 10.9634 | 18.5128 | 40.2664 | 23.2678
324.2542 | 217.8553 | 265.1677 | 283.1359 | 11.0039 | 18.5456 | 40.3984 | 23.3629
325.2542 | 218.1126 | 265.8382 | 282.4527 | 11.0261 | 18.6164 | 40.5429 | 23.4613
326.2542 | 218.4889 | 266.7293 | 283.4093 | 11.0639 | 18.7154 | 40.69 | 23.5158
327.2542 | 221.1468 | 269.0503 | 286.2556 | 11.0866 | 18.7853 | 40.8236 | 23.6003
328.2542 | 221.589 | 271.8534 | 286.1629 | 11.1191 | 18.8592 | 40.9323 | 23.7146
329.2542 | 221.2629 | 272.6715 | 286.7076 | 11.1626 | 18.9286 | 41.0548 | 23.8104
330.2542 | 220.2993 | 270.8501 | 285.4375 | 11.1872 | 18.9926 | 41.2242 | 23.8947
331.2542 | 219.4553 | 270.3132 | 286.5872 | 11.2137 | 19.1097 | 41.3863 | 23.9495
332.2542 | 218.4135 | 269.7341 | 287.1872 | 11.251 | 19.1986 | 41.5097 | 24.0474
333.2542 | 217.7278 | 270.1403 | 288.3801 | 11.2863 | 19.2748 | 41.6663 | 24.1413
334.2542 | 218.927 | 271.202 | 288.4726 | 11.3232 | 19.36 | 41.7798 | 24.232
335.2542 | 218.8605 | 270.4111 | 288.8173 | 11.3705 | 19.4263 | 41.9134 | 24.3048
336.2542 | 219.9689 | 273.1459 | 291.6419 | 11.3878 | 19.4951 | 42.0735 | 24.3823
337.2542 | 222.9974 | 273.9717 | 292.673 | 11.4354 | 19.6028 | 42.1973 | 24.4642
338.2542 | 225.4924 | 275.4657 | 293.7642 | 11.4623 | 19.7008 | 42.3416 | 24.526
339.2542 | 227.6185 | 276.9326 | 294.4551 | 11.5143 | 19.7547 | 42.4941 | 24.5995
340.2542 | 227.6675 | 276.7837 | 295.2615 | 11.5318 | 19.8347 | 42.6084 | 24.7061
341.2542 | 228.2047 | 278.3155 | 296.8803 | 11.585 | 19.9525 | 42.7558 | 24.7967
342.2542 | 230.6559 | 279.5614 | 297.428 | 11.6089 | 20.0465 | 42.9157 | 24.8928
343.2542 | 229.7511 | 280.0651 | 297.8132 | 11.6368 | 20.14 | 43.0714 | 24.9779
344.2542 | 230.8237 | 277.9223 | 298.4136 | 11.6872 | 20.1996 | 43.2256 | 25.0701
345.2542 | 230.3923 | 278.5951 | 300.1363 | 11.7189 | 20.3227 | 43.3559 | 25.1581
346.2542 | 231.5641 | 279.4803 | 300.8345 | 11.7436 | 20.4068 | 43.5092 | 25.2619
347.2542 | 230.1304 | 279.0132 | 300.7472 | 11.7795 | 20.5166 | 43.635 | 25.3428
348.2542 | 228.7167 | 279.7178 | 301.8528 | 11.8079 | 20.609 | 43.815 | 25.4421
349.2542 | 227.8351 | 279.4282 | 302.7514 | 11.8414 | 20.7096 | 43.9544 | 25.5212
350.2542 | 227.6568 | 279.1997 | 303.0173 | 11.8794 | 20.8088 | 44.0904 | 25.6115
351.2542 | 227.6419 | 278.6574 | 302.694 | 11.9143 | 20.9206 | 44.2305 | 25.6965
352.2542 | 226.8273 | 278.2347 | 302.1977 | 11.9548 | 21.0121 | 44.3873 | 25.7827
353.2542 | 227.2333 | 278.3019 | 301.276 | 11.981 | 21.0773 | 44.5008 | 25.8409
354.2542 | 227.5202 | 279.9036 | 299.9139 | 12.02 | 21.188 | 44.6605 | 25.9334
355.2542 | 226.3969 | 277.6063 | 296.8256 | 12.08 | 21.281 | 44.7996 | 26.034
356.2542 | 225.5008 | 276.2993 | 295.3986 | 12.1045 | 21.4062 | 44.967 | 26.122
357.2542 | 224.7498 | 276.2121 | 294.4663 | 12.1377 | 21.488 | 45.1211 | 26.2405
358.2542 | 224.9513 | 277.4184 | 293.1788 | 12.188 | 21.5707 | 45.2578 | 26.3009
359.2542 | 226.079 | 278.1207 | 292.5058 | 12.2292 | 21.6929 | 45.4127 | 26.4133
360.2542 | 228.036 | 278.9647 | 293.403 | 12.2597 | 21.7967 | 45.5601 | 26.4857
361.2542 | 226.6903 | 278.563 | 293.9427 | 12.3086 | 21.855 | 45.6774 | 26.5789
362.2542 | 225.6411 | 277.5083 | 294.1761 | 12.3304 | 21.9568 | 45.8532 | 26.6731
363.2542 | 225.9952 | 278.9435 | 295.3265 | 12.355 | 22.0232 | 46.0047 | 26.76
364.2542 | 226.2408 | 280.3317 | 295.78 | 12.4131 | 22.1347 | 46.142 | 26.8696
365.2542 | 227.5483 | 282.2379 | 295.6894 | 12.4553 | 22.2012 | 46.2814 | 26.9619
366.2542 | 226.9647 | 282.2991 | 297.3587 | 12.5059 | 22.2996 | 46.4428 | 27.0254
367.2542 | 228.7656 | 284.8513 | 298.0458 | 12.5394 | 22.3712 | 46.5552 | 27.1625
368.2542 | 231.0923 | 287.7427 | 301.7446 | 12.5777 | 22.4562 | 46.7284 | 27.2603
369.2542 | 232.7397 | 287.9898 | 301.5887 | 12.612 | 22.5442 | 46.8541 | 27.3559
370.2542 | 231.9523 | 288.7896 | 303.7036 | 12.6596 | 22.629 | 47.0032 | 27.4645
371.2542 | 233.556 | 287.9259 | 302.3782 | 12.6951 | 22.7151 | 47.1567 | 27.5726
372.2542 | 234.3979 | 288.3151 | 301.706 | 12.7292 | 22.779 | 47.2817 | 27.6577
373.2542 | 238.1129 | 290.6367 | 305.0614 | 12.784 | 22.8925 | 47.4658 | 27.7555
374.2542 | 238.338 | 290.1779 | 305.1476 | 12.8106 | 22.9752 | 47.6164 | 27.8696
375.2542 | 238.2059 | 290.9667 | 304.9824 | 12.8506 | 23.0755 | 47.7503 | 27.9648
376.2542 | 236.6658 | 291.9408 | 305.6753 | 12.8904 | 23.1508 | 47.8987 | 28.0321
377.2542 | 236.1217 | 290.3348 | 305.4301 | 12.9176 | 23.2332 | 48.0374 | 28.129
378.2542 | 238.7861 | 293.4418 | 306.6055 | 12.9851 | 23.3279 | 48.1905 | 28.2333
379.2542 | 239.3829 | 293.9545 | 306.8851 | 13.0139 | 23.4095 | 48.3374 | 28.3254
380.2542 | 238.82 | 292.9715 | 304.9112 | 13.0597 | 23.5153 | 48.4549 | 28.4426
381.2542 | 238.4307 | 293.1432 | 304.8717 | 13.0938 | 23.6327 | 48.6186 | 28.5383
382.2542 | 239.2516 | 293.1533 | 305.9759 | 13.1196 | 23.7267 | 48.7978 | 28.6226
383.2542 | 242.2007 | 295.6135 | 308.2568 | 13.1678 | 23.8327 | 48.9505 | 28.7081
384.2542 | 241.7881 | 295.4445 | 308.7545 | 13.2053 | 23.9454 | 49.1032 | 28.8096
385.2542 | 243.0201 | 296.318 | 309.5547 | 13.24 | 24.0236 | 49.25 | 28.8882
386.2542 | 244.8713 | 297.2049 | 310.3391 | 13.2988 | 24.1321 | 49.3748 | 29.0086
387.2542 | 247.6644 | 297.9014 | 311.3063 | 13.3435 | 24.2422 | 49.5455 | 29.0968
388.2542 | 249.285 | 298.9049 | 313.6229 | 13.387 | 24.3406 | 49.6826 | 29.2107
389.2542 | 248.5048 | 299.9061 | 312.6982 | 13.4126 | 24.4498 | 49.8524 | 29.2972
390.2542 | 248.6473 | 299.8917 | 313.3866 | 13.4635 | 24.5513 | 49.9866 | 29.4336
391.2542 | 248.7241 | 300.8006 | 312.6849 | 13.5008 | 24.6713 | 50.1376 | 29.5475
392.2542 | 246.7526 | 301.1135 | 314.3827 | 13.5359 | 24.7756 | 50.3232 | 29.6586
393.2542 | 245.7225 | 300.4039 | 314.9233 | 13.5851 | 24.8854 | 50.4839 | 29.7705
394.2542 | 244.2769 | 298.898 | 314.5156 | 13.6179 | 25.008 | 50.6333 | 29.8889
395.2542 | 246.0134 | 300.597 | 314.7442 | 13.6584 | 25.1105 | 50.7914 | 29.9921
396.2542 | 245.082 | 300.6537 | 315.1406 | 13.704 | 25.2223 | 50.9439 | 30.0768
397.2542 | 244.5548 | 300.4517 | 316.2084 | 13.7795 | 25.3412 | 51.0929 | 30.2037
398.2542 | 244.8463 | 299.3806 | 314.9347 | 13.786 | 25.4495 | 51.2625 | 30.3096
399.2542 | 244.1472 | 299.8228 | 313.8066 | 13.8393 | 25.5566 | 51.4314 | 30.4202
400.2542 | 244.5538 | 300.5612 | 314.0108 | 13.8882 | 25.6601 | 51.5688 | 30.5093
401.2542 | 243.7516 | 299.952 | 314.2898 | 13.9312 | 25.7722 | 51.728 | 30.6079
402.2542 | 243.0258 | 299.6204 | 313.7565 | 13.983 | 25.8613 | 51.8998 | 30.7016
403.2542 | 242.379 | 299.297 | 312.7746 | 14.0267 | 25.9822 | 52.0568 | 30.8064
404.2542 | 243.754 | 298.3869 | 313.1695 | 14.0743 | 26.0844 | 52.1978 | 30.9201
405.2542 | 244.5021 | 298.5264 | 312.3854 | 14.1253 | 26.1706 | 52.357 | 31.0343
406.2542 | 245.4697 | 299.5124 | 312.0906 | 14.1679 | 26.2565 | 52.5266 | 31.1444
407.2542 | 245.8066 | 297.6859 | 313.3406 | 14.2054 | 26.3716 | 52.6914 | 31.2446
408.2542 | 244.7447 | 297.3053 | 313.4683 | 14.2381 | 26.4653 | 52.8248 | 31.3461
409.2542 | 246.295 | 297.1768 | 312.962 | 14.3017 | 26.564 | 52.9692 | 31.4473
410.2542 | 246.9223 | 296.5333 | 311.5237 | 14.3477 | 26.6468 | 53.1544 | 31.5569
411.2542 | 246.3855 | 299.4285 | 313.5031 | 14.3827 | 26.7504 | 53.2667 | 31.656
412.2542 | 245.074 | 300.3302 | 313.2065 | 14.4227 | 26.8452 | 53.4214 | 31.7586
413.2542 | 243.6872 | 298.9357 | 311.9989 | 14.4851 | 26.9138 | 53.5976 | 31.8449
414.2542 | 243.8919 | 298.0559 | 311.6055 | 14.5196 | 27.0318 | 53.761 | 31.9261
415.2542 | 242.7962 | 298.5273 | 310.5477 | 14.553 | 27.1172 | 53.8899 | 32.0383
416.2542 | 243.381 | 299.4614 | 309.3595 | 14.6006 | 27.2163 | 54.0622 | 32.1369
417.2542 | 243.9179 | 300.6625 | 309.0864 | 14.6491 | 27.3173 | 54.2259 | 32.2445
418.2542 | 245.2967 | 301.5804 | 309.2255 | 14.7033 | 27.4245 | 54.3618 | 32.3495
419.2542 | 247.6098 | 301.9885 | 307.7004 | 14.743 | 27.5109 | 54.5058 | 32.466
420.2542 | 248.1388 | 303.9844 | 307.6086 | 14.7723 | 27.6126 | 54.6611 | 32.5606
421.2542 | 248.5818 | 303.8497 | 307.629 | 14.8363 | 27.7111 | 54.8078 | 32.6827
422.2542 | 247.0222 | 303.4051 | 307.0925 | 14.8743 | 27.7607 | 54.99 | 32.7903
423.2542 | 248.1663 | 303.6484 | 308.4188 | 14.9135 | 27.8455 | 55.13 | 32.9065
424.2542 | 248.186 | 303.4008 | 308.9767 | 14.9635 | 27.9673 | 55.2534 | 33.0364
425.2542 | 248.4438 | 303.9012 | 309.8488 | 15.0176 | 28.0791 | 55.4302 | 33.1696
426.2542 | 248.368 | 303.7812 | 310.7496 | 15.0537 | 28.1711 | 55.5763 | 33.2902
427.2542 | 247.5603 | 303.6683 | 311.6931 | 15.1125 | 28.2575 | 55.7239 | 33.4386
428.2542 | 248.2661 | 305.1404 | 312.1533 | 15.1645 | 28.3479 | 55.8728 | 33.5455
429.2542 | 247.8779 | 305.1843 | 313.0478 | 15.1969 | 28.4405 | 56.0211 | 33.6651
430.2542 | 248.1516 | 305.8646 | 313.8482 | 15.2394 | 28.5504 | 56.1967 | 33.7732
431.2542 | 248.4732 | 306.8557 | 313.6603 | 15.2939 | 28.6185 | 56.3277 | 33.8932
432.2542 | 250.8906 | 307.8135 | 313.4796 | 15.3369 | 28.7236 | 56.4979 | 33.9765
433.2542 | 250.7965 | 308.8339 | 314.0837 | 15.3634 | 28.7951 | 56.6619 | 34.088
434.2542 | 251.499 | 307.6889 | 314.369 | 15.436 | 28.9293 | 56.8281 | 34.2045
435.2542 | 250.2735 | 307.2689 | 314.7454 | 15.4872 | 29.0145 | 56.9724 | 34.3187
436.2542 | 248.9535 | 304.7266 | 314.9306 | 15.5309 | 29.1022 | 57.1311 | 34.4603
437.2542 | 247.3338 | 303.3129 | 314.8607 | 15.5798 | 29.1697 | 57.2693 | 34.5769
438.2542 | 246.8046 | 305.7653 | 314.7162 | 15.6176 | 29.2847 | 57.4075 | 34.7043
439.2542 | 248.4568 | 306.1633 | 314.191 | 15.6768 | 29.396 | 57.5766 | 34.7904
440.2542 | 248.4785 | 307.2351 | 314.5228 | 15.722 | 29.5027 | 57.7301 | 34.923
441.2542 | 248.6475 | 308.0441 | 315.4373 | 15.7689 | 29.6125 | 57.8812 | 35.0463
442.2542 | 247.9844 | 306.9227 | 317.0381 | 15.8176 | 29.7094 | 58.0369 | 35.1637
443.2542 | 248.5388 | 308.4426 | 317.1259 | 15.8677 | 29.8055 | 58.2145 | 35.2753
444.2542 | 250.6681 | 310.0007 | 319.808 | 15.9163 | 29.9058 | 58.3653 | 35.3964
445.2542 | 251.6061 | 310.474 | 322.1392 | 15.9439 | 29.9921 | 58.5 | 35.5094
446.2542 | 253.2563 | 312.1044 | 322.1454 | 16.0019 | 30.1212 | 58.6528 | 35.6196
447.2542 | 253.9557 | 312.6275 | 323.2347 | 16.0268 | 30.209 | 58.803 | 35.7195
448.2542 | 255.1643 | 314.4803 | 323.8405 | 16.0942 | 30.2966 | 58.9429 | 35.8365
449.2542 | 255.2071 | 314.1316 | 324.3159 | 16.1326 | 30.415 | 59.1033 | 35.9606
450.2542 | 255.9095 | 314.6983 | 326.2327 | 16.1735 | 30.489 | 59.2688 | 36.0683
451.2542 | 256.564 | 314.4572 | 325.275 | 16.2296 | 30.6395 | 59.4281 | 36.1768
452.2542 | 256.0049 | 314.0075 | 324.4786 | 16.2872 | 30.7351 | 59.5862 | 36.2922
453.2542 | 255.5447 | 313.0874 | 323.4082 | 16.3129 | 30.8205 | 59.752 | 36.3832
454.2542 | 255.4087 | 313.0519 | 322.9996 | 16.3794 | 30.9308 | 59.9109 | 36.4955
455.2542 | 257.4268 | 312.2259 | 322.9396 | 16.433 | 31.0395 | 60.0517 | 36.6199
456.2542 | 256.1503 | 311.6619 | 321.2797 | 16.4858 | 31.125 | 60.1891 | 36.7395
457.2542 | 256.0427 | 311.5971 | 320.3528 | 16.549 | 31.2471 | 60.3512 | 36.8827
458.2542 | 255.9599 | 311.6731 | 318.9979 | 16.6051 | 31.3263 | 60.4804 | 36.9811
459.2542 | 256.8276 | 311.0551 | 319.4643 | 16.6306 | 31.4451 | 60.664 | 37.1109
460.2542 | 257.6251 | 310.139 | 319.8338 | 16.7042 | 31.5343 | 60.7999 | 37.2302
461.2542 | 256.1595 | 310.0638 | 319.8599 | 16.739 | 31.6518 | 60.9691 | 37.3482
462.2542 | 256.2185 | 310.2183 | 320.6324 | 16.7847 | 31.7385 | 61.1269 | 37.4512
463.2542 | 255.6092 | 309.9196 | 320.4092 | 16.8381 | 31.8424 | 61.2453 | 37.6133
464.2542 | 256.3222 | 309.6813 | 320.4976 | 16.8952 | 31.9406 | 61.4152 | 37.7376
465.2542 | 256.0017 | 309.2118 | 320.213 | 16.9523 | 32.0304 | 61.5641 | 37.8598
466.2542 | 254.6189 | 308.7422 | 319.4965 | 17.0117 | 32.1487 | 61.7152 | 37.9865
467.2542 | 253.9032 | 309.1143 | 319.3814 | 17.0622 | 32.2522 | 61.8744 | 38.1186
468.2542 | 254.6916 | 309.2167 | 319.3131 | 17.0982 | 32.3549 | 62.0201 | 38.2368
469.2542 | 254.2484 | 310.4627 | 319.5674 | 17.1615 | 32.4417 | 62.1919 | 38.3535
470.2542 | 257.2352 | 311.6858 | 319.8784 | 17.2098 | 32.5425 | 62.3447 | 38.4921
471.2542 | 255.6358 | 311.8458 | 320.0053 | 17.252 | 32.6374 | 62.5025 | 38.6084
472.2542 | 256.3187 | 310.6307 | 319.4045 | 17.3111 | 32.7617 | 62.6526 | 38.7504
473.2542 | 259.0847 | 311.4562 | 318.4541 | 17.3966 | 32.866 | 62.8201 | 38.8686
474.2542 | 261.4228 | 311.65 | 317.7843 | 17.4263 | 32.9437 | 62.985 | 38.9992
475.2542 | 262.004 | 311.2791 | 317.5833 | 17.4732 | 33.0715 | 63.1094 | 39.1265
476.2542 | 261.7246 | 310.3348 | 316.1491 | 17.532 | 33.1568 | 63.2661 | 39.2609
477.2542 | 261.3936 | 309.7157 | 315.7704 | 17.5844 | 33.2772 | 63.4274 | 39.3785
478.2542 | 264.1521 | 308.9224 | 317.5124 | 17.6529 | 33.4179 | 63.5801 | 39.4886
479.2542 | 266.648 | 311.4432 | 320.9596 | 17.7304 | 33.5097 | 63.7477 | 39.6269
480.2542 | 268.2866 | 312.1185 | 320.9308 | 17.7733 | 33.6307 | 63.8839 | 39.7609
481.2542 | 267.5593 | 311.137 | 320.9026 | 17.7932 | 33.7446 | 64.0633 | 39.8965
482.2542 | 269.364 | 310.8372 | 319.948 | 17.8452 | 33.8383 | 64.223 | 40.0158
483.2542 | 268.2474 | 310.706 | 319.7037 | 17.9299 | 33.9506 | 64.3584 | 40.1447
484.2542 | 266.7464 | 310.6528 | 320.0954 | 17.9807 | 34.0713 | 64.5147 | 40.2667
485.2542 | 268.6038 | 310.8468 | 319.4484 | 18.0315 | 34.2076 | 64.6911 | 40.4215
486.2542 | 267.5048 | 310.8317 | 319.4938 | 18.0873 | 34.307 | 64.8444 | 40.5729
487.2542 | 265.2684 | 310.8179 | 319.7576 | 18.1436 | 34.4262 | 65.0027 | 40.7007
488.2542 | 263.3852 | 310.7042 | 319.0943 | 18.2124 | 34.546 | 65.1446 | 40.8359
489.2542 | 261.9641 | 311.0972 | 318.9991 | 18.2778 | 34.6856 | 65.3323 | 40.9682
490.2542 | 260.6648 | 311.0716 | 318.731 | 18.3325 | 34.8005 | 65.474 | 41.0989
491.2542 | 261.818 | 312.9166 | 319.5332 | 18.3926 | 34.9328 | 65.6375 | 41.2206
492.2542 | 261.8385 | 314.5963 | 319.6308 | 18.4505 | 35.0463 | 65.7671 | 41.3248
493.2542 | 262.6636 | 314.6059 | 319.3193 | 18.4902 | 35.1938 | 65.9412 | 41.4558
494.2542 | 263.9845 | 315.3582 | 319.1834 | 18.5863 | 35.3101 | 66.0829 | 41.5717
495.2542 | 265.8226 | 315.7029 | 320.4498 | 18.624 | 35.404 | 66.239 | 41.6967
496.2542 | 266.0462 | 315.865 | 321.5489 | 18.6922 | 35.5188 | 66.3966 | 41.8335
497.2542 | 265.8585 | 318.1371 | 322.2549 | 18.7389 | 35.6516 | 66.5468 | 41.9521
498.2542 | 265.4698 | 319.1742 | 323.6071 | 18.8146 | 35.7688 | 66.6839 | 42.063
499.2542 | 266.0118 | 319.7073 | 323.5633 | 18.8549 | 35.8808 | 66.8377 | 42.2046
500.2542 | 265.13 | 321.4394 | 325.1893 | 18.933 | 36.0001 | 66.995 | 42.3295
501.2542 | 266.3345 | 320.3323 | 325.0382 | 18.986 | 36.1354 | 67.1288 | 42.476
502.2542 | 265.8574 | 319.9501 | 324.0926 | 19.0512 | 36.2318 | 67.3011 | 42.596
503.2542 | 266.5859 | 320.4579 | 322.4261 | 19.1144 | 36.3577 | 67.4298 | 42.7321
504.2542 | 268.1721 | 321.0393 | 322.0007 | 19.158 | 36.4687 | 67.624 | 42.8573
505.2542 | 268.8788 | 320.4905 | 321.4592 | 19.2021 | 36.6159 | 67.7509 | 42.9667
506.2542 | 268.513 | 320.648 | 321.5365 | 19.2721 | 36.7176 | 67.9215 | 43.1139
507.2542 | 267.0541 | 319.1113 | 321.1172 | 19.3343 | 36.8336 | 68.0678 | 43.2477
508.2542 | 265.7615 | 318.4185 | 320.5366 | 19.407 | 36.9369 | 68.2031 | 43.3976
509.2542 | 265.5904 | 317.2757 | 319.8983 | 19.4463 | 37.0932 | 68.3672 | 43.5172
510.2542 | 267.1137 | 317.2065 | 319.1211 | 19.526 | 37.1981 | 68.5182 | 43.647
511.2542 | 268.0887 | 317.8295 | 319.4974 | 19.5968 | 37.3014 | 68.6432 | 43.7834
512.2542 | 269.4005 | 318.0644 | 318.2635 | 19.6591 | 37.4261 | 68.8131 | 43.9157
513.2542 | 272.5154 | 318.3135 | 319.4486 | 19.7134 | 37.5538 | 68.9623 | 44.0519
514.2542 | 275.1151 | 319.2907 | 319.3333 | 19.7778 | 37.6466 | 69.1063 | 44.1976
515.2542 | 273.3366 | 319.6341 | 318.6949 | 19.8216 | 37.754 | 69.2511 | 44.3326
516.2542 | 271.8787 | 317.8779 | 317.2535 | 19.8894 | 37.8758 | 69.3883 | 44.4549
517.2542 | 269.533 | 317.3871 | 316.673 | 19.9395 | 38.0049 | 69.5465 | 44.5935
518.2542 | 268.5744 | 316.9259 | 316.9783 | 19.9984 | 38.111 | 69.6898 | 44.7265
519.2542 | 267.0073 | 316.0876 | 316.381 | 20.0476 | 38.2358 | 69.8394 | 44.8599
520.2542 | 266.8218 | 315.5105 | 316.0235 | 20.1271 | 38.3523 | 69.9861 | 44.9801
521.2542 | 267.9561 | 315.7906 | 315.0591 | 20.1946 | 38.477 | 70.123 | 45.1238
522.2542 | 268.4714 | 316.1247 | 313.244 | 20.2499 | 38.5768 | 70.2808 | 45.2677
523.2542 | 271.3634 | 315.6671 | 313.8253 | 20.3267 | 38.6771 | 70.4222 | 45.3904
524.2542 | 272.1416 | 315.2481 | 315.0821 | 20.3846 | 38.8307 | 70.5733 | 45.5203
525.2542 | 271.6728 | 315.1349 | 315.5224 | 20.4363 | 38.9212 | 70.7231 | 45.6627
526.2542 | 271.3746 | 315.07 | 315.318 | 20.4975 | 39.0089 | 70.8804 | 45.8046
527.2542 | 272.1969 | 315.5168 | 316.3001 | 20.5697 | 39.145 | 70.9974 | 45.9603
528.2542 | 272.6446 | 315.7111 | 317.4244 | 20.6349 | 39.267 | 71.1628 | 46.0925
529.2542 | 272.1982 | 316.7446 | 318.7637 | 20.6858 | 39.3791 | 71.3129 | 46.2153
530.2542 | 271.5501 | 316.0173 | 318.848 | 20.756 | 39.488 | 71.4652 | 46.3738
531.2542 | 271.2821 | 313.8959 | 318.5765 | 20.8083 | 39.6057 | 71.6048 | 46.5033
532.2542 | 270.964 | 313.8628 | 317.9017 | 20.8962 | 39.7427 | 71.7444 | 46.6501
533.2542 | 272.7631 | 313.3603 | 316.9593 | 20.9473 | 39.8555 | 71.9028 | 46.7685
534.2542 | 272.2315 | 314.1807 | 316.7762 | 21.0079 | 39.9849 | 72.0266 | 46.9092
535.2542 | 272.2261 | 314.8283 | 316.3916 | 21.0748 | 40.1023 | 72.1981 | 47.0203
536.2542 | 271.0866 | 315.8577 | 316.5774 | 21.1254 | 40.2289 | 72.3448 | 47.1191
537.2542 | 271.1579 | 317.5994 | 317.9925 | 21.1949 | 40.3604 | 72.5207 | 47.2681
538.2542 | 272.9928 | 317.7808 | 317.4296 | 21.25 | 40.4623 | 72.6521 | 47.4044
539.2542 | 271.9952 | 317.026 | 317.1686 | 21.3292 | 40.608 | 72.8017 | 47.5498
540.2542 | 270.942 | 317.4091 | 317.5949 | 21.3907 | 40.7206 | 72.9602 | 47.6912
541.2542 | 271.0841 | 317.6665 | 317.5974 | 21.4586 | 40.8347 | 73.0818 | 47.8128
542.2542 | 269.924 | 317.6759 | 317.3531 | 21.5241 | 40.9591 | 73.2093 | 47.9804
543.2542 | 269.0477 | 317.0413 | 316.317 | 21.5957 | 41.0637 | 73.375 | 48.1115
544.2542 | 268.3141 | 318.4166 | 316.5742 | 21.6455 | 41.1921 | 73.54 | 48.2426
545.2542 | 267.899 | 318.972 | 317.6028 | 21.7109 | 41.3062 | 73.6944 | 48.374
546.2542 | 268.0547 | 318.5614 | 317.7929 | 21.7718 | 41.4166 | 73.8659 | 48.5266
547.2542 | 267.0878 | 317.8881 | 317.8203 | 21.8438 | 41.5523 | 73.9765 | 48.6712
548.2542 | 267.3562 | 317.2717 | 317.5656 | 21.91 | 41.6625 | 74.1146 | 48.8106
549.2542 | 268.9901 | 318.3881 | 318.4517 | 21.9867 | 41.7711 | 74.2843 | 48.9323
550.2542 | 269.3324 | 318.0661 | 318.9709 | 22.0376 | 41.9101 | 74.4323 | 49.0579
551.2542 | 269.3238 | 318.5159 | 318.7446 | 22.091 | 42.0135 | 74.5818 | 49.1708
552.2542 | 268.99 | 319.2099 | 319.2154 | 22.1572 | 42.1505 | 74.728 | 49.3103
553.2542 | 271.0158 | 318.8353 | 319.7065 | 22.2043 | 42.2596 | 74.8714 | 49.4384
554.2542 | 271.1839 | 318.2424 | 319.4748 | 22.3025 | 42.3916 | 75.017 | 49.5403
555.2542 | 270.8874 | 317.4192 | 319.5678 | 22.3526 | 42.5168 | 75.1674 | 49.6796
556.2542 | 272.3865 | 317.8127 | 321.6631 | 22.4281 | 42.6264 | 75.3253 | 49.7913
557.2542 | 273.7879 | 318.1161 | 320.752 | 22.4807 | 42.7359 | 75.4834 | 49.9344
558.2542 | 271.9899 | 316.5228 | 320.4429 | 22.542 | 42.8715 | 75.62 | 50.0568
559.2542 | 272.2667 | 317.3951 | 319.7155 | 22.6152 | 42.9885 | 75.7818 | 50.1793
560.2542 | 273.836 | 318.3752 | 322.1721 | 22.698 | 43.118 | 75.9211 | 50.3334
561.2542 | 274.5832 | 318.9334 | 321.7856 | 22.7626 | 43.2289 | 76.0634 | 50.4576
562.2542 | 274.1816 | 317.904 | 320.9825 | 22.8296 | 43.3828 | 76.2181 | 50.5983
563.2542 | 273.2102 | 317.6369 | 320.1729 | 22.893 | 43.5031 | 76.3594 | 50.7332
564.2542 | 272.5469 | 318.2379 | 320.0914 | 22.9525 | 43.6206 | 76.5318 | 50.8605
565.2542 | 271.5939 | 318.4885 | 319.2402 | 23.0213 | 43.7522 | 76.6834 | 50.9867
566.2542 | 271.4319 | 318.6491 | 318.7259 | 23.0935 | 43.884 | 76.8351 | 51.1224
567.2542 | 273.2615 | 318.915 | 319.6852 | 23.1492 | 44.0128 | 76.9917 | 51.2412
568.2542 | 275.1048 | 319.8534 | 320.8161 | 23.2368 | 44.1425 | 77.118 | 51.3849
569.2542 | 277.3224 | 319.7083 | 321.7968 | 23.2945 | 44.2435 | 77.2546 | 51.5293
570.2542 | 276.6632 | 319.9851 | 320.6624 | 23.3511 | 44.3922 | 77.4111 | 51.6778
571.2542 | 279.154 | 320.4159 | 321.467 | 23.4369 | 44.5297 | 77.58 | 51.8184
572.2542 | 280.8283 | 320.2317 | 323.6685 | 23.4775 | 44.6475 | 77.7238 | 51.9423
573.2542 | 281.7283 | 320.8392 | 322.3043 | 23.5608 | 44.7711 | 77.8662 | 52.1028
574.2542 | 280.9835 | 321.0095 | 321.8867 | 23.6188 | 44.9155 | 78.0252 | 52.2319
575.2542 | 282.2694 | 320.3806 | 321.3325 | 23.699 | 45.0701 | 78.1774 | 52.3575
576.2542 | 280.5884 | 319.984 | 320.3407 | 23.7654 | 45.1868 | 78.3169 | 52.4886
577.2542 | 279.26 | 319.1755 | 319.8 | 23.8212 | 45.3182 | 78.4826 | 52.6144
578.2542 | 280.1085 | 318.8321 | 321.387 | 23.8918 | 45.4775 | 78.6456 | 52.7507
579.2542 | 279.0545 | 319.6882 | 321.1769 | 23.9691 | 45.5908 | 78.7878 | 52.8896
580.2542 | 277.7217 | 319.4737 | 322.8182 | 24.033 | 45.7647 | 78.9509 | 53.0294
581.2542 | 277.5498 | 319.6328 | 323.7509 | 24.1013 | 45.8935 | 79.1038 | 53.1483
582.2542 | 277.4689 | 320.1335 | 325.6468 | 24.1586 | 46.0267 | 79.2588 | 53.2658
583.2542 | 276.8263 | 321.1566 | 327.0249 | 24.2426 | 46.1804 | 79.3951 | 53.3891
584.2542 | 275.9221 | 321.2783 | 326.9122 | 24.303 | 46.3259 | 79.5412 | 53.5122
585.2542 | 274.7803 | 320.2232 | 326.9156 | 24.3711 | 46.4604 | 79.6915 | 53.6314
586.2542 | 273.989 | 319.0001 | 324.5816 | 24.45 | 46.6055 | 79.831 | 53.7493
587.2542 | 274.7782 | 319.8069 | 324.0771 | 24.5147 | 46.7332 | 79.9862 | 53.8392
588.2542 | 274.6127 | 320.3944 | 324.0738 | 24.5789 | 46.8653 | 80.1365 | 53.98
589.2542 | 274.1792 | 320.1423 | 323.1541 | 24.6566 | 46.9853 | 80.2948 | 54.0828
590.2542 | 273.3661 | 319.942 | 323.4918 | 24.7305 | 47.1187 | 80.454 | 54.2375
591.2542 | 273.3016 | 320.266 | 324.4106 | 24.8015 | 47.2584 | 80.5862 | 54.376
592.2542 | 273.4541 | 321.0457 | 324.5055 | 24.8781 | 47.3837 | 80.7361 | 54.5127
593.2542 | 273.4413 | 321.4217 | 324.8792 | 24.9288 | 47.528 | 80.8566 | 54.6337
594.2542 | 274.3581 | 322.4007 | 324.4825 | 25.0195 | 47.6584 | 81.0113 | 54.7643
595.2542 | 275.5679 | 323.1469 | 324.753 | 25.0669 | 47.7742 | 81.1663 | 54.8879
596.2542 | 275.8261 | 323.5595 | 324.9294 | 25.1035 | 47.8967 | 81.3212 | 55.0123
597.2542 | 277.5585 | 323.8085 | 324.2375 | 25.2066 | 48.0302 | 81.4804 | 55.1362
598.2542 | 276.9279 | 324.1177 | 323.3226 | 25.2574 | 48.1618 | 81.618 | 55.2683
599.2542 | 277.6496 | 324.3312 | 322.271 | 25.3364 | 48.2798 | 81.7563 | 55.3935
600.2542 | 279.0167 | 325.426 | 323.5317 | 25.4107 | 48.4117 | 81.8973 | 55.5108
601.2542 | 279.6519 | 325.5092 | 324.2233 | 25.4751 | 48.552 | 82.0628 | 55.8088
602.2542 | 281.9877 | 326.5887 | 324.6124 | 25.559 | 48.6849 | 82.193 | 56.2322
603.2542 | 281.9272 | 327.4453 | 326.2073 | 25.5764 | 48.8119 | 82.3445 | 56.4745
604.2542 | 281.333 | 328.1578 | 327.1078 | 25.6804 | 48.9072 | 82.4825 | 56.587
605.2542 | 282.4991 | 330.047 | 326.2245 | 25.7563 | 49.0383 | 82.6318 | 56.6829
606.2542 | 282.2261 | 329.9908 | 325.1179 | 25.8196 | 49.171 | 82.7979 | 56.7831
607.2542 | 283.913 | 330.7995 | 324.9175 | 25.9244 | 49.3207 | 82.9185 | 56.9225
608.2542 | 284.4974 | 329.6692 | 323.6685 | 25.9577 | 49.4371 | 83.0731 | 57.027
609.2542 | 285.0031 | 330.2587 | 322.4009 | 26.0327 | 49.5802 | 83.2209 | 57.1441
610.2542 | 285.9274 | 330.1043 | 322.0361 | 26.1072 | 49.7215 | 83.379 | 57.2697
611.2542 | 284.502 | 328.8493 | 321.0585 | 26.1859 | 49.8662 | 83.5411 | 57.422
612.2542 | 284.2595 | 328.8013 | 320.7012 | 26.2579 | 50.0015 | 83.6654 | 57.5475
613.2542 | 283.3947 | 328.6129 | 320.9322 | 26.3193 | 50.1302 | 83.8116 | 57.659
614.2542 | 283.3951 | 328.8562 | 321.5775 | 26.4018 | 50.2603 | 83.9537 | 57.7775
615.2542 | 283.478 | 328.7651 | 321.8828 | 26.4554 | 50.4037 | 84.1097 | 57.8962
616.2542 | 284.0665 | 328.0059 | 320.9782 | 26.5348 | 50.5414 | 84.2525 | 58.0354
617.2542 | 283.1448 | 328.3759 | 320.3317 | 26.6004 | 50.6558 | 84.4034 | 58.1405
618.2542 | 283.5874 | 326.5196 | 318.4823 | 26.664 | 50.7904 | 84.5559 | 58.2913
619.2542 | 283.6148 | 326.3366 | 317.9731 | 26.744 | 50.9072 | 84.6902 | 58.3978
620.2542 | 284.6288 | 326.1911 | 319.8543 | 26.8059 | 51.0491 | 84.8421 | 58.5272
621.2542 | 283.9575 | 326.1873 | 319.6205 | 26.8829 | 51.1696 | 84.9798 | 58.6331
622.2542 | 283.5275 | 325.0829 | 319.7847 | 26.9482 | 51.2735 | 85.1285 | 58.7636
623.2542 | 282.7459 | 324.8025 | 320.3585 | 27.0248 | 51.412 | 85.2739 | 58.8818
624.2542 | 281.9481 | 325.0705 | 321.1625 | 27.1073 | 51.5304 | 85.401 | 59.0284
625.2542 | 282.0137 | 324.2365 | 320.3547 | 27.1576 | 51.6373 | 85.5568 | 59.1659
626.2542 | 282.3906 | 324.4761 | 319.9636 | 27.2461 | 51.7856 | 85.7022 | 59.2953
627.2542 | 281.9174 | 325.2924 | 319.5211 | 27.3151 | 51.9058 | 85.8521 | 59.4197
628.2542 | 281.6945 | 325.4899 | 319.3957 | 27.3836 | 52.0245 | 85.9828 | 59.5408
629.2542 | 281.2224 | 325.8221 | 319.8369 | 27.4508 | 52.1567 | 86.1417 | 59.6855
630.2542 | 281.9111 | 325.9199 | 320.7352 | 27.5389 | 52.2723 | 86.3046 | 59.8241
631.2542 | 282.0537 | 327.4211 | 321.5596 | 27.6163 | 52.4036 | 86.4384 | 59.9424
632.2542 | 283.8122 | 327.953 | 323.8934 | 27.6618 | 52.5364 | 86.5879 | 60.0611
633.2542 | 286.051 | 327.9572 | 324.1652 | 27.743 | 52.6864 | 86.7206 | 60.1858
634.2542 | 284.8816 | 328.7566 | 324.3296 | 27.8079 | 52.7857 | 86.8735 | 60.3031
635.2542 | 284.8938 | 328.9766 | 323.4722 | 27.8752 | 52.9106 | 87.0209 | 60.3912
636.2542 | 283.9735 | 329.5572 | 323.2765 | 27.9257 | 53.0503 | 87.1751 | 60.5231
637.2542 | 284.6049 | 329.3717 | 322.7726 | 28.031 | 53.1837 | 87.3213 | 60.6153
638.2542 | 285.2296 | 329.0868 | 323.8452 | 28.0894 | 53.3316 | 87.4783 | 60.7321
639.2542 | 283.3346 | 328.4746 | 324.9088 | 28.182 | 53.4485 | 87.6173 | 60.8758
640.2542 | 282.1453 | 326.9751 | 323.9095 | 28.2517 | 53.5703 | 87.7637 | 60.9868
641.2542 | 281.8393 | 326.9141 | 323.9879 | 28.2961 | 53.7255 | 87.9218 | 61.0934
642.2542 | 283.1996 | 327.4298 | 323.7728 | 28.4048 | 53.8599 | 88.078 | 61.2088
643.2542 | 284.4755 | 329.886 | 325.9208 | 28.484 | 53.9887 | 88.2156 | 61.3117
644.2542 | 283.8741 | 329.6411 | 325.1136 | 28.5419 | 54.1249 | 88.3594 | 61.4046
645.2542 | 283.5936 | 328.977 | 325.1088 | 28.614 | 54.2534 | 88.504 | 61.5454
646.2542 | 283.8631 | 328.6063 | 324.4812 | 28.6678 | 54.3919 | 88.6573 | 61.6675
647.2542 | 283.9799 | 328.2243 | 323.3038 | 28.7695 | 54.5338 | 88.8229 | 61.7786
648.2542 | 283.6577 | 327.0549 | 322.3383 | 28.831 | 54.6874 | 88.9828 | 61.8951
649.2542 | 284.5174 | 326.4841 | 322.9777 | 28.9241 | 54.8266 | 89.1154 | 62.0124
650.2542 | 284.8959 | 327.4918 | 323.2735 | 28.9866 | 54.9444 | 89.2603 | 62.1364
651.2542 | 285.9111 | 328.444 | 323.6906 | 29.0708 | 55.0988 | 89.4322 | 62.2593
652.2542 | 285.4747 | 327.9687 | 323.6139 | 29.1261 | 55.2299 | 89.5702 | 62.3665
653.2542 | 285.9267 | 327.8238 | 323.7898 | 29.201 | 55.3681 | 89.724 | 62.4801
654.2542 | 285.0473 | 326.6464 | 323.2284 | 29.2749 | 55.5028 | 89.8851 | 62.6053
655.2542 | 284.8784 | 326.1588 | 322.414 | 29.3711 | 55.6385 | 90.0226 | 62.744
656.2542 | 284.2901 | 325.6 | 322.5303 | 29.4211 | 55.7691 | 90.1875 | 62.8482
657.2542 | 284.0206 | 325.5644 | 322.2006 | 29.4993 | 55.9072 | 90.3339 | 62.9592
658.2542 | 283.7346 | 325.5117 | 322.214 | 29.5879 | 56.0458 | 90.461 | 63.0742
659.2542 | 282.72 | 325.2244 | 323.0266 | 29.6677 | 56.1676 | 90.6277 | 63.2017
660.2542 | 282.3961 | 326.5824 | 324.2316 | 29.7208 | 56.3061 | 90.7977 | 63.3276
661.2542 | 281.49 | 325.0543 | 323.1321 | 29.8029 | 56.4533 | 90.9445 | 63.46
662.2542 | 281.1942 | 324.1623 | 321.8631 | 29.8831 | 56.5874 | 91.0811 | 63.5667
663.2542 | 281.7979 | 324.648 | 322.1227 | 30.0268 | 56.7208 | 91.2128 | 63.7104
664.2542 | 282.558 | 325.2119 | 322.5314 | 30.0968 | 56.8468 | 91.3631 | 63.8381
665.2542 | 282.1726 | 325.89 | 323.083 | 30.1835 | 56.9808 | 91.5345 | 63.9778
666.2542 | 282.1098 | 326.052 | 321.8195 | 30.2443 | 57.1078 | 91.6594 | 64.0955
667.2542 | 281.2809 | 326.2703 | 323.3531 | 30.3392 | 57.2437 | 91.8184 | 64.2339
668.2542 | 280.4353 | 325.9303 | 324.1183 | 30.4171 | 57.373 | 91.9587 | 64.3844
669.2542 | 279.7405 | 328.377 | 325.1054 | 30.4888 | 57.5197 | 92.1238 | 64.4953
670.2542 | 279.6414 | 329.6137 | 324.22 | 30.5771 | 57.6506 | 92.258 | 64.6173
671.2542 | 279.7826 | 330.7708 | 325.4323 | 30.6465 | 57.7656 | 92.402 | 64.7299
672.2542 | 279.7254 | 329.6626 | 326.7132 | 30.7089 | 57.8881 | 92.5546 | 64.8492
673.2542 | 279.7026 | 329.4961 | 327.952 | 30.7905 | 58.0478 | 92.7001 | 64.9663
674.2542 | 280.2678 | 328.1222 | 327.9801 | 30.8727 | 58.162 | 92.8728 | 65.1063
675.2542 | 279.7944 | 328.9775 | 328.1277 | 30.9323 | 58.3167 | 92.9921 | 65.2068
676.2542 | 282.3856 | 329.2833 | 328.8227 | 31.017 | 58.4611 | 93.1702 | 65.3313
677.2542 | 282.7796 | 329.7006 | 329.0894 | 31.0873 | 58.5929 | 93.3189 | 65.4471
678.2542 | 282.7682 | 330.1466 | 328.788 | 31.1694 | 58.7165 | 93.4798 | 65.5644
679.2542 | 282.2166 | 327.5328 | 327.3854 | 31.25 | 58.8726 | 93.615 | 65.6857
680.2542 | 282.1059 | 327.5979 | 326.2573 | 31.3263 | 59.015 | 93.7659 | 65.8093
681.2542 | 281.8751 | 328.6574 | 326.4872 | 31.3881 | 59.1748 | 93.9137 | 65.9044
682.2542 | 283.568 | 329.6403 | 326.8648 | 31.4844 | 59.323 | 94.066 | 66.0339
683.2542 | 283.3538 | 329.543 | 326.5745 | 31.5583 | 59.4755 | 94.2187 | 66.1669
684.2542 | 283.705 | 329.9263 | 327.1912 | 31.6447 | 59.6294 | 94.3609 | 66.2887
685.2542 | 285.0037 | 331.4706 | 327.6323 | 31.7245 | 59.7599 | 94.5293 | 66.4115
686.2542 | 286.0339 | 333.1096 | 329.6606 | 31.8005 | 59.919 | 94.6731 | 66.5464
687.2542 | 285.031 | 333.3265 | 330.292 | 31.8503 | 60.0685 | 94.8176 | 66.6448
688.2542 | 283.6358 | 332.0485 | 329.9356 | 31.9491 | 60.2092 | 94.9745 | 66.7978
689.2542 | 283.7052 | 331.4739 | 329.7738 | 32.0297 | 60.3453 | 95.1139 | 66.909
690.2542 | 284.5397 | 331.5641 | 329.5061 | 32.105 | 60.5101 | 95.2793 | 67.0515
691.2542 | 284.0465 | 330.4267 | 328.6405 | 32.1751 | 60.6594 | 95.4236 | 67.1625
692.2542 | 283.0325 | 330.0979 | 328.2915 | 32.2419 | 60.808 | 95.5611 | 67.286
693.2542 | 283.7609 | 329.6687 | 327.8809 | 32.3372 | 60.9637 | 95.7194 | 67.415
694.2542 | 284.7183 | 330.1843 | 328.8312 | 32.4069 | 61.1169 | 95.8764 | 67.5451
695.2542 | 284.303 | 330.3032 | 328.072 | 32.4832 | 61.2512 | 96.021 | 67.6857
696.2542 | 283.8592 | 330.538 | 327.2322 | 32.5775 | 61.4087 | 96.1659 | 67.7984
697.2542 | 283.1673 | 330.7092 | 325.6569 | 32.6542 | 61.5577 | 96.3151 | 67.9219
698.2542 | 284.0829 | 331.0009 | 325.7227 | 32.7424 | 61.7028 | 96.4745 | 68.0554
699.2542 | 286.8297 | 331.844 | 326.9567 | 32.8272 | 61.8585 | 96.6248 | 68.1927
700.2542 | 288.6544 | 332.7418 | 327.3444 | 32.9006 | 62.0049 | 96.7756 | 68.3169
701.2542 | 291.0272 | 333.3597 | 327.254 | 32.9867 | 62.1604 | 96.9245 | 68.4588
702.2542 | 290.4461 | 333.9407 | 327.9217 | 33.0716 | 62.305 | 97.0676 | 68.5744
703.2542 | 291.7343 | 333.983 | 327.296 | 33.1505 | 62.4558 | 97.2277 | 68.7135
704.2542 | 292.8646 | 334.6084 | 328.485 | 33.2238 | 62.615 | 97.3806 | 68.8342
705.2542 | 292.7929 | 336.0997 | 327.885 | 33.3129 | 62.7525 | 97.5222 | 68.9584
706.2542 | 292.2352 | 336.64 | 328.6055 | 33.3886 | 62.9172 | 97.6719 | 69.0586
707.2542 | 291.9806 | 337.2172 | 330.1316 | 33.4788 | 63.0734 | 97.8214 | 69.2001
708.2542 | 290.4551 | 337.5559 | 329.4128 | 33.5518 | 63.2051 | 97.983 | 69.3263
709.2542 | 290.9382 | 337.8012 | 330.0626 | 33.658 | 63.3835 | 98.0965 | 69.4539
710.2542 | 292.2663 | 337.688 | 330.0772 | 33.7336 | 63.5288 | 98.2681 | 69.568
711.2542 | 291.9669 | 337.5942 | 330.3139 | 33.8109 | 63.6666 | 98.3957 | 69.6947
712.2542 | 292.5663 | 336.747 | 330.038 | 33.8909 | 63.8335 | 98.5537 | 69.8302
713.2542 | 292.6887 | 336.1547 | 330.4356 | 33.9722 | 63.9867 | 98.6913 | 69.9435
714.2542 | 291.7385 | 335.0551 | 330.4428 | 34.0629 | 64.1345 | 98.8459 | 70.0903
715.2542 | 290.9334 | 334.8555 | 330.7673 | 34.1522 | 64.2804 | 99.0055 | 70.2383
716.2542 | 291.2338 | 335.3232 | 331.1918 | 34.2431 | 64.4385 | 99.1406 | 70.4004
717.2542 | 291.3765 | 334.2252 | 330.8097 | 34.312 | 64.6013 | 99.2774 | 70.5449
718.2542 | 289.9108 | 333.6202 | 330.953 | 34.3977 | 64.7537 | 99.4362 | 70.6879
719.2542 | 288.5443 | 332.6169 | 330.944 | 34.4837 | 64.9089 | 99.6003 | 70.8299
720.2542 | 288.531 | 332.2143 | 330.1025 | 34.5676 | 65.0718 | 99.727 | 70.975
721.2542 | 288.0703 | 333.803 | 330.5045 | 34.6564 | 65.2188 | 99.8744 | 71.1298
722.2542 | 287.6821 | 334.5415 | 331.1879 | 34.7426 | 65.3777 | 100.0217 | 71.2605
723.2542 | 288.1569 | 334.4183 | 331.2056 | 34.8136 | 65.5254 | 100.1525 | 71.4119
724.2542 | 288.1666 | 333.5737 | 330.5777 | 34.9028 | 65.6879 | 100.3089 | 71.5499
725.2542 | 287.8242 | 333.6124 | 330.0472 | 34.9902 | 65.8221 | 100.4536 | 71.6649
726.2542 | 288.6983 | 333.4292 | 329.1719 | 35.0855 | 65.9712 | 100.5963 | 71.8114
727.2542 | 288.06 | 333.6197 | 329.6425 | 35.1542 | 66.1304 | 100.7307 | 71.9314
728.2542 | 287.2174 | 333.7165 | 329.9763 | 35.2435 | 66.291 | 100.888 | 72.0545
729.2542 | 286.8113 | 335.4745 | 329.9764 | 35.3289 | 66.4529 | 101.0322 | 72.2015
730.2542 | 287.4454 | 335.8228 | 330.0406 | 35.398 | 66.6092 | 101.1712 | 72.3186
731.2542 | 289.242 | 335.7811 | 330.1647 | 35.5181 | 66.7737 | 101.3213 | 72.4744
732.2542 | 290.1801 | 336.5268 | 330.3537 | 35.5611 | 66.9184 | 101.4604 | 72.6016
733.2542 | 291.7827 | 337.8285 | 332.1519 | 35.6718 | 67.0895 | 101.6039 | 72.7468
734.2542 | 290.6033 | 336.7916 | 333.0386 | 35.7611 | 67.2513 | 101.7392 | 72.8857
735.2542 | 290.6967 | 336.2126 | 333.1752 | 35.8492 | 67.4109 | 101.8859 | 73.0101
736.2542 | 293.0863 | 336.6613 | 333.7381 | 35.9456 | 67.5788 | 102.0279 | 73.144
737.2542 | 294.4679 | 336.8027 | 335.3192 | 36.0368 | 67.7502 | 102.1665 | 73.277
738.2542 | 293.3618 | 336.4157 | 335.0763 | 36.1158 | 67.9186 | 102.3108 | 73.3967
739.2542 | 292.1191 | 335.7371 | 333.5034 | 36.2019 | 68.0767 | 102.4422 | 73.5179
740.2542 | 292.3593 | 336.8987 | 333.2534 | 36.2775 | 68.2364 | 102.6006 | 73.663
741.2542 | 293.9644 | 338.2102 | 333.5362 | 36.3857 | 68.4084 | 102.7289 | 73.7695
742.2542 | 296.1521 | 338.0544 | 333.4458 | 36.4534 | 68.5804 | 102.8649 | 73.8822
743.2542 | 299.025 | 338.1178 | 333.7747 | 36.5455 | 68.7452 | 102.991 | 74.0019
744.2542 | 300.4708 | 338.7953 | 334.7354 | 36.6369 | 68.9093 | 103.1341 | 74.1269
745.2542 | 299.0254 | 338.7462 | 335.054 | 36.7314 | 69.0713 | 103.2832 | 74.2911
746.2542 | 297.6552 | 338.9472 | 336.1245 | 36.8116 | 69.2478 | 103.4136 | 74.4145
747.2542 | 296.7828 | 339.3994 | 336.1981 | 36.9007 | 69.4167 | 103.5433 | 74.5652
748.2542 | 299.252 | 339.5253 | 336.6676 | 36.9986 | 69.5684 | 103.6702 | 74.7167
749.2542 | 301.2559 | 339.2568 | 337.2597 | 37.0873 | 69.7408 | 103.8222 | 74.8595
750.2542 | 300.0952 | 340.4376 | 338.0656 | 37.163 | 69.9 | 103.9571 | 74.9949
751.2542 | 302.0254 | 340.492 | 339.5729 | 37.2765 | 70.0781 | 104.069 | 75.1297
752.2542 | 301.2599 | 341.0887 | 339.5546 | 37.3571 | 70.2405 | 104.2042 | 75.2526
753.2542 | 301.1882 | 340.9769 | 339.7896 | 37.4392 | 70.3917 | 104.3449 | 75.39
754.2542 | 300.3234 | 341.0015 | 339.7666 | 37.5419 | 70.5509 | 104.4641 | 75.5236
755.2542 | 299.2667 | 341.1529 | 339.7458 | 37.6205 | 70.7212 | 104.6078 | 75.6395
756.2542 | 297.2824 | 341.0461 | 340.1579 | 37.7024 | 70.881 | 104.7224 | 75.7532
757.2542 | 295.2528 | 340.4496 | 339.6459 | 37.7948 | 71.0482 | 104.857 | 75.8643
758.2542 | 293.7 | 340.0451 | 339.7232 | 37.8924 | 71.2152 | 104.9777 | 75.984
759.2542 | 293.0044 | 339.3693 | 339.6625 | 37.9917 | 71.383 | 105.1027 | 76.1104
760.2542 | 294.4779 | 340.0023 | 340.6118 | 38.0576 | 71.5479 | 105.2387 | 76.2315
761.2542 | 293.9308 | 339.4904 | 341.4505 | 38.1538 | 71.7159 | 105.3436 | 76.3511
762.2542 | 293.6608 | 338.6394 | 341.6243 | 38.262 | 71.8857 | 105.4964 | 76.4928
763.2542 | 295.754 | 338.9749 | 341.9222 | 38.3427 | 72.0492 | 105.6236 | 76.5833
764.2542 | 296.5413 | 339.1051 | 341.8112 | 38.4359 | 72.2035 | 105.7429 | 76.7117
765.2542 | 294.8747 | 338.5732 | 341.7238 | 38.5173 | 72.3644 | 105.8802 | 76.82
766.2542 | 293.0011 | 336.9139 | 341.6945 | 38.6067 | 72.5257 | 106.0043 | 76.9618
767.2542 | 291.2721 | 335.7217 | 341.0922 | 38.7028 | 72.7028 | 106.1344 | 77.0594
768.2542 | 290.0315 | 334.1697 | 340.4598 | 38.7928 | 72.86 | 106.2754 | 77.1862
769.2542 | 288.9463 | 333.8153 | 339.7642 | 38.8806 | 73.017 | 106.4165 | 77.3103
770.2542 | 288.227 | 333.8697 | 339.5458 | 38.9907 | 73.1748 | 106.5107 | 77.4286
771.2542 | 287.2866 | 335.0566 | 340.0387 | 39.0615 | 73.3303 | 106.6472 | 77.554
772.2542 | 286.19 | 334.175 | 340.1989 | 39.1707 | 73.5003 | 106.7882 | 77.6735
773.2542 | 286.5651 | 335.3623 | 340.0213 | 39.2561 | 73.6599 | 106.9214 | 77.7943
774.2542 | 285.4411 | 335.378 | 340.9577 | 39.3479 | 73.816 | 107.0276 | 77.8965
775.2542 | 285.3948 | 335.6715 | 340.9921 | 39.4296 | 73.9803 | 107.1534 | 78.0118
776.2542 | 284.9801 | 335.6994 | 340.6724 | 39.5213 | 74.1263 | 107.3061 | 78.1453
777.2542 | 283.8171 | 334.7572 | 340.0488 | 39.5939 | 74.2783 | 107.4349 | 78.2542
778.2542 | 282.9254 | 333.7435 | 338.3313 | 39.6906 | 74.4301 | 107.5404 | 78.3833
779.2542 | 281.8163 | 333.326 | 337.6552 | 39.7729 | 74.5779 | 107.6635 | 78.5074
780.2542 | 281.4719 | 332.7894 | 336.4814 | 39.8627 | 74.7298 | 107.806 | 78.6267
781.2542 | 280.9659 | 332.9424 | 337.3548 | 39.9447 | 74.8768 | 107.9241 | 78.7473
782.2542 | 280.7955 | 333.1784 | 337.3809 | 40.0676 | 75.0287 | 108.0435 | 78.8716
783.2542 | 281.1769 | 334.9123 | 336.7755 | 40.1304 | 75.1685 | 108.1824 | 78.991
784.2542 | 281.5464 | 335.2724 | 336.1277 | 40.2247 | 75.312 | 108.3033 | 79.104
785.2542 | 281.8036 | 334.7672 | 335.4441 | 40.3131 | 75.4531 | 108.4308 | 79.2208
786.2542 | 281.2124 | 334.454 | 335.45 | 40.3978 | 75.5851 | 108.5542 | 79.3647
787.2542 | 280.6298 | 334.5286 | 333.8035 | 40.4648 | 75.722 | 108.6855 | 79.4749
788.2542 | 279.4374 | 335.1144 | 334.2518 | 40.5644 | 75.867 | 108.8158 | 79.6007
789.2542 | 279.6297 | 335.4214 | 333.6111 | 40.6534 | 76.0053 | 108.9436 | 79.7074
790.2542 | 279.2501 | 335.5022 | 333.0364 | 40.7407 | 76.1422 | 109.0712 | 79.8211
791.2542 | 279.545 | 336.7474 | 333.8318 | 40.8445 | 76.2862 | 109.2255 | 79.9607
792.2542 | 280.223 | 337.1121 | 334.6817 | 40.9246 | 76.4229 | 109.3515 | 80.089
793.2542 | 278.8989 | 337.7976 | 334.9186 | 41.0123 | 76.5604 | 109.4691 | 80.2088
794.2542 | 278.7825 | 336.2176 | 335.3174 | 41.0835 | 76.6856 | 109.6151 | 80.3337
795.2542 | 277.4564 | 335.0064 | 333.9038 | 41.1751 | 76.8182 | 109.7321 | 80.4627
796.2542 | 276.8297 | 333.6405 | 332.9667 | 41.259 | 76.9505 | 109.8598 | 80.6023
797.2542 | 277.4447 | 332.9728 | 333.1945 | 41.3612 | 77.0879 | 109.9978 | 80.7332
798.2542 | 277.5014 | 332.3165 | 333.932 | 41.4365 | 77.2208 | 110.1226 | 80.8588
799.2542 | 277.4984 | 331.9041 | 332.3819 | 41.5295 | 77.3556 | 110.2341 | 80.9823
800.2542 | 277.7667 | 332.2915 | 332.5637 | 41.6151 | 77.4899 | 110.3901 | 81.1233
801.2542 | 277.6021 | 332.2348 | 332.4686 | 41.6952 | 77.6273 | 110.5196 | 81.2408
802.2542 | 277.0395 | 332.878 | 332.0117 | 41.7603 | 77.7665 | 110.6437 | 81.3791
803.2542 | 276.9623 | 332.1971 | 331.1904 | 41.8698 | 77.8976 | 110.7642 | 81.5163
804.2542 | 277.9178 | 331.8287 | 331.9984 | 41.9586 | 78.0375 | 110.9136 | 81.6367
805.2542 | 278.6289 | 331.6555 | 331.2351 | 42.0257 | 78.1745 | 111.0392 | 81.7809
806.2542 | 279.7351 | 332.6957 | 331.3853 | 42.1301 | 78.3137 | 111.1819 | 81.91
807.2542 | 281.5355 | 332.8288 | 332.2684 | 42.2206 | 78.4619 | 111.3139 | 82.0407
808.2542 | 282.799 | 333.467 | 332.9884 | 42.316 | 78.6053 | 111.4469 | 82.1591
809.2542 | 285.1904 | 333.1886 | 333.2197 | 42.41 | 78.7453 | 111.5673 | 82.2849
810.2542 | 286.9823 | 332.3094 | 333.0593 | 42.4838 | 78.8839 | 111.7086 | 82.4276
811.2542 | 286.5134 | 331.8264 | 332.3878 | 42.5767 | 79.0308 | 111.8406 | 82.6783
812.2542 | 285.5255 | 330.6668 | 331.9882 | 42.6598 | 79.1722 | 111.9737 | 82.8545
813.2542 | 285.0612 | 330.9589 | 331.8053 | 42.7527 | 79.3273 | 112.1115 | 82.9609
814.2542 | 283.944 | 331.0087 | 331.7799 | 42.8444 | 79.453 | 112.2417 | 83.1129
815.2542 | 282.9299 | 331.3429 | 332.2631 | 42.9373 | 79.5884 | 112.3705 | 83.263
816.2542 | 283.2254 | 331.8438 | 333.3336 | 43.0179 | 79.7359 | 112.5074 | 83.4082
817.2542 | 285.2042 | 333.1313 | 334.1763 | 43.1328 | 79.8803 | 112.6423 | 83.5426
818.2542 | 285.5878 | 332.6068 | 334.6484 | 43.2262 | 80.0207 | 112.7899 | 83.6704
819.2542 | 288.3737 | 333.1599 | 335.1881 | 43.3178 | 80.166 | 112.9091 | 83.8108
820.2542 | 286.7749 | 332.6661 | 334.6398 | 43.4091 | 80.2992 | 113.0392 | 83.9365
821.2542 | 287.7922 | 333.0201 | 334.2957 | 43.5012 | 80.4461 | 113.1886 | 84.0683
822.2542 | 289.7011 | 332.9155 | 333.7603 | 43.5855 | 80.5906 | 113.3305 | 84.1775
823.2542 | 288.8967 | 330.6853 | 332.9907 | 43.676 | 80.7357 | 113.451 | 84.3025
824.2542 | 288.2036 | 330.8337 | 332.6533 | 43.7514 | 80.8788 | 113.5827 | 84.4332
825.2542 | 286.6483 | 330.4464 | 331.7211 | 43.845 | 81.0316 | 113.7247 | 84.5434
826.2542 | 285.7439 | 329.6262 | 330.8353 | 43.9278 | 81.1753 | 113.8649 | 84.6695
827.2542 | 285.8484 | 328.3151 | 329.9265 | 44.0433 | 81.3177 | 114.004 | 84.8036
828.2542 | 286.1273 | 328.196 | 329.8915 | 44.1154 | 81.46 | 114.1403 | 84.9197
829.2542 | 286.8532 | 327.6627 | 330.9933 | 44.2239 | 81.6133 | 114.2696 | 85.0425
830.2542 | 286.5228 | 327.7738 | 330.3314 | 44.3133 | 81.751 | 114.4137 | 85.1742
831.2542 | 286.1152 | 328.8695 | 330.5668 | 44.4006 | 81.899 | 114.5376 | 85.2743
832.2542 | 288.18 | 331.1881 | 332.358 | 44.4947 | 82.0453 | 114.6561 | 85.3681
833.2542 | 287.5054 | 330.9767 | 331.8828 | 44.5911 | 82.1851 | 114.8005 | 85.5132
834.2542 | 287.1832 | 331.1137 | 330.8292 | 44.6737 | 82.3243 | 114.9326 | 85.6369
835.2542 | 286.8316 | 330.056 | 330.1317 | 44.7665 | 82.4778 | 115.0851 | 85.7601
836.2542 | 287.4224 | 329.4742 | 328.7393 | 44.8652 | 82.6294 | 115.1994 | 85.8626
837.2542 | 287.6589 | 330.1089 | 327.3925 | 44.9609 | 82.7676 | 115.3404 | 85.9864
838.2542 | 287.4544 | 331.0292 | 327.4081 | 45.0498 | 82.9211 | 115.4772 | 86.114
839.2542 | 288.3888 | 331.7831 | 328.2974 | 45.1388 | 83.0647 | 115.6267 | 86.2329
840.2542 | 289.8014 | 331.3149 | 327.9606 | 45.2283 | 83.2062 | 115.745 | 86.3689
841.2542 | 288.4058 | 331.4489 | 328.1555 | 45.3337 | 83.3491 | 115.895 | 86.4947
842.2542 | 287.1947 | 330.5956 | 328.9067 | 45.423 | 83.484 | 116.0229 | 86.6087
843.2542 | 286.4308 | 330.6121 | 329.4986 | 45.5082 | 83.6254 | 116.1723 | 86.7509
844.2542 | 285.5454 | 329.6506 | 328.9193 | 45.5892 | 83.7625 | 116.3118 | 86.8747
845.2542 | 284.4259 | 329.9414 | 329.7144 | 45.6985 | 83.8964 | 116.427 | 87.0043
846.2542 | 285.2167 | 330.8228 | 330.8225 | 45.7876 | 84.0264 | 116.5828 | 87.1373
847.2542 | 284.6325 | 331.5258 | 332.3799 | 45.8906 | 84.166 | 116.7064 | 87.2636
848.2542 | 284.3208 | 331.2752 | 333.0635 | 45.9881 | 84.3103 | 116.8528 | 87.3947
849.2542 | 283.2676 | 329.939 | 332.4259 | 46.0671 | 84.4449 | 116.9707 | 87.5268
850.2542 | 282.7652 | 329.6023 | 331.6434 | 46.1751 | 84.5905 | 117.1178 | 87.6447
851.2542 | 283.7479 | 329.4636 | 331.7644 | 46.256 | 84.7256 | 117.2484 | 87.7663
852.2542 | 285.8715 | 329.3746 | 333.5355 | 46.3522 | 84.8657 | 117.3721 | 87.8888
853.2542 | 284.1726 | 329.093 | 332.737 | 46.4255 | 85.0072 | 117.5142 | 88.0115
854.2542 | 283.8277 | 328.8995 | 332.6661 | 46.5388 | 85.1493 | 117.65 | 88.1328
855.2542 | 284.7132 | 328.9866 | 333.4511 | 46.6341 | 85.2908 | 117.7754 | 88.278
856.2542 | 286.0853 | 328.2454 | 332.8095 | 46.7143 | 85.426 | 117.9098 | 88.3929
857.2542 | 287.7388 | 328.4623 | 333.8265 | 46.8086 | 85.5773 | 118.0551 | 88.5174
858.2542 | 287.6486 | 330.1901 | 333.8912 | 46.9118 | 85.7109 | 118.1882 | 88.6509
859.2542 | 286.8972 | 329.9013 | 333.1656 | 47.0062 | 85.8448 | 118.3195 | 88.784
860.2542 | 286.2202 | 328.8291 | 330.8616 | 47.0954 | 85.9803 | 118.4513 | 88.926
861.2542 | 286.0358 | 328.8314 | 330.2405 | 47.1766 | 86.1297 | 118.5832 | 89.0505
862.2542 | 285.5974 | 330.303 | 329.3575 | 47.2886 | 86.2761 | 118.7089 | 89.1905
863.2542 | 285.7164 | 330.5849 | 329.264 | 47.3961 | 86.4128 | 118.8511 | 89.3299
864.2542 | 285.3975 | 329.4483 | 328.2359 | 47.4876 | 86.5607 | 118.9928 | 89.4731
865.2542 | 286.0788 | 329.7927 | 326.9422 | 47.5722 | 86.7009 | 119.1097 | 89.6001
866.2542 | 286.2573 | 330.7938 | 327.1616 | 47.6731 | 86.8322 | 119.256 | 89.7427
867.2542 | 288.5739 | 330.8032 | 326.0412 | 47.7623 | 86.9742 | 119.3877 | 89.8829
868.2542 | 289.1554 | 330.8849 | 325.4339 | 47.864 | 87.1156 | 119.5221 | 90.0338
869.2542 | 288.67 | 330.8725 | 326.1003 | 47.954 | 87.257 | 119.6531 | 90.1693
870.2542 | 288.2566 | 330.9107 | 326.4655 | 48.061 | 87.3882 | 119.7783 | 90.3182
871.2542 | 288.8061 | 331.1097 | 326.2752 | 48.1459 | 87.5242 | 119.9166 | 90.4607
872.2542 | 289.353 | 332.5817 | 327.5197 | 48.2508 | 87.6588 | 120.0358 | 90.5936
873.2542 | 290.5902 | 333.8514 | 328.155 | 48.3318 | 87.7974 | 120.1676 | 90.7295
874.2542 | 289.8339 | 334.4083 | 328.5049 | 48.4317 | 87.9406 | 120.3058 | 90.8613
875.2542 | 289.5609 | 334.8363 | 330.1588 | 48.5387 | 88.0781 | 120.4463 | 91.0239
876.2542 | 288.2638 | 334.8266 | 329.1038 | 48.6194 | 88.226 | 120.5638 | 91.1502
877.2542 | 290.8637 | 335.1427 | 329.7958 | 48.7493 | 88.3589 | 120.7232 | 91.3156
878.2542 | 292.2182 | 335.3888 | 330.2871 | 48.8509 | 88.5097 | 120.8372 | 91.4431
879.2542 | 292.6334 | 334.1565 | 329.5015 | 48.9476 | 88.6542 | 120.9713 | 91.5728
880.2542 | 291.6847 | 333.3991 | 328.5242 | 49.0336 | 88.7978 | 121.1108 | 91.7213
881.2542 | 293.0221 | 334.576 | 330.7741 | 49.1235 | 88.9501 | 121.2461 | 91.8629
882.2542 | 293.9616 | 334.9905 | 330.538 | 49.2333 | 89.1024 | 121.3749 | 91.987
883.2542 | 292.8538 | 333.6071 | 329.7254 | 49.3188 | 89.2535 | 121.5097 | 92.1186
884.2542 | 292.736 | 333.8803 | 328.5677 | 49.41 | 89.4122 | 121.6636 | 92.276
885.2542 | 292.1208 | 333.5924 | 329.0213 | 49.5348 | 89.5744 | 121.7924 | 92.4156
886.2542 | 294.4758 | 334.147 | 329.9031 | 49.6297 | 89.7309 | 121.9116 | 92.5652
887.2542 | 293.0678 | 333.466 | 328.4072 | 49.7337 | 89.8804 | 122.0579 | 92.7088
888.2542 | 292.2902 | 332.9618 | 327.0501 | 49.8267 | 90.0363 | 122.1883 | 92.827
889.2542 | 292.4827 | 333.081 | 327.0163 | 49.9289 | 90.1934 | 122.3195 | 92.9581
890.2542 | 292.9663 | 333.2236 | 326.8464 | 50.023 | 90.3489 | 122.4522 | 93.0808
891.2542 | 293.5072 | 333.1429 | 328.0599 | 50.1279 | 90.5244 | 122.5869 | 93.2146
892.2542 | 293.7765 | 333.1443 | 327.5691 | 50.2393 | 90.6608 | 122.7229 | 93.3593
893.2542 | 292.6137 | 332.2668 | 328.0464 | 50.3293 | 90.8198 | 122.8694 | 93.4956
894.2542 | 292.6662 | 332.564 | 328.0493 | 50.4334 | 90.9648 | 122.9922 | 93.6255
895.2542 | 295.3511 | 333.4529 | 328.6127 | 50.5442 | 91.109 | 123.1251 | 93.7701
896.2542 | 297.091 | 334.102 | 328.8152 | 50.6328 | 91.2526 | 123.2582 | 93.8986
897.2542 | 297.6828 | 334.0609 | 329.2341 | 50.7346 | 91.4048 | 123.3948 | 94.0225
898.2542 | 299.2676 | 333.861 | 330.0572 | 50.8428 | 91.5585 | 123.5094 | 94.1545
899.2542 | 300.3914 | 333.961 | 330.6395 | 50.9328 | 91.6999 | 123.6538 | 94.2967
900.2542 | 301.4546 | 335.5157 | 331.7005 | 51.0409 | 91.8529 | 123.7799 | 94.4189
901.2542 | 301.9871 | 335.726 | 333.0327 | 51.1497 | 91.9967 | 123.8989 | 94.5482
902.2542 | 302.3734 | 336.802 | 334.8383 | 51.2358 | 92.15 | 124.0285 | 94.6616
903.2542 | 300.5835 | 336.0891 | 335.5327 | 51.3424 | 92.2946 | 124.1778 | 94.801
904.2542 | 300.7189 | 336.2293 | 335.8128 | 51.4517 | 92.4493 | 124.3034 | 94.9459
905.2542 | 301.6465 | 335.6616 | 335.3038 | 51.5611 | 92.6069 | 124.4498 | 95.0985
906.2542 | 302.1784 | 335.9618 | 335.0234 | 51.6765 | 92.7656 | 124.5711 | 95.2451
907.2542 | 304.0654 | 336.915 | 334.3271 | 51.7609 | 92.9205 | 124.71 | 95.3988
908.2542 | 306.1973 | 337.4834 | 334.5134 | 51.8826 | 93.0697 | 124.8396 | 95.554
909.2542 | 307.6709 | 338.6393 | 334.2626 | 51.9694 | 93.2301 | 124.9802 | 95.7129
910.2542 | 306.6249 | 338.8383 | 334.0866 | 52.0817 | 93.3841 | 125.1187 | 95.9055
911.2542 | 307.1943 | 339.2958 | 334.4612 | 52.1894 | 93.5436 | 125.2565 | 96.1721
912.2542 | 306.7573 | 340.5771 | 335.106 | 52.2964 | 93.7 | 125.3958 | 96.512
913.2542 | 308.0123 | 341.765 | 335.8828 | 52.4095 | 93.8626 | 125.5236 | 96.8829
914.2542 | 309.8525 | 343.3845 | 337.3934 | 52.5151 | 94.0215 | 125.6722 | 97.2882
915.2542 | 312.0775 | 344.6465 | 339.7087 | 52.6297 | 94.1954 | 125.7959 | 97.6333
916.2542 | 313.7778 | 345.366 | 340.3592 | 52.7415 | 94.3468 | 125.9256 | 97.9628
917.2542 | 313.7219 | 346.4212 | 341.5632 | 52.8532 | 94.5078 | 126.0539 | 98.2441
918.2542 | 314.1463 | 346.2068 | 341.3674 | 52.9496 | 94.6722 | 126.1905 | 98.5052
919.2542 | 315.1673 | 347.6483 | 343.8597 | 53.0691 | 94.8423 | 126.3539 | 98.7581
920.2542 | 314.1088 | 349.3116 | 344.6234 | 53.1694 | 95.0233 | 126.4759 | 98.9724
921.2542 | 313.5226 | 350.1448 | 345.6168 | 53.2781 | 95.1951 | 126.6177 | 99.1711
922.2542 | 313.0154 | 351.3724 | 347.4286 | 53.3847 | 95.3628 | 126.7538 | 99.3721
923.2542 | 311.6057 | 350.7555 | 348.0477 | 53.5016 | 95.5499 | 126.9085 | 99.5564
924.2542 | 309.5499 | 349.3415 | 347.0446 | 53.6024 | 95.733 | 127.0558 | 99.706
925.2542 | 308.9497 | 349.4407 | 347.6437 | 53.7054 | 95.9223 | 127.196 | 99.8571
926.2542 | 307.7241 | 350.174 | 347.1441 | 53.8281 | 96.1119 | 127.3346 | 100.0006
927.2542 | 306.6942 | 350.5606 | 346.3521 | 53.9266 | 96.2898 | 127.4782 | 100.1536
928.2542 | 306.8317 | 352.1703 | 346.2302 | 54.0357 | 96.4816 | 127.6214 | 100.2559
929.2542 | 307.8244 | 351.9576 | 345.7682 | 54.1479 | 96.6606 | 127.7574 | 100.3968
930.2542 | 308.5707 | 352.9258 | 345.6372 | 54.2504 | 96.8493 | 127.9155 | 100.5315
931.2542 | 308.3165 | 352.6545 | 344.7775 | 54.3647 | 97.0308 | 128.0461 | 100.6628
932.2542 | 307.4053 | 351.7762 | 345.172 | 54.4842 | 97.2112 | 128.2 | 100.8005
933.2542 | 307.3155 | 352.4574 | 345.4593 | 54.582 | 97.3858 | 128.3275 | 100.9358
934.2542 | 307.2509 | 353.124 | 345.7027 | 54.6923 | 97.5519 | 128.4675 | 101.0786
935.2542 | 308.9408 | 354.2782 | 347.099 | 54.8041 | 97.704 | 128.6091 | 101.2233
936.2542 | 309.4493 | 354.1988 | 347.2382 | 54.9013 | 97.8687 | 128.7522 | 101.3602
937.2542 | 308.8901 | 354.8133 | 348.0441 | 55.0178 | 98.044 | 128.8815 | 101.5011
938.2542 | 309.7242 | 355.846 | 347.632 | 55.1161 | 98.2033 | 129.0289 | 101.6484
939.2542 | 311.0882 | 356.4382 | 348.2893 | 55.2126 | 98.3681 | 129.1446 | 101.7964
940.2542 | 311.5297 | 356.9863 | 348.3541 | 55.33 | 98.5161 | 129.2998 | 101.9457
941.2542 | 312.9745 | 356.8171 | 347.6298 | 55.4263 | 98.6764 | 129.4303 | 102.0923
942.2542 | 314.5828 | 356.4941 | 349.3846 | 55.5261 | 98.8333 | 129.5649 | 102.2311
943.2542 | 314.4916 | 356.6675 | 351.224 | 55.6542 | 98.9994 | 129.7042 | 102.3725
944.2542 | 313.9626 | 357.15 | 351.3972 | 55.765 | 99.1572 | 129.8208 | 102.5097
945.2542 | 314.3599 | 355.8462 | 351.632 | 55.8628 | 99.3156 | 129.9799 | 102.6466
946.2542 | 315.0089 | 356.1714 | 352.5947 | 55.9548 | 99.4749 | 130.1128 | 102.7985
947.2542 | 315.9496 | 355.4872 | 351.9237 | 56.0894 | 99.6405 | 130.2415 | 102.9573
948.2542 | 316.5684 | 355.5712 | 351.2704 | 56.1935 | 99.7958 | 130.371 | 103.1048
949.2542 | 317.2673 | 356.614 | 352.068 | 56.3176 | 99.9661 | 130.515 | 103.2607
950.2542 | 318.2121 | 357.3426 | 352.3422 | 56.4031 | 100.1324 | 130.6461 | 103.4307
951.2542 | 317.6787 | 357.8695 | 351.6831 | 56.5232 | 100.2999 | 130.7987 | 103.5644
952.2542 | 318.6585 | 359.872 | 352.345 | 56.6498 | 100.4596 | 130.9261 | 103.7179
953.2542 | 319.5765 | 360.6996 | 354.7546 | 56.7474 | 100.6306 | 131.0504 | 103.8859
954.2542 | 318.463 | 361.4173 | 355.2622 | 56.8569 | 100.7915 | 131.1951 | 104.0333
955.2542 | 318.1279 | 361.5417 | 354.9015 | 56.9725 | 100.9619 | 131.3329 | 104.1653
956.2542 | 317.1832 | 361.1633 | 355.3724 | 57.0784 | 101.1222 | 131.4661 | 104.3242
957.2542 | 316.9972 | 360.77 | 355.3181 | 57.1871 | 101.2904 | 131.6042 | 104.472
958.2542 | 318.606 | 361.3318 | 356.6127 | 57.293 | 101.4523 | 131.753 | 104.6214
959.2542 | 319.5412 | 361.2492 | 358.6731 | 57.3987 | 101.6274 | 131.8829 | 104.7817
960.2542 | 319.9326 | 360.7883 | 357.8104 | 57.5231 | 101.7773 | 132.0376 | 104.9292
961.2542 | 320.2746 | 361.4429 | 356.8311 | 57.6325 | 101.9458 | 132.1508 | 105.0729
962.2542 | 319.536 | 360.2152 | 355.5141 | 57.7494 | 102.1003 | 132.2898 | 105.2392
963.2542 | 320.0104 | 359.5511 | 354.9494 | 57.8578 | 102.2602 | 132.416 | 105.3806
964.2542 | 318.9201 | 358.8111 | 352.6723 | 57.9714 | 102.4126 | 132.5514 | 105.533
965.2542 | 318.5995 | 359.7798 | 351.7906 | 58.0832 | 102.5608 | 132.6945 | 105.6727
966.2542 | 318.7926 | 361.2167 | 351.3543 | 58.1985 | 102.7205 | 132.834 | 105.8171
967.2542 | 318.7271 | 361.1509 | 349.3202 | 58.3071 | 102.883 | 132.9539 | 105.9548
968.2542 | 319.9698 | 360.8996 | 348.7005 | 58.4172 | 103.0364 | 133.0812 | 106.1061
969.2542 | 319.1772 | 360.5004 | 349.0048 | 58.5181 | 103.1938 | 133.2099 | 106.2609
970.2542 | 318.7345 | 360.1562 | 350.1035 | 58.647 | 103.3413 | 133.3516 | 106.407
971.2542 | 318.8593 | 360.1439 | 350.4442 | 58.7342 | 103.4883 | 133.4973 | 106.5785
972.2542 | 318.5186 | 359.5824 | 350.524 | 58.8361 | 103.6399 | 133.6294 | 106.7325
973.2542 | 318.6435 | 359.8497 | 350.6135 | 58.9861 | 103.7879 | 133.7543 | 106.8942
974.2542 | 320.3408 | 359.7052 | 350.286 | 59.0776 | 103.9358 | 133.8849 | 107.0382
975.2542 | 321.2313 | 359.3224 | 349.7015 | 59.1777 | 104.0874 | 134.0037 | 107.1922
976.2542 | 323.2192 | 360.1145 | 350.5331 | 59.3091 | 104.2336 | 134.1319 | 107.343
977.2542 | 323.6426 | 361.4361 | 350.7434 | 59.4174 | 104.3729 | 134.2824 | 107.4968
978.2542 | 323.4935 | 361.5426 | 350.8635 | 59.5492 | 104.5147 | 134.3986 | 107.6542
979.2542 | 323.4789 | 362.5567 | 351.8009 | 59.6407 | 104.6557 | 134.5289 | 107.8254
980.2542 | 324.2896 | 362.7358 | 351.3934 | 59.7633 | 104.8014 | 134.6674 | 107.9861
981.2542 | 323.4458 | 362.4199 | 352.4837 | 59.8649 | 104.9394 | 134.7909 | 108.1414
982.2542 | 323.1551 | 363.0335 | 352.3748 | 59.9859 | 105.0806 | 134.921 | 108.3161
983.2542 | 323.3576 | 362.316 | 351.7629 | 60.0993 | 105.2238 | 135.0508 | 108.4939
984.2542 | 324.9202 | 363.3791 | 353.2275 | 60.2099 | 105.3713 | 135.1786 | 108.6622
985.2542 | 324.6031 | 363.4906 | 353.2113 | 60.3436 | 105.5182 | 135.3056 | 108.8369
986.2542 | 325.678 | 364.0145 | 352.8011 | 60.4544 | 105.6529 | 135.4519 | 109.0221
987.2542 | 325.2636 | 363.8016 | 352.9886 | 60.5565 | 105.8085 | 135.5708 | 109.1869
988.2542 | 325.8407 | 363.3574 | 353.6344 | 60.6809 | 105.9625 | 135.7082 | 109.3787
989.2542 | 327.7913 | 364.5164 | 354.2564 | 60.8043 | 106.1121 | 135.8365 | 109.5431
990.2542 | 326.9134 | 366.2314 | 356.5604 | 60.9071 | 106.2599 | 135.966 | 109.7203
991.2542 | 326.3059 | 367.0443 | 358.0642 | 61.0415 | 106.4007 | 136.0987 | 109.8813
992.2542 | 326.1004 | 368.4295 | 357.8271 | 61.1427 | 106.5432 | 136.2412 | 110.0574
993.2542 | 325.588 | 369.5189 | 358.4673 | 61.2729 | 106.6901 | 136.3851 | 110.2312
994.2542 | 326.3956 | 368.9465 | 358.4243 | 61.3809 | 106.8458 | 136.5233 | 110.3927
995.2542 | 326.6952 | 368.6813 | 358.7816 | 61.5036 | 107.0007 | 136.6434 | 110.5526
996.2542 | 327.5419 | 370.1214 | 359.0818 | 61.6232 | 107.157 | 136.785 | 110.7114
997.2542 | 327.1024 | 370.5196 | 359.1457 | 61.7435 | 107.3036 | 136.9008 | 110.8606
998.2542 | 327.2088 | 370.8668 | 358.5363 | 61.8421 | 107.4564 | 137.0353 | 111.0173
999.2542 | 326.8423 | 369.7484 | 357.7651 | 61.9636 | 107.6118 | 137.1615 | 111.1758
1000.2542 | 328.5327 | 369.9327 | 358.9511 | 62.0951 | 107.7732 | 137.3109 | 111.3218
1001.2542 | 327.2532 | 369.5069 | 359.9965 | 62.2239 | 107.9272 | 137.4469 | 111.4731
1002.2542 | 327.1383 | 368.9639 | 358.7117 | 62.3355 | 108.0772 | 137.5753 | 111.5956
1003.2542 | 325.9252 | 368.3254 | 358.2941 | 62.4515 | 108.2307 | 137.7025 | 111.7285
1004.2542 | 326.1049 | 368.9926 | 357.5913 | 62.5636 | 108.3852 | 137.8344 | 111.8745
1005.2542 | 326.3447 | 369.0902 | 358.7132 | 62.6741 | 108.5483 | 137.9697 | 111.9969
1006.2542 | 327.1454 | 368.8309 | 357.8894 | 62.8054 | 108.6988 | 138.1149 | 112.1568
1007.2542 | 325.0417 | 367.6092 | 357.478 | 62.929 | 108.865 | 138.2599 | 112.2972
1008.2542 | 324.221 | 366.6416 | 357.2907 | 63.034 | 109.013 | 138.3945 | 112.4324
1009.2542 | 323.2302 | 365.964 | 356.1883 | 63.1585 | 109.1716 | 138.5074 | 112.5597
1010.2542 | 322.6377 | 366.1271 | 356.1974 | 63.2882 | 109.324 | 138.6334 | 112.7246
1011.2542 | 323.526 | 367.127 | 356.9279 | 63.4045 | 109.4862 | 138.7738 | 112.8801
1012.2542 | 324.0391 | 368.7899 | 357.1889 | 63.5294 | 109.6433 | 138.9006 | 113.0142
1013.2542 | 324.547 | 369.7781 | 357.8976 | 63.6198 | 109.7919 | 139.0469 | 113.1482
1014.2542 | 324.2952 | 370.4966 | 358.5518 | 63.7646 | 109.9389 | 139.1804 | 113.3
1015.2542 | 324.3463 | 371.5751 | 359.5978 | 63.8796 | 110.1062 | 139.312 | 113.4279
1016.2542 | 324.5888 | 372.5146 | 359.6899 | 64.0093 | 110.2549 | 139.4343 | 113.5743
1017.2542 | 323.7296 | 373.4366 | 360.6892 | 64.1227 | 110.4137 | 139.5575 | 113.7126
1018.2542 | 323.5091 | 376.1178 | 363.0159 | 64.2362 | 110.5514 | 139.695 | 113.8587
1019.2542 | 323.1269 | 376.795 | 364.6859 | 64.3447 | 110.7085 | 139.831 | 113.9983
1020.2542 | 322.3654 | 377.007 | 365.0981 | 64.455 | 110.865 | 139.9757 | 114.1179
1021.2542 | 321.3716 | 376.8079 | 365.2521 | 64.5845 | 111.0162 | 140.1028 | 114.2798
1022.2542 | 321.0687 | 379.2276 | 367.8293 | 64.702 | 111.1651 | 140.2368 | 114.4098
1023.2542 | 322.6665 | 378.9809 | 367.9061 | 64.8204 | 111.3097 | 140.3915 | 114.5628
1024.2542 | 323.5899 | 380.5312 | 369.5275 | 64.9462 | 111.4636 | 140.5328 | 114.6885
1025.2542 | 323.4927 | 382.6303 | 369.8527 | 65.0553 | 111.6118 | 140.6406 | 114.8405
1026.2542 | 323.8613 | 383.449 | 371.0217 | 65.1662 | 111.7601 | 140.796 | 114.9766
1027.2542 | 323.6724 | 383.5543 | 370.9236 | 65.2889 | 111.9077 | 140.928 | 115.1015
1028.2542 | 323.3292 | 383.6548 | 371.0074 | 65.4091 | 112.0599 | 141.0566 | 115.2101
1029.2542 | 324.8794 | 383.6063 | 370.6418 | 65.5252 | 112.2079 | 141.197 | 115.3629
1030.2542 | 325.4539 | 383.955 | 370.5115 | 65.6312 | 112.3588 | 141.3309 | 115.4987
1031.2542 | 325.1928 | 384.5 | 370.7891 | 65.7702 | 112.502 | 141.4615 | 115.6316
1032.2542 | 325.0246 | 384.9089 | 371.2872 | 65.8789 | 112.6559 | 141.6074 | 115.76
1033.2542 | 325.5745 | 384.7936 | 372.2494 | 66.011 | 112.7995 | 141.7292 | 115.9114
1034.2542 | 325.2898 | 385.6965 | 372.932 | 66.1299 | 112.9525 | 141.8733 | 116.043
1035.2542 | 327.0509 | 386.3481 | 372.8511 | 66.2371 | 113.1018 | 141.9829 | 116.1609
1036.2542 | 326.83 | 386.7305 | 372.7838 | 66.3582 | 113.2514 | 142.1216 | 116.3021
1037.2542 | 329.6897 | 387.6443 | 372.825 | 66.4963 | 113.3941 | 142.2654 | 116.4439
1038.2542 | 331.789 | 387.9906 | 372.7877 | 66.6037 | 113.5476 | 142.4059 | 116.5705
1039.2542 | 334.4143 | 388.0196 | 373.0585 | 66.7247 | 113.6963 | 142.5236 | 116.7195
1040.2542 | 335.437 | 387.8656 | 374.4982 | 66.8396 | 113.8497 | 142.6511 | 116.8396
1041.2542 | 335.1609 | 387.3777 | 373.7033 | 66.9561 | 113.9959 | 142.8014 | 116.9755
1042.2542 | 335.8277 | 385.8195 | 373.0339 | 67.0837 | 114.1456 | 142.9314 | 117.1204
1043.2542 | 337.9271 | 384.6617 | 373.7993 | 67.1875 | 114.2934 | 143.0555 | 117.2479
1044.2542 | 338.6249 | 385.0479 | 374.6887 | 67.3103 | 114.4344 | 143.1862 | 117.3966
1045.2542 | 338.0548 | 385.9421 | 374.852 | 67.4371 | 114.5912 | 143.3201 | 117.518
1046.2542 | 339.835 | 387.4525 | 375.2761 | 67.5615 | 114.7371 | 143.4371 | 117.6644
1047.2542 | 339.3352 | 388.1703 | 376.0442 | 67.6747 | 114.8859 | 143.5898 | 117.8096
1048.2542 | 338.0569 | 388.618 | 376.3854 | 67.7925 | 115.0159 | 143.7138 | 117.9535
1049.2542 | 338.8114 | 389.0424 | 377.1974 | 67.9155 | 115.1645 | 143.8332 | 118.0778
1050.2542 | 341.0033 | 389.2513 | 377.404 | 68.0382 | 115.3137 | 143.9755 | 118.237
1051.2542 | 342.5293 | 391.0838 | 377.4598 | 68.1751 | 115.4596 | 144.1002 | 118.3789
1052.2542 | 344.8725 | 391.1315 | 378.2063 | 68.3089 | 115.604 | 144.2218 | 118.5184
1053.2542 | 344.8481 | 392.6078 | 379.1066 | 68.423 | 115.7578 | 144.3666 | 118.6827
1054.2542 | 343.9186 | 392.2011 | 381.3189 | 68.5532 | 115.9102 | 144.4793 | 118.8171
1055.2542 | 343.7222 | 392.0358 | 380.7605 | 68.6717 | 116.0461 | 144.6262 | 118.9774
1056.2542 | 343.4381 | 392.6934 | 380.1281 | 68.7888 | 116.2021 | 144.7408 | 119.1226
1057.2542 | 343.8031 | 392.377 | 379.2017 | 68.9052 | 116.3561 | 144.8723 | 119.2715
1058.2542 | 343.9507 | 391.7946 | 378.3675 | 69.0708 | 116.502 | 145.0154 | 119.4175
1059.2542 | 344.1838 | 390.7207 | 377.4387 | 69.1956 | 116.6527 | 145.1384 | 119.5589
1060.2542 | 344.9259 | 390.0176 | 377.8203 | 69.3217 | 116.8078 | 145.2847 | 119.7056
1061.2542 | 344.3484 | 391.1419 | 376.0865 | 69.4535 | 116.9585 | 145.4003 | 119.8369
1062.2542 | 343.1565 | 390.9972 | 376.2372 | 69.573 | 117.1035 | 145.5208 | 119.9702
1063.2542 | 343.0889 | 391.2096 | 374.9901 | 69.7093 | 117.2527 | 145.6599 | 120.1004
1064.2542 | 342.8238 | 392.6038 | 376.4045 | 69.8384 | 117.3981 | 145.7848 | 120.2449
1065.2542 | 342.8379 | 393.0108 | 377.7579 | 69.9664 | 117.5467 | 145.9221 | 120.3815
1066.2542 | 343.6672 | 394.7487 | 378.7404 | 70.1031 | 117.686 | 146.0455 | 120.5134
1067.2542 | 342.9458 | 395.9292 | 378.8517 | 70.2404 | 117.8384 | 146.1832 | 120.6464
1068.2542 | 341.299 | 394.9257 | 378.7364 | 70.3665 | 117.9793 | 146.3024 | 120.7738
1069.2542 | 340.5921 | 395.6341 | 378.1446 | 70.5033 | 118.1223 | 146.4419 | 120.9019
1070.2542 | 342.4292 | 396.3032 | 378.005 | 70.6386 | 118.2676 | 146.5567 | 121.0152
1071.2542 | 343.2174 | 397.4105 | 378.235 | 70.7679 | 118.4134 | 146.6883 | 121.1366
1072.2542 | 343.9985 | 398.0409 | 377.3437 | 70.8864 | 118.5567 | 146.825 | 121.2419
1073.2542 | 345.1061 | 398.0715 | 378.4088 | 71.0343 | 118.7077 | 146.941 | 121.3654
1074.2542 | 344.5455 | 397.5256 | 377.5889 | 71.1708 | 118.8503 | 147.0736 | 121.4756
1075.2542 | 346.0546 | 397.6984 | 377.6946 | 71.3038 | 119.0007 | 147.2109 | 121.5874
1076.2542 | 347.323 | 398.3835 | 377.0783 | 71.4399 | 119.1463 | 147.3306 | 121.7119
1077.2542 | 347.2442 | 398.1851 | 376.6578 | 71.5851 | 119.2903 | 147.4611 | 121.8264
1078.2542 | 348.7841 | 399.7061 | 378.2561 | 71.7224 | 119.4298 | 147.5872 | 121.9198
1079.2542 | 348.2532 | 400.0368 | 378.9832 | 71.8686 | 119.5809 | 147.7126 | 122.0078
1080.2542 | 348.229 | 399.5589 | 378.8802 | 72.0021 | 119.724 | 147.8439 | 122.1229
1081.2542 | 348.1992 | 399.8975 | 378.7932 | 72.1414 | 119.8701 | 147.9594 | 122.2355
1082.2542 | 349.4808 | 399.6507 | 378.7574 | 72.2883 | 119.9996 | 148.0943 | 122.3385
1083.2542 | 348.7845 | 399.7189 | 378.0831 | 72.4296 | 120.147 | 148.2138 | 122.444
1084.2542 | 349.6211 | 399.7843 | 377.6823 | 72.5768 | 120.2845 | 148.3435 | 122.5274
1085.2542 | 350.7959 | 399.0583 | 377.5969 | 72.7212 | 120.4372 | 148.461 | 122.6501
1086.2542 | 350.3397 | 398.518 | 377.103 | 72.8711 | 120.57 | 148.5959 | 122.7595
1087.2542 | 350.3062 | 398.3324 | 377.1527 | 73.0148 | 120.7246 | 148.7233 | 122.8775
1088.2542 | 349.2894 | 398.2378 | 376.9358 | 73.1867 | 120.8605 | 148.8498 | 122.9895
1089.2542 | 348.2092 | 398.7839 | 377.8237 | 73.3063 | 121.0036 | 148.9558 | 123.0847
1090.2542 | 348.1964 | 398.5606 | 378.7006 | 73.4692 | 121.1457 | 149.0901 | 123.1897
1091.2542 | 348.1487 | 398.579 | 378.5634 | 73.6143 | 121.2841 | 149.2179 | 123.277
1092.2542 | 348.1445 | 398.7223 | 378.5195 | 73.7913 | 121.4222 | 149.352 | 123.3855
1093.2542 | 347.667 | 398.0597 | 378.256 | 73.9516 | 121.568 | 149.4627 | 123.4884
1094.2542 | 348.2434 | 397.2859 | 378.1208 | 74.1117 | 121.7125 | 149.5903 | 123.6006
1095.2542 | 348.0088 | 397.7951 | 378.6438 | 74.27 | 121.8513 | 149.7186 | 123.6744
1096.2542 | 347.573 | 397.7363 | 379.7432 | 74.4209 | 121.9853 | 149.8528 | 123.7798
1097.2542 | 345.9925 | 397.8882 | 380.25 | 74.6046 | 122.1184 | 149.9582 | 123.8674
1098.2542 | 344.3804 | 397.3679 | 379.8924 | 74.7637 | 122.2535 | 150.0857 | 123.9738
1099.2542 | 343.9268 | 396.497 | 379.1304 | 74.9276 | 122.3894 | 150.2123 | 124.0574
1100.2542 | 343.4739 | 395.2154 | 378.6159 | 75.1147 | 122.5231 | 150.3458 | 124.1438
1101.2542 | 342.9309 | 394.4863 | 377.6807 | 75.2986 | 122.6647 | 150.4682 | 124.2462
1102.2542 | 342.9033 | 395.442 | 378.3663 | 75.4684 | 122.792 | 150.5843 | 124.3378
1103.2542 | 343.547 | 396.9418 | 379.6318 | 75.65 | 122.931 | 150.7065 | 124.4345
1104.2542 | 344.8061 | 397.0078 | 379.2616 | 75.8311 | 123.0588 | 150.8424 | 124.5221
1105.2542 | 346.0983 | 398.2141 | 379.8691 | 76.0078 | 123.1913 | 150.963 | 124.6157
1106.2542 | 345.0842 | 398.0536 | 379.7517 | 76.2059 | 123.3299 | 151.0857 | 124.7087
1107.2542 | 345.1621 | 398.5218 | 379.0859 | 76.3858 | 123.4624 | 151.2015 | 124.7889
1108.2542 | 344.6764 | 397.7723 | 378.358 | 76.6016 | 123.5974 | 151.3302 | 124.8914
1109.2542 | 344.4493 | 396.2907 | 376.8524 | 76.814 | 123.7278 | 151.4613 | 124.9684
1110.2542 | 343.8391 | 396.4864 | 375.7597 | 77.0215 | 123.8573 | 151.5761 | 125.0812
1111.2542 | 344.1186 | 396.798 | 375.7465 | 77.2315 | 123.9842 | 151.701 | 125.1654
1112.2542 | 343.4094 | 395.6662 | 375.2512 | 77.4583 | 124.1174 | 151.818 | 125.2385
1113.2542 | 344.6351 | 395.4952 | 376.2811 | 77.6899 | 124.2406 | 151.9365 | 125.3435
1114.2542 | 343.9156 | 395.6144 | 375.9421 | 77.8698 | 124.3791 | 152.0749 | 125.4219
1115.2542 | 344.1404 | 397.0093 | 375.4581 | 78.0593 | 124.5022 | 152.1963 | 125.4998
1116.2542 | 345.7231 | 397.7054 | 375.7781 | 78.2517 | 124.6285 | 152.3226 | 125.596
1117.2542 | 346.0467 | 398.5852 | 375.8964 | 78.453 | 124.7601 | 152.4313 | 125.6979
1118.2542 | 347.3339 | 399.3253 | 376.3786 | 78.624 | 124.8925 | 152.5625 | 125.8009
1119.2542 | 348.1181 | 400.8741 | 377.2116 | 78.8399 | 125.0279 | 152.6828 | 125.8806
1120.2542 | 349.6659 | 402.421 | 377.7602 | 79.0446 | 125.1529 | 152.8033 | 125.997
1121.2542 | 349.9801 | 404.0001 | 378.1089 | 79.2699 | 125.2824 | 152.9198 | 126.0883
1122.2542 | 349.9545 | 403.6486 | 378.7017 | 79.5098 | 125.405 | 153.0421 | 126.1966
1123.2542 | 350.8847 | 403.7856 | 378.1149 | 79.7595 | 125.5308 | 153.1793 | 126.3054
1124.2542 | 352.3425 | 405.1455 | 379.0408 | 80.0288 | 125.6663 | 153.3055 | 126.41
1125.2542 | 352.0651 | 405.6888 | 379.3153 | 80.3017 | 125.8 | 153.4134 | 126.4973
1126.2542 | 352.0813 | 405.9691 | 377.876 | 80.5555 | 125.9274 | 153.5453 | 126.5987
1127.2542 | 351.8451 | 406.5776 | 379.1224 | 80.8307 | 126.0529 | 153.6772 | 126.72
1128.2542 | 352.0968 | 408.2112 | 379.3498 | 81.1246 | 126.1883 | 153.7901 | 126.8043
1129.2542 | 352.2682 | 408.5998 | 378.7463 | 81.4013 | 126.3157 | 153.9126 | 126.9082
1130.2542 | 353.4255 | 407.7415 | 378.1275 | 81.6703 | 126.452 | 154.0409 | 126.9933
1131.2542 | 353.4124 | 408.0964 | 377.8156 | 81.9335 | 126.5862 | 154.1626 | 127.0978
1132.2542 | 354.4717 | 407.9422 | 377.8697 | 82.207 | 126.7354 | 154.2772 | 127.1807
1133.2542 | 353.8747 | 407.5058 | 376.6976 | 82.4736 | 126.8651 | 154.4131 | 127.2889
1134.2542 | 353.5894 | 406.5814 | 375.8852 | 82.7137 | 126.9908 | 154.5269 | 127.3935
1135.2542 | 353.32 | 406.2017 | 375.3327 | 83.0008 | 127.1265 | 154.6567 | 127.4982
1136.2542 | 353.4531 | 406.0595 | 375.1389 | 83.2499 | 127.2603 | 154.7783 | 127.5784
1137.2542 | 353.9306 | 404.8555 | 374.9616 | 83.5008 | 127.404 | 154.8961 | 127.6853
1138.2542 | 353.2545 | 404.0082 | 373.9003 | 83.758 | 127.531 | 155.0315 | 127.7982
1139.2542 | 352.9036 | 401.9501 | 372.2819 | 84.0054 | 127.6565 | 155.1556 | 127.8946
1140.2542 | 353.2045 | 401.1773 | 371.4754 | 84.2396 | 127.7892 | 155.2755 | 127.9959
1141.2542 | 353.4923 | 399.4271 | 369.9239 | 84.4852 | 127.9165 | 155.3958 | 128.1126
1142.2542 | 354.2879 | 398.7093 | 368.5316 | 84.7214 | 128.0407 | 155.5173 | 128.2025
1143.2542 | 354.9433 | 397.676 | 367.8604 | 84.9668 | 128.1659 | 155.6478 | 128.3237
1144.2542 | 354.9006 | 396.7653 | 367.5992 | 85.1937 | 128.2958 | 155.769 | 128.4051
1145.2542 | 356.1878 | 397.0066 | 368.8504 | 85.4185 | 128.4124 | 155.9005 | 128.5237
1146.2542 | 358.8825 | 399.9226 | 371.7542 | 85.6424 | 128.5521 | 156.0163 | 128.6055
1147.2542 | 358.2704 | 399.5813 | 371.7653 | 85.8727 | 128.6837 | 156.1312 | 128.6899
1148.2542 | 358.5666 | 399.9822 | 373.7361 | 86.0835 | 128.806 | 156.2622 | 128.8183
1149.2542 | 358.4109 | 400.3717 | 374.9226 | 86.3009 | 128.9257 | 156.3827 | 128.9204
1150.2542 | 357.5517 | 399.9172 | 376.2798 | 86.517 | 129.0442 | 156.5169 | 129.031
1151.2542 | 356.9835 | 399.4998 | 377.9767 | 86.7362 | 129.1734 | 156.6319 | 129.1247
1152.2542 | 356.9102 | 399.1206 | 379.1122 | 86.9475 | 129.2962 | 156.7569 | 129.223
1153.2542 | 356.3729 | 399.2425 | 380.288 | 87.137 | 129.4251 | 156.884 | 129.3358
1154.2542 | 355.4094 | 399.3428 | 379.8425 | 87.3385 | 129.5533 | 157.0003 | 129.4413
1155.2542 | 354.3004 | 398.3886 | 379.7902 | 87.5513 | 129.6721 | 157.1369 | 129.5513
1156.2542 | 353.8095 | 398.142 | 379.0714 | 87.7438 | 129.8011 | 157.2565 | 129.636
1157.2542 | 354.0559 | 398.6905 | 377.9091 | 87.9353 | 129.9274 | 157.3881 | 129.7444
1158.2542 | 354.4249 | 400.0518 | 378.395 | 88.1125 | 130.0626 | 157.5129 | 129.8502
1159.2542 | 353.1787 | 398.3056 | 377.7967 | 88.2857 | 130.1892 | 157.6564 | 129.9497
1160.2542 | 352.8748 | 397.5747 | 376.9016 | 88.4642 | 130.3186 | 157.7698 | 130.0608
1161.2542 | 351.8151 | 397.2046 | 377.1933 | 88.6412 | 130.4571 | 157.8913 | 130.1709
1162.2542 | 350.6261 | 397.3754 | 378.1781 | 88.8177 | 130.5849 | 158.0242 | 130.2728
1163.2542 | 350.3421 | 397.0134 | 376.687 | 88.9876 | 130.7131 | 158.1358 | 130.3713
1164.2542 | 351.8016 | 397.1733 | 377.154 | 89.1401 | 130.8404 | 158.2521 | 130.466
1165.2542 | 354.1345 | 398.0505 | 378.705 | 89.3053 | 130.9725 | 158.3914 | 130.5773
1166.2542 | 354.5796 | 398.2995 | 378.9566 | 89.4815 | 131.0941 | 158.5183 | 130.6669
1167.2542 | 355.2053 | 399.3719 | 378.4714 | 89.6608 | 131.2195 | 158.648 | 130.7805
1168.2542 | 355.6987 | 400.4264 | 381.0721 | 89.8196 | 131.352 | 158.774 | 130.8974
1169.2542 | 355.1977 | 400.3758 | 382.5155 | 89.993 | 131.4753 | 158.8983 | 130.9948
1170.2542 | 354.5349 | 402.2287 | 383.6781 | 90.178 | 131.6079 | 159.0148 | 131.0896
1171.2542 | 356.2408 | 403.4018 | 385.7444 | 90.3839 | 131.7362 | 159.1356 | 131.1741
1172.2542 | 357.0237 | 405.8679 | 387.0149 | 90.5748 | 131.8642 | 159.259 | 131.2833
1173.2542 | 357.4653 | 406.0525 | 386.7567 | 90.7822 | 131.9992 | 159.3834 | 131.383
1174.2542 | 357.2352 | 405.9473 | 385.8066 | 90.9593 | 132.1324 | 159.508 | 131.5004
1175.2542 | 358.2629 | 405.5377 | 386.1423 | 91.1517 | 132.2556 | 159.6288 | 131.5887
1176.2542 | 358.0651 | 405.8439 | 386.6653 | 91.3499 | 132.3841 | 159.7623 | 131.6995
1177.2542 | 358.2548 | 406.5969 | 387.5344 | 91.5486 | 132.5135 | 159.8882 | 131.8079
1178.2542 | 360.4066 | 407.0524 | 387.9496 | 91.7368 | 132.6448 | 160.0127 | 131.9104
1179.2542 | 361.1425 | 407.6116 | 388.7894 | 91.9112 | 132.7727 | 160.1399 | 132.0251
1180.2542 | 361.3365 | 406.7531 | 389.6437 | 92.1087 | 132.9013 | 160.2569 | 132.1272
1181.2542 | 360.2555 | 407.0281 | 390.6056 | 92.2928 | 133.0357 | 160.371 | 132.2161
1182.2542 | 361.6497 | 407.4071 | 390.4636 | 92.4879 | 133.1612 | 160.4927 | 132.3161
1183.2542 | 361.8594 | 406.7334 | 390.2244 | 92.6827 | 133.2905 | 160.617 | 132.4039
1184.2542 | 361.2878 | 406.8418 | 391.0871 | 92.8834 | 133.4271 | 160.7497 | 132.5179
1185.2542 | 361.6432 | 407.032 | 390.8751 | 93.0748 | 133.5542 | 160.8642 | 132.6286
1186.2542 | 361.207 | 406.6376 | 390.4423 | 93.2632 | 133.6925 | 160.9979 | 132.7088
1187.2542 | 361.0213 | 407.365 | 391.0222 | 93.4627 | 133.8316 | 161.1128 | 132.8236
1188.2542 | 362.4897 | 407.8421 | 391.2809 | 93.6428 | 133.9597 | 161.2397 | 132.9444
1189.2542 | 362.3337 | 408.336 | 390.9655 | 93.822 | 134.0881 | 161.3641 | 133.0655
1190.2542 | 362.843 | 409.6788 | 391.425 | 94.0105 | 134.2289 | 161.4857 | 133.1572
1191.2542 | 363.9302 | 409.2621 | 389.9154 | 94.1336 | 134.3521 | 161.6132 | 133.2557
1192.2542 | 363.3149 | 409.4205 | 389.1446 | 94.2853 | 134.4936 | 161.7272 | 133.3585
1193.2542 | 362.868 | 409.5464 | 389.3211 | 94.3917 | 134.6328 | 161.8473 | 133.4708
1194.2542 | 362.0775 | 410.075 | 390.5407 | 94.4637 | 134.7735 | 161.9797 | 133.5828
1195.2542 | 362.0594 | 411.5264 | 391.1698 | 94.5134 | 134.9032 | 162.0966 | 133.6969
1196.2542 | 362.4617 | 411.7745 | 391.3853 | 94.5517 | 135.0343 | 162.2267 | 133.8244
1197.2542 | 361.7797 | 411.178 | 390.9879 | 94.6018 | 135.1693 | 162.3368 | 133.9268
1198.2542 | 361.0058 | 410.4944 | 390.5648 | 94.6368 | 135.3052 | 162.4529 | 134.035
1199.2542 | 362.0411 | 409.6602 | 390.9271 | 94.6872 | 135.4436 | 162.5735 | 134.1425
1200.2542 | 361.7779 | 410.4549 | 390.2081 | 94.7362 | 135.5803 | 162.6991 | 134.2367
1201.2542 | 360.6051 | 409.867 | 390.3789 | 94.7595 | 135.716 | 162.8279 | 134.3433
1202.2542 | 360.3272 | 409.3951 | 390.5456 | 94.8154 | 135.8389 | 162.9462 | 134.4517
1203.2542 | 359.878 | 409.4904 | 391.1599 | 94.8533 | 135.968 | 163.0798 | 134.5469
1204.2542 | 360.0225 | 410.0801 | 392.9235 | 94.8989 | 136.1093 | 163.188 | 134.656
1205.2542 | 361.4996 | 409.72 | 393.8052 | 94.9415 | 136.2351 | 163.313 | 134.7541
1206.2542 | 362.1047 | 409.7366 | 393.0711 | 94.9543 | 136.368 | 163.4356 | 134.8594
1207.2542 | 361.6301 | 409.7475 | 393.042 | 95.0077 | 136.5025 | 163.5506 | 134.9669
1208.2542 | 363.9069 | 410.1426 | 391.9963 | 95.0472 | 136.635 | 163.671 | 135.0708
1209.2542 | 363.464 | 409.7646 | 391.1553 | 95.0933 | 136.7709 | 163.794 | 135.1661
1210.2542 | 363.7909 | 409.4475 | 389.6776 | 95.1422 | 136.9108 | 163.9275 | 135.2818
1211.2542 | 363.6626 | 409.1419 | 388.2126 | 95.1908 | 137.0448 | 164.0464 | 135.3782
1212.2542 | 364.3916 | 409.5624 | 388.2767 | 95.2249 | 137.1782 | 164.1672 | 135.488
1213.2542 | 364.6309 | 409.1543 | 387.5834 | 95.2672 | 137.3077 | 164.287 | 135.5825
1214.2542 | 364.4667 | 409.5031 | 388.131 | 95.2491 | 137.4433 | 164.4185 | 135.6744
1215.2542 | 364.4102 | 409.6127 | 388.846 | 95.2877 | 137.5802 | 164.5449 | 135.7885
1216.2542 | 362.9601 | 409.8819 | 389.8461 | 95.3415 | 137.708 | 164.6623 | 135.8959
1217.2542 | 361.8787 | 410.2334 | 389.1947 | 95.3866 | 137.8513 | 164.7887 | 135.9846
1218.2542 | 362.3103 | 411.8835 | 390.0807 | 95.4571 | 137.9855 | 164.9126 | 136.065
1219.2542 | 362.6116 | 412.9706 | 390.7447 | 95.5311 | 138.1194 | 165.0381 | 136.1681
1220.2542 | 362.9393 | 413.0207 | 390.897 | 95.604 | 138.2472 | 165.1521 | 136.2562
1221.2542 | 362.1945 | 413.0023 | 391.8466 | 95.6925 | 138.3857 | 165.2684 | 136.3547
1222.2542 | 361.1852 | 412.0225 | 392.8287 | 95.786 | 138.5097 | 165.3999 | 136.4687
1223.2542 | 360.0751 | 411.8466 | 394.4844 | 95.8708 | 138.6475 | 165.5235 | 136.569
1224.2542 | 360.0607 | 412.8476 | 395.6971 | 95.9625 | 138.7784 | 165.6491 | 136.6647
1225.2542 | 360.7135 | 412.7916 | 395.712 | 96.047 | 138.9065 | 165.7721 | 136.748
1226.2542 | 361.41 | 413.6438 | 394.893 | 96.1297 | 139.0393 | 165.8822 | 136.843
1227.2542 | 361.5716 | 412.6836 | 393.7796 | 96.2365 | 139.167 | 166.0233 | 136.9548
1228.2542 | 361.7549 | 412.9383 | 393.995 | 96.3341 | 139.3032 | 166.1253 | 137.0168
1229.2542 | 361.4779 | 411.5566 | 394.0546 | 96.4262 | 139.4222 | 166.2481 | 137.1328
1230.2542 | 360.8157 | 410.4942 | 394.1617 | 96.5152 | 139.5598 | 166.3811 | 137.2257
1231.2542 | 361.4323 | 410.647 | 394.0808 | 96.6324 | 139.6863 | 166.4966 | 137.3249
1232.2542 | 361.0712 | 409.262 | 393.6961 | 96.7283 | 139.8046 | 166.6186 | 137.4352
1233.2542 | 361.983 | 408.8664 | 393.2822 | 96.8374 | 139.9282 | 166.7453 | 137.54
1234.2542 | 361.575 | 409.8386 | 394.8392 | 96.9314 | 140.0556 | 166.8739 | 137.6255
1235.2542 | 361.6791 | 409.7918 | 395.3847 | 97.0649 | 140.1947 | 166.9831 | 137.7156
1236.2542 | 361.788 | 409.1629 | 394.6143 | 97.2153 | 140.3261 | 167.1158 | 137.8115
1237.2542 | 361.2022 | 409.1419 | 395.1776 | 97.3811 | 140.4481 | 167.2303 | 137.9154
1238.2542 | 361.5573 | 409.5866 | 396.3239 | 97.548 | 140.5856 | 167.3622 | 138.0277
1239.2542 | 363.5639 | 409.7819 | 398.4968 | 97.6976 | 140.7169 | 167.4863 | 138.1185
1240.2542 | 363.7709 | 410.0467 | 398.4521 | 97.847 | 140.8501 | 167.6024 | 138.222
1241.2542 | 363.7852 | 409.8862 | 398.9687 | 97.978 | 140.9728 | 167.72 | 138.3254
1242.2542 | 364.7812 | 410.6834 | 400.6252 | 98.0987 | 141.1078 | 167.8391 | 138.4267
1243.2542 | 364.4672 | 409.8905 | 400.2131 | 98.2068 | 141.2421 | 167.9696 | 138.529
1244.2542 | 363.8903 | 409.0326 | 398.5697 | 98.3118 | 141.382 | 168.096 | 138.63
1245.2542 | 365.0763 | 409.3038 | 398.0227 | 98.4166 | 141.5151 | 168.2026 | 138.7319
1246.2542 | 366.2661 | 409.7688 | 398.3928 | 98.5022 | 141.6607 | 168.3157 | 138.8229
1247.2542 | 366.2266 | 408.5976 | 396.8262 | 98.6064 | 141.793 | 168.4487 | 138.9049
1248.2542 | 365.6178 | 408.3061 | 394.709 | 98.7289 | 141.9378 | 168.5739 | 139.0168
1249.2542 | 365.4272 | 408.6553 | 393.837 | 98.8239 | 142.0805 | 168.6888 | 139.1333
1250.2542 | 365.8129 | 409.7559 | 394.2624 | 98.9237 | 142.216 | 168.8138 | 139.2275
1251.2542 | 367.1605 | 410.4324 | 394.3024 | 99.0168 | 142.353 | 168.92 | 139.2996
1252.2542 | 366.2289 | 411.2897 | 394.4328 | 99.1184 | 142.5008 | 169.0457 | 139.4226
1253.2542 | 366.0641 | 411.099 | 393.8951 | 99.2209 | 142.6327 | 169.17 | 139.5265
1254.2542 | 367.5293 | 411.6345 | 394.5708 | 99.3169 | 142.7791 | 169.2969 | 139.6351
1255.2542 | 368.5973 | 411.71 | 395.3978 | 99.4397 | 142.9204 | 169.4205 | 139.7395
1256.2542 | 369.2155 | 411.773 | 396.3452 | 99.5394 | 143.0581 | 169.534 | 139.8436
1257.2542 | 369.9946 | 411.1316 | 396.8703 | 99.6385 | 143.1965 | 169.6607 | 139.9473
1258.2542 | 369.1492 | 411.7702 | 397.9982 | 99.7389 | 143.3285 | 169.7886 | 140.0245
1259.2542 | 368.8736 | 412.6386 | 398.492 | 99.8654 | 143.4721 | 169.9062 | 140.1183
1260.2542 | 367.9543 | 412.3508 | 397.1117 | 99.967 | 143.6071 | 170.0364 | 140.2396
1261.2542 | 367.6554 | 412.6599 | 396.4764 | 100.1063 | 143.7478 | 170.1665 | 140.3477
1262.2542 | 367.4243 | 411.9923 | 395.7587 | 100.2138 | 143.8923 | 170.2908 | 140.4643
1263.2542 | 368.095 | 412.5764 | 394.9244 | 100.3127 | 144.0272 | 170.41 | 140.555
1264.2542 | 367.7999 | 411.7436 | 393.6683 | 100.4269 | 144.1695 | 170.5268 | 140.6593
1265.2542 | 368.4309 | 411.2453 | 392.0946 | 100.5457 | 144.3062 | 170.6579 | 140.7504
1266.2542 | 369.0995 | 411.405 | 392.6723 | 100.6702 | 144.4411 | 170.789 | 140.8676
1267.2542 | 371.757 | 411.7174 | 393.2753 | 100.7721 | 144.5855 | 170.919 | 140.9787
1268.2542 | 370.4877 | 411.229 | 393.6098 | 100.8947 | 144.7249 | 171.0488 | 141.072
1269.2542 | 370.1671 | 410.9836 | 394.4177 | 101.0016 | 144.8675 | 171.168 | 141.1714
1270.2542 | 369.8075 | 410.3091 | 393.6577 | 101.1093 | 145.0141 | 171.3005 | 141.2469
1271.2542 | 370.5163 | 410.4036 | 392.5501 | 101.2324 | 145.145 | 171.4291 | 141.3793
1272.2542 | 370.3868 | 411.3769 | 393.3801 | 101.3259 | 145.2734 | 171.5537 | 141.4806
1273.2542 | 370.9206 | 411.2912 | 393.6793 | 101.46 | 145.4106 | 171.6882 | 141.5875
1274.2542 | 370.0375 | 411.1486 | 393.1783 | 101.5744 | 145.5426 | 171.8169 | 141.6994
1275.2542 | 369.743 | 411.3105 | 392.2428 | 101.6784 | 145.6748 | 171.9458 | 141.8072
1276.2542 | 369.3797 | 411.3772 | 390.8492 | 101.809 | 145.8084 | 172.0814 | 141.919
1277.2542 | 369.7781 | 410.403 | 388.9628 | 101.911 | 145.9323 | 172.1974 | 142.0373
1278.2542 | 369.4681 | 409.6017 | 388.073 | 102.0359 | 146.0587 | 172.3315 | 142.1542
1279.2542 | 370.89 | 411.3188 | 388.962 | 102.1596 | 146.2004 | 172.4518 | 142.2502
1280.2542 | 372.1142 | 412.1764 | 389.9233 | 102.2744 | 146.334 | 172.5987 | 142.3658
1281.2542 | 371.7187 | 411.8252 | 388.9449 | 102.3895 | 146.4616 | 172.7187 | 142.4648
1282.2542 | 372.527 | 412.6092 | 390.0656 | 102.5106 | 146.5928 | 172.8481 | 142.5645
1283.2542 | 373.5298 | 414.5566 | 392.5696 | 102.6225 | 146.7207 | 172.9765 | 142.6671
1284.2542 | 373.3893 | 415.0229 | 394.8149 | 102.7421 | 146.853 | 173.1086 | 142.772
1285.2542 | 372.7269 | 416.1244 | 395.9226 | 102.8604 | 146.9902 | 173.2393 | 142.8801
1286.2542 | 372.6184 | 416.7345 | 396.2205 | 102.9675 | 147.116 | 173.372 | 142.9963
1287.2542 | 372.5179 | 416.2638 | 395.4144 | 103.0994 | 147.2424 | 173.492 | 143.1147
1288.2542 | 374.453 | 415.9629 | 394.6592 | 103.2137 | 147.362 | 173.6243 | 143.2233
1289.2542 | 376.6405 | 414.8068 | 393.3828 | 103.3483 | 147.4928 | 173.7551 | 143.3333
1290.2542 | 375.8727 | 414.2915 | 392.2786 | 103.4561 | 147.6265 | 173.8912 | 143.4237
1291.2542 | 375.0444 | 413.4668 | 392.1231 | 103.5688 | 147.7681 | 174.0202 | 143.5062
1292.2542 | 373.7698 | 412.5849 | 391.6121 | 103.6989 | 147.8901 | 174.1502 | 143.631
1293.2542 | 373.122 | 412.9607 | 391.6444 | 103.8098 | 148.0232 | 174.2835 | 143.7467
1294.2542 | 372.4688 | 414.2602 | 392.556 | 103.9252 | 148.1604 | 174.4211 | 143.8411
1295.2542 | 372.9153 | 414.9315 | 392.6034 | 104.0364 | 148.2813 | 174.5555 | 143.9442
1296.2542 | 373.6606 | 414.2995 | 392.2124 | 104.1759 | 148.4114 | 174.688 | 144.0599
1297.2542 | 373.8169 | 413.1409 | 391.4145 | 104.2867 | 148.5494 | 174.8076 | 144.1493
1298.2542 | 374.9544 | 414.5511 | 391.3633 | 104.4107 | 148.6686 | 174.9446 | 144.2576
1299.2542 | 373.786 | 413.3946 | 390.0262 | 104.5319 | 148.7983 | 175.0715 | 144.3804
1300.2542 | 372.4257 | 411.7022 | 388.6037 | 104.6507 | 148.927 | 175.2011 | 144.4877
1301.2542 | 372.4207 | 410.3419 | 387.3279 | 104.7773 | 149.0546 | 175.3198 | 144.5976
1302.2542 | 372.0336 | 408.9974 | 386.6489 | 104.899 | 149.1909 | 175.4489 | 144.6884
1303.2542 | 371.1636 | 408.5984 | 386.692 | 105.0185 | 149.317 | 175.5786 | 144.8076
1304.2542 | 370.7099 | 408.0967 | 386.0819 | 105.1268 | 149.4417 | 175.72 | 144.9256
1305.2542 | 369.3755 | 406.862 | 384.493 | 105.2542 | 149.5675 | 175.842 | 145.0357
1306.2542 | 370.105 | 406.2367 | 383.2203 | 105.3863 | 149.7022 | 175.9769 | 145.1219
1307.2542 | 370.5359 | 405.173 | 381.1685 | 105.4965 | 149.8251 | 176.0949 | 145.227
1308.2542 | 369.1553 | 403.7258 | 379.8332 | 105.6143 | 149.9499 | 176.2376 | 145.3347
1309.2542 | 369.0261 | 403.4418 | 379.5293 | 105.7329 | 150.0764 | 176.3558 | 145.4391
1310.2542 | 368.515 | 403.441 | 379.5075 | 105.8563 | 150.2104 | 176.4866 | 145.5539
1311.2542 | 367.1822 | 400.9145 | 377.8795 | 105.9893 | 150.3259 | 176.6074 | 145.6507
1312.2542 | 367.5377 | 400.5327 | 378.752 | 106.1072 | 150.4506 | 176.7425 | 145.774
1313.2542 | 368.8864 | 400.6307 | 378.3292 | 106.2233 | 150.5613 | 176.8684 | 145.8525
1314.2542 | 369.7054 | 400.8601 | 378.1505 | 106.3403 | 150.6978 | 176.9857 | 145.9619
1315.2542 | 370.4252 | 400.5979 | 377.9841 | 106.4636 | 150.8206 | 177.1303 | 146.0755
1316.2542 | 370.4596 | 399.9853 | 378.176 | 106.5824 | 150.9431 | 177.2401 | 146.1822
1317.2542 | 370.3656 | 399.7233 | 377.6096 | 106.7126 | 151.0683 | 177.3753 | 146.2998
1318.2542 | 370.4812 | 398.7222 | 376.8963 | 106.8369 | 151.1897 | 177.4989 | 146.3949
1319.2542 | 370.629 | 399.7014 | 377.4006 | 106.9653 | 151.3194 | 177.633 | 146.5027
1320.2542 | 370.8024 | 401.2265 | 378.1916 | 107.072 | 151.4427 | 177.7441 | 146.5938
1321.2542 | 372.0629 | 401.8728 | 379.0752 | 107.1957 | 151.5661 | 177.8687 | 146.6942
1322.2542 | 371.6042 | 401.359 | 379.4311 | 107.329 | 151.6854 | 177.9931 | 146.8059
1323.2542 | 370.0963 | 400.4939 | 378.5212 | 107.442 | 151.8116 | 178.1226 | 146.8956
1324.2542 | 368.8204 | 400.2392 | 378.5932 | 107.5635 | 151.9346 | 178.2402 | 147.0127
1325.2542 | 368.7559 | 400.5301 | 378.4563 | 107.686 | 152.0613 | 178.3671 | 147.105
1326.2542 | 369.618 | 400.1849 | 378.2552 | 107.7982 | 152.1851 | 178.4904 | 147.1844
1327.2542 | 369.479 | 400.587 | 377.8131 | 107.9161 | 152.2973 | 178.6154 | 147.3042
1328.2542 | 368.1162 | 399.8288 | 378.1637 | 108.0405 | 152.4194 | 178.7401 | 147.4309
1329.2542 | 368.0807 | 399.7163 | 378.0265 | 108.1626 | 152.538 | 178.8618 | 147.5312
1330.2542 | 369.9479 | 399.7162 | 378.2747 | 108.2824 | 152.6665 | 178.9938 | 147.6168
1331.2542 | 369.7182 | 399.0201 | 377.9531 | 108.416 | 152.7841 | 179.1238 | 147.7424
1332.2542 | 368.5528 | 398.0672 | 376.6775 | 108.5511 | 152.912 | 179.2338 | 147.854
1333.2542 | 367.8036 | 397.6837 | 375.9433 | 108.665 | 153.0301 | 179.3695 | 147.9235
1334.2542 | 367.6338 | 399.2235 | 376.0093 | 108.765 | 153.1578 | 179.484 | 148.0155
1335.2542 | 366.8354 | 399.9798 | 375.8164 | 108.8935 | 153.287 | 179.6175 | 148.1109
1336.2542 | 365.8836 | 399.7291 | 374.8387 | 109.0247 | 153.4076 | 179.7297 | 148.2035
1337.2542 | 365.6677 | 399.3453 | 374.0944 | 109.1294 | 153.5267 | 179.8576 | 148.3003
1338.2542 | 364.6052 | 398.5163 | 372.6342 | 109.2436 | 153.6509 | 179.9769 | 148.4023
1339.2542 | 363.5223 | 398.0976 | 372.1917 | 109.3991 | 153.7771 | 180.1126 | 148.4946
1340.2542 | 364.4979 | 398.3933 | 372.186 | 109.4955 | 153.8925 | 180.2283 | 148.5768
1341.2542 | 364.8954 | 397.3902 | 371.6168 | 109.6525 | 154.0096 | 180.3528 | 148.7031
1342.2542 | 365.1704 | 396.4002 | 371.1327 | 109.7707 | 154.1274 | 180.4773 | 148.8139
1343.2542 | 365.0578 | 395.7377 | 370.1998 | 109.8749 | 154.2469 | 180.5951 | 148.897
1344.2542 | 365.1576 | 395.8303 | 370.5491 | 109.9973 | 154.3758 | 180.7139 | 148.9755
1345.2542 | 364.4108 | 394.9176 | 370.9612 | 110.1273 | 154.499 | 180.8365 | 149.0556
1346.2542 | 363.2402 | 393.7702 | 370.8074 | 110.2456 | 154.6232 | 180.958 | 149.1491
1347.2542 | 361.8749 | 393.1111 | 370.9796 | 110.3733 | 154.7492 | 181.0799 | 149.2374
1348.2542 | 360.7671 | 394.2592 | 371.5012 | 110.4842 | 154.868 | 181.2079 | 149.3283
1349.2542 | 359.5738 | 394.5494 | 371.3368 | 110.5924 | 154.9872 | 181.326 | 149.4208
1350.2542 | 358.0652 | 392.7722 | 370.4306 | 110.7226 | 155.0965 | 181.4482 | 149.513
1351.2542 | 357.0853 | 391.168 | 369.0469 | 110.8649 | 155.2147 | 181.5677 | 149.639
1352.2542 | 357.3504 | 389.9171 | 367.901 | 110.9971 | 155.3377 | 181.6911 | 149.7458
1353.2542 | 359.032 | 390.8001 | 368.4203 | 111.1311 | 155.4537 | 181.8129 | 149.8364
1354.2542 | 359.8351 | 393.0488 | 369.0942 | 111.2406 | 155.5728 | 181.9351 | 149.9331
1355.2542 | 360.658 | 393.9421 | 370.0626 | 111.3605 | 155.6924 | 182.0448 | 150.0177
1356.2542 | 362.2305 | 393.7812 | 369.8544 | 111.473 | 155.8072 | 182.1532 | 150.1051
1357.2542 | 362.9744 | 393.0505 | 369.4362 | 111.6082 | 155.9308 | 182.2781 | 150.2026
1358.2542 | 362.8934 | 391.9771 | 368.241 | 111.7336 | 156.0466 | 182.4035 | 150.3065
1359.2542 | 362.2825 | 391.4219 | 369.0463 | 111.8591 | 156.1651 | 182.5268 | 150.406
1360.2542 | 361.9484 | 391.3417 | 370.1495 | 111.9735 | 156.2898 | 182.644 | 150.4884
1361.2542 | 362.9957 | 391.0763 | 370.7261 | 112.11 | 156.4056 | 182.7582 | 150.5708
1362.2542 | 365.1913 | 391.9225 | 370.3542 | 112.2206 | 156.5226 | 182.8773 | 150.6668
1363.2542 | 365.7114 | 392.0922 | 369.4635 | 112.3399 | 156.6393 | 182.9921 | 150.7529
1364.2542 | 366.5813 | 392.708 | 370.3879 | 112.4837 | 156.7632 | 183.1168 | 150.8499
1365.2542 | 367.2513 | 393.4816 | 370.8574 | 112.6029 | 156.8833 | 183.2341 | 150.9424
1366.2542 | 367.2797 | 393.5508 | 372.4141 | 112.7384 | 156.993 | 183.3488 | 151.0358
1367.2542 | 366.8367 | 394.1769 | 372.8117 | 112.8642 | 157.1184 | 183.4742 | 151.129
1368.2542 | 367.4524 | 394.8964 | 372.6432 | 112.9785 | 157.2406 | 183.5938 | 151.2282
1369.2542 | 367.4452 | 394.7895 | 372.654 | 113.0961 | 157.3548 | 183.7035 | 151.3068
1370.2542 | 368.0624 | 395.7491 | 372.3412 | 113.232 | 157.4699 | 183.8183 | 151.4016
1371.2542 | 368.2117 | 395.3173 | 371.836 | 113.3525 | 157.5901 | 183.9317 | 151.505
1372.2542 | 369.2141 | 395.55 | 371.0399 | 113.4626 | 157.7194 | 184.0558 | 151.5918
1373.2542 | 370.494 | 395.6559 | 370.5198 | 113.5971 | 157.8531 | 184.1821 | 151.6928
1374.2542 | 372.7238 | 396.4537 | 370.18 | 113.7287 | 157.9722 | 184.2936 | 151.791
1375.2542 | 372.9407 | 396.4138 | 370.1005 | 113.8626 | 158.0983 | 184.4125 | 151.8973
1376.2542 | 373.9169 | 396.981 | 371.0465 | 113.9737 | 158.2241 | 184.5205 | 151.9937
1377.2542 | 374.5005 | 396.8776 | 371.8785 | 114.1129 | 158.3385 | 184.645 | 152.0733
1378.2542 | 374.5321 | 396.5594 | 372.2443 | 114.2395 | 158.4664 | 184.7636 | 152.1637
1379.2542 | 376.6367 | 397.4674 | 373.0483 | 114.3681 | 158.5972 | 184.8899 | 152.2534
1380.2542 | 377.7446 | 397.3635 | 372.9746 | 114.4722 | 158.7144 | 185.0026 | 152.3383
1381.2542 | 379.0464 | 397.5665 | 374.7942 | 114.6044 | 158.8338 | 185.1117 | 152.4507
1382.2542 | 379.6589 | 397.1033 | 374.0923 | 114.7389 | 158.9628 | 185.2106 | 152.5493
1383.2542 | 378.852 | 398.0651 | 374.1028 | 114.8587 | 159.0823 | 185.3401 | 152.6507
1384.2542 | 380.5265 | 399.2594 | 374.265 | 114.9933 | 159.1983 | 185.462 | 152.7478
1385.2542 | 378.6844 | 399.8207 | 375.3872 | 115.1235 | 159.3293 | 185.568 | 152.8396
1386.2542 | 378.926 | 399.5027 | 375.8667 | 115.2324 | 159.4512 | 185.6869 | 152.9277
1387.2542 | 378.5412 | 400.4535 | 377.1828 | 115.3734 | 159.5778 | 185.8061 | 153.0287
1388.2542 | 378.3866 | 402.506 | 379.979 | 115.4859 | 159.6965 | 185.9151 | 153.1195
1389.2542 | 378.3828 | 403.5509 | 379.7791 | 115.6155 | 159.828 | 186.0457 | 153.2097
1390.2542 | 378.4333 | 403.3825 | 379.4452 | 115.754 | 159.9585 | 186.1611 | 153.2888
1391.2542 | 377.8806 | 403.5113 | 379.8849 | 115.8822 | 160.0804 | 186.271 | 153.4001
1392.2542 | 377.5887 | 404.7352 | 381.5139 | 116.0107 | 160.1959 | 186.3921 | 153.4963
1393.2542 | 376.6353 | 404.5799 | 381.6173 | 116.1497 | 160.3242 | 186.5077 | 153.5965
1394.2542 | 376.6556 | 404.416 | 381.0307 | 116.2549 | 160.453 | 186.6293 | 153.6961
1395.2542 | 377.7913 | 405.8975 | 381.389 | 116.3864 | 160.569 | 186.7524 | 153.7919
1396.2542 | 378.1845 | 406.8243 | 381.187 | 116.5208 | 160.6955 | 186.8745 | 153.9031
1397.2542 | 378.2481 | 406.7742 | 380.7506 | 116.6567 | 160.825 | 186.9805 | 154.0076
1398.2542 | 378.0055 | 407.8003 | 381.766 | 116.7837 | 160.9558 | 187.1043 | 154.1036
1399.2542 | 380.7879 | 408.5692 | 383.3823 | 116.9053 | 161.0913 | 187.2116 | 154.1808
1400.2542 | 381.2771 | 408.7267 | 384.9353 | 117.0245 | 161.2136 | 187.3333 | 154.2815
1401.2542 | 380.2116 | 409.0055 | 385.47 | 117.1599 | 161.3426 | 187.4543 | 154.3743
1402.2542 | 379.1796 | 409.3437 | 384.8777 | 117.2746 | 161.4831 | 187.5664 | 154.4802
1403.2542 | 379.7762 | 410.6715 | 385.4133 | 117.4113 | 161.6086 | 187.6898 | 154.5543
1404.2542 | 380.0667 | 412.3207 | 386.5016 | 117.5331 | 161.7386 | 187.8111 | 154.6541
1405.2542 | 380.1405 | 412.2446 | 387.1418 | 117.6747 | 161.8686 | 187.926 | 154.7598
1406.2542 | 380.1562 | 412.5465 | 387.0132 | 117.7775 | 161.9941 | 188.0447 | 154.8465
1407.2542 | 380.4879 | 413.3202 | 388.69 | 117.9264 | 162.123 | 188.1629 | 154.9503
1408.2542 | 381.4421 | 413.786 | 390.2885 | 118.0439 | 162.26 | 188.2723 | 155.0466
1409.2542 | 381.6014 | 414.9774 | 390.7608 | 118.179 | 162.3866 | 188.3835 | 155.1511
1410.2542 | 383.7407 | 415.8306 | 389.7655 | 118.3022 | 162.5164 | 188.506 | 155.2518
1411.2542 | 383.5328 | 417.2167 | 389.7863 | 118.4291 | 162.643 | 188.6315 | 155.3495
1412.2542 | 382.0854 | 416.4969 | 389.6889 | 118.5676 | 162.7609 | 188.7488 | 155.4601
1413.2542 | 382.1934 | 415.969 | 389.2263 | 118.68 | 162.8962 | 188.8651 | 155.5551
1414.2542 | 381.5566 | 416.0724 | 389.1591 | 118.8041 | 163.0319 | 188.9851 | 155.6429
1415.2542 | 381.4938 | 416.2938 | 389.4246 | 118.9526 | 163.1633 | 189.0999 | 155.7403
1416.2542 | 382.1144 | 415.8343 | 388.6133 | 119.0753 | 163.2971 | 189.221 | 155.8516
1417.2542 | 381.8088 | 415.3888 | 387.7902 | 119.2065 | 163.4266 | 189.3353 | 155.9553
1418.2542 | 382.9251 | 414.5922 | 388.0377 | 119.3336 | 163.5659 | 189.4526 | 156.0578
1419.2542 | 383.8926 | 414.0254 | 389.4319 | 119.4721 | 163.697 | 189.5722 | 156.1479
1420.2542 | 382.2034 | 413.8406 | 390.6628 | 119.5974 | 163.8267 | 189.6783 | 156.2534
1421.2542 | 381.6398 | 413.3671 | 390.2347 | 119.7069 | 163.9682 | 189.799 | 156.3403
1422.2542 | 381.7418 | 412.6302 | 390.6626 | 119.8415 | 164.1003 | 189.9201 | 156.4582
1423.2542 | 382.7359 | 414.6189 | 391.5457 | 119.9609 | 164.2408 | 190.0365 | 156.5556
1424.2542 | 382.4642 | 414.3508 | 391.0638 | 120.1033 | 164.3687 | 190.1549 | 156.6582
1425.2542 | 381.5668 | 413.9891 | 390.6862 | 120.2323 | 164.51 | 190.2736 | 156.7663
1426.2542 | 381.7574 | 413.8481 | 391.6828 | 120.3516 | 164.6385 | 190.3878 | 156.8657
1427.2542 | 380.5373 | 413.725 | 391.9956 | 120.4881 | 164.7729 | 190.4962 | 156.9737
1428.2542 | 379.9054 | 412.6005 | 391.8879 | 120.608 | 164.9041 | 190.6238 | 157.0948
1429.2542 | 379.5559 | 412.2921 | 391.8524 | 120.7235 | 165.0409 | 190.742 | 157.1987
1430.2542 | 379.0601 | 413.3281 | 393.359 | 120.8744 | 165.1783 | 190.8594 | 157.3031
1431.2542 | 378.8036 | 413.0645 | 392.9372 | 121.0002 | 165.2996 | 190.9702 | 157.4009
1432.2542 | 378.7055 | 412.7786 | 392.1747 | 121.1129 | 165.4345 | 191.0807 | 157.5062
1433.2542 | 379.008 | 413.2248 | 392.6141 | 121.25 | 165.5711 | 191.1925 | 157.6061
1434.2542 | 380.4175 | 413.3306 | 394.1954 | 121.3823 | 165.7024 | 191.3134 | 157.7156
1435.2542 | 379.2968 | 413.3489 | 395.0131 | 121.4934 | 165.8432 | 191.4364 | 157.8304
1436.2542 | 378.3954 | 412.3305 | 395.1966 | 121.6303 | 165.9706 | 191.5494 | 157.9254
1437.2542 | 378.28 | 412.6551 | 395.8809 | 121.7683 | 166.1036 | 191.6638 | 158.0371
1438.2542 | 379.4048 | 412.5818 | 395.2204 | 121.885 | 166.2385 | 191.7773 | 158.1521
1439.2542 | 380.0587 | 412.939 | 396.2193 | 121.9804 | 166.3618 | 191.8903 | 158.2466
1440.2542 | 379.6521 | 413.0167 | 394.8394 | 122.1415 | 166.4972 | 192.0014 | 158.3625
1441.2542 | 380.1006 | 414.1728 | 394.8205 | 122.2565 | 166.6253 | 192.1115 | 158.4524
1442.2542 | 381.9093 | 414.3829 | 394.1064 | 122.3787 | 166.7534 | 192.2226 | 158.5647
1443.2542 | 381.7533 | 415.4383 | 393.5447 | 122.5189 | 166.8796 | 192.3432 | 158.6725
1444.2542 | 381.8114 | 415.0011 | 392.7645 | 122.6331 | 167.0082 | 192.4506 | 158.7642
1445.2542 | 383.1286 | 415.1895 | 391.7608 | 122.746 | 167.1334 | 192.5606 | 158.876
1446.2542 | 383.4621 | 415.2918 | 391.5917 | 122.9085 | 167.2616 | 192.6775 | 158.9725
1447.2542 | 384.8856 | 415.7852 | 391.6469 | 123.0375 | 167.3881 | 192.7886 | 159.0687
1448.2542 | 385.5846 | 416.3237 | 392.8239 | 123.1552 | 167.5207 | 192.9025 | 159.1796
1449.2542 | 385.6562 | 416.188 | 391.416 | 123.2645 | 167.668 | 193.0192 | 159.2813
1450.2542 | 386.7192 | 416.1681 | 390.8246 | 123.42 | 167.7997 | 193.1141 | 159.373
1451.2542 | 388.9329 | 416.8671 | 390.2301 | 123.5368 | 167.9234 | 193.2412 | 159.4864
1452.2542 | 391.3845 | 418.4958 | 391.2428 | 123.6657 | 168.0469 | 193.366 | 159.5969
1453.2542 | 390.6861 | 418.8333 | 391.3257 | 123.7813 | 168.1831 | 193.4737 | 159.6853
1454.2542 | 390.8205 | 418.5199 | 392.0191 | 123.9113 | 168.3084 | 193.576 | 159.7819
1455.2542 | 390.9474 | 418.5339 | 391.6447 | 124.0357 | 168.446 | 193.6865 | 159.8887
1456.2698 | 390.7259 | 418.4362 | 391.1169 | 124.1636 | 168.5724 | 193.8108 | 159.9884
1457.2542 | 390.2927 | 418.0161 | 390.4857 | 124.2912 | 168.702 | 193.9067 | 160.0944
1458.2542 | 389.3354 | 417.189 | 390.1783 | 124.4201 | 168.8285 | 194.0271 | 160.1894
1459.2542 | 388.8348 | 417.4365 | 391.2693 | 124.5531 | 168.9584 | 194.1344 | 160.2817
1460.2542 | 388.068 | 417.2876 | 392.4372 | 124.6906 | 169.0843 | 194.2537 | 160.3994
1461.2542 | 388.4533 | 416.8202 | 394.0066 | 124.8037 | 169.2123 | 194.3716 | 160.5119
1462.2542 | 387.077 | 417.0775 | 394.1114 | 124.9389 | 169.3483 | 194.4687 | 160.6028
1463.2542 | 387.1091 | 417.1214 | 393.8618 | 125.0693 | 169.4729 | 194.5934 | 160.7071
1464.2542 | 386.761 | 417.9582 | 393.2187 | 125.1881 | 169.6047 | 194.6971 | 160.8217
1465.2542 | 385.5869 | 417.8985 | 392.9622 | 125.3251 | 169.7408 | 194.8087 | 160.9078
1466.2542 | 384.6375 | 417.2569 | 393.3941 | 125.4415 | 169.8711 | 194.9305 | 161.0073
1467.2542 | 383.6968 | 416.4197 | 393.5925 | 125.5853 | 170.0078 | 195.0396 | 161.1365
1468.2542 | 383.3509 | 416.9289 | 393.9375 | 125.7071 | 170.1369 | 195.1647 | 161.2363
1469.2542 | 382.6876 | 417.5158 | 394.4413 | 125.8463 | 170.2645 | 195.2596 | 161.3486
1470.2542 | 381.4508 | 417.5107 | 395.6947 | 125.9661 | 170.4024 | 195.3823 | 161.4518
1471.2542 | 382.0085 | 417.3683 | 394.5478 | 126.0899 | 170.5338 | 195.4842 | 161.5461
1472.2542 | 382.3825 | 416.751 | 392.9036 | 126.2252 | 170.6681 | 195.5966 | 161.657
1473.2542 | 382.4354 | 417.4939 | 392.4708 | 126.3371 | 170.8032 | 195.7152 | 161.7465
1474.2542 | 383.2612 | 417.207 | 393.3651 | 126.4689 | 170.9408 | 195.8323 | 161.8286
1475.2542 | 382.9909 | 417.6918 | 393.0382 | 126.5952 | 171.0702 | 195.9458 | 161.956
1476.2542 | 383.9846 | 417.3195 | 393.7331 | 126.7393 | 171.1984 | 196.0554 | 162.0504
1477.2542 | 385.1628 | 418.6158 | 394.5498 | 126.8574 | 171.3333 | 196.1836 | 162.1602
1478.2542 | 385.605 | 418.5088 | 394.6278 | 126.9913 | 171.4657 | 196.2867 | 162.2623
1479.2542 | 384.7643 | 419.0802 | 397.7908 | 127.1146 | 171.6011 | 196.408 | 162.3852
1480.2542 | 387.1083 | 421.3947 | 398.7999 | 127.2454 | 171.7292 | 196.5143 | 162.4844
1481.2542 | 388.1433 | 422.1783 | 398.9961 | 127.3721 | 171.8723 | 196.6376 | 162.5855
1482.2542 | 388.8656 | 422.1217 | 399.7794 | 127.4904 | 171.9993 | 196.7668 | 162.6918
1483.2542 | 388.9219 | 420.9827 | 399.9115 | 127.6187 | 172.1342 | 196.8709 | 162.7621
1484.2542 | 389.2475 | 421.5212 | 397.9401 | 127.7675 | 172.2653 | 196.992 | 162.8782
1485.2542 | 389.0326 | 421.2014 | 398.1166 | 127.8966 | 172.4087 | 197.1088 | 162.9734
1486.2542 | 389.3754 | 421.3835 | 399.1247 | 128.014 | 172.5388 | 197.2224 | 163.0872
1487.2542 | 388.4222 | 421.7667 | 397.9479 | 128.1436 | 172.6695 | 197.3429 | 163.1991
1488.2542 | 387.31 | 421.6453 | 397.0702 | 128.2806 | 172.805 | 197.4471 | 163.3195
1489.2542 | 387.1842 | 421.6468 | 396.2245 | 128.4092 | 172.9352 | 197.5746 | 163.4208
1490.2542 | 387.212 | 421.4113 | 394.4019 | 128.537 | 173.0694 | 197.6811 | 163.514
1491.2542 | 388.0425 | 422.1489 | 396.3058 | 128.6632 | 173.2037 | 197.7964 | 163.601
1492.2542 | 388.1266 | 421.7771 | 395.1502 | 128.8009 | 173.335 | 197.9017 | 163.7268
1493.2542 | 387.4551 | 422.4659 | 395.794 | 128.9218 | 173.4669 | 198.0269 | 163.8325
1494.2542 | 386.4363 | 422.3526 | 394.9634 | 129.0495 | 173.5857 | 198.1378 | 163.9446
1495.2542 | 386.6342 | 421.3442 | 394.7445 | 129.1824 | 173.7263 | 198.2504 | 164.0456
1496.2542 | 388.0562 | 420.8544 | 394.8357 | 129.3057 | 173.8513 | 198.3617 | 164.1412
1497.2542 | 388.6856 | 419.9292 | 394.0804 | 129.4413 | 173.9934 | 198.4755 | 164.2516
1498.2542 | 388.6934 | 419.2752 | 392.8843 | 129.563 | 174.1182 | 198.586 | 164.3518
1499.2542 | 387.3851 | 419.5294 | 391.6327 | 129.7105 | 174.2426 | 198.7036 | 164.4636
1500.2542 | 387.0574 | 418.695 | 390.2987 | 129.8271 | 174.376 | 198.8278 | 164.5752
1501.2542 | 387.0284 | 417.5046 | 389.6825 | 129.9638 | 174.5032 | 198.9306 | 164.689
1502.2542 | 387.1278 | 417.181 | 389.4732 | 130.0788 | 174.6383 | 199.0318 | 164.7874
1503.2542 | 387.5923 | 418.4322 | 390.3919 | 130.213 | 174.7591 | 199.1568 | 164.9058
1504.2542 | 387.2541 | 418.539 | 391.2434 | 130.3364 | 174.8895 | 199.2755 | 165.0016
1505.2542 | 387.0335 | 419.383 | 392.0811 | 130.4678 | 175.0203 | 199.3944 | 165.1086
1506.2542 | 387.7181 | 420.9281 | 392.6849 | 130.6026 | 175.1398 | 199.4999 | 165.22
1507.2542 | 388.9793 | 421.7793 | 393.0448 | 130.722 | 175.2708 | 199.6112 | 165.3135
1508.2542 | 390.0912 | 422.6141 | 392.4252 | 130.8778 | 175.3947 | 199.73 | 165.4424
1509.2542 | 390.5911 | 423.2986 | 392.3038 | 131.0004 | 175.5186 | 199.8481 | 165.5501
1510.2542 | 391.8083 | 423.9881 | 392.1751 | 131.1078 | 175.6461 | 199.9566 | 165.6439
1511.2542 | 393.1663 | 425.893 | 391.9204 | 131.2337 | 175.7755 | 200.0737 | 165.7519
1512.2542 | 392.8402 | 425.3451 | 391.7542 | 131.3725 | 175.8952 | 200.1871 | 165.8642
1513.2542 | 393.2739 | 425.7042 | 390.894 | 131.4999 | 176.0255 | 200.2879 | 165.9556
1514.2542 | 394.601 | 426.3438 | 390.8648 | 131.6411 | 176.1476 | 200.4098 | 166.0733
1515.2542 | 396.4866 | 425.2361 | 389.6325 | 131.7581 | 176.2713 | 200.5274 | 166.1783
1516.2542 | 398.1625 | 427.1942 | 389.9625 | 131.8696 | 176.4086 | 200.639 | 166.2812
1517.2542 | 397.4891 | 426.2672 | 389.1412 | 132.0243 | 176.5313 | 200.7556 | 166.3777
1518.2542 | 397.1192 | 426.7904 | 390.177 | 132.1558 | 176.6542 | 200.8781 | 166.4986
1519.2542 | 396.7144 | 426.926 | 391.9114 | 132.2971 | 176.789 | 200.9836 | 166.5882
1520.2542 | 395.736 | 426.571 | 393.456 | 132.4172 | 176.9114 | 201.0992 | 166.6846
1521.2542 | 395.6368 | 428.6857 | 396.1851 | 132.5426 | 177.0436 | 201.2319 | 166.7717
1522.2542 | 396.6048 | 429.8504 | 398.194 | 132.6797 | 177.1725 | 201.3349 | 166.8794
1523.2542 | 396.1129 | 430.3207 | 399.3941 | 132.803 | 177.3054 | 201.449 | 166.9829
1524.2542 | 396.8485 | 431.3256 | 399.9348 | 132.9373 | 177.4345 | 201.5798 | 167.1154
1525.2542 | 396.8867 | 430.7542 | 399.7615 | 133.0539 | 177.5623 | 201.6828 | 167.2383
1526.2542 | 396.8099 | 430.6681 | 399.4617 | 133.1829 | 177.6977 | 201.8047 | 167.3442
1527.2542 | 397.5349 | 430.4402 | 399.6777 | 133.3099 | 177.8132 | 201.9054 | 167.439
1528.2542 | 397.1021 | 431.9084 | 401.1233 | 133.4507 | 177.949 | 202.0315 | 167.54
1529.2542 | 398.0852 | 433.2811 | 401.9575 | 133.5806 | 178.0763 | 202.1504 | 167.6317
1530.2542 | 398.9563 | 434.0757 | 402.4535 | 133.6943 | 178.2035 | 202.2727 | 167.7394
1531.2542 | 400.2074 | 434.2301 | 401.5339 | 133.8277 | 178.327 | 202.3817 | 167.8517
1532.2542 | 401.7103 | 437.1496 | 403.6117 | 133.9613 | 178.4537 | 202.5089 | 167.9586
1533.2542 | 403.0822 | 438.7039 | 405.0444 | 134.0995 | 178.5731 | 202.6145 | 168.0701
1534.2542 | 404.3525 | 439.1421 | 407.8442 | 134.2378 | 178.7035 | 202.7453 | 168.1767
1535.2542 | 405.7559 | 440.2597 | 407.2057 | 134.3554 | 178.8299 | 202.8517 | 168.2783
1536.2542 | 409.809 | 442.8276 | 409.7936 | 134.4852 | 178.9593 | 202.9788 | 168.3908
1537.2542 | 412.0459 | 445.1371 | 410.2814 | 134.6139 | 179.0934 | 203.084 | 168.4891
1538.2542 | 411.7296 | 447.2327 | 411.6901 | 134.7551 | 179.22 | 203.2061 | 168.5889
1539.2542 | 412.4143 | 448.2719 | 412.327 | 134.8705 | 179.3549 | 203.3281 | 168.6908
1540.2542 | 412.9165 | 449.5799 | 413.0162 | 135.0143 | 179.4809 | 203.4411 | 168.7996
1541.2542 | 413.1441 | 449.4908 | 414.6036 | 135.1457 | 179.6219 | 203.5566 | 168.9273
1542.2542 | 413.5892 | 449.4964 | 416.0977 | 135.2719 | 179.7548 | 203.6764 | 169.0395
1543.2542 | 413.6216 | 448.6952 | 417.0061 | 135.3792 | 179.8883 | 203.8034 | 169.1334
1544.2542 | 411.976 | 448.439 | 417.5105 | 135.5602 | 180.0231 | 203.9344 | 169.258
1545.2542 | 412.6656 | 447.56 | 417.7622 | 135.6788 | 180.1618 | 204.0432 | 169.364
1546.2542 | 413.7763 | 446.9014 | 416.5987 | 135.8047 | 180.2973 | 204.1624 | 169.468
1547.2542 | 415.3398 | 447.1904 | 416.8178 | 135.9342 | 180.4393 | 204.2852 | 169.5709
1548.2542 | 415.1254 | 447.1908 | 416.2699 | 136.0666 | 180.5867 | 204.4028 | 169.6621
1549.2542 | 414.2661 | 446.0167 | 415.0183 | 136.2049 | 180.7194 | 204.5209 | 169.7607
1550.2542 | 412.3332 | 445.1423 | 414.4215 | 136.3179 | 180.857 | 204.6327 | 169.8359
1551.2542 | 411.9323 | 444.9059 | 414.0382 | 136.4586 | 181.0007 | 204.7589 | 169.955
1552.2542 | 412.4079 | 444.1465 | 413.9007 | 136.5982 | 181.1352 | 204.8686 | 170.0387
1553.2542 | 412.635 | 445.9627 | 414.9601 | 136.7315 | 181.2728 | 204.9915 | 170.1535
1554.2542 | 413.7047 | 447.1906 | 414.6945 | 136.8522 | 181.4117 | 205.1146 | 170.2714
1555.2542 | 416.416 | 446.9059 | 414.6572 | 136.9944 | 181.548 | 205.2269 | 170.3764
1556.2542 | 419.3555 | 449.477 | 414.1075 | 137.1246 | 181.6869 | 205.3376 | 170.4705
1557.2542 | 421.1219 | 451.9563 | 415.1047 | 137.2646 | 181.8241 | 205.4483 | 170.5846
1558.2542 | 422.7507 | 453.4362 | 414.7209 | 137.388 | 181.9653 | 205.5722 | 170.6834
1559.2542 | 424.209 | 454.4491 | 417.2295 | 137.5083 | 182.1071 | 205.6781 | 170.788
1560.2542 | 423.9209 | 456.8196 | 419.146 | 137.6501 | 182.2377 | 205.7918 | 170.8869
1561.2542 | 422.72 | 455.6723 | 417.9419 | 137.7842 | 182.3885 | 205.9112 | 171.0058
1562.2542 | 424.0064 | 458.2931 | 419.5443 | 137.9132 | 182.5122 | 206.0274 | 171.114
1563.2542 | 425.0247 | 458.3756 | 418.3753 | 138.0424 | 182.6554 | 206.1476 | 171.2186
1564.2542 | 425.7893 | 458.8539 | 419.4768 | 138.1855 | 182.79 | 206.2711 | 171.3377
1565.2542 | 426.3761 | 461.2057 | 420.9576 | 138.3355 | 182.9308 | 206.3689 | 171.453
1566.2542 | 426.2485 | 463.8816 | 420.6055 | 138.4451 | 183.0694 | 206.5016 | 171.5649
1567.2542 | 426.8629 | 464.1846 | 422.0762 | 138.5947 | 183.2191 | 206.6273 | 171.6591
1568.2542 | 426.3199 | 464.4134 | 420.805 | 138.7137 | 183.3504 | 206.7399 | 171.7762
1569.2542 | 426.8529 | 464.9927 | 422.243 | 138.8594 | 183.4886 | 206.8553 | 171.9084
1570.2542 | 428.0044 | 466.5498 | 423.7478 | 138.9989 | 183.633 | 206.9843 | 172.0247
1571.2542 | 428.5488 | 466.2597 | 422.549 | 139.1346 | 183.7761 | 207.0843 | 172.1292
1572.2542 | 428.8107 | 466.4706 | 423.8629 | 139.249 | 183.9132 | 207.201 | 172.2458
1573.2542 | 430.2831 | 465.8431 | 426.4118 | 139.3925 | 184.0586 | 207.3298 | 172.3629
1574.2542 | 431.5477 | 467.2067 | 426.5337 | 139.5262 | 184.2042 | 207.4425 | 172.4787
1575.2542 | 431.3254 | 468.3202 | 426.3323 | 139.6648 | 184.3494 | 207.5513 | 172.5989
1576.2542 | 433.9567 | 469.9226 | 426.8782 | 139.7959 | 184.4941 | 207.6661 | 172.7124
1577.2542 | 435.6493 | 471.6763 | 431.5421 | 139.9278 | 184.6363 | 207.7888 | 172.8432
1578.2542 | 433.7888 | 472.2468 | 431.6935 | 140.0636 | 184.7777 | 207.9043 | 172.9513
1579.2542 | 432.6266 | 471.665 | 431.9272 | 140.1955 | 184.9198 | 208.0155 | 173.077
1580.2542 | 431.5821 | 469.9497 | 430.0559 | 140.3243 | 185.0616 | 208.1494 | 173.2138
1581.2542 | 431.6875 | 471.8354 | 431.2997 | 140.4539 | 185.2081 | 208.2504 | 173.3253
1582.2542 | 432.2234 | 475.6442 | 433.4095 | 140.5938 | 185.3536 | 208.375 | 173.4496
1583.2542 | 432.2332 | 478.5579 | 432.1979 | 140.7213 | 185.5078 | 208.4911 | 173.5656
1584.2542 | 432.4814 | 480.9421 | 434.6772 | 140.8646 | 185.6457 | 208.6091 | 173.6784
1585.2542 | 435.8163 | 481.597 | 434.8638 | 141.002 | 185.7965 | 208.726 | 173.824
1586.2542 | 437.9785 | 482.6622 | 435.6718 | 141.1298 | 185.9357 | 208.8379 | 173.949
1587.2542 | 440.2948 | 485.2044 | 437.6897 | 141.2627 | 186.0881 | 208.9661 | 174.0871
1588.2542 | 438.5745 | 485.4613 | 438.1394 | 141.3945 | 186.2302 | 209.0768 | 174.2121
1589.2542 | 438.9783 | 487.7333 | 437.8581 | 141.5187 | 186.3707 | 209.1942 | 174.3319
1590.2542 | 439.5949 | 489.5348 | 438.3485 | 141.6579 | 186.5243 | 209.3253 | 174.4461
1591.2542 | 439.1653 | 491.8555 | 440.4135 | 141.7829 | 186.6691 | 209.4535 | 174.5801
1592.2542 | 440.3266 | 493.6327 | 441.7228 | 141.922 | 186.8209 | 209.5695 | 174.6964
1593.2542 | 440.0756 | 496.3226 | 444.7663 | 142.0484 | 186.9698 | 209.6857 | 174.8203
1594.2542 | 438.4185 | 495.5905 | 447.7636 | 142.1966 | 187.1222 | 209.8193 | 174.9487
1595.2542 | 436.8604 | 494.9993 | 449.0142 | 142.317 | 187.2911 | 209.9461 | 175.0668
1596.2542 | 438.7553 | 497.4196 | 450.5599 | 142.4599 | 187.4368 | 210.0633 | 175.1881
1597.2542 | 439.0036 | 500.5893 | 451.8817 | 142.5947 | 187.5813 | 210.1927 | 175.3546
1598.2542 | 439.0266 | 501.6307 | 453.0988 | 142.7282 | 187.7376 | 210.3163 | 175.4728
1599.2542 | 440.9145 | 502.8595 | 453.7995 | 142.8605 | 187.8927 | 210.4459 | 175.5985
1600.2542 | 441.2445 | 505.4693 | 454.6716 | 143.0139 | 188.0423 | 210.5616 | 175.7401
1601.2542 | 439.8913 | 507.1466 | 453.5807 | 143.1362 | 188.2076 | 210.6906 | 175.8689
1602.2542 | 439.9166 | 510.403 | 454.6845 | 143.2699 | 188.372 | 210.797 | 175.9806
1603.2542 | 439.6952 | 508.7062 | 452.9636 | 143.4015 | 188.5299 | 210.9226 | 176.1145
1604.2542 | 441.2917 | 508.0555 | 453.7933 | 143.5362 | 188.6768 | 211.0474 | 176.2616
1605.2542 | 441.2777 | 508.967 | 455.4013 | 143.6658 | 188.8401 | 211.1553 | 176.3646
1606.2542 | 440.9595 | 508.841 | 455.264 | 143.7935 | 188.9985 | 211.2879 | 176.496
1607.2542 | 442.1273 | 508.0623 | 455.2822 | 143.9442 | 189.155 | 211.4059 | 176.6313
1608.2542 | 443.3545 | 507.2224 | 454.4317 | 144.0502 | 189.3084 | 211.5102 | 176.7608
1609.2542 | 443.5573 | 504.8466 | 454.238 | 144.1986 | 189.4654 | 211.633 | 176.8997
1610.2542 | 442.6377 | 506.4356 | 452.7216 | 144.3458 | 189.6314 | 211.7551 | 177.0154
1611.2542 | 443.2534 | 507.9611 | 454.2231 | 144.4769 | 189.7889 | 211.8844 | 177.1488
1612.2542 | 442.3716 | 507.9677 | 455.5526 | 144.6032 | 189.9445 | 211.997 | 177.2957
1613.2542 | 440.8584 | 508.7769 | 458.2053 | 144.7364 | 190.1042 | 212.1268 | 177.4376
1614.2542 | 439.7585 | 509.5367 | 458.8498 | 144.8691 | 190.2603 | 212.2342 | 177.5518
1615.2542 | 441.048 | 511.9352 | 460.8059 | 145.0205 | 190.429 | 212.3584 | 177.7032
1616.2542 | 443.7139 | 512.7753 | 464.9606 | 145.1581 | 190.5864 | 212.4686 | 177.8338
1617.2542 | 445.3387 | 512.5954 | 464.8075 | 145.297 | 190.7471 | 212.596 | 177.9705
1618.2542 | 445.2386 | 512.6337 | 465.4284 | 145.4246 | 190.9001 | 212.7153 | 178.1196
1619.2542 | 447.5873 | 511.8483 | 467.7902 | 145.5401 | 191.0629 | 212.8401 | 178.2441
1620.2542 | 449.8122 | 511.5104 | 468.2424 | 145.6881 | 191.2214 | 212.9713 | 178.3682
1621.2542 | 449.3759 | 514.7503 | 467.2584 | 145.82 | 191.3859 | 213.0887 | 178.5123
1622.2542 | 449.2695 | 515.303 | 467.5853 | 145.9711 | 191.5455 | 213.2158 | 178.6596
1623.2542 | 451.0286 | 518.7068 | 467.0172 | 146.0913 | 191.706 | 213.3406 | 178.8009
1624.2542 | 451.6882 | 518.3236 | 466.4987 | 146.2394 | 191.878 | 213.461 | 178.9449
1625.2542 | 455.3059 | 520.9574 | 469.6509 | 146.3802 | 192.0433 | 213.585 | 179.0904
1626.2542 | 455.6779 | 526.2666 | 471.3291 | 146.5074 | 192.1987 | 213.7099 | 179.2168
1627.2542 | 457.1381 | 526.4004 | 472.8611 | 146.6262 | 192.3675 | 213.8265 | 179.3543
1628.2542 | 456.9298 | 523.619 | 470.8803 | 146.7888 | 192.5374 | 213.9571 | 179.4927
1629.2542 | 457.395 | 522.4786 | 469.8411 | 146.9155 | 192.7121 | 214.0844 | 179.6265
1630.2542 | 458.1567 | 521.0182 | 469.6611 | 147.0513 | 192.8831 | 214.2161 | 179.7611
1631.2542 | 459.7678 | 518.9784 | 468.2812 | 147.1758 | 193.0513 | 214.3393 | 179.9039
1632.2542 | 461.8041 | 519.6945 | 467.4387 | 147.3091 | 193.2209 | 214.4626 | 180.0592
1633.2542 | 462.7585 | 519.0241 | 466.1625 | 147.45 | 193.3788 | 214.5995 | 180.2044
1634.2542 | 466.8131 | 520.2923 | 468.4792 | 147.5912 | 193.5531 | 214.7295 | 180.3567
1635.2542 | 467.2715 | 525.9078 | 470.2265 | 147.7394 | 193.7233 | 214.8377 | 180.4985
1636.2542 | 465.8557 | 526.8271 | 469.2814 | 147.8665 | 193.8921 | 214.9798 | 180.6353
1637.2542 | 465.1293 | 527.7625 | 471.9866 | 148.0114 | 194.0694 | 215.1132 | 180.7698
1638.2542 | 467.9076 | 527.9392 | 472.5482 | 148.1434 | 194.2321 | 215.2293 | 180.9177
1639.2542 | 470.5781 | 528.5156 | 474.8303 | 148.2856 | 194.4157 | 215.3636 | 181.0306
1640.2542 | 471.9277 | 530.5216 | 476.1811 | 148.4268 | 194.5824 | 215.4925 | 181.1975
1641.2542 | 474.105 | 532.4844 | 478.0057 | 148.5509 | 194.7573 | 215.6228 | 181.3478
1642.2542 | 477.4616 | 531.9808 | 476.1857 | 148.6891 | 194.9303 | 215.7477 | 181.4915
1643.2542 | 479.9123 | 530.2377 | 474.6564 | 148.8249 | 195.0987 | 215.8818 | 181.6491
1644.2542 | 482.4312 | 530.7844 | 475.6461 | 148.9708 | 195.2637 | 216.0149 | 181.7838
1645.2542 | 485.1059 | 532.5014 | 476.0048 | 149.1031 | 195.4399 | 216.1413 | 181.9347
1646.2542 | 486.2957 | 530.3737 | 475.6192 | 149.2443 | 195.6082 | 216.2729 | 182.0799
1647.2542 | 486.1585 | 529.8684 | 474.4495 | 149.3616 | 195.7802 | 216.4166 | 182.2309
1648.2542 | 487.7291 | 530.6535 | 474.6959 | 149.5242 | 195.9531 | 216.5404 | 182.3823
1649.2542 | 491.168 | 531.2288 | 475.6377 | 149.6685 | 196.1239 | 216.665 | 182.5366
1650.2542 | 491.9619 | 532.2988 | 474.6724 | 149.8086 | 196.3049 | 216.7998 | 182.68
1651.2542 | 491.555 | 532.167 | 473.5919 | 149.9266 | 196.4839 | 216.9316 | 182.8306
1652.2542 | 491.2019 | 532.1848 | 472.6832 | 150.0752 | 196.6552 | 217.0557 | 182.9922
1653.2542 | 492.954 | 531.1287 | 471.3422 | 150.2075 | 196.8358 | 217.1675 | 183.1312
1654.2542 | 494.0107 | 531.3079 | 470.1977 | 150.3577 | 197.0076 | 217.3175 | 183.2914
1655.2542 | 494.0299 | 530.3813 | 469.0033 | 150.5018 | 197.1981 | 217.447 | 183.4454
1656.2542 | 494.6037 | 531.814 | 467.3345 | 150.638 | 197.3731 | 217.5624 | 183.5989
1657.2698 | 493.5349 | 532.4502 | 466.8553 | 150.7722 | 197.5586 | 217.7007 | 183.7687
1658.2542 | 490.6501 | 533.7453 | 465.931 | 150.9136 | 197.7172 | 217.8282 | 183.9356
1659.2542 | 489.6001 | 534.4831 | 467.3148 | 151.0419 | 197.8958 | 217.9602 | 184.0953
1660.2542 | 490.0183 | 533.2669 | 466.3798 | 151.1857 | 198.0533 | 218.1001 | 184.2622
1661.2542 | 488.8326 | 533.2067 | 465.2933 | 151.3367 | 198.2232 | 218.2167 | 184.4148
1662.2542 | 487.0847 | 533.5569 | 464.7198 | 151.4749 | 198.3922 | 218.3566 | 184.5862
1663.2542 | 488.0234 | 534.5664 | 464.5238 | 151.6059 | 198.5716 | 218.4783 | 184.7397
1664.2542 | 486.9203 | 531.9637 | 463.3891 | 151.7492 | 198.7411 | 218.6168 | 184.8959
1665.2542 | 486.4588 | 529.7551 | 461.8875 | 151.8762 | 198.9045 | 218.7436 | 185.0738
1666.2542 | 485.4481 | 530.1035 | 461.2679 | 152.0397 | 199.0741 | 218.8762 | 185.2692
1667.2542 | 486.4774 | 530.7567 | 460.725 | 152.1694 | 199.2349 | 218.9994 | 185.4332
1668.2542 | 487.3282 | 533.1389 | 462.4365 | 152.3203 | 199.4066 | 219.1324 | 185.6141
1669.2542 | 485.9091 | 534.5569 | 464.0278 | 152.462 | 199.5769 | 219.2522 | 185.7775
1670.2542 | 483.7173 | 532.8994 | 462.0013 | 152.5913 | 199.7531 | 219.3973 | 185.9531
1671.2542 | 484.508 | 530.2836 | 461.1153 | 152.7232 | 199.9104 | 219.5222 | 186.1122
1672.2542 | 483.1916 | 527.4731 | 458.553 | 152.8765 | 200.0932 | 219.6545 | 186.2656
1673.2542 | 483.3752 | 526.5872 | 458.0312 | 153.0244 | 200.2601 | 219.7826 | 186.425
1674.2542 | 482.6834 | 527.9701 | 460.9131 | 153.1613 | 200.4388 | 219.9212 | 186.5838
1675.2542 | 481.2592 | 529.1583 | 462.7329 | 153.3036 | 200.608 | 220.0506 | 186.7643
1676.2542 | 479.066 | 527.4838 | 460.9867 | 153.4348 | 200.7832 | 220.1854 | 186.9305
1677.2542 | 475.8061 | 526.569 | 459.6902 | 153.566 | 200.9539 | 220.3194 | 187.1026
1678.2542 | 474.1913 | 527.3518 | 461.4736 | 153.7064 | 201.1168 | 220.4444 | 187.2895
1679.2542 | 474.1053 | 528.608 | 458.7192 | 153.846 | 201.2906 | 220.5822 | 187.4458
1680.2542 | 473.8471 | 528.2624 | 457.1591 | 153.9835 | 201.4582 | 220.7136 | 187.6258
1681.2542 | 473.1687 | 530.4788 | 456.3999 | 154.1338 | 201.6317 | 220.8483 | 187.7824
1682.2542 | 471.4436 | 529.919 | 455.0122 | 154.2804 | 201.7986 | 220.9752 | 187.9791
1683.2542 | 470.6501 | 528.0717 | 451.751 | 154.4161 | 201.9685 | 221.1083 | 188.158
1684.2542 | 470.6322 | 527.8695 | 450.8002 | 154.5628 | 202.1336 | 221.2358 | 188.3461
1685.2542 | 468.8871 | 524.3592 | 448.7402 | 154.6808 | 202.297 | 221.3649 | 188.5259
1686.2542 | 471.1018 | 525.0608 | 448.3333 | 154.8447 | 202.4672 | 221.4967 | 188.6963
1687.2542 | 471.608 | 526.2431 | 448.6673 | 154.9829 | 202.6297 | 221.6158 | 188.8662
1688.2542 | 472.7708 | 525.8775 | 448.9879 | 155.1136 | 202.7989 | 221.7476 | 189.0292
1689.2542 | 472.5737 | 524.925 | 448.2392 | 155.2576 | 202.9729 | 221.8827 | 189.2072
1690.2542 | 470.2189 | 521.8997 | 446.311 | 155.4067 | 203.133 | 222.012 | 189.3841
1691.2542 | 468.5065 | 520.2032 | 446.2266 | 155.5438 | 203.301 | 222.1347 | 189.5752
1692.2542 | 469.3225 | 518.9848 | 446.0551 | 155.682 | 203.4691 | 222.2677 | 189.7593
1693.2542 | 468.2583 | 516.4104 | 444.6372 | 155.8287 | 203.627 | 222.4006 | 189.9329
1694.2542 | 470.0767 | 516.2217 | 445.08 | 155.9598 | 203.7948 | 222.5165 | 190.0895
1695.2542 | 471.181 | 515.4507 | 444.4825 | 156.1032 | 203.9536 | 222.6543 | 190.2585
1696.2542 | 470.1492 | 512.2452 | 441.2415 | 156.2438 | 204.1123 | 222.7848 | 190.4398
1697.2542 | 469.6028 | 508.4827 | 438.3714 | 156.3746 | 204.277 | 222.8969 | 190.5942
1698.2542 | 469.5014 | 505.6549 | 436.3361 | 156.5224 | 204.4359 | 223.0402 | 190.7693
1699.2542 | 469.3959 | 502.8132 | 435.405 | 156.6531 | 204.5964 | 223.1768 | 190.9343
1700.2542 | 467.2989 | 500.961 | 434.5127 | 156.8079 | 204.7503 | 223.3156 | 191.151
1701.2542 | 464.4259 | 498.2472 | 433.4557 | 156.9299 | 204.9059 | 223.4322 | 191.3178
1702.2542 | 465.1417 | 497.7244 | 434.405 | 157.0798 | 205.0609 | 223.5659 | 191.5016
1703.2542 | 467.3195 | 497.409 | 437.4312 | 157.2205 | 205.2183 | 223.6883 | 191.6591
1704.2542 | 467.822 | 497.2764 | 437.5304 | 157.3586 | 205.3674 | 223.8169 | 191.857
1705.2542 | 467.0837 | 495.5392 | 436.5419 | 157.5011 | 205.5201 | 223.9375 | 192.0202
1706.2542 | 469.5471 | 497.0514 | 436.7779 | 157.6282 | 205.682 | 224.0735 | 192.189
1707.2542 | 470.178 | 498.5165 | 438.966 | 157.7795 | 205.8314 | 224.2095 | 192.399
1708.2542 | 470.7513 | 499.669 | 440.261 | 157.9301 | 205.9761 | 224.3285 | 192.5461
1709.2542 | 469.7284 | 500.0368 | 440.5559 | 158.0775 | 206.1351 | 224.4613 | 192.7123
1710.2542 | 468.312 | 499.5079 | 438.0608 | 158.2097 | 206.2828 | 224.5767 | 192.8914
1711.2542 | 469.5774 | 498.2339 | 436.9006 | 158.3578 | 206.4399 | 224.729 | 193.0732
1712.2542 | 470.8965 | 497.6666 | 436.7241 | 158.4929 | 206.5973 | 224.8392 | 193.233
1713.2542 | 472.5452 | 496.9039 | 434.0159 | 158.6337 | 206.7457 | 224.9818 | 193.4147
1714.2542 | 473.7465 | 496.7152 | 434.3373 | 158.78 | 206.9154 | 225.12 | 193.5862
1715.2542 | 473.4878 | 495.5651 | 433.2134 | 158.919 | 207.077 | 225.2517 | 193.7757
1716.2542 | 472.0989 | 493.2731 | 431.0502 | 159.0686 | 207.2353 | 225.3807 | 193.9303
1717.2542 | 470.628 | 491.4873 | 428.9532 | 159.1998 | 207.3799 | 225.5062 | 194.125
1718.2542 | 469.9391 | 487.8677 | 426.0831 | 159.3436 | 207.5346 | 225.6334 | 194.2925
1719.2542 | 472.1387 | 485.4047 | 423.5584 | 159.479 | 207.6937 | 225.7623 | 194.4622
1720.2542 | 470.9883 | 483.7407 | 421.4057 | 159.6115 | 207.8484 | 225.8989 | 194.6491
1721.2542 | 469.1237 | 481.5345 | 419.4894 | 159.7627 | 207.9945 | 226.0226 | 194.8162
1722.2542 | 468.1159 | 478.9179 | 418.507 | 159.9059 | 208.1503 | 226.1913 | 195.0215
1723.2542 | 467.3689 | 478.3085 | 417.7304 | 160.0413 | 208.2891 | 226.2983 | 195.1653
1724.2542 | 466.9343 | 477.4219 | 417.4333 | 160.1659 | 208.4464 | 226.4276 | 195.3642
1725.2542 | 466.3871 | 476.0359 | 416.6413 | 160.3305 | 208.5875 | 226.5581 | 195.5437
1726.2542 | 465.649 | 476.434 | 415.8601 | 160.4819 | 208.7379 | 226.6847 | 195.7295
1727.2542 | 466.085 | 475.2499 | 415.4225 | 160.6137 | 208.8721 | 226.8105 | 195.9019
1728.2542 | 465.0091 | 474.1579 | 414.4245 | 160.7612 | 209.0205 | 226.9507 | 196.0789
1729.2542 | 466.2309 | 474.3515 | 413.2177 | 160.8984 | 209.1513 | 227.0823 | 196.251
1730.2542 | 470.0944 | 474.8195 | 412.7541 | 161.0501 | 209.3025 | 227.1998 | 196.4338
1731.2542 | 470.2358 | 474.3993 | 412.1641 | 161.1849 | 209.4354 | 227.3427 | 196.6017
1732.2542 | 470.4647 | 475.1275 | 411.6201 | 161.3192 | 209.5922 | 227.4688 | 196.7972
1733.2542 | 471.4004 | 476.5008 | 412.7308 | 161.4526 | 209.7322 | 227.5918 | 196.9778
1734.2542 | 474.964 | 475.369 | 412.3326 | 161.6153 | 209.8787 | 227.7185 | 197.1795
1735.2542 | 476.3542 | 476.7429 | 411.8114 | 161.7481 | 210.0103 | 227.8495 | 197.3535
1736.2542 | 474.2806 | 477.8746 | 412.3906 | 161.8976 | 210.1461 | 227.9935 | 197.5516
1737.2542 | 476.9177 | 478.1621 | 411.7793 | 162.037 | 210.2902 | 228.1208 | 197.7163
1738.2542 | 476.1273 | 480.4178 | 411.499 | 162.1847 | 210.4342 | 228.254 | 197.8957
1739.2542 | 475.0123 | 481.472 | 411.2416 | 162.3314 | 210.5789 | 228.385 | 198.0817
1740.2542 | 472.8001 | 479.7045 | 411.2738 | 162.4586 | 210.7231 | 228.5205 | 198.2588
1741.2542 | 471.4524 | 479.4641 | 410.5536 | 162.6019 | 210.8657 | 228.6559 | 198.4483
1742.2542 | 468.6916 | 476.7293 | 409.8623 | 162.7382 | 211.0126 | 228.7971 | 198.625
1743.2542 | 466.301 | 477.5253 | 410.477 | 162.8495 | 211.1554 | 228.9294 | 198.7975
1744.2542 | 464.7914 | 479.2116 | 411.3694 | 163.0224 | 211.2827 | 229.0705 | 199.016
1745.2542 | 462.6861 | 478.1485 | 410.3814 | 163.1643 | 211.4299 | 229.1986 | 199.1825
1746.2542 | 459.6708 | 476.8144 | 409.0219 | 163.3025 | 211.5745 | 229.3338 | 199.3872
1747.2542 | 458.4059 | 476.9675 | 408.9435 | 163.4606 | 211.7235 | 229.4662 | 199.5613
1748.2542 | 457.8216 | 476.9938 | 409.6965 | 163.6025 | 211.8615 | 229.6036 | 199.7452
1749.2542 | 457.1545 | 474.9455 | 408.0173 | 163.7393 | 211.995 | 229.7471 | 199.9571
1750.2542 | 455.5137 | 471.8931 | 406.327 | 163.8875 | 212.1349 | 229.8873 | 200.1789
1751.2542 | 456.2346 | 469.4916 | 405.5538 | 164.0252 | 212.2752 | 230.0241 | 200.3679
1752.2542 | 456.4581 | 469.4983 | 406.3843 | 164.1753 | 212.4184 | 230.1602 | 200.5519
1753.2542 | 456.3207 | 469.005 | 406.8631 | 164.3236 | 212.5619 | 230.2896 | 200.7401
1754.2542 | 456.3236 | 468.7254 | 406.1823 | 164.4516 | 212.7173 | 230.4367 | 200.9311
1755.2542 | 455.3038 | 467.1133 | 404.4467 | 164.6149 | 212.8512 | 230.5825 | 201.1526
1756.2542 | 453.6986 | 464.6215 | 402.4641 | 164.746 | 212.9963 | 230.7139 | 201.3654
1757.2542 | 457.2057 | 463.7756 | 402.6572 | 164.9157 | 213.1353 | 230.852 | 201.5419
1758.2542 | 455.9699 | 461.3577 | 401.6071 | 165.0563 | 213.2889 | 230.9935 | 201.7526
1759.2542 | 457.6009 | 459.9718 | 400.7467 | 165.1866 | 213.4279 | 231.1261 | 201.9479
1760.2542 | 457.8561 | 459.0117 | 400.1892 | 165.3263 | 213.5641 | 231.2662 | 202.1633
1761.2542 | 457.7537 | 456.8297 | 398.7901 | 165.4785 | 213.7077 | 231.406 | 202.3403
1762.2542 | 457.6434 | 454.4571 | 397.8464 | 165.6184 | 213.8548 | 231.5409 | 202.5405
1763.2542 | 458.4063 | 454.9411 | 398.0422 | 165.77 | 214.0015 | 231.6741 | 202.7442
1764.2542 | 457.7626 | 455.6972 | 397.9282 | 165.9097 | 214.1484 | 231.8066 | 202.9403
1765.2542 | 458.2211 | 456.0024 | 398.1259 | 166.0621 | 214.2895 | 231.9524 | 203.1715
1766.2542 | 459.3255 | 456.9905 | 398.063 | 166.1786 | 214.4154 | 232.0905 | 203.3633
1767.2542 | 459.1497 | 456.7786 | 397.7851 | 166.3295 | 214.5589 | 232.2319 | 203.5581
1768.2542 | 458.7396 | 455.2711 | 398.2665 | 166.4903 | 214.696 | 232.36 | 203.7548
1769.2542 | 459.2289 | 456.0906 | 398.7578 | 166.6329 | 214.8408 | 232.5001 | 203.9371
1770.2542 | 458.249 | 456.077 | 399.3574 | 166.789 | 214.9769 | 232.6448 | 204.1505
1771.2542 | 460.5927 | 456.2672 | 399.9859 | 166.9169 | 215.1134 | 232.7688 | 204.3304
1772.2542 | 461.8259 | 456.4146 | 399.438 | 167.0643 | 215.2604 | 232.9089 | 204.5001
1773.2542 | 464.11 | 459.4259 | 399.9143 | 167.2203 | 215.399 | 233.0508 | 204.6984
1774.2542 | 463.9253 | 460.7761 | 399.9581 | 167.3465 | 215.5413 | 233.2068 | 204.8944
1775.2542 | 463.2781 | 460.2538 | 398.9094 | 167.5132 | 215.6897 | 233.3429 | 205.0824
1776.2542 | 464.7919 | 460.8038 | 398.4248 | 167.6664 | 215.8317 | 233.4782 | 205.2699
1777.2542 | 464.0873 | 460.265 | 397.7736 | 167.818 | 215.9782 | 233.613 | 205.4616
1778.2542 | 463.7308 | 460.5006 | 397.4027 | 167.9586 | 216.1169 | 233.7526 | 205.6468
1779.2542 | 463.9428 | 459.6371 | 397.8389 | 168.115 | 216.2651 | 233.8988 | 205.8446
1780.2542 | 462.0757 | 458.5588 | 397.7384 | 168.2477 | 216.4016 | 234.0226 | 206.0165
1781.2542 | 462.2567 | 459.2568 | 397.6905 | 168.3855 | 216.5493 | 234.1641 | 206.2019
1782.2542 | 461.7165 | 457.6143 | 397.483 | 168.5422 | 216.7087 | 234.3133 | 206.3798
1783.2542 | 461.6046 | 457.2823 | 397.1983 | 168.6851 | 216.8529 | 234.4605 | 206.5695
1784.2542 | 460.6797 | 457.9248 | 397.5254 | 168.8282 | 216.995 | 234.5854 | 206.7689
1785.2542 | 461.6301 | 458.1594 | 398.5404 | 168.988 | 217.1315 | 234.7301 | 206.9633
1786.2542 | 460.6818 | 458.2115 | 399.0715 | 169.1243 | 217.2765 | 234.872 | 207.1424
1787.2542 | 462.1955 | 459.518 | 400.6089 | 169.2588 | 217.4128 | 235.0168 | 207.3319
1788.2542 | 461.4201 | 458.3829 | 401.3186 | 169.4133 | 217.5578 | 235.1611 | 207.5113
1789.2542 | 460.799 | 459.2192 | 401.5563 | 169.5575 | 217.7005 | 235.3127 | 207.6924
1790.2542 | 459.8939 | 459.8079 | 401.6142 | 169.7107 | 217.8481 | 235.4496 | 207.8632
1791.2542 | 459.9253 | 460.913 | 400.976 | 169.8585 | 217.9868 | 235.5956 | 208.0415
1792.2542 | 457.7683 | 462.4138 | 399.8193 | 170.0094 | 218.1322 | 235.7504 | 208.2063
1793.2542 | 457.1492 | 462.0424 | 401.0983 | 170.1648 | 218.2784 | 235.9029 | 208.3933
1794.2542 | 457.4389 | 462.5505 | 401.1104 | 170.2924 | 218.4298 | 236.0547 | 208.5596
1795.2542 | 455.7317 | 461.4028 | 400.089 | 170.4333 | 218.5612 | 236.1906 | 208.7379
1796.2542 | 454.9258 | 460.086 | 398.4699 | 170.5894 | 218.7104 | 236.3363 | 208.9303
1797.2542 | 456.5707 | 458.1509 | 397.5921 | 170.7336 | 218.8634 | 236.4841 | 209.088
1798.2542 | 456.8016 | 457.9216 | 398.7626 | 170.8906 | 219.0016 | 236.6283 | 209.2631
1799.2542 | 457.2683 | 460.1394 | 401.4411 | 171.0289 | 219.1481 | 236.7651 | 209.455
1800.2542 | 457.67 | 461.1206 | 402.1987 | 171.1864 | 219.2873 | 236.9035 | 209.6197
1801.2542 | 456.9063 | 462.021 | 403.0456 | 171.3305 | 219.438 | 237.0591 | 209.8036
1802.2542 | 457.6319 | 462.5262 | 404.4245 | 171.4806 | 219.5844 | 237.2021 | 209.9898
1803.2542 | 458.0375 | 463.6963 | 406.6804 | 171.6041 | 219.7279 | 237.3406 | 210.1447
1804.2542 | 459.6259 | 465.7343 | 408.6211 | 171.7626 | 219.8691 | 237.4919 | 210.3331
1805.2542 | 461.5228 | 466.3778 | 409.401 | 171.9062 | 220.0191 | 237.6324 | 210.5103
1806.2542 | 459.1234 | 466.5826 | 411.1589 | 172.0566 | 220.1566 | 237.7764 | 210.6773
1807.2542 | 457.6545 | 467.9513 | 412.7549 | 172.1896 | 220.3099 | 237.923 | 210.8448
1808.2542 | 458.0058 | 469.2467 | 414.6146 | 172.353 | 220.4608 | 238.0645 | 211.0113
1809.2542 | 459.2206 | 468.4251 | 414.6994 | 172.5001 | 220.6255 | 238.2123 | 211.1676
1810.2542 | 459.8403 | 469.6009 | 417.7745 | 172.6363 | 220.7749 | 238.3566 | 211.3313
1811.2542 | 460.0471 | 472.4855 | 419.1528 | 172.8016 | 220.9214 | 238.5019 | 211.5299
1812.2542 | 459.1062 | 472.3552 | 419.4109 | 172.9282 | 221.0821 | 238.6451 | 211.6878
1813.2542 | 459.3041 | 474.6722 | 420.7166 | 173.0755 | 221.2413 | 238.7881 | 211.8584
1814.2542 | 457.5106 | 474.6524 | 421.1181 | 173.2274 | 221.397 | 238.9432 | 212.0277
1815.2542 | 458.2077 | 475.1078 | 421.7121 | 173.3854 | 221.5474 | 239.0927 | 212.2099
1816.2542 | 458.5267 | 476.5908 | 423.4548 | 173.5191 | 221.7061 | 239.2366 | 212.3602
1817.2542 | 460.0462 | 476.2097 | 425.0707 | 173.6864 | 221.8711 | 239.3887 | 212.5306
1818.2542 | 461.0692 | 476.9961 | 427.0539 | 173.8348 | 222.0304 | 239.5379 | 212.7033
1819.2542 | 461.4527 | 478.0075 | 426.2029 | 173.98 | 222.192 | 239.7014 | 212.886
1820.2542 | 461.0446 | 477.023 | 424.6644 | 174.1127 | 222.3668 | 239.8365 | 213.0562
1821.2542 | 463.7429 | 475.2014 | 422.4144 | 174.274 | 222.5282 | 239.9868 | 213.2249
1822.2542 | 464.7555 | 473.0141 | 420.1096 | 174.4286 | 222.6948 | 240.1494 | 213.3967
1823.2542 | 468.3148 | 474.5853 | 421.0506 | 174.5529 | 222.8713 | 240.3006 | 213.556
1824.2542 | 470.4151 | 476.337 | 421.4118 | 174.6689 | 223.0344 | 240.4562 | 213.7264
1825.2542 | 470.2954 | 475.6308 | 421.2255 | 174.863 | 223.213 | 240.5968 | 213.8924
1826.2542 | 471.067 | 475.7259 | 421.8195 | 175.0163 | 223.3727 | 240.7471 | 214.0834
1827.2542 | 470.9153 | 475.484 | 421.9631 | 175.1753 | 223.542 | 240.8994 | 214.2413
1828.2542 | 471.1285 | 476.6519 | 424.3887 | 175.3081 | 223.7139 | 241.0456 | 214.4212
1829.2542 | 471.2042 | 477.2851 | 425.8533 | 175.4541 | 223.8885 | 241.197 | 214.581
1830.2542 | 470.6095 | 478.1544 | 427.2113 | 175.6086 | 224.0539 | 241.3515 | 214.7561
1831.2542 | 468.7569 | 477.3117 | 427.1888 | 175.759 | 224.2175 | 241.5087 | 214.8987
1832.2542 | 466.8816 | 477.0053 | 426.6402 | 175.8996 | 224.3882 | 241.6634 | 215.0656
1833.2542 | 464.5029 | 476.3526 | 425.8137 | 176.0622 | 224.5634 | 241.8249 | 215.2365
1834.2542 | 462.77 | 477.8749 | 426.0697 | 176.2048 | 224.7359 | 241.9773 | 215.3902
1835.2542 | 461.454 | 478.3985 | 425.0597 | 176.3391 | 224.9047 | 242.1286 | 215.557
1836.2542 | 461.0445 | 479.0109 | 425.5131 | 176.4921 | 225.076 | 242.2746 | 215.7104
1837.2542 | 459.9761 | 480.0491 | 425.2876 | 176.6393 | 225.2497 | 242.437 | 215.8784
1838.2542 | 457.545 | 479.2833 | 424.4317 | 176.8051 | 225.4114 | 242.5951 | 216.061
1839.2542 | 456.8784 | 480.7772 | 424.7099 | 176.9506 | 225.5913 | 242.7474 | 216.2143
1840.2542 | 455.8875 | 479.8977 | 423.707 | 177.1101 | 225.7554 | 242.9008 | 216.3843
1841.2542 | 455.2178 | 478.2465 | 422.7021 | 177.2521 | 225.9344 | 243.0527 | 216.5345
1842.2542 | 454.6794 | 477.6647 | 421.5881 | 177.4281 | 226.1075 | 243.2125 | 216.7357
1843.2542 | 457.1179 | 478.5186 | 422.9295 | 177.567 | 226.2782 | 243.3782 | 216.8887
1844.2542 | 458.7914 | 479.2702 | 425.8912 | 177.7097 | 226.4643 | 243.5262 | 217.0269
1845.2542 | 458.3764 | 478.4029 | 426.1599 | 177.865 | 226.6512 | 243.6842 | 217.1941
1846.2542 | 457.836 | 477.5312 | 426.2402 | 178.0169 | 226.8219 | 243.8365 | 217.3553
1847.2542 | 457.1799 | 476.5092 | 426.0168 | 178.137 | 226.9899 | 243.9923 | 217.5158
1848.2542 | 458.176 | 477.7486 | 427.1221 | 178.3015 | 227.1632 | 244.1566 | 217.7007
1849.2542 | 457.9747 | 478.3782 | 426.8557 | 178.4697 | 227.3278 | 244.3009 | 217.8662
1850.2542 | 458.7829 | 477.801 | 426.4638 | 178.6165 | 227.5041 | 244.4606 | 218.0209
1851.2542 | 458.8789 | 477.1785 | 426.0403 | 178.7674 | 227.6882 | 244.6123 | 218.1575
1852.2542 | 458.3158 | 477.6023 | 426.1946 | 178.92 | 227.8614 | 244.7626 | 218.3433
1853.2542 | 458.4728 | 476.9365 | 425.3889 | 179.0745 | 228.0252 | 244.929 | 218.5076
1854.2542 | 459.1954 | 475.8484 | 423.2262 | 179.2196 | 228.1983 | 245.0872 | 218.6736
1855.2542 | 458.7824 | 475.542 | 422.1318 | 179.3777 | 228.3914 | 245.2415 | 218.8378
1856.2542 | 458.596 | 475.5015 | 422.3612 | 179.5248 | 228.5601 | 245.3925 | 218.9901
1857.2542 | 458.2666 | 476.5207 | 421.0463 | 179.6798 | 228.7278 | 245.5703 | 219.1688
1858.2542 | 456.8528 | 475.1387 | 420.4417 | 179.828 | 228.8995 | 245.717 | 219.337
1859.2542 | 457.8192 | 476.2365 | 420.7645 | 179.9702 | 229.0782 | 245.8634 | 219.4832
1860.2542 | 456.7162 | 476.6285 | 422.1387 | 180.1312 | 229.2493 | 246.0273 | 219.6403
1861.2542 | 456.8538 | 477.734 | 422.5626 | 180.2783 | 229.415 | 246.1869 | 219.8179
1862.2542 | 457.7815 | 479.0855 | 426.1885 | 180.4363 | 229.5871 | 246.3371 | 219.987
1863.2542 | 458.2957 | 479.3319 | 429.5174 | 180.578 | 229.7583 | 246.4929 | 220.1542
1864.2542 | 457.9141 | 479.6638 | 430.5274 | 180.735 | 229.9259 | 246.648 | 220.3196
1865.2542 | 456.1144 | 479.8178 | 430.8607 | 180.8901 | 230.0946 | 246.8091 | 220.4777
1866.2542 | 454.4655 | 478.0192 | 430.0697 | 181.0485 | 230.2801 | 246.9654 | 220.6283
1867.2542 | 452.6449 | 476.5999 | 429.1691 | 181.1967 | 230.4483 | 247.1233 | 220.7819
1868.2542 | 451.7858 | 475.9473 | 428.6738 | 181.3427 | 230.6221 | 247.2838 | 220.941
1869.2542 | 451.7997 | 476.4041 | 427.9487 | 181.5078 | 230.7954 | 247.4472 | 221.104
1870.2542 | 453.7859 | 475.9931 | 425.6917 | 181.6473 | 230.9758 | 247.5986 | 221.2574
1871.2542 | 453.4992 | 476.0788 | 424.4146 | 181.8038 | 231.1392 | 247.7563 | 221.4372
1872.2542 | 453.0216 | 475.9658 | 422.743 | 181.9502 | 231.3247 | 247.9113 | 221.5863
1873.2542 | 454.3167 | 475.4796 | 421.6117 | 182.1122 | 231.4909 | 248.0617 | 221.7454
1874.2542 | 454.3044 | 476.6984 | 420.4898 | 182.263 | 231.6808 | 248.2169 | 221.8929
1875.2542 | 453.0675 | 475.2742 | 418.4415 | 182.4136 | 231.8476 | 248.3836 | 222.0737
1876.2542 | 453.3185 | 473.6269 | 417.3511 | 182.5614 | 232.0209 | 248.5383 | 222.2253
1877.2542 | 453.0393 | 472.5275 | 416.1872 | 182.7084 | 232.1999 | 248.704 | 222.3662
1878.2542 | 452.8895 | 472.5613 | 415.0829 | 182.8633 | 232.376 | 248.8643 | 222.5408
1879.2542 | 455.1093 | 473.3644 | 415.2947 | 183.0205 | 232.5513 | 249.0235 | 222.6936
1880.2542 | 454.7248 | 472.1268 | 415.0255 | 183.1753 | 232.7288 | 249.1712 | 222.8451
1881.2542 | 454.8122 | 471.4613 | 413.9139 | 183.3278 | 232.8926 | 249.3326 | 223.0284
1882.2542 | 454.7853 | 470.0625 | 413.3699 | 183.4805 | 233.0649 | 249.4877 | 223.1937
1883.2542 | 454.0718 | 469.5043 | 413.0755 | 183.6293 | 233.2306 | 249.6398 | 223.3265
1884.2542 | 453.8141 | 468.1023 | 411.9107 | 183.7914 | 233.39 | 249.7965 | 223.5037
1885.2542 | 454.2295 | 468.3002 | 411.8481 | 183.9497 | 233.5626 | 249.954 | 223.6932
1886.2542 | 454.299 | 467.8622 | 410.4273 | 184.0796 | 233.7195 | 250.1208 | 223.8478
1887.2542 | 454.7057 | 466.3894 | 409.3799 | 184.2493 | 233.8946 | 250.2553 | 224.0112
1888.2542 | 455.7484 | 464.8367 | 408.0725 | 184.4066 | 234.0489 | 250.4316 | 224.1664
1889.2542 | 455.8843 | 463.1529 | 407.1163 | 184.555 | 234.2161 | 250.5698 | 224.3185
1890.2542 | 455.8397 | 463.0313 | 408.1599 | 184.7106 | 234.3824 | 250.7263 | 224.4873
1891.2542 | 455.3259 | 462.3913 | 408.1484 | 184.8731 | 234.5385 | 250.8813 | 224.6496
1892.2542 | 454.0778 | 461.8142 | 407.6389 | 185.0193 | 234.6999 | 251.0154 | 224.8246
1893.2542 | 453.7036 | 462.7564 | 406.5505 | 185.1654 | 234.8552 | 251.1757 | 224.9901
1894.2542 | 452.6434 | 467.4909 | 405.7464 | 185.3123 | 235.0188 | 251.3288 | 225.138
1895.2542 | 452.1866 | 468.3275 | 406.09 | 185.4622 | 235.1746 | 251.4716 | 225.2826
1896.2542 | 451.2194 | 467.2054 | 405.2404 | 185.6348 | 235.3352 | 251.6191 | 225.4473
1897.2542 | 452.023 | 465.6156 | 404.7711 | 185.7984 | 235.4857 | 251.7692 | 225.6007
1898.2542 | 452.6455 | 463.8785 | 404.0037 | 185.9622 | 235.6447 | 251.9188 | 225.777
1899.2542 | 452.9718 | 462.9399 | 403.0395 | 186.0918 | 235.7949 | 252.0606 | 225.9471
1900.2542 | 453.3262 | 460.8614 | 402.6305 | 186.2417 | 235.9446 | 252.2059 | 226.1307
1901.2542 | 453.9344 | 460.8214 | 403.9175 | 186.4023 | 236.1008 | 252.3392 | 226.31
1902.2542 | 453.6429 | 460.036 | 403.3231 | 186.5352 | 236.2667 | 252.4857 | 226.4771
1903.2542 | 452.9067 | 459.1432 | 403.1897 | 186.6602 | 236.4015 | 252.6289 | 226.6542
1904.2542 | 454.6426 | 459.0104 | 404.8717 | 186.8046 | 236.5535 | 252.7549 | 226.8238
1905.2542 | 456.1713 | 460.1594 | 407.7842 | 186.9848 | 236.697 | 252.899 | 226.999
1906.2542 | 456.926 | 461.1994 | 409.7899 | 187.1178 | 236.8447 | 253.0407 | 227.1695
1907.2542 | 456.6587 | 462.002 | 410.4385 | 187.3082 | 236.9979 | 253.1848 | 227.3222
1908.2542 | 456.6146 | 464.8655 | 412.4236 | 187.4384 | 237.1457 | 253.3304 | 227.4907
1909.2542 | 458.0452 | 468.8825 | 416.276 | 187.5864 | 237.2921 | 253.4648 | 227.6567
1910.2542 | 458.6299 | 469.55 | 417.6097 | 187.776 | 237.447 | 253.5905 | 227.8187
1911.2542 | 459.3526 | 470.5596 | 419.1654 | 187.928 | 237.593 | 253.7291 | 227.9624
1912.2542 | 459.3641 | 471.3506 | 421.9993 | 188.0705 | 237.7369 | 253.863 | 228.1271
1913.2542 | 460.7363 | 473.7344 | 423.2257 | 188.2029 | 237.8864 | 253.9964 | 228.2814
1914.2542 | 461.8645 | 474.212 | 423.6815 | 188.3797 | 238.0476 | 254.1275 | 228.4186
1915.2542 | 462.1531 | 475.8532 | 424.3807 | 188.5152 | 238.2037 | 254.2773 | 228.5778
1916.2542 | 463.5894 | 478.7425 | 424.2677 | 188.6557 | 238.3521 | 254.4144 | 228.7368
1917.2542 | 462.4327 | 479.1858 | 422.7975 | 188.8262 | 238.5144 | 254.5617 | 228.9215
1918.2542 | 460.869 | 479.5479 | 423.5494 | 188.9751 | 238.6759 | 254.7056 | 229.083
1919.2542 | 460.1525 | 481.6784 | 423.7724 | 189.1248 | 238.8281 | 254.8516 | 229.2537
1920.2542 | 460.9822 | 483.301 | 426.4829 | 189.2513 | 238.9875 | 254.9922 | 229.416
1921.2542 | 461.1956 | 483.7973 | 426.7582 | 189.4052 | 239.1535 | 255.1485 | 229.5821
1922.2542 | 461.7154 | 484.0165 | 428.4919 | 189.576 | 239.3094 | 255.2888 | 229.7766
1923.2542 | 463.4347 | 485.1718 | 431.4504 | 189.7193 | 239.4642 | 255.4427 | 229.9391
1924.2542 | 463.4358 | 485.4747 | 433.2557 | 189.8613 | 239.6313 | 255.5939 | 230.1065
1925.2542 | 463.2698 | 485.1363 | 433.8601 | 190.0171 | 239.7933 | 255.7534 | 230.2699
1926.2542 | 461.8611 | 483.4627 | 433.5717 | 190.1488 | 239.9497 | 255.9049 | 230.4628
1927.2542 | 460.4774 | 481.9119 | 433.4107 | 190.311 | 240.1078 | 256.0752 | 230.6595
1928.2542 | 459.9522 | 481.5108 | 433.1116 | 190.4631 | 240.2672 | 256.2103 | 230.8235
1929.2542 | 459.3282 | 480.6668 | 431.5996 | 190.6102 | 240.4385 | 256.3722 | 230.9803
1930.2542 | 457.7802 | 479.7519 | 430.2538 | 190.7646 | 240.5969 | 256.5169 | 231.1463
1931.2542 | 455.7387 | 478.644 | 429.3791 | 190.915 | 240.756 | 256.677 | 231.3038
1932.2542 | 454.7158 | 479.2512 | 429.262 | 191.0525 | 240.9243 | 256.8265 | 231.4698
1933.2542 | 455.4761 | 480.9275 | 430.4955 | 191.1905 | 241.0832 | 256.9765 | 231.6257
1934.2542 | 455.6124 | 480.8521 | 431.4236 | 191.3439 | 241.2441 | 257.1387 | 231.7871
1935.2542 | 456.0924 | 481.8192 | 433.4319 | 191.5057 | 241.4 | 257.2931 | 231.9713
1936.2542 | 457.4394 | 482.0141 | 435.137 | 191.6497 | 241.5635 | 257.436 | 232.1379
1937.2542 | 456.9641 | 481.8456 | 436.3182 | 191.7992 | 241.7332 | 257.5833 | 232.3498
1938.2542 | 457.2238 | 482.9796 | 438.5948 | 191.942 | 241.8971 | 257.7371 | 232.5182
1939.2542 | 457.1102 | 483.1638 | 438.9469 | 192.0788 | 242.0683 | 257.8968 | 232.6941
1940.2542 | 456.8112 | 483.156 | 439.6287 | 192.2202 | 242.2314 | 258.0432 | 232.8607
1941.2542 | 456.7792 | 483.7334 | 442.3604 | 192.3618 | 242.3871 | 258.2076 | 233.0366
1942.2542 | 456.6796 | 484.4069 | 443.1366 | 192.5077 | 242.5533 | 258.3431 | 233.2258
1943.2542 | 457.4638 | 483.9217 | 441.4443 | 192.6452 | 242.708 | 258.5049 | 233.4068
1944.2542 | 458.6753 | 485.5998 | 441.9683 | 192.7949 | 242.8822 | 258.6554 | 233.5856
1945.2542 | 460.4375 | 487.141 | 441.7519 | 192.9337 | 243.0552 | 258.8005 | 233.7743
1946.2542 | 458.8321 | 484.9169 | 439.2775 | 193.0869 | 243.2242 | 258.9416 | 233.9526
1947.2542 | 458.5474 | 484.6227 | 437.5403 | 193.2317 | 243.3868 | 259.0951 | 234.1597
1948.2542 | 457.3502 | 483.4671 | 436.5972 | 193.3703 | 243.5452 | 259.259 | 234.3521
1949.2542 | 457.5098 | 483.9212 | 436.9316 | 193.5188 | 243.7088 | 259.4175 | 234.5442
1950.2542 | 456.999 | 483.2779 | 436.0553 | 193.6806 | 243.8699 | 259.5669 | 234.7535
1951.2542 | 456.6525 | 483.4554 | 436.2677 | 193.8204 | 244.0251 | 259.7217 | 234.9751
1952.2542 | 456.7957 | 483.3717 | 435.256 | 193.9604 | 244.1893 | 259.8798 | 235.1722
1953.2542 | 455.3607 | 481.4336 | 432.9259 | 194.1125 | 244.3407 | 260.0283 | 235.383
1954.2542 | 453.9405 | 480.5664 | 430.7619 | 194.2396 | 244.5098 | 260.1934 | 235.6006
1955.2542 | 454.7459 | 481.1062 | 429.2367 | 194.4005 | 244.6649 | 260.338 | 235.7893
1956.2542 | 454.2415 | 480.3896 | 427.7229 | 194.5257 | 244.8378 | 260.4835 | 235.9554
1957.2542 | 454.2636 | 480.0301 | 427.5192 | 194.6847 | 245.0004 | 260.6209 | 236.1818
1958.2542 | 454.1644 | 481.3666 | 427.2945 | 194.8503 | 245.167 | 260.7652 | 236.3807
1959.2542 | 454.7378 | 481.8688 | 426.3073 | 194.9704 | 245.3384 | 260.8957 | 236.6002
1960.2542 | 454.8632 | 482.679 | 424.7972 | 195.1171 | 245.5091 | 261.0323 | 236.8141
1961.2542 | 456.6354 | 482.4495 | 423.8999 | 195.2637 | 245.6537 | 261.1632 | 237.0016
1962.2542 | 456.8554 | 480.7765 | 422.376 | 195.415 | 245.7953 | 261.2991 | 237.1727
1963.2542 | 456.6329 | 481.445 | 422.8666 | 195.5554 | 245.948 | 261.4059 | 237.3731
1964.2542 | 456.9213 | 481.4709 | 422.6235 | 195.6962 | 246.0948 | 261.5233 | 237.5743
1965.2542 | 457.8149 | 479.4457 | 421.4423 | 195.8449 | 246.2258 | 261.6744 | 237.7609
1966.2542 | 458.6595 | 478.1622 | 421.4145 | 195.986 | 246.354 | 261.8264 | 237.9673
1967.2542 | 458.7391 | 477.6505 | 420.9547 | 196.1379 | 246.4908 | 261.9662 | 238.1733
1968.2542 | 459.3575 | 478.3531 | 422.4055 | 196.2803 | 246.6212 | 262.0991 | 238.3628
1969.2542 | 459.2075 | 478.1046 | 422.2932 | 196.4258 | 246.7636 | 262.2499 | 238.5673
1970.2542 | 458.5862 | 477.5802 | 421.3205 | 196.5626 | 246.9059 | 262.3834 | 238.7885
1971.2542 | 458.8938 | 477.5333 | 421.0116 | 196.7262 | 247.0467 | 262.5381 | 238.9907
1972.2542 | 458.4042 | 476.9238 | 420.9111 | 196.8575 | 247.2031 | 262.668 | 239.1921
1973.2542 | 458.0548 | 475.9449 | 420.0515 | 197.0173 | 247.3457 | 262.7974 | 239.3936
1974.2542 | 457.8824 | 474.9998 | 419.9275 | 197.1736 | 247.4924 | 262.9414 | 239.6055
1975.2542 | 458.4719 | 475.2643 | 420.0272 | 197.316 | 247.6411 | 263.0636 | 239.794
1976.2542 | 458.6532 | 474.2628 | 418.738 | 197.4688 | 247.7865 | 263.1888 | 239.9782
1977.2542 | 458.554 | 473.0351 | 418.8224 | 197.5851 | 247.9407 | 263.3074 | 240.1564
1978.2542 | 457.9372 | 473.0682 | 418.9629 | 197.7676 | 248.0873 | 263.4269 | 240.3814
1979.2542 | 458.3145 | 472.1831 | 419.1543 | 197.9003 | 248.2376 | 263.5534 | 240.5872
1980.2542 | 458.4579 | 471.2041 | 418.6477 | 198.0702 | 248.3807 | 263.6623 | 240.8016
1981.2542 | 458.4013 | 470.9984 | 418.3604 | 198.2023 | 248.5363 | 263.7626 | 240.985
1982.2542 | 458.3642 | 470.9061 | 417.1782 | 198.3448 | 248.6772 | 263.8859 | 241.1626
1983.2542 | 457.8591 | 469.534 | 415.8661 | 198.5061 | 248.8299 | 263.9939 | 241.3277
1984.2542 | 458.3309 | 468.867 | 415.5501 | 198.6408 | 248.9736 | 264.0937 | 241.521
1985.2542 | 458.5788 | 470.841 | 417.6284 | 198.8019 | 249.1242 | 264.1892 | 241.7231
1986.2542 | 458.7793 | 471.6803 | 417.6152 | 198.9501 | 249.2635 | 264.2834 | 241.8998
1987.2542 | 459.8911 | 472.5485 | 416.8539 | 199.0994 | 249.4136 | 264.3416 | 242.0411
1988.2542 | 460.2867 | 471.9465 | 417.7859 | 199.2315 | 249.5587 | 264.3959 | 242.1804
1989.2698 | 460.6238 | 472.697 | 418.2136 | 199.3954 | 249.7059 | 264.4824 | 242.3271
1990.2542 | 461.86 | 473.0946 | 418.7851 | 199.5473 | 249.8443 | 264.5606 | 242.4833
1991.2542 | 462.6931 | 473.2849 | 417.2824 | 199.695 | 249.9896 | 264.6506 | 242.6384
1992.2542 | 463.1969 | 472.9551 | 417.6718 | 199.8541 | 250.1364 | 264.7367 | 242.8004
1993.2542 | 462.8362 | 472.7956 | 418.2116 | 200.0111 | 250.2902 | 264.821 | 242.9361
1994.2542 | 463.3416 | 473.403 | 418.3926 | 200.156 | 250.4391 | 264.9025 | 243.0671
1995.2542 | 463.5094 | 476.0562 | 419.0385 | 200.3147 | 250.5717 | 265.0064 | 243.2138
1996.2542 | 464.6899 | 475.1938 | 418.4668 | 200.4482 | 250.7214 | 265.1525 | 243.3753
1997.2542 | 464.56 | 473.2608 | 417.7424 | 200.6039 | 250.8607 | 265.2988 | 243.5369
1998.2542 | 462.6387 | 471.3739 | 416.2728 | 200.7457 | 251.0062 | 265.4496 | 243.6754
1999.2542 | 462.8615 | 472.9008 | 416.0264 | 200.9032 | 251.1417 | 265.6116 | 243.8358
2000.2542 | 462.9504 | 473.139 | 415.7185 | 201.0599 | 251.284 | 265.7758 | 243.9902
2001.2542 | 463.3962 | 474.0849 | 415.0895 | 201.2087 | 251.4203 | 265.9247 | 244.1316
2002.2542 | 463.2973 | 473.6335 | 414.172 | 201.3553 | 251.5544 | 266.0805 | 244.3
2003.2542 | 464.7701 | 474.8745 | 414.7886 | 201.5017 | 251.6814 | 266.2217 | 244.4755
2004.2542 | 464.5927 | 473.7871 | 414.4247 | 201.6491 | 251.8095 | 266.3527 | 244.6397
2005.2542 | 463.5889 | 473.3364 | 414.1681 | 201.8111 | 251.9396 | 266.5001 | 244.7958
2006.2542 | 463.4852 | 473.5891 | 414.2106 | 201.969 | 252.071 | 266.6178 | 244.9567
2007.2542 | 463.7091 | 476.2313 | 414.6436 | 202.1133 | 252.2091 | 266.7262 | 245.1106
2008.2542 | 465.1632 | 477.2182 | 415.9764 | 202.2668 | 252.3385 | 266.8848 | 245.2522
2009.2542 | 464.6066 | 475.6859 | 415.794 | 202.4212 | 252.4651 | 267.0279 | 245.4075
2010.2542 | 465.9711 | 475.5699 | 415.8987 | 202.5716 | 252.6011 | 267.1379 | 245.5685
2011.2542 | 467.0376 | 475.3562 | 414.7995 | 202.7318 | 252.7373 | 267.2634 | 245.7103
2012.2542 | 466.9365 | 474.7944 | 414.3196 | 202.8803 | 252.8801 | 267.378 | 245.8762
2013.2542 | 465.346 | 472.8238 | 413.5405 | 203.0436 | 253.0098 | 267.4986 | 246.0561
2014.2542 | 464.727 | 471.5007 | 412.4555 | 203.1903 | 253.148 | 267.6166 | 246.1954
2015.2542 | 466.2496 | 472.0689 | 413.5008 | 203.3471 | 253.2748 | 267.7363 | 246.3371
2016.2542 | 468.2794 | 472.7232 | 413.5144 | 203.5024 | 253.4098 | 267.8412 | 246.503
2017.2542 | 468.666 | 472.4964 | 413.6321 | 203.6623 | 253.5371 | 267.9406 | 246.6611
2018.2542 | 468.3553 | 473.7204 | 414.4368 | 203.8249 | 253.6733 | 268.0466 | 246.8534
2019.2542 | 468.0296 | 474.8424 | 416.2692 | 203.9792 | 253.8127 | 268.1613 | 246.9961
2020.2542 | 468.6076 | 475.3707 | 417.7904 | 204.1261 | 253.9515 | 268.2633 | 247.1686
2021.2542 | 469.0124 | 474.6359 | 417.679 | 204.2942 | 254.0988 | 268.3515 | 247.3253
2022.2542 | 469.0299 | 474.061 | 417.1892 | 204.454 | 254.2273 | 268.448 | 247.4889
2023.2542 | 468.9038 | 475.5949 | 419.1107 | 204.5959 | 254.3727 | 268.5198 | 247.6314
2024.2542 | 469.3241 | 477.2421 | 420.5761 | 204.7493 | 254.5209 | 268.6275 | 247.7821
2025.2542 | 468.4838 | 476.8383 | 420.0208 | 204.9268 | 254.6576 | 268.7137 | 247.9567
2026.2542 | 470.1285 | 477.0084 | 419.3748 | 205.0821 | 254.7937 | 268.7961 | 248.1233
2027.2542 | 471.3574 | 476.4171 | 419.169 | 205.2489 | 254.9373 | 268.8913 | 248.2927
2028.2542 | 470.2009 | 475.2597 | 418.1245 | 205.4044 | 255.0644 | 268.9843 | 248.4443
2029.2542 | 470.2764 | 474.6162 | 417.5157 | 205.588 | 255.2138 | 269.0848 | 248.6156
2030.2542 | 470.8664 | 474.0327 | 416.3513 | 205.7736 | 255.3562 | 269.1977 | 248.7892
2031.2542 | 470.8046 | 472.0961 | 416.0982 | 205.9274 | 255.4939 | 269.2744 | 248.9774
2032.2542 | 470.9191 | 472.1191 | 415.5979 | 206.0928 | 255.6541 | 269.372 | 249.1347
2033.2542 | 471.1015 | 471.5815 | 415.2359 | 206.2647 | 255.7917 | 269.4657 | 249.291
2034.2542 | 471.7754 | 471.0629 | 414.6608 | 206.4356 | 255.9363 | 269.5736 | 249.4547
2035.2542 | 470.3947 | 469.8582 | 414.0782 | 206.5983 | 256.0769 | 269.6864 | 249.6085
2036.2542 | 469.6825 | 467.8878 | 413.4087 | 206.7732 | 256.2223 | 269.7814 | 249.7698
2037.2542 | 469.5004 | 468.1222 | 412.8921 | 206.9405 | 256.361 | 269.8795 | 249.9513
2038.2542 | 468.8949 | 468.8055 | 412.9683 | 207.1085 | 256.5031 | 269.9722 | 250.1185
2039.2542 | 467.7824 | 469.3056 | 412.3563 | 207.2763 | 256.6453 | 270.0664 | 250.2958
2040.2542 | 468.4855 | 471.4741 | 412.5075 | 207.445 | 256.7875 | 270.156 | 250.4402
2041.2542 | 468.3082 | 470.3443 | 411.7104 | 207.5989 | 256.92 | 270.2541 | 250.5998
2042.2542 | 468.3711 | 468.5954 | 410.9524 | 207.7575 | 257.0511 | 270.3473 | 250.7478
2043.2542 | 468.0641 | 467.263 | 410.3217 | 207.919 | 257.1858 | 270.4414 | 250.8882
2044.2542 | 467.8824 | 467.6215 | 409.947 | 208.0947 | 257.3217 | 270.5374 | 251.0303
2045.2542 | 468.6057 | 468.1882 | 410.1164 | 208.2413 | 257.4634 | 270.6317 | 251.1292
2046.2542 | 469.0562 | 469.5816 | 409.7469 | 208.4157 | 257.5951 | 270.7359 | 251.2535
2047.2542 | 468.9845 | 469.1904 | 409.3552 | 208.5647 | 257.7221 | 270.824 | 251.3869
2048.2542 | 467.979 | 468.5951 | 408.7443 | 208.7342 | 257.8678 | 270.9196 | 251.499
2049.2542 | 471.5328 | 469.315 | 409.3881 | 208.8961 | 257.9935 | 271.0001 | 251.6238
2050.2542 | 472.0126 | 469.6059 | 409.2818 | 209.0382 | 258.1286 | 271.1025 | 251.7487
2051.2542 | 473.139 | 471.1134 | 410.8521 | 209.2183 | 258.2596 | 271.1969 | 251.9291
2052.2542 | 473.3275 | 471.6355 | 411.4556 | 209.3756 | 258.3842 | 271.2785 | 252.0862
2053.2542 | 475.1058 | 472.051 | 411.8325 | 209.5429 | 258.5222 | 271.3617 | 252.2146
2054.2542 | 475.501 | 473.6541 | 412.39 | 209.6816 | 258.662 | 271.4398 | 252.3269
2055.2542 | 476.5555 | 474.6275 | 412.7228 | 209.8405 | 258.8074 | 271.5151 | 252.4558
2056.2542 | 477.6596 | 473.52 | 413.3133 | 210.0151 | 258.9393 | 271.6531 | 252.5992
2057.2542 | 476.5503 | 472.5409 | 413.1733 | 210.1733 | 259.075 | 271.7495 | 252.7236
2058.2542 | 478.5298 | 473.8108 | 413.9503 | 210.3332 | 259.2153 | 271.8517 | 252.851
2059.2542 | 479.2356 | 473.443 | 414.0614 | 210.4943 | 259.3439 | 271.9261 | 253.0132
2060.2542 | 478.1728 | 472.3436 | 413.6799 | 210.6389 | 259.4701 | 272.0046 | 253.1343
2061.2542 | 477.0042 | 471.3278 | 413.0686 | 210.8169 | 259.6113 | 272.1014 | 253.2733
2062.2542 | 476.6762 | 470.7345 | 412.5577 | 210.9692 | 259.7413 | 272.1692 | 253.4291
2063.2542 | 475.9758 | 470.384 | 411.7199 | 211.144 | 259.8782 | 272.2526 | 253.5619
2064.2542 | 476.0421 | 470.1105 | 412.1795 | 211.2725 | 260.0154 | 272.3307 | 253.6971
2065.2542 | 476.3983 | 470.4077 | 412.2698 | 211.4602 | 260.1457 | 272.4075 | 253.8325
2066.2542 | 476.0316 | 469.5546 | 412.2013 | 211.6245 | 260.2753 | 272.4848 | 253.9662
2067.2542 | 475.8514 | 469.8368 | 412.8263 | 211.7878 | 260.4025 | 272.5732 | 254.0816
2068.2542 | 476.3161 | 471.9359 | 413.0968 | 211.9494 | 260.5354 | 272.66 | 254.1918
2069.2542 | 477.6799 | 471.4284 | 413.0393 | 212.1114 | 260.669 | 272.7402 | 254.3941
2070.2542 | 478.6221 | 470.9958 | 414.095 | 212.2641 | 260.8018 | 272.8283 | 254.5684
2071.2542 | 479.1236 | 472.2917 | 414.3044 | 212.4405 | 260.9195 | 272.907 | 254.7248
2072.2542 | 479.5915 | 471.9281 | 414.2785 | 212.596 | 261.0508 | 272.9855 | 254.8805
2073.2542 | 479.7168 | 473.0963 | 414.5328 | 212.7655 | 261.1647 | 273.0795 | 255.0286
2074.2542 | 479.6194 | 473.2149 | 414.7869 | 212.9249 | 261.3018 | 273.1513 | 255.1955
2075.2542 | 479.8494 | 473.3838 | 415.0554 | 213.087 | 261.4312 | 273.234 | 255.3493
2076.2542 | 478.833 | 475.049 | 415.5845 | 213.2502 | 261.5614 | 273.3166 | 255.5575
2077.2542 | 478.3678 | 476.3795 | 416.4768 | 213.4112 | 261.6906 | 273.4086 | 255.7249
2078.2542 | 476.9514 | 474.7018 | 415.8225 | 213.5951 | 261.821 | 273.4956 | 255.8991
2079.2542 | 476.8398 | 475.3896 | 416.1049 | 213.7534 | 261.9597 | 273.5938 | 256.0465
2080.2542 | 477.485 | 474.9713 | 416.0804 | 213.9116 | 262.0866 | 273.6851 | 256.1931
2081.2542 | 479.7111 | 476.8122 | 417.0441 | 214.0549 | 262.2262 | 273.7816 | 256.3178
2082.2542 | 480.9384 | 476.5632 | 416.8222 | 214.2313 | 262.3547 | 273.8863 | 256.512
2083.2542 | 480.0707 | 474.7661 | 416.3146 | 214.3978 | 262.4696 | 273.9816 | 256.6829
2084.2542 | 480.3476 | 476.6407 | 417.6178 | 214.5678 | 262.5934 | 274.0752 | 256.8509
2085.2542 | 479.9298 | 478.8477 | 419.2812 | 214.7236 | 262.7217 | 274.1733 | 257.0167
2086.2542 | 479.6712 | 478.6844 | 418.9451 | 214.9055 | 262.8399 | 274.2737 | 257.1849
2087.2542 | 480.0913 | 478.2646 | 419.4808 | 215.0559 | 262.9623 | 274.3627 | 257.3494
2088.2542 | 481.1524 | 478.7068 | 421.9125 | 215.2268 | 263.0963 | 274.4505 | 257.5073
2089.2542 | 481.2889 | 477.7683 | 422.7789 | 215.3867 | 263.2234 | 274.5487 | 257.6789
2090.2542 | 480.3684 | 478.5315 | 424.0953 | 215.56 | 263.3551 | 274.6386 | 257.83
2091.2542 | 480.8888 | 478.9449 | 426.1136 | 215.7246 | 263.476 | 274.7214 | 257.95
2092.2542 | 482.6349 | 479.6894 | 426.2247 | 215.8842 | 263.6024 | 274.7985 | 258.0666
2093.2542 | 485.109 | 480.4015 | 425.5484 | 216.0638 | 263.7286 | 274.8936 | 258.2127
2094.2542 | 487.9257 | 478.6104 | 424.5211 | 216.2252 | 263.8573 | 274.9601 | 258.3257
2095.2542 | 486.6305 | 477.5264 | 423.4159 | 216.3941 | 263.998 | 275.0659 | 258.4452
2096.2542 | 486.3156 | 478.0651 | 423.8175 | 216.5611 | 264.1239 | 275.1374 | 258.5644
2097.2542 | 486.2098 | 479.8825 | 425.2897 | 216.7349 | 264.262 | 275.2174 | 258.6632
2098.2542 | 486.3752 | 482.1471 | 428.6055 | 216.9152 | 264.3936 | 275.3052 | 258.754
2099.2542 | 486.8876 | 483.7864 | 430.3435 | 217.0941 | 264.51 | 275.3809 | 258.8819
2100.2542 | 487.5705 | 483.6835 | 430.2489 | 217.2469 | 264.6431 | 275.4601 | 259.0493
2101.2542 | 487.6158 | 482.3755 | 428.9572 | 217.422 | 264.7703 | 275.5194 | 259.2464
2102.2542 | 488.1941 | 483.6413 | 428.9793 | 217.5937 | 264.9084 | 275.5877 | 259.4121
2103.2542 | 488.0793 | 484.961 | 428.2988 | 217.7573 | 265.0376 | 275.6569 | 259.5549
2104.2542 | 488.5351 | 485.2043 | 427.6042 | 217.9253 | 265.1771 | 275.708 | 259.651
2105.2542 | 488.6691 | 483.5586 | 426.1317 | 218.1041 | 265.3212 | 275.7807 | 259.7655
2106.2542 | 489.7916 | 485.2544 | 426.5502 | 218.2786 | 265.4306 | 275.8582 | 259.8566
2107.2542 | 489.5092 | 486.6109 | 426.7711 | 218.4521 | 265.5635 | 275.9093 | 259.8859
2108.2542 | 489.555 | 486.0551 | 426.7683 | 218.6299 | 265.6961 | 275.9716 | 259.8641
2109.2542 | 490.6946 | 487.6311 | 427.4642 | 218.7911 | 265.8179 | 276.045 | 259.8444
2110.2542 | 491.16 | 488.0233 | 428.1631 | 218.9678 | 265.9583 | 276.1513 | 259.8524
2111.2542 | 491.8111 | 489.4215 | 429.5267 | 219.1205 | 266.0945 | 276.2504 | 259.8357
2112.2542 | 494.1725 | 491.8858 | 431.0145 | 219.3046 | 266.2298 | 276.3406 | 259.8254
2113.2542 | 498.9605 | 497.1689 | 432.5003 | 219.4714 | 266.3564 | 276.4316 | 259.8275
2114.2542 | 499.238 | 498.281 | 433.6608 | 219.6233 | 266.4853 | 276.5341 | 259.8343
2115.2542 | 500.5667 | 498.5078 | 434.7255 | 219.8024 | 266.6138 | 276.6129 | 259.8975
2116.2542 | 501.7751 | 499.1532 | 434.7419 | 219.9658 | 266.7434 | 276.7116 | 259.9933
2117.2542 | 502.0435 | 500.7169 | 435.2769 | 220.1187 | 266.8686 | 276.8101 | 260.0595
2118.2542 | 502.7998 | 500.0364 | 434.9226 | 220.3002 | 267.0012 | 276.9235 | 260.1417
2119.2542 | 502.4414 | 499.7965 | 433.4973 | 220.4815 | 267.1305 | 277.0307 | 260.2434
2120.2542 | 503.6506 | 498.768 | 432.8324 | 220.6395 | 267.2565 | 277.1605 | 260.3562
2121.2542 | 503.0575 | 497.4977 | 431.8495 | 220.8068 | 267.4019 | 277.2971 | 260.4728
2122.2542 | 505.0219 | 500.6402 | 435.9204 | 220.9854 | 267.525 | 277.4302 | 260.5868
2123.2542 | 505.5097 | 502.8079 | 438.5301 | 221.181 | 267.6597 | 277.5549 | 260.6936
2124.2542 | 506.5028 | 504.8801 | 440.2925 | 221.3468 | 267.7793 | 277.6863 | 260.8067
2125.2542 | 508.6232 | 507.801 | 440.7934 | 221.5064 | 267.9127 | 277.8076 | 260.8945
2126.2542 | 509.0309 | 509.2912 | 440.5038 | 221.6722 | 268.0399 | 277.9236 | 261.0284
2127.2542 | 509.1607 | 509.336 | 441.0317 | 221.8466 | 268.1732 | 278.0384 | 261.1592
2128.2542 | 510.0995 | 511.2471 | 441.3654 | 222.0154 | 268.303 | 278.1543 | 261.2722
2129.2542 | 512.6362 | 512.4479 | 443.0945 | 222.1654 | 268.4293 | 278.2706 | 261.4218
2130.2542 | 513.481 | 513.0114 | 443.6972 | 222.3745 | 268.5594 | 278.3938 | 261.5842
2131.2542 | 514.6228 | 513.6001 | 444.0009 | 222.5452 | 268.6945 | 278.5345 | 261.7232
2132.2542 | 516.1308 | 515.6014 | 443.7719 | 222.7497 | 268.8285 | 278.6765 | 261.833
2133.2542 | 516.0611 | 515.2832 | 444.2141 | 222.9178 | 268.9501 | 278.8248 | 261.9714
2134.2542 | 517.3898 | 517.1517 | 444.2445 | 223.0943 | 269.0885 | 278.9577 | 262.1086
2135.2542 | 518.2153 | 527.8821 | 444.987 | 223.2596 | 269.2171 | 279.1182 | 262.23
2136.2542 | 518.0297 | 527.8432 | 444.9694 | 223.4457 | 269.348 | 279.2994 | 262.379
2137.2542 | 519.1153 | 528.2133 | 443.2464 | 223.6245 | 269.484 | 279.4635 | 262.5175
2138.2542 | 519.3997 | 526.4734 | 441.2087 | 223.7943 | 269.6252 | 279.6376 | 262.6336
2139.2542 | 519.019 | 524.2354 | 441.4859 | 223.9749 | 269.765 | 279.825 | 262.8037
2140.2542 | 520.2203 | 525.7847 | 442.7725 | 224.1616 | 269.8883 | 280.0325 | 262.9877
2141.2542 | 521.5872 | 524.9587 | 442.0927 | 224.3342 | 270.0121 | 280.5328 | 263.1572
2142.2542 | 522.7725 | 524.7754 | 441.706 | 224.5208 | 270.1395 | 280.8722 | 263.3202
2143.2542 | 524.1511 | 524.4733 | 442.0489 | 224.6981 | 270.2617 | 281.1558 | 263.4893
2144.2542 | 525.8078 | 526.0029 | 442.0995 | 224.8689 | 270.3874 | 281.4029 | 263.687
2145.2542 | 528.0294 | 528.137 | 443.932 | 225.0419 | 270.5191 | 281.6349 | 263.872
2146.2542 | 529.6661 | 529.4095 | 445.2368 | 225.2241 | 270.6515 | 281.8488 | 264.024
2147.2542 | 530.6518 | 533.7455 | 446.6405 | 225.4052 | 270.768 | 282.0311 | 264.1632
2148.2542 | 533.7562 | 533.5196 | 445.4668 | 225.5566 | 270.8927 | 282.2167 | 264.3257
2149.2542 | 534.1967 | 535.0536 | 445.9159 | 225.743 | 271.0238 | 282.2825 | 264.4662
2150.2542 | 534.874 | 536.6874 | 446.2707 | 225.9319 | 271.1572 | 282.3933 | 264.6246
2151.2542 | 536.5043 | 537.0669 | 446.4814 | 226.1124 | 271.2777 | 282.5019 | 264.7533
2152.2542 | 539.2338 | 537.3338 | 446.1972 | 226.2763 | 271.408 | 282.6186 | 264.9196
2153.2542 | 541.0442 | 536.7378 | 445.9615 | 226.5049 | 271.5432 | 282.745 | 265.0771
2154.2542 | 541.6834 | 537.7841 | 445.8344 | 226.6931 | 271.6621 | 282.8706 | 265.2633
2155.2542 | 543.2 | 536.9361 | 445.7398 | 226.863 | 271.7869 | 283.0129 | 265.4168
2156.2542 | 547.131 | 537.6182 | 447.174 | 227.0615 | 271.9203 | 283.1461 | 265.6146
2157.2542 | 548.82 | 536.0658 | 446.415 | 227.2351 | 272.0427 | 283.2819 | 265.8053
2158.2542 | 551.8289 | 537.4462 | 445.75 | 227.4037 | 272.1674 | 283.409 | 265.9862
2159.2542 | 555.5956 | 537.2821 | 445.7028 | 227.5939 | 272.2982 | 283.5334 | 266.0861
2160.2542 | 555.4167 | 536.5828 | 445.2056 | 227.7587 | 272.4324 | 283.6669 | 266.2872
2161.2542 | 556.8364 | 541.6869 | 444.9778 | 227.9327 | 272.5544 | 283.791 | 266.4395
2162.2542 | 555.4214 | 541.525 | 445.3238 | 228.1154 | 272.6755 | 283.931 | 266.6075
2163.2542 | 557.8724 | 544.1832 | 447.5118 | 228.3116 | 272.8048 | 284.0732 | 266.7859
2164.2542 | 561.8676 | 546.679 | 447.5043 | 228.492 | 272.929 | 284.2105 | 266.9644
2165.2542 | 560.5597 | 542.75 | 446.5539 | 228.6827 | 273.0566 | 284.3377 | 267.1384
2166.2542 | 562.711 | 544.8511 | 446.11 | 228.8545 | 273.1757 | 284.4661 | 267.3006
2167.2542 | 564.9863 | 546.8008 | 446.6066 | 229.0513 | 273.3077 | 284.5836 | 267.4755
2168.2542 | 566.0149 | 548.3473 | 448.4372 | 229.2401 | 273.4286 | 284.7184 | 267.6685
2169.2542 | 567.7032 | 549.6514 | 449.2365 | 229.4401 | 273.5593 | 284.8504 | 267.8247
2170.2542 | 568.0372 | 547.6885 | 447.7031 | 229.6261 | 273.6905 | 284.9716 | 267.978
2171.2542 | 570.7592 | 551.8584 | 448.4121 | 229.8086 | 273.8083 | 285.0985 | 268.1188
2172.2542 | 573.7873 | 554.5511 | 450.51 | 229.9879 | 273.9412 | 285.2135 | 268.2723
2173.2542 | 573.3283 | 553.3358 | 450.4399 | 230.1928 | 274.0634 | 285.3304 | 268.4165
2174.2542 | 572.5647 | 553.0592 | 452.3783 | 230.3602 | 274.1855 | 285.4647 | 268.5194
2175.2542 | 573.2316 | 552.5546 | 452.8927 | 230.5489 | 274.3115 | 285.5844 | 268.6328
2176.2542 | 574.3702 | 553.7374 | 453.1159 | 230.7325 | 274.4378 | 285.699 | 268.781
2177.2542 | 577.5329 | 560.6177 | 453.8619 | 230.9291 | 274.5581 | 285.8328 | 268.9792
2178.2542 | 579.6049 | 560.197 | 452.7569 | 231.1154 | 274.6758 | 285.9581 | 269.0625
2179.2542 | 579.7843 | 556.7141 | 451.4599 | 231.3275 | 274.8269 | 286.0915 | 269.135
2180.2542 | 581.8781 | 558.7754 | 452.3931 | 231.512 | 274.9428 | 286.2175 | 269.2193
2181.2542 | 581.7931 | 557.9433 | 453.0091 | 231.7235 | 275.0744 | 286.3452 | 269.3239
2182.2542 | 584.0056 | 559.3832 | 454.3425 | 231.8779 | 275.1892 | 286.4595 | 269.4278
2183.2542 | 588.2257 | 561.6366 | 455.6083 | 232.0775 | 275.3146 | 286.569 | 269.5242
2184.2542 | 590.7509 | 561.4912 | 456.2123 | 232.2614 | 275.448 | 286.7024 | 269.5808
2185.2542 | 591.5338 | 562.958 | 457.8687 | 232.4655 | 275.5687 | 286.8163 | 269.6576
2186.2542 | 592.6942 | 563.5474 | 458.2082 | 232.6486 | 275.7064 | 286.935 | 269.7406
2187.2542 | 594.5792 | 567.619 | 457.4613 | 232.8439 | 275.8357 | 287.0506 | 269.8437
2188.2542 | 594.3656 | 569.2357 | 458.1029 | 233.0297 | 275.9687 | 287.1743 | 269.9218
2189.2542 | 596.8465 | 570.9826 | 457.7775 | 233.2105 | 276.1032 | 287.3052 | 270.0171
2190.2542 | 601.0343 | 583.4735 | 459.3772 | 233.4159 | 276.2468 | 287.4296 | 270.1079
2191.2542 | 603.7409 | 588.786 | 460.5829 | 233.6195 | 276.3822 | 287.5639 | 270.1899
2192.2542 | 605.6097 | 597.876 | 461.3839 | 233.7921 | 276.5185 | 287.6972 | 270.2686
2193.2542 | 607.2554 | 600.6811 | 462.6292 | 233.9841 | 276.6503 | 287.8321 | 270.3695
2194.2542 | 607.2362 | 596.9408 | 462.1757 | 234.1835 | 276.7832 | 287.9551 | 270.4611
2195.2542 | 605.6959 | 598.9364 | 462.5698 | 234.3914 | 276.9222 | 288.1033 | 270.5383
2196.2542 | 606.4492 | 602.4657 | 464.4507 | 234.581 | 277.0459 | 288.2283 | 270.5974
2197.2542 | 607.6334 | 602.7906 | 465.4401 | 234.7693 | 277.19 | 288.3597 | 270.6707
2198.2542 | 609.1807 | 598.1862 | 465.3963 | 234.9821 | 277.3247 | 288.4882 | 270.7739
2199.2542 | 609.0862 | 600.4444 | 464.5679 | 235.161 | 277.4582 | 288.6222 | 270.8564
2200.2542 | 610.4017 | 614.8621 | 464.8396 | 235.3626 | 277.5957 | 288.7593 | 270.9448
2201.2542 | 610.1267 | 618.6238 | 465.8197 | 235.568 | 277.7384 | 288.8498 | 271.0857
2202.2542 | 609.813 | 620.8555 | 467.0504 | 235.7651 | 277.8739 | 288.8531 | 271.3856
2203.2542 | 608.7944 | 618.9684 | 468.3985 | 235.9606 | 278.0086 | 288.859 | 271.6575
2204.2542 | 610.1452 | 615.6867 | 469.0053 | 236.1721 | 278.1482 | 288.851 | 271.9153
2205.2542 | 610.1899 | 609.8232 | 467.6585 | 236.3608 | 278.2836 | 288.8532 | 272.1576
2206.2542 | 611.2951 | 606.2069 | 468.0564 | 236.5535 | 278.4284 | 288.8575 | 272.391
2207.2542 | 608.6525 | 603.3332 | 467.1528 | 236.7568 | 278.5672 | 288.8808 | 272.6063
2208.2542 | 609.2123 | 604.9349 | 468.4631 | 236.9336 | 278.7115 | 288.902 | 272.8563
2209.2542 | 610.3915 | 605.1789 | 470.0896 | 237.1079 | 278.8465 | 288.9411 | 273.0664
2210.2542 | 611.9626 | 611.6954 | 470.8579 | 237.3089 | 278.9935 | 289.0032 | 273.289
2211.2542 | 612.0069 | 613.3289 | 473.0266 | 237.5261 | 279.136 | 289.0613 | 273.5051
2212.2542 | 613.2622 | 611.0386 | 473.6033 | 237.7024 | 279.2778 | 289.1287 | 273.7057
2213.2542 | 614.021 | 606.1284 | 472.546 | 237.891 | 279.4219 | 289.1945 | 273.8918
2214.2542 | 615.0697 | 614.7251 | 472.7819 | 238.0967 | 279.565 | 289.2902 | 274.1035
2215.2542 | 617.0049 | 620.9574 | 473.9372 | 238.3129 | 279.7104 | 289.3702 | 274.2835
2216.2542 | 618.9095 | 619.719 | 475.4705 | 238.518 | 279.8529 | 289.4613 | 274.491
2217.2542 | 618.9307 | 621.6887 | 476.2425 | 238.7072 | 280.0049 | 289.5501 | 274.6593
2218.2542 | 619.1004 | 621.0054 | 476.8801 | 238.907 | 280.1531 | 289.6682 | 274.8396
2219.2542 | 620.1704 | 619.0512 | 478.2473 | 239.0984 | 280.3051 | 289.7731 | 275.0064
2220.2542 | 621.1428 | 623.2066 | 478.2394 | 239.2794 | 280.4506 | 289.8802 | 275.1835
2221.2542 | 622.4847 | 626.2161 | 478.8383 | 239.4827 | 280.5961 | 289.9859 | 275.352
2222.2542 | 622.9962 | 621.416 | 478.1619 | 239.6691 | 280.7394 | 290.094 | 275.5364
2223.2542 | 623.6328 | 617.5325 | 477.2873 | 239.8849 | 280.8701 | 290.2224 | 275.7388
2224.2542 | 626.4777 | 615.3867 | 477.3376 | 240.0759 | 281.0193 | 290.3553 | 275.9201
2225.2542 | 623.1079 | 618.8654 | 478.0974 | 240.2754 | 281.1783 | 290.4845 | 276.0872
2226.2542 | 623.5696 | 616.3062 | 479.3685 | 240.4588 | 281.3374 | 290.6068 | 276.2648
2227.2542 | 621.0215 | 614.118 | 477.7834 | 240.6518 | 281.4833 | 290.7382 | 276.4439
2228.2542 | 620.2704 | 614.6478 | 477.4739 | 240.8379 | 281.6344 | 290.8629 | 276.6113
2229.2542 | 622.444 | 617.4088 | 477.9857 | 241.0396 | 281.7858 | 291.0024 | 276.801
2230.2542 | 619.2769 | 626.7143 | 477.1636 | 241.2295 | 281.9326 | 291.1343 | 276.9762
2231.2542 | 617.763 | 623.6694 | 480.7882 | 241.4318 | 282.0849 | 291.2756 | 277.1464
2232.2542 | 616.3312 | 622.7355 | 481.9481 | 241.6348 | 282.236 | 291.4199 | 277.2917
2233.2542 | 614.0795 | 619.6877 | 481.8826 | 241.8157 | 282.3971 | 291.5631 | 277.4266
2234.2542 | 615.7938 | 616.558 | 481.788 | 242.0286 | 282.5438 | 291.7129 | 277.5849
2235.2542 | 617.6598 | 617.699 | 482.9944 | 242.2175 | 282.7026 | 291.8517 | 277.7242
2236.2542 | 617.3818 | 614.8233 | 483.1377 | 242.4174 | 282.8604 | 292.0036 | 277.8809
2237.2542 | 615.8445 | 614.8552 | 483.3163 | 242.6105 | 283.0124 | 292.1497 | 278.0508
2238.2542 | 615.0521 | 614.0308 | 482.9045 | 242.808 | 283.1725 | 292.3099 | 278.236
2239.2542 | 613.9948 | 615.0142 | 483.3304 | 242.9934 | 283.3344 | 292.4722 | 278.4011
2240.2542 | 614.901 | 618.5622 | 484.2492 | 243.2086 | 283.4859 | 292.6366 | 278.5876
2241.2542 | 612.7142 | 617.8294 | 486.0752 | 243.4364 | 283.6449 | 292.7951 | 278.7426
2242.2542 | 614.5788 | 620.2359 | 488.0956 | 243.6164 | 283.8176 | 292.9446 | 278.8848
2243.2542 | 613.4647 | 624.48 | 488.5105 | 243.8015 | 283.9822 | 293.086 | 279.0512
2244.2542 | 612.836 | 620.3729 | 488.1146 | 244.0007 | 284.1424 | 293.2386 | 279.2052
2245.2542 | 614.0905 | 615.4613 | 487.634 | 244.1766 | 284.3206 | 293.3774 | 279.3609
2246.2542 | 613.7224 | 612.7044 | 486.6982 | 244.4383 | 284.4893 | 293.5531 | 279.532
2247.2542 | 612.719 | 607.4918 | 485.7776 | 244.5776 | 284.6602 | 293.6893 | 279.6844
2248.2542 | 610.5403 | 607.2336 | 485.6663 | 244.7825 | 284.8314 | 293.8508 | 279.8292
2249.2542 | 612.9864 | 610.3462 | 484.8506 | 244.9971 | 284.9997 | 294.0148 | 280.0054
2250.2542 | 612.5141 | 605.3084 | 483.9923 | 245.1798 | 285.1812 | 294.1739 | 280.1587
2251.2542 | 610.2918 | 602.8599 | 483.3693 | 245.3688 | 285.3582 | 294.3247 | 280.3037
2252.2542 | 611.3143 | 603.3011 | 482.8984 | 245.5471 | 285.5372 | 294.4657 | 280.4583
2253.2542 | 609.6753 | 600.5276 | 482.0921 | 245.7759 | 285.7312 | 294.6281 | 280.6289
2254.2542 | 609.7988 | 603.942 | 485.5701 | 245.9557 | 285.9199 | 294.7763 | 280.7573
2255.2542 | 612.0736 | 604.7668 | 486.06 | 246.1589 | 286.1088 | 294.935 | 280.8659
2256.2542 | 611.3586 | 605.7882 | 486.1565 | 246.3707 | 286.2982 | 295.102 | 281.013
2257.2542 | 610.7269 | 605.7316 | 486.5227 | 246.5662 | 286.4925 | 295.259 | 281.1809
2258.2542 | 610.7069 | 606.1616 | 490.01 | 246.7954 | 286.6864 | 295.3967 | 281.3323
2259.2542 | 610.9628 | 604.3402 | 490.7687 | 247.06 | 286.8759 | 295.538 | 281.4524
2260.2542 | 610.7098 | 602.0675 | 489.9289 | 247.276 | 287.0648 | 295.6836 | 281.5923
2261.2542 | 611.488 | 607.2095 | 492.2345 | 247.4561 | 287.2641 | 295.8217 | 281.7507
2262.2542 | 609.4941 | 603.5856 | 492.5842 | 247.7127 | 287.4515 | 295.9674 | 281.9306
2263.2542 | 610.1952 | 607.6515 | 493.0465 | 247.8916 | 287.6595 | 296.1067 | 282.1792
2264.2542 | 612.3559 | 611.2612 | 493.0906 | 248.0823 | 287.8677 | 296.2327 | 282.4148
2265.2542 | 614.1722 | 617.5812 | 492.8789 | 248.3081 | 288.0784 | 296.3639 | 282.6376
2266.2542 | 612.1823 | 614.7864 | 492.0593 | 248.5309 | 288.2912 | 296.5192 | 282.8513
2267.2542 | 614.9997 | 617.718 | 492.4675 | 248.7821 | 288.5035 | 296.6881 | 283.041
2268.2542 | 615.7999 | 617.6114 | 496.1182 | 249.0003 | 288.7107 | 296.8385 | 283.1965
2269.2542 | 617.0805 | 612.1033 | 507.3267 | 249.2802 | 288.9196 | 297.011 | 283.396
2270.2542 | 616.1686 | 611.4189 | 509.4698 | 249.5046 | 289.1403 | 297.1656 | 283.5544
2271.2542 | 615.0999 | 612.2472 | 509.9208 | 249.6615 | 289.344 | 297.3315 | 283.7237
2272.2542 | 614.241 | 611.0864 | 507.1179 | 249.861 | 289.5499 | 297.4857 | 283.8784
2273.2542 | 613.5449 | 608.2488 | 504.6834 | 250.159 | 289.7515 | 297.6143 | 284.0592
2274.2542 | 613.8411 | 617.3337 | 503.6736 | 250.2523 | 289.9549 | 297.7185 | 284.3495
2275.2542 | 616.5862 | 616.2452 | 503.3472 | 250.5049 | 290.1462 | 297.8919 | 284.5531
2276.2542 | 619.1824 | 617.152 | 503.4859 | 250.5786 | 290.3494 | 298.0701 | 284.7693
2277.2542 | 621.1381 | 622.6045 | 503.6143 | 250.7579 | 290.5424 | 298.2367 | 284.9784
2278.2542 | 623.7702 | 620.4614 | 503.4044 | 250.9287 | 290.7364 | 298.4069 | 285.1662
2279.2542 | 623.5265 | 618.1997 | 502.1104 | 251.1267 | 290.9328 | 298.5734 | 285.3377
2280.2542 | 624.3912 | 613.667 | 500.0784 | 251.3192 | 291.1158 | 298.7573 | 285.5199
2281.2542 | 627.5051 | 616.6597 | 501.1615 | 251.5181 | 291.3101 | 298.9341 | 285.6828
2282.2542 | 628.444 | 621.4432 | 502.1082 | 251.6899 | 291.5038 | 299.1189 | 285.8493
2283.2542 | 628.353 | 629.6116 | 506.9761 | 251.9431 | 291.696 | 299.2912 | 286.0224
2284.2542 | 629.2853 | 626.5564 | 506.0819 | 252.061 | 291.8864 | 299.475 | 286.2247
2285.2542 | 628.6642 | 626.1147 | 505.816 | 252.2897 | 292.0758 | 299.6353 | 286.4234
2286.2542 | 629.2423 | 629.2672 | 505.4461 | 252.4375 | 292.271 | 299.7851 | 286.6069
2287.2542 | 630.0996 | 630.4216 | 505.6162 | 252.6472 | 292.4637 | 299.9209 | 286.8115
2288.2542 | 633.3965 | 633.5368 | 506.2178 | 252.8548 | 292.6645 | 300.0764 | 287.0043
2289.2542 | 633.6478 | 632.997 | 506.5496 | 253.0083 | 292.8666 | 300.2358 | 287.1845
2290.2542 | 632.5162 | 630.9429 | 505.9352 | 253.2345 | 293.0595 | 300.3812 | 287.3717
2291.2542 | 637.5231 | 632.8687 | 505.4508 | 253.4038 | 293.2523 | 300.5196 | 287.5891
2292.2542 | 635.1476 | 631.7804 | 507.0871 | 253.6712 | 293.4552 | 300.6674 | 287.7777
2293.2542 | 637.9658 | 633.5195 | 508.2452 | 253.8512 | 293.6512 | 300.8001 | 287.9817
2294.2542 | 636.4336 | 631.8777 | 508.8801 | 254.0064 | 293.8562 | 300.9321 | 288.1538
2295.2542 | 636.5436 | 627.6261 | 509.0155 | 254.2573 | 294.0545 | 301.0686 | 288.3713
2296.2542 | 635.8537 | 625.5598 | 508.2024 | 254.5415 | 294.2567 | 301.188 | 288.5937
2297.2542 | 635.7877 | 625.4563 | 509.7891 | 254.7421 | 294.468 | 301.3189 | 288.8018
2298.2542 | 634.5197 | 625.5561 | 511.3333 | 254.8106 | 294.6755 | 301.4484 | 289.003
2299.2542 | 634.5539 | 625.2168 | 512.4806 | 255.1004 | 294.8802 | 301.5571 | 289.2075
2300.2542 | 633.7546 | 623.1714 | 512.6197 | 255.2128 | 295.0732 | 301.6611 | 289.4362
2301.2542 | 631.9392 | 623.7699 | 511.9694 | 255.4821 | 295.2777 | 301.7728 | 289.6511
2302.2542 | 631.2188 | 623.4534 | 511.8146 | 255.6343 | 295.4756 | 301.8762 | 289.8475
2303.2542 | 629.279 | 623.7114 | 513.5574 | 255.8073 | 295.6609 | 301.9843 | 290.049
2304.2542 | 628.3963 | 622.3779 | 513.9898 | 256.0126 | 295.8515 | 302.0934 | 290.28
2305.2542 | 629.1895 | 621.9356 | 513.6253 | 256.1856 | 296.0314 | 302.1939 | 290.4962
2306.2542 | 627.808 | 618.8054 | 511.338 | 256.4116 | 296.2287 | 302.2808 | 290.7214
2307.2542 | 627.7206 | 617.8899 | 510.3783 | 256.8279 | 296.4355 | 302.374 | 290.9424
2308.2542 | 629.0826 | 619.2885 | 512.4534 | 257.0366 | 296.6337 | 302.4605 | 291.1458
2309.2542 | 629.9686 | 620.7043 | 512.0457 | 257.1059 | 296.8465 | 302.5489 | 291.5462
2310.2542 | 629.6247 | 614.9596 | 510.5281 | 257.2929 | 297.0646 | 302.6234 | 291.9162
2311.2542 | 627.8078 | 613.7955 | 508.1003 | 257.4363 | 297.2868 | 302.7025 | 292.2465
2312.2542 | 628.1139 | 613.617 | 507.5469 | 257.6515 | 297.5135 | 302.7775 | 292.5679
2313.2542 | 630.4262 | 618.0072 | 508.0289 | 257.8742 | 297.7512 | 302.8587 | 292.8698
2314.2542 | 633.0336 | 616.291 | 508.6895 | 258.1786 | 298.0021 | 302.9459 | 293.158
2315.2542 | 634.4994 | 615.6698 | 507.8485 | 258.3382 | 298.247 | 303.0273 | 293.4507
2316.2542 | 632.9519 | 615.4794 | 507.292 | 258.4674 | 298.4604 | 303.1125 | 293.7388
2317.2542 | 633.951 | 620.4701 | 511.1461 | 258.6921 | 298.6723 | 303.1832 | 293.9911
2318.2542 | 633.4176 | 621.5089 | 513.6211 | 259.0061 | 298.8778 | 303.2637 | 294.2505
2319.2542 | 636.3758 | 625.4652 | 515.1411 | 259.2737 | 299.0696 | 303.3594 | 294.5221
2320.2542 | 636.1214 | 629.1749 | 518.2475 | 259.4395 | 299.2589 | 303.4472 | 294.7463
2321.2542 | 639.3626 | 630.0418 | 523.4283 | 259.6355 | 299.4509 | 303.5347 | 295.0122
2322.2542 | 638.7891 | 628.1711 | 521.3221 | 259.839 | 299.6441 | 303.6231 | 295.2808
2323.2542 | 638.8896 | 631.1046 | 520.2347 | 260.1158 | 299.8353 | 303.722 | 295.5277
2324.2542 | 642.3295 | 640.7315 | 522.3869 | 260.2643 | 300.0344 | 303.7953 | 295.7735
2325.2542 | 641.312 | 636.0264 | 524.6501 | 260.4208 | 300.2202 | 303.8746 | 296.0219
2326.2542 | 643.5305 | 635.4479 | 526.3562 | 260.6554 | 300.3965 | 303.9702 | 296.2727
2327.2542 | 641.7242 | 632.5201 | 525.6335 | 260.7958 | 300.5885 | 304.0413 | 296.5236
2328.2542 | 642.3525 | 634.4957 | 527.9623 | 261.0559 | 300.7793 | 304.0763 | 296.789
2329.2542 | 642.3423 | 635.8477 | 530.9237 | 261.2666 | 300.9433 | 304.1084 | 297.0579
2330.2542 | 649.0955 | 641.5043 | 531.8273 | 261.5668 | 301.1353 | 304.1807 | 297.3063
2331.2542 | 649.8202 | 642.0288 | 534.0753 | 261.7257 | 301.3353 | 304.2786 | 297.5646
2332.2542 | 652.8139 | 641.9942 | 536.1986 | 261.9033 | 301.5398 | 304.3737 | 297.8503
2333.2542 | 651.9395 | 639.8728 | 536.6196 | 262.0932 | 301.7355 | 304.4463 | 298.1312
2334.2542 | 649.3824 | 635.5143 | 534.2826 | 262.2929 | 301.9417 | 304.543 | 298.4295
2335.2542 | 648.5213 | 646.6989 | 535.8513 | 262.5082 | 302.1491 | 304.6255 | 298.6776
2336.2542 | 647.474 | 643.6869 | 541.523 | 262.6863 | 302.3468 | 304.7255 | 298.9348
2337.2542 | 646.1383 | 641.323 | 543.0844 | 262.8439 | 302.5467 | 304.8041 | 299.2195
2338.2542 | 645.237 | 639.5182 | 544.6238 | 263.0496 | 302.7447 | 304.9113 | 299.5
2339.2542 | 647.2671 | 641.8825 | 544.129 | 263.3192 | 302.9455 | 305.0106 | 299.7966
2340.2542 | 646.5457 | 645.0744 | 545.7361 | 263.473 | 303.1317 | 305.1173 | 300.06
2341.2542 | 647.9687 | 648.4067 | 552.4287 | 263.7294 | 303.333 | 305.2137 | 300.3583
2342.2542 | 647.8488 | 648.8025 | 560.1572 | 263.8944 | 303.5337 | 305.3384 | 300.6317
2343.2542 | 648.5934 | 648.1469 | 558.0856 | 264.0919 | 303.7268 | 305.4351 | 300.9231
2344.2542 | 646.5101 | 643.8662 | 554.8967 | 264.3397 | 303.916 | 305.5545 | 301.1932
2345.2542 | 647.8258 | 654.1671 | 553.8398 | 264.6215 | 304.0995 | 305.6733 | 301.4697
2346.2542 | 650.1016 | 659.7257 | 557.8901 | 264.874 | 304.2705 | 305.7859 | 301.7496
2347.2542 | 650.1856 | 654.1674 | 557.9317 | 265.0263 | 304.4334 | 305.9241 | 302.0458
2348.2542 | 649.2272 | 663.6732 | 560.4361 | 265.1378 | 304.5987 | 306.0587 | 302.3233
2349.2542 | 648.0813 | 659.096 | 562.0817 | 265.3739 | 304.7645 | 306.1755 | 302.6085
2350.2542 | 647.5525 | 656.9747 | 562.3661 | 265.5006 | 304.9298 | 306.3208 | 302.8859
2351.2542 | 646.3588 | 654.1675 | 562.5029 | 265.6998 | 305.1217 | 306.463 | 303.2053
2352.2542 | 644.6488 | 646.7294 | 560.5535 | 265.8968 | 305.3462 | 306.6261 | 303.5143
2353.2542 | 644.2153 | 646.4641 | 560.1156 | 266.1255 | 305.5518 | 306.818 | 303.8071
2354.2542 | 643.8918 | 645.8006 | 558.0313 | 266.3223 | 305.7683 | 306.996 | 304.127
2355.2542 | 643.7378 | 640.6965 | 556.9632 | 266.4535 | 305.9825 | 307.1939 | 304.422
2356.2542 | 642.8356 | 637.2523 | 555.1721 | 266.6832 | 306.185 | 307.4138 | 304.7103
2357.2542 | 643.2023 | 638.8123 | 555.7398 | 266.8642 | 306.3769 | 307.6285 | 305.0033
2358.2542 | 645.7114 | 642.8102 | 555.5003 | 267.0894 | 306.5615 | 307.8338 | 305.3022
2359.2542 | 647.3632 | 653.3863 | 556.7994 | 267.3146 | 306.7579 | 308.0415 | 305.6
2360.2542 | 647.7952 | 659.7753 | 557.438 | 267.5816 | 306.9668 | 308.2419 | 305.8892
2361.2542 | 646.5209 | 665.4847 | 562.1254 | 267.7379 | 307.1304 | 308.4462 | 306.2067
2362.2542 | 648.7387 | 666.5869 | 564.9429 | 268.1136 | 307.3064 | 308.6679 | 306.5014
2363.2542 | 650.5017 | 665.4538 | 566.4225 | 268.3406 | 307.4628 | 308.8953 | 306.8102
2364.2542 | 651.0625 | 663.309 | 564.336 | 268.5244 | 307.6075 | 309.1423 | 307.1238
2365.2542 | 652.2478 | 669.9841 | 567.2616 | 268.7162 | 307.7454 | 309.3861 | 307.4242
2366.2542 | 650.9913 | 667.89 | 569.6471 | 268.7653 | 307.8923 | 309.6443 | 307.7309
2367.2542 | 650.6514 | 667.0785 | 577.1152 | 268.8589 | 308.0334 | 309.8932 | 308.0376
2368.2542 | 650.2905 | 663.0357 | 585.4034 | 269.3004 | 308.1841 | 310.1607 | 308.3342
2369.2542 | 649.6682 | 661.2011 | 587.4753 | 269.4183 | 308.3427 | 310.4136 | 308.6651
2370.2542 | 652.4935 | 661.8577 | 587.6485 | 269.6843 | 308.5018 | 310.6814 | 308.9808
2371.2542 | 655.6482 | 668.666 | 590.5678 | 270.116 | 308.6555 | 310.959 | 309.3341
2372.2542 | 655.5877 | 665.97 | 590.8968 | 270.3764 | 308.8156 | 311.2539 | 309.7524
2373.2542 | 658.6951 | 673.7656 | 598.3395 | 270.5625 | 308.9707 | 311.5523 | 310.1471
2374.2542 | 655.4953 | 671.7313 | 603.4657 | 270.6988 | 309.1439 | 311.8404 | 310.5445
2375.2542 | 654.3408 | 665.9215 | 606.2735 | 270.9392 | 309.314 | 312.14 | 310.9678
2376.2542 | 654.2676 | 663.9096 | 605.4967 | 271.1408 | 309.4736 | 312.4447 | 311.3939
2377.2542 | 656.1758 | 663.7935 | 605.7605 | 271.2851 | 309.6448 | 312.7591 | 311.7755
2378.2542 | 657.223 | 668.7492 | 606.5644 | 271.5919 | 309.8249 | 313.086 | 312.1537
2379.2542 | 657.464 | 664.4049 | 606.0707 | 271.741 | 310.0159 | 313.4106 | 312.5429
2380.2542 | 659.5887 | 672.8888 | 606.3027 | 271.8732 | 310.2285 | 313.715 | 312.951
2381.2542 | 658.0263 | 675.6401 | 611.7337 | 271.9776 | 310.4574 | 314.0501 | 313.3481
2382.2542 | 658.1067 | 670.5156 | 608.9521 | 272.3359 | 310.6922 | 314.3908 | 313.7296
2383.2542 | 657.2386 | 667.2196 | 604.4168 | 272.6214 | 310.9283 | 314.7298 | 314.1235
2384.2542 | 658.9259 | 663.5507 | 607.0704 | 272.9685 | 311.1724 | 315.0674 | 314.514
2385.2542 | 658.5139 | 662.2009 | 605.2148 | 273.1505 | 311.4179 | 315.4223 | 314.9009
2386.2542 | 660.2153 | 658.8946 | 601.2858 | 273.2832 | 311.6684 | 315.777 | 315.285
2387.2542 | 658.9621 | 656.5845 | 597.4441 | 273.5087 | 311.9467 | 316.129 | 315.6826
2388.2542 | 660.714 | 655.5812 | 596.1572 | 273.8356 | 312.2435 | 316.457 | 316.0743
2389.2542 | 662.0896 | 652.8513 | 595.4406 | 274.1086 | 312.5882 | 316.8027 | 316.4483
2390.2542 | 667.451 | 655.7232 | 593.5211 | 274.3311 | 312.9222 | 317.1362 | 316.8442
2391.2542 | 666.5486 | 657.4742 | 590.6294 | 274.7559 | 313.2104 | 317.4738 | 317.2067
2392.2542 | 665.9844 | 653.1417 | 590.7331 | 275.2614 | 313.5126 | 317.7997 | 317.5771
2393.2542 | 665.3783 | 648.4306 | 593.7981 | 275.8837 | 313.8139 | 318.1264 | 317.9678
2394.2542 | 664.0463 | 659.0636 | 591.9659 | 275.8226 | 314.1018 | 318.4502 | 318.3714
2395.2542 | 663.9471 | 662.9366 | 592.0794 | 276.1844 | 314.3404 | 318.7825 | 318.7628
2396.2542 | 664.9447 | 662.7614 | 590.529 | 276.4435 | 314.5979 | 319.1025 | 319.15
2397.2542 | 663.1269 | 673.6079 | 599.2739 | 276.6627 | 314.8691 | 319.4002 | 319.5851
2398.2542 | 669.1962 | 670.3878 | 599.9792 | 277.2819 | 315.1698 | 319.7034 | 319.9891
2399.2542 | 672.2653 | 667.7502 | 598.3191 | 277.5111 | 315.4835 | 320.0124 | 320.4128
2400.2542 | 672.7122 | 676.1292 | 598.0601 | 278.3403 | 315.8309 | 320.3206 | 320.8265
2401.2542 | 672.2239 | 678.2878 | 602.0264 | 278.661 | 316.1745 | 320.6336 | 321.2567
2402.2542 | 673.2249 | 691.1798 | 606.9869 | 278.7931 | 316.5234 | 320.9474 | 321.6825
2403.2542 | 672.6469 | 687.7525 | 605.3504 | 279.1994 | 316.8742 | 321.2736 | 322.0979
2404.2542 | 673.1734 | 682.7973 | 606.4591 | 279.5993 | 317.2626 | 321.5802 | 322.4843
2405.2542 | 671.4219 | 678.9922 | 606.3925 | 280.3965 | 317.622 | 321.9108 | 322.8717
2406.2542 | 668.6932 | 673.9376 | 605.7363 | 280.8481 | 317.9805 | 322.232 | 323.2133
2407.2542 | 666.797 | 669.5839 | 603.4786 | 281.3776 | 318.342 | 322.5715 | 323.6003
2408.2542 | 664.7815 | 666.2235 | 600.2939 | 281.513 | 318.7301 | 322.8914 | 323.9873
2409.2542 | 664.1959 | 663.8563 | 598.0578 | 281.6549 | 319.1123 | 323.2115 | 324.3637
2410.2542 | 666.0948 | 661.3497 | 595.9317 | 282.7347 | 319.4669 | 323.5325 | 324.7683
2411.2542 | 666.9953 | 659.6744 | 595.7629 | 284.3672 | 319.8342 | 323.8551 | 325.192
2412.2542 | 666.5651 | 658.5079 | 593.2866 | 284.4702 | 320.2329 | 324.1947 | 325.585
2413.2542 | 668.3061 | 658.5421 | 593.4137 | 284.9397 | 320.6372 | 324.5115 | 325.9892
2414.2542 | 668.2738 | 657.4601 | 591.683 | 285.1684 | 321.0498 | 324.8332 | 326.3941
2415.2542 | 666.3557 | 655.4826 | 588.8939 | 285.444 | 321.4683 | 325.1316 | 326.8047
2416.2542 | 665.9229 | 655.0273 | 587.6213 | 285.9508 | 321.8766 | 325.4438 | 327.2199
2417.2542 | 666.5401 | 654.5758 | 584.1595 | 286.3217 | 322.2863 | 325.7492 | 327.6366
2418.2542 | 665.8035 | 659.9472 | 584.9074 | 287.5209 | 322.6971 | 326.0443 | 328.0358
2419.2542 | 668.3842 | 657.6053 | 584.8222 | 288.4683 | 323.1297 | 326.3596 | 328.4505
2420.2542 | 669.8888 | 656.9558 | 585.4345 | 288.9852 | 323.5599 | 326.6581 | 328.7894
2421.2542 | 671.6457 | 656.0285 | 584.9865 | 290.9127 | 323.9941 | 326.9478 | 329.2001
2422.2542 | 673.4207 | 658.2456 | 585.1259 | 290.6006 | 324.4567 | 327.2288 | 329.5962
2423.2542 | 672.6132 | 657.6228 | 583.8944 | 291.1129 | 324.9442 | 327.5155 | 329.9961
2424.2542 | 674.0583 | 661.0275 | 582.1216 | 292.8272 | 325.4165 | 327.7864 | 330.3967
2425.2542 | 672.6888 | 661.1573 | 583.4145 | 293.9299 | 325.8915 | 328.079 | 330.7929
2426.2542 | 672.5844 | 659.2143 | 586.9428 | 294.6959 | 326.3691 | 328.372 | 331.2081
2427.2542 | 672.9856 | 659.7112 | 589.874 | 295.448 | 326.8628 | 328.6458 | 331.6509
2428.2542 | 674.2005 | 659.5031 | 589.8262 | 296.1892 | 327.3725 | 328.9385 | 332.0666
2429.2542 | 674.6136 | 658.9651 | 589.2494 | 297.1666 | 327.8698 | 329.2264 | 332.5105
2430.2542 | 675.7196 | 659.4187 | 590.1791 | 297.5545 | 328.3917 | 329.5158 | 332.9352
2431.2542 | 676.1993 | 661.4973 | 592.3 | 297.9405 | 328.9231 | 329.8008 | 333.3395
2432.2542 | 679.1559 | 664.3705 | 599.4777 | 298.9717 | 329.4571 | 330.0951 | 333.7755
2433.2542 | 679.9502 | 666.4967 | 598.4941 | 299.8065 | 329.9976 | 330.3459 | 334.1948
2434.2542 | 678.3244 | 663.1694 | 598.0637 | 300.33 | 330.5417 | 330.6198 | 334.613
2435.2542 | 677.6699 | 662.4804 | 602.5022 | 302.6258 | 331.0967 | 330.8845 | 335.0059
2436.2542 | 677.8684 | 662.1488 | 601.2335 | 303.7509 | 331.6778 | 331.1744 | 335.4104
2437.2542 | 679.6707 | 663.0602 | 600.3609 | 303.4339 | 332.2583 | 331.443 | 335.7944
2438.2542 | 678.2543 | 665.8927 | 602.0344 | 306.3275 | 332.8461 | 331.7011 | 336.2032
2439.2542 | 677.1752 | 663.5779 | 602.2429 | 306.531 | 333.4374 | 331.9795 | 336.5968
2440.2542 | 677.5816 | 660 | 600.7417 | 307.1486 | 334.0164 | 332.2751 | 337.0241
2441.2542 | 676.8543 | 653.5125 | 600.1676 | 307.3189 | 334.6104 | 332.5117 | 337.4317
2442.2542 | 676.1582 | 653.1775 | 601.0489 | 309.4994 | 335.2162 | 332.7718 | 337.7634
2443.2542 | 675.8111 | 653.0182 | 601.1742 | 310.1596 | 335.8345 | 333.0239 | 338.1698
2444.2542 | 676.7914 | 652.0932 | 602.835 | 311.1548 | 336.4562 | 333.2887 | 338.5945
2445.2542 | 676.0684 | 651.1373 | 605.1951 | 311.7713 | 337.0754 | 333.5541 | 339.001
2446.2542 | 676.6831 | 653.9721 | 606.5629 | 311.8005 | 337.7064 | 333.7831 | 339.4612
2447.2542 | 676.0255 | 653.3963 | 608.378 | 313.6565 | 338.3473 | 334.0348 | 339.8803
2448.2542 | 676.567 | 655.3743 | 611.0628 | 313.7743 | 338.9873 | 334.3408 | 340.2281
2449.2542 | 675.0121 | 662.3388 | 609.9726 | 314.3604 | 339.6284 | 334.5806 | 340.5702
2450.2542 | 674.8545 | 659.1539 | 608.6083 | 314.8312 | 340.281 | 334.8257 | 340.8907
2451.2542 | 676.3571 | 662.9558 | 609.7259 | 315.9671 | 340.9371 | 335.0641 | 341.2564
2452.2542 | 674.2512 | 659.1907 | 610.1155 | 315.3089 | 341.5808 | 335.3243 | 341.5836
2453.2542 | 675.0256 | 661.9948 | 611.1187 | 317.8709 | 342.2196 | 335.5523 | 341.927
2454.2542 | 676.5014 | 662.6819 | 617.8442 | 319.8678 | 342.8692 | 335.8016 | 342.3551
2455.2542 | 676.6137 | 659.6614 | 614.0893 | 320.8459 | 343.5266 | 336.0402 | 342.6393
2456.2542 | 675.3437 | 657.2783 | 612.5982 | 318.906 | 344.2044 | 336.3728 | 342.9525
2457.2542 | 674.4884 | 655.2912 | 610.6534 | 320.3101 | 344.8588 | 336.6036 | 343.2018
2458.2542 | 672.9582 | 650.2408 | 608.1288 | 319.9077 | 345.506 | 336.8082 | 343.5295
2459.2542 | 672.7018 | 649.4698 | 606.1766 | 322.3906 | 346.1609 | 337.0891 | 343.8011
2460.2542 | 672.8638 | 651.0767 | 603.4005 | 322.0839 | 346.8154 | 337.3143 | 344.0742
2461.2542 | 674.6499 | 651.4882 | 612.4493 | 322.6965 | 347.4772 | 337.5423 | 344.3548
2462.2542 | 672.1227 | 648.5262 | 610.0681 | 321.8706 | 348.1326 | 337.7821 | 344.6307
2463.2542 | 671.3823 | 646.508 | 611.1766 | 321.6676 | 348.786 | 338.0027 | 344.8427
2464.2542 | 671.0974 | 649.345 | 610.2664 | 323.9762 | 349.4495 | 338.2626 | 345.0682
2465.2542 | 670.2863 | 649.2302 | 614.9079 | 323.97 | 350.1123 | 338.4453 | 345.2416
2466.2542 | 669.2203 | 651.4786 | 613.3413 | 324.0216 | 350.7671 | 338.7108 | 345.4466
2467.2542 | 672.559 | 653.4951 | 611.6558 | 326.1215 | 351.4153 | 338.8612 | 345.6527
2468.2542 | 674.107 | 652.6904 | 610.6943 | 327.4151 | 352.0606 | 339.0735 | 345.8855
2469.2542 | 675.257 | 653.4013 | 610.9777 | 326.7815 | 352.7044 | 339.43 | 346.1884
2470.2542 | 674.7641 | 652.5719 | 611.156 | 326.9188 | 353.3381 | 339.5867 | 346.5332
2471.2542 | 673.6185 | 651.5217 | 607.1299 | 328.3924 | 353.9769 | 339.8184 | 346.921
2472.2542 | 673.8334 | 649.418 | 606.282 | 329.6823 | 354.6177 | 340.1584 | 347.2409
2473.2542 | 673.64 | 651.3404 | 607.3249 | 331.3822 | 355.2594 | 340.3138 | 347.5514
2474.2542 | 677.6635 | 651.7039 | 606.8907 | 329.9059 | 355.9086 | 340.4952 | 347.808
2475.2542 | 677.3307 | 647.9632 | 606.0288 | 329.8288 | 356.551 | 340.8665 | 348.1636
2476.2542 | 678.9508 | 652.3458 | 603.8381 | 331.6375 | 357.1992 | 341.0176 | 348.4127
2477.2542 | 678.0864 | 648.8623 | 602.7399 | 333.4021 | 357.8469 | 341.265 | 348.6976
2478.2542 | 677.84 | 646.664 | 602.3609 | 332.1199 | 358.481 | 341.5579 | 349.0417
2479.2542 | 675.9076 | 646.4163 | 603.6449 | 333.4635 | 359.1288 | 341.7176 | 349.3906
2480.2542 | 676.7847 | 646.8487 | 602.8813 | 333.7607 | 359.7643 | 341.9608 | 349.6854
2481.2542 | 676.2125 | 645.6072 | 602.0175 | 335.1354 | 360.3749 | 342.1647 | 350.1503
2482.2542 | 676.2264 | 646.5533 | 602.9497 | 334.2646 | 360.9709 | 342.3955 | 350.344
2483.2542 | 679.5881 | 648.5967 | 605.7712 | 335.2724 | 361.5807 | 342.712 | 350.5835
2484.2542 | 678.8506 | 649.7439 | 607.7237 | 335.4704 | 362.1793 | 342.8899 | 350.8912
2485.2542 | 675.7722 | 649.1529 | 610.3571 | 335.7779 | 362.7782 | 343.1182 | 351.2402
2486.2542 | 676.2363 | 647.1296 | 609.2046 | 336.9106 | 363.3612 | 343.3112 | 351.5281
2487.2542 | 675.7183 | 646.8788 | 607.762 | 337.2489 | 363.9312 | 343.4635 | 351.8132
2488.2542 | 678.5924 | 647.7274 | 605.8973 | 338.3118 | 364.5076 | 343.6646 | 352.1106
2489.2542 | 678.4526 | 650.0995 | 603.6903 | 340.5447 | 365.1005 | 343.8482 | 352.2967
2490.2542 | 677.8003 | 649.7229 | 602.4612 | 341.232 | 365.6485 | 344.1855 | 352.6835
2491.2542 | 676.2749 | 649.078 | 601.5532 | 341.0752 | 366.1996 | 344.3477 | 352.8631
2492.2542 | 674.8486 | 646.3495 | 601.7755 | 340.8223 | 366.7377 | 344.4907 | 353.125
2493.2542 | 673.8945 | 644.7087 | 600.7478 | 341.0932 | 367.2584 | 344.7497 | 353.3712
2494.2542 | 673.771 | 645.1433 | 601.2343 | 341.4253 | 367.7832 | 344.9329 | 353.6312
2495.2542 | 675.9438 | 645.497 | 599.6257 | 341.9658 | 368.323 | 345.1511 | 353.8021
2496.2542 | 675.0839 | 647.6772 | 598.468 | 342.9531 | 368.8523 | 345.2769 | 353.9923
2497.2542 | 674.3803 | 646.7958 | 599.9407 | 342.6552 | 369.3719 | 345.5421 | 354.2136
2498.2542 | 671.6271 | 644.9781 | 598.3798 | 344.9454 | 369.8924 | 345.7799 | 354.2541
2499.2542 | 672.2456 | 642.8824 | 596.6703 | 344.4763 | 370.4532 | 345.869 | 354.349
2500.2542 | 671.4447 | 641.9829 | 596.8815 | 345.2668 | 370.9578 | 346.074 | 354.5636
2501.2542 | 673.1596 | 645.2081 | 598.0997 | 345.7867 | 371.4277 | 346.1931 | 354.775
2502.2542 | 675.3039 | 644.1548 | 598.8261 | 345.0896 | 371.9405 | 346.3718 | 354.9692
2503.2542 | 677.7897 | 643.1606 | 598.204 | 346.0555 | 372.4816 | 346.7515 | 355.2592
2504.2542 | 676.8283 | 642.2401 | 597.2325 | 347.4651 | 372.9774 | 346.895 | 355.541
2505.2542 | 675.7817 | 639.9555 | 597.6362 | 347.3423 | 373.4543 | 347.1488 | 355.8867
2506.2542 | 673.9364 | 638.3899 | 592.8521 | 348.1011 | 373.9532 | 347.2856 | 356.1449
2507.2542 | 672.3273 | 641.7705 | 598.2389 | 349.6793 | 374.4108 | 347.5108 | 356.3025
2508.2542 | 671.9331 | 641.8427 | 599.1675 | 348.9565 | 374.906 | 347.6811 | 356.4763
2509.2542 | 670.1038 | 641.1113 | 597.5719 | 349.6386 | 375.3783 | 347.8309 | 356.7472
2510.2542 | 669.9384 | 644.9551 | 600.1679 | 349.3661 | 375.8301 | 348.022 | 356.9144
2511.2542 | 669.675 | 645.0211 | 600.3719 | 350.4774 | 376.2775 | 348.1705 | 357.217
2512.2542 | 669.5556 | 644.8621 | 601.164 | 350.8679 | 376.7666 | 348.385 | 357.461
2513.2542 | 669.8753 | 645.1828 | 601.0283 | 350.6877 | 377.1916 | 348.5061 | 357.7219
2514.2542 | 669.9858 | 646.0177 | 601.4792 | 351.3331 | 377.6218 | 348.6692 | 357.9441
2515.2542 | 669.0576 | 646.4156 | 600.1873 | 353.045 | 378.0777 | 348.9609 | 358.1733
2516.2542 | 669.3326 | 648.7016 | 601.7678 | 352.5856 | 378.5628 | 349.1475 | 358.3576
2517.2542 | 670.0543 | 650.318 | 602.218 | 354.3465 | 378.9956 | 349.2968 | 358.598
2518.2542 | 671.8576 | 649.7564 | 604.7993 | 355.1396 | 379.3972 | 349.4724 | 358.8482
2519.2542 | 673.5641 | 652.283 | 607.2415 | 355.6192 | 379.8099 | 349.6197 | 359.008
2520.2542 | 671.9644 | 650.7057 | 608.3139 | 356.8863 | 380.2465 | 349.784 | 359.2929
2521.2542 | 668.6048 | 648.632 | 608.036 | 355.2943 | 380.6998 | 350.0426 | 359.5194
2522.2542 | 667.8723 | 648.2727 | 608.7562 | 355.9664 | 381.0988 | 350.1862 | 359.7849
2523.2542 | 667.953 | 648.2337 | 608.0639 | 358.1131 | 381.5068 | 350.3264 | 359.9437
2524.2542 | 670.036 | 648.813 | 609.1124 | 358.17 | 381.9576 | 350.6524 | 360.1895
2525.2542 | 667.4281 | 648.2438 | 608.3484 | 359.2042 | 382.4461 | 350.7573 | 360.4853
2526.2542 | 667.0677 | 652.5481 | 609.3135 | 359.0133 | 382.9204 | 351.0518 | 360.7205
2527.2542 | 664.7895 | 650.7218 | 607.6534 | 359.4932 | 383.3303 | 351.2453 | 360.9713
2528.2542 | 668.1161 | 652.2304 | 610.2771 | 360.407 | 383.7847 | 351.3789 | 361.1202
2529.2542 | 670.4784 | 654.2346 | 613.0411 | 361.7629 | 384.329 | 351.6532 | 361.2645
2530.2542 | 671.7727 | 655.76 | 615.0109 | 363.9441 | 384.8005 | 351.8242 | 361.3764
2531.2542 | 670.8147 | 657.8522 | 617.0661 | 364.1892 | 385.1829 | 352.0104 | 361.7383
2532.2542 | 672.5606 | 660.5096 | 619.0598 | 365.3083 | 385.5962 | 352.2817 | 361.9609
2533.2542 | 674.6924 | 660.8845 | 620.3247 | 365.7643 | 386.0625 | 352.5069 | 362.025
2534.2542 | 676.7342 | 664.3123 | 622.4923 | 367.165 | 386.5239 | 352.714 | 362.3721
2535.2542 | 676.5035 | 662.339 | 621.1584 | 368.1207 | 387.1138 | 353.0817 | 362.5098
2536.2542 | 676.0973 | 662.9327 | 621.7254 | 368.9146 | 387.5364 | 353.2717 | 363.0285
2537.2542 | 675.0634 | 663.926 | 623.4418 | 369.3601 | 388.0963 | 353.4933 | 363.3355
2538.2542 | 672.4945 | 660.8905 | 622.0593 | 370.234 | 388.5541 | 353.762 | 363.6287
2539.2542 | 673.7071 | 660.9576 | 619.6613 | 372.2931 | 389.0397 | 353.9499 | 363.8051
2540.2542 | 672.3089 | 660.8112 | 619.2744 | 373.495 | 389.4331 | 354.1142 | 364.1455
2541.2542 | 673.0236 | 661.5506 | 620.2069 | 373.1621 | 389.9894 | 354.3482 | 364.2949
2542.2542 | 672.286 | 658.6703 | 620.9033 | 374.2498 | 390.4076 | 354.552 | 364.3554
2543.2542 | 673.5664 | 658.2797 | 620.6501 | 374.7338 | 390.7922 | 354.8273 | 364.9159
2544.2542 | 672.6237 | 660.544 | 621.9012 | 375.929 | 391.3897 | 355.1091 | 365.2059
2545.2542 | 669.1655 | 658.7929 | 619.6048 | 376.4081 | 391.8605 | 355.2881 | 365.5745
2546.2542 | 667.9179 | 655.5231 | 618.4201 | 376.413 | 392.2333 | 355.6313 | 365.9393
2547.2542 | 665.625 | 653.3125 | 618.4759 | 376.3357 | 392.5792 | 355.9115 | 366.2433
2548.2542 | 667.5177 | 653.5335 | 620.5976 | 376.5063 | 393.2618 | 356.121 | 366.5018
2549.2542 | 666.9754 | 653.0485 | 618.3343 | 375.5489 | 393.6702 | 356.3812 | 366.8113
2550.2542 | 666.4817 | 650.7718 | 616.5015 | 376.6197 | 394.112 | 356.6358 | 367.0746
2551.2542 | 666.6279 | 653.347 | 615.417 | 376.4762 | 394.5119 | 356.7895 | 367.4208
2552.2542 | 665.2856 | 657.0192 | 614.6566 | 376.5004 | 395.0958 | 356.8542 | 367.7747
2553.2542 | 664.364 | 657.6777 | 616.1913 | 377.5853 | 395.4733 | 357.1558 | 367.9672
2554.2542 | 664.4533 | 658.2627 | 619.0723 | 379.7749 | 395.9476 | 357.3565 | 368.3922
2555.2542 | 665.4104 | 659.3781 | 619.4491 | 379.093 | 396.2016 | 357.6557 | 368.6269
2556.2542 | 668.7332 | 661.9921 | 620.1507 | 379.0877 | 396.6193 | 357.7401 | 369.0569
2557.2542 | 668.4954 | 659.7928 | 619.9024 | 379.9319 | 397.2136 | 357.8928 | 369.3601
2558.2542 | 668.568 | 659.7369 | 620.0498 | 380.8102 | 397.6471 | 358.0693 | 369.5437
2559.2542 | 670.145 | 663.5564 | 617.8019 | 382.0433 | 397.9579 | 358.3682 | 369.7252
2560.2542 | 669.1044 | 660.6055 | 619.4397 | 382.9498 | 398.4775 | 358.6291 | 370.1474
2561.2542 | 669.6173 | 661.1035 | 619.3401 | 383.3717 | 398.7334 | 358.8443 | 370.469
2562.2542 | 670.3233 | 662.123 | 621.6664 | 383.7105 | 399.2579 | 359.1802 | 370.3389
2563.2542 | 669.8981 | 659.1233 | 619.6008 | 384.1538 | 399.495 | 359.5826 | 370.4164
2564.2542 | 669.2637 | 658.6181 | 619.4811 | 384.7814 | 400.2388 | 359.8722 | 370.4126
2565.2542 | 668.762 | 655.3582 | 619.6439 | 384.1626 | 400.2597 | 359.7233 | 371.5116
2566.2542 | 666.9383 | 652.9094 | 617.3914 | 381.4753 | 401.1375 | 359.9306 | 371.6077
2567.2542 | 666.2817 | 651.6711 | 615.9733 | 381.8559 | 401.2286 | 360.2153 | 371.8782
2568.2542 | 667.8689 | 654.0789 | 621.4439 | 383.0006 | 401.8809 | 360.262 | 372.0051
2569.2542 | 667.092 | 655.2099 | 632.6299 | 384.8678 | 402.0742 | 360.4466 | 372.2836
2570.2542 | 666.5018 | 656.5122 | 633.9893 | 385.5998 | 402.4238 | 360.0964 | 372.8206
2571.2542 | 667.0153 | 659.1037 | 632.4142 | 385.3008 | 402.8659 | 360.0217 | 373.0735
2572.2542 | 665.3494 | 657.4088 | 629.2572 | 385.9476 | 403.0694 | 359.6625 | 373.0137
2573.2542 | 663.8422 | 655.3371 | 625.2737 | 385.6967 | 403.6062 | 358.9933 | 372.9351
2574.2542 | 666.4239 | 656.9265 | 625.1677 | 387.6763 | 403.9231 | 358.8671 | 373.291
2575.2542 | 668.5433 | 660.7298 | 625.1298 | 387.6814 | 404.3353 | 359.9159 | 373.6011
2576.2542 | 670.5733 | 662.8177 | 629.8165 | 389.1941 | 404.986 | 359.4997 | 373.6015
2577.2542 | 669.6976 | 662.7666 | 631.1319 | 390.8281 | 404.9695 | 359.586 | 373.7732
2578.2542 | 666.9956 | 659.8876 | 628.6476 | 390.6304 | 405.5916 | 359.0926 | 373.3236
2579.2542 | 668.3585 | 658.2707 | 627.4902 | 391.0093 | 405.9454 | 358.2353 | 372.8419
2580.2542 | 671.7502 | 660.1446 | 627.966 | 391.1932 | 406.1678 | 358.1471 | 372.6302
2581.2542 | 669.4468 | 658.7203 | 628.7511 | 391.9303 | 406.1269 | 357.0942 | 372.1982
2582.2542 | 672.6086 | 659.6755 | 628.5921 | 392.9717 | 406.6495 | 355.5675 | 371.6579
2583.2542 | 671.3775 | 657.8887 | 628.6148 | 393.5339 | 406.5716 | 355.1914 | 371.2868
2584.2542 | 668.9081 | 656.2824 | 629.9953 | 392.6255 | 407.6036 | 352.2967 | 370.3056
2585.2542 | 668.8029 | 661.2658 | 629.7916 | 393.6368 | 407.1968 | 349.987 | 369.9736
2586.2542 | 669.4433 | 660.856 | 629.1726 | 393.8724 | 407.8192 | 349.258 | 369.6045
2587.2542 | 667.769 | 658.0197 | 627.5421 | 394.5933 | 407.6701 | 346.8182 | 369.1277
2588.2542 | 666.6231 | 657.4413 | 628.3385 | 395.7343 | 408.2932 | 347.5206 | 369.5388
2589.2542 | 667.7062 | 657.9641 | 628.8522 | 396.822 | 408.0957 | 349.9474 | 370.0551
2590.2542 | 667.6579 | 659.0299 | 628.4797 | 396.7968 | 408.5295 | 350.7648 | 370.7485
2591.2542 | 665.643 | 660.5588 | 630.3173 | 398.4677 | 409.1312 | 353.804 | 372.093
2592.2542 | 667.3998 | 660.5516 | 628.6202 | 399.2325 | 409.4513 | 356.7637 | 373.2095
2593.2542 | 667.2413 | 659.1692 | 626.4823 | 398.9773 | 409.3448 | 358.1274 | 373.1571
2594.2542 | 665.7944 | 657.6148 | 625.9723 | 398.9433 | 409.8018 | 361.0639 | 373.2135
2595.2542 | 666.9217 | 656.9025 | 625.8267 | 398.2242 | 410.1991 | 364.6455 | 375.0929
2596.2542 | 664.8285 | 656.3331 | 624.7916 | 392.6543 | 409.9959 | 365.9903 | 376.2916
2597.2542 | 664.5606 | 663.9779 | 632.1819 | 392.394 | 410.2683 | 366.721 | 375.933
2598.2542 | 665.7542 | 663.3665 | 634.4198 | 385.999 | 410.6981 | 367.5832 | 374.2172
2599.2542 | 665.348 | 661.9989 | 633.942 | 381.458 | 410.678 | 368.968 | 373.2102
2600.2542 | 666.6764 | 662.0839 | 634.7659 | 375.9103 | 410.7768 | 368.6998 | 376.0285
2601.2542 | 667.282 | 661.4445 | 632.1639 | 374.5413 | 410.3954 | 369.3867 | 376.2363
2602.2542 | 668.1127 | 662.2577 | 630.1821 | 375.4711 | 410.9899 | 367.8931 | 377.7511
2603.2542 | 666.1951 | 658.9638 | 627.7864 | 353.4069 | 410.77 | 367.3997 | 378.965
2604.2542 | 665.6539 | 658.6209 | 629.1393 | 358.5135 | 411.1639 | 366.8335 | 379.8104
2605.2542 | 665.8744 | 657.3156 | 629.0605 | 355.5339 | 411.4466 | 363.6381 | 379.4545
2606.2542 | 666.7955 | 657.7202 | 626.9492 | 354.1628 | 411.4748 | 357.8236 | 378.2136
2607.2542 | 670.3588 | 660.0447 | 628.5438 | 363.5357 | 411.8384 | 354.9823 | 377.7137
2608.2542 | 670.0591 | 663.8438 | 634.6992 | 344.0833 | 411.9644 | 353.7035 | 378.2159
2609.2542 | 672.2827 | 665.9956 | 636.0687 | 350.949 | 412.0423 | 352.3142 | 377.7365
2610.2542 | 673.6977 | 666.8738 | 637.2188 | 362.4312 | 412.1644 | 351.3013 | 377.3198
2611.2542 | 675.228 | 666.8762 | 639.8335 | 364.9587 | 412.0086 | 351.9538 | 377.7884
2612.2542 | 676.84 | 668.7027 | 639.6901 | 347.8065 | 412.3012 | 353.5537 | 378.3961
2613.2542 | 677.0634 | 667.6673 | 638.9032 | 350.7213 | 412.5811 | 352.8052 | 377.771
2614.2542 | 677.889 | 667.5495 | 635.4882 | 357.0529 | 412.5036 | 352.9166 | 377.8934
2615.2542 | 677.1987 | 667.9047 | 634.9993 | 366.3895 | 412.6299 | 350.9043 | 378.2287
2616.2542 | 675.9157 | 669.0093 | 634.1042 | 368.3668 | 412.5604 | 349.7546 | 378.572
2617.2542 | 676.2094 | 668.9014 | 634.3538 | 369.4251 | 412.7638 | 349.8587 | 378.8308
2618.2542 | 674.7531 | 667.9789 | 637.1942 | 373.0775 | 412.8392 | 350.082 | 379.0521
2619.2542 | 675.8007 | 667.4768 | 637.9539 | 375.4432 | 413.4105 | 350.1117 | 379.1804
2620.2542 | 675.0102 | 665.764 | 635.69 | 377.5492 | 413.5925 | 348.6374 | 379.0098
2621.2542 | 672.2364 | 663.8722 | 637.3879 | 378.9225 | 413.5938 | 348.4737 | 379.5339
2622.2542 | 669.6458 | 663.1985 | 635.0297 | 381.1652 | 414.1389 | 347.5432 | 379.6687
2623.2542 | 672.9491 | 664.0505 | 634.1803 | 380.956 | 414.361 | 346.3133 | 379.6974
2624.2542 | 673.7568 | 668.8852 | 634.4956 | 385.5678 | 414.7715 | 345.7008 | 380.2422
2625.2542 | 674.782 | 670.9108 | 637.4164 | 403.6415 | 414.6715 | 353.2191 | 377.5294
2626.2542 | 675.152 | 669.4249 | 636.3381 | 408.3489 | 414.9246 | 353.0899 | 376.893
2627.2542 | 674.7363 | 667.1854 | 634.1928 | 409.6712 | 415.1238 | 352.0914 | 377.4045
2628.2542 | 675.6075 | 673.3264 | 636.6625 | 411.9854 | 415.8375 | 351.298 | 377.5802
2629.2542 | 675.6333 | 671.2043 | 637.6282 | 413.692 | 415.9866 | 350.9189 | 377.7644
2630.2542 | 673.2443 | 667.4928 | 635.8625 | 412.2063 | 416.3838 | 351.8734 | 377.1779
2631.2542 | 673.1031 | 664.9223 | 635.8195 | 410.5418 | 416.3426 | 353.7071 | 376.0795
2632.2542 | 674.4675 | 665.9333 | 640.1798 | 412.6771 | 416.7642 | 355.3647 | 376.2943
2633.2542 | 677.6227 | 666.8905 | 639.2576 | 415.4603 | 416.8707 | 356.4995 | 377.0431
2634.2542 | 677.5654 | 666.403 | 637.6478 | 414.1044 | 417.0967 | 356.9232 | 376.5254
2635.2542 | 673.8062 | 664.7241 | 634.819 | 413.5662 | 417.2749 | 357.7851 | 376.6767
2636.2542 | 672.4942 | 664.341 | 636.3367 | 415.5895 | 417.4704 | 357.5849 | 375.6847
2637.2542 | 675.4515 | 666.3634 | 638.1396 | 417.5944 | 417.7555 | 357.3698 | 375.6579
2638.2542 | 675.2009 | 664.4619 | 636.3237 | 419.1161 | 417.8787 | 357.0466 | 375.2822
2639.2542 | 675.0442 | 663.1607 | 635.5726 | 421.4385 | 418.2579 | 357.8514 | 375.5385
2640.2542 | 674.5878 | 661.8162 | 634.5374 | 423.1791 | 418.3236 | 357.2876 | 374.95
2641.2542 | 674.7466 | 661.5699 | 632.8486 | 421.8593 | 418.4422 | 356.7549 | 373.2906
2642.2542 | 674.3538 | 664.0813 | 631.5516 | 431.7067 | 419.0136 | 365.8222 | 381.3251
2643.2542 | 676.9403 | 664.5177 | 630.7591 | 432.7204 | 419.1848 | 365.4697 | 379.3577
2644.2542 | 677.6148 | 664.5656 | 630.3592 | 432.2338 | 419.4035 | 365.2565 | 379.8865
2645.2542 | 677.1586 | 664.7442 | 630.0443 | 434.8261 | 419.5208 | 365.2818 | 380.2699
2646.2542 | 675.0043 | 661.2355 | 628.1 | 436.0406 | 419.805 | 365.6983 | 380.8542
2647.2542 | 674.3457 | 658.1537 | 627.6181 | 436.9339 | 420.3922 | 365.5929 | 381.3297
2648.2542 | 673.1067 | 658.1081 | 627.1129 | 437.5705 | 420.4019 | 365.3411 | 381.7035
2649.2542 | 673.2909 | 657.7732 | 626.3221 | 437.755 | 420.8736 | 364.7609 | 381.6283
2650.2542 | 674.4617 | 658.0885 | 626.0426 | 439.0853 | 420.742 | 364.7598 | 382.1763
2651.2542 | 673.2394 | 663.5022 | 628.2178 | 439.3666 | 421.2179 | 364.9015 | 382.2273
2652.2542 | 673.1793 | 661.8292 | 630.7215 | 446.8518 | 421.8408 | 380.9539 | 399.7525
2653.2542 | 672.9649 | 660.0198 | 628.1729 | 448.7891 | 421.8936 | 381.0324 | 400.1198
2654.2542 | 673.4395 | 660.5815 | 629.4828 | 449.7983 | 422.0684 | 381.4595 | 400.5455
2655.2542 | 673.9321 | 660.5671 | 630.2268 | 451.1891 | 422.4447 | 381.7396 | 400.9162
2656.2542 | 671.8602 | 659.471 | 628.8262 | 452.0767 | 422.6445 | 382.2325 | 401.3784
2657.2542 | 671.7447 | 658.3361 | 628.4738 | 452.2551 | 422.7645 | 382.2182 | 401.6273
2658.2542 | 673.3172 | 661.2644 | 630.2275 | 453.8643 | 423.1559 | 382.6425 | 402.4841
2659.2542 | 675.0192 | 660.7936 | 628.6875 | 453.5454 | 423.058 | 383.0451 | 402.8957
2660.2542 | 674.0833 | 659.8015 | 627.7529 | 454.001 | 423.337 | 383.6233 | 403.3442
2661.2542 | 673.794 | 659.8307 | 630.6771 | 454.7462 | 423.5179 | 383.8276 | 403.7196
2662.2542 | 672.0493 | 659.1069 | 631.6581 | 456.0864 | 423.6225 | 384.2567 | 404.2697
2663.2542 | 670.4278 | 658.9046 | 631.5 | 456.2162 | 424.7577 | 384.6268 | 404.5306
2664.2542 | 670.5613 | 656.7266 | 630.1777 | 458.0354 | 424.3429 | 385.0304 | 405.1181
2665.2542 | 671.3371 | 661.2846 | 629.1309 | 458.7745 | 426.0338 | 385.3275 | 405.7119
2666.2542 | 670.5623 | 662.0733 | 632.2183 | 459.2971 | 427.8479 | 385.6414 | 406.2351
2667.2542 | 673.6395 | 664.6113 | 634.0061 | 461.0937 | 430.5536 | 386.1066 | 406.5966
2668.2542 | 674.2805 | 663.8817 | 632.1838 | 461.5196 | 433.5377 | 386.5924 | 406.8911
2669.2542 | 673.528 | 662.4967 | 632.6389 | 462.2523 | 436.0902 | 386.9774 | 407.6383
2670.2542 | 672.9881 | 663.1112 | 631.2811 | 463.4831 | 438.2991 | 387.3434 | 408.2305
2671.2542 | 670.3864 | 660.7154 | 629.9454 | 463.7351 | 440.3285 | 388.0715 | 408.7605
2672.2542 | 670.787 | 659.6376 | 628.4087 | 466.1994 | 442.0426 | 388.5712 | 409.4956
2673.2542 | 670.9231 | 658.6901 | 629.3495 | 465.4471 | 443.8056 | 389.1918 | 410.0936
2674.2542 | 670.4674 | 660.3469 | 629.4988 | 467.3451 | 445.5036 | 389.316 | 410.7583
2675.2542 | 673.8781 | 661.3843 | 627.9448 | 468.2101 | 446.8927 | 389.624 | 411.1827
2676.2542 | 674.0781 | 662.8564 | 630.5715 | 468.9941 | 448.1898 | 390.4085 | 411.7727
2677.2542 | 674.0959 | 665.9823 | 634.0952 | 470.7087 | 449.3007 | 390.5489 | 412.0947
2678.2542 | 673.269 | 666.5942 | 634.5037 | 471.7443 | 450.4744 | 391.2039 | 412.336
2679.2542 | 673.1228 | 670.3593 | 635.4248 | 474.0613 | 451.7241 | 391.8293 | 412.6905
2680.2542 | 675.7242 | 673.3254 | 639.9504 | 475.9607 | 452.7964 | 392.3583 | 413.527
2681.2542 | 675.1934 | 674.5285 | 640.198 | 478.6965 | 453.9346 | 392.9287 | 413.8694
2682.2542 | 674.1658 | 672.5832 | 639.0328 | 479.801 | 454.6599 | 393.1481 | 414.4748
2683.2542 | 671.8626 | 670.7111 | 637.7299 | 479.8434 | 455.7545 | 393.3735 | 414.6066
2684.2542 | 672.2523 | 668.2727 | 639.3495 | 481.0548 | 456.663 | 394.4176 | 415.709
2685.2542 | 673.1901 | 666.9649 | 638.74 | 481.1638 | 457.4161 | 394.259 | 415.4332
2686.2542 | 672.0672 | 665.2502 | 637.1784 | 480.2865 | 458.1969 | 394.8992 | 416.38
2687.2542 | 672.7848 | 666.4669 | 637.883 | 480.9601 | 459.0909 | 395.71 | 416.7997
2688.2542 | 675.2165 | 672.2473 | 639.0303 | 482.6851 | 459.7692 | 395.7062 | 417.332
2689.2542 | 672.9992 | 670.8094 | 638.5106 | 484.7041 | 460.6278 | 396.5253 | 418.6134
2690.2542 | 669.4847 | 669.0088 | 638.5283 | 484.7951 | 461.3231 | 397.1999 | 418.6795
2691.2542 | 670.7591 | 670.6055 | 640.8451 | 485.3447 | 462.3112 | 397.4274 | 418.491
2692.2542 | 673.705 | 671.951 | 640.0958 | 486.7245 | 463.0557 | 397.8416 | 419.4233
2693.2542 | 674.7691 | 672.0104 | 637.4349 | 488.2228 | 463.8448 | 398.9463 | 420.2992
2694.2542 | 673.8658 | 669.421 | 636.0438 | 488.7271 | 464.2773 | 399.1561 | 420.8843
2695.2542 | 673.8424 | 669.9845 | 636.1009 | 489.4975 | 464.8907 | 399.2751 | 420.9104
2696.2542 | 675.4951 | 668.4809 | 637.0825 | 489.9908 | 465.3617 | 400.2674 | 421.5039
2697.2542 | 672.9248 | 663.9172 | 635.3204 | 489.1326 | 465.7952 | 400.1452 | 422.2061
2698.2542 | 673.089 | 665.0262 | 641.1735 | 488.5887 | 466.315 | 401.151 | 422.9122
2699.2542 | 673.9055 | 666.209 | 640.5269 | 490.0285 | 466.485 | 400.8768 | 422.8407
2700.2542 | 675.6802 | 668.1041 | 639.4086 | 490.7883 | 466.6058 | 402.2802 | 423.7393
2701.2542 | 675.3316 | 667.2816 | 639.7837 | 490.9015 | 466.326 | 402.0668 | 424.1043
2702.2542 | 675.0967 | 669.0105 | 639.0911 | 491.2016 | 466.6362 | 402.4617 | 424.2199
2703.2542 | 674.6704 | 668.0901 | 637.7007 | 493.1855 | 466.8975 | 403.0722 | 424.5752
2704.2542 | 674.2337 | 670.3285 | 641.254 | 493.6561 | 467.4246 | 403.5772 | 425.6275
2705.2542 | 675.5109 | 672.5829 | 641.9844 | 493.9158 | 467.773 | 403.9044 | 426.0216
2706.2542 | 677.5015 | 672.0002 | 641.5872 | 495.3111 | 468.2979 | 403.9317 | 426.3604
2707.2542 | 678.3444 | 672.5839 | 638.7303 | 495.3313 | 468.756 | 404.9398 | 427.1364
2708.2542 | 678.8917 | 674.0085 | 640.2137 | 495.3807 | 468.9876 | 405.3363 | 426.7204
2709.2542 | 678.9549 | 674.4529 | 642.8584 | 497.142 | 469.5728 | 405.4422 | 426.7286
2710.2542 | 679.0641 | 672.5259 | 640.8962 | 498.3173 | 469.7662 | 406.03 | 427.4573
2711.2542 | 679.6201 | 673.7748 | 641.9073 | 499.6392 | 470.196 | 406.5348 | 428.2353
2712.2542 | 680.0713 | 673.2432 | 640.9654 | 501.2042 | 470.6972 | 407.2184 | 428.4312
2713.2542 | 680.0359 | 672.2311 | 640.3509 | 502.0475 | 470.9106 | 407.6553 | 429.2502
2714.2542 | 679.5565 | 672.19 | 643.1665 | 502.4591 | 471.4268 | 408.1125 | 429.7875
2715.2542 | 678.5334 | 672.0302 | 643.7081 | 503.1236 | 472.2561 | 408.2635 | 429.9493
2716.2542 | 677.6264 | 671.596 | 644.4969 | 503.7137 | 472.9045 | 408.7353 | 429.3012
2717.2542 | 678.7558 | 672.4196 | 645.345 | 504.4 | 473.3447 | 408.6466 | 430.2757
2718.2542 | 677.4526 | 670.7804 | 644.9238 | 504.2148 | 473.8975 | 408.7597 | 429.7395
2719.2542 | 675.3767 | 670.0057 | 644.9922 | 506.2175 | 474.7829 | 408.7739 | 430.4668
2720.2542 | 674.1349 | 670.4568 | 647.3612 | 505.8405 | 475.5776 | 409.8655 | 431.5153
2721.2542 | 673.4936 | 670.8532 | 647.8436 | 505.786 | 475.9353 | 409.896 | 432.1705
2722.2542 | 672.7928 | 670.6648 | 648.1395 | 506.7999 | 476.9301 | 410.8021 | 433.1729
2723.2542 | 671.9079 | 672.4963 | 648.4633 | 506.608 | 477.4342 | 410.6427 | 432.3373
2724.2542 | 672.0451 | 672.5281 | 648.5997 | 507.9882 | 478.125 | 410.8796 | 433.3554
2725.2542 | 671.5183 | 673.7713 | 650.2451 | 509.5738 | 478.3393 | 411.5636 | 433.9224
2726.2542 | 673.4139 | 677.2655 | 651.2729 | 510.2276 | 478.3674 | 411.8521 | 434.9041
2727.2542 | 671.1765 | 675.3198 | 649.9393 | 510.4313 | 478.678 | 412.9489 | 435.9101
2728.2542 | 672.0719 | 677.2796 | 650.9245 | 511.9379 | 478.8738 | 412.2773 | 434.1111
2729.2542 | 672.8857 | 680.1776 | 652.7176 | 513.8059 | 479.3496 | 414.083 | 436.1598
2730.2542 | 675.519 | 681.7066 | 653.6447 | 515.9036 | 479.8808 | 413.7157 | 435.8974
2731.2542 | 676.3083 | 680.8554 | 652.2722 | 518.1544 | 479.929 | 413.7785 | 436.4656
2732.2542 | 679.9231 | 682.4005 | 652.4592 | 519.3085 | 480.2787 | 414.4501 | 436.8627
2733.2542 | 680.5377 | 683.1564 | 651.1479 | 520.1814 | 480.5136 | 414.1147 | 436.7312
2734.2542 | 684.7059 | 683.5603 | 651.0004 | 521.7753 | 480.8376 | 414.5425 | 437.4799
2735.2542 | 684.6932 | 685.6086 | 648.4345 | 524.0525 | 481.2083 | 415.0095 | 437.1466
2736.2542 | 684.0958 | 683.5951 | 647.9547 | 523.2155 | 481.6611 | 415.237 | 439.0192
2737.2542 | 686.4446 | 684.1393 | 648.6723 | 524.0037 | 481.6802 | 415.5848 | 439.3483
2738.2542 | 685.5841 | 682.0418 | 649.0268 | 524.874 | 481.8462 | 415.0924 | 438.2318
2739.2542 | 685.6448 | 681.6341 | 648.906 | 526.4553 | 482.3325 | 415.609 | 438.8784
2740.2542 | 685.8776 | 685.5441 | 651.8017 | 527.1789 | 482.2215 | 415.9403 | 438.9688
2741.2542 | 685.8152 | 684.3602 | 653.4344 | 528.3962 | 482.7399 | 416.4298 | 440.1209
2742.2542 | 686.7785 | 684.4936 | 652.0877 | 529.1319 | 483.3413 | 417.6369 | 442.2184
2743.2542 | 687.0938 | 685.762 | 657.0691 | 530.0662 | 483.7712 | 417.1291 | 441.6814
2744.2542 | 685.2079 | 685.2547 | 664.3048 | 530.0453 | 484.1335 | 417.0865 | 441.5874
2745.2542 | 684.7707 | 688.2217 | 666.4309 | 532.128 | 484.7092 | 417.5276 | 441.9988
2746.2542 | 685.5725 | 689.6232 | 668.4188 | 533.172 | 484.6393 | 417.9006 | 442.7254
2747.2542 | 686.5708 | 693.0683 | 666.6505 | 533.874 | 485.4234 | 417.7597 | 442.7888
2748.2542 | 685.4754 | 695.6157 | 665.6439 | 535.2531 | 485.8817 | 417.6099 | 441.909
2749.2542 | 686.2603 | 696.4533 | 668.3512 | 535.7065 | 486.2453 | 418.7461 | 443.4846
2750.2542 | 687.2642 | 693.9529 | 666.2858 | 536.5835 | 486.6852 | 419.0615 | 443.7536
2751.2542 | 687.7748 | 696.3877 | 669.1521 | 538.0727 | 486.964 | 419.1893 | 444.3535
2752.2542 | 689.4236 | 695.4687 | 667.9216 | 538.8413 | 487.2147 | 419.2252 | 444.3471
2753.2542 | 690.8223 | 698.0318 | 667.1191 | 540.3086 | 487.5756 | 420.0142 | 444.4411
2754.2542 | 691.6506 | 697.8815 | 667.4943 | 542.5476 | 488.0295 | 420.8058 | 445.4659
2755.2542 | 691.21 | 696.4465 | 665.0226 | 543.8772 | 488.3466 | 420.3764 | 445.5994
2756.2542 | 691.1064 | 695.1488 | 664.1318 | 545.0544 | 488.2722 | 420.4042 | 445.4638
2757.2542 | 690.9016 | 693.6567 | 662.5008 | 545.3344 | 488.2787 | 420.7226 | 445.0503
2758.2542 | 690.9275 | 693.0165 | 660.9015 | 545.6959 | 488.927 | 421.1126 | 445.5788
2759.2542 | 691.3109 | 696.5601 | 663.196 | 546.022 | 489.5124 | 421.7581 | 446.1417
2760.2542 | 691.3981 | 696.0765 | 662.8087 | 546.6447 | 490.1479 | 421.9629 | 447.6263
2761.2542 | 691.1918 | 693.8971 | 659.7263 | 549.1022 | 490.2386 | 422.4465 | 447.3436
2762.2542 | 692.195 | 692.6446 | 658.709 | 550.6265 | 489.8825 | 421.9587 | 447.8092
2763.2542 | 690.9641 | 692.4781 | 657.4062 | 551.5997 | 489.9863 | 422.2903 | 447.9426
2764.2542 | 692.1396 | 694.6064 | 656.7125 | 552.7494 | 490.5984 | 422.6268 | 448.6604
2765.2542 | 692.2911 | 694.8221 | 656.7344 | 553.3848 | 491.2374 | 422.6144 | 449.2833
2766.2542 | 692.3104 | 692.6512 | 655.5689 | 553.2407 | 491.0497 | 423.3315 | 449.5705
2767.2542 | 690.99 | 693.2018 | 658.3503 | 552.9325 | 491.2318 | 423.3856 | 449.9272
2768.2542 | 690.6597 | 694.2338 | 657.8152 | 554.7722 | 491.0545 | 422.7657 | 449.9062
2769.2542 | 690.2392 | 695.7163 | 656.8472 | 555.1712 | 490.935 | 422.6455 | 449.7535
2770.2542 | 692.326 | 695.8115 | 656.0043 | 555.176 | 491.7113 | 423.2655 | 449.7073
2771.2542 | 689.2992 | 693.3037 | 657.1949 | 555.8139 | 491.9008 | 424.0499 | 451.0194
2772.2542 | 687.2257 | 693.5868 | 660.745 | 556.6268 | 492.3494 | 423.7116 | 450.5054
2773.2542 | 687.621 | 695.3156 | 662.0121 | 558.3447 | 492.8507 | 424.0731 | 450.4854
2774.2542 | 689.2732 | 696.2168 | 661.3592 | 559.1811 | 493.6419 | 425.0007 | 451.0198
2775.2542 | 689.7855 | 696.7213 | 660.7661 | 559.912 | 493.6436 | 424.5996 | 450.8551
2776.2542 | 690.1275 | 699.5754 | 662.6842 | 562.4313 | 494.332 | 424.6803 | 452.1353
2777.2542 | 692.642 | 701.1963 | 664.7943 | 563.9863 | 494.7052 | 424.8454 | 452.0862
2778.2542 | 693.4159 | 699.8741 | 664.6725 | 563.8482 | 494.9668 | 425.4039 | 451.7215
2779.2542 | 692.417 | 699.3233 | 663.3946 | 565.1076 | 495.0816 | 426.3403 | 452.4853
2780.2542 | 692.2335 | 697.8494 | 661.7187 | 566.6167 | 494.9431 | 425.7397 | 452.4687
2781.2542 | 690.1353 | 698.0432 | 661.6872 | 566.777 | 495.2261 | 426.0742 | 452.4489
2782.2542 | 689.7789 | 695.0935 | 664.2781 | 566.887 | 495.291 | 426.661 | 452.9266
2783.2542 | 691.1484 | 696.5653 | 661.6742 | 567.5428 | 495.5438 | 426.1868 | 453.4406
2784.2542 | 693.2643 | 702.5578 | 667.3807 | 569.3371 | 495.3742 | 426.5758 | 453.6163
2785.2542 | 694.3438 | 703.6891 | 668.8923 | 571.1039 | 495.8653 | 426.0881 | 454.0804
2786.2542 | 694.3288 | 704.355 | 669.5571 | 572.5764 | 496.0062 | 426.8918 | 454.9222
2787.2542 | 693.5851 | 704.6743 | 668.1939 | 573.7758 | 496.3166 | 426.9111 | 454.8856
2788.2542 | 693.7597 | 706.6466 | 667.8756 | 574.6285 | 496.9526 | 427.7057 | 455.5187
2789.2542 | 693.8153 | 704.042 | 665.1247 | 575.5256 | 497.4098 | 427.4522 | 457.1296
2790.2542 | 694.5606 | 702.9097 | 669.2653 | 576.1542 | 497.4443 | 427.6728 | 455.9257
2791.2542 | 694.8665 | 702.6337 | 673.6045 | 576.983 | 497.9089 | 427.9526 | 455.7126
2792.2542 | 695.7766 | 703.5627 | 673.8174 | 577.5901 | 498.5348 | 428.073 | 456.3535
2793.2542 | 696.2094 | 703.521 | 672.1611 | 578.4644 | 498.8643 | 427.9227 | 455.8642
2794.2542 | 695.0055 | 702.9679 | 673.8115 | 579.5768 | 499.3625 | 428.1376 | 457.7077
2795.2542 | 693.1282 | 700.8299 | 672.5792 | 579.6053 | 499.9644 | 428.8707 | 457.9904
2796.2542 | 693.4489 | 698.6156 | 669.9692 | 580.3522 | 500.4749 | 428.3836 | 458.5624
2797.2542 | 695.3381 | 696.4064 | 666.2183 | 579.8419 | 500.7252 | 428.3507 | 457.5605
2798.2542 | 694.9659 | 695.6053 | 664.9892 | 581.4857 | 501.1588 | 428.6526 | 458.7617
2799.2542 | 694.979 | 696.316 | 664.885 | 582.1059 | 501.4497 | 428.6848 | 458.2348
2800.2542 | 694.6353 | 696.2846 | 664.8382 | 582.1418 | 501.5505 | 428.5681 | 459.5728
2801.2542 | 693.1246 | 695.044 | 663.3343 | 582.161 | 502.0156 | 428.9394 | 459.095
2802.2542 | 692.6191 | 693.9428 | 664.1533 | 581.9892 | 502.1968 | 429.622 | 456.5175
2803.2542 | 691.9256 | 693.568 | 662.917 | 582.5651 | 501.7812 | 429.6144 | 456.825
2804.2542 | 692.4083 | 693.7015 | 661.1968 | 583.6867 | 501.7196 | 429.5186 | 458.0218
2805.2542 | 693.5564 | 697.464 | 663.4396 | 585.0109 | 501.8787 | 429.5232 | 458.2695
2806.2542 | 693.369 | 698.065 | 666.704 | 585.6381 | 502.3286 | 429.7884 | 459.1217
2807.2542 | 693.0899 | 696.7845 | 664.139 | 586.3528 | 502.0878 | 429.5081 | 458.9655
2808.2542 | 692.8671 | 697.1191 | 663.0005 | 587.5797 | 502.1724 | 429.3992 | 459.0908
2809.2542 | 693.2607 | 698.017 | 663.3552 | 587.3824 | 502.8243 | 430.2806 | 460.3755
2810.2542 | 693.1991 | 698.6505 | 664.7027 | 587.4307 | 503.229 | 430.5199 | 460.4597
2811.2542 | 690.805 | 697.9763 | 666.0747 | 587.4718 | 503.077 | 430.3899 | 461.3223
2812.2542 | 687.4836 | 696.6138 | 665.6917 | 588.6144 | 503.3833 | 430.7399 | 461.6068
2813.2542 | 689.2437 | 695.2482 | 664.7973 | 588.8576 | 503.3271 | 431.0349 | 462.1122
2814.2542 | 690.4306 | 694.7329 | 663.7998 | 588.9046 | 503.6196 | 431.5524 | 462.1406
2815.2542 | 689.2318 | 695.001 | 663.9521 | 589.4046 | 503.7622 | 432.0802 | 464.0807
2816.2542 | 691.1462 | 701.2503 | 665.7484 | 590.6085 | 503.962 | 432.1751 | 465.0574
2817.2542 | 694.4569 | 702.6053 | 665.7861 | 592.9313 | 503.9767 | 431.486 | 463.9944
2818.2542 | 696.4194 | 703.1436 | 664.4394 | 594.3696 | 503.9252 | 431.8084 | 464.8652
2819.2542 | 697.0611 | 703.0414 | 664.9542 | 596.0045 | 503.788 | 432.537 | 465.1418
2820.2542 | 694.3006 | 701.9518 | 665.4976 | 596.8705 | 504.8337 | 432.5655 | 466.0901
2821.2542 | 694.7124 | 700.9769 | 665.94 | 596.8437 | 505.5808 | 433.2171 | 466.5731
2822.2542 | 691.7636 | 696.1682 | 663.3752 | 597.2357 | 505.4104 | 432.5152 | 468.6667
2823.2542 | 688.3772 | 692.9683 | 661.6881 | 597.9514 | 505.2317 | 432.7917 | 467.974
2824.2542 | 687.6018 | 693.3897 | 663.7544 | 597.8744 | 505.5297 | 433.6445 | 470.249
2825.2542 | 687.4692 | 694.1529 | 667.0225 | 597.7658 | 505.1855 | 433.6658 | 469.676
2826.2542 | 688.3518 | 696.4066 | 667.8217 | 597.2501 | 505.9328 | 433.6215 | 469.5336
2827.2542 | 689.2871 | 695.2152 | 668.492 | 597.5384 | 506.305 | 434.2452 | 469.4436
2828.2542 | 689.8431 | 694.7964 | 666.9336 | 597.1878 | 506.2478 | 434.741 | 469.8799
2829.2542 | 691.524 | 694.9708 | 663.3747 | 597.0778 | 506.3179 | 435.2655 | 469.0441
2830.2542 | 691.2722 | 692.1711 | 662.3209 | 596.5269 | 506.445 | 435.907 | 470.6348
2831.2542 | 690.7641 | 692.7669 | 661.6329 | 596.69 | 506.8105 | 435.9334 | 471.1673
2832.2542 | 692.4358 | 693.7188 | 661.5136 | 596.4075 | 506.4746 | 436.0603 | 471.6324
2833.2542 | 691.5742 | 695.0115 | 662.1136 | 597.5691 | 506.4747 | 436.753 | 472.9414
2834.2542 | 689.9743 | 696.148 | 665.8317 | 598.6034 | 506.9902 | 436.8062 | 472.4613
2835.2542 | 690.2714 | 697.7757 | 666.4178 | 598.5281 | 506.9637 | 436.7204 | 472.8673
2836.2542 | 691.3186 | 699.3446 | 666.1398 | 599.4162 | 507.2781 | 436.9659 | 472.9391
2837.2542 | 691.4321 | 698.3179 | 664.7302 | 600.1181 | 507.3492 | 437.3108 | 474.0155
2838.2542 | 693.9856 | 697.3733 | 664.1941 | 599.9165 | 507.24 | 437.4561 | 473.7633
2839.2542 | 694.1615 | 697.0887 | 664.8976 | 600.2837 | 507.1459 | 437.9598 | 474.7643
2840.2542 | 693.5436 | 693.4401 | 662.4928 | 599.3261 | 506.6358 | 438.1578 | 474.5836
2841.2542 | 695.8055 | 693.8426 | 664.6068 | 599.4878 | 506.5169 | 438.3237 | 475.5695
2842.2542 | 695.946 | 692.5265 | 663.4751 | 599.971 | 506.7604 | 438.3972 | 475.3407
2843.2542 | 694.1204 | 692.9072 | 664.2279 | 601.3184 | 506.4368 | 438.9054 | 477.2836
2844.2542 | 693.4471 | 692.6952 | 663.2669 | 602.7766 | 505.9929 | 438.4582 | 478.2697
2845.2542 | 693.9503 | 693.8337 | 662.3247 | 602.949 | 506.4443 | 438.9154 | 479.0284
2846.2542 | 694.994 | 691.6831 | 660.1861 | 603.1644 | 506.3669 | 439.0043 | 479.7932
2847.2542 | 694.5943 | 689.1369 | 658.3869 | 603.75 | 506.6672 | 438.9394 | 479.7578
2848.2542 | 694.4698 | 688.3819 | 658.5194 | 602.6378 | 506.8203 | 439.3768 | 479.6343
2849.2542 | 694.3225 | 690.4973 | 658.7978 | 602.2219 | 506.4765 | 440.1126 | 480.7823
2850.2542 | 695.6059 | 693.0676 | 659.6473 | 603.5931 | 506.7876 | 439.9947 | 480.1868
2851.2542 | 692.5668 | 693.977 | 659.1659 | 604.0496 | 506.728 | 440.6252 | 480.8138
2852.2542 | 691.9777 | 694.494 | 661.3542 | 604.5274 | 507.0651 | 440.8179 | 480.7279
2853.2542 | 693.69 | 694.2297 | 662.8099 | 603.631 | 506.8731 | 441.1811 | 481.345
2854.2542 | 695.6846 | 695.8458 | 664.0833 | 605.3406 | 507.3762 | 441.6851 | 482.0335
2855.2542 | 693.8273 | 697.4279 | 669.0139 | 606.5375 | 507.7017 | 442.2101 | 482.0762
2856.2542 | 696.9618 | 696.7068 | 665.5622 | 606.7092 | 507.7458 | 442.3331 | 482.0391
2857.2542 | 697.1875 | 696.7489 | 665.3674 | 607.1847 | 507.9269 | 442.2621 | 482.2923
2858.2542 | 694.6774 | 696.2635 | 663.9738 | 607.272 | 507.8931 | 442.5259 | 482.4041
2859.2542 | 693.3883 | 698.6909 | 665.5892 | 607.8315 | 507.9162 | 442.5778 | 483.3187
2860.2542 | 693.3982 | 699.8092 | 664.5316 | 608.3021 | 508.2393 | 442.9611 | 483.2223
2861.2542 | 695.8017 | 700.9948 | 665.0419 | 607.6937 | 507.5989 | 442.9675 | 483.9946
2862.2542 | 694.5048 | 701.673 | 666.8896 | 608.9737 | 508.6975 | 443.5523 | 484.4116
2863.2542 | 698.7803 | 705.9953 | 670.4461 | 609.9792 | 509.005 | 443.7419 | 484.9845
2864.2542 | 700.7969 | 706.1279 | 668.4481 | 612.5127 | 509.2371 | 444.2144 | 485.4139
2865.2542 | 701.9911 | 703.7998 | 666.4678 | 612.235 | 509.4579 | 445.0427 | 486.0681
2866.2542 | 701.1662 | 703.9116 | 665.7922 | 611.9568 | 509.207 | 444.7483 | 486.3603
2867.2542 | 700.6988 | 699.7747 | 664.2056 | 611.1118 | 509.2765 | 445.1411 | 486.6272
2868.2542 | 700.8723 | 698.4478 | 665.204 | 609.8993 | 509.0854 | 445.4473 | 485.7307
2869.2542 | 700.2136 | 700.178 | 665.7622 | 610.8459 | 508.8112 | 445.6548 | 486.9018
2870.2542 | 697.5422 | 698.6212 | 664.9107 | 609.9128 | 508.5562 | 445.7905 | 487.7749
2871.2542 | 695.2474 | 696.4755 | 664.4925 | 609.8744 | 508.4067 | 446.1859 | 488.2572
2872.2542 | 695.1396 | 695.6458 | 662.5103 | 608.9595 | 508.1915 | 446.4018 | 487.5695
2873.2542 | 695.6261 | 697.3154 | 666.2816 | 609.8078 | 508.477 | 445.9958 | 487.8429
2874.2542 | 694.4833 | 695.5213 | 666.1807 | 609.4242 | 508.8813 | 446.5031 | 488.6439
2875.2542 | 695.032 | 695.2162 | 665.7504 | 608.7585 | 509.253 | 446.727 | 489.3252
2876.2542 | 697.871 | 694.7037 | 665.4042 | 608.7187 | 508.8951 | 446.8045 | 489.2694
2877.2542 | 699.8642 | 694.5817 | 665.6438 | 609.1036 | 509.5226 | 447.0227 | 489.5956
2878.2542 | 699.6275 | 692.9369 | 663.4616 | 609.1918 | 509.4154 | 447.1732 | 490.1265
2879.2542 | 696.7028 | 691.4777 | 666.9334 | 608.6471 | 509.6254 | 447.3973 | 490.3235
2880.2542 | 697.7936 | 692.5606 | 669.4648 | 608.4417 | 509.3076 | 447.8009 | 491.0512
2881.2542 | 696.505 | 693.0236 | 667.6481 | 608.077 | 509.7159 | 448.1931 | 490.1483
2882.2542 | 694.8203 | 693.5129 | 666.4958 | 607.0281 | 509.7551 | 448.0555 | 490.9387
2883.2542 | 694.1832 | 696.3444 | 672.6872 | 607.3415 | 509.9674 | 448.0005 | 491.0649
2884.2542 | 693.6251 | 697.75 | 672.518 | 607.8172 | 509.8429 | 448.5194 | 491.6196
2885.2542 | 695.2168 | 697.4482 | 671.1756 | 608.6869 | 509.9956 | 449.0409 | 492.2926
2886.2542 | 696.0978 | 696.1546 | 670.7655 | 609.2662 | 510.4935 | 449.7824 | 492.5822
2887.2542 | 697.5436 | 694.7471 | 668.1407 | 608.929 | 510.3745 | 449.4218 | 493.1703
2888.2542 | 696.2627 | 689.5088 | 664.2246 | 607.6494 | 510.1426 | 449.1739 | 493.5659
2889.2542 | 696.8099 | 688.4574 | 663.3733 | 606.0576 | 509.8342 | 449.3713 | 493.536
2890.2542 | 697.0455 | 688.025 | 663.5181 | 606.7072 | 510.0093 | 449.4405 | 493.5547
2891.2542 | 696.7725 | 685.1301 | 661.2549 | 604.8167 | 510.537 | 449.7565 | 493.5861
2892.2542 | 697.7735 | 686.1039 | 662.2521 | 604.3861 | 510.926 | 449.7026 | 493.5565
2893.2542 | 698.6096 | 686.734 | 660.4034 | 605.0809 | 511.0292 | 449.9348 | 493.5028
2894.2542 | 697.5581 | 688.2351 | 664.3184 | 606.0199 | 510.7984 | 449.8075 | 494.1156
2895.2542 | 698.4959 | 690.9914 | 662.7588 | 606.3943 | 510.7208 | 449.713 | 494.3211
2896.2542 | 698.2166 | 688.5348 | 661.1587 | 605.5171 | 510.9716 | 450.4301 | 494.2224
2897.2542 | 697.6156 | 690.1439 | 661.4134 | 605.6978 | 510.9129 | 451.3251 | 495.1098
2898.2542 | 697.3819 | 691.0258 | 661.5448 | 605.8031 | 511.4002 | 451.3875 | 495.3115
2899.2542 | 696.9245 | 690.1124 | 659.4517 | 605.2868 | 511.2993 | 451.7351 | 495.9756
2900.2542 | 696.3864 | 688.9758 | 658.0026 | 605.5695 | 511.261 | 451.5904 | 496.842
2901.2542 | 695.4893 | 686.9509 | 656.7719 | 604.6447 | 510.7987 | 451.119 | 496.4233
2902.2542 | 694.8016 | 686.1181 | 663.0756 | 603.6628 | 510.8856 | 451.4291 | 496.4607
2903.2542 | 694.4708 | 684.8264 | 659.7287 | 602.8672 | 510.9616 | 451.3334 | 497.102
2904.2542 | 695.8022 | 684.1174 | 662.5486 | 601.2398 | 511.2966 | 451.5831 | 496.8493
2905.2542 | 697.562 | 684.8943 | 662.0053 | 600.0859 | 511.2606 | 451.8203 | 496.6492
2906.2542 | 699.7085 | 686.8487 | 662.4218 | 600.5044 | 511.1183 | 452.0604 | 497.1193
2907.2542 | 699.1617 | 688.9252 | 661.3327 | 600.6584 | 510.9852 | 451.762 | 497.4033
2908.2542 | 699.2561 | 689.8779 | 664.2323 | 600.5974 | 510.5118 | 451.7869 | 497.3284
2909.2542 | 700.3424 | 690.2645 | 665.1529 | 601.0403 | 510.4112 | 451.5809 | 498.0814
2910.2542 | 697.695 | 687.1998 | 660.1673 | 600.469 | 510.2187 | 451.4886 | 498.1905
2911.2542 | 696.1007 | 683.6673 | 658.2399 | 598.5798 | 509.5424 | 451.513 | 497.9028
2912.2542 | 696.4692 | 681.3139 | 655.5096 | 597.4272 | 509.2647 | 451.7576 | 498.2419
2913.2542 | 696.3896 | 679.3569 | 653.0351 | 596.6149 | 509.149 | 451.5913 | 498.7693
2914.2542 | 695.5107 | 677.9772 | 652.7965 | 594.7604 | 508.7167 | 451.717 | 499.4442
2915.2542 | 697.0213 | 680.0798 | 654.2331 | 595.276 | 508.3372 | 452.4267 | 499.0272
2916.2542 | 695.871 | 682.668 | 662.3173 | 595.2567 | 507.7458 | 452.1381 | 498.988
2917.2542 | 698.7422 | 688.6496 | 665.7883 | 596.8297 | 508.634 | 452.3999 | 499.7549
2918.2542 | 699.422 | 690.1187 | 664.6051 | 597.5477 | 508.3976 | 453.2587 | 500.2549
2919.2542 | 700.1367 | 690.2573 | 662.2285 | 598.0014 | 508.3706 | 453.0555 | 500.8083
2920.2542 | 701.9162 | 690.7726 | 660.9904 | 598.0528 | 508.1809 | 453.0183 | 501.0738
2921.2542 | 703.0109 | 690.0903 | 660.006 | 598.3091 | 507.9328 | 454.0591 | 501.8628
2922.2542 | 701.8268 | 687.8786 | 658.1136 | 597.7793 | 507.6037 | 454.0249 | 501.9745
2923.2542 | 699.9675 | 686.6919 | 657.819 | 597.7531 | 507.494 | 454.3185 | 501.8459
2924.2542 | 700.669 | 686.5154 | 656.0305 | 598.1035 | 507.5304 | 454.4048 | 502.4379
2925.2542 | 701.6922 | 686.9991 | 656.6285 | 598.1387 | 507.1552 | 454.066 | 503.1145
2926.2542 | 700.1754 | 686.8158 | 656.0109 | 597.5754 | 507.1834 | 454.4025 | 502.7288
2927.2542 | 697.7085 | 687.5887 | 657.2199 | 597.6094 | 506.5452 | 454.3932 | 503.3752
2928.2542 | 696.7061 | 688.6294 | 657.8728 | 596.8958 | 507.2025 | 454.5801 | 503.505
2929.2542 | 697.567 | 689.072 | 657.8623 | 596.9451 | 507.2602 | 454.548 | 503.6774
2930.2542 | 698.096 | 688.4406 | 656.7296 | 596.1147 | 506.9431 | 455.1396 | 504.0967
2931.2542 | 699.2636 | 686.3658 | 654.6812 | 595.1136 | 506.1073 | 455.426 | 504.2669
2932.2542 | 698.3723 | 687.3467 | 654.5116 | 595.5847 | 506.4411 | 455.3232 | 504.8515
2933.2542 | 697.7968 | 688.2981 | 654.3927 | 596.69 | 506.845 | 455.1725 | 505.7954
2934.2542 | 698.1745 | 688.2162 | 654.1203 | 596.7741 | 507.1608 | 455.2197 | 505.3332
2935.2542 | 700.0724 | 686.4991 | 651.2869 | 596.185 | 506.8645 | 455.6293 | 505.1117
2936.2542 | 699.7001 | 684.6944 | 648.6729 | 596.3192 | 506.692 | 455.1196 | 506.2418
2937.2542 | 700.6227 | 684.3434 | 646.7003 | 595.3163 | 506.2152 | 454.9229 | 506.5744
2938.2542 | 701.787 | 683.6736 | 645.2458 | 594.9513 | 506.6426 | 455.3584 | 507.0422
2939.2542 | 700.671 | 682.3303 | 644.8235 | 594.3761 | 506.3026 | 455.1962 | 506.9039
2940.2542 | 699.5522 | 680.4592 | 642.681 | 593.7698 | 505.8844 | 455.239 | 507.429
2941.2542 | 700.4538 | 682.2457 | 644.2402 | 593.8556 | 506.4266 | 455.7534 | 507.71
2942.2542 | 701.0329 | 684.2226 | 646.7661 | 594.6601 | 506.822 | 455.3862 | 508.1272
2943.2542 | 700.419 | 685.2412 | 647.0655 | 594.4559 | 506.535 | 455.1507 | 508.629
2944.2542 | 700.1805 | 687.2857 | 648.9053 | 595.0275 | 507.5982 | 455.7706 | 508.5304
2945.2542 | 698.0046 | 688.0872 | 650.4313 | 594.6237 | 507.4301 | 455.4103 | 509.3421
2946.2542 | 696.8306 | 688.7791 | 652.4513 | 594.3205 | 507.6645 | 454.9608 | 509.6351
2947.2542 | 698.3629 | 689.7482 | 654.4419 | 594.6933 | 507.222 | 455.8186 | 509.5567
2948.2542 | 698.8248 | 689.6022 | 654.1831 | 596.0402 | 507.43 | 455.8407 | 509.6547
2949.2542 | 702.9763 | 690.3528 | 653.2605 | 596.0452 | 507.4438 | 456.2229 | 510.0266
2950.2542 | 703.547 | 688.606 | 651.7475 | 596.5067 | 507.9149 | 456.4685 | 510.6655
2951.2542 | 703.3371 | 687.3824 | 650.6158 | 596.8677 | 508.1485 | 456.6237 | 511.3493
2952.2542 | 702.921 | 685.5274 | 648.5697 | 596.3408 | 507.5438 | 457.081 | 511.7335
2953.2542 | 701.8596 | 684.1428 | 648.1573 | 595.6528 | 507.5837 | 457.1336 | 511.9579
2954.2542 | 703.1552 | 687.0555 | 654.6493 | 596.3466 | 507.832 | 457.5977 | 512.5073
2955.2542 | 703.6228 | 686.9752 | 653.251 | 595.7584 | 507.2675 | 457.3897 | 512.0852
2956.2542 | 703.1925 | 688.79 | 651.8076 | 596.587 | 507.5781 | 457.6274 | 512.3606
2957.2542 | 701.9721 | 688.48 | 655.611 | 596.3033 | 508.3786 | 458.1624 | 512.4692
2958.2542 | 701.5782 | 688.1568 | 653.7942 | 595.7121 | 508.2525 | 458.0692 | 513.1213
2959.2542 | 702.5886 | 685.9486 | 651.424 | 595.2607 | 507.8964 | 458.325 | 512.9122
2960.2542 | 702.2505 | 682.3563 | 648.0943 | 594.4416 | 507.6502 | 457.0127 | 512.884
2961.2542 | 699.9941 | 680.625 | 645.7109 | 594.1935 | 507.9641 | 457.4041 | 513.1939
2962.2542 | 699.2532 | 679.8399 | 646.5007 | 594.0291 | 507.755 | 457.5788 | 513.8816
2963.2542 | 698.3435 | 679.7233 | 647.8676 | 593.3011 | 507.5475 | 457.8256 | 514.915
2964.2542 | 699.0531 | 678.0852 | 645.3124 | 593.6171 | 510.3967 | 458.6463 | 515.9623
2965.2542 | 698.9132 | 679.7314 | 645.3196 | 593.1822 | 510.0162 | 458.7374 | 516.6006
2966.2542 | 700.4395 | 679.1143 | 644.0572 | 591.3905 | 510.3367 | 459.0828 | 516.8099
2967.2542 | 701.8585 | 680.9999 | 644.6185 | 591.9091 | 509.9113 | 459.2887 | 516.7905
2968.2542 | 701.3065 | 679.847 | 643.5577 | 592.4193 | 510.3468 | 460.2069 | 516.986
2969.2542 | 702.7301 | 678.5997 | 641.6994 | 591.6951 | 510.773 | 459.4409 | 517.587
2970.2542 | 702.1045 | 678.3837 | 640.4334 | 592.2507 | 512.5645 | 459.5026 | 518.1924
2971.2542 | 700.3992 | 677.7785 | 643.3682 | 591.4963 | 512.5793 | 459.3908 | 518.6634
2972.2542 | 698.2852 | 679.1016 | 643.4763 | 592.126 | 512.725 | 459.3362 | 518.6884
2973.2542 | 699.7578 | 681.1438 | 642.7147 | 592.2162 | 513.8007 | 459.5873 | 520.0522
2974.2542 | 702.1001 | 680.654 | 641.5945 | 591.8353 | 514.1977 | 459.9836 | 519.8153
2975.2542 | 701.981 | 680.0625 | 641.8259 | 591.9481 | 513.9607 | 460.5251 | 520.6688
2976.2542 | 699.2593 | 680.5588 | 644.6206 | 592.1063 | 514.3765 | 460.4737 | 521.3711
2977.2542 | 698.1685 | 680.8529 | 645.0971 | 592.1939 | 515.3992 | 460.4147 | 521.799
2978.2542 | 698.2971 | 679.3909 | 643.3289 | 591.4992 | 514.1624 | 460.6401 | 522.5243
2979.2542 | 698.633 | 677.3064 | 641.5946 | 591.8847 | 515.6147 | 461.0028 | 522.9225
2980.2542 | 697.6836 | 677.2443 | 641.0666 | 591.6569 | 515.9121 | 460.9297 | 524.0163
2981.2542 | 696.0674 | 676.0084 | 640.7703 | 590.4745 | 515.596 | 460.9075 | 524.611
2982.2542 | 695.3658 | 676.4503 | 643.5025 | 590.8967 | 515.9623 | 460.6089 | 525.5079
2983.2542 | 693.2171 | 675.3169 | 644.2564 | 589.9996 | 515.6321 | 461.1468 | 526.0605
2984.2542 | 693.663 | 675.6724 | 643.523 | 589.9981 | 516.4855 | 461.1157 | 526.9986
2985.2542 | 696.3167 | 678.3162 | 644.6049 | 590.0349 | 516.5757 | 460.6861 | 526.9609
2986.2542 | 696.5917 | 678.5924 | 644.1211 | 590.2743 | 515.4259 | 461.3381 | 527.8529
2987.2542 | 696.0759 | 678.9861 | 643.1471 | 590.1835 | 514.7512 | 461.9643 | 528.2719
2988.2542 | 695.0782 | 678.3062 | 643.1106 | 589.6699 | 514.4805 | 462.0552 | 528.1006
2989.2542 | 694.207 | 678.8556 | 644.578 | 590.9083 | 516.5279 | 461.7496 | 529.3558
2990.2542 | 692.9061 | 678.2547 | 644.268 | 590.4491 | 517.1638 | 462.1087 | 530.1639
2991.2542 | 693.3627 | 677.2214 | 642.8379 | 591.3484 | 516.6235 | 462.1458 | 530.492
2992.2542 | 693.6508 | 677.6618 | 644.4425 | 590.7549 | 516.4231 | 462.2012 | 530.7503
2993.2542 | 694.3326 | 679.5559 | 649.4406 | 590.768 | 517.2854 | 462.2464 | 531.898
2994.2542 | 697.4574 | 679.324 | 647.7383 | 591.0992 | 516.9008 | 462.6977 | 532.3112
2995.2542 | 696.6994 | 676.3375 | 645.3093 | 590.1782 | 516.6676 | 462.4501 | 532.9028
2996.2542 | 694.2892 | 677.6649 | 645.9994 | 589.649 | 517.0198 | 462.4489 | 533.0411
2997.2542 | 693.4135 | 676.581 | 645.7373 | 590.3157 | 517.117 | 462.6181 | 533.8837
2998.2542 | 692.8471 | 674.3071 | 645.0418 | 589.5029 | 517.0368 | 462.6529 | 534.9814
2999.2542 | 691.5651 | 672.6883 | 643.1055 | 589.1592 | 518.1735 | 462.0699 | 534.685
3000.2542 | 691.7152 | 673.188 | 644.5274 | 589.8143 | 518.0428 | 462.1366 | 534.7705
3001.2542 | 690.8611 | 673.8264 | 643.635 | 588.6634 | 518.3148 | 462.9174 | 534.5835
3002.2542 | 690.754 | 672.1072 | 642.611 | 588.3884 | 518.1017 | 462.8476 | 534.4024
3003.2542 | 689.63 | 669.9616 | 639.6725 | 588.1624 | 517.6745 | 462.3467 | 534.3167
3004.2542 | 688.2884 | 670.7721 | 644.3181 | 585.3208 | 517.2205 | 462.9182 | 535.0993
3005.2542 | 687.4792 | 670.9302 | 643.7765 | 587.8475 | 517.9469 | 462.7608 | 535.6336
3006.2542 | 687.9986 | 672.6553 | 644.8416 | 587.3621 | 518.5671 | 463.2478 | 536.0062
3007.2542 | 687.4476 | 672.4896 | 645.1367 | 585.2395 | 518.1291 | 463.3273 | 536.7373
3008.2542 | 688.4895 | 671.0901 | 644.1994 | 588.3512 | 518.7968 | 463.5499 | 536.3442
3009.2542 | 687.3908 | 669.4836 | 641.6941 | 585.8564 | 519.0311 | 463.8123 | 536.4002
3010.2542 | 687.6611 | 669.0701 | 641.6841 | 584.8959 | 519.0856 | 463.8054 | 537.274
3011.2542 | 687.6157 | 669.6763 | 642.4351 | 584.3322 | 519.5587 | 464.3696 | 539.0754
3012.2542 | 686.6402 | 669.8567 | 642.1877 | 582.6759 | 520.3896 | 465.0857 | 538.6496
3013.2542 | 688.6325 | 670.8596 | 640.8862 | 584.28 | 520.7589 | 465.6463 | 539.1396
3014.2542 | 688.827 | 670.1579 | 639.6398 | 583.454 | 521.3197 | 465.8069 | 539.4284
3015.2542 | 690.325 | 670.3665 | 638.4736 | 584.3345 | 520.7087 | 466.0591 | 540.8587
3016.2542 | 688.8924 | 670.9043 | 638.301 | 583.4795 | 520.4429 | 467.1933 | 541.2119
3017.2542 | 687.5971 | 670.2233 | 637.0699 | 583.464 | 521.4362 | 466.875 | 541.8228
3018.2542 | 686.6843 | 669.1501 | 635.8386 | 583.6568 | 521.0314 | 467.4087 | 542.2103
3019.2542 | 687.5432 | 672.4881 | 637.5095 | 582.2809 | 520.7417 | 468.2305 | 542.4528
3020.2542 | 689.2103 | 676.1418 | 640.1754 | 584.4052 | 521.4557 | 468.8603 | 543.4144
3021.2542 | 690.0426 | 676.5733 | 640.2355 | 585.0895 | 521.7132 | 470.1374 | 544.2448
3022.2542 | 690.8349 | 678.1292 | 639.6215 | 585.4391 | 521.7233 | 470.5365 | 543.8707
3023.2542 | 690.4842 | 677.4349 | 639.7396 | 585.1015 | 521.9781 | 470.3916 | 544.8038
3024.2542 | 689.9977 | 675.5346 | 637.5324 | 584.8692 | 522.15 | 470.4107 | 544.4818
3025.2542 | 691.308 | 676.4566 | 637.7023 | 587.1422 | 521.5757 | 469.9775 | 545.2056
3026.2542 | 689.8042 | 675.5061 | 638.874 | 587.0101 | 522.0548 | 470.362 | 545.5018
3027.2542 | 688.6157 | 675.3128 | 640.4727 | 585.1624 | 522.4946 | 470.5451 | 545.6316
3028.2542 | 690.1885 | 675.6507 | 640.1338 | 585.4323 | 522.8438 | 470.3249 | 545.6759
3029.2542 | 688.8227 | 675.1451 | 639.5069 | 585.7422 | 523.0302 | 470.103 | 546.081
3030.2542 | 692.2998 | 676.8207 | 639.4829 | 585.9954 | 522.4459 | 469.9253 | 546.1808
3031.2542 | 694.2087 | 676.085 | 637.7823 | 585.9017 | 522.0692 | 469.5266 | 546.1128
3032.2542 | 692.4953 | 675.4747 | 636.737 | 585.4356 | 522.7071 | 470.1812 | 546.4718
3033.2542 | 692.112 | 674.7251 | 637.0035 | 584.3659 | 522.719 | 469.6343 | 547.3227
3034.2542 | 691.2786 | 674.0894 | 636.9194 | 584.755 | 522.8682 | 470.0271 | 546.8042
3035.2542 | 690.8997 | 674.1367 | 637.8596 | 583.8597 | 522.7476 | 469.412 | 547.6542
3036.2542 | 690.5121 | 674.3985 | 640.3987 | 584.8405 | 522.5867 | 469.4854 | 548.3865
3037.2542 | 690.3271 | 675.2459 | 640.67 | 584.527 | 523.7046 | 469.8447 | 548.163
3038.2542 | 689.2861 | 674.658 | 640.1422 | 584.3384 | 524.21 | 469.9248 | 548.0325
3039.2542 | 690.8156 | 674.676 | 640.0581 | 584.936 | 524.5949 | 469.8118 | 548.6355
3040.2542 | 692.5213 | 672.8383 | 638.0931 | 583.1863 | 524.7146 | 469.0885 | 548.3337
3041.2542 | 694.043 | 673.5735 | 636.7443 | 582.9445 | 522.4006 | 469.3962 | 549.0783
3042.2542 | 693.9009 | 673.8924 | 637.6914 | 584.1041 | 523.7715 | 468.8292 | 549.5798
3043.2542 | 694.0071 | 674.7304 | 639.1143 | 586.1352 | 524.4584 | 467.988 | 550.6173
3044.2542 | 693.1834 | 672.5225 | 637.278 | 585.8841 | 524.6831 | 468.0231 | 550.5779
3045.2542 | 694.8647 | 673.7553 | 637.7604 | 584.9571 | 525.7313 | 468.5527 | 551.318
3046.2542 | 693.5754 | 672.7394 | 637.1949 | 585.6411 | 525.8703 | 468.4716 | 551.2398
3047.2542 | 692.4032 | 672.6939 | 637.8192 | 584.7007 | 525.8612 | 468.1951 | 551.7507
3048.2542 | 691.9152 | 672.4416 | 638.2761 | 584.1002 | 525.9337 | 468.6551 | 552.2312
3049.2542 | 693.4924 | 673.5332 | 637.4498 | 584.9171 | 527.0677 | 468.0466 | 552.2686
3050.2542 | 693.4305 | 672.6342 | 635.8828 | 584.5198 | 527.1553 | 468.7015 | 552.5471
3051.2542 | 694.1259 | 671.9879 | 635.0019 | 584.3454 | 526.4786 | 468.1054 | 552.0645
3052.2542 | 694.4804 | 673.7312 | 635.4087 | 584.1849 | 526.6455 | 468.0986 | 553.2535
3053.2542 | 695.5211 | 673.0244 | 633.8386 | 584.14 | 528.0629 | 467.9626 | 553.7639
3054.2542 | 695.1461 | 674.5627 | 635.4826 | 584.9538 | 528.9672 | 467.5754 | 553.998
3055.2542 | 693.9267 | 675.7626 | 637.0083 | 585.4359 | 529.0329 | 467.1757 | 555.2077
3056.2542 | 694.4426 | 676.9106 | 638.4218 | 585.5218 | 529.1882 | 467.5473 | 555.552
3057.2542 | 693.0081 | 675.5714 | 637.9114 | 584.4466 | 529.4233 | 467.6477 | 555.5876
3058.2542 | 690.0647 | 675.838 | 638.3623 | 584.6493 | 530.4322 | 467.6326 | 556.6784
3059.2542 | 688.2175 | 675.6694 | 638.8088 | 585.1749 | 531.2154 | 467.7501 | 556.1954
3060.2542 | 689.1543 | 676.254 | 641.1129 | 585.0624 | 530.227 | 467.9611 | 556.9963
3061.2542 | 692.8199 | 678.7187 | 641.3335 | 586.0249 | 530.295 | 467.2154 | 556.7713
3062.2542 | 693.3499 | 678.3122 | 639.4486 | 585.6384 | 530.9125 | 467.5067 | 556.4086
3063.2542 | 694.813 | 675.6734 | 637.693 | 585.9602 | 529.4387 | 467.3916 | 555.9664
3064.2542 | 694.3471 | 677.5764 | 637.3991 | 586.4339 | 529.8411 | 466.666 | 556.4859
3065.2542 | 694.4445 | 677.3135 | 638.2608 | 586.0514 | 530.2368 | 466.5524 | 557.0428
3066.2542 | 694.0753 | 676.7447 | 636.9597 | 585.7369 | 528.6127 | 467.7238 | 557.4096
3067.2542 | 692.996 | 675.8938 | 635.8537 | 586.1525 | 529.5361 | 467.5397 | 557.8568
3068.2542 | 692.6988 | 676.2763 | 635.0585 | 586.1225 | 528.568 | 467.7211 | 558.3674
3069.2542 | 692.6412 | 675.8523 | 634.6811 | 586.2985 | 528.8845 | 468.4325 | 558.5741
3070.2542 | 691.8368 | 676.9216 | 634.6008 | 586.4686 | 529.2435 | 467.6797 | 560.03
3071.2542 | 691.4634 | 675.0926 | 632.9266 | 585.9315 | 529.0508 | 468.1009 | 560.3195
3072.2542 | 693.0268 | 677.4146 | 631.3685 | 584.3597 | 528.4292 | 467.8116 | 559.4488
3073.2542 | 691.4592 | 678.022 | 633.2394 | 584.7295 | 527.1225 | 467.1177 | 560.1638
3074.2542 | 689.6581 | 676.3216 | 634.2633 | 585.8246 | 528.3771 | 467.971 | 560.8801
3075.2542 | 688.5503 | 677.5654 | 635.0752 | 585.953 | 528.4491 | 468.3655 | 560.5293
3076.2542 | 685.9629 | 676.2442 | 635.0196 | 586.6027 | 528.6944 | 468.0486 | 560.6766
3077.2542 | 686.6952 | 674.791 | 634.6899 | 584.8456 | 528.1973 | 467.7092 | 561.0259
3078.2542 | 688.738 | 675.2961 | 634.4329 | 585.0851 | 527.5826 | 467.4328 | 561.1276
3079.2542 | 690.1373 | 675.2022 | 633.7563 | 584.1686 | 527.7123 | 468.0386 | 561.103
3080.2542 | 690.71 | 674.6197 | 633.1583 | 585.2322 | 528.2689 | 468.1921 | 560.9557
3081.2542 | 688.9594 | 671.7451 | 630.4895 | 584.2608 | 528.4284 | 467.9225 | 560.9188
3082.2542 | 687.3201 | 668.3434 | 627.9464 | 583.0502 | 527.2726 | 467.3445 | 561.5778
3083.2542 | 686.7038 | 668.2261 | 626.7948 | 581.3695 | 527.5862 | 467.8946 | 562.6035
3084.2542 | 686.9556 | 672.2386 | 629.43 | 583.967 | 529.263 | 468.0166 | 563.8739
3085.2542 | 690.2315 | 673.76 | 629.4531 | 584.1596 | 529.853 | 468.1479 | 563.7607
3086.2542 | 689.8967 | 674.8225 | 629.9684 | 583.3538 | 529.1307 | 468.6202 | 564.5076
3087.2542 | 688.7979 | 674.5634 | 629.434 | 583.3562 | 530.6459 | 468.6368 | 564.948
3088.2542 | 688.1571 | 671.8004 | 628.5963 | 583.7633 | 530.3382 | 468.214 | 565.2721
3089.2542 | 690.3169 | 673.8547 | 629.0077 | 582.7064 | 530.9496 | 468.657 | 566.1209
3090.2542 | 689.6912 | 673.2649 | 629.6974 | 583.0149 | 531.363 | 468.7173 | 566.5307
3091.2542 | 693.1041 | 675.4406 | 631.8898 | 583.687 | 530.923 | 468.397 | 566.9001
3092.2542 | 694.8346 | 679.3076 | 634.5365 | 584.0622 | 531.8105 | 469.2379 | 566.7901
3093.2542 | 693.7487 | 679.5979 | 633.9926 | 584.9841 | 531.657 | 469.3303 | 567.2021
3094.2542 | 692.8478 | 678.1338 | 632.49 | 585.0818 | 532.236 | 468.9813 | 567.939
3095.2542 | 692.147 | 679.4309 | 634.2583 | 585.4745 | 532.4231 | 469.2221 | 568.7404
3096.2542 | 691.4957 | 681.1587 | 634.8014 | 586.0211 | 533.2199 | 469.5296 | 568.4584
3097.2542 | 691.9269 | 681.8984 | 634.3749 | 586.5648 | 534.434 | 469.8258 | 568.7578
3098.2542 | 691.6982 | 680.9134 | 634.0672 | 586.6288 | 534.74 | 470.1356 | 569.2754
3099.2542 | 691.1264 | 679.4801 | 634.0639 | 586.2558 | 533.7938 | 470.3548 | 569.3516
3100.2542 | 693.3599 | 679.4792 | 633.081 | 586.1116 | 534.9872 | 470.2568 | 570.0287
3101.2542 | 692.8891 | 678.8426 | 633.3283 | 585.182 | 535.1606 | 470.3399 | 570.2227
3102.2542 | 692.567 | 678.6429 | 634.4109 | 585.2856 | 535.6347 | 470.5818 | 570.264
3103.2542 | 692.5061 | 678.927 | 633.7922 | 585.0689 | 535.751 | 471.1721 | 570.3111
3104.2542 | 693.6215 | 681.86 | 635.3364 | 586.2806 | 536.5402 | 471.438 | 569.8476
3105.2542 | 695.1021 | 682.7678 | 635.1087 | 586.494 | 536.3691 | 471.2699 | 570.4018
3106.2542 | 694.9357 | 681.1015 | 633.6693 | 586.6173 | 537.8316 | 471.2406 | 570.7274
3107.2542 | 693.3646 | 678.0771 | 631.9493 | 585.6041 | 538.2632 | 470.8695 | 571.5748
3108.2542 | 692.6448 | 676.8659 | 631.6 | 585.3391 | 538.751 | 471.5267 | 570.9767
3109.2542 | 691.0265 | 675.1549 | 629.3165 | 584.4629 | 539.2631 | 471.5003 | 571.2917
3110.2542 | 691.5445 | 675.5087 | 630.7121 | 584.5844 | 539.6072 | 471.6708 | 571.5027
3111.2542 | 691.0102 | 675.5016 | 629.946 | 584.6667 | 539.6886 | 471.4772 | 571.3068
3112.2542 | 688.9632 | 673.2959 | 628.0416 | 583.243 | 539.6245 | 472.4374 | 571.3394
3113.2542 | 689.2208 | 673.6499 | 628.2456 | 582.5813 | 540.0105 | 472.2149 | 571.2964
3114.2542 | 688.2443 | 674.3611 | 629.5619 | 585.0974 | 540.2712 | 472.4913 | 572.0977
3115.2542 | 687.957 | 673.2144 | 628.4597 | 585.0966 | 541.6969 | 473.0229 | 571.9793
3116.2542 | 689.988 | 672.7729 | 628.4333 | 583.5796 | 543.1864 | 472.8363 | 571.6768
3117.2542 | 690.0156 | 673.2022 | 628.1234 | 582.9733 | 543.1216 | 472.611 | 573.2491
3118.2542 | 689.8044 | 672.2746 | 626.7006 | 583.7652 | 543.8761 | 473.2084 | 573.5563
3119.2542 | 689.027 | 673.4998 | 626.113 | 583.3432 | 543.7309 | 473.742 | 573.8907
3120.2542 | 689.6233 | 674.4382 | 626.4122 | 583.7367 | 543.9985 | 473.6985 | 574.1253
3121.2542 | 689.838 | 676.3963 | 626.7766 | 583.7137 | 544.4743 | 473.4034 | 573.4558
3122.2542 | 691.2484 | 676.0909 | 627.1116 | 584.4824 | 545.0608 | 474.4768 | 573.8523
3123.2542 | 690.3219 | 674.6669 | 626.5048 | 584.0427 | 545.1659 | 474.4225 | 574.7732
3124.2542 | 688.7773 | 675.7198 | 628.1953 | 584.7251 | 546.0633 | 474.5155 | 575.2604
3125.2542 | 688.6889 | 675.8612 | 629.6352 | 584.688 | 546.3692 | 474.61 | 576.1896
3126.2542 | 690.5804 | 675.9682 | 628.5637 | 585.6664 | 547.3232 | 474.8782 | 576.1486
3127.2542 | 688.4975 | 674.3014 | 627.26 | 584.0225 | 546.8673 | 474.571 | 576.0168
3128.2542 | 688.5406 | 676.8316 | 628.8268 | 584.8366 | 547.5092 | 475.4359 | 576.4141
3129.2542 | 692.9118 | 678.875 | 628.8225 | 586.2968 | 548.3154 | 474.9903 | 576.4066
3130.2542 | 695.0495 | 679.5533 | 629.4659 | 585.774 | 548.4863 | 475.5668 | 576.911
3131.2542 | 698.4886 | 680.5038 | 629.2385 | 586.4059 | 548.2588 | 476.3814 | 577.5331
3132.2542 | 699.517 | 678.9056 | 629.6399 | 585.7026 | 549.8104 | 476.8764 | 577.5049
3133.2542 | 699.7973 | 678.2099 | 629.3292 | 585.8418 | 549.975 | 476.6534 | 577.9915
3134.2542 | 697.3796 | 675.5767 | 628.9969 | 586.3233 | 549.986 | 476.3601 | 577.7562
3135.2542 | 696.0273 | 673.2665 | 627.5721 | 584.7114 | 550.6283 | 475.8812 | 577.1214
3136.2542 | 695.1562 | 671.6927 | 626.6755 | 585.3532 | 551.8384 | 476.3054 | 577.8572
3137.2542 | 695.6159 | 669.3715 | 624.5312 | 584.0455 | 553.1155 | 476.0556 | 578.4453
3138.2542 | 697.5495 | 668.4946 | 624.0339 | 584.5264 | 552.98 | 476.6663 | 579.1497
3139.2542 | 696.9799 | 668.6254 | 623.8842 | 584.051 | 554.6311 | 476.8927 | 579.9306
3140.2542 | 693.982 | 666.5888 | 623.9246 | 583.3031 | 554.1552 | 477.3288 | 579.8945
3141.2542 | 691.7545 | 666.6727 | 624.6571 | 583.5361 | 554.3339 | 477.6772 | 580.9447
3142.2542 | 690.4255 | 668.5906 | 625.5312 | 583.2185 | 555.5198 | 477.757 | 581.2403
3143.2542 | 688.8308 | 670.9905 | 626.966 | 583.6243 | 555.8662 | 477.9156 | 580.9927
3144.2542 | 687.8771 | 671.371 | 626.2816 | 583.6703 | 556.553 | 478.3012 | 581.3171
3145.2542 | 684.4813 | 670.4015 | 625.3729 | 583.8984 | 555.7379 | 477.9404 | 581.4619
3146.2542 | 686.2196 | 669.4079 | 624.7704 | 583.5685 | 556.4794 | 477.968 | 582.1442
3147.2542 | 686.7311 | 668.9562 | 625.7287 | 584.271 | 557.0731 | 478.0257 | 582.1759
3148.2542 | 685.6333 | 668.0839 | 625.3455 | 583.3805 | 557.8266 | 477.7874 | 582.1184
3149.2542 | 684.364 | 665.47 | 623.4141 | 583.251 | 557.2248 | 477.6901 | 581.8988
3150.2542 | 683.8609 | 661.6328 | 622.5363 | 582.0949 | 556.7041 | 477.7083 | 582.5646
3151.2542 | 682.8555 | 659.9068 | 621.8143 | 581.8677 | 556.6721 | 478.5418 | 582.4493
3152.2542 | 682.2657 | 660.1497 | 620.6726 | 581.9346 | 557.474 | 478.1127 | 582.4466
3153.2542 | 683.491 | 663.0613 | 623.228 | 580.7251 | 557.7792 | 478.0558 | 582.8425
3154.2542 | 682.6366 | 661.9391 | 622.7782 | 580.7641 | 558.3047 | 478.4714 | 582.6213
3155.2542 | 682.7227 | 663.5537 | 624.8705 | 581.6756 | 558.7419 | 478.1455 | 582.2225
3156.2542 | 683.3842 | 664.9579 | 627.6526 | 581.5967 | 559.5873 | 478.3141 | 582.6665
3157.2542 | 681.9865 | 662.3462 | 625.8637 | 581.9384 | 559.8819 | 478.5656 | 583.5524
3158.2542 | 682.1156 | 662.7401 | 625.6886 | 582.1428 | 559.9559 | 479.4498 | 583.8432
3159.2542 | 682.1615 | 664.6353 | 626.8087 | 581.4412 | 559.5534 | 479.141 | 583.8042
3160.2542 | 682.2511 | 667.5994 | 628.4114 | 581.4796 | 559.69 | 478.6721 | 584.7933
3161.2542 | 679.9648 | 667.6528 | 628.6425 | 583.0039 | 560.7339 | 479.2403 | 585.6995
3162.2542 | 680.9489 | 667.2085 | 628.6161 | 582.6314 | 561.9584 | 479.972 | 586.1705
3163.2542 | 683.8585 | 667.6835 | 628.0017 | 583.3117 | 562.3638 | 480.2454 | 586.2149
3164.2542 | 684.9138 | 665.7787 | 626.3449 | 582.8262 | 562.3125 | 480.6161 | 586.5586
3165.2542 | 685.252 | 665.9829 | 624.1049 | 582.4143 | 562.1626 | 480.6664 | 586.5756
3166.2542 | 683.6577 | 662.8857 | 623.5407 | 581.881 | 562.0343 | 481.1874 | 586.8546
3167.2542 | 680.4663 | 663.1516 | 625.3703 | 582.409 | 562.9433 | 481.6046 | 587.8755
3168.2542 | 681.5534 | 664.5368 | 626.5967 | 582.1486 | 562.8615 | 481.7251 | 588.2111
3169.2542 | 683.0622 | 665.9509 | 626.3665 | 582.1623 | 564.0656 | 481.1792 | 587.6483
3170.2542 | 683.7796 | 666.5707 | 624.9651 | 583.2082 | 565.0968 | 480.6945 | 587.5116
3171.2542 | 683.7388 | 665.4759 | 623.2954 | 583.0491 | 564.541 | 481.1686 | 587.7855
3172.2542 | 684.881 | 664.6205 | 623.2001 | 583.4316 | 565.1485 | 481.4103 | 587.7811
3173.2542 | 684.5779 | 664.9688 | 623.9046 | 583.595 | 566.2476 | 481.0154 | 587.6256
3174.2542 | 686.5721 | 665.6475 | 623.3302 | 583.7824 | 566.9552 | 481.8984 | 587.7734
3175.2542 | 686.0432 | 664.9402 | 623.317 | 583.629 | 567.5282 | 482.8619 | 587.9939
3176.2542 | 687.5252 | 665.6148 | 622.9439 | 582.897 | 567.2503 | 482.2064 | 587.8426
3177.2542 | 688.9778 | 666.5967 | 623.6573 | 583.4422 | 567.1831 | 483.1519 | 587.7379
3178.2542 | 692.5782 | 667.1622 | 623.9912 | 584.669 | 568.155 | 483.0697 | 588.2322
3179.2542 | 694.5422 | 668.0489 | 622.7515 | 584.0277 | 568.6185 | 483.0094 | 588.6535
3180.2542 | 694.1495 | 667.7104 | 621.5379 | 584.4567 | 569.0739 | 483.758 | 588.7838
3181.2542 | 691.71 | 665.5442 | 621.2429 | 584.58 | 570.9283 | 483.9667 | 589.0813
3182.2542 | 692.3311 | 664.418 | 621.464 | 584.9116 | 570.2905 | 484.1255 | 589.2634
3183.2542 | 692.0844 | 663.9199 | 621.1308 | 585.253 | 569.9702 | 483.743 | 589.4708
3184.2542 | 687.0633 | 661.4225 | 619.9723 | 584.6662 | 568.4285 | 484.9517 | 589.3661
3185.2542 | 685.9594 | 658.9518 | 618.6559 | 585.1374 | 569.25 | 485.6473 | 590.1798
3186.2542 | 683.1191 | 658.8397 | 617.6109 | 585.8413 | 569.725 | 484.6875 | 589.7648
3187.2542 | 679.1986 | 658.6503 | 617.5238 | 585.8238 | 571.7988 | 484.0857 | 589.6377
3188.2542 | 680.7793 | 660.4781 | 618.6421 | 585.3936 | 572.3282 | 485.0835 | 589.3213
3189.2542 | 681.0574 | 662.0805 | 620.3108 | 584.9553 | 572.2721 | 485.6163 | 588.9336
3190.2542 | 679.0879 | 660.7528 | 620.0555 | 585.1606 | 572.5283 | 485.2413 | 588.7713
3191.2542 | 677.5416 | 658.8752 | 620.0236 | 584.8051 | 572.2184 | 485.8678 | 589.8443
3192.2542 | 678.0822 | 659.5042 | 619.7775 | 585.0503 | 572.2704 | 486.1399 | 589.6619
3193.2542 | 678.7953 | 660.4869 | 619.6364 | 585.8238 | 572.2084 | 486.3419 | 589.8096
3194.2542 | 677.095 | 659.0994 | 618.5029 | 585.5497 | 571.7087 | 486.7148 | 589.473
3195.2542 | 676.0227 | 657.5585 | 618.1532 | 585.9025 | 573.0776 | 486.1942 | 589.3342
3196.2542 | 679.4503 | 657.7937 | 617.599 | 585.124 | 572.9786 | 486.494 | 589.1676
3197.2542 | 679.8716 | 657.6628 | 617.3402 | 585.2465 | 572.4695 | 486.5758 | 589.101
3198.2542 | 680.0666 | 658.8555 | 617.9556 | 585.2348 | 572.8359 | 487.0472 | 589.129
3199.2542 | 679.4337 | 660.6533 | 618.0396 | 585.9521 | 572.8012 | 487.2658 | 589.6884
3200.2542 | 680.1187 | 660.4416 | 618.7206 | 585.8358 | 573.1352 | 486.6993 | 589.4382
3201.2542 | 680.4019 | 659.8723 | 619.4049 | 585.7826 | 573.3321 | 486.5197 | 588.8527
3202.2542 | 678.9779 | 660.5 | 619.224 | 585.9282 | 573.7944 | 486.7653 | 589.036
3203.2542 | 683.0516 | 662.031 | 619.3456 | 586.489 | 573.3338 | 486.2955 | 588.4241
3204.2542 | 684.6412 | 660.5627 | 617.8393 | 586.3397 | 572.8814 | 486.5176 | 588.2545
3205.2542 | 685.6149 | 659.2745 | 615.8391 | 585.9276 | 572.485 | 487.2343 | 588.6639
3206.2542 | 685.5311 | 657.8665 | 615.1718 | 586.4687 | 573.3768 | 487.4428 | 588.3704
3207.2542 | 686.5397 | 658.6618 | 615.8524 | 587.0413 | 573.416 | 487.7103 | 589.1134
3208.2542 | 685.4662 | 658.1146 | 615.3826 | 587.4249 | 573.2833 | 487.6983 | 588.4863
3209.2542 | 687.0167 | 657.284 | 615.0549 | 587.2182 | 574.0526 | 487.8046 | 588.4424
3210.2542 | 686.5359 | 657.3971 | 616.1714 | 587.1496 | 572.9697 | 488.7964 | 588.467
3211.2542 | 687.3182 | 658.815 | 615.7661 | 587.1535 | 572.1649 | 488.7636 | 588.6253
3212.2542 | 686.5613 | 659.8237 | 617.2681 | 588.8057 | 573.1054 | 489.4007 | 588.7419
3213.2542 | 685.4507 | 660.0931 | 617.2199 | 590.5547 | 573.0475 | 489.3956 | 588.2354
3214.2542 | 685.1722 | 659.0303 | 616.5456 | 590.2185 | 573.8105 | 489.2897 | 587.6977
3215.2542 | 684.1428 | 656.9345 | 613.7183 | 590.1093 | 573.6582 | 489.236 | 587.0154
3216.2542 | 686.6568 | 658.5278 | 614.7644 | 589.7849 | 573.6825 | 489.2299 | 587.1381
3217.2542 | 688.754 | 661.5937 | 615.5182 | 589.8687 | 572.9742 | 489.3385 | 587.2717
3218.2542 | 686.8651 | 663.0881 | 615.8908 | 590.417 | 573.1445 | 489.525 | 587.7053
3219.2542 | 684.3041 | 664.4952 | 616.6765 | 590.3122 | 572.8499 | 490.3636 | 588.0032
3220.2542 | 685.0639 | 666.2008 | 618.0139 | 590.1395 | 573.1767 | 490.3432 | 588.4453
3221.2542 | 685.6635 | 667.0838 | 617.1176 | 590.9981 | 573.2025 | 490.9912 | 587.9384
3222.2542 | 685.5278 | 667.3156 | 617.4078 | 590.7821 | 573.4921 | 490.8229 | 587.5603
3223.2542 | 684.6682 | 667.5262 | 616.9621 | 590.4779 | 573.733 | 490.4809 | 587.6598
3224.2542 | 682.2637 | 666.5756 | 617.9851 | 589.0937 | 573.6319 | 491.1225 | 587.6169
3225.2542 | 682.4976 | 667.346 | 617.4925 | 588.4141 | 574.0224 | 490.9732 | 587.4024
3226.2542 | 682.1982 | 666.2106 | 615.7184 | 588.2583 | 574.0351 | 490.1352 | 586.7104
3227.2542 | 679.7634 | 663.8657 | 615.1146 | 588.2655 | 573.4335 | 490.2056 | 586.9412
3228.2542 | 679.0067 | 663.2304 | 615.7986 | 587.8637 | 573.7245 | 490.2879 | 586.8079
3229.2542 | 678.2408 | 664.3274 | 617.0751 | 587.8537 | 573.2119 | 491.2331 | 587.1266
3230.2542 | 678.7217 | 664.4102 | 617.8655 | 587.452 | 573.1801 | 491.1112 | 586.5008
3231.2542 | 678.7886 | 666.2709 | 619.2447 | 587.9202 | 573.5411 | 491.0662 | 586.6185
3232.2542 | 678.4688 | 668.8014 | 621.0491 | 588.2427 | 572.8651 | 491.5483 | 586.2671
3233.2542 | 676.8633 | 668.5387 | 621.4274 | 587.7459 | 572.8481 | 491.2232 | 586.1017
3234.2542 | 675.5987 | 669.6345 | 622.2181 | 588.2997 | 571.9979 | 492.1102 | 586.5215
3235.2542 | 675.0726 | 668.567 | 621.322 | 588.2702 | 572.0605 | 492.9095 | 586.4656
3236.2542 | 675.4659 | 668.7591 | 621.6233 | 589.27 | 571.5576 | 492.9828 | 586.4421
3237.2542 | 674.5513 | 668.309 | 621.1228 | 589.0069 | 571.1835 | 492.4617 | 586.0961
3238.2542 | 677.4816 | 667.7844 | 620.8608 | 588.5972 | 571.9378 | 492.9106 | 586.112
3239.2542 | 676.9216 | 666.8272 | 619.4433 | 588.683 | 571.9187 | 492.6658 | 586.1337
3240.2542 | 676.1851 | 665.3852 | 618.0626 | 588.7479 | 571.8119 | 493.4088 | 586.3945
3241.2542 | 675.6066 | 662.471 | 615.7801 | 588.5618 | 571.3868 | 493.1468 | 585.7416
3242.2542 | 674.6316 | 661.0999 | 613.1843 | 588.3627 | 571.8314 | 492.7258 | 585.6915
3243.2542 | 672.4862 | 659.1483 | 611.3598 | 588.0349 | 571.3375 | 492.7215 | 585.9107
3244.2542 | 673.0598 | 660.4173 | 610.2438 | 587.4474 | 571.5303 | 493.2032 | 586.4529
3245.2542 | 674.3919 | 664.0791 | 612.2625 | 587.5888 | 571.6944 | 493.7246 | 586.8493
3246.2542 | 673.6979 | 663.5128 | 612.8346 | 587.7881 | 571.9975 | 494.0912 | 586.8752
3247.2542 | 675.8378 | 662.1193 | 612.5919 | 587.0284 | 572.3494 | 494.4754 | 587.8954
3248.2542 | 676.4659 | 660.7061 | 613.5147 | 587.051 | 573.3055 | 494.8811 | 588.2913
3249.2542 | 677.2756 | 661.624 | 614.5104 | 587.3111 | 573.3321 | 494.9641 | 587.9896
3250.2542 | 675.7043 | 660.5579 | 615.1428 | 587.3325 | 573.9664 | 494.4793 | 587.7149
3251.2542 | 677.1942 | 661.074 | 615.8726 | 587.4048 | 574.3259 | 494.2667 | 587.5182
3252.2542 | 679.3085 | 661.5662 | 616.8211 | 587.9635 | 575.0941 | 494.3203 | 587.298
3253.2542 | 681.7752 | 662.9044 | 617.3294 | 588.0427 | 574.6047 | 494.7397 | 587.8577
3254.2542 | 680.8427 | 661.2686 | 616.636 | 588.1066 | 573.9557 | 494.9868 | 587.6657
3255.2542 | 679.8781 | 661.8387 | 617.4565 | 588.6342 | 573.539 | 495.4607 | 587.4368
3256.2542 | 678.7962 | 661.5352 | 618.37 | 588.7721 | 573.9694 | 494.842 | 586.6488
3257.2542 | 680.2406 | 661.4982 | 618.4999 | 589.0373 | 573.6664 | 494.7091 | 587.0859
3258.2542 | 678.2754 | 659.6226 | 617.33 | 589.4884 | 573.8694 | 495.294 | 587.1539
3259.2542 | 674.6103 | 658.6255 | 617.8465 | 589.6389 | 573.5271 | 496.0419 | 587.1937
3260.2542 | 675.6323 | 660.5826 | 618.2475 | 590.0893 | 573.8061 | 496.1495 | 587.0745
3261.2542 | 677.8724 | 662.0341 | 617.4981 | 590.2073 | 574.1189 | 496.433 | 586.7342
3262.2542 | 677.5834 | 661.1985 | 616.0029 | 590.2652 | 573.6496 | 496.6134 | 587.1845
3263.2542 | 675.6129 | 661.2389 | 616.4739 | 590.117 | 573.8089 | 497.1858 | 587.0448
3264.2542 | 673.9492 | 663.5021 | 617.8025 | 590.4426 | 573.427 | 496.4571 | 586.0793
3265.2542 | 674.3839 | 664.4607 | 619.6534 | 590.8425 | 573.5853 | 496.2204 | 586.4565
3266.2542 | 673.1992 | 662.6221 | 618.9587 | 590.555 | 573.3528 | 496.5078 | 587.1237
3267.2542 | 671.3676 | 662.0669 | 618.6773 | 590.9078 | 573.3986 | 496.6043 | 587.3622
3268.2542 | 670.8186 | 663.2653 | 619.132 | 591.019 | 573.0621 | 497.1899 | 587.1181
3269.2542 | 673.2222 | 662.9346 | 618.6911 | 591.1568 | 573.783 | 497.6905 | 587.1898
3270.2542 | 672.3423 | 663.0104 | 618.6228 | 590.6642 | 574.2435 | 497.699 | 587.7708
3271.2542 | 671.5085 | 661.3294 | 617.9462 | 590.7138 | 574.6444 | 497.8923 | 587.0782
3272.2542 | 671.3971 | 659.1089 | 616.6985 | 591.1172 | 575.0319 | 497.6246 | 586.4476
3273.2542 | 670.5816 | 657.2803 | 616.1726 | 591.5577 | 574.5994 | 497.5996 | 586.554
3274.2542 | 670.1523 | 659.1034 | 618.1134 | 591.6159 | 574.5689 | 497.8584 | 587.2994
3275.2542 | 669.8213 | 659.2199 | 618.3595 | 591.743 | 574.365 | 498.6322 | 587.4341
3276.2542 | 672.1337 | 659.3783 | 617.9119 | 591.6804 | 574.0144 | 499.4016 | 587.8806
3277.2542 | 671.5 | 657.4173 | 616.7814 | 591.4983 | 574.4823 | 499.6067 | 587.9414
3278.2542 | 671.8962 | 657.2679 | 616.5754 | 591.2562 | 574.6192 | 499.6673 | 588.6885
3279.2542 | 674.4526 | 658.0332 | 617.5816 | 591.8234 | 575.3179 | 499.7456 | 588.6633
3280.2542 | 674.5193 | 658.5513 | 617.8582 | 592.1106 | 575.6691 | 499.4038 | 588.463
3281.2542 | 675.45 | 658.2917 | 618.209 | 591.9115 | 575.1682 | 499.166 | 588.6183
3282.2542 | 676.2267 | 657.0746 | 618.1546 | 592.0981 | 575.4467 | 499.6346 | 588.5491
3283.2542 | 675.673 | 656.179 | 616.6446 | 592.4656 | 576.0059 | 499.3872 | 588.2829
3284.2542 | 675.8033 | 654.5559 | 615.259 | 591.9269 | 576.1213 | 500.4192 | 588.4699
3285.2542 | 675.9088 | 654.4572 | 615.0941 | 592.0346 | 576.6609 | 500.6216 | 588.9427
3286.2542 | 679.0905 | 655.5312 | 615.1643 | 592.3879 | 576.7618 | 500.4487 | 589.0914
3287.2542 | 678.9909 | 655.0303 | 615.7314 | 592.2121 | 576.5059 | 500.4641 | 588.9456
3288.2542 | 679.931 | 653.0816 | 613.8048 | 592.7406 | 576.8926 | 500.7192 | 589.3563
3289.2542 | 681.2924 | 653.2515 | 612.6973 | 592.8383 | 577.4448 | 501.2629 | 588.9549
3290.2542 | 679.2332 | 653.0741 | 612.0526 | 592.9307 | 578.0724 | 501.2691 | 589.2132
3291.2542 | 679.553 | 654.1132 | 612.545 | 593.1389 | 578.2334 | 501.1279 | 589.2148
3292.2542 | 677.4726 | 654.4989 | 612.659 | 592.7837 | 578.4244 | 500.9799 | 589.7633
3293.2542 | 679.0986 | 655.5275 | 612.7184 | 592.6502 | 578.8782 | 501.0904 | 590.303
3294.2542 | 678.4966 | 656.0528 | 613.7396 | 592.0344 | 578.1375 | 502.0776 | 591.2386
3295.2542 | 678.1866 | 654.6479 | 614.22 | 592.4685 | 578.6745 | 501.7671 | 591.4426
3296.2542 | 677.3394 | 653.5092 | 613.4631 | 592.8504 | 578.6549 | 502.4421 | 591.0026
3297.2542 | 675.7204 | 651.8065 | 612.6216 | 592.7011 | 579.0514 | 502.7683 | 590.5354
3298.2542 | 674.6706 | 652.989 | 613.1771 | 592.991 | 578.8206 | 502.5995 | 590.4337
3299.2542 | 673.1019 | 652.9259 | 613.8234 | 593.0262 | 578.7612 | 502.2649 | 590.0186
3300.2542 | 672.9532 | 655.782 | 614.9222 | 593.718 | 579.0872 | 502.3794 | 589.9109
3301.2542 | 672.7791 | 655.2571 | 616.013 | 594.0564 | 579.128 | 502.4472 | 590.3786
3302.2542 | 674.0091 | 655.2383 | 614.4248 | 593.6238 | 578.1745 | 502.8735 | 590.6158
3303.2542 | 674.75 | 654.8739 | 613.5508 | 593.212 | 578.1192 | 503.1464 | 590.5056
3304.2542 | 671.9975 | 653.2762 | 612.3613 | 593.4149 | 578.3629 | 503.3828 | 590.4497
3305.2542 | 670.7023 | 653.5553 | 612.171 | 593.6649 | 578.8216 | 503.5358 | 590.2133
3306.2542 | 669.6012 | 651.8093 | 611.4737 | 593.3062 | 578.9701 | 503.1501 | 591.2993
3307.2542 | 669.955 | 652.751 | 612.7793 | 593.0538 | 579.6146 | 503.3473 | 591.9743
3308.2542 | 676.8305 | 652.451 | 611.7594 | 593.8027 | 580.2497 | 503.0702 | 591.769
3309.2542 | 676.6776 | 650.7834 | 611.3084 | 594.2384 | 580.9086 | 502.9578 | 591.73
3310.2542 | 675.1434 | 649.4106 | 610.0593 | 593.9883 | 580.8925 | 503.6096 | 592.2449
3311.2542 | 674.4396 | 650.812 | 609.5016 | 593.3586 | 580.9801 | 503.9462 | 591.8596
3312.2542 | 674.0587 | 652.595 | 610.1824 | 593.5877 | 580.8552 | 504.3813 | 592.5018
3313.2542 | 672.2493 | 652.8057 | 609.4882 | 594.0858 | 581.4762 | 503.922 | 591.7158
3314.2542 | 669.1562 | 650.7717 | 607.8253 | 593.6198 | 581.2123 | 504.3257 | 592.1795
3315.2542 | 669.8557 | 648.2782 | 606.289 | 592.8151 | 580.471 | 504.7497 | 592.5362
3316.2542 | 669.9208 | 647.8607 | 606.3194 | 592.3079 | 580.7802 | 505.2519 | 592.6368
3317.2542 | 670.9917 | 647.3876 | 606.4676 | 592.7283 | 581.4258 | 505.3625 | 593.0879
3318.2542 | 669.0679 | 646.6536 | 606.3144 | 592.7 | 581.6967 | 505.3478 | 593.0389
3319.2542 | 666.757 | 646.138 | 606.9941 | 592.7176 | 582.0505 | 505.243 | 592.652
3320.2542 | 669.0345 | 648.9011 | 609.2072 | 593.2726 | 581.9525 | 504.6146 | 592.9106
3321.2542 | 672.601 | 649.4156 | 608.2173 | 592.8656 | 582.286 | 504.4805 | 592.4201
3322.2542 | 674.3748 | 649.3115 | 607.7485 | 592.6692 | 582.3829 | 505.0099 | 593.274
3323.2542 | 674.3492 | 647.7284 | 606.9698 | 592.61 | 582.4972 | 505.8191 | 593.6304
3324.2542 | 672.3307 | 646.9274 | 606.179 | 593.1245 | 583.1781 | 505.5678 | 593.3042
3325.2542 | 672.3404 | 646.755 | 606.5254 | 593.1094 | 582.6237 | 504.7473 | 592.6846
3326.2542 | 669.8269 | 646.8962 | 606.09 | 593.5721 | 583.6815 | 504.7922 | 592.306
3327.2542 | 669.1612 | 645.9643 | 605.5894 | 593.5221 | 582.116 | 505.2355 | 592.5521
3328.2542 | 667.1835 | 642.7547 | 603.2899 | 593.5754 | 582.4867 | 505.7931 | 592.2001
3329.2542 | 667.8498 | 643.8505 | 604.5998 | 593.1433 | 583.0293 | 506.5092 | 592.7671
3330.2542 | 668.7691 | 645.4593 | 605.1748 | 593.3461 | 582.9908 | 506.0657 | 592.7492
3331.2542 | 668.6916 | 645.6007 | 605.366 | 593.6896 | 582.6329 | 505.8443 | 592.9505
3332.2542 | 668.4278 | 646.0056 | 604.7002 | 593.4161 | 582.9266 | 505.8777 | 592.4169
3333.2542 | 667.648 | 648.2395 | 607.6747 | 593.7255 | 582.3805 | 506.0878 | 592.9922
3334.2542 | 668.7969 | 648.5759 | 606.9239 | 593.6884 | 581.7704 | 506.6118 | 593.0217
3335.2542 | 671.5594 | 648.0293 | 606.7067 | 594.2072 | 582.7268 | 506.886 | 593.2716
3336.2542 | 672.3235 | 648.6057 | 607.5596 | 594.2813 | 583.5502 | 506.7793 | 592.9033
3337.2542 | 672.3669 | 648.7778 | 607.9271 | 594.22 | 582.5301 | 507.0307 | 593.4122
3338.2542 | 671.4748 | 648.7369 | 607.7695 | 594.5415 | 583.2972 | 507.402 | 593.5814
3339.2542 | 671.1009 | 647.4885 | 607.0584 | 594.6633 | 584.1914 | 507.3034 | 593.1599
3340.2542 | 670.4107 | 647.264 | 607.1169 | 594.5332 | 582.7456 | 506.8337 | 592.4301
3341.2542 | 670.7595 | 647.3926 | 607.179 | 594.881 | 583.3857 | 507.2842 | 592.8692
3342.2542 | 670.7986 | 646.8859 | 606.5135 | 595.1158 | 583.5351 | 507.3945 | 592.71
3343.2542 | 668.4548 | 647.364 | 605.701 | 595.3336 | 583.3502 | 508.0289 | 592.9628
3344.2542 | 667.4524 | 645.7335 | 604.9858 | 595.0359 | 583.345 | 507.9914 | 593.3595
3345.2542 | 668.3463 | 643.7499 | 604.4057 | 594.715 | 583.0983 | 508.3924 | 593.2302
3346.2542 | 669.1355 | 642.5095 | 603.1492 | 594.5907 | 582.4936 | 508.3348 | 592.8888
3347.2542 | 668.3507 | 642.1875 | 602.7676 | 594.9387 | 581.3395 | 508.918 | 593.5985
3348.2542 | 668.4771 | 640.9229 | 601.5786 | 594.2024 | 581.8329 | 508.9273 | 593.1897
3349.2542 | 670.2049 | 642.7755 | 600.5019 | 594.3958 | 581.9611 | 508.9441 | 593.1402
3350.2542 | 670.0869 | 644.0485 | 601.0504 | 595.1294 | 580.7152 | 508.968 | 592.9728
3351.2542 | 666.131 | 641.0474 | 600.4647 | 594.7998 | 581.4146 | 509.1603 | 592.6818
3352.2542 | 666.3683 | 642.7057 | 601.9048 | 594.943 | 581.1475 | 509.2934 | 593.0023
3353.2542 | 666.3409 | 642.9876 | 603.5474 | 595.4488 | 581.0717 | 509.4257 | 593.0319
3354.2542 | 664.9421 | 642.8436 | 604.3247 | 595.3571 | 581.1135 | 509.1595 | 593.4231
3355.2542 | 665.2582 | 641.93 | 602.9614 | 595.0611 | 580.2186 | 509.2916 | 593.5445
3356.2542 | 666.2275 | 643.7186 | 603.7011 | 595.4583 | 581.2161 | 510.1437 | 593.7459
3357.2542 | 665.8623 | 644.9608 | 604.9773 | 595.2714 | 581.8475 | 510.0193 | 593.3379
3358.2542 | 664.4206 | 642.9716 | 603.3458 | 595.3112 | 581.7462 | 509.7087 | 593.6405
3359.2542 | 665.1865 | 641.5612 | 601.659 | 595.0092 | 580.8128 | 510.3464 | 593.8523
3360.2542 | 666.6142 | 640.878 | 600.9396 | 594.9403 | 580.8782 | 510.6398 | 594.1087
3361.2542 | 665.8707 | 641.3546 | 601.1917 | 595.0052 | 580.9039 | 510.6442 | 593.6825
3362.2542 | 664.7832 | 643.3633 | 602.1373 | 595.297 | 580.8759 | 510.8337 | 594.1284
3363.2542 | 665.2386 | 644.3854 | 602.9405 | 595.8001 | 580.5131 | 510.9723 | 594.1099
3364.2542 | 666.8146 | 646.0181 | 603.2127 | 596.2303 | 580.5512 | 510.7276 | 594.2474
3365.2542 | 667.5497 | 645.2856 | 602.2013 | 595.9255 | 580.3613 | 511.4139 | 594.5869
3366.2542 | 666.6736 | 645.5268 | 602.1899 | 595.9762 | 580.6763 | 511.5112 | 594.8808
3367.2542 | 665.4196 | 646.1085 | 603.548 | 596.4909 | 581.8034 | 512.1199 | 595.3522
3368.2542 | 662.7593 | 645.7716 | 603.7126 | 596.1221 | 581.0344 | 511.5406 | 595.7978
3369.2542 | 665.3962 | 646.1394 | 604.6732 | 596.8437 | 582.0525 | 511.5238 | 595.7711
3370.2542 | 666.9003 | 649.1523 | 605.4854 | 597.013 | 581.8243 | 511.6974 | 595.7711
3371.2542 | 667.3141 | 648.9918 | 605.2696 | 597.0761 | 582.0289 | 512.2456 | 596.1175
3372.2542 | 668.7988 | 647.7132 | 604.2043 | 596.8554 | 581.8064 | 511.8911 | 595.8778
3373.2542 | 668.5741 | 645.7968 | 602.876 | 597.5273 | 581.8772 | 511.5737 | 595.4048
3374.2542 | 667.1467 | 644.7092 | 603.2403 | 597.5786 | 581.3307 | 512.0372 | 595.7894
3375.2542 | 663.3808 | 644.6386 | 603.7695 | 597.6716 | 582.0813 | 512.5853 | 595.9903
3376.2542 | 661.7566 | 645.7382 | 604.1954 | 597.5968 | 581.9947 | 512.5897 | 596.1929
3377.2542 | 661.4585 | 646.724 | 604.4197 | 597.7125 | 582.9463 | 512.5587 | 596.1375
3378.2542 | 661.6634 | 645.2246 | 604.1705 | 597.4899 | 582.9387 | 512.505 | 596.2822
3379.2542 | 663.0639 | 645.7116 | 604.4978 | 597.8371 | 582.4956 | 513.0114 | 596.3099
3380.2542 | 664.0981 | 646.7198 | 605.4362 | 597.8431 | 581.3894 | 513.1253 | 596.6439
3381.2542 | 665.5337 | 646.3036 | 605.2835 | 598.0434 | 581.1858 | 513.5052 | 596.4227
3382.2542 | 663.8014 | 646.6881 | 605.1137 | 598.1951 | 582.5337 | 513.4225 | 596.0435
3383.2542 | 664.5948 | 647.9756 | 605.7472 | 598.4869 | 581.6842 | 513.5777 | 596.1421
3384.2542 | 663.262 | 646.7124 | 604.8736 | 599.001 | 581.8185 | 513.5467 | 596.2523
3385.2542 | 664.1465 | 647.1754 | 604.6561 | 598.6386 | 582.0196 | 513.9926 | 596.3811
3386.2542 | 666.2833 | 648.0555 | 604.4824 | 598.3342 | 581.9544 | 513.8023 | 596.5701
3387.2542 | 666.5884 | 648.0975 | 604.1251 | 598.8741 | 582.3448 | 514.1419 | 596.8809
3388.2542 | 665.6606 | 646.7909 | 602.1625 | 599.0409 | 582.8167 | 514.4919 | 596.5556
3389.2542 | 666.9052 | 645.7527 | 600.9236 | 599.2284 | 582.7263 | 514.3692 | 596.5263
3390.2542 | 669.2209 | 644.7681 | 600.2348 | 599.0822 | 582.0975 | 514.6439 | 596.6863
3391.2542 | 668.5301 | 644.3673 | 601.7281 | 599.4398 | 582.9292 | 514.5269 | 596.7861
3392.2542 | 665.8062 | 642.8361 | 602.0954 | 599.5588 | 582.8808 | 514.6215 | 596.6693
3393.2542 | 665.2747 | 643.8507 | 602.142 | 599.9928 | 581.9623 | 514.5526 | 596.6912
3394.2542 | 664.272 | 645.1116 | 603.5212 | 599.5121 | 582.343 | 515.0022 | 597.0065
3395.2542 | 665.2055 | 644.5479 | 602.9633 | 599.6052 | 581.3771 | 515.1709 | 597.0099
3396.2542 | 665.7636 | 644.1071 | 603.5339 | 599.6491 | 581.7631 | 515.7472 | 597.0268
3397.2542 | 667.8985 | 645.1347 | 604.5101 | 599.3194 | 581.4083 | 515.7175 | 596.9812
3398.2542 | 669.0678 | 643.9717 | 603.5037 | 598.8242 | 580.373 | 515.929 | 597.3485
3399.2542 | 671.3154 | 643.6509 | 602.5216 | 599.5848 | 579.9702 | 516.1332 | 597.3776
3400.2542 | 672.4376 | 643.463 | 601.4364 | 599.793 | 580.5627 | 516.1844 | 597.2988
3401.2542 | 671.2644 | 641.72 | 600.9034 | 598.7058 | 580.1674 | 515.59 | 596.7379
3402.2542 | 671.2534 | 640.9121 | 600.5716 | 598.7865 | 580.6815 | 516.0168 | 597.4924
3403.2542 | 671.1872 | 639.9472 | 600.1742 | 598.9523 | 579.9625 | 516.0764 | 597.4776
3404.2542 | 669.8849 | 638.436 | 599.9994 | 599.2916 | 580.4088 | 515.7933 | 597.0552
3405.2542 | 670.1027 | 637.7571 | 599.5011 | 599.499 | 580.9173 | 515.7611 | 596.5441
3406.2542 | 668.1085 | 637.5222 | 599.0194 | 599.5178 | 580.6591 | 516.1006 | 596.8114
3407.2542 | 668.4798 | 638.1442 | 597.922 | 599.0891 | 580.1088 | 515.9803 | 596.7511
3408.2542 | 668.3583 | 637.1334 | 596.9742 | 599.1655 | 580.29 | 515.9086 | 596.6482
3409.2542 | 666.742 | 635.5553 | 595.9571 | 599.6734 | 580.1673 | 515.8642 | 596.2421
3410.2542 | 666.8149 | 635.5765 | 595.5043 | 599.0739 | 579.176 | 515.7709 | 596.2287
3411.2542 | 667.1175 | 635.8154 | 595.9791 | 599.2539 | 578.7649 | 515.9975 | 596.574
3412.2542 | 668.0819 | 635.7158 | 596.8914 | 599.4184 | 578.938 | 516.3956 | 597.0979
3413.2542 | 665.6665 | 633.722 | 595.8865 | 599.1116 | 579.881 | 516.5786 | 596.9083
3414.2542 | 662.2178 | 632.85 | 597.4421 | 599.3352 | 579.2875 | 516.6925 | 597.0076
3415.2542 | 662.1822 | 636.3636 | 600.4515 | 599.2999 | 580.3466 | 516.9207 | 597.6703
3416.2542 | 664.7025 | 639.591 | 601.2724 | 600.0147 | 580.598 | 516.6475 | 597.6596
3417.2542 | 666.588 | 641.6004 | 600.4559 | 600.1225 | 580.2957 | 516.8918 | 597.4909
3418.2542 | 669.1949 | 643.4017 | 602.3552 | 600.7454 | 580.0645 | 516.9308 | 597.5241
3419.2542 | 669.6794 | 643.176 | 601.6727 | 600.5533 | 580.5984 | 516.6394 | 597.4324
3420.2542 | 667.8527 | 642.0719 | 602.0559 | 601.0088 | 580.3494 | 517.0878 | 597.3592
3421.2542 | 666.1889 | 642.4946 | 601.953 | 601.0556 | 580.3391 | 517.3999 | 597.4014
3422.2542 | 665.03 | 643.3895 | 601.7388 | 601.0635 | 580.437 | 517.604 | 597.6635
3423.2542 | 666.2271 | 643.5415 | 602.0122 | 600.7388 | 581.1989 | 517.8365 | 597.8769
3424.2542 | 668.648 | 644.4872 | 601.8737 | 600.4885 | 581.2271 | 517.8414 | 597.9379
3425.2542 | 668.9726 | 644.673 | 602.5047 | 600.7154 | 581.159 | 517.9919 | 598.05
3426.2542 | 668.4797 | 644.0765 | 601.7666 | 601.2074 | 581.6421 | 518.2433 | 598.3216
3427.2542 | 666.2166 | 642.5414 | 601.0012 | 601.6769 | 581.0151 | 518.4529 | 598.3558
3428.2542 | 664.7034 | 642.2309 | 601.3592 | 600.8035 | 581.8029 | 518.6162 | 598.8494
3429.2542 | 666.705 | 643.0173 | 601.3615 | 601.0513 | 581.8955 | 518.2265 | 598.806
3430.2542 | 670.0429 | 641.943 | 599.8808 | 601.248 | 582.0427 | 518.3302 | 598.7313
3431.2542 | 671.0486 | 642.3594 | 599.5605 | 601.8345 | 581.7968 | 518.3427 | 598.4589
3432.2542 | 667.8659 | 643.9942 | 601.5033 | 602.3559 | 582.1174 | 518.3209 | 598.909
3433.2542 | 665.7577 | 643.3536 | 600.9281 | 601.9795 | 581.5879 | 518.7892 | 599.2283
3434.2542 | 666.5993 | 642.4399 | 600.4402 | 601.7212 | 581.428 | 518.9342 | 599.0164
3435.2542 | 666.2631 | 642.4341 | 600.2262 | 601.6857 | 581.9436 | 518.7655 | 598.991
3436.2542 | 665.1862 | 641.8664 | 600.7846 | 600.8473 | 581.6051 | 518.9089 | 599.2095
3437.2542 | 663.6699 | 639.6385 | 599.0806 | 600.575 | 582.1123 | 519.6659 | 599.2183
3438.2542 | 663.9194 | 640.0122 | 599.8045 | 600.9754 | 581.1834 | 519.458 | 599.2358
3439.2542 | 663.624 | 639.9676 | 599.7351 | 601.0948 | 580.6603 | 519.3799 | 599.3314
3440.2542 | 666.4665 | 639.4148 | 600.0334 | 601.1214 | 581.2001 | 519.5872 | 599.1909
3441.2542 | 667.4339 | 638.8397 | 599.8312 | 600.6532 | 581.0807 | 520.0008 | 598.9079
3442.2542 | 668.7038 | 639.4238 | 600.3637 | 600.9179 | 581.1012 | 520.5825 | 598.8672
3443.2542 | 671.2143 | 639.2375 | 600.3757 | 601.1307 | 580.7875 | 520.7901 | 599.0311
3444.2542 | 672.3605 | 641.098 | 600.3695 | 601.279 | 580.5219 | 520.8688 | 599.0305
3445.2542 | 673.1051 | 641.0933 | 600.42 | 601.5183 | 580.6635 | 521.1231 | 599.0001
3446.2542 | 672.0023 | 642.1512 | 600.6358 | 601.251 | 580.6893 | 520.7333 | 598.8958
3447.2542 | 672.2146 | 641.8904 | 600.02 | 601.5388 | 580.8664 | 521.1292 | 598.8954
3448.2542 | 668.9862 | 642.5369 | 600.6518 | 602.8235 | 580.8238 | 520.9632 | 598.6373
3449.2542 | 666.106 | 644.3771 | 602.4734 | 603.5382 | 581.6614 | 521.4948 | 598.8471
3450.2542 | 663.1565 | 643.6708 | 602.8111 | 603.0247 | 581.4807 | 521.9198 | 599.47
3451.2542 | 665.5583 | 646.2321 | 603.3023 | 603.7904 | 581.6853 | 522.4489 | 599.832
3452.2542 | 668.3778 | 650.4095 | 605.6768 | 604.3508 | 581.8034 | 522.1888 | 599.9539
3453.2542 | 671.1712 | 650.9557 | 605.6333 | 604.496 | 581.43 | 522.1714 | 600.2125
3454.2542 | 672.5579 | 650.6995 | 605.0374 | 604.8583 | 581.817 | 522.4122 | 599.8374
3455.2542 | 673.1543 | 648.9053 | 603.6946 | 604.2135 | 581.4978 | 522.66 | 599.6316
3456.2542 | 672.3785 | 648.284 | 603.8681 | 603.9644 | 580.856 | 522.77 | 599.8918
3457.2542 | 671.614 | 646.5914 | 602.7464 | 605.0901 | 581.4391 | 522.5635 | 599.8101
3458.2542 | 667.8126 | 643.2922 | 601.3976 | 604.0816 | 581.0343 | 522.9063 | 599.676
3459.2542 | 666.5141 | 642.3414 | 601.4513 | 605.0175 | 581.0388 | 523.099 | 599.4114
3460.2542 | 665.4739 | 641.8849 | 600.7694 | 604.6264 | 581.3172 | 523.0545 | 600.0361
3461.2542 | 664.2433 | 642.7689 | 601.1422 | 604.7555 | 580.9949 | 522.7691 | 599.9198
3462.2542 | 666.1928 | 642.0018 | 600.7911 | 605.0225 | 581.7372 | 523.2103 | 600.2489
3463.2542 | 666.8295 | 639.4968 | 599.2633 | 605.0942 | 580.9742 | 523.2328 | 600.0478
3464.2542 | 667.1403 | 639.2807 | 598.5819 | 606.0799 | 580.8074 | 523.0625 | 599.9283
3465.2542 | 666.7537 | 638.1966 | 598.1475 | 605.9798 | 581.5935 | 523.1043 | 599.8549
3466.2542 | 666.4054 | 637.5571 | 598.2603 | 606.0512 | 580.8728 | 523.4637 | 599.0079
3467.2542 | 665.7487 | 638.7558 | 599.0873 | 606.886 | 581.9794 | 523.6008 | 599.3412
3468.2542 | 665.1168 | 639.5729 | 598.9481 | 606.248 | 581.4726 | 523.2245 | 599.0784
3469.2542 | 666.9925 | 640.3282 | 598.483 | 607.4553 | 581.5878 | 523.5202 | 599.2206
3470.2542 | 666.8806 | 640.6065 | 599.2058 | 608.2766 | 581.3339 | 524.4511 | 600.2792
3471.2542 | 667.1231 | 641.7947 | 600.0152 | 608.5351 | 581.4469 | 524.3173 | 599.8065
3472.2542 | 668.6063 | 644.3441 | 602.0157 | 608.7765 | 581.2273 | 524.5622 | 600.2521
3473.2542 | 669.5773 | 644.3743 | 603.1017 | 609.5841 | 581.6072 | 524.7343 | 600.8939
3474.2542 | 667.5858 | 643.7255 | 603.9436 | 610.4993 | 581.9826 | 524.8723 | 600.7907
3475.2542 | 665.4347 | 643.0664 | 603.1211 | 609.4702 | 581.5369 | 525.2242 | 600.8473
3476.2542 | 664.843 | 644.6326 | 604.3188 | 609.9329 | 581.6292 | 525.9227 | 601.5018
3477.2542 | 666.226 | 649.3421 | 605.7589 | 610.7796 | 581.9195 | 525.8638 | 601.4724
3478.2542 | 668.3467 | 650.1649 | 606.7469 | 610.4609 | 582.1464 | 525.6488 | 601.7606
3479.2542 | 668.4173 | 649.2268 | 606.2466 | 611.5563 | 581.8051 | 525.8766 | 601.7461
3480.2542 | 667.9295 | 649.5882 | 606.4025 | 612.0242 | 581.7625 | 525.9879 | 601.9577
3481.2542 | 669.2252 | 650.6453 | 606.7082 | 612.4952 | 582.1083 | 526.1301 | 601.6885
3482.2542 | 672.0917 | 652.707 | 606.9275 | 612.851 | 581.2423 | 526.0961 | 601.6829
3483.2542 | 678.3863 | 652.5924 | 606.3291 | 612.7644 | 581.9605 | 526.1682 | 602.1312
3484.2542 | 677.341 | 650.8526 | 605.3381 | 612.778 | 581.5976 | 526.4319 | 602.2296
3485.2542 | 675.601 | 649.7195 | 604.6978 | 614.3478 | 582.5927 | 526.5699 | 602.7537
3486.2542 | 675.0787 | 650.4106 | 605.896 | 614.501 | 582.2348 | 526.7023 | 602.8505
3487.2542 | 679.0798 | 649.9975 | 604.9973 | 613.5165 | 582.2805 | 526.8588 | 602.488
3488.2542 | 677.6882 | 647.5046 | 602.5964 | 613.819 | 581.815 | 526.7789 | 602.5177
3489.2542 | 676.7768 | 646.3222 | 599.5339 | 613.2916 | 582.2647 | 526.8632 | 602.4118
3490.2542 | 674.3259 | 643.2161 | 598.3632 | 614.2273 | 581.9128 | 526.7237 | 602.2412
3491.2542 | 671.3908 | 641.9332 | 598.1386 | 612.3286 | 581.7936 | 527.1019 | 602.4992
3492.2542 | 668.321 | 640.1407 | 596.6008 | 611.7869 | 581.4276 | 527.5728 | 602.5203
3493.2542 | 668.0586 | 639.9571 | 596.0208 | 611.829 | 581.4532 | 527.7929 | 602.1447
3494.2542 | 670.4015 | 641.3971 | 597.0179 | 612.2415 | 581.677 | 527.7995 | 602.6283
3495.2542 | 673.047 | 640.6533 | 596.8918 | 612.7246 | 581.4602 | 528.3081 | 602.5869
3496.2542 | 672.1179 | 637.9248 | 595.8017 | 612.2488 | 581.8283 | 528.6114 | 602.6447
3497.2542 | 669.5574 | 636.6912 | 595.0127 | 612.1138 | 581.9789 | 528.551 | 602.5946
3498.2542 | 667.5432 | 637.72 | 596.114 | 611.4281 | 581.9842 | 528.6411 | 602.5884
3499.2542 | 669.4661 | 637.9526 | 596.5376 | 610.8574 | 582.68 | 528.5776 | 602.7453
3500.2542 | 670.1393 | 636.5869 | 595.7762 | 610.9397 | 582.274 | 528.2673 | 602.2145
3501.2542 | 669.935 | 636.6328 | 595.0821 | 611.1266 | 580.9995 | 528.8197 | 601.9625
3502.2542 | 670.7228 | 636.8049 | 595.5489 | 611.2582 | 581.611 | 529.0004 | 601.6998
3503.2542 | 671.144 | 637.3381 | 595.9381 | 610.4761 | 582.0251 | 529.5563 | 602.0564
3504.2542 | 671.2699 | 637.5187 | 595.8156 | 609.7995 | 581.863 | 529.4219 | 601.4861
3505.2542 | 672.8265 | 639.7613 | 596.4881 | 610.0074 | 582.3708 | 529.3768 | 601.5662
3506.2542 | 672.4167 | 639.8879 | 596.2382 | 609.2272 | 582.1545 | 529.6905 | 602.0825
3507.2542 | 671.3004 | 638.0551 | 595.6653 | 610.079 | 581.9744 | 529.7656 | 601.813
3508.2542 | 669.4616 | 636.4505 | 595.2325 | 609.1273 | 581.899 | 529.8771 | 602.0773
3509.2542 | 669.1533 | 634.3677 | 593.8805 | 609.3669 | 581.9944 | 529.8271 | 601.3544
3510.2542 | 667.0407 | 633.5158 | 593.1845 | 610.235 | 581.6743 | 530.3306 | 601.8783
3511.2542 | 668.8005 | 634.5299 | 594.0042 | 609.6532 | 581.5379 | 530.52 | 601.9771
3512.2542 | 673.983 | 637.7666 | 594.8176 | 610.1711 | 581.8356 | 531.1131 | 602.7948
3513.2542 | 675.235 | 637.818 | 594.4786 | 609.3096 | 581.6977 | 531.0011 | 602.7518
3514.2542 | 677.1323 | 638.3991 | 594.8346 | 610.8671 | 581.4428 | 531.2315 | 602.4766
3515.2542 | 676.7574 | 638.3161 | 594.3046 | 610.4246 | 581.9637 | 531.4458 | 602.5891
3516.2542 | 674.0041 | 638.5159 | 594.7616 | 610.992 | 582.1962 | 531.5916 | 602.1482
3517.2542 | 673.5113 | 639.9717 | 594.9988 | 608.87 | 581.8144 | 531.6875 | 602.2122
3518.2542 | 672.9278 | 639.4764 | 595.8381 | 610.7912 | 582.2281 | 531.9319 | 602.4072
3519.2542 | 673.2956 | 640.1871 | 596.0902 | 609.7258 | 581.9084 | 532.3516 | 602.7191
3520.2542 | 674.444 | 639.2166 | 595.7755 | 611.2788 | 581.226 | 532.3501 | 602.5861
3521.2542 | 674.6834 | 637.5684 | 594.5014 | 611.5768 | 581.6099 | 532.3256 | 602.3305
3522.2542 | 672.512 | 635.0644 | 593.335 | 612.1865 | 581.7168 | 532.3113 | 602.4666
3523.2542 | 673.3869 | 636.1489 | 593.7781 | 611.7649 | 581.1 | 532.0682 | 602.8586
3524.2542 | 671.8033 | 637.3732 | 594.8816 | 612.5304 | 581.9258 | 531.9297 | 602.4956
3525.2542 | 669.4287 | 637.8447 | 596.6448 | 610.7925 | 581.5976 | 532.6228 | 603.2844
3526.2542 | 670.6019 | 638.5233 | 596.4491 | 612.4643 | 581.0689 | 533.0821 | 602.904
3527.2542 | 670.0334 | 639.5924 | 596.1622 | 611.5245 | 580.9942 | 533.3824 | 602.5086
3528.2542 | 671.8403 | 641.6102 | 597.2934 | 613.5596 | 581.7433 | 533.538 | 602.8284
3529.2542 | 674.3156 | 641.8539 | 598.5423 | 611.7553 | 581.5434 | 533.3207 | 602.6235
3530.2542 | 675.6114 | 642.8754 | 599.3655 | 613.0017 | 581.709 | 533.8258 | 603.2549
3531.2542 | 673.6266 | 642.2658 | 598.7155 | 612.1371 | 581.3365 | 533.8996 | 603.3676
3532.2542 | 672.4577 | 642.9693 | 598.909 | 613.4158 | 581.7205 | 534.254 | 603.4604
3533.2542 | 672.9645 | 643.2945 | 599.3135 | 612.8384 | 581.3838 | 534.3545 | 603.2563
3534.2542 | 672.8631 | 644.2734 | 599.6163 | 613.3043 | 581.5411 | 534.6354 | 603.5491
3535.2542 | 671.8288 | 642.5832 | 599.1478 | 613.7373 | 580.8613 | 534.924 | 603.392
3536.2542 | 669.8043 | 640.6118 | 597.5288 | 613.5331 | 581.0314 | 534.7567 | 603.4049
3537.2542 | 667.9725 | 639.1161 | 596.3786 | 613.4468 | 581.6553 | 534.8155 | 602.9496
3538.2542 | 668.645 | 640.583 | 596.7829 | 614.3818 | 581.411 | 534.8829 | 603.3174
3539.2542 | 669.3503 | 642.2918 | 597.9428 | 614.6065 | 581.6875 | 534.9016 | 603.2311
3540.2542 | 670.4025 | 645.0868 | 599.5746 | 614.624 | 581.6365 | 535.3064 | 603.7555
3541.2542 | 671.6114 | 645.0524 | 598.8109 | 613.9398 | 580.6423 | 535.3442 | 604.0422
3542.2542 | 670.3431 | 643.7404 | 597.8103 | 615.4403 | 580.8655 | 535.2035 | 603.6929
3543.2542 | 667.6607 | 641.9101 | 596.5056 | 615.6352 | 580.6952 | 535.5405 | 603.8679
3544.2542 | 665.4916 | 640.6138 | 596.4705 | 615.3586 | 580.5514 | 536.2085 | 604.0577
3545.2542 | 664.7584 | 640.7423 | 597.6029 | 614.0429 | 580.9101 | 536.9026 | 604.2884
3546.2542 | 668.6607 | 643.0033 | 598.8895 | 613.6275 | 581.0167 | 537.5024 | 605.1781
3547.2542 | 669.5709 | 643.7989 | 600.4394 | 614.6488 | 581.1847 | 537.7717 | 605.322
3548.2542 | 668.946 | 645.6817 | 603.6652 | 616.9801 | 581.4604 | 538.4613 | 605.9229
3549.2542 | 664.7371 | 645.7409 | 604.9257 | 615.5273 | 580.9905 | 537.8975 | 605.7821
3550.2542 | 665.5756 | 645.5932 | 605.7349 | 617.0504 | 581.4487 | 538.5924 | 605.6475
3551.2542 | 665.757 | 644.8502 | 605.8417 | 617.1935 | 581.9712 | 539.1558 | 605.806
3552.2542 | 666.6885 | 644.3012 | 604.8685 | 618.3924 | 581.8196 | 539.4248 | 605.6281
3553.2542 | 666.8462 | 645.0971 | 604.4392 | 619.3422 | 582.4068 | 539.8346 | 605.7669
3554.2542 | 668.7955 | 646.5953 | 605.0638 | 619.0645 | 581.6401 | 540.1194 | 606.5138
3555.2542 | 668.7246 | 646.3444 | 604.3656 | 617.8519 | 582.0696 | 540.236 | 606.4523
3556.2542 | 668.8531 | 644.9809 | 603.4748 | 618.0732 | 582.0114 | 540.4533 | 606.3216
3557.2542 | 670.8462 | 645.785 | 603.9083 | 619.8641 | 582.5781 | 540.9472 | 606.8275
3558.2542 | 669.2913 | 644.5204 | 604.2457 | 618.5566 | 581.8062 | 540.7719 | 606.5444
3559.2542 | 670.7773 | 644.8334 | 604.8959 | 618.8359 | 581.6328 | 540.7954 | 606.2296
3560.2542 | 671.1552 | 643.6586 | 604.2003 | 617.0095 | 581.9119 | 540.9824 | 606.4898
3561.2542 | 670.533 | 640.9638 | 601.0574 | 619.7163 | 581.1619 | 541.1056 | 606.3834
3562.2542 | 667.829 | 638.0038 | 598.3755 | 620.3559 | 582.4652 | 540.961 | 606.1623
3563.2542 | 668.061 | 638.8839 | 598.0174 | 618.8196 | 582.5315 | 540.8539 | 606.3968
3564.2542 | 667.3313 | 639.1277 | 597.1575 | 616.0733 | 582.4082 | 540.8652 | 605.7527
3565.2542 | 667.2613 | 636.5838 | 595.4396 | 616.029 | 582.061 | 540.7892 | 605.2179
3566.2542 | 668.767 | 636.4233 | 595.9959 | 618.1708 | 582.0317 | 541.5943 | 605.6094
3567.2542 | 667.3391 | 637.7907 | 596.249 | 616.689 | 582.1151 | 541.4851 | 605.1768
3568.2542 | 666.5318 | 637.678 | 596.8907 | 618.0998 | 581.6964 | 542.0029 | 605.1421
3569.2542 | 667.4545 | 636.9042 | 595.4828 | 616.7718 | 581.689 | 542.2685 | 605.4071
3570.2542 | 669.1783 | 636.5027 | 594.3336 | 617.6676 | 580.8207 | 542.5168 | 605.211
3571.2542 | 668.7221 | 635.1836 | 594.3183 | 618.4142 | 581.6717 | 542.8666 | 605.0839
3572.2542 | 668.7903 | 635.6889 | 594.1914 | 617.0805 | 580.8163 | 542.3888 | 604.3831
3573.2542 | 669.9709 | 635.1944 | 592.0045 | 615.2884 | 580.8313 | 542.0888 | 604.0423
3574.2542 | 671.2494 | 634.7956 | 591.095 | 616.2593 | 581.181 | 542.5453 | 603.9747
3575.2542 | 669.5875 | 633.144 | 591.2569 | 616.9968 | 580.4187 | 543.0173 | 604.059
3576.2542 | 670.0946 | 632.6179 | 591.3734 | 616.7372 | 581.4685 | 542.9428 | 603.8108
3577.2542 | 669.8567 | 633.4253 | 591.812 | 616.9277 | 581.4587 | 542.8034 | 604.0608
3578.2542 | 668.7756 | 632.6706 | 591.3248 | 617.3108 | 580.7104 | 543.1347 | 604.1653
3579.2542 | 670.232 | 633.0149 | 591.0759 | 618.8081 | 580.977 | 543.6296 | 604.1983
3580.2542 | 670.4557 | 633.7937 | 591.5111 | 619.5743 | 581.0355 | 543.759 | 604.0577
3581.2542 | 670.5678 | 636.0701 | 593.654 | 620.5262 | 581.361 | 544.2925 | 605.0243
3582.2542 | 666.29 | 634.4064 | 593.2782 | 619.2415 | 580.8097 | 543.9261 | 604.1975
3583.2542 | 666.3161 | 635.9752 | 594.6644 | 618.7352 | 580.7755 | 544.1808 | 605.1393
3584.2542 | 667.9498 | 637.768 | 596.2941 | 619.3211 | 580.7298 | 544.6284 | 605.4649
3585.2542 | 667.1378 | 636.6346 | 595.2107 | 617.5635 | 580.3722 | 544.8609 | 605.5282
3586.2542 | 665.0051 | 634.3804 | 593.6117 | 616.8331 | 580.1797 | 544.828 | 604.9969
3587.2542 | 668.2893 | 635.5049 | 593.1267 | 617.6359 | 580.2406 | 545.0287 | 604.9244
3588.2542 | 670.0604 | 635.2309 | 593.7764 | 618.7914 | 581.0009 | 545.296 | 604.7974
3589.2542 | 667.2281 | 633.1814 | 592.334 | 619.9367 | 580.9746 | 545.4178 | 604.5628
3590.2542 | 664.312 | 631.628 | 592.7948 | 619.4829 | 581.0488 | 545.3339 | 604.3669
3591.2542 | 661.5104 | 632.6939 | 593.1711 | 618.3391 | 580.0838 | 545.8588 | 604.7104
3592.2542 | 664.0583 | 636.7564 | 594.3108 | 618.4938 | 580.647 | 545.8211 | 604.9579
3593.2542 | 666.0198 | 638.1415 | 594.7044 | 618.8003 | 580.6585 | 546.2744 | 605.2137
3594.2542 | 664.8414 | 637.1451 | 594.0786 | 619.7019 | 580.8381 | 546.2482 | 605.0631
3595.2542 | 664.8394 | 638.7574 | 598.0019 | 620.9824 | 581.3617 | 546.5491 | 605.4623
3596.2542 | 664.1112 | 638.4722 | 599.569 | 619.8622 | 581.3291 | 546.468 | 605.2273
3597.2542 | 663.1636 | 639.6136 | 601.1155 | 622.5998 | 581.4131 | 546.7856 | 605.6209
3598.2542 | 660.1758 | 638.4468 | 600.7271 | 622.8696 | 581.6697 | 547.4154 | 606.2542
3599.2542 | 659.0098 | 639.1909 | 601.168 | 620.1241 | 581.6889 | 547.6014 | 606.1675
3600.2542 | 658.6375 | 640.5644 | 603.0943 | 622.5426 | 581.7597 | 547.9336 | 606.6666
3601.2542 | 662.2166 | 641.3473 | 602.1482 | 621.6397 | 581.5138 | 548.0208 | 606.4035
3602.2542 | 663.0983 | 640.1675 | 600.5408 | 619.2882 | 581.2308 | 548.0168 | 606.6926
3603.2542 | 666.8807 | 639.9053 | 599.736 | 622.4209 | 581.3313 | 548.2748 | 606.6707
3604.2542 | 666.7265 | 639.3043 | 599.0582 | 620.923 | 580.6756 | 548.2816 | 606.7645
3605.2542 | 667.0416 | 640.2647 | 598.773 | 620.3489 | 580.6243 | 548.7158 | 606.6097
3606.2542 | 666.1997 | 639.665 | 597.1525 | 621.0482 | 581.2742 | 548.4589 | 606.519
3607.2542 | 665.9318 | 639.4865 | 596.5635 | 622.7227 | 581.6031 | 548.597 | 606.5874
3608.2542 | 665.6081 | 639.4638 | 596.0886 | 621.6476 | 581.2259 | 548.4761 | 606.0705
3609.2542 | 664.3999 | 639.0506 | 594.3368 | 623.6429 | 580.9703 | 548.3955 | 605.7134
3610.2542 | 665.3341 | 640.489 | 595.5515 | 624.8256 | 581.5363 | 548.6685 | 606.3975
3611.2542 | 664.4967 | 642.5697 | 597.7199 | 624.1654 | 581.6272 | 548.941 | 607.3731
3612.2542 | 664.2872 | 643.481 | 597.7401 | 625.5456 | 581.4881 | 549.213 | 607.3888
3613.2542 | 664.5691 | 644.0119 | 598.0439 | 625.3715 | 581.1233 | 549.5973 | 607.6914
3614.2542 | 663.5835 | 643.3311 | 598.0274 | 625.9349 | 581.4936 | 550.1973 | 608.0008
3615.2542 | 661.6515 | 640.5803 | 595.959 | 621.8157 | 580.9719 | 550.3522 | 607.4853
3616.2542 | 661.124 | 641.081 | 596.2197 | 625.6094 | 581.1352 | 550.6996 | 607.7113
3617.2542 | 658.2252 | 640.7919 | 596.4967 | 624.6256 | 581.4153 | 551.044 | 608.1381
3618.2542 | 663.5724 | 646.0074 | 598.5933 | 624.6559 | 581.761 | 551.0706 | 608.5181
3619.2542 | 665.963 | 648.9017 | 599.3694 | 624.9086 | 581.7359 | 551.0948 | 608.5022
3620.2542 | 666.6762 | 652.0412 | 600.6726 | 626.3669 | 581.6045 | 551.6427 | 608.9012
3621.2542 | 667.1972 | 653.4418 | 602.3882 | 626.1151 | 581.9756 | 551.4392 | 608.3174
3622.2542 | 668.0525 | 652.878 | 602.1018 | 629.13 | 582.0399 | 551.456 | 609.5761
3623.2542 | 667.787 | 650.8295 | 601.5401 | 628.7774 | 582.0925 | 550.998 | 609.8441
3624.2542 | 669.4851 | 649.9382 | 600.2037 | 628.6956 | 581.7614 | 551.1475 | 609.8118
3625.2542 | 668.0106 | 648.9788 | 601.2632 | 627.3938 | 581.4721 | 551.3723 | 609.8385
3626.2542 | 665.9084 | 649.0962 | 602.0081 | 627.0102 | 581.6463 | 551.5366 | 609.3838
3627.2542 | 666.9665 | 649.9961 | 601.8839 | 627.5482 | 581.509 | 552.0261 | 610.0935
3628.2542 | 668.5682 | 650.2825 | 601.9538 | 628.2917 | 581.7576 | 552.2155 | 610.0999
3629.2542 | 668.1546 | 650.314 | 601.8893 | 627.1287 | 582.0481 | 551.8223 | 610.0447
3630.2542 | 668.1372 | 650.119 | 601.1916 | 629.4811 | 582.1281 | 552.4082 | 609.6477
3631.2542 | 667.565 | 647.9656 | 600.2324 | 629.8134 | 582.0925 | 552.395 | 609.8461
3632.2542 | 669.9286 | 648.5968 | 600.6167 | 628.4398 | 582.2157 | 552.7383 | 610.3054
3633.2542 | 669.694 | 652.5217 | 602.961 | 627.4121 | 582.2114 | 553.1181 | 610.2896
3634.2542 | 669.2238 | 651.9543 | 603.4123 | 627.7003 | 582.3959 | 552.9572 | 610.1427
3635.2542 | 669.958 | 650.4292 | 602.7539 | 630.1468 | 582.268 | 553.3321 | 610.5091
3636.2542 | 668.3646 | 647.0831 | 600.3628 | 628.5455 | 582.1845 | 553.4324 | 609.9417
3637.2542 | 669.8722 | 645.9743 | 599.3637 | 630.5157 | 582.1762 | 553.3007 | 610.2371
3638.2542 | 670.326 | 646.1985 | 598.7589 | 631.2636 | 582.0182 | 552.8948 | 610.5905
3639.2542 | 670.1609 | 643.6518 | 596.9917 | 628.6085 | 581.6542 | 553.0794 | 610.4035
3640.2542 | 666.8107 | 641.0083 | 594.1105 | 629.9821 | 581.4221 | 553.086 | 609.9009
3641.2542 | 668.4496 | 645.1193 | 596.6371 | 628.6461 | 581.535 | 553.3481 | 609.5998
3642.2542 | 667.8299 | 644.5391 | 596.8336 | 628.1433 | 581.6573 | 553.357 | 609.1462
3643.2542 | 666.6185 | 642.5786 | 596.0989 | 625.5089 | 581.1889 | 553.5026 | 608.9089
3644.2542 | 669.0061 | 645.3779 | 595.9662 | 627.3621 | 581.827 | 553.9102 | 608.6
3645.2542 | 671.3687 | 644.6966 | 595.4711 | 626.5492 | 581.6699 | 554.0253 | 609.0787
3646.2542 | 672.0904 | 643.7129 | 595.9791 | 627.7011 | 581.8916 | 554.6556 | 609.019
3647.2542 | 672.8601 | 643.3177 | 594.6041 | 628.862 | 581.9553 | 554.9066 | 609.3059
3648.2542 | 670.3136 | 642.7149 | 594.0799 | 624.401 | 582.1531 | 554.714 | 609.2946
3649.2542 | 667.9874 | 643.3234 | 594.562 | 623.7352 | 581.935 | 555.0404 | 609.3973
3650.2542 | 668.7574 | 645.706 | 595.3505 | 625.2504 | 581.9949 | 555.4714 | 609.2315
3651.2542 | 668.8181 | 645.8037 | 595.9183 | 629.1179 | 582.3536 | 555.8665 | 609.5712
3652.2542 | 667.7942 | 645.9831 | 596.2217 | 627.0102 | 582.1005 | 556.0952 | 609.2338
3653.2542 | 670.2483 | 645.6324 | 595.7295 | 627.0819 | 582.052 | 556.0962 | 609.0802
3654.2542 | 670.702 | 645.5382 | 596.531 | 628.9411 | 582.4321 | 555.9468 | 608.7673
3655.2542 | 673.4297 | 646.234 | 595.8271 | 631.4698 | 582.4473 | 556.1019 | 609.2821
3656.2542 | 671.6821 | 645.4686 | 595.3749 | 630.6711 | 582.0605 | 555.8837 | 609.0378
3657.2542 | 670.8846 | 644.4704 | 594.7935 | 631.7739 | 582.0387 | 556.0625 | 609.0274
3658.2542 | 668.6678 | 640.6413 | 592.5022 | 628.1151 | 582.1602 | 555.8442 | 608.5654
3659.2542 | 669.6311 | 639.1731 | 591.3886 | 630.5819 | 582.0469 | 555.552 | 608.4569
3660.2542 | 669.6438 | 639.767 | 592.3443 | 632.4514 | 582.4388 | 555.8247 | 608.9853
3661.2542 | 667.0124 | 638.2078 | 592.4483 | 628.4966 | 581.9198 | 555.9161 | 608.8519
3662.2542 | 665.2653 | 636.0278 | 590.9023 | 629.0675 | 581.6465 | 556.224 | 608.6759
3663.2542 | 667.7545 | 637.4604 | 590.5037 | 628.5995 | 581.6694 | 556.4365 | 608.0706
3664.2542 | 670.7117 | 640.3386 | 590.7872 | 630.3509 | 581.8998 | 556.8024 | 609.5718
3665.2542 | 670.2403 | 640.0721 | 590.4244 | 629.7101 | 581.989 | 556.3283 | 609.037
3666.2542 | 667.7903 | 638.9559 | 590.9178 | 630.7693 | 582.1328 | 556.885 | 609.0506
3667.2542 | 664.4337 | 640.6322 | 595.4997 | 633.0674 | 582.2136 | 557.4362 | 609.7337
3668.2542 | 660.33 | 641.0534 | 596.2286 | 633.932 | 582.3037 | 557.7125 | 609.7365
3669.2542 | 658.5796 | 640.4444 | 597.102 | 630.1582 | 582.2633 | 558.1084 | 609.3373
3670.2542 | 656.2559 | 640.962 | 597.2031 | 630.0439 | 582.7786 | 558.1733 | 609.3222
3671.2542 | 657.7336 | 641.2917 | 596.8221 | 628.8528 | 582.6605 | 558.1043 | 609.4858
3672.2542 | 656.2188 | 638.9287 | 595.8427 | 629.2607 | 582.6729 | 558.3903 | 609.2045
3673.2542 | 655.0887 | 639.4778 | 596.5007 | 633.8639 | 582.7699 | 558.6645 | 609.3406
3674.2542 | 657.1742 | 642.2337 | 597.1272 | 631.4511 | 582.6858 | 558.3313 | 609.5024
3675.2542 | 660.0561 | 645.5705 | 599.1925 | 634.586 | 582.8216 | 558.6765 | 610.0803
3676.2542 | 659.4894 | 646.0268 | 599.9678 | 632.6268 | 583.3186 | 558.871 | 610.53
3677.2542 | 660.7365 | 647.3568 | 599.4792 | 632.0855 | 582.7079 | 558.9695 | 610.143
3678.2542 | 661.6923 | 646.6251 | 599.6932 | 629.3196 | 582.7241 | 559.0056 | 610.2199
3679.2542 | 661.2353 | 643.6494 | 598.3772 | 631.4089 | 583.0537 | 559.2618 | 609.6117
3680.2542 | 662.1922 | 645.9423 | 598.8628 | 633.3947 | 583.7727 | 559.3015 | 610.4771
3681.2542 | 660.8381 | 646.0921 | 599.077 | 632.9405 | 583.6784 | 559.4691 | 610.6352
3682.2542 | 660.8159 | 645.9427 | 599.0364 | 634.3063 | 583.5856 | 559.7429 | 611.0966
3683.2542 | 660.6297 | 646.7832 | 599.864 | 635.0342 | 583.6394 | 559.9078 | 610.928
3684.2542 | 662.243 | 646.1371 | 599.1475 | 634.3871 | 583.7018 | 559.6075 | 611.3195
3685.2542 | 663.2455 | 645.4775 | 598.7153 | 635.6376 | 583.7152 | 559.7163 | 611.6816
3686.2542 | 662.446 | 642.5302 | 596.7747 | 634.5224 | 583.5076 | 558.9021 | 611.454
3687.2542 | 662.3188 | 639.8959 | 594.0391 | 635.3644 | 583.3292 | 558.9578 | 611.3851
3688.2542 | 661.0807 | 637.5284 | 592.2679 | 633.0238 | 583.0805 | 559.3881 | 610.7596
3689.2542 | 661.5082 | 636.8705 | 590.7296 | 632.742 | 582.8924 | 559.1539 | 610.2233
3690.2542 | 663.285 | 634.9269 | 589.3492 | 630.6581 | 582.8382 | 559.4173 | 609.7328
3691.2542 | 666.2338 | 635.3326 | 588.6381 | 632.1802 | 583.0774 | 559.5621 | 610.2822
3692.2542 | 662.7917 | 634.4722 | 588.424 | 631.2502 | 583.12 | 559.2861 | 610.7769
3693.2542 | 662.0922 | 634.3346 | 589.0291 | 632.959 | 583.3461 | 559.3649 | 610.9997
3694.2542 | 665.5378 | 635.585 | 588.8324 | 634.464 | 583.2074 | 559.9374 | 611.2702
3695.2542 | 668.5769 | 636.9235 | 589.0321 | 633.698 | 583.3218 | 560.2459 | 611.2144
3696.2542 | 667.7046 | 638.2635 | 589.9289 | 633.2365 | 583.215 | 560.085 | 610.9597
3697.2542 | 664.5213 | 636.8335 | 590.025 | 635.3433 | 583.012 | 560.6174 | 610.8907
3698.2542 | 663.9057 | 635.9663 | 589.7131 | 633.6105 | 583.0964 | 560.7397 | 610.7811
3699.2542 | 665.7426 | 637.9547 | 590.3952 | 632.7194 | 582.6859 | 560.8408 | 610.4975
3700.2542 | 667.3166 | 639.8795 | 591.6541 | 632.2473 | 582.679 | 560.835 | 611.2235
3701.2542 | 665.6052 | 640.3446 | 592.1947 | 634.4532 | 583.0194 | 561.0611 | 611.3529
3702.2542 | 665.5091 | 640.2174 | 592.282 | 633.99 | 582.7348 | 560.6704 | 611.3373
3703.2542 | 666.6758 | 641.3484 | 593.2508 | 635.0199 | 583.1743 | 561.241 | 611.5315
3704.2542 | 666.0362 | 641.9478 | 593.6569 | 637.3238 | 583.1716 | 561.3799 | 611.7988
3705.2542 | 665.0382 | 642.6878 | 593.837 | 635.8625 | 583.3285 | 561.4154 | 612.3152
3706.2542 | 662.9458 | 643.1341 | 593.1699 | 630.3307 | 582.8033 | 561.3585 | 612.1131
3707.2542 | 663.5952 | 641.7755 | 592.782 | 632.4987 | 582.7117 | 561.7324 | 611.6135
3708.2542 | 664.1231 | 641.2012 | 591.8957 | 630.6613 | 582.6958 | 562.0232 | 611.6009
3709.2542 | 662.4795 | 640.5152 | 591.41 | 631.6169 | 582.9142 | 561.7608 | 611.4455
3710.2542 | 660.3552 | 641.3502 | 593.3219 | 636.0914 | 583.4394 | 562.8024 | 612.0525
3711.2542 | 660.5671 | 642.9385 | 594.377 | 634.4595 | 583.5895 | 562.711 | 611.8633
3712.2542 | 661.486 | 642.2537 | 593.7206 | 633.463 | 583.5501 | 562.1086 | 611.6484
3713.2542 | 663.7972 | 643.888 | 593.9617 | 635.1513 | 583.4685 | 562.5632 | 611.7533
3714.2542 | 661.4822 | 642.023 | 593.6827 | 635.1827 | 583.2203 | 562.7261 | 611.785
3715.2542 | 661.9785 | 642.8563 | 595.9692 | 633.1374 | 583.1157 | 562.7244 | 611.3861
3716.2542 | 661.1335 | 642.2128 | 595.2204 | 633.1832 | 583.0441 | 562.9845 | 610.9993
3717.2542 | 660.8077 | 643.1282 | 595.5636 | 636.4422 | 583.5145 | 563.1599 | 611.5355
3718.2542 | 662.979 | 643.1305 | 594.2552 | 633.9805 | 582.9733 | 563.2678 | 611.3227
3719.2542 | 663.4762 | 641.9756 | 592.7996 | 634.6581 | 582.9399 | 563.0346 | 611.0996
3720.2542 | 663.781 | 642.1452 | 592.1428 | 635.4353 | 583.1259 | 563.2179 | 611.048
3721.2542 | 662.8602 | 641.2835 | 591.7553 | 636.7406 | 583.0058 | 563.0966 | 611.1334
3722.2542 | 664.0237 | 640.8063 | 591.2212 | 634.3842 | 583.0716 | 562.9269 | 610.9698
3723.2542 | 663.171 | 639.4028 | 589.9973 | 634.4542 | 582.9174 | 563.1316 | 610.7978
3724.2542 | 660.7113 | 637.2599 | 588.5983 | 630.7235 | 582.8613 | 562.9791 | 610.3939
3725.2542 | 662.7519 | 639.9433 | 589.9352 | 631.7306 | 582.8527 | 563.6712 | 610.8297
3726.2542 | 663.7329 | 641.9697 | 591.6275 | 635.0018 | 583.205 | 563.8462 | 611.742
3727.2542 | 662.0123 | 642.1778 | 592.5851 | 632.78 | 583.0671 | 564.1442 | 611.3495
3728.2542 | 660.4253 | 641.3998 | 593.3143 | 634.051 | 583.0379 | 564.3629 | 611.5005
3729.2542 | 659.8014 | 642.2526 | 594.342 | 635.395 | 583.5096 | 564.4422 | 611.6227
3730.2542 | 659.0033 | 641.7222 | 594.6526 | 634.4562 | 583.2427 | 564.6276 | 611.2997
3731.2542 | 658.4665 | 643.1109 | 597.0074 | 635.5121 | 583.5634 | 564.9328 | 611.6712
3732.2542 | 658.0425 | 645.9188 | 598.1263 | 633.216 | 583.5598 | 565.1072 | 611.7943
3733.2542 | 660.2587 | 647.965 | 598.72 | 634.7145 | 583.7387 | 565.2978 | 611.9504
3734.2542 | 664.4708 | 648.5929 | 598.0729 | 635.3188 | 583.9367 | 565.6793 | 612.1013
3735.2542 | 662.9668 | 647.0977 | 597.302 | 639.2277 | 584.4734 | 565.8327 | 612.8071
3736.2542 | 661.3878 | 644.9457 | 594.9974 | 637.0073 | 584.1758 | 565.4532 | 612.5104
3737.2542 | 662.1542 | 644.0811 | 593.7596 | 637.1622 | 583.8757 | 565.0762 | 613.5297
3738.2542 | 661.4635 | 642.9494 | 592.841 | 636.2865 | 583.6994 | 564.6301 | 612.9569
3739.2542 | 662.6304 | 641.0298 | 591.6195 | 637.1738 | 583.9344 | 565.2131 | 613.0282
3740.2542 | 661.6862 | 639.9413 | 591.1031 | 635.1425 | 583.7358 | 565.5468 | 612.943
3741.2542 | 661.5595 | 639.4044 | 590.8317 | 635.5165 | 584.3076 | 564.9647 | 612.6773
3742.2542 | 661.4916 | 640.3468 | 590.5046 | 636.9772 | 584.1344 | 565.5504 | 612.7995
3743.2542 | 661.4255 | 640.2569 | 591.0364 | 635.0378 | 584.1788 | 565.301 | 612.6751
3744.2542 | 660.8033 | 639.8203 | 590.7061 | 637.9749 | 584.3621 | 565.7221 | 612.9266
3745.2542 | 659.0396 | 639.5396 | 590.3461 | 639.122 | 584.4006 | 566.1426 | 614.5325
3746.2542 | 659.6335 | 640.9986 | 592.0264 | 636.4172 | 584.3171 | 566.1185 | 615.1058
3747.2542 | 661.5631 | 643.2589 | 593.6497 | 637.5596 | 584.1326 | 566.5266 | 614.9618
3748.2542 | 661.6783 | 643.5357 | 592.2398 | 638.8829 | 584.5264 | 565.4095 | 615.2078
3749.2542 | 661.4023 | 645.3797 | 592.6997 | 638.757 | 584.5479 | 566.6316 | 615.0978
3750.2542 | 661.4582 | 645.9271 | 592.9178 | 638.1761 | 584.6262 | 566.3609 | 615.1501
3751.2542 | 661.5202 | 647.739 | 593.6861 | 638.1432 | 584.6488 | 565.7843 | 614.9843
3752.2542 | 660.4316 | 648.3214 | 594.1895 | 639.6313 | 584.4912 | 566.351 | 614.8262
3753.2542 | 659.1294 | 646.8678 | 593.8762 | 633.4789 | 584.427 | 567.1271 | 614.8146
3754.2542 | 658.3646 | 645.8781 | 592.6433 | 637.1935 | 584.6576 | 567.2085 | 614.5636
3755.2542 | 657.8695 | 643.1775 | 592.8588 | 635.1491 | 584.5815 | 566.7601 | 614.3765
3756.2542 | 656.5771 | 643.6589 | 592.0518 | 637.0068 | 584.6495 | 567.3213 | 614.1625
3757.2542 | 656.2345 | 643.1142 | 591.9205 | 635.7248 | 584.3729 | 567.0501 | 614.0937
3758.2542 | 657.1905 | 642.9892 | 591.1879 | 635.4675 | 584.1726 | 567.1476 | 613.8621
3759.2542 | 658.3388 | 641.965 | 591.5269 | 637.8639 | 584.3586 | 567.4112 | 614.228
3760.2542 | 659.7762 | 642.1487 | 592.0836 | 637.1513 | 584.088 | 567.4463 | 613.7181
3761.2542 | 658.46 | 640.8239 | 591.0014 | 635.2281 | 584.0569 | 566.9965 | 613.3106
3762.2542 | 656.8297 | 640.0695 | 591.4898 | 635.3475 | 584.05 | 567.2475 | 613.1444
3763.2542 | 655.1632 | 640.2119 | 592.0904 | 633.7921 | 584.0823 | 567.4459 | 612.7855
3764.2542 | 654.8058 | 642.0347 | 594.373 | 635.0701 | 584.3411 | 567.6331 | 612.678
3765.2542 | 656.8259 | 643.5167 | 593.8205 | 634.6355 | 584.4661 | 567.7112 | 612.8125
3766.2542 | 657.343 | 642.6315 | 593.701 | 636.0435 | 584.4783 | 567.8778 | 613.0451
3767.2542 | 655.5152 | 642.1578 | 593.082 | 635.0854 | 584.253 | 567.9748 | 612.968
3768.2542 | 657.0374 | 642.5004 | 594.0687 | 635.8847 | 584.2042 | 568.11 | 612.3716
3769.2542 | 657.9169 | 644.7479 | 594.9537 | 637.5106 | 584.429 | 568.3128 | 613.3045
3770.2542 | 656.8253 | 642.8733 | 594.4044 | 636.9617 | 584.5594 | 568.0711 | 613.2467
3771.2542 | 655.7766 | 642.7404 | 594.0726 | 639.5345 | 584.637 | 568.4077 | 613.8061
3772.2542 | 658.5267 | 643.8832 | 593.6845 | 636.7789 | 584.1862 | 567.8119 | 613.704
3773.2542 | 661.9487 | 644.1383 | 593.6385 | 636.0968 | 584.5414 | 567.4282 | 613.3909
3774.2542 | 664.0044 | 640.4223 | 591.8755 | 639.6839 | 584.7752 | 567.8507 | 613.3539
3775.2542 | 665.0791 | 639.6175 | 591.1924 | 640.5404 | 584.4689 | 567.7623 | 613.0181
3776.2542 | 664.2341 | 637.7931 | 590.3039 | 637.1101 | 584.0455 | 567.2568 | 612.7643
3777.2542 | 661.3419 | 636.0775 | 590.3355 | 637.8054 | 584.2065 | 567.4987 | 613.0428
3778.2542 | 660.0322 | 638.6074 | 589.716 | 638.7028 | 584.5236 | 567.8697 | 613.4624
3779.2542 | 662.5074 | 639.1934 | 589.4098 | 639.0876 | 584.4703 | 568.171 | 613.6758
3780.2542 | 663.0644 | 638.0181 | 590.0623 | 641.0687 | 585.0812 | 568.5319 | 614.0552
3781.2542 | 660.6028 | 634.6423 | 588.3243 | 641.1827 | 584.8296 | 568.306 | 613.6202
3782.2542 | 658.7119 | 633.8109 | 586.2944 | 639.2539 | 584.5263 | 567.8994 | 613.6112
3783.2542 | 661.7367 | 635.7621 | 585.9555 | 638.0606 | 584.4892 | 568.0491 | 613.8711
3784.2542 | 662.7045 | 635.4747 | 585.5807 | 634.4369 | 584.2134 | 567.8664 | 613.5781
3785.2542 | 664.6852 | 635.6079 | 585.122 | 634.3118 | 584.0799 | 567.3543 | 613.3365
3786.2542 | 662.8637 | 633.1845 | 584.1916 | 633.9299 | 584.0594 | 567.5575 | 613.0419
3787.2542 | 661.234 | 632.1881 | 583.8071 | 632.6801 | 583.9896 | 567.8389 | 612.9057
3788.2542 | 662.5768 | 634.0189 | 584.4806 | 636.8771 | 584.1876 | 568.2495 | 612.7024
3789.2542 | 663.3523 | 634.6661 | 584.8733 | 637.9213 | 584.5405 | 568.7353 | 612.7386
3790.2542 | 663.4837 | 634.118 | 585.2564 | 637.1119 | 584.5495 | 568.6092 | 612.6253
3791.2542 | 664.3983 | 632.8499 | 584.9234 | 636.2887 | 584.5236 | 568.556 | 611.9959
3792.2542 | 665.889 | 632.6631 | 583.6921 | 636.3019 | 584.4571 | 569.1879 | 609.5931
3793.2542 | 664.5829 | 631.241 | 582.8032 | 638.2292 | 584.8264 | 569.3205 | 590.98
3794.2542 | 663.5809 | 631.9406 | 582.4584 | 640.2917 | 585.2344 | 569.3005 | 613.3943
3795.2542 | 661.5311 | 633.2572 | 584.8562 | 639.7206 | 585.3211 | 568.7869 | 612.7931
3796.2542 | 662.7988 | 634.7189 | 585.0986 | 640.0659 | 585.2783 | 568.5625 | 613.4129
3797.2542 | 663.0409 | 633.0148 | 585.2696 | 642.3253 | 585.2963 | 568.779 | 613.8463
3798.2542 | 659.6483 | 630.5131 | 583.265 | 639.3967 | 584.7793 | 567.6183 | 613.7327
3799.2542 | 656.8294 | 630.3234 | 582.4136 | 638.7674 | 584.9692 | 567.5262 | 613.4165
3800.2542 | 659.2853 | 632.1616 | 583.159 | 642.2045 | 585.2737 | 568.1258 | 614.424
3801.2542 | 661.0164 | 634.142 | 582.7008 | 640.8305 | 584.8143 | 568.0994 | 614.2922
3802.2542 | 660.7137 | 632.49 | 582.0033 | 638.4367 | 584.7227 | 568.5175 | 613.737
3803.2542 | 658.7073 | 630.3215 | 581.4104 | 637.8969 | 584.4523 | 568.7644 | 547.5485
3804.2542 | 658.7882 | 629.938 | 581.6557 | 637.559 | 584.6104 | 569.3902 | 545.5219
3805.2542 | 662.1173 | 629.3309 | 580.5783 | 637.3995 | 584.5734 | 568.7805 | 544.6744
3806.2542 | 662.5396 | 631.7782 | 580.7893 | 639.7355 | 584.4475 | 568.749 | 544.0407
3807.2542 | 662.8166 | 631.1843 | 581.3032 | 640.4845 | 584.4228 | 568.6251 | 545.6582
3808.2542 | 663.6294 | 628.8026 | 581.794 | 640.6282 | 584.5749 | 569.2406 | 547.199
3809.2542 | 664.145 | 629.4274 | 581.2207 | 640.3857 | 583.9903 | 569.4324 | 545.6453
3810.2542 | 663.1281 | 625.5439 | 579.771 | 640.1996 | 584.0209 | 569.3276 | 544.7775
3811.2542 | 661.6651 | 627.9454 | 578.7922 | 636.4424 | 584.149 | 569.5378 | 545.3726
3812.2542 | 660.9781 | 629.5299 | 580.4469 | 635.2031 | 584.2706 | 569.63 | 545.8119
3813.2542 | 661.2865 | 631.5611 | 580.7234 | 635.6018 | 584.1695 | 569.7763 | 545.2244
3814.2542 | 662.4525 | 633.0435 | 581.8577 | 640.2754 | 584.7332 | 569.9281 | 545.6148
3815.2542 | 663.3193 | 635.2885 | 582.1571 | 635.6471 | 584.8248 | 569.7195 | 545.4261
3816.2542 | 663.9016 | 636.0523 | 582.5906 | 638.8871 | 584.9865 | 570.267 | 545.0308
3817.2542 | 662.9561 | 634.5002 | 581.7677 | 639.4849 | 584.773 | 570.7673 | 545.6849
3818.2542 | 660.6686 | 633.8037 | 582.2202 | 639.4102 | 584.9611 | 570.3942 | 545.6243
3819.2542 | 660.0727 | 634.1985 | 584.0817 | 638.2449 | 585.119 | 570.1177 | 545.484
3820.2542 | 660.8241 | 635.2804 | 583.8372 | 638.784 | 584.9535 | 569.615 | 547.417
3821.2542 | 658.8304 | 633.7328 | 582.482 | 637.8868 | 584.6218 | 569.7562 | 546.4149
3822.2542 | 657.5212 | 632.6559 | 581.8145 | 636.4318 | 584.1732 | 569.6452 | 545.6705
3823.2542 | 658.0014 | 636.8102 | 582.5466 | 636.6936 | 584.108 | 569.8033 | 545.9746
3824.2542 | 660.1908 | 637.3685 | 583.0881 | 637.8617 | 584.2962 | 569.302 | 546.1471
3825.2542 | 660.9097 | 635.4997 | 581.6289 | 636.5983 | 584.1087 | 569.6677 | 546.1968
3826.2542 | 658.7612 | 632.8473 | 580.4711 | 637.9351 | 584.2252 | 569.4371 | 545.7116
3827.2542 | 657.7158 | 634.0795 | 580.9959 | 639.2894 | 584.076 | 569.3334 | 546.0946
3828.2542 | 657.386 | 634.9795 | 581.8523 | 638.4716 | 584.3933 | 569.4855 | 546.3877
3829.2542 | 657.0383 | 638.0698 | 583.629 | 641.1521 | 584.8439 | 569.999 | 547.8901
3830.2542 | 656.4156 | 639.1135 | 584.5726 | 639.7809 | 585.506 | 569.8476 | 548.2801
3831.2542 | 654.4248 | 639.517 | 586.7618 | 640.0378 | 585.5568 | 569.7981 | 548.1363
3832.2542 | 655.587 | 642.3215 | 587.8718 | 643.1931 | 585.9228 | 569.8652 | 549.0772
3833.2542 | 657.3066 | 645.2158 | 586.6066 | 643.9531 | 585.7486 | 570.9408 | 548.7501
3834.2542 | 657.362 | 644.304 | 586.5045 | 642.3954 | 585.8631 | 570.2411 | 549.3463
3835.2542 | 656.7117 | 642.7783 | 586.802 | 642.4483 | 585.8299 | 570.5443 | 549.5687
3836.2542 | 655.5226 | 641.1551 | 586.9912 | 644.3275 | 586.3117 | 570.3714 | 550.1508
3837.2542 | 654.7758 | 640.2703 | 587.2873 | 642.4322 | 585.8926 | 570.3106 | 549.2513
3838.2542 | 654.1272 | 639.3022 | 585.4409 | 642.6205 | 585.7257 | 570.1209 | 549.7926
3839.2542 | 654.0481 | 641.0502 | 584.8812 | 645.1415 | 585.8048 | 570.4371 | 549.7181
3840.2542 | 655.6447 | 642.2219 | 584.6177 | 642.1124 | 585.7072 | 570.058 | 550.1045
3841.2542 | 653.8884 | 639.3127 | 584.0189 | 642.9316 | 585.9707 | 570.117 | 549.6421
3842.2542 | 653.4741 | 638.0966 | 583.865 | 644.5244 | 586.1724 | 570.1311 | 549.8207
3843.2542 | 652.0031 | 636.0557 | 582.7328 | 642.3726 | 585.6977 | 569.8092 | 550.0549
3844.2542 | 649.7991 | 634.6774 | 582.5067 | 642.9181 | 586.009 | 570.0948 | 551.2552
3845.2542 | 649.3206 | 635.6042 | 582.5811 | 643.0748 | 585.9829 | 570.0993 | 550.9704
3846.2542 | 649.8641 | 635.4903 | 583.7039 | 642.8168 | 586.184 | 570.4519 | 550.9488
3847.2542 | 649.7461 | 635.7533 | 586.4353 | 643.242 | 586.1213 | 571.4791 | 551.3487
3848.2542 | 651.2355 | 638.8351 | 586.5377 | 645.5323 | 585.9378 | 571.6861 | 551.2573
3849.2542 | 652.8017 | 641.1671 | 588.0076 | 646.0835 | 586.1842 | 572.1806 | 552.0002
3850.2542 | 653.8816 | 641.4336 | 588.8815 | 643.7918 | 586.4638 | 571.8368 | 552.0847
3851.2542 | 656.0444 | 641.0837 | 587.6198 | 644.2794 | 586.5364 | 572.4272 | 552.5041
3852.2542 | 656.322 | 642.0363 | 586.745 | 641.5425 | 586.096 | 571.7016 | 550.94
3853.2542 | 655.1808 | 641.6178 | 585.8998 | 641.2144 | 585.7634 | 571.8155 | 551.4428
3854.2542 | 656.01 | 643.0576 | 587.0712 | 642.4778 | 586.0777 | 572.4362 | 550.9134
3855.2542 | 655.7171 | 643.0967 | 587.6272 | 644.8136 | 586.5757 | 573.4357 | 551.1276
3856.2542 | 655.032 | 642.6608 | 588.0371 | 643.0632 | 586.5352 | 573.4671 | 550.9831
3857.2542 | 655.7619 | 643.3473 | 588.6698 | 645.4578 | 586.8219 | 573.5148 | 551.2491
3858.2542 | 658.4887 | 644.6815 | 589.3702 | 645.8726 | 586.8159 | 574.0184 | 550.9511
3859.2542 | 661.1956 | 642.8296 | 588.8298 | 645.4279 | 586.7733 | 573.8089 | 550.6636
3860.2542 | 661.0482 | 640.5106 | 586.9325 | 644.9416 | 586.4937 | 573.4874 | 549.8221
3861.2542 | 659.6822 | 639.593 | 586.2108 | 643.9357 | 586.4664 | 573.971 | 549.585
3862.2542 | 657.2671 | 638.9149 | 586.5523 | 642.6851 | 586.3109 | 574.4978 | 549.3002
3863.2542 | 654.7632 | 638.1805 | 586.9276 | 644.8267 | 586.5784 | 574.6107 | 549.5776
3864.2542 | 655.1412 | 637.165 | 585.8625 | 646.2313 | 586.6653 | 575.7382 | 550.2521
3865.2542 | 657.2481 | 636.4769 | 584.3444 | 645.0455 | 586.1249 | 575.0495 | 548.9151
3866.2542 | 659.8876 | 636.7062 | 584.2903 | 643.6346 | 586.1313 | 575.0649 | 547.5942
3867.2542 | 661.5608 | 636.4971 | 583.7942 | 644.797 | 586.3642 | 574.8324 | 547.3333
3868.2542 | 660.1253 | 633.9207 | 581.5904 | 645.3666 | 586.1133 | 573.8949 | 546.1496
3869.2542 | 658.0058 | 633.3803 | 581.769 | 643.7505 | 586.1939 | 573.966 | 545.516
3870.2542 | 659.0802 | 634.8351 | 582.2203 | 645.1495 | 586.0349 | 574.4506 | 545.9941
3871.2542 | 660.1309 | 636.1505 | 583.2563 | 646.1057 | 585.944 | 574.5887 | 546.3485
3872.2542 | 662.5224 | 638.2185 | 584.2214 | 645.0036 | 586.1955 | 573.526 | 545.7065
3873.2542 | 660.5341 | 635.6862 | 582.434 | 646.2181 | 586.147 | 573.9838 | 546.3526
3874.2542 | 658.8498 | 633.7161 | 580.8262 | 645.0042 | 586.5453 | 573.9709 | 546.5827
3875.2542 | 656.9614 | 633.0732 | 579.048 | 644.0978 | 585.8507 | 573.2812 | 547.0275
3876.2542 | 659.242 | 634.9528 | 579.7468 | 642.8332 | 585.4542 | 573.4919 | 547.6194
3877.2542 | 660.6558 | 635.3951 | 580.2584 | 639.9062 | 585.5727 | 573.2532 | 547.5202
3878.2542 | 659.4047 | 635.3698 | 580.1721 | 641.7535 | 585.5435 | 573.6802 | 548.0189
3879.2542 | 659.9211 | 634.2237 | 578.5904 | 641.1809 | 585.5558 | 573.544 | 548.2594
3880.2542 | 663.4122 | 634.3811 | 578.7941 | 641.5198 | 585.6952 | 573.5989 | 547.9591
3881.2542 | 662.4384 | 634.3864 | 579.0992 | 641.7994 | 585.3141 | 573.9862 | 548.0498
3882.2542 | 659.3588 | 633.1745 | 580.6115 | 643.5693 | 585.6488 | 574.5228 | 548.5096
3883.2542 | 658.2064 | 631.5843 | 579.5312 | 642.0436 | 585.5677 | 574.4639 | 548.2082
3884.2542 | 656.6201 | 632.0686 | 581.2105 | 644.542 | 585.6251 | 574.2612 | 549.2006
3885.2542 | 656.8055 | 631.4859 | 580.2946 | 644.8811 | 585.6961 | 574.7451 | 549.5031
3886.2542 | 659.8047 | 634.3657 | 580.2747 | 645.7603 | 585.7016 | 574.7299 | 549.8088
3887.2542 | 657.109 | 634.0864 | 580.0683 | 641.8634 | 585.4116 | 574.4253 | 549.0078
3888.2542 | 657.6599 | 635.7615 | 579.9385 | 642.2342 | 585.5047 | 574.0765 | 549.2148
3889.2542 | 656.4051 | 635.0103 | 579.428 | 643.7349 | 585.6611 | 574.6246 | 549.5138
3890.2542 | 654.8395 | 632.4884 | 577.6484 | 643.7123 | 585.518 | 574.5117 | 550.4045
3891.2542 | 653.0904 | 628.9854 | 576.5738 | 643.2302 | 585.3543 | 574.8068 | 548.214
3892.2542 | 655.5508 | 631.3873 | 577.0711 | 642.0346 | 585.1251 | 574.0795 | 547.8475
3893.2542 | 657.3875 | 632.5223 | 577.6498 | 644.1272 | 585.3248 | 575.3436 | 548.5519
3894.2542 | 656.0048 | 632.2176 | 577.8369 | 645.1017 | 585.6972 | 575.5344 | 548.3992
3895.2542 | 653.6947 | 630.6856 | 577.2494 | 645.5055 | 585.8398 | 575.4419 | 548.9789
3896.2542 | 651.0065 | 628.3504 | 575.878 | 644.4263 | 585.2862 | 574.9644 | 547.7033
3897.2542 | 650.7106 | 628.8334 | 576.2716 | 644.4714 | 585.1519 | 574.882 | 547.719
3898.2542 | 652.1017 | 632.3714 | 578.6049 | 643.736 | 585.1178 | 574.4462 | 546.3766
3899.2542 | 654.4057 | 634.8133 | 580.1554 | 645.308 | 585.4689 | 574.6288 | 547.2107
3900.2542 | 654.2528 | 635.7245 | 580.6253 | 645.7829 | 586.0129 | 575.3531 | 548.7917
3901.2542 | 652.8676 | 633.4749 | 579.2362 | 644.469 | 585.9591 | 575.2259 | 547.622
3902.2542 | 651.8311 | 633.321 | 579.969 | 643.7434 | 586.1645 | 575.1786 | 548.29
3903.2542 | 650.3233 | 634.1938 | 580.6252 | 645.002 | 585.9111 | 575.2087 | 547.5208
3904.2542 | 656.9139 | 639.6621 | 582.6523 | 643.3845 | 585.9548 | 575.5514 | 548.4506
3905.2542 | 658.1993 | 638.256 | 582.6931 | 644.4479 | 586.3724 | 575.5373 | 548.9147
3906.2542 | 656.7857 | 635.5362 | 581.0153 | 645.8848 | 586.3312 | 576.4018 | 550.5227
3907.2542 | 655.2589 | 633.7418 | 580.5711 | 645.8436 | 586.5352 | 576.5366 | 549.3485
3908.2542 | 658.7602 | 635.2943 | 581.0722 | 644.6254 | 586.3852 | 576.4549 | 550.2412
3909.2542 | 661.9805 | 636.8308 | 582.1539 | 644.1499 | 586.7019 | 576.1845 | 550.8877
3910.2542 | 660.927 | 632.6581 | 579.9155 | 645.0964 | 586.5442 | 576.6532 | 551.5725
3911.2542 | 661.7351 | 634.2547 | 579.9918 | 644.0748 | 586.6799 | 577.4964 | 552.3678
3912.2542 | 663.5461 | 637.7189 | 581.9571 | 643.7212 | 586.7899 | 576.5548 | 550.9212
3913.2542 | 664.9338 | 639.6248 | 582.8663 | 645.5052 | 587.0281 | 577.4074 | 553.5774
3914.2542 | 664.9146 | 642.5262 | 582.9683 | 644.9488 | 586.7863 | 578.54 | 551.3101
3915.2542 | 663.1148 | 641.2239 | 583.0929 | 645.6287 | 587.0045 | 577.8062 | 551.0076
3916.2542 | 663.5999 | 640.0035 | 582.9792 | 647.1843 | 587.0301 | 578.4429 | 552.1345
3917.2542 | 665.2271 | 639.0993 | 580.8465 | 646.4437 | 587.108 | 578.1778 | 550.1338
3918.2542 | 661.9854 | 635.5488 | 579.1084 | 644.66 | 586.9647 | 577.5212 | 541.6763
3919.2542 | 663.1424 | 637.1205 | 580.7027 | 647.141 | 587.0941 | 579.031 | 531.5216
3920.2542 | 664.0336 | 639.794 | 580.0655 | 644.3393 | 586.3603 | 578.2287 | 561.0306
3921.2542 | 664.0844 | 638.4207 | 579.447 | 644.9107 | 586.5548 | 578.4802 | 574.1246
3922.2542 | 665.5158 | 636.0949 | 579.1286 | 647.985 | 586.6434 | 578.7449 | 575.1975
3923.2542 | 661.387 | 635.0626 | 578.5589 | 644.8259 | 586.0595 | 578.0155 | 574.0769
3924.2542 | 663.4999 | 635.0647 | 579.8533 | 645.7698 | 586.6131 | 578.7818 | 574.6566
3925.2542 | 665.2826 | 635.8691 | 579.3997 | 647.2652 | 586.6243 | 578.9302 | 574.0658
3926.2542 | 663.421 | 634.4764 | 578.969 | 647.9079 | 586.4173 | 578.5958 | 572.9901
3927.2542 | 662.1416 | 633.4949 | 578.3459 | 648.6855 | 586.4063 | 578.9957 | 573.4484
3928.2542 | 660.0105 | 631.9499 | 577.1284 | 645.7889 | 586.1114 | 577.8916 | 570.5457
3929.2542 | 658.7699 | 633.0782 | 576.8183 | 645.6937 | 586.2044 | 578.3742 | 570.8375
3930.2542 | 657.3982 | 632.9996 | 577.7592 | 646.8867 | 586.3257 | 581.0925 | 568.0603
3931.2542 | 655.3815 | 629.7701 | 575.7924 | 644.6255 | 585.7157 | 581.8976 | 566.3611
3932.2542 | 654.2845 | 626.7209 | 575.4626 | 645.9055 | 585.8721 | 582.5586 | 568.041
3933.2542 | 654.8073 | 629.0833 | 574.7119 | 644.3373 | 585.5643 | 582.5608 | 567.8084
3934.2542 | 654.3368 | 628.896 | 575.7119 | 642.5675 | 585.5506 | 582.0766 | 566.5109
3935.2542 | 653.7576 | 626.7993 | 575.4811 | 643.8458 | 585.6293 | 582.1136 | 568.1336
3936.2542 | 653.8248 | 628.9355 | 574.9593 | 645.6013 | 585.7632 | 583.0154 | 569.6293
3937.2542 | 653.1415 | 629.6502 | 575.4092 | 645.5074 | 585.523 | 582.9969 | 567.984
3938.2542 | 653.0512 | 629.7466 | 575.2698 | 644.1813 | 585.651 | 582.8892 | 570.0015
3939.2542 | 657.4498 | 633.8445 | 576.8818 | 644.6235 | 585.7977 | 582.8504 | 570.6024
3940.2542 | 657.7536 | 635.4968 | 578.3806 | 644.3488 | 585.9328 | 583.6461 | 569.7989
3941.2542 | 655.8544 | 634.8794 | 577.5863 | 646.1943 | 585.7524 | 584.1494 | 571.0984
3942.2542 | 653.4723 | 634.4029 | 576.7275 | 643.8067 | 585.4243 | 583.3468 | 569.5674
3943.2542 | 652.6659 | 633.7471 | 576.6548 | 644.5893 | 586.0367 | 583.8015 | 568.3632
3944.2542 | 654.6746 | 636.246 | 578.0215 | 647.3777 | 586.4794 | 585.6411 | 567.5976
3945.2542 | 655.8819 | 638.7115 | 578.9491 | 646.1122 | 586.1282 | 585.7454 | 565.4566
3946.2542 | 655.2531 | 637.8181 | 579.7969 | 646.9454 | 586.8314 | 584.8161 | 563.1585
3947.2542 | 655.0883 | 637.5289 | 579.4048 | 646.5182 | 586.4494 | 575.3969 | 542.3261
3948.2542 | 659.0799 | 638.1552 | 579.9593 | 645.927 | 586.3883 | 574.8665 | 538.5587
3949.2542 | 657.0334 | 634.9085 | 579.5575 | 645.8642 | 586.3147 | 575.2207 | 540.1349
3950.2542 | 655.2417 | 634.2561 | 578.8906 | 646.5461 | 585.9574 | 574.8511 | 540.1438
3951.2542 | 653.2959 | 635.0706 | 578.6674 | 645.4244 | 585.8908 | 574.4925 | 540.3971
3952.2542 | 654.6099 | 634.271 | 578.4355 | 645.7661 | 585.9859 | 575.15 | 539.478
3953.2542 | 653.4425 | 632.3542 | 577.7561 | 647.3096 | 585.5559 | 575.2166 | 539.355
3954.2542 | 651.4523 | 631.773 | 577.1484 | 648.1906 | 586.4111 | 576.7565 | 538.0978
3955.2542 | 651.8486 | 631.7108 | 578.2206 | 646.4828 | 586.7612 | 575.0708 | 539.0262
3956.2542 | 652.9626 | 634.1935 | 579.9195 | 648.1156 | 586.6414 | 575.6079 | 538.9505
3957.2542 | 653.6408 | 633.2836 | 578.8089 | 646.2155 | 586.3023 | 570.5792 | 528.3531
3958.2542 | 654.5615 | 628.9806 | 577.7331 | 647.0163 | 586.5076 | 571.0232 | 529.2962
3959.2542 | 655.9864 | 628.2072 | 577.0622 | 645.9242 | 586.0292 | 571.295 | 527.2669
3960.2542 | 653.4345 | 626.348 | 575.7889 | 644.9426 | 585.7163 | 571.6116 | 528.9436